## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-11
Test Date: | 2006-11-20
Ignition Time Relative to Thermal Data: | 207 | s
Ignition Time Relative to Electrical Data: | 207 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Template Plot
Template Plot

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 11-1 |  |  |  | Location A | Location C - 6-cable bundle 11-2 |  |  |  | Location C | Location E - 3+1 Air drop bundle 11-3 |  | Location G - 6-cable bundle 11-4 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable 1 | TC-2 Above Bundle | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -207 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.4 | 270.8 | 5.3 | 15.8 | 15.8 | 15.9 | 16 | 18 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
1 | -206 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.4 | 258 | 5.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
2 | -205 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.3 | 247.1 | 6.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
3 | -204 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.3 | 243.1 | 6.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
4 | -203 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.3 | 230.2 | 6.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
5 | -202 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.6 | 266.3 | 5.3 | 15.8 | 15.8 | 15.9 | 16 | 18 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
6 | -201 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.8 | 252.1 | 5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
7 | -200 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.8 | 248.4 | 5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
8 | -199 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.5 | 250 | 5.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
9 | -198 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.4 | 245.1 | 6.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
10 | -197 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.5 | 248.1 | 6.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
11 | -196 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.2 | 250.1 | 8.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
12 | -195 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.4 | 246.3 | 9.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
13 | -194 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.6 | 244.4 | 9.1 | 15.8 | 15.7 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
14 | -193 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.4 | 247.7 | 9.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
15 | -192 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.5 | 244.8 | 8.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
16 | -191 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.4 | 228.9 | 7.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
17 | -190 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.7 | 248.6 | 6.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
18 | -189 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.8 | 238.8 | 6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
19 | -188 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 3.2 | 247.8 | 5.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
20 | -187 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 3.1 | 246.7 | 6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
21 | -186 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 3.4 | 231.2 | 6.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
22 | -185 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 3.2 | 224.3 | 5.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
23 | -184 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.1 | 227.5 | 5.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
24 | -183 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.8 | 231 | 5.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
25 | -182 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.2 | 250.9 | 6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
26 | -181 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.1 | 237.5 | 6.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
27 | -180 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.7 | 235.3 | 7.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
28 | -179 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.6 | 236.4 | 9.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
29 | -178 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.9 | 230.3 | 10.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
30 | -177 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.6 | 232.6 | 9.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
31 | -176 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.5 | 209 | 9.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
32 | -175 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.7 | 211.3 | 8.3 | 15.8 | 15.7 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
33 | -174 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.9 | 234.7 | 7.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
34 | -173 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.8 | 229.8 | 8.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
35 | -172 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.6 | 228 | 8.7 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
36 | -171 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.6 | 234.5 | 7.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
37 | -170 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.7 | 256.3 | 6.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
38 | -169 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3 | 248.4 | 6.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
39 | -168 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.3 | 236 | 6.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
40 | -167 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.4 | 238.2 | 6.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
41 | -166 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.2 | 235.1 | 6.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
42 | -165 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.3 | 233.8 | 7.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
43 | -164 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.6 | 235.4 | 7.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
44 | -163 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.1 | 233.7 | 7.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
45 | -162 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.3 | 250.3 | 7.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
46 | -161 | -7 | 0 | 0 | 17 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.1 | 228.5 | 9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
47 | -160 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2 | 224.1 | 10 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
48 | -159 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2 | 229.9 | 10.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
49 | -158 | -7 | 0 | 0 | 16.8 | 17.2 | 17 | 17 | 16.9 | 16.4 | 21.7 | 16.6 | 2 | 225.4 | 12.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
50 | -157 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.6 | 2.3 | 244.8 | 12.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
51 | -156 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.6 | 2.3 | 233.9 | 11.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
52 | -155 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.3 | 240.7 | 10.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
53 | -154 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.6 | 2 | 241.4 | 9.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
54 | -153 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.1 | 249.6 | 10.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
55 | -152 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2 | 239 | 10.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
56 | -151 | -7 | 0 | 0 | 16.9 | 17.2 | 17 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.1 | 251.4 | 10.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
57 | -150 | -6.9 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.3 | 247.8 | 11.7 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
58 | -149 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.2 | 244.9 | 11.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
59 | -148 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.9 | 240.2 | 10.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
60 | -147 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.8 | 235.3 | 8.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
61 | -146 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.9 | 241.5 | 7.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
62 | -145 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.9 | 244.4 | 8.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
63 | -144 | -7 | 0 | 0 | 16.9 | 17.2 | 17 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 1.8 | 250.3 | 9.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
64 | -143 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.7 | 255.9 | 9.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
65 | -142 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.8 | 254.3 | 9.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
66 | -141 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2 | 257.4 | 9.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
67 | -140 | -7 | 0 | 0 | 16.9 | 17.2 | 17 | 16.9 | 17 | 16.4 | 21.7 | 16.6 | 2.2 | 267.2 | 8.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
68 | -139 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.5 | 261.2 | 8.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
69 | -138 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.5 | 264.9 | 7.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
70 | -137 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 3 | 252.3 | 7.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
71 | -136 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 3 | 280.2 | 7.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
72 | -135 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.4 | 287.7 | 7.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
73 | -134 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.7 | 276.8 | 9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
74 | -133 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.8 | 271.9 | 9.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
75 | -132 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.6 | 268.4 | 9.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
76 | -131 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.3 | 266.7 | 9.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
77 | -130 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.2 | 247.5 | 9.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
78 | -129 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.6 | 2.4 | 270.8 | 10 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
79 | -128 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.6 | 2.7 | 269.5 | 10.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17 | 17.6 | 16.9
80 | -127 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.5 | 3 | 259.4 | 11.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
81 | -126 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.4 | 21.7 | 16.5 | 2.9 | 269.2 | 10.9 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
82 | -125 | -6.6 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.5 | 2.9 | 255.5 | 10.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
83 | -124 | -6.8 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.4 | 21.7 | 16.5 | 3.2 | 269.8 | 10 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
84 | -123 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.5 | 3.2 | 253.6 | 9.9 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
85 | -122 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.5 | 3 | 258.3 | 10.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
86 | -121 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.5 | 2.3 | 256.3 | 11.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
87 | -120 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.2 | 256.6 | 11.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
88 | -119 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.1 | 261.6 | 10.7 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
89 | -118 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2 | 260.5 | 10.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
90 | -117 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 1.9 | 263.7 | 10.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
91 | -116 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 1.9 | 274.3 | 10.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
92 | -115 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 1.8 | 263.6 | 9.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
93 | -114 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 1.8 | 269.4 | 9.7 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
94 | -113 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 1.8 | 269.9 | 9.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
95 | -112 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.1 | 265.2 | 9.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
96 | -111 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.6 | 2.3 | 271.3 | 9.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
97 | -110 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.6 | 272.5 | 9.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
98 | -109 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.6 | 269.3 | 9.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
99 | -108 | -6.9 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.5 | 275.8 | 8.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
100 | -107 | -6.9 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.5 | 282.4 | 8.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
101 | -106 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.5 | 2.4 | 278.8 | 9.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
102 | -105 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.7 | 269.2 | 8.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
103 | -104 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.7 | 256.1 | 8.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
104 | -103 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 2.6 | 261.8 | 8.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
105 | -102 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.9 | 261.2 | 8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
106 | -101 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.1 | 259.8 | 7.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
107 | -100 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 17 | 16.3 | 21.7 | 16.6 | 3.1 | 258.7 | 7.6 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
108 | -99 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 3.2 | 262.7 | 8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
109 | -98 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 16.9 | 16.3 | 21.7 | 16.5 | 3 | 266.4 | 8.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
110 | -97 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.8 | 258.6 | 9.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
111 | -96 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.3 | 21.7 | 16.5 | 2.5 | 262.1 | 9.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
112 | -95 | -6.9 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.5 | 256.7 | 9.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
113 | -94 | -6.9 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 16.9 | 16.3 | 21.7 | 16.5 | 2.5 | 250.3 | 8.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
114 | -93 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.1 | 238 | 8.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
115 | -92 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.1 | 246.1 | 7.9 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
116 | -91 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 16.9 | 16.3 | 21.7 | 16.5 | 1.9 | 241.6 | 7.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
117 | -90 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 1.9 | 232.9 | 7.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
118 | -89 | -7 | 0 | 0 | 17 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2 | 238.2 | 7.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
119 | -88 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.1 | 225.3 | 6.9 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.7 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
120 | -87 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.1 | 221.9 | 6.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
121 | -86 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.1 | 237.5 | 6.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
122 | -85 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2 | 246.3 | 5.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
123 | -84 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2 | 256.7 | 5.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
124 | -83 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2.2 | 264.1 | 5.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
125 | -82 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2 | 264.4 | 5.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
126 | -81 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.5 | 2 | 258 | 5.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
127 | -80 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2 | 262.3 | 5.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
128 | -79 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.2 | 280.1 | 5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
129 | -78 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.3 | 275.7 | 4.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
130 | -77 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.3 | 21.7 | 16.6 | 2.1 | 262 | 4.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
131 | -76 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2 | 242.7 | 3.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
132 | -75 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2 | 228.2 | 4.1 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
133 | -74 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.2 | 224 | 4.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
134 | -73 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.2 | 213.1 | 4.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
135 | -72 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.2 | 267.8 | 3.2 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
136 | -71 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.3 | 324 | 2.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
137 | -70 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.6 | 297.3 | 2.4 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
138 | -69 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.5 | 247.6 | 2.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
139 | -68 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.7 | 241.8 | 3.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
140 | -67 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 250 | 4.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
141 | -66 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.9 | 248.8 | 5.7 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
142 | -65 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.6 | 268.3 | 6.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
143 | -64 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.4 | 276.6 | 6.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
144 | -63 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.3 | 272.3 | 6.4 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
145 | -62 | -7 | 0 | 0 | 16.9 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.1 | 253.6 | 6.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
146 | -61 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2 | 277.2 | 6.5 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
147 | -60 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 1.9 | 256.9 | 6.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
148 | -59 | -6.9 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 1.9 | 235.2 | 5.9 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
149 | -58 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 1.9 | 242.4 | 6.3 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
150 | -57 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2 | 234.6 | 6.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.8 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
151 | -56 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2.1 | 239.2 | 6.4 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
152 | -55 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2.2 | 242.2 | 6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
153 | -54 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2.5 | 244.1 | 6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
154 | -53 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2.4 | 245.7 | 5.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
155 | -52 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2.4 | 245.5 | 5.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
156 | -51 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.2 | 245.3 | 4.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
157 | -50 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.1 | 242.7 | 4.5 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
158 | -49 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.2 | 242.3 | 4.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
159 | -48 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2.3 | 259.5 | 5.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
160 | -47 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.5 | 2 | 270.3 | 6.3 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
161 | -46 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 17 | 16.2 | 21.7 | 16.6 | 2 | 256 | 7 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.9 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
162 | -45 | -2.8 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.1 | 255 | 7.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
163 | -44 | -7.1 | 0 | 0 | 16.9 | 17.1 | 16.9 | 16.9 | 16.9 | 16.2 | 21.7 | 16.5 | 2.2 | 285.4 | 8.1 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
164 | -43 | -7.1 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.4 | 273.7 | 8.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
165 | -42 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 284.9 | 8.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
166 | -41 | -6.6 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 271.4 | 8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
167 | -40 | -6 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 3.1 | 290.7 | 7.8 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
168 | -39 | -6.2 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.8 | 278.9 | 7.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
169 | -38 | -6.1 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 275.6 | 8.3 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
170 | -37 | -5.9 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 260.1 | 7.8 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
171 | -36 | -6.3 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.5 | 264.1 | 7.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
172 | -35 | -6.6 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 270.5 | 7.6 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
173 | -34 | -6.8 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 268.7 | 7.5 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
174 | -33 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.9 | 269.1 | 7.4 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
175 | -32 | -7 | 0 | 0 | 16.8 | 17.2 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 3.1 | 264.3 | 7.7 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
176 | -31 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 3.1 | 267.9 | 8.6 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
177 | -30 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 3.2 | 267.1 | 9.9 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
178 | -29 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 3 | 264.9 | 11.5 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
179 | -28 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 256.8 | 11.2 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
180 | -27 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.6 | 247.9 | 10.9 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
181 | -26 | -7 | 0 | 0 | 16.9 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.6 | 250 | 9.9 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
182 | -25 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.7 | 261.3 | 9.6 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
183 | -24 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 274.5 | 9.7 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
184 | -23 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 16.9 | 16.9 | 16.2 | 21.7 | 16.5 | 2.8 | 259.7 | 9.7 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
185 | -22 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 16.9 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 251 | 10.5 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
186 | -21 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.9 | 262.2 | 11.5 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
187 | -20 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 16.9 | 16.9 | 16.2 | 21.7 | 16.6 | 2.9 | 265.2 | 11.4 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
188 | -19 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 16.9 | 16.9 | 16.2 | 21.7 | 16.6 | 2.9 | 250.8 | 12.4 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
189 | -18 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.6 | 257.8 | 13.4 | 15.8 | 15.7 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
190 | -17 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.6 | 2.6 | 263.5 | 12.4 | 15.8 | 15.8 | 15.8 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
191 | -16 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 16.9 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 261.5 | 11 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
192 | -15 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 263 | 10.3 | 15.8 | 15.7 | 15.8 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
193 | -14 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 275.3 | 11.3 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
194 | -13 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 269.1 | 12.6 | 15.8 | 15.7 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
195 | -12 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.4 | 282.7 | 12.2 | 15.8 | 15.8 | 15.9 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
196 | -11 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.6 | 285.1 | 12 | 15.8 | 15.8 | 15.9 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
197 | -10 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.9 | 285.4 | 11 | 15.8 | 15.8 | 16 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
198 | -9 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.7 | 294.2 | 10.5 | 15.8 | 15.8 | 16.1 | 16 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
199 | -8 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 285.7 | 10.7 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
200 | -7 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.4 | 279.4 | 11 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
201 | -6 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.4 | 285.3 | 10.2 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
202 | -5 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 291 | 9.3 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.9
203 | -4 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.5 | 299 | 8.6 | 15.8 | 15.8 | 16.1 | 16.1 | 18.1 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
204 | -3 | -7 | 0 | 0 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.3 | 309.7 | 8.2 | 15.8 | 15.8 | 16.1 | 16.1 | 18.2 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
205 | -2 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.3 | 276.7 | 8 | 15.8 | 15.9 | 16.1 | 16 | 18.2 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
206 | -1 | -7 | 0 | 0 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.2 | 278.5 | 7.4 | 15.8 | 15.9 | 16.1 | 16 | 18.2 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.8
207 | 0 | 63 | 25.2 | 29.4573 | 16.8 | 17.1 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.1 | 262 | 7.4 | 15.8 | 15.9 | 16.1 | 16.1 | 18.2 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
208 | 1 | 439.6 | 175.84 | 205.5468 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2 | 283.2 | 7.8 | 15.8 | 15.9 | 16.1 | 16.1 | 18.2 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.7 | 16.8
209 | 2 | 701.4 | 280.56 | 327.9585 | 16.9 | 17.1 | 16.8 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.1 | 271.8 | 7.9 | 15.8 | 16 | 16.1 | 16.1 | 18.3 | 15.8 | 15.7 | 16.1 | 15.7 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.1 | 17.6 | 16.9
210 | 3 | 750.1 | 300.04 | 350.7295 | 16.8 | 17.2 | 16.9 | 17 | 16.9 | 16.2 | 21.7 | 16.5 | 2.2 | 289.8 | 7.8 | 15.8 | 16.1 | 16.5 | 16.1 | 18.4 | 15.8 | 15.7 | 16.1 | 15.8 | 17.8 | 16 | 15.8 | 16 | 16.1 | 16.1 | 16.3 | 17.2 | 17.7 | 16.8
211 | 4 | 714.7 | 285.88 | 334.1772 | 16.9 | 17.1 | 16.9 | 17.1 | 16.9 | 16.2 | 21.7 | 16.5 | 2.4 | 291.4 | 7.7 | 15.8 | 19.6 | 30.1 | 16.1 | 22 | 15.8 | 15.9 | 17 | 15.8 | 18 | 16 | 15.8 | 16 | 16.1 | 16.2 | 16.3 | 17.1 | 17.6 | 16.8
212 | 5 | 682.9 | 273.16 | 319.3083 | 17 | 17.2 | 17.1 | 17.3 | 19.4 | 16.3 | 21.7 | 16.5 | 2.9 | 293.5 | 7.6 | 15.8 | 39.9 | 97.1 | 16.3 | 33.4 | 15.8 | 23 | 35.8 | 19 | 21.3 | 16 | 15.9 | 16 | 16.2 | 16.2 | 16.3 | 17.2 | 17.7 | 16.8
213 | 6 | 667.6 | 267.04 | 312.1544 | 17.1 | 17.3 | 17.4 | 17.6 | 40.1 | 16.3 | 21.7 | 16.5 | 3 | 291.2 | 8.2 | 15.8 | 80.6 | 177.3 | 16.6 | 61 | 15.8 | 43.8 | 75.4 | 26.2 | 29.3 | 16 | 16 | 16 | 16.5 | 16.4 | 16.3 | 17.4 | 17.7 | 16.8
214 | 7 | 653.3 | 261.32 | 305.468 | 17.6 | 17.5 | 17.8 | 18 | 71.1 | 16.3 | 21.7 | 16.5 | 3 | 295.2 | 8.7 | 15.8 | 133.9 | 268.9 | 17.3 | 87.9 | 15.9 | 69.6 | 128 | 31.4 | 39.1 | 16 | 16.1 | 16 | 17.2 | 16.6 | 16.3 | 17.5 | 17.7 | 16.8
215 | 8 | 638.5 | 255.4 | 298.5479 | 18.3 | 17.9 | 18.3 | 18.5 | 117.2 | 16.4 | 21.7 | 16.5 | 3.5 | 274.2 | 8.7 | 15.8 | 198.1 | 337.7 | 18.3 | 119.4 | 16.2 | 109.6 | 195.7 | 39.7 | 56.2 | 16 | 16.3 | 16 | 17.5 | 16.9 | 16.3 | 17.7 | 17.8 | 16.9
216 | 9 | 631.1 | 252.44 | 295.0878 | 18.9 | 18.6 | 19.5 | 19.7 | 161.1 | 16.4 | 21.7 | 16.5 | 3.8 | 279.9 | 8.7 | 15.8 | 278.4 | 405.5 | 19.6 | 149.2 | 16.7 | 158.1 | 265.2 | 47.4 | 69.5 | 16 | 16.6 | 16 | 17.8 | 17.2 | 16.3 | 18 | 18 | 16.9
217 | 10 | 627.9 | 251.16 | 293.5916 | 19.9 | 19.5 | 21.5 | 21.4 | 213.8 | 16.5 | 21.7 | 16.5 | 3.9 | 269.3 | 7.9 | 15.9 | 345.1 | 458.9 | 20.9 | 178 | 17.4 | 199.3 | 321.7 | 53.5 | 84 | 16.1 | 17.6 | 16 | 19.1 | 17.8 | 16.3 | 18.2 | 18.1 | 16.9
218 | 11 | 626.5 | 250.6 | 292.937 | 21 | 20.5 | 24.8 | 23.7 | 251.8 | 16.6 | 21.7 | 16.5 | 4.3 | 275.9 | 7.6 | 15.9 | 412 | 509.7 | 22.3 | 211.5 | 18.1 | 247.8 | 378 | 61.2 | 101.9 | 16.1 | 19.4 | 16 | 23 | 19.1 | 16.3 | 18.6 | 18.3 | 17
219 | 12 | 626.9 | 250.76 | 293.124 | 22.9 | 22.3 | 28.6 | 26.5 | 278.5 | 16.6 | 21.7 | 16.5 | 4 | 282.3 | 7.2 | 16 | 467.6 | 551.8 | 24 | 239.3 | 19 | 277.2 | 409.7 | 65.3 | 118.6 | 16.2 | 22.3 | 16 | 30.8 | 21.9 | 16.3 | 19 | 18.6 | 17.1
220 | 13 | 629.3 | 251.72 | 294.2462 | 26.2 | 24.8 | 32.7 | 28.9 | 323.1 | 16.6 | 21.7 | 16.5 | 3.8 | 265.7 | 6.4 | 16.1 | 528.6 | 592 | 25.8 | 269 | 19.9 | 326.2 | 465.8 | 70.8 | 135.1 | 16.3 | 25.4 | 16 | 38.9 | 24.6 | 16.3 | 19.4 | 18.8 | 17.3
221 | 14 | 631.6 | 252.64 | 295.3216 | 29.9 | 27.2 | 37.4 | 33.1 | 366 | 16.7 | 21.7 | 16.5 | 3.8 | 237.2 | 5.7 | 16.2 | 582.2 | 633.8 | 28.2 | 303.6 | 20.8 | 382.1 | 517.8 | 77.3 | 159.3 | 16.5 | 29.1 | 16 | 46.5 | 27.5 | 16.3 | 20 | 19.1 | 17.5
222 | 15 | 634 | 253.6 | 296.4438 | 33.8 | 29.9 | 42.9 | 38.3 | 424.6 | 16.7 | 21.7 | 16.5 | 4.2 | 232.3 | 5.4 | 16.3 | 628.3 | 671.7 | 31.1 | 335.2 | 21.8 | 429 | 562.8 | 81.3 | 183.6 | 16.7 | 33.4 | 16 | 53.7 | 31.4 | 16.3 | 20.6 | 19.3 | 17.7
223 | 16 | 633.7 | 253.48 | 296.3035 | 38.2 | 33.2 | 48.5 | 43.2 | 463.5 | 16.7 | 21.7 | 16.5 | 4.1 | 232.4 | 5.3 | 16.5 | 664.5 | 702.6 | 33.3 | 366.1 | 22.8 | 468.6 | 601.7 | 83.1 | 203.7 | 17 | 37.2 | 16 | 60 | 35.2 | 16.3 | 21.4 | 19.7 | 18
224 | 17 | 630.3 | 252.12 | 294.7138 | 43.8 | 37 | 54.9 | 46.6 | 492 | 16.8 | 21.7 | 16.6 | 3.7 | 242.7 | 5.4 | 16.7 | 698.1 | 730.9 | 36.9 | 389.5 | 23.9 | 506.7 | 640.4 | 87 | 222 | 17.3 | 41.8 | 16 | 66.7 | 38.9 | 16.3 | 22 | 20.1 | 18.2
225 | 18 | 624.1 | 249.64 | 291.8148 | 49.4 | 41.7 | 62.6 | 51.2 | 504.7 | 16.8 | 21.7 | 16.6 | 3.8 | 242.2 | 5.3 | 16.9 | 731.1 | 749.7 | 39.7 | 410.6 | 24.9 | 544.6 | 672.1 | 91 | 243.9 | 17.6 | 46.2 | 16 | 74.8 | 41.9 | 16.3 | 22.8 | 20.6 | 18.5
226 | 19 | 622.7 | 249.08 | 291.1602 | 54.9 | 47 | 68.3 | 56.4 | 514.6 | 16.9 | 21.7 | 16.7 | 3.9 | 243.5 | 5.3 | 17.2 | 757.3 | 763.5 | 41.7 | 428.7 | 26 | 585.4 | 702.9 | 94.6 | 262.8 | 18 | 50.5 | 16 | 82 | 47 | 16.3 | 23.4 | 21.2 | 18.8
227 | 20 | 604.8 | 241.92 | 282.7905 | 59.9 | 51.9 | 74.7 | 63.3 | 542.2 | 16.9 | 21.7 | 16.8 | 4.1 | 256.5 | 5.7 | 17.5 | 775.6 | 775.3 | 44 | 444.3 | 27 | 617 | 727.4 | 99.7 | 280.6 | 18.5 | 55.9 | 16 | 87.3 | 53.8 | 16.3 | 24.3 | 21.8 | 19.2
228 | 21 | 559.8 | 223.92 | 261.7496 | 65.5 | 57.2 | 81.6 | 69.7 | 568.5 | 17 | 21.7 | 17 | 4.2 | 249 | 6.2 | 17.9 | 792.3 | 790.4 | 46.5 | 462.9 | 28 | 646.5 | 750.5 | 107.5 | 300.4 | 18.9 | 61.7 | 16 | 95 | 58.8 | 16.3 | 25.3 | 22.3 | 19.5
229 | 22 | 516.3 | 206.52 | 241.41 | 70.7 | 63.4 | 88.8 | 75.4 | 596 | 17 | 21.7 | 17.1 | 4.2 | 249.2 | 7.3 | 18.2 | 805.9 | 794.7 | 48.8 | 475.7 | 29.1 | 667.1 | 766.3 | 111.3 | 319.3 | 19.4 | 67.3 | 16 | 101.9 | 63.4 | 16.3 | 26.2 | 22.9 | 19.8
230 | 23 | 492.3 | 196.92 | 230.1881 | 76.8 | 69.4 | 96.3 | 82 | 575.5 | 17 | 21.7 | 17.4 | 4 | 245.3 | 8 | 18.7 | 826.4 | 795.5 | 49.3 | 486.7 | 30.3 | 672.4 | 775.1 | 113.4 | 333.9 | 20 | 73 | 16 | 107.1 | 67.7 | 16.4 | 26.9 | 23.5 | 20.2
231 | 24 | 484.6 | 193.84 | 226.5878 | 82.3 | 75.3 | 103.8 | 87.8 | 563.5 | 17.1 | 21.7 | 17.8 | 3.6 | 260.3 | 8.7 | 19.1 | 839 | 792.4 | 50.4 | 497.6 | 31.6 | 676.5 | 784.2 | 117 | 349 | 20.6 | 78.6 | 16.1 | 112.7 | 73 | 16.4 | 27.7 | 24.1 | 20.5
232 | 25 | 485.1 | 194.04 | 226.8216 | 87.1 | 79.8 | 109.8 | 93.9 | 563.9 | 17.1 | 21.7 | 18.2 | 3.9 | 240.2 | 8.4 | 19.6 | 849.4 | 782.1 | 52.4 | 509.6 | 32.9 | 682.9 | 791 | 119.4 | 364.8 | 21.2 | 85 | 16.1 | 117.6 | 77.9 | 16.4 | 28.9 | 24.6 | 20.8
233 | 26 | 486.1 | 194.44 | 227.2892 | 92.3 | 83.6 | 115.8 | 100.5 | 552.3 | 17.1 | 21.7 | 18.7 | 3.6 | 261.2 | 9.2 | 20.1 | 857.3 | 771.8 | 54.2 | 518 | 34.2 | 678.6 | 793.1 | 122.3 | 377.6 | 21.8 | 90.2 | 16.1 | 124.4 | 81.8 | 16.4 | 29.8 | 25 | 21.1
234 | 27 | 488 | 195.2 | 228.1776 | 98 | 88 | 121.3 | 105.9 | 535.7 | 17.2 | 21.7 | 19.2 | 3.8 | 260.3 | 9.2 | 20.6 | 866 | 769.7 | 56.3 | 526.7 | 35.7 | 675.1 | 788.4 | 125 | 387 | 22.4 | 95.4 | 16.1 | 130.6 | 85.8 | 16.5 | 30.7 | 25.4 | 21.4
235 | 28 | 489 | 195.6 | 228.6451 | 103.4 | 92.6 | 126.6 | 111.1 | 510.7 | 17.2 | 21.7 | 19.8 | 3.8 | 248.4 | 9.1 | 21.2 | 876.5 | 765.4 | 59.3 | 539.2 | 37.1 | 659 | 776 | 126.4 | 395.2 | 23.1 | 100.2 | 16.1 | 133.9 | 89.7 | 16.5 | 31.7 | 25.8 | 21.7
236 | 29 | 489.4 | 195.76 | 228.8322 | 108.6 | 96.6 | 130.8 | 115.8 | 490.3 | 17.2 | 21.7 | 20.3 | 4.3 | 259.6 | 11.7 | 21.8 | 885.2 | 757.7 | 61.7 | 553.1 | 38.6 | 650.4 | 773.2 | 128.8 | 405.6 | 23.7 | 104.9 | 16.1 | 138.4 | 92.7 | 16.5 | 32.7 | 26.1 | 22
237 | 30 | 492.9 | 197.16 | 230.4687 | 112.5 | 99.5 | 135.5 | 120.1 | 474.7 | 17.3 | 21.7 | 20.9 | 4.5 | 270.4 | 12.7 | 22.4 | 890.4 | 778.4 | 64.3 | 560.6 | 40.2 | 644.2 | 774.4 | 130.9 | 413.5 | 24.3 | 109.5 | 16.2 | 143.6 | 95.9 | 16.6 | 33.6 | 26.4 | 22.3
238 | 31 | 491 | 196.4 | 229.5803 | 116.1 | 102.5 | 140 | 124.5 | 463.4 | 17.3 | 21.7 | 21.5 | 4.9 | 275.9 | 12 | 23 | 893.8 | 794 | 66.2 | 564 | 41.9 | 637.9 | 771.6 | 132.1 | 419.2 | 24.9 | 113.5 | 16.2 | 149.1 | 99.3 | 16.6 | 34.7 | 26.8 | 22.7
239 | 32 | 489.5 | 195.8 | 228.8789 | 120.7 | 105.8 | 143.4 | 128.8 | 451.1 | 17.4 | 21.7 | 22 | 4.8 | 265.4 | 11.8 | 23.7 | 897.2 | 797.1 | 68.6 | 570.9 | 43.6 | 626.4 | 763.8 | 132.8 | 424.8 | 25.5 | 117.7 | 16.2 | 153.2 | 103 | 16.6 | 35.8 | 27.1 | 23
240 | 33 | 487.9 | 195.16 | 228.1308 | 124.4 | 108.5 | 146.3 | 133.2 | 438.7 | 17.4 | 21.7 | 22.5 | 4.1 | 266 | 11.9 | 24.4 | 897.7 | 796.6 | 70.4 | 576.7 | 45.5 | 615.1 | 755.2 | 134.1 | 431.8 | 26.1 | 122.3 | 16.2 | 156.2 | 105.7 | 16.6 | 36.7 | 27.6 | 23.3
241 | 34 | 486.9 | 194.76 | 227.6632 | 126.2 | 111.8 | 149.9 | 136.7 | 428.9 | 17.5 | 21.7 | 22.9 | 4.1 | 264.3 | 11.4 | 25.1 | 898.2 | 795.8 | 72.4 | 577.7 | 47.5 | 608.1 | 757.8 | 136.6 | 435 | 26.8 | 125.9 | 16.3 | 158.6 | 109.3 | 16.6 | 37.4 | 28 | 23.6
242 | 35 | 486.5 | 194.6 | 227.4762 | 128.9 | 114.9 | 152.9 | 139.1 | 425.2 | 17.5 | 21.7 | 23.3 | 3.7 | 264.7 | 11.1 | 25.9 | 899.7 | 799 | 73.9 | 578.8 | 49.6 | 602.5 | 759.5 | 138.2 | 440.1 | 27.3 | 129 | 16.3 | 160.3 | 113.3 | 16.7 | 38.3 | 28.4 | 23.9
243 | 36 | 485.7 | 194.28 | 227.1021 | 131.3 | 118.1 | 155.2 | 141.3 | 424 | 17.5 | 21.7 | 23.8 | 3.5 | 271.4 | 10.9 | 26.6 | 904 | 807.2 | 76.9 | 580.5 | 51.8 | 602.9 | 769.1 | 140.7 | 446.9 | 27.9 | 131.4 | 16.3 | 161.8 | 116 | 16.7 | 39.1 | 28.8 | 24.1
244 | 37 | 486.4 | 194.56 | 227.4294 | 135.1 | 121.4 | 157 | 142.8 | 429.3 | 17.5 | 21.7 | 24.3 | 3.9 | 266.2 | 11 | 27.5 | 910 | 804.8 | 79.7 | 589.1 | 54.1 | 601 | 767.7 | 142.2 | 458 | 28.5 | 133.8 | 16.3 | 163.2 | 119.7 | 16.7 | 40 | 29.3 | 24.4
245 | 38 | 482.3 | 192.92 | 225.5124 | 137.9 | 124.3 | 158.8 | 144 | 425.8 | 17.6 | 21.7 | 24.7 | 4.2 | 269.5 | 11.7 | 28.3 | 913.8 | 812 | 83.1 | 594.3 | 56.4 | 598.5 | 770.2 | 144.3 | 462.4 | 29 | 136.1 | 16.4 | 163.9 | 123.1 | 16.7 | 40.8 | 29.7 | 24.6
246 | 39 | 482.4 | 192.96 | 225.5591 | 139.6 | 126.3 | 160.7 | 145.3 | 426.8 | 17.7 | 21.7 | 25.3 | 4.5 | 273.5 | 11.2 | 29.1 | 911.8 | 827.9 | 87.1 | 601.2 | 58.9 | 598.9 | 777.6 | 147.5 | 469.3 | 29.6 | 138 | 16.4 | 166.6 | 125.5 | 16.7 | 41.5 | 30.1 | 24.8
247 | 40 | 480.2 | 192.08 | 224.5305 | 142 | 128.8 | 162.5 | 147.2 | 438.7 | 17.8 | 21.7 | 25.8 | 4.6 | 260 | 11.5 | 30 | 912.1 | 827.7 | 90.7 | 604.4 | 61.6 | 602.3 | 785.5 | 149.9 | 476.1 | 30.1 | 140.5 | 16.4 | 167.9 | 128.1 | 16.7 | 42.2 | 30.5 | 25.1
248 | 41 | 480.7 | 192.28 | 224.7642 | 143.4 | 131.8 | 164.6 | 148.9 | 447.5 | 17.9 | 21.7 | 26.2 | 4.2 | 263.5 | 11.6 | 30.9 | 910 | 837.2 | 94.2 | 605.2 | 64.4 | 607.1 | 791.2 | 152.2 | 483.1 | 30.6 | 142.8 | 16.4 | 168.5 | 130.7 | 16.7 | 42.7 | 30.9 | 25.3
249 | 42 | 478.6 | 191.44 | 223.7823 | 144.6 | 134 | 166.9 | 149.9 | 463.4 | 18 | 21.7 | 26.6 | 4.2 | 265.1 | 11.9 | 31.8 | 908.9 | 836.7 | 97.3 | 605.5 | 67.3 | 611 | 788.1 | 154.3 | 490.7 | 31.2 | 145.2 | 16.5 | 169.6 | 133 | 16.8 | 43.2 | 31.3 | 25.5
250 | 43 | 476.6 | 190.64 | 222.8472 | 145.3 | 135.7 | 168.9 | 151.5 | 461.3 | 18 | 21.7 | 27 | 3.9 | 260.3 | 12.3 | 32.8 | 910.5 | 837 | 99.7 | 608.4 | 70.3 | 608 | 779.8 | 155.5 | 494.7 | 31.7 | 147.4 | 16.5 | 170.6 | 135.1 | 16.8 | 43.8 | 31.6 | 25.8
251 | 44 | 476.4 | 190.56 | 222.7537 | 146.5 | 137.5 | 170.2 | 153.1 | 453.5 | 18 | 21.7 | 27.3 | 4.3 | 261.3 | 12.7 | 33.8 | 913.7 | 830.5 | 101.7 | 613 | 74.5 | 604.4 | 774.5 | 156.6 | 501.3 | 32.2 | 149.7 | 16.6 | 171 | 136.6 | 16.8 | 44.6 | 32 | 26.1
252 | 45 | 476.5 | 190.6 | 222.8004 | 148.1 | 138.3 | 171.9 | 154.9 | 445.4 | 18 | 21.7 | 27.6 | 4.1 | 265.2 | 12.3 | 34.7 | 914.6 | 826.4 | 103.1 | 617.4 | 78.7 | 598.9 | 764.4 | 157.3 | 505.3 | 32.8 | 151.3 | 16.6 | 172 | 139 | 16.8 | 45.2 | 32.4 | 26.3
253 | 46 | 475.6 | 190.24 | 222.3796 | 149.3 | 138.7 | 173.1 | 156 | 449.3 | 18 | 21.7 | 27.9 | 4.2 | 265.5 | 10.2 | 35.7 | 910.2 | 836.9 | 105 | 617.4 | 82.1 | 602.2 | 768.8 | 158.9 | 510.4 | 33.3 | 152.8 | 16.6 | 172.5 | 141.6 | 16.8 | 45.9 | 32.9 | 26.6
254 | 47 | 474.7 | 189.88 | 221.9588 | 151.2 | 140.3 | 174.2 | 156.6 | 448.8 | 18.1 | 21.6 | 28.2 | 3.5 | 267.9 | 8.9 | 36.7 | 901.8 | 830.7 | 105.5 | 616 | 85.2 | 597.4 | 762.8 | 159.7 | 511.8 | 33.8 | 154.4 | 16.7 | 173.3 | 144.2 | 16.8 | 46.8 | 33.3 | 26.9
255 | 48 | 474.9 | 189.96 | 222.0523 | 153.1 | 141.8 | 175.1 | 157.3 | 436.8 | 18.2 | 21.6 | 28.5 | 3.5 | 263.1 | 8.9 | 37.7 | 901.3 | 826.5 | 106.7 | 612.5 | 88.4 | 583.4 | 749.3 | 159.8 | 513.8 | 34.3 | 156 | 16.7 | 173.9 | 146 | 16.8 | 47.4 | 33.7 | 27.2
256 | 49 | 473.6 | 189.44 | 221.4444 | 155.6 | 143.3 | 175.6 | 158.1 | 425.4 | 18.3 | 21.6 | 28.8 | 3.6 | 261.3 | 8.9 | 38.7 | 907.1 | 822.7 | 108.5 | 615.2 | 91.7 | 578.3 | 744.3 | 160 | 517.7 | 34.8 | 157.4 | 16.8 | 174.9 | 147.4 | 16.8 | 48 | 34.1 | 27.4
257 | 50 | 472 | 188.8 | 220.6963 | 158.3 | 143.5 | 176.2 | 159.3 | 424.3 | 18.4 | 21.6 | 29.1 | 3.4 | 261.6 | 8.8 | 39.6 | 915.9 | 825.8 | 109.3 | 620.9 | 95 | 580.1 | 754.2 | 161.2 | 521.5 | 35.3 | 158.7 | 16.8 | 176.4 | 149 | 16.8 | 48.6 | 34.4 | 27.7
258 | 51 | 472.6 | 189.04 | 220.9769 | 160.8 | 143.9 | 176.4 | 160.2 | 433.4 | 18.4 | 21.6 | 29.4 | 3.8 | 274.1 | 8.9 | 40.6 | 918.1 | 818.8 | 110.4 | 626 | 98.4 | 584.3 | 756.6 | 162.9 | 528.3 | 35.8 | 160.6 | 16.8 | 178 | 150.2 | 16.8 | 49.1 | 34.8 | 28
259 | 52 | 473.4 | 189.36 | 221.3509 | 162 | 144.3 | 176.7 | 160.9 | 435.6 | 18.4 | 21.6 | 29.6 | 4.1 | 266.7 | 9.2 | 41.6 | 914.4 | 812.3 | 110.7 | 621.6 | 101.8 | 578.3 | 758.8 | 164.1 | 532.8 | 36.2 | 162.4 | 16.9 | 179.1 | 151.3 | 16.8 | 49.7 | 35.2 | 28.2
260 | 53 | 471.1 | 188.44 | 220.2755 | 163.3 | 144.8 | 178.5 | 161.8 | 429.2 | 18.4 | 21.6 | 29.9 | 4.1 | 269.7 | 8.8 | 42.6 | 912.5 | 813.9 | 112.7 | 619.2 | 105.1 | 578.7 | 761.1 | 165.3 | 537.9 | 36.7 | 163.9 | 16.9 | 179.6 | 153 | 16.8 | 50.5 | 35.6 | 28.5
261 | 54 | 469.2 | 187.68 | 219.3871 | 163.2 | 145.1 | 180.2 | 162.7 | 424.7 | 18.3 | 21.6 | 30.2 | 4.3 | 269.5 | 8.5 | 43.7 | 918.3 | 823.8 | 115.4 | 626.2 | 108.8 | 574.9 | 754.7 | 166.5 | 541 | 37.2 | 165.2 | 17 | 180.5 | 154.7 | 16.8 | 51.2 | 35.9 | 28.8
262 | 55 | 469.3 | 187.72 | 219.4339 | 162.8 | 145.6 | 180.7 | 163.3 | 417.2 | 18.3 | 21.6 | 30.5 | 3.8 | 267.4 | 8.9 | 44.8 | 916.7 | 820.5 | 120 | 635.7 | 113.6 | 574.3 | 743.7 | 167.4 | 546.5 | 37.6 | 166.5 | 17 | 182 | 155.3 | 16.8 | 51.8 | 36.3 | 29
263 | 56 | 469.7 | 187.88 | 219.6209 | 162.7 | 147.1 | 181.4 | 163.9 | 411.2 | 18.3 | 21.6 | 30.8 | 3.7 | 274.8 | 7.8 | 45.9 | 919.1 | 824.3 | 124.7 | 644.2 | 119 | 574.4 | 746.7 | 168.7 | 550.4 | 38.1 | 167.7 | 17.1 | 183.7 | 155.5 | 16.8 | 52.2 | 36.7 | 29.3
264 | 57 | 469.4 | 187.76 | 219.4806 | 162.8 | 148.1 | 182 | 164.3 | 410.1 | 18.4 | 21.6 | 31 | 4 | 263.2 | 7.5 | 47 | 919.5 | 827.8 | 130.4 | 650.4 | 123.9 | 572.8 | 739.8 | 169.9 | 556.6 | 38.6 | 168.6 | 17.1 | 184.7 | 156.5 | 16.8 | 52.8 | 37.1 | 29.6
265 | 58 | 469.5 | 187.8 | 219.5274 | 163.6 | 148.7 | 181.7 | 165.2 | 409.4 | 18.4 | 21.6 | 31.4 | 3.7 | 263.7 | 7.8 | 48.2 | 913.4 | 827.3 | 137.5 | 654.9 | 128.4 | 573.7 | 729.4 | 171 | 562.6 | 39 | 169.5 | 17.2 | 185.4 | 157.6 | 16.9 | 53.4 | 37.6 | 29.9
266 | 59 | 470.5 | 188.2 | 219.995 | 164.8 | 148.4 | 181.7 | 165.9 | 410.2 | 18.4 | 21.6 | 31.7 | 4 | 265.1 | 7.7 | 49.3 | 914.8 | 829.3 | 143.2 | 656.2 | 133.1 | 574.3 | 719.3 | 171.9 | 567.8 | 39.5 | 170.4 | 17.2 | 186 | 159.3 | 16.9 | 54.2 | 38.1 | 30.1
267 | 60 | 470.6 | 188.24 | 220.0417 | 166.4 | 148.3 | 182.3 | 166.6 | 414.9 | 18.4 | 21.6 | 32.1 | 4.5 | 271.7 | 8.4 | 50.5 | 917.8 | 812.6 | 148.1 | 663.9 | 138 | 570.1 | 707.6 | 172.4 | 572.6 | 40 | 171.6 | 17.3 | 186.3 | 160.8 | 16.9 | 54.7 | 38.5 | 30.4
268 | 61 | 470.5 | 188.2 | 219.995 | 167.2 | 148.1 | 182.3 | 167.1 | 404.3 | 18.5 | 21.6 | 32.5 | 4.3 | 267.1 | 8.5 | 51.9 | 913.4 | 806 | 152.9 | 667.9 | 142.6 | 558.9 | 695.3 | 172.6 | 573.7 | 40.4 | 172.5 | 17.3 | 186.5 | 161.7 | 16.9 | 55.3 | 39 | 30.6
269 | 62 | 469.9 | 187.96 | 219.7144 | 167.1 | 147.6 | 183.4 | 167.2 | 391.7 | 18.5 | 21.6 | 32.7 | 4.2 | 264.8 | 8.7 | 53.4 | 915.2 | 794.6 | 156.9 | 669.8 | 147.1 | 552.1 | 679.8 | 173 | 576 | 40.9 | 173.2 | 17.4 | 187 | 162.5 | 16.9 | 55.9 | 39.4 | 30.9
270 | 63 | 470 | 188 | 219.7612 | 167.6 | 147.6 | 184.7 | 166.9 | 391.4 | 18.6 | 21.6 | 32.9 | 4.1 | 264.3 | 9.4 | 54.9 | 917.8 | 779.6 | 162.8 | 673 | 151.8 | 546.9 | 664.5 | 173.1 | 578.8 | 41.3 | 174 | 17.5 | 188.5 | 163.6 | 16.9 | 56.4 | 39.7 | 31.1
271 | 64 | 469.9 | 187.96 | 219.7144 | 168.2 | 146.9 | 185.9 | 167.5 | 396.5 | 18.7 | 21.6 | 33.2 | 3.9 | 262.5 | 9.5 | 56.3 | 920.7 | 784.6 | 171.7 | 684 | 156.3 | 546.8 | 660.2 | 173.9 | 583.6 | 41.7 | 175 | 17.5 | 189.1 | 164.7 | 17 | 57.1 | 40.1 | 31.3
272 | 65 | 467.4 | 186.96 | 218.5455 | 168 | 146.9 | 186.7 | 168.3 | 394.9 | 18.7 | 21.6 | 33.4 | 3.7 | 261.6 | 8.8 | 57.9 | 919.4 | 797.7 | 178.8 | 691.6 | 160.5 | 551.1 | 676.4 | 175.6 | 587.5 | 42.1 | 175.8 | 17.6 | 189.7 | 165.6 | 17 | 57.6 | 40.6 | 31.6
273 | 66 | 467.3 | 186.92 | 218.4987 | 168.1 | 148 | 187.5 | 168.4 | 402.7 | 18.8 | 21.6 | 33.6 | 4.2 | 249.8 | 9.5 | 59.3 | 916.2 | 809.9 | 187.9 | 701.6 | 164.4 | 555.7 | 683 | 177 | 593 | 42.5 | 176.5 | 17.6 | 190.2 | 166.2 | 17 | 58 | 41 | 31.8
274 | 67 | 466.9 | 186.76 | 218.3117 | 168.3 | 149.7 | 188 | 167.3 | 408.1 | 18.8 | 21.6 | 33.8 | 4.9 | 258 | 10.1 | 60.9 | 922.2 | 820.2 | 193.1 | 703.2 | 168.1 | 564.3 | 699.6 | 179.1 | 599.1 | 42.9 | 177.2 | 17.7 | 191.1 | 166.6 | 17 | 58.5 | 41.5 | 32
275 | 68 | 466.5 | 186.6 | 218.1246 | 169.5 | 150.2 | 188.1 | 167.4 | 409.3 | 18.9 | 21.6 | 34.1 | 4.3 | 246.9 | 10.2 | 62.6 | 925.3 | 818 | 196.4 | 704.9 | 171.5 | 562 | 705 | 180.6 | 601.5 | 43.3 | 177.9 | 17.7 | 191.9 | 167 | 17 | 59 | 41.9 | 32.3
276 | 69 | 466.6 | 186.64 | 218.1714 | 170.8 | 150.7 | 189 | 168.3 | 405.6 | 18.9 | 21.6 | 34.3 | 4.1 | 246.8 | 10.5 | 64.7 | 916 | 802.7 | 199.2 | 699 | 174.9 | 552.8 | 692.8 | 181.2 | 601 | 43.7 | 178.5 | 17.8 | 192.5 | 167.3 | 17.1 | 59.4 | 42.4 | 32.5
277 | 70 | 467.2 | 186.88 | 218.452 | 171.9 | 151.1 | 189.1 | 168.5 | 397.2 | 18.9 | 21.5 | 34.5 | 3.9 | 254.5 | 10.5 | 67 | 907.2 | 784.2 | 203 | 695.8 | 178.2 | 543.8 | 685.7 | 181.6 | 599.5 | 44.1 | 179.8 | 17.9 | 192.6 | 167.5 | 17.1 | 60 | 42.8 | 32.8
278 | 71 | 467.1 | 186.84 | 218.4052 | 173.4 | 152.4 | 189 | 169 | 388.2 | 18.9 | 21.5 | 34.6 | 3.6 | 248.8 | 10.9 | 68.8 | 899.4 | 770.1 | 206.2 | 698.9 | 181.3 | 535.1 | 672.6 | 181.8 | 600.6 | 44.5 | 180.2 | 17.9 | 191.7 | 168 | 17.1 | 60.5 | 43.2 | 33
279 | 72 | 467.4 | 186.96 | 218.5455 | 175.4 | 152.1 | 189 | 169.7 | 387.2 | 18.9 | 21.5 | 34.8 | 3.9 | 248.5 | 11.2 | 70.6 | 906.2 | 778.7 | 211.6 | 707.9 | 184.1 | 539.3 | 680.8 | 183 | 604.4 | 44.9 | 180.5 | 18 | 191.4 | 168.4 | 17.1 | 61 | 43.6 | 33.2
280 | 73 | 468.5 | 187.4 | 219.0598 | 175.4 | 151.4 | 188.7 | 170 | 399 | 19 | 21.5 | 35 | 4 | 247.6 | 10.4 | 72.5 | 916.2 | 791 | 217.9 | 714.5 | 186.8 | 546.1 | 690.4 | 184.9 | 608.6 | 45.3 | 180.9 | 18 | 191.2 | 168.7 | 17.1 | 61.5 | 43.9 | 33.5
281 | 74 | 469.4 | 187.76 | 219.4806 | 175.3 | 151.4 | 189.2 | 170.4 | 407.6 | 19 | 21.5 | 35.3 | 4.2 | 247.6 | 10.1 | 74.6 | 920.3 | 807.8 | 223.2 | 717.4 | 189.5 | 557.9 | 706.6 | 187.1 | 614.6 | 45.7 | 181.2 | 18.1 | 191.2 | 169 | 17.2 | 62 | 44.4 | 33.7
282 | 75 | 469.5 | 187.8 | 219.5274 | 176.3 | 152.1 | 190.1 | 171 | 426.1 | 19.1 | 21.5 | 35.6 | 4.1 | 253 | 10.1 | 76.2 | 925.5 | 813.3 | 226 | 722.3 | 192.1 | 570.5 | 724.3 | 189.4 | 619 | 46.1 | 181.8 | 18.2 | 190.7 | 169.4 | 17.2 | 62.4 | 44.8 | 34
283 | 76 | 469.4 | 187.76 | 219.4806 | 177 | 152.5 | 191 | 171.8 | 443.7 | 19.2 | 21.5 | 35.9 | 3.9 | 245.1 | 9.8 | 77.8 | 927 | 818.6 | 226.8 | 719.8 | 194.7 | 572.6 | 725.9 | 191.2 | 619.7 | 46.5 | 182.1 | 18.3 | 190.3 | 169.7 | 17.2 | 62.9 | 45.3 | 34.2
284 | 77 | 468 | 187.2 | 218.826 | 177.4 | 153.1 | 191.4 | 172.3 | 440.9 | 19.3 | 21.5 | 36.1 | 3.7 | 251.3 | 9.8 | 79.5 | 922.9 | 824.2 | 232.4 | 719.9 | 197.2 | 570.1 | 722 | 192.2 | 621.2 | 46.9 | 182.4 | 18.3 | 190.2 | 170.7 | 17.3 | 63.4 | 45.8 | 34.5
285 | 78 | 465 | 186 | 217.4233 | 177.7 | 153.9 | 191.1 | 172.5 | 438.6 | 19.4 | 21.5 | 36.3 | 4.1 | 246.2 | 10.6 | 81.2 | 922.7 | 824.1 | 239.7 | 721 | 199.6 | 572.6 | 719.7 | 193 | 623.3 | 47.3 | 182.7 | 18.4 | 190.2 | 171.4 | 17.3 | 63.8 | 46.3 | 34.7
286 | 79 | 466.7 | 186.68 | 218.2182 | 178 | 154.6 | 191.2 | 172.7 | 437.2 | 19.4 | 21.5 | 36.5 | 4.3 | 271.2 | 9.7 | 82.9 | 920.9 | 824.5 | 245.3 | 717 | 202.1 | 572.1 | 717.8 | 193.6 | 624.1 | 47.7 | 183 | 18.5 | 190.2 | 171.9 | 17.3 | 64.3 | 46.8 | 35
287 | 80 | 466 | 186.4 | 217.8909 | 178.2 | 155.6 | 191.7 | 172.4 | 428.4 | 19.5 | 21.5 | 36.6 | 4 | 258.9 | 8.6 | 84.7 | 912.9 | 827.2 | 249.6 | 710.8 | 204.6 | 563.2 | 705.2 | 193.6 | 622.2 | 48.2 | 183.4 | 18.5 | 190.7 | 172.3 | 17.4 | 64.9 | 47.4 | 35.2
288 | 81 | 465.9 | 186.36 | 217.8441 | 178.8 | 156.7 | 192.2 | 172.5 | 416.3 | 19.5 | 21.5 | 36.7 | 3.6 | 259.4 | 7.8 | 86.5 | 909.5 | 841.5 | 256 | 711 | 206.9 | 558.6 | 702.3 | 193.7 | 624.3 | 48.6 | 183.7 | 18.6 | 190.4 | 173.3 | 17.4 | 65.3 | 47.8 | 35.4
289 | 82 | 467.5 | 187 | 218.5922 | 178.9 | 156.9 | 192.4 | 172.5 | 421.2 | 19.5 | 21.5 | 36.9 | 3.8 | 246.5 | 7.8 | 88.4 | 910.3 | 850.5 | 262.3 | 712.2 | 209.2 | 564.5 | 715.7 | 194.5 | 626.2 | 49 | 184.5 | 18.7 | 190.1 | 173.8 | 17.4 | 65.7 | 48.3 | 35.6
290 | 83 | 466.9 | 186.76 | 218.3117 | 178.8 | 157.4 | 192.9 | 172.5 | 428.2 | 19.6 | 21.5 | 37 | 4 | 256.7 | 8.2 | 90.3 | 912.2 | 849.1 | 267.8 | 711.2 | 211.5 | 569.2 | 722.8 | 195.5 | 628.9 | 49.4 | 184.9 | 18.7 | 191.2 | 174.2 | 17.5 | 66.1 | 48.8 | 35.9
291 | 84 | 464.8 | 185.92 | 217.3298 | 179 | 158 | 193.2 | 172.4 | 426.7 | 19.6 | 21.5 | 37.1 | 3.9 | 260.3 | 8 | 92.3 | 911 | 848 | 272.2 | 709.2 | 213.8 | 563.1 | 714.6 | 195.7 | 626.2 | 49.8 | 185.5 | 18.8 | 191.9 | 174.2 | 17.5 | 66.5 | 49.3 | 36.1
292 | 85 | 464 | 185.6 | 216.9557 | 179.2 | 158.8 | 194 | 171.9 | 424 | 19.7 | 21.5 | 37.3 | 4.1 | 257.2 | 7.6 | 94.4 | 907.3 | 837.8 | 275.5 | 711 | 216.1 | 561.6 | 701.5 | 195.7 | 628.2 | 50.2 | 186.1 | 18.9 | 192.2 | 174.5 | 17.6 | 66.9 | 49.9 | 36.3
293 | 86 | 464 | 185.6 | 216.9557 | 179 | 159.9 | 194.4 | 171.8 | 429.7 | 19.8 | 21.5 | 37.5 | 4.3 | 261.5 | 7.3 | 96.6 | 910.6 | 830.5 | 280.5 | 715.4 | 218.2 | 563.1 | 686 | 195.8 | 631.1 | 50.5 | 186.4 | 19 | 192.1 | 174.9 | 17.6 | 67.4 | 50.4 | 36.5
294 | 87 | 464.6 | 185.84 | 217.2363 | 178.7 | 161.1 | 194.8 | 171.6 | 426.3 | 19.8 | 21.5 | 37.6 | 4.5 | 253.5 | 6.6 | 99 | 904.8 | 824 | 286.2 | 724.5 | 220.1 | 558.6 | 671.4 | 195.7 | 633 | 50.9 | 186.8 | 19 | 191.8 | 175.1 | 17.6 | 67.8 | 51 | 36.7
295 | 88 | 464.9 | 185.96 | 217.3765 | 179.9 | 161.4 | 194.8 | 171.5 | 416.1 | 19.9 | 21.4 | 37.8 | 5.1 | 243 | 6.1 | 101.3 | 904 | 824.9 | 292.5 | 729.4 | 221.7 | 552.9 | 670.1 | 195.6 | 633.7 | 51.3 | 186.8 | 19.1 | 191.6 | 175.3 | 17.7 | 68.3 | 51.5 | 36.9
296 | 89 | 465.6 | 186.24 | 217.7038 | 179.4 | 162 | 195.3 | 171.5 | 409.4 | 19.9 | 21.4 | 37.9 | 4.8 | 261 | 6.2 | 103.7 | 903.8 | 819.8 | 294.5 | 738.2 | 223.1 | 548.8 | 666.8 | 195.9 | 635.1 | 51.6 | 186.9 | 19.2 | 192.1 | 175.8 | 17.7 | 68.7 | 51.9 | 37.1
297 | 90 | 466.8 | 186.72 | 218.2649 | 179.1 | 162 | 195.6 | 171.6 | 400.8 | 19.9 | 21.4 | 38.1 | 4.3 | 260.2 | 6 | 106.1 | 902.5 | 816.6 | 297 | 738.3 | 224.5 | 544.2 | 669.1 | 196.3 | 636.5 | 52 | 186.9 | 19.3 | 192.6 | 176.2 | 17.8 | 69.3 | 52.3 | 37.4
298 | 91 | 467.3 | 186.92 | 218.4987 | 178.8 | 161.9 | 196.1 | 171.8 | 393.9 | 19.9 | 21.4 | 38.3 | 4.5 | 242.8 | 5.8 | 108.5 | 899.6 | 808.8 | 299.3 | 735.3 | 225.8 | 540.1 | 665.3 | 196.8 | 636.5 | 52.4 | 187.2 | 19.3 | 192.7 | 176.3 | 17.8 | 69.6 | 52.8 | 37.6
299 | 92 | 467.3 | 186.92 | 218.4987 | 179 | 161.4 | 196.8 | 171.9 | 389.3 | 20 | 21.4 | 38.5 | 4.1 | 277.9 | 5.8 | 111 | 891.8 | 797.6 | 299.4 | 734.4 | 227 | 537.3 | 660.1 | 197.3 | 636.1 | 52.7 | 187.7 | 19.4 | 192.6 | 177.1 | 17.9 | 70 | 53.2 | 37.8
300 | 93 | 466.2 | 186.48 | 217.9844 | 180.3 | 161.2 | 197.5 | 171.9 | 384.4 | 20 | 21.4 | 38.7 | 3.7 | 259 | 5.8 | 113.6 | 896.2 | 810.2 | 299.7 | 738.2 | 228.2 | 536 | 653.3 | 197.9 | 637.9 | 53.1 | 187.8 | 19.5 | 193 | 177.8 | 17.9 | 70.4 | 53.6 | 38
301 | 94 | 466.2 | 186.48 | 217.9844 | 180.3 | 161.5 | 197.8 | 172.2 | 383.5 | 20.1 | 21.4 | 38.9 | 4.1 | 256.2 | 7 | 116.2 | 893.5 | 826.5 | 299.4 | 733.2 | 229.4 | 544.7 | 671.2 | 199.4 | 640.3 | 53.4 | 188 | 19.6 | 193.3 | 178 | 18 | 70.8 | 54 | 38.2
302 | 95 | 466.8 | 186.72 | 218.2649 | 180.1 | 162 | 197.8 | 172.9 | 394.8 | 20.2 | 21.4 | 39 | 3.8 | 284.2 | 7 | 118.8 | 885.5 | 822 | 299.4 | 723.8 | 230.3 | 546.8 | 680.9 | 200.9 | 639.5 | 53.8 | 188.7 | 19.7 | 193.3 | 178.7 | 18 | 71.2 | 54.5 | 38.4
303 | 96 | 466.8 | 186.72 | 218.2649 | 180 | 162.9 | 198.2 | 173.2 | 399.4 | 20.2 | 21.4 | 39.1 | 3.3 | 258.3 | 7.1 | 121.5 | 881.3 | 828.1 | 297.8 | 722.4 | 231.1 | 544 | 688.5 | 201.9 | 639 | 54.2 | 189 | 19.8 | 193.5 | 179.8 | 18.1 | 71.6 | 54.9 | 38.7
304 | 97 | 466.9 | 186.76 | 218.3117 | 180.4 | 162.5 | 198.2 | 173.3 | 399.5 | 20.2 | 21.4 | 39.3 | 3.3 | 271.4 | 8.1 | 124.1 | 888.6 | 825.9 | 297.2 | 727.4 | 232 | 544.8 | 681.4 | 202.8 | 640.6 | 54.5 | 189.2 | 19.8 | 193.2 | 180.2 | 18.1 | 72 | 55.3 | 38.9
305 | 98 | 467.3 | 186.92 | 218.4987 | 181.1 | 162.9 | 197.9 | 173.5 | 397.7 | 20.3 | 21.4 | 39.4 | 3.3 | 266 | 8.7 | 126.7 | 891.6 | 831.5 | 296.6 | 735.8 | 232.8 | 543.9 | 674.5 | 203.3 | 642.8 | 54.9 | 189.8 | 19.9 | 193 | 181.1 | 18.2 | 72.5 | 55.8 | 39.2
306 | 99 | 466.5 | 186.6 | 218.1246 | 181.8 | 162.8 | 197.6 | 174.1 | 393.7 | 20.3 | 21.4 | 39.5 | 3.3 | 271.5 | 9.8 | 129.2 | 892.9 | 835.6 | 295 | 738.9 | 233.5 | 542.9 | 673.2 | 204.2 | 645.4 | 55.2 | 190.1 | 20 | 194 | 182.4 | 18.2 | 73 | 56.2 | 39.4
307 | 100 | 469 | 187.6 | 219.2936 | 182.2 | 163 | 197.7 | 174.5 | 391.3 | 20.4 | 21.4 | 39.7 | 3.3 | 262.6 | 10.1 | 131.7 | 893.4 | 830.6 | 292.8 | 731.8 | 234 | 543.6 | 677.9 | 205 | 643.7 | 55.6 | 190.6 | 20.1 | 195.2 | 183.2 | 18.3 | 73.4 | 56.7 | 39.6
308 | 101 | 469.4 | 187.76 | 219.4806 | 182.5 | 163 | 197.8 | 175.1 | 396.1 | 20.5 | 21.4 | 39.8 | 4 | 260.8 | 9.4 | 134.2 | 885.2 | 816.4 | 291.5 | 728.4 | 234.9 | 543.6 | 666.6 | 205.6 | 640.1 | 55.9 | 190.6 | 20.2 | 195.7 | 183.5 | 18.3 | 73.9 | 57.2 | 39.8
309 | 102 | 468.8 | 187.52 | 219.2001 | 182.4 | 163.5 | 197.2 | 176.2 | 396.4 | 20.5 | 21.4 | 39.9 | 3.6 | 268.2 | 8.9 | 136.7 | 882.1 | 825.9 | 290.8 | 728.7 | 235.8 | 545.4 | 675.7 | 206.6 | 641.9 | 56.3 | 190.7 | 20.3 | 195.9 | 184.4 | 18.4 | 74.4 | 57.7 | 40.1
310 | 103 | 467.9 | 187.16 | 218.7793 | 182.8 | 163.6 | 196.9 | 177 | 402.9 | 20.5 | 21.4 | 40.1 | 4.1 | 260.4 | 8.4 | 139.1 | 883.2 | 825.2 | 290.3 | 728.9 | 236.8 | 550 | 679.3 | 207.9 | 642.4 | 56.7 | 191.3 | 20.4 | 196.6 | 184.9 | 18.5 | 74.8 | 58.3 | 40.3
311 | 104 | 467.9 | 187.16 | 218.7793 | 183.3 | 165.2 | 196.8 | 176.3 | 412.9 | 20.6 | 21.4 | 40.2 | 4.4 | 253.7 | 8.5 | 141.5 | 880.6 | 825.2 | 289.7 | 729.7 | 237.9 | 552.6 | 679.9 | 208.9 | 642.2 | 57 | 191.6 | 20.4 | 197.2 | 185 | 18.5 | 75.1 | 58.8 | 40.6
312 | 105 | 467.8 | 187.12 | 218.7325 | 183.5 | 166.4 | 196.4 | 176.4 | 412.9 | 20.7 | 21.4 | 40.4 | 4.5 | 277 | 9.1 | 143.9 | 875.3 | 830.3 | 289.6 | 723.4 | 238.8 | 553.9 | 687.9 | 209.9 | 641 | 57.3 | 191.7 | 20.5 | 197.6 | 185.6 | 18.6 | 75.5 | 59.4 | 40.8
313 | 106 | 467.8 | 187.12 | 218.7325 | 183.6 | 167.5 | 195.6 | 176.6 | 411.5 | 20.8 | 21.4 | 40.6 | 4.4 | 266.3 | 8.9 | 146.3 | 876 | 806.1 | 290 | 725.7 | 239.9 | 555.1 | 680.6 | 210.7 | 641.6 | 57.7 | 192.1 | 20.6 | 198.2 | 186.2 | 18.6 | 76 | 60 | 41
314 | 107 | 469.1 | 187.64 | 219.3403 | 183.4 | 167.9 | 195.7 | 176 | 409.5 | 20.8 | 21.4 | 40.9 | 4.3 | 271.1 | 8.6 | 148.7 | 879.6 | 804.1 | 289.2 | 730.6 | 240.9 | 555.7 | 669.1 | 211.4 | 645 | 58 | 192.5 | 20.7 | 198 | 186.5 | 18.7 | 76.4 | 60.6 | 41.2
315 | 108 | 468.4 | 187.36 | 219.013 | 182.8 | 169 | 195 | 175.7 | 405.8 | 20.9 | 21.4 | 41.1 | 4 | 266.9 | 8.1 | 150.9 | 880.6 | 807.6 | 286.6 | 740.1 | 241.6 | 556.1 | 674.2 | 212.3 | 647.1 | 58.4 | 192.4 | 20.8 | 198.1 | 187.3 | 18.7 | 76.9 | 61.2 | 41.4
316 | 109 | 470 | 188 | 219.7612 | 181.9 | 170.2 | 194.3 | 176.2 | 408 | 20.9 | 21.3 | 41.3 | 4.1 | 255.8 | 8.3 | 153.2 | 880.1 | 823.1 | 284.8 | 739 | 242.4 | 564.4 | 682.8 | 213.8 | 650.1 | 58.7 | 192.6 | 20.9 | 198.3 | 187.7 | 18.8 | 77.2 | 61.7 | 41.7
317 | 110 | 467.4 | 186.96 | 218.5455 | 181.3 | 171.2 | 194.2 | 176.8 | 418.2 | 20.9 | 21.3 | 41.5 | 4.3 | 260.1 | 8.7 | 155.4 | 874.2 | 828.5 | 285 | 732.6 | 243.5 | 566.8 | 694.3 | 215.2 | 648.4 | 59 | 192.8 | 21 | 199.7 | 187.9 | 18.9 | 77.6 | 62.2 | 41.9
318 | 111 | 466.5 | 186.6 | 218.1246 | 182.8 | 172.9 | 195 | 177.1 | 420.3 | 20.9 | 21.4 | 41.6 | 4.2 | 262.6 | 9.3 | 157.5 | 860.1 | 822.9 | 283.7 | 725.3 | 245 | 562.3 | 701 | 216.3 | 645.7 | 59.3 | 193 | 21.1 | 199.8 | 187.9 | 18.9 | 78 | 62.7 | 42.1
319 | 112 | 467.2 | 186.88 | 218.452 | 184.5 | 174 | 195.8 | 177.5 | 423.5 | 21 | 21.3 | 41.8 | 4.2 | 253.9 | 8.9 | 159.6 | 854.1 | 819.2 | 283.4 | 730.2 | 246.5 | 557.6 | 695.8 | 217.1 | 643.9 | 59.6 | 193.1 | 21.2 | 199.6 | 188.1 | 19 | 78.2 | 63.2 | 42.3
320 | 113 | 467.1 | 186.84 | 218.4052 | 184.1 | 175.1 | 196 | 178.2 | 412.6 | 21 | 21.3 | 41.9 | 3.6 | 244.6 | 8.6 | 161.6 | 851.4 | 808.8 | 283.5 | 736.4 | 247.9 | 552.2 | 680.7 | 217.4 | 647.2 | 59.9 | 193.4 | 21.2 | 199.5 | 188.8 | 19.1 | 78.6 | 63.6 | 42.6
321 | 114 | 467.5 | 187 | 218.5922 | 183.2 | 175.8 | 195.3 | 178.6 | 404.4 | 21 | 21.3 | 41.9 | 3.3 | 253.6 | 8.4 | 163.6 | 850.7 | 797.3 | 283.5 | 739.4 | 249.1 | 545 | 669.5 | 217.8 | 646.8 | 60.3 | 193.8 | 21.3 | 198.9 | 189.3 | 19.2 | 79 | 63.9 | 42.8
322 | 115 | 468 | 187.2 | 218.826 | 184.5 | 176.1 | 194.6 | 178 | 401.4 | 21 | 21.3 | 42 | 3.8 | 244.1 | 8.5 | 165.6 | 851.5 | 797.7 | 283.3 | 742.3 | 250.2 | 543.3 | 658.5 | 218.1 | 648.2 | 60.6 | 194.1 | 21.4 | 198.5 | 189.2 | 19.2 | 79.3 | 64.4 | 43.1
323 | 116 | 468.5 | 187.4 | 219.0598 | 186.3 | 175.9 | 194.9 | 178 | 405.4 | 21.1 | 21.3 | 42.2 | 4.2 | 256.5 | 7.7 | 167.5 | 850.4 | 815.2 | 281.2 | 747.2 | 251.4 | 547.8 | 661.8 | 219.3 | 651 | 60.9 | 194.4 | 21.5 | 197.8 | 188.7 | 19.3 | 79.7 | 64.8 | 43.3
324 | 117 | 466.8 | 186.72 | 218.2649 | 186.5 | 175.9 | 195.4 | 178.7 | 412.6 | 21.1 | 21.3 | 42.4 | 3.7 | 264.8 | 7.4 | 169.3 | 855.5 | 832 | 278.6 | 748.4 | 252.8 | 554.2 | 678.9 | 221 | 653.7 | 61.2 | 195.1 | 21.6 | 198 | 188.9 | 19.4 | 80.1 | 65.2 | 43.5
325 | 118 | 467.3 | 186.92 | 218.4987 | 185.7 | 174.3 | 195.7 | 179 | 420.8 | 21.1 | 21.3 | 42.5 | 3.7 | 254.3 | 7.2 | 171.1 | 856 | 828.6 | 275.8 | 743.1 | 254.3 | 555.2 | 690.9 | 222.4 | 652.1 | 61.5 | 195.5 | 21.7 | 198.5 | 188.9 | 19.4 | 80.3 | 65.7 | 43.7
326 | 119 | 467.8 | 187.12 | 218.7325 | 185.7 | 173.2 | 196.6 | 179.3 | 413.3 | 21.2 | 21.3 | 42.7 | 4.1 | 258 | 6.7 | 172.9 | 853 | 816.7 | 273.4 | 743.5 | 255.7 | 555.6 | 696.5 | 223.8 | 652.6 | 61.9 | 195.8 | 21.8 | 198.9 | 188.9 | 19.5 | 80.6 | 66.2 | 43.9
327 | 120 | 467.3 | 186.92 | 218.4987 | 185.5 | 173.7 | 197.5 | 180.1 | 413.1 | 21.2 | 21.3 | 42.9 | 4.9 | 254.5 | 6.4 | 174.7 | 851 | 819.4 | 270.9 | 742.6 | 257.1 | 552.5 | 704.9 | 224.9 | 652 | 62.2 | 196.3 | 21.9 | 199.3 | 188.8 | 19.6 | 80.9 | 66.6 | 44.2
328 | 121 | 467.8 | 187.12 | 218.7325 | 184.9 | 174.9 | 197.4 | 180.3 | 418.5 | 21.2 | 21.3 | 43 | 4.5 | 284.6 | 7.1 | 176.4 | 842.6 | 823.4 | 268.3 | 739.4 | 258.5 | 554.8 | 717.2 | 226.3 | 649.6 | 62.5 | 197.1 | 22 | 199.9 | 189.6 | 19.6 | 81.4 | 67 | 44.4
329 | 122 | 467.6 | 187.04 | 218.639 | 184.5 | 175.9 | 198.2 | 180.9 | 422.1 | 21.4 | 21.3 | 43.1 | 4.4 | 286.6 | 8.3 | 178 | 829.4 | 824.9 | 265.4 | 731.7 | 260.1 | 551.6 | 723.4 | 227.5 | 647.3 | 62.9 | 197.7 | 22.1 | 199.9 | 190 | 19.7 | 81.7 | 67.5 | 44.6
330 | 123 | 467.7 | 187.08 | 218.6857 | 184.8 | 176.1 | 199.2 | 181.4 | 426.5 | 21.5 | 21.3 | 43.2 | 3.8 | 286.3 | 9.1 | 179.6 | 816.6 | 817.1 | 262.6 | 724 | 261.7 | 547.9 | 722.4 | 227.7 | 644.3 | 63.2 | 198.1 | 22.2 | 200.5 | 190.7 | 19.8 | 82.2 | 67.9 | 44.9
331 | 124 | 468 | 187.2 | 218.826 | 185.2 | 176.8 | 199.1 | 181.8 | 423.1 | 21.6 | 21.3 | 43.3 | 3.9 | 278.9 | 10.5 | 181.2 | 797.8 | 814.2 | 259.9 | 716.6 | 263.2 | 543.3 | 720.3 | 225.3 | 641.2 | 63.6 | 198.8 | 22.3 | 200.7 | 191.1 | 19.9 | 82.7 | 68.3 | 45.2
332 | 125 | 467 | 186.8 | 218.3584 | 185.1 | 177.6 | 199.8 | 182.4 | 425.6 | 21.7 | 21.3 | 43.5 | 3.9 | 267.2 | 9.6 | 182.7 | 776.9 | 800.9 | 257.5 | 714.1 | 264.6 | 541.2 | 726.2 | 223.4 | 637.4 | 64 | 199.6 | 22.4 | 201.4 | 190.7 | 20 | 82.9 | 68.7 | 45.5
333 | 126 | 467.7 | 187.08 | 218.6857 | 185 | 178.1 | 201.7 | 182.6 | 426.7 | 21.6 | 21.3 | 43.6 | 4.3 | 264.4 | 7.6 | 184.2 | 775.1 | 810.7 | 255.4 | 720 | 265.9 | 537.2 | 729.6 | 223.1 | 636.1 | 64.4 | 200 | 22.5 | 202.1 | 190.5 | 20.1 | 83.3 | 69.1 | 45.7
334 | 127 | 468.1 | 187.24 | 218.8728 | 185.4 | 178.6 | 202.4 | 183.4 | 429.1 | 21.7 | 21.3 | 43.8 | 5.1 | 269.4 | 7.9 | 185.7 | 778.9 | 822.6 | 253.1 | 726.9 | 267.3 | 539.7 | 739.2 | 224.5 | 637.9 | 64.7 | 200.3 | 22.6 | 203.3 | 190.4 | 20.1 | 83.7 | 69.5 | 46
335 | 128 | 467.6 | 187.04 | 218.639 | 185.3 | 179.1 | 202.2 | 183.6 | 442.1 | 21.7 | 21.3 | 44 | 4.4 | 263.9 | 9.4 | 187.1 | 781.4 | 823.7 | 250.4 | 727.8 | 268.7 | 541.3 | 743.1 | 226.5 | 637.6 | 65.1 | 200.6 | 22.7 | 203.3 | 191.3 | 20.2 | 84.1 | 69.9 | 46.2
336 | 129 | 468.2 | 187.28 | 218.9195 | 185.1 | 179.2 | 202.3 | 183.9 | 440 | 21.7 | 21.2 | 44.2 | 5 | 258.2 | 10 | 188.4 | 782.3 | 812.5 | 247.7 | 713.6 | 270.2 | 541.2 | 748.3 | 228.1 | 633.5 | 65.5 | 200.7 | 22.8 | 203.7 | 192.2 | 20.3 | 84.4 | 70.3 | 46.5
337 | 130 | 467.7 | 187.08 | 218.6857 | 185.9 | 179.2 | 201.8 | 184.2 | 455 | 21.8 | 21.2 | 44.4 | 5.9 | 260.8 | 11.9 | 189.7 | 774.8 | 803.7 | 245.1 | 704.9 | 271.6 | 551 | 764.5 | 230.4 | 632.2 | 65.9 | 201.3 | 22.9 | 205.6 | 192.9 | 20.4 | 84.8 | 70.8 | 46.7
338 | 131 | 468 | 187.2 | 218.826 | 186.8 | 179.7 | 202.5 | 185 | 467.8 | 21.9 | 21.2 | 44.6 | 5.8 | 264.1 | 12.1 | 190.9 | 763.5 | 792.5 | 242.6 | 700.2 | 272.9 | 555.6 | 768.5 | 232.4 | 630.7 | 66.3 | 201.8 | 23 | 206.1 | 193 | 20.5 | 85.1 | 71.3 | 47
339 | 132 | 470.5 | 188.2 | 219.995 | 187.7 | 180.2 | 203.5 | 185.5 | 466.4 | 21.9 | 21.2 | 44.7 | 4.9 | 274.3 | 12.2 | 192.1 | 765.4 | 805.5 | 240.3 | 699.5 | 274.1 | 558.3 | 766.5 | 234 | 629.4 | 66.6 | 202.3 | 23.1 | 206.2 | 193 | 20.6 | 85.4 | 71.8 | 47.2
340 | 133 | 472.8 | 189.12 | 221.0704 | 188.6 | 181.1 | 204.3 | 185.9 | 472.7 | 22 | 21.2 | 44.8 | 5.4 | 268.3 | 11.9 | 193.2 | 760.9 | 807.6 | 238.2 | 703 | 275.4 | 561.4 | 770.8 | 235.6 | 629.2 | 67 | 202.9 | 23.2 | 206.6 | 193.1 | 20.6 | 85.7 | 72.3 | 47.5
341 | 134 | 472.2 | 188.88 | 220.7898 | 189.1 | 181.8 | 203.8 | 186 | 478.6 | 22 | 21.2 | 45 | 5.2 | 266.4 | 13 | 194.2 | 749.8 | 795.1 | 236.2 | 702.7 | 276.7 | 559.3 | 768.5 | 237.2 | 626.3 | 67.4 | 203.8 | 23.3 | 206.9 | 193.3 | 20.7 | 86 | 72.8 | 47.7
342 | 135 | 470.4 | 188.16 | 219.9482 | 189.7 | 182.2 | 203.7 | 186.5 | 477.8 | 22.1 | 21.2 | 45.1 | 5.5 | 264.8 | 14.8 | 195 | 724.2 | 792.9 | 234.2 | 698.9 | 278.1 | 552.6 | 761.2 | 238.2 | 623.5 | 67.8 | 204.1 | 23.4 | 207.5 | 193.6 | 20.8 | 86.4 | 73.2 | 48
343 | 136 | 468.5 | 187.4 | 219.0598 | 190 | 182.6 | 204.1 | 187.1 | 468.3 | 22.2 | 21.2 | 45.3 | 6.6 | 270.4 | 13.8 | 195.8 | 715.3 | 805.7 | 232.2 | 698.9 | 278.8 | 550.4 | 767.2 | 239.3 | 620.1 | 68.2 | 204.6 | 23.5 | 208.7 | 193.7 | 20.9 | 86.8 | 73.7 | 48.2
344 | 137 | 469.2 | 187.68 | 219.3871 | 189.8 | 183.3 | 205.1 | 187.1 | 468.4 | 22.2 | 21.2 | 45.4 | 6.8 | 269.4 | 13.3 | 196.5 | 704.6 | 799.5 | 230.3 | 695.7 | 279.6 | 547 | 765.2 | 240.3 | 616 | 68.6 | 204.8 | 23.7 | 209.5 | 194 | 21 | 87.3 | 74.1 | 48.5
345 | 138 | 468.9 | 187.56 | 219.2468 | 190.1 | 183.4 | 206.7 | 186.9 | 463.4 | 22.3 | 21.2 | 45.5 | 5.7 | 274.1 | 13 | 197.1 | 685.2 | 777.7 | 228.3 | 688.9 | 280.9 | 539.6 | 754.1 | 241 | 612.3 | 69 | 205 | 23.8 | 209.6 | 194.3 | 21.1 | 87.6 | 74.6 | 48.7
346 | 139 | 470 | 188 | 219.7612 | 190.5 | 183.6 | 207.1 | 187.3 | 462.2 | 22.4 | 21.2 | 45.6 | 5.4 | 279.7 | 12.1 | 197.6 | 668.1 | 757.2 | 226.1 | 680 | 282.4 | 530.1 | 736.4 | 241.2 | 608.3 | 69.4 | 205.6 | 23.9 | 209.1 | 194.7 | 21.2 | 87.9 | 75 | 48.9
347 | 140 | 468.6 | 187.44 | 219.1066 | 190.6 | 183.2 | 207.6 | 186.8 | 463.4 | 22.4 | 21.2 | 45.7 | 4.9 | 272.2 | 10.9 | 197.8 | 655.5 | 754.3 | 223.9 | 669.5 | 283.9 | 527.9 | 747.5 | 242.2 | 605.7 | 69.8 | 206.7 | 24 | 209.2 | 194.8 | 21.2 | 88.2 | 75.4 | 49.1
348 | 141 | 469.6 | 187.84 | 219.5741 | 190.7 | 183.3 | 208.3 | 186.4 | 470.3 | 22.5 | 21.2 | 45.8 | 4.8 | 275.6 | 9.3 | 198 | 650.2 | 766.7 | 221.7 | 664.7 | 285.5 | 533.5 | 759.7 | 243.4 | 606.2 | 70.3 | 207 | 24.1 | 209.6 | 195.3 | 21.3 | 88.6 | 75.8 | 49.1
349 | 142 | 469.4 | 187.76 | 219.4806 | 192 | 182.9 | 209.1 | 186.2 | 477.1 | 22.5 | 21.2 | 45.8 | 5 | 263.7 | 9.5 | 198.1 | 660.5 | 770.2 | 219.7 | 672.2 | 287.1 | 534.8 | 754.8 | 244.3 | 605.7 | 70.7 | 207.7 | 24.2 | 210.9 | 195.3 | 21.4 | 89.1 | 76.2 | 49.6
350 | 143 | 469.4 | 187.76 | 219.4806 | 192.6 | 183.7 | 209.8 | 186.4 | 465.6 | 22.6 | 21.2 | 45.8 | 4.8 | 259.9 | 11.2 | 198 | 657.4 | 764.2 | 218.1 | 672.4 | 288.7 | 530.5 | 746.7 | 244.7 | 603.6 | 71.1 | 208.5 | 24.3 | 211 | 195.1 | 21.5 | 89.5 | 76.6 | 49.9
351 | 144 | 469.2 | 187.68 | 219.3871 | 192.9 | 184.2 | 210.8 | 186.7 | 456.9 | 22.7 | 21.2 | 45.9 | 5.2 | 249.2 | 12.9 | 197.8 | 667.5 | 775.8 | 216.7 | 680 | 290.3 | 530.9 | 747.5 | 245.4 | 605.2 | 71.5 | 209.2 | 24.4 | 210.7 | 194.6 | 21.6 | 89.9 | 77 | 50.2
352 | 145 | 468.7 | 187.48 | 219.1533 | 193.3 | 184.3 | 211.4 | 187 | 459.4 | 22.7 | 21.2 | 45.9 | 5.2 | 252.8 | 13 | 197.7 | 683.9 | 785.8 | 215.6 | 686.5 | 291.9 | 533.7 | 737.6 | 246.1 | 607.4 | 71.9 | 209.7 | 24.5 | 209.9 | 194.5 | 21.7 | 90.4 | 77.4 | 50.4
353 | 146 | 468.7 | 187.48 | 219.1533 | 193.5 | 184 | 211.8 | 187.3 | 452.1 | 22.8 | 21.2 | 46 | 4.9 | 254.3 | 12.2 | 197.5 | 698.8 | 796.4 | 214.8 | 692.5 | 293.6 | 532.7 | 720.6 | 246.5 | 609.5 | 72.3 | 209.7 | 24.6 | 209.6 | 194.3 | 21.8 | 90.8 | 77.7 | 50.6
354 | 147 | 468.3 | 187.32 | 218.9663 | 193.9 | 183.7 | 212.3 | 187.6 | 442.4 | 22.9 | 21.2 | 46.1 | 4.5 | 260.9 | 12.1 | 197.4 | 712.1 | 808.9 | 214.1 | 702 | 295.3 | 535.5 | 713.8 | 247 | 609.8 | 72.8 | 209.6 | 24.7 | 210.8 | 194.3 | 21.9 | 91.1 | 78.2 | 50.9
355 | 148 | 468.4 | 187.36 | 219.013 | 193.4 | 183.4 | 211.6 | 187.2 | 438.7 | 22.9 | 21.2 | 46.2 | 4.7 | 255.6 | 11.5 | 197.3 | 728 | 800.2 | 213.6 | 705.7 | 297 | 537.3 | 707.8 | 247.3 | 610.1 | 73.2 | 209.6 | 24.9 | 210.5 | 194.8 | 22 | 91.6 | 78.6 | 51.1
356 | 149 | 468.5 | 187.4 | 219.0598 | 192.8 | 183.4 | 211 | 186.9 | 430.3 | 23 | 21.2 | 46.3 | 4.6 | 254 | 11.2 | 197.2 | 740.4 | 803.8 | 213.2 | 707.3 | 298.5 | 540 | 721.6 | 248 | 611.8 | 73.5 | 209.7 | 25 | 209.7 | 194.7 | 22.1 | 91.9 | 79.2 | 51.4
357 | 150 | 468.7 | 187.48 | 219.1533 | 193 | 184 | 210.9 | 186.8 | 433.9 | 23 | 21.2 | 46.4 | 4.9 | 255.3 | 11.1 | 197.2 | 752.8 | 816.9 | 212.7 | 713.4 | 300 | 543.8 | 721.2 | 249.1 | 616.3 | 73.9 | 209.6 | 25.1 | 209.9 | 194.9 | 22.2 | 92.2 | 79.7 | 51.6
358 | 151 | 468.2 | 187.28 | 218.9195 | 191.4 | 184.9 | 210.4 | 185.9 | 434.6 | 23 | 21.2 | 46.4 | 4.8 | 260.5 | 11.6 | 197.2 | 767.8 | 820.8 | 212.1 | 710.6 | 301.6 | 547.2 | 728.4 | 250 | 615.7 | 74.3 | 209.3 | 25.2 | 210.2 | 194.8 | 22.3 | 92.6 | 80.2 | 51.8
359 | 152 | 467.8 | 187.12 | 218.7325 | 191 | 186.4 | 210.3 | 185.4 | 434.8 | 23.1 | 21.2 | 46.5 | 4.3 | 266.3 | 11.3 | 197.4 | 785.5 | 826 | 211.6 | 710.4 | 303.1 | 552.9 | 726.8 | 250.8 | 617 | 74.6 | 209.1 | 25.3 | 210.2 | 194.5 | 22.4 | 92.9 | 80.6 | 52
360 | 153 | 467.3 | 186.92 | 218.4987 | 192 | 187.4 | 210 | 185.4 | 439.4 | 23.2 | 21.2 | 46.6 | 4.5 | 259.8 | 10.6 | 197.6 | 796.1 | 837.2 | 211.2 | 712.5 | 304.7 | 565.9 | 735 | 252.3 | 622.5 | 75 | 209.1 | 25.4 | 210 | 194.4 | 22.5 | 93.2 | 81.1 | 52.2
361 | 154 | 468.4 | 187.36 | 219.013 | 191.8 | 187.2 | 209.3 | 185.9 | 448.9 | 23.3 | 21.2 | 46.7 | 4.6 | 256.6 | 10.3 | 197.8 | 796.3 | 847.8 | 210.9 | 718.2 | 306.3 | 577.6 | 746.4 | 254.1 | 626.1 | 75.3 | 209.5 | 25.5 | 209.6 | 194.4 | 22.6 | 93.5 | 81.7 | 52.4
362 | 155 | 468.1 | 187.24 | 218.8728 | 191.8 | 187.1 | 209.1 | 186.4 | 460 | 23.4 | 21.2 | 46.8 | 4.2 | 262.1 | 10.6 | 198.1 | 799.1 | 853 | 210.9 | 723.3 | 308 | 589.9 | 751.9 | 256 | 632.8 | 75.6 | 209.6 | 25.6 | 209.5 | 195.3 | 22.7 | 93.8 | 82.3 | 52.7
363 | 156 | 468.3 | 187.32 | 218.9663 | 191.9 | 186.7 | 209.3 | 187.1 | 465.4 | 23.4 | 21.2 | 47 | 4.8 | 261.5 | 10.6 | 198.5 | 807.8 | 857.4 | 210.9 | 727.2 | 309.9 | 595.7 | 764 | 257.9 | 635.5 | 76 | 209.8 | 25.7 | 209.1 | 196.2 | 22.8 | 94.2 | 82.8 | 52.9
364 | 157 | 468.1 | 187.24 | 218.8728 | 190.6 | 186.9 | 209.6 | 187.7 | 474.8 | 23.5 | 21.2 | 47.1 | 5.4 | 255.5 | 10 | 198.9 | 810.1 | 866 | 210.8 | 725.1 | 311.7 | 603.7 | 776 | 260.1 | 638.2 | 76.3 | 210.1 | 25.9 | 208.9 | 196.7 | 22.9 | 94.5 | 83.3 | 53.1
365 | 158 | 467.8 | 187.12 | 218.7325 | 190.3 | 186.5 | 210.4 | 188.3 | 481.6 | 23.6 | 21.2 | 47.2 | 5 | 263 | 10.9 | 199.4 | 802.5 | 862.3 | 210.6 | 721.6 | 313.5 | 602.5 | 789.6 | 261.9 | 636.5 | 76.6 | 210.5 | 26 | 208.4 | 197.3 | 23 | 94.8 | 83.8 | 53.4
366 | 159 | 467.5 | 187 | 218.5922 | 190.6 | 186.4 | 211.4 | 188.2 | 487.2 | 23.6 | 21.1 | 47.2 | 4.6 | 257.4 | 12.4 | 199.9 | 805.6 | 848.6 | 210.2 | 716.9 | 315.2 | 605.3 | 797.3 | 263.7 | 635.9 | 76.9 | 210.9 | 26.1 | 209.5 | 197.9 | 23.1 | 95.2 | 84.3 | 53.6
367 | 160 | 467.4 | 186.96 | 218.5455 | 191.3 | 187.5 | 212.6 | 188.2 | 500.3 | 23.7 | 21.1 | 47.2 | 4.4 | 260.6 | 12.2 | 200.5 | 810.2 | 840.9 | 209.9 | 708.2 | 316.8 | 603.5 | 800.9 | 265.1 | 634.1 | 77.3 | 211.5 | 26.2 | 210.9 | 198.5 | 23.2 | 95.6 | 84.7 | 53.9
368 | 161 | 467.7 | 187.08 | 218.6857 | 192.2 | 187.6 | 213.2 | 188.6 | 496.1 | 23.8 | 21.1 | 47.3 | 4.6 | 259.6 | 12 | 201.2 | 808.3 | 822.9 | 209.6 | 700.3 | 318.4 | 600.7 | 791.3 | 266.3 | 631.5 | 77.6 | 212.3 | 26.3 | 211.8 | 199 | 23.4 | 95.9 | 85.2 | 54.2
369 | 162 | 467.1 | 186.84 | 218.4052 | 192.8 | 188.3 | 213.9 | 189.1 | 482.3 | 23.9 | 21.1 | 47.3 | 4.1 | 256.5 | 11.6 | 201.8 | 802.5 | 822 | 209.4 | 699.6 | 319.9 | 595.1 | 786 | 267.2 | 631.4 | 78 | 212.9 | 26.4 | 212.3 | 199.7 | 23.5 | 96.2 | 85.6 | 54.4
370 | 163 | 467 | 186.8 | 218.3584 | 193.2 | 188 | 214.9 | 189.8 | 485.2 | 23.9 | 21.1 | 47.4 | 4.1 | 258.4 | 11.6 | 202.5 | 804.7 | 824 | 209.4 | 704.3 | 321.4 | 595 | 783.7 | 268.4 | 633 | 78.3 | 213.2 | 26.6 | 213 | 200.2 | 23.6 | 96.6 | 86 | 54.7
371 | 164 | 467.5 | 187 | 218.5922 | 192.4 | 188.1 | 214.5 | 189.4 | 480.7 | 24 | 21.1 | 47.5 | 4.1 | 277.2 | 11.9 | 203.2 | 796.6 | 813.6 | 209.4 | 697.1 | 322.9 | 588.7 | 775.1 | 269.3 | 631.3 | 78.7 | 213.5 | 26.7 | 213.4 | 200.3 | 23.7 | 96.9 | 86.4 | 55
372 | 165 | 467.7 | 187.08 | 218.6857 | 192.2 | 188.9 | 214.8 | 189.5 | 483.4 | 24.1 | 21.1 | 47.6 | 4.1 | 287 | 10.6 | 204 | 795 | 818.5 | 209.3 | 694.3 | 324.3 | 586.4 | 775.9 | 270.4 | 628.9 | 79.1 | 213.7 | 26.8 | 213.8 | 199.9 | 23.8 | 97.3 | 86.8 | 55.2
373 | 166 | 467 | 186.8 | 218.3584 | 192.9 | 189.1 | 215 | 189.6 | 473.7 | 24.1 | 21.1 | 47.7 | 4.6 | 288.2 | 8.6 | 204.7 | 789.9 | 804.2 | 209.3 | 687.8 | 325.8 | 580.3 | 770.3 | 271.2 | 626.9 | 79.4 | 213.8 | 26.9 | 214 | 199.9 | 23.9 | 97.6 | 87.3 | 55.5
374 | 167 | 467.9 | 187.16 | 218.7793 | 193.2 | 189.1 | 215.4 | 190 | 470.1 | 24.1 | 21.1 | 47.9 | 5 | 267.9 | 9.4 | 205.5 | 794.2 | 787.6 | 209.2 | 686.6 | 327.1 | 577.5 | 772.6 | 272 | 624.7 | 79.8 | 214.1 | 27 | 214.5 | 200.1 | 24 | 98 | 87.7 | 55.7
375 | 168 | 467.6 | 187.04 | 218.639 | 193.8 | 189.5 | 215.8 | 190.5 | 476.1 | 24.2 | 21.1 | 48 | 4 | 265.8 | 10.3 | 206.4 | 797.9 | 798.2 | 209.2 | 687 | 328.5 | 578.9 | 782.1 | 273.1 | 624.1 | 80.2 | 214.4 | 27.1 | 216 | 200.6 | 24.1 | 98.3 | 88.2 | 56
376 | 169 | 466.8 | 186.72 | 218.2649 | 194.5 | 189.7 | 216.9 | 191.2 | 478.4 | 24.2 | 21.1 | 48.2 | 4 | 264.1 | 10.9 | 207.1 | 796.3 | 793.5 | 209.2 | 691.4 | 330 | 580.2 | 783.5 | 274.1 | 623.9 | 80.5 | 214.6 | 27.3 | 216.1 | 201.1 | 24.2 | 98.7 | 88.7 | 56.2
377 | 170 | 467 | 186.8 | 218.3584 | 195.2 | 190.1 | 217.2 | 191.9 | 476 | 24.3 | 21.1 | 48.3 | 4.2 | 271.3 | 11.6 | 208 | 796 | 796 | 209.1 | 692.3 | 331.5 | 580 | 780.2 | 275.1 | 623.3 | 80.9 | 214.9 | 27.4 | 216.1 | 201.1 | 24.4 | 98.9 | 89.1 | 56.5
378 | 171 | 466.4 | 186.56 | 218.0779 | 195.9 | 191 | 218 | 192.5 | 480.8 | 24.3 | 21.1 | 48.4 | 3.9 | 270.5 | 9.5 | 208.8 | 793.3 | 793.9 | 209.1 | 694.3 | 333.1 | 584 | 785.4 | 276.3 | 624.2 | 81.3 | 215.4 | 27.5 | 216.1 | 201.6 | 24.5 | 99.3 | 89.6 | 56.7
379 | 172 | 468.6 | 187.44 | 219.1066 | 196.5 | 191.7 | 217.9 | 192.9 | 483.5 | 24.3 | 21.1 | 48.5 | 4.4 | 281.9 | 8.1 | 209.7 | 793.2 | 803.7 | 209 | 699.1 | 334.7 | 586.4 | 791.4 | 277.4 | 625.4 | 81.6 | 215.5 | 27.6 | 216.4 | 201.5 | 24.6 | 99.7 | 90 | 56.9
380 | 173 | 466.2 | 186.48 | 217.9844 | 197.1 | 191.8 | 217.1 | 192.6 | 487 | 24.3 | 21.1 | 48.7 | 4.5 | 269.3 | 8.8 | 210.6 | 793.7 | 801.4 | 209 | 701.2 | 336.3 | 587.8 | 794.6 | 278.4 | 624.4 | 82 | 216 | 27.7 | 218.1 | 201.5 | 24.7 | 99.9 | 90.5 | 57.2
381 | 174 | 465.6 | 186.24 | 217.7038 | 197.9 | 192 | 217.5 | 192.6 | 491.6 | 24.3 | 21.1 | 48.8 | 4.7 | 275.7 | 9.1 | 211.4 | 797.1 | 802.6 | 209 | 707.1 | 337.9 | 589.3 | 792.2 | 279.5 | 625.2 | 82.4 | 216.3 | 27.9 | 218.3 | 201.4 | 24.8 | 100.3 | 90.9 | 57.4
382 | 175 | 465.6 | 186.24 | 217.7038 | 198.3 | 191.7 | 217.5 | 193 | 483.1 | 24.3 | 21.1 | 48.9 | 4.8 | 270 | 8.7 | 212.2 | 798.3 | 807 | 209.2 | 715.2 | 339.5 | 583.4 | 783.3 | 280.2 | 625.7 | 82.7 | 216.7 | 28 | 218.1 | 201.6 | 24.9 | 100.7 | 91.3 | 57.6
383 | 176 | 464.6 | 185.84 | 217.2363 | 199.2 | 191.2 | 217.1 | 193.2 | 466.9 | 24.3 | 21.1 | 48.9 | 5.4 | 277.9 | 7.9 | 213 | 800 | 804.5 | 209.5 | 720.8 | 341 | 580.7 | 778.4 | 280.6 | 626.5 | 83.1 | 216.9 | 28.1 | 217.5 | 201.4 | 25 | 101.2 | 91.8 | 57.9
384 | 177 | 465 | 186 | 217.4233 | 199.8 | 191 | 215.9 | 193.4 | 465.2 | 24.3 | 21.1 | 49 | 5 | 258.3 | 7.9 | 214 | 805.8 | 811.6 | 209.8 | 728.9 | 342.5 | 580.4 | 767.1 | 281.1 | 627.5 | 83.5 | 216.9 | 28.2 | 217 | 201.5 | 25.2 | 101.5 | 92.2 | 58.1
385 | 178 | 465.6 | 186.24 | 217.7038 | 199.9 | 191 | 215.6 | 193.6 | 450.6 | 24.3 | 21.1 | 49 | 5.4 | 251.1 | 7.5 | 214.8 | 814.3 | 823.7 | 210.1 | 736 | 343.9 | 577.4 | 760.3 | 281.6 | 626.8 | 83.8 | 217 | 28.3 | 217.3 | 201.7 | 25.3 | 101.9 | 92.7 | 58.3
386 | 179 | 465.6 | 186.24 | 217.7038 | 199.9 | 191.2 | 215.3 | 193.5 | 449 | 24.4 | 21.1 | 49 | 5.1 | 273.1 | 7.3 | 215.7 | 817.2 | 833.8 | 210.4 | 738.9 | 345.4 | 583.2 | 762 | 282.4 | 627.9 | 84.2 | 216.9 | 28.5 | 216.5 | 201.7 | 25.4 | 102.2 | 93.2 | 58.5
387 | 180 | 465.9 | 186.36 | 217.8441 | 199.9 | 191.4 | 216 | 193.8 | 453.6 | 24.4 | 21.1 | 49.1 | 5.2 | 266.2 | 7.4 | 216.6 | 818.3 | 807.3 | 210.7 | 738.9 | 347 | 579.1 | 748.5 | 283 | 629.2 | 84.6 | 217 | 28.6 | 216.4 | 202 | 25.5 | 102.5 | 93.7 | 58.7
388 | 181 | 467.8 | 187.12 | 218.7325 | 200.1 | 191.5 | 216.4 | 194.2 | 448.4 | 24.4 | 21.1 | 49.2 | 5.7 | 255.3 | 7.7 | 217.6 | 821 | 808.5 | 211.1 | 737.1 | 348.5 | 578.2 | 744.7 | 283.6 | 631.7 | 84.9 | 216.7 | 28.7 | 216.3 | 202.2 | 25.6 | 102.9 | 94.2 | 59
389 | 182 | 468.7 | 187.48 | 219.1533 | 200.1 | 191.7 | 216.2 | 194.2 | 452.2 | 24.5 | 21.1 | 49.3 | 7.2 | 239.3 | 8.9 | 218.5 | 822.8 | 818.3 | 211.4 | 735.4 | 350 | 581.9 | 762.8 | 284.5 | 631.4 | 85.3 | 216.9 | 28.8 | 215.3 | 202.6 | 25.8 | 103.1 | 94.6 | 59.2
390 | 183 | 469.1 | 187.64 | 219.3403 | 201 | 191.5 | 215.3 | 194 | 461.8 | 24.5 | 21.1 | 49.5 | 6.8 | 240.1 | 9.9 | 219.4 | 824.1 | 820.2 | 211.7 | 732.4 | 351.7 | 582.4 | 768.6 | 285.3 | 630 | 85.6 | 217.2 | 28.9 | 215.2 | 202.5 | 25.9 | 103.5 | 95.1 | 59.4
391 | 184 | 468.9 | 187.56 | 219.2468 | 201.6 | 191.5 | 215.6 | 193.5 | 469 | 24.6 | 21.1 | 49.7 | 7.6 | 227 | 9.9 | 220.4 | 823.4 | 832.1 | 212 | 728.6 | 353.4 | 581.4 | 775.4 | 286.1 | 628.2 | 85.9 | 217.5 | 29.1 | 215.4 | 202.2 | 26 | 103.8 | 95.5 | 59.6
392 | 185 | 466.1 | 186.44 | 217.9376 | 202.1 | 191.7 | 215.9 | 193.6 | 475.1 | 24.6 | 21.1 | 49.8 | 7.6 | 232.1 | 8.6 | 221.3 | 819.4 | 832.5 | 212.2 | 733.5 | 355.2 | 582.5 | 779.5 | 286.9 | 628.7 | 86.3 | 217.6 | 29.2 | 215.8 | 202 | 26.1 | 104.2 | 96 | 59.8
393 | 186 | 466.6 | 186.64 | 218.1714 | 202.4 | 192 | 216.1 | 194.2 | 474.5 | 24.7 | 21.1 | 50 | 5.9 | 246.4 | 7 | 222.2 | 820.4 | 827 | 212.5 | 737.6 | 348.5 | 584.7 | 779.3 | 287.6 | 630.9 | 86.6 | 218.2 | 29.3 | 216.1 | 202.1 | 26.3 | 104.5 | 96.5 | 60
394 | 187 | 467 | 186.8 | 218.3584 | 202.9 | 192.2 | 216.2 | 194.5 | 478.7 | 24.7 | 21.1 | 50 | 5.4 | 256.2 | 7.1 | 223.1 | 821.3 | 835.7 | 213 | 741.5 | 348.4 | 593.4 | 780.6 | 288.2 | 634.9 | 87 | 218.3 | 29.4 | 216.4 | 202.2 | 26.4 | 105 | 96.9 | 60.3
395 | 188 | 466.4 | 186.56 | 218.0779 | 203 | 192 | 216.5 | 194.9 | 485 | 24.7 | 21.1 | 50 | 4.6 | 230.6 | 7.3 | 224.1 | 820.7 | 831.3 | 213.4 | 736 | 351.9 | 590.2 | 777.1 | 288.9 | 632.7 | 87.3 | 218.4 | 29.6 | 217 | 202.4 | 26.5 | 105.3 | 97.4 | 60.5
396 | 189 | 468.8 | 187.52 | 219.2001 | 203.1 | 191.7 | 216.3 | 195.3 | 481.2 | 24.8 | 21.1 | 50 | 5.5 | 234 | 8.9 | 225 | 820.5 | 846.4 | 213.8 | 739.2 | 355.3 | 592.2 | 784.9 | 289.6 | 634.5 | 87.7 | 218.6 | 29.7 | 217.8 | 202.3 | 26.6 | 105.7 | 97.9 | 60.7
397 | 190 | 468.8 | 187.52 | 219.2001 | 203.6 | 191.4 | 215 | 196 | 491.4 | 24.9 | 21.1 | 50.2 | 6.3 | 244 | 11.8 | 226 | 818.5 | 847.9 | 214.1 | 739.4 | 358.5 | 602.2 | 795.9 | 290.7 | 636.7 | 88 | 218.7 | 29.8 | 220.3 | 202.7 | 26.8 | 106 | 98.4 | 61
398 | 191 | 466.9 | 186.76 | 218.3117 | 203.3 | 191.7 | 215.1 | 196.1 | 505.2 | 24.9 | 21.1 | 50.3 | 7.1 | 244.3 | 12.3 | 226.9 | 820.6 | 853.3 | 214.4 | 741.5 | 361.8 | 609 | 799.9 | 291.7 | 636.2 | 88.4 | 219 | 29.9 | 220.6 | 202.7 | 26.9 | 106.4 | 98.8 | 61.3
399 | 192 | 467.5 | 187 | 218.5922 | 202.7 | 192.2 | 215.7 | 196.5 | 504.7 | 24.9 | 21.1 | 50.4 | 6.2 | 253.4 | 11.8 | 227.8 | 820.9 | 836.4 | 214.6 | 737.2 | 364.8 | 609.9 | 794.1 | 292.7 | 635.1 | 88.8 | 219.3 | 30.1 | 220.9 | 203 | 27 | 106.8 | 99.3 | 61.5
400 | 193 | 468.1 | 187.24 | 218.8728 | 203 | 192.7 | 215.3 | 197.3 | 505.8 | 25 | 21.1 | 50.5 | 5.4 | 233.2 | 11 | 228.8 | 818.2 | 811 | 214.8 | 727.6 | 367.6 | 608.7 | 796.6 | 293.5 | 632.8 | 89.1 | 219.5 | 30.2 | 220.5 | 203.4 | 27.1 | 107.1 | 99.8 | 61.8
401 | 194 | 468.3 | 187.32 | 218.9663 | 203.4 | 193.1 | 216.4 | 197.7 | 509.4 | 25 | 21.1 | 50.6 | 5.7 | 241.5 | 11.1 | 229.8 | 814.7 | 827.5 | 215 | 725.3 | 370.2 | 615.3 | 801 | 294.3 | 634 | 89.5 | 220.1 | 30.3 | 220.3 | 203.6 | 27.2 | 107.5 | 100.3 | 62
402 | 195 | 468.4 | 187.36 | 219.013 | 204.5 | 193.9 | 216 | 198.1 | 519.6 | 25.1 | 21.1 | 50.7 | 6.6 | 235.3 | 11 | 230.8 | 811.1 | 829.3 | 215.2 | 724.1 | 372.9 | 618.7 | 799.6 | 295.2 | 634.7 | 89.8 | 220.7 | 30.4 | 220.4 | 203.5 | 27.4 | 108 | 100.8 | 62.2
403 | 196 | 468.4 | 187.36 | 219.013 | 205.1 | 193.9 | 215.7 | 197.9 | 512.2 | 25.1 | 21.1 | 50.7 | 6 | 244.5 | 13.5 | 231.9 | 813 | 825.5 | 215.3 | 722.5 | 375.4 | 614.7 | 804.8 | 295.8 | 633.5 | 90.2 | 221.4 | 30.6 | 220.7 | 203.5 | 27.5 | 108.4 | 101.3 | 62.5
404 | 197 | 468.8 | 187.52 | 219.2001 | 205.3 | 193.4 | 215.7 | 198.3 | 498.3 | 25.2 | 21.1 | 50.7 | 6.2 | 239.8 | 13.9 | 233 | 815.3 | 822.4 | 215.6 | 726.1 | 378.1 | 611.8 | 801.9 | 296.4 | 633.3 | 90.6 | 222 | 30.7 | 220.3 | 203.7 | 27.6 | 108.8 | 101.8 | 62.8
405 | 198 | 468.1 | 187.24 | 218.8728 | 205.8 | 193.2 | 216 | 199 | 485.8 | 25.2 | 21.1 | 50.7 | 5.7 | 242.5 | 13.8 | 234.1 | 818.7 | 812.5 | 215.9 | 726.7 | 380.8 | 609.1 | 795.4 | 297 | 634.9 | 90.9 | 222.4 | 30.8 | 220.5 | 204 | 27.8 | 109.3 | 102.3 | 63
406 | 199 | 468 | 187.2 | 218.826 | 206.5 | 192.5 | 217.1 | 199.7 | 481.3 | 25.3 | 21.1 | 50.7 | 5.7 | 239.7 | 14.1 | 235.2 | 818.7 | 814.8 | 216.2 | 721.6 | 383.5 | 605.3 | 797.1 | 297.6 | 633.9 | 91.3 | 222.6 | 30.9 | 221 | 204.3 | 27.9 | 109.6 | 102.8 | 63.3
407 | 200 | 467.8 | 187.12 | 218.7325 | 207.1 | 192.1 | 217.4 | 199.7 | 480.9 | 25.3 | 21.1 | 50.7 | 4.7 | 242.7 | 14 | 236.3 | 815.3 | 811.7 | 216.5 | 721.3 | 386.3 | 599.8 | 793.1 | 298.2 | 633.7 | 91.7 | 222.3 | 31.1 | 220.7 | 204.4 | 28 | 110 | 103.2 | 63.6
408 | 201 | 467.9 | 187.16 | 218.7793 | 207.6 | 191.9 | 217.6 | 199.9 | 475.5 | 25.4 | 21.1 | 50.7 | 4.7 | 240.1 | 14.6 | 237.4 | 810.9 | 830.8 | 216.9 | 728.1 | 389.1 | 599.5 | 796.4 | 298.8 | 634.4 | 92.1 | 222.1 | 31.2 | 221 | 204.7 | 28.1 | 110.3 | 103.6 | 63.8
409 | 202 | 468 | 187.2 | 218.826 | 207.9 | 192.5 | 217.8 | 200.1 | 484.1 | 25.4 | 21.1 | 50.8 | 4.9 | 244.3 | 13.9 | 238.5 | 805.8 | 823.7 | 217.2 | 727.4 | 392 | 600.7 | 799.3 | 299.5 | 634.2 | 92.4 | 222.4 | 31.3 | 220.5 | 204.5 | 28.2 | 110.7 | 104 | 64
410 | 203 | 467.5 | 187 | 218.5922 | 208.2 | 193 | 217.9 | 200.3 | 499.6 | 25.5 | 21.1 | 50.9 | 5.4 | 239 | 12.4 | 239.5 | 796.3 | 813.3 | 217.5 | 719.9 | 394.9 | 588.8 | 793.5 | 300.2 | 632.3 | 92.8 | 222.7 | 31.4 | 220.4 | 204.6 | 28.4 | 111 | 104.5 | 64.2
411 | 204 | 468.3 | 187.32 | 218.9663 | 208.6 | 193.1 | 218.1 | 200.3 | 495.5 | 25.6 | 21.1 | 51 | 4.5 | 240.3 | 12.7 | 240.5 | 790.5 | 795.3 | 217.6 | 711.5 | 397.9 | 556.6 | 790.4 | 300.8 | 628.7 | 93.1 | 223.1 | 31.6 | 221.2 | 205 | 28.5 | 111.4 | 104.9 | 64.5
412 | 205 | 467.6 | 187.04 | 218.639 | 209.1 | 194.7 | 217.7 | 200.7 | 492 | 25.6 | 21.1 | 51 | 4.5 | 242.7 | 12.7 | 241.5 | 792.6 | 783.8 | 217.8 | 705.1 | 400.7 | 556.9 | 790.9 | 301.6 | 628.9 | 93.5 | 223.6 | 31.7 | 221.2 | 205.7 | 28.6 | 111.8 | 105.3 | 64.8
413 | 206 | 467.9 | 187.16 | 218.7793 | 209.1 | 196.6 | 219.3 | 201.2 | 486.9 | 25.7 | 21.1 | 51 | 4.7 | 237.2 | 12.2 | 242.4 | 792.2 | 791.8 | 217.9 | 704.3 | 403.5 | 560.2 | 783.5 | 302.3 | 628 | 93.8 | 224.1 | 31.8 | 220.3 | 206.2 | 28.8 | 112.1 | 105.8 | 65
414 | 207 | 468.7 | 187.48 | 219.1533 | 209.4 | 197.1 | 221.3 | 201.3 | 480.4 | 25.8 | 21 | 51.1 | 4.5 | 242.7 | 11.3 | 243.4 | 796 | 810.4 | 218.2 | 705.9 | 406.2 | 571.9 | 792.9 | 303.1 | 627.9 | 94.2 | 224.5 | 32 | 220.9 | 206.1 | 28.9 | 112.5 | 106.1 | 65.2
415 | 208 | 467.3 | 186.92 | 218.4987 | 209.4 | 197.7 | 222.5 | 201.5 | 482 | 25.9 | 21 | 51.1 | 4.1 | 241.1 | 9.7 | 244.3 | 795.7 | 821.8 | 218.6 | 708.4 | 409.1 | 580.3 | 796.1 | 303.9 | 627.4 | 94.5 | 224.7 | 32.1 | 222.5 | 206.9 | 29 | 112.8 | 106.6 | 65.5
416 | 209 | 468.8 | 187.52 | 219.2001 | 209.3 | 198.3 | 223.6 | 202 | 479.4 | 25.9 | 21.1 | 51.2 | 4.6 | 235.5 | 9.2 | 245.2 | 798.2 | 823.8 | 218.9 | 710.7 | 412 | 583.2 | 795.2 | 304.8 | 627 | 94.9 | 224.7 | 32.2 | 224.1 | 207.5 | 29.1 | 113.2 | 107.1 | 65.8
417 | 210 | 468.3 | 187.32 | 218.9663 | 209.8 | 198.2 | 224.5 | 202.8 | 485.7 | 26 | 21 | 51.4 | 5.1 | 235.1 | 9.1 | 246 | 797.4 | 831.6 | 219.4 | 714.5 | 414.8 | 589.4 | 798.9 | 305.6 | 626.4 | 95.2 | 224.8 | 32.3 | 224.7 | 207.8 | 29.3 | 113.5 | 107.6 | 66.1
418 | 211 | 467.9 | 187.16 | 218.7793 | 209.8 | 198 | 225.4 | 203.1 | 484.3 | 26 | 21 | 51.6 | 5.4 | 240.5 | 8.9 | 246.9 | 801.7 | 834.1 | 220.1 | 716.3 | 417.6 | 594.5 | 799.5 | 306.5 | 628.2 | 95.6 | 225 | 32.5 | 225.1 | 208.1 | 29.4 | 113.9 | 108 | 66.3
419 | 212 | 468.7 | 187.48 | 219.1533 | 210.2 | 198 | 225.9 | 203 | 479.3 | 26.1 | 21 | 51.8 | 5.4 | 239.6 | 9.7 | 247.7 | 803.6 | 825.2 | 220.8 | 714.1 | 420.3 | 592.8 | 800.7 | 307.3 | 626.1 | 96 | 225.8 | 32.6 | 225.1 | 208.3 | 29.5 | 114.2 | 108.5 | 66.6
420 | 213 | 468.5 | 187.4 | 219.0598 | 210 | 198.4 | 226.5 | 203.4 | 478.4 | 26.1 | 21 | 51.9 | 4.3 | 244.5 | 9.8 | 248.5 | 805.3 | 807.8 | 221.5 | 705.3 | 423.1 | 586.9 | 797.8 | 308.1 | 623.9 | 96.3 | 226.1 | 32.7 | 225.4 | 208.6 | 29.6 | 114.6 | 108.9 | 66.8
421 | 214 | 468.4 | 187.36 | 219.013 | 210.1 | 198.7 | 226.9 | 203.5 | 477.4 | 26.2 | 21 | 52 | 4.8 | 241.8 | 9.7 | 249.3 | 804.3 | 793.8 | 222.2 | 699.9 | 425.8 | 581.7 | 794.8 | 308.8 | 623.4 | 96.7 | 226.3 | 32.9 | 225.2 | 209.3 | 29.8 | 114.9 | 109.4 | 67
422 | 215 | 467.8 | 187.12 | 218.7325 | 210.1 | 198.3 | 226.2 | 203.9 | 477.9 | 26.2 | 21 | 52.1 | 4.7 | 242 | 8.9 | 250.1 | 807.3 | 804 | 222.9 | 698.4 | 428.1 | 581.6 | 795.8 | 309.5 | 623.7 | 97.1 | 226.6 | 33 | 224.2 | 209.6 | 29.9 | 115.2 | 109.8 | 67.3
423 | 216 | 469.4 | 187.76 | 219.4806 | 209.3 | 197.5 | 225.6 | 204.4 | 477.8 | 26.3 | 21 | 52.2 | 4.6 | 246.5 | 8.2 | 250.8 | 806.4 | 808.6 | 223.7 | 703.4 | 430.5 | 585 | 796.7 | 310.3 | 625.3 | 97.4 | 226.9 | 33.1 | 224.2 | 210 | 30 | 115.6 | 110.3 | 67.5
424 | 217 | 468.8 | 187.52 | 219.2001 | 208.5 | 197.5 | 225.9 | 204.7 | 479.2 | 26.4 | 21 | 52.2 | 4.7 | 253.7 | 8.2 | 251.4 | 803.9 | 789.9 | 224.4 | 704.2 | 432.8 | 588 | 800.7 | 311.1 | 624.6 | 97.8 | 227.2 | 33.2 | 224.2 | 209.9 | 30.1 | 115.9 | 110.8 | 67.7
425 | 218 | 469.4 | 187.76 | 219.4806 | 208.4 | 197.3 | 226.1 | 205.3 | 472.9 | 26.4 | 21 | 52.3 | 4.3 | 234.9 | 8.9 | 252.1 | 805.1 | 775.5 | 225.2 | 699.3 | 435.3 | 584.4 | 789.9 | 311.8 | 622.4 | 98.2 | 227.2 | 33.4 | 223.9 | 210 | 30.3 | 116.3 | 111.3 | 68
426 | 219 | 468.4 | 187.36 | 219.013 | 208.5 | 197.7 | 226.4 | 204.7 | 473.5 | 26.5 | 21 | 52.4 | 3.7 | 254.3 | 9.4 | 252.6 | 804 | 794.1 | 225.8 | 701.1 | 437.7 | 592.5 | 794.3 | 312.6 | 623.7 | 98.5 | 227.2 | 33.5 | 224.2 | 210 | 30.4 | 116.7 | 111.8 | 68.2
427 | 220 | 467.4 | 186.96 | 218.5455 | 208 | 197.8 | 226.6 | 203.9 | 469.6 | 26.5 | 21 | 52.6 | 3.8 | 247.9 | 9.8 | 253.2 | 801.1 | 802.8 | 226.4 | 706.2 | 440 | 596.1 | 782.2 | 313.2 | 626.1 | 98.9 | 227.3 | 33.6 | 224.1 | 210.3 | 30.5 | 117.1 | 112.2 | 68.5
428 | 221 | 467.4 | 186.96 | 218.5455 | 207.6 | 198.1 | 226.3 | 203.4 | 473.3 | 26.6 | 21 | 52.7 | 4.2 | 255.5 | 12 | 253.8 | 801.6 | 813.9 | 227.1 | 706.7 | 442.3 | 603.6 | 796.9 | 314 | 628.5 | 99.2 | 227.6 | 33.8 | 223.6 | 210.2 | 30.7 | 117.5 | 112.7 | 68.8
429 | 222 | 467 | 186.8 | 218.3584 | 207.3 | 198.2 | 225.4 | 203.2 | 477.3 | 26.6 | 21 | 52.9 | 4.8 | 251.4 | 13.4 | 254.6 | 801.9 | 824.7 | 227.7 | 710.2 | 444.5 | 611.5 | 801.7 | 314.9 | 630.1 | 99.6 | 227.8 | 33.9 | 223 | 210.3 | 30.8 | 117.9 | 113.2 | 69
430 | 223 | 467.3 | 186.92 | 218.4987 | 206.6 | 198.9 | 225.1 | 202.9 | 478.2 | 26.7 | 21 | 53 | 3.9 | 262.3 | 14.4 | 255.4 | 797.8 | 822.2 | 228.4 | 715 | 446.9 | 616.9 | 798.6 | 315.6 | 634.3 | 99.9 | 227.7 | 34 | 221.8 | 210.5 | 30.9 | 118.2 | 113.8 | 69.3
431 | 224 | 466.4 | 186.56 | 218.0779 | 206 | 199.9 | 225.5 | 202.6 | 477 | 26.7 | 21 | 53.1 | 4.3 | 267.2 | 15 | 256.4 | 795.5 | 822.8 | 229.1 | 711.4 | 449.2 | 617.7 | 804.3 | 316.4 | 635 | 100.2 | 227.8 | 34.2 | 221.1 | 211.1 | 31.1 | 118.5 | 114.4 | 69.5
432 | 225 | 467 | 186.8 | 218.3584 | 206.4 | 200.3 | 225.6 | 202.6 | 475.2 | 26.8 | 21 | 53.2 | 3.7 | 269.3 | 14.6 | 257.5 | 791.5 | 833.7 | 229.7 | 712.1 | 451.6 | 616.6 | 804.3 | 317.2 | 635.5 | 100.6 | 228 | 34.3 | 220.6 | 211.7 | 31.2 | 119 | 114.9 | 69.7
433 | 226 | 467.5 | 187 | 218.5922 | 207.7 | 199.9 | 225.6 | 203 | 465.2 | 26.8 | 21 | 53.3 | 4.2 | 258.2 | 13.3 | 258.6 | 794.2 | 845.2 | 230.4 | 717.5 | 453.8 | 617.4 | 803.6 | 317.9 | 637.4 | 100.9 | 227.8 | 34.4 | 220.3 | 212.2 | 31.3 | 119.4 | 115.3 | 70
434 | 227 | 467.8 | 187.12 | 218.7325 | 208.2 | 199.7 | 224.9 | 203 | 462.9 | 27 | 21 | 53.4 | 4.3 | 263.9 | 11.5 | 259.7 | 793.9 | 843.7 | 231.1 | 718.8 | 456.2 | 619.3 | 808.4 | 318.6 | 638.7 | 101.2 | 227.8 | 34.6 | 220.6 | 212.5 | 31.4 | 119.9 | 115.8 | 70.2
435 | 228 | 468 | 187.2 | 218.826 | 208.8 | 200.1 | 224.3 | 203.6 | 464.3 | 27.1 | 21 | 53.5 | 3.9 | 247.3 | 11.6 | 260.9 | 795.9 | 840.3 | 231.8 | 716.2 | 458.6 | 614.3 | 803.5 | 319.3 | 638.5 | 101.5 | 228.2 | 34.7 | 220.4 | 212.6 | 31.6 | 120.3 | 116.3 | 70.4
436 | 229 | 467.3 | 186.92 | 218.4987 | 209.2 | 199.9 | 224.3 | 203.9 | 459.1 | 27.2 | 21 | 53.6 | 4.5 | 256.5 | 11.7 | 262.2 | 798.8 | 839.9 | 232.5 | 717.6 | 460.8 | 616.2 | 803.2 | 320 | 641.7 | 101.8 | 228.4 | 34.8 | 220.1 | 212.7 | 31.7 | 120.5 | 116.8 | 70.7
437 | 230 | 467.6 | 187.04 | 218.639 | 209.4 | 200.4 | 225.2 | 204.1 | 462.2 | 27.3 | 21 | 53.6 | 4.9 | 251.5 | 11.8 | 263.6 | 794.7 | 844.5 | 233.3 | 722.2 | 463.1 | 619.5 | 805.7 | 320.8 | 642.9 | 102.1 | 228.3 | 35 | 219.8 | 213.1 | 31.8 | 120.8 | 117.2 | 70.9
438 | 231 | 467.7 | 187.08 | 218.6857 | 209.1 | 202 | 225.7 | 204.1 | 457.9 | 27.3 | 21 | 53.7 | 4.9 | 249.9 | 12.1 | 265 | 790.4 | 842.8 | 234.1 | 726.4 | 465.6 | 615.2 | 798.7 | 321.4 | 642.7 | 102.4 | 228.4 | 35.1 | 220.5 | 213.4 | 31.9 | 121.1 | 117.8 | 71.1
439 | 232 | 467.6 | 187.04 | 218.639 | 209.9 | 202.7 | 225 | 203.6 | 452.6 | 27.3 | 21 | 53.8 | 5.2 | 255.7 | 11.4 | 266.3 | 785.1 | 841.4 | 234.8 | 732.3 | 467.9 | 621.7 | 807.1 | 322.2 | 644 | 102.7 | 228.5 | 35.2 | 220.9 | 213.7 | 32.1 | 121.4 | 118.3 | 71.3
440 | 233 | 469.3 | 187.72 | 219.4339 | 211.2 | 202.7 | 225.2 | 203.6 | 462.3 | 27.3 | 21 | 53.9 | 5.6 | 259.3 | 10.2 | 267.6 | 783.3 | 834.2 | 235.5 | 734.5 | 470.1 | 629.9 | 813.2 | 322.9 | 645 | 103 | 228.7 | 35.4 | 221.4 | 214.1 | 32.2 | 121.6 | 118.8 | 71.6
441 | 234 | 467.8 | 187.12 | 218.7325 | 212 | 202.9 | 224.9 | 203.8 | 476.6 | 27.3 | 21 | 54.1 | 6.1 | 270.3 | 10.1 | 268.9 | 784.8 | 828.6 | 236.1 | 736.3 | 472.3 | 637.3 | 819.3 | 323.7 | 646.2 | 103.3 | 229 | 35.5 | 220.8 | 214.6 | 32.3 | 122.2 | 119.2 | 71.9
442 | 235 | 467.2 | 186.88 | 218.452 | 212.7 | 204.6 | 225.3 | 204.7 | 488.8 | 27.4 | 21 | 54.2 | 5.7 | 250.9 | 10.1 | 270.1 | 782.2 | 831.6 | 236.7 | 741.9 | 474.6 | 642 | 819.9 | 324.5 | 648 | 103.6 | 229.3 | 35.6 | 220.9 | 214.7 | 32.5 | 122.7 | 119.8 | 72.1
443 | 236 | 467.7 | 187.08 | 218.6857 | 211.9 | 205.1 | 226.1 | 205 | 494.9 | 27.4 | 21 | 54.3 | 6.2 | 255 | 10.6 | 271.4 | 780 | 841.9 | 237.4 | 745 | 476.9 | 644.3 | 817.6 | 325.3 | 650.1 | 103.9 | 229.9 | 35.8 | 220.4 | 214.7 | 32.6 | 122.9 | 120.2 | 72.4
444 | 237 | 466.8 | 186.72 | 218.2649 | 212.2 | 203.9 | 226.2 | 204.8 | 487.6 | 27.4 | 21 | 54.4 | 5.5 | 248.8 | 12.7 | 272.9 | 781 | 853.4 | 238.1 | 741.8 | 479.1 | 647.6 | 813.4 | 326 | 650.3 | 104.2 | 230.6 | 35.9 | 220.5 | 214.9 | 32.7 | 123.3 | 120.7 | 72.7
445 | 238 | 466.1 | 186.44 | 217.9376 | 212 | 204 | 226.1 | 204.6 | 483.1 | 27.5 | 21 | 54.4 | 4.8 | 248.1 | 14 | 274.2 | 779.7 | 851.9 | 238.9 | 739.5 | 481.1 | 647.6 | 813.5 | 326.8 | 650.3 | 104.5 | 230.9 | 36 | 221.7 | 215.6 | 32.9 | 123.6 | 121.2 | 73
446 | 239 | 467.2 | 186.88 | 218.452 | 212.3 | 204.5 | 226.2 | 204.4 | 481.2 | 27.6 | 21 | 54.5 | 4.5 | 251.4 | 14.1 | 275.6 | 779.9 | 850.1 | 239.7 | 737.9 | 483 | 643.5 | 814 | 327.5 | 651.2 | 104.8 | 231.3 | 36.2 | 222.2 | 216.5 | 33 | 123.9 | 121.8 | 73.3
447 | 240 | 466.6 | 186.64 | 218.1714 | 213.6 | 205.2 | 226 | 204.4 | 488.6 | 27.6 | 21 | 54.5 | 5.2 | 245.8 | 15.4 | 276.9 | 779.6 | 846.1 | 240.5 | 737.3 | 484.9 | 641.2 | 816.7 | 328.3 | 652.2 | 105.1 | 231.7 | 36.3 | 222.6 | 217.2 | 33.1 | 124.5 | 122.4 | 73.6
448 | 241 | 466.4 | 186.56 | 218.0779 | 213.9 | 205.8 | 225.6 | 203.8 | 487.3 | 27.7 | 21 | 54.6 | 4.9 | 247 | 15.9 | 278.3 | 775.6 | 856.3 | 241.3 | 745.5 | 486.7 | 645.6 | 816.2 | 328.9 | 653.9 | 105.4 | 232 | 36.4 | 222.2 | 216.8 | 33.3 | 124.9 | 123 | 73.8
449 | 242 | 467.2 | 186.88 | 218.452 | 213.3 | 206.2 | 225.1 | 203.5 | 485.8 | 27.7 | 21 | 54.6 | 4.9 | 252.7 | 15.5 | 279.7 | 773.2 | 862.3 | 242.2 | 753.7 | 488.6 | 652.1 | 813.2 | 329.7 | 658.6 | 105.7 | 232.1 | 36.6 | 223.1 | 217 | 33.4 | 125.2 | 123.5 | 74
450 | 243 | 466.3 | 186.52 | 218.0311 | 212.4 | 206.8 | 224.9 | 203.2 | 492.1 | 27.7 | 21 | 54.6 | 5.4 | 252.9 | 15.7 | 281.2 | 774.1 | 865.4 | 243.1 | 759.8 | 490.4 | 657.9 | 818.5 | 330.4 | 662.3 | 106 | 231.8 | 36.7 | 223.9 | 217.2 | 33.5 | 125.6 | 123.9 | 74.3
451 | 244 | 468.9 | 187.56 | 219.2468 | 211.2 | 207.1 | 223.7 | 202.7 | 492.2 | 27.7 | 21 | 54.7 | 6.7 | 253.1 | 15 | 282.7 | 774.8 | 855.7 | 243.9 | 762.7 | 492.4 | 664.2 | 815.8 | 331.1 | 667 | 106.3 | 232 | 36.8 | 224.2 | 217.2 | 33.7 | 125.9 | 124.3 | 74.5
452 | 245 | 472.4 | 188.96 | 220.8834 | 209.7 | 207.2 | 223.5 | 202.2 | 489.1 | 27.7 | 21 | 54.8 | 5.9 | 254.4 | 14.8 | 284.2 | 774.1 | 850.9 | 244.8 | 770.3 | 495 | 672.7 | 800.4 | 331.7 | 672.6 | 106.6 | 232.4 | 37 | 224.5 | 217 | 33.8 | 126.2 | 124.8 | 74.7
453 | 246 | 471.6 | 188.64 | 220.5093 | 208.7 | 207.5 | 224.6 | 201.9 | 487.1 | 27.6 | 20.9 | 54.9 | 5.8 | 251.2 | 13.8 | 285.9 | 771.2 | 862.7 | 245.7 | 775.1 | 497.7 | 682.7 | 805 | 332.4 | 677.7 | 106.9 | 232.7 | 37.1 | 223.9 | 216.6 | 34 | 126.5 | 125.4 | 75
454 | 247 | 471.6 | 188.64 | 220.5093 | 209 | 207.4 | 225.4 | 201.9 | 490.7 | 27.7 | 21 | 55 | 5.6 | 254.9 | 13.4 | 287.5 | 769.3 | 864.2 | 246.7 | 778.3 | 500.8 | 685.6 | 810.5 | 333 | 680.6 | 107.2 | 232.9 | 37.2 | 223.8 | 216.6 | 34.1 | 126.8 | 126.1 | 75.2
455 | 248 | 469.9 | 187.96 | 219.7144 | 210.2 | 206.5 | 225.9 | 201.5 | 492.1 | 27.7 | 20.9 | 55.1 | 5 | 250.1 | 13.5 | 289 | 766.4 | 863.2 | 247.6 | 782.9 | 503.9 | 688.7 | 812.6 | 333.7 | 683.9 | 107.5 | 233.2 | 37.4 | 224.2 | 216.5 | 34.2 | 127.3 | 126.8 | 75.5
456 | 249 | 470.4 | 188.16 | 219.9482 | 211.4 | 205.7 | 226.2 | 201.1 | 491.9 | 27.7 | 20.9 | 55.2 | 5.2 | 251 | 14.5 | 290.5 | 765.6 | 862.8 | 248.6 | 785.9 | 507.4 | 694.2 | 815.6 | 334.4 | 688.1 | 107.8 | 233.2 | 37.5 | 224.9 | 216.4 | 34.4 | 127.6 | 127.4 | 75.7
457 | 250 | 469.2 | 187.68 | 219.3871 | 212.3 | 205 | 226.9 | 201.2 | 495.5 | 27.7 | 20.9 | 55.4 | 5.1 | 251.7 | 14.8 | 292 | 766 | 873.7 | 249.7 | 787.6 | 511 | 700.8 | 817.3 | 335.1 | 692.4 | 108.1 | 233.2 | 37.6 | 225.7 | 216.5 | 34.5 | 127.9 | 128 | 75.9
458 | 251 | 468.5 | 187.4 | 219.0598 | 213.3 | 205.3 | 227.7 | 201.4 | 501.1 | 27.7 | 20.9 | 55.5 | 5 | 256.5 | 14.9 | 293.5 | 768.3 | 875.9 | 250.8 | 784.6 | 514.7 | 700.5 | 820.4 | 335.8 | 692.5 | 108.4 | 233.4 | 37.8 | 226.3 | 216.6 | 34.6 | 128.2 | 128.6 | 76.2
459 | 252 | 468.8 | 187.52 | 219.2001 | 213.8 | 205.5 | 227.7 | 201.2 | 498 | 27.8 | 20.9 | 55.6 | 4.8 | 260.2 | 14.4 | 295 | 770.8 | 869.3 | 251.9 | 783 | 518.4 | 695.9 | 818.2 | 336.6 | 692.7 | 108.6 | 233.7 | 37.9 | 226.8 | 216.6 | 34.8 | 128.6 | 129.2 | 76.3
460 | 253 | 469.1 | 187.64 | 219.3403 | 214.8 | 205.7 | 227.4 | 201.5 | 492.8 | 27.9 | 20.9 | 55.5 | 4.2 | 261.2 | 14.6 | 296.6 | 771.9 | 859.1 | 252.9 | 783.4 | 521.9 | 692.4 | 811.4 | 337.3 | 694.2 | 108.9 | 234 | 38.1 | 226.8 | 216.7 | 34.9 | 128.9 | 129.8 | 76.7
461 | 254 | 469.2 | 187.68 | 219.3871 | 215.7 | 206.7 | 227.8 | 202.2 | 485.9 | 28.1 | 20.9 | 55.5 | 4.6 | 262.6 | 14.4 | 298.1 | 772.6 | 855.9 | 254.1 | 779 | 525.2 | 687.3 | 807.7 | 338 | 694.2 | 109.2 | 234.3 | 38.2 | 226.3 | 217.3 | 35 | 129.3 | 130.3 | 76.9
462 | 255 | 469 | 187.6 | 219.2936 | 216.2 | 207.3 | 228.5 | 202.9 | 483.1 | 28.3 | 20.9 | 55.5 | 4.7 | 264.8 | 13.8 | 299.8 | 769.9 | 856 | 255.2 | 782.6 | 528.8 | 692.2 | 809.3 | 338.7 | 696.2 | 109.5 | 234 | 38.3 | 226.2 | 217.5 | 35.2 | 129.7 | 130.8 | 76.9
463 | 256 | 468.9 | 187.56 | 219.2468 | 217.9 | 206.5 | 228.2 | 202.2 | 481.2 | 28.3 | 20.9 | 55.6 | 4.4 | 261.9 | 13.9 | 301.5 | 771.5 | 855.8 | 256.3 | 786.9 | 532.8 | 697.1 | 810.1 | 339.4 | 698.8 | 109.8 | 234 | 38.5 | 226.2 | 217.6 | 35.3 | 130.1 | 131.4 | 77.4
464 | 257 | 469.3 | 187.72 | 219.4339 | 218.7 | 205.6 | 228.4 | 202.1 | 479.7 | 28.4 | 20.9 | 55.6 | 3.9 | 255.8 | 14 | 303.3 | 772.3 | 862.7 | 257.5 | 789.1 | 536.8 | 701.1 | 818.5 | 340.2 | 703.5 | 110 | 233.8 | 38.6 | 226.7 | 217.5 | 35.4 | 130.4 | 132 | 77.6
465 | 258 | 467.5 | 187 | 218.5922 | 219.5 | 205.7 | 228.8 | 202.1 | 480 | 28.5 | 20.9 | 55.6 | 4.8 | 263.6 | 13.3 | 305.1 | 773.4 | 863.9 | 258.8 | 786.7 | 540.4 | 703.3 | 820.5 | 340.9 | 703.9 | 110.3 | 233.9 | 38.7 | 227.5 | 217.6 | 35.6 | 130.7 | 132.5 | 77.9
466 | 259 | 466.7 | 186.68 | 218.2182 | 219.4 | 207 | 228.1 | 202.5 | 479.3 | 28.7 | 20.9 | 55.6 | 4.5 | 264.6 | 12.5 | 307 | 773.5 | 860.4 | 260.2 | 786.1 | 544.1 | 708.6 | 821.3 | 341.6 | 705.2 | 110.6 | 234.3 | 38.9 | 227.4 | 217.6 | 35.7 | 131.1 | 133 | 78.1
467 | 260 | 468.1 | 187.24 | 218.8728 | 219.5 | 207.8 | 228.2 | 203.1 | 481.5 | 28.8 | 20.9 | 55.6 | 4 | 259.2 | 11 | 308.9 | 775.1 | 864.3 | 261.5 | 785.8 | 547.9 | 707.6 | 820.5 | 342.4 | 706.2 | 110.8 | 234.5 | 39 | 228 | 217.8 | 35.8 | 131.4 | 133.6 | 78.3
468 | 261 | 469.3 | 187.72 | 219.4339 | 219.7 | 208.7 | 228.8 | 203.5 | 483.7 | 28.8 | 20.9 | 55.6 | 4.2 | 262.2 | 9.8 | 311.1 | 773.4 | 864.3 | 263 | 784.8 | 551.4 | 705.7 | 819.4 | 343.1 | 706.8 | 111.1 | 234.6 | 39.2 | 228.5 | 218.2 | 36 | 131.9 | 134.2 | 78.6
469 | 262 | 468.4 | 187.36 | 219.013 | 219.8 | 210.1 | 229.5 | 203.8 | 494.7 | 28.9 | 20.9 | 55.7 | 4.9 | 268.2 | 8.6 | 313.3 | 771.2 | 855 | 264.6 | 782.1 | 554.9 | 705.6 | 823.1 | 343.8 | 706.6 | 111.3 | 234.4 | 39.3 | 229.1 | 218.4 | 36.1 | 132.2 | 134.7 | 78.8
470 | 263 | 467.9 | 187.16 | 218.7793 | 220.2 | 211.2 | 229.5 | 204.4 | 494.8 | 28.9 | 20.9 | 55.8 | 5.3 | 259.7 | 7.8 | 315.7 | 770.7 | 853.1 | 266 | 785.1 | 558.6 | 700.8 | 827.2 | 344.6 | 707.3 | 111.6 | 234.4 | 39.4 | 229.5 | 218.5 | 36.2 | 132.5 | 135.2 | 79.1
471 | 264 | 466.3 | 186.52 | 218.0311 | 220.9 | 211.5 | 229.6 | 204.9 | 499.7 | 29 | 20.9 | 55.8 | 5.1 | 255 | 8.8 | 318.1 | 770.2 | 857.8 | 267.5 | 788 | 562 | 700.7 | 833.8 | 345.4 | 707.9 | 111.8 | 234.7 | 39.6 | 230.2 | 218.9 | 36.4 | 132.9 | 135.7 | 79.3
472 | 265 | 467.3 | 186.92 | 218.4987 | 221.6 | 212.6 | 229.6 | 205.9 | 511 | 29 | 20.9 | 56 | 4.8 | 240.3 | 8.2 | 320.5 | 769.2 | 843.6 | 269 | 779.6 | 565.5 | 700.1 | 836.6 | 346.1 | 705.6 | 112.1 | 235.3 | 39.7 | 229.6 | 219.5 | 36.5 | 133.3 | 136.2 | 79.6
473 | 266 | 467.6 | 187.04 | 218.639 | 222.3 | 213.9 | 230.4 | 207.1 | 524.3 | 29 | 20.9 | 56.2 | 4.8 | 254.2 | 7.9 | 323.2 | 766.1 | 833 | 270.5 | 769.9 | 569.1 | 701.6 | 841.5 | 346.8 | 703.5 | 112.3 | 235.9 | 39.9 | 229.7 | 220.4 | 36.6 | 133.8 | 136.8 | 79.9
474 | 267 | 467.7 | 187.08 | 218.6857 | 223.4 | 214.5 | 231.4 | 208.1 | 529.9 | 29.1 | 20.9 | 56.3 | 5.3 | 236.1 | 9.1 | 325.8 | 762.7 | 827.4 | 271.9 | 765.1 | 572.6 | 696.1 | 842.9 | 347.5 | 702.5 | 112.6 | 236.2 | 40 | 229.4 | 221 | 36.7 | 134.2 | 137.4 | 80.2
475 | 268 | 467.3 | 186.92 | 218.4987 | 224.2 | 214.4 | 232.8 | 208.7 | 527.2 | 29.2 | 20.9 | 56.5 | 5.8 | 258.4 | 8.6 | 328.3 | 762.5 | 830.5 | 273.5 | 761.5 | 575.3 | 689.7 | 839.7 | 348.2 | 701.2 | 112.8 | 237.3 | 40.1 | 229.1 | 221.5 | 36.9 | 134.6 | 137.9 | 80.5
476 | 269 | 466.9 | 186.76 | 218.3117 | 223.6 | 214.2 | 233.7 | 209.6 | 531.1 | 29.3 | 20.9 | 56.7 | 5.6 | 250.7 | 8.4 | 330.7 | 761 | 831.2 | 274.9 | 762.9 | 578.1 | 691 | 842 | 348.9 | 700.7 | 113.1 | 238.5 | 40.3 | 229.3 | 221.9 | 37 | 134.9 | 138.4 | 80.8
477 | 270 | 468.9 | 187.56 | 219.2468 | 223.5 | 214.2 | 233.9 | 210.5 | 529.7 | 29.4 | 20.9 | 56.8 | 4.8 | 261.5 | 8.6 | 333.1 | 759.5 | 833.3 | 276.4 | 763.2 | 581 | 687.7 | 840.2 | 349.7 | 698.9 | 113.4 | 239.1 | 40.4 | 230.4 | 222.3 | 37.1 | 135.2 | 138.9 | 81.1
478 | 271 | 470.9 | 188.36 | 220.182 | 223.8 | 214.5 | 232.8 | 211.5 | 527.2 | 29.5 | 20.9 | 56.9 | 5.2 | 258.5 | 10.3 | 335.4 | 759 | 822.5 | 277.7 | 767.2 | 583.5 | 683.7 | 831.8 | 350.4 | 700.9 | 113.7 | 239 | 40.5 | 231.5 | 222.7 | 37.3 | 135.6 | 139.4 | 81.4
479 | 272 | 470 | 188 | 219.7612 | 223.9 | 215.1 | 231.2 | 211.7 | 511.3 | 29.6 | 20.9 | 57 | 5.1 | 251.7 | 12.3 | 337.7 | 755.5 | 816.1 | 279.1 | 777 | 585.7 | 687 | 825 | 351.2 | 705.4 | 114 | 239.2 | 40.7 | 231.8 | 223.5 | 37.4 | 136.2 | 139.9 | 81.7
480 | 273 | 469.4 | 187.76 | 219.4806 | 223.1 | 215 | 231.1 | 212.1 | 498.4 | 29.7 | 20.9 | 57.1 | 4.7 | 249.6 | 13.6 | 339.7 | 751.2 | 806 | 280.6 | 783.2 | 587.9 | 686.5 | 815.7 | 352 | 709.5 | 114.3 | 239.3 | 40.8 | 231.9 | 224.7 | 37.5 | 136.6 | 140.4 | 82
481 | 274 | 469.6 | 187.84 | 219.5741 | 222.7 | 214.7 | 230.9 | 211.9 | 492.1 | 29.7 | 20.9 | 57.1 | 4.5 | 248.5 | 14.3 | 341.5 | 749 | 807.1 | 281.9 | 787.7 | 589.7 | 686 | 814.3 | 352.8 | 711.8 | 114.5 | 239.5 | 41 | 231.3 | 225.5 | 37.7 | 137.2 | 141 | 82.2
482 | 275 | 470.6 | 188.24 | 220.0417 | 222.7 | 214.2 | 231.7 | 211.4 | 490.6 | 29.7 | 20.9 | 57.1 | 5.4 | 248.8 | 15.4 | 343 | 747.1 | 824.3 | 283.4 | 787.9 | 591.4 | 688.9 | 824.1 | 353.5 | 711.7 | 114.8 | 239.7 | 41.1 | 230.7 | 225.9 | 37.8 | 137.7 | 141.5 | 82.5
483 | 276 | 469.5 | 187.8 | 219.5274 | 222.1 | 214.2 | 231 | 211.3 | 498.4 | 29.8 | 20.9 | 57.2 | 5.7 | 252.5 | 15.5 | 344.4 | 745.7 | 832.2 | 285 | 787.5 | 593.7 | 690.3 | 830.6 | 354.2 | 711.4 | 115.1 | 239.9 | 41.3 | 231 | 226 | 37.9 | 137.9 | 142.1 | 82.7
484 | 277 | 468.2 | 187.28 | 218.9195 | 220.5 | 214.1 | 229.9 | 211.2 | 499.1 | 29.8 | 20.9 | 57.3 | 6 | 251.8 | 15.1 | 345.6 | 746 | 835.3 | 286.4 | 781.3 | 596.2 | 688 | 829.3 | 355 | 710.1 | 115.4 | 240.4 | 41.4 | 231.3 | 225.7 | 38 | 138.1 | 142.8 | 83
485 | 278 | 468.9 | 187.56 | 219.2468 | 220.4 | 214.4 | 229.8 | 211.2 | 498.9 | 29.9 | 20.9 | 57.4 | 5.2 | 252.7 | 14.4 | 346.8 | 746.7 | 839.2 | 287.8 | 777.7 | 598.7 | 684.5 | 832.9 | 355.6 | 707.3 | 115.7 | 240.9 | 41.5 | 231.9 | 225.5 | 38.2 | 138.4 | 143.3 | 83.2
486 | 279 | 469.1 | 187.64 | 219.3403 | 220.7 | 214.7 | 230.8 | 211.6 | 502.9 | 30 | 20.9 | 57.4 | 4.5 | 253.4 | 14.3 | 348.1 | 746.6 | 842 | 289.2 | 774.2 | 601.1 | 681 | 832.5 | 356.2 | 704 | 116 | 241.3 | 41.7 | 231.3 | 225.6 | 38.3 | 138.7 | 143.9 | 83.5
487 | 280 | 469.4 | 187.76 | 219.4806 | 220.7 | 215.1 | 231.7 | 212.3 | 494.1 | 30.1 | 20.9 | 57.4 | 4.9 | 259.5 | 14.6 | 349.5 | 746.3 | 827.7 | 290.7 | 769.1 | 604 | 680.1 | 835.5 | 356.8 | 703.2 | 116.2 | 241.7 | 41.8 | 231.4 | 225.4 | 38.4 | 139.1 | 144.4 | 83.7
488 | 281 | 469.1 | 187.64 | 219.3403 | 220.4 | 216.2 | 232.4 | 212.6 | 496.6 | 30.2 | 20.9 | 57.5 | 4.6 | 258.2 | 13.7 | 350.7 | 747.3 | 816.1 | 292.2 | 765 | 607.2 | 675.4 | 833.1 | 357.4 | 701.1 | 116.5 | 242.3 | 42 | 231.2 | 225.2 | 38.5 | 139.4 | 144.8 | 84
489 | 282 | 467.8 | 187.12 | 218.7325 | 220.5 | 216 | 233.6 | 213 | 506.1 | 30.2 | 20.9 | 57.6 | 4.9 | 261.5 | 12.3 | 351.7 | 747.4 | 812.4 | 293.6 | 762.2 | 610.4 | 673 | 839.3 | 357.9 | 699.3 | 116.8 | 243.1 | 42.1 | 231.1 | 225.3 | 38.7 | 139.8 | 145.4 | 84.2
490 | 283 | 469.6 | 187.84 | 219.5741 | 220 | 215.8 | 234.9 | 213.9 | 512.7 | 30.3 | 20.9 | 57.6 | 4.6 | 255.6 | 12 | 352.3 | 747.9 | 813.9 | 295 | 762.5 | 613.5 | 670.3 | 838.3 | 358.5 | 697.6 | 117.1 | 243.8 | 42.2 | 231.4 | 225.1 | 38.8 | 140.1 | 145.9 | 84.5
491 | 284 | 469.7 | 187.88 | 219.6209 | 219.2 | 216.3 | 235.5 | 214.5 | 519.8 | 30.3 | 20.9 | 57.7 | 4.6 | 264.4 | 12.1 | 352.7 | 746.5 | 822.5 | 296.4 | 762.4 | 616.5 | 671.1 | 837.1 | 359.2 | 696.2 | 117.4 | 244.2 | 42.4 | 231.9 | 225.4 | 38.9 | 140.4 | 146.5 | 84.7
492 | 285 | 469.6 | 187.84 | 219.5741 | 218.5 | 216.1 | 236.3 | 214.4 | 527.2 | 30.3 | 20.9 | 57.8 | 4.4 | 263.2 | 11.8 | 352.9 | 745.1 | 825.6 | 298 | 763.4 | 619.5 | 672.8 | 835.9 | 359.8 | 695.7 | 117.7 | 244.6 | 42.5 | 233.4 | 225.4 | 39 | 140.8 | 147.1 | 85
493 | 286 | 469.4 | 187.76 | 219.4806 | 218.3 | 216.1 | 237.3 | 214.6 | 524.7 | 30.3 | 20.9 | 57.9 | 4.5 | 260.8 | 11.4 | 353 | 745.7 | 834.6 | 299.7 | 766.3 | 622.2 | 672.6 | 839.3 | 360.5 | 696 | 118.1 | 244.8 | 42.7 | 233.8 | 225.3 | 39.1 | 141.2 | 147.7 | 85.3
494 | 287 | 469 | 187.6 | 219.2936 | 217 | 216.4 | 238 | 215.2 | 518.9 | 30.3 | 20.9 | 58 | 4.3 | 255.1 | 11.3 | 352.9 | 744.9 | 836.2 | 301.3 | 769.9 | 624.9 | 674.8 | 841.4 | 361.2 | 696.6 | 118.4 | 244.9 | 42.8 | 234.1 | 225.3 | 39.2 | 141.6 | 148.3 | 85.6
495 | 288 | 468.7 | 187.48 | 219.1533 | 216 | 216.2 | 237.1 | 215.5 | 515.1 | 30.3 | 20.9 | 58.1 | 4.5 | 258.1 | 12.3 | 352.8 | 745.9 | 835.9 | 303.3 | 773 | 627.2 | 673.3 | 839.7 | 361.9 | 696.5 | 118.7 | 244.8 | 43 | 233.8 | 225.6 | 39.4 | 142 | 148.8 | 85.8
496 | 289 | 469 | 187.6 | 219.2936 | 216.7 | 216.6 | 236.4 | 215.6 | 507.1 | 30.3 | 20.9 | 58.1 | 4.8 | 258.8 | 12 | 352.6 | 746.6 | 832.9 | 305.2 | 772.7 | 629.7 | 670 | 838.4 | 362.6 | 696.4 | 119.1 | 244.7 | 43.1 | 233.6 | 225.5 | 39.5 | 142.4 | 149.4 | 86.1
497 | 290 | 469.1 | 187.64 | 219.3403 | 217.6 | 217.2 | 237.4 | 215.9 | 503.2 | 30.3 | 20.9 | 58.2 | 4.4 | 252.5 | 10.8 | 352.4 | 748.8 | 835.3 | 307.2 | 772.2 | 632 | 672.6 | 838.6 | 363.2 | 697.3 | 119.4 | 244.9 | 43.2 | 234 | 225.7 | 39.6 | 142.7 | 150 | 86.4
498 | 291 | 469.1 | 187.64 | 219.3403 | 218.6 | 217.4 | 238.3 | 215.4 | 500.7 | 30.4 | 20.9 | 58.2 | 4.3 | 251.7 | 10.5 | 351.8 | 748.6 | 838.7 | 309.3 | 777.1 | 634.3 | 673.1 | 835.7 | 363.8 | 699.4 | 119.7 | 245 | 43.4 | 234.4 | 226.1 | 39.7 | 143.1 | 150.5 | 86.7
499 | 292 | 468.9 | 187.56 | 219.2468 | 220.2 | 217.8 | 238.7 | 214.5 | 498.1 | 30.4 | 20.9 | 58.3 | 4.7 | 263.9 | 10.3 | 351 | 747.3 | 836.1 | 311.2 | 777.8 | 636.5 | 670.5 | 836.4 | 364.4 | 698.9 | 120 | 245.1 | 43.5 | 236.3 | 226.3 | 39.8 | 143.5 | 151.1 | 86.9
500 | 293 | 468.6 | 187.44 | 219.1066 | 221.7 | 218.3 | 238.9 | 214.5 | 501.5 | 30.4 | 20.9 | 58.4 | 4.3 | 250.2 | 10 | 350.2 | 746.7 | 838.3 | 313.3 | 778.5 | 638.9 | 673.2 | 836.6 | 365 | 700.1 | 120.3 | 245 | 43.7 | 236.7 | 226.3 | 39.9 | 143.9 | 151.6 | 87.2
501 | 294 | 468.6 | 187.44 | 219.1066 | 222.9 | 218.3 | 238 | 214.9 | 498.2 | 30.4 | 20.9 | 58.4 | 4 | 245.2 | 10.4 | 349.7 | 747.6 | 831.5 | 315.2 | 783.7 | 640.5 | 675.2 | 837.3 | 365.6 | 700.5 | 120.6 | 245.2 | 43.8 | 236.9 | 226.1 | 40 | 144.2 | 152.1 | 87.5
502 | 295 | 467.9 | 187.16 | 218.7793 | 222.3 | 217.6 | 236.7 | 214.6 | 490.1 | 30.5 | 20.9 | 58.5 | 4 | 254.4 | 9.9 | 349.4 | 749.3 | 812 | 317.3 | 791.9 | 641.9 | 676.8 | 833.3 | 366.3 | 702.6 | 120.9 | 245.5 | 43.9 | 237 | 225.8 | 40.1 | 144.6 | 152.7 | 87.8
503 | 296 | 469.1 | 187.64 | 219.3403 | 222.5 | 217.7 | 236.2 | 214.3 | 487.2 | 30.6 | 20.9 | 58.5 | 4.1 | 254.3 | 9.8 | 349.3 | 749.8 | 804.1 | 319.5 | 794.5 | 643.5 | 681 | 823.7 | 367 | 706.1 | 121.2 | 245.6 | 44.1 | 237.2 | 225.9 | 40.2 | 144.9 | 153.2 | 88
504 | 297 | 471.5 | 188.6 | 220.4625 | 223.3 | 218 | 236.8 | 214.8 | 478.5 | 30.7 | 20.9 | 58.5 | 4.3 | 254.9 | 9.8 | 349.5 | 748.9 | 809.4 | 321.5 | 798.6 | 644.9 | 685.2 | 817.6 | 367.6 | 709.9 | 121.5 | 245.8 | 44.2 | 237.3 | 226.1 | 40.3 | 145.3 | 153.8 | 88.2
505 | 298 | 470 | 188 | 219.7612 | 223.8 | 218.4 | 237.8 | 214.8 | 473.9 | 30.7 | 20.8 | 58.6 | 4.4 | 260.7 | 9.6 | 349.9 | 748.3 | 810.7 | 323.8 | 803.5 | 645.9 | 686.8 | 811.1 | 368.4 | 711.5 | 121.8 | 246 | 44.4 | 237.2 | 226 | 40.4 | 145.6 | 154.3 | 88.5
506 | 299 | 469.3 | 187.72 | 219.4339 | 224.4 | 218.3 | 238.2 | 214.6 | 470.4 | 30.8 | 20.8 | 58.7 | 4.3 | 254.6 | 10.7 | 353.6 | 747.8 | 806.2 | 325.4 | 806.1 | 646.9 | 686 | 795.9 | 369.3 | 713.2 | 122.1 | 245.6 | 44.5 | 237.2 | 226.3 | 40.5 | 146.2 | 154.9 | 88.7
507 | 300 | 468.6 | 187.44 | 219.1066 | 225.8 | 217.2 | 238 | 214.2 | 465.6 | 30.8 | 20.8 | 58.8 | 4.1 | 256.1 | 11 | 356.4 | 747.3 | 800.7 | 327.6 | 807.8 | 648.4 | 685.8 | 785.5 | 370.3 | 716.1 | 122.4 | 245.6 | 44.7 | 236.4 | 226.7 | 40.6 | 146.6 | 155.4 | 89
508 | 301 | 468.5 | 187.4 | 219.0598 | 226.3 | 216.7 | 238 | 213.7 | 463.9 | 30.9 | 20.8 | 58.9 | 4.1 | 258.2 | 11.6 | 357.9 | 746.2 | 791.4 | 329.3 | 809.7 | 650 | 686.1 | 786 | 371.4 | 717.5 | 122.6 | 245.4 | 44.8 | 236.1 | 226.9 | 40.7 | 146.9 | 156 | 89.2
509 | 302 | 469.5 | 187.8 | 219.5274 | 228.2 | 217.2 | 238 | 214 | 465.9 | 30.9 | 20.8 | 58.9 | 4.1 | 263 | 11.9 | 359.2 | 746.2 | 792.3 | 331.4 | 813.8 | 650.8 | 690.2 | 795 | 372.6 | 720 | 122.9 | 245 | 44.9 | 235.5 | 227 | 40.8 | 147.3 | 156.5 | 89.5
510 | 303 | 470 | 188 | 219.7612 | 230.2 | 217.5 | 237.5 | 213.9 | 468.7 | 31 | 20.8 | 59 | 4.6 | 262.4 | 11.3 | 360.6 | 747.3 | 797.8 | 332.9 | 815.7 | 651.6 | 689.9 | 802.1 | 374.1 | 720.2 | 123.1 | 244.9 | 45.1 | 234.5 | 226.9 | 40.9 | 147.6 | 157.1 | 89.7
511 | 304 | 469.5 | 187.8 | 219.5274 | 231.1 | 217.4 | 237.2 | 213.8 | 472.1 | 31.2 | 20.8 | 59 | 4.5 | 262.8 | 10.9 | 362.3 | 749.5 | 813.4 | 334.8 | 814.9 | 653 | 689.2 | 813.5 | 376.1 | 719.9 | 123.4 | 244.8 | 45.2 | 234.1 | 227.3 | 41 | 147.9 | 157.7 | 89.9
512 | 305 | 469.6 | 187.84 | 219.5741 | 231.4 | 217.9 | 237.8 | 214.2 | 478.9 | 31.3 | 20.8 | 59.1 | 4.4 | 270.4 | 10.8 | 364.3 | 749.6 | 821.8 | 337 | 813.8 | 654.3 | 691.1 | 813 | 377.8 | 720.7 | 123.6 | 244.9 | 45.4 | 233.8 | 228.2 | 41.1 | 148.5 | 158.2 | 90.2
513 | 306 | 469 | 187.6 | 219.2936 | 231 | 218.9 | 238 | 215.2 | 475.8 | 31.4 | 20.8 | 59.1 | 4.7 | 265.1 | 11 | 367 | 749.6 | 827.8 | 339.2 | 813.3 | 655.4 | 689.8 | 813.1 | 379.1 | 720.4 | 123.9 | 245 | 45.5 | 233 | 228.8 | 41.2 | 148.9 | 158.8 | 90.5
514 | 307 | 468.9 | 187.56 | 219.2468 | 230.5 | 219.5 | 238.5 | 215.9 | 473.9 | 31.5 | 20.8 | 59.1 | 4.5 | 259.3 | 11 | 369.5 | 749.9 | 827.2 | 341 | 817 | 656.3 | 695.7 | 810.2 | 380.2 | 724.8 | 124.1 | 245.1 | 45.7 | 232.6 | 229 | 41.3 | 149.1 | 159.3 | 90.7
515 | 308 | 469.1 | 187.64 | 219.3403 | 229.4 | 220.3 | 238.9 | 216.1 | 477.4 | 31.5 | 20.8 | 59.1 | 4.4 | 255.3 | 10.2 | 372.3 | 751.5 | 829.3 | 343.5 | 820.6 | 656.3 | 704 | 812 | 381.2 | 726.3 | 124.4 | 245.1 | 45.8 | 232.7 | 229.4 | 41.4 | 149.6 | 159.9 | 91
516 | 309 | 469.3 | 187.72 | 219.4339 | 228.9 | 221.4 | 238.2 | 216 | 489.1 | 31.5 | 20.8 | 59.2 | 3.9 | 255.5 | 9.2 | 376.1 | 750.6 | 837.1 | 345.6 | 822.4 | 656.5 | 709.8 | 816.9 | 382.1 | 728.4 | 124.6 | 245.1 | 45.9 | 232.5 | 229.8 | 41.5 | 150 | 160.5 | 91.3
517 | 310 | 468.5 | 187.4 | 219.0598 | 228.9 | 222.2 | 238.4 | 215.7 | 500 | 31.5 | 20.8 | 59.2 | 4 | 262.2 | 8.7 | 381.2 | 752 | 838.4 | 348 | 819.5 | 657.3 | 711.5 | 824.2 | 382.9 | 728.4 | 124.8 | 244.9 | 46.1 | 232.7 | 229.7 | 41.5 | 150.4 | 161.1 | 91.5
518 | 311 | 468.5 | 187.4 | 219.0598 | 229.5 | 223 | 237.9 | 215.9 | 513.4 | 31.5 | 20.8 | 59.3 | 3.6 | 263.6 | 9.3 | 386.3 | 754.3 | 836.7 | 351.1 | 814.6 | 658.2 | 710.9 | 830.9 | 383.8 | 726.2 | 125 | 244.6 | 46.2 | 233.5 | 229.7 | 41.6 | 150.6 | 161.6 | 91.8
519 | 312 | 468.2 | 187.28 | 218.9195 | 230.9 | 223.7 | 238.8 | 215.9 | 521.2 | 31.5 | 20.8 | 59.4 | 3.6 | 261.2 | 10.1 | 390.1 | 268.8 | 841 | 357.8 | 815.6 | 658.4 | 715.8 | 836 | 385 | 724.9 | 125.2 | 244.6 | 46.3 | 233.9 | 229.8 | 41.9 | 150.2 | 162.9 | 92
520 | 313 | 468.8 | 187.52 | 219.2001 | 232 | 224.3 | 238.9 | 215.9 | 535.3 | 31.5 | 20.8 | 59.4 | 4.1 | 249.9 | 10 | 392.8 | 65.2 | 838.2 | 358.2 | 815.2 | 659.6 | 718 | 840.3 | 386 | 724.7 | 125.5 | 245 | 46.5 | 234.4 | 229.8 | 41.8 | 151 | 163.1 | 92.3
521 | 314 | 468.2 | 187.28 | 218.9195 | 233 | 224.7 | 238.8 | 216.7 | 543.1 | 31.6 | 20.8 | 59.5 | 4.5 | 259.7 | 9.5 | 396.6 | 74.8 | 841.5 | 360.1 | 816.7 | 659.9 | 717.7 | 841.4 | 387 | 724 | 125.7 | 245.5 | 46.7 | 235.1 | 229.7 | 41.8 | 151.7 | 163.4 | 92.6
522 | 315 | 468.2 | 187.28 | 218.9195 | 231.4 | 225.9 | 238.7 | 217.1 | 557.4 | 31.8 | 20.8 | 59.5 | 5.6 | 266.9 | 9.5 | 401.1 | 86.7 | 842.7 | 363.3 | 820.4 | 660.1 | 724.2 | 845.5 | 388 | 725.9 | 125.9 | 246.1 | 46.8 | 235.6 | 230 | 41.8 | 152.3 | 164 | 92.9
523 | 316 | 468.4 | 187.36 | 219.013 | 229.4 | 227.1 | 237.9 | 217.6 | 559.8 | 31.9 | 20.8 | 59.5 | 5.8 | 264.1 | 10 | 405.1 | 498.5 | 841.7 | 366.8 | 822.2 | 660.3 | 729.8 | 843.2 | 389 | 727.6 | 126.2 | 246.8 | 46.9 | 235.8 | 230.3 | 41.9 | 152.7 | 164.7 | 93.2
524 | 317 | 468.6 | 187.44 | 219.1066 | 229 | 228.5 | 237.6 | 218.5 | 554.8 | 31.9 | 20.8 | 59.5 | 5.2 | 256.7 | 10 | 410 | 764.8 | 839.5 | 370.2 | 821.7 | 660.3 | 731.4 | 841 | 390.1 | 729.8 | 126.4 | 247.4 | 47.1 | 235.9 | 230.6 | 41.9 | 153.1 | 165.4 | 93.5
525 | 318 | 468.6 | 187.44 | 219.1066 | 230.1 | 229.5 | 238.5 | 219 | 546.2 | 32 | 20.8 | 59.6 | 4.9 | 264.6 | 9.4 | 414.6 | 767.7 | 833.7 | 374.1 | 823.7 | 660.6 | 733.1 | 835.8 | 391.1 | 731.9 | 126.7 | 247.8 | 47.2 | 235.4 | 231 | 42 | 153.5 | 166 | 93.8
526 | 319 | 468.3 | 187.32 | 218.9663 | 230.9 | 229.6 | 237.6 | 219.7 | 537.1 | 32.1 | 20.8 | 59.7 | 4.3 | 255.1 | 9.8 | 419 | 767.8 | 831.8 | 378.2 | 826.4 | 661.3 | 733.5 | 828.8 | 392.1 | 733.1 | 126.9 | 248 | 47.4 | 235.2 | 231.2 | 42.1 | 153.8 | 166.7 | 94.1
527 | 320 | 468 | 187.2 | 218.826 | 231.3 | 230.2 | 236.9 | 219.6 | 544.8 | 32.2 | 20.8 | 59.7 | 4.1 | 249.3 | 10.5 | 424.1 | 768.2 | 834.7 | 382.1 | 827.1 | 662.2 | 730.9 | 835 | 393 | 732.8 | 127.1 | 248.3 | 47.5 | 235.6 | 231.8 | 42.1 | 154.2 | 167.2 | 94.4
528 | 321 | 468.3 | 187.32 | 218.9663 | 231.9 | 231.2 | 237.2 | 219 | 546 | 32.3 | 20.8 | 59.8 | 4.4 | 243.4 | 10.9 | 428.9 | 768.4 | 837.7 | 386.4 | 825.5 | 663.3 | 729.2 | 838.5 | 394.1 | 733.2 | 127.4 | 248.4 | 47.7 | 236.4 | 232.4 | 42.2 | 154.5 | 167.9 | 94.6
529 | 322 | 470.6 | 188.24 | 220.0417 | 232.6 | 231.6 | 238 | 218.8 | 535.5 | 32.4 | 20.8 | 59.9 | 4.4 | 242.4 | 11 | 433.4 | 767.8 | 831.1 | 390.4 | 827.7 | 663.5 | 730.1 | 823.3 | 394.9 | 735.7 | 127.6 | 248.5 | 47.8 | 237.2 | 232.3 | 42.3 | 155 | 168.5 | 94.9
530 | 323 | 470.4 | 188.16 | 219.9482 | 232.8 | 231 | 238.5 | 219.2 | 518.4 | 32.5 | 20.8 | 60 | 4.3 | 242.7 | 11.4 | 437.5 | 767.9 | 826 | 394.6 | 831.2 | 663.5 | 728.1 | 812.3 | 395.8 | 736.5 | 127.8 | 248.8 | 48 | 238.8 | 232.3 | 42.4 | 155.3 | 169 | 95.1
531 | 324 | 470.2 | 188.08 | 219.8547 | 232.7 | 230.4 | 239 | 219.6 | 511 | 32.5 | 20.8 | 60.1 | 4.2 | 243.8 | 12 | 441.9 | 766.8 | 822.5 | 398.4 | 833.6 | 663.5 | 728.9 | 796.2 | 396.6 | 738.5 | 128.1 | 248.9 | 48.1 | 240.6 | 232.6 | 42.5 | 155.8 | 169.5 | 95.4
532 | 325 | 468.8 | 187.52 | 219.2001 | 233.5 | 230.1 | 240.3 | 220.3 | 503.7 | 32.5 | 20.8 | 60.2 | 3.9 | 254.1 | 9.9 | 446.4 | 765.8 | 820.2 | 402.5 | 835 | 663.5 | 727.3 | 792.3 | 397.5 | 740.5 | 128.3 | 248.9 | 48.3 | 240.5 | 233.3 | 42.7 | 156.3 | 170.1 | 95.7
533 | 326 | 468.6 | 187.44 | 219.1066 | 233.9 | 230 | 241.7 | 220.6 | 494.6 | 32.6 | 20.8 | 60.3 | 3.6 | 249.7 | 8.7 | 450.1 | 766.6 | 803.4 | 406.3 | 836 | 664.1 | 722.3 | 776.5 | 398.3 | 740.4 | 128.5 | 248.8 | 48.4 | 240.5 | 233.6 | 42.9 | 156.6 | 170.7 | 96
534 | 327 | 469.1 | 187.64 | 219.3403 | 235.1 | 229.7 | 242.3 | 220.8 | 486.1 | 32.6 | 20.8 | 60.4 | 3.9 | 245.2 | 9.4 | 454.5 | 768 | 798.2 | 410.7 | 835.8 | 665 | 717.7 | 775.8 | 399.1 | 740.5 | 128.7 | 248.9 | 48.6 | 241.2 | 233.8 | 43 | 156.8 | 171.2 | 96.3
535 | 328 | 469.6 | 187.84 | 219.5741 | 236.4 | 228.8 | 242.8 | 221.9 | 482.1 | 32.7 | 20.8 | 60.5 | 3.8 | 250.3 | 8.6 | 459.3 | 767.5 | 806.7 | 414.4 | 839.7 | 665.9 | 721.4 | 783.2 | 399.9 | 741.2 | 128.9 | 248.9 | 48.7 | 242 | 233.9 | 43.2 | 157.3 | 171.7 | 96.6
536 | 329 | 468.7 | 187.48 | 219.1533 | 237.5 | 228 | 243.2 | 222.6 | 489.9 | 32.8 | 20.8 | 60.6 | 3.7 | 253.7 | 8.4 | 464.2 | 768.1 | 811.1 | 419.1 | 840.1 | 666.4 | 726.7 | 790.8 | 400.8 | 744 | 129.2 | 249.1 | 48.8 | 242.6 | 234.4 | 43.4 | 157.7 | 172.2 | 96.8
537 | 330 | 468.6 | 187.44 | 219.1066 | 238.2 | 226.8 | 243.8 | 222.2 | 492.1 | 32.9 | 20.8 | 60.8 | 3.7 | 252 | 9.1 | 468.8 | 769 | 809.4 | 423.5 | 840.5 | 666.9 | 725.4 | 792.8 | 401.7 | 745.4 | 129.4 | 249.7 | 49 | 242.9 | 234.7 | 43.6 | 158.1 | 172.8 | 97.1
538 | 331 | 468.4 | 187.36 | 219.013 | 239 | 226.4 | 244.1 | 222.1 | 491.3 | 32.9 | 20.8 | 61 | 4.2 | 246.2 | 9.7 | 473.3 | 769.4 | 805.7 | 428 | 841.8 | 667.5 | 722.2 | 784.8 | 402.6 | 746 | 129.6 | 250.1 | 49.1 | 243.1 | 234.7 | 43.7 | 158.5 | 173.3 | 97.4
539 | 332 | 468.6 | 187.44 | 219.1066 | 239.8 | 225.7 | 244.3 | 222.7 | 495.5 | 32.8 | 20.8 | 61.2 | 4.3 | 246.8 | 9.3 | 477.9 | 767.9 | 807.7 | 432.6 | 844.3 | 667.8 | 724.4 | 774.1 | 403.5 | 747.1 | 129.8 | 250.5 | 49.3 | 243.4 | 234.8 | 43.9 | 158.9 | 173.8 | 97.7
540 | 333 | 468.6 | 187.44 | 219.1066 | 240.3 | 225.5 | 243.7 | 222.5 | 492.6 | 32.8 | 20.8 | 61.2 | 4.4 | 268.7 | 8.3 | 482.3 | 765.2 | 805.7 | 437 | 845 | 668.3 | 723.2 | 772.9 | 404.4 | 750.1 | 130 | 250.8 | 49.4 | 244 | 235 | 44.1 | 159.3 | 174.3 | 98
541 | 334 | 468.9 | 187.56 | 219.2468 | 239.9 | 225.6 | 243.2 | 222.7 | 491 | 32.9 | 20.8 | 61.2 | 4.5 | 258.1 | 7.7 | 486.8 | 761.9 | 795.9 | 440.9 | 845.3 | 669 | 718.8 | 770.2 | 405.4 | 749.4 | 130.2 | 251 | 49.6 | 244.2 | 235.1 | 44.3 | 159.7 | 174.9 | 98.2
542 | 335 | 468.5 | 187.4 | 219.0598 | 241.2 | 225.6 | 244.8 | 223.1 | 482.9 | 33 | 20.7 | 61.3 | 4.6 | 258.1 | 8.5 | 490.9 | 758.4 | 781.8 | 444.4 | 846.3 | 669.7 | 710.8 | 749.6 | 406.4 | 747.9 | 130.4 | 251.6 | 49.7 | 244.4 | 235.1 | 44.5 | 160.1 | 175.4 | 98.5
543 | 336 | 468.1 | 187.24 | 218.8728 | 243.4 | 225.4 | 245.8 | 223.4 | 471.4 | 33.1 | 20.7 | 61.3 | 4.3 | 256.8 | 9.1 | 495.4 | 754.9 | 768.7 | 447.8 | 845 | 670.4 | 703.3 | 736.9 | 407.4 | 747.2 | 130.6 | 252.2 | 49.9 | 244.6 | 235.1 | 44.6 | 160.5 | 176 | 98.8
544 | 337 | 469.8 | 187.92 | 219.6677 | 245.4 | 224 | 246.3 | 224.3 | 469.3 | 33.2 | 20.7 | 61.4 | 4.5 | 262.3 | 8.5 | 499.5 | 750.7 | 749.1 | 450.9 | 837.4 | 671.2 | 694.3 | 727 | 408.5 | 745.4 | 130.7 | 252.4 | 50 | 244.5 | 235.7 | 44.8 | 161 | 176.5 | 99.1
545 | 338 | 468 | 187.2 | 218.826 | 247.5 | 222.5 | 246.8 | 225.5 | 465.9 | 33.3 | 20.7 | 61.4 | 4.7 | 267.2 | 7.4 | 503.7 | 747.7 | 742.8 | 454.2 | 836.4 | 672.2 | 689.1 | 714.5 | 409.7 | 744.9 | 130.9 | 252.7 | 50.2 | 244.4 | 236 | 44.9 | 161.4 | 176.9 | 99.4
546 | 339 | 468.7 | 187.48 | 219.1533 | 250 | 221.7 | 247.5 | 226.5 | 458.4 | 33.3 | 20.7 | 61.4 | 4 | 269.5 | 7 | 507.5 | 745.1 | 736.9 | 456.9 | 836.7 | 672.7 | 680.9 | 703.8 | 410.8 | 742.9 | 131.1 | 252.9 | 50.3 | 245 | 236.5 | 45.1 | 161.9 | 177.4 | 99.7
547 | 340 | 467.7 | 187.08 | 218.6857 | 249.9 | 220.3 | 248.4 | 227.5 | 454.4 | 33.4 | 20.7 | 61.4 | 3.8 | 274.8 | 6.5 | 511.8 | 743.4 | 737.9 | 459.8 | 837.5 | 672.8 | 676.8 | 693.8 | 412 | 743.1 | 131.3 | 253.1 | 50.5 | 245.5 | 237.3 | 45.2 | 162.4 | 177.9 | 99.9
548 | 341 | 467.9 | 187.16 | 218.7793 | 250.9 | 219.8 | 249.7 | 227.8 | 451.9 | 33.4 | 20.7 | 61.5 | 3.9 | 261.9 | 6.9 | 515.8 | 742.4 | 732.9 | 462.8 | 839 | 673 | 675.6 | 692.7 | 413.1 | 743 | 131.5 | 253.4 | 50.6 | 246 | 237.8 | 45.4 | 162.8 | 178.3 | 100.3
549 | 342 | 467.7 | 187.08 | 218.6857 | 252.5 | 220.1 | 250.3 | 228.6 | 450.3 | 33.5 | 20.7 | 61.6 | 4 | 262.4 | 6.9 | 519.9 | 742 | 728.5 | 465.7 | 839.2 | 673.5 | 675.4 | 685.3 | 414.4 | 743 | 131.7 | 253.5 | 50.7 | 246.5 | 238.5 | 45.5 | 163.3 | 178.8 | 100.5
550 | 343 | 468.4 | 187.36 | 219.013 | 253.1 | 220.1 | 251.9 | 229.5 | 447.1 | 33.5 | 20.7 | 61.7 | 3.9 | 253.8 | 7 | 523.9 | 741.2 | 732.2 | 468.7 | 842 | 674.1 | 678.2 | 690.6 | 415.6 | 744.8 | 131.9 | 253.8 | 50.9 | 247.3 | 239.3 | 45.7 | 163.9 | 179.2 | 100.9
551 | 344 | 467.6 | 187.04 | 218.639 | 253.1 | 220 | 253.8 | 230.1 | 447.6 | 33.5 | 20.7 | 61.7 | 4 | 252.5 | 7.1 | 528.3 | 741.2 | 741.6 | 472.2 | 845.1 | 674.8 | 683.7 | 699.8 | 416.8 | 747.1 | 132.1 | 254.3 | 51.1 | 248.3 | 239.5 | 45.8 | 164.3 | 179.7 | 101.2
552 | 345 | 467.7 | 187.08 | 218.6857 | 253.6 | 220.7 | 254.9 | 230.2 | 449.7 | 33.6 | 20.7 | 61.8 | 4 | 252.1 | 6.8 | 532.8 | 741.1 | 751.6 | 475.1 | 848.1 | 675.5 | 691.4 | 710.7 | 418 | 749.6 | 132.3 | 254.7 | 51.2 | 249.2 | 239.8 | 46 | 164.7 | 180.2 | 101.5
553 | 346 | 468.7 | 187.48 | 219.1533 | 253.2 | 219.9 | 255.3 | 230.7 | 452.1 | 33.6 | 20.7 | 61.9 | 4.3 | 246 | 6.7 | 536.9 | 741.8 | 751.6 | 478.2 | 847.5 | 676.3 | 696.7 | 718.9 | 419.3 | 751.7 | 132.5 | 255.2 | 51.4 | 250.8 | 240.4 | 46.2 | 165.2 | 180.7 | 101.8
554 | 347 | 470.3 | 188.12 | 219.9014 | 253.7 | 219.8 | 255.6 | 231.5 | 457.6 | 33.7 | 20.7 | 62 | 4.4 | 242.5 | 6.4 | 541.1 | 743.6 | 741.2 | 481.6 | 842.5 | 677.3 | 699.1 | 717.5 | 420.6 | 752.5 | 132.7 | 255.4 | 51.5 | 252.6 | 241.2 | 46.3 | 165.8 | 181.3 | 102.2
555 | 348 | 469.5 | 187.8 | 219.5274 | 254.3 | 220.1 | 256.3 | 232.4 | 457.4 | 33.7 | 20.7 | 62.1 | 4.2 | 246.6 | 6.2 | 545.1 | 743.8 | 733.2 | 484.4 | 844.2 | 678.7 | 699.2 | 710.8 | 421.8 | 753.3 | 132.9 | 255.5 | 51.7 | 254 | 242.1 | 46.5 | 166.4 | 181.9 | 102.5
556 | 349 | 469.2 | 187.68 | 219.3871 | 255.5 | 220.9 | 256.6 | 232.8 | 459 | 33.7 | 20.7 | 62.3 | 4.3 | 241.2 | 6 | 549.5 | 744.1 | 733.9 | 486.9 | 846.9 | 679.6 | 700.6 | 705 | 423.1 | 754.2 | 133.1 | 255.8 | 51.8 | 254.7 | 243 | 46.6 | 166.9 | 182.5 | 102.8
557 | 350 | 468.7 | 187.48 | 219.1533 | 256.4 | 221.3 | 256.4 | 233.5 | 456.2 | 33.7 | 20.7 | 62.3 | 4 | 248.5 | 6 | 554 | 744.9 | 740.6 | 489.8 | 848.4 | 680.6 | 701.3 | 696.6 | 424.4 | 755.5 | 133.2 | 256.1 | 52 | 254.8 | 244.5 | 46.8 | 167.4 | 183 | 103.1
558 | 351 | 468.6 | 187.44 | 219.1066 | 257 | 221.1 | 257.3 | 234.1 | 456.9 | 33.6 | 20.7 | 62.4 | 3.7 | 252.1 | 5.5 | 558.4 | 745 | 740.1 | 493.1 | 846.6 | 681.1 | 700.7 | 690.6 | 425.7 | 756 | 133.4 | 256.5 | 52.1 | 255.1 | 245.2 | 47 | 168.1 | 183.5 | 103.3
559 | 352 | 469.8 | 187.92 | 219.6677 | 257.3 | 221.7 | 257.9 | 234.6 | 459.3 | 33.6 | 20.7 | 62.4 | 4 | 249.4 | 4.6 | 562.7 | 745 | 737.1 | 495.8 | 846 | 681.4 | 702 | 679.7 | 427.2 | 756 | 133.6 | 256.8 | 52.3 | 256.2 | 245.5 | 47.2 | 168.5 | 184.1 | 103.4
560 | 353 | 468.7 | 187.48 | 219.1533 | 259.9 | 222.1 | 257.9 | 235.1 | 458.7 | 33.6 | 20.7 | 62.5 | 3.9 | 263.5 | 4.7 | 567.1 | 744.6 | 742.1 | 498.8 | 850.1 | 682 | 701.4 | 684.9 | 428.7 | 755.6 | 133.8 | 257.3 | 52.4 | 256.2 | 246.1 | 47.3 | 169.1 | 184.5 | 104
561 | 354 | 469 | 187.6 | 219.2936 | 260.5 | 222.8 | 259.2 | 235.5 | 459.1 | 33.7 | 20.7 | 62.6 | 3.8 | 273.1 | 5.8 | 572 | 743.9 | 743.7 | 501.7 | 853.6 | 682.4 | 701.2 | 691 | 430.4 | 756.2 | 134 | 257.7 | 52.6 | 255.7 | 247.4 | 47.5 | 169.6 | 185.1 | 104.2
562 | 355 | 468.5 | 187.4 | 219.0598 | 259.7 | 223 | 260.2 | 235.5 | 461.9 | 33.7 | 20.7 | 62.6 | 4.1 | 265.6 | 6.3 | 577 | 744.4 | 732.7 | 505.4 | 854.6 | 682.9 | 699.6 | 692.7 | 432.1 | 758.1 | 134.1 | 258.2 | 52.7 | 255.8 | 248.1 | 47.7 | 170.1 | 185.6 | 104.4
563 | 356 | 468.9 | 187.56 | 219.2468 | 260.5 | 223.3 | 260.1 | 236 | 459.2 | 33.7 | 20.7 | 62.7 | 4.2 | 255.7 | 6.2 | 582.6 | 744.8 | 728.2 | 508.7 | 853.7 | 683.6 | 697.9 | 684.4 | 433.9 | 758 | 134.3 | 258.5 | 52.9 | 256.5 | 248.8 | 47.8 | 170.6 | 186.1 | 105
564 | 357 | 468.9 | 187.56 | 219.2468 | 260 | 223.7 | 260.4 | 236.1 | 456.4 | 33.7 | 20.7 | 62.7 | 4.6 | 244.5 | 6 | 588 | 744 | 722 | 512 | 849.9 | 684.2 | 694.5 | 669.6 | 435.8 | 755.6 | 134.5 | 259 | 53 | 256.9 | 249.2 | 48 | 171 | 186.6 | 105
565 | 358 | 469.3 | 187.72 | 219.4339 | 259.6 | 223.6 | 260.8 | 236.1 | 453.5 | 33.8 | 20.7 | 62.7 | 4.4 | 242.6 | 6.2 | 593.6 | 742.6 | 722.6 | 514.9 | 851.3 | 684.8 | 687.2 | 659.5 | 437.8 | 754.9 | 134.6 | 259.7 | 53.2 | 257.1 | 249.9 | 48.2 | 171.4 | 187 | 105.4
566 | 359 | 468.4 | 187.36 | 219.013 | 260.4 | 223.5 | 261.1 | 236.6 | 454.1 | 33.7 | 20.7 | 62.7 | 4.4 | 242.1 | 5.7 | 599.1 | 742.5 | 729 | 517.7 | 852 | 685.7 | 684.6 | 663.4 | 440.1 | 755.5 | 134.8 | 260.6 | 53.3 | 257.2 | 250.4 | 48.4 | 171.9 | 187.4 | 105.9
567 | 360 | 469 | 187.6 | 219.2936 | 260.7 | 223.1 | 261.9 | 237.2 | 448.6 | 33.7 | 20.7 | 62.7 | 4.7 | 241.7 | 5.3 | 604.5 | 742.5 | 713.2 | 520.1 | 850.2 | 686.5 | 675.4 | 655.7 | 442.5 | 754.2 | 134.9 | 261.1 | 53.5 | 257.4 | 250.5 | 48.6 | 172.3 | 187.9 | 106.1
568 | 361 | 468.7 | 187.48 | 219.1533 | 261.2 | 222.7 | 261.8 | 237.3 | 442.2 | 33.8 | 20.7 | 62.7 | 4.8 | 249.8 | 5.2 | 610 | 741.4 | 701 | 522.7 | 850.4 | 687.7 | 669.2 | 643.2 | 445.1 | 751.7 | 135.1 | 261.4 | 53.7 | 257.2 | 250.8 | 48.8 | 172.8 | 188.3 | 106.4
569 | 362 | 468.5 | 187.4 | 219.0598 | 263.1 | 222 | 262 | 237.6 | 440.2 | 33.9 | 20.7 | 62.9 | 4.3 | 249.4 | 5.1 | 615.5 | 741 | 719.2 | 525 | 852.9 | 688.6 | 668.6 | 646.1 | 447.9 | 750.5 | 135.2 | 261.5 | 53.8 | 257.3 | 251.1 | 49 | 173.2 | 188.8 | 106.7
570 | 363 | 469.7 | 187.88 | 219.6209 | 264.3 | 221.8 | 262.4 | 237.8 | 441.6 | 34 | 20.7 | 63 | 4.3 | 243.6 | 5.1 | 620.7 | 741.1 | 734.4 | 527.5 | 859 | 689.1 | 668.3 | 665.9 | 450.9 | 750.4 | 135.4 | 261.8 | 54 | 257.6 | 251.2 | 49.2 | 173.6 | 189.2 | 107.1
571 | 364 | 468.1 | 187.24 | 218.8728 | 264 | 221.3 | 262.7 | 237.8 | 442 | 34.1 | 20.7 | 63.1 | 4.5 | 269.1 | 5.1 | 625.3 | 741.6 | 728.9 | 529.9 | 857.3 | 690 | 663.7 | 673.9 | 454.2 | 750.8 | 135.6 | 261.8 | 54.1 | 257.7 | 251.3 | 49.3 | 174 | 189.6 | 107.4
572 | 365 | 468.6 | 187.44 | 219.1066 | 263.7 | 221 | 262.9 | 237.9 | 443.1 | 34.1 | 20.7 | 63.4 | 4.8 | 267.5 | 5.3 | 629.7 | 742.1 | 715.8 | 532.1 | 852 | 690.9 | 659.6 | 687.5 | 457.5 | 749.1 | 135.7 | 262.1 | 54.3 | 258.3 | 252 | 49.5 | 174.4 | 190.1 | 107.7
573 | 366 | 468.1 | 187.24 | 218.8728 | 264.2 | 220.3 | 262.7 | 237.9 | 450.1 | 34.2 | 20.7 | 63.7 | 4.9 | 234.3 | 5.7 | 634.1 | 742.9 | 707.8 | 534.1 | 851.6 | 692 | 651.3 | 678.9 | 460.9 | 746.7 | 135.9 | 262.4 | 54.4 | 258.1 | 252 | 49.7 | 174.8 | 190.5 | 108
574 | 367 | 468.8 | 187.52 | 219.2001 | 264.9 | 219.4 | 262.3 | 238.1 | 444 | 34.2 | 20.7 | 63.9 | 5.2 | 229.3 | 6.5 | 638.8 | 742.8 | 711.2 | 536.1 | 854.2 | 692.9 | 653.4 | 676.9 | 464.2 | 747.1 | 136 | 262.5 | 54.6 | 258.3 | 251.8 | 49.9 | 175.2 | 190.9 | 108.3
575 | 368 | 469.2 | 187.68 | 219.3871 | 265.9 | 219.5 | 262.3 | 238.3 | 442.2 | 34.2 | 20.7 | 64.1 | 5 | 229.1 | 6.5 | 643.7 | 742.8 | 718.7 | 538.6 | 857.2 | 693.9 | 649.7 | 686.1 | 467.3 | 745.8 | 136.2 | 262.6 | 54.7 | 258.2 | 251.9 | 50.1 | 175.5 | 191.2 | 108.6
576 | 369 | 473.5 | 189.4 | 221.3977 | 265.8 | 220.3 | 263.4 | 239.1 | 441.5 | 34.2 | 20.7 | 64.1 | 4.3 | 236 | 5.8 | 648.6 | 743 | 730.9 | 541.2 | 859.1 | 694.7 | 648 | 701.3 | 470.4 | 746.6 | 136.4 | 262.5 | 54.9 | 257.2 | 251.8 | 50.2 | 175.9 | 191.6 | 108.9
577 | 370 | 474.4 | 189.76 | 221.8185 | 265.1 | 220.4 | 264.1 | 239.3 | 446.4 | 34.2 | 20.6 | 64.1 | 3.9 | 226.6 | 5 | 653.1 | 743.3 | 743.1 | 543.8 | 858.9 | 695.7 | 650.7 | 721.7 | 473.5 | 747.6 | 136.5 | 262.7 | 55.1 | 256.5 | 251.6 | 50.4 | 176.2 | 192.1 | 109.2
578 | 371 | 489.5 | 195.8 | 228.8789 | 264.5 | 220.1 | 264 | 239 | 472.3 | 34.2 | 20.6 | 64.1 | 4.3 | 210.5 | 4.5 | 657.2 | 743 | 758.5 | 547.1 | 855.3 | 697 | 655.3 | 744.5 | 476.5 | 747 | 136.7 | 263.3 | 55.2 | 257.1 | 252 | 50.6 | 176.5 | 192.5 | 109.5
579 | 372 | 519.3 | 207.72 | 242.8127 | 263.6 | 219.8 | 263.4 | 238.9 | 479.5 | 34.2 | 20.7 | 64 | 4.7 | 222.3 | 3.4 | 661.4 | 742.9 | 771.4 | 550.1 | 850.6 | 698.9 | 654.9 | 751.4 | 479.3 | 747.8 | 136.9 | 263.6 | 55.4 | 257.3 | 252.1 | 50.8 | 176.8 | 193 | 109.8
580 | 373 | 535.2 | 214.08 | 250.2472 | 262.7 | 220.8 | 263 | 238.9 | 477 | 34.3 | 20.7 | 64.1 | 4.9 | 270.3 | 3.7 | 665.4 | 742.9 | 787.6 | 553.7 | 847.1 | 700.2 | 658.5 | 761.4 | 482.1 | 748.6 | 137.1 | 263.9 | 55.5 | 257.5 | 251.7 | 51 | 177.2 | 193.4 | 110.1
581 | 374 | 540.8 | 216.32 | 252.8656 | 261.7 | 221.6 | 263 | 239.2 | 482.6 | 34.3 | 20.6 | 64.3 | 5 | 256.7 | 4.1 | 669.6 | 743.8 | 792.9 | 557.6 | 853.1 | 701 | 667.2 | 775.4 | 484.9 | 750.4 | 137.2 | 264.2 | 55.7 | 257.3 | 252 | 51.2 | 177.6 | 193.9 | 110.3
582 | 375 | 544.8 | 217.92 | 254.7359 | 260.2 | 222.7 | 262.9 | 238.7 | 487.5 | 34.3 | 20.6 | 64.5 | 5 | 212.4 | 4.8 | 673.3 | 744.2 | 799.3 | 561.3 | 859.8 | 701.4 | 673 | 780.9 | 487.6 | 753.9 | 137.4 | 264.4 | 55.9 | 256.9 | 252.5 | 51.4 | 178 | 194.4 | 110.6
583 | 376 | 543.9 | 217.56 | 254.3151 | 258.5 | 224.1 | 262.2 | 237.6 | 494.2 | 34.4 | 20.6 | 64.8 | 5.2 | 192.8 | 4.9 | 676.3 | 745.3 | 797.2 | 565.4 | 860.6 | 701.6 | 676.5 | 782.1 | 490.2 | 754.6 | 137.6 | 264.4 | 56 | 256.4 | 252.6 | 51.5 | 178.4 | 195.1 | 110.9
584 | 377 | 543.4 | 217.36 | 254.0813 | 257.1 | 224.9 | 261.3 | 237.4 | 497.9 | 34.4 | 20.6 | 65 | 5.8 | 216.7 | 4.1 | 679.7 | 746.8 | 799.1 | 569.1 | 862.9 | 702 | 678.3 | 776.8 | 492.7 | 754.7 | 137.8 | 264.4 | 56.2 | 257 | 252.3 | 51.7 | 178.8 | 195.7 | 111.2
585 | 378 | 543.5 | 217.4 | 254.1281 | 255.9 | 226.9 | 261.4 | 237.3 | 499.5 | 34.4 | 20.6 | 65 | 5.2 | 247.3 | 3.9 | 683.3 | 747.1 | 811 | 573.3 | 864.5 | 702.4 | 682.3 | 787 | 495.3 | 756.2 | 138 | 264.5 | 56.3 | 257.1 | 252.6 | 51.9 | 179.2 | 196.3 | 111.5
586 | 379 | 542.9 | 217.16 | 253.8475 | 254.7 | 228.1 | 261.9 | 237.4 | 517 | 34.4 | 20.6 | 65 | 5.4 | 238.2 | 5.2 | 687.1 | 748.6 | 820.2 | 577.6 | 865.6 | 703 | 681.2 | 794.1 | 498 | 757.4 | 138.2 | 264.6 | 56.5 | 257.5 | 253.2 | 52.1 | 179.6 | 196.9 | 111.8
587 | 380 | 543.1 | 217.24 | 253.941 | 253.3 | 228.3 | 262.3 | 237.9 | 536.1 | 34.6 | 20.6 | 65 | 5.7 | 243.6 | 5.8 | 690.7 | 749.9 | 826.8 | 581.3 | 867.8 | 704 | 681 | 804 | 500.5 | 755.5 | 138.4 | 264.6 | 56.7 | 258.7 | 253.1 | 52.3 | 179.9 | 197.5 | 112.1
588 | 381 | 543.7 | 217.48 | 254.2216 | 252.5 | 229.6 | 262.4 | 237.2 | 548.3 | 34.8 | 20.6 | 65 | 5.8 | 237.3 | 6 | 694.3 | 753 | 834.3 | 585.4 | 867 | 705.2 | 687.4 | 807.6 | 503.1 | 758.1 | 138.6 | 264.7 | 56.8 | 259.6 | 253.4 | 52.5 | 180.4 | 198 | 112.4
589 | 382 | 546.2 | 218.48 | 255.3905 | 251.7 | 231.7 | 261.5 | 237.5 | 538.3 | 35 | 20.6 | 65.1 | 5.8 | 226.2 | 5.8 | 697.4 | 754 | 824.6 | 589.5 | 868.6 | 706.4 | 685.5 | 796.2 | 505.9 | 757.7 | 138.8 | 264.5 | 57 | 260.4 | 253.4 | 52.6 | 180.9 | 198.6 | 112.7
590 | 383 | 547.7 | 219.08 | 256.0919 | 250.5 | 233.5 | 261.7 | 238.7 | 528.7 | 35.2 | 20.6 | 65.2 | 5.1 | 225.2 | 6.1 | 700.9 | 753.8 | 819.4 | 592.7 | 870 | 707.2 | 687.3 | 783.6 | 508.9 | 760.2 | 139 | 264.8 | 57.2 | 260.6 | 253.4 | 52.8 | 181.3 | 199.2 | 113
591 | 384 | 546.9 | 218.76 | 255.7178 | 250 | 234.5 | 261.1 | 238.6 | 524.1 | 35.4 | 20.6 | 65.3 | 5.1 | 223.4 | 8.1 | 704 | 754.4 | 818.8 | 596.3 | 868.6 | 707.7 | 690.8 | 783.5 | 512.1 | 762.2 | 139.3 | 265.3 | 57.3 | 261 | 253.2 | 53 | 181.5 | 199.9 | 113.3
592 | 385 | 548.3 | 219.32 | 256.3724 | 249.2 | 234.6 | 260 | 237.6 | 520 | 35.5 | 20.6 | 65.3 | 4.6 | 230.1 | 8.5 | 707.2 | 755.3 | 814.9 | 599.3 | 869.5 | 708 | 690.6 | 774.9 | 515.4 | 763.3 | 139.5 | 265.6 | 57.5 | 261.4 | 253.4 | 53.2 | 181.8 | 200.4 | 113.6
593 | 386 | 547.8 | 219.12 | 256.1387 | 249.4 | 234.6 | 260.6 | 237.9 | 513.3 | 35.5 | 20.6 | 65.3 | 4.5 | 236.8 | 6.8 | 710.5 | 756 | 810.4 | 602.7 | 870.2 | 708.3 | 692 | 774.7 | 519 | 765 | 139.7 | 265.7 | 57.6 | 261.7 | 253.8 | 53.4 | 182.3 | 201 | 113.9
594 | 387 | 550.3 | 220.12 | 257.3076 | 249.9 | 235.7 | 261.1 | 238.5 | 508.7 | 35.7 | 20.6 | 65.4 | 4.4 | 228.1 | 7 | 713.8 | 756.1 | 814.4 | 606 | 874.1 | 709.1 | 693 | 772.7 | 522.8 | 765.9 | 139.9 | 265.6 | 57.8 | 262.5 | 253.9 | 53.6 | 182.6 | 201.6 | 114.2
595 | 388 | 551.2 | 220.48 | 257.7284 | 249.5 | 236.9 | 262.1 | 238.7 | 519.6 | 35.8 | 20.6 | 65.6 | 4.8 | 228.5 | 7.7 | 717.2 | 756.5 | 819.9 | 609.6 | 875.9 | 709.8 | 700 | 780.9 | 526.9 | 768.7 | 140.2 | 265.9 | 58 | 264.5 | 254 | 53.7 | 183 | 202.3 | 114.5
596 | 389 | 550.3 | 220.12 | 257.3076 | 249.4 | 237.1 | 262.2 | 239.2 | 525.4 | 36 | 20.6 | 65.7 | 5 | 220.6 | 6.6 | 720.2 | 756.8 | 827.2 | 613.9 | 881.8 | 710.7 | 703.3 | 784.9 | 531.3 | 771.2 | 140.4 | 266.2 | 58.1 | 265.2 | 254.4 | 53.9 | 183.4 | 203 | 114.8
597 | 390 | 550.6 | 220.24 | 257.4479 | 248.7 | 237.1 | 261.7 | 240.6 | 522.9 | 36.2 | 20.6 | 65.9 | 5.2 | 212.9 | 5.7 | 722.8 | 757.5 | 829.4 | 618.7 | 882.1 | 711.4 | 706.4 | 775.9 | 536.1 | 771.5 | 140.6 | 266.5 | 58.3 | 266 | 254.7 | 54.1 | 183.8 | 203.8 | 115.2
598 | 391 | 551.3 | 220.52 | 257.7752 | 248.4 | 237.9 | 260.9 | 242.1 | 522.5 | 36.3 | 20.6 | 66 | 4.8 | 220.6 | 5.4 | 725.7 | 757.8 | 836.5 | 623.3 | 881.8 | 712.1 | 706.7 | 786.6 | 541.3 | 773.6 | 140.8 | 266.9 | 58.5 | 266.7 | 255 | 54.3 | 184.3 | 204.6 | 115.5
599 | 392 | 552.4 | 220.96 | 258.2895 | 248.3 | 239.1 | 261.3 | 243.2 | 535.5 | 36.4 | 20.6 | 66 | 4.2 | 228.4 | 5.4 | 728.6 | 758.1 | 836.5 | 627.8 | 884.1 | 713.1 | 707.3 | 792.5 | 546.9 | 774.7 | 141 | 267.3 | 58.6 | 267.2 | 255 | 54.5 | 184.7 | 205.3 | 115.8
600 | 393 | 553.2 | 221.28 | 258.6636 | 248.3 | 239 | 262.2 | 243.4 | 536 | 36.4 | 20.6 | 66.1 | 4.7 | 248.4 | 6.1 | 731.3 | 758.9 | 835.3 | 631.8 | 886.2 | 714.2 | 710.4 | 793.5 | 553 | 775.4 | 141.3 | 267.6 | 58.8 | 268 | 255.2 | 54.6 | 185.1 | 206.1 | 116.1
601 | 394 | 553.6 | 221.44 | 258.8506 | 247.9 | 239.9 | 262.6 | 243.3 | 547.5 | 36.5 | 20.6 | 66.2 | 4.9 | 241.3 | 7.2 | 734 | 759.7 | 835.5 | 635.8 | 887.5 | 715.8 | 714.5 | 794.4 | 559.9 | 777.8 | 141.5 | 267.7 | 59 | 269.2 | 255.7 | 54.8 | 185.8 | 206.9 | 116.4
602 | 395 | 554.5 | 221.8 | 259.2714 | 246.9 | 241.8 | 262 | 243.4 | 540.8 | 36.5 | 20.6 | 66.3 | 4.4 | 234.3 | 7.7 | 736.5 | 759.9 | 836.4 | 639.4 | 887.2 | 717.7 | 716.4 | 798.4 | 567.3 | 780.1 | 141.7 | 268 | 59.1 | 270.4 | 256.1 | 55 | 186.2 | 207.7 | 116.7
603 | 396 | 556.4 | 222.56 | 260.1598 | 246.6 | 243.6 | 261.7 | 244 | 541.7 | 36.6 | 20.6 | 66.4 | 3.9 | 231.5 | 7.6 | 739 | 760.3 | 836.2 | 642.8 | 884.2 | 719.1 | 716.5 | 805.3 | 574.9 | 782.8 | 141.9 | 268.2 | 59.3 | 271.2 | 256.4 | 55.2 | 186.6 | 208.4 | 117.1
604 | 397 | 557 | 222.8 | 260.4404 | 247.3 | 244.4 | 261.2 | 243.9 | 536.3 | 36.6 | 20.6 | 66.5 | 4.9 | 245.3 | 7.2 | 741.8 | 761.5 | 836.7 | 645.7 | 883.2 | 720.4 | 717.4 | 804 | 583 | 784.8 | 142.1 | 268.5 | 59.5 | 272 | 256.6 | 55.4 | 187.1 | 209 | 117.4
605 | 398 | 556.4 | 222.56 | 260.1598 | 248.3 | 244.1 | 261.4 | 243.4 | 531.2 | 36.6 | 20.6 | 66.6 | 4.7 | 242.9 | 7 | 744.4 | 761.3 | 841.1 | 648.5 | 884 | 721.9 | 717.6 | 802.7 | 592 | 785.8 | 142.3 | 268.5 | 59.6 | 272.3 | 256.7 | 55.5 | 187.4 | 209.6 | 117.7
606 | 399 | 556 | 222.4 | 259.9728 | 248.1 | 244.8 | 262 | 243.9 | 524.8 | 36.7 | 20.6 | 66.7 | 4.1 | 224.6 | 7.5 | 746.8 | 760.2 | 840.5 | 651 | 886.4 | 722.9 | 716 | 799.3 | 601.7 | 787.6 | 142.6 | 268.4 | 59.8 | 272.4 | 256.9 | 55.7 | 187.9 | 210.3 | 118
607 | 400 | 556 | 222.4 | 259.9728 | 248 | 245.6 | 262.4 | 243.5 | 522.9 | 36.9 | 20.6 | 66.9 | 4.3 | 253.1 | 8.3 | 748.5 | 760.3 | 833.7 | 653.9 | 889.4 | 723.9 | 718.5 | 788.4 | 611.4 | 786.4 | 142.8 | 268.6 | 60 | 272.9 | 257.1 | 55.9 | 188.4 | 211 | 118.4
608 | 401 | 557.6 | 223.04 | 260.7209 | 248.8 | 246.7 | 262.6 | 243.8 | 518.9 | 37 | 20.6 | 67 | 4.5 | 240.5 | 9 | 750.3 | 761.7 | 833.5 | 655.9 | 891.4 | 725.2 | 719.9 | 785.7 | 620.8 | 787.3 | 143 | 268.7 | 60.2 | 273.7 | 257.4 | 56.1 | 188.7 | 211.8 | 118.7
609 | 402 | 558.5 | 223.4 | 261.1417 | 250 | 247.9 | 264.5 | 244.7 | 514.8 | 37.1 | 20.6 | 67.2 | 4.8 | 248.4 | 9.7 | 751.9 | 764.9 | 829.7 | 657.8 | 891.7 | 726.8 | 719.3 | 781.3 | 629.6 | 788 | 143.2 | 268.9 | 60.3 | 274.3 | 257.9 | 56.2 | 189.2 | 212.6 | 119
610 | 403 | 558.2 | 223.28 | 261.0015 | 251.6 | 248.7 | 264.6 | 245.6 | 509 | 37.2 | 20.6 | 67.3 | 4.5 | 242.2 | 9.3 | 754.3 | 766.7 | 825.6 | 659.9 | 889.6 | 728 | 717.2 | 763.6 | 637.9 | 787.2 | 143.5 | 269.2 | 60.5 | 275.5 | 258.6 | 56.4 | 189.8 | 213.3 | 119.4
611 | 404 | 558.8 | 223.52 | 261.282 | 254.1 | 249.4 | 263.4 | 246.9 | 505.1 | 37.3 | 20.6 | 67.4 | 4.7 | 253.5 | 9.4 | 757.1 | 768.2 | 824.8 | 662.4 | 887.7 | 728.8 | 715.5 | 759.4 | 646 | 787.4 | 143.7 | 269.6 | 60.7 | 276.9 | 259.4 | 56.6 | 190.4 | 213.9 | 119.7
612 | 405 | 558.7 | 223.48 | 261.2352 | 255.7 | 249.1 | 263.6 | 247.7 | 497.6 | 37.3 | 20.6 | 67.4 | 4.6 | 244.4 | 9.3 | 759.6 | 769 | 822.9 | 665.2 | 887.2 | 729.5 | 713.1 | 753.7 | 653.6 | 787.9 | 143.9 | 270.5 | 60.8 | 278.5 | 260.3 | 56.8 | 190.9 | 214.5 | 120.1
613 | 406 | 559.3 | 223.72 | 261.5158 | 256.6 | 248.6 | 264.8 | 248.5 | 499.6 | 37.4 | 20.6 | 67.6 | 4.8 | 234.1 | 9.2 | 761.8 | 769.8 | 820.7 | 668 | 887.5 | 730.3 | 713.3 | 753.2 | 660.3 | 788.8 | 144.1 | 271.1 | 61 | 279.8 | 261.3 | 57 | 191.4 | 215.2 | 120.4
614 | 407 | 560.8 | 224.32 | 262.2172 | 257.5 | 248.4 | 263.8 | 248.2 | 496.4 | 37.4 | 20.6 | 67.6 | 4.8 | 248 | 7.8 | 764 | 770.4 | 824.4 | 670.6 | 890.4 | 731 | 713.9 | 752.7 | 666.1 | 789.5 | 144.4 | 271.2 | 61.2 | 280.3 | 262.3 | 57.1 | 192 | 215.9 | 120.8
615 | 408 | 559.8 | 223.92 | 261.7496 | 258.4 | 249.1 | 264.4 | 248 | 500 | 37.5 | 20.6 | 67.6 | 4.4 | 272.1 | 7.1 | 766.5 | 770.3 | 829.3 | 674 | 890.4 | 731.9 | 713.3 | 758.4 | 671.7 | 790.7 | 144.6 | 271.3 | 61.3 | 281 | 262.8 | 57.3 | 192.6 | 216.7 | 121.2
616 | 409 | 560.7 | 224.28 | 262.1704 | 258.8 | 250.1 | 265.1 | 247.8 | 499.1 | 37.6 | 20.6 | 67.6 | 4.6 | 250.9 | 6.2 | 768.6 | 769.5 | 836 | 677.3 | 891.6 | 732.8 | 714 | 768.5 | 676.7 | 792.3 | 144.8 | 271.2 | 61.5 | 281.3 | 263.2 | 57.5 | 193 | 217.4 | 121.5
617 | 410 | 558.3 | 223.32 | 261.0482 | 259.3 | 250.7 | 264.3 | 248.6 | 496.2 | 37.7 | 20.6 | 67.7 | 4.8 | 248.2 | 6 | 770.9 | 770 | 839.5 | 680.7 | 892.9 | 734.1 | 717.2 | 776.4 | 681.5 | 794.8 | 145.1 | 271.3 | 61.7 | 281.8 | 264.1 | 57.7 | 193.6 | 218 | 121.8
618 | 411 | 558 | 223.2 | 260.9079 | 259 | 251.5 | 264 | 249.1 | 500.7 | 37.9 | 20.6 | 67.7 | 5 | 246.9 | 7.8 | 773.3 | 770.3 | 843.5 | 683.9 | 892.4 | 735.5 | 718 | 784.8 | 686.3 | 796.7 | 145.3 | 271.3 | 61.8 | 281.8 | 264.7 | 57.9 | 194.1 | 218.6 | 122.2
619 | 412 | 558.4 | 223.36 | 261.095 | 259.2 | 250.7 | 263.5 | 249.2 | 500.3 | 38 | 20.6 | 67.8 | 4.5 | 251.7 | 10 | 775.8 | 770.3 | 843.9 | 687.1 | 897.4 | 736.9 | 716.5 | 793.6 | 690.6 | 796.8 | 145.5 | 271.3 | 62 | 282 | 265.6 | 58 | 194.5 | 219.2 | 122.5
620 | 413 | 560.9 | 224.36 | 262.2639 | 258.5 | 249.4 | 263.5 | 249.7 | 505.5 | 38 | 20.6 | 67.9 | 3.8 | 243.4 | 10.4 | 778.5 | 770.2 | 847.1 | 690.6 | 898.6 | 738 | 716 | 791.3 | 694.4 | 796.7 | 145.8 | 271.3 | 62.2 | 282.2 | 265.7 | 58.2 | 195 | 219.8 | 122.8
621 | 414 | 560.7 | 224.28 | 262.1704 | 257.5 | 249.1 | 263.5 | 249.2 | 509.6 | 38.1 | 20.6 | 68 | 4 | 261.5 | 10.7 | 780.9 | 770.2 | 845.4 | 693.7 | 895.9 | 739 | 719.7 | 796.5 | 698.2 | 799.2 | 146 | 271.5 | 62.4 | 282.4 | 265.7 | 58.4 | 195.2 | 220.3 | 123.2
622 | 415 | 560.1 | 224.04 | 261.8899 | 257 | 249 | 263.5 | 248.4 | 526.6 | 38.1 | 20.6 | 68 | 3.9 | 243.7 | 11.3 | 782.8 | 770.8 | 849.1 | 696.7 | 899.2 | 740.1 | 720.2 | 805.4 | 702 | 801 | 146.2 | 271.3 | 62.5 | 282.7 | 265.6 | 58.6 | 195.6 | 220.8 | 123.5
623 | 416 | 560.5 | 224.2 | 262.0769 | 257.1 | 249.9 | 262.9 | 248.3 | 529.5 | 38.2 | 20.6 | 68.1 | 4.6 | 253.5 | 11.5 | 784.2 | 771 | 847.5 | 699.9 | 900.4 | 741.1 | 721.2 | 796.1 | 705.3 | 800.6 | 146.5 | 271.2 | 62.7 | 282.7 | 265.7 | 58.8 | 196.1 | 221.4 | 123.8
624 | 417 | 562.4 | 224.96 | 262.9653 | 256.6 | 250.5 | 261.2 | 248 | 518.6 | 38.2 | 20.5 | 68.3 | 4.5 | 246.5 | 11.2 | 785.8 | 772.1 | 844.7 | 702.3 | 901.9 | 741.7 | 719.4 | 791.6 | 708.3 | 801.5 | 146.7 | 271.4 | 62.9 | 283.2 | 265.8 | 58.9 | 196.5 | 222.3 | 124.1
625 | 418 | 562.3 | 224.92 | 262.9185 | 256.1 | 249.8 | 260.6 | 247.5 | 518.5 | 38.3 | 20.5 | 68.5 | 4.4 | 250.1 | 10.6 | 787.8 | 773.2 | 843.7 | 705.1 | 900.9 | 742.6 | 717.2 | 784.3 | 711.2 | 801.5 | 146.9 | 271.5 | 63 | 283.4 | 265.7 | 59.1 | 196.8 | 223 | 124.5
626 | 419 | 562.4 | 224.96 | 262.9653 | 256 | 249.9 | 261.3 | 247.2 | 511.7 | 38.4 | 20.5 | 68.6 | 4.2 | 250.1 | 10.3 | 789.7 | 774.4 | 847.2 | 708 | 901.2 | 743.8 | 717.6 | 790 | 714.3 | 800.3 | 147.2 | 271.6 | 63.2 | 283.1 | 265.8 | 59.3 | 197.3 | 223.6 | 124.8
627 | 420 | 562.8 | 225.12 | 263.1523 | 255.6 | 249.6 | 261.4 | 247 | 520.7 | 38.4 | 20.5 | 68.7 | 4.4 | 248.4 | 9.9 | 791.5 | 775.5 | 849.9 | 711.7 | 899.5 | 744.9 | 722.2 | 795.7 | 717.4 | 801.3 | 147.4 | 272 | 63.4 | 283.4 | 266.3 | 59.5 | 197.7 | 224.3 | 125.1
628 | 421 | 562.6 | 225.04 | 263.0588 | 256.3 | 250.1 | 259.9 | 246.9 | 528.1 | 38.5 | 20.5 | 68.8 | 4.1 | 247.9 | 9.4 | 793.7 | 777.1 | 849.6 | 715.1 | 900.7 | 745.9 | 722.4 | 792.1 | 720.2 | 803 | 147.7 | 272.5 | 63.6 | 283.5 | 266.4 | 59.7 | 198.2 | 225.1 | 125.5
629 | 422 | 563.3 | 225.32 | 263.3861 | 257.3 | 251 | 260.4 | 247.5 | 523.1 | 38.6 | 20.5 | 68.9 | 4.4 | 248.6 | 8.8 | 795.7 | 777.5 | 853.5 | 718.8 | 901.7 | 746.6 | 722.7 | 795.2 | 722.8 | 802.8 | 147.9 | 272.5 | 63.7 | 283.3 | 266.3 | 59.8 | 198.5 | 225.8 | 125.8
630 | 423 | 563.2 | 225.28 | 263.3393 | 258.1 | 251.5 | 260.9 | 247.1 | 522.8 | 38.7 | 20.5 | 69 | 4.3 | 250 | 8.5 | 798 | 777.8 | 854.2 | 722.9 | 899.1 | 747.4 | 721.8 | 791.5 | 725.1 | 801.7 | 148.1 | 272.6 | 63.9 | 283.2 | 266.3 | 60 | 198.8 | 226.5 | 126.1
631 | 424 | 562.5 | 225 | 263.012 | 258.6 | 251.5 | 260.4 | 246.6 | 516.1 | 38.7 | 20.5 | 69 | 4.2 | 251.6 | 8.2 | 800.7 | 778.6 | 853.3 | 726.8 | 900.2 | 748.1 | 723.4 | 782.4 | 727.3 | 802.3 | 148.4 | 272.7 | 64.1 | 283.6 | 266.3 | 60.2 | 199.1 | 227.2 | 126.4
632 | 425 | 563.7 | 225.48 | 263.5731 | 258.9 | 250.2 | 259.3 | 246 | 505.8 | 38.8 | 20.5 | 69 | 4.2 | 252.7 | 7.7 | 803.2 | 779.5 | 852.6 | 730.8 | 895.2 | 749 | 724.3 | 775.8 | 729.6 | 803.1 | 148.6 | 273.1 | 64.3 | 283.2 | 266.8 | 60.4 | 199.5 | 227.9 | 126.7
633 | 426 | 563.1 | 225.24 | 263.2926 | 259.3 | 248.8 | 259.6 | 246.5 | 502.8 | 38.9 | 20.5 | 69.1 | 4.1 | 250.6 | 7.5 | 805.4 | 780.6 | 850.4 | 734.7 | 896.4 | 750.2 | 723 | 781.5 | 732.2 | 804.9 | 148.9 | 273.2 | 64.4 | 283.3 | 267 | 60.6 | 199.8 | 228.6 | 127.1
634 | 427 | 562 | 224.8 | 262.7782 | 260.2 | 249 | 260.8 | 247.2 | 511.7 | 39 | 20.5 | 69.1 | 4.2 | 247.1 | 7.5 | 807.5 | 781.2 | 850.6 | 738.8 | 893.8 | 751.1 | 724 | 781.7 | 734.6 | 806.6 | 149.1 | 273.2 | 64.6 | 283.5 | 267 | 60.7 | 200.1 | 229.2 | 127.4
635 | 428 | 562.2 | 224.88 | 262.8718 | 260.8 | 249.8 | 261.6 | 248.1 | 510.4 | 39.1 | 20.5 | 69.2 | 4.2 | 242.3 | 7.6 | 809.6 | 781.5 | 845.9 | 742.4 | 889.9 | 752.1 | 726.3 | 773.3 | 736.8 | 808.5 | 149.4 | 273.1 | 64.8 | 283.2 | 267.1 | 60.9 | 200.4 | 229.8 | 127.7
636 | 429 | 562.1 | 224.84 | 262.825 | 259.9 | 249.7 | 261.2 | 249.2 | 505.5 | 39.1 | 20.5 | 69.3 | 4.1 | 241.5 | 7.5 | 811.3 | 781.6 | 845.4 | 746 | 890.8 | 753.3 | 728.2 | 757.8 | 739.2 | 810.3 | 149.6 | 273.2 | 64.9 | 283.8 | 267.4 | 61.1 | 200.7 | 230.4 | 128.1
637 | 430 | 563.1 | 225.24 | 263.2926 | 259.8 | 250.5 | 262 | 249.9 | 495.7 | 39.1 | 20.5 | 69.3 | 3.8 | 244.1 | 7.2 | 813.1 | 781.6 | 843.7 | 749.8 | 895.7 | 754.5 | 723.5 | 747.9 | 742 | 809.9 | 149.9 | 273.1 | 65.1 | 284.2 | 267.5 | 61.3 | 201.1 | 230.9 | 128.4
638 | 431 | 564.6 | 225.84 | 263.9939 | 260.5 | 251.6 | 261.8 | 250.4 | 490.4 | 39 | 20.5 | 69.3 | 4.3 | 238.7 | 7.3 | 815.1 | 781.5 | 844.8 | 753.9 | 898.8 | 755.6 | 722.1 | 741.9 | 745.2 | 811.2 | 150.2 | 273.4 | 65.3 | 284.7 | 267.5 | 61.5 | 201.6 | 231.5 | 128.7
639 | 432 | 562.7 | 225.08 | 263.1056 | 261.4 | 251.7 | 261.6 | 250.3 | 486.6 | 39 | 20.5 | 69.3 | 4.2 | 243.8 | 7.1 | 817.2 | 781.7 | 851.6 | 758.5 | 897.8 | 756.8 | 723.4 | 752.1 | 748.4 | 811.8 | 150.4 | 273.8 | 65.5 | 285.7 | 267.7 | 61.6 | 201.9 | 232 | 129.1
640 | 433 | 563.2 | 225.28 | 263.3393 | 262.6 | 251.1 | 262.5 | 249.8 | 492 | 39 | 20.5 | 69.3 | 4.5 | 234.4 | 7.1 | 819.3 | 782.7 | 852.7 | 762.5 | 896.6 | 758.1 | 727 | 764.9 | 751.2 | 815 | 150.7 | 274 | 65.7 | 286.4 | 268.5 | 61.8 | 202.5 | 232.6 | 129.4
641 | 434 | 564.1 | 225.64 | 263.7602 | 263.5 | 250.1 | 262.7 | 250.3 | 515.8 | 38.9 | 20.5 | 69.4 | 4.7 | 243.2 | 6.8 | 820.8 | 783 | 858.6 | 766.3 | 899.5 | 759.5 | 727.8 | 773.9 | 753.7 | 814.9 | 151 | 274.2 | 65.8 | 286.4 | 269.6 | 62 | 203.1 | 233.2 | 129.8
642 | 435 | 563.1 | 225.24 | 263.2926 | 264.2 | 250.3 | 263.6 | 250.5 | 526.6 | 38.9 | 20.5 | 69.4 | 4.3 | 246.8 | 6.5 | 822.6 | 782.7 | 862.2 | 769.9 | 902.6 | 761 | 723.4 | 781.8 | 755.4 | 814 | 151.3 | 274.3 | 66 | 286.9 | 270.3 | 62.2 | 203.4 | 233.8 | 130.1
643 | 436 | 562.9 | 225.16 | 263.1991 | 264.9 | 250.2 | 264.2 | 250.9 | 531 | 38.9 | 20.5 | 69.5 | 4.2 | 249.7 | 6.3 | 824.3 | 783 | 864.8 | 773.4 | 903.3 | 761.9 | 723.4 | 786.4 | 756.8 | 816.7 | 151.6 | 274.4 | 66.2 | 287 | 270.5 | 62.3 | 203.8 | 234.3 | 130.4
644 | 437 | 563.9 | 225.56 | 263.6666 | 265.3 | 249.3 | 264.2 | 251.2 | 522.9 | 39 | 20.5 | 69.7 | 4.1 | 252.9 | 5.9 | 825.9 | 783.6 | 865 | 776.6 | 902 | 762.8 | 723.5 | 778.3 | 757.8 | 818.3 | 151.8 | 274.6 | 66.4 | 286.7 | 270.4 | 62.5 | 204.2 | 234.8 | 130.7
645 | 438 | 564.8 | 225.92 | 264.0875 | 266.4 | 249.5 | 264.6 | 251.4 | 510.7 | 39 | 20.5 | 69.8 | 4.2 | 252.7 | 6 | 827.6 | 784.5 | 863.5 | 780 | 904.6 | 763.6 | 722.2 | 767.4 | 758.9 | 818.8 | 152.1 | 274.8 | 66.5 | 286.2 | 270.6 | 62.7 | 204.7 | 235.3 | 131
646 | 439 | 564.7 | 225.88 | 264.0407 | 267 | 250.8 | 264.9 | 251.8 | 501.4 | 39 | 20.5 | 69.8 | 4.4 | 249.4 | 6.2 | 829.5 | 784.9 | 862.7 | 783.4 | 905.2 | 764.2 | 722.7 | 762.7 | 760.2 | 818.6 | 152.4 | 275.2 | 66.7 | 287.6 | 271 | 62.9 | 205 | 235.8 | 131.3
647 | 440 | 565.2 | 226.08 | 264.2745 | 267.2 | 252.6 | 265.2 | 252.8 | 497.5 | 39.1 | 20.5 | 69.8 | 4.4 | 242.9 | 5.9 | 831.7 | 784.8 | 863.7 | 786.4 | 907.3 | 764.6 | 721.8 | 761.3 | 761.2 | 817.3 | 152.7 | 275.6 | 66.9 | 287.7 | 271.1 | 63.1 | 205.3 | 236.3 | 131.7
648 | 441 | 565 | 226 | 264.181 | 267.5 | 254.5 | 265.5 | 253.2 | 499.9 | 39.2 | 20.5 | 69.9 | 4.5 | 221.4 | 5.7 | 833.4 | 785.3 | 863.6 | 789.5 | 905.7 | 765.1 | 724.1 | 767.3 | 762.1 | 817.5 | 153 | 276.1 | 67.1 | 289 | 271.4 | 63.2 | 205.9 | 236.9 | 132
649 | 442 | 564.4 | 225.76 | 263.9004 | 268 | 255.9 | 265.2 | 253.7 | 507.1 | 39.2 | 20.5 | 70 | 4.4 | 246.1 | 5.6 | 835 | 785.3 | 864.7 | 792.4 | 905.9 | 765.8 | 724.8 | 770.6 | 762.9 | 819.4 | 153.3 | 276 | 67.2 | 288.9 | 271.8 | 63.4 | 206.3 | 237.6 | 132.4
650 | 443 | 564 | 225.6 | 263.7134 | 268.1 | 256.2 | 265.8 | 253.9 | 507.4 | 39.2 | 20.5 | 70 | 4.3 | 235.2 | 5.5 | 836.5 | 785.2 | 865.7 | 795.6 | 906.8 | 766.6 | 722.4 | 767.5 | 763.7 | 820.6 | 153.6 | 276 | 67.4 | 289 | 271.7 | 63.6 | 206.7 | 238.2 | 132.7
651 | 444 | 564.5 | 225.8 | 263.9472 | 268.4 | 257.2 | 266.7 | 254.3 | 498.8 | 39.2 | 20.5 | 70.1 | 4.5 | 220 | 4.9 | 838.3 | 786.5 | 865.3 | 798.9 | 908.7 | 767.3 | 722.4 | 765.4 | 764.7 | 821.5 | 153.9 | 276.2 | 67.6 | 288.9 | 271.8 | 63.8 | 207.2 | 238.7 | 133.1
652 | 445 | 565.1 | 226.04 | 264.2277 | 268.6 | 258.6 | 266.6 | 254.5 | 494.9 | 39.1 | 20.5 | 70.3 | 4.3 | 245.5 | 5.1 | 840 | 787.2 | 866.4 | 802.2 | 909.7 | 768.1 | 723.8 | 764.3 | 765.9 | 820.2 | 154.2 | 276.3 | 67.8 | 288.9 | 272.7 | 64 | 207.7 | 239.3 | 133.4
653 | 446 | 565.2 | 226.08 | 264.2745 | 268.9 | 260.3 | 265.8 | 255.6 | 497.2 | 39.2 | 20.4 | 70.4 | 3.5 | 246 | 7 | 841.7 | 787.3 | 866.2 | 805.1 | 906.6 | 768.8 | 722.6 | 755.6 | 766.8 | 821.9 | 154.5 | 276.4 | 68 | 289 | 273.3 | 64.1 | 208.3 | 239.9 | 133.7
654 | 447 | 563.3 | 225.32 | 263.3861 | 269 | 262 | 266.8 | 257 | 489.6 | 39.3 | 20.5 | 70.4 | 4.1 | 243.5 | 7.3 | 843 | 788.1 | 865.9 | 807.8 | 906.3 | 769.8 | 721 | 756.5 | 768 | 822.3 | 154.8 | 276.7 | 68.1 | 289.3 | 273.6 | 64.3 | 208.7 | 240.4 | 134.1
655 | 448 | 562.9 | 225.16 | 263.1991 | 269.5 | 263 | 267.6 | 257.5 | 494.9 | 39.4 | 20.4 | 70.5 | 4.1 | 242.1 | 7.3 | 844.4 | 788.9 | 866.3 | 810.6 | 906.1 | 770.7 | 720.3 | 759.8 | 769.2 | 822.4 | 155.2 | 276.7 | 68.3 | 289.3 | 274.2 | 64.5 | 209.2 | 240.9 | 134.4
656 | 449 | 563.3 | 225.32 | 263.3861 | 269.7 | 262.9 | 267.8 | 256.5 | 495.8 | 39.4 | 20.5 | 70.5 | 4.1 | 241.5 | 7.2 | 845.5 | 788.9 | 866.6 | 812.9 | 905.5 | 771.7 | 719 | 762.1 | 769.8 | 822.2 | 155.5 | 277.1 | 68.5 | 289.5 | 274.9 | 64.7 | 209.6 | 241.5 | 134.7
657 | 450 | 563 | 225.2 | 263.2458 | 268.7 | 262.4 | 268.6 | 255.7 | 505.6 | 39.5 | 20.4 | 70.7 | 4.4 | 255.4 | 7.1 | 846.5 | 789 | 867.8 | 815.2 | 903.2 | 772.8 | 720.2 | 768.4 | 770.5 | 821.5 | 155.8 | 277.6 | 68.7 | 289.8 | 275.6 | 64.9 | 210.1 | 242 | 135
658 | 451 | 563.7 | 225.48 | 263.5731 | 268.5 | 262.8 | 268.8 | 255.8 | 509.6 | 39.5 | 20.4 | 70.9 | 4.7 | 242.8 | 7.4 | 847.7 | 788.7 | 871 | 817.7 | 906 | 773.6 | 720.4 | 777.8 | 771.4 | 821.5 | 156.1 | 278.1 | 68.9 | 290.1 | 275.5 | 65 | 210.5 | 242.4 | 135.4
659 | 452 | 563.7 | 225.48 | 263.5731 | 268.5 | 262.5 | 268.5 | 255.5 | 531.6 | 39.6 | 20.4 | 71 | 4.3 | 258.3 | 7.1 | 848.7 | 789 | 871.4 | 819.7 | 904.5 | 774.3 | 721.4 | 791.5 | 771.8 | 820 | 156.4 | 278.5 | 69 | 289.6 | 275.5 | 65.2 | 210.8 | 242.9 | 135.7
660 | 453 | 564 | 225.6 | 263.7134 | 269.3 | 261.6 | 267.6 | 255.4 | 548.9 | 39.6 | 20.4 | 71.2 | 4.3 | 261 | 7.4 | 849.8 | 788.9 | 872.2 | 821.5 | 902.1 | 775.2 | 720.8 | 799 | 772.1 | 818.5 | 156.7 | 278.7 | 69.2 | 289.4 | 275.3 | 65.4 | 211.1 | 243.4 | 136
661 | 454 | 563 | 225.2 | 263.2458 | 269.7 | 261.9 | 267.6 | 256 | 568.1 | 39.5 | 20.4 | 71.4 | 4.5 | 250.7 | 7.6 | 851.2 | 789.7 | 872.3 | 823.6 | 902.8 | 776 | 722.6 | 803.3 | 772.3 | 819.8 | 157 | 279 | 69.4 | 289.6 | 274.8 | 65.6 | 211.4 | 243.9 | 136.3
662 | 455 | 564.3 | 225.72 | 263.8537 | 270.7 | 262.3 | 267.3 | 256.6 | 572.5 | 39.5 | 20.4 | 71.6 | 4.9 | 253.9 | 8.2 | 852.3 | 790.3 | 874.1 | 825.7 | 900.3 | 776.7 | 722.6 | 806.5 | 772.2 | 820.5 | 157.3 | 279.3 | 69.6 | 289.5 | 274.8 | 65.8 | 211.6 | 244.5 | 136.6
663 | 456 | 564.8 | 225.92 | 264.0875 | 271.5 | 262.1 | 266.5 | 257.6 | 577.5 | 39.6 | 20.4 | 71.7 | 4.6 | 257 | 8.5 | 852.7 | 789.6 | 871.2 | 826.9 | 896.5 | 777.7 | 721.6 | 802.5 | 772 | 815.5 | 157.7 | 279.9 | 69.7 | 289.1 | 274.6 | 65.9 | 211.9 | 245 | 136.9
664 | 457 | 564.7 | 225.88 | 264.0407 | 271.6 | 262 | 266.8 | 258.4 | 582.8 | 39.8 | 20.4 | 71.7 | 4.1 | 262.7 | 8.7 | 853.5 | 790 | 868.8 | 828.1 | 894.6 | 778.7 | 718.2 | 801 | 771.9 | 812.1 | 158 | 280.7 | 69.9 | 288.9 | 274.4 | 66.1 | 212.2 | 245.6 | 137.2
665 | 458 | 565.1 | 226.04 | 264.2277 | 273.9 | 261 | 268 | 258.7 | 600.2 | 39.9 | 20.4 | 71.7 | 4.6 | 263.5 | 10.6 | 854.3 | 789.8 | 865.8 | 828.9 | 894.4 | 779.4 | 718.1 | 806 | 771.9 | 812.9 | 158.3 | 281.5 | 70.1 | 288.1 | 275 | 66.3 | 212.5 | 246.2 | 137.5
666 | 459 | 564.1 | 225.64 | 263.7602 | 275.5 | 260.9 | 269.5 | 259.3 | 608.8 | 39.9 | 20.4 | 71.8 | 5.1 | 261.4 | 12.3 | 854.9 | 789.9 | 866.9 | 830 | 892.6 | 780.8 | 721.2 | 812.2 | 772.1 | 813.8 | 158.7 | 282.2 | 70.3 | 287.9 | 275.1 | 66.5 | 212.9 | 246.6 | 137.8
667 | 460 | 562.8 | 225.12 | 263.1523 | 276.5 | 261.4 | 271 | 260 | 623.1 | 40 | 20.4 | 71.9 | 6 | 254.7 | 12.3 | 855.7 | 789.9 | 867.3 | 831.2 | 891.5 | 782.4 | 717.4 | 814.3 | 772.4 | 812.6 | 159 | 283.1 | 70.5 | 288 | 275.2 | 66.7 | 213.2 | 247.1 | 138.2
668 | 461 | 562.2 | 224.88 | 262.8718 | 277.6 | 260.2 | 273.4 | 261 | 643.1 | 40.1 | 20.4 | 72 | 6 | 242.8 | 11.2 | 857.4 | 790.2 | 868.4 | 832.7 | 889.9 | 783.8 | 717.1 | 818.3 | 772.9 | 810.2 | 159.4 | 283.9 | 70.6 | 288 | 275.6 | 66.8 | 213.5 | 247.7 | 138.5
669 | 462 | 562.5 | 225 | 263.012 | 278.5 | 259.2 | 274.9 | 261.4 | 647.4 | 40.1 | 20.4 | 72.1 | 5.6 | 244.8 | 10 | 858.6 | 790.4 | 870 | 834.2 | 885.6 | 784.7 | 714.1 | 820.1 | 773.2 | 807.2 | 159.7 | 284.6 | 70.8 | 287.9 | 275.8 | 67 | 213.8 | 248.1 | 138.8
670 | 463 | 562.9 | 225.16 | 263.1991 | 277.5 | 259.3 | 276.5 | 261.8 | 645.6 | 40.2 | 20.4 | 72.2 | 5.3 | 240.9 | 8.8 | 859.6 | 790.2 | 870.6 | 835.3 | 886.5 | 785.1 | 715 | 820 | 773.6 | 805.8 | 160.1 | 285.6 | 71 | 287.6 | 276 | 67.2 | 214.2 | 248.6 | 139.2
671 | 464 | 563.4 | 225.36 | 263.4329 | 276.6 | 259.4 | 277.6 | 262.5 | 660.3 | 40.3 | 20.4 | 72.1 | 4.5 | 246.7 | 9.6 | 860.4 | 789.2 | 871.4 | 836.4 | 883.2 | 785.3 | 716.9 | 822.1 | 773.7 | 803.6 | 160.5 | 286.3 | 71.2 | 287.5 | 276.1 | 67.4 | 214.5 | 249.1 | 139.5
672 | 465 | 563.6 | 225.44 | 263.5264 | 277.4 | 258.6 | 278.1 | 262.9 | 683 | 40.4 | 20.4 | 72 | 4.6 | 245.9 | 10.9 | 860.7 | 789.2 | 870.8 | 837 | 882.2 | 785.4 | 720 | 825.3 | 773.4 | 802.6 | 160.9 | 287.1 | 71.4 | 287.9 | 276.4 | 67.6 | 215 | 249.7 | 139.9
673 | 466 | 563.4 | 225.36 | 263.4329 | 278.4 | 257.2 | 278.1 | 262.8 | 680.7 | 40.5 | 20.4 | 72 | 4.7 | 245.4 | 11.9 | 860.7 | 790 | 871.5 | 837.6 | 886 | 786 | 721.6 | 826.1 | 772.8 | 806.2 | 161.3 | 287.5 | 71.6 | 287.2 | 277 | 67.7 | 215.4 | 250.3 | 140.3
674 | 467 | 563.7 | 225.48 | 263.5731 | 279.4 | 256.4 | 278.1 | 262.9 | 664.5 | 40.6 | 20.4 | 71.9 | 4.6 | 250.9 | 12.7 | 860.5 | 790.5 | 870.1 | 838.1 | 888.8 | 786.3 | 722.1 | 825.7 | 772.1 | 804.2 | 161.7 | 288.1 | 71.7 | 286.6 | 277.2 | 67.9 | 215.7 | 250.9 | 140.6
675 | 468 | 564.3 | 225.72 | 263.8537 | 280 | 257.5 | 278.4 | 263 | 643.7 | 40.7 | 20.4 | 71.9 | 4.3 | 251.8 | 13.1 | 860.7 | 791.5 | 869.5 | 838.6 | 889.9 | 786.7 | 725.4 | 820.1 | 771.6 | 806.4 | 162.1 | 288.4 | 71.9 | 286.4 | 277.9 | 68.1 | 216.2 | 251.4 | 141
676 | 469 | 561.8 | 224.72 | 262.6847 | 280.3 | 258.4 | 279.8 | 263.5 | 622.5 | 40.8 | 20.4 | 71.9 | 4.3 | 251.9 | 13.4 | 860.8 | 793 | 869.4 | 839.2 | 892.2 | 787 | 724 | 806.8 | 771.2 | 809.6 | 162.5 | 288.7 | 72.1 | 285.8 | 278.6 | 68.3 | 216.6 | 251.9 | 141.3
677 | 470 | 561.5 | 224.6 | 262.5445 | 281.2 | 258.7 | 279.9 | 263.7 | 603.1 | 40.8 | 20.4 | 71.8 | 4.3 | 265.4 | 13.1 | 861.6 | 795.6 | 870.6 | 840.3 | 895.5 | 787.7 | 724 | 802.4 | 771.5 | 810.5 | 162.9 | 289 | 72.3 | 285.4 | 279 | 68.5 | 217.1 | 252.4 | 141.6
678 | 471 | 562.7 | 225.08 | 263.1056 | 281.7 | 259.1 | 279.1 | 264 | 585.9 | 40.9 | 20.4 | 71.7 | 4.5 | 272.4 | 12 | 863 | 797.2 | 871.4 | 841.9 | 895.2 | 788.1 | 723.8 | 800.3 | 772 | 812.1 | 163.4 | 289.1 | 72.5 | 285.4 | 279.7 | 68.6 | 217.6 | 252.8 | 142
679 | 472 | 563.6 | 225.44 | 263.5264 | 282.1 | 259.8 | 279.1 | 263.8 | 579.4 | 40.9 | 20.4 | 71.6 | 4.4 | 264.4 | 9.8 | 863.8 | 797.9 | 871.9 | 843.9 | 894.8 | 788.5 | 725.8 | 803.6 | 772.5 | 812 | 163.8 | 289.3 | 72.7 | 285.7 | 280.5 | 68.8 | 217.9 | 253.3 | 142.3
680 | 473 | 563.5 | 225.4 | 263.4796 | 281.6 | 259.8 | 279.6 | 263.2 | 596.3 | 41 | 20.4 | 71.6 | 4.3 | 253.6 | 9.2 | 863.8 | 798.2 | 870.3 | 844.8 | 893.2 | 789 | 727.6 | 806.4 | 772.9 | 813.4 | 164.2 | 289.5 | 72.9 | 285.7 | 281.6 | 69 | 218.4 | 253.9 | 142.6
681 | 474 | 562.8 | 225.12 | 263.1523 | 281.8 | 259.7 | 279.8 | 263.7 | 593.3 | 41 | 20.4 | 71.6 | 4.4 | 260.8 | 8.6 | 864.4 | 798.7 | 870.3 | 845 | 894.3 | 789.6 | 724.8 | 810.8 | 773 | 813.8 | 164.6 | 289.7 | 73 | 285.1 | 281.8 | 69.2 | 218.8 | 254.5 | 143
682 | 475 | 563.4 | 225.36 | 263.4329 | 282.7 | 260.3 | 279.4 | 263.2 | 586 | 41.1 | 20.4 | 71.7 | 4.8 | 251.2 | 9.4 | 865.6 | 798.7 | 870.9 | 845.8 | 891.3 | 789.9 | 726.2 | 811.8 | 773.1 | 814.7 | 165 | 289.9 | 73.2 | 284.7 | 281.4 | 69.4 | 219 | 254.9 | 143.3
683 | 476 | 563 | 225.2 | 263.2458 | 282.5 | 260.5 | 279.8 | 263 | 590.8 | 41.1 | 20.4 | 71.8 | 4.7 | 261.3 | 10.2 | 866 | 799.5 | 870.6 | 847.1 | 890 | 790.5 | 728.6 | 817.3 | 773.4 | 817.1 | 165.4 | 290.2 | 73.4 | 284.4 | 281 | 69.6 | 219.2 | 255.4 | 143.6
684 | 477 | 562.9 | 225.16 | 263.1991 | 282.6 | 260.9 | 280.7 | 263.4 | 609.1 | 41.1 | 20.4 | 71.9 | 4.6 | 260.5 | 10.5 | 865.7 | 801.4 | 870.8 | 848.1 | 892.1 | 791 | 729.4 | 814.2 | 773.5 | 819.1 | 165.8 | 290.6 | 73.6 | 284.1 | 280.6 | 69.8 | 219.5 | 256 | 143.9
685 | 478 | 562.4 | 224.96 | 262.9653 | 282.8 | 261.4 | 280.8 | 263.6 | 594.9 | 41 | 20.4 | 71.9 | 4.7 | 259.7 | 10.6 | 866.1 | 803.1 | 871.9 | 849.5 | 892.7 | 791.4 | 728.7 | 809.4 | 773.8 | 819.5 | 166.2 | 290.6 | 73.8 | 283.9 | 280.6 | 69.9 | 219.9 | 256.6 | 144.2
686 | 479 | 563 | 225.2 | 263.2458 | 282.2 | 261.8 | 280.6 | 264 | 588.4 | 40.9 | 20.4 | 71.8 | 4.4 | 256.2 | 10.9 | 866.2 | 803.7 | 873 | 850.6 | 892.5 | 791.5 | 731 | 811.8 | 774.1 | 821.8 | 166.6 | 290.6 | 74 | 284 | 280.8 | 70.1 | 220.2 | 257.1 | 144.5
687 | 480 | 565.9 | 226.36 | 264.6018 | 283 | 262.2 | 280 | 264 | 592.2 | 40.8 | 20.4 | 71.7 | 4.3 | 256.2 | 11.1 | 866.2 | 804.2 | 873.3 | 851.8 | 896.6 | 791.9 | 731.3 | 810.9 | 774.4 | 824 | 167 | 290.6 | 74.1 | 284.1 | 281.2 | 70.3 | 220.6 | 257.7 | 144.8
688 | 481 | 566.1 | 226.44 | 264.6953 | 282.8 | 262.9 | 280.1 | 263.8 | 582.1 | 40.8 | 20.4 | 71.7 | 4.2 | 257.8 | 10.5 | 866.2 | 804.6 | 872.3 | 852.9 | 899.3 | 792.2 | 729.4 | 802.3 | 774.4 | 823.7 | 167.3 | 290.1 | 74.3 | 284.3 | 281.5 | 70.5 | 221.1 | 258.2 | 145.2
689 | 482 | 566.4 | 226.56 | 264.8356 | 283.2 | 263.5 | 280.4 | 263.6 | 566.8 | 40.9 | 20.4 | 71.8 | 4.6 | 253.3 | 10 | 866.4 | 803.9 | 869 | 853.1 | 902.3 | 792.5 | 727.3 | 790.6 | 774.4 | 822.9 | 167.7 | 289.8 | 74.5 | 284.1 | 281.3 | 70.7 | 221.4 | 258.7 | 145.4
690 | 483 | 564.4 | 225.76 | 263.9004 | 284 | 264.3 | 280.4 | 263.7 | 548.1 | 40.9 | 20.4 | 72 | 4.2 | 255.1 | 9.5 | 866.9 | 803.7 | 868.7 | 853.9 | 909.8 | 792.9 | 725.4 | 782.1 | 774.9 | 823.3 | 168.1 | 289.7 | 74.7 | 283.7 | 281.1 | 70.9 | 221.6 | 259.2 | 145.8
691 | 484 | 563.6 | 225.44 | 263.5264 | 283.5 | 264.8 | 281.1 | 263.5 | 538.9 | 41 | 20.4 | 72.1 | 4.3 | 263.9 | 9.5 | 867.1 | 804.4 | 868.1 | 854.9 | 909.7 | 793.5 | 726.7 | 774.7 | 775.7 | 824.5 | 168.5 | 289.6 | 74.9 | 284.1 | 281.3 | 71 | 222 | 259.6 | 146.1
692 | 485 | 563.3 | 225.32 | 263.3861 | 284.3 | 264.9 | 282.4 | 263.6 | 523.4 | 41.1 | 20.4 | 72.2 | 4.5 | 264.5 | 9.5 | 867.4 | 803.8 | 868.3 | 855.7 | 905.9 | 794 | 724.3 | 768.7 | 776.5 | 825 | 168.8 | 289.6 | 75 | 284.8 | 281.4 | 71.2 | 222.5 | 260.1 | 146.4
693 | 486 | 564.4 | 225.76 | 263.9004 | 285.2 | 265.1 | 282.9 | 263.9 | 511.5 | 41.1 | 20.4 | 72.3 | 4.5 | 259.3 | 9 | 867.9 | 804.8 | 869.2 | 856.7 | 903.1 | 794.5 | 724.1 | 771.4 | 777.1 | 825.8 | 169.2 | 289.5 | 75.2 | 285.1 | 281.8 | 71.4 | 222.9 | 260.5 | 146.8
694 | 487 | 565.1 | 226.04 | 264.2277 | 286.5 | 265.2 | 283.1 | 263.1 | 509.9 | 41.1 | 20.4 | 72.4 | 4.5 | 252.4 | 8.5 | 868.1 | 806.4 | 869.4 | 857.7 | 905.3 | 795.2 | 725.1 | 776 | 777.9 | 827.6 | 169.5 | 289.6 | 75.4 | 286 | 282.1 | 71.6 | 223.3 | 261 | 147.1
695 | 488 | 564.5 | 225.8 | 263.9472 | 286.9 | 265.3 | 283.1 | 262.6 | 512.6 | 41.2 | 20.4 | 72.6 | 4.7 | 254.1 | 8.7 | 868.5 | 806.2 | 868.8 | 858.6 | 908.8 | 795.9 | 724.8 | 776.2 | 778.6 | 828 | 169.9 | 289.8 | 75.6 | 286.2 | 282.7 | 71.8 | 223.7 | 261.4 | 147.4
696 | 489 | 564.4 | 225.76 | 263.9004 | 287.7 | 265.2 | 283.6 | 262.8 | 520.9 | 41.3 | 20.4 | 72.7 | 4.6 | 250.2 | 9.4 | 868.5 | 807.1 | 867.4 | 859.2 | 914.2 | 796.5 | 726.6 | 783.1 | 779.3 | 828.4 | 170.2 | 290 | 75.8 | 286.2 | 283 | 72 | 224.1 | 261.9 | 147.7
697 | 490 | 564.9 | 225.96 | 264.1342 | 288.5 | 265.1 | 282.9 | 262.9 | 540.2 | 41.4 | 20.4 | 72.9 | 4.2 | 269 | 8.7 | 869.1 | 808.4 | 867.2 | 860.3 | 917.8 | 797.3 | 724.4 | 785.6 | 779.9 | 828.3 | 170.5 | 290.2 | 76 | 285.8 | 283.2 | 72.2 | 224.4 | 262.3 | 148
698 | 491 | 562.8 | 225.12 | 263.1523 | 289.1 | 265.1 | 282.8 | 262.8 | 547.3 | 41.5 | 20.4 | 73 | 4.1 | 277.4 | 7.8 | 869.5 | 808.1 | 866.1 | 861.3 | 925.4 | 798.1 | 722.9 | 784.3 | 780.6 | 825.9 | 170.8 | 290.1 | 76.2 | 285.6 | 283.4 | 72.4 | 224.8 | 262.8 | 148.3
699 | 492 | 562.2 | 224.88 | 262.8718 | 290.7 | 264.6 | 283.4 | 262.6 | 552.6 | 41.5 | 20.3 | 73.2 | 4.1 | 277.2 | 7.4 | 870.2 | 808.4 | 864.9 | 861.6 | 925.9 | 799 | 719.8 | 786.8 | 781.4 | 823.6 | 171.1 | 290.3 | 76.3 | 285.7 | 283.5 | 72.5 | 225.1 | 263.2 | 148.7
700 | 493 | 561.8 | 224.72 | 262.6847 | 291.4 | 264 | 284.1 | 262.8 | 564.3 | 41.4 | 20.4 | 73.3 | 4.6 | 268.9 | 7.2 | 871.1 | 809.4 | 866.2 | 862.3 | 922.7 | 799.7 | 717.8 | 795.2 | 782.1 | 822.1 | 171.5 | 290.7 | 76.5 | 286.2 | 284.1 | 72.7 | 225.5 | 263.6 | 149
701 | 494 | 563.7 | 225.48 | 263.5731 | 291.1 | 263.5 | 284.5 | 263.9 | 568.9 | 41.5 | 20.3 | 73.3 | 4.3 | 263.3 | 6.7 | 872 | 810.9 | 866.2 | 863.5 | 925.1 | 800.2 | 717.6 | 798.3 | 782.6 | 822.6 | 171.8 | 291.2 | 76.7 | 286.3 | 284.7 | 72.9 | 225.8 | 264 | 149.3
702 | 495 | 564.4 | 225.76 | 263.9004 | 292 | 262.5 | 285 | 264.7 | 563.9 | 41.6 | 20.3 | 73.3 | 4.4 | 246.3 | 6.3 | 872.6 | 812 | 867 | 864.4 | 924.3 | 800.6 | 718.9 | 795.9 | 783.2 | 823.1 | 172.1 | 291.2 | 76.9 | 286.7 | 284.8 | 73.1 | 226.2 | 264.4 | 149.6
703 | 496 | 565.2 | 226.08 | 264.2745 | 292.1 | 260.7 | 284.6 | 264.8 | 554.9 | 41.6 | 20.3 | 73.2 | 4.7 | 246.6 | 5.8 | 872.8 | 812.9 | 865.8 | 865.3 | 918.8 | 800.9 | 721.9 | 794.4 | 783.6 | 825.5 | 172.4 | 291.6 | 77.1 | 287.9 | 284.9 | 73.3 | 226.5 | 264.9 | 149.9
704 | 497 | 563.8 | 225.52 | 263.6199 | 292.8 | 259.1 | 284.5 | 265.2 | 555.5 | 41.7 | 20.3 | 73.2 | 4.3 | 246.5 | 5.5 | 873.1 | 813.6 | 864.7 | 866.1 | 914.8 | 801.4 | 723.4 | 795.9 | 784.1 | 827 | 172.8 | 291.7 | 77.3 | 289 | 285.4 | 73.5 | 226.9 | 265.3 | 150.2
705 | 498 | 563.3 | 225.32 | 263.3861 | 293.4 | 258.9 | 285.1 | 266.1 | 565 | 41.7 | 20.3 | 73.3 | 4.4 | 249.5 | 5.7 | 873.5 | 813.3 | 867.1 | 866.9 | 917.2 | 801.9 | 721.6 | 797.1 | 785 | 826.4 | 173.1 | 291.9 | 77.4 | 289.9 | 285.4 | 73.7 | 227.3 | 265.8 | 150.6
706 | 499 | 563.5 | 225.4 | 263.4796 | 293.7 | 259 | 285.4 | 266.2 | 586.6 | 41.7 | 20.3 | 73.4 | 4.5 | 261.3 | 6.6 | 873.3 | 812.7 | 867.7 | 868.2 | 913.6 | 802 | 723.8 | 805.2 | 785.7 | 826.2 | 173.4 | 292.5 | 77.6 | 289.7 | 285.2 | 73.9 | 227.5 | 266.2 | 151
707 | 500 | 563.2 | 225.28 | 263.3393 | 294.3 | 259.4 | 285.3 | 266.5 | 603.6 | 41.6 | 20.3 | 73.4 | 4.7 | 265.6 | 7.8 | 873.3 | 813.6 | 868.6 | 870.1 | 912.5 | 802.3 | 727.7 | 811.1 | 786.1 | 827.2 | 173.8 | 292.9 | 77.8 | 289.5 | 285.4 | 74.1 | 227.7 | 266.6 | 151.3
708 | 501 | 563.4 | 225.36 | 263.4329 | 295 | 259.5 | 285.4 | 267.5 | 614.6 | 41.6 | 20.3 | 73.5 | 4.6 | 250.1 | 8.2 | 873.2 | 813.5 | 869.1 | 871 | 916.4 | 802.5 | 729.5 | 812.4 | 786.1 | 827.9 | 174.1 | 293.5 | 78 | 289.2 | 285.8 | 74.3 | 228.1 | 267.1 | 151.6
709 | 502 | 563 | 225.2 | 263.2458 | 296 | 258.7 | 285.8 | 268.4 | 626 | 41.7 | 20.3 | 73.5 | 3.9 | 263.4 | 8.2 | 872.9 | 813.3 | 870 | 872 | 921.6 | 802.6 | 729.4 | 813.1 | 786 | 826.3 | 174.5 | 294.1 | 78.2 | 289.5 | 285.5 | 74.4 | 228.4 | 267.6 | 152
710 | 503 | 562.7 | 225.08 | 263.1056 | 295.4 | 258.4 | 286.8 | 268.9 | 609.4 | 41.8 | 20.3 | 73.5 | 4.4 | 259.7 | 7.5 | 872.8 | 814 | 869.7 | 873 | 918.3 | 802.7 | 729.2 | 809.6 | 785.7 | 825.7 | 174.8 | 294.6 | 78.4 | 290.4 | 285.4 | 74.7 | 228.7 | 268.1 | 152.2
711 | 504 | 565 | 226 | 264.181 | 295 | 258.1 | 287.1 | 269.5 | 594.1 | 41.9 | 20.3 | 73.6 | 4.6 | 251.6 | 6.8 | 872.7 | 815.4 | 868.3 | 873.7 | 918.7 | 803.1 | 728.1 | 804.3 | 785.3 | 825.7 | 175.2 | 295.1 | 78.6 | 292.5 | 285.5 | 74.8 | 229.1 | 268.6 | 152.6
712 | 505 | 565 | 226 | 264.181 | 295.8 | 258.2 | 287.5 | 269.4 | 593.2 | 41.8 | 20.3 | 73.6 | 4.4 | 245 | 6.2 | 872.8 | 816 | 869.9 | 874.6 | 922.1 | 803.9 | 723.1 | 806.9 | 785.7 | 824 | 175.5 | 295.4 | 78.7 | 292 | 285.5 | 75 | 229.5 | 269.2 | 153
713 | 506 | 565.4 | 226.16 | 264.368 | 297 | 258.9 | 288.6 | 269.7 | 603.6 | 41.8 | 20.3 | 73.7 | 4.5 | 233 | 5.9 | 872.8 | 814.9 | 869.7 | 875 | 921.8 | 804.1 | 721.5 | 809.1 | 786 | 820.6 | 175.9 | 295.5 | 78.9 | 291.2 | 285.6 | 75.2 | 229.7 | 269.6 | 153.4
714 | 507 | 564.7 | 225.88 | 264.0407 | 297.6 | 260 | 288.8 | 269.7 | 607.6 | 41.8 | 20.3 | 73.8 | 4.5 | 236.2 | 5.6 | 872.6 | 813.4 | 870.7 | 875.2 | 920.1 | 804.1 | 718.7 | 806.9 | 785.7 | 819 | 176.3 | 295.5 | 79.1 | 290.8 | 285.7 | 75.4 | 230 | 270.1 | 153.7
715 | 508 | 564 | 225.6 | 263.7134 | 297.3 | 261.1 | 288.2 | 269.5 | 608.6 | 41.8 | 20.3 | 73.8 | 4.4 | 243.7 | 5.5 | 872.7 | 813.2 | 870.8 | 875.3 | 920.6 | 804.1 | 717 | 810.6 | 785.1 | 817.1 | 176.7 | 296 | 79.3 | 291.1 | 285.9 | 75.6 | 230.3 | 270.6 | 154
716 | 509 | 564.5 | 225.8 | 263.9472 | 297.6 | 262.5 | 287.3 | 269.7 | 606.4 | 41.8 | 20.3 | 73.9 | 4 | 243 | 5.8 | 872.7 | 813.3 | 869 | 875.5 | 919.9 | 804.2 | 714.8 | 812.5 | 784.8 | 815.7 | 177 | 296.2 | 79.5 | 290.7 | 286.1 | 75.8 | 230.7 | 271 | 154.4
717 | 510 | 565.1 | 226.04 | 264.2277 | 298.4 | 263.2 | 287.2 | 270.7 | 608.1 | 41.8 | 20.3 | 74.1 | 4 | 241.6 | 6 | 872.6 | 813.7 | 867 | 875.8 | 913.2 | 804.3 | 715.9 | 813.9 | 784.6 | 816.1 | 177.4 | 296.2 | 79.7 | 290.4 | 286.2 | 76 | 231 | 271.4 | 154.7
718 | 511 | 564.7 | 225.88 | 264.0407 | 298.2 | 263.9 | 286.6 | 270.9 | 607 | 41.9 | 20.3 | 74.1 | 4.2 | 227.2 | 6 | 872.3 | 814.9 | 865.3 | 876 | 911.9 | 804.2 | 717.4 | 814.6 | 784.1 | 819.6 | 177.8 | 296.6 | 79.8 | 290.5 | 286.6 | 76.2 | 231.3 | 271.9 | 155
719 | 512 | 565.1 | 226.04 | 264.2277 | 298.6 | 263.1 | 286.2 | 271.1 | 599.2 | 42.1 | 20.3 | 74.1 | 4.2 | 236.8 | 6.1 | 871.9 | 816.1 | 864.3 | 875.9 | 913 | 804.6 | 716 | 804.4 | 783.4 | 821.2 | 178.2 | 296.8 | 80 | 290.8 | 287.1 | 76.4 | 231.7 | 272.5 | 155.3
720 | 513 | 564.3 | 225.72 | 263.8537 | 299.6 | 261.7 | 286.1 | 271.3 | 584.8 | 42.3 | 20.3 | 74.1 | 4 | 235.7 | 6.1 | 871.8 | 816.1 | 863.3 | 875.8 | 914.1 | 805.1 | 716.4 | 799.8 | 783.1 | 822.7 | 178.6 | 297.1 | 80.2 | 290.6 | 287.4 | 76.5 | 231.9 | 272.9 | 155.7
721 | 514 | 564.4 | 225.76 | 263.9004 | 300 | 260.7 | 286 | 270.7 | 570.2 | 42.3 | 20.3 | 74.1 | 4.1 | 217 | 6 | 871.8 | 816 | 866.1 | 876.1 | 919.8 | 805.4 | 714.8 | 794.8 | 783.4 | 822.5 | 179 | 297.2 | 80.4 | 291.6 | 287.7 | 76.7 | 232.2 | 273.3 | 156
722 | 515 | 564.4 | 225.76 | 263.9004 | 299.9 | 260.4 | 286 | 270.7 | 568.8 | 42.3 | 20.3 | 74.1 | 3.7 | 218.9 | 5.9 | 871.3 | 815.3 | 867.8 | 875.9 | 917.9 | 805.4 | 716.8 | 796.9 | 784 | 822.8 | 179.4 | 297.2 | 80.6 | 291.4 | 287.7 | 76.9 | 232.6 | 273.7 | 156.3
723 | 516 | 564.4 | 225.76 | 263.9004 | 299.5 | 259.4 | 286.2 | 270.6 | 566.2 | 42.2 | 20.3 | 74.2 | 4.6 | 211.1 | 5.5 | 870.4 | 815.5 | 867.6 | 875.8 | 923.3 | 805.6 | 716.7 | 796.5 | 784.1 | 823.6 | 179.7 | 297.4 | 80.8 | 291.4 | 287.6 | 77.1 | 232.9 | 274.2 | 156.6
724 | 517 | 564.2 | 225.68 | 263.8069 | 299.7 | 258.3 | 286.3 | 270.2 | 562.1 | 42.2 | 20.3 | 74.2 | 4.8 | 242.3 | 5 | 870.3 | 817.1 | 868.5 | 876 | 923.2 | 806 | 718 | 796.9 | 784.7 | 823.5 | 180.1 | 297.8 | 81 | 291.5 | 287.6 | 77.3 | 233 | 274.7 | 157
725 | 518 | 564.1 | 225.64 | 263.7602 | 298.7 | 258.2 | 286.4 | 269.6 | 561.3 | 42.2 | 20.3 | 74.4 | 4.5 | 223.4 | 5.1 | 869.7 | 817.9 | 868.7 | 875.8 | 922.4 | 806.5 | 719.5 | 793.5 | 785.4 | 823.6 | 180.4 | 297.9 | 81.1 | 292 | 287.5 | 77.5 | 233.3 | 275.1 | 157.3
726 | 519 | 563.2 | 225.28 | 263.3393 | 298.8 | 257.8 | 286.3 | 269.9 | 561.2 | 42.2 | 20.3 | 74.4 | 4.6 | 231 | 4.9 | 869.2 | 818.9 | 868.8 | 875.8 | 918.5 | 807.2 | 720.7 | 796 | 786.1 | 822.9 | 180.7 | 297.7 | 81.3 | 292.4 | 287.2 | 77.7 | 233.5 | 275.7 | 157.6
727 | 520 | 563.6 | 225.44 | 263.5264 | 297.8 | 257.2 | 286.5 | 269.7 | 567 | 42.2 | 20.3 | 74.4 | 4.6 | 215.6 | 4.2 | 869.4 | 820.4 | 870.8 | 876 | 921 | 807.9 | 722 | 796.6 | 786.9 | 824.6 | 181.1 | 297.7 | 81.5 | 292.3 | 286.6 | 77.9 | 233.8 | 276.2 | 157.9
728 | 521 | 563.5 | 225.4 | 263.4796 | 297.5 | 257.2 | 287 | 269 | 566.9 | 42.3 | 20.3 | 74.5 | 4.3 | 179.4 | 3.4 | 869.1 | 820.7 | 871.7 | 876.1 | 930.1 | 808.3 | 722.1 | 799.6 | 787.9 | 823.3 | 181.4 | 297.6 | 81.7 | 291.5 | 286.5 | 78.1 | 234 | 276.7 | 158.1
729 | 522 | 564.6 | 225.84 | 263.9939 | 297.3 | 257 | 287.2 | 268.4 | 567.7 | 42.5 | 20.3 | 74.6 | 4.8 | 155.4 | 2.4 | 868.5 | 821.4 | 871.9 | 876 | 930.6 | 808.5 | 723.8 | 804.5 | 788.7 | 824 | 181.8 | 297.7 | 81.9 | 291.4 | 286.5 | 78.3 | 234.4 | 277.2 | 158.5
730 | 523 | 564.9 | 225.96 | 264.1342 | 297.5 | 256.3 | 286.3 | 267.9 | 565.8 | 42.6 | 20.3 | 74.8 | 5.2 | 163 | 2.2 | 867.6 | 820.3 | 870 | 875.7 | 930.1 | 808.9 | 719.2 | 802.7 | 788.6 | 822.5 | 182.2 | 297.7 | 82.1 | 291.6 | 286.7 | 78.5 | 234.8 | 277.8 | 158.8
731 | 524 | 563.8 | 225.52 | 263.6199 | 298.1 | 256.1 | 286.2 | 268 | 562.9 | 42.7 | 20.3 | 75 | 5.8 | 190.7 | 3.7 | 867.5 | 819.3 | 868.8 | 875.6 | 928.5 | 809.7 | 714.5 | 794.3 | 788.9 | 818.2 | 182.5 | 297.5 | 82.2 | 292.5 | 286.8 | 78.7 | 235.1 | 278.3 | 159.1
732 | 525 | 563 | 225.2 | 263.2458 | 299 | 256.6 | 286.8 | 268.6 | 567.1 | 42.7 | 20.3 | 75.1 | 5.4 | 199 | 5.2 | 867.5 | 817.2 | 870.2 | 875.8 | 921.9 | 810.6 | 708.9 | 793.8 | 789.7 | 814.5 | 182.9 | 297.8 | 82.4 | 293.1 | 286.6 | 78.9 | 235.3 | 278.8 | 159.4
733 | 526 | 563.1 | 225.24 | 263.2926 | 300.1 | 256.3 | 288.2 | 268.9 | 566.4 | 42.8 | 20.3 | 75.2 | 5.2 | 245.8 | 5.5 | 867.8 | 815.2 | 870 | 876 | 914.6 | 811.2 | 705.2 | 797.9 | 790.3 | 810.5 | 183.3 | 298.1 | 82.6 | 293.4 | 286.5 | 79.1 | 235.6 | 279.2 | 159.7
734 | 527 | 564.1 | 225.64 | 263.7602 | 300.7 | 255.7 | 289.1 | 269.6 | 578 | 42.8 | 20.3 | 75.3 | 6 | 256.1 | 5.8 | 868.4 | 814.9 | 873 | 876.9 | 908.5 | 811.7 | 704.3 | 803.4 | 790.9 | 807.9 | 183.6 | 298.7 | 82.8 | 294 | 286.9 | 79.3 | 235.8 | 279.7 | 160
735 | 528 | 563.8 | 225.52 | 263.6199 | 300.1 | 255.4 | 289.7 | 270.2 | 603.6 | 42.9 | 20.3 | 75.5 | 5.2 | 252.4 | 5.3 | 868.9 | 814.3 | 874.8 | 877.7 | 904.2 | 811.7 | 703.6 | 802.6 | 790.9 | 805.4 | 184 | 299.7 | 83 | 294.3 | 287 | 79.4 | 236.1 | 280.2 | 160.3
736 | 529 | 563.9 | 225.56 | 263.6666 | 300.2 | 255.9 | 291.8 | 271.1 | 602.2 | 43 | 20.3 | 75.6 | 5 | 248.5 | 4.8 | 869.5 | 813.8 | 876.6 | 878.3 | 906.2 | 811.8 | 703.4 | 802.4 | 790.8 | 804.3 | 184.4 | 300.7 | 83.2 | 294.7 | 287.7 | 79.6 | 236.4 | 280.7 | 160.7
737 | 530 | 564.6 | 225.84 | 263.9939 | 300.4 | 257 | 292.2 | 272.4 | 613.1 | 43 | 20.3 | 75.7 | 5.3 | 258.2 | 5.3 | 869.5 | 813.5 | 875.9 | 878.3 | 906.4 | 811.7 | 705.3 | 804.7 | 790.5 | 803.2 | 184.9 | 301.1 | 83.3 | 295.3 | 288.6 | 79.8 | 236.8 | 281.2 | 161
738 | 531 | 564.3 | 225.72 | 263.8537 | 300.6 | 257.1 | 291.6 | 273.1 | 618.7 | 43.1 | 20.3 | 75.8 | 5.4 | 269.3 | 6.1 | 869.5 | 812.3 | 874.5 | 878.3 | 907.6 | 811.8 | 703.3 | 806.5 | 789.9 | 801.2 | 185.3 | 301.4 | 83.5 | 295.3 | 289.1 | 80 | 237.2 | 281.7 | 161.4
739 | 532 | 562.8 | 225.12 | 263.1523 | 301.2 | 257.2 | 291.1 | 273.8 | 637.8 | 43.2 | 20.3 | 76 | 4.8 | 239.5 | 6.6 | 869.5 | 811.7 | 872.6 | 878.3 | 906.3 | 812.2 | 705.9 | 810.1 | 789.7 | 801 | 185.8 | 301.7 | 83.7 | 295.1 | 289.6 | 80.2 | 237.5 | 282.2 | 161.7
740 | 533 | 562.1 | 224.84 | 262.825 | 302.4 | 257.7 | 291.6 | 274.9 | 658.8 | 43.3 | 20.3 | 76.2 | 5 | 221.8 | 6.4 | 869.7 | 810.7 | 871.8 | 878.4 | 899.6 | 812.6 | 707.7 | 813.1 | 789.5 | 799.6 | 186.2 | 302.4 | 83.9 | 295.2 | 289.8 | 80.4 | 237.9 | 282.8 | 162
741 | 534 | 562.7 | 225.08 | 263.1056 | 303.3 | 258.7 | 294 | 275.5 | 669.2 | 43.4 | 20.3 | 76.3 | 6.2 | 250.3 | 6 | 870 | 808.4 | 870.2 | 878.6 | 891.3 | 813.3 | 707.7 | 812 | 789.4 | 799 | 186.7 | 303.3 | 84.1 | 295.1 | 290.2 | 80.6 | 238.1 | 283.3 | 162.4
742 | 535 | 563.3 | 225.32 | 263.3861 | 304.2 | 259.9 | 294.4 | 276.4 | 662.8 | 43.5 | 20.3 | 76.4 | 5.3 | 256 | 6.7 | 870.8 | 807.7 | 869.2 | 879.1 | 892 | 814.1 | 710.5 | 813.8 | 789.7 | 797.8 | 187.2 | 303.7 | 84.3 | 295.1 | 290.5 | 80.8 | 238.5 | 283.8 | 162.7
743 | 536 | 563.1 | 225.24 | 263.2926 | 304.8 | 260.3 | 293.7 | 277.7 | 670.9 | 43.5 | 20.3 | 76.4 | 5.1 | 224.1 | 7.5 | 871.2 | 807.3 | 868.7 | 879.3 | 893 | 814.2 | 713 | 814.8 | 790 | 798 | 187.7 | 304.1 | 84.4 | 295.1 | 290.7 | 81 | 238.7 | 284.3 | 163.1
744 | 537 | 563.5 | 225.4 | 263.4796 | 305 | 260.8 | 293.8 | 278.7 | 671.5 | 43.5 | 20.2 | 76.5 | 4.8 | 217.4 | 7.5 | 871 | 807.5 | 870.7 | 879.1 | 899.7 | 814.1 | 714.5 | 813.6 | 789.9 | 798.3 | 188.2 | 304.5 | 84.6 | 295.5 | 291 | 81.2 | 239 | 284.8 | 163.4
745 | 538 | 563.7 | 225.48 | 263.5731 | 305.5 | 261.5 | 295.2 | 279.2 | 665.4 | 43.5 | 20.2 | 76.5 | 4.5 | 251 | 6.7 | 870.9 | 808.2 | 872.8 | 878.8 | 904.6 | 814.5 | 715.3 | 814.7 | 789.6 | 798.1 | 188.7 | 304.8 | 84.8 | 296.2 | 291.1 | 81.4 | 239.4 | 285.3 | 163.8
746 | 539 | 564.1 | 225.64 | 263.7602 | 305.9 | 262.3 | 296.3 | 279 | 673.3 | 43.5 | 20.2 | 76.6 | 4.8 | 265.6 | 6.6 | 870.5 | 807.1 | 875.2 | 878.4 | 903.2 | 814.6 | 716.4 | 812.4 | 789.5 | 795 | 189.2 | 305.6 | 85 | 297.1 | 291.3 | 81.6 | 239.7 | 285.8 | 164.1
747 | 540 | 564.3 | 225.72 | 263.8537 | 306.1 | 263 | 296.3 | 278.8 | 671.5 | 43.6 | 20.2 | 76.6 | 4.5 | 244.5 | 6.3 | 870.1 | 806.2 | 873.7 | 878 | 897.9 | 814.7 | 717.9 | 813.1 | 789.4 | 792.8 | 189.7 | 306.5 | 85.2 | 298.3 | 291.8 | 81.8 | 240.1 | 286.4 | 164.4
748 | 541 | 564.3 | 225.72 | 263.8537 | 306.1 | 263.7 | 296.2 | 278.5 | 673.3 | 43.7 | 20.2 | 76.6 | 4.6 | 251.8 | 7.4 | 869.8 | 805.8 | 874.5 | 877.4 | 893.4 | 815 | 717.6 | 814.4 | 789.5 | 791.9 | 190.3 | 307.1 | 85.4 | 298.5 | 292.4 | 82 | 240.5 | 286.9 | 164.8
749 | 542 | 564.3 | 225.72 | 263.8537 | 306 | 264.7 | 296.4 | 278.4 | 669.4 | 43.7 | 20.2 | 76.7 | 4.8 | 256.7 | 8.7 | 869.7 | 805.7 | 876.2 | 877.1 | 893.2 | 815.1 | 718.5 | 815.3 | 789.6 | 791.7 | 190.8 | 307.4 | 85.5 | 299.3 | 293.1 | 82.2 | 240.9 | 287.5 | 165.1
750 | 543 | 564.2 | 225.68 | 263.8069 | 305.9 | 265.8 | 297.1 | 279.1 | 665 | 43.8 | 20.2 | 76.8 | 4.8 | 272.1 | 8.6 | 869.6 | 807.7 | 876.4 | 877 | 897.5 | 814.9 | 717.6 | 816.3 | 789.2 | 792.2 | 191.3 | 308.1 | 85.7 | 299.3 | 293.5 | 82.4 | 241.2 | 288 | 165.5
751 | 544 | 564.6 | 225.84 | 263.9939 | 305.3 | 266.6 | 296.6 | 279.6 | 656.2 | 43.8 | 20.2 | 76.9 | 4.5 | 247.1 | 7.4 | 869.4 | 809.2 | 877.6 | 876.9 | 899.9 | 814.8 | 717.3 | 814.4 | 788.7 | 792.1 | 191.8 | 308.4 | 85.9 | 299.9 | 293.8 | 82.6 | 241.4 | 288.5 | 165.8
752 | 545 | 563 | 225.2 | 263.2458 | 305.5 | 266.4 | 296 | 279.4 | 663.3 | 43.9 | 20.2 | 77 | 4.4 | 242.2 | 6.8 | 868.8 | 809.6 | 875.8 | 876.5 | 903 | 814.6 | 719.1 | 816.4 | 788.5 | 791.3 | 192.4 | 308.4 | 86.1 | 300.3 | 294.2 | 82.8 | 241.8 | 289 | 166.1
753 | 546 | 564.4 | 225.76 | 263.9004 | 306.5 | 266.6 | 296.7 | 279.2 | 663.8 | 44 | 20.2 | 77 | 4.8 | 252.7 | 6.6 | 868.3 | 808.5 | 876.2 | 876 | 901.4 | 814.6 | 718.7 | 813.9 | 788.1 | 791.3 | 192.9 | 308.5 | 86.3 | 300.1 | 294.5 | 83 | 242.1 | 289.5 | 166.5
754 | 547 | 563.9 | 225.56 | 263.6666 | 308.2 | 266.9 | 297 | 278.8 | 645.2 | 44.1 | 20.2 | 77.1 | 5.4 | 227.5 | 5.3 | 868.1 | 807.8 | 873.2 | 875.4 | 897 | 814.8 | 713.6 | 808.3 | 787.9 | 789.4 | 193.5 | 308.7 | 86.4 | 299.7 | 294.5 | 83.2 | 242.4 | 290 | 166.8
755 | 548 | 563.9 | 225.56 | 263.6666 | 309.8 | 267.2 | 297.6 | 278.7 | 637.3 | 44.2 | 20.2 | 77.3 | 6 | 212.7 | 4.9 | 868.5 | 804.5 | 869.1 | 875.3 | 886.1 | 815.2 | 708.3 | 803 | 788.2 | 786.3 | 194.1 | 309.2 | 86.6 | 300 | 294.5 | 83.4 | 242.5 | 290.4 | 167.1
756 | 549 | 563.8 | 225.52 | 263.6199 | 311.2 | 267.3 | 298.3 | 279.2 | 643.5 | 44.3 | 20.2 | 77.4 | 5.5 | 229.7 | 4.3 | 868.7 | 802.1 | 869.5 | 875.1 | 877 | 816 | 709.3 | 804.9 | 788.7 | 785.2 | 194.6 | 309.6 | 86.8 | 300.6 | 294.1 | 83.6 | 242.8 | 290.9 | 167.4
757 | 550 | 564.3 | 225.72 | 263.8537 | 312.2 | 268.4 | 299 | 279.8 | 643 | 44.4 | 20.2 | 77.5 | 5.2 | 243.9 | 3.9 | 868.7 | 802.2 | 871.6 | 875.1 | 882.1 | 816.2 | 708.4 | 804.7 | 789.2 | 783.1 | 195.2 | 310.5 | 87 | 300.8 | 294 | 83.8 | 243 | 291.4 | 167.7
758 | 551 | 565.7 | 226.28 | 264.5083 | 310.8 | 269.6 | 299.9 | 280.7 | 644.1 | 44.4 | 20.2 | 77.5 | 5.6 | 225.2 | 4.5 | 868.9 | 801.8 | 872.1 | 875.1 | 881.7 | 816.2 | 708.3 | 801.2 | 789.5 | 781.5 | 195.7 | 311.6 | 87.2 | 301 | 294.3 | 84 | 243.2 | 291.9 | 168
759 | 552 | 566.6 | 226.64 | 264.9291 | 309.8 | 270.5 | 300.5 | 281.1 | 648.4 | 44.3 | 20.2 | 77.6 | 4.9 | 172 | 3.9 | 868.7 | 800.9 | 870.7 | 874.9 | 877.7 | 816.1 | 707.9 | 801.9 | 789.8 | 779.8 | 196.3 | 311.9 | 87.4 | 301.3 | 294.4 | 84.2 | 243.6 | 292.3 | 168.4
760 | 553 | 567.4 | 226.96 | 265.3032 | 307.7 | 270.8 | 301.1 | 281.2 | 662.6 | 44.3 | 20.2 | 77.6 | 4.2 | 212.2 | 3.1 | 869 | 800.2 | 871.4 | 875.2 | 879.6 | 815.6 | 707.1 | 803.7 | 789.6 | 778.3 | 196.8 | 311.9 | 87.5 | 302.1 | 295.1 | 84.4 | 244 | 292.8 | 168.8
761 | 554 | 565.9 | 226.36 | 264.6018 | 305.9 | 271.7 | 300.7 | 281.6 | 673.9 | 44.2 | 20.2 | 77.7 | 4.2 | 235.3 | 5 | 869 | 799.8 | 871.7 | 875.2 | 880.5 | 815.1 | 708.6 | 805 | 789.3 | 778 | 197.4 | 311.5 | 87.7 | 302.9 | 295.7 | 84.6 | 244.3 | 293.3 | 169.2
762 | 555 | 566.1 | 226.44 | 264.6953 | 304.9 | 272.9 | 301.4 | 281.9 | 670.5 | 44.3 | 20.2 | 77.7 | 4.2 | 209.6 | 5.8 | 869.5 | 800.2 | 869.2 | 875.5 | 877.6 | 814.9 | 709 | 805.4 | 788.6 | 778 | 197.9 | 311.5 | 87.9 | 304 | 296.1 | 84.8 | 244.7 | 293.8 | 169.5
763 | 556 | 566.7 | 226.68 | 264.9759 | 304.6 | 273.7 | 302.9 | 282.4 | 660.7 | 44.4 | 20.2 | 77.7 | 4.3 | 217.7 | 6.7 | 870.2 | 799.6 | 872 | 876.2 | 874.3 | 815.3 | 708.5 | 805.2 | 788.2 | 776.5 | 198.5 | 312.1 | 88.1 | 304.9 | 296.3 | 85 | 244.9 | 294.3 | 169.9
764 | 557 | 564.6 | 225.84 | 263.9939 | 304.7 | 274.4 | 303.8 | 283.3 | 655.3 | 44.5 | 20.2 | 77.7 | 4.9 | 237.1 | 7.9 | 870.7 | 799.6 | 872.2 | 876.8 | 874.4 | 815.3 | 707.2 | 802.8 | 788 | 774.7 | 199.1 | 312.7 | 88.3 | 305.9 | 296.4 | 85.2 | 245.2 | 294.8 | 170.3
765 | 558 | 564.2 | 225.68 | 263.8069 | 305 | 275.5 | 305 | 283.7 | 662.5 | 44.6 | 20.2 | 77.8 | 5.2 | 237 | 6.3 | 871.3 | 799 | 873.4 | 877.5 | 868.8 | 815 | 708.5 | 805.1 | 788.1 | 772 | 199.6 | 313.2 | 88.4 | 306.7 | 296.5 | 85.4 | 245.5 | 295.3 | 170.6
766 | 559 | 564.9 | 225.96 | 264.1342 | 304.4 | 276.4 | 305.8 | 284.5 | 665.9 | 44.8 | 20.2 | 77.9 | 5.1 | 225.4 | 5 | 872 | 798.3 | 871.4 | 877.9 | 863.5 | 814.9 | 707.3 | 806 | 787.8 | 770.6 | 200.2 | 313.4 | 88.6 | 307.8 | 296.7 | 85.6 | 245.8 | 295.9 | 171
767 | 560 | 564.9 | 225.96 | 264.1342 | 304.1 | 276.9 | 305.7 | 285.1 | 665 | 44.8 | 20.2 | 77.9 | 5.4 | 207.9 | 5.6 | 872.9 | 796.9 | 868.3 | 878.2 | 853.8 | 815.3 | 704.8 | 805.5 | 788 | 769.5 | 200.7 | 314 | 88.8 | 308.7 | 296.9 | 85.8 | 246.1 | 296.3 | 171.3
768 | 561 | 564.9 | 225.96 | 264.1342 | 303.7 | 277.3 | 306.3 | 285.4 | 670.3 | 44.8 | 20.2 | 78 | 5.6 | 202.8 | 7.8 | 873.3 | 795.9 | 866.6 | 878.5 | 847.7 | 815.4 | 703.2 | 806.2 | 788.6 | 766.9 | 201.2 | 314.7 | 89 | 309.7 | 297.2 | 86 | 246.4 | 296.9 | 171.7
769 | 562 | 565.2 | 226.08 | 264.2745 | 303.2 | 277.8 | 307.6 | 286.3 | 678.6 | 44.8 | 20.2 | 78.1 | 4.9 | 213.6 | 9.5 | 873.6 | 796.2 | 866.3 | 878.6 | 848 | 815 | 704.6 | 805.3 | 788.9 | 765.5 | 201.8 | 315.1 | 89.2 | 310.4 | 297.5 | 86.2 | 246.7 | 297.5 | 172
770 | 563 | 565.3 | 226.12 | 264.3213 | 302.7 | 278.7 | 308.2 | 287.5 | 670.8 | 44.8 | 20.2 | 78.2 | 5.1 | 225.3 | 8.4 | 873 | 798.2 | 867.2 | 878.5 | 854.5 | 814.3 | 707.1 | 804.2 | 788.6 | 765.6 | 202.3 | 315.7 | 89.3 | 311.8 | 297.6 | 86.4 | 247.1 | 298.2 | 172.2
771 | 564 | 564.8 | 225.92 | 264.0875 | 302.8 | 280.2 | 308.5 | 288 | 673.4 | 44.7 | 20.2 | 78.2 | 5 | 197.5 | 7.7 | 872.7 | 800 | 868.4 | 878.2 | 860.1 | 813.8 | 709.4 | 806.3 | 788.2 | 766.1 | 202.9 | 315.9 | 89.5 | 313.6 | 298.2 | 86.6 | 247.5 | 298.8 | 172.7
772 | 565 | 566 | 226.4 | 264.6486 | 303.4 | 281.1 | 308.6 | 288.4 | 682.5 | 44.8 | 20.2 | 78.1 | 5.1 | 213.2 | 8.2 | 872.5 | 801 | 866.3 | 878 | 858.9 | 813.2 | 711.4 | 810.1 | 787.5 | 765.7 | 203.4 | 316.7 | 89.7 | 314.6 | 298.8 | 86.8 | 247.9 | 299.4 | 173.1
773 | 566 | 564.8 | 225.92 | 264.0875 | 303.5 | 281.3 | 309.2 | 288.8 | 689.6 | 44.8 | 20.2 | 78.1 | 5.8 | 225.3 | 7.7 | 872.4 | 801.2 | 864.9 | 877.8 | 855.3 | 812.9 | 712.3 | 811.8 | 786.8 | 764 | 203.9 | 317.2 | 89.9 | 315.3 | 299.2 | 87 | 248.2 | 300 | 173.5
774 | 567 | 565.8 | 226.32 | 264.555 | 304.1 | 282.4 | 310.5 | 289.7 | 696.8 | 45 | 20.2 | 78.1 | 5.6 | 247.2 | 6.5 | 872.4 | 801.8 | 866.6 | 877.8 | 854.2 | 812.8 | 715.2 | 813 | 786.6 | 763.1 | 204.4 | 317.9 | 90.1 | 316.1 | 299.3 | 87.2 | 248.5 | 300.7 | 173.8
775 | 568 | 564.2 | 225.68 | 263.8069 | 305.2 | 283.8 | 311 | 290.5 | 690.9 | 45 | 20.2 | 78.1 | 5.5 | 240 | 6.2 | 873.1 | 802.5 | 869.1 | 878.3 | 850.7 | 812.9 | 712.1 | 813.9 | 786.6 | 761.3 | 204.8 | 318.4 | 90.3 | 316.7 | 299.3 | 87.4 | 248.8 | 301.3 | 174.2
776 | 569 | 563.9 | 225.56 | 263.6666 | 305.6 | 285 | 312 | 291.1 | 669.1 | 45.1 | 20.2 | 78.1 | 5.3 | 261.9 | 6.2 | 873.4 | 804.1 | 870.8 | 878.6 | 856.9 | 812.4 | 711.1 | 811.3 | 786.8 | 759.8 | 205.3 | 318.6 | 90.4 | 317.1 | 299.3 | 87.6 | 249.2 | 301.9 | 174.5
777 | 570 | 563.9 | 225.56 | 263.6666 | 305.1 | 285.5 | 311.2 | 291.5 | 655.1 | 45.2 | 20.2 | 78.1 | 5.2 | 248.2 | 6.4 | 873.5 | 806.2 | 869.7 | 878.8 | 861.8 | 811.7 | 708.7 | 808.1 | 786.4 | 759.7 | 205.7 | 318.9 | 90.6 | 317.6 | 299.5 | 87.9 | 249.5 | 302.4 | 174.9
778 | 571 | 563.8 | 225.52 | 263.6199 | 304.3 | 285.7 | 309.1 | 291.7 | 649.4 | 45.2 | 20.2 | 78.1 | 5.3 | 233 | 6.4 | 873.8 | 807.1 | 870.5 | 879 | 864.5 | 811.4 | 708.9 | 807.5 | 786.1 | 758.9 | 206.1 | 319.1 | 90.8 | 317.8 | 300 | 88.1 | 249.9 | 303 | 175.2
779 | 572 | 563.6 | 225.44 | 263.5264 | 303.6 | 285.7 | 309.5 | 291.9 | 636.6 | 45.3 | 20.2 | 78.2 | 4.6 | 269.8 | 6.7 | 874.1 | 807 | 869.7 | 879.4 | 862.3 | 811.3 | 707 | 802.3 | 785.9 | 758.6 | 206.4 | 319 | 91 | 317.7 | 299.7 | 88.3 | 250.2 | 303.5 | 175.6
780 | 573 | 564 | 225.6 | 263.7134 | 304 | 285.8 | 310 | 291.4 | 630.7 | 45.3 | 20.2 | 78.2 | 5 | 248.8 | 6.6 | 874.7 | 808.4 | 868.1 | 880 | 860.7 | 811.3 | 706.5 | 802.9 | 786.4 | 759.7 | 206.8 | 319.2 | 91.1 | 317.6 | 299.4 | 88.5 | 250.5 | 303.9 | 175.9
781 | 574 | 564.5 | 225.8 | 263.9472 | 303.9 | 286.1 | 310.1 | 291.2 | 629 | 45.3 | 20.2 | 78.2 | 5.3 | 242 | 7.5 | 876 | 808.8 | 864.3 | 880.6 | 857.6 | 811.4 | 703.9 | 803.6 | 787 | 758.5 | 207.2 | 319.5 | 91.3 | 317.6 | 299.1 | 88.7 | 250.7 | 304.3 | 176.2
782 | 575 | 563.2 | 225.28 | 263.3393 | 303 | 286.8 | 310.2 | 291 | 640.9 | 45.2 | 20.2 | 78.3 | 5.9 | 235.8 | 7.5 | 876.8 | 807.6 | 862.3 | 880.8 | 853.4 | 811.3 | 702.5 | 804.7 | 787.7 | 757.2 | 207.5 | 320.3 | 91.5 | 317.3 | 298.9 | 88.9 | 250.9 | 304.8 | 176.5
783 | 576 | 564.1 | 225.64 | 263.7602 | 303.4 | 286.1 | 310.4 | 291.1 | 645 | 45.2 | 20.2 | 78.4 | 6 | 234.9 | 7.1 | 877.4 | 807.5 | 863.8 | 881.5 | 848.5 | 811.5 | 701.4 | 805.5 | 788.2 | 755.4 | 207.8 | 320.5 | 91.7 | 317 | 298.6 | 89.1 | 251.3 | 305.3 | 176.8
784 | 577 | 564.3 | 225.72 | 263.8537 | 303.1 | 286.1 | 311.1 | 291.2 | 649.4 | 45.2 | 20.2 | 78.6 | 5.3 | 256.4 | 7.2 | 877.9 | 806.1 | 866.3 | 882.5 | 847.2 | 811.7 | 705.2 | 807.5 | 788.8 | 754.8 | 208.1 | 320.9 | 91.9 | 317.2 | 298.7 | 89.3 | 251.5 | 305.8 | 177.1
785 | 578 | 564.3 | 225.72 | 263.8537 | 302.6 | 286 | 312.9 | 291.4 | 659.8 | 45.2 | 20.2 | 78.7 | 5.3 | 249.9 | 8.6 | 877.7 | 808.1 | 868.4 | 882.8 | 853.5 | 811.4 | 708.6 | 809.2 | 789.1 | 755.6 | 208.4 | 321.3 | 92 | 317.4 | 298.7 | 89.5 | 251.8 | 306.4 | 177.5
786 | 579 | 564.8 | 225.92 | 264.0875 | 302 | 286.1 | 313.7 | 291.6 | 649 | 45.2 | 20.2 | 78.7 | 5.6 | 250.9 | 8.6 | 877.8 | 809 | 872.4 | 883.1 | 859.6 | 810.8 | 709.3 | 806.6 | 788.6 | 755.8 | 208.7 | 320.8 | 92.2 | 317.5 | 298.7 | 89.7 | 252.1 | 306.9 | 177.8
787 | 580 | 564.4 | 225.76 | 263.9004 | 301 | 286.1 | 313.5 | 291.3 | 637.5 | 45.2 | 20.2 | 78.8 | 5.6 | 243.8 | 7.8 | 878.2 | 810.7 | 874.8 | 883.6 | 865.4 | 810.5 | 710.5 | 804.8 | 788.3 | 757.6 | 209 | 320.3 | 92.4 | 317.5 | 298.8 | 89.9 | 252.4 | 307.4 | 178.1
788 | 581 | 564.6 | 225.84 | 263.9939 | 301.3 | 285.7 | 312.1 | 291 | 638.5 | 45.2 | 20.2 | 79 | 6 | 236.6 | 7.6 | 878.1 | 811 | 873.2 | 883.7 | 869.9 | 810.1 | 711.7 | 805.2 | 788.1 | 758.5 | 209.3 | 319.7 | 92.6 | 317.8 | 298.8 | 90.1 | 252.6 | 307.8 | 178.5
789 | 582 | 564.9 | 225.96 | 264.1342 | 300.9 | 285.3 | 309.7 | 291.1 | 634.5 | 45.2 | 20.2 | 79.1 | 6 | 230.3 | 6.8 | 878.1 | 811.1 | 868.9 | 883.8 | 873.5 | 809.5 | 713.1 | 802.1 | 787.4 | 761.5 | 209.6 | 319.7 | 92.8 | 317.8 | 299 | 90.3 | 253 | 308.3 | 178.8
790 | 583 | 565.6 | 226.24 | 264.4615 | 301.7 | 285.2 | 307.9 | 291.1 | 621.6 | 45.1 | 20.2 | 79.2 | 6.1 | 233.3 | 6.3 | 877.9 | 812.7 | 868.3 | 883.8 | 876.7 | 809 | 716.8 | 800.9 | 787 | 765.3 | 209.9 | 319.1 | 92.9 | 317.7 | 299.1 | 90.5 | 253.4 | 308.7 | 179.1
791 | 584 | 562.8 | 225.12 | 263.1523 | 302.9 | 284.5 | 306.8 | 290.6 | 630.2 | 45.1 | 20.2 | 79.3 | 5.4 | 244.1 | 6.2 | 877.9 | 813.9 | 868.6 | 884 | 887.2 | 808.8 | 718.8 | 802.7 | 786.8 | 767.1 | 210.2 | 318.4 | 93.1 | 317.2 | 299.1 | 90.7 | 253.6 | 309.2 | 179.4
792 | 585 | 563.3 | 225.32 | 263.3861 | 303.3 | 283.7 | 305.1 | 289.8 | 640.7 | 45.1 | 20.1 | 79.2 | 5.1 | 262.3 | 6.2 | 878.6 | 812.9 | 867.1 | 884.4 | 893.2 | 808.6 | 715.3 | 801.6 | 786.9 | 765.5 | 210.4 | 318.1 | 93.3 | 316.9 | 299.3 | 90.9 | 253.7 | 309.6 | 179.7
793 | 586 | 562.5 | 225 | 263.012 | 304.3 | 283.5 | 303.6 | 289.2 | 649.3 | 45.2 | 20.2 | 79.3 | 5.2 | 250.6 | 8.7 | 879.3 | 812.5 | 869.5 | 884.8 | 890.5 | 808.3 | 717.5 | 803.5 | 787.6 | 764.6 | 210.6 | 318.1 | 93.5 | 316.8 | 299.4 | 91.1 | 254 | 310.1 | 180
794 | 587 | 562.8 | 225.12 | 263.1523 | 304.3 | 283.3 | 303.1 | 289.6 | 653.6 | 45.2 | 20.2 | 79.3 | 5.3 | 248 | 10.9 | 879.6 | 813.4 | 867.4 | 884.8 | 889.8 | 807.7 | 720 | 803.3 | 787.6 | 766.9 | 210.8 | 318.5 | 93.7 | 316.2 | 299.6 | 91.4 | 254.3 | 310.6 | 180.4
795 | 588 | 563.3 | 225.32 | 263.3861 | 304.3 | 282.5 | 303.7 | 289.5 | 627.3 | 45.3 | 20.1 | 79.4 | 5.4 | 258.6 | 11.9 | 879.9 | 815.4 | 868.7 | 885.3 | 898.1 | 807.4 | 721.1 | 798.1 | 786.9 | 769.3 | 211 | 318.4 | 93.9 | 316.1 | 299.4 | 91.6 | 254.6 | 311.1 | 180.6
796 | 589 | 563.1 | 225.24 | 263.2926 | 304.7 | 281.8 | 304.2 | 288.8 | 616.2 | 45.5 | 20.1 | 79.5 | 5.7 | 263.9 | 11.2 | 880.1 | 817.1 | 870.5 | 885.6 | 904.4 | 807 | 721.4 | 799.9 | 786.7 | 771.2 | 211.2 | 318.1 | 94 | 317.3 | 299.6 | 91.8 | 254.8 | 311.6 | 181
797 | 590 | 562.6 | 225.04 | 263.0588 | 305 | 282.1 | 303.8 | 288.6 | 627.4 | 45.6 | 20.1 | 79.6 | 5.6 | 265.1 | 9.4 | 880.5 | 818.2 | 871.6 | 885.9 | 910.7 | 806.6 | 723.4 | 803.2 | 786.5 | 771.9 | 211.3 | 317.8 | 94.2 | 317.9 | 299.7 | 92 | 255.1 | 312 | 181.3
798 | 591 | 563.5 | 225.4 | 263.4796 | 305.8 | 282.4 | 303.6 | 288.6 | 649.4 | 45.7 | 20.1 | 79.6 | 5.8 | 271.5 | 8 | 880.7 | 818.1 | 871.5 | 886 | 909.8 | 806 | 726.3 | 805.2 | 786.2 | 771.7 | 211.5 | 317.8 | 94.4 | 317.8 | 299.7 | 92.2 | 255.3 | 312.4 | 181.7
799 | 592 | 562.8 | 225.12 | 263.1523 | 305 | 282.6 | 303.7 | 287.9 | 644.1 | 45.8 | 20.1 | 79.7 | 6.1 | 259.9 | 7.3 | 880.8 | 818.5 | 873 | 886.2 | 906.9 | 805.5 | 725.7 | 807.1 | 785.7 | 772.2 | 211.6 | 317.7 | 94.6 | 317.5 | 299.5 | 92.4 | 255.4 | 312.9 | 182
800 | 593 | 563.1 | 225.24 | 263.2926 | 302.8 | 282.9 | 302.7 | 287.2 | 652.6 | 45.9 | 20.1 | 79.8 | 6.1 | 264 | 7 | 881.5 | 819.2 | 876.1 | 886.6 | 904.1 | 804.9 | 727 | 807.3 | 785.6 | 772.8 | 211.7 | 317.5 | 94.8 | 317.1 | 299.1 | 92.6 | 255.5 | 313.3 | 182.3
801 | 594 | 563 | 225.2 | 263.2458 | 302.2 | 282.9 | 303.4 | 286.2 | 657.1 | 45.9 | 20.1 | 79.8 | 5.7 | 249.8 | 7.4 | 882.6 | 818.6 | 875.9 | 887 | 898.9 | 804.1 | 724.7 | 808.2 | 784.9 | 772.7 | 211.8 | 317 | 95 | 316.9 | 298.9 | 92.8 | 255.7 | 313.8 | 182.6
802 | 595 | 563.6 | 225.44 | 263.5264 | 301.8 | 282.9 | 303.6 | 285.6 | 662.2 | 46 | 20.1 | 79.9 | 6.4 | 256.2 | 8.1 | 883.6 | 815.9 | 874.2 | 887.2 | 885.9 | 804.3 | 723.8 | 809.5 | 784.8 | 770.3 | 211.9 | 317 | 95.2 | 317.2 | 298.6 | 93 | 255.8 | 314.3 | 182.9
803 | 596 | 564.3 | 225.72 | 263.8537 | 302.1 | 283 | 304.3 | 284.8 | 665.4 | 46 | 20.1 | 80 | 5.4 | 248.9 | 8.3 | 884.9 | 814.8 | 876.1 | 887.9 | 877.3 | 804.6 | 722.2 | 809 | 785.4 | 768.1 | 212 | 316.8 | 95.4 | 317.4 | 298.5 | 93.2 | 255.9 | 314.7 | 183.3
804 | 597 | 564.6 | 225.84 | 263.9939 | 301.8 | 283.7 | 304.3 | 285.4 | 652.8 | 46 | 20.1 | 80.1 | 5.2 | 246.1 | 9 | 885.2 | 815.8 | 876.4 | 888.3 | 881.3 | 804 | 726.4 | 808.3 | 785.8 | 770.4 | 212.1 | 317 | 95.6 | 317.4 | 298.5 | 93.4 | 256.2 | 315.3 | 183.6
805 | 598 | 564.8 | 225.92 | 264.0875 | 301.5 | 284.3 | 303.2 | 286.3 | 627.2 | 46 | 20.1 | 80.2 | 5.2 | 251.7 | 10 | 885 | 816.8 | 875 | 888.3 | 882.8 | 803.4 | 728.1 | 801.7 | 785.3 | 772.1 | 212.2 | 317.2 | 95.7 | 317.6 | 298.5 | 93.6 | 256.6 | 315.8 | 183.9
806 | 599 | 564.7 | 225.88 | 264.0407 | 300.8 | 284.7 | 303.4 | 286.9 | 605.7 | 46 | 20.1 | 80.2 | 5.3 | 257.6 | 10.1 | 885.1 | 818.5 | 877 | 888.6 | 888.1 | 802.8 | 729.8 | 800.7 | 785 | 773.6 | 212.3 | 317.3 | 95.9 | 317.4 | 298.7 | 93.8 | 256.8 | 316.4 | 184.2
807 | 600 | 565 | 226 | 264.181 | 299.3 | 284.9 | 304.1 | 286.8 | 610.1 | 46 | 20.1 | 80.2 | 5.3 | 234 | 9.5 | 885.5 | 819.3 | 878.4 | 888.8 | 888 | 802.2 | 730.8 | 803.1 | 784.8 | 774.9 | 212.5 | 316.7 | 96.1 | 316.7 | 298.9 | 94.1 | 257.1 | 316.9 | 184.5
808 | 601 | 565.8 | 226.32 | 264.555 | 298.2 | 284.8 | 303.7 | 286.5 | 629.5 | 46.1 | 20.1 | 80.3 | 6.5 | 255.7 | 8.8 | 885.6 | 819.2 | 878.5 | 888.6 | 889.3 | 801.7 | 734.3 | 803.3 | 784.9 | 775.7 | 212.6 | 316 | 96.3 | 316.2 | 298.8 | 94.3 | 257.3 | 317.4 | 184.8
809 | 602 | 564.6 | 225.84 | 263.9939 | 298.2 | 284.9 | 304.4 | 285.6 | 641.2 | 46.2 | 20.1 | 80.3 | 6.2 | 251.7 | 9.7 | 885.9 | 819.5 | 876.9 | 888.6 | 893.4 | 801.3 | 735.6 | 803.6 | 784.7 | 778 | 212.6 | 315.5 | 96.5 | 316.1 | 298.6 | 94.5 | 257.5 | 317.9 | 185.1
810 | 603 | 564.5 | 225.8 | 263.9472 | 297.6 | 285.1 | 304.5 | 285.4 | 633.9 | 46.3 | 20.1 | 80.4 | 5.2 | 248.7 | 9.8 | 886.5 | 819.5 | 877.5 | 888.8 | 899 | 801.1 | 733.8 | 803.9 | 784.4 | 778 | 212.7 | 315 | 96.7 | 316.2 | 298.3 | 94.7 | 257.7 | 318.3 | 185.4
811 | 604 | 565.5 | 226.2 | 264.4148 | 298.2 | 283.8 | 303.2 | 284.5 | 628 | 46.4 | 20.1 | 80.4 | 4.5 | 252 | 10.8 | 887.3 | 820.9 | 877.3 | 889.2 | 900.4 | 800.9 | 733.9 | 802.3 | 784.3 | 780.5 | 212.8 | 314.7 | 96.9 | 316.1 | 298 | 94.9 | 257.9 | 318.8 | 185.7
812 | 605 | 563.9 | 225.56 | 263.6666 | 298.3 | 282.4 | 302.7 | 283.6 | 624.2 | 46.5 | 20.1 | 80.4 | 4.8 | 258.2 | 11.5 | 887.8 | 822.6 | 875.7 | 889.4 | 898.3 | 800.5 | 735.2 | 802.3 | 784.6 | 783.2 | 212.9 | 314.4 | 97.1 | 316.4 | 297.9 | 95.1 | 258.2 | 319.2 | 186
813 | 606 | 564.3 | 225.72 | 263.8537 | 297.7 | 281.8 | 301.6 | 282.8 | 618.4 | 46.5 | 20.1 | 80.4 | 4.8 | 249.8 | 11.8 | 888.3 | 823.3 | 876.4 | 889.5 | 902.5 | 800.3 | 733.1 | 802.3 | 784.6 | 783.8 | 213 | 314.1 | 97.3 | 316.5 | 297.7 | 95.3 | 258.3 | 319.8 | 186.3
814 | 607 | 564.1 | 225.64 | 263.7602 | 296.5 | 282.9 | 300.5 | 282.8 | 625.9 | 46.4 | 20.1 | 80.4 | 4.4 | 249.1 | 11.2 | 888.9 | 823.6 | 875 | 889.7 | 896.8 | 800.2 | 732.9 | 803.5 | 785 | 785.2 | 213.2 | 314 | 97.5 | 317 | 297.3 | 95.5 | 258.4 | 320.2 | 186.7
815 | 608 | 563.4 | 225.36 | 263.4329 | 297.3 | 283.6 | 300.6 | 283.3 | 632.6 | 46.4 | 20.1 | 80.5 | 5.1 | 261.9 | 10.7 | 889.6 | 823.7 | 872.9 | 889.9 | 897.8 | 799.9 | 733 | 801.7 | 785 | 786.8 | 213.3 | 313.6 | 97.8 | 316.4 | 297.2 | 95.7 | 258.6 | 320.7 | 187
816 | 609 | 562.7 | 225.08 | 263.1056 | 298.4 | 283 | 300.8 | 283.4 | 626.8 | 46.3 | 20.1 | 80.6 | 5.4 | 265.1 | 12.1 | 890.6 | 822.7 | 870.4 | 890.3 | 897.2 | 799.9 | 732.2 | 801 | 785.3 | 788.6 | 213.5 | 313.1 | 98 | 316 | 297.1 | 95.9 | 258.7 | 321.1 | 187.2
817 | 610 | 565.5 | 226.2 | 264.4148 | 300.1 | 283.8 | 301.5 | 283.1 | 635.6 | 46.4 | 20.1 | 80.6 | 4.8 | 269 | 13.1 | 891.9 | 820.2 | 866.6 | 890.6 | 904.7 | 800.2 | 732.6 | 800.2 | 786.1 | 788.5 | 213.6 | 313.2 | 98.2 | 316.2 | 297.1 | 96.1 | 258.9 | 321.5 | 187.5
818 | 611 | 565.5 | 226.2 | 264.4148 | 302.1 | 284.2 | 302.4 | 283.7 | 642.6 | 46.5 | 20.1 | 80.6 | 5.2 | 270.2 | 12.9 | 892.7 | 818.2 | 865.1 | 890.9 | 906.4 | 800.6 | 732.7 | 798.8 | 787 | 789 | 213.7 | 313.7 | 98.4 | 315.8 | 296.8 | 96.3 | 259.1 | 321.9 | 187.8
819 | 612 | 564.6 | 225.84 | 263.9939 | 303.7 | 282.5 | 303.5 | 283.9 | 624.3 | 46.4 | 20.1 | 80.7 | 5.5 | 269.9 | 12.6 | 893.4 | 816.9 | 861.1 | 891.3 | 908.9 | 800.4 | 729.3 | 793 | 787.2 | 791.2 | 213.9 | 314.4 | 98.6 | 315.7 | 296.7 | 96.5 | 259.3 | 322.4 | 188.1
820 | 613 | 565.3 | 226.12 | 264.3213 | 304.2 | 281.6 | 304.5 | 283.6 | 602.6 | 46.3 | 20.1 | 80.7 | 5.5 | 281.4 | 12.7 | 893.9 | 815.9 | 857.5 | 891.6 | 907.9 | 800.3 | 726.7 | 792 | 787.5 | 790.2 | 214 | 315 | 98.8 | 315.4 | 296.7 | 96.7 | 259.4 | 322.8 | 188.4
821 | 614 | 564.8 | 225.92 | 264.0875 | 305.5 | 280.3 | 305.1 | 284.1 | 604 | 46.2 | 20.1 | 80.8 | 5.3 | 278 | 12 | 894.9 | 813.3 | 851.4 | 891.7 | 906.8 | 800.3 | 721.1 | 785.6 | 787.7 | 788.6 | 214.2 | 315.3 | 99 | 315.2 | 296.9 | 97 | 259.6 | 323.2 | 188.7
822 | 615 | 564.6 | 225.84 | 263.9939 | 306.3 | 279.4 | 305.4 | 284.6 | 595.7 | 46.2 | 20.1 | 80.9 | 5.7 | 277.5 | 12 | 895.5 | 810.3 | 847.3 | 891.9 | 900.6 | 800.5 | 715.1 | 777.5 | 788.3 | 787.6 | 214.4 | 315.5 | 99.3 | 314.9 | 297.5 | 97.2 | 259.9 | 323.5 | 189
823 | 616 | 564.2 | 225.68 | 263.8069 | 307.8 | 278.9 | 305.5 | 285.2 | 578.4 | 46.2 | 20.1 | 80.8 | 5.7 | 279.2 | 12.6 | 895.9 | 807.7 | 846.2 | 892.2 | 891.2 | 800.7 | 707 | 773.4 | 789.3 | 785.5 | 214.5 | 315.4 | 99.5 | 314.6 | 298 | 97.4 | 260.1 | 323.8 | 189.3
824 | 617 | 564.6 | 225.84 | 263.9939 | 309.4 | 278.6 | 305.6 | 285.6 | 571.8 | 46.2 | 20.1 | 80.8 | 5.7 | 283.4 | 12.8 | 896 | 806.1 | 850.7 | 892.4 | 885.9 | 800.5 | 703.4 | 777.3 | 790.7 | 784.2 | 214.7 | 315.6 | 99.7 | 316.3 | 298.6 | 97.6 | 260.3 | 324.1 | 189.7
825 | 618 | 564.7 | 225.88 | 264.0407 | 310.9 | 278.7 | 305 | 285.8 | 589.4 | 46.3 | 20.1 | 80.8 | 6.1 | 280.8 | 12.3 | 896.1 | 804.5 | 851.9 | 892.4 | 872.2 | 800.6 | 699.8 | 782.8 | 791.8 | 780.7 | 214.9 | 315.9 | 99.9 | 316.2 | 299.1 | 97.7 | 260.6 | 324.4 | 190
826 | 619 | 565 | 226 | 264.181 | 312.1 | 279.9 | 305.7 | 285.3 | 599.5 | 46.2 | 20.1 | 80.8 | 5.7 | 280.7 | 12 | 896 | 802.1 | 851.7 | 892.3 | 866.5 | 800.5 | 696.8 | 784.7 | 792.9 | 776.9 | 215.1 | 316.4 | 100.2 | 316 | 299.4 | 98 | 260.8 | 324.7 | 190.3
827 | 620 | 565.4 | 226.16 | 264.368 | 311.1 | 280.8 | 307.3 | 285.3 | 613.7 | 46.2 | 20.1 | 80.8 | 5.4 | 280.9 | 10.9 | 896.9 | 801.6 | 854.4 | 892.6 | 871 | 800.2 | 698.3 | 786.2 | 793.9 | 775.1 | 215.3 | 317 | 100.4 | 315.8 | 299.1 | 98.2 | 260.9 | 325.1 | 190.6
828 | 621 | 567 | 226.8 | 265.1161 | 310.4 | 281.4 | 308 | 285.5 | 604.4 | 46.4 | 20.1 | 80.8 | 5.3 | 274.1 | 8.8 | 896.9 | 802.7 | 858.1 | 892.7 | 878.5 | 799.9 | 700 | 787.3 | 794.4 | 774.2 | 215.5 | 318.2 | 100.6 | 316.1 | 299.1 | 98.4 | 261.1 | 325.5 | 190.9
829 | 622 | 566.1 | 226.44 | 264.6953 | 309.9 | 282.3 | 309 | 286.1 | 598.6 | 46.5 | 20.1 | 80.8 | 5 | 268 | 7.8 | 896.9 | 803 | 855.3 | 892.9 | 880.3 | 799.4 | 699.8 | 786 | 794.4 | 774 | 215.7 | 318.5 | 100.8 | 316 | 299.1 | 98.6 | 261.3 | 325.9 | 191.2
830 | 623 | 564.8 | 225.92 | 264.0875 | 309 | 283.1 | 309.7 | 286.5 | 600 | 46.6 | 20 | 80.8 | 5.6 | 273.6 | 8.3 | 897 | 803.5 | 856.9 | 892.9 | 884.8 | 799.1 | 698.4 | 787.8 | 794.4 | 773.6 | 215.9 | 319 | 101.1 | 316.3 | 299.4 | 98.8 | 261.5 | 326.2 | 191.5
831 | 624 | 564.3 | 225.72 | 263.8537 | 308.5 | 283.8 | 310.2 | 287.2 | 606 | 46.7 | 20.1 | 80.7 | 6.3 | 275.8 | 8.9 | 896.4 | 803.7 | 853.3 | 892.7 | 880.1 | 798.7 | 696.1 | 788 | 794.7 | 773.2 | 216.1 | 319 | 101.3 | 317.2 | 300.2 | 99 | 261.9 | 326.5 | 191.8
832 | 625 | 563.9 | 225.56 | 263.6666 | 308.4 | 284.3 | 310.6 | 288.2 | 597.2 | 46.8 | 20.1 | 80.8 | 5.8 | 268.7 | 8.5 | 897.1 | 804.3 | 853.9 | 892.7 | 883.6 | 798.4 | 694.8 | 785.3 | 794.7 | 772.6 | 216.3 | 318.6 | 101.5 | 317.8 | 300.8 | 99.2 | 262 | 326.8 | 192.1
833 | 626 | 564.4 | 225.76 | 263.9004 | 308.8 | 284.9 | 311.4 | 288.4 | 595.6 | 46.8 | 20.1 | 80.8 | 5.3 | 289.6 | 7.8 | 896.4 | 804 | 856.6 | 892.4 | 885.7 | 798.2 | 693.9 | 782.9 | 794.9 | 771.8 | 216.4 | 318.6 | 101.8 | 317.5 | 301.1 | 99.5 | 262.2 | 327.1 | 192.5
834 | 627 | 563.6 | 225.44 | 263.5264 | 309.2 | 284.7 | 312 | 288.9 | 599.8 | 46.8 | 20 | 80.9 | 5.4 | 275.6 | 7.9 | 896.1 | 804 | 862.3 | 892 | 888.1 | 797.8 | 694.1 | 787.1 | 795.4 | 769.7 | 216.6 | 318.5 | 102 | 317.7 | 301.1 | 99.7 | 262.5 | 327.4 | 192.7
835 | 628 | 563.9 | 225.56 | 263.6666 | 309.9 | 284.8 | 311.5 | 289.1 | 611.2 | 46.8 | 20 | 81 | 5.6 | 273.5 | 9.1 | 895 | 804.5 | 864.8 | 891.6 | 885 | 797.3 | 693.8 | 791.8 | 795.5 | 767.8 | 216.7 | 318.5 | 102.2 | 318 | 301.4 | 99.9 | 262.6 | 327.7 | 193
836 | 629 | 563.6 | 225.44 | 263.5264 | 309.9 | 284.7 | 311.1 | 289 | 629.5 | 46.8 | 20 | 81.2 | 5.4 | 271.9 | 9.2 | 895.2 | 804.2 | 862.4 | 891.4 | 877 | 796.7 | 693.8 | 794.3 | 795.4 | 766.6 | 216.9 | 318.6 | 102.5 | 318.5 | 301.8 | 100.1 | 263 | 327.9 | 193.3
837 | 630 | 563.3 | 225.32 | 263.3861 | 310.2 | 285 | 310.9 | 289.1 | 648 | 46.8 | 20 | 81.3 | 5 | 262.6 | 8.6 | 895.9 | 803.1 | 862.2 | 891.3 | 872.7 | 796.4 | 697.9 | 796.6 | 795.5 | 765.4 | 217.1 | 319.4 | 102.7 | 319 | 301.8 | 100.3 | 263.1 | 328.1 | 193.7
838 | 631 | 565.6 | 226.24 | 264.4615 | 311 | 285.8 | 309 | 289.4 | 661.3 | 46.9 | 20 | 81.4 | 5.8 | 271.8 | 8.5 | 895.9 | 803.7 | 862 | 891.3 | 873.9 | 795.8 | 703.4 | 797.5 | 795.2 | 765.5 | 217.3 | 319.6 | 102.9 | 319 | 302.4 | 100.5 | 263.3 | 328.4 | 194
839 | 632 | 565.2 | 226.08 | 264.2745 | 311.5 | 286.7 | 308.5 | 290.2 | 660.3 | 47 | 20 | 81.5 | 4.7 | 280.5 | 8 | 895.5 | 804.7 | 863.3 | 891.1 | 875.1 | 795.3 | 704.7 | 799.5 | 794.3 | 765.6 | 217.6 | 319.8 | 103.1 | 318.8 | 302.6 | 100.7 | 263.4 | 328.7 | 194.3
840 | 633 | 565.4 | 226.16 | 264.368 | 311.2 | 287.4 | 307.8 | 290.8 | 658.8 | 47 | 20 | 81.6 | 5.2 | 283.3 | 7.3 | 894.8 | 806 | 863.3 | 890.7 | 880.3 | 794.8 | 708.4 | 800.4 | 793.6 | 765.5 | 217.9 | 319.6 | 103.4 | 318.8 | 302.5 | 101 | 263.7 | 329.1 | 194.6
841 | 634 | 564.6 | 225.84 | 263.9939 | 311.3 | 287.8 | 306.8 | 291.3 | 657.6 | 47 | 20 | 81.7 | 5.2 | 277.1 | 7.8 | 894 | 808 | 863.9 | 890.3 | 888.8 | 794.2 | 712.3 | 801.9 | 792.7 | 768.3 | 218.2 | 319.6 | 103.6 | 319.1 | 302.4 | 101.2 | 263.9 | 329.5 | 194.9
842 | 635 | 564 | 225.6 | 263.7134 | 311.5 | 287.5 | 307.1 | 291.3 | 647.9 | 47 | 20 | 81.7 | 4.8 | 292.1 | 7.9 | 893.4 | 810.1 | 863.6 | 889.9 | 897.8 | 793.8 | 713.2 | 802.5 | 791.4 | 768.8 | 218.5 | 319.3 | 103.8 | 319.1 | 302.5 | 101.4 | 264.2 | 329.9 | 195.2
843 | 636 | 563.7 | 225.48 | 263.5731 | 311 | 287.5 | 306.9 | 290.7 | 655.7 | 46.9 | 20 | 81.7 | 5.1 | 257.5 | 7.6 | 892.9 | 811.4 | 866.3 | 889.6 | 901.2 | 793.4 | 714.9 | 802.9 | 790.5 | 769.9 | 218.8 | 319 | 104.1 | 318.7 | 302.6 | 101.6 | 264.4 | 330.3 | 195.5
844 | 637 | 565.3 | 226.12 | 264.3213 | 309.5 | 287.4 | 305.3 | 289.1 | 665.9 | 47 | 20 | 81.6 | 5.2 | 276.3 | 7.2 | 892.4 | 810.9 | 862.9 | 889.3 | 903.1 | 793 | 714.3 | 803.1 | 789.4 | 768.9 | 219.1 | 319.1 | 104.3 | 318.6 | 302.8 | 101.8 | 264.6 | 330.7 | 195.8
845 | 638 | 564.7 | 225.88 | 264.0407 | 308.5 | 287.1 | 305.1 | 288.1 | 652.7 | 47.1 | 20 | 81.6 | 4.8 | 267 | 6.7 | 893.3 | 811.2 | 864.6 | 889.7 | 902.6 | 792.9 | 714.9 | 803 | 788.4 | 770.4 | 219.4 | 319.1 | 104.5 | 318.6 | 302.6 | 102.1 | 264.8 | 331.1 | 196
846 | 639 | 565.1 | 226.04 | 264.2277 | 308.2 | 286.3 | 305.3 | 288.2 | 647.3 | 47.2 | 20 | 81.5 | 5.1 | 260.7 | 6.3 | 893.3 | 812.3 | 867.3 | 889.7 | 905.7 | 792.6 | 719 | 804.9 | 787.9 | 771.7 | 219.7 | 319.4 | 104.8 | 318.6 | 302.5 | 102.3 | 264.9 | 331.5 | 196.3
847 | 640 | 564.9 | 225.96 | 264.1342 | 307.3 | 286.4 | 304.7 | 288.2 | 652.3 | 47.1 | 20 | 81.5 | 5.2 | 279.4 | 6.7 | 892.6 | 812.9 | 869.3 | 889.8 | 896.9 | 792.3 | 719.4 | 806.5 | 787.4 | 768.9 | 219.9 | 319.9 | 105 | 318 | 302.3 | 102.5 | 265 | 331.8 | 196.6
848 | 641 | 565.4 | 226.16 | 264.368 | 306.8 | 286.4 | 303.8 | 288.4 | 664.4 | 47.1 | 20 | 81.6 | 5.4 | 287.2 | 6.6 | 893 | 813.6 | 869.7 | 890.1 | 895.6 | 792.2 | 721.9 | 806.6 | 787.2 | 769 | 220.2 | 319.9 | 105.2 | 318 | 301.9 | 102.7 | 265.2 | 332.2 | 196.9
849 | 642 | 565.6 | 226.24 | 264.4615 | 306.7 | 285.8 | 303.2 | 288.7 | 662.3 | 47.1 | 20 | 81.7 | 5 | 283.5 | 6.1 | 893.2 | 815.1 | 870.6 | 890.4 | 899.2 | 791.9 | 723.4 | 806.9 | 786.8 | 770 | 220.4 | 319.8 | 105.4 | 318 | 301.7 | 102.9 | 265.4 | 332.7 | 197.2
850 | 643 | 566 | 226.4 | 264.6486 | 306.1 | 285.1 | 302.6 | 288.5 | 661.6 | 47.1 | 20 | 81.8 | 5.6 | 275.7 | 5.5 | 892.9 | 815.4 | 871.5 | 890 | 904.3 | 791.4 | 724.7 | 806.7 | 786.5 | 769 | 220.7 | 319.7 | 105.7 | 317.7 | 301.7 | 103.2 | 265.5 | 333.1 | 197.5
851 | 644 | 565.3 | 226.12 | 264.3213 | 305.8 | 285.8 | 302.3 | 288.6 | 661.6 | 47.2 | 20 | 81.9 | 4.9 | 297.5 | 5.1 | 892.5 | 814.8 | 871.9 | 889.9 | 901 | 791.2 | 725.5 | 808.8 | 786.3 | 768 | 220.9 | 319.8 | 105.9 | 317.9 | 302 | 103.4 | 265.7 | 333.6 | 197.7
852 | 645 | 564.3 | 225.72 | 263.8537 | 306 | 286.9 | 301.6 | 288.8 | 657.5 | 47.4 | 20 | 82 | 5 | 330.3 | 4.7 | 892.5 | 816 | 871 | 889.9 | 887.7 | 791.2 | 725.6 | 809.7 | 786.4 | 766.9 | 221.2 | 320.1 | 106.1 | 318.2 | 302.2 | 103.6 | 265.9 | 334.1 | 198
853 | 646 | 564.1 | 225.64 | 263.7602 | 306.2 | 287 | 300.6 | 289 | 652.3 | 47.5 | 20 | 82.1 | 5.6 | 332.5 | 4.7 | 893.2 | 817 | 870.7 | 890.3 | 890 | 791.3 | 726.4 | 807.8 | 787 | 767.4 | 221.4 | 320.4 | 106.3 | 318.2 | 302.3 | 103.8 | 266 | 334.5 | 198.3
854 | 647 | 563.8 | 225.52 | 263.6199 | 306.6 | 287.5 | 300.5 | 289.4 | 641.2 | 47.6 | 20 | 82.1 | 6 | 298 | 5.5 | 893.1 | 817.9 | 870.1 | 890.6 | 895 | 791.5 | 726.6 | 806.3 | 787.5 | 769.1 | 221.7 | 320.4 | 106.6 | 318.4 | 302 | 104.1 | 266.1 | 334.9 | 198.6
855 | 648 | 564 | 225.6 | 263.7134 | 306.8 | 288 | 301.2 | 289.8 | 652.4 | 47.7 | 20 | 82.1 | 5.7 | 284.8 | 7.9 | 893.4 | 820.1 | 870.3 | 891.4 | 895 | 791.4 | 727 | 807.6 | 788.4 | 767.7 | 221.9 | 320.3 | 106.8 | 319 | 301.9 | 104.3 | 266.3 | 335.2 | 198.9
856 | 649 | 563.3 | 225.32 | 263.3861 | 307.2 | 288.2 | 301.6 | 289.6 | 676.1 | 47.8 | 20 | 82.1 | 5.5 | 291.2 | 8.7 | 893.6 | 821 | 870.2 | 891.2 | 897.7 | 791.1 | 729.5 | 807.1 | 788.7 | 768.4 | 222.1 | 320.3 | 107 | 319.2 | 301.9 | 104.5 | 266.5 | 335.7 | 199.2
857 | 650 | 563.9 | 225.56 | 263.6666 | 307.8 | 288 | 301.8 | 289.4 | 657.8 | 47.9 | 20 | 82.1 | 5.2 | 291.6 | 8.7 | 892.9 | 821.8 | 869.1 | 891.5 | 898.2 | 790.5 | 730.9 | 805.5 | 787.9 | 771.1 | 222.4 | 320.7 | 107.3 | 319.4 | 302.1 | 104.7 | 266.7 | 336.2 | 199.5
858 | 651 | 564 | 225.6 | 263.7134 | 308 | 288 | 300.9 | 289.5 | 638.6 | 47.9 | 20 | 82.2 | 5.3 | 293.7 | 7.5 | 893.3 | 823.5 | 870.2 | 892.1 | 897.5 | 790.2 | 732.9 | 803 | 787 | 773.7 | 222.6 | 320.8 | 107.5 | 319.8 | 302.2 | 104.9 | 267 | 336.6 | 199.8
859 | 652 | 563.9 | 225.56 | 263.6666 | 308.5 | 288.1 | 301 | 289.5 | 627.2 | 47.9 | 20 | 82.4 | 5 | 276.7 | 8 | 893.2 | 824.2 | 869.7 | 891.9 | 898.2 | 790.1 | 734.6 | 801.4 | 786.5 | 776.1 | 222.8 | 321 | 107.7 | 319.5 | 302.5 | 105.2 | 267.2 | 337.1 | 200.1
860 | 653 | 563.2 | 225.28 | 263.3393 | 308.2 | 288 | 302.3 | 289.5 | 618.7 | 47.8 | 20 | 82.4 | 4.6 | 292.3 | 8.8 | 893.7 | 824.9 | 867.4 | 892.1 | 896.8 | 790.1 | 735.6 | 801.3 | 786 | 779.4 | 223 | 321.2 | 108 | 319.2 | 302.6 | 105.4 | 267.4 | 337.5 | 200.4
861 | 654 | 563.6 | 225.44 | 263.5264 | 308.3 | 288.6 | 302.5 | 289.1 | 606.9 | 47.7 | 20 | 82.4 | 4.6 | 295.2 | 9.3 | 894.2 | 825.7 | 868.9 | 892.5 | 905.7 | 790 | 735.4 | 796.8 | 785.3 | 782.5 | 223.2 | 321 | 108.2 | 319.2 | 302.7 | 105.6 | 267.7 | 337.8 | 200.7
862 | 655 | 563.4 | 225.36 | 263.4329 | 308.8 | 289.8 | 302.5 | 288.1 | 586.2 | 47.7 | 20 | 82.5 | 4.6 | 297.7 | 9.4 | 894.6 | 826.5 | 870.9 | 892.6 | 914.7 | 790 | 734 | 794.7 | 784.9 | 783.1 | 223.4 | 321.1 | 108.4 | 319.6 | 302.7 | 105.9 | 267.8 | 338.1 | 201
863 | 656 | 563.4 | 225.36 | 263.4329 | 309.2 | 289.8 | 303.1 | 287.8 | 587.6 | 47.6 | 20 | 82.5 | 5.1 | 272.7 | 9.2 | 894.9 | 826.6 | 873.7 | 892.8 | 921.9 | 790.1 | 732.8 | 796.7 | 785 | 782.2 | 223.6 | 321.3 | 108.6 | 320 | 302.9 | 106.1 | 268.1 | 338.5 | 201.3
864 | 657 | 563.9 | 225.56 | 263.6666 | 309.2 | 288.5 | 302.7 | 287.8 | 606.9 | 47.7 | 20 | 82.6 | 5.4 | 281.1 | 8.2 | 895.1 | 826.1 | 872.7 | 892.9 | 920.4 | 790 | 731.5 | 799.4 | 785.3 | 779.9 | 223.8 | 321.3 | 108.9 | 320.5 | 302.8 | 106.3 | 268.3 | 338.9 | 201.5
865 | 658 | 563.2 | 225.28 | 263.3393 | 308.4 | 287.8 | 302.3 | 287.1 | 621.5 | 47.8 | 20 | 82.7 | 5 | 282.4 | 7.9 | 895.2 | 826.4 | 874 | 892.8 | 919.1 | 789.8 | 732.5 | 800.7 | 785.3 | 781 | 224 | 321.5 | 109.1 | 321.1 | 302.7 | 106.6 | 268.5 | 339.3 | 201.8
866 | 659 | 563.6 | 225.44 | 263.5264 | 309.2 | 288.2 | 302.6 | 286.6 | 607.6 | 48 | 20 | 82.8 | 4.6 | 288.3 | 7.4 | 895.5 | 827.3 | 874.4 | 893.9 | 919.1 | 789.6 | 730.1 | 799.1 | 784.8 | 781.7 | 224.2 | 321.6 | 109.3 | 321.6 | 302.5 | 106.8 | 268.6 | 339.7 | 202.1
867 | 660 | 564.2 | 225.68 | 263.8069 | 309.2 | 287.9 | 302.6 | 286.9 | 592.3 | 48 | 20 | 82.9 | 5 | 279 | 7.5 | 896 | 827.7 | 874.4 | 894.4 | 919.1 | 789.7 | 730.2 | 799.1 | 784.7 | 783.6 | 224.4 | 321.4 | 109.6 | 321.4 | 302.7 | 107 | 268.8 | 340.1 | 202.4
868 | 661 | 563.3 | 225.32 | 263.3861 | 308.9 | 286.8 | 303.1 | 287.2 | 587.1 | 48 | 20 | 83 | 4.7 | 263.8 | 7.1 | 896.9 | 828.7 | 872.5 | 895.2 | 921.8 | 790 | 728.1 | 797.2 | 784.9 | 785 | 224.6 | 321.2 | 109.8 | 321.1 | 302.6 | 107.3 | 269 | 340.5 | 202.6
869 | 662 | 564.1 | 225.64 | 263.7602 | 308.3 | 285.9 | 303.7 | 287.7 | 574.1 | 48 | 20 | 83 | 4.9 | 218.7 | 5.7 | 897.5 | 828.6 | 871.6 | 895.6 | 920.8 | 790.4 | 727.9 | 796.2 | 785.5 | 786.9 | 224.8 | 321.2 | 110.1 | 321.3 | 302.4 | 107.5 | 269.2 | 340.8 | 202.9
870 | 663 | 565.6 | 226.24 | 264.4615 | 308.7 | 285.5 | 303.9 | 287.5 | 576.6 | 48.1 | 20 | 83.1 | 5 | 229.8 | 4.6 | 898 | 829.3 | 870.9 | 896.1 | 916.7 | 790.5 | 728.8 | 798.3 | 786.1 | 787.4 | 224.9 | 321.2 | 110.3 | 321.9 | 302.4 | 107.8 | 269.4 | 341.1 | 203.2
871 | 664 | 564.1 | 225.64 | 263.7602 | 308.9 | 285.6 | 304 | 287.7 | 600.4 | 48.1 | 20 | 83.3 | 5.4 | 260.4 | 4.8 | 898.2 | 828.9 | 872.6 | 896.3 | 915.1 | 790.4 | 730.2 | 800.8 | 786.6 | 787.9 | 225.1 | 321.4 | 110.5 | 322.5 | 302.7 | 108.1 | 269.6 | 341.5 | 203.5
872 | 665 | 563.7 | 225.48 | 263.5731 | 309.9 | 285.5 | 304 | 288.1 | 595.5 | 48.2 | 20 | 83.3 | 5.9 | 268.3 | 5.3 | 898.8 | 828.3 | 871.7 | 896.5 | 913.6 | 790.7 | 729.8 | 800.7 | 786.7 | 789.3 | 225.3 | 321.4 | 110.7 | 322.3 | 302.8 | 108.4 | 269.9 | 341.8 | 203.8
873 | 666 | 563.3 | 225.32 | 263.3861 | 310.4 | 285.2 | 305 | 288.4 | 586.1 | 48.3 | 20 | 83.4 | 6 | 287.6 | 6.5 | 899.3 | 828.6 | 872 | 896.9 | 922.9 | 790.9 | 729.6 | 798.1 | 786.5 | 791.1 | 225.5 | 321.2 | 111 | 322.2 | 302.7 | 108.7 | 270.2 | 342.1 | 204.1
874 | 667 | 563.2 | 225.28 | 263.3393 | 309.9 | 284.6 | 305.5 | 288.5 | 575.1 | 48.3 | 20 | 83.5 | 5.4 | 288.6 | 7.4 | 899.9 | 828.7 | 867 | 897.1 | 922.2 | 791.2 | 727 | 795.6 | 786.9 | 791.3 | 225.6 | 321 | 111.2 | 322.2 | 302.7 | 108.9 | 270.5 | 342.5 | 204.4
875 | 668 | 564.6 | 225.84 | 263.9939 | 310.4 | 283.9 | 305.8 | 288.8 | 567.9 | 48.4 | 20 | 83.6 | 5.1 | 283.2 | 7.6 | 900.4 | 829.3 | 867.5 | 897.1 | 922 | 791.6 | 727.2 | 795.9 | 787.8 | 792.5 | 225.8 | 320.9 | 111.5 | 321.7 | 303.1 | 109.2 | 270.7 | 342.8 | 204.6
876 | 669 | 563.6 | 225.44 | 263.5264 | 310.1 | 284.1 | 305.9 | 288.9 | 574.3 | 48.5 | 20 | 83.8 | 5.2 | 285.6 | 8.2 | 901.1 | 830.6 | 871.6 | 897.6 | 927.7 | 791.6 | 726.6 | 797.8 | 788.7 | 791.2 | 226 | 320.9 | 111.7 | 321.6 | 303.4 | 109.5 | 270.8 | 343.1 | 204.9
877 | 670 | 563.1 | 225.24 | 263.2926 | 309.3 | 284.4 | 305.6 | 289 | 583.3 | 48.5 | 20 | 84 | 4.4 | 282.5 | 9.2 | 901.7 | 828.8 | 869 | 897.6 | 919.2 | 791.9 | 722 | 794 | 789.2 | 789 | 226.3 | 320.7 | 111.9 | 321.4 | 303.6 | 109.9 | 271 | 343.5 | 205.2
878 | 671 | 563.7 | 225.48 | 263.5731 | 308.9 | 284.6 | 306.3 | 289.1 | 572.3 | 48.5 | 20 | 84.2 | 4.3 | 285.9 | 9.9 | 903.1 | 825.2 | 860.8 | 898.2 | 907 | 792 | 712.2 | 787.4 | 789.7 | 785.8 | 226.5 | 321 | 112.2 | 321.6 | 303.9 | 110.2 | 271.1 | 343.8 | 205.5
879 | 672 | 563.5 | 225.4 | 263.4796 | 311 | 284.6 | 308.1 | 288.9 | 561.5 | 48.6 | 20 | 84.3 | 4.7 | 272.1 | 9.8 | 903.9 | 821.1 | 859.4 | 898.7 | 897.7 | 792.1 | 704 | 785.8 | 790.3 | 782 | 226.8 | 321.2 | 112.4 | 321.6 | 304.5 | 110.5 | 271.3 | 344 | 205.7
880 | 673 | 563.2 | 225.28 | 263.3393 | 311.7 | 284.7 | 308.6 | 289.1 | 564.6 | 48.6 | 20 | 84.5 | 4.5 | 271.7 | 8.8 | 904.3 | 818.7 | 863 | 898.9 | 893.1 | 792.1 | 700.5 | 788.2 | 791.1 | 779.5 | 227 | 321.2 | 112.7 | 322.1 | 305.1 | 110.7 | 271.6 | 344.2 | 206
881 | 674 | 563.8 | 225.52 | 263.6199 | 311.8 | 284.6 | 308.2 | 289.8 | 581.2 | 48.7 | 19.9 | 84.7 | 5.1 | 274.6 | 8.5 | 904.5 | 816.1 | 863.5 | 898.8 | 885.3 | 791.8 | 701.6 | 792 | 791.6 | 777.4 | 227.3 | 321.6 | 112.9 | 322.1 | 305.5 | 111 | 271.7 | 344.4 | 206.3
882 | 675 | 562.9 | 225.16 | 263.1991 | 312 | 284.6 | 308.7 | 290.6 | 603.4 | 48.7 | 19.9 | 84.8 | 4.7 | 265.7 | 8.4 | 905 | 814.6 | 864.8 | 899.3 | 885.3 | 791.7 | 705.8 | 794.4 | 792.2 | 776.1 | 227.6 | 322.1 | 113.2 | 322.3 | 305.4 | 111.4 | 271.8 | 344.7 | 206.6
883 | 676 | 563 | 225.2 | 263.2458 | 311.8 | 285.4 | 308.9 | 291.1 | 627.3 | 48.7 | 19.9 | 84.8 | 4.8 | 260.4 | 7.4 | 904.9 | 813.5 | 865.1 | 899.1 | 889.1 | 791.3 | 710.5 | 796.5 | 792.2 | 776 | 227.9 | 322.1 | 113.4 | 322.1 | 305.5 | 111.7 | 272 | 345 | 206.9
884 | 677 | 562.9 | 225.16 | 263.1991 | 312.8 | 286 | 309.6 | 291.4 | 623.8 | 48.6 | 19.9 | 84.8 | 5.1 | 263.5 | 6 | 904.6 | 814 | 866.3 | 898.9 | 893.3 | 790.8 | 713.8 | 797.2 | 791.4 | 780 | 228.2 | 322 | 113.7 | 321.8 | 305.3 | 112.1 | 272.1 | 345.3 | 207.2
885 | 678 | 562.5 | 225 | 263.012 | 313.6 | 286.6 | 309.3 | 291.2 | 621.5 | 48.5 | 19.9 | 84.7 | 5.1 | 267.5 | 5.8 | 904.1 | 815 | 867.2 | 898.7 | 896.8 | 790.3 | 716.9 | 799.6 | 790.7 | 781 | 228.4 | 322 | 113.9 | 322 | 305.2 | 112.4 | 272.2 | 345.7 | 207.5
886 | 679 | 564.1 | 225.64 | 263.7602 | 312.8 | 287.1 | 309.6 | 291.3 | 620.6 | 48.5 | 19.9 | 84.6 | 5.2 | 284.2 | 6.4 | 903.5 | 815.6 | 866.2 | 898.2 | 894.9 | 789.8 | 719.7 | 799.9 | 789.5 | 782.3 | 228.7 | 321.8 | 114.2 | 322 | 305.2 | 112.7 | 272.4 | 346.1 | 207.7
887 | 680 | 565.9 | 226.36 | 264.6018 | 311.7 | 287.5 | 310 | 291.4 | 621.1 | 48.4 | 19.9 | 84.6 | 4.7 | 290.2 | 6.9 | 903.1 | 815.3 | 861.2 | 897.1 | 901.1 | 789.7 | 722.3 | 799.2 | 788.6 | 782.6 | 228.9 | 321.8 | 114.4 | 322.1 | 305.2 | 113.1 | 272.5 | 346.4 | 208
888 | 681 | 564.8 | 225.92 | 264.0875 | 311.6 | 287.9 | 309.9 | 291.6 | 610.8 | 48.4 | 19.9 | 84.6 | 4.8 | 284.2 | 6.4 | 903.3 | 813.3 | 859 | 896.9 | 899.3 | 790.1 | 718.2 | 796.4 | 788.3 | 780 | 229.2 | 321.8 | 114.7 | 322 | 305.4 | 113.4 | 272.6 | 346.8 | 208.3
889 | 682 | 566.1 | 226.44 | 264.6953 | 312.1 | 288 | 310.8 | 291.1 | 607.8 | 48.6 | 19.9 | 84.6 | 4.4 | 261.3 | 6.5 | 903.8 | 812.1 | 858.3 | 897.1 | 890.6 | 790.3 | 714.4 | 796.8 | 788.6 | 778.2 | 229.3 | 321.8 | 115 | 322.1 | 305.2 | 113.7 | 272.7 | 347 | 208.5
890 | 683 | 565 | 226 | 264.181 | 311.8 | 287.7 | 311.5 | 291.1 | 610.7 | 48.6 | 19.9 | 84.5 | 4.8 | 253.7 | 6.1 | 904 | 811.2 | 858.7 | 897.4 | 887.7 | 790.5 | 711.2 | 797 | 789.3 | 775.6 | 229.5 | 322.2 | 115.2 | 322.5 | 305.1 | 114.1 | 272.8 | 347.2 | 208.8
891 | 684 | 565.8 | 226.32 | 264.555 | 312.8 | 287.2 | 310.9 | 291.7 | 618.5 | 48.6 | 19.9 | 84.5 | 4.7 | 253.3 | 5.1 | 904.1 | 811.3 | 859.6 | 897.4 | 888.1 | 790.5 | 711.8 | 798 | 790 | 775.1 | 229.6 | 322.9 | 115.5 | 322.6 | 305 | 114.4 | 273 | 347.5 | 209.1
892 | 685 | 565.1 | 226.04 | 264.2277 | 312.9 | 287 | 311.4 | 292 | 624 | 48.7 | 19.9 | 84.6 | 4.5 | 271.8 | 4.3 | 904.1 | 811.6 | 857.5 | 897.1 | 892.6 | 790.4 | 713.6 | 797.1 | 790.5 | 775.7 | 229.8 | 323.7 | 115.7 | 322.4 | 305 | 114.7 | 273.1 | 347.8 | 209.3
893 | 686 | 564 | 225.6 | 263.7134 | 312.9 | 287.4 | 312.2 | 292.3 | 620.5 | 48.7 | 19.9 | 84.7 | 4.8 | 262.2 | 4 | 904.1 | 811.1 | 861.1 | 897.3 | 898.1 | 790.4 | 713.6 | 798.7 | 790.6 | 776 | 230 | 324.3 | 116 | 322.4 | 304.9 | 115.1 | 273.2 | 348.2 | 209.6
894 | 687 | 564.6 | 225.84 | 263.9939 | 314.4 | 287.5 | 312.5 | 292.7 | 638.2 | 48.6 | 19.9 | 84.7 | 4.9 | 241.5 | 4.2 | 904 | 810.2 | 861.4 | 896.7 | 894.6 | 790.5 | 713.3 | 798.5 | 791 | 771.9 | 230.1 | 324.5 | 116.3 | 323.1 | 305.1 | 115.5 | 273.3 | 348.5 | 209.9
895 | 688 | 564.1 | 225.64 | 263.7602 | 314.6 | 287.5 | 312.4 | 293 | 639.6 | 48.6 | 19.9 | 84.7 | 4.9 | 243.2 | 4.6 | 903.3 | 809.9 | 862.6 | 896.3 | 892.7 | 790.3 | 714 | 799.8 | 791.4 | 770.4 | 230.3 | 325.1 | 116.5 | 323.6 | 305.1 | 115.9 | 273.4 | 348.8 | 210.2
896 | 689 | 564.5 | 225.8 | 263.9472 | 314.7 | 288.3 | 312.1 | 293.6 | 645.6 | 48.7 | 19.9 | 84.6 | 5.4 | 243.1 | 4.9 | 902.9 | 810.3 | 862.9 | 896 | 889.5 | 790.3 | 713.5 | 800.9 | 791.4 | 769.4 | 230.5 | 325.9 | 116.8 | 324 | 305.2 | 116.3 | 273.6 | 349.2 | 210.5
897 | 690 | 564.8 | 225.92 | 264.0875 | 314.5 | 289.7 | 312.1 | 293.7 | 654.2 | 48.7 | 19.9 | 84.6 | 5.4 | 250.3 | 4.9 | 903 | 810.9 | 861.2 | 896 | 886.1 | 790.9 | 717.3 | 803.6 | 792.1 | 769.2 | 230.7 | 326.7 | 117.1 | 324.7 | 305.6 | 116.5 | 273.8 | 349.5 | 210.7
898 | 691 | 565.1 | 226.04 | 264.2277 | 315.5 | 290.8 | 313.2 | 294.5 | 664.6 | 48.8 | 19.9 | 84.6 | 5.5 | 275.8 | 4.5 | 902.7 | 811.6 | 862.5 | 895.7 | 884 | 791 | 717.5 | 804.7 | 792.6 | 766.9 | 230.9 | 326.6 | 117.4 | 324.9 | 305.9 | 116.8 | 274 | 349.9 | 211
899 | 692 | 565.2 | 226.08 | 264.2745 | 316 | 291.2 | 314.3 | 294.6 | 674.8 | 48.8 | 19.9 | 84.7 | 5.1 | 271.4 | 4.3 | 902.5 | 811.3 | 865.6 | 895.7 | 880.4 | 790.9 | 717.3 | 806.6 | 792.4 | 764.5 | 231.1 | 326.8 | 117.6 | 325.2 | 306.1 | 117.3 | 274.2 | 350.3 | 211.3
900 | 693 | 565.4 | 226.16 | 264.368 | 316.3 | 291 | 314.4 | 294.8 | 671 | 48.9 | 19.9 | 84.7 | 5.4 | 251.1 | 4.8 | 902.1 | 811.1 | 866.3 | 895.3 | 873 | 790.9 | 714.9 | 807.2 | 791.7 | 762.2 | 231.3 | 327.8 | 117.9 | 325.6 | 306.5 | 117.7 | 274.4 | 350.7 | 211.6
901 | 694 | 565.1 | 226.04 | 264.2277 | 316.1 | 291.7 | 315 | 295.6 | 665.1 | 49 | 19.9 | 84.7 | 5.8 | 249.7 | 5.1 | 902.2 | 809.2 | 865.4 | 895.2 | 863.8 | 791 | 708.8 | 804.3 | 791.2 | 758 | 231.5 | 328.5 | 118.2 | 326.3 | 306.8 | 118.1 | 274.6 | 351.1 | 211.9
902 | 695 | 565.1 | 226.04 | 264.2277 | 316.4 | 292.4 | 316.8 | 296.1 | 645 | 49.1 | 19.9 | 84.7 | 5.4 | 258.8 | 5.3 | 902.3 | 806.8 | 859.5 | 895.1 | 860 | 790.9 | 702.2 | 797.7 | 790.9 | 754.9 | 231.8 | 328.3 | 118.5 | 326.8 | 307 | 118.5 | 274.8 | 351.4 | 212.1
903 | 696 | 563.8 | 225.52 | 263.6199 | 317 | 292.7 | 317.9 | 296.5 | 629.9 | 49.2 | 19.9 | 84.7 | 5.1 | 262.1 | 4.8 | 902.6 | 805 | 857.1 | 895.4 | 855.1 | 790.9 | 698.2 | 796 | 791.3 | 752.9 | 232 | 328.9 | 118.8 | 327.4 | 307.1 | 119 | 275 | 351.7 | 212.4
904 | 697 | 564.4 | 225.76 | 263.9004 | 317.5 | 293.1 | 318.3 | 296.8 | 619.9 | 49.2 | 19.9 | 84.7 | 4.8 | 270.2 | 4.6 | 902.9 | 804.4 | 858.2 | 895.9 | 855.1 | 790.8 | 697.2 | 797 | 791.8 | 751 | 232.3 | 330 | 119 | 327.5 | 307.5 | 119.4 | 275.2 | 351.9 | 212.7
905 | 698 | 564.3 | 225.72 | 263.8537 | 318.3 | 292.9 | 317.7 | 296.4 | 625.4 | 49.3 | 19.9 | 84.8 | 4.8 | 283.1 | 5.1 | 903.2 | 806 | 858.2 | 896.2 | 857.2 | 790.5 | 700.8 | 799.1 | 792.1 | 749.4 | 232.5 | 330.8 | 119.3 | 328 | 307.7 | 119.7 | 275.4 | 352.2 | 213
906 | 699 | 564.2 | 225.68 | 263.8069 | 318.4 | 293.8 | 317.8 | 296.6 | 650.9 | 49.4 | 19.9 | 84.9 | 5.1 | 281.4 | 5.5 | 903.2 | 806.7 | 859.8 | 896.3 | 855.8 | 790.1 | 705.2 | 801.9 | 792 | 749.4 | 232.8 | 331 | 119.6 | 328.1 | 308.2 | 120.1 | 275.6 | 352.6 | 213.3
907 | 700 | 563.7 | 225.48 | 263.5731 | 318.2 | 294.6 | 318.1 | 296.9 | 653.7 | 49.5 | 19.9 | 85.1 | 4.9 | 275.6 | 5.7 | 903 | 807.1 | 859.4 | 896 | 857.3 | 789.9 | 705.7 | 802.2 | 792 | 748.3 | 233.1 | 331.5 | 119.9 | 328.7 | 308.4 | 120.5 | 275.9 | 353 | 213.5
908 | 701 | 563.7 | 225.48 | 263.5731 | 318 | 295.3 | 318.2 | 297.1 | 634.1 | 49.5 | 19.9 | 85.4 | 5.2 | 273.7 | 5.7 | 902.9 | 808.2 | 859.5 | 895.7 | 860.4 | 789.7 | 704.8 | 802.5 | 792 | 748.5 | 233.4 | 332.4 | 120.2 | 328.8 | 308.4 | 120.9 | 276.1 | 353.3 | 213.9
909 | 702 | 564.7 | 225.88 | 264.0407 | 318 | 295.9 | 318.4 | 297.4 | 620.2 | 49.6 | 19.9 | 85.5 | 5.1 | 259.9 | 5.1 | 903.2 | 807.1 | 856.8 | 895.4 | 860.3 | 789.8 | 699.4 | 798.4 | 791.7 | 745.6 | 233.7 | 333.2 | 120.5 | 328.8 | 308.4 | 121.3 | 276.2 | 353.6 | 214.1
910 | 703 | 564.8 | 225.92 | 264.0875 | 318.3 | 296.4 | 319.4 | 297.7 | 596.2 | 49.6 | 19.9 | 85.5 | 5.4 | 248.1 | 4.7 | 903.3 | 805.5 | 855.1 | 895.5 | 857.3 | 790.2 | 694.5 | 793.6 | 791.7 | 743.8 | 234 | 333.4 | 120.8 | 328.7 | 308.3 | 121.8 | 276.4 | 353.9 | 214.4
911 | 704 | 564.2 | 225.68 | 263.8069 | 319.2 | 296.8 | 320 | 298 | 593.5 | 49.6 | 19.9 | 85.5 | 5.4 | 254.9 | 4.4 | 903.3 | 804.4 | 851.8 | 894.9 | 853.2 | 790.1 | 690.8 | 793.6 | 792.2 | 740.8 | 234.3 | 334.1 | 121.1 | 329.1 | 308.1 | 122.1 | 276.4 | 354.1 | 214.7
912 | 705 | 563.7 | 225.48 | 263.5731 | 319.9 | 297.2 | 319.1 | 298 | 602.4 | 49.7 | 19.9 | 85.5 | 5.2 | 249.4 | 4.1 | 903.2 | 802.9 | 844.6 | 894.7 | 835.4 | 790.4 | 689.2 | 793.7 | 793 | 738.4 | 234.7 | 334.5 | 121.4 | 329.5 | 307.9 | 122.5 | 276.6 | 354.4 | 214.9
913 | 706 | 563.8 | 225.52 | 263.6199 | 320.7 | 297.6 | 319.2 | 298.7 | 618.1 | 49.7 | 19.9 | 85.6 | 5.3 | 290.6 | 4.9 | 903.3 | 801.3 | 842 | 895 | 825.5 | 790.3 | 687.8 | 796.5 | 794.5 | 735.4 | 235 | 335.1 | 121.7 | 330.5 | 308 | 122.9 | 276.8 | 354.7 | 215.2
914 | 707 | 565.1 | 226.04 | 264.2277 | 321.3 | 297.7 | 320 | 299.3 | 631.7 | 49.8 | 19.9 | 85.7 | 4.5 | 275.1 | 5.7 | 903.5 | 800.8 | 845.1 | 895 | 822.9 | 790.1 | 690.4 | 800.3 | 795.2 | 733.9 | 235.2 | 335.9 | 122 | 330.8 | 308.3 | 123.2 | 277 | 355 | 215.5
915 | 708 | 565.4 | 226.16 | 264.368 | 321.8 | 298.3 | 321 | 299.4 | 665.3 | 49.9 | 19.9 | 85.9 | 5 | 271.5 | 6.2 | 903.6 | 800.1 | 846.2 | 894.8 | 823.5 | 790.2 | 694.7 | 801.4 | 795.4 | 733.1 | 235.6 | 335.9 | 122.2 | 331.4 | 308.6 | 123.7 | 277.1 | 355.4 | 215.9
916 | 709 | 564.9 | 225.96 | 264.1342 | 321.8 | 299.2 | 321.5 | 299.8 | 673.8 | 50 | 19.9 | 86 | 5.1 | 282 | 7 | 903.2 | 801 | 848.6 | 894.5 | 822 | 790.2 | 695.8 | 802.5 | 795.3 | 732 | 235.9 | 335.7 | 122.5 | 332.2 | 308.9 | 124.1 | 277.3 | 355.8 | 216.2
917 | 710 | 566 | 226.4 | 264.6486 | 322.4 | 299.9 | 322.4 | 300.6 | 682.1 | 50 | 19.9 | 86.2 | 5.2 | 266.6 | 6.9 | 902.8 | 801.5 | 851.3 | 894.2 | 821 | 790.4 | 700.3 | 804 | 795.2 | 730.5 | 236.3 | 336.3 | 122.8 | 332.4 | 309 | 124.5 | 277.4 | 356.2 | 216.5
918 | 711 | 566.4 | 226.56 | 264.8356 | 322.5 | 300.3 | 322.9 | 300.7 | 691.8 | 50 | 19.9 | 86.4 | 6.3 | 257.8 | 6.3 | 902.4 | 803.4 | 853 | 894.1 | 824.3 | 790.1 | 704.6 | 805.6 | 794.7 | 729 | 236.9 | 336.6 | 123.1 | 332.9 | 309.2 | 125 | 277.7 | 356.6 | 216.8
919 | 712 | 565.6 | 226.24 | 264.4615 | 322.9 | 300.5 | 323.1 | 301.2 | 697.7 | 50 | 19.9 | 86.5 | 7.7 | 279.8 | 6 | 901.8 | 806.2 | 852.2 | 893.9 | 831.2 | 789.5 | 710 | 807.3 | 793.7 | 729.5 | 237.5 | 337.1 | 123.4 | 333.5 | 309.7 | 125.3 | 277.9 | 357 | 217.1
920 | 713 | 564.1 | 225.64 | 263.7602 | 323.2 | 300.8 | 322.4 | 301.6 | 685.1 | 50.1 | 19.9 | 86.5 | 8.2 | 283.3 | 6.6 | 901.2 | 807 | 851.7 | 893.5 | 840.4 | 789.3 | 713.1 | 806 | 792.3 | 732.6 | 238.2 | 337.3 | 123.7 | 333.5 | 309.9 | 125.7 | 278.1 | 357.4 | 217.3
921 | 714 | 563.5 | 225.4 | 263.4796 | 323.7 | 300.8 | 321.7 | 302.3 | 659.6 | 50.1 | 19.9 | 86.6 | 8.3 | 275.7 | 6.7 | 900.6 | 809.9 | 850.3 | 893.2 | 851.7 | 789.4 | 716.8 | 804.6 | 791 | 736.3 | 239.1 | 337.2 | 124 | 333.2 | 310.2 | 126 | 278.4 | 357.7 | 217.6
922 | 715 | 563.2 | 225.28 | 263.3393 | 324.6 | 300.5 | 321.4 | 302.5 | 655 | 50.1 | 19.9 | 86.7 | 8.4 | 264.6 | 6 | 900 | 813.3 | 852.3 | 893.2 | 862.5 | 789.5 | 719.7 | 807.1 | 790.1 | 739.3 | 240.3 | 337.1 | 124.3 | 333.2 | 310.3 | 126.3 | 278.6 | 358 | 217.9
923 | 716 | 564.4 | 225.76 | 263.9004 | 324.4 | 300.1 | 320.7 | 302 | 663.5 | 50 | 19.9 | 86.7 | 8.8 | 262.6 | 5.9 | 899.7 | 814.6 | 854.8 | 893.1 | 870.9 | 789.5 | 722.3 | 808.1 | 789.6 | 740.4 | 241.5 | 336.8 | 124.6 | 333.1 | 310.2 | 126.6 | 278.8 | 358.3 | 218.2
924 | 717 | 564.5 | 225.8 | 263.9472 | 324.3 | 300 | 319.6 | 300.3 | 667.6 | 50.1 | 19.9 | 86.7 | 7.7 | 254.5 | 6.4 | 899.8 | 814.6 | 852.2 | 892.7 | 863.9 | 789.5 | 721.2 | 809.2 | 788.7 | 738.8 | 242.7 | 336.7 | 124.9 | 332.9 | 310.9 | 126.8 | 278.8 | 358.7 | 218.5
925 | 718 | 563.7 | 225.48 | 263.5731 | 323.4 | 299.8 | 320.5 | 299.3 | 677.6 | 50.2 | 19.9 | 86.7 | 7.1 | 250.9 | 7.3 | 899.8 | 812.5 | 850 | 892.3 | 845 | 790 | 719.7 | 810 | 788.7 | 736.5 | 243.9 | 337.2 | 125.2 | 333 | 311.1 | 127 | 279 | 359.1 | 218.7
926 | 719 | 563.7 | 225.48 | 263.5731 | 323.4 | 300.6 | 321.8 | 299.5 | 676.5 | 50.2 | 19.9 | 86.6 | 6.6 | 235.2 | 9.4 | 899.4 | 812.4 | 853 | 892.1 | 846.7 | 790 | 719.3 | 809.8 | 788.6 | 736.6 | 245.1 | 337.6 | 125.5 | 332.8 | 311 | 127.3 | 279 | 359.4 | 219
927 | 720 | 563.4 | 225.36 | 263.4329 | 323.4 | 301.2 | 322.9 | 299.6 | 682.3 | 50.3 | 19.9 | 86.5 | 6.4 | 262.2 | 10.1 | 899.1 | 813.7 | 853.1 | 892.1 | 847.9 | 789.9 | 722.3 | 810.3 | 788.1 | 738.2 | 246.2 | 337.4 | 125.8 | 333.2 | 310.8 | 127.8 | 279.1 | 359.8 | 219.3
928 | 721 | 563 | 225.2 | 263.2458 | 323.7 | 301.7 | 324.1 | 299.4 | 692 | 50.3 | 19.9 | 86.5 | 6.5 | 235 | 10.3 | 898.5 | 814.7 | 855.7 | 891.8 | 853.3 | 789.8 | 726.9 | 809.7 | 787.5 | 740.6 | 247.2 | 337.6 | 126.1 | 333.5 | 310.7 | 128.2 | 279.3 | 360.1 | 219.6
929 | 722 | 565.8 | 226.32 | 264.555 | 323.6 | 302.4 | 324.5 | 299.3 | 709.6 | 50.4 | 19.9 | 86.4 | 6.4 | 245.9 | 10.9 | 898.5 | 815.1 | 855.4 | 891.8 | 854.4 | 789.5 | 727.7 | 809.1 | 786.9 | 739.3 | 248.2 | 338 | 126.4 | 334 | 311.3 | 128.5 | 279.4 | 360.6 | 219.9
930 | 723 | 566.2 | 226.48 | 264.7421 | 323.4 | 302.8 | 324.3 | 299.7 | 712.7 | 50.4 | 19.8 | 86.3 | 6.2 | 251.7 | 11 | 898.7 | 812.7 | 851.7 | 891.7 | 847.3 | 789.9 | 726.4 | 810.3 | 787.2 | 737.1 | 249.1 | 338.8 | 126.7 | 334.5 | 311.6 | 128.9 | 279.6 | 361 | 220.2
931 | 724 | 567.3 | 226.92 | 265.2564 | 323.3 | 303.2 | 325.7 | 300.1 | 726.8 | 50.4 | 19.8 | 86.2 | 6.5 | 253.4 | 10.3 | 898.7 | 811.8 | 854.2 | 891.6 | 840.9 | 790.1 | 726.3 | 810.1 | 787.8 | 735.5 | 250.1 | 339.7 | 127 | 334.8 | 311.8 | 129.2 | 279.8 | 361.4 | 220.4
932 | 725 | 566.3 | 226.52 | 264.7888 | 323.1 | 302.8 | 326.2 | 300.3 | 719.9 | 50.5 | 19.8 | 86.2 | 6.7 | 260.2 | 9.4 | 898.5 | 811.6 | 854.5 | 891.6 | 841.5 | 790.3 | 726.1 | 810.2 | 788.4 | 734.6 | 251.1 | 340.1 | 127.3 | 335.1 | 312 | 129.6 | 280 | 361.9 | 220.7
933 | 726 | 566.1 | 226.44 | 264.6953 | 323.5 | 302.5 | 325.1 | 300.5 | 716.9 | 50.6 | 19.8 | 86.2 | 5.9 | 249.6 | 9 | 898.4 | 812 | 855 | 891.6 | 845.4 | 790.2 | 728.7 | 810.6 | 788.7 | 736.7 | 252 | 340.4 | 127.6 | 335.5 | 312.3 | 129.9 | 280.2 | 362.3 | 221
934 | 727 | 564.9 | 225.96 | 264.1342 | 323.9 | 302.6 | 324.9 | 300.5 | 722.1 | 50.5 | 19.8 | 86.1 | 5.3 | 271.9 | 8.2 | 898.2 | 813 | 854.6 | 891.6 | 850.1 | 790.2 | 731.6 | 810.8 | 788.8 | 738 | 252.9 | 340.3 | 127.9 | 336 | 312.4 | 130.2 | 280.4 | 362.7 | 221.3
935 | 728 | 564.1 | 225.64 | 263.7602 | 323.4 | 303.2 | 325.3 | 301 | 722.9 | 50.4 | 19.8 | 85.9 | 5.9 | 251 | 7.1 | 898.6 | 811.9 | 848.8 | 891.6 | 850.9 | 790.2 | 729.2 | 810.7 | 788.3 | 737.6 | 253.9 | 340.4 | 128.2 | 336.4 | 312.3 | 130.5 | 280.7 | 363.1 | 221.6
936 | 729 | 567.1 | 226.84 | 265.1629 | 323.7 | 303.7 | 324.5 | 301.4 | 713.6 | 50.3 | 19.8 | 85.8 | 7.1 | 252.2 | 6.5 | 898.8 | 811.1 | 846.6 | 891.8 | 849.2 | 790.6 | 727.1 | 808.5 | 788.1 | 738.8 | 254.8 | 340.5 | 128.5 | 337.1 | 312.4 | 130.9 | 280.8 | 363.5 | 221.9
937 | 730 | 565.7 | 226.28 | 264.5083 | 324.1 | 304.1 | 323.2 | 301.2 | 704 | 50.3 | 19.8 | 85.7 | 6.9 | 269.7 | 7.3 | 898.6 | 811.5 | 848.2 | 892 | 851.3 | 790.8 | 728.7 | 808.1 | 787.9 | 741.5 | 255.7 | 340.5 | 128.8 | 337.6 | 312.7 | 131.1 | 281 | 363.8 | 222.2
938 | 731 | 564.5 | 225.8 | 263.9472 | 324.3 | 304.3 | 322.9 | 301.8 | 705 | 50.3 | 19.8 | 85.8 | 6.6 | 245.1 | 7.2 | 898.4 | 812.5 | 848.2 | 891.8 | 857.7 | 790.6 | 730.6 | 807.4 | 787.4 | 743.8 | 256.5 | 341 | 129.1 | 337.8 | 313 | 131.4 | 281.3 | 364.2 | 222.5
939 | 732 | 564.8 | 225.92 | 264.0875 | 324.3 | 304.4 | 322.5 | 302 | 705.5 | 50.3 | 19.8 | 85.8 | 5.8 | 259.7 | 7.1 | 898.1 | 813.8 | 844.4 | 891.7 | 866 | 790.5 | 733 | 807.9 | 786.9 | 746.2 | 257.3 | 341.2 | 129.4 | 337.6 | 313.3 | 131.8 | 281.5 | 364.5 | 222.8
940 | 733 | 565.7 | 226.28 | 264.5083 | 324.3 | 304.7 | 322.5 | 301.7 | 703.7 | 50.3 | 19.8 | 85.9 | 6 | 244.5 | 6.4 | 898.2 | 813.9 | 842.9 | 891.9 | 866.7 | 790.6 | 735.6 | 808.8 | 786.6 | 747.2 | 258 | 341.2 | 129.7 | 337.8 | 313.4 | 132.1 | 281.6 | 364.9 | 223.1
941 | 734 | 565.5 | 226.2 | 264.4148 | 325.4 | 304.8 | 323.1 | 301.8 | 688.6 | 50.2 | 19.8 | 85.9 | 6.8 | 244 | 5.9 | 898.4 | 812.9 | 840.6 | 891.9 | 862.4 | 791 | 731.8 | 808.7 | 786.6 | 746.4 | 258.8 | 341.4 | 130 | 338 | 313.2 | 132.5 | 281.8 | 365.3 | 223.3
942 | 735 | 565.3 | 226.12 | 264.3213 | 326 | 304.7 | 322.7 | 301 | 679.2 | 50.2 | 19.8 | 85.9 | 7.3 | 278.3 | 5.7 | 898 | 811.7 | 839 | 891.6 | 858.5 | 791.3 | 729 | 808.2 | 786.6 | 745.3 | 259.5 | 341.5 | 130.3 | 338.2 | 313.8 | 132.7 | 281.9 | 365.6 | 223.6
943 | 736 | 565.4 | 226.16 | 264.368 | 326 | 304.9 | 322.5 | 299.9 | 690.2 | 50.2 | 19.8 | 85.9 | 6.5 | 263.7 | 6.3 | 897.1 | 813 | 844.4 | 891.2 | 861.6 | 791.5 | 731.5 | 809 | 786.7 | 746.8 | 260.3 | 341.8 | 130.6 | 337.8 | 314.4 | 132.8 | 282.2 | 366 | 223.9
944 | 737 | 565.4 | 226.16 | 264.368 | 326.6 | 305.4 | 321.9 | 299.8 | 715.4 | 50.2 | 19.8 | 86 | 6.8 | 259.3 | 9.7 | 896.3 | 813.8 | 847.1 | 890.6 | 864.5 | 791.3 | 736.1 | 808.2 | 787.1 | 746.3 | 261.1 | 342.8 | 130.8 | 337.6 | 314.7 | 133 | 282.4 | 366.3 | 224.1
945 | 738 | 565.2 | 226.08 | 264.2745 | 326.8 | 305.8 | 321.1 | 299.6 | 725.7 | 50.1 | 19.8 | 86 | 8 | 269.4 | 11.1 | 895.7 | 815.3 | 848.2 | 890.3 | 867.1 | 791 | 739.1 | 808.1 | 786.6 | 748.8 | 262 | 343.8 | 131.1 | 337.8 | 315 | 133.3 | 282.6 | 366.8 | 224.4
946 | 739 | 565 | 226 | 264.181 | 327.2 | 305.9 | 321.1 | 299.7 | 717.3 | 50 | 19.8 | 86.1 | 6.7 | 267.3 | 10.5 | 895.5 | 816.8 | 847.4 | 890.1 | 871.3 | 790.9 | 737.6 | 809.1 | 785.8 | 749.2 | 262.8 | 343.9 | 131.4 | 338.5 | 314.8 | 133.6 | 282.7 | 367.3 | 224.7
947 | 740 | 565.2 | 226.08 | 264.2745 | 328.2 | 305.7 | 322.2 | 300 | 710.5 | 50 | 19.8 | 86.1 | 6.5 | 255.8 | 11.8 | 895.4 | 816.5 | 846 | 890.2 | 867.2 | 791.1 | 734.9 | 809.9 | 785.7 | 747.5 | 263.6 | 344.2 | 131.7 | 338.9 | 314.6 | 134 | 282.8 | 367.7 | 225
948 | 741 | 565.4 | 226.16 | 264.368 | 329.2 | 305.8 | 323.6 | 300.4 | 711.8 | 50.1 | 19.8 | 86.1 | 6.6 | 267.9 | 12.3 | 894.9 | 816.2 | 849 | 890.1 | 858.8 | 791.4 | 734.5 | 809.2 | 785.8 | 746.1 | 264.4 | 344.4 | 132 | 339.1 | 314.8 | 134.3 | 283 | 368.1 | 225.3
949 | 742 | 564.9 | 225.96 | 264.1342 | 329.8 | 306.5 | 324.6 | 301.3 | 714.8 | 50.2 | 19.8 | 86.1 | 6.3 | 253.6 | 13.1 | 894.5 | 816 | 848.6 | 889.7 | 854.9 | 791.8 | 735.7 | 809.8 | 786.4 | 745.3 | 265.2 | 344.6 | 132.3 | 339.7 | 314.8 | 134.7 | 283.2 | 368.5 | 225.6
950 | 743 | 564.4 | 225.76 | 263.9004 | 330 | 307 | 325.1 | 302.2 | 714.8 | 50.3 | 19.8 | 86.1 | 5.9 | 247.5 | 12.7 | 894.4 | 815.4 | 849 | 889.2 | 847.2 | 791.9 | 735.7 | 808.9 | 786.6 | 743.6 | 265.9 | 344.9 | 132.6 | 340 | 315 | 134.9 | 283.5 | 369 | 225.9
951 | 744 | 564.3 | 225.72 | 263.8537 | 330 | 307.8 | 326.2 | 302.6 | 720.9 | 50.4 | 19.8 | 86.1 | 6.7 | 261.5 | 11.4 | 894.1 | 813.5 | 847.7 | 888.8 | 836.5 | 792.1 | 735.7 | 811.7 | 786.6 | 741.3 | 266.7 | 345.5 | 132.8 | 340.6 | 315.4 | 135.2 | 283.8 | 369.5 | 226.2
952 | 745 | 564.3 | 225.72 | 263.8537 | 330.4 | 308.3 | 327.2 | 303.6 | 715.7 | 50.4 | 19.8 | 86.1 | 6.7 | 260.4 | 11.3 | 894.6 | 812.2 | 844.9 | 888.9 | 829.1 | 792.6 | 735.1 | 811.1 | 787.2 | 740.2 | 267.4 | 345.7 | 133.1 | 341.2 | 315.9 | 135.5 | 284 | 370.1 | 226.5
953 | 746 | 563.9 | 225.56 | 263.6666 | 331.5 | 309.5 | 328.3 | 304 | 707 | 50.5 | 19.8 | 86.1 | 6.1 | 254.8 | 11.4 | 894.4 | 812.2 | 845.7 | 889.2 | 825.6 | 793.1 | 733.4 | 809.4 | 788.2 | 737.8 | 268.2 | 346.2 | 133.4 | 341.7 | 316.1 | 135.8 | 284.2 | 370.5 | 226.8
954 | 747 | 564.5 | 225.8 | 263.9472 | 332.3 | 309.6 | 328.6 | 304.8 | 721.5 | 50.5 | 19.8 | 86.2 | 6.3 | 261.2 | 11.7 | 894.4 | 812.7 | 847.7 | 889.2 | 824.2 | 793.2 | 735.3 | 811.1 | 789.3 | 737.4 | 268.9 | 346.7 | 133.7 | 342.5 | 316.5 | 136.2 | 284.4 | 371 | 227.1
955 | 748 | 564.5 | 225.8 | 263.9472 | 333.1 | 309.8 | 328.9 | 306.1 | 718.3 | 50.6 | 19.8 | 86.2 | 6.4 | 256.5 | 10.8 | 894.6 | 813.6 | 848.3 | 889.5 | 824.4 | 793.3 | 736.6 | 811.8 | 789.8 | 736.8 | 269.6 | 346.4 | 134 | 343.1 | 316.9 | 136.5 | 284.7 | 371.5 | 227.5
956 | 749 | 565 | 226 | 264.181 | 333.6 | 309.7 | 329.6 | 306.4 | 718.8 | 50.6 | 19.8 | 86.2 | 6.3 | 244 | 10 | 894.6 | 813.5 | 848.8 | 890.2 | 821.9 | 793.5 | 734.8 | 812.5 | 790.2 | 735.4 | 270.4 | 346.1 | 134.3 | 343.5 | 317.3 | 136.7 | 285 | 372 | 227.8
957 | 750 | 564.8 | 225.92 | 264.0875 | 333.5 | 309 | 330 | 306.9 | 720.2 | 50.6 | 19.8 | 86.2 | 5.9 | 259.6 | 9.7 | 894.1 | 815.2 | 850.6 | 890.1 | 830.7 | 793.4 | 735.8 | 812.4 | 790 | 735.4 | 271.1 | 346 | 134.6 | 343.9 | 317.6 | 136.9 | 285.2 | 372.5 | 228.1
958 | 751 | 564.5 | 225.8 | 263.9472 | 333.6 | 308.7 | 330.2 | 307.1 | 713 | 50.6 | 19.8 | 86.2 | 5.7 | 248.8 | 9.6 | 893.2 | 816.9 | 850.9 | 889.3 | 842 | 793.2 | 738.3 | 812 | 789.2 | 737.9 | 271.8 | 346.1 | 134.8 | 344.1 | 317.6 | 137.2 | 285.5 | 373 | 228.4
959 | 752 | 564 | 225.6 | 263.7134 | 333.5 | 309 | 330.1 | 306.6 | 715.3 | 50.6 | 19.8 | 86.2 | 6.2 | 260.2 | 11.9 | 892 | 817.9 | 850.9 | 888.4 | 848.2 | 792.9 | 739.8 | 812.2 | 788.3 | 741.3 | 272.5 | 346.6 | 135.1 | 344.3 | 317.7 | 137.6 | 285.7 | 373.3 | 228.7
960 | 753 | 564.1 | 225.64 | 263.7602 | 333.3 | 308.9 | 330.2 | 306.3 | 717.5 | 50.6 | 19.8 | 86.3 | 5 | 250.7 | 14.6 | 890.7 | 820.3 | 849.5 | 887.3 | 853.4 | 792.8 | 742.8 | 812.3 | 787.4 | 745.1 | 273.2 | 346.8 | 135.4 | 344.3 | 317.8 | 137.8 | 286 | 373.7 | 228.9
961 | 754 | 564.3 | 225.72 | 263.8537 | 333.8 | 309.2 | 328.9 | 306.1 | 710.9 | 50.7 | 19.8 | 86.4 | 6.1 | 248.4 | 15.3 | 889.7 | 822.8 | 845.2 | 887 | 864.4 | 792.7 | 746.3 | 810.7 | 786.8 | 749.3 | 273.9 | 346.8 | 135.7 | 344.5 | 318 | 138.1 | 286.2 | 374.2 | 229.2
962 | 755 | 564.6 | 225.84 | 263.9939 | 333.4 | 309.1 | 329 | 305.9 | 673 | 50.7 | 19.8 | 86.5 | 6.6 | 253.7 | 14.5 | 888.8 | 824.1 | 842.4 | 886.9 | 871.9 | 792.6 | 747.6 | 803.6 | 786 | 750.3 | 274.5 | 346.9 | 136 | 344.6 | 318.5 | 138.3 | 286.5 | 374.6 | 229.5
963 | 756 | 564.5 | 225.8 | 263.9472 | 332.4 | 309.7 | 329.6 | 304.6 | 649.7 | 50.8 | 19.8 | 86.5 | 6.1 | 261 | 13.5 | 888.2 | 826.6 | 847.4 | 886.7 | 874.1 | 792.5 | 749.2 | 804.5 | 785.5 | 752.4 | 275.1 | 346.8 | 136.3 | 344.4 | 318.8 | 138.6 | 286.6 | 375.3 | 229.8
964 | 757 | 564.9 | 225.96 | 264.1342 | 332.3 | 309.8 | 329.7 | 303.7 | 648.3 | 50.9 | 19.8 | 86.5 | 6.1 | 255.1 | 13.4 | 888.2 | 828.7 | 849.9 | 886.8 | 876.7 | 792.4 | 748.3 | 804.4 | 784.9 | 754.7 | 275.7 | 346.8 | 136.6 | 344.1 | 318.9 | 138.8 | 286.8 | 375.8 | 230.1
965 | 758 | 564.8 | 225.92 | 264.0875 | 332.6 | 309.5 | 328.1 | 303.2 | 639.1 | 50.8 | 19.8 | 86.6 | 6.7 | 253.9 | 14 | 888.2 | 830.1 | 851.8 | 887.2 | 875.5 | 792.6 | 747.5 | 803.3 | 784.5 | 753.7 | 276.3 | 346.2 | 136.8 | 343.5 | 319.1 | 139.1 | 286.9 | 376.2 | 230.4
966 | 759 | 564.7 | 225.88 | 264.0407 | 332.4 | 310.1 | 326.2 | 301.9 | 636.6 | 50.6 | 19.8 | 86.6 | 7 | 243.7 | 13.8 | 888.2 | 832 | 853.4 | 887.6 | 875.8 | 792.6 | 747.7 | 805.2 | 784.4 | 755.9 | 276.8 | 346 | 137.1 | 342.9 | 318.8 | 139.4 | 287 | 376.6 | 230.6
967 | 760 | 564.6 | 225.84 | 263.9939 | 332.3 | 310.3 | 325.7 | 300.9 | 655.6 | 50.5 | 19.8 | 86.7 | 6.7 | 247.4 | 12.7 | 888.3 | 832.3 | 854.1 | 887.7 | 877.7 | 792.5 | 748.4 | 806.6 | 784 | 758.1 | 277.3 | 345.6 | 137.4 | 342.4 | 318.3 | 139.6 | 287.2 | 377.1 | 230.8
968 | 761 | 564.7 | 225.88 | 264.0407 | 332.9 | 310.9 | 326.1 | 299.8 | 672 | 50.4 | 19.8 | 86.7 | 6.4 | 267.3 | 10.5 | 888.6 | 832.1 | 852.5 | 887.9 | 879.4 | 792.5 | 748.4 | 808.2 | 783.8 | 757.8 | 277.8 | 344.8 | 137.7 | 342.1 | 317.8 | 139.9 | 287.2 | 377.4 | 231.1
969 | 762 | 563.8 | 225.52 | 263.6199 | 333.4 | 311.8 | 326.5 | 298.4 | 669.6 | 50.3 | 19.8 | 86.8 | 6 | 267.4 | 11.8 | 889.1 | 833.3 | 851.7 | 888.3 | 884.4 | 792.4 | 745.7 | 809.6 | 783.4 | 756.7 | 278.3 | 344.4 | 138 | 341.9 | 317.4 | 140.1 | 287.3 | 377.8 | 231.4
970 | 763 | 564.6 | 225.84 | 263.9939 | 332.9 | 312.9 | 325.5 | 297.2 | 676 | 50.3 | 19.8 | 86.9 | 6.3 | 267.1 | 13.7 | 889.6 | 833.6 | 852.8 | 888.9 | 882.8 | 792.3 | 744.8 | 811.1 | 783.1 | 754 | 278.8 | 344.5 | 138.2 | 341.9 | 317.2 | 140.4 | 287.4 | 378.2 | 231.6
971 | 764 | 564.7 | 225.88 | 264.0407 | 333 | 313.4 | 324.5 | 296.3 | 676.7 | 50.4 | 19.8 | 86.9 | 5.2 | 266.7 | 13.7 | 890.1 | 833.8 | 852.7 | 889.5 | 884.9 | 792.1 | 745.7 | 810.3 | 782.5 | 755 | 279.3 | 344.7 | 138.5 | 341.4 | 317.4 | 140.6 | 287.5 | 378.6 | 231.9
972 | 765 | 564 | 225.6 | 263.7134 | 333.8 | 312.4 | 323 | 296.1 | 690.1 | 50.4 | 19.8 | 86.9 | 5 | 269.9 | 13.1 | 890.5 | 834.6 | 855.3 | 889.9 | 884.4 | 791.8 | 747.2 | 811.5 | 782.2 | 756.7 | 279.8 | 345 | 138.8 | 340.9 | 317.6 | 140.8 | 287.7 | 379.1 | 232.1
973 | 766 | 564.9 | 225.96 | 264.1342 | 332.3 | 311.7 | 321.7 | 295.9 | 688.3 | 50.5 | 19.8 | 86.9 | 5.1 | 269.2 | 13.3 | 891 | 836 | 858.5 | 890.6 | 887.5 | 791.6 | 747 | 811.4 | 781.8 | 760 | 280.2 | 345.2 | 139.1 | 340.4 | 317.5 | 141.1 | 287.8 | 379.5 | 232.4
974 | 767 | 563.7 | 225.48 | 263.5731 | 331 | 310.8 | 321 | 296.4 | 675.5 | 50.6 | 19.8 | 86.9 | 6.2 | 265.8 | 13 | 891.4 | 835.2 | 862 | 890.7 | 887.2 | 791.4 | 747.2 | 810.9 | 781.3 | 761 | 280.7 | 345.4 | 139.3 | 340.7 | 317.4 | 141.4 | 287.9 | 379.9 | 232.6
975 | 768 | 564.8 | 225.92 | 264.0875 | 331.6 | 310 | 320.7 | 297.2 | 665.2 | 50.8 | 19.8 | 86.9 | 6.4 | 261.8 | 12.8 | 891.5 | 834.1 | 862.9 | 890.5 | 882.8 | 791.3 | 747.9 | 810.6 | 780.8 | 763.1 | 281.2 | 345.6 | 139.6 | 340.4 | 317.3 | 141.7 | 288.1 | 380.3 | 232.9
976 | 769 | 564.7 | 225.88 | 264.0407 | 331.8 | 309.1 | 320 | 297.6 | 687.1 | 50.9 | 19.8 | 87 | 6 | 261.4 | 14.1 | 891.7 | 834.3 | 862.9 | 890.4 | 890.1 | 791.1 | 748.5 | 809.8 | 780.6 | 765.2 | 281.7 | 345.8 | 139.9 | 340.2 | 317.1 | 141.9 | 288.2 | 380.6 | 233.1
977 | 770 | 564.9 | 225.96 | 264.1342 | 331.7 | 308.3 | 321 | 297.2 | 694.5 | 50.8 | 19.8 | 87.1 | 5.9 | 262 | 15 | 892.2 | 833.7 | 863.7 | 891.1 | 890.4 | 791 | 747.8 | 809.9 | 780.1 | 764.2 | 282.2 | 345.7 | 140.2 | 340.2 | 317 | 142 | 288.3 | 381 | 233.4
978 | 771 | 563.2 | 225.28 | 263.3393 | 332.4 | 307.8 | 321.2 | 297.4 | 681.9 | 50.7 | 19.8 | 87.2 | 5.5 | 257.6 | 14.2 | 892.5 | 833.5 | 864.3 | 891.2 | 891.3 | 790.9 | 747.4 | 810.1 | 779.7 | 764.5 | 282.7 | 345.2 | 140.4 | 340.3 | 317.2 | 142.3 | 288.4 | 381.4 | 233.6
979 | 772 | 563.3 | 225.32 | 263.3861 | 332.8 | 307 | 321 | 298.2 | 684 | 50.8 | 19.8 | 87.2 | 4.8 | 268.4 | 13.7 | 893.1 | 833.3 | 863.5 | 891.5 | 893.4 | 790.8 | 747.6 | 810 | 779.5 | 763.8 | 283.1 | 344.9 | 140.7 | 340 | 317.1 | 142.5 | 288.5 | 381.7 | 233.9
980 | 773 | 562.7 | 225.08 | 263.1056 | 334.1 | 307 | 320 | 298.2 | 692.4 | 50.9 | 19.8 | 87.1 | 4.9 | 271.3 | 13.3 | 894 | 831.9 | 865.9 | 892.4 | 886.5 | 790.9 | 744.5 | 811.6 | 780 | 760.9 | 283.6 | 345 | 141 | 340.1 | 316.8 | 142.8 | 288.6 | 382.1 | 234.1
981 | 774 | 563.5 | 225.4 | 263.4796 | 334 | 306.8 | 319.5 | 297.9 | 689.5 | 50.9 | 19.8 | 87 | 5.5 | 261.5 | 11.8 | 895 | 830.1 | 865.4 | 893.1 | 871.6 | 791 | 740.6 | 813.3 | 780.5 | 756.9 | 284.1 | 345.5 | 141.2 | 339.9 | 316.5 | 143.1 | 288.7 | 382.5 | 234.4
982 | 775 | 563.6 | 225.44 | 263.5264 | 334 | 307.1 | 318.8 | 297.7 | 695.7 | 51 | 19.8 | 87.1 | 6.2 | 274.2 | 11.6 | 896.1 | 827.8 | 860.8 | 893.3 | 858.8 | 791 | 738.8 | 813.7 | 781.3 | 754.7 | 284.6 | 346.2 | 141.5 | 339.9 | 316.1 | 143.3 | 288.8 | 382.9 | 234.6
983 | 776 | 563.4 | 225.36 | 263.4329 | 334.7 | 307.9 | 319 | 298.6 | 696.1 | 51.1 | 19.8 | 87.2 | 5.8 | 266 | 12.7 | 896.8 | 826.4 | 863 | 894 | 852.9 | 791.2 | 736.7 | 813.8 | 782.2 | 753.2 | 285.1 | 346.7 | 141.8 | 340.2 | 316.1 | 143.6 | 288.9 | 383.3 | 234.9
984 | 777 | 562.9 | 225.16 | 263.1991 | 335.8 | 308 | 320.2 | 298.8 | 703.3 | 51.2 | 19.8 | 87.2 | 5.4 | 259.3 | 12.4 | 897.6 | 825.4 | 864.6 | 894.2 | 852.5 | 791.3 | 737.6 | 812.3 | 782.7 | 751.7 | 285.5 | 347.2 | 142 | 340.8 | 316.1 | 143.9 | 289.1 | 383.6 | 235.2
985 | 778 | 563 | 225.2 | 263.2458 | 335.8 | 307.9 | 321.5 | 299.6 | 718.5 | 51.3 | 19.8 | 87.2 | 6 | 261 | 12.5 | 897.8 | 825 | 865.3 | 894.5 | 857.3 | 791.1 | 741.2 | 813.6 | 783 | 752.2 | 286 | 347.4 | 142.3 | 341.3 | 316.3 | 144.2 | 289.2 | 384 | 235.5
986 | 779 | 565.1 | 226.04 | 264.2277 | 336.3 | 307.9 | 322.1 | 299.9 | 726.4 | 51.3 | 19.8 | 87.2 | 6.5 | 262.1 | 12.6 | 898.2 | 824.2 | 864.3 | 894.1 | 863.1 | 791.1 | 743.1 | 813.3 | 782.9 | 753 | 286.6 | 347.7 | 142.6 | 342 | 316.3 | 144.5 | 289.5 | 384.5 | 235.7
987 | 780 | 564.4 | 225.76 | 263.9004 | 336.9 | 308.7 | 323.2 | 300.4 | 730.8 | 51.4 | 19.8 | 87.3 | 6.4 | 259.6 | 12.3 | 898.4 | 824.2 | 863.1 | 894 | 870 | 790.9 | 745.6 | 813.5 | 782.7 | 754.1 | 287.1 | 347.9 | 142.9 | 342.3 | 316.4 | 144.7 | 289.8 | 384.9 | 236
988 | 781 | 563.2 | 225.28 | 263.3393 | 337.3 | 309.3 | 324.8 | 301.2 | 725.5 | 51.4 | 19.8 | 87.2 | 6.3 | 263.6 | 11.7 | 898.7 | 825.7 | 862.4 | 894.4 | 874.8 | 790.6 | 746.1 | 814.1 | 782.1 | 754.9 | 287.6 | 348.2 | 143.1 | 342 | 316.7 | 144.9 | 290 | 385.3 | 236.3
989 | 782 | 563.8 | 225.52 | 263.6199 | 338.7 | 309 | 325.1 | 301.5 | 720.2 | 51.5 | 19.8 | 87.1 | 6.4 | 253.9 | 11.8 | 899 | 826.9 | 862 | 894.3 | 877.4 | 790.6 | 748.5 | 814.8 | 782.4 | 755 | 288.1 | 348.9 | 143.4 | 341.8 | 317.4 | 145.2 | 290.2 | 385.7 | 236.6
990 | 783 | 564.2 | 225.68 | 263.8069 | 337.7 | 308.2 | 323.9 | 302 | 717.6 | 51.5 | 19.7 | 87.1 | 5.5 | 259.1 | 11.7 | 899.1 | 827.8 | 861.4 | 894.9 | 880.4 | 790.7 | 750 | 816.3 | 782.6 | 756.1 | 288.6 | 349.3 | 143.7 | 341.6 | 318.1 | 145.4 | 290.4 | 386.1 | 236.9
991 | 784 | 564.8 | 225.92 | 264.0875 | 336.9 | 308.1 | 324 | 302.6 | 708.5 | 51.6 | 19.8 | 87.1 | 5.5 | 253.5 | 11.1 | 899.2 | 828.8 | 861.2 | 894.8 | 878.5 | 790.6 | 750.5 | 815.4 | 782.5 | 757.2 | 289.2 | 349.4 | 143.9 | 341.4 | 318.6 | 145.7 | 290.5 | 386.5 | 237.1
992 | 785 | 564.8 | 225.92 | 264.0875 | 338 | 308.5 | 323.3 | 302.3 | 699.1 | 51.6 | 19.8 | 87.2 | 5.4 | 249.8 | 10.7 | 899.2 | 830.6 | 861.5 | 894.6 | 885.2 | 790.5 | 750.9 | 815.3 | 782 | 759.5 | 289.7 | 349.2 | 144.2 | 341.7 | 319 | 146 | 290.7 | 386.9 | 237.4
993 | 786 | 564.7 | 225.88 | 264.0407 | 338.9 | 308.9 | 322.1 | 302.2 | 708 | 51.6 | 19.7 | 87.3 | 5.6 | 250.7 | 10.3 | 899.1 | 829.7 | 861.5 | 894.1 | 888.2 | 790.5 | 752.7 | 816.3 | 782 | 760.3 | 290.2 | 348.5 | 144.4 | 342 | 319.3 | 146.2 | 290.8 | 387.3 | 237.7
994 | 787 | 564.8 | 225.92 | 264.0875 | 339.5 | 309.1 | 323.2 | 302.1 | 708.5 | 51.6 | 19.7 | 87.4 | 5 | 263.2 | 10.4 | 899 | 828.6 | 863.6 | 893.6 | 889.6 | 790.5 | 753.2 | 817.6 | 782.2 | 760.7 | 290.7 | 348.4 | 144.7 | 342.1 | 319.3 | 146.5 | 290.9 | 387.7 | 237.9
995 | 788 | 564.5 | 225.8 | 263.9472 | 340.4 | 309.3 | 324.6 | 301.8 | 727.1 | 51.6 | 19.7 | 87.4 | 4.9 | 255.9 | 9.6 | 898.9 | 827.3 | 864.2 | 893.5 | 888.5 | 790.4 | 755.3 | 816.7 | 782.5 | 760.2 | 291.1 | 348.8 | 145 | 342.6 | 319.4 | 146.8 | 291.1 | 388.1 | 238.2
996 | 789 | 565 | 226 | 264.181 | 341.2 | 309.6 | 324.8 | 301.7 | 715.9 | 51.5 | 19.7 | 87.4 | 5.1 | 262.1 | 9.2 | 898.7 | 827.6 | 864.5 | 893.2 | 883.1 | 790.1 | 756.9 | 816.6 | 782.2 | 763.1 | 291.6 | 349 | 145.3 | 343 | 319.4 | 147.1 | 291.3 | 388.5 | 238.5
997 | 790 | 564.4 | 225.76 | 263.9004 | 341.6 | 309.6 | 324.1 | 301.8 | 690.8 | 51.5 | 19.7 | 87.5 | 4.4 | 263.3 | 8.7 | 898.4 | 828 | 862.9 | 892.7 | 880.3 | 789.9 | 758.8 | 815.2 | 781.9 | 766.6 | 292.1 | 348.8 | 145.5 | 343.2 | 319.6 | 147.4 | 291.6 | 389 | 238.7
998 | 791 | 564.1 | 225.64 | 263.7602 | 342.2 | 309.4 | 324.3 | 301.7 | 681.4 | 51.5 | 19.7 | 87.6 | 4.5 | 266.8 | 8.3 | 898.3 | 829.7 | 861.2 | 892.7 | 883.4 | 790 | 758.9 | 815.4 | 782.2 | 768.3 | 292.6 | 348.5 | 145.8 | 343.3 | 319.8 | 147.6 | 291.8 | 389.3 | 239
999 | 792 | 564 | 225.6 | 263.7134 | 342.7 | 309.2 | 324.6 | 301 | 694.7 | 51.5 | 19.7 | 87.6 | 5.2 | 263.4 | 7.8 | 898.6 | 830.5 | 862.2 | 893 | 888.1 | 790.1 | 759.2 | 815.9 | 782.4 | 767.8 | 293.1 | 347.9 | 146 | 343.4 | 320.7 | 147.7 | 292 | 389.7 | 239.3
1000 | 793 | 564 | 225.6 | 263.7134 | 343.2 | 309.9 | 324.4 | 300.4 | 696.6 | 51.4 | 19.7 | 87.6 | 5.7 | 263.6 | 7.6 | 898.9 | 830.8 | 862.5 | 893.5 | 896.5 | 790.1 | 758.6 | 817.7 | 782.5 | 768.5 | 293.6 | 347.5 | 146.3 | 343.2 | 321.6 | 147.9 | 292.4 | 390 | 239.5
1001 | 794 | 564.1 | 225.64 | 263.7602 | 343.8 | 309.4 | 325.5 | 299.6 | 679 | 51.4 | 19.7 | 87.6 | 5.8 | 257 | 7.1 | 899.3 | 831.7 | 861.3 | 894 | 898.2 | 790.4 | 756.6 | 818.1 | 782.8 | 768.7 | 294.1 | 347.2 | 146.6 | 342.8 | 321.3 | 148.2 | 292.6 | 390.4 | 239.8
1002 | 795 | 564 | 225.6 | 263.7134 | 344.3 | 309 | 326 | 299.3 | 659.6 | 51.3 | 19.7 | 87.6 | 5.5 | 269.9 | 6.9 | 899.6 | 832.4 | 859.7 | 894.2 | 893.5 | 790.5 | 754.7 | 818 | 782.9 | 770.1 | 294.6 | 347.3 | 146.8 | 342.4 | 321.1 | 148.5 | 292.7 | 390.7 | 240
1003 | 796 | 563.8 | 225.52 | 263.6199 | 344.4 | 308.5 | 325.2 | 299.4 | 652.3 | 51.3 | 19.7 | 87.7 | 5.2 | 265.2 | 7.3 | 899.9 | 832.8 | 856.8 | 894.3 | 899.1 | 790.7 | 750.8 | 817.4 | 783.2 | 770.6 | 295.1 | 347.2 | 147.1 | 342.3 | 321.3 | 148.7 | 292.7 | 391 | 240.3
1004 | 797 | 563.4 | 225.36 | 263.4329 | 344.8 | 308.2 | 325.4 | 299.3 | 644.7 | 51.3 | 19.7 | 87.7 | 5.1 | 265.2 | 7.4 | 900.2 | 832.1 | 849.2 | 894.7 | 900.1 | 791 | 744.7 | 816.4 | 783.9 | 769.3 | 295.5 | 347 | 147.4 | 342.5 | 321.4 | 148.9 | 292.8 | 391.2 | 240.5
1005 | 798 | 564.6 | 225.84 | 263.9939 | 345.6 | 307.7 | 325.2 | 298.6 | 641.7 | 51.4 | 19.7 | 87.8 | 5.1 | 257.2 | 7.1 | 900.1 | 831.2 | 843.3 | 894.7 | 894.7 | 791.2 | 744.1 | 814.1 | 784.6 | 771.2 | 296 | 346.8 | 147.6 | 342.2 | 321.8 | 149.1 | 293 | 391.5 | 240.8
1006 | 799 | 564.5 | 225.8 | 263.9472 | 346.9 | 307.7 | 324.9 | 299.1 | 628.2 | 51.3 | 19.7 | 87.8 | 5.1 | 261 | 6.7 | 900.1 | 832.4 | 843.6 | 894.8 | 890.9 | 791.4 | 745.6 | 812.6 | 785 | 773.6 | 296.4 | 346.6 | 147.9 | 341.7 | 321.6 | 149.4 | 293.2 | 391.7 | 241
1007 | 800 | 563.5 | 225.4 | 263.4796 | 347.6 | 308.4 | 324.8 | 299.3 | 631.3 | 51.1 | 19.7 | 87.9 | 5.3 | 256 | 6.6 | 900.2 | 834.4 | 847.9 | 894.7 | 895.3 | 791.6 | 746.3 | 814.6 | 785.2 | 775.1 | 296.9 | 346.7 | 148.1 | 341.2 | 321.2 | 149.6 | 293.3 | 392 | 241.3
1008 | 801 | 564.6 | 225.84 | 263.9939 | 348.8 | 308.7 | 325.2 | 299 | 644.4 | 51.1 | 19.7 | 88 | 5 | 262.1 | 6.9 | 900.3 | 835.6 | 849.9 | 894.6 | 895.3 | 791.6 | 747.6 | 816.8 | 785.2 | 775.2 | 297.3 | 347.2 | 148.4 | 340.7 | 321.2 | 149.9 | 293.4 | 392.3 | 241.5
1009 | 802 | 564.2 | 225.68 | 263.8069 | 349.1 | 308.9 | 326.5 | 299.2 | 666.2 | 51.1 | 19.7 | 88.1 | 5.3 | 263.9 | 7 | 900.2 | 834.4 | 846.5 | 894.3 | 894.9 | 791.7 | 749 | 819.2 | 785.4 | 775.2 | 297.7 | 347.4 | 148.6 | 340.5 | 321.5 | 150.2 | 293.5 | 392.6 | 241.7
1010 | 803 | 565 | 226 | 264.181 | 348.6 | 309.2 | 327.4 | 299.6 | 673.1 | 51 | 19.7 | 88.1 | 4.8 | 267.4 | 7.2 | 900.2 | 834 | 846.9 | 894.2 | 898.4 | 791.8 | 748.9 | 819.5 | 785.6 | 776 | 298.1 | 347.1 | 148.9 | 340.3 | 321.8 | 150.4 | 293.6 | 392.9 | 242
1011 | 804 | 564.5 | 225.8 | 263.9472 | 350 | 309.6 | 327.3 | 299.4 | 696.5 | 51 | 19.7 | 88.2 | 4.5 | 267.3 | 7.3 | 900.3 | 832.7 | 847.6 | 894.1 | 900.3 | 791.8 | 749.5 | 819.3 | 786.4 | 774.1 | 298.5 | 347.4 | 149.1 | 340.5 | 321.7 | 150.7 | 293.7 | 393.2 | 242.2
1012 | 805 | 564.6 | 225.84 | 263.9939 | 351.1 | 309.9 | 326.2 | 299.5 | 720.7 | 51 | 19.7 | 88.2 | 5.4 | 267.1 | 7.2 | 900.2 | 832.5 | 850.3 | 894.2 | 900.2 | 791.6 | 749.4 | 820.1 | 787.1 | 771.4 | 298.9 | 347.9 | 149.4 | 340.8 | 321.8 | 151.1 | 293.8 | 393.6 | 242.4
1013 | 806 | 564.5 | 225.8 | 263.9472 | 352 | 310.4 | 326.1 | 299.9 | 718.4 | 51.1 | 19.7 | 88.3 | 5 | 273.9 | 6.9 | 899.8 | 832.2 | 853 | 894 | 899.5 | 791.4 | 751.3 | 821.4 | 787.3 | 771.2 | 299.4 | 348.4 | 149.6 | 341.1 | 321.9 | 151.5 | 294 | 394 | 242.7
1014 | 807 | 564.7 | 225.88 | 264.0407 | 351.9 | 311.2 | 326.8 | 300.7 | 704.6 | 51.1 | 19.7 | 88.3 | 4.9 | 271.2 | 6.7 | 899.3 | 833.8 | 857.8 | 893.6 | 901.6 | 791.2 | 751.5 | 823.3 | 786.7 | 772.6 | 299.8 | 349 | 149.9 | 341.5 | 321.9 | 151.9 | 294.2 | 394.4 | 243
1015 | 808 | 564.9 | 225.96 | 264.1342 | 352.3 | 311.7 | 326.4 | 300.9 | 694.8 | 51.2 | 19.7 | 88.4 | 5.5 | 283.4 | 6.9 | 899.3 | 835.7 | 860.6 | 893.8 | 906.2 | 791 | 750.3 | 822.6 | 786.2 | 772.8 | 300.3 | 349.4 | 150.2 | 341.7 | 321.8 | 152.1 | 294.4 | 394.8 | 243.2
1016 | 809 | 564.9 | 225.96 | 264.1342 | 352.5 | 312.3 | 326.6 | 300.9 | 684.1 | 51.3 | 19.7 | 88.5 | 4.6 | 282.3 | 8.2 | 899.3 | 836.3 | 859.4 | 894.2 | 906.2 | 790.9 | 750.3 | 823.3 | 785.9 | 772.6 | 300.7 | 349.6 | 150.4 | 341.9 | 321.7 | 152.4 | 294.6 | 395.2 | 243.5
1017 | 810 | 564.3 | 225.72 | 263.8537 | 352.7 | 312.8 | 326.9 | 301.1 | 664.9 | 51.4 | 19.7 | 88.5 | 5.1 | 283.8 | 8.7 | 899.3 | 837.8 | 858.7 | 894.2 | 905.4 | 791 | 752.1 | 822.8 | 786 | 774.8 | 301.1 | 349.4 | 150.7 | 342.3 | 321.9 | 152.6 | 294.8 | 395.5 | 243.7
1018 | 811 | 565 | 226 | 264.181 | 354.2 | 313.3 | 326.4 | 300.9 | 662.2 | 51.5 | 19.7 | 88.5 | 5.7 | 288.1 | 8.6 | 899.6 | 838 | 857.5 | 894.3 | 904 | 791 | 751.3 | 823.6 | 786.2 | 774.1 | 301.6 | 349.3 | 150.9 | 342.2 | 321.8 | 152.8 | 294.9 | 395.8 | 244
1019 | 812 | 564.9 | 225.96 | 264.1342 | 355.4 | 313.6 | 326.2 | 300.5 | 677.2 | 51.5 | 19.7 | 88.7 | 5.8 | 288.5 | 8.1 | 899.8 | 835.6 | 853.6 | 894.4 | 900.2 | 791 | 751.9 | 823.9 | 786.5 | 774.6 | 302 | 349.3 | 151.2 | 342.7 | 321.8 | 153 | 295 | 396.1 | 244.2
1020 | 813 | 564.1 | 225.64 | 263.7602 | 355.9 | 313.7 | 327.3 | 300.5 | 687.4 | 51.5 | 19.7 | 88.8 | 5.8 | 300.8 | 7.8 | 900.3 | 834.6 | 844.8 | 894.8 | 887.7 | 791.4 | 749.7 | 824 | 787 | 774.4 | 302.4 | 349.2 | 151.4 | 343.2 | 321.6 | 153.3 | 294.9 | 396.4 | 244.5
1021 | 814 | 564.1 | 225.64 | 263.7602 | 355.8 | 314 | 328.7 | 301.1 | 697.4 | 51.5 | 19.7 | 89 | 6 | 291.3 | 7.7 | 900.2 | 833.4 | 836 | 894.9 | 876 | 791.8 | 746.3 | 823.5 | 788.1 | 772.1 | 302.8 | 349.7 | 151.7 | 343.7 | 321.3 | 153.6 | 295.1 | 396.7 | 244.7
1022 | 815 | 565.3 | 226.12 | 264.3213 | 356.5 | 314.1 | 329.4 | 301.8 | 686.1 | 51.4 | 19.7 | 89.2 | 5.8 | 298.4 | 7.5 | 900.1 | 833.4 | 834.3 | 894.8 | 873.5 | 791.9 | 740.6 | 819.2 | 789.3 | 771.5 | 303.3 | 349.8 | 152 | 343.8 | 321.2 | 153.8 | 295.2 | 396.9 | 245
1023 | 816 | 564.9 | 225.96 | 264.1342 | 357.8 | 314.1 | 330.3 | 302.4 | 678.5 | 51.4 | 19.7 | 89.3 | 6.1 | 292.5 | 6.9 | 899.7 | 834.6 | 833.7 | 894.2 | 877.7 | 791.9 | 740 | 820.1 | 790 | 773 | 303.7 | 350.1 | 152.2 | 344 | 321.1 | 154.1 | 295.5 | 397.2 | 245.3
1024 | 817 | 565.4 | 226.16 | 264.368 | 358.2 | 313.8 | 330 | 302.8 | 677.4 | 51.4 | 19.7 | 89.3 | 5.5 | 293.6 | 6.4 | 899.1 | 836.6 | 834.7 | 893.5 | 881.8 | 791.8 | 739.8 | 820.9 | 790.1 | 771.6 | 304.2 | 350.5 | 152.5 | 344.6 | 321.4 | 154.3 | 295.6 | 397.4 | 245.6
1025 | 818 | 565.4 | 226.16 | 264.368 | 356.6 | 314 | 329.9 | 303.4 | 681.6 | 51.4 | 19.7 | 89.3 | 5 | 290.8 | 5.6 | 898.4 | 837.2 | 835.5 | 892.5 | 885.6 | 791.6 | 739.2 | 820.3 | 789.6 | 770.7 | 304.7 | 349.9 | 152.7 | 344.3 | 321.9 | 154.6 | 295.7 | 397.7 | 245.8
1026 | 819 | 563.8 | 225.52 | 263.6199 | 355.7 | 313.7 | 329.1 | 303.6 | 671.6 | 51.5 | 19.7 | 89.3 | 4.9 | 301.4 | 5.3 | 897.9 | 838.9 | 835.4 | 891.7 | 888.1 | 791.3 | 740.3 | 820.7 | 789.3 | 771.9 | 305.1 | 349.5 | 153 | 344 | 322.4 | 154.8 | 295.9 | 398 | 246.1
1027 | 820 | 564.8 | 225.92 | 264.0875 | 356.2 | 313.8 | 329 | 303.7 | 664.4 | 51.6 | 19.7 | 89.4 | 4.3 | 300.6 | 5.5 | 897.5 | 840.8 | 837.5 | 891.3 | 891.8 | 791.4 | 740.8 | 821.4 | 788.9 | 772.4 | 305.6 | 349.1 | 153.2 | 344.1 | 322.7 | 155 | 296.1 | 398.2 | 246.3
1028 | 821 | 565.5 | 226.2 | 264.4148 | 356.5 | 313.9 | 329.2 | 303.5 | 674.6 | 51.7 | 19.7 | 89.4 | 4.6 | 276.1 | 5.9 | 897.3 | 841.2 | 839.6 | 890.8 | 892.1 | 791.2 | 742.8 | 821.8 | 788.8 | 773.4 | 306.1 | 349.5 | 153.5 | 343.8 | 322.9 | 155.3 | 296.1 | 398.5 | 246.5
1029 | 822 | 565.2 | 226.08 | 264.2745 | 356 | 313.9 | 328.7 | 303.6 | 666.4 | 51.7 | 19.7 | 89.4 | 5.1 | 284.1 | 6.1 | 897.3 | 842.4 | 837.9 | 890.5 | 893.2 | 791.2 | 744.6 | 821.6 | 788.5 | 775.9 | 306.5 | 350.1 | 153.7 | 343 | 322.9 | 155.5 | 296.3 | 398.7 | 246.8
1030 | 823 | 565.5 | 226.2 | 264.4148 | 355.5 | 314 | 327.4 | 303 | 657.4 | 51.7 | 19.7 | 89.3 | 5 | 295.5 | 6 | 897.3 | 843.7 | 842.3 | 890.4 | 898.8 | 791.2 | 746 | 821.7 | 788.5 | 775.9 | 307 | 350.2 | 154 | 342.6 | 322.9 | 155.7 | 296.3 | 398.9 | 247
1031 | 824 | 565.1 | 226.04 | 264.2277 | 355.8 | 314.1 | 327.1 | 302.9 | 655.4 | 51.7 | 19.7 | 89.3 | 5.8 | 282.6 | 5.6 | 897.2 | 844.9 | 847.4 | 890.3 | 899.2 | 791.1 | 747.7 | 822.7 | 788.4 | 777 | 307.4 | 350 | 154.2 | 342.5 | 323.1 | 155.9 | 296.5 | 399.2 | 247.3
1032 | 825 | 564.6 | 225.84 | 263.9939 | 355.5 | 314.1 | 327.4 | 302.7 | 666.3 | 51.6 | 19.7 | 89.3 | 5.3 | 268.7 | 5.4 | 897 | 845.7 | 850.9 | 890 | 905.5 | 791.1 | 748.4 | 823.5 | 788.7 | 775.3 | 307.8 | 350.1 | 154.5 | 342.1 | 323.4 | 156.1 | 296.5 | 399.5 | 247.5
1033 | 826 | 564.7 | 225.88 | 264.0407 | 354.9 | 314.6 | 328.2 | 302.8 | 686.1 | 51.7 | 19.7 | 89.3 | 5.6 | 261 | 5 | 896.9 | 844.9 | 848.8 | 889.6 | 896.5 | 791.1 | 745.6 | 822.9 | 789.3 | 773.6 | 308.2 | 350.4 | 154.7 | 342.2 | 324 | 156.3 | 296.7 | 399.8 | 247.8
1034 | 827 | 564.3 | 225.72 | 263.8537 | 353.9 | 314.8 | 328.9 | 303.5 | 665.7 | 51.8 | 19.7 | 89.3 | 5.4 | 264.3 | 4.8 | 897.1 | 844 | 844.5 | 889.5 | 889.1 | 791.2 | 739.1 | 819.1 | 789.8 | 771.2 | 308.6 | 351.2 | 155 | 342.1 | 324.2 | 156.6 | 296.9 | 400.1 | 248
1035 | 828 | 564.8 | 225.92 | 264.0875 | 354.3 | 314.9 | 329.4 | 304 | 635.7 | 51.9 | 19.7 | 89.3 | 5.1 | 256.5 | 5 | 897.2 | 844.4 | 835.5 | 890.1 | 886.5 | 791.4 | 735.2 | 815.6 | 790.2 | 771.2 | 309 | 351.8 | 155.2 | 342.1 | 324.3 | 156.9 | 297 | 400.3 | 248.2
1036 | 829 | 564.5 | 225.8 | 263.9472 | 355.2 | 314.2 | 328.7 | 304.5 | 614.6 | 51.9 | 19.7 | 89.3 | 5 | 253.6 | 5.8 | 897 | 845.7 | 835.1 | 889.9 | 888.7 | 791.4 | 732.7 | 813 | 790.9 | 772.7 | 309.5 | 352.3 | 155.5 | 342.3 | 324.7 | 157.1 | 297.1 | 400.5 | 248.5
1037 | 830 | 564.2 | 225.68 | 263.8069 | 356.3 | 313.8 | 328.1 | 304.6 | 617.6 | 52 | 19.7 | 89.3 | 5 | 261 | 6.5 | 896.9 | 846.5 | 832.1 | 889.8 | 891.4 | 791.3 | 734.1 | 814.1 | 791 | 774.3 | 309.9 | 351.7 | 155.7 | 342.1 | 324.9 | 157.4 | 297.3 | 400.6 | 248.7
1038 | 831 | 564.2 | 225.68 | 263.8069 | 357.5 | 313.7 | 327.5 | 304.3 | 620.8 | 52.1 | 19.7 | 89.3 | 5.6 | 260.4 | 7.4 | 897.2 | 847.5 | 830.1 | 890.4 | 891.1 | 791.3 | 728.5 | 811.2 | 790.6 | 773.2 | 310.3 | 351.3 | 156 | 342.1 | 324.9 | 157.7 | 297.4 | 400.8 | 249
1039 | 832 | 564.6 | 225.84 | 263.9939 | 358.6 | 313.7 | 326.9 | 304 | 615.7 | 52.2 | 19.6 | 89.3 | 5.2 | 254.4 | 7.6 | 896.8 | 848.5 | 828.4 | 890.2 | 889 | 791.2 | 728.6 | 812.4 | 790.5 | 773.9 | 310.1 | 351 | 156.2 | 342.2 | 324.9 | 157.9 | 297.5 | 401 | 249.2
1040 | 833 | 564.9 | 225.96 | 264.1342 | 359.8 | 313.5 | 328.4 | 303.7 | 617.1 | 52.2 | 19.7 | 89.3 | 5.4 | 256.5 | 8 | 896.2 | 850.9 | 827.6 | 889.7 | 890.7 | 791.1 | 728.3 | 814.1 | 790.4 | 774.5 | 307.4 | 350.8 | 156.4 | 342.4 | 324.8 | 158.1 | 297.6 | 401.2 | 249.5
1041 | 834 | 564.8 | 225.92 | 264.0875 | 359.2 | 313.2 | 328.7 | 303 | 615.9 | 52.3 | 19.6 | 89.4 | 5.2 | 259.8 | 7.9 | 895.8 | 853.3 | 824.6 | 888.8 | 894.4 | 790.9 | 730.2 | 814.8 | 790 | 775.4 | 305.6 | 350.6 | 156.7 | 342.2 | 324.6 | 158.4 | 297.7 | 401.4 | 249.7
1042 | 835 | 564.6 | 225.84 | 263.9939 | 359.1 | 313 | 328.6 | 302.3 | 601.7 | 52.4 | 19.6 | 89.6 | 5.3 | 265.4 | 7.9 | 895.4 | 856.6 | 821.9 | 888.3 | 899.8 | 790.7 | 730.1 | 814.9 | 789.8 | 776.2 | 311 | 350.5 | 156.9 | 341.9 | 324.4 | 158.6 | 297.8 | 401.6 | 250
1043 | 836 | 563.7 | 225.48 | 263.5731 | 359.2 | 312.6 | 328 | 301.4 | 610.4 | 52.4 | 19.6 | 89.8 | 4.6 | 273.8 | 8.3 | 894.8 | 859 | 824.9 | 888.1 | 907.3 | 790.3 | 732 | 816.7 | 789.6 | 776.2 | 312.2 | 350.2 | 157.2 | 341.8 | 324.2 | 158.9 | 297.8 | 401.8 | 250.2
1044 | 837 | 564.5 | 225.8 | 263.9472 | 361.1 | 311.9 | 328.4 | 301.1 | 627.1 | 52.4 | 19.6 | 89.9 | 5 | 268.9 | 8.5 | 895.2 | 860.2 | 825.9 | 888.5 | 909.9 | 790.2 | 731 | 817.9 | 789.5 | 773.9 | 312.5 | 350 | 157.4 | 341.9 | 323.8 | 159.2 | 297.9 | 402 | 250.4
1045 | 838 | 564.5 | 225.8 | 263.9472 | 362 | 312 | 328.1 | 301.7 | 631 | 52.4 | 19.6 | 89.9 | 5.3 | 262.3 | 8.4 | 895.5 | 856 | 815.2 | 888.7 | 891.1 | 790.2 | 723.9 | 813.1 | 790.4 | 769 | 312.9 | 350.3 | 157.6 | 342.2 | 323.4 | 159.4 | 297.9 | 402.2 | 250.7
1046 | 839 | 564.7 | 225.88 | 264.0407 | 363.7 | 312.2 | 329.5 | 302 | 626.2 | 52.5 | 19.6 | 90.1 | 5.4 | 253.8 | 9 | 895.1 | 852.7 | 810.5 | 888.9 | 875.5 | 790.1 | 717.3 | 812 | 791.9 | 765.7 | 313.1 | 350.9 | 157.9 | 342.2 | 323.1 | 159.7 | 298 | 402.4 | 250.9
1047 | 840 | 564.6 | 225.84 | 263.9939 | 365.2 | 312.8 | 330 | 301.9 | 630.8 | 52.5 | 19.6 | 90.2 | 5.6 | 257.3 | 9.3 | 894.5 | 852.2 | 811.4 | 888.5 | 876.3 | 789.7 | 717.2 | 814.9 | 792.6 | 765.2 | 313.1 | 352 | 158.1 | 342.7 | 323 | 160 | 298.1 | 402.5 | 251.1
1048 | 841 | 564.4 | 225.76 | 263.9004 | 365.2 | 313.4 | 329.2 | 301.7 | 641 | 52.5 | 19.6 | 90.2 | 6 | 256.3 | 9.8 | 894.2 | 852 | 805.5 | 888.1 | 873.5 | 789.4 | 718.5 | 814.1 | 792.4 | 765.4 | 314 | 353 | 158.3 | 342.9 | 323.2 | 160.3 | 298.2 | 402.7 | 251.4
1049 | 842 | 565.8 | 226.32 | 264.555 | 365.9 | 313.8 | 328.1 | 301.9 | 636.6 | 52.4 | 19.6 | 90.3 | 5.8 | 262.9 | 10.4 | 893.9 | 850.6 | 801.2 | 888.1 | 869 | 789.3 | 715.1 | 812.3 | 793.1 | 763.3 | 314.6 | 353.6 | 158.6 | 343.2 | 323.2 | 160.5 | 298.3 | 402.9 | 251.6
1050 | 843 | 565.2 | 226.08 | 264.2745 | 366.4 | 314.1 | 329.1 | 302.6 | 638.3 | 52.4 | 19.6 | 90.4 | 5.8 | 261.2 | 9.8 | 894 | 847.6 | 799.5 | 888.3 | 857.6 | 788.9 | 713.4 | 813.3 | 793.6 | 761 | 315 | 354 | 158.8 | 343.2 | 323.2 | 160.8 | 298.4 | 403.1 | 251.9
1051 | 844 | 564.9 | 225.96 | 264.1342 | 367.1 | 314.7 | 329.9 | 303.1 | 638.3 | 52.4 | 19.6 | 90.4 | 5.4 | 263.3 | 9.7 | 893.1 | 845.5 | 803.8 | 887.9 | 848.9 | 788.6 | 713.4 | 813.7 | 794.2 | 759.4 | 315.5 | 354.4 | 159 | 343.1 | 323.2 | 161.1 | 298.6 | 403.3 | 252.1
1052 | 845 | 565.3 | 226.12 | 264.3213 | 367.2 | 315 | 329.4 | 303.5 | 648.6 | 52.4 | 19.6 | 90.5 | 5.4 | 254.1 | 10.8 | 891.9 | 845.9 | 804.2 | 886.6 | 851.6 | 788.2 | 718.4 | 816 | 794.5 | 760.9 | 315.9 | 354.9 | 159.3 | 343.2 | 323.3 | 161.3 | 298.7 | 403.4 | 252.3
1053 | 846 | 563.3 | 225.32 | 263.3861 | 367.8 | 315.3 | 330 | 303.7 | 654 | 52.4 | 19.6 | 90.5 | 5.3 | 254.6 | 10.7 | 891.6 | 846.1 | 796.2 | 886.1 | 853.9 | 787.9 | 717.2 | 814.1 | 794.3 | 760.8 | 316.4 | 355.3 | 159.5 | 343.7 | 323.3 | 161.6 | 298.8 | 403.7 | 252.6
1054 | 847 | 564.2 | 225.68 | 263.8069 | 368 | 315.4 | 330.2 | 304.2 | 655 | 52.5 | 19.6 | 90.6 | 5.9 | 259.6 | 9.9 | 891.2 | 843.8 | 788.2 | 885.9 | 848.6 | 787.7 | 713.9 | 809.1 | 794.7 | 760.8 | 316.8 | 355.6 | 159.8 | 344 | 323.6 | 161.9 | 298.9 | 403.8 | 252.8
1055 | 848 | 563.5 | 225.4 | 263.4796 | 367.7 | 315.7 | 328.7 | 305 | 645 | 52.5 | 19.6 | 90.7 | 6.1 | 253.4 | 8.9 | 890.7 | 838.9 | 776.8 | 885.6 | 836.3 | 787.5 | 708 | 800.6 | 795.4 | 759.2 | 317.3 | 355.6 | 160 | 344.2 | 323.9 | 162.2 | 299 | 404 | 253.1
1056 | 849 | 563.8 | 225.52 | 263.6199 | 366.7 | 316 | 328.8 | 305.4 | 629.2 | 52.6 | 19.6 | 90.8 | 5.5 | 248 | 8.2 | 890 | 832 | 769 | 885 | 821.9 | 787.5 | 700.2 | 790.4 | 795.9 | 755.5 | 317.7 | 356.1 | 160.3 | 344.3 | 324.2 | 162.4 | 299.1 | 404.1 | 253.3
1057 | 850 | 563.7 | 225.48 | 263.5731 | 365.7 | 316.3 | 330.7 | 305.7 | 604.5 | 52.6 | 19.6 | 90.8 | 5.6 | 252.1 | 8.4 | 887.8 | 824.1 | 756.6 | 882.9 | 805.1 | 787.1 | 690 | 779.5 | 796.4 | 750.8 | 318.2 | 357.3 | 160.5 | 344.3 | 324.3 | 162.7 | 299.2 | 404.2 | 253.5
1058 | 851 | 563.6 | 225.44 | 263.5264 | 364.1 | 316.9 | 332.4 | 305.7 | 594.6 | 52.6 | 19.6 | 90.8 | 6.1 | 251.4 | 9.5 | 886.3 | 816.7 | 748.1 | 881.1 | 788.2 | 786.7 | 680.8 | 772.9 | 796.8 | 745.5 | 318.7 | 358.2 | 160.7 | 344.2 | 324.4 | 163 | 299.3 | 404.3 | 253.8
1059 | 852 | 563.5 | 225.4 | 263.4796 | 361.8 | 317.2 | 334.3 | 306.1 | 586.3 | 52.6 | 19.6 | 90.8 | 6.6 | 247.1 | 10.3 | 884.7 | 813.3 | 745.2 | 879.9 | 784.5 | 786.3 | 676.7 | 775.5 | 796.7 | 743.7 | 319.3 | 358.4 | 161 | 344 | 324.7 | 163.3 | 299.4 | 404.4 | 254
1060 | 853 | 564 | 225.6 | 263.7134 | 362.3 | 317.6 | 335.3 | 306 | 596.8 | 52.6 | 19.6 | 90.9 | 6.3 | 241.6 | 9.9 | 882.5 | 813.4 | 748.8 | 878.4 | 790.5 | 785.4 | 677.9 | 781.1 | 795.8 | 744.4 | 319.8 | 358.2 | 161.2 | 344 | 325.1 | 163.5 | 299.5 | 404.5 | 254.2
1061 | 854 | 563.7 | 225.48 | 263.5731 | 363 | 317.4 | 335.5 | 305.6 | 609.3 | 52.7 | 19.6 | 91 | 6.5 | 235.6 | 9 | 880.7 | 811.7 | 748.2 | 877.1 | 785.5 | 784.6 | 677.3 | 783.9 | 794.8 | 742.1 | 320.3 | 358.6 | 161.5 | 344.5 | 325.4 | 163.8 | 299.7 | 404.6 | 254.5
1062 | 855 | 564.1 | 225.64 | 263.7602 | 361.7 | 317.3 | 335.7 | 305.1 | 613.8 | 52.7 | 19.6 | 91.2 | 6.3 | 246.9 | 8.2 | 879.1 | 811.1 | 751.4 | 876 | 783.8 | 784 | 677.7 | 788.5 | 794.4 | 738.3 | 320.9 | 359.1 | 161.7 | 345 | 325.7 | 164.1 | 299.8 | 404.8 | 254.7
1063 | 856 | 563.9 | 225.56 | 263.6666 | 360.6 | 317 | 335.6 | 305.1 | 624.4 | 52.8 | 19.6 | 91.2 | 6.8 | 242.5 | 7.8 | 877.6 | 811.3 | 759.2 | 875.2 | 780.3 | 783.4 | 680.8 | 793.7 | 794.5 | 736.5 | 321.4 | 359.6 | 162 | 345.4 | 325.6 | 164.4 | 299.9 | 405.1 | 255
1064 | 857 | 564.1 | 225.64 | 263.7602 | 359 | 317.4 | 335.2 | 305.1 | 630.6 | 52.9 | 19.6 | 91.3 | 6.4 | 245.4 | 6.9 | 876.6 | 814.3 | 762.4 | 874.6 | 784 | 782.6 | 687.7 | 800.9 | 795.2 | 734.8 | 321.9 | 360.1 | 162.2 | 345.7 | 325.5 | 164.7 | 300 | 405.4 | 255.2
1065 | 858 | 563.7 | 225.48 | 263.5731 | 357.6 | 318.2 | 334.5 | 305.3 | 659.5 | 52.9 | 19.6 | 91.4 | 6.3 | 258.3 | 6.3 | 875.5 | 816.5 | 761.2 | 873.5 | 789.3 | 781.8 | 698.4 | 807.5 | 795.5 | 736.9 | 322.4 | 360 | 162.4 | 346.2 | 325.7 | 165 | 300.2 | 405.9 | 255.5
1066 | 859 | 563.8 | 225.52 | 263.6199 | 357.3 | 318.9 | 335.8 | 305.7 | 681.3 | 52.9 | 19.6 | 91.5 | 6.4 | 264.8 | 6.2 | 874.4 | 813.2 | 754.7 | 872.4 | 782.3 | 781.4 | 698 | 804.2 | 795.4 | 734.9 | 322.9 | 360.9 | 162.7 | 347.6 | 326 | 165.3 | 300.3 | 406.3 | 255.7
1067 | 860 | 562.8 | 225.12 | 263.1523 | 357 | 319.2 | 337.7 | 306.1 | 667.7 | 53 | 19.6 | 91.5 | 6.1 | 257.7 | 6 | 873.1 | 811.6 | 759 | 871.4 | 774.3 | 781.2 | 695.1 | 804.6 | 795.7 | 730.9 | 323.4 | 362 | 162.9 | 348.5 | 326.1 | 165.6 | 300.4 | 406.6 | 256
1068 | 861 | 563.6 | 225.44 | 263.5264 | 357.1 | 319.6 | 339.2 | 306.6 | 648.6 | 53 | 19.6 | 91.6 | 5.4 | 254.2 | 6.3 | 872.2 | 811.9 | 758.2 | 870.5 | 773.8 | 780.9 | 696.5 | 806.1 | 796.2 | 730.7 | 323.9 | 362.2 | 163.2 | 348.8 | 326.3 | 165.9 | 300.6 | 406.9 | 256.3
1069 | 862 | 563.6 | 225.44 | 263.5264 | 357.5 | 320.4 | 339.8 | 306.4 | 666.1 | 53.1 | 19.6 | 91.7 | 4.9 | 242.9 | 6.6 | 871.2 | 812.6 | 760.4 | 869.7 | 772.4 | 780.7 | 700.2 | 810.1 | 796.8 | 730.3 | 324.5 | 362.1 | 163.4 | 349.3 | 326.5 | 166.2 | 300.7 | 407.2 | 256.5
1070 | 863 | 563.8 | 225.52 | 263.6199 | 357.5 | 321.5 | 340.4 | 306.6 | 686 | 53.1 | 19.6 | 91.8 | 5.5 | 230.8 | 8.1 | 869.6 | 817.6 | 772.3 | 868.7 | 779.6 | 780.2 | 707.9 | 815.2 | 797.5 | 731.1 | 325 | 362.3 | 163.7 | 349.9 | 326.7 | 166.5 | 300.8 | 407.5 | 256.8
1071 | 864 | 563.6 | 225.44 | 263.5264 | 357.4 | 322 | 340.5 | 307.9 | 704.1 | 53.2 | 19.6 | 91.9 | 4.9 | 235.9 | 8.4 | 868.2 | 820.9 | 782.9 | 867 | 786.7 | 779.7 | 716 | 818.4 | 797.5 | 731.2 | 325.5 | 362.1 | 163.9 | 351.2 | 327.3 | 166.8 | 301 | 407.8 | 257
1072 | 865 | 564 | 225.6 | 263.7134 | 358 | 322.3 | 340.5 | 308.2 | 708.4 | 53.3 | 19.6 | 91.8 | 5.3 | 249 | 7.7 | 867.5 | 821.8 | 783.4 | 865.8 | 791.3 | 779.5 | 719.2 | 820.8 | 797.1 | 731.8 | 326 | 362.9 | 164.2 | 352.1 | 327.4 | 167.1 | 301.2 | 408.2 | 257.3
1073 | 866 | 563.7 | 225.48 | 263.5731 | 358.6 | 322.4 | 341.2 | 308.8 | 704.1 | 53.3 | 19.6 | 91.8 | 5.1 | 240.2 | 7.4 | 867 | 825.1 | 788.3 | 865.2 | 799.8 | 779.4 | 722.8 | 821.7 | 796.9 | 734 | 326.4 | 363.9 | 164.4 | 352.5 | 327.4 | 167.4 | 301.4 | 408.5 | 257.6
1074 | 867 | 563.5 | 225.4 | 263.4796 | 359.1 | 322.1 | 342.3 | 309.6 | 708.1 | 53.3 | 19.6 | 91.7 | 4.8 | 245.6 | 7.7 | 866.3 | 829.9 | 796 | 864.4 | 808.5 | 779.1 | 727.7 | 823.6 | 796.7 | 736.9 | 326.9 | 364.5 | 164.7 | 352.6 | 327.6 | 167.7 | 301.6 | 408.8 | 257.8
1075 | 868 | 563.7 | 225.48 | 263.5731 | 359.3 | 321.9 | 342.2 | 309.6 | 706 | 53.3 | 19.6 | 91.7 | 4.8 | 248.1 | 8.6 | 865.2 | 833.9 | 801.7 | 863.1 | 815.1 | 778.8 | 730.6 | 825.5 | 795.8 | 737.5 | 327.3 | 364.3 | 164.9 | 352.5 | 327.7 | 168 | 301.8 | 409 | 258.1
1076 | 869 | 564 | 225.6 | 263.7134 | 360.2 | 321.7 | 341.7 | 310 | 689.6 | 53.3 | 19.6 | 91.6 | 4.9 | 245.5 | 10 | 865.1 | 839.2 | 797.5 | 862.2 | 823.2 | 778.8 | 732.8 | 824.9 | 794.5 | 740.1 | 327.8 | 364 | 165.2 | 352.5 | 327.8 | 168.3 | 302 | 409.3 | 258.3
1077 | 870 | 563.3 | 225.32 | 263.3861 | 360.3 | 321.3 | 342 | 310.1 | 662.6 | 53.3 | 19.6 | 91.6 | 4.7 | 234 | 10.7 | 864.3 | 843.4 | 801.4 | 861.5 | 833.5 | 778.8 | 734.2 | 824.7 | 793.6 | 743.4 | 328.2 | 363.6 | 165.4 | 352.4 | 328 | 168.6 | 302.1 | 409.5 | 258.6
1078 | 871 | 563.8 | 225.52 | 263.6199 | 360.2 | 321.6 | 341.6 | 309.9 | 672.7 | 53.3 | 19.6 | 91.5 | 5.3 | 232.7 | 10.9 | 865 | 845 | 805.4 | 861.7 | 837.3 | 779 | 735.4 | 827.5 | 793.9 | 743 | 328.6 | 363.5 | 165.7 | 351.9 | 328 | 168.9 | 302.2 | 409.7 | 258.8
1079 | 872 | 565.1 | 226.04 | 264.2277 | 361 | 322 | 341.5 | 309.9 | 694.2 | 53.3 | 19.6 | 91.3 | 4.6 | 230.6 | 10.7 | 865.5 | 844.8 | 805.8 | 861.8 | 836.2 | 779 | 736.7 | 829.8 | 794.5 | 742.5 | 328.9 | 363.9 | 165.9 | 351.6 | 327.8 | 169.2 | 302.3 | 409.9 | 259
1080 | 873 | 564.8 | 225.92 | 264.0875 | 361.3 | 322.2 | 341.5 | 309.4 | 690.3 | 53.3 | 19.6 | 91.3 | 4.7 | 229.7 | 9.8 | 865.2 | 846.5 | 812 | 861.7 | 839.9 | 779.1 | 738.4 | 830.6 | 794.4 | 743.6 | 329.3 | 364.3 | 166.2 | 351.4 | 327.7 | 169.4 | 302.4 | 410.2 | 259.3
1081 | 874 | 564.6 | 225.84 | 263.9939 | 361.3 | 322.2 | 341.7 | 308.8 | 688.4 | 53.3 | 19.6 | 91.3 | 4.5 | 235.9 | 8.6 | 864.5 | 848.1 | 810.9 | 860.4 | 847.9 | 779 | 741.4 | 830.4 | 793.8 | 747.4 | 329.6 | 364.1 | 166.4 | 351 | 327.7 | 169.7 | 302.5 | 410.4 | 259.5
1082 | 875 | 564.1 | 225.64 | 263.7602 | 361.6 | 322 | 341.3 | 308.9 | 688.1 | 53.3 | 19.6 | 91.4 | 4.3 | 231.2 | 8 | 864.7 | 850.3 | 807.7 | 860.1 | 852.7 | 779.3 | 740.7 | 829.6 | 793.2 | 748.8 | 330 | 364.2 | 166.7 | 350.7 | 327.7 | 170 | 302.6 | 410.6 | 259.7
1083 | 876 | 564.1 | 225.64 | 263.7602 | 363.4 | 321.7 | 340.9 | 309.5 | 687.9 | 53.3 | 19.6 | 91.4 | 4.5 | 231.7 | 7.3 | 864.6 | 851.1 | 809.4 | 860 | 853.3 | 779.4 | 740.3 | 830.9 | 793.6 | 750.1 | 330.3 | 364 | 167 | 350.6 | 327.6 | 170.3 | 302.8 | 410.8 | 260
1084 | 877 | 563.7 | 225.48 | 263.5731 | 364.4 | 321.3 | 340.1 | 309.4 | 693.1 | 53.3 | 19.6 | 91.4 | 5 | 241.7 | 6.7 | 864.4 | 851.2 | 812 | 859.2 | 854.3 | 779.5 | 742.9 | 831.8 | 793.9 | 752.4 | 330.7 | 363.6 | 167.2 | 350.6 | 328 | 170.6 | 302.9 | 411 | 260.2
1085 | 878 | 564.6 | 225.84 | 263.9939 | 364.9 | 321.3 | 339.2 | 309.3 | 682.1 | 53.3 | 19.6 | 91.5 | 4.7 | 234.5 | 5.8 | 864.5 | 852.7 | 803.8 | 859.3 | 856 | 779.7 | 743 | 830.6 | 793.8 | 754.8 | 331 | 363.2 | 167.5 | 350.5 | 328 | 170.9 | 303 | 411.2 | 260.4
1086 | 879 | 564.6 | 225.84 | 263.9939 | 364.9 | 321.5 | 338.2 | 309.4 | 658.1 | 53.3 | 19.6 | 91.5 | 5.1 | 243.1 | 4.9 | 864.6 | 855.4 | 801.4 | 859.4 | 861.3 | 779.9 | 738.8 | 820.1 | 794.1 | 757.4 | 331.3 | 363 | 167.7 | 350.3 | 327.8 | 171.2 | 303.2 | 411.4 | 260.6
1087 | 880 | 565.3 | 226.12 | 264.3213 | 364.2 | 321.5 | 337.7 | 309.6 | 629.9 | 53.3 | 19.6 | 91.5 | 5.4 | 262.4 | 4.3 | 865.5 | 858 | 793.5 | 859.8 | 867.6 | 780.1 | 735.7 | 811.3 | 795.4 | 759.1 | 331.6 | 362.4 | 168 | 349.9 | 327.7 | 171.4 | 303.4 | 411.5 | 260.9
1088 | 881 | 564.9 | 225.96 | 264.1342 | 363.7 | 321.2 | 337.4 | 309.7 | 607.7 | 53.3 | 19.6 | 91.4 | 5 | 262.4 | 3.8 | 865.7 | 858.4 | 789.1 | 859.6 | 864.2 | 780.3 | 734.4 | 806.3 | 796.4 | 761.5 | 331.9 | 361.6 | 168.2 | 349.6 | 327.9 | 171.7 | 303.6 | 411.6 | 261.1
1089 | 882 | 565.6 | 226.24 | 264.4615 | 364.5 | 320.9 | 337 | 309.3 | 593.9 | 53.3 | 19.6 | 91.4 | 5.6 | 249.9 | 3.5 | 866.5 | 858.8 | 781.5 | 860 | 867.9 | 780.5 | 732.4 | 807.1 | 797.1 | 762.5 | 332.1 | 360.9 | 168.5 | 349.2 | 328.1 | 172 | 303.8 | 411.7 | 261.3
1090 | 883 | 564.9 | 225.96 | 264.1342 | 365.1 | 320.2 | 336.8 | 308.7 | 599.2 | 53.3 | 19.6 | 91.3 | 5.8 | 244.5 | 3.3 | 866.7 | 853.6 | 776.1 | 860.2 | 876.9 | 780.7 | 725.7 | 803.9 | 798 | 761.1 | 332.4 | 360.1 | 168.7 | 349.1 | 328 | 172.3 | 303.8 | 411.8 | 261.5
1091 | 884 | 564.2 | 225.68 | 263.8069 | 365.1 | 318.9 | 336.7 | 308 | 589.5 | 53.2 | 19.6 | 91.3 | 5.9 | 245.8 | 3.4 | 866.6 | 850.9 | 782.1 | 860.6 | 875.7 | 780.6 | 719.8 | 804.8 | 799.6 | 759.6 | 332.6 | 359.3 | 169 | 348.4 | 328 | 172.5 | 303.9 | 411.9 | 261.8
1092 | 885 | 564.5 | 225.8 | 263.9472 | 366.5 | 317.7 | 336.6 | 307.2 | 597.8 | 53.2 | 19.6 | 91.3 | 5.7 | 247.9 | 4.1 | 866.4 | 853.1 | 792.1 | 860.7 | 879.7 | 780.3 | 723.1 | 813.1 | 799.7 | 760.5 | 332.9 | 358.9 | 169.2 | 348 | 327.8 | 172.8 | 304 | 412 | 262
1093 | 886 | 564.3 | 225.72 | 263.8537 | 368.7 | 316.9 | 336.9 | 307 | 617.6 | 53.3 | 19.6 | 91.4 | 5.5 | 270.2 | 5 | 866.5 | 856.2 | 803.1 | 860.5 | 884.9 | 780.3 | 726.6 | 818 | 799.1 | 761 | 333.1 | 358.4 | 169.5 | 347.8 | 327.4 | 173.1 | 304.1 | 412.1 | 262.2
1094 | 887 | 564.3 | 225.72 | 263.8537 | 368.8 | 317.4 | 336.7 | 306.9 | 634.3 | 53.2 | 19.6 | 91.5 | 5.8 | 274.2 | 5.8 | 867.1 | 856.6 | 810.6 | 860.8 | 884.8 | 780.3 | 729.1 | 822.3 | 798.9 | 758.9 | 333.3 | 358.4 | 169.7 | 347.5 | 327.1 | 173.4 | 304.2 | 412.3 | 262.4
1095 | 888 | 564.2 | 225.68 | 263.8069 | 369.2 | 318.2 | 336.5 | 306.4 | 644.6 | 53.1 | 19.6 | 91.5 | 5.9 | 266.6 | 6.5 | 867.7 | 857.6 | 807.3 | 861 | 882.3 | 780.2 | 730.7 | 822.4 | 798.7 | 760.1 | 333.6 | 358.6 | 170 | 347.2 | 327.2 | 173.6 | 304.3 | 412.5 | 262.6
1096 | 889 | 564.4 | 225.76 | 263.9004 | 369.7 | 318 | 335.8 | 306 | 629.8 | 53 | 19.6 | 91.6 | 6.1 | 267.8 | 6.8 | 867.2 | 859.3 | 814.4 | 860.5 | 883 | 780.1 | 733.2 | 824.3 | 798.3 | 762.3 | 333.8 | 359.1 | 170.2 | 346.8 | 327.3 | 173.9 | 304.4 | 412.7 | 262.8
1097 | 890 | 563.4 | 225.36 | 263.4329 | 369.5 | 317.9 | 335 | 305.9 | 650 | 53.1 | 19.6 | 91.6 | 6 | 274.6 | 6.5 | 868 | 862.2 | 821.1 | 860.9 | 879.6 | 780.1 | 736.4 | 828.8 | 798.7 | 760.3 | 333.9 | 359.4 | 170.5 | 346.7 | 327.2 | 174.2 | 304.5 | 412.9 | 263.1
1098 | 891 | 563.5 | 225.4 | 263.4796 | 369.5 | 318 | 335.3 | 305.8 | 658 | 53.2 | 19.6 | 91.7 | 5.8 | 281.3 | 6.2 | 869 | 861.8 | 823.7 | 861.1 | 875 | 780.3 | 737.5 | 830.5 | 799.9 | 760.6 | 333.4 | 358.8 | 170.7 | 347.2 | 326.8 | 174.5 | 304.5 | 413.1 | 263.3
1099 | 892 | 564 | 225.6 | 263.7134 | 370.9 | 318.3 | 335.8 | 306 | 669.2 | 53.3 | 19.6 | 91.7 | 5.8 | 270.4 | 6.7 | 869.7 | 859.1 | 827.2 | 861.4 | 867.3 | 780.5 | 736.7 | 830.2 | 801 | 761.1 | 231.5 | 358.4 | 171 | 347.6 | 326.9 | 174.8 | 304.6 | 413.3 | 263.5
1100 | 893 | 564 | 225.6 | 263.7134 | 370.9 | 318.8 | 335.9 | 306.1 | 674.5 | 53.4 | 19.6 | 91.8 | 5.4 | 262.9 | 7.4 | 869.6 | 859.4 | 833.9 | 861 | 865.4 | 780.6 | 735.2 | 832 | 801.2 | 759.1 | 227.7 | 358.5 | 171.2 | 347.6 | 327 | 175.1 | 304.7 | 413.6 | 263.8
1101 | 894 | 564.3 | 225.72 | 263.8537 | 371.6 | 319.7 | 336.4 | 306.4 | 681.6 | 53.4 | 19.6 | 91.8 | 5.7 | 275.2 | 7.5 | 870.1 | 862.4 | 832.9 | 861.4 | 864.3 | 780.4 | 736.7 | 834.2 | 800.7 | 757.9 | 227.8 | 359.2 | 171.5 | 347.8 | 327 | 175.4 | 304.8 | 413.8 | 264
1102 | 895 | 565 | 226 | 264.181 | 372.2 | 320.1 | 336.2 | 306.9 | 682.5 | 53.4 | 19.6 | 91.8 | 5.4 | 276.9 | 7.4 | 871 | 861.9 | 825.9 | 861.8 | 858.4 | 780.3 | 736.1 | 835.8 | 799.9 | 755.1 | 227.9 | 359.4 | 171.7 | 348.2 | 327 | 175.7 | 304.8 | 414.1 | 264.2
1103 | 896 | 565 | 226 | 264.181 | 372 | 320.9 | 335.9 | 306.8 | 683.4 | 53.3 | 19.6 | 92 | 6 | 267 | 7.1 | 871.5 | 857.7 | 814.7 | 862.1 | 850.5 | 780.4 | 733.9 | 835.5 | 800 | 753.3 | 228.3 | 360 | 172 | 348.7 | 327 | 176 | 304.9 | 414.3 | 264.4
1104 | 897 | 564.3 | 225.72 | 263.8537 | 372.7 | 321.8 | 337.1 | 307.2 | 698.4 | 53.3 | 19.6 | 92 | 5.9 | 270.7 | 6.7 | 871.7 | 853.1 | 807.7 | 862.1 | 845.3 | 780.4 | 732.7 | 835.8 | 801 | 751.6 | 228.6 | 360.4 | 172.2 | 349 | 327.3 | 176.3 | 305 | 414.6 | 264.7
1105 | 898 | 564.7 | 225.88 | 264.0407 | 372.8 | 322.4 | 339 | 307.8 | 698.5 | 53.4 | 19.5 | 92.1 | 5.7 | 273.9 | 6.5 | 871.9 | 851.2 | 811.1 | 862.1 | 839 | 780.3 | 730.6 | 835.5 | 802.1 | 748.8 | 212.1 | 309.2 | 172.5 | 349.5 | 327.7 | 176.6 | 305.2 | 414.8 | 264.9
1106 | 899 | 564.2 | 225.68 | 263.8069 | 372.3 | 323 | 339.4 | 308.6 | 690.3 | 53.5 | 19.6 | 92.1 | 5.8 | 273 | 6.5 | 871.8 | 852.7 | 813 | 862 | 839.4 | 780.3 | 733.5 | 834 | 802.5 | 750.4 | 195.9 | 262.1 | 172.7 | 350.1 | 328.4 | 176.9 | 305.4 | 415.1 | 265.2
1107 | 900 | 564.8 | 225.92 | 264.0875 | 371.6 | 323.5 | 339.8 | 309.1 | 691.9 | 53.6 | 19.6 | 92.1 | 5.9 | 269.4 | 6.5 | 872.1 | 855.1 | 806.1 | 862.3 | 844 | 780.3 | 732.5 | 831.8 | 802.9 | 750.4 | 195.7 | 260.6 | 173 | 350.4 | 329 | 177.3 | 305.6 | 415.3 | 265.4
1108 | 901 | 564.5 | 225.8 | 263.9472 | 370.2 | 323.6 | 340 | 309.2 | 681 | 53.7 | 19.5 | 92.1 | 5.8 | 267.9 | 6.8 | 872 | 852.9 | 798 | 862.5 | 843 | 780.6 | 726.1 | 826.8 | 804.3 | 748.9 | 195.7 | 259.6 | 173.2 | 350.8 | 329.4 | 177.5 | 305.7 | 415.5 | 265.6
1109 | 902 | 564.1 | 225.64 | 263.7602 | 371 | 323.9 | 338.8 | 309.3 | 666.3 | 53.7 | 19.5 | 92.2 | 5.9 | 270.3 | 6.9 | 872 | 846.3 | 786.8 | 862.8 | 829.2 | 780.7 | 719.7 | 818.6 | 806.6 | 745.5 | 195.4 | 258.1 | 173.5 | 351.8 | 329.6 | 177.8 | 305.8 | 415.6 | 265.9
1110 | 903 | 564.7 | 225.88 | 264.0407 | 372.2 | 324.2 | 339.2 | 309.4 | 655.3 | 53.7 | 19.5 | 92.3 | 5.2 | 268.6 | 6.7 | 871.8 | 840.6 | 780.8 | 863.1 | 816 | 780.8 | 713.9 | 813.5 | 809.2 | 743 | 195.3 | 257.4 | 173.8 | 352.8 | 329.8 | 178.1 | 306 | 415.8 | 266.1
1111 | 904 | 565 | 226 | 264.181 | 373.8 | 324 | 339.9 | 309.4 | 660.1 | 53.7 | 19.5 | 92.4 | 5.1 | 259.3 | 6.5 | 871.4 | 835.9 | 776.9 | 863.1 | 809.4 | 780.8 | 710.9 | 815.3 | 811.5 | 741.5 | 195 | 256.2 | 174 | 353.1 | 329.8 | 178.4 | 306.1 | 415.9 | 266.4
1112 | 905 | 564.5 | 225.8 | 263.9472 | 374.3 | 324.1 | 340.6 | 309.4 | 681 | 53.7 | 19.5 | 92.5 | 5.1 | 262.2 | 6.2 | 871.2 | 833.4 | 774.5 | 863 | 807.5 | 780.7 | 712.9 | 817.9 | 812 | 740.2 | 194.7 | 254.6 | 174.3 | 353.4 | 330 | 178.8 | 306.2 | 416.1 | 266.6
1113 | 906 | 565.1 | 226.04 | 264.2277 | 373.9 | 325.2 | 340.5 | 310 | 684.4 | 53.7 | 19.5 | 92.7 | 4.9 | 274.2 | 6.6 | 870.7 | 832.1 | 770.8 | 863 | 808.7 | 780.6 | 715.4 | 817.3 | 812 | 739.7 | 195.1 | 254.6 | 174.5 | 353.8 | 330.1 | 179.1 | 306.3 | 416.4 | 266.9
1114 | 907 | 565.6 | 226.24 | 264.4615 | 373.8 | 325.8 | 340.9 | 310.8 | 671.2 | 53.7 | 19.5 | 92.8 | 4.6 | 279.3 | 6.8 | 870.4 | 829.4 | 771.8 | 863.1 | 805.5 | 780.7 | 712 | 812.6 | 812.3 | 739.2 | 195.5 | 254.7 | 174.8 | 354.2 | 330.2 | 179.5 | 306.5 | 416.6 | 267.1
1115 | 908 | 564.6 | 225.84 | 263.9939 | 373.1 | 326.1 | 341.8 | 310.9 | 652.8 | 53.8 | 19.5 | 92.8 | 4.5 | 272 | 6.7 | 869.9 | 827.7 | 776 | 862.9 | 801.4 | 780.6 | 708.8 | 809.3 | 813.3 | 736.5 | 195.4 | 253.6 | 175.1 | 354.5 | 330.5 | 179.8 | 306.6 | 416.8 | 267.4
1116 | 909 | 564.3 | 225.72 | 263.8537 | 373.8 | 325.9 | 342.7 | 311.5 | 649.2 | 53.8 | 19.5 | 92.8 | 4.9 | 280.1 | 6.6 | 869.5 | 827.5 | 777.6 | 862.6 | 800.8 | 780.5 | 708.7 | 808.5 | 813.6 | 736.1 | 195 | 251.6 | 175.3 | 354.8 | 330.8 | 180.1 | 306.8 | 417 | 267.7
1117 | 910 | 564.8 | 225.92 | 264.0875 | 373.8 | 325.6 | 343.2 | 311.9 | 655.1 | 53.8 | 19.5 | 92.8 | 4.7 | 278 | 6.6 | 869 | 829.1 | 784.2 | 862.3 | 803.5 | 780.4 | 713.6 | 814.6 | 813.1 | 737.3 | 195.5 | 250.5 | 175.6 | 354.9 | 330.7 | 180.4 | 306.9 | 417.1 | 267.9
1118 | 911 | 563.8 | 225.52 | 263.6199 | 373.8 | 325.6 | 343.6 | 311.6 | 666.6 | 53.8 | 19.5 | 92.7 | 4.4 | 257.4 | 6.1 | 868.8 | 831.6 | 783.1 | 862 | 806.2 | 780.5 | 715.7 | 818.5 | 812.7 | 736.2 | 196.5 | 251 | 175.9 | 354.7 | 330.5 | 180.8 | 307 | 417.2 | 268.1
1119 | 912 | 564.1 | 225.64 | 263.7602 | 373.9 | 325.6 | 344.3 | 311.6 | 662.7 | 53.8 | 19.5 | 92.7 | 4.3 | 267.9 | 6.1 | 868.7 | 835.2 | 786 | 861.9 | 808.8 | 780.5 | 715.1 | 819.4 | 812.3 | 736.4 | 196.3 | 249.4 | 176.1 | 354.3 | 330.3 | 181.1 | 307.2 | 417.4 | 268.4
1120 | 913 | 564 | 225.6 | 263.7134 | 375.1 | 325.1 | 344.1 | 311.3 | 663.6 | 53.8 | 19.5 | 92.7 | 5.5 | 274.2 | 6.1 | 868.3 | 836.8 | 788.6 | 861.2 | 811.6 | 780.7 | 714.7 | 820.3 | 812.9 | 735.6 | 195.8 | 247.1 | 176.4 | 354.2 | 330.4 | 181.4 | 307.3 | 417.5 | 268.6
1121 | 914 | 563.9 | 225.56 | 263.6666 | 377.1 | 324.6 | 343.2 | 311.1 | 665.1 | 53.6 | 19.5 | 92.7 | 5.3 | 265.9 | 6.5 | 868 | 840.8 | 791.9 | 860.8 | 817.3 | 780.8 | 718.1 | 820.2 | 813.5 | 736.6 | 195.7 | 246 | 176.7 | 354.3 | 330.4 | 181.7 | 307.4 | 417.6 | 268.8
1122 | 915 | 563.9 | 225.56 | 263.6666 | 378.6 | 324.6 | 343.1 | 311.5 | 667.8 | 53.6 | 19.5 | 92.8 | 5.1 | 265.9 | 6.9 | 867.7 | 844 | 796.9 | 860.4 | 829.1 | 780.9 | 719.6 | 816.6 | 813 | 737.4 | 195.4 | 244.2 | 176.9 | 354.5 | 330.5 | 182.1 | 307.6 | 417.8 | 269.1
1123 | 916 | 565.5 | 226.2 | 264.4148 | 378.8 | 324.7 | 342.1 | 311.6 | 663.8 | 53.6 | 19.5 | 92.9 | 5.1 | 266.5 | 6.7 | 867.1 | 847.1 | 797.5 | 859.6 | 836.5 | 780.9 | 723.8 | 818.3 | 812.6 | 738.6 | 195.3 | 242.6 | 177.2 | 354.3 | 330.9 | 182.4 | 307.7 | 417.9 | 269.3
1124 | 917 | 567.8 | 227.12 | 265.4902 | 378.7 | 324.6 | 341.3 | 311.4 | 672.4 | 53.6 | 19.5 | 92.9 | 5.5 | 278.7 | 6.2 | 866.9 | 848 | 801 | 858.9 | 843.1 | 781.2 | 728.4 | 821.3 | 811.8 | 740.6 | 195 | 241 | 177.5 | 354.2 | 330.9 | 182.7 | 307.9 | 418.1 | 269.5
1125 | 918 | 567 | 226.8 | 265.1161 | 378.5 | 324.5 | 341.7 | 312 | 679.4 | 53.6 | 19.5 | 92.9 | 5.2 | 271.8 | 6.2 | 866.8 | 847.3 | 809.4 | 858.9 | 844.3 | 781.5 | 727.5 | 823 | 811.1 | 739.3 | 194.8 | 239.3 | 177.7 | 354 | 331 | 183 | 308 | 418.3 | 269.8
1126 | 919 | 566.2 | 226.48 | 264.7421 | 377.5 | 324.4 | 342.6 | 312.2 | 681 | 53.6 | 19.5 | 92.9 | 5.2 | 267.1 | 7 | 866.8 | 846.6 | 805.8 | 858.8 | 841.5 | 781.6 | 729 | 824.1 | 810.5 | 739.1 | 194.9 | 237.6 | 178 | 354 | 331.3 | 183.4 | 308.2 | 418.4 | 270
1127 | 920 | 566.6 | 226.64 | 264.9291 | 377.6 | 324.4 | 343.1 | 312.2 | 678.9 | 53.6 | 19.5 | 92.8 | 5.2 | 269.9 | 7.6 | 866.7 | 845 | 801.7 | 858.9 | 841.3 | 781.8 | 729.5 | 821 | 809.5 | 741.8 | 194.8 | 236.4 | 178.3 | 354 | 331.6 | 183.8 | 308.3 | 418.6 | 270.2
1128 | 921 | 565.9 | 226.36 | 264.6018 | 378 | 324.5 | 343 | 311.7 | 662.2 | 53.6 | 19.5 | 92.8 | 4.5 | 273 | 7.9 | 866.7 | 841.7 | 794.4 | 859.3 | 833.7 | 782.1 | 724.8 | 817.3 | 809.8 | 740.9 | 194.2 | 235.6 | 178.6 | 353.9 | 332.1 | 184 | 308.5 | 418.7 | 270.5
1129 | 922 | 564.7 | 225.88 | 264.0407 | 377.9 | 324.3 | 342.3 | 311.9 | 646.3 | 53.6 | 19.5 | 92.8 | 4.3 | 261.9 | 7.9 | 866.6 | 837.6 | 788 | 859.8 | 829.1 | 782.2 | 717.8 | 810.6 | 811.6 | 740.3 | 195 | 235.7 | 178.8 | 353.6 | 332.4 | 184.3 | 308.6 | 418.8 | 270.7
1130 | 923 | 564.4 | 225.76 | 263.9004 | 380 | 324 | 342.6 | 311.5 | 646.4 | 53.6 | 19.5 | 92.8 | 4.8 | 261.3 | 7.8 | 866.7 | 833.2 | 778.8 | 860.4 | 821.4 | 782.4 | 714.6 | 806.9 | 814.1 | 739.7 | 194 | 234.3 | 179.1 | 353.3 | 332.4 | 184.6 | 308.7 | 418.9 | 270.9
1131 | 924 | 565.6 | 226.24 | 264.4615 | 381.3 | 324.2 | 342.2 | 311.1 | 634.4 | 53.5 | 19.5 | 92.9 | 4.8 | 258.6 | 7.5 | 866.3 | 827.4 | 773.7 | 860.5 | 809.2 | 782.6 | 706.9 | 802.2 | 816.4 | 736.7 | 193.2 | 232.5 | 179.4 | 353.2 | 332.8 | 184.9 | 308.7 | 419 | 271.1
1132 | 925 | 565.3 | 226.12 | 264.3213 | 381.3 | 324.3 | 343.1 | 311.6 | 632.1 | 53.4 | 19.5 | 93 | 4.9 | 255.1 | 7.3 | 865.9 | 823.1 | 768.6 | 860.5 | 804.2 | 782.6 | 701.3 | 799.4 | 818.2 | 734.2 | 193.3 | 232.3 | 179.7 | 353.4 | 333 | 185.2 | 308.9 | 419.1 | 271.4
1133 | 926 | 564.9 | 225.96 | 264.1342 | 382.8 | 324.1 | 344.2 | 312.3 | 628.4 | 53.4 | 19.5 | 93.1 | 5.2 | 256.8 | 7.3 | 865.8 | 822.5 | 768 | 861 | 807.5 | 782.1 | 698.7 | 800.6 | 819.4 | 733.1 | 277 | 304.3 | 179.9 | 353.7 | 332.7 | 185.6 | 309.1 | 419.1 | 271.6
1134 | 927 | 565.5 | 226.2 | 264.4148 | 382.7 | 324.4 | 344.7 | 312.3 | 641.6 | 53.5 | 19.5 | 93.1 | 5 | 257.7 | 7.3 | 865.7 | 821.5 | 769.6 | 860.9 | 806.4 | 781.8 | 699.1 | 805.1 | 819.7 | 731.8 | 349.5 | 367.6 | 180.2 | 353.7 | 332.8 | 186 | 309.2 | 419.2 | 271.9
1135 | 928 | 565.9 | 226.36 | 264.6018 | 381.7 | 324.7 | 345.3 | 312.4 | 640.5 | 53.7 | 19.5 | 93.2 | 4.8 | 261 | 7.2 | 865.5 | 822.5 | 777.1 | 861 | 810.4 | 781.7 | 701.3 | 809.8 | 819.5 | 731.1 | 350 | 367.9 | 180.5 | 354.2 | 333 | 186.4 | 309.4 | 419.4 | 272.1
1136 | 929 | 566.4 | 226.56 | 264.8356 | 381.7 | 325 | 345.7 | 312.2 | 626.1 | 53.8 | 19.5 | 93.2 | 4.8 | 262.1 | 7.1 | 865.7 | 829.3 | 785.2 | 860.8 | 819.4 | 781.7 | 708.2 | 810.8 | 818 | 734.6 | 350.4 | 367.8 | 180.8 | 354.5 | 333.3 | 186.8 | 309.6 | 419.5 | 272.3
1137 | 930 | 565.1 | 226.04 | 264.2277 | 381.6 | 325.2 | 346.2 | 312.2 | 623.6 | 53.8 | 19.5 | 93.1 | 5.5 | 260.2 | 6.9 | 865.3 | 834.6 | 789.3 | 860 | 828.4 | 781.7 | 715.2 | 812.3 | 815.4 | 737.7 | 350.8 | 367.2 | 181 | 356.1 | 333.7 | 187.1 | 309.7 | 419.6 | 272.6
1138 | 931 | 564.6 | 225.84 | 263.9939 | 381.7 | 324.9 | 345.8 | 312.2 | 621.4 | 53.9 | 19.5 | 93.1 | 5.6 | 260.7 | 6.8 | 864.7 | 838.5 | 793.6 | 858.7 | 838.6 | 781.8 | 717.8 | 812 | 813.6 | 739.7 | 351.2 | 366.4 | 181.3 | 355.7 | 333.9 | 187.4 | 309.9 | 419.8 | 272.8
1139 | 932 | 565.2 | 226.08 | 264.2745 | 381.5 | 324.9 | 344.2 | 312.1 | 621.2 | 53.9 | 19.5 | 93 | 5.8 | 264.3 | 6.5 | 864.6 | 841 | 792.4 | 858.3 | 847.6 | 781.8 | 717 | 810.8 | 812.4 | 740.9 | 351.5 | 365.7 | 181.6 | 355.6 | 333.8 | 187.7 | 310 | 420 | 273
1140 | 933 | 564.7 | 225.88 | 264.0407 | 382.4 | 324.9 | 342.5 | 311.8 | 615.1 | 53.9 | 19.5 | 92.9 | 5.6 | 265.9 | 6 | 865.4 | 840.7 | 786.8 | 858.3 | 852.5 | 782 | 713.3 | 806.3 | 813.3 | 741.3 | 351.8 | 365.7 | 181.8 | 355.4 | 333.6 | 188 | 310 | 420.1 | 273.2
1141 | 934 | 564.1 | 225.64 | 263.7602 | 381.6 | 324.8 | 341.9 | 311.1 | 598.4 | 54 | 19.5 | 92.9 | 4.9 | 264.4 | 5.5 | 865 | 836.4 | 784.1 | 858.4 | 843.8 | 781.9 | 707.5 | 801.1 | 815.8 | 739.5 | 352.1 | 365.7 | 182.1 | 355.3 | 333.1 | 188.3 | 310.1 | 420.2 | 273.4
1142 | 935 | 564.5 | 225.8 | 263.9472 | 382.3 | 324.6 | 341.6 | 310.5 | 603.6 | 54 | 19.5 | 93 | 5.4 | 264.4 | 5.2 | 864.8 | 835.9 | 789.2 | 858.7 | 843.1 | 781.9 | 706 | 805.1 | 817.5 | 739.5 | 352.3 | 366 | 182.4 | 355.6 | 332.8 | 188.6 | 310.2 | 420.3 | 273.6
1143 | 936 | 564.3 | 225.72 | 263.8537 | 382.6 | 324.4 | 342.1 | 310 | 619.4 | 54 | 19.5 | 93 | 5.6 | 264.3 | 5 | 865 | 834.5 | 791 | 859.4 | 840.7 | 781.8 | 706.1 | 809.4 | 818 | 738.3 | 352.6 | 366.5 | 182.6 | 355.6 | 332.4 | 188.9 | 310.2 | 420.3 | 273.8
1144 | 937 | 563.4 | 225.36 | 263.4329 | 382.8 | 324.3 | 342.6 | 309.6 | 640.6 | 54.1 | 19.5 | 93.1 | 5.7 | 264.4 | 4.7 | 865.1 | 832.7 | 791.9 | 859.9 | 834.2 | 781.8 | 708 | 811.9 | 818.3 | 736.4 | 352.8 | 366.8 | 182.9 | 355.6 | 332.4 | 189.2 | 310.2 | 420.4 | 274.1
1145 | 938 | 563.5 | 225.4 | 263.4796 | 382 | 324.2 | 343.4 | 309.3 | 648.2 | 54.1 | 19.5 | 93.2 | 4.8 | 267.1 | 4.6 | 865.1 | 829.6 | 790.6 | 860 | 827.8 | 781.6 | 707.3 | 810.5 | 818.8 | 735.7 | 353.1 | 367.7 | 183.2 | 355.5 | 332.4 | 189.5 | 310.3 | 420.5 | 274.3
1146 | 939 | 563.5 | 225.4 | 263.4796 | 382.7 | 324.2 | 344.3 | 309.4 | 652.2 | 54.2 | 19.5 | 93.2 | 4.9 | 269 | 4.5 | 865.1 | 827.3 | 792.6 | 859.5 | 822.1 | 781.5 | 707.3 | 812.6 | 819.7 | 734.2 | 353.4 | 368.6 | 183.4 | 355.6 | 332.2 | 189.8 | 310.4 | 420.7 | 274.5
1147 | 940 | 563 | 225.2 | 263.2458 | 383.1 | 324.4 | 344.6 | 309.9 | 660.3 | 54.2 | 19.5 | 93.3 | 5.3 | 271 | 4.5 | 864.8 | 820.3 | 789.1 | 859.3 | 805.1 | 781.5 | 700.7 | 809.4 | 822 | 729.9 | 353.8 | 369.5 | 183.7 | 356 | 332.3 | 190.2 | 310.4 | 420.8 | 274.8
1148 | 941 | 249.7 | 99.88 | 116.754 | 383 | 325.2 | 345.8 | 310.1 | 654.9 | 54.2 | 19.5 | 93.3 | 4.9 | 277.8 | 4.7 | 864.6 | 814.3 | 783.8 | 859.3 | 797.2 | 781.2 | 696.9 | 809.2 | 823.7 | 726.5 | 354.1 | 370.2 | 184 | 356.5 | 332.4 | 190.5 | 310.5 | 421.1 | 275
1149 | 942 | -7 | 0 | 0 | 381.8 | 326.2 | 347.1 | 310.4 | 650.2 | 54.2 | 19.5 | 93.4 | 4.8 | 275.5 | 4.5 | 864 | 808.1 | 769.8 | 859.3 | 786.9 | 781 | 689.8 | 802.4 | 825.3 | 721.8 | 354.5 | 370.8 | 184.3 | 356.8 | 332.7 | 190.8 | 310.6 | 421.4 | 275.2
1150 | 943 | -7.1 | 0 | 0 | 380.7 | 326.2 | 346.4 | 310.8 | 614 | 54.1 | 19.5 | 93.5 | 4.3 | 263 | 4.3 | 862.7 | 796.1 | 744.4 | 858.8 | 769.4 | 780.4 | 676 | 780.8 | 826.3 | 715.6 | 354.9 | 370.1 | 184.5 | 356.6 | 332.3 | 191.1 | 310.6 | 421.6 | 275.4
1151 | 944 | -7.1 | 0 | 0 | 378.3 | 325.9 | 344.9 | 310.6 | 573.4 | 54.1 | 19.5 | 93.5 | 4 | 260 | 4.4 | 861 | 782 | 717.7 | 857.6 | 752.6 | 779.3 | 663 | 760.1 | 826.8 | 709.1 | 355.2 | 369 | 184.8 | 356.4 | 331.9 | 191.5 | 310.6 | 421.6 | 275.7
1152 | 945 | -7.1 | 0 | 0 | 374.9 | 325 | 343 | 309.6 | 539.9 | 54.2 | 19.5 | 93.6 | 3.7 | 272.3 | 4.5 | 858.9 | 769.1 | 694.3 | 855.6 | 737.3 | 777.8 | 649.6 | 740.9 | 826.4 | 702.7 | 355.4 | 367.1 | 185.1 | 355.6 | 331.4 | 191.7 | 310.5 | 421.5 | 275.8
1153 | 946 | -7.1 | 0 | 0 | 370.9 | 323.5 | 339.5 | 307.6 | 511 | 54.2 | 19.5 | 93.7 | 4.2 | 277.8 | 4.2 | 856.8 | 755.3 | 674.8 | 853.4 | 725.4 | 776.3 | 636.9 | 724.8 | 824.5 | 696.2 | 355.6 | 365.2 | 185.4 | 354.4 | 330.6 | 191.9 | 310.4 | 421.4 | 276
1154 | 947 | -7 | 0 | 0 | 367.2 | 321.7 | 335.7 | 305.2 | 488.2 | 54.3 | 19.5 | 93.7 | 4.4 | 277.7 | 4 | 854.2 | 739.4 | 657 | 850.6 | 715 | 774.8 | 625.4 | 710.1 | 822.4 | 690.6 | 355.6 | 362.5 | 185.6 | 352.9 | 329.2 | 192.1 | 310.2 | 421.2 | 276.2
1155 | 948 | -7 | 0 | 0 | 363.4 | 319.7 | 332 | 303 | 468.7 | 54.4 | 19.5 | 93.5 | 4.3 | 276.9 | 3.7 | 851.5 | 727.4 | 640 | 847.4 | 705.5 | 772.3 | 613.9 | 696.3 | 820.1 | 684.5 | 355.6 | 359.8 | 185.9 | 351.1 | 327.5 | 192.3 | 309.9 | 421 | 276.3
1156 | 949 | -7 | 0 | 0 | 359.6 | 317.9 | 328.7 | 300.4 | 451.2 | 54.4 | 19.4 | 93.3 | 4.5 | 276.2 | 3.6 | 848.6 | 716.6 | 625.4 | 844.2 | 697.4 | 770 | 601.1 | 683.9 | 817.1 | 678.6 | 355.5 | 357.1 | 186.2 | 349.1 | 325.6 | 192.4 | 309.5 | 420.9 | 276.4
1157 | 950 | -7 | 0 | 0 | 356 | 315.8 | 325.9 | 297.5 | 436.6 | 54.4 | 19.5 | 93 | 4.3 | 280.3 | 3.4 | 845.4 | 703.3 | 611.8 | 840.7 | 689.9 | 768.1 | 590.8 | 672.8 | 814 | 672.7 | 355.3 | 353.9 | 186.5 | 346.9 | 323.2 | 192.6 | 309.1 | 420.7 | 276.6
1158 | 951 | -7 | 0 | 0 | 352.5 | 313.7 | 322.8 | 294.7 | 424 | 54.5 | 19.4 | 92.8 | 4.4 | 284.3 | 3.2 | 842.1 | 687.8 | 599.9 | 837.1 | 682.9 | 766.8 | 582.4 | 661.9 | 811.7 | 667.4 | 355.1 | 351.1 | 186.7 | 344.8 | 320.8 | 192.7 | 308.6 | 420.5 | 276.6
1159 | 952 | -7 | 0 | 0 | 348.6 | 311.4 | 319.9 | 292.1 | 412.9 | 54.5 | 19.4 | 92.3 | 4.4 | 283.6 | 3.1 | 838.6 | 680 | 587.9 | 833.7 | 676.6 | 765.3 | 574.4 | 651.6 | 809.4 | 662.4 | 354.8 | 348.4 | 187 | 342.6 | 318.4 | 192.8 | 308.2 | 420.3 | 276.7
1160 | 953 | -7 | 0 | 0 | 344.9 | 309.1 | 317.6 | 289.8 | 402 | 54.4 | 19.4 | 91.9 | 4.4 | 284 | 3.2 | 835.1 | 674.7 | 576.2 | 831 | 669.4 | 763.6 | 566.4 | 642.6 | 807.9 | 657.6 | 354.5 | 345.9 | 187.2 | 340.4 | 316 | 192.9 | 307.8 | 420.1 | 276.8
1161 | 954 | -7 | 0 | 0 | 341.3 | 306.6 | 315.1 | 287.4 | 391.9 | 54.4 | 19.4 | 91.4 | 4.1 | 281.4 | 3.2 | 831.8 | 670.1 | 565.3 | 828.4 | 663.2 | 762 | 558.2 | 635 | 806.1 | 652.8 | 354.1 | 343.6 | 187.5 | 338.1 | 313.6 | 193.1 | 307.4 | 419.9 | 276.9
1162 | 955 | -7 | 0 | 0 | 337.9 | 304 | 312.5 | 285.1 | 384.1 | 54.4 | 19.4 | 90.9 | 4 | 273.7 | 3.9 | 828.7 | 661.7 | 555.5 | 825.6 | 658.1 | 760.6 | 551 | 628.3 | 804.1 | 648.3 | 353.7 | 341.3 | 187.7 | 335.9 | 311.4 | 193.2 | 307 | 419.7 | 277
1163 | 956 | -7 | 0 | 0 | 335 | 301.5 | 309.9 | 282.7 | 376.1 | 54.4 | 19.4 | 90.4 | 4.1 | 264.3 | 4.3 | 825.2 | 655.5 | 546.2 | 822.5 | 653.3 | 758.6 | 544.8 | 622.4 | 802 | 643.3 | 353.2 | 339.1 | 187.9 | 333.9 | 309.2 | 193.4 | 306.5 | 419.5 | 277.1
1164 | 957 | -7 | 0 | 0 | 332.5 | 299.4 | 307.2 | 280.4 | 367.7 | 54.3 | 19.4 | 90 | 3.9 | 267.4 | 4.4 | 821.7 | 652.8 | 536.6 | 819.6 | 647.7 | 756.9 | 537.9 | 614.7 | 800 | 638.6 | 352.7 | 336.9 | 188.2 | 331.8 | 307.2 | 193.5 | 306 | 419.2 | 277.1
1165 | 958 | -7 | 0 | 0 | 329.9 | 297.4 | 304.7 | 278.3 | 361.9 | 54.2 | 19.4 | 89.6 | 3.7 | 271.4 | 4.4 | 818.2 | 651.1 | 526.4 | 816.8 | 651.4 | 755.2 | 530.1 | 608.7 | 797.2 | 634.2 | 352.2 | 334.7 | 188.4 | 329.7 | 305.2 | 193.7 | 305.6 | 419 | 277.2
1166 | 959 | -7 | 0 | 0 | 327.4 | 295.5 | 302.5 | 276.2 | 356.1 | 54.2 | 19.4 | 89.1 | 3.8 | 271.6 | 4.3 | 814.7 | 649.8 | 517.2 | 814.5 | 649.7 | 754 | 524.3 | 603.8 | 794.7 | 630.2 | 351.6 | 332.5 | 188.6 | 327.8 | 303.2 | 193.8 | 305.2 | 418.8 | 277.3
1167 | 960 | -7 | 0 | 0 | 325.2 | 293.6 | 300.4 | 274.2 | 350.7 | 54.2 | 19.4 | 88.6 | 3.5 | 272 | 4.4 | 811.5 | 647.6 | 508.8 | 812.3 | 645.4 | 752.9 | 518.3 | 596.8 | 793.2 | 625.6 | 351 | 330.2 | 188.9 | 326 | 301.2 | 194 | 304.8 | 418.5 | 277.3
1168 | 961 | -7 | 0 | 0 | 323.2 | 291.8 | 298.3 | 272.4 | 346.3 | 54.1 | 19.4 | 88.2 | 3.2 | 269.5 | 4.5 | 808.5 | 644.8 | 501.4 | 810.2 | 640.9 | 751.5 | 513.2 | 592.7 | 791.4 | 621.5 | 350.4 | 328.2 | 189.1 | 324.2 | 299.3 | 194.2 | 304.4 | 418.3 | 277.4
1169 | 962 | -7 | 0 | 0 | 321.2 | 290 | 296.2 | 270.7 | 342.4 | 54.1 | 19.4 | 87.8 | 3.5 | 268.2 | 4.7 | 805.4 | 642.2 | 494.4 | 807.7 | 636.7 | 750 | 508.7 | 588.1 | 789.8 | 617.3 | 349.7 | 326.2 | 189.3 | 322.5 | 297.4 | 194.4 | 303.9 | 418.1 | 277.4
1170 | 963 | -7 | 0 | 0 | 319.3 | 288.3 | 294.3 | 269.1 | 338.3 | 54.1 | 19.4 | 87.4 | 3.9 | 271.7 | 4.8 | 802 | 640.9 | 486.9 | 805 | 631.7 | 748.3 | 504.2 | 583.4 | 787.7 | 613.2 | 349 | 324.4 | 189.5 | 320.9 | 295.6 | 194.6 | 303.4 | 417.8 | 277.5
1171 | 964 | -7 | 0 | 0 | 317.5 | 286.8 | 292.5 | 267.6 | 335.3 | 54.1 | 19.4 | 87.1 | 3.8 | 274.2 | 4.7 | 798.8 | 639.9 | 479.5 | 802.5 | 625.6 | 746.8 | 499.3 | 578 | 786.1 | 609.3 | 348.4 | 322.8 | 189.7 | 319.2 | 293.9 | 194.8 | 303 | 417.6 | 277.6
1172 | 965 | -7 | 0 | 0 | 315.7 | 285.3 | 290.6 | 266.2 | 332.6 | 54.1 | 19.4 | 86.7 | 3.6 | 273.8 | 4.4 | 795.5 | 638 | 472.4 | 800.3 | 619.5 | 745.3 | 493.7 | 573 | 784.5 | 605.7 | 347.7 | 321 | 189.9 | 317.7 | 292.2 | 195 | 302.6 | 417.3 | 277.6
1173 | 966 | -7 | 0 | 0 | 314.1 | 283.9 | 288.9 | 264.8 | 330.1 | 54 | 19.4 | 86.4 | 4.1 | 276.7 | 4.1 | 792.1 | 635.9 | 465.6 | 798 | 613.9 | 744.2 | 488.6 | 568.8 | 782.9 | 601.9 | 347 | 319.4 | 190.2 | 316.2 | 290.5 | 195.2 | 302.2 | 417.1 | 277.7
1174 | 967 | -7 | 0 | 0 | 312.5 | 282.5 | 287.5 | 263.6 | 327.8 | 53.8 | 19.4 | 86 | 3.8 | 273.1 | 4.1 | 789 | 633.4 | 459.1 | 795.6 | 608.2 | 743 | 484.3 | 564.5 | 781.2 | 598.3 | 346.3 | 317.9 | 190.4 | 314.8 | 289 | 195.5 | 301.8 | 416.8 | 277.7
1175 | 968 | -7 | 0 | 0 | 311 | 281.5 | 286.1 | 262.4 | 325.3 | 53.7 | 19.4 | 85.7 | 3.4 | 268.7 | 4 | 786.3 | 630.5 | 453.2 | 793.3 | 602.4 | 742.1 | 480.1 | 561.1 | 779 | 594.8 | 345.6 | 316.4 | 190.6 | 313.3 | 287.6 | 195.7 | 301.3 | 416.6 | 277.8
1176 | 969 | -7 | 0 | 0 | 309.5 | 280.5 | 284.9 | 261 | 324.2 | 53.7 | 19.4 | 85.3 | 3.5 | 262.7 | 4.1 | 783.7 | 624.9 | 447.5 | 791.2 | 596.9 | 741.4 | 475.7 | 556.3 | 776.8 | 591.4 | 344.9 | 314.9 | 190.8 | 311.9 | 286.2 | 195.9 | 300.9 | 416.3 | 277.8
1177 | 970 | -7 | 0 | 0 | 308 | 279.3 | 283.5 | 259.7 | 323 | 53.6 | 19.4 | 85 | 3.9 | 259.7 | 4.3 | 781.2 | 615.9 | 442.5 | 788.6 | 590.4 | 740.1 | 469 | 552.3 | 774.9 | 587.4 | 344.2 | 313.5 | 191 | 310.5 | 284.9 | 196.2 | 300.5 | 416.1 | 277.8
1178 | 971 | -7 | 0 | 0 | 306.7 | 278.1 | 282 | 258.6 | 320.5 | 53.5 | 19.4 | 84.6 | 3.9 | 256.3 | 4.2 | 778.5 | 609.9 | 437.4 | 785.3 | 582.1 | 738.5 | 462.1 | 548.7 | 772 | 583.7 | 343.5 | 312.2 | 191.2 | 309.2 | 283.8 | 196.5 | 300.1 | 415.8 | 277.9
1179 | 972 | -7 | 0 | 0 | 305.4 | 276.9 | 280.8 | 257.5 | 318.7 | 53.4 | 19.4 | 84.3 | 3.6 | 260.6 | 4.1 | 775.5 | 607.3 | 433 | 782 | 573.6 | 737.5 | 455.2 | 544.6 | 768.3 | 580.1 | 342.8 | 311 | 191.4 | 308.1 | 282.5 | 196.7 | 299.6 | 415.6 | 277.9
1180 | 973 | -7 | 0 | 0 | 304.3 | 275.8 | 279.6 | 256.4 | 316.3 | 53.4 | 19.4 | 84 | 3.6 | 265.4 | 3.9 | 772.4 | 607.8 | 428.5 | 778.9 | 568.1 | 736.5 | 449.7 | 540 | 765.2 | 576.8 | 342.1 | 309.8 | 191.6 | 306.9 | 281.3 | 197 | 299.2 | 415.3 | 277.9
1181 | 974 | -7 | 0 | 0 | 303.2 | 274.6 | 278.5 | 255.6 | 314 | 53.3 | 19.4 | 83.8 | 3.8 | 261.4 | 3.5 | 769.3 | 608 | 424 | 776.1 | 563.9 | 735.8 | 445.6 | 536.1 | 762.4 | 573.2 | 341.4 | 308.5 | 191.8 | 305.7 | 280.2 | 197.3 | 298.8 | 415.1 | 278
1182 | 975 | -7 | 0 | 0 | 302 | 273.6 | 277.5 | 254.7 | 311.9 | 53.2 | 19.4 | 83.6 | 3.6 | 257 | 3.3 | 766.1 | 607.5 | 419.3 | 773.4 | 559.8 | 735.1 | 441.4 | 532.4 | 759.9 | 569.9 | 340.7 | 307.1 | 192 | 304.5 | 279 | 197.6 | 298.4 | 414.8 | 278
1183 | 976 | -7 | 0 | 0 | 301 | 272.7 | 276.6 | 253.8 | 310.2 | 53.1 | 19.4 | 83.4 | 3.6 | 254.3 | 3.1 | 763 | 606.8 | 414.6 | 771 | 556.5 | 734.6 | 437.1 | 528.9 | 757.5 | 566.8 | 340 | 305.8 | 192.2 | 303.3 | 278 | 197.9 | 298.1 | 414.5 | 278.1
1184 | 977 | -7 | 0 | 0 | 300 | 271.9 | 275.5 | 252.9 | 308.7 | 53 | 19.4 | 83.2 | 3.3 | 252.6 | 3 | 760.1 | 605.6 | 409.8 | 768.5 | 553.6 | 734.2 | 431.4 | 525.3 | 754.9 | 563.5 | 339.3 | 304.6 | 192.4 | 302.3 | 276.9 | 198.3 | 297.6 | 414.3 | 278.1
1185 | 978 | -7 | 0 | 0 | 299.1 | 271.1 | 274.4 | 252 | 306.8 | 52.9 | 19.4 | 83 | 3.5 | 250.7 | 2.9 | 757.3 | 604.4 | 405.3 | 765.9 | 549.7 | 733.4 | 426 | 521.6 | 752.2 | 559.9 | 338.6 | 303.4 | 192.5 | 301.5 | 275.7 | 198.6 | 297.2 | 414 | 278.1
1186 | 979 | -7 | 0 | 0 | 298.1 | 270.4 | 273.5 | 251.2 | 305.2 | 52.8 | 19.4 | 82.8 | 3.6 | 246.9 | 2.8 | 754.5 | 603.3 | 400.8 | 763 | 544.1 | 732.4 | 422.5 | 518.3 | 749.5 | 556.5 | 337.9 | 302.2 | 192.7 | 300.6 | 274.8 | 199 | 296.8 | 413.7 | 278.1
1187 | 980 | -7 | 0 | 0 | 297.2 | 269.6 | 272.7 | 250.4 | 303 | 52.6 | 19.4 | 82.6 | 3.6 | 249.4 | 2.8 | 751.6 | 601.4 | 397 | 760.4 | 540.6 | 731.5 | 419.8 | 514.7 | 747.2 | 553.5 | 337.2 | 301.2 | 192.9 | 299.5 | 273.9 | 199.3 | 296.4 | 413.5 | 278.2
1188 | 981 | -7 | 0 | 0 | 296.4 | 268.9 | 271.5 | 249.4 | 301.3 | 52.5 | 19.4 | 82.4 | 3.6 | 252.9 | 2.7 | 748.8 | 599.7 | 393 | 757.8 | 536 | 730.8 | 415.2 | 511.5 | 744.8 | 550.4 | 336.5 | 300.2 | 193.1 | 298.4 | 273 | 199.7 | 295.9 | 413.2 | 278.2
1189 | 982 | -7 | 0 | 0 | 295.6 | 268.2 | 270.6 | 248.7 | 300.2 | 52.4 | 19.4 | 82.1 | 3.8 | 252 | 2.5 | 746 | 593.7 | 388.7 | 755.2 | 531.4 | 730.1 | 411.1 | 508.3 | 742.3 | 547.8 | 335.9 | 299.2 | 193.3 | 297.5 | 272 | 200.1 | 295.5 | 412.9 | 278.2
1190 | 983 | -7 | 0 | 0 | 294.7 | 267.5 | 269.9 | 248.1 | 298.6 | 52.3 | 19.4 | 81.9 | 3.6 | 245.9 | 2.2 | 743.2 | 591.2 | 384.1 | 753.1 | 528.4 | 729.3 | 406.6 | 505.3 | 739 | 545.2 | 335.2 | 298.3 | 193.5 | 296.5 | 271.2 | 200.5 | 295.1 | 412.7 | 278.2
1191 | 984 | -7 | 0 | 0 | 293.9 | 266.9 | 269.1 | 247.5 | 296.7 | 52.2 | 19.4 | 81.7 | 3.7 | 233.4 | 2 | 740.4 | 590.6 | 379.9 | 751 | 524.7 | 728.4 | 402.7 | 502.3 | 735.6 | 542.2 | 334.5 | 297.5 | 193.6 | 295.5 | 270.3 | 200.9 | 294.7 | 412.4 | 278.2
1192 | 985 | -7 | 0 | 0 | 293.1 | 266.2 | 268.4 | 246.7 | 295.3 | 52.1 | 19.4 | 81.5 | 3.5 | 221.6 | 1.9 | 737.7 | 588.6 | 375.8 | 749.1 | 520.4 | 727.5 | 399 | 499.9 | 732.7 | 539.3 | 333.8 | 296.6 | 193.8 | 294.6 | 269.5 | 201.3 | 294.3 | 412.1 | 278.3
1193 | 986 | -7 | 0 | 0 | 292.3 | 265.5 | 267.4 | 246 | 294.1 | 51.9 | 19.4 | 81.3 | 3.4 | 219.3 | 1.9 | 734.9 | 587.4 | 372.4 | 747.1 | 517.3 | 726.5 | 396.1 | 497.2 | 729.9 | 536.5 | 333.1 | 295.7 | 194 | 293.6 | 268.6 | 201.7 | 293.9 | 411.8 | 278.3
1194 | 987 | -7 | 0 | 0 | 291.5 | 264.8 | 266.4 | 245.4 | 292.9 | 51.8 | 19.4 | 81.1 | 4.1 | 222.8 | 1.8 | 732.4 | 585.6 | 368 | 745.1 | 513.9 | 725.5 | 391.4 | 494.2 | 727.1 | 534 | 332.5 | 294.8 | 194.1 | 292.8 | 267.8 | 202.1 | 293.4 | 411.6 | 278.3
1195 | 988 | -7 | 0 | 0 | 290.5 | 264.1 | 265.5 | 244.8 | 291.7 | 51.7 | 19.4 | 80.9 | 4.2 | 227.8 | 1.6 | 729.8 | 585.1 | 364.2 | 743.2 | 510.7 | 724.3 | 387.8 | 491.3 | 724.2 | 531 | 331.8 | 293.9 | 194.3 | 292.1 | 267.1 | 202.5 | 293.1 | 411.3 | 278.3
1196 | 989 | -7 | 0 | 0 | 289.8 | 263.5 | 264.7 | 244.3 | 290.7 | 51.6 | 19.4 | 80.7 | 3.9 | 233.4 | 1.6 | 727.3 | 584 | 360.6 | 741.1 | 507.9 | 722.7 | 384.4 | 489.1 | 721.2 | 528.3 | 331.2 | 293.1 | 194.5 | 291.4 | 266.3 | 202.9 | 292.7 | 411 | 278.3
1197 | 990 | -7 | 0 | 0 | 289 | 262.8 | 264 | 243.8 | 289.3 | 51.5 | 19.4 | 80.5 | 3.9 | 234.8 | 1.7 | 724.7 | 581.6 | 357 | 739 | 505.4 | 721.4 | 382.1 | 486.4 | 718.3 | 525.5 | 330.5 | 292.2 | 194.7 | 290.6 | 265.5 | 203.3 | 292.3 | 410.8 | 278.3
1198 | 991 | -7 | 0 | 0 | 288.3 | 262.2 | 263.1 | 243 | 288.1 | 51.4 | 19.4 | 80.4 | 4 | 238.9 | 1.8 | 722.1 | 580 | 353.8 | 736.9 | 503.4 | 719.7 | 378.9 | 483.4 | 715.6 | 522.7 | 329.9 | 291.3 | 194.8 | 289.9 | 264.8 | 203.7 | 291.9 | 410.5 | 278.3
1199 | 992 | -7 | 0 | 0 | 287.5 | 261.6 | 262.2 | 242.4 | 287.1 | 51.3 | 19.4 | 80.2 | 4.4 | 245.8 | 1.9 | 719.5 | 576.8 | 350.1 | 734.9 | 501.8 | 718 | 375.4 | 481.2 | 712.7 | 520.4 | 329.2 | 290.7 | 195 | 289.2 | 264.1 | 204 | 291.5 | 410.2 | 278.3
1200 | 993 | -7 | 0 | 0 | 286.8 | 261 | 261.4 | 241.7 | 286 | 51.2 | 19.4 | 80.1 | 4.2 | 256.1 | 2.2 | 716.8 | 573.8 | 346.8 | 732.7 | 500 | 716.6 | 372 | 478.5 | 709.3 | 518.3 | 328.6 | 290.1 | 195.2 | 288.4 | 263.4 | 204.4 | 291 | 409.9 | 278.3
1201 | 994 | -7 | 0 | 0 | 286.2 | 260.4 | 260.8 | 241 | 284.8 | 51.1 | 19.4 | 79.9 | 4.1 | 260.6 | 2.6 | 714.1 | 573.2 | 343.2 | 730.7 | 497.8 | 715.1 | 369 | 475.7 | 706.4 | 515.6 | 327.9 | 289.2 | 195.3 | 287.7 | 262.7 | 204.8 | 290.7 | 409.7 | 278.3
1202 | 995 | -7 | 0 | 0 | 285.6 | 259.8 | 260 | 240.4 | 283.5 | 50.9 | 19.4 | 79.6 | 3.9 | 261.1 | 3 | 711.5 | 572.3 | 339.5 | 728.8 | 495.2 | 713.6 | 365.6 | 473.5 | 703.6 | 513.6 | 327.3 | 288.4 | 195.5 | 286.8 | 262 | 205.2 | 290.3 | 409.4 | 278.3
1203 | 996 | -7 | 0 | 0 | 285.1 | 259.2 | 259.2 | 239.9 | 281.9 | 50.8 | 19.4 | 79.4 | 4 | 256 | 3.4 | 708.9 | 571.5 | 336.2 | 727.1 | 492.4 | 712.4 | 363.6 | 471.5 | 700.5 | 510.8 | 326.7 | 287.9 | 195.7 | 285.9 | 261.3 | 205.5 | 289.9 | 409.1 | 278.3
1204 | 997 | -7 | 0 | 0 | 284.5 | 258.6 | 258.5 | 239.3 | 280.8 | 50.8 | 19.4 | 79.2 | 4 | 245 | 3.5 | 706.5 | 570.8 | 333 | 725.7 | 488.9 | 711.2 | 361.3 | 469.2 | 697.5 | 508.2 | 326.1 | 287.3 | 195.8 | 285.1 | 260.5 | 205.9 | 289.5 | 408.8 | 278.3
1205 | 998 | -7 | 0 | 0 | 283.7 | 258 | 257.8 | 238.7 | 280 | 50.7 | 19.5 | 79 | 4.5 | 244.6 | 3.5 | 704.2 | 569 | 329.6 | 724.2 | 486 | 709.9 | 359.5 | 468 | 694.8 | 505.6 | 325.5 | 286.4 | 196 | 284.3 | 259.8 | 206.2 | 289 | 408.5 | 278.3
1206 | 999 | -7 | 0 | 0 | 283 | 257.4 | 257.1 | 238.1 | 279.2 | 50.5 | 19.4 | 78.8 | 4.8 | 249.2 | 3.8 | 701.9 | 562.6 | 326.9 | 722.7 | 483.2 | 708.5 | 358.4 | 465.9 | 692.5 | 502.9 | 324.9 | 285.6 | 196.2 | 283.6 | 259.2 | 206.5 | 288.6 | 408.3 | 278.3
1207 | 1000 | -7 | 0 | 0 | 282.3 | 256.8 | 256.3 | 237.4 | 279.5 | 50.4 | 19.4 | 78.6 | 4.7 | 247.8 | 4.4 | 699.6 | 555 | 324 | 721.5 | 480.1 | 707.1 | 356.3 | 463.9 | 690.4 | 500.8 | 324.2 | 285 | 196.3 | 282.9 | 258.6 | 206.8 | 288.2 | 408 | 278.3
1208 | 1001 | -7 | 0 | 0 | 281.7 | 256.4 | 255.7 | 236.8 | 279.4 | 50.4 | 19.4 | 78.3 | 4.3 | 247 | 4.7 | 697.3 | 552.1 | 321.2 | 719.9 | 479 | 706 | 353.9 | 461.3 | 688.3 | 498.7 | 323.6 | 284.5 | 196.5 | 282.3 | 258 | 207.1 | 287.8 | 407.7 | 278.3
1209 | 1002 | -7 | 0 | 0 | 281.1 | 255.8 | 255.1 | 236.2 | 278.6 | 50.3 | 19.4 | 78.1 | 4.1 | 264.5 | 5 | 694.8 | 552.3 | 318.1 | 718.1 | 478.6 | 704.3 | 352.4 | 458.3 | 686.3 | 496.1 | 323 | 283.9 | 196.6 | 281.6 | 257.5 | 207.3 | 287.5 | 407.4 | 278.3
1210 | 1003 | -7 | 0 | 0 | 280.6 | 255.3 | 254.5 | 235.6 | 277.6 | 50.1 | 19.4 | 77.9 | 3.6 | 250.5 | 5 | 692.3 | 549.5 | 314.9 | 716.5 | 477.2 | 702.1 | 350.2 | 455.9 | 684 | 493.6 | 322.4 | 283.4 | 196.8 | 281 | 256.8 | 207.6 | 287 | 407.1 | 278.3
1211 | 1004 | -7 | 0 | 0 | 280.1 | 254.7 | 253.8 | 235 | 276.5 | 50 | 19.4 | 77.8 | 3.2 | 245.2 | 4.9 | 690 | 548.4 | 311.9 | 715 | 475.1 | 700.1 | 348 | 453.7 | 681.5 | 491.2 | 321.8 | 282.9 | 197 | 280.4 | 256.2 | 207.8 | 286.6 | 406.9 | 278.3
1212 | 1005 | -7 | 0 | 0 | 279.4 | 254.2 | 253.2 | 234.5 | 275.4 | 49.9 | 19.4 | 77.6 | 3.7 | 263.4 | 4.8 | 688 | 547 | 309.2 | 713.5 | 472.6 | 698.4 | 346.6 | 450.9 | 679.2 | 488.9 | 321.2 | 282.4 | 197.1 | 279.8 | 255.6 | 208 | 286.2 | 406.6 | 278.2
1213 | 1006 | -7 | 0 | 0 | 278.5 | 253.6 | 252.7 | 234.1 | 274.6 | 49.9 | 19.5 | 77.4 | 3.7 | 251.4 | 4.8 | 686.1 | 545.2 | 306.9 | 711.8 | 470.1 | 696.7 | 343.9 | 449.1 | 676.8 | 486.7 | 320.7 | 281.9 | 197.3 | 279.2 | 255 | 208.2 | 285.8 | 406.3 | 278.2
1214 | 1007 | -7 | 0 | 0 | 277.9 | 253.2 | 252.1 | 233.5 | 273.9 | 49.9 | 19.5 | 77.2 | 3.7 | 252.4 | 6.2 | 683.9 | 533.3 | 304.4 | 709.9 | 467.5 | 695 | 341.6 | 447 | 674.3 | 484.4 | 320.1 | 281.3 | 197.5 | 278.7 | 254.4 | 208.4 | 285.4 | 406 | 278.2
1215 | 1008 | -7 | 0 | 0 | 277.3 | 252.7 | 251.5 | 232.9 | 273 | 49.9 | 19.5 | 76.9 | 3.5 | 240.5 | 7 | 681.8 | 530.6 | 301.8 | 708.6 | 464.7 | 693.3 | 340 | 444.3 | 671.7 | 482.2 | 319.5 | 280.7 | 197.6 | 278.2 | 253.8 | 208.6 | 285 | 405.7 | 278.2
1216 | 1009 | -7 | 0 | 0 | 276.6 | 252.3 | 250.8 | 232.4 | 272.8 | 49.9 | 19.5 | 76.7 | 3.2 | 257.4 | 8.7 | 679.7 | 531.9 | 299.5 | 707 | 462.8 | 691.8 | 338.3 | 442.2 | 669.1 | 479.7 | 318.9 | 280 | 197.8 | 277.7 | 253.2 | 208.8 | 284.7 | 405.4 | 278.2
1217 | 1010 | -7 | 0 | 0 | 276.1 | 251.7 | 250.2 | 231.9 | 272 | 49.9 | 19.5 | 76.6 | 3.3 | 262.1 | 9.4 | 677.5 | 533.1 | 297 | 705.2 | 460.1 | 690.4 | 336.1 | 439.9 | 666.6 | 477.8 | 318.4 | 279.4 | 197.9 | 277.2 | 252.5 | 209 | 284.2 | 405.1 | 278.2
1218 | 1011 | -7 | 0 | 0 | 275.6 | 251.2 | 249.5 | 231.5 | 271.5 | 49.9 | 19.5 | 76.4 | 3.4 | 258.3 | 9.1 | 675.3 | 531.2 | 295 | 703.5 | 458.2 | 689 | 334 | 438.1 | 663.8 | 476 | 317.8 | 278.9 | 198.1 | 276.7 | 252 | 209.1 | 283.9 | 404.9 | 278.1
1219 | 1012 | -7 | 0 | 0 | 275 | 250.7 | 248.9 | 231 | 270.7 | 49.8 | 19.5 | 76.1 | 3.3 | 249.5 | 8.3 | 673.2 | 519 | 293.1 | 701.7 | 457.3 | 687.7 | 331.6 | 435.8 | 660.8 | 473.7 | 317.3 | 278.5 | 198.2 | 276.2 | 251.6 | 209.3 | 283.5 | 404.6 | 278.1
1220 | 1013 | -7 | 0 | 0 | 274.4 | 250.3 | 248.2 | 230.6 | 269.9 | 49.8 | 19.5 | 75.9 | 3.2 | 254 | 7.8 | 671.1 | 509.8 | 291 | 699.9 | 456 | 686.1 | 330.3 | 433.7 | 657.8 | 471.8 | 316.7 | 278 | 198.4 | 275.7 | 251 | 209.4 | 283.1 | 404.3 | 278.1
1221 | 1014 | -7 | 0 | 0 | 273.9 | 249.8 | 247.6 | 230.2 | 268.9 | 49.7 | 19.5 | 75.7 | 3.8 | 244.3 | 7.3 | 669 | 512.5 | 288.2 | 697.9 | 453.3 | 684.5 | 327.7 | 431.7 | 655.1 | 470 | 316.2 | 277.5 | 198.6 | 275.2 | 250.5 | 209.6 | 282.7 | 404 | 278.1
1222 | 1015 | -7 | 0 | 0 | 273.5 | 249.4 | 247 | 229.7 | 267.9 | 49.6 | 19.5 | 75.5 | 4.3 | 254.3 | 6.9 | 666.7 | 515 | 285.7 | 696 | 451.5 | 683 | 325.4 | 429.5 | 652.2 | 467.8 | 315.7 | 277 | 198.7 | 274.8 | 249.9 | 209.7 | 282.3 | 403.7 | 278.1
1223 | 1016 | -7 | 0 | 0 | 273 | 249 | 246.2 | 229.4 | 267 | 49.5 | 19.5 | 75.2 | 3.7 | 272.9 | 6.3 | 664.6 | 517.4 | 283.4 | 694.4 | 450.5 | 681.1 | 322.6 | 426.9 | 649.5 | 465.7 | 315.2 | 276.5 | 198.9 | 274.3 | 249.3 | 209.9 | 281.9 | 403.4 | 278
1224 | 1017 | -7 | 0 | 0 | 272.4 | 248.6 | 245.6 | 229 | 266.3 | 49.4 | 19.5 | 75 | 3.6 | 278.1 | 5.6 | 662.7 | 517.7 | 281.1 | 692.6 | 449.7 | 679.3 | 320.7 | 424.4 | 646.7 | 463.6 | 314.6 | 276 | 199 | 273.8 | 248.8 | 210 | 281.4 | 403.2 | 278
1225 | 1018 | -7 | 0 | 0 | 271.8 | 248.2 | 245 | 228.6 | 265.3 | 49.3 | 19.5 | 74.9 | 3.6 | 282.6 | 5.9 | 660.7 | 518.2 | 278.4 | 690.9 | 447.7 | 677.5 | 318.7 | 421.9 | 643.9 | 461.5 | 314.1 | 275.6 | 199.2 | 273.3 | 248.2 | 210.1 | 281.1 | 402.9 | 278
1226 | 1019 | -7 | 0 | 0 | 271.4 | 247.7 | 244.7 | 228 | 264.7 | 49.3 | 19.5 | 74.7 | 3.7 | 269.1 | 6.5 | 658.7 | 518 | 276.2 | 689.2 | 445.5 | 675.6 | 317.7 | 420.9 | 641 | 459.3 | 313.6 | 275.6 | 199.3 | 272.8 | 247.6 | 210.2 | 280.7 | 402.6 | 277.9
1227 | 1020 | -7 | 0 | 0 | 271 | 247.3 | 244.1 | 227.4 | 264.4 | 49.2 | 19.5 | 74.5 | 3.8 | 285.3 | 6.7 | 656.6 | 518.3 | 274.1 | 687.3 | 444.3 | 673.6 | 316.7 | 419.7 | 637.7 | 458 | 313.1 | 275.5 | 199.5 | 272.3 | 247 | 210.3 | 280.3 | 402.3 | 277.9
1228 | 1021 | -7 | 0 | 0 | 270.5 | 246.9 | 243.8 | 226.8 | 264.3 | 49.1 | 19.5 | 74.4 | 3.7 | 290.4 | 6.6 | 654.4 | 515.4 | 272.3 | 685.4 | 443.1 | 671.6 | 315.5 | 418 | 634.2 | 455.6 | 312.6 | 275.5 | 199.6 | 271.7 | 246.4 | 210.3 | 279.9 | 402 | 277.9
1229 | 1022 | -7 | 0 | 0 | 270 | 246.5 | 243.4 | 226.4 | 263.9 | 49 | 19.5 | 74.1 | 3.7 | 279.5 | 6.9 | 652.5 | 511.1 | 270.6 | 683.6 | 442 | 670 | 314 | 416.1 | 630.6 | 453.2 | 312.1 | 275.3 | 199.8 | 271.1 | 245.9 | 210.4 | 279.5 | 401.7 | 277.9
1230 | 1023 | -7 | 0 | 0 | 269.5 | 246.1 | 242.9 | 225.9 | 263.7 | 48.9 | 19.5 | 73.9 | 4.2 | 268.4 | 7.7 | 650.7 | 509.4 | 268.8 | 681.8 | 441 | 668.2 | 311.9 | 414.1 | 627.1 | 451.5 | 311.6 | 274.6 | 199.9 | 270.5 | 245.4 | 210.5 | 279.1 | 401.4 | 277.8
1231 | 1024 | -7 | 0 | 0 | 268.9 | 245.7 | 242.3 | 225.4 | 263.7 | 48.9 | 19.5 | 73.7 | 4.3 | 271 | 8.2 | 648.8 | 499.6 | 266.8 | 679.9 | 439.3 | 666.5 | 310.3 | 412.7 | 624 | 449.7 | 311.1 | 273.9 | 200.1 | 270.1 | 244.8 | 210.6 | 278.7 | 401.1 | 277.8
1232 | 1025 | -7 | 0 | 0 | 268.4 | 245.3 | 241.8 | 224.9 | 263.8 | 48.8 | 19.5 | 73.5 | 4 | 287.5 | 8.1 | 646.9 | 494.5 | 264.8 | 678.1 | 438.2 | 665 | 309 | 410.7 | 620.9 | 447.8 | 310.6 | 273.2 | 200.2 | 269.6 | 244.1 | 210.7 | 278.3 | 400.9 | 277.8
1233 | 1026 | -7 | 0 | 0 | 267.9 | 244.9 | 241.3 | 224.3 | 263.9 | 48.7 | 19.5 | 73.4 | 3.8 | 256.5 | 7.9 | 644.9 | 491.5 | 262.9 | 676.1 | 437.3 | 663.1 | 307.1 | 409.2 | 617.8 | 446.2 | 310.1 | 272.5 | 200.4 | 269 | 243.5 | 210.8 | 277.9 | 400.5 | 277.7
1234 | 1027 | -7 | 0 | 0 | 267.4 | 244.5 | 240.8 | 223.9 | 263.6 | 48.6 | 19.5 | 73.2 | 4 | 263.5 | 7.6 | 642.9 | 488 | 261 | 674.2 | 436.1 | 661.4 | 305.5 | 407.7 | 614.7 | 444 | 309.6 | 272 | 200.5 | 268.5 | 243 | 210.8 | 277.5 | 400.3 | 277.7
1235 | 1028 | -7 | 0 | 0 | 266.9 | 244.1 | 240.3 | 223.4 | 263.4 | 48.5 | 19.5 | 73 | 4.1 | 271.2 | 7.2 | 640.9 | 485.5 | 258.7 | 672.2 | 434.5 | 659.9 | 303.7 | 405.6 | 611.6 | 442.5 | 309.1 | 271.4 | 200.7 | 268 | 242.4 | 210.9 | 277.1 | 400 | 277.6
1236 | 1029 | -7 | 0 | 0 | 266.3 | 243.7 | 239.8 | 222.9 | 263.2 | 48.4 | 19.5 | 72.8 | 3.8 | 257.4 | 7.1 | 638.9 | 482.7 | 256.3 | 670.4 | 433 | 657.8 | 301.7 | 403.7 | 608.6 | 441.2 | 308.6 | 270.8 | 200.8 | 267.4 | 241.9 | 210.9 | 276.8 | 399.7 | 277.6
1237 | 1030 | -7 | 0 | 0 | 265.8 | 243.3 | 239.3 | 222.4 | 263.2 | 48.4 | 19.5 | 72.7 | 3.9 | 253.7 | 7.5 | 636.8 | 480.3 | 253.5 | 668.6 | 431.6 | 655.8 | 300.6 | 402.4 | 605.5 | 439.7 | 308.1 | 270.3 | 201 | 266.7 | 241.4 | 211 | 276.4 | 399.4 | 277.6
1238 | 1031 | -7 | 0 | 0 | 265.3 | 243 | 238.8 | 222.1 | 262.8 | 48.2 | 19.5 | 72.5 | 3.9 | 271.2 | 7.9 | 634.9 | 482.9 | 250.6 | 666.9 | 430.5 | 654.2 | 300.1 | 400.6 | 602.3 | 438.3 | 307.6 | 270.1 | 201.1 | 266 | 240.9 | 211 | 276 | 399.1 | 277.5
1239 | 1032 | -7 | 0 | 0 | 264.7 | 242.7 | 238.2 | 221.8 | 262.4 | 48.1 | 19.5 | 72.4 | 4.2 | 259.3 | 7.7 | 632.9 | 483.9 | 248.2 | 665.2 | 428.9 | 652.5 | 298.8 | 398.8 | 599.1 | 436.4 | 307.1 | 270.1 | 201.3 | 265.4 | 240.6 | 211 | 275.6 | 398.8 | 277.5
1240 | 1033 | -7 | 0 | 0 | 264 | 242.5 | 237.8 | 221.4 | 262.3 | 47.9 | 19.5 | 72.2 | 3.8 | 267.7 | 7.6 | 631.1 | 485.6 | 246.5 | 663.5 | 426.1 | 650.7 | 298.1 | 396.5 | 595.9 | 434.4 | 306.6 | 269.9 | 201.4 | 264.9 | 240.2 | 211.1 | 275.2 | 398.5 | 277.5
1241 | 1034 | -7 | 0 | 0 | 263.5 | 242.3 | 237.4 | 220.9 | 262.3 | 47.8 | 19.5 | 72 | 3.5 | 277 | 7.9 | 629.1 | 484.4 | 244.2 | 661.8 | 423.5 | 649.2 | 296.5 | 393.7 | 593 | 432.3 | 306.1 | 269.7 | 201.5 | 264.3 | 239.8 | 211.1 | 274.8 | 398.2 | 277.4
1242 | 1035 | -7 | 0 | 0 | 263 | 242 | 236.8 | 220.4 | 262.3 | 47.8 | 19.5 | 71.9 | 3.5 | 272.2 | 8.3 | 627.3 | 484.3 | 241.9 | 660.3 | 421.3 | 647.9 | 294.7 | 391.3 | 590.4 | 430.2 | 305.6 | 269.2 | 201.7 | 263.9 | 239.4 | 211.1 | 274.4 | 397.9 | 277.4
1243 | 1036 | -7 | 0 | 0 | 262.4 | 241.8 | 236.2 | 219.8 | 262 | 47.7 | 19.5 | 71.8 | 3.7 | 271.3 | 8.8 | 625.6 | 483.4 | 239.7 | 659 | 418.6 | 646.5 | 293.3 | 389.2 | 587.8 | 428.2 | 305.1 | 268.6 | 201.8 | 263.4 | 238.9 | 211.2 | 274.1 | 397.6 | 277.3
1244 | 1037 | -7 | 0 | 0 | 262 | 241.4 | 235.5 | 219 | 261.6 | 47.5 | 19.5 | 71.7 | 3.3 | 274.5 | 8.9 | 623.7 | 482.9 | 237.4 | 657.5 | 416.3 | 645.2 | 292.4 | 387 | 585.4 | 426.5 | 304.6 | 268.1 | 202 | 263 | 238.5 | 211.2 | 273.7 | 397.4 | 277.3
1245 | 1038 | -7 | 0 | 0 | 261.6 | 241 | 235 | 218.2 | 261.1 | 47.4 | 19.5 | 71.5 | 3.6 | 274.9 | 9.7 | 621.8 | 485.3 | 235.4 | 656.2 | 414.9 | 644.1 | 290.8 | 384.9 | 582.9 | 425 | 304.1 | 267.7 | 202.1 | 262.5 | 238 | 211.2 | 273.3 | 397.1 | 277.2
1246 | 1039 | -7 | 0 | 0 | 261.2 | 240.6 | 234.5 | 217.8 | 260.3 | 47.4 | 19.5 | 71.4 | 3.5 | 270.7 | 9.4 | 620.2 | 485.6 | 233.1 | 654.8 | 412.8 | 643.1 | 289.5 | 382.7 | 580.4 | 423.3 | 303.6 | 267.4 | 202.2 | 261.9 | 237.4 | 211.2 | 273 | 396.8 | 277.2
1247 | 1040 | -7 | 0 | 0 | 260.8 | 240.2 | 233.8 | 217.4 | 259.6 | 47.3 | 19.5 | 71.3 | 3.5 | 285.6 | 8.7 | 618.4 | 483.4 | 231 | 653.5 | 411 | 641.9 | 289.1 | 380.4 | 578 | 421.6 | 303.1 | 267.1 | 202.4 | 261.5 | 237 | 211.2 | 272.5 | 396.5 | 277.2
1248 | 1041 | -7 | 0 | 0 | 260.4 | 239.7 | 233.3 | 217.1 | 258.2 | 47.2 | 19.5 | 71.2 | 3.4 | 277.5 | 8.1 | 616.7 | 485.9 | 228.7 | 652.2 | 409.4 | 641 | 288.2 | 378.8 | 575.8 | 420.2 | 302.7 | 266.7 | 202.5 | 261.1 | 236.6 | 211.2 | 272.2 | 396.2 | 277.1
1249 | 1042 | -7 | 0 | 0 | 259.8 | 239.2 | 232.9 | 216.7 | 256.4 | 47.1 | 19.5 | 71 | 3.3 | 279.7 | 7.5 | 615.1 | 487 | 226.5 | 650.7 | 408.2 | 640.3 | 287 | 376.8 | 573.6 | 418.8 | 302.2 | 266.6 | 202.6 | 260.7 | 236.2 | 211.2 | 271.8 | 395.9 | 277.1
1250 | 1043 | -7 | 0 | 0 | 259.3 | 238.9 | 232.3 | 216.4 | 254.5 | 46.9 | 19.5 | 70.9 | 3.5 | 281.6 | 6.6 | 613.6 | 486.4 | 224.6 | 649.7 | 406.9 | 639.5 | 286.6 | 375.4 | 571.4 | 417.1 | 301.7 | 266.4 | 202.8 | 260.2 | 235.8 | 211.3 | 271.4 | 395.6 | 277
1251 | 1044 | -7 | 0 | 0 | 259 | 238.5 | 231.7 | 216.1 | 253.2 | 46.8 | 19.5 | 70.7 | 3.1 | 279.5 | 6.2 | 612.3 | 480.9 | 222.9 | 648.7 | 405.7 | 638.8 | 285.9 | 373.4 | 569 | 415.6 | 301.3 | 265.9 | 202.9 | 259.8 | 235.4 | 211.3 | 271 | 395.3 | 277
1252 | 1045 | -7 | 0 | 0 | 258.7 | 238.2 | 231.3 | 215.7 | 252.3 | 46.6 | 19.5 | 70.6 | 3.7 | 283.4 | 6.3 | 611 | 480.5 | 221 | 647.4 | 404.4 | 637.9 | 283.6 | 371.3 | 566.7 | 414.3 | 300.8 | 265.4 | 203 | 259.3 | 235 | 211.3 | 270.7 | 395.1 | 276.9
1253 | 1046 | -7 | 0 | 0 | 258.4 | 237.8 | 230.9 | 215.5 | 251.4 | 46.6 | 19.5 | 70.5 | 4 | 292 | 6.4 | 609.5 | 480.3 | 218.8 | 646.2 | 402.8 | 637.1 | 282.1 | 369.6 | 564.5 | 412.4 | 300.3 | 265.1 | 203.1 | 258.8 | 234.6 | 211.3 | 270.3 | 394.8 | 276.9
1254 | 1047 | -7 | 0 | 0 | 258 | 237.6 | 230.4 | 215.2 | 250.9 | 46.6 | 19.6 | 70.3 | 3.6 | 292.2 | 6.4 | 607.9 | 479.8 | 216.8 | 644.8 | 400.8 | 636.3 | 280.6 | 367.3 | 562.3 | 411 | 299.9 | 265 | 203.3 | 258.2 | 234.2 | 211.3 | 269.9 | 394.5 | 276.8
1255 | 1048 | -7 | 0 | 0 | 257.7 | 237.2 | 229.9 | 215 | 250.6 | 46.6 | 19.5 | 70.2 | 3.7 | 284.7 | 7 | 606.4 | 476.9 | 215 | 643.5 | 399.3 | 635.2 | 279.9 | 365.4 | 560.1 | 409.4 | 299.5 | 264.8 | 203.4 | 257.8 | 233.8 | 211.3 | 269.5 | 394.2 | 276.8
1256 | 1049 | -7 | 0 | 0 | 257.3 | 236.7 | 229.5 | 214.7 | 250.4 | 46.6 | 19.6 | 70.1 | 3.9 | 293.1 | 7.3 | 605.1 | 476.8 | 213.1 | 642.3 | 397.7 | 634.4 | 279.7 | 363.2 | 557.9 | 408 | 299 | 264.3 | 203.5 | 257.5 | 233.3 | 211.3 | 269.1 | 393.9 | 276.7
1257 | 1050 | -7 | 0 | 0 | 256.9 | 236.3 | 229.2 | 214.1 | 250.5 | 46.5 | 19.6 | 69.9 | 3.8 | 288.4 | 6.9 | 603.7 | 475.3 | 211.6 | 641.1 | 396 | 633.6 | 278.7 | 361.5 | 555.7 | 406.3 | 298.6 | 263.7 | 203.6 | 257.1 | 232.9 | 211.3 | 268.8 | 393.7 | 276.7
1258 | 1051 | -7 | 0 | 0 | 256.5 | 235.9 | 228.9 | 213.8 | 250.7 | 46.3 | 19.6 | 69.8 | 4.2 | 276.5 | 6.5 | 602.3 | 476.5 | 209.5 | 640 | 394.2 | 632.6 | 278.8 | 360.2 | 553.4 | 404.5 | 298.2 | 263.2 | 203.8 | 256.7 | 232.4 | 211.3 | 268.4 | 393.4 | 276.6
1259 | 1052 | -7 | 0 | 0 | 256.1 | 235.6 | 228.5 | 213.4 | 251 | 46.2 | 19.6 | 69.6 | 4.6 | 266.6 | 6.5 | 601.1 | 476.1 | 207.9 | 638.9 | 393 | 631.9 | 279.1 | 358.5 | 551 | 403.1 | 297.7 | 262.6 | 203.9 | 256.3 | 232 | 211.3 | 268 | 393.1 | 276.6
1260 | 1053 | -7 | 0 | 0 | 255.7 | 235.2 | 228 | 213.1 | 251.4 | 46.1 | 19.6 | 69.5 | 4.9 | 274.5 | 7.3 | 599.9 | 474 | 206.4 | 637.8 | 392.1 | 631.2 | 279 | 356.7 | 548.5 | 401.7 | 297.3 | 262.2 | 204 | 255.9 | 231.6 | 211.2 | 267.7 | 392.8 | 276.5
1261 | 1054 | -7 | 0 | 0 | 255.2 | 234.8 | 227.4 | 212.6 | 251.4 | 46 | 19.6 | 69.4 | 4.5 | 269.7 | 7.9 | 598.7 | 471.3 | 205.2 | 636.5 | 389.7 | 630.2 | 278.5 | 354.6 | 546.1 | 400.3 | 296.9 | 261.9 | 204.1 | 255.5 | 231.2 | 211.2 | 267.3 | 392.5 | 276.4
1262 | 1055 | -7 | 0 | 0 | 254.8 | 234.5 | 226.9 | 212.3 | 251.4 | 45.8 | 19.6 | 69.3 | 4.2 | 277.7 | 8.1 | 597.2 | 471.4 | 204.6 | 635.1 | 386.7 | 629.5 | 277.8 | 352.2 | 543.6 | 398.8 | 296.4 | 261.7 | 204.2 | 255.1 | 230.8 | 211.2 | 267 | 392.2 | 276.4
1263 | 1056 | -7 | 0 | 0 | 254.4 | 234.3 | 226.4 | 212.1 | 251.6 | 45.8 | 19.6 | 69.1 | 4.2 | 278.6 | 8.3 | 595.9 | 469.9 | 204.4 | 633.7 | 383.9 | 628.6 | 277.1 | 350.1 | 541 | 397.3 | 296 | 261.6 | 204.4 | 254.7 | 230.4 | 211.1 | 266.6 | 391.9 | 276.4
1264 | 1057 | -7 | 0 | 0 | 253.9 | 234 | 226 | 211.6 | 251.5 | 45.7 | 19.6 | 69 | 4.3 | 270.7 | 8.2 | 594.5 | 466.5 | 203 | 632.4 | 380.1 | 627.6 | 276 | 348.3 | 538.5 | 396 | 295.6 | 261.3 | 204.5 | 254.3 | 229.9 | 211.1 | 266.2 | 391.6 | 276.3
1265 | 1058 | -7 | 0 | 0 | 253.5 | 233.7 | 225.5 | 211.1 | 251.1 | 45.6 | 19.6 | 68.9 | 3.9 | 277.4 | 7.9 | 592.8 | 466.8 | 201.4 | 631 | 377.7 | 626.8 | 275.2 | 346.4 | 536.1 | 394.9 | 295.2 | 261 | 204.6 | 253.8 | 229.5 | 211.1 | 265.9 | 391.3 | 276.2
1266 | 1059 | -7 | 0 | 0 | 253.1 | 233.4 | 225 | 210.6 | 251 | 45.6 | 19.6 | 68.8 | 4 | 268.9 | 7.4 | 591 | 465.5 | 199.8 | 629.6 | 376.3 | 625.9 | 274.1 | 344.3 | 533.7 | 393.2 | 294.8 | 260.6 | 204.7 | 253.4 | 229.1 | 211 | 265.5 | 391 | 276.2
1267 | 1060 | -7 | 0 | 0 | 252.6 | 233 | 224.5 | 210.1 | 250.8 | 45.6 | 19.6 | 68.7 | 3.9 | 258.2 | 6.5 | 589.4 | 463.6 | 198.1 | 628.3 | 375.4 | 625.1 | 273.3 | 342.5 | 531.4 | 391.9 | 294.4 | 260 | 204.8 | 252.9 | 228.6 | 211 | 265.1 | 390.7 | 276.1
1268 | 1061 | -7 | 0 | 0 | 252.2 | 232.6 | 224.1 | 209.6 | 250.7 | 45.5 | 19.6 | 68.5 | 4.7 | 247.3 | 5.8 | 587.9 | 463.5 | 196.5 | 627 | 374.1 | 624.6 | 273.1 | 341.4 | 529.1 | 390.5 | 293.9 | 259.7 | 204.9 | 252.6 | 228.2 | 210.9 | 264.8 | 390.5 | 276.1
1269 | 1062 | -7 | 0 | 0 | 251.9 | 232.2 | 223.7 | 209.2 | 250 | 45.5 | 19.6 | 68.4 | 5.1 | 236.1 | 5.4 | 586.5 | 465.1 | 195.4 | 625.7 | 372.9 | 624.2 | 272.5 | 339.9 | 526.9 | 389 | 293.5 | 259.2 | 205 | 252.2 | 227.8 | 210.8 | 264.4 | 390.2 | 276
1270 | 1063 | -7 | 0 | 0 | 251.3 | 231.6 | 223.3 | 208.7 | 248.9 | 45.4 | 19.6 | 68.3 | 4.6 | 229.2 | 4.7 | 585.1 | 466.3 | 194.1 | 624.5 | 370.8 | 624 | 271 | 338.1 | 524.7 | 387.5 | 293.1 | 258.9 | 205.1 | 251.9 | 227.4 | 210.8 | 264.1 | 389.9 | 275.9
1271 | 1064 | -7 | 0 | 0 | 250.8 | 231.2 | 222.8 | 208.2 | 247.7 | 45.2 | 19.6 | 68.2 | 4.9 | 243.8 | 5.5 | 583.4 | 465.7 | 192.6 | 623.2 | 369.5 | 623.6 | 269.8 | 336.2 | 522.6 | 386.1 | 292.7 | 258.7 | 205.3 | 251.5 | 227 | 210.7 | 263.7 | 389.6 | 275.8
1272 | 1065 | -7 | 0 | 0 | 250.4 | 230.9 | 222.4 | 207.7 | 246.5 | 45.1 | 19.6 | 68.1 | 5.1 | 251.4 | 6.4 | 581.9 | 464.8 | 191 | 621.9 | 368.2 | 623.1 | 268.1 | 335 | 520.5 | 384.7 | 292.3 | 258.4 | 205.4 | 251.2 | 226.7 | 210.7 | 263.4 | 389.4 | 275.8
1273 | 1066 | -7 | 0 | 0 | 250 | 230.6 | 222.1 | 207.3 | 245.2 | 45 | 19.6 | 68 | 4.8 | 260.2 | 6.9 | 580.6 | 464.5 | 189.6 | 620.9 | 367.2 | 622.2 | 267.3 | 333.4 | 518.5 | 383.3 | 291.9 | 258.1 | 205.5 | 250.9 | 226.3 | 210.6 | 263 | 389.1 | 275.7
1274 | 1067 | -7 | 0 | 0 | 249.6 | 230.4 | 222 | 207 | 244 | 44.9 | 19.6 | 67.8 | 4.1 | 255.2 | 7.2 | 579.3 | 456.4 | 188.2 | 619.8 | 365.8 | 620.9 | 267 | 331.7 | 516.5 | 381.8 | 291.4 | 257.8 | 205.6 | 250.5 | 226 | 210.6 | 262.7 | 388.8 | 275.7
1275 | 1068 | -7 | 0 | 0 | 249.1 | 230.2 | 221.8 | 206.5 | 244.1 | 44.8 | 19.6 | 67.7 | 4.1 | 241.5 | 7.3 | 578.1 | 446.9 | 186.9 | 618.6 | 364.7 | 619.9 | 265.7 | 329.6 | 514.5 | 380.5 | 291 | 257.6 | 205.7 | 250.2 | 225.7 | 210.5 | 262.4 | 388.5 | 275.6
1276 | 1069 | -7 | 0 | 0 | 248.6 | 230.1 | 221.6 | 206.1 | 244.4 | 44.8 | 19.6 | 67.6 | 4.1 | 249.4 | 7.4 | 576.7 | 447.2 | 185.6 | 617.3 | 364.2 | 618.6 | 264 | 327.8 | 512.5 | 379.3 | 290.6 | 257.5 | 205.8 | 249.9 | 225.3 | 210.5 | 262 | 388.2 | 275.6
1277 | 1070 | -7 | 0 | 0 | 248.1 | 229.8 | 221.2 | 205.8 | 244.8 | 44.7 | 19.6 | 67.4 | 4.2 | 251.5 | 7.9 | 575.5 | 447.4 | 184.3 | 615.9 | 362.1 | 617.4 | 262.6 | 325.5 | 510.6 | 377.6 | 290.2 | 257.5 | 205.9 | 249.5 | 224.9 | 210.5 | 261.7 | 387.9 | 275.5
1278 | 1071 | -7 | 0 | 0 | 247.7 | 229.5 | 220.7 | 205.4 | 245.1 | 44.7 | 19.6 | 67.2 | 4.6 | 231.1 | 8.3 | 574.4 | 441.2 | 182.8 | 614.5 | 359.8 | 616 | 262.1 | 323.8 | 508.6 | 376.3 | 289.8 | 257.3 | 206 | 249.2 | 224.5 | 210.4 | 261.3 | 387.7 | 275.4
1279 | 1072 | -7 | 0 | 0 | 247.4 | 229.2 | 220.3 | 205 | 245.1 | 44.7 | 19.6 | 67.1 | 5 | 225.6 | 8.4 | 573 | 433.1 | 181.5 | 613.1 | 357.3 | 614.9 | 260.6 | 321.7 | 506.7 | 374.8 | 289.4 | 257.2 | 206.1 | 248.9 | 224.1 | 210.4 | 261 | 387.4 | 275.4
1280 | 1073 | -7 | 0 | 0 | 247 | 229 | 219.9 | 204.7 | 245.2 | 44.6 | 19.6 | 66.9 | 4.9 | 243.2 | 7.8 | 571.5 | 434.1 | 180.5 | 611.6 | 356.2 | 613.6 | 259 | 319.3 | 504.8 | 373.4 | 289.1 | 256.9 | 206.2 | 248.6 | 223.7 | 210.3 | 260.6 | 387.1 | 275.3
1281 | 1074 | -7 | 0 | 0 | 246.5 | 228.8 | 219.4 | 204.3 | 245.1 | 44.6 | 19.6 | 66.8 | 4.7 | 241.8 | 8.4 | 570.1 | 435.1 | 179.4 | 610.3 | 354.7 | 611.8 | 258.4 | 317.4 | 503 | 372.1 | 288.7 | 256.6 | 206.3 | 248.1 | 223.4 | 210.3 | 260.3 | 386.8 | 275.2
1282 | 1075 | -7 | 0 | 0 | 246.1 | 228.5 | 219 | 204 | 244.9 | 44.5 | 19.6 | 66.7 | 4.7 | 243 | 8.3 | 568.8 | 429.3 | 178.1 | 608.7 | 353.3 | 610.2 | 256.9 | 316 | 501.2 | 371.2 | 288.3 | 256.5 | 206.4 | 247.8 | 223 | 210.3 | 259.9 | 386.5 | 275.2
1283 | 1076 | -7 | 0 | 0 | 245.8 | 228.1 | 218.5 | 203.6 | 244.8 | 44.5 | 19.6 | 66.5 | 3.9 | 253.4 | 7.2 | 567.4 | 425.6 | 176.9 | 607.1 | 351.5 | 608.6 | 256.2 | 314.6 | 499.7 | 369.9 | 287.9 | 256.3 | 206.5 | 247.4 | 222.5 | 210.2 | 259.6 | 386.2 | 275.1
1284 | 1077 | -7 | 0 | 0 | 245.5 | 227.7 | 218.1 | 203.3 | 244.5 | 44.4 | 19.6 | 66.3 | 3.9 | 246 | 6.7 | 565.7 | 425.8 | 175.7 | 605.5 | 349 | 607.2 | 254.9 | 312.4 | 498 | 368.4 | 287.5 | 255.9 | 206.6 | 247.1 | 222.2 | 210.1 | 259.2 | 386 | 275
1285 | 1078 | -7 | 0 | 0 | 245.3 | 227.3 | 217.6 | 203 | 244.2 | 44.4 | 19.6 | 66.2 | 3.9 | 236.7 | 7.1 | 563.9 | 427.7 | 174.5 | 604 | 348 | 606 | 253.6 | 309.9 | 496.2 | 366.5 | 287.2 | 255.4 | 206.7 | 246.8 | 221.8 | 210.1 | 258.9 | 385.7 | 275
1286 | 1079 | -7 | 0 | 0 | 245.1 | 226.8 | 217.1 | 202.6 | 243.9 | 44.3 | 19.6 | 66.1 | 3.6 | 237.6 | 8.5 | 562.5 | 429.4 | 173.5 | 602.9 | 346.2 | 604.3 | 252.9 | 308.1 | 494.3 | 365 | 286.8 | 255.3 | 206.8 | 246.5 | 221.5 | 210 | 258.6 | 385.4 | 274.9
1287 | 1080 | -7 | 0 | 0 | 245 | 226.5 | 216.8 | 202.3 | 243.6 | 44.3 | 19.6 | 66 | 4.3 | 242.9 | 9.8 | 561.1 | 430.4 | 172.9 | 601.6 | 344.8 | 603.1 | 251.8 | 306 | 492.4 | 364 | 286.4 | 255.1 | 206.9 | 246.1 | 221.2 | 209.9 | 258.2 | 385.1 | 274.8
1288 | 1081 | -7 | 0 | 0 | 244.9 | 226.2 | 216.8 | 201.9 | 243.4 | 44.2 | 19.6 | 65.9 | 3.8 | 238.3 | 10.6 | 559.5 | 432.1 | 171.8 | 600.1 | 343.4 | 601.2 | 251 | 303.3 | 490.5 | 363.1 | 286 | 254.8 | 207 | 245.7 | 220.9 | 209.8 | 257.9 | 384.8 | 274.8
1289 | 1082 | -7 | 0 | 0 | 244.6 | 225.8 | 216.4 | 201.5 | 243.3 | 44.1 | 19.6 | 65.8 | 3.8 | 239.5 | 10.6 | 558.3 | 432.4 | 171.1 | 598.8 | 341.8 | 598.9 | 250.2 | 300.8 | 488.5 | 361.8 | 285.6 | 254.3 | 207.1 | 245.4 | 220.7 | 209.8 | 257.6 | 384.5 | 274.7
1290 | 1083 | -7 | 0 | 0 | 244.3 | 225.5 | 215.9 | 201.2 | 242.9 | 44.1 | 19.6 | 65.7 | 3.9 | 239 | 10.1 | 556.9 | 431.5 | 170.2 | 597.4 | 340.2 | 597 | 248.6 | 298.6 | 486.6 | 360.4 | 285.3 | 254.2 | 207.1 | 245.1 | 220.4 | 209.7 | 257.2 | 384.3 | 274.6
1291 | 1084 | -7 | 0 | 0 | 244 | 225.3 | 215.6 | 200.9 | 242.5 | 44.1 | 19.6 | 65.6 | 4.2 | 238.5 | 9.7 | 555.3 | 432.4 | 169.3 | 596 | 338.8 | 595.3 | 247 | 296.3 | 484.7 | 359.3 | 284.9 | 253.9 | 207.2 | 244.7 | 220.1 | 209.7 | 256.9 | 384 | 274.5
1292 | 1085 | -7 | 0 | 0 | 243.7 | 225 | 215.5 | 200.5 | 242.2 | 44.1 | 19.6 | 65.5 | 4.2 | 239.6 | 9.6 | 553.8 | 432.5 | 168.5 | 594.6 | 337.2 | 594 | 246 | 294.3 | 482.9 | 358.1 | 284.5 | 253.1 | 207.3 | 244.5 | 219.8 | 209.6 | 256.6 | 383.7 | 274.5
1293 | 1086 | -7 | 0 | 0 | 243.4 | 224.4 | 215.1 | 200.1 | 241.9 | 44.1 | 19.6 | 65.3 | 4 | 235.6 | 9.2 | 552.3 | 433.7 | 167.6 | 593.2 | 336.9 | 592.8 | 244.6 | 292.7 | 481 | 356.7 | 284.2 | 252.4 | 207.4 | 244.2 | 219.5 | 209.5 | 256.2 | 383.4 | 274.4
1294 | 1087 | -7 | 0 | 0 | 243.1 | 224 | 214.8 | 199.8 | 241.7 | 44 | 19.6 | 65.3 | 4 | 236.5 | 8.8 | 551.1 | 434.2 | 167 | 592.1 | 337.2 | 591.5 | 244.3 | 291 | 479.2 | 355.3 | 283.8 | 251.9 | 207.5 | 243.9 | 219.1 | 209.5 | 256 | 383.2 | 274.3
1295 | 1088 | -7 | 0 | 0 | 242.8 | 223.5 | 214.4 | 199.5 | 241.5 | 43.9 | 19.6 | 65.2 | 4 | 239.6 | 8.6 | 549.8 | 433.3 | 166.4 | 590.9 | 337.7 | 590 | 243.4 | 288.8 | 477.3 | 354.3 | 283.4 | 251.4 | 207.6 | 243.7 | 218.9 | 209.4 | 255.6 | 382.9 | 274.3
1296 | 1089 | -7 | 0 | 0 | 242.4 | 223.1 | 213.8 | 199.3 | 241.2 | 43.9 | 19.6 | 65.1 | 3.7 | 240.4 | 8.5 | 548.5 | 432.6 | 165.5 | 589.4 | 337.5 | 588.3 | 242.6 | 286.4 | 475.4 | 353.1 | 283 | 251 | 207.7 | 243.4 | 218.6 | 209.3 | 255.3 | 382.6 | 274.2
1297 | 1090 | -7 | 0 | 0 | 242 | 222.9 | 213.3 | 199 | 241 | 43.8 | 19.6 | 65 | 3.6 | 237.7 | 8.1 | 547.3 | 426.5 | 164.7 | 588.3 | 336.1 | 587.1 | 241.6 | 284 | 473.5 | 352.2 | 282.7 | 250.4 | 207.8 | 243.1 | 218.2 | 209.2 | 254.9 | 382.3 | 274.1
1298 | 1091 | -7 | 0 | 0 | 241.7 | 222.6 | 212.9 | 198.8 | 240.8 | 43.7 | 19.6 | 64.9 | 3.8 | 235.8 | 7.4 | 546 | 421.4 | 164 | 587.2 | 334.8 | 586.3 | 240.5 | 282.1 | 471.8 | 351 | 282.3 | 249.8 | 207.9 | 242.8 | 217.9 | 209.1 | 254.7 | 382 | 274
1299 | 1092 | -7 | 0 | 0 | 241.3 | 222.3 | 212.6 | 198.6 | 240.6 | 43.6 | 19.6 | 64.8 | 3.5 | 207.7 | 6.5 | 544.5 | 422.1 | 163.3 | 586.1 | 334.2 | 585.1 | 239.2 | 280.2 | 470.2 | 350 | 281.9 | 249.4 | 207.9 | 242.5 | 217.5 | 209.1 | 254.3 | 381.8 | 273.9
1300 | 1093 | -7 | 0 | 0 | 241.1 | 221.9 | 212.3 | 198.4 | 240.3 | 43.6 | 19.6 | 64.8 | 3.4 | 209.5 | 5.4 | 542.9 | 424.5 | 163 | 584.6 | 333.6 | 583.6 | 239.1 | 278 | 468.6 | 348.6 | 281.6 | 249.1 | 208 | 242.2 | 217.2 | 209 | 254 | 381.5 | 273.9
1301 | 1094 | -7 | 0 | 0 | 240.9 | 221.6 | 211.9 | 198.2 | 240 | 43.5 | 19.6 | 64.7 | 3.4 | 251.9 | 4.6 | 541.5 | 425.3 | 162.4 | 583.4 | 332.9 | 581.9 | 238.6 | 276.6 | 466.8 | 347.3 | 281.2 | 248.9 | 208.1 | 242 | 216.9 | 208.9 | 253.7 | 381.2 | 273.8
1302 | 1095 | -7 | 0 | 0 | 240.5 | 221.3 | 211.5 | 197.9 | 239.6 | 43.5 | 19.6 | 64.6 | 3.6 | 232.4 | 4.3 | 540.1 | 425.5 | 161.6 | 582.4 | 331.8 | 580.2 | 237.7 | 275.1 | 464.9 | 346.2 | 280.8 | 248.6 | 208.2 | 241.7 | 216.5 | 208.8 | 253.4 | 380.9 | 273.7
1303 | 1096 | -7 | 0 | 0 | 240.1 | 221.2 | 211.1 | 197.6 | 239.2 | 43.4 | 19.6 | 64.4 | 3.5 | 212.1 | 5.5 | 539 | 424.6 | 160.9 | 581 | 330.4 | 578.9 | 236.1 | 273.3 | 463.1 | 345 | 280.5 | 248.2 | 208.3 | 241.4 | 216.2 | 208.8 | 253.1 | 380.6 | 273.6
1304 | 1097 | -7 | 0 | 0 | 239.8 | 220.9 | 210.6 | 197.3 | 239 | 43.4 | 19.6 | 64.3 | 3.3 | 226.1 | 6.5 | 537.9 | 424.4 | 160 | 579.8 | 327.6 | 577.6 | 235.2 | 271.2 | 461.4 | 343.8 | 280.1 | 247.9 | 208.3 | 241.1 | 215.9 | 208.7 | 252.8 | 380.3 | 273.6
1305 | 1098 | -7 | 0 | 0 | 239.5 | 220.7 | 210.2 | 197 | 238.8 | 43.4 | 19.7 | 64.1 | 3.4 | 223.2 | 6.3 | 536.7 | 422.3 | 159.1 | 578.6 | 325.7 | 575.9 | 234.8 | 269.7 | 459.6 | 342.9 | 279.8 | 247.5 | 208.4 | 240.8 | 215.6 | 208.6 | 252.5 | 380.1 | 273.5
1306 | 1099 | -7 | 0 | 0 | 239.1 | 220.4 | 209.9 | 196.7 | 238.7 | 43.3 | 19.7 | 64 | 3.5 | 237.3 | 5.8 | 535.4 | 420.5 | 158.3 | 577.4 | 324.9 | 574.1 | 234.2 | 268.1 | 458 | 341.9 | 279.5 | 247.3 | 208.5 | 240.4 | 215.3 | 208.5 | 252.2 | 379.8 | 273.4
1307 | 1100 | -7 | 0 | 0 | 238.9 | 220.1 | 209.8 | 196.5 | 238.7 | 43.2 | 19.7 | 63.9 | 3.7 | 223.9 | 5.7 | 534.3 | 418 | 157.5 | 576.2 | 323.7 | 572.1 | 233.5 | 265.9 | 456.4 | 340.4 | 279.1 | 247 | 208.6 | 240.1 | 215.1 | 208.5 | 251.8 | 379.5 | 273.4
1308 | 1101 | -7 | 0 | 0 | 238.5 | 219.7 | 209.7 | 196.3 | 238.5 | 43.1 | 19.7 | 63.7 | 3.3 | 230.8 | 5.6 | 533.1 | 418.1 | 156.6 | 575 | 322.4 | 570.3 | 232.4 | 264.1 | 454.7 | 339.1 | 278.8 | 246.9 | 208.6 | 239.8 | 214.8 | 208.4 | 251.5 | 379.2 | 273.3
1309 | 1102 | -7 | 0 | 0 | 238.1 | 219.3 | 209.3 | 196 | 238.1 | 43.1 | 19.7 | 63.7 | 3.7 | 229.8 | 5.4 | 532.1 | 418.5 | 155.8 | 573.8 | 321.6 | 568.4 | 231.8 | 262.6 | 453.1 | 338 | 278.5 | 246.6 | 208.7 | 239.5 | 214.6 | 208.3 | 251.2 | 378.9 | 273.2
1310 | 1103 | -7 | 0 | 0 | 237.7 | 219.1 | 208.8 | 195.7 | 237.8 | 43.1 | 19.7 | 63.6 | 4 | 220.7 | 5.4 | 531.1 | 417.3 | 154.8 | 572.6 | 320.4 | 566.3 | 230.7 | 260.5 | 451.5 | 336.7 | 278.1 | 246.3 | 208.8 | 239.1 | 214.3 | 208.3 | 250.9 | 378.6 | 273.1
1311 | 1104 | -7 | 0 | 0 | 237.4 | 218.6 | 208.3 | 195.5 | 237.4 | 43 | 19.7 | 63.5 | 3.8 | 214.1 | 5.4 | 530.1 | 411.7 | 153.8 | 571.4 | 318 | 564.6 | 229.7 | 258.8 | 450 | 335.9 | 277.8 | 246 | 208.9 | 238.9 | 213.9 | 208.2 | 250.6 | 378.4 | 273
1312 | 1105 | -7 | 0 | 0 | 237.2 | 218.2 | 207.9 | 195.3 | 237.1 | 43 | 19.7 | 63.4 | 3.8 | 214.9 | 5.5 | 528.6 | 409.1 | 153 | 570.1 | 316.7 | 562.9 | 229.2 | 258 | 448.5 | 335.1 | 277.5 | 245.9 | 208.9 | 238.6 | 213.6 | 208.2 | 250.3 | 378.1 | 273
1313 | 1106 | -7 | 0 | 0 | 236.9 | 217.7 | 207.5 | 195 | 236.7 | 43 | 19.7 | 63.3 | 4 | 217 | 5.5 | 527.3 | 411.8 | 152.1 | 568.8 | 316.6 | 561.3 | 228.1 | 256.1 | 447.1 | 334.4 | 277.2 | 245.9 | 209 | 238.3 | 213.4 | 208.1 | 250 | 377.8 | 272.9
1314 | 1107 | -7 | 0 | 0 | 236.6 | 217.3 | 207.2 | 194.7 | 236.4 | 42.9 | 19.7 | 63.2 | 3.7 | 231 | 5.5 | 526.4 | 412.9 | 151.2 | 567.5 | 316.4 | 559.3 | 228 | 254.8 | 445.5 | 333 | 276.9 | 245.5 | 209.1 | 238 | 213.1 | 208 | 249.7 | 377.6 | 272.8
1315 | 1108 | -7 | 0 | 0 | 236.2 | 217 | 207.2 | 194.4 | 236 | 42.8 | 19.7 | 63.1 | 3.4 | 232 | 5.2 | 525.5 | 411.3 | 150.5 | 566.4 | 315.8 | 557.5 | 227.2 | 253.8 | 443.6 | 332.1 | 276.5 | 245 | 209.2 | 237.7 | 212.8 | 207.9 | 249.4 | 377.3 | 272.7
1316 | 1109 | -7 | 0 | 0 | 235.9 | 216.6 | 207 | 194.1 | 235.5 | 42.7 | 19.7 | 63 | 3.7 | 236.9 | 4.8 | 524.5 | 408.5 | 149.8 | 565.1 | 315.6 | 555.8 | 226.6 | 252.7 | 441.6 | 331.1 | 276.2 | 244.6 | 209.2 | 237.5 | 212.4 | 207.9 | 249.1 | 377 | 272.6
1317 | 1110 | -7 | 0 | 0 | 235.5 | 216.3 | 206.5 | 193.9 | 235.1 | 42.7 | 19.7 | 62.9 | 3.8 | 256 | 5.4 | 523.3 | 408.6 | 148.9 | 563.8 | 314.9 | 554.1 | 225.5 | 251.5 | 439.7 | 329.9 | 275.9 | 244.1 | 209.3 | 237.2 | 212.1 | 207.8 | 248.7 | 376.7 | 272.6
1318 | 1111 | -7 | 0 | 0 | 235.2 | 216.1 | 206 | 193.7 | 234.6 | 42.7 | 19.7 | 62.8 | 3.4 | 246.9 | 6 | 522.1 | 407.5 | 148 | 562.5 | 313.8 | 552.5 | 224.4 | 249.8 | 437.8 | 329 | 275.6 | 243.7 | 209.4 | 236.9 | 211.7 | 207.8 | 248.5 | 376.4 | 272.5
1319 | 1112 | -7 | 0 | 0 | 235.1 | 215.8 | 205.6 | 193.4 | 234.1 | 42.7 | 19.7 | 62.7 | 3.7 | 231.5 | 6.2 | 520.7 | 402.1 | 147.3 | 561.1 | 312.3 | 551.1 | 223.3 | 248.3 | 435.8 | 327.9 | 275.3 | 243.5 | 209.4 | 236.5 | 211.4 | 207.8 | 248.2 | 376.1 | 272.4
1320 | 1113 | -7 | 0 | 0 | 234.9 | 215.6 | 205.4 | 193.2 | 233.6 | 42.6 | 19.7 | 62.7 | 3.4 | 245.9 | 6.7 | 519.7 | 401.9 | 146.4 | 559.9 | 310.9 | 549.6 | 223.4 | 247.2 | 433.9 | 326.9 | 274.9 | 243.3 | 209.5 | 236.1 | 211.2 | 207.7 | 247.9 | 375.9 | 272.3
1321 | 1114 | -7 | 0 | 0 | 234.4 | 215.4 | 205.2 | 193 | 233.3 | 42.6 | 19.7 | 62.6 | 3.5 | 246.7 | 6.7 | 518.6 | 397.7 | 145.4 | 558.7 | 308.7 | 548.2 | 222.8 | 245.4 | 431.9 | 325.9 | 274.6 | 243.2 | 209.6 | 235.7 | 210.9 | 207.6 | 247.6 | 375.6 | 272.2
1322 | 1115 | -7 | 0 | 0 | 234 | 215.2 | 204.8 | 192.8 | 233.1 | 42.5 | 19.7 | 62.6 | 3.6 | 248.3 | 6.6 | 517.5 | 392.6 | 144.5 | 557.5 | 307.2 | 547.1 | 222.2 | 243.9 | 430.1 | 325.2 | 274.3 | 243 | 209.6 | 235.4 | 210.7 | 207.6 | 247.3 | 375.3 | 272.2
1323 | 1116 | -7 | 0 | 0 | 233.6 | 215.1 | 204.3 | 192.6 | 232.7 | 42.4 | 19.7 | 62.5 | 3.4 | 249.4 | 6.3 | 516.1 | 392.8 | 143.7 | 556.2 | 306.3 | 546 | 221.5 | 242.5 | 428.4 | 323.9 | 274 | 242.9 | 209.7 | 235.3 | 210.4 | 207.5 | 247 | 375.1 | 272.1
1324 | 1117 | -7 | 0 | 0 | 233.3 | 215 | 204 | 192.3 | 232.3 | 42.3 | 19.7 | 62.5 | 3.9 | 260.7 | 5.7 | 514.6 | 394.2 | 142.9 | 554.9 | 305.6 | 544.9 | 221.1 | 241.1 | 426.9 | 322.9 | 273.7 | 242.7 | 209.8 | 235.1 | 210.1 | 207.5 | 246.7 | 374.8 | 272
1325 | 1118 | -7 | 0 | 0 | 233 | 214.8 | 203.7 | 192 | 232 | 42.3 | 19.7 | 62.4 | 4 | 259.7 | 5.8 | 513.2 | 394 | 141.9 | 553.5 | 304.7 | 543.4 | 220.7 | 239.8 | 425.3 | 321.9 | 273.3 | 242.5 | 209.8 | 234.9 | 209.7 | 207.5 | 246.4 | 374.5 | 271.9
1326 | 1119 | -7 | 0 | 0 | 232.8 | 214.6 | 203.6 | 191.7 | 231.7 | 42.2 | 19.7 | 62.3 | 3.9 | 248 | 6.6 | 511.8 | 390.3 | 140.9 | 552.3 | 303.9 | 541.9 | 220.5 | 238.4 | 423.6 | 321.1 | 273 | 242.3 | 209.9 | 234.6 | 209.4 | 207.4 | 246.2 | 374.2 | 271.8
1327 | 1120 | -7 | 0 | 0 | 232.5 | 214.5 | 203.7 | 191.5 | 231.5 | 42.2 | 19.7 | 62.3 | 3.6 | 243.3 | 7.4 | 510.5 | 392.9 | 140 | 551.1 | 303.4 | 540.9 | 220 | 236.7 | 422 | 320.3 | 272.7 | 242.1 | 210 | 234.4 | 209 | 207.4 | 245.8 | 373.9 | 271.7