## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-12
Test Date: | 2006-11-22
Ignition Time Relative to Thermal Data: | 190 | s
Ignition Time Relative to Electrical Data: | 190 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Template Plot
Template Plot

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 11-1 |  |  |  | Location A | Location C - 6-cable bundle 11-2 |  |  |  | Location C | Location E - 3+1 Air drop bundle 11-3 |  | Location G - 6-cable bundle 11-4 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable 1 | TC-2 Above Bundle | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -190 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.5 | 285.9 | 5.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
1 | -189 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.5 | 285.9 | 5.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
2 | -188 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.4 | 287 | 5.1 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
3 | -187 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.4 | 294.8 | 5.5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
4 | -186 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.6 | 292.6 | 5.9 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
5 | -185 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.5 | 274.8 | 6.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
6 | -184 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.3 | 272.4 | 6.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
7 | -183 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.3 | 267.5 | 5.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
8 | -182 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.2 | 289.9 | 5.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
9 | -181 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.2 | 280.2 | 5.1 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
10 | -180 | -6.9 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.1 | 275.5 | 4.9 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
11 | -179 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.1 | 292.6 | 4.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
12 | -178 | -6.8 | 0 | 0 | 17.3 | 17.4 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 281.3 | 4.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
13 | -177 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 282.8 | 4.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
14 | -176 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 0.9 | 288.3 | 4.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
15 | -175 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 246.4 | 4.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
16 | -174 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 238 | 4.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
17 | -173 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 238.7 | 4.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
18 | -172 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 240.8 | 4.5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
19 | -171 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 245.5 | 4.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
20 | -170 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 248.5 | 4.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
21 | -169 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 248.2 | 4.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
22 | -168 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.4 | 249.2 | 4.5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
23 | -167 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.2 | 248.6 | 4.6 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
24 | -166 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.1 | 249.1 | 4.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
25 | -165 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.9 | 17.8 | 21.5 | 17.6 | 1.2 | 248 | 4.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
26 | -164 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 237.6 | 3.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
27 | -163 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 217.9 | 3.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
28 | -162 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 204 | 3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
29 | -161 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 0.9 | 217.8 | 2.7 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
30 | -160 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 254.6 | 2.6 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
31 | -159 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 264.7 | 2.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
32 | -158 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1 | 240.2 | 2.1 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
33 | -157 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 212.1 | 2.1 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
34 | -156 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 198.6 | 1.9 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
35 | -155 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.8 | 17.8 | 21.5 | 17.6 | 1.1 | 192.7 | 1.5 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
36 | -154 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.6 | 1.2 | 192.1 | 1 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
37 | -153 | -7 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.6 | 1.2 | 192.4 | 0.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.2 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
38 | -152 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.6 | 1.4 | 192.3 | 0.5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.2 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
39 | -151 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.6 | 1.5 | 191.8 | 0.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
40 | -150 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.7 | 1.1 | 189.1 | 0.4 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
41 | -149 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.7 | 1.2 | 186.4 | 0.5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
42 | -148 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.7 | 1 | 186.3 | 0.3 | 16.1 | 16.6 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
43 | -147 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.7 | 1.1 | 188.5 | 0.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
44 | -146 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.7 | 1 | 204.5 | 0.1 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
45 | -145 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.7 | 1 | 243.5 | 0.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
46 | -144 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.8 | 21.5 | 17.7 | 1.1 | 273.4 | 1 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
47 | -143 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.7 | 1.1 | 268.3 | 1.8 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
48 | -142 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.7 | 1 | 264.2 | 2.8 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
49 | -141 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.3 | 17.8 | 17.9 | 21.5 | 17.7 | 1.1 | 281.5 | 2.8 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
50 | -140 | -6.9 | 0 | 0 | 17.2 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1.2 | 294 | 2.6 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
51 | -139 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 298.4 | 2.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
52 | -138 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1 | 298.8 | 2.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
53 | -137 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 299.5 | 2.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
54 | -136 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 298.2 | 3.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
55 | -135 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 293.7 | 3.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
56 | -134 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 295.9 | 4.3 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
57 | -133 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 298.1 | 4.6 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
58 | -132 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 323.6 | 4.8 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
59 | -131 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 325.6 | 4.8 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
60 | -130 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 290.6 | 5.9 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
61 | -129 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 316.2 | 6.2 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
62 | -128 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.7 | 307.5 | 6.1 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
63 | -127 | -6.8 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.7 | 308.4 | 5.6 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
64 | -126 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.7 | 327.8 | 5.4 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 16.9 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
65 | -125 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 340.1 | 5 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
66 | -124 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 348.7 | 4.3 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
67 | -123 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 349.1 | 3.3 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
68 | -122 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1 | 330.1 | 2.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
69 | -121 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 287.5 | 2.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
70 | -120 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.2 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 297.8 | 3.2 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
71 | -119 | -6.9 | 0 | 0 | 17.3 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 314.4 | 5.1 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
72 | -118 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.8 | 292.1 | 7.8 | 16.1 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
73 | -117 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 0.9 | 291.6 | 7.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
74 | -116 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.2 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 311.7 | 6.7 | 16.1 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
75 | -115 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 282.6 | 6.1 | 16.2 | 16.7 | 16.8 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
76 | -114 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.4 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 284 | 5.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
77 | -113 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 0.9 | 316.9 | 5.1 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
78 | -112 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1 | 299.1 | 5.3 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
79 | -111 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.2 | 17.9 | 18 | 21.5 | 17.8 | 0.8 | 284.6 | 6.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
80 | -110 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.2 | 17.9 | 18 | 21.5 | 17.7 | 0.8 | 290.4 | 6.7 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
81 | -109 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 0.8 | 288.2 | 7 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
82 | -108 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 0.9 | 310.5 | 7.2 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
83 | -107 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 307.4 | 7.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
84 | -106 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 0.9 | 302.2 | 6.4 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
85 | -105 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1 | 287.7 | 6.8 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
86 | -104 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 17.9 | 21.5 | 17.7 | 1 | 273.7 | 7.9 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
87 | -103 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 0.9 | 285.6 | 8.1 | 16.2 | 16.6 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
88 | -102 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1 | 272.9 | 9.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
89 | -101 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1 | 275.2 | 9.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
90 | -100 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 281.1 | 11.5 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
91 | -99 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 280.7 | 11.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.8 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
92 | -98 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.3 | 286.5 | 11.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
93 | -97 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 283.6 | 10.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
94 | -96 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 286.9 | 9.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
95 | -95 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1 | 269.7 | 9.5 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
96 | -94 | -6.9 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 270.6 | 8.6 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
97 | -93 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 268 | 8.6 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
98 | -92 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 276 | 8.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
99 | -91 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1 | 270.4 | 7.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
100 | -90 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 268.1 | 7.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
101 | -89 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 267.1 | 7.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.2 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
102 | -88 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.3 | 268.2 | 7.6 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
103 | -87 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 273.5 | 8.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
104 | -86 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.5 | 266.3 | 8.1 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
105 | -85 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.5 | 280.7 | 8.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
106 | -84 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 284.9 | 8.6 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
107 | -83 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 278.6 | 8.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
108 | -82 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.6 | 281.1 | 8.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
109 | -81 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.5 | 280.8 | 8.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
110 | -80 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.6 | 283.3 | 9.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
111 | -79 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.5 | 288.5 | 10.9 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
112 | -78 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 287.1 | 11.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
113 | -77 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.5 | 279.4 | 10.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
114 | -76 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 279.9 | 9.9 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
115 | -75 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.3 | 281.9 | 9.1 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
116 | -74 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.2 | 289.3 | 8.7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
117 | -73 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.3 | 286.4 | 8.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
118 | -72 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.3 | 282 | 8.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
119 | -71 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 290.1 | 8.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
120 | -70 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.4 | 294.6 | 8.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
121 | -69 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.4 | 295.1 | 8.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
122 | -68 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.4 | 283.5 | 8.5 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
123 | -67 | -6.8 | 0 | 0 | 17.4 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.2 | 288.8 | 8.4 | 16.2 | 16.7 | 17 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
124 | -66 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.8 | 1.1 | 294.9 | 8.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
125 | -65 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 297.2 | 7.9 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
126 | -64 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 295.4 | 7.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
127 | -63 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.1 | 284.5 | 7.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9 | 16.3 | 16.7 | 17.2 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
128 | -62 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 274.3 | 7.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
129 | -61 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 17.9 | 18 | 21.5 | 17.7 | 1.2 | 275 | 7.5 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
130 | -60 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.7 | 1.2 | 280.4 | 7 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
131 | -59 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.7 | 1.4 | 280.4 | 6.4 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
132 | -58 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.8 | 1.4 | 280.3 | 5.9 | 16.2 | 16.7 | 16.9 | 16.5 | 18.9 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
133 | -57 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.8 | 1.3 | 287.1 | 5.8 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
134 | -56 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.7 | 1.1 | 296.1 | 5.5 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
135 | -55 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.7 | 1.3 | 280 | 5.3 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
136 | -54 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.3 | 18 | 18 | 21.5 | 17.8 | 1.2 | 276.5 | 5.2 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
137 | -53 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.4 | 18 | 18 | 21.5 | 17.7 | 1.2 | 280.7 | 5.1 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
138 | -52 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.7 | 1.2 | 287.4 | 5.1 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
139 | -51 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.4 | 18 | 18 | 21.5 | 17.7 | 1.2 | 287.8 | 4.9 | 16.2 | 16.7 | 16.9 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
140 | -50 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.5 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.1 | 280.4 | 4.5 | 16.2 | 16.7 | 17 | 16.5 | 18.8 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
141 | -49 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.1 | 284.6 | 4.4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.7 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
142 | -48 | -6.8 | 0 | 0 | 17.5 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 0.9 | 277.8 | 4.5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
143 | -47 | -6.8 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1 | 269.3 | 4.3 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
144 | -46 | -6.9 | 0 | 0 | 17.5 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.7 | 1.2 | 282.8 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
145 | -45 | -6.8 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.1 | 295.1 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
146 | -44 | -6.9 | 0 | 0 | 17.6 | 17.5 | 17.5 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1 | 297.8 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
147 | -43 | -6.9 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1 | 298.6 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
148 | -42 | -6.8 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.2 | 294.5 | 4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
149 | -41 | -6.9 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.1 | 279.8 | 3.9 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
150 | -40 | -6.9 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.2 | 267.4 | 3.8 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
151 | -39 | -6.8 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.3 | 262.3 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
152 | -38 | -6.8 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.3 | 258.1 | 4.4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
153 | -37 | -6.8 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.3 | 261.3 | 4.4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.3 | 16.7 | 17.7 | 18.2 | 17.3
154 | -36 | -6.9 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.2 | 276.4 | 4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.8 | 18.2 | 17.3
155 | -35 | -6.9 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.1 | 270.6 | 3.7 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
156 | -34 | -3.6 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.3 | 252.2 | 3.5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
157 | -33 | -7.1 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.3 | 259.8 | 3.3 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
158 | -32 | -7.1 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.3 | 273.8 | 3.3 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
159 | -31 | -7.1 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.2 | 266.8 | 3.6 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
160 | -30 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.3 | 254.2 | 3.7 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
161 | -29 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.4 | 257 | 3.5 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
162 | -28 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.2 | 264 | 3.5 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
163 | -27 | -7 | 0 | 0 | 17.6 | 17.5 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.2 | 261.2 | 3.5 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
164 | -26 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 251.4 | 3.7 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
165 | -25 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.7 | 1.2 | 240.9 | 3.9 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
166 | -24 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 243.9 | 4.1 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
167 | -23 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.6 | 17.8 | 1.1 | 242.4 | 4.4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
168 | -22 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 246 | 4.5 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
169 | -21 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 251 | 4.5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
170 | -20 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 253.4 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
171 | -19 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 230.9 | 3.7 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
172 | -18 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 207.1 | 3.7 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
173 | -17 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 236.1 | 3.5 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
174 | -16 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 261.3 | 3.3 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
175 | -15 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 250.7 | 3.3 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
176 | -14 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 229.4 | 3.6 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
177 | -13 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.3 | 241.2 | 3.5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
178 | -12 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.3 | 258.5 | 3.4 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
179 | -11 | -7 | 0 | 0 | 17.6 | 17.6 | 17.7 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 259 | 3.5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.4 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
180 | -10 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 247.9 | 4.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
181 | -9 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 244.5 | 4.7 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
182 | -8 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.2 | 244 | 5.2 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
183 | -7 | -7 | 0 | 0 | 17.6 | 17.6 | 17.7 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.1 | 247.5 | 5.3 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
184 | -6 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.4 | 263 | 5.2 | 16.2 | 16.8 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.4 | 16.7 | 17.7 | 18.2 | 17.3
185 | -5 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.4 | 266.9 | 4.8 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
186 | -4 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.5 | 18 | 18.1 | 21.5 | 17.8 | 1.3 | 251.3 | 4.6 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
187 | -3 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.4 | 237.2 | 5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
188 | -2 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18.1 | 21.5 | 17.8 | 1.4 | 258 | 5 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
189 | -1 | -7 | 0 | 0 | 17.6 | 17.6 | 17.6 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.7 | 255.4 | 5.1 | 16.2 | 16.7 | 17 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 17 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
190 | 0 | 54.1 | 21.64 | 25.2959 | 17.6 | 17.6 | 17.7 | 17.5 | 18 | 18 | 21.5 | 17.8 | 1.8 | 256.1 | 5.1 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
191 | 1 | 430.5 | 172.2 | 201.2919 | 17.6 | 17.6 | 17.7 | 17.4 | 18 | 18 | 21.5 | 17.8 | 1.5 | 255.8 | 4.4 | 16.2 | 16.7 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17.1 | 17.5 | 16.7 | 17.7 | 18.2 | 17.3
192 | 2 | 706.3 | 282.52 | 330.2496 | 17.5 | 17.6 | 17.7 | 17.5 | 18 | 18 | 21.5 | 17.8 | 1.4 | 264.1 | 4.4 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.5 | 16.7 | 17.8 | 18.2 | 17.3
193 | 3 | 756.1 | 302.44 | 353.5349 | 17.5 | 17.6 | 17.7 | 17.5 | 18 | 18 | 21.5 | 17.8 | 1.3 | 261.9 | 5.1 | 16.2 | 16.8 | 17.1 | 16.5 | 18.9 | 16.3 | 16.8 | 17.3 | 16.3 | 18.7 | 16.6 | 16.9 | 16.7 | 17 | 17.5 | 16.7 | 17.8 | 18.2 | 17.3
194 | 4 | 708.1 | 283.24 | 331.0912 | 17.5 | 17.7 | 17.8 | 17.5 | 18 | 18.1 | 21.5 | 17.8 | 1.5 | 263.3 | 5.9 | 16.2 | 17.9 | 24.3 | 17.5 | 20.1 | 16.3 | 16.8 | 17.7 | 16.3 | 18.8 | 16.6 | 16.9 | 16.7 | 17.1 | 17.5 | 16.7 | 17.8 | 18.2 | 17.2
195 | 5 | 672.2 | 268.88 | 314.3052 | 17.6 | 17.7 | 17.9 | 17.6 | 19.2 | 18.1 | 21.5 | 17.8 | 1.6 | 263.5 | 6.7 | 16.2 | 36.2 | 77.4 | 24.6 | 29.6 | 16.3 | 22.8 | 36 | 16.3 | 21 | 16.6 | 16.9 | 16.7 | 17.1 | 17.5 | 16.7 | 17.8 | 18.2 | 17.3
196 | 6 | 652.2 | 260.88 | 304.9537 | 17.8 | 17.8 | 18.1 | 17.9 | 35.3 | 18.1 | 21.5 | 17.8 | 1.7 | 259.1 | 7.1 | 16.2 | 68.9 | 129.7 | 31.6 | 47.4 | 16.3 | 38.8 | 72.3 | 16.3 | 27.8 | 16.6 | 17 | 16.7 | 17.2 | 17.6 | 16.7 | 18 | 18.2 | 17.3
197 | 7 | 633.2 | 253.28 | 296.0697 | 18.1 | 18 | 18.5 | 18.2 | 67.2 | 18.2 | 21.5 | 17.8 | 1.8 | 256.5 | 7.5 | 16.3 | 118.4 | 210.1 | 39.2 | 72.9 | 16.4 | 67.2 | 120.5 | 16.4 | 37.9 | 16.6 | 17 | 16.7 | 17.4 | 17.7 | 16.7 | 18.1 | 18.2 | 17.3
198 | 8 | 624.2 | 249.68 | 291.8615 | 18.7 | 18.3 | 18.8 | 18.7 | 108.9 | 18.2 | 21.5 | 17.8 | 2 | 257.4 | 7.2 | 16.4 | 182.8 | 293.2 | 46.9 | 98.6 | 16.5 | 106.6 | 177.1 | 16.6 | 51 | 16.6 | 17.1 | 16.7 | 17.5 | 17.9 | 16.7 | 18.3 | 18.3 | 17.3
199 | 9 | 622.9 | 249.16 | 291.2537 | 19.4 | 18.9 | 19.8 | 19.8 | 143.3 | 18.3 | 21.5 | 17.8 | 2.2 | 240.8 | 6.7 | 16.5 | 247 | 355.5 | 56.6 | 129.1 | 16.7 | 143.5 | 224.8 | 16.9 | 66.8 | 16.6 | 17.2 | 16.7 | 17.7 | 18.1 | 16.7 | 18.5 | 18.4 | 17.3
200 | 10 | 625.4 | 250.16 | 292.4226 | 20.4 | 19.9 | 21.9 | 21.3 | 184.3 | 18.4 | 21.5 | 17.8 | 2.4 | 231.1 | 6.3 | 16.8 | 321.5 | 426.4 | 69.2 | 163.9 | 17.1 | 200 | 297.3 | 17.4 | 86.7 | 16.6 | 17.8 | 16.7 | 19.1 | 18.6 | 16.7 | 18.7 | 18.5 | 17.3
201 | 11 | 628.6 | 251.44 | 293.9189 | 21.7 | 21.1 | 24.4 | 23.4 | 244.9 | 18.4 | 21.5 | 17.8 | 2.7 | 247.3 | 5.8 | 17.1 | 387.4 | 483.6 | 78.7 | 187.4 | 17.6 | 263.9 | 366.5 | 18.3 | 110.6 | 16.6 | 19.1 | 16.7 | 22.2 | 20.4 | 16.6 | 19.1 | 18.6 | 17.3
202 | 12 | 630.9 | 252.36 | 294.9943 | 24.9 | 22.3 | 27.1 | 26.2 | 315.4 | 18.5 | 21.5 | 17.8 | 2.8 | 248.4 | 5.7 | 17.5 | 454.4 | 532.5 | 92.3 | 216.4 | 18.2 | 318.5 | 429.8 | 19.1 | 136.8 | 16.6 | 21 | 16.7 | 26.6 | 22.9 | 16.6 | 19.4 | 18.8 | 17.4
203 | 13 | 632.1 | 252.84 | 295.5554 | 29.2 | 24.7 | 30.5 | 29.6 | 361.1 | 18.5 | 21.5 | 17.8 | 2.4 | 240.9 | 5.8 | 18 | 512.4 | 579.7 | 106.3 | 245.7 | 19 | 361 | 477.1 | 20.2 | 163.3 | 16.7 | 23.8 | 16.7 | 31.7 | 24.9 | 16.6 | 19.8 | 19 | 17.6
204 | 14 | 633 | 253.2 | 295.9762 | 32.8 | 27.6 | 35.8 | 34.2 | 395.2 | 18.6 | 21.5 | 17.8 | 2.5 | 240 | 5.8 | 18.6 | 563 | 620.3 | 116.1 | 279.3 | 19.9 | 399 | 511.9 | 21.6 | 189.5 | 16.7 | 26.9 | 16.7 | 38.9 | 28.1 | 16.6 | 20.2 | 19.2 | 17.8
205 | 15 | 632.2 | 252.88 | 295.6021 | 36.6 | 30 | 41.7 | 39.4 | 405.2 | 18.7 | 21.5 | 17.8 | 2.6 | 241.7 | 5.9 | 19.4 | 608.6 | 662.1 | 126.5 | 306 | 20.9 | 435.3 | 556.2 | 23.5 | 211.1 | 16.8 | 30.2 | 16.7 | 46 | 31.2 | 16.6 | 20.9 | 19.5 | 18
206 | 16 | 622.1 | 248.84 | 290.8796 | 40.8 | 32.9 | 48 | 45 | 433 | 18.7 | 21.5 | 17.8 | 2.5 | 238.6 | 6.2 | 20.3 | 653.2 | 699.9 | 139.4 | 328.7 | 21.9 | 476.9 | 595.5 | 25.9 | 229.4 | 16.8 | 34.6 | 16.7 | 52.8 | 34 | 16.6 | 21.5 | 19.7 | 18.2
207 | 17 | 621.3 | 248.52 | 290.5056 | 45.8 | 37.5 | 53.6 | 50.1 | 465.4 | 18.8 | 21.5 | 17.9 | 2.3 | 243.1 | 6.2 | 21.3 | 698.1 | 732.3 | 150.7 | 352.3 | 22.9 | 512.1 | 622.7 | 28.4 | 249.9 | 16.9 | 39.6 | 16.7 | 59.2 | 37.6 | 16.6 | 22.2 | 20 | 18.4
208 | 18 | 606.3 | 242.52 | 283.4919 | 51 | 42 | 58.6 | 55 | 498.6 | 18.8 | 21.5 | 17.9 | 2.4 | 244.3 | 6 | 22.3 | 737 | 751.2 | 165.6 | 373.8 | 23.9 | 554.6 | 651.3 | 31.6 | 274.4 | 17.1 | 45 | 16.7 | 65.6 | 41.2 | 16.6 | 22.9 | 20.3 | 18.6
209 | 19 | 574.8 | 229.92 | 268.7632 | 56.2 | 47 | 63.6 | 60.2 | 532.1 | 18.8 | 21.5 | 18 | 2.4 | 243.5 | 5.4 | 23.4 | 761.2 | 770.3 | 180.4 | 392.6 | 24.9 | 587.8 | 670 | 35 | 299.4 | 17.2 | 50.4 | 16.7 | 71.2 | 44.4 | 16.7 | 23.7 | 20.7 | 18.8
210 | 20 | 537.4 | 214.96 | 251.2759 | 61.6 | 52.2 | 69.4 | 66.3 | 557.4 | 18.9 | 21.5 | 18.1 | 2.2 | 238.2 | 4.8 | 24.6 | 786.4 | 782.6 | 193.3 | 406.2 | 25.9 | 616 | 694.7 | 38.4 | 321.9 | 17.5 | 55.2 | 16.8 | 77.7 | 48.2 | 16.7 | 24.6 | 21.1 | 19.1
211 | 21 | 507.6 | 203.04 | 237.3421 | 67.5 | 56.9 | 76.9 | 72.4 | 559.9 | 18.9 | 21.5 | 18.2 | 2.2 | 249.4 | 4.5 | 25.8 | 806.7 | 786.2 | 199.3 | 419.6 | 27 | 633.4 | 708.5 | 41.6 | 345.3 | 17.7 | 60.5 | 16.8 | 84.2 | 52 | 16.7 | 25.1 | 21.4 | 19.4
212 | 22 | 493.5 | 197.4 | 230.7492 | 73.3 | 61.2 | 83.8 | 78.5 | 555.8 | 19 | 21.5 | 18.3 | 2.1 | 241.3 | 4.1 | 27 | 824.7 | 798.7 | 209.9 | 431.3 | 28.1 | 650.8 | 729.3 | 44.8 | 365.1 | 18 | 65.9 | 16.8 | 91.3 | 56 | 16.7 | 25.8 | 21.8 | 19.7
213 | 23 | 489.5 | 195.8 | 228.8789 | 78.5 | 66.2 | 90.9 | 84.5 | 554.2 | 19 | 21.5 | 18.5 | 2.1 | 212.7 | 3.6 | 28.2 | 837.9 | 799.7 | 217.3 | 444.7 | 29.3 | 660.8 | 740.8 | 47.8 | 383.3 | 18.2 | 69.8 | 16.8 | 97.2 | 59.7 | 16.7 | 26.7 | 22.3 | 19.9
214 | 24 | 489.3 | 195.72 | 228.7854 | 83.7 | 71.5 | 97.3 | 89.8 | 562.8 | 19.1 | 21.5 | 18.8 | 2.2 | 184.7 | 3.3 | 29.5 | 835.2 | 787.8 | 220.4 | 453 | 30.5 | 672.3 | 741.6 | 50.8 | 399.6 | 18.5 | 74.5 | 16.8 | 104.1 | 64.4 | 16.7 | 27.5 | 22.7 | 20.2
215 | 25 | 490.4 | 196.16 | 229.2997 | 88.5 | 77.2 | 102.1 | 94.8 | 554.2 | 19.1 | 21.5 | 19.1 | 2.3 | 204.8 | 2.8 | 30.9 | 836.4 | 787.4 | 225.3 | 461.7 | 31.8 | 680.2 | 742.1 | 53.5 | 413.9 | 18.8 | 79 | 16.8 | 110.7 | 68.8 | 16.8 | 28.5 | 23.1 | 20.4
216 | 26 | 491.6 | 196.64 | 229.8608 | 94.1 | 82.5 | 106.5 | 100.2 | 564.1 | 19.2 | 21.5 | 19.6 | 2.3 | 241.3 | 3 | 32.3 | 851.5 | 790.8 | 236.7 | 467.6 | 33.3 | 691 | 752.5 | 56.4 | 429.2 | 19.2 | 83.2 | 16.8 | 116.9 | 72.9 | 16.8 | 29.5 | 23.4 | 20.7
217 | 27 | 489.2 | 195.68 | 228.7386 | 99.7 | 87.3 | 111.3 | 105.5 | 571.5 | 19.2 | 21.5 | 20.1 | 2 | 247.3 | 3.3 | 33.8 | 862 | 791.8 | 249.4 | 484.8 | 34.9 | 692.3 | 744.4 | 59 | 444.9 | 19.5 | 87.6 | 16.8 | 122.7 | 77 | 16.8 | 30.3 | 23.8 | 21.1
218 | 28 | 489.7 | 195.88 | 228.9724 | 104.5 | 91.7 | 116.4 | 110.5 | 559.9 | 19.2 | 21.5 | 20.6 | 1.9 | 240.7 | 3.5 | 35.2 | 864.4 | 791 | 251.3 | 493.4 | 36.5 | 691.7 | 746.9 | 61.6 | 456.7 | 19.9 | 91.7 | 16.8 | 129.2 | 82.7 | 16.8 | 31.3 | 24.2 | 21.4
219 | 29 | 488.6 | 195.44 | 228.4581 | 109.5 | 96.3 | 121.8 | 115.3 | 542.5 | 19.3 | 21.5 | 21 | 2.3 | 245.7 | 4.4 | 36.7 | 858.5 | 786 | 252.6 | 507.8 | 38.2 | 683.5 | 739.9 | 63.8 | 469.5 | 20.3 | 96 | 16.8 | 134.7 | 86.1 | 16.9 | 32.1 | 24.6 | 21.7
220 | 30 | 487.5 | 195 | 227.9438 | 114 | 100.2 | 127.1 | 118.8 | 522.7 | 19.3 | 21.5 | 21.5 | 2.7 | 246.8 | 6.4 | 38.3 | 858.4 | 793.1 | 258.2 | 516.1 | 40 | 677.5 | 738.9 | 66 | 478.6 | 20.6 | 100.4 | 16.8 | 139.3 | 89.2 | 16.9 | 33.1 | 25 | 22
221 | 31 | 487.5 | 195 | 227.9438 | 118 | 103.5 | 131 | 122.2 | 505 | 19.4 | 21.5 | 21.9 | 2.6 | 233.4 | 6.6 | 40 | 871 | 808.9 | 270.6 | 516.4 | 41.9 | 670.4 | 743.9 | 68 | 487.6 | 21 | 104 | 16.8 | 144.2 | 92.6 | 17 | 34 | 25.4 | 22.3
222 | 32 | 485.7 | 194.28 | 227.1021 | 121.5 | 106.9 | 133.8 | 126.1 | 496.3 | 19.4 | 21.5 | 22.4 | 2.4 | 235.8 | 6.4 | 41.8 | 871.6 | 810.2 | 273.2 | 513.3 | 44 | 664.8 | 753.3 | 69.8 | 493.8 | 21.4 | 107.9 | 16.9 | 148.4 | 96.4 | 17 | 35 | 25.7 | 22.6
223 | 33 | 484.9 | 193.96 | 226.7281 | 124.4 | 109.5 | 136.6 | 129.4 | 493.2 | 19.4 | 21.5 | 22.9 | 2.1 | 254 | 5.2 | 43.6 | 858.2 | 795.8 | 276.3 | 508.6 | 46.2 | 661.5 | 766.3 | 71.5 | 498.4 | 21.8 | 111.4 | 16.9 | 151.9 | 99.9 | 17.1 | 35.8 | 26.1 | 22.9
224 | 34 | 484.4 | 193.76 | 226.4943 | 127.1 | 112 | 138.5 | 132.4 | 483.2 | 19.5 | 21.5 | 23.3 | 2 | 283.3 | 4.3 | 45.4 | 836.4 | 782.3 | 277.1 | 507.3 | 48.5 | 647.8 | 755.4 | 72.8 | 499.1 | 22.3 | 114.5 | 16.9 | 154.7 | 102.8 | 17.1 | 36.7 | 26.5 | 23.2
225 | 35 | 483.3 | 193.32 | 225.9799 | 129.5 | 113.9 | 141.1 | 135.4 | 471.2 | 19.5 | 21.5 | 23.7 | 1.8 | 280.5 | 4.5 | 47.4 | 834.1 | 771 | 282.4 | 503.2 | 51.1 | 635.6 | 736.9 | 74.3 | 503.1 | 22.7 | 117.3 | 16.9 | 157.6 | 106 | 17.2 | 37.3 | 26.9 | 23.5
226 | 36 | 483 | 193.2 | 225.8397 | 131.9 | 115.7 | 144.3 | 137.8 | 462.4 | 19.6 | 21.5 | 24.1 | 2.2 | 260.2 | 5.1 | 49.4 | 822.2 | 768.9 | 284.9 | 500.2 | 53.8 | 625 | 730 | 75.9 | 509.8 | 23.1 | 120.2 | 16.9 | 159.8 | 108.4 | 17.2 | 38.2 | 27.2 | 23.7
227 | 37 | 482 | 192.8 | 225.3721 | 134.1 | 117.7 | 147 | 140.4 | 448.5 | 19.6 | 21.5 | 24.6 | 2.5 | 261.9 | 5.5 | 51.4 | 803 | 760.4 | 287.7 | 500.7 | 56.7 | 610.7 | 716.2 | 77.2 | 512 | 23.6 | 123.4 | 17 | 161.9 | 111.2 | 17.3 | 38.8 | 27.5 | 24
228 | 38 | 482.4 | 192.96 | 225.5591 | 136.5 | 119.4 | 149.8 | 142.7 | 436.9 | 19.6 | 21.5 | 25.1 | 2.6 | 271 | 6 | 53.4 | 776.1 | 745 | 287.2 | 500.6 | 59.8 | 595.6 | 697.2 | 78.2 | 513.9 | 24.1 | 126.5 | 17 | 163.4 | 115.5 | 17.3 | 39.7 | 27.8 | 24.2
229 | 39 | 481.1 | 192.44 | 224.9513 | 139.6 | 122.2 | 152.6 | 144.6 | 437.8 | 19.7 | 21.5 | 25.5 | 2.5 | 254.2 | 5.8 | 55.4 | 764.9 | 742.4 | 292.3 | 498.5 | 63.1 | 591.1 | 703.4 | 79.5 | 518.7 | 24.5 | 129.1 | 17 | 164.9 | 118.3 | 17.4 | 40.5 | 28.1 | 24.5
230 | 40 | 481 | 192.4 | 224.9045 | 141.7 | 124.9 | 155.5 | 146.5 | 437.7 | 19.7 | 21.5 | 26 | 2.5 | 250.7 | 5.8 | 57.4 | 755.9 | 739 | 297.4 | 494.3 | 66.4 | 581.2 | 695.2 | 80.5 | 517 | 25 | 131.9 | 17 | 166.3 | 122 | 17.4 | 41.4 | 28.4 | 24.8
231 | 41 | 479.3 | 191.72 | 224.1096 | 143.5 | 127.6 | 157.9 | 148.3 | 431.7 | 19.8 | 21.5 | 26.5 | 2.2 | 273.4 | 5.9 | 59.3 | 738.8 | 725.2 | 303.9 | 496.1 | 70 | 573.7 | 690.1 | 81.7 | 519.7 | 25.5 | 134.6 | 17.1 | 167.7 | 125.3 | 17.5 | 41.9 | 28.7 | 24.9
232 | 42 | 477.9 | 191.16 | 223.455 | 145.2 | 130.2 | 160.4 | 149.8 | 426.1 | 19.8 | 21.5 | 27 | 2.1 | 251 | 5.9 | 61.2 | 736.7 | 730.7 | 310.7 | 500.3 | 73.6 | 561.9 | 681.2 | 82.6 | 523.2 | 26 | 136.6 | 17.1 | 168.1 | 128.3 | 17.5 | 42.5 | 29 | 25.1
233 | 43 | 477.3 | 190.92 | 223.1745 | 147 | 131.7 | 162.9 | 151 | 417.4 | 19.8 | 21.5 | 27.4 | 2.4 | 277.8 | 5.3 | 63.1 | 734.8 | 732 | 310.6 | 501.1 | 77.5 | 557.7 | 688.8 | 83.8 | 525.5 | 26.5 | 138.6 | 17.1 | 168.4 | 130.7 | 17.6 | 43.3 | 29.3 | 25.3
234 | 44 | 473.8 | 189.52 | 221.538 | 148.2 | 133.3 | 165.1 | 151.9 | 413.4 | 19.9 | 21.5 | 27.9 | 2.5 | 278.7 | 4.7 | 65 | 741.8 | 720.8 | 318 | 509.2 | 81.4 | 549.2 | 672.9 | 84.9 | 529.5 | 27 | 140.4 | 17.1 | 168.9 | 132.2 | 17.7 | 43.9 | 29.6 | 25.3
235 | 45 | 473.3 | 189.32 | 221.3042 | 150 | 134 | 166.5 | 152.9 | 407.4 | 20 | 21.5 | 28.3 | 2.5 | 253.6 | 4.3 | 66.9 | 750.9 | 720.5 | 323.9 | 527.2 | 85.5 | 547.6 | 667 | 86.2 | 538.8 | 27.5 | 142.2 | 17.2 | 169.5 | 133.7 | 17.7 | 44.4 | 29.9 | 25.5
236 | 46 | 474.4 | 189.76 | 221.8185 | 152.3 | 135.3 | 167.1 | 153.7 | 422.7 | 19.9 | 21.5 | 28.7 | 2.3 | 260.8 | 5.2 | 68.7 | 768.1 | 730.9 | 332.7 | 539.3 | 89.7 | 552.8 | 673.2 | 87.7 | 548.1 | 28 | 143.6 | 17.2 | 171 | 135.5 | 17.8 | 45 | 30.2 | 25.9
237 | 47 | 472.3 | 188.92 | 220.8366 | 154.1 | 137.2 | 168 | 155.2 | 421.9 | 20 | 21.5 | 29 | 2.6 | 263.2 | 5.9 | 70.5 | 788.5 | 745 | 336.6 | 549.9 | 93.8 | 550 | 669.3 | 88.9 | 555.4 | 28.4 | 145 | 17.3 | 171.9 | 137.2 | 17.9 | 45.7 | 30.5 | 26.2
238 | 48 | 472.8 | 189.12 | 221.0704 | 155.4 | 138.7 | 169.5 | 156.9 | 410.7 | 20.1 | 21.5 | 29.4 | 2.5 | 259.7 | 5.2 | 72.2 | 809.8 | 758.5 | 344.2 | 558.2 | 97.9 | 549.1 | 663.6 | 90.1 | 561.6 | 28.9 | 146.2 | 17.3 | 172.7 | 139.2 | 18 | 46 | 30.8 | 26.4
239 | 49 | 473.1 | 189.24 | 221.2107 | 156.4 | 139.6 | 170.3 | 158.1 | 407.9 | 20.2 | 21.5 | 29.7 | 2.6 | 260.3 | 4.4 | 73.9 | 820.9 | 754.8 | 350.5 | 564.2 | 101.9 | 543.3 | 653.6 | 91.1 | 565.8 | 29.4 | 147.7 | 17.3 | 173.6 | 141.7 | 18 | 46.7 | 31.2 | 26.7
240 | 50 | 472.5 | 189 | 220.9301 | 157.4 | 139.8 | 171.1 | 158.9 | 405.9 | 20.2 | 21.5 | 30.1 | 2.6 | 259.8 | 4.4 | 75.5 | 828 | 743.6 | 351.9 | 576.2 | 105.9 | 542.6 | 653.5 | 92.3 | 570.4 | 29.8 | 149.3 | 17.4 | 174.6 | 142.8 | 18.1 | 47.7 | 31.5 | 27
241 | 51 | 471.7 | 188.68 | 220.556 | 158.1 | 141.1 | 172.1 | 159.4 | 399.9 | 20.3 | 21.5 | 30.4 | 2.6 | 260 | 4.7 | 77.1 | 821.8 | 735 | 348.8 | 574.4 | 109.7 | 533.4 | 639.3 | 93 | 572.3 | 30.3 | 150.9 | 17.4 | 175.8 | 144 | 18.2 | 48.3 | 31.9 | 27.2
242 | 52 | 471 | 188.4 | 220.2287 | 159.2 | 142.3 | 172.8 | 159.6 | 391.8 | 20.3 | 21.5 | 30.7 | 2.5 | 270.6 | 5 | 78.8 | 814.9 | 731.5 | 346.1 | 574.5 | 113.4 | 525.5 | 630.6 | 93.7 | 573.6 | 30.7 | 152.2 | 17.5 | 176.6 | 145.3 | 18.3 | 48.7 | 32.2 | 27.5
243 | 53 | 471.6 | 188.64 | 220.5093 | 160 | 142.1 | 173.5 | 159.7 | 388.8 | 20.3 | 21.5 | 31 | 2.5 | 262.5 | 5.5 | 80.4 | 801.9 | 727.7 | 341.3 | 576.6 | 116.9 | 517.5 | 621.9 | 94.2 | 574.7 | 31.2 | 153.2 | 17.5 | 176.9 | 146.9 | 18.3 | 49.4 | 32.5 | 27.8
244 | 54 | 471.3 | 188.52 | 220.369 | 160.4 | 141.9 | 174.5 | 160.2 | 388.2 | 20.4 | 21.5 | 31.4 | 2.3 | 250.1 | 5.7 | 82.1 | 812.5 | 751.7 | 343.5 | 592.1 | 120.3 | 516.6 | 636.5 | 94.9 | 578.2 | 31.7 | 154.4 | 17.6 | 177 | 147.3 | 18.4 | 49.8 | 32.8 | 27.9
245 | 55 | 470.8 | 188.32 | 220.1352 | 161.1 | 141.6 | 174.4 | 160.7 | 395.8 | 20.4 | 21.5 | 31.7 | 2.3 | 253.5 | 5.4 | 83.8 | 828.4 | 760.6 | 346.8 | 608.9 | 123.4 | 519.6 | 643.5 | 96.1 | 585.3 | 32.1 | 155.2 | 17.6 | 177.3 | 148.2 | 18.5 | 50.5 | 33.1 | 28.1
246 | 56 | 470.9 | 188.36 | 220.182 | 161.9 | 142.4 | 174.9 | 161.2 | 400.9 | 20.5 | 21.5 | 32.1 | 2.6 | 266.1 | 5.6 | 85.4 | 837.8 | 742.1 | 345.5 | 618.2 | 126.4 | 519.5 | 631.4 | 97.3 | 591.9 | 32.5 | 155.9 | 17.7 | 177.9 | 149.3 | 18.6 | 51 | 33.5 | 28.5
247 | 57 | 471 | 188.4 | 220.2287 | 161.9 | 143.6 | 176 | 161.7 | 398.2 | 20.6 | 21.5 | 32.6 | 2.3 | 264.5 | 6.1 | 87.2 | 839.3 | 732.1 | 344.5 | 628.4 | 129.2 | 518.6 | 618 | 98.3 | 598.8 | 33 | 156.4 | 17.7 | 178.3 | 150 | 18.7 | 51.7 | 33.9 | 28.8
248 | 58 | 470.7 | 188.28 | 220.0885 | 162.5 | 144.9 | 177 | 162.4 | 395.7 | 20.6 | 21.5 | 33 | 2.5 | 266.3 | 6 | 88.9 | 848.1 | 752 | 345.5 | 632.8 | 131.8 | 515.4 | 619.1 | 99.1 | 602.2 | 33.4 | 157.1 | 17.7 | 178.7 | 150.7 | 18.8 | 52.2 | 34.3 | 28.9
249 | 59 | 470.4 | 188.16 | 219.9482 | 163.6 | 145.5 | 177.9 | 162.8 | 403 | 20.6 | 21.5 | 33.4 | 2.3 | 257.8 | 6 | 90.6 | 855.9 | 771.3 | 345.9 | 631 | 134.3 | 523.7 | 638.9 | 100.4 | 604.6 | 33.8 | 158 | 17.8 | 179 | 151.6 | 18.9 | 52.8 | 34.6 | 29.2
250 | 60 | 470.5 | 188.2 | 219.995 | 163.8 | 145.5 | 179.3 | 163.1 | 407.4 | 20.8 | 21.5 | 33.7 | 2.2 | 258.2 | 6 | 92.2 | 862.7 | 771 | 343.9 | 630.4 | 136.6 | 529.5 | 650.8 | 101.6 | 610.1 | 34.2 | 158.7 | 17.8 | 179 | 152.5 | 19 | 53.3 | 35.1 | 29
251 | 61 | 470.4 | 188.16 | 219.9482 | 164.6 | 145.7 | 179.6 | 163.5 | 404.1 | 20.7 | 21.4 | 34 | 2.4 | 259.6 | 6.1 | 93.8 | 868.5 | 774.3 | 342.1 | 635.1 | 139 | 531.2 | 655.7 | 102.5 | 613.8 | 34.6 | 159.3 | 17.9 | 179.2 | 153.1 | 19.1 | 53.9 | 35.4 | 29.5
252 | 62 | 470.1 | 188.04 | 219.8079 | 165.2 | 146.4 | 180.2 | 164.6 | 409 | 20.8 | 21.4 | 34.2 | 2.5 | 257.9 | 5.9 | 95.3 | 873.5 | 780.9 | 341 | 637 | 141.2 | 530.6 | 659.1 | 103.5 | 615.7 | 35 | 160.1 | 18 | 179.4 | 153.5 | 19.2 | 54.4 | 35.8 | 29.8
253 | 63 | 469.3 | 187.72 | 219.4339 | 165.2 | 147 | 180.1 | 165.2 | 408.2 | 20.8 | 21.4 | 34.4 | 2.4 | 258.6 | 5.6 | 96.9 | 879.6 | 775.5 | 338.6 | 637.6 | 143.4 | 530.3 | 662.7 | 104.4 | 616.6 | 35.5 | 160.8 | 18 | 179.8 | 154.4 | 19.3 | 55 | 36.2 | 29.9
254 | 64 | 470.6 | 188.24 | 220.0417 | 165.1 | 147.5 | 180 | 165.4 | 409.2 | 20.9 | 21.4 | 34.7 | 2.2 | 258 | 5.3 | 98.4 | 879.6 | 777.2 | 335.7 | 639.9 | 145.4 | 529.7 | 663.2 | 105.3 | 617.9 | 35.9 | 161.6 | 18.1 | 180.5 | 155.4 | 19.4 | 55.5 | 36.5 | 30.3
255 | 65 | 470 | 188 | 219.7612 | 164.8 | 147.7 | 180.3 | 165.5 | 414.7 | 21 | 21.4 | 34.9 | 2.3 | 260 | 5.4 | 99.8 | 884.2 | 779.3 | 333.1 | 641.5 | 147.4 | 536.5 | 671.2 | 106.4 | 622 | 36.3 | 162.3 | 18.1 | 181.3 | 156 | 19.5 | 56.1 | 36.9 | 30.4
256 | 66 | 470 | 188 | 219.7612 | 164.7 | 148.2 | 180.3 | 165.7 | 416.3 | 21 | 21.4 | 35.2 | 2.1 | 260.2 | 5.6 | 101.3 | 890.1 | 781.7 | 330.9 | 647.9 | 149.3 | 536.1 | 669.6 | 107.5 | 627.7 | 36.7 | 163.1 | 18.2 | 181.4 | 157.2 | 19.6 | 56.6 | 37.3 | 30.6
257 | 67 | 470 | 188 | 219.7612 | 165.2 | 148.7 | 180.2 | 165.5 | 419.6 | 21 | 21.4 | 35.4 | 2 | 244.8 | 5.5 | 102.8 | 895.4 | 795.4 | 329.4 | 654.3 | 151.2 | 543.1 | 688.4 | 108.9 | 633.2 | 37 | 163.8 | 18.2 | 181.6 | 158 | 19.7 | 57.1 | 37.7 | 31
258 | 68 | 470 | 188 | 219.7612 | 165.1 | 149.3 | 180.2 | 166 | 434.4 | 21 | 21.4 | 35.6 | 2.5 | 245 | 5.3 | 104.5 | 899.4 | 804 | 328.6 | 652.3 | 153.1 | 552.3 | 706.1 | 110.4 | 638.2 | 37.4 | 164.8 | 18.3 | 182.2 | 158.3 | 19.8 | 57.8 | 38 | 31.3
259 | 69 | 469.3 | 187.72 | 219.4339 | 165.2 | 150.3 | 180.4 | 166.4 | 443.4 | 21 | 21.4 | 35.9 | 2.4 | 257.1 | 5.2 | 106.1 | 899 | 813.4 | 328.2 | 650.7 | 155 | 559.2 | 711.7 | 112 | 642 | 37.8 | 165.3 | 18.4 | 182.5 | 158.7 | 19.9 | 58.3 | 38.4 | 31.5
260 | 70 | 468.9 | 187.56 | 219.2468 | 165.5 | 150.8 | 180.9 | 166.8 | 447.9 | 21 | 21.4 | 36.2 | 2.3 | 258.8 | 5.1 | 107.8 | 905.8 | 822.1 | 327.4 | 648.5 | 157 | 566 | 725.4 | 113.5 | 645.2 | 38.2 | 165.5 | 18.4 | 183.3 | 159.1 | 20 | 58.6 | 38.9 | 31.7
261 | 71 | 469.7 | 187.88 | 219.6209 | 164.8 | 151.1 | 181 | 167.2 | 452.3 | 21 | 21.4 | 36.5 | 2.5 | 262.3 | 4.7 | 109.5 | 907.9 | 827.2 | 326.3 | 641.2 | 159 | 569.4 | 734.9 | 115 | 646.2 | 38.5 | 166 | 18.5 | 183.7 | 159.5 | 20.1 | 58.8 | 39.3 | 32
262 | 72 | 470.6 | 188.24 | 220.0417 | 165.5 | 151.9 | 181.4 | 167.2 | 451 | 21 | 21.4 | 36.7 | 2.3 | 262.4 | 4.1 | 111.5 | 911.4 | 822.3 | 324.8 | 639 | 161 | 573.6 | 740 | 116.9 | 646.3 | 38.9 | 166.6 | 18.6 | 184.9 | 159.8 | 20.2 | 59.3 | 39.8 | 32.2
263 | 73 | 470.3 | 188.12 | 219.9014 | 166.5 | 151.9 | 180.9 | 168.1 | 455 | 21.1 | 21.4 | 36.9 | 2.5 | 254.6 | 3.7 | 113.6 | 912.7 | 806.7 | 323.2 | 643.3 | 163.1 | 578.5 | 740.8 | 118.3 | 648.5 | 39.3 | 167.3 | 18.6 | 185.4 | 161.4 | 20.3 | 59.8 | 40.3 | 32.4
264 | 74 | 469.2 | 187.68 | 219.3871 | 166.4 | 152.1 | 180.6 | 168.4 | 449.4 | 21.1 | 21.4 | 37.1 | 2.6 | 254.3 | 3.5 | 116 | 914.2 | 804.6 | 321.4 | 644.2 | 165.2 | 580.7 | 738.6 | 119.9 | 651.7 | 39.6 | 168 | 18.7 | 186 | 162.9 | 20.4 | 60.4 | 40.8 | 32.7
265 | 75 | 469.5 | 187.8 | 219.5274 | 166.7 | 153 | 180 | 168.2 | 443.7 | 21.2 | 21.4 | 37.3 | 2.4 | 258 | 3.5 | 118.8 | 921.3 | 815.1 | 319.8 | 644.2 | 167.2 | 580.6 | 740.8 | 121.3 | 651.7 | 40 | 168.4 | 18.8 | 187.2 | 163.3 | 20.6 | 60.8 | 41.3 | 32.9
266 | 76 | 470.3 | 188.12 | 219.9014 | 166.1 | 154 | 180.7 | 167.8 | 446.1 | 21.3 | 21.3 | 37.5 | 2.6 | 262.9 | 3.6 | 121.9 | 923.7 | 822.2 | 318.6 | 640.9 | 169.3 | 583.2 | 746.9 | 122.8 | 653.8 | 40.3 | 168.9 | 18.8 | 187.9 | 163.7 | 20.7 | 61.3 | 41.7 | 33.2
267 | 77 | 470.5 | 188.2 | 219.995 | 166.1 | 155.4 | 181.4 | 167.8 | 447.9 | 21.3 | 21.3 | 37.7 | 2.8 | 256.9 | 3.8 | 125.8 | 918.7 | 828.1 | 318.4 | 641.5 | 171.4 | 588.7 | 752.3 | 124.3 | 655.4 | 40.6 | 169.1 | 18.9 | 188.7 | 163.6 | 20.8 | 61.9 | 42.1 | 33.4
268 | 78 | 470.3 | 188.12 | 219.9014 | 166.7 | 156.2 | 181.7 | 168.1 | 447.8 | 21.3 | 21.3 | 37.9 | 2.7 | 246.2 | 4 | 127.9 | 920.7 | 820.3 | 318.1 | 638.9 | 173.4 | 584.6 | 745.6 | 125.2 | 654.7 | 41 | 169.6 | 19 | 189.9 | 163.6 | 20.9 | 62.2 | 42.6 | 33.7
269 | 79 | 469.5 | 187.8 | 219.5274 | 167.2 | 157.4 | 182.7 | 168.5 | 442.2 | 21.3 | 21.3 | 38.1 | 2.6 | 254.2 | 4 | 129.3 | 923.1 | 825 | 318 | 633.5 | 175.4 | 580.8 | 743.1 | 126.2 | 655.4 | 41.3 | 170.4 | 19.1 | 190.6 | 163.9 | 21 | 62.5 | 43 | 34
270 | 80 | 470.8 | 188.32 | 220.1352 | 167.9 | 158.4 | 183.4 | 169.1 | 443.2 | 21.4 | 21.3 | 38.4 | 2.7 | 267.5 | 4.1 | 131.3 | 908.6 | 827.1 | 318.3 | 632.5 | 177.3 | 582.3 | 743.1 | 127.5 | 657.5 | 41.6 | 170.9 | 19.1 | 191.4 | 165.1 | 21.2 | 63 | 43.4 | 34.2
271 | 81 | 468.5 | 187.4 | 219.0598 | 168.9 | 159.1 | 183.2 | 169.7 | 442.8 | 21.4 | 21.3 | 38.6 | 2.6 | 268 | 4.8 | 132.9 | 897.9 | 835.3 | 319.2 | 637.7 | 179 | 582.7 | 750.2 | 128.9 | 659.1 | 42 | 171.3 | 19.2 | 192.2 | 166.4 | 21.3 | 63.5 | 43.9 | 34.4
272 | 82 | 468.5 | 187.4 | 219.0598 | 169.1 | 159.7 | 183.9 | 169.9 | 443.3 | 21.5 | 21.3 | 38.7 | 2.3 | 254.1 | 4.8 | 134.7 | 901.8 | 840.3 | 320.6 | 646.4 | 180.9 | 582.3 | 750.9 | 130.3 | 661.5 | 42.3 | 171.9 | 19.3 | 192.9 | 167.6 | 21.4 | 63.9 | 44.4 | 34.7
273 | 83 | 470.5 | 188.2 | 219.995 | 169.1 | 159.1 | 184.2 | 170.5 | 442.3 | 21.5 | 21.3 | 38.9 | 2.7 | 247.7 | 5.1 | 136.6 | 898.7 | 844.2 | 322.3 | 648.2 | 182.8 | 581.5 | 751.2 | 131.7 | 663.7 | 42.6 | 172.6 | 19.4 | 192.8 | 168.9 | 21.5 | 64.4 | 44.9 | 35
274 | 84 | 470.6 | 188.24 | 220.0417 | 169.4 | 158.6 | 184.3 | 171.2 | 447.3 | 21.6 | 21.3 | 39 | 2.5 | 257.1 | 5 | 138.5 | 882.6 | 835.3 | 323.2 | 642.2 | 184.7 | 582 | 758.4 | 133.1 | 662.4 | 42.9 | 173.3 | 19.4 | 192.9 | 169.7 | 21.6 | 64.7 | 45.4 | 35.2
275 | 85 | 469.7 | 187.88 | 219.6209 | 169.8 | 158.6 | 184.8 | 171.8 | 458 | 21.6 | 21.3 | 39.2 | 2.3 | 272 | 5.2 | 140.2 | 864 | 820.9 | 323.4 | 635.3 | 186.5 | 583.7 | 760.3 | 134.2 | 660.7 | 43.3 | 173.7 | 19.5 | 192.5 | 169.8 | 21.8 | 65.1 | 45.8 | 35.5
276 | 86 | 469.6 | 187.84 | 219.5741 | 170.7 | 159.4 | 184.5 | 171.7 | 459.2 | 21.6 | 21.3 | 39.3 | 2.5 | 251.7 | 5 | 141.7 | 860.6 | 832.1 | 324.2 | 636.3 | 188.5 | 586.1 | 758.9 | 135.6 | 661.6 | 43.6 | 174.3 | 19.6 | 192.7 | 169.7 | 21.9 | 65.3 | 46.3 | 35.8
277 | 87 | 468 | 187.2 | 218.826 | 171.5 | 160.2 | 184.7 | 171.6 | 467.4 | 21.6 | 21.3 | 39.5 | 2.6 | 259.7 | 5 | 143.7 | 871 | 848.2 | 326.1 | 641.1 | 190.8 | 593.7 | 765.3 | 137.1 | 665.3 | 43.9 | 175.3 | 19.7 | 193.5 | 169.6 | 22 | 65.6 | 46.7 | 36
278 | 88 | 468.2 | 187.28 | 218.9195 | 172.3 | 161.2 | 185.4 | 171.9 | 472.8 | 21.7 | 21.3 | 39.6 | 2.5 | 238.5 | 4.6 | 146.4 | 875.6 | 845.1 | 328.2 | 644.2 | 193.3 | 596 | 766.2 | 138.6 | 668.2 | 44.2 | 175.8 | 19.8 | 194.6 | 169.8 | 22.2 | 66 | 47.2 | 36.2
279 | 89 | 468.6 | 187.44 | 219.1066 | 173 | 162.4 | 185.9 | 171.9 | 474.6 | 21.7 | 21.3 | 39.8 | 2.7 | 234.9 | 4.4 | 148.6 | 870.6 | 834.9 | 329.6 | 641 | 196 | 600.9 | 771.5 | 140 | 668.6 | 44.5 | 176.1 | 19.8 | 195.7 | 169.9 | 22.3 | 66.6 | 47.8 | 36.5
280 | 90 | 468.5 | 187.4 | 219.0598 | 173 | 163.3 | 187.5 | 172.2 | 470.6 | 21.7 | 21.3 | 39.9 | 2.4 | 263.2 | 4.3 | 150.9 | 852.5 | 825.7 | 330.4 | 630.9 | 198.9 | 594.1 | 762.4 | 141 | 666 | 44.8 | 176.2 | 19.9 | 197.2 | 169.7 | 22.4 | 67 | 48.3 | 36.7
281 | 91 | 468.3 | 187.32 | 218.9663 | 172.9 | 163.6 | 189 | 172.8 | 476.8 | 21.8 | 21.3 | 40.1 | 2.4 | 267.8 | 4.5 | 154.5 | 840.1 | 814.1 | 331.1 | 623.1 | 201.5 | 591.7 | 758.3 | 142.1 | 664.6 | 45.1 | 177 | 20 | 198.1 | 169.4 | 22.6 | 67.4 | 48.7 | 37
282 | 92 | 468.4 | 187.36 | 219.013 | 173.7 | 164.3 | 190.2 | 173.4 | 469.7 | 21.8 | 21.3 | 40.2 | 2.6 | 264.1 | 4.9 | 157.9 | 838.7 | 816.7 | 331.8 | 615 | 204.3 | 584.6 | 751 | 143 | 664 | 45.4 | 177.6 | 20.1 | 199.1 | 169.3 | 22.7 | 67.8 | 49.1 | 37.3
283 | 93 | 469 | 187.6 | 219.2936 | 174.3 | 164.9 | 190.9 | 173.4 | 464.2 | 21.8 | 21.2 | 40.3 | 2.6 | 263.3 | 5 | 160.5 | 842.7 | 820.6 | 333.5 | 621.8 | 207.4 | 580.9 | 741.6 | 144.2 | 664.6 | 45.7 | 178 | 20.2 | 200.3 | 169.4 | 22.8 | 68.4 | 49.6 | 37.5
284 | 94 | 468.7 | 187.48 | 219.1533 | 174.5 | 165 | 191.5 | 174 | 453 | 21.9 | 21.2 | 40.4 | 2.2 | 257.8 | 4.8 | 162.8 | 850.6 | 818.5 | 336.4 | 635.4 | 210.6 | 577.1 | 718.6 | 145.2 | 667.6 | 46 | 178.6 | 20.2 | 201 | 171.1 | 23 | 68.8 | 50 | 37.8
285 | 95 | 468.4 | 187.36 | 219.013 | 174.9 | 165.4 | 192 | 174.5 | 444.8 | 22 | 21.2 | 40.5 | 2.4 | 257.2 | 5 | 165 | 855.1 | 802.1 | 339 | 645.7 | 213.5 | 576.3 | 712.7 | 146.6 | 671.5 | 46.3 | 178.9 | 20.3 | 201.3 | 172.1 | 23.1 | 69.3 | 50.4 | 38
286 | 96 | 468.5 | 187.4 | 219.0598 | 175.7 | 165.3 | 192.7 | 174.6 | 430.4 | 22 | 21.2 | 40.6 | 2.4 | 260.9 | 5.2 | 167.1 | 856.2 | 785 | 341.1 | 656.2 | 215.8 | 571.9 | 695.4 | 147.5 | 673.8 | 46.5 | 179.2 | 20.4 | 201.5 | 172.6 | 23.3 | 69.7 | 50.9 | 38.3
287 | 97 | 468.5 | 187.4 | 219.0598 | 176.1 | 166 | 193.1 | 174.9 | 428.9 | 22.1 | 21.2 | 40.7 | 2.6 | 260.4 | 5.2 | 169.7 | 858.6 | 798.8 | 343.1 | 664.7 | 217.5 | 572.5 | 681.1 | 148.7 | 676.4 | 46.9 | 179.6 | 20.5 | 202.8 | 173.4 | 23.4 | 70.2 | 51.3 | 38.5
288 | 98 | 469.3 | 187.72 | 219.4339 | 176.4 | 166.5 | 192.7 | 175.2 | 434.2 | 22.1 | 21.2 | 40.8 | 2.7 | 262.9 | 5.3 | 172.8 | 868.7 | 789.6 | 345.4 | 677.9 | 219 | 576 | 678.2 | 150.1 | 680.6 | 47.2 | 180.1 | 20.6 | 202.6 | 174 | 23.6 | 70.7 | 51.8 | 38.8
289 | 99 | 467.8 | 187.12 | 218.7325 | 176.9 | 167.4 | 193.7 | 175.8 | 429.4 | 22.1 | 21.2 | 41 | 2.6 | 267 | 5.4 | 175.3 | 870.7 | 796.9 | 347.4 | 692.6 | 220.3 | 578.4 | 674.4 | 151.2 | 684.1 | 47.5 | 180.5 | 20.7 | 203 | 174.7 | 23.7 | 71.1 | 52.3 | 39
290 | 100 | 467.2 | 186.88 | 218.452 | 177.7 | 168 | 194.6 | 176.1 | 428.1 | 22.2 | 21.2 | 41.1 | 2.6 | 272.8 | 5.4 | 177.5 | 877.1 | 780 | 349.5 | 707 | 221.6 | 583.6 | 661.1 | 152.5 | 689.9 | 47.8 | 180.9 | 20.8 | 203.1 | 175.6 | 23.9 | 71.6 | 52.8 | 39.3
291 | 101 | 469.4 | 187.76 | 219.4806 | 178.2 | 168.7 | 195.4 | 176.2 | 428.2 | 22.2 | 21.2 | 41.3 | 2.2 | 274.5 | 5.1 | 179.5 | 879.1 | 786.5 | 352.1 | 716.1 | 222.9 | 586.8 | 662 | 153.7 | 694.3 | 48.1 | 181.2 | 20.8 | 203.2 | 176.4 | 24 | 71.9 | 53.3 | 39.5
292 | 102 | 469.6 | 187.84 | 219.5741 | 178.8 | 169.1 | 196.4 | 176.5 | 432 | 22.3 | 21.2 | 41.4 | 2.1 | 275.8 | 4.9 | 181.9 | 886.5 | 800.1 | 355.7 | 718 | 224.3 | 592 | 680.4 | 154.9 | 698 | 48.5 | 181.7 | 20.9 | 203.2 | 176.5 | 24.2 | 72.3 | 53.8 | 39.7
293 | 103 | 469.6 | 187.84 | 219.5741 | 178.9 | 169.5 | 197.2 | 177 | 431.1 | 22.3 | 21.2 | 41.6 | 2.5 | 271.4 | 4.6 | 184.1 | 886.7 | 806 | 359.6 | 720.1 | 226 | 590.9 | 677 | 155.7 | 699.7 | 48.8 | 182.2 | 21 | 203.3 | 176.8 | 24.3 | 72.6 | 54.2 | 40
294 | 104 | 468.4 | 187.36 | 219.013 | 178.9 | 170.1 | 197.5 | 177.1 | 431.4 | 22.4 | 21.2 | 41.7 | 2.5 | 270.8 | 4.4 | 186.2 | 887.3 | 803.1 | 363.6 | 726.6 | 228 | 596.4 | 678.1 | 156.5 | 702 | 49.2 | 182.7 | 21.1 | 203.6 | 177.6 | 24.5 | 73 | 54.7 | 40.2
295 | 105 | 468 | 187.2 | 218.826 | 179 | 171 | 198 | 177.4 | 430.9 | 22.4 | 21.2 | 41.8 | 2.3 | 271.2 | 4.1 | 187.9 | 882.2 | 808.2 | 368.3 | 729.5 | 229.8 | 598.6 | 681.5 | 157.2 | 703.9 | 49.5 | 183.2 | 21.2 | 204.4 | 178.3 | 24.6 | 73.4 | 55.3 | 40.5
296 | 106 | 468 | 187.2 | 218.826 | 179.5 | 171.5 | 198.5 | 177.9 | 435.5 | 22.5 | 21.2 | 41.9 | 2.3 | 271.5 | 4 | 189.2 | 877.5 | 820.1 | 373.4 | 725.2 | 231.7 | 605.4 | 707.4 | 158.2 | 706.9 | 49.8 | 183.6 | 21.3 | 204.7 | 178.7 | 24.8 | 73.8 | 55.8 | 40.8
297 | 107 | 468.4 | 187.36 | 219.013 | 180.1 | 171.8 | 198.6 | 178.6 | 438.3 | 22.5 | 21.2 | 41.9 | 2.3 | 267.2 | 4.3 | 190.4 | 877.6 | 828.4 | 377.7 | 722.6 | 233.6 | 609 | 707.2 | 159.1 | 709.9 | 50.2 | 184.3 | 21.4 | 205 | 178.8 | 24.9 | 74.1 | 56.3 | 41
298 | 108 | 467.8 | 187.12 | 218.7325 | 180.3 | 172.3 | 198.2 | 178.4 | 438 | 22.5 | 21.2 | 42 | 2.4 | 264.5 | 4.8 | 191.3 | 875.5 | 819.9 | 381.4 | 726.5 | 235.3 | 614.7 | 703.6 | 160.1 | 712.1 | 50.5 | 185.1 | 21.4 | 205.1 | 179.1 | 25.1 | 74.5 | 56.8 | 41.2
299 | 109 | 468.2 | 187.28 | 218.9195 | 180.6 | 173.4 | 197.9 | 178.5 | 445.7 | 22.6 | 21.2 | 42.1 | 2.6 | 258.9 | 5 | 192.1 | 879.2 | 814 | 384.7 | 736.8 | 237.2 | 616.9 | 700.1 | 161 | 713.2 | 50.8 | 185.9 | 21.5 | 205.2 | 179.2 | 25.3 | 74.9 | 57.4 | 41.5
300 | 110 | 469 | 187.6 | 219.2936 | 180.8 | 173.7 | 197.4 | 178.4 | 448 | 22.7 | 21.2 | 42.2 | 2.7 | 254.4 | 5 | 193.1 | 884.4 | 803.8 | 388 | 745.6 | 239.1 | 611.7 | 691.7 | 161.5 | 712.3 | 51.1 | 186.5 | 21.6 | 205.3 | 179.5 | 25.4 | 75.3 | 58.1 | 41.7
301 | 111 | 468.5 | 187.4 | 219.0598 | 180.8 | 174.5 | 197.8 | 179.1 | 437.6 | 22.7 | 21.2 | 42.3 | 2.8 | 255.2 | 4.9 | 194 | 881 | 801.7 | 390.9 | 747.1 | 240.4 | 596.8 | 673.2 | 161.1 | 709.6 | 51.5 | 187 | 21.7 | 206.1 | 179.9 | 25.6 | 75.7 | 58.6 | 41.9
302 | 112 | 469.2 | 187.68 | 219.3871 | 181.1 | 175 | 198.5 | 179.8 | 425.6 | 22.8 | 21.2 | 42.3 | 2.4 | 255.3 | 4.9 | 195 | 879.7 | 786.9 | 394 | 748.6 | 241.5 | 592.2 | 658.9 | 161.2 | 709.5 | 51.9 | 187.5 | 21.8 | 206.5 | 180.1 | 25.8 | 76.1 | 59.1 | 42.2
303 | 113 | 468.9 | 187.56 | 219.2468 | 181.7 | 175.4 | 199.2 | 179.8 | 424.4 | 22.8 | 21.2 | 42.4 | 2.4 | 255.3 | 4.9 | 195.9 | 881.6 | 795.3 | 397.7 | 753.5 | 242.1 | 597.3 | 665.4 | 162 | 712.2 | 52.2 | 187.7 | 21.9 | 207.2 | 180.4 | 25.9 | 76.4 | 59.5 | 42.5
304 | 114 | 469 | 187.6 | 219.2936 | 182.7 | 176.1 | 199.9 | 179.5 | 431.2 | 22.8 | 21.2 | 42.4 | 2.2 | 255 | 4.9 | 196.9 | 883.6 | 804.3 | 401.4 | 753 | 242.6 | 601.8 | 677 | 162.9 | 714.4 | 52.6 | 187.9 | 22 | 207.5 | 180.6 | 26.1 | 76.9 | 60 | 42.7
305 | 115 | 468.8 | 187.52 | 219.2001 | 183.6 | 176.6 | 201 | 179.6 | 436.8 | 22.9 | 21.2 | 42.6 | 2.3 | 255.2 | 4.9 | 198 | 884.4 | 805.4 | 405.6 | 751.2 | 243 | 606.3 | 673.8 | 164 | 715.9 | 52.9 | 188.1 | 22.1 | 207.4 | 180.9 | 26.2 | 77.3 | 60.5 | 43
306 | 116 | 468.8 | 187.52 | 219.2001 | 184.2 | 176.6 | 202 | 179.7 | 431.1 | 23 | 21.2 | 42.7 | 2.3 | 255.7 | 4.8 | 199 | 886 | 818.1 | 409.7 | 749.6 | 243.2 | 602.9 | 674.6 | 164.5 | 714.7 | 53.3 | 188.4 | 22.2 | 206.8 | 181.5 | 26.4 | 77.7 | 61.1 | 43.2
307 | 117 | 468.7 | 187.48 | 219.1533 | 184.4 | 176.4 | 202.7 | 180.1 | 432.6 | 23 | 21.2 | 42.8 | 2.4 | 255.8 | 4.6 | 200.2 | 891.8 | 830.5 | 413.6 | 742.1 | 243.2 | 604 | 695.7 | 165.4 | 716.3 | 53.7 | 188.6 | 22.3 | 206.7 | 181.7 | 26.6 | 78 | 61.7 | 43.5
308 | 118 | 468.2 | 187.28 | 218.9195 | 184.6 | 175.7 | 202.3 | 180.4 | 438 | 23.1 | 21.2 | 42.9 | 2.5 | 253.1 | 4.5 | 201.2 | 889.3 | 831.8 | 417.6 | 732.5 | 242.9 | 602.2 | 699.1 | 166.5 | 714.5 | 54 | 188.8 | 22.4 | 206.4 | 182.1 | 26.7 | 78.4 | 62.2 | 43.7
309 | 119 | 469.6 | 187.84 | 219.5741 | 183.9 | 176 | 202.5 | 180.9 | 437.6 | 23.2 | 21.1 | 43.1 | 2.7 | 252.6 | 4.3 | 202.2 | 885.5 | 824.1 | 421.3 | 730.7 | 242.8 | 603.4 | 692.9 | 167.4 | 714.2 | 54.4 | 189.2 | 22.5 | 206.3 | 182.2 | 26.9 | 78.8 | 62.7 | 43.9
310 | 120 | 469.4 | 187.76 | 219.4806 | 184 | 175.6 | 202.3 | 180.9 | 436.7 | 23.2 | 21.1 | 43.2 | 2.7 | 252.6 | 4.1 | 203.3 | 886.8 | 810.9 | 424.8 | 733 | 243.3 | 603.1 | 682.5 | 168 | 715.5 | 54.8 | 189.4 | 22.6 | 206.7 | 183 | 27.1 | 79.3 | 63.3 | 44.2
311 | 121 | 469 | 187.6 | 219.2936 | 184.1 | 175.5 | 201.7 | 181.5 | 430.6 | 23.3 | 21.1 | 43.3 | 2.7 | 254.2 | 4.2 | 204.2 | 885.9 | 802.3 | 427.7 | 739.1 | 244.3 | 594.6 | 668.1 | 168.2 | 712.9 | 55.1 | 189.7 | 22.7 | 208.4 | 184.4 | 27.2 | 79.7 | 63.8 | 44.4
312 | 122 | 469.3 | 187.72 | 219.4339 | 183.8 | 176.5 | 202.4 | 181.1 | 420.9 | 23.4 | 21.1 | 43.4 | 2.4 | 251.6 | 4.3 | 205.2 | 885.4 | 798.7 | 430.4 | 746.3 | 245.4 | 589.6 | 657.5 | 168.3 | 710.6 | 55.5 | 190 | 22.8 | 208.7 | 185.3 | 27.4 | 80.3 | 64.3 | 44.7
313 | 123 | 469.3 | 187.72 | 219.4339 | 182.8 | 176.8 | 202.3 | 180.4 | 416.3 | 23.4 | 21.1 | 43.6 | 2.3 | 248.2 | 4.4 | 206.1 | 885.7 | 783.9 | 433.4 | 753.8 | 246.8 | 588.5 | 640 | 168.5 | 710.3 | 55.8 | 190.2 | 22.9 | 209.2 | 186 | 27.6 | 80.6 | 64.7 | 45
314 | 124 | 469.2 | 187.68 | 219.3871 | 182.8 | 177.1 | 202.3 | 179.7 | 413.1 | 23.5 | 21.1 | 43.7 | 2.5 | 249.9 | 4.3 | 207.1 | 891.6 | 781.6 | 437 | 758.2 | 248.1 | 589.8 | 633.1 | 169.1 | 712.1 | 56.1 | 190.3 | 23 | 208.7 | 186.4 | 27.8 | 81.1 | 65.2 | 45.2
315 | 125 | 468.7 | 187.48 | 219.1533 | 184.2 | 177 | 202.8 | 179.6 | 409.4 | 23.6 | 21.1 | 43.8 | 2.5 | 252.9 | 4.1 | 208 | 891.3 | 789.3 | 440.6 | 758.9 | 249.4 | 585.8 | 629.5 | 169.5 | 711.7 | 56.5 | 190.2 | 23.1 | 208.5 | 186.5 | 27.9 | 81.4 | 65.6 | 45.4
316 | 126 | 469 | 187.6 | 219.2936 | 184.7 | 176.1 | 203.5 | 179.9 | 404 | 23.6 | 21.1 | 44 | 2.3 | 252.1 | 3.9 | 208.8 | 887.6 | 803.1 | 444 | 757.3 | 250.8 | 587.3 | 638.9 | 170 | 713.3 | 56.8 | 190.3 | 23.2 | 208.8 | 186.6 | 28.1 | 81.8 | 66.1 | 45.6
317 | 127 | 469.4 | 187.76 | 219.4806 | 184.3 | 176.3 | 204.2 | 180.1 | 406.1 | 23.7 | 21.1 | 44.1 | 2.3 | 247.8 | 3.8 | 209.7 | 889.3 | 824.2 | 448.3 | 751.3 | 252.3 | 594.1 | 665.5 | 171.2 | 714.9 | 57.2 | 190.7 | 23.3 | 208.7 | 186.4 | 28.3 | 82.2 | 66.6 | 45.9
318 | 128 | 471.7 | 188.68 | 220.556 | 184.4 | 176.7 | 204.5 | 179.6 | 414.6 | 23.7 | 21.1 | 44.3 | 2.2 | 244.6 | 3.7 | 210.7 | 880.8 | 837 | 453.3 | 745.5 | 253.9 | 606 | 686.5 | 172.5 | 715.4 | 57.5 | 191 | 23.4 | 209.1 | 186.3 | 28.5 | 82.6 | 67 | 46.1
319 | 129 | 472.3 | 188.92 | 220.8366 | 184.4 | 177.6 | 204.5 | 180 | 427.3 | 23.7 | 21.1 | 44.5 | 2.5 | 244.8 | 3.6 | 211.7 | 878.4 | 849.7 | 458.9 | 741.3 | 255.8 | 617.3 | 714.9 | 174.1 | 717.7 | 57.8 | 191.4 | 23.5 | 209.7 | 186.4 | 28.6 | 82.9 | 67.5 | 46.3
320 | 130 | 473.2 | 189.28 | 221.2574 | 185.3 | 178.1 | 204.4 | 180.4 | 444.2 | 23.8 | 21.1 | 44.7 | 2.6 | 244.9 | 3.6 | 212.8 | 882.2 | 854.5 | 465.6 | 737.3 | 258.4 | 621.7 | 724.8 | 175.4 | 717.6 | 58.2 | 192 | 23.6 | 209.6 | 186.7 | 28.8 | 83.3 | 68.1 | 46.6
321 | 131 | 471.6 | 188.64 | 220.5093 | 185.7 | 178.9 | 204.3 | 180.2 | 435.3 | 23.9 | 21.1 | 44.9 | 2.6 | 244.8 | 3.5 | 213.9 | 882.3 | 851.5 | 472.2 | 727 | 260.7 | 617.1 | 716.7 | 175.9 | 715 | 58.5 | 192.3 | 23.7 | 210.4 | 187.5 | 29 | 83.5 | 68.6 | 46.9
322 | 132 | 470.4 | 188.16 | 219.9482 | 186.1 | 180.3 | 204.2 | 180.6 | 429 | 23.9 | 21.1 | 45.1 | 2.2 | 244.8 | 3.4 | 215 | 880 | 854.2 | 477.7 | 717.9 | 262.6 | 615.1 | 717.1 | 176.7 | 713.6 | 58.8 | 192.5 | 23.9 | 211.2 | 188.4 | 29.2 | 83.7 | 69.2 | 47.1
323 | 133 | 470.4 | 188.16 | 219.9482 | 186 | 181.9 | 203.7 | 181.6 | 433.4 | 24 | 21.1 | 45.3 | 2.5 | 244.7 | 3.2 | 216.2 | 884.7 | 851.6 | 483.4 | 716.5 | 264.7 | 615 | 714.5 | 177.4 | 712.1 | 59.1 | 193 | 24 | 211.4 | 188.5 | 29.3 | 84.1 | 69.8 | 47.3
324 | 134 | 469.9 | 187.96 | 219.7144 | 186.6 | 184 | 202.9 | 182.3 | 431.6 | 24 | 21.1 | 45.3 | 2.7 | 244.7 | 3.1 | 217.6 | 884.4 | 842.6 | 489.8 | 712.6 | 267.3 | 609.7 | 706.1 | 177.8 | 710 | 59.4 | 193.3 | 24.1 | 212.5 | 188.3 | 29.5 | 84.4 | 70.3 | 47.6
325 | 135 | 470.5 | 188.2 | 219.995 | 186.7 | 185 | 203.1 | 182.3 | 429.2 | 24.1 | 21.1 | 45.4 | 2.6 | 244.7 | 3 | 218.8 | 885.1 | 848.1 | 495.9 | 709.3 | 269.5 | 607.9 | 710.6 | 178.3 | 709.5 | 59.7 | 193.6 | 24.2 | 213.5 | 188.5 | 29.7 | 84.9 | 70.9 | 47.9
326 | 136 | 470.3 | 188.12 | 219.9014 | 186.7 | 185.8 | 202.3 | 182.1 | 425.4 | 24.2 | 21.1 | 45.4 | 2.5 | 244.7 | 2.9 | 219.9 | 883.3 | 847 | 501.9 | 714.9 | 270.2 | 607.6 | 719.4 | 178.9 | 708.7 | 60.1 | 193.8 | 24.3 | 213.5 | 187.9 | 29.8 | 85.1 | 71.4 | 48.1
327 | 137 | 469.2 | 187.68 | 219.3871 | 187.3 | 186.6 | 202.7 | 181.5 | 431 | 24.2 | 21.1 | 45.5 | 2.4 | 243.8 | 2.9 | 220.9 | 879.8 | 846.8 | 506.8 | 719.2 | 271.4 | 609.9 | 731 | 179.9 | 709.7 | 60.4 | 194.3 | 24.4 | 214 | 188.5 | 30 | 85.4 | 72 | 48.3
328 | 138 | 470.8 | 188.32 | 220.1352 | 188.1 | 187.7 | 203.4 | 181.2 | 436.9 | 24.3 | 21.1 | 45.7 | 2.5 | 243.3 | 2.9 | 221.8 | 868.2 | 831.7 | 511.6 | 715.6 | 273.7 | 608.1 | 738.2 | 180.3 | 707.7 | 60.7 | 194.5 | 24.5 | 214.2 | 189.3 | 30.2 | 85.7 | 72.6 | 48.6
329 | 139 | 471.1 | 188.44 | 220.2755 | 188.8 | 188.8 | 203.9 | 181.4 | 442.1 | 24.4 | 21.1 | 45.9 | 2.7 | 240.9 | 2.9 | 222.9 | 850.7 | 815.4 | 515.8 | 705.6 | 278 | 606.9 | 735.8 | 180.6 | 703.9 | 61 | 194.6 | 24.6 | 214 | 189.3 | 30.4 | 86 | 73.1 | 48.8
330 | 140 | 471.1 | 188.44 | 220.2755 | 189.1 | 190 | 203.8 | 182.3 | 445.9 | 24.4 | 21.1 | 46.1 | 2.5 | 239.8 | 2.8 | 224.3 | 835.5 | 790.9 | 518.6 | 699.7 | 281.3 | 603.4 | 735.8 | 180.8 | 701.4 | 61.3 | 195 | 24.7 | 214 | 189.9 | 30.6 | 86.4 | 73.6 | 49
331 | 141 | 470.8 | 188.32 | 220.1352 | 189.7 | 190.4 | 204.2 | 183 | 442.9 | 24.5 | 21 | 46.3 | 2.3 | 240.5 | 2.8 | 225.6 | 840.3 | 801.3 | 522 | 703.4 | 284.4 | 601.7 | 733.7 | 181.2 | 703 | 61.6 | 195.4 | 24.9 | 214 | 190.8 | 30.7 | 86.8 | 74 | 49.3
332 | 142 | 469.1 | 187.64 | 219.3403 | 189.3 | 189.6 | 204.4 | 183.5 | 448.6 | 24.6 | 21 | 46.6 | 2.1 | 242.1 | 2.8 | 227.1 | 838.1 | 799.3 | 525.3 | 705.1 | 287.9 | 603 | 744 | 181.8 | 702.5 | 61.9 | 195.8 | 25 | 214.7 | 191.4 | 30.9 | 87.2 | 74.4 | 49.6
333 | 143 | 468.7 | 187.48 | 219.1533 | 189.2 | 188.5 | 204.1 | 184 | 454.9 | 24.7 | 21 | 46.7 | 2.2 | 242.3 | 2.7 | 228.4 | 835.5 | 801.6 | 528.5 | 700.8 | 290.6 | 599.2 | 738.1 | 182.3 | 699.8 | 62.2 | 196.2 | 25.1 | 215.5 | 191.3 | 31.1 | 87.5 | 74.9 | 49.8
334 | 144 | 468.9 | 187.56 | 219.2468 | 189.2 | 188.2 | 203.7 | 184.5 | 452.1 | 24.7 | 21 | 46.9 | 2.4 | 242.2 | 2.6 | 229.6 | 838.4 | 817.6 | 533.3 | 705.3 | 292 | 599.1 | 749.8 | 182.9 | 698.6 | 62.5 | 196.6 | 25.2 | 216.1 | 191.2 | 31.3 | 87.7 | 75.3 | 50
335 | 145 | 468.5 | 187.4 | 219.0598 | 189.7 | 188.2 | 204.6 | 185.3 | 448.9 | 24.7 | 21 | 47.2 | 2.2 | 240.7 | 2.4 | 231 | 840.5 | 808.4 | 537.7 | 713.8 | 293.9 | 598.6 | 731 | 183.6 | 700.3 | 62.8 | 196.9 | 25.3 | 217 | 191 | 31.5 | 88 | 75.8 | 50.3
336 | 146 | 468 | 187.2 | 218.826 | 187.8 | 188.2 | 205.8 | 185.4 | 437.1 | 24.8 | 21 | 47.3 | 2.2 | 233 | 2.2 | 232.7 | 842.7 | 816.8 | 542.4 | 715.5 | 295.9 | 598.9 | 729.5 | 184.1 | 700.5 | 63 | 197.5 | 25.4 | 217.4 | 190.6 | 31.7 | 88.3 | 76.3 | 50.6
337 | 147 | 469 | 187.6 | 219.2936 | 186.4 | 188.5 | 206.4 | 185.1 | 436.1 | 24.8 | 21 | 47.4 | 2.2 | 226.1 | 2.1 | 234.4 | 844.9 | 815 | 547.5 | 717.9 | 297.9 | 597.7 | 727.2 | 184.4 | 699.7 | 63.3 | 197.8 | 25.6 | 217.5 | 191.6 | 31.8 | 88.7 | 76.8 | 50.8
338 | 148 | 468.3 | 187.32 | 218.9663 | 187.8 | 188.7 | 206.5 | 184.5 | 429.6 | 24.8 | 21 | 47.5 | 2.2 | 224.1 | 2.1 | 236 | 854.3 | 824.2 | 553 | 723.5 | 300 | 600 | 717.2 | 185.1 | 701.4 | 63.5 | 197.8 | 25.7 | 217 | 192.3 | 32 | 89.2 | 77.2 | 51
339 | 149 | 468.9 | 187.56 | 219.2468 | 189.3 | 188.4 | 206.3 | 183.7 | 421.9 | 24.9 | 21 | 47.7 | 2.2 | 224.7 | 2.1 | 237.5 | 862.6 | 826.5 | 558 | 726.3 | 302.2 | 602.9 | 709.3 | 186.3 | 703.9 | 63.8 | 197.9 | 25.8 | 216.9 | 193.5 | 32.2 | 89.6 | 77.7 | 51.2
340 | 150 | 469.8 | 187.92 | 219.6677 | 189.6 | 188.4 | 205.4 | 182.8 | 419.2 | 24.9 | 21 | 47.7 | 2.4 | 224.3 | 2 | 239.4 | 867.3 | 833.1 | 561.8 | 729.7 | 304.2 | 603.4 | 701.4 | 187.1 | 704.8 | 64 | 198.4 | 25.9 | 216.3 | 194.7 | 32.4 | 90 | 78.3 | 51.4
341 | 151 | 469.2 | 187.68 | 219.3871 | 189.9 | 188 | 205.6 | 182.4 | 414.1 | 25 | 21 | 47.8 | 2.2 | 220.9 | 1.9 | 241.3 | 869 | 836.6 | 565.1 | 737.8 | 306.4 | 602 | 701.6 | 187.8 | 706.8 | 64.3 | 198.8 | 26 | 216.2 | 195 | 32.6 | 90.2 | 78.9 | 51.6
342 | 152 | 469.2 | 187.68 | 219.3871 | 190.7 | 188.2 | 206.6 | 182.4 | 414.3 | 25 | 21 | 47.9 | 2.4 | 199.8 | 1.8 | 243 | 869.9 | 822.6 | 568 | 738.9 | 308.8 | 607.8 | 697.1 | 188.7 | 709.5 | 64.5 | 198.7 | 26.1 | 216 | 194.8 | 32.8 | 90.5 | 79.4 | 51.9
343 | 153 | 469.5 | 187.8 | 219.5274 | 190.9 | 188.3 | 206.8 | 182.3 | 407.4 | 25.1 | 21 | 48 | 2.5 | 169.2 | 1.9 | 244.7 | 873.8 | 823 | 570.9 | 739.9 | 311.4 | 607.7 | 695.4 | 189.3 | 709.5 | 64.8 | 198.4 | 26.3 | 215.7 | 194.5 | 33 | 90.9 | 79.9 | 52.1
344 | 154 | 469.7 | 187.88 | 219.6209 | 191.5 | 188.2 | 207.7 | 182 | 404.6 | 25.2 | 21 | 48.2 | 2.1 | 159.3 | 2 | 246.3 | 872 | 836.3 | 574 | 743.8 | 313.8 | 608.8 | 698.3 | 189.8 | 709.8 | 65 | 198.2 | 26.4 | 215.2 | 195.1 | 33.1 | 91.1 | 80.4 | 52.3
345 | 155 | 470.1 | 188.04 | 219.8079 | 191.6 | 188.4 | 207.8 | 181.5 | 407.4 | 25.2 | 21 | 48.3 | 2.7 | 168.1 | 2.2 | 247.8 | 868.9 | 839 | 577.3 | 747 | 316.4 | 618 | 709.5 | 191.1 | 712.5 | 65.3 | 198 | 26.5 | 215.2 | 194.9 | 33.3 | 91.4 | 80.9 | 52.5
346 | 156 | 469.4 | 187.76 | 219.4806 | 192 | 188 | 207.6 | 181 | 410 | 25.2 | 21 | 48.4 | 2.7 | 173.7 | 2.5 | 249.4 | 865.3 | 840.6 | 580.1 | 748.9 | 318.9 | 622.5 | 710.4 | 192.4 | 713.6 | 65.5 | 198 | 26.6 | 215.6 | 194.9 | 33.5 | 91.7 | 81.4 | 52.8
347 | 157 | 469 | 187.6 | 219.2936 | 192.8 | 187.4 | 207.6 | 180.5 | 410 | 25.3 | 21 | 48.5 | 2.6 | 174.4 | 2.6 | 251.1 | 863.7 | 841.4 | 581.8 | 751.8 | 321.5 | 625.2 | 713 | 193.4 | 714.7 | 65.8 | 198.6 | 26.7 | 215.5 | 194.8 | 33.7 | 92 | 81.9 | 53
348 | 158 | 468.2 | 187.28 | 218.9195 | 193.3 | 186.4 | 207.3 | 181.1 | 409.1 | 25.3 | 21 | 48.6 | 2.4 | 174.2 | 2.6 | 252.9 | 866.3 | 827.8 | 584.6 | 759.8 | 323.9 | 624.8 | 706.4 | 194.6 | 716.2 | 66 | 198.8 | 26.9 | 215.1 | 195.5 | 33.9 | 92.3 | 82.4 | 53.2
349 | 159 | 468 | 187.2 | 218.826 | 193.5 | 185.6 | 207.2 | 181.7 | 412.1 | 25.3 | 21 | 48.7 | 2.7 | 172.3 | 2.4 | 254.6 | 864.2 | 828.9 | 587.2 | 762.2 | 326 | 634 | 706.7 | 196.2 | 718.2 | 66.3 | 198.8 | 27 | 215.4 | 196.6 | 34.1 | 92.6 | 82.9 | 53.5
350 | 160 | 468.9 | 187.56 | 219.2468 | 194.4 | 186.3 | 207.8 | 182.3 | 415.4 | 25.4 | 21 | 48.7 | 2.6 | 161.9 | 2.2 | 256.3 | 860.3 | 824.5 | 589.3 | 768.4 | 328.1 | 633.5 | 700.6 | 197.2 | 718.8 | 66.5 | 198.8 | 27.1 | 215.3 | 197.6 | 34.2 | 93 | 83.4 | 53.7
351 | 161 | 468.4 | 187.36 | 219.013 | 194.2 | 186.8 | 208.2 | 182.9 | 414.3 | 25.5 | 21 | 48.8 | 2.6 | 146.9 | 2.2 | 258.1 | 856.1 | 828.5 | 591.4 | 771.6 | 330.1 | 639.4 | 703.4 | 198.4 | 720.6 | 66.8 | 198.9 | 27.2 | 215.3 | 198.1 | 34.4 | 93.5 | 83.9 | 53.9
352 | 162 | 469 | 187.6 | 219.2936 | 193.9 | 186.8 | 208.8 | 183.5 | 423.2 | 25.5 | 21 | 48.8 | 2.5 | 133.5 | 2.3 | 259.7 | 855.4 | 820.9 | 593.7 | 777 | 332.2 | 643.6 | 707.4 | 199.9 | 722.3 | 67 | 198.8 | 27.3 | 215.7 | 197.9 | 34.6 | 93.8 | 84.5 | 54.2
353 | 163 | 468.4 | 187.36 | 219.013 | 193.8 | 186.9 | 208.9 | 183.5 | 426.6 | 25.6 | 21 | 49 | 2.5 | 127.9 | 2.3 | 261.1 | 850.6 | 826.8 | 595.4 | 778.5 | 334.1 | 646.5 | 706.7 | 201.2 | 722.7 | 67.3 | 198.8 | 27.5 | 215.9 | 198 | 34.8 | 94.1 | 85 | 54.4
354 | 164 | 468.9 | 187.56 | 219.2468 | 194.3 | 187.4 | 209.2 | 183.2 | 429 | 25.6 | 21 | 49.1 | 2.7 | 127.1 | 2.4 | 262.8 | 845.5 | 838.8 | 597.2 | 773.1 | 336 | 648.9 | 701.5 | 202.6 | 723.3 | 67.5 | 199 | 27.6 | 216.5 | 198.6 | 35 | 94.4 | 85.6 | 54.6
355 | 165 | 469.2 | 187.68 | 219.3871 | 194.5 | 188 | 209.3 | 182.8 | 428 | 25.7 | 21 | 49.1 | 2.6 | 112.7 | 2.5 | 264.5 | 846.3 | 839.1 | 598.2 | 767.9 | 337.8 | 645.9 | 693 | 203.7 | 722.6 | 67.8 | 199.3 | 27.7 | 216.4 | 199.7 | 35.2 | 94.8 | 86.2 | 54.8
356 | 166 | 469.6 | 187.84 | 219.5741 | 195.3 | 187.1 | 209.1 | 182.1 | 428.6 | 25.7 | 21 | 49.2 | 2.6 | 91 | 2.5 | 266.2 | 844.6 | 838.2 | 598.2 | 761.5 | 339.4 | 652.8 | 703.7 | 205.6 | 723.6 | 68 | 199.8 | 27.8 | 216.1 | 200 | 35.3 | 95.2 | 86.7 | 55
357 | 167 | 468.6 | 187.44 | 219.1066 | 195.5 | 186.8 | 209.3 | 182.1 | 429.2 | 25.8 | 21 | 49.3 | 2.8 | 80.9 | 2.5 | 267.9 | 841.5 | 844.7 | 598.6 | 758 | 341.1 | 651.4 | 709.6 | 207.1 | 723.3 | 68.3 | 200.2 | 28 | 216.1 | 199.5 | 35.5 | 95.6 | 87.3 | 55.2
358 | 168 | 469.2 | 187.68 | 219.3871 | 195.9 | 186.9 | 209.7 | 182 | 426.7 | 25.8 | 20.9 | 49.3 | 2.6 | 87.4 | 2.5 | 269.8 | 839.4 | 845 | 599.5 | 755.3 | 342.9 | 649.5 | 709.9 | 208.9 | 722.7 | 68.6 | 200.6 | 28.1 | 215.9 | 199.4 | 35.7 | 96 | 87.8 | 55.5
359 | 169 | 469.6 | 187.84 | 219.5741 | 196.8 | 186.9 | 209.1 | 182.5 | 421.2 | 25.8 | 20.9 | 49.4 | 2.7 | 97.2 | 2.5 | 271.8 | 838.4 | 834.7 | 600.3 | 749.3 | 344.8 | 642.3 | 703 | 210.3 | 721.6 | 68.9 | 200.6 | 28.2 | 215.8 | 199 | 35.9 | 96.5 | 88.4 | 55.7
360 | 170 | 469.9 | 187.96 | 219.7144 | 197.5 | 187 | 209 | 182.9 | 419.8 | 25.9 | 20.9 | 49.4 | 2.7 | 105.4 | 2.5 | 273.5 | 834.3 | 839 | 600.8 | 741 | 346.8 | 640.2 | 712.9 | 212 | 720.4 | 69.2 | 200.8 | 28.3 | 215.5 | 199.1 | 36.1 | 96.7 | 88.9 | 55.9
361 | 171 | 469.8 | 187.92 | 219.6677 | 198.4 | 186.2 | 209.3 | 182.5 | 423.6 | 25.9 | 20.9 | 49.4 | 2.8 | 115.6 | 2.5 | 275.3 | 827.2 | 845.4 | 600.9 | 737.6 | 348.6 | 643.5 | 726.8 | 213.6 | 719.4 | 69.4 | 201.1 | 28.5 | 215.1 | 199.1 | 36.3 | 97 | 89.5 | 56.1
362 | 172 | 470 | 188 | 219.7612 | 199.1 | 185.1 | 209.2 | 182.8 | 429.1 | 26 | 20.9 | 49.4 | 2.8 | 131.2 | 2.4 | 277.2 | 821.6 | 857.4 | 600.4 | 738.3 | 350.8 | 646.7 | 740.6 | 215.6 | 720.2 | 69.7 | 201.2 | 28.6 | 214.9 | 198.8 | 36.5 | 97.1 | 90.1 | 56.3
363 | 173 | 471.2 | 188.48 | 220.3223 | 199.7 | 184 | 208.7 | 183.4 | 433.7 | 26.1 | 20.9 | 49.5 | 2.7 | 137.5 | 2.4 | 279 | 815.2 | 863 | 598.6 | 742.4 | 353 | 650.8 | 752.2 | 217.8 | 720 | 70 | 201.5 | 28.7 | 214.8 | 198.6 | 36.6 | 97.4 | 90.7 | 56.6
364 | 174 | 470.3 | 188.12 | 219.9014 | 200.4 | 184 | 208 | 184.3 | 434 | 26.2 | 20.9 | 49.6 | 3.1 | 136.4 | 2.4 | 280.9 | 808.8 | 871.5 | 597 | 750.9 | 355.5 | 657 | 749.6 | 219.9 | 720.6 | 70.3 | 201.6 | 28.8 | 215 | 199.1 | 36.8 | 97.6 | 91.3 | 56.7
365 | 175 | 469.1 | 187.64 | 219.3403 | 200.3 | 184.3 | 208.2 | 184.4 | 438.9 | 26.3 | 20.9 | 49.7 | 3.3 | 137 | 2.4 | 282.6 | 811.9 | 864.3 | 595.6 | 747.8 | 357.9 | 658.2 | 762.7 | 222 | 720.4 | 70.5 | 201.9 | 29 | 215.3 | 199.1 | 37 | 97.9 | 91.8 | 56.9
366 | 176 | 468.2 | 187.28 | 218.9195 | 200.6 | 184.6 | 208.8 | 184.1 | 438.3 | 26.4 | 20.9 | 49.8 | 3.1 | 138.2 | 2.5 | 284.4 | 813 | 859.2 | 594.2 | 747.8 | 360.5 | 657 | 768.5 | 223.7 | 721.2 | 70.8 | 201.9 | 29.1 | 216 | 199.3 | 37.2 | 98.2 | 92.4 | 57.2
367 | 177 | 468.8 | 187.52 | 219.2001 | 200 | 184.9 | 209.1 | 184.6 | 439.5 | 26.4 | 20.9 | 49.9 | 3.3 | 146.2 | 2.7 | 286.2 | 813 | 856.9 | 593.3 | 744 | 362.9 | 661.6 | 779.2 | 225.8 | 720.8 | 71.1 | 202 | 29.2 | 216.5 | 200.4 | 37.4 | 98.6 | 92.9 | 57.4
368 | 178 | 468.6 | 187.44 | 219.1066 | 200 | 185.4 | 209.5 | 184.6 | 447.4 | 26.4 | 20.9 | 50 | 3.3 | 153 | 2.9 | 288.1 | 813.1 | 851.9 | 593 | 747.6 | 365.1 | 659.2 | 783.8 | 227.4 | 719.9 | 71.3 | 202 | 29.3 | 216.4 | 201 | 37.6 | 99.1 | 93.4 | 57.6
369 | 179 | 468.3 | 187.32 | 218.9663 | 199 | 185.5 | 209.7 | 185.2 | 461.7 | 26.4 | 20.9 | 50.2 | 3.7 | 157.5 | 3.1 | 290 | 806.2 | 859.8 | 591.7 | 744.3 | 366.9 | 661.6 | 793.3 | 229.4 | 719.1 | 71.6 | 202.3 | 29.5 | 216.4 | 201.7 | 37.8 | 99.5 | 94 | 57.9
370 | 180 | 468.3 | 187.32 | 218.9663 | 199.1 | 185 | 209.8 | 185.1 | 484.8 | 26.5 | 20.9 | 50.3 | 3.6 | 173 | 3.2 | 291.9 | 807.9 | 851.9 | 591.6 | 745 | 368.9 | 663.8 | 797.4 | 231.5 | 718.3 | 71.8 | 203 | 29.6 | 216.5 | 201.6 | 38 | 99.7 | 94.5 | 58.1
371 | 181 | 468.9 | 187.56 | 219.2468 | 199.5 | 184.5 | 210 | 184.8 | 486 | 26.5 | 20.9 | 50.3 | 3.8 | 182.3 | 3.1 | 293.8 | 809.6 | 856.1 | 591.8 | 739.2 | 370.5 | 657.2 | 792.4 | 232.8 | 717.5 | 72.1 | 203.2 | 29.7 | 217.2 | 201.8 | 38.1 | 100 | 95 | 58.3
372 | 182 | 468.6 | 187.44 | 219.1066 | 199.3 | 185 | 210.5 | 185.4 | 484.1 | 26.6 | 20.9 | 50.4 | 4.1 | 195.3 | 2.8 | 295.7 | 807 | 858.8 | 591.2 | 740.9 | 371.9 | 652.9 | 791.9 | 234.2 | 717.4 | 72.4 | 203.7 | 29.9 | 217.5 | 202.1 | 38.3 | 100.4 | 95.6 | 58.5
373 | 183 | 468.1 | 187.24 | 218.8728 | 198.7 | 185.6 | 210.7 | 186.5 | 478.1 | 26.7 | 20.9 | 50.5 | 3.5 | 207.3 | 2.6 | 297.6 | 803.9 | 864.2 | 591.7 | 747.3 | 373.6 | 654.1 | 790.6 | 235.9 | 718.3 | 72.6 | 204.2 | 30 | 218.2 | 201.6 | 38.5 | 100.7 | 96.1 | 58.6
374 | 184 | 468.7 | 187.48 | 219.1533 | 198.8 | 186.8 | 210.2 | 187 | 471.1 | 26.7 | 20.9 | 50.6 | 3.1 | 202.8 | 2.8 | 299.6 | 800.4 | 864.8 | 591.4 | 750.6 | 375.4 | 658.5 | 788.8 | 237.5 | 719.8 | 72.9 | 204.7 | 30.1 | 218.4 | 202.2 | 38.7 | 101 | 96.7 | 59
375 | 185 | 469 | 187.6 | 219.2936 | 198.8 | 187.8 | 209.9 | 187.1 | 470.2 | 26.8 | 20.9 | 50.7 | 3.3 | 196.8 | 3.7 | 301.7 | 794 | 873 | 590.8 | 752.9 | 377.3 | 659.2 | 793.2 | 239.1 | 719.5 | 73.2 | 205 | 30.3 | 218.8 | 202.4 | 38.9 | 101.3 | 97.3 | 59.3
376 | 186 | 468.7 | 187.48 | 219.1533 | 198.7 | 188.6 | 210.3 | 187.3 | 472.1 | 26.9 | 20.9 | 50.9 | 2.9 | 190.7 | 5 | 303.8 | 795.3 | 867.2 | 591.5 | 752.9 | 379.2 | 661.8 | 796.6 | 240.9 | 720.8 | 73.5 | 205.2 | 30.4 | 219.1 | 202.4 | 39.1 | 101.6 | 97.8 | 59.4
377 | 187 | 469.3 | 187.72 | 219.4339 | 199.1 | 189.5 | 210.7 | 187.3 | 461.3 | 26.9 | 20.9 | 50.9 | 2.9 | 177 | 3.9 | 305.7 | 799.6 | 859.8 | 592 | 761.7 | 381.5 | 655.4 | 784.6 | 242.1 | 720.9 | 73.7 | 205.4 | 30.5 | 218.9 | 202.4 | 39.3 | 101.9 | 98.4 | 59.7
378 | 188 | 469.4 | 187.76 | 219.4806 | 199.8 | 190.3 | 211.6 | 188.1 | 448.8 | 27 | 20.9 | 51 | 3.1 | 229.6 | 2.5 | 307.5 | 803.6 | 834.7 | 592.5 | 767.8 | 384 | 652.3 | 770.1 | 243.7 | 723.5 | 74 | 205.9 | 30.6 | 219.3 | 202.7 | 39.5 | 102.3 | 98.9 | 60
379 | 189 | 468.5 | 187.4 | 219.0598 | 201.1 | 189.8 | 211.3 | 188.9 | 441.5 | 27.1 | 20.9 | 51.1 | 3.4 | 290.1 | 3.1 | 309.4 | 807.2 | 817.6 | 591.8 | 769.3 | 386.4 | 647.7 | 764.3 | 245.4 | 723.6 | 74.3 | 206.2 | 30.8 | 219.4 | 202.8 | 39.7 | 102.7 | 99.4 | 60.2
380 | 190 | 469.2 | 187.68 | 219.3871 | 202.8 | 189.2 | 211.7 | 188.8 | 445.1 | 27.1 | 20.9 | 51.1 | 3.5 | 293.6 | 4.1 | 311.4 | 809.8 | 794.7 | 590 | 767.3 | 388.8 | 645.7 | 762.8 | 247.3 | 724.4 | 74.5 | 206.4 | 30.9 | 219.4 | 202.7 | 39.9 | 103.1 | 99.8 | 60.4
381 | 191 | 469.2 | 187.68 | 219.3871 | 204.1 | 188.9 | 212 | 189.4 | 443 | 27.2 | 20.9 | 51.3 | 3.8 | 238.6 | 4.2 | 313.4 | 819.8 | 766.7 | 587.6 | 768 | 391.1 | 634.6 | 745.1 | 248.9 | 725.2 | 74.8 | 206.9 | 31 | 220.1 | 202.1 | 40.1 | 103.4 | 100.3 | 60.5
382 | 192 | 469.8 | 187.92 | 219.6677 | 205.6 | 188.5 | 212 | 190.4 | 438.7 | 27.3 | 20.9 | 51.5 | 3.6 | 243.9 | 3.8 | 315.4 | 822 | 767.5 | 585.7 | 774.1 | 393.3 | 632.1 | 748.8 | 250.6 | 726.7 | 75.1 | 206.8 | 31.2 | 220.9 | 202 | 40.3 | 103.6 | 100.7 | 60.7
383 | 193 | 469.9 | 187.96 | 219.7144 | 207.2 | 188.5 | 212.4 | 190.9 | 442.6 | 27.3 | 20.9 | 51.7 | 3.8 | 260.7 | 3.4 | 317.4 | 830.6 | 765.2 | 584.4 | 776.2 | 395.4 | 635 | 753 | 252.6 | 729.4 | 75.4 | 207 | 31.3 | 221.8 | 202.1 | 40.5 | 103.9 | 101.1 | 61.1
384 | 194 | 468.8 | 187.52 | 219.2001 | 207.7 | 187.9 | 212.6 | 191.8 | 445.9 | 27.3 | 20.9 | 51.8 | 3.9 | 265.6 | 3.1 | 319.2 | 835.7 | 762.6 | 583.4 | 782.6 | 397.8 | 639 | 755.1 | 254.8 | 731.7 | 75.7 | 207.4 | 31.4 | 222.1 | 203.2 | 40.7 | 104.1 | 101.5 | 61.1
385 | 195 | 468.3 | 187.32 | 218.9663 | 208.7 | 187.2 | 213.1 | 192.7 | 447.7 | 27.4 | 20.9 | 52 | 4.5 | 254.7 | 2.7 | 321.1 | 834.7 | 765 | 582.8 | 782 | 400.5 | 639.2 | 755.9 | 256.4 | 732.7 | 75.9 | 208.2 | 31.6 | 223.2 | 204.5 | 40.9 | 104.5 | 101.8 | 61.5
386 | 196 | 468.2 | 187.28 | 218.9195 | 209.4 | 187 | 213.6 | 193.4 | 445.3 | 27.4 | 20.9 | 52.1 | 4.9 | 202.5 | 3 | 322.8 | 839.1 | 766.4 | 582.8 | 781.3 | 403 | 641.3 | 760.2 | 258.3 | 733.7 | 76.2 | 208.7 | 31.7 | 223.3 | 205.9 | 41.1 | 105 | 102.2 | 61.8
387 | 197 | 467.7 | 187.08 | 218.6857 | 209.2 | 187.2 | 214.3 | 194 | 448.1 | 27.5 | 20.9 | 52.2 | 4.3 | 206.2 | 4.7 | 324.5 | 849.4 | 774.6 | 583.3 | 782 | 405.8 | 646.6 | 771.1 | 260.5 | 734.7 | 76.5 | 209.3 | 31.8 | 223.9 | 206.9 | 41.3 | 105.4 | 102.6 | 62
388 | 198 | 468.7 | 187.48 | 219.1533 | 209.8 | 187.8 | 214.7 | 194.6 | 450.1 | 27.6 | 20.9 | 52.3 | 4.3 | 211.7 | 5.2 | 326 | 853.5 | 767.4 | 583.7 | 782.6 | 408.6 | 642.8 | 760 | 262.3 | 734.7 | 76.7 | 210 | 32 | 225 | 207.3 | 41.5 | 105.8 | 103.1 | 62.3
389 | 199 | 468.5 | 187.4 | 219.0598 | 210.1 | 188.5 | 215.3 | 195.7 | 445.7 | 27.6 | 20.9 | 52.4 | 3.9 | 201.1 | 4.9 | 327.3 | 850 | 766.5 | 584.7 | 783.8 | 411.4 | 642.7 | 758.2 | 264.2 | 735 | 77 | 210.9 | 32.1 | 226.5 | 207.4 | 41.6 | 106.2 | 103.5 | 62.6
390 | 200 | 468.8 | 187.52 | 219.2001 | 210 | 188.9 | 215.6 | 196.4 | 444.4 | 27.7 | 20.9 | 52.5 | 3.7 | 217.7 | 4.5 | 328.6 | 862.9 | 751.3 | 586.1 | 789.2 | 414.3 | 637.1 | 743.3 | 265.7 | 734.4 | 77.3 | 211.6 | 32.2 | 227.5 | 207.6 | 41.9 | 106.6 | 103.9 | 62.8
391 | 201 | 468.8 | 187.52 | 219.2001 | 210.7 | 188.7 | 216.2 | 196.7 | 438.6 | 27.7 | 20.9 | 52.5 | 3.6 | 226.3 | 4.1 | 330 | 863 | 758.6 | 587.5 | 794.6 | 416.9 | 635.1 | 737.3 | 267.5 | 733.9 | 77.6 | 212.4 | 32.3 | 227.9 | 207.6 | 42 | 106.9 | 104.3 | 63.1
392 | 202 | 468.3 | 187.32 | 218.9663 | 211.6 | 189 | 216.7 | 197 | 437 | 27.7 | 20.9 | 52.5 | 2.8 | 226.1 | 3.7 | 331.3 | 855.2 | 757.9 | 588 | 795.8 | 419.4 | 632.5 | 741.5 | 269 | 733.4 | 77.8 | 213.1 | 32.5 | 228.4 | 208 | 42.2 | 107.2 | 104.7 | 63.4
393 | 203 | 468.2 | 187.28 | 218.9195 | 211.8 | 189.3 | 217.3 | 197.7 | 439.7 | 27.8 | 20.9 | 52.5 | 3.5 | 227.6 | 3 | 332.5 | 874.5 | 747.8 | 588.1 | 799.7 | 421.9 | 632.8 | 742.3 | 270.8 | 734.8 | 78.1 | 213.6 | 32.6 | 228 | 208.9 | 42.4 | 107.6 | 105.1 | 63.5
394 | 204 | 469.1 | 187.64 | 219.3403 | 212.5 | 188.7 | 217.9 | 198.2 | 437.4 | 27.8 | 20.9 | 52.5 | 3.8 | 247.6 | 2.8 | 334 | 884.6 | 762.6 | 587.3 | 802.6 | 424.6 | 631.4 | 743.4 | 272.4 | 735.1 | 78.4 | 214.3 | 32.7 | 227.6 | 209.3 | 42.6 | 108 | 105.5 | 63.8
395 | 205 | 469.5 | 187.8 | 219.5274 | 212.4 | 188.5 | 218.3 | 198.5 | 448.1 | 27.9 | 20.9 | 52.5 | 3.4 | 263 | 3.1 | 335.5 | 881.2 | 772.5 | 587.1 | 797.8 | 427.3 | 635.4 | 754.9 | 274.2 | 734.6 | 78.7 | 214.8 | 32.9 | 227.7 | 209.6 | 42.8 | 108.3 | 105.9 | 64.1
396 | 206 | 469 | 187.6 | 219.2936 | 211.6 | 187.5 | 218.9 | 198.6 | 461.9 | 27.9 | 20.9 | 52.5 | 3.3 | 219.4 | 4.6 | 337 | 874.3 | 777.7 | 586.7 | 794.1 | 430.2 | 638.8 | 757.7 | 276.3 | 735.4 | 79 | 215.3 | 33 | 227.2 | 209.9 | 43 | 108.7 | 106.3 | 64.3
397 | 207 | 468.8 | 187.52 | 219.2001 | 211.4 | 187.8 | 219.9 | 198.9 | 461.3 | 28 | 20.9 | 52.6 | 3.3 | 244.4 | 6.4 | 338.4 | 861.3 | 782 | 585.9 | 789.4 | 433 | 637.1 | 758.1 | 277.8 | 735.3 | 79.3 | 215.8 | 33.1 | 227 | 210.2 | 43.2 | 109 | 106.7 | 64.5
398 | 208 | 469.1 | 187.64 | 219.3403 | 212 | 189 | 220.7 | 199.2 | 462.6 | 28 | 20.9 | 52.7 | 3.7 | 236.9 | 8.7 | 339.9 | 857.5 | 783.8 | 584.4 | 786.4 | 435.7 | 641.6 | 765.9 | 279.8 | 735.2 | 79.6 | 216.5 | 33.3 | 227.2 | 210.8 | 43.4 | 109.3 | 107.1 | 64.8
399 | 209 | 469.5 | 187.8 | 219.5274 | 212.2 | 189.8 | 221.3 | 199.2 | 470.6 | 28 | 20.9 | 52.8 | 3.9 | 256.1 | 11.8 | 341.4 | 842.8 | 790.1 | 583.4 | 787.9 | 438.7 | 649.1 | 780 | 281.8 | 735.1 | 79.9 | 217.2 | 33.4 | 227.9 | 210.6 | 43.6 | 109.7 | 107.5 | 65.1
400 | 210 | 470.1 | 188.04 | 219.8079 | 212.4 | 190.4 | 221.9 | 198.5 | 472.5 | 28.1 | 20.8 | 52.9 | 3.6 | 257.7 | 12.8 | 343 | 838.6 | 773 | 582.4 | 786 | 441.7 | 647.2 | 773.6 | 283.8 | 734.5 | 80.2 | 218 | 33.5 | 228.4 | 210.4 | 43.8 | 110.1 | 108 | 65.3
401 | 211 | 469.9 | 187.96 | 219.7144 | 212.8 | 190.5 | 222.8 | 198.6 | 468.9 | 28.1 | 20.8 | 53 | 3.4 | 245.8 | 11.5 | 344.6 | 833.8 | 780.4 | 581.6 | 782.9 | 444.7 | 646.1 | 774.9 | 285.7 | 733.8 | 80.5 | 218.7 | 33.7 | 228.6 | 210.6 | 44 | 110.4 | 108.4 | 65.5
402 | 212 | 469 | 187.6 | 219.2936 | 213.1 | 190.7 | 222.3 | 199.3 | 468.1 | 28.2 | 20.8 | 53 | 3.4 | 230.2 | 9.4 | 346.4 | 824.6 | 791.8 | 581.7 | 787.1 | 447.8 | 651.9 | 783.8 | 287.8 | 734 | 80.9 | 219.3 | 33.8 | 228.3 | 211 | 44.2 | 110.8 | 108.8 | 65.8
403 | 213 | 470.3 | 188.12 | 219.9014 | 213.3 | 191.3 | 222.6 | 199.9 | 477.3 | 28.2 | 20.8 | 53.1 | 3.6 | 232.9 | 8.4 | 348.4 | 811.5 | 802.5 | 581.3 | 792.2 | 450.9 | 667.7 | 790 | 290.8 | 736 | 81.2 | 219.7 | 33.9 | 228.3 | 211.2 | 44.4 | 111.1 | 109.2 | 66
404 | 214 | 468.8 | 187.52 | 219.2001 | 213.3 | 192.1 | 222.8 | 200.7 | 484.2 | 28.2 | 20.8 | 53.2 | 4.2 | 226.9 | 7.4 | 350.7 | 592.9 | 803.2 | 580.8 | 791.1 | 454 | 679.3 | 798.7 | 294.1 | 738 | 81.5 | 220.1 | 34.1 | 228.6 | 211 | 44.7 | 111.6 | 109.7 | 66.2
405 | 215 | 468.8 | 187.52 | 219.2001 | 213.8 | 193 | 223.2 | 201.4 | 489.6 | 28.2 | 20.8 | 53.2 | 4 | 222.2 | 6.8 | 353.3 | 806.7 | 808 | 580.2 | 791.7 | 457.3 | 681.8 | 796.8 | 296.7 | 737.8 | 81.8 | 220.5 | 34.2 | 228.9 | 211.1 | 44.9 | 111.9 | 110.1 | 66.5
406 | 216 | 469.7 | 187.88 | 219.6209 | 214.7 | 193.5 | 223.2 | 202.2 | 485.2 | 28.2 | 20.8 | 53.3 | 3.5 | 217.2 | 8 | 356.1 | 756.4 | 804 | 580.1 | 793.3 | 460.3 | 688.1 | 804.8 | 299 | 739.6 | 82.1 | 220.9 | 34.3 | 228.8 | 211.6 | 45.1 | 112.2 | 110.6 | 66.7
407 | 217 | 469.1 | 187.64 | 219.3403 | 215.9 | 193.9 | 223.3 | 202.9 | 495.3 | 28.3 | 20.8 | 53.4 | 3.8 | 217.1 | 8.5 | 359 | 380.3 | 812.1 | 581 | 794.2 | 463.5 | 692.2 | 808.9 | 302 | 739.8 | 82.5 | 221 | 34.5 | 228.9 | 212.1 | 45.3 | 112.6 | 111.1 | 66.9
408 | 218 | 468.6 | 187.44 | 219.1066 | 217.1 | 194.5 | 223.8 | 204.2 | 496.5 | 28.3 | 20.8 | 53.5 | 4 | 202.7 | 7.4 | 361.5 | 799.7 | 822.5 | 582 | 795.1 | 467.1 | 695.4 | 813.9 | 304.4 | 739.6 | 82.8 | 221.3 | 34.6 | 229.6 | 212.5 | 45.5 | 113 | 111.6 | 67.2
409 | 219 | 469.1 | 187.64 | 219.3403 | 217.4 | 194.8 | 224.3 | 205.5 | 504 | 28.4 | 20.8 | 53.5 | 3.9 | 259.3 | 5.9 | 363.9 | 796.7 | 826.9 | 583.3 | 796.5 | 470.7 | 700.9 | 820.2 | 307 | 740.6 | 83.1 | 221.7 | 34.7 | 229.9 | 212.8 | 45.7 | 113.4 | 112.1 | 67.5
410 | 220 | 468 | 187.2 | 218.826 | 217.1 | 195.3 | 224.6 | 206.8 | 521.4 | 28.4 | 20.8 | 53.6 | 3.9 | 208.8 | 6 | 366.3 | 797 | 824.8 | 584.5 | 794.8 | 474.5 | 701.1 | 822.9 | 309.7 | 740.6 | 83.4 | 222 | 34.8 | 230.5 | 213.1 | 45.9 | 113.7 | 112.6 | 67.8
411 | 221 | 467.9 | 187.16 | 218.7793 | 216.7 | 196.8 | 225 | 207.6 | 528.9 | 28.5 | 20.8 | 53.7 | 3.5 | 217.1 | 7.5 | 368.9 | 795.5 | 832.2 | 586.1 | 798.5 | 478.3 | 700.8 | 820.5 | 312.2 | 741.5 | 83.7 | 222 | 35 | 231.2 | 213.3 | 46.1 | 114.1 | 113.1 | 68
412 | 222 | 468.4 | 187.36 | 219.013 | 217.3 | 197 | 224.8 | 207.8 | 524.5 | 28.5 | 20.8 | 53.8 | 3.3 | 227.1 | 7.3 | 371.4 | 792.3 | 828.4 | 587.1 | 800.2 | 482.1 | 701.5 | 818.5 | 314.7 | 743.2 | 84 | 222.1 | 35.1 | 231.8 | 213.8 | 46.3 | 114.6 | 113.6 | 68.3
413 | 223 | 468.4 | 187.36 | 219.013 | 217 | 197.7 | 224.9 | 208.3 | 519.4 | 28.5 | 20.8 | 53.8 | 3.3 | 229 | 6.5 | 373.9 | 790.4 | 818.4 | 588.7 | 801.8 | 485.9 | 701.5 | 812.9 | 317 | 744.9 | 84.3 | 222 | 35.2 | 232.6 | 213.9 | 46.5 | 115 | 114 | 68.5
414 | 224 | 468.4 | 187.36 | 219.013 | 215.8 | 198 | 224.6 | 208.5 | 514.3 | 28.6 | 20.8 | 53.9 | 3.5 | 215 | 5.9 | 376.5 | 792.2 | 815.2 | 590.2 | 801.4 | 489.4 | 701.3 | 812.8 | 319.6 | 746.1 | 84.7 | 221.8 | 35.4 | 233.1 | 213.9 | 46.7 | 115.4 | 114.5 | 68.8
415 | 225 | 467.9 | 187.16 | 218.7793 | 215.7 | 198.2 | 224.7 | 208.6 | 508.6 | 28.7 | 20.8 | 53.9 | 3.7 | 233.3 | 5.7 | 379.5 | 791.6 | 809.4 | 592.4 | 802.2 | 492.8 | 702.2 | 810.6 | 322.3 | 748.2 | 85 | 221.8 | 35.5 | 233.8 | 214.5 | 47 | 115.8 | 115 | 68.9
416 | 226 | 468.5 | 187.4 | 219.0598 | 216.8 | 198.6 | 225.9 | 208.5 | 495.4 | 28.8 | 20.8 | 54 | 3.5 | 226.6 | 6.8 | 382.8 | 785.6 | 811.3 | 593.7 | 803.8 | 495.8 | 700.6 | 789.6 | 324.7 | 749.1 | 85.3 | 221.7 | 35.6 | 234 | 215 | 47.2 | 116.1 | 115.4 | 69.3
417 | 227 | 468.1 | 187.24 | 218.8728 | 217.4 | 198 | 226.9 | 208.7 | 484.7 | 28.8 | 20.8 | 54 | 3.2 | 221.7 | 7.8 | 386.3 | 784.1 | 796.4 | 595.7 | 808.8 | 498.5 | 702.1 | 784.8 | 327.3 | 750.2 | 85.6 | 222 | 35.8 | 233.6 | 215.6 | 47.4 | 116.5 | 115.9 | 69.5
418 | 228 | 468.3 | 187.32 | 218.9663 | 216.2 | 197.8 | 227.5 | 209 | 473.1 | 28.9 | 20.8 | 54.1 | 2.8 | 228.1 | 8.1 | 389.6 | 533.7 | 772.2 | 598 | 810.8 | 501.1 | 702.6 | 771.3 | 329.3 | 751.6 | 85.8 | 222.2 | 35.9 | 233.8 | 215.8 | 47.6 | 116.9 | 116.4 | 69.7
419 | 229 | 468.2 | 187.28 | 218.9195 | 216.9 | 197.1 | 227.9 | 209.6 | 466.3 | 29 | 20.8 | 54.2 | 2.9 | 252.9 | 8.1 | 392.8 | 787.2 | 757.8 | 600.7 | 813.1 | 503.7 | 700.3 | 757 | 331.8 | 751.9 | 86.1 | 222.4 | 36 | 233.8 | 215.5 | 47.8 | 117.4 | 116.8 | 70
420 | 230 | 468.6 | 187.44 | 219.1066 | 217.9 | 197 | 227.6 | 209.6 | 457.6 | 29 | 20.8 | 54.2 | 2.7 | 233 | 9 | 396.1 | 800.1 | 746.2 | 603.5 | 813.2 | 506.2 | 699.1 | 744.5 | 334.2 | 753.3 | 86.4 | 222.6 | 36.2 | 234.2 | 216 | 48 | 117.8 | 117.2 | 70.3
421 | 231 | 469.2 | 187.68 | 219.3871 | 217.9 | 196.9 | 227.9 | 210.1 | 448.2 | 29.1 | 20.8 | 54.3 | 2.8 | 242 | 8.8 | 399.7 | 796.4 | 739.8 | 606.1 | 814.2 | 508.8 | 702.9 | 734.1 | 336.9 | 754.7 | 86.7 | 222.9 | 36.3 | 234.5 | 215.9 | 48.2 | 118.3 | 117.6 | 70.5
422 | 232 | 469.5 | 187.8 | 219.5274 | 218.2 | 196.2 | 228.3 | 210.1 | 440.3 | 29.1 | 20.8 | 54.4 | 3.7 | 264.1 | 9.3 | 403.3 | 795.2 | 742.7 | 609.1 | 817 | 511.5 | 708 | 726.8 | 339.6 | 754.9 | 86.9 | 223.2 | 36.4 | 234.2 | 216.2 | 48.4 | 118.8 | 118 | 70.8
423 | 233 | 469.1 | 187.64 | 219.3403 | 218.6 | 195.4 | 228.7 | 210.3 | 431.5 | 29.1 | 20.8 | 54.5 | 3.6 | 258.4 | 10 | 406.7 | 802.9 | 731.2 | 612 | 820.4 | 514 | 705.4 | 709.8 | 341.5 | 755.3 | 87.2 | 223.6 | 36.6 | 234.3 | 217 | 48.6 | 119.2 | 118.4 | 71
424 | 234 | 468.9 | 187.56 | 219.2468 | 218.3 | 195.4 | 228.6 | 210.6 | 424.8 | 29.1 | 20.8 | 54.6 | 2.8 | 245.5 | 9.4 | 410.4 | 803.1 | 730.3 | 614.8 | 816.7 | 516.8 | 711.1 | 711.9 | 345 | 756.9 | 87.5 | 224 | 36.7 | 234.7 | 216.7 | 48.8 | 119.6 | 118.8 | 71.2
425 | 235 | 468.7 | 187.48 | 219.1533 | 217.8 | 195.7 | 229.7 | 211 | 426.8 | 29.2 | 20.8 | 54.7 | 3.3 | 246.6 | 8.3 | 414.3 | 802.3 | 747.6 | 617.7 | 820 | 519.7 | 720 | 723.4 | 348.6 | 758.7 | 87.8 | 224.4 | 36.8 | 235 | 216.5 | 49.1 | 119.9 | 119.3 | 71.5
426 | 236 | 466.4 | 186.56 | 218.0779 | 219 | 195.7 | 230.2 | 211.4 | 434.4 | 29.2 | 20.8 | 54.9 | 3.7 | 242.6 | 8.6 | 417.7 | 798.8 | 745.7 | 619.4 | 823 | 523 | 726.4 | 737.8 | 352.3 | 760.2 | 88.1 | 225 | 37 | 235.5 | 216.5 | 49.3 | 120.3 | 119.7 | 71.8
427 | 237 | 467.8 | 187.12 | 218.7325 | 220.6 | 195.4 | 230.5 | 211.9 | 435 | 29.3 | 20.7 | 55 | 3.3 | 255.3 | 9.2 | 420.7 | 797.9 | 738.9 | 621.1 | 824.6 | 526.1 | 723.7 | 725.7 | 355.2 | 761.3 | 88.4 | 225.4 | 37.1 | 235.6 | 216.8 | 49.5 | 120.7 | 120.1 | 72
428 | 238 | 468 | 187.2 | 218.826 | 222.2 | 195.3 | 231.2 | 212.2 | 432.5 | 29.3 | 20.7 | 55.1 | 3.2 | 251 | 11.1 | 424.8 | 803 | 744.1 | 623.5 | 823.2 | 529 | 722.4 | 735.4 | 357.9 | 762 | 88.7 | 226 | 37.2 | 235.1 | 217.7 | 49.7 | 121 | 120.6 | 72.3
429 | 239 | 468.1 | 187.24 | 218.8728 | 223.6 | 194.8 | 232 | 212.4 | 439.6 | 29.4 | 20.7 | 55.2 | 3.1 | 261.8 | 10.3 | 429.5 | 793.5 | 750.6 | 625 | 821.1 | 532.1 | 719.2 | 739.4 | 360.1 | 762.9 | 89 | 226.7 | 37.4 | 235.1 | 218.1 | 49.9 | 121.5 | 121 | 72.5
430 | 240 | 468.1 | 187.24 | 218.8728 | 224.7 | 194.4 | 233.4 | 212.3 | 441.3 | 29.5 | 20.7 | 55.3 | 3.5 | 250 | 8.7 | 433.6 | 782.9 | 746.9 | 626.5 | 822.8 | 535.2 | 717.8 | 744.4 | 362.3 | 762.9 | 89.3 | 227.3 | 37.5 | 235.7 | 218.6 | 50.1 | 122 | 121.4 | 72.8
431 | 241 | 467.5 | 187 | 218.5922 | 225.9 | 194.3 | 234.4 | 212.3 | 441.9 | 29.5 | 20.7 | 55.4 | 3 | 280.5 | 9.3 | 437.6 | 788.8 | 753.8 | 628.8 | 826 | 538.3 | 717.8 | 745.6 | 364.4 | 763.7 | 89.6 | 228 | 37.6 | 236.4 | 218.4 | 50.3 | 122.4 | 121.8 | 73
432 | 242 | 468.3 | 187.32 | 218.9663 | 227.1 | 194.7 | 235.3 | 212.8 | 449.9 | 29.6 | 20.7 | 55.5 | 3.4 | 249.9 | 8.5 | 441.8 | 767.3 | 745.9 | 630.9 | 828.1 | 541.3 | 717.9 | 746 | 366.7 | 765.6 | 89.9 | 228.8 | 37.7 | 236.8 | 219.2 | 50.6 | 122.8 | 122.2 | 73.3
433 | 243 | 468 | 187.2 | 218.826 | 227.3 | 194.7 | 235.8 | 213 | 447.8 | 29.6 | 20.7 | 55.5 | 3.7 | 259.1 | 10.4 | 445.8 | 789.8 | 746.5 | 634.6 | 828.5 | 544 | 714.7 | 735.1 | 368.3 | 766.8 | 90.3 | 229.2 | 37.9 | 238.1 | 220.3 | 50.8 | 123.2 | 122.6 | 73.6
434 | 244 | 468.4 | 187.36 | 219.013 | 227.5 | 194.3 | 236.5 | 213.2 | 440.8 | 29.7 | 20.7 | 55.6 | 3.7 | 259.6 | 10.6 | 450.1 | 795.4 | 735.5 | 638.5 | 830.4 | 546.2 | 712.7 | 730.5 | 370.1 | 767.4 | 90.6 | 229.7 | 38 | 237.8 | 221.2 | 51 | 123.7 | 123 | 73.8
435 | 245 | 466.6 | 186.64 | 218.1714 | 226.9 | 194.3 | 237.4 | 213.7 | 440.2 | 29.8 | 20.7 | 55.7 | 3.8 | 259.7 | 10.6 | 454.2 | 802.5 | 733.3 | 642.1 | 833 | 548.5 | 714.2 | 724.8 | 372.8 | 768 | 90.9 | 230.3 | 38.1 | 237.9 | 222.3 | 51.2 | 124.1 | 123.5 | 73.2
436 | 246 | 467.4 | 186.96 | 218.5455 | 228.2 | 194 | 237.2 | 213.3 | 439.1 | 29.8 | 20.7 | 55.8 | 4 | 264.9 | 10.3 | 458.6 | 800.5 | 740.7 | 644.8 | 833.5 | 550.9 | 718.1 | 733.2 | 375.7 | 769.2 | 91.2 | 230.7 | 38.3 | 238.4 | 223.3 | 51.4 | 124.7 | 123.9 | 73.8
437 | 247 | 468.3 | 187.32 | 218.9663 | 229.2 | 193 | 236.9 | 213.7 | 440.3 | 29.7 | 20.7 | 55.9 | 4.3 | 264.3 | 11.1 | 462.9 | 799.6 | 731.3 | 647.1 | 835 | 553.3 | 716.9 | 721.9 | 378.2 | 769.9 | 91.6 | 231.4 | 38.4 | 238.2 | 224.3 | 51.6 | 125.2 | 124.3 | 74.3
438 | 248 | 468 | 187.2 | 218.826 | 230.4 | 192 | 236.9 | 213.6 | 436 | 29.7 | 20.7 | 56 | 4.6 | 267.9 | 12.6 | 466.9 | 801.8 | 729.5 | 649.7 | 837.2 | 555.4 | 715.5 | 716 | 380 | 771.1 | 91.9 | 231.9 | 38.5 | 238.7 | 224 | 51.8 | 125.6 | 124.6 | 74.8
439 | 249 | 467.9 | 187.16 | 218.7793 | 230.2 | 192.2 | 237.4 | 213.8 | 430.8 | 29.7 | 20.7 | 56.1 | 4.2 | 268.9 | 13 | 470.1 | 798.4 | 723.7 | 652.6 | 839.8 | 557.2 | 716.8 | 712.6 | 381.9 | 772.5 | 92.2 | 232.3 | 38.7 | 238.5 | 223.8 | 52.1 | 126 | 125.1 | 74.8
440 | 250 | 468.8 | 187.52 | 219.2001 | 231.2 | 192.3 | 238.6 | 213.8 | 430.4 | 29.8 | 20.7 | 56.1 | 4.1 | 265.3 | 12.5 | 473.9 | 800.8 | 732.3 | 656.6 | 842.2 | 559.1 | 713.2 | 705.7 | 383.5 | 773.7 | 92.6 | 232.8 | 38.8 | 238.7 | 224.4 | 52.3 | 126.4 | 125.5 | 75.1
441 | 251 | 466.9 | 186.76 | 218.3117 | 231.1 | 191.9 | 240.3 | 213.6 | 425.5 | 29.9 | 20.7 | 56.2 | 4.3 | 262 | 12.6 | 477.5 | 800.5 | 733.3 | 660.4 | 847.6 | 560.9 | 710.5 | 702.1 | 385 | 774.1 | 92.9 | 233.4 | 38.9 | 238.8 | 224.6 | 52.5 | 126.8 | 125.9 | 75
442 | 252 | 467.3 | 186.92 | 218.4987 | 231.6 | 192.1 | 240.2 | 214 | 426.6 | 29.9 | 20.7 | 56.4 | 4.6 | 259.8 | 13.3 | 480.9 | 797.2 | 749.1 | 664.4 | 850.8 | 562.8 | 711.8 | 703.7 | 387.1 | 775.1 | 93.3 | 234.1 | 39.1 | 238.8 | 224.4 | 52.7 | 127.1 | 126.3 | 75.2
443 | 253 | 468.2 | 187.28 | 218.9195 | 231.7 | 193.2 | 240.4 | 214.6 | 430.7 | 30 | 20.7 | 56.4 | 4.6 | 263.5 | 12.9 | 484.3 | 796.1 | 763.1 | 671.6 | 852 | 564.7 | 712.6 | 714.4 | 389 | 775.3 | 93.6 | 234.5 | 39.2 | 239 | 224.3 | 52.9 | 127.5 | 126.7 | 75.6
444 | 254 | 467.6 | 187.04 | 218.639 | 230.6 | 193.9 | 240.5 | 214.4 | 433.7 | 30 | 20.7 | 56.5 | 4.5 | 257.5 | 12.4 | 487.9 | 792.1 | 768.8 | 679 | 849.9 | 566.7 | 711.6 | 725.9 | 391.3 | 775 | 94 | 234.9 | 39.3 | 238.9 | 224.9 | 53.1 | 127.8 | 127.1 | 75.8
445 | 255 | 471.2 | 188.48 | 220.3223 | 231.2 | 194.1 | 239.8 | 214.3 | 439 | 30 | 20.7 | 56.6 | 4.2 | 254.6 | 12.5 | 491.7 | 792 | 771.8 | 686.4 | 847.1 | 568.8 | 707.6 | 734.7 | 393.6 | 775.1 | 94.4 | 235.3 | 39.5 | 239.3 | 225 | 53.3 | 128.3 | 127.5 | 76.7
446 | 256 | 471.9 | 188.76 | 220.6496 | 231.3 | 195.1 | 239.9 | 214.9 | 446.8 | 30.1 | 20.7 | 56.6 | 3.6 | 255.8 | 12.4 | 495.6 | 793 | 775.7 | 692.7 | 844.8 | 571.1 | 705.3 | 734.3 | 395.7 | 775.3 | 94.7 | 235.7 | 39.6 | 239.2 | 224.8 | 53.5 | 128.6 | 128 | 77
447 | 257 | 471.7 | 188.68 | 220.556 | 231.7 | 195.9 | 239.9 | 215.1 | 448.9 | 30.1 | 20.7 | 56.6 | 3.5 | 251.2 | 11.7 | 499.2 | 795.5 | 780.2 | 696.2 | 841 | 573.6 | 704.5 | 740.2 | 399 | 775.3 | 95.1 | 236.2 | 39.8 | 239.4 | 224.9 | 53.7 | 128.9 | 128.4 | 77.4
448 | 258 | 469.6 | 187.84 | 219.5741 | 231.3 | 196 | 240 | 215.2 | 463.9 | 30.1 | 20.7 | 56.7 | 3.5 | 253.1 | 11.8 | 502.5 | 793.2 | 780.5 | 697.9 | 835.9 | 576.2 | 705.5 | 755 | 403 | 774.6 | 95.5 | 236.9 | 39.9 | 239.3 | 225 | 54 | 129.2 | 128.8 | 77.7
449 | 259 | 468.5 | 187.4 | 219.0598 | 231.6 | 195.8 | 240.3 | 214.9 | 472 | 30 | 20.7 | 56.8 | 3.2 | 249.1 | 11.5 | 505.6 | 793.5 | 783.8 | 699.8 | 826.1 | 578.7 | 707.9 | 767.1 | 406.5 | 774.4 | 95.8 | 237.2 | 40 | 239 | 224.7 | 54.2 | 129.7 | 129.3 | 77.9
450 | 260 | 468.8 | 187.52 | 219.2001 | 233.6 | 197.3 | 241 | 215.3 | 486.2 | 30 | 20.7 | 56.9 | 3.3 | 252.9 | 10.6 | 509 | 794.3 | 781.3 | 703.9 | 818.7 | 581.4 | 705.9 | 779.1 | 410.6 | 773.2 | 96.2 | 237.4 | 40.2 | 239.5 | 224.7 | 54.4 | 130.1 | 129.7 | 78.2
451 | 261 | 468.3 | 187.32 | 218.9663 | 235.1 | 198.2 | 241.9 | 216.3 | 502.2 | 30.1 | 20.7 | 57 | 3.3 | 257 | 10.5 | 512.8 | 788 | 786 | 706.5 | 810.7 | 584.1 | 708.2 | 787.8 | 414.8 | 772.4 | 96.6 | 237.6 | 40.3 | 240.4 | 225.4 | 54.6 | 130.4 | 130.1 | 78.5
452 | 262 | 469.1 | 187.64 | 219.3403 | 236 | 198.6 | 241.7 | 217.4 | 521.1 | 30.1 | 20.7 | 57.2 | 3.5 | 261.9 | 11 | 516.7 | 782.4 | 791.2 | 709.4 | 808.8 | 586.7 | 714.1 | 798.2 | 418.9 | 772.5 | 96.9 | 237.7 | 40.4 | 241.1 | 226.1 | 54.8 | 130.8 | 130.6 | 78.8
453 | 263 | 469.2 | 187.68 | 219.3871 | 235.4 | 199.9 | 241.2 | 218.5 | 538.4 | 30.2 | 20.7 | 57.3 | 3.6 | 264.5 | 12.1 | 520.8 | 783.6 | 797.1 | 712.3 | 804.7 | 589.4 | 719.1 | 809.9 | 422.9 | 772.2 | 97.3 | 238 | 40.6 | 242.5 | 226.9 | 55 | 131.3 | 131.1 | 79
454 | 264 | 469.4 | 187.76 | 219.4806 | 234.7 | 201.6 | 241.3 | 219.2 | 553 | 30.2 | 20.7 | 57.4 | 3.3 | 274.9 | 12 | 525.1 | 780.2 | 809.7 | 713.1 | 803.4 | 592 | 722.4 | 818.1 | 426.2 | 771.9 | 97.6 | 238.3 | 40.7 | 243.4 | 228 | 55.2 | 131.8 | 131.6 | 79.4
455 | 265 | 469.4 | 187.76 | 219.4806 | 234.2 | 202.9 | 241.6 | 220 | 556.7 | 30.3 | 20.7 | 57.5 | 3.3 | 277.6 | 11.6 | 529.8 | 777 | 824.2 | 713.5 | 806.3 | 594.6 | 728 | 824.2 | 429.8 | 773.5 | 98 | 238.8 | 40.8 | 244 | 229 | 55.4 | 132.3 | 132.1 | 79.7
456 | 266 | 468.8 | 187.52 | 219.2001 | 233.8 | 204.4 | 241.8 | 220.6 | 554.1 | 30.3 | 20.7 | 57.7 | 3.5 | 278 | 12 | 534.2 | 776.3 | 820.4 | 715.4 | 805.2 | 597 | 726.7 | 829.1 | 432.5 | 772.9 | 98.3 | 239.2 | 41 | 243.9 | 229.6 | 55.6 | 132.6 | 132.6 | 80
457 | 267 | 469.3 | 187.72 | 219.4339 | 234 | 206.1 | 243.2 | 221.1 | 556.1 | 30.3 | 20.7 | 57.9 | 3.2 | 279.4 | 11.4 | 538.8 | 774 | 825.1 | 716.1 | 802.2 | 599.4 | 732 | 834 | 436 | 773.4 | 98.7 | 239.4 | 41.1 | 244.1 | 230.5 | 55.8 | 133 | 133.1 | 80.3
458 | 268 | 469.3 | 187.72 | 219.4339 | 233.9 | 207.3 | 243.6 | 221.7 | 562.3 | 30.3 | 20.7 | 57.9 | 2.9 | 295.5 | 11.3 | 543.7 | 774.7 | 832.4 | 717.4 | 797.2 | 601.9 | 736.8 | 838.3 | 439.7 | 774 | 99 | 239.8 | 41.3 | 245.1 | 230.9 | 56.1 | 133.4 | 133.7 | 80.6
459 | 269 | 468.9 | 187.56 | 219.2468 | 234.5 | 208.4 | 244.1 | 222.2 | 561.4 | 30.3 | 20.7 | 58 | 3 | 279.4 | 10.6 | 548.9 | 772.9 | 831.3 | 717.3 | 799.4 | 604.2 | 740.7 | 833.8 | 442.6 | 775.2 | 99.4 | 240 | 41.4 | 245.9 | 231.3 | 56.3 | 133.8 | 134.3 | 80.9
460 | 270 | 469 | 187.6 | 219.2936 | 235.4 | 209.1 | 244 | 223.1 | 550.3 | 30.4 | 20.7 | 58.1 | 3.1 | 278.7 | 9.3 | 553.8 | 771 | 826.8 | 717.9 | 807.7 | 606.2 | 746.8 | 823 | 445.4 | 777 | 99.7 | 240.3 | 41.5 | 246.3 | 231.6 | 56.5 | 134.3 | 134.9 | 81.2
461 | 271 | 469.1 | 187.64 | 219.3403 | 236 | 209.1 | 242.7 | 223.2 | 538.2 | 30.5 | 20.7 | 58.1 | 2.9 | 275.8 | 8.4 | 558.7 | 769 | 823.5 | 718.6 | 818.1 | 608 | 750.4 | 816.3 | 448.1 | 778.8 | 100 | 240.5 | 41.7 | 246.5 | 231.6 | 56.7 | 134.6 | 135.4 | 81.5
462 | 272 | 468.7 | 187.48 | 219.1533 | 235.9 | 208.6 | 241.6 | 223.3 | 540.1 | 30.5 | 20.7 | 58.2 | 2.8 | 268.3 | 7.7 | 564.3 | 766.3 | 821.9 | 717.8 | 822.7 | 609.9 | 751.8 | 822 | 451.5 | 780 | 100.4 | 240.2 | 41.8 | 246.8 | 231.7 | 56.9 | 135 | 135.9 | 81.8
463 | 273 | 468.8 | 187.52 | 219.2001 | 236 | 208.3 | 240.3 | 223.7 | 545.6 | 30.6 | 20.7 | 58.3 | 2.8 | 280.8 | 7.6 | 570 | 770.9 | 812.2 | 720.3 | 826.1 | 611.6 | 752.6 | 812 | 454.3 | 780.4 | 100.7 | 240 | 41.9 | 247.5 | 231.8 | 57.1 | 135.5 | 136.5 | 82
464 | 274 | 468.7 | 187.48 | 219.1533 | 235.4 | 208.6 | 238.5 | 224.2 | 542.5 | 30.6 | 20.7 | 58.4 | 2.9 | 281.9 | 9.4 | 575.8 | 771.9 | 823.5 | 723.2 | 826 | 613.6 | 756.1 | 819.6 | 457.4 | 780.6 | 101 | 239.7 | 42.1 | 248 | 232 | 57.3 | 136 | 137 | 82.3
465 | 275 | 468.8 | 187.52 | 219.2001 | 235.5 | 209.4 | 237.5 | 224.8 | 550.9 | 30.6 | 20.7 | 58.4 | 2.9 | 290.3 | 10.8 | 581.7 | 769.8 | 829.6 | 728.5 | 820.6 | 616 | 760.5 | 828.9 | 461 | 781.3 | 101.3 | 239.7 | 42.2 | 248.1 | 232.3 | 57.5 | 136.4 | 137.5 | 82.6
466 | 276 | 469 | 187.6 | 219.2936 | 236 | 211.1 | 238.6 | 225.2 | 562.4 | 30.7 | 20.7 | 58.5 | 3 | 297 | 10.5 | 587.9 | 767.6 | 829.3 | 733.9 | 817.1 | 618.4 | 762.6 | 827.4 | 463.6 | 780.7 | 101.6 | 239.6 | 42.4 | 248 | 232.8 | 57.8 | 136.7 | 138.1 | 82.9
467 | 277 | 468.5 | 187.4 | 219.0598 | 236.1 | 213 | 238.6 | 225.6 | 549.8 | 30.7 | 20.7 | 58.6 | 3.1 | 293.8 | 10 | 594.2 | 767.4 | 820 | 738 | 814.4 | 620.9 | 760.7 | 826.6 | 465.5 | 781.3 | 101.9 | 239.8 | 42.5 | 248 | 232.6 | 58 | 137 | 138.7 | 83.2
468 | 278 | 468.2 | 187.28 | 218.9195 | 236.6 | 213.5 | 238.9 | 226 | 548.2 | 30.8 | 20.6 | 58.7 | 3.5 | 288.1 | 9.7 | 600.4 | 771 | 808.9 | 742.9 | 808.6 | 623.4 | 753.9 | 824.9 | 467.7 | 780.4 | 102.1 | 240.2 | 42.6 | 248.6 | 232.4 | 58.2 | 137.3 | 139.2 | 83.4
469 | 279 | 468.8 | 187.52 | 219.2001 | 237.4 | 213.5 | 239.5 | 227 | 555.7 | 30.9 | 20.6 | 58.7 | 3.3 | 291.8 | 9.1 | 607.1 | 774.7 | 806.5 | 748.2 | 799.4 | 625.9 | 750.4 | 828.2 | 470.5 | 779.5 | 102.4 | 240.3 | 42.8 | 249.3 | 232.4 | 58.4 | 137.6 | 139.8 | 83.8
470 | 280 | 470.5 | 188.2 | 219.995 | 237.9 | 214.2 | 239.8 | 227.9 | 567.7 | 30.9 | 20.6 | 58.8 | 3 | 296.3 | 8.6 | 613.6 | 776.2 | 798 | 753 | 788.7 | 628.5 | 744.2 | 823.8 | 472.9 | 776.9 | 102.7 | 240.5 | 42.9 | 250.1 | 232.3 | 58.6 | 138.1 | 140.3 | 84
471 | 281 | 469.2 | 187.68 | 219.3871 | 238.1 | 215.2 | 241.2 | 228.9 | 578.3 | 30.9 | 20.6 | 58.9 | 3.4 | 294.2 | 8.2 | 620.1 | 776.5 | 801.6 | 756.4 | 789.1 | 631.2 | 741.1 | 818.1 | 475.2 | 776 | 102.9 | 240.3 | 43 | 250.4 | 232.3 | 58.8 | 138.6 | 140.8 | 84.3
472 | 282 | 469 | 187.6 | 219.2936 | 238.7 | 215.3 | 241.5 | 229.4 | 581.3 | 30.9 | 20.6 | 59 | 2.9 | 296.7 | 6.8 | 626.7 | 777 | 805.4 | 759.1 | 791.6 | 633.9 | 742.2 | 821.6 | 477 | 776.3 | 103.2 | 240.8 | 43.2 | 251 | 232.3 | 59 | 139 | 141.3 | 84.6
473 | 283 | 468.1 | 187.24 | 218.8728 | 239.2 | 215.5 | 241.9 | 229.7 | 580.1 | 31 | 20.6 | 59.2 | 2.9 | 296 | 6.2 | 632.7 | 774 | 820 | 759.3 | 794.6 | 636.5 | 746.1 | 818.4 | 479.5 | 776.7 | 103.5 | 241.3 | 43.3 | 251.4 | 232.3 | 59.2 | 139.3 | 141.8 | 85
474 | 284 | 468.3 | 187.32 | 218.9663 | 239.6 | 216.3 | 242.4 | 229.7 | 568.5 | 31 | 20.6 | 59.3 | 2.7 | 284.3 | 6.4 | 638.1 | 772.1 | 822.5 | 762.3 | 795.3 | 638.7 | 741.9 | 813.5 | 480.4 | 776.1 | 103.8 | 241.8 | 43.5 | 251.9 | 232.7 | 59.5 | 139.9 | 142.3 | 85.2
475 | 285 | 469.6 | 187.84 | 219.5741 | 240 | 216.6 | 243 | 230 | 562.6 | 31 | 20.6 | 59.4 | 3 | 251.4 | 5.3 | 644.6 | 774.9 | 820 | 767.5 | 797.8 | 640.6 | 735.9 | 809 | 481 | 775.2 | 104 | 241.9 | 43.6 | 252.2 | 232.8 | 59.7 | 140.3 | 142.9 | 85.5
476 | 286 | 469.6 | 187.84 | 219.5741 | 239.9 | 216.4 | 243.5 | 230.5 | 560 | 31.1 | 20.6 | 59.5 | 2.6 | 269.6 | 4.6 | 652.2 | 776.3 | 826.8 | 771.9 | 802.9 | 642.4 | 735.3 | 813.4 | 482.1 | 775.1 | 104.3 | 242.2 | 43.7 | 252.6 | 232.9 | 59.9 | 140.8 | 143.5 | 85.8
477 | 287 | 469.7 | 187.88 | 219.6209 | 239.4 | 216.9 | 243.5 | 230.5 | 556.4 | 31.1 | 20.6 | 59.5 | 2.7 | 250.5 | 4.2 | 659.4 | 775.7 | 828.1 | 773.9 | 803.7 | 644.1 | 732.1 | 812.2 | 482.9 | 775.5 | 104.6 | 242.7 | 43.9 | 253 | 233.1 | 60.1 | 141.2 | 144 | 86.1
478 | 288 | 470.2 | 188.08 | 219.8547 | 239.2 | 217.2 | 243.3 | 230.7 | 543.2 | 31.1 | 20.6 | 59.6 | 3 | 219.6 | 4.8 | 665.6 | 774.4 | 833.4 | 774.9 | 809.2 | 645.8 | 730.8 | 812.8 | 482.9 | 775.9 | 104.8 | 242.6 | 44 | 252.6 | 233.5 | 60.3 | 141.6 | 144.5 | 86.4
479 | 289 | 470 | 188 | 219.7612 | 238.9 | 217.5 | 243.2 | 230.4 | 540.8 | 31.1 | 20.6 | 59.7 | 3.1 | 232.8 | 5 | 671.1 | 772.5 | 839.3 | 775.1 | 811.6 | 647.5 | 735.5 | 816.8 | 484.4 | 777.4 | 105.1 | 242.3 | 44.2 | 252.8 | 234 | 60.6 | 142 | 145 | 86.7
480 | 290 | 469.7 | 187.88 | 219.6209 | 238.6 | 218 | 243.9 | 230.5 | 538.7 | 31.1 | 20.6 | 59.7 | 3 | 254.6 | 5.3 | 676.6 | 770.5 | 841.3 | 775.9 | 815.2 | 649.2 | 733 | 817 | 485.6 | 777.6 | 105.4 | 242 | 44.3 | 252.5 | 234.2 | 60.8 | 142.3 | 145.5 | 87
481 | 291 | 469 | 187.6 | 219.2936 | 238 | 217.5 | 244.1 | 230.5 | 535.5 | 31.2 | 20.6 | 59.8 | 3.2 | 253 | 5.2 | 683.1 | 771.1 | 836.6 | 777.9 | 816.3 | 650.8 | 732.9 | 809.7 | 486.4 | 778.2 | 105.6 | 241.6 | 44.4 | 252.2 | 234.3 | 61 | 142.7 | 146.1 | 87.2
482 | 292 | 469.7 | 187.88 | 219.6209 | 238.1 | 216.9 | 243.5 | 230.6 | 529.8 | 31.3 | 20.6 | 60 | 3.2 | 267.8 | 4.6 | 689.5 | 773.3 | 836.6 | 780.1 | 818.7 | 652.4 | 730.6 | 802 | 487.8 | 778.1 | 105.9 | 241.7 | 44.6 | 252.3 | 234.9 | 61.2 | 142.9 | 146.6 | 87.5
483 | 293 | 469.4 | 187.76 | 219.4806 | 239.1 | 216 | 243.4 | 230.7 | 527.5 | 31.4 | 20.6 | 60.1 | 3.2 | 255.1 | 4.1 | 695.3 | 773 | 836.6 | 782.1 | 822.3 | 654 | 731.8 | 806 | 488.7 | 778 | 106.1 | 241.2 | 44.7 | 251.8 | 235.4 | 61.4 | 143.4 | 147.1 | 87.9
484 | 294 | 469.3 | 187.72 | 219.4339 | 239.7 | 215.4 | 244.2 | 230.9 | 527.9 | 31.5 | 20.6 | 60.2 | 3.6 | 235 | 3.7 | 700.7 | 772.8 | 835 | 785 | 822.6 | 655.2 | 730.9 | 806.5 | 489.6 | 778.6 | 106.4 | 240.8 | 44.9 | 251.7 | 235.7 | 61.6 | 143.9 | 147.5 | 88.1
485 | 295 | 468.2 | 187.28 | 218.9195 | 239.6 | 215.8 | 244.3 | 231 | 520.5 | 31.5 | 20.6 | 60.3 | 3.9 | 239.9 | 3.5 | 707.4 | 773.2 | 832.1 | 787.6 | 823.8 | 656.1 | 730.9 | 802.1 | 490.1 | 778.9 | 106.6 | 240.7 | 45 | 252.3 | 236.1 | 61.9 | 144.2 | 148 | 88.4
486 | 296 | 468.5 | 187.4 | 219.0598 | 239.5 | 215.5 | 244.2 | 231.3 | 520.9 | 31.6 | 20.6 | 60.4 | 4.5 | 252.3 | 4.1 | 713.8 | 772.7 | 830.3 | 789.8 | 827.2 | 657.3 | 732.4 | 808.2 | 491.5 | 779 | 106.9 | 241 | 45.2 | 252.7 | 236.5 | 62.1 | 144.6 | 148.5 | 88.7
487 | 297 | 468.9 | 187.56 | 219.2468 | 239.7 | 215.2 | 244 | 231.9 | 529.1 | 31.6 | 20.6 | 60.6 | 4.8 | 264.7 | 4.3 | 719.8 | 772.6 | 834.9 | 792.5 | 827.9 | 658.7 | 736.2 | 815.7 | 493.5 | 779.4 | 107.1 | 240.9 | 45.3 | 253 | 236.7 | 62.3 | 145.1 | 148.9 | 89
488 | 298 | 469.6 | 187.84 | 219.5741 | 240.8 | 215.5 | 244 | 232.3 | 547.9 | 31.6 | 20.6 | 60.6 | 4.7 | 267.1 | 4.1 | 725.6 | 772.9 | 841.1 | 795.5 | 825.8 | 660.1 | 735.4 | 822.6 | 495.1 | 779.8 | 107.4 | 240.8 | 45.4 | 253.5 | 236.5 | 62.5 | 145.6 | 149.4 | 89.3
489 | 299 | 469.3 | 187.72 | 219.4339 | 241.7 | 215.8 | 244.1 | 231.9 | 558.3 | 31.7 | 20.6 | 60.8 | 5 | 261.9 | 4.4 | 731.4 | 772.2 | 844.3 | 798.3 | 822 | 661.6 | 734.5 | 827.7 | 496.1 | 778.4 | 107.6 | 241.4 | 45.6 | 253.8 | 235.7 | 62.8 | 145.8 | 150 | 89.6
490 | 300 | 469.4 | 187.76 | 219.4806 | 242.1 | 215.8 | 244.7 | 232 | 575.5 | 31.8 | 20.6 | 60.9 | 4.5 | 247 | 6 | 736.7 | 771.2 | 842.3 | 801 | 814.4 | 663.1 | 736.7 | 828.2 | 498 | 777.1 | 107.8 | 242 | 45.7 | 254.3 | 234.9 | 63 | 146.1 | 150.6 | 89.9
491 | 301 | 470 | 188 | 219.7612 | 241.5 | 216 | 245.1 | 231.8 | 589.3 | 31.9 | 20.6 | 61.1 | 3.7 | 240.5 | 7.6 | 742.3 | 771.8 | 834.2 | 803.1 | 808.9 | 664.9 | 736 | 828.6 | 500 | 776.1 | 108.1 | 242.4 | 45.9 | 254.2 | 235.2 | 63.2 | 146.5 | 151.1 | 90.2
492 | 302 | 469.8 | 187.92 | 219.6677 | 241.3 | 216.8 | 244.2 | 231.4 | 589.5 | 31.9 | 20.6 | 61.1 | 3.6 | 253.8 | 10.8 | 747.8 | 772.6 | 833.9 | 803.5 | 810.1 | 666.6 | 733.8 | 832.5 | 501.5 | 775.2 | 108.3 | 242.9 | 46 | 253.8 | 236 | 63.5 | 146.9 | 151.7 | 90.5
493 | 303 | 469.2 | 187.68 | 219.3871 | 240.8 | 217.5 | 244.2 | 231.4 | 598.5 | 32 | 20.6 | 61.2 | 5.1 | 235.9 | 11.3 | 752.9 | 773.4 | 839.4 | 804.9 | 810.5 | 668.2 | 735.1 | 833.5 | 503.2 | 775.3 | 108.5 | 243.2 | 46.2 | 253.6 | 236.3 | 63.7 | 147.4 | 152.2 | 90.8
494 | 304 | 469.5 | 187.8 | 219.5274 | 241.4 | 218.1 | 245 | 231.1 | 608.3 | 32 | 20.6 | 61.3 | 4.9 | 231.3 | 10.7 | 757.9 | 774.7 | 842.4 | 806.3 | 810.5 | 669.7 | 738 | 833 | 505 | 774.8 | 108.8 | 243.8 | 46.3 | 254.3 | 236.2 | 63.9 | 147.8 | 152.8 | 91.1
495 | 305 | 469.2 | 187.68 | 219.3871 | 241.4 | 218.7 | 245 | 231.3 | 626.3 | 32.1 | 20.6 | 61.4 | 4.4 | 251.1 | 11.8 | 763 | 775.9 | 836.2 | 808.2 | 806.4 | 671.1 | 739 | 833.9 | 506 | 773.4 | 109 | 244.2 | 46.4 | 254.7 | 236.5 | 64.1 | 148.2 | 153.3 | 91.4
496 | 306 | 469 | 187.6 | 219.2936 | 240.5 | 219.9 | 246.2 | 232.2 | 639.7 | 32.2 | 20.6 | 61.4 | 4.7 | 254.7 | 12.7 | 768.2 | 778.1 | 829.6 | 811 | 801.8 | 672.8 | 737.5 | 835.5 | 506.8 | 773.1 | 109.2 | 244.9 | 46.6 | 254.7 | 236.9 | 64.4 | 148.5 | 154 | 91.8
497 | 307 | 468.9 | 187.56 | 219.2468 | 240.7 | 221.1 | 247.5 | 232.5 | 630.3 | 32.3 | 20.6 | 61.5 | 4.9 | 247.6 | 11.9 | 774.5 | 780 | 829.7 | 813.4 | 800.7 | 674.8 | 736.1 | 832 | 506.9 | 772.8 | 109.5 | 245.8 | 46.7 | 255.1 | 237.1 | 64.6 | 148.8 | 154.5 | 92.1
498 | 308 | 469.5 | 187.8 | 219.5274 | 241.2 | 221.1 | 248.5 | 232.8 | 619.5 | 32.4 | 20.6 | 61.5 | 4.6 | 257 | 10.9 | 779.9 | 780.1 | 839.2 | 814.6 | 807.4 | 676.7 | 736.8 | 828.7 | 506.7 | 773.5 | 109.7 | 246.4 | 46.9 | 255.8 | 237.7 | 64.8 | 149.4 | 155.1 | 92.4
499 | 309 | 469.1 | 187.64 | 219.3403 | 241.8 | 221.4 | 249.5 | 233.6 | 595.8 | 32.4 | 20.6 | 61.5 | 5 | 230.2 | 10.4 | 784.3 | 784.6 | 831.6 | 818 | 812.1 | 678.5 | 726.4 | 817.5 | 505.1 | 773.1 | 109.9 | 246.2 | 47 | 255.9 | 238.2 | 65 | 149.9 | 155.6 | 92.7
500 | 310 | 469.4 | 187.76 | 219.4806 | 242.2 | 221.2 | 249.7 | 233.9 | 572.3 | 32.4 | 20.6 | 61.5 | 4.5 | 246.6 | 10 | 789.8 | 788.1 | 832.5 | 822.5 | 815.9 | 679.9 | 726 | 814.8 | 503.7 | 774.1 | 110.2 | 246.4 | 47.2 | 256.3 | 238 | 65.3 | 150.2 | 156.1 | 93.1
501 | 311 | 469.1 | 187.64 | 219.3403 | 242.3 | 221.2 | 249.8 | 233.7 | 556.6 | 32.4 | 20.6 | 61.5 | 4.7 | 254.2 | 10.7 | 796 | 789.9 | 841.6 | 826.1 | 818.5 | 681.4 | 721.4 | 809.3 | 502.5 | 773.5 | 110.4 | 246.4 | 47.3 | 256.3 | 237.8 | 65.5 | 150.7 | 156.6 | 93.3
502 | 312 | 472.4 | 188.96 | 220.8834 | 242 | 221.4 | 248.6 | 233.7 | 545.8 | 32.5 | 20.6 | 61.5 | 4.8 | 244.5 | 11 | 802.1 | 792.2 | 839.7 | 829.6 | 821.9 | 682.6 | 717.8 | 801.4 | 501.4 | 774.8 | 110.7 | 246.4 | 47.4 | 256 | 238.3 | 65.7 | 151 | 157.1 | 93.6
503 | 313 | 473.8 | 189.52 | 221.538 | 241.4 | 222.2 | 247.2 | 233.8 | 534.4 | 32.6 | 20.6 | 61.5 | 5 | 245.2 | 10 | 808 | 793.6 | 841.2 | 832.7 | 820.9 | 683.8 | 711.1 | 792 | 500 | 775.2 | 110.9 | 246.2 | 47.6 | 255.3 | 238.6 | 65.9 | 151.5 | 157.7 | 93.9
504 | 314 | 473.6 | 189.44 | 221.4444 | 240 | 222.6 | 246.5 | 233.3 | 525.9 | 32.8 | 20.5 | 61.5 | 4.9 | 240.9 | 8.7 | 813.7 | 794.5 | 836.6 | 833.6 | 822.1 | 685.2 | 710.1 | 795.9 | 499.9 | 776.1 | 111.2 | 246 | 47.7 | 255.2 | 238.6 | 66.2 | 151.8 | 158.1 | 94.2
505 | 315 | 471.8 | 188.72 | 220.6028 | 240.1 | 222.7 | 247 | 231.9 | 522.4 | 33.1 | 20.5 | 61.7 | 5.6 | 249.7 | 8.7 | 819.9 | 794.8 | 829.8 | 835.7 | 822.2 | 686.7 | 705 | 786.5 | 499.2 | 775.5 | 111.5 | 245.8 | 47.9 | 255.4 | 239 | 66.4 | 152.1 | 158.6 | 94.4
506 | 316 | 471.2 | 188.48 | 220.3223 | 241.2 | 222.6 | 247.6 | 231.2 | 510.1 | 33.3 | 20.5 | 61.8 | 5.1 | 214.8 | 7.6 | 826.9 | 797.8 | 821.5 | 837.4 | 825.7 | 688.2 | 704.5 | 788.9 | 499 | 775.6 | 111.7 | 245.9 | 48 | 255 | 239.2 | 66.6 | 152.5 | 159.1 | 94.7
507 | 317 | 470.7 | 188.28 | 220.0885 | 242.5 | 222.4 | 247.5 | 230.8 | 514.4 | 33.4 | 20.5 | 62 | 4.9 | 247.3 | 7.4 | 834.1 | 800.7 | 824.7 | 838.8 | 818.9 | 689.8 | 702.9 | 792.9 | 499.6 | 774.8 | 112 | 245.9 | 48.2 | 254.7 | 239.3 | 66.8 | 152.7 | 159.6 | 94.9
508 | 318 | 468.6 | 187.44 | 219.1066 | 242.3 | 220.8 | 246.9 | 231 | 520.9 | 33.5 | 20.5 | 62.2 | 4.9 | 234.1 | 8.9 | 840 | 802 | 835.5 | 840.2 | 813.7 | 691.5 | 702.3 | 798.7 | 500.2 | 773.7 | 112.2 | 246.3 | 48.3 | 254.2 | 239.4 | 67.1 | 153 | 160.1 | 95.2
509 | 319 | 469.5 | 187.8 | 219.5274 | 242 | 219.6 | 247.7 | 231.5 | 536.9 | 33.6 | 20.5 | 62.3 | 4.6 | 252.9 | 10.2 | 844.9 | 800.9 | 847 | 843.1 | 811.3 | 692.8 | 708.2 | 811.4 | 501.9 | 773.6 | 112.5 | 247 | 48.5 | 254.2 | 239.8 | 67.3 | 153.4 | 160.5 | 95.4
510 | 320 | 470.3 | 188.12 | 219.9014 | 242.4 | 219.3 | 247.6 | 231.5 | 544.9 | 33.7 | 20.5 | 62.5 | 4.8 | 249.5 | 9.6 | 849.3 | 800.9 | 848 | 846.5 | 808.2 | 694.1 | 707 | 807.2 | 502.6 | 772.1 | 112.7 | 247.4 | 48.6 | 254.4 | 240.2 | 67.5 | 153.7 | 161 | 95.8
511 | 321 | 470.5 | 188.2 | 219.995 | 242.4 | 220.2 | 247.5 | 231.6 | 560.7 | 33.8 | 20.5 | 62.5 | 4.4 | 240.3 | 9.9 | 854.7 | 802.6 | 846.9 | 848.7 | 799.7 | 695.6 | 708 | 813.2 | 503.9 | 770.7 | 112.9 | 247.9 | 48.7 | 254.8 | 240.9 | 67.7 | 154.1 | 161.5 | 96.1
512 | 322 | 470.1 | 188.04 | 219.8079 | 242.5 | 220.8 | 248.9 | 231.6 | 576.4 | 33.8 | 20.5 | 62.6 | 4.1 | 220.9 | 9.5 | 860.2 | 804.7 | 854.7 | 850.2 | 795.8 | 697.2 | 707 | 823.6 | 504.7 | 770 | 113.2 | 248.3 | 48.9 | 254.5 | 241.3 | 68 | 154.7 | 162.1 | 96.3
513 | 323 | 470.7 | 188.28 | 220.0885 | 241.3 | 221.9 | 250.7 | 232.4 | 576.9 | 33.9 | 20.5 | 62.7 | 3.5 | 238.9 | 8.9 | 865 | 805.4 | 860.6 | 852.5 | 797.2 | 698.8 | 709.8 | 829.6 | 505.9 | 769.8 | 113.4 | 248.3 | 49 | 254.5 | 241.5 | 68.2 | 155 | 162.6 | 96.4
514 | 324 | 469.9 | 187.96 | 219.7144 | 240.2 | 222.7 | 250.9 | 233 | 577.5 | 34 | 20.5 | 62.7 | 3.4 | 259.4 | 8.5 | 869.6 | 806.6 | 860.7 | 855 | 793.7 | 700.2 | 710.1 | 832.9 | 506.8 | 768.4 | 113.7 | 248.8 | 49.2 | 254.6 | 241.4 | 68.4 | 155.3 | 163.2 | 96.6
515 | 325 | 469.5 | 187.8 | 219.5274 | 240.7 | 222.8 | 250.3 | 233.1 | 579.7 | 34.1 | 20.5 | 62.7 | 3 | 244.9 | 8 | 874.9 | 810.3 | 861.9 | 855.2 | 796.6 | 701.7 | 711.7 | 834.6 | 507.8 | 768.6 | 113.9 | 249.1 | 49.3 | 255.6 | 241.8 | 68.6 | 155.7 | 163.8 | 97.2
516 | 326 | 469.6 | 187.84 | 219.5741 | 241.2 | 223.5 | 251.8 | 234 | 578.9 | 34.3 | 20.5 | 62.8 | 3 | 247.1 | 8.5 | 878.9 | 809.5 | 871 | 857.5 | 797.3 | 703.1 | 713.7 | 836 | 508.8 | 768.6 | 114.2 | 249.2 | 49.4 | 255.6 | 242.6 | 68.9 | 156.1 | 164.4 | 97.2
517 | 327 | 470.2 | 188.08 | 219.8547 | 241.5 | 223.8 | 252.7 | 234.4 | 575.5 | 34.4 | 20.5 | 62.9 | 3.2 | 236.8 | 9.8 | 881.8 | 809 | 872.4 | 860.7 | 795 | 704.3 | 711.2 | 833.5 | 509.5 | 768.3 | 114.4 | 249.5 | 49.6 | 256.1 | 243 | 69.1 | 156.6 | 165 | 97.3
518 | 328 | 470.2 | 188.08 | 219.8547 | 242 | 223.4 | 252.1 | 234.2 | 575.2 | 34.4 | 20.5 | 63 | 3.1 | 248.6 | 8.7 | 884.7 | 811.6 | 871.8 | 863.2 | 794.7 | 705.6 | 708.7 | 835.5 | 510.1 | 768.4 | 114.7 | 249.6 | 49.7 | 256.5 | 243 | 69.3 | 157 | 165.6 | 97.8
519 | 329 | 467.5 | 187 | 218.5922 | 242.8 | 223.9 | 252.2 | 234.7 | 572.3 | 34.4 | 20.5 | 63.1 | 3.1 | 274.3 | 7 | 888.1 | 811.3 | 873.2 | 864.8 | 791.6 | 706.6 | 707.5 | 829.6 | 511 | 768 | 115 | 249.5 | 49.9 | 257 | 243.2 | 69.5 | 157.2 | 166.1 | 98
520 | 330 | 468.4 | 187.36 | 219.013 | 241.8 | 224.8 | 252.4 | 235.2 | 578.3 | 34.5 | 20.5 | 63.1 | 3.5 | 256.3 | 6.8 | 891.5 | 812.7 | 869.9 | 865.9 | 779.4 | 707.4 | 706.1 | 830.6 | 512 | 765.8 | 115.2 | 249.2 | 50 | 256.7 | 243.6 | 69.9 | 157.4 | 166.9 | 97.8
521 | 331 | 468.1 | 187.24 | 218.8728 | 243.2 | 225.1 | 251.5 | 235.2 | 593.4 | 34.5 | 20.5 | 63.2 | 4.1 | 256.1 | 7.2 | 896.3 | 816.7 | 863.1 | 863.1 | 775.8 | 709 | 702.4 | 831.2 | 512.9 | 763.9 | 115.5 | 249.7 | 50.2 | 256.7 | 244.1 | 70 | 158 | 167.3 | 98.8
522 | 332 | 468 | 187.2 | 218.826 | 242.6 | 224.1 | 252.1 | 235.9 | 592 | 34.6 | 20.5 | 63.3 | 3.6 | 252.1 | 9.4 | 900.4 | 818.8 | 863.4 | 863.2 | 779.5 | 710.1 | 701 | 830 | 513.1 | 764.4 | 115.8 | 250 | 50.3 | 257 | 244.2 | 70.2 | 158.5 | 167.8 | 99.2
523 | 333 | 468.5 | 187.4 | 219.0598 | 242.1 | 223.3 | 253.2 | 236.6 | 583.4 | 34.7 | 20.5 | 63.4 | 3.7 | 272.9 | 9.9 | 903.8 | 821.8 | 866.2 | 864.6 | 780.1 | 711.1 | 700.7 | 828.7 | 513 | 764.1 | 116 | 250.1 | 50.5 | 257.1 | 244.7 | 70.4 | 158.8 | 168.4 | 99.5
524 | 334 | 469.2 | 187.68 | 219.3871 | 241.2 | 223.7 | 253.6 | 237.1 | 568 | 34.8 | 20.5 | 63.5 | 4.5 | 266.6 | 10.3 | 907 | 821.4 | 873.1 | 867.5 | 783.7 | 711.9 | 699 | 826.2 | 512.3 | 763.9 | 116.3 | 250.1 | 50.6 | 256.9 | 244.8 | 70.7 | 159.2 | 168.8 | 99.8
525 | 335 | 468.7 | 187.48 | 219.1533 | 241.1 | 224.6 | 252.3 | 237.5 | 566.5 | 34.9 | 20.5 | 63.6 | 5 | 256 | 12.4 | 909.4 | 820.3 | 875.2 | 870.7 | 784.7 | 712.8 | 698.8 | 825.6 | 512.2 | 764.1 | 116.5 | 250.3 | 50.7 | 257.2 | 245.1 | 70.9 | 159.5 | 169.4 | 100
526 | 336 | 468.9 | 187.56 | 219.2468 | 241.2 | 225.1 | 251.2 | 237.2 | 573.1 | 35 | 20.5 | 63.8 | 4.8 | 259.7 | 12.7 | 911.9 | 820.6 | 877 | 872.6 | 785.3 | 713.9 | 697.7 | 824.1 | 512.4 | 763.2 | 116.8 | 250.7 | 50.9 | 257 | 245.7 | 71.1 | 160 | 169.9 | 100.4
527 | 337 | 468.1 | 187.24 | 218.8728 | 239.9 | 225.6 | 251.4 | 237.3 | 574.5 | 35 | 20.5 | 63.9 | 4.9 | 259.1 | 12.4 | 913.7 | 819.8 | 874.9 | 873.7 | 790.8 | 714.9 | 697.3 | 825.4 | 512.7 | 762.3 | 117.1 | 251 | 51 | 256.5 | 246.4 | 71.3 | 160.5 | 170.5 | 100.4
528 | 338 | 469.8 | 187.92 | 219.6677 | 240.4 | 225.5 | 250.8 | 237.9 | 566.1 | 35.1 | 20.5 | 64 | 4.3 | 251.8 | 12.1 | 916.2 | 820.4 | 871.5 | 874.8 | 800.9 | 715.3 | 692 | 815.1 | 511.2 | 761.2 | 117.3 | 251.1 | 51.2 | 256.1 | 246.7 | 71.5 | 160.8 | 171 | 100.8
529 | 339 | 469.3 | 187.72 | 219.4339 | 240.6 | 225.5 | 250.3 | 238.1 | 553.1 | 35.2 | 20.5 | 64 | 3.8 | 257.3 | 12.1 | 919.4 | 822.9 | 869 | 873.2 | 797.1 | 716.1 | 692.2 | 814.3 | 510.9 | 761.1 | 117.6 | 251.1 | 51.3 | 255.9 | 246.5 | 71.8 | 161.1 | 171.5 | 101
530 | 340 | 468.2 | 187.28 | 218.9195 | 240.6 | 224.9 | 249.3 | 237.8 | 549.3 | 35.2 | 20.5 | 64 | 4.1 | 251.7 | 11.1 | 922.4 | 825.4 | 873 | 871.5 | 787.7 | 717.3 | 690.9 | 814.1 | 510.9 | 759.2 | 117.8 | 251 | 51.5 | 255.7 | 246.3 | 72 | 161.4 | 171.9 | 101.4
531 | 341 | 469 | 187.6 | 219.2936 | 239.9 | 224.8 | 249.9 | 237.4 | 551.1 | 35.2 | 20.5 | 64 | 3.9 | 270.5 | 8.8 | 924.4 | 828.5 | 873.3 | 872.1 | 791.1 | 718.2 | 687.9 | 808.5 | 510.2 | 759.1 | 118.1 | 251 | 51.6 | 256.2 | 246.4 | 72.2 | 161.7 | 172.4 | 101.7
532 | 342 | 470.3 | 188.12 | 219.9014 | 240.4 | 225 | 249.7 | 237.1 | 542.9 | 35.1 | 20.5 | 64.1 | 3.9 | 266.3 | 10 | 927.2 | 831.3 | 876.3 | 871.5 | 791.1 | 719 | 682.6 | 807.5 | 509.4 | 757.9 | 118.3 | 251.4 | 51.8 | 256.9 | 246.3 | 72.4 | 161.9 | 172.9 | 102.1
533 | 343 | 469.6 | 187.84 | 219.5741 | 240.2 | 224.2 | 249.5 | 237.2 | 541.4 | 35.1 | 20.5 | 64.1 | 4.3 | 270.7 | 11.7 | 929.3 | 832.9 | 879 | 874.3 | 790.4 | 719.6 | 679.6 | 808.7 | 509.4 | 757.1 | 118.6 | 251.8 | 51.9 | 257.3 | 246 | 72.7 | 162.1 | 173.5 | 102.3
534 | 344 | 469.8 | 187.92 | 219.6677 | 238.6 | 224 | 249.2 | 237.5 | 542.1 | 35.2 | 20.5 | 64.3 | 3.5 | 263 | 12.2 | 930.9 | 832.1 | 882.7 | 878 | 795.5 | 720.3 | 679.4 | 815.8 | 509.3 | 757.8 | 118.8 | 252 | 52 | 257.1 | 246 | 72.9 | 162.5 | 174 | 102.3
535 | 345 | 469.6 | 187.84 | 219.5741 | 238 | 223.9 | 248.5 | 237.1 | 532.6 | 35.2 | 20.5 | 64.4 | 3.6 | 275.5 | 11.3 | 932.4 | 832.5 | 883.5 | 879.3 | 800.1 | 721.1 | 679.8 | 813.6 | 508.9 | 757.8 | 119 | 251.7 | 52.2 | 256.6 | 245.7 | 73.1 | 162.7 | 174.4 | 102.7
536 | 346 | 470.3 | 188.12 | 219.9014 | 236.7 | 224.7 | 249.2 | 237 | 539.7 | 35.3 | 20.5 | 64.5 | 4.3 | 282.2 | 11.4 | 933.7 | 834 | 882.3 | 878.2 | 798.5 | 721.9 | 681.4 | 812.3 | 509.5 | 756.7 | 119.3 | 252.3 | 52.3 | 256.2 | 245.8 | 73.3 | 163 | 174.9 | 102.8
537 | 347 | 469.9 | 187.96 | 219.7144 | 236.5 | 225.1 | 248.3 | 237.1 | 555.4 | 35.4 | 20.5 | 64.6 | 4.6 | 279.9 | 12.7 | 935.6 | 834.5 | 884 | 877.3 | 790.1 | 722.4 | 679.5 | 809.6 | 509.6 | 755.4 | 119.5 | 252.6 | 52.5 | 256.3 | 245.7 | 73.5 | 163.3 | 175.4 | 103
538 | 348 | 469.3 | 187.72 | 219.4339 | 237.3 | 225.4 | 247.8 | 237.3 | 557.2 | 35.4 | 20.5 | 64.7 | 4.3 | 278 | 14.2 | 938.4 | 836.4 | 884.6 | 876.4 | 787.7 | 723.2 | 675.2 | 806.6 | 509.5 | 754.7 | 119.7 | 252.7 | 52.6 | 256.2 | 245.7 | 73.7 | 163.7 | 175.9 | 103.4
539 | 349 | 468.3 | 187.32 | 218.9663 | 238.2 | 226.4 | 248.9 | 237.7 | 564.7 | 35.5 | 20.5 | 64.7 | 4.1 | 289.2 | 14.2 | 940.8 | 837.9 | 879.8 | 870.7 | 779 | 724.2 | 673.8 | 807.3 | 510 | 753 | 119.9 | 252.6 | 52.8 | 256.6 | 245.9 | 73.9 | 163.9 | 176.4 | 103.8
540 | 350 | 468.5 | 187.4 | 219.0598 | 239 | 227.7 | 249.4 | 238.3 | 582.2 | 35.5 | 20.5 | 64.8 | 4.2 | 280.9 | 13.2 | 942.2 | 837.3 | 878.2 | 868.7 | 775.1 | 725.1 | 673.9 | 804.7 | 510.9 | 751.3 | 120.2 | 253.1 | 52.9 | 257.4 | 245.7 | 74.1 | 164.3 | 176.9 | 104.3
541 | 351 | 468.8 | 187.52 | 219.2001 | 239.2 | 229.4 | 251.9 | 239.2 | 591.9 | 35.6 | 20.5 | 64.9 | 4.4 | 280.3 | 12.8 | 943.1 | 837.3 | 877.6 | 869.9 | 771.6 | 725.6 | 672.9 | 803.7 | 511.4 | 750.2 | 120.4 | 254.1 | 53.1 | 258.8 | 245.3 | 74.4 | 164.5 | 177.5 | 104.2
542 | 352 | 468.8 | 187.52 | 219.2001 | 239.8 | 230.1 | 252.2 | 239.7 | 598.8 | 35.7 | 20.4 | 65 | 4.5 | 270.4 | 14.3 | 943.7 | 838.2 | 878.7 | 871 | 770.1 | 726.2 | 670.7 | 805.3 | 511.8 | 748.9 | 120.6 | 254.7 | 53.2 | 259.8 | 245.8 | 74.6 | 164.9 | 178 | 104.6
543 | 353 | 468.8 | 187.52 | 219.2001 | 241.4 | 230.4 | 252.5 | 239.6 | 599.2 | 35.7 | 20.4 | 65.1 | 4.2 | 274.2 | 14.3 | 944.6 | 840.8 | 880 | 871.1 | 771.6 | 726.7 | 669.1 | 804.9 | 511.5 | 747.9 | 120.8 | 255.3 | 53.4 | 260 | 245.8 | 74.8 | 165.3 | 178.5 | 105.7
544 | 354 | 468 | 187.2 | 218.826 | 241.9 | 231.4 | 253.9 | 239.9 | 593 | 35.8 | 20.4 | 65.3 | 3.9 | 274.7 | 15.3 | 945.7 | 841.8 | 877.5 | 870.9 | 772.7 | 727.2 | 668.8 | 804.1 | 511.2 | 747.1 | 121 | 255.7 | 53.5 | 260.3 | 245.5 | 75 | 165.7 | 179.1 | 106.2
545 | 355 | 468.8 | 187.52 | 219.2001 | 242 | 232.3 | 254.7 | 240.2 | 586.8 | 35.9 | 20.4 | 65.3 | 4.3 | 276.1 | 14.9 | 946.5 | 843.1 | 878.9 | 872.3 | 773.5 | 727.4 | 667.5 | 805.3 | 511.1 | 746.2 | 121.2 | 255.9 | 53.6 | 260.4 | 245 | 75.2 | 166 | 179.6 | 106.5
546 | 356 | 468.9 | 187.56 | 219.2468 | 242.3 | 232 | 254.8 | 240.2 | 570.8 | 35.9 | 20.4 | 65.4 | 4.4 | 277.6 | 14.7 | 946.6 | 843.8 | 876.8 | 873.9 | 776.8 | 727.5 | 668.8 | 806.6 | 511 | 746.7 | 121.4 | 255.9 | 53.8 | 260.3 | 245.1 | 75.4 | 166.5 | 180.1 | 106.8
547 | 357 | 469 | 187.6 | 219.2936 | 242.7 | 232 | 255.1 | 240.4 | 569.9 | 36 | 20.4 | 65.4 | 4.1 | 276.3 | 14.8 | 946.9 | 844 | 878.1 | 876.2 | 775 | 727.6 | 668.4 | 808.3 | 511.5 | 745.4 | 121.7 | 255.9 | 53.9 | 260.1 | 245.3 | 75.6 | 166.9 | 180.6 | 107
548 | 358 | 469 | 187.6 | 219.2936 | 243.1 | 231.9 | 255.7 | 240.5 | 568.4 | 36.1 | 20.4 | 65.4 | 3.8 | 277.1 | 14.4 | 947.3 | 842.5 | 884.1 | 877.2 | 773.7 | 727.8 | 665.9 | 809 | 511 | 744 | 121.9 | 255.8 | 54.1 | 259.8 | 245 | 75.8 | 167.3 | 181 | 107.3
549 | 359 | 470 | 188 | 219.7612 | 243.2 | 231.1 | 256 | 240.3 | 562 | 36.1 | 20.4 | 65.5 | 4.2 | 277.7 | 13.8 | 948.1 | 842.4 | 883.9 | 877 | 775.9 | 728.4 | 662.5 | 806.2 | 511 | 742.8 | 122.1 | 255.4 | 54.2 | 259.7 | 244.7 | 76.1 | 167.5 | 181.4 | 107.5
550 | 360 | 470.7 | 188.28 | 220.0885 | 243.3 | 231.5 | 255.7 | 240.1 | 563.4 | 36.2 | 20.4 | 65.6 | 4.1 | 275.1 | 13.3 | 948.9 | 843.9 | 879.2 | 874.5 | 773.5 | 729.1 | 660.9 | 805.1 | 511.5 | 741.3 | 122.3 | 255.3 | 54.4 | 259.5 | 244.2 | 76.3 | 167.8 | 181.9 | 107.9
551 | 361 | 470.6 | 188.24 | 220.0417 | 243.6 | 231.6 | 256.4 | 240.3 | 573.3 | 36.3 | 20.4 | 65.7 | 4.4 | 273.6 | 13.4 | 949.2 | 843.8 | 880.6 | 877.3 | 772.4 | 729.9 | 661.1 | 804 | 511.8 | 739.7 | 122.5 | 255.5 | 54.5 | 259.6 | 243.6 | 76.5 | 168.1 | 182.4 | 108.2
552 | 362 | 469.4 | 187.76 | 219.4806 | 243.7 | 232 | 257.3 | 240.1 | 577.5 | 36.4 | 20.4 | 65.8 | 4 | 279.5 | 12.8 | 948.6 | 839.5 | 883.4 | 883.3 | 772.5 | 730.1 | 661 | 805.8 | 511.9 | 738.6 | 122.7 | 255.9 | 54.7 | 259.9 | 243.5 | 76.7 | 168.4 | 182.8 | 108.4
553 | 363 | 469 | 187.6 | 219.2936 | 243.8 | 232.7 | 257.3 | 240.5 | 578.9 | 36.5 | 20.4 | 65.9 | 3.9 | 293.6 | 12.8 | 948.1 | 840.1 | 880.5 | 883.4 | 772.1 | 730.6 | 658.7 | 803.1 | 512 | 737.4 | 123 | 256.3 | 54.8 | 260.4 | 243.7 | 76.9 | 168.7 | 183.3 | 108.8
554 | 364 | 469.6 | 187.84 | 219.5741 | 244.1 | 232.8 | 257.4 | 241.2 | 582.1 | 36.5 | 20.4 | 65.9 | 4.3 | 296.8 | 13.7 | 948.5 | 841.9 | 878.3 | 879.5 | 771.6 | 731.3 | 655.4 | 798.2 | 512.3 | 736 | 123.2 | 256.5 | 54.9 | 260.8 | 244.1 | 77.2 | 169 | 183.9 | 109
555 | 365 | 473.2 | 189.28 | 221.2574 | 244.3 | 232.5 | 256.6 | 241.9 | 572.5 | 36.6 | 20.4 | 66 | 4.3 | 283.6 | 13.9 | 948.7 | 843 | 879.5 | 880 | 773.7 | 731.9 | 654.3 | 791 | 512.1 | 735.8 | 123.4 | 256.6 | 55.1 | 261 | 244.4 | 77.4 | 169.3 | 184.4 | 109.3
556 | 366 | 474 | 189.6 | 221.6315 | 245 | 232.6 | 256.9 | 242.4 | 566.1 | 36.6 | 20.4 | 66 | 3.9 | 284 | 12.8 | 949 | 843.2 | 880.3 | 885.2 | 781.3 | 731.8 | 654.9 | 790 | 511.8 | 736.1 | 123.6 | 256.8 | 55.2 | 260.8 | 244.8 | 77.6 | 169.6 | 184.9 | 109.6
557 | 367 | 484.4 | 193.76 | 226.4943 | 244.6 | 232.6 | 257.5 | 242.4 | 559.6 | 36.6 | 20.4 | 66.1 | 3.8 | 283.1 | 12.3 | 948.2 | 840.2 | 883.9 | 893.6 | 791.7 | 731 | 658.8 | 793.9 | 511.8 | 738.7 | 123.8 | 257 | 55.4 | 260.5 | 245.2 | 77.8 | 170 | 185.3 | 109.9
558 | 368 | 516.1 | 206.44 | 241.3165 | 243.5 | 232.6 | 257.5 | 242.4 | 550.6 | 36.7 | 20.4 | 66.1 | 3.6 | 278.3 | 12.6 | 947.2 | 839 | 886.9 | 897.9 | 795.7 | 730.7 | 662.7 | 802.3 | 512.4 | 740 | 124 | 257 | 55.5 | 260.4 | 245.2 | 78 | 170.3 | 185.8 | 110.2
559 | 369 | 536.2 | 214.48 | 250.7148 | 242.7 | 233.1 | 256.9 | 242.4 | 555.7 | 36.7 | 20.4 | 66.2 | 3.8 | 279.9 | 12.7 | 946.6 | 836.9 | 890.1 | 901 | 793.4 | 730.6 | 663.3 | 808.8 | 513.2 | 739.2 | 124.3 | 256.9 | 55.7 | 260 | 245 | 78.2 | 170.6 | 186.3 | 110.5
560 | 370 | 542.7 | 217.08 | 253.754 | 242 | 233 | 256.8 | 242 | 575.7 | 36.8 | 20.4 | 66.2 | 3.4 | 279.2 | 11.7 | 946 | 836.1 | 887.8 | 898.5 | 790.3 | 730.5 | 664.6 | 810.6 | 514.2 | 737.4 | 124.5 | 257.1 | 55.8 | 259.8 | 245.1 | 78.5 | 171 | 186.8 | 110.8
561 | 371 | 544.6 | 217.84 | 254.6424 | 241.7 | 233.2 | 256.8 | 241.6 | 607.7 | 36.8 | 20.4 | 66.3 | 3.6 | 284.5 | 10.6 | 945.6 | 837.5 | 881.7 | 896.3 | 789.6 | 730.8 | 663.6 | 811.2 | 515.6 | 736.8 | 124.7 | 257.6 | 56 | 259.4 | 244.9 | 78.7 | 171.3 | 187.3 | 111.1
562 | 372 | 545.9 | 218.36 | 255.2503 | 242.1 | 233.4 | 255.8 | 241.1 | 630.5 | 36.8 | 20.4 | 66.4 | 3.5 | 278 | 9.6 | 945.4 | 840.3 | 877.4 | 890.8 | 780.5 | 731.3 | 661.1 | 808.3 | 516.4 | 734.6 | 124.9 | 258 | 56.1 | 259.3 | 244.8 | 78.9 | 171.6 | 187.9 | 111.4
563 | 373 | 547.2 | 218.88 | 255.8581 | 243 | 233.6 | 256.3 | 241 | 645.7 | 36.9 | 20.4 | 66.5 | 3.4 | 274.8 | 8.5 | 945.9 | 844.4 | 871.7 | 882.4 | 775 | 732.1 | 659.8 | 804.5 | 517.1 | 733.2 | 125.1 | 258.5 | 56.3 | 260.1 | 245.1 | 79.1 | 171.9 | 188.5 | 111.7
564 | 374 | 546.8 | 218.72 | 255.6711 | 244 | 233.3 | 257.7 | 241.5 | 650.8 | 37 | 20.4 | 66.6 | 3.2 | 276.2 | 8.4 | 946.9 | 848.8 | 864.4 | 872.3 | 763 | 733.1 | 658.6 | 798.9 | 517.6 | 732.2 | 125.3 | 259.4 | 56.4 | 261.3 | 245.1 | 79.4 | 172.1 | 189.1 | 112
565 | 375 | 546.7 | 218.68 | 255.6243 | 245.9 | 233.7 | 259.9 | 242.4 | 658.1 | 37.1 | 20.4 | 66.7 | 3.4 | 274.8 | 8.3 | 947.6 | 851.5 | 862.7 | 867.1 | 754.8 | 734.2 | 660.2 | 792.4 | 518.4 | 730.7 | 125.6 | 260.6 | 56.6 | 263.4 | 245 | 79.6 | 172.7 | 189.7 | 112.3
566 | 376 | 548.2 | 219.28 | 256.3257 | 247.5 | 233.8 | 262 | 243.6 | 665.8 | 37.1 | 20.4 | 66.7 | 3.6 | 280.3 | 8.3 | 947.5 | 850.4 | 870.2 | 877.1 | 755.9 | 735.3 | 664.4 | 792.7 | 519.4 | 730.2 | 125.8 | 261.8 | 56.7 | 265.3 | 245.1 | 79.8 | 173 | 190.3 | 112.6
567 | 377 | 548 | 219.2 | 256.2322 | 248.3 | 234.2 | 264.4 | 244.1 | 657.1 | 37.2 | 20.4 | 66.8 | 3.5 | 285.3 | 8.6 | 946.5 | 848.2 | 875 | 884.8 | 762.6 | 735.7 | 665.8 | 805.3 | 520.5 | 730.4 | 126 | 263.1 | 56.9 | 266.2 | 245 | 80 | 173.3 | 190.9 | 113
568 | 378 | 548.6 | 219.44 | 256.5127 | 249.1 | 235.2 | 265.7 | 245 | 656.1 | 37.2 | 20.4 | 66.8 | 3.6 | 276.2 | 8.6 | 945.8 | 846 | 877.5 | 889.8 | 764.2 | 736.2 | 669.8 | 808.7 | 522.5 | 729.7 | 126.3 | 263.9 | 57 | 267.7 | 245.4 | 80.3 | 173.7 | 191.4 | 113.3
569 | 379 | 549.6 | 219.84 | 256.9803 | 249.5 | 236.1 | 266.9 | 245.6 | 658.9 | 37.2 | 20.4 | 66.9 | 3.9 | 271.7 | 8.4 | 945.5 | 845.9 | 880 | 896.1 | 769.5 | 736.8 | 670.9 | 815.2 | 525.1 | 730.1 | 126.5 | 264.6 | 57.2 | 268.8 | 246.2 | 80.5 | 174.1 | 192 | 113.6
570 | 380 | 549.8 | 219.92 | 257.0738 | 250 | 236.5 | 267.4 | 246.1 | 646.2 | 37.3 | 20.4 | 67 | 4.1 | 277 | 7.9 | 945.4 | 846.7 | 880.3 | 898 | 777.9 | 737.2 | 667.4 | 809.9 | 527 | 730.2 | 126.8 | 265.4 | 57.3 | 269.2 | 247.2 | 80.7 | 174.6 | 192.6 | 114
571 | 381 | 551.6 | 220.64 | 257.9154 | 251 | 236.9 | 267.4 | 246.9 | 633.3 | 37.3 | 20.4 | 67.1 | 4.4 | 282 | 7.4 | 944.5 | 847.4 | 876.6 | 898.4 | 784.3 | 737.3 | 671.7 | 813.5 | 529.2 | 732 | 127 | 266.2 | 57.5 | 268.7 | 247.6 | 80.9 | 175 | 193.2 | 114.3
572 | 382 | 552.2 | 220.88 | 258.196 | 251.8 | 239.1 | 265.9 | 247.6 | 615.4 | 37.4 | 20.4 | 67.1 | 4.8 | 281.6 | 6.9 | 943.9 | 849.7 | 880.2 | 903.2 | 792 | 737.7 | 673.5 | 817.8 | 531.9 | 735.5 | 127.3 | 266.5 | 57.6 | 268.7 | 248.3 | 81.2 | 175.3 | 193.7 | 114.6
573 | 383 | 552.3 | 220.92 | 258.2428 | 251.4 | 241.4 | 265.2 | 248.3 | 604.1 | 37.4 | 20.4 | 67.2 | 4.1 | 286.6 | 6.7 | 943.8 | 852 | 879.8 | 903.9 | 794.7 | 738.2 | 673.5 | 821.5 | 535.7 | 734.7 | 127.5 | 266.8 | 57.8 | 269.5 | 249 | 81.4 | 175.8 | 194.2 | 114.9
574 | 384 | 553.4 | 221.36 | 258.7571 | 250.8 | 242.3 | 265.8 | 248.8 | 594.9 | 37.4 | 20.4 | 67.2 | 3.9 | 294.9 | 6.3 | 943.8 | 852.2 | 880.8 | 904.9 | 800.3 | 738.5 | 674.4 | 818.9 | 540.4 | 736.8 | 127.8 | 266.8 | 57.9 | 270 | 249.4 | 81.6 | 176.2 | 194.7 | 115.3
575 | 385 | 554.4 | 221.76 | 259.2247 | 250.4 | 242.5 | 266.6 | 249.1 | 595.6 | 37.5 | 20.4 | 67.2 | 3.8 | 281.9 | 6.1 | 943.4 | 853.2 | 879.6 | 903.4 | 804.3 | 739 | 679.2 | 823.4 | 545.2 | 738.4 | 128 | 266.8 | 58.1 | 270.1 | 250 | 81.9 | 176.5 | 195.2 | 115.6
576 | 386 | 553.7 | 221.48 | 258.8974 | 250.3 | 242.9 | 266.9 | 249.2 | 601.8 | 37.6 | 20.4 | 67.2 | 3.9 | 267.4 | 5.9 | 943 | 854.6 | 882.2 | 902.9 | 806.8 | 739 | 680.1 | 820.9 | 549.9 | 739.4 | 128.3 | 267.1 | 58.2 | 270.4 | 250.6 | 82.1 | 176.9 | 195.8 | 115.9
577 | 387 | 555.3 | 222.12 | 259.6455 | 250.5 | 243.9 | 266.9 | 249.3 | 608 | 37.6 | 20.4 | 67.3 | 3.6 | 275.8 | 6 | 942.9 | 853.9 | 887.3 | 904.3 | 812.1 | 739.3 | 683.6 | 820.9 | 555.2 | 741.2 | 128.5 | 267.2 | 58.4 | 270.3 | 250.8 | 82.3 | 177.2 | 196.3 | 116.2
578 | 388 | 556.9 | 222.76 | 260.3936 | 250.6 | 244.1 | 267 | 249.8 | 620.8 | 37.7 | 20.4 | 67.3 | 3.7 | 257.4 | 6.4 | 943.3 | 853.7 | 887.2 | 905.6 | 811.8 | 739.5 | 683.1 | 822 | 559.9 | 739.6 | 128.8 | 267.3 | 58.5 | 270.9 | 251.1 | 82.5 | 177.6 | 196.9 | 116.5
579 | 389 | 555.6 | 222.24 | 259.7858 | 251.8 | 244.7 | 266.2 | 250.2 | 625 | 37.8 | 20.4 | 67.4 | 4.1 | 261.8 | 7.3 | 944.4 | 854.1 | 888.7 | 905.8 | 809.5 | 739.9 | 682.6 | 816.7 | 564.7 | 739.9 | 129 | 267.7 | 58.7 | 271.2 | 251.5 | 82.8 | 177.9 | 197.5 | 116.8
580 | 390 | 555.6 | 222.24 | 259.7858 | 252.7 | 245.3 | 266.8 | 250.5 | 621 | 37.8 | 20.4 | 67.4 | 3.9 | 276.9 | 7.6 | 943.8 | 850.8 | 890.4 | 911.2 | 810.2 | 739.9 | 687.9 | 822.4 | 569.4 | 740.8 | 129.3 | 268 | 58.8 | 271.4 | 252 | 83 | 178.2 | 198 | 117.2
581 | 391 | 556.3 | 222.52 | 260.1131 | 252.9 | 246.1 | 267.2 | 250.9 | 613.3 | 37.8 | 20.4 | 67.5 | 3.9 | 263.5 | 7.2 | 942.5 | 849.1 | 890.3 | 912.1 | 815.2 | 739.5 | 689.1 | 823.8 | 573.8 | 741.7 | 129.6 | 268 | 59 | 271.7 | 252.2 | 83.2 | 178.5 | 198.5 | 117.5
582 | 392 | 558.5 | 223.4 | 261.1417 | 253.2 | 245.9 | 267.5 | 251 | 618.8 | 37.9 | 20.4 | 67.6 | 3.8 | 243.9 | 6.8 | 941.6 | 847.8 | 890.9 | 914.5 | 821 | 739.5 | 693 | 828.9 | 579.4 | 742.8 | 129.8 | 268.2 | 59.1 | 271.6 | 252.6 | 83.5 | 179 | 199 | 117.8
583 | 393 | 559.5 | 223.8 | 261.6093 | 253.4 | 246.8 | 267.9 | 250.8 | 627.6 | 37.9 | 20.4 | 67.7 | 3.4 | 257.4 | 6.9 | 941 | 847.1 | 889.7 | 914.3 | 823.4 | 739.4 | 692.7 | 831.2 | 585.1 | 744.2 | 130.1 | 268.2 | 59.3 | 271.4 | 253.3 | 83.7 | 179.3 | 199.6 | 118.1
584 | 394 | 560.3 | 224.12 | 261.9834 | 253.5 | 248 | 268.4 | 250.6 | 630.3 | 38 | 20.4 | 67.8 | 3.3 | 250.6 | 7.3 | 941.6 | 848.7 | 887.9 | 915.6 | 824 | 739.4 | 692.5 | 827.8 | 590.8 | 743.4 | 130.4 | 268 | 59.5 | 271.2 | 253.4 | 83.9 | 179.7 | 200.2 | 118.4
585 | 395 | 559.9 | 223.96 | 261.7963 | 253.7 | 248.7 | 269 | 251.1 | 628.8 | 38 | 20.3 | 67.8 | 3.3 | 251.5 | 7.2 | 942.1 | 848.3 | 889.4 | 916.4 | 825.2 | 739.6 | 694.3 | 833.2 | 596.6 | 745.3 | 130.6 | 268.2 | 59.6 | 271.1 | 253.6 | 84.1 | 180 | 200.7 | 118.7
586 | 396 | 560.3 | 224.12 | 261.9834 | 253.7 | 249.2 | 269.2 | 250.9 | 626.1 | 38 | 20.3 | 67.9 | 3.4 | 249.1 | 7 | 942 | 848.3 | 892.3 | 915.1 | 825.5 | 739.8 | 694.9 | 834.9 | 601.3 | 746.9 | 130.9 | 268.6 | 59.7 | 271.1 | 253.5 | 84.4 | 180.4 | 201.3 | 118.9
587 | 397 | 561.5 | 224.6 | 262.5445 | 253 | 249.4 | 269.3 | 250.2 | 613.2 | 38.1 | 20.3 | 67.9 | 3 | 246.1 | 6.7 | 941.5 | 846 | 892.8 | 918.6 | 829.9 | 739.7 | 698.4 | 839.2 | 605.7 | 749 | 131.2 | 269 | 59.9 | 270.6 | 253.6 | 84.6 | 180.7 | 201.8 | 119.3
588 | 398 | 562.3 | 224.92 | 262.9185 | 252.6 | 248.8 | 268 | 249.9 | 615.1 | 38.2 | 20.3 | 68 | 3.4 | 250.5 | 6.5 | 941.1 | 844.6 | 892.5 | 922 | 832.1 | 740.2 | 701.3 | 843.1 | 610.5 | 749.7 | 131.4 | 269.5 | 60.1 | 270.5 | 253.7 | 84.8 | 180.9 | 202.3 | 119.5
589 | 399 | 562 | 224.8 | 262.7782 | 252.8 | 248.9 | 267.8 | 250.1 | 624 | 38.3 | 20.3 | 68.1 | 3.3 | 240.5 | 6.6 | 940.6 | 845.7 | 888.8 | 922.1 | 832.2 | 740.9 | 701.1 | 840.4 | 615.2 | 748.4 | 131.7 | 269.8 | 60.2 | 270.4 | 253.7 | 85.1 | 181.2 | 202.9 | 119.8
590 | 400 | 563.8 | 225.52 | 263.6199 | 253.3 | 249.2 | 268.5 | 249.8 | 624.6 | 38.4 | 20.3 | 68.2 | 3.4 | 238.5 | 6.6 | 940.5 | 850.1 | 888.9 | 912.7 | 820 | 742 | 694 | 828.4 | 619.5 | 746.8 | 131.9 | 269.8 | 60.4 | 270.9 | 253.3 | 85.3 | 181.5 | 203.5 | 120.1
591 | 401 | 562.6 | 225.04 | 263.0588 | 254.4 | 249.6 | 269.3 | 250.2 | 633.6 | 38.4 | 20.3 | 68.3 | 3.5 | 242.9 | 6.5 | 941.4 | 851.8 | 885.3 | 903.9 | 811.1 | 743 | 691.5 | 826.3 | 624.5 | 745.3 | 132.2 | 270.2 | 60.5 | 271.3 | 253.4 | 85.5 | 181.8 | 204.1 | 120.5
592 | 402 | 564.6 | 225.84 | 263.9939 | 255.4 | 250.4 | 269.2 | 251.1 | 643.5 | 38.5 | 20.3 | 68.4 | 3.4 | 244.3 | 6.2 | 943.2 | 856.3 | 882.6 | 892 | 799.7 | 744.1 | 690.3 | 814 | 629.6 | 742.7 | 132.4 | 270.8 | 60.7 | 271.6 | 253.3 | 85.8 | 182.1 | 204.7 | 120.8
593 | 403 | 564.6 | 225.84 | 263.9939 | 256.9 | 251.2 | 269.4 | 251.6 | 659.8 | 38.5 | 20.3 | 68.6 | 3.5 | 244.2 | 5.8 | 944.1 | 855.1 | 883.9 | 896.2 | 795.7 | 745.2 | 690.4 | 812.7 | 635.7 | 741.1 | 132.7 | 271.6 | 60.8 | 272 | 253.6 | 86 | 182.4 | 205.4 | 121.1
594 | 404 | 565.5 | 226.2 | 264.4148 | 258.5 | 251.3 | 270.8 | 252.7 | 670.8 | 38.6 | 20.3 | 68.7 | 3.5 | 244.3 | 5.6 | 945 | 855.2 | 880.1 | 890.2 | 787 | 746.1 | 691.3 | 810.9 | 641.9 | 739.5 | 132.9 | 272.4 | 61 | 272.8 | 254.2 | 86.2 | 182.8 | 206 | 121.5
595 | 405 | 566 | 226.4 | 264.6486 | 260.3 | 252 | 271.7 | 254.1 | 676.8 | 38.6 | 20.3 | 68.8 | 3.5 | 246.5 | 5.3 | 945.4 | 855.3 | 880.2 | 885.5 | 782 | 746.6 | 688.8 | 808.9 | 646.6 | 737 | 133.2 | 273.2 | 61.1 | 274.8 | 254.8 | 86.5 | 183.3 | 206.7 | 121.8
596 | 406 | 566.5 | 226.6 | 264.8823 | 261.7 | 252.7 | 273.5 | 255.7 | 667.7 | 38.7 | 20.3 | 69 | 3.4 | 245.2 | 4.9 | 945.2 | 851.2 | 884.5 | 897.4 | 783.4 | 746.8 | 683.8 | 803.6 | 650.3 | 736 | 133.4 | 273.9 | 61.3 | 276.5 | 255.6 | 86.7 | 183.6 | 207.4 | 122.1
597 | 407 | 566.9 | 226.76 | 265.0694 | 262.9 | 253.5 | 274.7 | 257.1 | 654.8 | 38.8 | 20.3 | 69.2 | 3.3 | 244.3 | 4.5 | 945.6 | 851.9 | 884.7 | 898.9 | 787.9 | 746.7 | 680.9 | 804.7 | 654.2 | 736 | 133.7 | 274.9 | 61.4 | 278.2 | 255.8 | 86.9 | 184 | 208 | 122.6
598 | 408 | 566.8 | 226.72 | 265.0226 | 264.1 | 254 | 275.6 | 258.6 | 653.6 | 38.8 | 20.3 | 69.3 | 3.5 | 246 | 4.4 | 946.2 | 851.3 | 886.8 | 899.4 | 787 | 746.8 | 678.6 | 802.8 | 658.2 | 735.1 | 133.9 | 275.7 | 61.6 | 280.2 | 256.5 | 87.2 | 184.6 | 208.6 | 122.9
599 | 409 | 566.7 | 226.68 | 264.9759 | 264.6 | 254.7 | 277 | 259.6 | 656.9 | 38.8 | 20.3 | 69.5 | 3.7 | 249.4 | 4.6 | 946.7 | 850.8 | 885.9 | 899.5 | 785.5 | 747 | 676.6 | 798.8 | 662.1 | 733.5 | 134.2 | 276.9 | 61.8 | 281.1 | 257.8 | 87.4 | 185.4 | 209.2 | 123.3
600 | 410 | 566 | 226.4 | 264.6486 | 265.2 | 255.3 | 278.8 | 259.8 | 660.7 | 38.8 | 20.3 | 69.5 | 3.5 | 249.8 | 4.7 | 947.3 | 851.7 | 887 | 900.1 | 791.1 | 747.1 | 676.5 | 797.7 | 666.3 | 733.6 | 134.5 | 277.8 | 61.9 | 281.8 | 258.2 | 87.6 | 185.8 | 209.8 | 123.7
601 | 411 | 565.3 | 226.12 | 264.3213 | 265.9 | 256 | 280.3 | 260.7 | 653.9 | 38.9 | 20.3 | 69.6 | 3.4 | 248.3 | 4.2 | 947.9 | 852.1 | 887.7 | 901.9 | 798.4 | 747.2 | 677.2 | 802.7 | 670.4 | 733.5 | 134.7 | 278.4 | 62.1 | 281.9 | 259 | 87.9 | 186.2 | 210.3 | 124
602 | 412 | 565.5 | 226.2 | 264.4148 | 266.1 | 255.8 | 280.4 | 261.4 | 635.7 | 38.9 | 20.3 | 69.7 | 3.1 | 248.3 | 3.8 | 948.3 | 853.3 | 887.2 | 902.7 | 807.6 | 747 | 680.4 | 806.7 | 673.6 | 735.6 | 135 | 278.6 | 62.2 | 282.5 | 259.5 | 88.1 | 186.7 | 210.9 | 124.4
603 | 413 | 565.3 | 226.12 | 264.3213 | 265.7 | 255.7 | 280.3 | 261.8 | 612.8 | 38.9 | 20.3 | 69.8 | 3.2 | 248.5 | 3.6 | 948.5 | 851.9 | 886.6 | 908 | 815.4 | 746.5 | 681.4 | 800.9 | 676.5 | 738.8 | 135.3 | 278.8 | 62.4 | 282.8 | 260.2 | 88.3 | 187.1 | 211.3 | 124.7
604 | 414 | 565.3 | 226.12 | 264.3213 | 265.3 | 255.8 | 279.8 | 261.9 | 594.4 | 39 | 20.3 | 69.9 | 3.2 | 248.4 | 3.4 | 948.1 | 852.1 | 885.1 | 909.5 | 821.1 | 746.2 | 678.7 | 790.2 | 678.8 | 739.4 | 135.6 | 278.9 | 62.5 | 282.4 | 260.7 | 88.6 | 187.5 | 211.8 | 125
605 | 415 | 565.7 | 226.28 | 264.5083 | 264.6 | 254.7 | 278.7 | 261.7 | 579.5 | 39 | 20.3 | 70 | 3.4 | 248.3 | 3.1 | 947.6 | 850.3 | 885.4 | 912.6 | 825.9 | 746 | 678.4 | 787.3 | 681.4 | 741.2 | 135.8 | 278.5 | 62.7 | 281.5 | 261.2 | 88.8 | 187.8 | 212.2 | 125.3
606 | 416 | 565.3 | 226.12 | 264.3213 | 263.5 | 254.5 | 278.1 | 261.4 | 567.5 | 39 | 20.3 | 70.1 | 3.6 | 247.9 | 2.9 | 947.7 | 851 | 887.6 | 912.1 | 831.8 | 745.7 | 678.8 | 781.6 | 683.2 | 743 | 136.1 | 278 | 62.9 | 281.3 | 261.2 | 89 | 188.3 | 212.6 | 125.6
607 | 417 | 565.6 | 226.24 | 264.4615 | 262.7 | 254.9 | 277.2 | 261 | 564.5 | 39.1 | 20.3 | 70.2 | 3.4 | 247.7 | 2.6 | 947.8 | 850.3 | 889.2 | 917.2 | 833.5 | 745.3 | 678.6 | 789 | 684.9 | 743 | 136.4 | 277.4 | 63 | 281.1 | 260.9 | 89.3 | 188.6 | 213.1 | 125.9
608 | 418 | 566 | 226.4 | 264.6486 | 262.5 | 255.9 | 275.1 | 261.1 | 568.8 | 39.1 | 20.3 | 70.3 | 3.6 | 247.1 | 2.9 | 947.9 | 851.5 | 885.4 | 919.4 | 836.6 | 745 | 679.2 | 785.2 | 686.9 | 744.5 | 136.7 | 276.7 | 63.2 | 281.1 | 260.9 | 89.5 | 189 | 213.5 | 126.2
609 | 419 | 566 | 226.4 | 264.6486 | 262.6 | 255.3 | 274.5 | 260.5 | 564.5 | 39.2 | 20.3 | 70.3 | 3.5 | 246.2 | 3.6 | 948.1 | 852.9 | 885.1 | 916.9 | 839.3 | 745.1 | 676.8 | 777.4 | 689.3 | 743.7 | 136.9 | 276.5 | 63.3 | 281.3 | 260.7 | 89.7 | 189.3 | 214 | 126.6
610 | 420 | 566.1 | 226.44 | 264.6953 | 263 | 253.8 | 275.3 | 259.9 | 579 | 39.2 | 20.3 | 70.4 | 3.4 | 246.4 | 4.1 | 949 | 853.6 | 888.4 | 912.3 | 839.4 | 744.9 | 676.2 | 789.9 | 692.7 | 744.1 | 137.2 | 276.7 | 63.5 | 281.1 | 261.1 | 90 | 189.9 | 214.5 | 126.9
611 | 421 | 565.2 | 226.08 | 264.2745 | 263.5 | 253.5 | 275.8 | 259 | 594.5 | 39.3 | 20.3 | 70.6 | 3.6 | 246 | 4.2 | 950 | 852.7 | 888 | 910.5 | 831.6 | 745.2 | 674 | 787.7 | 696.2 | 741.4 | 137.4 | 276.8 | 63.6 | 280.3 | 261.8 | 90.2 | 190.2 | 215 | 127.2
612 | 422 | 566.8 | 226.72 | 265.0226 | 263.5 | 253.8 | 276.1 | 258.1 | 613.8 | 39.4 | 20.3 | 70.6 | 3.5 | 246.4 | 4.2 | 951 | 850 | 888.2 | 908 | 826.5 | 745.5 | 673.9 | 788.8 | 700.6 | 740.8 | 137.7 | 276.9 | 63.8 | 280 | 261.9 | 90.5 | 190.5 | 215.4 | 127.5
613 | 423 | 567.1 | 226.84 | 265.1629 | 263.4 | 253.6 | 275.2 | 258 | 631.4 | 39.5 | 20.3 | 70.8 | 3.5 | 248.5 | 4.2 | 952.5 | 849.8 | 884.9 | 895.7 | 817.7 | 745.9 | 672.6 | 787.9 | 704.5 | 739 | 137.9 | 277.4 | 64 | 280.1 | 261.6 | 90.7 | 190.8 | 215.9 | 127.8
614 | 424 | 565.6 | 226.24 | 264.4615 | 264 | 254 | 275.2 | 258.9 | 639.9 | 39.6 | 20.3 | 70.8 | 3.7 | 247.8 | 4.1 | 953.3 | 850.2 | 882.4 | 895.5 | 812.4 | 746.8 | 670.2 | 777.2 | 709 | 736.9 | 138.2 | 278.2 | 64.1 | 280.6 | 261.2 | 90.9 | 191.2 | 216.4 | 128.1
615 | 425 | 567 | 226.8 | 265.1161 | 265 | 254.7 | 277 | 260.3 | 640.4 | 39.7 | 20.3 | 70.9 | 3.3 | 244.9 | 3.9 | 953.6 | 849.8 | 882.3 | 899.2 | 812.6 | 747.5 | 669.5 | 777.7 | 713.7 | 736.5 | 138.4 | 279.3 | 64.3 | 281 | 261 | 91.2 | 191.6 | 216.9 | 128.5
616 | 426 | 567 | 226.8 | 265.1161 | 266.4 | 254.9 | 278.4 | 261 | 642.7 | 39.7 | 20.2 | 71.1 | 3.3 | 246.7 | 3.8 | 953.4 | 849.4 | 886.2 | 899.9 | 812.5 | 748 | 670 | 777.1 | 717.9 | 735.5 | 138.7 | 280.8 | 64.4 | 281.8 | 261.6 | 91.4 | 192 | 217.5 | 128.8
617 | 427 | 567.3 | 226.92 | 265.2564 | 267.5 | 254.9 | 279.3 | 261.7 | 641.7 | 39.8 | 20.2 | 71.2 | 3.2 | 256.8 | 3.7 | 953.3 | 848.6 | 889.2 | 906.4 | 812 | 747.8 | 669.7 | 780.7 | 722.1 | 734.7 | 138.9 | 281.9 | 64.6 | 282.8 | 262.8 | 91.6 | 192.5 | 218 | 129.1
618 | 428 | 567.6 | 227.04 | 265.3967 | 268.4 | 255.6 | 280.4 | 262.2 | 640.8 | 39.9 | 20.2 | 71.3 | 3.6 | 259.6 | 3.6 | 953.2 | 847.7 | 890.6 | 906.9 | 811.6 | 747.2 | 670.3 | 787.4 | 725.7 | 734.1 | 139.1 | 282.7 | 64.8 | 283.6 | 263.8 | 91.9 | 193 | 218.5 | 129.6
619 | 429 | 566.8 | 226.72 | 265.0226 | 269 | 256.1 | 281.3 | 262.7 | 645 | 40 | 20.2 | 71.4 | 3.4 | 253.6 | 3.3 | 953.1 | 848.1 | 892.2 | 912.9 | 817 | 746.7 | 672.1 | 788.2 | 729.1 | 735.3 | 139.4 | 283.2 | 64.9 | 284.3 | 264.6 | 92.1 | 193.4 | 219 | 129.9
620 | 430 | 566.9 | 226.76 | 265.0694 | 269.7 | 256.3 | 281.3 | 263.3 | 630.7 | 40.1 | 20.2 | 71.6 | 3.4 | 246.3 | 3.1 | 953 | 847.8 | 894.6 | 917.4 | 822.4 | 746 | 671.5 | 792.7 | 732.6 | 735.4 | 139.6 | 283.5 | 65.1 | 285.4 | 265.8 | 92.4 | 193.8 | 219.6 | 130.3
621 | 431 | 566.9 | 226.76 | 265.0694 | 270.7 | 257 | 281.5 | 263.6 | 623.1 | 40.3 | 20.2 | 71.7 | 3.5 | 243.3 | 3 | 952.6 | 847.9 | 892.4 | 916.9 | 825.6 | 745.7 | 671.3 | 793.6 | 736 | 735.1 | 139.8 | 283.7 | 65.2 | 285.8 | 266.7 | 92.6 | 194.3 | 220.1 | 130.6
622 | 432 | 566.9 | 226.76 | 265.0694 | 271.8 | 257.1 | 282.4 | 263.8 | 614.4 | 40.4 | 20.2 | 71.8 | 3.3 | 245.3 | 2.9 | 953 | 850.3 | 890.4 | 905.1 | 817 | 745.9 | 670.4 | 793.9 | 740.1 | 732.8 | 140 | 283.9 | 65.4 | 286.4 | 267 | 92.8 | 194.7 | 220.5 | 131
623 | 433 | 567 | 226.8 | 265.1161 | 272.9 | 257.8 | 282.4 | 264.2 | 624.4 | 40.5 | 20.2 | 72 | 3.5 | 244.7 | 3 | 953.4 | 850.8 | 891.9 | 908.5 | 813.8 | 746.1 | 672.4 | 795.2 | 745.1 | 731.1 | 140.2 | 284 | 65.6 | 286.9 | 267.1 | 93.1 | 195.2 | 221 | 131.4
624 | 434 | 567.5 | 227 | 265.3499 | 274.1 | 258.1 | 284.1 | 264.8 | 635.8 | 40.7 | 20.2 | 72.1 | 3.7 | 243 | 2.9 | 954 | 854.5 | 887.9 | 905.3 | 812.5 | 746.2 | 672.5 | 794.6 | 749.4 | 731 | 140.5 | 284.1 | 65.7 | 287.3 | 268 | 93.3 | 195.7 | 221.5 | 131.7
625 | 435 | 565.2 | 226.08 | 264.2745 | 274.7 | 258.7 | 285.6 | 265.9 | 637.5 | 40.8 | 20.2 | 72.2 | 3.4 | 241.6 | 2.8 | 954.2 | 854.1 | 887.8 | 905.8 | 811.2 | 746.6 | 669.8 | 791.3 | 754.1 | 730.1 | 140.7 | 284 | 65.9 | 288.1 | 268.7 | 93.5 | 195.9 | 222 | 132.1
626 | 436 | 564.2 | 225.68 | 263.8069 | 274.6 | 258.7 | 285.7 | 266.2 | 646 | 40.8 | 20.2 | 72.3 | 3.3 | 241.5 | 2.9 | 954 | 852.4 | 890.7 | 909 | 811.7 | 747.3 | 669.6 | 792.7 | 760.9 | 729.1 | 141 | 284.1 | 66.1 | 288.8 | 268.9 | 93.8 | 196.5 | 222.5 | 132.4
627 | 437 | 563.4 | 225.36 | 263.4329 | 274 | 258.6 | 286.1 | 266.4 | 643.4 | 40.9 | 20.2 | 72.4 | 3.4 | 244.4 | 3.2 | 953.1 | 849.5 | 892.8 | 915.8 | 820.4 | 747.3 | 675.4 | 799.7 | 764.6 | 732.2 | 141.2 | 284.4 | 66.2 | 289.2 | 268.6 | 94 | 196.8 | 223.1 | 132.7
628 | 438 | 564.4 | 225.76 | 263.9004 | 273.9 | 259 | 286.3 | 266.7 | 640.2 | 41 | 20.2 | 72.5 | 3.3 | 251.3 | 3.5 | 952.4 | 849.2 | 892.9 | 920.4 | 830.9 | 746.8 | 678.4 | 801.2 | 765.3 | 734.3 | 141.4 | 284.4 | 66.4 | 289.9 | 268.7 | 94.3 | 197.2 | 223.6 | 133.1
629 | 439 | 564.8 | 225.92 | 264.0875 | 273.4 | 259.6 | 285.5 | 266.9 | 615.6 | 41.1 | 20.2 | 72.5 | 3.3 | 256.4 | 3.7 | 951.7 | 848.6 | 891.3 | 921.7 | 838.5 | 746.1 | 677.2 | 795.7 | 767.2 | 736 | 141.7 | 284.2 | 66.5 | 290.3 | 269.4 | 94.5 | 197.6 | 224.1 | 133.4
630 | 440 | 565.9 | 226.36 | 264.6018 | 273.4 | 259.9 | 285.2 | 266.5 | 586.9 | 41.2 | 20.2 | 72.6 | 3.2 | 276.3 | 3.9 | 951.3 | 853.4 | 888.5 | 914.9 | 842.4 | 744.9 | 672.2 | 774.1 | 769.9 | 737.4 | 141.9 | 284.1 | 66.7 | 290.5 | 269.7 | 94.7 | 198 | 224.5 | 133.8
631 | 441 | 568 | 227.2 | 265.5837 | 273 | 260 | 284.1 | 266.2 | 565.1 | 41.4 | 20.2 | 72.8 | 3.3 | 287 | 4.1 | 951.2 | 855 | 892.1 | 916.9 | 849.6 | 744.1 | 672.5 | 779.4 | 772.4 | 738.8 | 142.2 | 283.5 | 66.9 | 290.2 | 269.6 | 95 | 198.5 | 225 | 134.1
632 | 442 | 567.6 | 227.04 | 265.3967 | 272.5 | 259.7 | 282.9 | 265.9 | 556.2 | 41.5 | 20.2 | 72.9 | 3.1 | 276 | 4.1 | 950.9 | 855.9 | 892.8 | 920.5 | 855.8 | 743.6 | 672.3 | 785.2 | 774 | 739.3 | 142.4 | 283 | 67 | 289.6 | 269.7 | 95.2 | 198.9 | 225.3 | 134.4
633 | 443 | 567.3 | 226.92 | 265.2564 | 272.1 | 259.9 | 281.9 | 265.1 | 553.7 | 41.5 | 20.2 | 73.1 | 3.1 | 260.8 | 3.9 | 951.1 | 860 | 891.2 | 918.2 | 859.1 | 743.5 | 671.9 | 783 | 775.3 | 740.9 | 142.7 | 282.2 | 67.2 | 289.2 | 269.4 | 95.4 | 199.2 | 225.7 | 134.7
634 | 444 | 566 | 226.4 | 264.6486 | 271.3 | 259.6 | 281.2 | 264 | 556.6 | 41.6 | 20.2 | 73.2 | 3.4 | 253.4 | 3.7 | 951.7 | 859.3 | 891 | 920 | 862.9 | 743.1 | 674.4 | 785.8 | 775 | 744.3 | 142.9 | 281.1 | 67.3 | 288.4 | 268.7 | 95.7 | 199.5 | 226.1 | 135
635 | 445 | 565.6 | 226.24 | 264.4615 | 270.5 | 259.2 | 280.6 | 263.1 | 566.7 | 41.6 | 20.2 | 73.3 | 3.4 | 256 | 3.4 | 951.9 | 855.8 | 893 | 919.9 | 866.6 | 742.2 | 683.4 | 795.8 | 774.9 | 746.7 | 143.2 | 280.5 | 67.5 | 287.7 | 268.3 | 95.9 | 199.7 | 226.5 | 135.2
636 | 446 | 565.2 | 226.08 | 264.2745 | 270 | 258.6 | 279.2 | 262.5 | 582.8 | 41.6 | 20.2 | 73.4 | 3.3 | 275 | 3.4 | 951.3 | 855.1 | 893.4 | 924.1 | 870 | 742 | 689.2 | 803 | 776.1 | 749.2 | 143.4 | 280.7 | 67.7 | 287.5 | 267.9 | 96.1 | 200 | 227 | 135.5
637 | 447 | 567.6 | 227.04 | 265.3967 | 269.4 | 258 | 278.9 | 262.7 | 574.8 | 41.6 | 20.2 | 73.5 | 3 | 303.5 | 3.8 | 951.2 | 858 | 887.9 | 921.4 | 870.8 | 742.1 | 688.9 | 801.3 | 778.3 | 750.7 | 143.6 | 281.1 | 67.9 | 286.9 | 267.7 | 96.4 | 200.3 | 227.5 | 135.9
638 | 448 | 565.5 | 226.2 | 264.4148 | 269.2 | 257.6 | 278.7 | 262.8 | 566 | 41.6 | 20.2 | 73.7 | 3.2 | 299.7 | 4.4 | 952 | 862.8 | 885.1 | 912.7 | 863.4 | 742.3 | 687.1 | 801.2 | 780.7 | 748.6 | 143.9 | 281.3 | 68 | 286.2 | 267.8 | 96.6 | 200.6 | 227.9 | 136.2
639 | 449 | 566.1 | 226.44 | 264.6953 | 270.3 | 257.9 | 278.7 | 262.4 | 581.6 | 41.7 | 20.2 | 73.8 | 3.3 | 278 | 4.6 | 953.3 | 862.6 | 884.6 | 909.8 | 850.7 | 743.2 | 683.8 | 793.4 | 784.9 | 747.9 | 144.1 | 281.8 | 68.2 | 285.8 | 267.8 | 96.9 | 200.9 | 228.4 | 136.5
640 | 450 | 565.6 | 226.24 | 264.4615 | 272.4 | 257.6 | 279.1 | 261.9 | 603.6 | 41.8 | 20.2 | 73.9 | 3.5 | 285 | 5.2 | 953.5 | 856.8 | 885.8 | 915 | 845.5 | 744.2 | 682.4 | 789.9 | 790.1 | 746.3 | 144.3 | 282.2 | 68.3 | 285.8 | 267.9 | 97.1 | 201.2 | 228.9 | 136.8
641 | 451 | 565.9 | 226.36 | 264.6018 | 272.5 | 257.1 | 279.7 | 262.2 | 618 | 41.9 | 20.2 | 74 | 3.1 | 286 | 5.4 | 954.3 | 855.1 | 882.8 | 910.2 | 836.7 | 744.3 | 679.3 | 785.9 | 791.4 | 744.6 | 144.6 | 282.8 | 68.5 | 286.4 | 267.9 | 97.3 | 201.5 | 229.4 | 137.1
642 | 452 | 567.2 | 226.88 | 265.2096 | 272.7 | 257.1 | 278.9 | 262.4 | 621.3 | 42 | 20.2 | 74 | 3.2 | 287.8 | 5 | 954.7 | 857.4 | 881.4 | 912 | 832.3 | 744.6 | 679.5 | 783.5 | 794.2 | 743.5 | 144.8 | 283.8 | 68.7 | 287.3 | 268.6 | 97.5 | 201.9 | 229.8 | 137.5
643 | 453 | 567.7 | 227.08 | 265.4434 | 272.9 | 257.7 | 278.8 | 262.4 | 633.6 | 42.1 | 20.2 | 74.2 | 3 | 294.7 | 4.8 | 955.1 | 855.7 | 881.7 | 913.9 | 827.8 | 744.9 | 677.8 | 787.1 | 797 | 741.7 | 145 | 284.7 | 68.8 | 288 | 269.2 | 97.8 | 202.3 | 230.3 | 137.8
644 | 454 | 568.4 | 227.36 | 265.7707 | 273.4 | 258.3 | 280.6 | 262.8 | 643.5 | 42.1 | 20.2 | 74.3 | 3.2 | 294.7 | 4.5 | 955.5 | 854.4 | 879.1 | 909.3 | 826.3 | 745.2 | 678.5 | 782.3 | 801 | 740.8 | 145.3 | 285.3 | 69 | 289.1 | 270.2 | 98 | 202.9 | 230.7 | 138.1
645 | 455 | 568.7 | 227.48 | 265.911 | 274.1 | 258.7 | 281.8 | 263.7 | 634.3 | 42.1 | 20.2 | 74.3 | 3.2 | 293 | 4 | 955.1 | 854 | 879.1 | 913.4 | 834.2 | 745.3 | 676.9 | 771.6 | 804.7 | 741.1 | 145.5 | 285.6 | 69.2 | 289.2 | 271 | 98.3 | 203.3 | 231.2 | 138.5
646 | 456 | 566.7 | 226.68 | 264.9759 | 274.9 | 258.7 | 282.9 | 264.2 | 625.8 | 42.1 | 20.2 | 74.4 | 3.2 | 286.7 | 3.7 | 954.7 | 853 | 881.1 | 915.3 | 842.5 | 745.3 | 677.1 | 778.5 | 807 | 742.8 | 145.8 | 285.9 | 69.3 | 290.2 | 270.9 | 98.5 | 203.8 | 231.6 | 138.8
647 | 457 | 567.6 | 227.04 | 265.3967 | 275.3 | 258 | 283.2 | 265.1 | 627.8 | 42.2 | 20.2 | 74.5 | 3.7 | 282.1 | 3.5 | 955.2 | 854 | 882.9 | 913 | 840.7 | 745.3 | 680.3 | 784.8 | 807 | 742.2 | 146 | 286.1 | 69.5 | 291.2 | 271.7 | 98.7 | 204.1 | 232 | 139.2
648 | 458 | 567.6 | 227.04 | 265.3967 | 275.8 | 257.9 | 283.5 | 265.5 | 634.8 | 42.3 | 20.2 | 74.6 | 3.3 | 282 | 3.5 | 955.2 | 854.9 | 883.6 | 918.2 | 845 | 745.2 | 680.4 | 782.5 | 806.9 | 741.9 | 146.2 | 286.2 | 69.7 | 291.8 | 272.2 | 99 | 204.5 | 232.5 | 139.5
649 | 459 | 566.6 | 226.64 | 264.9291 | 275.9 | 257.6 | 284.5 | 265.7 | 627.3 | 42.4 | 20.2 | 74.6 | 3.2 | 288.7 | 3.6 | 955 | 856.9 | 882 | 917 | 846.8 | 745.7 | 677.6 | 779.7 | 809 | 742.5 | 146.5 | 286.4 | 69.8 | 291.9 | 272.3 | 99.2 | 204.9 | 233 | 139.9
650 | 460 | 566.6 | 226.64 | 264.9291 | 275.5 | 257.6 | 285.3 | 265.9 | 637.4 | 42.5 | 20.2 | 74.7 | 3.2 | 289.9 | 3.9 | 955.9 | 856 | 881.6 | 910.4 | 841.3 | 746.3 | 681.5 | 778.6 | 811.9 | 740.4 | 146.8 | 286.5 | 70 | 292.1 | 272.4 | 99.4 | 205.2 | 233.4 | 140.2
651 | 461 | 565.3 | 226.12 | 264.3213 | 275.2 | 257.7 | 286.4 | 266.6 | 653.7 | 42.6 | 20.2 | 74.8 | 3.3 | 289 | 4.1 | 955.1 | 852.8 | 886.7 | 916.7 | 844.8 | 746.8 | 686.7 | 783.1 | 813.6 | 741 | 147 | 286.3 | 70.2 | 292.5 | 272.3 | 99.7 | 205.6 | 233.9 | 140.6
652 | 462 | 565 | 226 | 264.181 | 276.3 | 258.5 | 287.8 | 267.4 | 661.9 | 42.7 | 20.2 | 74.9 | 3.7 | 287.3 | 4 | 953.4 | 848.7 | 888.5 | 920 | 851.5 | 747 | 692.6 | 787.8 | 813.5 | 743.4 | 147.3 | 286.1 | 70.3 | 292.4 | 272.7 | 99.9 | 205.9 | 234.5 | 140.9
653 | 463 | 565.8 | 226.32 | 264.555 | 277.4 | 258.5 | 287.7 | 268 | 674.7 | 42.8 | 20.2 | 74.9 | 3.7 | 303.2 | 3.6 | 952.6 | 849.3 | 887.6 | 919.5 | 852.7 | 747 | 696.5 | 793.9 | 813.3 | 745.3 | 147.6 | 286.5 | 70.5 | 293.2 | 273.2 | 100.2 | 206.4 | 235 | 141.2
654 | 464 | 565.7 | 226.28 | 264.5083 | 278.7 | 259.1 | 287.7 | 268.2 | 696.6 | 42.9 | 20.2 | 75.1 | 3.8 | 313.7 | 3.3 | 953 | 847.6 | 885.6 | 915.3 | 839.4 | 747.6 | 694.9 | 792.2 | 813 | 741.1 | 147.9 | 287.4 | 70.7 | 294.6 | 274.4 | 100.4 | 206.8 | 235.5 | 141.6
655 | 465 | 567 | 226.8 | 265.1161 | 279.5 | 260.1 | 288.1 | 268.8 | 701.6 | 43 | 20.2 | 75.3 | 3.2 | 298.5 | 2.9 | 954.1 | 847.8 | 880.4 | 908 | 827.1 | 748.4 | 696.8 | 793.6 | 814.1 | 739.2 | 148.2 | 288.1 | 70.8 | 295.7 | 275.6 | 100.6 | 207.3 | 236 | 142
656 | 466 | 567.8 | 227.12 | 265.4902 | 280.7 | 261.1 | 289.4 | 270.7 | 713.5 | 43.1 | 20.1 | 75.4 | 3.6 | 267.7 | 2.7 | 954.8 | 850.6 | 879.3 | 901.1 | 819.9 | 749.2 | 700.7 | 792 | 814.8 | 737.7 | 148.4 | 289.1 | 71 | 296.6 | 276.4 | 100.9 | 207.7 | 236.6 | 142.3
657 | 467 | 568.9 | 227.56 | 266.0045 | 281.9 | 262.3 | 290.9 | 272.1 | 713.3 | 43.2 | 20.1 | 75.4 | 3.5 | 255.2 | 2.6 | 955 | 852 | 881.7 | 901.3 | 818.3 | 750.1 | 702.1 | 795.4 | 815.9 | 737.5 | 148.7 | 290.2 | 71.2 | 297.9 | 276.8 | 101.1 | 208.1 | 237.1 | 142.7
658 | 468 | 566.2 | 226.48 | 264.7421 | 282.8 | 263.7 | 292.9 | 272.7 | 704.9 | 43.3 | 20.1 | 75.5 | 3.5 | 255.6 | 2.4 | 954 | 849.5 | 885.7 | 909.7 | 825.4 | 750.4 | 704 | 798.4 | 816.1 | 739.2 | 149 | 290.8 | 71.4 | 299.3 | 277.4 | 101.4 | 208.6 | 237.7 | 143.1
659 | 469 | 566.1 | 226.44 | 264.6953 | 283.5 | 264.7 | 295 | 273.2 | 703.7 | 43.3 | 20.1 | 75.6 | 3.5 | 257.5 | 2.3 | 953.1 | 849.6 | 885.9 | 910.7 | 827.7 | 751 | 704.5 | 798 | 815.7 | 739.8 | 149.3 | 291 | 71.5 | 300.3 | 278.5 | 101.6 | 209 | 238.3 | 143.5
660 | 470 | 565.8 | 226.32 | 264.555 | 284.2 | 264.9 | 295.4 | 274 | 707.5 | 43.4 | 20.1 | 75.7 | 3.6 | 263.7 | 2.4 | 952.4 | 848.3 | 887 | 915.3 | 827.4 | 751.6 | 704.7 | 801.4 | 816 | 738.7 | 149.6 | 291.5 | 71.7 | 300.6 | 279 | 101.9 | 209.6 | 238.8 | 143.9
661 | 471 | 566.2 | 226.48 | 264.7421 | 285 | 265.2 | 295.5 | 274.8 | 702.8 | 43.4 | 20.1 | 75.7 | 3.3 | 276.3 | 2.8 | 952 | 847.3 | 888.4 | 917.7 | 832 | 752.1 | 712.4 | 807.8 | 816.4 | 740.9 | 149.9 | 291.8 | 71.9 | 301 | 279.3 | 102.1 | 210.2 | 239.3 | 144.2
662 | 472 | 567.7 | 227.08 | 265.4434 | 285.8 | 266 | 295.9 | 275.3 | 692.7 | 43.5 | 20.1 | 75.8 | 3.6 | 287.5 | 3.1 | 950.6 | 843.4 | 889.7 | 919.1 | 833.9 | 752.4 | 717 | 809.7 | 814.9 | 743.3 | 150.2 | 292.1 | 72 | 301.4 | 280.1 | 102.3 | 210.6 | 239.9 | 144.6
663 | 473 | 568.3 | 227.32 | 265.724 | 285.9 | 266.8 | 295.9 | 275.9 | 696 | 43.7 | 20.1 | 75.8 | 3.7 | 285.8 | 3.3 | 949.8 | 842.8 | 890.9 | 922.9 | 832.7 | 752.7 | 721.1 | 814.7 | 813.2 | 743.9 | 150.5 | 292.3 | 72.2 | 301.6 | 280.2 | 102.6 | 211 | 240.4 | 144.9
664 | 474 | 566.5 | 226.6 | 264.8823 | 285.2 | 266.7 | 296.4 | 275.8 | 687.4 | 43.8 | 20.1 | 75.8 | 3.3 | 284.7 | 3.4 | 948.4 | 840 | 888.9 | 917.9 | 833.2 | 752.9 | 723.1 | 817.9 | 811.8 | 746.1 | 150.8 | 292.8 | 72.4 | 302.1 | 279.8 | 102.9 | 211.4 | 241 | 145.3
665 | 475 | 566.3 | 226.52 | 264.7888 | 285.2 | 267 | 296 | 275.8 | 691.1 | 43.9 | 20.1 | 75.9 | 3.5 | 286.6 | 3.5 | 946.8 | 837.8 | 888.1 | 918.4 | 837.8 | 753.1 | 726.6 | 820.1 | 810.9 | 748.7 | 151.1 | 292.9 | 72.5 | 302.6 | 280.2 | 103.1 | 211.8 | 241.6 | 145.6
666 | 476 | 565.8 | 226.32 | 264.555 | 285.5 | 266.9 | 294.5 | 276 | 690.4 | 43.9 | 20.1 | 76 | 3.2 | 297.1 | 3.6 | 945.5 | 836.8 | 887.1 | 918.2 | 843.2 | 753 | 728.5 | 819.6 | 810.4 | 751.5 | 151.4 | 293 | 72.7 | 302.9 | 279.8 | 103.3 | 212.1 | 242.1 | 146
667 | 477 | 567.2 | 226.88 | 265.2096 | 285.6 | 267.2 | 293.3 | 275.3 | 690.9 | 44 | 20.1 | 76 | 3.2 | 299.2 | 3.9 | 944.1 | 836.7 | 888.1 | 918.3 | 844.6 | 753.5 | 730.5 | 823.6 | 809.8 | 753.4 | 151.7 | 293.2 | 72.9 | 303.2 | 279.2 | 103.6 | 212.5 | 242.7 | 146.3
668 | 478 | 569.3 | 227.72 | 266.1916 | 285.7 | 269.3 | 292.3 | 274.4 | 697.1 | 44.1 | 20.1 | 76.1 | 3.4 | 305.5 | 4 | 943.2 | 837.9 | 887.7 | 917.3 | 845.5 | 754.1 | 730.7 | 827.3 | 809 | 754.6 | 152 | 293.4 | 73 | 303.4 | 279 | 103.8 | 212.8 | 243.3 | 146.7
669 | 479 | 570 | 228 | 266.5189 | 286 | 271.2 | 292.9 | 274 | 705 | 44.1 | 20.1 | 76.1 | 3.6 | 298.6 | 4 | 942.6 | 840.8 | 887.5 | 916.6 | 848.7 | 754.6 | 731.4 | 829.9 | 809.2 | 756.1 | 152.3 | 293.6 | 73.2 | 303.7 | 279.1 | 104.1 | 213.2 | 243.9 | 147
670 | 480 | 568.8 | 227.52 | 265.9578 | 286.3 | 271.4 | 293.9 | 274.3 | 692.5 | 44.1 | 20.1 | 76.1 | 3.7 | 277 | 3.7 | 942.3 | 839.7 | 887.1 | 918 | 854.9 | 755 | 731.7 | 828.8 | 808.4 | 758.4 | 152.7 | 293.5 | 73.4 | 303.6 | 279.3 | 104.3 | 213.7 | 244.5 | 147.4
671 | 481 | 568 | 227.2 | 265.5837 | 286.3 | 272.2 | 294.6 | 274.7 | 694 | 44.2 | 20.1 | 76.2 | 3.4 | 282.9 | 3.5 | 942.4 | 841.7 | 886.4 | 917.9 | 855.8 | 755.3 | 732.5 | 829.7 | 807.7 | 761.3 | 153 | 293.9 | 73.6 | 304.1 | 279.3 | 104.6 | 214.1 | 244.9 | 147.8
672 | 482 | 567.3 | 226.92 | 265.2564 | 285.4 | 273.1 | 294.3 | 274.5 | 698.2 | 44.2 | 20.1 | 76.3 | 3.4 | 298.9 | 3.6 | 941.1 | 839.3 | 886.4 | 913 | 856.7 | 755.7 | 733.4 | 830.6 | 807.1 | 763.1 | 153.3 | 294.2 | 73.7 | 303.7 | 279.7 | 104.8 | 214.5 | 245.5 | 148.1
673 | 483 | 567.8 | 227.12 | 265.4902 | 284.9 | 272.8 | 294 | 273.7 | 699.6 | 44.3 | 20.1 | 76.3 | 3.6 | 292.6 | 3.4 | 940.5 | 840.4 | 886.2 | 915.6 | 859.4 | 756.4 | 732.3 | 825.7 | 807.4 | 764.6 | 153.6 | 294.6 | 73.9 | 303.4 | 280.4 | 105.1 | 214.9 | 246 | 148.4
674 | 484 | 567.3 | 226.92 | 265.2564 | 284.2 | 273.1 | 293.3 | 274.1 | 681.6 | 44.3 | 20.1 | 76.4 | 3 | 286.5 | 4.4 | 940 | 839.1 | 886.6 | 917.1 | 864.3 | 756.8 | 731.2 | 823.5 | 806.4 | 766.6 | 153.9 | 295 | 74.1 | 302.9 | 280.8 | 105.3 | 215.3 | 246.4 | 148.8
675 | 485 | 567.7 | 227.08 | 265.4434 | 283.6 | 273.7 | 294.2 | 274.3 | 662.1 | 44.3 | 20.1 | 76.5 | 3.2 | 305.7 | 5.4 | 939.5 | 841.7 | 888.2 | 918.5 | 868.9 | 756.9 | 729.5 | 821.4 | 805.3 | 768.9 | 154.2 | 295.2 | 74.3 | 302.3 | 281.1 | 105.6 | 215.6 | 246.8 | 149.1
676 | 486 | 568.1 | 227.24 | 265.6305 | 283.5 | 274.1 | 294.5 | 273.3 | 653.5 | 44.3 | 20.1 | 76.6 | 3 | 296.4 | 5.9 | 939.8 | 841.7 | 888.8 | 919 | 873.1 | 757 | 729.6 | 820 | 804.5 | 771.3 | 154.5 | 294.9 | 74.4 | 302.5 | 281 | 105.9 | 216.1 | 247.3 | 149.4
677 | 487 | 567 | 226.8 | 265.1161 | 283.6 | 274.2 | 294.6 | 272.6 | 642 | 44.3 | 20.1 | 76.6 | 3.2 | 271.3 | 6.6 | 939.8 | 843.1 | 889.2 | 917.9 | 879 | 756.9 | 727.5 | 818.3 | 804.2 | 772.6 | 154.9 | 294.4 | 74.6 | 302 | 280.7 | 106.1 | 216.4 | 247.7 | 149.7
678 | 488 | 567 | 226.8 | 265.1161 | 283.1 | 273.8 | 294.3 | 272.4 | 634.7 | 44.4 | 20.1 | 76.5 | 3.6 | 284.5 | 7 | 939.5 | 839.5 | 889.9 | 915.2 | 884.7 | 757.4 | 729.8 | 821.8 | 803.7 | 774.1 | 155.2 | 294.2 | 74.8 | 301.4 | 280.4 | 106.4 | 216.7 | 248.2 | 150.1
679 | 489 | 565.6 | 226.24 | 264.4615 | 282.5 | 274.7 | 293.4 | 272.3 | 645.8 | 44.5 | 20.1 | 76.5 | 3.5 | 260 | 6.3 | 939.4 | 836.9 | 889.8 | 915.8 | 882.7 | 757.7 | 730 | 821.4 | 803.9 | 774.7 | 155.5 | 293.8 | 75 | 300.7 | 280.4 | 106.6 | 217 | 248.7 | 150.4
680 | 490 | 566.3 | 226.52 | 264.7888 | 281.7 | 275 | 292.6 | 271.9 | 659.8 | 44.5 | 20.1 | 76.6 | 3.8 | 260.9 | 5.2 | 939.4 | 834.6 | 888.7 | 915.7 | 876.1 | 758.6 | 730.7 | 823.5 | 804.6 | 774 | 155.8 | 293.6 | 75.1 | 300.5 | 280 | 106.9 | 217.3 | 249.2 | 150.7
681 | 491 | 566.5 | 226.6 | 264.8823 | 281.1 | 274.8 | 291.7 | 272.1 | 679.5 | 44.6 | 20.1 | 76.6 | 3.4 | 283 | 4.5 | 939.7 | 834 | 888.1 | 919.9 | 866.8 | 759.4 | 728.3 | 820.4 | 805.3 | 772.1 | 156.1 | 293.6 | 75.3 | 300.5 | 279.8 | 107.1 | 217.5 | 249.8 | 151
682 | 492 | 566.8 | 226.72 | 265.0226 | 281.2 | 275.5 | 292.3 | 272.9 | 687.5 | 44.7 | 20.1 | 76.6 | 3.4 | 300.4 | 4.3 | 939.7 | 834.8 | 887.8 | 920.5 | 864.9 | 759.8 | 730.8 | 820.8 | 806.5 | 772.7 | 156.4 | 293.9 | 75.5 | 300.8 | 279.5 | 107.4 | 217.8 | 250.4 | 151.4
683 | 493 | 565.9 | 226.36 | 264.6018 | 281.8 | 275.8 | 292.6 | 273.9 | 670.5 | 44.8 | 20 | 76.7 | 3.1 | 307.3 | 3.9 | 938.9 | 834.5 | 888.4 | 918.9 | 868.9 | 759.9 | 732.1 | 820.5 | 806.9 | 775.6 | 156.8 | 294.5 | 75.7 | 301.2 | 279.6 | 107.6 | 218.2 | 250.9 | 151.7
684 | 494 | 566.1 | 226.44 | 264.6953 | 282 | 275.5 | 293.1 | 273.6 | 675.5 | 44.8 | 20 | 76.7 | 3.5 | 296.4 | 4 | 938.4 | 833 | 888.7 | 919.9 | 873.7 | 760.1 | 732.6 | 824.2 | 807.2 | 776.4 | 157.1 | 294.9 | 75.8 | 301.4 | 279.8 | 107.9 | 218.4 | 251.4 | 152.1
685 | 495 | 566.4 | 226.56 | 264.8356 | 282 | 274.5 | 294.2 | 273.3 | 689.8 | 44.9 | 20 | 76.7 | 3.7 | 273.3 | 4 | 937.9 | 832 | 888.2 | 917.3 | 875.4 | 760.5 | 733.3 | 825.2 | 807 | 776.9 | 157.4 | 295.3 | 76 | 301.7 | 280.1 | 108.2 | 218.8 | 251.9 | 152.4
686 | 496 | 566.5 | 226.6 | 264.8823 | 282.3 | 273.9 | 295 | 272.7 | 696 | 45 | 20 | 76.7 | 3.6 | 291.3 | 3.9 | 937.9 | 833.8 | 888.4 | 918.8 | 879.8 | 761.2 | 731.7 | 822.6 | 808 | 778.2 | 157.7 | 295.4 | 76.2 | 301.4 | 280.3 | 108.4 | 219.3 | 252.4 | 152.7
687 | 497 | 566.5 | 226.6 | 264.8823 | 282.7 | 273.9 | 296.2 | 272.6 | 684.8 | 45 | 20 | 76.7 | 3.9 | 308.4 | 3.7 | 937.9 | 833.2 | 889.6 | 919.7 | 879.2 | 762.7 | 733 | 824.1 | 809.4 | 776.7 | 158.1 | 295.2 | 76.4 | 301.2 | 280.6 | 108.7 | 219.6 | 252.9 | 153.1
688 | 498 | 566.6 | 226.64 | 264.9291 | 282.9 | 274.7 | 296.7 | 273.4 | 683.8 | 45.1 | 20 | 76.8 | 3.9 | 308.7 | 3.8 | 938.4 | 832.6 | 889.5 | 919.5 | 872.7 | 763.8 | 730.9 | 823.8 | 811.9 | 774.3 | 158.4 | 295.1 | 76.5 | 302.1 | 281 | 108.9 | 220 | 253.5 | 153.4
689 | 499 | 566.6 | 226.64 | 264.9291 | 283.2 | 274.1 | 297.4 | 274.3 | 687.8 | 45.1 | 20 | 77 | 4.1 | 296 | 4 | 938.8 | 833.7 | 888.6 | 920 | 867 | 764.6 | 731.8 | 824.3 | 814.5 | 774.4 | 158.7 | 295 | 76.7 | 301.9 | 281.3 | 109.2 | 220.3 | 254 | 153.8
690 | 500 | 566.7 | 226.68 | 264.9759 | 284.2 | 273.8 | 297.3 | 275 | 693.8 | 45.2 | 20 | 77.1 | 4 | 285.2 | 4.3 | 939.1 | 833.3 | 887.9 | 919.6 | 863.8 | 765.9 | 732 | 825 | 817.3 | 774.6 | 159 | 295.1 | 76.9 | 302.7 | 281.5 | 109.4 | 220.4 | 254.6 | 154.1
691 | 501 | 566.3 | 226.52 | 264.7888 | 285.3 | 273.6 | 296.3 | 275.4 | 688.6 | 45.2 | 20 | 77.3 | 4.2 | 308.5 | 4.2 | 939.2 | 834 | 888 | 919.8 | 864.9 | 766.5 | 733.7 | 825.7 | 818 | 777.5 | 159.4 | 295.5 | 77.1 | 303.5 | 281.7 | 109.7 | 220.8 | 255.1 | 154.4
692 | 502 | 566.1 | 226.44 | 264.6953 | 285.5 | 273.5 | 296.4 | 276.2 | 676.3 | 45.3 | 20 | 77.3 | 4 | 335.6 | 4.2 | 939.2 | 832.9 | 888.3 | 919.6 | 865.9 | 766.9 | 734.2 | 825.1 | 818.3 | 779.5 | 159.7 | 295.6 | 77.2 | 304 | 281.9 | 110 | 221.2 | 255.6 | 154.8
693 | 503 | 568.4 | 227.36 | 265.7707 | 286.3 | 273.5 | 296.7 | 276.7 | 683.4 | 45.4 | 20 | 77.3 | 4.2 | 340.4 | 3.3 | 939.3 | 833.9 | 888.8 | 922.6 | 868.5 | 768 | 732.9 | 825.5 | 820.1 | 778.7 | 160 | 295.5 | 77.4 | 304.4 | 281.6 | 110.2 | 221.5 | 256 | 155.1
694 | 504 | 569.2 | 227.68 | 266.1448 | 286.4 | 274.5 | 296.6 | 276.3 | 680.6 | 45.4 | 20 | 77.4 | 4 | 327.9 | 2.5 | 939.8 | 835.7 | 888.9 | 924.2 | 870.6 | 768.5 | 733.2 | 824.8 | 820.4 | 779.9 | 160.4 | 295.5 | 77.6 | 305 | 281.9 | 110.5 | 221.9 | 256.5 | 155.4
695 | 505 | 568.8 | 227.52 | 265.9578 | 285.5 | 275 | 297.5 | 276 | 665.7 | 45.5 | 20 | 77.5 | 3.9 | 301.8 | 2.3 | 939.9 | 832.6 | 889 | 921.1 | 866.4 | 768.7 | 735 | 821.9 | 820.1 | 780.1 | 160.7 | 295.6 | 77.8 | 305.3 | 282.1 | 110.7 | 222.3 | 257 | 155.8
696 | 506 | 568.4 | 227.36 | 265.7707 | 286.1 | 275.9 | 297.3 | 276.7 | 647.8 | 45.5 | 20 | 77.6 | 3.9 | 288.6 | 2.6 | 940.2 | 831.9 | 889.5 | 920 | 866.9 | 769.1 | 735.3 | 820 | 819.3 | 782.2 | 161.1 | 295.6 | 77.9 | 305.5 | 282.5 | 111 | 222.7 | 257.6 | 156.1
697 | 507 | 568.7 | 227.48 | 265.911 | 286.3 | 276.3 | 295.8 | 277.3 | 618.6 | 45.6 | 20 | 77.8 | 3.2 | 296.1 | 2.9 | 940.5 | 831.1 | 890.5 | 919.7 | 869 | 769 | 731.1 | 811.5 | 818.6 | 782.7 | 161.4 | 295.4 | 78.1 | 305.7 | 282.9 | 111.2 | 223 | 258.1 | 156.5
698 | 508 | 567.3 | 226.92 | 265.2564 | 285.3 | 275.1 | 295.3 | 277.8 | 602.8 | 45.6 | 20 | 77.9 | 3.8 | 292.7 | 2.9 | 940.5 | 830.9 | 891.4 | 918.5 | 873.5 | 769.4 | 728.7 | 810.7 | 818.9 | 783 | 161.8 | 295.3 | 78.3 | 306.1 | 282.7 | 111.5 | 223.4 | 258.6 | 156.8
699 | 509 | 567.4 | 226.96 | 265.3032 | 285 | 274.3 | 295.1 | 276.7 | 617.7 | 45.7 | 20 | 78 | 3.9 | 295 | 2.6 | 940 | 830 | 891.2 | 916.2 | 871.7 | 769.7 | 730.9 | 811.5 | 818.8 | 782.7 | 162.1 | 295.2 | 78.5 | 305.6 | 282.3 | 111.7 | 223.7 | 259 | 157.1
700 | 510 | 567.9 | 227.16 | 265.537 | 284.3 | 274.5 | 295.4 | 275.6 | 632.1 | 45.8 | 20 | 78.1 | 3.9 | 296.3 | 2.5 | 939.5 | 829.2 | 889.3 | 913.4 | 873.9 | 770.2 | 732.3 | 817.3 | 818.7 | 784 | 162.5 | 295.2 | 78.6 | 305.1 | 282.5 | 112 | 224.1 | 259.5 | 157.5
701 | 511 | 568 | 227.2 | 265.5837 | 283.9 | 273.6 | 295.1 | 275.5 | 631.5 | 45.9 | 20 | 78.2 | 3.8 | 298.3 | 2.6 | 939.2 | 830.1 | 889.3 | 914.4 | 875.8 | 771.1 | 730.1 | 818.4 | 818.4 | 784.3 | 162.8 | 295.2 | 78.8 | 304.5 | 282.4 | 112.3 | 224.3 | 260 | 157.8
702 | 512 | 568.2 | 227.28 | 265.6772 | 284.9 | 273.2 | 294.4 | 275.8 | 647.8 | 45.9 | 20 | 78.4 | 4.4 | 304.6 | 2.5 | 939.4 | 829.4 | 889.6 | 915.8 | 873.2 | 772.4 | 729.5 | 817.3 | 819.3 | 781.9 | 163.1 | 295.4 | 79 | 304.2 | 282.2 | 112.5 | 224.6 | 260.5 | 158.1
703 | 513 | 568 | 227.2 | 265.5837 | 285.7 | 273.3 | 294.6 | 276.6 | 665.9 | 45.9 | 20 | 78.4 | 4.2 | 311.8 | 3.2 | 939.9 | 828.8 | 888.8 | 918.2 | 865.5 | 773.6 | 731.3 | 816.9 | 820.8 | 781.3 | 163.5 | 295.5 | 79.2 | 304.7 | 281.9 | 112.8 | 224.8 | 261.1 | 158.5
704 | 514 | 567.5 | 227 | 265.3499 | 286 | 273.5 | 295 | 277.3 | 676.5 | 46 | 20 | 78.5 | 4.2 | 313.2 | 3.5 | 940.5 | 829.6 | 887.8 | 917.2 | 856.6 | 775.1 | 728.7 | 815.4 | 823 | 778.8 | 163.8 | 295.6 | 79.3 | 305.1 | 282.1 | 113 | 225.2 | 261.6 | 158.8
705 | 515 | 567.3 | 226.92 | 265.2564 | 287.2 | 274 | 295.3 | 278.6 | 685.8 | 46 | 20 | 78.6 | 4.3 | 321.8 | 3 | 941.3 | 831.4 | 887.6 | 914 | 843.9 | 776.9 | 727 | 813.6 | 825.9 | 775.2 | 164.2 | 296 | 79.5 | 306 | 282.8 | 113.3 | 225.5 | 262.2 | 159.2
706 | 516 | 567 | 226.8 | 265.1161 | 289.1 | 274.7 | 297.1 | 280.4 | 691.5 | 46 | 20 | 78.8 | 4.2 | 334.9 | 2.4 | 941.6 | 832.9 | 888.9 | 916.6 | 847.4 | 778.3 | 726.8 | 816 | 829 | 774.3 | 164.5 | 296.9 | 79.7 | 306.5 | 283.4 | 113.6 | 225.9 | 262.8 | 159.5
707 | 517 | 568.4 | 227.36 | 265.7707 | 290.3 | 275.9 | 297.7 | 281.7 | 682.1 | 46.1 | 20 | 78.9 | 4.2 | 324.1 | 1.9 | 942.1 | 831.9 | 891.3 | 917.9 | 849.1 | 779.2 | 727.2 | 811.7 | 830 | 774.2 | 164.9 | 297.7 | 79.9 | 307.5 | 284 | 113.8 | 226.3 | 263.5 | 159.9
708 | 518 | 569.2 | 227.68 | 266.1448 | 291.3 | 276.7 | 298 | 282.5 | 670.1 | 46.1 | 20 | 79 | 3.8 | 284 | 2 | 942.7 | 831.9 | 893.1 | 919.5 | 848.5 | 779.9 | 727 | 814.2 | 829.6 | 773 | 165.2 | 299 | 80 | 308.1 | 284.7 | 114.1 | 226.8 | 264 | 160.3
709 | 519 | 567.3 | 226.92 | 265.2564 | 292.2 | 276.8 | 298.6 | 283.2 | 666.1 | 46.2 | 20 | 79.2 | 3.8 | 253.3 | 1.9 | 943.1 | 830 | 893.7 | 919.1 | 845.3 | 780.1 | 725.1 | 814.2 | 829.4 | 772.3 | 165.6 | 299.8 | 80.2 | 308.6 | 285.3 | 114.4 | 227.1 | 264.5 | 160.7
710 | 520 | 567.7 | 227.08 | 265.4434 | 293.2 | 276.8 | 298.7 | 283.5 | 684.1 | 46.2 | 20 | 79.4 | 3.6 | 233.9 | 1.8 | 944.4 | 829.7 | 892.7 | 914.3 | 839.6 | 780.8 | 721.9 | 810.3 | 829.6 | 769.3 | 165.9 | 300.1 | 80.4 | 309.1 | 285.7 | 114.6 | 227.4 | 265.1 | 161
711 | 521 | 568 | 227.2 | 265.5837 | 294.5 | 277.3 | 298.9 | 283.9 | 703.6 | 46.3 | 20 | 79.5 | 3.4 | 222.4 | 1.8 | 945 | 829.4 | 892.4 | 913.4 | 839.5 | 781.6 | 722.4 | 809 | 831.2 | 769 | 166.3 | 300.4 | 80.6 | 309.8 | 285.8 | 114.9 | 227.8 | 265.7 | 161.4
712 | 522 | 568.4 | 227.36 | 265.7707 | 295.7 | 277.4 | 299.7 | 284.5 | 711.4 | 46.3 | 20 | 79.7 | 3.9 | 223.7 | 2.2 | 944.5 | 829.1 | 892.6 | 913.5 | 843.6 | 782.2 | 727.4 | 812.1 | 832.6 | 770.1 | 166.6 | 300.8 | 80.8 | 310.8 | 286.3 | 115.1 | 228.2 | 266.3 | 161.7
713 | 523 | 568.6 | 227.44 | 265.8643 | 296.5 | 278.2 | 300.4 | 285.4 | 714.2 | 46.4 | 20 | 79.8 | 3.5 | 234.4 | 2.7 | 943.5 | 830.7 | 893.2 | 912.7 | 845.6 | 782.8 | 725.7 | 809.2 | 833.4 | 768 | 167 | 301.3 | 80.9 | 311.6 | 286.8 | 115.4 | 228.6 | 267 | 162.1
714 | 524 | 568.1 | 227.24 | 265.6305 | 296.6 | 279 | 300 | 286.1 | 711.2 | 46.4 | 20 | 79.8 | 4 | 239.2 | 3.2 | 943.3 | 829.1 | 894.9 | 914.1 | 846.2 | 783.2 | 728.4 | 808.7 | 833.9 | 768.7 | 167.3 | 301.7 | 81.1 | 312.7 | 287.1 | 115.7 | 229 | 267.6 | 162.5
715 | 525 | 568.7 | 227.48 | 265.911 | 297.1 | 279.5 | 299.7 | 286.6 | 708.8 | 46.5 | 20 | 79.8 | 4 | 233.9 | 3.2 | 942.3 | 824.9 | 896.2 | 912.2 | 842.9 | 783 | 729.7 | 808 | 832.6 | 768.9 | 167.7 | 302 | 81.3 | 313.5 | 288.1 | 116 | 229.5 | 268.2 | 162.9
716 | 526 | 567.5 | 227 | 265.3499 | 298.2 | 279.9 | 299.1 | 286.8 | 708.1 | 46.6 | 20 | 79.8 | 4.1 | 214.7 | 3.5 | 942.2 | 824 | 895.9 | 914.9 | 840.6 | 783.3 | 727.5 | 807.5 | 833.6 | 766.6 | 168.1 | 302.5 | 81.5 | 314.5 | 289 | 116.2 | 230 | 268.7 | 163.3
717 | 527 | 567.8 | 227.12 | 265.4902 | 299 | 280.3 | 300.1 | 287.4 | 685.4 | 46.6 | 20 | 79.9 | 3.9 | 230.7 | 3.9 | 942.4 | 826 | 896.1 | 914.9 | 846 | 783.7 | 731.3 | 810 | 833.4 | 769.2 | 168.4 | 303 | 81.6 | 314.8 | 290.1 | 116.5 | 230.5 | 269.3 | 163.7
718 | 528 | 567.8 | 227.12 | 265.4902 | 299 | 280.7 | 301.1 | 287.5 | 679 | 46.7 | 20 | 80 | 3.9 | 229.1 | 4.6 | 942.9 | 826.5 | 895.9 | 914 | 842 | 783.5 | 730 | 808.4 | 831.6 | 767.6 | 168.8 | 303.4 | 81.8 | 314.7 | 291.1 | 116.8 | 230.9 | 269.9 | 164
719 | 529 | 567.7 | 227.08 | 265.4434 | 299.8 | 280.9 | 301.4 | 287.1 | 675.4 | 46.7 | 20 | 80 | 4.4 | 225.3 | 5.2 | 943.5 | 828.1 | 895.6 | 912.4 | 836.3 | 784.4 | 726.2 | 806.1 | 832.1 | 766.4 | 169.2 | 303.7 | 82 | 314.6 | 291.3 | 117 | 231.3 | 270.4 | 164.4
720 | 530 | 567.4 | 226.96 | 265.3032 | 300.4 | 280.4 | 302.5 | 287.7 | 669.9 | 46.7 | 20 | 80 | 4.1 | 234.6 | 5.2 | 943.5 | 826.6 | 895.8 | 912 | 835.1 | 785.1 | 726.1 | 806.9 | 832.5 | 766.2 | 169.6 | 303.9 | 82.2 | 314.7 | 291.7 | 117.3 | 231.6 | 270.9 | 164.7
721 | 531 | 566.4 | 226.56 | 264.8356 | 300.2 | 280.9 | 303.2 | 288.1 | 670.6 | 46.8 | 20 | 80.1 | 4 | 241.4 | 5.3 | 943.8 | 825.5 | 896.5 | 913.4 | 830.1 | 785.9 | 723.7 | 806.4 | 834.2 | 764.6 | 170 | 304.8 | 82.4 | 314.8 | 291.8 | 117.6 | 231.9 | 271.5 | 165.1
722 | 532 | 566.2 | 226.48 | 264.7421 | 299.9 | 281.1 | 303.6 | 288.7 | 676 | 46.8 | 19.9 | 80.2 | 3.9 | 218.8 | 5.4 | 944.3 | 824.7 | 896 | 912.8 | 824.9 | 786.8 | 721.3 | 805.8 | 834.9 | 763.2 | 170.4 | 305 | 82.5 | 315.2 | 291.7 | 117.9 | 232.2 | 272 | 165.5
723 | 533 | 567.3 | 226.92 | 265.2564 | 300.3 | 281.5 | 304.4 | 289.2 | 679 | 46.8 | 19.9 | 80.3 | 4.4 | 204.2 | 5.1 | 944.5 | 823.3 | 896.1 | 912.5 | 819.7 | 787.6 | 718.8 | 804.7 | 835.3 | 761.2 | 170.8 | 305.2 | 82.7 | 315.7 | 292.2 | 118.1 | 232.5 | 272.6 | 165.8
724 | 534 | 568 | 227.2 | 265.5837 | 300.3 | 282.6 | 305.4 | 290 | 676.8 | 46.9 | 19.9 | 80.4 | 4.4 | 208.2 | 4.8 | 944.6 | 820.6 | 895.5 | 912.8 | 820.2 | 788 | 719.4 | 804.3 | 834.2 | 760.1 | 171.2 | 305.6 | 82.9 | 316.1 | 292.8 | 118.4 | 232.9 | 273.2 | 166.3
725 | 535 | 567.3 | 226.92 | 265.2564 | 300 | 283.2 | 305.6 | 290.6 | 679.1 | 47 | 19.9 | 80.6 | 4.3 | 242.5 | 4.3 | 944.7 | 820.5 | 895.8 | 913.4 | 821.5 | 788.2 | 719.3 | 800.9 | 832.3 | 759.5 | 171.6 | 306 | 83.1 | 316.8 | 293.5 | 118.7 | 233.3 | 273.9 | 166.6
726 | 536 | 568.2 | 227.28 | 265.6772 | 300.2 | 283.8 | 306 | 290.7 | 688.4 | 47 | 19.9 | 80.6 | 4.6 | 253.9 | 4.2 | 945.5 | 823.2 | 895 | 908.5 | 813.2 | 788.5 | 716.2 | 797.8 | 831.7 | 757.5 | 172 | 306 | 83.2 | 317.4 | 293.4 | 119 | 233.7 | 274.5 | 167
727 | 537 | 568.2 | 227.28 | 265.6772 | 300.7 | 284.6 | 307 | 291.1 | 696 | 47 | 19.9 | 80.7 | 4.9 | 218.9 | 4.5 | 945.6 | 822.5 | 895.9 | 907.7 | 807.6 | 789.4 | 714.4 | 795.8 | 832.6 | 756.3 | 172.4 | 306.4 | 83.4 | 318.2 | 293.4 | 119.3 | 234 | 275.1 | 167.4
728 | 538 | 567.5 | 227 | 265.3499 | 301.3 | 285.5 | 307.5 | 292 | 705.9 | 47.1 | 19.9 | 80.8 | 4.7 | 220.9 | 4.6 | 945.7 | 823.8 | 896.3 | 905.1 | 810.4 | 789.8 | 714.4 | 796.5 | 832.9 | 756.8 | 172.8 | 306.7 | 83.6 | 319 | 293.6 | 119.6 | 234.4 | 275.8 | 167.8
729 | 539 | 568.1 | 227.24 | 265.6305 | 301.6 | 286.1 | 306.1 | 292.5 | 702.9 | 47.2 | 19.9 | 80.8 | 4.7 | 218.6 | 4.9 | 945.5 | 826.2 | 896.7 | 905.1 | 818.9 | 789.8 | 714.1 | 798.3 | 833.2 | 757.7 | 173.2 | 306.8 | 83.8 | 319.7 | 293.8 | 119.9 | 234.8 | 276.4 | 168.2
730 | 540 | 567.1 | 226.84 | 265.1629 | 301.5 | 286 | 305.8 | 292.6 | 686.4 | 47.2 | 19.9 | 80.8 | 4.5 | 204.4 | 4.8 | 945.5 | 829.4 | 898.4 | 906.9 | 827.6 | 789.7 | 715.2 | 798.2 | 832.8 | 758 | 173.6 | 307 | 83.9 | 320.2 | 294.4 | 120.1 | 235.2 | 277 | 168.6
731 | 541 | 568 | 227.2 | 265.5837 | 302 | 285.6 | 306.1 | 292.3 | 672.2 | 47.3 | 19.9 | 80.9 | 4.6 | 205.5 | 4.5 | 944.7 | 829.2 | 899.9 | 910.7 | 835.5 | 789.2 | 716.5 | 792.9 | 831.2 | 758.3 | 173.9 | 306.8 | 84.1 | 320.3 | 294.4 | 120.4 | 235.5 | 277.5 | 169
732 | 542 | 567.3 | 226.92 | 265.2564 | 302.1 | 285.2 | 306.7 | 292.4 | 642.1 | 47.4 | 19.9 | 81 | 4.6 | 208.4 | 4.5 | 944.2 | 827.9 | 900.4 | 914.1 | 840.9 | 788.7 | 719.8 | 788.1 | 829.1 | 759.3 | 174.3 | 306.5 | 84.3 | 319.6 | 294.2 | 120.7 | 236 | 278 | 169.3
733 | 543 | 567.1 | 226.84 | 265.1629 | 301.8 | 285.4 | 306.7 | 291.8 | 632.7 | 47.4 | 19.9 | 81.1 | 4.1 | 220.7 | 5.2 | 943.9 | 828 | 899.5 | 914.4 | 844.8 | 787.8 | 722.2 | 792.5 | 824.5 | 760.3 | 174.7 | 306.1 | 84.5 | 319.3 | 294 | 121 | 236.3 | 278.4 | 169.6
734 | 544 | 566.3 | 226.52 | 264.7888 | 301.5 | 286.1 | 305.4 | 290.1 | 631.3 | 47.5 | 19.9 | 81.2 | 4.3 | 236.1 | 6.3 | 943.5 | 827.9 | 899.3 | 913.8 | 853.7 | 787.7 | 726.2 | 795.1 | 822.8 | 761.8 | 175.1 | 305.6 | 84.7 | 318.8 | 293.7 | 121.3 | 236.6 | 278.9 | 170
735 | 545 | 567.4 | 226.96 | 265.3032 | 301.2 | 286.4 | 304.9 | 288.6 | 639.9 | 47.5 | 19.9 | 81.4 | 4.1 | 226.5 | 6.9 | 943.2 | 829.5 | 899.7 | 916.8 | 863.7 | 787.1 | 725.3 | 797.3 | 820.7 | 762.2 | 175.4 | 305.1 | 84.8 | 317.8 | 293.2 | 121.6 | 236.8 | 279.4 | 170.3
736 | 546 | 567.4 | 226.96 | 265.3032 | 300.6 | 287.3 | 304.2 | 287.8 | 639.7 | 47.6 | 19.9 | 81.5 | 4.6 | 199 | 7.2 | 943.3 | 829.1 | 900 | 917.4 | 866.7 | 786.9 | 720 | 795.5 | 818.8 | 761.7 | 175.8 | 304.9 | 85 | 317 | 292.8 | 121.9 | 237.1 | 279.9 | 170.6
737 | 547 | 567.8 | 227.12 | 265.4902 | 299.7 | 288.3 | 304 | 286.6 | 641.4 | 47.6 | 19.9 | 81.5 | 4.4 | 222.8 | 7.1 | 943.9 | 830.7 | 898.9 | 914.4 | 861 | 787.4 | 718.7 | 799.9 | 820 | 761.8 | 176.2 | 304.7 | 85.2 | 316.1 | 292.3 | 122.3 | 237.3 | 280.3 | 170.9
738 | 548 | 567.4 | 226.96 | 265.3032 | 299.7 | 288.7 | 303.8 | 285.1 | 635.2 | 47.7 | 19.9 | 81.6 | 4.2 | 203.5 | 6.7 | 944.4 | 832 | 899.1 | 913.1 | 859.5 | 788.1 | 717.4 | 799 | 822.7 | 761.9 | 176.5 | 304.9 | 85.4 | 315.1 | 292 | 122.6 | 237.4 | 280.8 | 171.2
739 | 549 | 568.2 | 227.28 | 265.6772 | 299.1 | 288.4 | 302.7 | 284.9 | 621.9 | 47.7 | 19.9 | 81.7 | 4.2 | 209.7 | 6.5 | 944.3 | 828.9 | 899.2 | 913.9 | 859 | 788.9 | 717.8 | 800.5 | 826.5 | 762.4 | 176.9 | 305.2 | 85.5 | 314.6 | 291.7 | 122.9 | 237.6 | 281.2 | 171.5
740 | 550 | 567.8 | 227.12 | 265.4902 | 298.8 | 288.2 | 302.5 | 285.1 | 628.1 | 47.8 | 19.9 | 81.8 | 3.7 | 245.1 | 6 | 944 | 827.1 | 898.8 | 913.7 | 861.1 | 788.9 | 720.1 | 801.9 | 827 | 763.4 | 177.2 | 305.1 | 85.7 | 314.1 | 291.5 | 123.3 | 237.8 | 281.7 | 171.9
741 | 551 | 568.5 | 227.4 | 265.8175 | 298.7 | 288 | 301.5 | 284.3 | 635.6 | 47.9 | 19.9 | 81.9 | 4.1 | 254.1 | 6.3 | 943.7 | 826.8 | 899.3 | 914.1 | 861.1 | 788.8 | 720.8 | 803.1 | 825.1 | 764 | 177.6 | 305 | 85.9 | 313.5 | 291.4 | 123.7 | 237.9 | 282.1 | 172.2
742 | 552 | 567.9 | 227.16 | 265.537 | 298.6 | 287.4 | 300.2 | 283.3 | 640.2 | 47.9 | 19.9 | 82 | 4.1 | 211.6 | 6.7 | 942.7 | 824.2 | 899.7 | 915.1 | 861.9 | 788.7 | 725.3 | 802.7 | 823.8 | 764.3 | 177.9 | 304.6 | 86.1 | 313 | 291 | 124 | 238.1 | 282.5 | 172.5
743 | 553 | 567.8 | 227.12 | 265.4902 | 298.5 | 285.8 | 300.1 | 283.2 | 665.9 | 48 | 19.9 | 82.1 | 4.2 | 220.2 | 5.3 | 942 | 822.4 | 899 | 916.6 | 859.2 | 788.7 | 725.7 | 804.7 | 822.3 | 763.5 | 178.2 | 304.3 | 86.3 | 312.7 | 290.5 | 124.4 | 238.3 | 282.9 | 172.8
744 | 554 | 567.5 | 227 | 265.3499 | 299.2 | 285.1 | 300.7 | 283.6 | 677.1 | 48.1 | 19.9 | 82.2 | 4.6 | 202.2 | 4.7 | 941.9 | 824.1 | 899.2 | 917 | 856.9 | 788.6 | 726.7 | 805.9 | 820.5 | 763.1 | 178.6 | 304.1 | 86.4 | 312.4 | 290.3 | 124.7 | 238.5 | 283.4 | 173.1
745 | 555 | 567.7 | 227.08 | 265.4434 | 300.1 | 285.4 | 301.1 | 283.6 | 679.3 | 48.1 | 19.9 | 82.3 | 4.6 | 199.1 | 4.2 | 941.7 | 821.6 | 899.9 | 917.1 | 851.7 | 789 | 721.9 | 806.6 | 819.9 | 762 | 178.9 | 304.1 | 86.6 | 312.2 | 290.2 | 125.1 | 238.7 | 283.9 | 173.5
746 | 556 | 567.4 | 226.96 | 265.3032 | 300.6 | 285.5 | 301.1 | 283.6 | 682.1 | 48.2 | 19.9 | 82.4 | 4.5 | 208.7 | 3.4 | 941.4 | 822.5 | 898.1 | 912.2 | 840 | 789.9 | 713.1 | 798.5 | 820.9 | 760.4 | 179.2 | 304.4 | 86.8 | 312.1 | 290.3 | 125.5 | 238.9 | 284.4 | 173.8
747 | 557 | 567.9 | 227.16 | 265.537 | 301.3 | 285.8 | 301.6 | 284.2 | 667.3 | 48.2 | 19.9 | 82.5 | 4.4 | 214 | 3.5 | 941.1 | 825.3 | 896.8 | 905.2 | 832.2 | 791.4 | 703.4 | 789.8 | 823.6 | 758.4 | 179.6 | 304.8 | 87 | 312 | 290.4 | 125.9 | 239.1 | 284.9 | 174.2
748 | 558 | 566.2 | 226.48 | 264.7421 | 301.6 | 286.3 | 302.3 | 285.3 | 667.2 | 48.3 | 19.9 | 82.6 | 4.2 | 229.7 | 3.4 | 940.5 | 825.6 | 897.4 | 904.3 | 832.6 | 792.4 | 706.1 | 794.3 | 825.8 | 758.4 | 179.9 | 305.2 | 87.1 | 312.4 | 290.8 | 126.3 | 239.4 | 285.4 | 174.5
749 | 559 | 567.6 | 227.04 | 265.3967 | 302.1 | 285.9 | 303.2 | 286.3 | 664.3 | 48.4 | 19.9 | 82.6 | 4.3 | 246.3 | 3.5 | 939.8 | 823.9 | 898.6 | 908.4 | 832.5 | 793.1 | 704.1 | 797.7 | 826.5 | 757.1 | 180.2 | 305.3 | 87.3 | 313.2 | 291.5 | 126.6 | 239.7 | 285.8 | 174.8
750 | 560 | 546.3 | 218.52 | 255.4373 | 299.5 | 286.4 | 305.8 | 287.7 | 660 | 48.7 | 19.9 | 82.6 | 4.1 | 240.6 | 3.4 | 939 | 824.3 | 897.2 | 909.8 | 834.5 | 793.5 | 705 | 796.9 | 825.9 | 756.7 | 180.5 | 305.4 | 87.5 | 314.5 | 292.1 | 127.1 | 239.8 | 286.4 | 173.1
751 | 561 | 496.5 | 198.6 | 232.152 | 285 | 292.1 | 316.7 | 293.5 | 659 | 50 | 19.8 | 82.8 | 4.4 | 226.6 | 3.2 | 938.2 | 827.4 | 896.2 | 912.5 | 839 | 793.7 | 706.9 | 797.2 | 827 | 756.3 | 180.8 | 305.5 | 87.6 | 315.2 | 292.3 | 127.7 | 239.7 | 287.2 | 163.2
752 | 562 | 644.7 | 257.88 | 301.4469 | 304.1 | 285.7 | 304.7 | 288.5 | 650 | 48.5 | 19.9 | 82.7 | 4.4 | 204.6 | 3.1 | 937.9 | 830.1 | 896.2 | 911.5 | 845.1 | 794.6 | 708.4 | 797.3 | 827.5 | 756.6 | 181.2 | 305.6 | 87.9 | 315.8 | 292.3 | 127.8 | 240.5 | 287.2 | 175.9
753 | 563 | 562.8 | 225.12 | 263.1523 | 297.2 | 289.1 | 308.3 | 291.5 | 630 | 49.1 | 19.8 | 82.8 | 4.7 | 209.9 | 2.9 | 937.4 | 831.9 | 896.6 | 912.6 | 852.9 | 794.5 | 709.9 | 796 | 827.2 | 758 | 181.5 | 305.4 | 88 | 316.1 | 292.8 | 128.3 | 240.6 | 287.8 | 171.8
754 | 564 | 587.4 | 234.96 | 274.6547 | 294.3 | 290.8 | 310.3 | 292.3 | 610.6 | 49.4 | 19.8 | 82.8 | 4.8 | 224.5 | 3.4 | 937 | 833.6 | 897 | 914.3 | 859.8 | 794.3 | 714.1 | 796.5 | 825.2 | 760.7 | 181.8 | 305.7 | 88.2 | 316.1 | 293.5 | 128.7 | 241 | 288.3 | 170.6
755 | 565 | 639.9 | 255.96 | 299.2025 | 303 | 288.5 | 304.9 | 288.9 | 599.7 | 48.6 | 19.8 | 82.8 | 4.3 | 200.7 | 4.3 | 937.2 | 833.1 | 897.6 | 913.3 | 863.9 | 794.1 | 715.4 | 796.9 | 822.5 | 761.6 | 182.2 | 305.8 | 88.4 | 315.9 | 293.8 | 129 | 241.6 | 288.5 | 176.9
756 | 566 | 606.6 | 242.64 | 283.6322 | 302.8 | 288.9 | 303.7 | 287.9 | 599.4 | 48.7 | 19.8 | 82.8 | 4.4 | 207 | 4.8 | 936.9 | 832.2 | 895.9 | 909.3 | 865.4 | 794 | 716.6 | 798.4 | 821 | 763.4 | 182.5 | 305.8 | 88.6 | 315.6 | 293.6 | 129.4 | 241.9 | 288.9 | 177.2
757 | 567 | 586.4 | 234.56 | 274.1871 | 303 | 288.8 | 302.2 | 286.7 | 605.7 | 48.8 | 19.8 | 82.9 | 4 | 248.9 | 4.9 | 936.4 | 832.5 | 894.5 | 906.1 | 865.3 | 794.3 | 723.1 | 797.5 | 820.7 | 765.8 | 182.9 | 305.6 | 88.8 | 314.8 | 294.8 | 129.8 | 242.3 | 289.3 | 177.5
758 | 568 | 579.4 | 231.76 | 270.9141 | 303.7 | 287.9 | 302.1 | 286.5 | 601.3 | 48.9 | 19.8 | 83 | 3.8 | 264.9 | 5 | 936 | 838.5 | 893.1 | 907.2 | 868.9 | 794.4 | 723.9 | 793.4 | 820.2 | 768.6 | 183.2 | 305.5 | 88.9 | 314.4 | 295.2 | 130.3 | 242.8 | 289.7 | 177.8
759 | 569 | 577.3 | 230.92 | 269.9322 | 304.7 | 287 | 302.3 | 286.3 | 587.5 | 48.9 | 19.8 | 83 | 4.3 | 229.2 | 5.1 | 936.4 | 837.1 | 893.7 | 908.1 | 873.7 | 794.6 | 725 | 791.9 | 820.1 | 771.4 | 183.6 | 305.5 | 89.1 | 314 | 295 | 130.7 | 243.1 | 290.1 | 178.2
760 | 570 | 576.5 | 230.6 | 269.5581 | 305.2 | 286.6 | 302.1 | 286.4 | 582.1 | 49 | 19.8 | 83.1 | 4.4 | 229.9 | 4.8 | 936 | 838.8 | 891.9 | 908.1 | 873.9 | 793.8 | 724.4 | 787.5 | 818.7 | 773 | 183.9 | 305.3 | 89.3 | 313.4 | 295 | 131.2 | 243.3 | 290.4 | 178.5
761 | 571 | 576.2 | 230.48 | 269.4178 | 305.1 | 285.7 | 301.7 | 285.9 | 572.7 | 49.1 | 19.8 | 83.2 | 4.2 | 255.7 | 4.6 | 936 | 838.8 | 891.8 | 907.6 | 878.5 | 793.6 | 728.2 | 787.8 | 818.9 | 775.5 | 184.3 | 304.8 | 89.5 | 312.8 | 294.8 | 131.7 | 243.5 | 290.8 | 178.6
762 | 572 | 579 | 231.6 | 270.7271 | 305.3 | 284.6 | 301.6 | 284.6 | 561.9 | 49.1 | 19.8 | 83.3 | 4.1 | 252.4 | 4.9 | 936.5 | 838.3 | 892.1 | 907.5 | 884 | 793.5 | 727.1 | 778.2 | 818.4 | 777 | 184.6 | 304.3 | 89.7 | 312.1 | 294.4 | 132.1 | 243.6 | 291.2 | 179.1
763 | 573 | 579.2 | 231.68 | 270.8206 | 305.6 | 283.1 | 301.8 | 284.2 | 548 | 49.1 | 19.8 | 83.3 | 3.9 | 244.6 | 5.3 | 935.9 | 838.3 | 892 | 907.8 | 891.1 | 792.9 | 728.1 | 776.9 | 818.8 | 778.9 | 184.9 | 303.8 | 89.8 | 311.7 | 294 | 132.6 | 243.8 | 291.6 | 179.4
764 | 574 | 578.1 | 231.24 | 270.3062 | 305.7 | 281.6 | 301.2 | 284 | 538.3 | 49.2 | 19.8 | 83.4 | 4.2 | 234.8 | 5 | 935.4 | 838.9 | 891 | 908.2 | 891.7 | 792.5 | 727 | 766.9 | 818.7 | 781.2 | 185.3 | 303.4 | 90 | 311 | 293.8 | 133 | 244 | 291.9 | 179.7
765 | 575 | 576.8 | 230.72 | 269.6984 | 305 | 280.4 | 300.5 | 283.1 | 534.6 | 49.2 | 19.8 | 83.5 | 4.4 | 227.6 | 4.5 | 935.2 | 838.1 | 890.3 | 907.7 | 897.5 | 792.2 | 726.8 | 763.8 | 818.3 | 782.9 | 185.6 | 303.3 | 90.2 | 310.8 | 293.6 | 133.5 | 244.2 | 292.3 | 180
766 | 576 | 575.7 | 230.28 | 269.1841 | 304.1 | 279.4 | 299.9 | 281.6 | 533.8 | 49.3 | 19.8 | 83.6 | 4.3 | 200.2 | 4.6 | 935.3 | 837.3 | 891.3 | 907.9 | 904.3 | 792.3 | 728.2 | 769.4 | 819 | 785.1 | 185.9 | 303.2 | 90.4 | 310.4 | 293.9 | 134 | 244.4 | 292.6 | 180.3
767 | 577 | 574.7 | 229.88 | 268.7165 | 303.3 | 278.6 | 299.5 | 280.7 | 539.8 | 49.3 | 19.8 | 83.6 | 3.9 | 191.4 | 4.7 | 935 | 838.2 | 892.1 | 908.5 | 905.8 | 792.3 | 729.8 | 772.7 | 819 | 787.4 | 186.3 | 302.9 | 90.6 | 310 | 294.9 | 134.4 | 244.9 | 293 | 180.6
768 | 578 | 574.1 | 229.64 | 268.4359 | 302.8 | 278.1 | 298.9 | 280.2 | 538.6 | 49.4 | 19.8 | 83.7 | 3.9 | 219.3 | 3.9 | 935.1 | 836.2 | 892.8 | 908.8 | 911.4 | 792.6 | 728.7 | 777.5 | 817.5 | 788.3 | 186.6 | 302.6 | 90.7 | 310 | 294.8 | 134.9 | 245.1 | 293.4 | 180.8
769 | 579 | 572 | 228.8 | 267.454 | 302.8 | 278 | 299.4 | 279.9 | 547.8 | 49.4 | 19.8 | 83.8 | 4.3 | 239.5 | 3.5 | 935.4 | 837.3 | 893.6 | 909.8 | 913.6 | 792.7 | 730 | 781.5 | 815.6 | 790 | 186.9 | 302.2 | 90.9 | 309.7 | 294.1 | 135.4 | 245.3 | 293.8 | 181.2
770 | 580 | 571.7 | 228.68 | 267.3137 | 302.7 | 277.6 | 299.2 | 280.6 | 552.5 | 49.4 | 19.8 | 83.8 | 4.3 | 218.1 | 3.6 | 935.4 | 838.5 | 894.2 | 909.4 | 911.5 | 793 | 730 | 784.8 | 813.6 | 790.5 | 187.2 | 301.8 | 91.1 | 309.3 | 293.3 | 135.9 | 245.4 | 294.2 | 181.4
771 | 581 | 572.8 | 229.12 | 267.8281 | 303.4 | 277.6 | 298.9 | 281.3 | 561.4 | 49.5 | 19.8 | 83.9 | 4.4 | 223.6 | 4 | 936.3 | 840.5 | 894.7 | 910.7 | 913 | 793.5 | 726.9 | 785.6 | 811.5 | 790.6 | 187.5 | 301.6 | 91.3 | 308.9 | 292.6 | 136.4 | 245.5 | 294.6 | 181.7
772 | 582 | 572.5 | 229 | 267.6878 | 304.1 | 277.5 | 298.7 | 281.2 | 588.6 | 49.6 | 19.8 | 84 | 4.2 | 233.5 | 3.8 | 937.2 | 841.1 | 895.5 | 909.1 | 907.4 | 794.3 | 724 | 787.4 | 810.5 | 789.6 | 187.8 | 301.4 | 91.5 | 308.7 | 292.4 | 136.8 | 245.7 | 295 | 182
773 | 583 | 571.2 | 228.48 | 267.08 | 304.9 | 277.5 | 299.6 | 281.1 | 607 | 49.6 | 19.8 | 84 | 4.2 | 237.3 | 3.3 | 936.8 | 838.3 | 896 | 909 | 902.7 | 794.9 | 725.3 | 791.3 | 810.3 | 791.1 | 188.1 | 301.1 | 91.7 | 308.8 | 292.6 | 137.3 | 246 | 295.4 | 182.3
774 | 584 | 568.5 | 227.4 | 265.8175 | 305.4 | 277.4 | 300.6 | 281.7 | 603.4 | 49.7 | 19.8 | 84.2 | 4.1 | 241.9 | 2.9 | 936.2 | 837.4 | 895 | 909.5 | 905.2 | 795.2 | 728.6 | 790.7 | 809.5 | 793.1 | 188.4 | 301.1 | 91.9 | 308.8 | 293 | 137.8 | 246.3 | 295.8 | 182.7
775 | 585 | 567.8 | 227.12 | 265.4902 | 305.4 | 277.5 | 301.1 | 282.1 | 606.8 | 49.7 | 19.8 | 84.3 | 4.4 | 248.8 | 3.1 | 935.9 | 842.7 | 894 | 911.3 | 905.4 | 795.7 | 727 | 794.4 | 808 | 792.7 | 188.7 | 301.4 | 92.1 | 308.8 | 293.2 | 138.3 | 246.5 | 296.2 | 183
776 | 586 | 568.6 | 227.44 | 265.8643 | 305.7 | 277.3 | 301.5 | 282.6 | 611.5 | 49.8 | 19.8 | 84.3 | 4 | 242.2 | 3.7 | 936.2 | 843.1 | 894 | 910.9 | 898.6 | 796.6 | 723.5 | 792.1 | 806 | 789.9 | 189 | 301.6 | 92.3 | 308.8 | 293.6 | 138.8 | 246.6 | 296.6 | 183.3
777 | 587 | 567.5 | 227 | 265.3499 | 306.1 | 277.6 | 302.3 | 283.2 | 621.1 | 49.8 | 19.8 | 84.3 | 3.8 | 213.6 | 3.7 | 936.7 | 846.2 | 893.5 | 909.2 | 896.3 | 797.7 | 718.2 | 792.5 | 805.6 | 789.2 | 189.2 | 302 | 92.5 | 308.9 | 293.4 | 139.3 | 246.8 | 296.9 | 183.6
778 | 588 | 567.7 | 227.08 | 265.4434 | 306.5 | 277.8 | 303.8 | 283.6 | 614.1 | 49.8 | 19.8 | 84.2 | 4.3 | 206 | 4.3 | 936.5 | 849.2 | 893.2 | 909.1 | 894.8 | 798.2 | 714.1 | 790.4 | 805.8 | 788.6 | 189.5 | 302.4 | 92.7 | 309 | 293.1 | 139.8 | 247 | 297.3 | 183.9
779 | 589 | 568.6 | 227.44 | 265.8643 | 307.3 | 278.5 | 304.9 | 283.6 | 612.8 | 49.8 | 19.8 | 84.2 | 4 | 206.1 | 5.1 | 936.4 | 852.5 | 891.1 | 906 | 890.4 | 799 | 709.2 | 788.7 | 805.4 | 785.8 | 189.8 | 302.7 | 92.9 | 308.9 | 292.8 | 140.2 | 247.2 | 297.6 | 184.2
780 | 590 | 569.3 | 227.72 | 266.1916 | 308.7 | 279 | 304.6 | 283.8 | 611.7 | 49.8 | 19.8 | 84.3 | 4.2 | 225.5 | 4.8 | 936.6 | 854.2 | 890 | 903.4 | 883.9 | 799.9 | 704.1 | 781.6 | 805.1 | 783 | 190.1 | 302.9 | 93.1 | 308.9 | 292.6 | 140.7 | 247.4 | 298 | 184.5
781 | 591 | 569.5 | 227.8 | 266.2851 | 309.5 | 279.2 | 304.8 | 284.4 | 612.1 | 49.8 | 19.8 | 84.4 | 4.5 | 252.2 | 4.6 | 936.5 | 856 | 888.7 | 899.2 | 876.7 | 800.6 | 698.8 | 776.9 | 805.5 | 779 | 190.4 | 303.2 | 93.3 | 309.5 | 292 | 141.2 | 247.6 | 298.4 | 184.8
782 | 592 | 569.3 | 227.72 | 266.1916 | 310.4 | 279.2 | 305.8 | 284.4 | 611.9 | 49.8 | 19.8 | 84.6 | 4.9 | 204.4 | 4.4 | 936.9 | 860 | 887.2 | 897.4 | 868 | 801.4 | 694 | 773.5 | 806.2 | 775.3 | 190.7 | 303.5 | 93.5 | 310.5 | 292.3 | 141.7 | 247.7 | 298.7 | 185.1
783 | 593 | 569.2 | 227.68 | 266.1448 | 310.9 | 279.5 | 306.4 | 285.6 | 610.7 | 49.9 | 19.8 | 84.7 | 4.8 | 188 | 4.9 | 936.7 | 861.1 | 886.1 | 895.9 | 866.2 | 802.1 | 691.5 | 773.6 | 807.2 | 773.1 | 191 | 303.8 | 93.7 | 311.3 | 292.1 | 142.2 | 247.8 | 299 | 185.4
784 | 594 | 569.4 | 227.76 | 266.2383 | 310.9 | 280.2 | 308.4 | 286.6 | 622.1 | 49.9 | 19.8 | 84.9 | 5.1 | 212.5 | 4.8 | 936.4 | 860.2 | 885.4 | 897.1 | 867.3 | 802.5 | 693.5 | 775.7 | 808.5 | 772.3 | 191.3 | 304.5 | 93.9 | 312.3 | 292.3 | 142.7 | 248 | 299.4 | 185.7
785 | 595 | 568.2 | 227.28 | 265.6772 | 310.5 | 280.8 | 310.5 | 287 | 634.3 | 49.9 | 19.8 | 85 | 4.5 | 230.4 | 3.9 | 936.2 | 861.2 | 882.3 | 893.6 | 864.9 | 802.7 | 694.2 | 779.9 | 809.1 | 771.6 | 191.6 | 305.2 | 94.1 | 313.7 | 292.6 | 143.2 | 248.2 | 299.8 | 186.1
786 | 596 | 567.2 | 226.88 | 265.2096 | 310.7 | 281.7 | 312 | 288.2 | 632.3 | 49.9 | 19.8 | 85.1 | 4.4 | 228.8 | 3.3 | 936.5 | 863.8 | 880.7 | 889.4 | 859.2 | 803.1 | 690.4 | 782.4 | 808.6 | 768 | 191.9 | 305.9 | 94.3 | 315 | 293.3 | 143.7 | 248.4 | 300.1 | 186.4
787 | 597 | 567.4 | 226.96 | 265.3032 | 311.6 | 281.8 | 312.4 | 289.3 | 624 | 50 | 19.8 | 85.2 | 4.9 | 227.7 | 3.4 | 936.5 | 862.2 | 880 | 890.2 | 858.8 | 803.2 | 691 | 785.1 | 808.2 | 766.8 | 192.2 | 306.2 | 94.5 | 316.2 | 293.2 | 144.2 | 248.7 | 300.5 | 186.8
788 | 598 | 566.9 | 226.76 | 265.0694 | 312.2 | 282.4 | 312.4 | 290.4 | 625 | 50 | 19.8 | 85.4 | 5.4 | 228.5 | 3.7 | 937.4 | 861.6 | 879.8 | 890.9 | 858 | 803.2 | 690.5 | 785 | 806.9 | 766.5 | 192.5 | 306.8 | 94.7 | 316.9 | 293.3 | 144.7 | 249 | 300.9 | 187.1
789 | 599 | 568.9 | 227.56 | 266.0045 | 312.9 | 283.5 | 313.4 | 290.4 | 625 | 50.1 | 19.8 | 85.5 | 5.6 | 218.2 | 3.6 | 937.5 | 863.4 | 878.9 | 892.2 | 858.7 | 803.6 | 691.5 | 785.7 | 806 | 765.6 | 192.8 | 307.3 | 95 | 317.6 | 293.6 | 145.2 | 249.3 | 301.2 | 187.4
790 | 600 | 568.8 | 227.52 | 265.9578 | 313.8 | 283.7 | 314 | 290 | 618.9 | 50.2 | 19.8 | 85.6 | 5.1 | 215.6 | 4 | 937 | 863.5 | 878.4 | 895.7 | 867.1 | 803.7 | 692.9 | 791.6 | 804.3 | 767.9 | 193.1 | 307.6 | 95.2 | 318.1 | 293.3 | 145.7 | 249.5 | 301.6 | 187.7
791 | 601 | 568.8 | 227.52 | 265.9578 | 314.6 | 283.5 | 314 | 290.1 | 613.9 | 50.3 | 19.8 | 85.6 | 5 | 245.6 | 4.1 | 936.3 | 858 | 879.5 | 898.5 | 872.9 | 803.5 | 698.1 | 794.2 | 802.2 | 769.2 | 193.4 | 307.9 | 95.4 | 318.3 | 293.4 | 146.2 | 249.8 | 301.9 | 188.1
792 | 602 | 567 | 226.8 | 265.1161 | 314.6 | 283.6 | 312.6 | 289.9 | 627.2 | 50.4 | 19.8 | 85.7 | 4.9 | 260.3 | 4 | 935.5 | 858.2 | 880.2 | 901.8 | 871.5 | 803.3 | 701.9 | 798.4 | 799.7 | 769.6 | 193.8 | 308.3 | 95.6 | 318.8 | 292.7 | 146.7 | 250 | 302.2 | 188.3
793 | 603 | 566.9 | 226.76 | 265.0694 | 314.4 | 283.9 | 312.1 | 289.4 | 630.4 | 50.4 | 19.8 | 85.7 | 4.9 | 226.3 | 4.6 | 935.4 | 857.9 | 879.9 | 902.5 | 865.4 | 803.9 | 701.1 | 797.2 | 796.7 | 767.2 | 194.1 | 308.4 | 95.8 | 319 | 292 | 147.1 | 250.2 | 302.5 | 188.6
794 | 604 | 568.5 | 227.4 | 265.8175 | 314.1 | 284.3 | 312.9 | 289.2 | 614.5 | 50.4 | 19.8 | 85.9 | 4.6 | 234.2 | 5.8 | 935.8 | 857.1 | 880.3 | 902.6 | 861.6 | 804.4 | 697.8 | 791.6 | 793.6 | 765.2 | 194.4 | 308.4 | 96.1 | 318.9 | 291.1 | 147.6 | 250.4 | 302.9 | 189
795 | 605 | 568 | 227.2 | 265.5837 | 315.1 | 284.5 | 313.4 | 289.2 | 622.2 | 50.4 | 19.8 | 85.9 | 4.3 | 236.5 | 6.7 | 935.8 | 857.1 | 880.3 | 903.5 | 861.3 | 804.7 | 701.2 | 793.4 | 793.1 | 764.5 | 194.7 | 308.5 | 96.3 | 318.7 | 291.3 | 148.1 | 250.5 | 303.2 | 189.2
796 | 606 | 568.1 | 227.24 | 265.6305 | 315.9 | 284.3 | 312.9 | 289.4 | 640.2 | 50.4 | 19.8 | 86 | 3.8 | 246.3 | 6.8 | 935.7 | 860.2 | 879.8 | 899.3 | 854.6 | 805.3 | 701.8 | 795.5 | 792.9 | 762.8 | 195.1 | 308.5 | 96.5 | 319.3 | 291.7 | 148.6 | 250.8 | 303.6 | 189.6
797 | 607 | 567.8 | 227.12 | 265.4902 | 317.1 | 284.8 | 313.4 | 289.7 | 640.7 | 50.5 | 19.8 | 86 | 3.3 | 252.8 | 7.2 | 936 | 860.5 | 879.5 | 898.4 | 854.3 | 805.6 | 697.8 | 792.2 | 791 | 761.8 | 195.4 | 308.7 | 96.8 | 319.8 | 292 | 149.1 | 251 | 303.9 | 189.9
798 | 608 | 567.6 | 227.04 | 265.3967 | 318 | 285.7 | 314.4 | 290.2 | 639.6 | 50.5 | 19.7 | 86 | 3.6 | 228.9 | 7.2 | 934.9 | 860.3 | 878.1 | 901 | 858.6 | 805.8 | 701.6 | 796.6 | 789.9 | 763.3 | 195.7 | 308.7 | 97 | 320.8 | 292 | 149.5 | 251.3 | 304.3 | 190.2
799 | 609 | 567.4 | 226.96 | 265.3032 | 318.6 | 285.8 | 314.5 | 290.5 | 639.4 | 50.6 | 19.7 | 86 | 3.6 | 228.1 | 7.4 | 934 | 863.5 | 874.5 | 897.9 | 859.2 | 805.7 | 696.2 | 787.3 | 787.8 | 761.4 | 196.1 | 308.7 | 97.2 | 321.5 | 292.4 | 150 | 251.6 | 304.6 | 190.5
800 | 610 | 568.6 | 227.44 | 265.8643 | 318.8 | 285.7 | 314.1 | 290.9 | 611.7 | 50.6 | 19.7 | 86 | 3.8 | 231.8 | 7.7 | 932.8 | 864 | 871.7 | 893.2 | 858.1 | 805.8 | 689.5 | 777.7 | 783.9 | 758.4 | 196.4 | 308.9 | 97.5 | 322 | 292.8 | 150.5 | 251.8 | 305 | 190.9
801 | 611 | 570.2 | 228.08 | 266.6124 | 318.4 | 285.9 | 314.7 | 291.7 | 588.1 | 50.7 | 19.8 | 86.1 | 4 | 242.8 | 8.1 | 931.7 | 869.4 | 871.4 | 895 | 864.2 | 805.6 | 689.7 | 775.2 | 781.7 | 762 | 196.7 | 309.1 | 97.7 | 322.1 | 293.7 | 151 | 252.1 | 305.3 | 191.2
802 | 612 | 571 | 228.4 | 266.9864 | 318.3 | 285.2 | 314.5 | 291.9 | 580.7 | 50.7 | 19.7 | 86.1 | 4.7 | 255 | 7.5 | 931.2 | 869.6 | 870.1 | 894.8 | 870.3 | 805.4 | 693.2 | 779.7 | 780.9 | 762.8 | 197.1 | 309 | 98 | 322.3 | 294.5 | 151.4 | 252.3 | 305.5 | 191.5
803 | 613 | 569.7 | 227.88 | 266.3786 | 318.8 | 284.8 | 313.5 | 291.7 | 583.5 | 50.7 | 19.7 | 86.1 | 4.9 | 248.8 | 7 | 931.3 | 869.4 | 867.2 | 891.5 | 873.1 | 805.4 | 691.6 | 779.1 | 779.1 | 760.4 | 197.4 | 308.8 | 98.2 | 322.1 | 295.2 | 151.9 | 252.5 | 305.8 | 191.8
804 | 614 | 568.1 | 227.24 | 265.6305 | 319.2 | 284.3 | 313 | 291.4 | 575.9 | 50.7 | 19.7 | 86.1 | 4.2 | 240.1 | 7.1 | 930.5 | 870.6 | 865.2 | 888.9 | 875.4 | 805.7 | 686.2 | 768.8 | 776.2 | 759.4 | 197.7 | 308.8 | 98.4 | 321.9 | 295.5 | 152.4 | 252.6 | 306 | 192.1
805 | 615 | 567.3 | 226.92 | 265.2564 | 318.6 | 284.7 | 313 | 291.1 | 561.6 | 50.8 | 19.7 | 86 | 4.2 | 247.6 | 7.3 | 930.4 | 873.1 | 863.6 | 886.8 | 881.9 | 805.4 | 686.3 | 767.4 | 774.7 | 762.1 | 198.1 | 308.9 | 98.7 | 321.5 | 295.6 | 152.9 | 252.8 | 306.3 | 192.4
806 | 616 | 568.5 | 227.4 | 265.8175 | 317.7 | 285.2 | 312.8 | 290.9 | 553 | 50.8 | 19.7 | 85.9 | 3.9 | 244 | 7.5 | 930.6 | 874.6 | 864.8 | 888 | 884.2 | 805 | 684.8 | 763.7 | 773.8 | 763.3 | 198.4 | 308.7 | 99 | 321.2 | 295.6 | 153.4 | 253 | 306.5 | 192.7
807 | 617 | 568.7 | 227.48 | 265.911 | 316.4 | 285.1 | 312.7 | 290.4 | 549.2 | 50.8 | 19.7 | 85.9 | 3.8 | 249.4 | 7.2 | 930.4 | 876.5 | 863.7 | 888.2 | 887 | 804.5 | 683.1 | 758.8 | 772.3 | 764.4 | 198.7 | 308.5 | 99.2 | 320.7 | 295.6 | 153.9 | 253.2 | 306.8 | 193
808 | 618 | 568.4 | 227.36 | 265.7707 | 315.6 | 284.5 | 311.3 | 289.5 | 542.5 | 50.8 | 19.7 | 85.9 | 4.3 | 240.4 | 7.2 | 930.9 | 879.3 | 863.9 | 887.3 | 892.9 | 804 | 682.8 | 759 | 771.4 | 765.9 | 199.1 | 308.1 | 99.5 | 320.3 | 296.6 | 154.4 | 253.5 | 307.1 | 193.2
809 | 619 | 568.8 | 227.52 | 265.9578 | 314.8 | 284 | 310.6 | 288.6 | 544.8 | 50.8 | 19.7 | 86 | 4 | 243.1 | 7.1 | 930.8 | 884.7 | 864.4 | 889.2 | 897.8 | 803.5 | 684.2 | 760.7 | 770.9 | 765.9 | 199.4 | 307.8 | 99.7 | 319.4 | 296.6 | 154.9 | 253.8 | 307.3 | 193.5
810 | 620 | 567 | 226.8 | 265.1161 | 314.6 | 283 | 309.9 | 288.3 | 542.4 | 50.9 | 19.7 | 86.1 | 4.1 | 242.9 | 6.9 | 931.4 | 886.2 | 863.8 | 887.7 | 899.9 | 803.3 | 687.9 | 760.1 | 771 | 768.6 | 199.7 | 307.4 | 100 | 318.6 | 296.7 | 155.5 | 253.9 | 307.6 | 193.8
811 | 621 | 567.2 | 226.88 | 265.2096 | 315.2 | 282.9 | 308.2 | 287.4 | 543.1 | 51 | 19.7 | 86.2 | 3.8 | 237.1 | 6.7 | 931.6 | 885.1 | 864.6 | 891.6 | 898.4 | 802.7 | 695.3 | 766.5 | 771.8 | 769.9 | 200.1 | 307.1 | 100.3 | 318 | 296.5 | 156 | 254.1 | 307.9 | 194.1
812 | 622 | 566.8 | 226.72 | 265.0226 | 314.3 | 282.5 | 307.4 | 286 | 556.4 | 51 | 19.7 | 86.2 | 4.6 | 222.3 | 6.6 | 931.1 | 885.6 | 864.9 | 895.8 | 898.7 | 802.3 | 698.1 | 775.3 | 772.3 | 771 | 200.4 | 306.8 | 100.5 | 317.3 | 296.5 | 156.5 | 254.2 | 308.2 | 194.4
813 | 623 | 567.7 | 227.08 | 265.4434 | 313.9 | 282.2 | 306.9 | 285.4 | 574.3 | 51.1 | 19.7 | 86.3 | 4.4 | 236.2 | 6.5 | 930.9 | 887.2 | 865 | 896.1 | 900.6 | 802.3 | 702 | 781.6 | 773.2 | 773.4 | 200.7 | 306.6 | 100.8 | 316.6 | 296.4 | 157 | 254.3 | 308.5 | 194.6
814 | 624 | 567.4 | 226.96 | 265.3032 | 314.1 | 281.9 | 306.3 | 284.8 | 590.6 | 51.1 | 19.7 | 86.4 | 3.8 | 240.5 | 6.6 | 930.8 | 889.6 | 864.3 | 896.8 | 901.6 | 802.6 | 702.1 | 784.7 | 772.9 | 773.2 | 201 | 306.3 | 101.1 | 315.9 | 296 | 157.6 | 254.4 | 308.8 | 194.9
815 | 625 | 567.2 | 226.88 | 265.2096 | 314.3 | 282.4 | 306.1 | 283.6 | 596.3 | 51.1 | 19.7 | 86.5 | 4.2 | 237.1 | 6.2 | 931.2 | 888.6 | 863.9 | 897 | 904.7 | 803.2 | 701.9 | 781.3 | 771.9 | 773.3 | 201.4 | 306.1 | 101.4 | 315.5 | 295.3 | 158.1 | 254.6 | 309.1 | 195.2
816 | 626 | 566.8 | 226.72 | 265.0226 | 314.5 | 282.8 | 306.2 | 283.1 | 598.5 | 51.1 | 19.7 | 86.5 | 4.2 | 231.9 | 5.5 | 931.5 | 888.9 | 864.8 | 898.7 | 908.8 | 804 | 701.5 | 784.6 | 770.7 | 773.5 | 201.7 | 306.2 | 101.7 | 315 | 295 | 158.6 | 254.7 | 309.4 | 195.5
817 | 627 | 566.9 | 226.76 | 265.0694 | 314.5 | 283.4 | 305.8 | 282.8 | 613.7 | 51.2 | 19.7 | 86.6 | 4.4 | 243.5 | 4.7 | 931.8 | 888.5 | 864.7 | 897.7 | 908 | 804.6 | 704.9 | 791.1 | 771.2 | 773.2 | 202.1 | 306.4 | 102 | 314.6 | 294.8 | 159.1 | 254.9 | 309.7 | 195.8
818 | 628 | 566.8 | 226.72 | 265.0226 | 313.7 | 283.9 | 305.7 | 282.9 | 607.6 | 51.2 | 19.7 | 86.7 | 4.5 | 262.7 | 4.1 | 932.7 | 884 | 863.1 | 893.5 | 905.1 | 805 | 701.9 | 788.1 | 770.1 | 771.6 | 202.4 | 306.5 | 102.3 | 314.4 | 293.6 | 159.7 | 254.9 | 310 | 196
819 | 629 | 566.8 | 226.72 | 265.0226 | 312.7 | 284.4 | 306 | 282.9 | 591.7 | 51.3 | 19.7 | 86.6 | 4.1 | 261.9 | 4 | 933.1 | 882.9 | 862.8 | 894.5 | 899.1 | 805.3 | 700.7 | 784.7 | 768.5 | 771.8 | 202.7 | 306.5 | 102.6 | 314.3 | 293 | 160.2 | 255 | 310.3 | 196.3
820 | 630 | 566.5 | 226.6 | 264.8823 | 312.2 | 284.1 | 306.7 | 282.8 | 589.2 | 51.4 | 19.7 | 86.7 | 4.3 | 243.7 | 4.4 | 933.1 | 884.9 | 862.4 | 894.7 | 903.8 | 805.7 | 702.9 | 786.5 | 768.3 | 773.6 | 203.1 | 306.7 | 102.8 | 314.1 | 292.6 | 160.8 | 255.2 | 310.6 | 196.6
821 | 631 | 566.5 | 226.6 | 264.8823 | 311.5 | 284.3 | 306.9 | 282.5 | 597.3 | 51.5 | 19.7 | 86.8 | 3.9 | 235.4 | 4.5 | 934.1 | 875.1 | 861.3 | 891.6 | 904.6 | 806.1 | 699.5 | 788.5 | 767.6 | 771.9 | 203.4 | 307 | 103.1 | 314.8 | 293 | 161.3 | 255.4 | 310.9 | 196.9
822 | 632 | 566.4 | 226.56 | 264.8356 | 311.3 | 284.8 | 307.7 | 282 | 597.9 | 51.5 | 19.7 | 86.9 | 3.7 | 250.8 | 5.1 | 934 | 862.7 | 858.4 | 888.4 | 899.6 | 806.6 | 694.3 | 782 | 765.7 | 768.4 | 203.8 | 307.1 | 103.4 | 314.6 | 293.4 | 161.9 | 255.5 | 311.1 | 197.2
823 | 633 | 566.8 | 226.72 | 265.0226 | 311.9 | 284.6 | 308.1 | 282 | 582.3 | 51.6 | 19.7 | 86.9 | 3.8 | 257.7 | 5 | 934.3 | 850.5 | 855.9 | 883 | 891.4 | 806.7 | 688.3 | 774.3 | 763.8 | 767.7 | 204.1 | 307.4 | 103.7 | 314.6 | 293.2 | 162.4 | 255.7 | 311.4 | 197.4
824 | 634 | 567.4 | 226.96 | 265.3032 | 312.6 | 285.1 | 309.1 | 282.8 | 563.1 | 51.6 | 19.7 | 87 | 4 | 247 | 4.7 | 934.6 | 836.9 | 852.4 | 878.5 | 886.4 | 806.6 | 680.4 | 762.9 | 761 | 765.5 | 204.5 | 307.7 | 104 | 314.7 | 293.2 | 163 | 255.8 | 311.6 | 197.7
825 | 635 | 567.5 | 227 | 265.3499 | 313 | 285.6 | 308.9 | 283.2 | 546.2 | 51.6 | 19.7 | 87.1 | 4.1 | 239.5 | 5.1 | 934 | 843.8 | 852.2 | 880.1 | 887.3 | 806.4 | 675.1 | 758 | 759 | 765.2 | 204.8 | 308.1 | 104.3 | 314.5 | 293.2 | 163.5 | 256 | 311.9 | 198
826 | 636 | 567.5 | 227 | 265.3499 | 312.2 | 285.1 | 308.1 | 282.7 | 549.8 | 51.7 | 19.7 | 87.3 | 4.1 | 237.7 | 5.9 | 933.7 | 848.4 | 852.2 | 883.6 | 891.6 | 806.6 | 672 | 759.9 | 758 | 764.7 | 205.2 | 308 | 104.6 | 314.5 | 293.5 | 164 | 256.1 | 312.1 | 198.2
827 | 637 | 567.6 | 227.04 | 265.3967 | 311.4 | 284.1 | 307.6 | 282.4 | 545 | 51.8 | 19.7 | 87.3 | 4 | 257.9 | 5.9 | 933.5 | 854.6 | 850.7 | 884 | 893.7 | 806.6 | 671.5 | 761.9 | 757.2 | 766.1 | 205.6 | 307.5 | 105 | 314.2 | 293.2 | 164.6 | 256.2 | 312.3 | 198.5
828 | 638 | 567.6 | 227.04 | 265.3967 | 311.4 | 284.4 | 306.6 | 282.4 | 543.5 | 51.8 | 19.7 | 87.4 | 4.3 | 251.4 | 6.8 | 933.5 | 856.1 | 850.1 | 886 | 894.2 | 806.6 | 670.5 | 765.3 | 756.5 | 765.6 | 206 | 307.2 | 105.3 | 313.9 | 292.8 | 165.1 | 256.3 | 312.6 | 198.8
829 | 639 | 567.4 | 226.96 | 265.3032 | 311.7 | 284.6 | 305.8 | 282 | 543.3 | 51.8 | 19.7 | 87.5 | 4.5 | 238.2 | 8.7 | 933.8 | 860.1 | 848.9 | 884.9 | 896.3 | 806.6 | 670.9 | 766.4 | 755.5 | 765 | 206.4 | 307.3 | 105.6 | 314 | 292.4 | 165.7 | 256.5 | 312.8 | 199
830 | 640 | 567.8 | 227.12 | 265.4902 | 313.2 | 284.7 | 305.5 | 281.5 | 550.5 | 51.9 | 19.7 | 87.8 | 4.6 | 230.9 | 10.9 | 933.7 | 861.6 | 849.5 | 885 | 896.3 | 806.9 | 668.2 | 761.9 | 754.6 | 764.8 | 206.8 | 307.8 | 105.9 | 314 | 292.2 | 166.2 | 256.5 | 313.1 | 199.3
831 | 641 | 567.9 | 227.16 | 265.537 | 313.5 | 285 | 305.8 | 281.6 | 558.6 | 52 | 19.7 | 87.9 | 4.2 | 249.5 | 10.8 | 933 | 858.3 | 848.7 | 886.4 | 895.7 | 807.3 | 668 | 762.5 | 754.3 | 763.8 | 207.2 | 307.9 | 106.2 | 314 | 292 | 166.8 | 256.6 | 313.3 | 199.5
832 | 642 | 567.6 | 227.04 | 265.3967 | 314.4 | 285.2 | 306.5 | 282.4 | 567.6 | 52.1 | 19.7 | 88 | 4.1 | 257.4 | 8.9 | 932.6 | 847.6 | 845.5 | 882.5 | 896.1 | 807.3 | 665.6 | 757.6 | 753.1 | 761.4 | 207.6 | 308.2 | 106.5 | 313.7 | 291.4 | 167.4 | 256.8 | 313.5 | 199.8
833 | 643 | 567.6 | 227.04 | 265.3967 | 315.7 | 285.4 | 306.9 | 283 | 565 | 52.1 | 19.7 | 88 | 4.3 | 273 | 6.6 | 932.1 | 853.4 | 844.2 | 879.5 | 892 | 807.2 | 666.8 | 766.2 | 752.5 | 762.3 | 208 | 308.5 | 106.8 | 313.6 | 290.9 | 168 | 256.9 | 313.8 | 200.1
834 | 644 | 567.5 | 227 | 265.3499 | 315.2 | 285.6 | 307.4 | 283.4 | 567.1 | 52.2 | 19.7 | 88.1 | 4.3 | 228.9 | 5.4 | 932.2 | 859.7 | 845.2 | 883.2 | 891.1 | 806.7 | 672.7 | 767.2 | 752.8 | 764.9 | 208.4 | 308.7 | 107.1 | 313.7 | 290.5 | 168.6 | 257 | 314 | 200.3
835 | 645 | 565.4 | 226.16 | 264.368 | 315.6 | 285.5 | 307.7 | 283.9 | 567.3 | 52.3 | 19.7 | 88.1 | 4.8 | 200.7 | 4.8 | 932.1 | 864.5 | 844.5 | 884.6 | 890.3 | 805.9 | 681.7 | 764.8 | 753.9 | 767.1 | 208.8 | 308.6 | 107.4 | 313.8 | 290.7 | 169.1 | 257.3 | 314.2 | 200.6
836 | 646 | 565.7 | 226.28 | 264.5083 | 317 | 286 | 307.2 | 284.1 | 573 | 52.4 | 19.7 | 88.3 | 4.9 | 236.6 | 4.8 | 931.7 | 872 | 844.2 | 884.5 | 893.2 | 805.3 | 684.4 | 764 | 754.9 | 767.6 | 209.2 | 308.4 | 107.8 | 313.8 | 291.1 | 169.7 | 257.4 | 314.5 | 200.9
837 | 647 | 566.5 | 226.6 | 264.8823 | 317.3 | 286.3 | 306.5 | 284.3 | 572.4 | 52.5 | 19.7 | 88.4 | 5.2 | 197.5 | 4.5 | 930.7 | 876.9 | 843.9 | 886 | 898.9 | 804.9 | 689.8 | 765.4 | 755.7 | 768.1 | 209.6 | 308.1 | 108.1 | 313.5 | 291 | 170.3 | 257.5 | 314.7 | 201.2
838 | 648 | 567.4 | 226.96 | 265.3032 | 318.6 | 286.7 | 306.6 | 284.4 | 570.4 | 52.6 | 19.6 | 88.4 | 5.2 | 232.5 | 4.5 | 929.6 | 871.6 | 841.4 | 885.5 | 899.9 | 804.6 | 689.7 | 759.8 | 755.8 | 769.7 | 210 | 307.8 | 108.4 | 313.4 | 291.2 | 170.9 | 257.7 | 315 | 201.4
839 | 649 | 566.3 | 226.52 | 264.7888 | 319.1 | 286.6 | 306.2 | 284 | 556.5 | 52.7 | 19.6 | 88.5 | 4.9 | 242.1 | 4.8 | 929 | 874.5 | 842.6 | 887.1 | 904.7 | 804.1 | 689.8 | 755.3 | 755.5 | 770.9 | 210.4 | 307.6 | 108.7 | 313.2 | 291.1 | 171.5 | 257.9 | 315.2 | 201.7
840 | 650 | 566.6 | 226.64 | 264.9291 | 318.9 | 285.9 | 305.2 | 283.5 | 544.8 | 52.7 | 19.6 | 88.5 | 5.1 | 210.5 | 5.1 | 929.1 | 870.4 | 843 | 887.6 | 903.5 | 803.6 | 692.3 | 750.7 | 755.1 | 772.2 | 210.8 | 307.6 | 109 | 312.8 | 292.1 | 172.1 | 258.2 | 315.4 | 202
841 | 651 | 566.5 | 226.6 | 264.8823 | 318.7 | 285.5 | 304.9 | 283.3 | 533.6 | 52.8 | 19.6 | 88.4 | 5 | 223.9 | 5.9 | 929.7 | 872.3 | 845.6 | 886.9 | 908.6 | 802.8 | 695.8 | 750 | 755.2 | 774.6 | 211.1 | 307.6 | 109.3 | 312.6 | 292.3 | 172.7 | 258.4 | 315.7 | 202.2
842 | 652 | 567.1 | 226.84 | 265.1629 | 318.6 | 285.5 | 305 | 283.5 | 527.5 | 52.8 | 19.6 | 88.3 | 4.9 | 219.5 | 6.5 | 930.5 | 875.7 | 846.3 | 888 | 914.2 | 801.8 | 696.3 | 749.3 | 755 | 775 | 211.5 | 307.3 | 109.7 | 312.7 | 292.3 | 173.3 | 258.6 | 316 | 202.5
843 | 653 | 569.3 | 227.72 | 266.1916 | 318.1 | 285 | 304.3 | 284.3 | 525.2 | 52.9 | 19.6 | 88.3 | 4.6 | 251.5 | 6.8 | 930.7 | 874.3 | 847.6 | 890.2 | 919.3 | 801.3 | 696.3 | 751.2 | 754.4 | 776.1 | 211.8 | 307.2 | 110 | 313 | 293 | 174 | 258.8 | 316.3 | 202.7
844 | 654 | 569.5 | 227.8 | 266.2851 | 316.9 | 283.9 | 304 | 284.3 | 531.8 | 53 | 19.6 | 88.3 | 4.9 | 245.7 | 8.1 | 931.1 | 873.7 | 848.9 | 891.1 | 917.2 | 801 | 698.1 | 758.6 | 754.6 | 776.8 | 212.2 | 307.3 | 110.3 | 312.7 | 293.8 | 174.6 | 259 | 316.5 | 203
845 | 655 | 567.6 | 227.04 | 265.3967 | 316.1 | 283.4 | 304.9 | 284.4 | 536.8 | 53 | 19.6 | 88.4 | 5.2 | 225.1 | 8.8 | 932 | 875.3 | 849.2 | 893.5 | 921.4 | 800.9 | 697.9 | 758.5 | 754.2 | 778 | 212.5 | 307.5 | 110.6 | 312.8 | 293.5 | 175.2 | 259.1 | 316.8 | 203.2
846 | 656 | 567 | 226.8 | 265.1161 | 316.2 | 283.8 | 305.1 | 284.4 | 534.1 | 53.1 | 19.6 | 88.6 | 5.1 | 238.7 | 10.8 | 931.9 | 880.6 | 850.5 | 896.8 | 919.5 | 801.1 | 698.9 | 760.8 | 754.2 | 780.3 | 212.9 | 307.7 | 111 | 313.4 | 293.9 | 175.8 | 259.3 | 317.1 | 203.5
847 | 657 | 567.4 | 226.96 | 265.3032 | 317 | 283.9 | 304.6 | 284.3 | 531.3 | 53.1 | 19.6 | 88.8 | 4.4 | 232.4 | 11.1 | 931.9 | 880.4 | 851.6 | 897.1 | 919.2 | 801.3 | 698.7 | 764.6 | 753.7 | 778.9 | 213.2 | 307.9 | 111.3 | 313.9 | 294 | 176.5 | 259.5 | 317.3 | 203.8
848 | 658 | 567.8 | 227.12 | 265.4902 | 317.3 | 283.7 | 304.2 | 284.6 | 528.9 | 53.2 | 19.6 | 88.9 | 4.6 | 240 | 10.2 | 931.7 | 881.7 | 851.3 | 896.5 | 917.7 | 801.5 | 699.8 | 761.6 | 752.7 | 781.3 | 213.5 | 307.8 | 111.6 | 314.3 | 294.7 | 177.1 | 259.7 | 317.6 | 204
849 | 659 | 568 | 227.2 | 265.5837 | 316.9 | 284.1 | 304.1 | 285 | 525.5 | 53.2 | 19.6 | 89.1 | 5.2 | 243.4 | 11.5 | 933.1 | 874.6 | 849.2 | 890.6 | 919.5 | 801.9 | 697.4 | 757.5 | 752.1 | 782.5 | 213.8 | 307.8 | 111.9 | 314.4 | 295.3 | 177.7 | 259.8 | 317.9 | 204.4
850 | 660 | 567.9 | 227.16 | 265.537 | 316.5 | 284.2 | 303.9 | 284.9 | 519.2 | 53.2 | 19.6 | 89.2 | 4.8 | 233.4 | 11.8 | 934.3 | 873.6 | 848.8 | 888.5 | 915.2 | 802 | 693.5 | 755.6 | 753.1 | 782.6 | 214.1 | 307.8 | 112.2 | 314.5 | 295.5 | 178.4 | 259.9 | 318.1 | 204.6
851 | 661 | 567.7 | 227.08 | 265.4434 | 316.9 | 284.3 | 303.3 | 284.9 | 522.4 | 53.2 | 19.6 | 89.3 | 4.5 | 239.6 | 11.7 | 934.1 | 878.7 | 848.3 | 890.2 | 915.7 | 801.7 | 698.3 | 760.1 | 758.2 | 784 | 214.4 | 307.3 | 112.6 | 314.7 | 295.5 | 179 | 260 | 318.3 | 204.9
852 | 662 | 567.4 | 226.96 | 265.3032 | 316.8 | 284.5 | 302.5 | 284.7 | 530.7 | 53.2 | 19.6 | 89.5 | 4.8 | 240.9 | 11.3 | 933.9 | 882.8 | 848.3 | 890.8 | 917.6 | 801.4 | 701.5 | 761 | 764.2 | 785.1 | 214.8 | 306.6 | 112.9 | 314.6 | 295.9 | 179.6 | 260.3 | 318.6 | 205.2
853 | 663 | 567.2 | 226.88 | 265.2096 | 315.9 | 284.6 | 302 | 284.1 | 533.1 | 53.2 | 19.6 | 89.6 | 4.8 | 241.5 | 10.8 | 933.5 | 882 | 845.8 | 890.2 | 915.1 | 801.6 | 704 | 764.4 | 769 | 785.9 | 215 | 306.3 | 113.2 | 314.3 | 296.8 | 180.2 | 260.5 | 318.9 | 205.5
854 | 664 | 567.9 | 227.16 | 265.537 | 316 | 284.6 | 301.9 | 284.3 | 538.6 | 53.2 | 19.6 | 89.7 | 4.6 | 236 | 10.9 | 932.7 | 879.6 | 845.3 | 891.3 | 913.6 | 801.8 | 709 | 762.9 | 774.3 | 787.8 | 215.3 | 306.3 | 113.5 | 314 | 297.8 | 180.8 | 260.7 | 319.1 | 205.7
855 | 665 | 567.7 | 227.08 | 265.4434 | 315.8 | 284.6 | 301.6 | 283.6 | 534.4 | 53.3 | 19.6 | 89.8 | 4.6 | 249.8 | 10.2 | 932.8 | 880.5 | 846.3 | 892.1 | 917.1 | 801.7 | 706.3 | 759.1 | 776.5 | 787.6 | 215.6 | 306.2 | 113.8 | 313.7 | 298.3 | 181.5 | 260.8 | 319.5 | 206
856 | 666 | 566.5 | 226.6 | 264.8823 | 315.2 | 284.9 | 301.2 | 283.3 | 542.2 | 53.3 | 19.6 | 89.8 | 4.5 | 251.1 | 10.5 | 933.1 | 878 | 847.4 | 892.2 | 916.6 | 802 | 704.4 | 763 | 777.5 | 785.9 | 215.8 | 306 | 114.2 | 313.4 | 298 | 182.1 | 260.9 | 319.7 | 206.2
857 | 667 | 566.7 | 226.68 | 264.9759 | 314.5 | 285 | 301.6 | 283.7 | 555.6 | 53.3 | 19.6 | 89.9 | 3.9 | 262 | 10.4 | 933.3 | 875 | 845.9 | 889.6 | 915.6 | 802.5 | 702.6 | 763.5 | 777 | 786.3 | 216.1 | 306.1 | 114.5 | 313.3 | 297.8 | 182.7 | 261.1 | 320 | 206.5
858 | 668 | 567.2 | 226.88 | 265.2096 | 314.2 | 285.1 | 301.8 | 284.1 | 560.3 | 53.4 | 19.6 | 89.9 | 3.3 | 247.4 | 9.3 | 933.9 | 874.5 | 843.8 | 885.6 | 912.7 | 802.7 | 699.7 | 764.9 | 776 | 786 | 216.4 | 306.3 | 114.8 | 313.3 | 298 | 183.3 | 261.3 | 320.3 | 206.8
859 | 669 | 567 | 226.8 | 265.1161 | 315.7 | 285.2 | 302.3 | 284.2 | 553.8 | 53.4 | 19.6 | 89.9 | 3.8 | 250.9 | 8.9 | 934.8 | 871.8 | 843.2 | 884.7 | 915.3 | 802.8 | 697.6 | 761.6 | 774.8 | 786.6 | 216.6 | 306.6 | 115.1 | 313.3 | 298.3 | 183.9 | 261.4 | 320.6 | 207
860 | 670 | 566.7 | 226.68 | 264.9759 | 317.5 | 285 | 303.4 | 284.6 | 551.7 | 53.4 | 19.6 | 90 | 5 | 250.6 | 10.2 | 935.3 | 866 | 840.6 | 881 | 916.9 | 803 | 692.4 | 759.6 | 773.5 | 785.1 | 216.8 | 307 | 115.5 | 313.1 | 298.4 | 184.5 | 261.5 | 320.8 | 207.3
861 | 671 | 568.9 | 227.56 | 266.0045 | 319 | 284.9 | 303.6 | 284.9 | 556.9 | 53.5 | 19.6 | 90 | 5.1 | 234.2 | 9.2 | 935.5 | 863.6 | 840.1 | 881.1 | 910.8 | 803.7 | 689.6 | 758.6 | 771.9 | 784.1 | 217 | 307.3 | 115.8 | 313 | 298.3 | 185.1 | 261.6 | 321 | 207.5
862 | 672 | 569.2 | 227.68 | 266.1448 | 320.8 | 284.8 | 302.9 | 284.9 | 564.7 | 53.5 | 19.6 | 90.1 | 5 | 205.6 | 6.9 | 935.2 | 866.4 | 839.7 | 882 | 906.6 | 803.8 | 689.8 | 762.3 | 771.7 | 783.5 | 217.2 | 307.7 | 116.1 | 313.1 | 298.3 | 185.7 | 261.8 | 321.3 | 207.8
863 | 673 | 567 | 226.8 | 265.1161 | 321.5 | 285.5 | 304.2 | 284.9 | 556.7 | 53.5 | 19.6 | 90.1 | 4.7 | 253.5 | 6.8 | 935.2 | 861.5 | 838.5 | 880.9 | 909.5 | 803.8 | 685.9 | 757 | 769.4 | 781.1 | 217.4 | 308.2 | 116.4 | 313.3 | 298.4 | 186.2 | 261.9 | 321.5 | 208
864 | 674 | 567 | 226.8 | 265.1161 | 322.8 | 285.9 | 305.1 | 285.3 | 540.4 | 53.6 | 19.6 | 90.1 | 4.9 | 239.5 | 6.3 | 935.4 | 865.1 | 838.8 | 881.3 | 917.9 | 803.6 | 685.2 | 755 | 767.5 | 782 | 217.5 | 308.1 | 116.7 | 313.1 | 298.6 | 186.8 | 262.1 | 321.7 | 208.3
865 | 675 | 566.9 | 226.76 | 265.0694 | 321.7 | 285.9 | 304.8 | 285.1 | 534.1 | 53.6 | 19.6 | 90.2 | 4.9 | 248.9 | 6.4 | 935.6 | 867.8 | 837.2 | 878.6 | 920.3 | 803 | 688.2 | 753.1 | 767.9 | 783.2 | 217.7 | 308 | 117.1 | 313.3 | 298.3 | 187.5 | 262.3 | 321.9 | 208.6
866 | 676 | 568 | 227.2 | 265.5837 | 321.1 | 285.9 | 304.8 | 285 | 535.6 | 53.7 | 19.6 | 90.3 | 5.2 | 242.8 | 8.3 | 935.8 | 877.1 | 838.6 | 879.7 | 925.9 | 802.4 | 693.1 | 757.1 | 770.1 | 786.1 | 217.8 | 308 | 117.4 | 313.3 | 298.3 | 188.1 | 262.4 | 322.1 | 208.8
867 | 677 | 568.3 | 227.32 | 265.724 | 322.1 | 285.8 | 304.5 | 284.9 | 530.2 | 53.8 | 19.6 | 90.4 | 4.7 | 256.8 | 10.3 | 935.6 | 882.8 | 840.9 | 883.3 | 927.5 | 801.9 | 696.7 | 757.3 | 772.5 | 787 | 217.8 | 307.9 | 117.7 | 313.4 | 298.4 | 188.7 | 262.7 | 322.4 | 209.1
868 | 678 | 567.8 | 227.12 | 265.4902 | 323.3 | 285.9 | 304.3 | 285.3 | 528.3 | 53.9 | 19.6 | 90.4 | 4.1 | 243.7 | 11.1 | 936 | 887.5 | 842.3 | 885.4 | 927.8 | 801.2 | 699.2 | 761.2 | 774.5 | 786.6 | 217.9 | 308 | 118 | 313.6 | 299.1 | 189.3 | 262.8 | 322.6 | 209.4
869 | 679 | 568.1 | 227.24 | 265.6305 | 323.2 | 285.7 | 304.6 | 285.6 | 537.8 | 53.9 | 19.6 | 90.5 | 4.4 | 231.8 | 10.6 | 935.8 | 887.6 | 844.4 | 886.9 | 926.9 | 801.1 | 700.7 | 770.3 | 776.4 | 787.2 | 217.9 | 308.2 | 118.4 | 313.8 | 299.4 | 190 | 263.1 | 322.9 | 209.6
870 | 680 | 567.4 | 226.96 | 265.3032 | 324 | 285.9 | 305 | 285.4 | 555.4 | 54 | 19.6 | 90.5 | 5.5 | 233.1 | 10.2 | 935.9 | 887 | 846.5 | 889.3 | 928.9 | 801 | 706.4 | 776.3 | 780.1 | 788.4 | 217.9 | 308.7 | 118.7 | 314.2 | 298.8 | 190.6 | 263.3 | 323.2 | 209.9
871 | 681 | 567.5 | 227 | 265.3499 | 324.5 | 286.5 | 304.9 | 285.1 | 568.6 | 54 | 19.6 | 90.6 | 5.1 | 235.5 | 9.9 | 936.1 | 891.6 | 844.2 | 888.7 | 928.6 | 801 | 708.4 | 777.3 | 782.5 | 789.1 | 217.9 | 309 | 119 | 314.4 | 299.3 | 191.3 | 263.5 | 323.5 | 210.1
872 | 682 | 568.1 | 227.24 | 265.6305 | 325.1 | 286.7 | 304.9 | 285.2 | 568.1 | 54 | 19.6 | 90.7 | 4.7 | 233 | 9.6 | 935.2 | 893.3 | 844 | 889.6 | 928.8 | 801.3 | 712.9 | 783.1 | 785.2 | 790.2 | 217.9 | 309 | 119.3 | 314.2 | 299.6 | 191.9 | 263.7 | 323.8 | 210.3
873 | 683 | 567.1 | 226.84 | 265.1629 | 325.4 | 286.9 | 304.4 | 285.6 | 575.3 | 54 | 19.6 | 90.7 | 4.9 | 236.1 | 8.5 | 934.5 | 891.3 | 843.1 | 888.3 | 927.7 | 801.7 | 714.1 | 781.2 | 787.4 | 791.9 | 217.9 | 309.4 | 119.7 | 314.1 | 300 | 192.6 | 263.9 | 324 | 210.6
874 | 684 | 567.4 | 226.96 | 265.3032 | 324.8 | 287.1 | 305.2 | 285.7 | 567.7 | 54.1 | 19.6 | 90.7 | 4.4 | 251.1 | 7.4 | 935.2 | 885.6 | 843.4 | 883.7 | 930 | 802.1 | 711.9 | 777.2 | 787 | 793.4 | 217.9 | 309.4 | 120 | 314 | 300.4 | 193.3 | 264.1 | 324.3 | 210.9
875 | 685 | 568.6 | 227.44 | 265.8643 | 325.3 | 287.5 | 306 | 285.7 | 563.6 | 54.1 | 19.6 | 90.7 | 5 | 256.3 | 7.5 | 936.3 | 883.5 | 841.8 | 879 | 927.3 | 802.4 | 711 | 773.5 | 786.3 | 793.9 | 218 | 309.2 | 120.3 | 313.9 | 301.1 | 193.9 | 264.3 | 324.6 | 211.1
876 | 686 | 567.6 | 227.04 | 265.3967 | 326.3 | 287.6 | 305.8 | 285.8 | 551.2 | 54.2 | 19.6 | 90.7 | 5.1 | 238.1 | 6.5 | 937.5 | 871.9 | 838 | 871.8 | 925.7 | 802.8 | 702.4 | 762 | 781.4 | 792 | 218 | 309.1 | 120.6 | 313.8 | 300.6 | 194.5 | 264.5 | 324.8 | 211.3
877 | 687 | 566.6 | 226.64 | 264.9291 | 326.5 | 287.6 | 305 | 285.6 | 535.7 | 54.2 | 19.6 | 90.7 | 4.5 | 231.7 | 6.1 | 938.3 | 857.4 | 834.4 | 866 | 920.4 | 802.7 | 693.1 | 748.6 | 775.2 | 790.4 | 218 | 308.9 | 121 | 313.8 | 300.8 | 195.2 | 264.6 | 325 | 211.6
878 | 688 | 566.6 | 226.64 | 264.9291 | 326.9 | 287.6 | 304.4 | 285.7 | 518.9 | 54.3 | 19.6 | 90.7 | 4.4 | 223.7 | 5.9 | 938 | 857.3 | 833.1 | 866.5 | 918.6 | 802.2 | 689.2 | 740.2 | 769.8 | 788.2 | 218 | 308.8 | 121.3 | 314.2 | 301.2 | 195.8 | 264.8 | 325.2 | 211.9
879 | 689 | 566.2 | 226.48 | 264.7421 | 327.3 | 287.6 | 303.2 | 286.1 | 509.9 | 54.3 | 19.6 | 90.8 | 5.2 | 246.7 | 5.8 | 937.5 | 857.3 | 834 | 869 | 921.1 | 801.4 | 686.6 | 740.1 | 766 | 788.7 | 218 | 308.5 | 121.6 | 314.9 | 302 | 196.4 | 265.1 | 325.5 | 212.1
880 | 690 | 567.2 | 226.88 | 265.2096 | 327.2 | 286.7 | 303.4 | 286.5 | 511.4 | 54.3 | 19.6 | 90.8 | 4.8 | 226.4 | 6.7 | 937.7 | 856.8 | 834.6 | 868.6 | 921.4 | 801 | 684.4 | 743.3 | 763.4 | 788.2 | 218 | 307.7 | 121.9 | 315.9 | 303.2 | 197 | 265.4 | 325.7 | 212.4
881 | 691 | 566.4 | 226.56 | 264.8356 | 327.2 | 286.3 | 303.1 | 286.8 | 517.3 | 54.3 | 19.6 | 90.8 | 4.1 | 241.6 | 7.3 | 937.1 | 859.1 | 835.3 | 870.6 | 922.1 | 800.9 | 686.5 | 748.8 | 762.4 | 787.9 | 218.1 | 307.1 | 122.2 | 315.7 | 304.1 | 197.7 | 265.6 | 325.9 | 212.6
882 | 692 | 566.9 | 226.76 | 265.0694 | 327 | 286.5 | 302.7 | 287.1 | 525.2 | 54.4 | 19.6 | 90.9 | 4.5 | 234 | 6.9 | 937 | 861.9 | 836.7 | 872.3 | 925.6 | 801.3 | 687.5 | 749.8 | 761.9 | 788.3 | 218.1 | 307.1 | 122.6 | 315.7 | 304.6 | 198.3 | 265.7 | 326.1 | 212.8
883 | 693 | 567.2 | 226.88 | 265.2096 | 327 | 286.1 | 302.8 | 287.4 | 525.6 | 54.5 | 19.6 | 91 | 4.9 | 250.7 | 6.2 | 936.9 | 866.4 | 836.4 | 871.6 | 927.2 | 801.3 | 689 | 749.3 | 762.9 | 789.3 | 218.2 | 307.1 | 122.9 | 315.4 | 304.6 | 198.9 | 265.9 | 326.4 | 213
884 | 694 | 568 | 227.2 | 265.5837 | 328 | 285.9 | 303.3 | 287 | 524.9 | 54.6 | 19.6 | 91.2 | 5 | 264.7 | 4.9 | 936.3 | 863.3 | 836.7 | 871.4 | 926.2 | 801.7 | 685.3 | 755.3 | 761.9 | 786.8 | 218.5 | 307.4 | 123.2 | 315.5 | 304 | 199.4 | 266 | 326.6 | 213.3
885 | 695 | 568.2 | 227.28 | 265.6772 | 329.1 | 285.8 | 304.7 | 287.1 | 536.5 | 54.7 | 19.6 | 91.2 | 5.1 | 266 | 4 | 936.3 | 865.5 | 838.4 | 872.1 | 930 | 802.2 | 683.7 | 751.8 | 760.9 | 785.9 | 218.7 | 308.1 | 123.5 | 316 | 304.1 | 200 | 266.2 | 326.8 | 213.7
886 | 696 | 567.7 | 227.08 | 265.4434 | 330 | 285.7 | 305.3 | 287.4 | 544.9 | 54.8 | 19.6 | 91.3 | 4.9 | 250 | 4.5 | 936.3 | 870.9 | 839.9 | 874.4 | 929.1 | 802.3 | 686.9 | 754 | 761.7 | 787.7 | 218.9 | 308.8 | 123.9 | 316.3 | 304.5 | 200.7 | 266.3 | 327 | 213.9
887 | 697 | 567.5 | 227 | 265.3499 | 330.3 | 285.7 | 305.9 | 287.5 | 551.1 | 54.8 | 19.6 | 91.4 | 4.5 | 231.7 | 4.2 | 935.6 | 877.6 | 841.6 | 876.7 | 926.3 | 801.8 | 694.3 | 753.2 | 764 | 789 | 219.1 | 309 | 124.2 | 316.4 | 304.7 | 201.3 | 266.5 | 327.2 | 214.1
888 | 698 | 567.6 | 227.04 | 265.3967 | 331.1 | 286 | 306.4 | 288 | 552.9 | 54.8 | 19.6 | 91.5 | 4.7 | 252.3 | 3.5 | 934.4 | 876.9 | 841.3 | 879.6 | 926 | 801.2 | 700.6 | 755.9 | 766.7 | 790.2 | 219.3 | 309.1 | 124.5 | 316.8 | 304.7 | 201.8 | 266.6 | 327.4 | 214.5
889 | 699 | 567.4 | 226.96 | 265.3032 | 331.5 | 286.3 | 306.1 | 288.1 | 555.4 | 54.8 | 19.6 | 91.5 | 5 | 262.5 | 3.3 | 933.6 | 880.2 | 837.4 | 880.2 | 923.8 | 800.8 | 703.9 | 755.8 | 769.7 | 791.1 | 219.5 | 308.9 | 124.8 | 316.6 | 304.8 | 202.4 | 266.7 | 327.6 | 214.7
890 | 700 | 568.1 | 227.24 | 265.6305 | 332 | 286.4 | 305.7 | 287.8 | 555.9 | 54.8 | 19.6 | 91.5 | 5 | 249.6 | 3.7 | 933 | 884.4 | 836.5 | 881.2 | 927.4 | 800.4 | 707.8 | 756 | 772.5 | 793.5 | 219.7 | 308.6 | 125.2 | 316.5 | 304.7 | 203 | 266.8 | 327.7 | 214.9
891 | 701 | 568.2 | 227.28 | 265.6772 | 331.3 | 286.6 | 306.2 | 287.8 | 553.4 | 54.8 | 19.6 | 91.6 | 4.8 | 246.3 | 4.4 | 933 | 884.9 | 837.1 | 881.3 | 932.8 | 800.1 | 705.4 | 754 | 772.9 | 793.8 | 219.8 | 308.2 | 125.5 | 316.8 | 304.5 | 203.6 | 267.1 | 327.9 | 215.2
892 | 702 | 568.5 | 227.4 | 265.8175 | 330.8 | 287.1 | 306.3 | 287.4 | 549.6 | 54.8 | 19.6 | 91.6 | 4.7 | 249.7 | 5.3 | 932.6 | 892 | 838.2 | 880.7 | 935.2 | 800.4 | 707.6 | 758.3 | 773.9 | 794.4 | 220 | 307.8 | 125.8 | 317 | 304.1 | 204.1 | 267.2 | 328 | 215.5
893 | 703 | 568.1 | 227.24 | 265.6305 | 331.2 | 287.4 | 306.6 | 287.8 | 558.8 | 54.8 | 19.6 | 91.7 | 4.9 | 254 | 6.2 | 932.6 | 892.9 | 839.2 | 879.6 | 937.4 | 800.5 | 710.8 | 759.8 | 775.9 | 795.5 | 220.2 | 307.6 | 126.1 | 317.2 | 304.1 | 204.7 | 267.4 | 328.2 | 215.7
894 | 704 | 566.2 | 226.48 | 264.7421 | 332.4 | 287.7 | 307 | 288 | 546.1 | 54.9 | 19.5 | 91.8 | 5.3 | 259 | 6 | 933.2 | 896.5 | 837.8 | 877.8 | 939.8 | 800.1 | 710.7 | 755.1 | 776.9 | 796.7 | 220.4 | 307.8 | 126.5 | 317.7 | 304.6 | 205.2 | 267.6 | 328.3 | 216
895 | 705 | 566.6 | 226.64 | 264.9291 | 333.2 | 288.1 | 307.3 | 287.9 | 543.1 | 54.9 | 19.5 | 91.7 | 5.2 | 245.5 | 5.6 | 933.5 | 897.5 | 836.2 | 878.2 | 937.8 | 799.9 | 710.9 | 757.4 | 776.8 | 797 | 220.6 | 308.1 | 126.8 | 318.2 | 304.5 | 205.8 | 267.6 | 328.5 | 216.2
896 | 706 | 566.2 | 226.48 | 264.7421 | 333.5 | 288.2 | 307.3 | 287.7 | 538.3 | 54.9 | 19.5 | 91.8 | 5.2 | 257.4 | 5.3 | 933.5 | 901.1 | 835.5 | 878 | 932.4 | 799.7 | 714.5 | 754 | 777.2 | 799.2 | 220.8 | 308.1 | 127.1 | 318.4 | 304.5 | 206.3 | 267.8 | 328.8 | 216.5
897 | 707 | 566.7 | 226.68 | 264.9759 | 333.4 | 288.3 | 307.1 | 287.5 | 529.2 | 54.9 | 19.5 | 91.8 | 5.4 | 255.7 | 6.1 | 932.6 | 898.5 | 837.2 | 879.2 | 930.7 | 799.6 | 714.2 | 746.8 | 777.6 | 800.6 | 221 | 307.7 | 127.4 | 318.7 | 304.7 | 206.8 | 268 | 329 | 216.7
898 | 708 | 566.2 | 226.48 | 264.7421 | 334.3 | 288.6 | 306.7 | 288.2 | 517.8 | 55 | 19.5 | 91.8 | 5.2 | 199.6 | 5.3 | 933 | 894 | 835.9 | 875.8 | 934 | 799.6 | 710.4 | 743.5 | 776.2 | 801.3 | 221.4 | 307.6 | 127.7 | 319.2 | 304.8 | 207.3 | 268.2 | 329.3 | 217
899 | 709 | 566.5 | 226.6 | 264.8823 | 334.5 | 288.7 | 306.2 | 288.9 | 516.9 | 55 | 19.5 | 91.9 | 5.1 | 247.5 | 5.2 | 933.6 | 892.4 | 835.8 | 875 | 936.4 | 799.2 | 709.3 | 741.3 | 776.1 | 802 | 221.7 | 307.8 | 128.1 | 319.8 | 305.1 | 207.8 | 268.4 | 329.5 | 217.3
900 | 710 | 566 | 226.4 | 264.6486 | 334.2 | 288.9 | 305.9 | 289.2 | 519.1 | 55 | 19.5 | 92 | 5.3 | 199.3 | 7.2 | 933.7 | 893.6 | 838.4 | 879.4 | 936.2 | 799 | 713.2 | 742.4 | 777.3 | 802.5 | 221.9 | 308.2 | 128.4 | 320.1 | 305.5 | 208.3 | 268.6 | 329.7 | 217.5
901 | 711 | 566.7 | 226.68 | 264.9759 | 334.6 | 289 | 304.9 | 289.6 | 516.4 | 55.1 | 19.5 | 92 | 5.7 | 244.3 | 7 | 934.2 | 893.7 | 838.8 | 879 | 938 | 798.6 | 714.2 | 745.2 | 778.2 | 803.9 | 222.2 | 308.5 | 128.7 | 320.4 | 305.8 | 208.8 | 268.8 | 330 | 217.8
902 | 712 | 566.5 | 226.6 | 264.8823 | 335.5 | 289 | 305.1 | 290.4 | 520.7 | 55 | 19.5 | 92 | 5.9 | 243.8 | 6.9 | 934 | 891.2 | 838.4 | 879.8 | 938.5 | 798.1 | 715.8 | 750.5 | 780.2 | 805.6 | 222.4 | 308.7 | 129 | 321.3 | 306 | 209.3 | 269 | 330.2 | 218
903 | 713 | 566.8 | 226.72 | 265.0226 | 337 | 288.9 | 305.6 | 291 | 537.5 | 55.1 | 19.5 | 92.2 | 5.1 | 268.3 | 6 | 934.1 | 888.2 | 836.4 | 876.7 | 935.7 | 798.4 | 714.4 | 756.5 | 780 | 805 | 222.6 | 309 | 129.4 | 322 | 306.8 | 209.7 | 269.2 | 330.5 | 218.4
904 | 714 | 566.6 | 226.64 | 264.9291 | 337.6 | 288.7 | 306.2 | 291.1 | 542.9 | 55.1 | 19.5 | 92.3 | 4.4 | 257.4 | 7.2 | 934 | 886.3 | 832.8 | 875.4 | 935 | 799.3 | 711 | 754.4 | 777.7 | 803.5 | 222.8 | 309 | 129.7 | 321.9 | 307.5 | 210.2 | 269.3 | 330.7 | 218.6
905 | 715 | 566.9 | 226.76 | 265.0694 | 338.4 | 288.8 | 306.2 | 290.9 | 544.3 | 55.2 | 19.5 | 92.3 | 4.2 | 244.9 | 7.3 | 934.5 | 875.8 | 832 | 872.2 | 937.8 | 799.9 | 706.1 | 751.6 | 774.9 | 801.3 | 223 | 309.3 | 130 | 322 | 307.9 | 210.6 | 269.5 | 330.9 | 218.8
906 | 716 | 566.5 | 226.6 | 264.8823 | 340.5 | 288.9 | 306.7 | 291.2 | 537.7 | 55.3 | 19.5 | 92.4 | 5 | 244.9 | 6.7 | 934.9 | 879.8 | 831.8 | 869.4 | 936.5 | 800.5 | 701.4 | 746.3 | 771.7 | 800.9 | 223.2 | 309.4 | 130.4 | 321.9 | 308.4 | 211 | 269.6 | 331.1 | 219.1
907 | 717 | 566.5 | 226.6 | 264.8823 | 341 | 289.2 | 308 | 291.3 | 540.1 | 55.3 | 19.5 | 92.3 | 5.5 | 243.1 | 7.7 | 934.7 | 886.7 | 834.9 | 871.3 | 933.4 | 801.3 | 700.6 | 756.4 | 769.7 | 799.1 | 223.3 | 310 | 130.7 | 321.6 | 308.5 | 211.3 | 269.8 | 331.3 | 219.4
908 | 718 | 567.2 | 226.88 | 265.2096 | 340 | 289 | 308.9 | 291.2 | 561.6 | 55.4 | 19.5 | 92.3 | 5.2 | 251.6 | 8.2 | 935 | 885.8 | 836.1 | 870.7 | 932.8 | 801.8 | 704.6 | 760.1 | 769.8 | 800.5 | 223.5 | 310.1 | 131 | 321.2 | 308.1 | 211.7 | 269.9 | 331.5 | 219.6
909 | 719 | 566.4 | 226.56 | 264.8356 | 339.7 | 289.1 | 309.5 | 291.2 | 574.1 | 55.4 | 19.5 | 92.5 | 5.1 | 239.9 | 9.5 | 934.9 | 882.6 | 836 | 871.7 | 934 | 802.4 | 705.1 | 765.5 | 770 | 798.1 | 223.6 | 310.2 | 131.3 | 320.9 | 307.6 | 212 | 269.9 | 331.7 | 219.9
910 | 720 | 567.7 | 227.08 | 265.4434 | 339.6 | 289.5 | 310.3 | 291.3 | 584.9 | 55.4 | 19.5 | 92.5 | 4.8 | 256 | 9.7 | 934.8 | 873.2 | 835.9 | 869.5 | 928.6 | 803.2 | 699.2 | 762.1 | 768.2 | 794.7 | 223.8 | 310.4 | 131.7 | 321 | 307.4 | 212.4 | 269.9 | 331.9 | 220.1
911 | 721 | 567.6 | 227.04 | 265.3967 | 340.2 | 290.1 | 311 | 291.5 | 602.3 | 55.4 | 19.5 | 92.4 | 4.7 | 256.1 | 9.4 | 934.5 | 865.3 | 836.5 | 869.2 | 920.5 | 804.3 | 698.6 | 766.7 | 767.7 | 791.6 | 224 | 310.5 | 132 | 320.9 | 307.3 | 212.7 | 270 | 332.2 | 220.4
912 | 722 | 566.7 | 226.68 | 264.9759 | 340.9 | 291 | 312.2 | 292 | 604.5 | 55.4 | 19.5 | 92.6 | 5.1 | 261.2 | 8.9 | 934.9 | 862 | 836.5 | 868.2 | 908 | 805.1 | 693.3 | 764.2 | 766 | 788.1 | 224.2 | 311.6 | 132.3 | 321.3 | 306.9 | 213.1 | 270.1 | 332.5 | 220.6
913 | 723 | 566.3 | 226.52 | 264.7888 | 341.2 | 292 | 313.5 | 293.2 | 605.1 | 55.4 | 19.5 | 92.7 | 5.1 | 259 | 8.1 | 935.6 | 867 | 839.2 | 869.8 | 902.3 | 805.6 | 694.5 | 766.1 | 764.9 | 787.5 | 224.5 | 312.5 | 132.6 | 322.9 | 306.5 | 213.5 | 270.2 | 332.8 | 220.9
914 | 724 | 565.8 | 226.32 | 264.555 | 341.8 | 292.5 | 314.4 | 294.7 | 600.3 | 55.4 | 19.5 | 92.7 | 5 | 260.5 | 7.1 | 935.5 | 870.3 | 840.7 | 872.9 | 907.7 | 805.4 | 697.5 | 760.9 | 764.4 | 789 | 224.7 | 312.9 | 133 | 323.6 | 306.4 | 214 | 270.4 | 333 | 221.2
915 | 725 | 566.6 | 226.64 | 264.9291 | 341.4 | 292.7 | 314.3 | 295.4 | 594.9 | 55.4 | 19.5 | 92.7 | 5.4 | 270.6 | 7.2 | 934 | 868.5 | 843 | 878.3 | 912.2 | 805 | 700.6 | 766.5 | 765.6 | 788.3 | 225 | 313 | 133.3 | 324.3 | 306.2 | 214.4 | 270.5 | 333.2 | 221.5
916 | 726 | 567.8 | 227.12 | 265.4902 | 341 | 293 | 313.3 | 295 | 600.7 | 55.5 | 19.5 | 92.8 | 4.9 | 263.9 | 7.1 | 933.2 | 874.4 | 840.3 | 878.3 | 912.4 | 804.3 | 705.7 | 761.8 | 767.5 | 788.3 | 225.3 | 313.1 | 133.6 | 324.5 | 306.6 | 214.8 | 270.6 | 333.5 | 221.7
917 | 727 | 566.8 | 226.72 | 265.0226 | 340.9 | 293 | 313.5 | 294.5 | 588.5 | 55.6 | 19.5 | 93 | 4.4 | 284 | 7 | 932.2 | 874.1 | 837.2 | 876.7 | 914.1 | 804.3 | 706.7 | 762.8 | 767.8 | 788.6 | 225.6 | 313.1 | 133.9 | 324.7 | 307 | 215.2 | 270.9 | 333.7 | 222
918 | 728 | 567.2 | 226.88 | 265.2096 | 341.5 | 292.8 | 313.8 | 293.9 | 592.3 | 55.6 | 19.5 | 93.1 | 4.8 | 267.6 | 6.6 | 932 | 875.2 | 838.6 | 876.5 | 915.1 | 804.5 | 706.6 | 765.4 | 768.2 | 788 | 225.9 | 312.9 | 134.3 | 324.7 | 306.8 | 215.5 | 270.9 | 333.9 | 222.2
919 | 729 | 566.9 | 226.76 | 265.0694 | 342.2 | 292.4 | 312.8 | 293.5 | 591.7 | 55.7 | 19.5 | 93.3 | 4.7 | 268.7 | 7.1 | 932.5 | 881.5 | 836.7 | 873.8 | 914.6 | 805 | 704.8 | 766.7 | 767.4 | 788.7 | 226.1 | 312.5 | 134.6 | 324.9 | 306.7 | 215.8 | 271 | 334.2 | 222.4
920 | 730 | 567.5 | 227 | 265.3499 | 341.6 | 292.4 | 312 | 293.5 | 582 | 55.7 | 19.5 | 93.4 | 4.9 | 255.1 | 7.6 | 932.6 | 887.3 | 835.7 | 874.2 | 919.2 | 805.2 | 704.3 | 767.2 | 767.1 | 790 | 226.3 | 312.1 | 134.9 | 324.8 | 306.4 | 216.1 | 271 | 334.4 | 222.7
921 | 731 | 567.9 | 227.16 | 265.537 | 342 | 293 | 312.2 | 293.4 | 580.2 | 55.8 | 19.5 | 93.3 | 5.4 | 257.3 | 8 | 932.9 | 883.7 | 833.9 | 873.1 | 922.6 | 805.3 | 703.7 | 767.6 | 767.4 | 789.8 | 226.5 | 312.1 | 135.3 | 324.8 | 305.8 | 216.4 | 271.1 | 334.6 | 222.9
922 | 732 | 567.4 | 226.96 | 265.3032 | 342.5 | 293.4 | 311.5 | 292.7 | 576.3 | 55.9 | 19.5 | 93.4 | 4.5 | 248.1 | 9.1 | 932.9 | 881.3 | 833.9 | 873.4 | 923.9 | 805.9 | 701.6 | 766.5 | 765.8 | 789.9 | 226.7 | 312.4 | 135.6 | 324.8 | 305.8 | 216.7 | 271.2 | 334.8 | 223.2
923 | 733 | 563.3 | 225.32 | 263.3861 | 342.2 | 293.5 | 311.8 | 292.7 | 572.3 | 56 | 19.5 | 93.5 | 3.9 | 251.3 | 8.2 | 932.3 | 878.5 | 835.1 | 875.8 | 922.9 | 806.1 | 704.6 | 761.8 | 766.1 | 791.4 | 227 | 312.7 | 135.9 | 324.8 | 306.1 | 217 | 271.4 | 335.1 | 223.3
924 | 734 | 563.7 | 225.48 | 263.5731 | 341.8 | 293.7 | 312.6 | 292.5 | 557.1 | 56.1 | 19.5 | 93.5 | 4 | 246.3 | 8 | 931.9 | 878.9 | 834.7 | 876 | 926.7 | 805.6 | 702.2 | 752.2 | 763.8 | 791.3 | 227.3 | 312.8 | 136.2 | 324.4 | 306.4 | 217.3 | 271.6 | 335.3 | 223.6
925 | 735 | 564.8 | 225.92 | 264.0875 | 342 | 293.9 | 312.9 | 292.7 | 541.3 | 56.2 | 19.5 | 93.7 | 4.3 | 251.8 | 7.9 | 932.1 | 882.7 | 835.5 | 876.1 | 928.7 | 804.6 | 703 | 747.8 | 763 | 792.2 | 227.7 | 312.6 | 136.6 | 324.1 | 306.4 | 217.5 | 271.8 | 335.5 | 223.7
926 | 736 | 565.4 | 226.16 | 264.368 | 341.6 | 294 | 313.1 | 292.5 | 534.8 | 56.2 | 19.5 | 93.7 | 4.7 | 253 | 7.2 | 932.8 | 877.9 | 831.1 | 870.8 | 928.9 | 803.9 | 701.9 | 745.6 | 762.8 | 792.1 | 228 | 312.3 | 136.9 | 324.2 | 306.7 | 217.8 | 271.9 | 335.7 | 224
927 | 737 | 567.5 | 227 | 265.3499 | 341.9 | 294.1 | 312.9 | 292.1 | 528.9 | 56.2 | 19.5 | 93.9 | 4.7 | 277.8 | 6.4 | 933.2 | 876.2 | 827.9 | 868.3 | 929.2 | 803.2 | 705.8 | 742.7 | 762.8 | 793.8 | 228.2 | 312.1 | 137.2 | 324.3 | 308.1 | 218.1 | 272.1 | 335.9 | 224.3
928 | 738 | 567.5 | 227 | 265.3499 | 344 | 294.2 | 312.3 | 291 | 520.5 | 56.3 | 19.5 | 94 | 4 | 272.7 | 5.6 | 933.6 | 875.7 | 831.6 | 872 | 932.7 | 802.4 | 707.6 | 735.6 | 763.2 | 794.9 | 228.5 | 311.8 | 137.5 | 324.5 | 309.9 | 218.4 | 272.6 | 336.2 | 224.6
929 | 739 | 568 | 227.2 | 265.5837 | 344.7 | 294.5 | 312.8 | 291 | 509.8 | 56.2 | 19.5 | 94 | 3.9 | 258.8 | 5.5 | 934 | 883.6 | 831.9 | 874.6 | 933.6 | 801.7 | 707.6 | 740.6 | 762.7 | 796.4 | 228.7 | 311.7 | 137.9 | 324.9 | 310.3 | 218.7 | 272.8 | 336.4 | 224.8
930 | 740 | 566 | 226.4 | 264.6486 | 344.2 | 294 | 313 | 291.8 | 509.3 | 56.2 | 19.5 | 94.1 | 4.5 | 260.6 | 7.3 | 933.7 | 882.7 | 830.7 | 875.4 | 930.9 | 801.4 | 706.6 | 740.9 | 762 | 797.3 | 228.9 | 311.6 | 138.2 | 325.6 | 310.5 | 219 | 273 | 336.7 | 225.1
931 | 741 | 566.2 | 226.48 | 264.7421 | 344.1 | 293.6 | 313.7 | 291.7 | 512.1 | 56.2 | 19.5 | 94.1 | 5 | 261.5 | 9.1 | 933.6 | 886.3 | 832.8 | 877.6 | 935.3 | 800.9 | 710.5 | 741.6 | 762.9 | 798.2 | 229.1 | 311.4 | 138.5 | 326 | 311.6 | 219.3 | 273.3 | 336.9 | 225.3
932 | 742 | 565.7 | 226.28 | 264.5083 | 344.4 | 293.6 | 313.8 | 292.3 | 511.8 | 56.1 | 19.5 | 94.1 | 4.7 | 259.3 | 9 | 934 | 889.4 | 834.7 | 879.5 | 935.5 | 800.1 | 714 | 747.8 | 764.8 | 799.1 | 229.4 | 311.3 | 138.8 | 326.4 | 312.8 | 219.6 | 273.6 | 337.2 | 225.5
933 | 743 | 566.5 | 226.6 | 264.8823 | 343.8 | 293.3 | 313.8 | 292.6 | 525 | 56 | 19.5 | 94.1 | 4.7 | 257.2 | 8.1 | 933.9 | 893.1 | 834.9 | 879.9 | 931.5 | 799.4 | 719.2 | 757.7 | 767.6 | 801.2 | 229.6 | 311.3 | 139.2 | 326.6 | 313.7 | 219.9 | 274 | 337.4 | 225.9
934 | 744 | 566.8 | 226.72 | 265.0226 | 343.1 | 292.6 | 313.8 | 292.6 | 541.1 | 56 | 19.5 | 94 | 3.9 | 262.6 | 8.5 | 934.2 | 901.8 | 835.4 | 879.5 | 932.5 | 799.3 | 721.3 | 757.4 | 769.6 | 802.3 | 229.8 | 311.2 | 139.5 | 326.5 | 314.8 | 220.2 | 274.3 | 337.7 | 226
935 | 745 | 566.3 | 226.52 | 264.7888 | 342.9 | 292.2 | 314 | 291.8 | 555.5 | 56 | 19.5 | 94 | 4.3 | 261.1 | 8.4 | 934.2 | 899.1 | 839.5 | 881.1 | 934.6 | 799.8 | 719.5 | 756.7 | 769.8 | 801.4 | 230 | 311.1 | 139.8 | 326.3 | 314.7 | 220.5 | 274.6 | 338 | 226.3
936 | 746 | 567.1 | 226.84 | 265.1629 | 341.9 | 292.1 | 313.5 | 291.8 | 557.2 | 56.1 | 19.4 | 94 | 5 | 264.7 | 8.3 | 933.4 | 894.8 | 844.4 | 883 | 934.1 | 800.1 | 720.8 | 763.5 | 770.9 | 802.8 | 230.2 | 310.9 | 140.1 | 326.3 | 313.6 | 220.7 | 274.6 | 338.3 | 226.6
937 | 747 | 567.2 | 226.88 | 265.2096 | 341.7 | 292.3 | 313.2 | 291.8 | 574.5 | 56.1 | 19.5 | 94 | 5.2 | 272.1 | 9.1 | 932.2 | 893.4 | 844.3 | 885.2 | 931.5 | 800.2 | 723.1 | 770.3 | 772.8 | 803.1 | 230.4 | 310.8 | 140.5 | 326.2 | 313.1 | 221 | 274.6 | 338.5 | 226.8
938 | 748 | 568.2 | 227.28 | 265.6772 | 343 | 292.2 | 313.4 | 292.3 | 570.4 | 56.1 | 19.5 | 94 | 4.6 | 253.6 | 9.2 | 931.1 | 897.7 | 845.4 | 887.1 | 929.7 | 800.6 | 727 | 767.2 | 775 | 804.6 | 230.6 | 311.2 | 140.8 | 326 | 312.8 | 221.2 | 274.7 | 338.8 | 227.1
939 | 749 | 567.4 | 226.96 | 265.3032 | 343.8 | 291.9 | 313.6 | 292.6 | 556.5 | 56.1 | 19.5 | 94.1 | 5 | 250.7 | 9.3 | 930.1 | 894.5 | 848 | 888.4 | 933.7 | 800.8 | 732.6 | 762.5 | 777.5 | 805.5 | 230.9 | 311.3 | 141.1 | 326.4 | 313.6 | 221.5 | 275 | 339 | 227.3
940 | 750 | 567.4 | 226.96 | 265.3032 | 343.9 | 291.9 | 312.9 | 292.5 | 552.8 | 56.2 | 19.4 | 94.1 | 5.3 | 259.2 | 8.8 | 929.3 | 884.5 | 853.9 | 889.9 | 937.8 | 800.7 | 735.1 | 765.7 | 779.3 | 805.9 | 231.1 | 311.2 | 141.4 | 326.7 | 313.9 | 221.8 | 275.2 | 339.3 | 227.6
941 | 751 | 567 | 226.8 | 265.1161 | 344 | 292.2 | 312.9 | 292.7 | 557.3 | 56.2 | 19.4 | 94.1 | 5.6 | 245.6 | 8.4 | 929.4 | 886.4 | 858.6 | 893.3 | 938 | 800.2 | 735.1 | 771.1 | 780.3 | 805.7 | 231.3 | 311 | 141.8 | 326.5 | 313.2 | 222.1 | 275.4 | 339.6 | 227.8
942 | 752 | 567.9 | 227.16 | 265.537 | 343.7 | 292.7 | 313.1 | 293.3 | 569.9 | 56.2 | 19.4 | 94.1 | 5.7 | 246.7 | 9 | 930.4 | 889.8 | 860.3 | 893.1 | 937 | 800.2 | 732.9 | 775.6 | 780.8 | 807.1 | 231.5 | 310.8 | 142.1 | 326.7 | 313.1 | 222.4 | 275.5 | 340 | 228.1
943 | 753 | 566.4 | 226.56 | 264.8356 | 343.4 | 293.2 | 312.9 | 293.3 | 567 | 56.3 | 19.4 | 94.2 | 5 | 273.2 | 8.5 | 930.9 | 888.3 | 861.3 | 890.9 | 938.7 | 800.4 | 732.8 | 771.8 | 781 | 807.5 | 231.7 | 310.8 | 142.4 | 326.8 | 313.3 | 222.6 | 275.6 | 340.3 | 228.3
944 | 754 | 567.1 | 226.84 | 265.1629 | 343.2 | 293.4 | 312.6 | 292.9 | 557.1 | 56.3 | 19.4 | 94.1 | 5.1 | 257.1 | 7.8 | 931.1 | 891.5 | 862.1 | 892.2 | 939.8 | 800.3 | 733.3 | 769.7 | 781.3 | 808.2 | 231.8 | 311.2 | 142.7 | 327.1 | 313.6 | 223 | 275.8 | 340.6 | 228.5
945 | 755 | 568.3 | 227.32 | 265.724 | 343.8 | 293.5 | 312.4 | 292.4 | 556.5 | 56.3 | 19.4 | 94.1 | 5.1 | 259.9 | 6.2 | 932.4 | 889.2 | 861.9 | 895.4 | 939.5 | 800.1 | 734.5 | 769.4 | 781.9 | 808.5 | 232 | 311.6 | 143 | 327.2 | 314.7 | 223.3 | 276 | 340.9 | 228.8
946 | 756 | 568.2 | 227.28 | 265.6772 | 344 | 293.9 | 312.6 | 291.8 | 554.7 | 56.3 | 19.4 | 94.1 | 5.3 | 281.2 | 5.4 | 933.5 | 901.8 | 861.7 | 894.6 | 935.3 | 800.3 | 733.5 | 769.4 | 781.2 | 809.2 | 232.2 | 311.7 | 143.3 | 327.3 | 316.2 | 223.7 | 276.3 | 341.2 | 229
947 | 757 | 567.7 | 227.08 | 265.4434 | 344.5 | 294.5 | 313.4 | 291.9 | 548.8 | 56.3 | 19.4 | 94.1 | 4.9 | 236.4 | 5.1 | 933.8 | 902 | 860 | 892.9 | 935.4 | 800.5 | 730.7 | 761.4 | 780.4 | 808.7 | 232.4 | 311.6 | 143.7 | 327.5 | 316.4 | 224.1 | 276.6 | 341.5 | 229.2
948 | 758 | 567.9 | 227.16 | 265.537 | 345.5 | 294.8 | 312.9 | 292.6 | 545.2 | 56.3 | 19.4 | 94.1 | 5.1 | 251.6 | 5 | 934.2 | 898 | 860.7 | 891.3 | 936.4 | 800.8 | 728.6 | 756.7 | 780.3 | 808.7 | 232.6 | 312 | 144 | 327.9 | 316.2 | 224.5 | 276.8 | 341.8 | 229.5
949 | 759 | 566.3 | 226.52 | 264.7888 | 346 | 295 | 312.6 | 292.8 | 538.8 | 56.4 | 19.4 | 94 | 4.9 | 275.3 | 6 | 935.8 | 897.5 | 858.1 | 888.4 | 933.9 | 801.1 | 725.4 | 759.2 | 779.6 | 808.1 | 232.8 | 312.3 | 144.3 | 328.5 | 316.9 | 224.8 | 277 | 342 | 229.8
950 | 760 | 565.8 | 226.32 | 264.555 | 345.1 | 295.3 | 312.9 | 293.2 | 549 | 56.4 | 19.4 | 94.1 | 4.4 | 257.9 | 7.5 | 935.8 | 899.9 | 856.3 | 888.5 | 932.5 | 801.7 | 721.1 | 761.1 | 778.6 | 807.6 | 233 | 312.5 | 144.6 | 328.8 | 317.3 | 225.2 | 277.1 | 342.3 | 230
951 | 761 | 568.9 | 227.56 | 266.0045 | 344.8 | 295.2 | 312.8 | 293.3 | 557.1 | 56.4 | 19.4 | 94.2 | 3.7 | 267.1 | 8.2 | 935.7 | 897 | 852.2 | 886.5 | 932.2 | 802.3 | 718.1 | 764.7 | 778 | 806.7 | 233.3 | 312.7 | 144.9 | 329 | 317.1 | 225.6 | 277.2 | 342.5 | 230.3
952 | 762 | 571.3 | 228.52 | 267.1267 | 345.8 | 295.4 | 313.8 | 292.5 | 567.7 | 56.5 | 19.4 | 94.4 | 4 | 251.4 | 8.1 | 935.6 | 898.8 | 851.5 | 886.8 | 930.6 | 802.8 | 719.2 | 772.7 | 779.4 | 805.6 | 233.5 | 312.6 | 145.3 | 328.9 | 316.9 | 226 | 277.4 | 342.8 | 230.6
953 | 763 | 569.6 | 227.84 | 266.3318 | 347 | 295.7 | 315 | 292.9 | 588.1 | 56.5 | 19.4 | 94.5 | 4 | 281.4 | 7.8 | 935.6 | 898.8 | 854.6 | 888.9 | 930.4 | 803.6 | 723 | 776.5 | 782.5 | 805.8 | 233.8 | 312.7 | 145.6 | 328.7 | 316.6 | 226.4 | 277.4 | 343 | 230.8
954 | 764 | 569.1 | 227.64 | 266.098 | 347.4 | 295.9 | 316 | 293.2 | 611.1 | 56.5 | 19.4 | 94.6 | 4.5 | 272.6 | 7.9 | 934.8 | 894.2 | 856.5 | 889.9 | 924.3 | 804.8 | 723 | 779.1 | 781.7 | 803.6 | 234 | 312.7 | 145.9 | 328.6 | 315.9 | 226.8 | 277.4 | 343.3 | 231
955 | 765 | 568 | 227.2 | 265.5837 | 346.8 | 295.9 | 317.1 | 293.3 | 616.4 | 56.5 | 19.4 | 94.7 | 4.5 | 273.6 | 7.9 | 933.7 | 888.6 | 858.4 | 892.3 | 919 | 805.5 | 724.4 | 781.6 | 783.5 | 802.1 | 234.3 | 312.8 | 146.2 | 328.7 | 315.2 | 227.2 | 277.5 | 343.5 | 231.3
956 | 766 | 566.5 | 226.6 | 264.8823 | 346.6 | 296.2 | 318.2 | 293.7 | 633.1 | 56.4 | 19.4 | 94.7 | 4.4 | 283.7 | 7.8 | 933.1 | 886.2 | 855.4 | 893 | 916.4 | 806.1 | 722.6 | 786.1 | 784.6 | 800.4 | 234.5 | 313 | 146.5 | 329 | 314.6 | 227.6 | 277.5 | 343.8 | 231.5
957 | 767 | 567 | 226.8 | 265.1161 | 347.8 | 296.9 | 318.9 | 293.9 | 650.5 | 56.4 | 19.4 | 94.8 | 4.6 | 253.8 | 7.9 | 933.3 | 883.8 | 853.8 | 893.1 | 914.1 | 807.1 | 723.1 | 784.6 | 785.6 | 800.2 | 234.8 | 313.1 | 146.9 | 329.2 | 314.4 | 228 | 277.6 | 344.1 | 231.7
958 | 768 | 567.4 | 226.96 | 265.3032 | 349.4 | 297.3 | 319.3 | 294.5 | 651.5 | 56.4 | 19.4 | 94.8 | 4.7 | 262.5 | 8.1 | 933.4 | 887.9 | 854.4 | 895.1 | 914.1 | 808 | 726 | 783.5 | 786.3 | 800 | 235.1 | 313.2 | 147.2 | 329.2 | 314 | 228.5 | 277.8 | 344.4 | 232
959 | 769 | 568.8 | 227.52 | 265.9578 | 349.3 | 297.9 | 319 | 295.3 | 642.2 | 56.4 | 19.4 | 95 | 4.8 | 250.1 | 8.3 | 932.7 | 888 | 853.4 | 896.4 | 915.4 | 808.2 | 729.6 | 779.8 | 788.3 | 801.5 | 235.4 | 313.6 | 147.5 | 329.1 | 314.1 | 228.9 | 277.9 | 344.6 | 232.3
960 | 770 | 567.9 | 227.16 | 265.537 | 349.9 | 298.7 | 319.4 | 295.4 | 619.5 | 56.4 | 19.4 | 95.1 | 5.1 | 259.6 | 7.6 | 933.5 | 881.8 | 846.8 | 889.8 | 916.7 | 808.5 | 727.5 | 773 | 785.7 | 802 | 235.7 | 314 | 147.8 | 329.8 | 314.1 | 229.4 | 278 | 344.9 | 232.5
961 | 771 | 568.3 | 227.32 | 265.724 | 351.3 | 299.1 | 319.2 | 295.7 | 589.8 | 56.4 | 19.4 | 95.1 | 5.2 | 259.1 | 7.3 | 934.2 | 876.6 | 840.4 | 882.6 | 917.3 | 808.4 | 720.3 | 757.8 | 780.4 | 801.8 | 236 | 314.2 | 148.2 | 330.7 | 314.4 | 230 | 278.2 | 345.2 | 232.7
962 | 772 | 568.2 | 227.28 | 265.6772 | 351.4 | 299.3 | 318.7 | 295.9 | 568.4 | 56.5 | 19.4 | 95.1 | 4.6 | 257.6 | 7 | 934.1 | 879.3 | 838.7 | 882.7 | 921.1 | 807.9 | 722.7 | 753.3 | 779.2 | 803.4 | 236.3 | 314.6 | 148.5 | 330.9 | 314.6 | 230.5 | 278.4 | 345.4 | 233
963 | 773 | 568.1 | 227.24 | 265.6305 | 351.7 | 299.2 | 318.6 | 296.4 | 558.6 | 56.6 | 19.4 | 95.1 | 4.4 | 260.5 | 6.8 | 934.3 | 881.6 | 841.1 | 883.3 | 926.1 | 807.1 | 722.7 | 753.6 | 779.5 | 804.5 | 236.6 | 314.8 | 148.8 | 331.1 | 315.1 | 231 | 278.5 | 345.6 | 233.2
964 | 774 | 568.7 | 227.48 | 265.911 | 352.3 | 299.1 | 318.2 | 296.8 | 564.6 | 56.6 | 19.4 | 95.2 | 4.4 | 253.1 | 6 | 934.8 | 889.1 | 844.1 | 886.2 | 931.4 | 806.7 | 724.1 | 758.9 | 780.4 | 805.9 | 236.9 | 314.9 | 149.1 | 331.4 | 315.5 | 231.5 | 278.7 | 345.8 | 233.4
965 | 775 | 566.9 | 226.76 | 265.0694 | 352.5 | 299 | 318.2 | 297.2 | 573.5 | 56.6 | 19.4 | 95.3 | 4.1 | 248.8 | 6.1 | 935.4 | 888.4 | 849.7 | 892.9 | 935.1 | 806.6 | 726.9 | 761.2 | 782.5 | 805.7 | 237.2 | 315.1 | 149.4 | 331.8 | 315.5 | 231.9 | 278.8 | 346.1 | 233.7
966 | 776 | 566.4 | 226.56 | 264.8356 | 351.9 | 298.8 | 318.5 | 297.3 | 577.1 | 56.7 | 19.4 | 95.4 | 4.5 | 255.9 | 6.4 | 935.8 | 889.3 | 850.1 | 896.2 | 935 | 806.5 | 727.7 | 762.8 | 783.9 | 806.2 | 237.5 | 315 | 149.8 | 331.9 | 315.4 | 232.4 | 279 | 346.3 | 234
967 | 777 | 567.3 | 226.92 | 265.2564 | 351.7 | 298.3 | 318.5 | 297.2 | 574.4 | 56.8 | 19.4 | 95.5 | 4.4 | 264.8 | 6.6 | 936.4 | 887.1 | 845.7 | 894.6 | 936.9 | 806.4 | 725.7 | 759.1 | 783.5 | 805.3 | 237.8 | 315.1 | 150.1 | 331.8 | 315.2 | 232.9 | 279.1 | 346.6 | 234.2
968 | 778 | 569.1 | 227.64 | 266.098 | 352.3 | 297.8 | 318.5 | 296.7 | 563.6 | 56.9 | 19.4 | 95.5 | 4.4 | 278.7 | 6.1 | 937.1 | 884.6 | 845.5 | 890.3 | 937.9 | 806.4 | 721.2 | 749.9 | 779.8 | 805 | 238.1 | 315.1 | 150.4 | 331.5 | 315 | 233.4 | 279.2 | 346.8 | 234.4
969 | 779 | 568.5 | 227.4 | 265.8175 | 352.1 | 297 | 318.6 | 296.6 | 555 | 57 | 19.4 | 95.5 | 4.3 | 273.4 | 5.4 | 937.5 | 886.8 | 846.2 | 889.1 | 936.5 | 806 | 720 | 750.9 | 778.3 | 805.3 | 238.4 | 315 | 150.7 | 331.2 | 314.8 | 234 | 279.3 | 347 | 234.7
970 | 780 | 570 | 228 | 266.5189 | 352 | 296.6 | 318.3 | 296.3 | 557.2 | 57 | 19.4 | 95.5 | 4.5 | 248.1 | 4.8 | 937.5 | 890.3 | 847.1 | 891.4 | 939.4 | 805.6 | 724.7 | 751.7 | 780 | 806.5 | 238.6 | 314.9 | 151.1 | 331.5 | 315.1 | 234.5 | 279.5 | 347.2 | 234.9
971 | 781 | 568.2 | 227.28 | 265.6772 | 352.4 | 296.9 | 317.5 | 295.6 | 557.5 | 57 | 19.4 | 95.6 | 4.4 | 254.7 | 5.2 | 937.1 | 887.7 | 850.5 | 894 | 938.5 | 805.3 | 726.6 | 759.9 | 780.4 | 806.7 | 238.9 | 314.9 | 151.4 | 331.6 | 315.8 | 235 | 279.7 | 347.5 | 235.1
972 | 782 | 566.5 | 226.6 | 264.8823 | 352.5 | 297.2 | 316.5 | 295.1 | 583 | 57.1 | 19.4 | 95.7 | 5.1 | 255.2 | 4.9 | 937.4 | 892.7 | 854.4 | 898.5 | 936.4 | 805.1 | 727.4 | 767.6 | 781.5 | 807.7 | 239.2 | 315.1 | 151.7 | 331.5 | 316.6 | 235.5 | 280 | 347.8 | 235.4
973 | 783 | 566.1 | 226.44 | 264.6953 | 352.2 | 297.5 | 316.3 | 294.1 | 600.6 | 57.1 | 19.4 | 95.9 | 4.8 | 239.6 | 4.9 | 936.3 | 893.5 | 857.1 | 900.5 | 934.1 | 805.1 | 729.5 | 771.9 | 782.7 | 807.9 | 239.5 | 315 | 152 | 331.4 | 316.7 | 235.9 | 280.3 | 348.1 | 235.6
974 | 784 | 566.9 | 226.76 | 265.0694 | 352.9 | 297.8 | 316.1 | 294.1 | 611.6 | 57.2 | 19.4 | 96 | 5 | 233.3 | 5 | 935.6 | 894.8 | 856.5 | 902.2 | 933 | 805.6 | 730.6 | 772.9 | 784.5 | 808 | 239.7 | 314.9 | 152.4 | 331.4 | 316.3 | 236.3 | 280.3 | 348.4 | 235.8
975 | 785 | 567 | 226.8 | 265.1161 | 353.1 | 297.9 | 315.8 | 294.4 | 611.6 | 57.3 | 19.4 | 96.1 | 5 | 234.2 | 5.2 | 935.5 | 902 | 854.9 | 900.3 | 930.5 | 806.1 | 733.1 | 771.5 | 785.8 | 809.3 | 240 | 315.7 | 152.7 | 331.6 | 316.7 | 236.8 | 280.4 | 348.7 | 236.1
976 | 786 | 567.1 | 226.84 | 265.1629 | 353.2 | 298.2 | 316.1 | 294.7 | 597.6 | 57.3 | 19.4 | 96.2 | 4.8 | 239.4 | 5 | 935.2 | 900 | 859 | 900.7 | 927.4 | 806.2 | 736.2 | 768.4 | 786.5 | 810.3 | 240.3 | 315.9 | 153 | 331.3 | 317.1 | 237.3 | 280.6 | 349 | 236.4
977 | 787 | 566.8 | 226.72 | 265.0226 | 352.8 | 298.1 | 315.6 | 294.5 | 586.6 | 57.4 | 19.4 | 96.3 | 4.7 | 248.1 | 5.5 | 934.1 | 892 | 861.5 | 899.1 | 927.4 | 806.4 | 739.4 | 770.6 | 787.3 | 811.3 | 240.5 | 316.2 | 153.3 | 331.2 | 317.2 | 237.7 | 280.7 | 349.3 | 236.6
978 | 788 | 567.1 | 226.84 | 265.1629 | 352.7 | 298.3 | 315.9 | 294.6 | 600.8 | 57.4 | 19.4 | 96.4 | 4.6 | 235 | 5.7 | 932.9 | 887.6 | 861.1 | 900.7 | 929.5 | 806.3 | 745 | 776.4 | 790 | 811.3 | 240.8 | 316.2 | 153.6 | 331.4 | 316.9 | 238.1 | 280.8 | 349.6 | 236.8
979 | 789 | 568.3 | 227.32 | 265.724 | 353.3 | 298.8 | 316.4 | 294.7 | 619.7 | 57.4 | 19.4 | 96.4 | 4.3 | 227.2 | 5.4 | 932 | 901 | 857.3 | 901.9 | 926 | 806.6 | 748.4 | 775.9 | 793.4 | 812.3 | 241 | 316 | 154 | 331.5 | 316.9 | 238.6 | 280.9 | 349.9 | 237.1
980 | 790 | 568.4 | 227.36 | 265.7707 | 354 | 299.1 | 316 | 294.9 | 612.4 | 57.4 | 19.4 | 96.3 | 4.2 | 244.5 | 5.1 | 931.5 | 902.1 | 858.8 | 904.1 | 929 | 807.1 | 749.4 | 776.3 | 795.8 | 813 | 241.3 | 315.9 | 154.3 | 331.5 | 317.2 | 239 | 281 | 350.2 | 237.3
981 | 791 | 568.3 | 227.32 | 265.724 | 354.7 | 299.3 | 316.8 | 294.9 | 611.4 | 57.3 | 19.4 | 96.2 | 4.4 | 241.5 | 5 | 931.9 | 906.6 | 860.5 | 904 | 931.8 | 807.4 | 749.8 | 777.6 | 797.3 | 813.7 | 241.6 | 316 | 154.6 | 331.9 | 317.1 | 239.5 | 281.2 | 350.6 | 237.5
982 | 792 | 568.1 | 227.24 | 265.6305 | 354.9 | 299.9 | 317.1 | 294.8 | 600.9 | 57.2 | 19.4 | 96.1 | 4.6 | 238.6 | 5.1 | 932.4 | 906.3 | 861.1 | 903.2 | 931.4 | 807.6 | 748.8 | 777.8 | 796.9 | 814.6 | 241.9 | 316.2 | 154.9 | 332.2 | 317.4 | 240 | 281.4 | 350.8 | 237.8
983 | 793 | 567.7 | 227.08 | 265.4434 | 354.5 | 300.5 | 317.9 | 294.8 | 589.5 | 57.2 | 19.4 | 96.1 | 4.4 | 242.5 | 5.2 | 932.1 | 903.4 | 859.4 | 905.1 | 932.1 | 807.5 | 747.6 | 777.5 | 796.7 | 815.2 | 242.2 | 316.3 | 155.3 | 332.2 | 317.5 | 240.5 | 281.6 | 351.1 | 238
984 | 794 | 568.1 | 227.24 | 265.6305 | 354.5 | 300.9 | 317.7 | 295.6 | 585.6 | 57.2 | 19.4 | 96.1 | 4.8 | 235.2 | 4.8 | 932 | 910.6 | 858.1 | 903.1 | 935.2 | 807.4 | 745.7 | 773 | 795.8 | 814.5 | 242.5 | 316.5 | 155.6 | 332.4 | 317.6 | 241 | 281.7 | 351.4 | 238.3
985 | 795 | 569.1 | 227.64 | 266.098 | 356.5 | 301 | 317.5 | 296.2 | 575.3 | 57.1 | 19.4 | 96.2 | 5 | 219.7 | 4.5 | 932.3 | 908.8 | 859 | 902.1 | 931.9 | 807.7 | 738.8 | 768.2 | 792.4 | 814.9 | 242.8 | 316.6 | 155.9 | 332.9 | 317.7 | 241.5 | 281.9 | 351.7 | 238.5
986 | 796 | 567.3 | 226.92 | 265.2564 | 357.9 | 301 | 317.5 | 296.7 | 565.3 | 57.1 | 19.4 | 96.2 | 4.5 | 218.9 | 5.2 | 932.1 | 906 | 857.8 | 901.4 | 926.4 | 807.8 | 738.9 | 767.1 | 791.6 | 815.9 | 243 | 316.7 | 156.2 | 333.7 | 318.5 | 242.1 | 282.1 | 352 | 238.8
987 | 797 | 567.8 | 227.12 | 265.4902 | 358.2 | 301.1 | 317.8 | 297.3 | 556.1 | 57 | 19.4 | 96.2 | 4.1 | 224.5 | 5.4 | 932.7 | 901.7 | 854.9 | 899.1 | 929.6 | 807.5 | 739.5 | 764.4 | 790.5 | 817 | 243.3 | 316.8 | 156.6 | 334 | 319 | 242.6 | 282.4 | 352.3 | 239
988 | 798 | 568.1 | 227.24 | 265.6305 | 357.5 | 300.7 | 317.6 | 296.9 | 550.3 | 57.1 | 19.4 | 96.3 | 4.6 | 215.6 | 5.8 | 932.9 | 896.6 | 859.5 | 901.6 | 933.3 | 807.1 | 741.5 | 770.5 | 791.1 | 816.6 | 243.5 | 316.8 | 156.9 | 334.4 | 319.5 | 243.2 | 282.6 | 352.6 | 239.3
989 | 799 | 568.2 | 227.28 | 265.6772 | 356.3 | 300.4 | 316.9 | 296.6 | 564.5 | 57 | 19.3 | 96.4 | 5.2 | 208 | 7 | 932.5 | 890.6 | 862.3 | 904.7 | 936.8 | 807 | 744 | 772.2 | 792.1 | 816.5 | 243.7 | 316.7 | 157.2 | 334.8 | 319.8 | 243.7 | 282.8 | 352.9 | 239.5
990 | 800 | 568.9 | 227.56 | 266.0045 | 354.6 | 300.2 | 316.9 | 297.1 | 585.1 | 57.1 | 19.3 | 96.4 | 4.8 | 240.5 | 6.9 | 932.7 | 894.6 | 862.2 | 908.6 | 939.1 | 807 | 744 | 776.2 | 791.9 | 815.9 | 243.9 | 316.7 | 157.5 | 335.1 | 319.7 | 244.3 | 282.9 | 353.3 | 239.8
991 | 801 | 568.9 | 227.56 | 266.0045 | 353.7 | 300 | 316.6 | 297.5 | 595.9 | 57.1 | 19.3 | 96.4 | 4.1 | 232.9 | 6.5 | 932.4 | 895.9 | 864.6 | 907.3 | 939.6 | 807 | 746.1 | 778.3 | 792.6 | 816.8 | 244.1 | 316.5 | 157.9 | 335 | 319.5 | 244.9 | 283 | 353.7 | 240
992 | 802 | 569.4 | 227.76 | 266.2383 | 352.7 | 299.6 | 317 | 297.2 | 605.1 | 57.1 | 19.3 | 96.5 | 4.5 | 256.7 | 6.8 | 932.2 | 888.4 | 866.8 | 906.9 | 942.5 | 806.9 | 750.1 | 781.8 | 794.5 | 818.1 | 244.3 | 316.3 | 158.2 | 334.7 | 319.3 | 245.4 | 283.1 | 354 | 240.2
993 | 803 | 569.7 | 227.88 | 266.3786 | 352.1 | 299.7 | 317.2 | 296.4 | 609 | 57.2 | 19.3 | 96.6 | 4.9 | 237.9 | 7.2 | 932.4 | 889.8 | 864.3 | 907.4 | 939.2 | 806.9 | 750.1 | 783.5 | 794.6 | 819.6 | 244.4 | 316.4 | 158.5 | 334.3 | 319 | 245.9 | 283.1 | 354.3 | 240.5
994 | 804 | 568.5 | 227.4 | 265.8175 | 351.6 | 300 | 316.8 | 295.8 | 623.8 | 57.2 | 19.3 | 96.7 | 4.7 | 246.1 | 7.5 | 932.5 | 904.5 | 859.5 | 907.4 | 935.9 | 807.5 | 749.4 | 785.7 | 796.3 | 818.9 | 244.6 | 316.8 | 158.8 | 334.2 | 318.9 | 246.3 | 283.1 | 354.7 | 240.7
995 | 805 | 567.1 | 226.84 | 265.1629 | 352.5 | 300.3 | 316.1 | 295.8 | 627.4 | 57.3 | 19.3 | 96.8 | 4.3 | 251.1 | 7.3 | 932.4 | 909.5 | 858 | 905.9 | 933.2 | 808.9 | 747.2 | 789 | 797.2 | 816.8 | 244.7 | 317.3 | 159.2 | 334.6 | 319.8 | 246.8 | 283.4 | 355 | 240.9
996 | 806 | 567 | 226.8 | 265.1161 | 353.6 | 300.7 | 317.5 | 296.4 | 641.8 | 57.3 | 19.3 | 96.9 | 4.5 | 233.7 | 6.8 | 932.7 | 897.2 | 851.9 | 898.5 | 923.8 | 810.2 | 744 | 788.6 | 796.5 | 812.3 | 244.9 | 317.8 | 159.5 | 335.4 | 320.3 | 247.2 | 283.7 | 355.3 | 241.2
997 | 807 | 567.1 | 226.84 | 265.1629 | 354.3 | 300.8 | 318.8 | 297.5 | 653.7 | 57.4 | 19.3 | 96.9 | 4.8 | 251.8 | 7 | 933.7 | 892.4 | 850.2 | 894.8 | 922 | 811.8 | 735.4 | 785.3 | 792.1 | 809.1 | 245.1 | 318.6 | 159.8 | 335.8 | 320.6 | 247.7 | 283.8 | 355.6 | 241.5
998 | 808 | 567.2 | 226.88 | 265.2096 | 354.4 | 301.4 | 320.1 | 298.6 | 669 | 57.4 | 19.3 | 96.9 | 4.6 | 260.3 | 6.9 | 933.2 | 891.6 | 853.9 | 898.8 | 920.2 | 812.2 | 734.9 | 788 | 791.7 | 807 | 245.3 | 319.3 | 160.2 | 336 | 320.6 | 248.2 | 283.8 | 355.9 | 241.7
999 | 809 | 566.5 | 226.6 | 264.8823 | 356.2 | 301.8 | 321.5 | 299.6 | 663.1 | 57.5 | 19.3 | 97 | 4.5 | 242.3 | 6.9 | 932.6 | 893.9 | 856.5 | 901 | 915.4 | 812.5 | 735.8 | 785.2 | 792.4 | 807.7 | 245.5 | 319.8 | 160.5 | 336.3 | 320.1 | 248.7 | 284 | 356.2 | 241.9
1000 | 810 | 566 | 226.4 | 264.6486 | 356 | 302.4 | 322.3 | 300.2 | 642.8 | 57.6 | 19.3 | 97 | 4.5 | 232.7 | 6.8 | 932.3 | 899.4 | 855.6 | 902.2 | 910.1 | 812.9 | 737.1 | 784.1 | 792.5 | 807.9 | 245.6 | 320.3 | 160.8 | 336.9 | 320.2 | 249.2 | 284.1 | 356.5 | 242.2
1001 | 811 | 567.2 | 226.88 | 265.2096 | 356.6 | 303.1 | 322.3 | 300.3 | 630.9 | 57.7 | 19.3 | 97.1 | 5.2 | 233.2 | 6.5 | 932.2 | 898.1 | 860.2 | 904.3 | 915.8 | 813 | 739.8 | 784.3 | 792.4 | 808.3 | 245.8 | 320.6 | 161.2 | 337.4 | 320.3 | 249.7 | 284.2 | 356.8 | 242.4
1002 | 812 | 567.5 | 227 | 265.3499 | 357.5 | 304 | 322.4 | 300 | 623.5 | 57.9 | 19.3 | 97.2 | 5 | 224.6 | 5.5 | 931.3 | 891.9 | 864.7 | 904.8 | 919.9 | 813 | 743.5 | 783.9 | 794.7 | 809.1 | 246 | 320.8 | 161.5 | 337.5 | 320.3 | 250.1 | 284.4 | 357.1 | 242.6
1003 | 813 | 568.1 | 227.24 | 265.6305 | 359.2 | 304.3 | 322.3 | 299.7 | 628.2 | 58 | 19.3 | 97.3 | 5 | 255.7 | 5.2 | 930.6 | 895.4 | 863.2 | 906.3 | 925.8 | 813.2 | 742.8 | 784.6 | 795 | 808.3 | 246.2 | 320.7 | 161.8 | 337.5 | 320.3 | 250.6 | 284.5 | 357.4 | 242.9
1004 | 814 | 568.5 | 227.4 | 265.8175 | 359.8 | 304.4 | 321.8 | 299.1 | 625.8 | 58.2 | 19.3 | 97.4 | 5.2 | 263.4 | 5 | 930.3 | 902.4 | 856.2 | 907.1 | 929.5 | 813.9 | 740.1 | 787.5 | 794.6 | 805.8 | 246.3 | 320.9 | 162.2 | 337.4 | 319.9 | 251 | 284.6 | 357.7 | 243.1
1005 | 815 | 568.1 | 227.24 | 265.6305 | 360.4 | 304.7 | 322 | 299.2 | 624.8 | 58.2 | 19.3 | 97.5 | 5 | 220 | 5.4 | 930.3 | 892.9 | 853.1 | 902.2 | 928.6 | 814.4 | 735.1 | 787.9 | 792.5 | 803.2 | 246.5 | 321 | 162.5 | 337.4 | 319.6 | 251.3 | 284.7 | 358 | 243.3
1006 | 816 | 567.7 | 227.08 | 265.4434 | 360.6 | 305.3 | 322.1 | 299.3 | 628.4 | 58.3 | 19.3 | 97.5 | 5 | 221.2 | 6 | 930.6 | 890.5 | 854.9 | 903.2 | 926.4 | 814.7 | 736.2 | 790.8 | 791.1 | 803 | 246.7 | 321.2 | 162.8 | 337.4 | 319.4 | 251.7 | 284.7 | 358.3 | 243.6
1007 | 817 | 567.3 | 226.92 | 265.2564 | 361.1 | 306.1 | 322.9 | 299.9 | 637 | 58.3 | 19.3 | 97.7 | 4.9 | 225.9 | 7 | 930.8 | 893.8 | 860.6 | 905.5 | 924.3 | 815.4 | 732.5 | 790.3 | 787.7 | 801.2 | 246.9 | 321.2 | 163.2 | 337.2 | 319.3 | 252.2 | 284.8 | 358.5 | 243.8
1008 | 818 | 567 | 226.8 | 265.1161 | 361.4 | 306.6 | 323.2 | 300.4 | 639.9 | 58.3 | 19.3 | 97.7 | 4.4 | 215.4 | 7.4 | 931.6 | 894.1 | 860.8 | 906.9 | 923 | 815.7 | 731.7 | 789.9 | 787 | 801.6 | 247.2 | 321.4 | 163.5 | 337.2 | 319.2 | 252.7 | 284.8 | 358.8 | 244.1
1009 | 819 | 566.4 | 226.56 | 264.8356 | 359.9 | 306.8 | 323.6 | 300.3 | 631.9 | 58.3 | 19.3 | 97.7 | 4.5 | 220.2 | 7.8 | 932.6 | 893.7 | 857.8 | 902.2 | 921.2 | 815.8 | 728.1 | 787 | 784.7 | 801.1 | 247.4 | 321.4 | 163.8 | 337.3 | 319.2 | 253.2 | 285 | 359.1 | 244.3
1010 | 820 | 566.5 | 226.6 | 264.8823 | 358.7 | 307.1 | 324.1 | 300.3 | 616.1 | 58.2 | 19.3 | 97.7 | 4.5 | 244.8 | 6.4 | 932.9 | 894.1 | 856.3 | 904.5 | 922.5 | 815.6 | 725.9 | 784.5 | 783.4 | 801.2 | 247.7 | 321.3 | 164.2 | 337.2 | 319.1 | 253.7 | 285 | 359.4 | 244.5
1011 | 821 | 566.9 | 226.76 | 265.0694 | 359.3 | 307.4 | 323.8 | 300.3 | 608 | 58.2 | 19.3 | 97.7 | 5.3 | 226.3 | 5.2 | 933.7 | 892.9 | 852 | 901.5 | 924.3 | 816.1 | 722.9 | 779.4 | 780.9 | 799.7 | 247.9 | 321.5 | 164.5 | 337.3 | 318.9 | 254.2 | 285.1 | 359.6 | 244.7
1012 | 822 | 566.3 | 226.52 | 264.7888 | 359.9 | 307.6 | 323.6 | 300.1 | 600.6 | 58.1 | 19.3 | 97.8 | 5.4 | 224.8 | 4.7 | 934.2 | 894.7 | 854.1 | 899.5 | 921.9 | 816.4 | 721.9 | 781.2 | 779.5 | 799.6 | 248.2 | 321.7 | 164.9 | 337.4 | 318.7 | 254.7 | 285.2 | 359.9 | 244.9
1013 | 823 | 567.8 | 227.12 | 265.4902 | 358.5 | 307.4 | 323.3 | 300.1 | 600.9 | 58.2 | 19.3 | 98 | 5.6 | 221.5 | 5.5 | 933.2 | 895.7 | 851.4 | 902.8 | 920.3 | 816.3 | 727.3 | 785 | 782.2 | 800.6 | 248.5 | 322.2 | 165.2 | 337.4 | 318.8 | 255.1 | 285.3 | 360.1 | 245.1
1014 | 824 | 567.8 | 227.12 | 265.4902 | 357.5 | 307.7 | 322.6 | 300.2 | 601.1 | 58.2 | 19.3 | 98.1 | 4.6 | 232.6 | 6.7 | 932.5 | 896.8 | 849.3 | 903.6 | 921.2 | 816.2 | 730.6 | 786.7 | 784.3 | 801.6 | 248.9 | 322.2 | 165.5 | 337.3 | 318.6 | 255.6 | 285.4 | 360.4 | 245.4
1015 | 825 | 568.4 | 227.36 | 265.7707 | 357 | 308 | 322.2 | 300.7 | 598.8 | 58.3 | 19.3 | 98.2 | 4.3 | 223.1 | 7 | 932.6 | 881.8 | 845 | 899 | 922.5 | 816.4 | 722.9 | 785.4 | 779.9 | 797 | 249.3 | 322.8 | 165.9 | 337.3 | 318.4 | 256 | 285.4 | 360.7 | 245.6
1016 | 826 | 567.6 | 227.04 | 265.3967 | 357.3 | 308 | 322.2 | 300.6 | 606.7 | 58.4 | 19.3 | 98.3 | 4.1 | 241.9 | 6 | 932.6 | 882 | 847.2 | 900.3 | 919.6 | 817.2 | 718.3 | 786.3 | 775.1 | 795.2 | 249.7 | 323.3 | 166.2 | 337.1 | 318.2 | 256.4 | 285.5 | 360.9 | 245.8
1017 | 827 | 567.7 | 227.08 | 265.4434 | 357.3 | 308 | 321.7 | 300.5 | 623.5 | 58.5 | 19.3 | 98.3 | 4.6 | 233.1 | 5.3 | 931.8 | 881.4 | 850.9 | 902.7 | 919.5 | 817.6 | 720.6 | 787 | 777.4 | 795.8 | 250.1 | 323.8 | 166.6 | 337 | 317.9 | 256.8 | 285.7 | 361.2 | 246.1
1018 | 828 | 567.8 | 227.12 | 265.4902 | 357.4 | 308.4 | 322.4 | 300.2 | 634.7 | 58.5 | 19.3 | 98.3 | 4.9 | 219.4 | 5.7 | 931.3 | 881.7 | 852 | 902.5 | 917.5 | 817.8 | 719.8 | 787.7 | 776.6 | 794.2 | 250.6 | 324.6 | 166.9 | 336.6 | 317.7 | 257.2 | 285.7 | 361.4 | 246.3
1019 | 829 | 567.6 | 227.04 | 265.3967 | 357.8 | 308.8 | 323.6 | 300.2 | 643.9 | 58.6 | 19.3 | 98.4 | 4.5 | 220.5 | 6 | 931.4 | 882.1 | 846.1 | 902.1 | 912.2 | 817.8 | 723.2 | 790.8 | 779.6 | 794.8 | 251 | 325.3 | 167.3 | 336.5 | 317.6 | 257.6 | 285.7 | 361.7 | 246.5
1020 | 830 | 568.4 | 227.36 | 265.7707 | 358.5 | 308.7 | 323.6 | 300.3 | 633.5 | 58.5 | 19.3 | 98.4 | 4.4 | 252.8 | 5.7 | 932 | 882.8 | 845.6 | 899.8 | 915.8 | 817.8 | 723.2 | 790.1 | 778.6 | 795.7 | 251.6 | 325.4 | 167.6 | 336.5 | 317.5 | 258 | 285.8 | 362 | 246.7
1021 | 831 | 566.9 | 226.76 | 265.0694 | 358.3 | 308.5 | 323.7 | 300.8 | 624.5 | 58.5 | 19.3 | 98.5 | 3.9 | 246.9 | 5.5 | 931.8 | 885.1 | 842.4 | 900.3 | 917.9 | 817.3 | 727.8 | 788.1 | 780.9 | 797.5 | 252.1 | 325.3 | 167.9 | 336.3 | 317.4 | 258.4 | 285.9 | 362.2 | 247
1022 | 832 | 566.1 | 226.44 | 264.6953 | 358 | 308.6 | 323.4 | 300.8 | 605.4 | 58.5 | 19.3 | 98.5 | 4.7 | 233 | 6.1 | 931.2 | 885.7 | 839.3 | 900.1 | 913.2 | 816.5 | 728.3 | 780.3 | 781 | 798.6 | 252.6 | 325.1 | 168.3 | 336.8 | 317.4 | 258.7 | 286.2 | 362.5 | 247.2
1023 | 833 | 565.9 | 226.36 | 264.6018 | 358.6 | 308.7 | 322.4 | 300.9 | 589.2 | 58.5 | 19.3 | 98.5 | 4.6 | 242.4 | 6.6 | 930.1 | 884.1 | 837.2 | 900.7 | 912.2 | 815.8 | 732.8 | 771.9 | 782.1 | 800 | 253.1 | 324.8 | 168.6 | 337.2 | 317.3 | 259.1 | 286.3 | 362.7 | 247.4
1024 | 834 | 566.3 | 226.52 | 264.7888 | 359.5 | 308.8 | 322.1 | 300.9 | 573.9 | 58.6 | 19.3 | 98.6 | 3.8 | 240.5 | 7 | 930 | 888.9 | 841 | 902.5 | 920.1 | 815.4 | 735 | 774 | 782.7 | 800.1 | 253.6 | 324.2 | 168.9 | 337.2 | 317.7 | 259.5 | 286.5 | 363 | 247.6
1025 | 835 | 566.8 | 226.72 | 265.0226 | 359.7 | 308.6 | 321.9 | 300.2 | 569.1 | 58.6 | 19.3 | 98.7 | 3.7 | 244.9 | 7.3 | 929.8 | 892.6 | 842.3 | 904.1 | 925.2 | 815.1 | 736.4 | 778.1 | 783.4 | 800.7 | 254.1 | 323.7 | 169.3 | 337.4 | 317.9 | 259.9 | 286.6 | 363.2 | 247.9
1026 | 836 | 566.7 | 226.68 | 264.9759 | 359.3 | 308.1 | 321.4 | 300 | 570.8 | 58.7 | 19.3 | 98.7 | 4.1 | 256.6 | 7.3 | 929.3 | 895.2 | 846.5 | 907.4 | 929.4 | 815.1 | 738.7 | 773.3 | 784.4 | 801.6 | 254.5 | 323.2 | 169.6 | 337.7 | 318.3 | 260.2 | 286.8 | 363.4 | 248.1
1027 | 837 | 565.9 | 226.36 | 264.6018 | 358.7 | 308.1 | 321.3 | 300.8 | 570.8 | 58.7 | 19.3 | 98.7 | 3.9 | 255.4 | 7.1 | 928.9 | 887.5 | 854 | 910.3 | 929.9 | 814.5 | 742.2 | 775.3 | 785.3 | 802.5 | 255 | 323.1 | 169.9 | 337.9 | 318.7 | 260.6 | 287 | 363.7 | 248.3
1028 | 838 | 565.8 | 226.32 | 264.555 | 359 | 308.7 | 321.4 | 301.4 | 576.9 | 58.7 | 19.3 | 98.8 | 4.5 | 250.9 | 7.1 | 928.4 | 889.4 | 859.7 | 911.3 | 932.2 | 813.3 | 744 | 780.3 | 786.2 | 803.2 | 255.4 | 323.2 | 170.3 | 338 | 319 | 260.8 | 287.1 | 364 | 248.6
1029 | 839 | 566 | 226.4 | 264.6486 | 358.4 | 308.9 | 320.6 | 301.2 | 584.9 | 58.7 | 19.3 | 98.9 | 4.5 | 271.6 | 6.8 | 928.2 | 898.2 | 861.1 | 912.2 | 931.1 | 812.6 | 745.4 | 782.8 | 787.3 | 804.8 | 255.8 | 323.1 | 170.6 | 338.1 | 319.2 | 261.1 | 287.3 | 364.4 | 248.8
1030 | 840 | 567.2 | 226.88 | 265.2096 | 357.6 | 308.8 | 321.3 | 300.7 | 590.5 | 58.7 | 19.3 | 99 | 4.3 | 263.9 | 7.7 | 928.6 | 901.6 | 855.4 | 908.9 | 931.9 | 813 | 741.3 | 781.3 | 786.6 | 803.3 | 256.2 | 323.2 | 171 | 338.2 | 319 | 261.4 | 287.3 | 364.7 | 249
1031 | 841 | 567.7 | 227.08 | 265.4434 | 357.3 | 308.6 | 321.3 | 300.2 | 595.1 | 58.7 | 19.3 | 99 | 4.3 | 255 | 9 | 929.3 | 890.7 | 849.2 | 902.4 | 923.5 | 814 | 732.3 | 778.2 | 783.5 | 799.9 | 256.6 | 323.3 | 171.3 | 338.2 | 319.3 | 261.6 | 287.5 | 365 | 249.2
1032 | 842 | 567.7 | 227.08 | 265.4434 | 357.5 | 308.2 | 320.9 | 300.5 | 586.9 | 58.7 | 19.3 | 99 | 4.3 | 252.7 | 9.5 | 929.6 | 890.6 | 846.8 | 899.4 | 923.1 | 814.4 | 726.7 | 777.9 | 781.4 | 798.8 | 256.9 | 323.4 | 171.7 | 337.9 | 319.8 | 261.9 | 287.7 | 365.2 | 249.5
1033 | 843 | 567.4 | 226.96 | 265.3032 | 357.1 | 308 | 321 | 300.9 | 583.6 | 58.7 | 19.2 | 99 | 4.1 | 250 | 9.3 | 930.9 | 885.7 | 844.5 | 896.8 | 917 | 814.6 | 722.4 | 779.9 | 779.5 | 796.9 | 257.4 | 323.7 | 172 | 337.5 | 319.9 | 262.2 | 287.7 | 365.4 | 249.7
1034 | 844 | 564.8 | 225.92 | 264.0875 | 357.9 | 307.9 | 321.7 | 301 | 597.3 | 58.8 | 19.2 | 98.9 | 4 | 250.9 | 8.9 | 930.8 | 880.5 | 839.4 | 893.4 | 915.8 | 815.1 | 713.6 | 780.3 | 774.5 | 795.6 | 257.8 | 324.5 | 172.3 | 337.3 | 319.8 | 262.4 | 287.8 | 365.5 | 249.9
1035 | 845 | 563.3 | 225.32 | 263.3861 | 358.8 | 308 | 322.4 | 300.7 | 595.6 | 58.9 | 19.2 | 98.9 | 3.8 | 248 | 8.5 | 931.3 | 874 | 832.8 | 888 | 916.4 | 816 | 709.1 | 779.9 | 770.3 | 793.4 | 258.3 | 325.1 | 172.7 | 336.9 | 319.5 | 262.7 | 287.8 | 365.7 | 250.2
1036 | 846 | 564.3 | 225.72 | 263.8537 | 359 | 308.3 | 322.5 | 301.2 | 596.7 | 59 | 19.2 | 99 | 4 | 249.7 | 8.1 | 931.2 | 877.9 | 833.2 | 890 | 912.8 | 816.3 | 713.1 | 781.8 | 771.6 | 794 | 258.8 | 325.4 | 173 | 336.7 | 319.3 | 262.9 | 287.8 | 365.9 | 250.4
1037 | 847 | 564.8 | 225.92 | 264.0875 | 358.8 | 308.2 | 323 | 301.4 | 603.8 | 59 | 19.2 | 99 | 4.1 | 248.4 | 7.5 | 931.2 | 883.9 | 836.3 | 893.7 | 918.5 | 816.3 | 716.3 | 779.3 | 773.8 | 794.9 | 259.2 | 325.3 | 173.4 | 336.9 | 318.9 | 263.2 | 288 | 366.1 | 250.6
1038 | 848 | 568 | 227.2 | 265.5837 | 359.9 | 308.3 | 323 | 301.1 | 584.2 | 59.1 | 19.2 | 99.1 | 4 | 244.6 | 7.3 | 931 | 884.5 | 839.7 | 896.4 | 920.7 | 816 | 716 | 774.1 | 773.5 | 796.1 | 259.8 | 325.5 | 173.7 | 337.1 | 318.5 | 263.5 | 288.2 | 366.3 | 250.8
1039 | 849 | 566.6 | 226.64 | 264.9291 | 359.6 | 308.6 | 322.9 | 301.2 | 574.8 | 59.1 | 19.2 | 99.1 | 4.3 | 250.2 | 7.4 | 930.9 | 881.4 | 834.1 | 894.5 | 923.2 | 815.3 | 713.5 | 767.5 | 770.9 | 796 | 260.3 | 326.1 | 174 | 337.4 | 318.8 | 263.8 | 288.3 | 366.5 | 251
1040 | 850 | 566.5 | 226.6 | 264.8823 | 359 | 308.9 | 323 | 301.4 | 563.3 | 59.2 | 19.2 | 99.2 | 4.4 | 246.7 | 7.2 | 931.8 | 885 | 833.4 | 892.4 | 930.1 | 814.3 | 709.4 | 758 | 767 | 795.4 | 260.8 | 326.1 | 174.4 | 337.3 | 319.4 | 264.1 | 288.5 | 366.7 | 251.2
1041 | 851 | 566.1 | 226.44 | 264.6953 | 358.7 | 309.1 | 322.6 | 301.3 | 558 | 59.3 | 19.2 | 99.2 | 4.5 | 249.7 | 6.8 | 933.1 | 877.2 | 829.3 | 887.5 | 932 | 813.4 | 706.8 | 752.5 | 763.3 | 796.3 | 261.3 | 326 | 174.7 | 337.3 | 319.5 | 264.4 | 288.7 | 366.8 | 251.4
1042 | 852 | 565.8 | 226.32 | 264.555 | 358.4 | 309.1 | 323 | 301.2 | 546.2 | 59.4 | 19.2 | 99.2 | 4.2 | 250 | 6.8 | 933 | 869.7 | 826.2 | 886.8 | 925.2 | 812.5 | 702.8 | 749.8 | 758.9 | 796.8 | 261.8 | 326 | 175 | 337.3 | 319.7 | 264.6 | 288.9 | 367 | 251.7
1043 | 853 | 568.4 | 227.36 | 265.7707 | 359 | 309.1 | 323.1 | 301.3 | 537.2 | 59.4 | 19.2 | 99.1 | 4.3 | 249.7 | 6.7 | 932.2 | 868.1 | 829 | 890.6 | 928.1 | 811.4 | 704 | 744.2 | 757.9 | 796.4 | 262.3 | 326 | 175.4 | 337.4 | 320 | 264.9 | 289 | 367.2 | 251.9
1044 | 854 | 567.7 | 227.08 | 265.4434 | 359.5 | 309.1 | 322.6 | 301 | 524.6 | 59.5 | 19.2 | 99 | 4.1 | 245.3 | 6.6 | 932.1 | 868.5 | 829.4 | 893.5 | 930.6 | 810.2 | 701.1 | 742.6 | 754.5 | 795.4 | 262.8 | 325.5 | 175.7 | 337.7 | 320.1 | 265.2 | 289.2 | 367.3 | 252.1
1045 | 855 | 566.4 | 226.56 | 264.8356 | 359.9 | 309.1 | 322.7 | 301.6 | 518.6 | 59.5 | 19.2 | 99.1 | 4.2 | 247.6 | 6.5 | 931.8 | 870.4 | 834.5 | 895 | 934.5 | 809 | 704.2 | 743.1 | 755.3 | 797.1 | 263.2 | 324.8 | 176 | 337.8 | 320.1 | 265.5 | 289.3 | 367.5 | 252.3
1046 | 856 | 566.8 | 226.72 | 265.0226 | 360.2 | 308.2 | 322.5 | 301.8 | 518 | 59.6 | 19.2 | 99.2 | 3.9 | 249.6 | 6.7 | 931.2 | 872.5 | 838.8 | 897 | 936.6 | 808.3 | 711.2 | 750.1 | 758.1 | 798.8 | 263.7 | 324.2 | 176.4 | 337.8 | 320.6 | 265.7 | 289.4 | 367.7 | 252.6
1047 | 857 | 567.7 | 227.08 | 265.4434 | 360.4 | 307.3 | 322.7 | 300.7 | 540.9 | 59.6 | 19.2 | 99.3 | 4.7 | 247.7 | 6.7 | 930.7 | 871.7 | 845.4 | 899.5 | 935.6 | 808.1 | 714.4 | 759.1 | 760.3 | 798.1 | 264 | 323.8 | 176.7 | 337.6 | 320.7 | 266 | 289.5 | 367.9 | 252.8
1048 | 858 | 567.4 | 226.96 | 265.3032 | 359.1 | 307 | 322.9 | 300.4 | 558.2 | 59.6 | 19.2 | 99.6 | 4.4 | 250.6 | 6.5 | 930.7 | 874.3 | 847.4 | 903.8 | 932.8 | 807.9 | 718.5 | 761.1 | 762.1 | 799.3 | 264.4 | 323.5 | 177 | 337.6 | 321 | 266.3 | 289.7 | 368.2 | 253
1049 | 859 | 567.6 | 227.04 | 265.3967 | 357.8 | 306.4 | 323.4 | 300.2 | 552.3 | 59.7 | 19.2 | 99.8 | 4 | 251.2 | 6.7 | 930.6 | 875.7 | 841.5 | 902.1 | 935.3 | 807.1 | 719.9 | 755 | 762.8 | 800 | 264.7 | 323.2 | 177.3 | 337.5 | 321.5 | 266.5 | 289.8 | 368.4 | 253.2
1050 | 860 | 567.4 | 226.96 | 265.3032 | 358 | 305.9 | 323.4 | 299.5 | 542.3 | 59.8 | 19.2 | 99.9 | 4.2 | 248.7 | 7.2 | 930.3 | 875.5 | 834 | 897.4 | 933.8 | 806.5 | 721.1 | 754.6 | 763.4 | 800.7 | 265.1 | 323.3 | 177.6 | 337.2 | 322 | 266.7 | 289.9 | 368.6 | 253.4
1051 | 861 | 567.4 | 226.96 | 265.3032 | 358.2 | 305.5 | 322.6 | 299.1 | 539.2 | 59.8 | 19.2 | 100.1 | 4.2 | 246 | 7.9 | 931.3 | 867.9 | 827.9 | 889.4 | 933.3 | 806.8 | 714.8 | 750.4 | 759.8 | 800.5 | 265.4 | 323.4 | 177.9 | 337.2 | 322.3 | 266.8 | 290 | 368.9 | 253.6
1052 | 862 | 567.2 | 226.88 | 265.2096 | 358.7 | 305.2 | 322.9 | 299.5 | 535 | 59.9 | 19.2 | 100.3 | 4 | 249.8 | 9.3 | 933.3 | 870.4 | 826.1 | 884.4 | 934.7 | 807.2 | 713.2 | 749.6 | 758.3 | 801.1 | 265.7 | 323.6 | 178.2 | 337.3 | 322.5 | 266.9 | 290 | 369 | 253.8
1053 | 863 | 567 | 226.8 | 265.1161 | 359.5 | 304.9 | 323.7 | 299.8 | 542.4 | 59.9 | 19.2 | 100.4 | 4.2 | 253 | 9.8 | 933.1 | 874.2 | 833 | 891 | 931.1 | 807.4 | 720.5 | 756.9 | 762.4 | 803 | 266.1 | 323.4 | 178.5 | 337.7 | 322.8 | 267 | 290.2 | 369.2 | 254.1
1054 | 864 | 566.8 | 226.72 | 265.0226 | 360 | 304.9 | 324.1 | 299.5 | 565.6 | 59.9 | 19.2 | 100.4 | 4.5 | 246.8 | 9.9 | 931.9 | 878.2 | 833.7 | 896.3 | 924.9 | 807.2 | 729.4 | 763.8 | 767.6 | 803.8 | 266.4 | 323.6 | 178.8 | 337.7 | 322.9 | 267.1 | 290.2 | 369.4 | 254.3
1055 | 865 | 567.7 | 227.08 | 265.4434 | 360.1 | 305.2 | 324.2 | 299.5 | 584.2 | 60 | 19.2 | 100.5 | 4.4 | 247.4 | 9.4 | 930.3 | 884.2 | 831.1 | 895.7 | 924.1 | 806.9 | 731.7 | 765.8 | 770.8 | 805.3 | 266.8 | 323.6 | 179.2 | 338.2 | 322.7 | 267.2 | 290.3 | 369.6 | 254.5
1056 | 866 | 568.7 | 227.48 | 265.911 | 359.6 | 305.2 | 323.9 | 299.9 | 589.2 | 60 | 19.2 | 100.6 | 5.1 | 264.9 | 8.9 | 929.4 | 883.8 | 837.4 | 897.5 | 922.8 | 807.2 | 734.5 | 773.1 | 772.4 | 807.3 | 267.1 | 323.5 | 179.5 | 338.2 | 322.6 | 267.4 | 290.3 | 370 | 254.8
1057 | 867 | 567.8 | 227.12 | 265.4902 | 359.2 | 305 | 324.3 | 300.3 | 601.6 | 60 | 19.2 | 100.8 | 5.9 | 267.5 | 8.7 | 927.8 | 885.3 | 830.3 | 899.2 | 916.7 | 806.9 | 739.8 | 774.1 | 774.6 | 807.5 | 267.5 | 323.2 | 179.8 | 338.3 | 322.9 | 267.5 | 290.5 | 370.2 | 255
1058 | 868 | 568.3 | 227.32 | 265.724 | 358.8 | 304.8 | 325.1 | 301 | 594 | 59.9 | 19.2 | 100.9 | 6.1 | 259.6 | 8.4 | 927.2 | 881.7 | 828.6 | 896.6 | 927.2 | 806.9 | 736 | 768.2 | 773.9 | 807.9 | 267.8 | 322.9 | 180.1 | 338.5 | 323 | 267.6 | 290.6 | 370.5 | 255.2
1059 | 869 | 566.8 | 226.72 | 265.0226 | 358.8 | 305.2 | 324.9 | 301.3 | 577.9 | 59.9 | 19.2 | 100.9 | 5.2 | 280.3 | 7.4 | 926.7 | 879.5 | 831.1 | 897 | 932.3 | 806.9 | 735.6 | 768.8 | 774.4 | 808.1 | 268.1 | 322.8 | 180.4 | 338.6 | 323 | 267.7 | 290.8 | 370.8 | 255.5
1060 | 870 | 567.1 | 226.84 | 265.1629 | 360.1 | 305.3 | 323.9 | 301.4 | 562.6 | 60 | 19.2 | 100.8 | 5.2 | 278.4 | 6.5 | 926.3 | 882.6 | 828.8 | 899.3 | 929.9 | 806.5 | 736.7 | 762.5 | 774.6 | 808.9 | 268.4 | 322.6 | 180.7 | 338.4 | 323.2 | 267.8 | 291 | 371 | 255.7
1061 | 871 | 567.2 | 226.88 | 265.2096 | 361.6 | 305.6 | 323.6 | 301.2 | 552.7 | 60 | 19.2 | 100.8 | 4.7 | 254.9 | 7.2 | 926.7 | 881.6 | 828.9 | 898.1 | 934.3 | 806.7 | 733.5 | 767.5 | 774.2 | 808.5 | 268.7 | 322.5 | 181 | 338.2 | 323.2 | 267.8 | 291 | 371.2 | 255.9
1062 | 872 | 568.4 | 227.36 | 265.7707 | 361 | 306.1 | 323.7 | 300.2 | 562.5 | 60.1 | 19.2 | 100.7 | 4.3 | 257.7 | 7.5 | 926.4 | 877.3 | 829.5 | 897.4 | 932 | 807.1 | 734.6 | 772.1 | 774.9 | 808.3 | 269 | 322.7 | 181.2 | 338.1 | 323.7 | 267.9 | 291.1 | 371.4 | 256.1
1063 | 873 | 568.1 | 227.24 | 265.6305 | 360.6 | 306.4 | 324.2 | 299.9 | 573.8 | 60.1 | 19.2 | 100.8 | 4.3 | 259.3 | 8.4 | 925.8 | 868.7 | 827.4 | 894.2 | 934.6 | 807.5 | 727.3 | 766.3 | 772.7 | 805.5 | 269.3 | 322.6 | 181.5 | 338.2 | 324.1 | 267.9 | 291.2 | 371.6 | 256.3
1064 | 874 | 565.8 | 226.32 | 264.555 | 360.8 | 306.5 | 325.4 | 299.5 | 560.7 | 60.1 | 19.2 | 100.8 | 4.6 | 267.1 | 9 | 926 | 866 | 829.2 | 894.8 | 936.3 | 807.3 | 722.2 | 757.3 | 768.4 | 804.5 | 269.6 | 322.7 | 181.8 | 338.4 | 324.7 | 268 | 291.3 | 371.7 | 256.5
1065 | 875 | 566.9 | 226.76 | 265.0694 | 360.5 | 306.5 | 326.4 | 299.4 | 552.5 | 60.1 | 19.2 | 100.8 | 4.9 | 265.2 | 8.8 | 926.3 | 865.4 | 827.9 | 893.3 | 939.6 | 806.6 | 720.8 | 753.3 | 766.3 | 804.6 | 269.9 | 323.1 | 182.1 | 338.4 | 325.7 | 268.1 | 291.6 | 371.9 | 256.7
1066 | 876 | 565.8 | 226.32 | 264.555 | 360.3 | 306.4 | 326.7 | 299.7 | 540.1 | 60.1 | 19.2 | 100.9 | 4.9 | 269.5 | 9.4 | 926.8 | 868.8 | 824.4 | 892.3 | 938.4 | 805.2 | 721.7 | 747.3 | 764.3 | 804.2 | 270.2 | 323.6 | 182.4 | 339.3 | 326 | 268.2 | 291.7 | 372.1 | 257
1067 | 877 | 567 | 226.8 | 265.1161 | 360.8 | 306.4 | 326.7 | 300.2 | 533.3 | 60.1 | 19.2 | 101 | 4.2 | 263.7 | 9.2 | 926.9 | 873 | 826.2 | 893.7 | 934.2 | 803.9 | 726.7 | 749.7 | 766.2 | 804.9 | 270.5 | 324.1 | 182.7 | 339.6 | 326.3 | 268.3 | 291.8 | 372.3 | 257.2
1068 | 878 | 568.1 | 227.24 | 265.6305 | 360.9 | 306.2 | 326.5 | 300.8 | 530.1 | 60 | 19.2 | 101 | 4.1 | 281.2 | 8.2 | 926.1 | 873.8 | 834.9 | 899.9 | 937.4 | 803 | 731.7 | 754.3 | 768.6 | 805.6 | 270.8 | 324.2 | 183 | 339.7 | 326.5 | 268.4 | 291.8 | 372.6 | 257.4
1069 | 879 | 567.2 | 226.88 | 265.2096 | 361.4 | 306.6 | 326.4 | 300.7 | 535.3 | 60 | 19.2 | 100.9 | 4 | 263 | 8.2 | 925.4 | 877 | 844.6 | 905.4 | 937.8 | 802.2 | 735.7 | 755.8 | 771.3 | 806.5 | 271.2 | 323.9 | 183.3 | 340.1 | 326.7 | 268.5 | 292 | 372.9 | 257.6
1070 | 880 | 566.6 | 226.64 | 264.9291 | 362 | 306.7 | 326.2 | 300.6 | 533.5 | 60.1 | 19.2 | 100.9 | 4.5 | 237.9 | 8.3 | 925.7 | 881.5 | 851.3 | 909.9 | 937.7 | 801.9 | 738.3 | 757.7 | 772.4 | 807.4 | 271.5 | 323.8 | 183.6 | 340.8 | 327.2 | 268.6 | 292.3 | 373.2 | 257.8
1071 | 881 | 566.8 | 226.72 | 265.0226 | 361.8 | 307.2 | 325.6 | 300.7 | 537.8 | 60.1 | 19.2 | 100.9 | 4.6 | 258 | 8.7 | 926.2 | 886.6 | 851.7 | 912.4 | 935.3 | 801.9 | 738.1 | 762.5 | 772.9 | 807.7 | 271.8 | 323.6 | 183.9 | 341.1 | 327.8 | 268.7 | 292.5 | 373.5 | 258.1
1072 | 882 | 566.9 | 226.76 | 265.0694 | 362.1 | 307.5 | 325 | 300.3 | 549.2 | 60.2 | 19.2 | 100.9 | 4.8 | 261.8 | 9.3 | 926 | 893.6 | 849.6 | 912.9 | 936.6 | 802.4 | 740.9 | 765.4 | 774.6 | 808.2 | 272 | 323.7 | 184.2 | 341.1 | 328.4 | 268.8 | 292.7 | 373.8 | 258.3
1073 | 883 | 566.9 | 226.76 | 265.0694 | 363.7 | 308 | 323.4 | 300.3 | 578.5 | 60.1 | 19.2 | 100.9 | 4.6 | 277.7 | 10.3 | 925.7 | 892.2 | 852.6 | 910.1 | 935.4 | 803.2 | 744.3 | 772.5 | 777.6 | 808.8 | 272.3 | 323.9 | 184.5 | 341.5 | 328.9 | 268.9 | 292.8 | 374 | 258.5
1074 | 884 | 566.8 | 226.72 | 265.0226 | 364.6 | 308.4 | 323.5 | 300.3 | 593 | 60.1 | 19.2 | 100.9 | 4.1 | 271.7 | 9.5 | 926 | 897.8 | 855.9 | 913.1 | 937.9 | 803.7 | 745.8 | 776.9 | 780.5 | 809.6 | 272.6 | 324.1 | 184.8 | 341.8 | 329.3 | 269 | 292.9 | 374.3 | 258.8
1075 | 885 | 566.2 | 226.48 | 264.7421 | 364.3 | 308.7 | 324.6 | 300.3 | 585.7 | 60.2 | 19.2 | 100.9 | 4.2 | 274.9 | 8.4 | 927.2 | 900.3 | 858.3 | 914.9 | 939.3 | 804.2 | 746.7 | 775.9 | 782 | 810.2 | 272.9 | 324.1 | 185.1 | 341.9 | 329.2 | 269 | 293.1 | 374.5 | 259
1076 | 886 | 567 | 226.8 | 265.1161 | 365.2 | 309 | 325.4 | 300.4 | 588.1 | 60.2 | 19.2 | 100.9 | 4.1 | 284.8 | 7.7 | 927.4 | 902.4 | 857.9 | 915.8 | 935.7 | 804.2 | 744.5 | 775.9 | 783.1 | 810.4 | 273.1 | 324.2 | 185.3 | 341.8 | 328.8 | 269.1 | 293.1 | 374.8 | 259.2
1077 | 887 | 566.6 | 226.64 | 264.9291 | 366.3 | 309.1 | 325.7 | 300.4 | 593.2 | 60.2 | 19.2 | 100.9 | 3.9 | 271.2 | 8.1 | 927.1 | 906.2 | 854.7 | 915.5 | 926.8 | 804.2 | 746.3 | 774.8 | 785.3 | 811.6 | 273.4 | 324.3 | 185.6 | 341.7 | 328.7 | 269.1 | 293.2 | 375 | 259.4
1078 | 888 | 567.2 | 226.88 | 265.2096 | 367 | 309.2 | 324.8 | 300.7 | 583.3 | 60.2 | 19.2 | 100.9 | 3.8 | 267.7 | 8.5 | 927.6 | 901.4 | 850.3 | 912.9 | 930.6 | 804.3 | 749.1 | 770.4 | 786.7 | 812.6 | 273.6 | 324.4 | 185.9 | 341.8 | 329.4 | 269.2 | 293.5 | 375.2 | 259.7
1079 | 889 | 567 | 226.8 | 265.1161 | 367.4 | 309.5 | 324.3 | 300.5 | 568.4 | 60.2 | 19.2 | 100.9 | 4.2 | 272.2 | 8.3 | 928.4 | 889.4 | 845.6 | 907.8 | 936.5 | 804.2 | 744 | 758.7 | 784 | 813.5 | 273.9 | 324.3 | 186.2 | 342.1 | 329.9 | 269.3 | 293.8 | 375.5 | 259.9
1080 | 890 | 566.6 | 226.64 | 264.9291 | 366.6 | 309.8 | 324.7 | 300.6 | 550 | 60.3 | 19.2 | 100.8 | 4 | 269.8 | 7.9 | 929.9 | 884.5 | 841.7 | 901 | 933.2 | 803.4 | 740.6 | 745.9 | 780.5 | 814.7 | 274.1 | 324.3 | 186.5 | 342.2 | 330 | 269.4 | 293.9 | 375.7 | 260.1
1081 | 891 | 566.1 | 226.44 | 264.6953 | 365.4 | 310 | 324.3 | 301.4 | 539.8 | 60.3 | 19.1 | 100.8 | 4 | 272.9 | 7.9 | 929.6 | 888.6 | 839.5 | 899.6 | 934.4 | 802.9 | 743.7 | 748.5 | 781.8 | 815.4 | 274.3 | 324.5 | 186.8 | 342.1 | 330.2 | 269.5 | 294 | 375.9 | 260.4
1082 | 892 | 569.2 | 227.68 | 266.1448 | 364.2 | 310 | 324.4 | 302.3 | 547.2 | 60.4 | 19.2 | 100.7 | 3.9 | 265.7 | 7.6 | 929.6 | 891.3 | 842.7 | 902.4 | 932.8 | 803.1 | 744.5 | 756.7 | 783.3 | 814.4 | 274.5 | 324.8 | 187.1 | 342.1 | 330.8 | 269.6 | 294.1 | 376.1 | 260.6
1083 | 893 | 569.2 | 227.68 | 266.1448 | 362.8 | 310 | 324.1 | 302.9 | 562.6 | 60.4 | 19.1 | 100.7 | 4.3 | 264.6 | 7.2 | 929.5 | 887.3 | 839.6 | 903 | 932.2 | 803.5 | 741.6 | 758.8 | 783.8 | 814.1 | 274.8 | 324.9 | 187.4 | 341.8 | 331.7 | 269.7 | 294.3 | 376.3 | 260.8
1084 | 894 | 567.6 | 227.04 | 265.3967 | 361.6 | 309.9 | 324.5 | 302.7 | 552.6 | 60.5 | 19.1 | 100.7 | 4 | 265.7 | 6.5 | 929.5 | 887.2 | 837 | 900.9 | 927.8 | 803.5 | 737.2 | 757.2 | 781.6 | 814 | 275 | 324.9 | 187.7 | 341.5 | 331.7 | 269.8 | 294.4 | 376.6 | 261
1085 | 895 | 566.4 | 226.56 | 264.8356 | 359.9 | 309.8 | 324.4 | 302.7 | 549.6 | 60.6 | 19.1 | 100.7 | 4.6 | 266.3 | 5.9 | 929.2 | 884.5 | 832.8 | 901.4 | 934.8 | 804 | 730.9 | 756.7 | 778.9 | 812.8 | 275.3 | 325.5 | 188 | 341.3 | 331.8 | 269.8 | 294.5 | 376.7 | 261.3
1086 | 896 | 567.4 | 226.96 | 265.3032 | 359.7 | 309.7 | 323.7 | 302.9 | 551.7 | 60.5 | 19.1 | 100.7 | 4.4 | 263.8 | 5.6 | 929.7 | 873.8 | 822.8 | 894.8 | 935.2 | 804.4 | 720.4 | 752.4 | 772.1 | 810.1 | 275.5 | 325.9 | 188.3 | 341.2 | 331.3 | 269.9 | 294.5 | 376.9 | 261.5
1087 | 897 | 568 | 227.2 | 265.5837 | 359.3 | 309.7 | 322.7 | 302.6 | 549.3 | 60.5 | 19.1 | 100.8 | 4.4 | 257.5 | 5.2 | 929.4 | 861.3 | 816.5 | 888.7 | 932.7 | 804.3 | 713.9 | 746.4 | 766.2 | 809 | 275.7 | 325.9 | 188.6 | 341.1 | 330.6 | 270 | 294.5 | 377.1 | 261.7
1088 | 898 | 568 | 227.2 | 265.5837 | 359.3 | 309.7 | 322.7 | 302 | 555.3 | 60.4 | 19.1 | 100.9 | 4.5 | 274.7 | 4.6 | 928.8 | 866.3 | 818.8 | 889.3 | 931.7 | 804.7 | 716.1 | 752.5 | 765.2 | 808.1 | 276 | 325.8 | 188.9 | 340.6 | 330.4 | 270.1 | 294.5 | 377.2 | 261.9
1089 | 899 | 567.7 | 227.08 | 265.4434 | 358.5 | 309.8 | 322.4 | 302.1 | 576.7 | 60.5 | 19.1 | 101 | 4.6 | 272 | 4.6 | 928.2 | 874.5 | 820.2 | 891.4 | 931.1 | 804.6 | 721.3 | 755.6 | 767.7 | 808.1 | 276.2 | 325.5 | 189.2 | 340.3 | 330.1 | 270.1 | 294.4 | 377.3 | 262.1
1090 | 900 | 567.5 | 227 | 265.3499 | 357.4 | 309.6 | 322.5 | 301.8 | 584.5 | 60.4 | 19.1 | 101 | 4.9 | 265.4 | 5.4 | 927.1 | 880.7 | 827.3 | 895.1 | 936.5 | 804.7 | 723.4 | 761.1 | 768.9 | 808.8 | 276.4 | 325.5 | 189.5 | 340 | 329.5 | 270.2 | 294.4 | 377.5 | 262.3
1091 | 901 | 567.8 | 227.12 | 265.4902 | 356.1 | 310.1 | 323.3 | 301.1 | 602.1 | 60.4 | 19.1 | 101.1 | 4.9 | 281.8 | 6.9 | 927.9 | 879.8 | 827.3 | 893.4 | 932.4 | 805.4 | 723.1 | 771.4 | 769.2 | 807.1 | 276.7 | 325.6 | 189.8 | 339.9 | 329 | 270.2 | 294.4 | 377.7 | 262.5
1092 | 902 | 567.8 | 227.12 | 265.4902 | 356.1 | 310.3 | 323.8 | 301.1 | 616.1 | 60.5 | 19.1 | 101.2 | 4.7 | 272.3 | 7.9 | 927.3 | 871.7 | 820.6 | 889.4 | 925.1 | 806.2 | 718.8 | 774 | 767.7 | 803.1 | 276.9 | 325.6 | 190.1 | 339.5 | 328.5 | 270.3 | 294.4 | 378 | 262.7
1093 | 903 | 567.3 | 226.92 | 265.2564 | 357.5 | 310.9 | 324.5 | 300.9 | 623.7 | 60.6 | 19.1 | 101.2 | 4.7 | 262 | 8.5 | 927.5 | 857.4 | 809.8 | 880.6 | 918.5 | 806.6 | 713.8 | 767.6 | 764.2 | 800.3 | 277.1 | 325.6 | 190.4 | 339.8 | 328.5 | 270.3 | 294.5 | 378.2 | 262.9
1094 | 904 | 567.4 | 226.96 | 265.3032 | 358.3 | 311.3 | 325.9 | 300.9 | 619.4 | 60.6 | 19.1 | 101.2 | 4.8 | 263.6 | 8 | 927 | 861.1 | 809.5 | 877 | 912.5 | 807.1 | 709.8 | 765.2 | 761.3 | 799.2 | 277.3 | 326.2 | 190.7 | 340.1 | 329 | 270.4 | 294.6 | 378.4 | 263.1
1095 | 905 | 566.4 | 226.56 | 264.8356 | 358.8 | 311.5 | 326.4 | 301.8 | 616.4 | 60.7 | 19.1 | 101.2 | 4.2 | 264.4 | 7.7 | 926.3 | 866.6 | 820.3 | 880.2 | 920.1 | 807.4 | 711.8 | 764.5 | 760.1 | 799.1 | 277.5 | 326.9 | 191 | 340.4 | 329.1 | 270.5 | 294.6 | 378.5 | 263.3
1096 | 906 | 567.1 | 226.84 | 265.1629 | 359.5 | 312 | 327 | 302.5 | 623.5 | 60.8 | 19.1 | 101.3 | 3.9 | 266.2 | 7.7 | 926 | 864.7 | 828.7 | 878.5 | 921.2 | 807.5 | 713.2 | 768.6 | 761 | 797.4 | 277.7 | 327.4 | 191.4 | 340.6 | 328.8 | 270.6 | 294.6 | 378.7 | 263.5
1097 | 907 | 567.8 | 227.12 | 265.4902 | 359.8 | 312.4 | 327.6 | 303.1 | 630.2 | 60.9 | 19.1 | 101.4 | 4.2 | 271.9 | 7.9 | 926.6 | 853.3 | 831 | 873.8 | 908.8 | 807.6 | 704.7 | 762.1 | 756.3 | 792.7 | 278 | 327.6 | 191.7 | 341.2 | 328.3 | 270.7 | 294.6 | 378.9 | 263.8
1098 | 908 | 568 | 227.2 | 265.5837 | 361 | 312.8 | 328.7 | 303.2 | 623.1 | 61 | 19.1 | 101.4 | 4.4 | 266.4 | 7.9 | 927.7 | 836.9 | 820.4 | 867 | 877.5 | 807.4 | 693.8 | 754.3 | 749.1 | 787.4 | 278.2 | 327.9 | 192 | 341.5 | 328.1 | 270.9 | 294.7 | 379.1 | 264
1099 | 909 | 567.6 | 227.04 | 265.3967 | 361.3 | 313.4 | 329.4 | 303 | 605 | 61 | 19.1 | 101.3 | 4.3 | 255.2 | 7.1 | 927 | 827 | 813.3 | 867.5 | 840.5 | 807 | 685.7 | 754.1 | 740.9 | 783.6 | 278.5 | 328.3 | 192.3 | 341.7 | 327.7 | 271 | 294.7 | 379.2 | 264.2
1100 | 910 | 567.3 | 226.92 | 265.2564 | 362 | 314 | 329.7 | 303.7 | 604.7 | 61.1 | 19.1 | 101.3 | 4.3 | 252.8 | 6.4 | 925.9 | 822.6 | 803.9 | 866.7 | 852.7 | 806.7 | 684.3 | 754.5 | 737.5 | 782.4 | 278.7 | 328.6 | 192.6 | 342.1 | 327.3 | 271.2 | 294.8 | 379.4 | 264.4
1101 | 911 | 565.4 | 226.16 | 264.368 | 364.4 | 314.4 | 330 | 304.3 | 594.7 | 61.1 | 19.1 | 101.3 | 4.2 | 255.1 | 6.1 | 925.4 | 824.6 | 799.7 | 865.6 | 876.8 | 806.2 | 686.5 | 753.2 | 736.4 | 784.1 | 278.9 | 329.1 | 193 | 342.3 | 326.9 | 271.3 | 294.9 | 379.6 | 264.7
1102 | 912 | 567.9 | 227.16 | 265.537 | 365.9 | 314.3 | 330.9 | 304.6 | 589.7 | 61.2 | 19.1 | 101.5 | 4.1 | 255.4 | 5.8 | 925 | 824.7 | 790.5 | 863 | 885.6 | 805.5 | 683.6 | 745.8 | 733.1 | 784.1 | 279.1 | 329.4 | 193.3 | 342.6 | 326.9 | 271.5 | 294.9 | 379.7 | 264.9
1103 | 913 | 568.1 | 227.24 | 265.6305 | 367 | 314.6 | 331.7 | 304.9 | 575 | 61.3 | 19.1 | 101.5 | 4 | 246.4 | 5.3 | 924.2 | 826.3 | 784.1 | 862.9 | 894.3 | 804.3 | 683.7 | 735.9 | 730.2 | 784.2 | 279.4 | 329.6 | 193.6 | 343.1 | 327 | 271.7 | 295 | 379.8 | 265.1
1104 | 914 | 567.9 | 227.16 | 265.537 | 367.7 | 315.5 | 331.7 | 305.6 | 560.3 | 61.4 | 19.1 | 101.5 | 3.9 | 229.5 | 5.2 | 923.8 | 829.5 | 787.9 | 864.5 | 903.9 | 802.7 | 681.8 | 731.2 | 727.6 | 784.5 | 279.6 | 329.7 | 193.9 | 343.3 | 327.1 | 271.9 | 295.1 | 380 | 265.4
1105 | 915 | 567.5 | 227 | 265.3499 | 368.4 | 315.4 | 331.3 | 306.3 | 549.2 | 61.4 | 19.1 | 101.5 | 4.3 | 226.7 | 5 | 924 | 838.1 | 796.1 | 864.8 | 904.9 | 801.2 | 681.9 | 727.6 | 725.8 | 785.1 | 279.8 | 329.7 | 194.2 | 343.4 | 327.1 | 272.1 | 295.3 | 380.1 | 265.6
1106 | 916 | 568.8 | 227.52 | 265.9578 | 368.4 | 315.4 | 331.4 | 306.3 | 542.2 | 61.5 | 19.1 | 101.6 | 4.1 | 224.3 | 4.8 | 923.5 | 855.2 | 806.7 | 869.8 | 908.8 | 800.1 | 689.1 | 735.2 | 726.7 | 786.5 | 280 | 329.8 | 194.5 | 343.5 | 327 | 272.3 | 295.3 | 380.2 | 265.8
1107 | 917 | 566.8 | 226.72 | 265.0226 | 368.1 | 315.2 | 330.4 | 305.5 | 544.3 | 61.5 | 19.1 | 101.7 | 3.8 | 232.5 | 4.6 | 922.3 | 859.6 | 817.2 | 875.1 | 906.7 | 799.5 | 695.3 | 740.9 | 729 | 789 | 280.2 | 329.8 | 194.8 | 343.2 | 326.9 | 272.5 | 295.4 | 380.4 | 266
1108 | 918 | 565.8 | 226.32 | 264.555 | 368.3 | 314.9 | 329.6 | 305.1 | 548.5 | 61.5 | 19.1 | 101.7 | 4.1 | 230 | 4.7 | 920.7 | 863.9 | 822.1 | 881.1 | 903.2 | 798.7 | 706 | 741.8 | 733.1 | 791 | 280.4 | 329.8 | 195.1 | 343 | 327.4 | 272.7 | 295.5 | 380.5 | 266.2
1109 | 919 | 566.7 | 226.68 | 264.9759 | 369.5 | 315 | 329.4 | 304.8 | 549.3 | 61.6 | 19.1 | 101.8 | 4.2 | 226 | 5.2 | 919.8 | 871.8 | 819.2 | 884.1 | 908.8 | 797.8 | 713.3 | 742 | 737.6 | 792.5 | 280.6 | 329.5 | 195.4 | 343.3 | 327.6 | 272.9 | 295.6 | 380.7 | 266.4
1110 | 920 | 566.4 | 226.56 | 264.8356 | 369.7 | 314.9 | 329.6 | 304.5 | 550.7 | 61.6 | 19.1 | 101.9 | 3.9 | 226.1 | 6 | 919 | 872.3 | 827 | 890.1 | 915.8 | 797.3 | 719.4 | 749.1 | 741.7 | 793.4 | 280.8 | 329.6 | 195.7 | 343.7 | 327.6 | 273.1 | 295.7 | 380.9 | 266.6
1111 | 921 | 567.1 | 226.84 | 265.1629 | 370.2 | 314.7 | 330 | 304.9 | 567.7 | 61.7 | 19.1 | 102 | 4 | 234 | 5.8 | 919.1 | 874.7 | 831.7 | 893.5 | 925.2 | 797.1 | 723.9 | 752.7 | 745 | 794 | 280.9 | 329.9 | 196 | 344.2 | 327.8 | 273.3 | 295.8 | 381.1 | 266.8
1112 | 922 | 566.5 | 226.6 | 264.8823 | 370.3 | 314.6 | 330.7 | 305.1 | 565.4 | 61.7 | 19.1 | 102.1 | 3.9 | 255.1 | 5.3 | 918.5 | 877.5 | 831.4 | 893.7 | 932.5 | 797.1 | 725.2 | 760.6 | 747.2 | 795.4 | 281.1 | 329.9 | 196.3 | 344.4 | 328.1 | 273.4 | 295.9 | 381.4 | 267.1
1113 | 923 | 567.3 | 226.92 | 265.2564 | 371.3 | 314.5 | 331.1 | 304.6 | 570.5 | 61.7 | 19.1 | 102.3 | 4.3 | 270.5 | 4.8 | 918.7 | 875.1 | 828.1 | 893.3 | 936.8 | 797.4 | 726.8 | 763.4 | 749.9 | 796.6 | 281.3 | 329.7 | 196.6 | 344.7 | 328.6 | 273.7 | 296.1 | 381.5 | 267.3
1114 | 924 | 567.6 | 227.04 | 265.3967 | 371.6 | 314.3 | 330.7 | 304.5 | 592.9 | 61.8 | 19.1 | 102.4 | 4.4 | 279.7 | 4.2 | 918.7 | 877.5 | 832.8 | 893.2 | 931.7 | 798 | 727.8 | 770.1 | 752.1 | 795.4 | 281.5 | 329.8 | 196.9 | 344.7 | 329.3 | 273.9 | 296.3 | 381.7 | 267.5
1115 | 925 | 566.7 | 226.68 | 264.9759 | 373 | 314.6 | 330.7 | 304.8 | 620.8 | 61.8 | 19.1 | 102.3 | 4.5 | 267.9 | 3.8 | 918.5 | 881.6 | 832.7 | 893.5 | 932.9 | 798.7 | 729.7 | 774.5 | 755.3 | 794.6 | 281.6 | 330.1 | 197.2 | 344.7 | 329.7 | 274 | 296.3 | 381.9 | 267.7
1116 | 926 | 567.6 | 227.04 | 265.3967 | 373.7 | 314.6 | 331.1 | 304.8 | 622 | 61.8 | 19.1 | 102.4 | 4.5 | 265.1 | 3.4 | 918.5 | 887.2 | 831.5 | 893 | 932.9 | 799.5 | 731 | 773.3 | 757.3 | 794.9 | 281.8 | 330.4 | 197.5 | 344.3 | 329.7 | 274.2 | 296.5 | 382.1 | 267.9
1117 | 927 | 567.3 | 226.92 | 265.2564 | 373.8 | 314.7 | 331.5 | 304.7 | 625.9 | 61.7 | 19.1 | 102.5 | 4.2 | 263.9 | 2.8 | 918.6 | 891.6 | 834.1 | 893.4 | 931.2 | 799.9 | 731 | 776.4 | 759.2 | 795.3 | 282 | 330.6 | 197.8 | 343.9 | 329.4 | 274.4 | 296.5 | 382.2 | 268.1
1118 | 928 | 566.6 | 226.64 | 264.9291 | 373.7 | 314.9 | 332.5 | 305.4 | 639 | 61.7 | 19.1 | 102.5 | 4.6 | 248.3 | 2.1 | 920.6 | 888.8 | 836.9 | 891 | 924.9 | 800.7 | 730.8 | 777.9 | 760.2 | 795.5 | 282.2 | 330.8 | 198.1 | 343.7 | 329 | 274.6 | 296.5 | 382.4 | 268.3
1119 | 929 | 566.3 | 226.52 | 264.7888 | 374.5 | 315.1 | 333.6 | 305.7 | 649.6 | 61.6 | 19.1 | 102.6 | 4.3 | 196.4 | 2.5 | 920.4 | 870.4 | 827 | 881.7 | 914.7 | 801.3 | 722 | 774.6 | 758.4 | 791 | 282.4 | 331.3 | 198.3 | 343.8 | 328.8 | 274.9 | 296.5 | 382.6 | 268.5
1120 | 930 | 565.9 | 226.36 | 264.6018 | 375.9 | 315 | 334.1 | 306 | 649 | 61.6 | 19.1 | 102.7 | 4.9 | 192 | 3.4 | 919.5 | 866.2 | 829.9 | 883.5 | 910.5 | 801.6 | 717.3 | 774.1 | 755.6 | 790 | 282.6 | 331.5 | 198.6 | 343.9 | 328.7 | 275.1 | 296.6 | 382.8 | 268.7
1121 | 931 | 567.2 | 226.88 | 265.2096 | 376.5 | 315.3 | 335.1 | 306.6 | 632.8 | 61.6 | 19.1 | 102.7 | 4.3 | 203.5 | 3.5 | 919.6 | 874 | 835.2 | 887.3 | 904.1 | 801.4 | 720.6 | 771.9 | 755.8 | 792 | 282.8 | 331.6 | 198.9 | 344.3 | 329 | 275.4 | 296.8 | 383 | 269
1122 | 932 | 566.9 | 226.76 | 265.0694 | 376.4 | 315.4 | 335.3 | 307.4 | 615.2 | 61.5 | 19.1 | 102.8 | 4.6 | 203.9 | 3.8 | 920.8 | 872.4 | 829.2 | 884.4 | 905.7 | 800.5 | 721.9 | 761.5 | 756.6 | 792.1 | 283 | 331.8 | 199.2 | 345.1 | 329.1 | 275.7 | 297 | 383.2 | 269.2
1123 | 933 | 567.3 | 226.92 | 265.2564 | 378.4 | 315.6 | 335.4 | 307.5 | 593.3 | 61.5 | 19.1 | 102.9 | 4.9 | 217.4 | 4.3 | 922.2 | 852.8 | 813 | 874.1 | 908.7 | 798.9 | 711.1 | 742 | 751.5 | 790 | 283.2 | 331.8 | 199.5 | 345.6 | 329.2 | 275.9 | 297.1 | 383.3 | 269.4
1124 | 934 | 569.1 | 227.64 | 266.098 | 380.8 | 316.1 | 334.3 | 307.9 | 566.8 | 61.5 | 19.1 | 103 | 4.5 | 245.9 | 4.3 | 922.3 | 839.9 | 804.2 | 870.7 | 912.1 | 796.9 | 703.7 | 727.8 | 744.9 | 789.4 | 283.4 | 331.9 | 199.7 | 346 | 329.5 | 276.2 | 297.4 | 383.5 | 269.6
1125 | 935 | 568.8 | 227.52 | 265.9578 | 382.6 | 316.4 | 333.1 | 308.2 | 548.2 | 61.5 | 19.1 | 103.1 | 4.7 | 240.6 | 4.4 | 922.8 | 826.4 | 795.5 | 863.5 | 910.9 | 794.7 | 697.7 | 716.8 | 738.7 | 788.6 | 283.6 | 332.1 | 200 | 346.7 | 330.1 | 276.4 | 297.7 | 383.6 | 269.8
1126 | 936 | 570.5 | 228.2 | 266.7527 | 383.1 | 316.4 | 332.8 | 308.3 | 535.4 | 61.5 | 19.1 | 103.1 | 4.4 | 208.1 | 4.7 | 922.3 | 829.3 | 800.2 | 862.6 | 910.6 | 792.9 | 696.6 | 717.2 | 734.3 | 788.6 | 283.7 | 332 | 200.3 | 347.5 | 330.3 | 276.7 | 298 | 383.7 | 270.1
1127 | 937 | 571.5 | 228.6 | 267.2202 | 383.6 | 316.1 | 332.2 | 309.1 | 534.4 | 61.5 | 19.1 | 103.1 | 4.3 | 206.9 | 4.8 | 920.8 | 839.9 | 803.2 | 866.2 | 913.6 | 792.5 | 696.2 | 730.4 | 732.5 | 788.3 | 283.9 | 331.6 | 200.6 | 347.9 | 330.6 | 276.9 | 298.1 | 383.8 | 270.3
1128 | 938 | 571.1 | 228.44 | 267.0332 | 382.7 | 316 | 332.2 | 309.1 | 557.2 | 61.6 | 19.1 | 103.2 | 4.1 | 214.4 | 4.3 | 918.8 | 855.2 | 803.7 | 874.2 | 914.2 | 792.8 | 702.8 | 740.5 | 734.4 | 788.3 | 284.1 | 331.4 | 200.9 | 348.1 | 331.1 | 277.2 | 298.2 | 384 | 270.5
1129 | 939 | 568.9 | 227.56 | 266.0045 | 382.4 | 315.8 | 332.1 | 309.3 | 569.4 | 61.6 | 19.1 | 103.2 | 4.5 | 213.2 | 3.9 | 916.9 | 862.4 | 818.5 | 878.5 | 918.9 | 793.1 | 710 | 745.6 | 738.5 | 789.4 | 284.2 | 331.5 | 201.1 | 348 | 331.3 | 277.4 | 298.3 | 384.2 | 270.7
1130 | 940 | 567 | 226.8 | 265.1161 | 384.1 | 315.7 | 332.3 | 309.2 | 592.2 | 61.7 | 19 | 103.2 | 4 | 207.2 | 3.8 | 915.7 | 869.6 | 826.5 | 882.3 | 926.4 | 793.3 | 720 | 749.5 | 743.3 | 790.5 | 284.3 | 331.7 | 201.4 | 347.7 | 331.5 | 277.6 | 298.4 | 384.3 | 270.9
1131 | 941 | 567.7 | 227.08 | 265.4434 | 384.6 | 315.4 | 333.5 | 308.8 | 596.8 | 61.7 | 19.1 | 103.2 | 4.4 | 203.3 | 3.8 | 915.2 | 869.5 | 833.9 | 886 | 931.5 | 793.2 | 726.7 | 752.9 | 747.1 | 791.2 | 284.5 | 331.7 | 201.7 | 347.6 | 331.1 | 277.7 | 298.4 | 384.5 | 271.1
1132 | 942 | 567.9 | 227.16 | 265.537 | 384 | 315.4 | 334.7 | 308.5 | 611.8 | 61.8 | 19.1 | 103.3 | 4.3 | 200.5 | 3.7 | 913.9 | 872 | 840.3 | 891.8 | 931.9 | 793.8 | 732.3 | 758.7 | 751.5 | 792.1 | 284.6 | 331.9 | 202 | 347.6 | 330.7 | 277.9 | 298.5 | 384.8 | 271.3
1133 | 943 | 568.5 | 227.4 | 265.8175 | 384.7 | 315.4 | 334.6 | 308.3 | 621.6 | 61.8 | 19 | 103.4 | 4.4 | 198.4 | 3.7 | 913.5 | 879.6 | 845.3 | 895.1 | 934.1 | 794.5 | 734.1 | 763.5 | 754.1 | 792.8 | 284.8 | 332.2 | 202.3 | 347.7 | 330.6 | 278.1 | 298.6 | 385 | 271.5
1134 | 944 | 568.6 | 227.44 | 265.8643 | 385.8 | 315.4 | 335.2 | 308.1 | 615.8 | 61.8 | 19 | 103.5 | 4.7 | 185.8 | 3.9 | 913.2 | 883.1 | 853.8 | 898.6 | 936.2 | 794.5 | 734.2 | 760.2 | 755.1 | 793.6 | 285 | 332.3 | 202.5 | 347.3 | 330.9 | 278.3 | 298.7 | 385.2 | 271.7
1135 | 945 | 568.6 | 227.44 | 265.8643 | 385.9 | 315.8 | 335.3 | 307.8 | 607.3 | 61.8 | 19 | 103.5 | 4.4 | 185.9 | 3.9 | 913.3 | 876 | 861.4 | 895.2 | 936 | 794.4 | 740.1 | 766 | 756.5 | 794.7 | 285.2 | 332.4 | 202.8 | 346.9 | 331.6 | 278.4 | 298.9 | 385.4 | 271.9
1136 | 946 | 568.8 | 227.52 | 265.9578 | 385.8 | 316.4 | 335 | 307.6 | 621.7 | 61.7 | 19 | 103.6 | 4.7 | 185.6 | 4 | 913.2 | 873.8 | 864.9 | 898.9 | 925 | 794.7 | 741.9 | 769.6 | 758.9 | 793 | 285.3 | 332.5 | 203.1 | 346.8 | 332.1 | 278.6 | 299 | 385.6 | 272.1
1137 | 947 | 568.2 | 227.28 | 265.6772 | 387.2 | 317.2 | 334.9 | 307.8 | 628.2 | 61.7 | 19 | 103.6 | 4.2 | 187.1 | 4.2 | 913.2 | 892.5 | 860.6 | 899.7 | 922.1 | 795.4 | 736.9 | 765.8 | 759.1 | 792.5 | 285.5 | 332.5 | 203.3 | 346.7 | 332.1 | 278.8 | 299.1 | 385.9 | 272.3
1138 | 948 | 568.5 | 227.4 | 265.8175 | 388.9 | 317.2 | 335.2 | 308.1 | 619.5 | 61.6 | 19 | 103.7 | 4.5 | 192.2 | 4.4 | 912.8 | 894.9 | 859.2 | 901 | 912.9 | 795.9 | 740.2 | 766.1 | 760.9 | 794.2 | 285.7 | 332.5 | 203.6 | 346.7 | 332.3 | 279 | 299.2 | 386.1 | 272.5
1139 | 949 | 568.1 | 227.24 | 265.6305 | 388.6 | 317.3 | 335 | 308.2 | 606.1 | 61.6 | 19 | 103.8 | 4.5 | 198.5 | 4.7 | 913.2 | 890.1 | 854.3 | 901.2 | 918.8 | 795.5 | 739.7 | 756.4 | 762.2 | 795.8 | 285.8 | 332.9 | 203.8 | 347 | 332.5 | 279.1 | 299.4 | 386.3 | 272.8
1140 | 950 | 568.3 | 227.32 | 265.724 | 388.3 | 317.6 | 335.1 | 308.3 | 586.1 | 61.6 | 19 | 103.9 | 4.3 | 197.4 | 4.7 | 913.1 | 892.6 | 850.5 | 898.3 | 924.6 | 794.8 | 738.3 | 753.2 | 761.2 | 796.6 | 286 | 333.4 | 204.1 | 347.4 | 332.8 | 279.3 | 299.7 | 386.4 | 273
1141 | 951 | 568 | 227.2 | 265.5837 | 388.8 | 317.6 | 334.4 | 308.6 | 567.8 | 61.7 | 19 | 103.9 | 3.7 | 196.7 | 4.6 | 913 | 892.9 | 847.8 | 899.2 | 932.5 | 794.5 | 738.4 | 750.4 | 760.8 | 797.4 | 286.2 | 333.8 | 204.3 | 347.6 | 332.7 | 279.5 | 299.8 | 386.6 | 273.2
1142 | 952 | 568.3 | 227.32 | 265.724 | 388.6 | 317.7 | 333.9 | 308.5 | 580 | 61.7 | 19 | 103.9 | 3.5 | 192.6 | 4.5 | 913.5 | 893.5 | 854.3 | 900.6 | 934 | 794.8 | 739.3 | 757.7 | 761.9 | 797.3 | 286.4 | 334.1 | 204.6 | 347.5 | 332.4 | 279.7 | 299.8 | 386.7 | 273.4
1143 | 953 | 567.9 | 227.16 | 265.537 | 389.1 | 317.7 | 333.8 | 307.9 | 602.6 | 61.7 | 19 | 103.9 | 4.2 | 190.1 | 4.5 | 914.1 | 897.9 | 856.3 | 901.9 | 937.9 | 795.1 | 744.8 | 762.6 | 765.3 | 798.4 | 286.6 | 334.1 | 204.9 | 347.7 | 332.3 | 279.9 | 299.9 | 386.9 | 273.6
1144 | 954 | 566.3 | 226.52 | 264.7888 | 390.3 | 317.6 | 334 | 307.5 | 616.3 | 61.6 | 19 | 103.9 | 4.2 | 187.6 | 4.4 | 914.4 | 907.1 | 855.9 | 901.6 | 936 | 795.1 | 748.2 | 766.1 | 768 | 800.3 | 286.8 | 334.1 | 205.1 | 347.9 | 332.4 | 280.1 | 300 | 387.1 | 273.8
1145 | 955 | 566.1 | 226.44 | 264.6953 | 390.8 | 317.7 | 334.1 | 307 | 625.3 | 61.6 | 19 | 103.8 | 4.4 | 178.2 | 4.3 | 915 | 909.1 | 857.5 | 898.2 | 935.3 | 795.4 | 747.5 | 773.7 | 769 | 800.9 | 287 | 334.5 | 205.3 | 347.8 | 332.4 | 280.3 | 300.2 | 387.3 | 274
1146 | 956 | 566.9 | 226.76 | 265.0694 | 390.2 | 317.9 | 333.8 | 307.5 | 638.3 | 61.5 | 19 | 103.8 | 4.2 | 176.5 | 4.2 | 914.9 | 908.7 | 860.8 | 900.3 | 936.9 | 796.1 | 746 | 778.6 | 769.8 | 801.3 | 287.2 | 334.8 | 205.6 | 347.9 | 332.4 | 280.4 | 300.2 | 387.6 | 274.2
1147 | 957 | 567.3 | 226.92 | 265.2564 | 389.1 | 318.2 | 333.2 | 307.9 | 649.6 | 61.5 | 19 | 103.8 | 4.2 | 181.2 | 4.4 | 914.6 | 911.6 | 857 | 901.4 | 935.3 | 796.7 | 746.7 | 779.3 | 771.7 | 801.1 | 287.4 | 335.1 | 205.8 | 348.3 | 332.5 | 280.6 | 300.3 | 387.8 | 274.4
1148 | 958 | 566.8 | 226.72 | 265.0226 | 389.8 | 318.7 | 333.7 | 308.5 | 634.8 | 61.6 | 19 | 103.9 | 4.4 | 184 | 4.8 | 914.3 | 911.6 | 857.3 | 899.5 | 931.7 | 796.9 | 744.2 | 775.8 | 771.5 | 801.9 | 287.6 | 335.3 | 206.1 | 348.4 | 332.8 | 280.8 | 300.4 | 388 | 274.7
1149 | 959 | 566.9 | 226.76 | 265.0694 | 390.5 | 318.9 | 334.1 | 309.2 | 618.5 | 61.7 | 19 | 104 | 4.8 | 178.9 | 5.1 | 914.8 | 902 | 854 | 897.5 | 934.8 | 796.7 | 744.8 | 770.4 | 771.7 | 802.7 | 287.8 | 335.8 | 206.3 | 348.7 | 333 | 281 | 300.5 | 388.2 | 274.9
1150 | 960 | 566.6 | 226.64 | 264.9291 | 391.1 | 319.1 | 334.5 | 309.2 | 604.5 | 61.8 | 19 | 104.1 | 4.9 | 182.7 | 4.8 | 915.7 | 897.2 | 852.9 | 891.5 | 933.7 | 796.2 | 739.2 | 761.8 | 769 | 801.7 | 288 | 336.1 | 206.5 | 348.7 | 333.6 | 281.1 | 300.7 | 388.5 | 275.1
1151 | 961 | 566.1 | 226.44 | 264.6953 | 391.3 | 319.3 | 334.7 | 308.9 | 584.4 | 61.9 | 19 | 104.3 | 5 | 185.9 | 4.9 | 917.6 | 898 | 850.1 | 889.5 | 934.5 | 795.1 | 733.5 | 754.5 | 765.7 | 801.1 | 288.3 | 336.4 | 206.8 | 348.7 | 333.7 | 281.3 | 300.9 | 388.6 | 275.3
1152 | 962 | 567 | 226.8 | 265.1161 | 391.9 | 319.3 | 334.3 | 308.7 | 568.4 | 61.9 | 19 | 104.4 | 5.4 | 196.8 | 5.8 | 919.2 | 898 | 844.6 | 886 | 937.8 | 794.4 | 731.6 | 753.7 | 762.9 | 801.8 | 288.6 | 336.2 | 207 | 348.9 | 333.8 | 281.5 | 301.1 | 388.8 | 275.5
1153 | 963 | 567.7 | 227.08 | 265.4434 | 391.1 | 319.3 | 334 | 308.8 | 560.5 | 61.9 | 19 | 104.4 | 4.9 | 197.3 | 7.3 | 920.3 | 896 | 844.7 | 885.5 | 939 | 793.7 | 731.6 | 754.1 | 761.3 | 803.5 | 288.8 | 336.1 | 207.3 | 349.2 | 333.7 | 281.7 | 301.3 | 388.9 | 275.7
1154 | 964 | 567.8 | 227.12 | 265.4902 | 390.7 | 319 | 333.5 | 308.5 | 567.1 | 62 | 19 | 104.4 | 4.5 | 197.6 | 7.9 | 919.6 | 890.6 | 847.4 | 889.4 | 936.8 | 793.5 | 734.1 | 762 | 761.8 | 804.5 | 289.1 | 336 | 207.5 | 349.3 | 333.5 | 281.8 | 301.3 | 389.1 | 275.9
1155 | 965 | 566.5 | 226.6 | 264.8823 | 389.7 | 318.8 | 333.2 | 308.4 | 601.4 | 62.1 | 19 | 104.5 | 4.8 | 201.3 | 7.4 | 919.6 | 892 | 849.1 | 893.6 | 931.8 | 793.9 | 737 | 765.8 | 764.5 | 803.7 | 289.3 | 335.7 | 207.7 | 349.7 | 333.3 | 282 | 301.3 | 389.2 | 276.1
1156 | 966 | 566.4 | 226.56 | 264.8356 | 389.2 | 318.8 | 333.7 | 308.3 | 619.8 | 62.1 | 19 | 104.5 | 4.9 | 196.5 | 7.1 | 919 | 893 | 844.7 | 894.5 | 931.7 | 794.6 | 739 | 770.1 | 766.2 | 803.6 | 289.4 | 335.4 | 207.9 | 349.8 | 333.3 | 282.2 | 301.5 | 389.5 | 276.3
1157 | 967 | 566.9 | 226.76 | 265.0694 | 388.9 | 318.7 | 335 | 308.1 | 622.1 | 62.2 | 19 | 104.5 | 4.7 | 204.3 | 6 | 919.2 | 892.8 | 840.8 | 891.8 | 927.3 | 795.8 | 734.7 | 771.8 | 766.5 | 802.3 | 289.7 | 335.6 | 208.2 | 350.1 | 333.6 | 282.3 | 301.5 | 389.6 | 276.5
1158 | 968 | 567.1 | 226.84 | 265.1629 | 388.5 | 319 | 335.3 | 308.6 | 624.2 | 62.2 | 19 | 104.6 | 5.2 | 256.7 | 5.4 | 919.3 | 884.9 | 832.8 | 884.3 | 923.4 | 796.6 | 728 | 769.8 | 765 | 800.3 | 288.4 | 336.1 | 208.4 | 350.1 | 333.8 | 282.5 | 301.7 | 389.8 | 276.8
1159 | 969 | 568.4 | 227.36 | 265.7707 | 387.9 | 319.1 | 336.2 | 309.2 | 606.6 | 62.2 | 19 | 104.6 | 4.8 | 245 | 5 | 919.9 | 880.9 | 826.1 | 879.5 | 922.5 | 796.4 | 726.7 | 758.8 | 762.7 | 801.5 | 277.6 | 336.8 | 208.7 | 350 | 334 | 282.7 | 301.8 | 390 | 276.9
1160 | 970 | 568.1 | 227.24 | 265.6305 | 387.7 | 319 | 336.5 | 309.5 | 584.9 | 62.3 | 19 | 104.6 | 4.5 | 218.1 | 4.6 | 920.6 | 877.3 | 824.7 | 877 | 929.5 | 795.5 | 726.5 | 752.9 | 759.8 | 802.5 | 269.5 | 337.2 | 208.9 | 350.3 | 334.1 | 282.9 | 302 | 390.1 | 277.2
1161 | 971 | 568.1 | 227.24 | 265.6305 | 387.9 | 318.7 | 336.5 | 309.7 | 572.5 | 62.3 | 19 | 104.6 | 4.6 | 233.3 | 4.6 | 920.3 | 881.5 | 835.9 | 881.5 | 926.5 | 794.7 | 729.9 | 754.2 | 758.9 | 802.7 | 264 | 337.4 | 209.1 | 350.3 | 334.3 | 283 | 302.1 | 390.3 | 277.4
1162 | 972 | 567.3 | 226.92 | 265.2564 | 388 | 318.8 | 336.5 | 310.1 | 582 | 62.3 | 19 | 104.6 | 4.7 | 233 | 5 | 919.7 | 883.7 | 841.6 | 887.4 | 928.9 | 794.6 | 732.6 | 760.7 | 759.3 | 803 | 264.1 | 337.1 | 209.4 | 350 | 334.5 | 283.2 | 302.2 | 390.4 | 277.5
1163 | 973 | 567.7 | 227.08 | 265.4434 | 388 | 318.7 | 336.2 | 310.2 | 583 | 62.3 | 19 | 104.7 | 4.8 | 221.8 | 4.4 | 921.1 | 887.4 | 847.4 | 891.5 | 936.3 | 794.6 | 736.3 | 759.7 | 760.5 | 804.3 | 287.8 | 336.8 | 209.6 | 350.2 | 335.1 | 283.3 | 302.3 | 390.6 | 277.7
1164 | 974 | 567.6 | 227.04 | 265.3967 | 387.7 | 318.6 | 336.1 | 310 | 571.2 | 62.3 | 19 | 104.8 | 4.8 | 222.5 | 3.9 | 921.7 | 881.9 | 838.6 | 891.9 | 931.5 | 793.7 | 736.2 | 752.3 | 760.2 | 803.8 | 279.1 | 336.7 | 209.8 | 350.2 | 335.4 | 283.4 | 302.6 | 390.9 | 277.9
1165 | 975 | 566.9 | 226.76 | 265.0694 | 386.9 | 318.4 | 335.8 | 310 | 557.7 | 62.3 | 19 | 104.9 | 5.5 | 208.6 | 3.6 | 921.9 | 871.4 | 831.6 | 888 | 936.7 | 792 | 728 | 736.6 | 757.1 | 802.8 | 265.6 | 336.8 | 210 | 350.6 | 335.8 | 283.6 | 302.8 | 391 | 278.1
1166 | 976 | 568.4 | 227.36 | 265.7707 | 386 | 318.3 | 335.6 | 310.1 | 541.1 | 62.3 | 19 | 104.9 | 5.2 | 225.8 | 3.5 | 922.5 | 872.9 | 831.9 | 885.7 | 938.2 | 790 | 722.1 | 727.4 | 752.3 | 801.9 | 243.8 | 336.9 | 210.3 | 350.9 | 336.6 | 283.7 | 303 | 391.2 | 278.3
1167 | 977 | 569.7 | 227.88 | 266.3786 | 385.9 | 318.2 | 335.7 | 310.6 | 532.2 | 62.3 | 19 | 104.9 | 5 | 227.8 | 3.9 | 922.1 | 874.2 | 834.1 | 886.8 | 939.1 | 788.6 | 723.6 | 726.7 | 749.2 | 802.1 | 231.9 | 336.9 | 210.5 | 351.5 | 337.3 | 283.9 | 303.2 | 391.4 | 278.5
1168 | 978 | 569.9 | 227.96 | 266.4721 | 385.4 | 318.2 | 335.2 | 310.7 | 531.4 | 62.2 | 19 | 105 | 4.6 | 207.7 | 5.6 | 922.1 | 873.6 | 831.5 | 890 | 942.2 | 787.6 | 727.5 | 732.6 | 749.5 | 802.7 | 227.3 | 332.2 | 210.7 | 352.1 | 338.3 | 284.1 | 303.4 | 391.5 | 278.8
1169 | 979 | 569.3 | 227.72 | 266.1916 | 385.3 | 318.3 | 335 | 311.2 | 529.9 | 62.3 | 19 | 105.1 | 4.5 | 214.6 | 6.3 | 921.6 | 868.2 | 837.3 | 891.9 | 941.1 | 786.4 | 730.2 | 728.1 | 749.5 | 802.4 | 237 | 328.2 | 210.9 | 352.6 | 339.8 | 284.2 | 303.8 | 391.7 | 279
1170 | 980 | 567.4 | 226.96 | 265.3032 | 385.4 | 318.3 | 335 | 311.8 | 528.9 | 62.3 | 18.9 | 105.2 | 4.5 | 193.2 | 6.3 | 921.9 | 869.4 | 834.1 | 891.2 | 945.4 | 785.9 | 730.3 | 735 | 749.8 | 802.7 | 229.4 | 309.4 | 211.2 | 353 | 340.5 | 284.4 | 304.1 | 391.9 | 279.2
1171 | 981 | 568.3 | 227.32 | 265.724 | 385.1 | 318.4 | 334.8 | 311.9 | 534.2 | 62.4 | 19 | 105.4 | 4.4 | 207.5 | 6.6 | 922 | 876.7 | 838 | 892.6 | 942.2 | 786 | 733 | 745.5 | 750.7 | 804.2 | 226.4 | 288.7 | 211.4 | 353.2 | 341.1 | 284.6 | 304.3 | 392.1 | 279.5
1172 | 982 | 568.4 | 227.36 | 265.7707 | 384.3 | 318.7 | 334.9 | 311.7 | 564.3 | 62.5 | 19 | 105.6 | 4.9 | 212.8 | 7.4 | 923.3 | 884.2 | 837.7 | 890.7 | 943.6 | 786.5 | 734.8 | 748.9 | 753 | 805.3 | 222.3 | 271.7 | 211.6 | 353.2 | 341.6 | 284.8 | 304.5 | 392.3 | 279.7
1173 | 983 | 568.5 | 227.4 | 265.8175 | 384.4 | 319.2 | 334.7 | 311.4 | 566.6 | 62.6 | 18.9 | 105.6 | 5.2 | 221.3 | 7.6 | 924 | 881.3 | 833.9 | 885.4 | 937.6 | 786.9 | 731.3 | 747.4 | 753.2 | 805.8 | 220 | 267.2 | 211.8 | 353.1 | 341.9 | 285 | 304.6 | 392.6 | 279.9
1174 | 984 | 567.8 | 227.12 | 265.4902 | 384.7 | 319.4 | 335.1 | 310.9 | 560.2 | 62.6 | 18.9 | 105.5 | 5.3 | 223.5 | 7.1 | 923.5 | 877.6 | 832.5 | 883.1 | 938.6 | 786.7 | 721.5 | 740.2 | 750.1 | 803.6 | 213 | 253.1 | 212 | 352.9 | 342.1 | 285.1 | 304.8 | 392.8 | 280.1
1175 | 985 | 566.3 | 226.52 | 264.7888 | 384.5 | 319.6 | 335.4 | 310.7 | 554.9 | 62.6 | 18.9 | 105.5 | 5.4 | 190.3 | 6.6 | 923.4 | 881.6 | 835.6 | 882.2 | 941 | 786.5 | 723.1 | 740.3 | 747.9 | 803.2 | 209.9 | 245.8 | 212.2 | 352.7 | 342.1 | 285.3 | 304.8 | 392.9 | 280.3
1176 | 986 | 566.5 | 226.6 | 264.8823 | 385.2 | 319.7 | 335.7 | 310.9 | 551.6 | 62.6 | 18.9 | 105.5 | 5.4 | 206.1 | 6 | 924.2 | 883.9 | 840.7 | 881.7 | 936 | 786.2 | 722.4 | 740.1 | 747.3 | 803.1 | 212 | 246.7 | 212.5 | 352.7 | 342.5 | 285.4 | 305.1 | 393 | 280.5
1177 | 987 | 567.5 | 227 | 265.3499 | 385 | 319.5 | 335.5 | 311 | 540.5 | 62.5 | 18.9 | 105.6 | 4.7 | 212 | 5.6 | 924.4 | 880.7 | 839.2 | 883.2 | 940.4 | 785.6 | 722 | 738.8 | 745.6 | 802.5 | 210.5 | 244.6 | 212.7 | 353 | 343 | 285.6 | 305.4 | 393.2 | 280.7
1178 | 988 | 567.1 | 226.84 | 265.1629 | 385.2 | 319.4 | 334.7 | 311.3 | 538.3 | 62.4 | 18.9 | 105.7 | 4.7 | 199.1 | 6.5 | 925.4 | 872.3 | 837.1 | 879.8 | 936.6 | 784.8 | 722 | 729.5 | 744 | 803 | 203.6 | 234.6 | 212.9 | 353.2 | 344 | 285.7 | 305.7 | 393.3 | 280.9
1179 | 989 | 567.2 | 226.88 | 265.2096 | 385.6 | 319.5 | 334.1 | 311.6 | 529.1 | 62.4 | 18.9 | 105.7 | 4.8 | 203.1 | 7.5 | 926.5 | 861.1 | 829.6 | 873.5 | 933.5 | 783.4 | 718.9 | 720.5 | 741.4 | 803.3 | 204.7 | 235.5 | 213.1 | 353.9 | 344.7 | 285.9 | 306 | 393.5 | 281.2
1180 | 990 | 567 | 226.8 | 265.1161 | 386.5 | 319.4 | 333.7 | 311.7 | 516.8 | 62.5 | 18.9 | 105.7 | 4.9 | 205 | 8.8 | 926.4 | 859.9 | 830.3 | 873.8 | 934.5 | 781.9 | 720.2 | 715 | 738.7 | 803 | 206.1 | 238.6 | 213.3 | 354 | 345.4 | 286.1 | 306.3 | 393.6 | 281.4
1181 | 991 | 566.2 | 226.48 | 264.7421 | 387.3 | 319.3 | 333.6 | 312.1 | 511.2 | 62.6 | 18.9 | 105.7 | 4.6 | 208 | 9.2 | 925.3 | 862 | 838.2 | 880.3 | 935.6 | 780.9 | 724.7 | 714.5 | 738.5 | 803 | 202.4 | 233.6 | 213.5 | 354.3 | 345.7 | 286.3 | 306.6 | 393.8 | 281.6
1182 | 992 | 568 | 227.2 | 265.5837 | 387.4 | 319.3 | 333.5 | 312.2 | 523.1 | 62.6 | 18.9 | 105.7 | 5.3 | 210.8 | 9.1 | 924.4 | 866.9 | 845.6 | 884.5 | 930 | 781 | 732.3 | 725.3 | 740.8 | 804 | 197.7 | 226.3 | 213.7 | 354.6 | 346.1 | 286.4 | 306.7 | 394 | 281.8
1183 | 993 | 567.1 | 226.84 | 265.1629 | 386.7 | 319.3 | 333.5 | 312.7 | 536.8 | 62.7 | 18.9 | 105.8 | 5.1 | 208 | 8.7 | 924.4 | 872.9 | 838.5 | 885.4 | 928 | 781.5 | 733.4 | 729.1 | 742.7 | 804.2 | 196.7 | 223.8 | 213.9 | 354.8 | 346.7 | 286.6 | 306.9 | 394.3 | 282
1184 | 994 | 566.9 | 226.76 | 265.0694 | 386.4 | 319.2 | 333.7 | 312.8 | 539.3 | 62.7 | 18.9 | 105.8 | 4.9 | 204 | 9 | 926.1 | 861.4 | 826 | 877.2 | 927 | 781.6 | 724.4 | 729 | 740.5 | 802.9 | 198.6 | 224.5 | 214.1 | 354.9 | 347.4 | 286.8 | 307.1 | 394.5 | 282.2
1185 | 995 | 568 | 227.2 | 265.5837 | 386.3 | 319 | 333.6 | 312.1 | 534.8 | 62.8 | 18.9 | 105.8 | 4.7 | 215.2 | 9.5 | 926.1 | 853.7 | 820.6 | 873.5 | 924.4 | 781.5 | 716.3 | 728.8 | 737.1 | 800.4 | 198.8 | 224.3 | 214.3 | 354.7 | 347.3 | 287 | 307.2 | 394.7 | 282.4
1186 | 996 | 567.9 | 227.16 | 265.537 | 387 | 319 | 333.6 | 311.7 | 530.5 | 62.9 | 18.9 | 105.9 | 4.6 | 211.2 | 9.3 | 926.3 | 848.5 | 824.8 | 873.4 | 923.7 | 780.9 | 707.8 | 723.5 | 732.6 | 797.1 | 196.1 | 220.5 | 214.6 | 354.6 | 347.3 | 287.1 | 307.3 | 394.8 | 282.6
1187 | 997 | 567.9 | 227.16 | 265.537 | 387.5 | 318.9 | 334 | 311.9 | 536.3 | 63 | 18.9 | 105.9 | 4.2 | 241.5 | 7.9 | 926.3 | 855.7 | 828.7 | 875.8 | 925.9 | 780.8 | 709.2 | 732.6 | 730.4 | 796.4 | 189.6 | 212.4 | 214.8 | 354.3 | 347.7 | 287.3 | 307.2 | 394.9 | 282.8
1188 | 998 | 567.2 | 226.88 | 265.2096 | 386.7 | 318.9 | 334 | 311.5 | 554.5 | 63 | 18.9 | 105.9 | 4.5 | 211.7 | 7 | 925.8 | 870.7 | 829.7 | 878.6 | 928.1 | 781.4 | 716.5 | 740.9 | 732.3 | 797.7 | 187.9 | 210.8 | 215 | 354.3 | 347.9 | 287.4 | 307.3 | 395 | 283
1189 | 999 | 567 | 226.8 | 265.1161 | 386 | 319.2 | 333.3 | 311.1 | 564 | 63 | 18.9 | 105.9 | 4.7 | 210.1 | 7.6 | 924.8 | 876.3 | 829.1 | 882.1 | 928.2 | 781.6 | 724.3 | 745.2 | 736.8 | 799.8 | 186.7 | 208.8 | 215.2 | 354.2 | 348 | 287.6 | 307.7 | 395.1 | 283.2
1190 | 1000 | 568 | 227.2 | 265.5837 | 385.6 | 319.4 | 333.2 | 311.1 | 562 | 62.9 | 18.9 | 106 | 4.4 | 199.1 | 8.5 | 923.9 | 880.5 | 834.1 | 885.3 | 931.1 | 781.3 | 727.2 | 745.4 | 739.8 | 800.2 | 183.1 | 204.7 | 215.4 | 354.3 | 347.8 | 287.7 | 307.8 | 395.3 | 283.4
1191 | 1001 | 567.8 | 227.12 | 265.4902 | 385.3 | 319.7 | 333.7 | 311 | 560.7 | 63 | 18.9 | 106 | 5.3 | 222.8 | 6.9 | 923.7 | 877.6 | 838.9 | 887.4 | 932 | 780.5 | 730 | 738.3 | 742.5 | 800.4 | 181.2 | 201.2 | 215.6 | 354.6 | 347.7 | 287.9 | 307.9 | 395.5 | 283.6
1192 | 1002 | 567.9 | 227.16 | 265.537 | 385.3 | 319.8 | 333.5 | 311.1 | 546.7 | 63 | 18.9 | 106.1 | 5.4 | 254.5 | 5.3 | 924.5 | 874.1 | 828.5 | 881 | 928.3 | 779.6 | 723.7 | 733.8 | 740.5 | 799.3 | 179.5 | 200.6 | 215.8 | 355 | 347.8 | 288.1 | 308.1 | 395.7 | 283.9
1193 | 1003 | 568.2 | 227.28 | 265.6772 | 385.8 | 319.7 | 333.3 | 311.7 | 536.7 | 63.2 | 18.9 | 106.1 | 5.2 | 209.6 | 5.7 | 926 | 860.7 | 823.8 | 874.5 | 931.2 | 778.9 | 722.6 | 731.1 | 738.1 | 799.9 | 178 | 199.5 | 216 | 355.4 | 348.1 | 288.3 | 308.3 | 395.9 | 284.1
1194 | 1004 | 566.4 | 226.56 | 264.8356 | 386.3 | 319.6 | 333.4 | 312.2 | 531.3 | 63.3 | 18.9 | 106.1 | 4.8 | 216.4 | 8 | 926 | 863.2 | 822.6 | 876.4 | 931.5 | 778.9 | 723.4 | 737.1 | 737.8 | 799.2 | 177.7 | 198.7 | 216.2 | 355.7 | 348.6 | 288.5 | 308.6 | 396 | 284.3
1195 | 1005 | 565.6 | 226.24 | 264.4615 | 386.1 | 319.5 | 332.9 | 312 | 534 | 63.3 | 18.9 | 106.2 | 5.4 | 203.6 | 9.2 | 925.9 | 864.7 | 819.1 | 872.7 | 929.3 | 779 | 717.5 | 738.3 | 736.4 | 797.5 | 177.9 | 197.9 | 216.4 | 355.9 | 349 | 288.7 | 308.8 | 396.2 | 284.5
1196 | 1006 | 567.8 | 227.12 | 265.4902 | 385.8 | 319.5 | 332.5 | 311.8 | 541 | 63.4 | 18.9 | 106.3 | 5.4 | 205.7 | 9.2 | 925.7 | 866.3 | 832 | 874.1 | 933.9 | 779.6 | 718.8 | 744.1 | 736.2 | 798.1 | 175.5 | 195 | 216.6 | 355.8 | 349.4 | 288.9 | 309 | 396.3 | 284.7
1197 | 1007 | 567.8 | 227.12 | 265.4902 | 386.1 | 319.7 | 332.8 | 311.7 | 560.1 | 63.4 | 18.9 | 106.4 | 5.2 | 215.5 | 8.7 | 924.3 | 868.7 | 835.4 | 878 | 929.7 | 779.9 | 723.3 | 749.2 | 738.4 | 798.6 | 174.4 | 188.1 | 216.8 | 355.5 | 349.2 | 289 | 309.1 | 396.4 | 284.9
1198 | 1008 | 567 | 226.8 | 265.1161 | 386.4 | 319.9 | 333 | 311.3 | 574 | 63.5 | 18.9 | 106.5 | 4.9 | 208.8 | 8.1 | 923.9 | 870.5 | 844 | 880.2 | 929.9 | 780.5 | 729.8 | 753.1 | 741.7 | 799.5 | 173.4 | 191.6 | 217 | 355.1 | 348.9 | 289.2 | 309.2 | 396.6 | 285
1199 | 1009 | 567.3 | 226.92 | 265.2564 | 386.7 | 319.9 | 333.2 | 310.7 | 588.6 | 63.5 | 18.9 | 106.6 | 4.5 | 204.5 | 7.9 | 925.2 | 874.4 | 852.6 | 882 | 930.3 | 781.1 | 736.3 | 759.9 | 745.3 | 800.8 | 172.1 | 191.6 | 217.2 | 354.6 | 348.7 | 289.4 | 309.3 | 396.8 | 285.2
1200 | 1010 | 566.8 | 226.72 | 265.0226 | 386.5 | 319.6 | 333.6 | 310.6 | 594.6 | 63.6 | 18.9 | 106.6 | 4.6 | 216.1 | 8.4 | 925.1 | 874.8 | 857 | 884.8 | 931.4 | 781.4 | 741.1 | 763.7 | 748.9 | 801.3 | 173.5 | 193.7 | 217.4 | 354.6 | 348.5 | 289.5 | 309.4 | 397 | 285.4
1201 | 1011 | 566 | 226.4 | 264.6486 | 385.8 | 319.8 | 333.4 | 310.9 | 608.4 | 63.6 | 18.9 | 106.5 | 4 | 211.6 | 8.7 | 924.8 | 876.8 | 859.5 | 886.9 | 931.5 | 781.8 | 745.6 | 767.9 | 753 | 801.6 | 169.9 | 188.9 | 217.6 | 354.5 | 348.6 | 289.7 | 309.5 | 397.2 | 285.6
1202 | 1012 | 567.7 | 227.08 | 265.4434 | 386.3 | 320.3 | 333.7 | 310.8 | 618.8 | 63.6 | 18.9 | 106.7 | 4.3 | 225.5 | 8.3 | 924.8 | 875.2 | 868 | 890.1 | 929.1 | 782.8 | 749.1 | 770 | 756.5 | 803.5 | 167.4 | 185.7 | 217.8 | 354.3 | 348.6 | 289.8 | 309.6 | 397.4 | 285.8
1203 | 1013 | 567.9 | 227.16 | 265.537 | 386.9 | 321.1 | 333.7 | 310.7 | 625.4 | 63.7 | 18.9 | 106.7 | 4.6 | 240.5 | 7.7 | 924.4 | 870.2 | 874.4 | 892.7 | 919.4 | 783.5 | 752 | 772.3 | 759.6 | 802.2 | 164.6 | 183.7 | 218 | 354.2 | 349 | 290 | 309.8 | 397.6 | 286
1204 | 1014 | 566.3 | 226.52 | 264.7888 | 386.8 | 321.8 | 332.9 | 310.5 | 643.3 | 63.7 | 18.9 | 106.7 | 4.8 | 245.9 | 6.8 | 924.2 | 875.8 | 870.5 | 891.7 | 918.1 | 784.2 | 755.9 | 775.8 | 762.9 | 802 | 163.1 | 182.2 | 218.2 | 354.1 | 349.2 | 290.1 | 310 | 397.9 | 286.2
1205 | 1015 | 566.2 | 226.48 | 264.7421 | 387.2 | 322.4 | 333.1 | 310.3 | 662.1 | 63.7 | 18.9 | 106.6 | 4.9 | 210.1 | 6.4 | 923.1 | 886.2 | 871.9 | 890.6 | 916 | 785 | 757.7 | 778.2 | 765.8 | 802.2 | 162.4 | 180.1 | 218.4 | 354.6 | 349.5 | 290.3 | 310 | 398.1 | 286.3
1206 | 1016 | 566.8 | 226.72 | 265.0226 | 386.8 | 323.2 | 333.8 | 310.8 | 680.4 | 63.7 | 18.9 | 106.6 | 4.7 | 193.8 | 6.6 | 922.4 | 882.6 | 871 | 890.1 | 918.6 | 785.6 | 760.2 | 779 | 768.7 | 802.1 | 161.5 | 178.7 | 218.6 | 354.8 | 349.6 | 290.5 | 310.3 | 398.3 | 286.6
1207 | 1017 | 566.9 | 226.76 | 265.0694 | 386.5 | 323.5 | 334.6 | 311.1 | 696.2 | 63.7 | 18.9 | 106.7 | 5 | 202.4 | 6.1 | 922.1 | 885.9 | 873.6 | 890.2 | 914.2 | 786.1 | 761 | 782.4 | 772.1 | 800.8 | 161.1 | 178.4 | 218.8 | 354.7 | 349.1 | 290.7 | 310.4 | 398.5 | 286.8
1208 | 1018 | 567.3 | 226.92 | 265.2564 | 386.3 | 324.1 | 335.3 | 310.9 | 698.1 | 63.7 | 18.9 | 106.7 | 5.1 | 190.8 | 6.1 | 921.5 | 889.4 | 868.6 | 886.1 | 911.3 | 787.4 | 756.1 | 780.9 | 773.4 | 799.2 | 155.8 | 178.6 | 219 | 354.5 | 348.3 | 290.9 | 310.4 | 398.7 | 287
1209 | 1019 | 567 | 226.8 | 265.1161 | 386.7 | 324.5 | 336.8 | 311.3 | 680.1 | 63.7 | 18.9 | 106.9 | 4.6 | 209.1 | 6.2 | 921.6 | 883.4 | 871.2 | 885.3 | 900.6 | 788.1 | 749.6 | 773.7 | 771.2 | 799.5 | 159.1 | 176.7 | 219.1 | 354.4 | 347.9 | 291.1 | 310.4 | 398.9 | 287.2
1210 | 1020 | 567.7 | 227.08 | 265.4434 | 385.9 | 324.9 | 338.2 | 311.8 | 652.6 | 63.7 | 18.9 | 106.9 | 5 | 215.1 | 6.2 | 922.6 | 882.6 | 876.5 | 888.6 | 909 | 788.3 | 750.8 | 773.6 | 771.1 | 800.3 | 158.1 | 173.7 | 219.3 | 354.3 | 347.5 | 291.3 | 310.5 | 399.1 | 287.4
1211 | 1021 | 568.4 | 227.36 | 265.7707 | 385.4 | 325.5 | 338.4 | 312.3 | 635.6 | 63.6 | 18.9 | 106.9 | 4.7 | 200.9 | 5.8 | 923.6 | 877.6 | 866 | 883.4 | 913.7 | 788 | 745.5 | 769.2 | 768.8 | 799.3 | 154.3 | 171.7 | 219.5 | 354.6 | 347.1 | 291.5 | 310.6 | 399.2 | 287.6
1212 | 1022 | 568 | 227.2 | 265.5837 | 385.8 | 325.5 | 337.7 | 312.4 | 620.4 | 63.5 | 18.9 | 106.9 | 4.7 | 226.1 | 5.4 | 924.6 | 868.2 | 851.9 | 874.9 | 911.3 | 787.6 | 733.7 | 757.9 | 762.6 | 795.6 | 151.2 | 171.2 | 219.7 | 354.9 | 346.6 | 291.7 | 310.6 | 399.4 | 287.8
1213 | 1023 | 567.8 | 227.12 | 265.4902 | 386.7 | 325.3 | 336.8 | 312.6 | 592.4 | 63.4 | 18.9 | 107 | 4.7 | 231 | 6.3 | 924.6 | 870.3 | 849.3 | 873.1 | 907.3 | 786.8 | 726.4 | 752.9 | 756 | 794 | 149.7 | 170.3 | 219.9 | 354.7 | 346.1 | 291.9 | 310.6 | 399.5 | 288
1214 | 1024 | 565.5 | 226.2 | 264.4148 | 386.9 | 325.2 | 335.8 | 312.7 | 597.3 | 63.4 | 18.9 | 107 | 4.8 | 212.6 | 6.9 | 924.7 | 870.2 | 837.6 | 869.6 | 917.2 | 786.8 | 723.1 | 752.6 | 753.6 | 794.3 | 149.2 | 169.7 | 220 | 354.5 | 345.6 | 292.1 | 310.7 | 399.6 | 288.2
1215 | 1025 | 565.8 | 226.32 | 264.555 | 386.7 | 324.6 | 336.2 | 313 | 585.4 | 63.3 | 18.9 | 107.1 | 4.4 | 202.5 | 6.4 | 924.8 | 869.1 | 835.5 | 866.8 | 926.8 | 785.7 | 719.3 | 742.2 | 749.5 | 794.6 | 149.7 | 169.1 | 220.2 | 354.4 | 345.3 | 292.2 | 310.8 | 399.7 | 288.3
1216 | 1026 | 567.3 | 226.92 | 265.2564 | 387.4 | 324.3 | 336.9 | 312.4 | 566.9 | 63.4 | 18.9 | 107.1 | 4.6 | 194 | 5.7 | 925.6 | 863.1 | 838.9 | 863.9 | 932.1 | 784.9 | 715.9 | 742.9 | 746.3 | 793.8 | 148.3 | 167.2 | 220.4 | 354.5 | 345.1 | 292.4 | 310.9 | 399.8 | 288.5
1217 | 1027 | 568.4 | 227.36 | 265.7707 | 387.4 | 323.7 | 337.1 | 312.4 | 563.6 | 63.5 | 18.9 | 107.1 | 4.6 | 179.2 | 5.8 | 926.1 | 856.1 | 847.7 | 862 | 923 | 784.6 | 710.4 | 743.7 | 742.9 | 792.1 | 149.3 | 167.8 | 220.6 | 354.7 | 345.1 | 292.6 | 310.9 | 399.9 | 288.7
1218 | 1028 | 568.2 | 227.28 | 265.6772 | 387.7 | 323.5 | 337.2 | 312.6 | 570.6 | 63.6 | 18.9 | 107.2 | 4.6 | 206.4 | 6.3 | 925 | 856.3 | 854.2 | 868.9 | 912.9 | 784.7 | 712.1 | 749.5 | 741.7 | 790.9 | 156.2 | 172 | 220.7 | 355 | 344.9 | 292.8 | 311 | 400.1 | 288.9
1219 | 1029 | 566.8 | 226.72 | 265.0226 | 388.5 | 323.1 | 337.1 | 312.2 | 591.8 | 63.6 | 18.9 | 107.3 | 4.9 | 204.9 | 6.5 | 923.6 | 856.6 | 861.7 | 871.8 | 927.2 | 784.8 | 718.9 | 756.3 | 744.1 | 791.7 | 156.6 | 170.1 | 220.9 | 355.1 | 344.6 | 292.9 | 311 | 400.2 | 289.1
1220 | 1030 | 566.8 | 226.72 | 265.0226 | 387.7 | 323.2 | 336.9 | 311.9 | 624.3 | 63.6 | 18.9 | 107.3 | 5.8 | 186.6 | 6.9 | 923 | 856.5 | 865 | 875.3 | 911.6 | 785.4 | 725.6 | 763.1 | 747.8 | 791.5 | 155.9 | 168.5 | 221.1 | 355 | 344.3 | 293.1 | 311 | 400.3 | 289.3
1221 | 1031 | 566.2 | 226.48 | 264.7421 | 387.4 | 323.4 | 337.1 | 311.7 | 643.1 | 63.6 | 18.9 | 107.5 | 6.3 | 215.2 | 7.6 | 922.5 | 855.2 | 873.6 | 878 | 912 | 786.2 | 735 | 767.1 | 752.7 | 792.9 | 154.6 | 167.6 | 221.2 | 354.8 | 344.2 | 293.2 | 311.1 | 400.5 | 289.4
1222 | 1032 | 565.8 | 226.32 | 264.555 | 387.3 | 323.7 | 337.9 | 311.6 | 646.4 | 63.6 | 18.9 | 107.6 | 5.7 | 198 | 9.2 | 922.6 | 856.7 | 871.8 | 877.2 | 905.4 | 786.5 | 732.6 | 770.9 | 754 | 789.4 | 155.5 | 169.1 | 221.4 | 354.8 | 344.9 | 293.4 | 311.1 | 400.8 | 289.6
1223 | 1033 | 566.3 | 226.52 | 264.7888 | 387.3 | 324.1 | 338.5 | 311.2 | 632.1 | 63.6 | 18.9 | 107.7 | 5.6 | 199.2 | 9.7 | 923 | 865.1 | 856 | 874.7 | 898 | 786 | 733.1 | 763.1 | 754.3 | 790.6 | 154 | 167.3 | 221.6 | 354.7 | 346 | 293.5 | 311.4 | 401 | 289.8
1224 | 1034 | 566.9 | 226.76 | 265.0694 | 387.8 | 324.5 | 338.6 | 311.2 | 609.9 | 63.6 | 18.9 | 107.8 | 4.9 | 203.9 | 9 | 923.7 | 866.7 | 849.1 | 871.8 | 900.2 | 785.4 | 730.6 | 762.4 | 752.1 | 790.1 | 153.2 | 165.9 | 221.7 | 354.5 | 346 | 293.6 | 311.5 | 401.2 | 290
1225 | 1035 | 567.4 | 226.96 | 265.3032 | 388.2 | 324.7 | 338.1 | 311.4 | 599.1 | 63.6 | 18.9 | 107.8 | 4.6 | 201.2 | 9.1 | 924 | 867.7 | 850.9 | 874.5 | 915.6 | 784.4 | 733 | 753.5 | 751.5 | 792.1 | 152.2 | 164.7 | 221.9 | 354.3 | 346.4 | 293.8 | 311.8 | 401.4 | 290.2
1226 | 1036 | 567.2 | 226.88 | 265.2096 | 388.5 | 324.8 | 338.2 | 311.8 | 581.2 | 63.6 | 18.9 | 107.7 | 4.6 | 192.2 | 10.3 | 924.2 | 865.2 | 854.9 | 875.1 | 909.8 | 783.1 | 731.9 | 749.4 | 749.8 | 792.1 | 151 | 163 | 222 | 354.3 | 347 | 294 | 312 | 401.5 | 290.3
1227 | 1037 | 568.6 | 227.44 | 265.8643 | 388.3 | 324.7 | 337.6 | 311.8 | 572.6 | 63.6 | 18.9 | 107.6 | 4.7 | 208 | 9.7 | 924.5 | 867.3 | 857.1 | 877.5 | 907.1 | 782.1 | 734.7 | 752 | 749.2 | 792.8 | 150.9 | 162.3 | 222.2 | 354.3 | 346.9 | 294.1 | 312 | 401.7 | 290.5
1228 | 1038 | 566.5 | 226.6 | 264.8823 | 388.1 | 324.4 | 337.1 | 311.7 | 568.9 | 63.8 | 18.8 | 107.6 | 5 | 206.8 | 8.8 | 924.3 | 871.2 | 860.9 | 877.7 | 916.4 | 781.4 | 739.2 | 754.9 | 751.1 | 794.3 | 150.3 | 160 | 222.3 | 354.4 | 347.6 | 294.3 | 312.1 | 401.8 | 290.7
1229 | 1039 | 565.6 | 226.24 | 264.4615 | 388.4 | 324.4 | 337.3 | 311.9 | 586.8 | 63.9 | 18.8 | 107.7 | 5.1 | 219.5 | 8 | 923.8 | 878.5 | 850.5 | 877.3 | 913.8 | 781.4 | 741.3 | 760.8 | 753.6 | 793.1 | 149.3 | 162.9 | 222.5 | 354.5 | 348.1 | 294.4 | 312.4 | 402 | 290.9
1230 | 1040 | 565.5 | 226.2 | 264.4148 | 388.7 | 324.2 | 337.3 | 311.8 | 601.6 | 64 | 18.8 | 107.8 | 5.6 | 237.3 | 6.9 | 923.1 | 879.3 | 848.4 | 869.6 | 914.7 | 781.9 | 738.1 | 759.7 | 753.3 | 793.7 | 149.8 | 161.7 | 222.6 | 354.5 | 348.4 | 294.6 | 312.7 | 402.2 | 291.1
1231 | 1041 | 567.8 | 227.12 | 265.4902 | 389.2 | 324.2 | 336.7 | 311.6 | 599.4 | 64 | 18.8 | 107.9 | 5.3 | 235.9 | 5.4 | 923.3 | 881.8 | 853.7 | 869.6 | 915.9 | 782 | 743.3 | 761.8 | 754.4 | 795.3 | 149.8 | 161.9 | 222.7 | 354.5 | 348.6 | 294.8 | 312.7 | 402.4 | 291.3
1232 | 1042 | 568 | 227.2 | 265.5837 | 389.4 | 324.2 | 336.5 | 311.9 | 603.9 | 64 | 18.8 | 107.9 | 5.4 | 219.4 | 4.8 | 924.6 | 881.1 | 848.8 | 866.7 | 928 | 782.1 | 741.6 | 762.2 | 754.7 | 794.3 | 148.7 | 160.5 | 222.9 | 354.7 | 349 | 294.9 | 313 | 402.5 | 291.5
1233 | 1043 | 567.7 | 227.08 | 265.4434 | 389.3 | 324.3 | 336.6 | 312.3 | 593.2 | 64 | 18.8 | 107.8 | 5.3 | 224.4 | 4.5 | 924.7 | 884.3 | 849.7 | 865.7 | 930.8 | 782.3 | 737.3 | 761.9 | 752.4 | 793.5 | 147.4 | 158.7 | 223 | 354.9 | 349.1 | 295.1 | 313.1 | 402.7 | 291.6
1234 | 1044 | 566.8 | 226.72 | 265.0226 | 389.1 | 324.2 | 336.7 | 312.6 | 601 | 63.9 | 18.8 | 107.8 | 5.2 | 232.4 | 4 | 924.7 | 884.4 | 852.6 | 867.8 | 932.9 | 782.5 | 736.1 | 764.9 | 752 | 792.5 | 146.5 | 157 | 223.2 | 355.1 | 349.4 | 295.2 | 313.3 | 402.8 | 291.8
1235 | 1045 | 566.1 | 226.44 | 264.6953 | 389.3 | 324.2 | 337 | 312.6 | 608 | 63.9 | 18.8 | 107.6 | 4.7 | 221.5 | 4.3 | 924.1 | 885.6 | 852 | 869.5 | 931.6 | 782.6 | 738.1 | 767.4 | 752.6 | 792.8 | 145.9 | 156.5 | 223.3 | 355.1 | 349.5 | 295.4 | 313.6 | 403 | 292
1236 | 1046 | 565.3 | 226.12 | 264.3213 | 389 | 324.3 | 338 | 312.7 | 607.9 | 63.9 | 18.8 | 107.6 | 5.3 | 199.1 | 4.3 | 923.4 | 881.7 | 845.9 | 867.5 | 929.7 | 782.5 | 738.2 | 764.2 | 752.2 | 792.8 | 144.9 | 155.7 | 223.4 | 355 | 349.8 | 295.5 | 313.8 | 403.1 | 292.2
1237 | 1047 | 566.5 | 226.6 | 264.8823 | 389 | 324.6 | 338.4 | 312.5 | 592.6 | 64 | 18.8 | 107.6 | 5.3 | 198.8 | 4.6 | 923.6 | 886.5 | 848.2 | 866.2 | 919.6 | 782.1 | 736.7 | 765 | 751.4 | 792.8 | 144.1 | 155.2 | 223.6 | 355 | 350.6 | 295.7 | 313.9 | 403.2 | 292.4
1238 | 1048 | 566.5 | 226.6 | 264.8823 | 389.7 | 324.8 | 338.5 | 312.4 | 589 | 64.1 | 18.8 | 107.7 | 5.2 | 210.7 | 5.5 | 923.4 | 886.7 | 855.4 | 867.3 | 913.6 | 781.9 | 737.8 | 763.8 | 751.2 | 793 | 145.1 | 156.7 | 223.7 | 355 | 351.8 | 295.8 | 314 | 403.3 | 292.6
1239 | 1049 | 566 | 226.4 | 264.6486 | 389.3 | 324.9 | 337.7 | 312.7 | 589.1 | 64.1 | 18.8 | 107.7 | 5.3 | 217.3 | 5.6 | 923.4 | 885.1 | 861.8 | 870.4 | 914.2 | 781.7 | 740.2 | 763.6 | 751.6 | 793.9 | 149.3 | 163.1 | 223.8 | 354.8 | 352.1 | 295.9 | 314.1 | 403.5 | 292.8
1240 | 1050 | 567.2 | 226.88 | 265.2096 | 389.9 | 325.1 | 336.7 | 312.9 | 582.2 | 64.1 | 18.8 | 107.8 | 5.3 | 236 | 4.7 | 923.2 | 879.9 | 863.5 | 871.5 | 917.9 | 781.2 | 744 | 761.7 | 752.7 | 795.8 | 148.9 | 163.2 | 224 | 354.9 | 352.5 | 296.1 | 314.3 | 403.6 | 293
1241 | 1051 | 567.1 | 226.84 | 265.1629 | 389.8 | 325.2 | 336.6 | 312.9 | 582.1 | 64.1 | 18.8 | 107.8 | 5.1 | 231.9 | 4.6 | 923 | 886.2 | 859.9 | 872.8 | 920.1 | 780.9 | 743.6 | 761 | 753.9 | 796.7 | 145.8 | 158.8 | 224.1 | 355.2 | 352.7 | 296.2 | 314.5 | 403.8 | 293.1
1242 | 1052 | 568.6 | 227.44 | 265.8643 | 389.6 | 325.3 | 336.5 | 312.9 | 581.5 | 64.2 | 18.8 | 107.8 | 5.4 | 215.1 | 4.5 | 922.9 | 882 | 860 | 870.2 | 917.6 | 781 | 737.8 | 759.7 | 752.4 | 795.5 | 144.5 | 157.1 | 224.2 | 355.4 | 352.7 | 296.3 | 314.5 | 403.9 | 293.3
1243 | 1053 | 565.7 | 226.28 | 264.5083 | 389.4 | 325.4 | 336.3 | 312.7 | 589 | 64.3 | 18.8 | 107.8 | 5.9 | 205.2 | 5.1 | 924.5 | 867.3 | 845.7 | 859.1 | 912.2 | 780.9 | 727.5 | 754.4 | 747.3 | 790.8 | 142.9 | 155 | 224.4 | 355.4 | 352.8 | 296.5 | 314.5 | 404.1 | 293.5
1244 | 1054 | 565.5 | 226.2 | 264.4148 | 390 | 325.5 | 337.1 | 312.8 | 589.7 | 64.4 | 18.8 | 107.9 | 5.7 | 217.2 | 5.8 | 924.4 | 865.1 | 841.5 | 853.4 | 903.2 | 780.9 | 724.3 | 756.1 | 744.1 | 789.9 | 141.9 | 153.7 | 224.5 | 355.4 | 352.5 | 296.6 | 314.7 | 404.2 | 293.7
1245 | 1055 | 567.4 | 226.96 | 265.3032 | 391.1 | 325.5 | 337.7 | 313 | 611.2 | 64.5 | 18.8 | 108 | 5.1 | 223.2 | 6.3 | 923.1 | 871.3 | 847.5 | 855.6 | 895.2 | 781 | 728.4 | 760.8 | 744.7 | 790 | 140.8 | 151 | 224.7 | 355.5 | 352.1 | 296.7 | 314.7 | 404.3 | 293.9
1246 | 1056 | 567.7 | 227.08 | 265.4434 | 391.9 | 325.7 | 337.3 | 313.5 | 610.1 | 64.5 | 18.8 | 108.1 | 5.4 | 223.4 | 5.9 | 921.9 | 874.1 | 850 | 860.3 | 892.3 | 780.6 | 734 | 763.3 | 747.5 | 790.9 | 139.8 | 147.6 | 224.8 | 355.6 | 351.8 | 296.9 | 314.8 | 404.4 | 294.1
1247 | 1057 | 566.4 | 226.56 | 264.8356 | 391.8 | 325.9 | 337.3 | 314 | 603.2 | 64.5 | 18.8 | 108.3 | 5.5 | 234.7 | 5.3 | 920.7 | 876.6 | 848.9 | 861.8 | 900 | 780.3 | 737 | 763.6 | 749.8 | 791.8 | 140.6 | 148.4 | 224.9 | 355.6 | 351.3 | 297 | 314.9 | 404.5 | 294.2
1248 | 1058 | 566.7 | 226.68 | 264.9759 | 392.4 | 325.9 | 337.1 | 314.3 | 603.8 | 64.6 | 18.8 | 108.4 | 5.2 | 231.3 | 4.9 | 919.6 | 875 | 854.1 | 865.7 | 908.6 | 780 | 741 | 767.9 | 752.5 | 792.4 | 140 | 145.8 | 225.1 | 355.7 | 351 | 297.2 | 315.1 | 404.6 | 294.4
1249 | 1059 | 566.9 | 226.76 | 265.0694 | 392.8 | 326.1 | 337.4 | 314.3 | 611.6 | 64.6 | 18.8 | 108.5 | 4.8 | 226.3 | 4.6 | 919.3 | 871.5 | 863 | 869.8 | 908.5 | 779.9 | 746 | 769.8 | 754.9 | 793.6 | 139 | 144.7 | 225.2 | 355.5 | 350.6 | 297.3 | 315.2 | 404.8 | 294.6
1250 | 1060 | 566.7 | 226.68 | 264.9759 | 391.6 | 326.4 | 337.3 | 314.3 | 623.3 | 64.5 | 18.8 | 108.5 | 5.3 | 222.9 | 4.6 | 919 | 865.2 | 869.4 | 867.1 | 905.5 | 779.5 | 750.8 | 770.7 | 758.1 | 795.4 | 138.5 | 149.2 | 225.3 | 355.3 | 350.1 | 297.5 | 315.2 | 405 | 294.7
1251 | 1061 | 565 | 226 | 264.181 | 391.2 | 326.8 | 337.1 | 313.7 | 627 | 64.5 | 18.8 | 108.4 | 5.3 | 232.7 | 4.5 | 919 | 872.5 | 869.7 | 868 | 906.4 | 778.9 | 754.2 | 770.9 | 761.8 | 796.6 | 136.3 | 143.6 | 225.5 | 355.2 | 349.8 | 297.6 | 315.3 | 405.2 | 294.9
1252 | 1062 | 563.6 | 225.44 | 263.5264 | 391.3 | 327 | 337 | 313.4 | 610.1 | 64.5 | 18.8 | 108.2 | 5.3 | 233.2 | 5.2 | 921.7 | 873.7 | 867.8 | 866.3 | 908.7 | 777.7 | 748.5 | 755.9 | 761.3 | 795.7 | 135.7 | 143.7 | 225.6 | 355.2 | 349.9 | 297.8 | 315.5 | 405.4 | 295.1
1253 | 1063 | 565 | 226 | 264.181 | 391.4 | 327.2 | 337.4 | 313.7 | 585.3 | 64.5 | 18.8 | 108.1 | 5.1 | 224.4 | 7.5 | 924.2 | 866.5 | 867.1 | 862 | 910.8 | 776.4 | 737.9 | 747.7 | 755.7 | 794.2 | 135.4 | 145.7 | 225.7 | 355.5 | 350.6 | 297.9 | 315.6 | 405.6 | 295.3
1254 | 1064 | 566.1 | 226.44 | 264.6953 | 391.3 | 327.3 | 337 | 314.4 | 576.4 | 64.6 | 18.8 | 108 | 5.4 | 208.2 | 7.1 | 924.3 | 867.5 | 866.5 | 858.9 | 915.4 | 775.4 | 737.8 | 746.2 | 752.2 | 794.3 | 135.6 | 147 | 225.9 | 356 | 351.6 | 298 | 315.8 | 405.8 | 295.4
1255 | 1065 | 566.9 | 226.76 | 265.0694 | 391 | 327.2 | 336.6 | 315.3 | 568.8 | 64.7 | 18.8 | 108 | 5 | 218.3 | 5.9 | 923.8 | 870.4 | 864.9 | 862.1 | 924.5 | 774.8 | 735.8 | 748.3 | 750.4 | 793.3 | 135.3 | 146.7 | 226 | 356.4 | 352.4 | 298.2 | 316 | 405.9 | 295.6
1256 | 1066 | 567.1 | 226.84 | 265.1629 | 391.1 | 327.1 | 336.8 | 315.6 | 579.8 | 64.8 | 18.8 | 108.1 | 5.4 | 210 | 5.8 | 922.4 | 872.5 | 863.9 | 864.5 | 920.4 | 775.1 | 743.8 | 757.6 | 752.6 | 794.8 | 134.8 | 145.5 | 226.1 | 356.5 | 352.7 | 298.3 | 316.2 | 406 | 295.8
1257 | 1067 | 565.7 | 226.28 | 264.5083 | 390.6 | 327.2 | 336.6 | 314.9 | 608.8 | 64.8 | 18.8 | 108.1 | 4.8 | 210.4 | 7.7 | 921.2 | 868 | 865.1 | 862.5 | 915.3 | 775.2 | 749.7 | 763 | 756.4 | 795.8 | 135 | 145.8 | 226.3 | 356.6 | 353 | 298.4 | 316.4 | 406.2 | 296
1258 | 1068 | 565.9 | 226.36 | 264.6018 | 390.3 | 327.5 | 336.6 | 314.6 | 630.8 | 64.9 | 18.8 | 108.3 | 4.3 | 199 | 9.4 | 920.5 | 865.8 | 866.8 | 862.1 | 913.1 | 775.4 | 754.3 | 766.8 | 761.2 | 797.1 | 134.9 | 146.1 | 226.4 | 356.7 | 353.1 | 298.6 | 316.5 | 406.4 | 296.2
1259 | 1069 | 565.5 | 226.2 | 264.4148 | 390.3 | 327.6 | 336.9 | 314 | 632.2 | 65 | 18.8 | 108.3 | 4.2 | 210.1 | 9.7 | 919.4 | 865.2 | 873.5 | 862.5 | 913.3 | 775.6 | 758.5 | 767.9 | 764.9 | 797.3 | 134.5 | 145.9 | 226.5 | 356.9 | 353.1 | 298.7 | 316.8 | 406.6 | 296.4
1260 | 1070 | 565.2 | 226.08 | 264.2745 | 389.9 | 327.6 | 336.7 | 314 | 630.3 | 65 | 18.8 | 108.2 | 3.9 | 218.3 | 8.7 | 918.8 | 867.3 | 879.2 | 862.6 | 914.9 | 775.7 | 760.5 | 767.1 | 768.2 | 797.4 | 134.2 | 145.9 | 226.7 | 356.7 | 353.4 | 298.8 | 317 | 406.9 | 296.6
1261 | 1071 | 566 | 226.4 | 264.6486 | 390.7 | 327.9 | 336.1 | 314.4 | 635.2 | 65.1 | 18.8 | 108.2 | 4 | 224.9 | 7.4 | 918.1 | 870 | 876.3 | 862.9 | 917.3 | 775.8 | 761 | 767.4 | 771.1 | 798.9 | 133.7 | 145.4 | 226.8 | 356.8 | 353.5 | 299 | 317.1 | 407.1 | 296.8
1262 | 1072 | 566.6 | 226.64 | 264.9291 | 391.5 | 328.5 | 336.1 | 314.7 | 648.5 | 65.1 | 18.8 | 108.2 | 4.5 | 243 | 6.6 | 917.4 | 871 | 870.2 | 862 | 905.7 | 776.3 | 764.5 | 769 | 773.6 | 799.5 | 133.4 | 145 | 226.9 | 356.9 | 353.5 | 299.1 | 317.2 | 407.3 | 296.9
1263 | 1073 | 566.7 | 226.68 | 264.9759 | 393.3 | 329.1 | 335.8 | 314.5 | 662.9 | 65.1 | 18.8 | 108.3 | 4.9 | 221.9 | 6.5 | 917.2 | 871.8 | 866.7 | 862.3 | 909.3 | 777 | 766.6 | 769.5 | 777.5 | 800.3 | 133.4 | 144.9 | 227.1 | 356.9 | 353.6 | 299.2 | 317.4 | 407.5 | 297.1
1264 | 1074 | 566.7 | 226.68 | 264.9759 | 395 | 329.2 | 335.4 | 313.9 | 669.3 | 65.1 | 18.8 | 108.3 | 4.5 | 215.6 | 6.8 | 917.6 | 890.5 | 855.7 | 860.4 | 905.5 | 777.7 | 766.6 | 770.7 | 780.4 | 800.7 | 133.3 | 144.6 | 227.2 | 356.8 | 353.8 | 299.3 | 317.5 | 407.7 | 297.3
1265 | 1075 | 568.3 | 227.32 | 265.724 | 395 | 329.2 | 336.1 | 313.9 | 653.7 | 65.1 | 18.8 | 108.3 | 5 | 205.6 | 8.1 | 917.7 | 881.6 | 844.5 | 854.3 | 906.9 | 777.9 | 756.1 | 766.2 | 776.8 | 798.9 | 132.3 | 143.3 | 227.3 | 356.9 | 354 | 299.5 | 317.7 | 407.9 | 297.5
1266 | 1076 | 567.1 | 226.84 | 265.1629 | 395.7 | 329.3 | 336.9 | 314 | 638.6 | 65.2 | 18.8 | 108.3 | 5.2 | 212.2 | 8.2 | 918.6 | 872.1 | 840.4 | 851.6 | 901 | 778.1 | 752.4 | 760.1 | 773.7 | 799 | 131.7 | 142.4 | 227.5 | 356.9 | 354.1 | 299.6 | 317.9 | 408 | 297.6
1267 | 1077 | 566.5 | 226.6 | 264.8823 | 397.3 | 329.5 | 338 | 314 | 632.1 | 65.2 | 18.8 | 108.2 | 4.9 | 206.3 | 7.8 | 918.9 | 875.4 | 841.7 | 853 | 898.9 | 778 | 746.1 | 758.5 | 769.5 | 797.8 | 132.7 | 143.9 | 227.6 | 356.8 | 354.3 | 299.7 | 318 | 408.1 | 297.8
1268 | 1078 | 566.8 | 226.72 | 265.0226 | 397.4 | 329.6 | 338.2 | 314.6 | 614.4 | 65.2 | 18.8 | 108.3 | 5 | 210.9 | 7.7 | 918.5 | 879.1 | 842.8 | 853.5 | 898.7 | 777.4 | 745.7 | 759.8 | 767.2 | 799.1 | 132.8 | 143.4 | 227.7 | 356.7 | 353.8 | 299.8 | 318.1 | 408.2 | 298
1269 | 1079 | 567.8 | 227.12 | 265.4902 | 397.2 | 329.8 | 338.5 | 314.8 | 604.1 | 65.1 | 18.8 | 108.2 | 5.1 | 205.2 | 7.6 | 918.6 | 877.9 | 843.8 | 853.6 | 908.1 | 776.9 | 743 | 757 | 765.5 | 799.9 | 133.4 | 144.3 | 227.9 | 356.9 | 353.3 | 300 | 318.2 | 408.3 | 298.1
1270 | 1080 | 565.9 | 226.36 | 264.6018 | 398.3 | 329.8 | 338.8 | 315 | 588.6 | 65.1 | 18.8 | 108.3 | 4.6 | 222.6 | 6.7 | 918.8 | 875.3 | 837.8 | 852.7 | 912.9 | 776 | 741.3 | 752.1 | 763.2 | 799.9 | 134.8 | 145.7 | 228 | 356.8 | 353 | 300.1 | 318.3 | 408.4 | 298.3
1271 | 1081 | 566.3 | 226.52 | 264.7888 | 398 | 329.8 | 339.2 | 315 | 581.1 | 65.1 | 18.8 | 108.4 | 5.4 | 194.3 | 6.8 | 918.5 | 873.6 | 831.1 | 852.5 | 912.5 | 774.9 | 744.1 | 749.9 | 763.3 | 800.1 | 135.7 | 146.5 | 228.1 | 356.8 | 353.5 | 300.2 | 318.5 | 408.5 | 298.5
1272 | 1082 | 566.2 | 226.48 | 264.7421 | 398 | 329.9 | 338.6 | 315.2 | 596.5 | 65.1 | 18.8 | 108.4 | 5.5 | 197.5 | 7 | 917.6 | 874.1 | 831.7 | 850.7 | 919 | 774.9 | 746.5 | 754.8 | 765.7 | 800.8 | 137.2 | 148.3 | 228.3 | 357.1 | 353.8 | 300.3 | 318.8 | 408.7 | 298.6
1273 | 1083 | 566.4 | 226.56 | 264.8356 | 398 | 329.7 | 338.5 | 315.2 | 601.8 | 65.1 | 18.8 | 108.5 | 4.9 | 214.6 | 7.1 | 918.3 | 880.2 | 833 | 851.6 | 919.7 | 775.1 | 749.6 | 756.1 | 768.2 | 802.2 | 136.8 | 147.8 | 228.4 | 357.4 | 353.6 | 300.4 | 319 | 408.8 | 298.8
1274 | 1084 | 570.1 | 228.04 | 266.5656 | 398.3 | 329.5 | 339 | 315.3 | 601.2 | 65.1 | 18.8 | 108.5 | 5.3 | 225.1 | 6.2 | 918.1 | 881.5 | 835.5 | 852.5 | 912.1 | 774.9 | 753.5 | 759.1 | 769.9 | 802.8 | 136.2 | 147 | 228.5 | 357.4 | 353.3 | 300.5 | 319 | 409 | 299
1275 | 1085 | 570.7 | 228.28 | 266.8462 | 399.8 | 329.7 | 339.6 | 315.3 | 600.7 | 65.1 | 18.8 | 108.5 | 4.8 | 222 | 5.2 | 918.1 | 880.1 | 839.5 | 854.5 | 909.8 | 774.8 | 750.5 | 760.7 | 770.5 | 802 | 136.1 | 147.2 | 228.7 | 357.2 | 353.1 | 300.7 | 319.2 | 409.2 | 299.2
1276 | 1086 | 568.9 | 227.56 | 266.0045 | 401.1 | 329.7 | 339.1 | 314.6 | 595.2 | 65.2 | 18.8 | 108.4 | 4.1 | 227.4 | 4.4 | 919 | 882.5 | 836.6 | 853.6 | 920.8 | 774.4 | 751.5 | 759.8 | 771.6 | 803.6 | 134.5 | 144.3 | 228.8 | 357.5 | 353.7 | 300.8 | 319.3 | 409.4 | 299.4
1277 | 1087 | 567.2 | 226.88 | 265.2096 | 401.3 | 329.7 | 339.1 | 314.6 | 588.4 | 65.2 | 18.8 | 108.3 | 4.2 | 243.9 | 4.4 | 919.3 | 878.3 | 834.2 | 852.9 | 919.4 | 774.1 | 750.1 | 751.2 | 770.4 | 803.2 | 133.1 | 141.9 | 228.9 | 357.9 | 354.1 | 300.9 | 319.4 | 409.5 | 299.6
1278 | 1088 | 566.9 | 226.76 | 265.0694 | 400.9 | 329.9 | 339.4 | 314.8 | 577.2 | 65.2 | 18.8 | 108.4 | 4.5 | 201.4 | 4.9 | 919 | 866.5 | 823.4 | 848.4 | 917.3 | 773.5 | 738.6 | 745.2 | 764.5 | 800.5 | 131.5 | 140.3 | 229.1 | 358.5 | 354.8 | 301 | 319.7 | 409.6 | 299.7
1279 | 1089 | 566.2 | 226.48 | 264.7421 | 401.3 | 329.7 | 339.2 | 315.2 | 575 | 65.2 | 18.8 | 108.4 | 4.6 | 198.6 | 5.4 | 918.4 | 868.9 | 829.5 | 848.1 | 922.5 | 773.1 | 739.5 | 747.4 | 760.5 | 801.5 | 131.2 | 139.8 | 229.2 | 358.8 | 355.3 | 301.1 | 319.9 | 409.7 | 299.9
1280 | 1090 | 567.8 | 227.12 | 265.4902 | 401.5 | 329.3 | 338.4 | 315.9 | 583.6 | 65.3 | 18.8 | 108.5 | 4.6 | 204.2 | 5.6 | 917.5 | 869.1 | 835.7 | 849.1 | 914.9 | 772.7 | 746.1 | 752.2 | 762.4 | 803.1 | 130.5 | 138.4 | 229.3 | 358.9 | 355.7 | 301.3 | 320.2 | 409.8 | 300.1
1281 | 1091 | 568.3 | 227.32 | 265.724 | 401.2 | 329.4 | 338.4 | 316.1 | 599.7 | 65.3 | 18.8 | 108.5 | 5.1 | 203.7 | 5.9 | 916.9 | 879.8 | 835 | 851.3 | 910.8 | 772.9 | 750.9 | 754.5 | 767.1 | 803.9 | 129.9 | 138.4 | 229.5 | 358.8 | 355.9 | 301.4 | 320.5 | 409.9 | 300.3
1282 | 1092 | 568.2 | 227.28 | 265.6772 | 400.2 | 329.5 | 338.5 | 315.6 | 603.5 | 65.4 | 18.8 | 108.6 | 5.3 | 218.3 | 6.7 | 916 | 879 | 833.4 | 850.8 | 917.8 | 772.8 | 750.5 | 754.3 | 768.4 | 804.7 | 129.7 | 138.7 | 229.6 | 358.6 | 356.4 | 301.5 | 320.6 | 410.1 | 300.5
1283 | 1093 | 567.9 | 227.16 | 265.537 | 400.2 | 329.7 | 338.9 | 315.3 | 609.9 | 65.4 | 18.8 | 108.7 | 5.3 | 223.5 | 7.5 | 916 | 877.9 | 835.7 | 850.1 | 913.3 | 772.8 | 752.2 | 758.6 | 769.8 | 804.8 | 129.1 | 137.8 | 229.7 | 358.5 | 356.8 | 301.6 | 320.6 | 410.2 | 300.6
1284 | 1094 | 567 | 226.8 | 265.1161 | 400.3 | 329.7 | 339.3 | 315.3 | 625.5 | 65.4 | 18.8 | 108.8 | 5.7 | 193.8 | 7.2 | 915.4 | 886.9 | 834.9 | 851.1 | 909.1 | 773.3 | 755.9 | 761 | 773.2 | 804 | 128.6 | 137.1 | 229.9 | 358.7 | 357 | 301.7 | 320.8 | 410.4 | 300.8
1285 | 1095 | 567.1 | 226.84 | 265.1629 | 400.5 | 330 | 339.5 | 315.4 | 623.2 | 65.4 | 18.8 | 108.8 | 4.7 | 225.1 | 8 | 915.5 | 891.4 | 833.6 | 851.7 | 911.1 | 774 | 756 | 762.5 | 774.3 | 803.8 | 128 | 136.4 | 230 | 358.9 | 357.3 | 301.8 | 321 | 410.5 | 301
1286 | 1096 | 566.4 | 226.56 | 264.8356 | 401.3 | 330.3 | 340 | 315.4 | 616.8 | 65.5 | 18.8 | 108.7 | 5.1 | 210 | 7.2 | 915.9 | 886.9 | 826.7 | 850.5 | 911.7 | 774.2 | 748.1 | 759.4 | 771.3 | 802.3 | 126.7 | 135.3 | 230.1 | 359 | 357.6 | 301.9 | 321.1 | 410.6 | 301.1
1287 | 1097 | 566.6 | 226.64 | 264.9291 | 401.8 | 330.1 | 340.2 | 315.5 | 606.6 | 65.5 | 18.8 | 108.7 | 5.7 | 195.2 | 8.1 | 917.5 | 885.4 | 830 | 845 | 911.7 | 774.2 | 747.1 | 763.8 | 768.7 | 802.3 | 126 | 134.4 | 230.2 | 358.9 | 357.4 | 302 | 321.1 | 410.7 | 301.3
1288 | 1098 | 567.9 | 227.16 | 265.537 | 402.6 | 330 | 341 | 315.3 | 610.2 | 65.4 | 18.8 | 108.7 | 5.4 | 205.2 | 10.1 | 918 | 881.7 | 839.3 | 845.3 | 913.8 | 774 | 749.4 | 766.8 | 769.7 | 802.8 | 126.6 | 135.1 | 230.4 | 358.7 | 356.8 | 302.1 | 321.2 | 410.8 | 301.4
1289 | 1099 | 569.1 | 227.64 | 266.098 | 403.1 | 330.1 | 341.4 | 315.5 | 623.1 | 65.4 | 18.7 | 108.7 | 5.7 | 214.5 | 10.8 | 918.1 | 884.3 | 843 | 847.1 | 911.1 | 774 | 751 | 768.6 | 770.7 | 803.3 | 127.7 | 136.1 | 230.5 | 358.6 | 356.7 | 302.2 | 321.3 | 410.9 | 301.6
1290 | 1100 | 568.3 | 227.32 | 265.724 | 403.2 | 330.4 | 341.6 | 315.2 | 628.8 | 65.4 | 18.7 | 108.6 | 5.2 | 240.5 | 8.2 | 918 | 881.1 | 850.5 | 850.3 | 912.4 | 774.1 | 756.1 | 770.4 | 773.3 | 803.6 | 127.2 | 135.2 | 230.7 | 358.7 | 356.7 | 302.3 | 321.4 | 411 | 301.8
1291 | 1101 | 567.7 | 227.08 | 265.4434 | 402.1 | 330.8 | 341.5 | 314.9 | 650.1 | 65.5 | 18.8 | 108.6 | 5.2 | 261.6 | 6.6 | 917.9 | 886.3 | 847.1 | 850.1 | 903 | 774.4 | 759.4 | 773.2 | 775.1 | 802.1 | 126.8 | 134.8 | 230.8 | 358.7 | 356.5 | 302.4 | 321.4 | 411.2 | 301.9
1292 | 1102 | 567 | 226.8 | 265.1161 | 401.6 | 330.9 | 341.4 | 314.8 | 659.3 | 65.5 | 18.7 | 108.6 | 5.2 | 238.1 | 5.1 | 917.4 | 887.9 | 834.8 | 847.5 | 903.2 | 774.7 | 758.5 | 770.1 | 776.1 | 801.9 | 126.5 | 134.3 | 230.9 | 359.1 | 356.6 | 302.5 | 321.5 | 411.4 | 302.1
1293 | 1103 | 567.6 | 227.04 | 265.3967 | 401.1 | 331 | 341.4 | 315.1 | 646 | 65.4 | 18.7 | 108.6 | 4.8 | 183.2 | 4 | 917.1 | 882.6 | 831.6 | 843.5 | 901.3 | 775.1 | 756.1 | 763.2 | 774.6 | 801.3 | 126.5 | 133.9 | 231 | 359.2 | 356.8 | 302.6 | 321.5 | 411.6 | 302.3
1294 | 1104 | 568.3 | 227.32 | 265.724 | 400.8 | 331.3 | 341.6 | 315.3 | 642.2 | 65.3 | 18.7 | 108.6 | 4.6 | 210.2 | 4.5 | 917.2 | 874.4 | 829 | 839.8 | 898.7 | 775.4 | 754.7 | 765.6 | 774 | 800.1 | 126.7 | 134.4 | 231.2 | 359.4 | 357 | 302.7 | 321.6 | 411.7 | 302.5
1295 | 1105 | 568.6 | 227.44 | 265.8643 | 401 | 331.3 | 342.4 | 315.4 | 640.3 | 65.2 | 18.7 | 108.7 | 4.6 | 222.2 | 7.2 | 916.5 | 872.4 | 831.9 | 841.2 | 899.2 | 775.3 | 753.2 | 767.5 | 773.5 | 799.7 | 129.3 | 137.5 | 231.3 | 359.8 | 356.6 | 302.9 | 321.8 | 411.8 | 302.7
1296 | 1106 | 567 | 226.8 | 265.1161 | 400.5 | 331.3 | 342.9 | 315.5 | 651 | 65.1 | 18.7 | 108.9 | 4.4 | 214 | 8.9 | 916.4 | 870.2 | 839.8 | 844.1 | 900.6 | 775.1 | 758 | 771.5 | 775.7 | 798.3 | 129.7 | 138.1 | 231.4 | 359.8 | 356.1 | 303 | 321.9 | 411.9 | 302.8
1297 | 1107 | 567.2 | 226.88 | 265.2096 | 400.2 | 331.4 | 342.4 | 315.9 | 660.6 | 65.1 | 18.7 | 109 | 5 | 213.3 | 9.6 | 917 | 868.7 | 849 | 846.2 | 895.4 | 775 | 760.2 | 775.5 | 777.4 | 799.3 | 129.1 | 138.5 | 231.6 | 359.7 | 355.5 | 303.1 | 321.9 | 412 | 303
1298 | 1108 | 568.3 | 227.32 | 265.724 | 400.3 | 331.5 | 342.3 | 316.3 | 656.4 | 65 | 18.7 | 109.1 | 5.4 | 216.9 | 9.9 | 917.8 | 866.9 | 852.9 | 846.3 | 902.1 | 775.1 | 756.2 | 775 | 776.9 | 799.7 | 129.1 | 138.6 | 231.7 | 359.6 | 354.8 | 303.3 | 321.9 | 412.1 | 303.2
1299 | 1109 | 568.8 | 227.52 | 265.9578 | 399.5 | 331.3 | 342.3 | 316.7 | 651.4 | 65.1 | 18.7 | 109.2 | 5.1 | 203.9 | 11.4 | 919.1 | 866.1 | 856.4 | 845 | 907.7 | 775.4 | 749.4 | 774.1 | 773 | 798.8 | 129.4 | 138.7 | 231.8 | 359.6 | 353.9 | 303.4 | 322 | 412.3 | 303.3
1300 | 1110 | 566.1 | 226.44 | 264.6953 | 399.9 | 331.2 | 342.6 | 317.1 | 637.7 | 65.1 | 18.7 | 109.3 | 4.8 | 216.6 | 12.1 | 919.9 | 866.4 | 859.4 | 845.6 | 917.4 | 775.6 | 749.2 | 776.1 | 770.3 | 799.9 | 128.5 | 137.1 | 232 | 359.6 | 353.2 | 303.5 | 322 | 412.4 | 303.5
1301 | 1111 | 566.2 | 226.48 | 264.7421 | 400.1 | 331.6 | 342.4 | 317.1 | 639.7 | 65.2 | 18.7 | 109.2 | 5.2 | 214.9 | 11.8 | 921.2 | 866.1 | 860.3 | 843.2 | 926.3 | 775.8 | 748.7 | 778 | 769.3 | 798.6 | 291.9 | 316.2 | 232.1 | 359.9 | 352.6 | 303.6 | 322.1 | 412.5 | 303.6
1302 | 1112 | 567.2 | 226.88 | 265.2096 | 401.7 | 332.3 | 341.4 | 316.6 | 637.6 | 65.3 | 18.7 | 109.2 | 5 | 205.2 | 11.7 | 921.6 | 863.3 | 861.7 | 845 | 918 | 775.9 | 746.6 | 776.7 | 768.2 | 798.1 | 316.9 | 344.4 | 232.2 | 359.8 | 352.1 | 303.7 | 322.1 | 412.6 | 303.8
1303 | 1113 | 566.6 | 226.64 | 264.9291 | 403.2 | 332.9 | 342 | 316.5 | 648.2 | 65.3 | 18.7 | 109.3 | 4.9 | 206.1 | 12 | 922.3 | 861.4 | 865.8 | 844.2 | 904.4 | 775.8 | 742.2 | 777.8 | 766.5 | 794.4 | 317 | 344.4 | 232.4 | 359.8 | 352.4 | 303.9 | 322.3 | 412.8 | 303.9
1304 | 1114 | 567.7 | 227.08 | 265.4434 | 404 | 333.2 | 342.4 | 316.7 | 656.7 | 65.4 | 18.7 | 109.5 | 4.7 | 217.7 | 11.3 | 922.9 | 868 | 862 | 843.7 | 893.7 | 775.7 | 742 | 775.1 | 765.2 | 795.2 | 317.1 | 344.5 | 232.5 | 360.1 | 352.7 | 304 | 322.4 | 412.9 | 304.1
1305 | 1115 | 567.3 | 226.92 | 265.2564 | 403.3 | 333.3 | 343.2 | 317 | 636.8 | 65.4 | 18.7 | 109.5 | 3.7 | 229 | 8.6 | 922.7 | 869.5 | 863.9 | 844.1 | 906 | 775.1 | 744 | 767.8 | 764.6 | 795.7 | 317.3 | 344.6 | 232.6 | 360.2 | 353.1 | 304.1 | 322.6 | 413.1 | 304.3
1306 | 1116 | 566.9 | 226.76 | 265.0694 | 402.3 | 333.4 | 342.8 | 317.5 | 617 | 65.4 | 18.7 | 109.6 | 4.4 | 218.7 | 7.9 | 922.5 | 866.5 | 868.1 | 846.3 | 917 | 774.2 | 747.9 | 765.6 | 765.4 | 796.1 | 317.6 | 344.8 | 232.8 | 360.1 | 353.5 | 304.2 | 322.7 | 413.2 | 304.5
1307 | 1117 | 566.8 | 226.72 | 265.0226 | 402.8 | 333.4 | 342.6 | 317.7 | 612.6 | 65.5 | 18.7 | 109.7 | 4.8 | 218.1 | 9.5 | 922.8 | 864.9 | 864.6 | 846 | 917.5 | 773.7 | 751.2 | 770.3 | 766.7 | 796.8 | 317.7 | 344.7 | 232.9 | 360.2 | 353.6 | 304.3 | 322.9 | 413.4 | 304.6
1308 | 1118 | 567.9 | 227.16 | 265.537 | 403.2 | 333.2 | 342.5 | 317.5 | 619.8 | 65.5 | 18.7 | 109.7 | 4.4 | 204 | 10.4 | 921.3 | 859.6 | 868.4 | 845.8 | 922.4 | 773.4 | 756.5 | 770.4 | 769.2 | 797.8 | 317.7 | 344.5 | 233.1 | 360.3 | 354.3 | 304.4 | 323 | 413.5 | 304.8
1309 | 1119 | 568 | 227.2 | 265.5837 | 402.4 | 333.4 | 342.5 | 317.4 | 635.5 | 65.6 | 18.7 | 109.6 | 4.3 | 204.4 | 11 | 920.6 | 859.8 | 867 | 845.9 | 925.2 | 773.6 | 762.7 | 772.5 | 773 | 798.1 | 317.7 | 344.2 | 233.2 | 360.4 | 354.3 | 304.5 | 323.1 | 413.7 | 305
1310 | 1120 | 568.7 | 227.48 | 265.911 | 401.1 | 333.5 | 342.7 | 317.2 | 637 | 65.6 | 18.7 | 109.5 | 4.2 | 213.4 | 11 | 920.5 | 863 | 864.9 | 845.4 | 914.7 | 774.2 | 765.7 | 773.4 | 776.1 | 798.9 | 317.8 | 344 | 233.3 | 360.7 | 354.6 | 304.6 | 323.3 | 413.9 | 305.2
1311 | 1121 | 565.3 | 226.12 | 264.3213 | 400.6 | 333.4 | 343 | 317.4 | 639.7 | 65.5 | 18.7 | 109.4 | 5.7 | 210.2 | 10.8 | 919.7 | 869 | 859.9 | 846.7 | 909.5 | 774.4 | 766.9 | 772.7 | 778 | 799.3 | 317.8 | 344 | 233.5 | 360.7 | 355.1 | 304.7 | 323.6 | 414.1 | 305.3
1312 | 1122 | 563.2 | 225.28 | 263.3393 | 400 | 333.4 | 343 | 317.6 | 635.8 | 65.4 | 18.7 | 109.4 | 5.5 | 206.9 | 10.2 | 918.7 | 875 | 857.7 | 844.7 | 898.8 | 774.5 | 770.4 | 770.7 | 778.8 | 800.2 | 318 | 344.3 | 233.6 | 360.7 | 355.3 | 304.7 | 323.7 | 414.2 | 305.5
1313 | 1123 | 564.6 | 225.84 | 263.9939 | 400.1 | 333.5 | 343.3 | 317.7 | 628.8 | 65.3 | 18.7 | 109.3 | 5.2 | 208.5 | 10.6 | 918.6 | 871 | 855.7 | 844 | 902.5 | 774.6 | 771.9 | 763.4 | 780.8 | 801.1 | 318.2 | 344.7 | 233.8 | 360.7 | 355.5 | 304.8 | 323.8 | 414.4 | 305.7
1314 | 1124 | 565.6 | 226.24 | 264.4615 | 399.9 | 333.8 | 343.3 | 318.3 | 627.4 | 65.2 | 18.7 | 109.3 | 6.1 | 197.4 | 10.6 | 919.2 | 868.7 | 861 | 845.5 | 909.9 | 774.8 | 772.9 | 763.9 | 782 | 802.4 | 318.4 | 345.1 | 233.9 | 360.9 | 355.7 | 304.9 | 324 | 414.5 | 305.8
1315 | 1125 | 567.2 | 226.88 | 265.2096 | 399.6 | 334 | 343.2 | 318.4 | 609.7 | 65.1 | 18.7 | 109.2 | 5.8 | 195.7 | 9.7 | 921 | 872.9 | 861.5 | 846.4 | 907.3 | 774.4 | 770.2 | 757.7 | 779.1 | 803.9 | 318.4 | 345.1 | 234 | 361.2 | 355.7 | 305 | 324.2 | 414.7 | 306
1316 | 1126 | 567.5 | 227 | 265.3499 | 400.2 | 334 | 342.9 | 318.7 | 591.2 | 65.1 | 18.7 | 109.3 | 5.8 | 203.5 | 8.8 | 920.6 | 865.4 | 864.4 | 844.3 | 909.3 | 773.9 | 770.3 | 757.9 | 779.5 | 805 | 318.4 | 345 | 234.2 | 361.6 | 355.8 | 305.1 | 324.4 | 414.9 | 306.2
1317 | 1127 | 568.9 | 227.56 | 266.0045 | 399.7 | 334 | 341.5 | 319.2 | 596.9 | 65.1 | 18.7 | 109.3 | 5.9 | 217.8 | 8 | 920.8 | 862.1 | 868.1 | 845.8 | 924.6 | 774 | 771.9 | 763.2 | 780.9 | 804.8 | 318.5 | 345.1 | 234.3 | 361.9 | 355.7 | 305.2 | 324.5 | 415 | 306.4
1318 | 1128 | 568 | 227.2 | 265.5837 | 399 | 334.1 | 341 | 319.6 | 607 | 65.1 | 18.7 | 109.3 | 5.1 | 231.6 | 6.2 | 919.3 | 858.2 | 872 | 843.8 | 911.9 | 773.9 | 774.3 | 767.1 | 782.5 | 805.2 | 318.5 | 345.2 | 234.4 | 362.2 | 355.9 | 305.3 | 324.7 | 415.3 | 306.6
1319 | 1129 | 566.6 | 226.64 | 264.9291 | 398.9 | 334.3 | 340.8 | 319.3 | 596.4 | 65.1 | 18.7 | 109.4 | 5.5 | 249.6 | 4.8 | 919.2 | 856.5 | 869.9 | 843.4 | 915 | 773.9 | 773.3 | 764.3 | 784.2 | 805.6 | 318.6 | 345.1 | 234.6 | 362.4 | 356.6 | 305.4 | 324.9 | 415.5 | 306.7
1320 | 1130 | 565.7 | 226.28 | 264.5083 | 398.1 | 334.3 | 340.6 | 319.4 | 586.6 | 65.1 | 18.7 | 109.4 | 5.9 | 246.5 | 4.4 | 918.7 | 855.3 | 873 | 843.1 | 915.6 | 773.8 | 772.6 | 766.2 | 785.3 | 806.8 | 318.7 | 345.3 | 234.7 | 362.4 | 357.3 | 305.6 | 325.3 | 415.7 | 306.9
1321 | 1131 | 566.7 | 226.68 | 264.9759 | 398.3 | 334.2 | 340.7 | 319.3 | 593.2 | 65.1 | 18.7 | 109.5 | 5.1 | 200.8 | 6.2 | 918.5 | 857 | 875.4 | 846.7 | 914.2 | 773.9 | 774.8 | 771 | 787.1 | 807.3 | 318.7 | 345.1 | 234.9 | 362.4 | 357.6 | 305.7 | 325.4 | 415.9 | 307.1
1322 | 1132 | 563 | 225.2 | 263.2458 | 399.3 | 334.4 | 340.9 | 318.9 | 613.7 | 65.2 | 18.7 | 109.6 | 5.1 | 212.7 | 9.3 | 918.4 | 857 | 876.2 | 846.1 | 912.9 | 774 | 774.8 | 775.3 | 787.4 | 807.7 | 318.8 | 345.1 | 235 | 362.4 | 357.8 | 305.8 | 325.6 | 416.1 | 307.3
1323 | 1133 | 188.7 | 75.48 | 88.2318 | 399.1 | 334.8 | 341.4 | 318.4 | 617.2 | 65.3 | 18.7 | 109.5 | 5.5 | 215.2 | 10.6 | 919.2 | 862.3 | 875 | 846.3 | 916.7 | 774 | 773.3 | 777.6 | 787.3 | 808.3 | 318.8 | 345.2 | 235.2 | 362.2 | 358 | 305.9 | 325.8 | 416.3 | 307.4
1324 | 1134 | -7 | 0 | 0 | 399.6 | 334.9 | 340.8 | 317.7 | 605.7 | 65.3 | 18.7 | 109.5 | 5 | 216.7 | 10.8 | 920.9 | 868.6 | 863.5 | 844.6 | 928.9 | 773.8 | 766.7 | 767.2 | 784.5 | 805.9 | 318.8 | 345.2 | 235.3 | 362.2 | 358.2 | 306 | 325.9 | 416.5 | 307.6
1325 | 1135 | -7 | 0 | 0 | 398.5 | 334.6 | 340.8 | 317.6 | 575.3 | 65.3 | 18.7 | 109.4 | 3.8 | 220.4 | 10.1 | 923.3 | 863.6 | 825.1 | 829.6 | 905.6 | 771.8 | 739.7 | 737.9 | 770.5 | 799.7 | 318.8 | 345 | 235.4 | 362.2 | 357.7 | 306.1 | 326 | 416.6 | 307.7
1326 | 1136 | -7 | 0 | 0 | 397.2 | 333.9 | 340 | 317.4 | 541.8 | 65.3 | 18.7 | 109.4 | 3.6 | 203.3 | 9.4 | 925.3 | 828.2 | 789.1 | 816.6 | 842.9 | 768.7 | 713.2 | 715 | 753.1 | 795 | 318.7 | 344 | 235.6 | 361.8 | 357 | 306.2 | 325.9 | 416.7 | 307.9
1327 | 1137 | -7 | 0 | 0 | 394.2 | 332.8 | 338.2 | 316.5 | 514.8 | 65.4 | 18.7 | 109.5 | 3.3 | 211.8 | 8.7 | 925.3 | 796.1 | 759 | 806.1 | 810.6 | 765.7 | 687.4 | 695.2 | 736.1 | 789.7 | 318.4 | 342.8 | 235.7 | 361 | 356.3 | 306.3 | 325.8 | 416.6 | 308
1328 | 1138 | -7 | 0 | 0 | 390.5 | 331.2 | 336.1 | 315 | 491.4 | 65.4 | 18.7 | 109.5 | 3.9 | 235.8 | 7.5 | 923.9 | 768.7 | 734.4 | 798.7 | 799.8 | 762.7 | 664.7 | 678.4 | 719.7 | 783.2 | 317.9 | 341.2 | 235.9 | 360 | 355.1 | 306.3 | 325.5 | 416.5 | 308.2
1329 | 1139 | -7 | 0 | 0 | 387.4 | 329.3 | 333.5 | 313.4 | 472.8 | 65.4 | 18.7 | 109.4 | 3.9 | 243 | 6.6 | 921.5 | 746.9 | 712.7 | 792.6 | 788.1 | 759.6 | 646.9 | 662.1 | 704.8 | 776.6 | 317.4 | 339.4 | 236 | 358.7 | 353 | 306.4 | 325.2 | 416.4 | 308.3
1330 | 1140 | -7 | 0 | 0 | 384.4 | 327.5 | 331.1 | 311.5 | 458 | 65.4 | 18.7 | 109.2 | 4.2 | 206 | 7.1 | 918 | 729.2 | 691.9 | 786.2 | 774.3 | 756.5 | 631.1 | 648 | 690.1 | 769.1 | 316.7 | 337.1 | 236.1 | 357.3 | 350.9 | 306.4 | 324.9 | 416.3 | 308.4
1331 | 1141 | -7 | 0 | 0 | 383.3 | 325.6 | 328.7 | 309.3 | 444.8 | 65.5 | 18.7 | 109.1 | 4.6 | 228.5 | 7.7 | 915.2 | 711.6 | 674.1 | 781.6 | 763.6 | 753.5 | 614.5 | 634.8 | 674.8 | 755.7 | 315.8 | 334.6 | 236.3 | 355.7 | 348.2 | 306.3 | 324.4 | 416.1 | 308.5
1332 | 1142 | -7 | 0 | 0 | 381.1 | 323.6 | 326.2 | 307.1 | 434.5 | 65.4 | 18.7 | 108.8 | 3.9 | 216.4 | 7.2 | 912.2 | 694.8 | 657.5 | 777 | 753.8 | 750.6 | 601 | 623.9 | 660.4 | 747.8 | 314.9 | 332.2 | 236.4 | 354.1 | 345.4 | 306.3 | 324 | 416 | 308.6
1333 | 1143 | -7 | 0 | 0 | 378.3 | 321.4 | 323.8 | 304.9 | 423.7 | 65.4 | 18.7 | 108.4 | 3.7 | 196.2 | 6.8 | 908.8 | 676.2 | 642.9 | 772 | 742.8 | 747.8 | 587.2 | 613.7 | 647.8 | 739.6 | 314 | 329.8 | 236.5 | 352.4 | 342.6 | 306.2 | 323.4 | 415.9 | 308.7
1334 | 1144 | -7 | 0 | 0 | 375.7 | 319.3 | 321.8 | 302.9 | 413.4 | 65.4 | 18.7 | 108 | 3.9 | 206.4 | 6.5 | 905.2 | 661.2 | 629.1 | 768.3 | 731.3 | 745.2 | 575.6 | 603.9 | 636.6 | 732.3 | 313 | 327.4 | 236.7 | 350.8 | 339.8 | 306.1 | 323 | 415.7 | 308.7
1335 | 1145 | -7 | 0 | 0 | 372.6 | 317.1 | 319.5 | 300.9 | 404.1 | 65.4 | 18.7 | 107.4 | 4 | 215.7 | 6.5 | 901.5 | 650.7 | 615.6 | 764.3 | 722.1 | 742.6 | 564.8 | 595.5 | 625 | 725.3 | 312.1 | 325 | 236.8 | 349.2 | 337.2 | 306 | 322.5 | 415.6 | 308.8
1336 | 1146 | -7 | 0 | 0 | 369.3 | 314.9 | 317.2 | 299.1 | 395.4 | 65.4 | 18.7 | 106.8 | 4 | 204 | 6.6 | 898.3 | 641.1 | 602.8 | 760.1 | 715.3 | 740 | 554.7 | 587.3 | 614.4 | 718.7 | 311.1 | 322.7 | 236.9 | 347.5 | 334.7 | 305.8 | 322 | 415.4 | 308.9
1337 | 1147 | -7 | 0 | 0 | 366.2 | 312.9 | 315.2 | 297.2 | 388.6 | 65.4 | 18.6 | 106.2 | 3.9 | 210.1 | 7.8 | 894.3 | 630.8 | 590.9 | 756.3 | 709.5 | 737.4 | 545.1 | 580 | 604.1 | 711.8 | 310.2 | 320.5 | 237.1 | 345.8 | 332.4 | 305.7 | 321.5 | 415.3 | 308.9
1338 | 1148 | -7 | 0 | 0 | 363.2 | 310.9 | 313.1 | 295.2 | 383 | 65.4 | 18.6 | 105.7 | 4.3 | 221.2 | 8.4 | 890 | 625.2 | 577.5 | 751.2 | 703.6 | 734.7 | 533.9 | 573 | 594.2 | 705.6 | 309.3 | 318.3 | 237.2 | 344.1 | 330.1 | 305.5 | 321 | 415.1 | 309
1339 | 1149 | -7 | 0 | 0 | 360.3 | 309.1 | 310.8 | 293.4 | 377.5 | 65.4 | 18.6 | 105.1 | 4.3 | 224.9 | 7.9 | 886 | 624.9 | 564.6 | 746.8 | 697 | 732.3 | 522.5 | 567.9 | 582.8 | 699.2 | 308.4 | 316.4 | 237.3 | 342.6 | 327.9 | 305.4 | 320.6 | 414.9 | 309
1340 | 1150 | -7 | 0 | 0 | 357.4 | 307.4 | 309 | 291.7 | 372.6 | 65.4 | 18.6 | 104.6 | 4.2 | 213.9 | 7.9 | 881.9 | 622.9 | 552.7 | 743.7 | 690.2 | 729.9 | 512.8 | 563.5 | 574.4 | 692.5 | 307.4 | 314.3 | 237.5 | 341 | 325.7 | 305.2 | 320 | 414.8 | 309.1
1341 | 1151 | -7 | 0 | 0 | 354.8 | 305.7 | 307.2 | 289.9 | 367.8 | 65.4 | 18.6 | 104.1 | 3.8 | 222.6 | 7.2 | 878.1 | 618.1 | 541.1 | 740.2 | 684.9 | 727.5 | 504.2 | 557.3 | 567.7 | 686.2 | 306.5 | 312.4 | 237.6 | 339.5 | 323.6 | 305 | 319.6 | 414.6 | 309.1
1342 | 1152 | -7 | 0 | 0 | 352.1 | 304.2 | 305.3 | 288.1 | 363.3 | 65.3 | 18.6 | 103.7 | 3.7 | 209.5 | 6.7 | 875.1 | 615.7 | 531 | 737 | 678.2 | 725.2 | 495.4 | 551.2 | 559.3 | 680.7 | 305.6 | 310.6 | 237.7 | 338 | 321.6 | 304.8 | 319.2 | 414.4 | 309.1
1343 | 1153 | -7 | 0 | 0 | 349.6 | 302.8 | 303.4 | 286.5 | 358.7 | 65.3 | 18.6 | 103.2 | 3.8 | 201.8 | 7.6 | 871.9 | 607.5 | 520.7 | 733.8 | 674.1 | 722.9 | 487.6 | 547.1 | 550.9 | 674.7 | 304.7 | 308.8 | 237.9 | 336.4 | 319.5 | 304.6 | 318.7 | 414.2 | 309.2
1344 | 1154 | -7 | 0 | 0 | 347 | 301.4 | 301.9 | 285.1 | 355.2 | 65.3 | 18.6 | 102.8 | 4.5 | 210.5 | 7.8 | 868.9 | 598.4 | 510.8 | 731 | 670.3 | 720.6 | 480.7 | 543.6 | 541.9 | 668.7 | 303.9 | 307 | 238 | 334.9 | 317.6 | 304.4 | 318.3 | 414 | 309.2
1345 | 1155 | -7 | 0 | 0 | 344.5 | 300.1 | 300.3 | 283.7 | 352.5 | 65.2 | 18.6 | 102.4 | 4.3 | 221.9 | 7.4 | 864.9 | 593 | 501.5 | 727.7 | 666.1 | 718.4 | 474 | 539.4 | 534.5 | 663.9 | 302.9 | 305.3 | 238.1 | 333.5 | 315.7 | 304.2 | 317.8 | 413.8 | 309.2
1346 | 1156 | -7 | 0 | 0 | 342.4 | 298.8 | 298.7 | 282.3 | 349.2 | 65.1 | 18.6 | 102.1 | 4.7 | 218.1 | 7.8 | 860.5 | 589.7 | 492.4 | 723.9 | 662.4 | 716.1 | 468.4 | 534.9 | 527.6 | 658.7 | 302 | 303.7 | 238.2 | 331.8 | 314 | 304 | 317.3 | 413.6 | 309.3
1347 | 1157 | -7 | 0 | 0 | 340.4 | 297.5 | 297.2 | 281 | 346.7 | 65 | 18.6 | 101.7 | 4.7 | 209.2 | 9.2 | 856.4 | 588.9 | 483.5 | 720 | 655.5 | 713.8 | 463.3 | 532 | 520.7 | 653.5 | 301 | 302 | 238.3 | 330 | 312.4 | 303.8 | 316.9 | 413.4 | 309.3
1348 | 1158 | -7 | 0 | 0 | 338.3 | 296.3 | 295.6 | 279.7 | 344.4 | 64.9 | 18.6 | 101.4 | 5.2 | 192.4 | 9.4 | 852.8 | 586.9 | 474.8 | 716.9 | 647.8 | 711.5 | 458.2 | 529.4 | 512.7 | 648.4 | 300.2 | 300.6 | 238.5 | 328.5 | 310.7 | 303.6 | 316.5 | 413.2 | 309.3
1349 | 1159 | -7 | 0 | 0 | 336.4 | 295.1 | 294.3 | 278.5 | 341.9 | 64.8 | 18.6 | 101 | 5.4 | 242.3 | 8.5 | 848.4 | 584.6 | 467.9 | 714.8 | 644.1 | 709.4 | 453.3 | 526.1 | 505.8 | 643.1 | 299.4 | 299.2 | 238.6 | 327.2 | 309.1 | 303.3 | 316 | 413 | 309.4
1350 | 1160 | -7 | 0 | 0 | 334.7 | 294 | 293.1 | 277.2 | 339.5 | 64.6 | 18.6 | 100.5 | 4.4 | 194.2 | 9 | 843 | 580.3 | 462.4 | 713.5 | 642.8 | 707.2 | 448.4 | 521.3 | 501.4 | 638 | 298.5 | 297.8 | 238.7 | 325.9 | 307.5 | 303.1 | 315.5 | 412.8 | 309.4
1351 | 1161 | -7 | 0 | 0 | 333.3 | 292.9 | 291.8 | 275.9 | 336.9 | 64.5 | 18.6 | 100.2 | 3.9 | 207 | 9.7 | 837.8 | 578.4 | 457.4 | 712.2 | 639.5 | 704.9 | 444.1 | 515.9 | 499.4 | 634.2 | 297.6 | 296.4 | 238.8 | 324.7 | 305.9 | 302.9 | 315.1 | 412.6 | 309.4
1352 | 1162 | -7 | 0 | 0 | 331.6 | 291.9 | 290.6 | 274.8 | 334.3 | 64.4 | 18.6 | 99.8 | 3.6 | 238.1 | 8.3 | 833.1 | 577.3 | 452.6 | 710 | 636.6 | 702.9 | 439.6 | 510.5 | 496.4 | 629.7 | 296.8 | 295 | 238.9 | 323.7 | 304.3 | 302.7 | 314.6 | 412.3 | 309.4
1353 | 1163 | -6.9 | 0 | 0 | 330.1 | 290.8 | 289.4 | 273.7 | 331.5 | 64.3 | 18.6 | 99.4 | 3.5 | 255 | 8.1 | 828.3 | 574.6 | 447.3 | 708.2 | 634.2 | 700.9 | 435.7 | 505.9 | 492.7 | 625.8 | 296 | 293.7 | 239.1 | 322.7 | 302.9 | 302.4 | 314.2 | 412.1 | 309.4
1354 | 1164 | -6.9 | 0 | 0 | 328.7 | 289.9 | 288.4 | 272.6 | 329.5 | 64.2 | 18.6 | 99.1 | 3.5 | 221.6 | 7.8 | 823.7 | 570 | 442.1 | 706.4 | 632.1 | 698.9 | 433.2 | 501.3 | 489.9 | 621.3 | 295.3 | 292.5 | 239.2 | 321.8 | 301.6 | 302.2 | 313.8 | 411.9 | 309.4
1355 | 1165 | -6.9 | 0 | 0 | 327.3 | 288.9 | 287.1 | 271.6 | 327.1 | 64.1 | 18.6 | 98.8 | 3.9 | 234.5 | 8.6 | 819.4 | 568.6 | 436.2 | 704.3 | 629.2 | 696.9 | 429.8 | 497.4 | 487 | 617 | 294.5 | 291.2 | 239.3 | 320.9 | 300.3 | 302 | 313.3 | 411.7 | 309.5
1356 | 1166 | -6.9 | 0 | 0 | 326 | 288 | 286 | 270.8 | 324.8 | 64.1 | 18.6 | 98.5 | 3.7 | 240 | 8.7 | 815.2 | 566.5 | 430.7 | 702.5 | 626.9 | 694.9 | 426.3 | 493.8 | 482.6 | 612.6 | 293.7 | 290.1 | 239.4 | 320 | 299.1 | 301.8 | 312.9 | 411.5 | 309.5
1357 | 1167 | -7 | 0 | 0 | 324.6 | 287 | 284.8 | 270 | 323 | 64 | 18.6 | 98.2 | 4.5 | 232.1 | 9.4 | 811.1 | 563.2 | 426.2 | 700.8 | 623.7 | 692.8 | 421.6 | 490.9 | 476 | 608.5 | 293 | 289 | 239.5 | 318.8 | 297.9 | 301.5 | 312.5 | 411.3 | 309.5
1358 | 1168 | -6.9 | 0 | 0 | 323.3 | 286.2 | 283.9 | 269.2 | 321.3 | 63.9 | 18.6 | 97.8 | 4 | 207.2 | 8.1 | 807.3 | 561.6 | 421.3 | 698.8 | 619.6 | 690.8 | 417.8 | 487.4 | 470.3 | 604.4 | 292.2 | 287.7 | 239.6 | 317.5 | 296.7 | 301.3 | 312.1 | 411 | 309.5
1359 | 1169 | -6.9 | 0 | 0 | 322.2 | 285.3 | 283 | 268.2 | 319.9 | 63.8 | 18.6 | 97.4 | 4.2 | 223.9 | 7.6 | 803.4 | 559.9 | 416.3 | 696.3 | 617.2 | 688.8 | 413.3 | 484.4 | 464.9 | 599.6 | 291.5 | 286.6 | 239.7 | 316.4 | 295.6 | 301.1 | 311.7 | 410.8 | 309.5
1360 | 1170 | -6.9 | 0 | 0 | 320.9 | 284.5 | 282 | 267.2 | 318.7 | 63.7 | 18.6 | 97.1 | 4.9 | 253 | 7.9 | 799.8 | 559 | 411.7 | 693.4 | 615.6 | 686.7 | 410.9 | 480.3 | 462.9 | 595.4 | 290.8 | 285.5 | 239.8 | 315.6 | 294.5 | 300.9 | 311.3 | 410.6 | 309.5
1361 | 1171 | -6.9 | 0 | 0 | 319.6 | 283.7 | 281.1 | 266.3 | 317 | 63.5 | 18.6 | 96.8 | 5.2 | 231.4 | 8.5 | 796.1 | 556.6 | 407 | 690.8 | 613 | 684.6 | 407.6 | 476.6 | 459.5 | 592.1 | 290.1 | 284.5 | 239.9 | 314.8 | 293.4 | 300.7 | 310.9 | 410.3 | 309.5
1362 | 1172 | -6.9 | 0 | 0 | 318.5 | 283 | 280.1 | 265.4 | 315.3 | 63.4 | 18.6 | 96.5 | 5.4 | 240.7 | 8.5 | 792.6 | 555 | 402.2 | 688.6 | 610.1 | 682.7 | 404.7 | 473.6 | 456.2 | 588.2 | 289.4 | 283.6 | 240 | 314 | 292.3 | 300.5 | 310.5 | 410.1 | 309.5
1363 | 1173 | -6.9 | 0 | 0 | 317.3 | 282.3 | 279.2 | 264.5 | 313.5 | 63.2 | 18.6 | 96.1 | 5 | 225 | 8.8 | 789.2 | 552.1 | 397.8 | 686.1 | 608 | 680.6 | 401.1 | 471.8 | 452.4 | 584.8 | 288.7 | 282.7 | 240.1 | 313.1 | 291.1 | 300.2 | 310.1 | 409.9 | 309.5
1364 | 1174 | -6.9 | 0 | 0 | 316.3 | 281.6 | 278.3 | 263.7 | 311.9 | 63 | 18.6 | 95.8 | 4.9 | 245.2 | 8.1 | 786 | 549.5 | 393 | 683.4 | 604.7 | 678.5 | 397.6 | 470.5 | 447.8 | 581 | 288 | 281.8 | 240.2 | 312.1 | 290.1 | 300 | 309.7 | 409.6 | 309.5
1365 | 1175 | -6.9 | 0 | 0 | 315.3 | 280.9 | 277.4 | 263 | 310.4 | 62.8 | 18.6 | 95.5 | 4.6 | 245.9 | 8.4 | 782.7 | 546 | 388.5 | 680.3 | 602.2 | 676.5 | 394.1 | 468.7 | 444.2 | 576.9 | 287.3 | 281.1 | 240.3 | 311.4 | 289.1 | 299.8 | 309.3 | 409.4 | 309.5
1366 | 1176 | -6.9 | 0 | 0 | 314.2 | 280.2 | 276.7 | 262.2 | 309 | 62.6 | 18.6 | 95.3 | 4.6 | 214.9 | 8.3 | 779.5 | 541.8 | 384.7 | 677.1 | 599.9 | 674.6 | 391.7 | 465.1 | 440.6 | 573.8 | 286.7 | 280.1 | 240.4 | 310.8 | 288.2 | 299.6 | 308.9 | 409.2 | 309.4
1367 | 1177 | -6.9 | 0 | 0 | 313.2 | 279.5 | 275.8 | 261.4 | 308.2 | 62.4 | 18.6 | 95 | 4.5 | 262.4 | 8.4 | 776.4 | 538.7 | 381.1 | 674.1 | 598.2 | 672.8 | 389.2 | 461.1 | 437.2 | 570.9 | 286.1 | 279.3 | 240.5 | 310.2 | 287.3 | 299.3 | 308.6 | 408.9 | 309.4
1368 | 1178 | -6.9 | 0 | 0 | 312.2 | 278.9 | 274.8 | 260.6 | 307.2 | 62.3 | 18.6 | 94.7 | 4.3 | 237.7 | 8.9 | 773.3 | 533.6 | 376.6 | 671 | 596.1 | 671 | 386.9 | 457.4 | 435.4 | 567.6 | 285.5 | 278.5 | 240.6 | 309.3 | 286.3 | 299.1 | 308.1 | 408.7 | 309.4
1369 | 1179 | -6.9 | 0 | 0 | 311.2 | 278.3 | 273.9 | 259.9 | 306.2 | 62.1 | 18.6 | 94.4 | 5.3 | 234.7 | 8.7 | 770.4 | 527.1 | 371.9 | 667.6 | 594.9 | 669.2 | 385.3 | 453.6 | 434.4 | 564.7 | 284.8 | 277.7 | 240.7 | 308.2 | 285.4 | 298.9 | 307.7 | 408.4 | 309.4
1370 | 1180 | -6.9 | 0 | 0 | 310.4 | 277.7 | 273.2 | 259.3 | 304.7 | 62 | 18.6 | 94.1 | 5.1 | 212.1 | 8 | 767.5 | 524.2 | 367.5 | 665.1 | 594 | 667.3 | 383.5 | 450.4 | 433.5 | 561.4 | 284.2 | 276.8 | 240.7 | 307.3 | 284.6 | 298.6 | 307.3 | 408.2 | 309.4
1371 | 1181 | -6.9 | 0 | 0 | 309.6 | 277.1 | 272.7 | 258.6 | 303.5 | 61.9 | 18.6 | 93.8 | 4.6 | 197.4 | 6.4 | 764.6 | 519.1 | 363.1 | 662.7 | 591.8 | 665.5 | 381.9 | 447.6 | 431.9 | 558.4 | 283.5 | 276 | 240.8 | 306.7 | 283.8 | 298.4 | 306.9 | 407.9 | 309.4
1372 | 1182 | -6.9 | 0 | 0 | 308.7 | 276.5 | 271.8 | 258 | 302.4 | 61.7 | 18.6 | 93.5 | 3.9 | 202.6 | 5.8 | 761.5 | 508.1 | 359.1 | 659.9 | 590.9 | 663.7 | 381.2 | 445.5 | 431.1 | 555.4 | 282.9 | 275.1 | 240.9 | 306.1 | 283 | 298.2 | 306.6 | 407.7 | 309.4
1373 | 1183 | -6.9 | 0 | 0 | 307.8 | 275.9 | 271.2 | 257.4 | 301.4 | 61.6 | 18.6 | 93.3 | 3.9 | 225.8 | 7.5 | 758.7 | 501.9 | 354.7 | 656.6 | 589 | 662 | 380.7 | 443.8 | 430.8 | 553.1 | 282.3 | 274.3 | 241 | 305.5 | 282.2 | 297.9 | 306.2 | 407.4 | 309.3
1374 | 1184 | -6.9 | 0 | 0 | 307 | 275.3 | 270.5 | 256.7 | 300.7 | 61.5 | 18.6 | 93.1 | 4 | 245.1 | 7.2 | 756.1 | 504.3 | 350 | 654 | 587.1 | 660.2 | 379.1 | 442.5 | 430 | 550.4 | 281.7 | 273.6 | 241.1 | 304.8 | 281.4 | 297.7 | 305.8 | 407.2 | 309.3
1375 | 1185 | -6.9 | 0 | 0 | 306.2 | 274.7 | 269.9 | 256 | 299.9 | 61.4 | 18.7 | 92.8 | 4 | 235.7 | 7.1 | 753.3 | 504.7 | 345.1 | 651.1 | 584.6 | 658.1 | 376.8 | 440.7 | 427.5 | 547.6 | 281.2 | 272.8 | 241.2 | 304.2 | 280.7 | 297.5 | 305.5 | 407 | 309.3
1376 | 1186 | -6.9 | 0 | 0 | 305.3 | 274.1 | 269 | 255.3 | 298.8 | 61.3 | 18.7 | 92.6 | 4.8 | 236.4 | 8.4 | 750.7 | 506.8 | 340.6 | 648.6 | 579.4 | 656.2 | 374.1 | 437.5 | 422.5 | 544.4 | 280.6 | 272 | 241.3 | 303.7 | 280 | 297.3 | 305 | 406.7 | 309.3
1377 | 1187 | -6.9 | 0 | 0 | 304.6 | 273.5 | 268.2 | 254.6 | 297.6 | 61.2 | 18.6 | 92.4 | 5 | 230.6 | 7.5 | 748.2 | 506.8 | 336.2 | 645.5 | 575 | 654.2 | 371.7 | 435.1 | 417.4 | 540.5 | 280 | 271.3 | 241.4 | 303.2 | 279.3 | 297.1 | 304.7 | 406.4 | 309.3
1378 | 1188 | -6.9 | 0 | 0 | 303.9 | 272.9 | 267.5 | 254 | 296.5 | 61 | 18.7 | 92.1 | 4.6 | 249.3 | 6.6 | 745.8 | 506.3 | 331.8 | 642.4 | 568.4 | 652.3 | 368.4 | 432.5 | 412.4 | 537.2 | 279.4 | 270.5 | 241.5 | 302.6 | 278.4 | 296.9 | 304.3 | 406.2 | 309.2
1379 | 1189 | -6.9 | 0 | 0 | 303.1 | 272.4 | 267 | 253.4 | 295.5 | 60.8 | 18.7 | 91.9 | 4.2 | 232.9 | 6 | 743.6 | 504.7 | 327.6 | 639.2 | 562.4 | 650.5 | 364.7 | 430.5 | 408 | 534.6 | 278.8 | 269.7 | 241.6 | 302 | 277.7 | 296.7 | 303.9 | 405.9 | 309.2
1380 | 1190 | -6.9 | 0 | 0 | 302.4 | 271.8 | 266.4 | 252.8 | 294.6 | 60.6 | 18.6 | 91.7 | 4.3 | 247.5 | 6.8 | 741.2 | 501.6 | 323.1 | 636.9 | 560.7 | 648.5 | 361.7 | 429.1 | 404.6 | 531.6 | 278.3 | 269 | 241.7 | 301.5 | 277 | 296.4 | 303.5 | 405.7 | 309.2
1381 | 1191 | -6.9 | 0 | 0 | 301.8 | 271.3 | 265.8 | 252.2 | 293.3 | 60.4 | 18.7 | 91.4 | 4.2 | 248.2 | 8.2 | 738.8 | 500.4 | 318.9 | 634.7 | 561.1 | 646.5 | 358.3 | 428.2 | 401 | 528.9 | 277.8 | 268.4 | 241.8 | 300.8 | 276.3 | 296.2 | 303.1 | 405.5 | 309.1
1382 | 1192 | -6.9 | 0 | 0 | 301.3 | 270.8 | 265.4 | 251.6 | 292.2 | 60.3 | 18.7 | 91.1 | 3.8 | 248.2 | 9.3 | 736.2 | 499.7 | 315.3 | 633.3 | 562 | 644.7 | 354.7 | 426.9 | 396.8 | 525.6 | 277.2 | 267.8 | 241.9 | 300.2 | 275.7 | 296 | 302.8 | 405.2 | 309.1
1383 | 1193 | -6.9 | 0 | 0 | 300.7 | 270.4 | 264.8 | 251 | 291.2 | 60.2 | 18.7 | 90.9 | 4.1 | 239.4 | 10.2 | 733.6 | 497.5 | 312.1 | 631.1 | 562.2 | 642.9 | 352.1 | 424.7 | 393.8 | 522.6 | 276.7 | 267.2 | 241.9 | 299.2 | 275.2 | 295.8 | 302.4 | 404.9 | 309.1
1384 | 1194 | -6.9 | 0 | 0 | 300.1 | 270 | 264.1 | 250.5 | 290.4 | 60.1 | 18.7 | 90.7 | 4.2 | 239.2 | 10.6 | 731.2 | 495.3 | 308.8 | 629.5 | 561.8 | 641.3 | 349.9 | 422.4 | 391.9 | 520.3 | 276.2 | 266.5 | 242 | 298.4 | 274.6 | 295.6 | 302.1 | 404.7 | 309.1
1385 | 1195 | -6.9 | 0 | 0 | 299.6 | 269.5 | 263.3 | 249.8 | 289.5 | 60 | 18.7 | 90.5 | 4.1 | 232.8 | 10 | 728.7 | 494.1 | 305.3 | 627.1 | 560.2 | 639.5 | 347.3 | 420.8 | 389.4 | 517.4 | 275.7 | 265.9 | 242.1 | 298.1 | 273.9 | 295.4 | 301.7 | 404.4 | 309
1386 | 1196 | -6.9 | 0 | 0 | 298.9 | 269 | 262.6 | 249.4 | 288.6 | 59.9 | 18.7 | 90.3 | 4.3 | 239.7 | 9.5 | 726.2 | 492 | 302.3 | 625.5 | 560.1 | 637.7 | 344.6 | 419.4 | 386.2 | 514.6 | 275.3 | 265.3 | 242.2 | 297.7 | 273.2 | 295.2 | 301.3 | 404.2 | 309
1387 | 1197 | -6.9 | 0 | 0 | 298.3 | 268.6 | 261.9 | 248.9 | 287.8 | 59.8 | 18.7 | 90.1 | 4.7 | 243 | 9.4 | 723.7 | 491.9 | 299.3 | 623.5 | 560 | 636 | 342.1 | 417.5 | 382.8 | 512 | 274.8 | 264.6 | 242.3 | 297.2 | 272.5 | 294.9 | 300.9 | 403.9 | 309
1388 | 1198 | -6.9 | 0 | 0 | 297.7 | 268.1 | 261.2 | 248.3 | 287.2 | 59.7 | 18.6 | 89.8 | 5 | 235 | 8.9 | 721.4 | 491.6 | 295.6 | 621.5 | 559.2 | 634.2 | 340.4 | 415.8 | 379.8 | 509.2 | 274.3 | 264 | 242.4 | 296.7 | 271.7 | 294.7 | 300.6 | 403.7 | 308.9
1389 | 1199 | -6.9 | 0 | 0 | 297.2 | 267.7 | 260.4 | 247.8 | 286.3 | 59.5 | 18.6 | 89.6 | 4.9 | 235.6 | 8.2 | 718.8 | 489.7 | 292.5 | 619.7 | 558.7 | 632.4 | 338.6 | 414.1 | 377.6 | 506.6 | 273.8 | 263.4 | 242.5 | 296.2 | 271.1 | 294.5 | 300.2 | 403.4 | 308.9
1390 | 1200 | -6.9 | 0 | 0 | 296.6 | 267.2 | 259.8 | 247.3 | 285.4 | 59.4 | 18.7 | 89.4 | 4.7 | 237.9 | 7.8 | 716.4 | 486.3 | 289.2 | 616.4 | 557.2 | 630.8 | 336.6 | 411.8 | 376 | 504.4 | 273.2 | 262.7 | 242.6 | 295.7 | 270.4 | 294.3 | 299.8 | 403.2 | 308.8
1391 | 1201 | -6.9 | 0 | 0 | 296.1 | 266.7 | 259.4 | 246.9 | 284.5 | 59.4 | 18.7 | 89.2 | 4 | 244.4 | 8.1 | 714 | 485.6 | 286.1 | 613.5 | 556.5 | 629.2 | 335.7 | 409 | 375.1 | 502.7 | 272.7 | 262 | 242.6 | 295.1 | 269.9 | 294.1 | 299.4 | 402.9 | 308.8
1392 | 1202 | -6.9 | 0 | 0 | 295.5 | 266.3 | 258.9 | 246.4 | 283.8 | 59.3 | 18.7 | 89 | 4 | 221.7 | 7.7 | 711.8 | 485 | 282.4 | 609.2 | 557.6 | 627.7 | 333.5 | 407.2 | 372.1 | 500.4 | 272.2 | 261.4 | 242.7 | 294.7 | 269.3 | 293.9 | 299 | 402.6 | 308.8
1393 | 1203 | -6.9 | 0 | 0 | 294.9 | 265.8 | 258.2 | 245.9 | 283.1 | 59.2 | 18.7 | 88.8 | 4.7 | 256.9 | 7.8 | 710 | 480.9 | 279.3 | 605.1 | 558.7 | 626.2 | 331.6 | 405 | 369.4 | 497.9 | 271.7 | 260.8 | 242.8 | 294.1 | 268.7 | 293.7 | 298.7 | 402.4 | 308.7
1394 | 1204 | -6.9 | 0 | 0 | 294.4 | 265.3 | 257.6 | 245.5 | 282.1 | 59.1 | 18.7 | 88.5 | 4.4 | 227.9 | 9.5 | 708 | 478.7 | 276.8 | 603.3 | 559.1 | 624.7 | 329.1 | 402.4 | 367.3 | 495.8 | 271.2 | 260.3 | 242.9 | 293.5 | 268.1 | 293.5 | 298.3 | 402.1 | 308.7
1395 | 1205 | -6.9 | 0 | 0 | 293.8 | 264.8 | 257.1 | 245 | 281.1 | 58.9 | 18.7 | 88.3 | 3.9 | 240.6 | 10 | 705.8 | 473.5 | 273.8 | 600.8 | 559.8 | 623.1 | 326.6 | 400.7 | 365.1 | 493.6 | 270.7 | 259.8 | 243 | 293 | 267.5 | 293.3 | 298 | 401.9 | 308.6
1396 | 1206 | -6.9 | 0 | 0 | 293.4 | 264.3 | 256.4 | 244.4 | 280.1 | 58.7 | 18.7 | 88.1 | 4.1 | 242.9 | 10.3 | 703.8 | 471.2 | 270.7 | 597.6 | 560 | 621.5 | 325 | 399 | 363.1 | 491.4 | 270.2 | 259.1 | 243.1 | 292.5 | 266.9 | 293.1 | 297.5 | 401.6 | 308.6
1397 | 1207 | -6.9 | 0 | 0 | 292.9 | 263.9 | 255.7 | 243.7 | 278.9 | 58.4 | 18.7 | 87.9 | 3.9 | 248.9 | 10.2 | 701.8 | 470.9 | 268 | 594.5 | 560.3 | 620 | 322.9 | 396.5 | 361.4 | 488.7 | 269.7 | 258.5 | 243.2 | 291.9 | 266.5 | 292.8 | 297.2 | 401.3 | 308.5
1398 | 1208 | -6.9 | 0 | 0 | 292.3 | 263.5 | 255.2 | 243.1 | 278.2 | 58.2 | 18.7 | 87.7 | 4.2 | 234.4 | 9.5 | 699.9 | 470.9 | 265.1 | 591.4 | 560.9 | 618.5 | 321.1 | 394.1 | 359.2 | 486.4 | 269.2 | 258 | 243.3 | 291.4 | 266 | 292.6 | 296.8 | 401.1 | 308.5
1399 | 1209 | -6.9 | 0 | 0 | 291.7 | 263.1 | 254.8 | 242.5 | 277.8 | 58.1 | 18.7 | 87.5 | 4.3 | 231.1 | 8.2 | 698 | 469.6 | 262.3 | 588.2 | 561.5 | 617 | 319.5 | 392.4 | 357.1 | 484 | 268.8 | 257.5 | 243.3 | 290.7 | 265.5 | 292.4 | 296.5 | 400.8 | 308.4
1400 | 1210 | -6.9 | 0 | 0 | 291.2 | 262.7 | 254.4 | 242 | 276.8 | 58 | 18.7 | 87.3 | 4.1 | 229.7 | 7.7 | 696.1 | 469.2 | 259.3 | 586 | 562.2 | 615.4 | 318.3 | 390.3 | 354.8 | 481.5 | 268.4 | 257 | 243.4 | 290.4 | 265 | 292.2 | 296.2 | 400.5 | 308.4
1401 | 1211 | -6.9 | 0 | 0 | 290.8 | 262.3 | 253.9 | 241.6 | 275.7 | 57.9 | 18.7 | 87 | 3.6 | 241 | 8.4 | 694.2 | 468.7 | 257.1 | 583.7 | 563.2 | 613.7 | 317.4 | 389.4 | 353.2 | 479.6 | 267.9 | 256.6 | 243.5 | 290 | 264.5 | 292 | 295.8 | 400.3 | 308.3
1402 | 1212 | -6.9 | 0 | 0 | 290.3 | 261.9 | 253.4 | 241.1 | 274.9 | 57.8 | 18.7 | 86.8 | 4 | 241.6 | 9.1 | 692.2 | 465.3 | 254.2 | 579.9 | 563.8 | 611.8 | 318 | 387 | 352.7 | 477.9 | 267.5 | 256.1 | 243.6 | 289.6 | 263.9 | 291.8 | 295.5 | 400 | 308.3
1403 | 1213 | -6.9 | 0 | 0 | 289.7 | 261.6 | 252.8 | 240.5 | 274.3 | 57.7 | 18.7 | 86.6 | 3.8 | 237.5 | 8.8 | 690.5 | 464.1 | 251.4 | 577.8 | 564.1 | 609.9 | 318.1 | 384.9 | 352.3 | 476 | 267 | 255.5 | 243.7 | 288.9 | 263.3 | 291.6 | 295.2 | 399.7 | 308.2
1404 | 1214 | -6.9 | 0 | 0 | 289.1 | 261.2 | 252.2 | 240.1 | 273.8 | 57.6 | 18.7 | 86.5 | 4 | 248.7 | 8.3 | 688.5 | 462.2 | 249.3 | 577.7 | 564 | 608.1 | 316.7 | 383.5 | 351.3 | 474 | 266.6 | 255 | 243.8 | 288.3 | 262.9 | 291.4 | 294.8 | 399.5 | 308.2
1405 | 1215 | -6.9 | 0 | 0 | 288.7 | 260.8 | 251.6 | 239.6 | 273.6 | 57.5 | 18.7 | 86.3 | 4 | 241.6 | 9 | 686.4 | 458.3 | 247.4 | 576.9 | 564.4 | 606.4 | 317.7 | 381.5 | 351.9 | 472.5 | 266.2 | 254.5 | 243.8 | 288 | 262.3 | 291.2 | 294.5 | 399.2 | 308.2
1406 | 1216 | -6.9 | 0 | 0 | 288.3 | 260.5 | 251.1 | 239.2 | 273.4 | 57.4 | 18.7 | 86.1 | 4.6 | 237 | 9.2 | 684.3 | 459.5 | 245.5 | 576.3 | 566.1 | 604.8 | 316.1 | 380.6 | 350.5 | 470.6 | 265.8 | 254 | 243.9 | 287.5 | 261.8 | 291 | 294.1 | 399 | 308.1
1407 | 1217 | -6.9 | 0 | 0 | 287.7 | 260.1 | 250.7 | 238.7 | 273.2 | 57.3 | 18.7 | 86 | 4.5 | 244.5 | 9.6 | 682.3 | 456.2 | 243.2 | 575.3 | 566.8 | 603.2 | 315.4 | 378.9 | 348.9 | 468.3 | 265.3 | 253.5 | 244 | 287.2 | 261.2 | 290.8 | 293.7 | 398.7 | 308.1
1408 | 1218 | -6.9 | 0 | 0 | 287.1 | 259.8 | 250.1 | 238.2 | 272.7 | 57.2 | 18.7 | 85.8 | 4.5 | 246.9 | 10 | 680.3 | 452.2 | 241.1 | 573.9 | 565.6 | 601.7 | 314.8 | 376.4 | 348.3 | 466.6 | 265 | 253 | 244.1 | 286.8 | 260.6 | 290.6 | 293.4 | 398.4 | 308
1409 | 1219 | -6.9 | 0 | 0 | 286.6 | 259.5 | 249.4 | 237.8 | 272.3 | 57.2 | 18.7 | 85.6 | 4.1 | 233.6 | 9.8 | 678.4 | 450.4 | 238.8 | 572.3 | 566.5 | 600.3 | 314.5 | 374.2 | 348.1 | 464.8 | 264.6 | 252.6 | 244.1 | 286.6 | 260.3 | 290.4 | 293 | 398.1 | 308
1410 | 1220 | -6.9 | 0 | 0 | 286.2 | 259.2 | 248.7 | 237.3 | 271.7 | 57.1 | 18.7 | 85.5 | 3.7 | 242.5 | 9 | 676.8 | 447.8 | 236.6 | 570.8 | 567.2 | 598.6 | 312.9 | 372.8 | 346.1 | 463.3 | 264.2 | 252.1 | 244.2 | 286.2 | 259.7 | 290.2 | 292.8 | 397.9 | 307.9
1411 | 1221 | -6.9 | 0 | 0 | 285.6 | 258.9 | 248.3 | 236.7 | 271.3 | 57 | 18.7 | 85.3 | 4.3 | 241.4 | 8.8 | 674.8 | 447.1 | 234.4 | 569.7 | 567.9 | 597 | 310.9 | 371.2 | 343.6 | 461 | 263.8 | 251.5 | 244.3 | 285.9 | 259.2 | 290 | 292.4 | 397.6 | 307.8
1412 | 1222 | -6.9 | 0 | 0 | 285 | 258.6 | 247.8 | 236.1 | 271.2 | 56.9 | 18.7 | 85.2 | 4.2 | 257.2 | 8.5 | 672.6 | 444.6 | 232.5 | 568.6 | 567.5 | 595.3 | 308.6 | 369.3 | 341.6 | 459.2 | 263.4 | 251.1 | 244.3 | 285.5 | 258.8 | 289.8 | 292 | 397.4 | 307.8
1413 | 1223 | -6.9 | 0 | 0 | 284.4 | 258.3 | 247.3 | 235.5 | 270.6 | 56.8 | 18.7 | 85 | 4.5 | 250.7 | 7.9 | 670.3 | 442.6 | 230.5 | 567.1 | 568.1 | 593.5 | 308.9 | 367.3 | 341.9 | 457.4 | 263.1 | 250.7 | 244.4 | 285.1 | 258.5 | 289.6 | 291.6 | 397.1 | 307.7
1414 | 1224 | -6.9 | 0 | 0 | 284.1 | 257.9 | 246.8 | 234.9 | 269.9 | 56.7 | 18.7 | 84.9 | 4.1 | 246.2 | 7.2 | 668 | 437.2 | 228 | 564.8 | 569.8 | 591.8 | 308.1 | 365.8 | 341.3 | 455.9 | 262.8 | 250.3 | 244.5 | 284.7 | 258.1 | 289.4 | 291.3 | 396.8 | 307.6
1415 | 1225 | -6.9 | 0 | 0 | 283.7 | 257.6 | 246.2 | 234.4 | 269.7 | 56.6 | 18.7 | 84.8 | 4.3 | 239.3 | 7 | 665.7 | 429.2 | 225.5 | 562.3 | 569.9 | 590.2 | 307.9 | 363.7 | 341.4 | 454.4 | 262.4 | 249.9 | 244.5 | 284.4 | 257.7 | 289.2 | 291 | 396.5 | 307.6
1416 | 1226 | -6.9 | 0 | 0 | 283.3 | 257.2 | 245.6 | 234 | 269.8 | 56.5 | 18.7 | 84.6 | 4.7 | 240.7 | 6.7 | 663.7 | 426.7 | 223.2 | 560.1 | 569.8 | 588.9 | 308.1 | 362 | 341.9 | 452.9 | 262.1 | 249.6 | 244.6 | 283.9 | 257.3 | 289 | 290.6 | 396.3 | 307.5
1417 | 1227 | -6.9 | 0 | 0 | 282.9 | 256.8 | 245.1 | 233.6 | 269.4 | 56.4 | 18.7 | 84.5 | 4.6 | 249.6 | 6.2 | 661.8 | 428.9 | 220.9 | 558.2 | 571 | 587.1 | 307.9 | 361.2 | 340.9 | 451.3 | 261.7 | 249.1 | 244.7 | 283.5 | 256.8 | 288.8 | 290.3 | 396 | 307.5
1418 | 1228 | -6.9 | 0 | 0 | 282.4 | 256.4 | 244.6 | 233.2 | 268.9 | 56.3 | 18.7 | 84.3 | 4.3 | 253.6 | 6.5 | 659.8 | 428.2 | 218.9 | 556.3 | 572.9 | 585.4 | 306.8 | 359.6 | 339.3 | 449.6 | 261.3 | 248.7 | 244.8 | 283.1 | 256.4 | 288.6 | 289.9 | 395.7 | 307.4
1419 | 1229 | -6.9 | 0 | 0 | 282 | 256.1 | 244.2 | 232.8 | 268.6 | 56.2 | 18.7 | 84.1 | 3.8 | 245.6 | 6.1 | 657.9 | 425.4 | 217.1 | 554.7 | 573.9 | 583.9 | 306.4 | 357.5 | 338.8 | 447.9 | 261 | 248.2 | 244.8 | 282.7 | 255.9 | 288.4 | 289.6 | 395.5 | 307.4
1420 | 1230 | -6.9 | 0 | 0 | 281.6 | 255.7 | 243.8 | 232.3 | 268.1 | 56.1 | 18.7 | 84 | 3.4 | 225.1 | 6.3 | 655.9 | 422.9 | 215.1 | 553.1 | 574.9 | 582.5 | 305.8 | 355.2 | 337.8 | 446.2 | 260.6 | 247.8 | 244.9 | 282.3 | 255.4 | 288.2 | 289.2 | 395.2 | 307.3
1421 | 1231 | -6.9 | 0 | 0 | 281.3 | 255.4 | 243.4 | 232 | 267.3 | 56 | 18.7 | 83.8 | 3.3 | 243.6 | 6.7 | 653.8 | 419.8 | 212.8 | 551.5 | 576.1 | 581.3 | 305.4 | 353.3 | 337.6 | 445.1 | 260.2 | 247.4 | 245 | 282 | 255 | 288.1 | 288.8 | 394.9 | 307.2
1422 | 1232 | -6.9 | 0 | 0 | 280.9 | 255 | 242.9 | 231.8 | 266.5 | 55.9 | 18.7 | 83.7 | 3.5 | 240 | 6.4 | 651.8 | 418 | 210.7 | 549.7 | 576.9 | 580.1 | 305.6 | 351.2 | 337.2 | 444 | 259.8 | 247 | 245 | 281.6 | 254.6 | 287.9 | 288.5 | 394.6 | 307.1
1423 | 1233 | -6.9 | 0 | 0 | 280.4 | 254.7 | 242.4 | 231.5 | 266 | 55.9 | 18.7 | 83.6 | 3.3 | 235 | 5.9 | 649.8 | 418.8 | 208.6 | 547.7 | 577.6 | 578.7 | 305.7 | 349.4 | 336.7 | 442.7 | 259.4 | 246.6 | 245.1 | 281.1 | 254.1 | 287.7 | 288.2 | 394.4 | 307.1
1424 | 1234 | -6.9 | 0 | 0 | 279.9 | 254.3 | 242.1 | 231.1 | 265.4 | 55.8 | 18.7 | 83.4 | 3.3 | 224.8 | 5.7 | 647.9 | 416.9 | 206.4 | 545.4 | 578.9 | 576.9 | 305.3 | 347.9 | 335.1 | 440.9 | 259 | 246.1 | 245.2 | 280.5 | 253.7 | 287.5 | 287.8 | 394.1 | 307
1425 | 1235 | -6.9 | 0 | 0 | 279.5 | 254 | 241.8 | 230.7 | 265 | 55.8 | 18.8 | 83.3 | 3.6 | 208.8 | 5.6 | 645.8 | 414.1 | 204.1 | 542.7 | 579.6 | 575.1 | 303.8 | 346.6 | 333 | 439 | 258.7 | 245.7 | 245.2 | 280 | 253.2 | 287.3 | 287.5 | 393.9 | 306.9
1426 | 1236 | -6.9 | 0 | 0 | 279 | 253.7 | 241.3 | 230.3 | 265.1 | 55.8 | 18.8 | 83.1 | 4 | 205 | 6 | 643.8 | 414.4 | 202.1 | 539.5 | 581.1 | 573.3 | 301.9 | 345.3 | 330.6 | 437.3 | 258.4 | 245.3 | 245.3 | 279.6 | 252.6 | 287.1 | 287.3 | 393.6 | 306.9
1427 | 1237 | -6.9 | 0 | 0 | 278.5 | 253.4 | 240.9 | 229.9 | 265.2 | 55.7 | 18.8 | 82.9 | 4 | 203.3 | 6.4 | 641.9 | 414.9 | 200.3 | 536.8 | 581.7 | 571.7 | 299.7 | 343.5 | 327.4 | 435.3 | 258 | 244.8 | 245.4 | 279.2 | 252.1 | 286.9 | 286.9 | 393.3 | 306.8
1428 | 1238 | -6.9 | 0 | 0 | 278.1 | 253 | 240.5 | 229.5 | 264.6 | 55.7 | 18.8 | 82.8 | 3.6 | 215.9 | 6.4 | 639.8 | 416.1 | 198.4 | 534.8 | 583.1 | 570.1 | 297.5 | 342.1 | 325.5 | 433.5 | 257.6 | 244.4 | 245.4 | 278.9 | 251.7 | 286.7 | 286.5 | 393 | 306.8
1429 | 1239 | -6.9 | 0 | 0 | 277.5 | 252.5 | 240 | 229.1 | 264 | 55.6 | 18.8 | 82.6 | 3.9 | 218.3 | 7.3 | 637.6 | 414.2 | 196.2 | 532.9 | 584.8 | 568.3 | 295.9 | 341.1 | 323.9 | 431.9 | 257.3 | 243.9 | 245.5 | 278.4 | 251.3 | 286.5 | 286.2 | 392.8 | 306.7
1430 | 1240 | -6.9 | 0 | 0 | 277.1 | 252.1 | 239.6 | 228.8 | 263.4 | 55.5 | 18.8 | 82.5 | 3.9 | 214.7 | 8.1 | 635.5 | 412.5 | 194.4 | 531.8 | 585.4 | 566.7 | 293.2 | 339.4 | 321.2 | 430.1 | 256.9 | 243.6 | 245.5 | 277.9 | 250.8 | 286.3 | 285.9 | 392.5 | 306.6
1431 | 1241 | -6.9 | 0 | 0 | 276.6 | 251.8 | 239.1 | 228.5 | 263.1 | 55.5 | 18.8 | 82.4 | 3.7 | 228.4 | 8 | 633.4 | 414.3 | 192.7 | 530.2 | 586.6 | 565 | 292.5 | 338 | 319.7 | 428.2 | 256.6 | 243.2 | 245.6 | 277.5 | 250.4 | 286.1 | 285.5 | 392.2 | 306.5
1432 | 1242 | -6.9 | 0 | 0 | 276.2 | 251.4 | 238.8 | 228.2 | 263.2 | 55.5 | 18.8 | 82.2 | 3.5 | 219.7 | 7.9 | 631.4 | 410.8 | 191.4 | 528.7 | 587.5 | 563.4 | 291.4 | 336.3 | 318.4 | 426.5 | 256.2 | 242.8 | 245.7 | 277.2 | 249.8 | 285.9 | 285.2 | 391.9 | 306.4
1433 | 1243 | -6.9 | 0 | 0 | 275.8 | 251 | 238.5 | 227.8 | 263.3 | 55.4 | 18.8 | 82 | 3.7 | 219.6 | 8.6 | 629.3 | 409.9 | 189.4 | 526.9 | 588.9 | 561.9 | 291.1 | 334.3 | 318.8 | 425.1 | 255.9 | 242.4 | 245.7 | 276.8 | 249.4 | 285.7 | 284.9 | 391.6 | 306.4
1434 | 1244 | -6.9 | 0 | 0 | 275.3 | 250.6 | 238.2 | 227.5 | 263.1 | 55.3 | 18.8 | 81.9 | 3.2 | 210.9 | 8.9 | 627.4 | 411.9 | 187.4 | 523.3 | 590.9 | 560.5 | 289.4 | 332.8 | 317.2 | 423.9 | 255.5 | 242 | 245.8 | 276.5 | 249 | 285.5 | 284.5 | 391.4 | 306.3
1435 | 1245 | -6.9 | 0 | 0 | 274.8 | 250.3 | 237.9 | 227.3 | 262.6 | 55.2 | 18.8 | 81.8 | 3.5 | 221.2 | 8.7 | 625.6 | 411.4 | 185.6 | 520.9 | 591.8 | 559 | 287.5 | 331.2 | 315.1 | 422 | 255.2 | 241.5 | 245.9 | 276.2 | 248.7 | 285.4 | 284.3 | 391.1 | 306.2
1436 | 1246 | -6.9 | 0 | 0 | 274.3 | 250.1 | 237.5 | 227.1 | 262.1 | 55.1 | 18.8 | 81.8 | 3.7 | 240.6 | 7.7 | 623.8 | 407.8 | 184.3 | 519.7 | 592.7 | 557.4 | 287 | 329.4 | 314.2 | 420.8 | 254.8 | 241.1 | 245.9 | 275.9 | 248.2 | 285.2 | 283.9 | 390.8 | 306.2
1437 | 1247 | -6.9 | 0 | 0 | 274 | 249.8 | 237.1 | 226.8 | 261.7 | 55 | 18.8 | 81.7 | 3.5 | 223.7 | 7.4 | 621.8 | 403.3 | 183.3 | 518.5 | 593.7 | 556 | 285.6 | 328 | 312.1 | 419.4 | 254.5 | 240.7 | 246 | 275.5 | 247.7 | 285 | 283.6 | 390.6 | 306.1
1438 | 1248 | -6.9 | 0 | 0 | 273.6 | 249.6 | 236.7 | 226.5 | 261 | 54.9 | 18.8 | 81.6 | 3.4 | 230.9 | 7.6 | 619.7 | 399.8 | 181.6 | 517.4 | 594.6 | 554.7 | 284.3 | 326.2 | 310.4 | 418 | 254.2 | 240.3 | 246 | 275.1 | 247.2 | 284.8 | 283.3 | 390.3 | 306
1439 | 1249 | -6.9 | 0 | 0 | 273.2 | 249.2 | 236.3 | 226.1 | 260.7 | 54.7 | 18.8 | 81.5 | 3.3 | 243.1 | 7.3 | 617.5 | 399.2 | 180.3 | 516.9 | 594.4 | 553.4 | 282.7 | 324.2 | 308.8 | 416.3 | 253.8 | 239.9 | 246.1 | 274.7 | 246.7 | 284.6 | 282.9 | 390 | 306
1440 | 1250 | -6.9 | 0 | 0 | 272.9 | 248.9 | 235.8 | 225.8 | 260.6 | 54.4 | 18.8 | 81.3 | 3.7 | 209 | 7.8 | 615.3 | 397.8 | 178.9 | 516.2 | 595.9 | 552 | 281.3 | 322.8 | 307.6 | 414.8 | 253.5 | 239.4 | 246.1 | 274.3 | 246.2 | 284.4 | 282.5 | 389.7 | 305.9
1441 | 1251 | -6.9 | 0 | 0 | 272.6 | 248.5 | 235.4 | 225.4 | 260.7 | 54.2 | 18.8 | 81.2 | 4 | 220.4 | 8.3 | 613 | 395.2 | 177.3 | 515.2 | 596.9 | 550.6 | 279.7 | 321.2 | 306 | 413.1 | 253.2 | 239 | 246.2 | 274 | 245.8 | 284.2 | 282.2 | 389.4 | 305.8
1442 | 1252 | -6.9 | 0 | 0 | 272.2 | 248.2 | 235 | 225 | 260.8 | 54 | 18.8 | 81.1 | 4.7 | 240.9 | 7.5 | 610.8 | 395.9 | 175.5 | 513.5 | 597.9 | 549.2 | 277.9 | 319.7 | 304.5 | 411.8 | 253 | 238.7 | 246.3 | 273.7 | 245.5 | 284.1 | 281.9 | 389.2 | 305.7
1443 | 1253 | -6.9 | 0 | 0 | 271.8 | 247.9 | 234.6 | 224.6 | 260.8 | 53.8 | 18.8 | 81 | 4.9 | 260.7 | 6.5 | 608.7 | 396.6 | 173.8 | 512 | 598.6 | 547.9 | 277.1 | 317.8 | 304.1 | 410.5 | 252.6 | 238.4 | 246.3 | 273.4 | 245.1 | 283.9 | 281.5 | 388.9 | 305.6
1444 | 1254 | -6.9 | 0 | 0 | 271.5 | 247.6 | 234.2 | 224.3 | 260.6 | 53.6 | 18.8 | 80.9 | 4.4 | 225.9 | 6 | 606.5 | 393.6 | 172.8 | 509.5 | 600.6 | 546.6 | 276.6 | 316 | 303.1 | 409 | 252.4 | 238 | 246.4 | 273.1 | 244.7 | 283.7 | 281.2 | 388.6 | 305.6
1445 | 1255 | -6.9 | 0 | 0 | 271.1 | 247.3 | 233.9 | 224.1 | 260.5 | 53.5 | 18.8 | 80.8 | 3.8 | 248.3 | 5.2 | 604.5 | 394 | 171 | 506.1 | 602.4 | 545.1 | 277.3 | 313.9 | 302.5 | 407.3 | 252.1 | 237.6 | 246.4 | 272.7 | 244.3 | 283.5 | 280.9 | 388.3 | 305.5
1446 | 1256 | -6.9 | 0 | 0 | 270.7 | 247 | 233.6 | 223.9 | 260.2 | 53.4 | 18.8 | 80.7 | 3.8 | 205.1 | 4.6 | 602.4 | 393.1 | 168.9 | 502.4 | 603.5 | 543.5 | 276 | 312.3 | 301.7 | 405.9 | 251.8 | 237.2 | 246.5 | 272.3 | 243.9 | 283.3 | 280.5 | 388 | 305.4
1447 | 1257 | -6.9 | 0 | 0 | 270.4 | 246.7 | 233.3 | 223.7 | 259.8 | 53.3 | 18.8 | 80.6 | 4 | 180.9 | 4.4 | 600.4 | 389.9 | 167.3 | 500.1 | 603.7 | 541.7 | 275.7 | 310.7 | 301.2 | 404.7 | 251.4 | 236.8 | 246.5 | 271.9 | 243.5 | 283.2 | 280.2 | 387.8 | 305.3
1448 | 1258 | -6.9 | 0 | 0 | 270 | 246.3 | 232.9 | 223.6 | 259.4 | 53.2 | 18.8 | 80.5 | 3.1 | 254.5 | 4.2 | 598.4 | 388 | 166 | 498.2 | 602.7 | 540.1 | 274.8 | 309.1 | 300.3 | 403.6 | 251.2 | 236.5 | 246.6 | 271.5 | 243.1 | 283 | 279.8 | 387.5 | 305.3
1449 | 1259 | -6.9 | 0 | 0 | 269.7 | 245.9 | 232.5 | 223.6 | 259 | 53.2 | 18.8 | 80.4 | 3.8 | 267.7 | 4.3 | 596.4 | 387.1 | 164.5 | 495.9 | 604.7 | 538.6 | 274.5 | 307.1 | 299.7 | 402.4 | 250.9 | 236.2 | 246.6 | 271.2 | 242.8 | 282.8 | 279.5 | 387.2 | 305.2
1450 | 1260 | -6.9 | 0 | 0 | 269.1 | 245.6 | 232.2 | 223.6 | 258.8 | 53.2 | 18.8 | 80.2 | 4 | 220.7 | 4.9 | 594.4 | 386.9 | 163.1 | 494.2 | 606 | 537 | 274.4 | 305.7 | 299.5 | 400.6 | 250.6 | 235.8 | 246.7 | 270.8 | 242.6 | 282.6 | 279.2 | 387 | 305.1
1451 | 1261 | -6.9 | 0 | 0 | 268.8 | 245.4 | 231.8 | 223.4 | 258.8 | 53.1 | 18.8 | 80.1 | 4.2 | 220.6 | 7.4 | 592.4 | 383.2 | 161.4 | 492 | 608.6 | 535.4 | 274.2 | 304.6 | 298.6 | 399.4 | 250.3 | 235.5 | 246.7 | 270.6 | 242.2 | 282.4 | 278.9 | 386.7 | 305
1452 | 1262 | -6.9 | 0 | 0 | 268.5 | 245.1 | 231.4 | 223 | 258.5 | 52.9 | 18.8 | 80 | 4.4 | 220.8 | 7.2 | 590.4 | 380.8 | 159.5 | 489 | 610.8 | 533.7 | 273.8 | 302.8 | 297.8 | 398 | 250 | 235.1 | 246.8 | 270.3 | 241.8 | 282.3 | 278.6 | 386.4 | 304.9
1453 | 1263 | -6.9 | 0 | 0 | 268.1 | 244.8 | 230.9 | 222.5 | 258.3 | 52.8 | 18.8 | 79.9 | 4.6 | 226.4 | 7.3 | 588.4 | 378.7 | 157.8 | 486.6 | 612.1 | 532.1 | 272.8 | 301.9 | 295.8 | 396.4 | 249.7 | 234.8 | 246.8 | 270 | 241.5 | 282.1 | 278.3 | 386.1 | 304.8
1454 | 1264 | -6.9 | 0 | 0 | 267.5 | 244.5 | 230.4 | 222.1 | 258 | 52.8 | 18.8 | 79.7 | 4.1 | 210 | 8.9 | 586.4 | 377.9 | 156.3 | 485.2 | 614.3 | 530.5 | 271.1 | 301.1 | 293.3 | 394.9 | 249.4 | 234.4 | 246.9 | 269.7 | 241.1 | 281.9 | 277.9 | 385.9 | 304.8
1455 | 1265 | -6.9 | 0 | 0 | 267.2 | 244.3 | 229.9 | 221.8 | 257.3 | 52.7 | 18.8 | 79.6 | 4 | 210.4 | 8.6 | 584.5 | 376.6 | 155 | 484.2 | 616.8 | 529 | 270 | 299.9 | 291.4 | 393.5 | 249.1 | 234 | 246.9 | 269.3 | 240.7 | 281.7 | 277.6 | 385.6 | 304.7
1456 | 1266 | -6.9 | 0 | 0 | 266.9 | 244 | 229.6 | 221.6 | 256.7 | 52.6 | 18.8 | 79.4 | 4 | 204.4 | 8.6 | 582.5 | 373 | 153.7 | 483.2 | 618.7 | 527.4 | 269.7 | 298 | 290.8 | 392.2 | 248.8 | 233.6 | 247 | 268.9 | 240.4 | 281.6 | 277.3 | 385.3 | 304.6
1457 | 1267 | -6.9 | 0 | 0 | 266.4 | 243.8 | 229.3 | 221.3 | 256.3 | 52.5 | 18.8 | 79.3 | 4.1 | 236.5 | 7.2 | 580.7 | 371.3 | 152.5 | 480.5 | 620.2 | 525.9 | 268.3 | 296.6 | 289.3 | 391 | 248.4 | 233.2 | 247 | 268.6 | 240 | 281.4 | 277 | 385 | 304.5
1458 | 1268 | -6.9 | 0 | 0 | 265.9 | 243.4 | 228.9 | 221 | 255.9 | 52.5 | 18.8 | 79.2 | 4.5 | 247 | 7.1 | 578.8 | 368.5 | 151.3 | 478.3 | 622.2 | 524.4 | 267.5 | 294.8 | 287.8 | 389.9 | 248.1 | 232.8 | 247.1 | 268.5 | 239.6 | 281.2 | 276.6 | 384.8 | 304.4
1459 | 1269 | -6.9 | 0 | 0 | 265.5 | 242.9 | 228.5 | 220.7 | 255.6 | 52.5 | 18.8 | 79.1 | 4.3 | 242.4 | 7.3 | 577 | 367.1 | 149.8 | 476.2 | 623.9 | 522.9 | 267.1 | 292.9 | 287.5 | 388.6 | 247.9 | 232.5 | 247.1 | 269.6 | 239.2 | 281 | 276.3 | 384.5 | 304.3
1460 | 1270 | -6.9 | 0 | 0 | 265 | 242.6 | 228.2 | 220.6 | 255.2 | 52.5 | 18.8 | 79 | 4.2 | 253.9 | 7.2 | 575.2 | 365.5 | 148.3 | 473.6 | 625.9 | 521.4 | 265.6 | 290.9 | 286.5 | 387.2 | 247.6 | 232.2 | 247.2 | 269.6 | 238.8 | 280.9 | 276 | 384.2 | 304.3
1461 | 1271 | -6.9 | 0 | 0 | 264.5 | 242.2 | 227.8 | 220.5 | 254.8 | 52.4 | 18.8 | 78.8 | 3.8 | 233.8 | 7 | 573.5 | 362.6 | 146.9 | 470.6 | 627.2 | 519.9 | 264.8 | 289.1 | 285.6 | 385.8 | 247.4 | 231.9 | 247.2 | 269 | 238.5 | 280.7 | 275.7 | 384 | 304.2
1462 | 1272 | -6.9 | 0 | 0 | 264 | 242 | 227.6 | 220.1 | 254.6 | 52.2 | 18.8 | 78.7 | 3.6 | 222.4 | 6.5 | 571.8 | 361.8 | 145.8 | 468.1 | 628.7 | 518.6 | 262.7 | 287.2 | 283.6 | 384.1 | 247.2 | 231.7 | 247.3 | 268.6 | 238.2 | 280.5 | 275.4 | 383.7 | 304.1
1463 | 1273 | -6.9 | 0 | 0 | 263.7 | 241.8 | 227.3 | 219.6 | 254.4 | 52 | 18.8 | 78.5 | 3.8 | 239.8 | 6.8 | 570.1 | 357.5 | 144.5 | 465.3 | 628.8 | 517.2 | 261.2 | 285.2 | 282.1 | 382.7 | 246.9 | 231.4 | 247.3 | 268.3 | 237.8 | 280.3 | 275.1 | 383.5 | 304
1464 | 1274 | -6.9 | 0 | 0 | 263.3 | 241.6 | 226.9 | 219.2 | 254.1 | 51.9 | 18.8 | 78.4 | 4.1 | 243.6 | 7.4 | 568.2 | 355.3 | 143.2 | 462 | 630.5 | 515.9 | 260.1 | 283.7 | 280.9 | 381.2 | 246.6 | 231 | 247.4 | 267.7 | 237.5 | 280.2 | 274.7 | 383.2 | 303.9
1465 | 1275 | -6.9 | 0 | 0 | 263 | 241.3 | 226.5 | 218.9 | 253.8 | 51.8 | 18.8 | 78.3 | 4.6 | 223.6 | 8.8 | 566.5 | 353.5 | 142.3 | 459.7 | 632 | 514.6 | 259 | 282.2 | 279.4 | 379.9 | 246.4 | 230.7 | 247.4 | 267.2 | 237.1 | 280 | 274.4 | 382.9 | 303.8
1466 | 1276 | -6.9 | 0 | 0 | 262.6 | 241 | 226.2 | 218.5 | 253.5 | 51.7 | 18.8 | 78.1 | 4.9 | 233 | 9.5 | 564.7 | 352.3 | 141.3 | 457.1 | 633 | 513.2 | 257.4 | 279.9 | 278 | 378.3 | 246.2 | 230.4 | 247.4 | 266.8 | 236.7 | 279.8 | 274.1 | 382.7 | 303.7
1467 | 1277 | -6.9 | 0 | 0 | 262.3 | 240.7 | 225.9 | 218.2 | 253.2 | 51.7 | 18.8 | 78 | 5.2 | 245.7 | 8.9 | 562.9 | 348.8 | 140 | 454.8 | 635 | 511.9 | 256.1 | 278.2 | 276.4 | 377.1 | 245.9 | 230.2 | 247.5 | 266.2 | 236.4 | 279.6 | 273.8 | 382.4 | 303.7
1468 | 1278 | -6.9 | 0 | 0 | 262 | 240.4 | 225.5 | 217.9 | 253 | 51.7 | 18.8 | 77.9 | 5.2 | 253.2 | 9 | 560.9 | 346.2 | 138.9 | 452.4 | 636 | 510.6 | 254.4 | 276.1 | 274.8 | 375.7 | 245.7 | 229.8 | 247.5 | 265.9 | 236 | 279.5 | 273.5 | 382.1 | 303.6
1469 | 1279 | -6.9 | 0 | 0 | 261.6 | 240.1 | 225 | 217.6 | 252.9 | 51.7 | 18.8 | 77.7 | 5.1 | 249.1 | 10.1 | 558.9 | 343.6 | 137.8 | 449.3 | 637.7 | 509.2 | 252.9 | 274.3 | 273.4 | 374.1 | 245.4 | 229.5 | 247.6 | 265.4 | 235.7 | 279.3 | 273.2 | 381.9 | 303.5
1470 | 1280 | -6.9 | 0 | 0 | 261.2 | 239.8 | 224.7 | 217.2 | 252.6 | 51.7 | 18.8 | 77.5 | 5 | 240.9 | 11.4 | 557.1 | 343.4 | 136.9 | 446.2 | 639.9 | 507.8 | 251.9 | 272.5 | 272.3 | 372.6 | 245.2 | 229.2 | 247.6 | 264.9 | 235.3 | 279.1 | 272.8 | 381.6 | 303.4
1471 | 1281 | -6.9 | 0 | 0 | 260.7 | 239.6 | 224.5 | 216.9 | 252.3 | 51.6 | 18.8 | 77.4 | 4.5 | 240.8 | 12.2 | 555.3 | 343.7 | 136.1 | 443 | 641.7 | 506.4 | 251.3 | 270.9 | 271.6 | 371.3 | 244.9 | 228.9 | 247.7 | 264.4 | 234.9 | 279 | 272.5 | 381.3 | 303.3
1472 | 1282 | -6.9 | 0 | 0 | 260.2 | 239.3 | 224.4 | 216.7 | 251.9 | 51.6 | 18.9 | 77.3 | 3.7 | 254.8 | 10.4 | 553.6 | 340.1 | 135.2 | 440.8 | 642.6 | 505 | 249.6 | 269.5 | 270 | 369.8 | 244.7 | 228.5 | 247.7 | 264.2 | 234.6 | 278.8 | 272.3 | 381.1 | 303.2
1473 | 1283 | -6.9 | 0 | 0 | 259.9 | 239 | 224.2 | 216.3 | 251.6 | 51.6 | 18.9 | 77.2 | 3.9 | 257 | 9.5 | 551.8 | 336.2 | 134.3 | 437.8 | 645 | 503.6 | 248 | 268 | 269.3 | 368.5 | 244.5 | 228.1 | 247.8 | 263.9 | 234.3 | 278.6 | 271.9 | 380.8 | 303.1
1474 | 1284 | -6.9 | 0 | 0 | 259.7 | 238.8 | 224.1 | 216.1 | 251.2 | 51.5 | 18.9 | 77.1 | 4.3 | 236.9 | 9.3 | 550.1 | 334.4 | 133.4 | 435.4 | 647.2 | 502.2 | 247.1 | 266.6 | 268.6 | 367.5 | 244.3 | 227.8 | 247.8 | 263.6 | 233.9 | 278.5 | 271.6 | 380.6 | 303
1475 | 1285 | -6.9 | 0 | 0 | 259.4 | 238.5 | 223.8 | 215.9 | 250.8 | 51.5 | 18.9 | 77 | 4.3 | 226.9 | 9.3 | 548.4 | 334.9 | 132.5 | 432.6 | 648.1 | 500.8 | 247.5 | 265.3 | 268.7 | 366.6 | 244 | 227.5 | 247.8 | 263.3 | 233.4 | 278.3 | 271.3 | 380.3 | 302.9
1476 | 1286 | -6.9 | 0 | 0 | 259.2 | 238.1 | 223.3 | 215.6 | 250.5 | 51.5 | 18.9 | 76.9 | 4 | 244.8 | 9.7 | 546.7 | 333.4 | 131.6 | 429.6 | 649.7 | 499.6 | 246.5 | 263.7 | 267.2 | 365.3 | 243.8 | 227.2 | 247.9 | 262.9 | 233.1 | 278.1 | 271 | 380.1 | 302.8
1477 | 1287 | -6.9 | 0 | 0 | 258.8 | 237.8 | 222.9 | 215.4 | 250.2 | 51.4 | 18.9 | 76.8 | 3.9 | 229.8 | 10.2 | 545 | 329.6 | 130.9 | 426.9 | 651.2 | 498.3 | 245.5 | 262 | 266 | 364.1 | 243.6 | 226.8 | 247.9 | 262.7 | 232.7 | 278 | 270.7 | 379.8 | 302.7
1478 | 1288 | -6.9 | 0 | 0 | 258.5 | 237.5 | 222.5 | 215.1 | 249.9 | 51.4 | 18.9 | 76.7 | 3.9 | 250.6 | 9.5 | 543.3 | 328 | 130.3 | 423.9 | 652.2 | 497 | 245 | 260.5 | 266 | 363.4 | 243.3 | 226.6 | 247.9 | 262.4 | 232.3 | 277.8 | 270.4 | 379.5 | 302.6
1479 | 1289 | -6.9 | 0 | 0 | 258.3 | 237.2 | 222 | 214.8 | 249.5 | 51.3 | 18.9 | 76.6 | 3.5 | 249.8 | 9.7 | 541.5 | 327.7 | 129.6 | 420.9 | 653.8 | 495.5 | 244.6 | 259.4 | 265.8 | 361.9 | 243 | 226.3 | 248 | 262 | 232 | 277.6 | 270.2 | 379.2 | 302.5
1480 | 1290 | -6.9 | 0 | 0 | 257.9 | 237 | 221.7 | 214.5 | 249.1 | 51.1 | 18.9 | 76.5 | 3.4 | 234.3 | 9.4 | 539.7 | 328 | 128.6 | 418.7 | 654.9 | 494.2 | 243.5 | 258 | 264.5 | 360.7 | 242.7 | 225.9 | 248 | 261.6 | 231.7 | 277.4 | 269.9 | 379 | 302.4
1481 | 1291 | -6.9 | 0 | 0 | 257.6 | 236.8 | 221.4 | 214.2 | 248.8 | 50.9 | 18.9 | 76.4 | 3.8 | 249.3 | 9.4 | 538 | 327.1 | 127.4 | 416.8 | 655.8 | 492.8 | 243.2 | 256.7 | 263.7 | 359.5 | 242.4 | 225.7 | 248.1 | 261.2 | 231.3 | 277.3 | 269.5 | 378.7 | 302.3
1482 | 1292 | -6.9 | 0 | 0 | 257.3 | 236.5 | 221.1 | 213.9 | 248.5 | 50.8 | 18.9 | 76.3 | 3.5 | 245.1 | 9.9 | 536.2 | 325.5 | 126.4 | 414.6 | 657.5 | 491.5 | 242 | 255.9 | 262.7 | 358.4 | 242.2 | 225.3 | 248.1 | 260.7 | 230.9 | 277.1 | 269.2 | 378.4 | 302.2
1483 | 1293 | -6.9 | 0 | 0 | 256.8 | 236.2 | 220.8 | 213.6 | 248.2 | 50.6 | 18.9 | 76.1 | 3.6 | 250.2 | 9.9 | 534.4 | 325.1 | 125.8 | 413.1 | 657.7 | 490.2 | 241.7 | 255.1 | 262 | 357.2 | 241.9 | 225 | 248.2 | 260.3 | 230.6 | 276.9 | 269 | 378.1 | 302.1
1484 | 1294 | -6.9 | 0 | 0 | 256.5 | 236 | 220.5 | 213.3 | 247.9 | 50.5 | 18.9 | 76 | 3.9 | 243.6 | 9.4 | 532.6 | 325.1 | 125.2 | 411.9 | 658.2 | 489 | 241.4 | 253.7 | 261.7 | 355.9 | 241.6 | 224.7 | 248.2 | 259.9 | 230.3 | 276.8 | 268.7 | 377.9 | 302
1485 | 1295 | -6.9 | 0 | 0 | 256.3 | 235.7 | 220.3 | 213.1 | 247.6 | 50.4 | 18.9 | 76 | 3.9 | 250.4 | 8.9 | 530.9 | 324.7 | 124.4 | 409.3 | 660.2 | 487.7 | 240.5 | 252.5 | 261 | 354.7 | 241.4 | 224.3 | 248.2 | 259.4 | 229.9 | 276.6 | 268.4 | 377.6 | 301.9
1486 | 1296 | -6.9 | 0 | 0 | 256 | 235.4 | 220.1 | 212.8 | 247.2 | 50.3 | 18.9 | 75.9 | 3.8 | 247.5 | 9.6 | 529 | 322.7 | 123.7 | 407.1 | 661.9 | 486.3 | 240.7 | 251.6 | 260.6 | 353.7 | 241.1 | 224 | 248.3 | 259 | 229.6 | 276.4 | 268.1 | 377.3 | 301.8
1487 | 1297 | -6.9 | 0 | 0 | 255.5 | 235 | 219.8 | 212.6 | 246.9 | 50.2 | 18.9 | 75.7 | 3.3 | 242.5 | 9.8 | 527.2 | 319.3 | 123.2 | 404.5 | 662.9 | 484.9 | 240.7 | 250.5 | 259.7 | 352.8 | 240.8 | 223.8 | 248.3 | 258.5 | 229.2 | 276.3 | 267.8 | 377.1 | 301.7
1488 | 1298 | -6.9 | 0 | 0 | 255 | 234.6 | 219.5 | 212.3 | 246.4 | 50.1 | 18.9 | 75.6 | 3.3 | 238.7 | 8.8 | 525.3 | 318.5 | 122.5 | 401 | 665.9 | 483.7 | 240.3 | 249.1 | 258.5 | 351.8 | 240.5 | 223.4 | 248.3 | 257.9 | 228.9 | 276.1 | 267.5 | 376.8 | 301.6
1489 | 1299 | -6.9 | 0 | 0 | 254.4 | 234.3 | 219.2 | 212.1 | 246 | 50 | 18.9 | 75.6 | 3.5 | 241 | 7.3 | 523.5 | 317.9 | 121.8 | 398.6 | 667.4 | 482.3 | 240.2 | 248.3 | 258 | 350.5 | 240.2 | 223.1 | 248.4 | 257.4 | 228.5 | 275.9 | 267.3 | 376.5 | 301.5
1490 | 1300 | -6.9 | 0 | 0 | 254.2 | 233.9 | 218.8 | 211.9 | 245.7 | 50 | 18.9 | 75.5 | 3.7 | 258.7 | 6.9 | 521.6 | 318.3 | 121.2 | 396.5 | 667.5 | 480.8 | 239.5 | 247.3 | 257.2 | 349.6 | 240 | 222.8 | 248.4 | 256.9 | 228.2 | 275.8 | 267 | 376.3 | 301.4
1491 | 1301 | -6.9 | 0 | 0 | 254 | 233.6 | 218.5 | 211.6 | 245.4 | 49.9 | 18.9 | 75.3 | 3.3 | 245.5 | 7.1 | 519.8 | 317 | 120.5 | 394.6 | 667.6 | 479.3 | 238.6 | 246.4 | 255.7 | 348.7 | 239.8 | 222.5 | 248.4 | 256.6 | 227.8 | 275.6 | 266.7 | 376 | 301.3
1492 | 1302 | -6.9 | 0 | 0 | 253.7 | 233.2 | 218.2 | 211.3 | 245.1 | 49.8 | 18.9 | 75.2 | 3.1 | 249 | 7.4 | 518 | 316.6 | 119.6 | 392.6 | 669.4 | 478 | 239 | 244.9 | 255.5 | 347.4 | 239.6 | 222.3 | 248.5 | 256.2 | 227.4 | 275.4 | 266.4 | 375.8 | 301.2
1493 | 1303 | -6.9 | 0 | 0 | 253.4 | 232.8 | 218.1 | 211.1 | 244.9 | 49.8 | 18.9 | 75.1 | 2.7 | 240.9 | 7.1 | 516.3 | 317.3 | 118.6 | 390.9 | 671.9 | 476.6 | 238.8 | 243.9 | 255.1 | 346.7 | 239.3 | 222 | 248.5 | 255.5 | 227 | 275.2 | 266.1 | 375.5 | 301.1
1494 | 1304 | -6.9 | 0 | 0 | 253.4 | 232.5 | 217.7 | 210.8 | 244.7 | 49.7 | 18.9 | 75 | 3.2 | 249.2 | 6.2 | 514.6 | 316 | 117.9 | 388.6 | 672.9 | 475.2 | 238.4 | 242.6 | 255 | 345.6 | 239.1 | 221.7 | 248.6 | 255.1 | 226.7 | 275.1 | 265.8 | 375.2 | 301
1495 | 1305 | -6.9 | 0 | 0 | 253.2 | 232.2 | 217.4 | 210.6 | 244.4 | 49.6 | 18.9 | 74.9 | 3.2 | 252.4 | 5.7 | 512.9 | 313.8 | 117.2 | 386.4 | 673.6 | 473.9 | 238.5 | 241.2 | 254.9 | 344.9 | 238.8 | 221.4 | 248.6 | 254.7 | 226.3 | 274.9 | 265.5 | 375 | 300.9
1496 | 1306 | -6.9 | 0 | 0 | 252.8 | 231.9 | 217.1 | 210.4 | 244.1 | 49.5 | 18.9 | 74.8 | 3.7 | 252.7 | 5.6 | 511.1 | 314.9 | 116.5 | 384.2 | 675.8 | 472.7 | 238.6 | 239.6 | 254.6 | 344 | 238.6 | 221.1 | 248.6 | 254.2 | 225.9 | 274.7 | 265.3 | 374.7 | 300.8
1497 | 1307 | -6.9 | 0 | 0 | 252.4 | 231.6 | 216.8 | 210.2 | 243.8 | 49.3 | 18.9 | 74.7 | 3.8 | 241.6 | 5.9 | 509.3 | 314.9 | 116.1 | 382.2 | 678 | 471.5 | 238.6 | 238.4 | 254.2 | 342.8 | 238.4 | 220.9 | 248.7 | 253.8 | 225.6 | 274.6 | 265 | 374.5 | 300.7
1498 | 1308 | -6.9 | 0 | 0 | 252 | 231.3 | 216.6 | 210 | 243.5 | 49.1 | 18.9 | 74.6 | 3.1 | 230.4 | 6.4 | 507.4 | 313 | 115.5 | 379.8 | 680.2 | 470.1 | 237.6 | 237.3 | 252.9 | 341.7 | 238.1 | 220.6 | 248.7 | 253.3 | 225.3 | 274.4 | 264.7 | 374.2 | 300.6
1499 | 1309 | -6.9 | 0 | 0 | 251.8 | 231 | 216.4 | 209.8 | 243.2 | 49.1 | 18.9 | 74.5 | 3.7 | 237.2 | 6 | 505.5 | 311.1 | 115.1 | 376.8 | 683.3 | 468.7 | 237.2 | 235.4 | 252.9 | 340.6 | 237.8 | 220.4 | 248.7 | 252.9 | 225 | 274.2 | 264.4 | 373.9 | 300.5
1500 | 1310 | -6.9 | 0 | 0 | 251.5 | 230.7 | 216.1 | 209.5 | 243 | 49 | 18.9 | 74.5 | 3.7 | 264.3 | 5.5 | 503.7 | 308.3 | 114.5 | 374.8 | 685.5 | 467.3 | 235.9 | 234.1 | 252 | 339.6 | 237.5 | 220.1 | 248.7 | 252.4 | 224.6 | 274.1 | 264.1 | 373.7 | 300.4
1501 | 1311 | -6.9 | 0 | 0 | 251.1 | 230.5 | 215.9 | 209.3 | 242.7 | 49 | 18.9 | 74.4 | 3.9 | 244.6 | 5.8 | 501.8 | 306.5 | 113.8 | 372.5 | 688.1 | 466 | 234.5 | 233.4 | 250.8 | 338.4 | 237.3 | 219.8 | 248.8 | 251.9 | 224.3 | 273.9 | 263.8 | 373.4 | 300.3
1502 | 1312 | -6.9 | 0 | 0 | 250.9 | 230.1 | 215.7 | 209.1 | 242.3 | 48.9 | 18.9 | 74.3 | 3.8 | 244 | 6.3 | 500.1 | 304.4 | 113.3 | 370.7 | 689.6 | 464.7 | 234.2 | 232.6 | 250.1 | 337.7 | 237.1 | 219.5 | 248.8 | 251.6 | 224 | 273.7 | 263.5 | 373.2 | 300.2
1503 | 1313 | -6.9 | 0 | 0 | 250.7 | 229.9 | 215.6 | 208.8 | 242 | 48.9 | 18.9 | 74.2 | 3.8 | 247.5 | 7 | 498.1 | 302.9 | 112.9 | 368.5 | 691.2 | 463.2 | 234.2 | 231.4 | 249.6 | 336.6 | 236.9 | 219.3 | 248.8 | 251.3 | 223.7 | 273.6 | 263.3 | 372.9 | 300.1
1504 | 1314 | -6.9 | 0 | 0 | 250.3 | 229.8 | 215.5 | 208.6 | 241.6 | 48.8 | 18.9 | 74 | 3.4 | 241.5 | 7.9 | 496.1 | 301 | 112.5 | 365.6 | 693.6 | 461.8 | 233.3 | 229.6 | 248.6 | 335.4 | 236.7 | 219 | 248.8 | 251 | 223.5 | 273.4 | 263 | 372.7 | 300
1505 | 1315 | -6.9 | 0 | 0 | 249.9 | 229.5 | 215.2 | 208.4 | 241.4 | 48.7 | 18.9 | 73.9 | 3.6 | 250.2 | 7.9 | 494.2 | 300.8 | 112.1 | 362.7 | 694.9 | 460.5 | 232.1 | 228.1 | 247.6 | 334.4 | 236.5 | 218.7 | 248.9 | 250.4 | 223.2 | 273.3 | 262.7 | 372.4 | 299.9
1506 | 1316 | -6.9 | 0 | 0 | 249.5 | 229.4 | 214.9 | 208.2 | 241.1 | 48.7 | 18.9 | 73.8 | 3.5 | 230.7 | 8.1 | 492.2 | 301.4 | 111.8 | 360.4 | 695.8 | 459.1 | 230.7 | 226.9 | 245.9 | 333.4 | 236.2 | 218.5 | 248.9 | 250 | 222.9 | 273.1 | 262.4 | 372.2 | 299.8
1507 | 1317 | -6.9 | 0 | 0 | 249.2 | 229.2 | 214.6 | 208 | 240.9 | 48.6 | 18.9 | 73.8 | 3.3 | 238 | 8 | 490.2 | 301 | 111.6 | 358.1 | 698.4 | 457.7 | 230.5 | 226.1 | 245.6 | 332.2 | 236 | 218.3 | 248.9 | 249.6 | 222.5 | 272.9 | 262.2 | 371.9 | 299.6
1508 | 1318 | -6.9 | 0 | 0 | 248.7 | 229 | 214.4 | 207.7 | 240.8 | 48.5 | 18.9 | 73.7 | 3.2 | 239.2 | 7.2 | 488.3 | 300 | 111.2 | 356.3 | 701 | 456.3 | 229.8 | 225 | 245.4 | 331.1 | 235.8 | 218 | 249 | 249.3 | 222.2 | 272.8 | 261.9 | 371.7 | 299.5
1509 | 1319 | -6.9 | 0 | 0 | 248.5 | 228.7 | 214.2 | 207.4 | 240.5 | 48.4 | 18.9 | 73.6 | 3 | 224.1 | 6.4 | 486.3 | 299.3 | 110.8 | 354.4 | 703.7 | 455.1 | 229.1 | 223.6 | 245.1 | 330.3 | 235.6 | 217.7 | 249 | 248.9 | 221.8 | 272.6 | 261.6 | 371.4 | 299.4
1510 | 1320 | -6.9 | 0 | 0 | 248 | 228.4 | 213.9 | 207.2 | 240.2 | 48.4 | 18.9 | 73.5 | 2.9 | 242.4 | 5.6 | 484.4 | 297.4 | 110.4 | 352.2 | 705.8 | 453.9 | 228.3 | 222 | 244.3 | 329.2 | 235.3 | 217.5 | 249 | 248.4 | 221.6 | 272.5 | 261.3 | 371.2 | 299.3
1511 | 1321 | -6.9 | 0 | 0 | 247.5 | 228.4 | 213.7 | 207.1 | 239.8 | 48.5 | 18.9 | 73.5 | 3.2 | 265.2 | 4.8 | 482.4 | 298.5 | 109.9 | 350.4 | 707.3 | 452.8 | 227.6 | 219.4 | 243.9 | 328.2 | 235 | 217.2 | 249 | 248 | 221.3 | 272.3 | 261.1 | 370.9 | 299.1
1512 | 1322 | -6.9 | 0 | 0 | 247.4 | 228 | 213.3 | 206.9 | 239.5 | 48.5 | 18.9 | 73.4 | 3.4 | 248.9 | 4.8 | 480.5 | 298.6 | 109.5 | 349.7 | 708 | 451.7 | 226.7 | 218.8 | 243.5 | 327.2 | 234.8 | 216.8 | 249.1 | 247.6 | 221 | 272.1 | 260.8 | 370.7 | 299.1
1513 | 1323 | -6.9 | 0 | 0 | 247.1 | 227.7 | 213.1 | 206.6 | 239.2 | 48.5 | 19 | 73.3 | 3.3 | 223.3 | 6.3 | 478.4 | 298.5 | 108.8 | 348 | 708.2 | 450.4 | 226 | 217.6 | 243.7 | 326.4 | 234.5 | 216.5 | 249.1 | 247.2 | 220.8 | 272 | 260.5 | 370.4 | 298.9
1514 | 1324 | -6.9 | 0 | 0 | 246.5 | 227.4 | 213 | 206.4 | 239 | 48.4 | 19 | 73.2 | 3.3 | 234.1 | 6.6 | 476.4 | 298.7 | 107.9 | 345.3 | 710.4 | 449.2 | 225.7 | 217 | 243.2 | 325.3 | 234.2 | 216.2 | 249.1 | 247 | 220.5 | 271.8 | 260.2 | 370.2 | 298.7
1515 | 1325 | -6.9 | 0 | 0 | 246.6 | 226.9 | 212.6 | 206.1 | 238.7 | 48.4 | 19 | 73.1 | 3.5 | 240.7 | 6.5 | 474.3 | 299.5 | 107.3 | 343.7 | 712 | 447.9 | 224.5 | 216 | 241.3 | 323.9 | 234 | 215.9 | 249.1 | 246.8 | 220.2 | 271.6 | 260 | 369.9 | 298.8
1516 | 1326 | -6.9 | 0 | 0 | 246.4 | 226.6 | 212.3 | 205.9 | 238.3 | 48.3 | 19 | 73 | 3.6 | 257.6 | 6.8 | 472.3 | 297.8 | 106.9 | 341.2 | 714.3 | 446.6 | 223.9 | 215 | 240.2 | 322.8 | 233.7 | 215.6 | 249.2 | 246.4 | 219.9 | 271.5 | 259.7 | 369.7 | 298.6
1517 | 1327 | -6.9 | 0 | 0 | 245.5 | 226.5 | 212.4 | 205.9 | 238 | 48.2 | 19 | 72.9 | 3.6 | 253.6 | 6.5 | 470.3 | 298.2 | 106.3 | 338.2 | 715.9 | 445.4 | 223.8 | 214.6 | 239.4 | 322.2 | 233.4 | 215.3 | 249.2 | 246 | 219.5 | 271.3 | 259.4 | 369.4 | 298.3
1518 | 1328 | -6.9 | 0 | 0 | 246 | 226 | 211.7 | 205.4 | 237.7 | 48 | 19 | 72.8 | 3.3 | 246.2 | 6.2 | 468.2 | 297.7 | 105.8 | 336.3 | 717 | 444 | 223.8 | 214.2 | 238.9 | 321.1 | 233.1 | 215 | 249.2 | 245.6 | 219.3 | 271.2 | 259.2 | 369.2 | 298.4
1519 | 1329 | -6.9 | 0 | 0 | 245.5 | 226 | 211.5 | 205.2 | 237.4 | 48 | 19 | 72.8 | 3.5 | 247.4 | 5.5 | 466.3 | 297.3 | 105.2 | 333.9 | 718.2 | 442.6 | 223.1 | 213.8 | 238.2 | 320.4 | 232.8 | 214.6 | 249.2 | 245.2 | 219 | 271 | 258.9 | 368.9 | 298.2
1520 | 1330 | -6.9 | 0 | 0 | 245 | 225.9 | 211.3 | 205 | 237.2 | 47.9 | 19 | 72.7 | 3.4 | 261.4 | 5.1 | 464.3 | 296.5 | 104.6 | 331.6 | 720.7 | 441.3 | 221.9 | 212.7 | 236.5 | 319.6 | 232.6 | 214.3 | 249.3 | 244.8 | 218.7 | 270.9 | 258.7 | 368.7 | 298
1521 | 1331 | -6.9 | 0 | 0 | 245 | 225.4 | 210.9 | 204.7 | 236.9 | 47.9 | 19 | 72.6 | 3.3 | 246.1 | 4.8 | 462.4 | 294.9 | 104 | 330.6 | 722.8 | 440 | 221.2 | 211.9 | 235.1 | 318.6 | 232.3 | 214 | 249.3 | 244.4 | 218.4 | 270.7 | 258.4 | 368.4 | 298.1
1522 | 1332 | -6.9 | 0 | 0 | 244.2 | 225.1 | 210.9 | 204.6 | 236.5 | 47.9 | 19 | 72.5 | 3.3 | 245.6 | 4.5 | 460.5 | 292.8 | 103.6 | 328.5 | 723.5 | 438.8 | 220.9 | 210.6 | 234.8 | 317.8 | 232.1 | 213.7 | 249.3 | 244 | 218.1 | 270.6 | 258.1 | 368.2 | 297.7
1523 | 1333 | -6.9 | 0 | 0 | 244.3 | 224.8 | 210.5 | 204.3 | 236.2 | 47.9 | 19 | 72.4 | 3.5 | 258.9 | 3.9 | 458.2 | 291.7 | 102.9 | 325.8 | 724.4 | 437.6 | 220.8 | 209.4 | 234.1 | 316.9 | 231.8 | 213.4 | 249.3 | 243.6 | 217.8 | 270.4 | 257.9 | 368 | 297.7
1524 | 1334 | -6.9 | 0 | 0 | 244.5 | 224.5 | 210.1 | 204 | 236 | 47.9 | 19 | 72.4 | 3.5 | 247.4 | 3.5 | 456.1 | 291.8 | 102.4 | 324.7 | 726 | 436.4 | 220.6 | 208.8 | 233.7 | 316.3 | 231.6 | 213.1 | 249.4 | 243.3 | 217.5 | 270.2 | 257.6 | 367.7 | 297.8
1525 | 1335 | -6.9 | 0 | 0 | 244.2 | 224.2 | 209.8 | 203.7 | 235.8 | 47.8 | 19 | 72.3 | 3.2 | 234.1 | 3.4 | 454 | 292.3 | 101.9 | 323.5 | 728.3 | 435.3 | 220.3 | 207.8 | 233.5 | 315.7 | 231.3 | 212.8 | 249.4 | 243 | 217.2 | 270.1 | 257.3 | 367.4 | 297.6
1526 | 1336 | -6.9 | 0 | 0 | 244 | 223.9 | 209.5 | 203.5 | 235.6 | 47.8 | 19 | 72.2 | 2.9 | 236.5 | 3.4 | 452 | 292 | 101.5 | 321.9 | 729.6 | 434.3 | 219.9 | 207 | 232.8 | 314.9 | 231.1 | 212.5 | 249.4 | 242.7 | 216.9 | 269.9 | 257 | 367.2 | 297.5
1527 | 1337 | -6.9 | 0 | 0 | 243.9 | 223.6 | 209.3 | 203.3 | 235.1 | 47.8 | 19 | 72.2 | 2.9 | 236.1 | 3.7 | 450.1 | 291.4 | 101.1 | 321.4 | 729.4 | 433.3 | 219.6 | 205.7 | 232.5 | 314.2 | 230.8 | 212.2 | 249.4 | 242.3 | 216.6 | 269.8 | 256.8 | 366.9 | 297.4
1528 | 1338 | -6.9 | 0 | 0 | 243.6 | 223.2 | 209.1 | 203.1 | 234.7 | 47.6 | 19 | 72.1 | 2.8 | 241.5 | 3.8 | 448.2 | 290.3 | 100.6 | 320.8 | 729.4 | 432.2 | 220 | 204.7 | 232.6 | 313.6 | 230.6 | 211.9 | 249.4 | 241.9 | 216.3 | 269.6 | 256.5 | 366.7 | 297.3
1529 | 1339 | -6.9 | 0 | 0 | 243.2 | 222.8 | 208.8 | 202.9 | 234.7 | 47.5 | 19 | 72 | 2.9 | 218 | 3.4 | 446.3 | 289.2 | 100.2 | 318.4 | 730.7 | 431.1 | 221 | 203.6 | 233.4 | 312.9 | 230.3 | 211.7 | 249.4 | 241.6 | 216 | 269.5 | 256.2 | 366.5 | 297.2
1530 | 1340 | -6.9 | 0 | 0 | 242.7 | 222.4 | 208.6 | 202.6 | 234.6 | 47.5 | 19 | 71.9 | 3.5 | 195.7 | 3.2 | 444.3 | 288.3 | 99.8 | 316.5 | 732.7 | 430.1 | 221.7 | 203.1 | 234.1 | 312.4 | 230 | 211.4 | 249.5 | 241.4 | 215.8 | 269.3 | 255.9 | 366.2 | 297.1
1531 | 1341 | -6.9 | 0 | 0 | 242.4 | 222.1 | 208.4 | 202.4 | 234.5 | 47.4 | 19 | 71.8 | 3.4 | 216 | 3.5 | 442.4 | 287.6 | 99.5 | 316 | 733.6 | 429 | 221.5 | 203.1 | 234.1 | 312 | 229.8 | 211.1 | 249.5 | 241.1 | 215.4 | 269.2 | 255.6 | 366 | 297
1532 | 1342 | -6.9 | 0 | 0 | 241.5 | 222 | 208.4 | 202.3 | 234.1 | 47.4 | 19 | 71.7 | 3.6 | 228.4 | 3.4 | 440.5 | 287.6 | 98.9 | 315.1 | 734.5 | 427.7 | 222.2 | 202 | 234.2 | 311.2 | 229.6 | 210.9 | 249.5 | 240.8 | 215.1 | 269 | 255.4 | 365.7 | 296.6
1533 | 1343 | -6.9 | 0 | 0 | 241.5 | 221.6 | 208 | 202 | 233.9 | 47.3 | 19 | 71.7 | 3.2 | 216.7 | 3.4 | 438.6 | 286.9 | 98.3 | 313 | 735.7 | 426.7 | 221.7 | 200.6 | 233.2 | 310 | 229.4 | 210.7 | 249.5 | 240.5 | 214.8 | 268.9 | 255.1 | 365.5 | 296.6
1534 | 1344 | -6.9 | 0 | 0 | 241.3 | 221.2 | 207.6 | 201.7 | 233.8 | 47.2 | 19 | 71.6 | 3.5 | 226.7 | 3.7 | 436.7 | 286.5 | 97.7 | 311.7 | 736.4 | 425.6 | 221.8 | 199.3 | 233.7 | 309.2 | 229.2 | 210.4 | 249.5 | 240 | 214.5 | 268.7 | 254.8 | 365.2 | 296.6
1535 | 1345 | -6.9 | 0 | 0 | 240.1 | 221.3 | 207.9 | 201.8 | 233.7 | 47.2 | 19 | 71.6 | 3.6 | 232.6 | 4.1 | 434.7 | 286.8 | 97.4 | 310.6 | 737.5 | 424.4 | 221.3 | 198.7 | 233.1 | 308.4 | 228.9 | 210.2 | 249.6 | 239.7 | 214.2 | 268.6 | 254.5 | 365 | 296.1
1536 | 1346 | -6.9 | 0 | 0 | 240.9 | 220.8 | 207.1 | 201.3 | 233.8 | 47.1 | 19 | 71.5 | 3.8 | 230.1 | 4.4 | 432.8 | 286.2 | 97.3 | 309.7 | 738.1 | 423.3 | 221.1 | 197.6 | 233.3 | 307.7 | 228.8 | 210 | 249.6 | 239.5 | 213.9 | 268.4 | 254.3 | 364.7 | 296.4
1537 | 1347 | -6.9 | 0 | 0 | 240.7 | 220.7 | 206.8 | 201.1 | 233.7 | 47.1 | 19 | 71.4 | 4 | 222.4 | 4.6 | 430.8 | 282 | 97.2 | 309 | 739.9 | 422.2 | 221.3 | 196.6 | 233.8 | 307.2 | 228.5 | 209.8 | 249.6 | 239.2 | 213.7 | 268.2 | 254 | 364.5 | 296.3
1538 | 1348 | -6.9 | 0 | 0 | 240.3 | 220.7 | 206.6 | 200.9 | 233.5 | 47 | 19 | 71.4 | 3.9 | 217.7 | 4.6 | 428.9 | 277.7 | 96.9 | 308.6 | 741.3 | 421.2 | 222.3 | 196.3 | 234.6 | 306.5 | 228.3 | 209.5 | 249.6 | 238.8 | 213.4 | 268.1 | 253.8 | 364.3 | 296.2
1539 | 1349 | -6.9 | 0 | 0 | 239.9 | 220.5 | 206.4 | 200.7 | 233.3 | 46.9 | 19 | 71.3 | 3.7 | 217.7 | 4.7 | 426.9 | 275.8 | 96.5 | 307.2 | 742.6 | 420.1 | 222.5 | 195.4 | 235.1 | 305.7 | 228.1 | 209.3 | 249.6 | 238.4 | 213.2 | 267.9 | 253.5 | 364 | 296
1540 | 1350 | -6.9 | 0 | 0 | 239.7 | 220.2 | 206.3 | 200.5 | 233 | 46.8 | 19 | 71.1 | 3.4 | 230.3 | 4.5 | 424.9 | 275.5 | 96.2 | 305.8 | 745 | 418.9 | 222.5 | 194.4 | 235 | 305.1 | 227.9 | 209 | 249.6 | 238.1 | 212.9 | 267.8 | 253.3 | 363.8 | 296
1541 | 1351 | -6.9 | 0 | 0 | 239.4 | 220 | 206.1 | 200.3 | 232.8 | 46.8 | 19 | 71.1 | 3.3 | 256.2 | 4.5 | 422.9 | 275.6 | 95.8 | 304.1 | 746.8 | 417.8 | 221.2 | 193.6 | 232.9 | 304.4 | 227.7 | 208.8 | 249.7 | 237.8 | 212.6 | 267.6 | 253 | 363.5 | 295.8
1542 | 1352 | -6.9 | 0 | 0 | 238.9 | 219.7 | 206 | 200.2 | 232.6 | 46.8 | 19 | 71 | 3.3 | 256.2 | 4.4 | 420.9 | 275.3 | 95.5 | 302.6 | 748.2 | 416.8 | 219.7 | 193 | 231.1 | 303.4 | 227.4 | 208.5 | 249.7 | 237.5 | 212.4 | 267.5 | 252.7 | 363.3 | 295.6
1543 | 1353 | -6.9 | 0 | 0 | 238.2 | 219.3 | 205.9 | 200.1 | 232.3 | 46.7 | 19 | 70.9 | 3.3 | 251.2 | 4.9 | 418.9 | 274.3 | 95.1 | 301.1 | 750 | 415.8 | 218.4 | 192.6 | 229.7 | 302.8 | 227.2 | 208.2 | 249.7 | 237.2 | 212.1 | 267.3 | 252.5 | 363 | 295.4
1544 | 1354 | -6.9 | 0 | 0 | 237.9 | 218.9 | 205.7 | 199.8 | 232.2 | 46.7 | 19.1 | 70.8 | 3.4 | 237.1 | 5.4 | 416.9 | 272.8 | 94.5 | 299.9 | 751.4 | 414.7 | 218.1 | 192.1 | 229.8 | 302.2 | 226.9 | 207.9 | 249.7 | 236.9 | 211.9 | 267.2 | 252.2 | 362.8 | 295.3
1545 | 1355 | -6.9 | 0 | 0 | 238 | 218.3 | 205.3 | 199.5 | 232 | 46.7 | 19.1 | 70.7 | 3.5 | 235.9 | 6.2 | 415 | 271.2 | 94 | 298.4 | 752.9 | 413.6 | 218.1 | 191.3 | 230 | 301.5 | 226.7 | 207.6 | 249.7 | 236.6 | 211.7 | 267 | 252 | 362.5 | 295.4
1546 | 1356 | -6.9 | 0 | 0 | 237.5 | 218 | 205.2 | 199.3 | 231.8 | 46.6 | 19.1 | 70.6 | 3.6 | 252.9 | 6.5 | 412.9 | 271.5 | 93.6 | 296.9 | 753.4 | 412.5 | 217.9 | 190.5 | 229.9 | 300.8 | 226.5 | 207.4 | 249.7 | 236.4 | 211.5 | 266.9 | 251.7 | 362.3 | 295.2
1547 | 1357 | -6.9 | 0 | 0 | 237.2 | 217.7 | 205 | 199.1 | 231.5 | 46.7 | 19.1 | 70.5 | 3.8 | 219.7 | 5.9 | 410.9 | 270.1 | 93.3 | 296 | 751.5 | 411.5 | 218.9 | 190.1 | 230.5 | 300.3 | 226.3 | 207.1 | 249.7 | 236 | 211.3 | 266.7 | 251.5 | 362 | 295.2
1548 | 1358 | -6.9 | 0 | 0 | 237 | 217.4 | 204.9 | 198.9 | 231.2 | 46.7 | 19.1 | 70.5 | 4.1 | 220.3 | 4.9 | 408.9 | 269.9 | 93 | 295.3 | 751.1 | 410.4 | 219.7 | 189.2 | 231 | 299.7 | 226.1 | 206.8 | 249.7 | 235.7 | 211 | 266.6 | 251.2 | 361.8 | 295
1549 | 1359 | -6.9 | 0 | 0 | 236.7 | 217.1 | 204.7 | 198.7 | 231.1 | 46.6 | 19.1 | 70.4 | 4.2 | 250.1 | 5.3 | 406.9 | 268.4 | 92.8 | 294.5 | 753.2 | 409.1 | 220.1 | 188.6 | 231.5 | 299.1 | 225.9 | 206.6 | 249.8 | 235.4 | 210.8 | 266.4 | 250.9 | 361.5 | 294.9
1550 | 1360 | -6.9 | 0 | 0 | 236.6 | 216.9 | 204.5 | 198.5 | 230.9 | 46.6 | 19.1 | 70.3 | 3.7 | 246.5 | 6.1 | 404.8 | 267.7 | 92.3 | 293.2 | 755.5 | 407.8 | 219.4 | 188 | 231.2 | 298.3 | 225.7 | 206.4 | 249.8 | 235.3 | 210.6 | 266.3 | 250.7 | 361.3 | 294.8
1551 | 1361 | -6.9 | 0 | 0 | 236.5 | 216.6 | 204.2 | 198.4 | 230.7 | 46.4 | 19.1 | 70.2 | 3.8 | 272.6 | 6.6 | 402.6 | 266.6 | 92 | 292.5 | 758 | 406.5 | 218.8 | 187.4 | 230.8 | 297.1 | 225.5 | 206.2 | 249.8 | 235.1 | 210.3 | 266.1 | 250.5 | 361.1 | 294.7
1552 | 1362 | -6.9 | 0 | 0 | 236.3 | 216.2 | 204 | 198.2 | 230.6 | 46.3 | 19.1 | 70.1 | 3.4 | 259.6 | 7.1 | 400.5 | 266.6 | 91.5 | 291.5 | 760.4 | 405.1 | 218.5 | 186.6 | 231.4 | 296.6 | 225.3 | 205.9 | 249.8 | 234.8 | 210.1 | 266 | 250.2 | 360.8 | 294.5
1553 | 1363 | -6.9 | 0 | 0 | 235.9 | 216.1 | 203.9 | 198.1 | 230.6 | 46.2 | 19.1 | 70.1 | 3.4 | 252.5 | 6.8 | 398.4 | 266.2 | 91.3 | 289.4 | 762.6 | 403.9 | 218 | 186 | 230.9 | 296 | 225.1 | 205.7 | 249.8 | 234.5 | 209.9 | 265.8 | 249.9 | 360.6 | 294.3
1554 | 1364 | -6.9 | 0 | 0 | 236 | 215.8 | 203.5 | 197.8 | 230.5 | 46.2 | 19.1 | 70 | 3.1 | 233.5 | 6.9 | 396.2 | 265.1 | 91 | 287.5 | 764.8 | 402.7 | 216.3 | 185.5 | 229.4 | 295 | 224.9 | 205.5 | 249.8 | 234.2 | 209.7 | 265.7 | 249.7 | 360.3 | 294.3
1555 | 1365 | -6.9 | 0 | 0 | 235.8 | 215.4 | 203.1 | 197.6 | 230.4 | 46.1 | 19.1 | 69.9 | 2.8 | 252.1 | 6.5 | 393.9 | 262 | 90.8 | 284.1 | 766.7 | 401.7 | 215.7 | 184.6 | 229.3 | 294.5 | 224.7 | 205.3 | 249.8 | 233.9 | 209.4 | 265.5 | 249.4 | 360.1 | 294.2
1556 | 1366 | -6.9 | 0 | 0 | 234.9 | 215.4 | 203.2 | 197.6 | 230.2 | 46.2 | 19.1 | 69.8 | 3.1 | 246.9 | 6.3 | 391.6 | 262.4 | 90.5 | 282.5 | 766.4 | 400.5 | 215.4 | 183.3 | 229.6 | 293.9 | 224.6 | 205 | 249.8 | 233.7 | 209.2 | 265.4 | 249.2 | 359.9 | 293.7
1557 | 1367 | -6.9 | 0 | 0 | 235.3 | 215.1 | 202.6 | 197.2 | 229.9 | 46.2 | 19.1 | 69.8 | 3.3 | 229.5 | 6.1 | 389.5 | 262.1 | 90.1 | 281.5 | 768.1 | 399.5 | 215.5 | 182.5 | 229.8 | 293.1 | 224.4 | 204.8 | 249.8 | 233.4 | 208.9 | 265.2 | 248.9 | 359.6 | 293.9
1558 | 1368 | -6.9 | 0 | 0 | 235.3 | 214.9 | 202.4 | 196.9 | 229.5 | 46.2 | 19.1 | 69.7 | 3.1 | 216.6 | 6.8 | 387.4 | 258.7 | 89.7 | 279.4 | 769.5 | 398.4 | 215.6 | 181.7 | 230.1 | 292.5 | 224.2 | 204.6 | 249.8 | 233.2 | 208.7 | 265 | 248.7 | 359.4 | 293.8
1559 | 1369 | -6.9 | 0 | 0 | 234.1 | 214.9 | 202.7 | 197.1 | 229.1 | 46.2 | 19.1 | 69.7 | 3.5 | 217.2 | 6.6 | 385.3 | 256 | 89.1 | 278.7 | 768.2 | 397.3 | 216.2 | 180.8 | 230.8 | 292.1 | 224 | 204.3 | 249.8 | 233 | 208.5 | 264.9 | 248.4 | 359.2 | 293.2
1560 | 1370 | -6.9 | 0 | 0 | 234.9 | 214.2 | 201.7 | 196.6 | 228.9 | 46 | 19.1 | 69.6 | 4 | 209 | 5.5 | 383.2 | 256.1 | 88.9 | 277.3 | 769 | 396.2 | 216.9 | 180.2 | 231.4 | 291.6 | 223.8 | 204.2 | 249.9 | 232.8 | 208.3 | 264.7 | 248.2 | 358.9 | 293.6
1561 | 1371 | -6.9 | 0 | 0 | 234.1 | 214.1 | 201.7 | 196.6 | 228.7 | 45.9 | 19.1 | 69.5 | 3.5 | 222.7 | 5.3 | 381 | 255.8 | 88.6 | 276.5 | 770.2 | 394.9 | 217.5 | 179.9 | 231.7 | 290.9 | 223.6 | 204 | 249.9 | 232.6 | 208 | 264.6 | 248 | 358.7 | 293.2
1562 | 1372 | -6.9 | 0 | 0 | 233.3 | 214 | 201.6 | 196.4 | 228.6 | 45.9 | 19.1 | 69.5 | 3.6 | 233.2 | 4.8 | 378.9 | 250.2 | 88.1 | 275.7 | 771.8 | 393.8 | 217.8 | 179.3 | 231.6 | 290.2 | 223.4 | 203.7 | 249.9 | 232.4 | 207.7 | 264.4 | 247.7 | 358.4 | 293
1563 | 1373 | -6.9 | 0 | 0 | 233.6 | 213.5 | 201 | 195.9 | 228.6 | 45.8 | 19.1 | 69.4 | 3.6 | 195.3 | 5.4 | 376.8 | 245.3 | 87.7 | 274.7 | 774.3 | 392.9 | 217.7 | 179.2 | 231.6 | 289.8 | 223.2 | 203.3 | 249.9 | 232.2 | 207.4 | 264.3 | 247.5 | 358.2 | 293.2
1564 | 1374 | -6.9 | 0 | 0 | 233.2 | 213.3 | 201 | 195.7 | 228.4 | 45.7 | 19.1 | 69.3 | 3.2 | 230.5 | 6.1 | 374.6 | 244.7 | 87.4 | 273.8 | 773 | 391.9 | 217.5 | 178.8 | 231.5 | 289.1 | 223 | 203.1 | 249.9 | 232 | 207.2 | 264.1 | 247.2 | 357.9 | 293
1565 | 1375 | -6.9 | 0 | 0 | 233.3 | 213 | 200.7 | 195.4 | 228.3 | 45.6 | 19.1 | 69.2 | 3.3 | 239.5 | 5.8 | 372.5 | 243 | 86.9 | 273.1 | 773 | 390.8 | 217.6 | 178 | 231.4 | 288.5 | 222.8 | 202.8 | 249.9 | 231.7 | 207 | 264 | 247 | 357.7 | 293
1566 | 1376 | -6.9 | 0 | 0 | 233 | 212.8 | 200.4 | 195.2 | 228.2 | 45.5 | 19.1 | 69.1 | 3 | 200 | 7 | 370.4 | 242.8 | 86.5 | 271.9 | 774.4 | 389.7 | 217.5 | 177.1 | 231.4 | 288 | 222.6 | 202.6 | 249.9 | 231.5 | 206.7 | 263.8 | 246.7 | 357.5 | 292.9
1567 | 1377 | -6.9 | 0 | 0 | 232.5 | 212.6 | 200.3 | 195.1 | 228 | 45.4 | 19.1 | 69 | 3.8 | 218 | 7.2 | 368.3 | 241.9 | 86.1 | 270.6 | 775.2 | 388.8 | 216.8 | 176.3 | 230.8 | 287.4 | 222.4 | 202.4 | 249.9 | 231.3 | 206.4 | 263.7 | 246.4 | 357.2 | 292.7
1568 | 1378 | -6.9 | 0 | 0 | 232.3 | 212.4 | 200.1 | 194.9 | 227.9 | 45.3 | 19.1 | 69 | 4.5 | 230.1 | 6.7 | 366.2 | 238.6 | 85.9 | 270 | 777 | 387.6 | 216.6 | 176 | 230.8 | 286.9 | 222.2 | 202.2 | 249.9 | 231.2 | 206.1 | 263.5 | 246.2 | 357 | 292.6
1569 | 1379 | -6.9 | 0 | 0 | 232.1 | 212.3 | 199.8 | 194.6 | 227.8 | 45.2 | 19.1 | 68.9 | 4.6 | 243.4 | 5.5 | 364.1 | 237.2 | 85.7 | 269.7 | 777.6 | 386.4 | 216.3 | 175.6 | 230.6 | 286.1 | 222 | 201.9 | 249.9 | 230.9 | 205.9 | 263.3 | 246 | 356.8 | 292.5
1570 | 1380 | -6.9 | 0 | 0 | 231.9 | 212.2 | 199.6 | 194.4 | 227.6 | 45.1 | 19.1 | 68.8 | 4.1 | 240.1 | 4.6 | 362.1 | 236.7 | 85.5 | 268.7 | 777.1 | 385.2 | 216.4 | 174.9 | 230.9 | 285.3 | 221.9 | 201.7 | 249.9 | 230.7 | 205.7 | 263.2 | 245.7 | 356.5 | 292.4
1571 | 1381 | -6.9 | 0 | 0 | 231.7 | 212.1 | 199.4 | 194.2 | 227.4 | 45.1 | 19.1 | 68.7 | 3.9 | 217.1 | 3.9 | 360 | 236.9 | 85.1 | 267.9 | 776.7 | 384.2 | 215.9 | 174.2 | 230.3 | 284.8 | 221.7 | 201.5 | 249.9 | 230.4 | 205.5 | 263 | 245.5 | 356.3 | 292.3
1572 | 1382 | -6.9 | 0 | 0 | 231.4 | 211.8 | 199.2 | 194 | 227.2 | 45.1 | 19.1 | 68.7 | 3.8 | 227.4 | 3.5 | 358 | 235.9 | 84.8 | 267.3 | 778 | 383.3 | 215.2 | 173.9 | 229.3 | 284.1 | 221.6 | 201.3 | 249.9 | 230.2 | 205.2 | 262.9 | 245.2 | 356 | 292.2
1573 | 1383 | -6.9 | 0 | 0 | 231.1 | 211.5 | 199 | 193.8 | 226.9 | 45.1 | 19.1 | 68.6 | 3.9 | 241.3 | 3.3 | 356 | 233.4 | 84.7 | 267.1 | 779.8 | 382.4 | 214.8 | 173 | 229 | 283.5 | 221.4 | 201.1 | 250 | 230 | 205 | 262.7 | 245 | 355.8 | 292.1
1574 | 1384 | -6.9 | 0 | 0 | 230.6 | 211.2 | 198.8 | 193.7 | 226.5 | 45.1 | 19.1 | 68.5 | 3.8 | 255.5 | 4.5 | 354 | 230.8 | 84.5 | 266.9 | 781.4 | 381.7 | 214.7 | 173 | 229.3 | 283.1 | 221.2 | 200.9 | 250 | 229.7 | 204.8 | 262.5 | 244.7 | 355.6 | 291.9
1575 | 1385 | -6.9 | 0 | 0 | 230.7 | 210.9 | 198.5 | 193.4 | 226.3 | 45.1 | 19.1 | 68.4 | 3.5 | 258.1 | 6.5 | 352 | 225.8 | 84.3 | 266.3 | 782.8 | 381.1 | 214.1 | 172.8 | 229.5 | 282.6 | 221 | 200.5 | 250 | 229.5 | 204.6 | 262.4 | 244.5 | 355.3 | 291.9
1576 | 1386 | -6.9 | 0 | 0 | 230.6 | 210.6 | 198.3 | 193.2 | 226.2 | 45.1 | 19.1 | 68.3 | 3.4 | 230.8 | 7.5 | 349.9 | 223 | 84.2 | 264.6 | 783.8 | 380.5 | 213.4 | 172.8 | 229.7 | 282.1 | 220.7 | 200.2 | 250 | 229.2 | 204.4 | 262.2 | 244.3 | 355.1 | 291.8
1577 | 1387 | -6.9 | 0 | 0 | 230.4 | 210.3 | 198.1 | 193 | 226 | 45 | 19.1 | 68.3 | 3.3 | 221.1 | 8.5 | 347.9 | 221.5 | 83.9 | 264.2 | 784.3 | 379.9 | 213.1 | 172.6 | 229.8 | 281.7 | 220.5 | 199.9 | 250 | 229 | 204.2 | 262.1 | 244 | 354.8 | 291.6
1578 | 1388 | -6.9 | 0 | 0 | 230.3 | 210 | 198 | 192.8 | 225.7 | 44.9 | 19.1 | 68.2 | 3.1 | 227.9 | 7.8 | 345.8 | 221.7 | 83.6 | 263.6 | 785.1 | 379.2 | 213.1 | 172.2 | 229.9 | 281.2 | 220.3 | 199.6 | 250 | 228.8 | 203.9 | 261.9 | 243.8 | 354.6 | 291.5
1579 | 1389 | -6.9 | 0 | 0 | 230.2 | 209.7 | 197.9 | 192.6 | 225.4 | 44.9 | 19.1 | 68.1 | 3.8 | 227.4 | 7 | 343.5 | 221.5 | 83.3 | 262 | 786.8 | 378.6 | 213.4 | 171.4 | 229.4 | 280.4 | 220.1 | 199.3 | 250 | 228.6 | 203.7 | 261.7 | 243.6 | 354.4 | 291.4
1580 | 1390 | -6.9 | 0 | 0 | 229.8 | 209.4 | 197.7 | 192.5 | 225.2 | 44.8 | 19.1 | 68.1 | 4.1 | 229.3 | 7.4 | 341.3 | 222.7 | 83.3 | 261.1 | 789.2 | 377.8 | 212.8 | 170.8 | 227.9 | 279.6 | 219.9 | 199.1 | 250 | 228.3 | 203.5 | 261.6 | 243.3 | 354.1 | 291.3
1581 | 1391 | -6.9 | 0 | 0 | 229.4 | 209 | 197.4 | 192.3 | 225.1 | 44.8 | 19.1 | 67.9 | 3.9 | 217.2 | 8.5 | 339.2 | 223.3 | 83.3 | 260.2 | 791.1 | 377 | 211.9 | 170.2 | 227.2 | 278.9 | 219.7 | 198.9 | 250 | 228 | 203.2 | 261.4 | 243.1 | 353.9 | 291.1
1582 | 1392 | -6.9 | 0 | 0 | 229.2 | 208.7 | 197.1 | 192.1 | 224.9 | 44.7 | 19.1 | 67.9 | 4.1 | 213.4 | 8.5 | 337.1 | 222.1 | 83.2 | 259.1 | 791.9 | 376.2 | 212.1 | 169.9 | 227.2 | 278.1 | 219.5 | 198.7 | 250 | 227.8 | 203.1 | 261.2 | 242.8 | 353.7 | 291
1583 | 1393 | -6.9 | 0 | 0 | 229 | 208.5 | 197 | 192 | 224.6 | 44.7 | 19.1 | 67.8 | 3.4 | 222.5 | 7.7 | 335 | 221 | 83 | 257.4 | 794.7 | 375.4 | 211.8 | 169.3 | 226.9 | 277.7 | 219.4 | 198.5 | 250 | 227.5 | 202.8 | 261.1 | 242.6 | 353.4 | 290.8
1584 | 1394 | -6.9 | 0 | 0 | 228.6 | 208.4 | 197 | 191.8 | 224.4 | 44.7 | 19.1 | 67.8 | 3.7 | 205.4 | 6.1 | 333 | 221.8 | 82.7 | 255.9 | 797.5 | 374.4 | 211.5 | 169.2 | 226.7 | 277.2 | 219.2 | 198.2 | 250 | 227.3 | 202.5 | 260.9 | 242.4 | 353.2 | 290.6
1585 | 1395 | -6.9 | 0 | 0 | 228.3 | 208.2 | 196.7 | 191.6 | 224.3 | 44.7 | 19.2 | 67.7 | 3.9 | 246.6 | 5.2 | 331 | 222.9 | 82.6 | 254.1 | 799.5 | 373.3 | 210.7 | 169.5 | 226.3 | 276.2 | 219 | 197.8 | 250 | 227.1 | 202.3 | 260.7 | 242.1 | 353 | 290.5
1586 | 1396 | -6.9 | 0 | 0 | 227.5 | 208 | 196.6 | 191.5 | 224.2 | 44.7 | 19.2 | 67.6 | 4.2 | 235 | 5.4 | 329.1 | 222.8 | 82.2 | 253.1 | 800.2 | 372.2 | 210.3 | 169 | 226.2 | 275.8 | 218.9 | 197.6 | 250 | 227 | 202 | 260.6 | 241.9 | 352.7 | 290.3
1587 | 1397 | -6.9 | 0 | 0 | 227.5 | 207.4 | 196.1 | 191.2 | 224 | 44.6 | 19.2 | 67.6 | 4.5 | 234.1 | 6.6 | 327.2 | 222.3 | 82 | 252.5 | 801.5 | 371.2 | 210.2 | 169.3 | 226 | 275.2 | 218.7 | 197.3 | 250 | 226.8 | 201.8 | 260.4 | 241.6 | 352.5 | 290.4
1588 | 1398 | -6.9 | 0 | 0 | 227.4 | 207.2 | 195.9 | 191 | 223.8 | 44.5 | 19.2 | 67.5 | 4 | 230.2 | 6.4 | 325.4 | 221.7 | 81.8 | 251.3 | 802.8 | 370.4 | 210.3 | 168.8 | 225.8 | 274.6 | 218.5 | 197 | 250 | 226.7 | 201.6 | 260.2 | 241.4 | 352.3 | 290.3
1589 | 1399 | -6.9 | 0 | 0 | 227.3 | 206.9 | 195.7 | 190.8 | 223.6 | 44.5 | 19.2 | 67.4 | 3.7 | 232.7 | 7.3 | 323.5 | 222.5 | 81.5 | 249.3 | 805.1 | 369.5 | 210 | 168.6 | 225 | 273.9 | 218.3 | 196.8 | 250 | 226.5 | 201.4 | 260 | 241.2 | 352 | 290.2
1590 | 1400 | -6.9 | 0 | 0 | 226.7 | 206.8 | 195.7 | 190.7 | 223.4 | 44.5 | 19.2 | 67.4 | 4 | 239 | 9 | 321.6 | 223.5 | 81.1 | 248.9 | 805.9 | 368.5 | 209.2 | 168.2 | 224.1 | 273.1 | 218.2 | 196.5 | 250 | 226.3 | 201.2 | 259.9 | 241 | 351.8 | 290
1591 | 1401 | -6.9 | 0 | 0 | 226.6 | 206.7 | 195.4 | 190.5 | 223.3 | 44.4 | 19.2 | 67.3 | 4.3 | 239.9 | 10.4 | 319.8 | 224 | 80.7 | 247.6 | 805.7 | 367.5 | 208.5 | 168 | 222.9 | 272.4 | 218 | 196.3 | 250 | 226.1 | 200.9 | 259.7 | 240.7 | 351.6 | 290
1592 | 1402 | -6.9 | 0 | 0 | 226.6 | 206.5 | 195.2 | 190.3 | 223.3 | 44.4 | 19.2 | 67.3 | 3.9 | 240.3 | 10.5 | 317.9 | 223.2 | 80.5 | 246.7 | 806.5 | 366.5 | 207.8 | 167.3 | 222.4 | 271.9 | 217.8 | 196.1 | 250 | 225.9 | 200.6 | 259.6 | 240.4 | 351.3 | 289.8
1593 | 1403 | -6.9 | 0 | 0 | 226.6 | 206.3 | 195 | 190.1 | 223.2 | 44.4 | 19.2 | 67.2 | 3.6 | 243.2 | 10.4 | 316 | 222.9 | 80.3 | 246.4 | 806.9 | 365.6 | 206.9 | 166.7 | 221.9 | 271.2 | 217.6 | 195.8 | 250 | 225.9 | 200.4 | 259.4 | 240.2 | 351.1 | 289.7
1594 | 1404 | -6.9 | 0 | 0 | 226.6 | 206 | 194.7 | 189.9 | 222.8 | 44.4 | 19.2 | 67.1 | 3.5 | 242.9 | 9.7 | 314.1 | 222.9 | 80 | 246 | 807.2 | 364.8 | 206.5 | 165.8 | 221.9 | 270.8 | 217.4 | 195.6 | 250 | 225.9 | 200.2 | 259.2 | 240 | 350.9 | 289.6
1595 | 1405 | -6.9 | 0 | 0 | 225.5 | 206.2 | 195.1 | 190 | 222.2 | 44.5 | 19.2 | 67 | 3.2 | 225.3 | 8.4 | 312.3 | 222.5 | 79.6 | 245 | 808.7 | 364 | 206.1 | 165.4 | 221.4 | 270.1 | 217.2 | 195.4 | 250 | 225.7 | 200 | 259.1 | 239.7 | 350.7 | 289
1596 | 1406 | -6.9 | 0 | 0 | 225.7 | 205.9 | 194.5 | 189.7 | 222 | 44.4 | 19.2 | 67 | 3 | 239.9 | 7.3 | 310.5 | 222.1 | 79.2 | 244.2 | 810.6 | 363.2 | 205.8 | 165.6 | 221.3 | 269.7 | 217 | 195.2 | 250 | 225.5 | 199.8 | 258.9 | 239.5 | 350.4 | 289.1
1597 | 1407 | -6.9 | 0 | 0 | 225.4 | 205.9 | 194.4 | 189.5 | 221.9 | 44.3 | 19.2 | 66.9 | 2.7 | 241.2 | 7.9 | 308.7 | 219.2 | 78.9 | 243.3 | 812.8 | 362.4 | 206.2 | 164.9 | 221 | 269.3 | 216.8 | 194.9 | 250 | 225.3 | 199.6 | 258.8 | 239.3 | 350.2 | 288.9
1598 | 1408 | -6.9 | 0 | 0 | 225.4 | 206 | 194.1 | 189.3 | 221.7 | 44.3 | 19.2 | 66.9 | 2.8 | 241.5 | 9.9 | 306.8 | 216.6 | 78.8 | 242.1 | 814.1 | 361.6 | 206.6 | 164.4 | 221.1 | 268.8 | 216.6 | 194.6 | 250 | 225.1 | 199.4 | 258.6 | 239 | 349.9 | 288.9
1599 | 1409 | -6.9 | 0 | 0 | 225.7 | 205.8 | 193.6 | 189 | 221.5 | 44.2 | 19.2 | 66.8 | 3 | 240.4 | 10 | 304.9 | 216.6 | 78.6 | 241.6 | 815 | 360.7 | 206.7 | 163.7 | 221.3 | 268.5 | 216.4 | 194.4 | 250 | 224.8 | 199.2 | 258.5 | 238.8 | 349.7 | 289
1600 | 1410 | -6.9 | 0 | 0 | 225.5 | 205.7 | 193.5 | 188.9 | 221.3 | 44.2 | 19.2 | 66.7 | 3 | 231.1 | 9.9 | 303 | 215.9 | 78.5 | 240.7 | 816.7 | 359.8 | 206.8 | 163.2 | 221 | 268.2 | 216.2 | 194.1 | 250 | 224.6 | 199 | 258.3 | 238.6 | 349.5 | 288.8
1601 | 1411 | -6.9 | 0 | 0 | 225.5 | 205.5 | 193.1 | 188.7 | 221.2 | 44.1 | 19.2 | 66.7 | 2.7 | 238 | 9.6 | 301 | 215.9 | 78.2 | 239.8 | 818.3 | 359 | 206.1 | 163 | 220.7 | 267.8 | 216 | 193.8 | 250 | 224.4 | 198.8 | 258.2 | 238.4 | 349.3 | 288.8
1602 | 1412 | -6.9 | 0 | 0 | 225.3 | 205.5 | 192.9 | 188.6 | 221.1 | 44.1 | 19.2 | 66.6 | 2.4 | 235.2 | 9.2 | 298.9 | 217.1 | 78 | 238.4 | 820 | 358.2 | 206.1 | 162.7 | 220.7 | 267.5 | 215.8 | 193.6 | 250 | 224.2 | 198.5 | 258 | 238.2 | 349 | 288.6
1603 | 1413 | -6.9 | 0 | 0 | 225.2 | 205.5 | 192.7 | 188.4 | 220.8 | 44 | 19.2 | 66.5 | 2.7 | 236.4 | 9 | 296.9 | 217.7 | 77.7 | 237.1 | 821.9 | 357.3 | 205.9 | 162.4 | 220.3 | 266.6 | 215.5 | 193.3 | 250 | 224.1 | 198.3 | 257.9 | 237.9 | 348.8 | 288.5
1604 | 1414 | -6.9 | 0 | 0 | 225 | 205.2 | 192.6 | 188.2 | 220.5 | 44 | 19.2 | 66.4 | 2.8 | 231.2 | 8.9 | 294.9 | 217.9 | 77.6 | 236.3 | 822.2 | 356.3 | 205.1 | 162.2 | 219.8 | 265.7 | 215.3 | 193.1 | 250 | 224 | 198 | 257.7 | 237.7 | 348.6 | 288.4
1605 | 1415 | -6.9 | 0 | 0 | 224.8 | 204.8 | 192.5 | 188.1 | 220.3 | 43.9 | 19.2 | 66.4 | 3 | 223.7 | 8.5 | 292.9 | 217.7 | 77.3 | 235.9 | 822.9 | 355.5 | 204.8 | 161.8 | 219.2 | 265.1 | 215.1 | 192.9 | 250 | 223.9 | 197.7 | 257.6 | 237.4 | 348.3 | 288.2
1606 | 1416 | -6.9 | 0 | 0 | 224.6 | 204.4 | 192.4 | 187.9 | 220.2 | 43.8 | 19.2 | 66.4 | 3.4 | 224.5 | 8.5 | 290.9 | 217.4 | 77.2 | 235.6 | 824 | 354.6 | 205.1 | 161.7 | 218.8 | 264.5 | 214.9 | 192.7 | 250 | 223.8 | 197.5 | 257.4 | 237.2 | 348.1 | 288.1
1607 | 1417 | -6.9 | 0 | 0 | 224.2 | 204.2 | 192.2 | 187.7 | 220 | 43.8 | 19.2 | 66.4 | 3.1 | 236.9 | 7.6 | 289 | 217.3 | 77 | 234.9 | 824.6 | 353.9 | 205.2 | 161.4 | 218.5 | 264 | 214.7 | 192.5 | 250 | 223.7 | 197.3 | 257.3 | 237 | 347.9 | 288
1608 | 1418 | -6.9 | 0 | 0 | 223.9 | 204 | 192 | 187.6 | 219.8 | 43.7 | 19.2 | 66.3 | 3.3 | 231.6 | 6.8 | 287.1 | 216.2 | 76.8 | 234.1 | 825.5 | 353.2 | 204.9 | 160.8 | 218.1 | 263.5 | 214.5 | 192.3 | 249.9 | 223.7 | 197.1 | 257.1 | 236.7 | 347.6 | 287.9
1609 | 1419 | -6.9 | 0 | 0 | 223.8 | 203.6 | 191.7 | 187.4 | 219.6 | 43.6 | 19.2 | 66.2 | 3.4 | 236.3 | 6.6 | 285.2 | 215 | 76.5 | 233.9 | 827.2 | 352.5 | 205.1 | 160.2 | 218.2 | 263.2 | 214.3 | 192.1 | 249.9 | 223.6 | 196.9 | 256.9 | 236.5 | 347.4 | 287.8
1610 | 1420 | -6.9 | 0 | 0 | 223.5 | 203.4 | 191.6 | 187.2 | 219.5 | 43.5 | 19.2 | 66.2 | 3.2 | 252.6 | 6.7 | 283.3 | 214.6 | 76.4 | 232.9 | 829.2 | 351.7 | 205.2 | 159.8 | 218.4 | 262.8 | 214.1 | 191.9 | 250 | 223.3 | 196.7 | 256.8 | 236.3 | 347.2 | 287.7
1611 | 1421 | -6.9 | 0 | 0 | 223.1 | 203.3 | 191.4 | 187.1 | 219.2 | 43.4 | 19.2 | 66.1 | 2.9 | 244.2 | 6.4 | 281.3 | 213.5 | 76.1 | 232.1 | 830.4 | 351 | 204.7 | 159.2 | 217.6 | 262.1 | 213.9 | 191.7 | 249.9 | 223 | 196.5 | 256.6 | 236.1 | 347 | 287.5
1612 | 1422 | -6.9 | 0 | 0 | 222.8 | 203.1 | 191.2 | 186.9 | 218.9 | 43.4 | 19.2 | 66 | 3.1 | 245.8 | 6.6 | 279.4 | 213.7 | 76.1 | 231.8 | 832.1 | 350.3 | 204 | 158.4 | 217.2 | 261.4 | 213.7 | 191.5 | 249.9 | 222.8 | 196.3 | 256.5 | 235.8 | 346.7 | 287.4
1613 | 1423 | -6.9 | 0 | 0 | 222.6 | 202.8 | 191 | 186.7 | 218.6 | 43.4 | 19.2 | 65.9 | 3.2 | 252 | 7.2 | 277.6 | 214.3 | 76.1 | 231.6 | 833.2 | 349.4 | 203.7 | 157.9 | 217.2 | 261 | 213.5 | 191.3 | 249.9 | 222.6 | 196 | 256.3 | 235.7 | 346.5 | 287.3
1614 | 1424 | -6.9 | 0 | 0 | 222.5 | 202.5 | 190.8 | 186.5 | 218.4 | 43.5 | 19.2 | 65.9 | 2.7 | 258.3 | 7.4 | 275.8 | 213.7 | 75.8 | 231.6 | 834.8 | 348.8 | 204 | 157.6 | 217 | 260.7 | 213.3 | 191.1 | 249.9 | 222.4 | 195.8 | 256.2 | 235.5 | 346.3 | 287.2
1615 | 1425 | -6.9 | 0 | 0 | 222.3 | 202.2 | 190.7 | 186.3 | 218.3 | 43.4 | 19.2 | 65.8 | 2.9 | 263.1 | 8.2 | 274.1 | 212.7 | 75.5 | 231 | 835.1 | 348 | 204.2 | 157.3 | 217.1 | 260.2 | 213.2 | 190.8 | 249.9 | 222.2 | 195.7 | 256 | 235.3 | 346.1 | 287.1
1616 | 1426 | -6.9 | 0 | 0 | 222 | 202 | 190.5 | 186.1 | 218.2 | 43.3 | 19.2 | 65.8 | 2.7 | 255.9 | 7.8 | 272.4 | 209.1 | 75.3 | 231 | 834.9 | 347.3 | 204.2 | 157.2 | 217.2 | 259.7 | 213 | 190.6 | 249.9 | 222.1 | 195.5 | 255.9 | 235 | 345.8 | 287
1617 | 1427 | -6.9 | 0 | 0 | 221.7 | 201.9 | 190.3 | 185.9 | 218.1 | 43.3 | 19.2 | 65.8 | 3 | 257.5 | 6.9 | 270.8 | 206.7 | 75.1 | 231.1 | 835.1 | 346.5 | 204.6 | 157.5 | 217.3 | 259.3 | 212.8 | 190.4 | 249.9 | 222 | 195.3 | 255.7 | 234.8 | 345.6 | 286.9