## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-8
Test Date: | 2006-11-10
Ignition Time Relative to Thermal Data: | 219 | s
Ignition Time Relative to Electrical Data: | 219 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3+1 bundle in conduit at Location E - circuit did not fail
Plot for the two slug calorimeters

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 8-1 |  |  |  | Location A | Location C - 6-cable bundle 8-3 |  |  |  | Location C | Location E - 3+1 bundle 8-4 in Conduit |  |  | Location G - 6-cable bundle 8-3 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Cable 1 TC | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -219 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.7 | 292.4 | 5.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.1 | 15.9
1 | -218 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.5 | 304.3 | 6.1 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
2 | -217 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.5 | 285.9 | 7.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.5 | 16.6 | 16.1 | 15.9
3 | -216 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.9 | 296.1 | 9.3 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
4 | -215 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.4 | 285.6 | 11.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
5 | -214 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.5 | 271.2 | 14.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
6.1 | -212.9 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.7 | 257.6 | 14 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
7.1 | -211.9 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.5 | 250.2 | 13.8 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.1 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.2 | 16
8.1 | -210.9 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.8 | 249.2 | 13.3 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
9.1 | -209.9 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.3 | 240.9 | 11.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
10.1 | -208.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.4 | 245.3 | 10.6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
11.1 | -207.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.6 | 241.3 | 9.6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
12.1 | -206.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5 | 231.1 | 8.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
13.1 | -205.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.9 | 238.7 | 8.1 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
14.1 | -204.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.9 | 249.4 | 7.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
15.1 | -203.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.4 | 246.4 | 7.6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
16.1 | -202.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.8 | 245.2 | 7.4 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
17.1 | -201.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5 | 239.3 | 7.2 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
18.1 | -200.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 4.7 | 248.3 | 7.1 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
19.1 | -199.9 | -6.7 | 0 | 0 | 15.4 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 5.2 | 252.5 | 7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
20.1 | -198.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 4.2 | 253.3 | 6.8 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
21.1 | -197.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 4.5 | 254.2 | 6.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
22.1 | -196.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 5.3 | 246 | 6.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.2 | 15.9
23.1 | -195.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6 | 255.5 | 6.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
24.1 | -194.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6.2 | 254.1 | 6.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
25.1 | -193.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 5.7 | 268.4 | 6.5 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
26.1 | -192.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 277.8 | 6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
27.1 | -191.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 5.8 | 260.2 | 5.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.2 | 15.9
28.1 | -190.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 5.7 | 256.5 | 6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
29.1 | -189.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 5.8 | 262.7 | 6.1 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
30.1 | -188.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6 | 275.2 | 5.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
31.1 | -187.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 5.8 | 259.8 | 5.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
32.1 | -186.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 5.9 | 249.3 | 5.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
33.1 | -185.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.3 | 255.6 | 6.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
34.1 | -184.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 251.8 | 6.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
35.1 | -183.9 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 260.6 | 6.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
36.1 | -182.9 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.9 | 255.8 | 7.5 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
37.1 | -181.9 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.9 | 264.2 | 8.5 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
38.1 | -180.9 | -6.5 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.9 | 266.1 | 8.5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
39.1 | -179.9 | -6.5 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 7.2 | 269.4 | 8.2 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 16
40.1 | -178.9 | -6.5 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 258.7 | 7.3 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
41.1 | -177.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 7.1 | 253.3 | 7.2 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
42.1 | -176.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7.2 | 251.2 | 7.4 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
43.1 | -175.9 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 7 | 249.8 | 7.5 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
44.1 | -174.9 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7 | 249 | 7.6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
45.1 | -173.9 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 252.5 | 7.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
46.2 | -172.8 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 258.5 | 7.4 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 16
47.2 | -171.8 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 252.4 | 7.2 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 16
48.2 | -170.8 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7.5 | 251.2 | 7.1 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
49.2 | -169.8 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7.9 | 249.1 | 6.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
50.2 | -168.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7.9 | 254.8 | 6.3 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 16
51.2 | -167.8 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7 | 249.6 | 6.1 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.1 | 15.9
52.2 | -166.8 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 260.8 | 6.3 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 16
53.2 | -165.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.5 | 245.9 | 6.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
54.2 | -164.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 235.7 | 7.1 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
55.2 | -163.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.5 | 228.7 | 7.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 16
56.2 | -162.8 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7 | 235.8 | 8.2 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
57.2 | -161.8 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 243.8 | 8.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
58.2 | -160.8 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 237 | 8.5 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
59.2 | -159.8 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.5 | 238.4 | 8.1 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
60.2 | -158.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 214.4 | 7.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
61.2 | -157.8 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 224.1 | 8.1 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
62.2 | -156.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 233.9 | 8.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
63.2 | -155.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.4 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 237.2 | 8.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
64.2 | -154.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 236.3 | 9.4 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
65.2 | -153.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.7 | 231.8 | 9.7 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
66.2 | -152.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.7 | 238.3 | 10 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.7 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
67.2 | -151.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.3 | 238.4 | 9.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
68.2 | -150.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.6 | 242.8 | 9.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
69.2 | -149.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.9 | 246.4 | 9.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.1 | 15.9
70.2 | -148.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.3 | 259.5 | 9.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
71.2 | -147.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.7 | 265.4 | 9.4 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
72.2 | -146.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7 | 272 | 7.5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.5 | 16.6 | 16.2 | 15.9
73.2 | -145.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 234.4 | 5.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
74.2 | -144.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.5 | 243 | 5.4 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
75.2 | -143.8 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.2 | 263.8 | 5.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
76.2 | -142.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 247.3 | 6.6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
77.2 | -141.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 7.6 | 221.8 | 6.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
78.2 | -140.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 8.6 | 260 | 6 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
79.2 | -139.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.3 | 22 | 15.2 | 8.2 | 249.1 | 6.3 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
80.2 | -138.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 8.4 | 219.9 | 6.9 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.7 | 16.2 | 15.9
81.2 | -137.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 7.4 | 220.7 | 6.2 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
82.2 | -136.8 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.5 | 226.7 | 6.4 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.1 | 14.6 | 16.6 | 16.2 | 15.9
83.3 | -135.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 225.2 | 7.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
84.3 | -134.7 | -6.8 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.3 | 233.3 | 9.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
85.3 | -133.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.8 | 231.2 | 11.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
86.3 | -132.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6.4 | 231.4 | 12.2 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
87.3 | -131.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.3 | 22 | 15.2 | 6 | 231 | 12.2 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
88.3 | -130.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.1 | 6.1 | 233.5 | 10.7 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
89.3 | -129.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.1 | 6.3 | 238.1 | 9.6 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
90.3 | -128.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 5.9 | 234.5 | 9.2 | 15.1 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
91.3 | -127.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6.2 | 225.7 | 8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
92.3 | -126.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 6.4 | 233.7 | 6.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
93.3 | -125.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6 | 243.9 | 6.4 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
94.3 | -124.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6 | 241.9 | 6.1 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
95.3 | -123.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 6.2 | 239.8 | 5.9 | 15 | 14.7 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
96.3 | -122.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.8 | 236 | 5.6 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
97.3 | -121.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 6 | 236.6 | 5.4 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
98.3 | -120.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.3 | 232.9 | 5.2 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
99.3 | -119.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.8 | 235.4 | 5 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.7 | 16.2 | 15.9
100.3 | -118.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.1 | 5.7 | 238.8 | 5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
101.3 | -117.7 | -6.6 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 6.1 | 240.2 | 5.1 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
102.3 | -116.7 | -6.6 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 6.1 | 237.2 | 5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
103.3 | -115.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.1 | 227.7 | 4.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
104.3 | -114.7 | -6.8 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.1 | 237.4 | 5.3 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
105.3 | -113.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6.7 | 245.9 | 7.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
106.3 | -112.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.9 | 235.6 | 8.4 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
107.3 | -111.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 6.3 | 241.1 | 8.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
108.3 | -110.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 6.5 | 247.8 | 9 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
109.3 | -109.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.8 | 252.2 | 8.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
110.3 | -108.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.2 | 258.6 | 8.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
111.3 | -107.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.1 | 262.3 | 6.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
112.3 | -106.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 5 | 267.1 | 5.8 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
113.3 | -105.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.1 | 4.5 | 268.2 | 5.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
114.3 | -104.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.8 | 15.4 | 22 | 15.2 | 5 | 245.1 | 6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
115.3 | -103.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.1 | 5.1 | 271.4 | 6.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
116.3 | -102.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.1 | 5.4 | 265.5 | 5.9 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
117.3 | -101.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.4 | 244.7 | 5.7 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
118.3 | -100.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.3 | 266.9 | 6.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
119.3 | -99.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.2 | 262.6 | 6.5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
120.3 | -98.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.3 | 257.7 | 5.6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
121.3 | -97.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.1 | 259.6 | 5.3 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
122.3 | -96.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.5 | 269.4 | 5.4 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
123.3 | -95.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.8 | 15.4 | 22 | 15.2 | 5.9 | 270.9 | 5.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
124.3 | -94.7 | -6.7 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 5.1 | 265.2 | 5.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
125.3 | -93.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 4.9 | 248.8 | 5.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
126.3 | -92.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.7 | 270.2 | 6.1 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
127.3 | -91.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.5 | 268.9 | 6.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
128.3 | -90.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.7 | 264.2 | 5.6 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
129.3 | -89.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.6 | 261.4 | 5.5 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
130.3 | -88.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 5.2 | 257.6 | 5.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
131.3 | -87.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 5.1 | 257.7 | 5 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
132.3 | -86.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 5.1 | 257 | 5.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
133.3 | -85.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.9 | 255.3 | 5.3 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
134.3 | -84.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.7 | 257.8 | 4.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
135.3 | -83.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 4.3 | 258.4 | 4.2 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
136.3 | -82.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 5.1 | 245.8 | 4 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
137.3 | -81.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 4.6 | 243.6 | 4.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
138.3 | -80.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 4.6 | 252 | 5.4 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
139.3 | -79.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 4.4 | 256.2 | 6.1 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
140.3 | -78.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 5 | 258.6 | 6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
141.3 | -77.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 4.9 | 260.7 | 5.9 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
142.3 | -76.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 4.6 | 255.2 | 6.2 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
143.3 | -75.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 4.8 | 254.2 | 6.1 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
144.3 | -74.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 5.2 | 251.4 | 5.7 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
145.3 | -73.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 4.7 | 244.2 | 5.5 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
146.3 | -72.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.5 | 22 | 15.2 | 4.9 | 255.6 | 5.5 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
147.3 | -71.7 | -6.6 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.5 | 22 | 15.2 | 5.1 | 250 | 5.6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
148.3 | -70.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 5.6 | 239.6 | 5.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
149.3 | -69.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 5.3 | 235.1 | 6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
150.3 | -68.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 5.7 | 236 | 6.1 | 15 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
151.3 | -67.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 5.4 | 235.5 | 6.3 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
152.3 | -66.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.5 | 22 | 15.2 | 4.7 | 236.6 | 6 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
153.3 | -65.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 5 | 243.6 | 5.8 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
154.3 | -64.7 | -6.8 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 5.8 | 245.2 | 5.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
155.3 | -63.7 | -6.8 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 5.6 | 252.2 | 6.3 | 15.1 | 14.8 | 14.9 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
156.3 | -62.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.4 | 15.9 | 15.4 | 22 | 15.2 | 5.4 | 260 | 7.2 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
157.3 | -61.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 5.3 | 245.3 | 8.1 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
158.3 | -60.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 5.4 | 244.3 | 7.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
159.3 | -59.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 5.3 | 240.5 | 7.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
160.3 | -58.7 | -6.7 | 0 | 0 | 15.5 | 15.7 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 5.5 | 242.1 | 8.6 | 15 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
161.3 | -57.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 5.8 | 241.8 | 8.6 | 15 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
162.3 | -56.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 6.1 | 241.1 | 7.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
163.3 | -55.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 6.4 | 273.2 | 7.6 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
164.3 | -54.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 6.5 | 272.1 | 5.4 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
165.3 | -53.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 6.6 | 218.8 | 5.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
166.3 | -52.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 6.5 | 205 | 7.1 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
167.3 | -51.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 5.9 | 215.5 | 9.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
168.3 | -50.7 | -6.6 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.3 | 6.1 | 208.1 | 11.6 | 15 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
169.3 | -49.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.8 | 15.2 | 22 | 15.2 | 6.4 | 227.2 | 12.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
170.3 | -48.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 6.2 | 199.7 | 11.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
171.3 | -47.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 6.4 | 239.7 | 9.5 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
172.3 | -46.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 6.1 | 250.7 | 7.8 | 15 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
173.3 | -45.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 5.3 | 269.3 | 7.6 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
174.3 | -44.7 | -6.8 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 5.9 | 255.8 | 7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
175.3 | -43.7 | -6.8 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 6.2 | 222.3 | 7.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
176.3 | -42.7 | -6.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 5.7 | 206.1 | 8.3 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
177.3 | -41.7 | -5.7 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.3 | 5.5 | 228.5 | 9.2 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
178.3 | -40.7 | -4.2 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 6.3 | 225.5 | 8.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 14.9 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
179.3 | -39.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 6.8 | 191.9 | 7.3 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
180.3 | -38.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 7.6 | 233.7 | 7.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
181.3 | -37.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 8.3 | 202.9 | 8.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
182.3 | -36.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 8.5 | 208.3 | 9.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15.1 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
183.3 | -35.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.2 | 22 | 15.2 | 8.1 | 218.6 | 10 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
184.3 | -34.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 7.6 | 224.2 | 9.5 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
185.3 | -33.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.1 | 265 | 8.2 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
186.3 | -32.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 10 | 235.4 | 7.9 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
187.3 | -31.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 10 | 245.8 | 10.1 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
188.3 | -30.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 9.3 | 242 | 13.5 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
189.3 | -29.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.5 | 242 | 14.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
190.3 | -28.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 9.1 | 241.9 | 14.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
191.3 | -27.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.8 | 239.3 | 14.7 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
192.3 | -26.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.2 | 242.6 | 14.3 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
193.3 | -25.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 7.9 | 239.4 | 13.4 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
194.3 | -24.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8 | 233.7 | 12.4 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
195.3 | -23.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 7.4 | 236.6 | 11.8 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
196.3 | -22.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 7.1 | 224.9 | 11.2 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
197.3 | -21.7 | -6.9 | 0 | 0 | 15.4 | 15.8 | 15.5 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.7 | 232.3 | 11.9 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
198.3 | -20.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.5 | 241.6 | 12.2 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
199.3 | -19.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.3 | 22 | 15.2 | 8.4 | 242.5 | 11.9 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15.1 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
200.3 | -18.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.2 | 255.6 | 12.4 | 15.1 | 14.8 | 15 | 15.3 | 16.2 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
201.3 | -17.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.2 | 255 | 12 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
202.3 | -16.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8 | 250.1 | 11.6 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
203.3 | -15.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.2 | 251.6 | 11.4 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
204.3 | -14.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.8 | 254.1 | 10.5 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
205.3 | -13.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.7 | 260 | 10.4 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
206.3 | -12.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 8.5 | 260.4 | 11 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
207.3 | -11.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.9 | 278.8 | 9.8 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
208.3 | -10.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.8 | 264.2 | 9.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
209.3 | -9.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.7 | 256.4 | 9.8 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
210.3 | -8.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.3 | 260.2 | 10.6 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
211.3 | -7.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.2 | 248.5 | 10.4 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
212.3 | -6.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.8 | 253.2 | 9 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
213.3 | -5.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.8 | 261.5 | 7.9 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
214.3 | -4.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7 | 246 | 7.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
215.3 | -3.7 | -6.9 | 0 | 0 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 7.3 | 248 | 7.6 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
216.3 | -2.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.6 | 241.1 | 7.6 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.2 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
217.3 | -1.7 | -6.9 | 0 | 0 | 15.5 | 15.8 | 15.5 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.8 | 246.9 | 6.5 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
218.3 | -0.7 | -5.7 | 0 | 0 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.9 | 243 | 5.4 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.2 | 15.9
219.3 | 0.3 | 158.7 | 63.48 | 74.2045 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.7 | 237.1 | 4.7 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
220.3 | 1.3 | 318.7 | 127.48 | 149.0168 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.1 | 273.2 | 4.4 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
221.3 | 2.3 | 351.2 | 140.48 | 164.213 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.6 | 263.3 | 4.3 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.5 | 16.6 | 16.1 | 15.9
222.3 | 3.3 | 335.6 | 134.24 | 156.9188 | 15.4 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.6 | 242.7 | 5 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
223.3 | 4.3 | 315.2 | 126.08 | 147.3803 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.1 | 239.8 | 6.5 | 15.1 | 14.8 | 15 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.6 | 16.1 | 15.9
224.3 | 5.3 | 300.5 | 120.2 | 140.5069 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.3 | 227.1 | 7.8 | 15.1 | 14.8 | 15.1 | 15.3 | 16.3 | 15 | 14.8 | 15.3 | 14.8 | 16.2 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
225.3 | 6.3 | 290 | 116 | 135.5973 | 15.5 | 15.8 | 15.6 | 15.5 | 15.9 | 15.4 | 22 | 15.2 | 6.3 | 236.1 | 7 | 15.1 | 14.9 | 15.6 | 15.3 | 16.4 | 15 | 14.8 | 15.3 | 14.8 | 16.3 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.2 | 14.6 | 16.7 | 16.1 | 15.9
226.3 | 7.3 | 287.9 | 115.16 | 134.6154 | 15.5 | 15.8 | 15.6 | 15.6 | 15.9 | 15.5 | 22 | 15.2 | 6.7 | 254.4 | 6.2 | 15.1 | 15.8 | 19.5 | 15.3 | 16.7 | 15.1 | 15.1 | 15.8 | 14.8 | 16.4 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.3 | 14.6 | 16.7 | 16.1 | 15.9
227.3 | 8.3 | 289.1 | 115.64 | 135.1765 | 15.5 | 15.8 | 15.6 | 15.6 | 16.4 | 15.5 | 22 | 15.2 | 6.7 | 260.5 | 6 | 15.1 | 18.1 | 23.9 | 15.3 | 17 | 15.1 | 16.3 | 17.6 | 14.9 | 16.7 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.3 | 14.6 | 16.7 | 16.1 | 15.9
228.3 | 9.3 | 283.7 | 113.48 | 132.6516 | 15.6 | 15.9 | 15.7 | 15.7 | 17.5 | 15.5 | 22 | 15.2 | 6.6 | 248.3 | 6.2 | 15.1 | 21.2 | 32.3 | 15.3 | 17.9 | 15.1 | 18.8 | 20.7 | 14.9 | 17.3 | 14.8 | 14.8 | 16.2 | 15.1 | 15 | 15.3 | 14.6 | 16.7 | 16.2 | 15.9
229.3 | 10.3 | 277.2 | 110.88 | 129.6123 | 15.6 | 15.9 | 15.7 | 15.8 | 21.3 | 15.5 | 22 | 15.2 | 6.8 | 247.7 | 6.6 | 15.1 | 26.6 | 49.3 | 15.4 | 19.4 | 15.1 | 23.7 | 24.3 | 14.9 | 18.4 | 14.8 | 14.8 | 16.2 | 15.1 | 15.1 | 15.4 | 14.6 | 16.8 | 16.2 | 16
230.3 | 11.3 | 272.9 | 109.16 | 127.6018 | 15.8 | 15.9 | 15.8 | 16.1 | 27.2 | 15.6 | 22 | 15.2 | 6.6 | 266 | 6.7 | 15.1 | 33.6 | 69 | 15.4 | 20.9 | 15.1 | 28.7 | 29.7 | 14.9 | 19.4 | 14.8 | 14.8 | 16.2 | 15.1 | 15.1 | 15.4 | 14.6 | 16.8 | 16.2 | 16
231.3 | 12.3 | 271.8 | 108.72 | 127.0874 | 15.9 | 16 | 16.4 | 16.7 | 31.1 | 15.6 | 22 | 15.2 | 6 | 245.9 | 6.6 | 15.1 | 39.7 | 83.4 | 15.5 | 22.1 | 15.1 | 33.4 | 34 | 14.9 | 20 | 14.8 | 14.8 | 16.2 | 15.1 | 15.3 | 15.5 | 14.6 | 16.9 | 16.2 | 16
232.3 | 13.3 | 270.8 | 108.32 | 126.6198 | 16 | 16.2 | 18.2 | 17.3 | 36.4 | 15.6 | 22 | 15.2 | 6.1 | 251.2 | 6.7 | 15.1 | 48.2 | 102 | 15.5 | 24.8 | 15.1 | 40.2 | 39.7 | 14.9 | 21.7 | 14.8 | 14.8 | 16.3 | 15.1 | 15.5 | 15.7 | 14.6 | 17 | 16.2 | 16
233.3 | 14.3 | 271 | 108.4 | 126.7134 | 16.1 | 16.5 | 20.2 | 18.1 | 43.3 | 15.6 | 22 | 15.2 | 5.9 | 242.2 | 6.2 | 15.1 | 59.9 | 133.3 | 15.6 | 27.3 | 15.1 | 48.3 | 51.9 | 15 | 23.4 | 14.8 | 14.8 | 16.3 | 15.2 | 15.7 | 16.2 | 14.6 | 17.1 | 16.3 | 16
234.3 | 15.3 | 271.4 | 108.56 | 126.9004 | 16.3 | 16.8 | 22 | 18.9 | 49 | 15.6 | 22 | 15.2 | 6.2 | 237.3 | 6.1 | 15.1 | 82.6 | 192.5 | 15.7 | 30.4 | 15.1 | 61 | 65.5 | 15 | 25.9 | 14.8 | 14.8 | 16.4 | 15.2 | 16.6 | 16.5 | 14.5 | 17.2 | 16.3 | 16
235.3 | 16.3 | 271.5 | 108.6 | 126.9471 | 16.5 | 17.2 | 24.3 | 20 | 62.6 | 15.6 | 22 | 15.2 | 6.2 | 247.2 | 5.9 | 15.2 | 120.1 | 254.8 | 15.8 | 34.5 | 15.1 | 78.8 | 94.9 | 15.1 | 29.7 | 14.8 | 14.8 | 16.4 | 15.2 | 17.8 | 16.9 | 14.6 | 17.4 | 16.3 | 16
236.3 | 17.3 | 271.5 | 108.6 | 126.9471 | 16.8 | 17.8 | 26.4 | 21.9 | 71.6 | 15.6 | 22 | 15.2 | 6.6 | 256.3 | 5.9 | 15.3 | 143.8 | 285.5 | 15.9 | 39.7 | 15.1 | 89.6 | 110 | 15.1 | 31.3 | 14.8 | 14.8 | 16.5 | 15.2 | 18.8 | 17.3 | 14.6 | 17.6 | 16.4 | 16.1
237.3 | 18.3 | 271.8 | 108.72 | 127.0874 | 17.5 | 18.6 | 29.2 | 24.2 | 78.4 | 15.6 | 22 | 15.2 | 7 | 245 | 5.8 | 15.4 | 170.2 | 333 | 15.9 | 45.4 | 15.1 | 102.3 | 131.7 | 15.2 | 34.3 | 14.8 | 14.8 | 16.5 | 15.2 | 20.4 | 17.9 | 14.6 | 17.7 | 16.4 | 16.1
238.3 | 19.3 | 273.1 | 109.24 | 127.6953 | 18.7 | 19.8 | 31.9 | 25.9 | 88.6 | 15.7 | 22 | 15.2 | 7 | 224.3 | 6 | 15.5 | 196.6 | 362.1 | 16 | 48.5 | 15.1 | 115.1 | 141.2 | 15.3 | 36.4 | 14.8 | 14.8 | 16.6 | 15.2 | 22.6 | 19 | 14.6 | 17.9 | 16.5 | 16.2
239.3 | 20.3 | 273.5 | 109.4 | 127.8823 | 20.4 | 21.3 | 34.3 | 28.2 | 100.5 | 15.7 | 22 | 15.2 | 7.4 | 208.3 | 6.3 | 15.7 | 217.5 | 380.5 | 16.1 | 52.3 | 15.1 | 129.1 | 159.9 | 15.4 | 39.2 | 14.8 | 14.8 | 16.7 | 15.3 | 25.5 | 20.6 | 14.6 | 18.1 | 16.6 | 16.2
240.3 | 21.3 | 273.5 | 109.4 | 127.8823 | 22.6 | 22.8 | 37 | 31.9 | 107.1 | 15.7 | 22 | 15.2 | 7.3 | 247.4 | 5.4 | 15.9 | 237.3 | 400.3 | 16.2 | 56.3 | 15.1 | 136.6 | 173.5 | 15.5 | 42.2 | 14.8 | 14.8 | 16.8 | 15.3 | 30.8 | 22.4 | 14.6 | 18.4 | 16.7 | 16.3
241.3 | 22.3 | 273.3 | 109.32 | 127.7888 | 24.5 | 24.3 | 39.7 | 35.6 | 108.4 | 15.7 | 22 | 15.2 | 7.6 | 223 | 5.2 | 16.1 | 245.7 | 416.8 | 16.3 | 62.2 | 15.1 | 139.7 | 173.1 | 15.6 | 43.7 | 14.8 | 14.8 | 16.9 | 15.4 | 36.4 | 24.6 | 14.6 | 18.7 | 16.7 | 16.5
242.3 | 23.3 | 274.5 | 109.8 | 128.3499 | 26 | 26.3 | 42.5 | 38.6 | 111.6 | 15.8 | 22 | 15.2 | 7.8 | 247.3 | 6.5 | 16.4 | 265.6 | 451.2 | 16.4 | 69.6 | 15.1 | 150 | 193.3 | 15.7 | 46.4 | 14.8 | 14.8 | 16.9 | 15.4 | 40.5 | 26.7 | 14.6 | 19 | 16.8 | 16.7
243.3 | 24.3 | 274.6 | 109.84 | 128.3966 | 28.7 | 28.7 | 45.4 | 41.6 | 120.7 | 15.8 | 22 | 15.3 | 7 | 219.4 | 7 | 16.6 | 284.3 | 472.3 | 16.4 | 74.5 | 15.1 | 160.6 | 211.5 | 15.8 | 49.3 | 14.8 | 14.8 | 16.9 | 15.5 | 45.6 | 29.3 | 14.7 | 19.4 | 16.9 | 16.8
244.3 | 25.3 | 274.5 | 109.8 | 128.3499 | 30.9 | 30.9 | 48.2 | 44.9 | 126.6 | 15.9 | 22 | 15.3 | 6.9 | 250.3 | 6.5 | 16.9 | 306.3 | 496.4 | 17.1 | 79.1 | 15.1 | 171.5 | 222.4 | 16 | 52.3 | 14.8 | 14.8 | 17 | 15.5 | 49.3 | 31.7 | 14.6 | 20 | 17 | 16.9
245.3 | 26.3 | 274.6 | 109.84 | 128.3966 | 33.1 | 33.1 | 51 | 48.4 | 135 | 15.9 | 22 | 15.3 | 7.7 | 250 | 6.7 | 17.3 | 330.5 | 515.4 | 18.4 | 83.2 | 15.1 | 180.6 | 246.3 | 16.1 | 56.1 | 14.8 | 14.8 | 17.1 | 15.6 | 53.9 | 33.6 | 14.6 | 20.4 | 17.1 | 17.1
246.3 | 27.3 | 275.8 | 110.32 | 128.9577 | 34.7 | 35.8 | 54.2 | 52 | 145 | 15.9 | 22 | 15.4 | 7.6 | 243.2 | 9.2 | 17.7 | 343 | 523.3 | 19.7 | 87.7 | 15.2 | 190.2 | 261 | 16.2 | 59.8 | 14.8 | 14.8 | 17.1 | 15.7 | 57.4 | 35.6 | 14.7 | 20.7 | 17.2 | 17.3
247.3 | 28.3 | 276.9 | 110.76 | 129.4721 | 36.8 | 38.9 | 57.6 | 55.9 | 147.5 | 16 | 22 | 15.4 | 9 | 237.6 | 9.9 | 18.2 | 349.3 | 534.1 | 20.9 | 91.8 | 15.2 | 193.2 | 257.4 | 16.4 | 62 | 14.8 | 14.8 | 17.3 | 15.7 | 58.1 | 37.5 | 14.7 | 21 | 17.4 | 17.4
248.3 | 29.3 | 277.1 | 110.84 | 129.5656 | 39.6 | 41.9 | 60.8 | 59.5 | 146.5 | 16 | 22 | 15.5 | 8.4 | 244.3 | 9.6 | 18.7 | 362.3 | 546 | 21.9 | 96.3 | 15.2 | 195.2 | 266 | 16.5 | 64.6 | 14.8 | 14.8 | 17.4 | 15.9 | 60.9 | 38.9 | 14.7 | 21.2 | 17.5 | 17.5
249.3 | 30.3 | 277 | 110.8 | 129.5188 | 42.1 | 44.2 | 64.2 | 62.3 | 151.3 | 16.1 | 22 | 15.6 | 8.4 | 243.8 | 10.5 | 19.3 | 367.3 | 548.8 | 23 | 97.9 | 15.3 | 198.9 | 266.4 | 16.7 | 67.2 | 14.8 | 14.8 | 17.4 | 15.9 | 64.5 | 40.8 | 14.7 | 21.7 | 17.6 | 17.7
250.3 | 31.3 | 277.3 | 110.92 | 129.6591 | 44.4 | 45.9 | 67.7 | 65.2 | 152.7 | 16.1 | 22 | 15.8 | 8.7 | 238.5 | 11.1 | 19.9 | 389.9 | 559.3 | 25.2 | 99.5 | 15.3 | 208.9 | 288.6 | 16.9 | 70.2 | 14.8 | 14.8 | 17.6 | 16 | 68.5 | 42.9 | 14.7 | 22 | 17.8 | 17.8
251.3 | 32.3 | 278.2 | 111.28 | 130.0799 | 46.6 | 48.2 | 70.5 | 68.6 | 159.6 | 16.1 | 22 | 16 | 8.8 | 239.5 | 11.2 | 20.6 | 400.4 | 564.8 | 27 | 101.7 | 15.3 | 215.8 | 296.6 | 17 | 73 | 14.8 | 14.9 | 17.7 | 16.1 | 73.4 | 44.9 | 14.7 | 22.3 | 17.9 | 18
252.3 | 33.3 | 279.5 | 111.8 | 130.6878 | 49.4 | 50.2 | 73.1 | 71.3 | 163.4 | 16.2 | 22 | 16.3 | 8.3 | 240 | 10.2 | 21.4 | 410.1 | 575.6 | 28.7 | 104.3 | 15.4 | 220.3 | 300.5 | 17.2 | 75.4 | 14.8 | 14.9 | 17.7 | 16.3 | 76.3 | 47 | 14.7 | 22.9 | 18 | 18.2
253.3 | 34.3 | 279.1 | 111.64 | 130.5007 | 51.9 | 53 | 75.5 | 74.1 | 163.5 | 16.2 | 22 | 16.6 | 8.4 | 251.7 | 9.9 | 22.2 | 411.5 | 577.7 | 29.9 | 106.2 | 15.5 | 225 | 298.7 | 17.4 | 76.7 | 14.8 | 14.9 | 17.8 | 16.4 | 79.1 | 48.6 | 14.8 | 23.3 | 18.2 | 18.4
254.3 | 35.3 | 278.2 | 111.28 | 130.0799 | 54.5 | 56.1 | 78.1 | 76.9 | 165 | 16.3 | 22 | 16.9 | 8.6 | 226 | 10.1 | 23.2 | 426.9 | 589.2 | 31.2 | 109.8 | 15.5 | 230.2 | 306.2 | 17.6 | 79.7 | 14.8 | 14.9 | 17.9 | 16.5 | 84 | 50.8 | 14.7 | 23.7 | 18.4 | 18.6
255.3 | 36.3 | 279.2 | 111.68 | 130.5475 | 58.1 | 57.9 | 80.7 | 80.1 | 175.2 | 16.3 | 22 | 17.3 | 8.6 | 220.2 | 9.8 | 24.2 | 441.2 | 603.6 | 33.2 | 113.7 | 15.6 | 240.1 | 316 | 17.8 | 83.1 | 14.8 | 14.9 | 18.1 | 16.6 | 87.2 | 53.4 | 14.8 | 24.2 | 18.5 | 18.8
256.3 | 37.3 | 279.3 | 111.72 | 130.5942 | 60.3 | 59.5 | 83.4 | 83.8 | 178.4 | 16.4 | 22 | 17.6 | 8.6 | 228.2 | 11.3 | 25.3 | 452.5 | 607.2 | 35.6 | 116.3 | 15.7 | 247.6 | 323.6 | 18.1 | 86.4 | 14.8 | 14.9 | 18.2 | 16.7 | 89.3 | 55.3 | 14.8 | 24.5 | 18.6 | 18.9
257.3 | 38.3 | 279.1 | 111.64 | 130.5007 | 62.1 | 61.2 | 86.6 | 86.4 | 180.7 | 16.4 | 22 | 18.1 | 7.3 | 232.7 | 12.3 | 26.5 | 452.7 | 605 | 36.9 | 118.2 | 15.8 | 248.8 | 318.2 | 18.3 | 88.5 | 14.8 | 14.9 | 18.2 | 16.9 | 91.4 | 57.3 | 14.8 | 24.8 | 18.8 | 19.1
258.3 | 39.3 | 280.7 | 112.28 | 131.2489 | 65.8 | 63.4 | 89.9 | 88.4 | 180.9 | 16.4 | 22 | 18.5 | 7.1 | 246.4 | 13 | 27.7 | 447.3 | 595.9 | 37.9 | 119.9 | 15.9 | 248.4 | 319.1 | 18.5 | 90.2 | 14.8 | 14.9 | 18.3 | 17 | 93.6 | 59.2 | 14.8 | 25.1 | 19 | 19.3
259.3 | 40.3 | 281.2 | 112.48 | 131.4826 | 69.5 | 65 | 92.6 | 90.4 | 182 | 16.5 | 22 | 18.9 | 6.8 | 249.7 | 12.7 | 29.1 | 448.9 | 598 | 38.8 | 122.8 | 16 | 248.5 | 315.3 | 18.7 | 92.3 | 14.8 | 15 | 18.3 | 17.1 | 96.3 | 61.2 | 14.8 | 25.6 | 19.1 | 19.4
260.3 | 41.3 | 281.3 | 112.52 | 131.5294 | 73 | 67 | 95.4 | 92.6 | 183.6 | 16.5 | 22 | 19.3 | 7 | 247.1 | 12 | 30.8 | 453.9 | 598.1 | 40.4 | 125.7 | 16.1 | 251.5 | 317.8 | 19 | 94.1 | 14.8 | 15 | 18.5 | 17.3 | 97.5 | 62.6 | 14.9 | 26.1 | 19.3 | 19.6
261.3 | 42.3 | 281.1 | 112.44 | 131.4359 | 75.2 | 69.5 | 98 | 94.4 | 185 | 16.5 | 22 | 19.6 | 7.2 | 255 | 11.6 | 32 | 466.9 | 602.9 | 43 | 128.8 | 16.2 | 258.8 | 333.6 | 19.3 | 97.5 | 14.8 | 15 | 18.7 | 17.4 | 99.2 | 63.8 | 14.9 | 26.4 | 19.5 | 19.8
262.3 | 43.3 | 281.8 | 112.72 | 131.7632 | 78.2 | 71 | 99.8 | 96.3 | 192.5 | 16.6 | 22 | 20 | 7.3 | 251.3 | 10.6 | 33.4 | 481.2 | 614.2 | 44.8 | 131.5 | 16.3 | 266.9 | 343.9 | 19.7 | 100 | 14.8 | 15 | 18.8 | 17.6 | 100.4 | 65.7 | 14.9 | 26.8 | 19.7 | 19.9
263.3 | 44.3 | 282.3 | 112.92 | 131.997 | 80 | 71.9 | 101.9 | 97.9 | 201 | 16.6 | 22 | 20.3 | 7 | 242.8 | 9.8 | 35 | 487.5 | 611.4 | 46.4 | 132.5 | 16.5 | 273.5 | 347.9 | 20.1 | 103.1 | 14.8 | 15 | 18.9 | 17.7 | 102.8 | 67.6 | 14.9 | 27.1 | 19.9 | 20.1
264.3 | 45.3 | 282 | 112.8 | 131.8567 | 81.5 | 72.9 | 103.8 | 99.5 | 199.8 | 16.6 | 22 | 20.6 | 7 | 244.1 | 11 | 36.8 | 480.6 | 598.7 | 46 | 134.3 | 16.6 | 271.2 | 342.3 | 20.5 | 103.1 | 14.8 | 15 | 19 | 17.9 | 104.2 | 69.3 | 15 | 27.5 | 20.1 | 20.3
265.3 | 46.3 | 283.1 | 113.24 | 132.371 | 84.4 | 75.6 | 105.8 | 102 | 200.1 | 16.6 | 22 | 21 | 6.6 | 240.8 | 11.3 | 38.6 | 484.3 | 609 | 47.1 | 136.3 | 16.8 | 272.3 | 342.5 | 21 | 104.7 | 14.8 | 15 | 19.1 | 18 | 104.6 | 70.9 | 15 | 27.8 | 20.3 | 20.5
266.3 | 47.3 | 283.8 | 113.52 | 132.6983 | 87.8 | 78.2 | 107.8 | 103.9 | 202.1 | 16.7 | 22 | 21.3 | 6.6 | 241.1 | 12.2 | 40.5 | 474.4 | 608.9 | 47.8 | 139.4 | 17 | 270.7 | 338.9 | 21.4 | 106.1 | 14.8 | 15.1 | 19.2 | 18.2 | 108.2 | 72.4 | 15 | 28.1 | 20.4 | 20.6
267.3 | 48.3 | 283.4 | 113.36 | 132.5113 | 89.9 | 80.6 | 109.4 | 105.7 | 202.5 | 16.7 | 22 | 21.5 | 6.1 | 241.9 | 12.1 | 42.5 | 472.4 | 612.3 | 48.8 | 143 | 17.2 | 269.8 | 339.9 | 21.8 | 107.4 | 14.8 | 15.1 | 19.3 | 18.3 | 109.8 | 74.3 | 15.1 | 28.6 | 20.6 | 20.9
268.3 | 49.3 | 283.2 | 113.28 | 132.4178 | 91.7 | 82.8 | 111.6 | 107.6 | 206.4 | 16.7 | 22 | 21.8 | 6.8 | 247.1 | 11.6 | 44.7 | 469.1 | 611.1 | 49.6 | 147.4 | 17.4 | 269.5 | 343.2 | 22.1 | 109.6 | 14.8 | 15.1 | 19.5 | 18.5 | 112.6 | 75.8 | 15.1 | 29 | 20.8 | 21
269.3 | 50.3 | 283.4 | 113.36 | 132.5113 | 92.1 | 84.4 | 113.8 | 109.3 | 207.1 | 16.8 | 22 | 22 | 7.8 | 246.5 | 10.7 | 46.9 | 467.9 | 612.2 | 51.3 | 152.6 | 17.7 | 272.7 | 348.3 | 22.5 | 111.4 | 14.8 | 15.1 | 19.6 | 18.6 | 113.8 | 77.4 | 15.1 | 29.5 | 20.9 | 21.2
270.3 | 51.3 | 284.5 | 113.8 | 133.0256 | 93.2 | 85.3 | 115.7 | 110.8 | 209.4 | 16.8 | 22 | 22.2 | 7.1 | 253.5 | 9.7 | 48.6 | 466.1 | 609.8 | 54.4 | 154.7 | 17.9 | 274.1 | 345.1 | 22.9 | 114.1 | 14.8 | 15.2 | 19.7 | 18.8 | 115.6 | 78.4 | 15.2 | 29.7 | 21.1 | 21.4
271.3 | 52.3 | 284.6 | 113.84 | 133.0724 | 94.1 | 87.1 | 117.9 | 112.2 | 210.5 | 16.9 | 22 | 22.4 | 6.9 | 289.5 | 8.1 | 50.5 | 476.6 | 610.3 | 57.2 | 156.8 | 18.2 | 280.9 | 358.1 | 23.3 | 120.9 | 14.8 | 15.2 | 19.9 | 19 | 117.3 | 79.7 | 15.2 | 30.2 | 21.3 | 21.6
272.3 | 53.3 | 284.4 | 113.76 | 132.9789 | 94.6 | 89.2 | 119.5 | 113.5 | 214 | 16.9 | 22 | 22.6 | 7 | 242 | 6.9 | 52.3 | 484.1 | 622.7 | 60.4 | 159.4 | 18.5 | 285.7 | 372.9 | 23.7 | 125.1 | 14.8 | 15.2 | 20 | 19.1 | 119.5 | 81.6 | 15.2 | 30.9 | 21.6 | 21.8
273.3 | 54.3 | 284.3 | 113.72 | 132.9321 | 95.1 | 91.5 | 120.6 | 114.7 | 213.6 | 16.9 | 22 | 22.8 | 6.8 | 251.7 | 7.3 | 54.2 | 486.5 | 621.7 | 63.9 | 162.9 | 18.8 | 286.1 | 369.6 | 24.1 | 127.4 | 14.8 | 15.2 | 20.1 | 19.3 | 119.7 | 83.9 | 15.3 | 31.5 | 21.9 | 22
274.3 | 55.3 | 286 | 114.4 | 133.727 | 95.7 | 93.3 | 122.2 | 115.9 | 213 | 16.9 | 22 | 23 | 6.5 | 253.3 | 8.6 | 56.2 | 495.6 | 624.4 | 67.9 | 166.2 | 19.1 | 289.1 | 374 | 24.5 | 131.8 | 14.8 | 15.3 | 20.1 | 19.5 | 119.6 | 85.2 | 15.3 | 31.9 | 22.2 | 22.2
275.3 | 56.3 | 286.7 | 114.68 | 134.0543 | 96.5 | 95.3 | 123.2 | 116.9 | 214.4 | 16.9 | 22 | 23.2 | 6.8 | 251.3 | 8.7 | 58.7 | 502.7 | 628 | 73.1 | 169.7 | 19.4 | 291 | 372.7 | 24.9 | 133.9 | 14.8 | 15.3 | 20.1 | 19.6 | 119.9 | 85.8 | 15.3 | 32.2 | 22.4 | 22.3
276.3 | 57.3 | 286.6 | 114.64 | 134.0076 | 98.6 | 97.1 | 123.9 | 117.4 | 214.8 | 16.9 | 22 | 23.3 | 6.7 | 252.8 | 8.5 | 62.3 | 505.3 | 626.7 | 78.8 | 170.5 | 19.7 | 290.8 | 371.7 | 25.3 | 134.9 | 14.8 | 15.3 | 20.2 | 19.8 | 120.2 | 86.6 | 15.4 | 32.7 | 22.7 | 22.4
277.3 | 58.3 | 286 | 114.4 | 133.727 | 100.9 | 98.7 | 124.8 | 117.8 | 214 | 17 | 22 | 23.5 | 7.1 | 245 | 8.4 | 63.9 | 507.8 | 627.9 | 82.5 | 171.8 | 20 | 290.3 | 375.9 | 25.7 | 136 | 14.8 | 15.3 | 20.3 | 20 | 120.4 | 87.3 | 15.4 | 33.1 | 22.9 | 22.5
278.3 | 59.3 | 285.9 | 114.36 | 133.6803 | 103.5 | 100 | 125.7 | 118.9 | 211.8 | 17 | 22 | 23.7 | 7.4 | 256.8 | 7.4 | 65.7 | 498 | 610.6 | 84.1 | 173.5 | 20.3 | 288.7 | 370.6 | 26.1 | 136.5 | 14.8 | 15.4 | 20.4 | 20.1 | 120.6 | 88.1 | 15.4 | 33.3 | 23.1 | 22.6
279.3 | 60.3 | 287.5 | 115 | 134.4284 | 105.6 | 101.4 | 126.5 | 120.1 | 208.7 | 17 | 22 | 23.9 | 7.2 | 246.7 | 7.6 | 67.7 | 492.4 | 607.1 | 88.4 | 177 | 20.7 | 286.9 | 365.8 | 26.5 | 137.9 | 14.8 | 15.4 | 20.5 | 20.3 | 120.8 | 88.7 | 15.5 | 33.6 | 23.3 | 22.7
280.3 | 61.3 | 287.7 | 115.08 | 134.5219 | 107.4 | 102.4 | 127.1 | 121.5 | 208.1 | 17 | 22 | 24.1 | 7.6 | 277.7 | 7.3 | 69.7 | 495.1 | 608 | 91.8 | 180 | 21 | 287.9 | 368.8 | 26.8 | 141 | 14.8 | 15.4 | 20.7 | 20.5 | 121.5 | 89.6 | 15.5 | 33.9 | 23.4 | 22.8
281.3 | 62.3 | 288.2 | 115.28 | 134.7557 | 108.4 | 103.1 | 127.8 | 122.7 | 207.1 | 17 | 22 | 24.2 | 7.8 | 254.7 | 6.2 | 71.7 | 490.8 | 603.6 | 95.9 | 181.9 | 21.4 | 285.8 | 361.7 | 27.2 | 141.4 | 14.8 | 15.5 | 20.7 | 20.7 | 122.2 | 90.8 | 15.6 | 34.3 | 23.6 | 23
282.3 | 63.3 | 287.6 | 115.04 | 134.4751 | 108.9 | 103.8 | 128.8 | 123.5 | 206.5 | 17 | 21.9 | 24.4 | 7.3 | 261.9 | 6.2 | 73.9 | 484.2 | 601.8 | 101.3 | 183.3 | 21.8 | 284.9 | 361.5 | 27.6 | 142.5 | 14.8 | 15.5 | 20.9 | 20.8 | 122.7 | 91.9 | 15.6 | 34.6 | 23.8 | 23.1
283.3 | 64.3 | 287.9 | 115.16 | 134.6154 | 109.1 | 104.9 | 129.5 | 123.6 | 207.9 | 17 | 21.9 | 24.5 | 6.9 | 259.4 | 7.1 | 76.1 | 481.4 | 592.1 | 105.5 | 184.1 | 22.1 | 284.9 | 361.7 | 28 | 144.2 | 14.8 | 15.5 | 21.1 | 21 | 123.2 | 92.3 | 15.6 | 34.9 | 24 | 23.2
284.3 | 65.3 | 289.1 | 115.64 | 135.1765 | 109.1 | 105.3 | 130.7 | 124.4 | 209.5 | 17.1 | 21.9 | 24.7 | 6.6 | 264 | 7.8 | 78.2 | 477 | 588.3 | 109.8 | 185.2 | 22.5 | 283.6 | 356.1 | 28.3 | 145.4 | 14.8 | 15.5 | 21.2 | 21.2 | 123.4 | 92.7 | 15.7 | 35.2 | 24.2 | 23.3
285.3 | 66.3 | 287.6 | 115.04 | 134.4751 | 110 | 106.1 | 131.8 | 125.2 | 209.3 | 17.1 | 21.9 | 24.8 | 6.4 | 268 | 8.3 | 80.5 | 474 | 593.2 | 113.2 | 187.7 | 22.8 | 284.8 | 354.4 | 28.7 | 147.9 | 14.8 | 15.6 | 21.2 | 21.3 | 123.7 | 93 | 15.8 | 35.6 | 24.4 | 23.4
286.3 | 67.3 | 286.7 | 114.68 | 134.0543 | 112.5 | 106.8 | 132.8 | 126 | 206.4 | 17.1 | 21.9 | 24.9 | 5.6 | 255.3 | 8.4 | 82.5 | 470.1 | 595 | 115.9 | 191.3 | 23.2 | 282.7 | 344.1 | 29.1 | 149.2 | 14.8 | 15.6 | 21.2 | 21.5 | 123.9 | 93.6 | 15.8 | 35.9 | 24.6 | 23.5
287.3 | 68.3 | 286.6 | 114.64 | 134.0076 | 113.6 | 106.9 | 133.8 | 126.3 | 204.7 | 17.1 | 21.9 | 25 | 6.5 | 264.2 | 8 | 84.4 | 476.4 | 599.8 | 118.7 | 193.8 | 23.6 | 282.8 | 346.7 | 29.4 | 151.4 | 14.8 | 15.7 | 21.4 | 21.6 | 124.6 | 94.6 | 15.8 | 36.2 | 24.7 | 23.7
288.3 | 69.3 | 286.9 | 114.76 | 134.1478 | 113.3 | 107.7 | 134.6 | 126.4 | 205.1 | 17.1 | 21.9 | 25.2 | 6.2 | 235 | 7.5 | 86.7 | 474.5 | 594.8 | 122.2 | 197.4 | 24 | 282.3 | 347 | 29.8 | 153.6 | 14.8 | 15.7 | 21.5 | 21.8 | 125 | 95.7 | 15.9 | 36.7 | 24.9 | 23.8
289.3 | 70.3 | 287.1 | 114.84 | 134.2413 | 113.7 | 108.7 | 135.6 | 127 | 204.6 | 17.1 | 21.9 | 25.4 | 7.3 | 259.7 | 7.1 | 88.8 | 482.2 | 602.7 | 127.8 | 203.2 | 24.3 | 285.2 | 345.9 | 30.1 | 158.3 | 14.8 | 15.7 | 21.6 | 21.9 | 125.5 | 96.5 | 15.9 | 37 | 25.1 | 23.9
290.3 | 71.3 | 286.9 | 114.76 | 134.1478 | 114.2 | 109.4 | 136.5 | 127.6 | 208.9 | 17.1 | 21.9 | 25.6 | 7.4 | 264.7 | 6.5 | 90.5 | 489.3 | 604.6 | 134.1 | 205.5 | 24.7 | 290.5 | 350 | 30.6 | 162.2 | 14.8 | 15.8 | 21.9 | 22.1 | 126.3 | 97.5 | 16 | 37.3 | 25.4 | 24.1
291.3 | 72.3 | 287.6 | 115.04 | 134.4751 | 113.8 | 110.7 | 137.3 | 126.9 | 213.9 | 17.1 | 21.9 | 25.8 | 7 | 252 | 6.1 | 92.3 | 493.3 | 603.2 | 138.7 | 207.1 | 25.1 | 295.6 | 355.5 | 31 | 164.8 | 14.8 | 15.8 | 22 | 22.3 | 126.4 | 98.5 | 16 | 37.6 | 25.6 | 24.2
292.3 | 73.3 | 287.8 | 115.12 | 134.5686 | 113.6 | 111.9 | 138 | 126.3 | 216 | 17.1 | 21.9 | 26 | 7.2 | 221.9 | 6 | 94.5 | 499.1 | 599.4 | 143.4 | 208.5 | 25.5 | 301.5 | 355.6 | 31.5 | 167.4 | 14.8 | 15.9 | 22.2 | 22.4 | 126.6 | 99 | 16.1 | 38 | 25.9 | 24.3
293.3 | 74.3 | 287.1 | 114.84 | 134.2413 | 113.4 | 112.2 | 138.7 | 126.4 | 219 | 17.1 | 21.9 | 26.1 | 7.6 | 238.8 | 6.2 | 97.3 | 502.7 | 591.8 | 146.9 | 209.9 | 25.9 | 305.8 | 361 | 32.1 | 169.6 | 14.8 | 15.9 | 22.2 | 22.6 | 127 | 99.4 | 16.1 | 38.3 | 26.1 | 24.5
294.3 | 75.3 | 288.9 | 115.56 | 135.083 | 114.3 | 112.8 | 139.6 | 127.1 | 218.8 | 17.1 | 21.9 | 26.2 | 7.1 | 272.5 | 6.5 | 100.5 | 510.9 | 597 | 153.9 | 211.6 | 26.3 | 310.5 | 375 | 32.6 | 173.2 | 14.8 | 15.9 | 22.2 | 22.7 | 127.1 | 99.9 | 16.2 | 38.6 | 26.4 | 24.6
295.3 | 76.3 | 290.7 | 116.28 | 135.9246 | 114.9 | 114.1 | 140.5 | 127 | 224.6 | 17.2 | 21.9 | 26.3 | 6.3 | 250.6 | 6.1 | 104 | 519.8 | 601 | 161.6 | 213.5 | 26.7 | 315.7 | 376.7 | 33.1 | 177 | 14.8 | 16 | 22.4 | 22.9 | 127.3 | 100.4 | 16.2 | 38.9 | 26.6 | 24.7
296.3 | 77.3 | 291.3 | 116.52 | 136.2052 | 115.1 | 114.8 | 141.5 | 126.9 | 226.6 | 17.2 | 21.9 | 26.4 | 7.6 | 249.4 | 6.1 | 107.5 | 522.1 | 592.3 | 164.8 | 215.7 | 27.1 | 319.1 | 375.5 | 33.6 | 180 | 14.8 | 16 | 22.5 | 23 | 127.2 | 101.1 | 16.3 | 39.2 | 26.8 | 24.8
297.3 | 78.3 | 290.9 | 116.36 | 136.0181 | 115.6 | 115.9 | 142.4 | 127 | 225.5 | 17.2 | 21.9 | 26.4 | 7.4 | 249.3 | 6.9 | 111.3 | 520.4 | 576.5 | 166.3 | 215.3 | 27.6 | 318.2 | 371.2 | 34.1 | 180 | 14.8 | 16.1 | 22.6 | 23.2 | 127.3 | 101.7 | 16.3 | 39.5 | 27 | 24.9
298.3 | 79.3 | 290.1 | 116.04 | 135.6441 | 115.9 | 117 | 143.6 | 127.6 | 222.7 | 17.2 | 21.9 | 26.4 | 7.4 | 247.1 | 7.9 | 115.7 | 507.4 | 562.4 | 166.5 | 215.6 | 28 | 313.6 | 362.5 | 34.5 | 179.6 | 14.8 | 16.1 | 22.7 | 23.3 | 127.9 | 102.2 | 16.4 | 39.9 | 27.2 | 25
299.3 | 80.3 | 289 | 115.6 | 135.1297 | 115.5 | 117.3 | 144.2 | 128.4 | 217.4 | 17.2 | 21.9 | 26.3 | 6.5 | 241.2 | 8.9 | 119.5 | 503 | 561.9 | 167.5 | 215.7 | 28.4 | 310.4 | 358.5 | 34.9 | 179.7 | 14.8 | 16.1 | 22.8 | 23.5 | 127.9 | 102.7 | 16.4 | 40.2 | 27.5 | 25.2
300.3 | 81.3 | 288.3 | 115.32 | 134.8024 | 115 | 117.4 | 144.3 | 128.7 | 216.4 | 17.2 | 21.9 | 26.4 | 6.9 | 245.1 | 8.9 | 122.9 | 510.8 | 573.4 | 169.7 | 218.7 | 28.8 | 309.3 | 360.6 | 35.3 | 180.9 | 14.8 | 16.2 | 22.9 | 23.6 | 127.7 | 102.9 | 16.5 | 40.5 | 27.6 | 25.3
301.3 | 82.3 | 288.1 | 115.24 | 134.7089 | 115.9 | 118.2 | 144.2 | 127.7 | 218.6 | 17.2 | 21.9 | 26.5 | 7.6 | 240.9 | 9.6 | 125.7 | 525.3 | 578.6 | 174.3 | 221.9 | 29.3 | 310.3 | 358.3 | 35.8 | 184.3 | 14.9 | 16.2 | 23 | 23.8 | 128.3 | 103.4 | 16.6 | 40.8 | 27.9 | 25.4
302.3 | 83.3 | 288 | 115.2 | 134.6622 | 117.1 | 117.9 | 144.4 | 127.3 | 223.3 | 17.3 | 21.9 | 26.7 | 8 | 241.4 | 10.8 | 128.2 | 527.4 | 569.8 | 172.7 | 222.3 | 29.7 | 310.6 | 360.9 | 36.2 | 185.5 | 14.8 | 16.3 | 23.2 | 23.9 | 129 | 103.5 | 16.6 | 41 | 28.1 | 25.6
303.3 | 84.3 | 288.4 | 115.36 | 134.8492 | 117.6 | 118.2 | 144.9 | 127.3 | 225.1 | 17.3 | 21.9 | 26.9 | 7.6 | 229.5 | 10.2 | 131.1 | 526.4 | 565.2 | 172.8 | 223.4 | 30.1 | 308.5 | 358.3 | 36.7 | 186.1 | 14.8 | 16.3 | 23.3 | 24 | 129.2 | 103.7 | 16.6 | 41.2 | 28.4 | 25.7
304.3 | 85.3 | 289.8 | 115.92 | 135.5038 | 117 | 118.8 | 145.2 | 128.1 | 223.4 | 17.3 | 21.9 | 27.1 | 7.2 | 242.4 | 9.2 | 134.8 | 538 | 578.6 | 177.9 | 226.6 | 30.5 | 310 | 369 | 37.1 | 189.2 | 14.9 | 16.4 | 23.6 | 24.2 | 129.3 | 104.2 | 16.7 | 41.6 | 28.6 | 25.8
305.3 | 86.3 | 289.6 | 115.84 | 135.4103 | 117 | 118.9 | 146.2 | 128.7 | 226.1 | 17.3 | 21.9 | 27.3 | 7 | 236.9 | 9.3 | 138.2 | 527 | 556.7 | 177.9 | 227.5 | 31 | 306.7 | 359 | 37.5 | 189.1 | 14.9 | 16.4 | 23.6 | 24.3 | 129.4 | 104.5 | 16.7 | 41.9 | 28.9 | 25.9
306.3 | 87.3 | 288.8 | 115.52 | 135.0362 | 118 | 119.1 | 147.2 | 129.9 | 221.8 | 17.4 | 21.9 | 27.4 | 6.2 | 246.1 | 9.3 | 141.5 | 535.3 | 561 | 184.1 | 227.7 | 31.4 | 307.4 | 367.3 | 37.9 | 190.4 | 14.9 | 16.5 | 23.7 | 24.4 | 129.3 | 105 | 16.8 | 42.4 | 29 | 26
307.3 | 88.3 | 289.3 | 115.72 | 135.27 | 119.7 | 118.8 | 147.8 | 130.6 | 221.7 | 17.4 | 21.9 | 27.5 | 6.6 | 233.5 | 9.2 | 145 | 540.3 | 567.7 | 185.5 | 231.6 | 31.9 | 309.3 | 366.6 | 38.3 | 193.8 | 14.9 | 16.5 | 23.8 | 24.5 | 130 | 105.2 | 16.9 | 42.8 | 29.3 | 26.2
308.3 | 89.3 | 289.3 | 115.72 | 135.27 | 120.3 | 119.5 | 148.4 | 131.4 | 223.2 | 17.4 | 21.9 | 27.5 | 7.6 | 261.9 | 10.8 | 148.5 | 545.5 | 571.8 | 186.9 | 233.4 | 32.3 | 309.5 | 368.5 | 38.8 | 195.4 | 14.9 | 16.6 | 23.8 | 24.7 | 131.4 | 105.7 | 16.9 | 43.2 | 29.5 | 26.3
309.3 | 90.3 | 289.1 | 115.64 | 135.1765 | 121 | 119.6 | 148.8 | 132.8 | 224.6 | 17.4 | 21.9 | 27.6 | 7.3 | 255.9 | 10.5 | 152.4 | 546.7 | 584.7 | 191.7 | 236.9 | 32.7 | 312.8 | 370.7 | 39.3 | 198.5 | 14.9 | 16.6 | 24 | 24.8 | 131.9 | 106.8 | 17 | 43.6 | 29.7 | 26.5
310.3 | 91.3 | 288.9 | 115.56 | 135.083 | 122 | 118.7 | 149.2 | 134.1 | 224.1 | 17.5 | 21.9 | 27.7 | 7 | 243.9 | 10.2 | 156.3 | 544.5 | 578.1 | 197.8 | 237.6 | 33.2 | 310.7 | 369.7 | 39.8 | 198 | 14.9 | 16.7 | 24.4 | 24.9 | 132.9 | 107.4 | 17.1 | 43.9 | 29.9 | 26.6
311.3 | 92.3 | 289 | 115.6 | 135.1297 | 123.1 | 118.8 | 148.6 | 135.2 | 222.5 | 17.5 | 21.9 | 27.8 | 7.1 | 238.3 | 9.6 | 160.1 | 574.5 | 592.7 | 208.2 | 240.8 | 33.6 | 312 | 378.5 | 40.2 | 200.8 | 14.9 | 16.7 | 24.5 | 25 | 133.7 | 108.3 | 17.1 | 44.1 | 30.1 | 26.8
312.3 | 93.3 | 288.7 | 115.48 | 134.9895 | 124.4 | 119.1 | 148.4 | 135.8 | 224.5 | 17.5 | 21.9 | 27.9 | 8.5 | 238.7 | 9.1 | 163.4 | 588.7 | 608 | 211.3 | 244.5 | 34.1 | 315 | 379.4 | 40.8 | 205 | 14.9 | 16.8 | 24.5 | 25.2 | 134.4 | 109 | 17.2 | 44.5 | 30.4 | 27
313.3 | 94.3 | 288.6 | 115.44 | 134.9427 | 125.4 | 118.5 | 148.2 | 135.6 | 226.6 | 17.6 | 21.9 | 27.9 | 8.7 | 242.3 | 10.3 | 166.3 | 610.4 | 618.4 | 214.4 | 249 | 34.6 | 321.1 | 377.4 | 41.2 | 209.2 | 14.9 | 16.8 | 24.5 | 25.3 | 135.2 | 109.5 | 17.3 | 44.8 | 30.6 | 27.1
314.3 | 95.3 | 288.7 | 115.48 | 134.9895 | 125.9 | 118.6 | 147.8 | 135.5 | 230.2 | 17.6 | 21.9 | 28 | 7.6 | 244.1 | 11.3 | 168.9 | 639.8 | 633 | 221 | 253.4 | 35 | 332.4 | 397.1 | 41.8 | 216 | 14.9 | 16.9 | 24.8 | 25.4 | 135.7 | 109.9 | 17.3 | 45.1 | 30.9 | 27.2
315.3 | 96.3 | 288.9 | 115.56 | 135.083 | 125.4 | 120.4 | 148.4 | 135.8 | 239.1 | 17.6 | 21.9 | 28 | 6.7 | 251.9 | 12.6 | 171.3 | 664.6 | 632.5 | 218.3 | 259.6 | 35.5 | 339.4 | 403.2 | 42.4 | 220.1 | 14.9 | 16.9 | 24.9 | 25.5 | 136.1 | 111 | 17.4 | 45.5 | 31.3 | 27.4
316.3 | 97.3 | 288.2 | 115.28 | 134.7557 | 124.7 | 121.8 | 148.8 | 137.2 | 238.7 | 17.6 | 21.9 | 28.1 | 6.3 | 251.6 | 12.3 | 173.5 | 672.8 | 636.5 | 216.1 | 261.1 | 36 | 338.9 | 400.9 | 43 | 221.2 | 14.9 | 16.9 | 25 | 25.7 | 136.7 | 111.7 | 17.5 | 45.9 | 31.6 | 27.6
317.3 | 98.3 | 287.1 | 114.84 | 134.2413 | 124.2 | 122.8 | 149.2 | 138.8 | 234.4 | 17.7 | 21.9 | 28.2 | 7.2 | 235.5 | 11.1 | 175.8 | 683.4 | 631.3 | 216.9 | 263.4 | 36.4 | 336.5 | 403.3 | 43.5 | 221.8 | 14.9 | 17 | 25.3 | 25.8 | 137.3 | 113.3 | 17.5 | 46.2 | 31.9 | 27.7
318.3 | 99.3 | 287.4 | 114.96 | 134.3816 | 123.6 | 123.8 | 149.9 | 140.1 | 233.8 | 17.7 | 21.9 | 28.3 | 8.2 | 233.8 | 9.5 | 178.4 | 692.9 | 642.1 | 218.5 | 268.8 | 36.9 | 339.1 | 406.8 | 44 | 224.2 | 14.9 | 17.1 | 25.5 | 25.9 | 137.8 | 114.4 | 17.6 | 46.6 | 32.2 | 27.9
319.3 | 100.3 | 287.3 | 114.92 | 134.3349 | 123.3 | 124.6 | 150.2 | 141 | 233.2 | 17.7 | 21.8 | 28.4 | 7.6 | 232.8 | 8.9 | 180.9 | 700.5 | 649.6 | 221.7 | 274.1 | 37.4 | 343.8 | 413.2 | 44.6 | 229.5 | 14.9 | 17.1 | 25.5 | 26.1 | 138.6 | 115.5 | 17.7 | 46.9 | 32.4 | 28
320.3 | 101.3 | 287.5 | 115 | 134.4284 | 123.5 | 125 | 150.3 | 141.5 | 237.3 | 17.7 | 21.8 | 28.4 | 7.9 | 220.8 | 11.1 | 183.3 | 712.3 | 649.4 | 226.2 | 276.3 | 37.8 | 347.5 | 423.7 | 45.2 | 234.1 | 14.9 | 17.2 | 25.9 | 26.2 | 139.2 | 116.2 | 17.8 | 47.2 | 32.7 | 28.2
321.3 | 102.3 | 287.4 | 114.96 | 134.3816 | 123.2 | 125.2 | 150.3 | 141.6 | 241.6 | 17.7 | 21.8 | 28.4 | 8.5 | 245.4 | 10.2 | 185.8 | 711.1 | 630.8 | 227 | 276.5 | 38.4 | 347.8 | 419.4 | 45.8 | 233.9 | 14.9 | 17.2 | 25.9 | 26.3 | 139.7 | 116.2 | 17.8 | 47.6 | 33.1 | 28.3
322.3 | 103.3 | 287.4 | 114.96 | 134.3816 | 123.2 | 125.8 | 150 | 141.7 | 238 | 17.7 | 21.8 | 28.5 | 7.7 | 241.4 | 9.7 | 188 | 712.3 | 626.7 | 227.4 | 276.8 | 38.9 | 344.1 | 410.3 | 46.3 | 232.9 | 14.9 | 17.3 | 26 | 26.5 | 140.1 | 116.7 | 17.9 | 48 | 33.5 | 28.5
323.3 | 104.3 | 288.3 | 115.32 | 134.8024 | 123.5 | 126.9 | 150.2 | 142.1 | 237.7 | 17.7 | 21.8 | 28.5 | 7.3 | 254.9 | 8.2 | 190 | 720.7 | 633 | 226.5 | 280.2 | 39.4 | 342.4 | 403.5 | 46.8 | 234.7 | 14.9 | 17.3 | 26.1 | 26.7 | 140.3 | 117.7 | 18 | 48.3 | 33.7 | 28.6
324.3 | 105.3 | 289.9 | 115.96 | 135.5506 | 124.7 | 127.9 | 150 | 142.3 | 237.5 | 17.7 | 21.8 | 28.6 | 7.6 | 230.1 | 8.4 | 192.1 | 716.7 | 628.3 | 225.9 | 281.2 | 39.9 | 342.5 | 407.5 | 47.3 | 235.8 | 14.9 | 17.4 | 26.1 | 26.8 | 140.7 | 118.4 | 18.1 | 48.7 | 33.9 | 28.8
325.3 | 106.3 | 288.7 | 115.48 | 134.9895 | 126 | 127.8 | 151 | 143 | 237 | 17.8 | 21.8 | 28.6 | 9.6 | 251.4 | 9.3 | 194.1 | 725.6 | 636.7 | 229.6 | 283 | 40.4 | 345.4 | 409.6 | 47.8 | 239.7 | 14.9 | 17.5 | 26.2 | 26.9 | 141.1 | 119.1 | 18 | 49.2 | 34 | 28.9
326.3 | 107.3 | 291.4 | 116.56 | 136.2519 | 126.8 | 128.3 | 152.3 | 144 | 240.3 | 17.9 | 21.8 | 28.7 | 9.5 | 258.1 | 8.8 | 196.2 | 741.1 | 635.7 | 232.3 | 285 | 40.9 | 347.5 | 409.6 | 48.4 | 243.2 | 14.9 | 17.5 | 26.3 | 27.1 | 141.6 | 119.9 | 18.1 | 49.5 | 34.1 | 28.9
327.3 | 108.3 | 289.3 | 115.72 | 135.27 | 127.6 | 128.2 | 151.9 | 143.6 | 241 | 17.8 | 21.8 | 28.8 | 8.8 | 270.5 | 9.5 | 198.3 | 745.8 | 644.8 | 237.1 | 287.8 | 41.5 | 349.6 | 409 | 48.9 | 245 | 14.9 | 17.6 | 26.5 | 27.2 | 141.6 | 120.8 | 18.2 | 49.7 | 34.8 | 29.2
328.3 | 109.3 | 287.8 | 115.12 | 134.5686 | 126.6 | 128.7 | 153.8 | 143.4 | 240.9 | 17.9 | 21.8 | 29 | 7.8 | 246.6 | 12.6 | 200.7 | 756.2 | 652.7 | 238.2 | 293.4 | 42 | 354.6 | 413.2 | 49.6 | 252.2 | 14.9 | 17.6 | 26.7 | 27.4 | 142.2 | 121.8 | 18.2 | 50.1 | 34.8 | 29.3
329.3 | 110.3 | 289.8 | 115.92 | 135.5038 | 127.7 | 129.5 | 154 | 143.8 | 242.4 | 17.9 | 21.8 | 29.1 | 7.8 | 235.3 | 10.4 | 202.7 | 762.7 | 647.4 | 238.3 | 294.7 | 42.5 | 357.2 | 419.8 | 50.1 | 253.9 | 15 | 17.7 | 27.2 | 27.5 | 142.7 | 122.3 | 18.4 | 50.5 | 35 | 29.4
330.3 | 111.3 | 291.2 | 116.48 | 136.1584 | 129.9 | 129.6 | 153.4 | 143.8 | 243.7 | 17.8 | 21.8 | 29.2 | 8 | 265.5 | 12 | 204.6 | 764.5 | 632.4 | 233.9 | 295.2 | 43.1 | 353.6 | 408.4 | 50.7 | 252.9 | 15 | 17.8 | 27.2 | 27.7 | 142.7 | 123.3 | 18.5 | 50.8 | 35.6 | 29.6
331.3 | 112.3 | 290.8 | 116.32 | 135.9714 | 129.5 | 128.8 | 154 | 144.3 | 240.9 | 17.8 | 21.8 | 29.3 | 7.4 | 253 | 16.7 | 206.5 | 761.6 | 628.1 | 232.9 | 295.3 | 43.6 | 350.5 | 408.5 | 51.2 | 253.1 | 15 | 17.8 | 27.3 | 27.8 | 142.9 | 123.2 | 18.5 | 51 | 35.9 | 29.8
332.3 | 113.3 | 289.8 | 115.92 | 135.5038 | 129.7 | 128.8 | 155 | 144.5 | 240.1 | 17.9 | 21.8 | 29.5 | 8 | 243.5 | 16.2 | 208 | 756.5 | 632.5 | 232.4 | 298.7 | 44.2 | 349.6 | 412.2 | 51.6 | 254.3 | 15 | 17.9 | 27.3 | 28 | 143.5 | 123.3 | 18.6 | 51.3 | 36.1 | 29.9
333.3 | 114.3 | 290.7 | 116.28 | 135.9246 | 130.1 | 129.5 | 155.4 | 144.8 | 241.9 | 17.9 | 21.8 | 29.5 | 9.2 | 243.7 | 13.3 | 209.9 | 756.5 | 645.1 | 231.8 | 307.1 | 44.7 | 354.6 | 425.4 | 52.1 | 257.2 | 15 | 18 | 27.6 | 28.1 | 143.6 | 123.4 | 18.7 | 51.6 | 36.3 | 30
334.3 | 115.3 | 288.4 | 115.36 | 134.8492 | 130.4 | 130.8 | 155.8 | 144.8 | 249.1 | 17.9 | 21.8 | 29.6 | 9.6 | 241.3 | 12.1 | 212 | 761 | 654.1 | 235.9 | 314.8 | 45.3 | 362.6 | 435.9 | 52.6 | 263.2 | 15 | 18 | 27.6 | 28.3 | 143.8 | 123.5 | 18.8 | 51.9 | 36.6 | 30.2
335.3 | 116.3 | 287.7 | 115.08 | 134.5219 | 130.6 | 132.2 | 156.1 | 144.8 | 254.9 | 17.9 | 21.8 | 29.7 | 9.3 | 249.5 | 10.8 | 214.4 | 765.1 | 658.1 | 238.6 | 317.9 | 45.9 | 366.7 | 433.1 | 53.3 | 266.6 | 15 | 18.1 | 27.8 | 28.4 | 144 | 123.4 | 18.9 | 52.1 | 37 | 30.3
336.3 | 117.3 | 288.1 | 115.24 | 134.7089 | 129.3 | 132.6 | 156.2 | 145.3 | 250.6 | 17.9 | 21.8 | 29.8 | 9.9 | 255.8 | 9.8 | 217.5 | 765 | 648.6 | 243.5 | 317.4 | 46.4 | 363.8 | 431.5 | 53.7 | 266.1 | 15 | 18.2 | 27.9 | 28.6 | 144 | 123.6 | 19 | 52.5 | 37.3 | 30.4
337.3 | 118.3 | 288 | 115.2 | 134.6622 | 128.5 | 133.1 | 156.2 | 145.8 | 248 | 17.9 | 21.8 | 29.9 | 9.4 | 261.3 | 8.5 | 220.3 | 771.2 | 653.6 | 251.4 | 319.9 | 47 | 367.8 | 450.3 | 54.2 | 268.2 | 15 | 18.2 | 28 | 28.7 | 144.3 | 124 | 19 | 52.8 | 37.6 | 30.6
338.3 | 119.3 | 288.4 | 115.36 | 134.8492 | 128.7 | 134 | 155.9 | 146.5 | 250.9 | 17.9 | 21.8 | 29.9 | 9 | 272.6 | 9.3 | 223.2 | 772.5 | 658.4 | 255.7 | 324.2 | 47.6 | 374.2 | 471.3 | 54.8 | 272.8 | 15 | 18.3 | 28.2 | 28.8 | 144.8 | 124.6 | 19.1 | 53.2 | 37.9 | 30.7
339.3 | 120.3 | 288.4 | 115.36 | 134.8492 | 128.7 | 133.7 | 156.1 | 146.7 | 256.3 | 17.9 | 21.8 | 30.1 | 10.7 | 259.9 | 9.8 | 226 | 770.8 | 654.8 | 257.4 | 326.9 | 48.2 | 374.9 | 468.9 | 55.4 | 274.4 | 15 | 18.4 | 28.4 | 29 | 145.1 | 124.6 | 19.2 | 53.5 | 38.2 | 30.9
340.3 | 121.3 | 288.4 | 115.36 | 134.8492 | 130.4 | 132.4 | 155.9 | 146.1 | 255.1 | 17.9 | 21.8 | 30.2 | 11.6 | 266.6 | 9.9 | 228.4 | 754.6 | 636.6 | 258.3 | 324.6 | 48.8 | 370.3 | 451.6 | 55.9 | 274.2 | 15 | 18.4 | 28.4 | 29.1 | 145.6 | 124.9 | 19.3 | 53.7 | 38.5 | 31
341.3 | 122.3 | 288.5 | 115.4 | 134.896 | 131.7 | 133.6 | 155.9 | 145.2 | 250.1 | 17.9 | 21.8 | 30.2 | 11.1 | 269.3 | 11 | 230.7 | 740.2 | 617 | 257.2 | 324 | 49.3 | 363.4 | 435 | 56.4 | 273.2 | 15 | 18.5 | 28.5 | 29.3 | 146.2 | 125.5 | 19.4 | 54.1 | 38.8 | 31.1
342.3 | 123.3 | 288 | 115.2 | 134.6622 | 131.2 | 134.4 | 156.8 | 145.7 | 245.4 | 18.1 | 21.8 | 30.3 | 10.4 | 263.6 | 14 | 233.1 | 731.6 | 614.3 | 258.7 | 325.4 | 49.9 | 359.2 | 426.3 | 56.9 | 273.9 | 15 | 18.5 | 28.8 | 29.4 | 146.8 | 126 | 19.3 | 54.6 | 38.8 | 31.2
343.3 | 124.3 | 288.2 | 115.28 | 134.7557 | 131.5 | 134.2 | 156.6 | 145.3 | 243.8 | 18 | 21.8 | 30.4 | 8.3 | 271.7 | 13.1 | 235.2 | 730.5 | 615 | 263.6 | 326.5 | 50.5 | 357.4 | 419.8 | 57.4 | 273.6 | 15 | 18.6 | 28.9 | 29.5 | 147.7 | 126.3 | 19.5 | 54.9 | 39.3 | 31.5
344.3 | 125.3 | 288.5 | 115.4 | 134.896 | 131.3 | 134.6 | 156.8 | 145.7 | 241.8 | 18 | 21.8 | 30.5 | 8 | 271.7 | 13.6 | 236.9 | 735.7 | 613.9 | 268.3 | 329.1 | 51.1 | 357.9 | 416.2 | 57.9 | 276.4 | 15 | 18.7 | 29 | 29.7 | 148.3 | 126.2 | 19.6 | 55.1 | 39.5 | 31.6
345.3 | 126.3 | 289.6 | 115.84 | 135.4103 | 132.6 | 135.6 | 157 | 145.8 | 242.8 | 18 | 21.8 | 30.5 | 7.2 | 247.5 | 14.4 | 238.8 | 737.5 | 626.1 | 273.4 | 330.7 | 51.7 | 359 | 414 | 58.5 | 278.5 | 15 | 18.8 | 29.2 | 29.8 | 148.5 | 126.4 | 19.7 | 55.4 | 39.7 | 31.8
346.3 | 127.3 | 288.2 | 115.28 | 134.7557 | 132.1 | 136.9 | 156.7 | 146.5 | 244.9 | 18 | 21.8 | 30.6 | 7.5 | 252.4 | 13.5 | 240.9 | 734.8 | 620.4 | 276.1 | 330.5 | 52.3 | 358.9 | 412.9 | 59 | 280.3 | 15.1 | 18.8 | 29.3 | 30 | 148.6 | 126.4 | 19.8 | 55.8 | 40 | 31.9
347.3 | 128.3 | 286.9 | 114.76 | 134.1478 | 132.1 | 136.8 | 156.4 | 146.9 | 246.5 | 18.1 | 21.8 | 30.6 | 7.9 | 246.2 | 12.8 | 243.4 | 721.2 | 608.6 | 278.1 | 331.3 | 52.9 | 356.4 | 407.6 | 59.5 | 279.8 | 15.1 | 18.9 | 29.4 | 30.1 | 148.4 | 126.9 | 19.9 | 56.1 | 40.3 | 32
348.3 | 129.3 | 287.6 | 115.04 | 134.4751 | 133 | 136.1 | 156.5 | 146.2 | 245.6 | 18.1 | 21.8 | 30.6 | 8.2 | 251.6 | 12.9 | 245.4 | 714.8 | 602.9 | 278.8 | 331.6 | 53.5 | 353.2 | 403.4 | 60 | 280.1 | 15.1 | 19 | 29.4 | 30.2 | 148.3 | 127.6 | 20 | 56.4 | 40.5 | 32.2
349.3 | 130.3 | 288.3 | 115.32 | 134.8024 | 133.4 | 135.3 | 156.7 | 146.1 | 243.2 | 18.1 | 21.8 | 30.7 | 8.8 | 250.1 | 11.9 | 247.7 | 713.8 | 598.7 | 279.7 | 332 | 54.1 | 350.9 | 402.6 | 60.5 | 280.2 | 15.1 | 19 | 29.6 | 30.4 | 147.8 | 127.9 | 20.1 | 56.8 | 40.8 | 32.3
350.3 | 131.3 | 288.2 | 115.28 | 134.7557 | 134.2 | 134.6 | 157.2 | 145.8 | 241.6 | 18.1 | 21.8 | 30.9 | 8.4 | 260.4 | 11.2 | 249.9 | 715.8 | 592.8 | 281 | 332.1 | 54.7 | 347.5 | 398.2 | 60.9 | 280.7 | 15.1 | 19.1 | 29.9 | 30.5 | 147.5 | 127.8 | 20.2 | 56.8 | 41 | 32.4
351.3 | 132.3 | 288.7 | 115.48 | 134.9895 | 135.8 | 134.7 | 157.6 | 146.3 | 240.8 | 18.1 | 21.8 | 31 | 8.1 | 233.1 | 9.6 | 252 | 721.1 | 592.4 | 282.8 | 333.6 | 55.3 | 346.9 | 395.5 | 61.4 | 281.9 | 15.1 | 19.2 | 29.9 | 30.7 | 147.5 | 128 | 20.2 | 57 | 41.2 | 32.5
352.3 | 133.3 | 289.4 | 115.76 | 135.3168 | 135.9 | 134.6 | 158 | 147 | 241 | 18.1 | 21.8 | 31 | 7.9 | 242.6 | 7.2 | 253.9 | 727 | 592.2 | 284.8 | 334.4 | 55.9 | 345 | 387.6 | 61.8 | 283.1 | 15.1 | 19.2 | 30 | 30.8 | 148 | 128.3 | 20.3 | 57.2 | 41.5 | 32.6
353.3 | 134.3 | 289.6 | 115.84 | 135.4103 | 136.5 | 133.9 | 158.3 | 147.4 | 238.9 | 18.1 | 21.8 | 31.1 | 8.2 | 172.3 | 5.9 | 255.6 | 726.4 | 588.3 | 289.3 | 334.6 | 56.5 | 344.3 | 384.8 | 62.3 | 284.6 | 15.1 | 19.3 | 30 | 30.9 | 148.3 | 128.5 | 20.4 | 57.5 | 41.7 | 32.8
354.3 | 135.3 | 287.2 | 114.88 | 134.2881 | 137.5 | 134.3 | 158.3 | 148 | 239.9 | 18.1 | 21.8 | 31.2 | 8.8 | 244.1 | 5.4 | 257.6 | 719.2 | 585 | 292.5 | 335.9 | 57.1 | 342.7 | 385.3 | 62.7 | 284.1 | 15.1 | 19.4 | 30.3 | 31 | 148.4 | 128.4 | 20.5 | 57.8 | 42 | 32.9
355.3 | 136.3 | 287.4 | 114.96 | 134.3816 | 137.9 | 135.1 | 158.2 | 148.3 | 237.5 | 18.1 | 21.8 | 31.2 | 9.4 | 259.1 | 6.3 | 259.7 | 719.2 | 579.9 | 293.5 | 334.8 | 57.7 | 340.9 | 380.6 | 63.2 | 283.7 | 15.1 | 19.5 | 30.4 | 31.2 | 149.1 | 128.7 | 20.6 | 58 | 42.2 | 33.1
356.3 | 137.3 | 287.8 | 115.12 | 134.5686 | 139.5 | 134.5 | 158.1 | 148.5 | 235.9 | 18.1 | 21.8 | 31.2 | 8.9 | 230.1 | 7.7 | 262 | 710.5 | 565.2 | 294.6 | 334.8 | 58.3 | 337.5 | 377.6 | 63.6 | 282.6 | 15.1 | 19.5 | 30.6 | 31.3 | 149.6 | 129.2 | 20.7 | 58.2 | 42.4 | 33.3
357.3 | 138.3 | 287.6 | 115.04 | 134.4751 | 140.1 | 134.2 | 158.6 | 148.6 | 235.6 | 18.1 | 21.8 | 31.3 | 8.9 | 228.1 | 9.5 | 263.9 | 702.7 | 567.9 | 296.3 | 334.7 | 58.9 | 334.2 | 379.1 | 64 | 282.3 | 15.1 | 19.6 | 30.7 | 31.4 | 150 | 129.8 | 20.8 | 58.4 | 42.6 | 33.5
358.3 | 139.3 | 288.1 | 115.24 | 134.7089 | 140.8 | 134.8 | 159.1 | 148.4 | 238.3 | 18.1 | 21.8 | 31.3 | 8.3 | 259.1 | 9.9 | 265.6 | 703.7 | 588.1 | 299.8 | 339.2 | 59.5 | 336.2 | 390.6 | 64.3 | 283.4 | 15.1 | 19.7 | 30.8 | 31.5 | 150 | 129.7 | 20.9 | 58.6 | 42.8 | 33.6
359.3 | 140.3 | 288.1 | 115.24 | 134.7089 | 140.8 | 134.9 | 160 | 147.8 | 239.7 | 18.1 | 21.8 | 31.3 | 8.3 | 240.9 | 9.7 | 267.4 | 701.3 | 590 | 300.9 | 340.3 | 60.1 | 333.4 | 385.5 | 64.8 | 283.9 | 15.1 | 19.8 | 30.8 | 31.7 | 150.5 | 130 | 20.9 | 59 | 43.1 | 33.8
360.3 | 141.3 | 288.1 | 115.24 | 134.7089 | 142.5 | 135.3 | 160.1 | 147.9 | 240.8 | 18.1 | 21.8 | 31.2 | 8 | 213.4 | 9.2 | 269.2 | 688.5 | 577.3 | 302.5 | 340.2 | 60.7 | 333.1 | 379.1 | 65.3 | 285.6 | 15.1 | 19.8 | 31 | 31.8 | 150.3 | 130.1 | 21.1 | 59.4 | 43.3 | 34
361.3 | 142.3 | 288.3 | 115.32 | 134.8024 | 142.6 | 135.5 | 159.9 | 148 | 239.1 | 18.1 | 21.8 | 31.2 | 8 | 260.2 | 7.4 | 270.7 | 679.2 | 564.8 | 301.6 | 339.4 | 61.3 | 329.9 | 373 | 65.7 | 284.1 | 15.2 | 19.9 | 31.3 | 31.9 | 150.7 | 130.2 | 21.1 | 59.5 | 43.6 | 34.2
362.3 | 143.3 | 287.9 | 115.16 | 134.6154 | 143 | 135.6 | 160.2 | 148.5 | 236.7 | 18.2 | 21.8 | 31.2 | 7.3 | 237.5 | 9.2 | 271.8 | 661.6 | 561.6 | 301 | 339.4 | 61.9 | 325.9 | 366 | 66 | 283.2 | 15.2 | 20 | 31.3 | 32 | 150.9 | 130.1 | 21.2 | 59.6 | 43.8 | 34.3
363.3 | 144.3 | 289.2 | 115.68 | 135.2233 | 143.1 | 135.9 | 160.8 | 148.2 | 234.7 | 18.2 | 21.8 | 31.3 | 8.5 | 245.9 | 12.2 | 272.8 | 659.1 | 564.7 | 299.6 | 341.5 | 62.5 | 322.9 | 364.5 | 66.3 | 282.5 | 15.2 | 20.1 | 31.5 | 32.1 | 151.1 | 130.3 | 21.3 | 59.9 | 44 | 34.4
364.3 | 145.3 | 288.3 | 115.32 | 134.8024 | 142.1 | 135.8 | 160.8 | 147.4 | 233.7 | 18.2 | 21.8 | 31.4 | 9.7 | 234.5 | 12 | 273.7 | 640.8 | 545 | 299.4 | 340.4 | 63.1 | 319.4 | 358.2 | 66.7 | 282.3 | 15.2 | 20.2 | 31.6 | 32.3 | 150.9 | 130.4 | 21.4 | 60.2 | 44.2 | 34.6
365.3 | 146.3 | 286.2 | 114.48 | 133.8205 | 142.5 | 136.2 | 161.1 | 146.9 | 232 | 18.2 | 21.8 | 31.4 | 11.8 | 247.7 | 10.3 | 274.4 | 623.4 | 534.8 | 299.7 | 340 | 63.7 | 316 | 350.4 | 67 | 281.6 | 15.2 | 20.2 | 31.7 | 32.4 | 150.7 | 130.9 | 21.5 | 60.4 | 44.4 | 34.7
366.3 | 147.3 | 286.4 | 114.56 | 133.914 | 142.1 | 136.1 | 161.1 | 146.7 | 229.3 | 18.2 | 21.7 | 31.4 | 11.4 | 224.4 | 11.9 | 274.9 | 605.7 | 532.2 | 299.3 | 340.5 | 64.3 | 312 | 341.4 | 67.4 | 281.3 | 15.2 | 20.3 | 31.9 | 32.5 | 150.4 | 131.1 | 21.6 | 60.6 | 44.6 | 34.8
367.3 | 148.3 | 287.7 | 115.08 | 134.5219 | 141.7 | 136.5 | 161.4 | 146.4 | 226.7 | 18.2 | 21.7 | 31.5 | 10.6 | 235.4 | 12.1 | 275.4 | 601 | 532.6 | 300.4 | 341.5 | 64.9 | 310.9 | 342 | 67.7 | 282.2 | 15.2 | 20.4 | 31.9 | 32.6 | 150.6 | 131.2 | 21.7 | 60.8 | 44.8 | 35
368.3 | 149.3 | 288.1 | 115.24 | 134.7089 | 142.4 | 137 | 161.2 | 147 | 226.5 | 18.3 | 21.8 | 31.5 | 9.8 | 240.7 | 13 | 275.9 | 589.3 | 539.7 | 301.4 | 341.8 | 65.5 | 308.3 | 338.3 | 68 | 281.7 | 15.2 | 20.5 | 32.1 | 32.7 | 150.8 | 131.4 | 21.8 | 61 | 45 | 35.1
369.3 | 150.3 | 288 | 115.2 | 134.6622 | 143.1 | 137.3 | 161.3 | 148 | 225.1 | 18.3 | 21.8 | 31.6 | 9.1 | 237.6 | 14.5 | 276.4 | 577.7 | 542.5 | 301.4 | 342.5 | 66.1 | 306.6 | 335.5 | 68.4 | 281.1 | 15.2 | 20.5 | 32.3 | 32.8 | 151 | 131.5 | 21.9 | 61.3 | 45.2 | 35.3
370.3 | 151.3 | 287.8 | 115.12 | 134.5686 | 142.7 | 137.4 | 160.9 | 148.1 | 222.7 | 18.4 | 21.8 | 31.7 | 10.5 | 245.1 | 16.8 | 277 | 566.3 | 541.6 | 301 | 342.5 | 66.7 | 301.5 | 328.8 | 68.6 | 280.2 | 15.2 | 20.6 | 32.3 | 32.9 | 151.1 | 131.7 | 22 | 61.7 | 45.4 | 35.4
371.3 | 152.3 | 288.7 | 115.48 | 134.9895 | 143.4 | 137.7 | 160.9 | 147.8 | 220.1 | 18.4 | 21.7 | 31.7 | 9.8 | 226.4 | 18 | 277.8 | 559.6 | 554.9 | 300.9 | 344.9 | 67.3 | 299.3 | 329.8 | 68.8 | 279.7 | 15.2 | 20.7 | 32.4 | 33.1 | 150.8 | 131.9 | 22.1 | 61.9 | 45.6 | 35.5
372.3 | 153.3 | 289.5 | 115.8 | 135.3635 | 144.7 | 137.7 | 160.5 | 148 | 221.8 | 18.4 | 21.7 | 31.9 | 9.7 | 251 | 15.6 | 278.7 | 556.3 | 554.4 | 302.1 | 345 | 67.9 | 297.2 | 327.6 | 69 | 278.7 | 15.3 | 20.8 | 32.4 | 33.2 | 150.8 | 132 | 22.2 | 62.2 | 45.8 | 35.7
373.3 | 154.3 | 286.9 | 114.76 | 134.1478 | 145.4 | 137 | 160 | 148.4 | 223 | 18.4 | 21.7 | 32 | 8.9 | 229.6 | 17.1 | 279.5 | 568.4 | 559.8 | 306.9 | 346.1 | 68.5 | 300.8 | 332.2 | 69.3 | 281 | 15.3 | 20.9 | 32.7 | 33.3 | 150.6 | 132.3 | 22.3 | 62.4 | 46 | 35.8
374.3 | 155.3 | 287.2 | 114.88 | 134.2881 | 144.9 | 135.4 | 159.5 | 148.2 | 227.3 | 18.4 | 21.8 | 32.1 | 8.7 | 235.6 | 16 | 280.6 | 574.2 | 565.1 | 307.9 | 347.9 | 69.1 | 305.9 | 331.2 | 69.8 | 284.2 | 15.3 | 20.9 | 32.9 | 33.4 | 150.6 | 132.6 | 22.4 | 62.6 | 46.2 | 35.9
375.3 | 156.3 | 287.1 | 114.84 | 134.2413 | 145.5 | 134.8 | 159.5 | 147.8 | 228.3 | 18.4 | 21.8 | 32.2 | 8 | 236.8 | 15.5 | 281.7 | 580.3 | 555.8 | 309.1 | 348.2 | 69.7 | 309.9 | 334.6 | 70.3 | 285.2 | 15.3 | 21 | 33.1 | 33.5 | 150.5 | 133 | 22.5 | 62.8 | 46.5 | 36
376.3 | 157.3 | 287.2 | 114.88 | 134.2881 | 145.3 | 134.2 | 160.1 | 148.4 | 226.8 | 18.4 | 21.7 | 32.3 | 8.1 | 241.5 | 14.2 | 282.9 | 579.7 | 553.2 | 309.7 | 348.4 | 70.2 | 310.5 | 336.1 | 70.7 | 284 | 15.3 | 21.1 | 33.3 | 33.6 | 150.2 | 133.2 | 22.6 | 63 | 46.8 | 36.2
377.3 | 158.3 | 287.4 | 114.96 | 134.3816 | 146.4 | 135.1 | 160.3 | 149.7 | 229.5 | 18.5 | 21.7 | 32.4 | 8.3 | 243.7 | 13.5 | 284.3 | 576.4 | 548.9 | 309.8 | 348.4 | 70.8 | 309.7 | 336.4 | 71.1 | 283.5 | 15.3 | 21.2 | 33.3 | 33.7 | 150.3 | 133.5 | 22.7 | 63.4 | 47 | 36.3
378.3 | 159.3 | 288.2 | 115.28 | 134.7557 | 146.6 | 135.5 | 160.8 | 149.7 | 230.8 | 18.5 | 21.7 | 32.5 | 7.5 | 247 | 13.5 | 285.6 | 575.9 | 544.4 | 310.3 | 348.1 | 71.4 | 310.5 | 349.6 | 71.4 | 283.5 | 15.3 | 21.3 | 33.4 | 33.8 | 150.2 | 133.8 | 22.8 | 63.4 | 47.2 | 36.4
379.3 | 160.3 | 289.1 | 115.64 | 135.1765 | 146.1 | 135.7 | 161.7 | 149.8 | 231.9 | 18.5 | 21.7 | 32.6 | 8 | 244.2 | 13.8 | 286.8 | 572.9 | 538.9 | 309.9 | 348.4 | 72 | 309.3 | 347.2 | 71.6 | 283 | 15.3 | 21.4 | 33.4 | 33.9 | 150.1 | 134.1 | 22.9 | 63.6 | 47.4 | 36.6
380.3 | 161.3 | 288 | 115.2 | 134.6622 | 145.7 | 135.9 | 162 | 150.2 | 233.2 | 18.5 | 21.7 | 32.6 | 7.4 | 239.9 | 13.8 | 288 | 571.6 | 533.7 | 310.5 | 348.5 | 72.6 | 310.3 | 351.8 | 71.9 | 283.5 | 15.3 | 21.5 | 33.7 | 34 | 150.2 | 134.3 | 23 | 63.8 | 47.6 | 36.7
381.3 | 162.3 | 288.9 | 115.56 | 135.083 | 145.4 | 135.6 | 162.3 | 150 | 233.4 | 18.5 | 21.7 | 32.7 | 7.2 | 240.8 | 12.3 | 289.4 | 558.4 | 530.7 | 310.5 | 347.5 | 73.2 | 309.5 | 349.5 | 72.3 | 282.8 | 15.3 | 21.5 | 33.9 | 34.1 | 150.8 | 134.7 | 23 | 63.9 | 47.8 | 36.9
382.3 | 163.3 | 289.8 | 115.92 | 135.5038 | 146 | 136.1 | 162.5 | 150.9 | 233.6 | 18.6 | 21.7 | 32.8 | 7.5 | 250 | 11.3 | 290.8 | 555.8 | 528.4 | 311.2 | 347.3 | 73.8 | 309 | 356 | 72.6 | 282.8 | 15.3 | 21.6 | 34 | 34.2 | 151.1 | 134.9 | 23.2 | 64.1 | 48.1 | 37
383.3 | 164.3 | 287.2 | 114.88 | 134.2881 | 145.3 | 137.4 | 163.1 | 152.4 | 237.4 | 18.6 | 21.7 | 32.9 | 8.2 | 255.9 | 10.1 | 292.2 | 556 | 530.9 | 312.1 | 348 | 74.4 | 309.1 | 362.5 | 72.9 | 283.2 | 15.4 | 21.7 | 34.2 | 34.3 | 151.8 | 135.2 | 23.3 | 64.3 | 48.3 | 37.2
384.3 | 165.3 | 287.1 | 114.84 | 134.2413 | 145.1 | 138 | 163.6 | 153.5 | 238.3 | 18.6 | 21.7 | 32.9 | 6.9 | 216.2 | 9.1 | 293.6 | 560.4 | 529.2 | 313.3 | 347.9 | 74.9 | 310 | 365.3 | 73.2 | 283.6 | 15.4 | 21.8 | 34.4 | 34.4 | 152.5 | 135.7 | 23.4 | 64.5 | 48.5 | 37.3
385.3 | 166.3 | 287.3 | 114.92 | 134.3349 | 144 | 138.2 | 164.2 | 153.6 | 239 | 18.6 | 21.7 | 33 | 6.8 | 229.2 | 8.7 | 295.1 | 559.2 | 529 | 313.3 | 348.1 | 75.5 | 310.1 | 363.7 | 73.5 | 283.9 | 15.4 | 21.9 | 34.5 | 34.5 | 153.2 | 135.8 | 23.5 | 64.9 | 48.7 | 37.5
386.3 | 167.3 | 287.6 | 115.04 | 134.4751 | 144.3 | 138.2 | 164.6 | 153.8 | 237.8 | 18.7 | 21.7 | 33 | 7.6 | 239.2 | 8.9 | 296.6 | 544.1 | 511.1 | 311.8 | 346.6 | 76.1 | 307.5 | 355.6 | 73.9 | 283.2 | 15.4 | 22 | 34.5 | 34.6 | 153.7 | 135.8 | 23.6 | 65.2 | 48.9 | 37.7
387.3 | 168.3 | 287.6 | 115.04 | 134.4751 | 145.1 | 136.8 | 164.7 | 154.3 | 233 | 18.7 | 21.7 | 33.1 | 8.5 | 253.6 | 10.2 | 297.9 | 529.4 | 501.3 | 309.8 | 345.9 | 76.7 | 302.9 | 347.4 | 74.1 | 281.2 | 15.4 | 22 | 34.7 | 34.7 | 154.1 | 135.6 | 23.7 | 65.5 | 49 | 37.8
388.3 | 169.3 | 287.7 | 115.08 | 134.5219 | 146.4 | 137 | 165 | 154 | 232.2 | 18.8 | 21.7 | 33.2 | 9 | 240.3 | 9.9 | 299 | 520 | 504.1 | 309.1 | 347.4 | 77.3 | 299.8 | 345.2 | 74.4 | 280.9 | 15.4 | 22.1 | 34.7 | 34.8 | 154.2 | 135.5 | 23.8 | 65.8 | 49.2 | 38
389.3 | 170.3 | 287.8 | 115.12 | 134.5686 | 147.5 | 136.7 | 164.5 | 153.4 | 233.2 | 18.8 | 21.7 | 33.3 | 9.6 | 250.1 | 10.9 | 299.9 | 516.3 | 507.8 | 308.5 | 347.9 | 77.9 | 298.7 | 345.1 | 74.7 | 280.9 | 15.4 | 22.2 | 34.8 | 34.9 | 154.2 | 135.8 | 23.9 | 66 | 49.3 | 38.1
390.3 | 171.3 | 287.8 | 115.12 | 134.5686 | 148.1 | 136.1 | 164.5 | 152.6 | 234.3 | 18.9 | 21.7 | 33.4 | 10.7 | 234.2 | 11.8 | 300.9 | 522.8 | 517.3 | 308.5 | 349.5 | 78.4 | 301.9 | 354.4 | 74.9 | 281.8 | 15.4 | 22.3 | 35 | 35 | 154.3 | 135.8 | 24 | 66.3 | 49.5 | 38.3
391.3 | 172.3 | 287.5 | 115 | 134.4284 | 147.5 | 136.9 | 164.4 | 151.5 | 237.7 | 18.9 | 21.7 | 33.5 | 10.4 | 216.3 | 11.2 | 302 | 519.9 | 510.6 | 308.8 | 349.7 | 79 | 300.7 | 351.6 | 75.2 | 281.5 | 15.5 | 22.4 | 35 | 35.1 | 154.3 | 135.9 | 24.1 | 66.6 | 49.7 | 38.4
392.3 | 173.3 | 287.7 | 115.08 | 134.5219 | 147.5 | 137.8 | 164.2 | 151.5 | 239.5 | 18.9 | 21.7 | 33.6 | 8.9 | 228.2 | 10.8 | 303.3 | 522.7 | 505.8 | 309.7 | 349 | 79.6 | 301.8 | 359.4 | 75.5 | 281.3 | 15.5 | 22.5 | 35.3 | 35.2 | 154.5 | 135.9 | 24.2 | 66.7 | 49.9 | 38.5
393.3 | 174.3 | 287.7 | 115.08 | 134.5219 | 148.7 | 138.4 | 164 | 152.3 | 241.4 | 18.9 | 21.7 | 33.7 | 9.4 | 241 | 12 | 304.8 | 530.7 | 518.6 | 310.6 | 349.8 | 80.2 | 306.1 | 372.8 | 75.8 | 282.2 | 15.5 | 22.6 | 35.5 | 35.2 | 155 | 135.9 | 24.3 | 66.9 | 50 | 38.7
394.3 | 175.3 | 287.8 | 115.12 | 134.5686 | 147.7 | 139.3 | 163.3 | 153.4 | 247.5 | 19 | 21.7 | 33.9 | 9.5 | 241.3 | 16.2 | 306.7 | 543 | 531.6 | 311.4 | 352.2 | 80.8 | 311.2 | 378.2 | 76.2 | 284.2 | 15.5 | 22.6 | 35.6 | 35.4 | 155.3 | 136.2 | 24.4 | 67.2 | 50.2 | 38.8
395.3 | 176.3 | 287.8 | 115.12 | 134.5686 | 147.5 | 139.1 | 163.5 | 154.3 | 251.9 | 19 | 21.7 | 34 | 9 | 242.7 | 18.9 | 308.9 | 569.9 | 557 | 312.3 | 356 | 81.3 | 319.6 | 396.4 | 76.6 | 286.1 | 15.5 | 22.7 | 35.7 | 35.5 | 155.8 | 136.2 | 24.5 | 67.5 | 50.5 | 39
396.3 | 177.3 | 288.4 | 115.36 | 134.8492 | 147.7 | 140.1 | 163.7 | 154.9 | 256.8 | 19.1 | 21.7 | 34.1 | 8.9 | 240.9 | 18.7 | 311.1 | 589.1 | 570.1 | 312 | 358.2 | 81.9 | 325.9 | 407.5 | 77.2 | 288.1 | 15.5 | 22.8 | 35.9 | 35.5 | 156.7 | 136.4 | 24.6 | 67.7 | 50.8 | 39.2
397.3 | 178.3 | 289.7 | 115.88 | 135.457 | 147.6 | 140.8 | 163.9 | 155.1 | 257.8 | 19.2 | 21.7 | 34.1 | 10.3 | 224.9 | 17.3 | 313.2 | 584.5 | 560.8 | 310.6 | 357.9 | 82.5 | 326.1 | 403.1 | 77.7 | 287.9 | 15.5 | 22.9 | 36 | 35.6 | 157.6 | 136.2 | 24.7 | 68.1 | 51 | 39.3
398.3 | 179.3 | 288.3 | 115.32 | 134.8024 | 147.7 | 141.4 | 164.3 | 155.8 | 253.5 | 19.2 | 21.7 | 34.1 | 9.7 | 223.1 | 16 | 314.7 | 575 | 548.9 | 309.7 | 358 | 83.1 | 326.1 | 394.6 | 78.1 | 287.6 | 15.5 | 23 | 36.1 | 35.7 | 158.4 | 136.5 | 24.9 | 68.4 | 51.3 | 39.5
399.3 | 180.3 | 287.3 | 114.92 | 134.3349 | 147 | 141.3 | 164.3 | 156.2 | 250.8 | 19.3 | 21.7 | 34.2 | 9.6 | 245.1 | 13.8 | 316.1 | 567 | 550.7 | 309.2 | 358.8 | 83.7 | 324.3 | 391.5 | 78.4 | 286.9 | 15.6 | 23.1 | 36.4 | 35.9 | 159.5 | 136.9 | 25 | 68.7 | 51.6 | 39.7
400.3 | 181.3 | 288.6 | 115.44 | 134.9427 | 146 | 140.8 | 163.4 | 156.8 | 249.8 | 19.3 | 21.7 | 34.2 | 9.5 | 200.6 | 11.4 | 317.2 | 561.2 | 555.2 | 308.9 | 359.2 | 84.3 | 322.5 | 389.3 | 78.7 | 287.6 | 15.6 | 23.2 | 36.6 | 36 | 159.6 | 137.1 | 25.1 | 69 | 51.8 | 39.9
401.3 | 182.3 | 288.7 | 115.48 | 134.9895 | 145.3 | 140.7 | 163.8 | 157 | 250.6 | 19.4 | 21.7 | 34.1 | 8.8 | 249.8 | 10.2 | 318.3 | 576.5 | 579.8 | 309.6 | 362.8 | 84.9 | 326 | 396.3 | 79 | 291 | 15.6 | 23.3 | 36.6 | 36 | 159.7 | 137.1 | 25.2 | 69.2 | 52 | 40.1
402.3 | 183.3 | 288.9 | 115.56 | 135.083 | 145.2 | 140.9 | 163.3 | 157.2 | 252.6 | 19.4 | 21.7 | 34 | 7.3 | 222.1 | 9.3 | 319.7 | 572.2 | 581.1 | 309.9 | 362.8 | 85.5 | 326.9 | 389.4 | 79.5 | 291.8 | 15.6 | 23.3 | 36.7 | 36.2 | 159.9 | 137.1 | 25.3 | 69.4 | 52.3 | 40.2
403.3 | 184.3 | 288.9 | 115.56 | 135.083 | 145.5 | 141.1 | 162.3 | 157.7 | 249.6 | 19.5 | 21.7 | 34 | 7.8 | 230 | 10.7 | 321 | 582.6 | 587.6 | 310.3 | 363.7 | 86.1 | 328.9 | 389.8 | 79.9 | 293.9 | 15.6 | 23.4 | 36.9 | 36.3 | 160.3 | 137.2 | 25.4 | 69.6 | 52.6 | 40.4
404.3 | 185.3 | 289.4 | 115.76 | 135.3168 | 145.8 | 142.1 | 162.2 | 157.7 | 253.2 | 19.5 | 21.7 | 34 | 7.4 | 222 | 14.2 | 322.3 | 598 | 601.4 | 310.7 | 365.6 | 86.7 | 333.7 | 391.2 | 80.4 | 297.1 | 15.6 | 23.5 | 37.2 | 36.4 | 160.7 | 137.1 | 25.5 | 69.9 | 52.8 | 40.5
405.3 | 186.3 | 287.3 | 114.92 | 134.3349 | 145.4 | 142.5 | 162.8 | 157.7 | 252.6 | 19.6 | 21.7 | 34 | 9.2 | 218.5 | 13.6 | 323.5 | 615.6 | 614.7 | 311.2 | 367.3 | 87.3 | 335.8 | 397.3 | 80.9 | 299.1 | 15.6 | 23.6 | 37.1 | 36.5 | 161.6 | 137.2 | 25.6 | 70.2 | 53.1 | 40.7
406.3 | 187.3 | 287.3 | 114.92 | 134.3349 | 146.1 | 142.9 | 163 | 157.8 | 254.6 | 19.6 | 21.7 | 34 | 10.1 | 266.6 | 10.7 | 324.9 | 631.4 | 627.2 | 311.8 | 370 | 87.9 | 338.6 | 403.7 | 81.5 | 300.8 | 15.6 | 23.7 | 37.4 | 36.6 | 161.7 | 138.4 | 25.7 | 70.6 | 53.3 | 40.9
407.3 | 188.3 | 287.5 | 115 | 134.4284 | 145.8 | 142.9 | 163.5 | 158.4 | 257.2 | 19.6 | 21.7 | 34.2 | 9.4 | 243.7 | 8.9 | 326.5 | 653.5 | 643.2 | 313 | 372.5 | 88.5 | 343.3 | 416.9 | 82 | 304 | 15.6 | 23.8 | 37.5 | 36.7 | 161.6 | 139.1 | 25.8 | 70.9 | 53.6 | 41.1
408.3 | 189.3 | 287.7 | 115.08 | 134.5219 | 146.2 | 143.2 | 164.2 | 158.5 | 260 | 19.7 | 21.7 | 34.3 | 9.6 | 232 | 9.3 | 328.3 | 672.1 | 648.5 | 314.5 | 374.8 | 89.1 | 351.1 | 433 | 82.7 | 308.6 | 15.7 | 23.9 | 37.6 | 36.8 | 161.7 | 139 | 25.9 | 71.1 | 53.9 | 41.2
409.3 | 190.3 | 287.6 | 115.04 | 134.4751 | 145.8 | 143.2 | 164.7 | 159 | 259.5 | 19.7 | 21.7 | 34.5 | 9.6 | 247.5 | 12.2 | 329.9 | 683.4 | 647.3 | 315.3 | 374.8 | 89.7 | 352.3 | 436 | 83.3 | 309.6 | 15.7 | 24 | 37.6 | 36.9 | 161.8 | 139.8 | 26.1 | 71.3 | 54.3 | 41.4
410.3 | 191.3 | 288 | 115.2 | 134.6622 | 146 | 143.3 | 165 | 158.6 | 258.3 | 19.8 | 21.7 | 34.5 | 9 | 251.5 | 17.7 | 331.6 | 700.4 | 660.3 | 316.6 | 378.2 | 90.4 | 357.4 | 442.1 | 84 | 313.6 | 15.7 | 24.1 | 37.8 | 37 | 162.1 | 140.4 | 26.1 | 71.5 | 54.7 | 41.5
411.3 | 192.3 | 288 | 115.2 | 134.6622 | 147 | 143.3 | 164.9 | 158.8 | 259.4 | 19.8 | 21.7 | 34.5 | 9 | 259.2 | 20.6 | 333.2 | 712.5 | 664.4 | 317.9 | 380 | 91 | 359.8 | 443.9 | 84.6 | 314.4 | 15.7 | 24.2 | 38.1 | 37.1 | 161.9 | 141.3 | 26.3 | 71.9 | 55 | 41.7
412.3 | 193.3 | 288.1 | 115.24 | 134.7089 | 148 | 143.3 | 165.3 | 158.3 | 259.4 | 19.8 | 21.7 | 34.5 | 9.3 | 259.7 | 18.9 | 334.9 | 721.3 | 681.6 | 319.3 | 381.7 | 91.6 | 362.7 | 446.9 | 85.3 | 316.5 | 15.7 | 24.3 | 38.1 | 37.3 | 161.4 | 141.3 | 26.4 | 72.1 | 55.3 | 41.8
413.3 | 194.3 | 288 | 115.2 | 134.6622 | 148 | 144 | 166.2 | 157.8 | 264.9 | 19.9 | 21.7 | 34.6 | 9 | 258.3 | 17 | 336.7 | 735.3 | 683.6 | 321 | 385.5 | 92.2 | 372.4 | 453.6 | 86.2 | 321.8 | 15.7 | 24.3 | 38.3 | 37.4 | 161.2 | 141.1 | 26.5 | 72.2 | 55.6 | 42
414.3 | 195.3 | 288.2 | 115.28 | 134.7557 | 148 | 144.6 | 166.4 | 157.7 | 266.8 | 19.9 | 21.7 | 34.7 | 8.6 | 256.8 | 15.4 | 338.3 | 735.9 | 664.4 | 322.2 | 385.7 | 92.9 | 372.1 | 450.2 | 86.8 | 322.8 | 15.7 | 24.4 | 38.3 | 37.5 | 161.1 | 141.1 | 26.6 | 72.4 | 55.9 | 42.1
415.3 | 196.3 | 289.3 | 115.72 | 135.27 | 148.5 | 144.6 | 166.3 | 158 | 265.5 | 19.8 | 21.7 | 34.7 | 7.7 | 249.5 | 13.5 | 339.9 | 734.7 | 655.3 | 323.4 | 385.4 | 93.5 | 371.4 | 449.6 | 87.5 | 322.7 | 15.8 | 24.5 | 38.4 | 37.6 | 161.1 | 141.2 | 26.7 | 72.7 | 56.3 | 42.2
416.3 | 197.3 | 288 | 115.2 | 134.6622 | 149.3 | 144.9 | 165.7 | 158.6 | 263.7 | 19.8 | 21.7 | 34.7 | 7.1 | 248.5 | 12.7 | 341.2 | 734.4 | 648.9 | 324.5 | 385.1 | 94.2 | 370.5 | 450.4 | 87.9 | 323 | 15.8 | 24.6 | 38.7 | 37.8 | 161.4 | 141.1 | 26.8 | 73 | 56.6 | 42.4
417.3 | 198.3 | 286.2 | 114.48 | 133.8205 | 151 | 144.9 | 165.5 | 159.3 | 265.8 | 19.7 | 21.7 | 34.7 | 7.6 | 249.1 | 11.8 | 342.7 | 737 | 647.6 | 326.1 | 385.9 | 94.8 | 371.4 | 454.2 | 88.4 | 323.1 | 15.8 | 24.7 | 38.9 | 37.9 | 161.4 | 141.2 | 26.9 | 73.1 | 56.9 | 42.5
418.3 | 199.3 | 287 | 114.8 | 134.1946 | 151.4 | 145.3 | 165 | 159.4 | 263.1 | 19.7 | 21.7 | 34.7 | 8.1 | 252.5 | 10.4 | 344.2 | 733.1 | 635.8 | 327.7 | 386.1 | 95.5 | 369.3 | 455 | 88.9 | 322 | 15.8 | 24.8 | 39 | 38.1 | 161.3 | 141.6 | 27 | 73.2 | 57.1 | 42.7
419.3 | 200.3 | 288 | 115.2 | 134.6622 | 152 | 145.9 | 164.6 | 158.9 | 262.5 | 19.8 | 21.7 | 34.8 | 8.6 | 247.3 | 10.7 | 345.7 | 723.5 | 626.7 | 329.1 | 385.6 | 96.1 | 366.1 | 448.7 | 89.1 | 321.3 | 15.8 | 24.9 | 39.1 | 38.2 | 161.7 | 141.8 | 27.1 | 73.4 | 57.4 | 42.8
420.3 | 201.3 | 288.1 | 115.24 | 134.7089 | 151.3 | 145.6 | 164.9 | 159.3 | 260 | 19.8 | 21.7 | 34.9 | 8.3 | 257 | 12.4 | 347.1 | 722 | 621.5 | 330.5 | 385.8 | 96.8 | 362.3 | 444.4 | 89.5 | 321.5 | 15.8 | 25 | 39.1 | 38.3 | 162 | 142 | 27.2 | 73.6 | 57.6 | 43
421.3 | 202.3 | 288.3 | 115.32 | 134.8024 | 151 | 144.7 | 165.7 | 160.5 | 259.2 | 19.9 | 21.7 | 35 | 9.5 | 263.1 | 12.7 | 348.5 | 728.6 | 624.8 | 332.5 | 387.2 | 97.4 | 362.6 | 447.1 | 89.9 | 322.4 | 15.8 | 25.1 | 39.2 | 38.5 | 162.6 | 142.4 | 27.4 | 73.8 | 57.8 | 43.2
422.3 | 203.3 | 288.4 | 115.36 | 134.8492 | 150.5 | 143.4 | 166.4 | 161.1 | 260.7 | 19.9 | 21.7 | 35.1 | 10.1 | 271.4 | 14.5 | 349.9 | 736.9 | 639.4 | 335.2 | 389.5 | 98.1 | 362.2 | 449.2 | 90.4 | 324.2 | 15.9 | 25.1 | 39.3 | 38.6 | 162.9 | 142.5 | 27.4 | 74.1 | 58.1 | 43.4
423.3 | 204.3 | 289.1 | 115.64 | 135.1765 | 151.3 | 142.6 | 166 | 160.9 | 262.7 | 20 | 21.6 | 35.1 | 8.4 | 281.6 | 15 | 351.6 | 744.4 | 644.6 | 336.7 | 392.2 | 98.8 | 364.5 | 450.5 | 91 | 326.4 | 15.9 | 25.2 | 39.5 | 38.7 | 163.3 | 143.1 | 27.6 | 74.4 | 58.3 | 43.6
424.3 | 205.3 | 289.3 | 115.72 | 135.27 | 151.8 | 142.3 | 164.8 | 161.5 | 267.5 | 20 | 21.6 | 35.1 | 8.1 | 279.9 | 15.4 | 353.2 | 752.3 | 648.9 | 338 | 395.6 | 99.4 | 365.4 | 454.1 | 91.6 | 328.2 | 15.9 | 25.3 | 39.7 | 38.8 | 163.8 | 143.6 | 27.7 | 74.6 | 58.6 | 43.7
425.3 | 206.3 | 290.3 | 116.12 | 135.7376 | 150.7 | 143.3 | 164.2 | 162.6 | 268.9 | 20 | 21.6 | 35.1 | 9.2 | 286.3 | 15.9 | 355 | 755.6 | 642.1 | 340.2 | 396.4 | 100.1 | 366.1 | 449.5 | 91.9 | 328.5 | 15.9 | 25.4 | 39.7 | 38.9 | 163.9 | 143.6 | 27.8 | 74.9 | 58.8 | 43.9
426.3 | 207.3 | 288.2 | 115.28 | 134.7557 | 150.3 | 144.1 | 163.8 | 162.8 | 267.1 | 20 | 21.6 | 35.2 | 9 | 289.4 | 14.9 | 356.7 | 743.6 | 633.3 | 342.1 | 395.8 | 100.8 | 366.3 | 442.7 | 92.2 | 329.1 | 15.9 | 25.5 | 39.8 | 39.1 | 164.2 | 143.8 | 27.9 | 75.2 | 59.1 | 44
427.3 | 208.3 | 287.1 | 114.84 | 134.2413 | 150 | 144.7 | 163.8 | 162.9 | 264.3 | 20.1 | 21.6 | 35.2 | 8.5 | 291.5 | 14.4 | 358.3 | 742.3 | 638.6 | 343.7 | 398.2 | 101.5 | 364.2 | 440.8 | 92.6 | 329.7 | 15.9 | 25.6 | 40.2 | 39.2 | 164.5 | 144.2 | 28 | 75.5 | 59.4 | 44.2
428.3 | 209.3 | 287.1 | 114.84 | 134.2413 | 151.3 | 144.1 | 164.4 | 163.4 | 262 | 20.1 | 21.6 | 35.2 | 8.7 | 288 | 13.1 | 359.7 | 744.6 | 634.1 | 344.4 | 397.9 | 102.2 | 359.9 | 429.6 | 93 | 329.6 | 16 | 25.7 | 40.3 | 39.3 | 164.6 | 144.2 | 28.1 | 75.8 | 59.6 | 44.4
429.3 | 210.3 | 287.3 | 114.92 | 134.3349 | 152.2 | 144.2 | 164.9 | 163.7 | 256.7 | 20.1 | 21.6 | 35.3 | 9.1 | 288.4 | 12.6 | 361 | 752.8 | 638.9 | 345.4 | 399.9 | 102.9 | 356.6 | 426.6 | 93.3 | 330.2 | 16 | 25.8 | 40.5 | 39.4 | 164.8 | 144.2 | 28.2 | 76 | 59.9 | 44.5
430.3 | 211.3 | 287.2 | 114.88 | 134.2881 | 151.9 | 144.5 | 164.8 | 163.9 | 256.2 | 20.1 | 21.6 | 35.3 | 9.5 | 293.7 | 13.6 | 361.9 | 751.6 | 619.7 | 346.4 | 399.2 | 103.6 | 353.7 | 422.3 | 93.8 | 330.5 | 16 | 25.9 | 40.5 | 39.5 | 164.8 | 144.6 | 28.3 | 76.2 | 60.1 | 44.7
431.3 | 212.3 | 286.4 | 114.56 | 133.914 | 151.3 | 144 | 164.6 | 163.7 | 253.7 | 20.2 | 21.6 | 35.4 | 8.9 | 297.1 | 13.7 | 362.9 | 744.1 | 613.2 | 346.8 | 398.2 | 104.3 | 349.7 | 418.1 | 94.2 | 329.2 | 16 | 26 | 40.6 | 39.6 | 164.8 | 145.2 | 28.4 | 76.6 | 60.4 | 44.9
432.3 | 213.3 | 287.1 | 114.84 | 134.2413 | 150.8 | 143.5 | 164 | 162.3 | 251.5 | 20.2 | 21.6 | 35.4 | 9.6 | 296.3 | 13.1 | 363.8 | 737 | 619.6 | 348.6 | 397.8 | 105 | 348.3 | 417.2 | 94.6 | 328.8 | 16 | 26 | 40.9 | 39.7 | 164.2 | 145.4 | 28.5 | 76.7 | 60.5 | 45
433.3 | 214.3 | 287.4 | 114.96 | 134.3816 | 150.3 | 142.3 | 164 | 161 | 251.3 | 20.2 | 21.6 | 35.5 | 9.3 | 294.5 | 11.5 | 364.9 | 736.7 | 616.2 | 351 | 399.5 | 105.7 | 346.9 | 408.3 | 94.9 | 329.9 | 16 | 26.1 | 41 | 39.9 | 164.1 | 145.2 | 28.7 | 76.9 | 60.8 | 45.2
434.3 | 215.3 | 287 | 114.8 | 134.1946 | 148.8 | 142.7 | 163.9 | 160.8 | 250.6 | 20.2 | 21.6 | 35.5 | 9.5 | 295.1 | 10.2 | 366.3 | 735.8 | 610.1 | 353.5 | 400.4 | 106.5 | 347.1 | 405.6 | 95.4 | 331 | 16.1 | 26.2 | 41 | 40 | 163.9 | 145 | 28.7 | 77 | 61.1 | 45.3
435.3 | 216.3 | 286.9 | 114.76 | 134.1478 | 148.1 | 143 | 163.3 | 160.8 | 247.6 | 20.2 | 21.6 | 35.6 | 8.2 | 297.9 | 11.9 | 367.7 | 728.8 | 602 | 354.3 | 399.5 | 107.2 | 342.8 | 399.8 | 95.7 | 329.3 | 16.1 | 26.3 | 41.1 | 40.1 | 163.6 | 144.8 | 28.8 | 77.2 | 61.3 | 45.4
436.3 | 217.3 | 287.2 | 114.88 | 134.2881 | 148.1 | 143.1 | 163.5 | 160.5 | 245.5 | 20.2 | 21.6 | 35.7 | 9 | 297.4 | 12.9 | 369 | 728.2 | 600.4 | 357.1 | 400.8 | 108 | 343.2 | 402.6 | 96 | 329.8 | 16.1 | 26.4 | 41.3 | 40.3 | 163.4 | 144.5 | 29 | 77.4 | 61.5 | 45.6
437.3 | 218.3 | 288.8 | 115.52 | 135.0362 | 148.5 | 143.4 | 163.8 | 159.8 | 246 | 20.2 | 21.6 | 35.8 | 8.6 | 292.5 | 13.4 | 370.4 | 731.1 | 604.8 | 360.2 | 401.8 | 108.8 | 343.2 | 401.9 | 96.3 | 330.3 | 16.1 | 26.5 | 41.4 | 40.4 | 163.4 | 144.3 | 29.1 | 77.5 | 61.7 | 45.7
438.3 | 219.3 | 289.1 | 115.64 | 135.1765 | 148.2 | 143.1 | 164 | 159.4 | 246.5 | 20.2 | 21.6 | 35.8 | 8.5 | 289.4 | 13.3 | 372.2 | 727.5 | 614.3 | 364.7 | 402.2 | 109.6 | 345.6 | 408.7 | 96.6 | 331 | 16.1 | 26.6 | 41.5 | 40.5 | 163.3 | 144.6 | 29.2 | 77.7 | 61.9 | 45.8
439.3 | 220.3 | 289 | 115.6 | 135.1297 | 148.5 | 141.3 | 164.5 | 159.4 | 246.8 | 20.1 | 21.6 | 36 | 8.9 | 288.2 | 12.8 | 374.3 | 729.6 | 610.6 | 367.8 | 401.6 | 110.5 | 343.3 | 401.6 | 96.9 | 329.4 | 16.1 | 26.7 | 41.6 | 40.7 | 162.9 | 144.4 | 29.3 | 78 | 62.1 | 45.9
440.3 | 221.3 | 289.5 | 115.8 | 135.3635 | 149.6 | 141.1 | 165 | 159.4 | 247.7 | 20.2 | 21.6 | 36.2 | 8.7 | 282.8 | 12.3 | 376.3 | 732.5 | 609.1 | 369.9 | 403.9 | 111.3 | 344.2 | 410.5 | 97.5 | 329.3 | 16.2 | 26.8 | 41.8 | 40.8 | 162.8 | 144.2 | 29.4 | 78.1 | 62.4 | 46.1
441.3 | 222.3 | 290 | 116 | 135.5973 | 151 | 141.9 | 165.4 | 159.2 | 252.7 | 20.2 | 21.6 | 36.3 | 9.1 | 284.4 | 11.9 | 378.1 | 720.9 | 599 | 371.3 | 403.4 | 112.2 | 344.2 | 408.5 | 97.9 | 328.6 | 16.2 | 26.9 | 42 | 40.9 | 163.2 | 144.6 | 29.5 | 78.3 | 62.6 | 46.3
442.3 | 223.3 | 288.3 | 115.32 | 134.8024 | 150.8 | 140.9 | 165.4 | 158.6 | 250.2 | 20.3 | 21.6 | 36.5 | 9.1 | 282.9 | 11.6 | 379.6 | 720.7 | 587.4 | 372.7 | 402.7 | 113.1 | 340.3 | 406.1 | 98.1 | 327.4 | 16.2 | 27 | 42.1 | 41 | 162.8 | 145 | 29.6 | 78.5 | 62.8 | 46.4
443.3 | 224.3 | 288 | 115.2 | 134.6622 | 150.6 | 140.5 | 165.7 | 158.5 | 247.9 | 20.3 | 21.6 | 36.5 | 8.2 | 288.8 | 10.7 | 380.9 | 708.1 | 584.9 | 375.5 | 403.5 | 114 | 338.1 | 407.3 | 98.3 | 327.6 | 16.2 | 27.1 | 42.2 | 41.2 | 162.8 | 144.9 | 29.7 | 78.7 | 63.1 | 46.6
444.3 | 225.3 | 287.8 | 115.12 | 134.5686 | 150.2 | 140.9 | 165.3 | 158.8 | 249.8 | 20.4 | 21.6 | 36.5 | 7.4 | 293.7 | 9.7 | 382.5 | 702.1 | 578.6 | 378.2 | 403.9 | 114.9 | 336.7 | 405.9 | 98.6 | 327.2 | 16.2 | 27.2 | 42.3 | 41.3 | 163.2 | 144.8 | 29.8 | 78.8 | 63.3 | 46.7
445.3 | 226.3 | 288.1 | 115.24 | 134.7089 | 148.7 | 140.8 | 165.1 | 159 | 251.3 | 20.4 | 21.6 | 36.5 | 7.4 | 294 | 9.4 | 384.1 | 702.1 | 575.9 | 380.6 | 404.9 | 115.8 | 335.3 | 402.3 | 99 | 327.5 | 16.2 | 27.3 | 42.5 | 41.4 | 163.4 | 145 | 29.9 | 79 | 63.5 | 46.8
446.3 | 227.3 | 290.2 | 116.08 | 135.6908 | 147.9 | 140.3 | 165.2 | 158.6 | 250.4 | 20.4 | 21.6 | 36.5 | 7.4 | 272.9 | 8.5 | 385.8 | 688.3 | 572.8 | 382.7 | 404.7 | 116.7 | 332.7 | 394.7 | 99.2 | 326.1 | 16.3 | 27.4 | 42.6 | 41.5 | 163.3 | 144.9 | 30 | 79.2 | 63.8 | 47
447.3 | 228.3 | 289.1 | 115.64 | 135.1765 | 148.1 | 140.5 | 165.2 | 158.3 | 247.6 | 20.5 | 21.6 | 36.5 | 6.5 | 289.3 | 7.7 | 387.7 | 680.2 | 567.7 | 385.1 | 404.6 | 117.6 | 329.4 | 386.8 | 99.4 | 325 | 16.3 | 27.4 | 42.6 | 41.6 | 163.1 | 145.1 | 30.1 | 79.4 | 64 | 47.1
448.3 | 229.3 | 287.4 | 114.96 | 134.3816 | 148.2 | 141.5 | 164.7 | 157.1 | 245.7 | 20.5 | 21.6 | 36.4 | 6.5 | 289.1 | 7.2 | 389.5 | 665.1 | 565.1 | 386.1 | 403.7 | 118.5 | 325.1 | 377.8 | 99.6 | 323.6 | 16.3 | 27.5 | 42.6 | 41.7 | 163.1 | 144.7 | 30.2 | 79.5 | 64.2 | 47.3
449.3 | 230.3 | 287.5 | 115 | 134.4284 | 149.6 | 141.9 | 164.5 | 155.9 | 241.5 | 20.5 | 21.6 | 36.4 | 6.2 | 292.2 | 7.1 | 391.1 | 654.2 | 549.1 | 386.3 | 402.2 | 119.4 | 321.2 | 368.3 | 99.8 | 322.3 | 16.3 | 27.6 | 42.8 | 41.8 | 162.8 | 144.4 | 30.3 | 79.8 | 64.4 | 47.4
450.3 | 231.3 | 287.9 | 115.16 | 134.6154 | 150.7 | 141.4 | 164.3 | 155.9 | 237.8 | 20.5 | 21.6 | 36.4 | 6.8 | 300.2 | 7.1 | 392.2 | 646.7 | 538.8 | 385.9 | 401.5 | 120.3 | 316.3 | 363.2 | 100 | 320.8 | 16.3 | 27.7 | 42.9 | 41.9 | 162.3 | 144.1 | 30.4 | 79.9 | 64.5 | 47.5
451.3 | 232.3 | 287.9 | 115.16 | 134.6154 | 151.6 | 141.8 | 164.2 | 156 | 238.4 | 20.6 | 21.6 | 36.4 | 7 | 310.9 | 6.5 | 393.2 | 631.2 | 545.9 | 388.2 | 401.4 | 121.2 | 313.9 | 362.4 | 100.2 | 319.8 | 16.3 | 27.8 | 43 | 42.1 | 161.9 | 144.1 | 30.6 | 79.9 | 64.7 | 47.7
452.3 | 233.3 | 288.1 | 115.24 | 134.7089 | 151.6 | 141.6 | 164.6 | 155.8 | 238.1 | 20.6 | 21.6 | 36.5 | 7.1 | 297.5 | 6.2 | 394.6 | 625.1 | 550.7 | 392.1 | 402.9 | 122.1 | 313.2 | 365.3 | 100.5 | 319.2 | 16.4 | 27.9 | 43.2 | 42.1 | 161.5 | 143.8 | 30.7 | 80 | 64.9 | 47.8
453.3 | 234.3 | 288 | 115.2 | 134.6622 | 151.1 | 142.5 | 165.3 | 155.6 | 240.3 | 20.7 | 21.6 | 36.6 | 7.6 | 282.5 | 7.2 | 396.4 | 622.4 | 547.6 | 395.1 | 403 | 123 | 312.2 | 367.7 | 100.7 | 318.4 | 16.4 | 28 | 43.5 | 42.2 | 161 | 143.7 | 30.8 | 80.2 | 65.1 | 47.9
454.3 | 235.3 | 287.2 | 114.88 | 134.2881 | 150.4 | 143.7 | 164.9 | 156.1 | 243.7 | 20.7 | 21.6 | 36.6 | 7.6 | 285.8 | 7.6 | 398.4 | 624.2 | 554.1 | 398.9 | 403.8 | 123.9 | 313.9 | 370 | 100.9 | 319.2 | 16.4 | 28.1 | 43.5 | 42.3 | 160.7 | 143.7 | 30.9 | 80.5 | 65.3 | 48
455.3 | 236.3 | 285.8 | 114.32 | 133.6335 | 149.6 | 143.9 | 164.8 | 156.2 | 245.8 | 20.7 | 21.6 | 36.7 | 8.1 | 294.4 | 7.8 | 400.6 | 616.9 | 542.3 | 402.1 | 402.5 | 124.8 | 314.5 | 366.6 | 101.3 | 319.7 | 16.4 | 28.2 | 43.6 | 42.4 | 160.8 | 143.7 | 31 | 80.6 | 65.5 | 48.2
456.3 | 237.3 | 286.5 | 114.6 | 133.9608 | 149.8 | 143.4 | 164.4 | 156.3 | 242.5 | 20.8 | 21.6 | 36.8 | 8.1 | 292 | 8.3 | 402.7 | 615.7 | 537.4 | 404.9 | 402.3 | 125.6 | 313.7 | 362.3 | 101.6 | 319.9 | 16.4 | 28.3 | 43.6 | 42.5 | 161.2 | 143.6 | 31.1 | 80.8 | 65.7 | 48.3
457.3 | 238.3 | 286.4 | 114.56 | 133.914 | 149.5 | 144.1 | 164.7 | 157 | 240.2 | 20.8 | 21.6 | 36.9 | 8.3 | 289.1 | 8.9 | 404.7 | 616.8 | 538.5 | 407.7 | 402.6 | 126.5 | 315.1 | 359.8 | 102.2 | 320.8 | 16.4 | 28.3 | 43.9 | 42.6 | 161.7 | 144 | 31.2 | 81 | 65.9 | 48.5
458.3 | 239.3 | 287.5 | 115 | 134.4284 | 149 | 144.7 | 164.9 | 157.5 | 237.8 | 20.8 | 21.6 | 36.9 | 8 | 287.8 | 9.4 | 406.6 | 606 | 537.5 | 409.6 | 401.9 | 127.3 | 314.5 | 359.9 | 102.7 | 320.5 | 16.5 | 28.4 | 44 | 42.7 | 161.5 | 144.7 | 31.3 | 81.2 | 66.1 | 48.7
459.3 | 240.3 | 287.6 | 115.04 | 134.4751 | 149.4 | 145.2 | 164.7 | 157.2 | 237.4 | 20.9 | 21.6 | 37 | 7.9 | 284.2 | 8.5 | 408.5 | 611.1 | 548 | 412.5 | 404.7 | 128.2 | 316.1 | 361.3 | 103.3 | 321.2 | 16.5 | 28.5 | 44.2 | 42.8 | 161.7 | 144.8 | 31.5 | 81.3 | 66.3 | 48.8
460.3 | 241.3 | 289.5 | 115.8 | 135.3635 | 149.4 | 145.2 | 165 | 157 | 238.4 | 20.9 | 21.6 | 37 | 7.5 | 298.2 | 7.8 | 410.6 | 615.1 | 560.3 | 416.3 | 406.8 | 129 | 317.3 | 363.4 | 103.9 | 321.4 | 16.5 | 28.6 | 44.3 | 42.8 | 162.1 | 144.7 | 31.6 | 81.5 | 66.5 | 48.9
461.3 | 242.3 | 289.4 | 115.76 | 135.3168 | 149.5 | 145.3 | 165.6 | 156.9 | 243 | 21 | 21.6 | 37.1 | 7 | 286.3 | 6.8 | 413.2 | 628.2 | 578.5 | 420.6 | 408.3 | 129.8 | 320.5 | 363.6 | 104.5 | 323.4 | 16.5 | 28.7 | 44.4 | 42.9 | 162.3 | 145 | 31.6 | 81.7 | 66.7 | 49.1
462.3 | 243.3 | 290.2 | 116.08 | 135.6908 | 149 | 144.7 | 165.3 | 157.1 | 242.6 | 21 | 21.6 | 37.1 | 7.3 | 302.2 | 6.1 | 416.3 | 637.5 | 584 | 424.6 | 409.9 | 130.6 | 323.8 | 365.1 | 105.1 | 325.2 | 16.6 | 28.8 | 44.7 | 43 | 162 | 145.1 | 31.8 | 81.9 | 66.9 | 49.2
463.3 | 244.3 | 287.6 | 115.04 | 134.4751 | 148.1 | 145.3 | 165.3 | 156.9 | 243.4 | 21.1 | 21.6 | 37.2 | 7.1 | 346 | 5.4 | 419.6 | 643.7 | 601.4 | 429.3 | 411.6 | 131.4 | 328 | 371.2 | 105.6 | 327 | 16.6 | 28.9 | 44.8 | 43.1 | 161.8 | 145.1 | 31.9 | 82.1 | 67.2 | 49.4
464.3 | 245.3 | 287.7 | 115.08 | 134.5219 | 147.9 | 144.6 | 165.8 | 155.9 | 247.4 | 21.1 | 21.6 | 37.2 | 7.8 | 274.9 | 4.5 | 423.1 | 654.1 | 604.8 | 433.9 | 413.2 | 132.3 | 333.7 | 372.4 | 106.5 | 328.3 | 16.6 | 29 | 44.8 | 43.2 | 161.6 | 145 | 32 | 82.3 | 67.4 | 49.5
465.3 | 246.3 | 287.7 | 115.08 | 134.5219 | 148.7 | 143.7 | 166.1 | 155.7 | 248.7 | 21.1 | 21.6 | 37.3 | 7.4 | 268.1 | 4.8 | 426.7 | 656.6 | 607.1 | 438.2 | 413 | 133.1 | 334.8 | 377.6 | 106.9 | 327.7 | 16.6 | 29.1 | 44.9 | 43.3 | 161.6 | 144.8 | 32.1 | 82.6 | 67.6 | 49.7
466.3 | 247.3 | 287.5 | 115 | 134.4284 | 150.2 | 143.3 | 166.4 | 156.3 | 248.4 | 21.1 | 21.6 | 37.3 | 7.2 | 311.7 | 5.5 | 430.4 | 652.3 | 605.9 | 440.4 | 413 | 133.9 | 332.2 | 374.8 | 107.1 | 327 | 16.6 | 29.2 | 45.1 | 43.4 | 161.9 | 144.7 | 32.2 | 82.8 | 67.9 | 49.8
467.3 | 248.3 | 287.7 | 115.08 | 134.5219 | 151.1 | 143.5 | 166.6 | 157.2 | 245.1 | 21.1 | 21.6 | 37.4 | 7.5 | 324.9 | 5.7 | 433.7 | 661 | 620.2 | 443.4 | 414.7 | 134.7 | 331.9 | 376.1 | 107.3 | 327.6 | 16.6 | 29.3 | 45.1 | 43.5 | 161.9 | 144.5 | 32.3 | 82.9 | 68.1 | 49.9
468.3 | 249.3 | 288.4 | 115.36 | 134.8492 | 151.1 | 143.1 | 166.8 | 157.4 | 245.6 | 21.1 | 21.6 | 37.4 | 7.6 | 336.6 | 6.1 | 436.8 | 668.7 | 619.8 | 446.4 | 416.4 | 135.5 | 331.9 | 376.4 | 107.7 | 328.3 | 16.7 | 29.3 | 45.3 | 43.6 | 162 | 144.4 | 32.5 | 83 | 68.3 | 50.1
469.3 | 250.3 | 289.6 | 115.84 | 135.4103 | 151 | 142.7 | 166.2 | 156.8 | 247.6 | 21.2 | 21.6 | 37.4 | 7.7 | 331.9 | 7.5 | 440.1 | 680.3 | 620.3 | 450.1 | 419 | 136.4 | 334 | 385.8 | 108.3 | 328.9 | 16.7 | 29.4 | 45.4 | 43.7 | 162 | 144.5 | 32.6 | 83.1 | 68.6 | 50.2
470.3 | 251.3 | 289.5 | 115.8 | 135.3635 | 150.8 | 142.3 | 165.7 | 156.8 | 249.2 | 21.2 | 21.6 | 37.4 | 7.4 | 325.3 | 7.1 | 443.5 | 690.7 | 614.8 | 454.9 | 419 | 137.2 | 337.9 | 392.4 | 109.1 | 329.7 | 16.7 | 29.5 | 45.6 | 43.7 | 161.7 | 144.6 | 32.7 | 83.3 | 68.8 | 50.4
471.3 | 252.3 | 289.5 | 115.8 | 135.3635 | 151.3 | 142.2 | 165.5 | 157.5 | 249 | 21.3 | 21.6 | 37.4 | 7 | 337.7 | 6.5 | 447.3 | 683.3 | 602.5 | 458.4 | 418.2 | 138 | 336.1 | 386.5 | 109.6 | 329 | 16.7 | 29.6 | 45.6 | 43.8 | 162.2 | 144.5 | 32.8 | 83.4 | 69.1 | 50.5
472.3 | 253.3 | 289.3 | 115.72 | 135.27 | 151 | 142 | 165.4 | 158.1 | 249.2 | 21.3 | 21.6 | 37.5 | 6.7 | 316.1 | 5.6 | 451.1 | 679.8 | 590 | 461.4 | 416.8 | 138.8 | 334.2 | 383.6 | 109.9 | 329.3 | 16.8 | 29.7 | 45.7 | 43.9 | 162.4 | 144.6 | 32.9 | 83.6 | 69.3 | 50.7
473.3 | 254.3 | 287.5 | 115 | 134.4284 | 152.2 | 142.5 | 165.3 | 158.3 | 249.2 | 21.3 | 21.6 | 37.5 | 7.4 | 320.4 | 5 | 454.8 | 673.7 | 587.7 | 465.4 | 417.3 | 139.7 | 334 | 380.5 | 110.1 | 329.5 | 16.8 | 29.8 | 46.1 | 44 | 162.5 | 144.5 | 33 | 83.9 | 69.5 | 50.9
474.3 | 255.3 | 287.3 | 114.92 | 134.3349 | 152.4 | 142.7 | 165.9 | 158.3 | 247.5 | 21.3 | 21.6 | 37.6 | 7.1 | 348.6 | 5.3 | 458.3 | 666.5 | 579.2 | 469 | 417.5 | 140.5 | 333.3 | 376.9 | 110.4 | 329.9 | 16.8 | 29.9 | 46.1 | 44.1 | 162.9 | 144.8 | 33.1 | 84.2 | 69.7 | 51
475.3 | 256.3 | 287.8 | 115.12 | 134.5686 | 152.6 | 143.1 | 165.8 | 159.1 | 245.2 | 21.3 | 21.6 | 37.6 | 6.9 | 320.7 | 4.5 | 461.1 | 657.8 | 575.6 | 472.6 | 416.5 | 141.3 | 332.6 | 380.5 | 110.9 | 329.4 | 16.8 | 30 | 46.3 | 44.2 | 163.6 | 144.7 | 33.2 | 84.4 | 70 | 51.2
476.3 | 257.3 | 286.3 | 114.52 | 133.8673 | 153.5 | 144 | 166 | 159.8 | 245.5 | 21.2 | 21.6 | 37.6 | 6.6 | 294.6 | 4.5 | 464.2 | 653.9 | 569.9 | 475.9 | 416 | 142.1 | 333.5 | 381.9 | 111.3 | 329.9 | 16.8 | 30.1 | 46.3 | 44.3 | 164 | 144.9 | 33.4 | 84.7 | 70.2 | 51.4
477.3 | 258.3 | 286.2 | 114.48 | 133.8205 | 154.1 | 144.9 | 166.8 | 160.1 | 245.2 | 21.2 | 21.6 | 37.6 | 6.8 | 290.1 | 5.2 | 467.4 | 646.2 | 567.6 | 478.4 | 415.7 | 142.9 | 332.6 | 380.8 | 111.5 | 330.1 | 16.9 | 30.2 | 46.5 | 44.4 | 164.1 | 145.4 | 33.5 | 84.9 | 70.4 | 51.5
478.3 | 259.3 | 286.7 | 114.68 | 134.0543 | 155.2 | 145.8 | 166.8 | 160.5 | 246.1 | 21.2 | 21.6 | 37.6 | 6.5 | 275.8 | 5 | 470.2 | 650.2 | 574.1 | 482.2 | 417.4 | 143.7 | 333.6 | 384.9 | 112.1 | 331.2 | 16.9 | 30.3 | 46.6 | 44.5 | 164.3 | 145.5 | 33.6 | 85.1 | 70.6 | 51.6
479.3 | 260.3 | 286.6 | 114.64 | 134.0076 | 155.8 | 145.9 | 166.9 | 160.3 | 248.2 | 21.2 | 21.6 | 37.7 | 6.5 | 260.1 | 5.6 | 473.4 | 652.3 | 554.9 | 485.7 | 415.5 | 144.5 | 333.3 | 381.7 | 112.3 | 331.9 | 16.9 | 30.4 | 46.6 | 44.6 | 164.2 | 145.5 | 33.7 | 85.4 | 70.8 | 51.8
480.3 | 261.3 | 287.2 | 114.88 | 134.2881 | 156.3 | 146.4 | 167 | 160.6 | 246.9 | 21.3 | 21.6 | 37.7 | 6.4 | 271.7 | 5.8 | 476.2 | 648.2 | 545.2 | 488.4 | 414 | 145.3 | 331.2 | 377.6 | 112.5 | 331.1 | 16.9 | 30.5 | 46.7 | 44.7 | 164.3 | 145.7 | 33.8 | 85.6 | 71 | 52
481.3 | 262.3 | 286.6 | 114.64 | 134.0076 | 157 | 147.2 | 167.5 | 161 | 243.7 | 21.4 | 21.6 | 37.8 | 6 | 265.4 | 5.9 | 478.5 | 643.3 | 548.2 | 492.1 | 414.4 | 146.1 | 329.1 | 372.2 | 112.9 | 330.4 | 16.9 | 30.6 | 46.9 | 44.8 | 164.4 | 146.3 | 33.9 | 85.7 | 71.2 | 52.1
482.3 | 263.3 | 289.3 | 115.72 | 135.27 | 156.7 | 147.2 | 167.8 | 161 | 242.5 | 21.4 | 21.6 | 37.9 | 6.3 | 260.5 | 5.7 | 480.9 | 650.7 | 553 | 497.4 | 415 | 146.9 | 329.2 | 370.3 | 113.4 | 331.4 | 16.9 | 30.7 | 47.2 | 44.9 | 164.8 | 147 | 34 | 85.9 | 71.4 | 52.3
483.3 | 264.3 | 289.1 | 115.64 | 135.1765 | 156.5 | 146.7 | 168.3 | 160.8 | 245.2 | 21.5 | 21.6 | 38 | 6.9 | 254.1 | 5.6 | 484.2 | 642.2 | 559.3 | 502.3 | 415.8 | 147.7 | 328.2 | 369.5 | 114 | 330.9 | 17 | 30.8 | 47.3 | 44.9 | 164.6 | 148 | 34.1 | 86.2 | 71.6 | 52.4
484.3 | 265.3 | 289 | 115.6 | 135.1297 | 155.5 | 146.7 | 168.1 | 160.9 | 244.4 | 21.6 | 21.6 | 38 | 6.8 | 265.3 | 5.4 | 487.7 | 639 | 546.8 | 506.7 | 414.5 | 148.5 | 324.9 | 364.5 | 114.5 | 330.2 | 17 | 30.9 | 47.5 | 45.1 | 164.3 | 148.1 | 34.3 | 86.5 | 71.8 | 52.6
485.3 | 266.3 | 289.8 | 115.92 | 135.5038 | 155 | 147.8 | 167.9 | 161.5 | 243.6 | 21.6 | 21.6 | 38 | 7 | 251.3 | 4.8 | 490.2 | 632.7 | 550.3 | 510.9 | 414.2 | 149.3 | 322.2 | 361.1 | 114.7 | 329.3 | 17 | 31 | 47.5 | 45.2 | 164.8 | 148.3 | 34.4 | 86.7 | 72 | 52.7
486.3 | 267.3 | 289.5 | 115.8 | 135.3635 | 155.6 | 147.8 | 168.2 | 161.9 | 241.6 | 21.6 | 21.6 | 38.1 | 6.9 | 240.6 | 4.4 | 492.3 | 624.7 | 534.7 | 514.9 | 412.8 | 150.1 | 319.6 | 357 | 115 | 327.9 | 17 | 31 | 47.6 | 45.3 | 164.8 | 148.7 | 34.5 | 86.9 | 72.2 | 52.9
487.3 | 268.3 | 288.9 | 115.56 | 135.083 | 156.8 | 146.4 | 167.8 | 162.4 | 238.3 | 21.6 | 21.6 | 38.1 | 6.8 | 250.9 | 3.9 | 494.3 | 614.2 | 519.1 | 517.2 | 412.1 | 150.9 | 315.2 | 349 | 115.1 | 326.3 | 17 | 31.1 | 47.8 | 45.4 | 165.4 | 148.6 | 34.6 | 87.2 | 72.4 | 53
488.3 | 269.3 | 288.4 | 115.36 | 134.8492 | 157.8 | 145.4 | 168 | 163.2 | 235 | 21.6 | 21.6 | 38.1 | 6.6 | 265.2 | 3.8 | 496.1 | 599.3 | 502.1 | 519.5 | 410.5 | 151.6 | 310 | 342.3 | 115.1 | 325 | 17.1 | 31.2 | 47.7 | 45.5 | 166.2 | 149.3 | 34.7 | 87.4 | 72.6 | 53.2
489.3 | 270.3 | 288.9 | 115.56 | 135.083 | 159.3 | 146.1 | 168.5 | 163.1 | 231.9 | 21.6 | 21.6 | 38.1 | 6.7 | 279.9 | 3.9 | 497.4 | 591.2 | 502.6 | 521 | 410 | 152.4 | 306.1 | 337.3 | 115.2 | 323.8 | 17.1 | 31.3 | 47.9 | 45.6 | 166.3 | 150 | 34.8 | 87.7 | 72.8 | 53.4
490.3 | 271.3 | 289.6 | 115.84 | 135.4103 | 161.3 | 147.1 | 169.4 | 161.9 | 231.3 | 21.6 | 21.6 | 38.2 | 6.6 | 287.6 | 4.1 | 498.7 | 589.7 | 505.6 | 524.2 | 409.8 | 153.2 | 304.5 | 335 | 115.6 | 323.1 | 17.1 | 31.4 | 48 | 45.7 | 166.3 | 150.1 | 35 | 87.9 | 72.9 | 53.5
491.3 | 272.3 | 290.3 | 116.12 | 135.7376 | 160.4 | 148.3 | 169.5 | 161.4 | 229.9 | 21.6 | 21.6 | 38.2 | 7 | 263.5 | 4 | 500.4 | 601.5 | 517.5 | 527.4 | 410.3 | 153.9 | 302.9 | 341.8 | 115.7 | 323 | 17.1 | 31.5 | 48.2 | 45.8 | 166.2 | 150.2 | 35 | 87.9 | 73.1 | 53.7
492.3 | 273.3 | 287.8 | 115.12 | 134.5686 | 160.8 | 148.9 | 168.9 | 161.7 | 233.3 | 21.6 | 21.6 | 38.3 | 6.9 | 261.2 | 3.8 | 502.7 | 598.2 | 515.1 | 532.6 | 410.8 | 154.6 | 302.7 | 342.6 | 116.2 | 323.2 | 17.1 | 31.6 | 48.5 | 45.9 | 166.2 | 150.1 | 35.2 | 88.1 | 73.2 | 53.8
493.3 | 274.3 | 287.7 | 115.08 | 134.5219 | 161 | 149 | 167.9 | 161.2 | 235 | 21.6 | 21.6 | 38.4 | 6.7 | 273.5 | 3.8 | 505.4 | 598.4 | 516.7 | 537.1 | 410.2 | 155.3 | 300.4 | 344.3 | 116.3 | 322.4 | 17.2 | 31.7 | 48.7 | 46 | 166 | 150 | 35.3 | 88.3 | 73.4 | 54
494.3 | 275.3 | 287.8 | 115.12 | 134.5686 | 160.9 | 150 | 167.4 | 161 | 235.1 | 21.6 | 21.6 | 38.5 | 7.5 | 274 | 3.9 | 508.2 | 607.1 | 533 | 543.4 | 411.9 | 156 | 302.6 | 351.4 | 116.9 | 322.9 | 17.2 | 31.8 | 48.7 | 46.2 | 165.8 | 149.8 | 35.4 | 88.6 | 73.6 | 54.1
495.3 | 276.3 | 288.1 | 115.24 | 134.7089 | 160.7 | 150.6 | 167.8 | 160.6 | 237.3 | 21.6 | 21.5 | 38.7 | 6.6 | 259.2 | 4.3 | 512.4 | 619.2 | 542.1 | 549.1 | 413.7 | 156.6 | 306.1 | 354.2 | 117.5 | 324.2 | 17.2 | 31.9 | 48.8 | 46.3 | 165.8 | 149.6 | 35.5 | 88.9 | 73.8 | 54.2
496.3 | 277.3 | 288.2 | 115.28 | 134.7557 | 159.5 | 151.4 | 167.7 | 161 | 237 | 21.6 | 21.6 | 38.8 | 6.8 | 256 | 5 | 516.7 | 622.3 | 543.5 | 554.5 | 413.5 | 157.3 | 308.6 | 357.4 | 117.8 | 324.9 | 17.2 | 32 | 48.9 | 46.4 | 165.8 | 149.3 | 35.6 | 89.1 | 74 | 54.4
497.3 | 278.3 | 286.7 | 114.68 | 134.0543 | 158.8 | 151.6 | 167.8 | 161.5 | 237.9 | 21.6 | 21.5 | 39 | 6 | 262.6 | 5.3 | 520.4 | 622.7 | 537 | 560.1 | 414.3 | 157.9 | 310.7 | 355.5 | 118.1 | 325.8 | 17.3 | 32.1 | 49 | 46.5 | 165.8 | 149.2 | 35.7 | 89.4 | 74.2 | 54.5
498.3 | 279.3 | 288 | 115.2 | 134.6622 | 158.4 | 150.4 | 168.3 | 161.3 | 236.6 | 21.6 | 21.5 | 39.1 | 6.8 | 261 | 5.4 | 523.5 | 617.7 | 525.2 | 565.7 | 412.9 | 158.6 | 310 | 351.6 | 118.1 | 325.1 | 17.3 | 32.2 | 49.1 | 46.6 | 166 | 149.6 | 35.8 | 89.5 | 74.4 | 54.7
499.3 | 280.3 | 288.8 | 115.52 | 135.0362 | 157.5 | 149.6 | 168.3 | 160.5 | 235 | 21.6 | 21.5 | 39.2 | 6.1 | 256.7 | 5.1 | 526.4 | 606.2 | 523 | 569.6 | 411.8 | 159.2 | 308.6 | 348.3 | 118 | 324.2 | 17.3 | 32.2 | 49.3 | 46.7 | 166.1 | 149.7 | 36 | 89.7 | 74.6 | 54.8
500.3 | 281.3 | 288.4 | 115.36 | 134.8492 | 156.2 | 149.7 | 169.2 | 159.7 | 234.6 | 21.7 | 21.5 | 39.3 | 6.2 | 252.4 | 5.1 | 528.5 | 610.2 | 542.1 | 574.3 | 413.1 | 159.9 | 310 | 355.3 | 118.1 | 324.9 | 17.3 | 32.3 | 49.5 | 46.9 | 166.3 | 149.9 | 36.1 | 90 | 74.8 | 55
501.3 | 282.3 | 288.8 | 115.52 | 135.0362 | 155.3 | 150 | 169.8 | 159.2 | 236.5 | 21.7 | 21.5 | 39.3 | 6.2 | 247.1 | 5.1 | 531.2 | 626.4 | 561.6 | 579.3 | 415.7 | 160.5 | 314 | 359.6 | 118.8 | 326.6 | 17.3 | 32.4 | 49.6 | 47 | 166.2 | 150 | 36.2 | 90.3 | 75 | 55.1
502.3 | 283.3 | 288.1 | 115.24 | 134.7089 | 155.1 | 150 | 170 | 160.2 | 238.9 | 21.7 | 21.5 | 39.3 | 6.2 | 247.9 | 5 | 534.7 | 632.6 | 584.7 | 585.1 | 418.8 | 161.1 | 316.9 | 367.1 | 119.8 | 328.8 | 17.4 | 32.5 | 49.7 | 47.1 | 166.1 | 149.9 | 36.3 | 90.5 | 75.2 | 55.3
503.3 | 284.3 | 288.1 | 115.24 | 134.7089 | 154.8 | 150.6 | 170 | 160.5 | 242.3 | 21.6 | 21.5 | 39.3 | 6.9 | 250.1 | 4.7 | 539.1 | 644.2 | 595.4 | 591.1 | 420.4 | 161.8 | 327.1 | 381.7 | 120.9 | 331.1 | 17.4 | 32.6 | 49.9 | 47.2 | 166.3 | 149.9 | 36.4 | 90.6 | 75.5 | 55.4
504.3 | 285.3 | 289.8 | 115.92 | 135.5038 | 155.2 | 151.2 | 169.8 | 160.9 | 245.5 | 21.7 | 21.5 | 39.4 | 6.7 | 242.9 | 4.4 | 543.8 | 652.2 | 589.6 | 596.6 | 420.9 | 162.4 | 331.2 | 384.4 | 121.3 | 333.1 | 17.4 | 32.7 | 49.9 | 47.3 | 166.3 | 150 | 36.6 | 90.9 | 75.8 | 55.5
505.3 | 286.3 | 289.4 | 115.76 | 135.3168 | 155.9 | 151.5 | 169.3 | 161.8 | 244 | 21.7 | 21.5 | 39.5 | 6 | 223.7 | 4.5 | 548.3 | 654.7 | 577.9 | 600.2 | 420.1 | 163 | 331.3 | 379.9 | 121.4 | 332.2 | 17.4 | 32.8 | 50 | 47.4 | 166.4 | 150.1 | 36.7 | 91 | 76.1 | 55.7
506.3 | 287.3 | 289.3 | 115.72 | 135.27 | 155.7 | 152 | 169.4 | 162.9 | 242.5 | 21.7 | 21.5 | 39.5 | 6.8 | 223.5 | 4.8 | 552.1 | 660.3 | 579.1 | 604.1 | 420.8 | 163.6 | 331.4 | 381.4 | 121.6 | 332.8 | 17.5 | 32.9 | 50.3 | 47.5 | 166.4 | 150.1 | 36.7 | 91.1 | 76.3 | 55.8
507.3 | 288.3 | 289.2 | 115.68 | 135.2233 | 155.9 | 151.6 | 169.7 | 163 | 242.6 | 21.7 | 21.5 | 39.6 | 6.7 | 245.6 | 4.6 | 555.6 | 653.5 | 568.9 | 608.7 | 420.1 | 164.3 | 330.5 | 377.5 | 121.9 | 332.7 | 17.5 | 33 | 50.3 | 47.6 | 166.9 | 150.1 | 36.9 | 91.2 | 76.5 | 56
508.3 | 289.3 | 289.2 | 115.68 | 135.2233 | 154.8 | 150.8 | 170.4 | 163.6 | 243.7 | 21.7 | 21.5 | 39.6 | 6.5 | 237.4 | 4.3 | 558.8 | 647.1 | 556.5 | 612 | 419.8 | 164.9 | 331.3 | 373 | 122 | 332.8 | 17.5 | 33.1 | 50.5 | 47.7 | 167.3 | 150 | 37 | 91.5 | 76.7 | 56.1
509.3 | 290.3 | 288 | 115.2 | 134.6622 | 154.3 | 149.7 | 171.5 | 164.1 | 243.3 | 21.7 | 21.5 | 39.6 | 6.6 | 234 | 4 | 561.8 | 640.7 | 547.7 | 614.8 | 419.7 | 165.4 | 330.3 | 370 | 122.1 | 332.5 | 17.5 | 33.2 | 50.6 | 47.8 | 167.7 | 150.5 | 37.1 | 91.7 | 76.9 | 56.3
510.3 | 291.3 | 288.9 | 115.56 | 135.083 | 156.7 | 148.1 | 172.4 | 164 | 242.9 | 21.8 | 21.5 | 39.6 | 7.3 | 246.9 | 4.5 | 564.3 | 643.7 | 544.5 | 617.2 | 420.3 | 166 | 328.3 | 364.5 | 122.3 | 332 | 17.6 | 33.3 | 50.9 | 47.9 | 167.6 | 151.2 | 37.2 | 91.9 | 77.2 | 56.4
511.3 | 292.3 | 288.7 | 115.48 | 134.9895 | 157.5 | 147.3 | 172.4 | 163.8 | 243.4 | 21.8 | 21.5 | 39.5 | 8.1 | 247.8 | 5.1 | 566.7 | 644.7 | 549.6 | 620.1 | 420.6 | 166.5 | 328 | 366.2 | 122.4 | 331.8 | 17.6 | 33.4 | 51.1 | 48 | 167.6 | 151.3 | 37.3 | 92 | 77.4 | 56.6
512.3 | 293.3 | 288.6 | 115.44 | 134.9427 | 156.5 | 147.5 | 172.5 | 164.1 | 246.2 | 21.9 | 21.5 | 39.5 | 8.3 | 223.9 | 4.9 | 569.4 | 646.6 | 549.7 | 622.9 | 420.5 | 167 | 328.2 | 365.1 | 122.6 | 332.4 | 17.6 | 33.5 | 51.3 | 48.2 | 167.7 | 151.3 | 37.4 | 92.1 | 77.6 | 56.7
513.3 | 294.3 | 288.5 | 115.4 | 134.896 | 156.7 | 147.2 | 173.2 | 164.9 | 248.2 | 21.9 | 21.5 | 39.6 | 8 | 233 | 4.4 | 572.1 | 649.7 | 543.3 | 624.5 | 421.5 | 167.5 | 330 | 376.1 | 122.7 | 333 | 17.6 | 33.6 | 51.4 | 48.3 | 167.4 | 151.4 | 37.6 | 92.4 | 77.8 | 56.8
514.3 | 295.3 | 288.4 | 115.36 | 134.8492 | 157.5 | 147.8 | 173 | 165.7 | 251.7 | 22 | 21.5 | 39.7 | 9 | 262.3 | 4.3 | 575.5 | 647.6 | 542.9 | 626.4 | 421.3 | 168 | 329.8 | 378.4 | 123 | 332.6 | 17.7 | 33.7 | 51.3 | 48.4 | 167.7 | 151.3 | 37.7 | 92.5 | 78 | 57
515.3 | 296.3 | 288.7 | 115.48 | 134.9895 | 157.2 | 147.9 | 173.1 | 166 | 251.6 | 22 | 21.5 | 39.7 | 10 | 248.5 | 5.4 | 578.4 | 636.5 | 535.1 | 628.4 | 420.8 | 168.5 | 328.8 | 377.1 | 123.1 | 332.2 | 17.7 | 33.8 | 51.6 | 48.5 | 168.5 | 151.4 | 37.8 | 92.7 | 78.2 | 57.1
516.3 | 297.3 | 288 | 115.2 | 134.6622 | 156.3 | 147.8 | 173.9 | 166.3 | 250 | 22 | 21.5 | 39.7 | 9.7 | 256.9 | 6.1 | 580.9 | 627.8 | 530.3 | 629.9 | 419.6 | 169 | 325.4 | 370 | 123.2 | 331 | 17.7 | 33.9 | 51.6 | 48.6 | 169 | 151.8 | 37.9 | 93 | 78.4 | 57.3
517.3 | 298.3 | 287.7 | 115.08 | 134.5219 | 155.5 | 147.9 | 174 | 166.8 | 245.7 | 22 | 21.5 | 39.7 | 8.1 | 266.6 | 6.3 | 583.1 | 620.2 | 542.5 | 633.3 | 420.8 | 169.4 | 322.6 | 371.2 | 123.3 | 331.2 | 17.8 | 34 | 51.8 | 48.7 | 169.3 | 152 | 38 | 93.3 | 78.6 | 57.4
518.3 | 299.3 | 289.1 | 115.64 | 135.1765 | 155.7 | 148.6 | 173.9 | 166.7 | 248.6 | 22 | 21.5 | 39.8 | 7.8 | 271.9 | 6.3 | 586 | 629.5 | 566 | 637.6 | 422.8 | 169.9 | 324.9 | 382.6 | 123.5 | 331.7 | 17.8 | 34.1 | 51.9 | 48.9 | 169.1 | 152.9 | 38.1 | 93.4 | 78.8 | 57.6
519.3 | 300.3 | 289.9 | 115.96 | 135.5506 | 155.6 | 149 | 173.4 | 166.9 | 255.4 | 22.1 | 21.5 | 39.7 | 7.8 | 247.7 | 7.1 | 590.3 | 647.5 | 577.7 | 642.7 | 426.3 | 170.3 | 331.6 | 386.6 | 124 | 333.8 | 17.8 | 34.2 | 52.1 | 49 | 169.4 | 154 | 38.3 | 93.7 | 78.9 | 57.8
520.3 | 301.3 | 289.8 | 115.92 | 135.5038 | 155.9 | 147.8 | 173.5 | 166.6 | 255 | 22.1 | 21.5 | 39.6 | 7.8 | 257.8 | 8.3 | 594.7 | 641.2 | 563.3 | 647.9 | 425.3 | 170.8 | 332.4 | 382.9 | 124.3 | 333.3 | 17.8 | 34.3 | 52.2 | 49.1 | 169.7 | 154.6 | 38.3 | 94 | 79.2 | 57.9
521.3 | 302.3 | 289.5 | 115.8 | 135.3635 | 156.8 | 148.5 | 172.5 | 165.8 | 254.4 | 22.1 | 21.5 | 39.6 | 6.8 | 253.7 | 9.4 | 598.9 | 632.6 | 547.3 | 652.2 | 423.7 | 171.3 | 330.4 | 376.1 | 124.5 | 332.5 | 17.9 | 34.4 | 52.4 | 49.2 | 171.3 | 154.3 | 38.5 | 94.3 | 79.4 | 58.1
522.3 | 303.3 | 289.2 | 115.68 | 135.2233 | 157.5 | 149.5 | 171.6 | 165.8 | 251.7 | 22.2 | 21.5 | 39.5 | 7.4 | 239.3 | 10.9 | 602.7 | 626 | 539.6 | 656.3 | 421.9 | 171.7 | 326.5 | 372.3 | 124.7 | 331 | 17.9 | 34.5 | 52.5 | 49.3 | 171.5 | 154.3 | 38.6 | 94.3 | 79.6 | 58.3
523.3 | 304.3 | 288.9 | 115.56 | 135.083 | 157.7 | 150 | 172.1 | 165.7 | 251.9 | 22.3 | 21.5 | 39.7 | 8.4 | 246.4 | 10.4 | 606 | 633.6 | 556.9 | 662.2 | 423.9 | 172.1 | 329.3 | 379.8 | 124.8 | 331.5 | 17.9 | 34.6 | 52.6 | 49.5 | 171.6 | 154.6 | 38.6 | 94.4 | 79.5 | 58.3
524.3 | 305.3 | 288.2 | 115.28 | 134.7557 | 159.1 | 148.7 | 172.2 | 165.3 | 255 | 22.3 | 21.5 | 39.8 | 9.4 | 239.3 | 10.3 | 609.8 | 645.5 | 562.8 | 667.2 | 426.3 | 172.6 | 331.4 | 378.2 | 125.2 | 333.7 | 17.9 | 34.7 | 52.7 | 49.6 | 171.7 | 154.5 | 38.8 | 94.6 | 80 | 58.6
525.3 | 306.3 | 288.3 | 115.32 | 134.8024 | 158.9 | 146.8 | 173 | 165 | 252.3 | 22.4 | 21.5 | 39.9 | 8.7 | 258.3 | 9.3 | 613.3 | 650.1 | 561.8 | 672 | 427.1 | 173.1 | 333.4 | 377.4 | 125.8 | 334.8 | 18 | 34.8 | 52.9 | 49.7 | 171.6 | 154.4 | 38.9 | 94.9 | 80.2 | 58.7
526.3 | 307.3 | 290.1 | 116.04 | 135.6441 | 158.2 | 145.8 | 173 | 165.1 | 249.9 | 22.5 | 21.5 | 40 | 7.1 | 249.2 | 8.4 | 616.8 | 649.2 | 558.6 | 676.4 | 427.4 | 173.6 | 332.4 | 371.4 | 126 | 334 | 18 | 34.9 | 53 | 49.8 | 171.4 | 154.3 | 39 | 95.1 | 80.4 | 58.9
527.3 | 308.3 | 289.8 | 115.92 | 135.5038 | 157.9 | 146.6 | 173.4 | 165.4 | 249.5 | 22.6 | 21.5 | 40.1 | 7.5 | 240.5 | 7.9 | 620.5 | 643.7 | 547.8 | 680 | 426.3 | 174 | 331.5 | 369.6 | 126.2 | 333.1 | 18 | 35 | 53.1 | 49.9 | 172 | 154.1 | 39.1 | 95.3 | 80.5 | 59
528.3 | 309.3 | 289.7 | 115.88 | 135.457 | 159.4 | 147.5 | 173.7 | 165.1 | 246.9 | 22.6 | 21.5 | 40.2 | 7.2 | 242.9 | 8.6 | 624.4 | 639.2 | 535.6 | 682.1 | 425.2 | 174.5 | 328.3 | 364 | 126.4 | 332.2 | 18 | 35.1 | 53.4 | 50 | 172 | 154.2 | 39.2 | 95.6 | 80.8 | 59.1
529.3 | 310.3 | 289.6 | 115.84 | 135.4103 | 160 | 147.1 | 173.8 | 165.3 | 243.3 | 22.7 | 21.5 | 40.3 | 7.4 | 249.8 | 9.6 | 627.9 | 635.9 | 514.9 | 682.8 | 424.3 | 175 | 326 | 363 | 126.6 | 331.4 | 18.1 | 35.2 | 53.4 | 50.1 | 171.8 | 154.1 | 39.4 | 95.7 | 81 | 59.3
530.3 | 311.3 | 289.4 | 115.76 | 135.3168 | 158.9 | 147.5 | 174.1 | 165.4 | 242 | 22.7 | 21.5 | 40.3 | 7.4 | 259.6 | 9.8 | 630.7 | 632.4 | 503.9 | 683.8 | 423 | 175.4 | 320.6 | 354.3 | 126.6 | 330.5 | 18.1 | 35.3 | 53.5 | 50.3 | 171.7 | 154.2 | 39.5 | 95.8 | 81.1 | 59.4
531.3 | 312.3 | 289.4 | 115.76 | 135.3168 | 158.9 | 149.1 | 173.3 | 165.2 | 239.7 | 22.8 | 21.5 | 40.4 | 8.5 | 224 | 10.3 | 633.1 | 630.3 | 508.9 | 686.1 | 422.9 | 175.9 | 319 | 351.4 | 126.8 | 330.6 | 18.1 | 35.4 | 53.7 | 50.4 | 172 | 154.8 | 39.6 | 96.1 | 81.3 | 59.6
532.3 | 313.3 | 289.1 | 115.64 | 135.1765 | 158.8 | 150.4 | 172.6 | 164.8 | 237.7 | 22.8 | 21.5 | 40.5 | 9.6 | 214.3 | 10 | 635.9 | 623.9 | 502.4 | 687.7 | 422 | 176.4 | 316.6 | 347.3 | 127.1 | 330 | 18.2 | 35.5 | 53.7 | 50.5 | 172 | 154.8 | 39.7 | 96.3 | 81.4 | 59.7
533.3 | 314.3 | 289 | 115.6 | 135.1297 | 159.6 | 150.5 | 171.5 | 164.5 | 236.8 | 22.8 | 21.5 | 40.5 | 10.1 | 243.3 | 11.9 | 638.4 | 621.7 | 505.4 | 690.1 | 422 | 176.8 | 313.6 | 339.7 | 127.2 | 329.2 | 18.2 | 35.6 | 53.9 | 50.6 | 171.7 | 155 | 39.8 | 96.6 | 81.6 | 59.8
534.3 | 315.3 | 289 | 115.6 | 135.1297 | 161.1 | 150.6 | 171.5 | 164.6 | 235.2 | 22.9 | 21.5 | 40.5 | 10.2 | 236.8 | 14.9 | 640.8 | 625.2 | 508 | 693.5 | 421.6 | 177.2 | 312.2 | 332.3 | 127.4 | 328.8 | 18.2 | 35.6 | 54 | 50.7 | 172 | 155.4 | 39.9 | 96.8 | 81.8 | 60
535.3 | 316.3 | 289.1 | 115.64 | 135.1765 | 162.3 | 150.4 | 171.5 | 163.9 | 233.4 | 22.9 | 21.5 | 40.6 | 10.2 | 246.2 | 13 | 643.1 | 629.1 | 501.7 | 696.6 | 420.7 | 177.7 | 310.9 | 326.4 | 127.6 | 328.2 | 18.2 | 35.8 | 54.2 | 50.8 | 172 | 155.5 | 40.1 | 97.1 | 81.9 | 60.2
536.3 | 317.3 | 288.9 | 115.56 | 135.083 | 162.9 | 150.2 | 171.8 | 163.1 | 232.8 | 22.9 | 21.5 | 40.6 | 10.6 | 220.6 | 12.9 | 645.2 | 639.7 | 504.3 | 700.3 | 421.8 | 178.1 | 309.7 | 323.3 | 127.8 | 328 | 18.3 | 35.9 | 54.3 | 50.9 | 171.9 | 155.2 | 40.1 | 97.3 | 82.1 | 60.3
537.3 | 318.3 | 289.3 | 115.72 | 135.27 | 162.9 | 149.9 | 172.4 | 163.5 | 233.6 | 22.9 | 21.5 | 40.7 | 11.1 | 229.5 | 11.5 | 647.3 | 631.5 | 489.7 | 703.5 | 420 | 178.6 | 308.6 | 322.7 | 127.9 | 327.2 | 18.3 | 36 | 54.4 | 51 | 172 | 155.2 | 40.3 | 97.4 | 82.3 | 60.4
538.3 | 319.3 | 289.2 | 115.68 | 135.2233 | 162.4 | 149.5 | 172.9 | 164.5 | 231.6 | 23 | 21.5 | 40.8 | 10.3 | 212 | 10.1 | 649.6 | 628.1 | 486 | 705.8 | 419.5 | 179 | 305.7 | 319.3 | 128.1 | 326.6 | 18.3 | 36 | 54.4 | 51.1 | 172.2 | 155.5 | 40.4 | 97.5 | 82.5 | 60.6
539.3 | 320.3 | 289.1 | 115.64 | 135.1765 | 162.9 | 149 | 173.4 | 164.9 | 229.6 | 23 | 21.5 | 40.9 | 9 | 225.4 | 11.2 | 651.8 | 617.7 | 480.5 | 707.9 | 419.1 | 179.4 | 303.5 | 315.6 | 128.2 | 325.4 | 18.4 | 36.1 | 54.5 | 51.2 | 172.4 | 155.4 | 40.5 | 97.7 | 82.7 | 60.7
540.3 | 321.3 | 289.2 | 115.68 | 135.2233 | 162.2 | 149 | 174.3 | 165.2 | 228.7 | 23 | 21.5 | 40.9 | 7.8 | 249.3 | 14.4 | 654.1 | 604.8 | 465.7 | 709.7 | 417.6 | 179.8 | 301.1 | 314.7 | 128.2 | 324.9 | 18.4 | 36.2 | 54.7 | 51.3 | 172.4 | 155.4 | 40.6 | 97.9 | 82.8 | 60.9
541.3 | 322.3 | 289.2 | 115.68 | 135.2233 | 162 | 149.2 | 174.7 | 165.2 | 227.9 | 23.1 | 21.5 | 41 | 7 | 254.5 | 15.7 | 656.5 | 599.1 | 460.9 | 711.6 | 417.2 | 180.1 | 296.9 | 312.3 | 128.2 | 323.4 | 18.4 | 36.2 | 54.8 | 51.4 | 172.1 | 155.1 | 40.7 | 98.1 | 82.9 | 61
542.3 | 323.3 | 289 | 115.6 | 135.1297 | 161.5 | 149.7 | 174.5 | 165 | 227.9 | 23.1 | 21.5 | 41 | 7.4 | 252.7 | 14.9 | 658.6 | 594.5 | 466.4 | 714.7 | 417.6 | 180.6 | 295.8 | 313.4 | 128.3 | 322.9 | 18.4 | 36.4 | 55.1 | 51.5 | 171.6 | 155 | 40.8 | 98.3 | 83.2 | 61.2
543.3 | 324.3 | 289.1 | 115.64 | 135.1765 | 162.4 | 149.8 | 173.8 | 164.1 | 229.4 | 23.2 | 21.5 | 41 | 7.9 | 257.2 | 14.2 | 661.1 | 588.9 | 473.9 | 717.9 | 417.6 | 181 | 294.3 | 311.7 | 128.4 | 322.4 | 18.5 | 36.5 | 55.2 | 51.6 | 171.1 | 154.9 | 40.9 | 98.5 | 83.3 | 61.3
544.3 | 325.3 | 289.2 | 115.68 | 135.2233 | 162.4 | 149.7 | 172.8 | 163.3 | 229 | 23.2 | 21.5 | 41.1 | 8.1 | 250.2 | 12.2 | 663.6 | 603 | 489.9 | 722.6 | 420 | 181.4 | 295.7 | 314.4 | 128.7 | 323.9 | 18.5 | 36.6 | 55.3 | 51.7 | 170.9 | 154.7 | 41 | 98.7 | 83.5 | 61.4
545.3 | 326.3 | 289.3 | 115.72 | 135.27 | 162.1 | 150.8 | 171.8 | 164.1 | 231.1 | 23.2 | 21.5 | 41.1 | 8 | 222.2 | 10.6 | 666.7 | 619.8 | 510.9 | 727.2 | 422.3 | 181.7 | 297.6 | 317.8 | 129.3 | 324.5 | 18.5 | 36.6 | 55.4 | 51.8 | 170.9 | 154.6 | 41.2 | 98.9 | 83.6 | 61.6
546.3 | 327.3 | 289.3 | 115.72 | 135.27 | 162.4 | 150.9 | 172.4 | 164.6 | 232.8 | 23.2 | 21.5 | 41.2 | 8.1 | 226.3 | 11.3 | 670.1 | 633.2 | 526.5 | 730.9 | 424.1 | 182.1 | 298.9 | 323.1 | 129.7 | 325.1 | 18.6 | 36.7 | 55.6 | 51.9 | 170.9 | 154.3 | 41.3 | 99.2 | 83.9 | 61.7
547.3 | 328.3 | 289.3 | 115.72 | 135.27 | 162.6 | 151.6 | 173.4 | 165 | 234.4 | 23.2 | 21.5 | 41.3 | 7.7 | 240 | 10.9 | 673.4 | 645.9 | 547.9 | 735.6 | 426.6 | 182.5 | 303.5 | 331 | 130.1 | 326.4 | 18.6 | 36.8 | 55.8 | 52 | 170.8 | 154.3 | 41.4 | 99.3 | 84 | 61.8
548.3 | 329.3 | 289.3 | 115.72 | 135.27 | 163.7 | 152.4 | 174 | 165 | 236.8 | 23.2 | 21.5 | 41.4 | 7.6 | 237.1 | 11.3 | 677 | 660.5 | 561.4 | 739.1 | 430 | 182.9 | 308.3 | 336.9 | 130.7 | 327.6 | 18.6 | 36.9 | 55.7 | 52.1 | 170.8 | 154.5 | 41.5 | 99.4 | 84.3 | 62
549.3 | 330.3 | 289.3 | 115.72 | 135.27 | 163.4 | 153.1 | 174 | 165.4 | 239.6 | 23.2 | 21.5 | 41.4 | 9.3 | 238.7 | 12.5 | 680.4 | 666.3 | 556.9 | 742.8 | 429.1 | 183.3 | 312.4 | 341.5 | 131.2 | 328.8 | 18.7 | 37 | 55.8 | 52.2 | 170.8 | 154.8 | 41.6 | 99.6 | 84.5 | 62.1
550.3 | 331.3 | 289.2 | 115.68 | 135.2233 | 162.1 | 153.4 | 173.9 | 166.4 | 239.3 | 23.2 | 21.5 | 41.4 | 8.8 | 239.4 | 12.2 | 683.8 | 672.9 | 555.7 | 746.6 | 429.7 | 183.7 | 316.2 | 346.3 | 131.6 | 329.2 | 18.7 | 37.1 | 56.1 | 52.3 | 171 | 155.1 | 41.7 | 99.8 | 84.7 | 62.2
551.3 | 332.3 | 289.2 | 115.68 | 135.2233 | 160.6 | 153.8 | 174.6 | 166.6 | 240.7 | 23.1 | 21.5 | 41.4 | 10.7 | 246.4 | 11.9 | 687.2 | 687.8 | 568.6 | 750.5 | 433.6 | 184 | 318.7 | 346 | 132.1 | 330.2 | 18.7 | 37.2 | 56.2 | 52.4 | 170.8 | 155.3 | 41.8 | 100.1 | 85 | 62.3
552.3 | 333.3 | 289.1 | 115.64 | 135.1765 | 160.1 | 153.7 | 175.2 | 166.4 | 240.4 | 23.1 | 21.5 | 41.3 | 11.3 | 249.4 | 12.8 | 690.3 | 696.4 | 569.8 | 754.7 | 433.7 | 184.4 | 321 | 351.9 | 132.8 | 331.1 | 18.7 | 37.3 | 56.4 | 52.5 | 171 | 155.2 | 41.9 | 100.4 | 85.2 | 62.5
553.3 | 334.3 | 289.3 | 115.72 | 135.27 | 160.1 | 153.8 | 175.6 | 166.6 | 239.9 | 23.1 | 21.5 | 41.3 | 10.2 | 249.2 | 15.4 | 693.5 | 699.1 | 564.7 | 757.2 | 433 | 184.8 | 322.8 | 353 | 133.5 | 331.3 | 18.8 | 37.4 | 56.5 | 52.5 | 171.1 | 155.4 | 42.1 | 100.5 | 85.4 | 62.6
554.3 | 335.3 | 289.3 | 115.72 | 135.27 | 160.1 | 153 | 176.4 | 166.8 | 240.4 | 23.1 | 21.5 | 41.3 | 9.8 | 242.7 | 17.3 | 696.7 | 694.8 | 550.6 | 758.9 | 432.6 | 185.3 | 325.1 | 352.7 | 133.9 | 331.1 | 18.8 | 37.5 | 56.6 | 52.6 | 171.2 | 155.2 | 42.1 | 100.7 | 85.7 | 62.8
555.3 | 336.3 | 289.3 | 115.72 | 135.27 | 159.4 | 153.1 | 176.4 | 167 | 239.9 | 23.1 | 21.5 | 41.3 | 9.2 | 241.6 | 15.6 | 699.9 | 691 | 543.5 | 759 | 431.4 | 185.7 | 323.8 | 351.3 | 133.9 | 330.3 | 18.8 | 37.6 | 56.7 | 52.7 | 171.6 | 155.1 | 42.3 | 101 | 85.9 | 62.9
556.3 | 337.3 | 289.2 | 115.68 | 135.2233 | 159.6 | 153.3 | 176.9 | 167.5 | 240.9 | 23.2 | 21.5 | 41.3 | 8.9 | 243.9 | 14.7 | 702.7 | 703.5 | 545.9 | 759.2 | 431.7 | 186.1 | 327.4 | 355.5 | 134.3 | 332.3 | 18.9 | 37.7 | 56.7 | 52.8 | 171.7 | 155 | 42.4 | 101.1 | 86.1 | 63.1
557.3 | 338.3 | 289.2 | 115.68 | 135.2233 | 159.6 | 153.2 | 177.7 | 167.9 | 241.1 | 23.2 | 21.5 | 41.3 | 9.1 | 254.3 | 14.4 | 705.7 | 708.6 | 542.4 | 758.5 | 432.3 | 186.5 | 326.7 | 353.4 | 134.6 | 331.9 | 18.9 | 37.8 | 56.8 | 52.9 | 171.5 | 155.1 | 42.5 | 101.3 | 86.3 | 63.3
558.3 | 339.3 | 289 | 115.6 | 135.1297 | 161 | 152.2 | 178 | 168 | 241.2 | 23.2 | 21.5 | 41.3 | 9.3 | 252 | 13.1 | 708.2 | 712.7 | 558.5 | 761.3 | 433.1 | 186.9 | 327.9 | 353 | 135 | 332.6 | 18.9 | 37.9 | 57.1 | 53 | 171.4 | 155.3 | 42.6 | 101.5 | 86.6 | 63.4
559.3 | 340.3 | 289 | 115.6 | 135.1297 | 160.8 | 152.5 | 177.9 | 169 | 243.8 | 23.3 | 21.5 | 41.3 | 9.1 | 247 | 12.2 | 710.5 | 727.7 | 574 | 762 | 436 | 187.3 | 329 | 353 | 135.4 | 334.3 | 19 | 38 | 57.3 | 53.1 | 171.3 | 155.6 | 42.7 | 101.8 | 86.8 | 63.6
560.3 | 341.3 | 289 | 115.6 | 135.1297 | 159.8 | 152.9 | 178.6 | 169.7 | 245.9 | 23.3 | 21.5 | 41.3 | 8.8 | 248 | 12.3 | 712.8 | 737 | 582 | 765.8 | 438.1 | 187.7 | 332.4 | 356.1 | 136.1 | 335.8 | 19 | 38.1 | 57.5 | 53.2 | 171.4 | 155.6 | 42.8 | 101.9 | 87 | 63.7
561.3 | 342.3 | 290.6 | 116.24 | 135.8779 | 159.5 | 152.4 | 179.1 | 169 | 245.6 | 23.4 | 21.5 | 41.3 | 8.6 | 242.1 | 12.1 | 715.4 | 741.7 | 586.6 | 769 | 440.5 | 188.1 | 336.5 | 358.6 | 136.8 | 337.1 | 19 | 38.2 | 57.5 | 53.3 | 171 | 155.6 | 42.9 | 102.1 | 87.3 | 63.9
562.3 | 343.3 | 288.6 | 115.44 | 134.9427 | 160.2 | 152.3 | 179.5 | 168.6 | 247.1 | 23.4 | 21.5 | 41.4 | 7.6 | 249.8 | 12 | 718 | 747.6 | 600.1 | 773.1 | 442.6 | 188.5 | 339.6 | 364.7 | 137.4 | 339.3 | 19.1 | 38.3 | 57.6 | 53.4 | 171.3 | 156 | 43.1 | 102.3 | 87.5 | 64
563.3 | 344.3 | 288.3 | 115.32 | 134.8024 | 159.9 | 153 | 180.3 | 169.2 | 248.7 | 23.4 | 21.5 | 41.4 | 7.9 | 241.8 | 12.5 | 721 | 758.3 | 603.1 | 774.6 | 444 | 189 | 343.8 | 370.8 | 138.1 | 341 | 19.1 | 38.4 | 57.8 | 53.5 | 171 | 156.1 | 43.2 | 102.4 | 87.8 | 64.2
564.3 | 345.3 | 288.6 | 115.44 | 134.9427 | 160 | 153.8 | 181 | 170 | 252.2 | 23.4 | 21.5 | 41.5 | 8.5 | 250.6 | 12.7 | 724.1 | 763.6 | 593.9 | 775.5 | 443.6 | 189.4 | 344.2 | 377.4 | 138.7 | 340.5 | 19.1 | 38.5 | 57.9 | 53.7 | 171 | 155.7 | 43.3 | 102.6 | 88 | 64.3
565.3 | 346.3 | 288.8 | 115.52 | 135.0362 | 160.3 | 154.5 | 180.6 | 171.1 | 252.6 | 23.4 | 21.5 | 41.6 | 8.5 | 247.5 | 12.4 | 727.1 | 758.8 | 578.8 | 775.8 | 442.1 | 189.8 | 343.6 | 381.2 | 138.9 | 340.2 | 19.2 | 38.6 | 58 | 53.8 | 171.1 | 155.6 | 43.4 | 102.7 | 88.2 | 64.5
566.3 | 347.3 | 289.2 | 115.68 | 135.2233 | 160.5 | 154.6 | 180.1 | 170.9 | 252.3 | 23.5 | 21.5 | 41.6 | 9.1 | 241.9 | 12.3 | 730.2 | 746.2 | 561.4 | 774.8 | 441.1 | 190.2 | 340.7 | 376.4 | 139 | 339.2 | 19.2 | 38.7 | 58 | 53.9 | 171.1 | 155.6 | 43.5 | 102.9 | 88.5 | 64.6
567.3 | 348.3 | 287.7 | 115.08 | 134.5219 | 159.5 | 154.6 | 179.7 | 170 | 250.3 | 23.5 | 21.5 | 41.6 | 8.9 | 236.1 | 12.7 | 733 | 740.5 | 546.5 | 773 | 440.4 | 190.6 | 338.3 | 375.4 | 139 | 338.2 | 19.3 | 38.8 | 58.1 | 54 | 171 | 155.4 | 43.6 | 103.2 | 88.7 | 64.8
568.3 | 349.3 | 286.8 | 114.72 | 134.1011 | 159.1 | 154.6 | 179.2 | 169.7 | 247.8 | 23.5 | 21.5 | 41.6 | 8.1 | 245.7 | 12.4 | 735.5 | 738.1 | 545.4 | 771.2 | 441.4 | 191 | 336 | 374.5 | 139.1 | 337.8 | 19.3 | 38.9 | 58.2 | 54.1 | 170.8 | 155.5 | 43.7 | 103.4 | 88.9 | 64.9
569.3 | 350.3 | 287.5 | 115 | 134.4284 | 160.7 | 156 | 179.1 | 170.8 | 249.5 | 23.5 | 21.5 | 41.7 | 10 | 246.6 | 11.2 | 737.8 | 741.9 | 536.2 | 769.4 | 441.2 | 191.3 | 336.8 | 377.6 | 139.3 | 338.4 | 19.3 | 39 | 58.4 | 54.2 | 170.7 | 155.6 | 43.8 | 103.6 | 89.1 | 65.1
570.3 | 351.3 | 287.9 | 115.16 | 134.6154 | 161.4 | 156.5 | 178.3 | 171.6 | 249.1 | 23.5 | 21.5 | 41.8 | 10 | 237.4 | 9.3 | 739.8 | 735.7 | 523.1 | 768.3 | 439.8 | 191.7 | 335.1 | 369.4 | 139.5 | 337.7 | 19.3 | 39.1 | 58.5 | 54.3 | 170.9 | 155.8 | 43.9 | 103.8 | 89.3 | 65.2
571.3 | 352.3 | 288 | 115.2 | 134.6622 | 161.9 | 157 | 178.1 | 171.8 | 247.6 | 23.5 | 21.5 | 41.9 | 7.6 | 252.6 | 8.7 | 741.4 | 737.1 | 506.2 | 766.5 | 438 | 192.1 | 332.8 | 363.6 | 139.7 | 336.9 | 19.4 | 39.2 | 58.7 | 54.4 | 171.2 | 156.2 | 44 | 104.1 | 89.6 | 65.4
572.3 | 353.3 | 288.3 | 115.32 | 134.8024 | 162 | 157.9 | 178.7 | 172.1 | 245.9 | 23.5 | 21.5 | 42 | 8.6 | 245.3 | 11.8 | 742.7 | 732.7 | 494.4 | 765.5 | 437.1 | 192.5 | 331.9 | 361.5 | 140 | 336.4 | 19.4 | 39.3 | 58.7 | 54.5 | 171.7 | 156.5 | 44.2 | 104.4 | 89.8 | 65.5
573.3 | 354.3 | 288.3 | 115.32 | 134.8024 | 162.2 | 158.6 | 178.9 | 172 | 244.2 | 23.5 | 21.5 | 42 | 10.2 | 252.2 | 13.3 | 744.3 | 724.5 | 486.2 | 763.1 | 436.6 | 192.9 | 329.2 | 357.1 | 140.1 | 335.5 | 19.5 | 39.4 | 59 | 54.6 | 172.2 | 156.8 | 44.3 | 104.6 | 90 | 65.7
574.3 | 355.3 | 287.9 | 115.16 | 134.6154 | 162.5 | 158.9 | 179.4 | 171.3 | 242.1 | 23.5 | 21.5 | 42.1 | 9.9 | 250.9 | 15.8 | 746.2 | 708.6 | 470 | 762 | 434.8 | 193.2 | 324.8 | 349.8 | 140.3 | 334.5 | 19.5 | 39.5 | 59.1 | 54.7 | 172.1 | 157.2 | 44.4 | 104.8 | 90.2 | 65.8
575.3 | 356.3 | 286.9 | 114.76 | 134.1478 | 162.5 | 158.6 | 180 | 171.4 | 238.2 | 23.5 | 21.5 | 42.2 | 9.8 | 257.2 | 17.4 | 747.5 | 697.2 | 459.3 | 760 | 432.8 | 193.6 | 320 | 343.8 | 140.3 | 333.4 | 19.5 | 39.6 | 59.1 | 54.8 | 172.2 | 157.9 | 44.5 | 105.1 | 90.3 | 66
576.3 | 357.3 | 288.8 | 115.52 | 135.0362 | 162.9 | 158.9 | 180.5 | 171 | 235.7 | 23.5 | 21.5 | 42.2 | 10.3 | 248.6 | 18.6 | 748.4 | 695.4 | 453.7 | 758.1 | 432 | 193.9 | 316.2 | 340.1 | 140.5 | 332.5 | 19.6 | 39.7 | 59.3 | 54.9 | 172 | 158.4 | 44.6 | 105.4 | 90.4 | 66.1
577.3 | 358.3 | 288.7 | 115.48 | 134.9895 | 162.7 | 159.4 | 181 | 170.1 | 234.5 | 23.5 | 21.5 | 42.3 | 13.8 | 252.4 | 20.3 | 749.3 | 692.4 | 450.3 | 756.3 | 431.3 | 194.3 | 313 | 338.8 | 140.5 | 331.2 | 19.6 | 39.8 | 59.4 | 55 | 172 | 158.2 | 44.7 | 105.6 | 90.5 | 66.2
578.3 | 359.3 | 287.8 | 115.12 | 134.5686 | 163.3 | 158.7 | 181.1 | 168.8 | 233.4 | 23.5 | 21.5 | 42.4 | 15 | 251 | 19.6 | 750.1 | 691.1 | 454 | 753.7 | 431.1 | 194.7 | 311 | 337.9 | 140.6 | 330.5 | 19.6 | 39.9 | 59.5 | 55.1 | 171.9 | 158.4 | 44.8 | 105.8 | 90.6 | 66.4
579.3 | 360.3 | 287.3 | 114.92 | 134.3349 | 163.1 | 157.7 | 180.1 | 168.7 | 235 | 23.6 | 21.5 | 42.5 | 12.6 | 241.1 | 23.6 | 751.2 | 684.5 | 449.8 | 752.7 | 430.3 | 195 | 308.7 | 333.8 | 140.7 | 329.7 | 19.7 | 40 | 59.7 | 55.2 | 171.7 | 158.5 | 44.9 | 106.1 | 90.8 | 66.5
580.3 | 361.3 | 288.6 | 115.44 | 134.9427 | 162.8 | 156.6 | 180.1 | 168.1 | 232.5 | 23.6 | 21.5 | 42.6 | 12.3 | 242.3 | 22.6 | 752.3 | 675.9 | 443.2 | 750.9 | 429.3 | 195.4 | 306.7 | 331.1 | 140.8 | 328.8 | 19.7 | 40.1 | 59.7 | 55.3 | 171.8 | 158.3 | 45 | 106.2 | 91 | 66.7
581.3 | 362.3 | 288.8 | 115.52 | 135.0362 | 163 | 155.4 | 180.4 | 167 | 232.5 | 23.6 | 21.5 | 42.7 | 11.9 | 236.3 | 21.3 | 753.2 | 671 | 438.7 | 751.3 | 428.8 | 195.7 | 305.4 | 331.9 | 140.9 | 328.3 | 19.7 | 40.2 | 59.9 | 55.4 | 171.9 | 158.2 | 45.2 | 106.4 | 91.1 | 66.8
582.3 | 363.3 | 288.3 | 115.32 | 134.8024 | 163 | 154.7 | 181.5 | 166.9 | 232 | 23.5 | 21.5 | 42.8 | 9.7 | 241.5 | 19.7 | 754.7 | 659.3 | 429.2 | 749.7 | 427.5 | 196.1 | 302.4 | 325.2 | 141 | 327.1 | 19.8 | 40.3 | 59.9 | 55.5 | 173 | 158.6 | 45.3 | 106.7 | 91.2 | 67
583.3 | 364.3 | 289.2 | 115.68 | 135.2233 | 162.5 | 153.4 | 182.1 | 168.2 | 230.6 | 23.5 | 21.5 | 42.8 | 9.1 | 239.1 | 19.8 | 755.6 | 646.8 | 419.7 | 748.9 | 426.4 | 196.4 | 299.2 | 322.8 | 141.1 | 326.2 | 19.8 | 40.4 | 60.1 | 55.6 | 172.8 | 159.2 | 45.4 | 106.9 | 91.4 | 67.2
584.3 | 365.3 | 288.9 | 115.56 | 135.083 | 162.3 | 153.5 | 181.1 | 169.1 | 228 | 23.4 | 21.5 | 42.9 | 9 | 239.6 | 18.1 | 756.2 | 637.8 | 413.2 | 747.1 | 426.2 | 196.7 | 296.2 | 316.5 | 141.2 | 325.4 | 19.8 | 40.5 | 60.2 | 55.7 | 172.6 | 159.1 | 45.4 | 107.1 | 91.6 | 67.4
585.3 | 366.3 | 288.8 | 115.52 | 135.0362 | 163.3 | 154.1 | 179.8 | 168.5 | 227.4 | 23.3 | 21.5 | 42.9 | 8.2 | 233.7 | 16.7 | 756.9 | 630.1 | 415.9 | 745.3 | 426.4 | 197.1 | 294.4 | 315.8 | 141.3 | 324.6 | 19.9 | 40.5 | 60.4 | 55.8 | 172.8 | 159.2 | 45.6 | 107.2 | 91.7 | 67.5
586.3 | 367.3 | 289 | 115.6 | 135.1297 | 164 | 154 | 178.9 | 168.6 | 227.4 | 23.3 | 21.5 | 43 | 7.6 | 229.8 | 14.7 | 758.1 | 622.1 | 409.2 | 742.2 | 426.6 | 197.4 | 292.7 | 313.7 | 141.5 | 323.9 | 19.9 | 40.6 | 60.6 | 56 | 173.8 | 159.3 | 45.7 | 107.3 | 91.9 | 67.7
587.3 | 368.3 | 289.9 | 115.96 | 135.5506 | 166.4 | 154.1 | 177.9 | 169.2 | 227.2 | 23.3 | 21.5 | 43.1 | 7.6 | 238.7 | 11.9 | 759 | 617.4 | 406 | 739.9 | 425.9 | 197.7 | 290 | 310.2 | 141.6 | 322.6 | 19.9 | 40.7 | 60.7 | 56.1 | 173.6 | 159.2 | 45.8 | 107.6 | 92 | 67.9
588.3 | 369.3 | 289.8 | 115.92 | 135.5038 | 166.7 | 154.9 | 177.8 | 169.1 | 224 | 23.2 | 21.5 | 43.1 | 8 | 244.9 | 12.3 | 759.6 | 614.6 | 403.8 | 738.7 | 425.4 | 198.1 | 287.2 | 309.6 | 141.7 | 321.7 | 20 | 40.8 | 60.7 | 56.2 | 173.4 | 159.2 | 45.9 | 107.8 | 92.2 | 68
589.3 | 370.3 | 289.1 | 115.64 | 135.1765 | 166 | 155.5 | 178.1 | 169.6 | 223.8 | 23.2 | 21.5 | 43.2 | 8.8 | 244.6 | 12.9 | 760.2 | 617.5 | 404.5 | 735.5 | 424.7 | 198.4 | 286.6 | 309.5 | 141.8 | 320.9 | 20 | 40.9 | 60.7 | 56.3 | 173.4 | 159.2 | 46.1 | 108 | 92.3 | 68.1
590.3 | 371.3 | 288.8 | 115.52 | 135.0362 | 165.3 | 155.7 | 178 | 170.3 | 224.9 | 23.2 | 21.5 | 43.2 | 9.3 | 236.8 | 13.3 | 760.8 | 615.8 | 400.6 | 735.1 | 424 | 198.7 | 286.1 | 308.4 | 142 | 320.8 | 20.1 | 41 | 60.8 | 56.4 | 173.9 | 159.3 | 46.1 | 108.1 | 92.4 | 68.3
591.3 | 372.3 | 289.7 | 115.88 | 135.457 | 164.5 | 155.5 | 177.6 | 170.4 | 223.7 | 23.3 | 21.5 | 43.2 | 8.8 | 238.1 | 12.4 | 761.4 | 620.4 | 406.8 | 732.7 | 423.1 | 199 | 285.3 | 306.2 | 142.1 | 319.9 | 20.1 | 41.1 | 60.9 | 56.6 | 174.3 | 159.3 | 46.3 | 108.3 | 92.5 | 68.4
592.3 | 373.3 | 288.1 | 115.24 | 134.7089 | 164.5 | 154.1 | 177.6 | 171 | 222.6 | 23.4 | 21.5 | 43.3 | 7.5 | 251.7 | 11.4 | 761.9 | 625.3 | 410.4 | 730.2 | 422.6 | 199.3 | 285.3 | 302.9 | 142.3 | 319.6 | 20.1 | 41.2 | 61 | 56.7 | 174.6 | 159.1 | 46.4 | 108.5 | 92.7 | 68.6
593.3 | 374.3 | 287.2 | 114.88 | 134.2881 | 164.6 | 152.2 | 178.2 | 171.7 | 222.3 | 23.4 | 21.5 | 43.2 | 7.6 | 261.6 | 10.1 | 762.6 | 622.8 | 416.1 | 727.9 | 422.4 | 199.7 | 284.3 | 301.6 | 142.4 | 319 | 20.2 | 41.3 | 61.1 | 56.8 | 174.8 | 159.4 | 46.5 | 108.7 | 92.8 | 68.7
594.3 | 375.3 | 287.5 | 115 | 134.4284 | 164.9 | 152.4 | 178.4 | 171.9 | 221.5 | 23.4 | 21.5 | 43 | 8.3 | 265.3 | 10.3 | 763.5 | 618 | 413.3 | 727.2 | 422 | 200 | 284.1 | 302.2 | 142.6 | 318.7 | 20.2 | 41.4 | 61.2 | 56.9 | 174.8 | 159.6 | 46.6 | 108.9 | 93 | 68.9
595.3 | 376.3 | 287.6 | 115.04 | 134.4751 | 164.8 | 153.3 | 178.6 | 172 | 223 | 23.4 | 21.5 | 43 | 7.8 | 265.5 | 8.8 | 764.5 | 615.2 | 414.8 | 727.7 | 421.4 | 200.3 | 283.5 | 305.1 | 142.8 | 317.8 | 20.2 | 41.5 | 61.3 | 57 | 174.8 | 159.5 | 46.6 | 109.1 | 93.1 | 69
596.3 | 377.3 | 288.2 | 115.28 | 134.7557 | 164.6 | 153.4 | 178.6 | 171.7 | 224 | 23.5 | 21.5 | 43 | 6.8 | 268.7 | 8.7 | 765.7 | 609.5 | 412.7 | 723.7 | 420.8 | 200.6 | 281.4 | 303 | 142.9 | 317.2 | 20.3 | 41.6 | 61.4 | 57.1 | 174.9 | 159.4 | 46.8 | 109.3 | 93.3 | 69.2
597.3 | 378.3 | 287.7 | 115.08 | 134.5219 | 164.2 | 153.5 | 179.1 | 170.9 | 224 | 23.5 | 21.5 | 43 | 7.5 | 278.9 | 9.5 | 766.4 | 601.4 | 411.6 | 722.9 | 420.5 | 200.9 | 281.8 | 307.2 | 143 | 316.7 | 20.3 | 41.7 | 61.7 | 57.2 | 174.6 | 159.6 | 46.9 | 109.5 | 93.4 | 69.3
598.3 | 379.3 | 289.5 | 115.8 | 135.3635 | 163.3 | 153.9 | 179.1 | 171.3 | 226 | 23.6 | 21.5 | 43 | 7.9 | 266 | 9.4 | 767.3 | 596.9 | 413.6 | 722.5 | 420.5 | 201.2 | 282.6 | 309.2 | 143.1 | 316.1 | 20.4 | 41.8 | 61.8 | 57.3 | 174.1 | 159.6 | 47.1 | 109.6 | 93.5 | 69.4
599.3 | 380.3 | 290.7 | 116.28 | 135.9246 | 162.3 | 154 | 178.9 | 171.3 | 226.9 | 23.6 | 21.5 | 43 | 7.7 | 269.4 | 9.4 | 768.3 | 593.9 | 411.7 | 720.9 | 419.3 | 201.5 | 282.3 | 307.2 | 143.3 | 315.7 | 20.4 | 41.9 | 61.9 | 57.4 | 174.1 | 159.2 | 47.1 | 109.8 | 93.6 | 69.5
600.3 | 381.3 | 289.7 | 115.88 | 135.457 | 162.1 | 154.6 | 178.3 | 170.8 | 228.3 | 23.7 | 21.5 | 43.1 | 7.7 | 257.6 | 8.7 | 768.7 | 597.5 | 419.7 | 718.8 | 419.2 | 201.9 | 281.9 | 309.1 | 143.5 | 315.1 | 20.4 | 42 | 62.1 | 57.5 | 173.9 | 158.9 | 47.3 | 109.9 | 93.8 | 69.7
601.3 | 382.3 | 289.3 | 115.72 | 135.27 | 161.5 | 155.2 | 177.8 | 171 | 230.2 | 23.7 | 21.5 | 43.2 | 7.7 | 254.6 | 8.5 | 769.3 | 607.2 | 429.9 | 717.8 | 420.2 | 202.2 | 283.6 | 317.4 | 143.7 | 315.3 | 20.5 | 42.1 | 62.2 | 57.6 | 173.7 | 158.5 | 47.3 | 110.1 | 94 | 69.8
602.3 | 383.3 | 289.3 | 115.72 | 135.27 | 161.6 | 155.4 | 177.3 | 171.2 | 234.3 | 23.8 | 21.5 | 43.4 | 8.9 | 248.3 | 8.9 | 770.4 | 615.2 | 440.9 | 715.6 | 420.8 | 202.5 | 287.9 | 329.8 | 144.1 | 316.4 | 20.5 | 42.2 | 62.6 | 57.8 | 173.6 | 158.4 | 47.4 | 110.1 | 94.1 | 69.9
603.3 | 384.3 | 288.6 | 115.44 | 134.9427 | 161.5 | 154.3 | 176.8 | 171.8 | 237.6 | 23.9 | 21.5 | 43.5 | 9.7 | 253.3 | 9.9 | 771.3 | 621.9 | 461.9 | 719.7 | 422.5 | 202.8 | 290.5 | 333 | 144.4 | 316.8 | 20.6 | 42.2 | 62.7 | 57.9 | 173.9 | 158.6 | 47.6 | 110.4 | 94.3 | 70.1
604.3 | 385.3 | 289.4 | 115.76 | 135.3168 | 161.3 | 152.4 | 176.5 | 172.6 | 238.6 | 24 | 21.5 | 43.5 | 11.4 | 246.1 | 10 | 772.7 | 625.3 | 472.7 | 723.3 | 423.1 | 203.1 | 293.8 | 339.9 | 144.8 | 317.3 | 20.6 | 42.3 | 62.8 | 57.9 | 174.4 | 159 | 47.7 | 110.6 | 94.5 | 70.2
605.3 | 386.3 | 289.5 | 115.8 | 135.3635 | 161.2 | 152.6 | 176.2 | 173.5 | 241 | 24.1 | 21.5 | 43.6 | 12.7 | 256.7 | 8.8 | 773.8 | 626.8 | 484.4 | 722 | 423.8 | 203.4 | 295.4 | 346.2 | 145.1 | 317.3 | 20.6 | 42.4 | 63 | 58 | 174.7 | 159 | 47.8 | 110.8 | 94.7 | 70.3
606.3 | 387.3 | 289.7 | 115.88 | 135.457 | 162.3 | 152.6 | 175.9 | 174.1 | 241.8 | 24.2 | 21.5 | 43.7 | 11.5 | 257.1 | 10.5 | 774.8 | 646.2 | 507.2 | 723.9 | 427.5 | 203.8 | 299.6 | 362.2 | 145.7 | 318.4 | 20.7 | 42.5 | 63 | 58.1 | 175.1 | 159.4 | 47.9 | 111 | 94.9 | 70.5
607.3 | 388.3 | 289.4 | 115.76 | 135.3168 | 162.8 | 152.2 | 176.1 | 174.7 | 244.8 | 24.3 | 21.5 | 43.7 | 10.4 | 245.1 | 10.1 | 776.2 | 656.5 | 522.9 | 731.8 | 428.8 | 204.1 | 305.3 | 366 | 146.2 | 320 | 20.7 | 42.6 | 63.3 | 58.2 | 175.6 | 160.1 | 48 | 111.2 | 95 | 70.7
608.3 | 389.3 | 288.8 | 115.52 | 135.0362 | 163 | 152.6 | 176.3 | 175 | 245.2 | 24.3 | 21.4 | 43.8 | 10.1 | 249 | 8.7 | 778.5 | 663 | 526 | 731.1 | 429.5 | 204.4 | 310.4 | 371 | 146.6 | 321.2 | 20.7 | 42.7 | 63.4 | 58.3 | 175.9 | 160.2 | 48.1 | 111.4 | 95.2 | 70.8
609.3 | 390.3 | 289.2 | 115.68 | 135.2233 | 163 | 153 | 176.3 | 175.3 | 247.5 | 24.4 | 21.4 | 43.8 | 10.5 | 249.5 | 9.7 | 780.5 | 664.1 | 528 | 728.3 | 429.6 | 204.8 | 312.1 | 369.6 | 147.1 | 320.7 | 20.8 | 42.8 | 63.4 | 58.4 | 176.3 | 160.7 | 48.3 | 111.6 | 95.4 | 71
610.3 | 391.3 | 290.1 | 116.04 | 135.6441 | 162.9 | 152.8 | 176.5 | 175.6 | 248.1 | 24.4 | 21.5 | 43.8 | 9.7 | 243.4 | 14.9 | 781.8 | 670.6 | 539.8 | 729 | 430.5 | 205.1 | 312.9 | 370.1 | 147.4 | 320.6 | 20.8 | 42.9 | 63.5 | 58.5 | 176.6 | 161.5 | 48.3 | 111.8 | 95.6 | 71.1
611.3 | 392.3 | 288.6 | 115.44 | 134.9427 | 163.9 | 152.2 | 176.7 | 174.9 | 248.1 | 24.4 | 21.5 | 43.8 | 10.2 | 240.7 | 15.7 | 783 | 674.6 | 541.3 | 725.3 | 430.4 | 205.4 | 314.3 | 372.4 | 147.7 | 320.9 | 20.9 | 43 | 63.6 | 58.6 | 177.1 | 162 | 48.5 | 112 | 95.8 | 71.3
612.3 | 393.3 | 288.5 | 115.4 | 134.896 | 163.7 | 152.8 | 177.2 | 173.7 | 249.4 | 24.5 | 21.5 | 43.8 | 10.8 | 244.4 | 16 | 783.3 | 681.6 | 554.2 | 727.7 | 430.5 | 205.8 | 318.3 | 375.6 | 148.1 | 321.8 | 20.9 | 43.1 | 63.7 | 58.7 | 177.2 | 162 | 48.6 | 112.2 | 95.9 | 71.4
613.3 | 394.3 | 288.5 | 115.4 | 134.896 | 162.1 | 153.8 | 177.4 | 173.5 | 251.2 | 24.4 | 21.5 | 43.8 | 11.1 | 251.3 | 15.4 | 784.4 | 681.8 | 547.1 | 728.6 | 430.8 | 206.1 | 320.4 | 373.6 | 148.5 | 322.4 | 20.9 | 43.3 | 63.7 | 58.8 | 177.6 | 162 | 48.7 | 112.5 | 96.2 | 71.6
614.3 | 395.3 | 288.8 | 115.52 | 135.0362 | 161.3 | 153.9 | 178.4 | 173.4 | 251.8 | 24.4 | 21.5 | 43.9 | 10.4 | 247.4 | 17.3 | 785.3 | 684.2 | 535.3 | 727.4 | 429.6 | 206.5 | 319.9 | 368.7 | 148.7 | 321.6 | 21 | 43.4 | 63.9 | 58.9 | 177.7 | 162.1 | 48.8 | 112.6 | 96.4 | 71.7
615.3 | 396.3 | 289.6 | 115.84 | 135.4103 | 163.5 | 152.6 | 178.5 | 173.8 | 251.1 | 24.3 | 21.5 | 43.9 | 9.1 | 243.9 | 18.7 | 785.6 | 677.5 | 517.2 | 724.9 | 428.1 | 206.9 | 318.8 | 361.8 | 148.9 | 321.2 | 21 | 43.5 | 64.1 | 59 | 178.3 | 162.1 | 48.9 | 112.8 | 96.6 | 71.9
616.3 | 397.3 | 289.1 | 115.64 | 135.1765 | 163.7 | 153.1 | 178.6 | 174.6 | 248.6 | 24.2 | 21.5 | 44 | 11.6 | 246.1 | 16.6 | 785.6 | 667.9 | 502.1 | 724.2 | 427.2 | 207.2 | 316.4 | 357.9 | 149 | 321.1 | 21.1 | 43.6 | 64.2 | 59 | 179.2 | 162.4 | 49.1 | 113.1 | 96.8 | 72.1
617.3 | 398.3 | 287.8 | 115.12 | 134.5686 | 163.1 | 152.8 | 178.8 | 175.7 | 248.6 | 24.2 | 21.5 | 44 | 11.2 | 242.5 | 13.7 | 785.7 | 667.1 | 509.4 | 728.9 | 427.9 | 207.6 | 317.2 | 361.1 | 149.2 | 322.1 | 21.1 | 43.7 | 64.3 | 59.2 | 179.1 | 162.7 | 49.2 | 113.3 | 96.9 | 72.3
618.3 | 399.3 | 287.9 | 115.16 | 134.6154 | 163.1 | 152.1 | 178.9 | 175.8 | 251.2 | 24.3 | 21.4 | 44.2 | 11.2 | 246.1 | 11.4 | 787 | 674.6 | 516.2 | 734.1 | 428.6 | 207.9 | 320.3 | 364 | 149.5 | 322.8 | 21.1 | 43.8 | 64.5 | 59.2 | 179.5 | 163 | 49.3 | 113.5 | 97.1 | 72.4
619.3 | 400.3 | 287.8 | 115.12 | 134.5686 | 163.3 | 151.8 | 179.3 | 176.3 | 254.7 | 24.3 | 21.4 | 44.3 | 11.5 | 247.9 | 13.5 | 789.1 | 677.2 | 508.9 | 736.8 | 428.5 | 208.3 | 322.2 | 369.9 | 149.8 | 323.2 | 21.2 | 43.9 | 64.7 | 59.3 | 180.1 | 163.4 | 49.4 | 113.7 | 97.3 | 72.6
620.3 | 401.3 | 287.5 | 115 | 134.4284 | 163 | 151.3 | 179.5 | 176.1 | 258.8 | 24.3 | 21.5 | 44.4 | 11 | 243.9 | 15.3 | 790.4 | 684.3 | 516.6 | 735.2 | 429.2 | 208.6 | 323.8 | 369.9 | 150 | 323.9 | 21.2 | 43.9 | 64.8 | 59.5 | 180.1 | 163.5 | 49.5 | 113.9 | 97.5 | 72.8
621.3 | 402.3 | 288.1 | 115.24 | 134.7089 | 163.6 | 152.3 | 180.1 | 176.4 | 258.7 | 24.4 | 21.4 | 44.5 | 11.9 | 237.5 | 14.8 | 791.1 | 685.1 | 510.8 | 734.2 | 428.3 | 209 | 322.2 | 363.5 | 150.3 | 323.7 | 21.3 | 44 | 64.9 | 59.6 | 180.2 | 163.7 | 49.6 | 114 | 97.7 | 72.9
622.3 | 403.3 | 288.5 | 115.4 | 134.896 | 164.5 | 153.7 | 180.4 | 177 | 255.2 | 24.4 | 21.4 | 44.6 | 11.7 | 248.8 | 15.7 | 791.2 | 679.8 | 503.1 | 731.6 | 427.8 | 209.3 | 319.9 | 362.2 | 150.5 | 323.1 | 21.3 | 44.2 | 65.1 | 59.6 | 180.2 | 163.7 | 49.8 | 114.2 | 97.8 | 73.1
623.3 | 404.3 | 288.2 | 115.28 | 134.7557 | 165.2 | 154.4 | 180.5 | 177.4 | 253.8 | 24.4 | 21.4 | 44.6 | 9.2 | 243.7 | 19 | 790.7 | 675.9 | 496.2 | 728.5 | 426.9 | 209.7 | 316.4 | 356.7 | 150.7 | 322.2 | 21.3 | 44.3 | 65.3 | 59.7 | 179.9 | 163.7 | 49.9 | 114.4 | 98 | 73.2
624.3 | 405.3 | 288.5 | 115.4 | 134.896 | 165.6 | 154.6 | 181.1 | 177.3 | 251.5 | 24.5 | 21.4 | 44.5 | 9.6 | 249.4 | 19.7 | 790.2 | 672.1 | 489.3 | 726 | 427.4 | 210 | 314.5 | 356.5 | 150.9 | 322 | 21.4 | 44.4 | 65.3 | 59.8 | 180.2 | 164.1 | 50 | 114.6 | 98.2 | 73.4
625.3 | 406.3 | 287.7 | 115.08 | 134.5219 | 167.5 | 155 | 181.9 | 177.2 | 250.6 | 24.5 | 21.4 | 44.5 | 10.3 | 246.9 | 20.9 | 789.5 | 658.3 | 473 | 723.9 | 425.6 | 210.4 | 310.2 | 348.9 | 151.1 | 320.7 | 21.4 | 44.5 | 65.5 | 59.9 | 179.8 | 164.6 | 50.1 | 114.9 | 98.3 | 73.5
626.3 | 407.3 | 288.2 | 115.28 | 134.7557 | 169.7 | 155.8 | 182.6 | 176.6 | 247.5 | 24.5 | 21.4 | 44.5 | 9.5 | 236.1 | 18.9 | 788.3 | 644.9 | 461.5 | 722.2 | 424.8 | 210.7 | 306.8 | 344.4 | 151.2 | 319.8 | 21.4 | 44.6 | 65.6 | 60 | 180.4 | 164.9 | 50.2 | 115 | 98.4 | 73.6
627.3 | 408.3 | 288.9 | 115.56 | 135.083 | 170.6 | 156 | 182.4 | 176.2 | 245.8 | 24.5 | 21.4 | 44.5 | 9.2 | 233 | 14.9 | 787.2 | 643.5 | 461.8 | 718.1 | 424.8 | 211 | 304.4 | 339 | 151.3 | 319.4 | 21.5 | 44.7 | 65.8 | 60.1 | 181.5 | 165.2 | 50.3 | 115.2 | 98.5 | 73.8
628.3 | 409.3 | 287.9 | 115.16 | 134.6154 | 170.8 | 155.4 | 182 | 176.3 | 243.3 | 24.6 | 21.4 | 44.5 | 10.2 | 239.8 | 16 | 786.3 | 649.2 | 466.6 | 714.3 | 425.4 | 211.3 | 302.8 | 335 | 151.5 | 318.9 | 21.5 | 44.8 | 65.9 | 60.2 | 181.4 | 165.7 | 50.4 | 115.5 | 98.6 | 74
629.3 | 410.3 | 288.5 | 115.4 | 134.896 | 171.7 | 155.1 | 182.1 | 176.9 | 241.3 | 24.6 | 21.4 | 44.5 | 8.2 | 247.3 | 17.9 | 785.6 | 656.1 | 481 | 716.3 | 427.7 | 211.6 | 304.2 | 339.6 | 151.8 | 319.4 | 21.6 | 44.9 | 66 | 60.3 | 181.4 | 165.6 | 50.5 | 115.6 | 98.7 | 74.1
630.3 | 411.3 | 288.6 | 115.44 | 134.9427 | 173.3 | 155.3 | 181.5 | 177.1 | 242.6 | 24.7 | 21.4 | 44.5 | 8.3 | 248.1 | 16.5 | 785.6 | 659.1 | 479.3 | 716.8 | 427.9 | 211.9 | 305.6 | 341.3 | 152.1 | 319.4 | 21.6 | 45 | 66.1 | 60.4 | 181.1 | 165.8 | 50.6 | 115.7 | 98.8 | 74.3
631.3 | 412.3 | 288.6 | 115.44 | 134.9427 | 172.9 | 156.2 | 181.4 | 177 | 243.7 | 24.8 | 21.4 | 44.6 | 10.2 | 244.7 | 15.6 | 785.6 | 665 | 481.4 | 716.1 | 428 | 212.2 | 304.7 | 341.5 | 152.4 | 319.4 | 21.6 | 45.1 | 66.3 | 60.5 | 180.6 | 165.9 | 50.8 | 116 | 98.9 | 74.4
632.3 | 413.3 | 288.8 | 115.52 | 135.0362 | 172.9 | 156.9 | 181.1 | 176.8 | 244.1 | 24.8 | 21.4 | 44.8 | 9.8 | 225.5 | 14.4 | 785.2 | 671.9 | 486.8 | 713.8 | 428.3 | 212.5 | 306.1 | 343 | 152.6 | 319.6 | 21.7 | 45.2 | 66.3 | 60.7 | 180.9 | 165.7 | 50.9 | 116.2 | 99.1 | 74.5
633.3 | 414.3 | 288.3 | 115.32 | 134.8024 | 173.9 | 157.1 | 181.3 | 176.9 | 245 | 24.8 | 21.4 | 44.9 | 9 | 239.6 | 11.7 | 784.7 | 680.5 | 496.5 | 712.4 | 428.6 | 212.8 | 307.2 | 343.2 | 152.9 | 320 | 21.7 | 45.3 | 66.3 | 60.8 | 181.2 | 165.8 | 51 | 116.4 | 99.3 | 74.7
634.3 | 415.3 | 288.6 | 115.44 | 134.9427 | 174 | 157 | 181.7 | 176.7 | 245.1 | 24.8 | 21.4 | 44.9 | 9.4 | 234.8 | 13.2 | 784.4 | 685.6 | 496.3 | 710.3 | 428.9 | 213.1 | 309.8 | 345.8 | 153.2 | 320.6 | 21.8 | 45.4 | 66.5 | 60.9 | 181.1 | 165.4 | 51.1 | 116.5 | 99.4 | 74.8
635.3 | 416.3 | 289.1 | 115.64 | 135.1765 | 173.4 | 157 | 182.9 | 176.4 | 249 | 24.8 | 21.4 | 45 | 9 | 227.9 | 11.8 | 784.4 | 691.2 | 501.5 | 709 | 429.5 | 213.4 | 312.6 | 353.5 | 153.6 | 321.3 | 21.8 | 45.5 | 66.7 | 61 | 181.4 | 165.5 | 51.2 | 116.6 | 99.6 | 74.9
636.3 | 417.3 | 288.6 | 115.44 | 134.9427 | 173 | 156.9 | 183.4 | 175.9 | 253.5 | 24.9 | 21.4 | 45.1 | 9.2 | 241.7 | 11.1 | 784.5 | 693.1 | 502.7 | 707.8 | 430.4 | 213.7 | 314.3 | 360.8 | 153.9 | 321.9 | 21.8 | 45.6 | 66.8 | 61.1 | 181.2 | 165.9 | 51.3 | 116.9 | 99.8 | 75
637.3 | 418.3 | 288.8 | 115.52 | 135.0362 | 172.4 | 157 | 183.7 | 176.7 | 254.4 | 24.9 | 21.4 | 45.2 | 9 | 243.5 | 10.8 | 785.1 | 698.7 | 508.2 | 712.8 | 431.1 | 213.9 | 317.6 | 366.8 | 154.4 | 323.3 | 21.9 | 45.7 | 67 | 61.2 | 180.9 | 165.6 | 51.4 | 117.1 | 100.1 | 75.2
638.3 | 419.3 | 289.1 | 115.64 | 135.1765 | 172.1 | 155.9 | 183.8 | 177.4 | 253.4 | 25 | 21.4 | 45.3 | 9.5 | 233.5 | 10.7 | 785.5 | 703.4 | 510.9 | 716.3 | 430.7 | 214.2 | 320.4 | 367.9 | 154.9 | 324.3 | 21.9 | 45.8 | 67.1 | 61.3 | 181.4 | 165.4 | 51.6 | 117.2 | 100.4 | 75.4
639.3 | 420.3 | 288.9 | 115.56 | 135.083 | 171.5 | 156.1 | 183.7 | 177.3 | 253.7 | 25.1 | 21.4 | 45.3 | 9.9 | 247.8 | 11.7 | 785.8 | 710.3 | 527.3 | 720.1 | 433.4 | 214.5 | 325.9 | 372.2 | 155.6 | 327.4 | 22 | 45.9 | 67.2 | 61.5 | 181.5 | 165.2 | 51.7 | 117.3 | 100.6 | 75.5
640.3 | 421.3 | 288.9 | 115.56 | 135.083 | 172.1 | 157.5 | 183.2 | 178 | 255.9 | 25 | 21.4 | 45.4 | 9.1 | 235.5 | 12.6 | 786.8 | 719.7 | 544.1 | 722.1 | 438.8 | 214.7 | 334.3 | 390.3 | 156.4 | 330.3 | 22 | 46 | 67.4 | 61.6 | 181.5 | 165.2 | 51.8 | 117.6 | 100.8 | 75.7
641.3 | 422.3 | 288.9 | 115.56 | 135.083 | 172.3 | 157.9 | 182.5 | 177.6 | 259.9 | 25.1 | 21.4 | 45.4 | 8.3 | 241.3 | 15.5 | 787.9 | 725.1 | 552.6 | 722.6 | 440.3 | 215 | 336.1 | 391.9 | 157.2 | 332 | 22 | 46.1 | 67.7 | 61.7 | 181.8 | 165.2 | 51.9 | 117.8 | 101 | 75.8
642.3 | 423.3 | 289.8 | 115.92 | 135.5038 | 171.5 | 157.9 | 182.8 | 175.9 | 262.2 | 25.1 | 21.4 | 45.4 | 8.6 | 240.5 | 18.8 | 788.5 | 723.1 | 550.8 | 720.9 | 440 | 215.3 | 337.4 | 390.5 | 157.7 | 332.6 | 22.1 | 46.2 | 67.9 | 61.8 | 181.9 | 165.3 | 52.1 | 118 | 101.3 | 75.9
643.3 | 424.3 | 287 | 114.8 | 134.1946 | 171.3 | 158.8 | 183.5 | 176.2 | 265.3 | 25.2 | 21.4 | 45.4 | 10 | 238.6 | 17.7 | 788.6 | 728.8 | 560.9 | 725.4 | 442 | 215.5 | 340.2 | 395.9 | 158.3 | 334.3 | 22.1 | 46.3 | 67.8 | 61.9 | 182.1 | 165.3 | 52.1 | 118.2 | 101.5 | 76.1
644.3 | 425.3 | 287.8 | 115.12 | 134.5686 | 171.9 | 159.3 | 183.8 | 177 | 267.3 | 25.2 | 21.4 | 45.4 | 10.5 | 240.3 | 15.3 | 789.5 | 732 | 567.3 | 728.2 | 443.9 | 215.8 | 342.1 | 399.3 | 158.9 | 335.1 | 22.2 | 46.4 | 67.8 | 62 | 182.2 | 165.5 | 52.3 | 118.3 | 101.7 | 76.3
645.3 | 426.3 | 288.7 | 115.48 | 134.9895 | 171.6 | 160.3 | 183.5 | 177.5 | 268.4 | 25.3 | 21.4 | 45.3 | 9.6 | 236 | 16.9 | 790.6 | 737.1 | 568.4 | 726.9 | 444.3 | 216.1 | 343.9 | 405.7 | 159.5 | 335.3 | 22.2 | 46.5 | 68 | 62.1 | 182.3 | 166.3 | 52.4 | 118.6 | 101.9 | 76.4
646.3 | 427.3 | 289 | 115.6 | 135.1297 | 171.1 | 161.3 | 182.3 | 177.2 | 268.3 | 25.3 | 21.4 | 45.4 | 9.4 | 243.8 | 15.7 | 791.3 | 737.8 | 567.1 | 727.8 | 444.1 | 216.3 | 343.4 | 400.3 | 160 | 335.9 | 22.3 | 46.6 | 68.2 | 62.2 | 181.9 | 166.6 | 52.4 | 118.8 | 102.1 | 76.6
647.3 | 428.3 | 289.6 | 115.84 | 135.4103 | 170.6 | 161 | 181.7 | 175.7 | 265.8 | 25.4 | 21.4 | 45.4 | 10.5 | 245.2 | 13.2 | 791.7 | 734 | 560.1 | 724.2 | 444.4 | 216.6 | 342.2 | 398.4 | 160.5 | 335.9 | 22.3 | 46.7 | 68.3 | 62.3 | 181.4 | 166.7 | 52.6 | 119 | 102.2 | 76.7
648.3 | 429.3 | 289.9 | 115.96 | 135.5506 | 169 | 160.5 | 181.4 | 175.4 | 264.6 | 25.4 | 21.4 | 45.4 | 11.1 | 241.1 | 12.4 | 791.5 | 733.3 | 547.1 | 722.1 | 445.1 | 216.9 | 340.9 | 393.8 | 160.9 | 335.7 | 22.3 | 46.8 | 68.5 | 62.4 | 180.8 | 166.7 | 52.7 | 119.1 | 102.4 | 76.9
649.3 | 430.3 | 286.5 | 114.6 | 133.9608 | 168.1 | 160.7 | 181.2 | 176.2 | 264.2 | 25.3 | 21.4 | 45.4 | 10.7 | 242.8 | 15.6 | 791.5 | 727 | 542.7 | 721 | 445.4 | 217.1 | 340.1 | 390.7 | 161.3 | 335.5 | 22.4 | 46.9 | 68.8 | 62.5 | 180.8 | 166.6 | 52.8 | 119.1 | 102.6 | 77
650.3 | 431.3 | 287.6 | 115.04 | 134.4751 | 169.1 | 160 | 181 | 176.2 | 264.1 | 25.3 | 21.4 | 45.4 | 10.9 | 247 | 17.2 | 791.2 | 727.6 | 535.5 | 720.9 | 445.9 | 217.4 | 339.7 | 387.8 | 161.6 | 335.7 | 22.4 | 47 | 68.9 | 62.6 | 180.6 | 166.3 | 53 | 119.3 | 102.8 | 77.1
651.3 | 432.3 | 288 | 115.2 | 134.6622 | 170.2 | 159.4 | 181.5 | 176.4 | 262.7 | 25.3 | 21.4 | 45.4 | 9.6 | 249.6 | 17.3 | 791 | 728.7 | 540.5 | 720.4 | 447 | 217.7 | 338.9 | 384.9 | 161.9 | 335.6 | 22.5 | 47.1 | 69 | 62.6 | 180.5 | 166.3 | 53 | 119.6 | 102.9 | 77.3
652.3 | 433.3 | 287.3 | 114.92 | 134.3349 | 172 | 158.8 | 181.1 | 176.5 | 259.7 | 25.3 | 21.4 | 45.4 | 10.3 | 253.2 | 14.6 | 791.1 | 729.3 | 537.5 | 719.7 | 446.8 | 218 | 338.4 | 390.7 | 162.2 | 335.7 | 22.5 | 47.2 | 69.1 | 62.8 | 180.9 | 166 | 53.2 | 119.8 | 103.1 | 77.4
653.3 | 434.3 | 287.1 | 114.84 | 134.2413 | 174.1 | 159 | 181.6 | 177.2 | 261.6 | 25.3 | 21.4 | 45.5 | 10.4 | 242.7 | 12 | 791.8 | 731 | 540.9 | 721.3 | 447.9 | 218.2 | 338.8 | 397.8 | 162.5 | 336.3 | 22.5 | 47.4 | 69.3 | 62.8 | 180.9 | 166.1 | 53.3 | 119.9 | 103.3 | 77.6
654.3 | 435.3 | 289.8 | 115.92 | 135.5038 | 173.9 | 159.1 | 182.3 | 176.9 | 263.9 | 25.3 | 21.4 | 45.5 | 9.7 | 240 | 16.9 | 792.1 | 730.9 | 530.4 | 723.1 | 448.4 | 218.5 | 338.6 | 396.2 | 162.9 | 336.3 | 22.6 | 47.5 | 69.4 | 62.9 | 181.1 | 167 | 53.4 | 120.1 | 103.4 | 77.7
655.3 | 436.3 | 290.6 | 116.24 | 135.8779 | 173.1 | 159.3 | 183 | 177 | 261.9 | 25.3 | 21.4 | 45.6 | 9.1 | 245.8 | 18.9 | 791.8 | 729.6 | 522.5 | 722.4 | 447.8 | 218.8 | 336 | 388.8 | 163.3 | 336 | 22.6 | 47.6 | 69.5 | 63 | 181.4 | 167.5 | 53.5 | 120.4 | 103.6 | 77.8
656.3 | 437.3 | 289.3 | 115.72 | 135.27 | 172.9 | 159.8 | 182.9 | 177.4 | 260.9 | 25.3 | 21.4 | 45.7 | 9.9 | 241.8 | 17.2 | 791.3 | 729.8 | 508.8 | 721.2 | 447.9 | 219.1 | 333.9 | 383.2 | 163.7 | 335.5 | 22.7 | 47.7 | 69.5 | 63.1 | 181.7 | 167.2 | 53.6 | 120.5 | 103.8 | 78
657.3 | 438.3 | 289.2 | 115.68 | 135.2233 | 172.2 | 159.7 | 183.3 | 177.4 | 257.5 | 25.3 | 21.4 | 45.9 | 11.2 | 240.5 | 18 | 791 | 732.2 | 505.2 | 721 | 449.5 | 219.4 | 331.9 | 382.2 | 164 | 335.7 | 22.7 | 47.8 | 69.8 | 63.2 | 182.3 | 167.3 | 53.7 | 120.7 | 103.9 | 78.1
658.3 | 439.3 | 289 | 115.6 | 135.1297 | 172.1 | 159.8 | 183.2 | 178.7 | 257.5 | 25.4 | 21.4 | 46 | 9.8 | 243.1 | 16.2 | 790.3 | 727.3 | 498.8 | 716.9 | 449.5 | 219.7 | 330.7 | 382.9 | 164.3 | 335.2 | 22.7 | 47.9 | 69.8 | 63.3 | 182.8 | 167.3 | 53.8 | 120.9 | 104.1 | 78.3
659.3 | 440.3 | 287.7 | 115.08 | 134.5219 | 173.3 | 159.4 | 183.1 | 180 | 260.7 | 25.4 | 21.4 | 46 | 9.2 | 243.1 | 14.4 | 789.6 | 726.3 | 492.3 | 715.7 | 449.3 | 220 | 331.6 | 385.9 | 164.8 | 335.7 | 22.8 | 48 | 70.2 | 63.4 | 183 | 168 | 54 | 121.1 | 104.3 | 78.5
660.3 | 441.3 | 287.7 | 115.08 | 134.5219 | 174 | 159.5 | 182.6 | 180.9 | 260.7 | 25.3 | 21.4 | 45.9 | 8.6 | 237.4 | 16 | 788.4 | 718.9 | 485.9 | 713.1 | 449 | 220.2 | 329.3 | 378.4 | 165.2 | 335.2 | 22.8 | 48.1 | 70.2 | 63.5 | 183.2 | 168.2 | 54.1 | 121.3 | 104.5 | 78.7
661.3 | 442.3 | 289.6 | 115.84 | 135.4103 | 173.7 | 160.2 | 182.4 | 180.8 | 257.3 | 25.3 | 21.4 | 45.9 | 9.7 | 240.1 | 15.7 | 787.7 | 723.8 | 488.1 | 713.2 | 450.8 | 220.5 | 329.7 | 381.5 | 165.7 | 335.6 | 22.9 | 48.2 | 70.3 | 63.6 | 183.3 | 168.2 | 54.2 | 121.6 | 104.7 | 78.8
662.3 | 443.3 | 289.6 | 115.84 | 135.4103 | 174 | 161.1 | 182.2 | 180.4 | 256.8 | 25.3 | 21.4 | 46 | 11.3 | 236 | 17.5 | 786.9 | 724.3 | 488.3 | 711.6 | 451.3 | 220.8 | 327.8 | 378.2 | 166.3 | 335.1 | 22.9 | 48.3 | 70.3 | 63.7 | 183.4 | 168.3 | 54.3 | 121.7 | 104.9 | 79
663.3 | 444.3 | 289.6 | 115.84 | 135.4103 | 174.6 | 161.5 | 181 | 180.5 | 255.2 | 25.3 | 21.4 | 46 | 11.6 | 240.3 | 17.5 | 786.2 | 723.4 | 478.6 | 711.1 | 450.7 | 221 | 326.1 | 374.4 | 167 | 335 | 23 | 48.3 | 70.4 | 63.9 | 183.7 | 168.5 | 54.4 | 122 | 105 | 79.2
664.3 | 445.3 | 289.6 | 115.84 | 135.4103 | 174.9 | 161.7 | 179.9 | 180.8 | 253.8 | 25.3 | 21.4 | 46.1 | 10.9 | 252.3 | 14.1 | 785.6 | 722.3 | 478.1 | 709.5 | 451.7 | 221.3 | 326.1 | 375.6 | 167.7 | 335.2 | 23 | 48.4 | 70.7 | 64 | 183.5 | 168.3 | 54.5 | 122 | 105.2 | 79.3
665.3 | 446.3 | 289.7 | 115.88 | 135.457 | 174.7 | 162 | 180.1 | 180.6 | 255 | 25.3 | 21.4 | 46.1 | 11.7 | 244.8 | 12.5 | 785.1 | 724.6 | 483.6 | 707.7 | 452.2 | 221.6 | 326.2 | 377.7 | 168.7 | 335.3 | 23 | 48.5 | 70.7 | 64.1 | 183.5 | 168 | 54.6 | 122.1 | 105.4 | 79.4
666.3 | 447.3 | 289.8 | 115.92 | 135.5038 | 175.6 | 162.2 | 180 | 179.8 | 254.9 | 25.3 | 21.4 | 46.1 | 12 | 250.3 | 12.1 | 785.3 | 730.3 | 509.2 | 712 | 455 | 221.8 | 330.3 | 394.5 | 170.1 | 337.7 | 23.1 | 48.6 | 70.9 | 64.2 | 183.5 | 167.7 | 54.7 | 122.1 | 105.5 | 79.6
667.3 | 448.3 | 289.6 | 115.84 | 135.4103 | 176.1 | 162.1 | 180.1 | 179.9 | 262.8 | 25.2 | 21.4 | 46.2 | 11.1 | 241.9 | 15.6 | 786.3 | 737.6 | 522.4 | 714.9 | 456.6 | 222.1 | 337.3 | 409.6 | 172.2 | 339.8 | 23.1 | 48.7 | 71.2 | 64.3 | 183.7 | 168 | 54.8 | 122.3 | 105.7 | 79.7
668.3 | 449.3 | 289.6 | 115.84 | 135.4103 | 175.1 | 162.9 | 180.4 | 180.2 | 264.6 | 25.2 | 21.4 | 46.2 | 10 | 241.8 | 17.3 | 787.1 | 742.9 | 554.6 | 720.7 | 459.4 | 222.4 | 342.5 | 416.5 | 174 | 342 | 23.2 | 48.8 | 71.1 | 64.4 | 183.8 | 168.5 | 55 | 122.4 | 105.9 | 79.8
669.3 | 450.3 | 289.4 | 115.76 | 135.3168 | 174.6 | 163.5 | 181 | 181.1 | 267.1 | 25.2 | 21.4 | 46.3 | 9 | 232.2 | 14.6 | 788.2 | 748.7 | 560.1 | 726.2 | 460.5 | 222.6 | 348 | 426.5 | 176.3 | 343.8 | 23.2 | 48.9 | 71.3 | 64.5 | 184 | 168.7 | 55.1 | 122.6 | 106.1 | 80
670.3 | 451.3 | 289.4 | 115.76 | 135.3168 | 174.3 | 163.5 | 180.5 | 181.5 | 266.1 | 25.2 | 21.4 | 46.3 | 10 | 241.6 | 14.8 | 789.3 | 753.9 | 566.4 | 725.3 | 462.5 | 222.9 | 348.7 | 421.2 | 178.2 | 344.6 | 23.3 | 49 | 71.5 | 64.6 | 184.4 | 168.8 | 55.2 | 122.9 | 106.3 | 80.1
671.3 | 452.3 | 289.1 | 115.64 | 135.1765 | 173.8 | 163.9 | 180.1 | 182.3 | 264.1 | 25.1 | 21.4 | 46.4 | 10.1 | 246.8 | 18.8 | 789.9 | 755.4 | 553.1 | 725.1 | 462.2 | 223.1 | 348 | 420.4 | 179.9 | 345.1 | 23.3 | 49.1 | 71.7 | 64.7 | 185.2 | 168.7 | 55.3 | 123 | 106.5 | 80.3
672.3 | 453.3 | 289 | 115.6 | 135.1297 | 173.5 | 163.5 | 179.3 | 182.6 | 263.9 | 25.1 | 21.4 | 46.4 | 10.8 | 246.2 | 18.8 | 790.4 | 753.8 | 549.8 | 724 | 463 | 223.4 | 346.9 | 422.3 | 181.3 | 344.9 | 23.4 | 49.2 | 71.7 | 64.8 | 185.6 | 168.7 | 55.4 | 123.1 | 106.7 | 80.4
673.3 | 454.3 | 288.9 | 115.56 | 135.083 | 173.7 | 162.6 | 179.2 | 182.7 | 265.9 | 25.2 | 21.4 | 46.5 | 9.4 | 244.3 | 18.4 | 790.9 | 757.4 | 560.4 | 724.6 | 465.4 | 223.7 | 348.8 | 424.8 | 182.8 | 346.4 | 23.4 | 49.3 | 71.9 | 64.9 | 185.9 | 168.7 | 55.5 | 123.2 | 106.9 | 80.6
674.3 | 455.3 | 288.9 | 115.56 | 135.083 | 173.5 | 162.4 | 179.6 | 182.9 | 267.4 | 25.2 | 21.4 | 46.4 | 9.1 | 244.3 | 17 | 790.9 | 760.7 | 559 | 723.9 | 466.2 | 223.9 | 349.1 | 422.2 | 184.5 | 347.9 | 23.4 | 49.4 | 72 | 65 | 186.3 | 168.7 | 55.6 | 123.5 | 107.1 | 80.7
675.3 | 456.3 | 289.1 | 115.64 | 135.1765 | 173.9 | 161.9 | 180 | 182.7 | 265.9 | 25.2 | 21.4 | 46.5 | 8.9 | 245.8 | 16.2 | 790.7 | 762.4 | 549.8 | 721.6 | 466.2 | 224.2 | 349 | 420.8 | 186.3 | 348.3 | 23.5 | 49.5 | 72.2 | 65.1 | 187 | 168.8 | 55.7 | 123.7 | 107.3 | 80.9
676.3 | 457.3 | 288.8 | 115.52 | 135.0362 | 172.8 | 162 | 180.1 | 182.9 | 265.1 | 25.2 | 21.4 | 46.5 | 9.1 | 251.9 | 15.6 | 790.1 | 759.2 | 554.5 | 721.4 | 467.1 | 224.5 | 348.6 | 414.4 | 187.9 | 348.6 | 23.5 | 49.6 | 72.3 | 65.2 | 187.4 | 169.7 | 55.8 | 123.9 | 107.6 | 81.1
677.3 | 458.3 | 288.6 | 115.44 | 134.9427 | 171.4 | 161.9 | 179.2 | 182.5 | 262.6 | 25.2 | 21.4 | 46.5 | 10.6 | 240.9 | 15.3 | 790.3 | 760.8 | 557.2 | 725.2 | 470.1 | 224.7 | 353 | 425.4 | 190 | 351 | 23.6 | 49.7 | 72.4 | 65.3 | 187.3 | 170.6 | 56 | 124.2 | 107.7 | 81.2
678.3 | 459.3 | 288.5 | 115.4 | 134.896 | 171.2 | 161.9 | 179.4 | 181.6 | 262.5 | 25.2 | 21.4 | 46.4 | 9.6 | 242.9 | 15.6 | 790.9 | 761.8 | 553.1 | 724 | 470.1 | 225 | 352.7 | 423.7 | 191.9 | 351 | 23.6 | 49.9 | 72.4 | 65.4 | 187.2 | 171 | 56.1 | 124.4 | 107.9 | 81.4
679.3 | 460.3 | 288.7 | 115.48 | 134.9895 | 171.8 | 162.5 | 179.7 | 180.6 | 260.5 | 25.3 | 21.4 | 46.3 | 10.5 | 253.3 | 14.6 | 790.9 | 758.5 | 543.4 | 721.6 | 470.7 | 225.3 | 350.8 | 414.1 | 193.2 | 350.6 | 23.6 | 50 | 72.6 | 65.5 | 187.2 | 171 | 56.2 | 124.5 | 108.1 | 81.5
680.3 | 461.3 | 288.9 | 115.56 | 135.083 | 172.9 | 162.6 | 180.1 | 181.4 | 256.9 | 25.3 | 21.4 | 46.2 | 10.6 | 258.6 | 11.6 | 790.2 | 756.1 | 536.8 | 720.3 | 471.8 | 225.6 | 348.8 | 408.5 | 194.4 | 350.4 | 23.7 | 50.1 | 72.7 | 65.6 | 187.1 | 171.1 | 56.3 | 124.7 | 108.3 | 81.7
681.3 | 462.3 | 288.8 | 115.52 | 135.0362 | 173.1 | 162.9 | 180.1 | 182.7 | 255.6 | 25.4 | 21.4 | 46.2 | 10.4 | 271 | 11.2 | 789.5 | 757.3 | 526.5 | 719.1 | 473.3 | 225.8 | 348.2 | 408.8 | 195.6 | 351 | 23.7 | 50.2 | 72.8 | 65.7 | 187.5 | 171.2 | 56.4 | 124.9 | 108.5 | 81.9
682.3 | 463.3 | 288.8 | 115.52 | 135.0362 | 173.4 | 163.1 | 179.7 | 183.1 | 257.1 | 25.4 | 21.4 | 46.1 | 10.9 | 218.7 | 11.9 | 788.8 | 753.1 | 522.2 | 718.3 | 474.1 | 226.1 | 347.2 | 405.4 | 196.6 | 350.8 | 23.8 | 50.3 | 72.9 | 65.9 | 188 | 171.1 | 56.5 | 125.1 | 108.7 | 82
683.3 | 464.3 | 289.1 | 115.64 | 135.1765 | 173.8 | 163.7 | 180.1 | 183.5 | 256.3 | 25.5 | 21.4 | 46 | 9.4 | 234.4 | 11.2 | 788 | 750.4 | 522.3 | 715.8 | 476.1 | 226.4 | 348.3 | 401.7 | 197.9 | 351.6 | 23.8 | 50.4 | 73.1 | 66 | 187.8 | 171.6 | 56.7 | 125.3 | 108.9 | 82.2
684.3 | 465.3 | 288.9 | 115.56 | 135.083 | 172.8 | 163.7 | 180 | 184.4 | 254.9 | 25.5 | 21.4 | 45.9 | 8 | 242.3 | 14.1 | 787.2 | 750.7 | 520.4 | 714.7 | 478.1 | 226.7 | 349.7 | 401.7 | 199.3 | 352 | 23.9 | 50.5 | 73.2 | 66.1 | 187.6 | 171.3 | 56.7 | 125.4 | 109.1 | 82.3
685.3 | 466.3 | 288.9 | 115.56 | 135.083 | 172.8 | 163.3 | 180.3 | 184.3 | 252.5 | 25.5 | 21.4 | 45.9 | 9.3 | 241.5 | 16.8 | 786.6 | 749 | 505.9 | 714.3 | 478.8 | 226.9 | 347.8 | 397.2 | 200.2 | 351.9 | 23.9 | 50.6 | 73.3 | 66.2 | 187.8 | 171.1 | 56.9 | 125.6 | 109.3 | 82.5
686.3 | 467.3 | 288.9 | 115.56 | 135.083 | 174.3 | 162.9 | 180.5 | 183.6 | 251.2 | 25.5 | 21.4 | 45.9 | 10 | 241.1 | 16.6 | 785.4 | 737.4 | 490.3 | 713.2 | 479.5 | 227.2 | 344.5 | 391.6 | 201 | 351.2 | 23.9 | 50.7 | 73.4 | 66.3 | 187.5 | 171.5 | 57 | 125.7 | 109.5 | 82.6
687.3 | 468.3 | 288.7 | 115.48 | 134.9895 | 175 | 162.7 | 180.8 | 183.5 | 249.3 | 25.5 | 21.4 | 46 | 8.6 | 250.3 | 15.3 | 783.6 | 731.1 | 489.6 | 709.7 | 480.2 | 227.5 | 341.5 | 388.2 | 201.5 | 350.5 | 24 | 50.8 | 73.5 | 66.4 | 187.3 | 171.7 | 57.1 | 125.8 | 109.7 | 82.7
688.3 | 469.3 | 288.6 | 115.44 | 134.9427 | 175.7 | 163 | 181.2 | 183.6 | 248.5 | 25.5 | 21.4 | 46 | 8.5 | 230.3 | 14 | 781 | 726.9 | 480.1 | 704.6 | 481.1 | 227.8 | 340.1 | 383.5 | 202.1 | 350.6 | 24 | 50.9 | 73.7 | 66.6 | 188 | 171.8 | 57.2 | 126.1 | 109.8 | 82.9
689.3 | 470.3 | 289.1 | 115.64 | 135.1765 | 176.7 | 162.8 | 181.1 | 183.8 | 247.6 | 25.6 | 21.4 | 46.1 | 9.9 | 231.8 | 12.9 | 778.1 | 723.2 | 468 | 702.6 | 482.7 | 228 | 336.5 | 376.2 | 202.6 | 350 | 24.1 | 51 | 73.6 | 66.7 | 187.5 | 172.1 | 57.3 | 126.3 | 110 | 83
690.3 | 471.3 | 290 | 116 | 135.5973 | 176.5 | 162.4 | 180.8 | 183.2 | 244.7 | 25.6 | 21.4 | 46.1 | 9.9 | 243.7 | 13.7 | 775.9 | 705.4 | 456.1 | 700.3 | 484.7 | 228.3 | 333.3 | 371.5 | 202.9 | 349.2 | 24.1 | 51.1 | 73.9 | 66.8 | 187.3 | 172.3 | 57.4 | 126.5 | 110.1 | 83.2
691.3 | 472.3 | 288.2 | 115.28 | 134.7557 | 176.8 | 161.2 | 181.2 | 182.9 | 243.9 | 25.7 | 21.4 | 46.2 | 9.9 | 231.3 | 15.8 | 773.4 | 674.8 | 440.8 | 697.8 | 484.7 | 228.5 | 329 | 365 | 202.8 | 347.9 | 24.2 | 51.2 | 73.9 | 66.9 | 186.7 | 172.2 | 57.5 | 126.6 | 110.3 | 83.3
692.3 | 473.3 | 289.2 | 115.68 | 135.2233 | 176.5 | 159.5 | 181.4 | 182.5 | 241.7 | 25.7 | 21.4 | 46.2 | 9.9 | 225.9 | 15.1 | 770.6 | 665.3 | 431.9 | 694.5 | 485 | 228.8 | 324.4 | 359.2 | 202.6 | 346.7 | 24.2 | 51.3 | 73.9 | 67 | 186.1 | 172.2 | 57.7 | 126.8 | 110.4 | 83.5
693.3 | 474.3 | 289.1 | 115.64 | 135.1765 | 175.7 | 159.3 | 182.2 | 181.8 | 239.9 | 25.7 | 21.4 | 46.3 | 9.6 | 244.2 | 14.4 | 768 | 661.4 | 425.7 | 689.3 | 485 | 229 | 321.4 | 355.5 | 202.6 | 346.2 | 24.3 | 51.4 | 74.1 | 67.1 | 185.7 | 172.5 | 57.8 | 126.9 | 110.5 | 83.6
694.3 | 475.3 | 289 | 115.6 | 135.1297 | 175.1 | 159.4 | 182 | 181.3 | 238.9 | 25.8 | 21.4 | 46.5 | 9.4 | 247.9 | 16.4 | 765.7 | 664.2 | 421.3 | 686.6 | 486.6 | 229.3 | 319.2 | 353.1 | 202.8 | 345.7 | 24.3 | 51.5 | 74.3 | 67.3 | 185.3 | 172.6 | 57.8 | 127.1 | 110.6 | 83.7
695.3 | 476.3 | 289.4 | 115.76 | 135.3168 | 175.1 | 159.1 | 181.4 | 180.8 | 237.8 | 25.8 | 21.4 | 46.6 | 8.5 | 247.4 | 17.5 | 763.7 | 661.2 | 412.5 | 682.8 | 488.2 | 229.5 | 315.7 | 347.4 | 202.8 | 344.7 | 24.4 | 51.6 | 74.5 | 67.4 | 184.7 | 172.7 | 58 | 127.3 | 110.7 | 83.9
696.3 | 477.3 | 289.5 | 115.8 | 135.3635 | 175.2 | 158.3 | 181.9 | 180.4 | 235.8 | 25.8 | 21.4 | 46.6 | 7.7 | 252.9 | 17.8 | 761.3 | 648.3 | 410.6 | 678.2 | 487.4 | 229.7 | 311.9 | 343.7 | 202.7 | 343.4 | 24.4 | 51.7 | 74.6 | 67.5 | 184.2 | 172.4 | 58.1 | 127.2 | 110.9 | 84
697.3 | 478.3 | 287.8 | 115.12 | 134.5686 | 174.2 | 157.8 | 181.3 | 179.5 | 234.8 | 25.9 | 21.4 | 46.7 | 7.7 | 257.9 | 16.4 | 758.5 | 651.1 | 403.6 | 674.5 | 487.1 | 229.9 | 309.5 | 340.9 | 202.6 | 342.7 | 24.5 | 51.8 | 74.7 | 67.6 | 183.8 | 172.5 | 58.2 | 127.3 | 111 | 84.1
698.3 | 479.3 | 287.5 | 115 | 134.4284 | 173.8 | 157.2 | 180.9 | 178.2 | 235.5 | 25.9 | 21.4 | 46.8 | 7.8 | 250.2 | 13.9 | 755.8 | 649.3 | 402.9 | 671.8 | 487.7 | 230.1 | 306.5 | 339.1 | 202.5 | 341.6 | 24.5 | 51.9 | 74.9 | 67.7 | 183.1 | 172.2 | 58.3 | 127.4 | 111.1 | 84.2
699.3 | 480.3 | 287.6 | 115.04 | 134.4751 | 174.7 | 157 | 180.6 | 177.2 | 234 | 25.9 | 21.4 | 47 | 8.8 | 255.2 | 11.9 | 753.6 | 647.5 | 399.6 | 669.7 | 488.3 | 230.3 | 302.9 | 334.1 | 202.1 | 340.5 | 24.5 | 52 | 75 | 67.8 | 182.5 | 172 | 58.4 | 127.4 | 111.3 | 84.3
700.3 | 481.3 | 287.9 | 115.16 | 134.6154 | 174.8 | 156.6 | 180.6 | 176.8 | 231.9 | 25.9 | 21.4 | 47.1 | 7.7 | 249 | 11.9 | 751.6 | 632.9 | 393.3 | 668.3 | 488.4 | 230.6 | 300.8 | 331.8 | 201.8 | 339.7 | 24.6 | 52.1 | 75 | 67.9 | 182 | 171.8 | 58.5 | 127.6 | 111.4 | 84.5
701.3 | 482.3 | 287.7 | 115.08 | 134.5219 | 175 | 157.1 | 180.3 | 176.7 | 231.2 | 25.9 | 21.4 | 47.1 | 7.3 | 254.5 | 11.8 | 749.9 | 630.6 | 392.7 | 666.7 | 489.3 | 230.8 | 299 | 330.4 | 201.8 | 339.2 | 24.6 | 52.1 | 75.1 | 68 | 181.2 | 171.3 | 58.6 | 127.6 | 111.5 | 84.6
702.3 | 483.3 | 287.8 | 115.12 | 134.5686 | 174.9 | 157.7 | 179.7 | 176.1 | 231.4 | 25.9 | 21.4 | 47.2 | 7.9 | 271.8 | 11.5 | 748.9 | 636.4 | 420.6 | 666.6 | 492.6 | 231 | 300.3 | 331.6 | 202.3 | 340.2 | 24.7 | 52.2 | 75.3 | 68.1 | 181.1 | 170.7 | 58.7 | 127.7 | 111.6 | 84.7
703.3 | 484.3 | 288 | 115.2 | 134.6622 | 174.4 | 158.4 | 178.6 | 176.1 | 233 | 26 | 21.4 | 47.3 | 8.8 | 265.7 | 12.1 | 748.6 | 646.5 | 451.9 | 668.9 | 496.4 | 231.2 | 306.1 | 335.9 | 203.6 | 342.4 | 24.7 | 52.3 | 75.4 | 68.3 | 180.9 | 170.5 | 58.8 | 127.7 | 111.8 | 84.8
704.3 | 485.3 | 287.7 | 115.08 | 134.5219 | 174.6 | 157.7 | 178.3 | 176.1 | 236.5 | 26 | 21.4 | 47.3 | 8.9 | 268.5 | 12.1 | 748.2 | 647.1 | 454.9 | 668.6 | 498.6 | 231.4 | 310.3 | 337.7 | 205.1 | 343.1 | 24.8 | 52.4 | 75.5 | 68.4 | 180.7 | 170.4 | 58.9 | 127.8 | 112 | 85
705.3 | 486.3 | 287.9 | 115.16 | 134.6154 | 174.4 | 157.3 | 178.3 | 176.4 | 237 | 26.1 | 21.4 | 47.3 | 9.4 | 254.5 | 11.5 | 746.9 | 635.4 | 446.6 | 666.3 | 497.3 | 231.6 | 307.5 | 332 | 205.3 | 341.5 | 24.8 | 52.5 | 75.5 | 68.5 | 180.3 | 170.3 | 59 | 127.8 | 112.2 | 85.1
706.3 | 487.3 | 287.9 | 115.16 | 134.6154 | 175.1 | 157.9 | 178.5 | 176.7 | 235.7 | 26.2 | 21.4 | 47.2 | 9.4 | 249.5 | 11.7 | 746.4 | 646.2 | 443.6 | 669 | 498.4 | 231.8 | 309.5 | 338.3 | 205.9 | 342.1 | 24.9 | 52.6 | 75.5 | 68.6 | 180.8 | 170.2 | 59.1 | 127.9 | 112.4 | 85.2
707.3 | 488.3 | 288.3 | 115.32 | 134.8024 | 175.5 | 158.3 | 178.3 | 176.6 | 241.4 | 26.3 | 21.4 | 47.3 | 9.6 | 269.7 | 9.7 | 746.2 | 638.1 | 433.4 | 667.8 | 498.2 | 231.9 | 311.5 | 342.1 | 207.1 | 341.7 | 24.9 | 52.8 | 75.7 | 68.7 | 180.8 | 170.5 | 59.2 | 128.1 | 112.5 | 85.4
708.3 | 489.3 | 288.6 | 115.44 | 134.9427 | 175 | 158.5 | 178 | 176.1 | 243.3 | 26.4 | 21.4 | 47.3 | 8.4 | 260.9 | 9.5 | 744.8 | 628.5 | 428 | 664.9 | 497.4 | 232.1 | 309 | 338.9 | 207 | 340.6 | 25 | 52.9 | 75.8 | 68.8 | 180.4 | 170.2 | 59.4 | 128.2 | 112.6 | 85.5
709.3 | 490.3 | 288.3 | 115.32 | 134.8024 | 174.9 | 158.3 | 178 | 175.9 | 241.5 | 26.5 | 21.4 | 47.3 | 9.6 | 272.8 | 9.9 | 743.7 | 633.9 | 425.7 | 662.7 | 497.4 | 232.3 | 307.7 | 337.7 | 207 | 340.4 | 25 | 53 | 76 | 68.9 | 180.5 | 169.9 | 59.5 | 128.3 | 112.7 | 85.6
710.3 | 491.3 | 287.8 | 115.12 | 134.5686 | 174.7 | 158.8 | 177.9 | 175.5 | 238 | 26.5 | 21.4 | 47.4 | 9.8 | 253.4 | 10 | 742.8 | 629.7 | 425.9 | 660.8 | 497.1 | 232.5 | 306.1 | 337 | 206.8 | 339.7 | 25.1 | 53.1 | 76.1 | 69 | 182.4 | 170 | 59.5 | 128.5 | 112.8 | 85.8
711.3 | 492.3 | 287.9 | 115.16 | 134.6154 | 174.6 | 159.2 | 177 | 175.5 | 235.7 | 26.5 | 21.4 | 47.5 | 10.4 | 258.2 | 11 | 742.3 | 636.9 | 443.4 | 659.2 | 498 | 232.7 | 306.9 | 342.4 | 206.9 | 339.5 | 25.1 | 53.1 | 76.4 | 69.1 | 183.2 | 170.1 | 59.7 | 128.6 | 112.9 | 86
712.3 | 493.3 | 287.6 | 115.04 | 134.4751 | 174.2 | 159.2 | 177 | 175.8 | 236.6 | 26.6 | 21.4 | 47.5 | 9.7 | 259.7 | 10.9 | 741.2 | 633.6 | 440.8 | 657.7 | 497.7 | 232.8 | 306 | 338.4 | 207.1 | 338.7 | 25.2 | 53.2 | 76.5 | 69.2 | 183.7 | 170.3 | 59.8 | 128.7 | 113 | 86.2
713.3 | 494.3 | 288.7 | 115.48 | 134.9895 | 175.1 | 159 | 177.4 | 176.1 | 234.9 | 26.6 | 21.4 | 47.6 | 9.3 | 270.8 | 10.8 | 739.4 | 633.5 | 444.8 | 654.9 | 497.1 | 233 | 304 | 336.2 | 206.8 | 337.8 | 25.2 | 53.3 | 76.6 | 69.3 | 183.9 | 170.3 | 59.9 | 128.7 | 113.1 | 86.4
714.3 | 495.3 | 289.5 | 115.8 | 135.3635 | 174.4 | 159.3 | 177.2 | 176.4 | 233.1 | 26.6 | 21.4 | 47.6 | 9.1 | 281.1 | 11.4 | 737.5 | 627.8 | 438 | 651.8 | 497 | 233.2 | 302.2 | 333.8 | 206.8 | 337 | 25.3 | 53.4 | 76.7 | 69.3 | 184.2 | 170.7 | 60 | 128.9 | 113.3 | 86.5
715.3 | 496.3 | 288.3 | 115.32 | 134.8024 | 175 | 159.1 | 177.1 | 177.3 | 232.1 | 26.7 | 21.4 | 47.7 | 8.5 | 283.8 | 11.1 | 735.2 | 626 | 441.1 | 647.6 | 497.8 | 233.4 | 300.8 | 333.3 | 206.7 | 336.2 | 25.3 | 53.5 | 76.8 | 69.4 | 184 | 170.9 | 60.1 | 129.1 | 113.4 | 86.6
716.3 | 497.3 | 288.5 | 115.4 | 134.896 | 174.8 | 158.1 | 177 | 178.2 | 230.9 | 26.7 | 21.4 | 47.8 | 8.4 | 282.1 | 10.6 | 733.2 | 627.2 | 456.5 | 645.1 | 499.3 | 233.5 | 299.7 | 333.8 | 206.6 | 336.2 | 25.4 | 53.7 | 77 | 69.5 | 184.2 | 170.9 | 60.2 | 129.2 | 113.5 | 86.7
717.3 | 498.3 | 289 | 115.6 | 135.1297 | 174.4 | 156.8 | 176.2 | 178.6 | 231.3 | 26.8 | 21.4 | 47.7 | 7.7 | 278.7 | 9.9 | 731.2 | 623.1 | 450 | 640.8 | 499 | 233.7 | 298.1 | 329.7 | 206.7 | 335.9 | 25.4 | 53.8 | 77 | 69.6 | 184.1 | 171 | 60.3 | 129.4 | 113.6 | 86.9
718.3 | 499.3 | 289.5 | 115.8 | 135.3635 | 174.9 | 156.2 | 175 | 178 | 228.8 | 26.8 | 21.4 | 47.7 | 7.3 | 266.1 | 9.3 | 729.5 | 614.2 | 448.7 | 638.7 | 499.3 | 233.8 | 295.7 | 324.9 | 206.5 | 335.2 | 25.5 | 53.9 | 77.1 | 69.7 | 183.7 | 171.3 | 60.4 | 129.5 | 113.7 | 87
719.3 | 500.3 | 289.1 | 115.64 | 135.1765 | 173.7 | 156.2 | 174.1 | 177.7 | 227.9 | 26.7 | 21.4 | 47.8 | 7.5 | 273.1 | 9.2 | 727.3 | 595.8 | 438.7 | 636.1 | 498.5 | 234 | 293 | 320.6 | 206.2 | 334.1 | 25.5 | 54 | 77 | 69.8 | 183.3 | 171.2 | 60.5 | 129.7 | 113.9 | 87.1
720.3 | 501.3 | 288.5 | 115.4 | 134.896 | 172.7 | 156 | 174 | 177.7 | 226.4 | 26.7 | 21.4 | 47.8 | 7.8 | 273.1 | 9.9 | 725.1 | 581.8 | 437.4 | 632.9 | 498 | 234.2 | 289.8 | 317.9 | 205.6 | 332.8 | 25.5 | 54.1 | 77.1 | 69.9 | 183.3 | 171.5 | 60.6 | 129.8 | 114 | 87.3
721.3 | 502.3 | 287.1 | 114.84 | 134.2413 | 171.6 | 155.9 | 175.1 | 176.9 | 225.4 | 26.6 | 21.4 | 47.8 | 7.8 | 269.8 | 9.9 | 724 | 578.8 | 436.4 | 632.1 | 498.5 | 234.3 | 289.6 | 316.6 | 205.5 | 332.8 | 25.6 | 54.2 | 77.3 | 70 | 182.9 | 171.4 | 60.7 | 129.9 | 114.1 | 87.4
722.3 | 503.3 | 287.3 | 114.92 | 134.3349 | 171 | 155.9 | 176.1 | 175.5 | 225.8 | 26.6 | 21.4 | 47.9 | 8.2 | 268.1 | 9.7 | 722.9 | 580.9 | 435.2 | 630.5 | 499.1 | 234.5 | 288.7 | 316.2 | 205.2 | 332 | 25.6 | 54.2 | 77.3 | 70.1 | 182.6 | 171.3 | 60.8 | 130.1 | 114.2 | 87.5
723.3 | 504.3 | 287.5 | 115 | 134.4284 | 170 | 155.5 | 176.8 | 175 | 226 | 26.6 | 21.4 | 47.9 | 7.8 | 267.1 | 9.5 | 722 | 578.3 | 436.3 | 629.6 | 499.1 | 234.7 | 287.8 | 316.5 | 205 | 331.3 | 25.7 | 54.3 | 77.5 | 70.2 | 182.3 | 171.2 | 60.9 | 130.2 | 114.3 | 87.7
724.3 | 505.3 | 287.6 | 115.04 | 134.4751 | 170.2 | 155.5 | 177.8 | 174.7 | 226.8 | 26.5 | 21.4 | 48 | 7.8 | 267.3 | 8.8 | 721.8 | 585.3 | 446.5 | 629.7 | 500.1 | 234.8 | 290.1 | 319 | 205.5 | 331.6 | 25.7 | 54.4 | 77.6 | 70.3 | 181.8 | 171.4 | 61 | 130.2 | 114.4 | 87.8
725.3 | 506.3 | 287.8 | 115.12 | 134.5686 | 170.1 | 155.9 | 177.8 | 174.4 | 228.9 | 26.4 | 21.4 | 48.1 | 7.4 | 264 | 9.7 | 721.7 | 591.3 | 465.5 | 629.7 | 502.6 | 235 | 291.8 | 322 | 206.3 | 332.3 | 25.8 | 54.5 | 77.7 | 70.4 | 181.3 | 171.5 | 61.1 | 130.2 | 114.5 | 87.9
726.3 | 507.3 | 287.9 | 115.16 | 134.6154 | 170.7 | 155.3 | 178 | 174.4 | 231.3 | 26.3 | 21.4 | 48.2 | 7.7 | 265.5 | 9.9 | 721.5 | 597.8 | 471.8 | 630.1 | 503.3 | 235.2 | 293.7 | 324.4 | 206.9 | 332.6 | 25.8 | 54.6 | 77.9 | 70.5 | 181.2 | 171.3 | 61.2 | 130.2 | 114.7 | 88
727.3 | 508.3 | 288.1 | 115.24 | 134.7089 | 171.9 | 154.8 | 178 | 174.9 | 232.3 | 26.2 | 21.4 | 48.3 | 7.6 | 269.6 | 9.3 | 722 | 602.5 | 466.9 | 632.7 | 503.1 | 235.3 | 294.7 | 326 | 207.4 | 332.5 | 25.9 | 54.7 | 78 | 70.6 | 180.8 | 171 | 61.3 | 130.4 | 114.8 | 88.1
728.3 | 509.3 | 288.1 | 115.24 | 134.7089 | 171.9 | 155 | 178.4 | 176.1 | 234.1 | 26.1 | 21.4 | 48.3 | 7.6 | 274.9 | 8.9 | 722.3 | 611.1 | 461.4 | 633.8 | 503.3 | 235.5 | 293.4 | 324.8 | 207.7 | 331.8 | 25.9 | 54.8 | 78.2 | 70.7 | 180.7 | 170.6 | 61.4 | 130.4 | 115 | 88.2
729.3 | 510.3 | 288.2 | 115.28 | 134.7557 | 170.3 | 155.8 | 178.6 | 176.5 | 237.2 | 26.1 | 21.4 | 48.3 | 7.3 | 274.8 | 8.7 | 721.8 | 605.4 | 457.5 | 631.5 | 503.2 | 235.7 | 292.4 | 322.6 | 207.8 | 331.4 | 26 | 54.9 | 78.1 | 70.8 | 180.6 | 170.5 | 61.5 | 130.6 | 115.1 | 88.3
730.3 | 511.3 | 288.4 | 115.36 | 134.8492 | 169.5 | 155.9 | 178.7 | 176.6 | 238.9 | 26.1 | 21.4 | 48.3 | 7.5 | 268.2 | 8.2 | 721.4 | 610.3 | 477.3 | 632.1 | 505.1 | 235.9 | 292.9 | 326.3 | 208.1 | 331.3 | 26 | 55 | 78.2 | 70.8 | 180.7 | 170.1 | 61.7 | 130.8 | 115.2 | 88.4
731.3 | 512.3 | 288.3 | 115.32 | 134.8024 | 168.8 | 155.5 | 178.2 | 176.4 | 240.2 | 26.1 | 21.4 | 48.2 | 7.3 | 263.4 | 7.9 | 721.2 | 613.7 | 493 | 631.5 | 507.3 | 236 | 297.3 | 329.5 | 209.2 | 332.4 | 26.1 | 55.1 | 78.5 | 70.9 | 180.6 | 170 | 61.7 | 131 | 115.4 | 88.6
732.3 | 513.3 | 288.7 | 115.48 | 134.9895 | 168.5 | 155.5 | 178 | 176.8 | 239.1 | 26 | 21.4 | 48.1 | 6.9 | 261.9 | 7 | 720.7 | 613.2 | 513.2 | 631.7 | 510.7 | 236.2 | 299.6 | 329.6 | 210.5 | 334.8 | 26.1 | 55.2 | 78.8 | 71 | 180.8 | 169.8 | 61.8 | 131.1 | 115.6 | 88.7
733.3 | 514.3 | 288.4 | 115.36 | 134.8492 | 168.2 | 155.9 | 178.1 | 177.6 | 237.1 | 26 | 21.4 | 48.2 | 6.3 | 259.2 | 6.7 | 720.8 | 620.1 | 534 | 635.2 | 512.1 | 236.4 | 303.9 | 333.1 | 212.4 | 337 | 26.2 | 55.3 | 78.9 | 71.1 | 181.1 | 169.7 | 61.9 | 131.2 | 115.8 | 88.8
734.3 | 515.3 | 288.4 | 115.36 | 134.8492 | 168 | 155.7 | 178.6 | 178 | 238.5 | 26 | 21.4 | 48.2 | 6.7 | 257.3 | 6.7 | 721.7 | 624.4 | 543.8 | 636.4 | 512.2 | 236.5 | 307.3 | 333.6 | 214 | 337.8 | 26.2 | 55.4 | 78.8 | 71.2 | 181.3 | 169.6 | 62 | 131.4 | 116 | 88.9
735.3 | 516.3 | 288.6 | 115.44 | 134.9427 | 168.4 | 156 | 179.2 | 178.2 | 237.3 | 26 | 21.4 | 48.1 | 7.2 | 256.9 | 6.8 | 722.6 | 628.2 | 552.1 | 638.3 | 513.5 | 236.7 | 309.5 | 336.6 | 215.1 | 338 | 26.3 | 55.5 | 78.9 | 71.3 | 181.9 | 169.4 | 62.2 | 131.5 | 116.3 | 89.1
736.3 | 517.3 | 288.3 | 115.32 | 134.8024 | 169.5 | 156.3 | 180 | 178.7 | 240.4 | 25.9 | 21.3 | 48 | 7.6 | 264.9 | 6.7 | 724.3 | 635.7 | 563.7 | 644.4 | 514.5 | 236.9 | 312.9 | 338.6 | 215.9 | 339.3 | 26.3 | 55.5 | 78.8 | 71.4 | 182.3 | 169.2 | 62.3 | 131.6 | 116.5 | 89.3
737.3 | 518.3 | 288.4 | 115.36 | 134.8492 | 169.7 | 156.7 | 180.7 | 178.7 | 240.7 | 25.9 | 21.4 | 48 | 7.2 | 264.6 | 6.8 | 726.1 | 642.8 | 564.3 | 645.4 | 517.1 | 237.1 | 315.9 | 345.5 | 216.9 | 340 | 26.4 | 55.6 | 78.9 | 71.5 | 182.1 | 169.3 | 62.4 | 131.8 | 116.7 | 89.4
738.3 | 519.3 | 288.4 | 115.36 | 134.8492 | 170 | 157.1 | 180.8 | 178.6 | 241.4 | 26 | 21.4 | 47.9 | 7.6 | 259.1 | 6.7 | 727 | 645.5 | 553.2 | 644.4 | 515.7 | 237.3 | 316.7 | 350 | 217.6 | 339.7 | 26.4 | 55.7 | 79.1 | 71.5 | 181.7 | 169.2 | 62.4 | 131.7 | 116.8 | 89.6
739.3 | 520.3 | 289.7 | 115.88 | 135.457 | 170 | 157.1 | 180.6 | 179.2 | 241.8 | 26 | 21.4 | 47.8 | 7.8 | 256.6 | 6.4 | 726.4 | 640.7 | 536.6 | 643.6 | 514.9 | 237.5 | 314.9 | 346.6 | 217.6 | 338.4 | 26.5 | 55.8 | 79.1 | 71.6 | 181.7 | 169 | 62.6 | 131.9 | 117 | 89.7
740.3 | 521.3 | 289.5 | 115.8 | 135.3635 | 169.8 | 156.7 | 180.7 | 179.4 | 240.9 | 26.1 | 21.4 | 47.6 | 7.5 | 253.1 | 6 | 726 | 632.9 | 535.6 | 642.8 | 516.3 | 237.7 | 314.3 | 345.4 | 217.5 | 338.1 | 26.5 | 55.9 | 79.3 | 71.7 | 182.4 | 169.2 | 62.7 | 132 | 117.1 | 89.8
741.3 | 522.3 | 289.2 | 115.68 | 135.2233 | 169.1 | 157.2 | 180.6 | 179 | 242.2 | 26.2 | 21.4 | 47.6 | 7.3 | 235.7 | 6 | 725.8 | 633.1 | 535.7 | 643.5 | 519.1 | 237.9 | 314.9 | 347.9 | 217.9 | 338.8 | 26.6 | 56 | 79.4 | 71.8 | 183.1 | 169.3 | 62.8 | 132.1 | 117.2 | 90
742.3 | 523.3 | 289 | 115.6 | 135.1297 | 168.4 | 158 | 180.3 | 179 | 244.7 | 26.2 | 21.4 | 47.6 | 6.9 | 254.3 | 5.6 | 725 | 628.9 | 529.8 | 641.4 | 520 | 238.1 | 313.8 | 342.8 | 218.3 | 338.6 | 26.6 | 56.1 | 79.6 | 71.9 | 183.1 | 169.4 | 62.9 | 132.3 | 117.4 | 90.1
743.3 | 524.3 | 289.5 | 115.8 | 135.3635 | 167.6 | 159.3 | 180 | 178.8 | 243.2 | 26.2 | 21.3 | 47.6 | 6.8 | 245.8 | 6 | 723.7 | 629.6 | 519 | 640.5 | 520.5 | 238.3 | 312.8 | 339.7 | 218.7 | 338.6 | 26.7 | 56.2 | 79.8 | 71.9 | 183 | 169.6 | 62.9 | 132.4 | 117.6 | 90.3
744.3 | 525.3 | 287.3 | 114.92 | 134.3349 | 167.4 | 159.4 | 179.8 | 178.2 | 241.1 | 26.2 | 21.3 | 47.8 | 7.4 | 241.8 | 6.8 | 722.5 | 628.2 | 514.4 | 639.2 | 520.3 | 238.5 | 312.4 | 339.6 | 218.8 | 338.1 | 26.7 | 56.3 | 79.9 | 72 | 182.9 | 169.3 | 63.1 | 132.6 | 117.7 | 90.4
745.3 | 526.3 | 287.2 | 114.88 | 134.2881 | 167.6 | 159.5 | 180.3 | 178 | 244.1 | 26.1 | 21.3 | 47.9 | 7.9 | 243.3 | 7.7 | 723.3 | 638 | 515.8 | 644 | 522.2 | 238.7 | 315.2 | 347.1 | 220 | 338.6 | 26.8 | 56.4 | 80 | 72.1 | 182.9 | 169.1 | 63.2 | 132.7 | 117.9 | 90.5
746.3 | 527.3 | 287.1 | 114.84 | 134.2413 | 168.4 | 160.2 | 180.6 | 177.3 | 249 | 26.1 | 21.3 | 48 | 8.2 | 262 | 8.6 | 726.9 | 658.8 | 531.1 | 653.7 | 526.4 | 238.9 | 323.2 | 371.6 | 222.3 | 341.7 | 26.8 | 56.5 | 80.1 | 72.2 | 182.8 | 169.1 | 63.3 | 132.8 | 118.1 | 90.6
747.3 | 528.3 | 287.3 | 114.92 | 134.3349 | 168.8 | 161.1 | 180.2 | 177.2 | 254.2 | 26.1 | 21.3 | 48.1 | 8.1 | 246.3 | 8.6 | 730.6 | 665.6 | 546.5 | 655.9 | 527.8 | 239.1 | 330.7 | 385.8 | 225.4 | 342.9 | 26.9 | 56.6 | 80.2 | 72.2 | 182.6 | 168.8 | 63.4 | 132.9 | 118.3 | 90.8
748.3 | 529.3 | 287.8 | 115.12 | 134.5686 | 169.5 | 161.8 | 180.4 | 177.2 | 255.6 | 26 | 21.3 | 48.3 | 7.4 | 254.1 | 7.7 | 732.3 | 667.3 | 552.4 | 655.5 | 528.9 | 239.3 | 330.5 | 388.1 | 226.1 | 343.2 | 26.9 | 56.7 | 80.3 | 72.3 | 182.6 | 168.6 | 63.5 | 133 | 118.5 | 90.9
749.3 | 530.3 | 287.8 | 115.12 | 134.5686 | 170.5 | 162.6 | 181.4 | 178 | 256.2 | 26 | 21.3 | 48.4 | 8.6 | 262.2 | 6.4 | 733.3 | 674.7 | 566.7 | 658.7 | 530.3 | 239.5 | 337.1 | 395.4 | 228.6 | 346.7 | 27 | 56.8 | 80.4 | 72.4 | 182.7 | 168.6 | 63.6 | 133.1 | 118.7 | 91
750.3 | 531.3 | 287.8 | 115.12 | 134.5686 | 169.5 | 162 | 181.7 | 179.5 | 254.5 | 26.1 | 21.3 | 48.5 | 8.6 | 257.8 | 5.9 | 734.3 | 674.2 | 575.1 | 662 | 530.9 | 239.7 | 342.4 | 395.2 | 230.4 | 348.2 | 27 | 56.9 | 80.6 | 72.5 | 182.9 | 168.6 | 63.7 | 133.3 | 118.9 | 91.2
751.3 | 532.3 | 288.2 | 115.28 | 134.7557 | 168.5 | 161.4 | 181.7 | 180.8 | 255.4 | 26.1 | 21.3 | 48.6 | 8 | 242.8 | 6.2 | 734.5 | 669.7 | 574.2 | 662.1 | 533.4 | 239.9 | 344.3 | 387.2 | 231.9 | 348.9 | 27.1 | 57 | 80.6 | 72.5 | 183.3 | 168.9 | 63.8 | 133.4 | 119.1 | 91.3
752.3 | 533.3 | 287.9 | 115.16 | 134.6154 | 168.1 | 161.4 | 182.2 | 181.4 | 252.9 | 26.1 | 21.3 | 48.6 | 8 | 254.9 | 6.3 | 734.8 | 671.8 | 598 | 667.1 | 538.2 | 240.2 | 345.4 | 387.5 | 232.9 | 351.7 | 27.1 | 57 | 80.8 | 72.6 | 183.4 | 169.1 | 63.9 | 133.6 | 119.4 | 91.4
753.3 | 534.3 | 288.1 | 115.24 | 134.7089 | 169.4 | 162.3 | 182.1 | 181.4 | 253 | 26.1 | 21.3 | 48.6 | 7.8 | 251.2 | 6.9 | 736.2 | 675.5 | 600.8 | 670.8 | 541.1 | 240.4 | 350.9 | 388.8 | 234.8 | 353.8 | 27.2 | 57.1 | 81 | 72.7 | 183.4 | 169.9 | 64 | 133.8 | 119.6 | 91.6
754.3 | 535.3 | 287.8 | 115.12 | 134.5686 | 168.7 | 162.9 | 182.4 | 181.4 | 255.6 | 26.2 | 21.3 | 48.6 | 8 | 257 | 7.5 | 736.1 | 670.4 | 590.5 | 667.8 | 539.8 | 240.6 | 351 | 381.1 | 235.4 | 353.4 | 27.2 | 57.2 | 80.9 | 72.8 | 183.4 | 170 | 64.1 | 134 | 119.9 | 91.7
755.3 | 536.3 | 288.5 | 115.4 | 134.896 | 168.1 | 163.8 | 182.9 | 181.8 | 252.6 | 26.2 | 21.3 | 48.5 | 7.3 | 261.7 | 8 | 735.4 | 673.6 | 596.8 | 669.2 | 542.4 | 240.9 | 351.4 | 378.7 | 235.8 | 353.9 | 27.3 | 57.3 | 81 | 72.8 | 183.6 | 170.2 | 64.2 | 134.2 | 120.1 | 91.8
756.3 | 537.3 | 287.9 | 115.16 | 134.6154 | 168.2 | 163.7 | 184 | 182.1 | 252 | 26.3 | 21.3 | 48.5 | 7.3 | 266.4 | 7.7 | 736.1 | 686.2 | 606 | 671.2 | 544.1 | 241.1 | 355.6 | 382.9 | 237.4 | 355.6 | 27.3 | 57.4 | 81.2 | 72.9 | 183.2 | 170.8 | 64.3 | 134.3 | 120.3 | 92
757.3 | 538.3 | 287.6 | 115.04 | 134.4751 | 168.7 | 164.2 | 184.6 | 182.2 | 255 | 26.4 | 21.3 | 48.4 | 7.6 | 258.7 | 7.6 | 737.3 | 688.8 | 617 | 674.9 | 545.8 | 241.4 | 358 | 395.1 | 239.2 | 357.4 | 27.4 | 57.5 | 81.3 | 73 | 183.3 | 170.9 | 64.4 | 134.4 | 120.5 | 92.1
758.3 | 539.3 | 288.1 | 115.24 | 134.7089 | 170 | 164.9 | 184.6 | 182.2 | 258.6 | 26.5 | 21.3 | 48.4 | 7 | 268.6 | 7.7 | 739.3 | 699.7 | 621.6 | 678.1 | 546.2 | 241.6 | 363.3 | 403.1 | 241.6 | 359.3 | 27.4 | 57.6 | 81.6 | 73.1 | 183.4 | 171 | 64.5 | 134.6 | 120.8 | 92.3
759.3 | 540.3 | 287.8 | 115.12 | 134.5686 | 170.4 | 165 | 184.9 | 182.7 | 261.3 | 26.5 | 21.3 | 48.4 | 7.3 | 268.8 | 7.4 | 741.1 | 698.3 | 606.8 | 678.9 | 545.8 | 241.9 | 362.4 | 401.3 | 242.5 | 358.8 | 27.5 | 57.7 | 81.5 | 73.2 | 183.6 | 171.5 | 64.6 | 134.7 | 121.1 | 92.4
760.3 | 541.3 | 288 | 115.2 | 134.6622 | 170.9 | 165.4 | 184.8 | 183.4 | 260 | 26.5 | 21.3 | 48.4 | 6.8 | 271.8 | 7.3 | 741.6 | 690.5 | 587.4 | 677 | 544.8 | 242.1 | 360.4 | 395.9 | 242.6 | 358 | 27.5 | 57.8 | 81.7 | 73.3 | 183.6 | 171.7 | 64.7 | 134.9 | 121.3 | 92.6
761.3 | 542.3 | 287.9 | 115.16 | 134.6154 | 171 | 165.7 | 184.3 | 183.3 | 258.7 | 26.5 | 21.3 | 48.4 | 7.4 | 269.5 | 7.4 | 739.9 | 674.7 | 565.4 | 673.6 | 543.6 | 242.4 | 354.6 | 387.2 | 241.5 | 356.5 | 27.6 | 57.9 | 81.7 | 73.4 | 184.2 | 171.6 | 64.8 | 135.1 | 121.5 | 92.7
762.3 | 543.3 | 288.3 | 115.32 | 134.8024 | 171.3 | 165.9 | 183.9 | 182.7 | 255.6 | 26.5 | 21.3 | 48.4 | 7.9 | 253.3 | 6.9 | 737 | 651.3 | 545.5 | 669.5 | 542.4 | 242.6 | 348.3 | 378.5 | 240.2 | 355.1 | 27.6 | 58 | 81.8 | 73.5 | 184.1 | 171.8 | 64.9 | 135.3 | 121.6 | 92.9
763.3 | 544.3 | 288.4 | 115.36 | 134.8492 | 171.5 | 166.1 | 183.7 | 182.1 | 253.1 | 26.5 | 21.3 | 48.4 | 7.6 | 249.1 | 6.4 | 734.5 | 647.9 | 532.3 | 665.8 | 541.9 | 242.9 | 345.1 | 377.7 | 239.4 | 354.7 | 27.7 | 58.1 | 81.9 | 73.5 | 183.7 | 172.3 | 65 | 135.5 | 121.7 | 93
764.3 | 545.3 | 287.4 | 114.96 | 134.3816 | 172.4 | 165 | 183.4 | 181.5 | 250.7 | 26.4 | 21.3 | 48.4 | 7.3 | 248.4 | 5.9 | 731.9 | 642 | 522.9 | 661.4 | 541.3 | 243.2 | 343 | 375.8 | 239 | 354 | 27.7 | 58.2 | 82.2 | 73.6 | 183.7 | 172.5 | 65.1 | 135.7 | 121.8 | 93.2
765.3 | 546.3 | 288.4 | 115.36 | 134.8492 | 172.4 | 164.7 | 183.7 | 180.4 | 250.7 | 26.5 | 21.3 | 48.5 | 7.5 | 233.8 | 5.6 | 729.4 | 645.4 | 516.2 | 657.6 | 541.4 | 243.4 | 340 | 369.9 | 238.5 | 354.1 | 27.8 | 58.3 | 82.2 | 73.7 | 183.3 | 172.6 | 65.2 | 135.8 | 121.9 | 93.3
766.3 | 547.3 | 290.4 | 116.16 | 135.7843 | 172.3 | 164.4 | 183.4 | 179.5 | 250.3 | 26.5 | 21.3 | 48.6 | 7.4 | 230.3 | 5.9 | 726.8 | 638.5 | 508.9 | 654.1 | 540.2 | 243.7 | 336.8 | 363.8 | 237.9 | 353.3 | 27.8 | 58.4 | 82.4 | 73.8 | 183.7 | 172.7 | 65.3 | 136 | 122.1 | 93.5
767.3 | 548.3 | 289.5 | 115.8 | 135.3635 | 171.7 | 163.7 | 182 | 178.8 | 248.2 | 26.5 | 21.3 | 48.7 | 6.4 | 247.7 | 6.2 | 725.1 | 637 | 512.5 | 652.8 | 540.4 | 243.9 | 333.2 | 360.7 | 237.3 | 352.5 | 27.9 | 58.5 | 82.5 | 73.9 | 183.8 | 172.4 | 65.4 | 136 | 122.2 | 93.6
768.3 | 549.3 | 288.1 | 115.24 | 134.7089 | 171.8 | 163.6 | 182.3 | 179.2 | 245.6 | 26.4 | 21.3 | 48.8 | 6.5 | 229.5 | 5.9 | 723.3 | 630.7 | 507 | 649.5 | 540.5 | 244.1 | 330.3 | 357.2 | 237 | 351.9 | 27.9 | 58.6 | 82.5 | 74 | 183.8 | 172.3 | 65.5 | 136.1 | 122.4 | 93.7
769.3 | 550.3 | 288.6 | 115.44 | 134.9427 | 172.1 | 163.7 | 182.9 | 179.7 | 243.8 | 26.4 | 21.3 | 48.9 | 7.1 | 213.4 | 5.5 | 720.6 | 625.1 | 494 | 645 | 539.2 | 244.3 | 327 | 350.1 | 236.6 | 351 | 28 | 58.7 | 82.6 | 74.1 | 183.3 | 172.4 | 65.6 | 136.4 | 122.5 | 93.9
770.3 | 551.3 | 288.1 | 115.24 | 134.7089 | 172.8 | 162.4 | 183 | 179.8 | 241.8 | 26.4 | 21.3 | 48.9 | 7.9 | 251.2 | 4.9 | 717 | 618.8 | 483.3 | 641.3 | 539.2 | 244.5 | 322.6 | 344.4 | 235.5 | 349.7 | 28 | 58.8 | 82.6 | 74.2 | 183.4 | 172.6 | 65.7 | 136.5 | 122.7 | 94
771.3 | 552.3 | 287 | 114.8 | 134.1946 | 172.6 | 161.9 | 182.5 | 179.7 | 240 | 26.3 | 21.3 | 48.9 | 7.4 | 235.4 | 4.9 | 714 | 614.6 | 482.7 | 637.5 | 539.7 | 244.7 | 319.8 | 342.3 | 234.6 | 349 | 28.1 | 58.9 | 82.7 | 74.3 | 183.2 | 172.6 | 65.8 | 136.7 | 122.8 | 94.1
772.3 | 553.3 | 288.6 | 115.44 | 134.9427 | 172.1 | 162.4 | 182.6 | 179.5 | 240.2 | 26.3 | 21.3 | 49 | 6.8 | 228 | 5.3 | 712.3 | 608.3 | 478.6 | 635.7 | 538.8 | 244.8 | 317.8 | 340.9 | 234.2 | 348.5 | 28.1 | 59 | 82.8 | 74.3 | 182.8 | 172.4 | 65.9 | 136.7 | 122.9 | 94.2
773.3 | 554.3 | 289.8 | 115.92 | 135.5038 | 172.5 | 162.5 | 183.3 | 179.4 | 240.2 | 26.4 | 21.3 | 49.1 | 6.9 | 198 | 5.1 | 711.4 | 610.7 | 489.7 | 634.9 | 539.4 | 245 | 317.6 | 341.1 | 234.4 | 348.4 | 28.2 | 59.1 | 83 | 74.5 | 182.6 | 172.2 | 66 | 136.9 | 123.1 | 94.4
774.3 | 555.3 | 289.7 | 115.88 | 135.457 | 174.1 | 161.6 | 183.4 | 179.5 | 242 | 26.4 | 21.3 | 49.2 | 7.2 | 181.3 | 5.1 | 711.8 | 614.3 | 505 | 637.3 | 540.7 | 245.2 | 321.8 | 343 | 235.7 | 349.4 | 28.2 | 59.2 | 83 | 74.6 | 182.6 | 172.4 | 66.1 | 136.8 | 123.2 | 94.5
775.3 | 556.3 | 289.3 | 115.72 | 135.27 | 175.2 | 161.1 | 183 | 180.1 | 243.1 | 26.4 | 21.3 | 49.3 | 6.6 | 211.3 | 4.9 | 712.4 | 617 | 515.3 | 637.4 | 542.6 | 245.4 | 323.3 | 342.7 | 236.9 | 349.7 | 28.3 | 59.3 | 83.1 | 74.6 | 182.7 | 172.9 | 66.2 | 137 | 123.3 | 94.6
776.3 | 557.3 | 289.6 | 115.84 | 135.4103 | 175.1 | 161.4 | 182.3 | 181 | 241.4 | 26.4 | 21.3 | 49.4 | 6 | 205.7 | 5.5 | 711.6 | 613.4 | 507.2 | 633.9 | 541.2 | 245.5 | 321.8 | 339.3 | 236.5 | 349.1 | 28.3 | 59.3 | 83.3 | 74.7 | 182.7 | 173.2 | 66.3 | 137 | 123.5 | 94.7
777.3 | 558.3 | 290.6 | 116.24 | 135.8779 | 175.4 | 161.4 | 181.3 | 181.1 | 239.3 | 26.4 | 21.3 | 49.4 | 7 | 219.2 | 6.6 | 709.9 | 611.5 | 495.5 | 631.2 | 539.4 | 245.7 | 319.2 | 335 | 236.1 | 348.4 | 28.4 | 59.4 | 83.4 | 74.8 | 182.8 | 173.2 | 66.4 | 137.1 | 123.7 | 94.8
778.3 | 559.3 | 288.5 | 115.4 | 134.896 | 175.6 | 161.7 | 180.7 | 181.2 | 237.9 | 26.5 | 21.3 | 49.4 | 8.2 | 225.9 | 6.4 | 708.1 | 609.1 | 502 | 630.1 | 540.6 | 245.8 | 317.9 | 331.7 | 235.7 | 347.8 | 28.4 | 59.5 | 83.5 | 74.9 | 182.9 | 173.2 | 66.5 | 137.3 | 123.9 | 94.9
779.3 | 560.3 | 288.7 | 115.48 | 134.9895 | 176 | 161.5 | 180.4 | 180.8 | 237.2 | 26.5 | 21.3 | 49.2 | 7.5 | 248.7 | 5.7 | 707.1 | 613.2 | 506.8 | 630.6 | 541.5 | 246 | 319.7 | 335.1 | 237 | 348.6 | 28.5 | 59.6 | 83.6 | 75 | 182.8 | 173 | 66.6 | 137.5 | 124 | 95.1
780.3 | 561.3 | 288.6 | 115.44 | 134.9427 | 176.9 | 161.2 | 180.3 | 180.6 | 238.6 | 26.5 | 21.3 | 49.1 | 7.9 | 230.7 | 5.9 | 705.3 | 609.8 | 499.7 | 629.1 | 539.7 | 246.1 | 317.6 | 333 | 236.8 | 347.7 | 28.5 | 59.7 | 83.8 | 75.2 | 182.6 | 172.9 | 66.7 | 137.5 | 124.1 | 95.2
781.3 | 562.3 | 288.6 | 115.44 | 134.9427 | 177.4 | 161.5 | 180.3 | 180.4 | 236.2 | 26.6 | 21.3 | 49 | 8 | 213.1 | 5.8 | 703.2 | 608 | 499.7 | 628 | 539.1 | 246.3 | 316.4 | 331.3 | 236.6 | 347.2 | 28.6 | 59.8 | 83.9 | 75.3 | 182.2 | 172.8 | 66.8 | 137.6 | 124.3 | 95.3
782.3 | 563.3 | 289 | 115.6 | 135.1297 | 176.7 | 161.9 | 180.2 | 179.8 | 235.4 | 26.6 | 21.3 | 49 | 7.9 | 245.7 | 5.2 | 701.6 | 608.5 | 503 | 626.3 | 538.6 | 246.5 | 315.5 | 329.8 | 236.8 | 346.7 | 28.6 | 59.9 | 83.9 | 75.4 | 182.3 | 173 | 66.9 | 137.7 | 124.4 | 95.4
783.3 | 564.3 | 288.6 | 115.44 | 134.9427 | 175.6 | 162.5 | 180.3 | 178.8 | 236.1 | 26.6 | 21.3 | 48.9 | 7.9 | 230.3 | 4.8 | 701.6 | 612.4 | 514.7 | 627.7 | 540.5 | 246.7 | 316.8 | 338 | 237.8 | 347.1 | 28.7 | 60 | 84 | 75.5 | 182.2 | 173 | 67 | 137.8 | 124.6 | 95.5
784.3 | 565.3 | 287.2 | 114.88 | 134.2881 | 175.1 | 163.3 | 180.2 | 178.8 | 238.7 | 26.6 | 21.3 | 49 | 8.3 | 220.8 | 5 | 701.5 | 610.2 | 525.1 | 626.8 | 540.9 | 246.9 | 316.3 | 336.6 | 237.9 | 346.8 | 28.7 | 60.1 | 84.2 | 75.6 | 181.9 | 172.8 | 67.1 | 137.9 | 124.8 | 95.7
785.3 | 566.3 | 293.8 | 117.52 | 137.3741 | 175 | 163.8 | 181.1 | 179 | 239.2 | 26.6 | 21.3 | 49.1 | 8.5 | 253.2 | 4.7 | 702.2 | 611.9 | 536.7 | 630.4 | 542.5 | 247.1 | 319.6 | 340 | 238.7 | 347.6 | 28.8 | 60.2 | 84.3 | 75.7 | 181.6 | 172.8 | 67.1 | 138 | 124.9 | 95.8
786.3 | 567.3 | 293.5 | 117.4 | 137.2338 | 175.1 | 164.4 | 181.7 | 179 | 243.5 | 26.6 | 21.3 | 49.2 | 9.3 | 254.4 | 5.7 | 703.5 | 611.8 | 529.1 | 632.7 | 541.9 | 247.3 | 321.4 | 341.5 | 239.5 | 347.8 | 28.8 | 60.3 | 84.5 | 75.8 | 181.8 | 172.5 | 67.3 | 138.1 | 125.1 | 95.9
787.3 | 568.3 | 296.4 | 118.56 | 138.5898 | 175.1 | 164.9 | 181.8 | 178.4 | 242.7 | 26.7 | 21.3 | 49.3 | 10.9 | 256.1 | 6.7 | 703.3 | 612.5 | 522.2 | 632.1 | 539.9 | 247.6 | 321.3 | 337.8 | 239.9 | 347.1 | 28.9 | 60.4 | 84.6 | 75.9 | 181.9 | 172.5 | 67.3 | 138.2 | 125.2 | 96
788.3 | 569.3 | 306 | 122.4 | 143.0785 | 176.1 | 165 | 181.9 | 178.4 | 240.1 | 26.7 | 21.3 | 49.4 | 12.5 | 240.7 | 8.7 | 701.8 | 606.7 | 520.9 | 629.1 | 539.2 | 248 | 319.3 | 334.9 | 239.5 | 346.1 | 28.9 | 60.5 | 84.5 | 75.9 | 182.1 | 172.3 | 67.5 | 138.3 | 125.4 | 96.1
789.3 | 570.3 | 321 | 128.4 | 150.0922 | 176.7 | 164.2 | 181.8 | 179.1 | 238.8 | 26.8 | 21.3 | 49.4 | 10.2 | 248.4 | 13.8 | 698.9 | 597.4 | 512.5 | 626 | 537.7 | 248.3 | 316.1 | 332.6 | 238.7 | 345.2 | 29 | 60.6 | 84.6 | 76 | 182.3 | 172.1 | 67.5 | 138.5 | 125.5 | 96.2
790.3 | 571.3 | 335.7 | 134.28 | 156.9656 | 177.9 | 164 | 181.4 | 179.8 | 236.5 | 26.8 | 21.3 | 49.3 | 8.5 | 239.9 | 14 | 696.1 | 591.2 | 507 | 624.3 | 537.5 | 248.6 | 313.8 | 329.3 | 238 | 344.7 | 29 | 60.7 | 84.8 | 76.1 | 183 | 172.3 | 67.7 | 138.7 | 125.7 | 96.4
791.3 | 572.3 | 345.5 | 138.2 | 161.5478 | 177.5 | 163.7 | 180.6 | 180.4 | 236.3 | 26.9 | 21.3 | 49.2 | 8.4 | 248.6 | 13.5 | 694.4 | 589.1 | 503.1 | 623.8 | 537.5 | 248.9 | 313.4 | 327.6 | 237.9 | 344.3 | 29.1 | 60.8 | 85 | 76.2 | 183.4 | 172.7 | 67.8 | 138.9 | 125.8 | 96.5
792.3 | 573.3 | 350.9 | 140.36 | 164.0728 | 176.4 | 162.4 | 180.3 | 181.7 | 237.7 | 26.9 | 21.3 | 49.2 | 8 | 240.7 | 12.6 | 693 | 586.3 | 497.3 | 625.1 | 536.7 | 249 | 313.3 | 328 | 237.5 | 344.4 | 29.1 | 60.8 | 85.1 | 76.3 | 184.5 | 173.2 | 67.8 | 139.1 | 125.9 | 96.6
793.3 | 574.3 | 353.1 | 141.24 | 165.1014 | 176.4 | 162.1 | 180.8 | 182.4 | 238.3 | 27 | 21.3 | 49.2 | 8.7 | 238.6 | 12.3 | 691.5 | 581.2 | 499.6 | 623.1 | 536.7 | 249.2 | 311.8 | 325.9 | 237 | 344 | 29.2 | 60.9 | 85.1 | 76.4 | 185 | 173.5 | 67.9 | 139.3 | 126.1 | 96.8
794.3 | 575.3 | 354.4 | 141.76 | 165.7093 | 176.8 | 162.9 | 181.6 | 182.1 | 239.3 | 27.2 | 21.3 | 49.3 | 9.1 | 236.9 | 11 | 690.8 | 583.3 | 503.9 | 622.2 | 536.7 | 249.4 | 312.7 | 324.7 | 237.6 | 344.8 | 29.2 | 61 | 85.2 | 76.4 | 185.7 | 173.7 | 68 | 139.4 | 126.2 | 96.9
795.3 | 576.3 | 355.5 | 142.2 | 166.2236 | 178.3 | 163.8 | 182.2 | 182.2 | 239.4 | 27.3 | 21.3 | 49.5 | 9.4 | 218.4 | 9.1 | 692.3 | 598 | 525.1 | 627.1 | 538.3 | 249.5 | 316.3 | 332.4 | 239.4 | 345.4 | 29.3 | 61.1 | 85.3 | 76.5 | 186.8 | 174.2 | 68.2 | 139.6 | 126.3 | 97.1
796.3 | 577.3 | 356.4 | 142.56 | 166.6444 | 179.4 | 164.2 | 183.2 | 183.2 | 240.2 | 27.3 | 21.3 | 49.5 | 8.2 | 215.3 | 8.7 | 696 | 612.2 | 534.1 | 632.4 | 539.1 | 249.7 | 320.5 | 347.9 | 241.7 | 347.3 | 29.3 | 61.2 | 85.5 | 76.6 | 187 | 175 | 68.2 | 139.7 | 126.5 | 97.2
797.3 | 578.3 | 356.8 | 142.72 | 166.8315 | 178.9 | 163.2 | 184.9 | 184.2 | 244.3 | 27.3 | 21.3 | 49.5 | 7 | 231.1 | 8.7 | 698.6 | 616.1 | 535.2 | 633.8 | 538.5 | 250 | 322.4 | 357 | 243.4 | 347.7 | 29.4 | 61.3 | 85.7 | 76.7 | 187.1 | 175.3 | 68.3 | 139.8 | 126.7 | 97.4
798.3 | 579.3 | 357.4 | 142.96 | 167.112 | 179.2 | 163.1 | 186.5 | 184.7 | 247.6 | 27.3 | 21.3 | 49.6 | 6.9 | 241.1 | 10 | 701.7 | 629.1 | 545.7 | 636.3 | 538.4 | 250.2 | 324.1 | 365.7 | 244.6 | 348.6 | 29.4 | 61.4 | 85.9 | 76.8 | 186.9 | 175.5 | 68.4 | 140.1 | 126.8 | 97.5
799.3 | 580.3 | 357.2 | 142.88 | 167.0185 | 179.9 | 163.7 | 187.6 | 184.3 | 250.7 | 27.3 | 21.3 | 49.7 | 8.4 | 246.6 | 11.8 | 706 | 638.6 | 566.6 | 645.8 | 540.8 | 250.4 | 330.3 | 379.5 | 248.5 | 351.6 | 29.5 | 61.5 | 86 | 76.9 | 187 | 175.8 | 68.5 | 140.1 | 127 | 97.6
800.3 | 581.3 | 357.9 | 143.16 | 167.3458 | 180.8 | 164 | 188.4 | 184.3 | 257.6 | 27.4 | 21.3 | 49.8 | 8.2 | 246.8 | 11.8 | 710.4 | 637.5 | 580.1 | 654.3 | 541 | 250.6 | 332.5 | 390.4 | 250 | 351.2 | 29.5 | 61.6 | 86.2 | 77 | 187.1 | 176.2 | 68.6 | 140.3 | 127.1 | 97.8
801.3 | 582.3 | 359.1 | 143.64 | 167.9069 | 181.3 | 164.7 | 189.2 | 185 | 265.2 | 27.4 | 21.3 | 49.8 | 8.1 | 254.8 | 11.6 | 715.3 | 640.8 | 577.8 | 660.8 | 540.4 | 250.8 | 334.5 | 397.1 | 251.2 | 351.3 | 29.6 | 61.7 | 86.4 | 77.1 | 187.6 | 176.8 | 68.7 | 140.5 | 127.3 | 97.9
802.3 | 583.3 | 360.8 | 144.32 | 168.7018 | 180.5 | 166.3 | 190.5 | 185.4 | 268 | 27.4 | 21.3 | 49.9 | 9.4 | 250.3 | 13 | 718.3 | 638.5 | 582.2 | 664 | 540.3 | 250.9 | 334.1 | 398.3 | 251.3 | 351.7 | 29.6 | 61.7 | 86.5 | 77.2 | 187.8 | 177 | 68.8 | 140.8 | 127.5 | 98
803.3 | 584.3 | 362.7 | 145.08 | 169.5902 | 180.4 | 166.9 | 191.1 | 186.4 | 268.1 | 27.5 | 21.3 | 49.9 | 10.8 | 243.7 | 12.8 | 719.1 | 631.4 | 584.9 | 664.1 | 540.4 | 251.2 | 333.7 | 398.5 | 251.4 | 351.8 | 29.7 | 61.8 | 86.6 | 77.4 | 187.9 | 177.3 | 68.9 | 140.8 | 127.6 | 98.1
804.3 | 585.3 | 362.7 | 145.08 | 169.5902 | 180.9 | 167.7 | 191.7 | 186.8 | 269.9 | 27.6 | 21.3 | 50 | 10.3 | 249.5 | 10.7 | 720.8 | 632.6 | 588.5 | 666 | 540.3 | 251.4 | 335.1 | 402.3 | 252.5 | 352.4 | 29.7 | 61.9 | 86.7 | 77.5 | 188.2 | 177.6 | 69 | 140.9 | 127.8 | 98.3
805.3 | 586.3 | 362.3 | 144.92 | 169.4031 | 181 | 167.6 | 192.1 | 186.5 | 270.8 | 27.7 | 21.3 | 50.1 | 9.5 | 237.1 | 7.1 | 722.2 | 628.4 | 595.3 | 667.1 | 541 | 251.7 | 336.3 | 400.9 | 254.3 | 353.8 | 29.8 | 62 | 86.8 | 77.6 | 188.8 | 178.5 | 69.1 | 141.1 | 128 | 98.4
806.3 | 587.3 | 363.3 | 145.32 | 169.8707 | 181.2 | 167 | 191.2 | 186.6 | 270.4 | 27.8 | 21.3 | 50.2 | 9.9 | 225.5 | 5.5 | 723.2 | 632.2 | 601.9 | 668.9 | 541.5 | 252 | 336.9 | 399.8 | 255.4 | 354.4 | 29.8 | 62.1 | 86.9 | 77.7 | 189 | 178.8 | 69.2 | 141.3 | 128.2 | 98.5
807.3 | 588.3 | 363.7 | 145.48 | 170.0577 | 183.4 | 167.5 | 191.1 | 187 | 270.7 | 27.9 | 21.3 | 50.2 | 10.2 | 221.4 | 8.1 | 723.9 | 637.3 | 602.1 | 669.5 | 541.3 | 252.2 | 338.1 | 400.3 | 256.9 | 354.5 | 29.9 | 62.2 | 87 | 77.8 | 189.2 | 179.4 | 69.3 | 141.6 | 128.4 | 98.7
808.3 | 589.3 | 365.7 | 146.28 | 170.9929 | 183.8 | 167.5 | 191 | 187.6 | 272.2 | 27.9 | 21.3 | 50.2 | 10.9 | 233.1 | 9.8 | 726.8 | 649 | 604.6 | 674.9 | 542.6 | 252.3 | 342 | 409.3 | 259.3 | 356.3 | 29.9 | 62.3 | 87.3 | 77.9 | 189.3 | 179.3 | 69.4 | 141.7 | 128.6 | 98.8
809.3 | 590.3 | 365.8 | 146.32 | 171.0396 | 184.6 | 167.6 | 190.8 | 187.4 | 273 | 27.9 | 21.3 | 50.4 | 9.7 | 221.8 | 11.4 | 730.1 | 653.2 | 601.1 | 678 | 542.3 | 252.5 | 342.8 | 408.5 | 260 | 356.5 | 30 | 62.4 | 87.5 | 78 | 189.5 | 179.4 | 69.5 | 141.8 | 128.7 | 98.9
810.3 | 591.3 | 367.3 | 146.92 | 171.741 | 186.2 | 168.5 | 190.3 | 188.2 | 272.5 | 27.9 | 21.3 | 50.5 | 10 | 221.8 | 16.1 | 731.9 | 650.5 | 596.4 | 679 | 541.8 | 252.7 | 343.7 | 407.5 | 260.5 | 356.8 | 30 | 62.5 | 87.5 | 78.1 | 189.8 | 179.5 | 69.6 | 141.9 | 128.9 | 99
811.3 | 592.3 | 367.1 | 146.84 | 171.6475 | 187.1 | 168.5 | 190.7 | 189 | 273.6 | 27.8 | 21.3 | 50.7 | 10.8 | 229.2 | 17.4 | 730.7 | 634.3 | 582.5 | 674.6 | 539.9 | 252.9 | 340.4 | 397.4 | 259.5 | 355.8 | 30.1 | 62.5 | 87.7 | 78.2 | 190.2 | 180.3 | 69.7 | 142.2 | 129.1 | 99.2
812.3 | 593.3 | 367.9 | 147.16 | 172.0216 | 188.7 | 167.3 | 191.4 | 189.6 | 270.6 | 27.8 | 21.3 | 50.9 | 9.1 | 225.5 | 13.7 | 727.4 | 621 | 567.3 | 671.2 | 538.9 | 253 | 336.3 | 389.1 | 257.7 | 354.6 | 30.1 | 62.6 | 87.8 | 78.3 | 190.7 | 180.9 | 69.8 | 142.4 | 129.2 | 99.4
813.3 | 594.3 | 368.2 | 147.28 | 172.1618 | 188.4 | 166.5 | 192.6 | 190 | 267.9 | 27.8 | 21.3 | 51 | 8.5 | 233.5 | 11 | 724.7 | 610.8 | 561.8 | 668.4 | 538.5 | 253.2 | 333.3 | 384.3 | 256.3 | 353.9 | 30.2 | 62.7 | 88 | 78.5 | 191.6 | 182.1 | 69.9 | 142.7 | 129.4 | 99.5
814.3 | 595.3 | 367.9 | 147.16 | 172.0216 | 187.6 | 165.9 | 193 | 190.5 | 268.3 | 27.9 | 21.3 | 51 | 9.1 | 224.4 | 8.5 | 724.1 | 611.7 | 575.5 | 668.9 | 540.3 | 253.4 | 333.1 | 384.7 | 256.7 | 355 | 30.2 | 62.8 | 88.1 | 78.6 | 192.3 | 182.3 | 70 | 142.9 | 129.5 | 99.7
815.3 | 596.3 | 369.5 | 147.8 | 172.7697 | 186.6 | 165 | 193 | 190.8 | 269.7 | 27.9 | 21.3 | 51.1 | 9.5 | 240.3 | 8.6 | 723.5 | 608.6 | 566.1 | 667.8 | 539.4 | 253.6 | 332.6 | 382.8 | 256.8 | 354.8 | 30.3 | 62.9 | 88.3 | 78.7 | 193 | 182.8 | 70.1 | 143.1 | 129.7 | 99.8
816.3 | 597.3 | 369.9 | 147.96 | 172.9567 | 185.8 | 163.9 | 192.8 | 191.4 | 270 | 28 | 21.3 | 51.2 | 9.8 | 230.2 | 12.7 | 723.1 | 609.8 | 560.4 | 666.8 | 539 | 253.7 | 335 | 383.7 | 257.3 | 355.4 | 30.3 | 63 | 88.4 | 78.8 | 193.5 | 183.1 | 70.2 | 143.4 | 129.8 | 100
817.3 | 598.3 | 371.4 | 148.56 | 173.6581 | 187.5 | 164 | 192.6 | 192.2 | 269.5 | 28 | 21.3 | 51.3 | 9.4 | 228.2 | 14.6 | 724.2 | 614.9 | 554.1 | 668.5 | 539 | 253.9 | 334.9 | 382.5 | 257.2 | 355.4 | 30.3 | 63.1 | 88.6 | 78.9 | 193.9 | 183.3 | 70.3 | 143.5 | 130 | 100.2
818.3 | 599.3 | 372.1 | 148.84 | 173.9854 | 188.8 | 164.6 | 192.8 | 192.6 | 269.3 | 28.1 | 21.3 | 51.5 | 9.2 | 207.1 | 13 | 725.6 | 615.6 | 548.9 | 670 | 538.9 | 254.1 | 335.1 | 386.4 | 257.3 | 355.6 | 30.4 | 63.2 | 88.7 | 79 | 194.4 | 183.7 | 70.4 | 143.6 | 130.2 | 100.3
819.3 | 600.3 | 371.1 | 148.44 | 173.5178 | 188.6 | 164.6 | 193.5 | 192.7 | 271.5 | 28.2 | 21.3 | 51.6 | 8.6 | 216.9 | 11.9 | 727.8 | 621.3 | 552.1 | 672.1 | 538.5 | 254.3 | 339.5 | 403.5 | 258.8 | 356.7 | 30.4 | 63.4 | 88.8 | 79.2 | 194.8 | 183.9 | 70.5 | 143.8 | 130.3 | 100.5
820.3 | 601.3 | 373.1 | 149.24 | 174.453 | 189.1 | 164.8 | 194 | 193.3 | 274.8 | 28.3 | 21.3 | 51.7 | 9.3 | 250.5 | 12.4 | 730.8 | 630.6 | 558.7 | 675.9 | 539.1 | 254.5 | 342.8 | 406.7 | 260.6 | 357.6 | 30.5 | 63.5 | 89 | 79.3 | 195.6 | 183.9 | 70.6 | 144 | 130.5 | 100.6
821.3 | 602.3 | 373.8 | 149.52 | 174.7803 | 190.6 | 165.5 | 194.9 | 193.9 | 276 | 28.4 | 21.3 | 51.8 | 9.9 | 250 | 14.4 | 734.1 | 639.7 | 571.7 | 680.2 | 540.3 | 254.6 | 346.9 | 415.2 | 262.5 | 358.6 | 30.5 | 63.6 | 89.2 | 79.4 | 196.2 | 183.8 | 70.7 | 144.2 | 130.6 | 100.8
822.3 | 603.3 | 373.6 | 149.44 | 174.6867 | 191.6 | 167.4 | 195.6 | 195.1 | 278.3 | 28.5 | 21.3 | 51.8 | 9 | 245 | 15.8 | 737 | 640.1 | 572.6 | 681.2 | 541.8 | 254.8 | 348.2 | 415.7 | 263.8 | 358.8 | 30.6 | 63.7 | 89.3 | 79.5 | 196.6 | 184.3 | 70.8 | 144.4 | 130.8 | 100.9
823.3 | 604.3 | 374 | 149.6 | 174.8738 | 193.3 | 169.1 | 196.7 | 196.7 | 277 | 28.6 | 21.3 | 51.9 | 9.2 | 249.6 | 16.2 | 737.7 | 635.6 | 573.6 | 679.7 | 540.4 | 255 | 345.3 | 408.1 | 263.1 | 358.1 | 30.6 | 63.8 | 89.4 | 79.7 | 196.9 | 184.5 | 71 | 144.7 | 130.9 | 101.1
824.3 | 605.3 | 375 | 150 | 175.3414 | 194.4 | 170.1 | 198 | 197.6 | 273.8 | 28.7 | 21.3 | 52 | 9.6 | 238.1 | 14.4 | 738.3 | 632.4 | 567.2 | 681.3 | 540.1 | 255.2 | 343.7 | 406 | 263.4 | 358 | 30.7 | 63.8 | 89.4 | 79.8 | 197.4 | 184.4 | 71 | 144.9 | 131.1 | 101.3
825.3 | 606.3 | 374.9 | 149.96 | 175.2946 | 195.7 | 170.2 | 198 | 197.5 | 272.9 | 28.8 | 21.3 | 52.1 | 9.9 | 247.4 | 13.9 | 738.9 | 632 | 565.5 | 681.7 | 540.5 | 255.4 | 343.1 | 409.8 | 263.2 | 358 | 30.7 | 63.9 | 89.6 | 79.9 | 198 | 184.8 | 71.1 | 145.1 | 131.3 | 101.4
826.3 | 607.3 | 375.1 | 150.04 | 175.3881 | 198.1 | 169.5 | 198.3 | 198.5 | 274.1 | 28.9 | 21.3 | 52.3 | 9 | 255.1 | 12.7 | 740.1 | 643.6 | 585.9 | 687.4 | 543.9 | 255.7 | 346.3 | 413.3 | 265.3 | 360 | 30.8 | 64 | 89.8 | 80 | 198.6 | 185.1 | 71.3 | 145.3 | 131.5 | 101.5
827.3 | 608.3 | 376.1 | 150.44 | 175.8557 | 198.7 | 169.5 | 199 | 198.9 | 278.3 | 28.9 | 21.3 | 52.4 | 7.8 | 267.2 | 11.4 | 742.7 | 654.2 | 604.7 | 692.5 | 546.6 | 256 | 351.6 | 424.7 | 268.1 | 361.5 | 30.8 | 64.1 | 90 | 80.2 | 198.7 | 186.1 | 71.3 | 145.5 | 131.7 | 101.7
828.3 | 609.3 | 376.4 | 150.56 | 175.996 | 199.1 | 170.6 | 198.9 | 198.7 | 286.6 | 29 | 21.3 | 52.5 | 8.2 | 259 | 12.5 | 746.2 | 670.4 | 628.3 | 698.7 | 548.6 | 256.3 | 356.8 | 439.1 | 271 | 363.3 | 30.9 | 64.2 | 90.1 | 80.3 | 199 | 186.6 | 71.4 | 145.8 | 131.9 | 101.8
829.3 | 610.3 | 376.7 | 150.68 | 176.1362 | 199.1 | 171.1 | 199.5 | 198.2 | 291.8 | 29 | 21.3 | 52.7 | 8.9 | 254.4 | 14.7 | 749.9 | 678.7 | 630.6 | 706.7 | 549.7 | 256.6 | 359.3 | 444.2 | 272.7 | 364.8 | 30.9 | 64.4 | 90.3 | 80.4 | 200 | 186.6 | 71.5 | 146 | 132.1 | 102
830.3 | 611.3 | 375.7 | 150.28 | 175.6687 | 197.5 | 172.2 | 201.2 | 198.5 | 292.8 | 29.1 | 21.3 | 52.8 | 8.6 | 255.4 | 15.1 | 751.8 | 676.1 | 631 | 706.1 | 549.3 | 256.9 | 361.5 | 442.2 | 274.3 | 365.4 | 31 | 64.5 | 90.5 | 80.5 | 200.1 | 186.6 | 71.6 | 146.3 | 132.3 | 102.1
831.3 | 612.3 | 377.1 | 150.84 | 176.3233 | 197.1 | 173.2 | 201.3 | 199 | 292 | 29.1 | 21.3 | 52.8 | 8.4 | 263.4 | 15.3 | 752.7 | 674.8 | 633.4 | 705.8 | 550.2 | 257.1 | 365 | 444.1 | 276.9 | 366.3 | 31 | 64.6 | 90.6 | 80.7 | 200.4 | 186.4 | 71.8 | 146.4 | 132.5 | 102.3
832.3 | 613.3 | 375.4 | 150.16 | 175.5284 | 196.9 | 172.8 | 201.7 | 199.7 | 293.6 | 29.1 | 21.3 | 52.8 | 9.1 | 272 | 12.3 | 752.3 | 669.6 | 618.4 | 702.9 | 548.9 | 257.4 | 363.3 | 442.9 | 276.4 | 365.9 | 31.1 | 64.7 | 90.8 | 80.8 | 201 | 186.9 | 71.8 | 146.5 | 132.8 | 102.4
833.3 | 614.3 | 375.3 | 150.12 | 175.4816 | 196.2 | 171.7 | 202 | 199.6 | 292.9 | 29.1 | 21.3 | 52.9 | 9.4 | 262.3 | 11.2 | 752.3 | 671.1 | 610.4 | 702.4 | 548 | 257.7 | 363.8 | 442.5 | 277 | 366.6 | 31.1 | 64.7 | 91 | 80.9 | 201.4 | 186.9 | 71.9 | 146.7 | 133 | 102.6
834.3 | 615.3 | 375.2 | 150.08 | 175.4349 | 194.7 | 171.5 | 203.5 | 200.6 | 293.1 | 29.2 | 21.3 | 52.9 | 10.1 | 253 | 10.3 | 752.4 | 669.7 | 611.1 | 702.9 | 549.8 | 257.9 | 363.5 | 436.3 | 277.7 | 367.6 | 31.2 | 64.8 | 91.1 | 81.1 | 202 | 187.2 | 72 | 147 | 132.9 | 102.7
835.3 | 616.3 | 375.5 | 150.2 | 175.5751 | 195.6 | 171.2 | 202.9 | 199.9 | 291.4 | 29.1 | 21.3 | 53 | 11 | 261.5 | 10.1 | 752.2 | 668.4 | 601.4 | 702.7 | 549.3 | 258.2 | 363.1 | 431.9 | 277.9 | 368.3 | 31.2 | 64.9 | 91.2 | 81.2 | 202.2 | 188.1 | 72.2 | 147.2 | 133.4 | 102.9
836.3 | 617.3 | 375.5 | 150.2 | 175.5751 | 195 | 171.7 | 202.3 | 199.5 | 288.8 | 29 | 21.3 | 53.1 | 10.7 | 263.4 | 11.4 | 752.9 | 674.7 | 595.1 | 706.1 | 549.3 | 258.4 | 364.9 | 435.4 | 279 | 368.9 | 31.3 | 65 | 91.4 | 81.4 | 202.1 | 188.8 | 72.3 | 147.5 | 133.6 | 103.1
837.3 | 618.3 | 373.9 | 149.56 | 174.827 | 196.2 | 171.9 | 201.8 | 199.7 | 290.6 | 29 | 21.3 | 53.1 | 10.1 | 253.8 | 11.9 | 754.4 | 677.5 | 596.7 | 710.3 | 550.2 | 258.5 | 366.6 | 439.5 | 280.2 | 370.6 | 31.3 | 65.1 | 91.6 | 81.5 | 202.6 | 189.1 | 72.4 | 147.7 | 133.8 | 103.2
838.3 | 619.3 | 376.5 | 150.6 | 176.0427 | 197.5 | 173 | 201.8 | 200.1 | 292.6 | 29 | 21.3 | 53.2 | 10.9 | 250.4 | 13 | 754.9 | 671.7 | 599.8 | 711.5 | 550.8 | 258.7 | 368.2 | 438 | 281.5 | 371.7 | 31.4 | 65.2 | 91.7 | 81.6 | 202.8 | 189.5 | 72.5 | 147.9 | 134.1 | 103.4
839.3 | 620.3 | 375.9 | 150.36 | 175.7622 | 198.3 | 173.6 | 202 | 199.8 | 292.1 | 29 | 21.3 | 53.2 | 9.3 | 238.2 | 14.3 | 754.5 | 670 | 603.1 | 710.6 | 550.8 | 258.9 | 367.5 | 438.9 | 281.8 | 372.1 | 31.4 | 65.3 | 91.8 | 81.8 | 203 | 189.5 | 72.6 | 148 | 134.3 | 103.6
840.3 | 621.3 | 375.4 | 150.16 | 175.5284 | 198.3 | 174.3 | 201.7 | 200 | 292.6 | 29.1 | 21.2 | 53.3 | 9.7 | 248.6 | 13.9 | 754.6 | 669.5 | 617.9 | 711.8 | 552.7 | 259.1 | 368.6 | 440.2 | 283.9 | 373.4 | 31.5 | 65.4 | 91.9 | 81.9 | 203 | 189.3 | 72.7 | 148.2 | 134.5 | 103.7
841.3 | 622.3 | 375.2 | 150.08 | 175.4349 | 197.8 | 174.4 | 201.8 | 200.1 | 294.7 | 29.1 | 21.2 | 53.4 | 11.1 | 244.2 | 15.9 | 757.1 | 674.5 | 627 | 716.7 | 555.2 | 259.4 | 370.7 | 447.2 | 286.1 | 375.8 | 31.5 | 65.5 | 92.1 | 82 | 203.2 | 189.4 | 72.8 | 148.3 | 134.7 | 103.9
842.3 | 623.3 | 374.7 | 149.88 | 175.2011 | 196.6 | 174.8 | 201.9 | 200.2 | 294.9 | 29.2 | 21.2 | 53.4 | 10.3 | 239.3 | 16.5 | 759.2 | 680.4 | 620.8 | 718.5 | 555.5 | 259.6 | 371.7 | 445.8 | 287.3 | 376.1 | 31.6 | 65.6 | 92.2 | 82.1 | 203.1 | 189.7 | 72.9 | 148.5 | 134.9 | 104
843.3 | 624.3 | 377.1 | 150.84 | 176.3233 | 196.5 | 174.4 | 201.4 | 200.4 | 292.8 | 29.2 | 21.2 | 53.4 | 10.2 | 248.9 | 14.3 | 759.1 | 675.8 | 602.6 | 716.2 | 554.2 | 259.8 | 367.6 | 434.2 | 285.6 | 374.8 | 31.6 | 65.7 | 92.4 | 82.3 | 203.5 | 189.7 | 73 | 148.6 | 135.1 | 104.2
844.3 | 625.3 | 377.7 | 151.08 | 176.6038 | 197 | 174 | 200.6 | 200.5 | 290.1 | 29.3 | 21.2 | 53.4 | 11.7 | 240.2 | 17.4 | 755.4 | 661.6 | 581.9 | 710.9 | 553.1 | 260 | 363.3 | 428.9 | 283.9 | 373.8 | 31.7 | 65.9 | 92.5 | 82.4 | 204.1 | 189.5 | 73.1 | 148.9 | 135.3 | 104.3
845.3 | 626.3 | 377.6 | 151.04 | 176.5571 | 197.9 | 173.6 | 200.6 | 201.1 | 287.8 | 29.3 | 21.2 | 53.5 | 12.5 | 250.9 | 18.3 | 751.3 | 649.6 | 568.8 | 704.9 | 551.7 | 260.2 | 358.5 | 419.1 | 281.8 | 372.5 | 31.7 | 66 | 92.6 | 82.5 | 203.9 | 190.1 | 73.2 | 149.1 | 135.5 | 104.5
846.3 | 627.3 | 378.7 | 151.48 | 177.0714 | 198.6 | 173.3 | 200.6 | 201 | 283.7 | 29.3 | 21.2 | 53.5 | 12 | 235.3 | 17.9 | 747.6 | 639.5 | 551.5 | 698.8 | 550.3 | 260.4 | 354.4 | 412 | 279.7 | 371.9 | 31.8 | 66.1 | 92.8 | 82.7 | 203.9 | 190.1 | 73.3 | 149.2 | 135.6 | 104.7
847.3 | 628.3 | 376.9 | 150.76 | 176.2298 | 198.6 | 173.1 | 200.6 | 200.4 | 279.1 | 29.4 | 21.2 | 53.5 | 11.1 | 243.1 | 19.8 | 745.6 | 635.7 | 543.1 | 696.9 | 550.4 | 260.6 | 351.8 | 410.9 | 278.3 | 371.7 | 31.8 | 66.2 | 92.9 | 82.8 | 203.8 | 189.9 | 73.4 | 149.4 | 135.7 | 104.8
848.3 | 629.3 | 376.1 | 150.44 | 175.8557 | 198 | 172.6 | 201.1 | 199.5 | 278.3 | 29.4 | 21.2 | 53.6 | 10.1 | 245.6 | 20.7 | 745.4 | 643.6 | 560 | 694.1 | 551.6 | 260.8 | 351.6 | 418.2 | 278.6 | 372 | 31.9 | 66.3 | 93.1 | 82.9 | 203.2 | 189.6 | 73.5 | 149.5 | 135.9 | 104.9
849.3 | 630.3 | 375.4 | 150.16 | 175.5284 | 197.1 | 172.5 | 201 | 198.3 | 281.3 | 29.5 | 21.2 | 53.6 | 9.5 | 243.1 | 21.5 | 746.4 | 657.8 | 579.7 | 695.2 | 552.5 | 261 | 355.4 | 436.3 | 280.8 | 373.6 | 32 | 66.4 | 93.3 | 83 | 202.9 | 189.5 | 73.6 | 149.7 | 136 | 105.1
850.3 | 631.3 | 376.7 | 150.68 | 176.1362 | 196.8 | 172.9 | 200.5 | 197.7 | 289.8 | 29.5 | 21.2 | 53.8 | 8.2 | 242.1 | 20.6 | 751.5 | 676 | 589 | 700.5 | 554.4 | 261.2 | 358.9 | 451.2 | 282.9 | 374.9 | 32 | 66.5 | 93.6 | 83.2 | 202.2 | 189.1 | 73.7 | 149.9 | 136.2 | 105.2
851.3 | 632.3 | 377.7 | 151.08 | 176.6038 | 197.3 | 174.1 | 200.6 | 197.7 | 293 | 29.5 | 21.2 | 54 | 9.4 | 234.8 | 18.5 | 753.4 | 680.6 | 599.6 | 701.9 | 555.6 | 261.5 | 360.9 | 456 | 284.9 | 375.9 | 32.1 | 66.6 | 93.7 | 83.3 | 201.6 | 188.8 | 73.8 | 150 | 136.4 | 105.3
852.3 | 633.3 | 377.8 | 151.12 | 176.6506 | 197.2 | 176.2 | 200.5 | 198 | 293.1 | 29.6 | 21.2 | 54.2 | 9.6 | 234.9 | 18.2 | 756.4 | 690.3 | 612 | 708.4 | 556.7 | 261.7 | 365.4 | 465.6 | 288.4 | 377.9 | 32.1 | 66.7 | 93.7 | 83.4 | 201.4 | 188.7 | 73.9 | 150.1 | 136.6 | 105.4
853.3 | 634.3 | 378.6 | 151.44 | 177.0246 | 196.5 | 177.7 | 200.4 | 198.4 | 294.6 | 29.6 | 21.2 | 54.4 | 10.1 | 246.8 | 16.7 | 759.2 | 703.3 | 622.9 | 713 | 557.3 | 261.9 | 369.7 | 475.8 | 291.9 | 379.7 | 32.2 | 66.9 | 93.9 | 83.5 | 201.7 | 188.6 | 74 | 150.2 | 136.9 | 105.6
854.3 | 635.3 | 378.6 | 151.44 | 177.0246 | 195.8 | 178.3 | 200.9 | 199.1 | 295.9 | 29.6 | 21.2 | 54.5 | 11.3 | 254 | 15.8 | 762.9 | 717.8 | 623.8 | 716.2 | 557.9 | 262.2 | 379.1 | 498.3 | 298.4 | 382.4 | 32.2 | 67 | 94.2 | 83.7 | 201.9 | 188.5 | 74.1 | 150.3 | 137.2 | 105.7
855.3 | 636.3 | 376.2 | 150.48 | 175.9024 | 195.5 | 178.1 | 201 | 199.6 | 301.6 | 29.6 | 21.2 | 54.4 | 11.4 | 245.8 | 16 | 764.4 | 724.6 | 634.6 | 717 | 558 | 262.4 | 385.3 | 512 | 302.5 | 383.5 | 32.3 | 67.1 | 94.3 | 83.8 | 202.6 | 188.6 | 74.2 | 150.5 | 137.5 | 105.8
856.3 | 637.3 | 376.1 | 150.44 | 175.8557 | 195.6 | 177.9 | 201.1 | 200.1 | 304.7 | 29.7 | 21.2 | 54.4 | 11.6 | 262 | 14.9 | 765.9 | 727.1 | 664.6 | 716.7 | 560.5 | 262.7 | 385.3 | 517.3 | 304.1 | 384.6 | 32.3 | 67.2 | 94.5 | 83.9 | 202.9 | 188.9 | 74.3 | 150.6 | 137.7 | 106
857.3 | 638.3 | 376.2 | 150.48 | 175.9024 | 195.8 | 177.9 | 200.9 | 201 | 306.2 | 29.7 | 21.2 | 54.4 | 10.9 | 263.1 | 14.7 | 767 | 725.1 | 667.1 | 716.6 | 561.9 | 262.9 | 383.9 | 510.4 | 304.8 | 385.6 | 32.4 | 67.3 | 94.6 | 84 | 203.2 | 189.1 | 74.5 | 150.7 | 138 | 106.2
858.3 | 639.3 | 376.3 | 150.52 | 175.9492 | 195.7 | 177 | 200.4 | 201.2 | 304.5 | 29.7 | 21.2 | 54.3 | 10.8 | 261.3 | 14.6 | 767.1 | 720.4 | 657.6 | 716.2 | 560.4 | 263.1 | 382.3 | 511.9 | 304.3 | 385.2 | 32.4 | 67.4 | 94.8 | 84.1 | 203.5 | 189.7 | 74.6 | 150.9 | 138.2 | 106.3
859.3 | 640.3 | 376.4 | 150.56 | 175.996 | 196.8 | 177.1 | 200.2 | 201.6 | 306.5 | 29.7 | 21.2 | 54.2 | 12.1 | 258.4 | 13.7 | 767.9 | 719.5 | 662.8 | 717.4 | 564.7 | 263.4 | 380.7 | 504.7 | 303.7 | 387 | 32.5 | 67.5 | 95.1 | 84.3 | 203.8 | 189.7 | 74.7 | 151.1 | 138.4 | 106.5
860.3 | 641.3 | 376.5 | 150.6 | 176.0427 | 198 | 177 | 201.3 | 200.9 | 305.1 | 29.7 | 21.2 | 54.1 | 10.2 | 249.7 | 12 | 765.8 | 713.8 | 656.9 | 714.8 | 565.2 | 263.6 | 380.9 | 491.2 | 304.2 | 388.7 | 32.5 | 67.7 | 95 | 84.4 | 204.2 | 190.3 | 74.8 | 151.3 | 138.6 | 106.7
861.3 | 642.3 | 376.7 | 150.68 | 176.1362 | 197.2 | 176.4 | 202.9 | 200 | 301.3 | 29.7 | 21.2 | 54 | 10.5 | 267.6 | 12.8 | 764.4 | 713.8 | 659.3 | 715.6 | 564.7 | 263.9 | 380.4 | 482.4 | 304.5 | 389.5 | 32.6 | 67.8 | 95.1 | 84.5 | 204.6 | 190.7 | 74.9 | 151.6 | 138.9 | 106.8
862.3 | 643.3 | 376.8 | 150.72 | 176.183 | 196.2 | 176.8 | 203.3 | 200.2 | 297.9 | 29.6 | 21.2 | 54 | 10.2 | 259 | 13.2 | 765.4 | 719.4 | 674.4 | 718.1 | 567.5 | 264.1 | 382.2 | 482 | 305.7 | 392 | 32.6 | 67.9 | 95.3 | 84.6 | 204.9 | 190.6 | 75 | 151.9 | 139.1 | 107
863.3 | 644.3 | 376.9 | 150.76 | 176.2298 | 195.9 | 177.2 | 202.6 | 200.3 | 298.3 | 29.6 | 21.2 | 54.1 | 11.5 | 256 | 12.9 | 765.7 | 722.9 | 667.2 | 717.6 | 567.6 | 264.4 | 385.6 | 484.8 | 308.6 | 393.6 | 32.7 | 68 | 95.6 | 84.7 | 205.3 | 190.8 | 75.1 | 152 | 139.4 | 107.1
864.3 | 645.3 | 377.6 | 151.04 | 176.5571 | 195.1 | 178.8 | 202 | 200 | 299.2 | 29.6 | 21.2 | 54.2 | 12.5 | 264.7 | 12 | 763.9 | 718 | 644.8 | 714.5 | 565.8 | 264.6 | 383.4 | 480.3 | 307.4 | 392.7 | 32.7 | 68.1 | 95.8 | 84.8 | 205.6 | 190.8 | 75.2 | 152.1 | 139.7 | 107.3
865.3 | 646.3 | 378.7 | 151.48 | 177.0714 | 194.7 | 179.2 | 201.7 | 199.7 | 297.2 | 29.6 | 21.2 | 54.4 | 11.3 | 275.6 | 12.1 | 763 | 715.7 | 627.4 | 713.2 | 565 | 264.9 | 379.7 | 473.2 | 304.9 | 391.7 | 32.8 | 68.2 | 95.9 | 85 | 205.5 | 190.9 | 75.3 | 152.2 | 139.9 | 107.5
866.3 | 647.3 | 377.5 | 151 | 176.5103 | 194.1 | 179.7 | 202.3 | 199.5 | 295.5 | 29.6 | 21.2 | 54.4 | 9.7 | 264.6 | 10.9 | 763.2 | 719.2 | 622.3 | 712.6 | 564.8 | 265.2 | 377 | 475.7 | 303.1 | 391.6 | 32.9 | 68.3 | 95.9 | 85.1 | 205.8 | 190.9 | 75.4 | 152.5 | 140.1 | 107.6
867.3 | 648.3 | 376.4 | 150.56 | 175.996 | 193.7 | 181 | 202.6 | 200.6 | 296.5 | 29.6 | 21.2 | 54.4 | 9.4 | 252.7 | 10.3 | 763 | 722.2 | 624.7 | 713.5 | 566.3 | 265.4 | 381.3 | 492.8 | 306 | 394.1 | 32.9 | 68.5 | 96.2 | 85.2 | 205.9 | 191.1 | 75.6 | 152.7 | 140.2 | 107.8
868.3 | 649.3 | 376.2 | 150.48 | 175.9024 | 194.2 | 181.5 | 203.4 | 201.9 | 301.5 | 29.6 | 21.2 | 54.5 | 10.1 | 266 | 10.9 | 765.9 | 728.6 | 630.5 | 718.1 | 568.3 | 265.7 | 388.8 | 507.4 | 310.9 | 396.4 | 33 | 68.6 | 96.2 | 85.3 | 206 | 191.8 | 75.6 | 152.8 | 140.4 | 108
869.3 | 650.3 | 377.1 | 150.84 | 176.3233 | 194.1 | 181 | 203.8 | 203.1 | 303.2 | 29.5 | 21.2 | 54.6 | 9.9 | 264.8 | 12.9 | 766.6 | 726.4 | 635.1 | 721 | 569.4 | 266 | 388.3 | 493.7 | 311.5 | 397.1 | 33 | 68.7 | 96.4 | 85.5 | 205.9 | 191.9 | 75.8 | 153 | 140.7 | 108.1
870.3 | 651.3 | 378.8 | 151.52 | 177.1181 | 194.7 | 181.6 | 203.3 | 203.5 | 302.4 | 29.4 | 21.2 | 54.6 | 9.2 | 267.9 | 13.2 | 765.8 | 725.9 | 632.1 | 721.8 | 571.4 | 266.2 | 389.4 | 493 | 312.7 | 398.9 | 33.1 | 68.8 | 96.9 | 85.6 | 206.1 | 192.2 | 75.9 | 153.2 | 141 | 108.3
871.3 | 652.3 | 378.1 | 151.24 | 176.7908 | 196.9 | 182.1 | 202.8 | 203.1 | 303 | 29.4 | 21.2 | 54.5 | 8 | 247.5 | 14.4 | 762.7 | 712.6 | 634.9 | 720.9 | 570.3 | 266.5 | 387.8 | 476.2 | 312 | 399.4 | 33.1 | 68.9 | 96.8 | 85.7 | 206.4 | 192.6 | 75.9 | 153.5 | 141.3 | 108.4
872.3 | 653.3 | 377.2 | 150.88 | 176.37 | 199.2 | 182.9 | 202.4 | 203.8 | 298.4 | 29.4 | 21.2 | 54.4 | 7.8 | 245.6 | 13.9 | 759 | 699.9 | 621 | 718.3 | 570.6 | 266.7 | 386.9 | 463.4 | 312 | 400.7 | 33.2 | 69 | 96.9 | 85.8 | 206.9 | 193.1 | 76.1 | 153.9 | 141.5 | 108.6
873.3 | 654.3 | 375.9 | 150.36 | 175.7622 | 198.4 | 183.6 | 203.1 | 204.2 | 294 | 29.4 | 21.2 | 54.4 | 10 | 236.6 | 13.9 | 755.7 | 693 | 608.8 | 715.2 | 570 | 267 | 384.6 | 453.4 | 311.6 | 400.3 | 33.3 | 69.2 | 96.9 | 86 | 207.4 | 193.7 | 76.2 | 154.1 | 141.8 | 108.8
874.3 | 655.3 | 375.9 | 150.36 | 175.7622 | 198.6 | 183.9 | 204.7 | 203.9 | 289.9 | 29.4 | 21.2 | 54.3 | 9.6 | 257.9 | 12.1 | 754.8 | 689.9 | 598 | 713.4 | 568.9 | 267.2 | 382.3 | 449.5 | 310.7 | 399.7 | 33.3 | 69.3 | 96.9 | 86.1 | 207.7 | 193.8 | 76.3 | 154.2 | 142 | 108.9
875.3 | 656.3 | 376.3 | 150.52 | 175.9492 | 199.1 | 183.7 | 205.8 | 204.2 | 290.6 | 29.5 | 21.2 | 54.2 | 9 | 260.6 | 12.7 | 755.1 | 698 | 600.6 | 711 | 568.8 | 267.5 | 383.6 | 461.3 | 311.6 | 400.5 | 33.4 | 69.4 | 97.3 | 86.2 | 207.7 | 193.6 | 76.4 | 154.3 | 142.3 | 109.1
876.3 | 657.3 | 375.5 | 150.2 | 175.5751 | 197.4 | 183.2 | 206.9 | 205.5 | 293.4 | 29.6 | 21.2 | 54.2 | 9.5 | 267.3 | 14.4 | 752.1 | 696.2 | 599.4 | 705.5 | 567.1 | 267.7 | 382.2 | 457 | 311.4 | 400.1 | 33.4 | 69.5 | 97.5 | 86.4 | 207.5 | 193.8 | 76.5 | 154.4 | 142.3 | 109.1
877.3 | 658.3 | 374.6 | 149.84 | 175.1543 | 197.9 | 182.1 | 206.1 | 205.2 | 294.5 | 29.6 | 21.2 | 54.2 | 10.5 | 238 | 13.7 | 751.6 | 697.7 | 602.9 | 703.8 | 569.3 | 268 | 380.8 | 457.4 | 310.8 | 399.8 | 33.5 | 69.6 | 97.7 | 86.5 | 207.1 | 193.9 | 76.6 | 154.6 | 142.7 | 109.4
878.3 | 659.3 | 375.8 | 150.32 | 175.7154 | 197.2 | 183.6 | 206.2 | 203.9 | 296.3 | 29.6 | 21.2 | 54.2 | 10.1 | 253.6 | 11.9 | 754.6 | 711.1 | 622.5 | 707.6 | 571.5 | 268.3 | 384.2 | 465.7 | 312.6 | 401.6 | 33.5 | 69.7 | 97.7 | 86.6 | 206.5 | 194.1 | 76.7 | 154.7 | 142.9 | 109.5
879.3 | 660.3 | 376.1 | 150.44 | 175.8557 | 196.7 | 184.3 | 206.7 | 203.4 | 297 | 29.6 | 21.2 | 54.2 | 10.1 | 250.5 | 12.1 | 756.7 | 709.1 | 621.5 | 712.5 | 573.6 | 268.5 | 384.6 | 462.5 | 313 | 402.7 | 33.6 | 69.8 | 97.8 | 86.8 | 206.1 | 194.4 | 76.8 | 154.8 | 143.1 | 109.6
880.3 | 661.3 | 376.2 | 150.48 | 175.9024 | 196.6 | 184 | 206.7 | 203.4 | 295.3 | 29.6 | 21.2 | 54.4 | 9.5 | 251.2 | 11.3 | 757.4 | 713.7 | 623.3 | 712.6 | 573.8 | 268.7 | 384.2 | 465.3 | 312.7 | 403.4 | 33.6 | 70 | 98 | 86.9 | 205.7 | 194.3 | 76.9 | 155 | 143.3 | 109.8
881.3 | 662.3 | 375.6 | 150.24 | 175.6219 | 198.3 | 184 | 206.2 | 203.8 | 295.7 | 29.7 | 21.2 | 54.5 | 10 | 271.5 | 12.6 | 754 | 700.3 | 601.3 | 708.7 | 571.8 | 268.9 | 381.4 | 462.5 | 311.1 | 401.9 | 33.7 | 70.1 | 98.4 | 87 | 205.7 | 194 | 77 | 155.1 | 143.6 | 109.9
882.3 | 663.3 | 375.2 | 150.08 | 175.4349 | 200.6 | 183.5 | 205.5 | 204.3 | 294.6 | 29.7 | 21.2 | 54.6 | 9.1 | 274.5 | 12.3 | 750.1 | 695.5 | 591.4 | 703.7 | 570.8 | 269.2 | 378.8 | 454.8 | 309.3 | 401 | 33.8 | 70.2 | 98.5 | 87.2 | 205.6 | 193.8 | 77.1 | 155.3 | 143.7 | 110
883.3 | 664.3 | 377.3 | 150.92 | 176.4168 | 200.3 | 183.6 | 205.4 | 204.6 | 291.5 | 29.7 | 21.2 | 54.7 | 8.9 | 264.4 | 11.1 | 746.9 | 694.4 | 592.9 | 698 | 571.6 | 269.4 | 377.5 | 452.4 | 308.8 | 401.4 | 33.8 | 70.3 | 98.6 | 87.3 | 205.8 | 194 | 77.2 | 155.5 | 143.9 | 110.2
884.3 | 665.3 | 377.9 | 151.16 | 176.6973 | 199.7 | 183.8 | 205.5 | 204.3 | 289.2 | 29.7 | 21.2 | 54.7 | 8.3 | 253.9 | 11.7 | 742.9 | 683.8 | 588.5 | 693.7 | 570.6 | 269.7 | 375 | 441.3 | 308 | 401.1 | 33.9 | 70.4 | 98.6 | 87.4 | 206 | 194.3 | 77.3 | 155.7 | 144.1 | 110.3
885.3 | 666.3 | 378 | 151.2 | 176.7441 | 199.8 | 183.6 | 205.2 | 203.9 | 287.3 | 29.7 | 21.2 | 54.6 | 8.4 | 239.6 | 11.4 | 742.7 | 685.3 | 599.7 | 693 | 571.3 | 269.9 | 375.5 | 443.1 | 308.2 | 401.9 | 34 | 70.5 | 98.8 | 87.5 | 205.6 | 194.3 | 77.4 | 155.8 | 144.4 | 110.5
886.3 | 667.3 | 378.2 | 151.28 | 176.8376 | 199.4 | 183.1 | 204.5 | 203.4 | 287.4 | 29.7 | 21.2 | 54.6 | 8 | 240.4 | 9.9 | 741.2 | 679.2 | 604.8 | 692.1 | 571.4 | 270.2 | 374.6 | 435.9 | 308.5 | 402.2 | 34 | 70.7 | 98.9 | 87.6 | 205.9 | 194.4 | 77.5 | 156.1 | 144.6 | 110.7
887.3 | 668.3 | 378.1 | 151.24 | 176.7908 | 198.4 | 183.8 | 203.2 | 203.2 | 288.8 | 29.7 | 21.2 | 54.7 | 7.6 | 235.4 | 8.9 | 738.1 | 672.3 | 589.7 | 688.6 | 570.9 | 270.5 | 373.1 | 428.7 | 308.7 | 402.1 | 34.1 | 70.8 | 99 | 87.8 | 205.7 | 194.7 | 77.6 | 156.4 | 144.9 | 110.8
888.3 | 669.3 | 377.9 | 151.16 | 176.6973 | 198.1 | 183.9 | 201.6 | 202.2 | 286.9 | 29.7 | 21.2 | 54.7 | 8.2 | 241.7 | 9.2 | 734.9 | 666.9 | 577.8 | 684 | 570.2 | 270.7 | 370.6 | 422.3 | 307.4 | 401.6 | 34.1 | 70.9 | 99.2 | 87.9 | 205.7 | 195 | 77.7 | 156.6 | 145.1 | 110.9
889.3 | 670.3 | 378 | 151.2 | 176.7441 | 198 | 184 | 200.9 | 201.6 | 285.9 | 29.6 | 21.2 | 54.7 | 7.9 | 231.1 | 10.1 | 730.8 | 660.9 | 569 | 679.8 | 568.8 | 270.9 | 368.4 | 417.2 | 306.8 | 401.1 | 34.2 | 71 | 99.2 | 88 | 205.9 | 196.1 | 77.8 | 156.7 | 145.3 | 111.1
890.3 | 671.3 | 377.7 | 151.08 | 176.6038 | 198.3 | 183.1 | 200.9 | 201 | 282.2 | 29.6 | 21.2 | 54.8 | 7.8 | 241.4 | 10.6 | 726.9 | 656.7 | 563.4 | 675.9 | 568.1 | 271.1 | 364.8 | 409.8 | 305.5 | 400.4 | 34.3 | 71.1 | 99.3 | 88.2 | 206 | 196.6 | 77.9 | 156.8 | 145.5 | 111.2
891.3 | 672.3 | 377.8 | 151.12 | 176.6506 | 197.5 | 183 | 202.1 | 200.9 | 280.2 | 29.6 | 21.2 | 54.9 | 6.9 | 239.6 | 10.1 | 723.1 | 655.2 | 549.3 | 672.5 | 567.1 | 271.4 | 361.5 | 405.6 | 303.8 | 399.5 | 34.3 | 71.2 | 99.5 | 88.3 | 206.1 | 197 | 78.1 | 157 | 145.7 | 111.4
892.3 | 673.3 | 377.7 | 151.08 | 176.6038 | 196.5 | 182.4 | 203.4 | 201.9 | 280.2 | 29.6 | 21.2 | 54.9 | 7.3 | 239.6 | 10 | 718.9 | 651.6 | 542.1 | 667.8 | 565.8 | 271.6 | 357.7 | 399.4 | 301.8 | 398.4 | 34.4 | 71.3 | 99.5 | 88.4 | 206.4 | 197.8 | 78.2 | 157.3 | 145.9 | 111.5
893.3 | 674.3 | 377.2 | 150.88 | 176.37 | 195.7 | 182.5 | 204.3 | 202.6 | 277.9 | 29.6 | 21.2 | 55 | 7.7 | 246.7 | 10.8 | 714.9 | 644.2 | 540.5 | 664.9 | 564.2 | 271.8 | 353.6 | 390.5 | 299.6 | 397.7 | 34.5 | 71.5 | 99.7 | 88.5 | 206.4 | 198.4 | 78.2 | 157.6 | 146 | 111.6
894.3 | 675.3 | 377.4 | 150.96 | 176.4635 | 196.1 | 181.8 | 203.9 | 202.4 | 273.4 | 29.5 | 21.2 | 55 | 8.1 | 237.5 | 10.9 | 710.2 | 630.8 | 526.3 | 660.5 | 562.3 | 272 | 349.3 | 381.9 | 297.4 | 396.5 | 34.5 | 71.6 | 99.7 | 88.7 | 206.3 | 199 | 78.3 | 157.9 | 146.3 | 111.8
895.3 | 676.3 | 377.2 | 150.88 | 176.37 | 196.2 | 180.6 | 203.7 | 202.8 | 269.3 | 29.6 | 21.2 | 55.1 | 6.9 | 235.5 | 10.8 | 704.9 | 609.9 | 508.6 | 656.3 | 560.5 | 272.3 | 344.7 | 374.3 | 294.8 | 395 | 34.6 | 71.7 | 100 | 88.8 | 206.2 | 199.4 | 78.5 | 158.1 | 146.4 | 112
896.3 | 677.3 | 377.2 | 150.88 | 176.37 | 198.7 | 179.3 | 204.3 | 202.5 | 265.8 | 29.6 | 21.2 | 54.9 | 6.8 | 226.4 | 10.3 | 700 | 594.7 | 495.7 | 652.6 | 559 | 272.5 | 340.1 | 367.3 | 292.4 | 394 | 34.6 | 71.8 | 100.1 | 88.9 | 205.7 | 199.7 | 78.6 | 158.4 | 146.6 | 112.1
897.3 | 678.3 | 377.1 | 150.84 | 176.3233 | 199.5 | 179 | 204.2 | 201.7 | 262.5 | 29.6 | 21.2 | 54.9 | 6.9 | 224.9 | 9.2 | 696.9 | 592.5 | 495.3 | 650.1 | 558.6 | 272.7 | 336.9 | 365.1 | 291.2 | 393.5 | 34.7 | 71.9 | 100 | 89.1 | 205.1 | 200.2 | 78.6 | 158.5 | 146.7 | 112.3
898.3 | 679.3 | 377.2 | 150.88 | 176.37 | 200.2 | 179.7 | 204.2 | 201.3 | 262.9 | 29.6 | 21.2 | 55 | 7 | 244.8 | 7.9 | 695.4 | 595.5 | 490.9 | 648.6 | 557.4 | 272.9 | 335.9 | 366.7 | 291.2 | 393.2 | 34.8 | 72 | 100.1 | 89.2 | 204.5 | 200.1 | 78.7 | 158.6 | 146.9 | 112.4
899.3 | 680.3 | 377.3 | 150.92 | 176.4168 | 199.8 | 179.9 | 204.2 | 201.1 | 262.8 | 29.7 | 21.2 | 55.1 | 7.8 | 231.3 | 7.3 | 694.6 | 601.5 | 495.1 | 648.7 | 557.3 | 273.1 | 334.2 | 363.8 | 290.3 | 392.3 | 34.8 | 72.1 | 100.4 | 89.4 | 203.9 | 199.8 | 78.8 | 158.8 | 147 | 112.5
900.3 | 681.3 | 377.4 | 150.96 | 176.4635 | 199.7 | 179.9 | 203.9 | 200.9 | 262.9 | 29.7 | 21.2 | 55.3 | 7.5 | 247.1 | 7 | 691.6 | 602.4 | 487.4 | 645.5 | 555.2 | 273.4 | 332.4 | 362.9 | 288.9 | 391.2 | 34.9 | 72.2 | 100.4 | 89.5 | 203.7 | 199.1 | 79 | 158.8 | 147.2 | 112.6
901.3 | 682.3 | 377.4 | 150.96 | 176.4635 | 200.1 | 180.8 | 203.3 | 199.8 | 262.7 | 29.8 | 21.2 | 55.5 | 6.1 | 237.3 | 6.6 | 689.4 | 597 | 487.5 | 643.4 | 553.4 | 273.6 | 330.7 | 362.1 | 287.7 | 390.1 | 35 | 72.3 | 100.6 | 89.7 | 203.5 | 199 | 79 | 158.8 | 147.3 | 112.8
902.3 | 683.3 | 377.6 | 151.04 | 176.5571 | 200.3 | 181.7 | 203.4 | 198.9 | 263.8 | 29.9 | 21.2 | 55.6 | 6.5 | 232.7 | 6.5 | 688.2 | 602 | 500.2 | 641.7 | 553.9 | 273.9 | 330.7 | 365.4 | 288.2 | 390.4 | 35 | 72.5 | 100.7 | 89.8 | 203.2 | 198.7 | 79.2 | 159 | 147.5 | 112.9
903.3 | 684.3 | 377.6 | 151.04 | 176.5571 | 200.1 | 180.9 | 203.6 | 198.4 | 267.1 | 29.9 | 21.2 | 55.7 | 6.7 | 253.4 | 7.2 | 687.1 | 609.8 | 509.9 | 641.4 | 555.4 | 274.1 | 332.9 | 372.2 | 288.8 | 390.4 | 35.1 | 72.6 | 100.8 | 89.9 | 203 | 198.7 | 79.2 | 159 | 147.6 | 113
904.3 | 685.3 | 377.5 | 151 | 176.5103 | 199.8 | 179.9 | 202.4 | 198.1 | 269.2 | 29.9 | 21.2 | 55.8 | 7.3 | 241.9 | 8.6 | 687.1 | 614.2 | 518.1 | 641 | 555.5 | 274.4 | 334.4 | 374.3 | 289.7 | 390.5 | 35.2 | 72.7 | 101.1 | 90.1 | 203.3 | 198.2 | 79.3 | 159 | 147.8 | 113.1
905.3 | 686.3 | 377.4 | 150.96 | 176.4635 | 199.5 | 179.2 | 201.3 | 198.2 | 271.6 | 30 | 21.2 | 55.9 | 6.7 | 246.8 | 9 | 686.8 | 624.8 | 526.3 | 639.6 | 555 | 274.6 | 336.4 | 377.2 | 290.4 | 390.5 | 35.2 | 72.8 | 101.3 | 90.2 | 203.8 | 197.8 | 79.4 | 159.2 | 148 | 113.3
906.3 | 687.3 | 376.6 | 150.64 | 176.0895 | 199.5 | 180 | 201.7 | 198.8 | 272.7 | 30.1 | 21.2 | 55.9 | 7.8 | 260.6 | 8.4 | 686 | 627.2 | 533.2 | 637.8 | 555.5 | 274.8 | 338.1 | 382.2 | 291.6 | 391.3 | 35.3 | 72.9 | 101.4 | 90.4 | 203.8 | 197.7 | 79.6 | 159.3 | 148.1 | 113.5
907.3 | 688.3 | 377.8 | 151.12 | 176.6506 | 198.2 | 180 | 202.4 | 200 | 271.5 | 30.2 | 21.2 | 55.9 | 7.8 | 275.3 | 7 | 684.5 | 627.4 | 534.9 | 636.2 | 555.1 | 275 | 337.2 | 380.9 | 291 | 390.9 | 35.4 | 73 | 101.5 | 90.5 | 204 | 197.3 | 79.6 | 159.3 | 148.2 | 113.6
908.3 | 689.3 | 377.9 | 151.16 | 176.6973 | 199.5 | 179.5 | 201.6 | 200 | 272.9 | 30.3 | 21.2 | 55.9 | 7.9 | 258.7 | 6.2 | 686.6 | 642.9 | 552.5 | 639.5 | 557.2 | 275.3 | 341.2 | 388.5 | 293 | 392.4 | 35.4 | 73.2 | 101.4 | 90.7 | 204 | 197.1 | 79.7 | 159.4 | 148.5 | 113.8
909.3 | 690.3 | 377.9 | 151.16 | 176.6973 | 200.1 | 178 | 201.2 | 199.7 | 275.7 | 30.3 | 21.2 | 55.9 | 8.1 | 259.9 | 6.2 | 691.1 | 653.3 | 569.1 | 647.2 | 557.8 | 275.5 | 346.1 | 393.3 | 294.7 | 394.3 | 35.5 | 73.3 | 101.6 | 90.8 | 204.3 | 197 | 79.8 | 159.5 | 148.7 | 113.9
910.3 | 691.3 | 378 | 151.2 | 176.7441 | 200.3 | 177.2 | 201.1 | 199.9 | 279.1 | 30.4 | 21.2 | 56 | 9.8 | 246.1 | 7.2 | 697.9 | 668.5 | 573.7 | 655.5 | 558.9 | 275.7 | 352.7 | 411.7 | 297.5 | 395.6 | 35.6 | 73.4 | 101.8 | 90.9 | 204.9 | 197.6 | 80 | 159.6 | 148.9 | 114.1
911.3 | 692.3 | 378.1 | 151.24 | 176.7908 | 198.8 | 175.9 | 201 | 200.4 | 283.8 | 30.4 | 21.1 | 56.1 | 8.7 | 260.7 | 7.8 | 703.4 | 674.1 | 600.7 | 662.9 | 562.1 | 275.8 | 355.8 | 421.9 | 299.4 | 396.7 | 35.6 | 73.4 | 102 | 91 | 205.1 | 197.4 | 80.1 | 159.7 | 149.1 | 114.2
912.3 | 693.3 | 377.8 | 151.12 | 176.6506 | 197.8 | 175.4 | 201.3 | 201 | 286.6 | 30.4 | 21.1 | 56.1 | 8.3 | 252.7 | 8.2 | 709.3 | 679.7 | 621.1 | 672 | 564.1 | 276 | 361.6 | 430.8 | 301.8 | 399.6 | 35.7 | 73.5 | 102.1 | 91.2 | 205.7 | 197.3 | 80.2 | 159.8 | 149.3 | 114.3
913.3 | 694.3 | 378 | 151.2 | 176.7441 | 197.1 | 176.1 | 201.8 | 201.4 | 288.8 | 30.5 | 21.1 | 56.1 | 7.4 | 261.7 | 8.2 | 712.7 | 683.7 | 633.8 | 675.6 | 565.9 | 276.2 | 362.7 | 437.1 | 303.6 | 399.8 | 35.8 | 73.7 | 102.2 | 91.3 | 206.1 | 197.1 | 80.3 | 160 | 149.6 | 114.5
914.3 | 695.3 | 378 | 151.2 | 176.7441 | 196.3 | 176 | 201.8 | 201 | 290.1 | 30.6 | 21.2 | 56 | 7.2 | 242 | 8.7 | 714.7 | 686.7 | 641.5 | 676.5 | 567.4 | 276.4 | 364.6 | 439.5 | 305.2 | 400.9 | 35.8 | 73.8 | 102.4 | 91.4 | 206.5 | 196.8 | 80.4 | 160 | 149.8 | 114.7
915.3 | 696.3 | 377.6 | 151.04 | 176.5571 | 196.7 | 175.6 | 201.7 | 199.9 | 290.4 | 30.6 | 21.1 | 55.9 | 6.9 | 240.7 | 7.9 | 714.7 | 680.4 | 625.4 | 676.7 | 567.1 | 276.6 | 364 | 430.4 | 305.5 | 401.5 | 35.9 | 73.9 | 102.5 | 91.6 | 207.2 | 196.4 | 80.5 | 160.2 | 150 | 114.8
916.3 | 697.3 | 375.7 | 150.28 | 175.6687 | 196.1 | 176.5 | 200.9 | 200.2 | 288.6 | 30.6 | 21.1 | 55.7 | 6.7 | 231.4 | 6.4 | 712 | 669.9 | 606 | 673.6 | 564.9 | 276.9 | 362 | 424.3 | 304.6 | 400.7 | 36 | 74 | 102.7 | 91.7 | 207.2 | 196.1 | 80.6 | 160.3 | 150.2 | 115
917.3 | 698.3 | 377.8 | 151.12 | 176.6506 | 196 | 178.1 | 200.2 | 201.5 | 286 | 30.6 | 21.1 | 55.6 | 7.4 | 247.3 | 5.5 | 709.1 | 660.8 | 590.3 | 671.3 | 564 | 277.1 | 359 | 417.6 | 302.6 | 399.8 | 36 | 74.1 | 102.8 | 91.8 | 207 | 196 | 80.7 | 160.4 | 150.4 | 115.1
918.3 | 699.3 | 378.9 | 151.56 | 177.1649 | 196.2 | 179.2 | 200.3 | 202.7 | 284.9 | 30.7 | 21.2 | 55.6 | 7.7 | 249.6 | 5.1 | 704.9 | 638.9 | 570.7 | 668 | 561.5 | 277.3 | 355.9 | 408.9 | 300.5 | 398.3 | 36.1 | 74.2 | 102.9 | 92 | 207.1 | 196.1 | 80.8 | 160.5 | 150.5 | 115.2
919.3 | 700.3 | 379.4 | 151.76 | 177.3987 | 198.7 | 178.3 | 199.4 | 202 | 281.7 | 30.6 | 21.1 | 55.6 | 7.1 | 253 | 4.5 | 701.5 | 626.1 | 560.3 | 664.1 | 560.2 | 277.6 | 351.7 | 402.5 | 298 | 397.3 | 36.1 | 74.3 | 103 | 92.1 | 207.4 | 196.3 | 80.9 | 160.6 | 150.7 | 115.4
920.3 | 701.3 | 379.1 | 151.64 | 177.2584 | 200 | 177.7 | 199.4 | 202 | 279.1 | 30.7 | 21.1 | 55.7 | 6.8 | 233.7 | 4.1 | 697.9 | 611.8 | 543.6 | 660.2 | 559 | 277.8 | 349 | 397.2 | 296.5 | 396.3 | 36.2 | 74.4 | 103.1 | 92.2 | 207.2 | 196.6 | 81 | 160.7 | 150.8 | 115.5
921.3 | 702.3 | 378.7 | 151.48 | 177.0714 | 200.6 | 177.3 | 200 | 202 | 277 | 30.8 | 21.2 | 55.8 | 6.2 | 229.3 | 4.4 | 693.2 | 596.8 | 527 | 655.4 | 557.3 | 278 | 344.4 | 387.4 | 294.2 | 395.1 | 36.2 | 74.5 | 103.2 | 92.3 | 207.1 | 197.1 | 81.1 | 160.9 | 150.9 | 115.7
922.3 | 703.3 | 377.4 | 150.96 | 176.4635 | 200.9 | 176.5 | 200.2 | 201.9 | 274 | 30.8 | 21.2 | 55.8 | 7.5 | 248.4 | 5.1 | 689.4 | 594.1 | 520.6 | 650.4 | 556.2 | 278.2 | 341.4 | 382.3 | 292.4 | 394 | 36.3 | 74.6 | 103.4 | 92.5 | 207.4 | 197 | 81.2 | 161.1 | 151.1 | 115.8
923.3 | 704.3 | 376.9 | 150.76 | 176.2298 | 201.6 | 175.6 | 200.7 | 201.9 | 273.1 | 30.9 | 21.2 | 56 | 7.2 | 255.6 | 5.2 | 686.7 | 591.3 | 530.3 | 646.8 | 556.1 | 278.5 | 339.3 | 381.1 | 291.6 | 393 | 36.3 | 74.8 | 103.5 | 92.6 | 207.5 | 197.3 | 81.3 | 161.3 | 151.2 | 116
924.3 | 705.3 | 376.3 | 150.52 | 175.9492 | 203.2 | 175.7 | 201 | 202.7 | 273.9 | 31 | 21.1 | 56.1 | 6.2 | 250.1 | 5.2 | 688.3 | 601.5 | 552.4 | 648.2 | 559.3 | 278.7 | 342.1 | 387.6 | 293.1 | 395 | 36.4 | 74.9 | 103.9 | 92.7 | 207.2 | 197.2 | 81.4 | 161.5 | 151.3 | 116.1
925.3 | 706.3 | 376.6 | 150.64 | 176.0895 | 203.4 | 175.2 | 200.5 | 203.1 | 275.4 | 31.1 | 21.1 | 56.3 | 6.8 | 247.5 | 5.1 | 690.7 | 610.2 | 571.6 | 651.1 | 560.4 | 278.9 | 345.1 | 400 | 295.3 | 395.4 | 36.5 | 75 | 103.8 | 92.9 | 207.2 | 197.1 | 81.5 | 161.5 | 151.5 | 116.3
926.3 | 707.3 | 378.8 | 151.52 | 177.1181 | 203.7 | 175.2 | 200.6 | 203.8 | 277.9 | 31.1 | 21.1 | 56.4 | 6.4 | 246.4 | 4.9 | 693.3 | 614.4 | 590.6 | 657.8 | 564 | 279.1 | 350.6 | 401.7 | 298.4 | 399 | 36.5 | 75.1 | 104 | 93 | 207.5 | 197.1 | 81.6 | 161.8 | 151.7 | 116.4
927.3 | 708.3 | 378.8 | 151.52 | 177.1181 | 204.5 | 175.4 | 200.2 | 204.6 | 278.3 | 31.1 | 21.1 | 56.6 | 6.4 | 249.8 | 4.7 | 696.2 | 622.6 | 601.4 | 660 | 565.6 | 279.3 | 353.5 | 403.6 | 300.3 | 400 | 36.6 | 75.2 | 104.1 | 93.1 | 207.9 | 197 | 81.7 | 161.9 | 151.9 | 116.5
928.3 | 709.3 | 378.5 | 151.4 | 176.9779 | 204.1 | 175.6 | 200.1 | 204.9 | 277.5 | 31.1 | 21.1 | 56.8 | 6.1 | 231.4 | 5.1 | 697.3 | 628.7 | 613.8 | 660.5 | 567.5 | 279.5 | 355 | 404.7 | 301.4 | 401.9 | 36.7 | 75.3 | 104.3 | 93.2 | 208.5 | 196.7 | 81.8 | 162.1 | 152 | 116.6
929.3 | 710.3 | 378.6 | 151.44 | 177.0246 | 203.3 | 176.1 | 200.7 | 205.5 | 277 | 31 | 21.1 | 57 | 6.9 | 216.1 | 5.6 | 698.3 | 629.2 | 605.9 | 663 | 568 | 279.8 | 356.1 | 405.3 | 302.5 | 402 | 36.7 | 75.4 | 104.3 | 93.3 | 210.2 | 197.4 | 81.9 | 162.2 | 152.3 | 116.8
930.3 | 711.3 | 378.2 | 151.28 | 176.8376 | 203.2 | 176.6 | 201.3 | 205.7 | 277 | 31.1 | 21.1 | 57 | 6.4 | 231.3 | 5 | 698 | 630 | 599.9 | 663.2 | 567.1 | 280 | 356.2 | 404.9 | 302.8 | 401.4 | 36.8 | 75.6 | 104.3 | 93.5 | 210.7 | 198.4 | 82 | 162.6 | 152.5 | 117
931.3 | 712.3 | 377.9 | 151.16 | 176.6973 | 202.9 | 176.9 | 201.5 | 206 | 276.2 | 31.1 | 21.1 | 57 | 7.1 | 239.2 | 4.8 | 697.2 | 631.2 | 597.4 | 662.5 | 566.7 | 280.3 | 354 | 399.7 | 301.5 | 400.5 | 36.8 | 75.7 | 104.6 | 93.6 | 210.6 | 199.4 | 82.1 | 162.9 | 152.6 | 117.1
932.3 | 713.3 | 377.9 | 151.16 | 176.6973 | 203.5 | 177.3 | 200.9 | 206.6 | 274.2 | 31 | 21.1 | 56.9 | 6.3 | 239.8 | 5.1 | 698.8 | 639.7 | 611 | 665.1 | 567.5 | 280.5 | 354.6 | 399.9 | 301.8 | 401 | 36.9 | 75.8 | 104.7 | 93.7 | 210.9 | 199.4 | 82.2 | 163 | 152.9 | 117.3
933.3 | 714.3 | 377.4 | 150.96 | 176.4635 | 202.3 | 178.4 | 201 | 207.1 | 273 | 31 | 21.1 | 56.9 | 6.4 | 239.2 | 5 | 702.2 | 646.2 | 614 | 669.9 | 568.4 | 280.8 | 356.9 | 397.9 | 303.4 | 402.5 | 37 | 75.9 | 104.7 | 93.9 | 210.9 | 199.9 | 82.3 | 163.2 | 153 | 117.5
934.3 | 715.3 | 377.4 | 150.96 | 176.4635 | 202.3 | 178.5 | 200.4 | 207.3 | 273 | 31 | 21.1 | 56.9 | 6.5 | 245.8 | 5.8 | 702.1 | 642.5 | 615.5 | 670.8 | 568.7 | 281 | 356.9 | 398.3 | 303.3 | 402.3 | 37 | 76 | 104.9 | 94 | 211.2 | 199.7 | 82.5 | 163.3 | 153.2 | 117.6
935.3 | 716.3 | 378.6 | 151.44 | 177.0246 | 202.5 | 178 | 200 | 207.1 | 273.4 | 30.9 | 21.1 | 57 | 5.9 | 229.9 | 5.7 | 702.5 | 643.3 | 628 | 672 | 569.8 | 281.3 | 357.5 | 396.5 | 303.6 | 402.5 | 37.1 | 76.1 | 105 | 94.1 | 211.2 | 199.6 | 82.5 | 163.4 | 153.4 | 117.8
936.3 | 717.3 | 377.4 | 150.96 | 176.4635 | 202.6 | 178 | 200.2 | 207.2 | 273 | 30.9 | 21.1 | 57.1 | 6.5 | 221.5 | 5.2 | 705.2 | 652.4 | 639.9 | 674.9 | 570.6 | 281.6 | 357.7 | 400.3 | 303.9 | 403.1 | 37.2 | 76.2 | 105.1 | 94.2 | 211.4 | 199.5 | 82.6 | 163.4 | 153.6 | 118
937.3 | 718.3 | 378.1 | 151.24 | 176.7908 | 202.8 | 178 | 200.4 | 206.6 | 274.4 | 30.9 | 21.1 | 57.2 | 6.2 | 247.5 | 5.3 | 707 | 650.5 | 630.7 | 676.1 | 570.1 | 281.8 | 357.4 | 398.4 | 304 | 403.1 | 37.2 | 76.3 | 105.2 | 94.4 | 210.9 | 200.1 | 82.7 | 163.5 | 153.9 | 118.1
938.3 | 719.3 | 377.8 | 151.12 | 176.6506 | 202.5 | 178.6 | 200.8 | 205.7 | 273.6 | 30.9 | 21.1 | 57.3 | 6.5 | 250.4 | 5.2 | 709.7 | 649.7 | 633.8 | 679.1 | 571.2 | 282 | 359.5 | 401.7 | 305.1 | 404.7 | 37.3 | 76.4 | 105.3 | 94.5 | 210.8 | 200.8 | 82.8 | 163.6 | 154.1 | 118.2
939.3 | 720.3 | 377.4 | 150.96 | 176.4635 | 202.7 | 179.3 | 200.7 | 205.6 | 275.5 | 30.9 | 21.1 | 57.4 | 6.2 | 234.4 | 5.1 | 708.5 | 642 | 632.1 | 678.2 | 570.7 | 282.3 | 360.8 | 398.8 | 305.8 | 404.9 | 37.3 | 76.5 | 105.4 | 94.6 | 210.6 | 201.2 | 82.9 | 163.8 | 154.3 | 118.4
940.3 | 721.3 | 378 | 151.2 | 176.7441 | 203.7 | 180.1 | 200.3 | 206.2 | 275.9 | 31 | 21.1 | 57.5 | 6.2 | 238.4 | 5.4 | 705.1 | 620.4 | 612.9 | 674.8 | 568.1 | 282.5 | 357.5 | 391.9 | 303.9 | 403.5 | 37.4 | 76.7 | 105.5 | 94.7 | 210.6 | 201.7 | 83 | 163.9 | 154.5 | 118.5
941.3 | 722.3 | 378.5 | 151.4 | 176.9779 | 203.4 | 180.5 | 201.1 | 206.2 | 272.6 | 31 | 21.1 | 57.6 | 5.9 | 244.6 | 6.3 | 702.9 | 613.5 | 595.2 | 672.3 | 566 | 282.7 | 354.3 | 387.7 | 301.7 | 402.4 | 37.5 | 76.8 | 105.8 | 94.8 | 210.6 | 201.9 | 83.1 | 164.1 | 154.7 | 118.7
942.3 | 723.3 | 376.3 | 150.52 | 175.9492 | 203.4 | 180.6 | 201.6 | 205.9 | 271.7 | 31.1 | 21.1 | 57.5 | 6.2 | 239.6 | 6.9 | 700.1 | 605.4 | 573.6 | 668.8 | 563.8 | 283 | 350.7 | 381.4 | 299.9 | 401.2 | 37.5 | 76.9 | 105.9 | 95 | 210.5 | 201.7 | 83.2 | 164.2 | 154.8 | 118.8
943.3 | 724.3 | 376 | 150.4 | 175.8089 | 203.8 | 180.7 | 202.2 | 205.7 | 270.3 | 31.2 | 21.1 | 57.5 | 6.8 | 249.3 | 7.8 | 696.9 | 599.7 | 560.8 | 665.6 | 562.2 | 283.2 | 347 | 377.3 | 297.9 | 399.8 | 37.6 | 77 | 105.9 | 95.1 | 210.5 | 201.4 | 83.3 | 164.3 | 155 | 118.9
944.3 | 725.3 | 376.3 | 150.52 | 175.9492 | 203.3 | 180.3 | 202.6 | 205.2 | 269.8 | 31.2 | 21.1 | 57.6 | 6.7 | 243.7 | 7.7 | 694 | 593.1 | 553.6 | 662.1 | 560.8 | 283.4 | 343.8 | 373.3 | 296.4 | 398.3 | 37.6 | 77.1 | 106.1 | 95.2 | 210.8 | 201.1 | 83.4 | 164.4 | 155.1 | 119.1
945.3 | 726.3 | 376.6 | 150.64 | 176.0895 | 203 | 179.7 | 203.2 | 204.7 | 269.6 | 31.2 | 21.1 | 57.6 | 7.2 | 248.4 | 7 | 695.7 | 600.7 | 555 | 662.5 | 560.9 | 283.7 | 343.3 | 375.6 | 296.1 | 398.7 | 37.7 | 77.2 | 106.3 | 95.3 | 210.5 | 201.3 | 83.5 | 164.4 | 155.2 | 119.3
946.3 | 727.3 | 376.7 | 150.68 | 176.1362 | 202 | 179.3 | 203.1 | 204 | 270.9 | 31.4 | 21.1 | 57.7 | 7.1 | 243.3 | 6 | 699.3 | 618.4 | 569.4 | 665.1 | 561.8 | 283.9 | 347 | 388.5 | 297.9 | 400.1 | 37.8 | 77.3 | 106.3 | 95.4 | 210.4 | 201.5 | 83.6 | 164.5 | 155.4 | 119.4
947.3 | 728.3 | 376.7 | 150.68 | 176.1362 | 201.1 | 179 | 202.9 | 203.3 | 275.7 | 31.4 | 21.1 | 57.8 | 6.8 | 242 | 5.5 | 702.2 | 626.3 | 594 | 668.3 | 565.1 | 284.2 | 350.7 | 396.9 | 299.9 | 401.5 | 37.8 | 77.3 | 106.5 | 95.5 | 210.3 | 201.6 | 83.7 | 164.6 | 155.5 | 119.5
948.3 | 729.3 | 376.9 | 150.76 | 176.2298 | 202 | 178.5 | 202.4 | 202.9 | 279 | 31.4 | 21.1 | 57.9 | 7 | 227.4 | 5.4 | 703.9 | 625.7 | 595.6 | 671.6 | 564.5 | 284.4 | 352.6 | 393.5 | 300.2 | 402.3 | 37.9 | 77.4 | 106.6 | 95.7 | 210.1 | 201.2 | 83.8 | 164.8 | 155.7 | 119.6
949.3 | 730.3 | 376.8 | 150.72 | 176.183 | 202.4 | 178.8 | 201.7 | 203 | 277.9 | 31.4 | 21.1 | 58 | 7.2 | 203.1 | 5.2 | 707.1 | 632.2 | 614.4 | 674.7 | 566.3 | 284.7 | 354.8 | 392.4 | 301.3 | 403.2 | 38 | 77.5 | 106.7 | 95.8 | 210.1 | 201.1 | 84 | 164.9 | 155.8 | 119.8
950.3 | 731.3 | 377 | 150.8 | 176.2765 | 200.9 | 179.9 | 202 | 204.3 | 277.3 | 31.5 | 21.1 | 58 | 7.8 | 200.5 | 5.5 | 710.5 | 640 | 628.5 | 679.1 | 568.3 | 284.9 | 357.5 | 393.1 | 302.2 | 403.7 | 38 | 77.6 | 106.9 | 95.9 | 209.9 | 200.8 | 84 | 165 | 156 | 119.9
951.3 | 732.3 | 376.9 | 150.76 | 176.2298 | 200.7 | 180.9 | 202.7 | 205 | 279.7 | 31.6 | 21.1 | 58 | 7.6 | 206.2 | 5.8 | 713.3 | 642.1 | 624.2 | 682.9 | 566.4 | 285.1 | 356.4 | 392.8 | 301.8 | 402.7 | 38.1 | 77.7 | 106.9 | 96 | 210.4 | 200.3 | 84.1 | 165 | 156.2 | 120
952.3 | 733.3 | 376.8 | 150.72 | 176.183 | 200.7 | 180.9 | 203.4 | 204.5 | 281.1 | 31.7 | 21.1 | 58.1 | 6.9 | 200.6 | 5.9 | 713.9 | 641.5 | 616.1 | 683.1 | 565.5 | 285.3 | 355.9 | 390.8 | 301.2 | 402.7 | 38.1 | 77.8 | 106.9 | 96.1 | 210.6 | 200.5 | 84.2 | 165.1 | 156.4 | 120.2
953.3 | 734.3 | 376.9 | 150.76 | 176.2298 | 200 | 181.1 | 203.9 | 204.4 | 282.7 | 31.8 | 21.1 | 58.2 | 6.3 | 205 | 6.3 | 712.1 | 642.6 | 615 | 680.1 | 564.3 | 285.6 | 356.9 | 392.6 | 301.1 | 401.9 | 38.2 | 77.9 | 107.1 | 96.2 | 210.7 | 201.2 | 84.4 | 165.3 | 156.6 | 120.3
954.3 | 735.3 | 376.9 | 150.76 | 176.2298 | 199 | 180.8 | 204.2 | 204.2 | 285.7 | 31.8 | 21.1 | 58.2 | 6.6 | 218.1 | 6.4 | 709.5 | 636.7 | 615.3 | 676.2 | 564.2 | 285.8 | 357.7 | 391.8 | 301.1 | 401.4 | 38.3 | 78 | 107.3 | 96.3 | 210.7 | 201.3 | 84.5 | 165.5 | 156.7 | 120.5
955.3 | 736.3 | 376.9 | 150.76 | 176.2298 | 199.1 | 180.2 | 203.7 | 203.7 | 285.9 | 31.9 | 21.1 | 58.2 | 6.4 | 244.9 | 5.7 | 709.1 | 640.6 | 614.1 | 674 | 564.6 | 286 | 357.6 | 399.7 | 300.8 | 401.1 | 38.3 | 78.1 | 107.6 | 96.5 | 210.6 | 200.9 | 84.5 | 165.5 | 156.9 | 120.6
956.3 | 737.3 | 376.7 | 150.68 | 176.1362 | 199.3 | 179.5 | 203.2 | 203.3 | 289 | 31.9 | 21.1 | 58.2 | 6.5 | 246.1 | 5 | 713 | 651.3 | 633.3 | 677.1 | 568.2 | 286.3 | 359.7 | 412.5 | 301.9 | 402.1 | 38.4 | 78.2 | 107.7 | 96.6 | 210.9 | 201 | 84.7 | 165.6 | 157.1 | 120.7
957.3 | 738.3 | 376.8 | 150.72 | 176.183 | 199.9 | 179 | 203.1 | 203.4 | 292.8 | 31.9 | 21.1 | 58.3 | 6.3 | 216.9 | 4.8 | 719.3 | 671.7 | 643.5 | 683.9 | 569.3 | 286.5 | 364.4 | 434.1 | 304 | 404 | 38.4 | 78.3 | 107.7 | 96.7 | 211.3 | 200.9 | 84.8 | 165.7 | 157.2 | 120.9
958.3 | 739.3 | 376.7 | 150.68 | 176.1362 | 200.7 | 180.7 | 202.5 | 203.2 | 299.2 | 31.9 | 21.1 | 58.4 | 6.6 | 233 | 4.5 | 724 | 672.1 | 641.8 | 689.3 | 570.3 | 286.7 | 368.9 | 446.8 | 307.2 | 405 | 38.5 | 78.4 | 108 | 96.8 | 211.2 | 200.7 | 84.9 | 165.9 | 157.4 | 121
959.3 | 740.3 | 377 | 150.8 | 176.2765 | 200.6 | 182.7 | 203 | 203.6 | 299.4 | 32 | 21.1 | 58.4 | 6.8 | 269.9 | 4.1 | 724.3 | 668.4 | 635 | 689.7 | 569.6 | 287 | 367.6 | 435.7 | 306.3 | 405 | 38.6 | 78.5 | 108 | 96.9 | 211 | 200.3 | 85 | 165.9 | 157.6 | 121.2
960.3 | 741.3 | 377.1 | 150.84 | 176.3233 | 199.6 | 182.8 | 204.5 | 204 | 297.3 | 32 | 21.1 | 58.4 | 7 | 282.9 | 3.6 | 723.9 | 663.9 | 628.8 | 689.8 | 569.2 | 287.2 | 366.8 | 435.8 | 306.7 | 405.5 | 38.6 | 78.6 | 108.1 | 97 | 211.4 | 199.9 | 85.1 | 166 | 157.8 | 121.3
961.3 | 742.3 | 377.2 | 150.88 | 176.37 | 200 | 182.9 | 204.6 | 204 | 297.2 | 32 | 21.1 | 58.5 | 6.8 | 269.3 | 3.5 | 725 | 668.1 | 633.4 | 691.6 | 570.1 | 287.5 | 366.2 | 431.9 | 306.5 | 405.2 | 38.7 | 78.6 | 108.3 | 97.1 | 211.3 | 199.6 | 85.2 | 166.1 | 158 | 121.4
962.3 | 743.3 | 377.3 | 150.92 | 176.4168 | 201.5 | 182.5 | 203.4 | 204 | 296.7 | 32.1 | 21.1 | 58.5 | 7 | 248.5 | 3.6 | 726.2 | 664.5 | 641 | 694.7 | 569.5 | 287.7 | 366.5 | 432.3 | 306.7 | 405.6 | 38.7 | 78.7 | 108.4 | 97.2 | 211.3 | 199.3 | 85.3 | 166.2 | 158.2 | 121.6
963.3 | 744.3 | 377.2 | 150.88 | 176.37 | 201.8 | 182.6 | 202.7 | 203.5 | 296.5 | 32.1 | 21.1 | 58.7 | 6.5 | 246.1 | 3.6 | 724.4 | 653.3 | 636.7 | 693.3 | 569.6 | 288 | 366 | 429.2 | 306.9 | 405.6 | 38.8 | 78.8 | 108.5 | 97.3 | 211.3 | 199.6 | 85.4 | 166.4 | 158.4 | 121.7
964.3 | 745.3 | 377.2 | 150.88 | 176.37 | 203.8 | 183.4 | 201.9 | 203.6 | 293.7 | 32.2 | 21.1 | 58.8 | 7 | 257.1 | 3.7 | 724.8 | 656.5 | 632.5 | 693 | 569.5 | 288.3 | 363.9 | 435.1 | 306.1 | 404.7 | 38.9 | 78.9 | 108.5 | 97.4 | 211.1 | 200.2 | 85.5 | 166.5 | 158.5 | 121.9
965.3 | 746.3 | 377.2 | 150.88 | 176.37 | 204.4 | 184 | 201.5 | 204.1 | 294.3 | 32.3 | 21.1 | 58.8 | 7.1 | 264.8 | 3.7 | 723.2 | 657.2 | 625.5 | 689.5 | 569.5 | 288.5 | 362.7 | 432.6 | 306 | 404.5 | 38.9 | 79 | 108.6 | 97.5 | 211.2 | 200.8 | 85.6 | 166.7 | 158.6 | 122
966.3 | 747.3 | 377.1 | 150.84 | 176.3233 | 203.7 | 183.2 | 202.5 | 204 | 291.9 | 32.3 | 21.1 | 58.8 | 7.4 | 261.9 | 3.9 | 721.5 | 645.8 | 605 | 685.7 | 567.5 | 288.8 | 360 | 425 | 304.5 | 403.4 | 39 | 79.1 | 108.9 | 97.6 | 211.2 | 200.9 | 85.7 | 166.8 | 158.8 | 122.1
967.3 | 748.3 | 377.2 | 150.88 | 176.37 | 203 | 182.9 | 203.3 | 203.9 | 289.7 | 32.3 | 21.1 | 58.8 | 7.7 | 254.4 | 5.1 | 719.2 | 639.4 | 594.4 | 683.1 | 565.5 | 289.1 | 357.1 | 417.3 | 302.7 | 402.3 | 39 | 79.2 | 108.9 | 97.7 | 211.4 | 200.5 | 85.8 | 166.8 | 159 | 122.3
968.3 | 749.3 | 377.2 | 150.88 | 176.37 | 202.3 | 182.8 | 203.2 | 204.7 | 286.5 | 32.3 | 21.1 | 58.7 | 7.1 | 253.2 | 6.4 | 715.3 | 631.1 | 578.5 | 679.7 | 563.3 | 289.4 | 356 | 410.5 | 302.2 | 401.9 | 39.1 | 79.3 | 109 | 97.8 | 212 | 200.6 | 85.9 | 166.9 | 159.1 | 122.4
969.3 | 750.3 | 376.7 | 150.68 | 176.1362 | 202.4 | 183.1 | 202.9 | 204.8 | 283.8 | 32.4 | 21.1 | 58.7 | 7.3 | 226.5 | 6.7 | 714.1 | 634.7 | 577 | 678.3 | 563.3 | 289.6 | 355.3 | 410.8 | 301.8 | 401.8 | 39.1 | 79.3 | 109.2 | 97.9 | 212.8 | 201 | 86 | 167 | 159.2 | 122.6
970.3 | 751.3 | 375.6 | 150.24 | 175.6219 | 202 | 183.3 | 203.2 | 204.3 | 282.3 | 32.4 | 21.1 | 58.7 | 7.6 | 240.9 | 5.8 | 710.4 | 623.1 | 564.2 | 673.4 | 562 | 289.9 | 354 | 406.4 | 301.2 | 400.6 | 39.2 | 79.4 | 109.3 | 98 | 212.8 | 201.8 | 86.1 | 167.1 | 159.4 | 122.7
971.3 | 752.3 | 376.2 | 150.48 | 175.9024 | 201.5 | 183.7 | 203.4 | 204.3 | 280.4 | 32.4 | 21.1 | 58.6 | 7.3 | 238.7 | 4.7 | 708.1 | 623.1 | 569.5 | 670.3 | 562 | 290.1 | 352.4 | 406.5 | 300.3 | 400.6 | 39.3 | 79.5 | 109.4 | 98 | 213 | 202.3 | 86.2 | 167.2 | 159.5 | 122.9
972.3 | 753.3 | 376.2 | 150.48 | 175.9024 | 201.6 | 183.8 | 203.5 | 204.3 | 281.3 | 32.4 | 21.1 | 58.6 | 7.7 | 246.9 | 4 | 703.8 | 616.7 | 555.4 | 665.4 | 559.9 | 290.4 | 351.3 | 403.5 | 300.5 | 399.8 | 39.3 | 79.6 | 109.5 | 98.1 | 212.9 | 202.6 | 86.3 | 167.3 | 159.7 | 123
973.3 | 754.3 | 376.2 | 150.48 | 175.9024 | 201.2 | 184.5 | 203.9 | 205.1 | 279.1 | 32.4 | 21.1 | 58.7 | 7.4 | 244.1 | 4.3 | 702.7 | 621.7 | 550.6 | 661.8 | 559 | 290.6 | 348.8 | 403.4 | 298.9 | 398.8 | 39.4 | 79.7 | 109.6 | 98.2 | 212.9 | 202.5 | 86.4 | 167.4 | 159.8 | 123.2
974.3 | 755.3 | 376.3 | 150.52 | 175.9492 | 201.3 | 184.8 | 204.2 | 204.9 | 278.1 | 32.4 | 21.1 | 58.8 | 7.3 | 245.8 | 4.4 | 704 | 623 | 540.3 | 661.4 | 557.8 | 290.9 | 347.6 | 399.9 | 298.1 | 398 | 39.4 | 79.8 | 109.8 | 98.3 | 213 | 202.2 | 86.5 | 167.4 | 159.9 | 123.3
975.3 | 756.3 | 377.3 | 150.92 | 176.4168 | 202.3 | 184.2 | 204.8 | 203.7 | 277.4 | 32.5 | 21.1 | 58.9 | 6.7 | 251 | 4.1 | 705.4 | 626.2 | 544.7 | 662.2 | 557.7 | 291.2 | 347.7 | 402.3 | 298 | 398.1 | 39.5 | 79.9 | 110 | 98.4 | 213 | 202.4 | 86.6 | 167.6 | 160 | 123.5
976.3 | 757.3 | 377.1 | 150.84 | 176.3233 | 203.5 | 183.6 | 205 | 203.5 | 280 | 32.5 | 21.1 | 59 | 6.2 | 267.4 | 3.8 | 708.3 | 635.6 | 547.8 | 665.6 | 557.8 | 291.4 | 351.9 | 406.5 | 299.8 | 399.3 | 39.6 | 80 | 110.1 | 98.5 | 212.9 | 202.4 | 86.7 | 167.8 | 160.2 | 123.7
977.3 | 758.3 | 377.2 | 150.88 | 176.37 | 203.9 | 183.6 | 205.6 | 203.8 | 281.5 | 32.5 | 21.1 | 59 | 6.8 | 270.2 | 4 | 711.2 | 652.4 | 559.2 | 667.3 | 558.5 | 291.7 | 357.5 | 423.6 | 302.2 | 401 | 39.6 | 80.1 | 110.3 | 98.6 | 213.1 | 202.3 | 86.8 | 167.9 | 160.3 | 123.8
978.3 | 759.3 | 376.9 | 150.76 | 176.2298 | 204 | 183.4 | 206.8 | 204 | 285.2 | 32.5 | 21.1 | 59.1 | 7.4 | 253.9 | 4.5 | 713 | 654.9 | 572.4 | 670.3 | 559.9 | 291.9 | 362.1 | 429.5 | 304.3 | 402.3 | 39.7 | 80.1 | 110.4 | 98.7 | 213.3 | 202.1 | 86.9 | 167.9 | 160.5 | 123.9
979.3 | 760.3 | 375.7 | 150.28 | 175.6687 | 204 | 184.3 | 207.5 | 204.2 | 286 | 32.5 | 21.1 | 59.2 | 7 | 254.8 | 4.8 | 714.2 | 651.8 | 588.1 | 673.7 | 560.1 | 292.2 | 362.8 | 426.5 | 305 | 402.1 | 39.7 | 80.2 | 110.5 | 98.8 | 213.6 | 201.7 | 87 | 167.9 | 160.7 | 124
980.3 | 761.3 | 375.9 | 150.36 | 175.7622 | 202.9 | 185.3 | 207.8 | 204.3 | 288.9 | 32.4 | 21.1 | 59.2 | 6.8 | 253.5 | 4.8 | 719.7 | 662.5 | 593.2 | 682 | 560.8 | 292.4 | 368.5 | 432.8 | 307.6 | 404.3 | 39.8 | 80.3 | 110.6 | 98.9 | 213.8 | 201.6 | 87.1 | 168 | 160.9 | 124.1
981.3 | 762.3 | 376.2 | 150.48 | 175.9024 | 202 | 185.2 | 207.9 | 204.1 | 290.6 | 32.5 | 21.1 | 59.2 | 6.8 | 251.7 | 4.7 | 723.3 | 663.3 | 613.2 | 688.9 | 562 | 292.7 | 371.1 | 431.4 | 309.1 | 405.5 | 39.9 | 80.4 | 110.7 | 99 | 213.7 | 201.1 | 87.2 | 168.1 | 161.1 | 124.3
982.3 | 763.3 | 376.4 | 150.56 | 175.996 | 201.8 | 183.9 | 207.8 | 204.1 | 289.6 | 32.5 | 21.1 | 59.3 | 7 | 260.3 | 4.5 | 725.5 | 661.4 | 611.4 | 692.8 | 562.6 | 292.9 | 372 | 430.2 | 310.2 | 406 | 39.9 | 80.5 | 110.8 | 99.1 | 214.1 | 200.8 | 87.3 | 168.2 | 161.3 | 124.5
983.3 | 764.3 | 376.5 | 150.6 | 176.0427 | 202.2 | 183.4 | 207.5 | 204.3 | 288.2 | 32.5 | 21.1 | 59.3 | 6.9 | 264.3 | 4.7 | 724.7 | 660.4 | 614 | 692.3 | 560.7 | 293.2 | 369.2 | 422.9 | 308.8 | 404.9 | 40 | 80.6 | 111 | 99.2 | 213.9 | 200.8 | 87.4 | 168.3 | 161.5 | 124.6
984.3 | 765.3 | 376.7 | 150.68 | 176.1362 | 201.9 | 183 | 207.5 | 204.5 | 286.9 | 32.5 | 21.1 | 59.3 | 6.7 | 244.4 | 5.4 | 722.7 | 653.9 | 601.7 | 689.9 | 560 | 293.4 | 367.9 | 419.3 | 308.4 | 404.6 | 40.1 | 80.7 | 111.1 | 99.3 | 213.6 | 201.1 | 87.5 | 168.4 | 161.7 | 124.8
985.3 | 766.3 | 376.8 | 150.72 | 176.183 | 201.6 | 182.7 | 207.3 | 203.3 | 285.3 | 32.6 | 21.1 | 59.3 | 6.2 | 208.2 | 4.8 | 718.6 | 639.3 | 582.2 | 684.6 | 557.6 | 293.7 | 364.6 | 413.6 | 307.1 | 403 | 40.1 | 80.8 | 111.3 | 99.4 | 213.4 | 201.6 | 87.6 | 168.5 | 161.9 | 124.9
986.3 | 767.3 | 376.7 | 150.68 | 176.1362 | 201.7 | 183.1 | 207 | 202.9 | 283.9 | 32.6 | 21.1 | 59.2 | 5.6 | 223.6 | 3.8 | 714.8 | 633.5 | 573.8 | 679.1 | 556.5 | 294 | 360.7 | 408.8 | 305.1 | 401.7 | 40.2 | 80.9 | 111.4 | 99.5 | 213.2 | 202.1 | 87.7 | 168.6 | 162 | 125
987.3 | 768.3 | 375.2 | 150.08 | 175.4349 | 201.7 | 182.8 | 207.1 | 203.1 | 284.4 | 32.6 | 21.1 | 59.2 | 6.3 | 258.3 | 3.8 | 714.6 | 633.7 | 576.5 | 678.5 | 557.1 | 294.2 | 359.9 | 410.4 | 305 | 402.4 | 40.2 | 81 | 111.4 | 99.6 | 213.1 | 202.4 | 87.8 | 168.7 | 162.2 | 125.2
988.3 | 769.3 | 375.5 | 150.2 | 175.5751 | 202.1 | 183.4 | 207.4 | 202.7 | 286.3 | 32.7 | 21.1 | 59.2 | 6.9 | 238.4 | 4.3 | 714.6 | 632.3 | 569.3 | 677 | 556.3 | 294.5 | 360.1 | 409.1 | 305.4 | 402.7 | 40.3 | 81.2 | 111.5 | 99.7 | 213.2 | 202.6 | 87.9 | 168.8 | 162.3 | 125.3
989.3 | 770.3 | 376.2 | 150.48 | 175.9024 | 202.8 | 183.7 | 207.5 | 201.9 | 285.2 | 32.7 | 21.1 | 59.2 | 7.2 | 232.2 | 5.6 | 713.5 | 632.2 | 564.2 | 674 | 555 | 294.8 | 359.6 | 409.5 | 305.4 | 402.2 | 40.4 | 81.3 | 111.8 | 99.8 | 213.1 | 202.7 | 88 | 168.9 | 162.5 | 125.4
990.3 | 771.3 | 377.5 | 151 | 176.5103 | 203.8 | 183.5 | 208.1 | 201.1 | 285.9 | 32.8 | 21.1 | 59.2 | 7 | 241.8 | 6 | 718.3 | 650.4 | 596.3 | 679.7 | 558.5 | 295 | 362 | 424.4 | 306.9 | 404.1 | 40.4 | 81.4 | 111.9 | 99.9 | 212.6 | 202.4 | 88.1 | 168.9 | 162.7 | 125.6
991.3 | 772.3 | 377.7 | 151.08 | 176.6038 | 204.4 | 183 | 208.7 | 201.5 | 291 | 32.8 | 21.1 | 59.4 | 7.1 | 238 | 6.2 | 727.2 | 666.5 | 630.4 | 693.1 | 563.1 | 295.3 | 369 | 439.7 | 311.3 | 406.9 | 40.5 | 81.5 | 112.1 | 100 | 212.6 | 202.1 | 88.2 | 168.9 | 162.8 | 125.7
992.3 | 773.3 | 377.9 | 151.16 | 176.6973 | 203.6 | 183.2 | 209 | 202.3 | 296.1 | 32.9 | 21.1 | 59.6 | 7.6 | 240.9 | 6.2 | 734.2 | 683.4 | 660 | 703.3 | 567.2 | 295.6 | 379 | 464.6 | 315.8 | 410.7 | 40.5 | 81.6 | 112.3 | 100.1 | 212.3 | 202.2 | 88.3 | 169 | 163.1 | 125.8
993.3 | 774.3 | 377.7 | 151.08 | 176.6038 | 203.4 | 183.1 | 209.2 | 202.8 | 308.2 | 33 | 21.1 | 59.8 | 7.3 | 243.9 | 6.1 | 741.3 | 702.9 | 695.2 | 715 | 572.1 | 295.8 | 389.5 | 496.2 | 321.3 | 414.8 | 40.6 | 81.7 | 112.3 | 100.2 | 212.5 | 201.5 | 88.4 | 169.1 | 163.4 | 126
994.3 | 775.3 | 377.7 | 151.08 | 176.6038 | 202.7 | 183.7 | 209.1 | 203.3 | 315.6 | 33.1 | 21 | 59.9 | 6.3 | 236 | 6.4 | 746.8 | 710.3 | 716.9 | 723.3 | 576.6 | 296.1 | 397.2 | 508.1 | 326.2 | 419.5 | 40.7 | 81.8 | 112.6 | 100.3 | 212.8 | 201.2 | 88.5 | 169.2 | 163.6 | 126.1
995.3 | 776.3 | 377.5 | 151 | 176.5103 | 202.7 | 184.4 | 209.2 | 203.8 | 315.3 | 33.1 | 21 | 60.1 | 7 | 236.7 | 6.5 | 750.3 | 700.7 | 720.4 | 731.4 | 578.1 | 296.4 | 400.9 | 497.6 | 328.6 | 422 | 40.7 | 81.9 | 112.7 | 100.4 | 213.6 | 201.3 | 88.6 | 169.3 | 164 | 126.2
996.3 | 777.3 | 377.7 | 151.08 | 176.6038 | 202.9 | 185.2 | 209.6 | 204.5 | 310.2 | 33.2 | 21.1 | 60.2 | 7.1 | 243.4 | 7 | 750.8 | 695.4 | 711.4 | 733.6 | 578.6 | 296.7 | 400.2 | 494.4 | 330 | 422.7 | 40.8 | 82 | 113 | 100.5 | 214.3 | 201.8 | 88.7 | 169.4 | 164.3 | 126.4
997.3 | 778.3 | 378.2 | 151.28 | 176.8376 | 202.9 | 185.2 | 209.7 | 205 | 310.2 | 33.3 | 21 | 60.2 | 6.1 | 245.9 | 7.8 | 750.5 | 701.5 | 707.6 | 732.1 | 580.4 | 297 | 401 | 500.9 | 330.6 | 423.5 | 40.9 | 82.1 | 113 | 100.6 | 214 | 202 | 88.8 | 169.4 | 164.5 | 126.6
998.3 | 779.3 | 375.2 | 150.08 | 175.4349 | 201.8 | 185.6 | 209.8 | 205.4 | 309.9 | 33.4 | 21 | 60.1 | 6.4 | 254.6 | 7.5 | 748.9 | 699.6 | 705.8 | 730.1 | 580.2 | 297.2 | 401.3 | 494.8 | 331.4 | 425.2 | 40.9 | 82.2 | 113.1 | 100.7 | 213.8 | 201.7 | 88.9 | 169.5 | 164.8 | 126.7
999.3 | 780.3 | 374.4 | 149.76 | 175.0608 | 201.1 | 185.5 | 209 | 205.5 | 309 | 33.4 | 21 | 60.1 | 6.7 | 265.2 | 6.8 | 752.2 | 709.9 | 711.3 | 733.7 | 582.3 | 297.5 | 403.3 | 489.9 | 332.4 | 427.1 | 41 | 82.3 | 113.3 | 100.8 | 214 | 202.6 | 89 | 169.6 | 165 | 126.9
1000.3 | 781.3 | 374.9 | 149.96 | 175.2946 | 200.9 | 185.1 | 206.6 | 205.7 | 307.7 | 33.5 | 21 | 60 | 7.8 | 259.6 | 7.5 | 754.4 | 713.7 | 708.2 | 734 | 583.6 | 297.8 | 404.7 | 487.7 | 333.3 | 428.4 | 41 | 82.4 | 113.4 | 100.9 | 214.4 | 202.6 | 89.1 | 169.8 | 165.2 | 127
1001.3 | 782.3 | 376 | 150.4 | 175.8089 | 200.9 | 185.3 | 205.7 | 205.5 | 306.5 | 33.5 | 21 | 60.1 | 8.1 | 259.2 | 6.9 | 757.8 | 718.8 | 708.7 | 737 | 585.6 | 298.1 | 407.7 | 485.4 | 335.3 | 431 | 41.1 | 82.5 | 113.4 | 101 | 214.1 | 202.5 | 89.2 | 169.9 | 165.5 | 127.2
1002.3 | 783.3 | 376.1 | 150.44 | 175.8557 | 201 | 186.2 | 205 | 205.9 | 304.2 | 33.5 | 21 | 60.1 | 8.6 | 280.4 | 6.6 | 756 | 697.3 | 686.5 | 734.6 | 583 | 298.4 | 404.2 | 474.6 | 333.9 | 429.2 | 41.2 | 82.6 | 113.5 | 101.1 | 214.1 | 202.2 | 89.3 | 170.1 | 165.7 | 127.3
1003.3 | 784.3 | 375.6 | 150.24 | 175.6219 | 203.2 | 186.8 | 204.7 | 206.4 | 302.3 | 33.5 | 21 | 60.2 | 8.1 | 281.8 | 7.1 | 751.7 | 682.3 | 659.5 | 729.7 | 581.1 | 298.7 | 399.4 | 460.8 | 332 | 428.2 | 41.2 | 82.7 | 113.6 | 101.2 | 213.8 | 202.2 | 89.4 | 170.2 | 165.9 | 127.4
1004.3 | 785.3 | 376.5 | 150.6 | 176.0427 | 204.6 | 187.2 | 205.2 | 206.9 | 296.4 | 33.5 | 21 | 60.3 | 7.2 | 274.6 | 6.9 | 746.5 | 662.2 | 640.9 | 724 | 578.8 | 299 | 393.1 | 448.4 | 329.3 | 425.9 | 41.3 | 82.8 | 113.7 | 101.3 | 213.8 | 202.4 | 89.5 | 170.3 | 166.1 | 127.6
1005.3 | 786.3 | 377.8 | 151.12 | 176.6506 | 204.3 | 186.8 | 205.8 | 206.6 | 291.9 | 33.4 | 21 | 60.3 | 8 | 271.7 | 8.7 | 744.5 | 654.5 | 625.9 | 720.7 | 577.1 | 299.3 | 388.6 | 442.2 | 326.8 | 424.6 | 41.3 | 82.9 | 113.8 | 101.4 | 213.2 | 202.9 | 89.6 | 170.4 | 166.3 | 127.7
1006.3 | 787.3 | 377.7 | 151.08 | 176.6038 | 203.1 | 186.6 | 206.3 | 206.5 | 289.8 | 33.4 | 21 | 60.3 | 8 | 266.3 | 9.8 | 744.7 | 654.8 | 624.4 | 722.3 | 577.5 | 299.7 | 387 | 436.7 | 325.8 | 424.6 | 41.4 | 83 | 113.9 | 101.5 | 212.9 | 203.1 | 89.6 | 170.4 | 166.4 | 127.8
1007.3 | 788.3 | 378.1 | 151.24 | 176.7908 | 202.7 | 186.2 | 206.8 | 205.8 | 288.7 | 33.4 | 21 | 60.4 | 7.9 | 277.3 | 10.4 | 746.5 | 665.2 | 630.2 | 725 | 577.7 | 300 | 386.2 | 433.7 | 325.8 | 425.1 | 41.5 | 83.1 | 114.2 | 101.6 | 212.3 | 203.4 | 89.8 | 170.6 | 166.5 | 127.9
1008.3 | 789.3 | 378.5 | 151.4 | 176.9779 | 202.7 | 186.1 | 206.8 | 205.1 | 290.5 | 33.4 | 21 | 60.4 | 7.3 | 278.2 | 10.7 | 748.2 | 672.8 | 634.5 | 724.2 | 577.3 | 300.2 | 385.8 | 436.9 | 325.8 | 425.3 | 41.5 | 83.2 | 114.3 | 101.7 | 212.2 | 203.1 | 89.9 | 170.7 | 166.7 | 128.1
1009.3 | 790.3 | 375.8 | 150.32 | 175.7154 | 202.4 | 186 | 206.7 | 205.4 | 292.8 | 33.4 | 21 | 60.5 | 7.6 | 275.3 | 10.3 | 748.7 | 675.2 | 637.4 | 723.9 | 577 | 300.5 | 385.4 | 437.2 | 325.1 | 425.6 | 41.6 | 83.3 | 114.4 | 101.8 | 211.9 | 202.5 | 90 | 170.8 | 166.9 | 128.2
1010.3 | 791.3 | 375.9 | 150.36 | 175.7622 | 202.3 | 186.8 | 206.9 | 205.7 | 293 | 33.4 | 21 | 60.6 | 7.5 | 276.8 | 9.7 | 748.2 | 665.7 | 625.5 | 722 | 575.5 | 300.7 | 384 | 431.7 | 324.7 | 424.9 | 41.7 | 83.4 | 114.4 | 101.9 | 211.4 | 202.1 | 90.1 | 170.8 | 167.1 | 128.4
1011.3 | 792.3 | 376.1 | 150.44 | 175.8557 | 202.1 | 187.3 | 206.8 | 204.8 | 289.7 | 33.3 | 21 | 60.6 | 7.6 | 277.3 | 9.2 | 748 | 657.7 | 622.1 | 720.6 | 574.4 | 301 | 381 | 428.6 | 323.1 | 423.7 | 41.7 | 83.4 | 114.6 | 102 | 210.9 | 201.9 | 90.1 | 170.9 | 167.4 | 128.5
1012.3 | 793.3 | 376.2 | 150.48 | 175.9024 | 201.8 | 187.6 | 206.5 | 204.7 | 287.9 | 33.3 | 21 | 60.7 | 7.8 | 288.6 | 9.4 | 746.8 | 660.3 | 616.8 | 719.6 | 573.8 | 301.4 | 378.9 | 429.1 | 322 | 423.2 | 41.8 | 83.5 | 114.8 | 102.1 | 210.5 | 202.2 | 90.3 | 171 | 167.5 | 128.6
1013.3 | 794.3 | 376.5 | 150.6 | 176.0427 | 201 | 187.2 | 205.8 | 204.7 | 289 | 33.3 | 21 | 60.7 | 7.7 | 276.4 | 9.2 | 745.3 | 662.8 | 610.1 | 718.7 | 572.1 | 301.7 | 377.2 | 434.2 | 321.2 | 423 | 41.9 | 83.6 | 114.9 | 102.2 | 210.5 | 202.1 | 90.4 | 171 | 167.6 | 128.7
1014.3 | 795.3 | 376.6 | 150.64 | 176.0895 | 200.5 | 187.1 | 205.8 | 205 | 287.9 | 33.3 | 21 | 60.7 | 7 | 285.8 | 8.1 | 741.5 | 650.3 | 598.7 | 713.6 | 571.3 | 302.1 | 373.2 | 426.9 | 319.4 | 421.2 | 41.9 | 83.7 | 114.9 | 102.3 | 210.3 | 201.9 | 90.5 | 171.1 | 167.8 | 128.8
1015.3 | 796.3 | 376.7 | 150.68 | 176.1362 | 200 | 186.8 | 205.5 | 205.2 | 288.2 | 33.2 | 21 | 60.7 | 6.7 | 283.3 | 7.9 | 736.6 | 634.1 | 580.1 | 706.5 | 568.5 | 302.4 | 369.2 | 418.9 | 317.5 | 419.4 | 42 | 83.8 | 115.1 | 102.4 | 210.3 | 201.5 | 90.5 | 171.1 | 168 | 128.9
1016.3 | 797.3 | 376.4 | 150.56 | 175.996 | 200.5 | 186.5 | 205.8 | 205 | 286.1 | 33.1 | 21 | 60.7 | 7.4 | 274.8 | 7.9 | 732.5 | 626.3 | 570.5 | 700.2 | 567.2 | 302.7 | 365.3 | 410.5 | 315.6 | 418.1 | 42 | 84 | 115.2 | 102.5 | 210.1 | 201.3 | 90.6 | 171.2 | 168.1 | 129
1017.3 | 798.3 | 375.4 | 150.16 | 175.5284 | 202.3 | 186.3 | 206.5 | 204.7 | 284.3 | 33.1 | 21 | 60.7 | 7 | 278 | 8.7 | 731.2 | 631.3 | 563.8 | 698.1 | 566.7 | 303.1 | 362 | 415.3 | 314 | 417.5 | 42.1 | 84.1 | 115.3 | 102.6 | 210.1 | 201 | 90.7 | 171.3 | 168.2 | 129.2
1018.3 | 799.3 | 376.5 | 150.6 | 176.0427 | 203.9 | 185.8 | 206.5 | 204.1 | 286.5 | 33 | 21 | 60.7 | 6 | 274.4 | 8.4 | 727.7 | 615.9 | 554 | 692.7 | 564.3 | 303.4 | 359.6 | 410.7 | 312.6 | 416.1 | 42.2 | 84.2 | 115.5 | 102.7 | 210.2 | 200.9 | 90.8 | 171.4 | 168.3 | 129.3
1019.3 | 800.3 | 376.3 | 150.52 | 175.9492 | 204.1 | 185.1 | 206.9 | 204.5 | 284.6 | 33 | 21 | 60.7 | 6.1 | 261.6 | 7.9 | 723.1 | 601 | 543 | 685.5 | 562.1 | 303.7 | 356.1 | 403.9 | 310.6 | 414.5 | 42.2 | 84.3 | 115.5 | 102.8 | 210.5 | 201 | 90.9 | 171.4 | 168.4 | 129.4
1020.3 | 801.3 | 374.7 | 149.88 | 175.2011 | 204.1 | 185 | 206.4 | 204.3 | 282.1 | 33 | 21 | 60.7 | 6.7 | 262.5 | 7.6 | 723.4 | 611.4 | 552 | 685.3 | 562.5 | 304 | 357.9 | 408.3 | 311.4 | 416.1 | 42.3 | 84.4 | 115.9 | 102.9 | 210.2 | 201.1 | 91 | 171.6 | 168.6 | 129.6
1021.3 | 802.3 | 375.4 | 150.16 | 175.5284 | 204.5 | 185.3 | 205.7 | 204.6 | 283.1 | 32.9 | 21 | 60.7 | 6.8 | 277.1 | 6.9 | 721.6 | 613.5 | 566.2 | 683.8 | 563.4 | 304.4 | 360.9 | 413.6 | 313.3 | 417.3 | 42.4 | 84.5 | 116.3 | 103 | 210 | 200.8 | 91.1 | 171.6 | 168.8 | 129.7
1022.3 | 803.3 | 375.9 | 150.36 | 175.7622 | 204.8 | 185 | 205.4 | 203.9 | 282.8 | 32.9 | 21 | 60.7 | 6.8 | 269.9 | 6.9 | 720.9 | 616.2 | 579.8 | 682.8 | 562.6 | 304.7 | 363.8 | 414.9 | 315.3 | 418.6 | 42.4 | 84.7 | 116.2 | 103.1 | 210.2 | 200.8 | 91.2 | 171.7 | 169 | 129.8
1023.3 | 804.3 | 378 | 151.2 | 176.7441 | 204.2 | 183.9 | 205.6 | 203.6 | 283.8 | 32.9 | 21 | 60.7 | 7.1 | 259 | 7 | 719.9 | 619.2 | 585.5 | 679.9 | 563.3 | 305 | 363.2 | 410 | 314.6 | 417.5 | 42.5 | 84.8 | 116.1 | 103.1 | 210 | 200.7 | 91.3 | 171.7 | 169.2 | 129.9
1024.3 | 805.3 | 378.1 | 151.24 | 176.7908 | 202.9 | 183.8 | 205.2 | 203.7 | 283.2 | 33 | 21 | 60.7 | 7.2 | 254.2 | 6.4 | 717.7 | 612.2 | 576.5 | 676.2 | 562.3 | 305.3 | 360.9 | 403.8 | 313 | 416 | 42.6 | 84.9 | 116.1 | 103.2 | 209.8 | 200.4 | 91.4 | 171.8 | 169.4 | 130
1025.3 | 806.3 | 378 | 151.2 | 176.7441 | 201.9 | 184.6 | 204.6 | 202.7 | 281.3 | 33 | 21 | 60.7 | 6.3 | 250.5 | 5.9 | 717 | 610.1 | 574.9 | 674.9 | 563 | 305.6 | 359.4 | 406.1 | 312.2 | 415.8 | 42.6 | 85 | 116.1 | 103.3 | 209.4 | 200.7 | 91.5 | 171.9 | 169.6 | 130.1
1026.3 | 807.3 | 377.9 | 151.16 | 176.6973 | 202.1 | 184.7 | 203.8 | 202.2 | 282.1 | 33.1 | 21 | 60.6 | 7.6 | 244.5 | 5.2 | 713.3 | 600.1 | 568.6 | 670 | 561.4 | 305.9 | 356.9 | 399.6 | 311.2 | 414.7 | 42.7 | 85.1 | 116.3 | 103.4 | 210 | 200.9 | 91.6 | 172 | 169.7 | 130.2
1027.3 | 808.3 | 377.8 | 151.12 | 176.6506 | 202.7 | 184.5 | 203 | 202.6 | 279.2 | 33.1 | 21 | 60.6 | 6.6 | 235.6 | 5 | 712.4 | 602 | 571.2 | 668.1 | 561.5 | 306.2 | 354.7 | 397.8 | 310.2 | 414.4 | 42.7 | 85.2 | 116.4 | 103.5 | 210.4 | 200.7 | 91.7 | 172.1 | 169.8 | 130.4
1028.3 | 809.3 | 377.8 | 151.12 | 176.6506 | 203.8 | 183.8 | 202.5 | 202.3 | 278.6 | 33.2 | 21 | 60.6 | 7.3 | 242.1 | 4.2 | 714.7 | 619.2 | 582.8 | 669.9 | 561.6 | 306.4 | 355.8 | 406.5 | 310.4 | 414.8 | 42.8 | 85.3 | 116.5 | 103.5 | 210.3 | 200.7 | 91.8 | 172.1 | 170 | 130.5
1029.3 | 810.3 | 377.5 | 151 | 176.5103 | 205.3 | 182.9 | 202.3 | 201.6 | 281.4 | 33.3 | 21 | 60.7 | 7.7 | 246.7 | 3.8 | 718.1 | 629.4 | 607.1 | 675.6 | 565.1 | 306.7 | 358.8 | 413.4 | 311.6 | 415.9 | 42.9 | 85.4 | 116.9 | 103.6 | 209.9 | 200.8 | 91.9 | 172.1 | 170.1 | 130.7
1030.3 | 811.3 | 377.6 | 151.04 | 176.5571 | 206.3 | 182.6 | 202.4 | 201.5 | 286.2 | 33.4 | 21 | 60.7 | 7.4 | 260.4 | 5.1 | 722 | 645.8 | 644.8 | 682.3 | 568.6 | 307 | 366.4 | 428.7 | 315.5 | 419.7 | 42.9 | 85.5 | 117 | 103.7 | 209.5 | 201 | 92 | 172.2 | 170.2 | 130.8
1031.3 | 812.3 | 377.3 | 150.92 | 176.4168 | 205.8 | 182.6 | 201.6 | 202.5 | 288.7 | 33.4 | 21 | 60.8 | 7.8 | 251 | 8 | 722.7 | 634.7 | 642.4 | 686.7 | 572.9 | 307.3 | 373.4 | 429.9 | 319.7 | 423 | 43 | 85.6 | 117 | 103.8 | 209.2 | 200.9 | 92.1 | 172.3 | 170.4 | 130.9
1032.3 | 813.3 | 377.5 | 151 | 176.5103 | 204.7 | 182.9 | 201.2 | 203.1 | 288 | 33.5 | 21 | 60.8 | 7.9 | 250 | 9.2 | 722.6 | 630.7 | 640.5 | 687.2 | 572.1 | 307.6 | 371.3 | 422.2 | 319.1 | 421 | 43.1 | 85.7 | 117 | 103.9 | 210.1 | 200.8 | 92.2 | 172.4 | 170.8 | 131
1033.3 | 814.3 | 377.4 | 150.96 | 176.4635 | 203.1 | 183.5 | 201.2 | 204.3 | 285.1 | 33.6 | 21 | 60.9 | 7.7 | 270.9 | 9.4 | 720.7 | 618.5 | 639.8 | 684.8 | 570.9 | 307.9 | 368.5 | 413.8 | 317.9 | 419.3 | 43.1 | 85.8 | 117.1 | 103.9 | 210.1 | 200.9 | 92.3 | 172.4 | 171 | 131.2
1034.3 | 815.3 | 377.5 | 151 | 176.5103 | 202.5 | 184.5 | 201.6 | 204.3 | 282.6 | 33.8 | 21 | 61 | 7.8 | 265.9 | 9.7 | 719.2 | 614.1 | 635.5 | 682.9 | 570.4 | 308.2 | 365.9 | 407.7 | 316.4 | 418.8 | 43.2 | 85.9 | 117.2 | 104 | 210.5 | 201.2 | 92.4 | 172.5 | 171.2 | 131.3
1035.3 | 816.3 | 376.5 | 150.6 | 176.0427 | 202.1 | 185.2 | 202.7 | 203.8 | 280 | 33.9 | 21 | 61.1 | 9.1 | 285.3 | 10 | 718.6 | 623.1 | 626.2 | 682.6 | 569.7 | 308.5 | 365.9 | 410.6 | 316.4 | 418.2 | 43.3 | 86 | 117.3 | 104.1 | 210.1 | 201.2 | 92.5 | 172.6 | 171.3 | 131.4
1036.3 | 817.3 | 377.3 | 150.92 | 176.4168 | 201.3 | 184.8 | 203.5 | 203.6 | 279.2 | 33.9 | 21 | 61.1 | 9.6 | 267.9 | 11 | 717.5 | 627.1 | 631.1 | 681.1 | 569.8 | 308.7 | 364.2 | 407.1 | 315.9 | 417.9 | 43.3 | 86.1 | 117.4 | 104.2 | 210.2 | 201.8 | 92.6 | 172.7 | 171.5 | 131.5
1037.3 | 818.3 | 377.9 | 151.16 | 176.6973 | 200.6 | 185 | 203.8 | 203.1 | 280.3 | 34 | 21 | 61.1 | 8.5 | 261.8 | 11 | 717.3 | 635.1 | 638.8 | 681 | 570 | 309 | 364.1 | 406.7 | 315.4 | 417.4 | 43.4 | 86.2 | 117.7 | 104.3 | 210.1 | 202.6 | 92.7 | 172.9 | 171.6 | 131.7
1038.3 | 819.3 | 376.2 | 150.48 | 175.9024 | 201.7 | 184.7 | 204.6 | 203 | 281 | 34 | 21 | 61 | 9.2 | 272 | 10 | 717.5 | 631 | 635.7 | 681.5 | 570.9 | 309.3 | 365 | 411.5 | 315.6 | 417.4 | 43.5 | 86.3 | 117.8 | 104.3 | 210 | 202.8 | 92.8 | 173 | 171.7 | 131.8
1039.3 | 820.3 | 376.5 | 150.6 | 176.0427 | 201.8 | 183.9 | 204.6 | 202.2 | 281.9 | 34 | 21 | 61.1 | 9.4 | 264.4 | 10.2 | 714 | 618.9 | 622.6 | 678.1 | 568.6 | 309.6 | 362.1 | 404.7 | 314 | 415.7 | 43.5 | 86.4 | 117.8 | 104.4 | 209.7 | 202.5 | 92.9 | 173 | 171.9 | 132
1040.3 | 821.3 | 377.7 | 151.08 | 176.6038 | 202.6 | 183.5 | 204.9 | 202.5 | 281.3 | 33.9 | 21 | 61.1 | 9.7 | 264.2 | 10.6 | 714.3 | 631.4 | 619.7 | 678.4 | 568 | 309.8 | 360.8 | 403.5 | 312.7 | 415 | 43.6 | 86.4 | 117.8 | 104.5 | 209.9 | 202.2 | 93 | 173 | 172 | 132.1
1041.3 | 822.3 | 377.9 | 151.16 | 176.6973 | 203.1 | 183.4 | 205.3 | 203.1 | 281.6 | 33.9 | 21 | 61.2 | 10.3 | 265 | 11.8 | 713 | 615.2 | 606.2 | 677.1 | 567 | 310.1 | 360 | 400.2 | 312.3 | 414.2 | 43.7 | 86.5 | 118 | 104.6 | 209.9 | 202.3 | 93 | 173.1 | 172 | 132.2
1042.3 | 823.3 | 378.3 | 151.32 | 176.8844 | 205.7 | 182.2 | 204.6 | 202.9 | 279.5 | 33.9 | 21 | 61.2 | 10.5 | 244.1 | 11.3 | 710.7 | 604.3 | 601.2 | 675.2 | 565.5 | 310.4 | 357.2 | 393.4 | 310.7 | 412.9 | 43.7 | 86.6 | 118.1 | 104.7 | 210 | 202.2 | 93.1 | 173.3 | 172.2 | 132.3
1043.3 | 824.3 | 378.4 | 151.36 | 176.9311 | 206.9 | 181.8 | 204.2 | 203 | 278 | 33.9 | 21 | 61.3 | 11.3 | 266.7 | 14.2 | 709.1 | 592.1 | 590.8 | 673.6 | 565.2 | 310.7 | 355.5 | 391.7 | 309.9 | 412.3 | 43.8 | 86.7 | 118.3 | 104.8 | 209.9 | 202.3 | 93.3 | 173.4 | 172.4 | 132.4
1044.3 | 825.3 | 378.5 | 151.4 | 176.9779 | 207.1 | 182 | 204.1 | 203.5 | 275 | 33.8 | 21 | 61.3 | 11.4 | 253.6 | 13.3 | 704.2 | 575.1 | 568.6 | 668.5 | 562.2 | 310.9 | 351.3 | 384.3 | 307.9 | 410.3 | 43.9 | 86.8 | 118.5 | 104.9 | 210.1 | 202.2 | 93.4 | 173.5 | 172.5 | 132.5
1045.3 | 826.3 | 378.1 | 151.24 | 176.7908 | 207.2 | 181.3 | 204.2 | 203.4 | 272.5 | 33.7 | 21 | 61.4 | 10.4 | 252.7 | 14.7 | 699.6 | 566.6 | 555.4 | 662.7 | 560.1 | 311.2 | 347.5 | 380.4 | 305.8 | 408.8 | 43.9 | 86.9 | 118.5 | 105 | 210.3 | 202.4 | 93.4 | 173.7 | 172.6 | 132.7
1046.3 | 827.3 | 378.1 | 151.24 | 176.7908 | 207 | 181.4 | 204.2 | 203.3 | 271.6 | 33.5 | 21 | 61.6 | 10.2 | 236 | 14.2 | 695.1 | 551.9 | 539.3 | 657.1 | 558 | 311.5 | 344.5 | 374.7 | 304.7 | 407.4 | 44 | 87 | 118.6 | 105.1 | 211 | 202.3 | 93.5 | 173.8 | 172.7 | 132.8
1047.3 | 828.3 | 378 | 151.2 | 176.7441 | 206.4 | 182.5 | 203.7 | 203.5 | 270.3 | 33.5 | 21 | 61.7 | 9.6 | 247.9 | 14.4 | 690.2 | 547.7 | 538.3 | 650.5 | 556.5 | 311.8 | 341.2 | 368.4 | 303.1 | 405.7 | 44 | 87.1 | 118.6 | 105.1 | 211.2 | 202.5 | 93.6 | 174 | 172.8 | 132.9
1048.3 | 829.3 | 378.2 | 151.28 | 176.8376 | 206.6 | 182.8 | 203.5 | 203.8 | 268.3 | 33.4 | 21 | 61.7 | 7.7 | 239.2 | 15.3 | 689.4 | 552 | 550.1 | 648.3 | 557 | 312 | 340.8 | 367.2 | 302.8 | 405.5 | 44.1 | 87.2 | 118.8 | 105.2 | 211 | 202.5 | 93.7 | 174 | 172.8 | 133.1
1049.3 | 830.3 | 378.1 | 151.24 | 176.7908 | 206.9 | 183.8 | 203.2 | 204.2 | 267 | 33.4 | 21 | 61.8 | 8.2 | 250 | 16.5 | 691.1 | 558.3 | 570.7 | 649.8 | 558.6 | 312.3 | 341.9 | 374.5 | 303.5 | 406.4 | 44.2 | 87.3 | 118.8 | 105.3 | 210.9 | 203 | 93.8 | 174.2 | 173 | 133.2
1050.3 | 831.3 | 378.7 | 151.48 | 177.0714 | 205.8 | 184.5 | 202.5 | 204.1 | 268.6 | 33.4 | 21 | 61.9 | 8.7 | 241.7 | 18.5 | 691.5 | 558.8 | 573.1 | 650.1 | 559.1 | 312.6 | 344.4 | 374.3 | 304.8 | 406.9 | 44.2 | 87.4 | 118.8 | 105.4 | 210.8 | 203.2 | 93.9 | 174.3 | 173.1 | 133.3
1051.3 | 832.3 | 379.9 | 151.96 | 177.6325 | 205.6 | 184.4 | 201.8 | 203.8 | 268.3 | 33.3 | 21 | 61.9 | 10.5 | 239.8 | 19.8 | 689.7 | 549.6 | 561.3 | 649 | 557.3 | 312.9 | 343.4 | 368.9 | 304.4 | 405.7 | 44.3 | 87.5 | 118.9 | 105.5 | 210.9 | 203.3 | 94 | 174.4 | 173.3 | 133.4
1052.3 | 833.3 | 379 | 151.6 | 177.2117 | 205.6 | 183.5 | 201.5 | 204.5 | 266.8 | 33.4 | 21 | 62 | 11.9 | 244.5 | 15.1 | 688.7 | 553.2 | 564.4 | 648.7 | 557.4 | 313.1 | 343.1 | 366.9 | 304.1 | 405.4 | 44.4 | 87.6 | 119.1 | 105.6 | 210.6 | 203.1 | 94.1 | 174.5 | 173.5 | 133.6
1053.3 | 834.3 | 379.3 | 151.72 | 177.3519 | 205.3 | 182.8 | 202 | 204.6 | 265.8 | 33.4 | 21 | 62.1 | 12.2 | 229.7 | 11.4 | 688.1 | 555.8 | 568.8 | 649.5 | 556.5 | 313.4 | 342.5 | 364.4 | 303.6 | 404.6 | 44.4 | 87.7 | 119.1 | 105.7 | 210.8 | 202.9 | 94.2 | 174.6 | 173.6 | 133.7
1054.3 | 835.3 | 378.9 | 151.56 | 177.1649 | 205.3 | 182.8 | 202.2 | 203.7 | 264 | 33.4 | 21 | 62.2 | 11.7 | 260.8 | 10.6 | 686.5 | 556.8 | 563 | 648.9 | 555.7 | 313.6 | 341.5 | 363.6 | 302.7 | 403.7 | 44.5 | 87.7 | 119.3 | 105.8 | 210.7 | 202.8 | 94.3 | 174.7 | 173.8 | 133.8
1055.3 | 836.3 | 378.3 | 151.32 | 176.8844 | 205.1 | 182.8 | 202.4 | 203.7 | 263.3 | 33.4 | 21 | 62.2 | 11.2 | 267.4 | 13.4 | 683.4 | 549.1 | 545 | 644.8 | 553.2 | 313.9 | 338.3 | 359.8 | 301.1 | 402.2 | 44.6 | 87.8 | 119.5 | 105.9 | 210.8 | 203.1 | 94.4 | 174.8 | 173.9 | 133.9
1056.3 | 837.3 | 376.5 | 150.6 | 176.0427 | 204.7 | 182.9 | 203.4 | 204.4 | 262 | 33.4 | 21 | 62.3 | 12.9 | 259.8 | 16.4 | 680.4 | 537.1 | 535.2 | 639.8 | 551.7 | 314.1 | 335 | 355.4 | 299.4 | 400.7 | 44.6 | 87.9 | 119.4 | 106 | 211.6 | 204.1 | 94.5 | 174.9 | 174 | 134.1
1057.3 | 838.3 | 376.5 | 150.6 | 176.0427 | 205.5 | 183.6 | 203.8 | 204.7 | 261.2 | 33.4 | 21 | 62.2 | 11 | 258.2 | 14.6 | 677.8 | 532.9 | 525.2 | 636.4 | 551.1 | 314.4 | 333.6 | 355.6 | 298.6 | 400.2 | 44.7 | 88 | 119.5 | 106.1 | 211.4 | 204.5 | 94.6 | 175.1 | 174.1 | 134.2
1058.3 | 839.3 | 376.7 | 150.68 | 176.1362 | 207.1 | 183.9 | 204 | 205.4 | 261.6 | 33.4 | 21 | 62.1 | 9.3 | 245.8 | 15.2 | 675.5 | 532.7 | 524.4 | 635 | 550.3 | 314.6 | 332.1 | 353.4 | 297.6 | 399.5 | 44.7 | 88.1 | 119.6 | 106.2 | 211.5 | 204.7 | 94.7 | 175.2 | 174.2 | 134.4
1059.3 | 840.3 | 376.2 | 150.48 | 175.9024 | 208.1 | 182.9 | 204.3 | 205.9 | 261.9 | 33.5 | 21 | 62 | 9.1 | 240.9 | 13.7 | 674.3 | 537.3 | 525.1 | 633.3 | 549.3 | 314.8 | 331.1 | 354.5 | 297.4 | 399.2 | 44.8 | 88.2 | 119.7 | 106.3 | 211.9 | 204.5 | 94.8 | 175.2 | 174.3 | 134.5
1060.3 | 841.3 | 375.3 | 150.12 | 175.4816 | 208.4 | 182.6 | 204 | 206.1 | 263.7 | 33.6 | 21 | 62 | 9.8 | 241.3 | 12.4 | 674.9 | 549.6 | 536.3 | 634.2 | 549.8 | 315.1 | 334.7 | 361.9 | 298.4 | 399.9 | 44.9 | 88.3 | 119.8 | 106.4 | 211.9 | 204.6 | 94.9 | 175.3 | 174.3 | 134.6
1061.3 | 842.3 | 377.4 | 150.96 | 176.4635 | 208.5 | 182.3 | 203.9 | 206.7 | 265.2 | 33.7 | 21 | 62 | 9.8 | 233.4 | 12.5 | 676.1 | 562.8 | 551.6 | 634.7 | 549.7 | 315.3 | 335.9 | 363.7 | 298.9 | 399.8 | 44.9 | 88.4 | 120.1 | 106.4 | 212.1 | 204.7 | 95 | 175.4 | 174.4 | 134.7
1062.3 | 843.3 | 378.3 | 151.32 | 176.8844 | 209.1 | 181.8 | 203.7 | 206.7 | 265.6 | 33.7 | 21 | 62 | 10.5 | 246.8 | 12.7 | 678.2 | 571.8 | 557.4 | 637.7 | 550.5 | 315.5 | 337.8 | 363.3 | 299.6 | 400 | 45 | 88.4 | 120.2 | 106.5 | 212.2 | 205.1 | 95.1 | 175.4 | 174.6 | 134.8
1063.3 | 844.3 | 376.9 | 150.76 | 176.2298 | 209.1 | 181.3 | 203.9 | 207.2 | 267 | 33.7 | 21 | 62.1 | 9.5 | 223.9 | 12.1 | 679.9 | 586.7 | 558.2 | 639.8 | 549 | 315.8 | 339.1 | 368.4 | 299.8 | 399.8 | 45.1 | 88.5 | 120.2 | 106.6 | 212.8 | 205.5 | 95.2 | 175.5 | 174.7 | 134.9
1064.3 | 845.3 | 376.3 | 150.52 | 175.9492 | 209 | 181.3 | 203.9 | 207 | 269.7 | 33.6 | 21 | 62.1 | 8 | 241.2 | 10.6 | 681.8 | 594.8 | 567.6 | 640.9 | 549 | 316 | 338.9 | 372.4 | 299.9 | 399.5 | 45.1 | 88.6 | 120.3 | 106.7 | 213 | 205.8 | 95.3 | 175.5 | 174.8 | 135.1
1065.3 | 846.3 | 375.6 | 150.24 | 175.6219 | 208.2 | 181 | 204.5 | 206.9 | 269.2 | 33.6 | 21 | 62 | 10.2 | 229.2 | 10.4 | 682.7 | 603.2 | 589.9 | 641.9 | 550.8 | 316.2 | 341.5 | 386.6 | 301.4 | 400.5 | 45.2 | 88.7 | 120.4 | 106.8 | 213 | 205.6 | 95.4 | 175.6 | 175 | 135.2
1066.3 | 847.3 | 377.5 | 151 | 176.5103 | 207.9 | 180.8 | 205 | 207.2 | 275.8 | 33.6 | 20.9 | 61.9 | 11.3 | 235.7 | 8.7 | 681.8 | 600.2 | 577.7 | 641 | 548.9 | 316.4 | 341 | 384.6 | 301.1 | 398.8 | 45.3 | 88.8 | 120.4 | 106.9 | 212.9 | 205.5 | 95.5 | 175.6 | 175.1 | 135.3
1067.3 | 848.3 | 378.1 | 151.24 | 176.7908 | 207 | 180.7 | 205.4 | 206.9 | 278.7 | 33.5 | 20.9 | 61.8 | 11.3 | 222.4 | 9.3 | 680.4 | 604.2 | 573 | 640.4 | 548.3 | 316.6 | 339.5 | 383.5 | 299.8 | 397.8 | 45.3 | 88.9 | 120.5 | 107 | 212.7 | 205.3 | 95.6 | 175.7 | 175.3 | 135.4
1068.3 | 849.3 | 378.3 | 151.32 | 176.8844 | 206 | 181.1 | 205.4 | 206.6 | 277.7 | 33.5 | 20.9 | 61.7 | 9.4 | 227.4 | 9 | 678.2 | 593.8 | 568.8 | 637 | 547.2 | 316.8 | 338.5 | 381.8 | 298.8 | 397.1 | 45.4 | 89 | 120.6 | 107.1 | 212.8 | 205.6 | 95.7 | 175.8 | 175.4 | 135.5
1069.3 | 850.3 | 378 | 151.2 | 176.7441 | 205.3 | 181.5 | 205.6 | 206.2 | 275.5 | 33.4 | 20.9 | 61.6 | 7.4 | 235.9 | 7.8 | 676.3 | 586.3 | 562.3 | 634.1 | 546.1 | 317 | 336.5 | 376.6 | 297.9 | 396.1 | 45.4 | 89.1 | 120.9 | 107.2 | 213.3 | 205.7 | 95.8 | 175.9 | 175.5 | 135.6
1070.3 | 851.3 | 378 | 151.2 | 176.7441 | 204.6 | 182 | 204.7 | 206 | 273.2 | 33.3 | 20.9 | 61.5 | 7.4 | 243.3 | 8.5 | 676.1 | 591.8 | 572.4 | 633.8 | 547.2 | 317.2 | 336.7 | 384.4 | 298.4 | 396.6 | 45.5 | 89.3 | 121.3 | 107.3 | 213.3 | 206.1 | 95.9 | 176 | 175.6 | 135.8
1071.3 | 852.3 | 378 | 151.2 | 176.7441 | 205.3 | 181.8 | 203.9 | 205.7 | 274.3 | 33.3 | 20.9 | 61.5 | 9.1 | 243.2 | 12.9 | 675.8 | 597.9 | 576.9 | 635 | 546.5 | 317.5 | 338.6 | 387.5 | 299.8 | 397.4 | 45.6 | 89.4 | 121.4 | 107.4 | 213.9 | 206 | 96 | 176.2 | 175.7 | 135.9
1072.3 | 853.3 | 377.9 | 151.16 | 176.6973 | 205.9 | 182.7 | 204 | 205.8 | 275.7 | 33.4 | 20.9 | 61.6 | 9.3 | 247.2 | 14.4 | 679.2 | 618.9 | 597.1 | 640.7 | 549.4 | 317.7 | 342.6 | 399 | 301.6 | 398.4 | 45.6 | 89.5 | 121.4 | 107.5 | 214 | 206 | 96.1 | 176.3 | 175.9 | 136
1073.3 | 854.3 | 377.8 | 151.12 | 176.6506 | 205.8 | 183.5 | 203.6 | 205.8 | 278.4 | 33.5 | 20.9 | 61.6 | 9.7 | 224.2 | 13.1 | 680.2 | 611.2 | 599.3 | 643.4 | 549.9 | 317.9 | 346.9 | 403.5 | 304.3 | 399.4 | 45.7 | 89.5 | 121.3 | 107.6 | 213.8 | 205.8 | 96.1 | 176.3 | 176.1 | 136.2
1074.3 | 855.3 | 377.8 | 151.12 | 176.6506 | 205.8 | 183.3 | 203.9 | 205.1 | 277 | 33.7 | 21 | 61.6 | 9.8 | 231.9 | 13 | 676.1 | 590.2 | 582.1 | 640.9 | 547 | 318.1 | 343.1 | 391.5 | 302.2 | 397.3 | 45.8 | 89.6 | 121.4 | 107.7 | 213.6 | 205.5 | 96.3 | 176.3 | 176.3 | 136.3
1075.3 | 856.3 | 377.7 | 151.08 | 176.6038 | 205.8 | 183.4 | 204.6 | 206.1 | 273.6 | 33.8 | 21 | 61.7 | 9.4 | 235.7 | 12.3 | 673.6 | 582.4 | 574.2 | 638.7 | 545.8 | 318.4 | 340.9 | 386.6 | 301.1 | 396.9 | 45.8 | 89.7 | 121.5 | 107.8 | 213.8 | 205.5 | 96.4 | 176.3 | 176.4 | 136.4
1076.3 | 857.3 | 377.9 | 151.16 | 176.6973 | 206.5 | 183.8 | 205.3 | 206.9 | 271.8 | 33.9 | 20.9 | 61.7 | 7.8 | 244.7 | 13.1 | 673.1 | 583.8 | 571.8 | 637.7 | 545.8 | 318.6 | 341.3 | 387.6 | 301.2 | 397.1 | 45.9 | 89.8 | 121.6 | 107.9 | 214.6 | 205.5 | 96.5 | 176.4 | 176.5 | 136.5
1077.3 | 858.3 | 377.7 | 151.08 | 176.6038 | 206.2 | 184.4 | 204.9 | 207.1 | 274 | 34 | 20.9 | 61.7 | 7.3 | 239.1 | 13.6 | 677.1 | 600.7 | 581.6 | 640.7 | 547 | 318.8 | 342.5 | 394.1 | 301.5 | 397 | 46 | 89.9 | 121.7 | 108 | 214.6 | 205.3 | 96.6 | 176.6 | 176.6 | 136.6
1078.3 | 859.3 | 376.9 | 150.76 | 176.2298 | 206.8 | 185.1 | 204.9 | 207.7 | 280.6 | 34.1 | 20.9 | 61.7 | 6.9 | 237.4 | 13.4 | 679.9 | 613.8 | 592.4 | 641.8 | 548.1 | 319 | 345.5 | 399.5 | 302.4 | 397.5 | 46 | 90 | 121.7 | 108.1 | 214.5 | 205 | 96.7 | 176.6 | 176.7 | 136.7
1079.3 | 860.3 | 377.7 | 151.08 | 176.6038 | 207.7 | 185.3 | 204.1 | 207.6 | 286.9 | 34.2 | 20.9 | 61.7 | 6.8 | 239.1 | 14.1 | 684.5 | 641.1 | 598.3 | 646.1 | 549.1 | 319.2 | 351.8 | 414.1 | 304.5 | 399.1 | 46.1 | 90.1 | 122 | 108.2 | 214.6 | 205 | 96.8 | 176.7 | 176.9 | 136.9
1080.3 | 861.3 | 377.4 | 150.96 | 176.4635 | 208.1 | 185.5 | 203.8 | 207.5 | 291.9 | 34.2 | 20.9 | 61.9 | 8 | 247 | 11.9 | 690.5 | 659.8 | 615.8 | 653.2 | 549.8 | 319.4 | 357 | 426.6 | 306.7 | 401 | 46.2 | 90.1 | 122.2 | 108.3 | 214.6 | 205.3 | 96.9 | 176.8 | 177 | 137
1081.3 | 862.3 | 377.4 | 150.96 | 176.4635 | 208.5 | 184.7 | 203.9 | 208.5 | 293.7 | 34.1 | 20.9 | 62 | 8.1 | 264.9 | 9.9 | 697.2 | 673.6 | 625.3 | 663.4 | 552.3 | 319.6 | 361.2 | 428.4 | 308.5 | 403.1 | 46.2 | 90.2 | 122.3 | 108.4 | 214.7 | 205.3 | 97 | 176.8 | 177.2 | 137.2
1082.3 | 863.3 | 378.5 | 151.4 | 176.9779 | 209.5 | 184.5 | 204.6 | 208.8 | 294.6 | 34 | 20.9 | 62.1 | 9.4 | 258.9 | 9.6 | 700.9 | 681.1 | 628.5 | 670.8 | 553.4 | 319.8 | 366.9 | 438.1 | 311.7 | 404.7 | 46.3 | 90.3 | 122.4 | 108.5 | 215 | 205.5 | 97.1 | 176.9 | 177.4 | 137.3
1083.3 | 864.3 | 377.8 | 151.12 | 176.6506 | 210.4 | 185.5 | 204.8 | 208.8 | 294.2 | 34.1 | 20.9 | 62.2 | 8.9 | 257.7 | 9.8 | 703.6 | 678.2 | 649 | 676.9 | 556 | 320 | 369.1 | 440.8 | 313 | 405.6 | 46.4 | 90.4 | 122.5 | 108.6 | 215.5 | 205.4 | 97.2 | 177 | 177.5 | 137.4
1084.3 | 865.3 | 376.7 | 150.68 | 176.1362 | 209.1 | 185.9 | 204.9 | 209.3 | 296.8 | 34.1 | 20.9 | 62.2 | 9.6 | 263.1 | 12.5 | 704.4 | 671.6 | 667.1 | 679.3 | 559.1 | 320.2 | 373.4 | 447 | 315.6 | 408 | 46.4 | 90.5 | 122.6 | 108.7 | 216 | 205.6 | 97.3 | 177.1 | 177.7 | 137.5
1085.3 | 866.3 | 376.9 | 150.76 | 176.2298 | 207.1 | 186.7 | 204.6 | 209.6 | 297.7 | 34.1 | 20.9 | 62.2 | 11 | 265.1 | 19.5 | 703.8 | 663.5 | 664.2 | 679.2 | 559.4 | 320.5 | 374.4 | 441 | 316.9 | 410.1 | 46.5 | 90.5 | 122.7 | 108.8 | 216.8 | 205.7 | 97.4 | 177.2 | 177.9 | 137.7
1086.3 | 867.3 | 378 | 151.2 | 176.7441 | 206 | 186.2 | 205.1 | 210 | 295.1 | 34.1 | 20.9 | 62.2 | 11.5 | 251.9 | 19.3 | 702.9 | 648 | 672.7 | 678.5 | 561.5 | 320.7 | 372.7 | 433.4 | 316.7 | 409.9 | 46.6 | 90.6 | 122.8 | 108.9 | 217.3 | 206.5 | 97.5 | 177.4 | 178.1 | 137.8
1087.3 | 868.3 | 377.3 | 150.92 | 176.4168 | 205.3 | 185.9 | 205.1 | 210.5 | 293.7 | 34.1 | 20.9 | 62.2 | 12.9 | 256 | 17.4 | 705.2 | 659 | 678.3 | 682.2 | 562.4 | 320.9 | 371.9 | 435.2 | 317.4 | 410.9 | 46.6 | 90.7 | 122.9 | 109 | 217 | 207.1 | 97.6 | 177.5 | 178.3 | 138
1088.3 | 869.3 | 378.3 | 151.32 | 176.8844 | 205.5 | 185.3 | 204.6 | 210.9 | 293.1 | 34.1 | 20.9 | 62.2 | 12.8 | 255.7 | 19.1 | 704.5 | 649.2 | 663.2 | 680.6 | 560.3 | 321.2 | 370.8 | 433.6 | 317.2 | 410.6 | 46.7 | 90.8 | 122.9 | 109.1 | 216.7 | 207.2 | 97.7 | 177.7 | 178.5 | 138.1
1089.3 | 870.3 | 377.5 | 151 | 176.5103 | 204.6 | 185.7 | 204.3 | 210.7 | 292.3 | 34.1 | 20.9 | 62.2 | 11.6 | 253.6 | 17.6 | 703.5 | 653.6 | 660.5 | 677.7 | 559.7 | 321.3 | 369.6 | 432.5 | 316.7 | 409.9 | 46.8 | 90.9 | 123.2 | 109.2 | 216.8 | 207.3 | 97.7 | 177.7 | 178.7 | 138.2
1090.3 | 871.3 | 376.1 | 150.44 | 175.8557 | 204.1 | 186.5 | 204.2 | 210.2 | 295.6 | 34.1 | 20.9 | 62.2 | 11 | 251.9 | 18.4 | 702.7 | 647.2 | 651.2 | 676.7 | 559.1 | 321.5 | 368.6 | 434.5 | 316.5 | 409.5 | 46.8 | 91 | 123.3 | 109.2 | 216.5 | 207.1 | 97.9 | 177.7 | 178.8 | 138.3
1091.3 | 872.3 | 376 | 150.4 | 175.8089 | 203.3 | 187.8 | 204.3 | 209.3 | 298.1 | 34.2 | 20.9 | 62.3 | 13.4 | 246.9 | 18.8 | 701 | 638.4 | 646 | 673.8 | 558.4 | 321.7 | 365.8 | 427.5 | 315 | 408.1 | 46.9 | 91.1 | 123.3 | 109.3 | 216.3 | 207.1 | 98 | 177.8 | 178.9 | 138.5
1092.3 | 873.3 | 376.5 | 150.6 | 176.0427 | 203.3 | 188.1 | 204 | 209 | 295.6 | 34.2 | 20.9 | 62.4 | 13 | 257.4 | 17 | 700.3 | 635.1 | 648.1 | 672.3 | 559.5 | 321.9 | 365.1 | 424 | 314.5 | 408.3 | 47 | 91.2 | 123.3 | 109.4 | 216.2 | 207.3 | 98.1 | 178 | 179 | 138.6
1093.3 | 874.3 | 376.2 | 150.48 | 175.9024 | 204.8 | 187.7 | 203.7 | 208.5 | 292.8 | 34.2 | 20.9 | 62.4 | 11.5 | 246.9 | 15 | 700.1 | 626.2 | 652.7 | 670.9 | 560.4 | 322.1 | 364.9 | 418.3 | 314.6 | 408.3 | 47 | 91.2 | 123.5 | 109.5 | 216 | 207.2 | 98.2 | 178 | 179.2 | 138.8
1094.3 | 875.3 | 376.2 | 150.48 | 175.9024 | 205.2 | 187.2 | 203.7 | 207.5 | 289.8 | 34.2 | 20.9 | 62.5 | 11.7 | 254.4 | 14 | 701.2 | 630.4 | 663.8 | 671.6 | 563.5 | 322.4 | 365.5 | 420.8 | 315.6 | 408.7 | 47.1 | 91.3 | 123.8 | 109.6 | 216 | 207 | 98.3 | 178.1 | 179.3 | 138.9
1095.3 | 876.3 | 378.5 | 151.4 | 176.9779 | 205.6 | 187.6 | 203.2 | 207 | 292.4 | 34.2 | 20.9 | 62.6 | 11.9 | 248 | 19.2 | 701.1 | 628.2 | 646.4 | 673.4 | 562.1 | 322.6 | 367.3 | 424.2 | 316.6 | 409.2 | 47.2 | 91.4 | 123.8 | 109.7 | 216.3 | 206.8 | 98.3 | 178.1 | 179.5 | 139
1096.3 | 877.3 | 378.1 | 151.24 | 176.7908 | 206.9 | 187.8 | 202.8 | 207 | 293 | 34.1 | 20.9 | 62.7 | 12.3 | 255.9 | 18.9 | 697.7 | 606.7 | 628.6 | 670.5 | 559.2 | 322.9 | 364.6 | 415.1 | 314.8 | 407.4 | 47.2 | 91.5 | 123.9 | 109.8 | 216.4 | 206.5 | 98.5 | 178.2 | 179.7 | 139.1
1097.3 | 878.3 | 378.2 | 151.28 | 176.8376 | 208.3 | 187.8 | 203.2 | 207.3 | 290.5 | 34.1 | 20.9 | 62.7 | 12.4 | 242 | 20 | 694.5 | 597.1 | 615.9 | 667.2 | 557.8 | 323.1 | 360.4 | 409 | 312.8 | 405.9 | 47.3 | 91.6 | 124.1 | 109.9 | 216.4 | 206.1 | 98.5 | 178.2 | 179.8 | 139.2
1098.3 | 879.3 | 378.3 | 151.32 | 176.8844 | 209.6 | 187.9 | 204 | 207.5 | 287.3 | 34.1 | 20.9 | 62.7 | 10.9 | 243 | 20.5 | 693.1 | 595.4 | 618.8 | 663 | 557 | 323.4 | 357 | 404.1 | 311.2 | 404.9 | 47.4 | 91.6 | 124.1 | 110 | 216.4 | 205.8 | 98.6 | 178.2 | 179.9 | 139.3
1099.3 | 880.3 | 377.7 | 151.08 | 176.6038 | 209.7 | 188.5 | 204.8 | 208.3 | 284.2 | 34.1 | 20.9 | 62.7 | 9.9 | 253.1 | 18.5 | 691 | 580.3 | 609.1 | 659.6 | 555.7 | 323.6 | 353.4 | 398 | 309.6 | 404.2 | 47.4 | 91.7 | 124.2 | 110.1 | 216.3 | 205.7 | 98.7 | 178.2 | 180 | 139.4
1100.3 | 881.3 | 377.5 | 151 | 176.5103 | 209.6 | 188.7 | 204.3 | 208.4 | 282.1 | 34 | 20.9 | 62.6 | 9.3 | 258.6 | 17.5 | 686.2 | 561.1 | 583.4 | 654.5 | 553.1 | 323.8 | 349.5 | 390.4 | 307.6 | 402.5 | 47.5 | 91.8 | 124.2 | 110.2 | 216.4 | 205.5 | 98.8 | 178.4 | 180.1 | 139.5
1101.3 | 882.3 | 377 | 150.8 | 176.2765 | 209.5 | 188.6 | 204.1 | 208.5 | 278.1 | 34 | 20.9 | 62.6 | 10.2 | 255.3 | 17.2 | 679.2 | 536.7 | 560.4 | 648.4 | 550.5 | 324 | 344.6 | 381.2 | 305.4 | 400.5 | 47.5 | 91.9 | 124.3 | 110.3 | 216.4 | 205.4 | 98.9 | 178.5 | 180.2 | 139.7
1102.3 | 883.3 | 376.8 | 150.72 | 176.183 | 209.6 | 188.1 | 203.5 | 209 | 273.5 | 34.1 | 20.9 | 62.5 | 11.3 | 256.6 | 17.2 | 672.4 | 514.5 | 540.8 | 642.1 | 547.9 | 324.2 | 339.3 | 373.2 | 303.1 | 399.1 | 47.6 | 92 | 124.3 | 110.4 | 217.3 | 205.4 | 99 | 178.7 | 180.3 | 139.8
1103.3 | 884.3 | 377.6 | 151.04 | 176.5571 | 210.4 | 188 | 203.8 | 209.9 | 269.7 | 34.1 | 20.9 | 62.5 | 13.3 | 257.8 | 16.1 | 665.7 | 497.8 | 522 | 635.4 | 545.6 | 324.4 | 334.6 | 365.5 | 301 | 397.5 | 47.7 | 92.2 | 124.4 | 110.5 | 217.7 | 205.3 | 99.1 | 178.8 | 180.3 | 140
1104.3 | 885.3 | 378.3 | 151.32 | 176.8844 | 212.3 | 187.4 | 204 | 210.7 | 266 | 34.1 | 20.9 | 62.5 | 12.4 | 253.6 | 14.9 | 661.7 | 495.3 | 519.2 | 627.7 | 544.8 | 324.7 | 330.8 | 359.5 | 299.4 | 396.2 | 47.7 | 92.3 | 124.6 | 110.5 | 217.8 | 205.2 | 99.2 | 178.8 | 180.4 | 140.1
1105.3 | 886.3 | 377.9 | 151.16 | 176.6973 | 212.5 | 187.3 | 205.2 | 210.4 | 265.1 | 34.2 | 20.9 | 62.5 | 11.1 | 262.2 | 12.3 | 659.8 | 495.1 | 511.8 | 622.5 | 543.7 | 324.9 | 329 | 357.3 | 298.4 | 395.6 | 47.8 | 92.3 | 124.7 | 110.6 | 217.8 | 205.2 | 99.3 | 178.9 | 180.4 | 140.2
1106.3 | 887.3 | 377.5 | 151 | 176.5103 | 211.7 | 187.9 | 206.1 | 210 | 265.1 | 34.2 | 20.9 | 62.5 | 13.5 | 257.6 | 11.8 | 657.2 | 486.1 | 501.3 | 619.2 | 541.9 | 325.1 | 327.1 | 351.8 | 297.3 | 394.3 | 47.9 | 92.5 | 124.6 | 110.7 | 217.9 | 205.5 | 99.4 | 179.1 | 180.5 | 140.3
1107.3 | 888.3 | 378 | 151.2 | 176.7441 | 211.3 | 187.1 | 206.5 | 210.5 | 262.9 | 34.2 | 20.9 | 62.6 | 13.4 | 252.6 | 11.9 | 659.4 | 512.5 | 520 | 620.9 | 542.3 | 325.3 | 328.3 | 355.5 | 297.4 | 394.8 | 47.9 | 92.6 | 124.7 | 110.8 | 218 | 205.8 | 99.5 | 179.2 | 180.7 | 140.5
1108.3 | 889.3 | 378 | 151.2 | 176.7441 | 211.9 | 187.3 | 206.9 | 211 | 267.4 | 34.2 | 20.9 | 62.7 | 11.9 | 254.1 | 11.6 | 663.6 | 539.2 | 541.3 | 627 | 544.5 | 325.5 | 338.3 | 376.4 | 301.6 | 398.8 | 48 | 92.7 | 124.9 | 110.9 | 217.5 | 206.1 | 99.6 | 179.2 | 180.8 | 140.6
1109.3 | 890.3 | 377.8 | 151.12 | 176.6506 | 211 | 187.4 | 207.6 | 211.3 | 275 | 34.1 | 20.9 | 62.7 | 9.4 | 253.5 | 10.9 | 667.1 | 556 | 567.1 | 632.8 | 546.4 | 325.7 | 342.1 | 385.6 | 303.2 | 399.5 | 48.1 | 92.8 | 125 | 111 | 217.6 | 206.2 | 99.7 | 179.3 | 180.9 | 140.7
1110.3 | 891.3 | 377.7 | 151.08 | 176.6038 | 210.2 | 186.7 | 207.7 | 211.4 | 278.8 | 34.1 | 20.9 | 62.8 | 9.7 | 240.8 | 15.8 | 667.5 | 553.9 | 572.9 | 635.6 | 547.1 | 326 | 345.7 | 382.9 | 305 | 400.6 | 48.1 | 92.9 | 125.2 | 111.1 | 217.2 | 206.1 | 99.8 | 179.3 | 181 | 140.8
1111.3 | 892.3 | 377.6 | 151.04 | 176.5571 | 209.5 | 186.4 | 207.7 | 211.1 | 279.1 | 34.1 | 20.9 | 62.7 | 11.4 | 244.2 | 19.1 | 670 | 563 | 598.4 | 643.6 | 548.9 | 326.2 | 349.4 | 385.1 | 306.4 | 402.2 | 48.2 | 92.9 | 125.3 | 111.2 | 217.1 | 206.6 | 99.9 | 179.4 | 181.2 | 141
1112.3 | 893.3 | 377.4 | 150.96 | 176.4635 | 208.8 | 186 | 207.7 | 211.3 | 280.4 | 34.1 | 20.9 | 62.8 | 11.3 | 246.5 | 20.1 | 674.5 | 584.5 | 626.1 | 651.7 | 552.4 | 326.4 | 357.6 | 404.6 | 311.3 | 407.2 | 48.3 | 93 | 125.4 | 111.2 | 216.6 | 207.1 | 100 | 179.5 | 181.2 | 141.1
1113.3 | 894.3 | 377.2 | 150.88 | 176.37 | 208.3 | 185.9 | 207.2 | 211.3 | 283.4 | 34 | 20.9 | 62.7 | 10.5 | 253.6 | 19.4 | 675.2 | 581.1 | 625.9 | 653.1 | 551.2 | 326.6 | 359.9 | 402.4 | 312.7 | 407 | 48.3 | 93.1 | 125.6 | 111.3 | 216.2 | 207.8 | 100 | 179.6 | 181.4 | 141.2
1114.3 | 895.3 | 377 | 150.8 | 176.2765 | 207.1 | 186.7 | 206.7 | 211.3 | 284.8 | 34 | 20.9 | 62.7 | 10.1 | 251 | 15.7 | 676.6 | 590.7 | 636.9 | 655.7 | 554.5 | 326.8 | 364.2 | 406.1 | 314.5 | 408.3 | 48.4 | 93.2 | 125.8 | 111.4 | 216.4 | 208.2 | 100.1 | 179.7 | 181.5 | 141.3
1115.3 | 896.3 | 377 | 150.8 | 176.2765 | 206.2 | 187.3 | 206.3 | 210 | 284.7 | 34 | 20.9 | 62.6 | 13.2 | 243.8 | 14.4 | 674.3 | 577.9 | 635.9 | 653.1 | 553.6 | 327 | 361.6 | 397.6 | 313.3 | 406.2 | 48.4 | 93.3 | 125.8 | 111.5 | 216.5 | 208.5 | 100.3 | 179.8 | 181.8 | 141.4
1116.3 | 897.3 | 377.3 | 150.92 | 176.4168 | 205.6 | 187.2 | 206.9 | 209.4 | 282.8 | 33.8 | 20.9 | 62.6 | 13.9 | 250.4 | 14.3 | 673 | 579.4 | 624.8 | 651 | 553.3 | 327.1 | 360.2 | 395.3 | 312.2 | 405.4 | 48.5 | 93.4 | 125.9 | 111.6 | 216.1 | 209.1 | 100.3 | 179.8 | 181.9 | 141.6
1117.3 | 898.3 | 377.2 | 150.88 | 176.37 | 205.3 | 187.4 | 207.2 | 208.2 | 284 | 33.7 | 20.9 | 62.5 | 12.2 | 256.7 | 13.1 | 671.9 | 575.1 | 613.7 | 648.2 | 552.4 | 327.4 | 357.8 | 392.8 | 311 | 404.4 | 48.6 | 93.5 | 126 | 111.7 | 215.6 | 208.8 | 100.4 | 179.9 | 182.1 | 141.7
1118.3 | 899.3 | 376.6 | 150.64 | 176.0895 | 204 | 188.4 | 207.2 | 207.1 | 282.9 | 33.7 | 20.9 | 62.4 | 11.3 | 249.3 | 15.8 | 668.9 | 569.1 | 606.2 | 642.3 | 550.8 | 327.5 | 355.2 | 393.5 | 309.6 | 403.3 | 48.6 | 93.6 | 126.2 | 111.8 | 215.6 | 208.1 | 100.5 | 179.9 | 182.1 | 141.7
1119.3 | 900.3 | 377.3 | 150.92 | 176.4168 | 205.8 | 189 | 206.9 | 205.4 | 284.5 | 33.7 | 20.9 | 62.3 | 12.1 | 238.1 | 19.5 | 669.3 | 578.5 | 609.2 | 641.1 | 550.1 | 327.7 | 354.3 | 395.5 | 309.5 | 403.1 | 48.7 | 93.7 | 126.3 | 111.9 | 216.2 | 207.6 | 100.6 | 179.9 | 182.3 | 141.9
1120.3 | 901.3 | 377.2 | 150.88 | 176.37 | 207.2 | 189.3 | 205.8 | 205.5 | 285.6 | 33.7 | 20.9 | 62.3 | 11.7 | 246.7 | 20.2 | 670.5 | 592.5 | 624.5 | 641.4 | 552 | 327.9 | 355.9 | 399.5 | 310 | 404.1 | 48.8 | 93.8 | 126.2 | 112 | 215.8 | 207.2 | 100.7 | 179.9 | 182.4 | 142.1
1121.3 | 902.3 | 376.7 | 150.68 | 176.1362 | 207.4 | 189.9 | 205.5 | 205.9 | 285.1 | 34 | 20.9 | 62.2 | 9.7 | 245.5 | 17.9 | 670 | 586.1 | 619.2 | 639.7 | 551.4 | 328.1 | 356.9 | 398.3 | 310.9 | 404.3 | 48.8 | 93.9 | 126.4 | 112.1 | 215.4 | 206.7 | 100.8 | 179.9 | 182.4 | 142.2
1122.3 | 903.3 | 377.2 | 150.88 | 176.37 | 209.7 | 189.6 | 205.4 | 205.9 | 284.1 | 34.1 | 20.9 | 62.3 | 9.9 | 271.6 | 14.8 | 669.1 | 589.3 | 621 | 638 | 550.1 | 328.2 | 356.2 | 393.7 | 310.2 | 403.5 | 48.9 | 94 | 126.5 | 112.2 | 215.2 | 206.6 | 100.9 | 179.9 | 182.7 | 142.3
1123.3 | 904.3 | 376.8 | 150.72 | 176.183 | 210.4 | 188.8 | 205.5 | 206 | 285.3 | 34.4 | 20.9 | 62.4 | 9.8 | 240.6 | 14.5 | 672 | 606 | 635.4 | 640.7 | 552.6 | 328.4 | 360.4 | 408.4 | 312.2 | 405.3 | 49 | 94.1 | 126.6 | 112.2 | 215.2 | 206.6 | 101 | 180 | 182.8 | 142.4
1124.3 | 905.3 | 377.2 | 150.88 | 176.37 | 210.6 | 188.4 | 204.6 | 206.1 | 288.1 | 34.6 | 20.9 | 62.5 | 9.9 | 249.3 | 16.3 | 673.7 | 599.1 | 639 | 643.6 | 553 | 328.6 | 364.6 | 405.6 | 314.3 | 406.9 | 49 | 94.2 | 126.6 | 112.3 | 216.1 | 206.8 | 101 | 180 | 182.9 | 142.5
1125.3 | 906.3 | 377.1 | 150.84 | 176.3233 | 209.5 | 188.8 | 204 | 205.5 | 288.1 | 34.7 | 20.9 | 62.5 | 9.5 | 246.3 | 13.9 | 673.8 | 599.9 | 615.8 | 643.7 | 551 | 328.8 | 362.4 | 400.5 | 313.6 | 405.5 | 49.1 | 94.2 | 126.8 | 112.4 | 216.1 | 207.3 | 101.2 | 180.1 | 183.1 | 142.6
1126.3 | 907.3 | 377.3 | 150.92 | 176.4168 | 209 | 188.2 | 204.1 | 205.6 | 285.5 | 34.8 | 20.9 | 62.6 | 9.8 | 246.4 | 14.5 | 672.1 | 589.8 | 600.5 | 641.5 | 548.6 | 329 | 359.3 | 394.9 | 311.8 | 403.9 | 49.2 | 94.3 | 126.7 | 112.5 | 216.2 | 207.4 | 101.2 | 180.2 | 183.3 | 142.7
1127.3 | 908.3 | 377.3 | 150.92 | 176.4168 | 210.1 | 187.3 | 204.2 | 205.5 | 282.3 | 34.8 | 20.9 | 62.6 | 9.3 | 256.4 | 14.2 | 671.3 | 584.9 | 596.7 | 642.3 | 548.1 | 329.2 | 355.6 | 391.7 | 310.1 | 402.8 | 49.3 | 94.4 | 126.9 | 112.6 | 215.9 | 207.6 | 101.3 | 180.2 | 183.4 | 142.8
1128.3 | 909.3 | 377.4 | 150.96 | 176.4635 | 211 | 186.6 | 203.9 | 205.8 | 281.2 | 34.8 | 20.9 | 62.5 | 8.7 | 239.8 | 12.9 | 670.5 | 582.1 | 605 | 643.4 | 549.4 | 329.5 | 355.7 | 391.5 | 309.7 | 403.4 | 49.3 | 94.5 | 127.2 | 112.6 | 215.7 | 207.3 | 101.4 | 180.3 | 183.4 | 142.9
1129.3 | 910.3 | 377.5 | 151 | 176.5103 | 211.4 | 186 | 203.8 | 205.7 | 281.8 | 34.8 | 20.9 | 62.5 | 8.2 | 238.5 | 10.8 | 671.1 | 583 | 607.8 | 643.8 | 551.9 | 329.7 | 356.5 | 398.1 | 310.4 | 405.2 | 49.4 | 94.6 | 127.2 | 112.7 | 215.6 | 206.8 | 101.5 | 180.3 | 183.5 | 143.1
1130.3 | 911.3 | 377.4 | 150.96 | 176.4635 | 212 | 184.9 | 203.7 | 206 | 284.3 | 34.8 | 20.9 | 62.6 | 8.2 | 246.5 | 11.4 | 669.3 | 573.2 | 594.9 | 642 | 549.9 | 329.9 | 354.8 | 394.1 | 309.9 | 403.7 | 49.4 | 94.7 | 127.2 | 112.8 | 215.4 | 206.3 | 101.6 | 180.4 | 183.7 | 143.2
1131.3 | 912.3 | 376 | 150.4 | 175.8089 | 212.5 | 184.2 | 202.9 | 206.3 | 284.5 | 34.8 | 20.9 | 62.6 | 7.6 | 257.4 | 11.3 | 666.5 | 566.5 | 583.6 | 638.1 | 548.4 | 330.2 | 352.4 | 393 | 309 | 402.2 | 49.5 | 94.8 | 127.4 | 112.9 | 215.4 | 206 | 101.7 | 180.5 | 183.9 | 143.3
1132.3 | 913.3 | 377.4 | 150.96 | 176.4635 | 212.3 | 183.7 | 202.8 | 205.7 | 283.3 | 34.8 | 20.9 | 62.7 | 7.8 | 253.5 | 11.5 | 661.8 | 542.4 | 564.3 | 633.9 | 545.7 | 330.4 | 348.9 | 382.3 | 307.7 | 400.8 | 49.6 | 94.9 | 127.4 | 113 | 215 | 206 | 101.8 | 180.6 | 184 | 143.4
1133.3 | 914.3 | 379.2 | 151.68 | 177.3052 | 212.1 | 184 | 202.3 | 205.4 | 279 | 34.8 | 20.9 | 62.8 | 7.6 | 257.1 | 11.7 | 661.2 | 548.8 | 567.5 | 632.3 | 545.3 | 330.6 | 345.5 | 378.5 | 305.7 | 399.8 | 49.6 | 95 | 127.5 | 113.1 | 214.7 | 205.9 | 101.9 | 180.6 | 184.1 | 143.5
1134.3 | 915.3 | 377.5 | 151 | 176.5103 | 211.6 | 183.3 | 201.8 | 204.9 | 276.2 | 34.8 | 20.9 | 62.9 | 7.7 | 253.7 | 10.5 | 658.7 | 543.8 | 557.7 | 628.5 | 543.9 | 330.8 | 343.4 | 376 | 304.7 | 398.7 | 49.7 | 95 | 127.7 | 113.1 | 214.4 | 205.8 | 101.9 | 180.6 | 184.2 | 143.6
1135.3 | 916.3 | 376.2 | 150.48 | 175.9024 | 211.1 | 183.3 | 202.2 | 203.7 | 276 | 34.8 | 20.9 | 62.9 | 7 | 261 | 9.1 | 656.2 | 542.2 | 560.1 | 625.2 | 543 | 331 | 341.6 | 376.2 | 303.7 | 397.6 | 49.8 | 95.1 | 127.8 | 113.2 | 214.2 | 205.8 | 102 | 180.7 | 184.2 | 143.7
1136.3 | 917.3 | 376.3 | 150.52 | 175.9492 | 211.9 | 183.7 | 203.2 | 203.5 | 273.8 | 34.8 | 20.9 | 63 | 6.5 | 255.4 | 8.8 | 655.7 | 548.6 | 564.1 | 623.5 | 543.4 | 331.2 | 339.4 | 373.1 | 302.5 | 396.6 | 49.8 | 95.2 | 127.8 | 113.3 | 213.8 | 205.7 | 102.1 | 180.8 | 184.3 | 143.8
1137.3 | 918.3 | 376.8 | 150.72 | 176.183 | 210.8 | 183.6 | 203.8 | 203.9 | 273.9 | 34.8 | 20.9 | 63 | 6.8 | 261.9 | 8.3 | 656.9 | 554.5 | 576.3 | 624.6 | 544.5 | 331.4 | 339.5 | 372 | 302.4 | 396.7 | 49.9 | 95.3 | 128.1 | 113.4 | 214 | 205.6 | 102.2 | 180.8 | 184.4 | 143.9
1138.3 | 919.3 | 377.3 | 150.92 | 176.4168 | 209.1 | 183.4 | 203.8 | 204.3 | 274.8 | 34.7 | 20.9 | 63.1 | 6.2 | 253.9 | 7.6 | 661.5 | 570.8 | 588.2 | 628.9 | 545.4 | 331.6 | 342.2 | 384.8 | 303.9 | 397.9 | 50 | 95.4 | 128.2 | 113.5 | 214 | 205.8 | 102.3 | 180.9 | 184.5 | 144
1139.3 | 920.3 | 378.6 | 151.44 | 177.0246 | 207.7 | 183 | 204.4 | 205 | 275 | 34.7 | 20.9 | 63.2 | 7.4 | 256.1 | 7.2 | 662.9 | 583.2 | 590.6 | 628.4 | 545.5 | 331.8 | 343.3 | 388.4 | 304.1 | 397.6 | 50 | 95.5 | 128.3 | 113.5 | 213.9 | 205.7 | 102.4 | 180.8 | 184.6 | 144.1
1140.3 | 921.3 | 378.5 | 151.4 | 176.9779 | 206.8 | 183 | 204.5 | 205.5 | 278.8 | 34.6 | 20.9 | 63.1 | 7.4 | 241.2 | 6.8 | 664.4 | 600.5 | 598.5 | 628.1 | 546.1 | 332 | 344.4 | 397.5 | 304.7 | 397.7 | 50.1 | 95.6 | 128.7 | 113.6 | 213.8 | 205.3 | 102.5 | 180.9 | 184.7 | 144.2
1141.3 | 922.3 | 378.3 | 151.32 | 176.8844 | 207.6 | 183.6 | 205.1 | 206.2 | 283.6 | 34.7 | 20.9 | 63.1 | 7.6 | 252.6 | 6.9 | 664 | 601.7 | 597.5 | 627.1 | 546.7 | 332.2 | 344.7 | 397.2 | 304.7 | 397.4 | 50.2 | 95.6 | 128.7 | 113.7 | 213.8 | 205.2 | 102.6 | 180.9 | 184.8 | 144.3
1142.3 | 923.3 | 379.3 | 151.72 | 177.3519 | 207.6 | 183.5 | 205.9 | 207.2 | 284.5 | 34.7 | 20.9 | 63.1 | 7.2 | 243.5 | 9 | 666.3 | 601 | 609.9 | 631 | 548.4 | 332.4 | 344.9 | 396.8 | 304 | 396.9 | 50.2 | 95.7 | 128.6 | 113.7 | 214 | 205.2 | 102.7 | 180.9 | 184.9 | 144.4
1143.3 | 924.3 | 375.8 | 150.32 | 175.7154 | 207 | 184.5 | 206.3 | 207.7 | 287.1 | 34.8 | 20.9 | 63.1 | 7 | 241.9 | 10 | 670.5 | 608.1 | 616.7 | 637.3 | 548.8 | 332.6 | 348.5 | 402.3 | 305.7 | 398.3 | 50.3 | 95.8 | 128.7 | 113.8 | 214.4 | 205.2 | 102.8 | 181 | 185 | 144.5
1144.3 | 925.3 | 375.3 | 150.12 | 175.4816 | 206.6 | 185.7 | 206.9 | 208.1 | 287.9 | 34.9 | 20.9 | 63.1 | 6.4 | 240.3 | 10.3 | 674.6 | 608.7 | 623 | 643.6 | 548.9 | 332.8 | 350 | 405.8 | 306.4 | 398.5 | 50.4 | 95.9 | 128.8 | 113.9 | 214.5 | 205.2 | 102.8 | 181.1 | 185.1 | 144.6
1145.3 | 926.3 | 376.8 | 150.72 | 176.183 | 206.2 | 186.6 | 207 | 208.3 | 288.8 | 34.9 | 20.9 | 63.2 | 7.4 | 245.6 | 9.9 | 675.1 | 596.9 | 617.2 | 646.3 | 547.4 | 333 | 350.7 | 400.3 | 306.6 | 398.2 | 50.4 | 95.9 | 128.9 | 113.9 | 214.6 | 205.2 | 103 | 181.2 | 185.3 | 144.8
1146.3 | 927.3 | 376.6 | 150.64 | 176.0895 | 206.7 | 186.3 | 207 | 208.9 | 288.2 | 34.9 | 20.9 | 63.3 | 7.1 | 241.4 | 9.3 | 672.9 | 579.1 | 603.5 | 644.6 | 546.2 | 333.2 | 349.4 | 393.6 | 305.8 | 396.9 | 50.5 | 96 | 129 | 114 | 215.8 | 205.4 | 103 | 181.3 | 185.4 | 144.9
1147.3 | 928.3 | 376.9 | 150.76 | 176.2298 | 208.2 | 185.8 | 207 | 209.6 | 285.9 | 34.9 | 20.9 | 63.4 | 7.1 | 239 | 9.4 | 669 | 562.6 | 582.8 | 640.2 | 543.8 | 333.4 | 345.8 | 387.1 | 304.2 | 395.2 | 50.6 | 96.1 | 129.1 | 114 | 215.8 | 205.3 | 103.1 | 181.3 | 185.5 | 145.1
1148.3 | 929.3 | 376.5 | 150.6 | 176.0427 | 210 | 185.9 | 207.3 | 209.5 | 281.5 | 34.9 | 20.9 | 63.3 | 6.6 | 245.1 | 9.2 | 665.5 | 548.6 | 572.9 | 635.6 | 542 | 333.6 | 342.2 | 381.5 | 302.8 | 393.8 | 50.6 | 96.2 | 129.2 | 114.1 | 215.6 | 205 | 103.2 | 181.4 | 185.6 | 145.2
1149.3 | 930.3 | 376.6 | 150.64 | 176.0895 | 210.7 | 185.6 | 207.6 | 209 | 279 | 34.9 | 20.9 | 63.3 | 6.8 | 262.4 | 7.2 | 663.8 | 540.4 | 565.4 | 632.2 | 540.5 | 333.8 | 338.4 | 375.1 | 301.2 | 392.6 | 50.7 | 96.4 | 129.2 | 114.2 | 215.5 | 204.9 | 103.3 | 181.4 | 185.7 | 145.3
1150.3 | 931.3 | 376.6 | 150.64 | 176.0895 | 210.2 | 184.9 | 208.2 | 209.4 | 276.3 | 34.9 | 20.9 | 63.3 | 6.8 | 262.6 | 5.7 | 665.1 | 552.3 | 568.3 | 631.6 | 540.1 | 334 | 337.1 | 379.4 | 300.3 | 392.1 | 50.8 | 96.5 | 129.3 | 114.2 | 215.2 | 204.5 | 103.4 | 181.3 | 185.8 | 145.4
1151.3 | 932.3 | 377.3 | 150.92 | 176.4168 | 210.9 | 183.5 | 208.4 | 208.8 | 276.3 | 34.8 | 20.9 | 63.5 | 7.9 | 234.1 | 5.3 | 665.1 | 545.6 | 565.4 | 630.7 | 538.6 | 334.2 | 336 | 376.1 | 299.8 | 391.3 | 50.8 | 96.6 | 129.4 | 114.3 | 214.9 | 204.2 | 103.4 | 181.4 | 185.8 | 145.5
1152.3 | 933.3 | 378.1 | 151.24 | 176.7908 | 211.2 | 182.6 | 208 | 207.9 | 274.5 | 34.8 | 20.9 | 63.6 | 7.6 | 242.1 | 5 | 665.2 | 558.2 | 566.2 | 630.7 | 538.3 | 334.4 | 335.2 | 379 | 298.9 | 390.9 | 50.9 | 96.7 | 129.6 | 114.3 | 214.8 | 204 | 103.6 | 181.4 | 185.9 | 145.6
1153.3 | 934.3 | 378.7 | 151.48 | 177.0714 | 210.8 | 182.1 | 207.5 | 207.1 | 278.6 | 34.7 | 20.9 | 63.7 | 6.2 | 269.4 | 5.5 | 666 | 586 | 583.5 | 631.4 | 539.9 | 334.6 | 336.4 | 387 | 299.6 | 391.3 | 51 | 96.7 | 129.7 | 114.4 | 214.6 | 203.6 | 103.6 | 181.4 | 186 | 145.7
1154.3 | 935.3 | 376.5 | 150.6 | 176.0427 | 210.2 | 181 | 207.7 | 206.8 | 283.8 | 34.7 | 20.9 | 63.8 | 6.4 | 267.5 | 6.3 | 669.6 | 609.6 | 611.8 | 637 | 543.8 | 334.8 | 340.2 | 397 | 301.8 | 393.6 | 51 | 96.8 | 129.7 | 114.5 | 214.3 | 203.3 | 103.7 | 181.4 | 186.1 | 145.8
1155.3 | 936.3 | 375.7 | 150.28 | 175.6687 | 209.3 | 180.3 | 208.2 | 206.5 | 286.4 | 34.7 | 20.9 | 63.9 | 6.7 | 260.3 | 7.8 | 674.4 | 627.7 | 637.3 | 646.8 | 546.6 | 335 | 346.9 | 404.5 | 304.5 | 395.9 | 51.1 | 96.9 | 129.9 | 114.5 | 213.9 | 203.2 | 103.8 | 181.4 | 186.3 | 145.9
1156.3 | 937.3 | 376.1 | 150.44 | 175.8557 | 208.5 | 180.8 | 207.7 | 207 | 291.5 | 34.8 | 20.9 | 64 | 6.9 | 232.5 | 8.2 | 682.1 | 657.2 | 674.6 | 660.8 | 553 | 335.2 | 361.1 | 435.7 | 312.1 | 401.5 | 51.2 | 97 | 130.1 | 114.6 | 215 | 203.2 | 103.9 | 181.5 | 186.5 | 146
1157.3 | 938.3 | 376.4 | 150.56 | 175.996 | 207.7 | 181.9 | 206.8 | 207.8 | 297.3 | 34.9 | 20.9 | 64.1 | 6.2 | 240.5 | 7.5 | 684.8 | 660.6 | 680.4 | 663.3 | 556.2 | 335.4 | 369.8 | 442.1 | 317.3 | 404.6 | 51.2 | 97.1 | 130.2 | 114.6 | 215.3 | 203.5 | 104 | 181.8 | 186.7 | 146.2
1158.3 | 939.3 | 376.2 | 150.48 | 175.9024 | 207.1 | 182.6 | 205.6 | 208.4 | 299.1 | 35 | 20.9 | 64.1 | 6.7 | 250.7 | 6.6 | 686.4 | 660.7 | 684.1 | 665.8 | 555.7 | 335.6 | 371 | 440.6 | 318.3 | 405 | 51.3 | 97.2 | 130.4 | 114.7 | 215.3 | 203.3 | 104 | 181.7 | 186.9 | 146.3
1159.3 | 940.3 | 376.5 | 150.6 | 176.0427 | 206.7 | 182.9 | 205.8 | 208.5 | 300.6 | 35.1 | 20.9 | 64 | 7.1 | 236.6 | 6.8 | 685.7 | 640.8 | 668 | 664.2 | 554.9 | 335.8 | 369.6 | 435.3 | 317.2 | 404 | 51.4 | 97.3 | 130.4 | 114.8 | 215.2 | 203.2 | 104.1 | 181.8 | 187.1 | 146.4
1160.3 | 941.3 | 376.5 | 150.6 | 176.0427 | 205.4 | 183.3 | 206.6 | 208.7 | 301.3 | 35.2 | 20.9 | 63.9 | 7.5 | 243.9 | 7.9 | 684.3 | 631.4 | 658.2 | 660.8 | 553.4 | 336 | 368.8 | 432.7 | 316.4 | 403.4 | 51.4 | 97.4 | 130.5 | 114.8 | 215.2 | 203.9 | 104.2 | 181.8 | 187.3 | 146.5
1161.3 | 942.3 | 376.7 | 150.68 | 176.1362 | 205.1 | 183.2 | 205.8 | 208.6 | 303.8 | 35.2 | 20.9 | 63.8 | 6.5 | 240.5 | 8.4 | 681.5 | 612.3 | 650.1 | 655.1 | 552.3 | 336.2 | 366.2 | 424.1 | 315.4 | 402.1 | 51.5 | 97.4 | 130.5 | 114.9 | 214.8 | 204.3 | 104.3 | 181.9 | 187.4 | 146.6
1162.3 | 943.3 | 376.8 | 150.72 | 176.183 | 204.8 | 181.8 | 204.7 | 208.4 | 300.8 | 35.2 | 20.9 | 63.7 | 6.9 | 235.5 | 8.8 | 679.1 | 608.4 | 641.3 | 649.1 | 550.1 | 336.4 | 363.2 | 421.4 | 314.3 | 401.1 | 51.6 | 97.5 | 130.6 | 114.9 | 214.6 | 204 | 104.4 | 181.9 | 187.5 | 146.7
1163.3 | 944.3 | 376.9 | 150.76 | 176.2298 | 204.8 | 181.5 | 204.9 | 207.3 | 302.2 | 35.2 | 20.9 | 63.6 | 8.4 | 225.4 | 8.5 | 680.3 | 623.5 | 631.4 | 649.2 | 550.8 | 336.6 | 365.6 | 431.8 | 315.4 | 401.9 | 51.6 | 97.6 | 130.8 | 115 | 214.5 | 203.8 | 104.4 | 181.9 | 187.6 | 146.8
1164.3 | 945.3 | 375.4 | 150.16 | 175.5284 | 204.3 | 182.2 | 204.7 | 205.9 | 301.9 | 35.1 | 20.9 | 63.7 | 10.3 | 215.2 | 8.5 | 678.7 | 609.5 | 624.2 | 646.4 | 550 | 336.8 | 363 | 423.4 | 314.1 | 400.2 | 51.7 | 97.7 | 130.9 | 115 | 214.3 | 203.8 | 104.6 | 182 | 187.7 | 146.9
1165.3 | 946.3 | 376.3 | 150.52 | 175.9492 | 203.8 | 183.4 | 204.9 | 205.4 | 299 | 35.1 | 20.9 | 63.7 | 10.2 | 210.1 | 9.2 | 678.1 | 609.6 | 625.9 | 643 | 549.9 | 337 | 361.7 | 420.8 | 312.9 | 399.7 | 51.8 | 97.8 | 131 | 115.1 | 214.2 | 204 | 104.6 | 182 | 187.8 | 147
1166.3 | 947.3 | 378 | 151.2 | 176.7441 | 203.5 | 184.2 | 205.9 | 205 | 297.9 | 35.1 | 20.9 | 63.6 | 9.2 | 224.5 | 9 | 677.4 | 615.6 | 623.2 | 640.9 | 549.9 | 337.2 | 360.1 | 415.1 | 312.1 | 399.6 | 51.8 | 97.8 | 131.2 | 115.2 | 214.2 | 203.9 | 104.7 | 182.1 | 187.9 | 147.1
1167.3 | 948.3 | 377.5 | 151 | 176.5103 | 203.2 | 184.5 | 207 | 204.3 | 295.2 | 35.1 | 20.9 | 63.6 | 9.3 | 201.9 | 10.4 | 678.1 | 630.9 | 637.7 | 640.3 | 550.6 | 337.4 | 359.2 | 417.3 | 311.9 | 399.4 | 51.9 | 97.9 | 131.3 | 115.2 | 213.7 | 204 | 104.8 | 182 | 188 | 147.1
1168.3 | 949.3 | 377.7 | 151.08 | 176.6038 | 203 | 185.5 | 208.2 | 204.1 | 295.4 | 35.1 | 20.9 | 63.6 | 9.4 | 224.6 | 9.2 | 679.5 | 644.9 | 645.5 | 641.3 | 550.3 | 337.6 | 360.6 | 430 | 312.5 | 399.8 | 52 | 98 | 131.6 | 115.3 | 213.1 | 203.9 | 104.9 | 182 | 188.1 | 147.2
1169.3 | 950.3 | 378.3 | 151.32 | 176.8844 | 202.7 | 187.1 | 208.5 | 203.7 | 296.4 | 35.1 | 20.9 | 63.7 | 8.9 | 200.8 | 8.1 | 678 | 633.4 | 627.8 | 637.1 | 548.4 | 337.7 | 359.4 | 428.3 | 312.2 | 398.9 | 52 | 98.1 | 131.7 | 115.4 | 212.7 | 203.4 | 104.9 | 181.9 | 188.2 | 147.3
1170.3 | 951.3 | 377.4 | 150.96 | 176.4635 | 202.8 | 188.6 | 208.3 | 203 | 294.4 | 35 | 20.9 | 63.8 | 8 | 214.5 | 7.3 | 674.7 | 610.1 | 613.6 | 632.9 | 546.5 | 338 | 355.7 | 417.3 | 310.7 | 397.3 | 52.1 | 98.2 | 131.7 | 115.4 | 212.4 | 203.1 | 105.1 | 182 | 188.3 | 147.4
1171.3 | 952.3 | 376.7 | 150.68 | 176.1362 | 203.2 | 188.8 | 208.5 | 203.4 | 290.6 | 35 | 20.9 | 64 | 7.9 | 205.8 | 6 | 669.8 | 584.2 | 593.7 | 627.9 | 544.3 | 338.1 | 351.8 | 406.3 | 308.9 | 395.8 | 52.2 | 98.3 | 131.7 | 115.5 | 212.2 | 203 | 105.1 | 182.1 | 188.4 | 147.5
1172.3 | 953.3 | 376.1 | 150.44 | 175.8557 | 204 | 189 | 208.2 | 203.7 | 285.9 | 35.1 | 20.9 | 64 | 8.4 | 231.2 | 5 | 663.6 | 558.1 | 573.9 | 621.4 | 541.9 | 338.3 | 346.1 | 394.2 | 306.5 | 394 | 52.2 | 98.4 | 131.7 | 115.6 | 212.1 | 203.1 | 105.2 | 182.1 | 188.5 | 147.6
1173.3 | 954.3 | 377.7 | 151.08 | 176.6038 | 205.7 | 189.3 | 208 | 203.3 | 281.9 | 35.1 | 20.9 | 64.1 | 8.6 | 298.9 | 4.4 | 659.8 | 546 | 573.4 | 616.8 | 541.6 | 338.5 | 342.2 | 387 | 304.6 | 392.8 | 52.3 | 98.5 | 131.9 | 115.6 | 212 | 202.9 | 105.3 | 182.1 | 188.6 | 147.7
1174.3 | 955.3 | 378.4 | 151.36 | 176.9311 | 206.5 | 190.3 | 206.8 | 203.4 | 280.9 | 35.2 | 20.9 | 64.1 | 7.8 | 284.3 | 4.5 | 657.6 | 547.4 | 573.3 | 613.1 | 541.1 | 338.7 | 341.2 | 384.6 | 304.1 | 392.1 | 52.4 | 98.6 | 131.9 | 115.7 | 212 | 202.4 | 105.4 | 182.2 | 188.6 | 147.8
1175.3 | 956.3 | 378.5 | 151.4 | 176.9779 | 207 | 191.3 | 204.5 | 203 | 284.6 | 35.2 | 20.9 | 64.2 | 7.3 | 234.8 | 6.6 | 657 | 549.7 | 568.9 | 611.1 | 539.2 | 338.9 | 339.3 | 384 | 303 | 390.9 | 52.4 | 98.6 | 132.1 | 115.8 | 211.6 | 202.4 | 105.5 | 182.2 | 188.7 | 147.9
1176.3 | 957.3 | 378.2 | 151.28 | 176.8376 | 207.2 | 191.1 | 203.9 | 203 | 284.7 | 35.2 | 20.9 | 64.4 | 7.7 | 236.5 | 8.1 | 659.4 | 574.8 | 580.2 | 612.4 | 539.7 | 339.1 | 338.8 | 384.1 | 302.1 | 390.5 | 52.5 | 98.7 | 132.2 | 115.8 | 211.5 | 202.4 | 105.6 | 182.1 | 188.8 | 147.9
1177.3 | 958.3 | 379.4 | 151.76 | 177.3987 | 206.9 | 190.9 | 204.8 | 202.8 | 286.4 | 35.2 | 20.9 | 64.5 | 8.1 | 233.5 | 8.8 | 662.3 | 571.5 | 581.2 | 616.9 | 540.2 | 339.3 | 342.1 | 383.2 | 303.7 | 391.7 | 52.6 | 98.8 | 132.2 | 115.9 | 211.6 | 202.5 | 105.6 | 182.1 | 188.9 | 148
1178.3 | 959.3 | 377.2 | 150.88 | 176.37 | 207.8 | 191.4 | 204.8 | 202.1 | 286.5 | 35.2 | 20.9 | 64.5 | 8.6 | 222.8 | 11.4 | 661.7 | 562.2 | 578.4 | 618.1 | 539.4 | 339.5 | 342.4 | 378.7 | 303.8 | 391.2 | 52.6 | 98.9 | 132.3 | 115.9 | 211.6 | 202.3 | 105.7 | 182.2 | 189 | 148.1
1179.3 | 960.3 | 375.6 | 150.24 | 175.6219 | 208.5 | 191.6 | 204.2 | 202.2 | 286.2 | 35.2 | 20.9 | 64.5 | 8.3 | 232 | 11.1 | 662.5 | 563.7 | 570.3 | 619.7 | 539.7 | 339.7 | 342.7 | 378 | 303.4 | 391.1 | 52.7 | 99 | 132.5 | 116 | 211.6 | 202.1 | 105.8 | 182.3 | 189.1 | 148.2
1180.3 | 961.3 | 376.4 | 150.56 | 175.996 | 209.1 | 191.9 | 203.6 | 202.8 | 286 | 35.1 | 20.9 | 64.6 | 8.9 | 215.3 | 10.4 | 661.7 | 556.3 | 562 | 619.8 | 539 | 339.9 | 342.9 | 377.5 | 303.2 | 390.6 | 52.8 | 99.1 | 132.4 | 116.1 | 211.8 | 202 | 105.9 | 182.3 | 189.2 | 148.3
1181.3 | 962.3 | 377.4 | 150.96 | 176.4635 | 208.4 | 192.1 | 203.3 | 203.3 | 284.5 | 35.1 | 20.9 | 64.6 | 9 | 221.2 | 9.1 | 660.1 | 554 | 566.2 | 619.4 | 537.8 | 340.1 | 342.6 | 377.9 | 303 | 390.2 | 52.8 | 99.2 | 132.4 | 116.1 | 211.4 | 202.3 | 105.9 | 182.3 | 189.3 | 148.4
1182.3 | 963.3 | 377.2 | 150.88 | 176.37 | 208.7 | 191.8 | 203 | 204 | 283 | 35 | 20.9 | 64.6 | 8.3 | 209.4 | 10.7 | 664.8 | 575.4 | 593.4 | 626.7 | 540.8 | 340.3 | 345.4 | 384.1 | 304.8 | 391.8 | 52.9 | 99.3 | 132.5 | 116.2 | 211.3 | 202.2 | 106 | 182.3 | 189.4 | 148.5
1183.3 | 964.3 | 376.2 | 150.48 | 175.9024 | 208 | 190.9 | 203 | 204.3 | 285.2 | 35.1 | 20.8 | 64.7 | 8.3 | 200.1 | 10 | 665.8 | 586.5 | 598.9 | 626.9 | 541.7 | 340.5 | 345.7 | 394.5 | 305.2 | 391.3 | 53 | 99.4 | 132.8 | 116.2 | 211.5 | 201.9 | 106.1 | 182.3 | 189.5 | 148.7
1184.3 | 965.3 | 377.2 | 150.88 | 176.37 | 207.3 | 190.3 | 202.6 | 204.9 | 288.8 | 35.1 | 20.9 | 64.7 | 7.9 | 211.6 | 9.6 | 668.1 | 617.7 | 608.1 | 629.2 | 541.8 | 340.7 | 346 | 409.8 | 305 | 390.7 | 53 | 99.5 | 133 | 116.3 | 211.6 | 202.3 | 106.2 | 182.3 | 189.6 | 148.8
1185.3 | 966.3 | 378.5 | 151.4 | 176.9779 | 206.4 | 190.4 | 202.4 | 204.9 | 296.5 | 35.1 | 20.9 | 64.7 | 7.8 | 231.6 | 9.7 | 670.5 | 626.7 | 618.4 | 631.7 | 542 | 340.9 | 346.9 | 424.1 | 306 | 390.6 | 53.1 | 99.6 | 133.5 | 116.4 | 211.7 | 202.4 | 106.3 | 182.3 | 189.8 | 148.9
1186.3 | 967.3 | 378.5 | 151.4 | 176.9779 | 205.8 | 191.1 | 204.1 | 206 | 304.9 | 35.1 | 20.9 | 64.8 | 7.8 | 212.6 | 9 | 674.8 | 638.2 | 634.6 | 637.8 | 545.9 | 341 | 353.1 | 442.9 | 308.3 | 392.3 | 53.2 | 99.6 | 133.3 | 116.4 | 211.6 | 202.3 | 106.4 | 182.4 | 189.9 | 149
1187.3 | 968.3 | 378.3 | 151.32 | 176.8844 | 205.2 | 191.9 | 205.8 | 206.3 | 310.1 | 35.1 | 20.9 | 64.9 | 7.6 | 221.3 | 9 | 675.6 | 630.8 | 632 | 637.7 | 545.1 | 341.2 | 356.6 | 437.3 | 309.7 | 392.8 | 53.2 | 99.7 | 133.3 | 116.5 | 212.2 | 202.7 | 106.5 | 182.4 | 190 | 149.1
1188.3 | 969.3 | 379 | 151.6 | 177.2117 | 205 | 192.8 | 207 | 206.5 | 310 | 35.2 | 20.9 | 64.9 | 8.9 | 220.9 | 9.8 | 679.4 | 645.6 | 652.1 | 643.6 | 547.6 | 341.4 | 361.5 | 450.8 | 311.5 | 394.6 | 53.3 | 99.8 | 133.5 | 116.5 | 212.4 | 202.7 | 106.5 | 182.4 | 190.2 | 149.2
1189.3 | 970.3 | 377.6 | 151.04 | 176.5571 | 204.6 | 193.1 | 207.1 | 207.2 | 315.5 | 35.3 | 20.8 | 64.9 | 8.7 | 233.7 | 8.5 | 684.8 | 660.2 | 672.5 | 653.5 | 550.5 | 341.6 | 366.9 | 468 | 314.7 | 397.5 | 53.4 | 99.9 | 133.6 | 116.6 | 213 | 203.2 | 106.7 | 182.5 | 190.3 | 149.3
1190.3 | 971.3 | 378.9 | 151.56 | 177.1649 | 203.9 | 193.1 | 206.3 | 207.7 | 323.3 | 35.4 | 20.9 | 64.9 | 7.8 | 219.2 | 7.5 | 688.8 | 658.2 | 678.5 | 660.4 | 552.8 | 341.8 | 372 | 473.7 | 318.5 | 398.6 | 53.5 | 99.9 | 133.7 | 116.7 | 213.3 | 203.1 | 106.7 | 182.5 | 190.5 | 149.4
1191.3 | 972.3 | 377.8 | 151.12 | 176.6506 | 203.9 | 192.5 | 205.8 | 208.5 | 325.6 | 35.4 | 20.8 | 64.9 | 7.7 | 208.8 | 7.9 | 690.6 | 655.4 | 685.6 | 664.4 | 553.8 | 342 | 373.9 | 474.1 | 318.8 | 399.1 | 53.5 | 100 | 133.7 | 116.7 | 213.7 | 203.1 | 106.8 | 182.6 | 190.7 | 149.5
1192.3 | 973.3 | 375.9 | 150.36 | 175.7622 | 204.2 | 192.6 | 205.3 | 209.5 | 328.6 | 35.4 | 20.8 | 64.8 | 7.2 | 242.3 | 6 | 690.8 | 658.4 | 690.1 | 666.6 | 555.4 | 342.2 | 375.9 | 482.6 | 320.2 | 400.6 | 53.6 | 100.1 | 133.9 | 116.8 | 214.6 | 203.2 | 106.8 | 182.6 | 190.9 | 149.6
1193.3 | 974.3 | 376.2 | 150.48 | 175.9024 | 204.1 | 192.9 | 205.9 | 209.7 | 330 | 35.5 | 20.8 | 64.8 | 7.3 | 235 | 5 | 691.5 | 659 | 695.3 | 668 | 557.1 | 342.4 | 376.6 | 484.6 | 320.8 | 401.2 | 53.6 | 100.2 | 134 | 116.9 | 214.7 | 203.4 | 107 | 182.7 | 191 | 149.7
1194.3 | 975.3 | 376.1 | 150.44 | 175.8557 | 203.4 | 193.7 | 206.4 | 209.5 | 326 | 35.5 | 20.8 | 64.9 | 7.7 | 262.6 | 7 | 692.9 | 666.4 | 701.4 | 668.8 | 559.1 | 342.6 | 377.6 | 481.4 | 321.9 | 403 | 53.7 | 100.3 | 134.3 | 116.9 | 215 | 203.1 | 107.1 | 182.8 | 191.2 | 149.8
1195.3 | 976.3 | 375.1 | 150.04 | 175.3881 | 202.8 | 194.5 | 206.7 | 209.1 | 323.9 | 35.5 | 20.8 | 64.9 | 7.7 | 261.2 | 11.7 | 694.9 | 673.8 | 709.3 | 671 | 562.1 | 342.7 | 379.7 | 484.9 | 323.1 | 404 | 53.8 | 100.3 | 134.3 | 117 | 215.3 | 203.3 | 107.1 | 182.8 | 191.4 | 149.9
1196.3 | 977.3 | 375.1 | 150.04 | 175.3881 | 202.8 | 195.3 | 207.2 | 209 | 325 | 35.5 | 20.8 | 64.9 | 7.3 | 232 | 11.6 | 699.4 | 677.6 | 708.2 | 678.8 | 563.6 | 342.9 | 382.8 | 484.9 | 324.6 | 405.2 | 53.9 | 100.4 | 134.5 | 117.1 | 215.7 | 203.5 | 107.2 | 182.9 | 191.5 | 150
1197.3 | 978.3 | 377.3 | 150.92 | 176.4168 | 202.6 | 196 | 207.3 | 208.9 | 324.4 | 35.4 | 20.8 | 65 | 6.9 | 244.5 | 11.5 | 700.3 | 668.6 | 701.4 | 679.1 | 563.1 | 343.1 | 382.5 | 478.4 | 324 | 404.5 | 53.9 | 100.5 | 134.4 | 117.1 | 215.6 | 203.6 | 107.3 | 183 | 191.7 | 150.1
1198.3 | 979.3 | 376.8 | 150.72 | 176.183 | 202.8 | 196.3 | 207.5 | 208.8 | 325.1 | 35.4 | 20.8 | 65.1 | 6.6 | 261.1 | 10.4 | 703.5 | 690.9 | 698.8 | 681.6 | 565 | 343.3 | 384.4 | 493.2 | 324.9 | 406.3 | 54 | 100.6 | 134.6 | 117.2 | 215.2 | 204.2 | 107.4 | 183 | 191.8 | 150.2
1199.3 | 980.3 | 376.4 | 150.56 | 175.996 | 203 | 196 | 207.6 | 208.9 | 323.9 | 35.4 | 20.8 | 65.2 | 6.5 | 238.1 | 9.4 | 702.9 | 671.8 | 689.5 | 681.4 | 565.4 | 343.5 | 386.6 | 480.9 | 326.5 | 408.2 | 54.1 | 100.7 | 134.7 | 117.3 | 214.9 | 204.5 | 107.5 | 183 | 192 | 150.3
1200.3 | 981.3 | 375.8 | 150.32 | 175.7154 | 202.4 | 195.4 | 208.1 | 208.2 | 320.7 | 35.5 | 20.8 | 65.3 | 6.1 | 254.9 | 9.3 | 702.9 | 671 | 681.5 | 681.9 | 564.1 | 343.7 | 385.7 | 472.9 | 326.3 | 408.1 | 54.1 | 100.7 | 134.8 | 117.4 | 214.8 | 204.4 | 107.5 | 183 | 192.1 | 150.4
1201.3 | 982.3 | 375.8 | 150.32 | 175.7154 | 201.9 | 194.4 | 208 | 208.2 | 318.7 | 35.5 | 20.8 | 65.3 | 5.9 | 252.6 | 9.3 | 705.5 | 675.9 | 682.7 | 688 | 565.4 | 344 | 387.1 | 471.6 | 327.5 | 410.2 | 54.2 | 100.8 | 134.9 | 117.4 | 214.5 | 204.1 | 107.6 | 183.1 | 192.3 | 150.5
1202.3 | 983.3 | 376.2 | 150.48 | 175.9024 | 201.4 | 193.2 | 207.9 | 208.3 | 318.8 | 35.5 | 20.8 | 65.4 | 6.5 | 249.2 | 10.5 | 708.8 | 677.4 | 687.9 | 694.2 | 567.7 | 344.2 | 395.2 | 477.5 | 332.5 | 414.5 | 54.3 | 100.9 | 135 | 117.5 | 214.4 | 204.1 | 107.7 | 183.1 | 192.4 | 150.6
1203.3 | 984.3 | 378.1 | 151.24 | 176.7908 | 202.1 | 192.2 | 208.4 | 208.5 | 321.2 | 35.5 | 20.8 | 65.4 | 6.7 | 245.9 | 12.2 | 710.2 | 694.1 | 689.6 | 696.4 | 567.9 | 344.4 | 400.6 | 497.5 | 336.2 | 415.7 | 54.3 | 101 | 135.1 | 117.6 | 214.5 | 203.8 | 107.8 | 183.2 | 192.6 | 150.7
1204.3 | 985.3 | 378 | 151.2 | 176.7441 | 202.4 | 191.5 | 208.7 | 208.2 | 329.8 | 35.5 | 20.8 | 65.4 | 6.7 | 246.2 | 11.7 | 714.2 | 708 | 705.4 | 702.1 | 570.1 | 344.6 | 403.3 | 507.2 | 337.6 | 416.5 | 54.4 | 101.1 | 135.4 | 117.6 | 214.7 | 203.9 | 107.8 | 183.2 | 192.8 | 150.8
1205.3 | 986.3 | 378.1 | 151.24 | 176.7908 | 201.9 | 191.6 | 209.6 | 208.4 | 335.1 | 35.5 | 20.8 | 65.4 | 6.9 | 249.7 | 11.3 | 716.8 | 711.8 | 703.8 | 704.4 | 571.9 | 344.8 | 405.3 | 517.7 | 338.8 | 418 | 54.5 | 101.2 | 135.5 | 117.7 | 214.8 | 203.9 | 107.9 | 183.3 | 193 | 150.9
1206.3 | 987.3 | 377.9 | 151.16 | 176.6973 | 201.8 | 191.1 | 210.7 | 209.5 | 335.9 | 35.6 | 20.8 | 65.4 | 6.9 | 250.9 | 11.1 | 716.2 | 696 | 693.9 | 702.2 | 571.9 | 345 | 405.4 | 510.7 | 338.1 | 417.5 | 54.5 | 101.2 | 135.6 | 117.8 | 214.7 | 204.6 | 108 | 183.3 | 193.2 | 151
1207.3 | 988.3 | 377.9 | 151.16 | 176.6973 | 202.3 | 190.7 | 210.4 | 210.3 | 335 | 35.6 | 20.8 | 65.4 | 7.6 | 269.9 | 9.7 | 716.6 | 689.9 | 684.6 | 701.7 | 571.2 | 345.2 | 406.7 | 505.7 | 338.8 | 418.8 | 54.6 | 101.3 | 135.7 | 117.8 | 214.7 | 205.6 | 108.1 | 183.5 | 193.3 | 151.1
1208.3 | 989.3 | 377.7 | 151.08 | 176.6038 | 202.3 | 190.2 | 210.2 | 210.1 | 331.3 | 35.6 | 20.8 | 65.4 | 7.9 | 254.5 | 9.1 | 719 | 698.7 | 685 | 704.3 | 571.3 | 345.4 | 408.1 | 507.8 | 339.8 | 421.8 | 54.7 | 101.4 | 135.7 | 117.9 | 215 | 205.8 | 108.2 | 183.6 | 193.5 | 151.2
1209.3 | 990.3 | 377.5 | 151 | 176.5103 | 202.3 | 190.8 | 210.9 | 210.7 | 332.1 | 35.6 | 20.8 | 65.4 | 8.5 | 263.9 | 9.3 | 719.5 | 687.8 | 672.1 | 702.8 | 569.9 | 345.7 | 407.1 | 502.7 | 339.5 | 421 | 54.7 | 101.5 | 135.9 | 118 | 215.9 | 206.7 | 108.3 | 183.7 | 193.7 | 151.3
1210.3 | 991.3 | 377.6 | 151.04 | 176.5571 | 202.9 | 191.3 | 211.2 | 210.9 | 332.7 | 35.6 | 20.8 | 65.4 | 9.1 | 280 | 8.7 | 719.5 | 690.6 | 657.6 | 701.3 | 568.3 | 345.9 | 406.3 | 503.6 | 338.7 | 420.9 | 54.8 | 101.6 | 136.1 | 118.1 | 216 | 206.8 | 108.4 | 183.8 | 193.9 | 151.5
1211.3 | 992.3 | 377.4 | 150.96 | 176.4635 | 203.7 | 192.4 | 211.7 | 210.8 | 335 | 35.6 | 20.8 | 65.4 | 9 | 256.9 | 10.4 | 719.3 | 696.6 | 660.1 | 700.7 | 567.4 | 346.1 | 405.1 | 499.2 | 337.5 | 420.9 | 54.9 | 101.6 | 136.3 | 118.1 | 216.2 | 206.9 | 108.4 | 183.8 | 194 | 151.6
1212.3 | 993.3 | 377.4 | 150.96 | 176.4635 | 203.7 | 193 | 212 | 211.4 | 333.7 | 35.6 | 20.8 | 65.3 | 9.3 | 258.2 | 11.5 | 718.5 | 690.9 | 652.9 | 698.1 | 566.9 | 346.3 | 403.7 | 490 | 336.9 | 420.5 | 54.9 | 101.7 | 136.4 | 118.2 | 216.5 | 207.2 | 108.5 | 183.9 | 194.1 | 151.7
1213.3 | 994.3 | 377.4 | 150.96 | 176.4635 | 204.6 | 193.8 | 212.1 | 210.9 | 331.8 | 35.6 | 20.8 | 65.3 | 9.3 | 265.3 | 11.6 | 716.2 | 679.7 | 649.9 | 694.1 | 564.7 | 346.6 | 400.7 | 483.5 | 335.6 | 419.7 | 55 | 101.8 | 136.4 | 118.3 | 216.7 | 207.2 | 108.6 | 184 | 194.2 | 151.8
1214.3 | 995.3 | 377.3 | 150.92 | 176.4168 | 205.2 | 194.6 | 212.4 | 211 | 327.4 | 35.7 | 20.8 | 65.3 | 8.9 | 271.1 | 11.3 | 715.1 | 664.5 | 652.5 | 690.5 | 564.3 | 346.8 | 397.5 | 483.3 | 334.4 | 418.8 | 55.1 | 101.9 | 136.5 | 118.4 | 217.2 | 207.1 | 108.7 | 184 | 194.3 | 151.9
1215.3 | 996.3 | 377.3 | 150.92 | 176.4168 | 205.6 | 195.2 | 212.6 | 211.2 | 325.7 | 35.7 | 20.8 | 65.3 | 9.2 | 272.9 | 11.6 | 714.4 | 649.5 | 652.4 | 688.4 | 564.5 | 347 | 396.3 | 480.9 | 334.3 | 418.5 | 55.1 | 102 | 136.7 | 118.4 | 217.6 | 207.2 | 108.8 | 184.1 | 194.4 | 152.1
1216.3 | 997.3 | 377.3 | 150.92 | 176.4168 | 206.1 | 195.6 | 213.8 | 211.9 | 323.7 | 35.7 | 20.8 | 65.2 | 9.1 | 275.3 | 11.8 | 717.2 | 665.7 | 666 | 691.9 | 566.3 | 347.2 | 396.8 | 484 | 334.5 | 419.2 | 55.2 | 102.1 | 136.9 | 118.5 | 218.1 | 207.6 | 108.9 | 184.2 | 194.5 | 152.2
1217.3 | 998.3 | 377.2 | 150.88 | 176.37 | 206.5 | 196.5 | 213.9 | 211.8 | 326.2 | 35.7 | 20.8 | 65.2 | 8.8 | 270.9 | 12.4 | 720.5 | 675.2 | 676.5 | 695.9 | 568.1 | 347.5 | 399 | 487.8 | 336 | 419.8 | 55.3 | 102.2 | 137 | 118.6 | 218.4 | 207.7 | 109 | 184.3 | 194.7 | 152.3
1218.3 | 999.3 | 377.3 | 150.92 | 176.4168 | 206.8 | 197.1 | 212.7 | 211.9 | 326.3 | 35.6 | 20.8 | 65.2 | 8.4 | 274 | 11.9 | 722.3 | 682.9 | 681.6 | 698 | 569.3 | 347.7 | 398.3 | 488.7 | 335.9 | 419.6 | 55.3 | 102.3 | 137.1 | 118.7 | 218.6 | 207.6 | 109.1 | 184.4 | 194.8 | 152.4
1219.3 | 1000.3 | 377.4 | 150.96 | 176.4635 | 207.6 | 198 | 212.9 | 212.8 | 327.1 | 35.6 | 20.8 | 65.1 | 8.7 | 275.1 | 11.3 | 722 | 664.9 | 678.3 | 698.4 | 568.7 | 348 | 396.9 | 480.8 | 335.1 | 419.8 | 55.4 | 102.4 | 137.3 | 118.7 | 219 | 208.1 | 109.1 | 184.4 | 195 | 152.6
1220.3 | 1001.3 | 377.4 | 150.96 | 176.4635 | 207.3 | 198.6 | 212.9 | 213.6 | 325.6 | 35.6 | 20.8 | 65.1 | 8.6 | 290.2 | 10.8 | 721.9 | 661.6 | 687.3 | 699.2 | 570.3 | 348.3 | 396.3 | 473.4 | 335 | 420.6 | 55.5 | 102.5 | 137.3 | 118.8 | 218.9 | 208.8 | 109.2 | 184.5 | 195.1 | 152.7
1221.3 | 1002.3 | 377.5 | 151 | 176.5103 | 206.5 | 198.9 | 213 | 213.6 | 322.8 | 35.6 | 20.8 | 65.1 | 9.2 | 283.2 | 11.9 | 724.1 | 672.2 | 702.6 | 702.3 | 571.4 | 348.5 | 397.3 | 477.3 | 335.8 | 421.5 | 55.5 | 102.6 | 137.3 | 118.9 | 219.6 | 209.1 | 109.3 | 184.6 | 195.3 | 152.8
1222.3 | 1003.3 | 377.4 | 150.96 | 176.4635 | 206.3 | 198.7 | 213.7 | 213.7 | 321.6 | 35.5 | 20.8 | 65 | 8.4 | 293.8 | 12.8 | 724.5 | 656.2 | 686.4 | 703.2 | 570 | 348.8 | 399.4 | 473.1 | 338 | 423.1 | 55.6 | 102.7 | 137.3 | 119 | 220.2 | 209.7 | 109.4 | 184.7 | 195.5 | 152.9
1223.3 | 1004.3 | 377.6 | 151.04 | 176.5571 | 206.3 | 199.4 | 213.6 | 213.9 | 318.7 | 35.5 | 20.8 | 65 | 8.3 | 293.4 | 12.4 | 721.7 | 644 | 676.2 | 699.9 | 569.9 | 349 | 397.7 | 462.4 | 337.2 | 421.8 | 55.7 | 102.9 | 137.4 | 119.1 | 220.3 | 210.2 | 109.5 | 184.9 | 195.6 | 153.1
1224.3 | 1005.3 | 377.3 | 150.92 | 176.4168 | 206.3 | 200.3 | 213.9 | 213.6 | 313.8 | 35.6 | 20.8 | 65 | 7.6 | 301.3 | 10.4 | 716.3 | 617.5 | 661.6 | 692.8 | 566.8 | 349.3 | 392.1 | 446.8 | 334.9 | 419.5 | 55.7 | 103 | 137.5 | 119.1 | 220.7 | 211.1 | 109.5 | 185 | 195.8 | 153.2
1225.3 | 1006.3 | 377.2 | 150.88 | 176.37 | 206.5 | 200 | 213.3 | 212.8 | 307.8 | 35.6 | 20.8 | 65 | 8.7 | 289.2 | 10 | 711.9 | 621.1 | 651.8 | 685.7 | 564.4 | 349.5 | 388 | 445.4 | 332.9 | 418.2 | 55.8 | 103.1 | 137.6 | 119.2 | 220.6 | 211.7 | 109.6 | 185 | 195.9 | 153.3
1226.3 | 1007.3 | 378.7 | 151.48 | 177.0714 | 207.1 | 198.9 | 212.8 | 212.9 | 309.4 | 35.6 | 20.8 | 64.9 | 8.2 | 292.5 | 10.4 | 711.8 | 618.5 | 640.9 | 682.9 | 563.7 | 349.7 | 386.6 | 442.9 | 332.3 | 417.6 | 55.9 | 103.2 | 137.8 | 119.3 | 220.4 | 212.2 | 109.7 | 185.2 | 195.9 | 153.4
1227.3 | 1008.3 | 377.8 | 151.12 | 176.6506 | 206.7 | 198.4 | 212.9 | 212.1 | 307.8 | 35.7 | 20.8 | 64.8 | 8.8 | 283.5 | 10.9 | 709.4 | 609.4 | 632.6 | 678.9 | 562.1 | 349.9 | 382.6 | 431.4 | 330.6 | 416.3 | 55.9 | 103.3 | 137.8 | 119.4 | 220.3 | 212.4 | 109.8 | 185.2 | 196 | 153.4
1228.3 | 1009.3 | 377.8 | 151.12 | 176.6506 | 206.6 | 197.7 | 213.5 | 211.7 | 304.4 | 35.7 | 20.8 | 64.8 | 7.8 | 286.7 | 10.9 | 710.4 | 619.6 | 635.2 | 678.7 | 562.4 | 350.2 | 380.5 | 434.1 | 330 | 416.9 | 56 | 103.5 | 137.9 | 119.5 | 219.8 | 212.3 | 109.9 | 185.3 | 196.1 | 153.5
1229.3 | 1010.3 | 377.9 | 151.16 | 176.6973 | 207.3 | 197 | 213.4 | 211.4 | 308.4 | 35.7 | 20.8 | 64.8 | 7.4 | 283.2 | 10.5 | 713.9 | 648.6 | 652.8 | 682.3 | 562.6 | 350.5 | 382.2 | 443.4 | 331.9 | 418 | 56.1 | 103.6 | 138 | 119.6 | 219.4 | 212.2 | 109.9 | 185.3 | 196.2 | 153.7
1230.3 | 1011.3 | 378.6 | 151.44 | 177.0246 | 207.7 | 196.5 | 212.8 | 212.4 | 311.8 | 35.8 | 20.8 | 65 | 7.5 | 284 | 10.5 | 718.4 | 670.7 | 673.3 | 688.1 | 567.4 | 350.8 | 390.3 | 463.2 | 336.5 | 421.7 | 56.1 | 103.7 | 138.1 | 119.7 | 218.9 | 212.4 | 110 | 185.4 | 196.4 | 153.7
1231.3 | 1012.3 | 377.3 | 150.92 | 176.4168 | 208.2 | 196.7 | 213.3 | 212.8 | 314.2 | 35.8 | 20.8 | 65.2 | 7.8 | 275.2 | 11.4 | 720.7 | 690.8 | 695.9 | 690.7 | 571.4 | 351 | 396.7 | 477.8 | 340.9 | 425.5 | 56.2 | 103.8 | 138.3 | 119.8 | 218.6 | 212.4 | 110.1 | 185.4 | 196.6 | 153.9
1232.3 | 1013.3 | 376.2 | 150.48 | 175.9024 | 207.7 | 196.2 | 213.4 | 212.3 | 314.4 | 36 | 20.8 | 65.3 | 7.9 | 279.8 | 12.4 | 721.2 | 686.1 | 704.7 | 691.9 | 574.4 | 351.3 | 397.6 | 476.5 | 342.1 | 425.3 | 56.3 | 103.9 | 138.4 | 119.9 | 218.5 | 212 | 110.2 | 185.4 | 196.7 | 154
1233.3 | 1014.3 | 376.3 | 150.52 | 175.9492 | 208 | 195.6 | 213.4 | 212.4 | 314.4 | 36.1 | 20.8 | 65.5 | 7.9 | 277.5 | 12 | 724 | 685.5 | 712.3 | 697.5 | 576 | 351.6 | 402.7 | 483.8 | 345.2 | 426.7 | 56.3 | 104 | 138.4 | 120 | 218.6 | 211.7 | 110.3 | 185.5 | 196.9 | 154.1
1234.3 | 1015.3 | 376.5 | 150.6 | 176.0427 | 207.8 | 194.6 | 213.8 | 213.2 | 320.6 | 36.2 | 20.8 | 65.6 | 8.2 | 278.5 | 11.1 | 723.6 | 691.2 | 714.1 | 697.3 | 576.1 | 351.9 | 407 | 488.2 | 348 | 427.1 | 56.4 | 104.1 | 138.6 | 120.1 | 218.8 | 211.6 | 110.4 | 185.5 | 197.1 | 154.2
1235.3 | 1016.3 | 376.5 | 150.6 | 176.0427 | 207.8 | 193.9 | 213.7 | 213.3 | 320.3 | 36.2 | 20.8 | 65.6 | 8.8 | 283 | 10.6 | 725.7 | 691.8 | 720.8 | 701.2 | 576.4 | 352.1 | 407.9 | 489.2 | 348 | 427 | 56.5 | 104.2 | 138.7 | 120.2 | 219 | 211.3 | 110.4 | 185.6 | 197.3 | 154.3
1236.3 | 1017.3 | 376.4 | 150.56 | 175.996 | 208.1 | 194.7 | 213.5 | 213 | 322.8 | 36.2 | 20.8 | 65.7 | 8.7 | 290.8 | 9.6 | 727.1 | 692.2 | 721.2 | 703.5 | 579 | 352.4 | 412.6 | 482.9 | 350.2 | 431.7 | 56.6 | 104.3 | 138.8 | 120.2 | 219.6 | 211.7 | 110.5 | 185.7 | 197.5 | 154.4
1237.3 | 1018.3 | 376.5 | 150.6 | 176.0427 | 207.9 | 195.1 | 212.4 | 212.9 | 322.3 | 36.2 | 20.8 | 65.7 | 8 | 317.5 | 8.2 | 725.4 | 679.9 | 721.1 | 701.5 | 578.8 | 352.7 | 411.1 | 471.5 | 349.4 | 430.7 | 56.6 | 104.4 | 138.8 | 120.3 | 220.3 | 212.2 | 110.6 | 185.8 | 197.7 | 154.6
1238.3 | 1019.3 | 376.5 | 150.6 | 176.0427 | 209.3 | 195.3 | 212.6 | 212.7 | 319.9 | 36.2 | 20.8 | 65.7 | 8.4 | 314.1 | 7 | 726.3 | 679.1 | 727.8 | 704.3 | 579.7 | 353 | 415.2 | 471.9 | 350.7 | 432.7 | 56.7 | 104.5 | 139.2 | 120.4 | 221.4 | 212.6 | 110.7 | 185.8 | 197.9 | 154.7
1239.3 | 1020.3 | 378 | 151.2 | 176.7441 | 209.4 | 195.6 | 212.9 | 213.2 | 321.6 | 36.2 | 20.8 | 65.7 | 7.7 | 316.5 | 7.6 | 727.5 | 681.2 | 729.6 | 706.2 | 581 | 353.2 | 420.4 | 476.9 | 353.7 | 434.7 | 56.8 | 104.5 | 139.3 | 120.5 | 221.6 | 212.5 | 110.8 | 185.9 | 198 | 154.8
1240.3 | 1021.3 | 377.5 | 151 | 176.5103 | 209.2 | 195.4 | 212.1 | 214.1 | 324.4 | 36.2 | 20.8 | 65.8 | 8.3 | 286 | 8.1 | 730 | 692.8 | 728.6 | 709 | 581.6 | 353.5 | 423.7 | 484.6 | 355 | 435.7 | 56.9 | 104.6 | 139.5 | 120.6 | 221.8 | 211.9 | 110.8 | 185.9 | 198.3 | 154.9
1241.3 | 1022.3 | 376.5 | 150.6 | 176.0427 | 208.7 | 195.5 | 211.6 | 213.9 | 325.1 | 36.1 | 20.8 | 65.8 | 8.7 | 318.2 | 7.3 | 733 | 690 | 729.1 | 713.3 | 585.6 | 353.8 | 428.7 | 480 | 359.8 | 439.3 | 56.9 | 104.7 | 139.6 | 120.7 | 221.8 | 211.8 | 110.9 | 186 | 198.5 | 155
1242.3 | 1023.3 | 378 | 151.2 | 176.7441 | 208.6 | 195.8 | 211.4 | 212.8 | 322 | 36.1 | 20.8 | 65.8 | 8.3 | 287.6 | 8.9 | 733.5 | 687 | 723.5 | 714.9 | 585.3 | 354 | 428.6 | 476.2 | 360.5 | 438.6 | 57 | 104.8 | 139.7 | 120.8 | 221.5 | 211.7 | 111 | 186.1 | 198.7 | 155.1
1243.3 | 1024.3 | 377.6 | 151.04 | 176.5571 | 208 | 195.9 | 211.6 | 212.9 | 321 | 36 | 20.8 | 65.8 | 7.4 | 303.2 | 10 | 734.9 | 679.9 | 722 | 718.9 | 585 | 354.3 | 425.3 | 471.4 | 359.1 | 438.2 | 57.1 | 104.9 | 139.8 | 120.9 | 221.8 | 211.7 | 111.1 | 186.2 | 198.9 | 155.2
1244.3 | 1025.3 | 377.9 | 151.16 | 176.6973 | 207.9 | 196.2 | 211.7 | 213.1 | 323 | 36 | 20.8 | 65.7 | 6.9 | 296.9 | 10.8 | 736.4 | 675.1 | 710.4 | 723.3 | 584.7 | 354.5 | 425.4 | 472.4 | 358.6 | 438.7 | 57.1 | 104.9 | 139.9 | 121 | 222 | 212 | 111.2 | 186.3 | 199 | 155.3
1245.3 | 1026.3 | 377 | 150.8 | 176.2765 | 210.2 | 195.5 | 212 | 213.8 | 323 | 36 | 20.8 | 65.6 | 8.8 | 298.4 | 11.3 | 735.2 | 653.8 | 695.5 | 724.6 | 582.6 | 354.8 | 422.6 | 462.8 | 357.1 | 437.5 | 57.2 | 105 | 140 | 121.1 | 221.8 | 212.4 | 111.2 | 186.3 | 199.2 | 155.4
1246.3 | 1027.3 | 375.8 | 150.32 | 175.7154 | 212.3 | 194.5 | 212.8 | 213 | 321.3 | 35.9 | 20.8 | 65.6 | 7.3 | 292 | 12.4 | 731.9 | 646.4 | 680 | 719.6 | 579.9 | 355 | 420.1 | 459.6 | 355.6 | 436.3 | 57.3 | 105.1 | 140.2 | 121.1 | 221.7 | 212.9 | 111.3 | 186.4 | 199.3 | 155.5
1247.3 | 1028.3 | 375.8 | 150.32 | 175.7154 | 215 | 193.5 | 213.9 | 213.1 | 322.1 | 35.9 | 20.8 | 65.5 | 6.6 | 289.2 | 12.8 | 730.3 | 642.4 | 673 | 715.1 | 578.3 | 355.3 | 417.9 | 460.2 | 354 | 435.4 | 57.4 | 105.2 | 140.2 | 121.2 | 221.8 | 212.6 | 111.4 | 186.5 | 199.4 | 155.6
1248.3 | 1029.3 | 376 | 150.4 | 175.8089 | 215.4 | 193.7 | 214.6 | 213.6 | 320.9 | 35.9 | 20.8 | 65.5 | 6.6 | 279.6 | 11.9 | 729.1 | 636.1 | 671.3 | 712.5 | 576.9 | 355.6 | 414.6 | 455.5 | 351.8 | 434 | 57.4 | 105.3 | 140.2 | 121.3 | 222.1 | 212.2 | 111.5 | 186.5 | 199.5 | 155.8
1249.3 | 1030.3 | 376.2 | 150.48 | 175.9024 | 214 | 193.8 | 215.5 | 213.7 | 323.1 | 35.9 | 20.8 | 65.5 | 6.1 | 292.5 | 11.5 | 728.5 | 651 | 686.6 | 710.6 | 577.4 | 355.8 | 413.5 | 462.6 | 350.8 | 433.6 | 57.5 | 105.4 | 140.5 | 121.4 | 222.1 | 212.3 | 111.6 | 186.5 | 199.6 | 155.9
1250.3 | 1031.3 | 375.4 | 150.16 | 175.5284 | 212.7 | 194.2 | 216.1 | 214.1 | 327.1 | 36 | 20.8 | 65.5 | 5.9 | 285.2 | 10.6 | 731.9 | 677.3 | 705 | 712.5 | 582.4 | 356.1 | 419.1 | 482.3 | 355.9 | 437.4 | 57.6 | 105.4 | 140.7 | 121.5 | 222.5 | 213 | 111.7 | 186.6 | 199.7 | 156
1251.3 | 1032.3 | 376.3 | 150.52 | 175.9492 | 212.2 | 194.6 | 217.3 | 213.9 | 332.9 | 36 | 20.8 | 65.5 | 6.7 | 286.3 | 10.5 | 737.8 | 699.8 | 720 | 721.6 | 585.1 | 356.4 | 425.9 | 495.1 | 359.4 | 441.2 | 57.6 | 105.5 | 140.9 | 121.6 | 222.3 | 213.2 | 111.7 | 186.6 | 199.9 | 156.1
1252.3 | 1033.3 | 376.8 | 150.72 | 176.183 | 211.9 | 194.1 | 217.9 | 214.2 | 336.9 | 35.9 | 20.8 | 65.5 | 7.5 | 281.2 | 8.8 | 740.3 | 696.5 | 705.4 | 724 | 583.8 | 356.7 | 429.7 | 498.4 | 361.4 | 442 | 57.7 | 105.6 | 141 | 121.7 | 222.6 | 213 | 111.8 | 186.7 | 200.1 | 156.2
1253.3 | 1034.3 | 376.9 | 150.76 | 176.2298 | 211.2 | 194.1 | 218.6 | 215.7 | 338.6 | 35.8 | 20.8 | 65.6 | 7.7 | 298.6 | 7.8 | 740.7 | 703.4 | 694.4 | 725.8 | 582.2 | 356.9 | 430.3 | 503 | 361.1 | 441.6 | 57.8 | 105.7 | 141.2 | 121.8 | 223.1 | 212.8 | 111.9 | 186.8 | 200.3 | 156.3
1254.3 | 1035.3 | 376.4 | 150.56 | 175.996 | 210.7 | 193.8 | 219.4 | 216.2 | 341.8 | 35.8 | 20.8 | 65.6 | 7.4 | 274.9 | 8.6 | 746.2 | 707 | 694.6 | 734.6 | 583.7 | 357.2 | 434.6 | 505 | 364 | 444.1 | 57.9 | 105.8 | 141.3 | 121.9 | 223.6 | 212.5 | 112 | 186.9 | 200.5 | 156.4
1255.3 | 1036.3 | 376.6 | 150.64 | 176.0895 | 211.3 | 194 | 219.6 | 216.3 | 343.6 | 35.8 | 20.7 | 65.6 | 7.1 | 274.8 | 9.1 | 750.9 | 717.5 | 694.6 | 742.1 | 583.9 | 357.5 | 436.8 | 509 | 365.2 | 444.7 | 57.9 | 105.9 | 141.4 | 122 | 223.9 | 212.6 | 112.1 | 187 | 200.7 | 156.6
1256.3 | 1037.3 | 376.5 | 150.6 | 176.0427 | 211.5 | 194.5 | 219 | 217.3 | 346.8 | 35.8 | 20.7 | 65.7 | 7.2 | 268.6 | 9.2 | 755.5 | 718 | 696.2 | 749.5 | 584.4 | 357.7 | 440.8 | 520.7 | 368.2 | 447.2 | 58 | 106 | 141.6 | 122.1 | 224.4 | 212.6 | 112.1 | 187.2 | 200.8 | 156.7
1257.3 | 1038.3 | 375.8 | 150.32 | 175.7154 | 211.5 | 194.8 | 218.8 | 218 | 345.4 | 35.8 | 20.7 | 65.7 | 6.3 | 281.4 | 9.3 | 757.4 | 711.1 | 701.1 | 753 | 585.4 | 358 | 441.5 | 513.7 | 368.9 | 448 | 58.1 | 106.1 | 141.7 | 122.2 | 224.9 | 212.7 | 112.2 | 187.3 | 201.1 | 156.8
1258.3 | 1039.3 | 376.9 | 150.76 | 176.2298 | 212.9 | 195.8 | 219.3 | 218.8 | 346.4 | 35.9 | 20.7 | 65.6 | 6.3 | 269.7 | 8.4 | 757.7 | 709.8 | 718.1 | 751.8 | 588.6 | 358.2 | 445.1 | 515.1 | 370.5 | 449.5 | 58.1 | 106.2 | 141.7 | 122.3 | 225.2 | 213.6 | 112.3 | 187.5 | 201.2 | 156.9
1259.3 | 1040.3 | 376.7 | 150.68 | 176.1362 | 212.9 | 196.9 | 220 | 219.7 | 345.6 | 35.9 | 20.7 | 65.6 | 6 | 272 | 7.5 | 758.6 | 700.4 | 725.9 | 753.3 | 591.6 | 358.5 | 448.9 | 509.5 | 372.2 | 451.4 | 58.2 | 106.3 | 141.8 | 122.3 | 225.4 | 214.2 | 112.4 | 187.6 | 201.4 | 157.1
1260.3 | 1041.3 | 377.2 | 150.88 | 176.37 | 212.7 | 198.4 | 220 | 220.6 | 344.1 | 35.9 | 20.7 | 65.7 | 5.7 | 290.1 | 6.3 | 759.3 | 700.6 | 726.4 | 753.6 | 591.2 | 358.9 | 455.9 | 513.3 | 374.7 | 453.4 | 58.3 | 106.4 | 142 | 122.4 | 226 | 214.7 | 112.5 | 187.7 | 201.6 | 157.2
1261.3 | 1042.3 | 376.7 | 150.68 | 176.1362 | 212.5 | 199.5 | 220 | 221.5 | 345.7 | 36 | 20.7 | 65.7 | 5.7 | 287.5 | 5.6 | 758.2 | 702.1 | 730.3 | 751.8 | 590.5 | 359.1 | 460.4 | 505.2 | 376.4 | 453.3 | 58.4 | 106.5 | 142 | 122.5 | 226.4 | 215.4 | 112.6 | 187.8 | 201.9 | 157.3
1262.3 | 1043.3 | 376.2 | 150.48 | 175.9024 | 213.3 | 198.9 | 220.5 | 222.4 | 344.7 | 36 | 20.7 | 65.7 | 5.7 | 269.1 | 4.9 | 758.7 | 695.6 | 729 | 753.7 | 591 | 359.4 | 460.6 | 498.9 | 377.1 | 453.5 | 58.4 | 106.6 | 142.2 | 122.6 | 227.5 | 215.8 | 112.7 | 188.1 | 202.1 | 157.5
1263.3 | 1044.3 | 376.5 | 150.6 | 176.0427 | 213 | 198.7 | 221.1 | 223.1 | 343.9 | 36.1 | 20.7 | 65.8 | 6.2 | 257 | 4.9 | 757.7 | 683.3 | 722.7 | 752.4 | 590.2 | 359.7 | 458.4 | 490.3 | 376.5 | 453.1 | 58.5 | 106.7 | 142.4 | 122.7 | 227.7 | 216.2 | 112.7 | 188.2 | 202.3 | 157.6
1264.3 | 1045.3 | 378.3 | 151.32 | 176.8844 | 213.3 | 198.7 | 222 | 223.6 | 341.8 | 36.1 | 20.7 | 65.9 | 7 | 274 | 5.4 | 754.1 | 682 | 714 | 745.3 | 588.2 | 360 | 456.9 | 491.5 | 376.1 | 452.1 | 58.6 | 106.8 | 142.5 | 122.8 | 227.9 | 216.3 | 112.8 | 188.2 | 202.5 | 157.8
1265.3 | 1046.3 | 378.5 | 151.4 | 176.9779 | 214.1 | 198.4 | 222.9 | 223.7 | 345.6 | 36.1 | 20.7 | 66 | 7.3 | 288.9 | 6.2 | 755.8 | 695 | 719.9 | 746.8 | 588.9 | 360.4 | 461.5 | 510.8 | 377.4 | 453.2 | 58.7 | 106.9 | 142.6 | 122.9 | 227.9 | 216.5 | 112.9 | 188.3 | 202.6 | 157.9
1266.3 | 1047.3 | 378.4 | 151.36 | 176.9311 | 216.2 | 197.7 | 223.1 | 223.1 | 349.3 | 36.1 | 20.7 | 66.1 | 8 | 266.7 | 8.1 | 757.8 | 698.5 | 724.9 | 749.5 | 590 | 360.7 | 468.7 | 511.2 | 380.4 | 454.9 | 58.7 | 107 | 142.8 | 123 | 228 | 216.7 | 113 | 188.5 | 202.8 | 158.1
1267.3 | 1048.3 | 378.1 | 151.24 | 176.7908 | 216.4 | 197.5 | 223 | 223.2 | 349.1 | 36.1 | 20.7 | 66.2 | 9.4 | 272.9 | 9.3 | 759.9 | 704.2 | 736 | 752.5 | 592.3 | 361 | 472.2 | 511.9 | 381.9 | 456.1 | 58.8 | 107 | 143 | 123.1 | 228.2 | 216.9 | 113.1 | 188.6 | 203 | 158.2
1268.3 | 1049.3 | 378.1 | 151.24 | 176.7908 | 216.3 | 198 | 223.1 | 222.4 | 349.2 | 36.1 | 20.7 | 66.3 | 9.7 | 278.1 | 9 | 760.6 | 704.2 | 739.6 | 753.2 | 593.2 | 361.3 | 475.3 | 509.3 | 383.6 | 456.9 | 58.9 | 107.1 | 143.1 | 123.3 | 228.1 | 216.8 | 113.2 | 188.7 | 203.2 | 158.3
1269.3 | 1050.3 | 378.2 | 151.28 | 176.8376 | 216.3 | 198.4 | 223.7 | 222.5 | 351.1 | 36 | 20.7 | 66.3 | 8.9 | 278.7 | 7.5 | 760.6 | 714.5 | 751.2 | 753.5 | 597.2 | 361.6 | 488.6 | 508 | 391.9 | 458.5 | 58.9 | 107.2 | 143.2 | 123.4 | 228.3 | 217 | 113.2 | 188.7 | 203.3 | 158.5
1270.3 | 1051.3 | 377.8 | 151.12 | 176.6506 | 215.7 | 198.5 | 224.2 | 222.8 | 351.9 | 35.9 | 20.7 | 66.3 | 8.5 | 247.5 | 6.5 | 763.4 | 728.2 | 750.1 | 756.4 | 596.9 | 361.9 | 501.8 | 515.1 | 394.6 | 459.4 | 59 | 107.3 | 143.5 | 123.5 | 228.5 | 216.9 | 113.3 | 188.8 | 203.6 | 158.6
1271.3 | 1052.3 | 377.7 | 151.08 | 176.6038 | 215.1 | 197.8 | 224.8 | 223.4 | 354.3 | 35.8 | 20.7 | 66.3 | 8.4 | 255.4 | 5.3 | 765.1 | 724.8 | 751.8 | 757.6 | 599.1 | 362.2 | 511.1 | 515.6 | 395.9 | 460.9 | 59.1 | 107.4 | 143.6 | 123.6 | 228.8 | 217.2 | 113.4 | 189 | 203.8 | 158.7
1272.3 | 1053.3 | 377.4 | 150.96 | 176.4635 | 214.8 | 198 | 226.2 | 224 | 356.9 | 35.7 | 20.7 | 66.3 | 7.3 | 251.3 | 4 | 764.9 | 702.7 | 744.4 | 756.6 | 600 | 362.6 | 519.7 | 504.4 | 396.4 | 460.1 | 59.2 | 107.5 | 143.7 | 123.7 | 229.1 | 217 | 113.5 | 189.1 | 203.9 | 158.8
1273.3 | 1054.3 | 377.4 | 150.96 | 176.4635 | 215.8 | 199.3 | 226.5 | 224.4 | 355 | 35.7 | 20.7 | 66.2 | 7.1 | 253.4 | 3.2 | 765.1 | 711.4 | 740.9 | 756.9 | 600.3 | 362.9 | 522.4 | 505.6 | 395.3 | 460 | 59.2 | 107.6 | 143.8 | 123.8 | 229.3 | 216.9 | 113.6 | 189.2 | 204.1 | 159
1274.3 | 1055.3 | 377.2 | 150.88 | 176.37 | 217.1 | 199.5 | 225.4 | 224.2 | 358.8 | 35.6 | 20.7 | 66.2 | 7.6 | 257.1 | 2.6 | 766 | 707.7 | 735 | 759.9 | 600.1 | 363.2 | 529.4 | 505.4 | 397 | 461.5 | 59.3 | 107.7 | 143.9 | 123.9 | 229.3 | 217 | 113.6 | 189.3 | 204.3 | 159.1
1275.3 | 1056.3 | 377.2 | 150.88 | 176.37 | 217.7 | 199.5 | 225.5 | 223.3 | 360.9 | 35.6 | 20.7 | 66.2 | 7.3 | 256.8 | 2 | 766.3 | 704.6 | 723.6 | 757.8 | 597.6 | 363.5 | 529.9 | 507.9 | 396.9 | 461.2 | 59.4 | 107.8 | 144 | 124 | 229.3 | 216.9 | 113.8 | 189.5 | 204.4 | 159.2
1276.3 | 1057.3 | 377.1 | 150.84 | 176.3233 | 218.8 | 200 | 226.3 | 223 | 361.1 | 35.6 | 20.7 | 66.1 | 7.9 | 250.4 | 1.6 | 767.5 | 704.3 | 720.2 | 757.9 | 596.7 | 363.8 | 532.9 | 506.2 | 398.6 | 462.6 | 59.5 | 107.9 | 144.2 | 124.1 | 229.9 | 217.1 | 113.9 | 189.7 | 204.6 | 159.4
1277.3 | 1058.3 | 377.3 | 150.92 | 176.4168 | 219.4 | 199.5 | 226.4 | 223.1 | 359.8 | 35.5 | 20.7 | 66.2 | 8.7 | 233.8 | 1.5 | 768.7 | 701.7 | 731.5 | 761.3 | 597.4 | 364.2 | 533.2 | 500 | 399.6 | 463.5 | 59.5 | 108 | 144.4 | 124.2 | 230 | 217.1 | 113.9 | 189.7 | 204.8 | 159.5
1278.3 | 1059.3 | 377.1 | 150.84 | 176.3233 | 221.4 | 199.9 | 226.1 | 223.1 | 358.3 | 35.5 | 20.7 | 66.2 | 9 | 204.7 | 2.5 | 772.1 | 715.6 | 743.1 | 768 | 602 | 364.5 | 551 | 514.7 | 407.4 | 466.7 | 59.6 | 108.2 | 144.5 | 124.3 | 230.7 | 217.4 | 114 | 189.9 | 205 | 159.6
1279.3 | 1060.3 | 377.5 | 151 | 176.5103 | 222 | 201.1 | 226.6 | 223.2 | 360.5 | 35.5 | 20.7 | 66.2 | 9.3 | 193.6 | 3.8 | 774.6 | 728.9 | 745 | 772.5 | 604.4 | 364.8 | 561.4 | 512.5 | 409.8 | 469 | 59.7 | 108.3 | 144.7 | 124.4 | 231.2 | 218 | 114.1 | 190 | 205.2 | 159.8
1280.3 | 1061.3 | 377.2 | 150.88 | 176.37 | 223.6 | 201.4 | 225.9 | 224.3 | 372.2 | 35.5 | 20.7 | 66.2 | 9.4 | 196.6 | 5 | 772.1 | 715 | 728.8 | 767.9 | 603.2 | 365.2 | 576.9 | 519.1 | 416.2 | 468.1 | 59.8 | 108.4 | 145.3 | 124.6 | 231.5 | 218.1 | 114.2 | 190.2 | 205.5 | 159.9
1281.3 | 1062.3 | 377.1 | 150.84 | 176.3233 | 225.3 | 202.5 | 225.3 | 224 | 385 | 35.5 | 20.7 | 66.3 | 8.7 | 202.4 | 6 | 767.4 | 685.5 | 713.3 | 759.8 | 600.2 | 365.5 | 570.3 | 505.5 | 413.8 | 466 | 59.8 | 108.6 | 145.4 | 124.7 | 231.4 | 218.9 | 114.3 | 190.3 | 205.7 | 160
1282.3 | 1063.3 | 375.9 | 150.36 | 175.7622 | 224.8 | 202.8 | 226.9 | 223.7 | 377.7 | 35.5 | 20.7 | 66.2 | 8.5 | 216.2 | 5.9 | 761.4 | 656.6 | 694.4 | 749.9 | 596.7 | 365.8 | 563.9 | 491.3 | 411.4 | 464 | 59.9 | 108.7 | 145.4 | 124.8 | 231.7 | 219.2 | 114.4 | 190.4 | 205.8 | 160.2
1283.3 | 1064.3 | 377 | 150.8 | 176.2765 | 224 | 202.3 | 228.1 | 224 | 369.9 | 35.5 | 20.7 | 66.2 | 8.2 | 207.6 | 4.6 | 755.4 | 649.7 | 689.7 | 739.7 | 594.4 | 366.1 | 559 | 480.2 | 414.5 | 462.1 | 60 | 108.8 | 145.5 | 124.9 | 231.9 | 219.3 | 114.5 | 190.5 | 205.9 | 160.3
1284.3 | 1065.3 | 375.6 | 150.24 | 175.6219 | 223.5 | 203 | 228 | 224 | 367 | 35.5 | 20.7 | 66.1 | 7.9 | 184.9 | 3.5 | 750.9 | 634.9 | 682.7 | 732.3 | 593 | 366.5 | 559.8 | 470.4 | 415.3 | 460.8 | 60 | 109 | 145.5 | 125 | 232 | 219.6 | 114.5 | 190.6 | 206.1 | 160.4
1285.3 | 1066.3 | 375.9 | 150.36 | 175.7622 | 222.3 | 204.1 | 227.7 | 223.6 | 361.7 | 35.5 | 20.7 | 66.1 | 7.2 | 172.7 | 2.7 | 746.4 | 623.4 | 668.9 | 724.1 | 590.1 | 366.8 | 550.4 | 458 | 413.3 | 458.3 | 60.1 | 109.1 | 145.6 | 125.1 | 231.8 | 219.4 | 114.6 | 190.6 | 206.2 | 160.5
1286.3 | 1067.3 | 376.1 | 150.44 | 175.8557 | 222.8 | 205.9 | 226.5 | 223.3 | 355 | 35.6 | 20.7 | 66.2 | 7.3 | 194.5 | 2.8 | 745 | 635.4 | 669.6 | 720.2 | 589.7 | 367.1 | 541.3 | 457 | 412.1 | 457.6 | 60.2 | 109.3 | 145.7 | 125.2 | 232.1 | 219.5 | 114.7 | 190.7 | 206.3 | 160.6
1287.3 | 1068.3 | 375.7 | 150.28 | 175.6687 | 222.5 | 206.6 | 225.2 | 223.1 | 357.2 | 35.7 | 20.7 | 66.4 | 6.1 | 204.1 | 3 | 745.5 | 637.6 | 671.5 | 720 | 589.9 | 367.5 | 545 | 462.4 | 412.6 | 459.3 | 60.3 | 109.4 | 145.8 | 125.3 | 232.2 | 219.5 | 114.8 | 190.8 | 206.4 | 160.7
1288.3 | 1069.3 | 378.1 | 151.24 | 176.7908 | 221.7 | 205.6 | 223.7 | 222.8 | 360.7 | 35.7 | 20.7 | 66.5 | 6.5 | 178.4 | 2.9 | 748 | 658.1 | 679.5 | 725.1 | 590.5 | 367.8 | 544.2 | 470 | 412.8 | 460.6 | 60.3 | 109.5 | 146 | 125.4 | 232.5 | 219.4 | 114.9 | 190.8 | 206.6 | 160.9
1289.3 | 1070.3 | 378.5 | 151.4 | 176.9779 | 222 | 205.2 | 223.7 | 222.5 | 361.6 | 35.8 | 20.7 | 66.7 | 7.2 | 191.8 | 2.7 | 749.8 | 659.6 | 683.1 | 729 | 591.4 | 368.1 | 552.4 | 468.4 | 416.2 | 463.2 | 60.4 | 109.6 | 146.2 | 125.5 | 232.7 | 219.5 | 115 | 191 | 206.8 | 161
1290.3 | 1071.3 | 378.4 | 151.36 | 176.9311 | 222.4 | 205.6 | 224.3 | 223.2 | 359.4 | 35.9 | 20.7 | 66.8 | 7.6 | 237 | 3.6 | 750.2 | 663.1 | 693.9 | 730.6 | 592 | 368.5 | 558 | 467.9 | 418.9 | 465.4 | 60.5 | 109.7 | 146.4 | 125.6 | 232.9 | 219.7 | 115 | 191.2 | 207 | 161.2
1291.3 | 1072.3 | 378.3 | 151.32 | 176.8844 | 221.2 | 205.8 | 224 | 224 | 356.9 | 36 | 20.7 | 66.9 | 7.8 | 250 | 7.2 | 749.8 | 667.4 | 709.1 | 732.2 | 593.9 | 368.8 | 566.5 | 468.7 | 422.7 | 467.1 | 60.6 | 109.9 | 146.5 | 125.7 | 233 | 219.9 | 115.1 | 191.3 | 207.3 | 161.3
1292.3 | 1073.3 | 378.8 | 151.52 | 177.1181 | 220.7 | 205.1 | 224.4 | 223.1 | 366 | 36.1 | 20.7 | 67 | 6.8 | 228.1 | 8.9 | 751.2 | 685.8 | 724.4 | 735.3 | 600.3 | 369.1 | 591.2 | 494.4 | 437.6 | 470.4 | 60.6 | 110 | 146.8 | 125.8 | 233 | 220.3 | 115.2 | 191.4 | 207.6 | 161.4
1293.3 | 1074.3 | 376.9 | 150.76 | 176.2298 | 220.7 | 204.4 | 225.6 | 221.3 | 376.6 | 36.2 | 20.7 | 67.1 | 6.8 | 234.2 | 7.5 | 754.3 | 693.4 | 725.4 | 740.2 | 603.6 | 369.5 | 606.4 | 495.2 | 442.6 | 473.7 | 60.7 | 110.1 | 146.8 | 125.9 | 233.1 | 220.9 | 115.3 | 191.5 | 207.9 | 161.6
1294.3 | 1075.3 | 376.1 | 150.44 | 175.8557 | 220.8 | 204.4 | 226.8 | 220.8 | 378.5 | 36.3 | 20.7 | 67.1 | 7.2 | 206.7 | 6.3 | 752.5 | 687.2 | 706.4 | 736.4 | 601.1 | 369.8 | 602.7 | 487 | 440.5 | 472.3 | 60.8 | 110.2 | 146.9 | 126 | 233.2 | 221.2 | 115.4 | 191.7 | 208.2 | 161.7
1295.3 | 1076.3 | 376.9 | 150.76 | 176.2298 | 220.6 | 204.7 | 227.5 | 221.2 | 372.3 | 36.4 | 20.7 | 67.1 | 7.2 | 221.4 | 5.5 | 748.9 | 677.1 | 694.1 | 729.5 | 599.8 | 370.1 | 588.1 | 475.2 | 436.5 | 469.8 | 60.9 | 110.3 | 146.9 | 126.1 | 233.2 | 221.4 | 115.5 | 191.8 | 208.5 | 161.8
1296.3 | 1077.3 | 376.8 | 150.72 | 176.183 | 220.3 | 204.7 | 226.6 | 222 | 366.7 | 36.4 | 20.7 | 67 | 7.7 | 244.9 | 6.5 | 747.7 | 679.3 | 693.4 | 725.1 | 599.5 | 370.5 | 578.9 | 475.8 | 434.6 | 469.4 | 60.9 | 110.4 | 147.1 | 126.2 | 233.3 | 221.1 | 115.6 | 191.8 | 208.6 | 162
1297.3 | 1078.3 | 376.1 | 150.44 | 175.8557 | 220.5 | 204.2 | 225.7 | 222.5 | 366.2 | 36.5 | 20.7 | 66.9 | 7 | 236.8 | 7.5 | 748 | 680.7 | 704.7 | 722.2 | 600.4 | 370.8 | 576.8 | 487.2 | 434.1 | 470.1 | 61 | 110.5 | 147.2 | 126.3 | 233.4 | 221.1 | 115.7 | 192 | 208.7 | 162.1
1298.3 | 1079.3 | 377.2 | 150.88 | 176.37 | 220.4 | 202.4 | 224.6 | 222.6 | 370.7 | 36.5 | 20.7 | 66.7 | 7.2 | 239.2 | 7.8 | 749.6 | 674.5 | 713.4 | 726.7 | 602.1 | 371.1 | 586.6 | 485.4 | 441.3 | 473.7 | 61.1 | 110.6 | 147.5 | 126.4 | 233.8 | 221.5 | 115.8 | 192.2 | 208.9 | 162.2
1299.3 | 1080.3 | 378.2 | 151.28 | 176.8376 | 220.8 | 201.8 | 224.3 | 221.9 | 373 | 36.6 | 20.7 | 66.7 | 7.3 | 232.7 | 7.6 | 746.9 | 657.7 | 708.1 | 724 | 600.2 | 371.4 | 579.8 | 473.5 | 439.4 | 471.5 | 61.2 | 110.7 | 147.7 | 126.6 | 233.6 | 221.6 | 115.9 | 192.3 | 209.2 | 162.4
1300.3 | 1081.3 | 378 | 151.2 | 176.7441 | 222.1 | 202.4 | 225.2 | 222.4 | 367.9 | 36.7 | 20.7 | 66.7 | 8 | 238.9 | 8.1 | 743 | 645.3 | 700.3 | 718.1 | 598.6 | 371.7 | 574.4 | 467.1 | 439 | 469.8 | 61.3 | 110.7 | 147.8 | 126.7 | 233.6 | 221.5 | 115.9 | 192.4 | 209.4 | 162.5
1301.3 | 1082.3 | 378.5 | 151.4 | 176.9779 | 223.2 | 203.3 | 226.3 | 223.3 | 367.4 | 36.8 | 20.7 | 66.7 | 8.1 | 242.9 | 8.6 | 740.1 | 624.7 | 685.9 | 712 | 596.5 | 372 | 564.6 | 456.4 | 436.8 | 467.8 | 61.3 | 110.9 | 147.9 | 126.8 | 233.7 | 221.6 | 116.1 | 192.4 | 209.5 | 162.6
1302.3 | 1083.3 | 378.8 | 151.52 | 177.1181 | 223.8 | 203.3 | 225.6 | 224 | 360.8 | 36.8 | 20.7 | 66.8 | 8.7 | 246.9 | 8.5 | 733.5 | 604.4 | 670.3 | 703.2 | 592.5 | 372.3 | 556 | 443 | 435 | 465.2 | 61.4 | 111 | 148 | 126.9 | 233.9 | 222.2 | 116.1 | 192.5 | 209.7 | 162.7
1303.3 | 1084.3 | 378.4 | 151.36 | 176.9311 | 223.7 | 202 | 225.5 | 224.2 | 354.5 | 36.8 | 20.7 | 66.9 | 9.1 | 250.9 | 8.2 | 730.6 | 604.1 | 671.7 | 699.5 | 592.4 | 372.6 | 550.2 | 437.3 | 434.3 | 464 | 61.5 | 111 | 148 | 127 | 234 | 222.8 | 116.2 | 192.8 | 209.8 | 162.8
1304.3 | 1085.3 | 377 | 150.8 | 176.2765 | 224.5 | 200.8 | 225.3 | 224.3 | 350.3 | 36.9 | 20.7 | 67.1 | 9.4 | 227.9 | 8.1 | 728.8 | 604.1 | 672.6 | 695.5 | 592.2 | 372.9 | 544.5 | 430.5 | 431.1 | 463.5 | 61.6 | 111.1 | 148.1 | 127.1 | 234 | 223.4 | 116.3 | 192.9 | 209.9 | 162.9
1305.3 | 1086.3 | 376.1 | 150.44 | 175.8557 | 224.7 | 200.7 | 225.3 | 223.9 | 348.6 | 36.9 | 20.7 | 67.2 | 8.3 | 255.5 | 8.2 | 729.8 | 618.7 | 675.7 | 695.8 | 592.9 | 373.2 | 539.9 | 430.8 | 429.1 | 462.9 | 61.6 | 111.2 | 148.3 | 127.2 | 233.9 | 223.5 | 116.4 | 193.1 | 210 | 163
1306.3 | 1087.3 | 376.3 | 150.52 | 175.9492 | 225 | 200.5 | 225.3 | 223.5 | 346 | 36.9 | 20.7 | 67.5 | 8.4 | 253.4 | 8.8 | 730 | 609.8 | 665.8 | 697.3 | 591.2 | 373.5 | 531.1 | 424 | 426.7 | 462.7 | 61.7 | 111.3 | 148.3 | 127.4 | 234.2 | 223.4 | 116.5 | 193.1 | 210.2 | 163.1
1307.3 | 1088.3 | 376.2 | 150.48 | 175.9024 | 225.9 | 201 | 224.4 | 222.3 | 341.3 | 36.9 | 20.7 | 67.6 | 9.1 | 249.7 | 10.3 | 729.8 | 608 | 658.7 | 698.1 | 589.9 | 373.8 | 520.6 | 422.3 | 423.2 | 461.6 | 61.8 | 111.4 | 148.5 | 127.5 | 234.4 | 223.1 | 116.6 | 193.2 | 210.3 | 163.2
1308.3 | 1089.3 | 375.7 | 150.28 | 175.6687 | 227.1 | 200.2 | 224.3 | 222.1 | 338.8 | 36.8 | 20.7 | 67.7 | 9.5 | 247.9 | 11.5 | 728.8 | 599.2 | 670.5 | 698.8 | 590.1 | 374.1 | 511.3 | 421.1 | 420.6 | 460.9 | 61.9 | 111.5 | 148.6 | 127.6 | 234.3 | 222.9 | 116.7 | 193.3 | 210.5 | 163.4
1309.3 | 1090.3 | 376 | 150.4 | 175.8089 | 228.3 | 199.7 | 224.2 | 222.7 | 337.7 | 36.8 | 20.7 | 67.8 | 10 | 252 | 11.5 | 730.7 | 613.5 | 685.4 | 702.7 | 592.2 | 374.4 | 515.9 | 432 | 422 | 463.4 | 61.9 | 111.6 | 148.8 | 127.8 | 234 | 223.2 | 116.7 | 193.4 | 210.6 | 163.5
1310.3 | 1091.3 | 378 | 151.2 | 176.7441 | 230 | 199.8 | 225.2 | 223.2 | 342.3 | 36.8 | 20.7 | 67.8 | 9.3 | 258.1 | 12.2 | 728.7 | 608.6 | 676.2 | 699.8 | 590.1 | 374.7 | 513.3 | 427.5 | 421.9 | 462.2 | 62 | 111.8 | 148.9 | 127.9 | 234.3 | 224.1 | 116.8 | 193.5 | 210.8 | 163.6
1311.3 | 1092.3 | 378.8 | 151.52 | 177.1181 | 229.2 | 199.9 | 226.3 | 223.4 | 338.6 | 36.8 | 20.7 | 67.8 | 8.5 | 268.4 | 13.1 | 726.8 | 615.7 | 687.4 | 696.3 | 589.8 | 375.1 | 506.2 | 429.2 | 420.2 | 461.3 | 62.1 | 111.9 | 149.1 | 128 | 234.3 | 224.4 | 117 | 193.6 | 210.9 | 163.7
1312.3 | 1093.3 | 376.7 | 150.68 | 176.1362 | 228.1 | 199.5 | 227.1 | 222.9 | 340.5 | 36.8 | 20.7 | 67.8 | 7.4 | 242.3 | 13.1 | 726.4 | 622.6 | 681.7 | 694.2 | 590 | 375.4 | 504.2 | 434.4 | 419.9 | 461.2 | 62.2 | 112 | 149.3 | 128.1 | 234.5 | 224.4 | 117 | 193.7 | 211.1 | 163.8
1313.3 | 1094.3 | 376.4 | 150.56 | 175.996 | 228.5 | 198.8 | 227.6 | 223.2 | 339.7 | 36.8 | 20.7 | 67.8 | 7.4 | 261.6 | 12.9 | 723.6 | 611.8 | 675.8 | 690.3 | 587.7 | 375.7 | 497.7 | 428.4 | 417.9 | 459.8 | 62.2 | 112.1 | 149.4 | 128.2 | 234.8 | 224.4 | 117.2 | 193.7 | 211.2 | 163.9
1314.3 | 1095.3 | 377 | 150.8 | 176.2765 | 229.7 | 198.1 | 227.8 | 224.3 | 335.9 | 36.8 | 20.7 | 67.8 | 7.4 | 258.2 | 12.6 | 722.8 | 620.5 | 676.2 | 690.2 | 587.9 | 376 | 490.9 | 422.4 | 415.7 | 459.4 | 62.3 | 112.3 | 149.5 | 128.4 | 235.1 | 224.8 | 117.2 | 193.9 | 211.4 | 164.1
1315.3 | 1096.3 | 375.9 | 150.36 | 175.7622 | 230 | 198.7 | 227.5 | 225.1 | 335.4 | 36.7 | 20.7 | 67.7 | 7.1 | 259.2 | 11.2 | 720.7 | 613 | 669.9 | 688 | 586 | 376.3 | 483.8 | 419.5 | 412.6 | 457.9 | 62.4 | 112.4 | 149.5 | 128.5 | 235.4 | 224.7 | 117.3 | 194 | 211.6 | 164.2
1316.3 | 1097.3 | 377.3 | 150.92 | 176.4168 | 229 | 199.1 | 226.9 | 225.4 | 336.4 | 36.6 | 20.7 | 67.6 | 7 | 250.9 | 9.6 | 718.7 | 615.3 | 658.5 | 684.3 | 583.7 | 376.6 | 476.8 | 418.6 | 409.7 | 456.4 | 62.5 | 112.5 | 149.7 | 128.6 | 235.3 | 224.7 | 117.4 | 194.1 | 211.7 | 164.3
1317.3 | 1098.3 | 377.9 | 151.16 | 176.6973 | 228.2 | 198.9 | 226.6 | 225.9 | 335.8 | 36.5 | 20.7 | 67.6 | 6.7 | 244.6 | 8.3 | 717.2 | 609.2 | 649.5 | 681.7 | 582.1 | 376.9 | 470.7 | 415.6 | 407.4 | 455.5 | 62.5 | 112.6 | 149.9 | 128.7 | 235.5 | 225 | 117.5 | 194.3 | 211.8 | 164.4
1318.3 | 1099.3 | 378.3 | 151.32 | 176.8844 | 227.6 | 199.5 | 226.7 | 226.2 | 333.2 | 36.5 | 20.7 | 67.6 | 6.9 | 243.5 | 8.2 | 717.5 | 616.7 | 653.5 | 683.8 | 582.2 | 377.1 | 468.6 | 415.8 | 406.4 | 455.5 | 62.6 | 112.7 | 150.2 | 128.9 | 235.6 | 225.2 | 117.6 | 194.4 | 211.9 | 164.5
1319.3 | 1100.3 | 378 | 151.2 | 176.7441 | 228.4 | 200.9 | 226.5 | 226.2 | 333.6 | 36.5 | 20.7 | 67.7 | 8.2 | 235.6 | 8.2 | 717 | 613.6 | 654.1 | 684.1 | 581.5 | 377.4 | 467.5 | 414.7 | 405.2 | 454.7 | 62.7 | 112.9 | 150.2 | 129 | 235.3 | 225.2 | 117.8 | 194.5 | 212 | 164.7
1320.3 | 1101.3 | 379.1 | 151.64 | 177.2584 | 228.9 | 201.7 | 227.2 | 225.3 | 330.5 | 36.4 | 20.7 | 67.8 | 8.4 | 261.6 | 9 | 715 | 602 | 640.4 | 680.8 | 579.3 | 377.6 | 461.1 | 410.6 | 402.8 | 452.7 | 62.8 | 113 | 150.3 | 129.1 | 235.3 | 225.1 | 117.8 | 194.6 | 212.2 | 164.8
1321.3 | 1102.3 | 377.9 | 151.16 | 176.6973 | 229.4 | 201.5 | 227.4 | 225.8 | 329.5 | 36.4 | 20.7 | 67.9 | 8.3 | 256.3 | 9.4 | 711 | 589.7 | 632.6 | 675.1 | 576.9 | 377.9 | 455.9 | 405.9 | 400.4 | 450.8 | 62.8 | 113.1 | 150.5 | 129.3 | 235.5 | 224.8 | 117.9 | 194.7 | 212.3 | 164.9
1322.3 | 1103.3 | 376.6 | 150.64 | 176.0895 | 231.1 | 200.9 | 226.8 | 226 | 326.3 | 36.4 | 20.7 | 67.8 | 8 | 256.8 | 8.9 | 708.8 | 585.1 | 635.6 | 671.6 | 575.5 | 378.1 | 451.3 | 403.9 | 398.3 | 450.4 | 62.9 | 113.2 | 150.5 | 129.4 | 235.4 | 224.8 | 118 | 194.7 | 212.4 | 165
1323.3 | 1104.3 | 377.4 | 150.96 | 176.4635 | 232.2 | 200.8 | 226.4 | 226.6 | 325.1 | 36.4 | 20.7 | 67.9 | 8.2 | 276.6 | 9.9 | 707.6 | 582.7 | 635.3 | 670.1 | 574.1 | 378.3 | 449.3 | 402.7 | 397.3 | 450.2 | 63 | 113.3 | 150.6 | 129.5 | 235.6 | 224.7 | 118.1 | 194.9 | 212.5 | 165.1
1324.3 | 1105.3 | 377 | 150.8 | 176.2765 | 231.9 | 201 | 226 | 226.9 | 324.2 | 36.3 | 20.7 | 67.8 | 8.3 | 275.1 | 10.2 | 708.5 | 605.7 | 638.4 | 671.3 | 574.7 | 378.5 | 450.3 | 406 | 397.3 | 450.4 | 63.1 | 113.4 | 150.9 | 129.6 | 235.5 | 224.4 | 118.2 | 195 | 212.6 | 165.3
1325.3 | 1106.3 | 377.5 | 151 | 176.5103 | 230.7 | 200.8 | 226.3 | 226.2 | 324.2 | 36.4 | 20.7 | 67.7 | 8.4 | 272.2 | 12 | 705.6 | 593.8 | 628.6 | 667.5 | 572 | 378.7 | 445.8 | 402.8 | 395.5 | 448.5 | 63.2 | 113.5 | 150.9 | 129.7 | 235.7 | 224 | 118.3 | 195.1 | 212.8 | 165.4
1326.3 | 1107.3 | 377.6 | 151.04 | 176.5571 | 229.7 | 200.4 | 226.1 | 225.3 | 321.5 | 36.4 | 20.7 | 67.7 | 8.2 | 276.9 | 15.2 | 704.3 | 595.4 | 624.9 | 667.3 | 571.2 | 378.9 | 439.9 | 398.4 | 392.6 | 446.8 | 63.2 | 113.7 | 150.9 | 129.9 | 235.6 | 223.8 | 118.4 | 195.2 | 212.9 | 165.6
1327.3 | 1108.3 | 377.7 | 151.08 | 176.6038 | 229.3 | 200.7 | 226.5 | 225.6 | 319.7 | 36.4 | 20.7 | 67.7 | 7.4 | 281.6 | 15.5 | 700.9 | 578.7 | 625.4 | 664.6 | 569.5 | 379.1 | 434 | 393.6 | 391.2 | 445.2 | 63.3 | 113.8 | 151 | 130 | 235.7 | 223.9 | 118.5 | 195.3 | 213 | 165.7
1328.3 | 1109.3 | 376.9 | 150.76 | 176.2298 | 229.8 | 201.3 | 226.4 | 226 | 317.4 | 36.5 | 20.7 | 67.7 | 7.7 | 271.3 | 13.2 | 698.2 | 567.8 | 622 | 662.7 | 569.5 | 379.3 | 428.9 | 387.3 | 389.6 | 443.9 | 63.4 | 113.9 | 151 | 130.1 | 235.6 | 224.2 | 118.6 | 195.4 | 213.1 | 165.8
1329.3 | 1110.3 | 377.6 | 151.04 | 176.5571 | 229.1 | 200.5 | 225.9 | 225.2 | 314.6 | 36.4 | 20.6 | 67.7 | 8.4 | 268.2 | 10.7 | 693.6 | 558.9 | 615.1 | 658.5 | 567.6 | 379.6 | 424.9 | 383.7 | 387.3 | 442.2 | 63.5 | 114 | 151 | 130.2 | 235.8 | 225 | 118.7 | 195.5 | 213.2 | 165.9
1330.3 | 1111.3 | 375.1 | 150.04 | 175.3881 | 228.5 | 199.8 | 225.1 | 225.2 | 312.3 | 36.4 | 20.6 | 67.7 | 8 | 287.2 | 8.3 | 690.1 | 550.1 | 612.7 | 654.7 | 566.2 | 379.8 | 420.3 | 379.9 | 384.9 | 440.5 | 63.6 | 114.1 | 151.1 | 130.3 | 235.4 | 225.6 | 118.7 | 195.7 | 213.2 | 166.1
1331.3 | 1112.3 | 375.9 | 150.36 | 175.7622 | 229.5 | 199.8 | 225.1 | 224.9 | 310.6 | 36.4 | 20.7 | 67.7 | 8.4 | 277.3 | 7.6 | 686.8 | 536.8 | 607.2 | 649.5 | 564.1 | 380.1 | 416.9 | 376.8 | 382.8 | 439.6 | 63.6 | 114.2 | 151.3 | 130.4 | 234.9 | 225.9 | 118.9 | 195.7 | 213.3 | 166.2
1332.3 | 1113.3 | 376.2 | 150.48 | 175.9024 | 229.8 | 199.5 | 225 | 224.7 | 308.3 | 36.4 | 20.7 | 67.8 | 7.9 | 280.1 | 7.2 | 684.7 | 542.7 | 619.2 | 645.7 | 563.4 | 380.3 | 414.2 | 374.7 | 381.7 | 438.3 | 63.7 | 114.3 | 151.3 | 130.6 | 234.6 | 225.5 | 119 | 195.9 | 213.4 | 166.3
1333.3 | 1114.3 | 376.1 | 150.44 | 175.8557 | 231.3 | 199.7 | 224.3 | 224.9 | 308 | 36.5 | 20.7 | 67.9 | 7.5 | 281 | 6.8 | 684.6 | 546.2 | 638.5 | 647.3 | 566 | 380.6 | 417.9 | 381.9 | 382 | 440 | 63.8 | 114.5 | 151.6 | 130.7 | 234.3 | 225.1 | 119.1 | 196 | 213.5 | 166.4
1334.3 | 1115.3 | 376.3 | 150.52 | 175.9492 | 233 | 200.3 | 224.7 | 225.1 | 312.6 | 36.6 | 20.7 | 67.9 | 7.6 | 280.9 | 7.4 | 686.1 | 561.9 | 642 | 651.6 | 567.4 | 380.8 | 431.2 | 394.7 | 386.5 | 441.7 | 63.9 | 114.6 | 151.6 | 130.8 | 234.1 | 224.8 | 119.2 | 196 | 213.6 | 166.5
1335.3 | 1116.3 | 376.4 | 150.56 | 175.996 | 231.6 | 200.2 | 225.4 | 225.1 | 318.8 | 36.7 | 20.6 | 68 | 7.4 | 285.6 | 7.3 | 688.9 | 573.6 | 648.1 | 656.9 | 567.6 | 381.1 | 435.5 | 404.1 | 388.2 | 441.9 | 63.9 | 114.7 | 151.9 | 130.9 | 234.4 | 224.8 | 119.3 | 196 | 213.8 | 166.6
1336.3 | 1117.3 | 376.5 | 150.6 | 176.0427 | 230.8 | 200.9 | 226.4 | 225.1 | 319.5 | 36.8 | 20.6 | 68 | 7.2 | 287 | 7.6 | 690.3 | 577.9 | 653.2 | 659.6 | 568.6 | 381.3 | 436.5 | 404.2 | 389.2 | 441.9 | 64 | 114.8 | 152 | 131 | 234 | 224.8 | 119.4 | 196.1 | 214 | 166.8
1337.3 | 1118.3 | 376.6 | 150.64 | 176.0895 | 229.1 | 201.3 | 227.4 | 225.5 | 321.2 | 36.9 | 20.6 | 68 | 8.2 | 285.6 | 8 | 690 | 570.8 | 649 | 658.7 | 567.4 | 381.6 | 433.8 | 401.6 | 388.5 | 440.8 | 64.1 | 114.9 | 152 | 131.1 | 233.5 | 224.7 | 119.5 | 196.1 | 214.1 | 166.9
1338.3 | 1119.3 | 376.6 | 150.64 | 176.0895 | 227.9 | 201.4 | 227.7 | 224.6 | 322.4 | 37 | 20.6 | 67.9 | 7.4 | 278.7 | 7.8 | 692.4 | 594.4 | 648 | 662 | 568.2 | 381.9 | 433 | 415 | 387.9 | 441.1 | 64.2 | 115 | 152.1 | 131.2 | 233.1 | 224.3 | 119.6 | 196.2 | 214.2 | 167
1339.3 | 1120.3 | 376.9 | 150.76 | 176.2298 | 227.2 | 201.6 | 228 | 223.9 | 329.1 | 37 | 20.6 | 67.8 | 6.6 | 253.6 | 6.4 | 695 | 606.4 | 644.5 | 664.2 | 566.4 | 382.1 | 436.3 | 421.2 | 387.9 | 440.8 | 64.3 | 115.1 | 152.3 | 131.3 | 233.2 | 224.6 | 119.6 | 196.2 | 214.4 | 167.1
1340.3 | 1121.3 | 377 | 150.8 | 176.2765 | 227.1 | 201.4 | 227.3 | 223.9 | 331.5 | 37.1 | 20.6 | 67.7 | 7.3 | 249 | 5.3 | 695.3 | 599.5 | 643.1 | 663.8 | 565.8 | 382.4 | 433 | 420.2 | 386 | 440.2 | 64.3 | 115.3 | 152.3 | 131.4 | 233.1 | 224.7 | 119.8 | 196.3 | 214.5 | 167.2
1341.3 | 1122.3 | 376.9 | 150.76 | 176.2298 | 227 | 200.8 | 227.2 | 223.2 | 329.6 | 37.1 | 20.6 | 67.8 | 7.2 | 252 | 5.6 | 695.6 | 605.1 | 641.4 | 663.8 | 565.3 | 382.6 | 430.5 | 419.6 | 384.8 | 439.7 | 64.4 | 115.4 | 152.4 | 131.5 | 233.6 | 224.5 | 119.9 | 196.4 | 214.6 | 167.3
1342.3 | 1123.3 | 377.1 | 150.84 | 176.3233 | 226.9 | 200.5 | 226.9 | 222.2 | 327.7 | 37.1 | 20.6 | 67.9 | 7 | 241.4 | 5.5 | 693.7 | 594.6 | 634.3 | 660.3 | 563.3 | 382.9 | 427.7 | 416.2 | 383.6 | 438.9 | 64.5 | 115.4 | 152.6 | 131.6 | 233.6 | 224.6 | 120 | 196.4 | 214.6 | 167.5
1343.3 | 1124.3 | 377.1 | 150.84 | 176.3233 | 227.1 | 201.4 | 226.8 | 221 | 325.2 | 37.1 | 20.6 | 68.1 | 7.9 | 246.7 | 6.3 | 690.4 | 586.4 | 623.1 | 656.3 | 561.1 | 383.1 | 421.5 | 408 | 380.5 | 436.5 | 64.6 | 115.5 | 152.7 | 131.7 | 233.7 | 224.3 | 120.1 | 196.5 | 214.7 | 167.6
1344.3 | 1125.3 | 376.9 | 150.76 | 176.2298 | 228.2 | 202.9 | 226.2 | 220.7 | 320.8 | 37.1 | 20.6 | 68.1 | 8.5 | 254.2 | 5.8 | 688.2 | 583 | 623.4 | 652.9 | 561.3 | 383.3 | 418.9 | 410 | 378.8 | 436.2 | 64.6 | 115.6 | 152.7 | 131.8 | 233.9 | 224.2 | 120.2 | 196.6 | 214.8 | 167.7
1345.3 | 1126.3 | 377.1 | 150.84 | 176.3233 | 227.8 | 204 | 225.7 | 221.5 | 322.3 | 37 | 20.6 | 68.1 | 7.6 | 274.7 | 5.6 | 686.7 | 580 | 631.2 | 650.1 | 560.6 | 383.6 | 417.1 | 405.1 | 378.2 | 435 | 64.7 | 115.7 | 152.8 | 131.9 | 234 | 224.5 | 120.3 | 196.7 | 214.9 | 167.9
1346.3 | 1127.3 | 377 | 150.8 | 176.2765 | 228.5 | 203.8 | 225.2 | 222 | 320.2 | 37 | 20.6 | 68.2 | 7.1 | 273.9 | 6 | 685.9 | 578.7 | 638.4 | 647.8 | 561 | 383.8 | 413.7 | 402.8 | 376.4 | 433.6 | 64.8 | 115.7 | 152.9 | 132 | 234.6 | 224.6 | 120.4 | 196.9 | 215 | 168
1347.3 | 1128.3 | 377.3 | 150.92 | 176.4168 | 227.6 | 203.3 | 224.9 | 223.2 | 321.6 | 37.1 | 20.6 | 68.3 | 7.4 | 300.9 | 6.7 | 682.7 | 562.7 | 625.8 | 642.9 | 559 | 384 | 410.7 | 399.3 | 374.8 | 431.9 | 64.9 | 115.8 | 153.1 | 132.1 | 235.2 | 225.1 | 120.5 | 196.9 | 215.1 | 168.1
1348.3 | 1129.3 | 377.1 | 150.84 | 176.3233 | 228.3 | 203 | 224.8 | 223.9 | 321.2 | 37.1 | 20.6 | 68.3 | 7.2 | 289.2 | 7.6 | 678.5 | 549.7 | 610.3 | 638.8 | 556.9 | 384.2 | 405.4 | 389.8 | 374.5 | 430 | 65 | 115.9 | 153.1 | 132.2 | 235.1 | 225.1 | 120.6 | 197 | 215.1 | 168.2
1349.3 | 1130.3 | 377.4 | 150.96 | 176.4635 | 229.3 | 203.3 | 225.4 | 224.6 | 316.9 | 37.2 | 20.6 | 68.4 | 6.9 | 292.9 | 8.3 | 673.3 | 534.1 | 597 | 633.5 | 554.4 | 384.4 | 402.1 | 382.5 | 373 | 428.3 | 65 | 116 | 153.3 | 132.3 | 235.2 | 224.9 | 120.7 | 197 | 215.2 | 168.3
1350.3 | 1131.3 | 378.3 | 151.32 | 176.8844 | 228.8 | 203.5 | 225.7 | 224.5 | 314.2 | 37.2 | 20.6 | 68.4 | 7.1 | 293.8 | 8.6 | 668.8 | 517.9 | 589.3 | 628.4 | 552.1 | 384.6 | 398.4 | 375.8 | 370.3 | 426.5 | 65.1 | 116.1 | 153.5 | 132.3 | 235.7 | 224.9 | 120.7 | 197.1 | 215.2 | 168.5
1351.3 | 1132.3 | 376.6 | 150.64 | 176.0895 | 229.6 | 203.5 | 225.1 | 224.3 | 310.3 | 37.2 | 20.6 | 68.3 | 7.7 | 278.6 | 8.8 | 669.8 | 536.9 | 599.9 | 630.7 | 552.1 | 384.8 | 398.6 | 378.3 | 369.4 | 426.6 | 65.2 | 116.3 | 153.6 | 132.4 | 235.9 | 224.9 | 120.9 | 197.2 | 215.3 | 168.6
1352.3 | 1133.3 | 376.4 | 150.56 | 175.996 | 229.7 | 202.5 | 225.1 | 223.6 | 310.2 | 37.1 | 20.6 | 68.3 | 7.5 | 285 | 8.3 | 672.5 | 558.5 | 616.3 | 633.9 | 554.9 | 384.9 | 400 | 384.1 | 369.2 | 426.6 | 65.3 | 116.4 | 154 | 132.5 | 235.7 | 225.2 | 121 | 197.4 | 215.3 | 168.8
1353.3 | 1134.3 | 376.6 | 150.64 | 176.0895 | 229.3 | 201.2 | 224.5 | 223.4 | 312.4 | 37 | 20.6 | 68.3 | 6.6 | 274.7 | 7.3 | 674.3 | 562.1 | 626.2 | 637.5 | 554.8 | 385.1 | 400.8 | 385 | 368.9 | 426.2 | 65.4 | 116.5 | 154 | 132.6 | 235.1 | 225.4 | 121.1 | 197.4 | 215.4 | 168.9
1354.3 | 1135.3 | 376.5 | 150.6 | 176.0427 | 228.9 | 201.5 | 225.1 | 223.1 | 313.2 | 36.9 | 20.6 | 68.4 | 6.6 | 256.2 | 6 | 680.8 | 587 | 649.6 | 650.7 | 559.2 | 385.3 | 411.5 | 397.3 | 373.9 | 429.9 | 65.4 | 116.6 | 154 | 132.7 | 234.8 | 225.2 | 121.1 | 197.5 | 215.5 | 169
1355.3 | 1136.3 | 376.6 | 150.64 | 176.0895 | 228.3 | 202.2 | 224.7 | 221.9 | 321.2 | 36.8 | 20.6 | 68.4 | 6.5 | 254.3 | 5.2 | 683.6 | 599.9 | 660.4 | 654.7 | 562.7 | 385.5 | 418.2 | 408.9 | 376.1 | 429.8 | 65.5 | 116.7 | 154.2 | 132.8 | 235 | 224.6 | 121.3 | 197.5 | 215.7 | 169
1356.3 | 1137.3 | 376.7 | 150.68 | 176.1362 | 227.5 | 202.6 | 223.4 | 220.7 | 323.9 | 36.7 | 20.6 | 68.6 | 6.8 | 261.7 | 4.9 | 685.1 | 603.7 | 659.7 | 657.4 | 564 | 385.7 | 419.2 | 410.1 | 376.4 | 430.2 | 65.6 | 116.8 | 154.2 | 132.9 | 235.2 | 224.1 | 121.4 | 197.5 | 215.8 | 169.2
1357.3 | 1138.3 | 376.7 | 150.68 | 176.1362 | 227 | 202.6 | 223.3 | 221.6 | 324.6 | 36.6 | 20.6 | 68.6 | 7 | 268.3 | 5.3 | 683.1 | 596.1 | 660.2 | 654.5 | 563.6 | 385.9 | 416.8 | 405.9 | 376 | 429.6 | 65.7 | 116.9 | 154.2 | 133 | 235.3 | 224 | 121.4 | 197.5 | 215.9 | 169.3
1358.3 | 1139.3 | 376.8 | 150.72 | 176.183 | 225.6 | 202.2 | 223.3 | 222 | 323.8 | 36.4 | 20.6 | 68.6 | 6.6 | 268.9 | 5.5 | 683 | 601.9 | 658.4 | 656.3 | 563.1 | 386.1 | 418.8 | 409.2 | 376.7 | 430.4 | 65.7 | 117.1 | 154.3 | 133.1 | 235.5 | 224 | 121.6 | 197.6 | 216 | 169.4
1359.3 | 1140.3 | 376.7 | 150.68 | 176.1362 | 225 | 201.3 | 223 | 222.8 | 323.6 | 36.3 | 20.6 | 68.6 | 5.7 | 260.8 | 5.3 | 681.7 | 588.5 | 649.6 | 653 | 562.2 | 386.3 | 416.4 | 403 | 375.3 | 428.9 | 65.8 | 117.2 | 154.5 | 133.1 | 235.5 | 224.2 | 121.7 | 197.7 | 216.1 | 169.5
1360.3 | 1141.3 | 377 | 150.8 | 176.2765 | 225.1 | 200.7 | 224.1 | 223 | 320.1 | 36.1 | 20.6 | 68.6 | 6.9 | 258.7 | 5.5 | 680.7 | 587 | 638 | 652.7 | 560 | 386.5 | 412.3 | 400.8 | 373.2 | 427 | 65.9 | 117.3 | 154.6 | 133.2 | 235.5 | 223.7 | 121.8 | 197.7 | 216.2 | 169.6
1361.3 | 1142.3 | 376.9 | 150.76 | 176.2298 | 225.4 | 200.5 | 224.7 | 222.4 | 318.6 | 36.1 | 20.6 | 68.6 | 7.1 | 266.6 | 5.4 | 680.1 | 591.3 | 639.5 | 650.9 | 558.6 | 386.7 | 411.7 | 403.3 | 372.3 | 426.3 | 66 | 117.5 | 154.8 | 133.3 | 235.4 | 223.6 | 121.9 | 197.7 | 216.3 | 169.8
1362.3 | 1143.3 | 377 | 150.8 | 176.2765 | 225.8 | 200.3 | 225.4 | 222.4 | 319.8 | 36.1 | 20.6 | 68.7 | 6.6 | 269.2 | 5.1 | 679.8 | 583 | 636.2 | 650.9 | 558.2 | 386.9 | 415.8 | 399.8 | 374 | 427.6 | 66.1 | 117.6 | 154.9 | 133.4 | 235.7 | 223.5 | 122 | 197.9 | 216.4 | 169.9
1363.3 | 1144.3 | 377 | 150.8 | 176.2765 | 225.3 | 199.5 | 225.3 | 222 | 318.5 | 36.1 | 20.6 | 68.8 | 6.1 | 275.2 | 4.8 | 678.6 | 570 | 633.6 | 649.2 | 557 | 387.1 | 414.9 | 394.4 | 373.8 | 426.5 | 66.1 | 117.7 | 155.1 | 133.5 | 237.1 | 223.6 | 122 | 198 | 216.5 | 170
1364.3 | 1145.3 | 377 | 150.8 | 176.2765 | 224.9 | 198.6 | 224.5 | 221.6 | 316.9 | 36.2 | 20.6 | 68.9 | 5.9 | 277.2 | 4.6 | 679.7 | 595.3 | 647.5 | 651.3 | 558.2 | 387.3 | 415.2 | 402.4 | 373.4 | 426.5 | 66.2 | 117.8 | 155.1 | 133.5 | 237 | 223.4 | 122.2 | 198 | 216.6 | 170.1
1365.3 | 1146.3 | 376.9 | 150.76 | 176.2298 | 224.9 | 198.8 | 224.3 | 222.1 | 319 | 36.3 | 20.6 | 69.1 | 5.9 | 276 | 4.2 | 680.9 | 597.7 | 656.3 | 652.8 | 561.9 | 387.4 | 418.5 | 409.7 | 374.7 | 427.7 | 66.3 | 117.9 | 155.1 | 133.6 | 237.5 | 223.7 | 122.3 | 198.1 | 216.7 | 170.3
1366.3 | 1147.3 | 376.9 | 150.76 | 176.2298 | 224.8 | 199.9 | 225.1 | 222.5 | 323.3 | 36.3 | 20.6 | 69.1 | 6.5 | 275.6 | 3.8 | 679.8 | 580.5 | 645.2 | 652.4 | 560.6 | 387.6 | 423.9 | 406.2 | 377.7 | 428.2 | 66.4 | 118 | 155.2 | 133.7 | 237.4 | 224.2 | 122.3 | 198.2 | 216.8 | 170.4
1367.3 | 1148.3 | 377 | 150.8 | 176.2765 | 225.9 | 200.9 | 225.6 | 223.2 | 324.3 | 36.4 | 20.6 | 69.1 | 6.7 | 274.5 | 3.4 | 677.1 | 564.1 | 634.1 | 649.3 | 558.4 | 387.8 | 419.5 | 396.8 | 376.3 | 426.2 | 66.5 | 118.2 | 155.4 | 133.8 | 237.9 | 224.8 | 122.4 | 198.3 | 216.9 | 170.5
1368.3 | 1149.3 | 377.6 | 151.04 | 176.5571 | 226.1 | 201.7 | 226 | 223.7 | 322.4 | 36.4 | 20.6 | 69.1 | 7.3 | 269.7 | 3.1 | 676.7 | 568.4 | 631.7 | 649.2 | 558.8 | 388 | 418.3 | 399.2 | 375.6 | 425.8 | 66.5 | 118.3 | 155.5 | 133.9 | 238.1 | 224.7 | 122.5 | 198.4 | 217 | 170.6
1369.3 | 1150.3 | 374.3 | 149.72 | 175.0141 | 226.3 | 202.5 | 226 | 224.2 | 323.5 | 36.5 | 20.6 | 69 | 8.4 | 263.9 | 3.1 | 678.3 | 579.8 | 637.1 | 651.7 | 559.3 | 388.1 | 419.6 | 401 | 375.7 | 426.4 | 66.6 | 118.4 | 155.6 | 133.9 | 238.3 | 224.8 | 122.7 | 198.6 | 217.1 | 170.7
1370.3 | 1151.3 | 374 | 149.6 | 174.8738 | 226.3 | 203.6 | 225.6 | 224.7 | 321.1 | 36.4 | 20.6 | 68.9 | 9.5 | 248.9 | 3.1 | 677.5 | 572.4 | 633.1 | 648.7 | 557.6 | 388.2 | 416.9 | 398.4 | 374.8 | 424.5 | 66.7 | 118.5 | 155.7 | 134 | 238.4 | 225.2 | 122.7 | 198.6 | 217.2 | 170.9
1371.3 | 1152.3 | 375.7 | 150.28 | 175.6687 | 225.9 | 204.3 | 225.7 | 225.7 | 320.6 | 36.4 | 20.6 | 68.9 | 9.7 | 233.7 | 3.1 | 676.9 | 571.7 | 635.1 | 645.7 | 556.9 | 388.4 | 414.1 | 395.8 | 373 | 423.1 | 66.8 | 118.7 | 155.9 | 134.1 | 238.1 | 226.2 | 122.9 | 198.8 | 217.2 | 171
1372.3 | 1153.3 | 376.3 | 150.52 | 175.9492 | 225.9 | 203.9 | 225.3 | 226.5 | 319.3 | 36.4 | 20.6 | 68.8 | 9.4 | 243.2 | 3.3 | 676 | 574.6 | 636.4 | 644.6 | 557 | 388.6 | 409.9 | 391 | 370.8 | 421.8 | 66.9 | 118.8 | 156 | 134.2 | 237.7 | 226.7 | 123 | 199 | 217.3 | 171.1
1373.3 | 1154.3 | 376.1 | 150.44 | 175.8557 | 226.5 | 203.2 | 224.9 | 226.9 | 319.2 | 36.4 | 20.6 | 68.7 | 8.8 | 244.4 | 3.6 | 676.1 | 575.5 | 632.3 | 645.2 | 555.5 | 388.8 | 408.1 | 390.2 | 369.8 | 421 | 67 | 118.9 | 156.1 | 134.3 | 237.4 | 226.5 | 123 | 199 | 217.4 | 171.2
1374.3 | 1155.3 | 375.4 | 150.16 | 175.5284 | 227.5 | 203.7 | 224.2 | 226 | 318.4 | 36.4 | 20.6 | 68.7 | 8.8 | 242 | 3.8 | 675.5 | 581.3 | 632.3 | 645.4 | 555.4 | 389 | 405.2 | 389.2 | 368.3 | 420.3 | 67 | 118.9 | 156.2 | 134.4 | 237.1 | 226.2 | 123.1 | 199 | 217.5 | 171.3
1375.3 | 1156.3 | 376.8 | 150.72 | 176.183 | 227.6 | 204.5 | 223.7 | 226.2 | 319.7 | 36.5 | 20.6 | 68.7 | 10 | 251.9 | 4.1 | 676.7 | 589.2 | 635.7 | 648.5 | 554.9 | 389.2 | 409.2 | 395.4 | 369 | 420.7 | 67.1 | 119 | 156.3 | 134.5 | 236.9 | 226 | 123.2 | 199 | 217.5 | 171.4
1376.3 | 1157.3 | 377.2 | 150.88 | 176.37 | 226.5 | 205.1 | 223.1 | 226.4 | 322.7 | 36.8 | 20.6 | 68.7 | 9.4 | 252.9 | 5.3 | 680.7 | 602.4 | 650.7 | 654 | 557.5 | 389.4 | 414.1 | 414 | 370.1 | 421.9 | 67.2 | 119.1 | 156.4 | 134.5 | 237.1 | 225.7 | 123.3 | 199 | 217.6 | 171.5
1377.3 | 1158.3 | 377.1 | 150.84 | 176.3233 | 225.9 | 205.1 | 223.3 | 226.5 | 327 | 37 | 20.6 | 68.9 | 8.1 | 253.5 | 5.7 | 683.1 | 611.3 | 662.7 | 656.8 | 559.8 | 389.6 | 421.1 | 417.9 | 372.2 | 422.7 | 67.3 | 119.2 | 156.4 | 134.6 | 237 | 225.7 | 123.4 | 199.1 | 217.7 | 171.7
1378.3 | 1159.3 | 377.1 | 150.84 | 176.3233 | 225.2 | 204.3 | 223.2 | 226.8 | 334.2 | 37.1 | 20.6 | 69 | 9.6 | 253.5 | 5.4 | 686 | 629.5 | 679.9 | 662.7 | 566.1 | 389.8 | 432.5 | 432.5 | 378 | 425.8 | 67.3 | 119.3 | 156.5 | 134.7 | 237.2 | 225.6 | 123.5 | 199.2 | 217.9 | 171.8
1379.3 | 1160.3 | 375.8 | 150.32 | 175.7154 | 224.6 | 204.1 | 223.3 | 226 | 340 | 37.3 | 20.6 | 69.1 | 9.3 | 197.1 | 5.6 | 689.6 | 637.8 | 680.4 | 669.2 | 565.9 | 390 | 444.7 | 431.3 | 385.7 | 427.6 | 67.4 | 119.4 | 156.8 | 134.8 | 237.1 | 225.5 | 123.6 | 199.3 | 218 | 171.9
1380.3 | 1161.3 | 375.9 | 150.36 | 175.7622 | 224.4 | 204 | 223.5 | 225.3 | 338.3 | 37.4 | 20.6 | 69.1 | 8.9 | 210 | 5.8 | 688.7 | 628.5 | 679.4 | 668.9 | 565.9 | 390.2 | 440.4 | 424.1 | 383.3 | 426.4 | 67.5 | 119.5 | 156.9 | 134.9 | 236.8 | 225.7 | 123.7 | 199.3 | 218.2 | 172
1381.3 | 1162.3 | 375.9 | 150.36 | 175.7622 | 224.1 | 203.7 | 223.3 | 225.8 | 337 | 37.5 | 20.6 | 69.2 | 8.1 | 239.6 | 8.6 | 686.5 | 615.7 | 670.9 | 666.4 | 564.9 | 390.4 | 436.1 | 419.3 | 381.9 | 425.3 | 67.6 | 119.6 | 156.9 | 135 | 236.6 | 225.7 | 123.8 | 199.4 | 218.4 | 172.1
1382.3 | 1163.3 | 377.2 | 150.88 | 176.37 | 224 | 202.8 | 223.9 | 225 | 335.9 | 37.5 | 20.6 | 69.2 | 7.1 | 235.8 | 12.6 | 686.8 | 612.9 | 679.9 | 668.1 | 566.3 | 390.6 | 435.1 | 419.9 | 381.1 | 425.4 | 67.7 | 119.7 | 156.9 | 135.1 | 236.4 | 225.7 | 123.9 | 199.4 | 218.4 | 172.2
1383.3 | 1164.3 | 378 | 151.2 | 176.7441 | 224.1 | 202.3 | 224 | 223.9 | 336.9 | 37.6 | 20.6 | 69.1 | 7 | 229.6 | 12.3 | 690.1 | 615.7 | 685.2 | 676.6 | 567.4 | 390.7 | 438.8 | 429.4 | 382.1 | 427.2 | 67.8 | 119.8 | 157 | 135.1 | 236.2 | 226 | 124 | 199.5 | 218.5 | 172.3
1384.3 | 1165.3 | 378.2 | 151.28 | 176.8376 | 224.4 | 201.6 | 223.4 | 223 | 342.4 | 37.6 | 20.6 | 69 | 7.3 | 233.8 | 10.8 | 693.4 | 616.1 | 685.1 | 684 | 567.9 | 391 | 451 | 435.1 | 385.2 | 428.7 | 67.8 | 119.9 | 157.2 | 135.2 | 235.9 | 225.6 | 124.1 | 199.7 | 218.6 | 172.4
1385.3 | 1166.3 | 378.1 | 151.24 | 176.7908 | 225 | 201.6 | 223.1 | 223.2 | 340.6 | 37.6 | 20.6 | 68.9 | 7.5 | 250 | 10.4 | 696.1 | 617 | 684.1 | 687.8 | 567.7 | 391.2 | 454.8 | 433 | 386.8 | 429.5 | 67.9 | 120 | 157.3 | 135.3 | 235.8 | 226 | 124.2 | 199.7 | 218.8 | 172.5
1386.3 | 1167.3 | 379 | 151.6 | 177.2117 | 224.8 | 202.6 | 223.7 | 223.5 | 337.2 | 37.6 | 20.6 | 69 | 7.5 | 245.6 | 10.4 | 697.3 | 630.6 | 686.9 | 688.9 | 568.4 | 391.4 | 457.2 | 432.2 | 387.6 | 429.6 | 68 | 120.1 | 157.5 | 135.4 | 235.8 | 226.2 | 124.3 | 199.8 | 218.9 | 172.6
1387.3 | 1168.3 | 379.9 | 151.96 | 177.6325 | 224.6 | 203 | 223.8 | 224.4 | 337.1 | 37.6 | 20.6 | 69 | 7.8 | 245.8 | 10.4 | 696.9 | 619.6 | 678.3 | 690 | 566.6 | 391.6 | 457.2 | 431 | 388 | 429.2 | 68.1 | 120.2 | 157.5 | 135.4 | 235.7 | 226 | 124.4 | 199.8 | 219 | 172.7
1388.3 | 1169.3 | 381.8 | 152.72 | 178.5209 | 223.7 | 204 | 224.2 | 225.2 | 336.3 | 37.6 | 20.6 | 69 | 7.5 | 243.8 | 10.7 | 691.8 | 590.7 | 655.8 | 682.2 | 562.2 | 391.8 | 451.6 | 417.1 | 386.4 | 426.8 | 68.2 | 120.3 | 157.5 | 135.5 | 235.9 | 225.9 | 124.5 | 199.9 | 219.1 | 172.9
1389.3 | 1170.3 | 384.6 | 153.84 | 179.8301 | 222.7 | 204.2 | 224.8 | 225.4 | 332.1 | 37.6 | 20.6 | 69 | 8.3 | 252.9 | 11.6 | 687 | 577.5 | 641.5 | 673.7 | 559.7 | 392.1 | 442 | 408.2 | 383.1 | 424.7 | 68.2 | 120.4 | 157.5 | 135.6 | 236 | 225.7 | 124.6 | 200 | 219.2 | 173
1390.3 | 1171.3 | 383.2 | 153.28 | 179.1755 | 222.2 | 204.6 | 224.9 | 225.3 | 327.7 | 37.6 | 20.6 | 69.1 | 7.7 | 248.5 | 12 | 682.6 | 565.3 | 631.4 | 667.1 | 558.1 | 392.3 | 437.5 | 403.2 | 382.2 | 424.1 | 68.3 | 120.5 | 157.7 | 135.7 | 235.5 | 225.7 | 124.7 | 200 | 219.3 | 173.1
1391.3 | 1172.3 | 385.6 | 154.24 | 180.2977 | 221.6 | 204.3 | 224.7 | 224.9 | 325.3 | 37.6 | 20.6 | 69.2 | 7.3 | 245.3 | 11.9 | 681.2 | 581.2 | 634 | 665.1 | 558.2 | 392.5 | 432.5 | 405.3 | 380.5 | 423.3 | 68.4 | 120.6 | 157.9 | 135.7 | 234.9 | 225.6 | 124.8 | 200.1 | 219.3 | 173.2
1392.3 | 1173.3 | 400.5 | 160.2 | 187.2646 | 222.6 | 203.3 | 223.6 | 223.6 | 325.3 | 37.4 | 20.6 | 69.4 | 7.4 | 241.8 | 11.9 | 678.7 | 574.9 | 630.1 | 661.1 | 557.1 | 392.7 | 429.2 | 398.8 | 379.7 | 422.1 | 68.5 | 120.7 | 158 | 135.8 | 234.3 | 225.6 | 124.9 | 200.2 | 219.4 | 173.3
1393.3 | 1174.3 | 421.2 | 168.48 | 196.9434 | 223.5 | 202.1 | 222.2 | 223.2 | 321.5 | 37.4 | 20.6 | 69.5 | 7.2 | 234.4 | 11.3 | 678.3 | 573 | 631.3 | 660.1 | 555.9 | 392.9 | 426.4 | 395.9 | 378.3 | 422.2 | 68.6 | 120.8 | 158.1 | 135.9 | 233.6 | 225.6 | 125 | 200.3 | 219.5 | 173.4
1394.3 | 1175.3 | 434.7 | 173.88 | 203.2557 | 223.3 | 201.8 | 221.8 | 222.5 | 320.6 | 37.3 | 20.6 | 69.6 | 7.8 | 244.9 | 10.7 | 678.5 | 570.2 | 621.5 | 660.5 | 554.4 | 393.1 | 422.1 | 395.1 | 376.6 | 420.9 | 68.6 | 120.8 | 158.2 | 135.9 | 233.2 | 225.4 | 125 | 200.3 | 219.6 | 173.5
1395.3 | 1176.3 | 440.8 | 176.32 | 206.1079 | 223.7 | 202 | 222.3 | 222.2 | 320.6 | 37.4 | 20.6 | 69.8 | 8 | 237.2 | 9.8 | 679 | 582.4 | 621 | 657.9 | 553.7 | 393.4 | 420.5 | 400.5 | 375 | 420.6 | 68.7 | 120.9 | 158.3 | 136 | 232.9 | 225.3 | 125.1 | 200.3 | 219.7 | 173.6
1396.3 | 1177.3 | 443.6 | 177.44 | 207.4171 | 224.2 | 201.8 | 223.2 | 222 | 322.8 | 37.4 | 20.6 | 70 | 8 | 239.1 | 8.7 | 678.9 | 591.4 | 619.6 | 655.3 | 553.3 | 393.7 | 420.4 | 403.6 | 374.9 | 420.4 | 68.8 | 121 | 158.3 | 136.1 | 232.8 | 225.3 | 125.3 | 200.4 | 219.8 | 173.7
1397.3 | 1178.3 | 445.2 | 178.08 | 208.1653 | 224.5 | 202 | 223.5 | 221.5 | 325 | 37.3 | 20.5 | 70.1 | 7.3 | 238.5 | 7.8 | 676.6 | 585.6 | 611.6 | 651.2 | 552.1 | 393.9 | 418.2 | 401.9 | 374.5 | 419.4 | 68.9 | 121.1 | 158.4 | 136.2 | 232.8 | 225.3 | 125.3 | 200.5 | 219.8 | 173.8
1398.3 | 1179.3 | 445.2 | 178.08 | 208.1653 | 224 | 202.8 | 223.6 | 221.2 | 324.6 | 37.3 | 20.6 | 70.3 | 7.8 | 206.6 | 7 | 673 | 576.1 | 608.1 | 646.1 | 550.3 | 394.1 | 412.4 | 395.4 | 372.5 | 417.7 | 69 | 121.1 | 158.6 | 136.2 | 233.8 | 225.3 | 125.4 | 200.6 | 219.9 | 173.9
1399.3 | 1180.3 | 446.9 | 178.76 | 208.9601 | 224.2 | 203.9 | 224.4 | 221.7 | 320.7 | 37.2 | 20.6 | 70.4 | 8.7 | 205.4 | 8.2 | 669.5 | 559.8 | 601.8 | 641.4 | 548.3 | 394.4 | 409.6 | 390.7 | 371.8 | 417.1 | 69 | 121.2 | 158.8 | 136.3 | 234 | 225.5 | 125.5 | 200.8 | 220 | 174.1
1400.3 | 1181.3 | 446.9 | 178.76 | 208.9601 | 225.1 | 204.7 | 225.1 | 222.5 | 318.4 | 37.1 | 20.6 | 70.3 | 8 | 218.7 | 8.2 | 666.1 | 554.2 | 592.5 | 637 | 546.4 | 394.6 | 404.4 | 383.8 | 370.3 | 415.5 | 69.1 | 121.3 | 158.9 | 136.3 | 234.3 | 225.7 | 125.6 | 201 | 220 | 174.2
1401.3 | 1182.3 | 449 | 179.6 | 209.9421 | 227.7 | 205.3 | 225.6 | 222.9 | 315.7 | 37.1 | 20.5 | 70.3 | 8.4 | 228.5 | 7.9 | 663.8 | 549.6 | 583.7 | 633.8 | 544.9 | 394.8 | 401.8 | 379.2 | 369.4 | 414.4 | 69.2 | 121.4 | 159 | 136.4 | 234.4 | 226 | 125.8 | 201.1 | 220.1 | 174.3
1402.3 | 1183.3 | 450.2 | 180.08 | 210.5031 | 228.8 | 206.5 | 226.5 | 223.4 | 315.1 | 37.1 | 20.5 | 70.4 | 7.5 | 210.2 | 8.2 | 663.3 | 550.8 | 580.8 | 631.7 | 544.1 | 394.9 | 400.5 | 377.3 | 367.9 | 413.6 | 69.3 | 121.5 | 159.1 | 136.5 | 235 | 226.3 | 125.8 | 201.2 | 220.1 | 174.5
1403.3 | 1184.3 | 449 | 179.6 | 209.9421 | 229.6 | 207.7 | 227.4 | 223.7 | 313.9 | 37.2 | 20.6 | 70.4 | 6.8 | 221.7 | 8.4 | 663.4 | 553.7 | 593.1 | 630.8 | 544.5 | 395.1 | 401.4 | 382.1 | 367.1 | 413.7 | 69.4 | 121.6 | 159.2 | 136.6 | 235.3 | 227 | 125.9 | 201.3 | 220.2 | 174.6
1404.3 | 1185.3 | 450 | 180 | 210.4096 | 229.1 | 208.3 | 227.9 | 224.4 | 316 | 37.4 | 20.5 | 70.6 | 6.5 | 231.7 | 8.6 | 666.1 | 563.2 | 603.4 | 633.3 | 546.3 | 395.3 | 406.7 | 391.1 | 369 | 415.8 | 69.5 | 121.7 | 159.5 | 136.6 | 235.5 | 228.3 | 126 | 201.5 | 220.2 | 174.7
1405.3 | 1186.3 | 450.8 | 180.32 | 210.7837 | 229.2 | 209.2 | 227.4 | 224.7 | 321.4 | 37.6 | 20.5 | 70.6 | 6.6 | 254.1 | 7.6 | 668.9 | 583.2 | 604.3 | 635.5 | 546.4 | 395.4 | 409.4 | 401.6 | 370.3 | 416.4 | 69.5 | 121.7 | 159.5 | 136.7 | 235.7 | 228.8 | 126.1 | 201.6 | 220.3 | 174.8
1406.3 | 1187.3 | 451.4 | 180.56 | 211.0642 | 229.7 | 209.7 | 226.6 | 224.8 | 324.6 | 37.7 | 20.5 | 70.7 | 6.6 | 238.7 | 8.2 | 671.6 | 599.9 | 607.2 | 637.8 | 546.5 | 395.4 | 412.9 | 408 | 371.2 | 416.8 | 69.6 | 121.8 | 159.6 | 136.8 | 235.7 | 229.1 | 126.2 | 201.7 | 220.4 | 174.9
1407.3 | 1188.3 | 452.3 | 180.92 | 211.4851 | 231.3 | 209.6 | 226.8 | 224.6 | 324.8 | 37.7 | 20.5 | 70.8 | 7.5 | 257.4 | 8.5 | 671.8 | 596.2 | 613.5 | 639 | 546.3 | 395.5 | 409.8 | 405.9 | 369.9 | 415.9 | 69.7 | 121.9 | 159.8 | 136.9 | 236 | 228.9 | 126.3 | 201.8 | 220.5 | 175.1
1408.3 | 1189.3 | 453.1 | 181.24 | 211.8591 | 232.5 | 209.7 | 227.7 | 226.3 | 323.2 | 37.6 | 20.5 | 70.9 | 7.2 | 264.3 | 8.7 | 673.3 | 595.8 | 620.6 | 644.2 | 547.8 | 395.6 | 411.7 | 408.9 | 370.8 | 416.3 | 69.8 | 121.9 | 159.9 | 136.9 | 236.6 | 229.2 | 126.4 | 201.9 | 220.6 | 175.2
1409.3 | 1190.3 | 453.5 | 181.4 | 212.0461 | 233.8 | 208.8 | 228.8 | 227.4 | 328.1 | 37.5 | 20.5 | 71 | 7.8 | 253.6 | 9.2 | 672.5 | 585.6 | 605.8 | 644.2 | 545.7 | 395.8 | 411.4 | 405.8 | 370.7 | 415.4 | 69.9 | 122 | 160 | 137 | 237.4 | 229.5 | 126.5 | 202 | 220.6 | 175.3
1410.3 | 1191.3 | 453.1 | 181.24 | 211.8591 | 235.8 | 208.3 | 230 | 227.6 | 329.7 | 37.5 | 20.5 | 71 | 8 | 253.5 | 10.3 | 670.2 | 574.9 | 601.2 | 642.4 | 544.9 | 395.9 | 409.7 | 403.5 | 370.1 | 414.7 | 69.9 | 122.1 | 160.1 | 137.1 | 237.7 | 229.9 | 126.6 | 202.2 | 220.7 | 175.4
1411.3 | 1192.3 | 455.5 | 182.2 | 212.9813 | 236.4 | 209.1 | 231.4 | 228.2 | 328.4 | 37.5 | 20.5 | 70.9 | 7.3 | 253.7 | 9.9 | 668 | 559.8 | 598.7 | 640.9 | 543.9 | 396.1 | 407.7 | 397.1 | 369.2 | 413.8 | 70 | 122.2 | 160.2 | 137.2 | 238.3 | 230.2 | 126.7 | 202.3 | 220.8 | 175.6
1412.3 | 1193.3 | 456 | 182.4 | 213.2151 | 237.7 | 209.5 | 232.5 | 228.9 | 326.5 | 37.4 | 20.5 | 70.9 | 7.6 | 255.5 | 9.7 | 667.4 | 551.7 | 597.4 | 640.1 | 542.7 | 396.2 | 406.8 | 392.4 | 368.6 | 413.1 | 70.1 | 122.3 | 160.2 | 137.3 | 239 | 230.6 | 126.8 | 202.4 | 220.9 | 175.7
1413.3 | 1194.3 | 457.4 | 182.96 | 213.8697 | 238.7 | 208.7 | 233.6 | 230.2 | 326.1 | 37.5 | 20.5 | 70.8 | 6.8 | 259.3 | 9.8 | 668.3 | 556.7 | 588.8 | 641.3 | 541.5 | 396.4 | 407.1 | 399.7 | 368 | 413.2 | 70.2 | 122.4 | 160.3 | 137.4 | 239.4 | 230.6 | 126.9 | 202.6 | 220.9 | 175.8
1414.3 | 1195.3 | 457.9 | 183.16 | 214.1035 | 239.8 | 208.5 | 234 | 230.8 | 328.1 | 37.4 | 20.5 | 70.9 | 7.5 | 263.8 | 10.2 | 667.2 | 559.7 | 585.5 | 640 | 540.3 | 396.5 | 403.4 | 395.4 | 366.1 | 411.9 | 70.3 | 122.5 | 160.5 | 137.5 | 239.7 | 230.6 | 126.9 | 202.7 | 221 | 176
1415.3 | 1196.3 | 458.9 | 183.56 | 214.5711 | 240.8 | 208.3 | 234.1 | 232.3 | 325.2 | 37.4 | 20.5 | 70.8 | 7.7 | 266.2 | 10.6 | 664.4 | 548.5 | 576.7 | 637.5 | 538.2 | 396.6 | 402 | 391 | 365.5 | 410.9 | 70.3 | 122.6 | 160.7 | 137.6 | 240.4 | 230.6 | 127.1 | 202.8 | 221 | 176.1
1416.3 | 1197.3 | 458.8 | 183.52 | 214.5243 | 240.3 | 208.6 | 234.4 | 232.7 | 324.7 | 37.5 | 20.5 | 70.8 | 8.1 | 260.5 | 9.6 | 661.2 | 533.2 | 571.6 | 633.6 | 537.1 | 396.7 | 398.2 | 385.2 | 364.2 | 409.8 | 70.4 | 122.7 | 160.8 | 137.7 | 240.5 | 230.7 | 127.2 | 203 | 221.1 | 176.2
1417.3 | 1198.3 | 460.4 | 184.16 | 215.2724 | 239.8 | 207.7 | 233.9 | 233.1 | 321.1 | 37.6 | 20.5 | 70.9 | 7.1 | 250.1 | 8.5 | 658.4 | 525 | 566.6 | 630.6 | 536 | 396.9 | 398 | 382.9 | 364.3 | 408.9 | 70.5 | 122.8 | 161 | 137.8 | 240.6 | 231 | 127.3 | 203.1 | 221.2 | 176.4
1418.3 | 1199.3 | 460.3 | 184.12 | 215.2257 | 241.3 | 208.1 | 233.9 | 233.4 | 322.3 | 37.7 | 20.5 | 71 | 6.6 | 255.7 | 7.8 | 658.1 | 532.9 | 566.8 | 629.7 | 535.6 | 397.1 | 398.7 | 386 | 364.5 | 408.6 | 70.6 | 122.9 | 161.2 | 137.9 | 241.1 | 231.5 | 127.4 | 203.2 | 221.2 | 176.5
1419.3 | 1200.3 | 460.5 | 184.2 | 215.3192 | 242.3 | 207.3 | 233.4 | 233.5 | 329.7 | 37.7 | 20.5 | 71.1 | 6.9 | 255.6 | 7 | 661.4 | 551.4 | 579.6 | 633.8 | 537.1 | 397.2 | 400.7 | 393.4 | 365.3 | 409.2 | 70.7 | 123 | 161.2 | 137.9 | 241.2 | 231.9 | 127.5 | 203.3 | 221.3 | 176.6
1420.3 | 1201.3 | 461.2 | 184.48 | 215.6465 | 243.7 | 206.9 | 233.5 | 233.9 | 332.9 | 37.7 | 20.5 | 71.3 | 6.6 | 253 | 6.6 | 665.7 | 563.8 | 586.4 | 639.6 | 537.5 | 397.4 | 403.2 | 396.7 | 366.5 | 409.6 | 70.8 | 123.1 | 161.4 | 138 | 241.4 | 232.4 | 127.6 | 203.5 | 221.4 | 176.7
1421.3 | 1202.3 | 460.8 | 184.32 | 215.4595 | 242.6 | 208 | 234.7 | 233.7 | 331.7 | 37.7 | 20.5 | 71.5 | 6.6 | 250.5 | 6.3 | 668.7 | 576.1 | 588.8 | 645.2 | 538.2 | 397.6 | 408.1 | 401.5 | 368.5 | 411.1 | 70.8 | 123.3 | 161.5 | 138.1 | 241.7 | 232.8 | 127.6 | 203.7 | 221.4 | 176.9
1422.3 | 1203.3 | 461.9 | 184.76 | 215.9738 | 241.5 | 209.2 | 235.3 | 234.1 | 333.7 | 37.8 | 20.5 | 71.8 | 7.2 | 268.2 | 5.9 | 670.2 | 585 | 593.2 | 645.2 | 538.3 | 397.8 | 412.9 | 405.9 | 370.3 | 411.6 | 70.9 | 123.4 | 161.6 | 138.2 | 241.8 | 233 | 127.8 | 203.8 | 221.6 | 177
1423.3 | 1204.3 | 463.4 | 185.36 | 216.6752 | 241.2 | 209.9 | 235.3 | 235.3 | 337.7 | 37.8 | 20.5 | 72 | 6.6 | 258.7 | 5.2 | 674.3 | 611.1 | 592.3 | 648 | 539.4 | 398 | 418.4 | 424.5 | 372.5 | 412.8 | 71 | 123.5 | 161.8 | 138.3 | 242 | 233.2 | 127.8 | 203.8 | 221.7 | 177.1
1424.3 | 1205.3 | 463.3 | 185.32 | 216.6284 | 241.3 | 210.2 | 234.8 | 236.7 | 341 | 37.8 | 20.5 | 72.2 | 6.8 | 257.1 | 4.5 | 679.9 | 623.6 | 609.8 | 657.4 | 541.3 | 398.2 | 424.8 | 429.6 | 375.2 | 414.6 | 71.1 | 123.6 | 162 | 138.4 | 242.3 | 234 | 128 | 203.9 | 221.8 | 177.2
1425.3 | 1206.3 | 464.6 | 185.84 | 217.2363 | 241.4 | 209.9 | 234.6 | 237.1 | 344.6 | 37.8 | 20.5 | 72.4 | 6.6 | 255.5 | 4 | 683.9 | 635.1 | 622.3 | 665 | 542.1 | 398.4 | 428.7 | 440.1 | 377.5 | 416 | 71.2 | 123.7 | 162.1 | 138.5 | 243.1 | 234.3 | 128.1 | 204.1 | 222 | 177.4
1426.3 | 1207.3 | 465.1 | 186.04 | 217.47 | 240.5 | 209.9 | 234.4 | 238.1 | 348.5 | 37.8 | 20.5 | 72.6 | 6.8 | 253.4 | 3.7 | 686.9 | 643.6 | 629.4 | 671.9 | 542.5 | 398.6 | 433.1 | 445.9 | 380.2 | 418 | 71.2 | 123.8 | 162.2 | 138.6 | 243.6 | 234.7 | 128.2 | 204.3 | 222.1 | 177.5
1427.3 | 1208.3 | 465.5 | 186.2 | 217.6571 | 240 | 209.3 | 234.5 | 238.3 | 351.6 | 37.8 | 20.5 | 72.7 | 7.7 | 237.3 | 3.5 | 687.3 | 639.7 | 633.5 | 673.3 | 542.3 | 398.8 | 438.7 | 451.7 | 383 | 418.6 | 71.3 | 123.9 | 162.3 | 138.7 | 243.5 | 235 | 128.2 | 204.4 | 222.2 | 177.6
1428.3 | 1209.3 | 465.3 | 186.12 | 217.5636 | 240.6 | 209.4 | 234.7 | 238.5 | 354.1 | 37.9 | 20.5 | 72.8 | 7.9 | 220.2 | 3.7 | 687.6 | 631.3 | 633.1 | 673.6 | 541.5 | 399.1 | 437.5 | 443.8 | 383.2 | 417.7 | 71.4 | 124 | 162.4 | 138.8 | 243.8 | 235.2 | 128.4 | 204.5 | 222.3 | 177.8
1429.3 | 1210.3 | 467 | 186.8 | 218.3584 | 241.2 | 210.3 | 234.6 | 239.1 | 352.3 | 37.9 | 20.5 | 72.9 | 7.2 | 233 | 4 | 687.3 | 632.3 | 633.7 | 672.5 | 540.6 | 399.3 | 437.4 | 444.8 | 382.5 | 418.3 | 71.5 | 124.1 | 162.5 | 138.9 | 243.9 | 235.3 | 128.4 | 204.7 | 222.5 | 177.9
1430.3 | 1211.3 | 465.4 | 186.16 | 217.6103 | 240.9 | 210.5 | 234.5 | 240.1 | 349.1 | 38 | 20.5 | 73.1 | 7.4 | 253.7 | 4.6 | 683.1 | 612 | 620.6 | 667 | 538.2 | 399.6 | 434.1 | 434.2 | 381.8 | 417 | 71.6 | 124.3 | 162.8 | 139 | 243.8 | 235.1 | 128.5 | 204.8 | 222.6 | 178.1
1431.3 | 1212.3 | 464.7 | 185.88 | 217.283 | 242.6 | 210.3 | 234.6 | 240.1 | 348.7 | 38 | 20.5 | 73.1 | 6.6 | 236.6 | 5.3 | 680.5 | 603.5 | 617.8 | 664.1 | 536.7 | 399.8 | 429.5 | 427.4 | 380.4 | 415.9 | 71.6 | 124.4 | 162.9 | 139.1 | 243.8 | 235.3 | 128.6 | 205 | 222.7 | 178.2
1432.3 | 1213.3 | 464.7 | 185.88 | 217.283 | 245.1 | 211 | 234.4 | 240.6 | 348.9 | 37.9 | 20.5 | 73.1 | 7 | 248 | 5.7 | 679.5 | 603.7 | 619.2 | 663 | 536.1 | 400.1 | 428.4 | 423.5 | 380.1 | 416.3 | 71.7 | 124.5 | 163.1 | 139.2 | 243.7 | 235.7 | 128.7 | 205.1 | 222.8 | 178.3
1433.3 | 1214.3 | 465 | 186 | 217.4233 | 247.4 | 211.3 | 234.3 | 240.2 | 346.7 | 37.8 | 20.5 | 73.1 | 7.2 | 250.1 | 6.1 | 680.9 | 615.6 | 633.8 | 665.7 | 539.3 | 400.4 | 431.4 | 424.1 | 381.6 | 417.7 | 71.8 | 124.7 | 163.3 | 139.3 | 243.8 | 235.6 | 128.8 | 205.3 | 222.9 | 178.5
1434.3 | 1215.3 | 465.2 | 186.08 | 217.5168 | 248 | 211.3 | 235.5 | 239.8 | 346.6 | 37.7 | 20.5 | 73.2 | 7 | 250 | 6.1 | 686.2 | 634.7 | 655 | 674.4 | 542.5 | 400.6 | 453 | 440.6 | 390.9 | 423.9 | 71.9 | 124.8 | 163.3 | 139.4 | 243.8 | 235.9 | 128.9 | 205.3 | 223 | 178.6
1435.3 | 1216.3 | 464.8 | 185.92 | 217.3298 | 247.3 | 212.6 | 236.8 | 240.4 | 355.2 | 37.7 | 20.5 | 73.3 | 7.2 | 232.8 | 5.8 | 692.7 | 657.3 | 660.8 | 684.9 | 543.9 | 400.9 | 468.9 | 450.7 | 395.9 | 426.5 | 72 | 124.9 | 163.5 | 139.5 | 244.2 | 236.9 | 129 | 205.4 | 223.2 | 178.7
1436.3 | 1217.3 | 463.5 | 185.4 | 216.7219 | 246.6 | 213.7 | 237.1 | 240.5 | 362.6 | 37.7 | 20.5 | 73.3 | 6.6 | 255.1 | 5.7 | 696.4 | 644.8 | 654.1 | 689.7 | 544.7 | 401.1 | 470.1 | 450.1 | 397.1 | 426.8 | 72.1 | 125.1 | 163.7 | 139.7 | 245.1 | 237.1 | 129.1 | 205.6 | 223.4 | 178.9
1437.3 | 1218.3 | 464.3 | 185.72 | 217.096 | 246.3 | 214.2 | 237.4 | 240.8 | 360 | 37.8 | 20.5 | 73.3 | 6.5 | 266.9 | 5.9 | 697.9 | 646 | 653.4 | 693.2 | 545.6 | 401.3 | 467 | 448 | 396.4 | 427.1 | 72.2 | 125.2 | 163.7 | 139.8 | 245.7 | 237 | 129.3 | 205.8 | 223.6 | 179.1
1438.3 | 1219.3 | 463.8 | 185.52 | 216.8622 | 245.9 | 215.1 | 237.5 | 241.7 | 357.6 | 37.8 | 20.5 | 73.4 | 6.8 | 252.4 | 5.3 | 702 | 661.1 | 658.5 | 698.9 | 547.3 | 401.5 | 470.5 | 461.6 | 398 | 429.1 | 72.2 | 125.3 | 163.9 | 139.9 | 246 | 236.9 | 129.3 | 205.9 | 223.7 | 179.2
1439.3 | 1220.3 | 466 | 186.4 | 217.8909 | 245.5 | 216.2 | 237.5 | 242 | 359.5 | 38 | 20.5 | 73.4 | 6.7 | 251.4 | 5.9 | 708.8 | 683.9 | 672.4 | 706.9 | 550.3 | 401.9 | 483 | 484.3 | 403.4 | 431.3 | 72.3 | 125.4 | 164.2 | 140 | 246.4 | 237.1 | 129.4 | 206 | 223.8 | 179.4
1440.3 | 1221.3 | 466.6 | 186.64 | 218.1714 | 244.9 | 217.4 | 237.9 | 241.3 | 363.1 | 38.1 | 20.5 | 73.3 | 7.1 | 255 | 6.4 | 712.5 | 700.3 | 682.9 | 711 | 552.5 | 402.2 | 486.6 | 487.5 | 405 | 432.6 | 72.4 | 125.5 | 164.4 | 140.1 | 246.8 | 237.2 | 129.5 | 206.1 | 224 | 179.5
1441.3 | 1222.3 | 466.6 | 186.64 | 218.1714 | 244.8 | 217.4 | 238 | 241.5 | 373.7 | 38.1 | 20.5 | 73.2 | 7.5 | 241.4 | 6.5 | 719.7 | 716 | 698.9 | 720.8 | 555.9 | 402.5 | 505.2 | 506.8 | 412.8 | 437.9 | 72.5 | 125.6 | 164.6 | 140.2 | 247 | 238.1 | 129.6 | 206.2 | 224.2 | 179.7
1442.3 | 1223.3 | 466.8 | 186.72 | 218.2649 | 245.1 | 217.8 | 237.5 | 242.6 | 382.8 | 38.2 | 20.5 | 73.2 | 7.2 | 251 | 6.4 | 728 | 727 | 721.8 | 733.7 | 560.2 | 402.8 | 516.8 | 523.7 | 418 | 442.4 | 72.6 | 125.7 | 164.8 | 140.3 | 247.2 | 238.7 | 129.7 | 206.3 | 224.4 | 179.8
1443.3 | 1224.3 | 466.4 | 186.56 | 218.0779 | 245.6 | 218.3 | 237.5 | 242.3 | 393.5 | 38.2 | 20.5 | 73.2 | 7.1 | 244 | 6.2 | 733 | 714.1 | 732.6 | 742.5 | 563.9 | 403.2 | 526.9 | 519.3 | 423.7 | 448.2 | 72.6 | 125.8 | 165.1 | 140.4 | 247.5 | 239.5 | 129.8 | 206.5 | 224.6 | 180
1444.3 | 1225.3 | 463.2 | 185.28 | 216.5816 | 245.8 | 218.1 | 239 | 241.5 | 393.5 | 38.2 | 20.5 | 73.2 | 7.2 | 246.6 | 6.1 | 738.4 | 717.1 | 747.4 | 751.8 | 570.8 | 403.6 | 538.9 | 519.8 | 431.4 | 454.8 | 72.7 | 125.9 | 165.4 | 140.5 | 247.9 | 240.3 | 129.9 | 206.7 | 224.8 | 180.1
1445.3 | 1226.3 | 462.9 | 185.16 | 216.4414 | 245.9 | 218 | 239.4 | 242.8 | 400.5 | 38.2 | 20.5 | 73.2 | 7.2 | 241.6 | 6.1 | 744.1 | 731.1 | 747.7 | 760.6 | 574 | 403.9 | 557.6 | 528.3 | 438.7 | 458.9 | 72.8 | 126 | 165.6 | 140.7 | 248.9 | 240.9 | 130 | 207 | 225.1 | 180.3
1446.3 | 1227.3 | 463.1 | 185.24 | 216.5349 | 245.9 | 218.4 | 239.6 | 244.8 | 407.5 | 38.2 | 20.5 | 73.2 | 7.2 | 240.5 | 6.1 | 747 | 734.4 | 749.5 | 765.7 | 575.6 | 404.2 | 555.7 | 525.4 | 438.6 | 458.2 | 72.9 | 126.1 | 165.8 | 140.8 | 249.7 | 241.5 | 130.1 | 207.2 | 225.4 | 180.5
1447.3 | 1228.3 | 462.6 | 185.04 | 216.3011 | 245.8 | 219.7 | 240.7 | 245.3 | 407.1 | 38.2 | 20.5 | 73.2 | 7.2 | 250.7 | 6.3 | 749.4 | 732.3 | 749.3 | 767.7 | 577.1 | 404.6 | 557.7 | 527.9 | 439.6 | 459.7 | 73 | 126.2 | 165.9 | 140.9 | 250.1 | 241.6 | 130.2 | 207.4 | 225.5 | 180.6
1448.3 | 1229.3 | 462.1 | 184.84 | 216.0673 | 245 | 221 | 241.9 | 245.1 | 407.2 | 38.2 | 20.5 | 73.1 | 7 | 247 | 6.6 | 749.6 | 717.5 | 731.9 | 767.2 | 575.5 | 405 | 555.8 | 516.5 | 440.2 | 459.6 | 73.1 | 126.3 | 165.9 | 141 | 250.3 | 241.9 | 130.3 | 207.5 | 225.7 | 180.8
1449.3 | 1230.3 | 463.8 | 185.52 | 216.8622 | 245.4 | 222.2 | 242 | 244.1 | 398.3 | 38.2 | 20.5 | 73.2 | 7.3 | 247.5 | 6.7 | 748.6 | 702.4 | 717.3 | 766.9 | 574.6 | 405.3 | 548.7 | 506.9 | 438.5 | 459.2 | 73.1 | 126.4 | 166 | 141.1 | 250.6 | 242.5 | 130.4 | 207.8 | 225.9 | 180.9
1450.3 | 1231.3 | 464.9 | 185.96 | 217.3765 | 246.8 | 222.9 | 242.1 | 243.9 | 391 | 38.1 | 20.5 | 73.3 | 7 | 249.5 | 6.9 | 745.9 | 679.6 | 706.4 | 763.2 | 573.3 | 405.7 | 539.9 | 493.7 | 436.3 | 458.2 | 73.2 | 126.5 | 166.1 | 141.3 | 250.9 | 242.6 | 130.5 | 208 | 226 | 181.1
1451.3 | 1232.3 | 465.6 | 186.24 | 217.7038 | 247 | 222.9 | 243 | 244.8 | 387.9 | 38.2 | 20.5 | 73.4 | 6.7 | 252.1 | 6.9 | 744.3 | 672.1 | 699.7 | 761.7 | 572.3 | 406.1 | 531 | 485.2 | 434.5 | 457.1 | 73.3 | 126.6 | 166.4 | 141.4 | 251 | 242.8 | 130.6 | 208.2 | 226.2 | 181.2
1452.3 | 1233.3 | 465.8 | 186.32 | 217.7973 | 247 | 223 | 243.5 | 245.1 | 388.7 | 38.2 | 20.4 | 73.5 | 7.4 | 248.6 | 7.2 | 747.7 | 678.7 | 713.8 | 762.4 | 575.2 | 406.4 | 533 | 489.5 | 435.6 | 458.6 | 73.4 | 126.7 | 166.5 | 141.5 | 251.2 | 242.7 | 130.7 | 208.3 | 226.3 | 181.4
1453.3 | 1234.3 | 465.6 | 186.24 | 217.7038 | 247.1 | 223.1 | 242.6 | 245 | 394.5 | 38.2 | 20.4 | 73.6 | 7.5 | 262.5 | 7.7 | 749.1 | 673.8 | 713.7 | 761.5 | 575.2 | 406.7 | 530.6 | 487.3 | 436.1 | 459.8 | 73.5 | 126.8 | 166.6 | 141.6 | 251.3 | 243.2 | 130.8 | 208.4 | 226.4 | 181.5
1454.3 | 1235.3 | 465.8 | 186.32 | 217.7973 | 247.8 | 223.4 | 242.4 | 244.4 | 390.5 | 38.2 | 20.4 | 73.7 | 8.2 | 266.9 | 7.2 | 748.4 | 673.9 | 707.6 | 758.6 | 574.3 | 407 | 524.1 | 482.4 | 434.8 | 459.1 | 73.6 | 126.9 | 166.7 | 141.8 | 252 | 244.1 | 130.9 | 208.5 | 226.6 | 181.6
1455.3 | 1236.3 | 466.1 | 186.44 | 217.9376 | 249 | 223.6 | 242 | 245.4 | 389.2 | 38.2 | 20.4 | 73.7 | 8.5 | 265.6 | 7.2 | 747.2 | 658.6 | 694.4 | 755 | 572.9 | 407.3 | 519.1 | 483.4 | 434.1 | 459.5 | 73.6 | 127.1 | 166.8 | 141.9 | 252.9 | 244.7 | 131 | 208.7 | 226.7 | 181.8
1456.3 | 1237.3 | 465.2 | 186.08 | 217.5168 | 252.1 | 224 | 241.5 | 246.8 | 385 | 38.2 | 20.4 | 73.8 | 8.3 | 262.2 | 6.9 | 745 | 654.2 | 690.3 | 751.1 | 571.1 | 407.7 | 510.6 | 478 | 431.3 | 457.5 | 73.7 | 127.2 | 167 | 142 | 253.2 | 245.8 | 131.1 | 209 | 226.9 | 182
1457.3 | 1238.3 | 465.1 | 186.04 | 217.47 | 253.1 | 224.4 | 241.4 | 247.5 | 380.4 | 38.2 | 20.4 | 74 | 7.2 | 271.7 | 6.5 | 742.6 | 652.9 | 681.3 | 746.4 | 569.9 | 408.2 | 509.9 | 475.1 | 430.7 | 456.9 | 73.8 | 127.3 | 167.3 | 142.1 | 253.2 | 246.6 | 131.2 | 209.2 | 227 | 182.1
1458.3 | 1239.3 | 465.2 | 186.08 | 217.5168 | 253 | 224 | 241.2 | 247 | 377 | 38.2 | 20.4 | 74.1 | 7.9 | 258.3 | 7.2 | 741.5 | 652.2 | 681.6 | 745.7 | 569.4 | 408.5 | 509.2 | 470 | 429.7 | 456.3 | 73.9 | 127.4 | 167.5 | 142.3 | 253.4 | 246.4 | 131.3 | 209.4 | 227.1 | 182.2
1459.3 | 1240.3 | 465.4 | 186.16 | 217.6103 | 252.3 | 223.7 | 241.5 | 245.9 | 376.4 | 38.4 | 20.4 | 74.1 | 8 | 267.1 | 8 | 742.9 | 668.6 | 674.9 | 746.7 | 569.7 | 408.9 | 507 | 471 | 428.8 | 456.6 | 74 | 127.6 | 167.7 | 142.4 | 254.1 | 246.3 | 131.4 | 209.7 | 227.3 | 182.4
1460.3 | 1241.3 | 465.7 | 186.28 | 217.7506 | 251.3 | 223.9 | 241.5 | 246.4 | 376.2 | 38.5 | 20.4 | 74.1 | 8.9 | 261.2 | 9.2 | 743.2 | 668.3 | 665.8 | 744.7 | 569 | 409.4 | 502 | 468.1 | 427.1 | 455.7 | 74.1 | 127.7 | 167.7 | 142.5 | 254.3 | 245.9 | 131.5 | 209.8 | 227.4 | 182.6
1461.3 | 1242.3 | 465.6 | 186.24 | 217.7038 | 251.8 | 224 | 241.8 | 246.4 | 374.8 | 38.5 | 20.4 | 74.2 | 9 | 269.9 | 9.5 | 740.2 | 659.7 | 654 | 739 | 567.2 | 409.7 | 501.8 | 461.9 | 427.5 | 454.7 | 74.1 | 127.9 | 167.8 | 142.7 | 254.4 | 245.5 | 131.5 | 209.9 | 227.6 | 182.7
1462.3 | 1243.3 | 465.8 | 186.32 | 217.7973 | 253.1 | 222.9 | 241.6 | 246.5 | 371.5 | 38.6 | 20.4 | 74.2 | 7.8 | 269.1 | 8.9 | 738.4 | 663.8 | 649.4 | 735.9 | 565.8 | 410.1 | 501.7 | 458.2 | 429 | 453.9 | 74.2 | 128 | 167.9 | 142.8 | 254.5 | 245.5 | 131.7 | 210.1 | 227.7 | 182.8
1463.3 | 1244.3 | 465.7 | 186.28 | 217.7506 | 254 | 221.4 | 241.4 | 246.8 | 369.6 | 38.6 | 20.4 | 74.2 | 8.4 | 266.1 | 9.3 | 738.1 | 649 | 636.1 | 736.6 | 564 | 410.4 | 500.5 | 455 | 428.1 | 454.4 | 74.3 | 128.2 | 168.1 | 142.9 | 254.4 | 245.9 | 131.8 | 210.3 | 227.8 | 183
1464.3 | 1245.3 | 465.7 | 186.28 | 217.7506 | 254.1 | 220.6 | 241.6 | 248 | 367.2 | 38.7 | 20.4 | 74.3 | 8.3 | 261 | 9.1 | 733.9 | 635.2 | 630.5 | 732.3 | 563 | 410.7 | 495.8 | 444.4 | 425.9 | 452.4 | 74.4 | 128.3 | 168.1 | 143.1 | 254.2 | 246.1 | 131.9 | 210.4 | 228 | 183.1
1465.3 | 1246.3 | 467.2 | 186.88 | 218.452 | 254.5 | 220.4 | 241.6 | 247.5 | 363.9 | 38.6 | 20.4 | 74.4 | 8.1 | 266.4 | 8.4 | 730.1 | 620.4 | 616.5 | 726.2 | 561.5 | 411.1 | 497.9 | 436.5 | 427.1 | 450.5 | 74.5 | 128.5 | 168.2 | 143.2 | 254.2 | 246.1 | 132 | 210.6 | 228.1 | 183.3
1466.3 | 1247.3 | 467.7 | 187.08 | 218.6857 | 254.5 | 220.2 | 242.4 | 247.3 | 363.2 | 38.6 | 20.4 | 74.5 | 8 | 264 | 8 | 727.3 | 615.4 | 609 | 721.3 | 560.4 | 411.5 | 500.1 | 431 | 426 | 449 | 74.6 | 128.7 | 168.5 | 143.3 | 254.1 | 245.9 | 132.1 | 210.7 | 228.2 | 183.4
1467.3 | 1248.3 | 467.6 | 187.04 | 218.639 | 254.4 | 220.1 | 243.4 | 247.9 | 361.8 | 38.6 | 20.4 | 74.6 | 7.7 | 264.8 | 8.2 | 723.5 | 601.4 | 603.7 | 715.3 | 560.2 | 411.9 | 496 | 427 | 424.7 | 448.9 | 74.7 | 128.8 | 168.7 | 143.5 | 254 | 245.7 | 132.2 | 210.9 | 228.3 | 183.5
1468.3 | 1249.3 | 467.1 | 186.84 | 218.4052 | 254.3 | 220.1 | 244.2 | 248.1 | 358 | 38.6 | 20.4 | 74.7 | 7.6 | 272.6 | 8.7 | 720.2 | 597.1 | 618.5 | 712 | 560 | 412.4 | 491.3 | 420.9 | 423.9 | 448.6 | 74.7 | 129 | 168.9 | 143.6 | 254 | 246 | 132.2 | 211.1 | 228.4 | 183.7
1469.3 | 1250.3 | 466.7 | 186.68 | 218.2182 | 254.3 | 221.8 | 244.2 | 248.8 | 355.5 | 38.6 | 20.4 | 74.8 | 7.8 | 261.1 | 8.9 | 718.6 | 614.6 | 630.7 | 709.2 | 561.6 | 413 | 495.7 | 429.4 | 425.9 | 449.2 | 74.8 | 129.1 | 168.9 | 143.7 | 254.3 | 246 | 132.4 | 211.3 | 228.5 | 183.9
1470.3 | 1251.3 | 465.5 | 186.2 | 217.6571 | 254.1 | 222.2 | 243.8 | 248.8 | 363.1 | 38.7 | 20.4 | 74.9 | 7.4 | 277.5 | 8.5 | 722.8 | 627.3 | 632.9 | 714 | 562.9 | 413.6 | 501.1 | 438.4 | 427.7 | 451 | 74.9 | 129.3 | 169.1 | 143.8 | 254.6 | 246.3 | 132.5 | 211.3 | 228.6 | 184
1471.3 | 1252.3 | 465.4 | 186.16 | 217.6103 | 254.7 | 222.6 | 244 | 248.3 | 370 | 38.7 | 20.4 | 74.9 | 6.8 | 277.7 | 8.3 | 726.5 | 635.6 | 639.8 | 716.7 | 564.5 | 414 | 505.2 | 443.3 | 428.8 | 451.9 | 75 | 129.5 | 169.2 | 144 | 255 | 246.8 | 132.6 | 211.4 | 228.8 | 184.2
1472.3 | 1253.3 | 465.4 | 186.16 | 217.6103 | 254.9 | 223.5 | 244.9 | 248.6 | 375.5 | 38.8 | 20.4 | 75 | 6.8 | 272.4 | 8.2 | 732.5 | 669.2 | 660.8 | 725.2 | 568.1 | 414.5 | 513.7 | 464.7 | 431.9 | 455.2 | 75.1 | 129.6 | 169.4 | 144.1 | 256.3 | 246.9 | 132.7 | 211.6 | 229 | 184.4
1473.3 | 1254.3 | 465.7 | 186.28 | 217.7506 | 254.3 | 223.8 | 245.5 | 248.8 | 384.5 | 38.8 | 20.4 | 75.2 | 7.5 | 274.5 | 8 | 740.6 | 684.9 | 671.8 | 738.2 | 570.5 | 414.9 | 530.8 | 485.4 | 442.2 | 461.9 | 75.2 | 129.7 | 169.8 | 144.3 | 257.1 | 246.7 | 132.8 | 211.7 | 229.2 | 184.6
1474.3 | 1255.3 | 465.5 | 186.2 | 217.6571 | 254.1 | 223.2 | 247.1 | 249.2 | 391.4 | 38.9 | 20.4 | 75.1 | 6.8 | 273.3 | 7.7 | 746.9 | 707.3 | 671.9 | 743.7 | 571.2 | 415.4 | 540.6 | 516.1 | 444.4 | 462 | 75.3 | 129.9 | 170.1 | 144.4 | 257.5 | 246.6 | 132.9 | 211.8 | 229.4 | 184.8
1475.3 | 1256.3 | 465.4 | 186.16 | 217.6103 | 253.5 | 222.8 | 248.3 | 250.4 | 400.8 | 38.9 | 20.4 | 75 | 6.5 | 275 | 7.4 | 748 | 716.5 | 660.6 | 742.1 | 570.5 | 415.9 | 545.3 | 517.8 | 445.7 | 461.9 | 75.3 | 130 | 170.3 | 144.6 | 258.3 | 246.5 | 133 | 211.8 | 229.6 | 185
1476.3 | 1257.3 | 465.7 | 186.28 | 217.7506 | 254.3 | 222.9 | 248.7 | 251.6 | 404.3 | 39 | 20.4 | 74.8 | 6.6 | 274.5 | 7.2 | 749.2 | 731.3 | 673.8 | 743.2 | 570 | 416.4 | 550.9 | 523.6 | 445.4 | 461.9 | 75.4 | 130.2 | 170.3 | 144.7 | 258.7 | 246.3 | 133.1 | 211.9 | 229.8 | 185.2
1477.3 | 1258.3 | 465.7 | 186.28 | 217.7506 | 254.7 | 223.4 | 250 | 252.1 | 407.7 | 39.1 | 20.4 | 74.7 | 7 | 273.4 | 6.8 | 754 | 753.1 | 710.3 | 749.1 | 578.7 | 416.9 | 567.1 | 544.5 | 453.7 | 469.5 | 75.5 | 130.3 | 170.6 | 144.8 | 259 | 246.4 | 133.2 | 212.1 | 230 | 185.3
1478.3 | 1259.3 | 467.5 | 187 | 218.5922 | 254.2 | 223.1 | 250.2 | 252.1 | 415.9 | 39.1 | 20.4 | 74.5 | 6.8 | 273.6 | 6.5 | 757.2 | 754 | 718.4 | 752.4 | 581.1 | 417.4 | 579.6 | 546.8 | 458 | 471.4 | 75.6 | 130.5 | 170.6 | 145 | 259.4 | 246.5 | 133.4 | 212.3 | 230.2 | 185.5
1479.3 | 1260.3 | 467.5 | 187 | 218.5922 | 253.4 | 224 | 250.1 | 252.6 | 420.1 | 39.2 | 20.4 | 74.4 | 6.5 | 268.1 | 6.3 | 760.4 | 754.4 | 730.4 | 757.6 | 584 | 417.9 | 582.1 | 545.6 | 459.5 | 472.7 | 75.7 | 130.6 | 170.7 | 145.1 | 260.2 | 246.6 | 133.4 | 212.5 | 230.5 | 185.7
1480.3 | 1261.3 | 466.7 | 186.68 | 218.2182 | 252.7 | 224.9 | 250.3 | 253.3 | 421.3 | 39.2 | 20.4 | 74.5 | 6.9 | 268.2 | 6.5 | 762.3 | 741.3 | 714.1 | 761.4 | 583.8 | 418.3 | 587.9 | 539.7 | 461.8 | 474.3 | 75.8 | 130.7 | 170.9 | 145.3 | 261.2 | 246.9 | 133.5 | 212.7 | 230.7 | 185.8
1481.3 | 1262.3 | 466.3 | 186.52 | 218.0311 | 253.2 | 225.8 | 249.6 | 253.8 | 416.1 | 39.2 | 20.4 | 74.5 | 6.7 | 267.8 | 6.6 | 761.8 | 733 | 696.7 | 761.9 | 582.6 | 418.7 | 598.2 | 531.8 | 462.2 | 473.8 | 75.9 | 130.8 | 171.1 | 145.4 | 260.9 | 247.1 | 133.6 | 213 | 230.9 | 186
1482.3 | 1263.3 | 467.2 | 186.88 | 218.452 | 253.9 | 226.3 | 248.9 | 253.6 | 413.5 | 39.2 | 20.4 | 74.5 | 7 | 268 | 6.7 | 759.9 | 726 | 683.6 | 760.1 | 581.1 | 419.2 | 594.4 | 529.5 | 461 | 472.2 | 76 | 131 | 171.3 | 145.5 | 260.6 | 247.8 | 133.7 | 213.1 | 231.1 | 186.2
1483.3 | 1264.3 | 467.5 | 187 | 218.5922 | 254.4 | 226.2 | 248.5 | 253.4 | 410.3 | 39.3 | 20.4 | 74.5 | 6.6 | 262.4 | 6.4 | 758.6 | 715.4 | 676.2 | 755.3 | 580.8 | 419.7 | 595.5 | 518.2 | 460 | 471.3 | 76 | 131.1 | 171.4 | 145.7 | 260.5 | 247.9 | 133.8 | 213.3 | 231.3 | 186.3
1484.3 | 1265.3 | 467.3 | 186.92 | 218.4987 | 254.8 | 225.3 | 249.5 | 252.9 | 408.5 | 39.3 | 20.4 | 74.5 | 7.1 | 257.5 | 5.7 | 755.5 | 714.6 | 665.1 | 748.2 | 578.7 | 420.2 | 599.6 | 516.3 | 459 | 469.9 | 76.1 | 131.2 | 171.8 | 145.8 | 260.2 | 249.1 | 133.9 | 213.5 | 231.4 | 186.4
1485.3 | 1266.3 | 467.4 | 186.96 | 218.5455 | 255.7 | 224.7 | 249.8 | 251.3 | 413.1 | 39.4 | 20.4 | 74.5 | 6.5 | 274.6 | 5.6 | 755 | 726 | 671.7 | 745.1 | 579.4 | 420.7 | 611.3 | 524.7 | 461.5 | 470.7 | 76.2 | 131.3 | 171.9 | 145.9 | 260 | 249.3 | 134 | 213.6 | 231.5 | 186.6
1486.3 | 1267.3 | 467 | 186.8 | 218.3584 | 256.1 | 224.4 | 250.3 | 250.5 | 423.1 | 39.6 | 20.4 | 74.6 | 6.9 | 273.9 | 5.6 | 756 | 728.4 | 680.8 | 744 | 582.2 | 421.2 | 613.5 | 527.8 | 462.6 | 471.9 | 76.3 | 131.4 | 171.9 | 146.1 | 259.8 | 249.6 | 134.1 | 213.7 | 231.7 | 186.7
1487.3 | 1268.3 | 465.2 | 186.08 | 217.5168 | 255.9 | 224.2 | 250.5 | 250.9 | 432 | 39.6 | 20.4 | 74.7 | 7.5 | 263.1 | 5.6 | 756.8 | 729.2 | 692.6 | 742.5 | 582.9 | 421.9 | 622.7 | 534.5 | 465.3 | 473.7 | 76.4 | 131.5 | 172 | 146.2 | 260.2 | 249.5 | 134.3 | 213.9 | 231.9 | 186.9
1488.3 | 1269.3 | 465.2 | 186.08 | 217.5168 | 256.1 | 224.4 | 250.2 | 251.4 | 447.8 | 39.6 | 20.4 | 74.9 | 7.5 | 264.5 | 6 | 757.7 | 739.4 | 701.7 | 740.1 | 585 | 422.4 | 631.6 | 546.1 | 467.9 | 473.8 | 76.5 | 131.6 | 172.2 | 146.4 | 260.6 | 249.1 | 134.4 | 214 | 232.1 | 187.1
1489.3 | 1270.3 | 465.2 | 186.08 | 217.5168 | 256.1 | 225.2 | 248.7 | 251.5 | 461.5 | 39.6 | 20.4 | 75 | 7.8 | 259.2 | 7.3 | 759.4 | 752.2 | 707.8 | 741.1 | 586 | 422.9 | 641.9 | 569.8 | 472.2 | 475.3 | 76.6 | 131.6 | 172.5 | 146.5 | 260.6 | 248.8 | 134.5 | 214.1 | 232.3 | 187.3
1490.3 | 1271.3 | 464.6 | 185.84 | 217.2363 | 255.9 | 226.2 | 248.1 | 251.8 | 479.8 | 39.6 | 20.4 | 75.2 | 8 | 268.6 | 8.2 | 761.7 | 762.9 | 722.7 | 744.9 | 588.1 | 423.4 | 651.7 | 581.9 | 476.8 | 477.3 | 76.7 | 131.7 | 172.9 | 146.6 | 261.4 | 249 | 134.6 | 214.3 | 232.6 | 187.4
1491.3 | 1272.3 | 468.2 | 187.28 | 218.9195 | 255.5 | 227.6 | 249.2 | 252 | 502.1 | 39.5 | 20.4 | 75.3 | 8.3 | 261.3 | 8.7 | 765.4 | 768.6 | 728.1 | 750.3 | 589.5 | 424 | 661.2 | 593.2 | 482.7 | 479.3 | 76.8 | 131.9 | 173.4 | 146.8 | 261.5 | 248.9 | 134.7 | 214.5 | 232.9 | 187.6
1492.3 | 1273.3 | 470 | 188 | 219.7612 | 255.3 | 228.7 | 250.5 | 252.5 | 513.9 | 39.5 | 20.4 | 75.4 | 8.3 | 265.7 | 9.5 | 772.1 | 772.8 | 748.7 | 761.2 | 594.3 | 424.5 | 668.9 | 598 | 488.1 | 484.8 | 76.9 | 132 | 173.6 | 146.9 | 261.7 | 248.8 | 134.8 | 214.6 | 233.1 | 187.8
1493.3 | 1274.3 | 469.3 | 187.72 | 219.4339 | 254.9 | 229.3 | 252.1 | 253.4 | 525.7 | 39.4 | 20.4 | 75.4 | 8 | 263.5 | 10.6 | 779.2 | 784.1 | 764.2 | 769.8 | 597.6 | 425.1 | 678.4 | 611.2 | 495.5 | 490.6 | 77 | 132.1 | 173.7 | 147 | 261.9 | 248.7 | 134.9 | 214.8 | 233.4 | 188
1494.3 | 1275.3 | 469 | 187.6 | 219.2936 | 254.9 | 229 | 252.9 | 254.3 | 542.7 | 39.4 | 20.4 | 75.3 | 8.3 | 264.8 | 12.3 | 781.8 | 776.8 | 762.9 | 772.6 | 598.6 | 425.7 | 679.7 | 605.1 | 498.7 | 492.4 | 77.1 | 132.2 | 173.9 | 147.2 | 262.4 | 248.8 | 135 | 214.9 | 233.8 | 188.1
1495.3 | 1276.3 | 468.4 | 187.36 | 219.013 | 254.7 | 228.2 | 253.2 | 255.5 | 552.6 | 39.4 | 20.4 | 75.3 | 7.9 | 266 | 12.3 | 785.1 | 792.8 | 771 | 778.3 | 600.1 | 426.4 | 688.1 | 616.5 | 500.7 | 493.3 | 77.2 | 132.4 | 174.1 | 147.3 | 262.5 | 248.8 | 135.1 | 215.1 | 234.1 | 188.3
1496.3 | 1277.3 | 466.8 | 186.72 | 218.2649 | 254.6 | 227.9 | 253.8 | 256.2 | 561.9 | 39.3 | 20.4 | 75.3 | 7.7 | 269 | 11 | 784.7 | 794.8 | 767.9 | 776.3 | 603.8 | 427.1 | 700.6 | 631.7 | 512.2 | 495.2 | 77.3 | 132.5 | 174.5 | 147.4 | 262.8 | 248.7 | 135.2 | 215.3 | 234.3 | 188.4
1497.3 | 1278.3 | 466.2 | 186.48 | 217.9844 | 255.1 | 228.6 | 255 | 256.7 | 570.7 | 39.3 | 20.4 | 75.3 | 7 | 265.7 | 9.9 | 784.5 | 791.9 | 770.2 | 773.1 | 606.2 | 427.8 | 708.6 | 630.5 | 522.4 | 497.3 | 77.4 | 132.7 | 174.6 | 147.6 | 263.4 | 248.8 | 135.3 | 215.4 | 234.7 | 188.6
1498.3 | 1279.3 | 467 | 186.8 | 218.3584 | 255.5 | 231 | 256.5 | 257.4 | 566 | 39.4 | 20.4 | 75.3 | 6.4 | 270 | 8.7 | 785.2 | 773.2 | 761.9 | 774.1 | 605.4 | 428.4 | 719.1 | 619 | 526.9 | 498.1 | 77.5 | 132.8 | 174.7 | 147.7 | 263.8 | 249.1 | 135.4 | 215.5 | 235 | 188.8
1499.3 | 1280.3 | 464.8 | 185.92 | 217.3298 | 255.8 | 232.4 | 256.6 | 256.7 | 564.3 | 39.6 | 20.4 | 75.3 | 6.4 | 276.3 | 7.6 | 781.3 | 747.7 | 732.4 | 768.8 | 602.6 | 428.9 | 730.9 | 596.2 | 532.7 | 495.8 | 77.6 | 133 | 175 | 147.8 | 263.6 | 250.3 | 135.6 | 215.7 | 235.2 | 188.9
1500.3 | 1281.3 | 465.7 | 186.28 | 217.7506 | 256.6 | 233.1 | 256.8 | 256.7 | 542.8 | 39.7 | 20.4 | 75.2 | 6.9 | 277.4 | 7.1 | 776.6 | 726.3 | 708.4 | 763.8 | 599.4 | 429.5 | 740.1 | 579.3 | 547.6 | 494 | 77.7 | 133.1 | 175.3 | 147.9 | 263.9 | 250.7 | 135.6 | 216 | 235.4 | 189.1
1501.3 | 1282.3 | 467.3 | 186.92 | 218.4987 | 257.2 | 232.1 | 256.9 | 257 | 521.4 | 39.9 | 20.4 | 75.3 | 7.6 | 272.2 | 6.4 | 778.7 | 734.4 | 714.1 | 766.3 | 599.9 | 430.3 | 751.7 | 577.8 | 560 | 494 | 77.8 | 133.3 | 175.4 | 148 | 263.6 | 250.5 | 135.8 | 216.2 | 235.6 | 189.2
1502.3 | 1283.3 | 467.8 | 187.12 | 218.7325 | 257.2 | 232.1 | 256.2 | 256.1 | 536.1 | 40 | 20.4 | 75.3 | 6.5 | 270.9 | 5.6 | 783 | 761.7 | 736 | 770.3 | 606 | 431.3 | 761.8 | 615.9 | 569.4 | 497.5 | 77.9 | 133.4 | 175.7 | 148.1 | 263.8 | 251 | 135.9 | 216.3 | 235.8 | 189.4
1503.3 | 1284.3 | 467.7 | 187.08 | 218.6857 | 258.1 | 233.7 | 255.5 | 254.3 | 545.6 | 40.1 | 20.4 | 75.3 | 7.1 | 242 | 5.2 | 786.8 | 776.1 | 749.4 | 775.2 | 612.9 | 431.9 | 761.8 | 627.9 | 571.3 | 503.5 | 78 | 133.6 | 175.8 | 148.2 | 264.2 | 250.8 | 136 | 216.4 | 236 | 189.5
1504.3 | 1285.3 | 468 | 187.2 | 218.826 | 257.3 | 233.7 | 255.4 | 253.2 | 549 | 40 | 20.4 | 75.5 | 7.5 | 246.6 | 5.2 | 789.8 | 785.7 | 760.8 | 779.4 | 616.9 | 432.5 | 764.6 | 644.9 | 575.6 | 508.1 | 78.1 | 133.7 | 176.1 | 148.3 | 264.5 | 251 | 136.1 | 216.6 | 236.4 | 189.7
1505.3 | 1286.3 | 468.4 | 187.36 | 219.013 | 257.3 | 234.1 | 256.1 | 254.1 | 541.5 | 39.9 | 20.4 | 75.6 | 7.5 | 266.3 | 5.3 | 788 | 772.5 | 758.9 | 775.8 | 618.1 | 433.1 | 770.4 | 621.8 | 579.2 | 509.1 | 78.2 | 133.8 | 176.4 | 148.4 | 264.3 | 251.1 | 136.2 | 216.9 | 236.8 | 189.9
1506.3 | 1287.3 | 465.9 | 186.36 | 217.8441 | 257.1 | 233.7 | 257.5 | 254.6 | 524.1 | 39.9 | 20.4 | 75.8 | 7.6 | 251.4 | 7.1 | 789.4 | 777.3 | 771.1 | 780.8 | 621.9 | 433.8 | 779.7 | 617.7 | 585.6 | 510 | 78.3 | 134 | 176.4 | 148.5 | 264.3 | 251.2 | 136.3 | 217.1 | 237.1 | 190.1
1507.3 | 1288.3 | 466.8 | 186.72 | 218.2649 | 256.7 | 234.7 | 258.1 | 255.2 | 530.4 | 39.9 | 20.3 | 75.8 | 7.9 | 251.5 | 8.3 | 792.9 | 791.7 | 781.9 | 786.2 | 627.7 | 434.4 | 782.9 | 638.5 | 589.5 | 514.6 | 78.4 | 134.1 | 176.6 | 148.7 | 265.1 | 251.2 | 136.5 | 217.3 | 237.4 | 190.2
1508.3 | 1289.3 | 465.9 | 186.36 | 217.8441 | 256.4 | 235.6 | 258.3 | 254.7 | 549.4 | 39.9 | 20.3 | 75.8 | 7.6 | 253 | 9.3 | 793.5 | 798.8 | 777 | 784 | 631.5 | 435 | 789.2 | 657.3 | 591.4 | 515.6 | 78.5 | 134.3 | 176.9 | 148.8 | 265.5 | 251.1 | 136.6 | 217.5 | 237.7 | 190.4
1509.3 | 1290.3 | 466.6 | 186.64 | 218.1714 | 256.4 | 234.7 | 257.6 | 252.4 | 573.5 | 39.9 | 20.3 | 75.8 | 8.1 | 259.9 | 9.9 | 798.4 | 812.7 | 778.7 | 786.2 | 634.7 | 435.7 | 793.1 | 680.9 | 593.8 | 517.5 | 78.6 | 134.5 | 177.2 | 148.9 | 265.5 | 251.1 | 136.7 | 217.6 | 238.1 | 190.5
1510.3 | 1291.3 | 467.9 | 187.16 | 218.7793 | 256.1 | 234.1 | 257.5 | 251.1 | 579.5 | 39.9 | 20.4 | 75.8 | 8 | 271.4 | 10.3 | 805 | 833.2 | 773.5 | 794.4 | 637.2 | 436.5 | 794 | 699.4 | 598.4 | 525.4 | 78.7 | 134.6 | 177.6 | 149 | 265.2 | 251.4 | 136.8 | 217.7 | 238.4 | 190.7
1511.3 | 1292.3 | 468 | 187.2 | 218.826 | 256.8 | 233.9 | 258.2 | 252 | 574.6 | 39.9 | 20.3 | 75.8 | 7.8 | 281.4 | 10 | 809.7 | 817.4 | 759.9 | 801.6 | 635.2 | 437.2 | 792.5 | 685.9 | 601.8 | 529.5 | 78.8 | 134.8 | 177.7 | 149.1 | 265.4 | 251.3 | 136.9 | 217.8 | 238.8 | 190.9
1512.3 | 1293.3 | 467.5 | 187 | 218.5922 | 257.7 | 234.6 | 258.1 | 253.9 | 568.7 | 39.9 | 20.4 | 75.8 | 8.8 | 277.1 | 9 | 810.4 | 802.7 | 750.9 | 801.3 | 634.3 | 437.8 | 802.3 | 663.3 | 605.9 | 529.5 | 78.9 | 135 | 177.9 | 149.3 | 266.2 | 251.1 | 137 | 217.9 | 239.2 | 191.1
1513.3 | 1294.3 | 468 | 187.2 | 218.826 | 257.2 | 235.4 | 256.6 | 256.7 | 556.9 | 39.8 | 20.3 | 75.8 | 8.6 | 290 | 8.9 | 811.4 | 782 | 738.5 | 802.6 | 633.6 | 438.4 | 804.2 | 646.3 | 610.4 | 529.9 | 78.9 | 135.1 | 178.2 | 149.4 | 266.1 | 251.4 | 137.2 | 218.1 | 239.5 | 191.3
1514.3 | 1295.3 | 466.2 | 186.48 | 217.9844 | 255.5 | 235.9 | 255.9 | 257.7 | 546.4 | 39.9 | 20.3 | 75.7 | 8.9 | 282.8 | 9.3 | 807.1 | 753.2 | 722.2 | 795.5 | 630.5 | 439 | 808.2 | 628.5 | 616.3 | 527.5 | 79 | 135.3 | 178.1 | 149.5 | 266.6 | 251.7 | 137.3 | 218.3 | 239.8 | 191.4
1515.3 | 1296.3 | 465.9 | 186.36 | 217.8441 | 254.6 | 235.5 | 256.3 | 257.9 | 530 | 40 | 20.3 | 75.6 | 9 | 276.8 | 10.1 | 801.6 | 726.3 | 718.7 | 788 | 627.5 | 439.7 | 813.3 | 604.2 | 616.5 | 525.1 | 79.1 | 135.5 | 178.3 | 149.6 | 266.2 | 252 | 137.4 | 218.7 | 240.1 | 191.6
1516.3 | 1297.3 | 465.6 | 186.24 | 217.7038 | 255.1 | 235.4 | 256.2 | 258.2 | 510 | 40.2 | 20.3 | 75.6 | 8.7 | 275.9 | 11.3 | 796.5 | 707.7 | 717.5 | 781.6 | 626.6 | 440.3 | 820.5 | 591 | 620.6 | 523.5 | 79.2 | 135.6 | 178.4 | 149.8 | 266.4 | 252 | 137.5 | 218.8 | 240.3 | 191.7
1517.3 | 1298.3 | 465.1 | 186.04 | 217.47 | 255.2 | 237 | 256.6 | 257.4 | 497.5 | 40.4 | 20.3 | 75.7 | 8.8 | 284.4 | 10.5 | 793 | 697.4 | 717.4 | 777.7 | 625.8 | 440.9 | 827.8 | 571 | 620.8 | 522 | 79.3 | 135.8 | 178.4 | 149.9 | 265.9 | 252 | 137.6 | 218.9 | 240.5 | 191.9
1518.3 | 1299.3 | 466.7 | 186.68 | 218.2182 | 254.9 | 236.9 | 257.2 | 255.6 | 487.6 | 40.5 | 20.3 | 75.8 | 9.5 | 275.5 | 10.7 | 786.8 | 681.2 | 689.1 | 770.8 | 622.4 | 441.6 | 831.2 | 552.2 | 621.1 | 519.5 | 79.4 | 135.9 | 178.6 | 150 | 265.8 | 252.1 | 137.7 | 219.1 | 240.7 | 192
1519.3 | 1300.3 | 467.6 | 187.04 | 218.639 | 255.6 | 235.3 | 256.8 | 255.3 | 472.7 | 40.5 | 20.3 | 76 | 8.9 | 284.1 | 12.8 | 781.6 | 663.4 | 674.4 | 766 | 619.4 | 442.3 | 832.8 | 540.1 | 621.7 | 517.1 | 79.5 | 136.1 | 178.7 | 150.1 | 265.4 | 252.5 | 137.8 | 219.2 | 240.9 | 192.2
1520.3 | 1301.3 | 467.5 | 187 | 218.5922 | 257 | 234.4 | 257.1 | 255 | 470.5 | 40.7 | 20.3 | 76.2 | 8 | 277.9 | 12.9 | 779.5 | 673.5 | 663.4 | 765.7 | 617.5 | 443 | 828.2 | 538.3 | 624 | 517.3 | 79.6 | 136.3 | 179 | 150.3 | 264.9 | 252.8 | 137.9 | 219.4 | 241.1 | 192.3
1521.3 | 1302.3 | 468.4 | 187.36 | 219.013 | 257.4 | 234.9 | 256.7 | 252.6 | 469 | 40.9 | 20.3 | 76.4 | 7.6 | 268.5 | 12 | 778.9 | 679.1 | 670.9 | 764.9 | 617.1 | 443.6 | 829.6 | 535 | 626 | 517.5 | 79.7 | 136.4 | 179.2 | 150.4 | 264.4 | 252.4 | 138 | 219.5 | 241.3 | 192.5
1522.3 | 1303.3 | 469.8 | 187.92 | 219.6677 | 258 | 235.2 | 254.6 | 250.5 | 477.5 | 41.1 | 20.3 | 76.5 | 6.5 | 264.8 | 11 | 782.9 | 711.4 | 698.2 | 769.6 | 621.4 | 444.3 | 824.7 | 552.5 | 625 | 520.7 | 79.8 | 136.6 | 179.2 | 150.5 | 264.6 | 252.2 | 138.2 | 219.6 | 241.5 | 192.6
1523.3 | 1304.3 | 471 | 188.4 | 220.2287 | 257.8 | 236 | 253 | 249.8 | 494.3 | 41.2 | 20.3 | 76.6 | 6.4 | 275.2 | 10.3 | 784.8 | 731.1 | 721.5 | 772 | 624.2 | 444.9 | 821.1 | 561.9 | 625 | 525.3 | 79.9 | 136.7 | 179.4 | 150.7 | 266.7 | 253.1 | 138.3 | 219.8 | 241.8 | 192.8
1524.3 | 1305.3 | 470.6 | 188.24 | 220.0417 | 256.9 | 235.4 | 252.4 | 251.3 | 500.9 | 41.3 | 20.3 | 76.7 | 6.7 | 270.8 | 9.3 | 786.7 | 744.4 | 740.1 | 775.9 | 626.4 | 445.5 | 818.3 | 566.9 | 622.9 | 527.5 | 80 | 136.8 | 179.7 | 150.8 | 266.8 | 253.9 | 138.4 | 220.1 | 242.1 | 193
1525.3 | 1306.3 | 468.3 | 187.32 | 218.9663 | 254.5 | 234.4 | 252.7 | 252.9 | 504 | 41.4 | 20.3 | 76.8 | 7.7 | 272.1 | 8.7 | 788 | 753.7 | 748.2 | 776.5 | 626.5 | 446.1 | 816.3 | 565.6 | 623.3 | 526.7 | 80.1 | 136.9 | 180 | 150.9 | 266.9 | 253.8 | 138.5 | 220.3 | 242.5 | 193.2
1526.3 | 1307.3 | 468.3 | 187.32 | 218.9663 | 253.7 | 233.4 | 253.9 | 253.9 | 500 | 41.5 | 20.3 | 76.9 | 7.8 | 264.3 | 8.3 | 789.4 | 747.3 | 736.7 | 778.1 | 626.4 | 446.8 | 820.7 | 564.7 | 627.5 | 527.1 | 80.2 | 137 | 180.1 | 151.1 | 266.7 | 253.5 | 138.6 | 220.3 | 242.8 | 193.4
1527.3 | 1308.3 | 468.2 | 187.28 | 218.9195 | 254.4 | 232.7 | 254.1 | 254 | 496.6 | 41.6 | 20.3 | 77 | 8.1 | 271.8 | 8.2 | 790.9 | 744.9 | 740.8 | 778.6 | 626.5 | 447.4 | 822.6 | 559.4 | 630.2 | 526.1 | 80.3 | 137.2 | 180.2 | 151.2 | 266.4 | 253.5 | 138.8 | 220.4 | 243 | 193.5
1528.3 | 1309.3 | 467.5 | 187 | 218.5922 | 255.6 | 232.3 | 255.1 | 254.3 | 493.1 | 41.6 | 20.3 | 77 | 7.4 | 261.2 | 7.8 | 794.2 | 753 | 738 | 781.2 | 627.9 | 448.1 | 824.5 | 571.5 | 630.5 | 528.6 | 80.4 | 137.3 | 180.3 | 151.4 | 266.2 | 253.2 | 138.9 | 220.4 | 243.3 | 193.7
1529.3 | 1310.3 | 466.7 | 186.68 | 218.2182 | 255.7 | 231.8 | 254.9 | 255 | 492.2 | 41.6 | 20.3 | 77 | 7.7 | 251.6 | 7.5 | 791.4 | 740.2 | 721.1 | 776.7 | 625.9 | 448.6 | 825.4 | 560 | 633 | 526.6 | 80.5 | 137.4 | 180.5 | 151.5 | 266.9 | 253 | 139 | 220.5 | 243.6 | 193.9
1530.3 | 1311.3 | 466.8 | 186.72 | 218.2649 | 256 | 231.7 | 255 | 255 | 487.7 | 41.6 | 20.3 | 77 | 7.4 | 264.6 | 7.3 | 788.7 | 744.7 | 717.1 | 770.3 | 624.3 | 449.2 | 828.4 | 558 | 634.4 | 524.6 | 80.6 | 137.5 | 180.7 | 151.6 | 266.8 | 252.9 | 139.1 | 220.6 | 243.9 | 194
1531.3 | 1312.3 | 466.4 | 186.56 | 218.0779 | 255.4 | 231.5 | 254.9 | 254.2 | 489.9 | 41.7 | 20.3 | 76.9 | 7.3 | 253.4 | 7.5 | 788.9 | 747.7 | 732.4 | 769.8 | 626.9 | 449.8 | 833.2 | 559.4 | 636.1 | 526.5 | 80.7 | 137.6 | 180.9 | 151.8 | 266.4 | 253 | 139.2 | 220.7 | 244.1 | 194.2
1532.3 | 1313.3 | 468.3 | 187.32 | 218.9663 | 254.6 | 231.4 | 255.3 | 252 | 489.5 | 41.7 | 20.3 | 76.8 | 8.3 | 257.7 | 7.4 | 790.4 | 747.6 | 740.2 | 773.5 | 629.3 | 450.4 | 836.5 | 553.4 | 641 | 526.4 | 80.8 | 137.7 | 181.2 | 151.9 | 266.2 | 253.1 | 139.3 | 220.8 | 244.3 | 194.3
1533.3 | 1314.3 | 468.1 | 187.24 | 218.8728 | 254.4 | 232.2 | 256.5 | 251.4 | 491.9 | 41.8 | 20.3 | 76.8 | 8.2 | 264.6 | 7.7 | 788.6 | 725.1 | 730.9 | 770 | 627 | 451 | 832.2 | 542.5 | 636.1 | 525.2 | 80.9 | 137.9 | 181.3 | 152 | 266.2 | 253.1 | 139.4 | 220.9 | 244.6 | 194.5
1534.3 | 1315.3 | 468.6 | 187.44 | 219.1066 | 255 | 232 | 256.4 | 252.1 | 479.4 | 41.8 | 20.3 | 76.8 | 8.1 | 263.3 | 7.4 | 785.2 | 714.8 | 714 | 766.3 | 624.9 | 451.5 | 834.7 | 533.7 | 640.1 | 522.5 | 81 | 138 | 181.4 | 152.2 | 266.8 | 253.1 | 139.6 | 221 | 244.9 | 194.6
1535.3 | 1316.3 | 466.9 | 186.76 | 218.3117 | 255.2 | 232.1 | 256.5 | 253.5 | 472.4 | 41.7 | 20.3 | 76.7 | 7.1 | 250.9 | 7.1 | 783.1 | 703.8 | 707.5 | 764.5 | 624.4 | 452.3 | 840.2 | 535.4 | 644.1 | 523.2 | 81.1 | 138.1 | 181.6 | 152.3 | 266.8 | 253 | 139.7 | 221.2 | 245 | 194.8
1536.3 | 1317.3 | 464.6 | 185.84 | 217.2363 | 255.4 | 231.9 | 256.3 | 253.1 | 476.5 | 41.6 | 20.3 | 76.8 | 7.1 | 255.4 | 7.4 | 783.1 | 706.1 | 698.8 | 765.1 | 623.4 | 452.9 | 838.2 | 536.6 | 643.8 | 524 | 81.2 | 138.2 | 181.7 | 152.4 | 267.1 | 253.3 | 139.8 | 221.2 | 245.2 | 195
1537.3 | 1318.3 | 464.9 | 185.96 | 217.3765 | 255.6 | 231.7 | 254.9 | 253.4 | 479.6 | 41.5 | 20.3 | 77 | 6.8 | 259.2 | 7.1 | 778.1 | 682.7 | 684.5 | 759.2 | 620.7 | 453.4 | 835.9 | 521.6 | 640.6 | 521.6 | 81.3 | 138.3 | 181.7 | 152.6 | 267 | 253.4 | 139.9 | 221.5 | 245.5 | 195.1
1538.3 | 1319.3 | 465.7 | 186.28 | 217.7506 | 256.1 | 231.7 | 255.3 | 253.4 | 464.8 | 41.4 | 20.3 | 77.2 | 7.1 | 239.2 | 6.3 | 773.3 | 660.3 | 667.9 | 754.6 | 619.1 | 453.9 | 844.4 | 509.9 | 640.7 | 520.5 | 81.4 | 138.5 | 181.8 | 152.7 | 266.7 | 253.2 | 140 | 221.6 | 245.7 | 195.3
1539.3 | 1320.3 | 464.8 | 185.92 | 217.3298 | 255.9 | 232.5 | 255.4 | 253.3 | 457.3 | 41.4 | 20.3 | 77.3 | 7 | 231.7 | 5.9 | 768.4 | 635.4 | 655.6 | 748.8 | 617.1 | 454.3 | 845.7 | 501.2 | 642 | 518.8 | 81.5 | 138.6 | 181.9 | 152.8 | 266.8 | 253.2 | 140.1 | 221.7 | 245.8 | 195.4
1540.3 | 1321.3 | 465.3 | 186.12 | 217.5636 | 257.6 | 233.2 | 255 | 253.5 | 449.2 | 41.4 | 20.3 | 77.4 | 6.4 | 233.9 | 5.6 | 765.4 | 628.3 | 656 | 743.5 | 615.2 | 454.8 | 837.5 | 495.4 | 646.9 | 516.4 | 81.6 | 138.7 | 182 | 152.9 | 266.5 | 253.2 | 140.3 | 221.8 | 246 | 195.6
1541.3 | 1322.3 | 466.7 | 186.68 | 218.2182 | 258.9 | 233 | 253.5 | 252.9 | 445.4 | 41.4 | 20.3 | 77.6 | 6.2 | 243.3 | 5.1 | 763.7 | 628.4 | 656.5 | 742.2 | 614.8 | 455.3 | 833.8 | 494.4 | 647.9 | 515.7 | 81.6 | 138.9 | 182.3 | 153.1 | 266.1 | 253.1 | 140.4 | 221.9 | 246.1 | 195.7
1542.3 | 1323.3 | 467 | 186.8 | 218.3584 | 258.8 | 232.8 | 253 | 251.2 | 444 | 41.4 | 20.3 | 77.7 | 6.7 | 282.8 | 4.7 | 765.1 | 647 | 659 | 744.9 | 613.8 | 455.8 | 833.8 | 494.9 | 650.6 | 515.4 | 81.8 | 139 | 182.5 | 153.2 | 266.2 | 253.2 | 140.5 | 221.9 | 246.3 | 195.9
1543.3 | 1324.3 | 466.5 | 186.6 | 218.1246 | 259.1 | 232.2 | 252.5 | 251.2 | 447.7 | 41.4 | 20.3 | 77.8 | 6.9 | 272.9 | 4.4 | 765.7 | 654 | 645.4 | 745.4 | 611.4 | 456.2 | 836.7 | 491.7 | 650.6 | 514.6 | 81.8 | 139.1 | 182.5 | 153.3 | 265.8 | 253.5 | 140.6 | 222 | 246.4 | 196
1544.3 | 1325.3 | 467.5 | 187 | 218.5922 | 258.6 | 232.7 | 252.5 | 252 | 442.9 | 41.2 | 20.3 | 78 | 6.7 | 242.7 | 4.3 | 766.8 | 666.7 | 651.3 | 748.2 | 610.8 | 456.8 | 842.7 | 502.5 | 646 | 515.3 | 81.9 | 139.3 | 182.7 | 153.4 | 265.7 | 253.3 | 140.7 | 222.2 | 246.6 | 196.2
1545.3 | 1326.3 | 468.1 | 187.24 | 218.8728 | 257.4 | 233.2 | 251.9 | 252.9 | 440.4 | 41.2 | 20.3 | 78.2 | 6.4 | 261.9 | 4.2 | 765.4 | 672.4 | 647.5 | 746.8 | 609.7 | 457.2 | 839.6 | 504.1 | 644.1 | 515.6 | 82 | 139.4 | 182.8 | 153.5 | 266.3 | 253.1 | 140.9 | 222.4 | 246.7 | 196.3
1546.3 | 1327.3 | 467.2 | 186.88 | 218.452 | 257.7 | 233.5 | 251.7 | 252.8 | 442.9 | 41.4 | 20.3 | 78.4 | 7 | 254.4 | 4.2 | 765.5 | 685.7 | 661.9 | 746.8 | 610 | 457.6 | 843.2 | 503.1 | 649.2 | 515.1 | 82.1 | 139.6 | 183 | 153.7 | 266.7 | 253.3 | 141 | 222.6 | 247 | 196.5
1547.3 | 1328.3 | 465.6 | 186.24 | 217.7038 | 259.1 | 232.8 | 251.8 | 254 | 449.5 | 41.6 | 20.3 | 78.5 | 7.3 | 225.5 | 4.9 | 767 | 678.9 | 666.4 | 750.9 | 609.8 | 458.1 | 840.3 | 506.1 | 648.7 | 517.3 | 82.2 | 139.7 | 183.1 | 153.8 | 267.2 | 253.6 | 141.1 | 222.7 | 247.2 | 196.6
1548.3 | 1329.3 | 465.8 | 186.32 | 217.7973 | 260.1 | 232.3 | 251.6 | 255.3 | 458.1 | 41.7 | 20.3 | 78.6 | 6.8 | 242 | 5.2 | 766.2 | 670.8 | 665.7 | 752.5 | 609.6 | 458.6 | 840.8 | 496 | 650.3 | 516.3 | 82.3 | 139.8 | 183.3 | 153.9 | 267.8 | 254 | 141.2 | 222.9 | 247.4 | 196.8
1549.3 | 1330.3 | 464.8 | 185.92 | 217.3298 | 261.1 | 232.2 | 252 | 255.9 | 451.9 | 41.8 | 20.3 | 78.7 | 7.3 | 250.7 | 5.3 | 766.2 | 671.6 | 676 | 753.1 | 609.4 | 459 | 840 | 498.6 | 652 | 517.3 | 82.4 | 139.9 | 183.5 | 154 | 268.4 | 254.4 | 141.4 | 223 | 247.6 | 197
1550.3 | 1331.3 | 466.2 | 186.48 | 217.9844 | 260.7 | 231.1 | 252.2 | 256.2 | 447.5 | 42 | 20.2 | 78.7 | 6.8 | 260.4 | 5.1 | 768.4 | 674.6 | 677.9 | 757.5 | 611.5 | 459.5 | 840.4 | 500.2 | 650.3 | 519.2 | 82.5 | 140.1 | 183.6 | 154.1 | 268.8 | 254.5 | 141.5 | 223.2 | 247.8 | 197.2
1551.3 | 1332.3 | 466.5 | 186.6 | 218.1246 | 260.6 | 230.4 | 252.6 | 257.1 | 448.2 | 42.1 | 20.2 | 78.7 | 7.1 | 264.4 | 5.1 | 766.6 | 663.8 | 668.2 | 756.9 | 608.7 | 459.9 | 837.1 | 489.7 | 651.7 | 517.6 | 82.6 | 140.2 | 183.7 | 154.2 | 269.5 | 254.5 | 141.6 | 223.3 | 248 | 197.4
1552.3 | 1333.3 | 467 | 186.8 | 218.3584 | 260.5 | 230.2 | 253.4 | 258.3 | 436.6 | 42.2 | 20.2 | 78.6 | 7.2 | 258.4 | 5.4 | 763.4 | 659.6 | 649.3 | 752.9 | 605.7 | 460.2 | 840.2 | 484.9 | 654.1 | 516 | 82.7 | 140.4 | 183.8 | 154.3 | 269.6 | 255.3 | 141.7 | 223.6 | 248.2 | 197.6
1553.3 | 1334.3 | 466.1 | 186.44 | 217.9376 | 261 | 230.1 | 253.6 | 257.8 | 430.4 | 42.2 | 20.2 | 78.6 | 7.9 | 249.6 | 6.1 | 756.6 | 638 | 633 | 745.7 | 603 | 460.5 | 847.2 | 476.1 | 654.3 | 513.6 | 82.8 | 140.5 | 183.9 | 154.5 | 269.8 | 255.8 | 141.8 | 223.8 | 248.4 | 197.7
1554.3 | 1335.3 | 465.9 | 186.36 | 217.8441 | 261.4 | 229.9 | 252.8 | 256.1 | 425.5 | 42.3 | 20.2 | 78.6 | 7 | 262.5 | 6.8 | 752.3 | 624.5 | 623.8 | 741.4 | 600.9 | 460.9 | 845.8 | 469.6 | 650.8 | 512.5 | 82.9 | 140.6 | 184.2 | 154.6 | 270.2 | 256 | 142 | 223.8 | 248.5 | 197.9
1555.3 | 1336.3 | 466.3 | 186.52 | 218.0311 | 262.6 | 230.2 | 251.6 | 255.7 | 426.7 | 42.3 | 20.2 | 78.6 | 7 | 275.7 | 7.1 | 750.1 | 622.8 | 616.6 | 739.6 | 599.1 | 461.4 | 848.9 | 465.9 | 650.6 | 511.1 | 83 | 140.8 | 184.3 | 154.7 | 269.6 | 257.1 | 142.1 | 224.1 | 248.6 | 198
1556.3 | 1337.3 | 467.5 | 187 | 218.5922 | 262.7 | 230.2 | 252 | 256.5 | 424.5 | 42.4 | 20.2 | 78.6 | 7.5 | 265.7 | 6.9 | 745.2 | 612.8 | 611.2 | 734.2 | 597.1 | 461.9 | 852.8 | 461.2 | 653.1 | 509.2 | 83.1 | 140.9 | 184.3 | 154.8 | 269.5 | 258.1 | 142.2 | 224.2 | 248.7 | 198.2
1557.3 | 1338.3 | 466.2 | 186.48 | 217.9844 | 262.7 | 231 | 252.1 | 257 | 425.3 | 42.5 | 20.2 | 78.6 | 7.2 | 256 | 6.6 | 741 | 609.2 | 610 | 728.5 | 594.9 | 462.3 | 850.8 | 461.4 | 652 | 507.7 | 83.2 | 141.1 | 184.5 | 155 | 269.2 | 258.4 | 142.3 | 224.3 | 248.8 | 198.3
1558.3 | 1339.3 | 465.8 | 186.32 | 217.7973 | 263.6 | 231.5 | 252.5 | 257.5 | 426 | 42.5 | 20.2 | 78.7 | 7.4 | 258.9 | 5.9 | 738.2 | 607.1 | 618.3 | 727.3 | 594.7 | 462.6 | 854.1 | 458.5 | 652.4 | 507.1 | 83.3 | 141.2 | 184.7 | 155.1 | 269 | 258.1 | 142.4 | 224.5 | 249 | 198.4
1559.3 | 1340.3 | 467.6 | 187.04 | 218.639 | 264.7 | 231.1 | 252.3 | 257.9 | 431.3 | 42.6 | 20.2 | 78.7 | 6.4 | 279.8 | 5 | 738.9 | 615.4 | 617.3 | 729.4 | 593.1 | 463 | 852.1 | 460.1 | 649.5 | 507.3 | 83.4 | 141.3 | 184.7 | 155.3 | 268.8 | 257.8 | 142.6 | 224.6 | 249.1 | 198.6
1560.3 | 1341.3 | 467.8 | 187.12 | 218.7325 | 266.2 | 230.1 | 251.8 | 259.2 | 432.7 | 42.6 | 20.2 | 78.7 | 6.3 | 281 | 4.5 | 736.8 | 613.4 | 615.7 | 727.6 | 591.1 | 463.4 | 854.3 | 457.5 | 650.3 | 506 | 83.5 | 141.5 | 185 | 155.4 | 268.9 | 257.7 | 142.7 | 224.7 | 249.2 | 198.7
1561.3 | 1342.3 | 467.8 | 187.12 | 218.7325 | 267.1 | 229.7 | 252.1 | 259.3 | 426.9 | 42.7 | 20.2 | 78.7 | 6.6 | 256.4 | 5.2 | 735 | 609.1 | 617.7 | 725.7 | 590.7 | 463.9 | 850 | 459.5 | 657 | 505.1 | 83.6 | 141.6 | 185.2 | 155.6 | 269.1 | 257.6 | 142.8 | 224.9 | 249.4 | 198.9
1562.3 | 1343.3 | 467.7 | 187.08 | 218.6857 | 267.7 | 229.6 | 253.6 | 258 | 428.7 | 42.8 | 20.2 | 78.7 | 7.3 | 279.1 | 6 | 735 | 613.6 | 627 | 725.3 | 589.8 | 464.3 | 848.3 | 460.3 | 651.6 | 505.2 | 83.7 | 141.7 | 185.5 | 155.7 | 268.8 | 257.5 | 142.9 | 225 | 249.5 | 199
1563.3 | 1344.3 | 467.7 | 187.08 | 218.6857 | 268.2 | 229.3 | 253.6 | 258.2 | 431.5 | 42.9 | 20.2 | 78.8 | 6.9 | 265.1 | 5.7 | 739.8 | 632.5 | 632 | 732.4 | 590.8 | 464.8 | 839.2 | 470.5 | 646.8 | 507.5 | 83.8 | 141.8 | 185.6 | 155.8 | 268.9 | 257.5 | 143 | 225.2 | 249.6 | 199.2
1564.3 | 1345.3 | 467.6 | 187.04 | 218.639 | 267.6 | 229.1 | 253.9 | 257.4 | 436.1 | 42.9 | 20.2 | 78.9 | 6.9 | 241 | 5.7 | 741.5 | 647.2 | 640.9 | 733.3 | 590.5 | 465.2 | 840.6 | 474.3 | 644.6 | 507.7 | 83.9 | 141.9 | 185.5 | 156 | 269.6 | 257.6 | 143.2 | 225.4 | 249.8 | 199.4
1565.3 | 1346.3 | 468.8 | 187.52 | 219.2001 | 269.3 | 230.1 | 253.6 | 257 | 430.5 | 43 | 20.2 | 78.9 | 6.9 | 248.4 | 5.8 | 742.5 | 643.6 | 637.8 | 733.7 | 589.7 | 465.6 | 827.2 | 478.3 | 640.6 | 508.2 | 84 | 142.1 | 185.7 | 156.1 | 269.5 | 257.7 | 143.3 | 225.5 | 249.9 | 199.6
1566.3 | 1347.3 | 467.1 | 186.84 | 218.4052 | 270.5 | 231.1 | 253 | 258.1 | 429 | 42.9 | 20.2 | 78.9 | 7.2 | 245 | 5.8 | 742.8 | 663.5 | 640.8 | 732.1 | 588.6 | 466.1 | 825.8 | 485.6 | 641 | 507.6 | 84 | 142.2 | 185.8 | 156.3 | 269.4 | 257.8 | 143.4 | 225.7 | 250.1 | 199.7
1567.3 | 1348.3 | 466.8 | 186.72 | 218.2649 | 270.7 | 232 | 252.3 | 257.8 | 434.4 | 42.9 | 20.2 | 78.9 | 6.7 | 254.3 | 6.2 | 746 | 668.7 | 652.7 | 737.9 | 590.2 | 466.5 | 825.3 | 493.7 | 638.5 | 508.9 | 84.1 | 142.3 | 186 | 156.4 | 269.2 | 257.9 | 143.6 | 225.8 | 250.2 | 199.9
1568.3 | 1349.3 | 467.5 | 187 | 218.5922 | 271.8 | 232.2 | 252.7 | 258.2 | 442.2 | 42.9 | 20.2 | 78.9 | 6.8 | 252.5 | 6.1 | 748.9 | 665.8 | 669 | 742 | 591.5 | 467 | 821.6 | 489.4 | 635.7 | 510.6 | 84.2 | 142.4 | 186.1 | 156.5 | 268.9 | 258 | 143.7 | 225.9 | 250.4 | 200
1569.3 | 1350.3 | 466.8 | 186.72 | 218.2649 | 272.2 | 231.7 | 253.3 | 259 | 441 | 42.9 | 20.2 | 78.9 | 6.7 | 226.5 | 5.7 | 754.3 | 688.8 | 686.1 | 749.1 | 594.7 | 467.4 | 828.2 | 503.3 | 632.2 | 513.4 | 84.3 | 142.6 | 186.3 | 156.7 | 268.9 | 258.8 | 143.8 | 226.1 | 250.6 | 200.2
1570.3 | 1351.3 | 466.2 | 186.48 | 217.9844 | 272.8 | 231.1 | 254.9 | 259.7 | 446.6 | 42.9 | 20.2 | 78.9 | 7 | 223.3 | 5.7 | 757.8 | 691.4 | 692.2 | 754.6 | 595.6 | 467.8 | 822.8 | 510.3 | 630.7 | 517.4 | 84.4 | 142.7 | 186.4 | 156.8 | 268.6 | 259.2 | 143.9 | 226.4 | 250.8 | 200.3
1571.3 | 1352.3 | 466.1 | 186.44 | 217.9376 | 271.6 | 231.1 | 254.9 | 259.7 | 444.6 | 43 | 20.2 | 79 | 7 | 232.9 | 5.4 | 757.9 | 682.1 | 691.5 | 756.1 | 594.8 | 468.3 | 822.6 | 498.1 | 625.4 | 517.2 | 84.5 | 142.8 | 186.6 | 157 | 268.5 | 258.9 | 144 | 226.6 | 251 | 200.4
1572.3 | 1353.3 | 467.8 | 187.12 | 218.7325 | 270.7 | 230.6 | 254.6 | 259.8 | 440.9 | 43.1 | 20.2 | 79 | 6.7 | 233.4 | 5 | 760.8 | 693 | 707.9 | 760.7 | 598.4 | 468.7 | 827.6 | 503.2 | 619.5 | 518.4 | 84.6 | 143 | 186.7 | 157.1 | 268.6 | 258.7 | 144.1 | 226.6 | 251.3 | 200.6
1573.3 | 1354.3 | 468.7 | 187.48 | 219.1533 | 272.1 | 230 | 255.5 | 259.4 | 443.6 | 43.2 | 20.2 | 79 | 7.9 | 225.6 | 5 | 761.8 | 693.7 | 707.4 | 761 | 600.1 | 469 | 832.6 | 509.4 | 614.5 | 518.6 | 84.7 | 143.1 | 186.8 | 157.2 | 269.2 | 258.6 | 144.3 | 226.7 | 251.5 | 200.7
1574.3 | 1355.3 | 467.3 | 186.92 | 218.4987 | 272.4 | 229.6 | 256.2 | 260.3 | 447.5 | 43.2 | 20.2 | 79 | 8 | 220.6 | 4.6 | 762.2 | 692.6 | 712.2 | 761.4 | 600.6 | 469.4 | 832.8 | 511.4 | 608 | 518.5 | 84.8 | 143.2 | 186.9 | 157.4 | 269.5 | 258.9 | 144.4 | 226.9 | 251.6 | 200.9
1575.3 | 1356.3 | 465.6 | 186.24 | 217.7038 | 272.4 | 229.5 | 256.3 | 260.2 | 453.2 | 43.3 | 20.2 | 79.1 | 8.2 | 213.7 | 4.4 | 765 | 692.9 | 725.8 | 767 | 603.2 | 469.8 | 818.1 | 516.3 | 604 | 520.9 | 84.9 | 143.3 | 187 | 157.5 | 269.7 | 258.8 | 144.5 | 227.1 | 251.8 | 201
1576.3 | 1357.3 | 465.8 | 186.32 | 217.7973 | 270.9 | 229.9 | 256.9 | 258.1 | 458.5 | 43.4 | 20.2 | 79.1 | 7.8 | 216.2 | 5 | 769 | 702.5 | 730.2 | 773.1 | 605.3 | 470.2 | 813.4 | 528.3 | 600.1 | 525 | 85 | 143.5 | 187.2 | 157.7 | 269.8 | 258.9 | 144.7 | 227.2 | 252 | 201.2
1577.3 | 1358.3 | 464.9 | 185.96 | 217.3765 | 270.2 | 230.1 | 256.7 | 257.3 | 460.6 | 43.4 | 20.2 | 79.2 | 8.3 | 232.6 | 5.1 | 771.5 | 709.6 | 736.4 | 773.7 | 606.5 | 470.6 | 817.2 | 528 | 599.6 | 525.9 | 85.1 | 143.6 | 187.4 | 157.8 | 269.7 | 259.1 | 144.8 | 227.3 | 252.2 | 201.3
1578.3 | 1359.3 | 466.2 | 186.48 | 217.9844 | 268.4 | 230.4 | 256.9 | 257.9 | 461.9 | 43.5 | 20.2 | 79.2 | 8.5 | 240.2 | 6 | 775.3 | 727.9 | 744.3 | 779.9 | 612 | 471.2 | 809.4 | 548.1 | 600 | 529.2 | 85.2 | 143.7 | 187.8 | 157.9 | 269.6 | 259 | 144.9 | 227.3 | 252.4 | 201.4
1579.3 | 1360.3 | 468.3 | 187.32 | 218.9663 | 267.5 | 231 | 257.3 | 258.7 | 476.5 | 43.5 | 20.2 | 79.2 | 9.2 | 245.1 | 6.9 | 777.9 | 725.9 | 742.9 | 782.5 | 614.4 | 471.6 | 805.6 | 550.3 | 599.9 | 530.5 | 85.3 | 143.9 | 187.8 | 158.1 | 269.6 | 259 | 145 | 227.4 | 252.7 | 201.6
1580.3 | 1361.3 | 467.8 | 187.12 | 218.7325 | 267.2 | 230.6 | 257.9 | 259.2 | 474.5 | 43.5 | 20.2 | 79.2 | 7.9 | 256.4 | 8.1 | 779 | 725.2 | 736.7 | 782.4 | 614.2 | 472.1 | 808.7 | 553.8 | 601.6 | 531.2 | 85.4 | 144 | 188 | 158.2 | 269.7 | 259.9 | 145.1 | 227.6 | 252.9 | 201.7
1581.3 | 1362.3 | 466.9 | 186.76 | 218.3117 | 266.9 | 229.8 | 258 | 259.4 | 468.8 | 43.5 | 20.2 | 79.2 | 7.8 | 254.6 | 9.6 | 782.4 | 732.9 | 747.6 | 787.2 | 615.5 | 472.6 | 811.2 | 561.7 | 599.2 | 531.3 | 85.5 | 144.2 | 188.1 | 158.3 | 269.9 | 259.8 | 145.3 | 227.8 | 253.2 | 201.8
1582.3 | 1363.3 | 465.1 | 186.04 | 217.47 | 266.4 | 228.7 | 258.8 | 259.7 | 474.3 | 43.5 | 20.2 | 79.3 | 8.3 | 241.6 | 12.3 | 786.7 | 732.5 | 757.4 | 791.4 | 617.8 | 473.1 | 808.6 | 572.4 | 598.5 | 533.7 | 85.6 | 144.3 | 188.2 | 158.5 | 270 | 259.9 | 145.4 | 228 | 253.4 | 202
1583.3 | 1364.3 | 464.7 | 185.88 | 217.283 | 265.8 | 228.5 | 257.3 | 259.7 | 473.3 | 43.5 | 20.2 | 79.3 | 9.2 | 242 | 11.4 | 788 | 724.5 | 755.1 | 791.3 | 618.7 | 473.7 | 808.1 | 560.8 | 596.6 | 532.3 | 85.7 | 144.4 | 188.4 | 158.6 | 270.2 | 259.7 | 145.5 | 228.1 | 253.7 | 202.2
1584.3 | 1365.3 | 466.7 | 186.68 | 218.2182 | 266.7 | 228.8 | 257.1 | 260 | 474.1 | 43.6 | 20.2 | 79.4 | 8.8 | 276.8 | 9.4 | 787.7 | 714.6 | 751.7 | 789.3 | 618.1 | 474.3 | 816.4 | 557.5 | 589.2 | 531.1 | 85.8 | 144.6 | 188.6 | 158.7 | 270.1 | 259.9 | 145.6 | 228.2 | 253.9 | 202.3
1585.3 | 1366.3 | 467.6 | 187.04 | 218.639 | 266.3 | 228.8 | 258.1 | 260.2 | 470.5 | 43.7 | 20.2 | 79.4 | 8.2 | 249 | 8.1 | 786.6 | 721 | 746.1 | 787.7 | 617.8 | 474.9 | 828.1 | 558.6 | 587.1 | 531.4 | 85.9 | 144.7 | 188.7 | 158.9 | 270.2 | 260.7 | 145.7 | 228.4 | 254.1 | 202.5
1586.3 | 1367.3 | 467.6 | 187.04 | 218.639 | 265.9 | 228.7 | 258.4 | 259.4 | 467.9 | 43.8 | 20.2 | 79.4 | 7.2 | 188.2 | 7.3 | 784.7 | 715.8 | 741.5 | 783.7 | 618 | 475.4 | 841.2 | 546.7 | 583.7 | 530.3 | 86 | 144.8 | 189 | 159 | 270.5 | 260.9 | 145.9 | 228.5 | 254.3 | 202.6
1587.3 | 1368.3 | 467.4 | 186.96 | 218.5455 | 265.8 | 229 | 257.7 | 259.7 | 460.1 | 43.9 | 20.2 | 79.4 | 8.2 | 263 | 6.8 | 783.3 | 711.8 | 725.6 | 782.8 | 615.7 | 475.8 | 845.2 | 540.7 | 581.6 | 529.6 | 86.1 | 145 | 189 | 159.1 | 270.8 | 260.8 | 146 | 228.6 | 254.5 | 202.8
1588.3 | 1369.3 | 467.5 | 187 | 218.5922 | 265.4 | 228.7 | 257.1 | 260.8 | 460.4 | 43.9 | 20.2 | 79.4 | 7.5 | 250.1 | 8.8 | 782.5 | 705 | 727.3 | 781.1 | 616 | 476.3 | 847.9 | 536.7 | 578.5 | 529 | 86.2 | 145.1 | 189.3 | 159.3 | 270.8 | 260.8 | 146.1 | 228.7 | 254.7 | 202.9
1589.3 | 1370.3 | 466.9 | 186.76 | 218.3117 | 266.2 | 228.4 | 257.2 | 260.8 | 454.1 | 44 | 20.2 | 79.3 | 8.2 | 250 | 9.6 | 780.7 | 693.1 | 722.5 | 778.4 | 613.9 | 476.9 | 850.9 | 528.5 | 575.1 | 527.9 | 86.3 | 145.2 | 189.5 | 159.4 | 271.1 | 260.8 | 146.3 | 228.9 | 254.8 | 203.1
1590.3 | 1371.3 | 467 | 186.8 | 218.3584 | 265.4 | 228.5 | 257.4 | 261.1 | 454.2 | 43.9 | 20.2 | 79.3 | 9.5 | 245.7 | 10 | 781.9 | 703.2 | 727.5 | 780.4 | 614.2 | 477.4 | 847 | 535.6 | 572.2 | 528.1 | 86.4 | 145.4 | 189.6 | 159.6 | 271.4 | 260.6 | 146.4 | 229 | 255 | 203.2
1591.3 | 1372.3 | 467.3 | 186.92 | 218.4987 | 264.8 | 229 | 257.8 | 261.2 | 458.9 | 43.9 | 20.2 | 79.5 | 9.2 | 263.6 | 11.7 | 781.7 | 697.3 | 721.9 | 780.1 | 613.6 | 478 | 846.4 | 530.9 | 570.1 | 527.5 | 86.4 | 145.5 | 189.8 | 159.7 | 271.7 | 260.9 | 146.5 | 229.2 | 255.1 | 203.4
1592.3 | 1373.3 | 467.6 | 187.04 | 218.639 | 264.2 | 229.5 | 257.3 | 260.1 | 459.4 | 43.8 | 20.2 | 79.6 | 11.2 | 249.2 | 11.2 | 780.8 | 701.3 | 711.3 | 776.7 | 612.7 | 478.6 | 840.4 | 529.8 | 565.9 | 525.3 | 86.5 | 145.6 | 189.7 | 159.8 | 271.8 | 260.7 | 146.6 | 229.3 | 255.3 | 203.6
1593.3 | 1374.3 | 467.7 | 187.08 | 218.6857 | 263.9 | 229.1 | 258.3 | 259.5 | 458.5 | 43.8 | 20.2 | 79.6 | 10.8 | 222.7 | 10.2 | 779.1 | 715.7 | 704.2 | 772 | 611.7 | 479.1 | 834.5 | 538.6 | 573.7 | 524.8 | 86.6 | 145.8 | 189.9 | 160 | 271.7 | 260.5 | 146.7 | 229.4 | 255.5 | 203.7
1594.3 | 1375.3 | 466.6 | 186.64 | 218.1714 | 263.5 | 228.5 | 259.1 | 259.4 | 472.7 | 43.7 | 20.2 | 79.7 | 9.2 | 245.8 | 10.3 | 777.9 | 698.6 | 697.6 | 769.6 | 611.2 | 479.6 | 832.1 | 540.7 | 570.8 | 524.7 | 86.7 | 145.9 | 189.9 | 160.1 | 271.5 | 260.4 | 146.9 | 229.5 | 255.6 | 203.8
1595.3 | 1376.3 | 466.7 | 186.68 | 218.2182 | 264.4 | 229.1 | 259.2 | 259.8 | 462.7 | 43.7 | 20.2 | 79.7 | 9.2 | 225.5 | 11.4 | 778.8 | 699.2 | 693.4 | 769.4 | 611.4 | 480.2 | 839.3 | 544.7 | 568.5 | 523.9 | 86.8 | 146 | 190.2 | 160.3 | 272.3 | 260.4 | 147 | 229.7 | 255.8 | 204
1596.3 | 1377.3 | 466.1 | 186.44 | 217.9376 | 265.4 | 229.3 | 259.4 | 259.4 | 461.3 | 43.6 | 20.2 | 79.7 | 8.7 | 256 | 10.7 | 777.9 | 698 | 689.5 | 766.3 | 609.5 | 480.8 | 836.1 | 540.3 | 563.4 | 522.8 | 86.9 | 146.2 | 190.5 | 160.4 | 273.3 | 260.4 | 147.1 | 229.8 | 255.9 | 204.2
1597.3 | 1378.3 | 465.9 | 186.36 | 217.8441 | 265.5 | 229.4 | 258.8 | 257.5 | 460 | 43.6 | 20.2 | 79.7 | 8.8 | 243.3 | 10.5 | 779.1 | 707 | 703.7 | 767.4 | 611.6 | 481.4 | 832.7 | 547.2 | 560.9 | 524.3 | 87 | 146.3 | 190.6 | 160.5 | 273.3 | 260.3 | 147.2 | 229.9 | 256 | 204.4
1598.3 | 1379.3 | 466.5 | 186.6 | 218.1246 | 265 | 230.2 | 257.9 | 256 | 466.3 | 43.6 | 20.2 | 79.7 | 8 | 245.8 | 15.1 | 778.3 | 700.9 | 701.4 | 766.5 | 611.7 | 482 | 822.7 | 548.7 | 557 | 523.3 | 87.1 | 146.5 | 190.8 | 160.7 | 273.4 | 260.3 | 147.3 | 230 | 256.2 | 204.5
1599.3 | 1380.3 | 467.7 | 187.08 | 218.6857 | 264.5 | 230.1 | 257.7 | 255.6 | 461.5 | 43.5 | 20.2 | 79.7 | 8.7 | 238.4 | 14.5 | 776.6 | 705.9 | 702.7 | 765.6 | 610.6 | 482.6 | 822.7 | 535 | 553 | 522.1 | 87.2 | 146.6 | 191 | 160.8 | 273.2 | 260.1 | 147.5 | 230 | 256.4 | 204.6
1600.3 | 1381.3 | 468.2 | 187.28 | 218.9195 | 263.7 | 230.2 | 258.1 | 255.8 | 452.4 | 43.5 | 20.1 | 79.7 | 9.6 | 236.7 | 13.9 | 774.9 | 694.2 | 696.1 | 766.5 | 608.7 | 483.2 | 827.6 | 523.4 | 548.3 | 520.9 | 87.3 | 146.7 | 190.9 | 160.9 | 272.7 | 259.9 | 147.6 | 230.1 | 256.5 | 204.8
1601.3 | 1382.3 | 466.4 | 186.56 | 218.0779 | 263.5 | 230 | 258.3 | 255.7 | 446.5 | 43.5 | 20.1 | 79.7 | 9.8 | 215.1 | 13.2 | 775 | 695.5 | 693.1 | 767.4 | 607.5 | 483.8 | 826 | 514.1 | 544.1 | 519.9 | 87.4 | 146.8 | 191.1 | 161 | 272.5 | 259.8 | 147.7 | 230.2 | 256.6 | 204.9
1602.3 | 1383.3 | 465.7 | 186.28 | 217.7506 | 263.7 | 229.6 | 257.6 | 255.2 | 446.2 | 43.5 | 20.1 | 79.6 | 9.6 | 221.5 | 11.5 | 772.9 | 700.1 | 686.2 | 762.3 | 605.1 | 484.5 | 832 | 512.9 | 542 | 517.9 | 87.5 | 147 | 191.3 | 161.1 | 272 | 259.6 | 147.8 | 230.2 | 256.8 | 205
1603.3 | 1384.3 | 465.7 | 186.28 | 217.7506 | 263.9 | 229.4 | 257.1 | 254.7 | 449.1 | 43.5 | 20.1 | 79.7 | 9.3 | 244.4 | 10.1 | 772.2 | 712 | 681.7 | 759.8 | 604.7 | 485.1 | 826.4 | 515.9 | 540.3 | 517 | 87.6 | 147.1 | 191.4 | 161.3 | 271.5 | 259.5 | 148 | 230.2 | 256.9 | 205.1
1604.3 | 1385.3 | 464.5 | 185.8 | 217.1895 | 263.9 | 229.3 | 257.5 | 254.1 | 455.2 | 43.6 | 20.1 | 79.7 | 10.3 | 247.9 | 11.6 | 769.5 | 707.5 | 676.4 | 756.5 | 603.5 | 485.7 | 824.9 | 513.7 | 537 | 515.9 | 87.7 | 147.2 | 191.6 | 161.4 | 270.9 | 259.8 | 148.1 | 230.2 | 257 | 205.2
1605.3 | 1386.3 | 465.8 | 186.32 | 217.7973 | 264 | 229.3 | 258.4 | 254.3 | 457.2 | 43.7 | 20.1 | 79.7 | 8.6 | 245.7 | 12.3 | 770.2 | 703.1 | 678 | 757.1 | 602.4 | 486.3 | 822.8 | 517.1 | 533.8 | 515.8 | 87.8 | 147.4 | 191.7 | 161.5 | 270.2 | 259.8 | 148.2 | 230.3 | 257.1 | 205.3
1606.3 | 1387.3 | 466.6 | 186.64 | 218.1714 | 264.6 | 229.5 | 259.6 | 254.4 | 460.8 | 43.7 | 20.1 | 79.8 | 8.4 | 246.6 | 11.8 | 770.1 | 714.4 | 676.2 | 755.4 | 601.4 | 486.9 | 807.2 | 517 | 532.5 | 516.1 | 87.9 | 147.5 | 191.8 | 161.6 | 269.8 | 259.7 | 148.3 | 230.3 | 257.3 | 205.5
1607.3 | 1388.3 | 466.7 | 186.68 | 218.2182 | 264.7 | 230.8 | 260.1 | 254 | 456.4 | 43.8 | 20.1 | 79.8 | 8.4 | 257.2 | 10 | 770.4 | 708.9 | 676.7 | 755.2 | 600.2 | 487.5 | 810 | 508.9 | 534.9 | 514.4 | 88 | 147.6 | 191.9 | 161.7 | 269.4 | 259.5 | 148.4 | 230.3 | 257.4 | 205.6
1608.3 | 1389.3 | 465.6 | 186.24 | 217.7038 | 263.7 | 231.9 | 259.8 | 254.3 | 448.1 | 43.9 | 20.1 | 79.8 | 7.7 | 267.8 | 9.7 | 767.6 | 692.6 | 669.8 | 751.2 | 599.2 | 488 | 809.4 | 503.2 | 533.8 | 512.4 | 88.1 | 147.7 | 192 | 161.9 | 269 | 259.2 | 148.5 | 230.4 | 257.6 | 205.7
1609.3 | 1390.3 | 465.1 | 186.04 | 217.47 | 263.6 | 231.5 | 257.7 | 254.9 | 447.4 | 44 | 20.1 | 79.8 | 7.4 | 271.7 | 8.9 | 770 | 709.5 | 682 | 756.3 | 600 | 488.6 | 804.5 | 512 | 534.3 | 513.3 | 88.2 | 147.9 | 192.1 | 162 | 268.8 | 259 | 148.7 | 230.5 | 257.7 | 205.8
1610.3 | 1391.3 | 466.8 | 186.72 | 218.2649 | 263.2 | 231 | 255.7 | 253.8 | 454.6 | 44.1 | 20.1 | 80 | 7.8 | 237.6 | 9.2 | 771.9 | 722.5 | 691.1 | 760.3 | 601.1 | 489.1 | 800.6 | 521.8 | 531.4 | 513.6 | 88.4 | 148 | 192.3 | 162.1 | 268.6 | 259.2 | 148.8 | 230.5 | 257.8 | 206
1611.3 | 1392.3 | 467.4 | 186.96 | 218.5455 | 263 | 231.3 | 255.8 | 252.9 | 460.4 | 44.1 | 20.1 | 80.2 | 9.3 | 247.2 | 10.2 | 773.1 | 732.1 | 688.1 | 759.2 | 600.7 | 489.7 | 800.2 | 529.4 | 534.9 | 513.1 | 88.5 | 148.1 | 192.6 | 162.2 | 268.6 | 259.2 | 148.9 | 230.5 | 258 | 206.1
1612.3 | 1393.3 | 467.3 | 186.92 | 218.4987 | 263.3 | 231.8 | 256.6 | 254.6 | 461.8 | 44.1 | 20.1 | 80.3 | 8.6 | 263.7 | 10.7 | 775.3 | 732 | 699.7 | 762.9 | 602.1 | 490.3 | 800.4 | 542.7 | 542.1 | 514.6 | 88.6 | 148.2 | 192.7 | 162.3 | 268.7 | 259.5 | 149.1 | 230.7 | 258.2 | 206.3
1613.3 | 1394.3 | 467.3 | 186.92 | 218.4987 | 262.4 | 233.3 | 257.7 | 255.5 | 461.3 | 44.2 | 20.1 | 80.4 | 8.1 | 266.6 | 11.5 | 781.5 | 742.2 | 720.5 | 775.8 | 605.9 | 491 | 791.7 | 558.7 | 541.3 | 518.5 | 88.7 | 148.3 | 192.9 | 162.4 | 269 | 259.2 | 149.2 | 230.7 | 258.3 | 206.4
1614.3 | 1395.3 | 467.5 | 187 | 218.5922 | 263 | 234.3 | 257.3 | 254.4 | 474.5 | 44.2 | 20.1 | 80.5 | 7.9 | 266.6 | 11.2 | 788.6 | 771.1 | 744.7 | 783 | 610.2 | 491.6 | 787.7 | 591.7 | 544.9 | 524.1 | 88.8 | 148.4 | 193.2 | 162.5 | 269.3 | 259 | 149.3 | 230.8 | 258.5 | 206.6
1615.3 | 1396.3 | 468.9 | 187.56 | 219.2468 | 263 | 234 | 257.9 | 255.9 | 489.6 | 44.2 | 20.1 | 80.5 | 7.9 | 260.5 | 9.5 | 795.6 | 784.9 | 750.2 | 789.2 | 613.6 | 492.2 | 787.4 | 616.2 | 552.5 | 531 | 88.9 | 148.6 | 193.3 | 162.6 | 269.7 | 258.9 | 149.4 | 230.9 | 258.7 | 206.7
1616.3 | 1397.3 | 467 | 186.8 | 218.3584 | 262.4 | 234 | 257.9 | 256.9 | 502.1 | 44.2 | 20.1 | 80.4 | 7.1 | 258.9 | 9.6 | 799.8 | 779.8 | 748 | 794.7 | 616.5 | 492.8 | 789 | 602.5 | 556.8 | 533.2 | 89 | 148.7 | 193.3 | 162.7 | 270 | 258.9 | 149.5 | 231 | 259.1 | 206.9
1617.3 | 1398.3 | 467.4 | 186.96 | 218.5455 | 261.8 | 234 | 258.2 | 257.9 | 501.3 | 44.2 | 20.1 | 80.4 | 7.9 | 272.4 | 10.2 | 800.8 | 773 | 755.5 | 797.8 | 617.6 | 493.4 | 784.5 | 598.8 | 557.2 | 534.1 | 89.2 | 148.8 | 193.4 | 162.8 | 270.1 | 259.1 | 149.7 | 231.2 | 259.3 | 207
1618.3 | 1399.3 | 467.4 | 186.96 | 218.5455 | 261.3 | 233.5 | 258.7 | 258.7 | 503.4 | 44.2 | 20.1 | 80.4 | 8.3 | 277.9 | 10.4 | 803.7 | 771 | 766.4 | 802.1 | 621.5 | 494.1 | 781.7 | 592.8 | 560.8 | 537.2 | 89.3 | 149 | 193.4 | 162.9 | 270.3 | 259.5 | 149.8 | 231.3 | 259.5 | 207.1
1619.3 | 1400.3 | 466.2 | 186.48 | 217.9844 | 261.4 | 232.4 | 259.1 | 258.3 | 501.4 | 44.2 | 20.1 | 80.3 | 9 | 276.8 | 9.9 | 806.8 | 775.4 | 774.4 | 808.1 | 624.9 | 494.8 | 784.7 | 589.4 | 559.7 | 537.3 | 89.4 | 149.1 | 193.5 | 163 | 270.4 | 259.6 | 149.9 | 231.5 | 259.8 | 207.2
1620.3 | 1401.3 | 465.6 | 186.24 | 217.7038 | 262.2 | 231.7 | 259.1 | 257.7 | 495.4 | 44.2 | 20.1 | 80.3 | 9 | 275.7 | 9.3 | 806.4 | 757.4 | 763.6 | 808.4 | 625.6 | 495.5 | 791.4 | 572.3 | 558 | 536.3 | 89.6 | 149.2 | 193.6 | 163.1 | 270.5 | 260 | 150.1 | 231.7 | 260 | 207.4
1621.3 | 1402.3 | 466.2 | 186.48 | 217.9844 | 263.5 | 232 | 258.2 | 257.8 | 485 | 44.2 | 20.1 | 80.4 | 8.9 | 275 | 8.5 | 804.6 | 743.2 | 750.1 | 805.8 | 624.1 | 496.1 | 806.3 | 561.5 | 557.3 | 534.3 | 89.7 | 149.4 | 193.9 | 163.2 | 270.5 | 260.6 | 150.2 | 231.8 | 260.2 | 207.6
1622.3 | 1403.3 | 466.8 | 186.72 | 218.2649 | 263.7 | 231.4 | 258.9 | 257.6 | 477.6 | 44.2 | 20.1 | 80.4 | 9 | 271.1 | 8.2 | 803 | 740.2 | 752.4 | 803 | 625 | 496.8 | 816.6 | 554.6 | 557.5 | 532.8 | 89.8 | 149.5 | 194.1 | 163.3 | 270.2 | 261.7 | 150.3 | 231.9 | 260.4 | 207.7
1623.3 | 1404.3 | 466.7 | 186.68 | 218.2182 | 263.8 | 230.7 | 259.1 | 257.3 | 481.6 | 44.3 | 20.1 | 80.4 | 9 | 266.9 | 8.3 | 802.8 | 737.9 | 753.4 | 800.4 | 625.3 | 497.4 | 817.4 | 561.3 | 556.5 | 532.5 | 89.9 | 149.7 | 194.2 | 163.4 | 269.9 | 262.3 | 150.4 | 232 | 260.5 | 207.8
1624.3 | 1405.3 | 465.9 | 186.36 | 217.8441 | 263.2 | 230.5 | 259.1 | 255.9 | 485.1 | 44.3 | 20.1 | 80.5 | 9.1 | 260.1 | 8.8 | 804 | 762 | 769.6 | 801.6 | 628.1 | 498 | 819.5 | 575.4 | 559.1 | 535.3 | 90.1 | 149.8 | 194.4 | 163.5 | 269.9 | 262.2 | 150.5 | 232.1 | 260.7 | 208
1625.3 | 1406.3 | 467.9 | 187.16 | 218.7793 | 262.5 | 230.4 | 259.1 | 255.2 | 494.9 | 44.3 | 20.1 | 80.5 | 8.8 | 256.8 | 9.6 | 805.4 | 773.7 | 772.4 | 801.3 | 630.1 | 498.7 | 808.9 | 577.9 | 559.7 | 537.7 | 90.2 | 150 | 194.6 | 163.6 | 270.2 | 262.2 | 150.6 | 232.2 | 260.9 | 208.1
1626.3 | 1407.3 | 467.6 | 187.04 | 218.639 | 261.4 | 231.2 | 258.6 | 254.3 | 498.3 | 44.4 | 20.1 | 80.5 | 8.9 | 260.5 | 10.4 | 806.9 | 770.5 | 763.3 | 804.1 | 631.2 | 499.3 | 810.5 | 576.8 | 560.8 | 540.2 | 90.3 | 150.1 | 194.6 | 163.7 | 270.2 | 262.4 | 150.8 | 232.4 | 261.2 | 208.3
1627.3 | 1408.3 | 467.2 | 186.88 | 218.452 | 261.5 | 232.8 | 258.7 | 254.1 | 495.2 | 44.4 | 20.1 | 80.5 | 9 | 256.5 | 11.1 | 805.3 | 754.1 | 753.8 | 802.7 | 629.2 | 500 | 811.6 | 569 | 565.7 | 540.5 | 90.5 | 150.3 | 194.7 | 163.8 | 270.4 | 262.5 | 150.9 | 232.5 | 261.5 | 208.4
1628.3 | 1409.3 | 465.7 | 186.28 | 217.7506 | 262.6 | 234.2 | 258.6 | 254.8 | 485.7 | 44.4 | 20.1 | 80.5 | 9.3 | 260.9 | 10.8 | 805.5 | 765.2 | 755.8 | 803.6 | 629.6 | 500.5 | 818.6 | 568.5 | 563.9 | 540.3 | 90.6 | 150.4 | 194.8 | 163.9 | 270.5 | 262.4 | 151 | 232.6 | 261.7 | 208.5
1629.3 | 1410.3 | 465.2 | 186.08 | 217.5168 | 262.6 | 235.6 | 257.6 | 255.3 | 485.5 | 44.4 | 20.1 | 80.4 | 8.5 | 255.1 | 10.8 | 805.2 | 759.6 | 751.2 | 804.1 | 629.2 | 501.1 | 810.1 | 567.4 | 563 | 540.9 | 90.8 | 150.6 | 194.9 | 164.1 | 270.4 | 262.6 | 151.1 | 232.7 | 261.9 | 208.7
1630.3 | 1411.3 | 465.5 | 186.2 | 217.6571 | 262.9 | 236.4 | 258.2 | 255.4 | 487.7 | 44.4 | 20.1 | 80.4 | 8.3 | 255.7 | 11.8 | 803.4 | 747.6 | 741.4 | 800.5 | 627 | 501.7 | 813.3 | 565.3 | 561.8 | 539.4 | 90.9 | 150.7 | 195 | 164.2 | 270.3 | 263.2 | 151.3 | 232.8 | 262.2 | 208.8
1631.3 | 1412.3 | 464.2 | 185.68 | 217.0492 | 262.7 | 235.7 | 257.7 | 254.1 | 487.8 | 44.4 | 20.1 | 80.3 | 7.6 | 251.3 | 11.9 | 799.8 | 739.4 | 727.6 | 794.8 | 624.8 | 502.3 | 815.5 | 563.3 | 573.6 | 537.7 | 91 | 150.9 | 195.3 | 164.3 | 270.3 | 262.9 | 151.4 | 233 | 262.3 | 208.9
1632.3 | 1413.3 | 464.9 | 185.96 | 217.3765 | 262.1 | 235.6 | 256.9 | 252.6 | 486.5 | 44.4 | 20.1 | 80.4 | 8.4 | 250.5 | 12.1 | 800.6 | 747.2 | 737.3 | 797.8 | 625.3 | 503 | 818.9 | 564.6 | 578.3 | 538.8 | 91.2 | 151 | 195.5 | 164.4 | 270.1 | 263 | 151.5 | 233 | 262.5 | 209.1
1633.3 | 1414.3 | 466.9 | 186.76 | 218.3117 | 261.8 | 235.2 | 256.9 | 251.7 | 496 | 44.5 | 20.1 | 80.4 | 9.6 | 248 | 12.9 | 806.1 | 782 | 752.8 | 804.6 | 629.5 | 503.5 | 816.4 | 590.8 | 580.9 | 542.7 | 91.3 | 151.2 | 195.7 | 164.5 | 270.2 | 263.2 | 151.6 | 233 | 262.6 | 209.2
1634.3 | 1415.3 | 467.6 | 187.04 | 218.639 | 262.2 | 236.2 | 255.4 | 251.5 | 522.7 | 44.6 | 20.1 | 80.3 | 11.9 | 251.6 | 12.4 | 812.7 | 803.9 | 769.2 | 810.5 | 635 | 504.2 | 813.6 | 622.4 | 587.3 | 547.5 | 91.4 | 151.3 | 195.9 | 164.6 | 270.3 | 263.1 | 151.8 | 233.1 | 262.8 | 209.3
1635.3 | 1416.3 | 466 | 186.4 | 217.8909 | 262.5 | 236.8 | 254.6 | 252.2 | 540.5 | 44.6 | 20.1 | 80.4 | 11.8 | 250.6 | 10.6 | 817.2 | 812.1 | 782.5 | 812.9 | 639.2 | 504.8 | 806.3 | 645.1 | 591.8 | 553.3 | 91.6 | 151.5 | 196 | 164.8 | 270.1 | 262.8 | 151.9 | 233.1 | 263.1 | 209.4
1636.3 | 1417.3 | 465.3 | 186.12 | 217.5636 | 262.6 | 238.1 | 255.8 | 253.8 | 545.9 | 44.7 | 20.1 | 80.5 | 11.1 | 247.8 | 10 | 819.9 | 820.7 | 781.7 | 817.3 | 642 | 505.4 | 802.9 | 637.9 | 591.4 | 556.2 | 91.7 | 151.6 | 196.1 | 164.9 | 270.3 | 262.6 | 152 | 233.1 | 263.5 | 209.6
1637.3 | 1418.3 | 466.3 | 186.52 | 218.0311 | 262.7 | 238.8 | 256.2 | 256.4 | 531.2 | 44.8 | 20.1 | 80.7 | 10 | 246.8 | 10.3 | 818 | 809.2 | 766.8 | 816.2 | 640.6 | 506 | 806.9 | 617.6 | 589.6 | 553.9 | 91.8 | 151.8 | 196.3 | 165 | 270.7 | 262.6 | 152.1 | 233.2 | 263.8 | 209.7
1638.3 | 1419.3 | 466.7 | 186.68 | 218.2182 | 262.5 | 239.2 | 256.3 | 257.6 | 519.8 | 44.9 | 20.1 | 80.7 | 8.3 | 252.2 | 11.1 | 817.3 | 806.3 | 756.6 | 815.6 | 639.4 | 506.7 | 814.8 | 616.3 | 590.7 | 552.1 | 92 | 151.9 | 196.5 | 165.1 | 270.8 | 262.5 | 152.2 | 233.2 | 264 | 209.8
1639.3 | 1420.3 | 467.1 | 186.84 | 218.4052 | 262.6 | 239.5 | 256.6 | 258.6 | 523.9 | 45 | 20.1 | 80.6 | 10.4 | 238.5 | 15.8 | 817 | 790.5 | 745.5 | 812.7 | 638.6 | 507.4 | 818.3 | 618.5 | 590.5 | 552 | 92.1 | 152.1 | 196.8 | 165.3 | 270.5 | 262.3 | 152.4 | 233.4 | 264.2 | 210
1640.3 | 1421.3 | 467.4 | 186.96 | 218.5455 | 262.5 | 239.9 | 257.6 | 258 | 509.8 | 45.1 | 20.1 | 80.6 | 13.1 | 224.1 | 16 | 816.3 | 780.5 | 739 | 811.5 | 637.4 | 508 | 814.6 | 610.8 | 592.2 | 551.8 | 92.2 | 152.2 | 196.8 | 165.4 | 270.3 | 262.7 | 152.5 | 233.3 | 264.3 | 210.1
1641.3 | 1422.3 | 467.3 | 186.92 | 218.4987 | 262 | 241.1 | 259.1 | 257 | 510.8 | 45.1 | 20.1 | 80.5 | 11.9 | 250.7 | 14 | 813.9 | 760.2 | 720 | 808.1 | 634.5 | 508.6 | 821.7 | 598.6 | 590 | 550.1 | 92.4 | 152.4 | 196.8 | 165.5 | 270 | 262.6 | 152.6 | 233.4 | 264.6 | 210.2
1642.3 | 1423.3 | 467.4 | 186.96 | 218.5455 | 261.6 | 241.2 | 260.3 | 256.2 | 497.5 | 45.1 | 20.1 | 80.5 | 10.8 | 246.2 | 11.9 | 806.6 | 726.4 | 707.5 | 795.9 | 630.8 | 509.1 | 822.4 | 575.1 | 595.3 | 546.3 | 92.5 | 152.5 | 196.8 | 165.6 | 270.1 | 262.3 | 152.7 | 233.4 | 264.8 | 210.3
1643.3 | 1424.3 | 467.2 | 186.88 | 218.452 | 261.2 | 240.6 | 261.8 | 256 | 480.2 | 45.2 | 20.1 | 80.5 | 11.5 | 237.3 | 10.4 | 799.1 | 703.9 | 686.8 | 785.8 | 627.2 | 509.7 | 822.2 | 559.3 | 606.4 | 543.3 | 92.6 | 152.7 | 197.1 | 165.7 | 270.1 | 262.1 | 152.8 | 233.4 | 264.9 | 210.4
1644.3 | 1425.3 | 467.3 | 186.92 | 218.4987 | 261.3 | 239.5 | 262.1 | 256.3 | 465.3 | 45.2 | 20.1 | 80.4 | 13 | 242.2 | 14.6 | 793.4 | 692.3 | 678 | 777.9 | 624.9 | 510.3 | 817.2 | 546.9 | 611.6 | 540.5 | 92.7 | 152.8 | 197.2 | 165.8 | 270.1 | 261.7 | 153 | 233.5 | 265.1 | 210.6
1645.3 | 1426.3 | 467.3 | 186.92 | 218.4987 | 261.8 | 238.4 | 261.3 | 255.2 | 458.6 | 45.1 | 20.1 | 80.4 | 11.2 | 245.3 | 18.5 | 789.5 | 674.7 | 678.5 | 774.5 | 623.6 | 510.9 | 816.4 | 537.6 | 616.5 | 538.6 | 92.9 | 153 | 197.2 | 166 | 270.4 | 261.5 | 153.1 | 233.6 | 265.2 | 210.7
1646.3 | 1427.3 | 467.1 | 186.84 | 218.4052 | 262 | 238 | 259.9 | 254.2 | 458.3 | 45 | 20.1 | 80.4 | 11.2 | 242.8 | 19.4 | 786.1 | 664.5 | 673.9 | 769.2 | 622.9 | 511.5 | 819.2 | 528.9 | 614.2 | 537.1 | 93 | 153.1 | 197.3 | 166.1 | 270.1 | 261.1 | 153.2 | 233.6 | 265.3 | 210.8
1647.3 | 1428.3 | 467.3 | 186.92 | 218.4987 | 262.5 | 237.4 | 259.5 | 253.9 | 453.7 | 45 | 20 | 80.5 | 10.9 | 234.5 | 19.9 | 779.3 | 662.4 | 657.3 | 759.8 | 619.5 | 511.9 | 822.4 | 519.6 | 621.5 | 534.2 | 93.1 | 153.3 | 197.5 | 166.2 | 269.7 | 261 | 153.3 | 233.7 | 265.4 | 210.9
1648.3 | 1429.3 | 467 | 186.8 | 218.3584 | 262.9 | 237 | 258.9 | 252.8 | 448.2 | 45 | 20 | 80.6 | 11.5 | 244.1 | 16.8 | 774.6 | 661.5 | 655.7 | 753.9 | 618.6 | 512.3 | 829.4 | 515.6 | 625.5 | 532.3 | 93.3 | 153.4 | 197.7 | 166.3 | 269.6 | 261.6 | 153.5 | 233.8 | 265.6 | 211.1
1649.3 | 1430.3 | 466.9 | 186.76 | 218.3117 | 262.9 | 236.7 | 259.2 | 252.9 | 446 | 45 | 20 | 80.7 | 10.8 | 248 | 17.6 | 771.7 | 655.6 | 646.6 | 751.4 | 616.5 | 512.8 | 835.6 | 508.8 | 619.4 | 530.5 | 93.4 | 153.6 | 197.7 | 166.4 | 269.6 | 262.1 | 153.6 | 233.9 | 265.7 | 211.2
1650.3 | 1431.3 | 467 | 186.8 | 218.3584 | 262.6 | 235.9 | 259.6 | 253.5 | 442.1 | 45.1 | 20 | 80.8 | 10.5 | 254.7 | 18.2 | 768.8 | 653.9 | 648 | 747.9 | 615.1 | 513.3 | 843.2 | 504.4 | 610.2 | 529.4 | 93.5 | 153.7 | 197.8 | 166.5 | 270.3 | 262 | 153.7 | 234 | 265.8 | 211.3
1651.3 | 1432.3 | 467.1 | 186.84 | 218.4052 | 262.8 | 235.6 | 259.5 | 254 | 445.4 | 45.1 | 20 | 80.8 | 10.8 | 244 | 17.6 | 768.4 | 660 | 649.6 | 749.3 | 614.8 | 513.8 | 844.8 | 500.6 | 603.8 | 529.2 | 93.6 | 153.8 | 198 | 166.6 | 270.4 | 261.9 | 153.8 | 234.1 | 265.9 | 211.4
1652.3 | 1433.3 | 467 | 186.8 | 218.3584 | 263 | 235.5 | 258.7 | 254.7 | 447 | 45.1 | 20 | 80.8 | 11.4 | 241.1 | 17.2 | 766.2 | 666.1 | 653.8 | 744.9 | 612.4 | 514.2 | 843.2 | 497.4 | 604.5 | 526.8 | 93.8 | 154 | 197.9 | 166.7 | 270.5 | 261.9 | 153.9 | 234.2 | 266.1 | 211.6
1653.3 | 1434.3 | 467 | 186.8 | 218.3584 | 263.2 | 234.9 | 257.3 | 256 | 443.7 | 45.1 | 20 | 80.7 | 10.3 | 250.6 | 17.1 | 769.8 | 695.5 | 681.2 | 747.9 | 614.2 | 514.7 | 842.7 | 511.3 | 608.6 | 528.8 | 93.9 | 154.1 | 198.1 | 166.8 | 270.8 | 261.7 | 154.1 | 234.3 | 266.2 | 211.7
1654.3 | 1435.3 | 467.1 | 186.84 | 218.4052 | 263.4 | 234.3 | 257.6 | 256.4 | 461.3 | 45.2 | 20 | 80.7 | 10.4 | 251.6 | 17.1 | 773.2 | 730.1 | 703.6 | 751 | 617.8 | 515.2 | 832.8 | 540.6 | 605.7 | 530.7 | 94 | 154.2 | 198.4 | 166.9 | 270.5 | 261.3 | 154.2 | 234.3 | 266.3 | 211.8
1655.3 | 1436.3 | 466.5 | 186.6 | 218.1246 | 263.5 | 233.9 | 257.6 | 256.9 | 483.5 | 45.2 | 20 | 80.8 | 10.9 | 246.7 | 16.6 | 778.8 | 745.5 | 716.3 | 759.1 | 619.8 | 515.7 | 823.6 | 553 | 604.3 | 533.9 | 94.1 | 154.4 | 198.5 | 167.1 | 270.7 | 261 | 154.3 | 234.3 | 266.5 | 212
1656.3 | 1437.3 | 466.9 | 186.76 | 218.3117 | 263.7 | 233.3 | 258.5 | 256.1 | 508.8 | 45.3 | 20 | 80.8 | 11.3 | 240.1 | 13.3 | 780.2 | 760.2 | 720.9 | 758.9 | 620.8 | 516.1 | 817.7 | 578 | 605.4 | 536.6 | 94.3 | 154.5 | 198.8 | 167.2 | 270.9 | 260.7 | 154.4 | 234.3 | 266.7 | 212.1
1657.3 | 1438.3 | 468.4 | 187.36 | 219.013 | 263.6 | 233 | 259.9 | 254.8 | 515.1 | 45.2 | 20 | 80.9 | 12.2 | 245.5 | 13.4 | 782.2 | 754.3 | 730.6 | 762.4 | 622.5 | 516.6 | 812.4 | 571.3 | 605.5 | 537.9 | 94.4 | 154.7 | 198.8 | 167.3 | 271 | 260.7 | 154.6 | 234.3 | 267 | 212.3
1658.3 | 1439.3 | 466.2 | 186.48 | 217.9844 | 263.2 | 233.4 | 259.6 | 256.1 | 510.4 | 45.2 | 20 | 81 | 11.5 | 241.2 | 15.7 | 779.9 | 733.6 | 710.5 | 760.4 | 622.1 | 517.2 | 815.5 | 553 | 607.7 | 536.2 | 94.5 | 154.8 | 198.9 | 167.4 | 270.8 | 260.8 | 154.7 | 234.3 | 267.2 | 212.4
1659.3 | 1440.3 | 465.6 | 186.24 | 217.7038 | 263 | 234 | 258.6 | 257.3 | 498.6 | 45.1 | 20 | 80.9 | 10.4 | 245.1 | 15.5 | 778 | 706.3 | 694 | 759.9 | 619.9 | 517.7 | 821.5 | 539.6 | 607.4 | 535 | 94.7 | 154.9 | 199.2 | 167.5 | 270.9 | 260.9 | 154.8 | 234.5 | 267.5 | 212.5
1660.3 | 1441.3 | 467.1 | 186.84 | 218.4052 | 263 | 234.5 | 257.6 | 258 | 490.3 | 45.1 | 20 | 80.8 | 10.9 | 240.9 | 20.2 | 775.4 | 703 | 684.3 | 756.1 | 616.8 | 518.1 | 819.9 | 531.8 | 615.4 | 532.7 | 94.8 | 155 | 199.3 | 167.6 | 271 | 260.9 | 154.9 | 234.5 | 267.6 | 212.6
1661.3 | 1442.3 | 466.9 | 186.76 | 218.3117 | 263.5 | 235.1 | 257.6 | 257.2 | 477 | 45.1 | 20 | 80.7 | 11.8 | 246.3 | 21.7 | 770.4 | 690.5 | 664.9 | 750.6 | 613.3 | 518.4 | 816.7 | 522.1 | 617.3 | 530.2 | 94.9 | 155.2 | 199.5 | 167.7 | 271.2 | 261.3 | 155 | 234.6 | 267.8 | 212.8
1662.3 | 1443.3 | 465.9 | 186.36 | 217.8441 | 264 | 234.9 | 256.9 | 256.8 | 463.6 | 45 | 20 | 80.6 | 11.9 | 243.2 | 20.8 | 766.8 | 682.5 | 659.5 | 746.3 | 611.3 | 518.7 | 813.9 | 509.9 | 622.5 | 528.1 | 95 | 155.3 | 199.5 | 167.8 | 270.9 | 261.5 | 155.1 | 234.8 | 267.9 | 212.9
1663.3 | 1444.3 | 466.2 | 186.48 | 217.9844 | 263.9 | 234.5 | 257.4 | 255 | 457.4 | 45 | 20 | 80.6 | 12.8 | 245 | 19.8 | 766.7 | 703.9 | 672.4 | 744.8 | 611.7 | 519.1 | 817.9 | 520.3 | 615.8 | 528 | 95.2 | 155.4 | 199.6 | 167.9 | 270.7 | 261.5 | 155.3 | 234.9 | 268 | 213
1664.3 | 1445.3 | 466.8 | 186.72 | 218.2649 | 263.8 | 233.4 | 258.2 | 253.8 | 472.4 | 44.9 | 20 | 80.6 | 11.4 | 246.3 | 18.2 | 770.7 | 727.3 | 691.3 | 749.7 | 614.3 | 519.5 | 812.4 | 547 | 616.8 | 530 | 95.3 | 155.6 | 199.9 | 168 | 270.6 | 261.5 | 155.4 | 234.9 | 268.2 | 213.1
1665.3 | 1446.3 | 468.3 | 187.32 | 218.9663 | 263.8 | 232.4 | 258.2 | 252.9 | 477.3 | 44.9 | 20 | 80.6 | 13.2 | 239 | 18.7 | 770.4 | 710.6 | 677.1 | 748.6 | 612.4 | 519.8 | 813.5 | 534 | 610.4 | 529.2 | 95.4 | 155.7 | 199.9 | 168.1 | 270.2 | 261.6 | 155.5 | 235 | 268.3 | 213.2
1666.3 | 1447.3 | 468.1 | 187.24 | 218.8728 | 263.6 | 232.1 | 258.3 | 252.5 | 467.6 | 44.8 | 20 | 80.6 | 11.7 | 239.4 | 20.1 | 764.4 | 689.3 | 659.1 | 742.5 | 608.8 | 520.3 | 818.8 | 517.1 | 607.2 | 526.9 | 95.5 | 155.8 | 200.1 | 168.2 | 269.7 | 261.4 | 155.6 | 235.1 | 268.5 | 213.4
1667.3 | 1448.3 | 468.1 | 187.24 | 218.8728 | 263.6 | 231.6 | 258 | 253.4 | 456.5 | 44.8 | 20 | 80.6 | 12.2 | 245 | 19.4 | 758.8 | 678.2 | 643.1 | 736.3 | 606.8 | 520.7 | 824.7 | 507.6 | 605.8 | 525.4 | 95.6 | 156 | 200.2 | 168.3 | 269.3 | 260.9 | 155.7 | 235.2 | 268.6 | 213.5
1668.3 | 1449.3 | 468.7 | 187.48 | 219.1533 | 263.7 | 231.7 | 258 | 253.7 | 444.2 | 44.9 | 20 | 80.7 | 12.4 | 225.7 | 15.5 | 751.9 | 649 | 620.8 | 729.5 | 603.4 | 520.9 | 821 | 495.9 | 608 | 522.8 | 95.8 | 156.1 | 200.1 | 168.3 | 269.1 | 260.5 | 155.9 | 235.2 | 268.8 | 213.6
1669.3 | 1450.3 | 466.8 | 186.72 | 218.2649 | 263.9 | 231.2 | 257.7 | 253.8 | 431.9 | 44.9 | 20 | 80.7 | 10.9 | 237.3 | 16.6 | 743.5 | 623.7 | 605.9 | 719.5 | 599.7 | 521 | 809 | 483.2 | 614.3 | 520.6 | 95.9 | 156.3 | 200.2 | 168.4 | 269.2 | 260.8 | 156 | 235.2 | 268.9 | 213.7
1670.3 | 1451.3 | 464 | 185.6 | 216.9557 | 264.4 | 230.9 | 257.3 | 253.6 | 425.7 | 44.9 | 20 | 80.7 | 10.7 | 237.6 | 17.7 | 737.5 | 623.5 | 606.5 | 710.8 | 597.5 | 521.3 | 802.3 | 477.1 | 620.6 | 518.7 | 96 | 156.4 | 200.3 | 168.5 | 269.1 | 261.6 | 156.1 | 235.3 | 269 | 213.8
1671.3 | 1452.3 | 463.6 | 185.44 | 216.7687 | 265 | 230 | 256.9 | 253.5 | 429.5 | 44.9 | 20 | 80.7 | 10.7 | 243.1 | 20.8 | 738.7 | 653.7 | 626.4 | 711.8 | 598.3 | 521.8 | 803.3 | 488.1 | 625.1 | 519.5 | 96.1 | 156.5 | 200.5 | 168.6 | 269.2 | 262 | 156.2 | 235.4 | 269 | 214
1672.3 | 1453.3 | 465 | 186 | 217.4233 | 264.2 | 229.3 | 256.4 | 252.8 | 444.1 | 44.9 | 20 | 80.7 | 10.3 | 236.4 | 21.2 | 739.6 | 662.1 | 634.7 | 710.9 | 598.5 | 522.2 | 804.5 | 501.7 | 619.5 | 520.6 | 96.2 | 156.7 | 200.5 | 168.7 | 268.8 | 261.9 | 156.3 | 235.4 | 269.1 | 214.1
1673.3 | 1454.3 | 465 | 186 | 217.4233 | 263.4 | 229.7 | 256.1 | 252.2 | 444.2 | 45 | 20 | 80.7 | 9.4 | 235.7 | 21.9 | 739.8 | 677.4 | 654.5 | 710.3 | 600.1 | 522.8 | 813.5 | 508.1 | 623.7 | 521.2 | 96.4 | 156.8 | 200.6 | 168.8 | 268.4 | 261.6 | 156.5 | 235.5 | 269.3 | 214.2
1674.3 | 1455.3 | 467.1 | 186.84 | 218.4052 | 263 | 231.1 | 255.4 | 253.2 | 449.6 | 45 | 20 | 80.8 | 10.7 | 240.8 | 20.9 | 743.1 | 700.3 | 674.1 | 716.5 | 603.6 | 523.3 | 816.7 | 529.6 | 628 | 523.9 | 96.5 | 156.9 | 200.8 | 168.9 | 268.5 | 261.2 | 156.6 | 235.4 | 269.4 | 214.3
1675.3 | 1456.3 | 467.1 | 186.84 | 218.4052 | 263.4 | 232.2 | 253.7 | 253.1 | 466.9 | 45 | 20 | 80.9 | 11.3 | 237.9 | 19.6 | 745.9 | 711.9 | 690.5 | 719.8 | 604.8 | 523.8 | 822.4 | 531.6 | 620.8 | 523.8 | 96.6 | 157.1 | 200.8 | 169 | 268.2 | 260.8 | 156.7 | 235.5 | 269.6 | 214.4
1676.3 | 1457.3 | 466.3 | 186.52 | 218.0311 | 263.3 | 233.2 | 252.8 | 253.1 | 467.4 | 45 | 20 | 81 | 12.6 | 242.8 | 20.4 | 745.4 | 700.9 | 684.8 | 719.8 | 602.5 | 524.3 | 819.1 | 525.7 | 616 | 522.1 | 96.7 | 157.2 | 200.9 | 169.1 | 267.7 | 260.6 | 156.8 | 235.5 | 269.8 | 214.5
1677.3 | 1458.3 | 467.1 | 186.84 | 218.4052 | 262.9 | 234.1 | 253.7 | 252.7 | 466 | 45.1 | 20 | 81 | 12.3 | 242.4 | 20.1 | 742.8 | 698.5 | 674.6 | 715.4 | 601.3 | 524.7 | 808.3 | 521.9 | 617.8 | 520.5 | 96.8 | 157.3 | 200.9 | 169.2 | 267.4 | 260.7 | 156.9 | 235.5 | 269.9 | 214.6
1678.3 | 1459.3 | 468.1 | 187.24 | 218.8728 | 262.4 | 234 | 254.3 | 252.1 | 460.9 | 45.2 | 20 | 80.9 | 11.8 | 238.9 | 21.5 | 741 | 691.5 | 664.3 | 713.7 | 599 | 525 | 807.7 | 510.9 | 617.2 | 518.6 | 97 | 157.5 | 200.9 | 169.3 | 267.2 | 260.7 | 157 | 235.5 | 270.1 | 214.7
1679.3 | 1460.3 | 467.3 | 186.92 | 218.4987 | 262.1 | 235.2 | 253.6 | 252.3 | 449.9 | 45.3 | 20 | 80.8 | 11.2 | 239.7 | 20.2 | 737.1 | 670.8 | 649 | 710.5 | 596.8 | 525.3 | 802.4 | 496.8 | 615.4 | 516.9 | 97.1 | 157.6 | 201.1 | 169.4 | 267.1 | 260.3 | 157.2 | 235.6 | 270.2 | 214.8
1680.3 | 1461.3 | 467.2 | 186.88 | 218.452 | 261.3 | 236.2 | 252.4 | 252.7 | 441.7 | 45.4 | 20 | 80.8 | 8.9 | 239 | 19.9 | 737.1 | 664.7 | 654.9 | 711.3 | 595.5 | 525.7 | 802.6 | 491.2 | 619.8 | 515.4 | 97.2 | 157.7 | 201.2 | 169.5 | 267 | 260 | 157.3 | 235.6 | 270.3 | 214.9
1681.3 | 1462.3 | 465.5 | 186.2 | 217.6571 | 261 | 237.1 | 251.1 | 253.4 | 443.9 | 45.5 | 20 | 80.9 | 8.2 | 242.4 | 20.1 | 737.9 | 666.3 | 656.2 | 711.3 | 594.5 | 526 | 804.2 | 492.3 | 618 | 515 | 97.3 | 157.8 | 201.3 | 169.6 | 266.8 | 259.7 | 157.4 | 235.7 | 270.4 | 215
1682.3 | 1463.3 | 465.7 | 186.28 | 217.7506 | 260.7 | 237.4 | 250.3 | 253.1 | 442.5 | 45.4 | 20 | 81 | 8.6 | 248.7 | 19.8 | 737 | 657.6 | 648 | 711.8 | 593.5 | 526.4 | 807.8 | 488.4 | 620.2 | 514.9 | 97.4 | 158 | 201.3 | 169.7 | 266.8 | 259.3 | 157.6 | 235.7 | 270.6 | 215.1
1683.3 | 1464.3 | 465.7 | 186.28 | 217.7506 | 260.2 | 237.1 | 249.8 | 251.6 | 442.5 | 45.4 | 20 | 81.1 | 9.1 | 236.3 | 17.9 | 740.9 | 678.6 | 662.1 | 718.9 | 595.2 | 526.8 | 808.1 | 501.4 | 617.9 | 517.7 | 97.5 | 158.1 | 201.5 | 169.7 | 267.1 | 259 | 157.6 | 235.7 | 270.7 | 215.2
1684.3 | 1465.3 | 465.9 | 186.36 | 217.8441 | 260 | 236.5 | 249.4 | 251.4 | 460.2 | 45.4 | 20 | 81.1 | 8.6 | 249.2 | 18 | 745.7 | 699.2 | 684.2 | 727.4 | 598.9 | 527.1 | 811.3 | 516.4 | 616 | 521.2 | 97.7 | 158.2 | 201.7 | 169.8 | 267.1 | 259 | 157.7 | 235.8 | 270.9 | 215.4
1685.3 | 1466.3 | 466.2 | 186.48 | 217.9844 | 259.7 | 235.7 | 248.5 | 251.8 | 467.8 | 45.4 | 20 | 81.2 | 9.5 | 246.4 | 18.7 | 749.4 | 698.2 | 702.6 | 735.2 | 601.4 | 527.5 | 806.1 | 518.1 | 613.3 | 526.2 | 97.8 | 158.3 | 201.9 | 169.9 | 267.3 | 258.9 | 157.9 | 235.8 | 271.1 | 215.5
1686.3 | 1467.3 | 466.3 | 186.52 | 218.0311 | 259.5 | 235.4 | 250.5 | 252.5 | 468.4 | 45.4 | 20 | 81.1 | 10.6 | 251.2 | 17.7 | 749.2 | 682.3 | 707.9 | 734 | 602.5 | 528 | 806.9 | 510 | 610.1 | 526.4 | 97.9 | 158.4 | 202 | 170 | 268 | 258.9 | 158 | 235.9 | 271.3 | 215.6
1687.3 | 1468.3 | 466.4 | 186.56 | 218.0779 | 259.4 | 235.5 | 251.6 | 253.4 | 460.1 | 45.3 | 20 | 81.1 | 9.6 | 241.4 | 14.6 | 748.1 | 675.9 | 696.6 | 738.4 | 601.8 | 528.4 | 810.9 | 502.2 | 608.7 | 525 | 98 | 158.5 | 202.1 | 170 | 268.4 | 259.3 | 158.1 | 236 | 271.5 | 215.7
1688.3 | 1469.3 | 466.5 | 186.6 | 218.1246 | 259.3 | 235.5 | 251.4 | 252.8 | 454.7 | 45.3 | 20 | 81.2 | 9 | 241.4 | 13.5 | 748.4 | 670.5 | 698.5 | 740.6 | 602.1 | 528.9 | 816.4 | 501 | 609.2 | 525.1 | 98.1 | 158.7 | 202.1 | 170.1 | 268.5 | 259.6 | 158.2 | 236.1 | 271.6 | 215.9
1689.3 | 1470.3 | 466.7 | 186.68 | 218.2182 | 259.7 | 234.5 | 251.3 | 252.4 | 452.6 | 45.2 | 20 | 81.2 | 9.7 | 244.1 | 14.9 | 746.5 | 675.2 | 693.3 | 736.4 | 600.7 | 529.4 | 819.4 | 500.9 | 605.4 | 523.5 | 98.2 | 158.8 | 202.3 | 170.2 | 268.3 | 259.8 | 158.4 | 236.1 | 271.7 | 216
1690.3 | 1471.3 | 466.7 | 186.68 | 218.2182 | 260.3 | 234.2 | 251 | 252.4 | 455.9 | 45.1 | 20 | 81.2 | 10.5 | 249.9 | 15.4 | 744 | 676.7 | 680.3 | 732.3 | 598.8 | 529.6 | 823.8 | 501.2 | 609.4 | 522.4 | 98.3 | 158.9 | 202.4 | 170.3 | 267.9 | 259.5 | 158.4 | 236.2 | 271.9 | 216.1
1691.3 | 1472.3 | 466.7 | 186.68 | 218.2182 | 261.1 | 234.2 | 250.3 | 251.4 | 451.8 | 45 | 20 | 81.2 | 10.7 | 240.6 | 13.5 | 740.4 | 677.4 | 669.9 | 725.5 | 596 | 529.8 | 820.7 | 499.9 | 618.5 | 520.3 | 98.5 | 159 | 202.5 | 170.4 | 267.3 | 259 | 158.6 | 236.3 | 272 | 216.2
1692.3 | 1473.3 | 466.8 | 186.72 | 218.2649 | 261.4 | 234.1 | 250.5 | 250.1 | 450.4 | 45 | 20 | 81.3 | 11 | 219 | 13.3 | 743.2 | 691.3 | 683.4 | 728.5 | 598.4 | 530.2 | 819.8 | 519 | 622.1 | 521.9 | 98.6 | 159.1 | 202.7 | 170.4 | 267 | 259.2 | 158.7 | 236.3 | 272.1 | 216.3
1693.3 | 1474.3 | 466.6 | 186.64 | 218.1714 | 261.9 | 234.2 | 250.9 | 248.7 | 458.8 | 45.1 | 20 | 81.3 | 10.4 | 244.3 | 9.9 | 749.2 | 709 | 690 | 734.7 | 599.3 | 530.5 | 817.6 | 541.6 | 620.4 | 524.1 | 98.7 | 159.2 | 202.9 | 170.5 | 266.9 | 259.7 | 158.8 | 236.3 | 272.2 | 216.4
1694.3 | 1475.3 | 466.6 | 186.64 | 218.1714 | 262.2 | 234.8 | 251.5 | 248.6 | 469.3 | 45.1 | 20 | 81.3 | 10.8 | 254.8 | 10.3 | 752.3 | 708.8 | 694.6 | 737 | 600.3 | 530.8 | 815.9 | 537.1 | 618.4 | 525 | 98.8 | 159.3 | 202.9 | 170.6 | 266.9 | 259.3 | 158.9 | 236.4 | 272.4 | 216.5
1695.3 | 1476.3 | 466.6 | 186.64 | 218.1714 | 261.9 | 236.2 | 251.7 | 248.8 | 470.8 | 45.2 | 20 | 81.3 | 10 | 243.1 | 17.4 | 754.1 | 696.2 | 697.5 | 739.8 | 600.8 | 531.3 | 813.2 | 525.5 | 617.6 | 526.4 | 98.9 | 159.4 | 203.1 | 170.7 | 267 | 259.6 | 159 | 236.4 | 272.6 | 216.6
1696.3 | 1477.3 | 466.4 | 186.56 | 218.0779 | 261.9 | 237.6 | 252.8 | 248.7 | 469 | 45.2 | 20 | 81.4 | 11.2 | 228.2 | 20.3 | 756.1 | 705.3 | 690 | 742.4 | 600.2 | 531.8 | 812.6 | 526.9 | 618.6 | 525.6 | 99 | 159.5 | 203.2 | 170.8 | 267.1 | 259.8 | 159.2 | 236.5 | 272.8 | 216.7
1697.3 | 1478.3 | 466.6 | 186.64 | 218.1714 | 261.8 | 237.7 | 252.5 | 248.8 | 470.9 | 45.2 | 20 | 81.4 | 10.2 | 233.5 | 18.2 | 757.7 | 714.9 | 688.8 | 743.3 | 600.3 | 532.2 | 810.6 | 532.7 | 615.1 | 526.6 | 99.2 | 159.7 | 203.5 | 170.9 | 267.5 | 259.7 | 159.3 | 236.6 | 272.9 | 216.8
1698.3 | 1479.3 | 466.4 | 186.56 | 218.0779 | 262.1 | 238 | 250.7 | 249.1 | 473.8 | 45.2 | 20 | 81.4 | 9.1 | 240.2 | 17.1 | 753.6 | 695.3 | 676.3 | 738.4 | 598 | 532.6 | 809.5 | 520.5 | 615.1 | 525.4 | 99.3 | 159.8 | 203.5 | 170.9 | 267.8 | 260.2 | 159.4 | 236.8 | 273.1 | 217
1699.3 | 1480.3 | 466.2 | 186.48 | 217.9844 | 262.8 | 238 | 250.7 | 250.3 | 457.2 | 45.1 | 20 | 81.4 | 11.8 | 227.2 | 17.1 | 749.8 | 679.8 | 663.1 | 735.6 | 595.5 | 532.8 | 811.2 | 509.8 | 618.9 | 522.8 | 99.4 | 159.9 | 203.3 | 171 | 268.7 | 260.3 | 159.5 | 236.9 | 273.3 | 217.1
1700.3 | 1481.3 | 466.4 | 186.56 | 218.0779 | 263.4 | 238.1 | 250.5 | 252.1 | 448.1 | 45 | 20 | 81.4 | 12.7 | 239.3 | 16.6 | 743.9 | 657.7 | 646.3 | 729.4 | 593.4 | 533 | 808.2 | 500.1 | 622.2 | 520.5 | 99.5 | 160 | 203.4 | 171.1 | 269.6 | 260.5 | 159.6 | 237 | 273.4 | 217.2
1701.3 | 1482.3 | 466.2 | 186.48 | 217.9844 | 263.5 | 238.1 | 250.4 | 253.5 | 441.9 | 44.9 | 20 | 81.4 | 13.6 | 239.6 | 18.4 | 741.5 | 654.6 | 652.4 | 726.6 | 593.1 | 533.4 | 811.8 | 494.6 | 622.7 | 519.5 | 99.6 | 160.1 | 203.5 | 171.2 | 269.7 | 260.7 | 159.8 | 237.1 | 273.5 | 217.4
1702.3 | 1483.3 | 466.3 | 186.52 | 218.0311 | 263.5 | 237.4 | 251.1 | 252.7 | 445 | 44.9 | 20 | 81.4 | 12.4 | 241.5 | 17.6 | 739.7 | 669.9 | 659.3 | 722.9 | 592.4 | 533.7 | 812.9 | 496.5 | 622.7 | 518.8 | 99.7 | 160.2 | 203.8 | 171.3 | 269.3 | 260.6 | 159.9 | 237.1 | 273.5 | 217.5
1703.3 | 1484.3 | 466.2 | 186.48 | 217.9844 | 263.9 | 236.5 | 251.8 | 251.7 | 446.7 | 44.9 | 20 | 81.4 | 13.5 | 235.7 | 20.4 | 737.9 | 678.5 | 663.4 | 721.1 | 592.6 | 534 | 810.1 | 502.5 | 627 | 518.7 | 99.8 | 160.3 | 204 | 171.3 | 269.2 | 261 | 160 | 237.2 | 273.6 | 217.5
1704.3 | 1485.3 | 466.4 | 186.56 | 218.0779 | 264 | 236.5 | 252.4 | 250.2 | 451.4 | 44.9 | 20 | 81.4 | 12.7 | 234.9 | 22.2 | 735.4 | 674.9 | 659.1 | 717.4 | 591.1 | 534.2 | 808.6 | 496.8 | 627.3 | 517.6 | 99.9 | 160.4 | 204.2 | 171.5 | 268.7 | 261.5 | 160.1 | 237.2 | 273.8 | 217.7
1705.3 | 1486.3 | 466.2 | 186.48 | 217.9844 | 264 | 235.7 | 253 | 250 | 443.5 | 45 | 20 | 81.5 | 11.9 | 235 | 22.3 | 733.8 | 667.7 | 654.3 | 714.2 | 589.7 | 534.4 | 807.8 | 494.7 | 630.2 | 515.8 | 100 | 160.6 | 204.2 | 171.5 | 268.3 | 261.6 | 160.2 | 237.3 | 273.9 | 217.8
1706.3 | 1487.3 | 466.3 | 186.52 | 218.0311 | 264 | 235.1 | 254.5 | 250.3 | 443 | 45.1 | 20 | 81.6 | 13.2 | 239.7 | 22.3 | 734.3 | 658.8 | 657.1 | 712.8 | 589.5 | 534.8 | 802.5 | 487.2 | 629.1 | 514.7 | 100.2 | 160.7 | 204.3 | 171.6 | 268 | 261.3 | 160.3 | 237.3 | 274 | 217.9
1707.3 | 1488.3 | 466.2 | 186.48 | 217.9844 | 263.7 | 234.1 | 255.4 | 251 | 448 | 45.1 | 20 | 81.7 | 15 | 243.3 | 23.5 | 738.2 | 671.5 | 669.6 | 715.4 | 590.6 | 535.2 | 804.1 | 489.6 | 629.9 | 514.7 | 100.3 | 160.8 | 204.4 | 171.7 | 267.7 | 261.4 | 160.4 | 237.3 | 274.1 | 218
1708.3 | 1489.3 | 466.2 | 186.48 | 217.9844 | 262.8 | 233.4 | 256.3 | 251.8 | 456.7 | 45.2 | 20 | 81.7 | 17.6 | 238.4 | 24.4 | 737.5 | 666.8 | 651.3 | 714.7 | 588.8 | 535.6 | 803.9 | 485 | 625.8 | 513.6 | 100.4 | 160.9 | 204.2 | 171.8 | 267.5 | 260.9 | 160.6 | 237.3 | 274.2 | 218
1709.3 | 1490.3 | 466.5 | 186.6 | 218.1246 | 262.7 | 232.5 | 256.2 | 253.1 | 451.6 | 45.2 | 20 | 81.7 | 14.8 | 241.2 | 31.6 | 736.8 | 673.7 | 641.2 | 714.8 | 587.9 | 535.8 | 811 | 484.2 | 624.8 | 512.3 | 100.5 | 161 | 204.4 | 171.9 | 267.4 | 260.6 | 160.7 | 237.3 | 274.3 | 218.1
1710.3 | 1491.3 | 467.8 | 187.12 | 218.7325 | 262 | 232.2 | 255.5 | 252.9 | 460.4 | 45.2 | 20 | 81.7 | 12.9 | 241.7 | 31 | 738.1 | 695.9 | 645.9 | 712.5 | 588.9 | 536.2 | 815.5 | 495.5 | 627.9 | 512 | 100.6 | 161.1 | 204.6 | 172 | 267.3 | 260.5 | 160.8 | 237.3 | 274.4 | 218.2
1711.3 | 1492.3 | 468.1 | 187.24 | 218.8728 | 261.5 | 232 | 254.7 | 252.5 | 460 | 45.2 | 20 | 81.7 | 11.7 | 244.1 | 29.3 | 737.6 | 691.2 | 649.4 | 710.9 | 587.5 | 536.6 | 814.6 | 492.7 | 630.2 | 511 | 100.7 | 161.2 | 204.6 | 172.1 | 267.9 | 260.8 | 160.9 | 237.4 | 274.5 | 218.3
1712.3 | 1493.3 | 468 | 187.2 | 218.826 | 261.3 | 232.9 | 254.7 | 252.9 | 453 | 45.1 | 20 | 81.7 | 13.3 | 249.7 | 29.9 | 736.8 | 694.3 | 658.6 | 705.5 | 588 | 536.8 | 816.2 | 493.2 | 633.9 | 509.8 | 100.8 | 161.3 | 204.8 | 172.2 | 269.2 | 261.4 | 161 | 237.6 | 274.6 | 218.5
1713.3 | 1494.3 | 467.4 | 186.96 | 218.5455 | 260.9 | 233.8 | 253.7 | 252 | 452.4 | 45 | 20 | 81.7 | 13.8 | 258.1 | 27 | 736.1 | 688.7 | 653.6 | 705.1 | 587.2 | 537.2 | 804.3 | 492.8 | 631.4 | 509.3 | 100.9 | 161.5 | 204.9 | 172.2 | 269.5 | 261.2 | 161.1 | 237.6 | 274.7 | 218.6
1714.3 | 1495.3 | 468.2 | 187.28 | 218.9195 | 260.6 | 234.3 | 252.2 | 249.7 | 446.5 | 45 | 20 | 81.6 | 13 | 258.9 | 24.7 | 737.4 | 679.3 | 647.2 | 709.2 | 586.5 | 537.6 | 805.8 | 487.2 | 626.6 | 508.9 | 101 | 161.6 | 205 | 172.3 | 269.2 | 261.1 | 161.3 | 237.6 | 274.8 | 218.7
1715.3 | 1496.3 | 467.5 | 187 | 218.5922 | 260.6 | 235 | 252.7 | 249.6 | 441.2 | 44.9 | 20 | 81.6 | 13.4 | 249.5 | 24.6 | 738.2 | 676.3 | 635.3 | 711.2 | 584.9 | 538.1 | 806.4 | 483.6 | 626 | 507.7 | 101.1 | 161.7 | 205.1 | 172.4 | 268.8 | 261.1 | 161.4 | 237.7 | 274.9 | 218.8
1716.3 | 1497.3 | 465.5 | 186.2 | 217.6571 | 260.6 | 235.6 | 252.7 | 250.5 | 440.2 | 44.9 | 19.9 | 81.6 | 13.8 | 245.3 | 20.9 | 736.8 | 680 | 628.7 | 709.8 | 583.3 | 538.4 | 806.2 | 482.4 | 627.9 | 507 | 101.3 | 161.8 | 205 | 172.5 | 268.5 | 260.7 | 161.5 | 237.7 | 275 | 218.9
1717.3 | 1498.3 | 465.4 | 186.16 | 217.6103 | 261 | 235.1 | 253.1 | 251 | 435.8 | 45 | 19.9 | 81.7 | 13.4 | 238.3 | 20.3 | 735.5 | 670.2 | 622.3 | 708.6 | 582.8 | 538.6 | 796.8 | 479.7 | 626.8 | 505.9 | 101.4 | 161.9 | 205.1 | 172.6 | 268.1 | 260.3 | 161.6 | 237.7 | 275.1 | 219
1718.3 | 1499.3 | 465.7 | 186.28 | 217.7506 | 260.5 | 235.2 | 253.1 | 251.2 | 430.2 | 45 | 19.9 | 81.6 | 14.2 | 240.2 | 22.4 | 735.7 | 675.1 | 627.9 | 710.2 | 583.5 | 539 | 793.1 | 480.4 | 626.5 | 505.3 | 101.5 | 162 | 205.3 | 172.7 | 267.8 | 259.9 | 161.7 | 237.7 | 275.2 | 219.1
1719.3 | 1500.3 | 465.6 | 186.24 | 217.7038 | 260.1 | 236.1 | 252.8 | 252.2 | 430.3 | 44.9 | 20 | 81.6 | 16.6 | 242 | 20.4 | 732.6 | 667.8 | 620.9 | 708.3 | 581 | 539.4 | 791.3 | 477.1 | 624.8 | 504.8 | 101.6 | 162.1 | 205.4 | 172.7 | 267.6 | 259.8 | 161.8 | 237.7 | 275.3 | 219.2
1720.3 | 1501.3 | 465.7 | 186.28 | 217.7506 | 259.7 | 236.9 | 252.3 | 252.9 | 426.9 | 44.9 | 19.9 | 81.6 | 17.5 | 238.1 | 22.4 | 728.8 | 657.8 | 610.9 | 704.8 | 578.7 | 539.6 | 781.4 | 473.5 | 624.6 | 503 | 101.7 | 162.2 | 205.3 | 172.8 | 267.3 | 260.5 | 162 | 237.8 | 275.4 | 219.3
1721.3 | 1502.3 | 465.5 | 186.2 | 217.6571 | 259.6 | 236.5 | 251.3 | 252.5 | 423.7 | 44.8 | 19.9 | 81.6 | 16.2 | 243.8 | 24.8 | 724.7 | 645.9 | 596.8 | 699.8 | 576.3 | 539.7 | 789.9 | 467.3 | 628.3 | 501.7 | 101.8 | 162.3 | 205.4 | 172.9 | 267.3 | 260.7 | 162 | 237.9 | 275.4 | 219.4
1722.3 | 1503.3 | 465.5 | 186.2 | 217.6571 | 259.7 | 236.4 | 251 | 251.4 | 423.3 | 44.7 | 20 | 81.6 | 17.2 | 245.1 | 25.5 | 718.5 | 625.7 | 582.9 | 694.5 | 573.9 | 539.9 | 788.6 | 458.5 | 627.7 | 500.1 | 101.9 | 162.4 | 205.4 | 173 | 266.8 | 260.8 | 162.2 | 237.9 | 275.5 | 219.5
1723.3 | 1504.3 | 466.9 | 186.76 | 218.3117 | 259.3 | 236.1 | 249.8 | 249.9 | 420.6 | 44.6 | 19.9 | 81.7 | 22.3 | 248.8 | 24.9 | 715.4 | 616 | 573.9 | 692.8 | 572.8 | 539.9 | 786.1 | 454.6 | 625.9 | 499.3 | 102 | 162.5 | 205.4 | 173.1 | 266.4 | 260.7 | 162.3 | 238 | 275.6 | 219.6
1724.3 | 1505.3 | 467 | 186.8 | 218.3584 | 258.6 | 237 | 248.6 | 248.8 | 417.9 | 44.5 | 19.9 | 81.9 | 20.2 | 252.6 | 27.5 | 711.5 | 625.9 | 575.4 | 687.9 | 570.6 | 540.2 | 784.4 | 451.3 | 628.8 | 498.1 | 102.1 | 162.6 | 205.5 | 173.2 | 265.8 | 260.9 | 162.4 | 238.1 | 275.6 | 219.6
1725.3 | 1506.3 | 465.6 | 186.24 | 217.7038 | 258.6 | 236.7 | 246.9 | 249 | 418.2 | 44.5 | 19.9 | 81.9 | 16.9 | 257.2 | 34.4 | 711.7 | 613.4 | 586.4 | 689.8 | 570.5 | 540.6 | 784.7 | 449.9 | 629.9 | 497.9 | 102.2 | 162.7 | 205.6 | 173.2 | 265.8 | 260.6 | 162.5 | 238.1 | 275.7 | 219.7
1726.3 | 1507.3 | 465.8 | 186.32 | 217.7973 | 258.6 | 236.7 | 245.4 | 248.8 | 415.1 | 44.4 | 19.9 | 81.8 | 18 | 264.1 | 38.3 | 710.3 | 609.3 | 589.7 | 689.9 | 569.4 | 541 | 777.6 | 446.3 | 625.3 | 497.5 | 102.3 | 162.8 | 205.6 | 173.3 | 265.6 | 260.3 | 162.6 | 238.1 | 275.7 | 219.8
1727.3 | 1508.3 | 466 | 186.4 | 217.8909 | 259.7 | 235.9 | 245.3 | 247.8 | 415 | 44.3 | 19.9 | 81.7 | 16.9 | 265.7 | 35.5 | 711.7 | 625 | 603.1 | 691.5 | 570.4 | 541.2 | 778.3 | 449.2 | 628.2 | 497.9 | 102.4 | 162.9 | 205.7 | 173.4 | 265.3 | 260.2 | 162.7 | 238.2 | 275.8 | 219.9
1728.3 | 1509.3 | 466.3 | 186.52 | 218.0311 | 260.4 | 235 | 245.7 | 247.1 | 413.6 | 44.3 | 20 | 81.8 | 14.3 | 263.6 | 32.6 | 708.5 | 607.2 | 590.7 | 689.6 | 568.1 | 541.5 | 769.8 | 443.3 | 628.7 | 496.4 | 102.6 | 163.1 | 205.8 | 173.5 | 265.1 | 259.8 | 162.8 | 238.2 | 275.9 | 220
1729.3 | 1510.3 | 467.3 | 186.92 | 218.4987 | 259.8 | 234.9 | 246.3 | 247.6 | 410.9 | 44.1 | 19.9 | 81.6 | 13.6 | 263 | 30 | 704.9 | 594.7 | 579.7 | 686.1 | 565.6 | 541.5 | 761.6 | 442.4 | 632.2 | 495 | 102.7 | 163.2 | 205.9 | 173.6 | 266 | 259.8 | 162.9 | 238.2 | 276 | 220.1
1730.3 | 1511.3 | 467.5 | 187 | 218.5922 | 259.1 | 234.2 | 246.3 | 247.8 | 413 | 43.9 | 19.9 | 81.4 | 12.2 | 267.5 | 27.3 | 701.4 | 589.5 | 576.9 | 681.4 | 564.1 | 541.9 | 758.4 | 435.5 | 631.3 | 493.9 | 102.8 | 163.3 | 205.9 | 173.7 | 266.6 | 260.3 | 163.1 | 238.3 | 276 | 220.3
1731.3 | 1512.3 | 467.3 | 186.92 | 218.4987 | 258.5 | 233.8 | 246.1 | 247.9 | 413.1 | 43.8 | 19.9 | 81.3 | 11.4 | 267.4 | 23.4 | 701.9 | 586.6 | 584 | 681.6 | 564.9 | 542.2 | 764.1 | 434.8 | 634.1 | 494.1 | 102.9 | 163.4 | 206 | 173.8 | 266.9 | 260.1 | 163.2 | 238.3 | 276 | 220.4
1732.3 | 1513.3 | 467.3 | 186.92 | 218.4987 | 259 | 233.8 | 245.3 | 248.2 | 414.1 | 43.7 | 19.9 | 81.3 | 11 | 266.2 | 20.4 | 700.9 | 599.2 | 584.2 | 678.7 | 564.7 | 542.3 | 763.2 | 434.8 | 634.4 | 493.4 | 103 | 163.5 | 206.1 | 173.8 | 266.8 | 259.8 | 163.3 | 238.3 | 276.1 | 220.5
1733.3 | 1514.3 | 467.2 | 186.88 | 218.452 | 260.7 | 233.9 | 245 | 248.5 | 412 | 43.7 | 19.9 | 81.3 | 10.4 | 273.1 | 19.4 | 697.3 | 585.5 | 573.2 | 673.8 | 563 | 542.1 | 768.2 | 438.2 | 633 | 493.1 | 103.1 | 163.7 | 206.2 | 173.9 | 266.6 | 259.6 | 163.4 | 238.3 | 276.2 | 220.6
1734.3 | 1515.3 | 466.9 | 186.76 | 218.3117 | 263.2 | 233.9 | 244.1 | 248.5 | 408 | 43.8 | 19.9 | 81.2 | 9.7 | 266.6 | 17.8 | 690.5 | 561.1 | 561.8 | 668.3 | 560 | 541.6 | 760.6 | 426.7 | 633.8 | 491.6 | 103.2 | 163.8 | 206.3 | 174 | 266.4 | 259.4 | 163.5 | 238.3 | 276.2 | 220.7
1735.3 | 1516.3 | 467.1 | 186.84 | 218.4052 | 264.2 | 233.1 | 243.7 | 248.6 | 401.4 | 43.8 | 19.9 | 81.1 | 10.5 | 271.1 | 16.9 | 685.4 | 552.4 | 568.2 | 661.4 | 558.6 | 541.3 | 753 | 419.2 | 635.4 | 490.6 | 103.3 | 163.9 | 206.4 | 174.1 | 266.3 | 259.1 | 163.6 | 238.3 | 276.3 | 220.8
1736.3 | 1517.3 | 466.8 | 186.72 | 218.2649 | 264.3 | 233.2 | 243.8 | 248.4 | 397.2 | 43.8 | 19.9 | 81 | 11.2 | 298.1 | 14.4 | 684.6 | 569.5 | 579.8 | 661.4 | 559.1 | 541.9 | 758.9 | 419.8 | 636.1 | 490.3 | 103.4 | 164 | 206.4 | 174.1 | 266.9 | 258.9 | 163.7 | 238.3 | 276.3 | 220.8
1737.3 | 1518.3 | 469 | 187.6 | 219.2936 | 265.1 | 233.5 | 244.3 | 248.1 | 398.5 | 43.7 | 19.9 | 81.1 | 9.7 | 281.2 | 11.6 | 686.3 | 589.7 | 589.4 | 664.2 | 558.3 | 542.5 | 764.7 | 430.5 | 642.4 | 490.8 | 103.5 | 164.1 | 206.5 | 174.2 | 266.7 | 258.8 | 163.8 | 238.3 | 276.3 | 221
1738.3 | 1519.3 | 468.5 | 187.4 | 219.0598 | 266 | 233 | 243.8 | 248.8 | 406.9 | 43.5 | 19.9 | 81.1 | 8.8 | 275 | 10.6 | 694.2 | 634.2 | 622.1 | 676.3 | 561 | 543 | 769.7 | 458.8 | 644 | 493.5 | 103.6 | 164.2 | 206.7 | 174.3 | 266.5 | 258.4 | 163.9 | 238.3 | 276.3 | 221
1739.3 | 1520.3 | 467.7 | 187.08 | 218.6857 | 265.1 | 232.4 | 243.8 | 249 | 424.2 | 43.2 | 19.9 | 81.1 | 8.9 | 273.6 | 10.6 | 699.4 | 660.6 | 632.9 | 682.8 | 564.3 | 543.3 | 770.8 | 478.7 | 642.8 | 498.4 | 103.7 | 164.4 | 206.8 | 174.4 | 266.3 | 258.1 | 164.1 | 238.4 | 276.4 | 221.1
1740.3 | 1521.3 | 468.2 | 187.28 | 218.9195 | 263 | 232.4 | 244.8 | 248.3 | 443.8 | 42.9 | 19.9 | 81.2 | 8.9 | 282.9 | 14.7 | 701.7 | 670.4 | 634 | 680.7 | 564.1 | 543.6 | 764.9 | 499.5 | 640.4 | 497.7 | 103.8 | 164.5 | 207.1 | 174.5 | 266.7 | 258 | 164.2 | 238.3 | 276.5 | 221.2
1741.3 | 1522.3 | 466.9 | 186.76 | 218.3117 | 261.4 | 232.2 | 246.2 | 247.3 | 448.3 | 42.5 | 19.9 | 81.2 | 10.9 | 277.7 | 17.7 | 701.9 | 678.4 | 620.6 | 677.6 | 561.9 | 544 | 760.6 | 501.9 | 640.6 | 497 | 103.9 | 164.6 | 207.2 | 174.5 | 266.6 | 257.7 | 164.3 | 238.2 | 276.7 | 221.3
1742.3 | 1523.3 | 466 | 186.4 | 217.8909 | 260.8 | 232.1 | 247.7 | 247.4 | 452.5 | 42.2 | 19.9 | 81.3 | 10.9 | 274.9 | 17.9 | 700.6 | 688.2 | 607.9 | 673.9 | 559.9 | 544.2 | 768.4 | 513.9 | 641.5 | 496.4 | 104 | 164.7 | 207.9 | 174.6 | 266.7 | 257.6 | 164.4 | 238.1 | 276.8 | 221.4
1743.3 | 1524.3 | 466 | 186.4 | 217.8909 | 260.9 | 232.2 | 250.1 | 248.2 | 464.5 | 41.9 | 19.9 | 81.2 | 10.1 | 284.1 | 17.6 | 702.9 | 708.6 | 616.1 | 674.9 | 560 | 544.3 | 780.3 | 534.7 | 642.3 | 497.2 | 104.1 | 164.8 | 208 | 174.6 | 266.8 | 257.3 | 164.5 | 238.2 | 277 | 221.5
1744.3 | 1525.3 | 466.2 | 186.48 | 217.9844 | 261.3 | 232.7 | 252.3 | 248.3 | 497.5 | 41.7 | 19.9 | 81.2 | 9.7 | 281.2 | 15.2 | 710 | 732 | 627 | 683.7 | 561.5 | 544.6 | 785.5 | 567.5 | 641.3 | 502.5 | 104.3 | 164.9 | 207.9 | 174.7 | 267.6 | 257.1 | 164.6 | 238.2 | 277.1 | 221.6
1745.3 | 1526.3 | 466.4 | 186.56 | 218.0779 | 261.2 | 234.3 | 254.3 | 250.7 | 494.1 | 41.5 | 19.9 | 81 | 10 | 269.9 | 13.7 | 712.8 | 733.6 | 631.8 | 683 | 561.8 | 544.9 | 785.4 | 561.1 | 636.8 | 502.3 | 104.4 | 165 | 207.8 | 174.8 | 268 | 257.2 | 164.7 | 238.2 | 277.2 | 221.7
1746.3 | 1527.3 | 466.5 | 186.6 | 218.1246 | 261.2 | 236.3 | 255 | 251.5 | 491.7 | 41.2 | 19.9 | 80.8 | 10.2 | 276.5 | 13.9 | 711.9 | 720 | 623.4 | 680.9 | 561.7 | 545.2 | 775.2 | 550.8 | 636.3 | 501.7 | 104.5 | 165.1 | 207.8 | 174.8 | 268.4 | 257.5 | 164.8 | 238.3 | 277.3 | 221.8
1747.3 | 1528.3 | 466.6 | 186.64 | 218.1714 | 260.9 | 237.9 | 255.1 | 252.2 | 480.8 | 41.2 | 19.9 | 80.7 | 9.8 | 278.9 | 13.1 | 706.7 | 685.9 | 603.8 | 676.8 | 559.8 | 545.2 | 767.1 | 532.6 | 633.8 | 500.5 | 104.6 | 165.2 | 207.8 | 174.9 | 268.6 | 257.3 | 165 | 238.3 | 277.4 | 222
1748.3 | 1529.3 | 465 | 186 | 217.4233 | 261.2 | 238.6 | 254.5 | 252.6 | 462.6 | 41.3 | 19.9 | 80.7 | 9.1 | 269.7 | 12.2 | 700.8 | 655.7 | 594.5 | 670.8 | 557.9 | 545.2 | 757.2 | 515.3 | 636.6 | 498.6 | 104.7 | 165.4 | 207.8 | 174.9 | 268.4 | 257.2 | 165.1 | 238.3 | 277.4 | 222
1749.3 | 1530.3 | 466 | 186.4 | 217.8909 | 261.9 | 238.1 | 252.8 | 252.1 | 447.2 | 41.4 | 19.9 | 80.6 | 9.5 | 268.2 | 12.4 | 701.6 | 653.6 | 592.5 | 672.4 | 558.6 | 545.6 | 759 | 511.3 | 638.2 | 499.1 | 104.8 | 165.5 | 208.1 | 175 | 267.8 | 257.4 | 165.1 | 238.3 | 277.5 | 222.1
1750.3 | 1531.3 | 466.2 | 186.48 | 217.9844 | 262.1 | 238.4 | 252.6 | 250.6 | 445.5 | 41.5 | 19.9 | 80.8 | 9.9 | 276.6 | 11.9 | 705.1 | 657.2 | 603.5 | 675.4 | 559.9 | 546.1 | 766.4 | 508.6 | 635.6 | 499.9 | 104.9 | 165.6 | 208.2 | 175.1 | 268.5 | 257.3 | 165.3 | 238.4 | 277.5 | 222.2
1751.3 | 1532.3 | 465.7 | 186.28 | 217.7506 | 262.1 | 238.8 | 252 | 249.2 | 442.5 | 41.8 | 19.9 | 81 | 9.2 | 269.3 | 11.2 | 708.8 | 661.3 | 607.6 | 679.3 | 560.7 | 546.3 | 763.1 | 503.7 | 634.9 | 500 | 105 | 165.7 | 208.3 | 175.1 | 268.5 | 257.4 | 165.4 | 238.4 | 277.6 | 222.3
1752.3 | 1533.3 | 466.4 | 186.56 | 218.0779 | 261.6 | 238.4 | 250.9 | 247.5 | 440.8 | 42.1 | 19.9 | 81.2 | 10 | 274.8 | 10.1 | 706.2 | 647.3 | 597.6 | 676.3 | 558.7 | 546.5 | 758.1 | 493.4 | 633.8 | 498.5 | 105.1 | 165.8 | 208.2 | 175.2 | 268.1 | 257.7 | 165.5 | 238.4 | 277.7 | 222.4
1753.3 | 1534.3 | 465 | 186 | 217.4233 | 261 | 238.4 | 250.8 | 247.4 | 437.9 | 42.4 | 19.9 | 81.3 | 9.5 | 276.9 | 9.8 | 704.1 | 658 | 601 | 671 | 558.7 | 547 | 760.2 | 492 | 636.9 | 498.8 | 105.2 | 166 | 208.3 | 175.2 | 267.6 | 258 | 165.6 | 238.5 | 277.8 | 222.5
1754.3 | 1535.3 | 466.3 | 186.52 | 218.0311 | 260.8 | 238.8 | 250.7 | 247.4 | 435.9 | 42.6 | 19.9 | 81.3 | 9.2 | 282.1 | 9.1 | 699.2 | 635.5 | 589.8 | 668.9 | 556.3 | 547 | 762.1 | 482.6 | 635.2 | 497.8 | 105.3 | 166.1 | 208.3 | 175.3 | 267.1 | 258.1 | 165.7 | 238.6 | 277.9 | 222.6
1755.3 | 1536.3 | 465.6 | 186.24 | 217.7038 | 260.9 | 238.2 | 249.3 | 246.5 | 425.8 | 42.7 | 19.9 | 81.3 | 9.1 | 281.4 | 9.5 | 698.9 | 636.2 | 590.1 | 667.7 | 555 | 546.9 | 766 | 475.9 | 634.9 | 496.4 | 105.4 | 166.2 | 208.4 | 175.4 | 266.3 | 258.3 | 165.8 | 238.6 | 277.9 | 222.6
1756.3 | 1537.3 | 467.6 | 187.04 | 218.639 | 260.6 | 237.7 | 248.1 | 245.3 | 427.1 | 42.7 | 19.9 | 81.3 | 9.8 | 282 | 9.5 | 704.4 | 663.6 | 618.2 | 675.6 | 557.3 | 547 | 771.9 | 489.4 | 637.3 | 496.9 | 105.5 | 166.3 | 208.6 | 175.4 | 265.9 | 258.3 | 165.9 | 238.6 | 278 | 222.7
1757.3 | 1538.3 | 467.9 | 187.16 | 218.7793 | 260.3 | 236.9 | 248.1 | 244 | 442 | 42.7 | 19.9 | 81.4 | 9.6 | 260.7 | 9.3 | 712.1 | 687.9 | 651.7 | 689.4 | 561.3 | 547.2 | 776.7 | 509.2 | 636.6 | 501.9 | 105.6 | 166.4 | 208.6 | 175.5 | 265.4 | 258 | 166 | 238.5 | 278.1 | 222.7
1758.3 | 1539.3 | 467.8 | 187.12 | 218.7325 | 259.7 | 235.7 | 248.1 | 244.6 | 452.6 | 42.7 | 19.9 | 81.4 | 9.7 | 279.2 | 8.5 | 719 | 687.1 | 665.8 | 701.5 | 564 | 547.3 | 768.9 | 510.3 | 630.2 | 505.9 | 105.7 | 166.5 | 208.7 | 175.5 | 265.2 | 257.8 | 166.1 | 238.6 | 278.2 | 222.8
1759.3 | 1540.3 | 467.8 | 187.12 | 218.7325 | 259.8 | 235.8 | 247.6 | 245.7 | 453.4 | 42.7 | 19.9 | 81.4 | 10.2 | 261.3 | 8.4 | 718.7 | 659.8 | 652 | 699.9 | 561.3 | 547.1 | 760.1 | 499.6 | 632 | 504.3 | 105.8 | 166.6 | 208.8 | 175.6 | 265.2 | 257.6 | 166.2 | 238.6 | 278.4 | 222.9
1760.3 | 1541.3 | 467.7 | 187.08 | 218.6857 | 260.5 | 235.1 | 247.3 | 247.4 | 449 | 42.8 | 19.9 | 81.5 | 9.1 | 273.7 | 10.1 | 717.2 | 646.8 | 651.8 | 698.8 | 559.9 | 547.3 | 761.5 | 492 | 637.4 | 503 | 105.9 | 166.7 | 208.9 | 175.7 | 265.5 | 257.4 | 166.4 | 238.6 | 278.5 | 223
1761.3 | 1542.3 | 467.3 | 186.92 | 218.4987 | 260.7 | 234.4 | 247.1 | 249.3 | 439.4 | 42.8 | 19.9 | 81.5 | 8.9 | 266.4 | 10.9 | 715.3 | 642 | 652.9 | 697.8 | 559.3 | 547.6 | 764.3 | 482.1 | 637.1 | 502.6 | 106 | 166.8 | 208.9 | 175.7 | 265.6 | 257.8 | 166.4 | 238.8 | 278.6 | 223.1
1762.3 | 1543.3 | 467.4 | 186.96 | 218.5455 | 261 | 234 | 246.4 | 249.9 | 434.7 | 42.9 | 19.9 | 81.5 | 10 | 268.3 | 11.3 | 715.9 | 655.3 | 665.2 | 701.6 | 560.9 | 548 | 770.5 | 474.7 | 636.1 | 503 | 106.1 | 166.8 | 209 | 175.8 | 265.4 | 258.4 | 166.5 | 239 | 278.6 | 223.3
1763.3 | 1544.3 | 468.1 | 187.24 | 218.8728 | 261.1 | 232.4 | 247.1 | 250 | 439.5 | 42.9 | 19.9 | 81.4 | 9.6 | 270.9 | 11.8 | 718 | 661.3 | 666.7 | 704.3 | 559.9 | 548.2 | 767.7 | 483.7 | 635.8 | 503.2 | 106.2 | 166.9 | 209.1 | 175.9 | 265.1 | 258.4 | 166.6 | 239 | 278.7 | 223.3
1764.3 | 1545.3 | 467.9 | 187.16 | 218.7793 | 261.4 | 231.4 | 248.4 | 248.7 | 446.5 | 42.8 | 19.9 | 81.5 | 10.6 | 268.8 | 13.2 | 717.8 | 656.9 | 669.9 | 702.7 | 559.6 | 548.6 | 761.3 | 481.5 | 635.3 | 502.1 | 106.3 | 167 | 209.3 | 175.9 | 265.2 | 258.4 | 166.8 | 239 | 278.8 | 223.4
1765.3 | 1546.3 | 468 | 187.2 | 218.826 | 261.3 | 232.9 | 249.9 | 247.6 | 447.4 | 42.7 | 19.9 | 81.6 | 10.5 | 269.3 | 13.2 | 718.7 | 660.5 | 651 | 703.1 | 559.2 | 549 | 759.7 | 480 | 636.2 | 501.1 | 106.4 | 167.1 | 209.5 | 176 | 265.8 | 258.2 | 166.8 | 238.9 | 278.9 | 223.5
1766.3 | 1547.3 | 467.7 | 187.08 | 218.6857 | 261.5 | 234.2 | 250.9 | 247.3 | 440.6 | 42.7 | 19.9 | 81.7 | 9.4 | 276.1 | 12.6 | 715.1 | 639.9 | 633.1 | 698 | 557 | 549.1 | 754.8 | 474.3 | 633.1 | 499.7 | 106.5 | 167.2 | 209.4 | 176.1 | 266.2 | 257.9 | 167 | 238.9 | 279 | 223.6
1767.3 | 1548.3 | 467.9 | 187.16 | 218.7793 | 261.9 | 234.1 | 251.1 | 248.1 | 434 | 42.7 | 19.9 | 81.7 | 9.9 | 269.6 | 12.1 | 710.2 | 612.1 | 617.6 | 692.2 | 555.5 | 549.3 | 753.7 | 463.8 | 632.1 | 498 | 106.6 | 167.3 | 209.3 | 176.2 | 266.2 | 257.6 | 167.1 | 238.9 | 279.1 | 223.7
1768.3 | 1549.3 | 468.7 | 187.48 | 219.1533 | 262.1 | 234.3 | 249.5 | 248.3 | 423.6 | 42.8 | 19.9 | 81.6 | 9.2 | 270.6 | 11.9 | 705.6 | 595 | 602.9 | 685.8 | 553.4 | 549.4 | 745.9 | 453.6 | 634.5 | 496.5 | 106.7 | 167.4 | 209.3 | 176.2 | 267 | 257.4 | 167.2 | 238.9 | 279.1 | 223.8
1769.3 | 1550.3 | 466.6 | 186.64 | 218.1714 | 261.7 | 233.9 | 247.3 | 249.4 | 422.6 | 42.9 | 19.9 | 81.6 | 9.7 | 276.5 | 11.5 | 706.1 | 601.3 | 606.7 | 684.1 | 552.8 | 549.8 | 742.8 | 457 | 637.2 | 496.7 | 106.8 | 167.5 | 209.5 | 176.3 | 267.1 | 257.6 | 167.3 | 238.9 | 279.2 | 224
1770.3 | 1551.3 | 466.1 | 186.44 | 217.9376 | 261.6 | 232.9 | 245.6 | 249.8 | 427.7 | 43 | 19.9 | 81.7 | 9.3 | 252.1 | 11.1 | 709.3 | 600.6 | 599.3 | 690.1 | 551.9 | 550.2 | 746.2 | 456.8 | 633 | 497.6 | 107 | 167.6 | 209.5 | 176.4 | 267.2 | 257.9 | 167.4 | 238.9 | 279.3 | 224.1
1771.3 | 1552.3 | 466.1 | 186.44 | 217.9376 | 261.8 | 232.2 | 244.1 | 248.7 | 425.4 | 43.2 | 19.9 | 81.8 | 9.2 | 258.5 | 11.1 | 706.6 | 595.8 | 590.3 | 688.2 | 550.7 | 550.4 | 742.3 | 451.2 | 628.5 | 496.3 | 107.1 | 167.7 | 209.6 | 176.5 | 267.9 | 258.3 | 167.5 | 239 | 279.4 | 224.2
1772.3 | 1553.3 | 466.2 | 186.48 | 217.9844 | 262.3 | 232.4 | 243.5 | 247.8 | 415.1 | 43.3 | 19.9 | 81.9 | 8.4 | 245.5 | 10.5 | 703.9 | 584.8 | 597.1 | 684.6 | 550.3 | 550.7 | 739.3 | 442.9 | 629.5 | 495.9 | 107.2 | 167.8 | 209.7 | 176.5 | 267.6 | 259 | 167.6 | 239.2 | 279.5 | 224.3
1773.3 | 1554.3 | 465.3 | 186.12 | 217.5636 | 263.3 | 232.1 | 243.4 | 247.7 | 408.3 | 43.4 | 19.9 | 82 | 8.6 | 253.3 | 8.8 | 705 | 590.8 | 597.9 | 686.7 | 549.5 | 551.1 | 741.9 | 441.6 | 629.1 | 495.5 | 107.3 | 167.9 | 209.8 | 176.6 | 267.5 | 259.2 | 167.7 | 239.2 | 279.5 | 224.4
1774.3 | 1555.3 | 467.8 | 187.12 | 218.7325 | 264.3 | 231.1 | 243.8 | 248.4 | 405 | 43.5 | 19.9 | 82.1 | 9.4 | 261.8 | 9.7 | 703.4 | 585 | 586.9 | 684.7 | 548.5 | 551.4 | 740.4 | 437.1 | 631.7 | 494.7 | 107.4 | 168 | 209.9 | 176.7 | 267.6 | 259.1 | 167.8 | 239.3 | 279.6 | 224.5
1775.3 | 1556.3 | 469 | 187.6 | 219.2936 | 264.2 | 230.4 | 244.2 | 248.1 | 398.8 | 43.5 | 19.9 | 82.2 | 9.5 | 264.4 | 11 | 701.4 | 587.9 | 578.2 | 682.3 | 547 | 551.6 | 739.1 | 434.8 | 632.3 | 494 | 107.5 | 168.1 | 209.9 | 176.7 | 267.8 | 258.9 | 167.9 | 239.3 | 279.7 | 224.6
1776.3 | 1557.3 | 469.7 | 187.88 | 219.6209 | 264.7 | 230.6 | 244.6 | 247.8 | 394.1 | 43.4 | 19.9 | 82.3 | 9.6 | 252.5 | 12.5 | 697.1 | 578.3 | 570.6 | 678.1 | 545.2 | 551.8 | 737.8 | 428.7 | 635.8 | 492.7 | 107.6 | 168.2 | 209.9 | 176.8 | 267.9 | 258.9 | 168 | 239.3 | 279.7 | 224.7
1777.3 | 1558.3 | 467.2 | 186.88 | 218.452 | 265.9 | 231 | 244 | 247.9 | 391.6 | 43.2 | 19.9 | 82.4 | 10.5 | 263.4 | 12.9 | 693.7 | 574.8 | 561 | 673.7 | 543.2 | 551.9 | 739.4 | 425.5 | 636.6 | 491.2 | 107.7 | 168.3 | 209.9 | 176.9 | 268 | 258.8 | 168.1 | 239.3 | 279.7 | 224.7
1778.3 | 1559.3 | 466 | 186.4 | 217.8909 | 265.8 | 230.6 | 244.8 | 248 | 391.6 | 43.1 | 19.9 | 82.4 | 11.7 | 261.4 | 12.4 | 691.2 | 566.9 | 549.9 | 670.7 | 541.3 | 552.1 | 739.6 | 421.4 | 639 | 490.4 | 107.8 | 168.4 | 210 | 177 | 267.8 | 258.8 | 168.2 | 239.4 | 279.8 | 224.8
1779.3 | 1560.3 | 466.6 | 186.64 | 218.1714 | 265.3 | 230.3 | 246.1 | 248.1 | 386.9 | 42.9 | 19.9 | 82.4 | 11.3 | 270.6 | 11.6 | 687.9 | 566.8 | 552 | 666.8 | 540.1 | 552.4 | 734.7 | 419.2 | 639.7 | 489.8 | 107.9 | 168.4 | 210.3 | 177 | 267.6 | 258.6 | 168.3 | 239.4 | 279.8 | 224.9
1780.3 | 1561.3 | 470.4 | 188.16 | 219.9482 | 263.8 | 230.9 | 245.8 | 247.8 | 386.2 | 42.8 | 19.9 | 82.4 | 10.3 | 256.9 | 11.3 | 688.1 | 594.5 | 570.7 | 665.1 | 540.8 | 552.8 | 740.7 | 424.5 | 640.1 | 489.6 | 108 | 168.5 | 210.3 | 177.1 | 267.1 | 258.2 | 168.4 | 239.4 | 279.8 | 225
1781.3 | 1562.3 | 479.5 | 191.8 | 224.2031 | 263.1 | 231.9 | 245.8 | 246.9 | 392.2 | 42.7 | 19.9 | 82.4 | 10 | 261.8 | 14 | 692.6 | 632.9 | 607.7 | 667.8 | 544.2 | 553.4 | 746.3 | 437.9 | 640.1 | 491.6 | 108.1 | 168.6 | 210.3 | 177.2 | 266.5 | 258.1 | 168.5 | 239.4 | 279.8 | 225
1782.3 | 1563.3 | 473.3 | 189.32 | 221.3042 | 262.8 | 232.8 | 245.9 | 246.3 | 402.7 | 42.7 | 19.9 | 82.4 | 9.2 | 244.1 | 13.8 | 696.6 | 641 | 627.2 | 669.8 | 547.4 | 554.1 | 752.7 | 439.7 | 639.9 | 494 | 108.2 | 168.7 | 210.3 | 177.3 | 265.9 | 259.1 | 168.6 | 239.5 | 279.8 | 225.1
1783.3 | 1564.3 | 486.2 | 194.48 | 227.3359 | 262.3 | 232.8 | 245.3 | 247.7 | 407.5 | 42.7 | 19.9 | 82.4 | 8.4 | 242.6 | 12.8 | 697.9 | 635.5 | 618.7 | 671.6 | 547 | 554.5 | 751.9 | 439.5 | 641.4 | 493.5 | 108.3 | 168.8 | 210.5 | 177.3 | 265.2 | 259.8 | 168.7 | 239.6 | 279.9 | 225.2
1784.3 | 1565.3 | 511.3 | 204.52 | 239.0721 | 262.2 | 233.3 | 245.3 | 248.1 | 403.1 | 42.8 | 19.9 | 82.5 | 7.8 | 250 | 15.9 | 696.5 | 631.1 | 604.4 | 669.4 | 545.4 | 554.7 | 746.8 | 433.6 | 641 | 491.8 | 108.4 | 168.9 | 210.5 | 177.4 | 264.9 | 259.7 | 168.8 | 239.6 | 280 | 225.2
1785.3 | 1566.3 | 522.2 | 208.88 | 244.1687 | 262.3 | 233.5 | 246 | 247.8 | 401.9 | 42.8 | 19.9 | 82.6 | 8.6 | 245.8 | 15.8 | 693.7 | 623.9 | 596.4 | 666.1 | 544.5 | 554.9 | 742.2 | 431.6 | 641.1 | 490.8 | 108.5 | 169 | 210.6 | 177.5 | 264.6 | 259.5 | 168.9 | 239.6 | 280 | 225.3
1786.3 | 1567.3 | 525.7 | 210.28 | 245.8052 | 262.6 | 233.4 | 246 | 248 | 399.8 | 42.8 | 19.9 | 82.7 | 9.5 | 242.8 | 12.5 | 694.1 | 623.8 | 612.8 | 664.5 | 545.8 | 555.5 | 742.2 | 427.5 | 640 | 489.7 | 108.6 | 169.1 | 210.8 | 177.6 | 264.1 | 259.2 | 169 | 239.5 | 280.1 | 225.4
1787.3 | 1568.3 | 527.5 | 211 | 246.6468 | 262.8 | 232.8 | 247.5 | 247.8 | 404.9 | 42.9 | 19.9 | 82.7 | 8.8 | 249.5 | 10.4 | 698.3 | 624.2 | 627 | 668.7 | 549.1 | 556.4 | 740.5 | 431.9 | 639.5 | 491.7 | 108.7 | 169.1 | 210.9 | 177.6 | 263.8 | 259 | 169.1 | 239.6 | 280.1 | 225.4
1788.3 | 1569.3 | 529 | 211.6 | 247.3482 | 263 | 232.6 | 247.9 | 245.8 | 410.5 | 43.1 | 19.9 | 83 | 9.8 | 245 | 11.3 | 699.3 | 629.8 | 628.4 | 670.7 | 547.8 | 557 | 742.6 | 435.2 | 642.4 | 491.1 | 108.8 | 169.2 | 210.9 | 177.7 | 263.5 | 258.6 | 169.3 | 239.6 | 280.2 | 225.5
1789.3 | 1570.3 | 529.9 | 211.96 | 247.769 | 262.7 | 232.1 | 247.3 | 245.1 | 413.8 | 43.2 | 19.9 | 83.1 | 8.5 | 253.1 | 11.8 | 697.2 | 624.2 | 615.1 | 667.7 | 546.4 | 557.5 | 739.9 | 436 | 637.1 | 490.1 | 108.9 | 169.3 | 211 | 177.8 | 263.9 | 258.4 | 169.3 | 239.5 | 280.3 | 225.6
1790.3 | 1571.3 | 529.1 | 211.64 | 247.395 | 262.9 | 231.7 | 246.9 | 245.1 | 409.2 | 43.3 | 19.9 | 83.1 | 8 | 246.2 | 13.4 | 692.7 | 616.5 | 600.9 | 664.6 | 544.5 | 557.8 | 743.4 | 431.1 | 636.6 | 489.1 | 109 | 169.4 | 211 | 177.8 | 264.1 | 258.5 | 169.4 | 239.6 | 280.3 | 225.7
1791.3 | 1572.3 | 528.3 | 211.32 | 247.0209 | 263 | 232.4 | 246.3 | 245.5 | 401.6 | 43.4 | 19.9 | 83.1 | 8.8 | 254.5 | 12.8 | 693.3 | 627.9 | 605 | 665.6 | 544.8 | 558.3 | 738.4 | 434.9 | 638.1 | 488.9 | 109.1 | 169.4 | 211 | 177.9 | 264.7 | 258.6 | 169.5 | 239.7 | 280.4 | 225.8
1792.3 | 1573.3 | 529.9 | 211.96 | 247.769 | 263.6 | 232.7 | 246.4 | 246.1 | 402.2 | 43.5 | 19.9 | 83.2 | 7.7 | 262.8 | 14 | 697.8 | 631.6 | 604.5 | 670.6 | 544.8 | 559.1 | 735.2 | 438.4 | 637.6 | 489.5 | 109.3 | 169.5 | 211.1 | 178 | 264.7 | 259.5 | 169.6 | 239.7 | 280.5 | 225.9
1793.3 | 1574.3 | 529.7 | 211.88 | 247.6755 | 264.3 | 232.2 | 245.9 | 246.4 | 408.9 | 43.6 | 19.9 | 83.2 | 7.2 | 261.2 | 13.7 | 700.5 | 649.2 | 604.1 | 673.5 | 545.1 | 559.8 | 741 | 453.5 | 640 | 490.9 | 109.4 | 169.6 | 211.3 | 178.1 | 264.9 | 260.6 | 169.7 | 239.8 | 280.5 | 225.9
1794.3 | 1575.3 | 530.1 | 212.04 | 247.8625 | 264.2 | 232.2 | 245.8 | 245.7 | 420.8 | 43.7 | 19.9 | 83.3 | 7 | 254.8 | 12.7 | 702.1 | 651.2 | 611.8 | 676.3 | 545.5 | 560.5 | 738.6 | 455.3 | 639.9 | 491.8 | 109.5 | 169.7 | 211.4 | 178.1 | 264.9 | 260.9 | 169.8 | 239.9 | 280.6 | 226
1795.3 | 1576.3 | 529.9 | 211.96 | 247.769 | 264.2 | 232.7 | 247.2 | 246.3 | 416.2 | 43.8 | 19.9 | 83.3 | 7.8 | 263.2 | 12.1 | 700.7 | 645.4 | 611 | 674.2 | 545.1 | 561.4 | 740.5 | 449.1 | 644.5 | 490.1 | 109.6 | 169.8 | 211.5 | 178.2 | 265.1 | 261 | 169.9 | 239.9 | 280.7 | 226.1
1796.3 | 1577.3 | 530.5 | 212.2 | 248.0496 | 264.2 | 233.4 | 247.6 | 247.3 | 411.5 | 43.9 | 19.9 | 83.4 | 8.8 | 263.2 | 11.5 | 697 | 633.4 | 602.8 | 670.4 | 543.3 | 562.3 | 738.9 | 443.4 | 643.7 | 489.2 | 109.7 | 169.9 | 211.7 | 178.3 | 265.8 | 260.8 | 170 | 240.1 | 280.8 | 226.2
1797.3 | 1578.3 | 531.2 | 212.48 | 248.3769 | 264.1 | 233.3 | 246.9 | 248.2 | 409.6 | 44.1 | 19.9 | 83.5 | 9.7 | 260.2 | 12.3 | 696.6 | 627.5 | 615.4 | 669.4 | 544.2 | 563.4 | 739.6 | 437.5 | 643.2 | 489.4 | 109.8 | 170 | 211.6 | 178.4 | 266.2 | 260.6 | 170.1 | 240.1 | 280.9 | 226.2
1798.3 | 1579.3 | 530.4 | 212.16 | 248.0028 | 264.1 | 233 | 246.6 | 249.5 | 404.4 | 44.2 | 19.9 | 83.6 | 8.9 | 250 | 13.2 | 698.7 | 643 | 630.1 | 673 | 546.2 | 564.5 | 745.9 | 444.1 | 642.8 | 490.5 | 109.9 | 170.1 | 211.8 | 178.5 | 266.4 | 260.4 | 170.2 | 240.1 | 280.9 | 226.3
1799.3 | 1580.3 | 531.8 | 212.72 | 248.6574 | 264.7 | 233.6 | 246 | 250.2 | 412 | 44.3 | 19.9 | 83.7 | 9.3 | 240.5 | 14.2 | 702.7 | 656.7 | 648.1 | 677.8 | 548.4 | 565.4 | 746.5 | 454.8 | 642.2 | 491.9 | 110 | 170.1 | 211.8 | 178.5 | 266.4 | 260.4 | 170.3 | 240.1 | 281 | 226.4
1800.3 | 1581.3 | 532.7 | 213.08 | 249.0782 | 265.2 | 233.7 | 246.1 | 250.5 | 419.4 | 44.4 | 19.9 | 83.9 | 9.2 | 257.9 | 13.8 | 706.7 | 659.9 | 659.8 | 685.5 | 549.6 | 566.3 | 742.1 | 452.5 | 637.5 | 493.8 | 110.1 | 170.2 | 211.9 | 178.6 | 267.1 | 260.6 | 170.4 | 240.2 | 281.1 | 226.5
1801.3 | 1582.3 | 533.4 | 213.36 | 249.4055 | 265.1 | 233.5 | 245.8 | 250.3 | 419.9 | 44.4 | 19.9 | 84 | 8.7 | 260.8 | 12.8 | 707.7 | 662.2 | 652 | 684.7 | 549.7 | 566.9 | 746.6 | 458.7 | 638.4 | 494.7 | 110.2 | 170.3 | 211.9 | 178.7 | 267.2 | 261.2 | 170.5 | 240.3 | 281.3 | 226.6
1802.3 | 1583.3 | 533.5 | 213.4 | 249.4523 | 265.1 | 233.8 | 244.9 | 249.9 | 427.3 | 44.5 | 19.9 | 84 | 8.8 | 244.2 | 11.8 | 708.4 | 667.5 | 649.9 | 684.2 | 550 | 567.9 | 751.2 | 462.2 | 641.9 | 495.1 | 110.3 | 170.4 | 212.1 | 178.8 | 267 | 262.3 | 170.6 | 240.5 | 281.4 | 226.7
1803.3 | 1584.3 | 533.1 | 213.24 | 249.2653 | 265.6 | 234.5 | 244.7 | 248.7 | 435 | 44.6 | 19.9 | 84 | 8.4 | 243.8 | 13.1 | 714.9 | 698.6 | 652.2 | 693.7 | 550.9 | 568.4 | 760.6 | 483.5 | 645.5 | 498.4 | 110.4 | 170.5 | 212.3 | 178.9 | 266.9 | 263.1 | 170.7 | 240.6 | 281.5 | 226.8
1804.3 | 1585.3 | 533.6 | 213.44 | 249.4991 | 265.3 | 235.4 | 245.8 | 247.6 | 446.9 | 44.7 | 19.8 | 84.2 | 8.2 | 240.8 | 13.2 | 716.7 | 704.1 | 640.3 | 693.2 | 549.7 | 568.7 | 759 | 486.3 | 649.7 | 497.7 | 110.5 | 170.5 | 212.6 | 179 | 267.1 | 264.3 | 170.8 | 240.7 | 281.6 | 226.9
1805.3 | 1586.3 | 533.8 | 213.52 | 249.5926 | 265.1 | 236.2 | 247.2 | 247 | 441.4 | 44.8 | 19.8 | 84.3 | 8.3 | 251.1 | 11.9 | 715.6 | 698.9 | 632.6 | 690.7 | 548.2 | 569.4 | 751.8 | 478.8 | 652.7 | 496.9 | 110.6 | 170.6 | 212.5 | 179.1 | 267.6 | 264.7 | 170.9 | 240.9 | 281.7 | 227
1806.3 | 1587.3 | 533.3 | 213.32 | 249.3588 | 265.1 | 235.5 | 248.4 | 246.9 | 437.5 | 44.8 | 19.8 | 84.4 | 7.5 | 252.2 | 11.5 | 717 | 702.8 | 644 | 693 | 549.2 | 570.2 | 748.6 | 479.9 | 652.8 | 497.6 | 110.7 | 170.7 | 212.7 | 179.2 | 267.9 | 264.9 | 171 | 241 | 281.7 | 227.1
1807.3 | 1588.3 | 532.8 | 213.12 | 249.125 | 265.4 | 235.4 | 249.2 | 246.9 | 435.6 | 44.8 | 19.8 | 84.4 | 8.2 | 258.1 | 13 | 719.4 | 698.8 | 662.7 | 696.4 | 551.7 | 571.1 | 750.3 | 481.6 | 655 | 498.2 | 110.8 | 170.7 | 212.9 | 179.2 | 268.1 | 264.6 | 171.1 | 241.1 | 281.8 | 227.2
1808.3 | 1589.3 | 533.3 | 213.32 | 249.3588 | 266.4 | 236 | 249.4 | 247.5 | 435 | 44.8 | 19.8 | 84.4 | 8.3 | 246.9 | 13.5 | 722.8 | 713.2 | 667.8 | 698.6 | 551.6 | 572 | 762 | 483.6 | 655.2 | 498.9 | 110.9 | 170.8 | 212.9 | 179.3 | 268.1 | 264.8 | 171.2 | 241.2 | 281.8 | 227.3
1809.3 | 1590.3 | 533.9 | 213.56 | 249.6393 | 267.2 | 236.8 | 249.7 | 248.8 | 434.4 | 44.8 | 19.8 | 84.5 | 8.9 | 266.7 | 12.9 | 720.7 | 707 | 666.9 | 696 | 553.6 | 572.7 | 767.1 | 486.5 | 657.4 | 501 | 111 | 170.9 | 213 | 179.4 | 268.4 | 264.7 | 171.3 | 241.2 | 281.9 | 227.4
1810.3 | 1591.3 | 533.4 | 213.36 | 249.4055 | 268.1 | 238 | 250.5 | 250.6 | 435.3 | 44.8 | 19.8 | 84.4 | 8.2 | 265.2 | 13.5 | 721.5 | 689.8 | 671.1 | 701.3 | 554.9 | 573.5 | 770.5 | 482.6 | 658.1 | 503 | 111.2 | 171 | 213.1 | 179.5 | 269.1 | 264.9 | 171.4 | 241.4 | 282 | 227.5
1811.3 | 1592.3 | 533.5 | 213.4 | 249.4523 | 268.2 | 239.4 | 252.5 | 251.3 | 433.5 | 44.8 | 19.8 | 84.4 | 8.2 | 267.2 | 13.4 | 723.1 | 673.9 | 670.5 | 708.5 | 555.2 | 574 | 780.3 | 487.7 | 658.8 | 508.4 | 111.3 | 171.1 | 213.4 | 179.7 | 271.2 | 265.7 | 171.5 | 241.6 | 282.2 | 227.6
1812.3 | 1593.3 | 534.2 | 213.68 | 249.7796 | 268.9 | 240.1 | 255.2 | 253.5 | 435.1 | 44.8 | 19.8 | 84.4 | 8.3 | 271.1 | 13.1 | 725.4 | 682.1 | 667.3 | 713.4 | 554.3 | 574.8 | 779.8 | 491.4 | 658.9 | 508.5 | 111.4 | 171.2 | 213.6 | 179.8 | 273.7 | 266.4 | 171.6 | 241.9 | 282.3 | 227.8
1813.3 | 1594.3 | 533.7 | 213.48 | 249.5458 | 270.7 | 241.2 | 258.7 | 256 | 436.9 | 44.8 | 19.8 | 84.3 | 8 | 262.3 | 13.2 | 729.6 | 695.8 | 653.5 | 721.7 | 554.6 | 575.4 | 778.1 | 498.8 | 657.5 | 509.9 | 111.5 | 171.2 | 213.6 | 179.9 | 274.6 | 267.3 | 171.7 | 242.1 | 282.5 | 228
1814.3 | 1595.3 | 534.7 | 213.88 | 250.0134 | 271.7 | 242 | 260.3 | 257.9 | 435.4 | 44.8 | 19.8 | 84.2 | 8.6 | 271.8 | 12.3 | 731.4 | 689.2 | 645 | 722.6 | 554.6 | 576 | 773.8 | 495.7 | 658.8 | 509.5 | 111.6 | 171.3 | 213.7 | 180 | 275.9 | 268.4 | 171.8 | 242.4 | 282.7 | 228.2
1815.3 | 1596.3 | 535 | 214 | 250.1537 | 272.3 | 243 | 261.2 | 259.1 | 431.4 | 44.8 | 19.8 | 84.1 | 7.7 | 248.8 | 10.6 | 729.1 | 677.6 | 642.8 | 720.5 | 554.2 | 576.6 | 772.8 | 488.6 | 660.7 | 509.1 | 111.7 | 171.4 | 213.8 | 180.1 | 276.3 | 269.2 | 171.9 | 242.7 | 282.8 | 228.3
1816.3 | 1597.3 | 534.8 | 213.92 | 250.0602 | 273.2 | 243.8 | 261.3 | 259.1 | 427.4 | 44.8 | 19.8 | 84 | 7.9 | 270.8 | 8.5 | 726.1 | 665.2 | 639.6 | 717.7 | 554.1 | 577.2 | 772 | 480.5 | 658.3 | 509.2 | 111.8 | 171.5 | 213.8 | 180.3 | 276.7 | 269.8 | 172 | 242.9 | 282.9 | 228.4
1817.3 | 1598.3 | 535.1 | 214.04 | 250.2004 | 274.3 | 244.9 | 261.4 | 258.4 | 419.7 | 44.8 | 19.8 | 84 | 8.4 | 269.1 | 8.1 | 727.1 | 659.5 | 660 | 720.1 | 555.9 | 578 | 778.2 | 473.9 | 657.5 | 510.2 | 111.9 | 171.6 | 213.9 | 180.4 | 277.2 | 270.2 | 172.1 | 243.1 | 283.1 | 228.6
1818.3 | 1599.3 | 535.6 | 214.24 | 250.4342 | 276.2 | 245.6 | 261.7 | 258.6 | 419 | 44.8 | 19.8 | 84 | 8.7 | 267.1 | 8 | 728.7 | 646.5 | 668.4 | 724 | 556.9 | 578.8 | 781.2 | 473.7 | 659.4 | 511.4 | 112 | 171.7 | 214 | 180.5 | 277.7 | 270.8 | 172.2 | 243.2 | 283.2 | 228.7
1819.3 | 1600.3 | 534.9 | 213.96 | 250.1069 | 278.1 | 246 | 262.9 | 260.3 | 418.1 | 44.9 | 19.8 | 84.1 | 8 | 276.7 | 7.5 | 727.7 | 638.9 | 656.4 | 724.1 | 554.6 | 579.6 | 781.3 | 471.3 | 659.2 | 511.9 | 112.1 | 171.8 | 214.3 | 180.7 | 278.4 | 271.2 | 172.3 | 243.4 | 283.3 | 228.8
1820.3 | 1601.3 | 536.2 | 214.48 | 250.7148 | 279.4 | 246.4 | 264.9 | 261.6 | 418.6 | 45 | 19.8 | 84.1 | 8.3 | 258 | 6.7 | 729.5 | 624.6 | 645.8 | 727.4 | 553.7 | 580.1 | 777 | 469.3 | 656.6 | 511.7 | 112.2 | 171.9 | 214.5 | 180.8 | 279 | 271.5 | 172.4 | 243.6 | 283.4 | 228.9
1821.3 | 1602.3 | 537.1 | 214.84 | 251.1356 | 279.2 | 247.4 | 266 | 263.3 | 425.3 | 45.1 | 19.8 | 84.1 | 8.5 | 253.5 | 5.8 | 731.7 | 631.9 | 648.4 | 729.8 | 555.2 | 580.9 | 776.5 | 473.8 | 657.4 | 512.4 | 112.3 | 172 | 214.5 | 181 | 279.6 | 271.5 | 172.5 | 243.9 | 283.5 | 229.1
1822.3 | 1603.3 | 536.4 | 214.56 | 250.8083 | 278.8 | 248.3 | 267.2 | 264.6 | 428.3 | 45.3 | 19.8 | 84.1 | 7.9 | 258.6 | 5.7 | 734.8 | 634.3 | 649.3 | 734.4 | 554.2 | 581.4 | 772.9 | 474.1 | 655.6 | 512.9 | 112.4 | 172.1 | 214.6 | 181.1 | 280 | 271.5 | 172.6 | 244 | 283.6 | 229.2
1823.3 | 1604.3 | 536.9 | 214.76 | 251.0421 | 279.6 | 248.9 | 268.1 | 263.9 | 426.5 | 45.3 | 19.8 | 84.1 | 9.6 | 227.3 | 5.1 | 737.2 | 652.2 | 653.1 | 736.6 | 553.3 | 582 | 773.4 | 477.9 | 654.9 | 513.5 | 112.5 | 172.2 | 214.7 | 181.3 | 280.3 | 271.8 | 172.7 | 244.2 | 283.7 | 229.3
1824.3 | 1605.3 | 537.5 | 215 | 251.3226 | 279.9 | 248.9 | 268.2 | 264 | 430.6 | 45.3 | 19.8 | 84.1 | 9 | 228.4 | 5.4 | 742.4 | 689 | 651.2 | 742.1 | 554 | 582.7 | 773.1 | 503.1 | 655.2 | 515.6 | 112.6 | 172.3 | 214.9 | 181.4 | 280.8 | 271.9 | 172.8 | 244.2 | 283.9 | 229.4
1825.3 | 1606.3 | 538.9 | 215.56 | 251.9772 | 280.4 | 248.3 | 267.1 | 264.7 | 439.2 | 45.4 | 19.8 | 84.1 | 9.7 | 249.5 | 6.8 | 744 | 688.8 | 652.2 | 740.1 | 553.9 | 583.5 | 770.9 | 496.3 | 654.8 | 516.1 | 112.7 | 172.4 | 215 | 181.6 | 281.3 | 272 | 172.9 | 244.3 | 284 | 229.6
1826.3 | 1607.3 | 539.8 | 215.92 | 252.398 | 280.4 | 248.6 | 265.5 | 265.2 | 437.6 | 45.4 | 19.8 | 84.1 | 10.3 | 242.8 | 8.3 | 741.8 | 680.6 | 658.9 | 733.5 | 553.7 | 584 | 764 | 491.7 | 656.8 | 515.3 | 112.8 | 172.5 | 215 | 181.7 | 282.1 | 272.3 | 173 | 244.4 | 284.1 | 229.7
1827.3 | 1608.3 | 538.7 | 215.48 | 251.8837 | 280 | 248.1 | 265.4 | 266.1 | 435.5 | 45.5 | 19.8 | 84.1 | 10.9 | 241 | 8.5 | 743.9 | 682.5 | 662.7 | 737.7 | 555.8 | 584.7 | 764.3 | 498 | 658.9 | 516.2 | 112.9 | 172.6 | 215.2 | 181.9 | 282.2 | 272.6 | 173.1 | 244.5 | 284.3 | 229.8
1828.3 | 1609.3 | 538.5 | 215.4 | 251.7902 | 279.8 | 247.5 | 266.4 | 266.6 | 437.6 | 45.6 | 19.8 | 84.2 | 9.4 | 261 | 7.9 | 745.1 | 689.8 | 662 | 737.3 | 555.8 | 585.6 | 769.5 | 504.2 | 660.8 | 517.9 | 113 | 172.7 | 215.5 | 182 | 281.9 | 272.4 | 173.2 | 244.6 | 284.4 | 229.9
1829.3 | 1610.3 | 538.6 | 215.44 | 251.8369 | 279.6 | 247.1 | 266.9 | 267.5 | 440.8 | 45.7 | 19.8 | 84.3 | 9.5 | 251.5 | 8 | 744.4 | 696.5 | 669.5 | 732.4 | 556.3 | 586.6 | 767.3 | 501.7 | 658.5 | 518.3 | 113.1 | 172.8 | 215.4 | 182.2 | 281.5 | 272.4 | 173.3 | 244.7 | 284.5 | 230
1830.3 | 1611.3 | 538.5 | 215.4 | 251.7902 | 280.1 | 246.9 | 266.4 | 268.2 | 441.5 | 45.8 | 19.8 | 84.3 | 9.5 | 225.1 | 8.6 | 749.3 | 715.9 | 676 | 738 | 558.9 | 587.5 | 770.7 | 521.6 | 656.6 | 520.6 | 113.2 | 172.9 | 215.5 | 182.3 | 281.1 | 273.1 | 173.4 | 244.8 | 284.6 | 230.1
1831.3 | 1612.3 | 539.3 | 215.72 | 252.1643 | 280.3 | 246.8 | 265.4 | 268.5 | 449.4 | 45.9 | 19.8 | 84.4 | 8.5 | 241.9 | 11.7 | 754.1 | 718.2 | 695.5 | 741.6 | 562.6 | 588.2 | 776.3 | 535.3 | 655.7 | 525.1 | 113.3 | 173 | 215.6 | 182.5 | 281.3 | 274 | 173.5 | 245 | 284.8 | 230.2
1832.3 | 1613.3 | 539.8 | 215.92 | 252.398 | 279.1 | 246.4 | 264.8 | 268.3 | 454.5 | 45.9 | 19.8 | 84.5 | 9.5 | 242.8 | 17.3 | 761.7 | 745.4 | 711.4 | 747.2 | 567.2 | 589 | 784.3 | 550.9 | 656.3 | 529.7 | 113.4 | 173.1 | 215.8 | 182.6 | 281.3 | 274.9 | 173.6 | 245.2 | 285 | 230.3
1833.3 | 1614.3 | 540.2 | 216.08 | 252.5851 | 278.6 | 245.3 | 265.7 | 266.6 | 462.5 | 46 | 19.8 | 84.5 | 8.6 | 245.7 | 16.9 | 766.8 | 750.6 | 721.4 | 755.2 | 569.7 | 589.9 | 787.7 | 564.1 | 657.2 | 533.8 | 113.5 | 173.2 | 216 | 182.8 | 281.1 | 275.1 | 173.7 | 245.4 | 285.1 | 230.5
1834.3 | 1615.3 | 540.6 | 216.24 | 252.7721 | 278.3 | 244.4 | 267.1 | 266.9 | 469.7 | 46 | 19.8 | 84.6 | 8 | 250.9 | 15.3 | 772.3 | 757.1 | 720.3 | 763.1 | 571.7 | 590.6 | 786.8 | 571.5 | 659 | 535.9 | 113.6 | 173.3 | 216.2 | 182.9 | 280.9 | 275.2 | 173.8 | 245.5 | 285.4 | 230.6
1835.3 | 1616.3 | 541 | 216.4 | 252.9591 | 277.5 | 244.7 | 268.1 | 267.8 | 469.5 | 46.1 | 19.8 | 84.6 | 7.2 | 263.9 | 12.8 | 777.7 | 762.9 | 735.5 | 768.8 | 576 | 591.5 | 788.4 | 576.9 | 659.9 | 539.6 | 113.7 | 173.4 | 216.5 | 183.1 | 281.6 | 275.2 | 173.9 | 245.7 | 285.5 | 230.7
1836.3 | 1617.3 | 540.2 | 216.08 | 252.5851 | 276.6 | 245.5 | 267.9 | 267.7 | 477.6 | 46.1 | 19.8 | 84.6 | 7.1 | 260.5 | 10.5 | 785.4 | 777.7 | 753.8 | 776.4 | 581.7 | 592.3 | 789 | 596.5 | 658.5 | 546.2 | 113.8 | 173.5 | 216.6 | 183.2 | 282.1 | 275.5 | 174 | 245.7 | 285.7 | 230.9
1837.3 | 1618.3 | 540.4 | 216.16 | 252.6786 | 276.3 | 246.3 | 268 | 267.6 | 490.4 | 46.1 | 19.8 | 84.6 | 7.3 | 226.6 | 10.8 | 791.9 | 785.7 | 758.5 | 783 | 587.9 | 593 | 784.8 | 619.6 | 657.4 | 552.6 | 113.9 | 173.7 | 216.9 | 183.4 | 282 | 275.3 | 174.1 | 245.8 | 286 | 231.1
1838.3 | 1619.3 | 541.3 | 216.52 | 253.0994 | 275.8 | 247.1 | 267.5 | 268.4 | 500.4 | 46.2 | 19.8 | 84.5 | 7.8 | 233.2 | 12.7 | 797.6 | 802.3 | 765.4 | 789.6 | 592.8 | 593.8 | 781.6 | 629.3 | 656.2 | 555.3 | 114 | 173.8 | 216.9 | 183.5 | 282.3 | 275 | 174.2 | 245.9 | 286.3 | 231.2
1839.3 | 1620.3 | 542.5 | 217 | 253.6605 | 275.3 | 248.1 | 266.8 | 269.2 | 507.6 | 46.3 | 19.8 | 84.4 | 8 | 233.2 | 12.3 | 802.1 | 799.4 | 766 | 793.2 | 595.3 | 594.5 | 784.3 | 639.9 | 657.2 | 558 | 114.1 | 173.9 | 217.1 | 183.6 | 282.8 | 274.8 | 174.3 | 245.9 | 286.5 | 231.3
1840.3 | 1621.3 | 542.5 | 217 | 253.6605 | 275.3 | 247.6 | 267.1 | 269.3 | 513.1 | 46.4 | 19.8 | 84.3 | 7.7 | 240 | 11.5 | 806.7 | 815.5 | 770.6 | 798.9 | 597.3 | 595.5 | 786 | 661.3 | 658.9 | 559.5 | 114.2 | 174 | 217.5 | 183.8 | 282.6 | 274.6 | 174.4 | 246 | 286.8 | 231.4
1841.3 | 1622.3 | 543 | 217.2 | 253.8943 | 275.8 | 247.6 | 268.2 | 268.8 | 524.4 | 46.5 | 19.8 | 84.4 | 7.3 | 247.7 | 11.1 | 813.8 | 832.9 | 779 | 807.6 | 601.6 | 596.2 | 792.5 | 683.6 | 660 | 564.5 | 114.3 | 174.1 | 217.7 | 183.9 | 282.6 | 274.4 | 174.5 | 246 | 287 | 231.6
1842.3 | 1623.3 | 543.7 | 217.48 | 254.2216 | 277.2 | 248.1 | 269.5 | 270.2 | 530.5 | 46.5 | 19.8 | 84.4 | 7.1 | 239.7 | 11.1 | 816.6 | 845.7 | 782.4 | 806.1 | 605.2 | 597.3 | 790.6 | 697.4 | 660.7 | 566.3 | 114.4 | 174.2 | 217.9 | 184 | 283.1 | 274.4 | 174.7 | 246.1 | 287.3 | 231.7
1843.3 | 1624.3 | 542.9 | 217.16 | 253.8475 | 277.9 | 248.3 | 270 | 271.2 | 528.9 | 46.5 | 19.8 | 84.4 | 6.3 | 229.4 | 10.3 | 821.5 | 838.6 | 794.1 | 813.1 | 609.3 | 598.5 | 789.6 | 691.5 | 661.1 | 570.6 | 114.5 | 174.3 | 217.9 | 184.2 | 283.8 | 274.7 | 174.7 | 246.2 | 287.6 | 231.8
1844.3 | 1625.3 | 543.1 | 217.24 | 253.941 | 278.8 | 248.7 | 269.9 | 271.9 | 517.3 | 46.5 | 19.8 | 84.5 | 6.6 | 262.3 | 9.3 | 826.9 | 833.8 | 799.3 | 819 | 612.5 | 599.7 | 789.5 | 678.9 | 663.2 | 575.2 | 114.6 | 174.4 | 218 | 184.3 | 283.8 | 274.8 | 174.8 | 246.3 | 287.9 | 232
1845.3 | 1626.3 | 542.4 | 216.96 | 253.6137 | 279 | 249 | 270.9 | 271.2 | 513.7 | 46.5 | 19.8 | 84.5 | 7.6 | 245.4 | 7.8 | 828.3 | 824 | 794.9 | 817.8 | 615.5 | 601 | 786.7 | 665.4 | 663.2 | 578.7 | 114.7 | 174.5 | 218.2 | 184.4 | 283.8 | 275.2 | 174.9 | 246.4 | 288.1 | 232.1
1846.3 | 1627.3 | 545.9 | 218.36 | 255.2503 | 279.3 | 249.2 | 270.3 | 270.6 | 500 | 46.5 | 19.8 | 84.7 | 8.8 | 275.9 | 7.4 | 828.9 | 808.8 | 790.6 | 821.7 | 616.3 | 602.5 | 784.6 | 651.2 | 664.1 | 579.2 | 114.8 | 174.7 | 218.4 | 184.6 | 283.7 | 275.4 | 175 | 246.6 | 288.4 | 232.2
1847.3 | 1628.3 | 551.7 | 220.68 | 257.9622 | 279.7 | 250.2 | 269 | 270.9 | 494.1 | 46.5 | 19.8 | 84.8 | 9.2 | 248.5 | 6.5 | 829.2 | 799.4 | 786.9 | 826.3 | 619.3 | 603.6 | 780.7 | 645.2 | 660.8 | 581.3 | 114.8 | 174.8 | 218.5 | 184.7 | 284.1 | 275.8 | 175.1 | 246.8 | 288.7 | 232.3
1848.3 | 1629.3 | 553.5 | 221.4 | 258.8038 | 280.6 | 250.7 | 268.9 | 270 | 502 | 46.6 | 19.8 | 84.8 | 9.3 | 225.8 | 6 | 829.9 | 780.3 | 773.2 | 828.7 | 617.4 | 604.7 | 774.4 | 639.1 | 660.2 | 580.7 | 114.9 | 174.9 | 218.7 | 184.8 | 285.2 | 276.4 | 175.2 | 246.9 | 288.9 | 232.5
1849.3 | 1630.3 | 554.4 | 221.76 | 259.2247 | 281.5 | 250.1 | 268.1 | 270.2 | 502 | 46.7 | 19.8 | 84.8 | 10.2 | 265.6 | 7 | 825.4 | 752.3 | 757.3 | 826.3 | 615.8 | 605.7 | 772 | 614.9 | 660.7 | 578.8 | 115 | 175 | 218.9 | 185 | 286.4 | 276.5 | 175.3 | 247.1 | 289.2 | 232.7
1850.3 | 1631.3 | 553.3 | 221.32 | 258.7103 | 281.7 | 249.9 | 268.7 | 270.7 | 490.8 | 46.8 | 19.8 | 84.8 | 10.8 | 247.9 | 8.4 | 823.7 | 751.2 | 747.1 | 826.3 | 614.6 | 606.8 | 767.5 | 604.7 | 661.9 | 577.2 | 115.1 | 175.1 | 219.1 | 185.1 | 286.7 | 276.6 | 175.4 | 247.3 | 289.3 | 232.8
1851.3 | 1632.3 | 551.9 | 220.76 | 258.0557 | 282.1 | 249.6 | 269.1 | 270.2 | 485.9 | 46.8 | 19.8 | 84.8 | 11.5 | 250.9 | 11.3 | 821 | 726.3 | 723.5 | 822.4 | 611.6 | 607.7 | 759.7 | 594 | 662.5 | 576 | 115.2 | 175.2 | 219.2 | 185.2 | 286.6 | 276.7 | 175.5 | 247.5 | 289.5 | 233
1852.3 | 1633.3 | 552.9 | 221.16 | 258.5233 | 283.2 | 249.7 | 270 | 270.9 | 483 | 46.8 | 19.8 | 84.8 | 12 | 244.1 | 13.5 | 818.7 | 722.7 | 717.2 | 817.9 | 609.9 | 608.7 | 758.5 | 586.3 | 665.2 | 574.1 | 115.3 | 175.3 | 219.5 | 185.4 | 286.8 | 276.9 | 175.6 | 247.6 | 289.7 | 233.1
1853.3 | 1634.3 | 552.5 | 221 | 258.3363 | 283.9 | 249.4 | 271.9 | 271.9 | 487.3 | 46.8 | 19.8 | 84.8 | 10.9 | 242.7 | 14.5 | 818.5 | 740 | 726.1 | 814.6 | 610.6 | 610.1 | 758.4 | 591.5 | 665.6 | 574.4 | 115.4 | 175.3 | 219.7 | 185.5 | 287.2 | 277.4 | 175.7 | 247.7 | 289.8 | 233.2
1854.3 | 1635.3 | 552 | 220.8 | 258.1025 | 283.6 | 249.3 | 273.1 | 272.2 | 485.9 | 46.8 | 19.8 | 84.9 | 11.7 | 253.5 | 14.4 | 824.4 | 775.1 | 752 | 822.5 | 616.9 | 611.2 | 762.3 | 620.9 | 664.7 | 577.8 | 115.5 | 175.5 | 219.8 | 185.6 | 287.4 | 277.4 | 175.7 | 247.7 | 290 | 233.4
1855.3 | 1636.3 | 551.8 | 220.72 | 258.009 | 284.4 | 248.9 | 273.1 | 271.4 | 494.1 | 46.8 | 19.8 | 85 | 13.1 | 254.1 | 14.1 | 831.7 | 782.9 | 767.7 | 833.4 | 620.4 | 612 | 762.9 | 633.5 | 663.9 | 581.7 | 115.6 | 175.6 | 220.1 | 185.8 | 287.2 | 277.6 | 175.9 | 247.9 | 290.3 | 233.5
1856.3 | 1637.3 | 551.6 | 220.64 | 257.9154 | 285.4 | 248.9 | 273 | 270.9 | 492.2 | 46.9 | 19.8 | 85.1 | 13.8 | 250.7 | 15.1 | 837.5 | 789.9 | 777 | 841.4 | 621.4 | 613 | 759.2 | 630.1 | 661.8 | 583.6 | 115.7 | 175.6 | 220.1 | 185.9 | 286.7 | 277.7 | 176 | 248 | 290.5 | 233.6
1857.3 | 1638.3 | 551.5 | 220.6 | 257.8687 | 284.3 | 248.9 | 272.7 | 271.7 | 488.7 | 46.8 | 19.8 | 85.1 | 13.5 | 246.9 | 17.4 | 840.8 | 781.3 | 762.8 | 843.5 | 621 | 614.1 | 759.2 | 614.3 | 662.6 | 582.6 | 115.8 | 175.8 | 220.1 | 186 | 286.4 | 277.7 | 176.1 | 248.2 | 290.8 | 233.7
1858.3 | 1639.3 | 550.9 | 220.36 | 257.5881 | 284.4 | 248.3 | 273 | 271.9 | 483.2 | 46.8 | 19.8 | 85.1 | 12 | 244.2 | 20.6 | 842.1 | 786.7 | 757.3 | 843.9 | 619.8 | 615.3 | 762.9 | 607.8 | 665.1 | 581.9 | 115.9 | 175.8 | 220.3 | 186.2 | 286.5 | 278.1 | 176.2 | 248.3 | 291.1 | 233.8
1859.3 | 1640.3 | 551.5 | 220.6 | 257.8687 | 285.1 | 248.2 | 273 | 272 | 482.7 | 46.8 | 19.8 | 85.1 | 12.6 | 244.2 | 19.9 | 844.1 | 786.9 | 755.2 | 846.3 | 620 | 616.3 | 769.3 | 599.1 | 668.2 | 584.5 | 116 | 175.9 | 220.6 | 186.3 | 287.1 | 278.5 | 176.3 | 248.5 | 291.3 | 233.9
1860.3 | 1641.3 | 551.5 | 220.6 | 257.8687 | 284.6 | 248.5 | 274.2 | 272.3 | 489 | 46.8 | 19.8 | 85.2 | 12.4 | 241.9 | 19.5 | 848.7 | 804.7 | 774.5 | 851.3 | 622.6 | 617.3 | 772.9 | 614.2 | 670.8 | 586.7 | 116.1 | 176.1 | 220.9 | 186.4 | 287.6 | 278.9 | 176.4 | 248.7 | 291.6 | 234.1
1861.3 | 1642.3 | 550.3 | 220.12 | 257.3076 | 285.3 | 249.2 | 275.5 | 271.7 | 499 | 46.8 | 19.8 | 85.3 | 11.8 | 238 | 19.5 | 851.4 | 796.7 | 768.1 | 854.1 | 623 | 618.3 | 771.8 | 603.5 | 670.1 | 588.8 | 116.2 | 176.2 | 221.1 | 186.6 | 288.2 | 279.4 | 176.5 | 248.9 | 291.8 | 234.3
1862.3 | 1643.3 | 551.2 | 220.48 | 257.7284 | 285.9 | 249.4 | 275.8 | 271.6 | 489.2 | 46.8 | 19.8 | 85.3 | 10.7 | 242.5 | 17.7 | 851 | 791.5 | 763.2 | 845.7 | 623.9 | 619.5 | 765.4 | 602 | 669.9 | 587.7 | 116.3 | 176.3 | 221.1 | 186.7 | 289.2 | 279.9 | 176.6 | 249.1 | 292.1 | 234.4
1863.3 | 1644.3 | 551.2 | 220.48 | 257.7284 | 286.4 | 249.9 | 275.8 | 273.4 | 490.7 | 46.7 | 19.8 | 85.4 | 9.5 | 236.5 | 16.3 | 851.4 | 806.4 | 770.1 | 841.6 | 625 | 620.6 | 765.5 | 610.3 | 669 | 587.4 | 116.4 | 176.4 | 221.4 | 186.8 | 289.3 | 280.1 | 176.7 | 249.2 | 292.4 | 234.6
1864.3 | 1645.3 | 550.1 | 220.04 | 257.2141 | 287.1 | 249.8 | 275.8 | 273.3 | 492.5 | 46.7 | 19.8 | 85.2 | 9.8 | 236.5 | 18.1 | 852.3 | 808.7 | 765.2 | 842.2 | 625.9 | 621.6 | 758.7 | 611.5 | 667.2 | 586.1 | 116.4 | 176.5 | 221.6 | 187 | 289.1 | 280 | 176.8 | 249.3 | 292.7 | 234.7
1865.3 | 1646.3 | 551.3 | 220.52 | 257.7752 | 288.2 | 249.6 | 275.4 | 272.6 | 491.1 | 46.7 | 19.8 | 85.1 | 10.9 | 234.4 | 17.3 | 854.6 | 814.4 | 758.5 | 843.8 | 625.9 | 622.5 | 759.4 | 617.6 | 667.2 | 587.7 | 116.5 | 176.7 | 221.8 | 187.1 | 289.4 | 280.5 | 176.9 | 249.4 | 292.9 | 234.9
1866.3 | 1647.3 | 552.9 | 221.16 | 258.5233 | 290.3 | 249.8 | 275.3 | 273.3 | 485.1 | 46.6 | 19.8 | 85.1 | 10.7 | 245.5 | 17 | 854.8 | 805.5 | 745.5 | 843.2 | 624.8 | 623.5 | 761.4 | 611.1 | 666.8 | 587.6 | 116.6 | 176.8 | 222.1 | 187.3 | 289.7 | 280.8 | 176.9 | 249.7 | 293.2 | 235
1867.3 | 1648.3 | 552.9 | 221.16 | 258.5233 | 289.6 | 249.7 | 276.3 | 275 | 485.6 | 46.7 | 19.8 | 85.1 | 9.1 | 250.3 | 20.3 | 852.3 | 781.8 | 746.5 | 837.3 | 624 | 624.6 | 752.3 | 598.2 | 664.7 | 586.3 | 116.7 | 176.9 | 222.2 | 187.4 | 289.9 | 280.8 | 177 | 249.8 | 293.5 | 235.2
1868.3 | 1649.3 | 553.2 | 221.28 | 258.6636 | 289.5 | 249.9 | 276.5 | 275.7 | 485.9 | 46.7 | 19.8 | 85 | 7.1 | 240.9 | 21.7 | 849.8 | 774.7 | 737.3 | 832.6 | 622.3 | 625.6 | 749.3 | 592.8 | 663.3 | 585.3 | 116.8 | 177.1 | 222.2 | 187.5 | 289.9 | 280.9 | 177.2 | 249.9 | 293.8 | 235.3
1869.3 | 1650.3 | 551.7 | 220.68 | 257.9622 | 289.8 | 250.3 | 275.4 | 274.9 | 487.7 | 46.8 | 19.8 | 85 | 6.6 | 242.5 | 16.2 | 842.9 | 751.9 | 706.7 | 823.1 | 618.6 | 626.2 | 740.8 | 582.4 | 662 | 583.2 | 116.9 | 177.2 | 222.4 | 187.7 | 290.1 | 281.2 | 177.2 | 250 | 294.1 | 235.4
1870.3 | 1651.3 | 551.5 | 220.6 | 257.8687 | 291.1 | 250.5 | 275.1 | 274.8 | 476.3 | 46.9 | 19.8 | 84.8 | 6.6 | 257.2 | 14.3 | 835.6 | 736.2 | 685.4 | 811 | 615.2 | 626.5 | 729.2 | 567.4 | 662.2 | 580 | 117 | 177.3 | 222.5 | 187.8 | 290.6 | 281.8 | 177.4 | 250.2 | 294.3 | 235.6
1871.3 | 1652.3 | 552 | 220.8 | 258.1025 | 292.1 | 250.7 | 275.4 | 275.3 | 474.2 | 47 | 19.7 | 84.8 | 6.5 | 249.2 | 14.8 | 836.4 | 738.8 | 691.1 | 811.5 | 614.2 | 627.3 | 731.4 | 571.1 | 663.8 | 579.1 | 117.1 | 177.5 | 222.7 | 188 | 290.4 | 282.2 | 177.4 | 250.3 | 294.5 | 235.7
1872.3 | 1653.3 | 551.5 | 220.6 | 257.8687 | 293.6 | 250.8 | 275.7 | 274.9 | 474.6 | 47 | 19.8 | 84.8 | 6.2 | 239.3 | 12.5 | 838.5 | 753.1 | 694.5 | 814.9 | 615 | 628.4 | 738 | 571.8 | 663.2 | 580.1 | 117.2 | 177.6 | 222.8 | 188.1 | 291.1 | 282.4 | 177.5 | 250.5 | 294.6 | 235.9
1873.3 | 1654.3 | 551 | 220.4 | 257.6349 | 293.8 | 250.9 | 275.5 | 274.9 | 480.2 | 46.9 | 19.7 | 85 | 7.7 | 247 | 9.9 | 841.5 | 757.2 | 694.2 | 820.8 | 613.9 | 629.7 | 737.8 | 574.6 | 661.5 | 581.2 | 117.3 | 177.7 | 223 | 188.2 | 291.7 | 282.7 | 177.6 | 250.6 | 294.9 | 236.1
1874.3 | 1655.3 | 551.2 | 220.48 | 257.7284 | 294.7 | 250.7 | 276.4 | 274.7 | 485.9 | 46.9 | 19.7 | 85.3 | 8.5 | 258.4 | 8.8 | 845.5 | 783.3 | 712.6 | 825.2 | 617.3 | 630.6 | 743 | 604.3 | 661.1 | 583.9 | 117.4 | 177.9 | 223.3 | 188.4 | 292.1 | 283.1 | 177.7 | 250.7 | 295.2 | 236.2
1875.3 | 1656.3 | 551.6 | 220.64 | 257.9154 | 295.5 | 251.2 | 277.6 | 274.8 | 500.9 | 46.9 | 19.7 | 85.5 | 8.5 | 296.3 | 9.4 | 848.3 | 802.2 | 730.4 | 826.7 | 618.1 | 631.6 | 744.1 | 613.4 | 662 | 584.4 | 117.5 | 178 | 223.6 | 188.5 | 292.1 | 283.9 | 177.8 | 250.9 | 295.5 | 236.4
1876.3 | 1657.3 | 551.8 | 220.72 | 258.009 | 295.7 | 252.2 | 277.4 | 273.7 | 499.8 | 46.9 | 19.7 | 85.7 | 9.1 | 282.5 | 11.1 | 847.6 | 782.6 | 724.2 | 823 | 618.2 | 632.7 | 732.9 | 605.4 | 658.9 | 583 | 117.6 | 178.1 | 223.8 | 188.7 | 291.7 | 283.9 | 177.9 | 251 | 295.8 | 236.5
1877.3 | 1658.3 | 551.4 | 220.56 | 257.8219 | 296.1 | 252.7 | 277.3 | 274 | 486.8 | 47 | 19.7 | 85.8 | 8 | 274.8 | 10.9 | 841.4 | 760.8 | 703.6 | 815.7 | 615.5 | 633.5 | 723.5 | 584.3 | 658.4 | 580.1 | 117.7 | 178.2 | 224 | 188.8 | 291.7 | 283.6 | 178 | 251.2 | 296.1 | 236.6
1878.3 | 1659.3 | 552 | 220.8 | 258.1025 | 296 | 253.1 | 278.1 | 273.4 | 479.3 | 47.1 | 19.7 | 86 | 7.7 | 275.4 | 9.6 | 835.4 | 749.7 | 695.7 | 809.4 | 614.3 | 634.3 | 716 | 571.4 | 657.1 | 577.6 | 117.8 | 178.4 | 224.1 | 188.9 | 291.3 | 283.1 | 178.1 | 251.3 | 296.3 | 236.7
1879.3 | 1660.3 | 553 | 221.2 | 258.5701 | 296.5 | 254.5 | 277.8 | 272.2 | 478 | 47.2 | 19.7 | 86.2 | 8.2 | 273.2 | 8.6 | 828.2 | 727.6 | 685.7 | 797.5 | 612.2 | 635.3 | 709.4 | 561.6 | 657.5 | 575.6 | 117.9 | 178.5 | 224.1 | 189.1 | 291.2 | 282.9 | 178.2 | 251.3 | 296.5 | 236.9
1880.3 | 1661.3 | 552 | 220.8 | 258.1025 | 296.5 | 254.8 | 277.2 | 270.5 | 480.1 | 47.3 | 19.7 | 86.5 | 7.7 | 270.7 | 8.8 | 825.4 | 731.1 | 682.3 | 793 | 611.5 | 636.2 | 710.4 | 566.8 | 658.8 | 574.6 | 118 | 178.6 | 224.2 | 189.2 | 290.7 | 282.7 | 178.3 | 251.4 | 296.7 | 237
1881.3 | 1662.3 | 552 | 220.8 | 258.1025 | 296.1 | 254.7 | 276.2 | 270.3 | 490 | 47.4 | 19.7 | 86.7 | 7.8 | 286.6 | 9.7 | 826.6 | 751.1 | 691.3 | 791.4 | 613.8 | 637 | 713.2 | 581.9 | 660.3 | 574.6 | 118.1 | 178.7 | 224.5 | 189.4 | 290.2 | 282.4 | 178.4 | 251.4 | 296.9 | 237.1
1882.3 | 1663.3 | 552.1 | 220.84 | 258.1492 | 295.5 | 255.1 | 274.7 | 269.8 | 491.1 | 47.5 | 19.7 | 87 | 8.2 | 288.4 | 11.1 | 825.6 | 746 | 685.9 | 791.4 | 612.2 | 637.9 | 713.3 | 578.5 | 660.4 | 574.1 | 118.2 | 178.9 | 224.6 | 189.5 | 289.6 | 281.8 | 178.5 | 251.5 | 297.2 | 237.2
1883.3 | 1664.3 | 553.1 | 221.24 | 258.6168 | 295.1 | 255.2 | 275.5 | 269.7 | 492.7 | 47.5 | 19.7 | 87.3 | 8.1 | 287.9 | 12.2 | 825.2 | 755.2 | 700.6 | 795.5 | 612.6 | 639 | 716.6 | 582.9 | 661.6 | 574.1 | 118.3 | 179 | 224.8 | 189.6 | 289.5 | 281.3 | 178.6 | 251.5 | 297.4 | 237.3
1884.3 | 1665.3 | 553 | 221.2 | 258.5701 | 295.6 | 255.7 | 276.3 | 270.7 | 497.2 | 47.5 | 19.7 | 87.5 | 7.9 | 293.6 | 13.7 | 830 | 780.2 | 711.9 | 804.4 | 614.1 | 639.6 | 728.6 | 599 | 660.5 | 576.9 | 118.4 | 179.1 | 224.9 | 189.8 | 289.2 | 281.1 | 178.7 | 251.6 | 297.6 | 237.4
1885.3 | 1666.3 | 556.5 | 222.6 | 260.2066 | 296.7 | 256.6 | 276.7 | 269.9 | 498.2 | 47.6 | 19.7 | 87.6 | 7.4 | 276.1 | 13.4 | 834.5 | 791.3 | 739.4 | 813.1 | 618.5 | 640.4 | 740 | 607.4 | 660.2 | 580.1 | 118.5 | 179.2 | 225.1 | 189.9 | 289.2 | 282.1 | 178.7 | 251.8 | 297.9 | 237.5
1886.3 | 1667.3 | 560.4 | 224.16 | 262.0301 | 297.1 | 257.9 | 276.1 | 270.9 | 503.2 | 47.6 | 19.7 | 87.7 | 7.4 | 274.2 | 12.5 | 839.3 | 798.4 | 764.5 | 823.4 | 623.2 | 641.2 | 747.4 | 611.4 | 660.1 | 583.9 | 118.6 | 179.3 | 225.2 | 190 | 289.3 | 284 | 178.8 | 252.2 | 298.2 | 237.7
1887.3 | 1668.3 | 561.1 | 224.44 | 262.3574 | 298 | 258.3 | 275.6 | 272.3 | 499.6 | 47.6 | 19.7 | 87.9 | 7.7 | 282.5 | 13.2 | 844.1 | 789.3 | 773.8 | 834.1 | 626.3 | 642.3 | 750.1 | 612 | 658.2 | 588.7 | 118.7 | 179.4 | 225.3 | 190.1 | 289.6 | 285.2 | 178.9 | 252.4 | 298.5 | 237.8
1888.3 | 1669.3 | 560.9 | 224.36 | 262.2639 | 297.7 | 259.1 | 275.3 | 272.5 | 500 | 47.6 | 19.7 | 88 | 7.8 | 281.9 | 15.8 | 848.3 | 796.8 | 788.2 | 844.1 | 630.6 | 643.2 | 755.6 | 613.9 | 658.2 | 593.1 | 118.8 | 179.5 | 225.7 | 190.3 | 289.9 | 285.9 | 179.1 | 252.6 | 298.8 | 237.9
1889.3 | 1670.3 | 560.7 | 224.28 | 262.1704 | 297.2 | 259.8 | 276.1 | 273.2 | 508 | 47.6 | 19.7 | 87.9 | 8 | 273.6 | 14.8 | 852.9 | 821.1 | 797.6 | 850.9 | 633.5 | 643.6 | 758.4 | 640.5 | 658.2 | 597.4 | 118.9 | 179.6 | 225.9 | 190.4 | 291.3 | 285.8 | 179.2 | 252.8 | 299.2 | 238.1
1890.3 | 1671.3 | 560.9 | 224.36 | 262.2639 | 296.6 | 259.7 | 276.5 | 271.8 | 521.8 | 47.6 | 19.7 | 87.9 | 8.4 | 266.5 | 12.9 | 859.8 | 836.7 | 805.5 | 865.6 | 638.7 | 643.7 | 762.9 | 668 | 659.2 | 604.1 | 118.9 | 179.7 | 226.1 | 190.5 | 292.1 | 286 | 179.2 | 252.9 | 299.7 | 238.3
1891.3 | 1672.3 | 559.7 | 223.88 | 261.7028 | 295.3 | 259.4 | 275.9 | 271.5 | 538.3 | 47.6 | 19.7 | 88 | 8.6 | 278.9 | 12.3 | 863.4 | 842 | 798.9 | 864.4 | 640.1 | 644 | 761.7 | 682.1 | 659.4 | 603.1 | 119.1 | 179.8 | 226.5 | 190.7 | 292.1 | 285.9 | 179.3 | 253.1 | 300.2 | 238.5
1892.3 | 1673.3 | 558 | 223.2 | 260.9079 | 294.6 | 259.4 | 276.1 | 273 | 541.2 | 47.6 | 19.7 | 88 | 7.6 | 289.3 | 11.9 | 866.9 | 843 | 803.1 | 861.5 | 642.3 | 645.1 | 761.5 | 684.8 | 659.4 | 604.7 | 119.2 | 179.9 | 226.7 | 190.8 | 292.1 | 285.7 | 179.4 | 253.3 | 300.6 | 238.6
1893.3 | 1674.3 | 556.5 | 222.6 | 260.2066 | 294.9 | 259.6 | 277.3 | 274.4 | 547.9 | 47.6 | 19.7 | 88.1 | 7.8 | 288.9 | 10.9 | 871.1 | 853.1 | 811.8 | 865.3 | 646.8 | 646 | 762.4 | 706.3 | 658.7 | 607.1 | 119.3 | 180.1 | 227 | 190.9 | 292 | 285.4 | 179.5 | 253.4 | 301 | 238.7
1894.3 | 1675.3 | 556.7 | 222.68 | 260.3001 | 296.4 | 260 | 276.7 | 275.1 | 555.6 | 47.5 | 19.7 | 88.1 | 7.1 | 290.4 | 10.5 | 875.8 | 868.4 | 809.7 | 872 | 649.5 | 646.2 | 771.8 | 727.7 | 658.7 | 612.6 | 119.3 | 180.2 | 227.3 | 191.1 | 292.1 | 285.1 | 179.6 | 253.4 | 301.4 | 238.8
1895.3 | 1676.3 | 557.4 | 222.96 | 260.6274 | 296.8 | 261.2 | 275.5 | 275 | 557.1 | 47.5 | 19.7 | 88.1 | 7.2 | 284.1 | 10.7 | 879.9 | 869.4 | 805.7 | 873.3 | 651.9 | 646.8 | 779.5 | 724.2 | 660.3 | 616.7 | 119.4 | 180.3 | 227.5 | 191.2 | 292 | 284.7 | 179.7 | 253.6 | 301.8 | 239
1896.3 | 1677.3 | 556.5 | 222.6 | 260.2066 | 297.1 | 262.2 | 276.8 | 276.5 | 569.8 | 47.5 | 19.7 | 88.1 | 7.1 | 280.5 | 9 | 883.3 | 876.6 | 810.4 | 877.8 | 654 | 647.8 | 780.8 | 732.7 | 659.7 | 617.1 | 119.5 | 180.4 | 227.9 | 191.3 | 292.1 | 284.3 | 179.8 | 253.8 | 302.2 | 239.1
1897.4 | 1678.4 | 556 | 222.4 | 259.9728 | 299.5 | 262.6 | 279.9 | 277.8 | 570.3 | 47.5 | 19.7 | 88.1 | 6.9 | 304.9 | 6.9 | 885.7 | 869.3 | 805.5 | 880.4 | 655.5 | 648.8 | 774.4 | 731.5 | 657.1 | 618.2 | 119.7 | 180.5 | 227.8 | 191.5 | 292.6 | 284.3 | 179.9 | 253.8 | 302.6 | 239.2
1898.4 | 1679.4 | 556.3 | 222.52 | 260.1131 | 302 | 262.9 | 281.3 | 279.5 | 558.5 | 47.5 | 19.7 | 88 | 7.1 | 340.3 | 5.8 | 889.8 | 866.5 | 792 | 887.3 | 655.1 | 649.8 | 772.8 | 726.3 | 656.3 | 620 | 119.8 | 180.6 | 227.8 | 191.6 | 292.9 | 284.5 | 180 | 253.9 | 303 | 239.4
1899.4 | 1680.4 | 555.6 | 222.24 | 259.7858 | 303.8 | 263.5 | 282.3 | 280 | 568.9 | 47.5 | 19.7 | 88 | 7.5 | 333.4 | 5.2 | 893.4 | 877.3 | 788.4 | 891 | 654.7 | 650.5 | 776.2 | 743.8 | 657.5 | 621.5 | 119.8 | 180.7 | 228.2 | 191.7 | 292.9 | 284.6 | 180.1 | 254.1 | 303.4 | 239.5
1900.4 | 1681.4 | 555.9 | 222.36 | 259.926 | 304 | 264.2 | 282.2 | 280.5 | 582.5 | 47.6 | 19.7 | 87.8 | 7.2 | 343.1 | 5.7 | 896.5 | 888.8 | 796.8 | 890 | 657.1 | 651.3 | 780.3 | 764.8 | 658.7 | 625.1 | 119.9 | 180.8 | 228.6 | 191.8 | 293.1 | 284.6 | 180.2 | 254.2 | 303.8 | 239.7
1901.4 | 1682.4 | 556 | 222.4 | 259.9728 | 304.6 | 264.8 | 280.7 | 281.4 | 591.5 | 47.6 | 19.7 | 87.8 | 7.1 | 327.6 | 6.1 | 899.8 | 897.1 | 805 | 895 | 661.2 | 652.1 | 780.6 | 764.6 | 660.7 | 630.2 | 120 | 181 | 228.8 | 191.9 | 293.4 | 284.8 | 180.3 | 254.3 | 304.2 | 239.8
1902.4 | 1683.4 | 555.9 | 222.36 | 259.926 | 304.8 | 265.6 | 280.3 | 281.5 | 583.9 | 47.7 | 19.7 | 87.8 | 7.7 | 337.2 | 6.3 | 899.3 | 881.1 | 794 | 888.8 | 662 | 653.6 | 774.9 | 745 | 660.1 | 629.4 | 120.1 | 181.1 | 229.1 | 192.1 | 293.9 | 285 | 180.4 | 254.5 | 304.7 | 239.9
1903.4 | 1684.4 | 555.6 | 222.24 | 259.7858 | 306.3 | 265.8 | 279.8 | 281.4 | 575.7 | 47.7 | 19.7 | 87.9 | 8 | 336.1 | 6.9 | 894.1 | 856.6 | 779.7 | 876.3 | 658.7 | 655 | 767.6 | 724.5 | 660.2 | 627.1 | 120.2 | 181.2 | 229.2 | 192.2 | 294.5 | 285 | 180.5 | 254.6 | 305.1 | 240.1
1904.4 | 1685.4 | 555.6 | 222.24 | 259.7858 | 308.8 | 265.8 | 280.1 | 283.2 | 556.4 | 47.7 | 19.7 | 87.9 | 7.8 | 330.7 | 7.6 | 891.7 | 834.4 | 777.2 | 872.9 | 660.5 | 656.7 | 760.8 | 703.9 | 659.1 | 627.9 | 120.3 | 181.3 | 229.1 | 192.3 | 295 | 285.5 | 180.6 | 254.8 | 305.5 | 240.3
1905.4 | 1686.4 | 556.6 | 222.64 | 260.2533 | 310.2 | 266.1 | 279.8 | 283.9 | 546.7 | 47.7 | 19.7 | 88 | 7.6 | 330.6 | 7.2 | 891.3 | 828.4 | 783.7 | 872.9 | 662.1 | 658 | 761.8 | 692 | 659.8 | 629.2 | 120.4 | 181.4 | 229.3 | 192.4 | 295.9 | 285.9 | 180.7 | 255.1 | 305.8 | 240.4
1906.4 | 1687.4 | 557.1 | 222.84 | 260.4871 | 309.6 | 265.5 | 277.6 | 284.7 | 547.4 | 47.8 | 19.7 | 87.9 | 7.3 | 324.4 | 6.8 | 894.8 | 841.2 | 779.8 | 880.4 | 663.2 | 658.7 | 763.4 | 697.4 | 659.1 | 630 | 120.5 | 181.6 | 229.5 | 192.6 | 296 | 286.1 | 180.8 | 255.2 | 306.2 | 240.5
1907.4 | 1688.4 | 555.7 | 222.28 | 259.8325 | 309.2 | 264.3 | 277.2 | 283.5 | 541.6 | 47.8 | 19.7 | 88 | 6.4 | 300.1 | 5.7 | 898.2 | 850.6 | 783.5 | 887.1 | 665.2 | 659.7 | 766.7 | 697 | 659.6 | 632.9 | 120.6 | 181.7 | 229.7 | 192.7 | 296.3 | 286 | 180.9 | 255.5 | 306.6 | 240.7
1908.4 | 1689.4 | 554.9 | 221.96 | 259.4585 | 309 | 263.6 | 277.7 | 283.6 | 534.5 | 47.8 | 19.7 | 88.2 | 7.3 | 271.5 | 5.2 | 898.3 | 843.3 | 780.2 | 885.1 | 663.4 | 660.7 | 760 | 689.6 | 658.3 | 630.8 | 120.7 | 181.8 | 230 | 192.8 | 296.4 | 286.1 | 181 | 255.6 | 307.1 | 240.8
1909.4 | 1690.4 | 554.3 | 221.72 | 259.1779 | 308.3 | 262.9 | 277.9 | 282.5 | 525.8 | 47.9 | 19.7 | 88.3 | 6 | 274.6 | 5.1 | 894.8 | 839 | 774.8 | 877.1 | 663.3 | 662 | 753.2 | 681.5 | 657.4 | 628.7 | 120.8 | 182 | 230.3 | 192.9 | 296.4 | 285.8 | 181 | 255.7 | 307.4 | 241
1910.4 | 1691.4 | 553.7 | 221.48 | 258.8974 | 309 | 262.3 | 277.2 | 280.9 | 525 | 48 | 19.7 | 88.4 | 6.6 | 271.2 | 5 | 893 | 844.3 | 770.9 | 870.8 | 661.9 | 663 | 752.2 | 689.4 | 656.9 | 628.2 | 120.9 | 182.1 | 230.6 | 193.1 | 296.4 | 285.7 | 181.1 | 255.8 | 307.8 | 241.1
1911.4 | 1692.4 | 554.5 | 221.8 | 259.2714 | 310 | 261.6 | 277.9 | 281.9 | 541.1 | 48 | 19.7 | 88.5 | 6.4 | 252.2 | 5 | 892.9 | 834.7 | 756.3 | 869.7 | 658.4 | 663.8 | 749.5 | 693.7 | 655.7 | 627.2 | 121 | 182.2 | 230.8 | 193.2 | 297.2 | 285.7 | 181.3 | 256 | 308.2 | 241.3
1912.4 | 1693.4 | 553.7 | 221.48 | 258.8974 | 309.7 | 261.2 | 278.5 | 282.5 | 537.7 | 48 | 19.7 | 88.7 | 7 | 252.3 | 5.8 | 893 | 826.1 | 752.6 | 868.1 | 658.1 | 665 | 748.9 | 686.4 | 655.5 | 626.4 | 121.1 | 182.4 | 230.9 | 193.4 | 297.5 | 285.9 | 181.4 | 256.2 | 308.6 | 241.4
1913.4 | 1694.4 | 554.2 | 221.68 | 259.1311 | 309.2 | 261.3 | 280.6 | 282.3 | 529.3 | 48 | 19.7 | 88.8 | 7.3 | 245.5 | 6.4 | 891.7 | 815.6 | 738.2 | 866.2 | 654.6 | 665.9 | 748.9 | 679.5 | 655.3 | 626.2 | 121.2 | 182.5 | 231.2 | 193.5 | 298.3 | 286.4 | 181.4 | 256.3 | 309 | 241.6
1914.4 | 1695.4 | 555.1 | 222.04 | 259.552 | 309.5 | 260.9 | 280.2 | 283.4 | 527 | 48.1 | 19.7 | 88.8 | 7.7 | 211.5 | 5.7 | 890.7 | 816.8 | 728.8 | 864.6 | 652.6 | 667.1 | 744.6 | 671.7 | 655.6 | 625.4 | 121.3 | 182.6 | 231.4 | 193.6 | 299 | 286.8 | 181.6 | 256.4 | 309.4 | 241.8
1915.4 | 1696.4 | 554.4 | 221.76 | 259.2247 | 311.1 | 260.1 | 280.5 | 283.7 | 528.1 | 48 | 19.7 | 88.8 | 7.1 | 209.4 | 5.3 | 891.4 | 823.7 | 727 | 861.2 | 651.3 | 668.3 | 743.9 | 673 | 656.7 | 624.7 | 121.4 | 182.7 | 231.6 | 193.8 | 299.8 | 287.3 | 181.6 | 256.6 | 309.8 | 242
1916.4 | 1697.4 | 554 | 221.6 | 259.0376 | 312.2 | 261.3 | 281.1 | 283.2 | 524.4 | 48 | 19.6 | 88.8 | 7.5 | 212.3 | 5 | 890.7 | 818.8 | 722.9 | 858.3 | 649.3 | 669 | 744.6 | 673.9 | 657 | 624.7 | 121.5 | 182.9 | 232 | 193.9 | 300.4 | 287.7 | 181.8 | 256.8 | 310.2 | 242.2
1917.4 | 1698.4 | 553.8 | 221.52 | 258.9441 | 313.6 | 262.1 | 282.1 | 283.8 | 525.7 | 48.1 | 19.6 | 88.9 | 7.9 | 200.7 | 4.7 | 889.8 | 825.9 | 723.4 | 853.9 | 648.7 | 669.7 | 750.2 | 679.9 | 659 | 626 | 121.6 | 183 | 232.2 | 194 | 301.5 | 288 | 181.9 | 256.9 | 310.5 | 242.4
1918.4 | 1699.4 | 552.8 | 221.12 | 258.4765 | 314.1 | 262.7 | 283.1 | 283 | 531.2 | 48.2 | 19.6 | 88.9 | 7.4 | 215.2 | 4.5 | 891.9 | 837.8 | 737.1 | 859.5 | 649.3 | 670.6 | 751.2 | 684.6 | 659.2 | 627.3 | 121.7 | 183.2 | 232.2 | 194.2 | 302.8 | 288.4 | 182 | 257.1 | 310.9 | 242.6
1919.4 | 1700.4 | 553.4 | 221.36 | 258.7571 | 313.4 | 263.5 | 283.8 | 283.8 | 537.3 | 48.2 | 19.6 | 88.9 | 6.9 | 237.4 | 4.2 | 894.2 | 837.8 | 741.9 | 868 | 649.8 | 671.6 | 753.5 | 691.3 | 658.3 | 628.6 | 121.8 | 183.3 | 232.5 | 194.3 | 303.1 | 288.7 | 182.1 | 257.2 | 311.2 | 242.8
1920.4 | 1701.4 | 554.5 | 221.8 | 259.2714 | 313.6 | 264.4 | 284.1 | 285.6 | 552.8 | 48.3 | 19.6 | 88.8 | 6.8 | 198.7 | 4 | 896 | 838.9 | 752.7 | 871 | 650.4 | 672.5 | 752 | 697.5 | 657.1 | 628.3 | 121.9 | 183.4 | 232.9 | 194.5 | 303.7 | 288.7 | 182.2 | 257.4 | 311.7 | 242.9
1921.4 | 1702.4 | 555.4 | 222.16 | 259.6922 | 314.3 | 265.2 | 284.2 | 285.2 | 553.8 | 48.3 | 19.6 | 88.7 | 6.8 | 178 | 4.7 | 898.5 | 818.7 | 766.1 | 876.8 | 652.5 | 673.7 | 755.1 | 681.8 | 659.1 | 629.3 | 122 | 183.5 | 233 | 194.6 | 303.7 | 288.8 | 182.4 | 257.6 | 312.2 | 243.1
1922.4 | 1703.4 | 556.4 | 222.56 | 260.1598 | 315.4 | 266.3 | 285.7 | 284.9 | 540.9 | 48.3 | 19.6 | 88.6 | 7.2 | 208.5 | 7.1 | 898.7 | 825.1 | 772.8 | 876.9 | 655 | 674.9 | 757.6 | 683.7 | 660 | 632.8 | 122.1 | 183.7 | 233.1 | 194.8 | 303.5 | 288.9 | 182.5 | 257.8 | 312.5 | 243.3
1923.4 | 1704.4 | 555.5 | 222.2 | 259.739 | 315 | 267.1 | 285.7 | 284.9 | 542.8 | 48.3 | 19.6 | 88.6 | 7.4 | 218.8 | 7.8 | 898.3 | 838.7 | 786.8 | 877.9 | 658.5 | 675.5 | 760 | 699.5 | 660.6 | 633.5 | 122.2 | 183.8 | 233.2 | 194.9 | 304.1 | 289.1 | 182.7 | 257.9 | 313 | 243.4
1924.4 | 1705.4 | 554.9 | 221.96 | 259.4585 | 315.7 | 267.4 | 284 | 284.1 | 549.3 | 48.3 | 19.6 | 88.6 | 7.9 | 291.3 | 6.4 | 902.7 | 845.3 | 797.3 | 886.3 | 660.7 | 675.9 | 769.1 | 710 | 660.8 | 636.9 | 122.3 | 184 | 233.5 | 195.1 | 304.6 | 289.6 | 182.7 | 258.1 | 313.4 | 243.6
1925.4 | 1706.4 | 555.8 | 222.32 | 259.8793 | 313.8 | 267.6 | 282.2 | 284.4 | 540.1 | 48.3 | 19.6 | 88.7 | 9 | 265.7 | 4.2 | 906.5 | 840.8 | 808.8 | 896.1 | 664.6 | 676.3 | 776.5 | 701.9 | 663.3 | 641.2 | 122.4 | 184.1 | 233.6 | 195.2 | 304.9 | 290.5 | 182.8 | 258.3 | 313.9 | 243.8
1926.4 | 1707.4 | 554.5 | 221.8 | 259.2714 | 311.9 | 267.7 | 281.7 | 284 | 536.7 | 48.3 | 19.6 | 88.7 | 8 | 193.1 | 4.4 | 910.6 | 850.5 | 820.2 | 905.8 | 667.1 | 676.8 | 780.2 | 711.4 | 664.7 | 643.9 | 122.5 | 184.2 | 233.8 | 195.4 | 305.1 | 290.6 | 182.9 | 258.5 | 314.4 | 244
1927.4 | 1708.4 | 553.7 | 221.48 | 258.8974 | 310.9 | 266.7 | 281.8 | 284.7 | 550.4 | 48.4 | 19.6 | 88.9 | 7.5 | 215 | 6.1 | 913.5 | 867.5 | 828.3 | 913.6 | 672 | 677.2 | 784.3 | 734 | 666.8 | 649.9 | 122.6 | 184.3 | 234.1 | 195.6 | 304.7 | 290.5 | 183 | 258.6 | 314.8 | 244.2
1928.4 | 1709.4 | 554.1 | 221.64 | 259.0844 | 310.5 | 266 | 281.1 | 284.9 | 557.7 | 48.4 | 19.6 | 88.9 | 8.9 | 224.9 | 6.1 | 915.9 | 879.6 | 829 | 913.5 | 677.1 | 677.7 | 784 | 743.8 | 668.8 | 655.5 | 122.6 | 184.5 | 234.3 | 195.8 | 305.1 | 290.6 | 183.1 | 258.8 | 315.3 | 244.3
1929.4 | 1710.4 | 554.8 | 221.92 | 259.4117 | 308.9 | 265 | 280.9 | 285 | 557.2 | 48.6 | 19.6 | 88.9 | 8.2 | 186.2 | 7 | 918 | 881.7 | 825.3 | 913.5 | 679 | 678.6 | 783.1 | 734.1 | 668.2 | 658.7 | 122.8 | 184.6 | 234.5 | 196 | 305.6 | 290.4 | 183.1 | 259.1 | 315.8 | 244.5
1930.4 | 1711.4 | 554.9 | 221.96 | 259.4585 | 308 | 264.5 | 282.2 | 286.8 | 557 | 48.6 | 19.6 | 88.9 | 8.1 | 203.2 | 7.9 | 919.4 | 867 | 822.5 | 917.8 | 681.6 | 680.2 | 781.8 | 719.6 | 669.1 | 660.1 | 122.8 | 184.7 | 234.5 | 196.2 | 305.6 | 290.4 | 183.2 | 259.3 | 316.4 | 244.7
1931.4 | 1712.4 | 555.7 | 222.28 | 259.8325 | 307.3 | 264.1 | 283.2 | 287.3 | 540.4 | 48.7 | 19.6 | 88.8 | 6.8 | 218.1 | 8.4 | 921.1 | 875.9 | 824.8 | 917.8 | 684.5 | 681.6 | 779.4 | 719.1 | 670.5 | 660.9 | 123 | 184.9 | 234.6 | 196.5 | 305.6 | 290.3 | 183.3 | 259.4 | 316.9 | 244.8
1932.4 | 1713.4 | 555.4 | 222.16 | 259.6922 | 308.4 | 264.4 | 282.4 | 287.5 | 537.6 | 48.7 | 19.6 | 88.9 | 7.1 | 237 | 8.6 | 922.9 | 879.6 | 827.5 | 920.6 | 687.1 | 682.3 | 776.4 | 729.5 | 670.8 | 664.9 | 123 | 185 | 234.9 | 196.7 | 305.2 | 290.3 | 183.4 | 259.4 | 317.4 | 245
1933.4 | 1714.4 | 555.9 | 222.36 | 259.926 | 309.5 | 264.5 | 281.4 | 287.9 | 538.8 | 48.6 | 19.6 | 88.9 | 8.8 | 243.7 | 9.8 | 925.2 | 873.2 | 820.2 | 926 | 687.2 | 683.1 | 778.8 | 726.4 | 671 | 666.1 | 123.1 | 185.1 | 235.1 | 196.9 | 305.1 | 290.3 | 183.5 | 259.6 | 318 | 245.1
1934.4 | 1715.4 | 556.2 | 222.48 | 260.0663 | 307.7 | 264.4 | 281 | 287.7 | 540.7 | 48.6 | 19.6 | 88.8 | 9 | 245.3 | 10.3 | 927.6 | 866.1 | 810.8 | 927.6 | 686 | 683.9 | 779.9 | 731.3 | 670.9 | 666 | 123.2 | 185.2 | 235.3 | 197.2 | 304.9 | 290.4 | 183.6 | 259.7 | 318.5 | 245.3
1935.4 | 1716.4 | 557.2 | 222.88 | 260.5339 | 308.3 | 263.1 | 282.7 | 287.8 | 557.6 | 48.6 | 19.6 | 88.7 | 8.2 | 260.7 | 11.8 | 928.8 | 874.6 | 805.8 | 938.2 | 687.3 | 684.1 | 783.9 | 756.2 | 672.5 | 666.8 | 123.3 | 185.4 | 235.8 | 197.4 | 304.7 | 290.6 | 183.7 | 259.9 | 318.9 | 245.4
1936.4 | 1717.4 | 556.3 | 222.52 | 260.1131 | 308.7 | 262 | 284.5 | 288.2 | 567.5 | 48.5 | 19.6 | 88.7 | 7.9 | 253.6 | 12.8 | 929.1 | 868.3 | 794.1 | 933.5 | 686.2 | 685.2 | 775.8 | 751.7 | 671.5 | 665.1 | 123.4 | 185.5 | 236 | 197.6 | 304.7 | 290.8 | 183.8 | 259.9 | 319.3 | 245.6
1937.4 | 1718.4 | 555.3 | 222.12 | 259.6455 | 308.7 | 262.9 | 285.1 | 287.7 | 562.9 | 48.5 | 19.6 | 88.7 | 7.6 | 253.7 | 12 | 929.3 | 876.8 | 794.3 | 921.3 | 687.2 | 686.4 | 776.6 | 757.7 | 672.9 | 664.9 | 123.5 | 185.6 | 236 | 197.8 | 304.5 | 291 | 183.9 | 260 | 319.7 | 245.8
1938.4 | 1719.4 | 554.7 | 221.88 | 259.3649 | 311.2 | 264.2 | 285.8 | 289.3 | 559.8 | 48.6 | 19.6 | 88.7 | 8.7 | 247.1 | 11 | 926.8 | 874.9 | 794.1 | 909.9 | 686.5 | 687.3 | 778.1 | 761.3 | 673.8 | 664.1 | 123.6 | 185.7 | 236.3 | 198 | 304.2 | 290.9 | 184 | 260.2 | 320.1 | 245.9
1939.4 | 1720.4 | 555.2 | 222.08 | 259.5987 | 311.7 | 263.8 | 286.9 | 290.7 | 570.3 | 48.6 | 19.6 | 88.7 | 9.2 | 233.9 | 10.2 | 926.5 | 879.8 | 804.5 | 907.9 | 687.4 | 688.3 | 779.5 | 759.8 | 675.3 | 664.5 | 123.7 | 185.9 | 236.6 | 198.1 | 304.4 | 290.7 | 184.1 | 260.3 | 320.5 | 246
1940.4 | 1721.4 | 555.8 | 222.32 | 259.8793 | 310.6 | 263.1 | 287.5 | 290.8 | 567.6 | 48.8 | 19.6 | 88.6 | 8.5 | 252 | 10.2 | 929.4 | 883.7 | 810.7 | 918 | 688.4 | 688.8 | 789.1 | 772.5 | 677.1 | 666.6 | 123.8 | 186 | 236.7 | 198.3 | 304.4 | 290.8 | 184.2 | 260.4 | 320.9 | 246.2
1941.4 | 1722.4 | 557.1 | 222.84 | 260.4871 | 312.1 | 263.5 | 289.2 | 290.5 | 577.6 | 48.8 | 19.6 | 88.7 | 8.2 | 254.9 | 11.6 | 931.8 | 889 | 809.8 | 925.1 | 688.8 | 689.4 | 797.4 | 786.6 | 679.1 | 669.3 | 123.9 | 186.1 | 237 | 198.4 | 304.2 | 290.7 | 184.3 | 260.6 | 321.4 | 246.3
1942.4 | 1723.4 | 555.9 | 222.36 | 259.926 | 313.6 | 263.4 | 290.4 | 291.2 | 586.1 | 48.8 | 19.6 | 88.8 | 9.2 | 238.7 | 11.2 | 933.7 | 901.3 | 820.4 | 934 | 693 | 690.1 | 797 | 791.8 | 681.5 | 674.5 | 124 | 186.3 | 237.4 | 198.6 | 304.7 | 290.7 | 184.4 | 260.8 | 321.9 | 246.5
1943.4 | 1724.4 | 555.5 | 222.2 | 259.739 | 313.9 | 263 | 289.6 | 290.9 | 591.2 | 48.8 | 19.6 | 88.9 | 9.1 | 244 | 10.4 | 934.6 | 897.8 | 825.6 | 939.5 | 695.1 | 690.8 | 795.8 | 792.8 | 681.6 | 678.8 | 124.1 | 186.4 | 237.6 | 198.7 | 305.1 | 290.7 | 184.5 | 260.9 | 322.4 | 246.6
1944.4 | 1725.4 | 555.8 | 222.32 | 259.8793 | 314.5 | 263.1 | 289.1 | 291 | 587.5 | 48.9 | 19.6 | 88.8 | 8.7 | 252.3 | 12.1 | 936.7 | 887.6 | 826.5 | 937.2 | 696.1 | 691.9 | 796.9 | 781.7 | 681.4 | 678.2 | 124.2 | 186.5 | 237.7 | 198.9 | 305.2 | 290.9 | 184.6 | 261.2 | 323 | 246.8
1945.4 | 1726.4 | 556 | 222.4 | 259.9728 | 315.4 | 264.4 | 289.5 | 290.8 | 580.3 | 48.9 | 19.6 | 88.8 | 8.3 | 247.7 | 13.5 | 938.9 | 890.6 | 832.4 | 940.9 | 698.4 | 692.9 | 798 | 778.6 | 682.1 | 682 | 124.3 | 186.6 | 237.9 | 199 | 305.1 | 291.5 | 184.7 | 261.4 | 323.5 | 247
1946.4 | 1727.4 | 556.4 | 222.56 | 260.1598 | 317.6 | 265.2 | 291.1 | 290.4 | 580 | 48.9 | 19.6 | 88.6 | 8.1 | 236.7 | 13.6 | 941.4 | 896.2 | 840.3 | 949.1 | 701.4 | 693.5 | 803 | 787.6 | 683 | 683.9 | 124.4 | 186.8 | 238.1 | 199.2 | 305.1 | 291.6 | 184.8 | 261.5 | 324 | 247.1
1947.4 | 1728.4 | 555.7 | 222.28 | 259.8325 | 319.2 | 266 | 291.5 | 289.3 | 588.3 | 48.8 | 19.6 | 88.5 | 8.3 | 236.3 | 12.5 | 940.6 | 877.5 | 822.2 | 943.1 | 699.9 | 694.5 | 795.8 | 777.3 | 681.3 | 682.5 | 124.5 | 186.9 | 238.6 | 199.3 | 306.3 | 291.6 | 184.8 | 261.8 | 324.6 | 247.2
1948.4 | 1729.4 | 556 | 222.4 | 259.9728 | 317.7 | 266.3 | 291 | 288 | 580.7 | 48.8 | 19.6 | 88.5 | 8.3 | 233.3 | 12.7 | 938.5 | 855.8 | 816.2 | 932.7 | 701.3 | 696 | 784.5 | 762.5 | 678.7 | 679.8 | 124.6 | 187 | 238.7 | 199.5 | 306.5 | 291.7 | 185 | 261.9 | 325.1 | 247.5
1949.4 | 1730.4 | 556.1 | 222.44 | 260.0195 | 317.5 | 266.6 | 290.9 | 289.1 | 564.6 | 48.7 | 19.6 | 88.6 | 8.7 | 239.2 | 14.4 | 934.1 | 855.1 | 815.5 | 919.7 | 702.4 | 697.5 | 779.8 | 750.2 | 677.2 | 679.4 | 124.7 | 187.1 | 238.7 | 199.7 | 306.5 | 291.8 | 185.1 | 262 | 325.5 | 247.6
1950.4 | 1731.4 | 556.2 | 222.48 | 260.0663 | 317.3 | 266.9 | 291.3 | 290.6 | 559.1 | 48.7 | 19.6 | 88.6 | 8.1 | 244.1 | 14.3 | 932.5 | 874.4 | 827.5 | 914 | 706.2 | 698.3 | 781.8 | 760 | 676.9 | 683.1 | 124.8 | 187.3 | 238.9 | 199.9 | 306.9 | 292 | 185.2 | 262.1 | 326 | 247.8
1951.4 | 1732.4 | 557.9 | 223.16 | 260.8612 | 317.3 | 266.7 | 290 | 291.4 | 556.3 | 48.7 | 19.6 | 88.6 | 8.2 | 240.8 | 13.3 | 927.4 | 866 | 828.8 | 902.8 | 708.7 | 699.6 | 773 | 746.7 | 674.9 | 681.7 | 124.9 | 187.4 | 238.9 | 200 | 307 | 292 | 185.2 | 262.3 | 326.5 | 248
1952.4 | 1733.4 | 556.4 | 222.56 | 260.1598 | 316.7 | 267 | 288.3 | 292.2 | 551.9 | 48.7 | 19.6 | 88.7 | 7.5 | 233.5 | 12.3 | 923.7 | 863.3 | 827.2 | 896.3 | 713.1 | 700.9 | 772 | 747.7 | 675.8 | 683.3 | 125 | 187.5 | 239.2 | 200.2 | 307.1 | 292.1 | 185.4 | 262.4 | 327 | 248.1
1953.4 | 1734.4 | 555.2 | 222.08 | 259.5987 | 316.6 | 267 | 286.2 | 289.9 | 549.1 | 48.7 | 19.6 | 88.6 | 8.2 | 242.7 | 14 | 920.7 | 864.3 | 827.9 | 892.6 | 712.4 | 702 | 767.6 | 736.6 | 676.5 | 681.3 | 125.1 | 187.7 | 239.2 | 200.3 | 307.1 | 292.6 | 185.4 | 262.5 | 327.5 | 248.3
1954.4 | 1735.4 | 555.1 | 222.04 | 259.552 | 316.1 | 267.3 | 284 | 288 | 543.7 | 48.7 | 19.6 | 88.6 | 8.4 | 234.1 | 13.5 | 918.8 | 865.6 | 836 | 887.6 | 713.1 | 703.2 | 770.2 | 737.9 | 675.5 | 682.3 | 125.2 | 187.8 | 239.4 | 200.5 | 306.6 | 293.4 | 185.6 | 262.7 | 328 | 248.4
1955.4 | 1736.4 | 556.6 | 222.64 | 260.2533 | 315.8 | 267.6 | 282.3 | 286.8 | 546.6 | 48.7 | 19.6 | 88.8 | 8 | 244.6 | 11.7 | 918.5 | 861.5 | 834.8 | 890.1 | 714.2 | 704.2 | 768.2 | 733.6 | 674.6 | 683.8 | 125.3 | 188 | 239.7 | 200.7 | 306.1 | 293.6 | 185.7 | 262.8 | 328.5 | 248.5
1956.4 | 1737.4 | 558.7 | 223.48 | 261.2352 | 315.3 | 268.2 | 280.6 | 284.8 | 537 | 48.9 | 19.6 | 89 | 7.9 | 241.3 | 11.6 | 918.3 | 856.9 | 831.6 | 895.3 | 714.2 | 705 | 770.5 | 723.7 | 675 | 685.5 | 125.4 | 188.1 | 239.8 | 200.8 | 306.2 | 293.6 | 185.7 | 263 | 329 | 248.6
1957.4 | 1738.4 | 559.1 | 223.64 | 261.4223 | 314.7 | 269.1 | 281.6 | 283.6 | 531.8 | 49.1 | 19.6 | 89.2 | 7.1 | 244.6 | 11.3 | 912.3 | 843 | 799.1 | 881.3 | 710.1 | 705.4 | 750.3 | 710.3 | 673 | 680.3 | 125.5 | 188.2 | 240.1 | 201 | 306.8 | 293.3 | 185.8 | 263.2 | 329.5 | 248.8
1958.4 | 1739.4 | 558.4 | 223.36 | 261.095 | 314.4 | 268.6 | 282.1 | 282.8 | 521.4 | 49.2 | 19.6 | 89.4 | 6.2 | 244.1 | 10.4 | 904.4 | 823.3 | 787.9 | 863.8 | 707.9 | 706.6 | 737.2 | 689.1 | 672.7 | 675.8 | 125.6 | 188.4 | 240.1 | 201.2 | 306.7 | 293.5 | 185.9 | 263.3 | 329.9 | 249
1959.4 | 1740.4 | 558 | 223.2 | 260.9079 | 313.8 | 268.8 | 282.6 | 282.4 | 512.8 | 49.3 | 19.5 | 89.6 | 6.3 | 243.9 | 9.4 | 901.8 | 820.8 | 794.3 | 865.1 | 707.9 | 708 | 740.7 | 675.9 | 674.6 | 674.6 | 125.7 | 188.5 | 240.1 | 201.3 | 306.4 | 294 | 186 | 263.5 | 330.1 | 249.1
1960.4 | 1741.4 | 557.8 | 223.12 | 260.8144 | 312.6 | 268.4 | 283.1 | 281.7 | 518 | 49.3 | 19.5 | 89.8 | 7.3 | 241.4 | 9.3 | 901.9 | 822.1 | 779.1 | 869.9 | 707 | 708.7 | 742.6 | 687.2 | 674.5 | 674 | 125.8 | 188.6 | 240.2 | 201.5 | 305.8 | 293.9 | 186.1 | 263.8 | 330.4 | 249.2
1961.4 | 1742.4 | 556.9 | 222.76 | 260.3936 | 311.8 | 267 | 283.1 | 280.6 | 515.5 | 49.3 | 19.5 | 89.9 | 7.3 | 239.8 | 8.8 | 900.7 | 807.5 | 777.9 | 872 | 705.6 | 709.9 | 737.2 | 669.3 | 674.9 | 670.9 | 125.9 | 188.7 | 240.4 | 201.7 | 305.5 | 293.8 | 186.3 | 263.9 | 330.8 | 249.4
1962.4 | 1743.4 | 558.2 | 223.28 | 261.0015 | 312.7 | 266.3 | 282.9 | 280.9 | 510.9 | 49.4 | 19.5 | 90.1 | 7 | 246.6 | 8.6 | 897.4 | 788.5 | 777.3 | 867.8 | 705.7 | 711 | 736.9 | 656.4 | 675.3 | 670.1 | 126 | 188.9 | 240.4 | 201.8 | 305.9 | 293.9 | 186.4 | 264 | 331.2 | 249.5
1963.4 | 1744.4 | 558.2 | 223.28 | 261.0015 | 313.1 | 266.2 | 282.2 | 281.8 | 510.1 | 49.4 | 19.5 | 90.2 | 6.5 | 240.8 | 8.7 | 892.1 | 789.1 | 782 | 864.1 | 705.9 | 712.2 | 738.8 | 642.8 | 675.5 | 668.2 | 126.1 | 189 | 240.6 | 202 | 305.5 | 293.9 | 186.5 | 264.2 | 331.7 | 249.7
1964.4 | 1745.4 | 556.9 | 222.76 | 260.3936 | 313.8 | 265.6 | 280.9 | 280.2 | 506.7 | 49.5 | 19.5 | 90.3 | 7 | 239.4 | 8.2 | 891.2 | 797.3 | 790.2 | 868.4 | 707.2 | 713.1 | 743.5 | 638 | 677 | 669 | 126.2 | 189.1 | 240.7 | 202.2 | 305.3 | 294 | 186.5 | 264.4 | 332.1 | 249.8
1965.4 | 1746.4 | 556.6 | 222.64 | 260.2533 | 313.7 | 264.7 | 279.5 | 279.5 | 505.4 | 49.6 | 19.5 | 90.3 | 6.4 | 244.8 | 8.1 | 891.6 | 815.6 | 798.4 | 868.9 | 709 | 713.6 | 750.3 | 650.5 | 680 | 671.1 | 126.3 | 189.3 | 240.9 | 202.4 | 305.8 | 294.2 | 186.7 | 264.5 | 332.6 | 250
1966.4 | 1747.4 | 555.6 | 222.24 | 259.7858 | 315.4 | 264.4 | 279.5 | 280.5 | 510.6 | 49.6 | 19.5 | 90.4 | 6 | 258.2 | 8.5 | 892.4 | 816.3 | 800.9 | 869.8 | 710.2 | 714 | 756.9 | 661.6 | 682 | 673.2 | 126.4 | 189.4 | 241.2 | 202.6 | 306 | 294.6 | 186.8 | 264.7 | 333 | 250.1
1967.4 | 1748.4 | 556.8 | 222.72 | 260.3468 | 315.9 | 264.2 | 281 | 281.6 | 515.3 | 49.7 | 19.5 | 90.6 | 6.8 | 267.1 | 7.7 | 896.8 | 828.9 | 808.1 | 881.8 | 711.4 | 714.3 | 767.1 | 675.3 | 682.9 | 677.8 | 126.5 | 189.6 | 241.5 | 202.8 | 306.4 | 294.8 | 186.9 | 264.8 | 333.5 | 250.3
1968.4 | 1749.4 | 557.6 | 223.04 | 260.7209 | 315.2 | 264.1 | 284.3 | 280.8 | 521.5 | 49.7 | 19.5 | 90.7 | 5.9 | 267.5 | 7.2 | 900.6 | 818.9 | 806.4 | 892 | 711.1 | 714.6 | 771.6 | 681.7 | 685.3 | 678 | 126.6 | 189.7 | 241.7 | 203 | 306.3 | 295.2 | 187 | 264.9 | 333.9 | 250.4
1969.4 | 1750.4 | 558.3 | 223.32 | 261.0482 | 315.8 | 264.2 | 285.3 | 279.9 | 526.5 | 49.7 | 19.5 | 90.8 | 6 | 255.6 | 8.5 | 903.1 | 843.5 | 815.4 | 896.5 | 714.6 | 715 | 775.6 | 694.8 | 688.3 | 679.8 | 126.7 | 189.8 | 241.9 | 203.1 | 306.1 | 295.2 | 187.1 | 265.1 | 334.4 | 250.6
1970.4 | 1751.4 | 559.6 | 223.84 | 261.6561 | 317.3 | 264.2 | 285.3 | 281.3 | 526.3 | 49.8 | 19.5 | 91 | 7.1 | 249 | 7.1 | 905.5 | 845.7 | 818.6 | 902.5 | 717.1 | 715.2 | 778.5 | 700 | 688.9 | 682.2 | 126.8 | 189.9 | 242 | 203.3 | 306.1 | 295.4 | 187.2 | 265.2 | 334.9 | 250.7
1971.4 | 1752.4 | 557.9 | 223.16 | 260.8612 | 318.9 | 264.2 | 286.4 | 283 | 521 | 49.8 | 19.5 | 91 | 7 | 250 | 6.9 | 905.7 | 846.6 | 817 | 899 | 717.6 | 715.9 | 777.3 | 699.9 | 690.4 | 681.5 | 126.9 | 190 | 242.1 | 203.5 | 306.1 | 295.4 | 187.3 | 265.3 | 335.5 | 250.8
1972.4 | 1753.4 | 557.5 | 223 | 260.6742 | 319.4 | 263.8 | 286.4 | 284.2 | 518.6 | 49.9 | 19.5 | 91.1 | 7.6 | 250 | 6.7 | 905.2 | 845 | 823.8 | 895.9 | 717 | 716.6 | 775.5 | 692.8 | 690.3 | 682.7 | 127 | 190.1 | 242.3 | 203.7 | 306.2 | 295.5 | 187.4 | 265.5 | 335.9 | 251
1973.4 | 1754.4 | 558.9 | 223.56 | 261.3288 | 321.2 | 263.4 | 285.5 | 285.8 | 516.5 | 50 | 19.5 | 91.1 | 7 | 262.8 | 6.5 | 907.8 | 856 | 834.7 | 900.5 | 719.3 | 717.2 | 779.8 | 694 | 691.5 | 684.2 | 127.1 | 190.2 | 242.6 | 203.9 | 306 | 295.6 | 187.5 | 265.5 | 336.4 | 251.1
1974.4 | 1755.4 | 558.3 | 223.32 | 261.0482 | 319.8 | 263.4 | 286.5 | 286.1 | 529.8 | 50.1 | 19.5 | 91 | 6.7 | 256.6 | 7.2 | 911 | 860.7 | 845.5 | 906.7 | 722.8 | 717.4 | 782.3 | 719.7 | 692.7 | 689 | 127.2 | 190.3 | 242.9 | 204.1 | 306.5 | 295.7 | 187.6 | 265.7 | 336.9 | 251.3
1975.4 | 1756.4 | 558.3 | 223.32 | 261.0482 | 318.2 | 263.9 | 286.5 | 285.5 | 544.7 | 50.1 | 19.5 | 91 | 6.8 | 269.8 | 7.7 | 912 | 870.6 | 848.5 | 905.4 | 724.6 | 718.3 | 778.4 | 727.3 | 693.7 | 689.7 | 127.3 | 190.4 | 243.3 | 204.2 | 306.7 | 296.2 | 187.7 | 265.9 | 337.4 | 251.5
1976.4 | 1757.4 | 558.3 | 223.32 | 261.0482 | 317.1 | 264.6 | 287.2 | 285.2 | 553.1 | 50.1 | 19.5 | 91.1 | 6.8 | 279.6 | 7.4 | 912 | 880.9 | 840.5 | 903.1 | 723.2 | 719 | 771.4 | 740.5 | 694.9 | 687.6 | 127.5 | 190.5 | 243.5 | 204.4 | 306.5 | 296.6 | 187.8 | 266 | 337.9 | 251.6
1977.4 | 1758.4 | 557.3 | 222.92 | 260.5806 | 317.2 | 265.7 | 288.5 | 286.3 | 553.5 | 50.1 | 19.5 | 91.2 | 5.5 | 272.2 | 7.4 | 912.6 | 878.5 | 834.3 | 903.5 | 722.2 | 719.3 | 775.8 | 747.1 | 694.9 | 689.1 | 127.6 | 190.6 | 243.5 | 204.6 | 306 | 296.7 | 187.9 | 266.1 | 338.4 | 251.7
1978.4 | 1759.4 | 557 | 222.8 | 260.4404 | 318.4 | 267.2 | 289.2 | 286.2 | 552.1 | 50.1 | 19.5 | 91.2 | 6.1 | 289.3 | 7.5 | 916.1 | 885.7 | 838.9 | 911.2 | 723.5 | 719.6 | 781.4 | 754.7 | 696.2 | 690.8 | 127.7 | 190.6 | 243.6 | 204.7 | 305.8 | 296.5 | 188 | 266.3 | 338.8 | 251.9
1979.4 | 1760.4 | 557.2 | 222.88 | 260.5339 | 320.5 | 268.6 | 288.1 | 286.2 | 552.9 | 50.2 | 19.5 | 91.3 | 5.9 | 271.5 | 7.1 | 919 | 886.4 | 843 | 916.2 | 725.4 | 719.8 | 786.4 | 756.6 | 696.9 | 695 | 127.8 | 190.7 | 243.7 | 204.9 | 305.8 | 296.4 | 188.1 | 266.4 | 339.4 | 252
1980.4 | 1761.4 | 557.7 | 223.08 | 260.7677 | 321.6 | 269.3 | 288.6 | 285.2 | 553.7 | 50.2 | 19.5 | 91.3 | 6.3 | 263.5 | 6.4 | 922.3 | 878.3 | 842.4 | 922.7 | 726.4 | 720.1 | 792.1 | 761.9 | 699.7 | 697.3 | 127.9 | 190.8 | 243.9 | 205.1 | 305.9 | 296.5 | 188.2 | 266.6 | 339.9 | 252.2
1981.4 | 1762.4 | 558.4 | 223.36 | 261.095 | 322.7 | 269.9 | 288.4 | 284.5 | 547.9 | 50.2 | 19.5 | 91.2 | 7.3 | 245.2 | 6.1 | 923.7 | 874.4 | 844.9 | 924.1 | 727.7 | 720.5 | 794.7 | 756.6 | 700.7 | 697.3 | 128 | 190.9 | 244 | 205.3 | 305.8 | 297.3 | 188.3 | 266.7 | 340.5 | 252.3
1982.4 | 1763.4 | 558.8 | 223.52 | 261.282 | 322.2 | 270.6 | 288.3 | 283.9 | 552.8 | 50.3 | 19.5 | 91.2 | 7.2 | 244.5 | 5.5 | 925.6 | 885.3 | 852.2 | 930.1 | 730.6 | 721.1 | 791.9 | 765.7 | 702.3 | 700.6 | 128.1 | 191 | 244.2 | 205.5 | 305.9 | 297.6 | 188.4 | 267 | 341 | 252.5
1983.4 | 1764.4 | 558.5 | 223.4 | 261.1417 | 323.5 | 271.2 | 288.8 | 282.6 | 558.1 | 50.3 | 19.5 | 91.3 | 6.6 | 283.1 | 4.9 | 927.7 | 884.5 | 855.5 | 937.7 | 733.7 | 721.6 | 792.1 | 757.1 | 703.5 | 704.1 | 128.2 | 191.2 | 244.4 | 205.6 | 305.9 | 298 | 188.5 | 267.1 | 341.5 | 252.6
1984.4 | 1765.4 | 557.3 | 222.92 | 260.5806 | 323.9 | 272.2 | 288.5 | 282.9 | 549.9 | 50.3 | 19.5 | 91.3 | 7 | 286.3 | 4.3 | 928.9 | 889.3 | 855.8 | 940.8 | 738.5 | 721.9 | 793.5 | 761.5 | 703.4 | 707.4 | 128.3 | 191.3 | 244.8 | 205.8 | 305.8 | 298 | 188.6 | 267.3 | 342 | 252.8
1985.4 | 1766.4 | 556.9 | 222.76 | 260.3936 | 323.2 | 273 | 289 | 283.7 | 554.9 | 50.3 | 19.5 | 91.3 | 6.8 | 237.4 | 4.3 | 929.9 | 875.8 | 855.9 | 943.5 | 740.7 | 722.5 | 793 | 757.8 | 705.4 | 708.8 | 128.4 | 191.4 | 245 | 206 | 305.9 | 298.3 | 188.7 | 267.4 | 342.6 | 252.9
1986.4 | 1767.4 | 558.2 | 223.28 | 261.0015 | 323.2 | 273.5 | 289.7 | 284.3 | 560.2 | 50.3 | 19.5 | 91.2 | 6.7 | 244.4 | 4.7 | 931 | 887.8 | 853.4 | 942.2 | 743.5 | 722.8 | 792.7 | 775.1 | 705.1 | 710 | 128.5 | 191.5 | 245.3 | 206.2 | 306 | 298.2 | 188.8 | 267.5 | 343.2 | 253.1
1987.4 | 1768.4 | 558.3 | 223.32 | 261.0482 | 322.5 | 274.1 | 290.1 | 284.5 | 573.3 | 50.2 | 19.5 | 91 | 7.5 | 263.9 | 4.5 | 930.8 | 887.2 | 843.7 | 934.2 | 744.4 | 723.9 | 787.3 | 773 | 704.5 | 710.4 | 128.6 | 191.6 | 245.4 | 206.4 | 306.7 | 298.1 | 189 | 267.7 | 343.7 | 253.2
1988.4 | 1769.4 | 558.7 | 223.48 | 261.2352 | 322.4 | 274.4 | 289.6 | 285.6 | 573 | 50.2 | 19.5 | 90.9 | 7.9 | 249.5 | 4.6 | 931.5 | 883 | 847.6 | 937.4 | 747.9 | 724.7 | 786.5 | 771.4 | 704.9 | 713.8 | 128.7 | 191.8 | 245.4 | 206.6 | 306.7 | 298 | 189 | 267.8 | 344.3 | 253.4
1989.4 | 1770.4 | 558.8 | 223.52 | 261.282 | 322.9 | 274 | 290.3 | 286 | 560.9 | 50.3 | 19.5 | 90.9 | 7.4 | 268.8 | 5.4 | 931.5 | 875.2 | 853.6 | 941.8 | 750.6 | 725.5 | 789.1 | 764.8 | 705 | 717.1 | 128.8 | 191.9 | 245.5 | 206.8 | 306.6 | 298.2 | 189.1 | 267.9 | 345 | 253.6
1990.4 | 1771.4 | 558.3 | 223.32 | 261.0482 | 323 | 274.4 | 289.9 | 285.3 | 552.5 | 50.3 | 19.5 | 91.1 | 7.8 | 285.3 | 7.4 | 931.9 | 854.7 | 854.6 | 943.9 | 752.3 | 726.1 | 787.7 | 756.5 | 704.7 | 715.6 | 128.9 | 192 | 245.8 | 207 | 306.6 | 298.3 | 189.3 | 268.2 | 345.7 | 253.7
1991.4 | 1772.4 | 557.9 | 223.16 | 260.8612 | 324.5 | 274.5 | 287.5 | 285.7 | 550.8 | 50.4 | 19.5 | 91.3 | 8.3 | 256.9 | 7.2 | 932.1 | 851.6 | 854.2 | 942.3 | 754 | 726.6 | 786.9 | 752.1 | 704.6 | 715.9 | 129.1 | 192.1 | 246.1 | 207.2 | 306.7 | 298.4 | 189.4 | 268.3 | 346.2 | 253.9
1992.4 | 1773.4 | 557.9 | 223.16 | 260.8612 | 323.3 | 274.9 | 287.6 | 285.6 | 549.6 | 50.4 | 19.5 | 91.4 | 8.3 | 273.3 | 5.7 | 931.5 | 845.6 | 848.9 | 940.3 | 753.9 | 727.2 | 787.8 | 745.7 | 705 | 717.7 | 129.2 | 192.2 | 246.1 | 207.4 | 306.9 | 298.5 | 189.5 | 268.4 | 346.7 | 254
1993.4 | 1774.4 | 558.2 | 223.28 | 261.0015 | 323 | 274.9 | 287.9 | 285.4 | 549.8 | 50.5 | 19.5 | 91.5 | 8.2 | 260.3 | 6 | 932.7 | 852.3 | 848.9 | 946 | 755.7 | 727.8 | 791.2 | 756.8 | 709.1 | 721.4 | 129.3 | 192.3 | 246.4 | 207.6 | 306.9 | 298.6 | 189.6 | 268.6 | 347.3 | 254.2
1994.4 | 1775.4 | 558.5 | 223.4 | 261.1417 | 322.3 | 274.3 | 287.7 | 285.2 | 553.2 | 50.6 | 19.5 | 91.5 | 8 | 249.2 | 6.8 | 933.1 | 847.9 | 843.2 | 948.7 | 755 | 728.5 | 780.8 | 747.6 | 708.4 | 719.4 | 129.4 | 192.4 | 246.4 | 207.8 | 307 | 299.2 | 189.7 | 268.7 | 348 | 254.3
1995.4 | 1776.4 | 558.3 | 223.32 | 261.0482 | 324.7 | 274.5 | 287.7 | 286.6 | 553.5 | 50.6 | 19.4 | 91.5 | 7.9 | 252.1 | 7.1 | 933.3 | 859.2 | 843.2 | 948 | 756.6 | 729.4 | 783.6 | 759.9 | 709.1 | 720.1 | 129.5 | 192.5 | 246.5 | 208 | 307.2 | 299.7 | 189.8 | 268.9 | 348.4 | 254.5
1996.4 | 1777.4 | 557.5 | 223 | 260.6742 | 326.4 | 274.2 | 289.2 | 287.6 | 563 | 50.6 | 19.5 | 91.5 | 8.1 | 250.9 | 6.8 | 934.3 | 867.9 | 842.8 | 948.8 | 758.9 | 729.7 | 787 | 769.5 | 709.7 | 723.7 | 129.6 | 192.6 | 246.9 | 208.3 | 307.4 | 300.1 | 189.9 | 269.1 | 348.8 | 254.6
1997.4 | 1778.4 | 558.2 | 223.28 | 261.0015 | 326.8 | 274.9 | 288.7 | 287.6 | 563.6 | 50.6 | 19.5 | 91.7 | 8.1 | 264.5 | 6.2 | 932.4 | 861.1 | 833.8 | 941.2 | 758.6 | 730.2 | 787.4 | 777.1 | 709.1 | 721.9 | 129.7 | 192.7 | 247.1 | 208.5 | 307.6 | 300.3 | 190 | 269.2 | 349.3 | 254.8
1998.4 | 1779.4 | 558.6 | 223.44 | 261.1885 | 327.7 | 274.6 | 289.2 | 288.4 | 560 | 50.6 | 19.4 | 91.9 | 8.2 | 281.7 | 5.7 | 929.8 | 859.4 | 826.2 | 932.3 | 757.3 | 731.2 | 786.3 | 774.6 | 709.2 | 719.5 | 129.8 | 192.8 | 247.3 | 208.7 | 307.3 | 300.6 | 190.1 | 269.4 | 349.8 | 254.9
1999.4 | 1780.4 | 559.1 | 223.64 | 261.4223 | 328 | 274.4 | 290.9 | 289 | 551.1 | 50.6 | 19.4 | 92 | 9.2 | 282 | 4.9 | 923.7 | 842.6 | 811.6 | 918.5 | 754.6 | 732.1 | 777.6 | 750.2 | 708.5 | 718.3 | 129.9 | 193 | 247.4 | 208.9 | 307.5 | 301.1 | 190.2 | 269.5 | 350.4 | 255.1
2000.4 | 1781.4 | 559.5 | 223.8 | 261.6093 | 327.1 | 274.4 | 291.7 | 290 | 541.8 | 50.6 | 19.4 | 91.9 | 8.6 | 284.5 | 4.3 | 922 | 835.9 | 800 | 914.1 | 751.5 | 732.9 | 779.7 | 733.5 | 710.9 | 715.9 | 130 | 193.1 | 247.6 | 209.1 | 307.5 | 301 | 190.3 | 269.7 | 350.9 | 255.3
2001.4 | 1782.4 | 558.4 | 223.36 | 261.095 | 326.8 | 274.9 | 291.1 | 291 | 538.5 | 50.6 | 19.4 | 91.9 | 8.9 | 259.2 | 4.6 | 923.5 | 841.8 | 794.4 | 918.5 | 750.8 | 733.7 | 782.5 | 742.8 | 713.6 | 717.8 | 130.1 | 193.2 | 247.8 | 209.3 | 307.9 | 300.7 | 190.4 | 269.9 | 351.3 | 255.4
2002.4 | 1783.4 | 558 | 223.2 | 260.9079 | 328.3 | 275.7 | 292.2 | 292.3 | 542.6 | 50.7 | 19.4 | 91.9 | 9.3 | 245.6 | 5.6 | 922 | 837 | 796.5 | 914.4 | 750.9 | 734.5 | 778.7 | 733.9 | 713.9 | 717.6 | 130.2 | 193.4 | 248.1 | 209.5 | 308.3 | 300.5 | 190.5 | 270 | 351.8 | 255.6
2003.4 | 1784.4 | 558.3 | 223.32 | 261.0482 | 329.4 | 275.6 | 292 | 292.9 | 540 | 50.7 | 19.4 | 91.9 | 10.1 | 273.6 | 5.9 | 921 | 833.6 | 797.4 | 912.2 | 750.9 | 735.4 | 770.3 | 743.1 | 712.8 | 714.8 | 130.4 | 193.5 | 248.1 | 209.7 | 309.5 | 300.4 | 190.6 | 270.3 | 352.3 | 255.8
2004.4 | 1785.4 | 558.6 | 223.44 | 261.1885 | 328.7 | 275.9 | 293.1 | 293.5 | 549.7 | 50.6 | 19.4 | 91.8 | 9.2 | 281.2 | 6.2 | 922.4 | 845.4 | 800.1 | 918.6 | 750.5 | 736.2 | 770.6 | 748.3 | 710.3 | 715.8 | 130.5 | 193.6 | 248.3 | 209.9 | 309.7 | 300.2 | 190.8 | 270.4 | 352.8 | 255.9
2005.4 | 1786.4 | 559.2 | 223.68 | 261.469 | 328.5 | 275.8 | 292.7 | 292.3 | 552.8 | 50.6 | 19.4 | 91.8 | 9.7 | 251.2 | 8.7 | 922.6 | 850.6 | 801.7 | 919.1 | 750 | 736.7 | 768.5 | 741.6 | 709.6 | 714.8 | 130.6 | 193.7 | 248.5 | 210.1 | 309.6 | 300.2 | 190.9 | 270.6 | 353.4 | 256.1
2006.4 | 1787.4 | 559.1 | 223.64 | 261.4223 | 329.5 | 275.7 | 293 | 292.6 | 548.4 | 50.6 | 19.4 | 91.7 | 9.8 | 281.4 | 11 | 920.5 | 847.2 | 812.2 | 913.2 | 749.4 | 737.5 | 759.4 | 735.4 | 707.1 | 711.2 | 130.7 | 193.8 | 248.6 | 210.3 | 310.1 | 300.4 | 190.9 | 270.7 | 354 | 256.2
2007.4 | 1788.4 | 559.9 | 223.96 | 261.7963 | 331.1 | 275.5 | 292.6 | 293.5 | 553.1 | 50.5 | 19.4 | 91.6 | 9.4 | 264.4 | 11.8 | 920.2 | 851.9 | 824.5 | 911.4 | 750.5 | 738.3 | 760.5 | 749.2 | 706.9 | 712.1 | 130.8 | 193.9 | 248.8 | 210.5 | 310.8 | 300.3 | 191.1 | 270.9 | 354.4 | 256.4
2008.4 | 1789.4 | 558.4 | 223.36 | 261.095 | 331.7 | 275.2 | 290.9 | 292.8 | 548.9 | 50.6 | 19.4 | 91.6 | 9.4 | 274.4 | 12 | 919.8 | 827 | 804.1 | 911.1 | 746.2 | 738.7 | 758 | 734.6 | 706.1 | 710.5 | 130.9 | 194 | 249 | 210.7 | 311.5 | 300.3 | 191.2 | 271.1 | 355 | 256.6
2009.4 | 1790.4 | 558.6 | 223.44 | 261.1885 | 330.5 | 275.1 | 290.7 | 292.6 | 541.8 | 50.7 | 19.4 | 91.6 | 8.7 | 268.7 | 11.9 | 919 | 826.8 | 799.1 | 912.7 | 745.5 | 739.4 | 761.7 | 732.6 | 706.8 | 709.6 | 131 | 194.2 | 249.1 | 210.9 | 311.3 | 300.4 | 191.3 | 271.2 | 355.5 | 256.7
2010.4 | 1791.4 | 558.3 | 223.32 | 261.0482 | 330.7 | 275.1 | 291.6 | 292.3 | 553.6 | 50.7 | 19.4 | 91.6 | 9 | 278.8 | 11.1 | 916.9 | 824.6 | 775.7 | 909 | 743.4 | 739.9 | 756.8 | 730.6 | 705.9 | 707.5 | 131.1 | 194.3 | 249.5 | 211 | 313.3 | 300.3 | 191.4 | 271.4 | 355.9 | 256.9
2011.4 | 1792.4 | 558.6 | 223.44 | 261.1885 | 331.2 | 275.7 | 291.4 | 291.7 | 550.3 | 50.9 | 19.4 | 91.7 | 8.8 | 289.5 | 10.4 | 908.4 | 798.8 | 746.3 | 890.5 | 738.9 | 740.6 | 740.8 | 706.1 | 704.5 | 701.8 | 131.2 | 194.5 | 249.6 | 211.2 | 313 | 300.7 | 191.5 | 271.5 | 356.4 | 257.1
2012.4 | 1793.4 | 557.7 | 223.08 | 260.7677 | 331.4 | 276.7 | 290.4 | 291.9 | 529.4 | 50.9 | 19.4 | 91.8 | 9.3 | 304.7 | 10 | 898.3 | 765.7 | 718.7 | 870.9 | 734.1 | 740.9 | 718 | 680 | 701.2 | 696.1 | 131.3 | 194.6 | 249.5 | 211.4 | 313.1 | 300.5 | 191.6 | 271.6 | 356.7 | 257.2
2013.4 | 1794.4 | 558 | 223.2 | 260.9079 | 330.8 | 277.4 | 290.9 | 291.8 | 514.3 | 51 | 19.4 | 91.8 | 9.2 | 317.4 | 8.6 | 886.4 | 740.8 | 694.1 | 847.4 | 729 | 741.5 | 699.8 | 659.7 | 699 | 690.8 | 131.5 | 194.8 | 250 | 211.6 | 313.6 | 300.3 | 191.7 | 271.7 | 357 | 257.4
2014.4 | 1795.4 | 558 | 223.2 | 260.9079 | 330.2 | 278 | 291.4 | 291.7 | 507.2 | 51 | 19.4 | 91.8 | 7.8 | 304.5 | 7.2 | 882.1 | 749 | 703.2 | 837.4 | 728.2 | 741.9 | 691.2 | 663 | 695.5 | 687.5 | 131.6 | 194.9 | 250.2 | 211.8 | 312.7 | 300 | 191.8 | 271.7 | 357.3 | 257.6
2015.4 | 1796.4 | 558.9 | 223.56 | 261.3288 | 332.3 | 278 | 290 | 290.8 | 508.4 | 51 | 19.4 | 91.9 | 7.6 | 297.8 | 7 | 879.3 | 768.5 | 715.2 | 834.5 | 726.6 | 742.7 | 690.4 | 668.4 | 693.2 | 685.9 | 131.7 | 195.1 | 250.2 | 211.9 | 312.6 | 299.7 | 192 | 271.8 | 357.6 | 257.7
2016.4 | 1797.4 | 559 | 223.6 | 261.3755 | 333.1 | 278.2 | 289.7 | 291 | 504.1 | 51 | 19.4 | 92.1 | 7.3 | 297.1 | 7.1 | 872.5 | 753 | 705.5 | 826.2 | 723.3 | 743.6 | 684.2 | 652.4 | 691.6 | 682.5 | 131.8 | 195.1 | 250.1 | 212.1 | 312.4 | 299.4 | 192 | 271.8 | 357.9 | 257.8
2017.4 | 1798.4 | 559.2 | 223.68 | 261.469 | 333.8 | 278.4 | 290.6 | 291.7 | 496 | 51 | 19.4 | 92.3 | 6.4 | 290.8 | 6.4 | 869 | 764.4 | 712.5 | 825.3 | 722.5 | 744.7 | 682.4 | 653.3 | 691.3 | 680.5 | 131.9 | 195.2 | 250.3 | 212.2 | 312.4 | 299.1 | 192.1 | 271.8 | 358.3 | 258
2018.4 | 1799.4 | 559.6 | 223.84 | 261.6561 | 334.1 | 277.4 | 289.7 | 291.9 | 500.6 | 51.1 | 19.4 | 92.5 | 5.9 | 294.3 | 5.3 | 868.4 | 791.6 | 720.6 | 827.9 | 722 | 745.5 | 692.1 | 673.1 | 691.1 | 680.1 | 132 | 195.3 | 250.6 | 212.4 | 311.7 | 298.7 | 192.2 | 271.9 | 358.6 | 258.1
2019.4 | 1800.4 | 558.7 | 223.48 | 261.2352 | 333.7 | 277.9 | 287.9 | 292 | 513.1 | 51 | 19.4 | 92.8 | 6.2 | 294.3 | 4.4 | 865.2 | 776.7 | 707.2 | 825.2 | 718.9 | 745.8 | 692.8 | 661.9 | 692.5 | 676.5 | 132.2 | 195.3 | 250.9 | 212.5 | 311.3 | 298.6 | 192.4 | 272 | 358.9 | 258.3
2020.4 | 1801.4 | 558.2 | 223.28 | 261.0015 | 333.5 | 277.3 | 287.3 | 291.8 | 505.9 | 51 | 19.4 | 93.1 | 6.5 | 295 | 3.8 | 863.6 | 758.3 | 702.7 | 827.8 | 715.5 | 746.4 | 688.4 | 648.1 | 693.7 | 673.9 | 132.3 | 195.4 | 250.9 | 212.6 | 311 | 298.9 | 192.5 | 272.1 | 359.1 | 258.4
2021.4 | 1802.4 | 559.4 | 223.76 | 261.5625 | 334.8 | 276.9 | 288 | 290.3 | 499.6 | 51 | 19.4 | 93.3 | 6.1 | 307.9 | 3.5 | 860.5 | 740.5 | 687 | 826.2 | 710.8 | 746.9 | 685.3 | 636.2 | 694.7 | 670.7 | 132.4 | 195.5 | 250.9 | 212.8 | 310.9 | 298.6 | 192.6 | 272.2 | 359.4 | 258.5
2022.4 | 1803.4 | 559.2 | 223.68 | 261.469 | 336.2 | 276.6 | 288.3 | 288 | 495 | 51 | 19.4 | 93.4 | 6.4 | 305.3 | 3.4 | 856.5 | 725.1 | 681.2 | 822 | 708.5 | 747.4 | 678.7 | 624.9 | 693.1 | 667.7 | 132.5 | 195.6 | 251.2 | 212.9 | 310.5 | 298.6 | 192.7 | 272.2 | 359.8 | 258.7
2023.4 | 1804.4 | 559.3 | 223.72 | 261.5158 | 336.2 | 276.4 | 288.1 | 286 | 493.2 | 50.9 | 19.4 | 93.5 | 6.1 | 315.7 | 3.3 | 852.8 | 714 | 671.8 | 814.5 | 705.6 | 747.8 | 674.1 | 617.5 | 693.1 | 664.6 | 132.6 | 195.7 | 251.4 | 213.1 | 310.4 | 298.4 | 192.8 | 272.2 | 360 | 258.8
2024.4 | 1805.4 | 559.5 | 223.8 | 261.6093 | 337.8 | 276.6 | 286.5 | 286.2 | 486 | 50.9 | 19.4 | 93.7 | 5.7 | 347.5 | 4.1 | 845.6 | 697.4 | 660.1 | 802.5 | 701.4 | 747.9 | 666.5 | 604.1 | 694.1 | 660.8 | 132.8 | 195.9 | 251.5 | 213.2 | 310.6 | 298.9 | 192.9 | 272.4 | 360.3 | 258.9
2025.4 | 1806.4 | 560.2 | 224.08 | 261.9366 | 338.8 | 276.2 | 286.4 | 286.2 | 476.8 | 50.9 | 19.4 | 93.9 | 6.4 | 185 | 4.9 | 838.3 | 692.1 | 647.3 | 791.2 | 698.2 | 747.9 | 657.7 | 592.2 | 694.6 | 657.1 | 132.9 | 196 | 251.5 | 213.4 | 310.9 | 298.6 | 193 | 272.5 | 360.5 | 259.1
2026.4 | 1807.4 | 560 | 224 | 261.8431 | 338.7 | 276.1 | 286.9 | 285.7 | 469.1 | 51 | 19.4 | 94 | 5.7 | 330.2 | 4.6 | 832.8 | 687.9 | 649.2 | 784.7 | 696 | 748.1 | 654 | 584.3 | 692.9 | 654.2 | 133 | 196 | 251.6 | 213.5 | 311 | 298.8 | 193.2 | 272.6 | 360.7 | 259.2
2027.4 | 1808.4 | 559.3 | 223.72 | 261.5158 | 338.7 | 275.3 | 286.2 | 286 | 470.6 | 51 | 19.4 | 94.3 | 5.8 | 342.9 | 3.4 | 834.1 | 708.3 | 670.2 | 790.4 | 696.7 | 748.1 | 670.1 | 602.9 | 692.8 | 654.8 | 133.1 | 196.1 | 251.8 | 213.7 | 310.2 | 298.7 | 193.2 | 272.7 | 360.9 | 259.4
2028.4 | 1809.4 | 559.2 | 223.68 | 261.469 | 337.7 | 274.6 | 284.8 | 285.9 | 483.5 | 51.1 | 19.4 | 94.3 | 5.8 | 46.3 | 2.8 | 838.6 | 739.3 | 698 | 801.6 | 698 | 747.9 | 684.3 | 623.3 | 692.3 | 656.6 | 133.2 | 196.2 | 252.1 | 213.8 | 309.6 | 299.1 | 193.4 | 272.7 | 361.2 | 259.5
2029.4 | 1810.4 | 558.6 | 223.44 | 261.1885 | 337.3 | 274.2 | 283.7 | 284.5 | 499.9 | 51.1 | 19.4 | 94.4 | 5.8 | 334.9 | 2.9 | 843.8 | 767 | 731.8 | 812.9 | 701.3 | 747.8 | 701 | 642.7 | 693.3 | 661.5 | 133.4 | 196.3 | 252.1 | 214 | 309.3 | 299 | 193.5 | 272.9 | 361.6 | 259.6
2030.4 | 1811.4 | 558.9 | 223.56 | 261.3288 | 336.2 | 274 | 283.2 | 283.2 | 498.9 | 51.1 | 19.4 | 94.6 | 5.6 | 275.8 | 4.1 | 844.6 | 774.9 | 742.9 | 809.5 | 703.5 | 747.9 | 704.8 | 645.8 | 693.2 | 662.6 | 133.5 | 196.4 | 252.1 | 214.1 | 309.4 | 298.8 | 193.6 | 273 | 362.1 | 259.7
2031.4 | 1812.4 | 559.6 | 223.84 | 261.6561 | 334.7 | 274.4 | 282.3 | 283.8 | 496.9 | 51.2 | 19.4 | 94.8 | 5.8 | 192.1 | 9 | 847.3 | 773.7 | 768.8 | 816.7 | 705.8 | 748.3 | 709.1 | 648.7 | 695 | 664.8 | 133.6 | 196.5 | 252.2 | 214.2 | 309.3 | 298.6 | 193.7 | 273.1 | 362.5 | 259.9
2032.4 | 1813.4 | 558.7 | 223.48 | 261.2352 | 333.3 | 274.8 | 282.6 | 283.6 | 506.2 | 51.3 | 19.4 | 94.9 | 6.1 | 180.3 | 12.1 | 853.1 | 790.6 | 785 | 832.2 | 708.8 | 748 | 718.2 | 670 | 695.2 | 667.7 | 133.7 | 196.6 | 252.3 | 214.3 | 309.2 | 298.3 | 193.8 | 273.1 | 362.9 | 260
2033.4 | 1814.4 | 558.3 | 223.32 | 261.0482 | 332 | 275.3 | 282.8 | 282.2 | 520.8 | 51.3 | 19.4 | 95 | 6.1 | 185.9 | 11.3 | 857 | 797 | 790.1 | 839.2 | 711.7 | 747.8 | 730.8 | 687.9 | 696.5 | 669.6 | 133.9 | 196.7 | 253 | 214.5 | 309.3 | 298.1 | 193.9 | 273.2 | 363.3 | 260.1
2034.4 | 1815.4 | 558.9 | 223.56 | 261.3288 | 331.1 | 275.3 | 282.7 | 282.1 | 535.2 | 51.4 | 19.4 | 95 | 6 | 319.9 | 9 | 862.1 | 794.9 | 805.9 | 854 | 714.3 | 748 | 733 | 691.5 | 695.2 | 670.9 | 134 | 196.7 | 253.3 | 214.6 | 309.5 | 297.9 | 194.1 | 273.3 | 363.8 | 260.2
2035.4 | 1816.4 | 559.1 | 223.64 | 261.4223 | 330.6 | 274.8 | 282.6 | 282 | 551.5 | 51.4 | 19.4 | 95.2 | 5.9 | 302.9 | 7.2 | 864 | 806.2 | 808.6 | 856.6 | 715.7 | 747.8 | 739.8 | 710.7 | 695 | 672.9 | 134.1 | 196.8 | 253.2 | 214.7 | 309.3 | 297.7 | 194.2 | 273.3 | 364.2 | 260.4
2036.4 | 1817.4 | 560.2 | 224.08 | 261.9366 | 330.9 | 274.5 | 283.7 | 282.3 | 553.6 | 51.5 | 19.4 | 95.2 | 5.2 | 294.4 | 7 | 862.9 | 804.7 | 812.2 | 849.2 | 715.7 | 748 | 741.2 | 707 | 695.9 | 671.6 | 134.2 | 196.9 | 253.4 | 214.8 | 309 | 297.6 | 194.3 | 273.4 | 364.6 | 260.5
2037.4 | 1818.4 | 560.7 | 224.28 | 262.1704 | 332.2 | 274.7 | 285.5 | 281.8 | 558.5 | 51.5 | 19.4 | 95.2 | 5.4 | 291.8 | 7.3 | 865.4 | 816.1 | 809.5 | 853.9 | 716.1 | 748.2 | 747.4 | 704.3 | 697.1 | 672.4 | 134.4 | 197 | 253.6 | 215 | 308.7 | 297.4 | 194.4 | 273.4 | 365 | 260.7
2038.4 | 1819.4 | 560.4 | 224.16 | 262.0301 | 333.3 | 275.4 | 286 | 281.3 | 552.9 | 51.6 | 19.4 | 95.3 | 6 | 302.1 | 6.7 | 868.1 | 818.3 | 793.5 | 860.8 | 715.9 | 748.1 | 754.1 | 707.6 | 698.7 | 674.8 | 134.5 | 197.1 | 253.7 | 215.1 | 308.5 | 297.4 | 194.5 | 273.5 | 365.4 | 260.8
2039.4 | 1820.4 | 561 | 224.4 | 262.3107 | 335.1 | 275.8 | 285.1 | 282 | 542.1 | 51.6 | 19.4 | 95.3 | 6.1 | 309.6 | 5.1 | 871.4 | 819.8 | 789.7 | 868.6 | 715.6 | 748.5 | 757.4 | 702.1 | 701.7 | 677.3 | 134.6 | 197.1 | 253.8 | 215.2 | 308.6 | 297.7 | 194.6 | 273.6 | 365.8 | 260.9
2040.4 | 1821.4 | 561.3 | 224.52 | 262.4509 | 335.3 | 275.8 | 286.9 | 283.6 | 536.3 | 51.6 | 19.4 | 95.4 | 6.4 | 304.4 | 4.4 | 874.6 | 821 | 797.6 | 875.7 | 717.2 | 749 | 760.7 | 692.4 | 704.4 | 678.6 | 134.7 | 197.2 | 253.9 | 215.3 | 308.7 | 298.6 | 194.7 | 273.8 | 366.1 | 261
2041.4 | 1822.4 | 560.5 | 224.2 | 262.0769 | 336.8 | 275.5 | 288.4 | 284.4 | 532.5 | 51.6 | 19.4 | 95.4 | 7 | 316.4 | 3.7 | 877.3 | 816.6 | 790.6 | 880.2 | 716.6 | 749.2 | 765.3 | 687.8 | 705.5 | 679.3 | 134.9 | 197.3 | 254 | 215.5 | 308.7 | 298.9 | 194.8 | 274 | 366.5 | 261.1
2042.4 | 1823.4 | 558.8 | 223.52 | 261.282 | 338.9 | 274.9 | 288.2 | 285.1 | 536.9 | 51.7 | 19.4 | 95.4 | 7.6 | 333.5 | 3.6 | 879.3 | 809.4 | 787.6 | 880.1 | 716.5 | 749.4 | 771.5 | 699.6 | 709 | 680.9 | 135 | 197.4 | 254.3 | 215.6 | 308.5 | 299.1 | 194.9 | 274.2 | 366.8 | 261.3
2043.4 | 1824.4 | 559.1 | 223.64 | 261.4223 | 340.1 | 274.2 | 289.5 | 286.2 | 541.9 | 51.8 | 19.4 | 95.3 | 7.1 | 335.7 | 4.3 | 882.9 | 818.2 | 787.9 | 884.8 | 717.1 | 749.3 | 776.8 | 713.5 | 710.9 | 685.9 | 135.1 | 197.5 | 254.5 | 215.8 | 308.7 | 299.5 | 195.1 | 274.3 | 367.2 | 261.4
2044.4 | 1825.4 | 559.4 | 223.76 | 261.5625 | 341.4 | 273.5 | 290.6 | 287.5 | 554.6 | 51.9 | 19.4 | 95.3 | 8.4 | 326.1 | 4.7 | 887 | 834.3 | 798 | 894.6 | 718.9 | 749.2 | 782.3 | 729.4 | 712.5 | 688.5 | 135.2 | 197.6 | 254.9 | 216 | 308.7 | 299.8 | 195.2 | 274.4 | 367.5 | 261.5
2045.4 | 1826.4 | 560.7 | 224.28 | 262.1704 | 341.6 | 273 | 290.1 | 288.9 | 558.1 | 51.8 | 19.4 | 95.2 | 9.1 | 322 | 4.3 | 889 | 831.3 | 799.7 | 894.6 | 718.6 | 749.6 | 776.1 | 733.2 | 712.5 | 687 | 135.4 | 197.7 | 255.1 | 216.1 | 308.9 | 299.9 | 195.3 | 274.5 | 367.9 | 261.7
2046.4 | 1827.4 | 560.1 | 224.04 | 261.8899 | 342.6 | 272.6 | 289.7 | 290.2 | 556.2 | 51.8 | 19.4 | 95.1 | 8.9 | 302.1 | 4.3 | 891.4 | 833 | 805.3 | 896.7 | 719.1 | 749.9 | 780.5 | 739 | 712.5 | 689.8 | 135.5 | 197.7 | 255.2 | 216.3 | 308.8 | 299.9 | 195.4 | 274.5 | 368.2 | 261.8
2047.4 | 1828.4 | 559.7 | 223.88 | 261.7028 | 343.8 | 272.5 | 290.1 | 291.5 | 571.1 | 51.8 | 19.4 | 94.9 | 8.6 | 296.7 | 5.5 | 894.9 | 846.6 | 817.4 | 904.9 | 722.4 | 749.9 | 783 | 760.5 | 712.6 | 693.8 | 135.6 | 197.8 | 255.4 | 216.4 | 308.8 | 299.9 | 195.5 | 274.6 | 368.6 | 262
2048.4 | 1829.4 | 559.1 | 223.64 | 261.4223 | 343.7 | 273 | 290.4 | 291.6 | 583.8 | 51.9 | 19.4 | 94.8 | 8.6 | 321.2 | 5.6 | 898.8 | 855.2 | 828 | 915 | 725.7 | 749.8 | 786.5 | 773 | 713.1 | 698 | 135.8 | 197.9 | 255.5 | 216.6 | 309 | 299.9 | 195.6 | 274.7 | 369 | 262.1
2049.4 | 1830.4 | 560.3 | 224.12 | 261.9834 | 344.2 | 274.7 | 289.4 | 291.6 | 595.2 | 51.9 | 19.4 | 94.6 | 8.5 | 276.4 | 5.9 | 901.9 | 869.9 | 837.5 | 920.4 | 729.7 | 750 | 787.8 | 787 | 713.8 | 701.5 | 135.9 | 198 | 255.7 | 216.7 | 309.3 | 299.8 | 195.7 | 274.8 | 369.4 | 262.2
2050.4 | 1831.4 | 560.1 | 224.04 | 261.8899 | 343.5 | 276.1 | 288.2 | 292 | 606.2 | 51.9 | 19.4 | 94.5 | 8 | 262 | 6.4 | 904.3 | 873.1 | 844.4 | 925.5 | 733.2 | 750.1 | 791.5 | 790.6 | 713.9 | 706.9 | 136 | 198.1 | 256 | 216.8 | 309.5 | 299.9 | 195.8 | 274.9 | 370 | 262.4
2051.4 | 1832.4 | 559.7 | 223.88 | 261.7028 | 343.6 | 277.1 | 288.5 | 291.7 | 603.5 | 52 | 19.3 | 94.4 | 7.7 | 272.7 | 6.1 | 906.8 | 872.1 | 851.7 | 933.5 | 736 | 750.4 | 792.3 | 791.1 | 716.4 | 708.9 | 136.2 | 198.2 | 256.1 | 216.9 | 309.7 | 299.9 | 195.9 | 275 | 370.4 | 262.5
2052.4 | 1833.4 | 560.2 | 224.08 | 261.9366 | 345.4 | 277.4 | 288.8 | 292.4 | 596.1 | 52.1 | 19.3 | 94.3 | 7.9 | 262.8 | 5.7 | 908.6 | 861.7 | 848.2 | 935.8 | 739.6 | 750.7 | 790.3 | 784 | 714.9 | 710.6 | 136.3 | 198.3 | 256.1 | 217.1 | 310.2 | 300.2 | 196 | 275.2 | 370.9 | 262.6
2053.4 | 1834.4 | 559.8 | 223.92 | 261.7496 | 345.7 | 277.6 | 287.3 | 293.7 | 589.9 | 52.2 | 19.3 | 94.3 | 7.8 | 257.2 | 5.6 | 910 | 848.9 | 833.2 | 932.6 | 740 | 751.2 | 787 | 780.1 | 715.3 | 711.7 | 136.4 | 198.4 | 256.2 | 217.2 | 310.5 | 300.4 | 196.1 | 275.4 | 371.4 | 262.8
2054.4 | 1835.4 | 559.4 | 223.76 | 261.5625 | 345 | 277.6 | 287.5 | 293.8 | 576.5 | 52.2 | 19.3 | 94.4 | 7.7 | 260.9 | 5.6 | 911.6 | 844.6 | 833.7 | 934.7 | 739.4 | 751.7 | 787.7 | 764.4 | 717.7 | 711.7 | 136.6 | 198.5 | 256.3 | 217.3 | 310.8 | 300.4 | 196.2 | 275.5 | 371.9 | 262.9
2055.4 | 1836.4 | 559.8 | 223.92 | 261.7496 | 345.3 | 277.4 | 288.3 | 294 | 572.3 | 52.2 | 19.3 | 94.5 | 7.6 | 271.1 | 6.4 | 913 | 846 | 842.1 | 937 | 741.7 | 752.2 | 792.2 | 765.8 | 720.2 | 715.3 | 136.7 | 198.6 | 256.6 | 217.4 | 310.8 | 300.5 | 196.3 | 275.7 | 372.3 | 263.1
2056.4 | 1837.4 | 560.6 | 224.24 | 262.1236 | 346 | 276.8 | 289.1 | 293.9 | 570.1 | 52.2 | 19.3 | 94.4 | 7.9 | 261.4 | 6.6 | 913.7 | 848.5 | 850.7 | 940.3 | 746.3 | 752.6 | 793.4 | 773.1 | 722.7 | 718.6 | 136.8 | 198.7 | 257 | 217.6 | 310.9 | 300.7 | 196.5 | 275.8 | 372.7 | 263.2
2057.4 | 1838.4 | 559.9 | 223.96 | 261.7963 | 345.1 | 276 | 289.4 | 294.8 | 565 | 52.2 | 19.3 | 94.3 | 8.1 | 281 | 6.3 | 914.8 | 841.5 | 833.2 | 938.3 | 745.2 | 752.9 | 792.6 | 761.2 | 722.4 | 718.4 | 137 | 198.8 | 257.2 | 217.7 | 311 | 301.2 | 196.6 | 276 | 373.2 | 263.4
2058.4 | 1839.4 | 559.5 | 223.8 | 261.6093 | 343.2 | 274.9 | 290.1 | 295.1 | 556.9 | 52.1 | 19.3 | 94.3 | 8.1 | 288.2 | 6 | 915.4 | 831.7 | 813.7 | 936.6 | 743 | 753.6 | 791.2 | 747.4 | 722.9 | 716.7 | 137.1 | 198.9 | 257.2 | 217.9 | 311.1 | 301.4 | 196.7 | 276.2 | 373.7 | 263.5
2059.4 | 1840.4 | 559.6 | 223.84 | 261.6561 | 345.1 | 274.6 | 290.8 | 295.4 | 546.5 | 52 | 19.3 | 94.2 | 7.7 | 283.1 | 6.2 | 916.2 | 819.5 | 811.6 | 938.5 | 741.6 | 753.9 | 791.7 | 743.8 | 724.5 | 717.1 | 137.2 | 199.1 | 257.3 | 218 | 311.3 | 301.6 | 196.8 | 276.4 | 374.2 | 263.7
2060.4 | 1841.4 | 559.7 | 223.88 | 261.7028 | 345.1 | 274.7 | 291.3 | 295.1 | 540 | 52 | 19.3 | 94.1 | 8.1 | 283.8 | 7.1 | 917.7 | 823.1 | 819.5 | 943.7 | 743.6 | 754.3 | 795 | 749.6 | 726.6 | 719.7 | 137.4 | 199.2 | 257.5 | 218.2 | 312.1 | 302 | 196.9 | 276.5 | 374.5 | 263.8
2061.4 | 1842.4 | 561.2 | 224.48 | 262.4042 | 343.5 | 275 | 291.1 | 293.9 | 535.8 | 52 | 19.3 | 94 | 7.6 | 267.6 | 7.7 | 917.5 | 815.7 | 814.2 | 944.1 | 743.9 | 754.9 | 789.8 | 733.2 | 726.8 | 718.2 | 137.5 | 199.4 | 257.5 | 218.4 | 313 | 302.4 | 197 | 276.7 | 374.9 | 264
2062.4 | 1843.4 | 561.5 | 224.6 | 262.5445 | 343.7 | 275.7 | 292.3 | 294.6 | 526.4 | 52.1 | 19.3 | 94 | 6.9 | 272.7 | 7.8 | 915.3 | 807.2 | 789 | 935.2 | 740.7 | 755.8 | 782.5 | 720.6 | 724.9 | 716.6 | 137.6 | 199.5 | 257.6 | 218.6 | 312.7 | 302.6 | 197.1 | 276.9 | 375.2 | 264.2
2063.4 | 1844.4 | 560.9 | 224.36 | 262.2639 | 345.6 | 275.4 | 292.3 | 296.1 | 522 | 52.2 | 19.3 | 93.9 | 7.4 | 273.5 | 7.9 | 910.6 | 790.4 | 784 | 921.6 | 739.8 | 756.8 | 767.8 | 709.7 | 723 | 712 | 137.8 | 199.7 | 257.7 | 218.7 | 312.7 | 302.8 | 197.2 | 277 | 375.6 | 264.3
2064.4 | 1845.4 | 559.7 | 223.88 | 261.7028 | 347.2 | 275.6 | 292.2 | 296.3 | 523.1 | 52.3 | 19.3 | 93.8 | 8.1 | 282.6 | 8.5 | 905.6 | 778.6 | 762.8 | 913.9 | 736.1 | 757.9 | 747.7 | 691.9 | 719.9 | 707.5 | 137.9 | 199.8 | 257.8 | 218.9 | 313.2 | 303.1 | 197.4 | 277.2 | 375.9 | 264.4
2065.4 | 1846.4 | 560.6 | 224.24 | 262.1236 | 348 | 274.6 | 292.2 | 295.9 | 516.8 | 52.4 | 19.3 | 93.7 | 8.3 | 255.5 | 8.3 | 901.6 | 781.5 | 763.5 | 906.6 | 734.2 | 759 | 738.7 | 685.7 | 719.1 | 704.5 | 138 | 200 | 257.9 | 219.1 | 314.7 | 303.8 | 197.4 | 277.4 | 376.1 | 264.6
2066.4 | 1847.4 | 560.8 | 224.32 | 262.2172 | 348.2 | 274.2 | 292.7 | 296 | 505.1 | 52.4 | 19.3 | 93.7 | 8.9 | 246.8 | 7.8 | 898.5 | 781.5 | 767.1 | 901.1 | 732.7 | 760 | 728.8 | 671.4 | 718.5 | 701 | 138.2 | 200.1 | 258 | 219.3 | 314.5 | 303.9 | 197.6 | 277.7 | 376.3 | 264.8
2067.4 | 1848.4 | 561.1 | 224.44 | 262.3574 | 347.9 | 273.6 | 293.6 | 296.6 | 503.9 | 52.5 | 19.3 | 93.7 | 9.5 | 261.7 | 8 | 898.6 | 781 | 777.3 | 903.2 | 733.7 | 760.8 | 731.3 | 670.2 | 716 | 701.3 | 138.3 | 200.3 | 258.2 | 219.5 | 314.4 | 304.2 | 197.7 | 277.8 | 376.5 | 264.9
2068.4 | 1849.4 | 560.2 | 224.08 | 261.9366 | 348 | 273.2 | 292.6 | 295.9 | 516.6 | 52.6 | 19.3 | 93.9 | 9.6 | 272.5 | 9.8 | 897.2 | 786.5 | 768.9 | 902.6 | 732.4 | 761.2 | 731.1 | 672.9 | 715.2 | 699.7 | 138.5 | 200.4 | 258.5 | 219.6 | 314.4 | 304.4 | 197.8 | 278 | 376.8 | 265.1
2069.4 | 1850.4 | 560.8 | 224.32 | 262.2172 | 348.5 | 273 | 293.3 | 295.6 | 521.4 | 52.6 | 19.3 | 94.1 | 9.1 | 265.5 | 11.4 | 894.6 | 779.9 | 758 | 897.3 | 728.9 | 761.9 | 727 | 671.9 | 716.2 | 695.6 | 138.6 | 200.6 | 258.7 | 219.8 | 314.5 | 304.6 | 197.9 | 278.1 | 377.2 | 265.2
2070.4 | 1851.4 | 560.9 | 224.36 | 262.2639 | 349.8 | 272.9 | 294.8 | 295.5 | 519.3 | 52.6 | 19.3 | 94.3 | 9 | 270.1 | 11.3 | 895.9 | 786.5 | 766.5 | 900.6 | 729.2 | 762.3 | 736.5 | 673.5 | 715.6 | 695.2 | 138.7 | 200.8 | 258.7 | 220 | 314.5 | 304.7 | 198 | 278.2 | 377.4 | 265.4
2071.4 | 1852.4 | 560.5 | 224.2 | 262.0769 | 351.1 | 273 | 293.8 | 295 | 526 | 52.7 | 19.3 | 94.3 | 8.8 | 266.1 | 11.3 | 895.8 | 796.1 | 780.4 | 899.5 | 729.9 | 762.8 | 736.3 | 682.9 | 713.2 | 694.4 | 138.9 | 200.9 | 258.8 | 220.1 | 314.2 | 304.7 | 198.2 | 278.3 | 377.8 | 265.5
2072.4 | 1853.4 | 560.3 | 224.12 | 261.9834 | 350.7 | 273.6 | 291.9 | 295.5 | 530.4 | 52.7 | 19.3 | 94.4 | 9.2 | 241.1 | 11.6 | 896.8 | 794.9 | 800.5 | 904.3 | 731.4 | 763 | 741.9 | 681.5 | 712.7 | 697 | 139 | 201.1 | 258.8 | 220.3 | 313.8 | 304.5 | 198.3 | 278.4 | 378.1 | 265.6
2073.4 | 1854.4 | 561 | 224.4 | 262.3107 | 351.7 | 273.9 | 291.8 | 295.8 | 529 | 52.8 | 19.3 | 94.5 | 9.9 | 255 | 10.6 | 896.2 | 795.2 | 805.4 | 904.3 | 732.4 | 762.9 | 747.6 | 682.4 | 714.3 | 699.2 | 139.2 | 201.2 | 259 | 220.4 | 313.8 | 304.6 | 198.4 | 278.5 | 378.5 | 265.8
2074.4 | 1855.4 | 559.7 | 223.88 | 261.7028 | 351.4 | 274 | 291.3 | 296.4 | 528.9 | 52.8 | 19.3 | 94.7 | 10.3 | 277 | 13.1 | 895.4 | 785.6 | 801.9 | 904.4 | 731.7 | 763.3 | 743.1 | 674.3 | 716 | 697.8 | 139.3 | 201.4 | 259.1 | 220.6 | 313.8 | 305.1 | 198.5 | 278.6 | 378.8 | 265.9
2075.4 | 1856.4 | 560 | 224 | 261.8431 | 352.2 | 273.7 | 291.6 | 297 | 524 | 52.8 | 19.3 | 94.8 | 9.6 | 259.3 | 13.3 | 893.6 | 782.8 | 802.6 | 899.8 | 730.4 | 763.8 | 737.9 | 671.6 | 716.3 | 697.3 | 139.4 | 201.5 | 259.3 | 220.8 | 313.9 | 305.6 | 198.6 | 278.8 | 379.1 | 266
2076.4 | 1857.4 | 559.6 | 223.84 | 261.6561 | 351.8 | 273.5 | 293 | 295.6 | 523.6 | 52.8 | 19.3 | 94.8 | 9.9 | 263.4 | 13.1 | 891 | 791.5 | 811.7 | 895 | 730.8 | 764.2 | 738.8 | 683.2 | 716.3 | 696.8 | 139.6 | 201.6 | 259.4 | 220.9 | 313.8 | 305.7 | 198.7 | 279 | 379.3 | 266.2
2077.4 | 1858.4 | 559.1 | 223.64 | 261.4223 | 351.4 | 273.4 | 293.7 | 294.9 | 520.7 | 52.7 | 19.3 | 94.8 | 9.9 | 263.2 | 15.9 | 893.9 | 794.5 | 814.3 | 905.2 | 732.4 | 764.1 | 740 | 688.9 | 714.3 | 697.5 | 139.7 | 201.6 | 259.3 | 221.1 | 313.7 | 305.7 | 198.8 | 279.2 | 379.6 | 266.3
2078.4 | 1859.4 | 559.8 | 223.92 | 261.7496 | 352.3 | 273.7 | 293.7 | 294.4 | 509.1 | 52.7 | 19.3 | 94.9 | 11.7 | 266 | 17.3 | 895.1 | 792.8 | 802.2 | 910.7 | 730.8 | 764 | 735.1 | 685.9 | 713.6 | 696.5 | 139.9 | 201.7 | 259.6 | 221.3 | 313.9 | 305.8 | 199 | 279.3 | 380 | 266.5
2079.4 | 1860.4 | 559.7 | 223.88 | 261.7028 | 353.4 | 273.3 | 292.6 | 293.4 | 502.6 | 52.6 | 19.3 | 95 | 13.7 | 264.6 | 16.8 | 892.3 | 784.9 | 802.3 | 904.4 | 730.9 | 764.5 | 732.1 | 687.1 | 713.6 | 694.8 | 140 | 201.8 | 259.8 | 221.4 | 314.1 | 305.7 | 199.1 | 279.4 | 380.2 | 266.6
2080.4 | 1861.4 | 560.1 | 224.04 | 261.8899 | 352.1 | 273.4 | 292.2 | 293.9 | 512.1 | 52.6 | 19.3 | 95 | 12.4 | 263.2 | 16.9 | 891.2 | 785.2 | 792 | 905.1 | 729.4 | 764.9 | 729.1 | 690.7 | 712 | 693.8 | 140.2 | 201.8 | 259.9 | 221.6 | 313.8 | 305.7 | 199.3 | 279.6 | 380.4 | 266.7
2081.4 | 1862.4 | 559.9 | 223.96 | 261.7963 | 352.6 | 274.4 | 292 | 293.7 | 512.7 | 52.5 | 19.3 | 94.9 | 10.6 | 267.8 | 15.6 | 892.1 | 779.7 | 779.8 | 907 | 729.2 | 765.3 | 728.3 | 675.2 | 711 | 692.9 | 140.3 | 201.9 | 260 | 221.7 | 313.4 | 305.5 | 199.4 | 279.6 | 380.7 | 266.8
2082.4 | 1863.4 | 560.7 | 224.28 | 262.1704 | 352.4 | 275 | 291.8 | 294.5 | 504.8 | 52.4 | 19.3 | 94.9 | 10.6 | 266.9 | 16.4 | 888.4 | 770.4 | 765.3 | 898.7 | 725.6 | 765.6 | 720.2 | 663.6 | 710.1 | 689 | 140.5 | 201.9 | 260.1 | 221.9 | 313.3 | 305.3 | 199.5 | 279.7 | 381 | 266.9
2083.4 | 1864.4 | 560.6 | 224.24 | 262.1236 | 353.5 | 274.8 | 292.4 | 295.1 | 494.6 | 52.3 | 19.3 | 94.9 | 11.1 | 262.1 | 16.9 | 887.3 | 774.7 | 764.8 | 895 | 724.5 | 766.1 | 712.7 | 651.7 | 708.8 | 685.9 | 140.6 | 202 | 260.3 | 222 | 313.1 | 305.1 | 199.6 | 279.8 | 381.2 | 267.1
2084.4 | 1865.4 | 559.2 | 223.68 | 261.469 | 355.7 | 274.6 | 293.2 | 294.3 | 494.4 | 52.3 | 19.3 | 95 | 11 | 258.4 | 16.1 | 885.1 | 781.4 | 768.3 | 886.8 | 724.4 | 766.6 | 707.9 | 662.2 | 707.8 | 685.1 | 140.8 | 202.2 | 260.5 | 222.2 | 312.9 | 305 | 199.7 | 279.9 | 381.4 | 267.2
2085.4 | 1866.4 | 558.9 | 223.56 | 261.3288 | 355.7 | 274.6 | 294.7 | 293.1 | 493 | 52.4 | 19.3 | 95 | 11.5 | 258.2 | 15.1 | 882.3 | 786.6 | 762.5 | 879 | 721.2 | 767.3 | 702.8 | 665 | 706 | 682.5 | 140.9 | 202.3 | 260.6 | 222.3 | 312.4 | 305 | 199.8 | 280 | 381.5 | 267.3
2086.4 | 1867.4 | 559.1 | 223.64 | 261.4223 | 356.8 | 274.2 | 294.7 | 292.7 | 496.6 | 52.5 | 19.3 | 95.2 | 12.1 | 270.4 | 15.3 | 881.6 | 791.6 | 775.4 | 878.1 | 720 | 767.7 | 705.8 | 665.7 | 704.7 | 681 | 141.1 | 202.4 | 260.6 | 222.5 | 312.1 | 305 | 199.9 | 280.1 | 381.7 | 267.4
2087.4 | 1868.4 | 559.2 | 223.68 | 261.469 | 358 | 273.9 | 294.8 | 290.7 | 504.9 | 52.5 | 19.3 | 95.3 | 11.6 | 272.4 | 15.9 | 884.3 | 806.6 | 779.6 | 885 | 720.5 | 767.9 | 707.6 | 677.6 | 705.7 | 680.3 | 141.2 | 202.6 | 261 | 222.6 | 312 | 305.6 | 200.1 | 280.2 | 381.9 | 267.5
2088.4 | 1869.4 | 559.3 | 223.72 | 261.5158 | 358.5 | 273.9 | 295.4 | 291 | 513.6 | 52.4 | 19.3 | 95.4 | 10.2 | 257.9 | 16 | 885.5 | 815.8 | 794.1 | 888.5 | 721.3 | 768 | 714.1 | 693.6 | 706.8 | 681.7 | 141.4 | 202.6 | 261.2 | 222.8 | 311.8 | 305.8 | 200.2 | 280.3 | 382.1 | 267.7
2089.4 | 1870.4 | 559 | 223.6 | 261.3755 | 357.6 | 273.1 | 296 | 291.5 | 516.5 | 52.4 | 19.3 | 95.5 | 10.1 | 255.8 | 15.5 | 887.2 | 821.4 | 806.3 | 894.3 | 723.4 | 767.8 | 720.6 | 700.8 | 706.3 | 682.5 | 141.5 | 202.8 | 261.1 | 222.9 | 311.9 | 306 | 200.3 | 280.4 | 382.4 | 267.8
2090.4 | 1871.4 | 557.9 | 223.16 | 260.8612 | 356.3 | 272.3 | 296 | 290.9 | 517.6 | 52.1 | 19.3 | 95.4 | 10.6 | 269.6 | 15.3 | 887.9 | 820.1 | 791.8 | 897.2 | 723 | 767.5 | 725.8 | 702.2 | 706.4 | 683.2 | 141.7 | 202.9 | 261.1 | 223.1 | 311.9 | 306.2 | 200.4 | 280.5 | 382.7 | 267.9
2091.4 | 1872.4 | 559.1 | 223.64 | 261.4223 | 355.3 | 272.2 | 295.5 | 291.2 | 513.8 | 52 | 19.3 | 95.3 | 9.7 | 265.2 | 14.9 | 887.2 | 819.4 | 778 | 893.6 | 720.1 | 767.4 | 722 | 698.6 | 707.4 | 681.7 | 141.9 | 203 | 261.4 | 223.2 | 311.8 | 306.3 | 200.5 | 280.7 | 383 | 268.1
2092.4 | 1873.4 | 559.2 | 223.68 | 261.469 | 356.4 | 271.9 | 295.2 | 292.6 | 509.6 | 51.8 | 19.3 | 95.2 | 9.5 | 267.1 | 14 | 881.9 | 796.9 | 762.6 | 877.1 | 717.6 | 767.7 | 707.9 | 683.4 | 707.4 | 678.9 | 142 | 203.1 | 261.7 | 223.4 | 312 | 306.2 | 200.7 | 280.8 | 383.2 | 268.2
2093.4 | 1874.4 | 559 | 223.6 | 261.3755 | 358 | 271.3 | 295.9 | 292.2 | 507 | 51.7 | 19.3 | 95.1 | 10 | 272 | 13.1 | 878.2 | 784.6 | 758.1 | 870.6 | 715.7 | 768 | 703.7 | 678.1 | 705.8 | 677 | 142.2 | 203.2 | 261.8 | 223.5 | 312.4 | 306.1 | 200.8 | 280.9 | 383.4 | 268.3
2094.4 | 1875.4 | 558.9 | 223.56 | 261.3288 | 359.3 | 271.1 | 295.4 | 293.1 | 511.1 | 51.7 | 19.3 | 95 | 9.8 | 267.7 | 12.7 | 878.8 | 783.2 | 767.9 | 875.6 | 717.5 | 768.3 | 708.4 | 682.7 | 706.8 | 677.9 | 142.3 | 203.4 | 261.8 | 223.7 | 312.2 | 306.9 | 200.9 | 281 | 383.6 | 268.5
2095.4 | 1876.4 | 559.4 | 223.76 | 261.5625 | 358.8 | 272.7 | 295 | 295.5 | 517 | 51.7 | 19.3 | 95 | 9 | 262.8 | 12.4 | 877.5 | 763.1 | 747.3 | 876.9 | 715.4 | 768.1 | 704.4 | 675.1 | 705.1 | 676.6 | 142.5 | 203.6 | 262 | 223.9 | 312 | 307.1 | 201.1 | 281.2 | 383.8 | 268.6
2096.4 | 1877.4 | 559.9 | 223.96 | 261.7963 | 359.6 | 272.7 | 294.6 | 296.3 | 509 | 51.7 | 19.3 | 95.1 | 9.4 | 263.2 | 12.1 | 872.9 | 743.3 | 723.1 | 870.8 | 711 | 768.3 | 690.1 | 657 | 707.7 | 671.5 | 142.6 | 203.8 | 262 | 224 | 311.7 | 306.9 | 201.1 | 281.4 | 384 | 268.8
2097.4 | 1878.4 | 559.7 | 223.88 | 261.7028 | 360.2 | 272.8 | 295.2 | 295 | 501.6 | 51.7 | 19.3 | 95.2 | 9.1 | 267.4 | 11.1 | 865.4 | 719.7 | 689.9 | 855.6 | 706.8 | 768.5 | 675.7 | 642.6 | 703.4 | 667.2 | 142.8 | 204 | 262.1 | 224.2 | 311.4 | 306.7 | 201.2 | 281.4 | 384.2 | 268.9
2098.4 | 1879.4 | 559.3 | 223.72 | 261.5158 | 358.2 | 273.6 | 295.6 | 294.1 | 493.6 | 51.7 | 19.3 | 95.4 | 9.3 | 274.5 | 9.7 | 853.5 | 697.2 | 662.9 | 828.9 | 701.6 | 768.3 | 660.3 | 622.8 | 701.5 | 662.8 | 142.9 | 204.3 | 262.3 | 224.4 | 311 | 306.6 | 201.4 | 281.4 | 384.4 | 269.1
2099.4 | 1880.4 | 561.4 | 224.56 | 262.4977 | 355.3 | 274.5 | 295.6 | 294.5 | 480.2 | 51.9 | 19.3 | 95.4 | 10 | 260.2 | 9.9 | 841.2 | 667.9 | 637.8 | 807.1 | 696.9 | 767.6 | 640.6 | 602.7 | 698.9 | 658.3 | 143.1 | 204.5 | 262.2 | 224.5 | 310.6 | 306.5 | 201.5 | 281.5 | 384.4 | 269.2
2100.4 | 1881.4 | 561.9 | 224.76 | 262.7315 | 356.6 | 274.6 | 295.8 | 294.8 | 466.9 | 52.1 | 19.3 | 95.4 | 9.6 | 268.5 | 10.5 | 829.1 | 638.1 | 614 | 789.5 | 692.1 | 766.5 | 624.8 | 588.7 | 700.1 | 654.4 | 143.2 | 204.8 | 262.5 | 224.6 | 309.7 | 306.1 | 201.6 | 281.5 | 384.4 | 269.3
2101.4 | 1882.4 | 563.6 | 225.44 | 263.5264 | 358.4 | 274.2 | 295.2 | 294.6 | 460.5 | 52.3 | 19.3 | 95.5 | 9.3 | 263.2 | 10.2 | 821.7 | 629 | 608.7 | 782.5 | 688.5 | 765.8 | 612.8 | 576.5 | 702.1 | 650.2 | 143.4 | 205 | 262.8 | 224.8 | 308.9 | 305.2 | 201.8 | 281.4 | 384.4 | 269.4
2102.4 | 1883.4 | 562.3 | 224.92 | 262.9185 | 357.1 | 273.3 | 294.3 | 293 | 452.1 | 52.4 | 19.3 | 95.6 | 8.9 | 269.3 | 9.9 | 817.6 | 636.7 | 609.7 | 779.7 | 686.4 | 766.1 | 608.3 | 571.1 | 695.9 | 646.5 | 143.6 | 205.1 | 262.7 | 224.9 | 308 | 304.3 | 201.8 | 281.3 | 384.4 | 269.4
2103.4 | 1884.4 | 561 | 224.4 | 262.3107 | 355.1 | 272.8 | 294.3 | 291.9 | 454.5 | 52.5 | 19.3 | 95.9 | 9.3 | 272.4 | 11 | 818.6 | 672.8 | 636.1 | 786.3 | 686.5 | 766.4 | 614.3 | 600.8 | 693.4 | 645.5 | 143.7 | 205.3 | 263.1 | 225 | 306.9 | 303.4 | 202 | 281.2 | 384.5 | 269.5
2104.4 | 1885.4 | 560.9 | 224.36 | 262.2639 | 353.1 | 271.8 | 293.8 | 290.8 | 459.2 | 52.7 | 19.2 | 96.5 | 9.6 | 281 | 12.7 | 820.4 | 694.2 | 642.5 | 792 | 685.1 | 766.5 | 628.3 | 611.1 | 691.8 | 646.6 | 143.9 | 205.4 | 263 | 225.1 | 306.1 | 302.8 | 202.1 | 281.1 | 384.7 | 269.6
2105.4 | 1886.4 | 560.3 | 224.12 | 261.9834 | 353 | 272.1 | 292.7 | 291.6 | 467.9 | 52.7 | 19.2 | 96.9 | 9.9 | 270.8 | 12.4 | 823.4 | 725.1 | 672.4 | 800.9 | 686.2 | 766.7 | 647.3 | 635 | 691.1 | 649 | 144 | 205.6 | 263 | 225.2 | 305.4 | 302.1 | 202.2 | 281 | 385 | 269.7
2106.4 | 1887.4 | 560.7 | 224.28 | 262.1704 | 351.9 | 273.1 | 291 | 291.5 | 488.9 | 52.7 | 19.2 | 97.1 | 10.1 | 284 | 11.8 | 827.5 | 756.3 | 697.1 | 809.3 | 686.7 | 766.6 | 659.8 | 663.7 | 693.6 | 649.8 | 144.2 | 205.7 | 263.3 | 225.3 | 305.1 | 301.6 | 202.3 | 281 | 385.2 | 269.8
2107.4 | 1888.4 | 560.7 | 224.28 | 262.1704 | 351 | 273.4 | 288.7 | 291.4 | 516.2 | 52.8 | 19.2 | 97.2 | 10.5 | 280.4 | 12 | 831.9 | 767.6 | 715.7 | 822 | 687.4 | 766.1 | 673.4 | 687 | 693.2 | 652.6 | 144.4 | 205.8 | 263.5 | 225.3 | 305.1 | 301.8 | 202.4 | 281 | 385.5 | 269.8
2108.4 | 1889.4 | 560.5 | 224.2 | 262.0769 | 350.9 | 273.9 | 288.7 | 294.3 | 514.2 | 52.8 | 19.2 | 97.3 | 10.5 | 286.2 | 11.4 | 837.4 | 792.6 | 745.1 | 836.1 | 690 | 765.9 | 689.8 | 695 | 695.9 | 656.2 | 144.5 | 205.9 | 263.5 | 225.5 | 305.3 | 302.3 | 202.6 | 281.1 | 385.7 | 270
2109.4 | 1890.4 | 559.8 | 223.92 | 261.7496 | 349.9 | 274 | 288 | 294.6 | 524.4 | 52.8 | 19.2 | 97.3 | 9.2 | 261.9 | 9.8 | 842.4 | 804.3 | 755 | 846.5 | 692.8 | 765.5 | 705.8 | 703.1 | 697.9 | 661.4 | 144.7 | 206 | 263.7 | 225.6 | 305.2 | 302.8 | 202.7 | 281.3 | 385.9 | 270.1
2110.4 | 1891.4 | 559.2 | 223.68 | 261.469 | 350.5 | 273.8 | 287.8 | 294.7 | 526.7 | 52.9 | 19.2 | 97.2 | 8.5 | 266.7 | 9.2 | 843.6 | 803.6 | 768.1 | 843.1 | 693.3 | 765.5 | 704 | 700.3 | 698.2 | 660.9 | 144.8 | 206.1 | 263.8 | 225.7 | 305.7 | 302.8 | 202.8 | 281.3 | 386.2 | 270.3
2111.4 | 1892.4 | 559.8 | 223.92 | 261.7496 | 351.2 | 274.1 | 287.2 | 295.4 | 519.5 | 52.8 | 19.2 | 96.9 | 9.4 | 270.4 | 11.5 | 843.8 | 783.9 | 771.3 | 840.1 | 694 | 765.8 | 702.2 | 687.5 | 699.5 | 660.3 | 145 | 206.2 | 263.8 | 225.8 | 306.2 | 302.7 | 202.9 | 281.3 | 386.4 | 270.4
2112.4 | 1893.4 | 560.3 | 224.12 | 261.9834 | 350 | 274.3 | 288.1 | 294.5 | 512.9 | 52.8 | 19.2 | 96.8 | 9.4 | 268.4 | 11.4 | 845.3 | 769.4 | 768.9 | 841.2 | 694 | 766.3 | 701.2 | 682 | 700.8 | 659.7 | 145.2 | 206.3 | 263.9 | 225.9 | 306.6 | 302.6 | 203 | 281.5 | 386.6 | 270.5
2113.4 | 1894.4 | 558.7 | 223.48 | 261.2352 | 349.5 | 274.1 | 289.4 | 293.7 | 509.3 | 52.6 | 19.2 | 96.5 | 8.8 | 255.7 | 10.4 | 845.8 | 768.9 | 750.3 | 844.4 | 692.4 | 766.6 | 699.7 | 680.1 | 698.8 | 659 | 145.3 | 206.4 | 263.9 | 226 | 307.2 | 302.8 | 203.2 | 281.6 | 386.8 | 270.6
2114.4 | 1895.4 | 559.5 | 223.8 | 261.6093 | 349.6 | 273.9 | 289.7 | 292.8 | 511.9 | 52.5 | 19.2 | 96.3 | 8.6 | 261.5 | 9.7 | 846.4 | 766.6 | 741.2 | 848.7 | 689.7 | 766.8 | 698.3 | 693.1 | 700.8 | 657.8 | 145.5 | 206.6 | 264.1 | 226.1 | 307.6 | 303.1 | 203.3 | 281.7 | 387 | 270.7
2115.4 | 1896.4 | 561.3 | 224.52 | 262.4509 | 351 | 274 | 290.6 | 293 | 510.1 | 52.3 | 19.2 | 96.3 | 8.9 | 249.4 | 9.6 | 842.4 | 736.5 | 726.7 | 839.2 | 686.7 | 767.1 | 688.6 | 669.4 | 700.3 | 655.7 | 145.6 | 206.7 | 264.2 | 226.3 | 307.6 | 303.7 | 203.4 | 281.9 | 387.2 | 270.8
2116.4 | 1897.4 | 561.2 | 224.48 | 262.4042 | 351.9 | 274.1 | 291.3 | 293.1 | 495.6 | 52.2 | 19.2 | 96.3 | 9.2 | 260.3 | 9.2 | 835.1 | 708.2 | 703.8 | 822.5 | 683.7 | 767.6 | 674.3 | 642.1 | 700.5 | 652.5 | 145.8 | 206.8 | 264.1 | 226.4 | 308 | 304.1 | 203.5 | 282.2 | 387.4 | 271
2117.4 | 1898.4 | 560.4 | 224.16 | 262.0301 | 352.7 | 274.2 | 290.8 | 293.1 | 479.1 | 52.1 | 19.2 | 96.4 | 9.1 | 251 | 9.1 | 829.3 | 680.8 | 678.8 | 816.8 | 679.8 | 767.8 | 655.9 | 621.4 | 696.4 | 648.1 | 145.9 | 206.9 | 264.1 | 226.5 | 308.2 | 304.3 | 203.6 | 282.3 | 387.6 | 271.1
2118.4 | 1899.4 | 560.6 | 224.24 | 262.1236 | 355.4 | 273.7 | 290.9 | 293 | 468.4 | 52.1 | 19.2 | 96.4 | 9.1 | 240.1 | 9.2 | 821 | 656.5 | 652.9 | 805.1 | 675.4 | 767.5 | 638.9 | 604.3 | 694.5 | 643.9 | 146.1 | 207.1 | 264.2 | 226.7 | 308.7 | 304.6 | 203.8 | 282.4 | 387.7 | 271.2
2119.4 | 1900.4 | 561.2 | 224.48 | 262.4042 | 357.3 | 273.6 | 290.1 | 292.5 | 456.3 | 52.2 | 19.2 | 96.5 | 8.8 | 242.9 | 7.8 | 813 | 647.9 | 633.8 | 788.8 | 671.5 | 767.1 | 627 | 588.3 | 695.5 | 640 | 146.3 | 207.2 | 264.4 | 226.8 | 309 | 305.1 | 203.9 | 282.5 | 387.7 | 271.4
2120.4 | 1901.4 | 562.1 | 224.84 | 262.825 | 355.9 | 273.6 | 289.2 | 292.5 | 448.2 | 52.4 | 19.2 | 96.5 | 8.5 | 259.2 | 6.8 | 806 | 640.6 | 622.3 | 775.6 | 668.1 | 766.6 | 615.7 | 579.2 | 691.6 | 635.9 | 146.4 | 207.3 | 264.5 | 227 | 309.2 | 305.2 | 204 | 282.6 | 387.7 | 271.5
2121.4 | 1902.4 | 561.4 | 224.56 | 262.4977 | 357.7 | 273.4 | 289.2 | 292.7 | 444.7 | 52.6 | 19.2 | 96.6 | 7.4 | 251.6 | 6.2 | 804.2 | 645.3 | 614 | 776.8 | 666.3 | 766.4 | 615 | 578.9 | 690.2 | 634.2 | 146.6 | 207.4 | 264.6 | 227.1 | 309 | 305.3 | 204.1 | 282.7 | 387.7 | 271.6
2122.4 | 1903.4 | 559.3 | 223.72 | 261.5158 | 358.2 | 272.8 | 290.5 | 291.7 | 444.2 | 52.6 | 19.2 | 96.8 | 7.6 | 256.3 | 6 | 803 | 649.4 | 604 | 780.4 | 663.9 | 766.6 | 612.1 | 570.5 | 689.5 | 631.8 | 146.8 | 207.5 | 264.6 | 227.2 | 308.9 | 305.2 | 204.3 | 282.8 | 387.8 | 271.7
2123.4 | 1904.4 | 559.4 | 223.76 | 261.5625 | 357 | 272 | 290.9 | 291.6 | 439.5 | 52.7 | 19.2 | 96.9 | 7.6 | 239.5 | 5.8 | 801.2 | 646 | 603.8 | 777.4 | 661.6 | 766.7 | 611.3 | 566.5 | 687.4 | 629.4 | 146.9 | 207.6 | 264.8 | 227.4 | 308.8 | 305 | 204.4 | 282.9 | 387.8 | 271.8
2124.4 | 1905.4 | 559.7 | 223.88 | 261.7028 | 355.6 | 271.5 | 290.5 | 291.8 | 438.5 | 52.7 | 19.2 | 96.9 | 6.7 | 238.3 | 7.4 | 798.5 | 641.6 | 602 | 772.3 | 659.2 | 766.8 | 606.6 | 563 | 685.9 | 626.8 | 147.1 | 207.6 | 264.8 | 227.5 | 309.4 | 304.9 | 204.5 | 282.9 | 387.9 | 271.9
2125.4 | 1906.4 | 560 | 224 | 261.8431 | 354.6 | 271.7 | 290.4 | 290.2 | 439.7 | 52.7 | 19.2 | 97.2 | 7 | 245.4 | 8.3 | 797.3 | 655.1 | 606.4 | 770.8 | 657.5 | 767 | 603 | 557.6 | 684 | 624.3 | 147.2 | 207.7 | 264.7 | 227.6 | 309.4 | 304.7 | 204.6 | 282.9 | 387.9 | 272.1
2126.4 | 1907.4 | 559.9 | 223.96 | 261.7963 | 354 | 272.2 | 290.5 | 289 | 440.6 | 52.8 | 19.2 | 97.4 | 7.4 | 240.9 | 8.3 | 800 | 682.5 | 635.3 | 779.5 | 658.3 | 767 | 613.3 | 570.8 | 684.2 | 625.2 | 147.4 | 207.8 | 264.9 | 227.7 | 309.4 | 304.4 | 204.7 | 282.9 | 388 | 272.2
2127.4 | 1908.4 | 560.4 | 224.16 | 262.0301 | 353.4 | 271.9 | 289.8 | 289.1 | 457.7 | 52.8 | 19.2 | 97.5 | 7.6 | 238.7 | 8 | 805.8 | 700 | 653.1 | 792.9 | 660 | 766.9 | 628.8 | 592.1 | 682.7 | 627.4 | 147.6 | 207.9 | 265 | 227.8 | 309 | 303.9 | 204.9 | 282.9 | 388.1 | 272.3
2128.4 | 1909.4 | 560 | 224 | 261.8431 | 353 | 271.6 | 289.3 | 288.1 | 463.5 | 52.8 | 19.2 | 97.6 | 7.7 | 264.6 | 8.2 | 806.4 | 702.7 | 666.8 | 791.1 | 659.6 | 766.6 | 633.1 | 593.3 | 682.8 | 626.5 | 147.7 | 208 | 265.1 | 227.9 | 308.7 | 303.5 | 205 | 282.9 | 388.3 | 272.4
2129.4 | 1910.4 | 560 | 224 | 261.8431 | 353.9 | 271.7 | 288.6 | 286.8 | 462.9 | 52.9 | 19.2 | 97.9 | 8.3 | 253.2 | 8.4 | 808 | 712.5 | 690.4 | 795 | 661.1 | 766.8 | 637.4 | 596.1 | 685.6 | 628.9 | 147.9 | 208.2 | 265.4 | 227.9 | 308.2 | 303.5 | 205.1 | 282.9 | 388.5 | 272.5
2130.4 | 1911.4 | 559.8 | 223.92 | 261.7496 | 353.5 | 271.5 | 289.3 | 287.1 | 469.2 | 52.9 | 19.2 | 98.1 | 9 | 251.3 | 7.4 | 812.8 | 732.3 | 729.5 | 806.8 | 663.2 | 766.8 | 648.8 | 603.1 | 685.9 | 630.8 | 148 | 208.4 | 265.7 | 228 | 307.9 | 303.3 | 205.2 | 282.9 | 388.6 | 272.6
2131.4 | 1912.4 | 559.7 | 223.88 | 261.7028 | 353.2 | 271.4 | 290.4 | 285.8 | 468.9 | 53 | 19.2 | 98.4 | 8.7 | 256.9 | 8 | 816.5 | 743.4 | 727.8 | 815.8 | 662.7 | 766.9 | 645.4 | 605.5 | 685.7 | 629.6 | 148.2 | 208.6 | 265.7 | 228 | 307.6 | 303 | 205.4 | 283 | 388.7 | 272.7
2132.4 | 1913.4 | 559.9 | 223.96 | 261.7963 | 352.5 | 272.2 | 289.7 | 284.7 | 465.1 | 53.1 | 19.2 | 98.5 | 8.1 | 249.8 | 10.1 | 818.9 | 735.6 | 719.3 | 821.7 | 662.4 | 767.1 | 643.9 | 599.1 | 685.9 | 629 | 148.4 | 208.7 | 265.8 | 228.1 | 307.2 | 302.7 | 205.5 | 283 | 388.8 | 272.8
2133.4 | 1914.4 | 559.9 | 223.96 | 261.7963 | 353.7 | 273.2 | 289.5 | 285.1 | 470.1 | 53.2 | 19.2 | 98.6 | 8.8 | 259 | 10.5 | 824.1 | 751.1 | 725.3 | 830.8 | 663 | 766.7 | 660.1 | 610.8 | 687.5 | 631.5 | 148.5 | 208.8 | 266 | 228.1 | 306.9 | 302.5 | 205.6 | 283.1 | 388.9 | 272.9
2134.4 | 1915.4 | 560 | 224 | 261.8431 | 353.5 | 273.6 | 291 | 286.1 | 484.5 | 53.4 | 19.2 | 98.6 | 8 | 243 | 10.4 | 827.6 | 773.1 | 735.8 | 839.2 | 664.4 | 766.2 | 667.8 | 629.9 | 689.1 | 631.9 | 148.7 | 208.9 | 265.9 | 228.1 | 306.3 | 302.2 | 205.8 | 283.1 | 389 | 273
2135.4 | 1916.4 | 560 | 224 | 261.8431 | 351.8 | 273.7 | 292 | 286.8 | 488.9 | 53.5 | 19.2 | 98.7 | 7.6 | 262.9 | 10.3 | 829.2 | 768.5 | 726.8 | 841.6 | 662 | 766.1 | 661.1 | 630.2 | 688.7 | 631.3 | 148.8 | 209 | 266 | 228.2 | 306.1 | 302.6 | 205.8 | 283.1 | 389.2 | 273.1
2136.4 | 1917.4 | 560.1 | 224.04 | 261.8899 | 352.7 | 273.4 | 292.6 | 287 | 478.7 | 53.5 | 19.2 | 98.6 | 7.6 | 279.6 | 10.1 | 830.8 | 765.6 | 728.2 | 841.6 | 661.7 | 766.4 | 654.2 | 630 | 688.8 | 629.9 | 149 | 209.2 | 266.1 | 228.3 | 306 | 302.8 | 206 | 283.1 | 389.3 | 273.1
2137.4 | 1918.4 | 560.3 | 224.12 | 261.9834 | 353.9 | 273.7 | 293.3 | 285.9 | 477.7 | 53.5 | 19.2 | 98.5 | 7.7 | 288.8 | 8.8 | 831.9 | 757.1 | 725.6 | 840.6 | 660.5 | 766.6 | 653.4 | 622.3 | 688.6 | 629.1 | 149.2 | 209.2 | 266.2 | 228.3 | 305.9 | 303.2 | 206.1 | 283.3 | 389.4 | 273.2
2138.4 | 1919.4 | 560.5 | 224.2 | 262.0769 | 354.7 | 273.1 | 293.6 | 286.5 | 478.3 | 53.5 | 19.2 | 98.5 | 8.2 | 296.3 | 9 | 834.8 | 769.6 | 729.2 | 847.2 | 661.7 | 766.4 | 663 | 641.2 | 688.9 | 631 | 149.3 | 209.3 | 266.4 | 228.4 | 306 | 303.1 | 206.3 | 283.5 | 389.5 | 273.3
2139.4 | 1920.4 | 560.9 | 224.36 | 262.2639 | 355.1 | 273.2 | 293.4 | 287.2 | 485.9 | 53.4 | 19.2 | 98.4 | 8 | 302.9 | 8.6 | 835.4 | 766.9 | 739.1 | 841.5 | 662.9 | 766.4 | 663 | 634.4 | 688.5 | 629.8 | 149.5 | 209.4 | 266.4 | 228.5 | 306.1 | 303.4 | 206.3 | 283.6 | 389.6 | 273.4
2140.4 | 1921.4 | 561.9 | 224.76 | 262.7315 | 354.7 | 273.5 | 293 | 288.1 | 481.6 | 53.4 | 19.2 | 98.3 | 8.3 | 297.3 | 9.4 | 837.1 | 768.1 | 755.5 | 841.7 | 666.2 | 766.5 | 665.3 | 636.8 | 688.6 | 630.8 | 149.6 | 209.6 | 266.4 | 228.6 | 306.2 | 303.8 | 206.5 | 283.6 | 389.7 | 273.5
2141.4 | 1922.4 | 560.9 | 224.36 | 262.2639 | 354.6 | 273.8 | 292.6 | 289.3 | 481.4 | 53.3 | 19.2 | 98.2 | 8.8 | 310.9 | 9.7 | 837.2 | 755.9 | 756 | 839 | 667.1 | 766.7 | 670.4 | 633 | 689.5 | 631.6 | 149.8 | 209.7 | 266.5 | 228.7 | 306.4 | 304.4 | 206.6 | 283.8 | 389.8 | 273.6
2142.4 | 1923.4 | 561.1 | 224.44 | 262.3574 | 355 | 274.3 | 293 | 289.3 | 483.4 | 53.2 | 19.2 | 98.3 | 8.7 | 306.3 | 9.2 | 838.3 | 760.1 | 758.2 | 840 | 668.1 | 767 | 676.1 | 630.8 | 691.1 | 631.3 | 150 | 209.8 | 266.6 | 228.7 | 306.4 | 304.5 | 206.7 | 283.8 | 390 | 273.7
2143.4 | 1924.4 | 560.3 | 224.12 | 261.9834 | 356.1 | 274.4 | 292.7 | 288.6 | 480.6 | 53.2 | 19.2 | 98.3 | 7.9 | 296 | 8.6 | 839.6 | 762.6 | 760.4 | 841.6 | 669.5 | 766.8 | 679.6 | 633.6 | 691.3 | 633.5 | 150.1 | 210 | 266.9 | 228.8 | 306.7 | 304.7 | 206.9 | 283.9 | 390.2 | 273.8
2144.4 | 1925.4 | 559.4 | 223.76 | 261.5625 | 356.3 | 274.4 | 292.7 | 289.3 | 476.5 | 53.2 | 19.2 | 98.3 | 7.8 | 284.1 | 7.9 | 838.9 | 760.7 | 768.9 | 842.1 | 668.9 | 767.1 | 678.8 | 624.7 | 689.9 | 633.9 | 150.3 | 210.1 | 267 | 228.9 | 306.9 | 305.1 | 207 | 284.1 | 390.4 | 273.9
2145.4 | 1926.4 | 560 | 224 | 261.8431 | 357.3 | 274.7 | 293.5 | 290.9 | 473.8 | 53.2 | 19.2 | 98.1 | 7.4 | 307.7 | 8 | 842.3 | 761.1 | 765.4 | 854.5 | 669.7 | 767.6 | 684.9 | 626.9 | 690.1 | 637.2 | 150.5 | 210.2 | 267.1 | 228.9 | 307.3 | 305.3 | 207.2 | 284.3 | 390.7 | 274
2146.4 | 1927.4 | 560.2 | 224.08 | 261.9366 | 358.2 | 274.7 | 294.4 | 291.3 | 474.7 | 53.2 | 19.2 | 97.9 | 8.5 | 281.6 | 8.8 | 846.3 | 772.6 | 763.8 | 862.2 | 670 | 767.5 | 695.7 | 645.1 | 693.5 | 640.3 | 150.6 | 210.3 | 267.3 | 229 | 307.6 | 305.4 | 207.3 | 284.4 | 390.9 | 274.1
2147.4 | 1928.4 | 561.6 | 224.64 | 262.5912 | 358.6 | 274.7 | 296 | 290.6 | 480 | 53.3 | 19.2 | 97.7 | 8.6 | 270.2 | 9 | 850.8 | 775.9 | 779.4 | 872.4 | 673.7 | 767.4 | 704.4 | 653.2 | 694 | 644.8 | 150.8 | 210.4 | 267.3 | 229 | 307.7 | 305.8 | 207.4 | 284.6 | 391.1 | 274.2
2148.4 | 1929.4 | 560.2 | 224.08 | 261.9366 | 358.9 | 275 | 296.9 | 290.5 | 475.6 | 53.4 | 19.2 | 97.8 | 9 | 281.6 | 8.8 | 853.1 | 778.5 | 783.1 | 874.7 | 675.1 | 767.8 | 701.9 | 645.1 | 693.1 | 645.1 | 150.9 | 210.5 | 267.3 | 229.1 | 308.4 | 306.3 | 207.6 | 284.7 | 391.3 | 274.4
2149.4 | 1930.4 | 561.1 | 224.44 | 262.3574 | 358.9 | 274.7 | 297.9 | 291.4 | 474.4 | 53.4 | 19.2 | 97.8 | 9.2 | 310.8 | 7.3 | 856.2 | 785.9 | 789.9 | 877.5 | 678 | 768 | 709.9 | 652.9 | 693.1 | 648.7 | 151.1 | 210.6 | 267.4 | 229.2 | 308.8 | 306.5 | 207.7 | 284.9 | 391.5 | 274.5
2150.4 | 1931.4 | 561.3 | 224.52 | 262.4509 | 359.5 | 274.8 | 298.8 | 291.3 | 478.2 | 53.5 | 19.2 | 97.8 | 8.6 | 285.4 | 5.9 | 859.8 | 794 | 783.8 | 883.9 | 679.2 | 767.7 | 716.6 | 650.8 | 694.9 | 652.4 | 151.3 | 210.7 | 267.5 | 229.2 | 309.5 | 306.7 | 207.8 | 285 | 391.8 | 274.6
2151.4 | 1932.4 | 561 | 224.4 | 262.3107 | 360.3 | 275.3 | 298.6 | 292.8 | 485 | 53.6 | 19.2 | 97.7 | 8 | 290 | 7.4 | 861.4 | 785.1 | 772 | 883.7 | 679.1 | 767.4 | 710.5 | 648.7 | 694.5 | 651.2 | 151.4 | 210.8 | 267.7 | 229.3 | 309.9 | 306.9 | 207.9 | 285.1 | 392 | 274.8
2152.4 | 1933.4 | 561.2 | 224.48 | 262.4042 | 360.2 | 275.7 | 298.5 | 294 | 484.6 | 53.6 | 19.2 | 97.6 | 8.6 | 307.4 | 9.4 | 860.5 | 767.9 | 752.3 | 878.5 | 677.1 | 767.6 | 698.5 | 644 | 692.4 | 648.7 | 151.6 | 210.9 | 267.8 | 229.4 | 310.6 | 307.2 | 208.1 | 285.2 | 392.1 | 275
2153.4 | 1934.4 | 560.6 | 224.24 | 262.1236 | 360.4 | 275.6 | 298.5 | 293.7 | 481.5 | 53.7 | 19.2 | 97.5 | 8.4 | 296.9 | 10.3 | 860.6 | 758.4 | 752.4 | 874 | 677.1 | 768 | 693.9 | 644 | 691 | 648.4 | 151.7 | 211.1 | 268 | 229.4 | 311.4 | 307.6 | 208.2 | 285.2 | 392.2 | 275.1
2154.4 | 1935.4 | 560.5 | 224.2 | 262.0769 | 361.5 | 275.3 | 299.8 | 295.4 | 489.2 | 53.6 | 19.2 | 97.4 | 9.2 | 291.8 | 14 | 862.6 | 780.7 | 747.8 | 875.9 | 677.4 | 768.1 | 704.9 | 679.7 | 692.4 | 651.6 | 151.9 | 211.2 | 268.3 | 229.5 | 312.9 | 308.2 | 208.3 | 285.4 | 392.3 | 275.3
2155.4 | 1936.4 | 559.8 | 223.92 | 261.7496 | 361.2 | 274.3 | 300.4 | 296.7 | 497.4 | 53.6 | 19.2 | 97.2 | 9.6 | 294.6 | 14.4 | 863.4 | 789.4 | 754.6 | 876 | 678.2 | 768 | 699.6 | 677.2 | 689 | 650.6 | 152.1 | 211.4 | 268.4 | 229.6 | 313.4 | 308.3 | 208.5 | 285.6 | 392.5 | 275.5
2156.4 | 1937.4 | 559.2 | 223.68 | 261.469 | 361.9 | 273.9 | 301.3 | 297.1 | 500.1 | 53.7 | 19.2 | 97.2 | 8 | 296.8 | 13.9 | 866.9 | 804.3 | 765.6 | 879.4 | 680.1 | 768.2 | 702.6 | 701.8 | 687.2 | 651.5 | 152.2 | 211.6 | 268.6 | 229.7 | 313.6 | 308 | 208.6 | 285.6 | 392.7 | 275.6
2157.4 | 1938.4 | 559 | 223.6 | 261.3755 | 361 | 273.4 | 302 | 297.5 | 512.1 | 53.7 | 19.1 | 97.1 | 7.7 | 293.8 | 11.5 | 870.6 | 811 | 764.5 | 887 | 679.5 | 768.2 | 712.2 | 712.2 | 687.2 | 654.2 | 152.4 | 211.8 | 268.9 | 229.8 | 313.2 | 307.5 | 208.7 | 285.7 | 392.8 | 275.7
2158.4 | 1939.4 | 559.6 | 223.84 | 261.6561 | 358.7 | 273 | 303.1 | 298.6 | 520 | 53.7 | 19.1 | 97.1 | 8.6 | 303.1 | 9.4 | 873.1 | 812.9 | 755.6 | 892.9 | 678.4 | 768.3 | 711.9 | 716 | 684.4 | 654.7 | 152.5 | 212 | 269.1 | 229.9 | 313.2 | 307.6 | 208.8 | 285.7 | 393 | 275.8
2159.4 | 1940.4 | 559.6 | 223.84 | 261.6561 | 359 | 274.3 | 302.9 | 300.1 | 516.5 | 53.6 | 19.2 | 97 | 8.6 | 302.9 | 9.8 | 874.3 | 807.4 | 760.9 | 896.2 | 678.9 | 768.7 | 707.8 | 707.5 | 682.6 | 654.5 | 152.7 | 212.2 | 269.2 | 229.9 | 313.6 | 307.5 | 209 | 285.7 | 393.2 | 276
2160.4 | 1941.4 | 559.6 | 223.84 | 261.6561 | 359.9 | 275.6 | 303.4 | 300.7 | 518 | 53.5 | 19.1 | 96.8 | 7.8 | 288.3 | 10.6 | 878.8 | 815.5 | 769.2 | 906.2 | 680.1 | 769.1 | 710.4 | 715.4 | 681.1 | 654.1 | 152.9 | 212.4 | 269.3 | 230 | 313.6 | 307.3 | 209.1 | 285.8 | 393.3 | 276.1
2161.4 | 1942.4 | 559.9 | 223.96 | 261.7963 | 359.3 | 277 | 303.1 | 301.9 | 521.2 | 53.4 | 19.1 | 96.7 | 7.8 | 289.5 | 11.8 | 882.8 | 819.5 | 780.6 | 912.1 | 681.1 | 769.5 | 711.1 | 716.2 | 680.6 | 654.9 | 153 | 212.6 | 269.6 | 230.1 | 313.6 | 307 | 209.2 | 285.9 | 393.4 | 276.2
2162.4 | 1943.4 | 560.1 | 224.04 | 261.8899 | 358.1 | 277.7 | 302.2 | 302.3 | 525.1 | 53.3 | 19.1 | 96.6 | 8 | 290 | 12 | 883.7 | 810.4 | 786.5 | 911.7 | 681.9 | 770 | 711.2 | 716.1 | 679.6 | 656.6 | 153.2 | 212.8 | 269.7 | 230.2 | 314.1 | 306.9 | 209.4 | 285.9 | 393.5 | 276.4
2163.4 | 1944.4 | 560.4 | 224.16 | 262.0301 | 358.9 | 278.4 | 301.5 | 302 | 521.4 | 53.2 | 19.1 | 96.4 | 8.8 | 298.8 | 11.9 | 885.1 | 811.8 | 793 | 908.1 | 683.6 | 770.4 | 718.2 | 716 | 680.7 | 658.5 | 153.4 | 212.9 | 269.7 | 230.3 | 314.3 | 306.9 | 209.5 | 286.1 | 393.7 | 276.5
2164.4 | 1945.4 | 560.6 | 224.24 | 262.1236 | 359.5 | 278.4 | 301.4 | 300.7 | 518.4 | 53.2 | 19.1 | 96.3 | 8.5 | 305.5 | 10 | 888.5 | 823.1 | 794.6 | 911.1 | 685.4 | 770.5 | 728.9 | 722.5 | 683.6 | 661.7 | 153.5 | 213.1 | 270 | 230.4 | 314.3 | 307.1 | 209.6 | 286.2 | 394 | 276.6
2165.4 | 1946.4 | 560.4 | 224.16 | 262.0301 | 358.9 | 278.9 | 300.8 | 299.4 | 521.5 | 53.2 | 19.1 | 96.3 | 8 | 306.9 | 9 | 890.5 | 813.3 | 803.9 | 916 | 686.4 | 770.7 | 734.2 | 716.8 | 687 | 665.6 | 153.7 | 213.3 | 270.2 | 230.5 | 314.4 | 307.3 | 209.7 | 286.3 | 394.2 | 276.7
2166.4 | 1947.4 | 560.2 | 224.08 | 261.9366 | 359.3 | 278.5 | 301 | 299.4 | 516.8 | 53.2 | 19.1 | 96.2 | 7.7 | 320.8 | 7.6 | 892.7 | 816.6 | 811.4 | 920.8 | 688.6 | 770.9 | 738.5 | 715.3 | 689.4 | 667.8 | 153.8 | 213.5 | 270.1 | 230.6 | 314.5 | 307.5 | 209.9 | 286.4 | 394.4 | 276.9
2167.4 | 1948.4 | 560.3 | 224.12 | 261.9834 | 359.6 | 277.4 | 301 | 299.9 | 519.5 | 53.3 | 19.1 | 96.2 | 7.4 | 321 | 7.1 | 894.4 | 819.3 | 819.1 | 922.8 | 690.7 | 770.8 | 740.1 | 716.8 | 690.4 | 670.2 | 154 | 213.7 | 270.2 | 230.7 | 315 | 307.7 | 210 | 286.5 | 394.7 | 277
2168.4 | 1949.4 | 560.2 | 224.08 | 261.9366 | 359 | 276.6 | 299.8 | 298.1 | 530.3 | 53.4 | 19.1 | 96.1 | 7.7 | 317.7 | 6.4 | 897.2 | 834.8 | 818.9 | 928.7 | 692.2 | 770.9 | 741.7 | 735.7 | 689.9 | 671 | 154.1 | 213.9 | 270.5 | 230.8 | 315.1 | 307.9 | 210.2 | 286.6 | 394.9 | 277.1
2169.4 | 1950.4 | 560.4 | 224.16 | 262.0301 | 357.9 | 275.8 | 300.4 | 297.5 | 540.3 | 53.5 | 19.1 | 96 | 7.8 | 324.9 | 5.5 | 899.1 | 829 | 812.2 | 926.2 | 692.3 | 771.1 | 731.3 | 740.3 | 686.4 | 671.4 | 154.3 | 214.1 | 270.6 | 230.9 | 315.3 | 308.1 | 210.3 | 286.8 | 395.1 | 277.2
2170.4 | 1951.4 | 560.5 | 224.2 | 262.0769 | 357.8 | 275.3 | 299.7 | 296.1 | 538 | 53.5 | 19.1 | 96 | 7.5 | 315.5 | 5.9 | 900.2 | 832.8 | 814.6 | 923.3 | 694.5 | 771.8 | 728.7 | 750.6 | 685.4 | 672.4 | 154.5 | 214.3 | 270.6 | 231 | 315.5 | 308.1 | 210.4 | 286.9 | 395.4 | 277.4
2171.4 | 1952.4 | 560.8 | 224.32 | 262.2172 | 357.2 | 275 | 299.1 | 295 | 546.1 | 53.5 | 19.1 | 95.9 | 6.8 | 326.4 | 5.4 | 901.8 | 828.9 | 825 | 926.5 | 697.6 | 772.1 | 731.1 | 750.4 | 684 | 674.3 | 154.6 | 214.4 | 270.8 | 231.1 | 315.3 | 308.2 | 210.5 | 286.9 | 395.5 | 277.5
2172.4 | 1953.4 | 560.7 | 224.28 | 262.1704 | 356.4 | 274.8 | 299.4 | 295.7 | 541.2 | 53.5 | 19.1 | 95.9 | 7.4 | 329.8 | 4.1 | 903.4 | 838.1 | 839.2 | 934.2 | 700.3 | 772.3 | 734.1 | 757.6 | 685.3 | 677.6 | 154.8 | 214.6 | 271 | 231.2 | 315.1 | 308 | 210.7 | 287 | 395.7 | 277.6
2173.4 | 1954.4 | 560.6 | 224.24 | 262.1236 | 354.6 | 274.7 | 300.6 | 295.6 | 555.4 | 53.5 | 19.1 | 96 | 7.2 | 313.7 | 3.4 | 904.7 | 849.3 | 842.4 | 932.9 | 701.5 | 772.3 | 735.8 | 769.2 | 685.5 | 678.7 | 154.9 | 214.8 | 271.4 | 231.3 | 315 | 307.8 | 210.8 | 286.9 | 395.9 | 277.7
2174.4 | 1955.4 | 560.4 | 224.16 | 262.0301 | 353.8 | 275 | 301.5 | 295.9 | 568.9 | 53.4 | 19.1 | 96 | 7.2 | 300.4 | 3.1 | 903.3 | 850.4 | 816.2 | 920.4 | 700.7 | 772.5 | 733.5 | 789 | 684.1 | 677.7 | 155.1 | 215 | 271.8 | 231.4 | 314.8 | 307.8 | 210.9 | 286.9 | 396.3 | 277.8
2175.4 | 1956.4 | 560.5 | 224.2 | 262.0769 | 353.3 | 275.1 | 301.8 | 296.6 | 574.7 | 53.4 | 19.1 | 96.1 | 6.8 | 295.1 | 2.8 | 897.9 | 842.7 | 786.3 | 903 | 697.8 | 773.2 | 719.6 | 796.7 | 679.7 | 676.2 | 155.3 | 215.2 | 272.4 | 231.5 | 314.8 | 307.7 | 211.1 | 286.9 | 396.6 | 277.9
2176.4 | 1957.4 | 560.8 | 224.32 | 262.2172 | 354.3 | 275.4 | 302.3 | 298.4 | 574.4 | 53.4 | 19.1 | 96.4 | 7.5 | 305 | 2.4 | 891.4 | 843 | 780.7 | 881.8 | 696.6 | 774.3 | 703.4 | 797.3 | 674.1 | 672.8 | 155.4 | 215.3 | 272.7 | 231.6 | 315.1 | 307.8 | 211.2 | 287 | 396.9 | 278
2177.4 | 1958.4 | 561.5 | 224.6 | 262.5445 | 355.9 | 276.4 | 303.7 | 300.5 | 575.3 | 53.4 | 19.1 | 96.6 | 7.8 | 323.6 | 2.6 | 890.6 | 852.7 | 794.4 | 878.9 | 700.8 | 775.4 | 705.6 | 814.1 | 673.7 | 675.9 | 155.6 | 215.5 | 272.6 | 231.7 | 315.6 | 308.2 | 211.4 | 287.1 | 397.1 | 278.2
2178.4 | 1959.4 | 561.8 | 224.72 | 262.6847 | 355.4 | 277.8 | 304.6 | 301.8 | 586.4 | 53.4 | 19.1 | 96.8 | 8.1 | 335.2 | 2.8 | 892.1 | 853.3 | 802.7 | 883.7 | 705 | 775.7 | 715.9 | 826.2 | 676.9 | 678 | 155.8 | 215.6 | 272.7 | 231.8 | 316.3 | 308.3 | 211.5 | 287.1 | 397.3 | 278.4
2179.4 | 1960.4 | 562.5 | 225 | 263.012 | 354.7 | 278.8 | 303.7 | 302.8 | 610.3 | 53.5 | 19.1 | 96.9 | 6.9 | 317.9 | 2.9 | 891.8 | 853.8 | 796.8 | 882.9 | 707.9 | 775.9 | 721.1 | 838.1 | 680.6 | 680.7 | 155.9 | 215.8 | 273.3 | 231.9 | 316.8 | 308.2 | 211.6 | 287.2 | 397.6 | 278.5
2180.4 | 1961.4 | 561.4 | 224.56 | 262.4977 | 353.3 | 279.6 | 304 | 303 | 625.9 | 53.5 | 19.1 | 96.8 | 7.2 | 269 | 3.3 | 890.6 | 850.2 | 783.1 | 878.3 | 705.3 | 776.4 | 725.3 | 841.6 | 681.8 | 679.9 | 156.1 | 215.9 | 273.9 | 232 | 317.5 | 308 | 211.8 | 287.3 | 398 | 278.7
2181.4 | 1962.4 | 560.8 | 224.32 | 262.2172 | 352.7 | 280.1 | 302.9 | 304.6 | 630.2 | 53.5 | 19.1 | 96.7 | 7.4 | 249 | 3.7 | 889.1 | 849.4 | 776.4 | 875.4 | 702.1 | 776.9 | 727 | 842.2 | 680.5 | 677.3 | 156.2 | 216 | 274.2 | 232.1 | 318 | 308.3 | 211.9 | 287.3 | 398.3 | 278.8
2182.4 | 1963.4 | 560.5 | 224.2 | 262.0769 | 353 | 281.5 | 301.7 | 305.2 | 642 | 53.6 | 19.1 | 96.5 | 7.8 | 286.4 | 4.2 | 889.3 | 852.2 | 782.7 | 877.2 | 703 | 777.6 | 728.9 | 850.2 | 681.1 | 679.3 | 156.4 | 216 | 274.3 | 232.2 | 318.4 | 308.6 | 212 | 287.5 | 398.6 | 279
2183.4 | 1964.4 | 560.5 | 224.2 | 262.0769 | 352.9 | 282.7 | 301 | 307 | 624.2 | 53.6 | 19.1 | 96.5 | 7.5 | 290.8 | 4 | 891.1 | 853.8 | 802.6 | 886.7 | 706.7 | 778 | 736.5 | 845.6 | 681.6 | 683.7 | 156.6 | 216.1 | 274.1 | 232.3 | 318.5 | 308.9 | 212.2 | 287.6 | 398.8 | 279.2
2184.4 | 1965.4 | 560.5 | 224.2 | 262.0769 | 352.2 | 284.5 | 301.4 | 307.8 | 619.5 | 53.6 | 19.1 | 96.5 | 6.4 | 283.7 | 4.3 | 892.4 | 856.6 | 819.5 | 899.5 | 711.2 | 778.4 | 741.6 | 855.7 | 683.6 | 686.7 | 156.7 | 216.2 | 274.3 | 232.4 | 319.5 | 309.2 | 212.3 | 287.7 | 399 | 279.4
2185.4 | 1966.4 | 560.5 | 224.2 | 262.0769 | 351.8 | 286.9 | 301.5 | 307.5 | 630.7 | 53.5 | 19.1 | 96.6 | 6.3 | 279.6 | 5.3 | 893.3 | 863.1 | 835.8 | 905.9 | 716.3 | 778.8 | 749.7 | 862.8 | 687.3 | 692.7 | 156.9 | 216.3 | 274.6 | 232.5 | 319 | 309.5 | 212.5 | 287.8 | 399.4 | 279.6
2186.4 | 1967.4 | 560.6 | 224.24 | 262.1236 | 350.5 | 287.8 | 300.8 | 307 | 623.6 | 53.5 | 19.1 | 96.6 | 7.1 | 298.8 | 5.5 | 894.1 | 861.8 | 840.1 | 911.2 | 720.1 | 778.9 | 752.7 | 865 | 689.9 | 695.9 | 157 | 216.4 | 274.5 | 232.6 | 318.6 | 309.7 | 212.6 | 287.9 | 399.8 | 279.7
2187.4 | 1968.4 | 560.4 | 224.16 | 262.0301 | 349.4 | 289.1 | 301.9 | 307.2 | 611.6 | 53.4 | 19.1 | 96.6 | 7.3 | 286.2 | 5.3 | 894.9 | 858.6 | 841.3 | 914.2 | 723.7 | 779.3 | 752.4 | 855.1 | 691.4 | 699.8 | 157.2 | 216.6 | 274.6 | 232.7 | 318.3 | 309.8 | 212.7 | 288.2 | 400.2 | 279.8
2188.4 | 1969.4 | 560.5 | 224.2 | 262.0769 | 348.6 | 289.7 | 302.5 | 307 | 615 | 53.4 | 19.1 | 96.6 | 7 | 288.2 | 5.8 | 894.4 | 859.2 | 845.1 | 917.1 | 728 | 779.5 | 759.1 | 850.6 | 695.1 | 705.5 | 157.4 | 216.7 | 274.8 | 232.8 | 318.3 | 309.7 | 212.8 | 288.3 | 400.5 | 280
2189.4 | 1970.4 | 560.5 | 224.2 | 262.0769 | 348.3 | 289.5 | 302 | 307 | 612.1 | 53.4 | 19.1 | 96.6 | 7.2 | 287 | 6.3 | 894.7 | 853.8 | 842.9 | 921 | 733 | 779.9 | 758.3 | 835.8 | 696.5 | 708.5 | 157.5 | 216.8 | 274.9 | 232.9 | 317.9 | 309.9 | 213 | 288.4 | 400.9 | 280.1
2190.4 | 1971.4 | 560.7 | 224.28 | 262.1704 | 347 | 290.2 | 301.9 | 307.1 | 589.7 | 53.5 | 19.1 | 96.6 | 7.1 | 295.5 | 6.5 | 895.1 | 844.5 | 847.7 | 922.1 | 736.4 | 780.4 | 760.7 | 825.9 | 697.2 | 711 | 157.7 | 217 | 275.1 | 232.9 | 317.4 | 310 | 213.1 | 288.6 | 401.3 | 280.2
2191.4 | 1972.4 | 560.9 | 224.36 | 262.2639 | 346.8 | 289.8 | 301.9 | 306.2 | 585.7 | 53.5 | 19.1 | 96.5 | 7.2 | 278.2 | 7 | 896.9 | 842.6 | 851.7 | 918.1 | 741.9 | 780.9 | 757.1 | 825.1 | 695.9 | 712.9 | 157.9 | 217.1 | 275.2 | 233 | 317 | 310.1 | 213.2 | 288.7 | 401.6 | 280.3
2192.4 | 1973.4 | 561.7 | 224.68 | 262.638 | 346 | 288.4 | 302.1 | 304.2 | 579.4 | 53.6 | 19.1 | 96.5 | 6.8 | 289.8 | 7.4 | 898.3 | 842.2 | 854.7 | 918.1 | 745.5 | 781.6 | 752.4 | 818.8 | 693.7 | 715.5 | 158 | 217.2 | 275.2 | 233.1 | 316.8 | 310.1 | 213.4 | 288.8 | 402 | 280.4
2193.4 | 1974.4 | 562.3 | 224.92 | 262.9185 | 344.8 | 287.4 | 301.5 | 302 | 565.8 | 53.6 | 19.1 | 96.4 | 7 | 286.7 | 8.1 | 899.2 | 836.9 | 843.4 | 919.2 | 746.6 | 782.4 | 745.7 | 804.5 | 689.8 | 716 | 158.2 | 217.4 | 275.3 | 233.2 | 316.8 | 310.1 | 213.5 | 288.8 | 402.3 | 280.5
2194.4 | 1975.4 | 562.5 | 225 | 263.012 | 343.4 | 286.9 | 299.6 | 300.6 | 555.9 | 53.7 | 19.1 | 96.3 | 7 | 276 | 8.2 | 900 | 836.5 | 841.7 | 914.7 | 748.5 | 783 | 743 | 807.4 | 687.4 | 715.9 | 158.3 | 217.5 | 275.4 | 233.3 | 316.9 | 309.9 | 213.6 | 288.9 | 402.7 | 280.7
2195.4 | 1976.4 | 561.7 | 224.68 | 262.638 | 342.4 | 286.9 | 299.7 | 299.2 | 560.9 | 53.7 | 19.1 | 96.2 | 7.4 | 271 | 7.6 | 900.6 | 845 | 845.1 | 910.6 | 749.8 | 783.9 | 733.3 | 824.3 | 684.5 | 715.5 | 158.5 | 217.6 | 275.7 | 233.3 | 316.7 | 309.6 | 213.8 | 288.9 | 403 | 280.8
2196.4 | 1977.4 | 561.1 | 224.44 | 262.3574 | 341.6 | 286.3 | 299.7 | 298.5 | 572.9 | 53.7 | 19.1 | 96.2 | 7.4 | 241.6 | 6.9 | 900.7 | 848.6 | 841 | 906.6 | 751.1 | 784.9 | 730.8 | 841.3 | 681.8 | 717.3 | 158.7 | 217.7 | 276 | 233.4 | 316.4 | 309.5 | 213.9 | 289 | 403.3 | 280.9
2197.4 | 1978.4 | 560.8 | 224.32 | 262.2172 | 340.5 | 286.3 | 298.3 | 299.2 | 582.2 | 53.8 | 19.1 | 96.3 | 7.6 | 242.6 | 6.8 | 901.6 | 851.7 | 849.3 | 906.4 | 754.3 | 785.5 | 731.5 | 847.1 | 681.9 | 717.7 | 158.8 | 217.8 | 276.2 | 233.4 | 316.4 | 309.4 | 214 | 289.1 | 403.6 | 281
2198.4 | 1979.4 | 560.5 | 224.2 | 262.0769 | 339.5 | 286.4 | 296.6 | 298.3 | 577.3 | 53.8 | 19.1 | 96.4 | 7.5 | 246.7 | 6.4 | 902.3 | 853.2 | 849 | 909.7 | 757.6 | 786.1 | 737.6 | 840.4 | 683.1 | 720.8 | 159 | 217.9 | 276.2 | 233.5 | 316.7 | 309.2 | 214.2 | 289.2 | 404 | 281.1
2199.4 | 1980.4 | 560.1 | 224.04 | 261.8899 | 338.6 | 286.2 | 295.1 | 297.7 | 572.2 | 53.9 | 19.1 | 96.5 | 6.7 | 267.6 | 7.1 | 902.1 | 849.2 | 852.2 | 911 | 759.8 | 786.8 | 734.8 | 828.9 | 681.8 | 721.1 | 159.2 | 218.1 | 276.1 | 233.5 | 316.7 | 309 | 214.3 | 289.3 | 404.4 | 281.3
2200.4 | 1981.4 | 560.6 | 224.24 | 262.1236 | 337.8 | 286.4 | 294.9 | 298.3 | 567.4 | 54.1 | 19.1 | 96.7 | 7.2 | 268.3 | 8 | 900.5 | 836 | 849.5 | 910.5 | 759.5 | 787.6 | 730.9 | 809.1 | 679.7 | 718.7 | 159.3 | 218.2 | 276.1 | 233.5 | 316.7 | 308.8 | 214.4 | 289.3 | 404.8 | 281.4
2201.4 | 1982.4 | 561 | 224.4 | 262.3107 | 336.7 | 287.1 | 294.2 | 297.9 | 557.4 | 54.2 | 19.1 | 96.9 | 6.9 | 262.6 | 7.9 | 899.9 | 834.3 | 846.7 | 910 | 760.6 | 788.4 | 730.2 | 802 | 679.2 | 720.3 | 159.5 | 218.3 | 276.1 | 233.6 | 316.7 | 308.5 | 214.5 | 289.4 | 405 | 281.5
2202.4 | 1983.4 | 561.3 | 224.52 | 262.4509 | 335.9 | 286.8 | 293.5 | 298.2 | 553.4 | 54.2 | 19.1 | 97 | 7.2 | 276.4 | 7.6 | 900.5 | 833.6 | 848.8 | 916.1 | 761.3 | 788.8 | 733.4 | 800.3 | 679.1 | 720.8 | 159.7 | 218.4 | 276.3 | 233.6 | 316.5 | 308.4 | 214.7 | 289.6 | 405.3 | 281.6
2203.4 | 1984.4 | 559.9 | 223.96 | 261.7963 | 335.4 | 286.6 | 292.7 | 298.4 | 555.3 | 54.3 | 19.1 | 97.1 | 7.4 | 263 | 6.9 | 901 | 839.5 | 838.1 | 921.2 | 759.3 | 789.2 | 737.1 | 799.6 | 679.2 | 721.5 | 159.8 | 218.5 | 276.5 | 233.7 | 316.4 | 308.4 | 214.8 | 289.6 | 405.5 | 281.7
2204.4 | 1985.4 | 559.8 | 223.92 | 261.7496 | 335.7 | 287.4 | 290.7 | 297.9 | 557.2 | 54.3 | 19.1 | 97.4 | 6.9 | 261.9 | 6.3 | 902.3 | 841.1 | 826.1 | 924.4 | 758.6 | 789.2 | 741.3 | 796.4 | 681.9 | 721.9 | 160 | 218.6 | 276.6 | 233.7 | 316.5 | 308.4 | 214.9 | 289.7 | 405.7 | 281.8
2205.4 | 1986.4 | 560.4 | 224.16 | 262.0301 | 336 | 288.1 | 290.1 | 296.6 | 549.6 | 54.3 | 19.1 | 97.5 | 6.8 | 272.7 | 6.6 | 903.5 | 851.4 | 830.3 | 923.6 | 758.5 | 789.5 | 735.3 | 796.9 | 681 | 720.3 | 160.2 | 218.8 | 276.8 | 233.7 | 316.3 | 308.4 | 215 | 289.8 | 406 | 281.9
2206.4 | 1987.4 | 560.8 | 224.32 | 262.2172 | 337.2 | 288.7 | 290.3 | 296.8 | 558.1 | 54.3 | 19.1 | 97.8 | 7.2 | 276.6 | 6.7 | 904.3 | 855.4 | 833.3 | 924.2 | 759.1 | 789.5 | 733.7 | 801.3 | 681.4 | 720.1 | 160.3 | 218.9 | 276.9 | 233.8 | 316.1 | 308.1 | 215.1 | 289.8 | 406.1 | 282
2207.4 | 1988.4 | 560.8 | 224.32 | 262.2172 | 337.3 | 288.3 | 289.6 | 296.8 | 549.2 | 54.3 | 19.1 | 97.9 | 7.4 | 256.2 | 7 | 902.1 | 837 | 812.8 | 918.5 | 756.3 | 789.8 | 728.9 | 774.8 | 678.6 | 719.1 | 160.5 | 219 | 276.9 | 233.8 | 316.1 | 307.9 | 215.2 | 289.8 | 406.3 | 282.1
2208.4 | 1989.4 | 559.1 | 223.64 | 261.4223 | 337.6 | 288 | 289.5 | 296.7 | 538.3 | 54.4 | 19.1 | 97.8 | 8 | 275.5 | 8.2 | 900 | 829 | 795.8 | 915.7 | 752.8 | 790.2 | 726.3 | 762.9 | 677.9 | 718.1 | 160.6 | 219.1 | 277 | 233.9 | 316.3 | 308 | 215.3 | 289.9 | 406.5 | 282.2
2209.4 | 1990.4 | 559.2 | 223.68 | 261.469 | 338.2 | 287.3 | 289.4 | 296.2 | 537.4 | 54.6 | 19.1 | 97.9 | 7.6 | 270.4 | 8.7 | 900.3 | 823.6 | 801.2 | 919 | 752.3 | 790.6 | 731.9 | 769.1 | 681 | 718.4 | 160.8 | 219.3 | 277.1 | 234 | 316.5 | 308.1 | 215.4 | 290 | 406.7 | 282.4
2210.4 | 1991.4 | 559.3 | 223.72 | 261.5158 | 337.4 | 286.5 | 289.3 | 294.9 | 541.8 | 54.6 | 19.1 | 98 | 7.5 | 257.5 | 7.7 | 901.1 | 828 | 807.2 | 919.7 | 751.3 | 790.8 | 733.4 | 771.1 | 680.9 | 717 | 161 | 219.4 | 277.3 | 234.1 | 316.9 | 308 | 215.5 | 290.1 | 406.8 | 282.5
2211.4 | 1992.4 | 559.3 | 223.72 | 261.5158 | 337.1 | 286.4 | 287.9 | 293.9 | 545.6 | 54.7 | 19.1 | 98.1 | 7.9 | 271.1 | 7.2 | 900.7 | 818 | 803.6 | 920.4 | 750 | 791.2 | 735.8 | 758.3 | 682 | 718.8 | 161.1 | 219.6 | 277.4 | 234.2 | 317.2 | 308.2 | 215.6 | 290.2 | 407.1 | 282.6
2212.4 | 1993.4 | 559.2 | 223.68 | 261.469 | 336.3 | 285.6 | 288 | 294.9 | 534.3 | 54.7 | 19.1 | 98.1 | 8 | 279.7 | 7.5 | 898 | 801.2 | 799.1 | 912.1 | 749 | 791.9 | 727.9 | 745.5 | 677.8 | 715.6 | 161.3 | 219.8 | 277.4 | 234.3 | 316.7 | 308.1 | 215.7 | 290.3 | 407.3 | 282.8
2213.4 | 1994.4 | 558.9 | 223.56 | 261.3288 | 335.7 | 284.8 | 289 | 295.8 | 528.3 | 54.6 | 19.1 | 98.2 | 8.3 | 281.4 | 8.3 | 893.6 | 797.2 | 786.8 | 902.3 | 745.2 | 792.7 | 715 | 736.2 | 672.2 | 711.1 | 161.5 | 219.9 | 277.7 | 234.4 | 317 | 308.2 | 215.8 | 290.3 | 407.5 | 282.9
2214.4 | 1995.4 | 560.4 | 224.16 | 262.0301 | 335.9 | 284.4 | 289.3 | 296.6 | 530.4 | 54.6 | 19.1 | 98.3 | 7.9 | 292.6 | 9.7 | 889.3 | 793.1 | 774.2 | 897.8 | 742.3 | 793.8 | 702.6 | 732.2 | 666.3 | 707.6 | 161.6 | 220 | 277.8 | 234.5 | 317 | 308.3 | 215.9 | 290.4 | 407.5 | 283
2215.4 | 1996.4 | 560.5 | 224.2 | 262.0769 | 336.7 | 284.6 | 289.9 | 295.8 | 525.5 | 54.5 | 19.1 | 98.2 | 8.2 | 300.7 | 10.4 | 889.2 | 791.1 | 765.6 | 902.9 | 740.9 | 794.5 | 697.4 | 728.7 | 663.6 | 706.2 | 161.8 | 220.1 | 277.8 | 234.6 | 316.7 | 308.5 | 216 | 290.5 | 407.6 | 283.1
2216.4 | 1997.4 | 559.4 | 223.76 | 261.5625 | 337.2 | 284.3 | 290.3 | 293.4 | 518.7 | 54.5 | 19 | 98.2 | 7.7 | 280.2 | 10 | 890.1 | 791.4 | 759.7 | 905.5 | 739.2 | 794.8 | 693.9 | 726.3 | 661.7 | 702.7 | 162 | 220.2 | 277.9 | 234.7 | 316.6 | 308.4 | 216.1 | 290.5 | 407.7 | 283.2
2217.4 | 1998.4 | 559 | 223.6 | 261.3755 | 337.4 | 283.3 | 291.8 | 292.1 | 519.3 | 54.5 | 19 | 98.3 | 8.3 | 273.4 | 9.8 | 889.5 | 790.2 | 763.9 | 902.4 | 738 | 794.9 | 692.9 | 727 | 662 | 701.5 | 162.1 | 220.4 | 278.2 | 234.9 | 317 | 308.4 | 216.2 | 290.6 | 407.8 | 283.3
2218.4 | 1999.4 | 560.1 | 224.04 | 261.8899 | 336.8 | 282.4 | 292.8 | 290.1 | 524.2 | 54.5 | 19 | 98.3 | 8.4 | 289.9 | 10.6 | 887.1 | 783.6 | 762.1 | 899.6 | 736.5 | 795.3 | 690.5 | 730.1 | 661.6 | 700.4 | 162.3 | 220.5 | 278.3 | 235 | 317.3 | 308.5 | 216.3 | 290.6 | 408 | 283.4
2219.4 | 2000.4 | 561.1 | 224.44 | 262.3574 | 336.1 | 281.5 | 293.6 | 288.6 | 518.5 | 54.6 | 19 | 98.5 | 8 | 278.7 | 10.2 | 885.9 | 777.7 | 767.6 | 899 | 735.8 | 795.9 | 689.6 | 717.8 | 659.3 | 698.6 | 162.4 | 220.7 | 278.2 | 235.2 | 317.9 | 308.9 | 216.4 | 290.7 | 408.1 | 283.6
2220.4 | 2001.4 | 560.4 | 224.16 | 262.0301 | 336.2 | 281.2 | 294.2 | 288.2 | 511.7 | 54.7 | 19 | 98.4 | 8.7 | 272 | 10.4 | 883.4 | 781.7 | 765.3 | 893.4 | 733.5 | 796 | 687.9 | 713.3 | 657.8 | 696 | 162.6 | 220.8 | 278.2 | 235.3 | 317.9 | 309.1 | 216.5 | 290.8 | 408.3 | 283.7
2221.4 | 2002.4 | 559.7 | 223.88 | 261.7028 | 335.8 | 280.3 | 294 | 288.3 | 508 | 54.7 | 19 | 98.5 | 8.8 | 291.9 | 12.2 | 878.2 | 763.7 | 746.8 | 880.7 | 729.9 | 796.2 | 675 | 699.6 | 653.4 | 692.3 | 162.8 | 220.9 | 278.3 | 235.5 | 317.6 | 309.1 | 216.6 | 290.9 | 408.4 | 283.8
2222.4 | 2003.4 | 560.9 | 224.36 | 262.2639 | 335.3 | 279.7 | 293.8 | 288.1 | 496 | 54.8 | 19 | 98.4 | 9 | 294.5 | 13.5 | 873.7 | 758.7 | 743.4 | 873.9 | 728 | 796.8 | 665.8 | 681.6 | 647.1 | 688.8 | 162.9 | 221.1 | 278.4 | 235.6 | 317.1 | 308.8 | 216.7 | 290.9 | 408.4 | 283.9
2223.4 | 2004.4 | 560.4 | 224.16 | 262.0301 | 335 | 279.1 | 294.5 | 287.5 | 493.7 | 54.9 | 19 | 98.4 | 9 | 289.6 | 13.9 | 876.2 | 765.8 | 748.1 | 887.8 | 727.6 | 796.9 | 677.6 | 687.2 | 650.6 | 689.6 | 163.1 | 221.2 | 278.5 | 235.8 | 316.5 | 308.6 | 216.8 | 290.9 | 408.4 | 284
2224.4 | 2005.4 | 559.3 | 223.72 | 261.5158 | 336.2 | 279.5 | 293.6 | 288.2 | 497.4 | 55 | 19 | 98.4 | 8.2 | 299.1 | 13.2 | 877.3 | 761.4 | 750.6 | 893.7 | 726.6 | 796.5 | 674.9 | 684.9 | 650.2 | 687.7 | 163.3 | 221.3 | 278.6 | 236 | 316.4 | 308.7 | 216.9 | 291 | 408.5 | 284
2225.4 | 2006.4 | 560.6 | 224.24 | 262.1236 | 338.4 | 279.7 | 292.5 | 289.4 | 491.4 | 54.9 | 19 | 98.4 | 7.7 | 299.6 | 12.5 | 876.5 | 759.3 | 758.2 | 892.5 | 725 | 796.8 | 670.4 | 677.5 | 647.9 | 685.8 | 163.4 | 221.4 | 278.8 | 236.1 | 316.1 | 308.7 | 217 | 291 | 408.6 | 284.1
2226.4 | 2007.4 | 560.1 | 224.04 | 261.8899 | 339.4 | 279.7 | 291.3 | 289.9 | 485.3 | 54.9 | 19 | 98.4 | 9.4 | 299.6 | 12.6 | 875.1 | 749.6 | 763.8 | 889.4 | 724.2 | 797.2 | 662.7 | 670.9 | 645.1 | 683.3 | 163.6 | 221.5 | 278.7 | 236.3 | 315.7 | 308.8 | 217.1 | 291.1 | 408.7 | 284.2
2227.4 | 2008.4 | 560.1 | 224.04 | 261.8899 | 339.9 | 280.1 | 291.5 | 288.9 | 483.9 | 54.9 | 19 | 98.5 | 8.4 | 295.3 | 12.5 | 869 | 737.8 | 746.8 | 872.7 | 720.1 | 797.8 | 653.5 | 657.2 | 640.3 | 679.4 | 163.8 | 221.7 | 278.9 | 236.4 | 315.9 | 308.7 | 217.2 | 291.1 | 408.7 | 284.3
2228.4 | 2009.4 | 561.6 | 224.64 | 262.5912 | 340.2 | 280.6 | 292.4 | 288.4 | 486 | 54.9 | 19 | 98.6 | 7.9 | 314.2 | 11.8 | 865.1 | 742.7 | 741 | 862.1 | 717.1 | 798.4 | 654.1 | 666.7 | 638.5 | 677.6 | 163.9 | 221.8 | 279.1 | 236.6 | 315.7 | 308.5 | 217.3 | 291.2 | 408.8 | 284.4
2229.4 | 2010.4 | 562.4 | 224.96 | 262.9653 | 340.1 | 280.6 | 292.6 | 288 | 498.1 | 54.9 | 19 | 98.7 | 8.4 | 304 | 9.4 | 867.3 | 766 | 752 | 876.5 | 718.5 | 798.4 | 666.8 | 683 | 644 | 679.4 | 164.1 | 221.9 | 279.2 | 236.7 | 315.2 | 308.4 | 217.4 | 291.3 | 408.8 | 284.5
2230.4 | 2011.4 | 562.6 | 225.04 | 263.0588 | 339.7 | 280.4 | 294.4 | 288.1 | 500.6 | 54.9 | 19 | 98.8 | 9.1 | 296.3 | 8.7 | 871.1 | 778 | 764.4 | 893.2 | 719.4 | 798 | 679.4 | 683.9 | 648.5 | 682.6 | 164.2 | 222 | 279.3 | 236.9 | 314.7 | 308.5 | 217.5 | 291.4 | 408.9 | 284.6
2231.4 | 2012.4 | 563.4 | 225.36 | 263.4329 | 338.6 | 280.4 | 296 | 288.9 | 495.5 | 54.9 | 19 | 98.8 | 8.9 | 269.3 | 9.8 | 874.7 | 778.1 | 773.9 | 900.9 | 722.2 | 797.8 | 687.8 | 691.1 | 651.9 | 684.8 | 164.4 | 222.2 | 279.4 | 237.1 | 314.8 | 308.5 | 217.6 | 291.5 | 409.1 | 284.7
2232.4 | 2013.4 | 560.9 | 224.36 | 262.2639 | 338 | 280.6 | 296.5 | 288.7 | 517.3 | 54.9 | 19 | 98.7 | 8.9 | 274.8 | 11 | 875.9 | 781.2 | 768.3 | 900.3 | 723.1 | 797.4 | 695.8 | 706.7 | 655.6 | 686.6 | 164.6 | 222.3 | 279.6 | 237.2 | 314.7 | 308.7 | 217.7 | 291.6 | 409.3 | 284.8
2233.4 | 2014.4 | 560.8 | 224.32 | 262.2172 | 337.4 | 280.8 | 296.1 | 289.2 | 522.6 | 54.9 | 19 | 98.7 | 9.4 | 282.3 | 13.3 | 874.3 | 768.6 | 759.6 | 895.1 | 721.1 | 797.3 | 687.2 | 689.8 | 652.2 | 682.4 | 164.7 | 222.4 | 279.7 | 237.3 | 314.6 | 308.9 | 217.9 | 291.6 | 409.6 | 284.9
2234.4 | 2015.4 | 560.9 | 224.36 | 262.2639 | 336.5 | 280.9 | 296.1 | 289.8 | 513.6 | 55 | 19 | 98.8 | 9.8 | 280 | 12.8 | 876.5 | 780.6 | 756.9 | 901.3 | 721.3 | 797.5 | 688.5 | 695.1 | 652 | 683.1 | 164.9 | 222.4 | 279.8 | 237.5 | 314.6 | 308.7 | 218 | 291.7 | 409.7 | 285
2235.4 | 2016.4 | 561.5 | 224.6 | 262.5445 | 336.6 | 281.2 | 296.6 | 289.9 | 509.8 | 55 | 19 | 98.8 | 9.6 | 290.9 | 11.9 | 878.1 | 781.4 | 750.9 | 901.8 | 720.8 | 797.3 | 697.8 | 685.3 | 655.2 | 684 | 165 | 222.5 | 279.8 | 237.6 | 314.8 | 309.2 | 218.1 | 291.9 | 409.9 | 285.1
2236.4 | 2017.4 | 560.9 | 224.36 | 262.2639 | 335.9 | 281.1 | 297.1 | 289.3 | 506.9 | 55 | 19 | 98.9 | 10.4 | 280.6 | 11.8 | 876.7 | 776.2 | 735.1 | 895.3 | 718.2 | 796.9 | 702.3 | 681.8 | 658 | 683.5 | 165.2 | 222.6 | 279.9 | 237.7 | 315.4 | 309.6 | 218.2 | 292 | 410.1 | 285.2
2237.4 | 2018.4 | 560.5 | 224.2 | 262.0769 | 335.4 | 281.1 | 296.4 | 289.8 | 503.4 | 55.1 | 19 | 98.9 | 9.4 | 283.7 | 12.5 | 875.2 | 781.9 | 744.1 | 894.8 | 717 | 796.5 | 702.5 | 688.9 | 658.1 | 683.4 | 165.4 | 222.7 | 280.1 | 237.9 | 316.1 | 309.8 | 218.3 | 292 | 410.2 | 285.3
2238.4 | 2019.4 | 560.5 | 224.2 | 262.0769 | 334.6 | 281.3 | 295.5 | 290.2 | 505 | 55 | 19 | 98.8 | 8.3 | 287.2 | 12.4 | 874.1 | 784.5 | 760 | 895.4 | 717.5 | 796.4 | 701.3 | 695.8 | 658.5 | 683.6 | 165.5 | 222.8 | 280.1 | 238 | 316.2 | 309.8 | 218.4 | 292.1 | 410.3 | 285.5
2239.4 | 2020.4 | 561.9 | 224.76 | 262.7315 | 333.8 | 281.4 | 296.3 | 289.8 | 504 | 55 | 19 | 98.8 | 8.1 | 268 | 12.5 | 875.3 | 785.9 | 762.2 | 898.3 | 718.2 | 796.5 | 699.4 | 708.2 | 657.7 | 683.2 | 165.7 | 222.8 | 280.1 | 238.2 | 316.2 | 309.9 | 218.5 | 292.2 | 410.4 | 285.6
2240.4 | 2021.4 | 562.2 | 224.88 | 262.8718 | 332.8 | 281.3 | 296.9 | 290.4 | 505.5 | 55 | 19 | 98.8 | 7.8 | 272.8 | 11.9 | 877 | 780.9 | 760.6 | 906.5 | 716.5 | 796.7 | 697.5 | 707.9 | 656.1 | 681.7 | 165.9 | 222.9 | 280.4 | 238.3 | 316.3 | 310.2 | 218.6 | 292.3 | 410.6 | 285.6
2241.4 | 2022.4 | 561.7 | 224.68 | 262.638 | 332.1 | 281.4 | 297.3 | 290.3 | 520.5 | 54.9 | 19 | 98.8 | 8.2 | 276.4 | 11 | 879.5 | 790.2 | 777.3 | 911.5 | 718.6 | 796.8 | 703.8 | 728.6 | 658.5 | 684.2 | 166 | 223 | 280.7 | 238.5 | 316.4 | 310.8 | 218.8 | 292.4 | 410.7 | 285.7
2242.4 | 2023.4 | 561.7 | 224.68 | 262.638 | 332.3 | 281.5 | 296.6 | 290.3 | 525.9 | 54.9 | 19 | 98.9 | 8 | 264.5 | 10.7 | 881.6 | 805.1 | 789.3 | 914 | 720.2 | 796.5 | 706.4 | 737.4 | 658.9 | 686.7 | 166.2 | 223 | 280.7 | 238.7 | 316.1 | 310.8 | 218.9 | 292.4 | 410.8 | 285.8
2243.4 | 2024.4 | 562 | 224.8 | 262.7782 | 332.3 | 282.8 | 296.2 | 290.7 | 540.5 | 54.9 | 19 | 98.9 | 8 | 272.4 | 10 | 884.1 | 814.8 | 805.5 | 919.3 | 724.2 | 796.2 | 718 | 760 | 664 | 691 | 166.3 | 223.1 | 280.8 | 238.8 | 316.2 | 310.9 | 219 | 292.5 | 411 | 285.9
2244.4 | 2025.4 | 562.1 | 224.84 | 262.825 | 331.6 | 284.1 | 296.8 | 290.7 | 561.9 | 54.9 | 19 | 98.9 | 7.7 | 281.3 | 9.5 | 886.1 | 826.5 | 797.2 | 917.4 | 725.1 | 795.9 | 725.2 | 787.8 | 667.8 | 692.9 | 166.5 | 223.2 | 280.9 | 238.9 | 316.3 | 310.7 | 219.1 | 292.6 | 411.3 | 286
2245.4 | 2026.4 | 561.5 | 224.6 | 262.5445 | 331 | 283.8 | 297.1 | 291.4 | 577.2 | 54.9 | 19 | 98.9 | 7.7 | 273.7 | 8.9 | 886.4 | 829.9 | 797.4 | 909 | 725.7 | 795.7 | 721 | 803.8 | 666.8 | 691.4 | 166.7 | 223.3 | 281.4 | 239 | 316.5 | 310.5 | 219.3 | 292.5 | 411.6 | 286.1
2246.4 | 2027.4 | 561.1 | 224.44 | 262.3574 | 330.5 | 284.4 | 296.8 | 292.8 | 596.1 | 55 | 19 | 98.8 | 8.5 | 265.4 | 7.9 | 886.4 | 838.8 | 811.9 | 909.5 | 731.3 | 795.9 | 726.5 | 822.3 | 668.9 | 695.7 | 166.8 | 223.3 | 281.7 | 239.1 | 316.9 | 310.4 | 219.4 | 292.6 | 411.9 | 286.2
2247.4 | 2028.4 | 560.8 | 224.32 | 262.2172 | 330.6 | 284.5 | 296 | 295.9 | 607.2 | 55 | 19 | 98.7 | 8.4 | 276.1 | 7.8 | 887.4 | 831.3 | 813 | 916.6 | 733.3 | 796.1 | 731 | 806.4 | 669.3 | 699.3 | 167 | 223.4 | 281.7 | 239.2 | 317.1 | 310.4 | 219.5 | 292.6 | 412.3 | 286.4
2248.4 | 2029.4 | 560.3 | 224.12 | 261.9834 | 330.3 | 285.8 | 295.9 | 297.3 | 579.9 | 55.1 | 19 | 98.7 | 7.9 | 256 | 7.5 | 886.7 | 817.6 | 814.3 | 916.2 | 734.4 | 796.7 | 731.2 | 778.8 | 669.4 | 701.4 | 167.2 | 223.5 | 281.5 | 239.3 | 317 | 310.3 | 219.6 | 292.7 | 412.5 | 286.5
2249.4 | 2030.4 | 560 | 224 | 261.8431 | 330.2 | 287.2 | 296.1 | 297.9 | 561.3 | 55.1 | 19 | 98.7 | 7 | 246.9 | 8.4 | 886.3 | 814.5 | 812.6 | 914.9 | 735.7 | 797 | 724 | 770.9 | 667 | 701.7 | 167.3 | 223.5 | 281.6 | 239.4 | 317 | 310.4 | 219.8 | 292.7 | 412.8 | 286.6
2250.4 | 2031.4 | 560.5 | 224.2 | 262.0769 | 329.7 | 288 | 295.3 | 298.3 | 561 | 55.1 | 19 | 98.7 | 7.9 | 238.5 | 11.1 | 888.3 | 825.8 | 822.2 | 917 | 738.2 | 797.2 | 727.9 | 789.5 | 670.7 | 705.1 | 167.5 | 223.6 | 281.8 | 239.5 | 317.9 | 310.7 | 219.9 | 292.8 | 413 | 286.7
2251.4 | 2032.4 | 561.3 | 224.52 | 262.4509 | 329.3 | 289.2 | 294.1 | 299 | 570.3 | 55.1 | 19 | 98.7 | 8.4 | 226.6 | 12.3 | 889.4 | 834.2 | 826.8 | 921.7 | 738.9 | 796.8 | 733.7 | 790 | 674.1 | 706.8 | 167.6 | 223.6 | 281.9 | 239.7 | 317.8 | 310.7 | 220 | 292.8 | 413.1 | 286.8
2252.4 | 2033.4 | 561.4 | 224.56 | 262.4977 | 328.7 | 289.9 | 294 | 299 | 565.1 | 55.1 | 19 | 98.8 | 9.4 | 238.2 | 10.5 | 891.3 | 834.4 | 826.4 | 923.5 | 738.8 | 796.6 | 734.6 | 792.1 | 673.9 | 705.9 | 167.8 | 223.7 | 282.1 | 239.8 | 317.9 | 310.9 | 220.2 | 292.9 | 413.3 | 286.9
2253.4 | 2034.4 | 561.2 | 224.48 | 262.4042 | 328.1 | 290.7 | 292.2 | 299.8 | 565.7 | 55.1 | 19 | 98.8 | 10.4 | 224.8 | 8.8 | 890.8 | 824 | 826.3 | 922.2 | 740.2 | 796.3 | 736.2 | 781.8 | 674.9 | 706.9 | 168 | 223.7 | 282.1 | 239.8 | 318.2 | 311.4 | 220.3 | 293 | 413.5 | 287
2254.4 | 2035.4 | 559.8 | 223.92 | 261.7496 | 327.8 | 291.1 | 291.2 | 300.7 | 552.6 | 55 | 19 | 98.9 | 9.3 | 249.2 | 8 | 887.9 | 819.8 | 826.8 | 914.5 | 740.6 | 796.7 | 725.5 | 773.8 | 671.7 | 705.9 | 168.1 | 223.8 | 282.1 | 239.9 | 318.3 | 311.7 | 220.4 | 293.1 | 413.6 | 287.1
2255.4 | 2036.4 | 559.4 | 223.76 | 261.5625 | 327.9 | 291.5 | 291.9 | 300.4 | 565.4 | 55 | 19 | 98.9 | 9 | 260.5 | 9 | 889.3 | 834.1 | 833.4 | 926.1 | 742.7 | 796.9 | 734.2 | 786.6 | 675.8 | 710.7 | 168.3 | 223.9 | 282.3 | 240 | 318.1 | 311.6 | 220.6 | 293.2 | 413.7 | 287.2
2256.4 | 2037.4 | 509.1 | 203.64 | 238.0434 | 327.7 | 291.5 | 291.8 | 300.7 | 556.6 | 55.1 | 19 | 98.9 | 9.1 | 258.5 | 9.9 | 890.2 | 817.3 | 821.4 | 922.1 | 742.8 | 796.7 | 737.1 | 769 | 677.4 | 713.7 | 168.5 | 223.9 | 282.4 | 240.2 | 318 | 311.7 | 220.7 | 293.3 | 414 | 287.3
2257.4 | 2038.4 | 74.8 | 29.92 | 34.9748 | 327.3 | 291 | 290.9 | 299.6 | 547.2 | 55.1 | 19 | 98.8 | 9 | 239.8 | 9 | 889.3 | 806.5 | 813.9 | 910.5 | 742.4 | 796.8 | 734.3 | 755.4 | 676.4 | 711.7 | 168.6 | 224 | 282.4 | 240.4 | 317.8 | 311.9 | 220.8 | 293.4 | 414.3 | 287.4
2258.4 | 2039.4 | -6.9 | 0 | 0 | 326.5 | 290.3 | 290.5 | 297.1 | 527.1 | 55.2 | 19 | 98.7 | 9.5 | 236.5 | 10.5 | 880 | 756.1 | 770.6 | 883.4 | 736.7 | 797.4 | 709.4 | 715.5 | 666.4 | 704.6 | 168.8 | 224 | 282.2 | 240.5 | 317.5 | 311.9 | 220.9 | 293.5 | 414.5 | 287.5
2259.4 | 2040.4 | -6.9 | 0 | 0 | 325.3 | 289.7 | 288.9 | 294.7 | 499.7 | 55.2 | 19 | 98.6 | 8.6 | 244 | 11.5 | 864.5 | 702.1 | 709.9 | 839.3 | 727.3 | 798.1 | 671.6 | 672.6 | 651.1 | 695.8 | 168.9 | 224.1 | 281.9 | 240.6 | 317 | 311.5 | 221 | 293.3 | 414.5 | 287.5
2260.4 | 2041.4 | -6.9 | 0 | 0 | 323.3 | 289.4 | 287.7 | 293.1 | 475.1 | 55.3 | 18.9 | 98.5 | 8.5 | 252.6 | 12 | 848.6 | 659.6 | 660.2 | 803 | 719.4 | 797.9 | 635.6 | 638.9 | 636.1 | 687.7 | 169.1 | 224.2 | 281.8 | 240.6 | 316.3 | 310.6 | 221.2 | 293.1 | 414.4 | 287.6
2261.4 | 2042.4 | -6.9 | 0 | 0 | 321.1 | 288.7 | 285.9 | 290.4 | 455.4 | 55.2 | 19 | 98.5 | 8.9 | 241.3 | 12.7 | 833.5 | 622.9 | 619.2 | 768.4 | 711.5 | 797 | 606.3 | 605.3 | 620.7 | 680.9 | 169.3 | 224.3 | 281.7 | 240.7 | 315.7 | 309.6 | 221.3 | 292.9 | 414.2 | 287.7
2262.4 | 2043.4 | -6.9 | 0 | 0 | 318.7 | 287.5 | 284.4 | 287.2 | 438.2 | 55.1 | 19 | 98.5 | 7.9 | 244.9 | 14 | 819.3 | 591.3 | 583.6 | 739.2 | 704.1 | 796.3 | 581.1 | 574.1 | 608.9 | 673.9 | 169.4 | 224.4 | 281.5 | 240.6 | 314.8 | 308.6 | 221.4 | 292.6 | 414 | 287.7
2263.4 | 2044.4 | -6.9 | 0 | 0 | 316.5 | 285.9 | 282.3 | 284.9 | 422.2 | 55.1 | 19 | 98.1 | 9 | 243.7 | 13.2 | 805.6 | 566.7 | 553.9 | 716.1 | 697.4 | 795.6 | 560 | 550 | 598 | 666.7 | 169.6 | 224.5 | 281.4 | 240.5 | 313.5 | 307.6 | 221.5 | 292.4 | 413.7 | 287.7
2264.4 | 2045.4 | -6.9 | 0 | 0 | 314.3 | 283.9 | 279.7 | 282.4 | 408.2 | 55 | 19 | 97.6 | 9.3 | 236.3 | 13.6 | 792.5 | 542.8 | 526.8 | 692.4 | 690.8 | 794.6 | 539.4 | 525.9 | 586.3 | 660.1 | 169.7 | 224.6 | 281.2 | 240.4 | 311.7 | 305.9 | 221.6 | 292 | 413.5 | 287.8
2265.4 | 2046.4 | -6.9 | 0 | 0 | 312 | 281.8 | 276.8 | 279.2 | 396.7 | 54.9 | 19 | 97 | 9.8 | 256.9 | 15.7 | 779.5 | 524.4 | 507.1 | 674 | 684.6 | 793.6 | 521.3 | 504.2 | 575.7 | 653.7 | 169.9 | 224.7 | 281.1 | 240.3 | 309.7 | 303.9 | 221.7 | 291.6 | 413.2 | 287.8
2266.4 | 2047.4 | -6.9 | 0 | 0 | 309.6 | 279.5 | 273.9 | 276.4 | 385.7 | 54.8 | 19 | 96.2 | 9.7 | 258.6 | 13.9 | 766.9 | 508.9 | 488.6 | 656.7 | 678.5 | 792.6 | 506.5 | 483.4 | 569.3 | 648 | 170.1 | 224.7 | 280.9 | 240.2 | 307.7 | 301.6 | 221.8 | 291.2 | 413 | 287.8
2267.4 | 2048.4 | -6.9 | 0 | 0 | 306.8 | 277.3 | 271.2 | 274 | 375.7 | 54.7 | 18.9 | 95.4 | 9 | 254.4 | 11.5 | 754.6 | 493.3 | 468.6 | 636 | 672.4 | 791.2 | 493.3 | 467.7 | 563.7 | 642.2 | 170.2 | 224.8 | 280.8 | 240.1 | 305.8 | 299.2 | 221.9 | 290.7 | 412.8 | 287.8
2268.4 | 2049.4 | -6.9 | 0 | 0 | 303.8 | 275 | 268.8 | 271.6 | 366.5 | 54.5 | 18.9 | 94.7 | 7.6 | 252.4 | 13.8 | 742.8 | 478.5 | 453.5 | 619.1 | 667 | 789.7 | 481.3 | 450.6 | 557.4 | 636.7 | 170.4 | 224.8 | 280.6 | 240 | 303.9 | 296.9 | 222.1 | 290.2 | 412.6 | 287.7
2269.4 | 2050.4 | -6.8 | 0 | 0 | 301 | 272.6 | 266.5 | 269.6 | 358 | 54.4 | 18.9 | 94.1 | 7.4 | 258.3 | 14.5 | 731.2 | 465.1 | 436.5 | 602.6 | 661.9 | 788.2 | 468.8 | 436.5 | 551.9 | 631.4 | 170.5 | 224.9 | 280.4 | 239.9 | 302 | 294.8 | 222.1 | 289.7 | 412.4 | 287.7
2270.4 | 2051.4 | -6.8 | 0 | 0 | 298.3 | 270.2 | 263.8 | 267.2 | 350.3 | 54.3 | 18.9 | 93.6 | 7.4 | 250.6 | 12.6 | 720.1 | 451.1 | 420.3 | 584.1 | 656.2 | 786.5 | 459.8 | 424.8 | 546.6 | 626.3 | 170.7 | 225 | 280.3 | 239.8 | 300.1 | 292.7 | 222.2 | 289.3 | 412.1 | 287.7
2271.4 | 2052.4 | -6.8 | 0 | 0 | 295.9 | 267.8 | 261 | 264.9 | 343.4 | 54.1 | 18.9 | 93.1 | 7.7 | 252.9 | 10.2 | 709.2 | 437.3 | 404.4 | 565.3 | 650.6 | 784.9 | 449.5 | 413.1 | 540.2 | 620.9 | 170.9 | 225.1 | 280.1 | 239.6 | 298.1 | 290.7 | 222.3 | 288.9 | 411.9 | 287.7
2272.4 | 2053.4 | -6.8 | 0 | 0 | 293.7 | 265.2 | 258.5 | 262.3 | 337 | 53.9 | 18.9 | 92.7 | 8.1 | 278 | 9 | 699.2 | 427.6 | 391.9 | 553.5 | 644.9 | 783.7 | 439.7 | 399.7 | 534.2 | 615.6 | 171 | 225.1 | 280 | 239.5 | 296.1 | 288.7 | 222.4 | 288.4 | 411.7 | 287.7
2273.4 | 2054.4 | -6.8 | 0 | 0 | 291.6 | 263 | 256.1 | 259.9 | 331 | 53.8 | 18.9 | 92.2 | 8.2 | 278.4 | 8.8 | 689.5 | 422.1 | 382.2 | 545.8 | 640.2 | 782.5 | 432.7 | 388.4 | 530.4 | 611.4 | 171.2 | 225.2 | 279.8 | 239.3 | 294.1 | 286.9 | 222.5 | 287.9 | 411.5 | 287.6
2274.4 | 2055.4 | -6.8 | 0 | 0 | 289.5 | 261.2 | 253.8 | 257.6 | 325.9 | 53.6 | 18.9 | 91.9 | 7.8 | 257.4 | 8.6 | 680.4 | 414.1 | 372.4 | 537 | 634.9 | 780.7 | 426 | 379.3 | 526.2 | 607.4 | 171.3 | 225.3 | 279.6 | 239.1 | 292.4 | 285 | 222.6 | 287.4 | 411.2 | 287.6
2275.4 | 2056.4 | -6.8 | 0 | 0 | 287.6 | 259.6 | 251.9 | 255.4 | 321.1 | 53.5 | 18.9 | 91.5 | 8.4 | 281.9 | 7.7 | 672 | 406.4 | 365 | 532.6 | 630.3 | 778.8 | 419.3 | 369.9 | 522 | 603.3 | 171.5 | 225.4 | 279.5 | 239 | 291.1 | 283.3 | 222.7 | 287 | 411 | 287.6
2276.4 | 2057.4 | -6.8 | 0 | 0 | 285.9 | 257.8 | 250 | 253.6 | 317 | 53.4 | 18.9 | 91.3 | 9.7 | 228.5 | 6.6 | 664.1 | 399.6 | 357.2 | 528.2 | 626.3 | 776.6 | 414.8 | 362.5 | 517.9 | 599.3 | 171.7 | 225.5 | 279.3 | 238.9 | 289.8 | 281.5 | 222.8 | 286.5 | 410.7 | 287.5
2277.4 | 2058.4 | -6.8 | 0 | 0 | 284.1 | 256 | 247.8 | 251.9 | 313.1 | 53.4 | 18.9 | 90.9 | 8.6 | 231.3 | 6.5 | 656.2 | 393.5 | 349.1 | 522.2 | 621.9 | 774.6 | 410.1 | 354.5 | 513.7 | 595 | 171.8 | 225.6 | 279.1 | 238.7 | 288.6 | 279.7 | 222.9 | 286.1 | 410.5 | 287.5
2278.4 | 2059.4 | -6.8 | 0 | 0 | 282.4 | 254 | 245.5 | 250.2 | 309.4 | 53.3 | 18.9 | 90.5 | 8.3 | 247.3 | 6.6 | 648.4 | 385.9 | 340.3 | 515.7 | 617.6 | 772.6 | 405.2 | 347.6 | 510.1 | 591.1 | 172 | 225.7 | 279 | 238.5 | 287.2 | 278 | 223 | 285.6 | 410.2 | 287.4
2279.4 | 2060.4 | -6.8 | 0 | 0 | 280.6 | 252.2 | 243.9 | 248.7 | 306.2 | 53.4 | 18.9 | 90.1 | 8.4 | 251.1 | 7.4 | 641.2 | 381.7 | 332.8 | 511.9 | 613.3 | 770.6 | 401.3 | 340.9 | 506.8 | 587.7 | 172.1 | 225.8 | 278.8 | 238.3 | 285.9 | 276.5 | 223.1 | 285.2 | 409.9 | 287.4
2280.4 | 2061.4 | -6.8 | 0 | 0 | 279.1 | 250.5 | 242.4 | 247.2 | 303 | 53.3 | 18.9 | 89.8 | 8.5 | 261.6 | 7.8 | 634.5 | 375.3 | 325.3 | 510.8 | 608.9 | 768.6 | 397.7 | 335.6 | 502.9 | 584.1 | 172.3 | 225.9 | 278.6 | 238.1 | 284.7 | 274.8 | 223.2 | 284.7 | 409.7 | 287.4
2281.4 | 2062.4 | -6.8 | 0 | 0 | 277.7 | 249 | 240.6 | 245.9 | 299.8 | 53.3 | 18.9 | 89.5 | 7.7 | 265.2 | 7.1 | 628 | 370.8 | 318.4 | 508.5 | 605.2 | 766.4 | 395.7 | 331.4 | 500.9 | 580.2 | 172.4 | 226 | 278.5 | 238 | 283.4 | 273.1 | 223.3 | 284.2 | 409.4 | 287.3
2282.4 | 2063.4 | -6.8 | 0 | 0 | 276.3 | 247.8 | 239.4 | 244.8 | 297.2 | 53.2 | 18.9 | 89.1 | 7.9 | 278.9 | 6.2 | 621.7 | 364 | 313.1 | 504.3 | 601.3 | 764.3 | 394.3 | 325.7 | 498.9 | 576.2 | 172.6 | 226.1 | 278.3 | 237.8 | 282.3 | 271.7 | 223.4 | 283.8 | 409.1 | 287.3
2283.4 | 2064.4 | -6.8 | 0 | 0 | 275 | 246.6 | 238.3 | 243.3 | 295 | 53.1 | 18.9 | 88.7 | 9 | 263.8 | 6.1 | 615.1 | 358.7 | 307.9 | 498.2 | 597.5 | 762.2 | 392 | 320 | 495.9 | 572.8 | 172.8 | 226.2 | 278.1 | 237.6 | 281 | 270.2 | 223.5 | 283.3 | 408.8 | 287.2
2284.4 | 2065.4 | -6.8 | 0 | 0 | 273.5 | 245.4 | 237 | 242 | 293.4 | 53.1 | 18.9 | 88.3 | 8.6 | 254.9 | 6.2 | 608.3 | 353.6 | 303.1 | 490.6 | 593.9 | 760.2 | 387.7 | 314.4 | 493.7 | 569.4 | 172.9 | 226.3 | 277.9 | 237.4 | 279.6 | 268.5 | 223.6 | 282.8 | 408.5 | 287.2
2285.4 | 2066.4 | -6.8 | 0 | 0 | 272 | 244.1 | 236 | 241 | 290.9 | 53 | 18.9 | 87.8 | 8.1 | 259.9 | 6.3 | 601.5 | 348.9 | 297.3 | 480 | 590.1 | 758.2 | 383.4 | 310.2 | 490.8 | 566.1 | 173.1 | 226.3 | 277.8 | 237.2 | 278.2 | 267.1 | 223.6 | 282.4 | 408.2 | 287.1
2286.4 | 2067.4 | -6.8 | 0 | 0 | 270.7 | 242.6 | 235 | 240.1 | 288.4 | 52.9 | 18.9 | 87.3 | 9.1 | 260.6 | 5.9 | 595.1 | 343 | 291.7 | 473 | 586.6 | 756.5 | 378.4 | 304.3 | 488.6 | 562.7 | 173.2 | 226.4 | 277.6 | 237 | 276.8 | 265.6 | 223.7 | 281.9 | 407.9 | 287
2287.4 | 2068.4 | -6.8 | 0 | 0 | 269.6 | 241.4 | 233.8 | 238.9 | 285.9 | 52.8 | 18.9 | 86.9 | 8.9 | 281.3 | 6.9 | 589.1 | 337.9 | 286.1 | 468.4 | 583 | 754.8 | 375.4 | 301.2 | 486.4 | 559.4 | 173.4 | 226.5 | 277.4 | 236.8 | 275.6 | 264.2 | 223.8 | 281.4 | 407.6 | 287
2288.4 | 2069.4 | -6.8 | 0 | 0 | 268.4 | 240.4 | 232.6 | 237.8 | 283.7 | 52.6 | 18.9 | 86.3 | 9.5 | 256.7 | 8.3 | 583.5 | 333.4 | 281.5 | 463.5 | 579.7 | 752.8 | 372.7 | 297.3 | 484.1 | 557 | 173.5 | 226.5 | 277.2 | 236.6 | 274.3 | 263 | 223.9 | 281 | 407.4 | 286.9
2289.4 | 2070.4 | -6.8 | 0 | 0 | 267.3 | 239.5 | 231.5 | 236.9 | 282 | 52.4 | 18.9 | 85.8 | 8.4 | 299.2 | 8 | 577.9 | 328.3 | 276.8 | 456.8 | 576.3 | 750.9 | 370.7 | 293.3 | 481.6 | 554.1 | 173.7 | 226.6 | 277 | 236.5 | 273 | 261.9 | 224 | 280.5 | 407.1 | 286.9
2290.4 | 2071.4 | -6.8 | 0 | 0 | 266.2 | 238.3 | 230.5 | 235.8 | 280.2 | 52.3 | 18.9 | 85.3 | 9.3 | 287.4 | 8.1 | 572.5 | 322.4 | 272.2 | 451.6 | 572.8 | 749 | 367.9 | 289.6 | 479.3 | 551.1 | 173.9 | 226.6 | 276.9 | 236.3 | 271.9 | 260.7 | 224.1 | 280.1 | 406.8 | 286.8
2291.4 | 2072.4 | -6.8 | 0 | 0 | 265.1 | 237 | 229.6 | 234.7 | 278.6 | 52.2 | 18.9 | 84.9 | 9 | 270.7 | 8.6 | 566.6 | 317.3 | 267 | 443.7 | 569.5 | 747 | 365.4 | 287.3 | 476.6 | 548.3 | 174 | 226.7 | 276.7 | 236.1 | 271 | 259.4 | 224.1 | 279.7 | 406.5 | 286.7
2292.4 | 2073.4 | -6.8 | 0 | 0 | 263.8 | 235.6 | 228.7 | 233.7 | 277.1 | 52 | 18.9 | 84.3 | 8.5 | 262.1 | 8 | 561.2 | 313.1 | 262.4 | 437.3 | 566.1 | 745 | 362.5 | 284.7 | 474.9 | 545.3 | 174.2 | 226.8 | 276.5 | 235.9 | 270.3 | 258.2 | 224.2 | 279.3 | 406.1 | 286.7
2293.4 | 2074.4 | -6.8 | 0 | 0 | 262.6 | 234.6 | 227.7 | 233 | 275.7 | 51.8 | 18.9 | 83.8 | 9.4 | 262.6 | 11.4 | 556.1 | 308.1 | 258.4 | 432.6 | 563 | 743.2 | 359.3 | 280.3 | 471.6 | 542.4 | 174.3 | 226.8 | 276.3 | 235.7 | 269.3 | 257.1 | 224.3 | 278.8 | 405.8 | 286.6
2294.4 | 2075.4 | -6.8 | 0 | 0 | 261.6 | 233.7 | 226.9 | 231.8 | 274.2 | 51.7 | 18.9 | 83.4 | 9 | 269.2 | 14.5 | 551.2 | 303 | 254.1 | 428.3 | 559.8 | 741.3 | 357.8 | 276.5 | 468.8 | 539.5 | 174.5 | 226.9 | 276.2 | 235.5 | 268.3 | 256 | 224.4 | 278.4 | 405.5 | 286.5
2295.4 | 2076.4 | -6.8 | 0 | 0 | 260.2 | 233.1 | 226.2 | 230.9 | 272.6 | 51.5 | 18.9 | 83 | 9.5 | 269.5 | 13.6 | 546.1 | 298.3 | 250 | 421 | 556.6 | 739.3 | 357.1 | 275.5 | 466.7 | 537.3 | 174.6 | 227 | 276 | 235.3 | 267.3 | 255 | 224.5 | 277.9 | 405.1 | 286.5
2296.4 | 2077.4 | -6.8 | 0 | 0 | 259.1 | 232.3 | 225.4 | 230.2 | 271.2 | 51.3 | 18.9 | 82.6 | 10 | 264.5 | 15 | 541.1 | 293.5 | 246 | 413.6 | 553 | 737.3 | 356 | 272.9 | 465.2 | 535 | 174.8 | 227.1 | 275.8 | 235.1 | 266.3 | 253.8 | 224.5 | 277.5 | 404.8 | 286.4
2297.4 | 2078.4 | -6.8 | 0 | 0 | 258.3 | 231.7 | 224.7 | 229.3 | 270.3 | 51.1 | 18.9 | 82.2 | 9.4 | 261.9 | 15.2 | 536.3 | 287.4 | 242.1 | 405.1 | 549.6 | 735.8 | 352.2 | 268.6 | 462.9 | 532.4 | 174.9 | 227.1 | 275.6 | 234.9 | 265.5 | 252.8 | 224.6 | 277.1 | 404.5 | 286.3
2298.4 | 2079.4 | -6.8 | 0 | 0 | 256.9 | 231 | 223.7 | 228.5 | 269 | 51 | 18.9 | 81.7 | 9.4 | 261.5 | 14.2 | 531.6 | 283.2 | 238.4 | 397.7 | 546.3 | 734.3 | 349 | 265.1 | 461.4 | 529.1 | 175.1 | 227.2 | 275.4 | 234.7 | 265.1 | 251.8 | 224.7 | 276.6 | 404.1 | 286.2
2299.4 | 2080.4 | -6.8 | 0 | 0 | 255.9 | 230.1 | 222.7 | 227.9 | 267.5 | 50.8 | 18.9 | 81.3 | 9.6 | 257.8 | 13.2 | 527.1 | 279.8 | 234.8 | 393.2 | 542.8 | 732.5 | 347.8 | 261.6 | 460.9 | 526.7 | 175.2 | 227.3 | 275.2 | 234.6 | 264.5 | 250.8 | 224.8 | 276.2 | 403.8 | 286.2
2300.4 | 2081.4 | -6.8 | 0 | 0 | 255.1 | 229.2 | 221.9 | 227.3 | 266.2 | 50.7 | 18.9 | 81 | 9.9 | 259 | 13.6 | 522.8 | 277.4 | 231.9 | 390.3 | 539.5 | 730.8 | 347.8 | 258.7 | 459.2 | 524.9 | 175.4 | 227.3 | 275.1 | 234.4 | 263.9 | 249.8 | 224.9 | 275.8 | 403.5 | 286.1
2301.4 | 2082.4 | -6.8 | 0 | 0 | 254.2 | 228.6 | 221.1 | 226.4 | 265.2 | 50.5 | 18.9 | 80.8 | 9.9 | 257.3 | 14.2 | 518.9 | 273.1 | 229 | 388.7 | 536.8 | 729.1 | 347.8 | 256.5 | 457.4 | 522.4 | 175.5 | 227.4 | 274.9 | 234.2 | 262.9 | 248.9 | 224.9 | 275.4 | 403.1 | 286
2302.4 | 2083.4 | -6.8 | 0 | 0 | 253.5 | 228.1 | 220.3 | 225.8 | 264.2 | 50.4 | 18.9 | 80.4 | 9.8 | 265.7 | 14.8 | 515.1 | 269.7 | 226.2 | 387.7 | 534 | 727.2 | 348.4 | 254.4 | 457.3 | 520.5 | 175.7 | 227.4 | 274.7 | 234 | 262 | 248 | 225 | 274.9 | 402.8 | 285.9
2303.4 | 2084.4 | -6.8 | 0 | 0 | 253 | 227.6 | 219.4 | 224.9 | 263.8 | 50.3 | 18.9 | 80 | 9.7 | 260.5 | 15.9 | 511.3 | 266 | 223.4 | 386.3 | 531.6 | 725.4 | 347.5 | 253.2 | 455.4 | 518.8 | 175.8 | 227.5 | 274.5 | 233.8 | 261.3 | 247.1 | 225.1 | 274.5 | 402.5 | 285.9
2304.4 | 2085.4 | -6.8 | 0 | 0 | 252.6 | 227.1 | 219 | 224.4 | 262.5 | 50.2 | 18.9 | 79.6 | 9.8 | 268.9 | 15.1 | 507.5 | 262.5 | 220.8 | 385 | 528.9 | 723.7 | 346.9 | 251.7 | 455.1 | 517 | 175.9 | 227.5 | 274.4 | 233.6 | 260.7 | 246.3 | 225.1 | 274 | 402.1 | 285.8
2305.4 | 2086.4 | -6.8 | 0 | 0 | 251.9 | 226.5 | 218.3 | 223.8 | 261.5 | 50.2 | 18.9 | 79.3 | 9.7 | 275.2 | 16 | 503.9 | 259.5 | 218.3 | 383.1 | 526.3 | 722 | 346.5 | 251.6 | 454.3 | 515.1 | 176.1 | 227.6 | 274.2 | 233.5 | 260.1 | 245.6 | 225.2 | 273.6 | 401.8 | 285.7
2306.4 | 2087.4 | -6.8 | 0 | 0 | 251.2 | 225.9 | 217.7 | 223.4 | 260.8 | 50.2 | 18.9 | 79 | 9.9 | 278.4 | 14.7 | 500.1 | 257.4 | 214.7 | 379.7 | 523.5 | 720.3 | 345.6 | 249.5 | 453.8 | 513.4 | 176.2 | 227.6 | 274 | 233.3 | 259.3 | 244.7 | 225.3 | 273.2 | 401.4 | 285.6
2307.4 | 2088.4 | -6.8 | 0 | 0 | 250.5 | 225.3 | 217.2 | 222.8 | 260.5 | 50.2 | 18.9 | 78.7 | 9.6 | 281.4 | 15.6 | 496.6 | 254.1 | 211.1 | 376.4 | 520.6 | 718.8 | 343.7 | 249 | 449.7 | 511.7 | 176.4 | 227.6 | 273.8 | 233.1 | 258.6 | 243.8 | 225.3 | 272.8 | 401 | 285.5
2308.4 | 2089.4 | -6.8 | 0 | 0 | 249.8 | 224.9 | 216.6 | 222 | 259.6 | 50.1 | 18.9 | 78.3 | 9.6 | 269.2 | 13.8 | 493.1 | 250.2 | 208 | 372.2 | 518 | 717.1 | 342.2 | 247.9 | 448.2 | 509.4 | 176.5 | 227.7 | 273.6 | 232.9 | 257.8 | 243 | 225.4 | 272.4 | 400.7 | 285.5
2309.4 | 2090.4 | -6.8 | 0 | 0 | 249.1 | 224.3 | 216.2 | 221.5 | 258.3 | 49.9 | 18.9 | 78 | 9.1 | 282 | 11.5 | 489.2 | 246.9 | 205.3 | 367.8 | 515.3 | 715.5 | 339.4 | 245.5 | 446.6 | 506.9 | 176.7 | 227.7 | 273.5 | 232.7 | 257.3 | 242.3 | 225.5 | 272 | 400.3 | 285.4
2310.4 | 2091.4 | -6.8 | 0 | 0 | 248.5 | 223.9 | 215.7 | 220.8 | 257.2 | 49.6 | 18.9 | 77.7 | 8.8 | 293.3 | 10.2 | 485.5 | 242.9 | 202.7 | 363.7 | 512.9 | 713.9 | 337.6 | 243.7 | 445 | 504.2 | 176.8 | 227.8 | 273.3 | 232.6 | 256.8 | 241.4 | 225.5 | 271.6 | 400 | 285.3
2311.4 | 2092.4 | -6.8 | 0 | 0 | 247.8 | 223.4 | 215.1 | 220.3 | 256.5 | 49.3 | 18.9 | 77.4 | 8.8 | 249.7 | 9.4 | 481.5 | 243.2 | 200.1 | 359.3 | 509.9 | 712.1 | 337 | 243 | 443.3 | 501.6 | 177 | 227.8 | 273.1 | 232.4 | 256.3 | 240.7 | 225.6 | 271.1 | 399.6 | 285.2
2312.4 | 2093.4 | -6.8 | 0 | 0 | 247.4 | 223 | 214.6 | 219.8 | 255.7 | 49 | 18.9 | 77 | 9.2 | 261.1 | 11.1 | 477.5 | 241.3 | 198.2 | 355.4 | 507.4 | 710.4 | 335.9 | 242.7 | 442.3 | 499.9 | 177.1 | 227.8 | 272.9 | 232.2 | 256 | 239.9 | 225.7 | 270.7 | 399.2 | 285.1
2313.4 | 2094.4 | -6.8 | 0 | 0 | 247 | 222.5 | 214.3 | 219.1 | 255 | 48.8 | 18.9 | 76.8 | 10.3 | 259.9 | 11.9 | 474.2 | 237.8 | 196.1 | 353.5 | 505 | 708.7 | 335.5 | 242.2 | 441.6 | 498.2 | 177.2 | 227.9 | 272.7 | 232 | 255.7 | 239.2 | 225.7 | 270.3 | 398.9 | 285
2314.4 | 2095.4 | -6.8 | 0 | 0 | 246.3 | 221.9 | 213.6 | 218.6 | 254.5 | 48.6 | 18.9 | 76.4 | 9.8 | 267 | 13.9 | 470.6 | 235.5 | 193.5 | 348.6 | 502.7 | 707.1 | 335.1 | 240.6 | 440.2 | 496.4 | 177.4 | 227.9 | 272.6 | 231.8 | 255.3 | 238.4 | 225.8 | 269.9 | 398.5 | 284.9
2315.4 | 2096.4 | -6.8 | 0 | 0 | 245.9 | 221.3 | 213.1 | 218.1 | 254.1 | 48.6 | 18.9 | 76 | 10.4 | 262 | 16.8 | 467.3 | 230.7 | 190.7 | 342.9 | 500.1 | 705.5 | 333.9 | 238.2 | 439 | 494.6 | 177.5 | 227.9 | 272.4 | 231.7 | 254.8 | 237.6 | 225.9 | 269.5 | 398.1 | 284.9
2316.4 | 2097.4 | -6.8 | 0 | 0 | 245.4 | 220.7 | 212.6 | 217.5 | 253.3 | 48.5 | 18.9 | 75.7 | 9 | 260.7 | 16.4 | 464.2 | 229.6 | 187.9 | 339.4 | 497.8 | 704.3 | 331.3 | 236.5 | 436 | 492.6 | 177.7 | 228 | 272.2 | 231.5 | 254.2 | 236.9 | 225.9 | 269.1 | 397.7 | 284.8
2317.4 | 2098.4 | -6.8 | 0 | 0 | 244.7 | 220.2 | 211.9 | 217 | 252.5 | 48.4 | 19 | 75.4 | 7.6 | 250.2 | 16.4 | 461.3 | 225.8 | 185.3 | 336.8 | 495.5 | 703 | 329.7 | 235.1 | 435.1 | 490.8 | 177.8 | 228 | 272 | 231.3 | 253.5 | 236.1 | 226 | 268.7 | 397.4 | 284.7
2318.4 | 2099.4 | -6.8 | 0 | 0 | 244.1 | 219.8 | 211.1 | 216.5 | 251.4 | 48.2 | 19 | 75.1 | 8 | 248.8 | 15.8 | 458.4 | 223.7 | 182.7 | 334.9 | 493.3 | 701.6 | 327.3 | 233.2 | 434.6 | 488.4 | 178 | 228.1 | 271.8 | 231.1 | 252.8 | 235.4 | 226 | 268.2 | 397 | 284.6
2319.4 | 2100.4 | -6.8 | 0 | 0 | 243.6 | 219.4 | 210.6 | 215.9 | 250.4 | 47.9 | 19 | 74.8 | 7.2 | 247.4 | 16 | 455.8 | 221.4 | 180.4 | 334.7 | 490.6 | 700.1 | 326.8 | 232 | 433.7 | 486.7 | 178.1 | 228.1 | 271.7 | 231 | 252.3 | 234.7 | 226.1 | 267.8 | 396.6 | 284.5
2320.4 | 2101.4 | -6.8 | 0 | 0 | 243.2 | 219.1 | 210.1 | 215.3 | 250 | 47.6 | 19 | 74.6 | 7.4 | 246.1 | 16.4 | 453.4 | 218.5 | 177.5 | 334 | 488.1 | 698.7 | 327.3 | 230.1 | 432.6 | 485.2 | 178.2 | 228.2 | 271.5 | 230.8 | 252 | 234.1 | 226.2 | 267.4 | 396.2 | 284.4
2321.4 | 2102.4 | -6.8 | 0 | 0 | 243 | 218.7 | 209.9 | 214.7 | 249.2 | 47.4 | 19 | 74.4 | 8.3 | 245.6 | 13.7 | 450.9 | 216.7 | 176.1 | 332.3 | 485.9 | 697.3 | 326.7 | 228.1 | 432.1 | 483.6 | 178.4 | 228.2 | 271.3 | 230.6 | 251.4 | 233.3 | 226.2 | 267 | 395.9 | 284.3
2322.4 | 2103.4 | -6.8 | 0 | 0 | 242.8 | 218.2 | 209.5 | 214.1 | 248.7 | 47.3 | 19 | 74.2 | 9.5 | 253.2 | 12.1 | 448.2 | 218.2 | 174.1 | 330.3 | 483.6 | 695.9 | 326.7 | 226.9 | 431.7 | 482.1 | 178.5 | 228.3 | 271.1 | 230.4 | 250.7 | 232.6 | 226.3 | 266.6 | 395.5 | 284.2
2323.4 | 2104.4 | -6.8 | 0 | 0 | 242.4 | 217.8 | 209.1 | 213.5 | 248 | 47.2 | 19 | 74 | 8.3 | 243 | 11 | 445.2 | 217.5 | 172.9 | 328 | 481.2 | 694.4 | 327.3 | 225.7 | 431 | 480.6 | 178.6 | 228.3 | 270.9 | 230.2 | 250.3 | 231.9 | 226.3 | 266.2 | 395.2 | 284.1
2324.4 | 2105.4 | -6.8 | 0 | 0 | 242 | 217.3 | 208.4 | 213.1 | 247.6 | 47.2 | 19 | 73.8 | 7.7 | 272.8 | 9.3 | 442.4 | 216.4 | 171 | 326.3 | 478.8 | 692.8 | 327.3 | 224.4 | 430.1 | 479.4 | 178.8 | 228.3 | 270.8 | 230.1 | 249.9 | 231.3 | 226.4 | 265.8 | 394.8 | 284
2325.4 | 2106.4 | -6.8 | 0 | 0 | 241.6 | 216.8 | 208 | 212.5 | 248 | 47.2 | 19 | 73.6 | 6.5 | 257.2 | 9.4 | 440 | 213.4 | 169.3 | 325.1 | 476.5 | 691.3 | 326.6 | 223.9 | 429 | 478 | 178.9 | 228.3 | 270.6 | 229.9 | 249.7 | 230.6 | 226.4 | 265.4 | 394.4 | 283.9
2326.4 | 2107.4 | -6.8 | 0 | 0 | 240.9 | 216.4 | 207.9 | 212 | 247.8 | 47.2 | 19 | 73.4 | 7.6 | 262.3 | 11 | 437.4 | 210.8 | 168.1 | 322.9 | 474.2 | 689.9 | 326 | 222.8 | 429.5 | 476.5 | 179.1 | 228.4 | 270.4 | 229.7 | 249 | 230 | 226.5 | 265.1 | 394.1 | 283.8
2327.4 | 2108.4 | -6.8 | 0 | 0 | 240.2 | 216 | 207.6 | 211.7 | 247 | 47.1 | 19 | 73.2 | 9.6 | 256.9 | 9.7 | 435 | 209.8 | 166.9 | 321.4 | 472 | 688.6 | 325 | 220.9 | 427.4 | 475.1 | 179.2 | 228.3 | 270.2 | 229.5 | 248.4 | 229.6 | 226.5 | 264.7 | 393.7 | 283.7
2328.4 | 2109.4 | -6.8 | 0 | 0 | 239.8 | 215.6 | 207.1 | 211.6 | 246.3 | 47 | 19 | 73 | 8.8 | 239.4 | 9.4 | 432.4 | 209.8 | 164.7 | 319.8 | 469.7 | 687.3 | 324.9 | 220.9 | 425.8 | 473.2 | 179.3 | 228.3 | 270 | 229.4 | 248 | 229.1 | 226.6 | 264.3 | 393.3 | 283.6
2329.4 | 2110.4 | -6.8 | 0 | 0 | 239.5 | 215.1 | 206.9 | 211.3 | 246.2 | 46.8 | 19 | 72.7 | 8.7 | 251.5 | 12.8 | 429.9 | 208.8 | 163.1 | 318.3 | 467.3 | 686 | 325.1 | 220.2 | 424.8 | 471.8 | 179.5 | 228.3 | 269.9 | 229.2 | 247.8 | 228.5 | 226.6 | 264 | 392.9 | 283.5
2330.4 | 2111.4 | -6.8 | 0 | 0 | 239.2 | 214.7 | 206.6 | 210.8 | 245.3 | 46.7 | 19 | 72.5 | 10.4 | 245.1 | 16.4 | 427.4 | 206.7 | 161.7 | 317.5 | 464.9 | 684.6 | 324.8 | 218.5 | 425.4 | 470.6 | 179.6 | 228.3 | 269.7 | 229.1 | 247.6 | 228 | 226.7 | 263.6 | 392.5 | 283.4
2331.4 | 2112.4 | -6.8 | 0 | 0 | 238.8 | 214.3 | 206.1 | 210.4 | 245.1 | 46.4 | 19 | 72.2 | 9.8 | 254.8 | 16 | 425 | 203.8 | 159.8 | 315.9 | 462.9 | 683.2 | 324.1 | 217.1 | 424.4 | 469.4 | 179.7 | 228.3 | 269.5 | 228.9 | 246.8 | 227.4 | 226.7 | 263.2 | 392.1 | 283.3
2332.4 | 2113.4 | -6.8 | 0 | 0 | 238.3 | 213.9 | 205.4 | 210 | 244.6 | 46.2 | 19 | 71.9 | 9.6 | 231.5 | 13 | 422.8 | 200.7 | 158.2 | 314.9 | 460.8 | 681.8 | 323.9 | 216.9 | 423.7 | 468 | 179.9 | 228.3 | 269.3 | 228.8 | 246.4 | 226.9 | 226.8 | 262.8 | 391.8 | 283.2
2333.4 | 2114.4 | -6.8 | 0 | 0 | 237.6 | 213.5 | 204.9 | 209.7 | 244.5 | 46.1 | 19 | 71.6 | 11.1 | 250.2 | 15.5 | 420.5 | 198.3 | 157 | 312.5 | 458.9 | 680.5 | 322.9 | 214.8 | 422.2 | 466.7 | 180 | 228.3 | 269.2 | 228.6 | 245.8 | 226.3 | 226.8 | 262.4 | 391.4 | 283.1
2334.4 | 2115.4 | -6.8 | 0 | 0 | 237 | 213 | 204.4 | 209.3 | 244.2 | 45.9 | 19 | 71.2 | 11.2 | 238.3 | 18.5 | 417.8 | 195.5 | 155.4 | 307.5 | 457.1 | 679.2 | 322.1 | 212.9 | 420.6 | 465.2 | 180.1 | 228.2 | 269 | 228.4 | 245 | 225.8 | 226.9 | 262.1 | 391 | 283
2335.4 | 2116.4 | -6.8 | 0 | 0 | 236.6 | 212.5 | 204.4 | 208.8 | 243.2 | 45.8 | 19 | 70.9 | 11.3 | 245.5 | 20.6 | 415.1 | 194.1 | 153.8 | 303.8 | 455 | 677.9 | 321.1 | 210.7 | 419.8 | 463 | 180.2 | 228.2 | 268.8 | 228.3 | 244.4 | 225.3 | 226.9 | 261.7 | 390.6 | 282.9
2336.4 | 2117.4 | -6.8 | 0 | 0 | 236.3 | 212 | 204.3 | 208.1 | 242.1 | 45.7 | 19 | 70.6 | 11.4 | 240.5 | 17.4 | 412.6 | 192.1 | 152.8 | 301.4 | 453.1 | 676.7 | 319.7 | 209 | 419.2 | 461 | 180.4 | 228.2 | 268.6 | 228.1 | 244 | 224.8 | 227 | 261.3 | 390.2 | 282.8
2337.4 | 2118.4 | -6.8 | 0 | 0 | 236.1 | 211.5 | 204 | 207.8 | 241.3 | 45.6 | 19 | 70.4 | 10.7 | 232.4 | 14.7 | 410.1 | 190.8 | 151.6 | 299.1 | 451.2 | 675.4 | 319.3 | 207.3 | 418.3 | 459.3 | 180.5 | 228.2 | 268.4 | 227.9 | 243.8 | 224.2 | 227 | 260.9 | 389.8 | 282.7
2338.4 | 2119.4 | -6.8 | 0 | 0 | 235.6 | 211.1 | 203.6 | 207.3 | 240.6 | 45.4 | 19 | 70.1 | 11.3 | 241.8 | 18.1 | 407.6 | 189.7 | 150.1 | 296.8 | 449.4 | 674.1 | 319.3 | 206.2 | 417.9 | 458.2 | 180.7 | 228.2 | 268.3 | 227.7 | 243.6 | 223.7 | 227.1 | 260.6 | 389.4 | 282.6
2339.4 | 2120.4 | -6.8 | 0 | 0 | 235.1 | 210.8 | 203.1 | 206.9 | 240.2 | 45.2 | 19 | 69.9 | 10.9 | 244.3 | 20.5 | 405.6 | 190.7 | 148.4 | 295.6 | 447.5 | 672.9 | 319.4 | 205.1 | 417.5 | 457.1 | 180.8 | 228.2 | 268.1 | 227.6 | 243.2 | 223.3 | 227.1 | 260.2 | 389.1 | 282.5
2340.4 | 2121.4 | -6.8 | 0 | 0 | 234.9 | 210.4 | 202.7 | 206.7 | 239.6 | 45 | 19 | 69.7 | 11.3 | 241 | 21.6 | 403.3 | 190.3 | 146.9 | 293.9 | 445.7 | 671.7 | 318.8 | 204.3 | 417.1 | 455.8 | 180.9 | 228.2 | 267.9 | 227.5 | 242.7 | 222.9 | 227.1 | 259.8 | 388.7 | 282.4
2341.4 | 2122.4 | -6.8 | 0 | 0 | 234.9 | 210 | 202.3 | 206.2 | 239.3 | 44.8 | 19 | 69.5 | 9.2 | 242 | 22.2 | 401.2 | 188.6 | 145.8 | 293 | 443.8 | 670.4 | 318.7 | 203.5 | 416.9 | 454.9 | 181 | 228.2 | 267.8 | 227.3 | 242.2 | 222.4 | 227.2 | 259.5 | 388.3 | 282.3
2342.4 | 2123.4 | -6.8 | 0 | 0 | 234.7 | 209.6 | 202.2 | 205.6 | 239 | 44.7 | 19 | 69.3 | 10.7 | 238.4 | 20.4 | 399.2 | 186.6 | 144.7 | 293.1 | 442 | 669.2 | 318.7 | 202.9 | 416 | 453.7 | 181.2 | 228.1 | 267.6 | 227.1 | 241.6 | 221.9 | 227.2 | 259.1 | 387.9 | 282.2
2343.4 | 2124.4 | -6.8 | 0 | 0 | 234.4 | 209.2 | 201.9 | 205.3 | 238.8 | 44.7 | 19 | 69.3 | 10.4 | 242.8 | 19.4 | 397.1 | 184.9 | 143.9 | 292.4 | 440.1 | 667.9 | 318.3 | 203.3 | 416.3 | 452.6 | 181.3 | 228.1 | 267.4 | 227 | 241.5 | 221.5 | 227.3 | 258.8 | 387.5 | 282.1
2344.4 | 2125.4 | -6.8 | 0 | 0 | 234.1 | 208.9 | 201.6 | 205.2 | 238.6 | 44.6 | 19 | 69.2 | 10.8 | 227.7 | 18.3 | 395 | 184.4 | 143.5 | 291.3 | 438.4 | 666.6 | 317.2 | 203.3 | 416.7 | 451.6 | 181.4 | 228.1 | 267.2 | 226.8 | 241.4 | 221 | 227.3 | 258.4 | 387.1 | 282
2345.4 | 2126.4 | -6.8 | 0 | 0 | 233.8 | 208.6 | 201.3 | 205.1 | 238 | 44.6 | 19 | 69 | 10.5 | 246.2 | 14.2 | 392.9 | 183.3 | 142.6 | 289.8 | 436.7 | 665.3 | 315.9 | 203.2 | 415.3 | 450.2 | 181.6 | 228.2 | 267.1 | 226.6 | 241.1 | 220.6 | 227.3 | 258.1 | 386.7 | 281.9
2346.4 | 2127.4 | -6.8 | 0 | 0 | 233.5 | 208.3 | 200.8 | 204.8 | 237.4 | 44.5 | 19 | 68.9 | 11 | 235.2 | 14.9 | 390.8 | 185.2 | 142 | 287.9 | 434.9 | 664 | 315.2 | 203.6 | 415.2 | 448.8 | 181.7 | 228.2 | 266.9 | 226.4 | 240.8 | 220.1 | 227.4 | 257.7 | 386.3 | 281.8
2347.4 | 2128.4 | -6.8 | 0 | 0 | 233.1 | 208.1 | 200.8 | 204.5 | 236.9 | 44.4 | 19 | 68.7 | 11.9 | 238.7 | 18.4 | 388.8 | 186.3 | 141.6 | 286.7 | 433.2 | 662.7 | 314.6 | 203.8 | 413.5 | 447.5 | 181.8 | 228.2 | 266.7 | 226.3 | 240.7 | 219.6 | 227.5 | 257.3 | 385.9 | 281.7
2348.4 | 2129.4 | -6.8 | 0 | 0 | 232.6 | 207.7 | 200.7 | 204.2 | 236.3 | 44.2 | 19.1 | 68.5 | 10.5 | 244.2 | 21.2 | 386.8 | 185.7 | 140.8 | 285.8 | 431.6 | 661.6 | 314.2 | 202.6 | 412 | 446.4 | 181.9 | 228.2 | 266.6 | 226.1 | 240.3 | 219.1 | 227.5 | 256.9 | 385.6 | 281.5
2349.4 | 2130.4 | -6.8 | 0 | 0 | 232.3 | 207.4 | 200.3 | 204 | 235.9 | 44 | 19.1 | 68.3 | 9.6 | 243.2 | 22.4 | 384.9 | 183.4 | 139.6 | 284.9 | 429.9 | 660.4 | 314 | 202 | 412.9 | 444.7 | 182.1 | 228.2 | 266.4 | 226 | 239.7 | 218.7 | 227.5 | 256.6 | 385.2 | 281.4
2350.4 | 2131.4 | -6.8 | 0 | 0 | 232 | 207 | 200.1 | 203.5 | 235.1 | 43.8 | 19.1 | 68.1 | 8.5 | 246.8 | 21.7 | 383 | 183.8 | 139.2 | 283 | 428.2 | 659.1 | 313.4 | 202.1 | 413.1 | 443.5 | 182.2 | 228.2 | 266.2 | 225.8 | 239.2 | 218.4 | 227.6 | 256.2 | 384.8 | 281.3
2351.4 | 2132.4 | -6.8 | 0 | 0 | 231.4 | 206.7 | 200 | 203 | 234.7 | 43.6 | 19.1 | 67.9 | 10.6 | 247.7 | 20.7 | 380.9 | 181.3 | 138.4 | 280.7 | 426.2 | 657.8 | 312.5 | 202 | 412.5 | 441.4 | 182.3 | 228.2 | 266.1 | 225.7 | 238.7 | 218 | 227.6 | 255.9 | 384.4 | 281.2
2352.4 | 2133.4 | -6.8 | 0 | 0 | 230.9 | 206.4 | 199.8 | 202.4 | 234.2 | 43.4 | 19.1 | 67.8 | 10.7 | 258.7 | 18.8 | 378.9 | 181.2 | 137.6 | 278.8 | 424.4 | 656.7 | 312.1 | 201.6 | 412.2 | 440.8 | 182.4 | 228.2 | 265.9 | 225.5 | 238.4 | 217.6 | 227.7 | 255.6 | 384 | 281.1
2353.4 | 2134.4 | -6.8 | 0 | 0 | 230.4 | 206.1 | 199.5 | 201.9 | 233.5 | 43.2 | 19.1 | 67.7 | 10.7 | 247.1 | 16.6 | 377.2 | 181.2 | 137 | 276.9 | 422.7 | 655.5 | 311.7 | 200.5 | 412 | 439.7 | 182.5 | 228.2 | 265.7 | 225.3 | 237.8 | 217.2 | 227.7 | 255.2 | 383.6 | 281
2354.4 | 2135.4 | -6.8 | 0 | 0 | 230 | 205.8 | 198.9 | 201.4 | 232.7 | 43 | 19.1 | 67.6 | 9.1 | 238.9 | 15.7 | 375.4 | 179.1 | 135.9 | 275.7 | 420.9 | 654.3 | 311 | 200.5 | 411.3 | 438.2 | 182.7 | 228.3 | 265.5 | 225.2 | 237.2 | 216.8 | 227.7 | 254.8 | 383.2 | 280.9
2355.4 | 2136.4 | -6.8 | 0 | 0 | 229.7 | 205.5 | 198.6 | 201.1 | 232.2 | 42.8 | 19.1 | 67.5 | 10.3 | 234.9 | 12.6 | 373.5 | 177.4 | 134.6 | 273 | 419.1 | 653.1 | 309.6 | 199.1 | 410.7 | 437.2 | 182.8 | 228.3 | 265.4 | 225 | 236.6 | 216.4 | 227.8 | 254.4 | 382.8 | 280.8
2356.4 | 2137.4 | -6.8 | 0 | 0 | 229.4 | 205.5 | 198.3 | 200.8 | 232 | 42.6 | 19.1 | 67.4 | 9.1 | 255.3 | 10.2 | 371.5 | 174.9 | 133.4 | 269.2 | 416.9 | 652 | 309 | 197.7 | 409 | 435.8 | 182.9 | 228.3 | 265.2 | 224.9 | 236.5 | 216 | 227.8 | 254.1 | 382.4 | 280.7
2357.4 | 2138.4 | -6.8 | 0 | 0 | 229.1 | 205.3 | 197.9 | 200.5 | 231.4 | 42.6 | 19.1 | 67.2 | 9.3 | 241.3 | 14.9 | 369.7 | 174 | 132.3 | 266.9 | 414.9 | 650.9 | 308.2 | 197.4 | 407.9 | 434.3 | 183 | 228.3 | 265.1 | 224.7 | 236.1 | 215.5 | 227.8 | 253.8 | 382.1 | 280.6
2358.4 | 2139.4 | -6.8 | 0 | 0 | 228.8 | 205 | 197.5 | 200.2 | 230.9 | 42.6 | 19.1 | 67.1 | 8.5 | 246.4 | 18.1 | 368 | 173.4 | 131 | 265.9 | 413.2 | 649.8 | 307.7 | 197.4 | 407.4 | 433.6 | 183.1 | 228.3 | 264.9 | 224.5 | 235.9 | 215.1 | 227.9 | 253.4 | 381.7 | 280.4
2359.4 | 2140.4 | -6.8 | 0 | 0 | 228.6 | 204.8 | 197.3 | 200.1 | 230.6 | 42.6 | 19.1 | 66.8 | 8.3 | 249.2 | 17.4 | 366.5 | 173.2 | 130.1 | 265 | 411.3 | 648.7 | 307 | 196.3 | 406.7 | 432.7 | 183.3 | 228.3 | 264.7 | 224.4 | 235.6 | 214.7 | 227.9 | 253.1 | 381.3 | 280.3
2360.4 | 2141.4 | -6.8 | 0 | 0 | 228.2 | 204.7 | 196.9 | 200.1 | 230.1 | 42.5 | 19.1 | 66.6 | 9.1 | 249.6 | 16.6 | 364.7 | 170.8 | 129.2 | 263.9 | 410 | 647.5 | 306.2 | 195.7 | 405.9 | 431.6 | 183.4 | 228.3 | 264.5 | 224.2 | 235.2 | 214.3 | 228 | 252.7 | 380.9 | 280.2
2361.4 | 2142.4 | -6.8 | 0 | 0 | 227.7 | 204.5 | 196.6 | 199.6 | 229.7 | 42.4 | 19.1 | 66.4 | 8.3 | 246.4 | 15.6 | 362.6 | 170 | 127.8 | 260.3 | 408.7 | 646.3 | 306.3 | 196.3 | 406.3 | 430.4 | 183.5 | 228.2 | 264.4 | 224 | 234.8 | 213.9 | 228 | 252.4 | 380.5 | 280.1
2362.4 | 2143.4 | -6.8 | 0 | 0 | 227.4 | 204.2 | 196.6 | 199.2 | 229.2 | 42.2 | 19.1 | 66.3 | 8.2 | 250.9 | 14.3 | 360.5 | 167.5 | 126.7 | 257.5 | 406.9 | 645.2 | 305.6 | 196.6 | 405 | 429.2 | 183.6 | 228.2 | 264.2 | 223.9 | 234.3 | 213.6 | 228 | 252 | 380.1 | 280
2363.4 | 2144.4 | -6.8 | 0 | 0 | 227.1 | 204 | 196.4 | 198.9 | 228.6 | 42.1 | 19.1 | 66.1 | 8.7 | 246.5 | 13 | 358.7 | 164.9 | 125.9 | 254.9 | 405.2 | 644.3 | 304.2 | 196.4 | 403.2 | 428.1 | 183.7 | 228.2 | 264 | 223.7 | 233.9 | 213.2 | 228.1 | 251.7 | 379.8 | 279.9
2364.4 | 2145.4 | -6.8 | 0 | 0 | 226.9 | 203.7 | 196.3 | 198.5 | 228.1 | 42.1 | 19.1 | 66 | 8.2 | 245.8 | 12.8 | 356.8 | 163.4 | 125 | 252.9 | 403.5 | 643.5 | 302.4 | 194.2 | 401.3 | 426.7 | 183.9 | 228.2 | 263.8 | 223.6 | 233.6 | 212.8 | 228.1 | 251.3 | 379.4 | 279.8
2365.4 | 2146.4 | -6.8 | 0 | 0 | 226.7 | 203.6 | 196.2 | 198.3 | 227.4 | 42 | 19.1 | 65.9 | 8.6 | 251.6 | 11.8 | 355.1 | 162.9 | 124 | 251.7 | 402 | 642.7 | 301.3 | 192.9 | 399.7 | 425.5 | 184 | 228.1 | 263.7 | 223.4 | 233.3 | 212.4 | 228.1 | 251 | 379 | 279.6
2366.4 | 2147.4 | -6.8 | 0 | 0 | 226.3 | 203.3 | 195.8 | 197.9 | 226.9 | 41.9 | 19.1 | 65.8 | 9.1 | 252.4 | 13.3 | 353.5 | 162.1 | 123.1 | 251.1 | 400.6 | 641.7 | 300.6 | 192.3 | 399.4 | 424.5 | 184.1 | 228.1 | 263.5 | 223.3 | 233 | 212 | 228.2 | 250.7 | 378.6 | 279.5
2367.4 | 2148.4 | -6.8 | 0 | 0 | 226.1 | 203 | 195.5 | 197.4 | 226.3 | 41.9 | 19.1 | 65.6 | 8.8 | 254.8 | 13.2 | 352.1 | 162.5 | 122 | 251.2 | 398.8 | 640.7 | 300 | 192.3 | 398.8 | 423.1 | 184.2 | 228.1 | 263.3 | 223.1 | 233 | 211.7 | 228.2 | 250.4 | 378.2 | 279.4
2368.4 | 2149.4 | -6.8 | 0 | 0 | 225.8 | 202.8 | 195.4 | 196.8 | 226.2 | 41.9 | 19.1 | 65.5 | 8 | 258.8 | 12.4 | 350.5 | 163.5 | 121 | 250.5 | 397.1 | 639.6 | 299.9 | 192.2 | 399.1 | 422.2 | 184.3 | 228.1 | 263.2 | 223 | 232.7 | 211.3 | 228.2 | 250.1 | 377.8 | 279.3
2369.4 | 2150.4 | -6.8 | 0 | 0 | 225.5 | 202.6 | 195.2 | 196.6 | 226.2 | 41.8 | 19.1 | 65.4 | 8.3 | 249.6 | 11.2 | 348.9 | 163.3 | 120.3 | 249.2 | 395.6 | 638.5 | 299.4 | 192.1 | 398 | 421.4 | 184.4 | 228 | 263 | 222.8 | 232.4 | 211 | 228.2 | 249.7 | 377.4 | 279.2
2370.4 | 2151.4 | -6.8 | 0 | 0 | 225.3 | 202.4 | 194.9 | 196.3 | 225.8 | 41.8 | 19.1 | 65.3 | 8.4 | 246.4 | 9.1 | 347.5 | 161.9 | 119.2 | 248.6 | 393.8 | 637.4 | 298.5 | 191.9 | 397.6 | 420.3 | 184.6 | 228 | 262.9 | 222.7 | 232.2 | 210.6 | 228.3 | 249.5 | 377.1 | 279.1
2371.4 | 2152.4 | -6.8 | 0 | 0 | 225.1 | 202.2 | 194.6 | 196.1 | 225.9 | 41.7 | 19.1 | 65 | 7.9 | 239 | 8.8 | 346.2 | 159.9 | 118.3 | 248.1 | 392.1 | 636.3 | 297.5 | 191.6 | 396.9 | 419.3 | 184.7 | 228 | 262.7 | 222.6 | 232.1 | 210.3 | 228.3 | 249.1 | 376.7 | 278.9
2372.4 | 2153.4 | -6.8 | 0 | 0 | 224.6 | 201.9 | 194.3 | 195.8 | 225.7 | 41.6 | 19.1 | 64.9 | 8.8 | 267.4 | 8 | 344.9 | 158.1 | 117.2 | 247.5 | 390.2 | 635.3 | 297.3 | 190.4 | 396.5 | 418.4 | 184.8 | 227.9 | 262.5 | 222.4 | 231.9 | 210 | 228.3 | 248.8 | 376.3 | 278.8
2373.4 | 2154.4 | -6.8 | 0 | 0 | 224.2 | 201.6 | 193.9 | 195.4 | 225.8 | 41.4 | 19.1 | 64.7 | 7.8 | 239.1 | 7.9 | 343.4 | 156.9 | 116.4 | 246.1 | 388.3 | 634.3 | 296.9 | 189.9 | 395.1 | 417.6 | 184.9 | 227.9 | 262.4 | 222.3 | 231.6 | 209.6 | 228.4 | 248.5 | 375.9 | 278.7
2374.4 | 2155.4 | -6.8 | 0 | 0 | 223.8 | 201.3 | 193.5 | 194.9 | 225.7 | 41.3 | 19.1 | 64.6 | 7.6 | 247 | 7.8 | 341.7 | 156.1 | 115.8 | 243.4 | 386.7 | 633.2 | 296.3 | 189.8 | 394.4 | 416.4 | 185 | 227.8 | 262.2 | 222.2 | 231.1 | 209.3 | 228.4 | 248.1 | 375.6 | 278.6
2375.4 | 2156.4 | -6.8 | 0 | 0 | 223.5 | 200.9 | 193.4 | 194.6 | 225.5 | 41.2 | 19.1 | 64.5 | 7.5 | 255.1 | 7.9 | 340 | 154.9 | 115.1 | 240.3 | 385.1 | 632.2 | 295.4 | 188.6 | 393.9 | 415.2 | 185.1 | 227.8 | 262.1 | 222.1 | 230.8 | 209 | 228.4 | 247.8 | 375.2 | 278.5
2376.4 | 2157.4 | -6.8 | 0 | 0 | 223.1 | 200.5 | 193.2 | 194.2 | 225.5 | 41.1 | 19.1 | 64.5 | 7.3 | 240.3 | 6.8 | 338.4 | 153.7 | 114.6 | 237.4 | 383.8 | 631.2 | 294.2 | 187 | 391.7 | 414.2 | 185.2 | 227.8 | 261.9 | 221.9 | 230.7 | 208.7 | 228.4 | 247.5 | 374.8 | 278.4
2377.4 | 2158.4 | -6.8 | 0 | 0 | 222.8 | 200.2 | 192.9 | 193.9 | 224.8 | 41.1 | 19.1 | 64.5 | 7.3 | 257.7 | 6.8 | 336.9 | 153.3 | 114.1 | 235.8 | 382.2 | 630.3 | 293.9 | 186.8 | 390.7 | 413.1 | 185.3 | 227.8 | 261.7 | 221.8 | 230.2 | 208.4 | 228.5 | 247.2 | 374.4 | 278.2
2378.4 | 2159.4 | -6.8 | 0 | 0 | 222.5 | 199.8 | 192.5 | 193.5 | 223.9 | 41 | 19.1 | 64.3 | 7.1 | 248.4 | 8.3 | 335.3 | 154.6 | 113.1 | 234.4 | 380.7 | 629.5 | 293.4 | 186.1 | 391.2 | 412.2 | 185.5 | 227.8 | 261.6 | 221.7 | 230 | 208.1 | 228.5 | 246.9 | 374 | 278.1
2379.4 | 2160.4 | -6.8 | 0 | 0 | 222.2 | 199.5 | 192.4 | 193.2 | 223.1 | 41 | 19.1 | 64.2 | 6.3 | 246.1 | 9.6 | 333.6 | 156.4 | 112.2 | 232.5 | 379.2 | 628.6 | 292.8 | 185.2 | 391.8 | 411.2 | 185.6 | 227.7 | 261.4 | 221.6 | 229.8 | 207.8 | 228.6 | 246.6 | 373.6 | 278
2380.4 | 2161.4 | -6.8 | 0 | 0 | 222.1 | 199.2 | 192.2 | 192.9 | 222.7 | 41 | 19.1 | 64.1 | 6.6 | 233.4 | 9.8 | 332.1 | 154.7 | 111.3 | 231.1 | 377.8 | 627.6 | 291.9 | 185.4 | 392.4 | 410.2 | 185.7 | 227.7 | 261.2 | 221.5 | 229.4 | 207.5 | 228.5 | 246.3 | 373.3 | 277.9
2381.4 | 2162.4 | -6.8 | 0 | 0 | 221.7 | 199 | 192 | 192.8 | 222.3 | 41 | 19.1 | 64 | 7.7 | 243.4 | 9 | 330.9 | 154 | 110.7 | 230.3 | 376.2 | 626.6 | 291.1 | 185 | 392.3 | 409.4 | 185.8 | 227.7 | 261.1 | 221.3 | 229 | 207.1 | 228.6 | 246 | 372.9 | 277.7
2382.4 | 2163.4 | -6.8 | 0 | 0 | 221.4 | 198.8 | 191.9 | 192.6 | 222 | 40.9 | 19.1 | 63.9 | 8.7 | 234.1 | 8.3 | 329.2 | 153.6 | 110.2 | 229.6 | 374.6 | 625.7 | 290.3 | 183.8 | 391.9 | 408.3 | 185.9 | 227.7 | 260.9 | 221.2 | 228.8 | 206.9 | 228.6 | 245.6 | 372.5 | 277.6
2383.4 | 2164.4 | -6.8 | 0 | 0 | 221 | 198.5 | 191.8 | 192.3 | 222.2 | 40.9 | 19.1 | 63.8 | 9.1 | 254.1 | 7.8 | 327.8 | 152.9 | 109.6 | 229.6 | 373.2 | 624.8 | 289.9 | 182.3 | 391 | 407.5 | 186 | 227.7 | 260.8 | 221.1 | 228.3 | 206.6 | 228.6 | 245.3 | 372.1 | 277.5
2384.4 | 2165.4 | -6.8 | 0 | 0 | 220.8 | 198.3 | 191.6 | 192 | 222 | 40.8 | 19.2 | 63.8 | 8.5 | 242.7 | 6.9 | 326.6 | 153.2 | 109 | 230 | 371.8 | 623.9 | 289.1 | 181.3 | 389.3 | 406.5 | 186.1 | 227.7 | 260.6 | 221 | 227.9 | 206.3 | 228.7 | 245 | 371.7 | 277.4
2385.4 | 2166.4 | -6.8 | 0 | 0 | 220.6 | 198 | 191.3 | 191.7 | 221.5 | 40.7 | 19.2 | 63.7 | 7.9 | 220.1 | 6.6 | 325.2 | 151.4 | 108.6 | 230.2 | 370.6 | 622.9 | 289.4 | 179.9 | 389.2 | 405.5 | 186.2 | 227.6 | 260.5 | 220.9 | 227.4 | 205.9 | 228.7 | 244.7 | 371.3 | 277.3
2386.4 | 2167.4 | -6.8 | 0 | 0 | 220.3 | 197.8 | 191.1 | 191.5 | 220.9 | 40.7 | 19.2 | 63.5 | 7.7 | 259.7 | 6.8 | 323.9 | 150.5 | 108.1 | 229.7 | 369.5 | 622 | 289.3 | 180.1 | 388.7 | 404.5 | 186.3 | 227.6 | 260.3 | 220.8 | 227.1 | 205.6 | 228.7 | 244.4 | 371 | 277.1
2387.4 | 2168.4 | -6.8 | 0 | 0 | 220.2 | 197.5 | 190.9 | 191.1 | 220.5 | 40.6 | 19.2 | 63.4 | 8.2 | 246.3 | 7.7 | 322.6 | 149.7 | 107.5 | 228.6 | 368.4 | 621.1 | 288.4 | 179.9 | 387.5 | 403.6 | 186.4 | 227.6 | 260.1 | 220.7 | 227 | 205.2 | 228.7 | 244.1 | 370.6 | 277
2388.4 | 2169.4 | -6.8 | 0 | 0 | 220.1 | 197.2 | 190.7 | 190.6 | 219.9 | 40.5 | 19.2 | 63.3 | 9.9 | 217.6 | 10.3 | 321.2 | 148.9 | 107.2 | 227 | 367.1 | 620.1 | 287.6 | 180.3 | 387.7 | 402.6 | 186.5 | 227.6 | 260 | 220.6 | 226.8 | 204.9 | 228.7 | 243.8 | 370.2 | 276.9
2389.4 | 2170.4 | -6.8 | 0 | 0 | 219.7 | 197 | 190.4 | 190.3 | 219.4 | 40.5 | 19.2 | 63.1 | 9.6 | 232.5 | 9.6 | 319.9 | 149.7 | 106.9 | 225.5 | 365.7 | 619.2 | 286.5 | 180.1 | 387.6 | 401.6 | 186.6 | 227.6 | 259.8 | 220.5 | 226.4 | 204.6 | 228.8 | 243.4 | 369.8 | 276.8
2390.4 | 2171.4 | -6.8 | 0 | 0 | 219.4 | 196.8 | 190.2 | 189.9 | 218.9 | 40.4 | 19.2 | 63 | 9.9 | 227.7 | 8.3 | 318.5 | 149.7 | 106.5 | 224 | 364.1 | 618.4 | 285.8 | 178.6 | 387 | 400.7 | 186.7 | 227.5 | 259.7 | 220.4 | 226.1 | 204.3 | 228.8 | 243.1 | 369.4 | 276.6
2391.4 | 2172.4 | -6.8 | 0 | 0 | 219.3 | 196.6 | 189.9 | 189.6 | 218.4 | 40.3 | 19.2 | 62.9 | 9 | 234.9 | 7.8 | 317 | 148.8 | 106.2 | 222.7 | 362.6 | 617.6 | 285.4 | 177.6 | 385.9 | 399.7 | 186.9 | 227.5 | 259.5 | 220.3 | 225.8 | 203.9 | 228.8 | 242.9 | 369 | 276.5
2392.4 | 2173.4 | -6.8 | 0 | 0 | 219.1 | 196.3 | 189.6 | 189.5 | 217.9 | 40.2 | 19.2 | 62.8 | 8.6 | 239.2 | 7.5 | 315.4 | 146.6 | 105.1 | 219.8 | 361.2 | 616.8 | 284.7 | 177 | 385.5 | 399 | 187 | 227.5 | 259.3 | 220.2 | 225.2 | 203.6 | 228.8 | 242.5 | 368.6 | 276.4
2393.4 | 2174.4 | -6.8 | 0 | 0 | 218.9 | 196.1 | 189.3 | 189.3 | 217.5 | 40.1 | 19.2 | 62.7 | 6.9 | 232.1 | 8.5 | 313.9 | 145.2 | 104.5 | 216.5 | 359.6 | 616 | 283.8 | 175.5 | 382.8 | 398 | 187.1 | 227.5 | 259.2 | 220.1 | 224.9 | 203.4 | 228.9 | 242.2 | 368.3 | 276.3
2394.4 | 2175.4 | -6.8 | 0 | 0 | 218.7 | 195.9 | 189.1 | 189.1 | 217.1 | 40.1 | 19.2 | 62.6 | 7.7 | 251.5 | 10.2 | 312.5 | 144.7 | 103.9 | 213.2 | 357.6 | 615.4 | 282.8 | 173.9 | 379.5 | 397.4 | 187.2 | 227.5 | 259.1 | 220 | 224.4 | 203.1 | 228.9 | 242 | 367.9 | 276.1
2395.4 | 2176.4 | -6.8 | 0 | 0 | 218.4 | 195.7 | 189 | 188.9 | 216.8 | 40 | 19.2 | 62.5 | 8.2 | 247.5 | 8.3 | 311.2 | 143.4 | 103.4 | 210 | 355.9 | 614.8 | 281.2 | 172.4 | 376.9 | 396 | 187.3 | 227.4 | 258.9 | 219.9 | 223.9 | 202.9 | 228.9 | 241.6 | 367.5 | 276
2396.4 | 2177.4 | -6.8 | 0 | 0 | 218 | 195.4 | 188.9 | 188.9 | 216.3 | 40 | 19.2 | 62.5 | 8.7 | 224 | 7.8 | 309.9 | 142.4 | 102.9 | 207.9 | 354.3 | 614.2 | 279.7 | 171.7 | 375.5 | 394.6 | 187.4 | 227.4 | 258.7 | 219.9 | 223.7 | 202.6 | 228.9 | 241.3 | 367.2 | 275.9
2397.4 | 2178.4 | -6.8 | 0 | 0 | 217.7 | 195.2 | 188.7 | 188.7 | 215.9 | 40 | 19.2 | 62.4 | 9.4 | 232.9 | 8.7 | 308.5 | 141.3 | 102.5 | 206.3 | 352.8 | 613.7 | 278.9 | 170.3 | 374.9 | 393.2 | 187.5 | 227.4 | 258.6 | 219.8 | 223.6 | 202.4 | 228.9 | 241 | 366.8 | 275.8
2398.4 | 2179.4 | -6.8 | 0 | 0 | 217.5 | 194.8 | 188.3 | 188.4 | 215.5 | 40 | 19.2 | 62.3 | 8.8 | 240.4 | 8.3 | 306.9 | 140.5 | 101.8 | 204.8 | 351.4 | 613.2 | 278.3 | 169.4 | 375.3 | 392.3 | 187.6 | 227.4 | 258.4 | 219.7 | 223.4 | 202.1 | 229 | 240.7 | 366.4 | 275.7
2399.4 | 2180.4 | -6.8 | 0 | 0 | 217.2 | 194.5 | 187.9 | 187.9 | 215.3 | 39.9 | 19.2 | 62.2 | 8.6 | 240.7 | 8.3 | 305.1 | 139.8 | 101 | 202.8 | 350.1 | 612.4 | 278.6 | 169.6 | 374.6 | 391.1 | 187.7 | 227.3 | 258.2 | 219.6 | 223.4 | 201.9 | 229 | 240.4 | 366.1 | 275.5
2400.4 | 2181.4 | -6.8 | 0 | 0 | 216.9 | 194.1 | 187.7 | 187.5 | 215.1 | 39.9 | 19.2 | 62.1 | 8.4 | 241 | 9.6 | 303.8 | 139.1 | 100.5 | 200.7 | 348.8 | 611.6 | 278.5 | 169.5 | 373.8 | 390.5 | 187.8 | 227.3 | 258.1 | 219.5 | 223.3 | 201.6 | 229 | 240.1 | 365.7 | 275.4
2401.4 | 2182.4 | -6.8 | 0 | 0 | 216.5 | 193.8 | 187.5 | 187.3 | 214.6 | 39.8 | 19.2 | 61.9 | 7.2 | 217.8 | 11.1 | 302.5 | 137.9 | 99.5 | 199 | 347.7 | 610.8 | 278.3 | 169.2 | 371.4 | 389.8 | 187.9 | 227.3 | 257.9 | 219.5 | 223.1 | 201.3 | 229 | 239.8 | 365.3 | 275.3
2402.4 | 2183.4 | -6.8 | 0 | 0 | 216.4 | 193.7 | 187.3 | 187.2 | 214.1 | 39.7 | 19.2 | 61.7 | 8.1 | 245 | 9.8 | 301.3 | 138.2 | 99 | 198.7 | 346.5 | 609.9 | 277.6 | 168.7 | 369.7 | 389.1 | 188 | 227.3 | 257.8 | 219.4 | 222.7 | 201.1 | 229 | 239.5 | 365 | 275.1
2403.4 | 2184.4 | -6.8 | 0 | 0 | 216.2 | 193.6 | 187.2 | 187.1 | 213.9 | 39.6 | 19.2 | 61.6 | 9.4 | 240.8 | 9.6 | 300.1 | 137.7 | 98.5 | 198.4 | 345.4 | 609.1 | 277 | 168.9 | 370.8 | 388.3 | 188.1 | 227.2 | 257.7 | 219.3 | 222.3 | 200.8 | 229 | 239.2 | 364.6 | 275
2404.4 | 2185.4 | -6.8 | 0 | 0 | 215.9 | 193.4 | 187.1 | 186.8 | 213.6 | 39.6 | 19.2 | 61.6 | 8.6 | 227.2 | 10.2 | 298.9 | 137.5 | 98.2 | 198.2 | 344.6 | 608.2 | 277.1 | 169.1 | 372.5 | 387.5 | 188.2 | 227.2 | 257.5 | 219.3 | 222 | 200.6 | 229.1 | 238.9 | 364.2 | 274.9
2405.4 | 2186.4 | -6.8 | 0 | 0 | 215.6 | 193.1 | 187 | 186.5 | 213.4 | 39.4 | 19.2 | 61.6 | 7.6 | 247.7 | 11.9 | 297.7 | 137 | 97.9 | 197.7 | 343.5 | 607.4 | 277.2 | 169.5 | 373.8 | 386.8 | 188.3 | 227.2 | 257.4 | 219.2 | 221.7 | 200.3 | 229.1 | 238.7 | 363.9 | 274.8
2406.4 | 2187.4 | -6.8 | 0 | 0 | 215.3 | 192.8 | 186.5 | 186.2 | 213.4 | 39.3 | 19.2 | 61.5 | 6.7 | 246.5 | 12.7 | 296.6 | 136.6 | 97.7 | 197.7 | 342.3 | 606.5 | 276.4 | 169.7 | 374 | 386.2 | 188.4 | 227.1 | 257.2 | 219.1 | 221.3 | 200 | 229.1 | 238.4 | 363.5 | 274.6
2407.4 | 2188.4 | -6.8 | 0 | 0 | 215.1 | 192.5 | 186.2 | 185.9 | 212.9 | 39.3 | 19.2 | 61.4 | 7 | 240.9 | 12.2 | 295.3 | 136.3 | 96.9 | 197.4 | 341.1 | 605.6 | 275.8 | 170.5 | 374 | 385.6 | 188.5 | 227.1 | 257 | 219 | 221.2 | 199.7 | 229.1 | 238.1 | 363.1 | 274.5
2408.4 | 2189.4 | -6.8 | 0 | 0 | 214.9 | 192.3 | 186 | 185.6 | 212.7 | 39.2 | 19.2 | 61.4 | 7.5 | 233.4 | 15.4 | 293.9 | 135.3 | 96.2 | 195.9 | 339.8 | 604.8 | 275.7 | 170.5 | 374 | 384.7 | 188.6 | 227.1 | 256.9 | 219 | 220.6 | 199.4 | 229.1 | 237.8 | 362.7 | 274.4
2409.4 | 2190.4 | -6.8 | 0 | 0 | 214.8 | 192.1 | 185.8 | 185.3 | 212.3 | 39.1 | 19.3 | 61.3 | 7.7 | 236.7 | 14.5 | 292.6 | 134.8 | 95.6 | 194.1 | 338.6 | 604 | 275.5 | 170.7 | 374.3 | 384 | 188.7 | 227 | 256.7 | 218.9 | 220.2 | 199.2 | 229.2 | 237.4 | 362.4 | 274.3
2410.4 | 2191.4 | -6.8 | 0 | 0 | 214.3 | 192 | 185.8 | 185.2 | 211.8 | 39 | 19.3 | 61.2 | 8.2 | 228.9 | 13.3 | 291.4 | 134.9 | 95.2 | 192.5 | 337.3 | 603.2 | 274.9 | 171.2 | 373.6 | 383.4 | 188.8 | 227 | 256.6 | 218.8 | 220.1 | 198.9 | 229.2 | 237.2 | 362 | 274.1
2411.4 | 2192.4 | -6.8 | 0 | 0 | 214.1 | 191.9 | 185.7 | 185.1 | 211.4 | 38.9 | 19.2 | 61.1 | 8.2 | 235 | 13.6 | 290.3 | 133.5 | 94.4 | 191 | 336 | 602.5 | 275.1 | 171.6 | 372.3 | 382.5 | 188.9 | 226.9 | 256.4 | 218.8 | 219.6 | 198.6 | 229.2 | 236.8 | 361.6 | 274
2412.4 | 2193.4 | -6.8 | 0 | 0 | 213.9 | 191.8 | 185.6 | 185 | 211.2 | 38.9 | 19.2 | 61 | 7.6 | 229.1 | 13.7 | 289 | 132.3 | 94 | 188.8 | 334.9 | 601.8 | 275.3 | 170.9 | 372.2 | 381.7 | 189 | 226.9 | 256.3 | 218.7 | 219.3 | 198.4 | 229.2 | 236.6 | 361.3 | 273.9
2413.4 | 2194.4 | -6.8 | 0 | 0 | 213.8 | 191.7 | 185.4 | 184.7 | 210.9 | 38.9 | 19.2 | 60.9 | 6.6 | 231.4 | 13 | 287.8 | 131.2 | 93.6 | 187.4 | 333.8 | 601.1 | 274.5 | 170.4 | 371.3 | 380.9 | 189.1 | 226.9 | 256.1 | 218.6 | 218.9 | 198.2 | 229.2 | 236.3 | 360.9 | 273.8
2414.4 | 2195.4 | -6.8 | 0 | 0 | 213.5 | 191.6 | 185.3 | 184.5 | 210.5 | 38.8 | 19.3 | 60.8 | 7.2 | 246.1 | 11.1 | 286.6 | 130.1 | 93.1 | 186.1 | 332.4 | 600.4 | 274 | 169.9 | 369.5 | 379.9 | 189.2 | 226.9 | 255.9 | 218.6 | 218.8 | 198 | 229.2 | 236 | 360.6 | 273.6
2415.4 | 2196.4 | -6.8 | 0 | 0 | 213.2 | 191.5 | 185.2 | 184.3 | 210.1 | 38.8 | 19.3 | 60.8 | 7.4 | 246.3 | 8.8 | 285.4 | 129.4 | 93 | 184.4 | 331.2 | 599.7 | 273.8 | 169 | 368.8 | 379.1 | 189.3 | 226.8 | 255.8 | 218.5 | 218.5 | 197.7 | 229.2 | 235.8 | 360.2 | 273.5
2416.4 | 2197.4 | -6.8 | 0 | 0 | 213.1 | 191.5 | 185.1 | 184.2 | 209.9 | 38.8 | 19.3 | 60.7 | 7.4 | 247.6 | 9.2 | 284.1 | 128.8 | 92.6 | 182.8 | 329.9 | 599 | 273.3 | 167.8 | 368.2 | 378.3 | 189.4 | 226.8 | 255.7 | 218.5 | 218.3 | 197.5 | 229.2 | 235.5 | 359.8 | 273.4
2417.4 | 2198.4 | -6.8 | 0 | 0 | 212.7 | 191.4 | 184.9 | 184 | 209.8 | 38.8 | 19.3 | 60.6 | 7.8 | 249.4 | 9.9 | 283 | 128.9 | 92.3 | 181.8 | 328.7 | 598.3 | 273.4 | 166.5 | 369 | 377.7 | 189.5 | 226.8 | 255.5 | 218.4 | 217.9 | 197.2 | 229.3 | 235.2 | 359.5 | 273.3
2418.4 | 2199.4 | -6.8 | 0 | 0 | 212.5 | 191.2 | 184.6 | 183.8 | 210 | 38.8 | 19.3 | 60.5 | 8 | 234.2 | 9.5 | 281.8 | 127.7 | 91.7 | 180.7 | 327.6 | 597.5 | 273.3 | 165.3 | 369.3 | 377.2 | 189.6 | 226.8 | 255.4 | 218.4 | 217.6 | 197 | 229.3 | 234.9 | 359.1 | 273.1
2419.4 | 2200.4 | -6.8 | 0 | 0 | 212.4 | 190.9 | 184.4 | 183.7 | 209.7 | 38.8 | 19.3 | 60.5 | 8 | 234.9 | 9.2 | 280.6 | 127.1 | 91.3 | 179.9 | 326.4 | 596.8 | 273.2 | 165.1 | 368.1 | 376.5 | 189.7 | 226.8 | 255.2 | 218.3 | 217.2 | 196.8 | 229.3 | 234.6 | 358.7 | 273
2420.4 | 2201.4 | -6.8 | 0 | 0 | 212.2 | 190.7 | 184.3 | 183.5 | 209.3 | 38.8 | 19.3 | 60.4 | 8.8 | 241.3 | 13.1 | 279.5 | 126.3 | 91.1 | 179.6 | 325.2 | 596.1 | 273 | 164.5 | 367 | 375.9 | 189.8 | 226.7 | 255 | 218.3 | 217.2 | 196.6 | 229.3 | 234.4 | 358.4 | 272.9
2421.4 | 2202.4 | -6.8 | 0 | 0 | 212.1 | 190.5 | 184.3 | 183.3 | 209.1 | 38.8 | 19.3 | 60.3 | 8.8 | 243.6 | 15.9 | 278.3 | 125.8 | 90.6 | 179.4 | 324.1 | 595.4 | 273.2 | 164.1 | 367.6 | 375.2 | 189.8 | 226.7 | 254.9 | 218.2 | 217 | 196.3 | 229.3 | 234.1 | 358 | 272.7
2422.4 | 2203.4 | -6.8 | 0 | 0 | 212 | 190.2 | 184.3 | 183 | 208.7 | 38.8 | 19.3 | 60.2 | 7.8 | 243.8 | 16.8 | 277.2 | 125 | 90.5 | 178.7 | 323.2 | 594.7 | 272.8 | 164.1 | 367.6 | 374.2 | 189.9 | 226.7 | 254.7 | 218.2 | 216.8 | 196.1 | 229.3 | 233.8 | 357.7 | 272.6
2423.4 | 2204.4 | -6.8 | 0 | 0 | 211.9 | 190 | 184.1 | 182.6 | 208.7 | 38.8 | 19.3 | 60.1 | 8.8 | 235.2 | 17.6 | 276.1 | 124 | 90.2 | 177.7 | 322.2 | 593.9 | 271.8 | 163.4 | 367.7 | 373.3 | 190 | 226.6 | 254.6 | 218.1 | 216.7 | 195.8 | 229.4 | 233.6 | 357.3 | 272.5
2424.4 | 2205.4 | -6.8 | 0 | 0 | 211.6 | 189.8 | 183.9 | 182.5 | 208.4 | 38.8 | 19.3 | 60 | 9.4 | 241.2 | 17.1 | 275 | 124.7 | 89.8 | 176.8 | 321 | 593.1 | 271.3 | 163.1 | 366.6 | 372.7 | 190.1 | 226.6 | 254.4 | 218.1 | 216.3 | 195.5 | 229.4 | 233.3 | 356.9 | 272.4
2425.4 | 2206.4 | -6.8 | 0 | 0 | 211.4 | 189.6 | 183.8 | 182.3 | 208 | 38.7 | 19.3 | 59.9 | 10.4 | 242 | 17.1 | 274.1 | 123.6 | 89.4 | 176.1 | 320 | 592.5 | 270.8 | 162.4 | 364.3 | 372 | 190.2 | 226.6 | 254.3 | 218 | 215.9 | 195.3 | 229.4 | 233.1 | 356.5 | 272.2
2426.4 | 2207.4 | -6.8 | 0 | 0 | 211.2 | 189.4 | 183.5 | 182.3 | 207.6 | 38.6 | 19.3 | 59.8 | 10.8 | 240.7 | 16.7 | 273.1 | 121.8 | 89 | 175.6 | 318.6 | 592 | 270.2 | 161.5 | 363.8 | 371.2 | 190.3 | 226.6 | 254.2 | 218 | 215.8 | 195.1 | 229.4 | 232.8 | 356.2 | 272.1
2427.4 | 2208.4 | -6.8 | 0 | 0 | 210.9 | 189.2 | 183.2 | 182.1 | 207.2 | 38.5 | 19.3 | 59.7 | 10.3 | 240.5 | 16.5 | 271.7 | 120.9 | 88.6 | 175 | 317.1 | 591.4 | 270 | 161.7 | 363.9 | 370.3 | 190.4 | 226.6 | 254 | 217.9 | 215.3 | 194.9 | 229.4 | 232.5 | 355.8 | 272
2428.4 | 2209.4 | -6.8 | 0 | 0 | 210.5 | 189 | 183 | 182 | 206.7 | 38.5 | 19.3 | 59.6 | 10.1 | 242.7 | 18.4 | 270.4 | 119.8 | 88.3 | 173 | 316 | 590.8 | 269.4 | 161.4 | 363 | 369.4 | 190.5 | 226.5 | 253.9 | 217.9 | 214.8 | 194.6 | 229.4 | 232.2 | 355.4 | 271.8
2429.4 | 2210.4 | -6.8 | 0 | 0 | 210.2 | 188.8 | 182.9 | 181.7 | 206.3 | 38.4 | 19.3 | 59.4 | 10.1 | 251.8 | 20.9 | 269.2 | 119.2 | 87.5 | 171.4 | 314.7 | 590.3 | 268.4 | 160.2 | 363.1 | 368.8 | 190.6 | 226.5 | 253.7 | 217.8 | 214.7 | 194.4 | 229.4 | 231.9 | 355.1 | 271.7
2430.4 | 2211.4 | -6.8 | 0 | 0 | 210.1 | 188.7 | 182.6 | 181.3 | 206 | 38.4 | 19.3 | 59.3 | 9.7 | 251.1 | 18 | 268.2 | 118.5 | 87.1 | 170.7 | 313.6 | 589.7 | 267.4 | 160.1 | 361.9 | 368 | 190.7 | 226.5 | 253.6 | 217.8 | 214.5 | 194.1 | 229.4 | 231.8 | 354.7 | 271.6
2431.4 | 2212.4 | -6.8 | 0 | 0 | 209.8 | 188.5 | 182.3 | 181.1 | 205.6 | 38.4 | 19.3 | 59.2 | 9.7 | 251.8 | 14.7 | 267 | 117.7 | 86.6 | 169.2 | 312.5 | 589.1 | 266.9 | 159.6 | 358.4 | 367.4 | 190.8 | 226.4 | 253.4 | 217.7 | 214.3 | 193.9 | 229.4 | 231.5 | 354.3 | 271.4
2432.4 | 2213.4 | -6.8 | 0 | 0 | 209.7 | 188.3 | 182.1 | 180.7 | 205.4 | 38.4 | 19.3 | 59.1 | 9.5 | 241.2 | 13.9 | 265.9 | 117.3 | 86.1 | 168.1 | 311.4 | 588.5 | 266.6 | 158.8 | 357.7 | 366.7 | 190.9 | 226.4 | 253.3 | 217.7 | 214.1 | 193.7 | 229.4 | 231.2 | 354 | 271.3
2433.4 | 2214.4 | -6.8 | 0 | 0 | 209.5 | 188 | 181.9 | 180.3 | 205 | 38.4 | 19.3 | 59 | 8.8 | 252.2 | 15.4 | 264.8 | 116.9 | 85.8 | 167.1 | 310.2 | 588 | 266.9 | 157.7 | 357.5 | 365.8 | 191 | 226.4 | 253.1 | 217.7 | 214 | 193.5 | 229.4 | 230.9 | 353.6 | 271.2
2434.4 | 2215.4 | -6.8 | 0 | 0 | 209.3 | 187.9 | 181.7 | 179.9 | 204.7 | 38.4 | 19.3 | 58.8 | 9.5 | 253.4 | 17.5 | 263.6 | 116 | 85.4 | 165.2 | 309.1 | 587.4 | 267 | 156.7 | 357.5 | 364.9 | 191 | 226.3 | 253 | 217.6 | 213.9 | 193.2 | 229.5 | 230.7 | 353.2 | 271.1
2435.4 | 2216.4 | -6.8 | 0 | 0 | 208.9 | 187.7 | 181.5 | 179.6 | 204.4 | 38.4 | 19.3 | 58.7 | 9.4 | 253 | 18.2 | 262.6 | 115.4 | 85.1 | 164 | 308 | 586.9 | 266.1 | 155 | 356.3 | 363.5 | 191.1 | 226.3 | 252.8 | 217.6 | 213.7 | 193 | 229.5 | 230.4 | 352.9 | 270.9
2436.4 | 2217.4 | -6.8 | 0 | 0 | 208.5 | 187.6 | 181.3 | 179.4 | 204.1 | 38.3 | 19.3 | 58.6 | 8.9 | 253.7 | 18 | 261.5 | 114.8 | 84.8 | 162.2 | 306.7 | 586.7 | 264.1 | 153.5 | 355.1 | 362.1 | 191.2 | 226.3 | 252.7 | 217.5 | 213.4 | 192.8 | 229.5 | 230.2 | 352.5 | 270.8
2437.4 | 2218.4 | -6.8 | 0 | 0 | 208.2 | 187.5 | 181.2 | 179.3 | 203.7 | 38.2 | 19.3 | 58.5 | 8.8 | 247.9 | 18.4 | 260.5 | 113.7 | 84.5 | 160.4 | 305.3 | 586.4 | 262.2 | 151.9 | 354 | 361.4 | 191.3 | 226.3 | 252.5 | 217.5 | 213.3 | 192.5 | 229.5 | 229.8 | 352.2 | 270.7
2438.4 | 2219.4 | -6.8 | 0 | 0 | 208 | 187.3 | 181 | 179.1 | 203.4 | 38.1 | 19.3 | 58.4 | 10 | 253.4 | 16.9 | 259.5 | 113 | 84 | 159.2 | 304 | 586.3 | 259.7 | 150.4 | 353.2 | 360.5 | 191.4 | 226.2 | 252.4 | 217.4 | 213.1 | 192.2 | 229.5 | 229.6 | 351.8 | 270.5
2439.4 | 2220.4 | -6.8 | 0 | 0 | 207.9 | 187.1 | 180.8 | 179 | 203.2 | 38 | 19.4 | 58.3 | 10.2 | 262.1 | 15.2 | 258.5 | 111.6 | 83.3 | 157.8 | 302.6 | 586.4 | 257.7 | 149 | 351.8 | 359.6 | 191.5 | 226.2 | 252.2 | 217.4 | 213 | 192 | 229.5 | 229.4 | 351.4 | 270.4
2440.4 | 2221.4 | -6.8 | 0 | 0 | 207.7 | 187 | 180.7 | 178.9 | 202.9 | 37.9 | 19.4 | 58.2 | 10.8 | 261.9 | 12.2 | 257.4 | 110.4 | 82.8 | 156.4 | 301.4 | 586.5 | 256.6 | 148.7 | 352.4 | 358 | 191.6 | 226.2 | 252.1 | 217.3 | 212.7 | 191.7 | 229.5 | 229.1 | 351 | 270.3
2441.4 | 2222.4 | -6.8 | 0 | 0 | 207.5 | 186.8 | 180.5 | 178.7 | 202.5 | 37.8 | 19.4 | 58.2 | 10.4 | 244.2 | 13.1 | 256.3 | 109.6 | 82.7 | 155.5 | 300.3 | 586.3 | 256.3 | 149.2 | 352.1 | 356.7 | 191.7 | 226.1 | 252 | 217.3 | 212.3 | 191.5 | 229.5 | 228.9 | 350.7 | 270.1
2442.4 | 2223.4 | -6.8 | 0 | 0 | 207.4 | 186.6 | 180.4 | 178.4 | 202.3 | 37.8 | 19.4 | 58.1 | 10.5 | 249.1 | 13.5 | 255.4 | 108.9 | 81.9 | 156.1 | 299 | 585.7 | 256.2 | 149 | 352.1 | 355.8 | 191.7 | 226.1 | 251.8 | 217.3 | 212 | 191.4 | 229.5 | 228.6 | 350.3 | 270
2443.4 | 2224.4 | -6.7 | 0 | 0 | 207.2 | 186.5 | 180.3 | 178.2 | 202.1 | 37.8 | 19.4 | 58 | 10.4 | 240.2 | 15.1 | 254.5 | 108.9 | 81.9 | 156.6 | 298.1 | 585 | 256.3 | 148.8 | 351.6 | 355.3 | 191.8 | 226.1 | 251.7 | 217.2 | 211.8 | 191.1 | 229.5 | 228.3 | 350 | 269.9
2444.4 | 2225.4 | -6.7 | 0 | 0 | 207 | 186.3 | 180.1 | 178 | 202 | 37.8 | 19.4 | 57.8 | 10.8 | 251.8 | 14.3 | 253.5 | 107.8 | 81.7 | 156.9 | 297.1 | 584.2 | 256.2 | 149.2 | 351.3 | 355.1 | 191.9 | 226 | 251.5 | 217.2 | 211.7 | 190.9 | 229.5 | 228.1 | 349.6 | 269.7
2445.4 | 2226.4 | -6.7 | 0 | 0 | 206.7 | 186.2 | 179.8 | 177.8 | 201.7 | 37.7 | 19.4 | 57.8 | 9.8 | 251.2 | 11.3 | 252.5 | 107.8 | 81.1 | 156.4 | 296.1 | 583.6 | 255.9 | 149.6 | 351.2 | 354.7 | 192 | 226 | 251.4 | 217.2 | 211.6 | 190.7 | 229.6 | 227.8 | 349.3 | 269.6
2446.4 | 2227.4 | -6.7 | 0 | 0 | 206.7 | 186 | 179.8 | 177.7 | 201.4 | 37.7 | 19.4 | 57.7 | 9.6 | 246.7 | 10.9 | 251.6 | 107.2 | 80.4 | 155.5 | 295 | 582.8 | 255.6 | 150 | 352 | 354.3 | 192.1 | 226 | 251.2 | 217.1 | 211.3 | 190.6 | 229.6 | 227.6 | 348.9 | 269.5
2447.4 | 2228.4 | -6.7 | 0 | 0 | 206.5 | 185.9 | 179.7 | 177.4 | 201.3 | 37.6 | 19.4 | 57.5 | 10.1 | 235.5 | 11.7 | 250.7 | 106 | 80.1 | 155 | 294 | 582.1 | 255.3 | 150.1 | 351.2 | 354 | 192.2 | 225.9 | 251.1 | 217.1 | 211.1 | 190.4 | 229.6 | 227.3 | 348.6 | 269.3
2448.4 | 2229.4 | -6.7 | 0 | 0 | 206.4 | 185.7 | 179.6 | 177.1 | 201 | 37.5 | 19.4 | 57.4 | 10.6 | 244.7 | 17.7 | 249.9 | 105.5 | 79.8 | 154.5 | 293 | 581.4 | 255.1 | 150.2 | 350.8 | 353.5 | 192.3 | 225.9 | 250.9 | 217 | 211.1 | 190.2 | 229.6 | 227.1 | 348.2 | 269.2
2449.4 | 2230.4 | -6.7 | 0 | 0 | 206.2 | 185.6 | 179.4 | 176.8 | 200.8 | 37.5 | 19.4 | 57.4 | 10.9 | 246.6 | 20.3 | 249 | 104.9 | 79.4 | 154.3 | 292 | 580.9 | 254.8 | 149.6 | 348.6 | 353 | 192.3 | 225.9 | 250.8 | 217 | 210.6 | 189.9 | 229.6 | 226.8 | 347.9 | 269.1
2450.4 | 2231.4 | -6.7 | 0 | 0 | 206 | 185.4 | 179.1 | 176.4 | 200.8 | 37.4 | 19.4 | 57.2 | 9.2 | 246.3 | 17.5 | 248.2 | 103.9 | 79.3 | 154.7 | 290.9 | 580.4 | 254.4 | 149.3 | 348.6 | 352.3 | 192.4 | 225.8 | 250.6 | 217 | 210.4 | 189.7 | 229.6 | 226.6 | 347.5 | 268.9
2451.4 | 2232.4 | -6.8 | 0 | 0 | 205.9 | 185.2 | 178.9 | 176.3 | 200.5 | 37.3 | 19.4 | 57.1 | 9.6 | 255 | 15 | 247.3 | 103 | 79.2 | 154.8 | 289.9 | 579.8 | 254.1 | 148.6 | 348.7 | 351.6 | 192.5 | 225.8 | 250.5 | 216.9 | 210.2 | 189.5 | 229.6 | 226.3 | 347.2 | 268.8
2452.4 | 2233.4 | -6.8 | 0 | 0 | 205.9 | 185 | 178.7 | 176.1 | 200.4 | 37.3 | 19.4 | 57 | 10.2 | 258.2 | 13.2 | 246.1 | 101.7 | 79.1 | 153.8 | 289 | 579.1 | 253.7 | 148.2 | 348.1 | 351.1 | 192.6 | 225.8 | 250.3 | 216.9 | 209.9 | 189.2 | 229.6 | 226.1 | 346.8 | 268.7
2453.4 | 2234.4 | -6.8 | 0 | 0 | 205.9 | 184.8 | 178.4 | 175.8 | 200.1 | 37.2 | 19.4 | 56.9 | 9.7 | 223.2 | 10.4 | 245 | 100.9 | 78.6 | 152.9 | 288 | 578.5 | 253.2 | 147.3 | 348.4 | 350.5 | 192.7 | 225.7 | 250.2 | 216.9 | 209.6 | 189 | 229.6 | 225.8 | 346.5 | 268.5
2454.4 | 2235.4 | -6.8 | 0 | 0 | 205.8 | 184.6 | 178.2 | 175.6 | 199.9 | 37.1 | 19.4 | 56.8 | 9.4 | 248.9 | 12.7 | 244.1 | 101.2 | 77.9 | 152.7 | 287.1 | 577.9 | 253 | 146.6 | 346.8 | 349.7 | 192.8 | 225.7 | 250.1 | 216.9 | 209.3 | 188.8 | 229.6 | 225.6 | 346.1 | 268.4
2455.4 | 2236.4 | -6.8 | 0 | 0 | 205.8 | 184.4 | 178 | 175.5 | 199.9 | 37 | 19.4 | 56.7 | 9.2 | 249.8 | 14.7 | 243.2 | 100.7 | 77.7 | 152.7 | 286.2 | 577.3 | 253.1 | 146.3 | 345.8 | 348.7 | 192.9 | 225.6 | 249.9 | 216.8 | 209 | 188.6 | 229.6 | 225.3 | 345.8 | 268.3
2456.4 | 2237.4 | -6.8 | 0 | 0 | 205.6 | 184.3 | 177.9 | 175.2 | 199.8 | 37 | 19.4 | 56.5 | 8.7 | 251.4 | 13.9 | 242.5 | 99.5 | 77.6 | 152.7 | 285.2 | 576.7 | 253.2 | 146 | 346.9 | 348.3 | 192.9 | 225.6 | 249.8 | 216.8 | 208.9 | 188.4 | 229.6 | 225.1 | 345.4 | 268.1
2457.4 | 2238.4 | -6.8 | 0 | 0 | 205.4 | 184.1 | 177.9 | 174.9 | 199.8 | 36.9 | 19.4 | 56.4 | 8.6 | 235.8 | 15 | 241.5 | 98.7 | 77.6 | 153 | 284.4 | 576.1 | 252.9 | 145.5 | 347.2 | 347.9 | 193 | 225.6 | 249.6 | 216.8 | 208.4 | 188.2 | 229.6 | 224.8 | 345.1 | 268
2458.4 | 2239.4 | -6.8 | 0 | 0 | 205 | 184 | 177.8 | 174.5 | 199.8 | 36.9 | 19.4 | 56.3 | 8.7 | 225.4 | 14.4 | 240.7 | 98.4 | 77.4 | 152.5 | 283.6 | 575.6 | 253 | 145.8 | 347.6 | 347.5 | 193.1 | 225.5 | 249.5 | 216.7 | 207.9 | 188 | 229.6 | 224.5 | 344.7 | 267.9
2459.4 | 2240.4 | -6.8 | 0 | 0 | 204.6 | 183.8 | 177.6 | 174.2 | 199.9 | 37 | 19.4 | 56.3 | 7.3 | 253.6 | 13.9 | 239.7 | 97.8 | 77.2 | 151.8 | 282.7 | 575.1 | 252.7 | 145.7 | 347.3 | 346.3 | 193.2 | 225.5 | 249.4 | 216.7 | 207.4 | 187.8 | 229.6 | 224.3 | 344.4 | 267.8
2460.4 | 2241.4 | -6.8 | 0 | 0 | 204.3 | 183.6 | 177.3 | 173.7 | 199.9 | 37 | 19.4 | 56.1 | 7.4 | 234.4 | 13.8 | 238.9 | 97.1 | 76.9 | 151 | 281.3 | 574.5 | 252.5 | 145.8 | 347.7 | 345.7 | 193.3 | 225.5 | 249.2 | 216.7 | 207.2 | 187.6 | 229.6 | 224 | 344 | 267.6
2461.4 | 2242.4 | -6.8 | 0 | 0 | 204 | 183.4 | 177.1 | 173.2 | 199.4 | 37 | 19.4 | 56 | 7.9 | 246.2 | 13.9 | 237.9 | 96.6 | 76.7 | 150.6 | 280.2 | 574 | 252.2 | 145.7 | 347.5 | 345.3 | 193.3 | 225.4 | 249.1 | 216.7 | 207.1 | 187.4 | 229.6 | 223.8 | 343.7 | 267.5
2462.4 | 2243.4 | -6.8 | 0 | 0 | 203.9 | 183.2 | 177 | 173 | 199.3 | 37 | 19.4 | 55.9 | 8.3 | 241.3 | 12.1 | 236.7 | 96.1 | 76 | 150.1 | 279.2 | 573.5 | 251.9 | 145 | 346.8 | 343.9 | 193.4 | 225.4 | 248.9 | 216.6 | 206.9 | 187.2 | 229.7 | 223.6 | 343.3 | 267.4
2463.4 | 2244.4 | -6.8 | 0 | 0 | 203.6 | 183.1 | 177 | 173 | 199 | 37 | 19.4 | 55.8 | 8.2 | 246.3 | 11.1 | 235.6 | 95.6 | 75.5 | 148.8 | 278.2 | 573 | 251.8 | 144.5 | 346.2 | 342.7 | 193.5 | 225.3 | 248.8 | 216.6 | 206.7 | 187 | 229.6 | 223.3 | 342.9 | 267.2
2464.4 | 2245.4 | -6.8 | 0 | 0 | 203.2 | 182.9 | 176.8 | 173.1 | 198.5 | 37 | 19.4 | 55.7 | 8.3 | 241.5 | 11.8 | 234.8 | 94.9 | 75.1 | 147.8 | 277.2 | 572.5 | 251.8 | 144.2 | 345.7 | 341.9 | 193.6 | 225.3 | 248.7 | 216.6 | 206.4 | 186.7 | 229.6 | 223.1 | 342.6 | 267.1
2465.4 | 2246.4 | -6.7 | 0 | 0 | 203 | 182.7 | 176.4 | 173 | 198.2 | 36.9 | 19.4 | 55.6 | 8.2 | 249 | 11.5 | 234 | 94.5 | 75 | 146.8 | 276.2 | 572 | 251.9 | 143.5 | 343.2 | 341.6 | 193.7 | 225.3 | 248.5 | 216.5 | 206.2 | 186.5 | 229.6 | 222.9 | 342.3 | 267
2466.4 | 2247.4 | -6.7 | 0 | 0 | 202.8 | 182.6 | 176.3 | 172.8 | 198 | 36.8 | 19.4 | 55.6 | 7.3 | 247.7 | 9.9 | 233.2 | 94.2 | 74.9 | 146 | 275.3 | 571.4 | 251.4 | 142.8 | 339.9 | 340.9 | 193.7 | 225.2 | 248.4 | 216.5 | 206 | 186.3 | 229.6 | 222.6 | 341.9 | 266.8
2467.4 | 2248.4 | -6.7 | 0 | 0 | 202.5 | 182.4 | 176.3 | 172.6 | 197.7 | 36.8 | 19.4 | 55.5 | 7.2 | 257.7 | 9.1 | 232.4 | 93.3 | 74.5 | 145.4 | 274.3 | 570.8 | 250.4 | 142.3 | 338 | 340.1 | 193.8 | 225.2 | 248.2 | 216.5 | 206 | 186.2 | 229.6 | 222.4 | 341.6 | 266.7
2468.4 | 2249.4 | -6.7 | 0 | 0 | 202.4 | 182.2 | 176.1 | 172.3 | 197.4 | 36.7 | 19.4 | 55.5 | 7.2 | 243.5 | 9.5 | 231.7 | 92.4 | 74 | 144.2 | 273.4 | 570.3 | 250.1 | 141.7 | 339.2 | 339.7 | 193.9 | 225.2 | 248.1 | 216.5 | 205.9 | 186 | 229.6 | 222.1 | 341.3 | 266.5
2469.4 | 2250.4 | -6.7 | 0 | 0 | 202.3 | 182 | 175.8 | 172 | 197.6 | 36.7 | 19.4 | 55.5 | 8.3 | 268.1 | 8.2 | 230.9 | 91.5 | 74.5 | 142.8 | 272.6 | 569.7 | 249.7 | 141.8 | 339.9 | 339.4 | 194 | 225.1 | 248 | 216.4 | 205.9 | 185.8 | 229.7 | 222 | 340.9 | 266.4
2470.4 | 2251.4 | -6.6 | 0 | 0 | 202 | 181.9 | 175.6 | 171.7 | 197.2 | 36.6 | 19.4 | 55.4 | 8.1 | 239.9 | 8.1 | 230 | 91.8 | 74 | 141.8 | 271.8 | 569.3 | 249.2 | 141.1 | 339.9 | 339.1 | 194.1 | 225.1 | 247.8 | 216.4 | 205.7 | 185.6 | 229.7 | 221.7 | 340.6 | 266.3
2471.4 | 2252.4 | -6.6 | 0 | 0 | 202 | 181.7 | 175.4 | 171.4 | 196.7 | 36.5 | 19.5 | 55.4 | 8.2 | 246.8 | 9.2 | 229.2 | 91.6 | 73.4 | 140.9 | 270.8 | 568.9 | 248.7 | 140.8 | 340.4 | 338.6 | 194.1 | 225.1 | 247.7 | 216.4 | 205.4 | 185.4 | 229.6 | 221.5 | 340.2 | 266.1
2472.4 | 2253.4 | -6.7 | 0 | 0 | 201.9 | 181.5 | 175.3 | 171.3 | 196.4 | 36.5 | 19.5 | 55.4 | 9.6 | 241 | 10.1 | 228.4 | 91.3 | 73.2 | 140 | 269.9 | 568.4 | 248.4 | 140.7 | 340.9 | 338 | 194.2 | 225 | 247.5 | 216.3 | 205.1 | 185.2 | 229.7 | 221.3 | 339.9 | 266
2473.4 | 2254.4 | -6.7 | 0 | 0 | 201.7 | 181.4 | 175.1 | 171.3 | 196.2 | 36.5 | 19.5 | 55.4 | 8.6 | 237.9 | 9.3 | 227.3 | 91.2 | 72.8 | 139.1 | 269 | 567.9 | 247.9 | 141.1 | 341.7 | 337.6 | 194.3 | 225 | 247.4 | 216.3 | 205.1 | 185 | 229.7 | 221 | 339.5 | 265.9
2474.4 | 2255.4 | -6.8 | 0 | 0 | 201.5 | 181.3 | 174.9 | 171.3 | 196 | 36.4 | 19.5 | 55.3 | 8 | 248.6 | 11.4 | 226.5 | 91.3 | 72.4 | 138.3 | 268 | 567.3 | 247.6 | 140.2 | 342.1 | 337.1 | 194.4 | 225 | 247.3 | 216.3 | 205 | 184.8 | 229.7 | 220.8 | 339.2 | 265.7
2475.4 | 2256.4 | -6.8 | 0 | 0 | 201.3 | 181.1 | 174.8 | 171.2 | 195.8 | 36.5 | 19.5 | 55.2 | 7.4 | 241.8 | 14.7 | 225.7 | 91.7 | 72 | 138.3 | 267.2 | 566.7 | 247.2 | 139.4 | 342.2 | 336.5 | 194.4 | 224.9 | 247.1 | 216.2 | 204.8 | 184.6 | 229.6 | 220.5 | 338.9 | 265.6
2476.4 | 2257.4 | -6.7 | 0 | 0 | 201.2 | 180.9 | 174.6 | 171.1 | 195.5 | 36.5 | 19.5 | 55.1 | 8.1 | 248.9 | 17.7 | 225.1 | 90.9 | 72.1 | 138.1 | 266.5 | 566.2 | 247.5 | 139.4 | 342 | 335.9 | 194.5 | 224.9 | 247 | 216.2 | 204.6 | 184.4 | 229.7 | 220.3 | 338.5 | 265.5
2477.4 | 2258.4 | -6.7 | 0 | 0 | 200.8 | 180.9 | 174.6 | 171 | 195.4 | 36.5 | 19.5 | 55.1 | 8.7 | 230 | 18.1 | 224.4 | 90.7 | 72 | 138.4 | 265.8 | 565.7 | 247.3 | 139.8 | 341.9 | 335.6 | 194.6 | 224.9 | 246.9 | 216.1 | 204.3 | 184.2 | 229.7 | 220.1 | 338.1 | 265.3
2478.4 | 2259.4 | -6.7 | 0 | 0 | 200.9 | 180.6 | 174.2 | 170.7 | 195.4 | 36.5 | 19.5 | 55 | 10.1 | 236.9 | 15.4 | 223.8 | 90.7 | 71.6 | 138.6 | 264.9 | 565.2 | 246.3 | 140.3 | 340.9 | 335.4 | 194.7 | 224.8 | 246.7 | 216.1 | 204.1 | 184 | 229.7 | 219.9 | 337.8 | 265.2
2479.4 | 2260.4 | -6.7 | 0 | 0 | 201 | 180.4 | 173.9 | 170.5 | 195.1 | 36.4 | 19.5 | 54.9 | 9.6 | 248.1 | 14.6 | 223.2 | 90.2 | 71.4 | 138.6 | 264.1 | 564.7 | 246.1 | 140.1 | 340.7 | 335 | 194.8 | 224.8 | 246.6 | 216.1 | 203.9 | 183.8 | 229.7 | 219.6 | 337.5 | 265.1
2480.4 | 2261.4 | -6.7 | 0 | 0 | 200 | 180.4 | 174.3 | 170.7 | 194.7 | 36.4 | 19.5 | 54.9 | 8.8 | 241 | 15.7 | 222.5 | 89.4 | 71.5 | 138.8 | 263.3 | 564.2 | 245.5 | 139.7 | 339.9 | 334.6 | 194.8 | 224.8 | 246.4 | 216 | 203.5 | 183.7 | 229.6 | 219.4 | 337 | 264.9
2481.4 | 2262.4 | -6.7 | 0 | 0 | 200.5 | 179.9 | 173.8 | 170.3 | 194.9 | 36.2 | 19.5 | 54.8 | 10.4 | 242.3 | 14 | 221.8 | 88.9 | 71.5 | 139 | 262.4 | 563.9 | 244.6 | 139.8 | 338.9 | 334.3 | 194.9 | 224.7 | 246.3 | 216 | 203 | 183.5 | 229.7 | 219.2 | 336.8 | 264.8
2482.4 | 2263.4 | -6.8 | 0 | 0 | 200.4 | 179.7 | 173.6 | 170.2 | 194.9 | 36.1 | 19.5 | 54.8 | 9.2 | 244.2 | 14.8 | 221.1 | 88.9 | 71.5 | 138.9 | 261.5 | 563.5 | 244.2 | 140 | 339.3 | 333.9 | 195 | 224.7 | 246.2 | 216 | 202.7 | 183.3 | 229.7 | 219 | 336.5 | 264.7
2483.4 | 2264.4 | -6.8 | 0 | 0 | 200.4 | 179.4 | 173.3 | 170.1 | 194.7 | 36 | 19.5 | 54.8 | 10.3 | 252.1 | 16.7 | 220.2 | 89.5 | 71.5 | 138.4 | 260.6 | 563.1 | 244.1 | 140 | 338.5 | 333.6 | 195.1 | 224.6 | 246.1 | 215.9 | 202.5 | 183.1 | 229.6 | 218.8 | 336.1 | 264.6
2484.4 | 2265.4 | -6.8 | 0 | 0 | 200.3 | 179.2 | 173.1 | 170 | 194.5 | 36 | 19.5 | 54.7 | 9.7 | 246.5 | 16.2 | 219.3 | 89.2 | 71.4 | 137.7 | 259.8 | 562.7 | 243.8 | 140.1 | 337.2 | 333.2 | 195.1 | 224.6 | 245.9 | 215.9 | 202.2 | 182.9 | 229.7 | 218.6 | 335.8 | 264.4
2485.4 | 2266.4 | -6.8 | 0 | 0 | 200.2 | 178.9 | 172.8 | 169.9 | 194.4 | 35.9 | 19.5 | 54.7 | 10 | 250.1 | 17.9 | 218.8 | 88.2 | 71.1 | 137.4 | 258.9 | 562.4 | 243 | 139.3 | 336.4 | 332.7 | 195.2 | 224.5 | 245.8 | 215.9 | 201.7 | 182.7 | 229.7 | 218.3 | 335.4 | 264.3
2486.4 | 2267.4 | -6.8 | 0 | 0 | 200.1 | 178.7 | 172.5 | 169.7 | 194.1 | 35.9 | 19.5 | 54.6 | 10.3 | 249.1 | 19.2 | 218.2 | 87.6 | 70.7 | 137.1 | 258 | 562 | 242.8 | 139.1 | 336.3 | 332.1 | 195.3 | 224.5 | 245.6 | 215.8 | 201.4 | 182.4 | 229.7 | 218.1 | 335.1 | 264.2
2487.4 | 2268.4 | -6.7 | 0 | 0 | 199.9 | 178.5 | 172.4 | 169.5 | 194.1 | 35.8 | 19.5 | 54.5 | 11.1 | 255 | 19.3 | 217.6 | 86.5 | 70.2 | 137 | 257.3 | 561.6 | 242.4 | 138.9 | 336.2 | 331.6 | 195.4 | 224.5 | 245.5 | 215.8 | 201.1 | 182.2 | 229.7 | 217.9 | 334.8 | 264
2488.4 | 2269.4 | -6.6 | 0 | 0 | 199.8 | 178.3 | 172.4 | 169.4 | 194.4 | 35.8 | 19.5 | 54.4 | 10.1 | 244.1 | 18.3 | 217 | 85.7 | 70.1 | 137.1 | 256.5 | 561.2 | 241.6 | 138.5 | 335.5 | 331.2 | 195.4 | 224.5 | 245.4 | 215.7 | 200.8 | 182 | 229.6 | 217.7 | 334.5 | 263.9
2489.4 | 2270.4 | -6.5 | 0 | 0 | 199.6 | 178.2 | 172.1 | 169.4 | 194.1 | 35.7 | 19.5 | 54.3 | 9.7 | 241.2 | 17.3 | 216.3 | 85.1 | 69.7 | 136.7 | 255.5 | 560.7 | 241.3 | 138.5 | 335.3 | 330.9 | 195.5 | 224.4 | 245.2 | 215.7 | 200.6 | 181.8 | 229.6 | 217.4 | 334.1 | 263.7
2490.4 | 2271.4 | -6.5 | 0 | 0 | 199.4 | 178 | 172 | 169.1 | 193.7 | 35.7 | 19.5 | 54.2 | 10.6 | 255.9 | 16.1 | 215.4 | 84.3 | 69.4 | 136 | 254.7 | 560.3 | 240.6 | 137.2 | 334.2 | 330.2 | 195.6 | 224.4 | 245.1 | 215.7 | 200.3 | 181.6 | 229.7 | 217.2 | 333.8 | 263.6
2491.4 | 2272.4 | -6.5 | 0 | 0 | 199.2 | 177.8 | 172 | 168.9 | 193.4 | 35.7 | 19.5 | 54.1 | 10.2 | 251.5 | 15.6 | 214.8 | 83.7 | 69.2 | 135.8 | 253.9 | 559.8 | 240.4 | 136.3 | 333.1 | 329.6 | 195.6 | 224.3 | 245 | 215.6 | 200 | 181.5 | 229.7 | 217 | 333.4 | 263.5
2492.4 | 2273.4 | -6.5 | 0 | 0 | 199.1 | 177.6 | 171.8 | 168.7 | 193 | 35.7 | 19.5 | 53.9 | 10.3 | 254.3 | 16.5 | 214.3 | 83.2 | 69.4 | 135.5 | 253.2 | 559.3 | 240.1 | 136 | 333.4 | 329 | 195.7 | 224.3 | 244.8 | 215.6 | 199.6 | 181.3 | 229.6 | 216.7 | 333.1 | 263.3
2493.4 | 2274.4 | -6.5 | 0 | 0 | 198.9 | 177.5 | 171.5 | 168.3 | 193 | 35.6 | 19.6 | 53.8 | 10.3 | 256.6 | 15.9 | 213.7 | 82.8 | 69.4 | 134.9 | 252.5 | 558.8 | 239.7 | 136.4 | 333.9 | 328.5 | 195.8 | 224.3 | 244.7 | 215.5 | 199.4 | 181.1 | 229.7 | 216.5 | 332.8 | 263.2
2494.4 | 2275.4 | -6.5 | 0 | 0 | 198.7 | 177.4 | 171.5 | 168 | 192.9 | 35.6 | 19.5 | 53.8 | 9.2 | 254.6 | 14.8 | 213 | 83.1 | 69.5 | 134.1 | 251.5 | 558.2 | 239.4 | 136.7 | 334 | 327.9 | 195.9 | 224.2 | 244.5 | 215.5 | 199.3 | 181 | 229.6 | 216.3 | 332.5 | 263.1
2495.4 | 2276.4 | -6.5 | 0 | 0 | 198.6 | 177.2 | 171.4 | 167.8 | 192.7 | 35.6 | 19.6 | 53.7 | 8.3 | 257.5 | 13.8 | 212.1 | 83.3 | 69.1 | 133.2 | 250.9 | 557.9 | 238.9 | 137 | 333.2 | 327.6 | 195.9 | 224.2 | 244.4 | 215.5 | 199.2 | 180.9 | 229.7 | 216.1 | 332.1 | 262.9
2496.4 | 2277.4 | -6.5 | 0 | 0 | 198.4 | 177 | 171.4 | 167.6 | 192.3 | 35.6 | 19.6 | 53.6 | 7.6 | 274.2 | 13.7 | 211.4 | 82.6 | 69.1 | 132.5 | 250.2 | 557.5 | 238.1 | 136.5 | 332.7 | 327.1 | 196 | 224.2 | 244.3 | 215.4 | 199.1 | 180.6 | 229.7 | 215.9 | 331.8 | 262.8
2497.4 | 2278.4 | -6.6 | 0 | 0 | 198.2 | 176.8 | 171.2 | 167.4 | 192 | 35.5 | 19.6 | 53.6 | 6.8 | 276.8 | 12.8 | 210.7 | 82 | 68.7 | 131.8 | 249.3 | 557.1 | 237.5 | 135.5 | 332.2 | 326.7 | 196.1 | 224.1 | 244.2 | 215.4 | 199.1 | 180.4 | 229.7 | 215.7 | 331.5 | 262.7
2498.4 | 2279.4 | -6.7 | 0 | 0 | 198 | 176.7 | 171.1 | 167.1 | 192 | 35.5 | 19.6 | 53.6 | 6.5 | 280.9 | 12.2 | 210.1 | 81.6 | 68.8 | 131.3 | 248.6 | 556.7 | 236.4 | 134.4 | 330.1 | 326.2 | 196.2 | 224.1 | 244 | 215.3 | 198.9 | 180.2 | 229.6 | 215.4 | 331.1 | 262.5
2499.4 | 2280.4 | -6.8 | 0 | 0 | 197.9 | 176.5 | 171 | 166.8 | 191.9 | 35.5 | 19.6 | 53.5 | 6.8 | 265.3 | 12.5 | 209.5 | 81.2 | 69 | 130.9 | 247.8 | 556.3 | 236.3 | 134.6 | 329.1 | 325.3 | 196.2 | 224.1 | 243.9 | 215.3 | 198.6 | 180.1 | 229.6 | 215.2 | 330.8 | 262.4
2500.4 | 2281.4 | -6.7 | 0 | 0 | 197.9 | 176.3 | 170.9 | 166.5 | 191.8 | 35.4 | 19.6 | 53.5 | 7 | 268 | 12.6 | 209 | 81 | 68.7 | 130.6 | 247.1 | 555.9 | 236.2 | 134.6 | 329.3 | 324.4 | 196.3 | 224 | 243.8 | 215.2 | 198.3 | 179.9 | 229.7 | 215.1 | 330.5 | 262.3
2501.4 | 2282.4 | -6.7 | 0 | 0 | 197.7 | 176.2 | 170.8 | 166.4 | 191.6 | 35.3 | 19.6 | 53.4 | 7.3 | 274.5 | 12.1 | 208.4 | 81.4 | 68.4 | 130.7 | 246.3 | 555.5 | 235.8 | 134.8 | 329.8 | 323.6 | 196.3 | 224 | 243.6 | 215.2 | 198 | 179.8 | 229.6 | 214.8 | 330.2 | 262.1
2502.4 | 2283.4 | -6.7 | 0 | 0 | 197.3 | 176 | 170.8 | 166.4 | 191.3 | 35.1 | 19.6 | 53.4 | 7.5 | 272 | 11.6 | 207.8 | 81.3 | 68.1 | 130.4 | 245.4 | 555.1 | 235.4 | 134.7 | 329.2 | 323.1 | 196.4 | 224 | 243.5 | 215.2 | 197.9 | 179.6 | 229.6 | 214.6 | 329.8 | 262
2503.4 | 2284.4 | -6.6 | 0 | 0 | 196.9 | 175.9 | 170.6 | 166.3 | 191 | 35 | 19.6 | 53.3 | 8.4 | 270.9 | 10.7 | 207.3 | 80.4 | 67.7 | 130.4 | 244.5 | 554.7 | 234.9 | 134.5 | 328.1 | 323 | 196.5 | 223.9 | 243.4 | 215.1 | 197.7 | 179.5 | 229.6 | 214.4 | 329.5 | 261.9
2504.4 | 2285.4 | -6.5 | 0 | 0 | 196.6 | 175.7 | 170.4 | 166.2 | 190.7 | 34.9 | 19.6 | 53.2 | 8.9 | 281.8 | 10.7 | 206.7 | 80 | 67.5 | 130.1 | 243.7 | 554.4 | 234.8 | 134.3 | 327.8 | 322.2 | 196.6 | 223.9 | 243.2 | 215.1 | 197.7 | 179.3 | 229.6 | 214.1 | 329.2 | 261.7
2505.4 | 2286.4 | -6.5 | 0 | 0 | 196.3 | 175.6 | 170.2 | 165.9 | 190.3 | 34.9 | 19.6 | 53.1 | 8.7 | 281.2 | 10.8 | 206 | 78.9 | 67.5 | 129.5 | 242.9 | 554 | 234.3 | 134.2 | 327 | 321.8 | 196.6 | 223.9 | 243.1 | 215 | 197.6 | 179.2 | 229.6 | 213.9 | 328.9 | 261.6
2506.4 | 2287.4 | -6.5 | 0 | 0 | 196 | 175.5 | 170 | 165.8 | 190 | 34.8 | 19.6 | 53.1 | 8.5 | 280.4 | 10.6 | 205.5 | 78 | 67.4 | 129.6 | 242.2 | 553.7 | 233.9 | 134.2 | 327.8 | 321.2 | 196.7 | 223.8 | 243 | 215 | 197.4 | 179 | 229.6 | 213.7 | 328.5 | 261.5
2507.4 | 2288.4 | -6.5 | 0 | 0 | 195.9 | 175.3 | 169.9 | 165.8 | 189.7 | 34.8 | 19.6 | 53 | 9 | 280.7 | 12.5 | 205 | 77.4 | 67.1 | 129.9 | 241.4 | 553.3 | 233.5 | 133.3 | 328.6 | 320.8 | 196.8 | 223.8 | 242.8 | 214.9 | 197 | 178.9 | 229.6 | 213.6 | 328.2 | 261.3
2508.4 | 2289.4 | -6.5 | 0 | 0 | 195.7 | 175.1 | 169.7 | 165.9 | 189.5 | 34.8 | 19.6 | 53 | 8.6 | 277.2 | 12.2 | 204.4 | 76.8 | 67 | 129.9 | 240.6 | 553 | 233.4 | 132.9 | 327.8 | 320.4 | 196.8 | 223.8 | 242.7 | 214.9 | 196.8 | 178.7 | 229.6 | 213.3 | 327.9 | 261.2
2509.4 | 2290.4 | -6.6 | 0 | 0 | 195.6 | 174.9 | 169.5 | 165.8 | 189.2 | 34.8 | 19.6 | 53 | 8.1 | 277.3 | 10.6 | 203.9 | 76.7 | 66.9 | 130 | 239.9 | 552.6 | 232.8 | 132.8 | 328 | 319.6 | 196.9 | 223.7 | 242.6 | 214.8 | 196.8 | 178.5 | 229.6 | 213.1 | 327.6 | 261.1
2510.4 | 2291.4 | -6.6 | 0 | 0 | 195.5 | 174.7 | 169.3 | 165.7 | 189.2 | 34.8 | 19.6 | 53 | 7 | 288.6 | 9.9 | 203.1 | 76.3 | 66.7 | 130 | 239.3 | 552.2 | 232.3 | 132.7 | 328 | 318.9 | 197 | 223.7 | 242.4 | 214.8 | 196.7 | 178.4 | 229.6 | 212.9 | 327.2 | 260.9
2511.4 | 2292.4 | -6.6 | 0 | 0 | 195.4 | 174.5 | 169.1 | 165.4 | 189.2 | 34.9 | 19.6 | 53 | 6.4 | 287.6 | 9.4 | 202.6 | 76 | 66.8 | 130.3 | 238.5 | 551.8 | 231.6 | 132.6 | 328.3 | 318.2 | 197 | 223.7 | 242.3 | 214.7 | 196.6 | 178.3 | 229.6 | 212.7 | 326.9 | 260.8
2512.4 | 2293.4 | -6.5 | 0 | 0 | 195.1 | 174.3 | 168.9 | 165 | 189 | 34.9 | 19.6 | 53.1 | 6.5 | 285.5 | 8.8 | 202.1 | 76.1 | 66.8 | 130.4 | 237.7 | 551.4 | 231.2 | 132.5 | 327.7 | 317.7 | 197.1 | 223.6 | 242.2 | 214.7 | 196.5 | 178.1 | 229.6 | 212.4 | 326.6 | 260.7
2513.4 | 2294.4 | -6.5 | 0 | 0 | 194.8 | 174.2 | 168.6 | 164.8 | 188.8 | 35 | 19.6 | 53 | 6.2 | 295.2 | 7.7 | 201.5 | 75.6 | 66.5 | 130.1 | 236.9 | 551.1 | 230.7 | 132.6 | 327.3 | 317.4 | 197.2 | 223.6 | 242.1 | 214.6 | 196.3 | 177.9 | 229.6 | 212.2 | 326.3 | 260.5
2514.4 | 2295.4 | -6.5 | 0 | 0 | 194.6 | 174.1 | 168.5 | 164.6 | 188.7 | 35 | 19.6 | 53 | 5.9 | 300.3 | 6.3 | 201 | 74.8 | 66.4 | 129.7 | 236.1 | 550.7 | 230.2 | 132.1 | 326.7 | 317.1 | 197.2 | 223.5 | 241.9 | 214.6 | 196.1 | 177.7 | 229.6 | 212 | 325.9 | 260.4
2515.4 | 2296.4 | -6.5 | 0 | 0 | 194.4 | 174 | 168.5 | 164.7 | 188.5 | 35 | 19.6 | 52.9 | 5.6 | 283 | 5.8 | 200.5 | 74.5 | 66.4 | 129 | 235.3 | 550.4 | 229.6 | 131.1 | 325.7 | 316.6 | 197.3 | 223.5 | 241.8 | 214.6 | 196 | 177.5 | 229.6 | 211.8 | 325.6 | 260.3
2516.4 | 2297.4 | -6.5 | 0 | 0 | 194.2 | 173.9 | 168.4 | 164.6 | 188.4 | 35 | 19.6 | 52.8 | 5.4 | 293.2 | 5.9 | 199.8 | 74.2 | 66.5 | 128.4 | 234.7 | 550.1 | 229.5 | 130.6 | 325.6 | 315.8 | 197.4 | 223.5 | 241.7 | 214.5 | 195.9 | 177.3 | 229.6 | 211.6 | 325.3 | 260.1
2517.4 | 2298.4 | -6.5 | 0 | 0 | 194.1 | 173.8 | 168.3 | 164.5 | 188.4 | 35 | 19.7 | 52.8 | 5.7 | 284.3 | 5.8 | 199.1 | 73.8 | 66.7 | 127.4 | 234.1 | 549.8 | 229.7 | 130.1 | 325.9 | 315.5 | 197.4 | 223.4 | 241.5 | 214.5 | 195.8 | 177.1 | 229.6 | 211.4 | 325 | 260
2518.4 | 2299.4 | -6.6 | 0 | 0 | 194.1 | 173.7 | 168.1 | 164.4 | 188.3 | 34.9 | 19.6 | 52.7 | 6.2 | 254 | 5.8 | 198.4 | 74.2 | 66.6 | 126.1 | 233.3 | 549.5 | 229.7 | 129 | 325.7 | 315 | 197.5 | 223.4 | 241.4 | 214.4 | 195.6 | 177 | 229.6 | 211.2 | 324.7 | 259.9
2519.4 | 2300.4 | -6.5 | 0 | 0 | 194 | 173.6 | 167.9 | 164.3 | 188.2 | 34.9 | 19.6 | 52.7 | 6.2 | 253.6 | 6.3 | 197.6 | 74.3 | 66.7 | 124.7 | 232.5 | 549.3 | 229.3 | 128.2 | 325 | 314.2 | 197.6 | 223.4 | 241.3 | 214.4 | 195.5 | 176.9 | 229.6 | 211 | 324.4 | 259.7
2520.4 | 2301.4 | -6.5 | 0 | 0 | 193.8 | 173.4 | 167.8 | 164.2 | 187.9 | 34.8 | 19.6 | 52.7 | 6.3 | 259.5 | 6.5 | 196.6 | 74.6 | 66.5 | 123.2 | 231.9 | 549.5 | 228.4 | 127.2 | 323.7 | 313.3 | 197.6 | 223.3 | 241.1 | 214.3 | 195.4 | 176.7 | 229.6 | 210.8 | 324 | 259.6
2521.4 | 2302.4 | -6.5 | 0 | 0 | 193.7 | 173.3 | 167.6 | 164.2 | 187.6 | 34.7 | 19.7 | 52.8 | 5.9 | 260.1 | 5.8 | 195.6 | 74 | 66.2 | 121.6 | 231.1 | 549.6 | 227.7 | 126 | 321.6 | 312.4 | 197.7 | 223.3 | 241 | 214.3 | 195.3 | 176.6 | 229.6 | 210.6 | 323.7 | 259.5
2522.4 | 2303.4 | -6.5 | 0 | 0 | 193.7 | 173.1 | 167.4 | 164.2 | 187.2 | 34.6 | 19.7 | 52.8 | 6.1 | 259.3 | 5.3 | 195 | 73.4 | 66.1 | 121 | 230.4 | 549.6 | 226.6 | 124.7 | 319.5 | 311.7 | 197.8 | 223.3 | 240.9 | 214.2 | 194.8 | 176.4 | 229.5 | 210.4 | 323.4 | 259.3
2523.4 | 2304.4 | -6.5 | 0 | 0 | 193.7 | 173 | 167.3 | 164.1 | 186.9 | 34.6 | 19.7 | 52.7 | 6.4 | 259.7 | 4.9 | 194.4 | 73.2 | 66 | 120.9 | 229.9 | 549.7 | 225.8 | 123.8 | 317.8 | 311.3 | 197.8 | 223.2 | 240.7 | 214.2 | 194.5 | 176.2 | 229.5 | 210.2 | 323.1 | 259.2
2524.4 | 2305.4 | -6.6 | 0 | 0 | 193.7 | 172.8 | 167.2 | 163.9 | 186.8 | 34.5 | 19.7 | 52.8 | 6.2 | 259.8 | 4.9 | 193.7 | 72.8 | 65.7 | 120.4 | 229.2 | 549.7 | 225.5 | 123.7 | 317.6 | 310.8 | 197.9 | 223.2 | 240.6 | 214.1 | 194.2 | 176.1 | 229.5 | 210 | 322.8 | 259.1
2525.4 | 2306.4 | -6.6 | 0 | 0 | 193.5 | 172.8 | 167.2 | 163.9 | 186.7 | 34.5 | 19.7 | 52.8 | 6.5 | 254.4 | 5.6 | 193.1 | 72.6 | 65.6 | 120.2 | 228.4 | 549.3 | 226 | 123.7 | 319.2 | 310.5 | 197.9 | 223.2 | 240.5 | 214.1 | 193.8 | 175.9 | 229.5 | 209.8 | 322.5 | 258.9
2526.4 | 2307.4 | -6.5 | 0 | 0 | 193.4 | 172.6 | 167.1 | 163.9 | 186.7 | 34.5 | 19.7 | 52.7 | 6.2 | 243.8 | 6 | 192.4 | 72.2 | 65.4 | 119.9 | 227.8 | 548.9 | 225.8 | 123.6 | 318.9 | 310.3 | 198 | 223.1 | 240.3 | 214 | 193.5 | 175.7 | 229.5 | 209.6 | 322.2 | 258.8
2527.4 | 2308.4 | -6.5 | 0 | 0 | 193.2 | 172.4 | 167.1 | 163.9 | 186.5 | 34.5 | 19.7 | 52.6 | 6.4 | 259.2 | 6 | 191.9 | 71.9 | 65.1 | 120 | 227.1 | 548.4 | 225.7 | 123.4 | 319.7 | 310.2 | 198.1 | 223.1 | 240.2 | 214 | 193.3 | 175.6 | 229.5 | 209.4 | 321.9 | 258.6
2528.4 | 2309.4 | -6.5 | 0 | 0 | 193 | 172.3 | 167 | 163.7 | 186.1 | 34.5 | 19.7 | 52.4 | 6.8 | 273.9 | 5.7 | 191.4 | 71.6 | 64.9 | 119.9 | 226.4 | 547.8 | 225.3 | 123.3 | 320.8 | 309.8 | 198.1 | 223.1 | 240.1 | 213.9 | 193.1 | 175.5 | 229.5 | 209.2 | 321.5 | 258.5
2529.4 | 2310.4 | -6.5 | 0 | 0 | 192.7 | 172.2 | 167 | 163.6 | 185.7 | 34.5 | 19.7 | 52.3 | 6.9 | 255.5 | 5.5 | 190.8 | 71 | 64.6 | 119.7 | 225.7 | 547.3 | 225.2 | 123.5 | 320.7 | 309.3 | 198.2 | 223 | 240 | 213.9 | 192.7 | 175.4 | 229.5 | 209 | 321.2 | 258.4
2530.4 | 2311.4 | -6.6 | 0 | 0 | 192.9 | 172 | 166.7 | 163.2 | 185.4 | 34.5 | 19.7 | 52.2 | 6.2 | 243.5 | 6 | 190.3 | 70.6 | 64.5 | 119.5 | 225.2 | 546.9 | 224.9 | 123.2 | 319.3 | 308.9 | 198.3 | 223 | 239.8 | 213.8 | 192.5 | 175.2 | 229.5 | 208.8 | 320.9 | 258.2
2531.4 | 2312.4 | -6.6 | 0 | 0 | 192.6 | 171.9 | 166.7 | 163 | 185.3 | 34.6 | 19.7 | 52.2 | 6.4 | 234.4 | 6.3 | 189.7 | 70 | 64.4 | 118.6 | 224.4 | 546.4 | 224.6 | 123.4 | 318.3 | 308.5 | 198.3 | 222.9 | 239.7 | 213.8 | 192.2 | 175 | 229.4 | 208.6 | 320.6 | 258.1
2532.4 | 2313.4 | -6.6 | 0 | 0 | 192.3 | 171.8 | 166.5 | 162.9 | 185.1 | 34.6 | 19.7 | 52.2 | 6.3 | 224.9 | 5.7 | 189 | 69.7 | 64.4 | 117.4 | 223.4 | 546 | 224.5 | 123.7 | 318.2 | 308.1 | 198.4 | 222.9 | 239.6 | 213.7 | 192 | 174.9 | 229.5 | 208.4 | 320.2 | 258
2533.4 | 2314.4 | -6.6 | 0 | 0 | 192.5 | 171.6 | 166 | 162.6 | 184.7 | 34.6 | 19.7 | 52.1 | 6.5 | 225.8 | 5 | 188.5 | 69.3 | 64.3 | 116.3 | 222.8 | 545.6 | 223.8 | 123.2 | 318.9 | 307.7 | 198.4 | 222.9 | 239.5 | 213.7 | 191.8 | 174.7 | 229.5 | 208.2 | 320 | 257.9
2534.4 | 2315.4 | -6.5 | 0 | 0 | 192.1 | 171.6 | 166.1 | 162.6 | 184.4 | 34.6 | 19.7 | 52.1 | 7.1 | 230.7 | 4.6 | 187.9 | 69.1 | 64.3 | 115.7 | 222 | 545.2 | 223.3 | 122.5 | 317.9 | 307.3 | 198.5 | 222.8 | 239.3 | 213.6 | 191.7 | 174.6 | 229.4 | 208 | 319.6 | 257.7
2535.4 | 2316.4 | -6.6 | 0 | 0 | 192 | 171.5 | 166 | 162.4 | 184.1 | 34.5 | 19.7 | 52.2 | 6.4 | 227.6 | 4.5 | 187.4 | 68.7 | 64.4 | 115.1 | 221.2 | 544.9 | 222.5 | 121.7 | 315.2 | 306.9 | 198.6 | 222.8 | 239.2 | 213.6 | 191.4 | 174.5 | 229.4 | 207.8 | 319.3 | 257.6
2536.4 | 2317.4 | -6.7 | 0 | 0 | 192.1 | 171.3 | 165.7 | 162.2 | 183.9 | 34.4 | 19.7 | 52.2 | 6.2 | 220.5 | 4.7 | 186.8 | 68.3 | 64.5 | 114.6 | 220.5 | 544.5 | 222 | 121.1 | 314.9 | 306.3 | 198.6 | 222.8 | 239.1 | 213.5 | 191.2 | 174.3 | 229.4 | 207.6 | 319.1 | 257.5
2537.4 | 2318.4 | -6.6 | 0 | 0 | 191.9 | 171.1 | 165.4 | 162.2 | 183.8 | 34.4 | 19.7 | 52.2 | 6.5 | 220 | 4.9 | 186.2 | 68.2 | 64.2 | 114.1 | 219.9 | 544.1 | 221.6 | 121.1 | 315.6 | 305.8 | 198.7 | 222.7 | 239 | 213.5 | 191.1 | 174.2 | 229.4 | 207.5 | 318.8 | 257.3
2538.4 | 2319.4 | -6.5 | 0 | 0 | 191.7 | 170.9 | 165.1 | 162 | 183.9 | 34.4 | 19.7 | 52.3 | 6.6 | 232.6 | 4.6 | 185.5 | 68 | 64 | 113.1 | 219.2 | 543.8 | 220.8 | 121 | 315 | 305.5 | 198.8 | 222.7 | 238.8 | 213.4 | 190.9 | 174.1 | 229.4 | 207.3 | 318.5 | 257.2
2539.4 | 2320.4 | -6.5 | 0 | 0 | 191.4 | 170.7 | 165 | 161.8 | 183.6 | 34.3 | 19.7 | 52.3 | 6.9 | 254.3 | 4.1 | 184.8 | 67.9 | 64 | 112.4 | 218.6 | 543.5 | 220.4 | 121 | 314.9 | 305.2 | 198.8 | 222.6 | 238.7 | 213.3 | 190.9 | 173.9 | 229.4 | 207.1 | 318.2 | 257.1
2540.4 | 2321.4 | -6.5 | 0 | 0 | 190.8 | 170.8 | 164.9 | 161.6 | 183.2 | 34.3 | 19.7 | 52.3 | 6.6 | 239 | 3.4 | 184.3 | 67.7 | 64.1 | 112.5 | 218 | 543.2 | 220.4 | 121.2 | 316.1 | 304.7 | 198.9 | 222.6 | 238.6 | 213.3 | 190.9 | 173.8 | 229.3 | 206.9 | 317.8 | 256.9
2541.4 | 2322.4 | -6.5 | 0 | 0 | 190.8 | 170.6 | 164.5 | 161.5 | 183 | 34.2 | 19.7 | 52.2 | 6.4 | 214.8 | 3.2 | 183.9 | 67.5 | 63.9 | 112.8 | 217.3 | 542.8 | 220.2 | 120.8 | 317.1 | 304.4 | 198.9 | 222.6 | 238.4 | 213.2 | 190.9 | 173.7 | 229.3 | 206.7 | 317.6 | 256.8
2542.4 | 2323.4 | -6.5 | 0 | 0 | 190.7 | 170.5 | 164.2 | 161.4 | 183 | 34.2 | 19.7 | 52.1 | 5.7 | 222.1 | 3.6 | 183.4 | 67.5 | 63.8 | 112.9 | 216.7 | 542.4 | 219.8 | 120.7 | 317.6 | 304.1 | 199 | 222.5 | 238.3 | 213.2 | 190.8 | 173.5 | 229.4 | 206.5 | 317.2 | 256.7
2543.4 | 2324.4 | -6.5 | 0 | 0 | 190.1 | 170.5 | 164.3 | 161.4 | 182.9 | 34.2 | 19.7 | 52.1 | 6.3 | 230.2 | 3.8 | 182.8 | 67.4 | 63.8 | 113 | 216.1 | 542 | 219.9 | 120.5 | 317.7 | 303.8 | 199 | 222.5 | 238.2 | 213.1 | 190.7 | 173.3 | 229.3 | 206.3 | 316.9 | 256.5
2544.4 | 2325.4 | -6.5 | 0 | 0 | 190.2 | 170.3 | 164.2 | 160.9 | 182.7 | 34.1 | 19.7 | 52.1 | 6.4 | 218.7 | 3.8 | 182.2 | 66.8 | 63.5 | 112.6 | 215.6 | 541.6 | 220.1 | 120.3 | 317.1 | 303.5 | 199.1 | 222.5 | 238.1 | 213.1 | 190.5 | 173.2 | 229.3 | 206.1 | 316.6 | 256.4
2545.4 | 2326.4 | -6.4 | 0 | 0 | 190.3 | 170.1 | 164 | 160.4 | 182.7 | 34.1 | 19.7 | 52 | 6.1 | 218.6 | 3.9 | 181.7 | 66.5 | 63.5 | 111.8 | 214.9 | 541.2 | 220.1 | 119.9 | 317.2 | 303.2 | 199.2 | 222.4 | 238 | 213 | 190.2 | 173 | 229.3 | 205.9 | 316.3 | 256.2
2546.4 | 2327.4 | -6.5 | 0 | 0 | 190.1 | 169.9 | 163.9 | 160.1 | 182.4 | 34.1 | 19.7 | 51.9 | 6.3 | 241.2 | 4.6 | 181 | 66.4 | 63.4 | 111.3 | 214.3 | 540.9 | 219.8 | 120.1 | 317.3 | 302.9 | 199.2 | 222.4 | 237.8 | 213 | 190.1 | 172.9 | 229.3 | 205.7 | 316 | 256.1
2547.4 | 2328.4 | -6.5 | 0 | 0 | 189.8 | 169.8 | 163.8 | 160.1 | 182.3 | 34.1 | 19.7 | 51.9 | 6.7 | 236.1 | 6 | 180.4 | 66.6 | 63.2 | 111.1 | 213.7 | 540.6 | 219.4 | 120.2 | 317.2 | 302.7 | 199.3 | 222.3 | 237.7 | 212.9 | 190.1 | 172.8 | 229.3 | 205.6 | 315.7 | 256
2548.4 | 2329.4 | -6.4 | 0 | 0 | 189.9 | 169.5 | 163.6 | 159.8 | 182.4 | 34.1 | 19.7 | 51.9 | 6.4 | 235.9 | 6.2 | 179.9 | 66.3 | 62.9 | 110.7 | 213.1 | 540.2 | 219.6 | 120.6 | 318 | 302.5 | 199.3 | 222.3 | 237.6 | 212.9 | 189.9 | 172.6 | 229.3 | 205.4 | 315.4 | 255.9
2549.4 | 2330.4 | -6.4 | 0 | 0 | 189.7 | 169.3 | 163.4 | 159.4 | 182.2 | 34.1 | 19.8 | 51.9 | 6.5 | 236.2 | 6.1 | 179.5 | 66 | 62.9 | 110.4 | 212.5 | 539.9 | 219.6 | 121 | 317.9 | 302.2 | 199.4 | 222.3 | 237.4 | 212.8 | 189.8 | 172.5 | 229.2 | 205.2 | 315.1 | 255.7
2550.4 | 2331.4 | -6.4 | 0 | 0 | 189.8 | 169 | 163.1 | 159.1 | 181.9 | 34 | 19.8 | 51.9 | 6.2 | 242.2 | 6 | 178.9 | 65.5 | 62.7 | 110.2 | 211.7 | 539.5 | 218.8 | 121.4 | 316.5 | 301.7 | 199.4 | 222.2 | 237.3 | 212.7 | 189.7 | 172.3 | 229.2 | 205 | 314.8 | 255.6
2551.4 | 2332.4 | -6.3 | 0 | 0 | 189.2 | 169 | 163.3 | 159.3 | 181.7 | 34 | 19.8 | 51.8 | 6.3 | 229 | 5.6 | 178.5 | 65.3 | 62.4 | 110.3 | 211.1 | 539.2 | 218.6 | 121.4 | 316.1 | 301.5 | 199.5 | 222.2 | 237.2 | 212.7 | 189.4 | 172.2 | 229.2 | 204.8 | 314.5 | 255.4
2552.4 | 2333.4 | -6.3 | 0 | 0 | 189.3 | 168.7 | 163.1 | 159.2 | 181.5 | 34 | 19.8 | 51.8 | 6 | 220.4 | 5.2 | 178.2 | 65.3 | 62.3 | 110.5 | 210.5 | 538.8 | 218.5 | 121.4 | 315.3 | 301 | 199.6 | 222.1 | 237.1 | 212.6 | 189.2 | 172 | 229.2 | 204.6 | 314.2 | 255.3
2553.4 | 2334.4 | -6.3 | 0 | 0 | 189.4 | 168.5 | 162.8 | 159.1 | 181.4 | 34 | 19.8 | 51.9 | 6.1 | 227.9 | 4.6 | 177.7 | 65.2 | 62.2 | 110.8 | 209.9 | 538.4 | 217.9 | 121.5 | 315 | 300.3 | 199.6 | 222.1 | 236.9 | 212.6 | 189.1 | 171.9 | 229.2 | 204.4 | 313.9 | 255.2
2554.4 | 2335.4 | -6.3 | 0 | 0 | 188.9 | 168.5 | 162.6 | 158.9 | 181.4 | 34 | 19.8 | 51.9 | 5.8 | 232.7 | 3.8 | 177.2 | 65.1 | 62.3 | 110.9 | 209.3 | 538 | 217.7 | 121.8 | 314.5 | 300 | 199.7 | 222.1 | 236.8 | 212.5 | 188.8 | 171.7 | 229.2 | 204.2 | 313.6 | 255.1
2555.4 | 2336.4 | -6.3 | 0 | 0 | 188.8 | 168.4 | 162.4 | 158.7 | 181.2 | 34 | 19.8 | 51.8 | 6.2 | 251.7 | 3.2 | 176.8 | 64.8 | 62.4 | 110.7 | 208.7 | 537.7 | 217.3 | 121.7 | 314.1 | 299.8 | 199.7 | 222 | 236.7 | 212.5 | 188.6 | 171.6 | 229.2 | 204.1 | 313.3 | 254.9
2556.4 | 2337.4 | -6.3 | 0 | 0 | 188.8 | 168.3 | 162.1 | 158.6 | 181 | 34 | 19.8 | 51.7 | 6.8 | 247.9 | 2.6 | 176.5 | 64.5 | 62.5 | 110.4 | 208 | 537.3 | 216.9 | 122.1 | 313.8 | 299.4 | 199.8 | 222 | 236.6 | 212.4 | 188.5 | 171.4 | 229.2 | 203.9 | 313 | 254.8
2557.4 | 2338.4 | -6.4 | 0 | 0 | 188.5 | 168.3 | 161.9 | 158.2 | 180.8 | 33.9 | 19.8 | 51.7 | 7 | 213.4 | 2 | 175.8 | 64.2 | 62.1 | 110.2 | 207.3 | 536.8 | 216.9 | 122.5 | 313.2 | 298.9 | 199.8 | 222 | 236.4 | 212.4 | 188.4 | 171.3 | 229.1 | 203.7 | 312.7 | 254.7
2558.4 | 2339.4 | -6.3 | 0 | 0 | 188.4 | 168.1 | 161.9 | 157.9 | 180.8 | 33.9 | 19.8 | 51.6 | 7.1 | 215.6 | 1.6 | 175 | 63.9 | 61.8 | 110.4 | 206.5 | 536.3 | 216.9 | 122.4 | 311.7 | 298.4 | 199.9 | 221.9 | 236.3 | 212.3 | 188.2 | 171.1 | 229.1 | 203.5 | 312.4 | 254.5
2559.4 | 2340.4 | -6.4 | 0 | 0 | 188.3 | 168 | 161.9 | 157.9 | 180.9 | 33.9 | 19.8 | 51.5 | 7.2 | 214.3 | 1.8 | 174.5 | 63.4 | 61.7 | 110.1 | 205.8 | 535.8 | 216.6 | 122 | 311.6 | 297.6 | 199.9 | 221.9 | 236.2 | 212.2 | 187.9 | 171 | 229.1 | 203.3 | 312.1 | 254.4
2560.4 | 2341.4 | -6.4 | 0 | 0 | 188 | 167.9 | 161.9 | 157.9 | 180.6 | 33.9 | 19.8 | 51.5 | 8.1 | 201.9 | 3.9 | 173.9 | 63.3 | 61.4 | 109.4 | 205.2 | 535.4 | 216.8 | 121.5 | 311.9 | 297.1 | 200 | 221.8 | 236.1 | 212.2 | 187.8 | 170.9 | 229.1 | 203.2 | 311.8 | 254.3
2561.4 | 2342.4 | -6.4 | 0 | 0 | 187.8 | 167.8 | 161.9 | 157.6 | 180.5 | 33.9 | 19.8 | 51.4 | 8.8 | 197.4 | 7.8 | 173.4 | 63.1 | 61.3 | 108.8 | 204.6 | 535.1 | 216.9 | 121.2 | 312.4 | 296.8 | 200.1 | 221.8 | 236 | 212.1 | 187.6 | 170.7 | 229.1 | 203 | 311.4 | 254.1
2562.4 | 2343.4 | -6.3 | 0 | 0 | 188 | 167.6 | 161.5 | 157.3 | 180.4 | 33.8 | 19.8 | 51.4 | 9.1 | 212.1 | 8.2 | 172.8 | 62.6 | 61.1 | 108 | 204.1 | 534.8 | 217.1 | 121.2 | 312.6 | 296.4 | 200.1 | 221.8 | 235.8 | 212.1 | 187.5 | 170.6 | 229.1 | 202.8 | 311.2 | 254
2563.4 | 2344.4 | -6.3 | 0 | 0 | 188 | 167.4 | 161.3 | 157 | 180.3 | 33.7 | 19.8 | 51.3 | 10.2 | 208 | 7.9 | 172.4 | 62.2 | 61.1 | 107.3 | 203.5 | 534.5 | 216.7 | 121 | 312.7 | 296 | 200.2 | 221.7 | 235.7 | 212 | 187.2 | 170.4 | 229 | 202.6 | 311 | 253.9
2564.4 | 2345.4 | -6.4 | 0 | 0 | 187.3 | 167.5 | 161.5 | 156.9 | 180 | 33.7 | 19.8 | 51.3 | 8.8 | 210 | 8.7 | 172.1 | 61.9 | 61.2 | 106.9 | 202.7 | 534.1 | 216.5 | 120.8 | 312.7 | 295.5 | 200.2 | 221.7 | 235.6 | 212 | 186.8 | 170.3 | 229 | 202.5 | 310.6 | 253.7
2565.4 | 2346.4 | -6.4 | 0 | 0 | 187.1 | 167.4 | 161.5 | 156.6 | 179.8 | 33.7 | 19.8 | 51.2 | 7.9 | 223.1 | 7.3 | 171.5 | 61.6 | 60.9 | 106.4 | 202.2 | 533.9 | 216.6 | 120.3 | 312.5 | 294.8 | 200.3 | 221.6 | 235.5 | 211.9 | 186.6 | 170.2 | 229 | 202.3 | 310.3 | 253.6
2566.4 | 2347.4 | -6.5 | 0 | 0 | 186.8 | 167.3 | 161.4 | 156.8 | 179.6 | 33.7 | 19.8 | 51.2 | 7.9 | 189 | 6.3 | 171 | 61.5 | 60.9 | 105.9 | 201.7 | 533.9 | 215.9 | 120.1 | 311.6 | 294.4 | 200.3 | 221.6 | 235.4 | 211.9 | 186.3 | 170 | 229 | 202.1 | 310 | 253.5
2567.4 | 2348.4 | -6.6 | 0 | 0 | 186.3 | 167.3 | 161.5 | 156.9 | 179.6 | 33.7 | 19.8 | 51.1 | 7.5 | 219.3 | 5.1 | 170.4 | 62.2 | 60.8 | 105.2 | 201.1 | 533.7 | 215.6 | 119.6 | 311.7 | 294.1 | 200.4 | 221.6 | 235.2 | 211.8 | 186 | 169.9 | 229 | 201.9 | 309.7 | 253.3
2568.4 | 2349.4 | -6.6 | 0 | 0 | 186.7 | 167 | 161.2 | 156.6 | 179.3 | 33.7 | 19.8 | 51.1 | 9.4 | 267.7 | 5.1 | 169.9 | 61.9 | 60.5 | 104.6 | 200.6 | 533.3 | 215.5 | 119.6 | 311.5 | 293.5 | 200.4 | 221.5 | 235.1 | 211.7 | 185.8 | 169.8 | 228.9 | 201.8 | 309.5 | 253.2
2569.4 | 2350.4 | -6.5 | 0 | 0 | 186.7 | 166.9 | 161.1 | 156.4 | 179.2 | 33.6 | 19.8 | 51.1 | 10.4 | 240.4 | 5.7 | 169.5 | 61.5 | 60.4 | 104.1 | 199.8 | 533 | 214.9 | 119.4 | 311 | 293.1 | 200.5 | 221.5 | 235 | 211.7 | 185.8 | 169.7 | 228.9 | 201.6 | 309.2 | 253.1
2570.4 | 2351.4 | -6.6 | 0 | 0 | 186.6 | 166.8 | 161 | 156.4 | 179.1 | 33.7 | 19.8 | 51 | 11.1 | 228.5 | 6.1 | 169 | 61.1 | 60.4 | 103.6 | 199.2 | 532.7 | 214.7 | 118.5 | 308.8 | 293 | 200.6 | 221.5 | 234.9 | 211.6 | 185.7 | 169.5 | 228.9 | 201.4 | 308.9 | 253
2571.4 | 2352.4 | -6.6 | 0 | 0 | 186.3 | 166.7 | 161 | 156.5 | 179 | 33.8 | 19.8 | 51 | 9.5 | 245.6 | 5.9 | 168.6 | 60.8 | 60.2 | 103.2 | 198.6 | 532.4 | 214.7 | 117.7 | 308.4 | 292.5 | 200.6 | 221.4 | 234.8 | 211.6 | 185.8 | 169.4 | 228.9 | 201.3 | 308.6 | 252.8
2572.4 | 2353.4 | -6.7 | 0 | 0 | 185.8 | 166.7 | 161 | 156.4 | 178.9 | 33.8 | 19.8 | 50.9 | 7.5 | 276.5 | 5.3 | 168.1 | 60.8 | 60 | 102.6 | 197.9 | 532.1 | 214.7 | 117.4 | 309.1 | 291.8 | 200.6 | 221.4 | 234.6 | 211.5 | 185.8 | 169.3 | 228.9 | 201.1 | 308.3 | 252.7
2573.4 | 2354.4 | -6.8 | 0 | 0 | 185.9 | 166.5 | 160.8 | 156.1 | 178.7 | 33.9 | 19.8 | 50.9 | 7.6 | 238.7 | 7.5 | 167.6 | 61.4 | 59.8 | 101.8 | 197.3 | 531.7 | 214.8 | 117.4 | 309.8 | 291.3 | 200.7 | 221.3 | 234.5 | 211.5 | 185.6 | 169.2 | 228.9 | 201 | 308 | 252.6
2574.4 | 2355.4 | -6.8 | 0 | 0 | 185.9 | 166.3 | 160.6 | 155.6 | 178.5 | 33.9 | 19.8 | 50.9 | 9.3 | 241.4 | 14.2 | 167.1 | 61.7 | 59.6 | 101.2 | 196.6 | 531.3 | 214.4 | 117.3 | 310.5 | 291 | 200.8 | 221.3 | 234.4 | 211.4 | 185.4 | 169 | 228.9 | 200.8 | 307.8 | 252.4
2575.4 | 2356.4 | -6.8 | 0 | 0 | 185.3 | 166.3 | 160.8 | 155.4 | 178.3 | 33.9 | 19.8 | 50.8 | 9.1 | 236.8 | 14 | 166.7 | 61.3 | 59.8 | 101.1 | 196.1 | 531 | 213.9 | 117.1 | 310.9 | 290.4 | 200.8 | 221.3 | 234.3 | 211.3 | 185.3 | 168.9 | 228.8 | 200.6 | 307.4 | 252.3
2576.4 | 2357.4 | -6.8 | 0 | 0 | 185.4 | 166.1 | 160.5 | 154.9 | 178.1 | 33.9 | 19.8 | 50.8 | 9.8 | 245.2 | 10.2 | 166.2 | 61.5 | 59.7 | 101.4 | 195.7 | 530.5 | 213.9 | 117.2 | 310.1 | 289.9 | 200.9 | 221.2 | 234.2 | 211.3 | 185.1 | 168.8 | 228.8 | 200.4 | 307.2 | 252.2
2577.4 | 2358.4 | -6.5 | 0 | 0 | 185.2 | 166 | 160.5 | 155 | 177.9 | 33.9 | 19.8 | 50.8 | 9.6 | 213.6 | 10.1 | 165.8 | 61.6 | 59.5 | 101.7 | 195.2 | 530 | 213.9 | 117.4 | 310.1 | 289.9 | 200.9 | 221.2 | 234 | 211.2 | 185 | 168.6 | 228.8 | 200.2 | 306.9 | 252.1
2578.4 | 2359.4 | -6.4 | 0 | 0 | 184.3 | 166.2 | 160.7 | 155.1 | 177.7 | 33.9 | 19.8 | 50.7 | 9.6 | 211.3 | 11.8 | 165.5 | 61.2 | 59.5 | 101.9 | 194.6 | 529.6 | 213.5 | 117.6 | 310.2 | 289.6 | 201 | 221.1 | 233.9 | 211.2 | 184.7 | 168.5 | 228.8 | 200.1 | 306.5 | 251.9
2579.4 | 2360.4 | -6.3 | 0 | 0 | 184.9 | 165.9 | 160.2 | 154.5 | 177.7 | 33.8 | 19.8 | 50.6 | 9.4 | 234.9 | 9.6 | 165.1 | 61 | 59.4 | 101.6 | 194.1 | 529.3 | 213.1 | 117.9 | 309.5 | 289.4 | 201 | 221.1 | 233.8 | 211.1 | 184.4 | 168.4 | 228.8 | 199.9 | 306.4 | 251.8
2580.4 | 2361.4 | -6.4 | 0 | 0 | 184.7 | 165.8 | 160.1 | 154.3 | 177.6 | 33.8 | 19.8 | 50.6 | 9 | 252.4 | 9.8 | 164.5 | 60.8 | 59.2 | 101.5 | 193.6 | 529.1 | 213.2 | 118 | 308.3 | 289 | 201.1 | 221.1 | 233.7 | 211.1 | 184.2 | 168.3 | 228.7 | 199.7 | 306.1 | 251.7
2581.4 | 2362.4 | -6.4 | 0 | 0 | 184.3 | 165.8 | 160.1 | 154.4 | 177.7 | 33.7 | 19.8 | 50.5 | 9 | 247.7 | 10.5 | 164 | 60.9 | 59 | 101.3 | 193.1 | 528.8 | 213.2 | 118.3 | 308.1 | 288.8 | 201.1 | 221 | 233.6 | 211 | 183.9 | 168.1 | 228.7 | 199.6 | 305.7 | 251.5
2582.4 | 2363.4 | -6.5 | 0 | 0 | 184.1 | 165.7 | 160 | 154.3 | 177.9 | 33.7 | 19.8 | 50.4 | 8.1 | 226 | 10.2 | 163.5 | 60.6 | 59 | 100.9 | 192.6 | 528.6 | 212.8 | 118.2 | 306.9 | 288.4 | 201.2 | 221 | 233.5 | 210.9 | 183.6 | 168 | 228.7 | 199.4 | 305.5 | 251.4
2583.4 | 2364.4 | -6.5 | 0 | 0 | 184.4 | 165.5 | 159.6 | 153.9 | 177.7 | 33.6 | 19.9 | 50.3 | 7.4 | 219.9 | 11 | 163 | 60.2 | 58.9 | 100.7 | 192 | 528.4 | 212 | 117.8 | 306.5 | 288.1 | 201.2 | 220.9 | 233.3 | 210.9 | 183.4 | 167.9 | 228.7 | 199.2 | 305.3 | 251.3
2584.4 | 2365.4 | -6.5 | 0 | 0 | 184.4 | 165.4 | 159.4 | 153.6 | 177.4 | 33.5 | 19.9 | 50.2 | 8.3 | 245.5 | 12.8 | 162.5 | 60.2 | 58.6 | 100.5 | 191.4 | 528 | 211.9 | 116.9 | 307.3 | 287.8 | 201.2 | 220.9 | 233.2 | 210.8 | 183.3 | 167.8 | 228.7 | 199 | 305 | 251.1
2585.4 | 2366.4 | -6.5 | 0 | 0 | 184 | 165.4 | 159.5 | 153.5 | 177.2 | 33.5 | 19.9 | 50.2 | 7.7 | 242.7 | 15.6 | 161.9 | 60 | 58.4 | 100 | 190.8 | 527.7 | 211.8 | 116.5 | 306.3 | 287.3 | 201.3 | 220.9 | 233.1 | 210.8 | 183.2 | 167.7 | 228.6 | 198.9 | 304.7 | 251
2586.4 | 2367.4 | -6.5 | 0 | 0 | 183.8 | 165.3 | 159.4 | 153.6 | 177.2 | 33.5 | 19.9 | 50.1 | 7.6 | 248.4 | 14.6 | 161.4 | 59.7 | 58.2 | 99.8 | 190.3 | 527.4 | 211.3 | 116.3 | 306.3 | 286.7 | 201.3 | 220.8 | 233 | 210.7 | 183.1 | 167.6 | 228.6 | 198.7 | 304.3 | 250.8
2587.4 | 2368.4 | -6.5 | 0 | 0 | 183.7 | 165.1 | 159.3 | 153.5 | 177.1 | 33.4 | 19.9 | 50 | 8.7 | 262.7 | 12.5 | 160.9 | 59.7 | 58.2 | 100.1 | 189.8 | 527.1 | 211 | 116.2 | 306.1 | 286.2 | 201.4 | 220.8 | 232.9 | 210.6 | 183 | 167.4 | 228.6 | 198.6 | 304.1 | 250.7
2588.4 | 2369.4 | -6.7 | 0 | 0 | 183.6 | 164.9 | 159.2 | 153.4 | 176.8 | 33.4 | 19.9 | 49.9 | 8.5 | 270 | 12.6 | 160.3 | 59.9 | 58.1 | 100.6 | 189.4 | 526.7 | 210.9 | 116.2 | 305.8 | 285.5 | 201.4 | 220.8 | 232.8 | 210.6 | 183 | 167.3 | 228.6 | 198.4 | 303.8 | 250.6
2589.4 | 2370.4 | -6.8 | 0 | 0 | 183.4 | 164.8 | 159 | 153.5 | 176.7 | 33.4 | 19.9 | 49.9 | 7.7 | 261.8 | 12.3 | 159.9 | 59.6 | 57.9 | 100.9 | 188.9 | 526.4 | 210.8 | 116.3 | 305.2 | 285.2 | 201.5 | 220.7 | 232.6 | 210.5 | 183 | 167.2 | 228.6 | 198.2 | 303.5 | 250.5
2590.4 | 2371.4 | -6.7 | 0 | 0 | 183.5 | 164.5 | 158.9 | 153.3 | 176.8 | 33.4 | 19.9 | 49.8 | 8.1 | 258.6 | 12 | 159.5 | 59.3 | 57.9 | 101.1 | 188.4 | 526.1 | 210.5 | 116.4 | 305.8 | 284.9 | 201.5 | 220.7 | 232.5 | 210.5 | 182.7 | 167.1 | 228.5 | 198 | 303.3 | 250.3
2591.4 | 2372.4 | -6.7 | 0 | 0 | 183.4 | 164.3 | 158.7 | 153.1 | 176.8 | 33.4 | 19.9 | 49.7 | 8.3 | 245.8 | 13.8 | 158.9 | 59.3 | 57.8 | 101.1 | 188 | 525.8 | 210.3 | 116.5 | 305.4 | 284.7 | 201.6 | 220.6 | 232.4 | 210.4 | 182.5 | 167 | 228.5 | 197.9 | 303 | 250.2
2592.4 | 2373.4 | -6.6 | 0 | 0 | 183 | 164.3 | 158.5 | 153.1 | 176.4 | 33.4 | 19.9 | 49.7 | 8.7 | 236.5 | 14.1 | 158.3 | 59.3 | 57.7 | 100.8 | 187.4 | 525.4 | 209.9 | 116.6 | 306 | 284.4 | 201.6 | 220.6 | 232.3 | 210.4 | 182.2 | 166.8 | 228.5 | 197.7 | 302.7 | 250.1
2593.4 | 2374.4 | -6.6 | 0 | 0 | 183 | 164.1 | 158.2 | 152.9 | 176.2 | 33.4 | 19.9 | 49.7 | 9.9 | 249.9 | 14.2 | 158 | 59.2 | 57.8 | 100.5 | 186.9 | 525 | 209.4 | 116.2 | 306.6 | 283.8 | 201.7 | 220.6 | 232.2 | 210.3 | 182 | 166.7 | 228.5 | 197.5 | 302.4 | 250
2594.4 | 2375.4 | -6.6 | 0 | 0 | 182.9 | 163.9 | 158.1 | 152.8 | 176.2 | 33.4 | 19.9 | 49.6 | 10.4 | 234.7 | 14.2 | 157.6 | 59.8 | 57.6 | 100.4 | 186.4 | 524.7 | 209.1 | 115.8 | 305.7 | 283 | 201.7 | 220.5 | 232.1 | 210.3 | 181.7 | 166.6 | 228.4 | 197.4 | 302.2 | 249.8
2595.4 | 2376.4 | -6.5 | 0 | 0 | 182.6 | 163.9 | 158 | 152.9 | 176.3 | 33.4 | 19.9 | 49.6 | 9.9 | 248.3 | 13.8 | 157.1 | 60.5 | 57.4 | 100.5 | 185.9 | 524.3 | 209.1 | 115.7 | 304 | 282.4 | 201.8 | 220.5 | 231.9 | 210.2 | 181.6 | 166.6 | 228.4 | 197.2 | 301.9 | 249.7
2596.4 | 2377.4 | -6.6 | 0 | 0 | 182 | 163.9 | 158.1 | 152.9 | 176.4 | 33.4 | 19.9 | 49.5 | 9.8 | 256.4 | 12.9 | 156.6 | 60.3 | 57.3 | 100.2 | 185.3 | 524 | 208.6 | 114.5 | 302.4 | 282.1 | 201.8 | 220.5 | 231.8 | 210.1 | 181.3 | 166.4 | 228.4 | 197.1 | 301.5 | 249.5
2597.4 | 2378.4 | -6.5 | 0 | 0 | 182.1 | 163.7 | 157.8 | 152.7 | 176.2 | 33.3 | 19.9 | 49.4 | 9 | 236.8 | 14.4 | 156.1 | 59.8 | 57.3 | 100.2 | 184.7 | 523.7 | 208.5 | 114.1 | 300.7 | 281.6 | 201.9 | 220.4 | 231.7 | 210.1 | 181.3 | 166.2 | 228.4 | 196.9 | 301.4 | 249.4
2598.4 | 2379.4 | -6.5 | 0 | 0 | 181.9 | 163.7 | 157.7 | 152.8 | 176 | 33.2 | 19.9 | 49.3 | 8.7 | 236.4 | 15.5 | 155.7 | 59.6 | 57.2 | 99.8 | 184.2 | 523.3 | 208.4 | 113.4 | 300.1 | 281.2 | 201.9 | 220.4 | 231.6 | 210 | 181.1 | 166.1 | 228.4 | 196.7 | 301 | 249.3
2599.4 | 2380.4 | -6.5 | 0 | 0 | 181.2 | 163.8 | 157.9 | 152.9 | 175.9 | 33.2 | 19.9 | 49.4 | 8.4 | 236.3 | 16.3 | 155.4 | 59.2 | 57.2 | 99.1 | 183.5 | 522.8 | 207.9 | 112.8 | 299 | 280.7 | 202 | 220.3 | 231.5 | 210 | 181 | 165.9 | 228.3 | 196.6 | 300.7 | 249.1
2600.4 | 2381.4 | -6.5 | 0 | 0 | 181.6 | 163.4 | 157.6 | 152.6 | 175.9 | 33.2 | 19.9 | 49.3 | 8.6 | 250.8 | 15.4 | 155 | 59 | 56.9 | 98.9 | 183 | 522.3 | 207.1 | 112.1 | 298.9 | 279.7 | 202 | 220.3 | 231.4 | 209.9 | 181 | 165.8 | 228.3 | 196.4 | 300.5 | 249
2601.4 | 2382.4 | -6.6 | 0 | 0 | 181.7 | 163.2 | 157.4 | 152.3 | 175.8 | 33.1 | 19.9 | 49.2 | 8.8 | 240.7 | 13.1 | 154.7 | 58.7 | 56.7 | 98.2 | 182.4 | 521.8 | 207.2 | 111.5 | 299.4 | 279.4 | 202 | 220.3 | 231.2 | 209.8 | 181.1 | 165.6 | 228.3 | 196.2 | 300.3 | 248.9
2602.4 | 2383.4 | -6.6 | 0 | 0 | 181.4 | 163.1 | 157.3 | 152.4 | 175.8 | 33 | 19.9 | 49.1 | 7.6 | 234.5 | 11.5 | 154.2 | 58.3 | 56.7 | 97.8 | 182 | 521.5 | 207.3 | 111.4 | 299.9 | 278.6 | 202.1 | 220.2 | 231.1 | 209.8 | 180.9 | 165.5 | 228.3 | 196.1 | 300 | 248.8
2603.4 | 2384.4 | -6.4 | 0 | 0 | 181.1 | 163 | 157.2 | 152.5 | 175.7 | 33 | 19.9 | 49 | 7.4 | 239 | 10.9 | 153.9 | 58.3 | 56.7 | 97.4 | 181.5 | 521.1 | 207.1 | 111.6 | 300 | 278.4 | 202.1 | 220.2 | 231 | 209.7 | 180.6 | 165.3 | 228.3 | 195.9 | 299.7 | 248.6
2604.4 | 2385.4 | -6.4 | 0 | 0 | 181.2 | 162.8 | 156.9 | 152.4 | 175.8 | 33 | 19.9 | 49 | 7.9 | 236.5 | 10.8 | 153.4 | 58.4 | 56.5 | 97.1 | 181.2 | 520.8 | 206.5 | 111.6 | 300.3 | 278.3 | 202.2 | 220.1 | 230.9 | 209.7 | 180.3 | 165.2 | 228.2 | 195.8 | 299.5 | 248.5
2605.4 | 2386.4 | -6.4 | 0 | 0 | 181 | 162.7 | 156.9 | 152.4 | 175.9 | 32.9 | 19.9 | 49 | 8.3 | 239.4 | 11.3 | 153 | 58.1 | 56.4 | 97.1 | 180.7 | 520.6 | 206.1 | 111.3 | 300.4 | 278.3 | 202.2 | 220.1 | 230.8 | 209.6 | 180 | 165.1 | 228.2 | 195.6 | 299.2 | 248.4
2606.4 | 2387.4 | -6.4 | 0 | 0 | 180.6 | 162.6 | 156.9 | 152.4 | 175.9 | 32.9 | 19.9 | 48.9 | 8.1 | 250.7 | 11.7 | 152.7 | 58 | 56.3 | 97.3 | 180.3 | 520.4 | 206 | 111.5 | 299.9 | 278 | 202.3 | 220.1 | 230.7 | 209.5 | 180 | 165 | 228.2 | 195.5 | 298.9 | 248.2
2607.4 | 2388.4 | -6.4 | 0 | 0 | 180.6 | 162.4 | 156.7 | 152.1 | 175.7 | 32.8 | 19.9 | 48.9 | 7.7 | 247.7 | 12.3 | 152.5 | 57.9 | 56.2 | 97.5 | 179.9 | 520.1 | 205.7 | 111.7 | 300.2 | 277.5 | 202.3 | 220 | 230.6 | 209.5 | 179.8 | 164.9 | 228.1 | 195.3 | 298.7 | 248.1
2608.4 | 2389.4 | -6.4 | 0 | 0 | 180.6 | 162.1 | 156.3 | 151.8 | 175.3 | 32.8 | 19.9 | 48.8 | 7.5 | 250.1 | 13 | 152.2 | 58.1 | 56 | 97.7 | 179.4 | 519.8 | 205.4 | 111.8 | 299.7 | 277.2 | 202.4 | 220 | 230.4 | 209.4 | 179.5 | 164.8 | 228.1 | 195.1 | 298.4 | 248
2609.4 | 2390.4 | -6.4 | 0 | 0 | 180.4 | 162.1 | 156.1 | 151.9 | 175 | 32.8 | 20 | 48.7 | 6.9 | 256.5 | 12.5 | 152 | 58 | 55.9 | 97.9 | 179 | 519.6 | 205.3 | 112 | 299.5 | 277.1 | 202.4 | 220 | 230.3 | 209.4 | 179.3 | 164.6 | 228.1 | 195 | 298.1 | 247.9
2610.4 | 2391.4 | -6.5 | 0 | 0 | 180.2 | 162 | 156 | 151.8 | 174.8 | 32.8 | 20 | 48.6 | 6.3 | 262.1 | 11.8 | 151.7 | 57.8 | 55.8 | 97.7 | 178.5 | 519.3 | 204.6 | 112.2 | 299.8 | 276.9 | 202.4 | 219.9 | 230.2 | 209.3 | 179.1 | 164.4 | 228.1 | 194.8 | 297.8 | 247.7
2611.4 | 2392.4 | -6.5 | 0 | 0 | 180.4 | 161.8 | 155.8 | 151.3 | 174.9 | 32.7 | 20 | 48.6 | 6.7 | 252.6 | 10.7 | 151.4 | 57.7 | 55.8 | 97.1 | 178 | 519 | 203.7 | 112.2 | 300.1 | 276.6 | 202.5 | 219.9 | 230.1 | 209.2 | 178.9 | 164.2 | 228 | 194.6 | 297.6 | 247.6
2612.4 | 2393.4 | -6.5 | 0 | 0 | 180.1 | 161.7 | 155.8 | 150.9 | 175.1 | 32.7 | 20 | 48.6 | 8 | 242.1 | 10.5 | 151.1 | 57.4 | 55.8 | 96.2 | 177.3 | 518.6 | 203.9 | 112.2 | 300.1 | 276.3 | 202.5 | 219.8 | 230 | 209.2 | 178.8 | 164.1 | 228 | 194.5 | 297.3 | 247.5
2613.4 | 2394.4 | -6.5 | 0 | 0 | 179.6 | 161.7 | 155.9 | 150.9 | 175.2 | 32.7 | 20 | 48.6 | 7.5 | 254.6 | 10.5 | 150.7 | 57.2 | 55.6 | 95.4 | 176.8 | 518.3 | 204 | 112.1 | 299.5 | 276.1 | 202.6 | 219.8 | 229.9 | 209.1 | 178.7 | 164 | 228 | 194.3 | 297.1 | 247.3
2614.4 | 2395.4 | -6.6 | 0 | 0 | 179.5 | 161.5 | 155.6 | 150.6 | 175.2 | 32.7 | 20 | 48.6 | 7.1 | 251.8 | 10.9 | 150.2 | 57.1 | 55.5 | 94.5 | 176.4 | 518 | 203.7 | 111.8 | 296.8 | 275.2 | 202.6 | 219.8 | 229.8 | 209.1 | 178.7 | 163.8 | 228 | 194.2 | 296.8 | 247.2
2615.4 | 2396.4 | -6.6 | 0 | 0 | 179.4 | 161.4 | 155.5 | 150.4 | 175 | 32.7 | 20 | 48.5 | 7.3 | 228.1 | 10.8 | 149.8 | 56.8 | 55.5 | 94 | 175.9 | 517.6 | 203.1 | 111.1 | 296.9 | 274.9 | 202.6 | 219.7 | 229.7 | 209 | 178.5 | 163.7 | 228 | 194 | 296.6 | 247.1
2616.4 | 2397.4 | -6.6 | 0 | 0 | 179.1 | 161.4 | 155.6 | 150.2 | 174.7 | 32.7 | 20 | 48.5 | 7.4 | 237.2 | 11 | 149.5 | 56.7 | 55.3 | 94 | 175.4 | 517.3 | 202.2 | 110.3 | 295.6 | 274.6 | 202.7 | 219.7 | 229.5 | 209 | 178.2 | 163.5 | 227.9 | 193.8 | 296.3 | 247
2617.4 | 2398.4 | -6.5 | 0 | 0 | 178.8 | 161.3 | 155.6 | 149.9 | 174.5 | 32.7 | 20 | 48.5 | 7.2 | 255.4 | 9.7 | 149.3 | 56.8 | 54.9 | 94.4 | 174.8 | 517.2 | 201.4 | 109.7 | 294.5 | 274.2 | 202.7 | 219.7 | 229.4 | 208.9 | 178 | 163.4 | 227.9 | 193.7 | 296 | 246.8
2618.4 | 2399.4 | -6.5 | 0 | 0 | 179 | 161 | 155.4 | 149.6 | 174.4 | 32.7 | 20 | 48.5 | 8.2 | 280.5 | 8.6 | 148.9 | 56.7 | 54.7 | 94.6 | 174.4 | 517 | 201.5 | 109.1 | 294.6 | 273.9 | 202.8 | 219.6 | 229.3 | 208.8 | 177.8 | 163.3 | 227.9 | 193.6 | 295.8 | 246.7
2619.4 | 2400.4 | -6.4 | 0 | 0 | 178.9 | 160.8 | 155.2 | 149.3 | 174.5 | 32.6 | 20 | 48.4 | 7.7 | 255.2 | 11.9 | 148.6 | 56.4 | 54.7 | 94.5 | 173.9 | 516.7 | 201.4 | 108.7 | 294.6 | 273.6 | 202.8 | 219.6 | 229.2 | 208.8 | 177.7 | 163.2 | 227.8 | 193.4 | 295.5 | 246.6
2620.4 | 2401.4 | -6.4 | 0 | 0 | 178.6 | 160.6 | 155.3 | 149 | 174.6 | 32.5 | 20 | 48.4 | 7.5 | 252.3 | 12.6 | 148.2 | 56.1 | 54.5 | 94.1 | 173.4 | 516.4 | 200.7 | 108.8 | 294.5 | 273.4 | 202.9 | 219.5 | 229.1 | 208.7 | 177.5 | 163.1 | 227.8 | 193.2 | 295.3 | 246.4
2621.4 | 2402.4 | -6.4 | 0 | 0 | 178.2 | 160.6 | 155.4 | 148.8 | 174.5 | 32.5 | 20 | 48.3 | 7.4 | 249.8 | 12.2 | 147.9 | 55.9 | 54.5 | 93.6 | 172.8 | 516.2 | 200.3 | 109 | 294.8 | 273 | 202.9 | 219.5 | 229 | 208.6 | 177.3 | 163 | 227.8 | 193.1 | 294.9 | 246.3
2622.4 | 2403.4 | -6.4 | 0 | 0 | 178.4 | 160.3 | 154.9 | 148.4 | 174.2 | 32.4 | 20 | 48.3 | 8.6 | 252.2 | 11.5 | 147.5 | 55.7 | 54.4 | 92.7 | 172.4 | 515.9 | 200 | 108.8 | 295.6 | 272.5 | 202.9 | 219.5 | 228.9 | 208.6 | 177 | 162.8 | 227.8 | 193 | 294.7 | 246.2
2623.4 | 2404.4 | -6.5 | 0 | 0 | 178.3 | 160.2 | 154.8 | 148.2 | 174 | 32.3 | 20 | 48.2 | 9.6 | 237.1 | 10.9 | 147.1 | 55.7 | 54.6 | 91.7 | 172.1 | 515.6 | 200.1 | 108.2 | 295.2 | 272.2 | 203 | 219.4 | 228.8 | 208.5 | 176.7 | 162.7 | 227.8 | 192.8 | 294.5 | 246
2624.4 | 2405.4 | -6.5 | 0 | 0 | 177.6 | 160.4 | 155.2 | 148.4 | 173.8 | 32.3 | 20 | 48.2 | 9.6 | 245.9 | 11.9 | 146.6 | 55.6 | 54.5 | 90.9 | 171.4 | 515.3 | 199.7 | 107.8 | 294.6 | 271.6 | 203 | 219.4 | 228.7 | 208.5 | 176.5 | 162.5 | 227.7 | 192.7 | 294.1 | 245.9
2625.4 | 2406.4 | -6.4 | 0 | 0 | 178 | 160.1 | 154.8 | 148 | 173.6 | 32.2 | 20 | 48.1 | 9.5 | 256.7 | 15.9 | 146.2 | 55.4 | 54.6 | 90.6 | 171 | 515.1 | 199.8 | 107.3 | 294.1 | 271 | 203.1 | 219.3 | 228.6 | 208.4 | 176.3 | 162.4 | 227.7 | 192.5 | 294 | 245.8
2626.4 | 2407.4 | -6.4 | 0 | 0 | 177.8 | 160.1 | 154.7 | 147.7 | 173.3 | 32.2 | 20 | 48 | 8.2 | 249 | 19.5 | 145.8 | 55.4 | 54.5 | 90.3 | 170.5 | 514.7 | 199.5 | 106.3 | 292.4 | 270.4 | 203.1 | 219.3 | 228.5 | 208.3 | 176.1 | 162.2 | 227.7 | 192.3 | 293.7 | 245.7
2627.4 | 2408.4 | -6.4 | 0 | 0 | 177.4 | 160.1 | 154.6 | 147.8 | 173 | 32.2 | 20 | 48 | 7.8 | 252.6 | 18.7 | 145.3 | 55.7 | 54.3 | 90 | 170 | 514.2 | 198.6 | 105.5 | 290.5 | 270.1 | 203.1 | 219.3 | 228.3 | 208.3 | 176.1 | 162.1 | 227.6 | 192.2 | 293.5 | 245.5
2628.4 | 2409.4 | -6.3 | 0 | 0 | 177.2 | 160 | 154.5 | 147.7 | 172.8 | 32.2 | 20 | 47.9 | 7.7 | 254.1 | 19.5 | 144.7 | 56.4 | 54 | 90 | 169.7 | 513.7 | 197.8 | 104.8 | 291.2 | 269.8 | 203.2 | 219.2 | 228.2 | 208.2 | 176.1 | 161.9 | 227.6 | 192 | 293.2 | 245.4
2629.4 | 2410.4 | -6.3 | 0 | 0 | 177.2 | 159.9 | 154.3 | 147.5 | 172.6 | 32.2 | 20 | 47.9 | 8.8 | 260.6 | 20.3 | 144.2 | 57.1 | 53.8 | 89.8 | 169.3 | 513.3 | 197.1 | 104.8 | 291.7 | 269.5 | 203.2 | 219.2 | 228.1 | 208.1 | 176.2 | 161.8 | 227.6 | 191.9 | 293 | 245.3
2630.4 | 2411.4 | -6.3 | 0 | 0 | 177 | 159.8 | 154.1 | 147.4 | 172.3 | 32.2 | 20 | 47.8 | 9.4 | 272.8 | 19.4 | 143.8 | 57.3 | 53.9 | 90 | 168.8 | 513 | 196.2 | 105.1 | 291.1 | 269.3 | 203.3 | 219.1 | 228 | 208.1 | 176.2 | 161.7 | 227.6 | 191.7 | 292.7 | 245.1
2631.4 | 2412.4 | -6.3 | 0 | 0 | 176.8 | 159.7 | 154 | 147.3 | 172.3 | 32.2 | 20 | 47.7 | 9.6 | 269.8 | 17.3 | 143.5 | 56.9 | 53.7 | 90.1 | 168.4 | 512.6 | 196.4 | 104.9 | 291 | 269.1 | 203.3 | 219.1 | 227.9 | 208 | 176.2 | 161.6 | 227.5 | 191.5 | 292.5 | 245
2632.4 | 2413.4 | -6.3 | 0 | 0 | 176.9 | 159.5 | 153.7 | 147.5 | 172.4 | 32.2 | 20 | 47.7 | 9.6 | 270.7 | 16.1 | 143.2 | 56.6 | 53.2 | 90.5 | 167.9 | 512.2 | 196.9 | 104.7 | 291.4 | 268.9 | 203.3 | 219.1 | 227.8 | 208 | 176.2 | 161.4 | 227.5 | 191.4 | 292.3 | 244.9
2633.4 | 2414.4 | -6.3 | 0 | 0 | 176.8 | 159.3 | 153.6 | 147.7 | 172.3 | 32.2 | 20 | 47.6 | 9.2 | 261.6 | 13.6 | 143 | 56.2 | 53 | 90.6 | 167.5 | 511.8 | 197.2 | 104.9 | 290.7 | 268.6 | 203.4 | 219 | 227.7 | 207.9 | 175.9 | 161.3 | 227.5 | 191.3 | 292 | 244.7
2634.4 | 2415.4 | -6.3 | 0 | 0 | 176.5 | 159.2 | 153.5 | 147.9 | 172.1 | 32.2 | 20 | 47.6 | 9.9 | 278.5 | 12.3 | 142.7 | 55.9 | 52.7 | 90.9 | 167.1 | 511.5 | 197.2 | 105.2 | 291.3 | 268.5 | 203.4 | 219 | 227.6 | 207.8 | 175.7 | 161.2 | 227.4 | 191.1 | 291.8 | 244.6
2635.4 | 2416.4 | -6.4 | 0 | 0 | 176.4 | 159 | 153.2 | 147.9 | 171.8 | 32.1 | 20 | 47.6 | 11.4 | 269.8 | 11.4 | 142.5 | 55.6 | 52.6 | 91.2 | 166.7 | 511.1 | 197.1 | 105.4 | 291.6 | 268.2 | 203.4 | 218.9 | 227.5 | 207.8 | 175.7 | 161.1 | 227.4 | 190.9 | 291.5 | 244.5
2636.4 | 2417.4 | -6.5 | 0 | 0 | 176.4 | 158.9 | 153 | 147.7 | 171.5 | 32 | 20 | 47.6 | 10.3 | 272.8 | 11.6 | 142.3 | 55.5 | 52.6 | 91.4 | 166.2 | 510.7 | 197.2 | 105.3 | 292 | 268 | 203.5 | 218.9 | 227.3 | 207.7 | 175.5 | 161.1 | 227.4 | 190.8 | 291.3 | 244.4
2637.4 | 2418.4 | -6.6 | 0 | 0 | 176.2 | 158.8 | 153 | 147.4 | 171.3 | 32 | 20 | 47.6 | 9.7 | 266.9 | 11 | 142.1 | 55.6 | 52.5 | 91.7 | 165.8 | 510.4 | 197.1 | 105.4 | 292.8 | 267.8 | 203.5 | 218.9 | 227.2 | 207.6 | 175.3 | 160.9 | 227.4 | 190.6 | 291 | 244.2
2638.4 | 2419.4 | -6.6 | 0 | 0 | 175.8 | 158.7 | 153 | 147.4 | 171.3 | 32 | 20 | 47.6 | 8.8 | 264.7 | 10.6 | 141.8 | 55.7 | 52.7 | 91.8 | 165.5 | 510.1 | 197.1 | 105.4 | 293.3 | 267.5 | 203.6 | 218.8 | 227.1 | 207.6 | 175.1 | 160.8 | 227.3 | 190.5 | 290.8 | 244.1
2639.4 | 2420.4 | -6.5 | 0 | 0 | 175.7 | 158.6 | 152.9 | 147.5 | 171.4 | 32 | 20.1 | 47.5 | 8.4 | 267.3 | 10.1 | 141.5 | 55.8 | 52.8 | 91.9 | 165.2 | 509.7 | 197.4 | 105.5 | 294 | 267.4 | 203.6 | 218.8 | 227 | 207.5 | 174.9 | 160.6 | 227.3 | 190.3 | 290.6 | 244
2640.4 | 2421.4 | -6.5 | 0 | 0 | 175.5 | 158.4 | 152.9 | 147.6 | 171.2 | 31.9 | 20 | 47.4 | 7.9 | 250.4 | 10.3 | 141.2 | 56 | 52.8 | 92 | 164.9 | 509.3 | 197.4 | 105.5 | 293.7 | 267.2 | 203.6 | 218.8 | 226.9 | 207.5 | 174.8 | 160.4 | 227.3 | 190.2 | 290.3 | 243.8
2641.4 | 2422.4 | -6.4 | 0 | 0 | 175.1 | 158.4 | 152.9 | 147.6 | 170.9 | 32 | 20 | 47.4 | 7.9 | 246.3 | 12.2 | 140.9 | 55.8 | 52.6 | 92 | 164.5 | 508.9 | 196.9 | 105.8 | 293.7 | 267 | 203.7 | 218.7 | 226.8 | 207.4 | 174.8 | 160.3 | 227.2 | 190 | 290.1 | 243.7
2642.4 | 2423.4 | -6.3 | 0 | 0 | 175 | 158.3 | 152.7 | 147.3 | 170.6 | 31.9 | 20.1 | 47.4 | 8.2 | 255.8 | 13 | 140.5 | 55.6 | 52.6 | 92 | 164.1 | 508.6 | 196.4 | 105.9 | 293.9 | 266.8 | 203.7 | 218.7 | 226.7 | 207.4 | 174.7 | 160.1 | 227.2 | 189.9 | 289.8 | 243.6
2643.4 | 2424.4 | -6.3 | 0 | 0 | 174.9 | 158.2 | 152.3 | 146.9 | 170.2 | 32 | 20 | 47.3 | 8.5 | 251.9 | 12.4 | 140.1 | 55.6 | 52.6 | 91.6 | 163.8 | 508.3 | 196.4 | 105.9 | 294.7 | 266.6 | 203.7 | 218.6 | 226.6 | 207.3 | 174.4 | 160 | 227.2 | 189.7 | 289.6 | 243.4
2644.4 | 2425.4 | -6.3 | 0 | 0 | 174.8 | 158.1 | 151.9 | 146.6 | 170.1 | 31.9 | 20.1 | 47.2 | 8.1 | 266.9 | 11.2 | 139.8 | 55.2 | 52.3 | 91.3 | 163.4 | 507.9 | 196.3 | 105.9 | 294.5 | 266.4 | 203.8 | 218.6 | 226.5 | 207.2 | 174.1 | 159.8 | 227.1 | 189.6 | 289.3 | 243.3
2645.4 | 2426.4 | -6.5 | 0 | 0 | 174.6 | 158.1 | 151.7 | 146.4 | 170 | 31.9 | 20.1 | 47.1 | 7.8 | 263.7 | 11.5 | 139.6 | 54.9 | 52.2 | 91.1 | 163.1 | 507.6 | 196.4 | 105.7 | 294.8 | 266.1 | 203.8 | 218.5 | 226.4 | 207.2 | 173.8 | 159.7 | 227.1 | 189.4 | 289.1 | 243.2
2646.4 | 2427.4 | -6.6 | 0 | 0 | 174.6 | 157.9 | 151.3 | 146.1 | 170 | 31.9 | 20.1 | 47 | 8.2 | 245.6 | 10.8 | 139.2 | 54.7 | 52.1 | 91.2 | 162.7 | 507.2 | 196.4 | 105.7 | 294.4 | 265.8 | 203.9 | 218.5 | 226.3 | 207.1 | 173.5 | 159.6 | 227.1 | 189.3 | 288.9 | 243
2647.4 | 2428.4 | -6.5 | 0 | 0 | 174.3 | 157.8 | 151.4 | 145.9 | 169.7 | 31.9 | 20.1 | 46.9 | 8.5 | 261.7 | 10.3 | 138.9 | 54.9 | 52.1 | 91.3 | 162.3 | 506.8 | 196 | 105.5 | 294.5 | 265.7 | 203.9 | 218.5 | 226.1 | 207 | 173.3 | 159.5 | 227 | 189.1 | 288.6 | 242.9
2648.4 | 2429.4 | -6.5 | 0 | 0 | 174.1 | 157.6 | 151.4 | 145.7 | 169.4 | 31.9 | 20.1 | 46.9 | 8 | 259.6 | 12.9 | 138.5 | 55 | 52 | 91.2 | 162.1 | 506.4 | 195.9 | 105.6 | 293.7 | 265.6 | 203.9 | 218.4 | 226 | 207 | 173.3 | 159.4 | 227 | 188.9 | 288.3 | 242.8
2649.4 | 2430.4 | -6.4 | 0 | 0 | 173.8 | 157.6 | 151.5 | 145.6 | 169.2 | 31.8 | 20.1 | 46.8 | 8.8 | 267.3 | 13.2 | 138.2 | 55.3 | 51.9 | 91.1 | 161.8 | 506.1 | 195.7 | 105.3 | 293.8 | 265.3 | 204 | 218.4 | 225.9 | 206.9 | 173.4 | 159.3 | 227 | 188.9 | 288.1 | 242.6
2650.4 | 2431.4 | -6.3 | 0 | 0 | 173.8 | 157.4 | 151.2 | 145.4 | 169 | 31.8 | 20.1 | 46.8 | 8.1 | 263.5 | 14 | 137.9 | 55.7 | 51.5 | 91.1 | 161.4 | 505.6 | 195.6 | 105.6 | 294 | 265 | 204 | 218.3 | 225.8 | 206.8 | 173.3 | 159.1 | 227 | 188.7 | 287.9 | 242.5
2651.4 | 2432.4 | -6.3 | 0 | 0 | 173.7 | 157.3 | 151.1 | 145.2 | 168.9 | 31.7 | 20.1 | 46.8 | 9 | 252.6 | 13.1 | 137.6 | 55.5 | 51.4 | 91.1 | 161 | 505.2 | 195.3 | 105.7 | 293.7 | 264.8 | 204 | 218.3 | 225.7 | 206.8 | 173 | 159 | 226.9 | 188.5 | 287.6 | 242.4
2652.4 | 2433.4 | -6.3 | 0 | 0 | 173.1 | 157.4 | 151.4 | 145.4 | 168.9 | 31.7 | 20.1 | 46.8 | 9.2 | 272.6 | 11.8 | 137.4 | 55.2 | 51.1 | 90.9 | 160.6 | 504.8 | 195 | 105.9 | 294.2 | 264.5 | 204.1 | 218.3 | 225.6 | 206.7 | 172.9 | 158.8 | 226.9 | 188.4 | 287.2 | 242.2
2653.4 | 2434.4 | -6.2 | 0 | 0 | 173.5 | 157.1 | 150.8 | 145.2 | 169.1 | 31.6 | 20.1 | 46.7 | 9.1 | 275.3 | 11.2 | 137.1 | 54.9 | 51 | 90.8 | 160.2 | 504.5 | 194.7 | 106.1 | 293.9 | 264.1 | 204.1 | 218.2 | 225.5 | 206.7 | 172.9 | 158.7 | 226.9 | 188.2 | 287.1 | 242.1
2654.4 | 2435.4 | -6.2 | 0 | 0 | 173.5 | 156.9 | 150.7 | 144.8 | 169 | 31.6 | 20.1 | 46.7 | 9 | 261.9 | 10.2 | 137 | 54.6 | 50.8 | 90.8 | 159.8 | 504.2 | 194.2 | 106.3 | 293.2 | 263.6 | 204.1 | 218.2 | 225.4 | 206.6 | 172.8 | 158.5 | 226.8 | 188.1 | 286.9 | 242
2655.4 | 2436.4 | -6.2 | 0 | 0 | 173 | 157 | 151 | 144.8 | 168.8 | 31.5 | 20.1 | 46.7 | 9 | 280.4 | 9.3 | 136.7 | 54.2 | 50.6 | 90.7 | 159.3 | 503.8 | 193.5 | 106.1 | 292.4 | 263.4 | 204.2 | 218.2 | 225.3 | 206.5 | 172.6 | 158.3 | 226.8 | 187.9 | 286.6 | 241.8
2656.4 | 2437.4 | -6.2 | 0 | 0 | 173.1 | 156.8 | 150.9 | 144.6 | 168.6 | 31.4 | 20.1 | 46.6 | 8.7 | 275.1 | 9.2 | 136.5 | 54.3 | 50.5 | 91 | 159 | 503.4 | 192.6 | 106.1 | 291.4 | 263 | 204.2 | 218.1 | 225.2 | 206.5 | 172.4 | 158.2 | 226.8 | 187.8 | 286.4 | 241.7
2657.4 | 2438.4 | -6.2 | 0 | 0 | 173.1 | 156.7 | 150.7 | 144.3 | 168.4 | 31.3 | 20.1 | 46.5 | 9 | 281.4 | 10 | 136.2 | 54 | 50.5 | 90.9 | 158.6 | 503 | 192.1 | 106.1 | 290.1 | 262.5 | 204.2 | 218.1 | 225.1 | 206.4 | 172.1 | 158.1 | 226.7 | 187.7 | 286.2 | 241.6
2658.4 | 2439.4 | -6.2 | 0 | 0 | 172.7 | 156.7 | 150.7 | 144.1 | 168.2 | 31.2 | 20.1 | 46.4 | 8.6 | 274.1 | 9.6 | 135.9 | 54 | 50.4 | 90.7 | 158.2 | 502.6 | 191.7 | 105.6 | 289.8 | 262.3 | 204.3 | 218 | 225 | 206.4 | 171.8 | 158 | 226.7 | 187.5 | 285.9 | 241.5
2659.4 | 2440.4 | -6.2 | 0 | 0 | 172.8 | 156.5 | 150.3 | 144 | 168.2 | 31.1 | 20.1 | 46.4 | 9.1 | 253.6 | 8.7 | 135.7 | 53.8 | 50.2 | 90.7 | 157.7 | 502.2 | 192.1 | 105 | 290.3 | 262 | 204.3 | 218 | 224.9 | 206.3 | 171.6 | 157.9 | 226.6 | 187.4 | 285.7 | 241.3
2660.4 | 2441.4 | -6.2 | 0 | 0 | 172.6 | 156.4 | 150 | 143.9 | 168.2 | 31.1 | 20.1 | 46.4 | 8.1 | 267.9 | 8 | 135.5 | 53.3 | 49.9 | 90.9 | 157.2 | 501.8 | 191.7 | 104.5 | 290.9 | 261.8 | 204.3 | 218 | 224.8 | 206.2 | 171.3 | 157.7 | 226.6 | 187.2 | 285.5 | 241.2
2661.4 | 2442.4 | -6.2 | 0 | 0 | 172.4 | 156.4 | 149.9 | 143.8 | 168.1 | 31 | 20.1 | 46.4 | 8.6 | 235.6 | 8.3 | 135.3 | 53 | 49.6 | 91.3 | 156.8 | 501.4 | 191.3 | 104.4 | 291 | 261.4 | 204.4 | 217.9 | 224.6 | 206.2 | 171.1 | 157.6 | 226.6 | 187.1 | 285.3 | 241.1
2662.4 | 2443.4 | -6.2 | 0 | 0 | 172 | 156.4 | 150 | 143.7 | 168.1 | 31 | 20.1 | 46.3 | 8.1 | 257.4 | 9.6 | 135.1 | 52.8 | 49.4 | 91.2 | 156.4 | 501 | 191 | 104.1 | 290.3 | 260.8 | 204.4 | 217.9 | 224.5 | 206.1 | 170.9 | 157.5 | 226.5 | 186.9 | 285 | 240.9
2663.4 | 2444.4 | -6.2 | 0 | 0 | 172 | 156.3 | 149.8 | 143.4 | 168 | 31 | 20.1 | 46.3 | 9.2 | 265.6 | 10.6 | 134.9 | 52.6 | 49.2 | 91 | 156 | 500.5 | 190.9 | 103.6 | 289.7 | 260.5 | 204.4 | 217.9 | 224.4 | 206 | 170.7 | 157.4 | 226.5 | 186.8 | 284.8 | 240.8
2664.4 | 2445.4 | -6.2 | 0 | 0 | 171.9 | 156.1 | 149.5 | 143.2 | 167.7 | 31.1 | 20.1 | 46.2 | 8.7 | 264.6 | 11.7 | 134.6 | 52.3 | 48.8 | 90.6 | 155.6 | 500.1 | 191 | 103.4 | 289.6 | 260.3 | 204.5 | 217.8 | 224.3 | 206 | 170.6 | 157.2 | 226.5 | 186.6 | 284.5 | 240.7
2665.4 | 2446.4 | -6.2 | 0 | 0 | 171.6 | 156 | 149.5 | 143.1 | 167.6 | 31.2 | 20.1 | 46.2 | 7.9 | 259 | 13 | 134.3 | 52 | 48.5 | 90.1 | 155.3 | 499.8 | 191.3 | 103 | 289.5 | 260.1 | 204.5 | 217.8 | 224.2 | 205.9 | 170.6 | 157.1 | 226.4 | 186.5 | 284.3 | 240.5
2666.4 | 2447.4 | -6.2 | 0 | 0 | 171.2 | 155.9 | 149.6 | 143 | 167.6 | 31.3 | 20.1 | 46.2 | 8 | 257.7 | 12.9 | 134.1 | 51.6 | 48.3 | 89.7 | 154.9 | 499.4 | 191.5 | 102.3 | 288.9 | 259.7 | 204.5 | 217.8 | 224.1 | 205.8 | 170.5 | 156.9 | 226.4 | 186.4 | 284 | 240.4
2667.4 | 2448.4 | -6.2 | 0 | 0 | 171.4 | 155.7 | 149.5 | 142.8 | 167.7 | 31.4 | 20.1 | 46.1 | 7.9 | 262.3 | 11.7 | 133.8 | 51.3 | 47.9 | 89.4 | 154.5 | 499 | 191.3 | 101.6 | 287.9 | 259.3 | 204.6 | 217.7 | 224 | 205.8 | 170.3 | 156.8 | 226.3 | 186.2 | 283.9 | 240.3
2668.4 | 2449.4 | -6.2 | 0 | 0 | 171.3 | 155.5 | 149.6 | 142.7 | 167.7 | 31.4 | 20.1 | 46 | 8 | 268.7 | 11.8 | 133.4 | 51.3 | 47.9 | 89.2 | 154.2 | 498.7 | 190.4 | 101.1 | 287.7 | 259 | 204.6 | 217.7 | 223.9 | 205.7 | 170.2 | 156.7 | 226.3 | 186.1 | 283.6 | 240.2
2669.4 | 2450.4 | -6.2 | 0 | 0 | 171 | 155.4 | 149.6 | 142.6 | 167.6 | 31.5 | 20.1 | 45.9 | 8.2 | 265.1 | 10.5 | 133.1 | 51.3 | 47.7 | 88.9 | 153.8 | 498.3 | 189.7 | 100.9 | 288.3 | 258.7 | 204.6 | 217.7 | 223.8 | 205.7 | 170.1 | 156.6 | 226.2 | 185.9 | 283.3 | 240