## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Test Facts
Last row in IRMS data sheets: | 166
Time when Penlight power was initiated: | 50 s

## Shorting Summary
Shorting Sequence for Penlight Test 2
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, XLPE insulated, Hypalon jacketed, CAROLFIRE Cable Item #14 Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.7 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 50 seconds of baseline data monitoring. Special Note: This test is identical to Penlight Test 3. Penlight test 1 is also similar except that Test 1 was rung at 475C and tests 2 and 3 were run at 470C.
DAQ Time | Penlight Time | Event | Interpretation
50 | 0 | Initiate Penlight Heating
914 | 864 | Conductor 2 shorts to Drain wire at less than 1000 ohms (121) | First short circuit inditations are between conductor 2 and the un-insulated drain wire
922 | 872 | Conductor 2 shows momentary short to external ground at less than 1000 ohms (820) | In this case, there is some indication of early interactions between one insulated conductor and ground.
922-925 (next cycle) | 872-875 (next cycle) | Conductor 1 shorts to drain wire at less than 1000 ohms AND C2-Drain short drops below 100 ohms. | Intra-cable shorting occurs between conductors and un-insulated drain wire eventually forming a single common intra-cable shorting group.
943 | 893 | C1-Drain short drops below 100 ohms, then recovers somewhat.
960 | 910 | Conductor 3 shorts to drain wire at less than 1000 ohms.
965 | 915 | Conductor 2 again shows momentary short to external ground at less than 1000 ohms (302) | Intermittent shorts to external ground are again observed followed shortly by more persistent external ground shorts, all within one minute of the first indications of serious degradation (at 914s).
968 | 918 | Drain wire shows momentary short to external ground at less than 1000 ohms (921)
984 - 1010 | 934 - 960 | All conductors begin to show persistent shorts to external ground at less than 1000 ohms.
1030 - 1139 | 980 - 1089 | Various conductors and drain show intermittent drop in resistance to external ground below 100 ohms, then recover back to 100-1000 ohms resistances.
1160 - 1172 | 1110 - 1122 | All conductors and drain show persistent shorts to external ground at less than 100. | All conductors have shorted to external ground at less than 100 ohms.
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | This test followed a somewhat more complex behavior than other tests involving the same cable. In this case there were earlier indications of shorts between one insulated conductor and ground, and the progression from initial faults to shorts to external ground progressed rather quickly.
Observation 3 | This test was a direct repeat of Penlight Test 3, and there is a great deal of consistency. The initial fault times are quite similar (729s for Test 2, versus 695s for Test 3 after start of heating). The initial shorting behavior and transitions are also very consistent between the two tests.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center

## PenTemps
DAQ Time | Penlight Time | Shroud Temp | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5
0 | -50 | 34.0696 | 30.904 | 30.5996 | 30.7759 | 29.0801 | 28.903
0.6309 | -49.3691 | 34.0686 | 30.9028 | 30.5975 | 30.7792 | 29.0752 | 28.8976
1.2418 | -48.7582 | 34.0553 | 30.9099 | 30.5977 | 30.7717 | 29.0651 | 28.8927
2.2232 | -47.7768 | 34.0544 | 30.8994 | 30.6006 | 30.7774 | 29.06 | 28.9
3.2246 | -46.7754 | 34.0471 | 30.8998 | 30.5956 | 30.7743 | 29.0712 | 28.8946
4.2161 | -45.7839 | 34.0448 | 30.8998 | 30.5987 | 30.774 | 29.0729 | 28.8992
5.2175 | -44.7825 | 34.0328 | 30.9011 | 30.5974 | 30.7777 | 29.0664 | 28.8992
6.2189 | -43.7811 | 34.0252 | 30.9002 | 30.5993 | 30.7778 | 29.0747 | 28.9006
7.2204 | -42.7796 | 34.0143 | 30.9072 | 30.5948 | 30.7739 | 29.0673 | 28.9041
8.2218 | -41.7782 | 34.0076 | 30.9032 | 30.6075 | 30.7747 | 29.0721 | 28.9027
9.2233 | -40.7767 | 33.9972 | 30.8995 | 30.6021 | 30.7738 | 29.0639 | 28.8976
10.2247 | -39.7753 | 33.9939 | 30.8991 | 30.6085 | 30.771 | 29.0766 | 28.903
11.2261 | -38.7739 | 33.9872 | 30.9007 | 30.6116 | 30.7745 | 29.071 | 28.9007
12.2276 | -37.7724 | 33.9837 | 30.8978 | 30.6005 | 30.7721 | 29.0681 | 28.9107
13.219 | -36.781 | 33.9796 | 30.9031 | 30.6055 | 30.7765 | 29.0732 | 28.913
14.2204 | -35.7796 | 33.9726 | 30.8989 | 30.6111 | 30.7769 | 29.0547 | 28.9047
15.2219 | -34.7781 | 33.9759 | 30.9003 | 30.6025 | 30.7722 | 29.0595 | 28.9047
16.2233 | -33.7767 | 33.9551 | 30.9016 | 30.6137 | 30.7731 | 29.0479 | 28.9131
17.2248 | -32.7752 | 33.9536 | 30.9046 | 30.6145 | 30.7728 | 29.0584 | 28.914
18.2162 | -31.7838 | 33.9515 | 30.9072 | 30.607 | 30.7831 | 29.0704 | 28.9185
19.2176 | -30.7824 | 33.9503 | 30.9005 | 30.6203 | 30.7752 | 29.062 | 28.9174
20.2191 | -29.7809 | 33.9387 | 30.9062 | 30.6152 | 30.7772 | 29.0654 | 28.9214
21.2205 | -28.7795 | 33.926 | 30.9012 | 30.614 | 30.7729 | 29.0609 | 28.9212
22.222 | -27.778 | 33.9189 | 30.9056 | 30.6103 | 30.7707 | 29.0568 | 28.9234
23.2234 | -26.7766 | 33.913 | 30.9036 | 30.6124 | 30.7798 | 29.0659 | 28.9311
24.2248 | -25.7752 | 33.9079 | 30.9047 | 30.6116 | 30.7802 | 29.066 | 28.9298
25.2263 | -24.7737 | 33.9042 | 30.9036 | 30.617 | 30.7727 | 29.075 | 28.9285
26.2177 | -23.7823 | 33.9015 | 30.908 | 30.6144 | 30.7757 | 29.0721 | 28.9265
27.2191 | -22.7809 | 33.8947 | 30.9033 | 30.6158 | 30.7804 | 29.0731 | 28.9294
28.2206 | -21.7794 | 33.8877 | 30.9071 | 30.6145 | 30.7814 | 29.0833 | 28.9381
29.222 | -20.778 | 33.8776 | 30.9079 | 30.607 | 30.7782 | 29.072 | 28.9359
30.2235 | -19.7765 | 33.8786 | 30.914 | 30.6126 | 30.7758 | 29.0849 | 28.9332
31.2249 | -18.7751 | 33.8719 | 30.9133 | 30.6086 | 30.7842 | 29.0828 | 28.9365
32.2163 | -17.7837 | 33.8673 | 30.9059 | 30.62 | 30.7851 | 29.0695 | 28.9331
33.2278 | -16.7722 | 33.8658 | 30.913 | 30.6189 | 30.7764 | 29.0785 | 28.9322
34.2192 | -15.7808 | 33.8599 | 30.9127 | 30.6238 | 30.7905 | 29.0715 | 28.9355
35.2206 | -14.7794 | 33.847 | 30.9118 | 30.6123 | 30.7743 | 29.0726 | 28.931
36.2221 | -13.7779 | 33.8425 | 30.9131 | 30.6162 | 30.7803 | 29.0777 | 28.9373
37.2235 | -12.7765 | 33.8363 | 30.9142 | 30.6239 | 30.784 | 29.0753 | 28.9309
38.225 | -11.775 | 33.8317 | 30.9154 | 30.6303 | 30.7845 | 29.0784 | 28.9354
39.2264 | -10.7736 | 33.8216 | 30.912 | 30.6262 | 30.7809 | 29.0846 | 28.9306
40.2178 | -9.7822 | 33.8143 | 30.9124 | 30.6221 | 30.7869 | 29.0862 | 28.9242
41.2193 | -8.7807 | 33.8066 | 30.9171 | 30.6219 | 30.7796 | 29.0799 | 28.9225
42.2207 | -7.7793 | 33.8045 | 30.9111 | 30.6255 | 30.7842 | 29.0861 | 28.9073
43.2222 | -6.7778 | 33.794 | 30.9116 | 30.6191 | 30.7854 | 29.0668 | 28.9099
44.2236 | -5.7764 | 33.7886 | 30.9144 | 30.6137 | 30.7856 | 29.0858 | 28.9
45.225 | -4.775 | 33.7784 | 30.9142 | 30.6187 | 30.7817 | 29.0711 | 28.8982
46.2165 | -3.7835 | 33.7683 | 30.9146 | 30.6292 | 30.787 | 29.0792 | 28.8925
47.2179 | -2.7821 | 33.7684 | 30.7251 | 30.6084 | 30.7006 | 29.1339 | 28.9335
48.2193 | -1.7807 | 33.7601 | 30.7674 | 30.6216 | 30.7192 | 29.1135 | 28.9182
49.2208 | -0.7792 | 33.7896 | 30.8316 | 30.6315 | 30.7472 | 29.0954 | 28.8999
50.2222 | 0.2222 | 34.143 | 30.8538 | 30.6331 | 30.7687 | 29.0852 | 28.8998
51.2237 | 1.2237 | 35.0297 | 30.8619 | 30.6339 | 30.7686 | 29.0843 | 28.9089
52.2251 | 2.2251 | 36.5035 | 30.8678 | 30.6371 | 30.777 | 29.0959 | 28.9161
53.2165 | 3.2165 | 38.5073 | 30.874 | 30.6429 | 30.7863 | 29.0976 | 28.9294
54.218 | 4.218 | 40.9646 | 30.8811 | 30.6225 | 30.7935 | 29.0925 | 28.9582
55.2194 | 5.2194 | 43.8001 | 30.8841 | 30.6384 | 30.8074 | 29.1138 | 28.9802
56.2208 | 6.2208 | 46.9635 | 30.8899 | 30.6482 | 30.8318 | 29.1361 | 29.0176
57.2223 | 7.2223 | 50.4281 | 30.9027 | 30.6387 | 30.8602 | 29.1513 | 29.0714
58.2237 | 8.2237 | 54.1148 | 30.9207 | 30.6558 | 30.8979 | 29.1846 | 29.1252
59.2252 | 9.2252 | 58.0541 | 30.9392 | 30.6388 | 30.9385 | 29.2272 | 29.1925
60.2266 | 10.2266 | 62.1607 | 30.9608 | 30.6437 | 31.0028 | 29.2655 | 29.267
61.218 | 11.218 | 66.4445 | 30.9837 | 30.6351 | 31.0593 | 29.319 | 29.3499
62.2195 | 12.2195 | 70.885 | 31.0187 | 30.6415 | 31.1301 | 29.3647 | 29.457
63.2209 | 13.2209 | 75.4204 | 31.0578 | 30.6402 | 31.2091 | 29.4412 | 29.5766
64.2223 | 14.2223 | 80.1259 | 31.0974 | 30.6422 | 31.3025 | 29.5265 | 29.7131
65.2238 | 15.2238 | 84.9622 | 31.1511 | 30.6494 | 31.4142 | 29.6101 | 29.869
66.2252 | 16.2252 | 89.9104 | 31.202 | 30.6639 | 31.5279 | 29.6946 | 30.0538
67.2167 | 17.2167 | 94.9443 | 31.2671 | 30.6553 | 31.6559 | 29.8151 | 30.2467
68.2181 | 18.2181 | 100.0348 | 31.3388 | 30.6502 | 31.8009 | 29.9318 | 30.447
69.2195 | 19.2195 | 105.2397 | 31.4188 | 30.6605 | 31.9531 | 30.065 | 30.6662
70.221 | 20.221 | 110.5433 | 31.5068 | 30.6616 | 32.1223 | 30.2274 | 30.9161
71.2224 | 21.2224 | 115.8781 | 31.6084 | 30.6657 | 32.3048 | 30.3801 | 31.1791
72.2239 | 22.2239 | 121.2894 | 31.7153 | 30.6675 | 32.5058 | 30.5557 | 31.4523
73.2253 | 23.2253 | 126.7763 | 31.8313 | 30.6883 | 32.7201 | 30.7464 | 31.7424
74.2267 | 24.2267 | 132.341 | 31.955 | 30.6909 | 32.958 | 30.9527 | 32.0647
75.2182 | 25.2182 | 137.9748 | 32.0851 | 30.6963 | 33.1995 | 31.15 | 32.3909
76.2196 | 26.2196 | 143.5631 | 32.2404 | 30.6975 | 33.4675 | 31.391 | 32.7465
77.221 | 27.221 | 149.0928 | 32.3914 | 30.7124 | 33.7426 | 31.6186 | 33.1208
78.2225 | 28.2225 | 154.6423 | 32.5587 | 30.704 | 34.0271 | 31.8835 | 33.506
79.2239 | 29.2239 | 160.1296 | 32.7401 | 30.7277 | 34.3383 | 32.1427 | 33.9052
80.2254 | 30.2254 | 165.6344 | 32.9281 | 30.7469 | 34.662 | 32.4183 | 34.3324
81.2168 | 31.2168 | 171.1408 | 33.138 | 30.7564 | 34.9942 | 32.7219 | 34.7869
82.2182 | 32.2182 | 176.7404 | 33.3485 | 30.7618 | 35.3528 | 33.0359 | 35.2634
83.2197 | 33.2197 | 182.3063 | 33.5898 | 30.7831 | 35.7214 | 33.3653 | 35.7552
84.2211 | 34.2211 | 187.7104 | 33.8355 | 30.8042 | 36.1218 | 33.7255 | 36.2824
85.2225 | 35.2225 | 193.1478 | 34.1004 | 30.8223 | 36.5339 | 34.0766 | 36.828
86.224 | 36.224 | 198.5347 | 34.3849 | 30.8448 | 36.9602 | 34.4768 | 37.3886
87.2254 | 37.2254 | 203.9905 | 34.6804 | 30.8847 | 37.4099 | 34.8743 | 37.9799
88.2269 | 38.2269 | 209.4572 | 34.9963 | 30.9 | 37.8762 | 35.2872 | 38.5891
89.2183 | 39.2183 | 214.8574 | 35.3277 | 30.9325 | 38.3656 | 35.7039 | 39.2123
90.2197 | 40.2197 | 220.2665 | 35.679 | 30.9792 | 38.8697 | 36.1514 | 39.8621
91.2212 | 41.2212 | 225.6869 | 36.0484 | 31.0142 | 39.4151 | 36.6024 | 40.5485
92.2226 | 42.2226 | 231.1409 | 36.4292 | 31.0477 | 39.9739 | 37.0943 | 41.2451
93.224 | 43.224 | 236.5736 | 36.8334 | 31.0852 | 40.5563 | 37.5851 | 41.9677
94.2255 | 44.2255 | 241.9793 | 37.2499 | 31.1365 | 41.1646 | 38.1334 | 42.7055
95.2169 | 45.2169 | 247.3324 | 37.694 | 31.1819 | 41.7964 | 38.6642 | 43.4563
96.2284 | 46.2284 | 252.7307 | 38.1489 | 31.237 | 42.4487 | 39.2315 | 44.2394
97.2198 | 47.2198 | 258.1954 | 38.6181 | 31.2914 | 43.1215 | 39.8123 | 45.0512
98.2212 | 48.2212 | 263.6742 | 39.1126 | 31.335 | 43.8254 | 40.4409 | 45.906
99.2227 | 49.2227 | 269.0271 | 39.6325 | 31.4059 | 44.5436 | 41.0734 | 46.7901
100.2241 | 50.2241 | 274.3944 | 40.1651 | 31.4789 | 45.2939 | 41.7196 | 47.692
101.2256 | 51.2256 | 279.7287 | 40.7144 | 31.543 | 46.0725 | 42.3911 | 48.6268
102.227 | 52.227 | 284.9693 | 41.2799 | 31.6265 | 46.8758 | 43.0579 | 49.5879
103.2184 | 53.2184 | 290.153 | 41.8565 | 31.6968 | 47.7119 | 43.7704 | 50.5685
104.2199 | 54.2199 | 295.4217 | 42.4583 | 31.7875 | 48.5679 | 44.5069 | 51.5814
105.2213 | 55.2213 | 300.7164 | 43.0706 | 31.8782 | 49.4469 | 45.245 | 52.6037
106.2227 | 56.2227 | 305.9583 | 43.7094 | 31.9736 | 50.3557 | 46.0094 | 53.6482
107.2242 | 57.2242 | 311.3157 | 44.3678 | 32.0712 | 51.2925 | 46.7988 | 54.7243
108.2256 | 58.2256 | 316.6279 | 45.0489 | 32.1741 | 52.2512 | 47.5993 | 55.8352
109.217 | 59.217 | 321.8808 | 45.7704 | 32.2858 | 53.2374 | 48.4266 | 56.9527
110.2185 | 60.2185 | 327.1072 | 46.5169 | 32.4026 | 54.2516 | 49.2848 | 58.1057
111.2199 | 61.2199 | 332.2613 | 47.285 | 32.5253 | 55.2917 | 50.1531 | 59.2944
112.2214 | 62.2214 | 337.47 | 48.0823 | 32.6405 | 56.3572 | 51.0657 | 60.5129
113.2228 | 63.2228 | 342.5744 | 48.8889 | 32.778 | 57.4642 | 51.9737 | 61.7772
114.2242 | 64.2242 | 347.5318 | 49.7308 | 32.9214 | 58.6021 | 52.9423 | 63.0644
115.2257 | 65.2257 | 352.63 | 50.5768 | 33.061 | 59.7625 | 53.9128 | 64.3741
116.2171 | 66.2171 | 357.6629 | 51.4365 | 33.2158 | 60.9446 | 54.9076 | 65.7049
117.2186 | 67.2186 | 362.6505 | 52.3202 | 33.3614 | 62.1486 | 55.9368 | 67.0593
118.22 | 68.22 | 367.7257 | 53.2334 | 33.5271 | 63.3804 | 56.9685 | 68.4732
119.2214 | 69.2214 | 372.7074 | 54.1597 | 33.7031 | 64.6219 | 58.0046 | 69.9222
120.2229 | 70.2229 | 377.6525 | 55.1239 | 33.8809 | 65.9023 | 59.0858 | 71.4083
121.2243 | 71.2243 | 382.5141 | 56.1013 | 34.0649 | 67.2268 | 60.1692 | 72.9086
122.2258 | 72.2258 | 387.3899 | 57.1281 | 34.2544 | 68.5698 | 61.3082 | 74.4194
123.2272 | 73.2272 | 392.2433 | 58.1993 | 34.4535 | 69.9447 | 62.471 | 75.9723
124.2186 | 74.2186 | 397.0979 | 59.3229 | 34.6585 | 71.3535 | 63.6423 | 77.5596
125.2201 | 75.2201 | 401.8902 | 60.4788 | 34.869 | 72.7951 | 64.8642 | 79.1611
126.2215 | 76.2215 | 406.6624 | 61.6706 | 35.0989 | 74.2488 | 66.116 | 80.7943
127.2229 | 77.2229 | 411.4633 | 62.9012 | 35.3276 | 75.7503 | 67.3696 | 82.4771
128.2244 | 78.2244 | 416.2318 | 64.1563 | 35.5728 | 77.2785 | 68.6827 | 84.1952
129.2158 | 79.2158 | 420.9305 | 65.4317 | 35.8076 | 78.8286 | 69.9942 | 85.9351
130.2172 | 80.2172 | 425.5581 | 66.7258 | 36.0613 | 80.408 | 71.3472 | 87.7249
131.2187 | 81.2187 | 430.0659 | 68.0445 | 36.3218 | 82.0041 | 72.7057 | 89.55
132.2201 | 82.2201 | 434.6488 | 69.2318 | 36.5896 | 83.5772 | 74.1408 | 91.4154
133.2216 | 83.2216 | 439.0661 | 70.6166 | 36.8639 | 85.2451 | 75.5604 | 93.2992
134.223 | 84.223 | 443.0893 | 71.983 | 37.1513 | 86.9333 | 77.0114 | 95.2194
135.2244 | 85.2244 | 446.849 | 73.4209 | 37.4319 | 88.6399 | 78.48 | 97.1692
136.2259 | 86.2259 | 450.3554 | 74.8778 | 37.7292 | 90.3755 | 79.9647 | 99.116
137.2173 | 87.2173 | 453.6479 | 76.3464 | 38.0483 | 92.1193 | 81.4382 | 101.1185
138.2187 | 88.2187 | 456.7976 | 77.8169 | 38.3834 | 93.8621 | 82.9433 | 103.1314
139.2202 | 89.2202 | 459.631 | 79.2899 | 38.6981 | 95.5969 | 84.4491 | 105.1579
140.2216 | 90.2216 | 462.326 | 80.779 | 39.0259 | 97.3558 | 85.9719 | 107.2114
141.2231 | 91.2231 | 464.967 | 82.2599 | 39.3798 | 99.0942 | 87.5051 | 109.272
142.2245 | 92.2245 | 467.5489 | 83.7442 | 39.7224 | 100.8374 | 89.0765 | 111.3466
143.2259 | 93.2259 | 469.9501 | 85.2562 | 40.0987 | 102.6031 | 90.6227 | 113.4539
144.2274 | 94.2274 | 472.349 | 86.7802 | 40.4758 | 104.3575 | 92.1943 | 115.5442
145.2188 | 95.2188 | 474.4331 | 88.3668 | 40.8614 | 106.1574 | 93.7263 | 117.5815
146.2203 | 96.2203 | 476.1619 | 89.8975 | 41.2488 | 107.9189 | 95.3038 | 119.6549
147.2217 | 97.2217 | 477.7827 | 91.4425 | 41.6537 | 109.6699 | 96.8818 | 121.7133
148.2231 | 98.2231 | 479.0436 | 92.9936 | 42.0638 | 111.4219 | 98.4557 | 123.7372
149.2246 | 99.2246 | 480.2205 | 94.5434 | 42.4698 | 113.1567 | 100.0317 | 125.7478
150.216 | 100.216 | 481.0595 | 96.1075 | 42.9005 | 114.8749 | 101.6127 | 127.7124
151.2174 | 101.2174 | 481.8352 | 97.6573 | 43.3457 | 116.5745 | 103.1839 | 129.6427
152.2189 | 102.2189 | 482.4085 | 99.2038 | 43.774 | 118.2178 | 104.7356 | 131.5307
153.2203 | 103.2203 | 482.7736 | 100.7391 | 44.2305 | 119.8454 | 106.2926 | 133.3791
154.2218 | 104.2218 | 482.9225 | 102.2754 | 44.6853 | 121.4464 | 107.8408 | 135.1879
155.2232 | 105.2232 | 482.9447 | 103.7926 | 45.1382 | 123.0163 | 109.3679 | 136.9563
156.2246 | 106.2246 | 482.9854 | 105.3038 | 45.6163 | 124.5655 | 110.8855 | 138.6982
157.2161 | 107.2161 | 482.9484 | 106.8077 | 46.0907 | 126.0757 | 112.3945 | 140.3996
158.2175 | 108.2175 | 482.6117 | 108.2976 | 46.568 | 127.5593 | 113.8922 | 142.052
159.2189 | 109.2189 | 482.3532 | 109.7769 | 47.0719 | 128.9972 | 115.3676 | 143.6667
160.2204 | 110.2204 | 481.8586 | 111.253 | 47.563 | 130.4081 | 116.8587 | 145.2717
161.2218 | 111.2218 | 481.2926 | 112.7031 | 48.0612 | 131.793 | 118.3291 | 146.8214
162.2233 | 112.2233 | 480.8484 | 114.1456 | 48.5706 | 133.1403 | 119.7846 | 148.3456
163.2247 | 113.2247 | 480.4789 | 115.5734 | 49.0992 | 134.4827 | 121.2395 | 149.8475
164.2261 | 114.2261 | 480.077 | 116.9903 | 49.6168 | 135.7811 | 122.6922 | 151.3182
165.2176 | 115.2176 | 479.5432 | 118.3908 | 50.1414 | 137.0451 | 124.1274 | 152.7562
166.219 | 116.219 | 479.0866 | 119.7904 | 50.6684 | 138.2942 | 125.5616 | 154.1764
167.2205 | 117.2205 | 478.5769 | 121.1618 | 51.2058 | 139.5254 | 126.9585 | 155.5612
168.2219 | 118.2219 | 478.1303 | 122.5228 | 51.7604 | 140.7376 | 128.3621 | 156.9457
169.2233 | 119.2233 | 477.9012 | 123.8769 | 52.2971 | 141.9284 | 129.7294 | 158.3236
170.2248 | 120.2248 | 477.7812 | 125.2292 | 52.8506 | 143.0886 | 131.0953 | 159.6824
171.2162 | 121.2162 | 477.4211 | 126.5697 | 53.4304 | 144.2485 | 132.4433 | 161.0177
172.2176 | 122.2176 | 476.9546 | 127.8747 | 53.9928 | 145.3784 | 133.7785 | 162.338
173.2191 | 123.2191 | 476.4722 | 129.1812 | 54.5702 | 146.4865 | 135.1121 | 163.6367
174.2205 | 124.2205 | 476.0932 | 130.4749 | 55.1496 | 147.5655 | 136.5988 | 164.9249
175.222 | 125.222 | 475.7903 | 131.7485 | 55.7319 | 148.638 | 139.2627 | 166.188
176.2234 | 126.2234 | 475.6798 | 133.0107 | 56.314 | 149.68 | 141.1013 | 167.4377
177.2248 | 127.2248 | 475.4355 | 134.2723 | 56.8976 | 150.6921 | 142.6404 | 168.6681
178.2163 | 128.2163 | 475.2587 | 135.5144 | 57.4919 | 151.6826 | 144.0526 | 169.8818
179.2177 | 129.2177 | 475.064 | 136.7484 | 58.0826 | 152.6612 | 145.4514 | 171.0666
180.2191 | 130.2191 | 475.042 | 137.9832 | 58.6832 | 153.6228 | 146.7504 | 172.2462
181.2206 | 131.2206 | 474.9733 | 139.2011 | 59.2881 | 154.5656 | 148.0231 | 173.4325
182.222 | 132.222 | 475.1002 | 140.4083 | 59.8933 | 155.489 | 149.2773 | 174.5962
183.2235 | 133.2235 | 475.2438 | 141.6129 | 60.4924 | 156.4107 | 150.4815 | 175.729
184.2249 | 134.2249 | 475.3973 | 142.8025 | 61.0983 | 157.3019 | 151.7015 | 176.8559
185.2263 | 135.2263 | 475.7437 | 143.9957 | 61.7082 | 158.2007 | 153.0262 | 177.9711
186.2278 | 136.2278 | 475.9131 | 145.171 | 62.2977 | 159.0815 | 154.2504 | 179.0809
187.2192 | 137.2192 | 476.1348 | 146.3372 | 62.9014 | 159.9563 | 155.4438 | 180.1851
188.2206 | 138.2206 | 476.2673 | 147.5088 | 63.5171 | 160.8229 | 156.7082 | 181.3076
189.2221 | 139.2221 | 476.2764 | 148.6831 | 64.1132 | 161.6915 | 157.9606 | 182.4111
190.2235 | 140.2235 | 476.2999 | 149.8385 | 64.7102 | 162.5403 | 159.3503 | 183.5272
191.225 | 141.225 | 476.438 | 150.9899 | 65.3169 | 163.3955 | 162.1848 | 184.6202
192.2164 | 142.2164 | 476.6616 | 152.1428 | 65.9175 | 164.233 | 164.4981 | 185.7249
193.2178 | 143.2178 | 476.9387 | 153.2875 | 66.516 | 165.0626 | 166.059 | 186.7967
194.2193 | 144.2193 | 476.979 | 154.4443 | 67.1162 | 165.8919 | 167.4599 | 187.847
195.2207 | 145.2207 | 477.0408 | 155.5889 | 67.6949 | 166.7229 | 168.6917 | 188.8995
196.2222 | 146.2222 | 477.0798 | 156.7262 | 68.3235 | 167.5461 | 169.8429 | 189.9428
197.2236 | 147.2236 | 477.3573 | 157.8643 | 68.9137 | 168.3597 | 170.9189 | 190.9985
198.225 | 148.225 | 477.4143 | 159.0115 | 69.5141 | 169.1565 | 172.0613 | 192.02
199.2165 | 149.2165 | 477.6523 | 160.132 | 70.1151 | 169.9348 | 173.0875 | 193.0409
200.2179 | 150.2179 | 477.7458 | 161.263 | 70.7105 | 170.7021 | 174.1567 | 194.0476
201.2193 | 151.2193 | 477.7977 | 162.3806 | 71.3083 | 171.4684 | 175.2277 | 195.0419
202.2208 | 152.2208 | 477.8836 | 163.507 | 71.9122 | 172.2468 | 176.2327 | 196.0552
203.2222 | 153.2222 | 478.0208 | 164.6002 | 72.492 | 173.0122 | 177.3373 | 197.0641
204.2237 | 154.2237 | 477.8366 | 165.69 | 73.0893 | 173.7852 | 178.3584 | 198.0596
205.2251 | 155.2251 | 477.8229 | 166.7704 | 73.6751 | 174.5433 | 179.3506 | 199.0322
206.2265 | 156.2265 | 477.7222 | 167.8423 | 74.2763 | 175.2915 | 180.3333 | 199.9712
207.228 | 157.228 | 477.6447 | 168.9103 | 74.8661 | 176.05 | 181.2936 | 200.9054
208.2194 | 158.2194 | 477.4453 | 169.9612 | 75.4619 | 176.7855 | 182.191 | 201.8237
209.2208 | 159.2208 | 477.4191 | 171.0096 | 76.0605 | 177.5267 | 183.1503 | 202.7396
210.2223 | 160.2223 | 477.3283 | 172.0432 | 76.6599 | 178.2393 | 184.068 | 203.628
211.2237 | 161.2237 | 477.2833 | 173.0751 | 77.2607 | 178.9662 | 184.9886 | 204.5187
212.2252 | 162.2252 | 477.122 | 174.0825 | 77.8816 | 179.693 | 185.9082 | 205.391
213.2166 | 163.2166 | 477.1013 | 175.0598 | 78.4831 | 180.4054 | 186.8107 | 206.2551
214.218 | 164.218 | 476.9463 | 176.0188 | 79.0891 | 181.1246 | 187.7184 | 207.1248
215.2195 | 165.2195 | 476.8429 | 176.9635 | 79.7 | 181.8468 | 188.5841 | 208.0006
216.2209 | 166.2209 | 476.8473 | 177.8915 | 80.2908 | 182.5648 | 189.4547 | 208.838
217.2224 | 167.2224 | 476.9553 | 178.8106 | 80.9037 | 183.287 | 190.3053 | 209.6694
218.2238 | 168.2238 | 477.1585 | 179.7152 | 81.5096 | 184.0011 | 191.1423 | 210.5028
219.2252 | 169.2252 | 477.221 | 180.6187 | 82.1073 | 184.6985 | 191.9416 | 211.3455
220.2167 | 170.2167 | 477.3598 | 181.5104 | 82.7079 | 185.4116 | 192.7497 | 212.1716
221.2181 | 171.2181 | 477.3728 | 182.3998 | 83.2946 | 186.1139 | 193.5256 | 213.0063
222.2195 | 172.2195 | 477.3027 | 183.3017 | 83.8789 | 186.8097 | 194.3216 | 213.8244
223.221 | 173.221 | 477.2881 | 184.1796 | 84.4659 | 187.5062 | 195.1205 | 214.6317
224.2224 | 174.2224 | 477.3168 | 185.0547 | 85.0614 | 188.2074 | 195.9297 | 215.4392
225.2239 | 175.2239 | 477.4757 | 185.9183 | 85.6059 | 188.9023 | 196.6705 | 216.249
226.2253 | 176.2253 | 477.6135 | 186.7699 | 86.2155 | 189.5905 | 197.4276 | 217.0574
227.2267 | 177.2267 | 477.6497 | 187.6189 | 86.7943 | 190.2955 | 198.1812 | 217.8698
228.2182 | 178.2182 | 477.8501 | 188.4488 | 87.3688 | 190.9936 | 198.9427 | 218.6743
229.2196 | 179.2196 | 477.9425 | 189.2619 | 87.9435 | 191.6884 | 199.6504 | 219.4448
230.221 | 180.221 | 478.1954 | 190.0635 | 88.5172 | 192.3876 | 200.4079 | 220.2256
231.2225 | 181.2225 | 478.634 | 190.8519 | 89.0842 | 193.1059 | 201.1375 | 220.9963
232.2239 | 182.2239 | 478.9716 | 191.6352 | 89.6482 | 193.8154 | 201.8699 | 221.7759
233.2254 | 183.2254 | 479.0889 | 192.3973 | 90.2146 | 194.5428 | 202.5792 | 222.5327
234.2168 | 184.2168 | 479.1531 | 193.1701 | 90.7849 | 195.2526 | 203.3609 | 223.3072
235.2182 | 185.2182 | 479.2602 | 193.9259 | 91.3436 | 195.9555 | 204.0473 | 224.0866
236.2197 | 186.2197 | 479.4607 | 194.6794 | 91.9088 | 196.6607 | 204.7614 | 224.8499
237.2211 | 187.2211 | 479.5658 | 195.4354 | 92.4665 | 197.3827 | 205.427 | 225.5957
238.2225 | 188.2225 | 479.7871 | 196.1963 | 93.0362 | 198.0976 | 206.1284 | 226.3579
239.224 | 189.224 | 479.8755 | 196.9601 | 93.5812 | 198.8152 | 206.7929 | 227.1021
240.2254 | 190.2254 | 479.8041 | 197.7101 | 94.1649 | 199.5072 | 207.4166 | 227.8249
241.2169 | 191.2169 | 479.7519 | 198.4654 | 94.7219 | 200.1402 | 208.0951 | 228.5656
242.2183 | 192.2183 | 479.5892 | 199.2125 | 95.2729 | 200.7765 | 208.7703 | 229.2893
243.2197 | 193.2197 | 479.5797 | 199.9484 | 95.8594 | 201.4283 | 209.4351 | 230.0202
244.2212 | 194.2212 | 479.3875 | 200.6697 | 96.4347 | 202.0986 | 210.093 | 230.7491
245.2226 | 195.2226 | 479.2581 | 201.3862 | 97.0127 | 202.7861 | 210.7368 | 231.4591
246.2241 | 196.2241 | 479.177 | 202.1013 | 97.6171 | 203.4633 | 211.3715 | 232.1612
247.2255 | 197.2255 | 478.8609 | 202.8253 | 98.2238 | 204.1794 | 212.009 | 232.8263
248.2269 | 198.2269 | 478.6369 | 203.5363 | 98.8576 | 204.883 | 212.5925 | 233.4954
249.2284 | 199.2284 | 478.5094 | 204.2348 | 99.4877 | 205.5653 | 213.2251 | 234.1628
250.2198 | 200.2198 | 478.5272 | 204.9184 | 100.152 | 206.2606 | 213.8678 | 234.819
251.2212 | 201.2212 | 478.6085 | 205.618 | 100.8574 | 206.9708 | 214.4505 | 235.4634
252.2227 | 202.2227 | 478.8696 | 206.311 | 101.5787 | 207.699 | 215.0645 | 236.0905
253.2241 | 203.2241 | 478.9748 | 207.0105 | 102.3019 | 208.3806 | 215.6632 | 236.6999
254.2256 | 204.2256 | 478.9387 | 207.7314 | 103.0517 | 209.0589 | 216.3005 | 237.2868
255.217 | 205.217 | 478.7356 | 208.4377 | 103.7931 | 209.711 | 216.903 | 237.8956
256.2184 | 206.2184 | 478.6734 | 209.1652 | 104.5305 | 210.3642 | 217.5018 | 238.4883
257.2199 | 207.2199 | 478.5326 | 209.9123 | 105.2418 | 211.0066 | 218.1059 | 239.0667
258.2213 | 208.2213 | 478.3576 | 210.7065 | 105.9408 | 211.6626 | 218.6993 | 239.6587
259.2227 | 209.2227 | 478.3226 | 211.5152 | 106.6156 | 212.3403 | 219.3004 | 240.2458
260.2242 | 210.2242 | 478.3918 | 212.3505 | 107.2597 | 213.008 | 219.8702 | 240.8571
261.2256 | 211.2256 | 478.3423 | 213.1959 | 107.8544 | 213.6942 | 220.4575 | 241.4609
262.217 | 212.217 | 478.1648 | 214.0356 | 108.4267 | 214.3631 | 221.0507 | 242.0496
263.2185 | 213.2185 | 477.9993 | 214.8803 | 108.9469 | 215.0083 | 221.6929 | 242.632
264.2199 | 214.2199 | 477.9879 | 215.7322 | 109.4313 | 215.6998 | 222.2809 | 243.1946
265.2214 | 215.2214 | 478.0399 | 216.5714 | 109.8706 | 216.4034 | 222.8524 | 243.7588
266.2228 | 216.2228 | 478.0807 | 217.3942 | 110.3136 | 217.0957 | 223.4 | 244.3002
267.2242 | 217.2242 | 477.947 | 218.2131 | 110.7307 | 217.791 | 223.9992 | 244.8482
268.2257 | 218.2257 | 478.0756 | 219.0157 | 111.1693 | 218.4886 | 224.589 | 245.3733
269.2271 | 219.2271 | 478.237 | 219.9011 | 111.6402 | 219.0989 | 225.0918 | 245.9005
270.2186 | 220.2186 | 478.3628 | 220.7603 | 112.1485 | 219.7436 | 225.6336 | 246.4187
271.22 | 221.22 | 478.4636 | 221.6305 | 112.691 | 220.3875 | 226.1842 | 246.9227
272.2214 | 222.2214 | 478.5539 | 222.5048 | 113.2479 | 221.0513 | 226.7326 | 247.4146
273.2229 | 223.2229 | 478.2852 | 223.3248 | 113.8137 | 221.7099 | 227.2581 | 247.9123
274.2243 | 224.2243 | 478.2247 | 224.1609 | 114.3614 | 222.3847 | 227.8356 | 248.417
275.2258 | 225.2258 | 478.2568 | 224.9086 | 114.9104 | 223.0485 | 228.4111 | 248.9272
276.2172 | 226.2172 | 478.2044 | 225.4476 | 115.4336 | 223.7209 | 228.9516 | 249.4456
277.2186 | 227.2186 | 478.2607 | 225.8227 | 115.9538 | 224.3965 | 229.4967 | 249.9462
278.2201 | 228.2201 | 478.3232 | 226.053 | 116.4625 | 225.0611 | 230.0765 | 250.4133
279.2215 | 229.2215 | 478.4412 | 225.8849 | 116.9547 | 225.7487 | 230.6029 | 250.872
280.2229 | 230.2229 | 478.5276 | 225.5572 | 117.4578 | 226.4323 | 231.1641 | 251.3669
281.2244 | 231.2244 | 478.5682 | 225.1526 | 117.9654 | 227.1366 | 231.718 | 251.7896
282.2258 | 232.2258 | 478.7363 | 224.6806 | 118.5375 | 227.8344 | 232.303 | 252.2525
283.2172 | 233.2172 | 479.0597 | 224.2224 | 119.1776 | 228.5559 | 232.8671 | 252.7118
284.2187 | 234.2187 | 479.2142 | 223.7011 | 119.9106 | 229.258 | 233.425 | 253.1808
285.2201 | 235.2201 | 479.2677 | 223.3207 | 120.7594 | 229.9573 | 234.024 | 253.6398
286.2216 | 236.2216 | 479.5761 | 223.0434 | 121.7351 | 230.5874 | 234.5926 | 254.1145
287.223 | 237.223 | 479.6731 | 222.8744 | 122.8239 | 231.1966 | 235.1395 | 254.5829
288.2244 | 238.2244 | 479.5606 | 222.6715 | 123.9813 | 231.8318 | 235.6485 | 255.0478
289.2259 | 239.2259 | 479.6132 | 222.395 | 125.2133 | 232.4488 | 236.2288 | 255.5208
290.2173 | 240.2173 | 479.7954 | 222.1205 | 126.4345 | 233.0507 | 236.7653 | 256.0158
291.2188 | 241.2188 | 479.8351 | 221.8988 | 127.6489 | 233.6642 | 237.3136 | 256.479
292.2202 | 242.2202 | 479.8687 | 221.7939 | 128.8525 | 234.2819 | 237.8588 | 256.9504
293.2216 | 243.2216 | 479.8777 | 221.676 | 130.0327 | 234.893 | 238.4346 | 257.4344
294.2231 | 244.2231 | 479.8939 | 221.7332 | 131.1745 | 235.5205 | 239.009 | 257.9039
295.2245 | 245.2245 | 479.777 | 221.822 | 132.3051 | 236.162 | 239.5291 | 258.3607
296.226 | 246.226 | 479.5993 | 221.8622 | 133.4029 | 236.7985 | 240.0192 | 258.804
297.2274 | 247.2274 | 479.4346 | 221.8938 | 134.4788 | 237.4302 | 240.5474 | 259.2453
298.2188 | 248.2188 | 479.4673 | 221.9484 | 135.5359 | 238.0439 | 241.087 | 259.6708
299.2203 | 249.2203 | 479.6607 | 222.0533 | 136.5849 | 238.6372 | 241.6518 | 260.0997
300.2217 | 250.2217 | 479.7262 | 222.2266 | 137.5968 | 239.2202 | 242.1942 | 260.5333
301.2231 | 251.2231 | 479.6156 | 222.4609 | 138.5871 | 239.8055 | 242.7132 | 260.9632
302.2246 | 252.2246 | 479.5729 | 222.7193 | 139.5802 | 240.3741 | 243.2355 | 261.3681
303.216 | 253.216 | 479.4712 | 223.0265 | 140.54 | 240.9415 | 243.8063 | 261.7763
304.2174 | 254.2174 | 479.4573 | 223.3945 | 141.5048 | 241.5174 | 244.3496 | 262.1839
305.2189 | 255.2189 | 479.4476 | 223.8118 | 142.4483 | 242.0744 | 244.816 | 262.5518
306.2203 | 256.2203 | 479.5516 | 224.2685 | 143.382 | 242.6332 | 245.3792 | 262.9549
307.2218 | 257.2218 | 479.3405 | 224.8566 | 144.3065 | 243.1696 | 245.9503 | 263.3419
308.2232 | 258.2232 | 479.1825 | 225.4383 | 145.223 | 243.6993 | 246.405 | 263.7513
309.2246 | 259.2246 | 479.1224 | 226.1853 | 146.1142 | 244.2169 | 246.9618 | 264.1469
310.2261 | 260.2261 | 478.9646 | 227.1828 | 147.021 | 244.7263 | 247.5094 | 264.5428
311.2275 | 261.2275 | 478.9997 | 228.1518 | 147.8985 | 245.246 | 248.0509 | 264.9209
312.2189 | 262.2189 | 479.22 | 229.0794 | 148.7819 | 245.7796 | 248.553 | 265.291
313.2204 | 263.2204 | 479.2935 | 230.0583 | 149.635 | 246.2924 | 249.0824 | 265.6652
314.2218 | 264.2218 | 479.3475 | 231.219 | 150.5057 | 246.7458 | 249.6259 | 266.0095
315.2233 | 265.2233 | 479.3305 | 232.4248 | 151.3673 | 247.1991 | 250.1055 | 266.3656
316.2247 | 266.2247 | 479.231 | 233.946 | 152.2255 | 247.6578 | 250.6273 | 266.718
317.2261 | 267.2261 | 479.1213 | 235.282 | 153.0617 | 248.0804 | 251.1552 | 267.0538
318.2176 | 268.2176 | 478.9606 | 236.4515 | 153.9061 | 248.4887 | 251.6673 | 267.3919
319.219 | 269.219 | 478.7061 | 237.371 | 154.7306 | 248.8701 | 252.2245 | 267.7343
320.2205 | 270.2205 | 478.642 | 238.2775 | 155.5485 | 249.2061 | 252.7517 | 268.0687
321.2219 | 271.2219 | 478.761 | 239.0596 | 156.3744 | 249.5247 | 253.2577 | 268.4117
322.2233 | 272.2233 | 478.7744 | 239.7675 | 157.1747 | 249.8021 | 253.7847 | 268.7456
323.2248 | 273.2248 | 478.7843 | 240.4812 | 157.9753 | 250.0374 | 254.2759 | 269.0823
324.3063 | 274.3063 | 478.7282 | 241.1707 | 158.8413 | 250.3244 | 254.8573 | 269.4495
325.2176 | 275.2176 | 478.9303 | 241.6663 | 159.544 | 250.6018 | 255.2866 | 269.7516
326.2191 | 276.2191 | 479.0557 | 242.1736 | 160.3385 | 250.832 | 255.7666 | 270.0849
327.2205 | 277.2205 | 478.9762 | 242.5909 | 161.1044 | 251.0955 | 256.2611 | 270.4153
328.222 | 278.222 | 479.1891 | 242.9974 | 161.8964 | 251.3049 | 256.7454 | 270.7224
329.2234 | 279.2234 | 479.4883 | 243.3169 | 162.6588 | 251.4653 | 257.1521 | 271.0207
330.2248 | 280.2248 | 479.5592 | 243.5316 | 163.4223 | 251.432 | 257.5837 | 271.2917
331.2263 | 281.2263 | 479.5266 | 243.6975 | 164.1902 | 251.5249 | 258.0277 | 271.5782
332.2277 | 282.2277 | 479.5988 | 243.8841 | 164.9354 | 251.6758 | 258.4249 | 271.8711
333.2191 | 283.2191 | 479.579 | 243.9187 | 165.682 | 251.7565 | 258.8608 | 272.171
334.2206 | 284.2206 | 479.5367 | 243.944 | 166.4213 | 251.8935 | 259.3524 | 272.461
335.222 | 285.222 | 479.3892 | 244.0764 | 167.1592 | 252.1526 | 259.8283 | 272.7399
336.2235 | 286.2235 | 479.2161 | 244.2992 | 167.8782 | 252.3674 | 260.2684 | 273.0176
337.2249 | 287.2249 | 479.0868 | 244.4673 | 168.6164 | 252.4581 | 260.786 | 273.3016
338.2263 | 288.2263 | 478.8546 | 244.6998 | 169.36 | 252.6156 | 261.2937 | 273.5805
339.2278 | 289.2278 | 478.6545 | 245.0188 | 170.0772 | 252.7757 | 261.7083 | 273.8493
340.2192 | 290.2192 | 478.5809 | 245.3652 | 170.7988 | 252.8073 | 262.0257 | 274.1092
341.2207 | 291.2207 | 478.6289 | 245.9816 | 171.5111 | 252.9478 | 262.457 | 274.3624
342.2221 | 292.2221 | 478.4727 | 246.3888 | 172.1968 | 252.9919 | 262.8176 | 274.6116
343.2235 | 293.2235 | 478.279 | 246.782 | 172.8892 | 253.163 | 263.2591 | 274.8519
344.225 | 294.225 | 478.0351 | 247.0605 | 173.5982 | 253.5637 | 263.5222 | 275.0922
345.2164 | 295.2164 | 477.9534 | 247.3163 | 174.2837 | 253.8681 | 263.9488 | 275.3323
346.2178 | 296.2178 | 478.0475 | 247.5502 | 174.9653 | 254.1569 | 264.3638 | 275.5725
347.2193 | 297.2193 | 478.0724 | 247.0907 | 175.6534 | 254.3962 | 264.7922 | 275.8244
348.2207 | 298.2207 | 478.0753 | 246.8903 | 176.331 | 254.5929 | 265.2708 | 276.0785
349.2222 | 299.2222 | 477.8523 | 246.8319 | 176.9776 | 254.8868 | 265.7189 | 276.3358
350.2236 | 300.2236 | 477.6201 | 246.838 | 177.6395 | 255.6089 | 266.1393 | 276.5928
351.225 | 301.225 | 477.5957 | 246.9091 | 178.3017 | 256.2486 | 266.606 | 276.8487
352.2265 | 302.2265 | 477.6945 | 247.1363 | 178.9542 | 256.8081 | 267.0235 | 277.1017
353.2179 | 303.2179 | 477.7642 | 247.2632 | 179.5758 | 257.316 | 267.3711 | 277.329
354.2193 | 304.2193 | 477.8081 | 247.2863 | 180.2182 | 257.7854 | 267.8072 | 277.5941
355.2208 | 305.2208 | 477.9442 | 247.4546 | 180.8539 | 258.1307 | 268.1872 | 277.8549
356.2222 | 306.2222 | 477.9555 | 247.6342 | 181.4705 | 258.3757 | 268.7087 | 278.1231
357.2237 | 307.2237 | 478.0573 | 247.7961 | 182.0851 | 258.3662 | 269.1316 | 278.4007
358.2251 | 308.2251 | 478.1489 | 247.9774 | 182.7013 | 257.3705 | 269.5273 | 278.6955
359.2265 | 309.2265 | 478.113 | 248.2116 | 183.2998 | 257.0634 | 269.9687 | 278.9643
360.218 | 310.218 | 478.1719 | 248.3739 | 183.9128 | 256.6852 | 270.2636 | 279.2394
361.2194 | 311.2194 | 478.4149 | 248.4907 | 184.5077 | 256.542 | 270.7181 | 279.5207
362.2208 | 312.2208 | 478.5605 | 248.6386 | 185.0989 | 256.5229 | 271.1871 | 279.8027
363.2223 | 313.2223 | 478.6621 | 248.7953 | 185.6658 | 256.6297 | 271.5909 | 280.0778
364.2237 | 314.2237 | 478.8924 | 248.9334 | 186.2626 | 256.8327 | 272.0126 | 280.3601
365.2252 | 315.2252 | 479.0789 | 249.1626 | 186.8364 | 256.859 | 272.4044 | 280.6276
366.2166 | 316.2166 | 479.2633 | 249.3497 | 187.4032 | 256.7897 | 272.8411 | 280.9087
367.218 | 317.218 | 479.3971 | 249.5128 | 187.9755 | 256.7954 | 273.3767 | 281.2112
368.2195 | 318.2195 | 479.4629 | 249.705 | 188.5479 | 256.882 | 273.8517 | 281.5085
369.2209 | 319.2209 | 479.5318 | 249.7614 | 189.1224 | 257.2026 | 274.3229 | 281.8093
370.2224 | 320.2224 | 479.5601 | 250.0065 | 189.6717 | 257.6354 | 274.795 | 282.0947
371.2238 | 321.2238 | 479.443 | 250.2724 | 190.2292 | 257.7312 | 275.2267 | 282.3846
372.2252 | 322.2252 | 479.2679 | 250.7745 | 190.7823 | 257.9193 | 275.6837 | 282.6869
373.2267 | 323.2267 | 479.0189 | 251.435 | 191.3481 | 258.0737 | 275.9643 | 282.9952
374.2281 | 324.2281 | 478.8914 | 252.1946 | 191.8794 | 258.2987 | 276.3797 | 283.2852
375.2195 | 325.2195 | 478.7594 | 252.9754 | 192.4333 | 258.6154 | 276.7599 | 283.593
376.221 | 326.221 | 478.6265 | 253.7764 | 192.9755 | 258.9277 | 277.2278 | 283.9063
377.2224 | 327.2224 | 478.5881 | 254.6089 | 193.511 | 259.2644 | 277.6842 | 284.2312
378.2239 | 328.2239 | 478.4982 | 255.5271 | 194.0479 | 259.612 | 278.1549 | 284.5553
379.2253 | 329.2253 | 478.3734 | 256.3059 | 194.5856 | 259.9919 | 278.6161 | 284.8684
380.2267 | 330.2267 | 478.2405 | 257.0165 | 195.1096 | 260.3471 | 279.0311 | 285.1855
381.2182 | 331.2182 | 478.2734 | 257.6927 | 195.6513 | 260.6613 | 279.3571 | 285.5067
382.2196 | 332.2196 | 478.3237 | 258.2678 | 196.1754 | 260.8932 | 279.6905 | 285.8807
383.221 | 333.221 | 478.3592 | 258.6966 | 196.7059 | 261.265 | 280.1027 | 286.2418
384.2225 | 334.2225 | 478.2186 | 258.9761 | 197.2261 | 261.7037 | 280.521 | 286.5709
385.2239 | 335.2239 | 478.1896 | 259.2913 | 197.7462 | 262.1105 | 280.9042 | 286.9004
386.2254 | 336.2254 | 478.135 | 259.6393 | 198.2634 | 262.5017 | 281.2189 | 287.2204
387.2168 | 337.2168 | 478.2083 | 260.0044 | 198.7925 | 263.064 | 281.6092 | 287.5274
388.2182 | 338.2182 | 478.2185 | 260.3171 | 199.3113 | 264.0306 | 282.0344 | 287.8351
389.2197 | 339.2197 | 478.3047 | 260.5138 | 199.814 | 264.5078 | 282.5108 | 288.135
390.2211 | 340.2211 | 478.3378 | 260.6668 | 200.3428 | 264.5887 | 282.8306 | 288.437
391.2226 | 341.2226 | 478.2728 | 260.9183 | 200.8416 | 264.7761 | 283.2752 | 288.7374
392.224 | 342.224 | 478.2579 | 261.0486 | 201.3598 | 265.016 | 283.6638 | 289.0329
393.2254 | 343.2254 | 478.2828 | 261.0882 | 201.8552 | 265.3399 | 284.0005 | 289.3198
394.2169 | 344.2169 | 478.3301 | 261.0954 | 202.3653 | 265.7358 | 284.4731 | 289.5889
395.2183 | 345.2183 | 478.4869 | 260.972 | 202.8674 | 266.1571 | 284.9379 | 289.874
396.2197 | 346.2197 | 478.6224 | 260.9271 | 203.3603 | 266.5161 | 285.3366 | 290.1421
397.2212 | 347.2212 | 478.6748 | 260.8473 | 203.8723 | 267.0214 | 285.8472 | 290.4052
398.2226 | 348.2226 | 478.5623 | 260.7255 | 204.3688 | 267.527 | 286.3958 | 290.6798
399.2241 | 349.2241 | 478.6094 | 260.6622 | 204.8651 | 267.9968 | 286.9388 | 290.9562
400.2255 | 350.2255 | 478.649 | 260.4365 | 205.3442 | 268.4301 | 287.369 | 291.2207
401.2269 | 351.2269 | 478.6129 | 259.7097 | 205.8494 | 268.8445 | 287.8798 | 291.4953
402.2184 | 352.2184 | 478.458 | 259.0117 | 206.3256 | 269.2282 | 288.2945 | 291.7654
403.2198 | 353.2198 | 478.3335 | 258.5115 | 206.8216 | 269.6096 | 288.7258 | 291.9924
404.2212 | 354.2212 | 478.2641 | 258.2489 | 207.3021 | 270.0238 | 289.0863 | 292.161
405.2227 | 355.2227 | 478.287 | 257.9325 | 207.7914 | 270.4781 | 289.4636 | 292.2771
406.2241 | 356.2241 | 478.1505 | 257.5074 | 208.2685 | 270.9222 | 289.7607 | 292.5226
407.2256 | 357.2256 | 478.3074 | 256.9464 | 208.7452 | 271.6337 | 290.0567 | 292.8236
408.217 | 358.217 | 478.3177 | 256.4569 | 209.229 | 272.3765 | 290.3478 | 293.0915
409.2184 | 359.2184 | 478.1719 | 256.1401 | 209.7024 | 273.1482 | 290.662 | 293.3611
410.2199 | 360.2199 | 478.0832 | 255.983 | 210.1741 | 273.9114 | 290.9545 | 293.609
411.2213 | 361.2213 | 478.0797 | 255.9258 | 210.6425 | 274.5758 | 291.2147 | 293.8523
412.2227 | 362.2227 | 477.9868 | 255.8902 | 211.1118 | 275.2781 | 291.4726 | 294.1297
413.2242 | 363.2242 | 478.1873 | 255.8436 | 211.5719 | 275.9432 | 291.7265 | 294.4318
414.2256 | 364.2256 | 478.559 | 255.7771 | 212.0553 | 276.5898 | 291.9882 | 294.724
415.2171 | 365.2171 | 478.7336 | 255.6598 | 212.5143 | 277.4829 | 292.2394 | 295.0395
416.2185 | 366.2185 | 478.8158 | 255.5417 | 212.9958 | 278.279 | 292.4906 | 295.3448
417.2199 | 367.2199 | 478.7181 | 255.4287 | 213.442 | 278.9735 | 292.6809 | 295.6188
418.2214 | 368.2214 | 478.7208 | 255.2829 | 213.9135 | 279.6235 | 292.871 | 295.87
419.2228 | 369.2228 | 478.6804 | 255.3471 | 214.3666 | 280.198 | 293.0109 | 296.1117
420.2243 | 370.2243 | 478.6884 | 255.4498 | 214.8265 | 280.78 | 293.2113 | 296.3413
421.2257 | 371.2257 | 478.803 | 255.5422 | 215.2836 | 281.4023 | 293.3849 | 296.5715
422.2271 | 372.2271 | 478.8262 | 255.6927 | 215.7376 | 281.9654 | 293.5516 | 296.8
423.2186 | 373.2186 | 478.7468 | 255.8789 | 216.199 | 282.5023 | 293.7671 | 296.9951
424.22 | 374.22 | 478.5898 | 256.0984 | 216.6521 | 283.0023 | 293.9854 | 297.1627
425.2214 | 375.2214 | 478.3144 | 256.3249 | 217.1101 | 283.4777 | 294.1752 | 297.3551
426.2229 | 376.2229 | 478.1629 | 256.6241 | 217.5567 | 283.9317 | 294.3495 | 297.5271
427.2243 | 377.2243 | 478.1066 | 256.9967 | 218.0023 | 284.3376 | 294.5205 | 297.6984
428.2258 | 378.2258 | 478.1508 | 257.4281 | 218.4705 | 284.7043 | 294.7157 | 297.8925
429.2172 | 379.2172 | 478.1686 | 257.8768 | 218.9262 | 285.1017 | 294.7851 | 298.0984
430.2186 | 380.2186 | 478.1226 | 258.326 | 219.3888 | 285.4312 | 294.9976 | 298.2948
431.2201 | 381.2201 | 478.109 | 258.7922 | 219.8294 | 285.7718 | 295.1598 | 298.483
432.2215 | 382.2215 | 478.2553 | 259.2811 | 220.2829 | 286.1749 | 295.3505 | 298.6763
433.2229 | 383.2229 | 478.4402 | 259.7847 | 220.7375 | 286.5499 | 295.4405 | 298.8249
434.2244 | 384.2244 | 478.5117 | 260.2494 | 221.1869 | 286.9433 | 295.718 | 298.9671
435.2258 | 385.2258 | 478.5088 | 260.7112 | 221.6375 | 287.3366 | 295.921 | 299.1418
436.2172 | 386.2172 | 478.5456 | 261.1939 | 222.0822 | 287.7178 | 296.1568 | 299.3299
437.2187 | 387.2187 | 478.6095 | 261.7045 | 222.5453 | 288.0896 | 296.4125 | 299.5013
438.2201 | 388.2201 | 478.7061 | 262.2232 | 222.9927 | 288.4246 | 296.5791 | 299.6711
439.2216 | 389.2216 | 478.7532 | 262.7252 | 223.4204 | 288.7694 | 296.7962 | 299.8471
440.223 | 390.223 | 478.8363 | 263.2291 | 223.8628 | 289.1345 | 297.0375 | 300.0263
441.2244 | 391.2244 | 478.8089 | 263.7135 | 224.3067 | 289.4844 | 297.2069 | 300.1592
442.2259 | 392.2259 | 479.021 | 264.1785 | 224.7251 | 289.8357 | 297.4517 | 300.2833
443.2273 | 393.2273 | 479.2147 | 264.6486 | 225.1461 | 290.1738 | 297.6722 | 300.426
444.2188 | 394.2188 | 479.4115 | 265.1315 | 225.5784 | 290.5263 | 297.8644 | 300.5306
445.2202 | 395.2202 | 479.4111 | 265.6177 | 226.0204 | 290.9001 | 298.0575 | 300.7552
446.2216 | 396.2216 | 479.468 | 266.0734 | 226.4378 | 291.2966 | 298.2585 | 300.8776
447.2231 | 397.2231 | 479.6646 | 266.5356 | 226.8819 | 291.6889 | 298.4965 | 300.9821
448.2245 | 398.2245 | 479.901 | 267.1381 | 227.3344 | 292.0854 | 298.7533 | 301.055
449.226 | 399.226 | 480.071 | 268.4564 | 227.759 | 292.4946 | 299.0692 | 301.0004
450.2174 | 400.2174 | 480.0838 | 269.5838 | 228.1958 | 292.907 | 299.8786 | 301
451.2188 | 401.2188 | 480.0245 | 270.6172 | 228.6446 | 293.3264 | 300.5074 | 301.0939
452.2203 | 402.2203 | 480.1736 | 271.5127 | 229.0882 | 293.7545 | 301.088 | 301.2154
453.2217 | 403.2217 | 480.3477 | 272.3472 | 229.5224 | 294.173 | 301.7438 | 301.3498
454.2231 | 404.2231 | 480.2485 | 273.1388 | 229.9657 | 294.6042 | 302.441 | 301.5011
455.2246 | 405.2246 | 480.1289 | 273.9122 | 230.3982 | 295.0522 | 303.0325 | 301.6833
456.216 | 406.216 | 480.0016 | 274.6529 | 230.8546 | 295.5096 | 303.6105 | 301.8751
457.2174 | 407.2174 | 479.9739 | 275.3465 | 231.2839 | 295.9557 | 304.1884 | 302.0485
458.2189 | 408.2189 | 479.9749 | 276.0035 | 231.7286 | 296.3918 | 304.9185 | 302.1667
459.2203 | 409.2203 | 480.0398 | 276.6352 | 232.1472 | 296.8122 | 305.6803 | 302.1904
460.2218 | 410.2218 | 479.9631 | 277.2304 | 232.6066 | 297.2403 | 306.2615 | 302.2775
461.2232 | 411.2232 | 479.8249 | 277.8122 | 233.0445 | 297.6697 | 306.8257 | 302.2878
462.2246 | 412.2246 | 479.7725 | 278.3567 | 233.4909 | 298.0911 | 307.368 | 302.3106
463.2261 | 413.2261 | 479.7132 | 278.8943 | 233.9257 | 298.5199 | 307.9571 | 302.3276
464.2275 | 414.2275 | 479.6001 | 279.4783 | 234.3631 | 298.9764 | 308.56 | 302.3953
465.219 | 415.219 | 479.6306 | 279.9735 | 234.7986 | 299.459 | 309.1291 | 302.4412
466.2204 | 416.2204 | 479.5872 | 280.4484 | 235.2349 | 299.9336 | 309.6788 | 302.5604
467.2218 | 417.2218 | 479.6765 | 280.8998 | 235.6842 | 300.3578 | 310.1944 | 302.6867
468.2233 | 418.2233 | 479.6031 | 281.3225 | 236.124 | 300.8153 | 310.63 | 302.7476
469.2247 | 419.2247 | 479.4796 | 281.7314 | 236.5617 | 301.275 | 311.3044 | 302.4413
470.2262 | 420.2262 | 479.4124 | 282.1177 | 236.9826 | 301.7454 | 311.9721 | 302.3044
471.2176 | 421.2176 | 479.2821 | 282.4977 | 237.4399 | 302.2361 | 312.4874 | 302.3028
472.219 | 422.219 | 479.1681 | 282.8684 | 237.8729 | 302.869 | 313.0071 | 302.4506
473.2205 | 423.2205 | 479.0317 | 283.2404 | 238.3016 | 303.7351 | 313.5887 | 302.6349
474.2219 | 424.2219 | 479.0641 | 283.5918 | 238.7469 | 304.4418 | 313.9866 | 302.703
475.2233 | 425.2233 | 479.0303 | 283.9705 | 239.1749 | 305.1579 | 314.5219 | 302.7971
476.2248 | 426.2248 | 478.9998 | 284.427 | 239.613 | 305.7777 | 315.0486 | 302.9511
477.2162 | 427.2162 | 479.0879 | 284.9419 | 240.0538 | 306.3495 | 315.1698 | 302.8539
478.2176 | 428.2176 | 478.9905 | 285.4485 | 240.481 | 307.0482 | 315.5037 | 302.9011
479.2191 | 429.2191 | 478.9466 | 286.0432 | 240.9357 | 308.101 | 315.8515 | 302.8746
480.2205 | 430.2205 | 479.169 | 286.5971 | 241.37 | 309.2362 | 316.1504 | 302.9422
481.222 | 431.222 | 479.1168 | 287.1121 | 241.826 | 309.8227 | 316.5603 | 302.9994
482.2234 | 432.2234 | 478.8869 | 287.571 | 242.2549 | 310.4213 | 316.8454 | 303.0771
483.2248 | 433.2248 | 478.8403 | 288.0425 | 242.694 | 311.0222 | 317.2403 | 303.1358
484.2263 | 434.2263 | 478.9143 | 288.5172 | 243.1195 | 311.5708 | 317.6538 | 303.1392
485.2277 | 435.2277 | 478.9845 | 289.0149 | 243.5754 | 311.7937 | 318.0594 | 303.1748
486.2191 | 436.2191 | 478.9816 | 289.4654 | 244.0046 | 312.0569 | 318.4661 | 303.2451
487.2206 | 437.2206 | 478.8536 | 289.9373 | 244.4325 | 312.4741 | 318.8636 | 303.3109
488.222 | 438.222 | 478.5985 | 290.3817 | 244.8634 | 312.9717 | 319.2857 | 303.3636
489.2235 | 439.2235 | 478.262 | 290.7987 | 245.3313 | 313.3805 | 319.7288 | 303.479
490.2249 | 440.2249 | 478.0323 | 291.1917 | 245.751 | 313.6807 | 320.1399 | 303.7445
491.2263 | 441.2263 | 477.7696 | 291.5687 | 246.2094 | 313.9964 | 320.5354 | 303.8733
492.2178 | 442.2178 | 477.8441 | 291.969 | 246.6499 | 314.4002 | 320.9776 | 304.0858
493.2192 | 443.2192 | 478.0948 | 292.3876 | 247.0865 | 314.8493 | 321.5653 | 304.1879
494.2207 | 444.2207 | 478.1037 | 292.8633 | 247.5546 | 315.3069 | 322.086 | 304.3216
495.2221 | 445.2221 | 478.0343 | 293.3353 | 248.0075 | 315.7364 | 322.541 | 304.4201
496.2235 | 446.2235 | 477.9213 | 293.7511 | 248.4579 | 316.0554 | 322.9778 | 304.4601
497.225 | 447.225 | 477.7759 | 294.1397 | 248.9145 | 316.3844 | 323.4366 | 304.4392
498.2164 | 448.2164 | 477.7866 | 294.5001 | 249.3757 | 316.8982 | 323.788 | 304.5215
499.2178 | 449.2178 | 477.9621 | 294.8602 | 249.815 | 317.3721 | 324.2547 | 304.5897
500.2193 | 450.2193 | 477.9391 | 295.3009 | 250.2609 | 317.768 | 324.6808 | 304.6839
501.2207 | 451.2207 | 477.9956 | 295.7888 | 250.7142 | 318.0298 | 325.178 | 304.7605
502.2222 | 452.2222 | 477.9951 | 296.2879 | 251.1473 | 318.3488 | 325.632 | 304.9339
503.2236 | 453.2236 | 478.0048 | 296.7679 | 251.5836 | 318.7267 | 326.1537 | 305.1559
504.225 | 454.225 | 477.8883 | 297.2417 | 252.0149 | 319.3457 | 326.8894 | 305.4439
505.2165 | 455.2165 | 477.7102 | 297.7846 | 252.4025 | 319.702 | 327.3321 | 305.6611
506.2279 | 456.2279 | 477.7385 | 298.4014 | 252.794 | 320.0286 | 327.7899 | 305.4911
507.2193 | 457.2193 | 477.6986 | 299.0036 | 253.1889 | 320.4251 | 328.2761 | 305.5311
508.2408 | 458.2408 | 477.9041 | 299.5692 | 253.5782 | 320.718 | 328.8435 | 306.0298
509.2222 | 459.2222 | 478.0279 | 300.1014 | 253.9521 | 320.9991 | 329.2004 | 306.384
510.2237 | 460.2237 | 478.0564 | 300.6879 | 254.3318 | 321.117 | 329.7841 | 306.6442
511.2251 | 461.2251 | 478.0548 | 301.4409 | 254.7169 | 321.4977 | 330.305 | 306.9717
512.2265 | 462.2265 | 478.1764 | 302.2839 | 255.1072 | 321.8702 | 331.1672 | 307.2169
513.218 | 463.218 | 478.2128 | 303.3163 | 255.4892 | 322.277 | 332.0697 | 307.436
514.2194 | 464.2194 | 478.2417 | 304.5006 | 255.858 | 322.5268 | 333.7693 | 307.6707
515.2209 | 465.2209 | 478.3363 | 305.4402 | 256.2471 | 322.7699 | 335.3877 | 307.8199
516.2223 | 466.2223 | 478.2764 | 306.2136 | 256.6388 | 323.0253 | 336.8667 | 307.7809
517.2237 | 467.2237 | 478.2621 | 306.8888 | 257.0356 | 323.3188 | 338.3083 | 307.9428
518.2252 | 468.2252 | 478.263 | 307.4414 | 257.416 | 323.5815 | 339.2902 | 308.1953
519.2266 | 469.2266 | 478.283 | 307.9494 | 257.7909 | 323.9168 | 340.5528 | 308.239
520.218 | 470.218 | 478.2694 | 308.427 | 258.1828 | 324.3004 | 341.4895 | 308.4433
521.2195 | 471.2195 | 478.1195 | 308.9135 | 258.5584 | 324.6426 | 342.5294 | 308.8223
522.2209 | 472.2209 | 478.1332 | 309.4146 | 258.9494 | 324.9341 | 343.9825 | 308.652
523.2224 | 473.2224 | 478.0502 | 309.9297 | 259.3211 | 325.2654 | 345.2465 | 308.6338
524.2238 | 474.2238 | 477.8719 | 310.4435 | 259.713 | 325.6662 | 346.8156 | 308.7901
525.2252 | 475.2252 | 477.7715 | 310.9224 | 260.1013 | 325.9952 | 347.9838 | 308.8517
526.2167 | 476.2167 | 477.6594 | 311.3531 | 260.4844 | 326.3562 | 348.9761 | 309.0546
527.2281 | 477.2281 | 477.5565 | 311.8702 | 260.8605 | 326.7015 | 349.301 | 309.0773
528.2195 | 478.2195 | 477.3381 | 312.4132 | 261.2373 | 327.0358 | 349.9133 | 308.9573
529.221 | 479.221 | 477.1519 | 312.8286 | 261.6174 | 327.3579 | 350.1597 | 308.8801
530.2224 | 480.2224 | 477.1254 | 313.2272 | 262.0043 | 327.7081 | 351.315 | 308.8824
531.2239 | 481.2239 | 477.0047 | 313.6308 | 262.3719 | 328.0792 | 352.6292 | 308.9435
532.2253 | 482.2253 | 476.9603 | 314.0128 | 262.7546 | 328.4569 | 352.8367 | 309.0483
533.2167 | 483.2167 | 476.9691 | 314.4436 | 263.1307 | 328.7638 | 352.6054 | 309.2482
534.2182 | 484.2182 | 476.927 | 314.7117 | 263.4944 | 329.1004 | 353.2076 | 309.2881
535.2196 | 485.2196 | 476.9553 | 314.961 | 263.8746 | 329.4607 | 353.5162 | 309.6794
536.221 | 486.221 | 476.9679 | 315.3477 | 264.2511 | 329.7902 | 353.9647 | 309.9453
537.2225 | 487.2225 | 477.0598 | 315.7024 | 264.6219 | 330.1708 | 354.1873 | 310.1195
538.2239 | 488.2239 | 477.2666 | 315.9834 | 265.0055 | 330.3855 | 354.6178 | 309.9254
539.2254 | 489.2254 | 477.3845 | 316.2003 | 265.3769 | 330.7033 | 355.4627 | 309.9121
540.2168 | 490.2168 | 477.4562 | 316.6993 | 265.7467 | 330.9917 | 356.1946 | 310.0823
541.2182 | 491.2182 | 477.5365 | 317.3477 | 266.1373 | 331.24 | 357.3782 | 310.3305
542.2197 | 492.2197 | 477.7903 | 317.9326 | 266.4976 | 331.5651 | 357.3613 | 310.5391
543.2211 | 493.2211 | 477.9065 | 318.3872 | 266.874 | 331.9008 | 356.2575 | 310.619
544.2226 | 494.2226 | 478.0199 | 318.6911 | 267.3831 | 332.225 | 355.9347 | 310.3698
545.224 | 495.224 | 478.0663 | 319.0805 | 267.8406 | 332.5394 | 356.2131 | 310.5573
546.2254 | 496.2254 | 478.003 | 319.2199 | 268.2025 | 332.8987 | 355.414 | 310.325
547.2169 | 497.2169 | 477.9797 | 319.691 | 268.5699 | 333.1782 | 355.4084 | 310.2535
548.2183 | 498.2183 | 478.1067 | 320.5511 | 268.9337 | 333.5083 | 355.5991 | 310.5139
549.2197 | 499.2197 | 477.9973 | 321.6416 | 269.305 | 333.813 | 356.3393 | 310.4847
550.2212 | 500.2212 | 477.9765 | 322.1111 | 269.6821 | 334.1293 | 357.4494 | 310.3628
551.2226 | 501.2226 | 477.9886 | 322.4721 | 270.04 | 334.5038 | 357.5007 | 310.3332
552.2241 | 502.2241 | 478.0288 | 322.9558 | 270.4136 | 334.8868 | 357.5332 | 310.0385
553.2255 | 503.2255 | 478.1153 | 323.3588 | 270.7995 | 335.2586 | 357.7761 | 310.0748
554.2269 | 504.2269 | 478.1023 | 323.7197 | 271.1737 | 335.5303 | 358.1676 | 310.0212
555.2184 | 505.2184 | 478.1286 | 323.9485 | 271.5571 | 335.9007 | 358.1296 | 310.2426
556.2198 | 506.2198 | 478.2111 | 324.3563 | 271.9413 | 336.21 | 358.5365 | 310.2095
557.2212 | 507.2212 | 478.4027 | 324.7828 | 272.3316 | 336.564 | 358.2599 | 310.3218
558.2227 | 508.2227 | 478.4012 | 325.3739 | 272.7146 | 336.9125 | 357.6531 | 310.0943
559.2241 | 509.2241 | 478.3429 | 325.7286 | 273.0932 | 337.1937 | 357.6821 | 310.4396
560.2256 | 510.2256 | 478.331 | 326.0616 | 273.5056 | 337.5754 | 358.3891 | 310.2736
561.217 | 511.217 | 478.3341 | 326.6026 | 273.8987 | 337.899 | 358.0495 | 309.928
562.2184 | 512.2184 | 478.4029 | 327.348 | 274.3019 | 338.2278 | 359.4375 | 309.7143
563.2199 | 513.2199 | 478.3493 | 327.7994 | 274.6966 | 338.5904 | 359.557 | 309.6066
564.2213 | 514.2213 | 478.4028 | 328.016 | 275.1078 | 338.9604 | 359.8087 | 310.2056
565.2228 | 515.2228 | 478.4036 | 328.2259 | 275.5053 | 339.278 | 358.8848 | 310.7139
566.2242 | 516.2242 | 478.3732 | 328.4546 | 275.9447 | 339.6361 | 358.5032 | 310.8988
567.2256 | 517.2256 | 478.2739 | 328.5013 | 276.3391 | 339.9822 | 358.8505 | 310.9145
568.2171 | 518.2171 | 478.2899 | 328.7831 | 276.7387 | 340.3435 | 358.7819 | 310.7107
569.2185 | 519.2185 | 478.344 | 329.118 | 277.1489 | 340.6671 | 358.6899 | 310.1915
570.2199 | 520.2199 | 478.3244 | 329.2953 | 277.5492 | 341.0245 | 346.5614 | 310.1585
571.2214 | 521.2214 | 478.2496 | 330.1085 | 277.9365 | 341.3496 | 335.9224 | 309.6539
572.2228 | 522.2228 | 478.3597 | 331.7402 | 278.3512 | 341.6555 | 333.092 | 310.0339
573.2243 | 523.2243 | 478.5087 | 332.5511 | 278.753 | 341.9745 | 330.048 | 310.3563
574.2257 | 524.2257 | 478.652 | 332.8822 | 279.1483 | 342.354 | 327.4716 | 310.2846
575.2171 | 525.2171 | 478.7177 | 332.9784 | 279.5483 | 342.596 | 324.8551 | 310.2637
576.2186 | 526.2186 | 478.6892 | 332.9315 | 279.9374 | 342.8449 | 322.9426 | 310.4915
577.22 | 527.22 | 478.5402 | 332.7677 | 280.3591 | 343.2366 | 322.8734 | 311.3803
578.2214 | 528.2214 | 478.4346 | 332.8267 | 280.7467 | 343.5671 | 323.7424 | 311.2345
579.2229 | 529.2229 | 478.2685 | 333.1277 | 281.1548 | 343.8926 | 322.5389 | 311.2451
580.2243 | 530.2243 | 478.1547 | 333.6726 | 281.5462 | 344.2058 | 322.3398 | 311.2906
581.2258 | 531.2258 | 478.009 | 333.8347 | 281.9325 | 344.4654 | 322.0039 | 313.6892
582.2172 | 532.2172 | 477.9364 | 333.8913 | 282.3261 | 344.7608 | 322.9878 | 316.7822
583.2186 | 533.2186 | 477.9402 | 334.1791 | 282.7104 | 345.0635 | 324.437 | 318.8982
584.2201 | 534.2201 | 478.0704 | 334.7663 | 283.1211 | 345.4018 | 326.9757 | 320.4601
585.2215 | 535.2215 | 478.1084 | 335.2176 | 283.5063 | 345.7512 | 326.6756 | 321.7341
586.2229 | 536.2229 | 478.1658 | 335.6508 | 283.916 | 346.0982 | 323.8701 | 322.8651
587.2244 | 537.2244 | 478.2311 | 336.0584 | 284.2826 | 346.453 | 324.5685 | 323.9177
588.2258 | 538.2258 | 478.3671 | 336.5232 | 284.697 | 346.755 | 324.9373 | 324.6332
589.2173 | 539.2173 | 478.4653 | 337.2349 | 285.097 | 347.0759 | 325.4378 | 325.3075
590.2187 | 540.2187 | 478.5774 | 337.4175 | 285.4863 | 347.4102 | 325.2917 | 326.3679
591.2201 | 541.2201 | 478.5495 | 337.4119 | 285.8798 | 347.7007 | 323.9606 | 328.0692
592.2216 | 542.2216 | 478.7557 | 337.4232 | 286.2648 | 347.9602 | 322.7628 | 329.2281
593.223 | 543.223 | 478.5888 | 337.4695 | 286.6432 | 348.0818 | 325.5915 | 330.4073
594.2245 | 544.2245 | 478.3329 | 337.9849 | 287.022 | 348.3397 | 328.0594 | 331.478
595.2259 | 545.2259 | 478.2823 | 338.551 | 287.4256 | 348.5398 | 330.2216 | 332.2959
596.2273 | 546.2273 | 478.2169 | 338.6341 | 287.7984 | 348.8619 | 331.9266 | 333.0158
597.2188 | 547.2188 | 477.9751 | 338.5308 | 288.1665 | 349.15 | 333.3645 | 334.205
598.2202 | 548.2202 | 477.6152 | 338.8032 | 288.5667 | 349.4456 | 334.9367 | 335.0773
599.2216 | 549.2216 | 477.4029 | 339.4241 | 288.956 | 349.7311 | 335.9114 | 336.0372
600.2231 | 550.2231 | 477.2498 | 339.5405 | 289.3278 | 350.0556 | 336.8734 | 337.0481
601.2245 | 551.2245 | 477.0955 | 340.0285 | 289.7373 | 350.2801 | 337.561 | 337.975
602.226 | 552.226 | 477.0808 | 341.3544 | 290.1272 | 350.5947 | 338.1364 | 338.803
603.2174 | 553.2174 | 477.1374 | 342.3719 | 290.5082 | 350.8824 | 337.8026 | 339.7496
604.2188 | 554.2188 | 477.1377 | 342.5662 | 290.8991 | 351.1257 | 337.3129 | 340.7243
605.2203 | 555.2203 | 477.1091 | 342.4786 | 291.2984 | 351.399 | 337.649 | 341.5362
606.2217 | 556.2217 | 476.8713 | 342.4497 | 291.7135 | 351.7207 | 338.208 | 342.6334
607.2231 | 557.2231 | 476.7623 | 342.3202 | 292.1236 | 351.9792 | 338.5158 | 343.8565
608.2246 | 558.2246 | 476.7776 | 342.6163 | 292.5195 | 352.2354 | 339.3887 | 342.7699
609.226 | 559.226 | 476.9491 | 343.0407 | 292.9291 | 352.4558 | 340.2311 | 340.5972
610.2174 | 560.2174 | 477.2303 | 343.3472 | 293.3422 | 352.7379 | 341.1884 | 338.3398
611.2189 | 561.2189 | 477.4596 | 343.4588 | 293.7624 | 353.0123 | 341.8811 | 339.0142
612.2203 | 562.2203 | 477.6734 | 344.0471 | 294.2254 | 353.2925 | 342.6262 | 338.4495
613.2218 | 563.2218 | 477.6265 | 344.3176 | 294.6945 | 353.4055 | 343.2898 | 337.6651
614.2232 | 564.2232 | 477.4726 | 344.569 | 295.1547 | 353.5772 | 343.7213 | 336.6965
615.2246 | 565.2246 | 477.4772 | 344.5805 | 295.6098 | 353.9254 | 344.241 | 336.1374
616.2261 | 566.2261 | 477.5344 | 344.5841 | 296.0259 | 354.2536 | 344.4356 | 335.9757
617.2175 | 567.2175 | 477.6335 | 344.6363 | 296.485 | 354.5447 | 345.0258 | 333.8758
618.219 | 568.219 | 477.717 | 344.7282 | 296.9469 | 354.7973 | 345.6808 | 332.8915
619.2204 | 569.2204 | 477.7622 | 345.0469 | 297.3519 | 355.0776 | 346.2754 | 333.7054
620.2218 | 570.2218 | 477.9651 | 345.8946 | 297.7517 | 355.3599 | 346.5153 | 333.0782
621.2233 | 571.2233 | 478.138 | 345.4031 | 298.1391 | 355.6022 | 347.0194 | 332.0213
622.2247 | 572.2247 | 478.3762 | 345.7778 | 298.5653 | 355.8815 | 347.5317 | 329.6526
623.2262 | 573.2262 | 478.6163 | 346.4806 | 299.0157 | 356.1136 | 347.987 | 329.9631
624.2176 | 574.2176 | 478.8049 | 347.3612 | 299.5754 | 356.3107 | 347.9613 | 329.1254
625.219 | 575.219 | 478.9189 | 347.9454 | 300.1027 | 356.569 | 347.8947 | 329.16
626.2205 | 576.2205 | 478.9336 | 347.7156 | 300.4618 | 356.8719 | 348.2013 | 330.1632
627.2219 | 577.2219 | 478.8749 | 347.465 | 300.7825 | 357.0729 | 348.4783 | 330.0944
628.2233 | 578.2233 | 478.8881 | 347.9486 | 301.0827 | 357.1697 | 348.6415 | 330.8038
629.2248 | 579.2248 | 478.8334 | 348.8704 | 301.4771 | 357.3835 | 349.1168 | 330.356
630.2162 | 580.2162 | 478.8168 | 348.6528 | 302.0408 | 357.6659 | 349.4167 | 329.9624
631.2176 | 581.2176 | 478.8094 | 348.4939 | 302.4839 | 357.8994 | 350.2391 | 330.7571
632.2191 | 582.2191 | 478.731 | 348.9161 | 302.8386 | 358.1889 | 350.6868 | 331.6712
633.2205 | 583.2205 | 478.7783 | 349.2895 | 303.1869 | 358.4787 | 351.0107 | 331.6035
634.222 | 584.222 | 478.8648 | 349.1945 | 303.569 | 358.7583 | 348.2459 | 332.4295
635.2234 | 585.2234 | 478.7923 | 349.0382 | 303.875 | 359.0672 | 349.0615 | 333.0119
636.2248 | 586.2248 | 478.5586 | 349.8937 | 304.2387 | 359.2521 | 350.5059 | 333.2537
637.2263 | 587.2263 | 478.3177 | 350.4759 | 304.6271 | 359.4594 | 351.6242 | 333.451
638.2177 | 588.2177 | 478.079 | 350.2589 | 305.0645 | 359.7372 | 352.3287 | 332.7128
639.2192 | 589.2192 | 478.099 | 350.5625 | 305.5855 | 359.9943 | 353.2192 | 332.8612
640.2206 | 590.2206 | 478.0462 | 350.8308 | 305.964 | 360.3058 | 354.151 | 332.7598
641.222 | 591.222 | 478.0086 | 351.1608 | 306.3166 | 360.5168 | 354.6877 | 332.8701
642.2235 | 592.2235 | 477.8624 | 351.5614 | 306.8933 | 360.8383 | 354.8079 | 333.6927
643.2249 | 593.2249 | 477.6927 | 351.7422 | 307.2893 | 361.1079 | 355.1854 | 334.3533
644.2264 | 594.2264 | 477.59 | 351.4836 | 307.7231 | 361.3717 | 355.8433 | 334.8659
645.2178 | 595.2178 | 477.4885 | 352.0474 | 308.0743 | 361.6449 | 356.3683 | 335.3605
646.2192 | 596.2192 | 477.4824 | 353.086 | 308.3415 | 361.9497 | 357.2441 | 335.8454
647.2207 | 597.2207 | 477.3693 | 353.5481 | 308.673 | 362.2209 | 357.7214 | 336.0362
648.2221 | 598.2221 | 477.3872 | 353.4099 | 309.087 | 362.4468 | 357.8244 | 336.2857
649.2235 | 599.2235 | 477.4069 | 353.0308 | 309.4671 | 362.6799 | 358.1753 | 336.0686
650.225 | 600.225 | 477.3096 | 353.6796 | 309.7994 | 362.9627 | 358.3304 | 336.3061
651.2164 | 601.2164 | 477.0228 | 353.9393 | 310.0745 | 363.1998 | 358.3225 | 336.3917
652.2178 | 602.2178 | 476.6011 | 354.1673 | 310.3855 | 363.4487 | 358.5674 | 336.5916
653.2193 | 603.2193 | 476.4023 | 354.3354 | 310.7136 | 363.7216 | 358.6354 | 335.5742
654.2207 | 604.2207 | 476.2241 | 354.4329 | 311.2417 | 363.7729 | 358.8802 | 335.243
655.2222 | 605.2222 | 476.1869 | 354.3017 | 311.6457 | 364.0098 | 358.8682 | 335.1904
656.2236 | 606.2236 | 476.1617 | 354.9193 | 311.9714 | 364.23 | 357.8701 | 334.904
657.225 | 607.225 | 476.1819 | 355.2153 | 312.3163 | 364.5009 | 357.0054 | 334.7142
658.2265 | 608.2265 | 476.1693 | 355.2368 | 312.7096 | 364.6935 | 356.51 | 334.6317
659.2179 | 609.2179 | 476.246 | 355.3553 | 313.0075 | 364.9501 | 356.4987 | 334.3703
660.2193 | 610.2193 | 476.3294 | 355.6563 | 313.3047 | 365.1767 | 356.4013 | 334.5589
661.2208 | 611.2208 | 476.6445 | 356.1992 | 313.7281 | 365.3593 | 355.3539 | 334.7378
662.2222 | 612.2222 | 476.5638 | 356.3857 | 314.1089 | 365.5664 | 354.5274 | 334.5631
663.2237 | 613.2237 | 476.6448 | 356.3955 | 314.3975 | 365.7961 | 355.1281 | 334.2543
664.2251 | 614.2251 | 476.7757 | 356.7964 | 314.9394 | 365.9605 | 355.1563 | 333.7938
665.2265 | 615.2265 | 476.7949 | 356.9384 | 315.2319 | 366.2135 | 356.0066 | 334.3445
666.218 | 616.218 | 476.909 | 357.4389 | 315.4904 | 366.4579 | 356.632 | 334.9903
667.2194 | 617.2194 | 477.0164 | 357.5033 | 315.7347 | 366.6795 | 357.3625 | 335.1649
668.2209 | 618.2209 | 477.0284 | 357.5751 | 316.0169 | 366.8763 | 357.8408 | 335.7133
669.2223 | 619.2223 | 476.9836 | 357.8209 | 316.3643 | 367.0104 | 358.2461 | 336.2222
670.2237 | 620.2237 | 477.0733 | 358.3321 | 316.7061 | 367.2318 | 358.4562 | 336.915
671.2252 | 621.2252 | 477.1778 | 358.4939 | 317.1233 | 367.4408 | 358.9317 | 337.4559
672.2166 | 622.2166 | 477.1107 | 358.1525 | 317.4839 | 367.6855 | 359.5351 | 337.992
673.218 | 623.218 | 476.994 | 358.6592 | 317.7721 | 367.9796 | 360.2631 | 337.9465
674.2195 | 624.2195 | 476.8572 | 358.9075 | 318.098 | 368.219 | 360.7725 | 337.9719
675.2209 | 625.2209 | 476.7696 | 358.9686 | 318.3584 | 368.4663 | 361.2804 | 337.9233
676.2224 | 626.2224 | 476.883 | 358.9206 | 318.6963 | 368.7102 | 361.5495 | 338.0989
677.2238 | 627.2238 | 477.0485 | 359.439 | 318.9761 | 368.9591 | 362.0793 | 338.2235
678.2252 | 628.2252 | 477.3728 | 359.9333 | 319.387 | 369.1707 | 362.4052 | 338.3346
679.2267 | 629.2267 | 477.5044 | 360.0226 | 319.6969 | 369.4198 | 362.6027 | 338.8881
680.2281 | 630.2281 | 477.5712 | 360.1108 | 319.9809 | 369.6852 | 362.6343 | 339.0123
681.2195 | 631.2195 | 477.4767 | 360.734 | 320.2522 | 369.9121 | 362.7032 | 339.276
682.221 | 632.221 | 477.4823 | 361.0001 | 320.511 | 370.1231 | 363.0634 | 339.2097
683.2224 | 633.2224 | 477.5432 | 361.54 | 320.7669 | 370.3781 | 363.1755 | 339.3468
684.2239 | 634.2239 | 477.5863 | 361.5722 | 321.0581 | 370.6582 | 363.4076 | 339.5061
685.2754 | 635.2754 | 477.5687 | 361.6523 | 321.5126 | 370.9302 | 363.3808 | 339.7248
686.2267 | 636.2267 | 477.5496 | 362.0119 | 321.8358 | 371.1849 | 363.0702 | 340.0371
687.2182 | 637.2182 | 477.6086 | 362.3793 | 322.1945 | 371.3957 | 362.7697 | 340.4266
688.2196 | 638.2196 | 477.7345 | 362.7538 | 322.5052 | 371.6123 | 362.79 | 341.0312
689.2211 | 639.2211 | 477.8122 | 362.9516 | 322.7936 | 371.8739 | 362.9078 | 341.3678
690.2225 | 640.2225 | 477.8812 | 363.0532 | 323.113 | 372.1619 | 363.074 | 341.5582
691.2239 | 641.2239 | 478.0218 | 363.3541 | 323.8337 | 372.4724 | 363.3133 | 341.8441
692.2254 | 642.2254 | 478.1458 | 363.6311 | 324.1437 | 372.7315 | 363.0178 | 342.3823
693.2168 | 643.2168 | 478.3805 | 363.7827 | 324.4022 | 372.9469 | 362.9902 | 342.6369
694.2182 | 644.2182 | 478.4888 | 363.7694 | 324.6449 | 373.2239 | 362.4526 | 343.5236
695.2197 | 645.2197 | 478.7617 | 363.9834 | 324.9404 | 373.5239 | 362.162 | 344.0734
696.2211 | 646.2211 | 478.8629 | 364.6667 | 325.2007 | 373.7218 | 362.2624 | 344.4981
697.2226 | 647.2226 | 478.8944 | 365.1843 | 325.454 | 373.8974 | 362.7907 | 344.9161
698.224 | 648.224 | 478.8189 | 365.2226 | 325.8394 | 374.1306 | 363.0394 | 345.2951
699.2254 | 649.2254 | 478.7651 | 365.3409 | 326.2532 | 374.3173 | 363.3813 | 345.7639
700.2169 | 650.2169 | 478.674 | 365.7484 | 326.5663 | 374.6069 | 363.8693 | 346.7845
701.2183 | 651.2183 | 478.537 | 366.0546 | 326.8393 | 374.9255 | 364.2601 | 347.2894
702.2197 | 652.2197 | 478.4533 | 365.9945 | 327.0954 | 375.236 | 364.412 | 347.0709
703.2212 | 653.2212 | 478.4081 | 366.0803 | 327.3627 | 375.5445 | 364.6466 | 347.6486
704.2226 | 654.2226 | 478.3733 | 366.685 | 327.6309 | 375.8733 | 364.816 | 348.407
705.2241 | 655.2241 | 478.44 | 367.1263 | 327.8998 | 376.1942 | 365.1372 | 348.9838
706.2255 | 656.2255 | 478.4059 | 367.204 | 328.1681 | 376.5095 | 365.0916 | 349.461
707.2169 | 657.2169 | 478.3787 | 367.4532 | 328.4555 | 376.7912 | 364.1825 | 349.6836
708.2184 | 658.2184 | 478.2835 | 367.5708 | 328.7275 | 377.0888 | 363.9364 | 349.862
709.2198 | 659.2198 | 478.1902 | 367.9963 | 329.0084 | 377.3199 | 364.1 | 350.4575
710.2212 | 660.2212 | 478.3273 | 368.0155 | 329.2963 | 377.6187 | 364.3597 | 351.0888
711.2227 | 661.2227 | 478.4413 | 368.2158 | 329.6044 | 377.915 | 364.7078 | 351.4075
712.2241 | 662.2241 | 478.5171 | 368.2414 | 330.3483 | 378.1819 | 365.2779 | 351.8517
713.2256 | 663.2256 | 478.6137 | 368.5492 | 331.2264 | 378.4415 | 365.7185 | 352.175
714.217 | 664.217 | 478.5626 | 368.7326 | 331.4559 | 378.7683 | 366.0103 | 352.5312
715.2184 | 665.2184 | 478.4882 | 368.9689 | 331.6543 | 379.0188 | 366.2437 | 352.1506
716.2199 | 666.2199 | 478.4103 | 369.0126 | 331.8626 | 379.3225 | 366.7954 | 352.1429
717.2213 | 667.2213 | 478.3375 | 369.625 | 332.0761 | 379.554 | 367.4044 | 352.107
718.2228 | 668.2228 | 478.3179 | 369.7283 | 332.3149 | 379.8938 | 367.7657 | 352.0485
719.2242 | 669.2242 | 478.3173 | 369.8902 | 332.5687 | 380.2338 | 367.989 | 352.2871
720.2256 | 670.2256 | 478.3012 | 370.4127 | 332.8155 | 380.538 | 368.1692 | 353.108
721.2271 | 671.2271 | 478.43 | 370.6192 | 333.0974 | 380.8395 | 368.8537 | 353.531
722.2185 | 672.2185 | 478.4604 | 370.7821 | 333.7144 | 381.1024 | 369.5628 | 353.7428
723.2199 | 673.2199 | 478.2967 | 371.0742 | 334.1272 | 381.3266 | 369.9801 | 354.136
724.2214 | 674.2214 | 478.1522 | 371.2744 | 334.4109 | 381.4219 | 370.6652 | 354.3471
725.2228 | 675.2228 | 478.0449 | 371.4975 | 334.6414 | 381.6025 | 371.3417 | 354.7031
726.2243 | 676.2243 | 477.9355 | 371.5822 | 334.8902 | 381.8165 | 371.7418 | 354.8358
727.2257 | 677.2257 | 477.8967 | 371.9993 | 335.1358 | 381.9806 | 372.212 | 354.9443
728.2271 | 678.2271 | 477.8661 | 372.0504 | 335.3961 | 382.1104 | 372.4032 | 355.1876
729.2186 | 679.2186 | 477.9864 | 371.9989 | 335.648 | 382.2622 | 372.8014 | 354.9587
730.22 | 680.22 | 477.9496 | 372.2596 | 335.9305 | 382.4283 | 373.2458 | 355.2243
731.2214 | 681.2214 | 477.8124 | 372.6238 | 336.271 | 382.6634 | 373.8383 | 355.5008
732.2229 | 682.2229 | 477.742 | 372.502 | 336.9395 | 382.8805 | 374.1792 | 355.365
733.2243 | 683.2243 | 477.6778 | 373.0281 | 337.2461 | 383.0904 | 374.1352 | 356.0667
734.2258 | 684.2258 | 477.717 | 373.2645 | 337.49 | 383.254 | 374.1815 | 356.6387
735.2172 | 685.2172 | 477.7209 | 373.3438 | 337.6961 | 383.4755 | 374.2131 | 356.8467
736.2186 | 686.2186 | 477.572 | 373.6648 | 337.9465 | 383.6898 | 374.2793 | 356.9355
737.2201 | 687.2201 | 477.5635 | 373.8149 | 338.1937 | 383.8268 | 374.3067 | 357.4234
738.2215 | 688.2215 | 477.7035 | 373.9405 | 338.4575 | 383.9539 | 374.3967 | 357.531
739.223 | 689.223 | 477.5893 | 374.299 | 338.7267 | 384.1411 | 374.1579 | 357.5433
740.2244 | 690.2244 | 477.5768 | 374.6982 | 338.9986 | 384.3153 | 374.002 | 357.4286
741.2258 | 691.2258 | 477.6863 | 374.8259 | 339.252 | 384.5353 | 373.818 | 358.0804
742.2173 | 692.2173 | 477.8142 | 374.8314 | 339.5581 | 384.7024 | 373.7825 | 358.0586
743.2187 | 693.2187 | 477.9138 | 375.0918 | 339.829 | 384.8872 | 373.8728 | 357.9301
744.2201 | 694.2201 | 478.0696 | 375.4069 | 340.1195 | 385.1041 | 373.7262 | 358.5209
745.2216 | 695.2216 | 477.9475 | 375.7755 | 340.4049 | 385.2834 | 373.7847 | 358.8084
746.223 | 696.223 | 477.737 | 375.9301 | 340.6987 | 385.4634 | 373.6124 | 359.1154
747.2245 | 697.2245 | 477.5 | 376.0127 | 340.9851 | 385.6788 | 373.6589 | 359.8033
748.2259 | 698.2259 | 477.291 | 376.3021 | 341.282 | 385.8929 | 373.54 | 360.2351
749.2173 | 699.2173 | 477.1717 | 376.7018 | 341.5892 | 386.108 | 373.7249 | 360.4675
750.2188 | 700.2188 | 477.0758 | 376.6438 | 341.8879 | 386.3144 | 373.4456 | 360.7908
751.2202 | 701.2202 | 477.0518 | 376.8534 | 342.1823 | 386.4719 | 372.9075 | 360.7415
752.2216 | 702.2216 | 477.002 | 376.9509 | 342.4918 | 386.657 | 372.5213 | 360.6981
753.2231 | 703.2231 | 477.0758 | 377.0726 | 342.8043 | 386.6617 | 372.5374 | 360.5338
754.2245 | 704.2245 | 477.2855 | 377.0463 | 343.0906 | 386.8134 | 372.1546 | 360.5146
755.226 | 705.226 | 477.1969 | 377.4208 | 343.3909 | 387.0328 | 371.8171 | 360.658
756.2174 | 706.2174 | 477.1604 | 377.5781 | 343.7003 | 387.1286 | 371.4809 | 360.4256
757.2188 | 707.2188 | 476.9917 | 377.6365 | 344.0083 | 387.2777 | 371.3728 | 360.6369
758.2203 | 708.2203 | 476.9185 | 377.751 | 344.3139 | 387.5171 | 371.1265 | 361.1867
759.2217 | 709.2217 | 476.9508 | 377.778 | 344.6109 | 387.721 | 370.9292 | 361.6631
760.2231 | 710.2231 | 477.0547 | 378.1187 | 344.9192 | 387.9929 | 370.713 | 362.0535
761.2246 | 711.2246 | 477.0458 | 378.1847 | 345.2083 | 388.2075 | 370.5536 | 361.8239
762.216 | 712.216 | 476.9381 | 378.3378 | 345.5228 | 388.4456 | 370.181 | 361.3797
763.2175 | 713.2175 | 477.0927 | 378.46 | 346.1421 | 388.6637 | 369.5641 | 361.4177
764.2189 | 714.2189 | 477.1415 | 378.7874 | 346.6262 | 388.8955 | 369.425 | 361.4977
765.2203 | 715.2203 | 477.1248 | 379.0223 | 346.9097 | 389.1531 | 369.3186 | 362.0142
766.2218 | 716.2218 | 477.0938 | 379.3877 | 347.164 | 389.372 | 369.2216 | 362.557
767.2232 | 717.2232 | 477.2362 | 379.4185 | 347.4118 | 389.5562 | 369.1449 | 363.0851
768.2247 | 718.2247 | 477.3292 | 379.4493 | 347.6812 | 389.7323 | 368.9176 | 363.2157
769.2261 | 719.2261 | 477.5038 | 379.8013 | 347.9348 | 389.9453 | 368.7846 | 363.9648
770.2275 | 720.2275 | 477.7317 | 379.865 | 348.2051 | 390.1539 | 368.6023 | 364.1336
771.219 | 721.219 | 477.9508 | 380.181 | 348.4832 | 390.3432 | 368.5288 | 364.1677
772.2204 | 722.2204 | 477.9632 | 380.2739 | 348.746 | 390.4869 | 368.3816 | 363.7292
773.2218 | 723.2218 | 477.8319 | 380.5173 | 349.027 | 390.6775 | 368.4495 | 363.2916
774.2233 | 724.2233 | 477.7345 | 381.0029 | 349.3114 | 390.8528 | 368.3852 | 363.347
775.2247 | 725.2247 | 477.7465 | 381.2574 | 349.5955 | 391.085 | 368.265 | 363.3735
776.2262 | 726.2262 | 477.7545 | 381.4825 | 349.8759 | 391.213 | 368.2578 | 363.509
777.2176 | 727.2176 | 477.7297 | 381.7104 | 350.1643 | 391.4203 | 368.4086 | 363.8548
778.219 | 728.219 | 477.7341 | 381.8459 | 350.7774 | 391.6382 | 368.4239 | 364.8846
779.2205 | 729.2205 | 477.6632 | 382.0596 | 351.0719 | 391.8562 | 368.4565 | 364.9492
780.2219 | 730.2219 | 477.4698 | 382.1779 | 351.3207 | 392.0615 | 368.4953 | 364.637
781.2233 | 731.2233 | 477.4128 | 382.3213 | 351.5727 | 392.2373 | 368.4454 | 364.8251
782.2248 | 732.2248 | 477.4683 | 382.4618 | 351.8479 | 392.4415 | 368.1977 | 364.5169
783.2262 | 733.2262 | 477.4601 | 382.8555 | 352.1169 | 392.6176 | 368.3055 | 364.4216
784.2176 | 734.2176 | 477.4468 | 383.162 | 352.3556 | 392.8061 | 368.3835 | 365.1249
785.2191 | 735.2191 | 477.3099 | 383.544 | 352.6504 | 392.9093 | 368.3831 | 365.2547
786.2205 | 736.2205 | 477.1784 | 383.7884 | 352.9135 | 393.0978 | 368.2675 | 365.4883
787.222 | 737.222 | 477.2009 | 383.8249 | 353.1894 | 393.2687 | 368.2195 | 365.671
788.2234 | 738.2234 | 477.2125 | 383.9976 | 353.4803 | 393.4257 | 368.1984 | 366.1165
789.2248 | 739.2248 | 477.1329 | 384.3112 | 354.0582 | 393.5666 | 368.2841 | 366.5825
790.2163 | 740.2163 | 477.224 | 384.3634 | 354.3387 | 393.7256 | 368.3426 | 366.9762
791.2177 | 741.2177 | 477.1452 | 384.4718 | 354.5984 | 393.9491 | 368.2003 | 367.1188
792.2192 | 742.2192 | 477.2341 | 384.706 | 354.8994 | 394.257 | 367.8706 | 367.4892
793.2206 | 743.2206 | 477.2689 | 384.9962 | 355.3307 | 394.6865 | 368.024 | 367.7279
794.222 | 744.222 | 477.3483 | 385.2443 | 355.6215 | 395.2166 | 368.4884 | 367.5066
795.2235 | 745.2235 | 477.3649 | 385.4696 | 355.8709 | 395.8832 | 369.0612 | 367.6136
796.2249 | 746.2249 | 477.5627 | 386.0089 | 356.1333 | 396.7218 | 369.5475 | 367.6509
797.2264 | 747.2264 | 477.6004 | 386.5941 | 356.374 | 397.9137 | 369.9707 | 368.2741
798.2178 | 748.2178 | 477.7506 | 387.2312 | 356.6285 | 399.3687 | 370.5148 | 367.8835
799.2192 | 749.2192 | 478.0241 | 387.8917 | 356.8848 | 400.9568 | 371.0689 | 369.1553
800.2207 | 750.2207 | 478.1944 | 388.9802 | 357.1501 | 402.659 | 371.989 | 369.6876
801.2221 | 751.2221 | 478.3723 | 389.837 | 357.4314 | 404.4689 | 372.5292 | 370.7539
802.2235 | 752.2235 | 478.4257 | 390.7743 | 357.7109 | 406.3267 | 373.6035 | 371.3778
803.225 | 753.225 | 478.1504 | 391.7581 | 358.065 | 408.2009 | 379.159 | 372.4224
804.2264 | 754.2264 | 478.0632 | 393.0169 | 358.4536 | 410.1044 | 387.4392 | 376.7101 | Time of ignition
805.2178 | 755.2178 | 478.1084 | 393.9294 | 358.7299 | 411.9955 | 398.6297 | 380.9613 | 754 | 0
806.2193 | 756.2193 | 478.0446 | 395.0374 | 358.9763 | 413.8431 | 410.6684 | 387.104 | 754 | 900
807.2207 | 757.2207 | 477.9671 | 396.2225 | 359.2149 | 415.6907 | 419.1009 | 392.3718
808.2222 | 758.2222 | 477.7306 | 397.1069 | 359.4605 | 417.5814 | 425.1081 | 398.4353
809.2236 | 759.2236 | 477.5651 | 398.3906 | 359.6794 | 419.5075 | 431.3521 | 404.2858
810.225 | 760.225 | 477.5316 | 399.4352 | 359.9557 | 421.4502 | 441.5753 | 409.4139
811.2265 | 761.2265 | 477.3939 | 400.348 | 360.2141 | 423.4438 | 447.2208 | 414.5372
812.2279 | 762.2279 | 477.2538 | 401.0944 | 360.4536 | 425.3784 | 450.5316 | 419.1244
813.2194 | 763.2194 | 477.1887 | 401.9391 | 360.8262 | 427.3712 | 459.6743 | 425.5237
814.2208 | 764.2208 | 476.9771 | 402.8261 | 361.2293 | 429.4277 | 460.6577 | 430.3297
815.2222 | 765.2222 | 477.0069 | 403.6683 | 361.6247 | 431.4216 | 467.7119 | 433.8234
816.2237 | 766.2237 | 476.9353 | 404.5132 | 361.9039 | 433.4691 | 469.3299 | 438.3561
817.2251 | 767.2251 | 476.9951 | 405.2917 | 362.2483 | 435.5067 | 471.6728 | 445.6145
818.2266 | 768.2266 | 477.0844 | 406.1275 | 362.5775 | 437.406 | 474.1421 | 452.0928
819.218 | 769.218 | 477.1096 | 406.7111 | 362.8976 | 439.5093 | 477.5522 | 457.666
820.2194 | 770.2194 | 476.9394 | 407.8227 | 363.1926 | 441.6468 | 480.8558 | 462.0481
821.2209 | 771.2209 | 476.9185 | 408.4078 | 363.5259 | 443.6959 | 488.4089 | 467.29
822.2223 | 772.2223 | 477.0203 | 409.5136 | 363.8984 | 445.7048 | 491.1283 | 472.3131
823.2237 | 773.2237 | 477.1367 | 410.6603 | 364.2344 | 447.855 | 495.9809 | 478.0573
824.2252 | 774.2252 | 477.1961 | 411.6202 | 364.5746 | 449.8769 | 500.4946 | 482.6861
825.2266 | 775.2266 | 476.9015 | 413.0042 | 364.9459 | 451.7944 | 506.2161 | 488.7103
826.218 | 776.218 | 476.4573 | 413.8924 | 365.2306 | 453.9725 | 518.781 | 494.3586
827.2195 | 777.2195 | 476.0753 | 415.2242 | 365.6409 | 456.0772 | 525.1913 | 498.0568
828.2209 | 778.2209 | 475.7713 | 416.2502 | 366.0663 | 458.2259 | 528.5556 | 501.519
829.2224 | 779.2224 | 475.4984 | 417.5356 | 366.416 | 460.377 | 535.426 | 503.6896
830.2238 | 780.2238 | 475.2248 | 418.6544 | 366.7417 | 462.8 | 552.4289 | 508.9872
831.2252 | 781.2252 | 474.8045 | 419.3862 | 367.0594 | 465.7214 | 558.1142 | 514.5283
832.2167 | 782.2167 | 474.2707 | 420.6816 | 367.4125 | 468.3461 | 565.6279 | 519.0694
833.2181 | 783.2181 | 473.5981 | 421.6229 | 367.7918 | 470.5114 | 584.2821 | 522.7643
834.2195 | 784.2195 | 473.0818 | 422.7916 | 368.1261 | 472.2195 | 596.8734 | 525.8458
835.221 | 785.221 | 472.6527 | 423.7246 | 368.4757 | 473.7374 | 593.185 | 529.45
836.2224 | 786.2224 | 472.3216 | 424.626 | 368.8947 | 475.179 | 602.4673 | 533.4324
837.2239 | 787.2239 | 471.7073 | 425.264 | 369.3397 | 476.463 | 606.0759 | 538.4183
838.2253 | 788.2253 | 471.1129 | 426.3646 | 369.6635 | 477.7091 | 596.4614 | 541.8572
839.2267 | 789.2267 | 470.5713 | 426.755 | 370.0217 | 478.9666 | 591.8384 | 546.5233
840.2182 | 790.2182 | 470.1001 | 427.5161 | 370.508 | 480.3754 | 589.1191 | 551.6071
841.2196 | 791.2196 | 469.6329 | 428.5694 | 370.8905 | 481.6392 | 595.5999 | 556.9121
842.2211 | 792.2211 | 469.1311 | 429.8595 | 371.337 | 482.7563 | 603.8509 | 561.2741
843.2225 | 793.2225 | 468.6801 | 430.5735 | 371.7114 | 483.6374 | 592.5561 | 564.9014
844.2239 | 794.2239 | 468.1432 | 431.2651 | 372.106 | 484.6276 | 582.5911 | 568.5458
845.2254 | 795.2254 | 467.4478 | 432.1321 | 372.5072 | 485.4934 | 574.2681 | 571.4261
846.2168 | 796.2168 | 466.7349 | 432.8185 | 372.8886 | 485.7509 | 573.0599 | 574.6414
847.2182 | 797.2182 | 466.2025 | 433.6776 | 373.2926 | 485.8239 | 574.4068 | 575.1285
848.2197 | 798.2197 | 465.7996 | 434.4625 | 373.7088 | 485.8793 | 571.5959 | 578.281
849.2211 | 799.2211 | 465.53 | 434.9547 | 374.0155 | 486.1087 | 572.2711 | 580.6285
850.2226 | 800.2226 | 465.0234 | 435.6319 | 374.391 | 486.4033 | 566.6067 | 582.2692
851.224 | 801.224 | 464.4898 | 435.9343 | 374.7695 | 486.6894 | 563.2486 | 583.2762
852.2254 | 802.2254 | 464.0147 | 436.9473 | 375.1307 | 487.0113 | 563.5052 | 584.4149
853.2269 | 803.2269 | 463.5572 | 438.0963 | 375.4581 | 487.4387 | 561.9272 | 586.1193
854.2283 | 804.2283 | 462.8845 | 438.5689 | 375.7895 | 487.5516 | 577.8997 | 586.9063
855.2197 | 805.2197 | 462.111 | 439.2756 | 376.1124 | 487.6562 | 591.1687 | 585.2172
856.2212 | 806.2212 | 461.4778 | 440.1307 | 376.4396 | 487.8649 | 610.804 | 585.6866
857.2226 | 807.2226 | 460.9353 | 441.024 | 376.7186 | 487.9643 | 619.005 | 583.8196
858.2241 | 808.2241 | 460.2501 | 441.9594 | 377.0034 | 487.9346 | 636.7592 | 579.28
859.2255 | 809.2255 | 459.6267 | 443.2397 | 377.265 | 488.1303 | 651.8671 | 575.7757
860.2269 | 810.2269 | 458.9105 | 444.6312 | 377.5115 | 488.3451 | 653.9163 | 573.8692
861.2184 | 811.2184 | 458.1287 | 445.9356 | 377.7262 | 488.6079 | 667.6763 | 572.0111
862.2198 | 812.2198 | 457.3264 | 447.353 | 377.9589 | 488.9403 | 679.9788 | 571.405
863.2213 | 813.2213 | 456.7518 | 448.4498 | 378.0908 | 489.4102 | 677.7184 | 571.4731
864.2227 | 814.2227 | 456.2296 | 449.4279 | 378.2685 | 489.9705 | 678.7617 | 572.8949
865.2241 | 815.2241 | 455.6548 | 450.4887 | 378.418 | 490.5654 | 675.2101 | 574.7353
866.2756 | 816.2756 | 455.1413 | 451.6012 | 378.5619 | 491.0889 | 682.5114 | 576.7495
867.217 | 817.217 | 454.726 | 452.5028 | 378.6857 | 491.4287 | 671.3357 | 577.3108
868.2184 | 818.2184 | 454.274 | 453.6031 | 378.8246 | 491.7705 | 675.2682 | 576.6173
869.2199 | 819.2199 | 453.6319 | 454.626 | 378.9355 | 491.995 | 670.9021 | 577.0118
870.2213 | 820.2213 | 452.8594 | 455.5389 | 379.0288 | 491.9897 | 676.8945 | 575.3563
871.2228 | 821.2228 | 452.3603 | 456.656 | 379.124 | 493.0902 | 672.2752 | 574.2194
872.2242 | 822.2242 | 451.8845 | 457.7889 | 379.2728 | 495.079 | 669.9289 | 573.4523
873.2256 | 823.2256 | 451.4509 | 458.8544 | 379.3799 | 496.7506 | 685.7917 | 574.7761
874.2171 | 824.2171 | 451.0324 | 459.7632 | 379.4852 | 498.3906 | 678.6105 | 575.2093
875.2185 | 825.2185 | 450.6579 | 460.6944 | 379.56 | 499.6583 | 675.0015 | 575.2205
876.2199 | 826.2199 | 450.2173 | 461.4355 | 379.6567 | 500.2024 | 671.0979 | 575.8318
877.2214 | 827.2214 | 449.6861 | 462.192 | 379.8093 | 501.0659 | 673.7475 | 576.4484
878.2228 | 828.2228 | 449.0346 | 462.8417 | 379.9078 | 501.7326 | 670.0354 | 573.8101
879.2243 | 829.2243 | 448.4186 | 463.4476 | 380.0637 | 502.2809 | 682.6138 | 568.7838
880.2257 | 830.2257 | 447.86 | 464.1529 | 380.2007 | 502.9057 | 674.4092 | 564.6086
881.2271 | 831.2271 | 447.3433 | 464.7241 | 380.3773 | 503.6367 | 674.2422 | 560.0737
882.2186 | 832.2186 | 446.7295 | 465.1685 | 380.6131 | 504.1877 | 673.9128 | 557.1082
883.22 | 833.22 | 446.1597 | 465.5203 | 380.6998 | 505.1713 | 676.0949 | 555.1077
884.2214 | 834.2214 | 445.4658 | 465.7786 | 380.8599 | 506.1246 | 668.8861 | 554.7234
885.2229 | 835.2229 | 444.7636 | 465.9504 | 381.0649 | 506.8462 | 666.3942 | 553.93
886.2243 | 836.2243 | 444.2473 | 466.1666 | 381.2069 | 506.8219 | 676.0036 | 553.5652
887.2258 | 837.2258 | 443.655 | 466.4814 | 381.3862 | 507.2892 | 680.1216 | 553.0873
888.2172 | 838.2172 | 443.0191 | 466.8102 | 381.5575 | 506.5373 | 678.5024 | 553.3571
889.2186 | 839.2186 | 442.3642 | 467.1231 | 381.7758 | 506.0883 | 670.5259 | 553.7202
890.2201 | 840.2201 | 441.7166 | 467.5152 | 382.0152 | 505.5513 | 667.8689 | 553.6861
891.2215 | 841.2215 | 441.2257 | 467.7964 | 382.3164 | 505.7535 | 664.881 | 554.4566
892.223 | 842.223 | 440.679 | 467.9513 | 382.5775 | 505.6582 | 664.6793 | 555.1082
893.2244 | 843.2244 | 440.1923 | 468.0561 | 382.7355 | 506.2708 | 663.2998 | 555.8886
894.2258 | 844.2258 | 439.6944 | 468.2445 | 382.9854 | 507.2428 | 661.35 | 556.2999
895.2273 | 845.2273 | 439.1345 | 468.2406 | 383.3997 | 507.8317 | 659.4268 | 557.1418
896.2187 | 846.2187 | 438.4717 | 468.4742 | 383.7236 | 508.4611 | 663.8362 | 558.3687
897.2201 | 847.2201 | 437.8245 | 468.5897 | 384.0166 | 508.9866 | 665.1531 | 559.7071
898.2216 | 848.2216 | 437.2814 | 468.8039 | 384.2614 | 509.13 | 663.1829 | 561.1185
899.223 | 849.223 | 436.8637 | 469.0608 | 384.48 | 509.5357 | 658.1842 | 562.6846
900.2245 | 850.2245 | 436.5831 | 469.194 | 384.7592 | 509.5935 | 655.5783 | 564.2961
901.2259 | 851.2259 | 436.1015 | 469.4179 | 385.1002 | 509.7481 | 651.3146 | 565.3627
902.2273 | 852.2273 | 435.5376 | 469.5407 | 385.4172 | 510.3003 | 648.8992 | 565.6984
903.2188 | 853.2188 | 434.8898 | 469.7561 | 385.8131 | 511.3901 | 645.6095 | 566.6407
904.2202 | 854.2202 | 434.2666 | 469.916 | 386.1565 | 512.2842 | 642.1566 | 568.0689
905.2216 | 855.2216 | 433.6674 | 470.13 | 386.4724 | 512.9505 | 639.0077 | 569.3481
906.2231 | 856.2231 | 432.9814 | 470.2183 | 386.9474 | 513.6861 | 636.1286 | 570.0232
907.2245 | 857.2245 | 432.4763 | 470.3529 | 387.2436 | 514.3559 | 632.9728 | 570.2212
908.226 | 858.226 | 432.1487 | 470.3502 | 387.5889 | 515.1552 | 630.5448 | 570.8981
909.2174 | 859.2174 | 431.7157 | 470.1965 | 388.074 | 516.083 | 625.3872 | 572.4748
910.2188 | 860.2188 | 431.1944 | 470.1541 | 388.3349 | 516.972 | 620.0439 | 573.5213
911.2203 | 861.2203 | 430.6423 | 470.2124 | 388.6432 | 517.782 | 614.7385 | 573.9921
912.2217 | 862.2217 | 430.0774 | 470.2958 | 389.1424 | 518.5433 | 610.9085 | 574.7263
913.2232 | 863.2232 | 429.4712 | 470.2115 | 389.5276 | 519.256 | 628.158 | 575.1832
914.2246 | 864.2246 | 428.9299 | 470.1322 | 389.9172 | 519.9184 | 618.6793 | 575.32 | Time of first failure
915.226 | 865.226 | 428.3642 | 470.1271 | 390.375 | 520.6005 | 617.194 | 575.9053 | 864 | 0
916.2175 | 866.2175 | 427.893 | 470.1946 | 390.8547 | 521.2332 | 621.3737 | 576.196 | 864 | 800
917.2189 | 867.2189 | 427.3299 | 470.3657 | 391.2428 | 521.7386 | 613.5599 | 576.5244
918.2203 | 868.2203 | 426.7696 | 470.4579 | 391.5577 | 522.1964 | 609.7958 | 576.7051
919.2218 | 869.2218 | 426.2781 | 470.6136 | 391.9547 | 522.7273 | 608.216 | 577.0671
920.2232 | 870.2232 | 425.7554 | 470.7119 | 392.2243 | 523.1207 | 605.5919 | 578.0813
921.2247 | 871.2247 | 425.1604 | 470.8924 | 392.6261 | 523.5341 | 603.5185 | 578.9596
922.2261 | 872.2261 | 424.6587 | 471.0518 | 393.1479 | 523.9082 | 605.0351 | 579.824
923.2175 | 873.2175 | 424.1557 | 471.0347 | 393.5739 | 524.3244 | 600.2545 | 580.6393
924.219 | 874.219 | 423.5935 | 471.2195 | 394.0375 | 524.858 | 599.1053 | 581.7356
925.2204 | 875.2204 | 422.9936 | 471.5513 | 394.5502 | 525.5099 | 597.6579 | 582.373
926.2218 | 876.2218 | 422.3502 | 471.7159 | 394.9933 | 525.9675 | 601.99 | 583.2847
927.2233 | 877.2233 | 421.8512 | 471.7686 | 395.4479 | 526.3803 | 601.3598 | 583.8131
928.2247 | 878.2247 | 421.3512 | 471.9356 | 395.7714 | 526.8777 | 599.913 | 584.3065
929.2262 | 879.2262 | 420.8473 | 472.2256 | 396.1852 | 527.1269 | 595.1965 | 584.8548
930.2176 | 880.2176 | 420.3525 | 472.374 | 396.6165 | 527.4074 | 588.2021 | 585.8531
931.219 | 881.219 | 419.7845 | 472.5306 | 397.0759 | 527.7468 | 583.2368 | 586.5877
932.2205 | 882.2205 | 419.2158 | 472.595 | 397.6927 | 528.1497 | 580.8453 | 587.1431
933.2219 | 883.2219 | 418.7388 | 472.7804 | 398.2045 | 528.6528 | 576.0531 | 587.9559
934.2233 | 884.2233 | 418.2122 | 473.0211 | 398.6518 | 529.1006 | 570.6351 | 587.7411
935.2248 | 885.2248 | 417.785 | 473.2324 | 399.1614 | 529.4959 | 565.2363 | 587.68
936.2162 | 886.2162 | 417.2782 | 473.4385 | 399.6068 | 529.8442 | 559.8879 | 587.6189
937.2277 | 887.2277 | 416.7616 | 473.7081 | 400.1336 | 530.0558 | 555.4045 | 587.6717
938.2291 | 888.2291 | 416.3477 | 473.9878 | 400.6643 | 530.0945 | 556.5514 | 587.9332
939.2205 | 889.2205 | 415.8267 | 474.3532 | 401.1853 | 530.1867 | 552.8709 | 588.7102
940.222 | 890.222 | 415.4165 | 474.6303 | 401.6659 | 530.1634 | 549.6338 | 588.6978
941.2234 | 891.2234 | 415.1228 | 474.8303 | 402.1518 | 530.0984 | 545.1704 | 588.8203
942.2249 | 892.2249 | 414.6707 | 475.0259 | 402.6454 | 530.1081 | 555.7897 | 588.8979
943.2263 | 893.2263 | 414.1181 | 475.5336 | 403.1789 | 530.287 | 549.7972 | 588.8667
944.2277 | 894.2277 | 413.5786 | 475.8671 | 403.716 | 530.3888 | 548.9344 | 588.4161
945.2192 | 895.2192 | 413.2043 | 476.2158 | 404.221 | 530.4798 | 544.7753 | 588.4216
946.2206 | 896.2206 | 412.6925 | 476.6062 | 404.7093 | 530.5148 | 539.357 | 587.9858
947.222 | 897.222 | 412.1533 | 476.9645 | 405.2556 | 530.5097 | 535.7952 | 587.691
948.2235 | 898.2235 | 411.5531 | 477.4472 | 405.776 | 530.701 | 532.3052 | 587.045
949.2249 | 899.2249 | 411.0552 | 477.9328 | 406.2619 | 530.6759 | 529.84 | 586.3957
950.2264 | 900.2264 | 410.6737 | 478.3084 | 406.7688 | 530.6068 | 528.3731 | 585.6832
951.2178 | 901.2178 | 410.3009 | 478.7163 | 407.3482 | 530.6485 | 525.0442 | 585.9391
952.2192 | 902.2192 | 409.8935 | 479.3242 | 407.9347 | 530.6172 | 520.5135 | 586.2779
953.2207 | 903.2207 | 409.4318 | 479.7864 | 408.6214 | 530.6574 | 515.9191 | 586.4522
954.2221 | 904.2221 | 408.9105 | 480.1232 | 409.2607 | 530.6698 | 514.399 | 585.9732
955.2235 | 905.2235 | 408.5375 | 480.6157 | 409.9245 | 530.7949 | 510.2674 | 585.0123
956.225 | 906.225 | 408.1082 | 481.0375 | 410.5247 | 530.9507 | 507.0443 | 584.3539
957.2164 | 907.2164 | 407.6027 | 481.6009 | 411.1933 | 530.9835 | 513.4898 | 583.811
958.2178 | 908.2178 | 407.0687 | 482.1946 | 411.9106 | 531.1121 | 512.9347 | 583.5003
959.2193 | 909.2193 | 406.5195 | 482.9273 | 412.6661 | 531.1297 | 519.7932 | 583.2285
960.2207 | 910.2207 | 406.0112 | 483.5191 | 413.392 | 531.1977 | 517.0897 | 583.4629
961.2222 | 911.2222 | 405.5957 | 484.0759 | 414.2365 | 531.3129 | 516.6872 | 584.8693
962.2236 | 912.2236 | 405.2063 | 484.7461 | 415.0411 | 531.3741 | 514.7393 | 586.2317
963.225 | 913.225 | 404.7936 | 485.2241 | 415.9057 | 531.4515 | 511.4736 | 586.695
964.2265 | 914.2265 | 404.4296 | 485.8592 | 416.9175 | 531.4888 | 510.8874 | 587.1124
965.2179 | 915.2179 | 403.9039 | 486.37 | 417.9901 | 531.4823 | 507.4468 | 587.6957
966.2194 | 916.2194 | 403.5349 | 486.9612 | 419.0636 | 531.6168 | 505.0545 | 588.2922
967.2208 | 917.2208 | 403.1639 | 487.6407 | 420.1893 | 531.7844 | 500.4313 | 588.7433
968.2222 | 918.2222 | 402.6401 | 488.2924 | 421.3457 | 531.8907 | 497.6089 | 588.7272
969.2237 | 919.2237 | 402.1736 | 488.9948 | 422.554 | 531.9294 | 497.3705 | 589.0742
970.2251 | 920.2251 | 401.707 | 489.5542 | 423.7571 | 532.0609 | 493.9284 | 589.1402
971.2266 | 921.2266 | 401.375 | 490.0745 | 424.9316 | 532.1707 | 490.3231 | 589.7369
972.218 | 922.218 | 401.0992 | 490.6206 | 426.1404 | 532.2857 | 487.9707 | 590.5536
973.2194 | 923.2194 | 400.7252 | 491.2097 | 427.339 | 532.4513 | 488.4277 | 591.3485
974.2209 | 924.2209 | 400.3239 | 491.7454 | 428.5405 | 532.5028 | 487.0411 | 592.1945
975.2223 | 925.2223 | 399.766 | 492.3985 | 429.7394 | 532.5995 | 487.0144 | 592.3236
976.2237 | 926.2237 | 399.3043 | 493.0011 | 430.9201 | 532.7021 | 488.1104 | 592.5768
977.2252 | 927.2252 | 398.8376 | 493.4732 | 432.0515 | 532.795 | 485.7384 | 593.1459
978.2166 | 928.2166 | 398.2975 | 494.0198 | 433.1388 | 532.9368 | 483.7397 | 593.3822
979.218 | 929.218 | 397.9269 | 494.5055 | 434.1956 | 533.1502 | 480.1574 | 593.7405
980.2195 | 930.2195 | 397.6272 | 494.9264 | 435.2092 | 533.4203 | 479.2509 | 593.9317
981.2209 | 931.2209 | 397.3304 | 495.5038 | 436.2491 | 533.7225 | 477.3275 | 594.933
982.2224 | 932.2224 | 396.9471 | 496.1776 | 437.2155 | 534.0844 | 475.3107 | 595.5888
983.2238 | 933.2238 | 396.4847 | 496.7483 | 438.1761 | 534.4715 | 475.596 | 595.624
984.2252 | 934.2252 | 396.0369 | 497.4133 | 439.1104 | 534.8428 | 475.4657 | 594.9103
985.2267 | 935.2267 | 395.5307 | 498.0195 | 440.0026 | 535.1288 | 475.7637 | 594.5979
986.2281 | 936.2281 | 395.1536 | 498.6085 | 440.8789 | 535.2922 | 475.0097 | 593.8865
987.2196 | 937.2196 | 394.7706 | 499.2437 | 441.7123 | 535.3628 | 474.9002 | 592.9342
988.221 | 938.221 | 394.5428 | 499.8826 | 442.5311 | 535.5313 | 473.5049 | 592.0218
989.2224 | 939.2224 | 394.4003 | 500.3671 | 443.4546 | 535.8655 | 471.9896 | 592.0127
990.2239 | 940.2239 | 394.1267 | 500.8777 | 444.3621 | 536.1628 | 471.7034 | 591.8067
991.2253 | 941.2253 | 393.843 | 501.5445 | 445.2245 | 536.5045 | 470.1732 | 592.0742
992.2268 | 942.2268 | 393.4977 | 502.2653 | 446.0285 | 536.9181 | 469.243 | 591.6493
993.2182 | 943.2182 | 393.1234 | 502.9031 | 446.9185 | 537.175 | 469.8731 | 591.7463
994.2196 | 944.2196 | 392.6466 | 503.6091 | 447.8306 | 537.4018 | 469.7923 | 591.7112
995.2211 | 945.2211 | 392.3388 | 504.1973 | 448.799 | 537.5858 | 470.6487 | 592.0155
996.2225 | 946.2225 | 391.9999 | 504.9076 | 449.8593 | 537.7388 | 472.3179 | 591.774
997.2239 | 947.2239 | 391.6849 | 505.5215 | 450.9539 | 538.0232 | 472.5452 | 591.9223
998.2254 | 948.2254 | 391.434 | 506.0672 | 452.0595 | 538.4352 | 471.5696 | 591.8542
999.2168 | 949.2168 | 391.062 | 506.7068 | 453.2714 | 538.9106 | 471.6475 | 591.707
1000.2182 | 950.2182 | 390.6717 | 507.4219 | 454.6081 | 539.4448 | 470.9846 | 591.9116
1001.2197 | 951.2197 | 390.3935 | 508.0372 | 455.9918 | 540.0226 | 472.2149 | 592.2575
1002.2211 | 952.2211 | 390.1128 | 508.5659 | 457.4606 | 540.5966 | 472.8252 | 592.8482
1003.2226 | 953.2226 | 389.8109 | 509.0379 | 459.0493 | 541.0585 | 473.0954 | 593.1668
1004.224 | 954.224 | 389.5546 | 509.5097 | 460.7569 | 541.5944 | 473.6834 | 593.3387
1005.2254 | 955.2254 | 389.2331 | 509.9557 | 462.7748 | 542.2447 | 474.0065 | 593.3786
1006.2269 | 956.2269 | 388.8402 | 510.4057 | 464.6846 | 543.0215 | 475.67 | 593.3684
1007.2183 | 957.2183 | 388.4951 | 510.8976 | 466.6912 | 543.7523 | 478.1827 | 593.2438
1008.2197 | 958.2197 | 388.1874 | 511.377 | 468.3188 | 544.1854 | 480.8873 | 593.0827
1009.2212 | 959.2212 | 387.6488 | 511.919 | 469.5591 | 544.775 | 482.1579 | 592.8201
1010.2226 | 960.2226 | 387.1471 | 512.3628 | 470.4916 | 545.2964 | 486.6653 | 592.4399
1011.2241 | 961.2241 | 386.6348 | 512.8815 | 471.3891 | 546.0316 | 486.3963 | 592.1832
1012.2255 | 962.2255 | 386.144 | 513.3088 | 472.1497 | 546.834 | 484.6556 | 591.9222
1013.2169 | 963.2169 | 385.6405 | 513.7456 | 473.0057 | 547.8245 | 485.5863 | 591.2855
1014.2184 | 964.2184 | 385.1759 | 514.2258 | 473.8782 | 548.9143 | 490.3392 | 590.8235
1015.2198 | 965.2198 | 384.748 | 514.5912 | 474.5292 | 550.2209 | 490.9045 | 590.6754
1016.2213 | 966.2213 | 384.2331 | 514.9847 | 475.5164 | 551.0875 | 498.0731 | 590.1606
1017.2227 | 967.2227 | 383.7945 | 515.2784 | 476.6195 | 551.867 | 498.3744 | 589.9248
1018.2241 | 968.2241 | 383.2564 | 515.7086 | 477.4378 | 552.5817 | 501.9674 | 589.4788
1019.2256 | 969.2256 | 382.8679 | 516.0225 | 478.7404 | 553.2488 | 509.7279 | 589.1068
1020.227 | 970.227 | 382.547 | 516.314 | 480.4315 | 554.0423 | 509.2674 | 588.719
1021.2184 | 971.2184 | 382.215 | 516.7115 | 481.7632 | 554.7047 | 513.9266 | 589.3585
1022.2199 | 972.2199 | 381.8723 | 517.0467 | 483.0942 | 555.1089 | 511.9763 | 589.2561
1023.2213 | 973.2213 | 381.545 | 517.3474 | 483.9597 | 555.5139 | 512.1314 | 588.95
1024.2228 | 974.2228 | 381.3679 | 517.6613 | 484.7496 | 556.149 | 513.8115 | 588.6475
1025.2242 | 975.2242 | 381.1603 | 518.0375 | 485.6519 | 556.4346 | 513.2868 | 588.7347
1026.2256 | 976.2256 | 380.9498 | 518.3955 | 486.4774 | 556.8193 | 513.0918 | 588.7262
1027.2271 | 977.2271 | 380.8355 | 518.8375 | 487.5485 | 557.0397 | 518.0069 | 589.0909
1028.2185 | 978.2185 | 380.6972 | 519.154 | 488.5126 | 557.3378 | 519.5317 | 589.7245
1029.2199 | 979.2199 | 380.5154 | 519.5039 | 489.4679 | 557.4752 | 528.4859 | 590.3943
1030.2214 | 980.2214 | 380.1365 | 519.9404 | 490.5959 | 557.9395 | 537.0109 | 590.5627
1031.2228 | 981.2228 | 379.7673 | 520.1596 | 492.2033 | 558.0624 | 537.4921 | 591.1701
1032.2243 | 982.2243 | 379.357 | 520.5685 | 493.6965 | 558.0129 | 538.3926 | 591.3522
1033.2257 | 983.2257 | 378.9427 | 521.0212 | 495.0231 | 558.0396 | 544.2596 | 591.0166
1034.2271 | 984.2271 | 378.536 | 521.4231 | 496.1674 | 558.3253 | 548.6365 | 590.8511
1035.2186 | 985.2186 | 378.1711 | 521.8581 | 497.1553 | 558.7722 | 556.8125 | 590.5441
1036.22 | 986.22 | 377.8159 | 522.3084 | 498.0714 | 559.4369 | 562.1461 | 590.281
1037.2215 | 987.2215 | 377.4232 | 522.7182 | 498.8436 | 560.0975 | 565.4925 | 590.3127
1038.2229 | 988.2229 | 377.1069 | 523.1825 | 499.6664 | 560.5847 | 566.8495 | 590.4935
1039.2243 | 989.2243 | 376.7082 | 523.6189 | 500.3212 | 560.9781 | 571.9181 | 590.9878
1040.2258 | 990.2258 | 376.2743 | 524.0482 | 501.1248 | 561.3747 | 572.6734 | 591.1218
1041.2172 | 991.2172 | 375.9362 | 524.4677 | 501.8741 | 561.7145 | 580.4044 | 591.2404
1042.2186 | 992.2186 | 375.5055 | 524.8929 | 502.6123 | 562.0462 | 579.8402 | 592.1572
1043.2201 | 993.2201 | 375.1493 | 525.3239 | 503.3295 | 562.3167 | 588.1365 | 592.3071
1044.2215 | 994.2215 | 374.756 | 525.8101 | 504.0479 | 562.6677 | 584.5346 | 592.4176
1045.223 | 995.223 | 374.3794 | 526.2732 | 504.6909 | 563.1037 | 590.9158 | 592.6079
1046.2344 | 996.2344 | 374.1051 | 526.8638 | 505.4006 | 563.416 | 586.6463 | 592.7585
1047.2258 | 997.2258 | 373.9743 | 527.4205 | 506.051 | 563.6275 | 583.2074 | 593.0948
1048.2173 | 998.2173 | 373.7226 | 527.9007 | 506.6768 | 563.8571 | 582.8872 | 593.3328
1049.2187 | 999.2187 | 373.3276 | 528.4504 | 507.3767 | 564.0745 | 596.6113 | 593.4191
1050.2201 | 1000.2201 | 372.8523 | 528.8177 | 508.0913 | 564.2273 | 592.1254 | 593.1337
1051.2216 | 1001.2216 | 372.4553 | 529.2859 | 508.7873 | 564.492 | 604.4791 | 593.0005
1052.223 | 1002.223 | 372.0972 | 529.8301 | 509.5112 | 564.8578 | 609.5651 | 593.0552
1053.2245 | 1003.2245 | 371.8231 | 530.4112 | 510.1937 | 565.2207 | 609.6088 | 593.6432
1054.2259 | 1004.2259 | 371.4853 | 530.8028 | 510.9057 | 565.5519 | 602.9543 | 593.5071
1055.2273 | 1005.2273 | 371.1406 | 531.5083 | 511.5753 | 565.863 | 618.4378 | 593.3306
1056.2188 | 1006.2188 | 370.7984 | 531.9692 | 512.2546 | 566.0994 | 622.0241 | 592.3951
1057.2202 | 1007.2202 | 370.5319 | 532.3975 | 512.7959 | 566.2776 | 618.6056 | 592.3577
1058.2216 | 1008.2216 | 370.2852 | 532.9887 | 513.3757 | 566.2582 | 631.9128 | 592.5487
1059.2231 | 1009.2231 | 370.12 | 533.3969 | 513.9895 | 566.1585 | 653.1609 | 592.771
1060.2245 | 1010.2245 | 369.8738 | 533.7772 | 514.4974 | 566.2018 | 647.3353 | 592.939
1061.226 | 1011.226 | 369.7082 | 534.1955 | 515.071 | 566.4314 | 664.6583 | 592.6825
1062.2174 | 1012.2174 | 369.4112 | 534.6454 | 515.5347 | 566.6631 | 673.0452 | 592.0252
1063.2188 | 1013.2188 | 369.1417 | 535.1045 | 516.0743 | 566.6903 | 653.6411 | 591.4405
1064.2203 | 1014.2203 | 368.8746 | 535.4996 | 516.6332 | 566.4846 | 647.2569 | 590.8593
1065.2217 | 1015.2217 | 368.6093 | 535.8954 | 517.1953 | 566.2399 | 643.7922 | 591.0499
1066.2232 | 1016.2232 | 368.4081 | 536.2081 | 517.7622 | 566.0853 | 641.3057 | 590.9836
1067.2246 | 1017.2246 | 368.2133 | 536.4777 | 518.3292 | 566.0346 | 646.2882 | 591.4405
1068.216 | 1018.216 | 368.0436 | 536.8306 | 518.8489 | 566.0062 | 652.4602 | 592.3939
1069.2275 | 1019.2275 | 367.839 | 537.1363 | 519.3791 | 565.8374 | 659.6158 | 592.6826
1070.2189 | 1020.2189 | 367.6807 | 537.4836 | 519.9034 | 565.686 | 664.2351 | 592.826
1071.2203 | 1021.2203 | 367.5263 | 537.7391 | 520.3675 | 565.545 | 664.5169 | 592.9257
1072.2218 | 1022.2218 | 367.4336 | 538.0039 | 520.8961 | 565.5392 | 662.0978 | 593.8732
1073.2232 | 1023.2232 | 367.2361 | 538.2466 | 521.3912 | 565.5777 | 661.1392 | 594.2759
1074.2247 | 1024.2247 | 367.0925 | 538.5047 | 521.8996 | 565.6348 | 664.3416 | 595.8198
1075.2261 | 1025.2261 | 366.9502 | 538.8244 | 522.4156 | 565.65 | 656.2957 | 596.1653
1076.2275 | 1026.2275 | 366.7934 | 539.1994 | 522.9212 | 565.6167 | 678.1892 | 596.8732
1077.219 | 1027.219 | 366.6214 | 539.6895 | 523.4034 | 565.5135 | 666.413 | 596.9893
1078.2204 | 1028.2204 | 366.3239 | 540.1036 | 523.8753 | 565.3454 | 667.5904 | 596.3791
1079.2218 | 1029.2218 | 365.9977 | 540.4725 | 524.3048 | 565.1235 | 673.2162 | 595.7759
1080.2233 | 1030.2233 | 365.5623 | 540.7709 | 524.7434 | 564.8676 | 665.539 | 596.4917
1081.2247 | 1031.2247 | 365.2364 | 541.0543 | 525.1062 | 564.675 | 658.9753 | 597.1212
1082.2262 | 1032.2262 | 364.9072 | 541.3143 | 525.4269 | 564.5226 | 662.0856 | 597.264
1083.2176 | 1033.2176 | 364.5704 | 541.4831 | 525.7587 | 564.4387 | 660.4879 | 597.8555
1084.219 | 1034.219 | 364.2508 | 541.6929 | 526.0669 | 564.4051 | 661.0407 | 598.238
1085.2205 | 1035.2205 | 363.8727 | 541.8263 | 526.371 | 564.3737 | 665.0504 | 598.3916
1086.2219 | 1036.2219 | 363.516 | 542.1701 | 526.6558 | 564.4063 | 662.1533 | 598.0175
1087.2234 | 1037.2234 | 363.082 | 542.3132 | 526.9177 | 564.4339 | 665.6591 | 597.1032
1088.2248 | 1038.2248 | 362.7349 | 542.6217 | 527.2116 | 564.3938 | 666.127 | 597.8133
1089.2162 | 1039.2162 | 362.5074 | 542.9264 | 527.4709 | 564.2689 | 670.7757 | 597.8873
1090.2177 | 1040.2177 | 362.0617 | 543.1973 | 527.7026 | 564.0871 | 691.0588 | 597.158
1091.2191 | 1041.2191 | 361.5712 | 543.3785 | 527.9312 | 564.1589 | 701.9227 | 596.3927
1092.2205 | 1042.2205 | 361.1002 | 543.6975 | 528.1489 | 564.1701 | 694.325 | 595.3655
1093.222 | 1043.222 | 360.606 | 543.9607 | 528.3341 | 564.1208 | 683.5064 | 595.1176
1094.2234 | 1044.2234 | 360.1338 | 544.1437 | 528.4989 | 563.9335 | 697.1608 | 594.9646
1095.2249 | 1045.2249 | 359.607 | 544.3104 | 528.6717 | 563.6692 | 706.0723 | 595.1629
1096.2163 | 1046.2163 | 359.2304 | 544.4615 | 528.8153 | 563.43 | 701.4185 | 594.433
1097.2177 | 1047.2177 | 358.9699 | 544.605 | 528.9669 | 563.1512 | 690.0798 | 594.2565
1098.2192 | 1048.2192 | 358.763 | 544.819 | 529.1077 | 562.844 | 686.2002 | 594.4541
1099.2206 | 1049.2206 | 358.4773 | 545.0069 | 529.3314 | 562.7217 | 677.1484 | 595.3355
1100.222 | 1050.222 | 358.1717 | 545.2212 | 529.5192 | 562.7248 | 681.4305 | 595.7516
1101.2235 | 1051.2235 | 357.7803 | 545.4233 | 529.6599 | 562.8392 | 687.217 | 595.2452
1102.2249 | 1052.2249 | 357.4055 | 545.657 | 529.9138 | 562.9878 | 698.0004 | 595.3204
1103.2264 | 1053.2264 | 357.0153 | 545.7867 | 530.1855 | 563.1902 | 689.4398 | 595.4192
1104.2178 | 1054.2178 | 356.5854 | 545.9329 | 530.4111 | 563.2474 | 675.9142 | 595.7503
1105.2192 | 1055.2192 | 356.2024 | 546.0507 | 530.6546 | 562.6575 | 669.7772 | 596.0253
1106.2207 | 1056.2207 | 355.8155 | 546.2329 | 530.906 | 561.6167 | 665.5254 | 596.744
1107.2221 | 1057.2221 | 355.5319 | 546.4693 | 531.1421 | 560.6033 | 659.3345 | 597.3028
1108.2235 | 1058.2235 | 355.293 | 546.7012 | 531.3999 | 559.5607 | 673.4338 | 597.0259
1109.225 | 1059.225 | 354.9538 | 546.8483 | 531.6485 | 558.1528 | 665.8508 | 597.1508
1110.2264 | 1060.2264 | 354.5823 | 547.1262 | 531.9073 | 556.9132 | 667.3493 | 597.4502
1111.2279 | 1061.2279 | 354.2368 | 547.4308 | 532.1675 | 555.421 | 665.0527 | 596.9103
1112.2193 | 1062.2193 | 353.9281 | 547.5567 | 532.4359 | 554.048 | 654.7269 | 596.9666
1113.2207 | 1063.2207 | 353.5899 | 547.8579 | 532.7138 | 552.5425 | 653.5469 | 597.3763
1114.2222 | 1064.2222 | 353.1868 | 548.1768 | 532.9807 | 551.3965 | 667.5411 | 597.2602
1115.2236 | 1065.2236 | 352.8021 | 548.4963 | 533.2456 | 550.278 | 680.5416 | 596.26
1116.2251 | 1066.2251 | 352.3936 | 548.695 | 533.569 | 549.5818 | 691.0923 | 595.3627
1117.2265 | 1067.2265 | 352.0238 | 548.9096 | 533.8359 | 548.5304 | 689.66 | 594.9462
1118.2279 | 1068.2279 | 351.5786 | 549.1544 | 534.13 | 547.851 | 692.839 | 595.094
1119.2194 | 1069.2194 | 351.1889 | 549.4505 | 534.4271 | 547.1295 | 690.1301 | 594.7501
1120.2208 | 1070.2208 | 350.8762 | 549.7049 | 534.7254 | 546.7066 | 697.1525 | 594.4478
1121.2222 | 1071.2222 | 350.5268 | 549.9839 | 535.0412 | 545.9835 | 673.0813 | 594.0225
1122.2237 | 1072.2237 | 350.1889 | 550.4428 | 535.3673 | 545.7998 | 672.914 | 593.373
1123.2251 | 1073.2251 | 349.8156 | 550.8754 | 535.6806 | 545.6126 | 684.3007 | 592.7855
1124.2266 | 1074.2266 | 349.5229 | 551.0982 | 535.9843 | 545.4268 | 679.1528 | 593.6172
1125.218 | 1075.218 | 349.3106 | 551.4658 | 536.2765 | 545.2733 | 671.3504 | 592.3171
1126.2194 | 1076.2194 | 349.0902 | 551.941 | 536.5409 | 545.0611 | 663.2598 | 591.6702
1127.2209 | 1077.2209 | 348.7594 | 552.3489 | 536.8275 | 545.0064 | 676.8198 | 591.4852
1128.2223 | 1078.2223 | 348.421 | 552.8382 | 537.1458 | 544.552 | 659.4972 | 590.8454
1129.2237 | 1079.2237 | 348.0147 | 553.3154 | 537.4801 | 544.0579 | 650.7553 | 590.0313
1130.2252 | 1080.2252 | 347.529 | 553.8055 | 537.8029 | 543.6768 | 679.782 | 589.6513
1131.2266 | 1081.2266 | 347.0759 | 554.2556 | 538.0982 | 543.2817 | 666.8297 | 589.12
1132.218 | 1082.218 | 346.648 | 554.6058 | 538.4105 | 543.263 | 658.4699 | 588.7549
1133.2195 | 1083.2195 | 346.2615 | 555.0171 | 538.7461 | 543.061 | 670.5793 | 588.6857
1134.2209 | 1084.2209 | 345.9711 | 555.3754 | 539.0789 | 542.7193 | 661.5872 | 587.6751
1135.2224 | 1085.2224 | 345.6064 | 555.8461 | 539.418 | 542.5431 | 664.4914 | 587.4714
1136.2238 | 1086.2238 | 345.1999 | 556.2937 | 539.7539 | 542.4005 | 670.3549 | 586.6104
1137.2252 | 1087.2252 | 344.9345 | 556.7059 | 540.1177 | 542.3343 | 670.333 | 586.3793
1138.2167 | 1088.2167 | 344.7139 | 557.0662 | 540.4498 | 542.1035 | 656.8647 | 586.3053
1139.2181 | 1089.2181 | 344.4334 | 557.4844 | 540.7987 | 541.8765 | 643.9456 | 585.9125
1140.2196 | 1090.2196 | 344.1385 | 557.9333 | 541.1767 | 541.6354 | 627.9123 | 585.867
1141.221 | 1091.221 | 343.8725 | 558.4402 | 541.5418 | 541.7091 | 628.8852 | 586.1646
1142.2224 | 1092.2224 | 343.5665 | 558.9891 | 541.8916 | 541.5641 | 618.2613 | 585.6243
1143.2239 | 1093.2239 | 343.2718 | 559.4374 | 542.2693 | 541.6595 | 619.3342 | 584.7836
1144.2253 | 1094.2253 | 343.0325 | 559.9154 | 542.6271 | 542.0092 | 606.6128 | 583.8629
1145.2268 | 1095.2268 | 342.7166 | 560.4557 | 542.9893 | 542.121 | 595.741 | 583.4856
1146.2182 | 1096.2182 | 342.4459 | 560.946 | 543.3444 | 542.1549 | 597.4577 | 583.022
1147.2196 | 1097.2196 | 342.1329 | 561.5212 | 543.69 | 542.0161 | 595.5808 | 582.6823
1148.2211 | 1098.2211 | 341.7732 | 562.1452 | 544.063 | 542.1955 | 592.7468 | 582.5017
1149.2225 | 1099.2225 | 341.3504 | 562.7331 | 544.431 | 542.8109 | 602.03 | 582.3105
1150.2239 | 1100.2239 | 340.9197 | 563.3726 | 544.8006 | 542.7583 | 610.7394 | 582.2384
1151.2254 | 1101.2254 | 340.5028 | 563.9943 | 545.1953 | 542.7454 | 606.0737 | 581.8786
1152.2268 | 1102.2268 | 340.1518 | 564.5821 | 545.5681 | 543.0294 | 604.4676 | 580.9151
1153.2182 | 1103.2182 | 339.6297 | 565.1381 | 545.9868 | 543.1795 | 594.9832 | 580.5178
1154.2197 | 1104.2197 | 339.1017 | 565.7101 | 546.3814 | 543.1597 | 587.0837 | 580.2371
1155.2211 | 1105.2211 | 338.6395 | 566.1987 | 546.7604 | 543.2556 | 588.1305 | 580.3411
1156.2226 | 1106.2226 | 338.2275 | 566.6814 | 547.1899 | 543.2238 | 586.1464 | 579.7768
1157.224 | 1107.224 | 337.8147 | 567.1005 | 547.5938 | 543.2631 | 581.7042 | 579.005
1158.2254 | 1108.2254 | 337.3472 | 567.4756 | 548.0052 | 543.2739 | 575.8059 | 578.3893
1159.2269 | 1109.2269 | 336.9202 | 567.8625 | 548.4167 | 543.3386 | 570.254 | 577.9589
1160.2283 | 1110.2283 | 336.505 | 568.2366 | 548.8227 | 543.4082 | 567.8141 | 578.0957
1161.2198 | 1111.2198 | 336.1644 | 568.5848 | 549.2152 | 543.4393 | 564.9978 | 577.4157
1162.2212 | 1112.2212 | 335.792 | 568.9122 | 549.5986 | 543.574 | 557.7029 | 576.5291
1163.2226 | 1113.2226 | 335.4747 | 569.2864 | 549.9682 | 543.8226 | 548.2122 | 575.4931
1164.2241 | 1114.2241 | 335.2006 | 569.6716 | 550.3461 | 544.1947 | 539.0545 | 575.0201
1165.2255 | 1115.2255 | 334.9691 | 570.0708 | 550.7679 | 544.3667 | 527.4161 | 574.3912
1166.227 | 1116.227 | 334.7298 | 570.5147 | 551.1784 | 544.5174 | 515.7892 | 573.9935
1167.2184 | 1117.2184 | 334.3396 | 571.0686 | 551.5865 | 544.8728 | 506.5286 | 573.4581
1168.2198 | 1118.2198 | 334.0078 | 571.6214 | 552.0113 | 544.9433 | 498.6482 | 572.7573
1169.2213 | 1119.2213 | 333.7287 | 572.1779 | 552.4446 | 545.1128 | 488.5458 | 572.0943
1170.2227 | 1120.2227 | 333.4417 | 572.7246 | 552.8619 | 545.2118 | 481.292 | 571.6119
1171.2241 | 1121.2241 | 333.2345 | 573.2504 | 553.2744 | 545.4397 | 472.3521 | 570.4994
1172.2256 | 1122.2256 | 332.9832 | 573.7811 | 553.7229 | 545.5279 | 465.3242 | 570.073
1173.217 | 1123.217 | 332.6748 | 574.3772 | 554.1467 | 545.4853 | 458.8174 | 569.3888
1174.2184 | 1124.2184 | 332.2788 | 574.9557 | 554.5873 | 545.5183 | 453.0676 | 568.0319
1175.2199 | 1125.2199 | 331.8471 | 575.453 | 555.0169 | 545.5981 | 449.4943 | 567.0229
1176.2213 | 1126.2213 | 331.4651 | 575.9043 | 555.4893 | 545.9186 | 445.4886 | 566.4181
1177.2228 | 1127.2228 | 331.0568 | 576.3178 | 555.904 | 546.048 | 441.9898 | 564.7507
1178.2242 | 1128.2242 | 330.5691 | 576.7089 | 556.3465 | 546.1917 | 440.4012 | 563.5696
1179.2256 | 1129.2256 | 330.0924 | 577.1036 | 556.7858 | 546.3257 | 437.2097 | 562.5903
1180.2171 | 1130.2171 | 329.6814 | 577.5322 | 557.2357 | 546.516 | 433.971 | 562.348
1181.2185 | 1131.2185 | 329.2179 | 577.9338 | 557.675 | 546.4428 | 430.6233 | 560.7326
1182.2199 | 1132.2199 | 328.7195 | 578.2995 | 558.1229 | 546.4283 | 425.4554 | 559.248
1183.2214 | 1133.2214 | 328.2772 | 578.65 | 558.5839 | 546.616 | 421.2567 | 557.5508
1184.2228 | 1134.2228 | 327.945 | 579.0228 | 559.0407 | 546.7711 | 418.9107 | 556.0516
1185.2243 | 1135.2243 | 327.5998 | 579.4526 | 559.4886 | 546.9646 | 416.9903 | 555.253
1186.2257 | 1136.2257 | 327.3152 | 579.907 | 559.9656 | 547.1068 | 413.3844 | 553.6259
1187.2271 | 1137.2271 | 326.9229 | 580.3353 | 560.4265 | 547.1672 | 410.7909 | 551.821
1188.2186 | 1138.2186 | 326.4913 | 580.7211 | 560.8812 | 547.4487 | 409.4094 | 550.5516
1189.22 | 1139.22 | 326.1604 | 581.095 | 561.3371 | 547.7573 | 407.068 | 549.2102
1190.2215 | 1140.2215 | 325.7741 | 581.4891 | 561.7726 | 548.2111 | 406.5531 | 547.8748
1191.2229 | 1141.2229 | 325.4416 | 581.9314 | 562.2382 | 548.6765 | 404.2002 | 546.4825
1192.2243 | 1142.2243 | 325.1895 | 582.3895 | 562.6862 | 549.1336 | 403.83 | 545.4927
1193.2158 | 1143.2158 | 324.8224 | 582.9374 | 563.1429 | 549.2666 | 402.7677 | 544.2656
1194.2172 | 1144.2172 | 324.4079 | 583.5119 | 563.6016 | 549.3504 | 401.9267 | 543.5978
1195.2186 | 1145.2186 | 323.9903 | 584.055 | 564.0591 | 549.2559 | 399.6254 | 542.8551
1196.2201 | 1146.2201 | 323.5927 | 584.5548 | 564.5186 | 549.524 | 398.1645 | 541.7758
1197.2215 | 1147.2215 | 323.1651 | 585.095 | 564.9529 | 549.9932 | 396.8366 | 540.3797
1198.223 | 1148.223 | 322.7897 | 585.627 | 565.4018 | 550.3084 | 395.2438 | 539.2499
1199.2244 | 1149.2244 | 322.4471 | 586.1473 | 565.8564 | 550.7306 | 393.7941 | 537.9068
1200.2258 | 1150.2258 | 322.2099 | 586.62 | 566.3133 | 551.183 | 392.5482 | 536.5002
1201.2273 | 1151.2273 | 322.0373 | 587.0362 | 566.7505 | 551.5402 | 391.8573 | 535.0512
1202.2187 | 1152.2187 | 321.8085 | 587.5046 | 567.2272 | 551.7648 | 391.6568 | 533.8206
1203.2201 | 1153.2201 | 321.5272 | 588.0332 | 567.6641 | 551.9267 | 391.1992 | 532.639
1204.2216 | 1154.2216 | 321.2779 | 588.5569 | 568.1401 | 551.9663 | 389.4151 | 531.2787
1205.223 | 1155.223 | 321.0262 | 589.0408 | 568.5715 | 552.1506 | 386.9376 | 529.8269
1206.2245 | 1156.2245 | 320.7412 | 589.6006 | 569.0128 | 552.6491 | 385.0291 | 528.4962
1207.2259 | 1157.2259 | 320.3792 | 590.2348 | 569.4537 | 553.0523 | 383.9325 | 527.3306
1208.2273 | 1158.2273 | 320.0938 | 590.8569 | 569.8784 | 553.6336 | 382.9654 | 526.2495
1209.2188 | 1159.2188 | 319.827 | 591.4989 | 570.3502 | 554.1009 | 382.9073 | 525.2562
1210.2202 | 1160.2202 | 319.6007 | 592.0603 | 570.7859 | 554.9442 | 381.7456 | 524.2308
1211.2217 | 1161.2217 | 319.2693 | 592.6525 | 571.2607 | 555.3517 | 381.7079 | 523.2992
1212.2231 | 1162.2231 | 318.9299 | 593.2828 | 571.7412 | 555.5955 | 381.2081 | 522.2342
1213.2245 | 1163.2245 | 318.6254 | 593.8594 | 572.2247 | 555.8655 | 380.0582 | 521.1611
1214.216 | 1164.216 | 318.2447 | 594.315 | 572.711 | 556.055 | 378.1841 | 520.0277
1215.2174 | 1165.2174 | 317.8716 | 594.7001 | 573.1931 | 556.4077 | 377.0019 | 519.0047
1216.2188 | 1166.2188 | 317.533 | 595.0533 | 573.7111 | 556.7057 | 375.615 | 517.7384
1217.2203 | 1167.2203 | 317.2226 | 595.4172 | 574.177 | 556.8382 | 375.416 | 516.548
1218.2217 | 1168.2217 | 316.8697 | 595.8079 | 574.6409 | 557.9093 | 374.1573 | 515.2555
1219.2232 | 1169.2232 | 316.4621 | 596.2319 | 575.0701 | 558.8317 | 373.0358 | 513.8999
1220.2246 | 1170.2246 | 316.0388 | 596.6854 | 575.5253 | 559.1535 | 372.0632 | 512.5398
1221.226 | 1171.226 | 315.735 | 597.1533 | 575.9646 | 559.4822 | 372.7024 | 511.1268
1222.2175 | 1172.2175 | 315.4319 | 597.5993 | 576.3962 | 559.7605 | 371.3384 | 509.9102
1223.2189 | 1173.2189 | 315.1653 | 598.0161 | 576.8367 | 559.8455 | 369.7948 | 508.6179
1224.2203 | 1174.2203 | 314.8782 | 598.4329 | 577.2859 | 560.143 | 369.6046 | 507.3582
1225.2218 | 1175.2218 | 314.5553 | 598.8078 | 577.713 | 560.2636 | 369.9758 | 506.1389
1226.2232 | 1176.2232 | 314.209 | 599.1592 | 578.1401 | 560.3569 | 370.8319 | 505.1218
1227.3649 | 1177.3649 | 313.8081 | 599.5849 | 578.624 | 560.5782 | 370.4142 | 503.837
1228.2261 | 1178.2261 | 313.605 | 599.8798 | 578.9758 | 560.6265 | 370.1504 | 502.9709
1229.2275 | 1179.2275 | 313.3188 | 600.1334 | 579.4 | 561.0294 | 369.7976 | 501.8753
1230.219 | 1180.219 | 313.0221 | 600.3948 | 579.8134 | 561.421 | 369.2819 | 500.9167
1231.2204 | 1181.2204 | 312.679 | 600.8625 | 580.2319 | 561.7745 | 368.8172 | 499.9834
1232.2218 | 1182.2218 | 312.3388 | 601.4678 | 580.6314 | 562.0939 | 368.4714 | 499.2085
1233.2233 | 1183.2233 | 311.9487 | 602.0355 | 581.051 | 562.2432 | 369.2041 | 498.2723
1234.2247 | 1184.2247 | 311.5971 | 602.5148 | 581.4321 | 562.3191 | 369.0844 | 497.3482
1235.2262 | 1185.2262 | 311.2619 | 602.9667 | 581.8667 | 562.4503 | 368.6814 | 496.2209
1236.2176 | 1186.2176 | 310.7735 | 603.4131 | 582.3004 | 562.8454 | 367.4568 | 495.3494
1237.219 | 1187.219 | 310.296 | 603.7991 | 582.6693 | 562.9626 | 366.012 | 494.3731
1238.2205 | 1188.2205 | 309.8675 | 604.1529 | 583.0698 | 563.0143 | 363.2532 | 493.5112
1239.2219 | 1189.2219 | 309.5383 | 604.4778 | 583.4886 | 563.2153 | 363.283 | 492.5499
1240.2234 | 1190.2234 | 309.1631 | 604.745 | 583.8854 | 563.6196 | 364.3528 | 491.9058
1241.2248 | 1191.2248 | 308.7129 | 605.0482 | 584.2881 | 563.9136 | 365.8912 | 491.2317
1242.2262 | 1192.2262 | 308.2126 | 605.399 | 584.6951 | 564.3144 | 365.1595 | 490.4585
1243.2277 | 1193.2277 | 307.7178 | 605.761 | 585.0846 | 564.4982 | 362.9191 | 489.826
1244.2191 | 1194.2191 | 307.2636 | 606.1321 | 585.4724 | 565.1899 | 361.6571 | 489.1043
1245.2205 | 1195.2205 | 306.9146 | 606.4696 | 585.8696 | 565.4446 | 361.47 | 488.4215
1246.222 | 1196.222 | 306.6654 | 606.7611 | 586.2658 | 566.0329 | 360.7869 | 487.5959
1247.2234 | 1197.2234 | 306.4537 | 607.0082 | 586.6447 | 566.425 | 359.9527 | 486.8295
1248.2249 | 1198.2249 | 306.1758 | 607.2628 | 587.048 | 566.7068 | 357.8022 | 485.9072
1249.2263 | 1199.2263 | 305.9443 | 607.6046 | 587.4406 | 567.0967 | 356.3242 | 485.1254
1250.2177 | 1200.2177 | 305.6273 | 607.9952 | 587.8116 | 567.2245 | 355.4046 | 484.5153
1251.2192 | 1201.2192 | 305.2627 | 608.4256 | 588.2052 | 567.2821 | 354.6872 | 483.8636
1252.2206 | 1202.2206 | 304.9138 | 608.9298 | 588.5955 | 567.56 | 354.0024 | 483.2424
1253.222 | 1203.222 | 304.5258 | 609.391 | 588.9866 | 567.8085 | 353.7205 | 482.5388
1254.2235 | 1204.2235 | 304.0769 | 609.7364 | 589.3782 | 568.3152 | 354.3394 | 481.9153
1255.2249 | 1205.2249 | 303.7679 | 610.023 | 589.7679 | 568.5632 | 353.8171 | 481.3531
1256.2164 | 1206.2164 | 303.4664 | 610.3033 | 590.1817 | 568.8873 | 353.5054 | 480.7661
1257.2178 | 1207.2178 | 303.0541 | 610.5068 | 590.5892 | 568.8341 | 354.299 | 480.1768
1258.2192 | 1208.2192 | 302.6729 | 610.7334 | 591.0004 | 569.1277 | 353.5108 | 479.4456
1259.2207 | 1209.2207 | 302.3871 | 611.1224 | 591.3861 | 569.2696 | 352.8209 | 478.8133
1260.2221 | 1210.2221 | 302.0112 | 611.5498 | 591.7917 | 569.5462 | 352.0284 | 478.2441
1261.2236 | 1211.2236 | 301.7457 | 611.9211 | 592.1607 | 569.8777 | 352.1584 | 477.5615
1262.225 | 1212.225 | 301.4732 | 612.2912 | 592.4956 | 570.4115 | 352.0505 | 476.9401
1263.2164 | 1213.2164 | 301.0943 | 612.6289 | 592.8862 | 570.694 | 351.7922 | 476.2712
1264.2179 | 1214.2179 | 300.7618 | 612.9152 | 593.2736 | 570.9262 | 349.6471 | 475.7776
1265.2193 | 1215.2193 | 300.4602 | 613.1787 | 593.6573 | 571.0192 | 347.575 | 475.2688
1266.2207 | 1216.2207 | 300.1738 | 613.4464 | 594.0553 | 570.9691 | 348.1574 | 474.5681
1267.2222 | 1217.2222 | 299.8795 | 613.6921 | 594.4487 | 571.1347 | 347.1788 | 474.0179
1268.2236 | 1218.2236 | 299.5612 | 613.9461 | 594.8102 | 571.0952 | 347.9778 | 473.4439
1269.2251 | 1219.2251 | 299.2505 | 614.218 | 595.2275 | 571.204 | 346.5521 | 472.822
1270.2265 | 1220.2265 | 298.9702 | 614.4548 | 595.6016 | 571.749 | 345.6008 | 472.218
1271.2279 | 1221.2279 | 298.6877 | 614.7739 | 595.9545 | 572.0884 | 344.1593 | 471.7031
1272.2194 | 1222.2194 | 298.4357 | 615.1642 | 596.3034 | 572.6205 | 344.2661 | 471.1174
1273.2208 | 1223.2208 | 298.2231 | 615.5272 | 596.6543 | 572.9315 | 342.5993 | 470.7271
1274.2222 | 1224.2222 | 298.0459 | 615.8484 | 597.0369 | 573.2967 | 342.6769 | 470.2508
1275.2237 | 1225.2237 | 297.7302 | 616.1704 | 597.4027 | 573.3731 | 342.8095 | 469.9201
1276.2251 | 1226.2251 | 297.3262 | 616.5177 | 597.7255 | 573.454 | 342.0099 | 469.4038
1277.2266 | 1227.2266 | 296.9222 | 616.7953 | 598.0231 | 573.6615 | 341.8472 | 468.9921
1278.218 | 1228.218 | 296.6312 | 617.1002 | 598.3241 | 574.0451 | 340.7997 | 468.4764
1279.2194 | 1229.2194 | 296.3794 | 617.342 | 598.6307 | 574.6389 | 340.1587 | 468.1145
1280.2209 | 1230.2209 | 296.1144 | 617.6953 | 598.929 | 574.7473 | 338.1976 | 467.8262
1281.2223 | 1231.2223 | 295.8941 | 618.0118 | 599.2061 | 574.7295 | 337.2606 | 467.4018
1282.2237 | 1232.2237 | 295.5321 | 618.3986 | 599.4963 | 575.2889 | 336.2994 | 466.9223
1283.2252 | 1233.2252 | 295.1137 | 618.64 | 599.8181 | 575.3773 | 335.4486 | 466.6856
1284.2266 | 1234.2266 | 294.6607 | 618.7853 | 600.0997 | 575.1378 | 336.6354 | 466.1822
1285.2281 | 1235.2281 | 294.3193 | 619.0084 | 600.3707 | 575.091 | 334.8988 | 465.9987
1286.2195 | 1236.2195 | 293.9925 | 619.3759 | 600.6969 | 575.0528 | 334.5811 | 465.5752
1287.2209 | 1237.2209 | 293.6261 | 619.73 | 600.9941 | 575.1938 | 335.532 | 465.2837
1288.2224 | 1238.2224 | 293.21 | 620.0487 | 601.3064 | 575.5032 | 334.0845 | 464.9447
1289.2238 | 1239.2238 | 292.9054 | 620.3498 | 601.6371 | 575.9496 | 335.1357 | 464.5882
1290.2253 | 1240.2253 | 292.6627 | 620.7097 | 601.9488 | 576.3003 | 335.2092 | 464.3139
1291.2267 | 1241.2267 | 292.3081 | 621.1388 | 602.2261 | 576.6219 | 334.0604 | 464.1345
1292.2281 | 1242.2281 | 291.9513 | 621.4719 | 602.4995 | 576.8994 | 331.8924 | 463.8086
1293.2196 | 1243.2196 | 291.5994 | 621.8245 | 602.7478 | 576.8816 | 330.9008 | 463.5378
1294.221 | 1244.221 | 291.3445 | 622.1815 | 603.0204 | 576.9622 | 330.1981 | 463.3994
1295.2224 | 1245.2224 | 291.1019 | 622.5683 | 603.2797 | 577.5579 | 329.5787 | 463.0653
1296.2239 | 1246.2239 | 290.8295 | 622.9361 | 603.5403 | 577.6101 | 328.4185 | 462.8417
1297.2253 | 1247.2253 | 290.4698 | 623.1593 | 603.8245 | 577.4503 | 328.427 | 462.4919
1298.2268 | 1248.2268 | 290.1291 | 623.267 | 604.0911 | 577.5097 | 328.2853 | 462.324
1299.2182 | 1249.2182 | 289.8797 | 623.4318 | 604.3615 | 577.5683 | 327.341 | 462.1102
1300.2196 | 1250.2196 | 289.6589 | 623.6268 | 604.6109 | 577.8341 | 327.7798 | 461.7311
1301.2211 | 1251.2211 | 289.375 | 623.8966 | 604.8666 | 577.8238 | 326.5684 | 461.5967
1302.2225 | 1252.2225 | 289.1504 | 624.1879 | 605.1397 | 577.7736 | 326.3604 | 461.3778
1303.2239 | 1253.2239 | 288.9657 | 624.6432 | 605.4165 | 578.024 | 326.1916 | 461.2
1304.2254 | 1254.2254 | 288.7376 | 624.9577 | 605.6853 | 578.1774 | 325.4965 | 460.9761
1305.2168 | 1255.2168 | 288.494 | 625.4067 | 605.9833 | 578.5056 | 324.278 | 460.7385
1306.2182 | 1256.2182 | 288.2115 | 625.887 | 606.2381 | 578.7238 | 324.6263 | 460.647
1307.2197 | 1257.2197 | 287.8303 | 626.2331 | 606.5057 | 578.9216 | 321.966 | 460.6019
1308.2211 | 1258.2211 | 287.5148 | 626.3675 | 606.7913 | 579.0154 | 321.4968 | 460.3802
1309.2226 | 1259.2226 | 287.2046 | 626.558 | 607.0295 | 579.0962 | 320.1168 | 460.1739
1310.224 | 1260.224 | 286.8923 | 626.7274 | 607.3079 | 579.2575 | 320.1564 | 459.889
1311.2254 | 1261.2254 | 286.5575 | 626.9028 | 607.5855 | 579.3668 | 320.8752 | 459.7902
1312.2269 | 1262.2269 | 286.1921 | 627.0319 | 607.848 | 579.7415 | 318.5243 | 459.3885
1313.2283 | 1263.2283 | 285.8415 | 627.1814 | 608.0982 | 579.8326 | 316.1669 | 459.1554
1314.2198 | 1264.2198 | 285.5081 | 627.3433 | 608.3621 | 580.3329 | 316.664 | 458.993
1315.2212 | 1265.2212 | 285.2358 | 627.419 | 608.6314 | 580.5867 | 317.1616 | 458.879
1316.2226 | 1266.2226 | 284.9284 | 627.5469 | 608.8257 | 581.0583 | 316.3983 | 458.6751
1317.2241 | 1267.2241 | 284.6466 | 627.5845 | 609.0362 | 581.3774 | 316.5669 | 458.3155
1318.2255 | 1268.2255 | 284.3029 | 627.6726 | 609.2613 | 581.7283 | 316.7464 | 458.2027
1319.227 | 1269.227 | 283.8978 | 627.7814 | 609.4716 | 582.4223 | 315.9826 | 458.0682
1320.2184 | 1270.2184 | 283.4816 | 627.895 | 609.7074 | 582.6375 | 316.3139 | 457.7852
1321.2198 | 1271.2198 | 283.0648 | 627.98 | 609.9509 | 582.5265 | 317.7818 | 457.7245
1322.2213 | 1272.2213 | 282.6368 | 627.9759 | 610.1861 | 582.6549 | 318.3478 | 457.5789
1323.2227 | 1273.2227 | 282.1861 | 628.0508 | 610.4072 | 582.8957 | 318.6687 | 457.65
1324.2241 | 1274.2241 | 281.7853 | 628.1866 | 610.6326 | 582.655 | 319.3254 | 457.4737
1325.2256 | 1275.2256 | 281.3282 | 628.3106 | 610.8826 | 582.7743 | 318.6991 | 457.2991
1326.217 | 1276.217 | 280.9332 | 628.3705 | 611.1124 | 582.7145 | 314.7959 | 457.1927
1327.2184 | 1277.2184 | 280.5683 | 628.5443 | 611.3433 | 582.8363 | 313.2828 | 456.902
1328.2199 | 1278.2199 | 280.2125 | 628.857 | 611.5613 | 582.7746 | 313.1296 | 456.7316
1329.2213 | 1279.2213 | 279.8331 | 629.105 | 611.7404 | 582.6691 | 311.6603 | 456.4153
1330.2228 | 1280.2228 | 279.4499 | 629.1717 | 611.9514 | 582.7627 | 310.934 | 456.1922
1331.2242 | 1281.2242 | 279.1039 | 629.2613 | 612.1179 | 583.0262 | 309.3333 | 455.9374
1332.2256 | 1282.2256 | 278.7893 | 629.4519 | 612.3301 | 583.7193 | 307.3874 | 455.7924
1333.2271 | 1283.2271 | 278.6038 | 629.5741 | 612.5182 | 583.7111 | 306.9823 | 455.5774
1334.2185 | 1284.2185 | 278.3149 | 629.642 | 612.6598 | 583.5351 | 306.2221 | 455.5627
1335.22 | 1285.22 | 277.967 | 629.76 | 612.8329 | 583.4087 | 306.3963 | 455.4223
1336.2214 | 1286.2214 | 277.6565 | 629.8431 | 613.0113 | 583.6253 | 307.2482 | 455.1555
1337.2228 | 1287.2228 | 277.367 | 629.994 | 613.1896 | 583.7678 | 308.803 | 455.0239
1338.2243 | 1288.2243 | 277.041 | 630.2246 | 613.4087 | 583.6749 | 309.8284 | 454.9394
1339.2257 | 1289.2257 | 276.7495 | 630.3618 | 613.6003 | 583.6159 | 310.54 | 454.7941
1340.2272 | 1290.2272 | 276.5331 | 630.3458 | 613.7775 | 583.6441 | 310.9236 | 454.5439
1341.2186 | 1291.2186 | 276.2909 | 630.4281 | 613.9845 | 583.9537 | 308.6354 | 454.4334
1342.22 | 1292.22 | 276.0333 | 630.6416 | 614.1874 | 584.1952 | 308.7828 | 454.1377
1343.2215 | 1293.2215 | 275.6986 | 630.8768 | 614.3851 | 584.2062 | 308.9844 | 454.0301
1344.2229 | 1294.2229 | 275.3766 | 631.0904 | 614.559 | 584.1446 | 308.6488 | 453.8157
1345.2243 | 1295.2243 | 275.1086 | 631.3177 | 614.7309 | 584.0395 | 307.6698 | 453.7522
1346.2158 | 1296.2158 | 274.8123 | 631.5103 | 614.926 | 584.3831 | 307.1082 | 453.4813
1347.2172 | 1297.2172 | 274.6056 | 631.4746 | 615.0834 | 584.4905 | 306.0794 | 453.2573
1348.2186 | 1298.2186 | 274.3758 | 631.7125 | 615.3008 | 584.7237 | 305.2111 | 453.134
1349.2201 | 1299.2201 | 274.1609 | 632.096 | 615.4876 | 584.8629 | 305.435 | 452.9771
1350.2215 | 1300.2215 | 273.859 | 632.3932 | 615.6506 | 584.9421 | 305.6928 | 452.8945
1351.223 | 1301.223 | 273.545 | 632.5782 | 615.8143 | 584.9835 | 306.9394 | 452.7786
1352.2244 | 1302.2244 | 273.2282 | 632.6982 | 615.9878 | 584.934 | 306.2121 | 452.5036
1353.2258 | 1303.2258 | 272.9242 | 632.7684 | 616.1307 | 585.139 | 306.6176 | 452.3044
1354.2273 | 1304.2273 | 272.5228 | 632.8801 | 616.264 | 585.5177 | 305.5056 | 452.2218
1355.2187 | 1305.2187 | 272.1642 | 633.0262 | 616.3933 | 585.5149 | 305.0761 | 452.1645
1356.2201 | 1306.2201 | 271.9706 | 633.0286 | 616.5331 | 585.991 | 304.963 | 451.7978
1357.2216 | 1307.2216 | 271.6536 | 633.1346 | 616.6737 | 586.0676 | 305.0899 | 451.7292
1358.223 | 1308.223 | 271.3152 | 633.2869 | 616.7967 | 585.9512 | 304.588 | 451.7933
1359.2245 | 1309.2245 | 270.9475 | 633.4805 | 616.9851 | 585.8695 | 303.3274 | 451.6894
1360.2259 | 1310.2259 | 270.5596 | 633.5991 | 617.1221 | 585.8002 | 303.2673 | 451.2795
1361.2273 | 1311.2273 | 270.2041 | 633.7627 | 617.2699 | 585.8536 | 302.3599 | 451.1355
1362.2188 | 1312.2188 | 269.8981 | 633.8174 | 617.4187 | 585.8388 | 302.0358 | 450.924
1363.2202 | 1313.2202 | 269.594 | 633.9056 | 617.553 | 586.2427 | 301.8371 | 450.6315
1364.2217 | 1314.2217 | 269.3029 | 634.0733 | 617.6966 | 586.5616 | 301.8458 | 450.4714
1365.2231 | 1315.2231 | 269.0006 | 634.217 | 617.8342 | 586.6687 | 301.5968 | 450.3369
1366.2245 | 1316.2245 | 268.7249 | 634.3458 | 617.983 | 586.7178 | 300.1994 | 450.1888
1367.216 | 1317.216 | 268.4845 | 634.4996 | 618.1333 | 586.5737 | 299.8295 | 449.9579
1368.2274 | 1318.2274 | 268.1471 | 634.762 | 618.2896 | 586.73 | 301.4868 | 449.8724
1369.2188 | 1319.2188 | 267.8211 | 634.9048 | 618.4474 | 587.035 | 301.7186 | 449.592
1370.2203 | 1320.2203 | 267.5136 | 634.9867 | 618.5872 | 587.0124 | 302.2027 | 449.4707
1371.2217 | 1321.2217 | 267.2524 | 635.0292 | 618.7134 | 587.2139 | 301.8962 | 449.5047
1372.2232 | 1322.2232 | 266.9504 | 635.0735 | 618.8374 | 587.3494 | 300.9854 | 449.3827
1373.2246 | 1323.2246 | 266.5996 | 635.0694 | 618.9655 | 587.4843 | 301.783 | 449.1828
1374.226 | 1324.226 | 266.2745 | 635.193 | 619.0828 | 587.7306 | 301.8834 | 449.2358
1375.2175 | 1325.2175 | 265.9015 | 635.3488 | 619.1804 | 588.1579 | 300.3826 | 449.0824
1376.2189 | 1326.2189 | 265.5804 | 635.441 | 619.2631 | 588.6479 | 300.7375 | 448.8332
1377.2203 | 1327.2203 | 265.3032 | 635.5837 | 619.371 | 588.7233 | 301.4907 | 448.4738
1378.2218 | 1328.2218 | 264.9578 | 635.6537 | 619.5062 | 588.855 | 300.5757 | 448.5595
1379.2232 | 1329.2232 | 264.5845 | 635.6821 | 619.6443 | 589.1778 | 301.0214 | 448.3301
1380.2247 | 1330.2247 | 264.2346 | 635.815 | 619.7783 | 589.3267 | 301.2383 | 448.2739
1381.2261 | 1331.2261 | 263.8923 | 635.9983 | 619.951 | 589.5867 | 299.7664 | 448.0413
1382.2275 | 1332.2275 | 263.5446 | 636.1264 | 620.0676 | 589.5881 | 299.524 | 447.9565
1383.219 | 1333.219 | 263.2583 | 636.2727 | 620.2 | 589.3862 | 299.8958 | 447.609
1384.2204 | 1334.2204 | 263.0669 | 636.2967 | 620.3197 | 589.48 | 298.8171 | 447.3875
1385.2219 | 1335.2219 | 262.8852 | 636.6274 | 620.4202 | 589.5636 | 297.6524 | 447.1281
1386.2233 | 1336.2233 | 262.711 | 637.0395 | 620.5553 | 589.7169 | 296.3808 | 446.9749
1387.2247 | 1337.2247 | 262.4678 | 637.2391 | 620.7464 | 589.8099 | 295.6039 | 446.8541
1388.2162 | 1338.2162 | 262.2787 | 637.4501 | 620.8736 | 590.0537 | 295.3666 | 446.6106
1389.2176 | 1339.2176 | 262.1324 | 637.8654 | 620.9531 | 590.1314 | 295.4888 | 446.3551
1390.219 | 1340.219 | 261.8918 | 638.0799 | 621.0368 | 590.0624 | 295.092 | 446.2878
1391.2205 | 1341.2205 | 261.6885 | 638.2433 | 621.1315 | 590.0123 | 295.2089 | 446.1371
1392.2219 | 1342.2219 | 261.4518 | 638.3907 | 621.2082 | 589.7514 | 293.9988 | 445.968
1393.2234 | 1343.2234 | 261.1745 | 638.4265 | 621.2835 | 589.675 | 294.3696 | 445.9278
1394.2248 | 1344.2248 | 260.945 | 638.5031 | 621.3244 | 589.6649 | 292.9253 | 445.5898
1395.2162 | 1345.2162 | 260.7734 | 638.6683 | 621.4158 | 589.7448 | 291.7895 | 445.4124
1396.2277 | 1346.2277 | 260.6027 | 638.9169 | 621.5247 | 589.6726 | 290.8443 | 445.1366
1397.2191 | 1347.2191 | 260.4304 | 639.1355 | 621.6266 | 589.5387 | 289.9422 | 444.8579
1398.2205 | 1348.2205 | 260.1944 | 639.1827 | 621.7317 | 589.3445 | 289.0223 | 444.564
1399.222 | 1349.222 | 259.9046 | 639.2705 | 621.8342 | 589.1922 | 288.4637 | 444.4695
1400.2234 | 1350.2234 | 259.6246 | 639.4626 | 621.9137 | 589.2495 | 289.0729 | 444.3241
1401.2249 | 1351.2249 | 259.26 | 639.5135 | 621.9789 | 589.4449 | 288.1249 | 444.2271
1402.2263 | 1352.2263 | 258.8871 | 639.491 | 622.0659 | 589.5875 | 289.53 | 444.1301
1403.2177 | 1353.2177 | 258.6978 | 639.4455 | 622.1376 | 589.5781 | 288.2293 | 444.1916
1404.2192 | 1354.2192 | 258.4224 | 639.6396 | 622.1888 | 589.7819 | 286.7294 | 443.786
1405.2206 | 1355.2206 | 258.1137 | 639.7178 | 622.2902 | 590.1251 | 286.5844 | 443.5744
1406.222 | 1356.222 | 257.8411 | 639.8745 | 622.3733 | 590.3206 | 286.1091 | 443.3869
1407.2235 | 1357.2235 | 257.5918 | 640.0572 | 622.4101 | 590.2739 | 285.1905 | 443.3174
1408.2249 | 1358.2249 | 257.2999 | 640.1364 | 622.4788 | 590.5558 | 284.5209 | 443.4
1409.2164 | 1359.2164 | 256.9539 | 640.2851 | 622.5035 | 590.6566 | 286.0627 | 443.641
1410.2278 | 1360.2278 | 256.6545 | 640.4258 | 622.5394 | 590.5597 | 286.406 | 443.9159
1411.2192 | 1361.2192 | 256.3078 | 640.393 | 622.5653 | 590.6182 | 286.1456 | 444.1347
1412.2207 | 1362.2207 | 256.0485 | 640.3932 | 622.5767 | 590.4344 | 285.1968 | 444.1086
1413.2221 | 1363.2221 | 255.8013 | 640.415 | 622.6413 | 590.433 | 285.9748 | 444.2935
1414.2236 | 1364.2236 | 255.6015 | 640.7393 | 622.6696 | 590.49 | 286.4954 | 444.336
1415.225 | 1365.225 | 255.3791 | 640.9085 | 622.7375 | 590.6495 | 285.3042 | 444.2406
1416.2264 | 1366.2264 | 255.2031 | 640.8553 | 622.8249 | 590.7727 | 285.5993 | 444.2148
1417.2279 | 1367.2279 | 255.0856 | 640.9331 | 622.8911 | 591.0023 | 284.2814 | 444.1333
1418.2193 | 1368.2193 | 254.8686 | 641.2683 | 622.9528 | 591.1215 | 282.7502 | 444.1435
1419.2207 | 1369.2207 | 254.6018 | 641.4948 | 623.0508 | 591.0649 | 282.8802 | 444.0972
1420.2222 | 1370.2222 | 254.3356 | 641.6994 | 623.1321 | 591.2536 | 283.1342 | 444.0167
1421.2236 | 1371.2236 | 254.0575 | 641.813 | 623.204 | 591.3962 | 282.3371 | 444.1187
1422.2251 | 1372.2251 | 253.7753 | 641.8986 | 623.2715 | 591.4268 | 281.1929 | 444.115
1423.2265 | 1373.2265 | 253.4832 | 641.8705 | 623.2881 | 591.3819 | 280.7702 | 444.0253
1424.2179 | 1374.2179 | 253.266 | 641.8598 | 623.2875 | 591.1868 | 280.2451 | 443.8956
1425.2194 | 1375.2194 | 253.0523 | 642.0451 | 623.3288 | 591.1623 | 279.0315 | 443.7304
1426.2208 | 1376.2208 | 252.8163 | 642.0332 | 623.3427 | 591.1433 | 278.6131 | 443.6472
1427.2222 | 1377.2222 | 252.5809 | 642.1661 | 623.3812 | 591.0508 | 278.745 | 443.5156
1428.2237 | 1378.2237 | 252.3891 | 642.0153 | 623.415 | 590.8884 | 277.9051 | 443.3798
1429.2251 | 1379.2251 | 252.1676 | 642.1619 | 623.4499 | 591.042 | 277.8204 | 443.3733
1430.2166 | 1380.2166 | 251.8204 | 642.1381 | 623.4669 | 591.2324 | 278.0358 | 443.3649
1431.218 | 1381.218 | 251.4487 | 642.0246 | 623.4733 | 591.4831 | 278.5827 | 443.1432
1432.2194 | 1382.2194 | 251.2299 | 642.0051 | 623.4949 | 591.5764 | 276.9064 | 443.0957
1433.2209 | 1383.2209 | 251.038 | 641.9684 | 623.5033 | 591.3924 | 276.0019 | 442.9142
1434.2223 | 1384.2223 | 250.7971 | 641.7862 | 623.5084 | 591.1931 | 275.0129 | 442.7517
1435.2238 | 1385.2238 | 250.4777 | 641.4329 | 623.5222 | 591.2683 | 273.874 | 442.6714
1436.2252 | 1386.2252 | 250.2075 | 641.4059 | 623.5592 | 591.3785 | 274.5042 | 442.6198
1437.2166 | 1387.2166 | 249.894 | 641.1447 | 623.6227 | 591.4859 | 273.766 | 442.477
1438.2181 | 1388.2181 | 249.6432 | 641.0102 | 623.6326 | 591.5354 | 273.266 | 442.4231
1439.2195 | 1389.2195 | 249.3752 | 640.8945 | 623.6804 | 591.5689 | 273.3897 | 442.2996
1440.2209 | 1390.2209 | 249.0595 | 640.8382 | 623.7074 | 591.467 | 272.4488 | 442.1249
1441.2224 | 1391.2224 | 248.8104 | 640.5015 | 623.734 | 591.3116 | 272.1777 | 442.135
1442.2238 | 1392.2238 | 248.6454 | 640.1189 | 623.7538 | 591.3283 | 272.1689 | 442.0283
1443.2253 | 1393.2253 | 248.4202 | 639.946 | 623.7486 | 591.4533 | 271.5674 | 441.9406
1444.2267 | 1394.2267 | 248.2142 | 639.7238 | 623.7919 | 591.423 | 271.1374 | 441.6352
1445.2281 | 1395.2281 | 247.9385 | 639.4027 | 623.8117 | 591.3679 | 271.4559 | 441.3441
1446.2196 | 1396.2196 | 247.6165 | 639.1724 | 623.816 | 591.1737 | 272.0603 | 441.1931
1447.221 | 1397.221 | 247.351 | 638.8994 | 623.7889 | 591.0353 | 270.9504 | 441.0114
1448.2224 | 1398.2224 | 247.0617 | 638.7981 | 623.7583 | 590.78 | 270.5106 | 440.7458
1449.2239 | 1399.2239 | 246.776 | 638.5832 | 623.7251 | 590.5042 | 270.2628 | 440.6562
1450.2253 | 1400.2253 | 246.5076 | 638.3984 | 623.7084 | 590.3739 | 271.3158 | 440.5362
1451.2167 | 1401.2167 | 246.2714 | 638.3742 | 623.6639 | 590.4685 | 270.3019 | 440.2794
1452.2182 | 1402.2182 | 245.9447 | 638.1047 | 623.6061 | 590.4371 | 270.8491 | 440.1594
1453.2196 | 1403.2196 | 245.5501 | 637.6558 | 623.5879 | 590.4439 | 270.4202 | 440.1017
1454.2211 | 1404.2211 | 245.2192 | 637.1864 | 623.6022 | 590.3032 | 271.0731 | 440.0087
1455.2225 | 1405.2225 | 244.8925 | 636.7541 | 623.6529 | 590.3246 | 271.0121 | 439.7911
1456.2239 | 1406.2239 | 244.6071 | 636.1949 | 623.6595 | 590.4829 | 271.6316 | 439.7341
1457.2254 | 1407.2254 | 244.3562 | 635.6159 | 623.667 | 590.632 | 271.6479 | 439.5342
1458.2268 | 1408.2268 | 244.098 | 635.1793 | 623.6362 | 590.5283 | 270.8786 | 439.3056
1459.2183 | 1409.2183 | 243.8402 | 634.6645 | 623.6204 | 590.5791 | 271.4275 | 439.1629
1460.2197 | 1410.2197 | 243.5236 | 634.3873 | 623.5709 | 590.5786 | 271.2639 | 439.0024
1461.2211 | 1411.2211 | 243.2191 | 634.1372 | 623.5323 | 590.4463 | 270.5387 | 438.7575
1462.2226 | 1412.2226 | 242.8826 | 633.6751 | 623.5015 | 590.4903 | 269.8814 | 438.4803
1463.224 | 1413.224 | 242.5652 | 633.0622 | 623.5277 | 590.4489 | 270.0788 | 438.304
1464.2255 | 1414.2255 | 242.2876 | 632.4811 | 623.4998 | 590.6871 | 270.1952 | 437.9495
1465.2269 | 1415.2269 | 242.0161 | 631.8031 | 623.4444 | 590.8769 | 270.924 | 437.753
1466.2183 | 1416.2183 | 241.7253 | 631.1203 | 623.3909 | 590.8373 | 268.9953 | 437.4953
1467.2198 | 1417.2198 | 241.4167 | 630.4129 | 623.3818 | 590.839 | 268.5121 | 437.3625
1468.2212 | 1418.2212 | 241.193 | 629.6941 | 623.4261 | 590.9475 | 268.1256 | 437.2625
1469.2226 | 1419.2226 | 240.9202 | 629.0454 | 623.3851 | 591.1792 | 267.657 | 437.066
1470.2241 | 1420.2241 | 240.6613 | 628.3621 | 623.3576 | 591.1894 | 267.1862 | 436.8515
1471.2255 | 1421.2255 | 240.4725 | 627.5765 | 623.3178 | 591.3438 | 266.4611 | 436.589
1472.2169 | 1422.2169 | 240.2343 | 626.9207 | 623.2811 | 591.2279 | 265.8596 | 436.3947
1473.2184 | 1423.2184 | 240.0251 | 626.3353 | 623.2418 | 591.0558 | 265.5207 | 436.4226
1474.2198 | 1424.2198 | 239.8345 | 625.707 | 623.2115 | 590.8522 | 264.8625 | 436.1019
1475.2213 | 1425.2213 | 239.6676 | 625.0581 | 623.2006 | 590.4629 | 263.6062 | 435.9343
1476.2227 | 1426.2227 | 239.5544 | 624.3758 | 623.155 | 590.085 | 263.2923 | 435.7003
1477.2241 | 1427.2241 | 239.4183 | 623.8305 | 623.0967 | 589.8575 | 261.9336 | 435.5636
1478.2256 | 1428.2256 | 239.2543 | 623.25 | 623.0468 | 589.7046 | 261.3589 | 435.4058
1479.217 | 1429.217 | 239.0433 | 622.7446 | 622.9997 | 589.5311 | 261.0754 | 435.3902
1480.2184 | 1430.2184 | 238.8734 | 622.3148 | 622.957 | 589.3696 | 259.6446 | 435.3337
1481.2199 | 1431.2199 | 238.6709 | 621.7323 | 622.869 | 589.1889 | 258.4975 | 435.0906
1482.2213 | 1432.2213 | 238.4095 | 621.156 | 622.8493 | 589.0466 | 257.4033 | 434.9157
1483.2228 | 1433.2228 | 238.211 | 620.5079 | 622.8181 | 588.9731 | 257.5682 | 434.7316
1484.2242 | 1434.2242 | 238.0042 | 619.9488 | 622.7277 | 588.8304 | 257.5715 | 434.5216
1485.2256 | 1435.2256 | 237.7715 | 619.4132 | 622.6713 | 588.715 | 258.2106 | 434.4535
1486.2271 | 1436.2271 | 237.5259 | 618.9027 | 622.6287 | 588.6784 | 256.9337 | 434.3119
1487.2185 | 1437.2185 | 237.3245 | 618.2902 | 622.6114 | 588.6065 | 256.7183 | 434.2076
1488.22 | 1438.22 | 237.0979 | 617.6805 | 622.6106 | 588.5302 | 256.0513 | 434.0188
1489.2214 | 1439.2214 | 236.8424 | 617.146 | 622.4986 | 588.3153 | 255.4159 | 433.8726
1490.2228 | 1440.2228 | 236.6113 | 616.5904 | 622.4264 | 588.2681 | 253.9332 | 433.6648
1491.2243 | 1441.2243 | 236.4015 | 616.0152 | 622.4054 | 588.2055 | 254.0537 | 433.3445
1492.2257 | 1442.2257 | 236.1973 | 615.4481 | 622.3917 | 588.001 | 252.8047 | 433.2369
1493.2272 | 1443.2272 | 236.0235 | 614.93 | 622.3657 | 587.8137 | 252.6807 | 432.9012
1494.2186 | 1444.2186 | 235.8137 | 614.4614 | 622.3166 | 587.6498 | 252.3577 | 432.6018
1495.22 | 1445.22 | 235.5505 | 613.9975 | 622.2409 | 587.458 | 252.1054 | 432.4355
1496.2215 | 1446.2215 | 235.2608 | 613.507 | 622.2038 | 587.3308 | 251.8259 | 432.3064
1497.2229 | 1447.2229 | 235.0319 | 613.0653 | 622.1231 | 587.2026 | 252.6898 | 432.1809
1498.2243 | 1448.2243 | 234.773 | 612.5681 | 622.022 | 587.1249 | 252.6194 | 432.1156
1499.2158 | 1449.2158 | 234.5368 | 612.1248 | 621.8949 | 586.8715 | 252.0266 | 431.9121
1500.2272 | 1450.2272 | 234.3217 | 611.6576 | 621.7955 | 586.674 | 251.2428 | 431.7973
1501.2186 | 1451.2186 | 234.0901 | 611.2251 | 621.6605 | 586.49 | 250.9585 | 431.6414
1502.2201 | 1452.2201 | 233.8714 | 610.8111 | 621.5856 | 586.2571 | 250.8816 | 431.5908
1503.2215 | 1453.2215 | 233.6604 | 610.3999 | 621.5207 | 586.1806 | 250.4735 | 431.3405
1504.223 | 1454.223 | 233.4823 | 609.9786 | 621.4419 | 586.2203 | 250.3697 | 431.2077
1505.2244 | 1455.2244 | 233.2692 | 609.5637 | 621.4008 | 586.1862 | 250.0396 | 430.8819
1506.2258 | 1456.2258 | 233.0037 | 609.1331 | 621.321 | 586.1373 | 249.6394 | 430.6261
1507.2273 | 1457.2273 | 232.7494 | 608.7211 | 621.2488 | 585.9959 | 248.6983 | 430.4395
1508.2187 | 1458.2187 | 232.4816 | 608.2802 | 621.2645 | 585.8383 | 248.56 | 430.3629
1509.2202 | 1459.2202 | 232.2655 | 607.8199 | 621.2049 | 585.638 | 248.3504 | 430.0972
1510.2216 | 1460.2216 | 232.0435 | 607.3236 | 621.1155 | 585.4237 | 247.7081 | 429.887
1511.223 | 1461.223 | 231.8233 | 606.8315 | 621.0265 | 585.1985 | 247.2448 | 429.7505
1512.2245 | 1462.2245 | 231.6193 | 606.3481 | 620.9273 | 585.1339 | 246.8347 | 429.5835
1513.2259 | 1463.2259 | 231.4415 | 605.895 | 620.8012 | 585.0699 | 247.5247 | 429.4866
1514.2274 | 1464.2274 | 231.2031 | 605.4591 | 620.6616 | 584.9608 | 248.7545 | 429.2032
1515.2188 | 1465.2188 | 230.9181 | 604.9933 | 620.5793 | 584.7535 | 249.174 | 429.0857
1516.2202 | 1466.2202 | 230.6584 | 604.5357 | 620.4559 | 584.5772 | 248.9732 | 428.7442
1517.2217 | 1467.2217 | 230.4301 | 604.0795 | 620.3254 | 584.5382 | 248.6636 | 428.6764
1518.2231 | 1468.2231 | 230.0802 | 603.6328 | 620.1721 | 584.479 | 247.8129 | 428.5909
1519.2245 | 1469.2245 | 229.716 | 603.1923 | 620.0335 | 584.3348 | 248.5324 | 428.4857
1520.216 | 1470.216 | 229.3665 | 602.6864 | 619.9005 | 584.2142 | 249.6126 | 428.266
1521.2174 | 1471.2174 | 229.0966 | 602.137 | 619.7803 | 584.1347 | 250.7237 | 427.9952
1522.2188 | 1472.2188 | 228.7973 | 601.591 | 619.6322 | 584.0783 | 250.8121 | 427.6982
1523.2203 | 1473.2203 | 228.4914 | 601.0685 | 619.4398 | 583.8572 | 249.9273 | 427.5794
1524.2217 | 1474.2217 | 228.1947 | 600.538 | 619.259 | 583.6983 | 250.0034 | 427.3113
1525.2232 | 1475.2232 | 227.8805 | 599.975 | 619.1184 | 583.6262 | 249.5436 | 426.9845
1526.2246 | 1476.2246 | 227.5592 | 599.4268 | 618.9256 | 583.5011 | 249.7484 | 426.8518
1527.226 | 1477.226 | 227.3164 | 598.8898 | 618.8078 | 583.3492 | 250.1157 | 426.6906
1528.2275 | 1478.2275 | 227.0713 | 598.3252 | 618.6932 | 583.2213 | 249.7135 | 426.5469
1529.2189 | 1479.2189 | 226.8265 | 597.6775 | 618.6263 | 582.9194 | 247.6597 | 426.4119
1530.2203 | 1480.2203 | 226.5419 | 597.0308 | 618.4852 | 582.5984 | 246.1717 | 426.1786
1531.2218 | 1481.2218 | 226.2523 | 596.4041 | 618.344 | 582.3575 | 246.2468 | 426.1826
1532.2232 | 1482.2232 | 225.9671 | 595.7674 | 618.1971 | 582.0824 | 246.359 | 425.8915
1533.2247 | 1483.2247 | 225.7195 | 595.1323 | 618.0472 | 581.7224 | 247.2006 | 425.7612
1534.2261 | 1484.2261 | 225.4561 | 594.479 | 617.8989 | 581.4834 | 247.738 | 425.4727
1535.2275 | 1485.2275 | 225.2166 | 593.8116 | 617.7768 | 581.2931 | 247.8272 | 425.2273
1536.219 | 1486.219 | 224.9625 | 593.1862 | 617.5888 | 580.9207 | 247.785 | 425.0637
1537.2204 | 1487.2204 | 224.7713 | 592.5813 | 617.4178 | 580.6018 | 247.4319 | 424.9467
1538.2219 | 1488.2219 | 224.5406 | 591.9709 | 617.2409 | 580.5093 | 247.0686 | 424.6696
1539.2233 | 1489.2233 | 224.344 | 591.3728 | 617.0602 | 580.4035 | 246.721 | 424.589
1540.2247 | 1490.2247 | 224.2047 | 590.7754 | 616.9065 | 580.2815 | 246.6861 | 424.4722
1541.2262 | 1491.2262 | 224.1201 | 590.1848 | 616.7463 | 580.088 | 245.0141 | 424.2124
1542.2176 | 1492.2176 | 224.0008 | 589.5933 | 616.583 | 579.7935 | 244.4911 | 424.0254
1543.219 | 1493.219 | 223.834 | 589.0467 | 616.46 | 579.562 | 244.3041 | 423.8762
1544.2205 | 1494.2205 | 223.6654 | 588.5261 | 616.292 | 579.2329 | 243.7088 | 423.5886
1545.2219 | 1495.2219 | 223.4984 | 588.0214 | 616.1156 | 578.8772 | 243.7412 | 423.4211
1546.2234 | 1496.2234 | 223.2987 | 587.5078 | 615.9813 | 578.5214 | 243.7646 | 423.2114
1547.2248 | 1497.2248 | 223.0594 | 586.9748 | 615.7932 | 578.359 | 242.7264 | 422.9806
1548.2262 | 1498.2262 | 222.8858 | 586.4786 | 615.5728 | 578.2649 | 242.4195 | 422.7939
1549.2177 | 1499.2177 | 222.6363 | 585.9794 | 615.381 | 578.0518 | 242.392 | 422.8282
1550.2191 | 1500.2191 | 222.3707 | 585.4511 | 615.1885 | 577.9941 | 241.9368 | 422.7707
1551.2205 | 1501.2205 | 222.1037 | 584.9094 | 615.0024 | 577.8503 | 241.5251 | 422.5878
1552.222 | 1502.222 | 221.8945 | 584.3556 | 614.8412 | 577.5142 | 241.7499 | 422.3755
1553.2234 | 1503.2234 | 221.5919 | 583.8176 | 614.6295 | 577.1603 | 242.1524 | 422.1645
1554.2249 | 1504.2249 | 221.2973 | 583.3093 | 614.4204 | 576.8343 | 242.3807 | 422.0281
1555.2263 | 1505.2263 | 221.0245 | 582.7843 | 614.2337 | 576.5984 | 242.2863 | 421.794
1556.2177 | 1506.2177 | 220.6861 | 582.2672 | 614.031 | 576.389 | 242.7368 | 421.6616
1557.2192 | 1507.2192 | 220.3904 | 581.7508 | 613.7941 | 576.2332 | 242.5957 | 421.5243
1558.2206 | 1508.2206 | 220.2324 | 581.2249 | 613.51 | 575.9953 | 241.7616 | 421.2625
1559.2221 | 1509.2221 | 220.088 | 580.7389 | 613.3385 | 575.6349 | 241.0814 | 421.0905
1560.2235 | 1510.2235 | 219.8985 | 580.2558 | 613.1454 | 575.2498 | 240.6427 | 420.8587
1561.2249 | 1511.2249 | 219.6796 | 579.7425 | 612.9374 | 574.818 | 239.8621 | 420.7775
1562.2164 | 1512.2164 | 219.4863 | 579.26 | 612.7489 | 574.3167 | 239.921 | 420.6944
1563.2178 | 1513.2178 | 219.3091 | 578.7678 | 612.5429 | 573.8388 | 238.6889 | 420.5786
1564.2192 | 1514.2192 | 219.1334 | 578.2334 | 612.3372 | 573.3503 | 237.5427 | 420.3744
1565.2207 | 1515.2207 | 219.019 | 577.6779 | 612.0968 | 572.8379 | 237.0132 | 420.3394
1566.2221 | 1516.2221 | 218.9147 | 577.0835 | 611.8673 | 572.4034 | 236.2647 | 420.0783
1567.2236 | 1517.2236 | 218.7584 | 576.4635 | 611.6336 | 571.9281 | 236.0548 | 419.7281
1568.225 | 1518.225 | 218.5416 | 575.8094 | 611.3731 | 571.4976 | 235.4117 | 419.5771
1569.2264 | 1519.2264 | 218.3415 | 575.1378 | 611.1517 | 571.2424 | 236.2565 | 419.411
1570.2279 | 1520.2279 | 218.0596 | 574.449 | 610.9123 | 570.9047 | 236.6464 | 419.2076
1571.2193 | 1521.2193 | 217.7931 | 573.762 | 610.6778 | 570.499 | 237.3013 | 419.0135
1572.2207 | 1522.2207 | 217.5096 | 573.0727 | 610.4463 | 570.0883 | 236.8309 | 418.6644
1573.2222 | 1523.2222 | 217.2514 | 572.3588 | 610.192 | 569.5758 | 236.8723 | 418.3455
1574.2236 | 1524.2236 | 216.9626 | 571.6433 | 609.9717 | 569.104 | 237.8755 | 418.2046
1575.2251 | 1525.2251 | 216.6751 | 570.9304 | 609.7275 | 568.7077 | 238.584 | 418.2294
1576.2265 | 1526.2265 | 216.4186 | 570.2042 | 609.4817 | 568.3554 | 238.5329 | 418.1391
1577.2179 | 1527.2179 | 216.2079 | 569.4775 | 609.2111 | 567.9737 | 239.0494 | 417.8731
1578.2194 | 1528.2194 | 215.9859 | 568.7428 | 608.9332 | 567.5801 | 238.6436 | 417.5967
1579.2208 | 1529.2208 | 215.769 | 567.983 | 608.6774 | 567.2331 | 239.1465 | 417.5953
1580.2222 | 1530.2222 | 215.5808 | 567.2364 | 608.4374 | 566.8907 | 238.3646 | 417.3323
1581.2237 | 1531.2237 | 215.3518 | 566.4925 | 608.1942 | 566.5001 | 237.935 | 417.2446
1582.2251 | 1532.2251 | 215.1405 | 565.7383 | 607.9436 | 566.1124 | 236.8111 | 417.0266
1583.2166 | 1533.2166 | 214.9553 | 565.0085 | 607.6339 | 565.6834 | 235.6018 | 416.8766
1584.218 | 1534.218 | 214.7719 | 564.2734 | 607.3461 | 565.2297 | 234.2799 | 416.6278
1585.2194 | 1535.2194 | 214.6103 | 563.5321 | 607.0756 | 564.7464 | 234.5383 | 416.47
1586.2209 | 1536.2209 | 214.4541 | 562.7926 | 606.7731 | 564.2889 | 234.4895 | 416.1354
1587.2223 | 1537.2223 | 214.275 | 562.061 | 606.534 | 563.8221 | 234.2127 | 416.0951
1588.2438 | 1538.2438 | 214.0737 | 561.3061 | 606.3024 | 563.3151 | 233.8009 | 415.9969
1589.2252 | 1539.2252 | 213.9157 | 560.5949 | 606.0742 | 562.8409 | 233.0923 | 415.7862
1590.2266 | 1540.2266 | 213.6637 | 559.8881 | 605.804 | 562.381 | 233.4419 | 415.7495
1591.2281 | 1541.2281 | 213.3895 | 559.1723 | 605.5377 | 561.8489 | 234.2026 | 415.6347
1592.2195 | 1542.2195 | 213.1357 | 558.4636 | 605.2887 | 561.3053 | 234.0128 | 415.4571
1593.2209 | 1543.2209 | 212.8843 | 557.7461 | 604.9936 | 560.8309 | 233.785 | 415.4301
1594.2224 | 1544.2224 | 212.687 | 557.0332 | 604.6896 | 560.3806 | 233.0981 | 415.1798
1595.2238 | 1545.2238 | 212.4819 | 556.3324 | 604.3828 | 559.9115 | 233.3619 | 415.0044
1596.2253 | 1546.2253 | 212.3194 | 555.6449 | 604.079 | 559.4776 | 232.402 | 414.8854
1597.2167 | 1547.2167 | 212.0902 | 554.9595 | 603.7465 | 559.1629 | 231.4455 | 414.7669
1598.2181 | 1548.2181 | 211.7683 | 554.2746 | 603.4514 | 558.8178 | 231.7107 | 414.7906
1599.2196 | 1549.2196 | 211.5229 | 553.6071 | 603.1756 | 558.3745 | 232.2464 | 414.6711
1600.221 | 1550.221 | 211.3398 | 552.9427 | 602.8454 | 557.8641 | 232.0532 | 414.5508
1601.2224 | 1551.2224 | 211.1356 | 552.2788 | 602.5503 | 557.3938 | 230.9746 | 414.4924
1602.2239 | 1552.2239 | 210.9697 | 551.6435 | 602.208 | 557.0056 | 230.9365 | 414.3369
1603.2253 | 1553.2253 | 210.7531 | 551.0095 | 601.8699 | 556.6316 | 229.6626 | 414.0814
1604.2168 | 1554.2168 | 210.5365 | 550.3987 | 601.5306 | 556.2245 | 229.023 | 414.0066
1605.2182 | 1555.2182 | 210.3253 | 549.7935 | 601.2419 | 555.7494 | 229.9029 | 413.8644
1606.2196 | 1556.2196 | 210.062 | 549.2059 | 600.9313 | 555.2997 | 231.0147 | 413.7039
1607.2211 | 1557.2211 | 209.8254 | 548.6089 | 600.5853 | 554.8621 | 230.2605 | 413.6371
1608.2225 | 1558.2225 | 209.5687 | 548.0164 | 600.2153 | 554.457 | 231.0299 | 413.5295
1609.224 | 1559.224 | 209.3323 | 547.4261 | 599.9025 | 553.9891 | 231.286 | 413.3544
1610.2254 | 1560.2254 | 209.1272 | 546.8377 | 599.5862 | 553.5041 | 229.8829 | 413.0831
1611.2268 | 1561.2268 | 208.9597 | 546.2513 | 599.2747 | 552.9601 | 228.7587 | 412.9662
1612.2183 | 1562.2183 | 208.7047 | 545.655 | 598.9469 | 552.3744 | 228.4937 | 412.8238
1613.2197 | 1563.2197 | 208.5052 | 545.0581 | 598.5829 | 551.7892 | 228.5394 | 412.6556
1614.2211 | 1564.2211 | 208.3567 | 544.4582 | 598.2406 | 551.1833 | 228.4172 | 412.2902
1615.2226 | 1565.2226 | 208.2152 | 543.8567 | 597.8507 | 550.6092 | 227.0276 | 412.0759
1616.224 | 1566.224 | 208.0579 | 543.2307 | 597.5108 | 550.012 | 226.6942 | 411.9179
1617.2255 | 1567.2255 | 207.8742 | 542.6041 | 597.1027 | 549.4221 | 225.8747 | 411.6617
1618.2269 | 1568.2269 | 207.7132 | 541.9661 | 596.7584 | 548.8192 | 225.753 | 411.4409
1619.2183 | 1569.2183 | 207.5116 | 541.3128 | 596.3459 | 548.2098 | 225.3395 | 411.4214
1620.2198 | 1570.2198 | 207.3155 | 540.6536 | 595.9804 | 547.6324 | 224.9657 | 411.1644
1621.2212 | 1571.2212 | 207.0817 | 540.0024 | 595.5596 | 547.0863 | 225.0969 | 411.0223
1622.2226 | 1572.2226 | 206.8933 | 539.3789 | 595.1568 | 546.522 | 226.0788 | 410.8356
1623.2241 | 1573.2241 | 206.6818 | 538.7462 | 594.7572 | 545.9536 | 226.2809 | 410.6894
1624.2255 | 1574.2255 | 206.4461 | 538.1218 | 594.3307 | 545.3603 | 226.4461 | 410.5084
1625.2169 | 1575.2169 | 206.2003 | 537.5252 | 593.8767 | 544.7719 | 227.0089 | 410.2503
1626.2184 | 1576.2184 | 205.9234 | 536.9262 | 593.4367 | 544.1158 | 227.4078 | 410.0219
1627.2198 | 1577.2198 | 205.7091 | 536.3434 | 593.0193 | 543.5427 | 227.0437 | 409.9516
1628.2213 | 1578.2213 | 205.516 | 535.7816 | 592.5592 | 542.928 | 226.6179 | 409.8852
1629.2227 | 1579.2227 | 205.3246 | 535.2249 | 592.1063 | 542.2699 | 226.0621 | 409.7777
1630.2241 | 1580.2241 | 205.1396 | 534.6555 | 591.6474 | 541.6644 | 225.1997 | 409.5763
1631.2256 | 1581.2256 | 204.9013 | 534.0774 | 591.2343 | 541.0482 | 225.0824 | 409.4668
1632.217 | 1582.217 | 204.6317 | 533.5077 | 590.7952 | 540.4159 | 225.5881 | 409.3359
1633.2185 | 1583.2185 | 204.373 | 532.9417 | 590.3473 | 539.7804 | 225.6779 | 409.2001
1634.2199 | 1584.2199 | 204.1724 | 532.3777 | 589.8825 | 539.1257 | 226.2866 | 409.1131
1635.2213 | 1585.2213 | 203.9883 | 531.814 | 589.3993 | 538.4335 | 226.6007 | 408.9641
1636.2228 | 1586.2228 | 203.863 | 531.2541 | 588.937 | 537.7829 | 225.8988 | 408.739
1637.2242 | 1587.2242 | 203.7208 | 530.7015 | 588.4634 | 537.0786 | 225.2094 | 408.5629
1638.2257 | 1588.2257 | 203.5334 | 530.163 | 588.0092 | 536.2943 | 224.9004 | 408.408
1639.2271 | 1589.2271 | 203.3721 | 529.6289 | 587.5568 | 535.523 | 224.5661 | 408.3132
1640.2185 | 1590.2185 | 203.1606 | 529.1206 | 587.1233 | 534.809 | 223.9421 | 408.2676
1641.22 | 1591.22 | 202.8893 | 528.6123 | 586.7119 | 534.1124 | 223.1854 | 408.1313
1642.2214 | 1592.2214 | 202.6637 | 528.1141 | 586.2893 | 533.3652 | 223.2666 | 407.992
1643.2228 | 1593.2228 | 202.4911 | 527.6222 | 585.8992 | 532.6362 | 223.0438 | 407.8424
1644.2243 | 1594.2243 | 202.2797 | 527.1261 | 585.4807 | 531.8839 | 222.8206 | 407.7129
1645.2257 | 1595.2257 | 202.06 | 526.6273 | 585.0779 | 531.0425 | 222.2573 | 407.6664
1646.2171 | 1596.2171 | 201.8709 | 526.1326 | 584.6875 | 530.3306 | 221.9276 | 407.5163
1647.2186 | 1597.2186 | 201.6699 | 525.6366 | 584.3057 | 529.5667 | 221.9499 | 407.2992
1648.22 | 1598.22 | 201.4679 | 525.1301 | 583.9011 | 528.81 | 221.7998 | 407.1005
1649.2215 | 1599.2215 | 201.2429 | 524.6393 | 583.4818 | 528.0681 | 221.5294 | 407.0336
1650.2229 | 1600.2229 | 201.0764 | 524.1491 | 583.0685 | 527.3287 | 220.1996 | 406.83
1651.2243 | 1601.2243 | 200.9594 | 523.63 | 582.6771 | 526.5221 | 219.7577 | 406.6961
1652.2258 | 1602.2258 | 200.8344 | 523.1244 | 582.269 | 525.7613 | 219.1291 | 406.5337
1653.2272 | 1603.2272 | 200.6736 | 522.6182 | 581.8595 | 524.9899 | 218.468 | 406.1847
1654.2186 | 1604.2186 | 200.4679 | 522.0972 | 581.4469 | 524.2522 | 218.1199 | 406.0727
1655.2201 | 1605.2201 | 200.2803 | 521.5834 | 581.0645 | 523.5246 | 217.9058 | 405.7343
1656.2215 | 1606.2215 | 200.169 | 521.0575 | 580.648 | 522.7954 | 216.9878 | 405.5445
1657.223 | 1607.223 | 200.0827 | 520.5245 | 580.2149 | 522.0578 | 216.1484 | 405.2658
1658.2244 | 1608.2244 | 199.986 | 519.9937 | 579.7902 | 521.3115 | 215.5571 | 404.9014
1659.2258 | 1609.2258 | 199.8257 | 519.4538 | 579.3659 | 520.5842 | 215.0487 | 404.7549
1660.2273 | 1610.2273 | 199.6798 | 518.9198 | 578.9119 | 519.8787 | 214.2689 | 404.5516
1661.2187 | 1611.2187 | 199.5462 | 518.3811 | 578.4892 | 519.1899 | 213.7432 | 404.4171
1662.2202 | 1612.2202 | 199.398 | 517.8395 | 578.0562 | 518.5112 | 213.5083 | 404.069
1663.2216 | 1613.2216 | 199.2561 | 517.3069 | 577.6499 | 517.8317 | 213.5411 | 403.9658
1664.223 | 1614.223 | 199.092 | 516.773 | 577.2151 | 517.238 | 213.2668 | 403.8356
1665.2245 | 1615.2245 | 198.939 | 516.2337 | 576.7918 | 516.5897 | 213.5071 | 403.6706
1666.2259 | 1616.2259 | 198.797 | 515.708 | 576.3371 | 515.9219 | 213.086 | 403.4425
1667.2173 | 1617.2173 | 198.6059 | 515.1772 | 575.8883 | 515.26 | 212.1249 | 403.491
1668.2188 | 1618.2188 | 198.4067 | 514.6538 | 575.4453 | 514.622 | 212.4687 | 403.3245
1669.2202 | 1619.2202 | 198.2491 | 514.1319 | 574.9868 | 513.9833 | 211.8912 | 403.2015
1670.2217 | 1620.2217 | 198.0591 | 513.597 | 574.5303 | 513.3469 | 211.3316 | 403.1831
1671.2231 | 1621.2231 | 197.821 | 513.0582 | 574.0467 | 512.6962 | 211.4848 | 403.0566
1672.2245 | 1622.2245 | 197.6456 | 512.5034 | 573.5544 | 512.0446 | 211.5846 | 403.0201
1673.226 | 1623.226 | 197.5147 | 511.9611 | 573.0524 | 511.4669 | 211.34 | 402.8844
1674.2274 | 1624.2274 | 197.3699 | 511.4104 | 572.5583 | 510.8038 | 210.8988 | 402.7044
1675.2188 | 1625.2188 | 197.1973 | 510.879 | 572.0666 | 510.1616 | 210.639 | 402.3855
1676.2203 | 1626.2203 | 197.0293 | 510.3548 | 571.5611 | 509.5484 | 210.4568 | 402.1165
1677.2217 | 1627.2217 | 196.8978 | 509.8429 | 571.0882 | 508.9638 | 210.3642 | 402.0765
1678.2232 | 1628.2232 | 196.772 | 509.3294 | 570.5951 | 508.3649 | 210.1266 | 401.8129
1679.2246 | 1629.2246 | 196.5999 | 508.828 | 570.1124 | 507.749 | 209.8091 | 401.5827
1680.226 | 1630.226 | 196.417 | 508.3335 | 569.6361 | 507.1419 | 209.1117 | 401.2988
1681.2275 | 1631.2275 | 196.2527 | 507.8394 | 569.1487 | 506.4395 | 208.4553 | 401.1117
1682.2189 | 1632.2189 | 196.0365 | 507.3498 | 568.677 | 505.8056 | 208.8774 | 400.8478
1683.2204 | 1633.2204 | 195.8567 | 506.8452 | 568.2016 | 505.2162 | 209.1531 | 400.669
1684.2218 | 1634.2218 | 195.6686 | 506.3296 | 567.7408 | 504.6054 | 208.782 | 400.5137
1685.2332 | 1635.2332 | 195.5146 | 505.8251 | 567.248 | 503.9455 | 208.7076 | 400.232
1686.2247 | 1636.2247 | 195.3601 | 505.3025 | 566.7344 | 503.318 | 208.8041 | 400.0972
1687.2261 | 1637.2261 | 195.1751 | 504.7837 | 566.2452 | 502.6202 | 208.6524 | 399.7871
1688.2175 | 1638.2175 | 194.9772 | 504.2614 | 565.7667 | 501.9822 | 208.04 | 399.7411
1689.219 | 1639.219 | 194.8159 | 503.7443 | 565.2867 | 501.3162 | 208.1128 | 399.6048
1690.2204 | 1640.2204 | 194.6252 | 503.2228 | 564.7907 | 500.6939 | 207.5459 | 399.5467
1691.2219 | 1641.2219 | 194.4558 | 502.7134 | 564.3006 | 500.0616 | 207.8922 | 399.3264
1692.2233 | 1642.2233 | 194.2868 | 502.1855 | 563.8066 | 499.5125 | 207.0195 | 399.1129
1693.2247 | 1643.2247 | 194.1029 | 501.6848 | 563.3074 | 498.8599 | 206.0176 | 398.8446
1694.2162 | 1644.2162 | 193.8831 | 501.19 | 562.7973 | 498.2095 | 205.247 | 398.7656
1695.2276 | 1645.2276 | 193.6835 | 500.6967 | 562.2686 | 497.602 | 204.5921 | 398.5393
1696.219 | 1646.219 | 193.5287 | 500.2145 | 561.7869 | 496.9259 | 204.3515 | 398.1865
1697.2205 | 1647.2205 | 193.3215 | 499.86 | 561.2776 | 496.3097 | 204.04 | 397.8971
1698.2219 | 1648.2219 | 193.1102 | 499.3731 | 560.7855 | 495.6383 | 203.9821 | 397.7269
1699.2234 | 1649.2234 | 192.9382 | 498.8928 | 560.2588 | 495.0029 | 203.4483 | 397.7038
1700.2248 | 1650.2248 | 192.7632 | 498.4036 | 559.776 | 494.379 | 203.3558 | 397.4291
1701.2262 | 1651.2262 | 192.5141 | 497.8881 | 559.2777 | 493.761 | 203.0707 | 397.2823
1702.2277 | 1652.2277 | 192.326 | 497.3517 | 558.7849 | 493.1557 | 202.7528 | 397.0849
1703.2191 | 1653.2191 | 192.1528 | 496.8224 | 558.2642 | 492.5592 | 202.9975 | 396.8787
1704.2205 | 1654.2205 | 192.0253 | 496.2864 | 557.7636 | 491.9454 | 203.3826 | 396.8739
1705.222 | 1655.222 | 191.8209 | 495.761 | 557.2436 | 491.3865 | 202.4264 | 396.5975
1706.2234 | 1656.2234 | 191.5698 | 495.2477 | 556.7271 | 490.8118 | 202.2545 | 396.3041
1707.2249 | 1657.2249 | 191.3653 | 494.7421 | 556.2211 | 490.2411 | 201.8363 | 396.1635
1708.2263 | 1658.2263 | 191.1702 | 494.2388 | 555.6979 | 489.692 | 201.4583 | 395.9833
1709.2177 | 1659.2177 | 190.9733 | 493.7391 | 555.1655 | 489.1296 | 201.7439 | 395.7285
1710.2192 | 1660.2192 | 190.7836 | 493.2403 | 554.6158 | 488.596 | 202.3165 | 395.6461
1711.2206 | 1661.2206 | 190.6322 | 492.738 | 554.081 | 488.0023 | 202.3211 | 395.2755
1712.2221 | 1662.2221 | 190.5168 | 492.243 | 553.5285 | 487.4275 | 201.7831 | 395.0983
1713.2235 | 1663.2235 | 190.4406 | 491.7484 | 552.9619 | 486.8501 | 201.0408 | 394.8306
1714.2249 | 1664.2249 | 190.2768 | 491.2273 | 552.411 | 486.3878 | 200.4239 | 394.6176
1715.2264 | 1665.2264 | 190.0612 | 490.7142 | 551.8729 | 485.8761 | 199.843 | 394.3787
1716.2278 | 1666.2278 | 189.8566 | 490.1905 | 551.3385 | 485.2416 | 199.3833 | 394.2166
1717.2192 | 1667.2192 | 189.6606 | 489.6627 | 550.7879 | 484.6316 | 198.5331 | 393.9837
1718.2207 | 1668.2207 | 189.5137 | 489.134 | 550.211 | 484.0775 | 197.7366 | 393.6739
1719.2221 | 1669.2221 | 189.3378 | 488.6068 | 549.6505 | 483.6176 | 197.7015 | 393.5202
1720.2236 | 1670.2236 | 189.1694 | 488.0735 | 549.0826 | 483.1396 | 197.0309 | 393.1869
1721.225 | 1671.225 | 189.0387 | 487.5554 | 548.5053 | 482.6686 | 196.4991 | 392.8065
1722.2264 | 1672.2264 | 188.9102 | 487.0309 | 547.9016 | 482.139 | 196.783 | 392.47
1723.2279 | 1673.2279 | 188.7122 | 486.5105 | 547.3324 | 481.658 | 196.5835 | 392.3597
1724.2193 | 1674.2193 | 188.5433 | 485.9911 | 546.7335 | 481.1512 | 196.3257 | 392.088
1725.2207 | 1675.2207 | 188.3961 | 485.4732 | 546.1318 | 480.6435 | 196.2633 | 391.9782
1726.2222 | 1676.2222 | 188.21 | 484.9524 | 545.5332 | 480.1185 | 196.0002 | 391.7599
1727.2236 | 1677.2236 | 187.9613 | 484.4223 | 544.9205 | 479.5616 | 196.1308 | 391.5645
1728.2251 | 1678.2251 | 187.7554 | 483.8574 | 544.3048 | 479.2109 | 196.482 | 391.3552
1729.2165 | 1679.2165 | 187.5629 | 483.2892 | 543.6888 | 478.7903 | 195.3929 | 391.1399
1730.2279 | 1680.2279 | 187.3903 | 482.7338 | 543.0868 | 478.3264 | 194.7766 | 390.8891
1731.2194 | 1681.2194 | 187.1927 | 482.1808 | 542.4806 | 477.7971 | 194.9912 | 390.6753
1732.2208 | 1682.2208 | 187.063 | 481.6362 | 541.8699 | 477.3552 | 195.0433 | 390.4554
1733.2223 | 1683.2223 | 186.8897 | 481.0755 | 541.2421 | 476.9415 | 194.3276 | 390.362
1734.2237 | 1684.2237 | 186.7364 | 480.5306 | 540.6317 | 476.4769 | 194.5714 | 390.1192
1735.2251 | 1685.2251 | 186.5816 | 479.9861 | 540.0079 | 475.9865 | 193.8365 | 389.7473
1736.2166 | 1686.2166 | 186.4759 | 479.4557 | 539.3603 | 475.4768 | 193.1596 | 389.474
1737.218 | 1687.218 | 186.3554 | 478.9089 | 538.7475 | 474.9578 | 192.4916 | 389.1231
1738.2194 | 1688.2194 | 186.2057 | 478.409 | 538.1086 | 474.4388 | 192.1648 | 388.8392
1739.2209 | 1689.2209 | 186.0217 | 477.8856 | 537.4789 | 473.8665 | 191.1549 | 388.4288
1740.2223 | 1690.2223 | 185.815 | 477.3754 | 536.8454 | 473.3091 | 190.8967 | 388.23
1741.2238 | 1691.2238 | 185.6733 | 476.857 | 536.1884 | 472.7593 | 191.3793 | 388.0227
1742.2252 | 1692.2252 | 185.5516 | 476.3419 | 535.5518 | 472.2177 | 191.4591 | 387.7553
1743.2266 | 1693.2266 | 185.4139 | 475.8165 | 534.8783 | 471.6823 | 191.5986 | 387.4559
1744.2281 | 1694.2281 | 185.2205 | 475.2868 | 534.216 | 471.1317 | 191.8396 | 387.2071
1745.2195 | 1695.2195 | 185.0284 | 474.7506 | 533.5503 | 470.6487 | 191.4433 | 386.9626
1746.2209 | 1696.2209 | 184.8186 | 474.2185 | 532.8933 | 470.1796 | 190.9325 | 386.8648
1747.2224 | 1697.2224 | 184.5811 | 473.6814 | 532.2478 | 469.6982 | 191.1316 | 386.6465
1748.2238 | 1698.2238 | 184.3531 | 473.1572 | 531.6099 | 469.1742 | 190.7294 | 386.5128

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 2 |  |  | 2006-06-29 | 15:03
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-48.3333 | 229938 |  | -45.6667 | 229738 | -44.6667 | 229738 | -43.3333 | 115169 | -48.3333 | 115169
-37.5 | 229938 |  | -35.1667 | 229738 | -33.8333 | 229738 | -32.8333 | 230438 | -37.5 | 229738
-26.5 | 229938 |  | -24.5 | 229738 | -23.1667 | 229738 | -21.8333 | 230438 | -26.5 | 229738
-15.8333 | 229938 |  | -13.5 | 229738 | -12.1667 | 229738 | -11.1667 | 230438 | -15.8333 | 229738
-5.1667 | 45927.6 |  | -2.5 | 229738 | -1.5 | 115169 | -0.16667 | 230438 | -5.1667 | 45927.6
5.3333 | 230038 |  | 8.1667 | 229738 | 9 | 229738 | 10.5 | 230438 | 5.3333 | 229738
16.5 | 229938 |  | 18.8333 | 229738 | 20.1667 | 115169 | 21.1667 | 230438 | 16.5 | 115169
27.5 | 229938 |  | 29.5 | 114819 | 30.8333 | 229738 | 32.1667 | 230438 | 27.5 | 114819
38.1667 | 229938 |  | 40.5 | 230038 | 41.8333 | 229738 | 42.8333 | 230438 | 38.1667 | 229738
49 | 230038 |  | 51.5 | 230038 | 52.6667 | 229738 | 53.8333 | 230438 | 49 | 229738
59.6667 | 230038 |  | 62.3333 | 229738 | 63.1667 | 114919 | 64.5 | 230438 | 59.6667 | 114919
70.5 | 229938 |  | 73 | 229738 | 74.1667 | 115169 | 75.3333 | 115169 | 70.5 | 115169
81.5 | 114919 |  | 83.6667 | 114819 | 85 | 114819 | 86.1667 | 230438 | 81.5 | 114819
92.1667 | 114969 |  | 94.5 | 115419 | 95.8333 | 229738 | 96.8333 | 230438 | 92.1667 | 114969
102.8333 | 229938 |  | 105.5 | 229738 | 106.5 | 229738 | 107.8333 | 230438 | 102.8333 | 229738
113.5 | 229938 |  | 116.1667 | 229738 | 117.1667 | 115169 | 118.5 | 230438 | 113.5 | 115169
124.5 | 114919 |  | 126.8333 | 115419 | 128.1667 | 114819 | 129.1667 | 230438 | 124.5 | 114819
135.5 | 114919 |  | 137.5 | 114819 | 138.8333 | 115169 | 140.1667 | 117869 | 135.5 | 114819
146.1667 | 229938 |  | 148.5 | 115419 | 149.8333 | 229738 | 150.8333 | 230438 | 146.1667 | 115419
156.8333 | 229938 |  | 159.5 | 229738 | 160.5 | 229738 | 161.8333 | 115419 | 156.8333 | 115419
167.5 | 114969 |  | 170.1667 | 114819 | 171.3333 | 114819 | 172.6667 | 230438 | 167.5 | 114819
178.5 | 229938 |  | 180.8333 | 229738 | 182 | 229738 | 183 | 230438 | 178.5 | 229738
189.5 | 229938 |  | 191.5 | 114969 | 192.8333 | 114819 | 194.1667 | 230438 | 189.5 | 114819
200.1667 | 229938 |  | 202.5 | 115419 | 203.8333 | 229738 | 204.8333 | 230438 | 200.1667 | 115419
210.8333 | 114969 |  | 213.5 | 114969 | 214.5 | 114819 | 215.8333 | 115419 | 210.8333 | 114819
221.5 | 229938 |  | 224.1667 | 114819 | 225.1667 | 115169 | 226.5 | 117869 | 221.5 | 114819
232.5 | 229938 |  | 235 | 229738 | 236.1667 | 229738 | 237.3333 | 115169 | 232.5 | 115169
243.5 | 229938 |  | 245.5 | 114819 | 246.8333 | 229738 | 248.1667 | 230438 | 243.5 | 114819
254.1667 | 229938 |  | 256.5 | 114819 | 257.8333 | 114819 | 258.8333 | 230438 | 254.1667 | 114819
264.8333 | 229938 |  | 267.5 | 229738 | 268.5 | 114919 | 269.8333 | 115169 | 264.8333 | 114919
275.5 | 229938 |  | 278.1667 | 229738 | 279.1667 | 229738 | 280.5 | 230438 | 275.5 | 229738
286.5 | 229938 |  | 288.8333 | 114969 | 290.1667 | 229738 | 291.1667 | 230438 | 286.5 | 114969
297.5 | 114919 |  | 299.5 | 115419 | 300.8333 | 229738 | 302.1667 | 117869 | 297.5 | 114919
308.1667 | 114969 |  | 310.5 | 229738 | 311.8333 | 229738 | 312.8333 | 230438 | 308.1667 | 114969
318.8333 | 229938 |  | 321.5 | 114819 | 322.5 | 115169 | 323.8333 | 115419 | 318.8333 | 114819
329.5 | 229938 |  | 332.1667 | 229738 | 333.1667 | 229738 | 334.5 | 117869 | 329.5 | 117869
340.5 | 117869 |  | 342.8333 | 229738 | 344.1667 | 229738 | 345.1667 | 230438 | 340.5 | 117869
351.5 | 229938 |  | 353.6667 | 76512.6667 | 355 | 229738 | 356.1667 | 115419 | 351.5 | 76512.6667
362.3333 | 229938 |  | 364.5 | 229738 | 365.8333 | 229738 | 367 | 230438 | 362.3333 | 229738
372.8333 | 117869 |  | 375.5 | 229738 | 376.5 | 229738 | 377.8333 | 115169 | 372.8333 | 115169
383.5 | 229938 |  | 386.1667 | 229738 | 387.1667 | 229738 | 388.5 | 230438 | 383.5 | 229738
394.5 | 114969 |  | 396.8333 | 229738 | 398.1667 | 229738 | 399.1667 | 230438 | 394.5 | 114969
405.5 | 114919 |  | 407.5 | 114819 | 408.8333 | 229738 | 410.1667 | 230438 | 405.5 | 114819
416.3333 | 229938 |  | 418.5 | 229738 | 419.8333 | 229738 | 421 | 230438 | 416.3333 | 229738
426.8333 | 229938 |  | 429.5 | 229738 | 430.5 | 114919 | 431.8333 | 230438 | 426.8333 | 114919
437.5 | 114919 |  | 440.1667 | 229738 | 441.1667 | 229738 | 442.5 | 115169 | 437.5 | 114919
448.5 | 114969 |  | 450.8333 | 229738 | 452.1667 | 229738 | 453.1667 | 230438 | 448.5 | 114969
459.5 | 229938 |  | 461.5 | 229738 | 462.8333 | 229738 | 464.1667 | 230438 | 459.5 | 229738
470.3333 | 229938 |  | 472.5 | 229738 | 473.8333 | 114819 | 475 | 230438 | 470.3333 | 114819
480.8333 | 117869 |  | 483.5 | 114969 | 484.5 | 229738 | 485.8333 | 117869 | 480.8333 | 114969
491.5 | 229938 |  | 494.1667 | 229738 | 495.1667 | 229738 | 496.5 | 230438 | 491.5 | 229738
502.5 | 114919 |  | 504.8333 | 229738 | 506.1667 | 229738 | 507.1667 | 230438 | 502.5 | 114919
513.5 | 229938 |  | 515.5 | 115419 | 516.8333 | 229738 | 518.1667 | 230438 | 513.5 | 115419
524.3333 | 229938 |  | 526.5 | 229738 | 527.8333 | 115169 | 529 | 115169 | 524.3333 | 115169
534.8333 | 229938 |  | 537.5 | 229738 | 538.3333 | 229738 | 539.6667 | 230438 | 534.8333 | 229738
545.5 | 229938 |  | 548.1667 | 229738 | 549.1667 | 114819 | 550.5 | 115419 | 545.5 | 114819
556.5 | 229938 |  | 558.8333 | 115419 | 560.1667 | 229738 | 561.1667 | 230438 | 556.5 | 115419
567.5 | 117869 |  | 569.5 | 229738 | 570.8333 | 229738 | 572.1667 | 230438 | 567.5 | 117869
578.1667 | 114919 |  | 580.5 | 229738 | 581.8333 | 229738 | 582.8333 | 230438 | 578.1667 | 114919
588.8333 | 229938 |  | 591.5 | 229738 | 592.3333 | 229738 | 593.6667 | 230438 | 588.8333 | 229738
599.5 | 229938 |  | 602 | 229738 | 603.1667 | 229738 | 604.3333 | 230438 | 599.5 | 229738
610.5 | 229938 |  | 612.8333 | 229738 | 614.1667 | 229738 | 615.1667 | 230438 | 610.5 | 229738
621.5 | 229938 |  | 623.5 | 229738 | 624.8333 | 229738 | 626.1667 | 230438 | 621.5 | 229738
632.1667 | 229938 |  | 634.5 | 229738 | 635.8333 | 229738 | 636.8333 | 230438 | 632.1667 | 229738
642.8333 | 229938 |  | 645.5 | 229738 | 646.5 | 229738 | 647.8333 | 230438 | 642.8333 | 229738
653.5 | 229938 |  | 656.1667 | 229738 | 657.1667 | 229738 | 658.5 | 230438 | 653.5 | 229738
664.5 | 229938 |  | 666.8333 | 229738 | 668.1667 | 229738 | 669.1667 | 230438 | 664.5 | 229738
675.5 | 229938 |  | 677.5 | 229738 | 678.8333 | 229738 | 680.1667 | 230438 | 675.5 | 229738
686.1667 | 114969 |  | 688.5 | 114819 | 689.8333 | 229738 | 690.8333 | 230438 | 686.1667 | 114819
696.6667 | 229938 |  | 699.3333 | 115419 | 700.3333 | 229738 | 701.6667 | 115419 | 696.6667 | 115419
707.5 | 229938 |  | 710 | 229738 | 711.1667 | 229738 | 712.3333 | 230438 | 707.5 | 229738
718.5 | 229938 |  | 720.6667 | 229738 | 722 | 229738 | 723.1667 | 230438 | 718.5 | 229738
729.5 | 229938 |  | 731.5 | 115419 | 732.8333 | 229738 | 734.1667 | 230438 | 729.5 | 115419
740.1667 | 229938 |  | 742.5 | 229738 | 743.8333 | 229738 | 744.8333 | 230438 | 740.1667 | 229738
750.8333 | 229938 |  | 753.5 | 229738 | 754.3333 | 229738 | 755.6667 | 230438 | 750.8333 | 229738
761.5 | 229938 |  | 764 | 229738 | 765.1667 | 229738 | 766.3333 | 230438 | 761.5 | 229738
772.5 | 229938 |  | 774.6667 | 229738 | 776 | 229738 | 777.1667 | 230438 | 772.5 | 229738
783.5 | 229938 |  | 785.5 | 229738 | 786.8333 | 229738 | 788.1667 | 230438 | 783.5 | 229738
794.1667 | 117869 |  | 796.5 | 229738 | 797.8333 | 229738 | 798.8333 | 230438 | 794.1667 | 117869
804.8333 | 229938 |  | 807.5 | 114969 | 808.5 | 115169 | 809.8333 | 230438 | 804.8333 | 114969
815.5 | 229938 |  | 818 | 229738 | 819.1667 | 229738 | 820.3333 | 230438 | 815.5 | 229738
826.5 | 229938 |  | 828.6667 | 229738 | 830 | 229738 | 831.1667 | 230438 | 826.5 | 229738
837.3333 | 114919 |  | 839.5 | 77182.6048 | 840.8333 | 229738 | 842 | 15286.4945 | 837.3333 | 15286.4945
848 | 229938 |  | 850.5 | 12566.2728 | 851.6667 | 229738 | 852.8333 | 3310.1384 | 848 | 3310.1384
858.6667 | 229938 |  | 861.3333 | 2130.8197 | 862.3333 | 58702.2382 | 863.6667 | 3602.894 | 858.6667 | 2130.8197
869.5 | 1075.5165 |  | 872 | 820.0507 | 873.1667 | 22052.8272 | 874.3333 | 1259.7635 | 869.5 | 820.0507
880.5 | 5315.3464 |  | 882.6667 | 1587.9693 | 884 | 14471.7484 | 885.1667 | 1379.6256 | 880.5 | 1379.6256
891.3333 | 1809.9858 |  | 893.5 | 1393.1569 | 894.8333 | 6230.1364 | 896 | 1210.7424 | 891.3333 | 1210.7424
902 | 3237.2236 |  | 904.5 | 1375.5688 | 905.6667 | 2964.0226 | 906.8333 | 1091.9042 | 902 | 1091.9042
912.6667 | 1928.3347 |  | 915.3333 | 302.162 | 916.3333 | 2908.5068 | 917.6667 | 921.1389 | 912.6667 | 302.162
923.5 | 2237.5882 |  | 926 | 1002.7741 | 927.1667 | 1960.8256 | 928.3333 | 926.247 | 923.5 | 926.247
934.5 | 655.871 |  | 936.6667 | 790.331 | 938 | 6286.9699 | 939.1667 | 1190.839 | 934.5 | 655.871
945.3333 | 943.7312 |  | 947.5 | 999.9785 | 948.8333 | 355.4008 | 950 | 1012.6102 | 945.3333 | 355.4008
956 | 531.1877 |  | 958.5 | 413.3675 | 959.6667 | 781.9736 | 960.8333 | 935.3726 | 956 | 413.3675
966.6667 | 2044.5846 |  | 969.3333 | 308.7579 | 970.3333 | 496.6537 | 971.6667 | 536.8069 | 966.6667 | 308.7579
977.5 | 673.002 |  | 980 | 42.373 | 981.1667 | 956.7885 | 982.3333 | 38.7365 | 977.5 | 38.7365
988.5 | 608.6146 |  | 990.6667 | 436.4445 | 992 | 746.2809 | 993.1667 | 628.4609 | 988.5 | 436.4445
999.3333 | 363.3264 |  | 1001.5 | 49.6708 | 1002.8333 | 541.3329 | 1004 | 50.6878 | 999.3333 | 49.6708
1010 | 323.6538 |  | 1012.5 | 492.3385 | 1013.6667 | 1073.6633 | 1014.8333 | 735.9838 | 1010 | 323.6538
1020.6667 | 463.6252 |  | 1023.3333 | 493.7736 | 1024.3333 | 536.8103 | 1025.6667 | 2390.3632 | 1020.6667 | 463.6252
1031.5 | 104.9616 |  | 1034 | 183.7021 | 1035.1667 | 321.0903 | 1036.3333 | 141.8458 | 1031.5 | 104.9616
1042.5 | 258.1219 |  | 1044.6667 | 51.1472 | 1046 | 55.4717 | 1047.1667 | 352.3398 | 1042.5 | 51.1472
1053.3333 | 256.7253 |  | 1055.5 | 217.8886 | 1056.8333 | 385.2471 | 1058 | 474.4766 | 1053.3333 | 217.8886
1064 | 346.9091 |  | 1066.5 | 131.405 | 1067.6667 | 154.1195 | 1068.8333 | 239.3897 | 1064 | 131.405
1074.6667 | 151.714 |  | 1077.3333 | 124.209 | 1078.3333 | 152.9121 | 1079.6667 | 293.8818 | 1074.6667 | 124.209
1085.5 | 104.8954 |  | 1088 | 32.1942 | 1089.1667 | 31.6399 | 1090.3333 | 172.1398 | 1085.5 | 31.6399
1096.5 | 84.5313 |  | 1098.6667 | 104.0137 | 1100 | 198.8563 | 1101.1667 | 164.1656 | 1096.5 | 84.5313
1107.3333 | 128.6353 |  | 1109.5 | 107.7929 | 1110.8333 | 91.9279 | 1112 | 111.3931 | 1107.3333 | 91.9279
1118 | 29.0157 |  | 1120.5 | 19.2108 | 1121.6667 | 26.4378 | 1122.8333 | 35.6322 | 1118 | 19.2108
1128.6667 | 73.0746 |  | 1131.3333 | 51.5381 | 1132.1667 | 18.0543 | 1133.5 | 18.9136 | 1128.6667 | 18.0543
1139.5 | 0.05119 |  | 1141.8333 | 0.033407 | 1143.3333 | 23.564 | 1144.3333 | 14.0434 | 1139.5 | 0.033407
1150.5 | 8.5039 |  | 1152.6667 | 30.7186 | 1154 | 59.9814 | 1155.1667 | 73.0442 | 1150.5 | 8.5039
1161.3333 | 32.057 |  | 1163.5 | 85.3226 | 1164.8333 | 6.6514 | 1166 | 14.1414 | 1161.3333 | 6.6514
1172 | 14.7797 |  | 1174.5 | 45.1227 | 1175.6667 | 46.4846 | 1176.8333 | 17.8918 | 1172 | 14.7797
1182.5 | 29.8579 |  | 1185.1667 | 48.7526 | 1186.1667 | 26.1122 | 1187.5 | 24.1021 | 1182.5 | 24.1021
1193.5 | 7.1955 |  | 1195.8333 | 26.5861 | 1197.1667 | 24.7207 | 1198.1667 | 18.3453 | 1193.5 | 7.1955
1204.5 | 19.8244 |  | 1206.6667 | 47.5 | 1208 | 28.439 | 1209.1667 | 41.3447 | 1204.5 | 19.8244
1215.3333 | 5.7988 |  | 1217.5 | 10.8681 | 1218.8333 | 7.9441 | 1220 | 44.7446 | 1215.3333 | 5.7988
1226 | 61.586 |  | 1228.5 | 10.9924 | 1229.6667 | 40.8436 | 1230.8333 | 51.4017 | 1226 | 10.9924
1236.6667 | 45.3701 |  | 1239.3333 | 16.497 | 1240.3333 | 26.3271 | 1241.6667 | 28.2253 | 1236.6667 | 16.497
1247.5 | 25.2013 |  | 1250 | 2.6949 | 1251.1667 | 0.72063 | 1252.3333 | 3.4122 | 1247.5 | 0.72063
1258.5 | 12.7615 |  | 1260.6667 | 2.7199 | 1262 | 1.2917 | 1263.1667 | 5.8703 | 1258.5 | 1.2917
1269.1667 | 23.5299 |  | 1271.5 | 22.3329 | 1272.8333 | 44.741 | 1273.8333 | 53.0705 | 1269.1667 | 22.3329
1279.8333 | 19.2752 |  | 1282.5 | 40.7727 | 1283.5 | 13.5257 | 1284.8333 | 14.398 | 1279.8333 | 13.5257
1290.5 | 1.1704 |  | 1293.1667 | 0.72005 | 1294.3333 | 15.4302 | 1295.6667 | 59.9966 | 1290.5 | 0.72005
1301.5 | 7.919 |  | 1304 | 2.8356 | 1305.1667 | 7.5306 | 1306.3333 | 30.775 | 1301.5 | 2.8356
1312.5 | 0.17847 |  | 1314.5 | 1.627 | 1315.8333 | 1.2312 | 1317.1667 | 24.4676 | 1312.5 | 0.17847
1323.1667 | 3.9889 |  | 1325.6667 | 24.7285 | 1327 | 3.6595 | 1327.8333 | 70.8217 | 1323.1667 | 3.6595
1333.8333 | 52.5614 |  | 1336.5 | 25.8735 | 1337.5 | 14.7685 | 1338.8333 | 61.9197 | 1333.8333 | 14.7685
1344.5 | 20.3685 |  | 1347.1667 | 7.3321 | 1348.1667 | 22.7576 | 1349.5 | 26.4513 | 1344.5 | 7.3321
1355.5 | 19.1966 |  | 1357.8333 | 51.3578 | 1359.1667 | 6.9841 | 1360.1667 | 9.5498 | 1355.5 | 6.9841
1366.5 | 3.4064 |  | 1368.6667 | 5.2759 | 1370 | 8.7949 | 1371.1667 | 24.9731 | 1366.5 | 3.4064
1377.3333 | 13.6792 |  | 1379.5 | 1.7244 | 1380.8333 | 7.9721 | 1382 | 0.83964 | 1377.3333 | 0.83964
1388 | 9.9705 |  | 1390.5 | 0.63141 | 1391.6667 | 3.0571 | 1392.8333 | 1.0712 | 1388 | 0.63141
1398.6667 | 12.7457 |  | 1401.3333 | 3.1327 | 1402.3333 | 6.0752 | 1403.6667 | 5.2807 | 1398.6667 | 3.1327
1409.5 | 14.0287 |  | 1411.8333 | 13.8189 | 1413.1667 | 10.1989 | 1414.1667 | 14.9322 | 1409.5 | 10.1989
1420.5 | 4.5654 |  | 1422.5 | 2.2794 | 1423.8333 | 8.5488 | 1425.1667 | 1.1621 | 1420.5 | 1.1621
1431.1667 | 2.2912 |  | 1433.5 | 8.5681 | 1434.8333 | 6.2435 | 1435.8333 | 13.9057 | 1431.1667 | 2.2912
1441.8333 | 12.9259 |  | 1444.5 | 16.0499 | 1445.5 | 12.2421 | 1446.8333 | 34.6822 | 1441.8333 | 12.2421
1452.5 | 0.78301 |  | 1455.1667 | 2.2332 | 1456.1667 | 0.69969 | 1457.5 | 24.1972 | 1452.5 | 0.69969
1463.5 | 0.10193 |  | 1465.8333 | 0.56446 | 1467.1667 | 1.1701 | 1468.1667 | 19.0628 | 1463.5 | 0.10193
1474.5 | 1.1385 |  | 1476.5 | 3.6505 | 1477.8333 | 10.3504 | 1479.1667 | 0.71604 | 1474.5 | 0.71604
1485.3333 | 4.255 |  | 1487.5 | 8.0006 | 1488.8333 | 46.159 | 1490 | 10.7217 | 1485.3333 | 4.255
1496 | 1.5991 |  | 1498.5 | 6.7808 | 1499.6667 | 6.9003 | 1500.8333 | 4.4199 | 1496 | 1.5991
1506.6667 | 2.8272 |  | 1509.3333 | 1.9395 | 1510.1667 | 0.62342 | 1511.5 | 4.0321 | 1506.6667 | 0.62342
1517.5 | 1.6874 |  | 1519.8333 | 13.7742 | 1521.1667 | 9.4638 | 1522.1667 | 15.5656 | 1517.5 | 1.6874
1528.5 | 19.7439 |  | 1530.5 | 33.204 | 1531.8333 | 41.7384 | 1533.1667 | 17.9871 | 1528.5 | 17.9871
1539.1667 | 7.7327 |  | 1541.5 | 9.7989 | 1542.8333 | 105.0843 | 1543.8333 | 12.3248 | 1539.1667 | 7.7327
1549.8333 | 19.107 |  | 1552.5 | 5.7774 | 1553.5 | 1.9663 | 1554.8333 | 1.2486 | 1549.8333 | 1.2486
1560.5 | 17.9136 |  | 1563.1667 | 8.0271 | 1564.1667 | 23.9127 | 1565.5 | 14.135 | 1560.5 | 8.0271
1571.5 | 9.986 |  | 1573.8333 | 34.0503 | 1575.1667 | 27.205 | 1576.1667 | 47.6978 | 1571.5 | 9.986
1582.5 | 3.902 |  | 1584.5 | 3.3701 | 1585.8333 | 30.836 | 1587.1667 | 15.4794 | 1582.5 | 3.3701
1593.1667 | 53.4438 |  | 1595.5 | 192.1353 | 1596.8333 | 23.3242 | 1597.8333 | 37.3803 | 1593.1667 | 23.3242
1603.8333 | 3.182 |  | 1606.5 | 0.69684 | 1607.5 | 0.62272 | 1608.8333 | 74.3049 | 1603.8333 | 0.62272
1614.5 | 27.6689 |  | 1617.1667 | 102.1988 | 1618.1667 | 73.0685 | 1619.5 | 63.7348 | 1614.5 | 27.6689
1625.5 | 69.0185 |  | 1627.8333 | 9.0209 | 1629.1667 | 118.4217 | 1630.1667 | 14.8881 | 1625.5 | 9.0209
1636.5 | 28.7031 |  | 1638.5 | 29.3138 | 1639.8333 | 39.0371 | 1641.1667 | 74.8074 | 1636.5 | 28.7031
1647.1667 | 8.9277 |  | 1649.6667 | 7.9784 | 1650.8333 | 7.815 | 1652 | 111.809 | 1647.1667 | 7.815
1657.8333 | 99.136 |  | 1660.5 | 20.5712 | 1661.5 | 35.3927 | 1662.8333 | 54.8168 | 1657.8333 | 20.5712
1668.5 | 31.4408 |  | 1671.1667 | 439.4492 | 1672.1667 | 39.5164 | 1673.5 | 116.684 | 1668.5 | 31.4408
1679.5 | 31.8261 |  | 1681.8333 | 124.4121 | 1683.1667 | 2.4261 | 1684.1667 | 1.7286 | 1679.5 | 1.7286

## C-C
Conductor to Conductor Resistances
Penlight Test 2 |  |  | 2006-06-29 | 15:03
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-50 | 230037.9994 | -48.5 | 229937.9994 | -46.5 | 235837.9994 | -44.5 | 229737.9994 | -42.5 | 230937.9994 | -41 | 230437.9994 | -50 | 229737.9994
-39.5 | 230037.9994 | -37.5 | 229937.9994 | -35.5 | 235837.9994 | -33.5 | 229737.9994 | -32.5 | 230937.9994 | -30.5 | 230437.9994 | -39.5 | 229737.9994
-28.5 | 230037.9994 | -26.5 | 229937.9994 | -24.5 | 235837.9994 | -23.5 | 229737.9994 | -21.5 | 230937.9994 | -19.5 | 230437.9994 | -28.5 | 229737.9994
-17.5 | 230037.9994 | -15.5 | 229937.9994 | -14.5 | 235837.9994 | -12.5 | 229737.9994 | -10.5 | 230937.9994 | -8.5 | 230437.9994 | -17.5 | 229737.9994
-6.5 | 45927.5969 | -5.5 | 229937.9994 | -3.5 | 235837.9994 | -1.5 | 229737.9994 | 0.5 | 230937.9994 | 2.5 | 115168.9988 | -6.5 | 45927.5969
3.5 | 230037.9994 | 5 | 229738.0869 | 7.5 | 235837.9994 | 9.5 | 229737.9994 | 11.5 | 230937.9994 | 12.5 | 230437.9994 | 3.5 | 229737.9994
14.5 | 230037.9994 | 16.5 | 229937.9994 | 18.5 | 235837.9994 | 20.5 | 229737.9994 | 21.5 | 230937.9994 | 23.5 | 115168.9988 | 14.5 | 115168.9988
25.5 | 230037.9994 | 27.5 | 229937.9994 | 29.5 | 235837.9994 | 30.5 | 114818.9988 | 32.5 | 230937.9994 | 34.5 | 230437.9994 | 25.5 | 114818.9988
36.5 | 230037.9994 | 38.5 | 229937.9994 | 39.5 | 235837.9994 | 41.5 | 229538.087 | 43.5 | 230937.9994 | 45.5 | 230437.9994 | 36.5 | 229538.087
47.5 | 230037.9994 | 49 | 229738.0869 | 50.5 | 235837.9994 | 52.5 | 229538.087 | 54.5 | 230937.9994 | 56.5 | 230437.9994 | 47.5 | 229538.087
58 | 230037.9994 | 59.5 | 229538.2608 | 61.5 | 235837.9994 | 63.5 | 229737.9994 | 65.5 | 230937.9994 | 66.5 | 230437.9994 | 58 | 229538.2608
68.5 | 229838.0869 | 70.5 | 229937.9994 | 72.5 | 235638.0848 | 74.5 | 229737.9994 | 76 | 230937.9994 | 77.5 | 115168.9988 | 68.5 | 115168.9988
79.5 | 229638.2607 | 81.5 | 114918.9988 | 83.5 | 117868.9988 | 85 | 114818.9988 | 86.5 | 115418.9988 | 88.5 | 115168.9988 | 79.5 | 114818.9988
90.5 | 114968.9988 | 92.5 | 229937.9994 | 93.5 | 235837.9994 | 95.5 | 229737.9994 | 97.5 | 115418.9988 | 99.5 | 230437.9994 | 90.5 | 114968.9988
101.5 | 230037.9994 | 102.5 | 229937.9994 | 104.5 | 235837.9994 | 106.5 | 229737.9994 | 108.5 | 230937.9994 | 110.5 | 230437.9994 | 101.5 | 229737.9994
111.5 | 230037.9994 | 113.5 | 229937.9994 | 115.5 | 235837.9994 | 117.5 | 229737.9994 | 119.5 | 230937.9994 | 120.5 | 115168.9988 | 111.5 | 115168.9988
122.5 | 114968.9988 | 124.5 | 114918.9988 | 126.5 | 235638.0848 | 128.5 | 229737.9994 | 129.5 | 115418.9988 | 131.5 | 115168.9988 | 122.5 | 114918.9988
133.5 | 230037.9994 | 135.5 | 114918.9988 | 137.5 | 235837.9994 | 138.5 | 114818.9988 | 140.5 | 230937.9994 | 142.5 | 115168.9988 | 133.5 | 114818.9988
144.5 | 230037.9994 | 146.5 | 229937.9994 | 147.5 | 235837.9994 | 149.5 | 229737.9994 | 151.5 | 115418.9988 | 153.5 | 230437.9994 | 144.5 | 115418.9988
155.5 | 230037.9994 | 156.5 | 229937.9994 | 158.5 | 235837.9994 | 160.5 | 229737.9994 | 162.5 | 230937.9994 | 164.5 | 230437.9994 | 155.5 | 229737.9994
165.5 | 114968.9988 | 167.5 | 229937.9994 | 169.5 | 117868.9988 | 171.5 | 114818.9988 | 173.5 | 230937.9994 | 175 | 230437.9994 | 165.5 | 114818.9988
176.5 | 230037.9994 | 178.5 | 229937.9994 | 180.5 | 235837.9994 | 182.5 | 229737.9994 | 183.5 | 230937.9994 | 185 | 230437.9994 | 176.5 | 229737.9994
187.5 | 230037.9994 | 189.5 | 229937.9994 | 191.5 | 235837.9994 | 192.5 | 229737.9994 | 194.5 | 115418.9988 | 196.5 | 115168.9988 | 187.5 | 115168.9988
198.5 | 230037.9994 | 200.5 | 229937.9994 | 201.5 | 235837.9994 | 203.5 | 229538.087 | 205.5 | 115418.9988 | 207.5 | 230437.9994 | 198.5 | 115418.9988
209.5 | 114968.9988 | 210.5 | 229937.9994 | 212.5 | 235837.9994 | 214.5 | 229737.9994 | 216.5 | 115418.9988 | 218.5 | 230437.9994 | 209.5 | 114968.9988
219.5 | 230037.9994 | 221.5 | 229937.9994 | 223.5 | 235837.9994 | 225.5 | 114818.9988 | 227.5 | 230937.9994 | 228.5 | 115168.9988 | 219.5 | 114818.9988
230.5 | 230037.9994 | 232.5 | 229937.9994 | 234.5 | 235837.9994 | 236.5 | 229737.9994 | 238 | 230937.9994 | 239.5 | 230437.9994 | 230.5 | 229737.9994
241.5 | 230037.9994 | 243.5 | 229937.9994 | 245.5 | 235837.9994 | 246.5 | 114818.9988 | 248.5 | 230937.9994 | 250.5 | 230437.9994 | 241.5 | 114818.9988
252.5 | 230037.9994 | 254.5 | 229937.9994 | 255.5 | 235837.9994 | 257.5 | 114818.9988 | 259.5 | 230937.9994 | 261.5 | 230437.9994 | 252.5 | 114818.9988
263.5 | 230037.9994 | 264.5 | 229937.9994 | 266.5 | 235837.9994 | 268.5 | 229737.9994 | 270.5 | 230937.9994 | 272.5 | 230437.9994 | 263.5 | 229737.9994
273.5 | 230037.9994 | 275.5 | 229937.9994 | 277.5 | 235837.9994 | 279.5 | 229737.9994 | 281.5 | 230937.9994 | 282.5 | 230437.9994 | 273.5 | 229737.9994
284.5 | 230037.9994 | 286.5 | 229937.9994 | 288.5 | 235837.9994 | 290.5 | 229737.9994 | 291.5 | 115418.9988 | 293.5 | 230437.9994 | 284.5 | 115418.9988
295.5 | 230037.9994 | 297.5 | 114918.9988 | 299.5 | 235837.9994 | 300.5 | 229737.9994 | 302.5 | 115418.9988 | 304.5 | 230437.9994 | 295.5 | 114918.9988
306.5 | 114968.9988 | 308.5 | 229937.9994 | 309.5 | 235837.9994 | 311.5 | 229737.9994 | 313.5 | 230937.9994 | 315.5 | 230437.9994 | 306.5 | 114968.9988
317.5 | 230037.9994 | 318.5 | 229937.9994 | 320.5 | 235837.9994 | 322.5 | 114818.9988 | 324.5 | 230937.9994 | 326.5 | 115168.9988 | 317.5 | 114818.9988
327.5 | 230037.9994 | 329.5 | 229937.9994 | 331.5 | 235837.9994 | 333.5 | 229737.9994 | 335.5 | 230937.9994 | 336.5 | 230437.9994 | 327.5 | 229737.9994
338.5 | 230037.9994 | 340.5 | 229937.9994 | 342.5 | 117868.9988 | 344.5 | 229737.9994 | 345.5 | 230937.9994 | 347.5 | 230437.9994 | 338.5 | 117868.9988
349.5 | 230037.9994 | 351.5 | 229937.9994 | 353.5 | 235837.9994 | 355 | 76512.6648 | 356.5 | 230937.9994 | 358.5 | 230437.9994 | 349.5 | 76512.6648
360.5 | 230037.9994 | 362.5 | 229937.9994 | 364 | 235837.9994 | 365.5 | 229737.9994 | 367.5 | 230937.9994 | 369.5 | 230437.9994 | 360.5 | 229737.9994
371.5 | 230037.9994 | 372.5 | 229937.9994 | 374.5 | 117868.9988 | 376.5 | 229737.9994 | 378.5 | 230937.9994 | 380.5 | 230437.9994 | 371.5 | 117868.9988
381.5 | 230037.9994 | 383.5 | 229937.9994 | 385.5 | 235837.9994 | 387.5 | 229737.9994 | 389.5 | 230937.9994 | 390.5 | 230437.9994 | 381.5 | 229737.9994
392.5 | 114968.9988 | 394.5 | 229937.9994 | 396.5 | 235837.9994 | 398.5 | 229737.9994 | 399.5 | 230937.9994 | 401.5 | 230437.9994 | 392.5 | 114968.9988
403.5 | 114968.9988 | 405.5 | 114918.9988 | 407.5 | 235837.9994 | 408.5 | 114818.9988 | 410.5 | 230937.9994 | 412.5 | 230437.9994 | 403.5 | 114818.9988
414.5 | 230037.9994 | 416.5 | 229937.9994 | 418 | 235837.9994 | 419.5 | 229737.9994 | 421.5 | 230937.9994 | 423.5 | 230437.9994 | 414.5 | 229737.9994
425.5 | 230037.9994 | 426.5 | 229937.9994 | 428.5 | 235837.9994 | 430.5 | 229737.9994 | 432.5 | 230937.9994 | 434.5 | 230437.9994 | 425.5 | 229737.9994
435.5 | 230037.9994 | 437.5 | 114918.9988 | 439.5 | 235837.9994 | 441.5 | 229737.9994 | 443.5 | 230937.9994 | 444.5 | 230437.9994 | 435.5 | 114918.9988
446.5 | 114968.9988 | 448.5 | 229937.9994 | 450.5 | 235837.9994 | 452.5 | 229737.9994 | 453.5 | 230937.9994 | 455.5 | 230437.9994 | 446.5 | 114968.9988
457.5 | 230037.9994 | 459.5 | 229937.9994 | 461.5 | 235837.9994 | 462.5 | 229737.9994 | 464.5 | 230937.9994 | 466.5 | 230437.9994 | 457.5 | 229737.9994
468.5 | 230037.9994 | 470.5 | 229937.9994 | 472 | 235837.9994 | 473.5 | 229737.9994 | 475.5 | 230937.9994 | 477.5 | 230437.9994 | 468.5 | 229737.9994
479.5 | 230037.9994 | 480.5 | 229937.9994 | 482.5 | 117868.9988 | 484.5 | 229737.9994 | 486.5 | 230937.9994 | 488.5 | 230437.9994 | 479.5 | 117868.9988
489.5 | 230037.9994 | 491.5 | 229937.9994 | 493.5 | 235837.9994 | 495.5 | 229737.9994 | 497.5 | 230937.9994 | 498.5 | 230437.9994 | 489.5 | 229737.9994
500.5 | 230037.9994 | 502.5 | 114918.9988 | 504.5 | 235837.9994 | 506.5 | 229737.9994 | 507.5 | 230937.9994 | 509.5 | 230238.0868 | 500.5 | 114918.9988
511.5 | 230037.9994 | 513.5 | 229937.9994 | 515.5 | 235837.9994 | 516.5 | 229737.9994 | 518.5 | 115418.9988 | 520.5 | 230437.9994 | 511.5 | 115418.9988
522.5 | 230037.9994 | 524.5 | 229937.9994 | 526 | 235837.9994 | 527.5 | 229737.9994 | 529.5 | 230937.9994 | 531.5 | 115168.9988 | 522.5 | 115168.9988
533.5 | 230037.9994 | 534.5 | 229937.9994 | 536.5 | 235837.9994 | 538.5 | 229737.9994 | 540.5 | 230937.9994 | 542 | 230437.9994 | 533.5 | 229737.9994
543.5 | 230037.9994 | 545.5 | 229937.9994 | 547.5 | 235837.9994 | 549.5 | 229737.9994 | 551.5 | 230937.9994 | 552.5 | 115168.9988 | 543.5 | 115168.9988
554.5 | 230037.9994 | 556.5 | 229937.9994 | 558.5 | 235837.9994 | 560.5 | 229737.9994 | 561.5 | 115418.9988 | 563.5 | 230437.9994 | 554.5 | 115418.9988
565.5 | 230037.9994 | 567.5 | 229937.9994 | 569.5 | 117868.9988 | 570.5 | 229737.9994 | 572.5 | 230937.9994 | 574.5 | 230437.9994 | 565.5 | 117868.9988
576.5 | 230037.9994 | 578.5 | 114918.9988 | 579.5 | 235837.9994 | 581.5 | 229737.9994 | 583.5 | 230937.9994 | 585.5 | 230437.9994 | 576.5 | 114918.9988
587.5 | 230037.9994 | 588.5 | 229937.9994 | 590.5 | 235837.9994 | 592.5 | 229737.9994 | 594.5 | 230937.9994 | 596 | 230437.9994 | 587.5 | 229737.9994
597.5 | 230037.9994 | 599.5 | 229937.9994 | 601.5 | 235837.9994 | 603.5 | 229737.9994 | 605 | 230937.9994 | 606.5 | 230437.9994 | 597.5 | 229737.9994
608.5 | 230037.9994 | 610.5 | 229937.9994 | 612.5 | 235837.9994 | 614.5 | 229737.9994 | 615.5 | 230937.9994 | 617.5 | 230437.9994 | 608.5 | 229737.9994
619.5 | 230037.9994 | 621.5 | 229937.9994 | 623.5 | 235837.9994 | 624.5 | 229737.9994 | 626.5 | 230937.9994 | 628.5 | 230437.9994 | 619.5 | 229737.9994
630.5 | 230037.9994 | 632.5 | 229937.9994 | 633.5 | 235837.9994 | 635.5 | 229737.9994 | 637.5 | 230937.9994 | 639.5 | 230437.9994 | 630.5 | 229737.9994
641.5 | 230037.9994 | 642.5 | 229937.9994 | 644.5 | 235837.9994 | 646.5 | 229737.9994 | 648.5 | 230937.9994 | 650.5 | 230437.9994 | 641.5 | 229737.9994
651.5 | 230037.9994 | 653.5 | 229937.9994 | 655.5 | 235837.9994 | 657.5 | 229737.9994 | 659.5 | 230937.9994 | 660.5 | 230437.9994 | 651.5 | 229737.9994
662.5 | 230037.9994 | 664.5 | 229937.9994 | 666.5 | 235837.9994 | 668.5 | 229737.9994 | 669.5 | 230937.9994 | 671.5 | 230437.9994 | 662.5 | 229737.9994
673.5 | 230037.9994 | 675.5 | 229937.9994 | 677.5 | 235837.9994 | 678.5 | 229737.9994 | 680.5 | 230937.9994 | 682.5 | 230437.9994 | 673.5 | 229737.9994
684.5 | 114968.9988 | 686.5 | 229937.9994 | 687.5 | 235837.9994 | 689.5 | 114818.9988 | 691.5 | 230937.9994 | 693.5 | 230437.9994 | 684.5 | 114818.9988
695 | 230037.9994 | 696.5 | 229937.9994 | 698.5 | 235837.9994 | 700.5 | 229737.9994 | 702.5 | 115418.9988 | 704 | 230437.9994 | 695 | 115418.9988
705.5 | 230037.9994 | 707.5 | 229937.9994 | 709.5 | 235837.9994 | 711.5 | 229737.9994 | 713 | 230937.9994 | 714.5 | 230437.9994 | 705.5 | 229737.9994
716.5 | 230037.9994 | 718.5 | 229937.9994 | 720.5 | 235837.9994 | 722 | 229737.9994 | 723.5 | 230937.9994 | 725.5 | 230437.9994 | 716.5 | 229737.9994
727.5 | 230037.9994 | 729.5 | 229937.9994 | 731.5 | 235837.9994 | 732.5 | 229737.9994 | 734.5 | 115418.9988 | 736.5 | 230437.9994 | 727.5 | 115418.9988
738.5 | 230037.9994 | 740.5 | 229937.9994 | 741.5 | 235837.9994 | 743.5 | 229737.9994 | 745.5 | 230937.9994 | 747.5 | 230437.9994 | 738.5 | 229737.9994
749.5 | 230037.9994 | 750.5 | 229937.9994 | 752.5 | 235837.9994 | 754.5 | 229737.9994 | 756.5 | 230937.9994 | 758 | 230437.9994 | 749.5 | 229737.9994
759.5 | 230037.9994 | 761.5 | 229937.9994 | 763.5 | 235837.9994 | 765.5 | 229737.9994 | 767 | 230937.9994 | 768.5 | 230437.9994 | 759.5 | 229737.9994
770.5 | 230037.9994 | 772.5 | 229937.9994 | 774.5 | 235837.9994 | 776 | 229737.9994 | 777.5 | 230937.9994 | 779.5 | 230437.9994 | 770.5 | 229737.9994
781.5 | 230037.9994 | 783.5 | 229937.9994 | 785.5 | 235837.9994 | 786.5 | 229737.9994 | 788.5 | 230937.9994 | 790.5 | 230437.9994 | 781.5 | 229737.9994
792.5 | 230037.9994 | 794.5 | 229937.9994 | 795.5 | 117868.9988 | 797.5 | 229737.9994 | 799.5 | 230937.9994 | 801.5 | 230437.9994 | 792.5 | 117868.9988
803.5 | 230037.9994 | 804.5 | 229937.9994 | 806.5 | 235837.9994 | 808.5 | 229737.9994 | 810.5 | 230937.9994 | 812.5 | 115168.9988 | 803.5 | 115168.9988
813.5 | 230037.9994 | 815.5 | 229937.9994 | 817.5 | 235837.9994 | 819.5 | 229737.9994 | 821 | 230937.9994 | 822.5 | 230437.9994 | 813.5 | 229737.9994
824.5 | 230037.9994 | 826.5 | 229937.9994 | 828.5 | 235837.9994 | 830 | 229737.9994 | 831.5 | 230937.9994 | 833.5 | 230437.9994 | 824.5 | 229737.9994
835.5 | 230037.9994 | 837.5 | 114918.9988 | 839 | 235837.9994 | 840.5 | 229737.9994 | 842.5 | 114420.4929 | 844.5 | 230437.9994 | 835.5 | 114420.4929
846.5 | 230037.9994 | 848 | 229937.9994 | 849.5 | 235837.9994 | 851.5 | 229737.9994 | 853.5 | 1583.6612 | 855.5 | 113568.3451 | 846.5 | 1583.6612
857 | 229638.2607 | 858.5 | 229937.9994 | 860.5 | 235837.9994 | 862.5 | 56039.0368 | 864.5 | 120.8404 | 866 | 17082.6328 | 857 | 120.8404
867.5 | 9393.8207 | 869.5 | 113921.5432 | 871.5 | 659.9687 | 873.5 | 15496.7291 | 875 | 50.6229 | 876.5 | 7927.7849 | 867.5 | 50.6229
878.5 | 2308.7706 | 880.5 | 112780.9395 | 882.5 | 2089.1738 | 884 | 5044.1207 | 885.5 | 785.1841 | 887.5 | 4082.823 | 878.5 | 785.1841
889.5 | 1952.9433 | 891.5 | 6150.8261 | 893 | 59.344 | 894.5 | 1659.659 | 896.5 | 173.494 | 898.5 | 1462.2069 | 889.5 | 59.344
900.5 | 2401.998 | 902 | 8440.7466 | 903.5 | 1195.7501 | 905.5 | 1156.7397 | 907.5 | 259.4389 | 909.5 | 626.7909 | 900.5 | 259.4389
911 | 883.4138 | 912.5 | 2295.6364 | 914.5 | 662.6912 | 916.5 | 756.6503 | 918.5 | 43.4134 | 920 | 573.8614 | 911 | 43.4134
921.5 | 483.9594 | 923.5 | 1947.0107 | 925.5 | 751.2127 | 927.5 | 523.723 | 929 | 523.4382 | 930.5 | 441.9134 | 921.5 | 441.9134
932.5 | 546.906 | 934.5 | 582.2928 | 936.5 | 39.5753 | 938 | 450.3386 | 939.5 | 26.3723 | 941.5 | 398.3112 | 932.5 | 26.3723
943.5 | 26.8527 | 945.5 | 903.8073 | 947 | 28.4816 | 948.5 | 148.8848 | 950.5 | 30.2601 | 952.5 | 76.486 | 943.5 | 26.8527
954.5 | 109.8371 | 956 | 18.9302 | 957.5 | 442.0446 | 959.5 | 24.3801 | 961.5 | 38.3762 | 963.5 | 25.5394 | 954.5 | 18.9302
965 | 467.436 | 966.5 | 219.6992 | 968.5 | 25.4655 | 970.5 | 50.772 | 972.5 | 7.6946 | 974 | 25.6914 | 965 | 7.6946
975.5 | 41.5865 | 977.5 | 4.6072 | 979.5 | 28.98 | 981.5 | 24.1157 | 983 | 3.2316 | 984.5 | 48.2978 | 975.5 | 3.2316
986.5 | 49.2495 | 988.5 | 0.71509 | 990.5 | 16.8098 | 992 | 38.6532 | 993.5 | 32.2743 | 995.5 | 24.9625 | 986.5 | 0.71509
997.5 | 30.4329 | 999.5 | 7.3711 | 1001 | 27.336 | 1002.5 | 17.6551 | 1004.5 | 2.4835 | 1006.5 | 45.4072 | 997.5 | 2.4835
1008.5 | 40.2758 | 1010 | 0.83258 | 1011.5 | 0.62584 | 1013.5 | 3.2687 | 1015.5 | 20.3303 | 1017.5 | 23.1884 | 1008.5 | 0.62584
1019 | 44.8279 | 1020.5 | 38.7909 | 1022.5 | 53.5211 | 1024.5 | 8.7989 | 1026.5 | 6.8659 | 1028 | 2.9889 | 1019 | 2.9889
1029.5 | 150.6349 | 1031.5 | 18.8554 | 1033.5 | 15.5656 | 1035.5 | 5.4651 | 1037 | 55.4582 | 1038.5 | 37.5752 | 1029.5 | 5.4651
1040.5 | 10.5847 | 1042.5 | 37.4888 | 1044.5 | 61.8526 | 1046 | 1.4604 | 1047.5 | 31.6301 | 1049.5 | 23.575 | 1040.5 | 1.4604
1051.5 | 12.402 | 1053.5 | 1.5809 | 1055 | 47.2767 | 1056.5 | 3.4538 | 1058.5 | 2.2612 | 1060.5 | 56.41 | 1051.5 | 1.5809
1062.5 | 40.0017 | 1064 | 34.2229 | 1065.5 | 26.262 | 1067.5 | 7.4296 | 1069.5 | 23.4333 | 1071.5 | 17.2913 | 1062.5 | 7.4296
1073 | 11.3558 | 1074.5 | 36.5725 | 1076.5 | 52.1232 | 1078.5 | 0.48139 | 1080.5 | 4.6828 | 1082 | 30.0401 | 1073 | 0.48139
1083.5 | 9.0137 | 1085.5 | 21.1209 | 1087.5 | 2.5054 | 1089.5 | 7.5069 | 1091 | 36.8699 | 1092.5 | 34.1517 | 1083.5 | 2.5054
1094.5 | 41.454 | 1096.5 | 4.2796 | 1098.5 | 1.2446 | 1100 | 16.382 | 1101.5 | 17.8931 | 1103.5 | 19.1346 | 1094.5 | 1.2446
1105.5 | 43.0636 | 1107.5 | 36.771 | 1109 | 3.8403 | 1110.5 | 19.1178 | 1112.5 | 3.2448 | 1114.5 | 46.4581 | 1105.5 | 3.2448
1116.5 | 7.2987 | 1118 | 29.9488 | 1119.5 | 59.2288 | 1121.5 | 1.4612 | 1123.5 | 6.5006 | 1125.5 | 7.7665 | 1116.5 | 1.4612
1127 | 28.3467 | 1128.5 | 20.5688 | 1130.5 | 20.2009 | 1132.5 | 20.7061 | 1134.5 | 48.1933 | 1135.5 | 10.1788 | 1127 | 10.1788
1137.5 | 0.01793 | 1139.5 | 9.5834 | 1141.5 | 42.1564 | 1143.5 | 18.3489 | 1144.5 | 1.7044 | 1147 | 31.6367 | 1137.5 | 0.01793
1148.5 | 7.7762 | 1150.5 | 30.5578 | 1152.5 | 28.2551 | 1154 | 32.1784 | 1155.5 | 6.5623 | 1157.5 | 32.5196 | 1148.5 | 6.5623
1159.5 | 29.1338 | 1161.5 | 8.5437 | 1163 | 18.7762 | 1164.5 | 27.4117 | 1166.5 | 34.2116 | 1168.5 | 2.4124 | 1159.5 | 2.4124
1170.5 | 16.7854 | 1172 | 8.3783 | 1173.5 | 27.7315 | 1175.5 | 83.9739 | 1177.5 | 34.4484 | 1179.5 | 8.4165 | 1170.5 | 8.3783
1180.5 | 12.8737 | 1182.5 | 39.135 | 1184.5 | 15.9786 | 1186.5 | 46.6383 | 1188.5 | 43.0671 | 1189.5 | 14.1014 | 1180.5 | 12.8737
1191.5 | 5.5221 | 1193.5 | 5.9187 | 1195.5 | 22.1351 | 1197.5 | 10.8081 | 1198.5 | 12.09 | 1200.5 | 4.6313 | 1191.5 | 4.6313
1202.5 | 56.7211 | 1204.5 | 1.0471 | 1206.5 | 22.6622 | 1208 | 27.2657 | 1209.5 | 32.4022 | 1211.5 | 11.2199 | 1202.5 | 1.0471
1213.5 | 16.7832 | 1215.5 | 0.034064 | 1217 | 39.8704 | 1218.5 | 3.1023 | 1220.5 | 39.599 | 1222.5 | 15.1869 | 1213.5 | 0.034064
1224.5 | 38.5293 | 1226 | 70.6372 | 1227.5 | 41.8529 | 1229.5 | 54.2731 | 1231.5 | 4.1993 | 1233.5 | 11.4058 | 1224.5 | 4.1993
1235 | 4.4724 | 1236.5 | 25.8465 | 1238.5 | 36.8474 | 1240.5 | 71.4658 | 1242.5 | 6.6767 | 1244 | 13.956 | 1235 | 4.4724
1245.5 | 19.5861 | 1247.5 | 27.0775 | 1249.5 | 63.3084 | 1251.5 | 28.9732 | 1253 | 3.2692 | 1254.5 | 2.1497 | 1245.5 | 2.1497
1256.5 | 35.7175 | 1258.5 | 16.9986 | 1260.5 | 22.0326 | 1262 | 2.0236 | 1263.5 | 27.7515 | 1265.5 | 30.2006 | 1256.5 | 2.0236
1267.5 | 45.2405 | 1269.5 | 5.9835 | 1270.5 | 71.436 | 1272.5 | 20.0688 | 1274.5 | 155.8959 | 1276.5 | 35.8653 | 1267.5 | 5.9835
1278.5 | 12.7391 | 1279.5 | 27.85 | 1281.5 | 2.2295 | 1283.5 | 54.4085 | 1285.5 | 19.8023 | 1287.5 | 7.3738 | 1278.5 | 2.2295
1288.5 | 0.48322 | 1290.5 | 41.0703 | 1292.5 | 47.1988 | 1294.5 | 3.9798 | 1296.5 | 8.4255 | 1298 | 1.5854 | 1288.5 | 0.48322
1299.5 | 7.8664 | 1301.5 | 15.259 | 1303.5 | 3.2425 | 1305.5 | 7.0288 | 1307 | 74.9457 | 1308.5 | 39.8227 | 1299.5 | 3.2425
1310.5 | 1.3709 | 1312.5 | 36.1955 | 1314.5 | 5.8935 | 1315.5 | 1.6586 | 1317.5 | 53.946 | 1319.5 | 2.8221 | 1310.5 | 1.3709
1321.5 | 0.71259 | 1323.5 | 1.0113 | 1324.5 | 69.0601 | 1327 | 120.309 | 1328.5 | 11.1801 | 1330.5 | 16.7109 | 1321.5 | 0.71259
1332.5 | 12.6319 | 1333.5 | 22.3654 | 1335.5 | 54.5427 | 1337.5 | 61.728 | 1339.5 | 7.5351 | 1341.5 | 3.2405 | 1332.5 | 3.2405
1342.5 | 18.5671 | 1344.5 | 44.3352 | 1346.5 | 31.3647 | 1348.5 | 6.1058 | 1350.5 | 8.7956 | 1351.5 | 33.6174 | 1342.5 | 6.1058
1353.5 | 77.9004 | 1355.5 | 15.4331 | 1357.5 | 29.9918 | 1359.5 | 52.8923 | 1360.5 | 40.7182 | 1362.5 | 1.5222 | 1353.5 | 1.5222
1364.5 | 39.2696 | 1366.5 | 3.0866 | 1368.5 | 5.4927 | 1370 | 7.2706 | 1371.5 | 29.1464 | 1373.5 | 18.8911 | 1364.5 | 3.0866
1375.5 | 7.5853 | 1377.5 | 64.9354 | 1379 | 53.7587 | 1380.5 | 4.4793 | 1382.5 | 1.1254 | 1384.5 | 9.7938 | 1375.5 | 1.1254
1386.5 | 9.3824 | 1388 | 62.3569 | 1389.5 | 18.8569 | 1391.5 | 46.0258 | 1393.5 | 18.8363 | 1395.5 | 2.5987 | 1386.5 | 2.5987
1397 | 38.3435 | 1398.5 | 27.548 | 1400.5 | 75.2466 | 1402.5 | 18.6879 | 1404.5 | 0.75151 | 1406 | 0.24231 | 1397 | 0.24231
1407.5 | 62.5545 | 1409.5 | 73.8162 | 1411.5 | 13.6793 | 1413.5 | 0.56873 | 1414.5 | 42.7326 | 1416.5 | 32.1417 | 1407.5 | 0.56873
1418.5 | 21.2522 | 1420.5 | 70.5005 | 1422.5 | 9.5024 | 1423.5 | 46.025 | 1425.5 | 1.4127 | 1427.5 | 1.8785 | 1418.5 | 1.4127
1429.5 | 5.2502 | 1431.5 | 16.224 | 1432.5 | 9.4741 | 1434.5 | 3.4486 | 1436.5 | 34.7955 | 1438.5 | 8.5731 | 1429.5 | 3.4486
1440.5 | 6.7831 | 1441.5 | 16.863 | 1443.5 | 23.78 | 1445.5 | 27.264 | 1447.5 | 50.7355 | 1449.5 | 11.6831 | 1440.5 | 6.7831
1450.5 | 0.72425 | 1452.5 | 0.10356 | 1454.5 | 36.5445 | 1456.5 | 33.6776 | 1458.5 | 42.1853 | 1459.5 | 15.363 | 1450.5 | 0.10356
1461.5 | 0.4508 | 1463.5 | 30.2152 | 1465.5 | 29.0532 | 1467.5 | 2.5787 | 1468.5 | 80.4147 | 1470.5 | 39.041 | 1461.5 | 0.4508
1472.5 | 1.3205 | 1474.5 | 6.3144 | 1476.5 | 0.86735 | 1477.5 | 25.2717 | 1479.5 | 17.4035 | 1481.5 | 32.5557 | 1472.5 | 0.86735
1483.5 | 7.3511 | 1485.5 | 4.4478 | 1487 | 37.4784 | 1488.5 | 5.3144 | 1490.5 | 24.2343 | 1492.5 | 33.9775 | 1483.5 | 4.4478
1494.5 | 54.3471 | 1496 | 5.8285 | 1497.5 | 8.0278 | 1499.5 | 43.8614 | 1501.5 | 6.8876 | 1503.5 | 7.592 | 1494.5 | 5.8285
1505 | 49.0198 | 1506.5 | 2.4478 | 1508.5 | 4.4325 | 1510.5 | 1.5036 | 1512.5 | 20.6623 | 1513.5 | 0.12421 | 1505 | 0.12421
1515.5 | 2.806 | 1517.5 | 4.5457 | 1519.5 | 101.7831 | 1521.5 | 60.4437 | 1522.5 | 5.0783 | 1524.5 | 38.4234 | 1515.5 | 2.806
1526.5 | 35.3484 | 1528.5 | 35.7187 | 1530.5 | 11.9992 | 1531.5 | 41.8621 | 1533.5 | 25.9442 | 1535.5 | 55.5452 | 1526.5 | 11.9992
1537.5 | 0.98013 | 1539.5 | 11.3213 | 1540.5 | 34.6349 | 1542.5 | 4.7483 | 1544.5 | 11.1104 | 1546.5 | 8.7421 | 1537.5 | 0.98013
1548.5 | 25.3633 | 1549.5 | 42.7865 | 1551.5 | 25.5113 | 1553.5 | 58.1373 | 1555.5 | 7.0052 | 1557.5 | 0.9273 | 1548.5 | 0.9273
1558.5 | 8.5456 | 1560.5 | 14.8353 | 1562.5 | 21.7618 | 1564.5 | 44.5092 | 1566.5 | 8.346 | 1567.5 | 16.6023 | 1558.5 | 8.346
1569.5 | 55.2294 | 1571.5 | 3.9383 | 1573.5 | 57.6321 | 1575.5 | 44.4721 | 1576.5 | 9.9477 | 1578.5 | 24.8965 | 1569.5 | 3.9383
1580.5 | 0.99778 | 1582.5 | 45.4804 | 1584.5 | 32.7702 | 1585.5 | 6.2992 | 1587.5 | 4.2126 | 1589.5 | 11.679 | 1580.5 | 0.99778
1591.5 | 8.1181 | 1593.5 | 19.5385 | 1594.5 | 15.3743 | 1596.5 | 31.0263 | 1598.5 | 30.9122 | 1600.5 | 4.9972 | 1591.5 | 4.9972
1602.5 | 0.32916 | 1603.5 | 18.1103 | 1605.5 | 5.6512 | 1607.5 | 0.083441 | 1609.5 | 32.8033 | 1611.5 | 5.1788 | 1602.5 | 0.083441
1612.5 | 4.0093 | 1614.5 | 6.7014 | 1616.5 | 26.347 | 1618.5 | 20.8403 | 1620.5 | 10.2763 | 1621.5 | 5.2309 | 1612.5 | 4.0093
1623.5 | 5.0831 | 1625.5 | 19.6364 | 1627.5 | 20.4005 | 1629.5 | 8.8613 | 1630.5 | 2.4596 | 1632.5 | 18.3674 | 1623.5 | 2.4596
1634.5 | 1.5486 | 1636.5 | 10.181 | 1638.5 | 36.9602 | 1639.5 | 8.5148 | 1641.5 | 21.1248 | 1643.5 | 3.6763 | 1634.5 | 1.5486
1645.5 | 2.0972 | 1647.5 | 1.9046 | 1648.5 | 10.9312 | 1650.5 | 3.6945 | 1653 | 14.3566 | 1654.5 | 17.1117 | 1645.5 | 1.9046
1656.5 | 13.7611 | 1657.5 | 10.8428 | 1659.5 | 0.85691 | 1661.5 | 3.7621 | 1663.5 | 2.9729 | 1665.5 | 20.3746 | 1656.5 | 0.85691
1666.5 | 3.2087 | 1668.5 | 2.9379 | 1670.5 | 14.3239 | 1672.5 | 30.3944 | 1674.5 | 40.0256 | 1675.5 | 2.7951 | 1666.5 | 2.7951
1677.5 | 2.0349 | 1679.5 | 3.241 | 1681.5 | 36.9488 | 1683.5 | 6.3588 | 1684.5 | 18.6507 | 1686.5 | 0.71925 | 1677.5 | 0.71925

## C3-4
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 140.7436 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38897.627 | 1 | 0 | 38897.627 | 2 | 0 | -41 | 9 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230438 | 115169 | 230437.9994
38897.6271 | 1 | 0 | 38897.6271 | 1 | 0 | -30.5 | 19.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6272 | 1 | 0 | 38897.6272 | 1 | 0 | -19.5 | 30.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6273 | 1 | 0 | 38897.6274 | 1 | 0 | -8.5 | 41.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6275 | 2 | 0 | 38897.6275 | 1 | 0 | 2.5 | 52.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6276 | 1 | 0 | 38897.6276 | 1 | 0 | 12.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6277 | 2 | 0 | 38897.6277 | 1 | 0 | 23.5 | 73.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6278 | 1 | 0 | 38897.6279 | 1 | 0 | 34.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.628 | 1 | 0 | 38897.628 | 1 | 0 | 45.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6281 | 1 | 0 | 38897.6281 | 1 | 0 | 56.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6282 | 1 | 0 | 38897.6282 | 1 | 0 | 66.5 | 116.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6283 | 2 | 0 | 38897.6284 | 2 | 0 | 77.5 | 127.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115169 | 115169 | 115168.9988
38897.6285 | 2 | 0 | 38897.6285 | 1 | 0 | 88.5 | 138.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6286 | 1 | 0 | 38897.6286 | 1 | 0 | 99.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6287 | 1 | 0 | 38897.6287 | 1 | 0 | 110.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6288 | 2 | 0 | 38897.6289 | 1 | 0 | 120.5 | 170.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.629 | 2 | 0 | 38897.629 | 1 | 0 | 131.5 | 181.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6291 | 2 | 0 | 38897.6291 | 1 | 0 | 142.5 | 192.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6292 | 1 | 0 | 38897.6292 | 1 | 0 | 153.5 | 203.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6294 | 1 | 0 | 38897.6294 | 1 | 0 | 164.5 | 214.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6295 | 1 | 0 | 38897.6295 | 1 | 0 | 175 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6296 | 1 | 0 |  | 1 | 0 | 185 | 235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6297 | 2 | 0 | 38897.6297 | 1 | 0 | 196.5 | 246.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6298 | 1 | 0 | 38897.6299 | 1 | 0 | 207.5 | 257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.63 | 1 | 0 | 38897.63 | 1 | 0 | 218.5 | 268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6301 | 2 | 0 | 38897.6301 | 1 | 0 | 228.5 | 278.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6302 | 1 | 0 | 38897.6302 | 2 | 0 | 239.5 | 289.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230438 | 115169 | 230437.9994
38897.6303 | 1 | 0 | 38897.6304 | 1 | 0 | 250.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6305 | 1 | 0 | 38897.6305 | 1 | 0 | 261.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6306 | 1 | 0 | 38897.6306 | 2 | 0 | 272.5 | 322.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230438 | 115169 | 230437.9994
38897.6307 | 1 | 0 | 38897.6307 | 1 | 0 | 282.5 | 332.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6308 | 1 | 0 | 38897.6309 | 1 | 0 | 293.5 | 343.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.631 | 1 | 0 | 38897.631 | 1 | 0 | 304.5 | 354.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6311 | 1 | 0 | 38897.6311 | 1 | 0 | 315.5 | 365.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6312 | 2 | 0 | 38897.6312 | 1 | 0 | 326.5 | 376.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.6313 | 1 | 0 | 38897.6314 | 1 | 0 | 336.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6315 | 1 | 0 | 38897.6315 | 1 | 0 | 347.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6316 | 1 | 0 | 38897.6316 | 1 | 0 | 358.5 | 408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6317 | 1 | 0 | 38897.6317 | 1 | 0 | 369.5 | 419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6319 | 1 | 0 | 38897.6319 | 2 | 0 | 380.5 | 430.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230438 | 115169 | 230437.9994
38897.632 | 1 | 0 | 38897.632 | 1 | 0 | 390.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6321 | 1 | 0 | 38897.6321 | 1 | 0 | 401.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6322 | 1 | 0 | 38897.6322 | 1 | 0 | 412.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6323 | 1 | 0 | 38897.6324 | 1 | 0 | 423.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6325 | 1 | 0 | 38897.6325 | 1 | 0 | 434.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6326 | 1 | 0 | 38897.6326 | 2 | 0 | 444.5 | 494.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230438 | 115169 | 230437.9994
38897.6327 | 1 | 0 | 38897.6327 | 1 | 0 | 455.5 | 505.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6328 | 1 | 0 | 38897.6329 | 1 | 0 | 466.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.633 | 1 | 0 | 38897.633 | 1 | 0 | 477.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6331 | 1 | 0 | 38897.6331 | 1 | 0 | 488.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6332 | 1 | 0 | 38897.6332 | 1 | 0 | 498.5 | 548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6333 | 1 | 1 | 38897.6334 | 1 | 0 | 509.5 | 559.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 531016718.44 | 230438 | 230238.0868
38897.6335 | 1 | 0 | 38897.6335 | 1 | 0 | 520.5 | 570.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6336 | 2 | 0 | 38897.6336 | 2 | 0 | 531.5 | 581.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115169 | 115169 | 115168.9988
38897.6337 | 1 | 0 | 38897.6337 | 1 | 0 | 542 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6338 | 2 | 0 | 38897.6339 | 1 | 0 | 552.5 | 602.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.634 | 1 | 0 | 38897.634 | 1 | 0 | 563.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6341 | 1 | 0 | 38897.6341 | 1 | 0 | 574.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6342 | 1 | 0 | 38897.6342 | 1 | 0 | 585.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6344 | 1 | 0 | 38897.6344 | 1 | 0 | 596 | 646 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6345 | 1 | 0 | 38897.6345 | 1 | 0 | 606.5 | 656.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6346 | 1 | 0 | 38897.6346 | 1 | 0 | 617.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6347 | 1 | 0 | 38897.6347 | 1 | 0 | 628.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6348 | 1 | 0 | 38897.6349 | 1 | 0 | 639.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.635 | 1 | 0 | 38897.635 | 1 | 0 | 650.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6351 | 1 | 0 | 38897.6351 | 1 | 0 | 660.5 | 710.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6352 | 1 | 0 | 38897.6352 | 1 | 0 | 671.5 | 721.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6353 | 1 | 0 | 38897.6354 | 1 | 0 | 682.5 | 732.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6355 | 1 | 0 | 38897.6355 | 1 | 0 | 693.5 | 743.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6356 | 1 | 0 | 38897.6356 | 1 | 0 | 704 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6357 | 1 | 0 | 38897.6357 | 1 | 0 | 714.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6358 | 1 | 0 | 38897.6359 | 1 | 0 | 725.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.636 | 1 | 0 | 38897.636 | 1 | 0 | 736.5 | 786.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6361 | 1 | 0 | 38897.6361 | 1 | 0 | 747.5 | 797.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6362 | 1 | 0 | 38897.6362 | 1 | 0 | 758 | 808 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6363 | 1 | 0 | 38897.6364 | 1 | 0 | 768.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6365 | 1 | 0 | 38897.6365 | 1 | 0 | 779.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6366 | 1 | 0 | 38897.6366 | 1 | 0 | 790.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6367 | 1 | 0 | 38897.6367 | 1 | 0 | 801.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6369 | 2 | 0 | 38897.6369 | 1 | 0 | 812.5 | 862.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115169 | 230438 | 115168.9988
38897.637 | 1 | 0 | 38897.637 | 1 | 0 | 822.5 | 872.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6371 | 1 | 0 | 38897.6371 | 1 | 0 | 833.5 | 883.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6372 | 1 | 0 | 38897.6372 | 1 | 0 | 844.5 | 894.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38897.6373 | 2 | 2 | 38897.6374 | 35 | 5 | 855.5 | 905.5 | 0.1221 | 0.1221 | 2.1368 | 0.30525 | 0.001221 | 0.001221 | 0.021368 | 0.0030525 | 0 | 0.018315 | 8715896.474 | 7567.9189 | 113568.3451
38897.6375 | 10 | 13 | 38897.6375 | 72 | 10 | 866 | 916 | 0.6105 | 0.79365 | 4.3956 | 0.6105 | 0.006105 | 0.0079365 | 0.043956 | 0.006105 | 0.0018315 | 0.037851 | 86973.2613 | 3602.894 | 17082.6328
38897.6376 | 29 | 27 | 38897.6376 | 143 | 33 | 876.5 | 926.5 | 1.7705 | 1.6484 | 8.7302 | 2.0147 | 0.017705 | 0.016484 | 0.087302 | 0.020147 | 0.001221 | 0.067155 | 363275.2358 | 1965.9624 | 7927.7849
38897.6377 | 66 | 50 | 38897.6377 | 213 | 61 | 887.5 | 937.5 | 4.0293 | 3.0525 | 13.0037 | 3.7241 | 0.040293 | 0.030525 | 0.13004 | 0.037241 | 0.009768 | 0.092796 | 18094.7888 | 1379.6256 | 4082.823
38897.6378 | 168 | 127 | 38897.6379 | 382 | 220 | 898.5 | 948.5 | 10.2564 | 7.7534 | 23.3211 | 13.431 | 0.10256 | 0.077534 | 0.23321 | 0.13431 | 0.025031 | 0.098901 | 7005.3759 | 1210.7424 | 1462.2069
38897.638 | 314 | 260 | 38897.638 | 357 | 231 | 909.5 | 959.5 | 19.1697 | 15.873 | 21.7949 | 14.1026 | 0.1917 | 0.15873 | 0.21795 | 0.14103 | 0.032967 | 0.076923 | 5272.2872 | 1602.0411 | 626.7909
38897.6381 | 329 | 271 | 38897.6381 | 469 | 287 | 920 | 970 | 20.0855 | 16.5446 | 28.6325 | 17.5214 | 0.20085 | 0.16545 | 0.28632 | 0.17521 | 0.035409 | 0.11111 | 6210.4029 | 1035.2877 | 573.8614
38897.6382 | 395 | 324 | 38897.6382 | 575 | 381 | 930.5 | 980.5 | 24.1148 | 19.7802 | 35.1038 | 23.2601 | 0.24115 | 0.1978 | 0.35104 | 0.2326 | 0.043346 | 0.11844 | 5303.6456 | 926.247 | 441.9134
38897.6383 | 407 | 357 | 38897.6384 | 696 | 555 | 941.5 | 991.5 | 24.8474 | 21.7949 | 42.4908 | 33.8828 | 0.24847 | 0.21795 | 0.42491 | 0.33883 | 0.030525 | 0.086081 | 9481.8791 | 1190.839 | 398.3112
38897.6385 | 903 | 762 | 38897.6385 | 1059 | 894 | 952.5 | 1002.5 | 55.1282 | 46.5201 | 64.652 | 54.5788 | 0.55128 | 0.4652 | 0.64652 | 0.54579 | 0.086081 | 0.10073 | 2132.9321 | 1012.6102 | 76.486
38897.6386 | 1104 | 945 | 38897.6386 | 949 | 798 | 963.5 | 1013.5 | 67.3993 | 57.6923 | 57.9365 | 48.7179 | 0.67399 | 0.57692 | 0.57937 | 0.48718 | 0.09707 | 0.092186 | 1199.705 | 1605.4941 | 25.5394
38897.6387 | 1106 | 939 | 38897.6387 | 1271 | 1028 | 974 | 1024 | 67.5214 | 57.326 | 77.5946 | 62.7595 | 0.67521 | 0.57326 | 0.77595 | 0.62759 | 0.10195 | 0.14835 | 496.6537 | 1260.5348 | 25.6914
38897.6388 | 995 | 851 | 38897.6389 | 1123 | 952 | 984.5 | 1034.5 | 60.7448 | 51.9536 | 68.5592 | 58.1197 | 0.60745 | 0.51954 | 0.68559 | 0.5812 | 0.087912 | 0.1044 | 2987.7272 | 849.7997 | 48.2978
38897.639 | 1105 | 931 | 38897.639 | 1263 | 1074 | 995.5 | 1045.5 | 67.4603 | 56.8376 | 77.1062 | 65.5678 | 0.6746 | 0.56838 | 0.77106 | 0.65568 | 0.10623 | 0.11538 | 4641.7827 | 628.4609 | 24.9625
38897.6391 | 992 | 881 | 38897.6391 | 1097 | 918 | 1006.5 | 1056.5 | 60.5617 | 53.7851 | 66.9719 | 56.044 | 0.60562 | 0.53785 | 0.66972 | 0.56044 | 0.067766 | 0.10928 | 3302.2617 | 1236.8755 | 45.4072
38897.6392 | 1129 | 937 | 38897.6392 | 1147 | 951 | 1017.5 | 1067.5 | 68.9255 | 57.2039 | 70.0244 | 58.0586 | 0.68926 | 0.57204 | 0.70024 | 0.58059 | 0.11722 | 0.11966 | 1216.8345 | 982.9575 | 23.1884
38897.6394 | 1282 | 1056 | 38897.6394 | 1032 | 834 | 1028 | 1078 | 78.2662 | 64.4689 | 63.0037 | 50.9158 | 0.78266 | 0.64469 | 0.63004 | 0.50916 | 0.13797 | 0.12088 | 536.8103 | 2986.5002 | 2.9889
38897.6395 | 1078 | 844 | 38897.6395 | 1235 | 966 | 1038.5 | 1088.5 | 65.812 | 51.5263 | 75.3968 | 58.9744 | 0.65812 | 0.51526 | 0.75397 | 0.58974 | 0.14286 | 0.16422 | 2127.1741 | 478.7295 | 37.5752
38897.6396 | 1189 | 857 | 38897.6396 | 1379 | 1004 | 1049.5 | 1099.5 | 72.5885 | 52.3199 | 84.188 | 61.2943 | 0.72589 | 0.5232 | 0.84188 | 0.61294 | 0.20269 | 0.22894 | 1257.6255 | 352.3398 | 23.575
38897.6397 | 1116 | 734 | 38897.6397 | 1256 | 914 | 1060.5 | 1110.5 | 68.1319 | 44.8107 | 76.6789 | 55.7998 | 0.68132 | 0.44811 | 0.76679 | 0.558 | 0.23321 | 0.20879 | 385.2471 | 1001.798 | 56.41
38897.6398 | 1340 | 809 | 38897.6399 | 1348 | 886 | 1071.5 | 1121.5 | 81.8071 | 49.3895 | 82.2955 | 54.0904 | 0.81807 | 0.49389 | 0.82295 | 0.5409 | 0.32418 | 0.28205 | 154.1195 | 848.1512 | 17.2913
38897.64 | 1245 | 756 | 38897.64 | 1219 | 697 | 1082 | 1132 | 76.0073 | 46.1538 | 74.42 | 42.5519 | 0.76007 | 0.46154 | 0.7442 | 0.42552 | 0.29853 | 0.31868 | 457.546 | 293.8818 | 30.0401
38897.6401 | 1249 | 686 | 38897.6401 | 1509 | 787 | 1092.5 | 1142.5 | 76.2515 | 41.8803 | 92.1245 | 48.0464 | 0.76252 | 0.4188 | 0.92125 | 0.48046 | 0.34371 | 0.44078 | 642.2278 | 172.1398 | 34.1517
38897.6402 | 1423 | 695 | 38897.6402 | 1567 | 648 | 1103.5 | 1153.5 | 86.8742 | 42.4298 | 95.6654 | 39.5604 | 0.86874 | 0.4243 | 0.95665 | 0.3956 | 0.44444 | 0.56105 | 198.8563 | 244.4836 | 19.1346
38897.6403 | 1549 | 419 | 38897.6404 | 1645 | 556 | 1114.5 | 1164.5 | 94.5665 | 25.58 | 100.4274 | 33.9438 | 0.94567 | 0.2558 | 1.0043 | 0.33944 | 0.68987 | 0.66484 | 91.9279 | 136.392 | 46.4581
38897.6405 | 1930 | 415 | 38897.6405 | 1601 | 301 | 1125.5 | 1175.5 | 117.8266 | 25.3358 | 97.7411 | 18.3761 | 1.1783 | 0.25336 | 0.97741 | 0.18376 | 0.92491 | 0.79365 | 26.4378 | 436.2087 | 7.7665
38897.6406 | 2024 | 234 | 38897.6406 | 1771 | 190 | 1135.5 | 1185.5 | 123.5653 | 14.2857 | 108.1197 | 11.5995 | 1.2357 | 0.14286 | 1.0812 | 0.116 | 1.0928 | 0.9652 | 18.0543 | 101.0902 | 10.1788
| 1713 | 384 | 38897.6407 | 1962 | 217 | 1147 | 1197 | 104.5788 | 23.4432 | 119.7802 | 13.2479 | 1.0458 | 0.23443 | 1.1978 | 0.13248 | 0.81136 | 1.0653 | 56.1852 | 139.8067 | 31.6367
38897.6408 | 1401 | 534 | 38897.6409 | 1699 | 587 | 1157.5 | 1207.5 | 85.5311 | 32.6007 | 103.7241 | 35.8364 | 0.85531 | 0.32601 | 1.0372 | 0.35836 | 0.5293 | 0.67888 | 345.1115 | 88.2724 | 32.5196
38897.641 | 2034 | 337 | 38897.641 | 1906 | 295 | 1168.5 | 1218.5 | 124.1758 | 20.5739 | 116.3614 | 18.0098 | 1.2418 | 0.20574 | 1.1636 | 0.1801 | 1.036 | 0.98352 | 6.6514 | 14.1414 | 2.4124
38897.6411 | 1874 | 511 | 38897.6411 | 1615 | 326 | 1179.5 | 1229.5 | 114.4078 | 31.1966 | 98.5958 | 19.9023 | 1.1441 | 0.31197 | 0.98596 | 0.19902 | 0.83211 | 0.78694 | 46.4846 | 117.4731 | 8.4165
38897.6412 | 1949 | 274 | 38897.6412 | 1804 | 256 | 1189.5 | 1239.5 | 118.9866 | 16.7277 | 110.1343 | 15.6288 | 1.1899 | 0.16728 | 1.1013 | 0.15629 | 1.0226 | 0.94505 | 26.1122 | 88.331 | 14.1014
38897.6413 | 2018 | 327 | 38897.6414 | 2049 | 324 | 1200.5 | 1250.5 | 123.199 | 19.9634 | 125.0916 | 19.7802 | 1.232 | 0.19963 | 1.2509 | 0.1978 | 1.0324 | 1.0531 | 24.7207 | 61.8741 | 4.6313
38897.6415 | 1920 | 322 | 38897.6415 | 1882 | 346 | 1211.5 | 1261.5 | 117.2161 | 19.6581 | 114.8962 | 21.1233 | 1.1722 | 0.19658 | 1.149 | 0.21123 | 0.97558 | 0.93773 | 28.439 | 132.5715 | 11.2199
38897.6416 | 1954 | 262 | 38897.6416 | 1986 | 325 | 1222.5 | 1272.5 | 119.2918 | 15.9951 | 121.2454 | 19.8413 | 1.1929 | 0.15995 | 1.2125 | 0.19841 | 1.033 | 1.014 | 25.7333 | 80.2371 | 15.1869
38897.6417 | 1871 | 333 | 38897.6417 | 1763 | 263 | 1233.5 | 1283.5 | 114.2247 | 20.3297 | 107.6313 | 16.0562 | 1.1422 | 0.2033 | 1.0763 | 0.16056 | 0.93895 | 0.91575 | 44.2273 | 59.9087 | 11.4058
38897.6419 | 1936 | 295 | 38897.6419 | 1688 | 248 | 1244 | 1294 | 118.1929 | 18.0098 | 103.0525 | 15.1404 | 1.1819 | 0.1801 | 1.0305 | 0.1514 | 1.0018 | 0.87912 | 26.3271 | 123.9706 | 13.956
38897.642 | 2266 | 113 | 38897.642 | 1898 | 99 | 1254.5 | 1304.5 | 138.3394 | 6.8987 | 115.873 | 6.044 | 1.3834 | 0.068987 | 1.1587 | 0.06044 | 1.3144 | 1.0983 | 0.72063 | 3.4122 | 2.1497
38897.6421 | 1936 | 81 | 38897.6421 | 2152 | 136 | 1265.5 | 1315.5 | 118.1929 | 4.9451 | 131.3797 | 8.3028 | 1.1819 | 0.049451 | 1.3138 | 0.083028 | 1.1325 | 1.2308 | 37.6489 | 9.269 | 30.2006
38897.6422 | 1750 | 290 | 38897.6422 | 1720 | 288 | 1276.5 | 1326.5 | 106.8376 | 17.7045 | 105.0061 | 17.5824 | 1.0684 | 0.17705 | 1.0501 | 0.17582 | 0.89133 | 0.87424 | 54.9846 | 64.4538 | 35.8653
38897.6423 | 1809 | 313 | 38897.6424 | 2040 | 366 | 1287.5 | 1337.5 | 110.4396 | 19.1087 | 124.5421 | 22.3443 | 1.1044 | 0.19109 | 1.2454 | 0.22344 | 0.91331 | 1.022 | 13.5257 | 14.398 | 7.3738
38897.6425 | 2051 | 248 | 38897.6425 | 1862 | 212 | 1298 | 1348 | 125.2137 | 15.1404 | 113.6752 | 12.9426 | 1.2521 | 0.1514 | 1.1368 | 0.12943 | 1.1007 | 1.0073 | 15.4302 | 160.6012 | 1.5854
38897.6426 | 2160 | 54 | 38897.6426 | 1988 | 67 | 1308.5 | 1358.5 | 131.8681 | 3.2967 | 121.3675 | 4.0904 | 1.3187 | 0.032967 | 1.2137 | 0.040904 | 1.2857 | 1.1728 | 7.5306 | 30.775 | 39.8227
38897.6427 | 1920 | 337 | 38897.6427 | 1955 | 341 | 1319.5 | 1369.5 | 117.2161 | 20.5739 | 119.3529 | 20.8181 | 1.1722 | 0.20574 | 1.1935 | 0.20818 | 0.96642 | 0.98535 | 187.3794 | 24.4676 | 2.8221
38897.6428 | 1674 | 450 | 38897.6429 | 1654 | 380 | 1330.5 | 1380.5 | 102.1978 | 27.4725 | 100.9768 | 23.199 | 1.022 | 0.27473 | 1.0098 | 0.23199 | 0.74725 | 0.77778 | 107.2678 | 70.8217 | 16.7109
38897.643 | 2042 | 255 | 38897.643 | 1649 | 211 | 1341.5 | 1391.5 | 124.6642 | 15.5678 | 100.6716 | 12.8816 | 1.2466 | 0.15568 | 1.0067 | 0.12882 | 1.091 | 0.8779 | 14.7685 | 7073.1576 | 3.2405
38897.6431 | 1919 | 208 | 38897.6431 | 1787 | 214 | 1351.5 | 1401.5 | 117.1551 | 12.6984 | 109.0965 | 13.0647 | 1.1716 | 0.12698 | 1.091 | 0.13065 | 1.0446 | 0.96032 | 27.8295 | 64.4725 | 33.6174
38897.6432 | 2067 | 267 | 38897.6432 | 1997 | 252 | 1362.5 | 1412.5 | 126.1905 | 16.3004 | 121.917 | 15.3846 | 1.2619 | 0.163 | 1.2192 | 0.15385 | 1.0989 | 1.0653 | 6.9841 | 16.551 | 1.5222
38897.6433 | 1856 | 231 | 38897.6434 | 2087 | 199 | 1373.5 | 1423.5 | 113.3089 | 14.1026 | 127.4115 | 12.149 | 1.1331 | 0.14103 | 1.2741 | 0.12149 | 0.99206 | 1.1526 | 64.1968 | 24.9731 | 18.8911
38897.6435 | 1900 | 95 | 38897.6435 | 2259 | 91 | 1384.5 | 1434.5 | 115.9951 | 5.7998 | 137.9121 | 5.5556 | 1.16 | 0.057998 | 1.3791 | 0.055556 | 1.102 | 1.3236 | 8.3084 | 3.0903 | 9.7938
38897.6436 | 1974 | 96 | 38897.6436 | 2288 | 116 | 1395.5 | 1445.5 | 120.5128 | 5.8608 | 139.6825 | 7.0818 | 1.2051 | 0.058608 | 1.3968 | 0.070818 | 1.1465 | 1.326 | 3.0571 | 1.0712 | 2.5987
38897.6437 | 2188 | 118 | 38897.6437 | 2289 | 130 | 1406 | 1456 | 133.5775 | 7.2039 | 139.7436 | 7.9365 | 1.3358 | 0.072039 | 1.3974 | 0.079365 | 1.2637 | 1.3181 | 6.0752 | 85.5883 | 0.24231
38897.6438 | 1979 | 112 | 38897.6439 | 2027 | 129 | 1416.5 | 1466.5 | 120.8181 | 6.8376 | 123.7485 | 7.8755 | 1.2082 | 0.068376 | 1.2375 | 0.078755 | 1.1398 | 1.1587 | 24.8762 | 20.1808 | 32.1417
38897.644 | 2102 | 191 | 38897.644 | 2214 | 192 | 1427.5 | 1477.5 | 128.3272 | 11.6606 | 135.1648 | 11.7216 | 1.2833 | 0.11661 | 1.3516 | 0.11722 | 1.1667 | 1.2344 | 8.5488 | 40.8082 | 1.8785
38897.6441 | 2163 | 184 | 38897.6441 | 1785 | 155 | 1438.5 | 1488.5 | 132.0513 | 11.2332 | 108.9744 | 9.4628 | 1.3205 | 0.11233 | 1.0897 | 0.094628 | 1.2082 | 0.99512 | 6.2435 | 61.0344 | 8.5731
38897.6442 | 1784 | 414 | 38897.6442 | 1649 | 319 | 1449.5 | 1499.5 | 108.9133 | 25.2747 | 100.6716 | 19.475 | 1.0891 | 0.25275 | 1.0067 | 0.19475 | 0.83639 | 0.81197 | 60.2826 | 81.9629 | 11.6831
38897.6443 | 2089 | 157 | 38897.6444 | 1794 | 118 | 1459.5 | 1509.5 | 127.5336 | 9.5849 | 109.5238 | 7.2039 | 1.2753 | 0.095849 | 1.0952 | 0.072039 | 1.1795 | 1.0232 | 12.7096 | 68.4055 | 15.363
38897.6445 | 1824 | 140 | 38897.6445 | 2001 | 136 | 1470.5 | 1520.5 | 111.3553 | 8.547 | 122.1612 | 8.3028 | 1.1136 | 0.08547 | 1.2216 | 0.083028 | 1.0281 | 1.1386 | 50.6937 | 19.0628 | 39.041
38897.6446 | 1742 | 152 | 38897.6446 | 2075 | 211 | 1481.5 | 1531.5 | 106.3492 | 9.2796 | 126.6789 | 12.8816 | 1.0635 | 0.092796 | 1.2668 | 0.12882 | 0.9707 | 1.138 | 117.7681 | 13.6737 | 32.5557
38897.6447 | 1850 | 162 | 38897.6447 | 1978 | 177 | 1492.5 | 1542.5 | 112.9426 | 9.8901 | 120.757 | 10.8059 | 1.1294 | 0.098901 | 1.2076 | 0.10806 | 1.0305 | 1.0995 | 46.159 | 23.0949 | 33.9775
38897.6448 | 2018 | 108 | 38897.6449 | 2234 | 132 | 1503.5 | 1553.5 | 123.199 | 6.5934 | 136.3858 | 8.0586 | 1.232 | 0.065934 | 1.3639 | 0.080586 | 1.1661 | 1.2833 | 6.9003 | 4.7899 | 7.592
38897.645 | 2041 | 271 | 38897.645 | 2120 | 208 | 1513.5 | 1563.5 | 124.6032 | 16.5446 | 129.4261 | 12.6984 | 1.246 | 0.16545 | 1.2943 | 0.12698 | 1.0806 | 1.1673 | 3.8716 | 5.3572 | 0.12421
38897.6451 | 1682 | 193 | 38897.6451 | 1974 | 201 | 1524.5 | 1574.5 | 102.6862 | 11.7827 | 120.5128 | 12.2711 | 1.0269 | 0.11783 | 1.2051 | 0.12271 | 0.90904 | 1.0824 | 110.9411 | 20.8176 | 38.4234
38897.6452 | 1714 | 162 | 38897.6452 | 1939 | 215 | 1535.5 | 1585.5 | 104.6398 | 9.8901 | 118.3761 | 13.1258 | 1.0464 | 0.098901 | 1.1838 | 0.13126 | 0.9475 | 1.0525 | 62.8478 | 26.5127 | 55.5452
38897.6453 | 1964 | 190 | 38897.6454 | 2112 | 219 | 1546.5 | 1596.5 | 119.9023 | 11.5995 | 128.9377 | 13.37 | 1.199 | 0.116 | 1.2894 | 0.1337 | 1.083 | 1.1557 | 146.9017 | 12.3248 | 8.7421
38897.6455 | 1962 | 196 | 38897.6455 | 2187 | 225 | 1557.5 | 1607.5 | 119.7802 | 11.9658 | 133.5165 | 13.7363 | 1.1978 | 0.11966 | 1.3352 | 0.13736 | 1.0781 | 1.1978 | 1.9663 | 1.2486 | 0.9273
38897.6456 | 1840 | 205 | 38897.6456 | 2056 | 251 | 1567.5 | 1617.5 | 112.3321 | 12.5153 | 125.5189 | 15.3236 | 1.1233 | 0.12515 | 1.2552 | 0.15324 | 0.99817 | 1.102 | 171.3053 | 15.0367 | 16.6023
38897.6457 | 1902 | 299 | 38897.6457 | 1715 | 316 | 1578.5 | 1628.5 | 116.1172 | 18.254 | 104.7009 | 19.2918 | 1.1612 | 0.18254 | 1.047 | 0.19292 | 0.97863 | 0.85409 | 27.205 | 248.6361 | 24.8965
38897.6458 | 1844 | 549 | 38897.6459 | 1506 | 424 | 1589.5 | 1639.5 | 112.5763 | 33.5165 | 91.9414 | 25.8852 | 1.1258 | 0.33516 | 0.91941 | 0.25885 | 0.7906 | 0.66056 | 30.836 | 272.8104 | 11.679
38897.646 | 1710 | 503 | 38897.646 | 1858 | 452 | 1600.5 | 1650.5 | 104.3956 | 30.7082 | 113.431 | 27.5946 | 1.044 | 0.30708 | 1.1343 | 0.27595 | 0.73687 | 0.85836 | 23.3242 | 37.3803 | 4.9972
38897.6461 | 1773 | 606 | 38897.6461 | 1486 | 548 | 1611.5 | 1661.5 | 108.2418 | 36.9963 | 90.7204 | 33.4554 | 1.0824 | 0.36996 | 0.9072 | 0.33455 | 0.71245 | 0.57265 | 26.8532 | 74.3049 | 5.1788
38897.6462 | 1686 | 670 | 38897.6462 | 1418 | 474 | 1621.5 | 1671.5 | 102.9304 | 40.9035 | 86.569 | 28.9377 | 1.0293 | 0.40904 | 0.86569 | 0.28938 | 0.62027 | 0.57631 | 86.2308 | 225.0449 | 5.2309
38897.6463 | 1411 | 687 | 38897.6464 | 1394 | 614 | 1632.5 | 1682.5 | 86.1416 | 41.9414 | 85.1038 | 37.4847 | 0.86142 | 0.41941 | 0.85104 | 0.37485 | 0.442 | 0.47619 | 317.2325 | 155.406 | 18.3674
38897.6465 | 1589 | 783 | 38897.6465 | 1606 | 709 | 1643.5 | 1693.5 | 97.0085 | 47.8022 | 98.0464 | 43.2845 | 0.97009 | 0.47802 | 0.98046 | 0.43284 | 0.49206 | 0.54762 | 39.0371 | 76.0838 | 3.6763
38897.6466 | 1667 | 786 | 38897.6466 | 1428 | 594 | 1654.5 | 1704.5 | 101.7705 | 47.9853 | 87.1795 | 36.2637 | 1.0177 | 0.47985 | 0.87179 | 0.36264 | 0.53785 | 0.50916 | 79.3696 | 1024.9441 | 17.1117
38897.6467 | 1450 | 699 | 38897.6467 | 1555 | 824 | 1665.5 | 1715.5 | 88.5226 | 42.674 | 94.9328 | 50.3053 | 0.88523 | 0.42674 | 0.94933 | 0.50305 | 0.45849 | 0.44628 | 125.3349 | 1020.0695 | 20.3746
38897.6468 | 1557 | 778 | 38897.6469 | 1530 | 769 | 1675.5 | 1725.5 | 95.0549 | 47.4969 | 93.4066 | 46.9475 | 0.95055 | 0.47497 | 0.93407 | 0.46947 | 0.47558 | 0.46459 | 150.4897 | 276.1768 | 2.7951
38897.647 | 1292 | 712 | 38897.647 | 1712 | 835 | 1686.5 | 1736.5 | 78.8767 | 43.4676 | 104.5177 | 50.9768 | 0.78877 | 0.43468 | 1.0452 | 0.50977 | 0.35409 | 0.53541 | 2.4261 | 1.7286 | 0.71925

## C2-4
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 141.0488 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38897.627 | 1 | 0 | 38897.627 | 1 | 0 | -42.5 | 7.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6271 | 1 | 0 | 38897.6271 | 1 | 0 | -32.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6272 | 1 | 0 | 38897.6272 | 1 | 0 | -21.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6273 | 1 | 0 | 38897.6273 | 1 | 0 | -10.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6275 | 1 | 0 | 38897.6275 | 1 | 0 | 0.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6276 | 1 | 0 | 38897.6276 | 1 | 0 | 11.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6277 | 1 | 0 | 38897.6277 | 1 | 0 | 21.5 | 71.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6278 | 1 | 0 | 38897.6278 | 1 | 0 | 32.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.628 | 1 | 0 | 38897.628 | 1 | 0 | 43.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6281 | 1 | 0 | 38897.6281 | 1 | 0 | 54.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6282 | 1 | 0 | 38897.6282 | 1 | 0 | 65.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6283 | 1 | 0 | 38897.6283 | 1 | 0 | 76 | 126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6284 | 2 | 0 | 38897.6285 | 1 | 0 | 86.5 | 136.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6286 | 2 | 0 | 38897.6286 | 1 | 0 | 97.5 | 147.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6287 | 1 | 0 | 38897.6287 | 1 | 0 | 108.5 | 158.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6288 | 1 | 0 | 38897.6288 | 1 | 0 | 119.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6289 | 2 | 0 | 38897.629 | 1 | 0 | 129.5 | 179.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6291 | 1 | 0 | 38897.6291 | 1 | 0 | 140.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6292 | 2 | 0 | 38897.6292 | 1 | 0 | 151.5 | 201.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6293 | 1 | 0 | 38897.6293 | 2 | 0 | 162.5 | 212.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230938 | 115419 | 230937.9994
38897.6295 | 1 | 0 | 38897.6295 | 1 | 0 | 173.5 | 223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6296 | 1 | 0 | 38897.6296 | 1 | 0 | 183.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6297 | 2 | 0 | 38897.6297 | 1 | 0 | 194.5 | 244.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6298 | 2 | 0 | 38897.6298 | 1 | 0 | 205.5 | 255.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.63 | 2 | 0 | 38897.63 | 2 | 0 | 216.5 | 266.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115419 | 115419 | 115418.9988
38897.6301 | 1 | 0 | 38897.6301 | 1 | 0 | 227.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6302 | 1 | 0 | 38897.6302 | 1 | 0 | 238 | 288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6303 | 1 | 0 | 38897.6303 | 1 | 0 | 248.5 | 298.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6305 | 1 | 0 | 38897.6305 | 1 | 0 | 259.5 | 309.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6306 | 1 | 0 | 38897.6306 | 1 | 0 | 270.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6307 | 1 | 0 | 38897.6307 | 1 | 0 | 281.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6308 | 2 | 0 | 38897.6308 | 1 | 0 | 291.5 | 341.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6309 | 2 | 0 | 38897.631 | 1 | 0 | 302.5 | 352.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6311 | 1 | 0 | 38897.6311 | 1 | 0 | 313.5 | 363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6312 | 1 | 0 | 38897.6312 | 2 | 0 | 324.5 | 374.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230938 | 115419 | 230937.9994
38897.6313 | 1 | 0 | 38897.6313 | 1 | 0 | 335.5 | 385.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6314 | 1 | 0 | 38897.6315 | 1 | 0 | 345.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6316 | 1 | 0 | 38897.6316 | 2 | 0 | 356.5 | 406.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230938 | 115419 | 230937.9994
38897.6317 | 1 | 0 | 38897.6317 | 1 | 0 | 367.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6318 | 1 | 0 | 38897.6318 | 1 | 0 | 378.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.632 | 1 | 0 | 38897.632 | 1 | 0 | 389.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6321 | 1 | 0 | 38897.6321 | 1 | 0 | 399.5 | 449.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6322 | 1 | 0 | 38897.6322 | 1 | 0 | 410.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6323 | 1 | 0 | 38897.6323 | 1 | 0 | 421.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6325 | 1 | 0 | 38897.6325 | 1 | 0 | 432.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6326 | 1 | 0 | 38897.6326 | 1 | 0 | 443.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6327 | 1 | 0 | 38897.6327 | 1 | 0 | 453.5 | 503.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6328 | 1 | 0 | 38897.6328 | 1 | 0 | 464.5 | 514.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.633 | 1 | 0 | 38897.633 | 1 | 0 | 475.5 | 525.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6331 | 1 | 0 | 38897.6331 | 1 | 0 | 486.5 | 536.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6332 | 1 | 0 | 38897.6332 | 1 | 0 | 497.5 | 547.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6333 | 1 | 0 | 38897.6333 | 1 | 0 | 507.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6334 | 2 | 0 | 38897.6335 | 1 | 0 | 518.5 | 568.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6336 | 1 | 0 | 38897.6336 | 1 | 0 | 529.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6337 | 1 | 0 | 38897.6337 | 1 | 0 | 540.5 | 590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6338 | 1 | 0 | 38897.6338 | 2 | 0 | 551.5 | 601.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230938 | 115419 | 230937.9994
38897.6339 | 2 | 0 | 38897.634 | 1 | 0 | 561.5 | 611.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6341 | 1 | 0 | 38897.6341 | 1 | 0 | 572.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6342 | 1 | 0 | 38897.6342 | 1 | 0 | 583.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6343 | 1 | 0 | 38897.6343 | 1 | 0 | 594.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6345 | 1 | 0 | 38897.6345 | 1 | 0 | 605 | 655 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6346 | 1 | 0 | 38897.6346 | 1 | 0 | 615.5 | 665.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6347 | 1 | 0 | 38897.6347 | 1 | 0 | 626.5 | 676.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6348 | 1 | 0 | 38897.6348 | 1 | 0 | 637.5 | 687.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.635 | 1 | 0 | 38897.635 | 1 | 0 | 648.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6351 | 1 | 0 | 38897.6351 | 1 | 0 | 659.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6352 | 1 | 0 | 38897.6352 | 1 | 0 | 669.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6353 | 1 | 0 | 38897.6353 | 1 | 0 | 680.5 | 730.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6355 | 1 | 0 | 38897.6355 | 1 | 0 | 691.5 | 741.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6356 | 2 | 0 | 38897.6356 | 2 | 0 | 702.5 | 752.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 115419 | 115419 | 115418.9988
38897.6357 | 1 | 0 | 38897.6357 | 1 | 0 | 713 | 763 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6358 | 1 | 0 | 38897.6358 | 1 | 0 | 723.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6359 | 2 | 0 | 38897.636 | 1 | 0 | 734.5 | 784.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115419 | 230938 | 115418.9988
38897.6361 | 1 | 0 | 38897.6361 | 1 | 0 | 745.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6362 | 1 | 0 | 38897.6362 | 1 | 0 | 756.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6363 | 1 | 0 | 38897.6363 | 1 | 0 | 767 | 817 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6364 | 1 | 0 | 38897.6365 | 1 | 0 | 777.5 | 827.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6366 | 1 | 0 | 38897.6366 | 1 | 0 | 788.5 | 838.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6367 | 1 | 0 | 38897.6367 | 1 | 0 | 799.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6368 | 1 | 0 | 38897.6368 | 1 | 0 | 810.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.637 | 1 | 0 | 38897.637 | 1 | 0 | 821 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6371 | 1 | 0 | 38897.6371 | 1 | 0 | 831.5 | 881.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230938 | 230938 | 230937.9994
38897.6372 | 5 | 2 | 38897.6372 | 18 | 3 | 842.5 | 892.5 | 0.30525 | 0.1221 | 1.0989 | 0.18315 | 0.0030525 | 0.001221 | 0.010989 | 0.0018315 | 0.0018315 | 0.0091575 | 77182.6048 | 15286.4945 | 114420.4929
38897.6373 | 146 | 125 | 38897.6373 | 600 | 544 | 853.5 | 903.5 | 8.9133 | 7.6313 | 36.63 | 33.2112 | 0.089133 | 0.076313 | 0.3663 | 0.33211 | 0.012821 | 0.034188 | 12566.2728 | 3310.1384 | 1583.6612
38897.6375 | 771 | 695 | 38897.6375 | 380 | 353 | 864.5 | 914.5 | 47.0696 | 42.4298 | 23.199 | 21.5507 | 0.4707 | 0.4243 | 0.23199 | 0.21551 | 0.046398 | 0.016484 | 2130.8197 | 18501.5627 | 120.8404
38897.6376 | 965 | 870 | 38897.6376 | 1067 | 1039 | 875 | 925 | 58.9133 | 53.1136 | 65.1404 | 63.431 | 0.58913 | 0.53114 | 0.6514 | 0.63431 | 0.057998 | 0.017094 | 820.0507 | 1259.7635 | 50.6229
38897.6377 | 282 | 229 | 38897.6377 | 710 | 693 | 885.5 | 935.5 | 17.2161 | 13.9805 | 43.3455 | 42.3077 | 0.17216 | 0.1398 | 0.43346 | 0.42308 | 0.032357 | 0.010379 | 3815.1376 | 137432.7537 | 785.1841
38897.6378 | 629 | 594 | 38897.6378 | 578 | 470 | 896.5 | 946.5 | 38.4005 | 36.2637 | 35.2869 | 28.6935 | 0.384 | 0.36264 | 0.35287 | 0.28694 | 0.021368 | 0.065934 | 74846.0819 | 1813.5439 | 173.494
38897.638 | 540 | 462 | 38897.638 | 820 | 670 | 907.5 | 957.5 | 32.967 | 28.2051 | 50.0611 | 40.9035 | 0.32967 | 0.28205 | 0.50061 | 0.40904 | 0.047619 | 0.091575 | 4960.6322 | 1091.9042 | 259.4389
38897.6381 | 1115 | 807 | 38897.6381 | 1034 | 881 | 918.5 | 968.5 | 68.0708 | 49.2674 | 63.1258 | 53.7851 | 0.68071 | 0.49267 | 0.63126 | 0.53785 | 0.18803 | 0.093407 | 302.162 | 921.1389 | 43.4134
38897.6382 | 361 | 295 | 38897.6382 | 555 | 420 | 929 | 979 | 22.0391 | 18.0098 | 33.8828 | 25.641 | 0.22039 | 0.1801 | 0.33883 | 0.25641 | 0.040293 | 0.082418 | 4337.7604 | 1400.7452 | 523.4382
38897.6383 | 1109 | 949 | 38897.6383 | 1266 | 1116 | 939.5 | 989.5 | 67.7045 | 57.9365 | 77.2894 | 68.1319 | 0.67705 | 0.57937 | 0.77289 | 0.68132 | 0.09768 | 0.091575 | 790.331 | 11876.9426 | 26.3723
38897.6384 | 1088 | 927 | 38897.6385 | 1270 | 1113 | 950.5 | 1000.5 | 66.4225 | 56.5934 | 77.5336 | 67.9487 | 0.66422 | 0.56593 | 0.77534 | 0.67949 | 0.098291 | 0.095849 | 1092.7363 | 1886.6058 | 30.2601
38897.6386 | 1014 | 922 | 38897.6386 | 1194 | 1021 | 961.5 | 1011.5 | 61.9048 | 56.2882 | 72.8938 | 62.3321 | 0.61905 | 0.56288 | 0.72894 | 0.62332 | 0.056166 | 0.10562 | 890.6677 | 1721.7079 | 38.3762
38897.6387 | 1194 | 1023 | 38897.6387 | 1277 | 1110 | 972.5 | 1022.5 | 72.8938 | 62.4542 | 77.9609 | 67.7656 | 0.72894 | 0.62454 | 0.77961 | 0.67766 | 0.1044 | 0.10195 | 308.7579 | 536.8069 | 7.6946
38897.6388 | 1121 | 1066 | 38897.6388 | 1277 | 1101 | 983 | 1033 | 68.4371 | 65.0794 | 77.9609 | 67.2161 | 0.68437 | 0.65079 | 0.77961 | 0.67216 | 0.033578 | 0.10745 | 42.373 | 38.7365 | 3.2316
38897.6389 | 1078 | 905 | 38897.639 | 1149 | 1049 | 993.5 | 1043.5 | 65.812 | 55.2503 | 70.1465 | 64.0415 | 0.65812 | 0.5525 | 0.70147 | 0.64042 | 0.10562 | 0.06105 | 436.4445 | 827.4807 | 32.2743
38897.6391 | 1214 | 1021 | 38897.6391 | 1241 | 1112 | 1004.5 | 1054.5 | 74.1148 | 62.3321 | 75.7631 | 67.8877 | 0.74115 | 0.62332 | 0.75763 | 0.67888 | 0.11783 | 0.078755 | 49.6708 | 50.6878 | 2.4835
38897.6392 | 1141 | 950 | 38897.6392 | 1208 | 1005 | 1015.5 | 1065.5 | 69.6581 | 57.9976 | 73.7485 | 61.3553 | 0.69658 | 0.57998 | 0.73748 | 0.61355 | 0.11661 | 0.12393 | 1888.5007 | 735.9838 | 20.3303
38897.6393 | 1305 | 1081 | 38897.6393 | 1177 | 961 | 1026.5 | 1076.5 | 79.6703 | 65.9951 | 71.8559 | 58.6691 | 0.7967 | 0.65995 | 0.71856 | 0.58669 | 0.13675 | 0.13187 | 493.7736 | 5302.0202 | 6.8659
38897.6395 | 1030 | 815 | 38897.6395 | 1072 | 901 | 1037 | 1087 | 62.8816 | 49.7558 | 65.4457 | 55.0061 | 0.62882 | 0.49756 | 0.65446 | 0.55006 | 0.13126 | 0.1044 | 670.8993 | 3374.089 | 55.4582
38897.6396 | 1156 | 849 | 38897.6396 | 1085 | 787 | 1047.5 | 1097.5 | 70.5739 | 51.8315 | 66.2393 | 48.0464 | 0.70574 | 0.51832 | 0.66239 | 0.48046 | 0.18742 | 0.18193 | 605.8878 | 728.9244 | 31.6301
38897.6397 | 1330 | 957 | 38897.6397 | 1256 | 919 | 1058.5 | 1108.5 | 81.1966 | 58.4249 | 76.6789 | 56.105 | 0.81197 | 0.58425 | 0.76679 | 0.56105 | 0.22772 | 0.20574 | 217.8886 | 1243.7359 | 2.2612
38897.6398 | 1311 | 784 | 38897.6398 | 1178 | 706 | 1069.5 | 1119.5 | 80.0366 | 47.8632 | 71.917 | 43.1013 | 0.80037 | 0.47863 | 0.71917 | 0.43101 | 0.32173 | 0.28816 | 255.0209 | 580.2317 | 23.4333
38897.64 | 1511 | 840 | 38897.64 | 1218 | 655 | 1080.5 | 1130.5 | 92.2466 | 51.2821 | 74.359 | 39.9878 | 0.92247 | 0.51282 | 0.74359 | 0.39988 | 0.40965 | 0.34371 | 124.209 | 3063.0434 | 4.6828
38897.6401 | 1308 | 682 | 38897.6401 | 1216 | 637 | 1091 | 1141 | 79.8535 | 41.6361 | 74.2369 | 38.8889 | 0.79853 | 0.41636 | 0.74237 | 0.38889 | 0.38217 | 0.35348 | 228.3052 | 364.8085 | 36.8699
38897.6402 | 1423 | 689 | 38897.6402 | 1599 | 800 | 1101.5 | 1151.5 | 86.8742 | 42.0635 | 97.619 | 48.84 | 0.86874 | 0.42063 | 0.97619 | 0.4884 | 0.44811 | 0.48779 | 282.3336 | 164.1656 | 17.8931
38897.6403 | 1597 | 672 | 38897.6403 | 1437 | 450 | 1112.5 | 1162.5 | 97.4969 | 41.0256 | 87.7289 | 27.4725 | 0.97497 | 0.41026 | 0.87729 | 0.27473 | 0.56471 | 0.60256 | 221.7317 | 111.3931 | 3.2448
38897.6405 | 1764 | 438 | 38897.6405 | 1851 | 436 | 1123.5 | 1173.5 | 107.6923 | 26.7399 | 113.0037 | 26.6178 | 1.0769 | 0.2674 | 1.13 | 0.26618 | 0.80952 | 0.86386 | 564.5915 | 35.6322 | 6.5006
38897.6406 | 1678 | 245 | 38897.6406 | 1779 | 238 | 1134.5 | 1184.5 | 102.442 | 14.9573 | 108.6081 | 14.5299 | 1.0244 | 0.14957 | 1.0861 | 0.1453 | 0.87485 | 0.94078 | 72.3386 | 43.8435 | 48.1933
38897.6407 | 2126 | 214 | 38897.6407 | 2110 | 220 | 1144.5 | 1194.5 | 129.7924 | 13.0647 | 128.8156 | 13.431 | 1.2979 | 0.13065 | 1.2882 | 0.13431 | 1.1673 | 1.1538 | 47.5026 | 14.0434 | 1.7044
38897.6408 | 1827 | 442 | 38897.6408 | 1539 | 439 | 1155.5 | 1205.5 | 111.5385 | 26.9841 | 93.956 | 26.801 | 1.1154 | 0.26984 | 0.93956 | 0.26801 | 0.84554 | 0.67155 | 30.7186 | 234.3889 | 6.5623
38897.6409 | 1546 | 382 | 38897.641 | 1685 | 308 | 1166.5 | 1216.5 | 94.3834 | 23.3211 | 102.8694 | 18.8034 | 0.94383 | 0.23321 | 1.0287 | 0.18803 | 0.71062 | 0.84066 | 178.4653 | 51.9239 | 34.2116
38897.6411 | 1432 | 421 | 38897.6411 | 1747 | 477 | 1177.5 | 1227.5 | 87.4237 | 25.7021 | 106.6545 | 29.1209 | 0.87424 | 0.25702 | 1.0665 | 0.29121 | 0.61722 | 0.77534 | 842.3617 | 46.4309 | 34.4484
38897.6412 | 1674 | 216 | 38897.6412 | 1923 | 267 | 1188.5 | 1238.5 | 102.1978 | 13.1868 | 117.3993 | 16.3004 | 1.022 | 0.13187 | 1.174 | 0.163 | 0.89011 | 1.011 | 91.1855 | 28.4172 | 43.0671
38897.6413 | 1812 | 280 | 38897.6413 | 2001 | 311 | 1198.5 | 1248.5 | 110.6227 | 17.094 | 122.1612 | 18.9866 | 1.1062 | 0.17094 | 1.2216 | 0.18987 | 0.93529 | 1.0317 | 8713.6185 | 18.3453 | 12.09
38897.6414 | 1716 | 282 | 38897.6415 | 1834 | 301 | 1209.5 | 1259.5 | 104.7619 | 17.2161 | 111.9658 | 18.3761 | 1.0476 | 0.17216 | 1.1197 | 0.18376 | 0.87546 | 0.9359 | 79.0473 | 41.3447 | 32.4022
38897.6416 | 1751 | 309 | 38897.6416 | 2025 | 340 | 1220.5 | 1270.5 | 106.8987 | 18.8645 | 123.6264 | 20.757 | 1.069 | 0.18864 | 1.2363 | 0.20757 | 0.88034 | 1.0287 | 50.0021 | 95.5804 | 39.599
38897.6417 | 2075 | 260 | 38897.6417 | 1709 | 244 | 1231.5 | 1281.5 | 126.6789 | 15.873 | 104.3346 | 14.8962 | 1.2668 | 0.15873 | 1.0433 | 0.14896 | 1.1081 | 0.89438 | 10.9924 | 79.684 | 4.1993
38897.6418 | 2013 | 327 | 38897.6418 | 1606 | 263 | 1242.5 | 1292.5 | 122.8938 | 19.9634 | 98.0464 | 16.0562 | 1.2289 | 0.19963 | 0.98046 | 0.16056 | 1.0293 | 0.8199 | 16.497 | 280.3744 | 6.6767
38897.642 | 2206 | 170 | 38897.642 | 2103 | 114 | 1253 | 1303 | 134.6764 | 10.3785 | 128.3883 | 6.9597 | 1.3468 | 0.10379 | 1.2839 | 0.069597 | 1.243 | 1.2143 | 2.6949 | 9.2533 | 3.2692
38897.6421 | 1848 | 77 | 38897.6421 | 2192 | 88 | 1263.5 | 1313.5 | 112.8205 | 4.7009 | 133.8217 | 5.3724 | 1.1282 | 0.047009 | 1.3382 | 0.053724 | 1.0812 | 1.2845 | 100.6666 | 5.8703 | 27.7515
38897.6422 | 1893 | 130 | 38897.6422 | 1633 | 265 | 1274.5 | 1324.5 | 115.5678 | 7.9365 | 99.6947 | 16.1783 | 1.1557 | 0.079365 | 0.99695 | 0.16178 | 1.0763 | 0.83516 | 24.4273 | 239.23 | 155.8959
38897.6423 | 1848 | 321 | 38897.6423 | 1728 | 294 | 1285.5 | 1335.5 | 112.8205 | 19.5971 | 105.4945 | 17.9487 | 1.1282 | 0.19597 | 1.0549 | 0.17949 | 0.93223 | 0.87546 | 40.7727 | 81.6883 | 19.8023
38897.6425 | 1909 | 350 | 38897.6425 | 1602 | 254 | 1296.5 | 1346.5 | 116.5446 | 21.3675 | 97.8022 | 15.5067 | 1.1654 | 0.21368 | 0.97802 | 0.15507 | 0.95177 | 0.82295 | 30.8948 | 134.71 | 8.4255
38897.6426 | 1796 | 123 | 38897.6426 | 1853 | 106 | 1307 | 1357 | 109.6459 | 7.5092 | 113.1258 | 6.4713 | 1.0965 | 0.075092 | 1.1313 | 0.064713 | 1.0214 | 1.0665 | 40.3821 | 30.8102 | 74.9457
38897.6427 | 2059 | 130 | 38897.6427 | 1865 | 242 | 1317.5 | 1367.5 | 125.7021 | 7.9365 | 113.8584 | 14.7741 | 1.257 | 0.079365 | 1.1386 | 0.14774 | 1.1777 | 0.99084 | 12.4199 | 136.8384 | 53.946
38897.6428 | 1910 | 453 | 38897.6428 | 1607 | 349 | 1328.5 | 1378.5 | 116.6056 | 27.6557 | 98.1074 | 21.3065 | 1.1661 | 0.27656 | 0.98107 | 0.21306 | 0.8895 | 0.76801 | 27.1507 | 2565.3855 | 11.1801
38897.643 | 1962 | 302 | 38897.643 | 1838 | 277 | 1339.5 | 1389.5 | 119.7802 | 18.4371 | 112.21 | 16.9109 | 1.1978 | 0.18437 | 1.1221 | 0.16911 | 1.0134 | 0.95299 | 25.8735 | 96.3245 | 7.5351
38897.6431 | 2125 | 268 | 38897.6431 | 1764 | 214 | 1350.5 | 1400.5 | 129.7314 | 16.3614 | 107.6923 | 13.0647 | 1.2973 | 0.16361 | 1.0769 | 0.13065 | 1.1337 | 0.94628 | 7.3321 | 39.9203 | 8.7956
38897.6432 | 1753 | 219 | 38897.6432 | 1861 | 228 | 1360.5 | 1410.5 | 107.0208 | 13.37 | 113.6142 | 13.9194 | 1.0702 | 0.1337 | 1.1361 | 0.13919 | 0.93651 | 0.99695 | 60.4553 | 35.7826 | 40.7182
38897.6433 | 1856 | 228 | 38897.6433 | 2104 | 252 | 1371.5 | 1421.5 | 113.3089 | 13.9194 | 128.4493 | 15.3846 | 1.1331 | 0.13919 | 1.2845 | 0.15385 | 0.99389 | 1.1306 | 42.0995 | 41.5528 | 29.1464
38897.6434 | 2047 | 112 | 38897.6435 | 2271 | 118 | 1382.5 | 1432.5 | 124.9695 | 6.8376 | 138.6447 | 7.2039 | 1.2497 | 0.068376 | 1.3864 | 0.072039 | 1.1813 | 1.3144 | 1.7244 | 0.83964 | 1.1254
38897.6436 | 2294 | 117 | 38897.6436 | 1901 | 94 | 1393.5 | 1443.5 | 140.0488 | 7.1429 | 116.0562 | 5.7387 | 1.4005 | 0.071429 | 1.1606 | 0.057387 | 1.3291 | 1.1032 | 0.63141 | 28.0454 | 18.8363
38897.6437 | 2177 | 116 | 38897.6437 | 2274 | 90 | 1404.5 | 1454.5 | 132.906 | 7.0818 | 138.8278 | 5.4945 | 1.3291 | 0.070818 | 1.3883 | 0.054945 | 1.2582 | 1.3333 | 3.1327 | 5.2807 | 0.75151
38897.6438 | 1830 | 112 | 38897.6438 | 2058 | 122 | 1414.5 | 1464.5 | 111.7216 | 6.8376 | 125.641 | 7.4481 | 1.1172 | 0.068376 | 1.2564 | 0.074481 | 1.0488 | 1.1819 | 49.629 | 14.9322 | 42.7326
38897.6439 | 1967 | 154 | 38897.644 | 2217 | 187 | 1425.5 | 1475.5 | 120.0855 | 9.4017 | 135.348 | 11.4164 | 1.2009 | 0.094017 | 1.3535 | 0.11416 | 1.1068 | 1.2393 | 2.2794 | 1.1621 | 1.4127
38897.6441 | 1729 | 151 | 38897.6441 | 2068 | 176 | 1436.5 | 1486.5 | 105.5556 | 9.2186 | 126.2515 | 10.7448 | 1.0556 | 0.092186 | 1.2625 | 0.10745 | 0.96337 | 1.1551 | 118.1386 | 13.9057 | 34.7955
38897.6442 | 1588 | 320 | 38897.6442 | 1657 | 329 | 1447.5 | 1497.5 | 96.9475 | 19.536 | 101.16 | 20.0855 | 0.96947 | 0.19536 | 1.0116 | 0.20085 | 0.77411 | 0.81074 | 90.8761 | 67.6399 | 50.7355
38897.6443 | 1671 | 202 | 38897.6443 | 1927 | 172 | 1458.5 | 1508.5 | 102.0147 | 12.3321 | 117.6435 | 10.5006 | 1.0201 | 0.12332 | 1.1764 | 0.10501 | 0.89683 | 1.0714 | 100.8177 | 24.1972 | 42.1853
38897.6444 | 1759 | 129 | 38897.6445 | 1867 | 156 | 1468.5 | 1518.5 | 107.3871 | 7.8755 | 113.9805 | 9.5238 | 1.0739 | 0.078755 | 1.1398 | 0.095238 | 0.99512 | 1.0446 | 44.6915 | 32.555 | 80.4147
38897.6446 | 1960 | 110 | 38897.6446 | 2207 | 116 | 1479.5 | 1529.5 | 119.6581 | 6.7155 | 134.7375 | 7.0818 | 1.1966 | 0.067155 | 1.3474 | 0.070818 | 1.1294 | 1.2766 | 60.5369 | 8.6532 | 17.4035
38897.6447 | 1806 | 144 | 38897.6447 | 2114 | 173 | 1490.5 | 1540.5 | 110.2564 | 8.7912 | 129.0598 | 10.5617 | 1.1026 | 0.087912 | 1.2906 | 0.10562 | 1.0147 | 1.185 | 158.146 | 10.7217 | 24.2343
38897.6448 | 2003 | 117 | 38897.6448 | 2239 | 122 | 1501.5 | 1551.5 | 122.2833 | 7.1429 | 136.6911 | 7.4481 | 1.2228 | 0.071429 | 1.3669 | 0.074481 | 1.1514 | 1.2924 | 6.7808 | 4.4199 | 6.8876
38897.645 | 1763 | 244 | 38897.645 | 1997 | 276 | 1512.5 | 1562.5 | 107.6313 | 14.8962 | 121.917 | 16.8498 | 1.0763 | 0.14896 | 1.2192 | 0.1685 | 0.92735 | 1.0507 | 185.7282 | 19.9301 | 20.6623
38897.6451 | 2159 | 243 | 38897.6451 | 2110 | 246 | 1522.5 | 1572.5 | 131.8071 | 14.8352 | 128.8156 | 15.0183 | 1.3181 | 0.14835 | 1.2882 | 0.15018 | 1.1697 | 1.138 | 42.6584 | 15.5656 | 5.0783
38897.6452 | 1826 | 185 | 38897.6452 | 2015 | 196 | 1533.5 | 1583.5 | 111.4774 | 11.2943 | 123.0159 | 11.9658 | 1.1148 | 0.11294 | 1.2302 | 0.11966 | 1.0018 | 1.1105 | 72.0739 | 19.093 | 25.9442
38897.6453 | 2047 | 200 | 38897.6453 | 1908 | 176 | 1544.5 | 1594.5 | 124.9695 | 12.21 | 116.4835 | 10.7448 | 1.2497 | 0.1221 | 1.1648 | 0.10745 | 1.1276 | 1.0574 | 17.8376 | 53.9876 | 11.1104
38897.6455 | 2163 | 203 | 38897.6455 | 1747 | 185 | 1555.5 | 1605.5 | 132.0513 | 12.3932 | 106.6545 | 11.2943 | 1.3205 | 0.12393 | 1.0665 | 0.11294 | 1.1966 | 0.9536 | 5.7774 | 34.3494 | 7.0052
38897.6456 | 2125 | 241 | 38897.6456 | 1654 | 209 | 1566.5 | 1616.5 | 129.7314 | 14.7131 | 100.9768 | 12.7595 | 1.2973 | 0.14713 | 1.0098 | 0.12759 | 1.1502 | 0.88217 | 8.0271 | 56.6489 | 8.346
38897.6457 | 1770 | 417 | 38897.6457 | 1736 | 304 | 1576.5 | 1626.5 | 108.0586 | 25.4579 | 105.9829 | 18.5592 | 1.0806 | 0.25458 | 1.0598 | 0.18559 | 0.82601 | 0.87424 | 102.013 | 50.6508 | 9.9477
38897.6458 | 1997 | 457 | 38897.6458 | 1509 | 436 | 1587.5 | 1637.5 | 121.917 | 27.8999 | 92.1245 | 26.6178 | 1.2192 | 0.279 | 0.92125 | 0.26618 | 0.94017 | 0.65507 | 6.9759 | 15.4794 | 4.2126
38897.6459 | 1502 | 473 | 38897.646 | 1623 | 484 | 1598.5 | 1648.5 | 91.6972 | 28.8767 | 99.0842 | 29.5482 | 0.91697 | 0.28877 | 0.99084 | 0.29548 | 0.62821 | 0.69536 | 193.8293 | 77.2949 | 30.9122
38897.6461 | 1436 | 502 | 38897.6461 | 1741 | 519 | 1609.5 | 1659.5 | 87.6679 | 30.6471 | 106.2882 | 31.685 | 0.87668 | 0.30647 | 1.0629 | 0.31685 | 0.57021 | 0.74603 | 290.6756 | 79.2811 | 32.8033
38897.6462 | 1790 | 652 | 38897.6462 | 1659 | 622 | 1620.5 | 1670.5 | 109.2796 | 39.8046 | 101.2821 | 37.9731 | 1.0928 | 0.39805 | 1.0128 | 0.37973 | 0.69475 | 0.63309 | 102.1988 | 103.6869 | 10.2763
38897.6463 | 1851 | 567 | 38897.6463 | 1611 | 522 | 1630.5 | 1680.5 | 113.0037 | 34.6154 | 98.3516 | 31.8681 | 1.13 | 0.34615 | 0.98352 | 0.31868 | 0.78388 | 0.66484 | 9.0209 | 14.8881 | 2.4596
38897.6464 | 1427 | 625 | 38897.6465 | 1725 | 577 | 1641.5 | 1691.5 | 87.1184 | 38.1563 | 105.3114 | 35.2259 | 0.87118 | 0.38156 | 1.0531 | 0.35226 | 0.48962 | 0.70085 | 63.0936 | 104.4957 | 21.1248
| 1538 | 674 | 38897.6466 | 1462 | 692 | 1653 | 1703 | 93.895 | 41.1477 | 89.2552 | 42.2466 | 0.93895 | 0.41148 | 0.89255 | 0.42247 | 0.52747 | 0.47009 | 88.2457 | 5985.4137 | 14.3566
38897.6467 | 1649 | 722 | 38897.6467 | 1697 | 641 | 1663.5 | 1713.5 | 100.6716 | 44.0781 | 103.602 | 39.1331 | 1.0067 | 0.44078 | 1.036 | 0.39133 | 0.56593 | 0.64469 | 29.4718 | 54.8168 | 2.9729
38897.6468 | 1176 | 767 | 38897.6468 | 1385 | 751 | 1674.5 | 1724.5 | 71.7949 | 46.8254 | 84.5543 | 45.8486 | 0.71795 | 0.46825 | 0.84554 | 0.45849 | 0.24969 | 0.38706 | 439.4492 | 508.4076 | 40.0256
38897.6469 | 1282 | 823 | 38897.647 | 1394 | 827 | 1684.5 | 1734.5 | 78.2662 | 50.2442 | 85.1038 | 50.4884 | 0.78266 | 0.50244 | 0.85104 | 0.50488 | 0.28022 | 0.34615 | 568.777 | 295.8362 | 18.6507

## C2-3
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 140.3162 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38897.6269 | 1 | 0 | 38897.6269 | 1 | 0 | -44.5 | 5.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6271 | 1 | 0 | 38897.6271 | 1 | 0 | -33.5 | 16.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6272 | 1 | 0 | 38897.6272 | 1 | 0 | -23.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6273 | 1 | 0 | 38897.6273 | 1 | 0 | -12.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6274 | 1 | 0 | 38897.6274 | 1 | 0 | -1.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6276 | 1 | 0 | 38897.6276 | 1 | 0 | 9.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6277 | 1 | 0 | 38897.6277 | 1 | 0 | 20.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6278 | 2 | 0 | 38897.6278 | 1 | 0 | 30.5 | 80.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6279 | 1 | 1 | 38897.6279 | 1 | 0 | 41.5 | 91.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 527795486.44 | 229738 | 229538.087
38897.6281 | 1 | 1 | 38897.6281 | 1 | 0 | 52.5 | 102.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 527795486.44 | 229738 | 229538.087
38897.6282 | 1 | 0 | 38897.6282 | 1 | 0 | 63.5 | 113.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6283 | 1 | 0 | 38897.6283 | 1 | 0 | 74.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6284 | 2 | 0 | 38897.6284 | 2 | 0 | 85 | 135 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114819 | 114819 | 114818.9988
38897.6286 | 1 | 0 | 38897.6286 | 1 | 0 | 95.5 | 145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6287 | 1 | 0 | 38897.6287 | 1 | 0 | 106.5 | 156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6288 | 1 | 0 | 38897.6288 | 1 | 0 | 117.5 | 167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6289 | 1 | 0 | 38897.6289 | 2 | 0 | 128.5 | 178.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229738 | 114819 | 229737.9994
38897.6291 | 2 | 0 | 38897.6291 | 1 | 0 | 138.5 | 188.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6292 | 1 | 0 | 38897.6292 | 1 | 0 | 149.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6293 | 1 | 0 | 38897.6293 | 1 | 0 | 160.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6294 | 2 | 0 | 38897.6294 | 2 | 0 | 171.5 | 221.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114819 | 114819 | 114818.9988
38897.6296 | 1 | 0 | 38897.6296 | 1 | 0 | 182.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6297 | 1 | 0 | 38897.6297 | 2 | 0 | 192.5 | 242.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229738 | 114819 | 229737.9994
38897.6298 | 1 | 1 | 38897.6298 | 1 | 0 | 203.5 | 253.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 527795486.44 | 229738 | 229538.087
38897.6299 | 1 | 0 | 38897.6299 | 2 | 0 | 214.5 | 264.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229738 | 114819 | 229737.9994
38897.6301 | 2 | 0 | 38897.6301 | 1 | 0 | 225.5 | 275.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6302 | 1 | 0 | 38897.6302 | 1 | 0 | 236.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6303 | 2 | 0 | 38897.6303 | 1 | 0 | 246.5 | 296.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6304 | 2 | 0 | 38897.6304 | 2 | 0 | 257.5 | 307.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114819 | 114819 | 114818.9988
38897.6306 | 1 | 0 | 38897.6306 | 1 | 0 | 268.5 | 318.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6307 | 1 | 0 | 38897.6307 | 1 | 0 | 279.5 | 329.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6308 | 1 | 0 | 38897.6308 | 1 | 0 | 290.5 | 340.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6309 | 1 | 0 | 38897.6309 | 1 | 0 | 300.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6311 | 1 | 0 | 38897.6311 | 1 | 0 | 311.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6312 | 2 | 0 | 38897.6312 | 1 | 0 | 322.5 | 372.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6313 | 1 | 0 | 38897.6313 | 1 | 0 | 333.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6314 | 1 | 0 | 38897.6314 | 1 | 0 | 344.5 | 394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6316 | 3 | 0 | 38897.6316 | 1 | 0 | 355 | 405 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 76512.6667 | 229738 | 76512.6648
38897.6317 | 1 | 0 | 38897.6317 | 1 | 0 | 365.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6318 | 1 | 0 | 38897.6318 | 1 | 0 | 376.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6319 | 1 | 0 | 38897.6319 | 1 | 0 | 387.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6321 | 1 | 0 | 38897.6321 | 1 | 0 | 398.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6322 | 2 | 0 | 38897.6322 | 1 | 0 | 408.5 | 458.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6323 | 1 | 0 | 38897.6323 | 1 | 0 | 419.5 | 469.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6324 | 1 | 0 | 38897.6324 | 1 | 0 | 430.5 | 480.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6326 | 1 | 0 | 38897.6326 | 1 | 0 | 441.5 | 491.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6327 | 1 | 0 | 38897.6327 | 1 | 0 | 452.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6328 | 1 | 0 | 38897.6328 | 1 | 0 | 462.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6329 | 1 | 0 | 38897.6329 | 2 | 0 | 473.5 | 523.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229738 | 114819 | 229737.9994
38897.6331 | 1 | 0 | 38897.6331 | 1 | 0 | 484.5 | 534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6332 | 1 | 0 | 38897.6332 | 1 | 0 | 495.5 | 545.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6333 | 1 | 0 | 38897.6333 | 1 | 0 | 506.5 | 556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6334 | 1 | 0 | 38897.6334 | 1 | 0 | 516.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6336 | 1 | 0 | 38897.6336 | 1 | 0 | 527.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6337 | 1 | 0 | 38897.6337 | 1 | 0 | 538.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6338 | 1 | 0 | 38897.6338 | 2 | 0 | 549.5 | 599.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229738 | 114819 | 229737.9994
38897.6339 | 1 | 0 | 38897.6339 | 1 | 0 | 560.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6341 | 1 | 0 | 38897.6341 | 1 | 0 | 570.5 | 620.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6342 | 1 | 0 | 38897.6342 | 1 | 0 | 581.5 | 631.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6343 | 1 | 0 | 38897.6343 | 1 | 0 | 592.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6344 | 1 | 0 | 38897.6344 | 1 | 0 | 603.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6346 | 1 | 0 | 38897.6346 | 1 | 0 | 614.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6347 | 1 | 0 | 38897.6347 | 1 | 0 | 624.5 | 674.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6348 | 1 | 0 | 38897.6348 | 1 | 0 | 635.5 | 685.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6349 | 1 | 0 | 38897.6349 | 1 | 0 | 646.5 | 696.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6351 | 1 | 0 | 38897.6351 | 1 | 0 | 657.5 | 707.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6352 | 1 | 0 | 38897.6352 | 1 | 0 | 668.5 | 718.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6353 | 1 | 0 | 38897.6353 | 1 | 0 | 678.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6354 | 2 | 0 | 38897.6354 | 1 | 0 | 689.5 | 739.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114819 | 229738 | 114818.9988
38897.6356 | 1 | 0 | 38897.6356 | 1 | 0 | 700.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6357 | 1 | 0 | 38897.6357 | 1 | 0 | 711.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6358 | 1 | 0 | 38897.6358 | 1 | 0 | 722 | 772 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6359 | 1 | 0 | 38897.6359 | 1 | 0 | 732.5 | 782.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6361 | 1 | 0 | 38897.6361 | 1 | 0 | 743.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6362 | 1 | 0 | 38897.6362 | 1 | 0 | 754.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6363 | 1 | 0 | 38897.6363 | 1 | 0 | 765.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6364 | 1 | 0 | 38897.6364 | 1 | 0 | 776 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6366 | 1 | 0 | 38897.6366 | 1 | 0 | 786.5 | 836.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6367 | 1 | 0 | 38897.6367 | 1 | 0 | 797.5 | 847.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6368 | 1 | 0 | 38897.6368 | 1 | 0 | 808.5 | 858.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6369 | 1 | 0 | 38897.6369 | 1 | 0 | 819.5 | 869.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6371 | 1 | 0 | 38897.6371 | 1 | 0 | 830 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6372 | 1 | 0 | 38897.6372 | 1 | 0 | 840.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6373 | 1 | 0 | 38897.6373 | 1 | 0 | 851.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229738 | 229738 | 229737.9994
38897.6374 | 49 | 4 | 38897.6374 | 9 | 5 | 862.5 | 912.5 | 2.9915 | 0.2442 | 0.54945 | 0.30525 | 0.029915 | 0.002442 | 0.0054945 | 0.0030525 | 0.027473 | 0.002442 | 4999.3792 | 58702.2382 | 56039.0368
38897.6376 | 105 | 14 | 38897.6376 | 28 | 17 | 873.5 | 923.5 | 6.4103 | 0.8547 | 1.7094 | 1.0379 | 0.064103 | 0.008547 | 0.017094 | 0.010379 | 0.055556 | 0.0067155 | 2411.9904 | 22052.8272 | 15496.7291
38897.6377 | 175 | 41 | 38897.6377 | 58 | 40 | 884 | 934 | 10.6838 | 2.5031 | 3.5409 | 2.442 | 0.10684 | 0.025031 | 0.035409 | 0.02442 | 0.081807 | 0.010989 | 1587.9693 | 14471.7484 | 5044.1207
38897.6378 | 262 | 114 | 38897.6378 | 165 | 122 | 894.5 | 944.5 | 15.9951 | 6.9597 | 10.0733 | 7.4481 | 0.15995 | 0.069597 | 0.10073 | 0.074481 | 0.090354 | 0.026252 | 1393.1569 | 6230.1364 | 1659.659
38897.6379 | 304 | 155 | 38897.6379 | 218 | 153 | 905.5 | 955.5 | 18.5592 | 9.4628 | 13.3089 | 9.3407 | 0.18559 | 0.094628 | 0.13309 | 0.093407 | 0.090965 | 0.039683 | 1375.5688 | 3861.3273 | 1156.7397
38897.6381 | 366 | 221 | 38897.6381 | 302 | 238 | 916.5 | 966.5 | 22.3443 | 13.4921 | 18.4371 | 14.5299 | 0.22344 | 0.13492 | 0.18437 | 0.1453 | 0.088523 | 0.039072 | 1382.033 | 4267.6848 | 756.6503
38897.6382 | 475 | 288 | 38897.6382 | 343 | 280 | 927.5 | 977.5 | 28.9988 | 17.5824 | 20.9402 | 17.094 | 0.28999 | 0.17582 | 0.2094 | 0.17094 | 0.11416 | 0.038462 | 1002.7741 | 5574.4631 | 523.723
38897.6383 | 524 | 319 | 38897.6383 | 478 | 408 | 938 | 988 | 31.9902 | 19.475 | 29.1819 | 24.9084 | 0.3199 | 0.19475 | 0.29182 | 0.24908 | 0.12515 | 0.042735 | 883.5435 | 7641.4929 | 450.3386
38897.6384 | 734 | 538 | 38897.6384 | 1077 | 713 | 948.5 | 998.5 | 44.8107 | 32.8449 | 65.7509 | 43.5287 | 0.44811 | 0.32845 | 0.65751 | 0.43529 | 0.11966 | 0.22222 | 3505.8809 | 355.4008 | 148.8848
38897.6386 | 1105 | 936 | 38897.6386 | 909 | 875 | 959.5 | 1009.5 | 67.4603 | 57.1429 | 55.4945 | 53.4188 | 0.6746 | 0.57143 | 0.55495 | 0.53419 | 0.10317 | 0.020757 | 413.3675 | 781.9736 | 24.3801
38897.6387 | 941 | 882 | 38897.6387 | 995 | 904 | 970.5 | 1020.5 | 57.4481 | 53.8462 | 60.7448 | 55.1893 | 0.57448 | 0.53846 | 0.60745 | 0.55189 | 0.03602 | 0.055556 | 28902.0319 | 1624.2043 | 50.772
38897.6388 | 1108 | 940 | 38897.6388 | 1197 | 1022 | 981.5 | 1031.5 | 67.6435 | 57.3871 | 73.0769 | 62.3932 | 0.67643 | 0.57387 | 0.73077 | 0.62393 | 0.10256 | 0.10684 | 1706.5237 | 956.7885 | 24.1157
38897.6389 | 1052 | 884 | 38897.6389 | 996 | 840 | 992 | 1042 | 64.2247 | 53.9683 | 60.8059 | 51.2821 | 0.64225 | 0.53968 | 0.60806 | 0.51282 | 0.10256 | 0.095238 | 1088.6844 | 1651.8724 | 38.6532
38897.6391 | 1140 | 958 | 38897.6391 | 1268 | 1073 | 1002.5 | 1052.5 | 69.5971 | 58.486 | 77.4115 | 65.5067 | 0.69597 | 0.58486 | 0.77411 | 0.65507 | 0.11111 | 0.11905 | 23032.0908 | 541.3329 | 17.6551
38897.6392 | 1231 | 1033 | 38897.6392 | 999 | 850 | 1013.5 | 1063.5 | 75.1526 | 63.0647 | 60.989 | 51.8926 | 0.75153 | 0.63065 | 0.60989 | 0.51893 | 0.12088 | 0.090965 | 492.3385 | 5495.2629 | 3.2687
38897.6393 | 1302 | 1096 | 38897.6393 | 1015 | 831 | 1024.5 | 1074.5 | 79.4872 | 66.9109 | 61.9658 | 50.7326 | 0.79487 | 0.66911 | 0.61966 | 0.50733 | 0.12576 | 0.11233 | 586.7402 | 3028.9808 | 8.7989
38897.6394 | 1293 | 1083 | 38897.6394 | 1302 | 1044 | 1035.5 | 1085.5 | 78.9377 | 66.1172 | 79.4872 | 63.7363 | 0.78938 | 0.66117 | 0.79487 | 0.63736 | 0.12821 | 0.15751 | 183.7021 | 321.0903 | 5.4651
38897.6396 | 1246 | 1011 | 38897.6396 | 1344 | 1037 | 1046 | 1096 | 76.0684 | 61.7216 | 82.0513 | 63.3089 | 0.76068 | 0.61722 | 0.82051 | 0.63309 | 0.14347 | 0.18742 | 51.1472 | 55.4717 | 1.4604
38897.6397 | 1343 | 918 | 38897.6397 | 1272 | 855 | 1056.5 | 1106.5 | 81.9902 | 56.044 | 77.6557 | 52.1978 | 0.8199 | 0.56044 | 0.77656 | 0.52198 | 0.25946 | 0.25458 | 366.4284 | 558.8279 | 3.4538
38897.6398 | 1466 | 905 | 38897.6398 | 1184 | 723 | 1067.5 | 1117.5 | 89.4994 | 55.2503 | 72.2833 | 44.1392 | 0.89499 | 0.5525 | 0.72283 | 0.44139 | 0.34249 | 0.28144 | 131.405 | 1249.1995 | 7.4296
38897.6399 | 1426 | 866 | 38897.6399 | 1341 | 747 | 1078.5 | 1128.5 | 87.0574 | 52.8694 | 81.8681 | 45.6044 | 0.87057 | 0.52869 | 0.81868 | 0.45604 | 0.34188 | 0.36264 | 866.5788 | 188.5352 | 0.48139
38897.6401 | 1364 | 712 | 38897.6401 | 1654 | 742 | 1089.5 | 1139.5 | 83.2723 | 43.4676 | 100.9768 | 45.2991 | 0.83272 | 0.43468 | 1.0098 | 0.45299 | 0.39805 | 0.55678 | 32.1942 | 31.6399 | 7.5069
38897.6402 | 1495 | 685 | 38897.6402 | 1278 | 623 | 1100 | 1150 | 91.2698 | 41.8193 | 78.022 | 38.0342 | 0.9127 | 0.41819 | 0.78022 | 0.38034 | 0.49451 | 0.39988 | 104.0137 | 1820.7918 | 16.382
38897.6403 | 1506 | 645 | 38897.6403 | 1306 | 577 | 1110.5 | 1160.5 | 91.9414 | 39.3773 | 79.7314 | 35.2259 | 0.91941 | 0.39377 | 0.79731 | 0.35226 | 0.52564 | 0.44505 | 107.7929 | 512.2909 | 19.1178
38897.6404 | 1908 | 404 | 38897.6404 | 1599 | 405 | 1121.5 | 1171.5 | 116.4835 | 24.6642 | 97.619 | 24.7253 | 1.1648 | 0.24664 | 0.97619 | 0.24725 | 0.91819 | 0.72894 | 19.2108 | 76.5029 | 1.4612
38897.6406 | 1792 | 306 | 38897.6406 | 1786 | 258 | 1132.5 | 1182.5 | 109.4017 | 18.6813 | 109.0354 | 15.7509 | 1.094 | 0.18681 | 1.0904 | 0.15751 | 0.9072 | 0.93284 | 61.4341 | 46.2421 | 20.7061
38897.6407 | 1955 | 175 | 38897.6407 | 2005 | 189 | 1143.5 | 1193.5 | 119.3529 | 10.6838 | 122.4054 | 11.5385 | 1.1935 | 0.10684 | 1.2241 | 0.11538 | 1.0867 | 1.1087 | 33.102 | 23.564 | 18.3489
38897.6408 | 1425 | 470 | 38897.6408 | 1695 | 576 | 1154 | 1204 | 86.9963 | 28.6935 | 103.4799 | 35.1648 | 0.86996 | 0.28694 | 1.0348 | 0.35165 | 0.58303 | 0.68315 | 509.4845 | 59.9814 | 32.1784
38897.6409 | 1526 | 400 | 38897.6409 | 1780 | 442 | 1164.5 | 1214.5 | 93.1624 | 24.42 | 108.6691 | 26.9841 | 0.93162 | 0.2442 | 1.0867 | 0.26984 | 0.68742 | 0.81685 | 461.0419 | 41.7331 | 27.4117
38897.6411 | 1722 | 203 | 38897.6411 | 1785 | 365 | 1175.5 | 1225.5 | 105.1282 | 12.3932 | 108.9744 | 22.2833 | 1.0513 | 0.12393 | 1.0897 | 0.22283 | 0.92735 | 0.86691 | 45.1227 | 84.01 | 83.9739
38897.6412 | 1759 | 235 | 38897.6412 | 2086 | 277 | 1186.5 | 1236.5 | 107.3871 | 14.3468 | 127.3504 | 16.9109 | 1.0739 | 0.14347 | 1.2735 | 0.16911 | 0.9304 | 1.1044 | 48.7526 | 56.2686 | 46.6383
38897.6413 | 1869 | 296 | 38897.6413 | 1932 | 311 | 1197.5 | 1247.5 | 114.1026 | 18.0708 | 117.9487 | 18.9866 | 1.141 | 0.18071 | 1.1795 | 0.18987 | 0.96032 | 0.98962 | 67.6274 | 31.5538 | 10.8081
38897.6414 | 1760 | 301 | 38897.6414 | 2012 | 341 | 1208 | 1258 | 107.4481 | 18.3761 | 122.8327 | 20.8181 | 1.0745 | 0.18376 | 1.2283 | 0.20818 | 0.89072 | 1.0201 | 60.5341 | 52.8426 | 27.2657
38897.6416 | 2049 | 274 | 38897.6416 | 1619 | 285 | 1218.5 | 1268.5 | 125.0916 | 16.7277 | 98.84 | 17.3993 | 1.2509 | 0.16728 | 0.9884 | 0.17399 | 1.0836 | 0.81441 | 10.8681 | 52.7325 | 3.1023
38897.6417 | 1681 | 215 | 38897.6417 | 1803 | 234 | 1229.5 | 1279.5 | 102.6252 | 13.1258 | 110.0733 | 14.2857 | 1.0263 | 0.13126 | 1.1007 | 0.14286 | 0.89499 | 0.95788 | 65.7066 | 40.8436 | 54.2731
38897.6418 | 1595 | 256 | 38897.6418 | 1621 | 270 | 1240.5 | 1290.5 | 97.3748 | 15.6288 | 98.9621 | 16.4835 | 0.97375 | 0.15629 | 0.98962 | 0.16484 | 0.81746 | 0.82479 | 72.5887 | 69.1881 | 71.4658
38897.6419 | 1582 | 293 | 38897.6419 | 1894 | 241 | 1251.5 | 1301.5 | 96.5812 | 17.8877 | 115.6288 | 14.7131 | 0.96581 | 0.17888 | 1.1563 | 0.14713 | 0.78694 | 1.0092 | 593.4334 | 25.0796 | 28.9732
38897.6421 | 2019 | 108 | 38897.6421 | 2282 | 94 | 1262 | 1312 | 123.2601 | 6.5934 | 139.3162 | 5.7387 | 1.2326 | 0.065934 | 1.3932 | 0.057387 | 1.1667 | 1.3358 | 2.7199 | 1.2917 | 2.0236
38897.6422 | 1951 | 268 | 38897.6422 | 1617 | 236 | 1272.5 | 1322.5 | 119.1087 | 16.3614 | 98.7179 | 14.4078 | 1.1911 | 0.16361 | 0.98718 | 0.14408 | 1.0275 | 0.8431 | 22.3329 | 210.1307 | 20.0688
38897.6423 | 1586 | 274 | 38897.6423 | 1717 | 281 | 1283.5 | 1333.5 | 96.8254 | 16.7277 | 104.823 | 17.1551 | 0.96825 | 0.16728 | 1.0482 | 0.17155 | 0.80098 | 0.87668 | 91.298 | 51.5309 | 54.4085
38897.6424 | 1958 | 358 | 38897.6424 | 1688 | 308 | 1294.5 | 1344.5 | 119.536 | 21.8559 | 103.0525 | 18.8034 | 1.1954 | 0.21856 | 1.0305 | 0.18803 | 0.9768 | 0.84249 | 20.2038 | 422.5118 | 3.9798
38897.6426 | 2210 | 177 | 38897.6426 | 1848 | 127 | 1305.5 | 1355.5 | 134.9206 | 10.8059 | 112.8205 | 7.7534 | 1.3492 | 0.10806 | 1.1282 | 0.077534 | 1.2411 | 1.0507 | 2.8356 | 16.3312 | 7.0288
38897.6427 | 2036 | 111 | 38897.6427 | 2244 | 156 | 1315.5 | 1365.5 | 124.2979 | 6.7766 | 136.9963 | 9.5238 | 1.243 | 0.067766 | 1.37 | 0.095238 | 1.1752 | 1.2747 | 2.3982 | 1.2312 | 1.6586
| 1861 | 161 | 38897.6428 | 1562 | 372 | 1327 | 1377 | 113.6142 | 9.8291 | 95.3602 | 22.7106 | 1.1361 | 0.098291 | 0.9536 | 0.22711 | 1.0379 | 0.7265 | 24.7285 | 234.2665 | 120.309
38897.6429 | 1686 | 211 | 38897.6429 | 1784 | 265 | 1337.5 | 1387.5 | 102.9304 | 12.8816 | 108.9133 | 16.1783 | 1.0293 | 0.12882 | 1.0891 | 0.16178 | 0.90049 | 0.92735 | 59.1237 | 48.0376 | 61.728
38897.6431 | 2122 | 263 | 38897.6431 | 2109 | 256 | 1348.5 | 1398.5 | 129.5482 | 16.0562 | 128.7546 | 15.6288 | 1.2955 | 0.16056 | 1.2875 | 0.15629 | 1.1349 | 1.1313 | 25.0774 | 22.7576 | 6.1058
38897.6432 | 1742 | 208 | 38897.6432 | 1795 | 239 | 1359.5 | 1409.5 | 106.3492 | 12.6984 | 109.5849 | 14.591 | 1.0635 | 0.12698 | 1.0958 | 0.14591 | 0.93651 | 0.94994 | 51.3578 | 46.1547 | 52.8923
38897.6433 | 2135 | 273 | 38897.6433 | 1699 | 221 | 1370 | 1420 | 130.3419 | 16.6667 | 103.7241 | 13.4921 | 1.3034 | 0.16667 | 1.0372 | 0.13492 | 1.1368 | 0.90232 | 5.2759 | 22.1105 | 7.2706
38897.6434 | 2250 | 123 | 38897.6434 | 2231 | 106 | 1380.5 | 1430.5 | 137.3626 | 7.5092 | 136.2027 | 6.4713 | 1.3736 | 0.075092 | 1.362 | 0.064713 | 1.2985 | 1.2973 | 8.2825 | 7.9721 | 4.4793
38897.6436 | 1812 | 96 | 38897.6436 | 2073 | 103 | 1391.5 | 1441.5 | 110.6227 | 5.8608 | 126.5568 | 6.2882 | 1.1062 | 0.058608 | 1.2656 | 0.062882 | 1.0476 | 1.2027 | 50.4636 | 12.763 | 46.0258
38897.6437 | 2098 | 108 | 38897.6437 | 1989 | 98 | 1402.5 | 1452.5 | 128.083 | 6.5934 | 121.4286 | 5.9829 | 1.2808 | 0.065934 | 1.2143 | 0.059829 | 1.2149 | 1.1545 | 12.4951 | 27.9554 | 18.6879
38897.6438 | 2182 | 124 | 38897.6438 | 2184 | 129 | 1413.5 | 1463.5 | 133.2112 | 7.5702 | 133.3333 | 7.8755 | 1.3321 | 0.075702 | 1.3333 | 0.078755 | 1.2564 | 1.2546 | 13.8189 | 10.1989 | 0.56873
38897.6439 | 1886 | 148 | 38897.6439 | 1857 | 140 | 1423.5 | 1473.5 | 115.1404 | 9.0354 | 113.37 | 8.547 | 1.1514 | 0.090354 | 1.1337 | 0.08547 | 1.0611 | 1.0482 | 31.4416 | 34.707 | 46.025
38897.6441 | 2105 | 176 | 38897.6441 | 2216 | 187 | 1434.5 | 1484.5 | 128.5104 | 10.7448 | 135.2869 | 11.4164 | 1.2851 | 0.10745 | 1.3529 | 0.11416 | 1.1777 | 1.2387 | 8.5681 | 53.662 | 3.4486
38897.6442 | 1685 | 294 | 38897.6442 | 1894 | 374 | 1445.5 | 1495.5 | 102.8694 | 17.9487 | 115.6288 | 22.8327 | 1.0287 | 0.17949 | 1.1563 | 0.22833 | 0.84921 | 0.92796 | 119.4356 | 33.5068 | 27.264
38897.6443 | 1645 | 301 | 38897.6443 | 1834 | 357 | 1456.5 | 1506.5 | 100.4274 | 18.3761 | 111.9658 | 21.7949 | 1.0043 | 0.18376 | 1.1197 | 0.21795 | 0.82051 | 0.90171 | 109.1395 | 40.3845 | 33.6776
38897.6444 | 1843 | 141 | 38897.6444 | 2238 | 150 | 1467.5 | 1517.5 | 112.5153 | 8.6081 | 136.63 | 9.1575 | 1.1252 | 0.086081 | 1.3663 | 0.091575 | 1.0391 | 1.2747 | 3.3113 | 1.1701 | 2.5787
38897.6445 | 2025 | 74 | 38897.6446 | 2132 | 95 | 1477.5 | 1527.5 | 123.6264 | 4.5177 | 130.1587 | 5.7998 | 1.2363 | 0.045177 | 1.3016 | 0.057998 | 1.1911 | 1.2436 | 22.1172 | 10.3504 | 25.2717
38897.6447 | 2116 | 157 | 38897.6447 | 2237 | 175 | 1488.5 | 1538.5 | 129.1819 | 9.5849 | 136.569 | 10.6838 | 1.2918 | 0.095849 | 1.3657 | 0.10684 | 1.196 | 1.2589 | 8.0006 | 48.9749 | 5.3144
38897.6448 | 1997 | 142 | 38897.6448 | 1759 | 143 | 1499.5 | 1549.5 | 121.917 | 8.6691 | 107.3871 | 8.7302 | 1.2192 | 0.086691 | 1.0739 | 0.087302 | 1.1325 | 0.98657 | 18.4485 | 64.1455 | 43.8614
38897.6449 | 1918 | 111 | 38897.6449 | 2264 | 148 | 1510.5 | 1560.5 | 117.094 | 6.7766 | 138.2173 | 9.0354 | 1.1709 | 0.067766 | 1.3822 | 0.090354 | 1.1032 | 1.2918 | 1.9395 | 0.62342 | 1.5036
38897.6451 | 1706 | 228 | 38897.6451 | 2097 | 212 | 1521.5 | 1571.5 | 104.1514 | 13.9194 | 128.022 | 12.9426 | 1.0415 | 0.13919 | 1.2802 | 0.12943 | 0.90232 | 1.1508 | 53.6986 | 60.8256 | 60.4437
38897.6452 | 1868 | 191 | 38897.6452 | 1729 | 148 | 1531.5 | 1581.5 | 114.0415 | 11.6606 | 105.5556 | 9.0354 | 1.1404 | 0.11661 | 1.0556 | 0.090354 | 1.0238 | 0.9652 | 33.204 | 50.1537 | 41.8621
38897.6453 | 2109 | 200 | 38897.6453 | 1725 | 160 | 1542.5 | 1592.5 | 128.7546 | 12.21 | 105.3114 | 9.768 | 1.2875 | 0.1221 | 1.0531 | 0.09768 | 1.1654 | 0.95543 | 9.7989 | 845.2999 | 4.7483
38897.6454 | 1686 | 170 | 38897.6454 | 1901 | 207 | 1553.5 | 1603.5 | 102.9304 | 10.3785 | 116.0562 | 12.6374 | 1.0293 | 0.10379 | 1.1606 | 0.12637 | 0.92552 | 1.0342 | 66.1978 | 28.7685 | 58.1373
38897.6456 | 1690 | 184 | 38897.6456 | 1944 | 209 | 1564.5 | 1614.5 | 103.1746 | 11.2332 | 118.6813 | 12.7595 | 1.0317 | 0.11233 | 1.1868 | 0.12759 | 0.91941 | 1.0592 | 82.6004 | 23.9127 | 44.5092
38897.6457 | 1572 | 285 | 38897.6457 | 1785 | 284 | 1575.5 | 1625.5 | 95.9707 | 17.3993 | 108.9744 | 17.3382 | 0.95971 | 0.17399 | 1.0897 | 0.17338 | 0.78571 | 0.91636 | 125.3435 | 40.2833 | 44.4721
38897.6458 | 1895 | 522 | 38897.6458 | 1764 | 360 | 1585.5 | 1635.5 | 115.6899 | 31.8681 | 107.6923 | 21.978 | 1.1569 | 0.31868 | 1.0769 | 0.21978 | 0.83822 | 0.85714 | 3388.1144 | 38.3515 | 6.2992
38897.6459 | 1574 | 353 | 38897.6459 | 1808 | 418 | 1596.5 | 1646.5 | 96.0928 | 21.5507 | 110.3785 | 25.5189 | 0.96093 | 0.21551 | 1.1038 | 0.25519 | 0.74542 | 0.8486 | 192.1353 | 41.8254 | 31.0263
38897.6461 | 1706 | 522 | 38897.6461 | 1787 | 580 | 1607.5 | 1657.5 | 104.1514 | 31.8681 | 109.0965 | 35.409 | 1.0415 | 0.31868 | 1.091 | 0.35409 | 0.72283 | 0.73687 | 0.69684 | 0.62272 | 0.083441
38897.6462 | 1568 | 489 | 38897.6462 | 1676 | 528 | 1618.5 | 1668.5 | 95.7265 | 29.8535 | 102.3199 | 32.2344 | 0.95726 | 0.29853 | 1.0232 | 0.32234 | 0.65873 | 0.70085 | 178.2438 | 73.0685 | 20.8403
38897.6463 | 1699 | 703 | 38897.6463 | 1698 | 690 | 1629.5 | 1679.5 | 103.7241 | 42.9182 | 103.663 | 42.1245 | 1.0372 | 0.42918 | 1.0366 | 0.42125 | 0.60806 | 0.61538 | 113.167 | 150.7425 | 8.8613
38897.6464 | 1744 | 463 | 38897.6464 | 1577 | 573 | 1639.5 | 1689.5 | 106.4713 | 28.2662 | 96.2759 | 34.9817 | 1.0647 | 0.28266 | 0.96276 | 0.34982 | 0.78205 | 0.61294 | 29.3138 | 75.8782 | 8.5148
38897.6466 | 1888 | 573 | 38897.6466 | 1288 | 594 | 1650.5 | 1700.5 | 115.2625 | 34.9817 | 78.6325 | 36.2637 | 1.1526 | 0.34982 | 0.78632 | 0.36264 | 0.80281 | 0.42369 | 7.9784 | 14.9661 | 3.6945
38897.6467 | 1682 | 720 | 38897.6467 | 1342 | 690 | 1661.5 | 1711.5 | 102.6862 | 43.956 | 81.9292 | 42.1245 | 1.0269 | 0.43956 | 0.81929 | 0.42125 | 0.5873 | 0.39805 | 20.5712 | 35.3927 | 3.7621
38897.6468 | 1271 | 704 | 38897.6468 | 1350 | 720 | 1672.5 | 1722.5 | 77.5946 | 42.9792 | 82.4176 | 43.956 | 0.77595 | 0.42979 | 0.82418 | 0.43956 | 0.34615 | 0.38462 | 496.1887 | 195.585 | 30.3944
38897.6469 | 1479 | 879 | 38897.6469 | 1179 | 695 | 1683.5 | 1733.5 | 90.293 | 53.663 | 71.978 | 42.4298 | 0.90293 | 0.53663 | 0.71978 | 0.4243 | 0.3663 | 0.29548 | 124.4121 | 1499.9578 | 6.3588

## C1-4
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 144.0403 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38897.6269 | 1 | 0 | 38897.6269 | 1 | 0 | -46.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.627 | 1 | 0 | 38897.627 | 1 | 0 | -35.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6272 | 1 | 0 | 38897.6272 | 1 | 0 | -24.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6273 | 1 | 0 | 38897.6273 | 1 | 0 | -14.5 | 35.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6274 | 1 | 0 | 38897.6274 | 1 | 0 | -3.5 | 46.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6275 | 1 | 0 | 38897.6275 | 1 | 0 | 7.5 | 57.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6277 | 1 | 0 | 38897.6277 | 1 | 0 | 18.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6278 | 1 | 0 | 38897.6278 | 1 | 0 | 29.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6279 | 1 | 0 | 38897.6279 | 1 | 0 | 39.5 | 89.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.628 | 1 | 0 | 38897.628 | 1 | 0 | 50.5 | 100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6282 | 1 | 0 | 38897.6282 | 1 | 0 | 61.5 | 111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6283 | 1 | 1 | 38897.6283 | 1 | 0 | 72.5 | 122.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 556195622.44 | 235838 | 235638.0848
38897.6284 | 2 | 0 | 38897.6284 | 2 | 1 | 83.5 | 133.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6285 | 1 | 0 | 38897.6285 | 1 | 0 | 93.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6287 | 1 | 0 | 38897.6287 | 1 | 0 | 104.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6288 | 1 | 0 | 38897.6288 | 1 | 0 | 115.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6289 | 1 | 1 | 38897.6289 | 1 | 0 | 126.5 | 176.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 556195622.44 | 235838 | 235638.0848
38897.629 | 1 | 0 | 38897.6291 | 2 | 0 | 137.5 | 187.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235838 | 117869 | 235837.9994
38897.6292 | 1 | 0 | 38897.6292 | 1 | 0 | 147.5 | 197.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6293 | 1 | 0 | 38897.6293 | 1 | 0 | 158.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6294 | 2 | 0 | 38897.6294 | 1 | 0 | 169.5 | 219.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6295 | 1 | 0 | 38897.6295 | 1 | 0 | 180.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6297 | 1 | 0 | 38897.6297 | 1 | 0 | 191.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6298 | 1 | 0 | 38897.6298 | 1 | 0 | 201.5 | 251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6299 | 1 | 0 | 38897.6299 | 1 | 0 | 212.5 | 262.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.63 | 1 | 0 | 38897.63 | 2 | 0 | 223.5 | 273.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235838 | 117869 | 235837.9994
38897.6302 | 1 | 0 | 38897.6302 | 1 | 0 | 234.5 | 284.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6303 | 1 | 0 | 38897.6303 | 1 | 0 | 245.5 | 295.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6304 | 1 | 0 | 38897.6304 | 1 | 0 | 255.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6305 | 1 | 0 | 38897.6305 | 1 | 0 | 266.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6307 | 1 | 0 | 38897.6307 | 1 | 0 | 277.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6308 | 1 | 0 | 38897.6308 | 1 | 0 | 288.5 | 338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6309 | 1 | 0 | 38897.6309 | 2 | 0 | 299.5 | 349.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235838 | 117869 | 235837.9994
38897.631 | 1 | 0 | 38897.631 | 1 | 0 | 309.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6312 | 1 | 0 | 38897.6312 | 1 | 0 | 320.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6313 | 1 | 0 | 38897.6313 | 2 | 0 | 331.5 | 381.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 235838 | 117869 | 235837.9994
38897.6314 | 2 | 0 | 38897.6314 | 1 | 0 | 342.5 | 392.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6315 | 1 | 0 | 38897.6316 | 1 | 0 | 353.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6317 | 1 | 0 | 38897.6317 | 1 | 0 | 364 | 414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6318 | 2 | 0 | 38897.6318 | 1 | 0 | 374.5 | 424.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6319 | 1 | 0 | 38897.6319 | 1 | 0 | 385.5 | 435.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.632 | 1 | 0 | 38897.632 | 1 | 0 | 396.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6322 | 1 | 0 | 38897.6322 | 1 | 0 | 407.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6323 | 1 | 0 | 38897.6323 | 1 | 0 | 418 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6324 | 1 | 0 | 38897.6324 | 1 | 0 | 428.5 | 478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6325 | 1 | 0 | 38897.6325 | 1 | 0 | 439.5 | 489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6327 | 1 | 0 | 38897.6327 | 1 | 0 | 450.5 | 500.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6328 | 1 | 0 | 38897.6328 | 1 | 0 | 461.5 | 511.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6329 | 1 | 0 | 38897.6329 | 1 | 0 | 472 | 522 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.633 | 2 | 0 | 38897.633 | 2 | 0 | 482.5 | 532.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117869 | 117869 | 117868.9988
38897.6332 | 1 | 0 | 38897.6332 | 1 | 0 | 493.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6333 | 1 | 0 | 38897.6333 | 1 | 0 | 504.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6334 | 1 | 0 | 38897.6334 | 1 | 0 | 515.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6335 | 1 | 0 | 38897.6335 | 1 | 0 | 526 | 576 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6337 | 1 | 0 | 38897.6337 | 1 | 0 | 536.5 | 586.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6338 | 1 | 0 | 38897.6338 | 1 | 0 | 547.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6339 | 1 | 0 | 38897.6339 | 1 | 0 | 558.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.634 | 2 | 0 | 38897.6341 | 1 | 0 | 569.5 | 619.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6342 | 1 | 0 | 38897.6342 | 1 | 0 | 579.5 | 629.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6343 | 1 | 0 | 38897.6343 | 1 | 0 | 590.5 | 640.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6344 | 1 | 0 | 38897.6344 | 1 | 0 | 601.5 | 651.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6345 | 1 | 0 | 38897.6345 | 1 | 0 | 612.5 | 662.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6347 | 1 | 0 | 38897.6347 | 1 | 0 | 623.5 | 673.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6348 | 1 | 0 | 38897.6348 | 1 | 0 | 633.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6349 | 1 | 0 | 38897.6349 | 1 | 0 | 644.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.635 | 1 | 0 | 38897.635 | 1 | 0 | 655.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6352 | 1 | 0 | 38897.6352 | 1 | 0 | 666.5 | 716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6353 | 1 | 0 | 38897.6353 | 1 | 0 | 677.5 | 727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6354 | 1 | 0 | 38897.6354 | 1 | 0 | 687.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6355 | 1 | 0 | 38897.6355 | 1 | 0 | 698.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6357 | 1 | 0 | 38897.6357 | 1 | 0 | 709.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6358 | 1 | 0 | 38897.6358 | 1 | 0 | 720.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6359 | 1 | 0 | 38897.6359 | 1 | 0 | 731.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.636 | 1 | 0 | 38897.636 | 1 | 0 | 741.5 | 791.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6362 | 1 | 0 | 38897.6362 | 1 | 0 | 752.5 | 802.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6363 | 1 | 0 | 38897.6363 | 1 | 0 | 763.5 | 813.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6364 | 1 | 0 | 38897.6364 | 1 | 0 | 774.5 | 824.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6365 | 1 | 0 | 38897.6366 | 1 | 0 | 785.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6367 | 2 | 0 | 38897.6367 | 1 | 0 | 795.5 | 845.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117869 | 235838 | 117868.9988
38897.6368 | 1 | 0 | 38897.6368 | 1 | 0 | 806.5 | 856.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6369 | 1 | 0 | 38897.6369 | 1 | 0 | 817.5 | 867.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.637 | 1 | 0 | 38897.637 | 1 | 0 | 828.5 | 878.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6372 | 1 | 0 | 38897.6372 | 1 | 0 | 839 | 889 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6373 | 1 | 0 | 38897.6373 | 1 | 0 | 849.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235838 | 235838 | 235837.9994
38897.6374 | 1 | 0 | 38897.6374 | 81 | 21 | 860.5 | 910.5 | 0.06105 | 0 | 4.9451 | 1.2821 | 0.0006105 | 0 | 0.049451 | 0.012821 | 0.0006105 | 0.03663 | 235838 | 3832.3 | 235837.9994
38897.6375 | 68 | 292 | 38897.6375 | 257 | 163 | 871.5 | 921.5 | 4.1514 | 17.8266 | 15.6899 | 9.9512 | 0.041514 | 0.17827 | 0.1569 | 0.099512 | 0.13675 | 0.057387 | 1075.5165 | 2666.4894 | 659.9687
38897.6377 | 143 | 100 | 38897.6377 | 676 | 642 | 882.5 | 932.5 | 8.7302 | 6.105 | 41.2698 | 39.1941 | 0.087302 | 0.06105 | 0.4127 | 0.39194 | 0.026252 | 0.020757 | 5315.3464 | 7679.0348 | 2089.1738
38897.6378 | 941 | 874 | 38897.6378 | 187 | 78 | 893 | 943 | 57.4481 | 53.3578 | 11.4164 | 4.7619 | 0.57448 | 0.53358 | 0.11416 | 0.047619 | 0.040904 | 0.066545 | 5992.2057 | 2017.0976 | 59.344
38897.6379 | 218 | 155 | 38897.6379 | 329 | 179 | 903.5 | 953.5 | 13.3089 | 9.4628 | 20.0855 | 10.928 | 0.13309 | 0.094628 | 0.20085 | 0.10928 | 0.038462 | 0.091575 | 4127.5631 | 1393.8858 | 1195.7501
38897.638 | 307 | 251 | 38897.638 | 440 | 276 | 914.5 | 964.5 | 18.7424 | 15.3236 | 26.862 | 16.8498 | 0.18742 | 0.15324 | 0.26862 | 0.1685 | 0.034188 | 0.10012 | 5835.263 | 1205.1098 | 662.6912
38897.6382 | 292 | 226 | 38897.6382 | 416 | 246 | 925.5 | 975.5 | 17.8266 | 13.7973 | 25.3968 | 15.0183 | 0.17827 | 0.13797 | 0.25397 | 0.15018 | 0.040293 | 0.10379 | 4410.0324 | 1181.9478 | 751.2127
38897.6383 | 1027 | 945 | 38897.6383 | 982 | 822 | 936.5 | 986.5 | 62.6984 | 57.6923 | 59.9512 | 50.1832 | 0.62698 | 0.57692 | 0.59951 | 0.50183 | 0.050061 | 0.09768 | 2766.7181 | 2792.3402 | 39.5753
38897.6384 | 1065 | 993 | 38897.6384 | 1180 | 1042 | 947 | 997 | 65.0183 | 60.6227 | 72.0391 | 63.6142 | 0.65018 | 0.60623 | 0.72039 | 0.63614 | 0.043956 | 0.084249 | 943.7312 | 1524.0446 | 28.4816
38897.6385 | 397 | 333 | 38897.6385 | 457 | 250 | 957.5 | 1007.5 | 24.2369 | 20.3297 | 27.8999 | 15.2625 | 0.24237 | 0.2033 | 0.279 | 0.15263 | 0.039072 | 0.12637 | 6909.9797 | 935.3726 | 442.0446
38897.6387 | 1126 | 962 | 38897.6387 | 1237 | 1064 | 968.5 | 1018.5 | 68.7424 | 58.7302 | 75.5189 | 64.9573 | 0.68742 | 0.5873 | 0.75519 | 0.64957 | 0.10012 | 0.10562 | 2044.5846 | 927.8928 | 25.4655
38897.6388 | 1079 | 983 | 38897.6388 | 1048 | 886 | 979.5 | 1029.5 | 65.873 | 60.0122 | 63.9805 | 54.0904 | 0.65873 | 0.60012 | 0.6398 | 0.5409 | 0.058608 | 0.098901 | 2422.9129 | 2277.8176 | 28.98
38897.6389 | 1133 | 1035 | 38897.6389 | 994 | 971 | 990.5 | 1040.5 | 69.1697 | 63.1868 | 60.6838 | 59.2796 | 0.6917 | 0.63187 | 0.60684 | 0.5928 | 0.059829 | 0.014042 | 608.6146 | 999.9658 | 16.8098
38897.639 | 1132 | 951 | 38897.639 | 1036 | 867 | 1001 | 1051 | 69.1087 | 58.0586 | 63.2479 | 52.9304 | 0.69109 | 0.58059 | 0.63248 | 0.5293 | 0.1105 | 0.10317 | 1014.776 | 1583.7023 | 27.336
38897.6392 | 1283 | 1084 | 38897.6392 | 1024 | 908 | 1011.5 | 1061.5 | 78.3272 | 66.1783 | 62.5153 | 55.4335 | 0.78327 | 0.66178 | 0.62515 | 0.55433 | 0.12149 | 0.070818 | 323.6538 | 811.5507 | 0.62584
38897.6393 | 970 | 892 | 38897.6393 | 1088 | 886 | 1022.5 | 1072.5 | 59.2186 | 54.4567 | 66.4225 | 54.0904 | 0.59219 | 0.54457 | 0.66422 | 0.5409 | 0.047619 | 0.12332 | 1204.8405 | 2390.3632 | 53.5211
38897.6394 | 1280 | 853 | 38897.6394 | 1206 | 1034 | 1033.5 | 1083.5 | 78.1441 | 52.0757 | 73.6264 | 63.1258 | 0.78144 | 0.52076 | 0.73626 | 0.63126 | 0.26068 | 0.10501 | 104.9616 | 141.8458 | 15.5656
38897.6395 | 1044 | 793 | 38897.6395 | 1101 | 885 | 1044.5 | 1094.5 | 63.7363 | 48.4127 | 67.2161 | 54.0293 | 0.63736 | 0.48413 | 0.67216 | 0.54029 | 0.15324 | 0.13187 | 659.5237 | 1538.1316 | 61.8526
38897.6397 | 1059 | 827 | 38897.6397 | 1093 | 791 | 1055 | 1105 | 64.652 | 50.4884 | 66.7277 | 48.2906 | 0.64652 | 0.50488 | 0.66728 | 0.48291 | 0.14164 | 0.18437 | 2253.5863 | 474.4766 | 47.2767
38897.6398 | 1208 | 839 | 38897.6398 | 1331 | 870 | 1065.5 | 1115.5 | 73.7485 | 51.221 | 81.2576 | 53.1136 | 0.73748 | 0.51221 | 0.81258 | 0.53114 | 0.22527 | 0.28144 | 6215.1339 | 239.3897 | 26.262
38897.6399 | 1198 | 692 | 38897.6399 | 1306 | 787 | 1076.5 | 1126.5 | 73.138 | 42.2466 | 79.7314 | 48.0464 | 0.73138 | 0.42247 | 0.79731 | 0.48046 | 0.30891 | 0.31685 | 390.407 | 331.8616 | 52.1232
38897.64 | 1488 | 842 | 38897.64 | 1341 | 691 | 1087.5 | 1137.5 | 90.8425 | 51.4042 | 81.8681 | 42.1856 | 0.90842 | 0.51404 | 0.81868 | 0.42186 | 0.39438 | 0.39683 | 276.3538 | 254.6216 | 2.5054
38897.6402 | 1591 | 758 | 38897.6402 | 1336 | 659 | 1098.5 | 1148.5 | 97.1306 | 46.2759 | 81.5629 | 40.232 | 0.97131 | 0.46276 | 0.81563 | 0.40232 | 0.50855 | 0.41331 | 84.5313 | 997.5145 | 1.2446
38897.6403 | 1671 | 732 | 38897.6403 | 1588 | 654 | 1109 | 1159 | 102.0147 | 44.6886 | 96.9475 | 39.9267 | 1.0201 | 0.44689 | 0.96947 | 0.39927 | 0.57326 | 0.57021 | 128.6353 | 181.2514 | 3.8403
38897.6404 | 1440 | 417 | 38897.6404 | 1555 | 440 | 1119.5 | 1169.5 | 87.9121 | 25.4579 | 94.9328 | 26.862 | 0.87912 | 0.25458 | 0.94933 | 0.26862 | 0.62454 | 0.68071 | 155.3537 | 96.7064 | 59.2288
38897.6405 | 1751 | 268 | 38897.6405 | 2046 | 351 | 1130.5 | 1180.5 | 106.8987 | 16.3614 | 124.9084 | 21.4286 | 1.069 | 0.16361 | 1.2491 | 0.21429 | 0.90537 | 1.0348 | 921.4 | 18.9136 | 20.2009
38897.6407 | 1766 | 155 | 38897.6407 | 2073 | 197 | 1141.5 | 1191.5 | 107.8144 | 9.4628 | 126.5568 | 12.0269 | 1.0781 | 0.094628 | 1.2656 | 0.12027 | 0.98352 | 1.1453 | 81.7204 | 17.5163 | 42.1564
38897.6408 | 1508 | 510 | 38897.6408 | 1626 | 460 | 1152.5 | 1202.5 | 92.0635 | 31.1355 | 99.2674 | 28.083 | 0.92063 | 0.31136 | 0.99267 | 0.28083 | 0.60928 | 0.71184 | 283.9897 | 73.0442 | 28.2551
38897.6409 | 1636 | 554 | 38897.6409 | 1806 | 541 | 1163 | 1213 | 99.8779 | 33.8217 | 110.2564 | 33.0281 | 0.99878 | 0.33822 | 1.1026 | 0.33028 | 0.66056 | 0.77228 | 98.5666 | 159.1495 | 18.7762
38897.641 | 1760 | 212 | 38897.641 | 2081 | 327 | 1173.5 | 1223.5 | 107.4481 | 12.9426 | 127.0452 | 19.9634 | 1.0745 | 0.12943 | 1.2705 | 0.19963 | 0.94505 | 1.0708 | 165.0718 | 17.8918 | 27.7315
38897.6412 | 1880 | 263 | 38897.6412 | 2016 | 282 | 1184.5 | 1234.5 | 114.7741 | 16.0562 | 123.0769 | 17.2161 | 1.1477 | 0.16056 | 1.2308 | 0.17216 | 0.98718 | 1.0586 | 91.1697 | 24.1021 | 15.9786
38897.6413 | 1958 | 287 | 38897.6413 | 1666 | 242 | 1195.5 | 1245.5 | 119.536 | 17.5214 | 101.7094 | 14.7741 | 1.1954 | 0.17521 | 1.0171 | 0.14774 | 1.0201 | 0.86935 | 27.8492 | 124.9258 | 22.1351
38897.6414 | 1848 | 319 | 38897.6414 | 1788 | 284 | 1206.5 | 1256.5 | 112.8205 | 19.475 | 109.1575 | 17.3382 | 1.1282 | 0.19475 | 1.0916 | 0.17338 | 0.93346 | 0.91819 | 51.1842 | 60.1997 | 22.6622
38897.6415 | 1661 | 305 | 38897.6415 | 1819 | 311 | 1217 | 1267 | 101.4042 | 18.6203 | 111.0501 | 18.9866 | 1.014 | 0.1862 | 1.1105 | 0.18987 | 0.82784 | 0.92063 | 103.563 | 44.7446 | 39.8704
38897.6417 | 1761 | 268 | 38897.6417 | 2110 | 294 | 1227.5 | 1277.5 | 107.5092 | 16.3614 | 128.8156 | 17.9487 | 1.0751 | 0.16361 | 1.2882 | 0.17949 | 0.91148 | 1.1087 | 61.586 | 51.4017 | 41.8529
38897.6418 | 1608 | 281 | 38897.6418 | 1939 | 312 | 1238.5 | 1288.5 | 98.1685 | 17.1551 | 118.3761 | 19.0476 | 0.98168 | 0.17155 | 1.1838 | 0.19048 | 0.81013 | 0.99328 | 226.7031 | 28.2253 | 36.8474
38897.6419 | 1562 | 296 | 38897.6419 | 1720 | 330 | 1249.5 | 1299.5 | 95.3602 | 18.0708 | 105.0061 | 20.1465 | 0.9536 | 0.18071 | 1.0501 | 0.20147 | 0.77289 | 0.8486 | 103.5511 | 59.6817 | 63.3084
38897.642 | 1917 | 105 | 38897.642 | 2213 | 120 | 1260.5 | 1310.5 | 117.033 | 6.4103 | 135.1038 | 7.326 | 1.1703 | 0.064103 | 1.351 | 0.07326 | 1.1062 | 1.2778 | 114.6893 | 7.3618 | 22.0326
38897.6422 | 1631 | 238 | 38897.6422 | 1750 | 262 | 1270.5 | 1320.5 | 99.5726 | 14.5299 | 106.8376 | 15.9951 | 0.99573 | 0.1453 | 1.0684 | 0.15995 | 0.85043 | 0.90842 | 77.1148 | 53.0705 | 71.436
38897.6423 | 2029 | 323 | 38897.6423 | 1704 | 278 | 1281.5 | 1331.5 | 123.8706 | 19.7192 | 104.0293 | 16.9719 | 1.2387 | 0.19719 | 1.0403 | 0.16972 | 1.0415 | 0.87057 | 19.2752 | 4028.1504 | 2.2295
38897.6424 | 1675 | 303 | 38897.6424 | 1739 | 311 | 1292.5 | 1342.5 | 102.2589 | 18.4982 | 106.1661 | 18.9866 | 1.0226 | 0.18498 | 1.0617 | 0.18987 | 0.83761 | 0.87179 | 78.9392 | 59.9966 | 47.1988
38897.6425 | 2195 | 158 | 38897.6425 | 2032 | 155 | 1303.5 | 1353.5 | 134.0049 | 9.6459 | 124.0537 | 9.4628 | 1.34 | 0.096459 | 1.2405 | 0.094628 | 1.2436 | 1.1459 | 7.919 | 407.6423 | 3.2425
38897.6427 | 2288 | 97 | 38897.6427 | 1901 | 96 | 1314.5 | 1364.5 | 139.6825 | 5.9219 | 116.0562 | 5.8608 | 1.3968 | 0.059219 | 1.1606 | 0.058608 | 1.3376 | 1.102 | 2.8228 | 28.7222 | 5.8935
38897.6428 | 1714 | 312 | 38897.6428 | 1543 | 377 | 1324.5 | 1374.5 | 104.6398 | 19.0476 | 94.2002 | 23.0159 | 1.0464 | 0.19048 | 0.942 | 0.23016 | 0.85592 | 0.71184 | 52.4162 | 182.7349 | 69.0601
38897.6429 | 1549 | 334 | 38897.6429 | 1671 | 305 | 1335.5 | 1385.5 | 94.5665 | 20.3907 | 102.0147 | 18.6203 | 0.94567 | 0.20391 | 1.0201 | 0.1862 | 0.74176 | 0.83394 | 119.9511 | 61.9197 | 54.5427
38897.643 | 1857 | 201 | 38897.643 | 2012 | 251 | 1346.5 | 1396.5 | 113.37 | 12.2711 | 122.8327 | 15.3236 | 1.1337 | 0.12271 | 1.2283 | 0.15324 | 1.011 | 1.0751 | 56.0622 | 26.4513 | 31.3647
38897.6432 | 1791 | 128 | 38897.6432 | 2185 | 229 | 1357.5 | 1407.5 | 109.3407 | 7.8144 | 133.3944 | 13.9805 | 1.0934 | 0.078144 | 1.3339 | 0.1398 | 1.0153 | 1.1941 | 176.1526 | 9.5498 | 29.9918
38897.6433 | 2108 | 269 | 38897.6433 | 1717 | 216 | 1368.5 | 1418.5 | 128.6935 | 16.4225 | 104.823 | 13.1868 | 1.2869 | 0.16422 | 1.0482 | 0.13187 | 1.1227 | 0.91636 | 13.295 | 519.4165 | 5.4927
38897.6434 | 2000 | 122 | 38897.6434 | 1852 | 98 | 1379 | 1429 | 122.1001 | 7.4481 | 113.0647 | 5.9829 | 1.221 | 0.074481 | 1.1306 | 0.059829 | 1.1465 | 1.0708 | 23.0603 | 38.1768 | 53.7587
38897.6435 | 2080 | 104 | 38897.6435 | 2292 | 89 | 1389.5 | 1439.5 | 126.9841 | 6.3492 | 139.9267 | 5.4335 | 1.2698 | 0.063492 | 1.3993 | 0.054335 | 1.2063 | 1.3449 | 9.9705 | 12.5899 | 18.8569
38897.6437 | 1838 | 97 | 38897.6437 | 2014 | 102 | 1400.5 | 1450.5 | 112.21 | 5.9219 | 122.9548 | 6.2271 | 1.1221 | 0.059219 | 1.2295 | 0.062271 | 1.0629 | 1.1673 | 40.9242 | 20.7715 | 75.2466
38897.6438 | 2145 | 130 | 38897.6438 | 2054 | 112 | 1411.5 | 1461.5 | 130.9524 | 7.9365 | 125.3968 | 6.8376 | 1.3095 | 0.079365 | 1.254 | 0.068376 | 1.2302 | 1.1856 | 14.0287 | 26.7026 | 13.6793
38897.6439 | 2248 | 160 | 38897.6439 | 1786 | 133 | 1422.5 | 1472.5 | 137.2405 | 9.768 | 109.0354 | 8.1197 | 1.3724 | 0.09768 | 1.0904 | 0.081197 | 1.2747 | 1.0092 | 4.5654 | 45.4982 | 9.5024
38897.644 | 2228 | 184 | 38897.644 | 1821 | 150 | 1432.5 | 1482.5 | 136.0195 | 11.2332 | 111.1722 | 9.1575 | 1.3602 | 0.11233 | 1.1117 | 0.091575 | 1.2479 | 1.0201 | 5.4392 | 49.541 | 9.4741
38897.6442 | 1992 | 191 | 38897.6442 | 1999 | 218 | 1443.5 | 1493.5 | 121.6117 | 11.6606 | 122.0391 | 13.3089 | 1.2161 | 0.11661 | 1.2204 | 0.13309 | 1.0995 | 1.0873 | 29.3837 | 34.6822 | 23.78
38897.6443 | 1663 | 301 | 38897.6443 | 1852 | 292 | 1454.5 | 1504.5 | 101.5263 | 18.3761 | 113.0647 | 17.8266 | 1.0153 | 0.18376 | 1.1306 | 0.17827 | 0.8315 | 0.95238 | 119.8408 | 38.5447 | 36.5445
38897.6444 | 1945 | 153 | 38897.6444 | 2045 | 145 | 1465.5 | 1515.5 | 118.7424 | 9.3407 | 124.8474 | 8.8523 | 1.1874 | 0.093407 | 1.2485 | 0.088523 | 1.094 | 1.16 | 39.6407 | 20.4913 | 29.0532
38897.6445 | 2184 | 79 | 38897.6445 | 2343 | 61 | 1476.5 | 1526.5 | 133.3333 | 4.823 | 143.0403 | 3.7241 | 1.3333 | 0.04823 | 1.4304 | 0.037241 | 1.2851 | 1.3932 | 1.3349 | 0.71604 | 0.86735
38897.6447 | 2070 | 155 | 38897.6447 | 1728 | 130 | 1487 | 1537 | 126.3736 | 9.4628 | 105.4945 | 7.9365 | 1.2637 | 0.094628 | 1.0549 | 0.079365 | 1.1691 | 0.97558 | 16.9085 | 76.1473 | 37.4784
38897.6448 | 2264 | 140 | 38897.6448 | 1804 | 125 | 1497.5 | 1547.5 | 138.2173 | 8.547 | 110.1343 | 7.6313 | 1.3822 | 0.08547 | 1.1013 | 0.076313 | 1.2967 | 1.025 | 3.7554 | 33.6685 | 8.0278
38897.6449 | 2100 | 121 | 38897.6449 | 2278 | 132 | 1508.5 | 1558.5 | 128.2051 | 7.3871 | 139.072 | 8.0586 | 1.2821 | 0.073871 | 1.3907 | 0.080586 | 1.2082 | 1.3101 | 5.2085 | 4.0321 | 4.4325
38897.645 | 1970 | 149 | 38897.645 | 1638 | 223 | 1519.5 | 1569.5 | 120.2686 | 9.0965 | 100 | 13.6142 | 1.2027 | 0.090965 | 1 | 0.13614 | 1.1117 | 0.86386 | 22.4578 | 170.9327 | 101.7831
38897.6452 | 2052 | 172 | 38897.6452 | 2098 | 161 | 1530.5 | 1580.5 | 125.2747 | 10.5006 | 128.083 | 9.8291 | 1.2527 | 0.10501 | 1.2808 | 0.098291 | 1.1477 | 1.1825 | 33.2749 | 17.9871 | 11.9992
38897.6453 | 1959 | 200 | 38897.6453 | 1799 | 166 | 1540.5 | 1590.5 | 119.5971 | 12.21 | 109.8291 | 10.1343 | 1.196 | 0.1221 | 1.0983 | 0.10134 | 1.0739 | 0.99695 | 29.0036 | 52.8333 | 34.6349
38897.6454 | 1896 | 180 | 38897.6454 | 2067 | 206 | 1551.5 | 1601.5 | 115.7509 | 10.989 | 126.1905 | 12.5763 | 1.1575 | 0.10989 | 1.2619 | 0.12576 | 1.0476 | 1.1361 | 59.0144 | 19.3382 | 25.5113
38897.6455 | 1830 | 192 | 38897.6455 | 2155 | 241 | 1562.5 | 1612.5 | 111.7216 | 11.7216 | 131.5629 | 14.7131 | 1.1172 | 0.11722 | 1.3156 | 0.14713 | 1 | 1.1685 | 189.2875 | 14.135 | 21.7618
38897.6457 | 1705 | 235 | 38897.6457 | 2179 | 228 | 1573.5 | 1623.5 | 104.0904 | 14.3468 | 133.0281 | 13.9194 | 1.0409 | 0.14347 | 1.3303 | 0.13919 | 0.89744 | 1.1911 | 33.3411 | 47.6978 | 57.6321
38897.6458 | 1624 | 416 | 38897.6458 | 1714 | 450 | 1584.5 | 1634.5 | 99.1453 | 25.3968 | 104.6398 | 27.4725 | 0.99145 | 0.25397 | 1.0464 | 0.27473 | 0.73748 | 0.77167 | 113.2408 | 74.4712 | 32.7702
38897.6459 | 1650 | 492 | 38897.6459 | 1793 | 549 | 1594.5 | 1644.5 | 100.7326 | 30.0366 | 109.4628 | 33.5165 | 1.0073 | 0.30037 | 1.0946 | 0.33516 | 0.70696 | 0.75946 | 300.4804 | 53.367 | 15.3743
38897.646 | 1770 | 548 | 38897.646 | 1511 | 444 | 1605.5 | 1655.5 | 108.0586 | 33.4554 | 92.2466 | 27.1062 | 1.0806 | 0.33455 | 0.92247 | 0.27106 | 0.74603 | 0.6514 | 56.7929 | 297.4564 | 5.6512
38897.6462 | 1474 | 528 | 38897.6462 | 1732 | 660 | 1616.5 | 1666.5 | 89.9878 | 32.2344 | 105.7387 | 40.293 | 0.89988 | 0.32234 | 1.0574 | 0.40293 | 0.57753 | 0.65446 | 753.0875 | 63.7348 | 26.347
38897.6463 | 1508 | 653 | 38897.6463 | 1685 | 671 | 1627.5 | 1677.5 | 92.0635 | 39.8657 | 102.8694 | 40.9646 | 0.92063 | 0.39866 | 1.0287 | 0.40965 | 0.52198 | 0.61905 | 158.9658 | 204.4294 | 20.4005
38897.6464 | 1558 | 430 | 38897.6464 | 1911 | 510 | 1638.5 | 1688.5 | 95.116 | 26.2515 | 116.6667 | 31.1355 | 0.95116 | 0.26252 | 1.1667 | 0.31136 | 0.68864 | 0.85531 | 144.8651 | 74.8074 | 36.9602
38897.6465 | 1442 | 760 | 38897.6465 | 1469 | 671 | 1648.5 | 1698.5 | 88.0342 | 46.398 | 89.6825 | 40.9646 | 0.88034 | 0.46398 | 0.89683 | 0.40965 | 0.41636 | 0.48718 | 40420.5707 | 111.809 | 10.9312
38897.6467 | 1483 | 868 | 38897.6467 | 1436 | 577 | 1659.5 | 1709.5 | 90.5372 | 52.9915 | 87.6679 | 35.2259 | 0.90537 | 0.52991 | 0.87668 | 0.35226 | 0.37546 | 0.52442 | 173.516 | 789.6041 | 0.85691
38897.6468 | 1439 | 727 | 38897.6468 | 1517 | 725 | 1670.5 | 1720.5 | 87.851 | 44.3834 | 92.6129 | 44.2613 | 0.87851 | 0.44383 | 0.92613 | 0.44261 | 0.43468 | 0.48352 | 1034.7183 | 116.684 | 14.3239
38897.6469 | 1214 | 736 | 38897.6469 | 1409 | 850 | 1681.5 | 1731.5 | 74.1148 | 44.9328 | 86.0195 | 51.8926 | 0.74115 | 0.44933 | 0.8602 | 0.51893 | 0.29182 | 0.34127 | 1080.1954 | 197.8678 | 36.9488

## C1-3
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 140.4383 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38897.6269 | 1 | 0 | 38897.6269 | 1 | 0 | -48.5 | 1.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.627 | 1 | 0 | 38897.627 | 1 | 0 | -37.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6271 | 1 | 0 | 38897.6272 | 1 | 0 | -26.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6273 | 1 | 0 | 38897.6273 | 1 | 0 | -15.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6274 | 1 | 0 | 38897.6274 | 1 | 0 | -5.5 | 44.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6275 | 1 | 1 |  | 1 | 0 | 5 | 55 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 528714838.44 | 229938 | 229738.0869
38897.6276 | 1 | 0 | 38897.6277 | 1 | 0 | 16.5 | 66.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6278 | 1 | 0 | 38897.6278 | 2 | 1 | 27.5 | 77.5 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6279 | 1 | 0 | 38897.6279 | 1 | 0 | 38.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.628 | 1 | 1 | 38897.628 | 1 | 0 | 49 | 99 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 528714838.44 | 229938 | 229738.0869
38897.6281 | 2 | 1 | 38897.6281 | 2 | 0 | 59.5 | 109.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038.1742 | 114919 | 229538.2608
38897.6283 | 1 | 0 | 38897.6283 | 1 | 0 | 70.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6284 | 2 | 0 | 38897.6284 | 2 | 0 | 81.5 | 131.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114919 | 114919 | 114918.9988
38897.6285 | 1 | 0 | 38897.6285 | 1 | 0 | 92.5 | 142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6286 | 1 | 0 | 38897.6286 | 1 | 0 | 102.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6288 | 1 | 0 | 38897.6288 | 1 | 0 | 113.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6289 | 2 | 0 | 38897.6289 | 2 | 0 | 124.5 | 174.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114919 | 114919 | 114918.9988
38897.629 | 2 | 0 | 38897.629 | 1 | 0 | 135.5 | 185.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6291 | 1 | 0 | 38897.6292 | 1 | 0 | 146.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6293 | 1 | 0 | 38897.6293 | 1 | 0 | 156.5 | 206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6294 | 1 | 0 | 38897.6294 | 1 | 0 | 167.5 | 217.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6295 | 1 | 0 | 38897.6295 | 1 | 0 | 178.5 | 228.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6296 | 1 | 0 | 38897.6297 | 1 | 0 | 189.5 | 239.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6298 | 1 | 0 | 38897.6298 | 1 | 0 | 200.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6299 | 1 | 0 | 38897.6299 | 1 | 0 | 210.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.63 | 1 | 0 | 38897.63 | 1 | 0 | 221.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6301 | 1 | 0 | 38897.6302 | 1 | 0 | 232.5 | 282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6303 | 1 | 0 | 38897.6303 | 1 | 0 | 243.5 | 293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6304 | 1 | 0 | 38897.6304 | 1 | 0 | 254.5 | 304.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6305 | 1 | 0 | 38897.6305 | 2 | 0 | 264.5 | 314.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229938 | 114919 | 229937.9994
38897.6306 | 1 | 0 | 38897.6306 | 1 | 0 | 275.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6308 | 1 | 0 | 38897.6308 | 1 | 0 | 286.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6309 | 2 | 0 | 38897.6309 | 1 | 0 | 297.5 | 347.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.631 | 1 | 0 | 38897.631 | 1 | 0 | 308.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6311 | 1 | 0 | 38897.6311 | 1 | 0 | 318.5 | 368.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6313 | 1 | 0 | 38897.6313 | 1 | 0 | 329.5 | 379.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6314 | 1 | 0 | 38897.6314 | 1 | 0 | 340.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6315 | 1 | 0 | 38897.6315 | 1 | 0 | 351.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6316 | 1 | 0 | 38897.6317 | 1 | 0 | 362.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6318 | 1 | 0 | 38897.6318 | 1 | 0 | 372.5 | 422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6319 | 1 | 0 | 38897.6319 | 1 | 0 | 383.5 | 433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.632 | 1 | 0 | 38897.632 | 1 | 0 | 394.5 | 444.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6321 | 2 | 0 | 38897.6322 | 1 | 0 | 405.5 | 455.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6323 | 1 | 0 | 38897.6323 | 1 | 0 | 416.5 | 466.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6324 | 1 | 0 | 38897.6324 | 2 | 0 | 426.5 | 476.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 229938 | 114919 | 229937.9994
38897.6325 | 2 | 0 | 38897.6325 | 1 | 0 | 437.5 | 487.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6326 | 1 | 0 | 38897.6327 | 1 | 0 | 448.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6328 | 1 | 0 | 38897.6328 | 1 | 0 | 459.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6329 | 1 | 0 | 38897.6329 | 1 | 0 | 470.5 | 520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.633 | 1 | 0 | 38897.633 | 1 | 0 | 480.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6331 | 1 | 0 | 38897.6331 | 1 | 0 | 491.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6333 | 2 | 0 | 38897.6333 | 1 | 0 | 502.5 | 552.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6334 | 1 | 0 | 38897.6334 | 1 | 0 | 513.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6335 | 1 | 0 | 38897.6335 | 1 | 0 | 524.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6336 | 1 | 0 | 38897.6336 | 1 | 0 | 534.5 | 584.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6338 | 1 | 0 | 38897.6338 | 1 | 0 | 545.5 | 595.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6339 | 1 | 0 | 38897.6339 | 1 | 0 | 556.5 | 606.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.634 | 1 | 0 | 38897.634 | 1 | 0 | 567.5 | 617.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6341 | 2 | 0 | 38897.6342 | 1 | 0 | 578.5 | 628.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6343 | 1 | 0 | 38897.6343 | 1 | 0 | 588.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6344 | 1 | 0 | 38897.6344 | 1 | 0 | 599.5 | 649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6345 | 1 | 0 | 38897.6345 | 1 | 0 | 610.5 | 660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6346 | 1 | 0 | 38897.6347 | 1 | 0 | 621.5 | 671.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6348 | 1 | 0 | 38897.6348 | 1 | 0 | 632.5 | 682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6349 | 1 | 0 | 38897.6349 | 1 | 0 | 642.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.635 | 1 | 0 | 38897.635 | 1 | 0 | 653.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6351 | 1 | 0 | 38897.6352 | 1 | 0 | 664.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6353 | 1 | 0 | 38897.6353 | 1 | 0 | 675.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6354 | 1 | 0 | 38897.6354 | 1 | 0 | 686.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6355 | 1 | 0 | 38897.6355 | 1 | 0 | 696.5 | 746.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6356 | 1 | 0 | 38897.6356 | 1 | 0 | 707.5 | 757.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6358 | 1 | 0 | 38897.6358 | 1 | 0 | 718.5 | 768.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6359 | 1 | 0 | 38897.6359 | 1 | 0 | 729.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.636 | 1 | 0 | 38897.636 | 1 | 0 | 740.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6361 | 1 | 0 | 38897.6361 | 1 | 0 | 750.5 | 800.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6363 | 1 | 0 | 38897.6363 | 1 | 0 | 761.5 | 811.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6364 | 1 | 0 | 38897.6364 | 1 | 0 | 772.5 | 822.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6365 | 1 | 0 | 38897.6365 | 1 | 0 | 783.5 | 833.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6366 | 1 | 0 | 38897.6367 | 1 | 0 | 794.5 | 844.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6368 | 1 | 0 | 38897.6368 | 1 | 0 | 804.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6369 | 1 | 0 | 38897.6369 | 1 | 0 | 815.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.637 | 1 | 0 | 38897.637 | 1 | 0 | 826.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6371 | 2 | 0 | 38897.6372 | 1 | 0 | 837.5 | 887.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114919 | 229938 | 114918.9988
38897.6373 | 1 | 0 | 38897.6373 | 1 | 0 | 848 | 898 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6374 | 1 | 0 | 38897.6374 | 1 | 0 | 858.5 | 908.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38897.6375 | 13 | 2 | 38897.6375 | 10 | 3 | 869.5 | 919.5 | 0.79365 | 0.1221 | 0.6105 | 0.18315 | 0.0079365 | 0.001221 | 0.006105 | 0.0018315 | 0.0067155 | 0.0042735 | 20805.9013 | 32787.2513 | 113921.5432
38897.6376 | 28 | 2 | 38897.6377 | 24 | 9 | 880.5 | 930.5 | 1.7094 | 0.1221 | 1.4652 | 0.54945 | 0.017094 | 0.001221 | 0.014652 | 0.0054945 | 0.015873 | 0.0091575 | 8744.325 | 15280.7167 | 112780.9395
38897.6378 | 153 | 34 | 38897.6378 | 70 | 44 | 891.5 | 941.5 | 9.3407 | 2.0757 | 4.2735 | 2.6862 | 0.093407 | 0.020757 | 0.042735 | 0.026862 | 0.07265 | 0.015873 | 1809.9858 | 9463.1765 | 6150.8261
38897.6379 | 94 | 25 | 38897.6379 | 103 | 28 | 902 | 952 | 5.7387 | 1.5263 | 6.2882 | 1.7094 | 0.057387 | 0.015263 | 0.062882 | 0.017094 | 0.042125 | 0.045788 | 3237.2236 | 2964.0226 | 8440.7466
38897.638 | 197 | 85 | 38897.638 | 169 | 91 | 912.5 | 962.5 | 12.0269 | 5.1893 | 10.3175 | 5.5556 | 0.12027 | 0.051893 | 0.10317 | 0.055556 | 0.068376 | 0.047619 | 1928.3347 | 2908.5068 | 2295.6364
38897.6381 | 197 | 98 | 38897.6381 | 215 | 104 | 923.5 | 973.5 | 12.0269 | 5.9829 | 13.1258 | 6.3492 | 0.12027 | 0.059829 | 0.13126 | 0.063492 | 0.06044 | 0.067766 | 2237.5882 | 1960.8256 | 1947.0107
38897.6383 | 530 | 256 | 38897.6383 | 365 | 290 | 934.5 | 984.5 | 32.3565 | 15.6288 | 22.2833 | 17.7045 | 0.32357 | 0.15629 | 0.22283 | 0.17705 | 0.16728 | 0.045788 | 655.871 | 6286.9699 | 582.2928
38897.6384 | 281 | 192 | 38897.6384 | 553 | 443 | 945.5 | 995.5 | 17.1551 | 11.7216 | 33.7607 | 27.0452 | 0.17155 | 0.11722 | 0.33761 | 0.27045 | 0.054335 | 0.067155 | 2562.2394 | 1884.7716 | 903.8073
38897.6385 | 1144 | 966 | 38897.6385 | 894 | 801 | 956 | 1006 | 69.8413 | 58.9744 | 54.5788 | 48.9011 | 0.69841 | 0.58974 | 0.54579 | 0.48901 | 0.10867 | 0.056777 | 531.1877 | 2433.4294 | 18.9302
38897.6386 | 593 | 513 | 38897.6386 | 1048 | 754 | 966.5 | 1016.5 | 36.2027 | 31.3187 | 63.9805 | 46.0317 | 0.36203 | 0.31319 | 0.6398 | 0.46032 | 0.04884 | 0.17949 | 3459.2756 | 1674.095 | 219.6992
38897.6388 | 1253 | 1103 | 38897.6388 | 992 | 832 | 977.5 | 1027.5 | 76.4957 | 67.3382 | 60.5617 | 50.7937 | 0.76496 | 0.67338 | 0.60562 | 0.50794 | 0.091575 | 0.09768 | 2288.8964 | 1058.1266 | 4.6072
38897.6389 | 1246 | 1063 | 38897.6389 | 1191 | 996 | 988.5 | 1038.5 | 76.0684 | 64.8962 | 72.7106 | 60.8059 | 0.76068 | 0.64896 | 0.72711 | 0.60806 | 0.11172 | 0.11905 | 2599.5344 | 746.2809 | 0.71509
38897.639 | 1278 | 1113 | 38897.639 | 996 | 888 | 999.5 | 1049.5 | 78.022 | 67.9487 | 60.8059 | 54.2125 | 0.78022 | 0.67949 | 0.60806 | 0.54212 | 0.10073 | 0.065934 | 363.3264 | 956.2319 | 7.3711
38897.6391 | 1253 | 1057 | 38897.6391 | 1229 | 1033 | 1010 | 1060 | 76.4957 | 64.5299 | 75.0305 | 63.0647 | 0.76496 | 0.6453 | 0.75031 | 0.63065 | 0.11966 | 0.11966 | 1073.6633 | 1073.6633 | 0.83258
38897.6393 | 1027 | 900 | 38897.6393 | 1130 | 928 | 1020.5 | 1070.5 | 62.6984 | 54.9451 | 68.9866 | 56.6545 | 0.62698 | 0.54945 | 0.68987 | 0.56654 | 0.077534 | 0.12332 | 1975.5854 | 1438.9831 | 38.7909
38897.6394 | 1166 | 941 | 38897.6394 | 991 | 871 | 1031.5 | 1081.5 | 71.1844 | 57.4481 | 60.5006 | 53.1746 | 0.71184 | 0.57448 | 0.60501 | 0.53175 | 0.13736 | 0.07326 | 366.4052 | 1112.3311 | 18.8554
38897.6395 | 1077 | 832 | 38897.6395 | 1252 | 959 | 1042.5 | 1092.5 | 65.7509 | 50.7937 | 76.4347 | 58.547 | 0.65751 | 0.50794 | 0.76435 | 0.58547 | 0.14957 | 0.17888 | 3706.3196 | 392.4675 | 37.4888
38897.6396 | 1345 | 940 | 38897.6397 | 1137 | 789 | 1053.5 | 1103.5 | 82.1123 | 57.3871 | 69.4139 | 48.1685 | 0.82112 | 0.57387 | 0.69414 | 0.48168 | 0.24725 | 0.21245 | 256.7253 | 2860.7033 | 1.5809
38897.6398 | 1221 | 768 | 38897.6398 | 1296 | 862 | 1064 | 1114 | 74.5421 | 46.8864 | 79.1209 | 52.6252 | 0.74542 | 0.46886 | 0.79121 | 0.52625 | 0.27656 | 0.26496 | 346.9091 | 541.3867 | 34.2229
38897.6399 | 1193 | 690 | 38897.6399 | 1438 | 835 | 1074.5 | 1124.5 | 72.8327 | 42.1245 | 87.79 | 50.9768 | 0.72833 | 0.42125 | 0.8779 | 0.50977 | 0.30708 | 0.36813 | 2139.4328 | 152.9121 | 36.5725
38897.64 | 1309 | 751 | 38897.64 | 1546 | 774 | 1085.5 | 1135.5 | 79.9145 | 45.8486 | 94.3834 | 47.2527 | 0.79915 | 0.45849 | 0.94383 | 0.47253 | 0.34066 | 0.47131 | 104.8954 | 194.0003 | 21.1209
38897.6401 | 1530 | 806 | 38897.6402 | 1287 | 658 | 1096.5 | 1146.5 | 93.4066 | 49.2063 | 78.5714 | 40.1709 | 0.93407 | 0.49206 | 0.78571 | 0.40171 | 0.442 | 0.384 | 110.4213 | 3061.5027 | 4.2796
38897.6403 | 1374 | 574 | 38897.6403 | 1418 | 571 | 1107.5 | 1157.5 | 83.8828 | 35.0427 | 86.569 | 34.8596 | 0.83883 | 0.35043 | 0.86569 | 0.3486 | 0.4884 | 0.51709 | 222.8526 | 149.3593 | 36.771
38897.6404 | 1469 | 452 | 38897.6404 | 1724 | 551 | 1118 | 1168 | 89.6825 | 27.5946 | 105.2503 | 33.6386 | 0.89683 | 0.27595 | 1.0525 | 0.33639 | 0.62088 | 0.71612 | 411.0909 | 55.4763 | 29.9488
38897.6405 | 1700 | 315 | 38897.6405 | 1891 | 327 | 1128.5 | 1178.5 | 103.7851 | 19.2308 | 115.4457 | 19.9634 | 1.0379 | 0.19231 | 1.1545 | 0.19963 | 0.84554 | 0.95482 | 192.084 | 29.3723 | 20.5688
38897.6406 | 2181 | 196 | 38897.6406 | 2208 | 153 | 1139.5 | 1189.5 | 133.1502 | 11.9658 | 134.7985 | 9.3407 | 1.3315 | 0.11966 | 1.348 | 0.093407 | 1.2118 | 1.2546 | 8.6414 | 32.4768 | 9.5834
38897.6408 | 1751 | 319 | 38897.6408 | 1838 | 429 | 1150.5 | 1200.5 | 106.8987 | 19.475 | 112.21 | 26.1905 | 1.069 | 0.19475 | 1.1221 | 0.2619 | 0.87424 | 0.8602 | 55.0987 | 73.3474 | 30.5578
38897.6409 | 1776 | 618 | 38897.6409 | 1385 | 508 | 1161.5 | 1211.5 | 108.4249 | 37.7289 | 84.5543 | 31.0134 | 1.0842 | 0.37729 | 0.84554 | 0.31013 | 0.70696 | 0.53541 | 32.057 | 129.3499 | 8.5437
38897.641 | 2017 | 316 | 38897.641 | 1632 | 219 | 1172 | 1222 | 123.138 | 19.2918 | 99.6337 | 13.37 | 1.2314 | 0.19292 | 0.99634 | 0.1337 | 1.0385 | 0.86264 | 17.4103 | 430.8771 | 8.3783
38897.6411 | 1720 | 284 | 38897.6411 | 1682 | 245 | 1182.5 | 1232.5 | 105.0061 | 17.3382 | 102.6862 | 14.9573 | 1.0501 | 0.17338 | 1.0269 | 0.14957 | 0.87668 | 0.87729 | 60.2884 | 60.0008 | 39.135
38897.6413 | 2057 | 284 | 38897.6413 | 1596 | 261 | 1193.5 | 1243.5 | 125.58 | 17.3382 | 97.4359 | 15.9341 | 1.2558 | 0.17338 | 0.97436 | 0.15934 | 1.0824 | 0.81502 | 11.1884 | 70.5945 | 5.9187
38897.6414 | 1989 | 307 | 38897.6414 | 1832 | 275 | 1204.5 | 1254.5 | 121.4286 | 18.7424 | 111.8437 | 16.7888 | 1.2143 | 0.18742 | 1.1184 | 0.16789 | 1.0269 | 0.95055 | 19.8244 | 275.8099 | 1.0471
38897.6415 | 1952 | 350 | 38897.6415 | 2036 | 294 | 1215.5 | 1265.5 | 119.1697 | 21.3675 | 124.2979 | 17.9487 | 1.1917 | 0.21368 | 1.243 | 0.17949 | 0.97802 | 1.0635 | 5.7988 | 7.9441 | 0.034064
38897.6416 | 1603 | 255 | 38897.6416 | 1612 | 254 | 1226 | 1276 | 97.8632 | 15.5678 | 98.4127 | 15.5067 | 0.97863 | 0.15568 | 0.98413 | 0.15507 | 0.82295 | 0.82906 | 71.3995 | 68.6831 | 70.6372
38897.6418 | 1741 | 286 | 38897.6418 | 1882 | 339 | 1236.5 | 1286.5 | 106.2882 | 17.4603 | 114.8962 | 20.696 | 1.0629 | 0.1746 | 1.149 | 0.20696 | 0.88828 | 0.942 | 81.8654 | 37.0607 | 25.8465
38897.6419 | 1717 | 303 | 38897.6419 | 2002 | 366 | 1247.5 | 1297.5 | 104.823 | 18.4982 | 122.2222 | 22.3443 | 1.0482 | 0.18498 | 1.2222 | 0.22344 | 0.86325 | 0.99878 | 85.599 | 41.3667 | 27.0775
38897.642 | 1913 | 95 | 38897.642 | 2184 | 129 | 1258.5 | 1308.5 | 116.7888 | 5.7998 | 133.3333 | 7.8755 | 1.1679 | 0.057998 | 1.3333 | 0.078755 | 1.1099 | 1.2546 | 200.7375 | 5.8461 | 16.9986
38897.6421 | 2052 | 308 | 38897.6422 | 2094 | 311 | 1269.5 | 1319.5 | 125.2747 | 18.8034 | 127.8388 | 18.9866 | 1.2527 | 0.18803 | 1.2784 | 0.18987 | 1.0647 | 1.0885 | 23.5299 | 44.741 | 5.9835
38897.6423 | 1584 | 283 | 38897.6423 | 1944 | 328 | 1279.5 | 1329.5 | 96.7033 | 17.2772 | 118.6813 | 20.0244 | 0.96703 | 0.17277 | 1.1868 | 0.20024 | 0.79426 | 0.98657 | 2569.9105 | 22.2288 | 27.85
38897.6424 | 1692 | 292 | 38897.6424 | 1743 | 330 | 1290.5 | 1340.5 | 103.2967 | 17.8266 | 106.4103 | 20.1465 | 1.033 | 0.17827 | 1.0641 | 0.20147 | 0.8547 | 0.86264 | 66.009 | 61.0447 | 41.0703
38897.6425 | 1905 | 138 | 38897.6425 | 2133 | 164 | 1301.5 | 1351.5 | 116.3004 | 8.4249 | 130.2198 | 10.0122 | 1.163 | 0.084249 | 1.3022 | 0.10012 | 1.0788 | 1.2021 | 181.1543 | 8.9104 | 15.259
38897.6426 | 1891 | 94 | 38897.6427 | 2091 | 103 | 1312.5 | 1362.5 | 115.4457 | 5.7387 | 127.6557 | 6.2882 | 1.1545 | 0.057387 | 1.2766 | 0.062882 | 1.0971 | 1.2137 | 40.1481 | 12.0928 | 36.1955
38897.6428 | 1890 | 319 | 38897.6428 | 1957 | 435 | 1323.5 | 1373.5 | 115.3846 | 19.475 | 119.475 | 26.5568 | 1.1538 | 0.19475 | 1.1947 | 0.26557 | 0.9591 | 0.92918 | 3.9889 | 3.6595 | 1.0113
38897.6429 | 1680 | 414 | 38897.6429 | 1619 | 352 | 1333.5 | 1383.5 | 102.5641 | 25.2747 | 98.84 | 21.4896 | 1.0256 | 0.25275 | 0.9884 | 0.2149 | 0.77289 | 0.7735 | 81.9271 | 81.3734 | 22.3654
38897.643 | 1834 | 219 | 38897.643 | 2117 | 175 | 1344.5 | 1394.5 | 111.9658 | 13.37 | 129.243 | 10.6838 | 1.1197 | 0.1337 | 1.2924 | 0.10684 | 0.98596 | 1.1856 | 36.5495 | 64.6062 | 44.3352
38897.6431 | 1995 | 243 | 38897.6431 | 1664 | 200 | 1355.5 | 1405.5 | 121.7949 | 14.8352 | 101.5873 | 12.21 | 1.2179 | 0.14835 | 1.0159 | 0.1221 | 1.0696 | 0.89377 | 19.1966 | 150.7481 | 15.4331
38897.6433 | 2131 | 274 | 38897.6433 | 1846 | 231 | 1366.5 | 1416.5 | 130.0977 | 16.7277 | 112.6984 | 14.1026 | 1.301 | 0.16728 | 1.127 | 0.14103 | 1.1337 | 0.98596 | 3.4064 | 8.7949 | 3.0866
38897.6434 | 1691 | 167 | 38897.6434 | 1870 | 205 | 1377.5 | 1427.5 | 103.2357 | 10.1954 | 114.1636 | 12.5153 | 1.0324 | 0.10195 | 1.1416 | 0.12515 | 0.9304 | 1.0165 | 60.3503 | 32.4738 | 64.9354
38897.6435 | 1899 | 95 | 38897.6435 | 1941 | 98 | 1388 | 1438 | 115.9341 | 5.7998 | 118.4982 | 5.9829 | 1.1593 | 0.057998 | 1.185 | 0.059829 | 1.1013 | 1.1252 | 28.5138 | 23.9697 | 62.3569
38897.6436 | 1986 | 92 | 38897.6436 | 2101 | 116 | 1398.5 | 1448.5 | 121.2454 | 5.6166 | 128.2662 | 7.0818 | 1.2125 | 0.056166 | 1.2827 | 0.070818 | 1.1563 | 1.2118 | 26.6705 | 12.8627 | 27.548
38897.6438 | 1777 | 99 | 38897.6438 | 1965 | 107 | 1409.5 | 1459.5 | 108.486 | 6.044 | 119.9634 | 6.5324 | 1.0849 | 0.06044 | 1.1996 | 0.065324 | 1.0244 | 1.1343 | 43.5393 | 20.802 | 73.8162
38897.6439 | 1746 | 115 | 38897.6439 | 2202 | 150 | 1420.5 | 1470.5 | 106.5934 | 7.0208 | 134.4322 | 9.1575 | 1.0659 | 0.070208 | 1.3443 | 0.091575 | 0.99573 | 1.2527 | 49.3761 | 22.6276 | 70.5005
38897.644 | 2037 | 160 | 38897.644 | 2005 | 178 | 1431.5 | 1481.5 | 124.359 | 9.768 | 122.4054 | 10.8669 | 1.2436 | 0.09768 | 1.2241 | 0.10867 | 1.1459 | 1.1154 | 18.8156 | 33.5287 | 16.224
38897.6441 | 1865 | 171 | 38897.6441 | 2086 | 199 | 1441.5 | 1491.5 | 113.8584 | 10.4396 | 127.3504 | 12.149 | 1.1386 | 0.1044 | 1.2735 | 0.12149 | 1.0342 | 1.152 | 146.5014 | 12.2421 | 16.863
38897.6443 | 1858 | 385 | 38897.6443 | 2011 | 328 | 1452.5 | 1502.5 | 113.431 | 23.5043 | 122.7717 | 20.0244 | 1.1343 | 0.23504 | 1.2277 | 0.20024 | 0.89927 | 1.0275 | 0.78301 | 0.69969 | 0.10356
38897.6444 | 1908 | 199 | 38897.6444 | 1793 | 158 | 1463.5 | 1513.5 | 116.4835 | 12.149 | 109.4628 | 9.6459 | 1.1648 | 0.12149 | 1.0946 | 0.096459 | 1.0433 | 0.99817 | 30.945 | 45.1238 | 30.2152
38897.6445 | 2062 | 179 | 38897.6445 | 2140 | 149 | 1474.5 | 1524.5 | 125.8852 | 10.928 | 130.6471 | 9.0965 | 1.2589 | 0.10928 | 1.3065 | 0.090965 | 1.1496 | 1.2155 | 21.2533 | 23.5098 | 6.3144
38897.6446 | 2140 | 180 | 38897.6447 | 2067 | 162 | 1485.5 | 1535.5 | 130.6471 | 10.989 | 126.1905 | 9.8901 | 1.3065 | 0.10989 | 1.2619 | 0.098901 | 1.1966 | 1.163 | 7.2207 | 68.9348 | 4.4478
38897.6448 | 2239 | 175 | 38897.6448 | 1843 | 102 | 1496 | 1546 | 136.6911 | 10.6838 | 112.5153 | 6.2271 | 1.3669 | 0.10684 | 1.1252 | 0.062271 | 1.2601 | 1.0629 | 1.5991 | 9.8625 | 5.8285
38897.6449 | 1762 | 110 | 38897.6449 | 2284 | 134 | 1506.5 | 1556.5 | 107.5702 | 6.7155 | 139.4383 | 8.1807 | 1.0757 | 0.067155 | 1.3944 | 0.081807 | 1.0085 | 1.3126 | 2.8272 | 0.63252 | 2.4478
38897.645 | 2243 | 121 | 38897.645 | 1892 | 103 | 1517.5 | 1567.5 | 136.9353 | 7.3871 | 115.5067 | 6.2882 | 1.3694 | 0.073871 | 1.1551 | 0.062882 | 1.2955 | 1.0922 | 1.6874 | 9.4638 | 4.5457
38897.6451 | 1860 | 199 | 38897.6452 | 1812 | 174 | 1528.5 | 1578.5 | 113.5531 | 12.149 | 110.6227 | 10.6227 | 1.1355 | 0.12149 | 1.1062 | 0.10623 | 1.014 | 1 | 37.1873 | 41.7384 | 35.7187
38897.6453 | 2136 | 211 | 38897.6453 | 1692 | 163 | 1539.5 | 1589.5 | 130.4029 | 12.8816 | 103.2967 | 9.9512 | 1.304 | 0.12882 | 1.033 | 0.099512 | 1.1752 | 0.93346 | 7.7327 | 105.0843 | 11.3213
38897.6454 | 1704 | 178 | 38897.6454 | 1966 | 209 | 1549.5 | 1599.5 | 104.0293 | 10.8669 | 120.0244 | 12.7595 | 1.0403 | 0.10867 | 1.2002 | 0.12759 | 0.93162 | 1.0726 | 82.127 | 22.2547 | 42.7865
38897.6455 | 2024 | 205 | 38897.6455 | 1898 | 206 | 1560.5 | 1610.5 | 123.5653 | 12.5153 | 115.873 | 12.5763 | 1.2357 | 0.12515 | 1.1587 | 0.12576 | 1.1105 | 1.033 | 17.9136 | 74.2349 | 14.8353
38897.6456 | 2056 | 282 | 38897.6456 | 1553 | 303 | 1571.5 | 1621.5 | 125.5189 | 17.2161 | 94.8107 | 18.4982 | 1.2552 | 0.17216 | 0.94811 | 0.18498 | 1.083 | 0.76313 | 9.986 | 41.8875 | 3.9383
38897.6458 | 1528 | 364 | 38897.6458 | 1924 | 374 | 1582.5 | 1632.5 | 93.2845 | 22.2222 | 117.4603 | 22.8327 | 0.93284 | 0.22222 | 1.1746 | 0.22833 | 0.71062 | 0.94628 | 122.5854 | 68.1744 | 45.4804
38897.6459 | 1715 | 384 | 38897.6459 | 1849 | 502 | 1593.5 | 1643.5 | 104.7009 | 23.4432 | 112.8816 | 30.6471 | 1.047 | 0.23443 | 1.1288 | 0.30647 | 0.81258 | 0.82234 | 85.5421 | 59.38 | 19.5385
38897.646 | 1629 | 434 | 38897.646 | 1845 | 489 | 1603.5 | 1653.5 | 99.4505 | 26.4957 | 112.6374 | 29.8535 | 0.99451 | 0.26496 | 1.1264 | 0.29853 | 0.72955 | 0.82784 | 210.9582 | 49.5011 | 18.1103
38897.6461 | 1756 | 645 | 38897.6461 | 1520 | 554 | 1614.5 | 1664.5 | 107.2039 | 39.3773 | 92.7961 | 33.8217 | 1.072 | 0.39377 | 0.92796 | 0.33822 | 0.67827 | 0.58974 | 27.6689 | 75.308 | 6.7014
38897.6463 | 1464 | 614 | 38897.6463 | 1462 | 540 | 1625.5 | 1675.5 | 89.3773 | 37.4847 | 89.2552 | 32.967 | 0.89377 | 0.37485 | 0.89255 | 0.32967 | 0.51893 | 0.56288 | 252.2911 | 118.4217 | 19.6364
38897.6464 | 1655 | 486 | 38897.6464 | 1868 | 472 | 1636.5 | 1686.5 | 101.0379 | 29.6703 | 114.0415 | 28.8156 | 1.0104 | 0.2967 | 1.1404 | 0.28816 | 0.71368 | 0.85226 | 28.7031 | 45.0221 | 10.181
38897.6465 | 1496 | 637 | 38897.6465 | 1770 | 632 | 1647.5 | 1697.5 | 91.3309 | 38.8889 | 108.0586 | 38.5836 | 0.91331 | 0.38889 | 1.0806 | 0.38584 | 0.52442 | 0.69475 | 8.9277 | 7.815 | 1.9046
38897.6466 | 1617 | 806 | 38897.6466 | 1561 | 738 | 1657.5 | 1707.5 | 98.7179 | 49.2063 | 95.2991 | 45.0549 | 0.98718 | 0.49206 | 0.95299 | 0.45055 | 0.49512 | 0.50244 | 140.5798 | 248.088 | 10.8428
38897.6468 | 1477 | 746 | 38897.6468 | 1580 | 814 | 1668.5 | 1718.5 | 90.1709 | 45.5433 | 96.4591 | 49.6947 | 0.90171 | 0.45543 | 0.96459 | 0.49695 | 0.44628 | 0.46764 | 31.4408 | 39.5164 | 2.9379
38897.6469 | 1421 | 785 | 38897.6469 | 1463 | 901 | 1679.5 | 1729.5 | 86.7521 | 47.9243 | 89.3162 | 55.0061 | 0.86752 | 0.47924 | 0.89316 | 0.55006 | 0.38828 | 0.3431 | 31.8261 | 36.9051 | 3.241

## C1-2
Penlight Test 2 |  |  | 2006-06-29 | 15:03 |  | Vs = |  | 140.4994 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38897.6269 | 1 | 0 | 38897.6269 | 1 | 0 | -50 | 0 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.627 | 1 | 0 | 38897.627 | 1 | 0 | -39.5 | 10.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6271 | 1 | 0 | 38897.6271 | 1 | 0 | -28.5 | 21.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6272 | 1 | 0 | 38897.6273 | 1 | 0 | -17.5 | 32.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6274 | 5 | 0 | 38897.6274 | 1 | 0 | -6.5 | 43.5 | 0.30525 | 0 | 0.06105 | 0 | 0.0030525 | 0 | 0.0006105 | 0 | 0.0030525 | 0.0006105 | 45927.6 | 230038 | 45927.5969
38897.6275 | 1 | 0 | 38897.6275 | 1 | 0 | 3.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6276 | 1 | 0 | 38897.6276 | 1 | 0 | 14.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6277 | 1 | 0 | 38897.6278 | 1 | 0 | 25.5 | 75.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6279 | 1 | 0 | 38897.6279 | 1 | 0 | 36.5 | 86.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.628 | 1 | 0 | 38897.628 | 1 | 0 | 47.5 | 97.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6281 | 1 | 0 | 38897.6281 | 1 | 0 | 58 | 108 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6282 | 1 | 1 | 38897.6283 | 1 | 0 | 68.5 | 118.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 529174814.44 | 230038 | 229838.0869
38897.6284 | 2 | 1 | 38897.6284 | 2 | 0 | 79.5 | 129.5 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230138.1741 | 114969 | 229638.2607
38897.6285 | 2 | 0 | 38897.6285 | 1 | 0 | 90.5 | 140.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6286 | 1 | 0 | 38897.6286 | 1 | 0 | 101.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6287 | 1 | 0 | 38897.6288 | 1 | 0 | 111.5 | 161.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6289 | 2 | 0 | 38897.6289 | 1 | 0 | 122.5 | 172.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.629 | 1 | 0 | 38897.629 | 1 | 0 | 133.5 | 183.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6291 | 1 | 0 | 38897.6291 | 1 | 0 | 144.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6292 | 1 | 0 | 38897.6293 | 1 | 0 | 155.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6294 | 2 | 0 | 38897.6294 | 1 | 0 | 165.5 | 215.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6295 | 1 | 0 | 38897.6295 | 1 | 0 | 176.5 | 226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6296 | 1 | 0 | 38897.6296 | 2 | 0 | 187.5 | 237.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038 | 114969 | 230037.9994
38897.6297 | 1 | 0 | 38897.6298 | 1 | 0 | 198.5 | 248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6299 | 2 | 0 | 38897.6299 | 2 | 0 | 209.5 | 259.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114969 | 114969 | 114968.9988
38897.63 | 1 | 0 | 38897.63 | 1 | 0 | 219.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6301 | 1 | 0 | 38897.6301 | 1 | 0 | 230.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6302 | 1 | 0 | 38897.6303 | 1 | 0 | 241.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6304 | 1 | 0 | 38897.6304 | 1 | 0 | 252.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6305 | 1 | 0 | 38897.6305 | 1 | 0 | 263.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6306 | 1 | 0 | 38897.6306 | 1 | 0 | 273.5 | 323.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6307 | 1 | 0 | 38897.6308 | 2 | 0 | 284.5 | 334.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038 | 114969 | 230037.9994
38897.6309 | 1 | 0 | 38897.6309 | 1 | 0 | 295.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.631 | 2 | 0 | 38897.631 | 1 | 0 | 306.5 | 356.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6311 | 1 | 0 | 38897.6311 | 1 | 0 | 317.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6312 | 1 | 0 | 38897.6312 | 1 | 0 | 327.5 | 377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6314 | 1 | 0 | 38897.6314 | 1 | 0 | 338.5 | 388.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6315 | 1 | 0 | 38897.6315 | 2 | 0 | 349.5 | 399.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038 | 114969 | 230037.9994
38897.6316 | 1 | 0 | 38897.6316 | 1 | 0 | 360.5 | 410.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6317 | 1 | 0 | 38897.6318 | 1 | 0 | 371.5 | 421.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6319 | 1 | 0 | 38897.6319 | 1 | 0 | 381.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.632 | 2 | 0 | 38897.632 | 1 | 0 | 392.5 | 442.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6321 | 2 | 0 | 38897.6321 | 1 | 0 | 403.5 | 453.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6322 | 1 | 0 | 38897.6323 | 1 | 0 | 414.5 | 464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6324 | 1 | 0 | 38897.6324 | 1 | 0 | 425.5 | 475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6325 | 1 | 0 | 38897.6325 | 1 | 0 | 435.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6326 | 2 | 0 | 38897.6326 | 1 | 0 | 446.5 | 496.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6327 | 1 | 0 | 38897.6328 | 1 | 0 | 457.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6329 | 1 | 0 | 38897.6329 | 1 | 0 | 468.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.633 | 1 | 0 | 38897.633 | 2 | 0 | 479.5 | 529.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038 | 114969 | 230037.9994
38897.6331 | 1 | 0 | 38897.6331 | 1 | 0 | 489.5 | 539.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6332 | 1 | 0 | 38897.6333 | 1 | 0 | 500.5 | 550.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6334 | 1 | 0 | 38897.6334 | 1 | 0 | 511.5 | 561.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6335 | 1 | 0 | 38897.6335 | 1 | 0 | 522.5 | 572.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6336 | 1 | 0 | 38897.6336 | 1 | 0 | 533.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6337 | 1 | 0 | 38897.6338 | 1 | 0 | 543.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6339 | 1 | 0 | 38897.6339 | 1 | 0 | 554.5 | 604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.634 | 1 | 0 | 38897.634 | 1 | 0 | 565.5 | 615.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6341 | 1 | 0 | 38897.6341 | 1 | 0 | 576.5 | 626.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6342 | 1 | 0 | 38897.6343 | 1 | 0 | 587.5 | 637.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6344 | 1 | 0 | 38897.6344 | 1 | 0 | 597.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6345 | 1 | 0 | 38897.6345 | 1 | 0 | 608.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6346 | 1 | 0 | 38897.6346 | 1 | 0 | 619.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6347 | 1 | 0 | 38897.6348 | 1 | 0 | 630.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6349 | 1 | 0 | 38897.6349 | 1 | 0 | 641.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.635 | 1 | 0 | 38897.635 | 1 | 0 | 651.5 | 701.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6351 | 1 | 0 | 38897.6351 | 1 | 0 | 662.5 | 712.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6352 | 1 | 0 | 38897.6353 | 1 | 0 | 673.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6354 | 2 | 0 | 38897.6354 | 1 | 0 | 684.5 | 734.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114969 | 230038 | 114968.9988
38897.6355 | 1 | 0 | 38897.6355 | 1 | 0 | 695 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6356 | 1 | 0 | 38897.6356 | 1 | 0 | 705.5 | 755.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6357 | 1 | 0 | 38897.6358 | 1 | 0 | 716.5 | 766.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6359 | 1 | 0 | 38897.6359 | 1 | 0 | 727.5 | 777.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.636 | 1 | 0 | 38897.636 | 1 | 0 | 738.5 | 788.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6361 | 1 | 0 | 38897.6361 | 1 | 0 | 749.5 | 799.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6362 | 1 | 0 | 38897.6363 | 1 | 0 | 759.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6364 | 1 | 0 | 38897.6364 | 1 | 0 | 770.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6365 | 1 | 0 | 38897.6365 | 1 | 0 | 781.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6366 | 1 | 0 | 38897.6366 | 1 | 0 | 792.5 | 842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6367 | 1 | 0 | 38897.6368 | 2 | 0 | 803.5 | 853.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 230038 | 114969 | 230037.9994
38897.6369 | 1 | 0 | 38897.6369 | 1 | 0 | 813.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.637 | 1 | 0 | 38897.637 | 1 | 0 | 824.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6371 | 1 | 0 | 38897.6371 | 1 | 0 | 835.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6372 | 1 | 0 | 38897.6373 | 1 | 0 | 846.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230038 | 230038 | 230037.9994
38897.6374 | 1 | 1 | 38897.6374 | 3 | 0 | 857 | 907 | 0.06105 | 0.06105 | 0.18315 | 0 | 0.0006105 | 0.0006105 | 0.0018315 | 0 | 0 | 0.0018315 | 176238246.1467 | 76612.6667 | 229638.2607
38897.6375 | 47 | 23 | 38897.6375 | 164 | 93 | 867.5 | 917.5 | 2.8694 | 1.4042 | 10.0122 | 5.6777 | 0.028694 | 0.014042 | 0.10012 | 0.056777 | 0.014652 | 0.043346 | 9697.8014 | 3051.6118 | 9393.8207
38897.6376 | 129 | 88 | 38897.6376 | 202 | 145 | 878.5 | 928.5 | 7.8755 | 5.3724 | 12.3321 | 8.8523 | 0.078755 | 0.053724 | 0.12332 | 0.088523 | 0.025031 | 0.034799 | 5610.6227 | 3858.0469 | 2308.7706
38897.6377 | 155 | 100 | 38897.6378 | 234 | 132 | 889.5 | 939.5 | 9.4628 | 6.105 | 14.2857 | 8.0586 | 0.094628 | 0.06105 | 0.14286 | 0.080586 | 0.033578 | 0.062271 | 4274.3294 | 2090.1248 | 1952.9433
38897.6379 | 135 | 82 | 38897.6379 | 203 | 79 | 900.5 | 950.5 | 8.2418 | 5.0061 | 12.3932 | 4.823 | 0.082418 | 0.050061 | 0.12393 | 0.04823 | 0.032357 | 0.075702 | 4492.4135 | 1716.5859 | 2401.998
38897.638 | 258 | 196 | 38897.638 | 296 | 158 | 911 | 961 | 15.7509 | 11.9658 | 18.0708 | 9.6459 | 0.15751 | 0.11966 | 0.18071 | 0.096459 | 0.037851 | 0.084249 | 4180.2559 | 1494.0956 | 883.4138
38897.6381 | 407 | 308 | 38897.6381 | 369 | 235 | 921.5 | 971.5 | 24.8474 | 18.8034 | 22.5275 | 14.3468 | 0.24847 | 0.18803 | 0.22527 | 0.14347 | 0.06044 | 0.081807 | 2391.652 | 1556.1853 | 483.9594
38897.6382 | 341 | 279 | 38897.6383 | 535 | 349 | 932.5 | 982.5 | 20.8181 | 17.033 | 32.6618 | 21.3065 | 0.20818 | 0.17033 | 0.32662 | 0.21306 | 0.037851 | 0.11355 | 5840.5309 | 981.1886 | 546.906
38897.6384 | 1006 | 1000 | 38897.6384 | 444 | 257 | 943.5 | 993.5 | 61.4164 | 61.0501 | 27.1062 | 15.6899 | 0.61416 | 0.6105 | 0.27106 | 0.1569 | 0.003663 | 0.11416 | 1222.0318 | 999.9785 | 26.8527
38897.6385 | 778 | 713 | 38897.6385 | 1051 | 890 | 954.5 | 1004.5 | 47.4969 | 43.5287 | 64.1636 | 54.3346 | 0.47497 | 0.43529 | 0.64164 | 0.54335 | 0.039683 | 0.098291 | 3789.6728 | 2874.7906 | 109.8371
38897.6386 | 378 | 307 | 38897.6386 | 696 | 485 | 965 | 1015 | 23.0769 | 18.7424 | 42.4908 | 29.6093 | 0.23077 | 0.18742 | 0.42491 | 0.29609 | 0.043346 | 0.12882 | 5972.6897 | 791.2965 | 467.436
38897.6387 | 953 | 907 | 38897.6387 | 1133 | 958 | 975.5 | 1025.5 | 58.1807 | 55.3724 | 69.1697 | 58.486 | 0.58181 | 0.55372 | 0.6917 | 0.58486 | 0.028083 | 0.10684 | 673.002 | 587.6139 | 41.5865
38897.6389 | 1004 | 842 | 38897.6389 | 1115 | 941 | 986.5 | 1036.5 | 61.2943 | 51.4042 | 68.0708 | 57.4481 | 0.61294 | 0.51404 | 0.68071 | 0.57448 | 0.098901 | 0.10623 | 1634.7916 | 1018.8842 | 49.2495
38897.639 | 1000 | 960 | 38897.639 | 1061 | 886 | 997.5 | 1047.5 | 61.0501 | 58.6081 | 64.7741 | 54.0904 | 0.6105 | 0.58608 | 0.64774 | 0.5409 | 0.02442 | 0.10684 | 645.0539 | 593.5177 | 30.4329
38897.6391 | 1047 | 869 | 38897.6391 | 1139 | 953 | 1008.5 | 1058.5 | 63.9194 | 53.0525 | 69.536 | 58.1807 | 0.63919 | 0.53053 | 0.69536 | 0.58181 | 0.10867 | 0.11355 | 1391.4606 | 989.1685 | 40.2758
38897.6392 | 1030 | 849 | 38897.6392 | 1176 | 1069 | 1019 | 1069 | 62.8816 | 51.8315 | 71.7949 | 65.2625 | 0.62882 | 0.51832 | 0.71795 | 0.65263 | 0.1105 | 0.065324 | 463.6252 | 910.6918 | 44.8279
38897.6394 | 723 | 580 | 38897.6394 | 679 | 431 | 1029.5 | 1079.5 | 44.1392 | 35.409 | 41.453 | 26.3126 | 0.44139 | 0.35409 | 0.41453 | 0.26313 | 0.087302 | 0.1514 | 2621.079 | 700.6414 | 150.6349
38897.6395 | 1276 | 923 | 38897.6395 | 1082 | 822 | 1040.5 | 1090.5 | 77.8999 | 56.3492 | 66.0562 | 50.1832 | 0.779 | 0.56349 | 0.66056 | 0.50183 | 0.21551 | 0.15873 | 258.1219 | 2086.0427 | 10.5847
38897.6396 | 1259 | 904 | 38897.6396 | 1280 | 915 | 1051.5 | 1101.5 | 76.862 | 55.1893 | 78.1441 | 55.8608 | 0.76862 | 0.55189 | 0.78144 | 0.55861 | 0.21673 | 0.22283 | 727.8787 | 426.8337 | 12.402
38897.6397 | 1139 | 728 | 38897.6398 | 1360 | 858 | 1062.5 | 1112.5 | 69.536 | 44.4444 | 83.0281 | 52.381 | 0.69536 | 0.44444 | 0.83028 | 0.52381 | 0.25092 | 0.30647 | 2189.2375 | 203.406 | 40.0017
38897.6399 | 1376 | 825 | 38897.6399 | 1381 | 872 | 1073 | 1123 | 84.0049 | 50.3663 | 84.3101 | 53.2357 | 0.84005 | 0.50366 | 0.8431 | 0.53236 | 0.33639 | 0.31074 | 151.714 | 1399.483 | 11.3558
38897.64 | 1470 | 762 | 38897.64 | 1189 | 645 | 1083.5 | 1133.5 | 89.7436 | 46.5201 | 72.5885 | 39.3773 | 0.89744 | 0.4652 | 0.72589 | 0.39377 | 0.43223 | 0.33211 | 116.1602 | 9872.2452 | 9.0137
38897.6401 | 1260 | 624 | 38897.6401 | 1419 | 706 | 1094.5 | 1144.5 | 76.9231 | 38.0952 | 86.63 | 43.1013 | 0.76923 | 0.38095 | 0.8663 | 0.43101 | 0.38828 | 0.43529 | 411.3708 | 162.9876 | 41.454
38897.6402 | 1225 | 627 | 38897.6403 | 1441 | 744 | 1105.5 | 1155.5 | 74.7863 | 38.2784 | 87.9731 | 45.4212 | 0.74786 | 0.38278 | 0.87973 | 0.45421 | 0.36508 | 0.42552 | 593.1324 | 150.5308 | 43.0636
38897.6404 | 1639 | 537 | 38897.6404 | 1797 | 565 | 1116.5 | 1166.5 | 100.0611 | 32.7839 | 109.707 | 34.4933 | 1.0006 | 0.32784 | 1.0971 | 0.34493 | 0.67277 | 0.75214 | 29.0157 | 45.4764 | 7.2987
38897.6405 | 1722 | 316 | 38897.6405 | 1996 | 350 | 1127 | 1177 | 105.1282 | 19.2918 | 121.8559 | 21.3675 | 1.0513 | 0.19292 | 1.2186 | 0.21368 | 0.85836 | 1.0049 | 73.0746 | 51.5381 | 28.3467
38897.6406 | 1994 | 200 | 38897.6406 | 2182 | 183 | 1137.5 | 1187.5 | 121.7338 | 12.21 | 133.2112 | 11.1722 | 1.2173 | 0.1221 | 1.3321 | 0.11172 | 1.0952 | 1.2204 | 0.05119 | 0.033407 | 0.01793
38897.6407 | 2106 | 249 | 38897.6408 | 1644 | 220 | 1148.5 | 1198.5 | 128.5714 | 15.2015 | 100.3663 | 13.431 | 1.2857 | 0.15201 | 1.0037 | 0.13431 | 1.1337 | 0.86935 | 8.5039 | 56.5221 | 7.7762
38897.6409 | 1436 | 530 | 38897.6409 | 1579 | 551 | 1159.5 | 1209.5 | 87.6679 | 32.3565 | 96.398 | 33.6386 | 0.87668 | 0.32357 | 0.96398 | 0.33639 | 0.55311 | 0.62759 | 303.8257 | 85.3226 | 29.1338
38897.641 | 2044 | 311 | 38897.641 | 1684 | 219 | 1170.5 | 1220.5 | 124.7863 | 18.9866 | 102.8083 | 13.37 | 1.2479 | 0.18987 | 1.0281 | 0.1337 | 1.058 | 0.89438 | 14.7797 | 3682.808 | 16.7854
38897.6411 | 1889 | 347 | 38897.6411 | 1665 | 315 | 1180.5 | 1230.5 | 115.3236 | 21.1844 | 101.6484 | 19.2308 | 1.1532 | 0.21184 | 1.0165 | 0.19231 | 0.94139 | 0.82418 | 29.8579 | 215.7212 | 12.8737
38897.6412 | 2095 | 280 | 38897.6413 | 1840 | 240 | 1191.5 | 1241.5 | 127.8999 | 17.094 | 112.3321 | 14.652 | 1.279 | 0.17094 | 1.1233 | 0.14652 | 1.1081 | 0.9768 | 7.1955 | 26.5861 | 5.5221
38897.6414 | 1600 | 254 | 38897.6414 | 1745 | 266 | 1202.5 | 1252.5 | 97.6801 | 15.5067 | 106.5324 | 16.2393 | 0.9768 | 0.15507 | 1.0653 | 0.16239 | 0.82173 | 0.90293 | 86.4553 | 47.5 | 56.7211
38897.6415 | 1850 | 339 | 38897.6415 | 1678 | 296 | 1213.5 | 1263.5 | 112.9426 | 20.696 | 102.442 | 18.0708 | 1.1294 | 0.20696 | 1.0244 | 0.18071 | 0.92247 | 0.84371 | 38.2396 | 102.541 | 16.7832
38897.6416 | 1632 | 256 | 38897.6416 | 1881 | 294 | 1224.5 | 1274.5 | 99.6337 | 15.6288 | 114.8352 | 17.9487 | 0.99634 | 0.15629 | 1.1484 | 0.17949 | 0.84005 | 0.96886 | 119.7241 | 31.3381 | 38.5293
38897.6417 | 2055 | 314 | 38897.6417 | 2055 | 348 | 1235 | 1285 | 125.4579 | 19.1697 | 125.4579 | 21.2454 | 1.2546 | 0.1917 | 1.2546 | 0.21245 | 1.0629 | 1.0421 | 45.3701 | 26.2113 | 4.4724
38897.6419 | 1930 | 282 | 38897.6419 | 1702 | 268 | 1245.5 | 1295.5 | 117.8266 | 17.2161 | 103.9072 | 16.3614 | 1.1783 | 0.17216 | 1.0391 | 0.16361 | 1.0061 | 0.87546 | 25.2013 | 161.7491 | 19.5861
38897.642 | 2074 | 123 | 38897.642 | 1753 | 113 | 1256.5 | 1306.5 | 126.6178 | 7.5092 | 107.0208 | 6.8987 | 1.2662 | 0.075092 | 1.0702 | 0.068987 | 1.1911 | 1.0012 | 12.7615 | 72.6788 | 35.7175
38897.6421 | 1848 | 217 | 38897.6421 | 1810 | 285 | 1267.5 | 1317.5 | 112.8205 | 13.2479 | 110.5006 | 17.3993 | 1.1282 | 0.13248 | 1.105 | 0.17399 | 0.99573 | 0.93101 | 34.2044 | 71.032 | 45.2405
38897.6422 | 1856 | 317 | 38897.6423 | 1868 | 318 | 1278.5 | 1328.5 | 113.3089 | 19.3529 | 114.0415 | 19.4139 | 1.1331 | 0.19353 | 1.1404 | 0.19414 | 0.93956 | 0.94628 | 52.5065 | 45.8914 | 12.7391
38897.6424 | 1750 | 329 | 38897.6424 | 2135 | 292 | 1288.5 | 1338.5 | 106.8376 | 20.0855 | 130.3419 | 17.8266 | 1.0684 | 0.20085 | 1.3034 | 0.17827 | 0.86752 | 1.1252 | 1.1704 | 0.72005 | 0.48322
38897.6425 | 1988 | 203 | 38897.6425 | 2041 | 175 | 1299.5 | 1349.5 | 121.3675 | 12.3932 | 124.6032 | 10.6838 | 1.2137 | 0.12393 | 1.246 | 0.10684 | 1.0897 | 1.1392 | 53.5854 | 16.9142 | 7.8664
38897.6426 | 2285 | 114 | 38897.6426 | 1789 | 88 | 1310.5 | 1360.5 | 139.4994 | 6.9597 | 109.2186 | 5.3724 | 1.395 | 0.069597 | 1.0922 | 0.053724 | 1.3254 | 1.0385 | 0.17847 | 1.627 | 1.3709
38897.6427 | 1945 | 360 | 38897.6428 | 1619 | 324 | 1321.5 | 1371.5 | 118.7424 | 21.978 | 98.84 | 19.7802 | 1.1874 | 0.21978 | 0.9884 | 0.1978 | 0.96764 | 0.7906 | 20.5642 | 243.2283 | 0.71259
38897.6429 | 1755 | 456 | 38897.6429 | 1545 | 384 | 1332.5 | 1382.5 | 107.1429 | 27.8388 | 94.3223 | 23.4432 | 1.0714 | 0.27839 | 0.94322 | 0.23443 | 0.79304 | 0.70879 | 52.5614 | 175.7285 | 12.6319
38897.643 | 1977 | 253 | 38897.643 | 1693 | 233 | 1342.5 | 1392.5 | 120.696 | 15.4457 | 103.3578 | 14.2247 | 1.207 | 0.15446 | 1.0336 | 0.14225 | 1.0525 | 0.89133 | 20.3685 | 192.4783 | 18.5671
38897.6431 | 1786 | 226 | 38897.6431 | 2114 | 257 | 1353.5 | 1403.5 | 109.0354 | 13.7973 | 129.0598 | 15.6899 | 1.0904 | 0.13797 | 1.2906 | 0.1569 | 0.95238 | 1.1337 | 30.2192 | 155.354 | 77.9004
38897.6432 | 1695 | 219 | 38897.6433 | 1906 | 240 | 1364.5 | 1414.5 | 103.4799 | 13.37 | 116.3614 | 14.652 | 1.0348 | 0.1337 | 1.1636 | 0.14652 | 0.9011 | 1.0171 | 85.5819 | 28.5356 | 39.2696
38897.6434 | 2146 | 232 | 38897.6434 | 2041 | 219 | 1375.5 | 1425.5 | 131.0134 | 14.1636 | 124.6032 | 13.37 | 1.3101 | 0.14164 | 1.246 | 0.1337 | 1.1685 | 1.1123 | 13.6792 | 29.8156 | 7.5853
38897.6435 | 2055 | 102 | 38897.6435 | 2205 | 117 | 1386.5 | 1436.5 | 125.4579 | 6.2271 | 134.6154 | 7.1429 | 1.2546 | 0.062271 | 1.3462 | 0.071429 | 1.1923 | 1.2747 | 47.7337 | 7.0989 | 9.3824
38897.6436 | 2077 | 103 | 38897.6436 | 1826 | 95 | 1397 | 1447 | 126.801 | 6.2882 | 111.4774 | 5.7998 | 1.268 | 0.062882 | 1.1148 | 0.057998 | 1.2051 | 1.0568 | 12.7457 | 48.2302 | 38.3435
38897.6437 | 1787 | 97 | 38897.6438 | 2019 | 113 | 1407.5 | 1457.5 | 109.0965 | 5.9219 | 123.2601 | 6.8987 | 1.091 | 0.059219 | 1.2326 | 0.068987 | 1.0317 | 1.1636 | 45.9361 | 17.0108 | 62.5545
38897.6439 | 1922 | 120 | 38897.6439 | 2109 | 121 | 1418.5 | 1468.5 | 117.3382 | 7.326 | 128.7546 | 7.3871 | 1.1734 | 0.07326 | 1.2875 | 0.073871 | 1.1001 | 1.2137 | 54.0799 | 10.9043 | 21.2522
38897.644 | 2216 | 184 | 38897.644 | 1804 | 143 | 1429.5 | 1479.5 | 135.2869 | 11.2332 | 110.1343 | 8.7302 | 1.3529 | 0.11233 | 1.1013 | 0.087302 | 1.2405 | 1.014 | 2.2912 | 10.8593 | 5.2502
38897.6441 | 2201 | 197 | 38897.6441 | 2174 | 158 | 1440.5 | 1490.5 | 134.3712 | 12.0269 | 132.7228 | 9.6459 | 1.3437 | 0.12027 | 1.3272 | 0.096459 | 1.2234 | 1.2308 | 12.9259 | 16.0499 | 6.7831
38897.6442 | 1838 | 348 | 38897.6442 | 2022 | 384 | 1450.5 | 1500.5 | 112.21 | 21.2454 | 123.4432 | 23.4432 | 1.1221 | 0.21245 | 1.2344 | 0.23443 | 0.90965 | 1 | 2.7141 | 2.2332 | 0.72425
38897.6444 | 2275 | 134 | 38897.6444 | 1796 | 106 | 1461.5 | 1511.5 | 138.8889 | 8.1807 | 109.6459 | 6.4713 | 1.3889 | 0.081807 | 1.0965 | 0.064713 | 1.3071 | 1.0317 | 0.10193 | 0.56446 | 0.4508
38897.6445 | 2252 | 79 | 38897.6445 | 1877 | 152 | 1472.5 | 1522.5 | 137.4847 | 4.823 | 114.591 | 9.2796 | 1.3748 | 0.04823 | 1.1459 | 0.092796 | 1.3266 | 1.0531 | 1.1385 | 3.6505 | 1.3205
38897.6446 | 2188 | 174 | 38897.6446 | 1773 | 153 | 1483.5 | 1533.5 | 133.5775 | 10.6227 | 108.2418 | 9.3407 | 1.3358 | 0.10623 | 1.0824 | 0.093407 | 1.2295 | 0.98901 | 4.255 | 26.7427 | 7.3511
38897.6447 | 1912 | 151 | 38897.6448 | 2177 | 175 | 1494.5 | 1544.5 | 116.7277 | 9.2186 | 132.906 | 10.6838 | 1.1673 | 0.092186 | 1.3291 | 0.10684 | 1.0751 | 1.2222 | 26.4278 | 52.4989 | 54.3471
38897.6449 | 1760 | 110 | 38897.6449 | 2059 | 138 | 1505 | 1555 | 107.4481 | 6.7155 | 125.7021 | 8.4249 | 1.0745 | 0.067155 | 1.257 | 0.084249 | 1.0073 | 1.1728 | 61.5213 | 14.2855 | 49.0198
38897.645 | 2180 | 158 | 38897.645 | 2184 | 112 | 1515.5 | 1565.5 | 133.0891 | 9.6459 | 133.3333 | 6.8376 | 1.3309 | 0.096459 | 1.3333 | 0.068376 | 1.2344 | 1.265 | 3.8301 | 13.7742 | 2.806
38897.6451 | 1986 | 178 | 38897.6451 | 1764 | 186 | 1526.5 | 1576.5 | 121.2454 | 10.8669 | 107.6923 | 11.3553 | 1.2125 | 0.10867 | 1.0769 | 0.11355 | 1.1038 | 0.96337 | 19.7439 | 84.5021 | 35.3484
38897.6452 | 2090 | 222 | 38897.6453 | 2144 | 198 | 1537.5 | 1587.5 | 127.5946 | 13.5531 | 130.8913 | 12.0879 | 1.2759 | 0.13553 | 1.3089 | 0.12088 | 1.1404 | 1.188 | 7.7442 | 25.7682 | 0.98013
38897.6454 | 1743 | 172 | 38897.6454 | 2190 | 170 | 1548.5 | 1598.5 | 106.4103 | 10.5006 | 133.6996 | 10.3785 | 1.0641 | 0.10501 | 1.337 | 0.10379 | 0.9591 | 1.2332 | 19.107 | 12.7277 | 25.3633
38897.6455 | 1956 | 198 | 38897.6455 | 2078 | 213 | 1558.5 | 1608.5 | 119.4139 | 12.0879 | 126.862 | 13.0037 | 1.1941 | 0.12088 | 1.2686 | 0.13004 | 1.0733 | 1.1386 | 149.2699 | 12.9698 | 8.5456
38897.6456 | 1657 | 203 | 38897.6456 | 1853 | 230 | 1569.5 | 1619.5 | 101.16 | 12.3932 | 113.1258 | 14.0415 | 1.0116 | 0.12393 | 1.1313 | 0.14042 | 0.88767 | 0.99084 | 75.118 | 34.0503 | 55.2294
38897.6457 | 1809 | 377 | 38897.6458 | 1942 | 465 | 1580.5 | 1630.5 | 110.4396 | 23.0159 | 118.5592 | 28.3883 | 1.1044 | 0.23016 | 1.1856 | 0.28388 | 0.87424 | 0.90171 | 3.902 | 3.3701 | 0.99778
38897.6459 | 1746 | 498 | 38897.6459 | 1572 | 441 | 1591.5 | 1641.5 | 106.5934 | 30.4029 | 95.9707 | 26.9231 | 1.0659 | 0.30403 | 0.95971 | 0.26923 | 0.7619 | 0.69048 | 53.4438 | 238.4888 | 8.1181
38897.646 | 1782 | 571 | 38897.646 | 1796 | 451 | 1602.5 | 1652.5 | 108.7912 | 34.8596 | 109.6459 | 27.5336 | 1.0879 | 0.3486 | 1.0965 | 0.27534 | 0.73932 | 0.82112 | 3.182 | 3.7786 | 0.32916
38897.6461 | 1708 | 559 | 38897.6461 | 1806 | 602 | 1612.5 | 1662.5 | 104.2735 | 34.127 | 110.2564 | 36.7521 | 1.0427 | 0.34127 | 1.1026 | 0.36752 | 0.70147 | 0.73504 | 40.9935 | 187.2704 | 4.0093
38897.6462 | 1704 | 640 | 38897.6462 | 1513 | 518 | 1623.5 | 1673.5 | 104.0293 | 39.072 | 92.3687 | 31.6239 | 1.0403 | 0.39072 | 0.92369 | 0.31624 | 0.64957 | 0.60745 | 69.0185 | 322.4766 | 5.0831
38897.6464 | 1696 | 615 | 38897.6464 | 1465 | 527 | 1634.5 | 1684.5 | 103.5409 | 37.5458 | 89.4383 | 32.1734 | 1.0354 | 0.37546 | 0.89438 | 0.32173 | 0.65995 | 0.57265 | 55.6819 | 9900.3958 | 1.5486
38897.6465 | 1727 | 693 | 38897.6465 | 1325 | 727 | 1645.5 | 1695.5 | 105.4335 | 42.3077 | 80.8913 | 44.3834 | 1.0543 | 0.42308 | 0.80891 | 0.44383 | 0.63126 | 0.36508 | 9.5776 | 13.9629 | 2.0972
38897.6466 | 1555 | 636 | 38897.6466 | 1703 | 770 | 1656.5 | 1706.5 | 94.9328 | 38.8278 | 103.9683 | 47.0085 | 0.94933 | 0.38828 | 1.0397 | 0.47009 | 0.56105 | 0.5696 | 99.136 | 382.8673 | 13.7611
38897.6467 | 1564 | 710 | 38897.6467 | 1362 | 597 | 1666.5 | 1716.5 | 95.4823 | 43.3455 | 83.1502 | 36.4469 | 0.95482 | 0.43346 | 0.8315 | 0.36447 | 0.52137 | 0.46703 | 103.7554 | 495.432 | 3.2087
38897.6469 | 1400 | 881 | 38897.6469 | 1399 | 731 | 1677.5 | 1727.5 | 85.4701 | 53.7851 | 85.409 | 44.6276 | 0.8547 | 0.53785 | 0.85409 | 0.44628 | 0.31685 | 0.40781 | 140.944 | 730.9339 | 2.0349

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 2 |  |  | 2006-06-29 | 15:03
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-48.3333 | 231938 |  | -45.6667 | 230238 | -44.6667 | 230038 | -43.3333 | 193981.6667 | -48.3333 | 193981.6667
-37.5 | 231938 |  | -35.1667 | 230238 | -33.8333 | 230038 | -32.8333 | 232404.6667 | -37.5 | 230038
-26.5 | 231938 |  | -24.5 | 230238 | -23.1667 | 230038 | -21.8333 | 232404.6667 | -26.5 | 230038
-15.8333 | 231938 |  | -13.5 | 230238 | -12.1667 | 230038 | -11.1667 | 232404.6667 | -15.8333 | 230038
-5.1667 | 170567.8667 |  | -2.5 | 230238 | -1.5 | 191615 | -0.16667 | 232404.6667 | -5.1667 | 170567.8667
5.3333 | 176393571.48 |  | 8.1667 | 230238 | 9 | 230038 | 10.5 | 232404.6667 | 5.3333 | 230038
16.5 | 231938 |  | 18.8333 | 230238 | 20.1667 | 191615 | 21.1667 | 232404.6667 | 16.5 | 191615
27.5 | 231938 |  | 29.5 | 191931.6667 | 30.8333 | 230038 | 32.1667 | 232404.6667 | 27.5 | 191931.6667
38.1667 | 231938 |  | 40.5 | 176085487.48 | 41.8333 | 230038 | 42.8333 | 232404.6667 | 38.1667 | 230038
49 | 176393571.48 |  | 51.5 | 176085487.48 | 52.6667 | 230038 | 53.8333 | 232404.6667 | 49 | 230038
59.6667 | 231971.3914 |  | 62.3333 | 230238 | 63.1667 | 191698.3333 | 64.5 | 232404.6667 | 59.6667 | 191698.3333
70.5 | 361866791.6267 |  | 73 | 230238 | 74.1667 | 191615 | 75.3333 | 193981.6667 | 70.5 | 191615
81.5 | 154308.7247 |  | 83.6667 | 115069 | 85 | 114969 | 86.1667 | 232404.6667 | 81.5 | 114969
92.1667 | 193581.6667 |  | 94.5 | 191731.6667 | 95.8333 | 230038 | 96.8333 | 232404.6667 | 92.1667 | 191731.6667
102.8333 | 231938 |  | 105.5 | 230238 | 106.5 | 230038 | 107.8333 | 232404.6667 | 102.8333 | 230038
113.5 | 231938 |  | 116.1667 | 230238 | 117.1667 | 191615 | 118.5 | 232404.6667 | 113.5 | 191615
124.5 | 185475170.1467 |  | 126.8333 | 191731.6667 | 128.1667 | 114969 | 129.1667 | 232404.6667 | 124.5 | 114969
135.5 | 193598.3333 |  | 137.5 | 191931.6667 | 138.8333 | 191615 | 140.1667 | 193081.6667 | 135.5 | 191615
146.1667 | 231938 |  | 148.5 | 191731.6667 | 149.8333 | 230038 | 150.8333 | 232404.6667 | 146.1667 | 191731.6667
156.8333 | 231938 |  | 159.5 | 230238 | 160.5 | 230038 | 161.8333 | 193898.3333 | 156.8333 | 193898.3333
167.5 | 154258.6667 |  | 170.1667 | 191931.6667 | 171.3333 | 191731.6667 | 172.6667 | 232404.6667 | 167.5 | 154258.6667
178.5 | 231938 |  | 180.8333 | 230238 | 182 | 230038 | 183 | 232404.6667 | 178.5 | 230038
189.5 | 231938 |  | 191.5 | 153375.3333 | 192.8333 | 153308.6667 | 194.1667 | 232404.6667 | 189.5 | 153308.6667
200.1667 | 231938 |  | 202.5 | 176046981.1467 | 203.8333 | 230038 | 204.8333 | 232404.6667 | 200.1667 | 230038
210.8333 | 193581.6667 |  | 213.5 | 153375.3333 | 214.5 | 191731.6667 | 215.8333 | 193898.3333 | 210.8333 | 153375.3333
221.5 | 231938 |  | 224.1667 | 191931.6667 | 225.1667 | 191615 | 226.5 | 193081.6667 | 221.5 | 191615
232.5 | 231938 |  | 235 | 230238 | 236.1667 | 230038 | 237.3333 | 193981.6667 | 232.5 | 193981.6667
243.5 | 231938 |  | 245.5 | 191931.6667 | 246.8333 | 230038 | 248.1667 | 232404.6667 | 243.5 | 191931.6667
254.1667 | 231938 |  | 256.5 | 191931.6667 | 257.8333 | 191731.6667 | 258.8333 | 232404.6667 | 254.1667 | 191731.6667
264.8333 | 231938 |  | 267.5 | 230238 | 268.5 | 191698.3333 | 269.8333 | 193981.6667 | 264.8333 | 191698.3333
275.5 | 231938 |  | 278.1667 | 230238 | 279.1667 | 230038 | 280.5 | 232404.6667 | 275.5 | 230038
286.5 | 231938 |  | 288.8333 | 153375.3333 | 290.1667 | 230038 | 291.1667 | 232404.6667 | 286.5 | 153375.3333
297.5 | 193598.3333 |  | 299.5 | 191731.6667 | 300.8333 | 230038 | 302.1667 | 193081.6667 | 297.5 | 191731.6667
308.1667 | 193581.6667 |  | 310.5 | 230238 | 311.8333 | 230038 | 312.8333 | 232404.6667 | 308.1667 | 193581.6667
318.8333 | 231938 |  | 321.5 | 191931.6667 | 322.5 | 191615 | 323.8333 | 193898.3333 | 318.8333 | 191615
329.5 | 231938 |  | 332.1667 | 230238 | 333.1667 | 230038 | 334.5 | 193081.6667 | 329.5 | 193081.6667
340.5 | 192615 |  | 342.8333 | 230238 | 344.1667 | 230038 | 345.1667 | 232404.6667 | 340.5 | 192615
351.5 | 231938 |  | 353.6667 | 140806.5556 | 355 | 230038 | 356.1667 | 193898.3333 | 351.5 | 140806.5556
362.3333 | 231938 |  | 364.5 | 230238 | 365.8333 | 230038 | 367 | 232404.6667 | 362.3333 | 230038
372.8333 | 192615 |  | 375.5 | 230238 | 376.5 | 230038 | 377.8333 | 193981.6667 | 372.8333 | 192615
383.5 | 231938 |  | 386.1667 | 230238 | 387.1667 | 230038 | 388.5 | 232404.6667 | 383.5 | 230038
394.5 | 193581.6667 |  | 396.8333 | 230238 | 398.1667 | 230038 | 399.1667 | 232404.6667 | 394.5 | 193581.6667
405.5 | 155242 |  | 407.5 | 191931.6667 | 408.8333 | 230038 | 410.1667 | 232404.6667 | 405.5 | 155242
416.3333 | 231938 |  | 418.5 | 230238 | 419.8333 | 230038 | 421 | 232404.6667 | 416.3333 | 230038
426.8333 | 231938 |  | 429.5 | 230238 | 430.5 | 191698.3333 | 431.8333 | 232404.6667 | 426.8333 | 191698.3333
437.5 | 193598.3333 |  | 440.1667 | 230238 | 441.1667 | 230038 | 442.5 | 193981.6667 | 437.5 | 193598.3333
448.5 | 193581.6667 |  | 450.8333 | 230238 | 452.1667 | 230038 | 453.1667 | 232404.6667 | 448.5 | 193581.6667
459.5 | 231938 |  | 461.5 | 230238 | 462.8333 | 230038 | 464.1667 | 232404.6667 | 459.5 | 230038
470.3333 | 231938 |  | 472.5 | 230238 | 473.8333 | 191731.6667 | 475 | 232404.6667 | 470.3333 | 191731.6667
480.8333 | 192615 |  | 483.5 | 191881.6667 | 484.5 | 230038 | 485.8333 | 193081.6667 | 480.8333 | 191881.6667
491.5 | 231938 |  | 494.1667 | 230238 | 495.1667 | 230038 | 496.5 | 232404.6667 | 491.5 | 230038
502.5 | 193598.3333 |  | 504.8333 | 230238 | 506.1667 | 177158798.1467 | 507.1667 | 232404.6667 | 502.5 | 193598.3333
513.5 | 231938 |  | 515.5 | 191731.6667 | 516.8333 | 230038 | 518.1667 | 232404.6667 | 513.5 | 191731.6667
524.3333 | 231938 |  | 526.5 | 230238 | 527.8333 | 191615 | 529 | 193981.6667 | 524.3333 | 191615
534.8333 | 231938 |  | 537.5 | 230238 | 538.3333 | 230038 | 539.6667 | 232404.6667 | 534.8333 | 230038
545.5 | 231938 |  | 548.1667 | 230238 | 549.1667 | 153308.6667 | 550.5 | 193898.3333 | 545.5 | 153308.6667
556.5 | 231938 |  | 558.8333 | 191731.6667 | 560.1667 | 230038 | 561.1667 | 232404.6667 | 556.5 | 191731.6667
567.5 | 192615 |  | 569.5 | 230238 | 570.8333 | 230038 | 572.1667 | 232404.6667 | 567.5 | 192615
578.1667 | 193598.3333 |  | 580.5 | 230238 | 581.8333 | 230038 | 582.8333 | 232404.6667 | 578.1667 | 193598.3333
588.8333 | 231938 |  | 591.5 | 230238 | 592.3333 | 230038 | 593.6667 | 232404.6667 | 588.8333 | 230038
599.5 | 231938 |  | 602 | 230238 | 603.1667 | 230038 | 604.3333 | 232404.6667 | 599.5 | 230038
610.5 | 231938 |  | 612.8333 | 230238 | 614.1667 | 230038 | 615.1667 | 232404.6667 | 610.5 | 230038
621.5 | 231938 |  | 623.5 | 230238 | 624.8333 | 230038 | 626.1667 | 232404.6667 | 621.5 | 230038
632.1667 | 231938 |  | 634.5 | 230238 | 635.8333 | 230038 | 636.8333 | 232404.6667 | 632.1667 | 230038
642.8333 | 231938 |  | 645.5 | 230238 | 646.5 | 230038 | 647.8333 | 232404.6667 | 642.8333 | 230038
653.5 | 231938 |  | 656.1667 | 230238 | 657.1667 | 230038 | 658.5 | 232404.6667 | 653.5 | 230038
664.5 | 231938 |  | 666.8333 | 230238 | 668.1667 | 230038 | 669.1667 | 232404.6667 | 664.5 | 230038
675.5 | 231938 |  | 677.5 | 230238 | 678.8333 | 230038 | 680.1667 | 232404.6667 | 675.5 | 230038
686.1667 | 193581.6667 |  | 688.5 | 191931.6667 | 689.8333 | 230038 | 690.8333 | 232404.6667 | 686.1667 | 191931.6667
696.6667 | 231938 |  | 699.3333 | 191731.6667 | 700.3333 | 230038 | 701.6667 | 193898.3333 | 696.6667 | 191731.6667
707.5 | 231938 |  | 710 | 230238 | 711.1667 | 230038 | 712.3333 | 232404.6667 | 707.5 | 230038
718.5 | 231938 |  | 720.6667 | 230238 | 722 | 230038 | 723.1667 | 232404.6667 | 718.5 | 230038
729.5 | 231938 |  | 731.5 | 191731.6667 | 732.8333 | 230038 | 734.1667 | 232404.6667 | 729.5 | 191731.6667
740.1667 | 231938 |  | 742.5 | 230238 | 743.8333 | 230038 | 744.8333 | 232404.6667 | 740.1667 | 230038
750.8333 | 231938 |  | 753.5 | 230238 | 754.3333 | 230038 | 755.6667 | 232404.6667 | 750.8333 | 230038
761.5 | 231938 |  | 764 | 230238 | 765.1667 | 230038 | 766.3333 | 232404.6667 | 761.5 | 230038
772.5 | 231938 |  | 774.6667 | 230238 | 776 | 230038 | 777.1667 | 232404.6667 | 772.5 | 230038
783.5 | 231938 |  | 785.5 | 230238 | 786.8333 | 230038 | 788.1667 | 232404.6667 | 783.5 | 230038
794.1667 | 192615 |  | 796.5 | 230238 | 797.8333 | 230038 | 798.8333 | 232404.6667 | 794.1667 | 192615
804.8333 | 231938 |  | 807.5 | 191881.6667 | 808.5 | 191615 | 809.8333 | 232404.6667 | 804.8333 | 191615
815.5 | 231938 |  | 818 | 230238 | 819.1667 | 230038 | 820.3333 | 232404.6667 | 815.5 | 230038
826.5 | 231938 |  | 828.6667 | 230238 | 830 | 230038 | 831.1667 | 232404.6667 | 826.5 | 230038
837.3333 | 193598.3333 |  | 839.5 | 178986.2016 | 840.8333 | 230038 | 842 | 160520.8315 | 837.3333 | 160520.8315
848 | 231938 |  | 850.5 | 157447.4243 | 851.6667 | 3058524.158 | 852.8333 | 82238.6857 | 848 | 82238.6857
858.6667 | 58901340.7156 |  | 861.3333 | 27914.2885 | 862.3333 | 125204.4998 | 863.6667 | 8645.5855 | 858.6667 | 8645.5855
869.5 | 10526.4064 |  | 872 | 2094.551 | 873.1667 | 139371.7714 | 874.3333 | 1964.0718 | 869.5 | 1964.0718
880.5 | 6556.7647 |  | 882.6667 | 3087.0513 | 884 | 15949.0846 | 885.1667 | 48830.4714 | 880.5 | 3087.0513
891.3333 | 4025.5069 |  | 893.5 | 26109.7879 | 894.8333 | 7566.2296 | 896 | 1680.4613 | 891.3333 | 1680.4613
902 | 3952.4001 |  | 904.5 | 2684.2623 | 905.6667 | 4032.5457 | 906.8333 | 1362.6104 | 902 | 1362.6104
912.6667 | 3981.2845 |  | 915.3333 | 1059.4302 | 916.3333 | 4462.1982 | 917.6667 | 1053.8454 | 912.6667 | 1053.8454
923.5 | 3013.0909 |  | 926 | 2298.9066 | 927.1667 | 4279.6448 | 928.3333 | 1169.6467 | 923.5 | 1169.6467
934.5 | 3087.7067 |  | 936.6667 | 885.021 | 938 | 7803.4473 | 939.1667 | 5286.7073 | 934.5 | 885.021
945.3333 | 1576.0008 |  | 947.5 | 1866.1986 | 948.8333 | 1457.7015 | 950 | 1474.4202 | 945.3333 | 1457.7015
956 | 3743.6134 |  | 958.5 | 1392.9419 | 959.6667 | 1471.7027 | 960.8333 | 1420.8582 | 956 | 1392.9419
966.6667 | 3825.5166 |  | 969.3333 | 10000.6954 | 970.3333 | 1264.9843 | 971.6667 | 908.4115 | 966.6667 | 908.4115
977.5 | 1794.9371 |  | 980 | 778.8369 | 981.1667 | 1667.5474 | 982.3333 | 1055.4513 | 977.5 | 778.8369
988.5 | 1614.3135 |  | 990.6667 | 848.0043 | 992 | 2346.6453 | 993.1667 | 818.6358 | 988.5 | 818.6358
999.3333 | 674.3854 |  | 1001.5 | 7891.7598 | 1002.8333 | 1599.9422 | 1004 | 957.0885 | 999.3333 | 674.3854
1010 | 929.5926 |  | 1012.5 | 1123.3359 | 1013.6667 | 2595.2536 | 1014.8333 | 843.4973 | 1010 | 843.4973
1020.6667 | 1214.6837 |  | 1023.3333 | 663.7352 | 1024.3333 | 1668.2581 | 1025.6667 | 3559.6279 | 1020.6667 | 663.7352
1031.5 | 1030.8153 |  | 1034 | 518.4143 | 1035.1667 | 1186.8652 | 1036.3333 | 1331.5548 | 1031.5 | 518.4143
1042.5 | 1541.3217 |  | 1044.6667 | 914.3593 | 1046 | 568.5216 | 1047.1667 | 873.1319 | 1042.5 | 568.5216
1053.3333 | 1079.3968 |  | 1055.5 | 337.0502 | 1056.8333 | 1268.2594 | 1058 | 906.6702 | 1053.3333 | 337.0502
1064 | 2917.0935 |  | 1066.5 | 196.6106 | 1067.6667 | 648.2352 | 1068.8333 | 555.9242 | 1064 | 196.6106
1074.6667 | 893.8513 |  | 1077.3333 | 796.7569 | 1078.3333 | 266.3311 | 1079.6667 | 1229.5956 | 1074.6667 | 266.3311
1085.5 | 165.8031 |  | 1088 | 3377.5815 | 1089.1667 | 289.2893 | 1090.3333 | 263.8566 | 1085.5 | 165.8031
1096.5 | 202.1078 |  | 1098.6667 | 183.1116 | 1100 | 1693.7169 | 1101.1667 | 468.7213 | 1096.5 | 183.1116
1107.3333 | 314.8734 |  | 1109.5 | 160.0185 | 1110.8333 | 251.1927 | 1112 | 143.0122 | 1107.3333 | 143.0122
1118 | 198.4868 |  | 1120.5 | 209.7596 | 1121.6667 | 52.8057 | 1122.8333 | 189.5157 | 1118 | 52.8057
1128.6667 | 395.5195 |  | 1131.3333 | 61.7702 | 1132.1667 | 31.2229 | 1133.5 | 54.6158 | 1128.6667 | 31.2229
1139.5 | 30.1377 |  | 1141.8333 | 26.8793 | 1143.3333 | 37.4087 | 1144.3333 | 57.1221 | 1139.5 | 26.8793
1150.5 | 115.8641 |  | 1152.6667 | 198.9084 | 1154 | 159.4801 | 1155.1667 | 131.9018 | 1150.5 | 115.8641
1161.3333 | 144.8164 |  | 1163.5 | 241.6099 | 1164.8333 | 59.2448 | 1166 | 75.0716 | 1161.3333 | 59.2448
1172 | 65.7539 |  | 1174.5 | 1523.4308 | 1175.6667 | 187.1239 | 1176.8333 | 60.5986 | 1172 | 60.5986
1182.5 | 60.4387 |  | 1185.1667 | 118.5531 | 1186.1667 | 47.4605 | 1187.5 | 46.9501 | 1182.5 | 46.9501
1193.5 | 15.411 |  | 1195.8333 | 2935.944 | 1197.1667 | 42.2897 | 1198.1667 | 68.3817 | 1193.5 | 15.411
1204.5 | 52.488 |  | 1206.6667 | 62.3605 | 1208 | 119.0305 | 1209.1667 | 78.0386 | 1204.5 | 52.488
1215.3333 | 49.2005 |  | 1217.5 | 54.4704 | 1218.8333 | 28.8033 | 1220 | 73.5207 | 1215.3333 | 28.8033
1226 | 84.2365 |  | 1228.5 | 36.0124 | 1229.6667 | 51.2513 | 1230.8333 | 63.6648 | 1226 | 36.0124
1236.6667 | 117.9795 |  | 1239.3333 | 38.4323 | 1240.3333 | 44.192 | 1241.6667 | 144.1901 | 1236.6667 | 38.4323
1247.5 | 71.4504 |  | 1250 | 252.6258 | 1251.1667 | 22.389 | 1252.3333 | 24.1157 | 1247.5 | 22.389
1258.5 | 109.3961 |  | 1260.6667 | 58.6884 | 1262 | 14.9289 | 1263.1667 | 7.5004 | 1258.5 | 7.5004
1269.1667 | 44.9497 |  | 1271.5 | 39.2641 | 1272.8333 | 103.2854 | 1273.8333 | 118.9181 | 1269.1667 | 39.2641
1279.8333 | 880.564 |  | 1282.5 | 59.3207 | 1283.5 | 29.0951 | 1284.8333 | 1374.7456 | 1279.8333 | 29.0951
1290.5 | 48.7062 |  | 1293.1667 | 17.2729 | 1294.3333 | 166.3289 | 1295.6667 | 118.4359 | 1290.5 | 17.2729
1301.5 | 80.8862 |  | 1304 | 20.044 | 1305.1667 | 10.9241 | 1306.3333 | 156.4092 | 1301.5 | 10.9241
1312.5 | 14.3831 |  | 1314.5 | 5.4817 | 1315.8333 | 66.9011 | 1317.1667 | 63.3427 | 1312.5 | 5.4817
1323.1667 | 25.6564 |  | 1325.6667 | 98.3692 | 1327 | 115.0646 | 1327.8333 | 939.6473 | 1323.1667 | 25.6564
1333.8333 | 84.8132 |  | 1336.5 | 86.9086 | 1337.5 | 48.0598 | 1338.8333 | 2410.4673 | 1333.8333 | 48.0598
1344.5 | 37.6601 |  | 1347.1667 | 74.9626 | 1348.1667 | 38.3978 | 1349.5 | 43.6147 | 1344.5 | 37.6601
1355.5 | 75.1894 |  | 1357.8333 | 89.0557 | 1359.1667 | 67.9623 | 1360.1667 | 20.6278 | 1355.5 | 20.6278
1366.5 | 34.0944 |  | 1368.6667 | 25.3037 | 1370 | 31.7007 | 1371.1667 | 195.3141 | 1366.5 | 25.3037
1377.3333 | 32.3633 |  | 1379.5 | 13.2742 | 1380.8333 | 16.2514 | 1382 | 14.0356 | 1377.3333 | 13.2742
1388 | 28.7393 |  | 1390.5 | 19.398 | 1391.6667 | 13.2633 | 1392.8333 | 13.9022 | 1388 | 13.2633
1398.6667 | 26.7801 |  | 1401.3333 | 21.286 | 1402.3333 | 15.6311 | 1403.6667 | 37.2135 | 1398.6667 | 15.6311
1409.5 | 34.5014 |  | 1411.8333 | 26.8196 | 1413.1667 | 18.6257 | 1414.1667 | 20.6052 | 1409.5 | 18.6257
1420.5 | 36.0071 |  | 1422.5 | 14.8751 | 1423.8333 | 21.9611 | 1425.1667 | 29.1562 | 1420.5 | 14.8751
1431.1667 | 8.8487 |  | 1433.5 | 45.8554 | 1434.8333 | 31.1447 | 1435.8333 | 41.4937 | 1431.1667 | 8.8487
1441.8333 | 62.937 |  | 1444.5 | 75.4539 | 1445.5 | 35.3438 | 1446.8333 | 61.4283 | 1441.8333 | 35.3438
1452.5 | 41.1126 |  | 1455.1667 | 70.7301 | 1456.1667 | 17.9313 | 1457.5 | 43.7158 | 1452.5 | 17.9313
1463.5 | 23.5625 |  | 1465.8333 | 16.1891 | 1467.1667 | 32.3292 | 1468.1667 | 24.0364 | 1463.5 | 16.1891
1474.5 | 7.9089 |  | 1476.5 | 28.7682 | 1477.8333 | 50.5428 | 1479.1667 | 7.681 | 1474.5 | 7.681
1485.3333 | 9.4614 |  | 1487.5 | 64.2965 | 1488.8333 | 54.6896 | 1490 | 36.6547 | 1485.3333 | 9.4614
1496 | 10.5941 |  | 1498.5 | 25.9094 | 1499.6667 | 26.9694 | 1500.8333 | 14.2928 | 1496 | 10.5941
1506.6667 | 23.1857 |  | 1509.3333 | 67.3177 | 1510.1667 | 1.7092 | 1511.5 | 9.7731 | 1506.6667 | 1.7092
1517.5 | 9.3251 |  | 1519.8333 | 36.7104 | 1521.1667 | 60.4102 | 1522.1667 | 69.1053 | 1517.5 | 9.3251
1528.5 | 30.0687 |  | 1530.5 | 63.26 | 1531.8333 | 51.5799 | 1533.1667 | 21.1976 | 1528.5 | 21.1976
1539.1667 | 14.8268 |  | 1541.5 | 17.8016 | 1542.8333 | 365.7619 | 1543.8333 | 39.7152 | 1539.1667 | 14.8268
1549.8333 | 53.4162 |  | 1552.5 | 28.2343 | 1553.5 | 17.6632 | 1554.8333 | 18.312 | 1549.8333 | 17.6632
1560.5 | 118.8237 |  | 1563.1667 | 34.5324 | 1564.1667 | 89.8176 | 1565.5 | 28.6069 | 1560.5 | 28.6069
1571.5 | 39.4817 |  | 1573.8333 | 87.1356 | 1575.1667 | 36.4586 | 1576.1667 | 115.6616 | 1571.5 | 36.4586
1582.5 | 79.9094 |  | 1584.5 | 1132.8201 | 1585.8333 | 45.7873 | 1587.1667 | 120.9204 | 1582.5 | 45.7873
1593.1667 | 146.4888 |  | 1595.5 | 208.1511 | 1596.8333 | 41.5099 | 1597.8333 | 56.014 | 1593.1667 | 41.5099
1603.8333 | 90.311 |  | 1606.5 | 98.3837 | 1607.5 | 25.659 | 1608.8333 | 150.3474 | 1603.8333 | 25.659
1614.5 | 273.9166 |  | 1617.1667 | 155.9043 | 1618.1667 | 78.2024 | 1619.5 | 130.8222 | 1614.5 | 78.2024
1625.5 | 160.0918 |  | 1627.8333 | 148.2215 | 1629.1667 | 195.4656 | 1630.1667 | 124.9078 | 1625.5 | 124.9078
1636.5 | 76.4167 |  | 1638.5 | 3330.9344 | 1639.8333 | 53.3124 | 1641.1667 | 85.129 | 1636.5 | 53.3124
1647.1667 | 13479.692 |  | 1649.6667 | 36.729 | 1650.8333 | 34.0502 | 1652 | 2374.0556 | 1647.1667 | 34.0502
1657.8333 | 137.7439 |  | 1660.5 | 144.3034 | 1661.5 | 136.2719 | 1662.8333 | 621.4968 | 1657.8333 | 136.2719
1668.5 | 389.9715 |  | 1671.1667 | 477.0233 | 1672.1667 | 128.5304 | 1673.5 | 300.4228 | 1668.5 | 128.5304
1679.5 | 417.6551 |  | 1681.8333 | 474.7077 | 1683.1667 | 513.0963 | 1684.1667 | 165.1442 | 1679.5 | 165.1442
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 2 |  |  | 2006-06-29 | 15:03
38897.6269 | 1 | 0 | 1 | XLPE | 3-C | Tray
38897.627 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38897.6271 | 1 | 0 | 1
38897.6272 | 1 | 0 | 1
38897.6274 | 5 | 0 | 1
38897.6275 | 1 | 0 | 1
38897.6276 | 1 | 0 | 1
38897.6277 | 1 | 0 | 1
38897.6279 | 1 | 0 | 1
38897.628 | 1 | 0 | 1
38897.6281 | 1 | 0 | 1
38897.6282 | 1 | 1 | 1
38897.6284 | 2 | 1 | 1
38897.6285 | 2 | 0 | 1
38897.6286 | 1 | 0 | 1
38897.6287 | 1 | 0 | 1
38897.6289 | 2 | 0 | 1
38897.629 | 1 | 0 | 1
38897.6291 | 1 | 0 | 1
38897.6292 | 1 | 0 | 1
38897.6294 | 2 | 0 | 1
38897.6295 | 1 | 0 | 1
38897.6296 | 1 | 0 | 1
38897.6297 | 1 | 0 | 1
38897.6299 | 2 | 0 | 1
38897.63 | 1 | 0 | 1
38897.6301 | 1 | 0 | 1
38897.6302 | 1 | 0 | 1
38897.6304 | 1 | 0 | 1
38897.6305 | 1 | 0 | 1
38897.6306 | 1 | 0 | 1
38897.6307 | 1 | 0 | 1
38897.6309 | 1 | 0 | 1
38897.631 | 2 | 0 | 1
38897.6311 | 1 | 0 | 1
38897.6312 | 1 | 0 | 1
38897.6314 | 1 | 0 | 1
38897.6315 | 1 | 0 | 1
38897.6316 | 1 | 0 | 1
38897.6317 | 1 | 0 | 1
38897.6319 | 1 | 0 | 1
38897.632 | 2 | 0 | 1
38897.6321 | 2 | 0 | 1
38897.6322 | 1 | 0 | 1
38897.6324 | 1 | 0 | 1
38897.6325 | 1 | 0 | 1
38897.6326 | 2 | 0 | 1
38897.6327 | 1 | 0 | 1
38897.6329 | 1 | 0 | 1
38897.633 | 1 | 0 | 1
38897.6331 | 1 | 0 | 1
38897.6332 | 1 | 0 | 1
38897.6334 | 1 | 0 | 1
38897.6335 | 1 | 0 | 1
38897.6336 | 1 | 0 | 1
38897.6337 | 1 | 0 | 1
38897.6339 | 1 | 0 | 1
38897.634 | 1 | 0 | 1
38897.6341 | 1 | 0 | 1
38897.6342 | 1 | 0 | 1
38897.6344 | 1 | 0 | 1
38897.6345 | 1 | 0 | 1
38897.6346 | 1 | 0 | 1
38897.6347 | 1 | 0 | 1
38897.6349 | 1 | 0 | 1
38897.635 | 1 | 0 | 1
38897.6351 | 1 | 0 | 1
38897.6352 | 1 | 0 | 1
38897.6354 | 2 | 0 | 1
38897.6355 | 1 | 0 | 1
38897.6356 | 1 | 0 | 1
38897.6357 | 1 | 0 | 1
38897.6359 | 1 | 0 | 1
38897.636 | 1 | 0 | 1
38897.6361 | 1 | 0 | 1
38897.6362 | 1 | 0 | 1
38897.6364 | 1 | 0 | 1
38897.6365 | 1 | 0 | 1
38897.6366 | 1 | 0 | 1
38897.6367 | 1 | 0 | 1
38897.6369 | 1 | 0 | 1
38897.637 | 1 | 0 | 1
38897.6371 | 1 | 0 | 1
38897.6372 | 1 | 0 | 1
38897.6374 | 1 | 1 | 1
38897.6375 | 47 | 23 | 1
38897.6376 | 129 | 88 | 1
38897.6377 | 155 | 100 | 1
38897.6379 | 135 | 82 | 1
38897.638 | 258 | 196 | 1
38897.6381 | 407 | 308 | 1
38897.6382 | 341 | 279 | 1
38897.6384 | 1006 | 1000 | 1
38897.6385 | 778 | 713 | 1
38897.6386 | 378 | 307 | 1
38897.6387 | 953 | 907 | 1
38897.6389 | 1004 | 842 | 1
38897.639 | 1000 | 960 | 1
38897.6391 | 1047 | 869 | 1
38897.6392 | 1030 | 849 | 1
38897.6394 | 723 | 580 | 1
38897.6395 | 1276 | 923 | 1
38897.6396 | 1259 | 904 | 1
38897.6397 | 1139 | 728 | 1
38897.6399 | 1376 | 825 | 1
38897.64 | 1470 | 762 | 1
38897.6401 | 1260 | 624 | 1
38897.6402 | 1225 | 627 | 1
38897.6404 | 1639 | 537 | 1
38897.6405 | 1722 | 316 | 1
38897.6406 | 1994 | 200 | 1
38897.6407 | 2106 | 249 | 1
38897.6409 | 1436 | 530 | 1
38897.641 | 2044 | 311 | 1
38897.6411 | 1889 | 347 | 1
38897.6412 | 2095 | 280 | 1
38897.6414 | 1600 | 254 | 1
38897.6415 | 1850 | 339 | 1
38897.6416 | 1632 | 256 | 1
38897.6417 | 2055 | 314 | 1
38897.6419 | 1930 | 282 | 1
38897.642 | 2074 | 123 | 1
38897.6421 | 1848 | 217 | 1
38897.6422 | 1856 | 317 | 1
38897.6424 | 1750 | 329 | 1
38897.6425 | 1988 | 203 | 1
38897.6426 | 2285 | 114 | 1
38897.6427 | 1945 | 360 | 1
38897.6429 | 1755 | 456 | 1
38897.643 | 1977 | 253 | 1
38897.6431 | 1786 | 226 | 1
38897.6432 | 1695 | 219 | 1
38897.6434 | 2146 | 232 | 1
38897.6435 | 2055 | 102 | 1
38897.6436 | 2077 | 103 | 1
38897.6437 | 1787 | 97 | 1
38897.6439 | 1922 | 120 | 1
38897.644 | 2216 | 184 | 1
38897.6441 | 2201 | 197 | 1
38897.6442 | 1838 | 348 | 1
38897.6444 | 2275 | 134 | 1
38897.6445 | 2252 | 79 | 1
38897.6446 | 2188 | 174 | 1
38897.6447 | 1912 | 151 | 1
38897.6449 | 1760 | 110 | 1
38897.645 | 2180 | 158 | 1
38897.6451 | 1986 | 178 | 1
38897.6452 | 2090 | 222 | 1
38897.6454 | 1743 | 172 | 1
38897.6455 | 1956 | 198 | 1
38897.6456 | 1657 | 203 | 1
38897.6457 | 1809 | 377 | 1
38897.6459 | 1746 | 498 | 1
38897.646 | 1782 | 571 | 1
38897.6461 | 1708 | 559 | 1
38897.6462 | 1704 | 640 | 1
38897.6464 | 1696 | 615 | 1
38897.6465 | 1727 | 693 | 1
38897.6466 | 1555 | 636 | 1
38897.6467 | 1564 | 710 | 1
38897.6469 | 1400 | 881 | 1
38897.6269 | 1 | 0 | 2
38897.627 | 1 | 0 | 2
38897.6271 | 1 | 0 | 2
38897.6273 | 1 | 0 | 2
38897.6274 | 1 | 0 | 2
38897.6275 | 1 | 0 | 2
38897.6276 | 1 | 0 | 2
38897.6278 | 1 | 0 | 2
38897.6279 | 1 | 0 | 2
38897.628 | 1 | 0 | 2
38897.6281 | 1 | 0 | 2
38897.6283 | 1 | 0 | 2
38897.6284 | 2 | 0 | 2
38897.6285 | 1 | 0 | 2
38897.6286 | 1 | 0 | 2
38897.6288 | 1 | 0 | 2
38897.6289 | 1 | 0 | 2
38897.629 | 1 | 0 | 2
38897.6291 | 1 | 0 | 2
38897.6293 | 1 | 0 | 2
38897.6294 | 1 | 0 | 2
38897.6295 | 1 | 0 | 2
38897.6296 | 2 | 0 | 2
38897.6298 | 1 | 0 | 2
38897.6299 | 2 | 0 | 2
38897.63 | 1 | 0 | 2
38897.6301 | 1 | 0 | 2
38897.6303 | 1 | 0 | 2
38897.6304 | 1 | 0 | 2
38897.6305 | 1 | 0 | 2
38897.6306 | 1 | 0 | 2
38897.6308 | 2 | 0 | 2
38897.6309 | 1 | 0 | 2
38897.631 | 1 | 0 | 2
38897.6311 | 1 | 0 | 2
38897.6312 | 1 | 0 | 2
38897.6314 | 1 | 0 | 2
38897.6315 | 2 | 0 | 2
38897.6316 | 1 | 0 | 2
38897.6318 | 1 | 0 | 2
38897.6319 | 1 | 0 | 2
38897.632 | 1 | 0 | 2
38897.6321 | 1 | 0 | 2
38897.6323 | 1 | 0 | 2
38897.6324 | 1 | 0 | 2
38897.6325 | 1 | 0 | 2
38897.6326 | 1 | 0 | 2
38897.6328 | 1 | 0 | 2
38897.6329 | 1 | 0 | 2
38897.633 | 2 | 0 | 2
38897.6331 | 1 | 0 | 2
38897.6333 | 1 | 0 | 2
38897.6334 | 1 | 0 | 2
38897.6335 | 1 | 0 | 2
38897.6336 | 1 | 0 | 2
38897.6338 | 1 | 0 | 2
38897.6339 | 1 | 0 | 2
38897.634 | 1 | 0 | 2
38897.6341 | 1 | 0 | 2
38897.6343 | 1 | 0 | 2
38897.6344 | 1 | 0 | 2
38897.6345 | 1 | 0 | 2
38897.6346 | 1 | 0 | 2
38897.6348 | 1 | 0 | 2
38897.6349 | 1 | 0 | 2
38897.635 | 1 | 0 | 2
38897.6351 | 1 | 0 | 2
38897.6353 | 1 | 0 | 2
38897.6354 | 1 | 0 | 2
38897.6355 | 1 | 0 | 2
38897.6356 | 1 | 0 | 2
38897.6358 | 1 | 0 | 2
38897.6359 | 1 | 0 | 2
38897.636 | 1 | 0 | 2
38897.6361 | 1 | 0 | 2
38897.6363 | 1 | 0 | 2
38897.6364 | 1 | 0 | 2
38897.6365 | 1 | 0 | 2
38897.6366 | 1 | 0 | 2
38897.6368 | 2 | 0 | 2
38897.6369 | 1 | 0 | 2
38897.637 | 1 | 0 | 2
38897.6371 | 1 | 0 | 2
38897.6373 | 1 | 0 | 2
38897.6374 | 3 | 0 | 2
38897.6375 | 164 | 93 | 2
38897.6376 | 202 | 145 | 2
38897.6378 | 234 | 132 | 2
38897.6379 | 203 | 79 | 2
38897.638 | 296 | 158 | 2
38897.6381 | 369 | 235 | 2
38897.6383 | 535 | 349 | 2
38897.6384 | 444 | 257 | 2
38897.6385 | 1051 | 890 | 2
38897.6386 | 696 | 485 | 2
38897.6387 | 1133 | 958 | 2
38897.6389 | 1115 | 941 | 2
38897.639 | 1061 | 886 | 2
38897.6391 | 1139 | 953 | 2
38897.6392 | 1176 | 1069 | 2
38897.6394 | 679 | 431 | 2
38897.6395 | 1082 | 822 | 2
38897.6396 | 1280 | 915 | 2
38897.6398 | 1360 | 858 | 2
38897.6399 | 1381 | 872 | 2
38897.64 | 1189 | 645 | 2
38897.6401 | 1419 | 706 | 2
38897.6403 | 1441 | 744 | 2
38897.6404 | 1797 | 565 | 2
38897.6405 | 1996 | 350 | 2
38897.6406 | 2182 | 183 | 2
38897.6408 | 1644 | 220 | 2
38897.6409 | 1579 | 551 | 2
38897.641 | 1684 | 219 | 2
38897.6411 | 1665 | 315 | 2
38897.6413 | 1840 | 240 | 2
38897.6414 | 1745 | 266 | 2
38897.6415 | 1678 | 296 | 2
38897.6416 | 1881 | 294 | 2
38897.6417 | 2055 | 348 | 2
38897.6419 | 1702 | 268 | 2
38897.642 | 1753 | 113 | 2
38897.6421 | 1810 | 285 | 2
38897.6423 | 1868 | 318 | 2
38897.6424 | 2135 | 292 | 2
38897.6425 | 2041 | 175 | 2
38897.6426 | 1789 | 88 | 2
38897.6428 | 1619 | 324 | 2
38897.6429 | 1545 | 384 | 2
38897.643 | 1693 | 233 | 2
38897.6431 | 2114 | 257 | 2
38897.6433 | 1906 | 240 | 2
38897.6434 | 2041 | 219 | 2
38897.6435 | 2205 | 117 | 2
38897.6436 | 1826 | 95 | 2
38897.6438 | 2019 | 113 | 2
38897.6439 | 2109 | 121 | 2
38897.644 | 1804 | 143 | 2
38897.6441 | 2174 | 158 | 2
38897.6442 | 2022 | 384 | 2
38897.6444 | 1796 | 106 | 2
38897.6445 | 1877 | 152 | 2
38897.6446 | 1773 | 153 | 2
38897.6448 | 2177 | 175 | 2
38897.6449 | 2059 | 138 | 2
38897.645 | 2184 | 112 | 2
38897.6451 | 1764 | 186 | 2
38897.6453 | 2144 | 198 | 2
38897.6454 | 2190 | 170 | 2
38897.6455 | 2078 | 213 | 2
38897.6456 | 1853 | 230 | 2
38897.6458 | 1942 | 465 | 2
38897.6459 | 1572 | 441 | 2
38897.646 | 1796 | 451 | 2
38897.6461 | 1806 | 602 | 2
38897.6462 | 1513 | 518 | 2
38897.6464 | 1465 | 527 | 2
38897.6465 | 1325 | 727 | 2
38897.6466 | 1703 | 770 | 2
38897.6467 | 1362 | 597 | 2
38897.6469 | 1399 | 731 | 2
38897.6269 | 1 | 0 | 3
38897.627 | 1 | 0 | 3
38897.6271 | 1 | 0 | 3
38897.6273 | 1 | 0 | 3
38897.6274 | 1 | 0 | 3
38897.6275 | 1 | 1 | 3
38897.6276 | 1 | 0 | 3
38897.6278 | 1 | 0 | 3
38897.6279 | 1 | 0 | 3
38897.628 | 1 | 1 | 3
38897.6281 | 2 | 1 | 3
38897.6283 | 1 | 0 | 3
38897.6284 | 2 | 0 | 3
38897.6285 | 1 | 0 | 3
38897.6286 | 1 | 0 | 3
38897.6288 | 1 | 0 | 3
38897.6289 | 2 | 0 | 3
38897.629 | 2 | 0 | 3
38897.6291 | 1 | 0 | 3
38897.6293 | 1 | 0 | 3
38897.6294 | 1 | 0 | 3
38897.6295 | 1 | 0 | 3
38897.6296 | 1 | 0 | 3
38897.6298 | 1 | 0 | 3
38897.6299 | 1 | 0 | 3
38897.63 | 1 | 0 | 3
38897.6301 | 1 | 0 | 3
38897.6303 | 1 | 0 | 3
38897.6304 | 1 | 0 | 3
38897.6305 | 1 | 0 | 3
38897.6306 | 1 | 0 | 3
38897.6308 | 1 | 0 | 3
38897.6309 | 2 | 0 | 3
38897.631 | 1 | 0 | 3
38897.6311 | 1 | 0 | 3
38897.6313 | 1 | 0 | 3
38897.6314 | 1 | 0 | 3
38897.6315 | 1 | 0 | 3
38897.6316 | 1 | 0 | 3
38897.6318 | 1 | 0 | 3
38897.6319 | 1 | 0 | 3
38897.632 | 1 | 0 | 3
38897.6321 | 2 | 0 | 3
38897.6323 | 1 | 0 | 3
38897.6324 | 1 | 0 | 3
38897.6325 | 2 | 0 | 3
38897.6326 | 1 | 0 | 3
38897.6328 | 1 | 0 | 3
38897.6329 | 1 | 0 | 3
38897.633 | 1 | 0 | 3
38897.6331 | 1 | 0 | 3
38897.6333 | 2 | 0 | 3
38897.6334 | 1 | 0 | 3
38897.6335 | 1 | 0 | 3
38897.6336 | 1 | 0 | 3
38897.6338 | 1 | 0 | 3
38897.6339 | 1 | 0 | 3
38897.634 | 1 | 0 | 3
38897.6341 | 2 | 0 | 3
38897.6343 | 1 | 0 | 3
38897.6344 | 1 | 0 | 3
38897.6345 | 1 | 0 | 3
38897.6346 | 1 | 0 | 3
38897.6348 | 1 | 0 | 3
38897.6349 | 1 | 0 | 3
38897.635 | 1 | 0 | 3
38897.6351 | 1 | 0 | 3
38897.6353 | 1 | 0 | 3
38897.6354 | 1 | 0 | 3
38897.6355 | 1 | 0 | 3
38897.6356 | 1 | 0 | 3
38897.6358 | 1 | 0 | 3
38897.6359 | 1 | 0 | 3
38897.636 | 1 | 0 | 3
38897.6361 | 1 | 0 | 3
38897.6363 | 1 | 0 | 3
38897.6364 | 1 | 0 | 3
38897.6365 | 1 | 0 | 3
38897.6366 | 1 | 0 | 3
38897.6368 | 1 | 0 | 3
38897.6369 | 1 | 0 | 3
38897.637 | 1 | 0 | 3
38897.6371 | 2 | 0 | 3
38897.6373 | 1 | 0 | 3
38897.6374 | 1 | 0 | 3
38897.6375 | 13 | 2 | 3
38897.6376 | 28 | 2 | 3
38897.6378 | 153 | 34 | 3
38897.6379 | 94 | 25 | 3
38897.638 | 197 | 85 | 3
38897.6381 | 197 | 98 | 3
38897.6383 | 530 | 256 | 3
38897.6384 | 281 | 192 | 3
38897.6385 | 1144 | 966 | 3
38897.6386 | 593 | 513 | 3
38897.6388 | 1253 | 1103 | 3
38897.6389 | 1246 | 1063 | 3
38897.639 | 1278 | 1113 | 3
38897.6391 | 1253 | 1057 | 3
38897.6393 | 1027 | 900 | 3
38897.6394 | 1166 | 941 | 3
38897.6395 | 1077 | 832 | 3
38897.6396 | 1345 | 940 | 3
38897.6398 | 1221 | 768 | 3
38897.6399 | 1193 | 690 | 3
38897.64 | 1309 | 751 | 3
38897.6401 | 1530 | 806 | 3
38897.6403 | 1374 | 574 | 3
38897.6404 | 1469 | 452 | 3
38897.6405 | 1700 | 315 | 3
38897.6406 | 2181 | 196 | 3
38897.6408 | 1751 | 319 | 3
38897.6409 | 1776 | 618 | 3
38897.641 | 2017 | 316 | 3
38897.6411 | 1720 | 284 | 3
38897.6413 | 2057 | 284 | 3
38897.6414 | 1989 | 307 | 3
38897.6415 | 1952 | 350 | 3
38897.6416 | 1603 | 255 | 3
38897.6418 | 1741 | 286 | 3
38897.6419 | 1717 | 303 | 3
38897.642 | 1913 | 95 | 3
38897.6421 | 2052 | 308 | 3
38897.6423 | 1584 | 283 | 3
38897.6424 | 1692 | 292 | 3
38897.6425 | 1905 | 138 | 3
38897.6426 | 1891 | 94 | 3
38897.6428 | 1890 | 319 | 3
38897.6429 | 1680 | 414 | 3
38897.643 | 1834 | 219 | 3
38897.6431 | 1995 | 243 | 3
38897.6433 | 2131 | 274 | 3
38897.6434 | 1691 | 167 | 3
38897.6435 | 1899 | 95 | 3
38897.6436 | 1986 | 92 | 3
38897.6438 | 1777 | 99 | 3
38897.6439 | 1746 | 115 | 3
38897.644 | 2037 | 160 | 3
38897.6441 | 1865 | 171 | 3
38897.6443 | 1858 | 385 | 3
38897.6444 | 1908 | 199 | 3
38897.6445 | 2062 | 179 | 3
38897.6446 | 2140 | 180 | 3
38897.6448 | 2239 | 175 | 3
38897.6449 | 1762 | 110 | 3
38897.645 | 2243 | 121 | 3
38897.6451 | 1860 | 199 | 3
38897.6453 | 2136 | 211 | 3
38897.6454 | 1704 | 178 | 3
38897.6455 | 2024 | 205 | 3
38897.6456 | 2056 | 282 | 3
38897.6458 | 1528 | 364 | 3
38897.6459 | 1715 | 384 | 3
38897.646 | 1629 | 434 | 3
38897.6461 | 1756 | 645 | 3
38897.6463 | 1464 | 614 | 3
38897.6464 | 1655 | 486 | 3
38897.6465 | 1496 | 637 | 3
38897.6466 | 1617 | 806 | 3
38897.6468 | 1477 | 746 | 3
38897.6469 | 1421 | 785 | 3
38897.6269 | 1 | 0 | 4
38897.627 | 1 | 0 | 4
38897.6272 | 1 | 0 | 4
38897.6273 | 1 | 0 | 4
38897.6274 | 1 | 0 | 4
38897.6277 | 1 | 0 | 4
38897.6278 | 2 | 1 | 4
38897.6279 | 1 | 0 | 4
38897.628 | 1 | 0 | 4
38897.6281 | 2 | 0 | 4
38897.6283 | 1 | 0 | 4
38897.6284 | 2 | 0 | 4
38897.6285 | 1 | 0 | 4
38897.6286 | 1 | 0 | 4
38897.6288 | 1 | 0 | 4
38897.6289 | 2 | 0 | 4
38897.629 | 1 | 0 | 4
38897.6292 | 1 | 1 | 4
38897.6293 | 1 | 0 | 4
38897.6294 | 1 | 0 | 4
38897.6295 | 1 | 1 | 4
38897.6297 | 1 | 0 | 4
38897.6298 | 1 | 0 | 4
38897.6299 | 1 | 0 | 4
38897.63 | 1 | 0 | 4
38897.6302 | 1 | 0 | 4
38897.6303 | 1 | 0 | 4
38897.6304 | 1 | 0 | 4
38897.6305 | 2 | 0 | 4
38897.6306 | 1 | 0 | 4
38897.6308 | 1 | 0 | 4
38897.6309 | 1 | 0 | 4
38897.631 | 1 | 0 | 4
38897.6311 | 1 | 0 | 4
38897.6313 | 1 | 0 | 4
38897.6314 | 1 | 0 | 4
38897.6315 | 1 | 0 | 4
38897.6317 | 1 | 0 | 4
38897.6318 | 1 | 0 | 4
38897.6319 | 1 | 0 | 4
38897.632 | 1 | 0 | 4
38897.6322 | 1 | 0 | 4
38897.6323 | 1 | 0 | 4
38897.6324 | 2 | 0 | 4
38897.6325 | 1 | 0 | 4
38897.6327 | 1 | 0 | 4
38897.6328 | 1 | 0 | 4
38897.6329 | 1 | 0 | 4
38897.633 | 1 | 0 | 4
38897.6331 | 1 | 0 | 4
38897.6333 | 1 | 0 | 4
38897.6334 | 1 | 0 | 4
38897.6335 | 1 | 0 | 4
38897.6336 | 1 | 0 | 4
38897.6338 | 1 | 0 | 4
38897.6339 | 1 | 0 | 4
38897.634 | 1 | 0 | 4
38897.6342 | 1 | 0 | 4
38897.6343 | 1 | 0 | 4
38897.6344 | 1 | 0 | 4
38897.6345 | 1 | 0 | 4
38897.6347 | 1 | 0 | 4
38897.6348 | 1 | 0 | 4
38897.6349 | 1 | 0 | 4
38897.635 | 1 | 0 | 4
38897.6352 | 1 | 0 | 4
38897.6353 | 1 | 0 | 4
38897.6354 | 1 | 0 | 4
38897.6355 | 1 | 0 | 4
38897.6356 | 1 | 0 | 4
38897.6358 | 1 | 0 | 4
38897.6359 | 1 | 0 | 4
38897.636 | 1 | 0 | 4
38897.6361 | 1 | 0 | 4
38897.6363 | 1 | 0 | 4
38897.6364 | 1 | 0 | 4
38897.6365 | 1 | 0 | 4
38897.6367 | 1 | 0 | 4
38897.6368 | 1 | 0 | 4
38897.6369 | 1 | 0 | 4
38897.637 | 1 | 0 | 4
38897.6372 | 1 | 0 | 4
38897.6373 | 1 | 0 | 4
38897.6374 | 1 | 0 | 4
38897.6375 | 10 | 3 | 4
38897.6377 | 24 | 9 | 4
38897.6378 | 70 | 44 | 4
38897.6379 | 103 | 28 | 4
38897.638 | 169 | 91 | 4
38897.6381 | 215 | 104 | 4
38897.6383 | 365 | 290 | 4
38897.6384 | 553 | 443 | 4
38897.6385 | 894 | 801 | 4
38897.6386 | 1048 | 754 | 4
38897.6388 | 992 | 832 | 4
38897.6389 | 1191 | 996 | 4
38897.639 | 996 | 888 | 4
38897.6391 | 1229 | 1033 | 4
38897.6393 | 1130 | 928 | 4
38897.6394 | 991 | 871 | 4
38897.6395 | 1252 | 959 | 4
38897.6397 | 1137 | 789 | 4
38897.6398 | 1296 | 862 | 4
38897.6399 | 1438 | 835 | 4
38897.64 | 1546 | 774 | 4
38897.6402 | 1287 | 658 | 4
38897.6403 | 1418 | 571 | 4
38897.6404 | 1724 | 551 | 4
38897.6405 | 1891 | 327 | 4
38897.6406 | 2208 | 153 | 4
38897.6408 | 1838 | 429 | 4
38897.6409 | 1385 | 508 | 4
38897.641 | 1632 | 219 | 4
38897.6411 | 1682 | 245 | 4
38897.6413 | 1596 | 261 | 4
38897.6414 | 1832 | 275 | 4
38897.6415 | 2036 | 294 | 4
38897.6416 | 1612 | 254 | 4
38897.6418 | 1882 | 339 | 4
38897.6419 | 2002 | 366 | 4
38897.642 | 2184 | 129 | 4
38897.6422 | 2094 | 311 | 4
38897.6423 | 1944 | 328 | 4
38897.6424 | 1743 | 330 | 4
38897.6425 | 2133 | 164 | 4
38897.6427 | 2091 | 103 | 4
38897.6428 | 1957 | 435 | 4
38897.6429 | 1619 | 352 | 4
38897.643 | 2117 | 175 | 4
38897.6431 | 1664 | 200 | 4
38897.6433 | 1846 | 231 | 4
38897.6434 | 1870 | 205 | 4
38897.6435 | 1941 | 98 | 4
38897.6436 | 2101 | 116 | 4
38897.6438 | 1965 | 107 | 4
38897.6439 | 2202 | 150 | 4
38897.644 | 2005 | 178 | 4
38897.6441 | 2086 | 199 | 4
38897.6443 | 2011 | 328 | 4
38897.6444 | 1793 | 158 | 4
38897.6445 | 2140 | 149 | 4
38897.6447 | 2067 | 162 | 4
38897.6448 | 1843 | 102 | 4
38897.6449 | 2284 | 134 | 4
38897.645 | 1892 | 103 | 4
38897.6452 | 1812 | 174 | 4
38897.6453 | 1692 | 163 | 4
38897.6454 | 1966 | 209 | 4
38897.6455 | 1898 | 206 | 4
38897.6456 | 1553 | 303 | 4
38897.6458 | 1924 | 374 | 4
38897.6459 | 1849 | 502 | 4
38897.646 | 1845 | 489 | 4
38897.6461 | 1520 | 554 | 4
38897.6463 | 1462 | 540 | 4
38897.6464 | 1868 | 472 | 4
38897.6465 | 1770 | 632 | 4
38897.6466 | 1561 | 738 | 4
38897.6468 | 1580 | 814 | 4
38897.6469 | 1463 | 901 | 4
38897.6269 | 1 | 0 | 5
38897.627 | 1 | 0 | 5
38897.6272 | 1 | 0 | 5
38897.6273 | 1 | 0 | 5
38897.6274 | 1 | 0 | 5
38897.6275 | 1 | 0 | 5
38897.6277 | 1 | 0 | 5
38897.6278 | 1 | 0 | 5
38897.6279 | 1 | 0 | 5
38897.628 | 1 | 0 | 5
38897.6282 | 1 | 0 | 5
38897.6283 | 1 | 1 | 5
38897.6284 | 2 | 0 | 5
38897.6285 | 1 | 0 | 5
38897.6287 | 1 | 0 | 5
38897.6288 | 1 | 0 | 5
38897.6289 | 1 | 1 | 5
38897.629 | 1 | 0 | 5
38897.6292 | 1 | 0 | 5
38897.6293 | 1 | 0 | 5
38897.6294 | 2 | 0 | 5
38897.6295 | 1 | 0 | 5
38897.6297 | 1 | 0 | 5
38897.6298 | 1 | 0 | 5
38897.6299 | 1 | 0 | 5
38897.63 | 1 | 0 | 5
38897.6302 | 1 | 0 | 5
38897.6303 | 1 | 0 | 5
38897.6304 | 1 | 0 | 5
38897.6305 | 1 | 0 | 5
38897.6307 | 1 | 0 | 5
38897.6308 | 1 | 0 | 5
38897.6309 | 1 | 0 | 5
38897.631 | 1 | 0 | 5
38897.6312 | 1 | 0 | 5
38897.6313 | 1 | 0 | 5
38897.6314 | 2 | 0 | 5
38897.6315 | 1 | 0 | 5
38897.6317 | 1 | 0 | 5
38897.6318 | 2 | 0 | 5
38897.6319 | 1 | 0 | 5
38897.632 | 1 | 0 | 5
38897.6322 | 1 | 0 | 5
38897.6323 | 1 | 0 | 5
38897.6324 | 1 | 0 | 5
38897.6325 | 1 | 0 | 5
38897.6327 | 1 | 0 | 5
38897.6328 | 1 | 0 | 5
38897.6329 | 1 | 0 | 5
38897.633 | 2 | 0 | 5
38897.6332 | 1 | 0 | 5
38897.6333 | 1 | 0 | 5
38897.6334 | 1 | 0 | 5
38897.6335 | 1 | 0 | 5
38897.6337 | 1 | 0 | 5
38897.6338 | 1 | 0 | 5
38897.6339 | 1 | 0 | 5
38897.634 | 2 | 0 | 5
38897.6342 | 1 | 0 | 5
38897.6343 | 1 | 0 | 5
38897.6344 | 1 | 0 | 5
38897.6345 | 1 | 0 | 5
38897.6347 | 1 | 0 | 5
38897.6348 | 1 | 0 | 5
38897.6349 | 1 | 0 | 5
38897.635 | 1 | 0 | 5
38897.6352 | 1 | 0 | 5
38897.6353 | 1 | 0 | 5
38897.6354 | 1 | 0 | 5
38897.6355 | 1 | 0 | 5
38897.6357 | 1 | 0 | 5
38897.6358 | 1 | 0 | 5
38897.6359 | 1 | 0 | 5
38897.636 | 1 | 0 | 5
38897.6362 | 1 | 0 | 5
38897.6363 | 1 | 0 | 5
38897.6364 | 1 | 0 | 5
38897.6365 | 1 | 0 | 5
38897.6367 | 2 | 0 | 5
38897.6368 | 1 | 0 | 5
38897.6369 | 1 | 0 | 5
38897.637 | 1 | 0 | 5
38897.6372 | 1 | 0 | 5
38897.6373 | 1 | 0 | 5
38897.6374 | 1 | 0 | 5
38897.6375 | 68 | 292 | 5
38897.6377 | 143 | 100 | 5
38897.6378 | 941 | 874 | 5
38897.6379 | 218 | 155 | 5
38897.638 | 307 | 251 | 5
38897.6382 | 292 | 226 | 5
38897.6383 | 1027 | 945 | 5
38897.6384 | 1065 | 993 | 5
38897.6385 | 397 | 333 | 5
38897.6387 | 1126 | 962 | 5
38897.6388 | 1079 | 983 | 5
38897.6389 | 1133 | 1035 | 5
38897.639 | 1132 | 951 | 5
38897.6392 | 1283 | 1084 | 5
38897.6393 | 970 | 892 | 5
38897.6394 | 1280 | 853 | 5
38897.6395 | 1044 | 793 | 5
38897.6397 | 1059 | 827 | 5
38897.6398 | 1208 | 839 | 5
38897.6399 | 1198 | 692 | 5
38897.64 | 1488 | 842 | 5
38897.6402 | 1591 | 758 | 5
38897.6403 | 1671 | 732 | 5
38897.6404 | 1440 | 417 | 5
38897.6405 | 1751 | 268 | 5
38897.6407 | 1766 | 155 | 5
38897.6408 | 1508 | 510 | 5
38897.6409 | 1636 | 554 | 5
38897.641 | 1760 | 212 | 5
38897.6412 | 1880 | 263 | 5
38897.6413 | 1958 | 287 | 5
38897.6414 | 1848 | 319 | 5
38897.6415 | 1661 | 305 | 5
38897.6417 | 1761 | 268 | 5
38897.6418 | 1608 | 281 | 5
38897.6419 | 1562 | 296 | 5
38897.642 | 1917 | 105 | 5
38897.6422 | 1631 | 238 | 5
38897.6423 | 2029 | 323 | 5
38897.6424 | 1675 | 303 | 5
38897.6425 | 2195 | 158 | 5
38897.6427 | 2288 | 97 | 5
38897.6428 | 1714 | 312 | 5
38897.6429 | 1549 | 334 | 5
38897.643 | 1857 | 201 | 5
38897.6432 | 1791 | 128 | 5
38897.6433 | 2108 | 269 | 5
38897.6434 | 2000 | 122 | 5
38897.6435 | 2080 | 104 | 5
38897.6437 | 1838 | 97 | 5
38897.6438 | 2145 | 130 | 5
38897.6439 | 2248 | 160 | 5
38897.644 | 2228 | 184 | 5
38897.6442 | 1992 | 191 | 5
38897.6443 | 1663 | 301 | 5
38897.6444 | 1945 | 153 | 5
38897.6445 | 2184 | 79 | 5
38897.6447 | 2070 | 155 | 5
38897.6448 | 2264 | 140 | 5
38897.6449 | 2100 | 121 | 5
38897.645 | 1970 | 149 | 5
38897.6452 | 2052 | 172 | 5
38897.6453 | 1959 | 200 | 5
38897.6454 | 1896 | 180 | 5
38897.6455 | 1830 | 192 | 5
38897.6457 | 1705 | 235 | 5
38897.6458 | 1624 | 416 | 5
38897.6459 | 1650 | 492 | 5
38897.646 | 1770 | 548 | 5
38897.6462 | 1474 | 528 | 5
38897.6463 | 1508 | 653 | 5
38897.6464 | 1558 | 430 | 5
38897.6465 | 1442 | 760 | 5
38897.6467 | 1483 | 868 | 5
38897.6468 | 1439 | 727 | 5
38897.6469 | 1214 | 736 | 5
38897.6269 | 1 | 0 | 6
38897.627 | 1 | 0 | 6
38897.6272 | 1 | 0 | 6
38897.6273 | 1 | 0 | 6
38897.6274 | 1 | 0 | 6
38897.6275 | 1 | 0 | 6
38897.6277 | 1 | 0 | 6
38897.6278 | 1 | 0 | 6
38897.6279 | 1 | 0 | 6
38897.628 | 1 | 0 | 6
38897.6282 | 1 | 0 | 6
38897.6283 | 1 | 0 | 6
38897.6284 | 2 | 1 | 6
38897.6285 | 1 | 0 | 6
38897.6287 | 1 | 0 | 6
38897.6288 | 1 | 0 | 6
38897.6289 | 1 | 0 | 6
38897.6291 | 2 | 0 | 6
38897.6292 | 1 | 0 | 6
38897.6293 | 1 | 0 | 6
38897.6294 | 1 | 0 | 6
38897.6295 | 1 | 0 | 6
38897.6297 | 1 | 0 | 6
38897.6298 | 1 | 0 | 6
38897.6299 | 1 | 0 | 6
38897.63 | 2 | 0 | 6
38897.6302 | 1 | 0 | 6
38897.6303 | 1 | 0 | 6
38897.6304 | 1 | 0 | 6
38897.6305 | 1 | 0 | 6
38897.6307 | 1 | 0 | 6
38897.6308 | 1 | 0 | 6
38897.6309 | 2 | 0 | 6
38897.631 | 1 | 0 | 6
38897.6312 | 1 | 0 | 6
38897.6313 | 2 | 0 | 6
38897.6314 | 1 | 0 | 6
38897.6316 | 1 | 0 | 6
38897.6317 | 1 | 0 | 6
38897.6318 | 1 | 0 | 6
38897.6319 | 1 | 0 | 6
38897.632 | 1 | 0 | 6
38897.6322 | 1 | 0 | 6
38897.6323 | 1 | 0 | 6
38897.6324 | 1 | 0 | 6
38897.6325 | 1 | 0 | 6
38897.6327 | 1 | 0 | 6
38897.6328 | 1 | 0 | 6
38897.6329 | 1 | 0 | 6
38897.633 | 2 | 0 | 6
38897.6332 | 1 | 0 | 6
38897.6333 | 1 | 0 | 6
38897.6334 | 1 | 0 | 6
38897.6335 | 1 | 0 | 6
38897.6337 | 1 | 0 | 6
38897.6338 | 1 | 0 | 6
38897.6339 | 1 | 0 | 6
38897.6341 | 1 | 0 | 6
38897.6342 | 1 | 0 | 6
38897.6343 | 1 | 0 | 6
38897.6344 | 1 | 0 | 6
38897.6345 | 1 | 0 | 6
38897.6347 | 1 | 0 | 6
38897.6348 | 1 | 0 | 6
38897.6349 | 1 | 0 | 6
38897.635 | 1 | 0 | 6
38897.6352 | 1 | 0 | 6
38897.6353 | 1 | 0 | 6
38897.6354 | 1 | 0 | 6
38897.6355 | 1 | 0 | 6
38897.6357 | 1 | 0 | 6
38897.6358 | 1 | 0 | 6
38897.6359 | 1 | 0 | 6
38897.636 | 1 | 0 | 6
38897.6362 | 1 | 0 | 6
38897.6363 | 1 | 0 | 6
38897.6364 | 1 | 0 | 6
38897.6366 | 1 | 0 | 6
38897.6367 | 1 | 0 | 6
38897.6368 | 1 | 0 | 6
38897.6369 | 1 | 0 | 6
38897.637 | 1 | 0 | 6
38897.6372 | 1 | 0 | 6
38897.6373 | 1 | 0 | 6
38897.6374 | 81 | 21 | 6
38897.6375 | 257 | 163 | 6
38897.6377 | 676 | 642 | 6
38897.6378 | 187 | 78 | 6
38897.6379 | 329 | 179 | 6
38897.638 | 440 | 276 | 6
38897.6382 | 416 | 246 | 6
38897.6383 | 982 | 822 | 6
38897.6384 | 1180 | 1042 | 6
38897.6385 | 457 | 250 | 6
38897.6387 | 1237 | 1064 | 6
38897.6388 | 1048 | 886 | 6
38897.6389 | 994 | 971 | 6
38897.639 | 1036 | 867 | 6
38897.6392 | 1024 | 908 | 6
38897.6393 | 1088 | 886 | 6
38897.6394 | 1206 | 1034 | 6
38897.6395 | 1101 | 885 | 6
38897.6397 | 1093 | 791 | 6
38897.6398 | 1331 | 870 | 6
38897.6399 | 1306 | 787 | 6
38897.64 | 1341 | 691 | 6
38897.6402 | 1336 | 659 | 6
38897.6403 | 1588 | 654 | 6
38897.6404 | 1555 | 440 | 6
38897.6405 | 2046 | 351 | 6
38897.6407 | 2073 | 197 | 6
38897.6408 | 1626 | 460 | 6
38897.6409 | 1806 | 541 | 6
38897.641 | 2081 | 327 | 6
38897.6412 | 2016 | 282 | 6
38897.6413 | 1666 | 242 | 6
38897.6414 | 1788 | 284 | 6
38897.6415 | 1819 | 311 | 6
38897.6417 | 2110 | 294 | 6
38897.6418 | 1939 | 312 | 6
38897.6419 | 1720 | 330 | 6
38897.642 | 2213 | 120 | 6
38897.6422 | 1750 | 262 | 6
38897.6423 | 1704 | 278 | 6
38897.6424 | 1739 | 311 | 6
38897.6425 | 2032 | 155 | 6
38897.6427 | 1901 | 96 | 6
38897.6428 | 1543 | 377 | 6
38897.6429 | 1671 | 305 | 6
38897.643 | 2012 | 251 | 6
38897.6432 | 2185 | 229 | 6
38897.6433 | 1717 | 216 | 6
38897.6434 | 1852 | 98 | 6
38897.6435 | 2292 | 89 | 6
38897.6437 | 2014 | 102 | 6
38897.6438 | 2054 | 112 | 6
38897.6439 | 1786 | 133 | 6
38897.644 | 1821 | 150 | 6
38897.6442 | 1999 | 218 | 6
38897.6443 | 1852 | 292 | 6
38897.6444 | 2045 | 145 | 6
38897.6445 | 2343 | 61 | 6
38897.6447 | 1728 | 130 | 6
38897.6448 | 1804 | 125 | 6
38897.6449 | 2278 | 132 | 6
38897.645 | 1638 | 223 | 6
38897.6452 | 2098 | 161 | 6
38897.6453 | 1799 | 166 | 6
38897.6454 | 2067 | 206 | 6
38897.6455 | 2155 | 241 | 6
38897.6457 | 2179 | 228 | 6
38897.6458 | 1714 | 450 | 6
38897.6459 | 1793 | 549 | 6
38897.646 | 1511 | 444 | 6
38897.6462 | 1732 | 660 | 6
38897.6463 | 1685 | 671 | 6
38897.6464 | 1911 | 510 | 6
38897.6465 | 1469 | 671 | 6
38897.6467 | 1436 | 577 | 6
38897.6468 | 1517 | 725 | 6
38897.6469 | 1409 | 850 | 6
38897.6269 | 1 | 0 | 7
38897.6271 | 1 | 0 | 7
38897.6272 | 1 | 0 | 7
38897.6273 | 1 | 0 | 7
38897.6274 | 1 | 0 | 7
38897.6276 | 1 | 0 | 7
38897.6277 | 1 | 0 | 7
38897.6278 | 2 | 0 | 7
38897.6279 | 1 | 1 | 7
38897.6281 | 1 | 1 | 7
38897.6282 | 1 | 0 | 7
38897.6283 | 1 | 0 | 7
38897.6284 | 2 | 0 | 7
38897.6286 | 1 | 0 | 7
38897.6287 | 1 | 0 | 7
38897.6288 | 1 | 0 | 7
38897.6289 | 1 | 0 | 7
38897.6291 | 2 | 0 | 7
38897.6292 | 1 | 0 | 7
38897.6293 | 1 | 0 | 7
38897.6294 | 2 | 0 | 7
38897.6296 | 1 | 0 | 7
38897.6297 | 1 | 0 | 7
38897.6298 | 1 | 1 | 7
38897.6299 | 1 | 0 | 7
38897.6301 | 2 | 0 | 7
38897.6302 | 1 | 0 | 7
38897.6303 | 2 | 0 | 7
38897.6304 | 2 | 0 | 7
38897.6306 | 1 | 0 | 7
38897.6307 | 1 | 0 | 7
38897.6308 | 1 | 0 | 7
38897.6309 | 1 | 0 | 7
38897.6311 | 1 | 0 | 7
38897.6312 | 2 | 0 | 7
38897.6313 | 1 | 0 | 7
38897.6314 | 1 | 0 | 7
38897.6316 | 3 | 0 | 7
38897.6317 | 1 | 0 | 7
38897.6318 | 1 | 0 | 7
38897.6319 | 1 | 0 | 7
38897.6321 | 1 | 0 | 7
38897.6322 | 2 | 0 | 7
38897.6323 | 1 | 0 | 7
38897.6324 | 1 | 0 | 7
38897.6326 | 1 | 0 | 7
38897.6327 | 1 | 0 | 7
38897.6328 | 1 | 0 | 7
38897.6329 | 1 | 0 | 7
38897.6331 | 1 | 0 | 7
38897.6332 | 1 | 0 | 7
38897.6333 | 1 | 0 | 7
38897.6334 | 1 | 0 | 7
38897.6336 | 1 | 0 | 7
38897.6337 | 1 | 0 | 7
38897.6338 | 1 | 0 | 7
38897.6339 | 1 | 0 | 7
38897.6341 | 1 | 0 | 7
38897.6342 | 1 | 0 | 7
38897.6343 | 1 | 0 | 7
38897.6344 | 1 | 0 | 7
38897.6346 | 1 | 0 | 7
38897.6347 | 1 | 0 | 7
38897.6348 | 1 | 0 | 7
38897.6349 | 1 | 0 | 7
38897.6351 | 1 | 0 | 7
38897.6352 | 1 | 0 | 7
38897.6353 | 1 | 0 | 7
38897.6354 | 2 | 0 | 7
38897.6356 | 1 | 0 | 7
38897.6357 | 1 | 0 | 7
38897.6358 | 1 | 0 | 7
38897.6359 | 1 | 0 | 7
38897.6361 | 1 | 0 | 7
38897.6362 | 1 | 0 | 7
38897.6363 | 1 | 0 | 7
38897.6364 | 1 | 0 | 7
38897.6366 | 1 | 0 | 7
38897.6367 | 1 | 0 | 7
38897.6368 | 1 | 0 | 7
38897.6369 | 1 | 0 | 7
38897.6371 | 1 | 0 | 7
38897.6372 | 1 | 0 | 7
38897.6373 | 1 | 0 | 7
38897.6374 | 49 | 4 | 7
38897.6376 | 105 | 14 | 7
38897.6377 | 175 | 41 | 7
38897.6378 | 262 | 114 | 7
38897.6379 | 304 | 155 | 7
38897.6381 | 366 | 221 | 7
38897.6382 | 475 | 288 | 7
38897.6383 | 524 | 319 | 7
38897.6384 | 734 | 538 | 7
38897.6386 | 1105 | 936 | 7
38897.6387 | 941 | 882 | 7
38897.6388 | 1108 | 940 | 7
38897.6389 | 1052 | 884 | 7
38897.6391 | 1140 | 958 | 7
38897.6392 | 1231 | 1033 | 7
38897.6393 | 1302 | 1096 | 7
38897.6394 | 1293 | 1083 | 7
38897.6396 | 1246 | 1011 | 7
38897.6397 | 1343 | 918 | 7
38897.6398 | 1466 | 905 | 7
38897.6399 | 1426 | 866 | 7
38897.6401 | 1364 | 712 | 7
38897.6402 | 1495 | 685 | 7
38897.6403 | 1506 | 645 | 7
38897.6404 | 1908 | 404 | 7
38897.6406 | 1792 | 306 | 7
38897.6407 | 1955 | 175 | 7
38897.6408 | 1425 | 470 | 7
38897.6409 | 1526 | 400 | 7
38897.6411 | 1722 | 203 | 7
38897.6412 | 1759 | 235 | 7
38897.6413 | 1869 | 296 | 7
38897.6414 | 1760 | 301 | 7
38897.6416 | 2049 | 274 | 7
38897.6417 | 1681 | 215 | 7
38897.6418 | 1595 | 256 | 7
38897.6419 | 1582 | 293 | 7
38897.6421 | 2019 | 108 | 7
38897.6422 | 1951 | 268 | 7
38897.6423 | 1586 | 274 | 7
38897.6424 | 1958 | 358 | 7
38897.6426 | 2210 | 177 | 7
38897.6427 | 2036 | 111 | 7
38897.6429 | 1686 | 211 | 7
38897.6431 | 2122 | 263 | 7
38897.6432 | 1742 | 208 | 7
38897.6433 | 2135 | 273 | 7
38897.6434 | 2250 | 123 | 7
38897.6436 | 1812 | 96 | 7
38897.6437 | 2098 | 108 | 7
38897.6438 | 2182 | 124 | 7
38897.6439 | 1886 | 148 | 7
38897.6441 | 2105 | 176 | 7
38897.6442 | 1685 | 294 | 7
38897.6443 | 1645 | 301 | 7
38897.6444 | 1843 | 141 | 7
38897.6445 | 2025 | 74 | 7
38897.6447 | 2116 | 157 | 7
38897.6448 | 1997 | 142 | 7
38897.6449 | 1918 | 111 | 7
38897.6451 | 1706 | 228 | 7
38897.6452 | 1868 | 191 | 7
38897.6453 | 2109 | 200 | 7
38897.6454 | 1686 | 170 | 7
38897.6456 | 1690 | 184 | 7
38897.6457 | 1572 | 285 | 7
38897.6458 | 1895 | 522 | 7
38897.6459 | 1574 | 353 | 7
38897.6461 | 1706 | 522 | 7
38897.6462 | 1568 | 489 | 7
38897.6463 | 1699 | 703 | 7
38897.6464 | 1744 | 463 | 7
38897.6466 | 1888 | 573 | 7
38897.6467 | 1682 | 720 | 7
38897.6468 | 1271 | 704 | 7
38897.6469 | 1479 | 879 | 7
38897.6269 | 1 | 0 | 8
38897.6271 | 1 | 0 | 8
38897.6272 | 1 | 0 | 8
38897.6273 | 1 | 0 | 8
38897.6274 | 1 | 0 | 8
38897.6276 | 1 | 0 | 8
38897.6277 | 1 | 0 | 8
38897.6278 | 1 | 0 | 8
38897.6279 | 1 | 0 | 8
38897.6281 | 1 | 0 | 8
38897.6282 | 1 | 0 | 8
38897.6283 | 1 | 0 | 8
38897.6284 | 2 | 0 | 8
38897.6286 | 1 | 0 | 8
38897.6287 | 1 | 0 | 8
38897.6288 | 1 | 0 | 8
38897.6289 | 2 | 0 | 8
38897.6291 | 1 | 0 | 8
38897.6292 | 1 | 0 | 8
38897.6293 | 1 | 0 | 8
38897.6294 | 2 | 0 | 8
38897.6296 | 1 | 0 | 8
38897.6297 | 2 | 0 | 8
38897.6298 | 1 | 0 | 8
38897.6299 | 2 | 0 | 8
38897.6301 | 1 | 0 | 8
38897.6302 | 1 | 0 | 8
38897.6303 | 1 | 0 | 8
38897.6304 | 2 | 0 | 8
38897.6306 | 1 | 0 | 8
38897.6307 | 1 | 0 | 8
38897.6308 | 1 | 0 | 8
38897.6309 | 1 | 0 | 8
38897.6311 | 1 | 0 | 8
38897.6312 | 1 | 0 | 8
38897.6313 | 1 | 0 | 8
38897.6314 | 1 | 0 | 8
38897.6316 | 1 | 0 | 8
38897.6317 | 1 | 0 | 8
38897.6318 | 1 | 0 | 8
38897.6319 | 1 | 0 | 8
38897.6321 | 1 | 0 | 8
38897.6322 | 1 | 0 | 8
38897.6323 | 1 | 0 | 8
38897.6324 | 1 | 0 | 8
38897.6326 | 1 | 0 | 8
38897.6327 | 1 | 0 | 8
38897.6328 | 1 | 0 | 8
38897.6329 | 2 | 0 | 8
38897.6331 | 1 | 0 | 8
38897.6332 | 1 | 0 | 8
38897.6333 | 1 | 0 | 8
38897.6334 | 1 | 0 | 8
38897.6336 | 1 | 0 | 8
38897.6337 | 1 | 0 | 8
38897.6338 | 2 | 0 | 8
38897.6339 | 1 | 0 | 8
38897.6341 | 1 | 0 | 8
38897.6342 | 1 | 0 | 8
38897.6343 | 1 | 0 | 8
38897.6344 | 1 | 0 | 8
38897.6346 | 1 | 0 | 8
38897.6347 | 1 | 0 | 8
38897.6348 | 1 | 0 | 8
38897.6349 | 1 | 0 | 8
38897.6351 | 1 | 0 | 8
38897.6352 | 1 | 0 | 8
38897.6353 | 1 | 0 | 8
38897.6354 | 1 | 0 | 8
38897.6356 | 1 | 0 | 8
38897.6357 | 1 | 0 | 8
38897.6358 | 1 | 0 | 8
38897.6359 | 1 | 0 | 8
38897.6361 | 1 | 0 | 8
38897.6362 | 1 | 0 | 8
38897.6363 | 1 | 0 | 8
38897.6364 | 1 | 0 | 8
38897.6366 | 1 | 0 | 8
38897.6367 | 1 | 0 | 8
38897.6368 | 1 | 0 | 8
38897.6369 | 1 | 0 | 8
38897.6371 | 1 | 0 | 8
38897.6372 | 1 | 0 | 8
38897.6373 | 1 | 0 | 8
38897.6374 | 9 | 5 | 8
38897.6376 | 28 | 17 | 8
38897.6377 | 58 | 40 | 8
38897.6378 | 165 | 122 | 8
38897.6379 | 218 | 153 | 8
38897.6381 | 302 | 238 | 8
38897.6382 | 343 | 280 | 8
38897.6383 | 478 | 408 | 8
38897.6384 | 1077 | 713 | 8
38897.6386 | 909 | 875 | 8
38897.6387 | 995 | 904 | 8
38897.6388 | 1197 | 1022 | 8
38897.6389 | 996 | 840 | 8
38897.6391 | 1268 | 1073 | 8
38897.6392 | 999 | 850 | 8
38897.6393 | 1015 | 831 | 8
38897.6394 | 1302 | 1044 | 8
38897.6396 | 1344 | 1037 | 8
38897.6397 | 1272 | 855 | 8
38897.6398 | 1184 | 723 | 8
38897.6399 | 1341 | 747 | 8
38897.6401 | 1654 | 742 | 8
38897.6402 | 1278 | 623 | 8
38897.6403 | 1306 | 577 | 8
38897.6404 | 1599 | 405 | 8
38897.6406 | 1786 | 258 | 8
38897.6407 | 2005 | 189 | 8
38897.6408 | 1695 | 576 | 8
38897.6409 | 1780 | 442 | 8
38897.6411 | 1785 | 365 | 8
38897.6412 | 2086 | 277 | 8
38897.6413 | 1932 | 311 | 8
38897.6414 | 2012 | 341 | 8
38897.6416 | 1619 | 285 | 8
38897.6417 | 1803 | 234 | 8
38897.6418 | 1621 | 270 | 8
38897.6419 | 1894 | 241 | 8
38897.6421 | 2282 | 94 | 8
38897.6422 | 1617 | 236 | 8
38897.6423 | 1717 | 281 | 8
38897.6424 | 1688 | 308 | 8
38897.6426 | 1848 | 127 | 8
38897.6427 | 2244 | 156 | 8
38897.6428 | 1562 | 372 | 8
38897.6429 | 1784 | 265 | 8
38897.6431 | 2109 | 256 | 8
38897.6432 | 1795 | 239 | 8
38897.6433 | 1699 | 221 | 8
38897.6434 | 2231 | 106 | 8
38897.6436 | 2073 | 103 | 8
38897.6437 | 1989 | 98 | 8
38897.6438 | 2184 | 129 | 8
38897.6439 | 1857 | 140 | 8
38897.6441 | 2216 | 187 | 8
38897.6442 | 1894 | 374 | 8
38897.6443 | 1834 | 357 | 8
38897.6444 | 2238 | 150 | 8
38897.6446 | 2132 | 95 | 8
38897.6447 | 2237 | 175 | 8
38897.6448 | 1759 | 143 | 8
38897.6449 | 2264 | 148 | 8
38897.6451 | 2097 | 212 | 8
38897.6452 | 1729 | 148 | 8
38897.6453 | 1725 | 160 | 8
38897.6454 | 1901 | 207 | 8
38897.6456 | 1944 | 209 | 8
38897.6457 | 1785 | 284 | 8
38897.6458 | 1764 | 360 | 8
38897.6459 | 1808 | 418 | 8
38897.6461 | 1787 | 580 | 8
38897.6462 | 1676 | 528 | 8
38897.6463 | 1698 | 690 | 8
38897.6464 | 1577 | 573 | 8
38897.6466 | 1288 | 594 | 8
38897.6467 | 1342 | 690 | 8
38897.6468 | 1350 | 720 | 8
38897.6469 | 1179 | 695 | 8
38897.627 | 1 | 0 | 9
38897.6271 | 1 | 0 | 9
38897.6272 | 1 | 0 | 9
38897.6273 | 1 | 0 | 9
38897.6275 | 1 | 0 | 9
38897.6276 | 1 | 0 | 9
38897.6277 | 1 | 0 | 9
38897.6278 | 1 | 0 | 9
38897.628 | 1 | 0 | 9
38897.6281 | 1 | 0 | 9
38897.6282 | 1 | 0 | 9
38897.6283 | 1 | 0 | 9
38897.6284 | 2 | 0 | 9
38897.6286 | 2 | 0 | 9
38897.6287 | 1 | 0 | 9
38897.6288 | 1 | 0 | 9
38897.6289 | 2 | 0 | 9
38897.6291 | 1 | 0 | 9
38897.6292 | 2 | 0 | 9
38897.6293 | 1 | 0 | 9
38897.6295 | 1 | 0 | 9
38897.6296 | 1 | 0 | 9
38897.6297 | 2 | 0 | 9
38897.6298 | 2 | 0 | 9
38897.63 | 2 | 0 | 9
38897.6301 | 1 | 0 | 9
38897.6302 | 1 | 0 | 9
38897.6303 | 1 | 0 | 9
38897.6305 | 1 | 0 | 9
38897.6306 | 1 | 0 | 9
38897.6307 | 1 | 0 | 9
38897.6308 | 2 | 0 | 9
38897.6309 | 2 | 0 | 9
38897.6311 | 1 | 0 | 9
38897.6312 | 1 | 0 | 9
38897.6313 | 1 | 0 | 9
38897.6314 | 1 | 0 | 9
38897.6316 | 1 | 0 | 9
38897.6317 | 1 | 0 | 9
38897.6318 | 1 | 0 | 9
38897.632 | 1 | 0 | 9
38897.6321 | 1 | 0 | 9
38897.6322 | 1 | 0 | 9
38897.6323 | 1 | 0 | 9
38897.6325 | 1 | 0 | 9
38897.6326 | 1 | 0 | 9
38897.6327 | 1 | 0 | 9
38897.6328 | 1 | 0 | 9
38897.633 | 1 | 0 | 9
38897.6331 | 1 | 0 | 9
38897.6332 | 1 | 0 | 9
38897.6333 | 1 | 0 | 9
38897.6334 | 2 | 0 | 9
38897.6336 | 1 | 0 | 9
38897.6337 | 1 | 0 | 9
38897.6338 | 1 | 0 | 9
38897.6339 | 2 | 0 | 9
38897.6341 | 1 | 0 | 9
38897.6342 | 1 | 0 | 9
38897.6343 | 1 | 0 | 9
38897.6345 | 1 | 0 | 9
38897.6346 | 1 | 0 | 9
38897.6347 | 1 | 0 | 9
38897.6348 | 1 | 0 | 9
38897.635 | 1 | 0 | 9
38897.6351 | 1 | 0 | 9
38897.6352 | 1 | 0 | 9
38897.6353 | 1 | 0 | 9
38897.6355 | 1 | 0 | 9
38897.6356 | 2 | 0 | 9
38897.6357 | 1 | 0 | 9
38897.6358 | 1 | 0 | 9
38897.6359 | 2 | 0 | 9
38897.6361 | 1 | 0 | 9
38897.6362 | 1 | 0 | 9
38897.6363 | 1 | 0 | 9
38897.6364 | 1 | 0 | 9
38897.6366 | 1 | 0 | 9
38897.6367 | 1 | 0 | 9
38897.6368 | 1 | 0 | 9
38897.637 | 1 | 0 | 9
38897.6371 | 1 | 0 | 9
38897.6372 | 5 | 2 | 9
38897.6373 | 146 | 125 | 9
38897.6375 | 771 | 695 | 9
38897.6376 | 965 | 870 | 9
38897.6377 | 282 | 229 | 9
38897.6378 | 629 | 594 | 9
38897.638 | 540 | 462 | 9
38897.6381 | 1115 | 807 | 9
38897.6382 | 361 | 295 | 9
38897.6383 | 1109 | 949 | 9
38897.6384 | 1088 | 927 | 9
38897.6386 | 1014 | 922 | 9
38897.6387 | 1194 | 1023 | 9
38897.6388 | 1121 | 1066 | 9
38897.6389 | 1078 | 905 | 9
38897.6391 | 1214 | 1021 | 9
38897.6392 | 1141 | 950 | 9
38897.6393 | 1305 | 1081 | 9
38897.6395 | 1030 | 815 | 9
38897.6396 | 1156 | 849 | 9
38897.6397 | 1330 | 957 | 9
38897.6398 | 1311 | 784 | 9
38897.64 | 1511 | 840 | 9
38897.6401 | 1308 | 682 | 9
38897.6402 | 1423 | 689 | 9
38897.6403 | 1597 | 672 | 9
38897.6405 | 1764 | 438 | 9
38897.6406 | 1678 | 245 | 9
38897.6407 | 2126 | 214 | 9
38897.6408 | 1827 | 442 | 9
38897.6409 | 1546 | 382 | 9
38897.6411 | 1432 | 421 | 9
38897.6412 | 1674 | 216 | 9
38897.6413 | 1812 | 280 | 9
38897.6414 | 1716 | 282 | 9
38897.6416 | 1751 | 309 | 9
38897.6417 | 2075 | 260 | 9
38897.6418 | 2013 | 327 | 9
38897.642 | 2206 | 170 | 9
38897.6421 | 1848 | 77 | 9
38897.6422 | 1893 | 130 | 9
38897.6423 | 1848 | 321 | 9
38897.6425 | 1909 | 350 | 9
38897.6426 | 1796 | 123 | 9
38897.6427 | 2059 | 130 | 9
38897.6428 | 1910 | 453 | 9
38897.643 | 1962 | 302 | 9
38897.6431 | 2125 | 268 | 9
38897.6432 | 1753 | 219 | 9
38897.6433 | 1856 | 228 | 9
38897.6434 | 2047 | 112 | 9
38897.6436 | 2294 | 117 | 9
38897.6437 | 2177 | 116 | 9
38897.6438 | 1830 | 112 | 9
38897.6439 | 1967 | 154 | 9
38897.6441 | 1729 | 151 | 9
38897.6442 | 1588 | 320 | 9
38897.6443 | 1671 | 202 | 9
38897.6444 | 1759 | 129 | 9
38897.6446 | 1960 | 110 | 9
38897.6447 | 1806 | 144 | 9
38897.6448 | 2003 | 117 | 9
38897.645 | 1763 | 244 | 9
38897.6451 | 2159 | 243 | 9
38897.6452 | 1826 | 185 | 9
38897.6453 | 2047 | 200 | 9
38897.6455 | 2163 | 203 | 9
38897.6456 | 2125 | 241 | 9
38897.6457 | 1770 | 417 | 9
38897.6458 | 1997 | 457 | 9
38897.6459 | 1502 | 473 | 9
38897.6461 | 1436 | 502 | 9
38897.6462 | 1790 | 652 | 9
38897.6463 | 1851 | 567 | 9
38897.6464 | 1427 | 625 | 9
38897.6467 | 1649 | 722 | 9
38897.6468 | 1176 | 767 | 9
38897.6469 | 1282 | 823 | 9
38897.627 | 1 | 0 | 10
38897.6271 | 1 | 0 | 10
38897.6272 | 1 | 0 | 10
38897.6273 | 1 | 0 | 10
38897.6275 | 1 | 0 | 10
38897.6276 | 1 | 0 | 10
38897.6277 | 1 | 0 | 10
38897.6278 | 1 | 0 | 10
38897.628 | 1 | 0 | 10
38897.6281 | 1 | 0 | 10
38897.6282 | 1 | 0 | 10
38897.6283 | 1 | 0 | 10
38897.6285 | 1 | 0 | 10
38897.6286 | 1 | 0 | 10
38897.6287 | 1 | 0 | 10
38897.6288 | 1 | 0 | 10
38897.629 | 1 | 0 | 10
38897.6291 | 1 | 0 | 10
38897.6292 | 1 | 0 | 10
38897.6293 | 2 | 0 | 10
38897.6295 | 1 | 0 | 10
38897.6296 | 1 | 0 | 10
38897.6297 | 1 | 0 | 10
38897.6298 | 1 | 0 | 10
38897.63 | 2 | 0 | 10
38897.6301 | 1 | 0 | 10
38897.6302 | 1 | 0 | 10
38897.6303 | 1 | 0 | 10
38897.6305 | 1 | 0 | 10
38897.6306 | 1 | 0 | 10
38897.6307 | 1 | 0 | 10
38897.6308 | 1 | 0 | 10
38897.631 | 1 | 0 | 10
38897.6311 | 1 | 0 | 10
38897.6312 | 2 | 0 | 10
38897.6313 | 1 | 0 | 10
38897.6315 | 1 | 0 | 10
38897.6316 | 2 | 0 | 10
38897.6317 | 1 | 0 | 10
38897.6318 | 1 | 0 | 10
38897.632 | 1 | 0 | 10
38897.6321 | 1 | 0 | 10
38897.6322 | 1 | 0 | 10
38897.6323 | 1 | 0 | 10
38897.6325 | 1 | 0 | 10
38897.6326 | 1 | 0 | 10
38897.6327 | 1 | 0 | 10
38897.6328 | 1 | 0 | 10
38897.633 | 1 | 0 | 10
38897.6331 | 1 | 0 | 10
38897.6332 | 1 | 0 | 10
38897.6333 | 1 | 0 | 10
38897.6335 | 1 | 0 | 10
38897.6336 | 1 | 0 | 10
38897.6337 | 1 | 0 | 10
38897.6338 | 2 | 0 | 10
38897.634 | 1 | 0 | 10
38897.6341 | 1 | 0 | 10
38897.6342 | 1 | 0 | 10
38897.6343 | 1 | 0 | 10
38897.6345 | 1 | 0 | 10
38897.6346 | 1 | 0 | 10
38897.6347 | 1 | 0 | 10
38897.6348 | 1 | 0 | 10
38897.635 | 1 | 0 | 10
38897.6351 | 1 | 0 | 10
38897.6352 | 1 | 0 | 10
38897.6353 | 1 | 0 | 10
38897.6355 | 1 | 0 | 10
38897.6356 | 2 | 0 | 10
38897.6357 | 1 | 0 | 10
38897.6358 | 1 | 0 | 10
38897.636 | 1 | 0 | 10
38897.6361 | 1 | 0 | 10
38897.6362 | 1 | 0 | 10
38897.6363 | 1 | 0 | 10
38897.6365 | 1 | 0 | 10
38897.6366 | 1 | 0 | 10
38897.6367 | 1 | 0 | 10
38897.6368 | 1 | 0 | 10
38897.637 | 1 | 0 | 10
38897.6371 | 1 | 0 | 10
38897.6372 | 18 | 3 | 10
38897.6373 | 600 | 544 | 10
38897.6375 | 380 | 353 | 10
38897.6376 | 1067 | 1039 | 10
38897.6377 | 710 | 693 | 10
38897.6378 | 578 | 470 | 10
38897.638 | 820 | 670 | 10
38897.6381 | 1034 | 881 | 10
38897.6382 | 555 | 420 | 10
38897.6383 | 1266 | 1116 | 10
38897.6385 | 1270 | 1113 | 10
38897.6386 | 1194 | 1021 | 10
38897.6387 | 1277 | 1110 | 10
38897.6388 | 1277 | 1101 | 10
38897.639 | 1149 | 1049 | 10
38897.6391 | 1241 | 1112 | 10
38897.6392 | 1208 | 1005 | 10
38897.6393 | 1177 | 961 | 10
38897.6395 | 1072 | 901 | 10
38897.6396 | 1085 | 787 | 10
38897.6397 | 1256 | 919 | 10
38897.6398 | 1178 | 706 | 10
38897.64 | 1218 | 655 | 10
38897.6401 | 1216 | 637 | 10
38897.6402 | 1599 | 800 | 10
38897.6403 | 1437 | 450 | 10
38897.6405 | 1851 | 436 | 10
38897.6406 | 1779 | 238 | 10
38897.6407 | 2110 | 220 | 10
38897.6408 | 1539 | 439 | 10
38897.641 | 1685 | 308 | 10
38897.6411 | 1747 | 477 | 10
38897.6412 | 1923 | 267 | 10
38897.6413 | 2001 | 311 | 10
38897.6415 | 1834 | 301 | 10
38897.6416 | 2025 | 340 | 10
38897.6417 | 1709 | 244 | 10
38897.6418 | 1606 | 263 | 10
38897.642 | 2103 | 114 | 10
38897.6421 | 2192 | 88 | 10
38897.6422 | 1633 | 265 | 10
38897.6423 | 1728 | 294 | 10
38897.6425 | 1602 | 254 | 10
38897.6426 | 1853 | 106 | 10
38897.6427 | 1865 | 242 | 10
38897.6428 | 1607 | 349 | 10
38897.643 | 1838 | 277 | 10
38897.6431 | 1764 | 214 | 10
38897.6432 | 1861 | 228 | 10
38897.6433 | 2104 | 252 | 10
38897.6435 | 2271 | 118 | 10
38897.6436 | 1901 | 94 | 10
38897.6437 | 2274 | 90 | 10
38897.6438 | 2058 | 122 | 10
38897.644 | 2217 | 187 | 10
38897.6441 | 2068 | 176 | 10
38897.6442 | 1657 | 329 | 10
38897.6443 | 1927 | 172 | 10
38897.6445 | 1867 | 156 | 10
38897.6446 | 2207 | 116 | 10
38897.6447 | 2114 | 173 | 10
38897.6448 | 2239 | 122 | 10
38897.645 | 1997 | 276 | 10
38897.6451 | 2110 | 246 | 10
38897.6452 | 2015 | 196 | 10
38897.6453 | 1908 | 176 | 10
38897.6455 | 1747 | 185 | 10
38897.6456 | 1654 | 209 | 10
38897.6457 | 1736 | 304 | 10
38897.6458 | 1509 | 436 | 10
38897.646 | 1623 | 484 | 10
38897.6461 | 1741 | 519 | 10
38897.6462 | 1659 | 622 | 10
38897.6463 | 1611 | 522 | 10
38897.6465 | 1725 | 577 | 10
38897.6466 | 1462 | 692 | 10
38897.6467 | 1697 | 641 | 10
38897.6468 | 1385 | 751 | 10
38897.647 | 1394 | 827 | 10
38897.627 | 1 | 0 | 11
38897.6271 | 1 | 0 | 11
38897.6272 | 1 | 0 | 11
38897.6273 | 1 | 0 | 11
38897.6275 | 2 | 0 | 11
38897.6276 | 1 | 0 | 11
38897.6277 | 2 | 0 | 11
38897.6278 | 1 | 0 | 11
38897.628 | 1 | 0 | 11
38897.6281 | 1 | 0 | 11
38897.6282 | 1 | 0 | 11
38897.6283 | 2 | 0 | 11
38897.6285 | 2 | 0 | 11
38897.6286 | 1 | 0 | 11
38897.6287 | 1 | 0 | 11
38897.6288 | 2 | 0 | 11
38897.629 | 2 | 0 | 11
38897.6291 | 2 | 0 | 11
38897.6292 | 1 | 0 | 11
38897.6294 | 1 | 0 | 11
38897.6295 | 1 | 0 | 11
38897.6296 | 1 | 0 | 11
38897.6297 | 2 | 0 | 11
38897.6298 | 1 | 0 | 11
38897.63 | 1 | 0 | 11
38897.6301 | 2 | 0 | 11
38897.6302 | 1 | 0 | 11
38897.6303 | 1 | 0 | 11
38897.6305 | 1 | 0 | 11
38897.6306 | 1 | 0 | 11
38897.6307 | 1 | 0 | 11
38897.6308 | 1 | 0 | 11
38897.631 | 1 | 0 | 11
38897.6311 | 1 | 0 | 11
38897.6312 | 2 | 0 | 11
38897.6313 | 1 | 0 | 11
38897.6315 | 1 | 0 | 11
38897.6316 | 1 | 0 | 11
38897.6317 | 1 | 0 | 11
38897.6319 | 1 | 0 | 11
38897.632 | 1 | 0 | 11
38897.6321 | 1 | 0 | 11
38897.6322 | 1 | 0 | 11
38897.6323 | 1 | 0 | 11
38897.6325 | 1 | 0 | 11
38897.6326 | 1 | 0 | 11
38897.6327 | 1 | 0 | 11
38897.6328 | 1 | 0 | 11
38897.633 | 1 | 0 | 11
38897.6331 | 1 | 0 | 11
38897.6332 | 1 | 0 | 11
38897.6333 | 1 | 1 | 11
38897.6335 | 1 | 0 | 11
38897.6336 | 2 | 0 | 11
38897.6337 | 1 | 0 | 11
38897.6338 | 2 | 0 | 11
38897.634 | 1 | 0 | 11
38897.6341 | 1 | 0 | 11
38897.6342 | 1 | 0 | 11
38897.6344 | 1 | 0 | 11
38897.6345 | 1 | 0 | 11
38897.6346 | 1 | 0 | 11
38897.6347 | 1 | 0 | 11
38897.6348 | 1 | 0 | 11
38897.635 | 1 | 0 | 11
38897.6351 | 1 | 0 | 11
38897.6352 | 1 | 0 | 11
38897.6353 | 1 | 0 | 11
38897.6355 | 1 | 0 | 11
38897.6356 | 1 | 0 | 11
38897.6357 | 1 | 0 | 11
38897.6358 | 1 | 0 | 11
38897.636 | 1 | 0 | 11
38897.6361 | 1 | 0 | 11
38897.6362 | 1 | 0 | 11
38897.6363 | 1 | 0 | 11
38897.6365 | 1 | 0 | 11
38897.6366 | 1 | 0 | 11
38897.6367 | 1 | 0 | 11
38897.6369 | 2 | 0 | 11
38897.637 | 1 | 0 | 11
38897.6371 | 1 | 0 | 11
38897.6372 | 1 | 0 | 11
38897.6373 | 2 | 2 | 11
38897.6375 | 10 | 13 | 11
38897.6376 | 29 | 27 | 11
38897.6377 | 66 | 50 | 11
38897.6378 | 168 | 127 | 11
38897.638 | 314 | 260 | 11
38897.6381 | 329 | 271 | 11
38897.6382 | 395 | 324 | 11
38897.6383 | 407 | 357 | 11
38897.6385 | 903 | 762 | 11
38897.6386 | 1104 | 945 | 11
38897.6387 | 1106 | 939 | 11
38897.6388 | 995 | 851 | 11
38897.639 | 1105 | 931 | 11
38897.6391 | 992 | 881 | 11
38897.6392 | 1129 | 937 | 11
38897.6394 | 1282 | 1056 | 11
38897.6395 | 1078 | 844 | 11
38897.6396 | 1189 | 857 | 11
38897.6397 | 1116 | 734 | 11
38897.6398 | 1340 | 809 | 11
38897.64 | 1245 | 756 | 11
38897.6401 | 1249 | 686 | 11
38897.6402 | 1423 | 695 | 11
38897.6403 | 1549 | 419 | 11
38897.6405 | 1930 | 415 | 11
38897.6406 | 2024 | 234 | 11
38897.6408 | 1401 | 534 | 11
38897.641 | 2034 | 337 | 11
38897.6411 | 1874 | 511 | 11
38897.6412 | 1949 | 274 | 11
38897.6413 | 2018 | 327 | 11
38897.6415 | 1920 | 322 | 11
38897.6416 | 1954 | 262 | 11
38897.6417 | 1871 | 333 | 11
38897.6419 | 1936 | 295 | 11
38897.642 | 2266 | 113 | 11
38897.6421 | 1936 | 81 | 11
38897.6422 | 1750 | 290 | 11
38897.6423 | 1809 | 313 | 11
38897.6425 | 2051 | 248 | 11
38897.6426 | 2160 | 54 | 11
38897.6427 | 1920 | 337 | 11
38897.6428 | 1674 | 450 | 11
38897.643 | 2042 | 255 | 11
38897.6431 | 1919 | 208 | 11
38897.6432 | 2067 | 267 | 11
38897.6433 | 1856 | 231 | 11
38897.6435 | 1900 | 95 | 11
38897.6436 | 1974 | 96 | 11
38897.6437 | 2188 | 118 | 11
38897.6438 | 1979 | 112 | 11
38897.644 | 2102 | 191 | 11
38897.6441 | 2163 | 184 | 11
38897.6442 | 1784 | 414 | 11
38897.6443 | 2089 | 157 | 11
38897.6445 | 1824 | 140 | 11
38897.6446 | 1742 | 152 | 11
38897.6447 | 1850 | 162 | 11
38897.6448 | 2018 | 108 | 11
38897.645 | 2041 | 271 | 11
38897.6451 | 1682 | 193 | 11
38897.6452 | 1714 | 162 | 11
38897.6453 | 1964 | 190 | 11
38897.6455 | 1962 | 196 | 11
38897.6456 | 1840 | 205 | 11
38897.6457 | 1902 | 299 | 11
38897.6458 | 1844 | 549 | 11
38897.646 | 1710 | 503 | 11
38897.6461 | 1773 | 606 | 11
38897.6462 | 1686 | 670 | 11
38897.6463 | 1411 | 687 | 11
38897.6465 | 1589 | 783 | 11
38897.6466 | 1667 | 786 | 11
38897.6467 | 1450 | 699 | 11
38897.6468 | 1557 | 778 | 11
38897.647 | 1292 | 712 | 11
38897.627 | 2 | 0 | 12
38897.6271 | 1 | 0 | 12
38897.6272 | 1 | 0 | 12
38897.6274 | 1 | 0 | 12
38897.6275 | 1 | 0 | 12
38897.6276 | 1 | 0 | 12
38897.6277 | 1 | 0 | 12
38897.6279 | 1 | 0 | 12
38897.628 | 1 | 0 | 12
38897.6281 | 1 | 0 | 12
38897.6282 | 1 | 0 | 12
38897.6284 | 2 | 0 | 12
38897.6285 | 1 | 0 | 12
38897.6286 | 1 | 0 | 12
38897.6287 | 1 | 0 | 12
38897.6289 | 1 | 0 | 12
38897.629 | 1 | 0 | 12
38897.6291 | 1 | 0 | 12
38897.6292 | 1 | 0 | 12
38897.6294 | 1 | 0 | 12
38897.6295 | 1 | 0 | 12
38897.6297 | 1 | 0 | 12
38897.6299 | 1 | 0 | 12
38897.63 | 1 | 0 | 12
38897.6301 | 1 | 0 | 12
38897.6302 | 2 | 0 | 12
38897.6304 | 1 | 0 | 12
38897.6305 | 1 | 0 | 12
38897.6306 | 2 | 0 | 12
38897.6307 | 1 | 0 | 12
38897.6309 | 1 | 0 | 12
38897.631 | 1 | 0 | 12
38897.6311 | 1 | 0 | 12
38897.6312 | 1 | 0 | 12
38897.6314 | 1 | 0 | 12
38897.6315 | 1 | 0 | 12
38897.6316 | 1 | 0 | 12
38897.6317 | 1 | 0 | 12
38897.6319 | 2 | 0 | 12
38897.632 | 1 | 0 | 12
38897.6321 | 1 | 0 | 12
38897.6322 | 1 | 0 | 12
38897.6324 | 1 | 0 | 12
38897.6325 | 1 | 0 | 12
38897.6326 | 2 | 0 | 12
38897.6327 | 1 | 0 | 12
38897.6329 | 1 | 0 | 12
38897.633 | 1 | 0 | 12
38897.6331 | 1 | 0 | 12
38897.6332 | 1 | 0 | 12
38897.6334 | 1 | 0 | 12
38897.6335 | 1 | 0 | 12
38897.6336 | 2 | 0 | 12
38897.6337 | 1 | 0 | 12
38897.6339 | 1 | 0 | 12
38897.634 | 1 | 0 | 12
38897.6341 | 1 | 0 | 12
38897.6342 | 1 | 0 | 12
38897.6344 | 1 | 0 | 12
38897.6345 | 1 | 0 | 12
38897.6346 | 1 | 0 | 12
38897.6347 | 1 | 0 | 12
38897.6349 | 1 | 0 | 12
38897.635 | 1 | 0 | 12
38897.6351 | 1 | 0 | 12
38897.6352 | 1 | 0 | 12
38897.6354 | 1 | 0 | 12
38897.6355 | 1 | 0 | 12
38897.6356 | 1 | 0 | 12
38897.6357 | 1 | 0 | 12
38897.6359 | 1 | 0 | 12
38897.636 | 1 | 0 | 12
38897.6361 | 1 | 0 | 12
38897.6362 | 1 | 0 | 12
38897.6364 | 1 | 0 | 12
38897.6365 | 1 | 0 | 12
38897.6366 | 1 | 0 | 12
38897.6367 | 1 | 0 | 12
38897.6369 | 1 | 0 | 12
38897.637 | 1 | 0 | 12
38897.6371 | 1 | 0 | 12
38897.6372 | 1 | 0 | 12
38897.6374 | 35 | 5 | 12
38897.6375 | 72 | 10 | 12
38897.6376 | 143 | 33 | 12
38897.6377 | 213 | 61 | 12
38897.6379 | 382 | 220 | 12
38897.638 | 357 | 231 | 12
38897.6381 | 469 | 287 | 12
38897.6382 | 575 | 381 | 12
38897.6384 | 696 | 555 | 12
38897.6385 | 1059 | 894 | 12
38897.6386 | 949 | 798 | 12
38897.6387 | 1271 | 1028 | 12
38897.6389 | 1123 | 952 | 12
38897.639 | 1263 | 1074 | 12
38897.6391 | 1097 | 918 | 12
38897.6392 | 1147 | 951 | 12
38897.6394 | 1032 | 834 | 12
38897.6395 | 1235 | 966 | 12
38897.6396 | 1379 | 1004 | 12
38897.6397 | 1256 | 914 | 12
38897.6399 | 1348 | 886 | 12
38897.64 | 1219 | 697 | 12
38897.6401 | 1509 | 787 | 12
38897.6402 | 1567 | 648 | 12
38897.6404 | 1645 | 556 | 12
38897.6405 | 1601 | 301 | 12
38897.6406 | 1771 | 190 | 12
38897.6407 | 1962 | 217 | 12
38897.6409 | 1699 | 587 | 12
38897.641 | 1906 | 295 | 12
38897.6411 | 1615 | 326 | 12
38897.6412 | 1804 | 256 | 12
38897.6414 | 2049 | 324 | 12
38897.6415 | 1882 | 346 | 12
38897.6416 | 1986 | 325 | 12
38897.6417 | 1763 | 263 | 12
38897.6419 | 1688 | 248 | 12
38897.642 | 1898 | 99 | 12
38897.6421 | 2152 | 136 | 12
38897.6422 | 1720 | 288 | 12
38897.6424 | 2040 | 366 | 12
38897.6425 | 1862 | 212 | 12
38897.6426 | 1988 | 67 | 12
38897.6427 | 1955 | 341 | 12
38897.6429 | 1654 | 380 | 12
38897.643 | 1649 | 211 | 12
38897.6431 | 1787 | 214 | 12
38897.6432 | 1997 | 252 | 12
38897.6434 | 2087 | 199 | 12
38897.6435 | 2259 | 91 | 12
38897.6436 | 2288 | 116 | 12
38897.6437 | 2289 | 130 | 12
38897.6439 | 2027 | 129 | 12
38897.644 | 2214 | 192 | 12
38897.6441 | 1785 | 155 | 12
38897.6442 | 1649 | 319 | 12
38897.6444 | 1794 | 118 | 12
38897.6445 | 2001 | 136 | 12
38897.6446 | 2075 | 211 | 12
38897.6447 | 1978 | 177 | 12
38897.6449 | 2234 | 132 | 12
38897.645 | 2120 | 208 | 12
38897.6451 | 1974 | 201 | 12
38897.6452 | 1939 | 215 | 12
38897.6454 | 2112 | 219 | 12
38897.6455 | 2187 | 225 | 12
38897.6456 | 2056 | 251 | 12
38897.6457 | 1715 | 316 | 12
38897.6459 | 1506 | 424 | 12
38897.646 | 1858 | 452 | 12
38897.6461 | 1486 | 548 | 12
38897.6462 | 1418 | 474 | 12
38897.6464 | 1394 | 614 | 12
38897.6465 | 1606 | 709 | 12
38897.6466 | 1428 | 594 | 12
38897.6467 | 1555 | 824 | 12
38897.6469 | 1530 | 769 | 12
38897.647 | 1712 | 835 | 12