## Test Facts
Last row in IRMS data sheets: | 147
Time when Penlight power was initiated: | 90 s

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 3
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.7 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 90 seconds of baseline data monitoring. Special Note: This test is identical to Penlight Test 2.
DAQ Time | Penlight Time | Event | Interpretation
90 | 0 | Initiate Penlight Heating
880 | 790 | Conductor 1 shorts to Drain wire at less than 1000 ohms (645) | First short circuit inditations are between conductor 1 and the un-insulated drain wire
889 (next cycle) | 799 (next cycle) | Conductor 1 shows momentary short to drain wire at less than 1000 ohms (820)
892, 899 | 802, 809 | Drain wire and Conductor 1 short to external ground at less than 1000 ohms. | First indications of interaction with external ground are short-lived (one cycle)
905 | 815 | Conductor 2 shorts to drain wire at less than 1000 ohms. | Intra-cable shorting occurs between conductors and un-insulated drain wire eventually forming a single common intra-cable shorting group.
910 (next cycle) | 820 (next cycle) | Conductor 3 shorts to Conductor 1 at less than 1000 ohms.
945 | 855 | Conductor 3 shorts to External Ground at less than 1000 ohms | Intermittent shorts to external ground are again observed followed shortly by more persistent external ground shorts, all just slightly greater than one minute after the first indications of serious degradation (at 880s).
960 | 870 | Conductor 3 shorts to drain wire at less than 1000 ohms.
966 | 876 | Conductor 2 shorts to external ground initially at less than 100 ohms, recovering to 100-1000 ohms for next measurement cycle
1093 | 1003 | All conductors and drain show essentially persistent shorts to external ground at less than 100. The last conductor to short to the external ground at less than 100 ohms is Conductor 3. | All conductors have shorted to ground.
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | This test followed a somewhat complex behavior relative to the external ground. In this case there were earlier indications of shorts between one insulated conductor and ground, and the progression from initial faults to shorts to external ground progressed rather quickly.
Observation 3 | This test was a direct repeat of Penlight Test 3, and there is a great deal of consistency. The initial fault times are quite similar (729s for Test 2, versus 695s for Test 3 after start of heating). The initial shorting behavior and transitions are also very consistent between the two tests.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 3 |  |  | 2006-07-05 | 14:09
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-87.5 | 234838 |  | -85 | 232038 | -83.8333 | 234638 | -82.6667 | 235138 | -87.5 | 232038
-76.5 | 232038 |  | -74.3333 | 232038 | -73 | 234638 | -71.8333 | 235138 | -76.5 | 232038
-65.8333 | 232038 |  | -63.5 | 232038 | -62.1667 | 234638 | -61.1667 | 235138 | -65.8333 | 232038
-55.1667 | 232038 |  | -52.5 | 232038 | -51.5 | 234638 | -50.1667 | 235138 | -55.1667 | 232038
-44.5 | 232038 |  | -41.8333 | 232038 | -40.8333 | 234638 | -39.5 | 235138 | -44.5 | 232038
-33.5 | 232038 |  | -31.1667 | 232038 | -29.8333 | 234638 | -28.8333 | 235138 | -33.5 | 232038
-22.5 | 232038 |  | -20.5 | 232038 | -19.1667 | 234638 | -17.8333 | 235138 | -22.5 | 232038
-11.6667 | 232038 |  | -9.5 | 78312.6667 | -8.1667 | 234638 | -7 | 235138 | -11.6667 | 78312.6667
-1.1667 | 232038 |  | 1.5 | 232038 | 2.5 | 234638 | 3.8333 | 235138 | -1.1667 | 232038
9.5 | 232038 |  | 12.1667 | 232038 | 13.1667 | 234638 | 14.5 | 235138 | 9.5 | 232038
20.5 | 232038 |  | 23 | 232038 | 24.1667 | 234638 | 25.3333 | 235138 | 20.5 | 232038
31.5 | 232038 |  | 33.6667 | 232038 | 35 | 234638 | 36.1667 | 235138 | 31.5 | 232038
42.3333 | 232038 |  | 44.5 | 232038 | 45.8333 | 234638 | 47 | 235138 | 42.3333 | 232038
53 | 232038 |  | 55.5 | 232038 | 56.6667 | 234638 | 57.8333 | 235138 | 53 | 232038
63.5 | 232038 |  | 66.1667 | 232038 | 67.1667 | 234638 | 68.5 | 235138 | 63.5 | 232038
74.5 | 232038 |  | 76.8333 | 232038 | 78.1667 | 118169 | 79.1667 | 235138 | 74.5 | 118169
85.5 | 117369 |  | 87.6667 | 115969 | 89 | 234638 | 90.1667 | 235138 | 85.5 | 115969
96.3333 | 232038 |  | 98.5 | 232038 | 99.8333 | 234638 | 101 | 235138 | 96.3333 | 232038
107 | 232038 |  | 109.5 | 232038 | 110.6667 | 234638 | 111.8333 | 235138 | 107 | 232038
117.5 | 115969 |  | 120.1667 | 232038 | 121.1667 | 234638 | 122.5 | 118169 | 117.5 | 115969
128.5 | 232038 |  | 130.8333 | 232038 | 132.1667 | 234638 | 133.1667 | 235138 | 128.5 | 232038
139.5 | 232038 |  | 141.6667 | 232038 | 143 | 234638 | 144.1667 | 235138 | 139.5 | 232038
150.3333 | 232038 |  | 152.5 | 232038 | 153.8333 | 234638 | 155 | 235138 | 150.3333 | 232038
161 | 232038 |  | 163.5 | 232038 | 164.6667 | 234638 | 165.8333 | 235138 | 161 | 232038
171.6667 | 232038 |  | 174.3333 | 115969 | 175.1667 | 234638 | 176.5 | 118069 | 171.6667 | 115969
182.5 | 117369 |  | 184.8333 | 232038 | 186.1667 | 234638 | 187.1667 | 235138 | 182.5 | 117369
193.5 | 232038 |  | 195.5 | 232038 | 196.8333 | 117369 | 198.1667 | 235138 | 193.5 | 117369
204.3333 | 232038 |  | 206.5 | 232038 | 207.8333 | 234638 | 209 | 235138 | 204.3333 | 232038
215 | 232038 |  | 217.5 | 117269 | 218.6667 | 234638 | 219.8333 | 235138 | 215 | 117269
225.6667 | 117369 |  | 228.3333 | 232038 | 229.3333 | 234638 | 230.6667 | 235138 | 225.6667 | 117369
236.5 | 232038 |  | 238.8333 | 232038 | 240.1667 | 234638 | 241.1667 | 235138 | 236.5 | 232038
247.5 | 232038 |  | 249.5 | 232038 | 250.8333 | 234638 | 252.1667 | 235138 | 247.5 | 232038
258.1667 | 118069 |  | 260.5 | 232038 | 261.8333 | 234638 | 262.8333 | 235138 | 258.1667 | 118069
268.8333 | 232038 |  | 271.5 | 232038 | 272.5 | 234638 | 273.8333 | 235138 | 268.8333 | 232038
279.5 | 232038 |  | 282.1667 | 232038 | 283.1667 | 234638 | 284.5 | 118069 | 279.5 | 118069
290.5 | 232038 |  | 292.8333 | 232038 | 294.1667 | 234638 | 295.1667 | 235138 | 290.5 | 232038
301.5 | 232038 |  | 303.5 | 117519 | 304.8333 | 117269 | 306.1667 | 235138 | 301.5 | 117269
312.1667 | 232038 |  | 314.5 | 117269 | 315.8333 | 234638 | 316.8333 | 235138 | 312.1667 | 117269
322.8333 | 232038 |  | 325.5 | 232038 | 326.5 | 117369 | 327.8333 | 235138 | 322.8333 | 117369
333.5 | 232038 |  | 336.1667 | 232038 | 337.1667 | 234638 | 338.5 | 235138 | 333.5 | 232038
344.5 | 232038 |  | 346.8333 | 232038 | 348.1667 | 234638 | 349.1667 | 235138 | 344.5 | 232038
355.5 | 232038 |  | 357.5 | 232038 | 358.8333 | 234638 | 360.1667 | 235138 | 355.5 | 232038
366.1667 | 232038 |  | 368.5 | 232038 | 369.8333 | 234638 | 370.8333 | 235138 | 366.1667 | 232038
376.8333 | 232038 |  | 379.5 | 232038 | 380.5 | 234638 | 381.8333 | 235138 | 376.8333 | 232038
387.5 | 232038 |  | 390.1667 | 232038 | 391.1667 | 234638 | 392.5 | 235138 | 387.5 | 232038
398.5 | 232038 |  | 400.8333 | 117269 | 402.1667 | 234638 | 403.1667 | 235138 | 398.5 | 117269
409.3333 | 232038 |  | 411.5 | 232038 | 412.8333 | 234638 | 414 | 235138 | 409.3333 | 232038
420.1667 | 232038 |  | 422.5 | 232038 | 423.8333 | 234638 | 424.8333 | 235138 | 420.1667 | 232038
430.8333 | 232038 |  | 433.5 | 232038 | 434.5 | 234638 | 435.8333 | 235138 | 430.8333 | 232038
441.5 | 232038 |  | 444 | 232038 | 445.1667 | 234638 | 446.3333 | 235138 | 441.5 | 232038
452.5 | 232038 |  | 454.6667 | 232038 | 456 | 234638 | 457.1667 | 235138 | 452.5 | 232038
463.5 | 232038 |  | 465.5 | 232038 | 466.8333 | 234638 | 468.1667 | 235138 | 463.5 | 232038
474.1667 | 117369 |  | 476.5 | 232038 | 477.8333 | 234638 | 478.8333 | 235138 | 474.1667 | 117369
484.8333 | 232038 |  | 487.5 | 232038 | 488.5 | 234638 | 489.8333 | 235138 | 484.8333 | 232038
495.5 | 232038 |  | 498.1667 | 232038 | 499.1667 | 234638 | 500.5 | 235138 | 495.5 | 232038
506.5 | 232038 |  | 508.6667 | 232038 | 510 | 234638 | 511.1667 | 235138 | 506.5 | 232038
517.3333 | 232038 |  | 519.5 | 115969 | 520.8333 | 234638 | 522 | 235138 | 517.3333 | 115969
528 | 232038 |  | 530.5 | 232038 | 531.6667 | 118169 | 532.8333 | 235138 | 528 | 118169
538.6667 | 232038 |  | 541.3333 | 115969 | 542.3333 | 234638 | 543.6667 | 235138 | 538.6667 | 115969
549.5 | 115969 |  | 552 | 232038 | 553.1667 | 234638 | 554.3333 | 235138 | 549.5 | 115969
560.5 | 232038 |  | 562.8333 | 232038 | 564.1667 | 117269 | 565.1667 | 235138 | 560.5 | 117269
571.3333 | 232038 |  | 573.5 | 232038 | 574.8333 | 234638 | 576 | 235138 | 571.3333 | 232038
582.1667 | 232038 |  | 584.5 | 232038 | 585.8333 | 234638 | 586.8333 | 118169 | 582.1667 | 118169
592.8333 | 232038 |  | 595.5 | 232038 | 596.5 | 234638 | 597.8333 | 235138 | 592.8333 | 232038
603.5 | 118069 |  | 606.1667 | 232038 | 607.1667 | 234638 | 608.5 | 118069 | 603.5 | 118069
614.5 | 232038 |  | 616.8333 | 232038 | 618.1667 | 117369 | 619.1667 | 235138 | 614.5 | 117369
625.5 | 232038 |  | 627.5 | 232038 | 628.8333 | 234638 | 630.1667 | 235138 | 625.5 | 232038
636.1667 | 232038 |  | 638.5 | 232038 | 639.8333 | 234638 | 640.8333 | 235138 | 636.1667 | 232038
646.8333 | 232038 |  | 649.5 | 232038 | 650.3333 | 234638 | 651.6667 | 235138 | 646.8333 | 232038
657.5 | 232038 |  | 660 | 232038 | 661.1667 | 234638 | 662.3333 | 235138 | 657.5 | 232038
668.5 | 232038 |  | 670.6667 | 232038 | 672 | 234638 | 673.1667 | 235138 | 668.5 | 232038
679.5 | 232038 |  | 681.5 | 232038 | 682.8333 | 234638 | 684.1667 | 235138 | 679.5 | 232038
690.1667 | 232038 |  | 692.5 | 232038 | 693.8333 | 234638 | 694.8333 | 235138 | 690.1667 | 232038
700.8333 | 232038 |  | 703.5 | 232038 | 704.5 | 234638 | 705.8333 | 235138 | 700.8333 | 232038
711.5 | 232038 |  | 714.1667 | 232038 | 715.1667 | 234638 | 716.5 | 235138 | 711.5 | 232038
722.5 | 232038 |  | 724.8333 | 232038 | 726.1667 | 234638 | 727.1667 | 235138 | 722.5 | 232038
733.5 | 232038 |  | 735.5 | 232038 | 736.8333 | 234638 | 738.1667 | 235138 | 733.5 | 232038
744 | 232038 |  | 746.5 | 232038 | 747.6667 | 234638 | 748.8333 | 235138 | 744 | 232038
754.6667 | 232038 |  | 757.3333 | 232038 | 758.3333 | 234638 | 759.6667 | 235138 | 754.6667 | 232038
765.5 | 15655.8667 |  | 768 | 232038 | 769.1667 | 234638 | 770.3333 | 8989.9231 | 765.5 | 8989.9231
776.5 | 3440.9099 |  | 778.8333 | 232038 | 780.1667 | 234638 | 781.1667 | 1700.3146 | 776.5 | 1700.3146
787.5 | 2752.7107 |  | 789.5 | 232038 | 790.8333 | 234638 | 792.1667 | 1006.0893 | 787.5 | 1006.0893
798 | 1879.033 |  | 800.5 | 29993.454 | 801.6667 | 5609.4689 | 802.8333 | 655.6882 | 798 | 655.6882
808.6667 | 703.8953 |  | 811.3333 | 4037.6816 | 812.3333 | 2591.2499 | 813.6667 | 746.0471 | 808.6667 | 703.8953
819.5 | 661.9025 |  | 822.1667 | 1520.8 | 823.1667 | 1442.1864 | 824.5 | 534.7277 | 819.5 | 534.7277
830.5 | 544.7652 |  | 833 | 1351.7527 | 834.3333 | 1249.2154 | 835.1667 | 486.3036 | 830.5 | 486.3036
841.3333 | 616.5223 |  | 843.5 | 1221.7764 | 844.8333 | 1178.9056 | 846 | 516.2172 | 841.3333 | 516.2172
852 | 720.3872 |  | 854.5 | 1051.6317 | 855.6667 | 815.4116 | 856.8333 | 543.831 | 852 | 543.831
862.6667 | 702.3908 |  | 865.3333 | 1040.9029 | 866.5 | 642.6114 | 867.8333 | 392.3932 | 862.6667 | 392.3932
873.5 | 697.3827 |  | 876 | 42.4357 | 877.1667 | 965.5806 | 878.3333 | 47.2049 | 873.5 | 42.4357
884.5 | 355.6549 |  | 886.6667 | 743.5173 | 888 | 284.8089 | 889.1667 | 469.0066 | 884.5 | 284.8089
895.3333 | 104.3472 |  | 897.5 | 202.4672 | 898.8333 | 794.9261 | 900 | 454.3325 | 895.3333 | 104.3472
906 | 814.7406 |  | 908.5 | 333.1751 | 909.6667 | 375.1668 | 910.8333 | 327.7993 | 906 | 327.7993
916.6667 | 262.1589 |  | 919.3333 | 174.4117 | 920.1667 | 724.1388 | 921.5 | 284.9265 | 916.6667 | 174.4117
927.5 | 47.2129 |  | 930 | 56.598 | 931.1667 | 394.3387 | 932.3333 | 402.0284 | 927.5 | 47.2129
938.5 | 418.6516 |  | 940.6667 | 407.4338 | 942 | 215.9992 | 943.1667 | 297.8205 | 938.5 | 215.9992
949.3333 | 311.4569 |  | 951.5 | 300.0055 | 952.8333 | 196.9232 | 954 | 934.6673 | 949.3333 | 196.9232
960 | 128.1114 |  | 962.5 | 182.5231 | 963.6667 | 185.5175 | 964.8333 | 179.564 | 960 | 128.1114
970.6667 | 297.7989 |  | 973.3333 | 222.6702 | 974.3333 | 256.6411 | 975.6667 | 183.9638 | 970.6667 | 183.9638
981.5 | 226.9502 |  | 984 | 165.811 | 985.1667 | 216.8835 | 986.3333 | 181.3135 | 981.5 | 165.811
992.5 | 208.6258 |  | 994.6667 | 348.8305 | 996 | 103.9581 | 997.1667 | 194.8643 | 992.5 | 103.9581
1003.3333 | 35.1953 |  | 1005.5 | 33.3251 | 1006.8333 | 62.631 | 1008 | 90.5381 | 1003.3333 | 33.3251
1014 | 121.1688 |  | 1016.5 | 74.0435 | 1017.6667 | 52.5737 | 1018.8333 | 84.2706 | 1014 | 52.5737
1024.6667 | 338.5705 |  | 1027.3333 | 53.8814 | 1028.1667 | 170.7696 | 1029.5 | 74.0398 | 1024.6667 | 53.8814
1035.5 | 32.8526 |  | 1038 | 38.5748 | 1039.1667 | 206.7892 | 1040.3333 | 304.9014 | 1035.5 | 32.8526
1046.5 | 373.1359 |  | 1048.6667 | 251.4712 | 1050 | 128.0143 | 1051.1667 | 173.0384 | 1046.5 | 128.0143
1057.3333 | 53.4843 |  | 1059.5 | 51.4314 | 1060.8333 | 41.3837 | 1062 | 111.6637 | 1057.3333 | 41.3837
1068 | 33.471 |  | 1070.5 | 30.1668 | 1071.6667 | 58.8288 | 1072.8333 | 73.1085 | 1068 | 30.1668
1078.6667 | 43.1397 |  | 1081.3333 | 224.2451 | 1082.3333 | 43.0691 | 1083.6667 | 86.6868 | 1078.6667 | 43.0691
1089.5 | 21.987 |  | 1092 | 64.7869 | 1093.1667 | 84.5918 | 1094.3333 | 33.1914 | 1089.5 | 21.987
1100.5 | 31.481 |  | 1102.6667 | 33.128 | 1104 | 62.0966 | 1105.1667 | 104.4289 | 1100.5 | 31.481
1111.3333 | 55.6525 |  | 1113.5 | 49.954 | 1114.8333 | 65.0936 | 1116 | 79.9398 | 1111.3333 | 49.954
1122 | 39.297 |  | 1124.5 | 58.0101 | 1125.6667 | 64.8246 | 1126.8333 | 55.7115 | 1122 | 39.297
1132.6667 | 2.7116 |  | 1135.3333 | 41.3829 | 1136.3333 | 45.3596 | 1137.6667 | 3.2931 | 1132.6667 | 2.7116
1143.5 | 3.8455 |  | 1146 | 7.1959 | 1147.1667 | 3.3942 | 1148.3333 | 1.8904 | 1143.5 | 1.8904
1154.5 | 0.14351 |  | 1156.6667 | 0.71933 | 1158 | 6.3829 | 1159.1667 | 0.47164 | 1154.5 | 0.14351
1165.1667 | 0.42886 |  | 1167.5 | 3.5821 | 1168.8333 | 15.7768 | 1169.8333 | 1.0551 | 1165.1667 | 0.42886
1176 | 3.7496 |  | 1178.5 | 3.8459 | 1179.6667 | 4.8065 | 1180.8333 | 4.6058 | 1176 | 3.7496
1186.5 | 1.1897 |  | 1189.1667 | 0.35718 | 1190.3333 | 0.66114 | 1191.6667 | 0.35967 | 1186.5 | 0.35718
1197.5 | 13.9345 |  | 1200 | 3.5305 | 1201.1667 | 6.7756 | 1202.3333 | 11.4204 | 1197.5 | 3.5305
1208.5 | 14.2946 |  | 1210.6667 | 10.0296 | 1212 | 6.2532 | 1213.1667 | 18.9819 | 1208.5 | 6.2532
1219.1667 | 2.1486 |  | 1221.5 | 6.1867 | 1222.8333 | 15.5172 | 1223.8333 | 5.4866 | 1219.1667 | 2.1486
1230 | 18.8302 |  | 1232.5 | 16.7773 | 1233.6667 | 9.0331 | 1234.8333 | 20.3706 | 1230 | 9.0331
1240.6667 | 17.4317 |  | 1243.3333 | 4.5218 | 1244.1667 | 12.1419 | 1245.5 | 16.1457 | 1240.6667 | 4.5218
1251.5 | 6.6749 |  | 1253.8333 | 28.1948 | 1255.1667 | 2.4336 | 1256.1667 | 11.0324 | 1251.5 | 2.4336
1262.5 | 20.5886 |  | 1264.6667 | 3.7115 | 1266 | 3.4327 | 1267.1667 | 26.7967 | 1262.5 | 3.4327
1273.1667 | 10.0719 |  | 1275.5 | 19.4271 | 1276.8333 | 3.4849 | 1277.8333 | 8.0819 | 1273.1667 | 3.4849
1283.8333 | 42.3853 |  | 1286.5 | 5.4976 | 1287.5 | 6.59 | 1288.8333 | 29.8643 | 1283.8333 | 5.4976
1294.5 | 28.1531 |  | 1297.1667 | 6.3007 | 1298.1667 | 14.535 | 1299.5 | 7.4084 | 1294.5 | 6.3007
1305.5 | 4.8887 |  | 1307.8333 | 10.6763 | 1309.1667 | 39.4897 | 1310.1667 | 22.477 | 1305.5 | 4.8887
1316.5 | 8.4624 |  | 1318.6667 | 3.9451 | 1320 | 26.1919 | 1321.1667 | 7.5596 | 1316.5 | 3.9451
1327.3333 | 12.7422 |  | 1329.5 | 8.0746 | 1330.8333 | 13.2303 | 1332 | 35.5463 | 1327.3333 | 8.0746
1338 | 7.3678 |  | 1340.5 | 5.006 | 1341.6667 | 11.3316 | 1342.8333 | 10.8369 | 1338 | 5.006
1348.6667 | 2.8563 |  | 1351.3333 | 32.2955 | 1352.3333 | 5.4705 | 1353.6667 | 12.8504 | 1348.6667 | 2.8563
1359.5 | 5.54 |  | 1361.8333 | 6.1921 | 1363.1667 | 4.7491 | 1364.1667 | 8.4768 | 1359.5 | 4.7491
1370.5 | 6.7032 |  | 1372.6667 | 9.0314 | 1374 | 8.1759 | 1375.1667 | 14.0857 | 1370.5 | 6.7032
1381.1667 | 0.51666 |  | 1383.5 | 10.8207 | 1384.8333 | 1.2755 | 1385.8333 | 6.7788 | 1381.1667 | 0.51666
1392 | 8.1828 |  | 1394.5 | 8.9048 | 1395.6667 | 3.1535 | 1396.8333 | 5.6019 | 1392 | 3.1535
1402.6667 | 12.0802 |  | 1405.3333 | 3.5827 | 1406.1667 | 4.5309 | 1407.5 | 1.5598 | 1402.6667 | 1.5598
1413.5 | 0.6351 |  | 1415.8333 | 26.4767 | 1417.1667 | 0.33702 | 1418.1667 | 6.5668 | 1413.5 | 0.33702
1424.5 | 1.9842 |  | 1426.6667 | 0.82927 | 1428 | 16.3397 | 1429.1667 | 6.9483 | 1424.5 | 0.82927
1435.1667 | 2.2896 |  | 1437.5 | 32.9537 | 1438.8333 | 1.1671 | 1439.8333 | 0.23257 | 1435.1667 | 0.23257

## C-C
Conductor to Conductor Resistances
Penlight Test 3 |  |  | 2006-07-05 | 14:09
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-89.5 | 231838.0862 | -87.5 | 234837.9994 | -85.5 | 236237.9994 | -83.5 | 234637.9994 | -82 | 235137.9994 | -80.5 | 236437.9994 | -89.5 | 231838.0862
-78.5 | 232037.9994 | -76.5 | 234837.9994 | -74.5 | 236237.9994 | -73 | 234637.9994 | -71.5 | 235137.9994 | -69.5 | 236437.9994 | -78.5 | 232037.9994
-67.5 | 232037.9994 | -65.5 | 234837.9994 | -64.5 | 236237.9994 | -62.5 | 234637.9994 | -60.5 | 235137.9994 | -58.5 | 236437.9994 | -67.5 | 232037.9994
-56.5 | 232037.9994 | -55.5 | 234837.9994 | -53.5 | 236237.9994 | -51.5 | 234637.9994 | -49.5 | 235137.9994 | -47.5 | 236437.9994 | -56.5 | 232037.9994
-46.5 | 232037.9994 | -44.5 | 234837.9994 | -42.5 | 236237.9994 | -40.5 | 234637.9994 | -38.5 | 235137.9994 | -37.5 | 236437.9994 | -46.5 | 232037.9994
-35.5 | 232037.9994 | -33.5 | 234837.9994 | -31.5 | 236237.9994 | -29.5 | 234637.9994 | -28.5 | 235137.9994 | -26.5 | 236437.9994 | -35.5 | 232037.9994
-24.5 | 232037.9994 | -22.5 | 234837.9994 | -20.5 | 236237.9994 | -19.5 | 234637.9994 | -17.5 | 235137.9994 | -15.5 | 236437.9994 | -24.5 | 232037.9994
-13.5 | 232037.9994 | -11.5 | 234837.9994 | -10 | 236237.9994 | -8.5 | 234637.9994 | -6.5 | 78312.6648 | -4.5 | 236437.9994 | -13.5 | 78312.6648
-2.5 | 232037.9994 | -1.5 | 234837.9994 | 0.5 | 236237.9994 | 2.5 | 234637.9994 | 4.5 | 235137.9994 | 6.5 | 236437.9994 | -2.5 | 232037.9994
7.5 | 232037.9994 | 9.5 | 234837.9994 | 11.5 | 236237.9994 | 13.5 | 234637.9994 | 15.5 | 235137.9994 | 16.5 | 236437.9994 | 7.5 | 232037.9994
18.5 | 232037.9994 | 20.5 | 234837.9994 | 22.5 | 236237.9994 | 24.5 | 234637.9994 | 26 | 235137.9994 | 27.5 | 236437.9994 | 18.5 | 232037.9994
29.5 | 232037.9994 | 31.5 | 234837.9994 | 33.5 | 236237.9994 | 35 | 234637.9994 | 36.5 | 235137.9994 | 38.5 | 236437.9994 | 29.5 | 232037.9994
40.5 | 232037.9994 | 42.5 | 234837.9994 | 44 | 236237.9994 | 45.5 | 234637.9994 | 47.5 | 235137.9994 | 49.5 | 236437.9994 | 40.5 | 232037.9994
51.5 | 232037.9994 | 53 | 234837.9994 | 54.5 | 236237.9994 | 56.5 | 234438.0852 | 58.5 | 235137.9994 | 60.5 | 236437.9994 | 51.5 | 232037.9994
61.5 | 232037.9994 | 63.5 | 234837.9994 | 65.5 | 236237.9994 | 67.5 | 234637.9994 | 69.5 | 235137.9994 | 70.5 | 236437.9994 | 61.5 | 232037.9994
72.5 | 232037.9994 | 74.5 | 234837.9994 | 76.5 | 236237.9994 | 78.5 | 234637.9994 | 79.5 | 234838.1275 | 81.5 | 118168.9988 | 72.5 | 118168.9988
83.5 | 232037.9994 | 85.5 | 117368.9988 | 87.5 | 118068.9988 | 89 | 234637.9994 | 90.5 | 235137.9994 | 92.5 | 236437.9994 | 83.5 | 117368.9988
94.5 | 232037.9994 | 96.5 | 234837.9994 | 98 | 236237.9994 | 99.5 | 234637.9994 | 101.5 | 235137.9994 | 103.5 | 236437.9994 | 94.5 | 232037.9994
105.5 | 232037.9994 | 107 | 234837.9994 | 108.5 | 236237.9994 | 110.5 | 234637.9994 | 112.5 | 235137.9994 | 114.5 | 236238.0846 | 105.5 | 232037.9994
115.5 | 115968.9988 | 117.5 | 234837.9994 | 119.5 | 236237.9994 | 121.5 | 234637.9994 | 123.5 | 235137.9994 | 124.5 | 236437.9994 | 115.5 | 115968.9988
126.5 | 232037.9994 | 128.5 | 234837.9994 | 130.5 | 236237.9994 | 132.5 | 234637.9994 | 133.5 | 235137.9994 | 135.5 | 236437.9994 | 126.5 | 232037.9994
137.5 | 232037.9994 | 139.5 | 234837.9994 | 141.5 | 236237.9994 | 143 | 234637.9994 | 144.5 | 235137.9994 | 146.5 | 236437.9994 | 137.5 | 232037.9994
148.5 | 232037.9994 | 150.5 | 234837.9994 | 152 | 236237.9994 | 153.5 | 234637.9994 | 155.5 | 235137.9994 | 157.5 | 236437.9994 | 148.5 | 232037.9994
159.5 | 232037.9994 | 161 | 234837.9994 | 162.5 | 236237.9994 | 164.5 | 234637.9994 | 166.5 | 235137.9994 | 168.5 | 236437.9994 | 159.5 | 232037.9994
170 | 232037.9994 | 171.5 | 234837.9994 | 173.5 | 236237.9994 | 175.5 | 234637.9994 | 177.5 | 235137.9994 | 178.5 | 236437.9994 | 170 | 232037.9994
180.5 | 232037.9994 | 182.5 | 117368.9988 | 184.5 | 236237.9994 | 186.5 | 234637.9994 | 187.5 | 235137.9994 | 189.5 | 236437.9994 | 180.5 | 117368.9988
191.5 | 232037.9994 | 193.5 | 234837.9994 | 195.5 | 236237.9994 | 196.5 | 234637.9994 | 198.5 | 235137.9994 | 200.5 | 236437.9994 | 191.5 | 232037.9994
202.5 | 232037.9994 | 204.5 | 234837.9994 | 206 | 236237.9994 | 207.5 | 234637.9994 | 209.5 | 235137.9994 | 211.5 | 236437.9994 | 202.5 | 232037.9994
213.5 | 232037.9994 | 215 | 234837.9994 | 216.5 | 236237.9994 | 218.5 | 117268.9988 | 220.5 | 235137.9994 | 222.5 | 236437.9994 | 213.5 | 117268.9988
224 | 232037.9994 | 225.5 | 117368.9988 | 227.5 | 236237.9994 | 229.5 | 234438.0852 | 231.5 | 235137.9994 | 233 | 236437.9994 | 224 | 117368.9988
234.5 | 232037.9994 | 236.5 | 234837.9994 | 238.5 | 236237.9994 | 240.5 | 234637.9994 | 241.5 | 235137.9994 | 243.5 | 236437.9994 | 234.5 | 232037.9994
245.5 | 232037.9994 | 247.5 | 234837.9994 | 249.5 | 236237.9994 | 250.5 | 234637.9994 | 252.5 | 235137.9994 | 254.5 | 236437.9994 | 245.5 | 232037.9994
256.5 | 232037.9994 | 258.5 | 234837.9994 | 259.5 | 118068.9988 | 261.5 | 234637.9994 | 263.5 | 235137.9994 | 265.5 | 236437.9994 | 256.5 | 118068.9988
267.5 | 232037.9994 | 268.5 | 234837.9994 | 270.5 | 236237.9994 | 272.5 | 234637.9994 | 274.5 | 235137.9994 | 276.5 | 236437.9994 | 267.5 | 232037.9994
277.5 | 232037.9994 | 279.5 | 234837.9994 | 281.5 | 236237.9994 | 283.5 | 234637.9994 | 285.5 | 235137.9994 | 286.5 | 236437.9994 | 277.5 | 232037.9994
288.5 | 232037.9994 | 290.5 | 234837.9994 | 292.5 | 236237.9994 | 294.5 | 234637.9994 | 295.5 | 235137.9994 | 297.5 | 236437.9994 | 288.5 | 232037.9994
299.5 | 232037.9994 | 301.5 | 234837.9994 | 303.5 | 236237.9994 | 304.5 | 234637.9994 | 306.5 | 117518.9988 | 308.5 | 236437.9994 | 299.5 | 117518.9988
310.5 | 232037.9994 | 312.5 | 234837.9994 | 313.5 | 236237.9994 | 315.5 | 117268.9988 | 317.5 | 235137.9994 | 319.5 | 236437.9994 | 310.5 | 117268.9988
321.5 | 232037.9994 | 322.5 | 234837.9994 | 324.5 | 236237.9994 | 326.5 | 234637.9994 | 328.5 | 235137.9994 | 330.5 | 236437.9994 | 321.5 | 232037.9994
331.5 | 232037.9994 | 333.5 | 234837.9994 | 335.5 | 236237.9994 | 337.5 | 234637.9994 | 339.5 | 235137.9994 | 340.5 | 236437.9994 | 331.5 | 232037.9994
342.5 | 232037.9994 | 344.5 | 234837.9994 | 346.5 | 236237.9994 | 348.5 | 234637.9994 | 349.5 | 235137.9994 | 351.5 | 236437.9994 | 342.5 | 232037.9994
353.5 | 232037.9994 | 355.5 | 234837.9994 | 357.5 | 236237.9994 | 358.5 | 234637.9994 | 360.5 | 235137.9994 | 362.5 | 236437.9994 | 353.5 | 232037.9994
364.5 | 232037.9994 | 366.5 | 234837.9994 | 367.5 | 236237.9994 | 369.5 | 234637.9994 | 371.5 | 235137.9994 | 373.5 | 236437.9994 | 364.5 | 232037.9994
375.5 | 232037.9994 | 376.5 | 234837.9994 | 378.5 | 236237.9994 | 380.5 | 234637.9994 | 382.5 | 235137.9994 | 384.5 | 236437.9994 | 375.5 | 232037.9994
385.5 | 232037.9994 | 387.5 | 234837.9994 | 389.5 | 236237.9994 | 391.5 | 234637.9994 | 393.5 | 235137.9994 | 394.5 | 236437.9994 | 385.5 | 232037.9994
396.5 | 232037.9994 | 398.5 | 234837.9994 | 400.5 | 236237.9994 | 402.5 | 117268.9988 | 403.5 | 235137.9994 | 405.5 | 236437.9994 | 396.5 | 117268.9988
407.5 | 232037.9994 | 409.5 | 234837.9994 | 411 | 236237.9994 | 412.5 | 234637.9994 | 414.5 | 235137.9994 | 416.5 | 236437.9994 | 407.5 | 232037.9994
418.5 | 232037.9994 | 420.5 | 234837.9994 | 421.5 | 236237.9994 | 423.5 | 234637.9994 | 425.5 | 235137.9994 | 427.5 | 236437.9994 | 418.5 | 232037.9994
429.5 | 232037.9994 | 430.5 | 234837.9994 | 432.5 | 236237.9994 | 434.5 | 234637.9994 | 436.5 | 235137.9994 | 438.5 | 236437.9994 | 429.5 | 232037.9994
439.5 | 232037.9994 | 441.5 | 234837.9994 | 443.5 | 236237.9994 | 445.5 | 234637.9994 | 447 | 235137.9994 | 448.5 | 236437.9994 | 439.5 | 232037.9994
450.5 | 232037.9994 | 452.5 | 234837.9994 | 454.5 | 236237.9994 | 456 | 234637.9994 | 457.5 | 235137.9994 | 459.5 | 236437.9994 | 450.5 | 232037.9994
461.5 | 232037.9994 | 463.5 | 234837.9994 | 465.5 | 236237.9994 | 466.5 | 234637.9994 | 468.5 | 235137.9994 | 470.5 | 236437.9994 | 461.5 | 232037.9994
472.5 | 232037.9994 | 474.5 | 117368.9988 | 475.5 | 236237.9994 | 477.5 | 234637.9994 | 479.5 | 235137.9994 | 481.5 | 236437.9994 | 472.5 | 117368.9988
483.5 | 232037.9994 | 484.5 | 234837.9994 | 486.5 | 236237.9994 | 488.5 | 234637.9994 | 490.5 | 235137.9994 | 492.5 | 236437.9994 | 483.5 | 232037.9994
493.5 | 232037.9994 | 495.5 | 234837.9994 | 497.5 | 236237.9994 | 499.5 | 234637.9994 | 501.5 | 235137.9994 | 502.5 | 236437.9994 | 493.5 | 232037.9994
504.5 | 232037.9994 | 506.5 | 234837.9994 | 508.5 | 236237.9994 | 510 | 234637.9994 | 511.5 | 235137.9994 | 513.5 | 236437.9994 | 504.5 | 232037.9994
515.5 | 232037.9994 | 517.5 | 234837.9994 | 519 | 236237.9994 | 520.5 | 234637.9994 | 522.5 | 235137.9994 | 524.5 | 236437.9994 | 515.5 | 232037.9994
526.5 | 232037.9994 | 528 | 234837.9994 | 529.5 | 236237.9994 | 531.5 | 234637.9994 | 533.5 | 235137.9994 | 535.5 | 118168.9988 | 526.5 | 118168.9988
537 | 232037.9994 | 538.5 | 234837.9994 | 540.5 | 236237.9994 | 542.5 | 234637.9994 | 544.5 | 234938.085 | 546 | 236437.9994 | 537 | 232037.9994
547.5 | 115968.9988 | 549.5 | 234837.9994 | 551.5 | 236237.9994 | 553.5 | 234637.9994 | 555 | 235137.9994 | 556.5 | 236437.9994 | 547.5 | 115968.9988
558.5 | 232037.9994 | 560.5 | 234837.9994 | 562.5 | 236237.9994 | 564.5 | 234637.9994 | 565.5 | 235137.9994 | 567.5 | 236437.9994 | 558.5 | 232037.9994
569.5 | 232037.9994 | 571.5 | 234837.9994 | 573 | 236237.9994 | 574.5 | 234637.9994 | 576.5 | 235137.9994 | 578.5 | 236437.9994 | 569.5 | 232037.9994
580.5 | 232037.9994 | 582.5 | 234837.9994 | 583.5 | 236237.9994 | 585.5 | 234637.9994 | 587.5 | 235137.9994 | 589.5 | 236437.9994 | 580.5 | 232037.9994
591.5 | 232037.9994 | 592.5 | 234837.9994 | 594.5 | 236237.9994 | 596.5 | 234637.9994 | 598.5 | 234938.085 | 600.5 | 236437.9994 | 591.5 | 232037.9994
601.5 | 232037.9994 | 603.5 | 234837.9994 | 605.5 | 118068.9988 | 607.5 | 234637.9994 | 609.5 | 235137.9994 | 610.5 | 236437.9994 | 601.5 | 118068.9988
612.5 | 232037.9994 | 614.5 | 234837.9994 | 616.5 | 236237.9994 | 618.5 | 234637.9994 | 619.5 | 235137.9994 | 621.5 | 236437.9994 | 612.5 | 232037.9994
623.5 | 232037.9994 | 625.5 | 234837.9994 | 627.5 | 236237.9994 | 628.5 | 234637.9994 | 630.5 | 235137.9994 | 632.5 | 236437.9994 | 623.5 | 232037.9994
634.5 | 232037.9994 | 636.5 | 234638.0851 | 637.5 | 236237.9994 | 639.5 | 234637.9994 | 641.5 | 235137.9994 | 643.5 | 236437.9994 | 634.5 | 232037.9994
645.5 | 232037.9994 | 646.5 | 234837.9994 | 648.5 | 236237.9994 | 650.5 | 234637.9994 | 652.5 | 235137.9994 | 654 | 236437.9994 | 645.5 | 232037.9994
655.5 | 232037.9994 | 657.5 | 234837.9994 | 659.5 | 236237.9994 | 661.5 | 234637.9994 | 663 | 235137.9994 | 664.5 | 236437.9994 | 655.5 | 232037.9994
666.5 | 232037.9994 | 668.5 | 234837.9994 | 670.5 | 236237.9994 | 672 | 234637.9994 | 673.5 | 235137.9994 | 675.5 | 236437.9994 | 666.5 | 232037.9994
677.5 | 232037.9994 | 679.5 | 234837.9994 | 681.5 | 236237.9994 | 682.5 | 234637.9994 | 684.5 | 235137.9994 | 686.5 | 236437.9994 | 677.5 | 232037.9994
688.5 | 232037.9994 | 690.5 | 234837.9994 | 691.5 | 236237.9994 | 693.5 | 234637.9994 | 695.5 | 235137.9994 | 697.5 | 236437.9994 | 688.5 | 232037.9994
699.5 | 232037.9994 | 700.5 | 234837.9994 | 702.5 | 236237.9994 | 704.5 | 234637.9994 | 706.5 | 235137.9994 | 708.5 | 236437.9994 | 699.5 | 232037.9994
709.5 | 232037.9994 | 711.5 | 234837.9994 | 713.5 | 236237.9994 | 715.5 | 234637.9994 | 717.5 | 235137.9994 | 718.5 | 236437.9994 | 709.5 | 232037.9994
720.5 | 232037.9994 | 722.5 | 234837.9994 | 724.5 | 236237.9994 | 726.5 | 234637.9994 | 727.5 | 235137.9994 | 729.5 | 236437.9994 | 720.5 | 232037.9994
731.5 | 232037.9994 | 733.5 | 234837.9994 | 735.5 | 236237.9994 | 736.5 | 234637.9994 | 738.5 | 235137.9994 | 740.5 | 236437.9994 | 731.5 | 232037.9994
742.5 | 232037.9994 | 744 | 234837.9994 | 745.5 | 236237.9994 | 747.5 | 234637.9994 | 749.5 | 235137.9994 | 751.5 | 236437.9994 | 742.5 | 232037.9994
753 | 232037.9994 | 754.5 | 234837.9994 | 756.5 | 236237.9994 | 758.5 | 234637.9994 | 760.5 | 235137.9994 | 762 | 236437.9994 | 753 | 232037.9994
763.5 | 232037.9994 | 765.5 | 234837.9994 | 767.5 | 15655.8575 | 769.5 | 234637.9994 | 771 | 235137.9994 | 772.5 | 236437.9994 | 763.5 | 15655.8575
774.5 | 46327.5969 | 776.5 | 21257.9933 | 778.5 | 2589.2332 | 780.5 | 234637.9994 | 781.5 | 235137.9994 | 783.5 | 236437.9994 | 774.5 | 2589.2332
785.5 | 6008.8715 | 787.5 | 4598.7295 | 789.5 | 645.6199 | 790.5 | 234338.1278 | 792.5 | 235137.9994 | 794.5 | 236437.9994 | 785.5 | 645.6199
796.5 | 2663.4963 | 798 | 2347.2122 | 799.5 | 59.9281 | 801.5 | 19130.0118 | 803.5 | 212847.4373 | 805.5 | 1937.5351 | 796.5 | 59.9281
807 | 211506.5368 | 808.5 | 1535.0234 | 810.5 | 175.3549 | 812.5 | 12972.2077 | 814.5 | 392.2964 | 816 | 1384.6889 | 807 | 175.3549
817.5 | 1697.8843 | 819.5 | 962.5386 | 821.5 | 166.4668 | 823.5 | 3851.3432 | 825.5 | 468.9404 | 826.5 | 493.5122 | 817.5 | 166.4668
828.5 | 1003.5024 | 830.5 | 543.388 | 832.5 | 281.6293 | 835 | 1862.4572 | 835.5 | 381.101 | 837.5 | 435.4643 | 828.5 | 281.6293
839.5 | 663.8573 | 841.5 | 319.8715 | 843 | 95.8301 | 844.5 | 1166.8223 | 846.5 | 306.587 | 848.5 | 348.4032 | 839.5 | 95.8301
850.5 | 658.8235 | 852 | 471.3792 | 853.5 | 123.2919 | 855.5 | 489.5677 | 857.5 | 343.9653 | 859.5 | 63.3196 | 850.5 | 63.3196
861 | 485.73 | 862.5 | 249.4619 | 864.5 | 197.5348 | 866.5 | 297.9774 | 868.5 | 246.8192 | 870.5 | 34.138 | 861 | 34.138
871.5 | 57.155 | 873.5 | 42.3058 | 875.5 | 22.728 | 877.5 | 1.1698 | 879 | 0.22756 | 880.5 | 16.5626 | 871.5 | 0.22756
882.5 | 0.69006 | 884.5 | 2.7534 | 886.5 | 32.9955 | 888 | 36.2585 | 889.5 | 42.4711 | 891.5 | 12.1667 | 882.5 | 0.69006
893.5 | 14.8234 | 895.5 | 5.2179 | 897 | 23.6472 | 898.5 | 38.7472 | 900.5 | 28.8913 | 902.5 | 51.9822 | 893.5 | 5.2179
904.5 | 51.5006 | 906 | 48.064 | 907.5 | 1.4624 | 909.5 | 19.2243 | 911.5 | 20.3066 | 913.5 | 13.9074 | 904.5 | 1.4624
915 | 20.83 | 916.5 | 2.4882 | 918.5 | 19.826 | 920.5 | 0.47846 | 922.5 | 12.315 | 923.5 | 12.8003 | 915 | 0.47846
925.5 | 1.0406 | 927.5 | 54.1522 | 929.5 | 5.054 | 931.5 | 34.4348 | 933 | 29.1689 | 934.5 | 30.0548 | 925.5 | 1.0406
936.5 | 59.6814 | 938.5 | 43.836 | 940.5 | 28.6316 | 942 | 5.8298 | 943.5 | 52.3624 | 945.5 | 38.6497 | 936.5 | 5.8298
947.5 | 39.5541 | 949.5 | 41.4586 | 951 | 18.1239 | 952.5 | 13.405 | 954.5 | 37.9522 | 956.5 | 22.5043 | 947.5 | 13.405
958.5 | 17.2043 | 960 | 2.4634 | 961.5 | 31.2425 | 963.5 | 50.6532 | 965.5 | 9.8751 | 967.5 | 35.1364 | 958.5 | 2.4634
969 | 35.3624 | 970.5 | 15.6466 | 972.5 | 43.2892 | 974.5 | 0.84746 | 976.5 | 1.8101 | 978 | 52.0592 | 969 | 0.84746
979.5 | 4.6467 | 981.5 | 34.2003 | 983.5 | 41.777 | 985.5 | 53.5302 | 987 | 25.831 | 988.5 | 53.4441 | 979.5 | 4.6467
990.5 | 48.4028 | 992.5 | 15.4222 | 994.5 | 26.7117 | 996 | 35.4639 | 997.5 | 32.8883 | 999.5 | 3.4544 | 990.5 | 3.4544
1001.5 | 30.7821 | 1003.5 | 3.3016 | 1005 | 5.4292 | 1006.5 | 0.95157 | 1008.5 | 7.0703 | 1010.5 | 69.1733 | 1001.5 | 0.95157
1012.5 | 56.8297 | 1014 | 16.5411 | 1015.5 | 43.3646 | 1017.5 | 35.8148 | 1019.5 | 11.9716 | 1021.5 | 28.3302 | 1012.5 | 11.9716
1023 | 19.0574 | 1024.5 | 51.9788 | 1026.5 | 24.0879 | 1028.5 | 7.6916 | 1030.5 | 9.8471 | 1031.5 | 27.8486 | 1023 | 7.6916
1033.5 | 1.3452 | 1035.5 | 37.8686 | 1037.5 | 11.8236 | 1039.5 | 32.2319 | 1041 | 63.1655 | 1042.5 | 50.31 | 1033.5 | 1.3452
1044.5 | 27.3164 | 1046.5 | 45.1138 | 1048.5 | 44.5383 | 1050 | 53.7213 | 1051.5 | 53.175 | 1053.5 | 22.6527 | 1044.5 | 22.6527
1055.5 | 25.7147 | 1057.5 | 38.6724 | 1059 | 3.5951 | 1060.5 | 24.9298 | 1062.5 | 32.9004 | 1064.5 | 73.6629 | 1055.5 | 3.5951
1066.5 | 12.3913 | 1068 | 31.8232 | 1069.5 | 57.3291 | 1071.5 | 2.7274 | 1073.5 | 42.0967 | 1075.5 | 20.2444 | 1066.5 | 2.7274
1077 | 5.0226 | 1078.5 | 24.6984 | 1080.5 | 0.67466 | 1082.5 | 13.3909 | 1084.5 | 44.7958 | 1086 | 37.0286 | 1077 | 0.67466
1087.5 | 15.6472 | 1089.5 | 59.7271 | 1091.5 | 3.7019 | 1093.5 | 16.9154 | 1095 | 22.1983 | 1096.5 | 16.6162 | 1087.5 | 3.7019
1098.5 | 24.1014 | 1100.5 | 42.1632 | 1102.5 | 1.8299 | 1104 | 43.4377 | 1105.5 | 0.9587 | 1107.5 | 8.6565 | 1098.5 | 0.9587
1109.5 | 6.1921 | 1111.5 | 30.3882 | 1113 | 19.7728 | 1114.5 | 46.6922 | 1116.5 | 13.8085 | 1118.5 | 16.5227 | 1109.5 | 6.1921
1120.5 | 10.9856 | 1122 | 0.25133 | 1123.5 | 27.0979 | 1125.5 | 37.0916 | 1127.5 | 2.4746 | 1129.5 | 44.9862 | 1120.5 | 0.25133
1131 | 8.7185 | 1132.5 | 1.919 | 1134.5 | 0.37524 | 1136.5 | 0.22057 | 1138.5 | 60.4579 | 1140 | 4.8624 | 1131 | 0.22057
1141.5 | 5.5067 | 1143.5 | 11.529 | 1145.5 | 17.5016 | 1147.5 | 1.9 | 1149 | 75.7051 | 1150.5 | 64.6659 | 1141.5 | 1.9
1152.5 | 0.53694 | 1154.5 | 40.5706 | 1156.5 | 44.4895 | 1158 | 182.0709 | 1159.5 | 2.8454 | 1161.5 | 126.6261 | 1152.5 | 0.53694
1163.5 | 4.104 | 1165.5 | 104.6403 | 1166.5 | 3.3832 | 1168.5 | 117.0109 | 1170.5 | 3.6288 | 1172.5 | 12.3339 | 1163.5 | 3.3832
1174.5 | 19.7336 | 1176 | 2.866 | 1177.5 | 180.5127 | 1179.5 | 111.8681 | 1181.5 | 32.7975 | 1183.5 | 15.8474 | 1174.5 | 2.866
1184.5 | 3.1794 | 1186.5 | 8.3477 | 1188.5 | 13.1474 | 1190.5 | 2.3582 | 1192.5 | 31.5247 | 1194 | 0.36 | 1184.5 | 0.36
1195.5 | 15.2867 | 1197.5 | 65.2357 | 1199.5 | 53.5311 | 1201.5 | 92.9097 | 1203 | 38.2663 | 1204.5 | 0.49883 | 1195.5 | 0.49883
1206.5 | 63.8318 | 1208.5 | 5.2829 | 1210.5 | 71.1449 | 1212 | 9.4302 | 1213.5 | 41.6778 | 1215.5 | 41.7732 | 1206.5 | 5.2829
1217.5 | 17.0744 | 1219.5 | 4.2645 | 1220.5 | 2.1878 | 1222.5 | 37.5472 | 1224.5 | 17.8381 | 1226.5 | 74.4901 | 1217.5 | 2.1878
1228.5 | 27.2316 | 1230 | 44.8319 | 1231.5 | 103.8253 | 1233.5 | 30.0442 | 1235.5 | 43.5498 | 1237.5 | 28.1026 | 1228.5 | 27.2316
1239 | 20.9974 | 1240.5 | 103.5527 | 1242.5 | 47.5419 | 1244.5 | 40.1612 | 1246.5 | 7.9752 | 1247.5 | 28.9675 | 1239 | 7.9752
1249.5 | 91.9986 | 1251.5 | 31.2726 | 1253.5 | 11.2003 | 1255.5 | 17.1031 | 1256.5 | 61.695 | 1258.5 | 3.4177 | 1249.5 | 3.4177
1260.5 | 72.7307 | 1262.5 | 38.1401 | 1264.5 | 81.1918 | 1266 | 89.3547 | 1267.5 | 13.1156 | 1269.5 | 5.3926 | 1260.5 | 5.3926
1271.5 | 36.6702 | 1273.5 | 25.3437 | 1274.5 | 103.838 | 1276.5 | 67.0499 | 1278.5 | 21.7945 | 1280.5 | 8.7711 | 1271.5 | 8.7711
1282.5 | 19.7794 | 1283.5 | 6.0962 | 1285.5 | 110.6574 | 1287.5 | 38.742 | 1289.5 | 18.7543 | 1291.5 | 13.5826 | 1282.5 | 6.0962
1292.5 | 3.519 | 1294.5 | 26.9245 | 1296.5 | 81.1306 | 1298.5 | 1.4561 | 1300.5 | 34.7134 | 1301.5 | 18.9826 | 1292.5 | 1.4561
1303.5 | 43.4462 | 1305.5 | 19.2036 | 1307.5 | 0.62604 | 1309.5 | 95.1961 | 1310.5 | 33.0829 | 1312.5 | 76.2305 | 1303.5 | 0.62604
1314.5 | 62.8193 | 1316.5 | 18.4492 | 1318.5 | 8.8092 | 1320 | 66.9329 | 1321.5 | 10.3815 | 1323.5 | 113.0233 | 1314.5 | 8.8092
1325.5 | 93.1244 | 1327.5 | 32.7006 | 1329 | 24.9633 | 1330.5 | 86.1979 | 1332.5 | 23.3318 | 1334.5 | 33.8529 | 1325.5 | 23.3318
1336.5 | 4.442 | 1338 | 31.0039 | 1339.5 | 26.0779 | 1341.5 | 68.1305 | 1343.5 | 4.4474 | 1345.5 | 72.3158 | 1336.5 | 4.442
1347 | 10.2057 | 1348.5 | 17.1276 | 1350.5 | 47.9821 | 1352.5 | 119.7959 | 1354.5 | 111.5036 | 1356 | 2.7209 | 1347 | 2.7209
1357.5 | 5.2021 | 1359.5 | 22.881 | 1361.5 | 27.2848 | 1363.5 | 10.7873 | 1364.5 | 0.90785 | 1366.5 | 35.4452 | 1357.5 | 0.90785
1368.5 | 89.3028 | 1370.5 | 8.298 | 1372.5 | 41.3328 | 1374 | 24.585 | 1375.5 | 26.6654 | 1377.5 | 44.6092 | 1368.5 | 8.298
1379.5 | 8.241 | 1381.5 | 0.85269 | 1382.5 | 10.792 | 1384.5 | 2.6722 | 1386.5 | 17.7744 | 1388.5 | 7.1036 | 1379.5 | 0.85269
1390.5 | 23.3512 | 1392 | 62.7176 | 1393.5 | 26.3682 | 1395.5 | 11.5229 | 1397.5 | 20.776 | 1399.5 | 2.1734 | 1390.5 | 2.1734
1401 | 34.0651 | 1402.5 | 123.4943 | 1404.5 | 100.2539 | 1406.5 | 30.5968 | 1408.5 | 3.1604 | 1409.5 | 19.2081 | 1401 | 3.1604
1411.5 | 84.1687 | 1413.5 | 0.60162 | 1415.5 | 4.3323 | 1417.5 | 44.3184 | 1418.5 | 72.9507 | 1420.5 | 86.2186 | 1411.5 | 0.60162
1422.5 | 2.1045 | 1424.5 | 4.3083 | 1426.5 | 14.0352 | 1428 | 135.3294 | 1429.5 | 75.2764 | 1431.5 | 129.817 | 1422.5 | 2.1045
1433.5 | 66.2164 | 1435.5 | 22.3819 | 1436.5 | 6.9429 | 1438.5 | 4.5734 | 1440.5 | 26.018 | 1442.5 | 1.0274 | 1433.5 | 1.0274

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5
0 | -90 | 25.9831 | 23.6173 | 23.89 | 23.7635 | 22.9668 | 22.4388
0.6309 | -89.3691 | 25.9832 | 23.62 | 23.896 | 23.76 | 22.9553 | 22.44
1.412 | -88.588 | 25.9871 | 23.6198 | 23.8821 | 23.7613 | 22.9662 | 22.4411
2.4035 | -87.5965 | 25.985 | 23.6226 | 23.8944 | 23.7617 | 22.9555 | 22.4382
3.4049 | -86.5951 | 25.9889 | 23.6139 | 23.8968 | 23.762 | 22.9553 | 22.4451
4.4063 | -85.5937 | 25.9901 | 23.6195 | 23.8925 | 23.7662 | 22.9588 | 22.4356
5.4078 | -84.5922 | 25.9898 | 23.6137 | 23.8921 | 23.7649 | 22.9431 | 22.4371
6.4092 | -83.5908 | 25.984 | 23.6218 | 23.8871 | 23.7578 | 22.9554 | 22.4402
7.4107 | -82.5893 | 25.9893 | 23.6156 | 23.8892 | 23.7634 | 22.9544 | 22.4366
8.4121 | -81.5879 | 25.9922 | 23.6227 | 23.8997 | 23.7739 | 22.9575 | 22.4359
9.4035 | -80.5965 | 25.9876 | 23.6195 | 23.8898 | 23.7612 | 22.959 | 22.4358
10.405 | -79.595 | 25.9902 | 23.621 | 23.8944 | 23.7639 | 22.9449 | 22.4422
11.4064 | -78.5936 | 25.9933 | 23.6211 | 23.8956 | 23.7661 | 22.9459 | 22.4423
12.4078 | -77.5922 | 25.9918 | 23.6253 | 23.9025 | 23.7675 | 22.9627 | 22.4423
13.4093 | -76.5907 | 25.9909 | 23.625 | 23.901 | 23.7708 | 22.9508 | 22.446
14.4107 | -75.5893 | 25.9882 | 23.6299 | 23.8986 | 23.7697 | 22.9557 | 22.4469
15.4122 | -74.5878 | 25.9906 | 23.6227 | 23.8909 | 23.7694 | 22.9514 | 22.4482
16.4136 | -73.5864 | 25.9934 | 23.6249 | 23.9007 | 23.7744 | 22.9583 | 22.4405
17.405 | -72.595 | 25.9825 | 23.6309 | 23.9074 | 23.7752 | 22.9444 | 22.4455
18.4065 | -71.5935 | 25.9908 | 23.6281 | 23.9003 | 23.778 | 22.9595 | 22.4498
19.4079 | -70.5921 | 25.9932 | 23.6393 | 23.9016 | 23.7768 | 22.9668 | 22.4509
20.4093 | -69.5907 | 25.99 | 23.6257 | 23.9012 | 23.7806 | 22.9581 | 22.453
21.4108 | -68.5892 | 25.9891 | 23.6385 | 23.9015 | 23.7724 | 22.9491 | 22.4479
22.4122 | -67.5878 | 25.9917 | 23.6292 | 23.896 | 23.7764 | 22.9678 | 22.4538
23.4037 | -66.5963 | 25.9884 | 23.628 | 23.8898 | 23.7815 | 22.9722 | 22.4518
24.4051 | -65.5949 | 25.988 | 23.6291 | 23.8987 | 23.7812 | 22.9494 | 22.4487
25.4065 | -64.5935 | 25.9855 | 23.6369 | 23.9081 | 23.776 | 22.9679 | 22.4517
26.408 | -63.592 | 25.9872 | 23.6375 | 23.9048 | 23.7825 | 22.9735 | 22.4597
27.4094 | -62.5906 | 25.9853 | 23.6328 | 23.91 | 23.7823 | 22.9553 | 22.4536
28.4109 | -61.5891 | 25.9918 | 23.6391 | 23.8997 | 23.7845 | 22.9573 | 22.4572
29.4123 | -60.5877 | 25.9908 | 23.6427 | 23.9002 | 23.7848 | 22.9673 | 22.4597
30.4037 | -59.5963 | 25.9918 | 23.6442 | 23.9055 | 23.785 | 22.962 | 22.4581
31.4052 | -58.5948 | 25.9909 | 23.6417 | 23.9165 | 23.7855 | 22.9691 | 22.4513
32.4066 | -57.5934 | 25.994 | 23.6515 | 23.9039 | 23.788 | 22.966 | 22.4548
33.408 | -56.592 | 25.9918 | 23.6391 | 23.8976 | 23.7834 | 22.9756 | 22.4594
34.4095 | -55.5905 | 25.9918 | 23.6447 | 23.9055 | 23.7873 | 22.9669 | 22.4593
35.4109 | -54.5891 | 25.9976 | 23.6448 | 23.9161 | 23.7905 | 22.9654 | 22.4618
36.4023 | -53.5977 | 25.991 | 23.6424 | 23.9215 | 23.7841 | 22.9687 | 22.4646
37.4038 | -52.5962 | 25.992 | 23.644 | 23.9091 | 23.7968 | 22.9795 | 22.4652
38.4052 | -51.5948 | 25.9959 | 23.6426 | 23.9231 | 23.7943 | 22.967 | 22.4663
39.4067 | -50.5933 | 26.0001 | 23.6475 | 23.9078 | 23.7965 | 22.978 | 22.4609
40.4081 | -49.5919 | 26.0013 | 23.6432 | 23.9154 | 23.7904 | 22.9811 | 22.4713
41.4095 | -48.5905 | 25.9987 | 23.6506 | 23.9266 | 23.7911 | 22.97 | 22.4626
42.411 | -47.589 | 26.0016 | 23.6424 | 23.9229 | 23.7921 | 22.9703 | 22.471
43.4124 | -46.5876 | 25.9983 | 23.6504 | 23.9127 | 23.7982 | 22.9755 | 22.4714
44.4038 | -45.5962 | 25.9934 | 23.6436 | 23.917 | 23.794 | 22.9864 | 22.4686
45.4053 | -44.5947 | 26.0004 | 23.6518 | 23.9174 | 23.7918 | 22.9809 | 22.4697
46.4067 | -43.5933 | 26.0032 | 23.6464 | 23.9214 | 23.7978 | 22.9923 | 22.4733
47.4082 | -42.5918 | 25.9991 | 23.6453 | 23.9251 | 23.7971 | 22.9862 | 22.4727
48.4096 | -41.5904 | 26.0065 | 23.6554 | 23.9245 | 23.803 | 22.9777 | 22.4738
49.411 | -40.589 | 26.0072 | 23.6572 | 23.9173 | 23.8034 | 22.9799 | 22.469
50.4125 | -39.5875 | 26.0039 | 23.6627 | 23.9207 | 23.8063 | 22.9814 | 22.4733
51.4039 | -38.5961 | 26.0018 | 23.648 | 23.9391 | 23.7973 | 22.9826 | 22.4631
52.4054 | -37.5946 | 26.0066 | 23.6514 | 23.9321 | 23.8011 | 22.9841 | 22.4736
53.4068 | -36.5932 | 26.0073 | 23.6498 | 23.9171 | 23.8 | 22.9806 | 22.4739
54.4082 | -35.5918 | 26.0054 | 23.657 | 23.9332 | 23.8053 | 22.9909 | 22.4726
55.4097 | -34.5903 | 26.0051 | 23.6557 | 23.9274 | 23.7997 | 22.9921 | 22.4784
56.4111 | -33.5889 | 26.0016 | 23.6613 | 23.921 | 23.8045 | 22.9985 | 22.48
57.4025 | -32.5975 | 26.0071 | 23.6615 | 23.9283 | 23.802 | 22.9935 | 22.4785
58.414 | -31.586 | 26.0079 | 23.658 | 23.9368 | 23.8002 | 23.0027 | 22.4847
59.4054 | -30.5946 | 26.0072 | 23.658 | 23.9383 | 23.8066 | 22.9895 | 22.48
60.4069 | -29.5931 | 26.0089 | 23.6564 | 23.9331 | 23.8076 | 22.9945 | 22.4843
61.4083 | -28.5917 | 26.0094 | 23.661 | 23.9394 | 23.8013 | 22.9875 | 22.4835
62.4097 | -27.5903 | 26.0059 | 23.6647 | 23.9373 | 23.8108 | 22.9945 | 22.4862
63.4112 | -26.5888 | 26.0123 | 23.6662 | 23.9403 | 23.8072 | 22.9973 | 22.483
64.4126 | -25.5874 | 26.0085 | 23.6604 | 23.9234 | 23.8129 | 22.9961 | 22.4878
65.404 | -24.596 | 26.015 | 23.6638 | 23.9351 | 23.8119 | 22.987 | 22.4844
66.4055 | -23.5945 | 26.0135 | 23.6661 | 23.9283 | 23.8082 | 22.9995 | 22.4848
67.4069 | -22.5931 | 26.0086 | 23.6617 | 23.9301 | 23.8124 | 22.9991 | 22.4823
68.4084 | -21.5916 | 26.0101 | 23.661 | 23.9436 | 23.8079 | 22.9932 | 22.4849
69.4098 | -20.5902 | 26.0067 | 23.6627 | 23.9434 | 23.8103 | 22.9963 | 22.4885
70.4112 | -19.5888 | 26.0099 | 23.6659 | 23.9168 | 23.8156 | 22.992 | 22.4888
71.4027 | -18.5973 | 26.0101 | 23.6655 | 23.9424 | 23.8107 | 22.9967 | 22.4858
72.4041 | -17.5959 | 26.0146 | 23.6689 | 23.9458 | 23.8179 | 22.99 | 22.4944
73.4056 | -16.5944 | 26.0115 | 23.6744 | 23.9469 | 23.8159 | 22.9962 | 22.4962
74.407 | -15.593 | 26.0107 | 23.6709 | 23.9459 | 23.8192 | 23.0024 | 22.4957
75.4084 | -14.5916 | 26.0069 | 23.6735 | 23.9395 | 23.8216 | 23.0085 | 22.4957
76.4099 | -13.5901 | 26.0057 | 23.6748 | 23.9453 | 23.8174 | 23.0054 | 22.4914
77.4113 | -12.5887 | 26.005 | 23.6669 | 23.9457 | 23.8197 | 22.9986 | 22.4957
78.4027 | -11.5973 | 26.0021 | 23.6698 | 23.9434 | 23.8219 | 22.9928 | 22.4896
79.4042 | -10.5958 | 26.0095 | 23.6728 | 23.9528 | 23.8171 | 23.0121 | 22.4924
80.4056 | -9.5944 | 26.0132 | 23.6758 | 23.9511 | 23.8154 | 23.0092 | 22.4902
81.4071 | -8.5929 | 26.0069 | 23.6789 | 23.9556 | 23.8142 | 23.0144 | 22.4993
82.4085 | -7.5915 | 26.0106 | 23.675 | 23.9554 | 23.8214 | 23.0136 | 22.4903
83.4099 | -6.5901 | 26.0048 | 23.6751 | 23.9443 | 23.8192 | 23.0147 | 22.499
84.4114 | -5.5886 | 26.0085 | 23.6816 | 23.9531 | 23.8218 | 23.0126 | 22.4995
85.4128 | -4.5872 | 26.0121 | 23.6734 | 23.9416 | 23.8149 | 23.0026 | 22.5011
86.4042 | -3.5958 | 26.017 | 23.4606 | 23.9577 | 23.7312 | 23.0764 | 22.5371
87.4057 | -2.5943 | 26.0221 | 23.5448 | 23.9695 | 23.7799 | 23.0615 | 22.535
88.4071 | -1.5929 | 26.2277 | 23.5665 | 23.9602 | 23.7909 | 23.0567 | 22.5404
89.4086 | -0.5914 | 26.9208 | 23.5822 | 23.9733 | 23.8005 | 23.0767 | 22.5383
90.41 | 0.41 | 28.212 | 23.5936 | 23.9729 | 23.8036 | 23.0741 | 22.5466
91.4014 | 1.4014 | 30.0444 | 23.6068 | 23.9748 | 23.8064 | 23.1091 | 22.5587
92.4029 | 2.4029 | 32.3761 | 23.5979 | 23.9794 | 23.8167 | 23.1495 | 22.5778
93.4043 | 3.4043 | 35.1024 | 23.6029 | 23.96 | 23.8252 | 23.1864 | 22.5936
94.4057 | 4.4057 | 38.1963 | 23.601 | 23.9822 | 23.838 | 23.2249 | 22.6187
95.4072 | 5.4072 | 41.5866 | 23.6064 | 23.9644 | 23.8571 | 23.2933 | 22.6606
96.4086 | 6.4086 | 45.2435 | 23.5982 | 23.966 | 23.8726 | 23.3584 | 22.7019
97.4101 | 7.4101 | 49.118 | 23.6174 | 23.9842 | 23.9107 | 23.4496 | 22.7523
98.4115 | 8.4115 | 53.166 | 23.6244 | 23.9815 | 23.9454 | 23.5634 | 22.8064
99.4029 | 9.4029 | 57.4201 | 23.6173 | 23.9867 | 23.9887 | 23.689 | 22.8642
100.4044 | 10.4044 | 61.824 | 23.6197 | 23.9697 | 24.0308 | 23.8116 | 22.9308
101.4058 | 11.4058 | 66.3503 | 23.6227 | 23.9859 | 24.0936 | 23.9692 | 23.0097
102.4073 | 12.4073 | 71.0167 | 23.643 | 23.9892 | 24.1635 | 24.1292 | 23.0991
103.4087 | 13.4087 | 75.8335 | 23.6385 | 23.9833 | 24.2312 | 24.33 | 23.1893
104.4101 | 14.4101 | 80.7741 | 23.6557 | 23.9887 | 24.3288 | 24.5389 | 23.295
105.4116 | 15.4116 | 85.811 | 23.6549 | 23.9758 | 24.4197 | 24.762 | 23.4238
106.413 | 16.413 | 90.9587 | 23.6787 | 23.9935 | 24.5291 | 24.988 | 23.5638
107.4044 | 17.4044 | 96.2294 | 23.682 | 24.0017 | 24.648 | 25.2809 | 23.7182
108.4059 | 18.4059 | 101.5487 | 23.7008 | 24.0089 | 24.7691 | 25.5871 | 23.8891
109.4073 | 19.4073 | 106.9409 | 23.7299 | 24.009 | 24.9258 | 25.9178 | 24.0736
110.4088 | 20.4088 | 112.3977 | 23.7486 | 24.0049 | 25.0768 | 26.2342 | 24.2681
111.4102 | 21.4102 | 117.995 | 23.7799 | 24.0164 | 25.2538 | 26.5769 | 24.4852
112.4016 | 22.4016 | 123.631 | 23.8164 | 24.0177 | 25.443 | 26.9565 | 24.7118
113.4031 | 23.4031 | 129.2527 | 23.8545 | 24.0463 | 25.6474 | 27.361 | 24.9631
114.4045 | 24.4045 | 134.8851 | 23.884 | 24.0384 | 25.8531 | 27.7863 | 25.2196
115.4059 | 25.4059 | 140.5341 | 23.9238 | 24.0553 | 26.0979 | 28.2304 | 25.4955
116.4074 | 26.4074 | 146.119 | 23.9939 | 24.0549 | 26.3539 | 28.7243 | 25.7929
117.4088 | 27.4088 | 151.7151 | 24.0328 | 24.0797 | 26.6134 | 29.2008 | 26.102
118.4103 | 28.4103 | 157.3465 | 24.1016 | 24.1045 | 26.9 | 29.7256 | 26.4264
119.4117 | 29.4117 | 163.0014 | 24.1638 | 24.1162 | 27.2003 | 30.3807 | 26.786
120.4031 | 30.4031 | 168.6117 | 24.2372 | 24.1311 | 27.5126 | 30.91 | 27.1452
121.4146 | 31.4146 | 174.1495 | 24.3109 | 24.1593 | 27.8432 | 31.5295 | 27.5311
122.406 | 32.406 | 179.6563 | 24.3879 | 24.1838 | 28.2027 | 32.2234 | 27.9264
123.4075 | 33.4075 | 185.1525 | 24.4799 | 24.2176 | 28.5789 | 32.8232 | 28.3495
124.4089 | 34.4089 | 190.6169 | 24.5696 | 24.2518 | 28.9654 | 33.457 | 28.7928
125.4103 | 35.4103 | 196.1801 | 24.6764 | 24.2769 | 29.3743 | 34.1614 | 29.251
126.4118 | 36.4118 | 201.8557 | 24.7703 | 24.2987 | 29.7906 | 34.8681 | 29.7345
127.4032 | 37.4032 | 207.5352 | 24.9047 | 24.3507 | 30.2212 | 35.6046 | 30.2328
128.4046 | 38.4046 | 213.2028 | 25.0033 | 24.3789 | 30.6733 | 36.4017 | 30.7513
129.4061 | 39.4061 | 218.7468 | 25.1373 | 24.4351 | 31.1295 | 37.2127 | 31.2868
130.4075 | 40.4075 | 224.172 | 25.266 | 24.4901 | 31.6256 | 38.0429 | 31.858
131.409 | 41.409 | 229.5696 | 25.4049 | 24.5379 | 32.1301 | 38.9074 | 32.4355
132.4104 | 42.4104 | 235.0072 | 25.5673 | 24.5934 | 32.6637 | 39.7703 | 33.0375
133.4118 | 43.4118 | 240.5171 | 25.7144 | 24.6627 | 33.2102 | 40.6829 | 33.6516
134.4033 | 44.4033 | 245.9304 | 25.9023 | 24.7168 | 33.7817 | 41.5945 | 34.2972
135.4047 | 45.4047 | 251.4236 | 26.0633 | 24.7885 | 34.3782 | 42.5408 | 34.958
136.4061 | 46.4061 | 256.9081 | 26.2704 | 24.8692 | 34.9965 | 43.5006 | 35.6511
137.4076 | 47.4076 | 262.2731 | 26.4704 | 24.9479 | 35.622 | 44.4383 | 36.3679
138.409 | 48.409 | 267.6618 | 26.6806 | 25.0278 | 36.2822 | 45.4835 | 37.093
139.4105 | 49.4105 | 272.9952 | 26.8937 | 25.1161 | 36.942 | 46.525 | 37.8352
140.4019 | 50.4019 | 278.359 | 27.1114 | 25.2066 | 37.6407 | 47.6042 | 38.5962
141.4033 | 51.4033 | 283.6569 | 27.3677 | 25.3231 | 38.3579 | 48.6828 | 39.3858
142.4048 | 52.4048 | 289.007 | 27.5951 | 25.4214 | 39.085 | 49.7984 | 40.1792
143.4062 | 53.4062 | 294.2877 | 27.863 | 25.527 | 39.8651 | 50.9584 | 41.0217
144.4076 | 54.4076 | 299.5581 | 28.1278 | 25.6354 | 40.6656 | 52.1712 | 41.8759
145.4091 | 55.4091 | 304.9119 | 28.4127 | 25.7643 | 41.4811 | 53.3576 | 42.7608
146.4105 | 56.4105 | 310.293 | 28.6874 | 25.8946 | 42.3135 | 54.7626 | 43.6678
147.402 | 57.402 | 315.6313 | 28.9945 | 26.0279 | 43.168 | 56.075 | 44.6085
148.4034 | 58.4034 | 320.963 | 29.2986 | 26.1781 | 44.0409 | 57.3676 | 45.572
149.4048 | 59.4048 | 326.1325 | 29.622 | 26.3045 | 44.9646 | 58.6918 | 46.5683
150.4063 | 60.4063 | 331.3178 | 29.9573 | 26.4766 | 45.9164 | 60.1544 | 47.5882
151.4077 | 61.4077 | 336.5255 | 30.2997 | 26.6491 | 46.8866 | 61.5455 | 48.6292
152.4092 | 62.4092 | 341.6389 | 30.668 | 26.8045 | 47.889 | 62.9886 | 49.6858
153.4106 | 63.4106 | 346.8447 | 31.0396 | 26.988 | 48.9051 | 64.5065 | 50.7825
154.412 | 64.412 | 352.141 | 31.4477 | 27.181 | 49.95 | 66.0454 | 51.8979
155.4035 | 65.4035 | 357.2124 | 31.8292 | 27.3543 | 51.0229 | 67.5904 | 53.0315
156.4049 | 66.4049 | 362.3335 | 32.2646 | 27.568 | 52.1086 | 69.1551 | 54.198
157.4063 | 67.4063 | 367.3817 | 32.6758 | 27.7705 | 53.2154 | 70.8311 | 55.4066
158.4078 | 68.4078 | 372.447 | 33.123 | 27.9867 | 54.367 | 72.5063 | 56.6184
159.4092 | 69.4092 | 377.5042 | 33.5686 | 28.1922 | 55.5559 | 74.2006 | 57.8603
160.4107 | 70.4107 | 382.4817 | 34.0346 | 28.4363 | 56.7525 | 75.9622 | 59.1231
161.4021 | 71.4021 | 387.51 | 34.5283 | 28.6773 | 57.9864 | 77.7378 | 60.4028
162.4035 | 72.4035 | 392.5575 | 35.011 | 28.9434 | 59.2425 | 79.5888 | 61.7198
163.405 | 73.405 | 397.3975 | 35.5429 | 29.1902 | 60.5375 | 81.4269 | 63.0558
164.4064 | 74.4064 | 402.257 | 36.067 | 29.4525 | 61.846 | 83.3127 | 64.4239
165.4078 | 75.4078 | 406.8636 | 36.6235 | 29.7297 | 63.1918 | 85.2139 | 65.8291
166.4093 | 76.4093 | 411.5954 | 37.173 | 30.0193 | 64.5753 | 87.1979 | 67.2636
167.4107 | 77.4107 | 416.4013 | 37.7528 | 30.3093 | 65.9658 | 89.1173 | 68.7227
168.4122 | 78.4122 | 420.961 | 38.3477 | 30.623 | 67.3759 | 91.1037 | 70.2213
169.4136 | 79.4136 | 425.4691 | 38.9662 | 30.9348 | 68.8244 | 93.136 | 71.7403
170.405 | 80.405 | 430.0369 | 39.6048 | 31.2627 | 70.2742 | 95.2295 | 73.2841
171.4065 | 81.4065 | 434.7126 | 40.145 | 31.5684 | 71.6876 | 97.412 | 74.8944
172.4079 | 82.4079 | 439.2269 | 40.8316 | 31.915 | 73.1876 | 99.5904 | 76.4756
173.4094 | 83.4094 | 443.4533 | 41.472 | 32.2989 | 74.6933 | 101.8684 | 78.0819
174.4108 | 84.4108 | 447.1095 | 42.2002 | 32.6653 | 76.2239 | 104.0822 | 79.6931
175.4122 | 85.4122 | 450.559 | 42.8997 | 33.0217 | 77.7562 | 106.3199 | 81.325
176.4037 | 86.4037 | 453.7471 | 43.6788 | 33.4076 | 79.3292 | 108.5509 | 82.9773
177.4051 | 87.4051 | 456.9026 | 44.4131 | 33.7992 | 80.9099 | 110.7818 | 84.6494
178.4065 | 88.4065 | 459.8452 | 45.1789 | 34.2159 | 82.5117 | 113.0072 | 86.3073
179.408 | 89.408 | 462.8312 | 45.9679 | 34.6231 | 84.1309 | 115.2181 | 87.9889
180.4094 | 90.4094 | 465.5185 | 46.7336 | 35.0556 | 85.738 | 117.5079 | 89.6756
181.4109 | 91.4109 | 468.1836 | 47.5461 | 35.4801 | 87.3509 | 119.7383 | 91.3641
182.4023 | 92.4023 | 470.6511 | 48.386 | 35.9197 | 88.9833 | 121.9238 | 93.0708
183.4037 | 93.4037 | 472.932 | 49.2346 | 36.3798 | 90.6139 | 124.1301 | 94.7843
184.4052 | 94.4052 | 475.0736 | 50.1106 | 36.8609 | 92.2679 | 126.2911 | 96.4795
185.4066 | 95.4066 | 477.0005 | 50.9933 | 37.3218 | 93.9224 | 128.5638 | 98.1784
186.408 | 96.408 | 478.7229 | 51.8656 | 37.8113 | 95.5408 | 130.7047 | 99.8638
187.4095 | 97.4095 | 480.2878 | 52.7629 | 38.3159 | 97.1783 | 132.7632 | 101.5413
188.4109 | 98.4109 | 481.5136 | 53.6815 | 38.8188 | 98.8227 | 134.8255 | 103.2099
189.4124 | 99.4124 | 482.4421 | 54.5925 | 39.3313 | 100.4477 | 136.8719 | 104.8684
190.4038 | 100.4038 | 483.275 | 55.5279 | 39.8352 | 102.0793 | 138.8339 | 106.4834
191.4052 | 101.4052 | 483.8103 | 56.4825 | 40.3879 | 103.696 | 140.7633 | 108.0954
192.4067 | 102.4067 | 484.088 | 57.4512 | 40.924 | 105.2922 | 142.6603 | 109.6681
193.4081 | 103.4081 | 484.2171 | 58.3997 | 41.4503 | 106.8538 | 144.5083 | 111.2166
194.4095 | 104.4095 | 484.1782 | 59.3697 | 42.0075 | 108.3799 | 146.3398 | 112.7479
195.411 | 105.411 | 484.15 | 60.3507 | 42.5787 | 109.8811 | 148.1172 | 114.2635
196.4124 | 106.4124 | 484.1028 | 61.349 | 43.1375 | 111.351 | 149.9254 | 115.7437
197.4039 | 107.4039 | 484.2053 | 62.3443 | 43.7067 | 112.7947 | 151.7014 | 117.2147
198.4053 | 108.4053 | 483.982 | 63.3388 | 44.2815 | 114.2077 | 153.4012 | 118.6501
199.4067 | 109.4067 | 483.8351 | 64.347 | 44.8628 | 115.6012 | 155.0569 | 120.0618
200.4082 | 110.4082 | 483.4414 | 65.3526 | 45.4426 | 116.9672 | 156.678 | 121.4664
201.4096 | 111.4096 | 482.8204 | 66.3642 | 46.0344 | 118.3128 | 158.2435 | 122.8264
202.4111 | 112.4111 | 482.2013 | 67.3799 | 46.6458 | 119.6506 | 159.7444 | 124.1716
203.4025 | 113.4025 | 481.533 | 68.3993 | 47.2335 | 120.9555 | 161.2741 | 125.4727
204.4039 | 114.4039 | 480.8842 | 69.4227 | 47.8551 | 122.2501 | 162.766 | 126.782
205.4054 | 115.4054 | 480.2676 | 70.4498 | 48.4485 | 123.5203 | 164.1502 | 128.0472
206.4068 | 116.4068 | 479.7752 | 71.4946 | 49.0638 | 124.7625 | 165.5382 | 129.2928
207.4082 | 117.4082 | 478.9625 | 72.5044 | 49.6819 | 125.9686 | 166.944 | 130.5221
208.4097 | 118.4097 | 478.3525 | 73.5395 | 50.2964 | 127.1576 | 168.328 | 131.7381
209.4111 | 119.4111 | 477.7657 | 74.5733 | 50.9211 | 128.3254 | 169.661 | 132.9289
210.4025 | 120.4025 | 477.3759 | 75.6052 | 51.5551 | 129.4715 | 170.99 | 134.0991
211.414 | 121.414 | 477.0265 | 76.6518 | 52.1908 | 130.6072 | 172.3218 | 135.2379
212.4054 | 122.4054 | 476.6894 | 77.6874 | 52.8218 | 131.7171 | 173.5538 | 136.3633
213.4069 | 123.4069 | 476.2736 | 78.7227 | 53.4729 | 132.8074 | 174.7948 | 137.4689
214.4083 | 124.4083 | 475.7886 | 79.7789 | 54.1217 | 133.8977 | 176.0058 | 138.5569
215.4097 | 125.4097 | 475.3682 | 80.8125 | 54.7711 | 134.9661 | 177.2496 | 139.6281
216.4112 | 126.4112 | 474.9377 | 81.8553 | 55.4197 | 136.0194 | 178.5081 | 140.6995
217.4126 | 127.4126 | 474.766 | 82.896 | 56.0991 | 137.0602 | 179.715 | 141.7608
218.404 | 128.404 | 474.6947 | 83.9438 | 56.7673 | 138.0909 | 180.828 | 142.8106
219.4055 | 129.4055 | 474.5885 | 84.9489 | 57.4205 | 139.106 | 181.979 | 143.8558
220.4069 | 130.4069 | 474.5275 | 85.9753 | 58.0985 | 140.1245 | 183.1105 | 144.8821
221.4084 | 131.4084 | 474.4914 | 86.9919 | 58.7645 | 141.1448 | 184.2646 | 145.8903
222.4098 | 132.4098 | 474.499 | 88.0324 | 59.4305 | 142.1324 | 185.3902 | 146.9062
223.4112 | 133.4112 | 474.4549 | 89.0426 | 60.1052 | 143.1107 | 186.534 | 147.9103
224.4027 | 134.4027 | 474.5131 | 90.0351 | 60.7884 | 144.0819 | 187.6822 | 148.9106
225.4041 | 135.4041 | 474.7148 | 91.0512 | 61.4637 | 145.0606 | 188.8121 | 149.9121
226.4056 | 136.4056 | 474.9563 | 92.0577 | 62.128 | 146.0495 | 189.948 | 150.9053
227.437 | 137.437 | 475.213 | 93.1 | 62.8404 | 147.0375 | 191.0692 | 151.9054
228.4084 | 138.4084 | 475.5525 | 94.0618 | 63.4879 | 147.9747 | 192.1328 | 152.8838
229.4099 | 139.4099 | 475.8869 | 95.069 | 64.1683 | 148.9442 | 193.2428 | 153.8814
230.4113 | 140.4113 | 476.1595 | 96.0498 | 64.8472 | 149.9171 | 194.341 | 154.8434
231.4027 | 141.4027 | 476.479 | 97.0234 | 65.5115 | 150.8837 | 195.3675 | 155.8149
232.4042 | 142.4042 | 476.7923 | 98.0032 | 66.197 | 151.8507 | 196.487 | 156.7816
233.4056 | 143.4056 | 477.0354 | 98.965 | 66.8431 | 152.7856 | 197.5565 | 157.7213
234.4071 | 144.4071 | 477.1621 | 99.9332 | 67.529 | 153.7099 | 198.5717 | 158.666
235.4085 | 145.4085 | 477.431 | 100.8989 | 68.1839 | 154.6269 | 199.6231 | 159.6139
236.4099 | 146.4099 | 477.6479 | 101.8759 | 68.8537 | 155.5522 | 200.6772 | 160.5467
237.4114 | 147.4114 | 477.663 | 102.8286 | 69.5086 | 156.4727 | 201.6389 | 161.4772
238.4128 | 148.4128 | 477.7 | 103.7941 | 70.1773 | 157.3957 | 202.6717 | 162.39
239.4042 | 149.4042 | 477.7932 | 104.7667 | 70.8445 | 158.3103 | 203.6657 | 163.2902
240.4057 | 150.4057 | 477.9218 | 105.7245 | 71.5121 | 159.2281 | 204.6804 | 164.2091
241.4071 | 151.4071 | 478.0474 | 106.7004 | 72.1735 | 160.1569 | 205.6525 | 165.1071
242.4086 | 152.4086 | 478.1508 | 107.6951 | 72.8488 | 161.0585 | 206.5694 | 166.0109
243.41 | 153.41 | 478.2644 | 108.6866 | 73.5027 | 161.9542 | 207.507 | 166.908
244.4014 | 154.4014 | 478.3806 | 109.6988 | 74.1656 | 162.8356 | 208.4222 | 167.8158
245.4029 | 155.4029 | 478.5613 | 110.7152 | 74.8306 | 163.709 | 209.3226 | 168.7074
246.4043 | 156.4043 | 478.8143 | 111.7699 | 75.4747 | 164.5713 | 210.1764 | 169.6
247.4058 | 157.4058 | 478.8849 | 112.8176 | 76.1371 | 165.4257 | 211.0665 | 170.4912
248.4072 | 158.4072 | 479.0495 | 113.8967 | 76.8016 | 166.2781 | 211.9513 | 171.3686
249.4086 | 159.4086 | 479.1225 | 114.9884 | 77.4397 | 167.0984 | 212.8178 | 172.2535
250.4101 | 160.4101 | 479.2426 | 116.1005 | 78.0973 | 167.9209 | 213.6846 | 173.1228
251.4115 | 161.4115 | 479.3005 | 117.2382 | 78.7509 | 168.731 | 214.557 | 173.9838
252.4029 | 162.4029 | 479.4039 | 118.3798 | 79.3953 | 169.5459 | 215.4368 | 174.8429
253.4044 | 163.4044 | 479.3773 | 119.5116 | 80.0432 | 170.333 | 216.2573 | 175.6928
254.4058 | 164.4058 | 479.2961 | 120.6326 | 80.685 | 171.0909 | 217.0837 | 176.558
255.4073 | 165.4073 | 479.3508 | 121.7566 | 81.3408 | 171.8263 | 217.894 | 177.4064
256.4087 | 166.4087 | 479.4702 | 122.8793 | 81.9696 | 172.5663 | 218.6752 | 178.2396
257.4101 | 167.4101 | 479.3197 | 123.9849 | 82.5985 | 173.2897 | 219.5183 | 179.0716
258.4116 | 168.4116 | 479.0978 | 125.0781 | 83.2411 | 173.994 | 220.2849 | 179.9125
259.413 | 169.413 | 478.9808 | 126.1809 | 83.8804 | 174.6767 | 221.059 | 180.7306
260.4044 | 170.4044 | 478.8392 | 127.2652 | 84.5056 | 175.343 | 221.7897 | 181.553
261.4059 | 171.4059 | 478.8253 | 128.3367 | 85.1468 | 176.0045 | 222.5493 | 182.3691
262.4073 | 172.4073 | 478.741 | 129.4205 | 85.7764 | 176.6682 | 223.2306 | 183.1902
263.4088 | 173.4088 | 478.7643 | 130.5405 | 86.3946 | 177.3257 | 223.8702 | 183.9975
264.4102 | 174.4102 | 478.6653 | 131.6761 | 87.0103 | 177.9693 | 224.563 | 184.7986
265.4016 | 175.4016 | 478.6427 | 132.7934 | 87.6323 | 178.5936 | 225.2055 | 185.5946
266.4031 | 176.4031 | 478.4943 | 133.8905 | 88.2577 | 179.2154 | 225.8263 | 186.3856
267.4045 | 177.4045 | 478.6674 | 134.978 | 88.8703 | 179.8225 | 226.564 | 187.1677
268.4059 | 178.4059 | 478.8558 | 136.0476 | 89.4703 | 180.4185 | 227.2377 | 187.9498
269.4074 | 179.4074 | 479.1376 | 137.0774 | 90.0897 | 181.0225 | 228.006 | 188.7331
270.4088 | 180.4088 | 479.2362 | 138.1249 | 90.6849 | 181.6221 | 228.696 | 189.5231
271.4103 | 181.4103 | 479.2233 | 139.1531 | 91.3063 | 182.2104 | 229.3532 | 190.3032
272.4017 | 182.4017 | 479.3822 | 140.2087 | 91.8877 | 182.7812 | 230.0243 | 191.0578
273.4031 | 183.4031 | 479.5684 | 141.3131 | 92.4877 | 183.3185 | 230.6995 | 191.8121
274.4046 | 184.4046 | 479.682 | 142.4019 | 93.0874 | 183.8847 | 231.3347 | 192.5637
275.406 | 185.406 | 479.6721 | 143.4815 | 93.709 | 184.4333 | 231.9718 | 193.2956
276.4075 | 186.4075 | 479.6612 | 144.5946 | 94.3022 | 185.0086 | 232.5993 | 194.025
277.4089 | 187.4089 | 479.7631 | 145.6574 | 94.8975 | 185.5645 | 233.2359 | 194.743
278.4103 | 188.4103 | 479.6699 | 146.7082 | 95.5086 | 186.095 | 233.8764 | 195.4559
279.4118 | 189.4118 | 479.7295 | 147.745 | 96.1072 | 186.6327 | 234.4891 | 196.1428
280.4132 | 190.4132 | 479.9502 | 148.7551 | 96.7046 | 187.1583 | 235.0752 | 196.7848
281.4046 | 191.4046 | 479.9619 | 149.7518 | 97.3145 | 187.6771 | 235.6414 | 197.4742
282.4061 | 192.4061 | 480.0941 | 150.7306 | 97.9615 | 188.1846 | 236.2492 | 198.1567
283.4075 | 193.4075 | 480.2566 | 151.6984 | 98.6037 | 188.6928 | 236.823 | 198.8244
284.409 | 194.409 | 480.2336 | 152.6405 | 99.224 | 189.2015 | 237.3698 | 199.4954
285.4104 | 195.4104 | 480.2311 | 153.5919 | 99.9021 | 189.708 | 238.0815 | 200.1527
286.4018 | 196.4018 | 480.1504 | 154.5034 | 100.5569 | 190.1968 | 238.8024 | 200.8279
287.4033 | 197.4033 | 480.1036 | 155.3978 | 101.2618 | 190.6902 | 239.5019 | 201.4646
288.4047 | 198.4047 | 480.1737 | 156.2578 | 101.9624 | 191.1532 | 240.1387 | 202.1128
289.4061 | 199.4061 | 480.0029 | 157.0846 | 102.6663 | 191.6071 | 240.8111 | 202.7474
290.4076 | 200.4076 | 479.9876 | 157.8771 | 103.3696 | 192.087 | 241.4864 | 203.3779
291.409 | 201.409 | 480.0241 | 158.6139 | 104.0729 | 192.5696 | 242.1896 | 203.9858
292.4105 | 202.4105 | 480.0194 | 159.3417 | 104.7603 | 193.0686 | 242.9001 | 204.5828
293.4019 | 203.4019 | 479.9324 | 160.0447 | 105.4403 | 193.5608 | 243.5482 | 205.1643
294.4033 | 204.4033 | 479.9024 | 160.7182 | 106.0903 | 194.0603 | 244.2463 | 205.7524
295.4048 | 205.4048 | 479.9024 | 161.364 | 106.7371 | 194.5623 | 244.9251 | 206.3042
296.4062 | 206.4062 | 479.8834 | 162.0234 | 107.3503 | 195.0449 | 245.5231 | 206.8556
297.4077 | 207.4077 | 479.8063 | 162.6456 | 107.9427 | 195.5147 | 246.0691 | 207.4059
298.4091 | 208.4091 | 479.7851 | 163.2561 | 108.4983 | 195.9945 | 246.5945 | 207.953
299.4105 | 209.4105 | 479.8196 | 163.8703 | 109.0314 | 196.4513 | 247.2991 | 208.4839
300.412 | 210.412 | 479.7295 | 164.4526 | 109.5317 | 196.9011 | 247.965 | 209.0117
301.4134 | 211.4134 | 479.5449 | 165.0442 | 110.0267 | 197.3719 | 248.4691 | 209.5116
302.4048 | 212.4048 | 479.3955 | 165.6083 | 110.5074 | 197.8496 | 249.0859 | 210.0095
303.4063 | 213.4063 | 479.2794 | 166.1967 | 111 | 198.3557 | 249.7285 | 210.4931
304.4077 | 214.4077 | 479.3959 | 166.7425 | 111.5159 | 198.8253 | 250.3875 | 210.9685
305.4092 | 215.4092 | 479.358 | 167.273 | 112.0741 | 199.3178 | 251.1363 | 211.4482
306.4106 | 216.4106 | 479.4555 | 167.8006 | 112.6374 | 199.6502 | 251.7672 | 211.9075
307.402 | 217.402 | 479.4426 | 168.2988 | 113.2343 | 200.0543 | 252.299 | 212.3607
308.4035 | 218.4035 | 479.4066 | 168.7809 | 113.8436 | 200.4689 | 252.8558 | 212.8008
309.4049 | 219.4049 | 479.4344 | 169.2331 | 114.444 | 200.8945 | 253.2943 | 213.2461
310.4063 | 220.4063 | 479.4508 | 169.7022 | 115.0466 | 201.3868 | 253.9058 | 213.6827
311.4078 | 221.4078 | 479.3329 | 170.1064 | 115.6515 | 201.884 | 254.509 | 214.1185
312.4092 | 222.4092 | 479.1299 | 170.4844 | 116.2504 | 202.3977 | 255.0208 | 214.564
313.4107 | 223.4107 | 478.9963 | 170.7998 | 116.8756 | 202.8324 | 255.6283 | 214.9818
314.4021 | 224.4021 | 478.9968 | 171.054 | 117.5291 | 203.2856 | 256.2215 | 215.3834
315.4035 | 225.4035 | 478.9801 | 171.296 | 118.2123 | 203.7553 | 256.7991 | 215.7922
316.405 | 226.405 | 478.9818 | 171.5158 | 118.9404 | 204.1533 | 257.2424 | 216.1721
317.4064 | 227.4064 | 479.0834 | 171.7105 | 119.7287 | 204.5608 | 257.6777 | 216.5555
318.4078 | 228.4078 | 479.1871 | 171.8931 | 120.5853 | 205.0047 | 258.3032 | 216.942
319.4093 | 229.4093 | 479.3429 | 172.1065 | 121.5007 | 205.488 | 258.9853 | 217.3229
320.4107 | 230.4107 | 479.3553 | 172.3085 | 122.4706 | 205.9519 | 259.5995 | 217.6868
321.4122 | 231.4122 | 479.3535 | 172.5141 | 123.4687 | 206.4113 | 260.1512 | 218.0536
322.4136 | 232.4136 | 479.4876 | 172.7281 | 124.4712 | 206.8781 | 260.63 | 218.4331
323.405 | 233.405 | 479.5971 | 172.9527 | 125.4824 | 207.3584 | 261.1202 | 218.8336
324.4065 | 234.4065 | 479.6984 | 173.1761 | 126.5151 | 207.7728 | 261.6467 | 219.2148
325.4079 | 235.4079 | 479.9099 | 173.4094 | 127.5233 | 208.1858 | 262.352 | 219.5982
326.4094 | 236.4094 | 479.8744 | 173.6392 | 128.534 | 208.623 | 262.954 | 219.9924
327.4108 | 237.4108 | 479.8711 | 173.8631 | 129.5157 | 209.0808 | 263.5244 | 220.3945
328.4022 | 238.4022 | 479.7942 | 174.0884 | 130.5316 | 209.5873 | 264.1574 | 220.7931
329.4037 | 239.4037 | 479.8742 | 174.3233 | 131.5264 | 209.8853 | 264.8 | 221.2042
330.4051 | 240.4051 | 479.9804 | 174.5481 | 132.5029 | 209.9233 | 265.423 | 221.5817
331.4065 | 241.4065 | 480.0744 | 174.7844 | 133.4727 | 210.3029 | 265.993 | 221.954
332.408 | 242.408 | 479.969 | 175.0379 | 134.446 | 210.8331 | 266.4041 | 222.3549
333.4094 | 243.4094 | 479.9407 | 175.2902 | 135.4103 | 211.4009 | 266.8845 | 222.7436
334.4109 | 244.4109 | 479.958 | 175.5592 | 136.3573 | 212.0441 | 267.3752 | 223.1515
335.4123 | 245.4123 | 479.9005 | 175.8332 | 137.3119 | 212.5898 | 267.8386 | 223.5316
336.4037 | 246.4037 | 479.9481 | 176.1231 | 138.2402 | 213.12 | 268.204 | 223.896
337.4052 | 247.4052 | 479.9246 | 176.4449 | 139.1671 | 213.8767 | 268.537 | 224.2041
338.4066 | 248.4066 | 479.7184 | 176.7543 | 140.0892 | 214.5927 | 268.8917 | 224.5027
339.408 | 249.408 | 479.7213 | 177.0864 | 140.9906 | 215.2231 | 269.4076 | 224.8249
340.4095 | 250.4095 | 479.7822 | 177.4272 | 141.913 | 215.7889 | 269.9969 | 225.1854
341.4109 | 251.4109 | 479.7689 | 177.794 | 142.8191 | 216.2457 | 270.5748 | 225.5682
342.4124 | 252.4124 | 479.7634 | 178.1772 | 143.7164 | 216.7329 | 270.9182 | 225.9593
343.4038 | 253.4038 | 479.7697 | 178.569 | 144.5903 | 217.4174 | 271.4536 | 226.3307
344.4052 | 254.4052 | 479.4033 | 178.9761 | 145.494 | 218.2074 | 271.9493 | 226.6564
345.4067 | 255.4067 | 479.1979 | 179.3941 | 146.3646 | 218.8003 | 272.3976 | 226.9839
346.4081 | 256.4081 | 479.2535 | 179.8178 | 147.2135 | 219.3448 | 272.8208 | 227.3158
347.4096 | 257.4096 | 479.2872 | 180.2409 | 148.0683 | 219.8911 | 273.235 | 227.6479
348.411 | 258.411 | 479.352 | 180.6782 | 148.941 | 220.696 | 273.6955 | 228.0041
349.4024 | 259.4024 | 479.3362 | 181.1444 | 149.7999 | 221.3123 | 274.1398 | 228.3488
350.4039 | 260.4039 | 479.3163 | 181.6199 | 150.6498 | 221.833 | 274.5919 | 228.6684
351.4053 | 261.4053 | 479.31 | 182.1021 | 151.4863 | 222.5873 | 275.0087 | 228.9744
352.4067 | 262.4067 | 479.2729 | 182.5862 | 152.3236 | 223.1686 | 275.4533 | 229.2941
353.4082 | 263.4082 | 479.2766 | 183.0846 | 153.1639 | 223.6282 | 276.006 | 229.6161
354.4096 | 264.4096 | 479.2879 | 183.6128 | 154.0021 | 224.101 | 276.4086 | 229.9265
355.4111 | 265.4111 | 479.3476 | 184.1407 | 154.8079 | 224.943 | 276.8267 | 230.239
356.4025 | 266.4025 | 479.3475 | 184.6721 | 155.6528 | 225.6506 | 277.1605 | 230.5118
357.4039 | 267.4039 | 479.3491 | 185.1792 | 156.4728 | 226.2122 | 277.5219 | 230.8072
358.4054 | 268.4054 | 479.4322 | 185.7046 | 157.2975 | 226.8138 | 277.8857 | 231.0697
359.4068 | 269.4068 | 479.5159 | 186.2288 | 158.0998 | 227.7181 | 278.2984 | 231.3343
360.4082 | 270.4082 | 479.5895 | 186.7726 | 158.9154 | 228.4037 | 278.6739 | 231.6407
361.4097 | 271.4097 | 479.7992 | 187.2975 | 159.7307 | 228.9987 | 279.0231 | 231.9397
362.4111 | 272.4111 | 479.8503 | 187.8468 | 160.5353 | 229.5269 | 279.3606 | 232.2078
363.4126 | 273.4126 | 479.783 | 188.3589 | 161.3351 | 229.9748 | 279.6341 | 232.5049
364.404 | 274.404 | 479.8334 | 188.8736 | 162.1326 | 230.5076 | 280.0132 | 232.789
365.4054 | 275.4054 | 479.9233 | 189.3823 | 162.9221 | 231.0052 | 280.4644 | 233.0737
366.4069 | 276.4069 | 479.9848 | 189.8692 | 163.7155 | 231.5562 | 280.9409 | 233.3773
367.4083 | 277.4083 | 480.0611 | 190.3946 | 164.4755 | 232.0951 | 281.4 | 233.7085
368.4097 | 278.4097 | 480.0544 | 190.918 | 165.2674 | 232.7302 | 281.7804 | 234.0406
369.4112 | 279.4112 | 480.049 | 191.4728 | 166.0402 | 233.3959 | 282.1474 | 234.3007
370.4026 | 280.4026 | 480.0651 | 192.024 | 166.8175 | 234.0287 | 282.3858 | 234.6279
371.4041 | 281.4041 | 480.1242 | 192.5958 | 167.569 | 234.7211 | 282.5904 | 234.9644
372.4055 | 282.4055 | 480.0633 | 193.1737 | 168.3203 | 235.3504 | 282.8434 | 235.2864
373.4069 | 283.4069 | 480.0103 | 193.7531 | 169.0755 | 235.9574 | 283.2667 | 235.5934
374.4084 | 284.4084 | 479.9409 | 194.3342 | 169.8107 | 236.5575 | 283.7188 | 235.9144
375.4098 | 285.4098 | 479.7075 | 194.9092 | 170.5667 | 237.1914 | 284.1086 | 236.2096
376.4113 | 286.4113 | 479.6184 | 195.4991 | 171.3136 | 237.905 | 284.484 | 236.506
377.4027 | 287.4027 | 479.5735 | 196.0714 | 172.0417 | 238.5604 | 284.9423 | 236.803
378.4041 | 288.4041 | 479.4672 | 196.649 | 172.7756 | 239.2351 | 285.2912 | 237.1052
379.4056 | 289.4056 | 479.4108 | 197.1991 | 173.488 | 239.8868 | 285.6706 | 237.4066
380.407 | 290.407 | 479.4269 | 197.7814 | 174.1844 | 240.5546 | 286.084 | 237.7006
381.4084 | 291.4084 | 479.4451 | 198.3659 | 174.9017 | 241.1737 | 286.3975 | 237.9957
382.4099 | 292.4099 | 479.5341 | 199.0355 | 175.5717 | 241.72 | 286.7002 | 238.2656
383.4113 | 293.4113 | 479.5454 | 199.6498 | 176.2609 | 242.2815 | 286.966 | 238.561
384.4128 | 294.4128 | 479.5837 | 200.2669 | 176.9283 | 242.848 | 287.2219 | 238.8629
385.4042 | 295.4042 | 479.5294 | 200.8719 | 177.5887 | 243.3984 | 287.5525 | 239.1641
386.4056 | 296.4056 | 479.562 | 201.4871 | 178.2504 | 243.9867 | 287.818 | 239.4449
387.4071 | 297.4071 | 479.5262 | 202.1415 | 178.9074 | 244.5663 | 288.1447 | 239.7317
388.4085 | 298.4085 | 479.5514 | 202.8149 | 179.5599 | 245.1569 | 288.5159 | 240.0233
389.4099 | 299.4099 | 479.6245 | 203.4682 | 180.1871 | 245.7235 | 288.8545 | 240.2543
390.4114 | 300.4114 | 479.5928 | 204.1317 | 180.8174 | 246.2461 | 289.1781 | 240.5182
391.4128 | 301.4128 | 479.6384 | 204.7774 | 181.4398 | 246.8082 | 289.5066 | 240.7721
392.4042 | 302.4042 | 479.6686 | 205.4246 | 182.0507 | 247.3696 | 289.8076 | 241.0552
393.4057 | 303.4057 | 479.6054 | 206.0459 | 182.6362 | 247.8599 | 290.1922 | 241.3663
394.4071 | 304.4071 | 479.4635 | 206.6502 | 183.2275 | 248.4573 | 290.5239 | 241.6849
395.4086 | 305.4086 | 479.2849 | 207.2303 | 183.8117 | 249.2822 | 290.8391 | 241.989
396.41 | 306.41 | 479.2903 | 207.7823 | 184.3719 | 250.1999 | 291.1398 | 242.292
397.4114 | 307.4114 | 479.2894 | 208.3434 | 184.9506 | 251.1177 | 291.429 | 242.613
398.4029 | 308.4029 | 479.182 | 208.9107 | 185.5084 | 251.7292 | 291.7294 | 242.9337
399.4043 | 309.4043 | 478.988 | 209.4553 | 186.0767 | 252.2303 | 291.7689 | 243.2362
400.4058 | 310.4058 | 478.7187 | 210.0195 | 186.6187 | 252.7848 | 292.0602 | 243.5502
401.4072 | 311.4072 | 478.5403 | 210.5701 | 187.1695 | 253.2843 | 292.2959 | 243.8834
402.4086 | 312.4086 | 478.534 | 211.1442 | 187.7103 | 253.8205 | 292.3983 | 244.191
403.4101 | 313.4101 | 478.6021 | 211.6776 | 188.2567 | 254.4471 | 292.4711 | 244.511
404.4115 | 314.4115 | 478.7707 | 212.218 | 188.7922 | 255.1634 | 292.6641 | 244.8004
405.413 | 315.413 | 478.8063 | 212.7509 | 189.3243 | 255.846 | 292.8236 | 245.1085
406.4044 | 316.4044 | 478.8916 | 213.2731 | 189.8577 | 256.8828 | 293.0436 | 245.3911
407.4058 | 317.4058 | 478.9504 | 213.8177 | 190.3893 | 258.4656 | 293.3317 | 245.6561
408.4673 | 318.4673 | 479.0094 | 214.3817 | 190.9409 | 260.0714 | 293.5755 | 245.9695
409.4087 | 319.4087 | 479.1335 | 214.8878 | 191.4368 | 261.3489 | 293.7982 | 246.2546
410.4101 | 320.4101 | 479.1798 | 215.3887 | 191.9529 | 262.5992 | 294.1255 | 246.6
411.4116 | 321.4116 | 479.2 | 215.9422 | 192.4715 | 263.6981 | 294.248 | 246.8986
412.413 | 322.413 | 479.2562 | 216.4667 | 192.9701 | 264.7677 | 294.5243 | 247.2204
413.4044 | 323.4044 | 479.3977 | 217.0174 | 193.4982 | 265.8395 | 294.694 | 247.5425
414.4059 | 324.4059 | 479.664 | 217.5509 | 193.9926 | 266.8031 | 294.9938 | 247.8769
415.4073 | 325.4073 | 479.8237 | 218.1056 | 194.4938 | 267.5908 | 295.2837 | 248.1774
416.4088 | 326.4088 | 479.9316 | 218.6707 | 195.0168 | 268.352 | 295.4683 | 248.493
417.4102 | 327.4102 | 480.0369 | 219.2334 | 195.5262 | 269.202 | 295.6591 | 248.8078
418.4116 | 328.4116 | 480.1068 | 219.8016 | 196.0014 | 270.0941 | 295.9642 | 249.0987
419.4031 | 329.4031 | 480.2146 | 220.3652 | 196.5164 | 271.054 | 296.2229 | 249.3487
420.4045 | 330.4045 | 480.3882 | 220.9579 | 197.0141 | 272.0641 | 296.4848 | 249.5936
421.406 | 331.406 | 480.5055 | 221.5338 | 197.4944 | 273.1576 | 296.6959 | 249.8604
422.4074 | 332.4074 | 480.4642 | 222.1232 | 197.9988 | 274.2832 | 296.8742 | 250.1396
423.4088 | 333.4088 | 480.3749 | 222.6784 | 198.5031 | 275.4386 | 297.0459 | 250.4847
424.4103 | 334.4103 | 480.2542 | 223.2857 | 198.9777 | 276.7178 | 297.1573 | 250.7907
425.4117 | 335.4117 | 480.1644 | 223.8766 | 199.4565 | 278.038 | 297.2534 | 251.1341
426.4132 | 336.4132 | 479.9334 | 224.4837 | 199.9522 | 279.255 | 297.293 | 251.4803
427.4046 | 337.4046 | 479.7984 | 225.0798 | 200.4568 | 280.3845 | 297.477 | 251.7963
428.406 | 338.406 | 479.811 | 225.677 | 200.9422 | 281.3854 | 297.7505 | 252.092
429.4075 | 339.4075 | 479.8075 | 226.2837 | 201.4248 | 282.2168 | 298.0274 | 252.3978
430.4089 | 340.4089 | 479.8055 | 226.8967 | 201.9117 | 282.9712 | 298.4008 | 252.749
431.4103 | 341.4103 | 479.8181 | 227.5689 | 202.3938 | 283.8722 | 298.7409 | 253.0744
432.4118 | 342.4118 | 479.6658 | 228.2852 | 202.8774 | 284.8315 | 298.9286 | 253.3594
433.4132 | 343.4132 | 479.6622 | 229.0848 | 203.3532 | 285.6538 | 299.0476 | 253.6299
434.4046 | 344.4046 | 479.65 | 230.061 | 203.8413 | 286.4392 | 299.1439 | 253.9177
435.4061 | 345.4061 | 479.6039 | 231.2867 | 204.3267 | 287.1764 | 299.2492 | 254.2304
436.4075 | 346.4075 | 479.572 | 232.6569 | 204.8276 | 287.8136 | 299.5681 | 254.4767
437.409 | 347.409 | 479.4695 | 234.1946 | 205.3108 | 288.2921 | 299.9198 | 254.6972
438.4104 | 348.4104 | 479.3878 | 235.8659 | 205.7737 | 288.9932 | 300.1239 | 254.8944
439.4018 | 349.4018 | 479.3976 | 237.5282 | 206.289 | 289.7743 | 300.322 | 255.1393
440.4033 | 350.4033 | 479.4976 | 239.2581 | 206.7716 | 290.454 | 300.3155 | 255.421
441.4047 | 351.4047 | 479.5811 | 241.0331 | 207.2548 | 291.0014 | 300.4012 | 255.7167
442.4061 | 352.4061 | 479.5516 | 242.7787 | 207.7486 | 291.2959 | 300.6101 | 256.0406
443.4076 | 353.4076 | 479.546 | 244.4251 | 208.2407 | 291.6283 | 300.7336 | 256.3435
444.409 | 354.409 | 479.604 | 246.0947 | 208.7382 | 291.9654 | 300.8682 | 256.6822
445.4105 | 355.4105 | 479.4625 | 247.7537 | 209.2251 | 292.3103 | 301.1023 | 256.9891
446.4019 | 356.4019 | 479.231 | 249.2989 | 209.7384 | 292.7128 | 301.3134 | 257.3081
447.4133 | 357.4133 | 479.1554 | 250.8818 | 210.2362 | 293.0803 | 301.5133 | 257.6138
448.4048 | 358.4048 | 479.3024 | 252.4517 | 210.7329 | 293.4474 | 301.4991 | 257.9366
449.4062 | 359.4062 | 479.1796 | 253.9551 | 211.2399 | 293.8364 | 301.6408 | 258.2702
450.4077 | 360.4077 | 479.0605 | 255.2631 | 211.7617 | 294.2082 | 301.7852 | 258.6428
451.4091 | 361.4091 | 479.0295 | 256.5328 | 212.2499 | 294.58 | 301.6415 | 259.0192
452.4105 | 362.4105 | 479.0251 | 257.8046 | 212.7519 | 294.8839 | 301.5745 | 259.3719
453.412 | 363.412 | 479.1021 | 259.05 | 213.2148 | 295.1257 | 301.493 | 259.7226
454.4034 | 364.4034 | 479.0526 | 260.2742 | 213.7058 | 295.3429 | 301.5497 | 260.0764
455.4048 | 365.4048 | 479.1135 | 261.4866 | 214.1768 | 295.6037 | 301.7431 | 260.4469
456.4063 | 366.4063 | 479.1715 | 262.6621 | 214.6079 | 295.8541 | 301.8765 | 260.7967
457.4077 | 367.4077 | 479.0435 | 263.7812 | 215.0963 | 296.1292 | 302.1011 | 261.1169
458.4092 | 368.4092 | 478.8214 | 264.8492 | 215.5441 | 296.3588 | 302.2996 | 261.446
459.4106 | 369.4106 | 478.7375 | 265.8336 | 215.9935 | 295.99 | 302.492 | 261.7531
460.412 | 370.412 | 478.7159 | 266.7406 | 216.4436 | 296.1727 | 302.6484 | 262.0519
461.4035 | 371.4035 | 478.7909 | 267.6142 | 216.9168 | 296.399 | 302.8813 | 262.4456
462.4049 | 372.4049 | 478.8432 | 268.5027 | 217.3869 | 296.5722 | 303.2292 | 262.7789
463.4063 | 373.4063 | 478.7611 | 269.328 | 217.8793 | 296.4165 | 303.3846 | 263.1209
464.4078 | 374.4078 | 478.6811 | 270.1272 | 218.3566 | 296.6697 | 303.5788 | 263.4543
465.4092 | 375.4092 | 478.6236 | 270.8687 | 218.8653 | 296.7553 | 303.7933 | 263.7811
466.4107 | 376.4107 | 478.6564 | 271.6198 | 219.3277 | 296.7499 | 303.9658 | 264.1429
467.4021 | 377.4021 | 478.6483 | 272.3093 | 219.7917 | 296.7498 | 304.1062 | 264.4477
468.4135 | 378.4135 | 478.6009 | 273.0006 | 220.2429 | 296.7705 | 304.3856 | 264.7523
469.405 | 379.405 | 478.6761 | 273.6463 | 220.7284 | 296.7564 | 304.6109 | 265.0939
470.4064 | 380.4064 | 478.6649 | 274.3008 | 221.1742 | 296.7663 | 304.9596 | 265.4679
471.4079 | 381.4079 | 478.7735 | 274.9449 | 221.6449 | 296.8034 | 305.3419 | 265.8211
472.4093 | 382.4093 | 478.6705 | 275.5739 | 222.131 | 296.8775 | 305.7663 | 266.0543
473.4107 | 383.4107 | 478.6032 | 276.1635 | 222.5857 | 297.0186 | 307.119 | 266.3525
474.4122 | 384.4122 | 478.6525 | 276.7189 | 223.0613 | 297.1569 | 310.2238 | 266.6098
475.4036 | 385.4036 | 478.967 | 277.3632 | 223.5562 | 297.3426 | 309.0951 | 266.8381
476.405 | 386.405 | 479.218 | 278.0126 | 224.0169 | 297.5692 | 308.3621 | 267.1109
477.4065 | 387.4065 | 479.2594 | 278.6219 | 224.4979 | 297.7618 | 308.503 | 267.3929
478.4079 | 388.4079 | 479.2954 | 279.1524 | 224.9414 | 297.9145 | 308.41 | 267.7802
479.4094 | 389.4094 | 479.3471 | 279.6102 | 225.4373 | 298.0589 | 308.4024 | 268.197
480.4108 | 390.4108 | 479.2958 | 279.9789 | 225.8765 | 298.2547 | 308.2467 | 268.5067
481.4022 | 391.4022 | 479.2868 | 280.3683 | 226.3302 | 298.4563 | 308.8524 | 268.7996
482.4037 | 392.4037 | 479.3019 | 280.5873 | 226.7846 | 298.6513 | 308.2447 | 269.0879
483.4051 | 393.4051 | 479.314 | 280.8416 | 227.2389 | 298.846 | 309.2087 | 269.4261
484.4065 | 394.4065 | 479.2643 | 281.1463 | 227.7034 | 299.0375 | 309.4386 | 269.735
485.408 | 395.408 | 479.1908 | 281.4887 | 228.147 | 299.226 | 309.8958 | 270.0415
486.4094 | 396.4094 | 479.0229 | 281.8433 | 228.6003 | 299.4494 | 310.1995 | 270.2929
487.4109 | 397.4109 | 478.9079 | 282.241 | 229.0372 | 299.6221 | 310.667 | 270.5997
488.4023 | 398.4023 | 478.9374 | 282.6734 | 229.4942 | 299.8091 | 310.9978 | 270.8447
489.4137 | 399.4137 | 478.906 | 283.0846 | 229.9546 | 299.9369 | 310.8961 | 271.057
490.4052 | 400.4052 | 478.7262 | 283.4591 | 230.4073 | 300.0013 | 311.6206 | 271.3057
491.4066 | 401.4066 | 478.6984 | 283.8878 | 230.8811 | 300.1128 | 312.4654 | 271.6468
492.408 | 402.408 | 478.7639 | 284.2777 | 231.3307 | 300.1247 | 313.5821 | 272.0171
493.4095 | 403.4095 | 478.5786 | 284.6017 | 231.784 | 300.1179 | 314.2598 | 272.3028
494.4109 | 404.4109 | 478.5607 | 284.9759 | 232.2637 | 300.2319 | 314.12 | 272.6271
495.4124 | 405.4124 | 478.5147 | 285.2425 | 232.721 | 300.4213 | 315.1254 | 272.9224
496.4038 | 406.4038 | 478.4329 | 285.4474 | 233.1899 | 300.5979 | 316.1523 | 273.2112
497.4052 | 407.4052 | 478.436 | 285.637 | 233.6622 | 300.7136 | 316.8799 | 273.4718
498.4067 | 408.4067 | 478.3371 | 285.83 | 234.1154 | 300.7889 | 317.9936 | 273.7953
499.4081 | 409.4081 | 478.2866 | 285.955 | 234.5848 | 300.8362 | 318.553 | 274.0096
500.4096 | 410.4096 | 478.4613 | 285.8745 | 235.0622 | 300.9215 | 318.7811 | 274.244
501.411 | 411.411 | 478.6498 | 285.7929 | 235.542 | 300.942 | 318.9006 | 274.5778
502.4024 | 412.4024 | 478.8721 | 285.5104 | 236.0114 | 300.9444 | 319.2766 | 275.0441
503.4039 | 413.4039 | 478.9124 | 285.3247 | 236.474 | 300.9565 | 319.4172 | 275.4749
504.4053 | 414.4053 | 478.8959 | 285.282 | 236.9558 | 300.9324 | 319.445 | 275.8325
505.4067 | 415.4067 | 478.9872 | 285.3324 | 237.4127 | 300.9421 | 319.6223 | 275.9683
506.4082 | 416.4082 | 478.9706 | 285.3595 | 237.8825 | 300.9923 | 319.2738 | 276.0537
507.4096 | 417.4096 | 479.0615 | 285.4162 | 238.3332 | 301.0784 | 319.846 | 276.2317
508.4111 | 418.4111 | 479.1191 | 285.4556 | 238.8113 | 301.3271 | 319.8617 | 276.428
509.4025 | 419.4025 | 479.0555 | 285.4518 | 239.2735 | 301.6021 | 319.917 | 276.6968
510.4039 | 420.4039 | 478.9445 | 285.4469 | 239.7252 | 301.7877 | 320.7432 | 276.899
511.4054 | 421.4054 | 478.8407 | 285.4292 | 240.1908 | 301.9574 | 320.5481 | 277.2149
512.4068 | 422.4068 | 478.7927 | 285.3494 | 240.6589 | 301.9864 | 320.6565 | 277.3542
513.4082 | 423.4082 | 479.0006 | 285.2157 | 241.1067 | 301.8956 | 321.1226 | 277.5808
514.4097 | 424.4097 | 478.9857 | 284.9668 | 241.548 | 301.7329 | 321.6164 | 277.9062
515.4111 | 425.4111 | 478.8752 | 284.8498 | 241.9946 | 301.5889 | 321.8677 | 278.0464
516.4126 | 426.4126 | 478.8409 | 284.7304 | 242.4408 | 301.5058 | 321.651 | 278.3243
517.404 | 427.404 | 478.6428 | 284.6513 | 242.8931 | 301.4255 | 321.5165 | 278.4197
518.4054 | 428.4054 | 478.6973 | 284.598 | 243.3433 | 301.4042 | 322.2071 | 278.6409
519.4069 | 429.4069 | 478.7088 | 284.6166 | 243.7979 | 301.3583 | 322.8243 | 278.9852
520.4083 | 430.4083 | 478.4439 | 284.7873 | 244.251 | 301.2539 | 323.3873 | 279.2507
521.4097 | 431.4097 | 478.4212 | 285.027 | 244.7059 | 301.1017 | 323.7267 | 279.5179
522.4112 | 432.4112 | 478.3733 | 285.2452 | 245.1607 | 300.9516 | 324.8774 | 279.5984
523.4026 | 433.4026 | 478.2406 | 285.3678 | 245.5858 | 300.7933 | 326.2688 | 279.6776
524.4041 | 434.4041 | 478.0509 | 285.5874 | 246.0177 | 300.601 | 326.2128 | 279.9975
525.4055 | 435.4055 | 477.8674 | 285.8643 | 246.4634 | 300.443 | 326.224 | 280.4019
526.4069 | 436.4069 | 477.7222 | 286.0969 | 246.901 | 300.487 | 326.0312 | 280.8508
527.4084 | 437.4084 | 477.6888 | 286.415 | 247.327 | 300.4669 | 325.5741 | 281.1568
528.4098 | 438.4098 | 477.7385 | 286.7287 | 247.7814 | 300.4264 | 325.9047 | 281.3768
529.4113 | 439.4113 | 477.6676 | 286.9842 | 248.2097 | 300.4721 | 326.3453 | 281.7346
530.4027 | 440.4027 | 477.7233 | 287.1785 | 248.649 | 300.4952 | 325.8371 | 282.111
531.4041 | 441.4041 | 477.7688 | 287.4942 | 249.101 | 300.4759 | 325.2922 | 282.5639
532.4056 | 442.4056 | 477.6763 | 287.8431 | 249.5433 | 300.5923 | 325.194 | 283.0157
533.407 | 443.407 | 477.7209 | 288.1827 | 249.9977 | 300.786 | 326.0365 | 283.4811
534.4084 | 444.4084 | 477.7012 | 288.4507 | 250.4431 | 301.1073 | 325.6508 | 283.8167
535.4099 | 445.4099 | 477.6033 | 288.7536 | 250.8716 | 301.2945 | 325.2583 | 284.0366
536.4113 | 446.4113 | 477.5558 | 289.0277 | 251.3118 | 301.5574 | 325.0513 | 284.3808
537.4128 | 447.4128 | 477.47 | 289.3279 | 251.7436 | 301.9108 | 324.0072 | 284.5992
538.4042 | 448.4042 | 477.3912 | 289.759 | 252.1777 | 302.4322 | 323.7757 | 285.0188
539.4056 | 449.4056 | 477.4608 | 290.1365 | 252.6152 | 302.6867 | 323.2185 | 285.2978
540.4071 | 450.4071 | 477.63 | 290.66 | 253.0569 | 303.0724 | 323.1286 | 285.5687
541.4085 | 451.4085 | 477.7449 | 291.2283 | 253.4998 | 303.5136 | 322.9126 | 285.8973
542.4099 | 452.4099 | 477.8369 | 291.7059 | 253.9281 | 303.9723 | 322.9464 | 286.3317
543.4114 | 453.4114 | 477.865 | 292.0555 | 254.3567 | 304.4427 | 323.2322 | 286.4973
544.4028 | 454.4028 | 477.879 | 292.3778 | 254.7863 | 304.808 | 323.0175 | 286.7048
545.4043 | 455.4043 | 478.1779 | 292.6992 | 255.2496 | 305.1949 | 322.3496 | 286.8656
546.4057 | 456.4057 | 478.1924 | 293.1551 | 255.6706 | 305.5809 | 322.6823 | 286.8283
547.4071 | 457.4071 | 478.1704 | 293.655 | 256.109 | 305.9971 | 322.8844 | 286.9317
548.4086 | 458.4086 | 478.1897 | 294.1294 | 256.5289 | 306.3878 | 322.852 | 287.0824
549.41 | 459.41 | 478.2482 | 294.5075 | 257.0112 | 306.8347 | 322.1208 | 287.3211
550.4115 | 460.4115 | 478.2118 | 294.8656 | 257.4903 | 307.2752 | 322.4407 | 287.5104
551.4029 | 461.4029 | 478.0787 | 295.5293 | 257.9593 | 307.7693 | 323.5367 | 287.7545
552.4043 | 462.4043 | 477.8715 | 296.3373 | 258.4122 | 308.2831 | 323.6289 | 288.0576
553.4058 | 463.4058 | 477.5746 | 296.8133 | 258.8745 | 308.7944 | 324.1076 | 288.3207
554.4072 | 464.4072 | 477.4382 | 297.3888 | 259.313 | 309.2838 | 323.6681 | 288.4017
555.4086 | 465.4086 | 477.492 | 297.7765 | 259.7481 | 309.6572 | 323.8894 | 288.6795
556.4101 | 466.4101 | 477.5603 | 297.9624 | 260.1903 | 309.9628 | 324.0682 | 288.8979
557.4115 | 467.4115 | 477.5143 | 298.0007 | 260.6449 | 310.2517 | 323.8531 | 288.9966
558.413 | 468.413 | 477.5041 | 298.2385 | 261.0984 | 310.5108 | 323.0815 | 289.2104
559.4044 | 469.4044 | 477.6988 | 298.7106 | 261.5503 | 310.7295 | 323.2106 | 289.2315
560.4058 | 470.4058 | 477.8272 | 299.1127 | 262.0158 | 311.0138 | 323.373 | 289.3935
561.4073 | 471.4073 | 477.9255 | 299.4014 | 262.4628 | 311.346 | 323.8157 | 289.6197
562.4087 | 472.4087 | 478.0163 | 299.6308 | 262.8986 | 311.699 | 323.5338 | 289.9546
563.4101 | 473.4101 | 477.9179 | 299.9033 | 263.3057 | 312.0292 | 323.153 | 290.2322
564.4116 | 474.4116 | 477.7432 | 300.4151 | 263.7298 | 312.3949 | 323.0197 | 290.5255
565.403 | 475.403 | 477.6796 | 301.0067 | 264.1184 | 312.7174 | 323.6578 | 290.823
566.4044 | 476.4044 | 477.7611 | 301.985 | 264.5328 | 313.1173 | 323.9678 | 291.005
567.4059 | 477.4059 | 477.9359 | 302.3221 | 264.9709 | 313.4672 | 324.3827 | 291.1953
568.4073 | 478.4073 | 478.1087 | 302.7269 | 265.4115 | 313.779 | 324.7506 | 291.349
569.4088 | 479.4088 | 478.28 | 303.4085 | 265.8785 | 314.1242 | 325.0669 | 291.5148
570.4102 | 480.4102 | 478.3925 | 303.953 | 266.3725 | 314.4616 | 325.2167 | 291.6269
571.4016 | 481.4016 | 478.3113 | 304.1445 | 266.9072 | 314.799 | 325.6499 | 291.6992
572.4031 | 482.4031 | 478.1845 | 304.4164 | 267.3817 | 315.1516 | 325.8402 | 291.9217
573.4045 | 483.4045 | 478.2894 | 304.9128 | 267.8039 | 315.5242 | 326.5089 | 292.3071
574.406 | 484.406 | 478.3296 | 305.7832 | 268.1974 | 315.9043 | 326.4465 | 292.7524
575.4074 | 485.4074 | 478.388 | 306.6499 | 268.6058 | 316.2806 | 326.3178 | 292.9669
576.4088 | 486.4088 | 478.4595 | 307.4809 | 269.0543 | 316.644 | 326.3571 | 293.1507
577.4103 | 487.4103 | 478.4454 | 308.0805 | 269.4668 | 316.9619 | 325.6717 | 293.5855
578.4117 | 488.4117 | 478.486 | 308.2278 | 269.8941 | 317.2978 | 325.2093 | 293.8518
579.4132 | 489.4132 | 478.6119 | 308.8281 | 270.3205 | 317.66 | 325.3746 | 294.1186
580.4046 | 490.4046 | 478.7582 | 309.5272 | 270.7436 | 318.0452 | 324.9527 | 294.4537
581.406 | 491.406 | 478.8887 | 309.5766 | 271.2565 | 318.4121 | 324.4424 | 294.6386
582.4075 | 492.4075 | 479.0764 | 309.9141 | 271.7 | 318.7418 | 324.1335 | 295.019
583.4089 | 493.4089 | 479.2689 | 309.9663 | 272.1364 | 319.1529 | 323.2433 | 295.3279
584.4103 | 494.4103 | 479.3516 | 310.1483 | 272.5388 | 319.4857 | 323.778 | 295.6326
585.4118 | 495.4118 | 479.2734 | 310.5028 | 273.0779 | 319.6757 | 323.7474 | 296.0478
586.4032 | 496.4032 | 479.2038 | 310.7035 | 273.7561 | 319.8084 | 324.9585 | 296.271
587.4046 | 497.4046 | 479.0624 | 310.9882 | 274.4279 | 320.0388 | 325.1351 | 296.6629
588.4161 | 498.4161 | 479.0353 | 311.8033 | 274.9456 | 320.2466 | 324.6681 | 297.0642
589.4075 | 499.4075 | 478.9756 | 312.0599 | 275.3858 | 320.5431 | 325.1867 | 297.344
590.409 | 500.409 | 479.014 | 312.1934 | 275.7688 | 320.8617 | 324.5256 | 297.6509
591.4104 | 501.4104 | 478.9553 | 312.4415 | 276.1566 | 321.2765 | 324.7324 | 297.869
592.4018 | 502.4018 | 478.9433 | 312.7751 | 276.5507 | 321.4818 | 325.1492 | 298.1002
593.4033 | 503.4033 | 479.0154 | 313.2962 | 276.9828 | 321.6742 | 324.5992 | 298.4408
594.4047 | 504.4047 | 479.0416 | 313.8016 | 277.3605 | 321.8093 | 323.9275 | 298.7546
595.4062 | 505.4062 | 478.9234 | 313.928 | 277.7576 | 322.0338 | 324.0084 | 298.9655
596.4076 | 506.4076 | 478.8167 | 314.4175 | 278.1563 | 322.4627 | 323.1448 | 299.1802
597.409 | 507.409 | 478.7124 | 314.5566 | 278.5788 | 322.6936 | 322.6153 | 299.3984
598.4105 | 508.4105 | 478.612 | 315.1886 | 279.6529 | 322.8682 | 321.8977 | 299.6788
599.4119 | 509.4119 | 478.3875 | 315.4064 | 281.5562 | 323.072 | 321.8872 | 299.8868
600.4134 | 510.4134 | 478.351 | 315.1813 | 282.3946 | 323.3631 | 321.9598 | 300.0055
601.4048 | 511.4048 | 478.3796 | 314.7274 | 282.8743 | 323.682 | 322.1333 | 300.1814
602.4062 | 512.4062 | 478.2671 | 314.4994 | 283.2887 | 323.9461 | 322.356 | 300.3702
603.4077 | 513.4077 | 478.1544 | 314.7209 | 283.6887 | 324.252 | 322.5837 | 300.6567
604.4091 | 514.4091 | 478.0604 | 315.0825 | 284.1614 | 324.5517 | 323.145 | 301.0094
605.4105 | 515.4105 | 478.0062 | 315.868 | 284.7483 | 324.7329 | 322.1235 | 301.2741
606.412 | 516.412 | 478.0327 | 316.1588 | 285.1842 | 324.8836 | 321.629 | 301.6445
607.4034 | 517.4034 | 477.9176 | 316.3392 | 285.6527 | 325.097 | 321.3386 | 301.8899
608.4048 | 518.4048 | 477.9192 | 316.8393 | 286.2068 | 325.3656 | 321.1569 | 302.0706
609.4063 | 519.4063 | 477.9072 | 317.0758 | 286.863 | 325.653 | 321.121 | 302.3157
610.4077 | 520.4077 | 477.8999 | 317.3574 | 287.3283 | 325.9838 | 320.7897 | 302.4842
611.4092 | 521.4092 | 477.8965 | 317.2632 | 287.7623 | 326.2923 | 320.3549 | 302.5887
612.4106 | 522.4106 | 477.8563 | 316.7648 | 288.0685 | 326.5877 | 320.7851 | 302.6534
613.402 | 523.402 | 477.756 | 316.9948 | 288.328 | 326.9034 | 321.067 | 302.7913
614.4035 | 524.4035 | 477.9101 | 317.7306 | 288.5494 | 327.2311 | 320.587 | 302.8913
615.4049 | 525.4049 | 477.9508 | 318.2889 | 288.9614 | 327.5637 | 320.6886 | 303.0227
616.4063 | 526.4063 | 478.0062 | 318.1291 | 289.3325 | 327.9165 | 320.5145 | 303.3578
617.4078 | 527.4078 | 477.9986 | 318.6055 | 289.6811 | 328.2682 | 320.6291 | 303.3925
618.4092 | 528.4092 | 478.0461 | 318.5781 | 290.0484 | 328.6466 | 320.3562 | 303.5224
619.4107 | 529.4107 | 478.2314 | 318.3472 | 290.4084 | 328.5338 | 320.7281 | 303.747
620.4121 | 530.4121 | 478.3309 | 318.4719 | 290.8401 | 328.7588 | 321.3771 | 303.9323
621.4135 | 531.4135 | 478.3509 | 318.6412 | 291.2806 | 329.1691 | 321.9996 | 304.2402
622.405 | 532.405 | 478.324 | 318.8451 | 291.7687 | 329.5175 | 321.4726 | 304.4313
623.4064 | 533.4064 | 478.327 | 319.1864 | 292.1948 | 329.7758 | 321.1672 | 304.7924
624.4079 | 534.4079 | 478.4598 | 319.6901 | 292.4658 | 330.1315 | 321.3102 | 305.061
625.4093 | 535.4093 | 478.5798 | 319.7565 | 292.7231 | 330.4662 | 321.4917 | 305.2119
626.4107 | 536.4107 | 478.7047 | 320.2983 | 292.9547 | 330.7333 | 322.1211 | 305.3469
627.4122 | 537.4122 | 478.6799 | 320.1864 | 293.1775 | 331.0125 | 321.5632 | 305.527
628.4036 | 538.4036 | 478.6206 | 320.1361 | 293.3786 | 331.2261 | 321.6301 | 305.8995
629.405 | 539.405 | 478.5283 | 320.4382 | 293.6106 | 331.4618 | 320.9463 | 306.1731
630.4065 | 540.4065 | 478.5645 | 321.4698 | 293.8479 | 331.7482 | 321.0885 | 306.5318
631.4079 | 541.4079 | 478.6411 | 321.7432 | 294.0771 | 332.0616 | 320.563 | 306.744
632.4094 | 542.4094 | 478.6235 | 321.3526 | 294.4008 | 332.3258 | 320.0675 | 306.9769
633.4108 | 543.4108 | 478.5193 | 320.837 | 294.8565 | 332.511 | 319.9856 | 307.2753
634.4022 | 544.4022 | 478.4459 | 321.6002 | 295.2984 | 332.7735 | 319.7706 | 307.5303
635.4037 | 545.4037 | 478.3447 | 322.8856 | 295.7973 | 333.0726 | 320.0002 | 307.5998
636.4051 | 546.4051 | 478.2314 | 323.3125 | 296.2036 | 333.4075 | 319.3203 | 307.8064
637.4065 | 547.4065 | 478.2123 | 323.2329 | 296.5309 | 333.6874 | 319.8908 | 308.1679
638.408 | 548.408 | 478.1978 | 323.3064 | 296.8044 | 333.9525 | 319.9284 | 308.4775
639.4094 | 549.4094 | 478.2313 | 323.7693 | 297.0494 | 334.3135 | 319.556 | 308.7966
640.4109 | 550.4109 | 478.1623 | 324.4705 | 297.2725 | 334.5597 | 319.1896 | 309.1417
641.4023 | 551.4023 | 478.1188 | 325.1204 | 297.4989 | 334.7965 | 319.1027 | 309.496
642.4037 | 552.4037 | 478.209 | 325.1738 | 297.8332 | 334.9922 | 320.1534 | 309.8604
643.4052 | 553.4052 | 478.3001 | 325.4241 | 298.3836 | 335.2316 | 320.5561 | 310.1499
644.4066 | 554.4066 | 478.2483 | 325.4583 | 299.0073 | 335.5296 | 320.3508 | 310.4985
645.4081 | 555.4081 | 478.2425 | 325.7477 | 299.4813 | 335.8572 | 320.2846 | 310.8685
646.4095 | 556.4095 | 478.2258 | 326.491 | 299.7934 | 336.1653 | 321.4907 | 311.2096
647.4109 | 557.4109 | 478.2376 | 327.2741 | 300.0845 | 336.3723 | 320.5265 | 311.5639
648.4124 | 558.4124 | 478.3017 | 327.1457 | 300.37 | 336.6326 | 318.8091 | 311.8746
649.4038 | 559.4038 | 478.2798 | 327.1585 | 300.6137 | 336.925 | 318.6858 | 312.3204
650.4052 | 560.4052 | 478.181 | 328.0823 | 300.9154 | 337.158 | 319.0498 | 312.7976
651.4067 | 561.4067 | 478.0732 | 327.833 | 301.1741 | 337.4816 | 319.823 | 313.3164
652.4081 | 562.4081 | 478.0891 | 328.1466 | 301.4783 | 337.7063 | 319.422 | 313.7467
653.4096 | 563.4096 | 478.1347 | 328.5434 | 301.8173 | 337.9915 | 318.5343 | 314.069
654.411 | 564.411 | 478.2303 | 329.067 | 302.4812 | 338.3097 | 318.291 | 314.4357
655.4024 | 565.4024 | 478.2861 | 329.4794 | 303.1559 | 338.4534 | 317.706 | 314.6508
656.4039 | 566.4039 | 478.3202 | 329.974 | 303.6181 | 338.6723 | 317.624 | 315.0631
657.4053 | 567.4053 | 478.3358 | 329.6608 | 303.9039 | 338.9407 | 317.4969 | 315.3473
658.4067 | 568.4067 | 478.3784 | 330.1352 | 304.1925 | 339.251 | 317.0015 | 315.4712
659.4082 | 569.4082 | 478.2907 | 330.3205 | 304.4149 | 339.5689 | 317.2218 | 315.6982
660.4096 | 570.4096 | 478.3056 | 330.9781 | 304.8541 | 339.5528 | 317.7688 | 315.6923
661.4111 | 571.4111 | 478.3306 | 331.5564 | 305.4351 | 339.7215 | 318.7049 | 315.8048
662.4025 | 572.4025 | 478.3065 | 331.6885 | 305.8138 | 339.9668 | 319.6972 | 316.0855
663.4039 | 573.4039 | 478.4273 | 332.7767 | 306.1702 | 340.2312 | 319.7927 | 316.4555
664.4054 | 574.4054 | 478.4879 | 333.352 | 306.4665 | 340.6253 | 318.6743 | 316.5871
665.4068 | 575.4068 | 478.5164 | 333.8308 | 306.7741 | 340.9225 | 318.3958 | 317.0041
666.4082 | 576.4082 | 478.5335 | 334.1549 | 307.0699 | 341.2251 | 318.6426 | 317.4928
667.4097 | 577.4097 | 478.5308 | 334.0065 | 307.6174 | 341.5264 | 317.9735 | 317.9605
668.4111 | 578.4111 | 478.4448 | 333.8389 | 308.2957 | 341.7489 | 317.9951 | 318.4078
669.4126 | 579.4126 | 478.432 | 334.582 | 308.8514 | 341.9493 | 317.948 | 318.8311
670.414 | 580.414 | 478.3103 | 335.0306 | 309.1567 | 342.2767 | 318.2766 | 319.3102
671.4054 | 581.4054 | 478.4562 | 335.078 | 309.3936 | 342.5637 | 318.0916 | 319.7917
672.4069 | 582.4069 | 478.4614 | 336.5661 | 309.5889 | 342.8411 | 316.8647 | 320.3561
673.4083 | 583.4083 | 478.3675 | 336.9084 | 309.8894 | 343.1399 | 316.5876 | 320.7672
674.4098 | 584.4098 | 478.4323 | 337.4513 | 310.2396 | 343.4525 | 317.8688 | 321.1466
675.4112 | 585.4112 | 478.5289 | 337.9875 | 310.5076 | 343.7285 | 318.3548 | 321.5752
676.4026 | 586.4026 | 478.5341 | 338.4082 | 310.9265 | 343.8212 | 317.9906 | 322.1974
677.4041 | 587.4041 | 478.6579 | 338.549 | 311.2479 | 343.989 | 318.665 | 322.8689
678.4055 | 588.4055 | 478.7069 | 338.3511 | 311.5269 | 344.1311 | 319.0689 | 323.4012
679.4069 | 589.4069 | 478.866 | 338.9734 | 311.9441 | 344.4388 | 318.7856 | 323.8856
680.4084 | 590.4084 | 478.9337 | 339.6258 | 312.34 | 344.7103 | 319.5942 | 324.4229
681.4098 | 591.4098 | 478.92 | 339.413 | 312.6696 | 344.9761 | 318.6354 | 325.0355
682.4113 | 592.4113 | 478.8657 | 339.8051 | 313.0358 | 345.2185 | 317.4024 | 325.6472
683.4027 | 593.4027 | 478.8704 | 340.2554 | 313.6082 | 345.4637 | 318.8819 | 326.1453
684.4041 | 594.4041 | 478.8262 | 341.0208 | 314.0823 | 345.7226 | 318.6776 | 326.3935
685.4056 | 595.4056 | 478.752 | 341.3901 | 314.507 | 345.9459 | 318.3412 | 326.7409
686.407 | 596.407 | 478.8038 | 341.46 | 314.9619 | 346.122 | 318.9028 | 327.2751
687.4084 | 597.4084 | 478.8708 | 342.1222 | 315.2468 | 346.3634 | 318.8082 | 327.7708
688.4099 | 598.4099 | 478.8578 | 342.2129 | 315.4118 | 346.6094 | 317.7351 | 328.172
689.4113 | 599.4113 | 478.8294 | 342.5886 | 315.7472 | 346.8538 | 318.3256 | 328.6462
690.4128 | 600.4128 | 478.8135 | 342.9252 | 316.0416 | 347.0452 | 318.2153 | 329.2303
691.4042 | 601.4042 | 478.8272 | 342.5582 | 316.2793 | 347.3457 | 317.3761 | 329.6909
692.4056 | 602.4056 | 478.9113 | 342.608 | 316.4686 | 347.592 | 317.8909 | 330.2109
693.4071 | 603.4071 | 479.0247 | 342.9403 | 316.7669 | 347.8041 | 318.113 | 330.7765
694.4085 | 604.4085 | 479.1314 | 343.4295 | 317.1205 | 347.9902 | 319.0973 | 331.3199
695.41 | 605.41 | 479.2499 | 343.8727 | 317.6403 | 348.3235 | 318.8495 | 331.8567
696.4114 | 606.4114 | 479.1343 | 344.6995 | 318.1153 | 348.5608 | 318.2015 | 332.338
697.4028 | 607.4028 | 479.2225 | 344.6074 | 318.4239 | 348.8389 | 318.3995 | 332.9084
698.4043 | 608.4043 | 479.2498 | 345.3614 | 318.6364 | 349.0896 | 319.8434 | 333.421
699.4057 | 609.4057 | 479.352 | 345.697 | 318.8332 | 349.35 | 318.826 | 333.806
700.4071 | 610.4071 | 479.3571 | 346.1228 | 319.0878 | 349.6015 | 318.7838 | 334.0922
701.4086 | 611.4086 | 479.364 | 346.4403 | 319.339 | 349.8169 | 319.6377 | 334.3696
702.41 | 612.41 | 479.156 | 346.7189 | 319.6296 | 350.0855 | 320.5916 | 334.4966
703.4115 | 613.4115 | 479.0262 | 346.7261 | 320.0931 | 350.4053 | 321.0598 | 334.389
704.4029 | 614.4029 | 478.9347 | 346.5941 | 320.6889 | 350.74 | 321.0718 | 334.4242
705.4043 | 615.4043 | 478.8962 | 346.881 | 321.3358 | 350.9811 | 321.839 | 334.4666
706.4058 | 616.4058 | 478.961 | 347.5042 | 321.8659 | 351.1795 | 322.6309 | 334.6222
707.4072 | 617.4072 | 478.9141 | 347.8796 | 322.0838 | 351.429 | 322.7841 | 334.8131
708.4086 | 618.4086 | 478.9067 | 348.7217 | 322.2494 | 351.6627 | 322.9246 | 334.9889
709.4101 | 619.4101 | 478.7811 | 349.142 | 322.8317 | 351.9245 | 323.4209 | 335.227
710.4115 | 620.4115 | 478.5419 | 349.3691 | 323.2633 | 352.1637 | 324.3114 | 335.4004
711.4029 | 621.4029 | 478.5929 | 349.9287 | 323.4702 | 352.2814 | 323.714 | 335.503
712.4044 | 622.4044 | 478.6109 | 350.4367 | 323.6408 | 352.3173 | 323.4785 | 335.6319
713.4058 | 623.4058 | 478.4126 | 350.2384 | 323.7915 | 352.5214 | 323.0287 | 335.868
714.4073 | 624.4073 | 478.3809 | 350.9939 | 323.9762 | 352.7888 | 323.2058 | 336.0089
715.4087 | 625.4087 | 478.2256 | 351.1393 | 324.2195 | 352.9654 | 323.2476 | 336.1293
716.4101 | 626.4101 | 478.1982 | 350.6322 | 324.8815 | 353.2214 | 322.041 | 336.396
717.4116 | 627.4116 | 478.1699 | 351.1903 | 325.5048 | 353.4888 | 321.7295 | 336.6382
718.403 | 628.403 | 478.1898 | 352.3651 | 326.076 | 353.6935 | 321.8444 | 336.9732
719.4045 | 629.4045 | 478.2122 | 352.689 | 326.3808 | 353.9376 | 321.1215 | 337.3223
720.4059 | 630.4059 | 478.2012 | 353.142 | 326.5153 | 354.1552 | 321.3677 | 337.5514
721.4073 | 631.4073 | 478.115 | 353.2915 | 326.6533 | 354.3804 | 320.9211 | 337.648
722.4088 | 632.4088 | 478.0088 | 353.4511 | 326.7933 | 354.5273 | 321.0605 | 337.7364
723.4102 | 633.4102 | 477.892 | 353.748 | 326.9743 | 354.6115 | 321.1534 | 337.8334
724.4117 | 634.4117 | 477.7985 | 353.8765 | 327.4093 | 354.84 | 320.0561 | 337.9764
725.4031 | 635.4031 | 477.7555 | 354.1728 | 327.9526 | 355.054 | 319.8618 | 338.1309
726.4045 | 636.4045 | 477.7106 | 354.6571 | 328.3415 | 355.263 | 319.8825 | 338.2877
727.406 | 637.406 | 477.7214 | 354.9459 | 328.6618 | 355.5417 | 319.3886 | 338.484
728.4074 | 638.4074 | 477.7837 | 354.6621 | 328.8979 | 355.8546 | 319.5473 | 338.7057
729.4088 | 639.4088 | 478.0972 | 354.8677 | 329.1163 | 356.1185 | 319.3644 | 345.5487
730.4103 | 640.4103 | 478.2442 | 355.3495 | 329.4026 | 356.3148 | 320.5269 | 360.4965
731.4117 | 641.4117 | 478.3849 | 355.3971 | 329.7492 | 356.3151 | 321.882 | 379.7753
732.4132 | 642.4132 | 478.4386 | 356.159 | 329.9934 | 356.6452 | 323.6061 | 397.8263
733.4046 | 643.4046 | 478.4641 | 356.888 | 330.1424 | 356.9802 | 325.3214 | 413.326
734.406 | 644.406 | 478.4694 | 357.0573 | 330.3587 | 357.218 | 327.371 | 425.2391
735.4075 | 645.4075 | 478.5211 | 357.371 | 330.7135 | 357.6216 | 329.4978 | 434.1745
736.4089 | 646.4089 | 478.5501 | 357.6948 | 331.047 | 358.3406 | 331.6235 | 440.976
737.4103 | 647.4103 | 478.6608 | 358.0486 | 331.3471 | 359.366 | 333.9149 | 448.006
738.4118 | 648.4118 | 478.8828 | 358.8942 | 331.6516 | 361.0308 | 334.9534 | 455.3123
739.4032 | 649.4032 | 479.0333 | 359.8159 | 331.9646 | 363.2094 | 337.3617 | 462.2344
740.4046 | 650.4046 | 479.2364 | 360.1896 | 332.2046 | 365.813 | 340.0973 | 470.2508
741.4061 | 651.4061 | 479.4255 | 360.7211 | 332.4488 | 368.7384 | 342.9564 | 478.2287
742.4075 | 652.4075 | 479.6655 | 361.6916 | 333.0496 | 371.8565 | 344.3978 | 487.4219
743.409 | 653.409 | 479.8899 | 362.3941 | 334.3927 | 374.7037 | 354.2132 | 494.798
744.4104 | 654.4104 | 480.1478 | 363.1395 | 335.2413 | 377.7202 | 368.4348 | 501.5741
745.4018 | 655.4018 | 480.2806 | 364.8536 | 335.5762 | 380.9181 | 367.3255 | 511.0826
746.4033 | 656.4033 | 480.2463 | 365.0436 | 335.6918 | 384.1819 | 367.3915 | 520.7358
747.4047 | 657.4047 | 480.3532 | 366.9084 | 336.4266 | 387.4808 | 371.0171 | 530.279
748.4062 | 658.4062 | 480.4624 | 368.4718 | 337.2285 | 390.8309 | 372.7778 | 540.0851
749.4076 | 659.4076 | 480.4018 | 369.5855 | 337.671 | 394.0241 | 373.864 | 551.1635
750.409 | 660.409 | 480.2955 | 370.8492 | 337.8582 | 397.4071 | 374.4633 | 557.4581
751.4105 | 661.4105 | 480.1679 | 372.1749 | 338.1257 | 400.7574 | 375.914 | 563.178
752.4119 | 662.4119 | 480.2284 | 372.7186 | 338.4134 | 403.9855 | 377.2396 | 567.5317
753.4134 | 663.4134 | 480.2315 | 374.2061 | 338.6599 | 406.9414 | 379.0755 | 572.1464
754.4048 | 664.4048 | 480.2063 | 376.0162 | 339.7722 | 409.7396 | 381.631 | 579.982
755.4062 | 665.4062 | 480.0488 | 377.7331 | 340.8101 | 412.847 | 385.2246 | 585.6579
756.4077 | 666.4077 | 479.732 | 378.8239 | 341.2787 | 415.9699 | 387.9428 | 588.7582
757.4091 | 667.4091 | 479.5032 | 380.977 | 341.559 | 419.195 | 391.541 | 592.7075
758.4105 | 668.4105 | 479.3141 | 381.9834 | 341.8508 | 422.4232 | 394.4564 | 596.1381
759.412 | 669.412 | 479.0003 | 383.0268 | 342.2095 | 425.6613 | 397.64 | 600.7914
760.4134 | 670.4134 | 478.5407 | 384.952 | 342.5984 | 428.7505 | 400.4624 | 604.4049
761.4048 | 671.4048 | 478.1942 | 385.2282 | 342.9805 | 431.6214 | 403.607 | 603.3413
762.4063 | 672.4063 | 477.8085 | 386.4241 | 343.3285 | 434.5817 | 405.692 | 605.3139
763.4077 | 673.4077 | 477.5632 | 388.2013 | 343.7925 | 437.3432 | 407.9427 | 607.0742
764.4092 | 674.4092 | 477.0573 | 388.5898 | 344.2734 | 440.2416 | 410.0345 | 608.4839
765.4106 | 675.4106 | 476.5117 | 389.0376 | 344.8525 | 443.1751 | 412.2879 | 611.1297
766.402 | 676.402 | 476.0431 | 389.6386 | 345.4191 | 446.244 | 413.3723 | 614.0845
767.4035 | 677.4035 | 475.4819 | 389.8065 | 346.0567 | 449.381 | 413.8252 | 613.6144
768.4049 | 678.4049 | 474.9308 | 390.7429 | 346.6659 | 452.4442 | 414.2096 | 613.3725
769.5666 | 679.5666 | 474.3116 | 392.5909 | 347.334 | 453.8737 | 415.2882 | 611.6163
770.4078 | 680.4078 | 473.7578 | 393.7549 | 347.9446 | 451.8516 | 415.6623 | 610.9285
771.4092 | 681.4092 | 473.402 | 394.9166 | 348.5478 | 450.3293 | 416.7183 | 608.945
772.4107 | 682.4107 | 473.2745 | 396.0523 | 349.1479 | 449.234 | 417.6949 | 605.5953
773.4121 | 683.4121 | 472.9367 | 397.5256 | 349.7518 | 446.9551 | 418.5693 | 601.6015
774.4136 | 684.4136 | 472.3882 | 398.7151 | 350.2808 | 446.2105 | 420.3717 | 598.9776
775.405 | 685.405 | 471.9283 | 399.9868 | 350.8001 | 445.4706 | 422.2523 | 597.3406
776.4064 | 686.4064 | 471.4534 | 402.0108 | 351.3684 | 445.7057 | 423.3326 | 594.8405
777.4079 | 687.4079 | 471.1075 | 403.5758 | 351.9035 | 447.3865 | 424.221 | 594.937
778.4093 | 688.4093 | 470.4686 | 405.4871 | 352.3761 | 450.0567 | 425.4476 | 593.6468
779.4107 | 689.4107 | 470.283 | 405.9999 | 353.0185 | 452.8433 | 427.4373 | 593.1745
780.4122 | 690.4122 | 470.1018 | 406.8238 | 353.6749 | 458.0186 | 428.1433 | 592.195
781.4036 | 691.4036 | 469.8375 | 407.6994 | 354.2914 | 464.3078 | 428.7404 | 591.2013
782.405 | 692.405 | 469.5467 | 408.7311 | 354.8616 | 471.9746 | 428.9225 | 593.0757
783.4065 | 693.4065 | 469.2777 | 409.6058 | 355.5724 | 478.4684 | 429.1415 | 591.6265
784.4079 | 694.4079 | 469.1416 | 410.6109 | 356.2093 | 483.2069 | 429.6921 | 591.2459
785.4094 | 695.4094 | 468.5648 | 411.8653 | 356.9504 | 487.2773 | 430.521 | 592.9958
786.4108 | 696.4108 | 467.8983 | 413.1062 | 357.6139 | 490.4319 | 431.5162 | 594.0399
787.4122 | 697.4122 | 467.1303 | 414.303 | 358.1751 | 492.0834 | 431.5898 | 596.1943
788.4037 | 698.4037 | 466.4385 | 415.3937 | 358.9601 | 494.6775 | 431.754 | 596.8499
789.4051 | 699.4051 | 465.8212 | 416.4389 | 359.6808 | 495.5478 | 430.8462 | 597.3809
790.4065 | 700.4065 | 465.3521 | 417.6811 | 360.121 | 495.8952 | 430.2994 | 599.7982
791.408 | 701.408 | 464.9284 | 418.7879 | 360.7162 | 495.4433 | 430.3534 | 602.3724
792.4094 | 702.4094 | 464.5666 | 419.763 | 361.2254 | 495.3875 | 430.7901 | 602.8832
793.4109 | 703.4109 | 464.1986 | 420.6586 | 361.7305 | 496.8105 | 430.7697 | 605.0936
794.4123 | 704.4123 | 463.6696 | 421.6893 | 362.3977 | 495.4688 | 430.3694 | 605.4516
795.4137 | 705.4137 | 462.8738 | 422.6114 | 363.054 | 495.0299 | 429.5737 | 605.7214
796.4052 | 706.4052 | 462.1734 | 423.2304 | 363.7603 | 494.9793 | 428.2991 | 606.3684
797.4066 | 707.4066 | 461.4148 | 423.9141 | 364.3892 | 495.4545 | 426.8427 | 608.3818
798.4081 | 708.4081 | 460.803 | 424.509 | 365.1729 | 494.8554 | 426.2838 | 611.5697
799.4095 | 709.4095 | 460.3156 | 425.0355 | 365.7183 | 495.9912 | 424.8197 | 615.9434
800.4109 | 710.4109 | 459.6696 | 425.9503 | 366.4037 | 496.7849 | 424.3884 | 620.4581
801.4024 | 711.4024 | 459.0453 | 426.5102 | 367.1036 | 496.8967 | 424.5436 | 622.4562
802.4038 | 712.4038 | 458.486 | 426.9506 | 367.6403 | 497.8751 | 423.789 | 624.6994
803.4052 | 713.4052 | 457.944 | 427.4855 | 368.3031 | 498.0654 | 423.609 | 627.3891
804.4067 | 714.4067 | 457.5088 | 428.1934 | 368.9775 | 499.0112 | 423.2116 | 631.4845
805.4081 | 715.4081 | 457.0937 | 429.0313 | 369.6811 | 499.5312 | 422.3681 | 636.0077
806.4096 | 716.4096 | 456.4561 | 429.9887 | 370.3247 | 499.596 | 420.9913 | 637.7686
807.411 | 717.411 | 455.9625 | 430.9941 | 371.1527 | 498.6252 | 419.6069 | 637.6533
808.4024 | 718.4024 | 455.2909 | 431.9643 | 371.7968 | 497.1605 | 418.0055 | 637.2906
809.4039 | 719.4039 | 454.5665 | 432.7041 | 372.4767 | 497.2853 | 417.0586 | 638.1512
810.4053 | 720.4053 | 453.8576 | 433.2866 | 373.1135 | 498.7085 | 416.5486 | 638.5005
811.4067 | 721.4067 | 453.1485 | 434.7173 | 373.8215 | 500.6667 | 416.3588 | 640.8144
812.4082 | 722.4082 | 452.5697 | 435.143 | 374.5025 | 502.4093 | 415.9975 | 640.3751
813.4096 | 723.4096 | 451.9669 | 436.3741 | 375.1807 | 503.5522 | 415.2224 | 639.9545
814.4111 | 724.4111 | 451.197 | 436.9852 | 375.9305 | 503.7798 | 413.7449 | 640.8844
815.4125 | 725.4125 | 450.4105 | 437.0945 | 376.6898 | 503.9936 | 411.5399 | 642.5803
816.4039 | 726.4039 | 449.7081 | 438.2307 | 377.3534 | 503.792 | 410.5966 | 642.3611
817.4054 | 727.4054 | 449.0181 | 438.7982 | 377.9787 | 503.8964 | 409.5084 | 641.7466
818.4068 | 728.4068 | 448.3074 | 439.877 | 378.7172 | 503.7355 | 409.0084 | 640.1202
819.4083 | 729.4083 | 447.6168 | 440.5825 | 379.387 | 503.4863 | 408.2965 | 641.0472
820.4097 | 730.4097 | 446.9686 | 441.3428 | 380.1194 | 503.7975 | 407.3574 | 640.9578
821.4111 | 731.4111 | 446.3914 | 441.9779 | 380.7086 | 505.3358 | 406.9193 | 640.5563
822.4126 | 732.4126 | 445.8758 | 442.284 | 381.343 | 506.644 | 406.3522 | 640.2443
823.404 | 733.404 | 445.2915 | 442.275 | 381.9956 | 507.0471 | 404.9291 | 639.1604
824.4054 | 734.4054 | 444.8978 | 442.1614 | 382.5929 | 506.6136 | 403.8422 | 639.4223
825.4069 | 735.4069 | 444.4924 | 443.3877 | 383.219 | 506.5313 | 402.4592 | 639.5577
826.4083 | 736.4083 | 444.0129 | 443.8504 | 383.9369 | 506.8375 | 402.0471 | 640.4316
827.4098 | 737.4098 | 443.703 | 444.39 | 384.5929 | 506.925 | 402.0905 | 638.904
828.4112 | 738.4112 | 443.3399 | 444.8583 | 385.2669 | 507.5237 | 401.3754 | 640.0671
829.4026 | 739.4026 | 442.7565 | 444.5753 | 385.9222 | 507.9305 | 400.8126 | 640.9226
830.4041 | 740.4041 | 442.0927 | 444.9512 | 386.5211 | 508.7403 | 400.207 | 640.9094
831.4055 | 741.4055 | 441.7297 | 444.8264 | 387.1017 | 509.1888 | 399.0192 | 641.1103
832.4069 | 742.4069 | 441.0673 | 444.9571 | 387.6541 | 509.7371 | 397.2556 | 639.908
833.4084 | 743.4084 | 440.2735 | 445.0541 | 388.2799 | 510.3767 | 396.4769 | 639.0113
834.4098 | 744.4098 | 439.511 | 445.1452 | 388.9127 | 510.4058 | 394.9816 | 637.7605
835.4113 | 745.4113 | 438.9044 | 445.2626 | 389.5021 | 510.4355 | 393.9805 | 638.4622
836.4127 | 746.4127 | 438.4039 | 445.3916 | 390.1024 | 510.6595 | 392.2289 | 637.2474
837.4041 | 747.4041 | 437.7794 | 445.2562 | 390.715 | 510.9915 | 391.9885 | 636.3468
838.4056 | 748.4056 | 437.0821 | 445.2927 | 391.2468 | 510.9543 | 390.7393 | 636.0876
839.407 | 749.407 | 436.4132 | 445.2806 | 391.8045 | 511.0317 | 389.597 | 635.3978
840.4084 | 750.4084 | 435.8547 | 445.2515 | 392.3079 | 511.0621 | 388.658 | 638.2718
841.4099 | 751.4099 | 435.1659 | 445.0094 | 392.8042 | 510.9256 | 388.1998 | 637.9298
842.4113 | 752.4113 | 434.5581 | 444.9039 | 393.2113 | 511.2847 | 387.6429 | 637.1954
843.4028 | 753.4028 | 434.0931 | 444.7213 | 393.6878 | 511.3607 | 386.6127 | 638.7479
844.4042 | 754.4042 | 433.563 | 444.5399 | 394.0462 | 511.7754 | 386.21 | 638.4452
845.4056 | 755.4056 | 433.0919 | 444.1893 | 394.4471 | 512.2702 | 385.1164 | 640.0203
846.4071 | 756.4071 | 432.6005 | 443.925 | 394.7746 | 512.8582 | 383.8061 | 642.2816
847.4085 | 757.4085 | 432.1716 | 443.8067 | 395.0876 | 513.1636 | 382.6262 | 640.7775
848.41 | 758.41 | 431.6948 | 443.8738 | 395.4115 | 513.8908 | 381.2386 | 638.9651
849.4114 | 759.4114 | 431.2246 | 443.7656 | 395.6823 | 514.1859 | 379.544 | 634.4873
850.4028 | 760.4028 | 430.5762 | 443.7382 | 395.899 | 515.0703 | 379.3658 | 635.8719
851.4043 | 761.4043 | 430.049 | 443.8061 | 396.1743 | 515.9391 | 379.0127 | 633.1099
852.4057 | 762.4057 | 429.4555 | 443.8208 | 396.4164 | 517.4219 | 379.2701 | 632.3878
853.4071 | 763.4071 | 428.9298 | 444.0277 | 396.6432 | 518.5948 | 378.2436 | 632.3286
854.4086 | 764.4086 | 428.3874 | 444.1534 | 396.8769 | 519.611 | 377.8789 | 630.0468
855.41 | 765.41 | 427.9111 | 444.2486 | 397.091 | 520.2263 | 377.5925 | 629.2805
856.4115 | 766.4115 | 427.4029 | 444.4708 | 397.346 | 521.0779 | 376.6239 | 629.8039
857.4129 | 767.4129 | 426.9825 | 444.8011 | 397.5428 | 521.8147 | 376.37 | 631.8562
858.4043 | 768.4043 | 426.3454 | 445.0537 | 397.8267 | 522.7805 | 375.3972 | 632.3403
859.4058 | 769.4058 | 425.7792 | 445.3315 | 398.0937 | 524.0086 | 374.1233 | 634.8775
860.4072 | 770.4072 | 425.2427 | 445.6862 | 398.3426 | 523.0381 | 374.6434 | 635.9142
861.4086 | 771.4086 | 424.6686 | 445.8244 | 398.6541 | 522.6506 | 374.164 | 636.0898
862.4101 | 772.4101 | 424.0282 | 446.0522 | 398.9887 | 523.0878 | 373.4703 | 637.543
863.4115 | 773.4115 | 423.3941 | 446.2563 | 399.2774 | 523.2534 | 372.4003 | 637.6754
864.413 | 774.413 | 422.9054 | 446.5884 | 399.5551 | 523.9699 | 371.1321 | 635.8221
865.4044 | 775.4044 | 422.4754 | 446.8909 | 399.8841 | 524.4667 | 370.6434 | 633.8246
866.4058 | 776.4058 | 421.9385 | 447.1976 | 400.1528 | 524.4896 | 369.7291 | 635.107
867.4073 | 777.4073 | 421.4078 | 447.5187 | 400.4837 | 524.72 | 369.0092 | 635.3896
868.4087 | 778.4087 | 420.9927 | 447.9003 | 400.8241 | 524.9228 | 368.0274 | 632.3
869.4102 | 779.4102 | 420.4213 | 448.303 | 401.2648 | 525.423 | 367.7395 | 634.0573
870.4116 | 780.4116 | 420.0144 | 448.6563 | 401.6429 | 526.0648 | 367.3812 | 634.6356
871.403 | 781.403 | 419.6927 | 449.1243 | 402.016 | 526.5316 | 365.8543 | 631.2588
872.4045 | 782.4045 | 419.2678 | 449.5585 | 402.3638 | 526.8816 | 365.6405 | 632.1173
873.4059 | 783.4059 | 418.8332 | 449.9956 | 402.7647 | 527.1487 | 365.3367 | 632.6723
874.4073 | 784.4073 | 418.3524 | 450.4174 | 403.1629 | 527.5975 | 364.378 | 630.6786
875.4088 | 785.4088 | 417.8009 | 450.8415 | 403.569 | 529.2159 | 364.3914 | 630.8226
876.4102 | 786.4102 | 417.2762 | 451.2507 | 403.9766 | 529.9415 | 363.4005 | 634.3305
877.4016 | 787.4016 | 416.854 | 451.6854 | 404.4584 | 529.8211 | 362.4444 | 635.1171
878.4131 | 788.4131 | 416.2412 | 452.1298 | 404.9892 | 529.4868 | 361.7934 | 631.6481
879.4045 | 789.4045 | 415.6291 | 452.4949 | 405.4641 | 529.3858 | 361.5684 | 631.5062
880.406 | 790.406 | 415.208 | 452.9142 | 405.872 | 529.5754 | 360.6947 | 630.8541
881.4074 | 791.4074 | 414.6431 | 453.3169 | 406.408 | 529.7475 | 359.4486 | 627.6349
882.4088 | 792.4088 | 414.2234 | 453.7492 | 406.9486 | 530.0218 | 358.4325 | 627.0045
883.4103 | 793.4103 | 413.7313 | 454.1207 | 407.4235 | 530.9943 | 358.2966 | 626.8896
884.4117 | 794.4117 | 413.1158 | 454.4565 | 407.965 | 532.2925 | 356.845 | 629.4448
885.4031 | 795.4031 | 412.5137 | 454.9159 | 408.4224 | 533.692 | 356.2563 | 631.9476
886.4046 | 796.4046 | 412.0231 | 455.2139 | 408.905 | 534.7221 | 356.0551 | 634.8671
887.406 | 797.406 | 411.5704 | 455.5892 | 409.4479 | 535.2524 | 354.9046 | 638.9828
888.4075 | 798.4075 | 411.11 | 455.9138 | 409.9402 | 534.9797 | 354.2558 | 637.4653
889.4089 | 799.4089 | 410.6099 | 456.3641 | 410.4495 | 535.0249 | 354.6206 | 638.1198
890.4103 | 800.4103 | 410.0685 | 456.7086 | 410.9401 | 535.1219 | 354.0097 | 637.4346
891.4118 | 801.4118 | 409.5814 | 457.2219 | 411.4076 | 535.0352 | 353.8745 | 639.9641
892.4032 | 802.4032 | 409.1556 | 457.7231 | 411.8303 | 535.4859 | 353.5684 | 638.007
893.4047 | 803.4047 | 408.8141 | 458.1733 | 412.2814 | 536.0328 | 353.4429 | 637.0326
894.4061 | 804.4061 | 408.4511 | 458.3267 | 412.7109 | 536.1924 | 351.5284 | 638.3845
895.4075 | 805.4075 | 407.9815 | 458.4928 | 413.1062 | 536.3027 | 350.0458 | 640.9098
896.409 | 806.409 | 407.4121 | 459.0657 | 413.5995 | 536.3222 | 350.1254 | 640.6977
897.4104 | 807.4104 | 406.9016 | 459.5548 | 414.05 | 536.7768 | 349.0637 | 637.9523
898.4018 | 808.4018 | 406.354 | 460.1177 | 414.477 | 536.7516 | 349.3789 | 639.2329
899.4133 | 809.4133 | 405.9197 | 460.5956 | 414.9169 | 536.7404 | 348.7455 | 640.448
900.4047 | 810.4047 | 405.4946 | 460.952 | 415.4951 | 536.4968 | 348.5009 | 640.6345
901.4062 | 811.4062 | 404.9823 | 461.5681 | 416.1273 | 536.2287 | 348.2758 | 640.4548
902.4076 | 812.4076 | 404.5224 | 462.136 | 416.7317 | 536.4057 | 348.5829 | 638.9408
903.409 | 813.409 | 404.1158 | 462.7094 | 417.3583 | 536.4344 | 347.9776 | 639.3929
904.4105 | 814.4105 | 403.6156 | 463.2938 | 418.0404 | 536.4872 | 346.6005 | 635.4937
905.4119 | 815.4119 | 403.1917 | 463.8702 | 418.8644 | 536.6238 | 345.5479 | 634.219
906.4033 | 816.4033 | 402.8213 | 464.6238 | 419.649 | 536.5741 | 345.196 | 637.0878
907.4048 | 817.4048 | 402.3492 | 465.2679 | 420.4413 | 536.4394 | 344.396 | 637.9933
908.4062 | 818.4062 | 401.8437 | 465.8969 | 421.2701 | 536.9758 | 344.1917 | 636.6892
909.4077 | 819.4077 | 401.322 | 466.5516 | 422.1871 | 537.6506 | 344.6098 | 636.4911
910.4091 | 820.4091 | 401.0744 | 467.1465 | 423.0905 | 538.0413 | 345.0914 | 638.9769
911.4105 | 821.4105 | 400.7055 | 467.6661 | 424.0548 | 538.4712 | 344.2846 | 640.2584
912.412 | 822.412 | 400.2076 | 468.5068 | 424.9096 | 539.0216 | 343.821 | 641.5923
913.4034 | 823.4034 | 399.6261 | 469.0059 | 425.7741 | 539.2697 | 343.9054 | 643.6405
914.4048 | 824.4048 | 399.1345 | 469.4494 | 426.6653 | 539.0465 | 343.6395 | 644.8487
915.4063 | 825.4063 | 398.5907 | 470.1036 | 427.5052 | 538.9001 | 343.7463 | 643.236
916.4077 | 826.4077 | 397.9741 | 470.8696 | 428.2978 | 539.0845 | 343.4876 | 642.1659
917.4092 | 827.4092 | 397.358 | 471.3704 | 429.0838 | 538.9038 | 343.3062 | 643.3156
918.4106 | 828.4106 | 396.7996 | 471.9334 | 429.874 | 538.5337 | 342.8158 | 646.5262
919.402 | 829.402 | 396.3561 | 473.1106 | 430.5879 | 538.2109 | 342.5494 | 642.8699
920.4035 | 830.4035 | 395.929 | 474.1364 | 431.4783 | 537.7751 | 342.3496 | 645.2685
921.4049 | 831.4049 | 395.5091 | 474.9553 | 432.1615 | 537.3923 | 341.7053 | 644.3152
922.4064 | 832.4064 | 395.0748 | 475.7259 | 432.8587 | 536.7796 | 340.3719 | 647.4336
923.4078 | 833.4078 | 394.7012 | 476.3234 | 433.4317 | 536.7204 | 339.9654 | 645.9516
924.4092 | 834.4092 | 394.2212 | 477.3029 | 434.159 | 536.7736 | 339.324 | 645.4828
925.4107 | 835.4107 | 393.7414 | 478.0898 | 434.8381 | 537.1242 | 339.4035 | 646.3749
926.4121 | 836.4121 | 393.2078 | 478.6301 | 435.5879 | 537.2709 | 339.3385 | 646.7666
927.4035 | 837.4035 | 392.6456 | 479.0607 | 436.3486 | 537.083 | 339.0264 | 646.6232
928.405 | 838.405 | 392.111 | 479.9794 | 437.0855 | 536.7589 | 339.0064 | 646.2778
929.4064 | 839.4064 | 391.6593 | 480.6508 | 437.8893 | 536.5374 | 338.0226 | 646.3011
930.4079 | 840.4079 | 391.293 | 481.1852 | 438.7058 | 536.5522 | 338.0081 | 645.7415
931.4093 | 841.4093 | 390.9353 | 481.7216 | 439.5332 | 536.398 | 337.4305 | 643.4007
932.4107 | 842.4107 | 390.5306 | 482.4442 | 440.4373 | 536.1626 | 336.685 | 645.0084
933.4022 | 843.4022 | 390.1411 | 482.7061 | 441.3767 | 535.9325 | 336.2392 | 644.4782
934.4036 | 844.4036 | 389.8165 | 483.434 | 442.264 | 535.5757 | 335.5554 | 641.406
935.405 | 845.405 | 389.4608 | 484.1585 | 443.2569 | 535.4948 | 334.4627 | 641.1149
936.4065 | 846.4065 | 389.0636 | 484.9039 | 444.5458 | 535.3588 | 334.1643 | 639.8407
937.4079 | 847.4079 | 388.631 | 484.9868 | 445.7146 | 535.3884 | 333.5922 | 638.7332
938.4094 | 848.4094 | 388.2081 | 485.9735 | 446.8959 | 535.8649 | 334.216 | 637.4802
939.4108 | 849.4108 | 387.8329 | 486.1527 | 448.0881 | 536.3273 | 334.3193 | 636.7429
940.4022 | 850.4022 | 387.4572 | 487.0833 | 449.1868 | 536.4745 | 334.1254 | 639.3712
941.4037 | 851.4037 | 386.9776 | 487.6437 | 450.6878 | 537.2147 | 333.5902 | 638.1349
942.4051 | 852.4051 | 386.5198 | 488.1205 | 452.3647 | 537.3316 | 334.5147 | 636.1652
943.4066 | 853.4066 | 386.0809 | 488.4241 | 454.3236 | 537.337 | 335.1155 | 637.503
944.408 | 854.408 | 385.7048 | 488.8948 | 456.4605 | 537.3863 | 335.1366 | 635.8984
945.4094 | 855.4094 | 385.2504 | 489.5302 | 458.5061 | 537.4717 | 334.6207 | 635.6311
946.4109 | 856.4109 | 384.8078 | 489.8911 | 460.4728 | 537.4428 | 334.6776 | 635.453
947.4123 | 857.4123 | 384.3658 | 490.4103 | 462.1493 | 537.3619 | 334.016 | 636.2652
948.4138 | 858.4138 | 383.944 | 490.5276 | 464.0364 | 537.3541 | 333.5641 | 635.7934
949.4052 | 859.4052 | 383.5962 | 491.1335 | 465.8879 | 537.5063 | 333.1419 | 636.3837
950.4066 | 860.4066 | 383.2856 | 491.5476 | 467.8278 | 537.7389 | 333.7024 | 638.1483
951.4081 | 861.4081 | 382.917 | 491.7719 | 470.0975 | 538.0623 | 334.0383 | 638.3481
952.4095 | 862.4095 | 382.6321 | 492.1861 | 472.4654 | 538.3155 | 333.913 | 639.5941
953.4109 | 863.4109 | 382.3061 | 492.2284 | 474.4038 | 538.3888 | 333.9353 | 641.2154
954.4124 | 864.4124 | 381.961 | 491.6395 | 476.0771 | 538.5651 | 333.4703 | 640.2473
955.4038 | 865.4038 | 381.6167 | 492.0999 | 477.4025 | 538.6025 | 333.5531 | 639.7167
956.4052 | 866.4052 | 381.1737 | 492.3609 | 478.6169 | 538.6795 | 333.5075 | 638.6
957.4067 | 867.4067 | 380.769 | 492.5615 | 479.8081 | 538.6402 | 333.4184 | 640.4631
958.4081 | 868.4081 | 380.3522 | 493.3065 | 480.6623 | 538.6205 | 333.0815 | 642.3188
959.4096 | 869.4096 | 379.9691 | 492.9063 | 481.5383 | 538.5646 | 332.4957 | 641.6315
960.411 | 870.411 | 379.5977 | 493.3671 | 482.2562 | 538.3706 | 332.585 | 642.4919
961.4024 | 871.4024 | 379.2834 | 493.4104 | 482.7237 | 538.3351 | 332.374 | 643.1436
962.4039 | 872.4039 | 378.903 | 493.8902 | 483.1079 | 538.0468 | 332.607 | 642.9404
963.4053 | 873.4053 | 378.531 | 494.6167 | 483.6586 | 538.1884 | 332.1509 | 644.8604
964.4067 | 874.4067 | 378.271 | 495.5041 | 484.2421 | 538.4337 | 331.9342 | 644.1175
965.4082 | 875.4082 | 377.8775 | 495.9102 | 485.3782 | 538.5839 | 332.3338 | 644.0951
966.4096 | 876.4096 | 377.5502 | 496.3539 | 486.0878 | 537.9817 | 332.0008 | 645.709
967.4111 | 877.4111 | 377.176 | 496.8533 | 486.977 | 535.7746 | 332.2856 | 649.374
968.4025 | 878.4025 | 376.9272 | 497.2326 | 487.7781 | 535.1363 | 331.5827 | 646.98
969.4039 | 879.4039 | 376.6712 | 497.5233 | 488.3415 | 534.9794 | 332.021 | 650.4536
970.4054 | 880.4054 | 376.3158 | 497.3395 | 488.9105 | 534.7483 | 332.4666 | 647.2381
971.4068 | 881.4068 | 375.9612 | 497.4043 | 489.1805 | 534.0541 | 332.0827 | 651.522
972.4083 | 882.4083 | 375.6837 | 497.0643 | 488.9003 | 533.8538 | 331.3234 | 647.2059
973.4097 | 883.4097 | 375.5172 | 496.6385 | 488.7227 | 533.7115 | 331.8289 | 647.3741
974.4111 | 884.4111 | 375.2649 | 496.3458 | 488.3842 | 532.7424 | 332.0177 | 647.7716
975.4126 | 885.4126 | 375.0781 | 496.728 | 488.8202 | 530.3977 | 332.0708 | 649.7778
976.404 | 886.404 | 374.8052 | 497.1162 | 489.2566 | 528.3537 | 332.1754 | 649.3786
977.4054 | 887.4054 | 374.4555 | 497.3551 | 489.9052 | 527.4584 | 332.4738 | 652.9669
978.4069 | 888.4069 | 374.1875 | 497.9327 | 490.2098 | 527.0397 | 332.208 | 657.7355
979.4083 | 889.4083 | 373.9155 | 498.4357 | 490.4412 | 526.882 | 332.4817 | 659.6243
980.4098 | 890.4098 | 373.6804 | 498.9016 | 490.7153 | 526.5435 | 332.7773 | 658.2941
981.4112 | 891.4112 | 373.3281 | 499.508 | 490.7522 | 526.007 | 332.3731 | 652.8896
982.4026 | 892.4026 | 373.0322 | 499.8718 | 491.126 | 525.6779 | 332.1589 | 651.806
983.4041 | 893.4041 | 372.6718 | 500.0446 | 491.3552 | 524.9193 | 331.9223 | 655.6277
984.4055 | 894.4055 | 372.4565 | 500.4673 | 491.4828 | 524.3732 | 331.3411 | 657.6422
985.4069 | 895.4069 | 372.2313 | 500.8104 | 492.029 | 524.634 | 331.7639 | 659.8317
986.4084 | 896.4084 | 372.0366 | 501.0023 | 492.6658 | 525.0645 | 331.4078 | 659.4273
987.4098 | 897.4098 | 371.6978 | 501.3106 | 493.6111 | 525.1264 | 331.525 | 659.2452
988.4113 | 898.4113 | 371.3975 | 501.5983 | 494.1217 | 525.4834 | 330.9649 | 655.0018
989.4127 | 899.4127 | 371.1198 | 501.7636 | 494.8272 | 526.0806 | 330.1027 | 653.9794
990.4041 | 900.4041 | 370.9221 | 501.9406 | 495.5232 | 526.6895 | 330.9511 | 655.122
991.4056 | 901.4056 | 370.75 | 502.3394 | 496.2346 | 527.4899 | 331.409 | 657.0546
992.407 | 902.407 | 370.5119 | 502.6515 | 496.8171 | 528.1456 | 330.938 | 659.6021
993.4085 | 903.4085 | 370.2087 | 502.9196 | 497.3118 | 528.8733 | 330.9399 | 663.1442
994.4099 | 904.4099 | 369.9857 | 503.332 | 497.8293 | 529.595 | 332.0978 | 662.3899
995.4113 | 905.4113 | 369.7127 | 503.8402 | 498.3145 | 530.3327 | 333.3786 | 661.7848
996.4128 | 906.4128 | 369.5494 | 504.3802 | 498.7225 | 531.2003 | 333.8725 | 657.2342
997.4042 | 907.4042 | 369.3132 | 504.9237 | 499.1055 | 531.9888 | 333.8665 | 649.8668
998.4056 | 908.4056 | 369.0708 | 505.3325 | 499.5558 | 532.7966 | 334.5766 | 650.7022
999.4071 | 909.4071 | 368.8127 | 505.822 | 500.0033 | 533.5355 | 335.0893 | 649.076
1000.4085 | 910.4085 | 368.6313 | 506.2143 | 500.3873 | 534.0844 | 335.6954 | 647.5606
1001.41 | 911.41 | 368.3169 | 506.7078 | 500.934 | 534.3449 | 335.4797 | 649.6444
1002.4114 | 912.4114 | 367.9817 | 507.1743 | 501.4824 | 534.5134 | 335.6861 | 649.1343
1003.4028 | 913.4028 | 367.6614 | 507.628 | 502.0589 | 534.7572 | 336.1713 | 657.5059
1004.4043 | 914.4043 | 367.3717 | 508.1842 | 502.5544 | 535.0677 | 336.895 | 654.8558
1005.4057 | 915.4057 | 367.1209 | 508.862 | 503.0557 | 535.1758 | 336.3786 | 654.7876
1006.4071 | 916.4071 | 366.9292 | 509.418 | 503.6228 | 535.1289 | 337.4897 | 653.4271
1007.4086 | 917.4086 | 366.69 | 510.0925 | 504.1916 | 535.2007 | 337.7752 | 652.7287
1008.41 | 918.41 | 366.3932 | 510.824 | 504.7691 | 535.2727 | 337.3503 | 656.0442
1009.4115 | 919.4115 | 366.1685 | 511.5091 | 505.3332 | 535.4672 | 337.4072 | 655.5394
1010.4029 | 920.4029 | 365.9552 | 512.2729 | 505.9697 | 535.6476 | 337.8271 | 654.5237
1011.4043 | 921.4043 | 365.7162 | 513.0167 | 506.541 | 535.884 | 337.7985 | 653.7957
1012.4058 | 922.4058 | 365.3985 | 513.7881 | 507.1256 | 536.1219 | 338.0483 | 653.9173
1013.4072 | 923.4072 | 365.1756 | 514.6292 | 507.6919 | 536.3727 | 338.7588 | 649.7911
1014.4086 | 924.4086 | 364.9912 | 515.4239 | 508.3589 | 536.6282 | 338.2542 | 648.7979
1015.4101 | 925.4101 | 364.7545 | 516.2703 | 508.9398 | 536.9173 | 339.0647 | 647.467
1016.4115 | 926.4115 | 364.5663 | 517.1744 | 509.6368 | 537.2627 | 339.3461 | 648.2486
1017.403 | 927.403 | 364.3653 | 518.1148 | 510.261 | 537.6771 | 339.7061 | 649.2428
1018.4044 | 928.4044 | 364.2012 | 518.9907 | 510.977 | 538.0989 | 339.6165 | 645.4601
1019.4058 | 929.4058 | 363.9448 | 519.9642 | 511.6986 | 538.5106 | 339.9582 | 646.0829
1020.4073 | 930.4073 | 363.6139 | 520.9073 | 512.3721 | 538.9425 | 340.3651 | 645.2259
1021.4087 | 931.4087 | 363.3688 | 521.9008 | 513.0503 | 539.2519 | 341.2031 | 644.4488
1022.4102 | 932.4102 | 363.1546 | 522.8018 | 513.7216 | 539.6369 | 340.9704 | 645.2769
1023.4116 | 933.4116 | 362.9279 | 523.6983 | 514.4572 | 540.0248 | 341.0602 | 644.6624
1024.403 | 934.403 | 362.6938 | 524.5938 | 515.1293 | 540.4281 | 341.2272 | 646.2125
1025.4045 | 935.4045 | 362.488 | 525.4033 | 515.8128 | 540.8133 | 341.5775 | 646.6357
1026.4059 | 936.4059 | 362.2334 | 526.2247 | 516.5257 | 541.1303 | 342.2435 | 645.0158
1027.4073 | 937.4073 | 361.9109 | 527.0598 | 517.2385 | 541.4887 | 341.8675 | 643.0803
1028.4088 | 938.4088 | 361.6437 | 527.8344 | 517.9957 | 541.8467 | 341.2942 | 644.5551
1029.4102 | 939.4102 | 361.3141 | 528.6423 | 518.689 | 542.1116 | 341.9887 | 645.0117
1030.4117 | 940.4117 | 360.9714 | 529.3709 | 519.3823 | 542.3881 | 342.1008 | 642.1325
1031.4031 | 941.4031 | 360.6304 | 530.0246 | 520.0454 | 542.5909 | 341.8045 | 639.5849
1032.4045 | 942.4045 | 360.3575 | 530.7088 | 520.7103 | 542.777 | 341.1368 | 639.5246
1033.406 | 943.406 | 360.1811 | 531.4027 | 521.352 | 542.8716 | 341.0494 | 642.5892
1034.4074 | 944.4074 | 359.8222 | 532.1008 | 521.9401 | 543.0113 | 341.6555 | 640.6007
1035.4088 | 945.4088 | 359.4427 | 532.8005 | 522.5269 | 543.1784 | 341.5727 | 638.9697
1036.4103 | 946.4103 | 359.1507 | 533.4364 | 523.0823 | 543.3041 | 341.305 | 638.6618
1037.4117 | 947.4117 | 358.7944 | 534.0822 | 523.6315 | 543.4369 | 340.717 | 636.9681
1038.4132 | 948.4132 | 358.4648 | 534.7353 | 524.15 | 543.4979 | 341.0312 | 634.7149
1039.4046 | 949.4046 | 358.0523 | 535.3943 | 524.7012 | 543.5527 | 340.3156 | 632.9662
1040.406 | 950.406 | 357.7079 | 536.0781 | 525.1669 | 543.5136 | 339.7648 | 631.8801
1041.4075 | 951.4075 | 357.2994 | 536.777 | 525.6726 | 543.4702 | 340.0919 | 630.8789
1042.4089 | 952.4089 | 356.933 | 537.4168 | 526.1382 | 543.4791 | 339.5125 | 630.0306
1043.4104 | 953.4104 | 356.6548 | 538.035 | 526.5735 | 543.4087 | 339.4958 | 630.87
1044.4118 | 954.4118 | 356.3712 | 538.6293 | 527.0282 | 543.2693 | 338.7705 | 632.2651
1045.4032 | 955.4032 | 356.0513 | 539.2712 | 527.4661 | 543.1379 | 338.9365 | 632.3651
1046.4047 | 956.4047 | 355.8072 | 539.9137 | 527.8761 | 542.8341 | 338.9533 | 631.4826
1047.4061 | 957.4061 | 355.6268 | 540.5309 | 528.2396 | 542.5286 | 338.7351 | 631.0374
1048.4075 | 958.4075 | 355.3402 | 541.1899 | 528.6795 | 542.2478 | 338.0361 | 631.9336
1049.409 | 959.409 | 354.921 | 541.7552 | 529.1138 | 541.9481 | 338.0418 | 631.1753
1050.4104 | 960.4104 | 354.5448 | 542.3045 | 529.498 | 541.6719 | 337.7118 | 629.3314
1051.4119 | 961.4119 | 354.1092 | 542.8009 | 529.8071 | 541.4484 | 337.412 | 627.7736
1052.4033 | 962.4033 | 353.7281 | 543.2551 | 530.1353 | 541.3283 | 337.137 | 626.585
1053.4047 | 963.4047 | 353.3871 | 543.7092 | 530.4669 | 541.2672 | 338.0379 | 628.0954
1054.4062 | 964.4062 | 353.124 | 544.118 | 530.7144 | 541.3876 | 337.375 | 628.552
1055.4076 | 965.4076 | 352.8172 | 544.4983 | 530.9385 | 541.9794 | 336.8827 | 627.7723
1056.409 | 966.409 | 352.5225 | 544.8474 | 531.1173 | 542.3479 | 336.6442 | 626.3759
1057.4105 | 967.4105 | 352.2376 | 545.1606 | 531.2675 | 542.6655 | 335.9498 | 624.3841
1058.4119 | 968.4119 | 351.8616 | 545.5467 | 531.4304 | 543.583 | 335.9155 | 625.2892
1059.4033 | 969.4033 | 351.4745 | 545.8904 | 531.5456 | 544.3837 | 335.1972 | 625.7937
1060.4048 | 970.4048 | 351.1844 | 546.2435 | 531.6542 | 545.0048 | 334.5677 | 625.2753
1061.4062 | 971.4062 | 350.8935 | 546.5653 | 531.7272 | 545.6376 | 334.2889 | 626.595
1062.4077 | 972.4077 | 350.5137 | 546.85 | 531.7354 | 546.4552 | 333.3556 | 625.3456
1063.4091 | 973.4091 | 350.1133 | 547.1072 | 531.8093 | 547.0767 | 331.7398 | 623.8962
1064.4105 | 974.4105 | 349.7304 | 547.3707 | 531.823 | 548.7907 | 330.5718 | 623.1575
1065.412 | 975.412 | 349.4529 | 547.6036 | 531.8186 | 551.2928 | 329.4474 | 622.7245
1066.4034 | 976.4034 | 349.1758 | 547.8846 | 531.8335 | 553.7947 | 328.8302 | 621.5734
1067.4049 | 977.4049 | 348.8322 | 548.2069 | 531.8276 | 555.1784 | 328.0747 | 619.6622
1068.4063 | 978.4063 | 348.4842 | 548.5348 | 531.8698 | 555.8096 | 327.4014 | 618.7178
1069.4077 | 979.4077 | 348.1283 | 548.8073 | 531.9444 | 556.646 | 326.8406 | 617.6716
1070.4092 | 980.4092 | 347.7778 | 549.1008 | 532.0125 | 557.94 | 325.5172 | 616.1733
1071.4106 | 981.4106 | 347.3936 | 549.4358 | 532.0764 | 559.7585 | 324.737 | 615.1995
1072.402 | 982.402 | 347.0651 | 549.7943 | 532.1543 | 561.0587 | 323.9117 | 614.8092
1073.4135 | 983.4135 | 346.8079 | 550.1289 | 532.2111 | 561.3335 | 322.4234 | 614.7608
1074.4049 | 984.4049 | 346.6411 | 550.5564 | 532.37 | 560.6445 | 321.6567 | 621.0287
1075.4064 | 985.4064 | 346.4205 | 550.9368 | 532.5168 | 559.9866 | 320.9902 | 625.0114
1076.4078 | 986.4078 | 346.1315 | 551.2798 | 532.6225 | 560.3102 | 320.0922 | 623.3024
1077.4092 | 987.4092 | 345.7802 | 551.6185 | 532.7573 | 560.7632 | 318.9523 | 622.0926
1078.4107 | 988.4107 | 345.4362 | 551.9861 | 532.8683 | 561.9035 | 318.0412 | 618.3485
1079.4121 | 989.4121 | 345.0978 | 552.3314 | 533.0283 | 563.1519 | 317.5486 | 615.4581
1080.4136 | 990.4136 | 344.8385 | 552.7052 | 533.2728 | 564.6957 | 317.4344 | 613.308
1081.405 | 991.405 | 344.5685 | 553.0934 | 533.4991 | 565.7725 | 317.0872 | 611.7398
1082.4064 | 992.4064 | 344.2083 | 553.5089 | 533.7375 | 567.1286 | 316.3556 | 610.3743
1083.4079 | 993.4079 | 343.7579 | 553.9851 | 533.9692 | 567.8624 | 315.6424 | 609.7293
1084.4093 | 994.4093 | 343.3196 | 554.5628 | 534.2059 | 567.9783 | 314.382 | 610.1927
1085.4107 | 995.4107 | 342.8548 | 555.1289 | 534.4066 | 567.661 | 313.3078 | 612.4801
1086.4122 | 996.4122 | 342.4168 | 555.6516 | 534.5528 | 567.7065 | 311.7269 | 614.931
1087.4036 | 997.4036 | 342.0771 | 556.219 | 534.7482 | 567.8587 | 311.3061 | 613.8197
1088.405 | 998.405 | 341.7101 | 556.7257 | 534.9743 | 568.6064 | 310.3255 | 612.6647
1089.4065 | 999.4065 | 341.2916 | 557.1809 | 535.3161 | 569.2049 | 309.1168 | 611.2841
1090.4079 | 1000.4079 | 340.8861 | 557.6177 | 535.5443 | 570.9076 | 307.7981 | 609.8022
1091.4094 | 1001.4094 | 340.5211 | 558.0833 | 535.7843 | 571.6947 | 306.3009 | 608.1621
1092.4108 | 1002.4108 | 340.1578 | 558.5557 | 536.0578 | 572.1599 | 304.9811 | 607.2118
1093.4022 | 1003.4022 | 339.786 | 558.9766 | 536.3177 | 572.5783 | 304.4128 | 607.4257
1094.4137 | 1004.4137 | 339.5205 | 559.4054 | 536.5303 | 572.6168 | 303.7844 | 608.4617
1095.4051 | 1005.4051 | 339.1538 | 559.789 | 536.6898 | 572.6017 | 302.8369 | 608.7192
1096.4066 | 1006.4066 | 338.804 | 560.1536 | 536.8942 | 572.4768 | 302.2418 | 607.4381
1097.408 | 1007.408 | 338.4025 | 560.5442 | 537.1347 | 572.3951 | 301.6993 | 605.8111
1098.4094 | 1008.4094 | 338.0541 | 560.9721 | 537.4127 | 573.009 | 301.2179 | 604.5052
1099.4109 | 1009.4109 | 337.7374 | 561.3845 | 537.6073 | 574.1038 | 300.4308 | 603.0688
1100.4023 | 1010.4023 | 337.485 | 561.8561 | 537.9462 | 574.5957 | 299.1055 | 601.2037
1101.4037 | 1011.4037 | 337.1511 | 562.3613 | 538.2172 | 574.7159 | 297.9979 | 599.8609
1102.4052 | 1012.4052 | 336.7711 | 562.8571 | 538.5358 | 575.3897 | 297.8851 | 598.6894
1103.4066 | 1013.4066 | 336.4931 | 563.3433 | 538.8242 | 575.5788 | 296.6177 | 597.6883
1104.4081 | 1014.4081 | 336.2157 | 563.8331 | 539.0992 | 576.3304 | 295.7781 | 596.8994
1105.4095 | 1015.4095 | 335.8151 | 564.3104 | 539.4765 | 576.6513 | 295.7594 | 595.7582
1106.4109 | 1016.4109 | 335.4313 | 564.7706 | 539.8508 | 577.0095 | 294.9796 | 595.3517
1107.4124 | 1017.4124 | 335.1511 | 565.2366 | 540.258 | 577.6358 | 294.7627 | 594.4712
1108.4038 | 1018.4038 | 334.8053 | 565.6871 | 540.6553 | 578.3912 | 294.0477 | 594.304
1109.4052 | 1019.4052 | 334.4279 | 566.1166 | 541.0701 | 578.5494 | 293.6029 | 594.7421
1110.4067 | 1020.4067 | 334.1287 | 566.6055 | 541.4331 | 579.6103 | 293.3514 | 594.8685
1111.4081 | 1021.4081 | 333.7211 | 567.0767 | 541.7641 | 580.6612 | 292.8919 | 594.4743
1112.4096 | 1022.4096 | 333.3579 | 567.539 | 542.1788 | 581.5589 | 292.4872 | 593.6976
1113.411 | 1023.411 | 333.035 | 568.031 | 542.4838 | 581.8026 | 292.6124 | 593.8593
1114.4024 | 1024.4024 | 332.7408 | 568.5251 | 542.8437 | 582.8709 | 291.8606 | 593.7903
1115.4039 | 1025.4039 | 332.3861 | 569.0411 | 543.2051 | 583.1715 | 290.9248 | 593.9927
1116.4053 | 1026.4053 | 331.9956 | 569.5686 | 543.5397 | 583.61 | 290.7724 | 594.3149
1117.4068 | 1027.4068 | 331.603 | 570.0778 | 543.9032 | 583.6163 | 289.8241 | 594.5281
1118.4082 | 1028.4082 | 331.2808 | 570.5982 | 544.2198 | 583.211 | 289.1274 | 595.4265
1119.4096 | 1029.4096 | 331.0678 | 571.1164 | 544.52 | 582.8584 | 287.7957 | 596.9758
1120.4111 | 1030.4111 | 330.8992 | 571.6162 | 544.84 | 582.6604 | 287.13 | 598.2052
1121.4125 | 1031.4125 | 330.6369 | 572.1228 | 545.2316 | 582.9193 | 286.0599 | 599.3402
1122.414 | 1032.414 | 330.3238 | 572.6257 | 545.5625 | 582.8941 | 285.5025 | 599.6994
1123.4054 | 1033.4054 | 330.0055 | 573.1587 | 545.9715 | 582.0554 | 285.0625 | 603.4292
1124.4068 | 1034.4068 | 329.6931 | 573.743 | 546.3046 | 581.8282 | 284.0612 | 602.9015
1125.4083 | 1035.4083 | 329.2842 | 574.3386 | 546.7573 | 581.1653 | 283.4188 | 603.8262
1126.4097 | 1036.4097 | 328.8703 | 574.9798 | 547.1271 | 581.1976 | 283.6243 | 603.3057
1127.4111 | 1037.4111 | 328.5517 | 575.7004 | 547.4933 | 581.6187 | 282.8655 | 602.4427
1128.4126 | 1038.4126 | 328.2661 | 576.3718 | 547.9017 | 581.9729 | 282.2799 | 601.2429
1129.404 | 1039.404 | 327.9279 | 576.9377 | 548.2705 | 581.9734 | 281.9478 | 600.4509
1130.4255 | 1040.4255 | 327.5525 | 577.5699 | 548.6682 | 582.6673 | 281.3841 | 600.1315
1131.4069 | 1041.4069 | 327.1209 | 578.1604 | 549.0067 | 583.8736 | 281.5091 | 598.9447
1132.4083 | 1042.4083 | 326.689 | 578.7268 | 549.4451 | 584.9024 | 280.1991 | 597.1947
1133.4098 | 1043.4098 | 326.2601 | 579.283 | 549.8875 | 585.9144 | 279.6064 | 596.3416
1134.4112 | 1044.4112 | 325.8663 | 579.8432 | 550.302 | 586.4403 | 279.3784 | 595.6452
1135.4026 | 1045.4026 | 325.5207 | 580.4112 | 550.8288 | 586.7742 | 279.0179 | 594.7651
1136.4041 | 1046.4041 | 325.197 | 581.0247 | 551.2164 | 587.5533 | 278.0895 | 594.3201
1137.4055 | 1047.4055 | 324.9185 | 581.5761 | 551.6788 | 588.2243 | 277.9458 | 594.4972
1138.4069 | 1048.4069 | 324.5685 | 582.125 | 552.0922 | 588.6849 | 277.9111 | 594.8167
1139.4084 | 1049.4084 | 324.2286 | 582.628 | 552.5375 | 589.9413 | 277.7525 | 595.1891
1140.4098 | 1050.4098 | 323.8981 | 583.1148 | 552.9656 | 590.6941 | 277.5146 | 595.4607
1141.4113 | 1051.4113 | 323.5334 | 583.5561 | 553.4162 | 591.4378 | 276.4703 | 597.7114
1142.4027 | 1052.4027 | 323.1667 | 583.9937 | 553.8273 | 591.9963 | 275.6131 | 601.6427
1143.4041 | 1053.4041 | 322.8166 | 584.5778 | 554.2952 | 591.888 | 275.4066 | 608.4994
1144.4056 | 1054.4056 | 322.4824 | 585.1675 | 554.7211 | 591.6685 | 275.5167 | 614.9023
1145.407 | 1055.407 | 322.2455 | 585.6772 | 555.1549 | 591.078 | 274.5816 | 617.8527
1146.4085 | 1056.4085 | 321.9392 | 586.216 | 555.5833 | 591.0016 | 274.9038 | 617.8772
1147.4099 | 1057.4099 | 321.619 | 586.7522 | 555.9678 | 591.0327 | 274.6531 | 617.1653
1148.4113 | 1058.4113 | 321.2556 | 587.3006 | 556.3802 | 591.1874 | 273.9474 | 614.7715
1149.4128 | 1059.4128 | 320.9278 | 587.7854 | 556.8073 | 591.7333 | 274.1499 | 615.3381
1150.4042 | 1060.4042 | 320.5736 | 588.2108 | 557.3206 | 592.6794 | 274.1036 | 619.7965
1151.4056 | 1061.4056 | 320.1787 | 588.7784 | 557.7939 | 593.6978 | 273.6717 | 624.4985
1152.4071 | 1062.4071 | 319.8406 | 589.341 | 558.2082 | 594.6653 | 272.8859 | 621.5756
1153.4085 | 1063.4085 | 319.5891 | 589.8386 | 558.6296 | 595.4505 | 271.905 | 624.9806
1154.41 | 1064.41 | 319.2203 | 590.4551 | 559.0664 | 596.0949 | 271.8342 | 627.8795
1155.4114 | 1065.4114 | 318.8159 | 591.0609 | 559.5398 | 596.1757 | 271.4216 | 632.6221
1156.4028 | 1066.4028 | 318.464 | 591.524 | 559.9725 | 595.9278 | 270.722 | 636.9387
1157.4043 | 1067.4043 | 318.1615 | 592.0184 | 560.4341 | 595.7919 | 270.4196 | 635.5234
1158.4057 | 1068.4057 | 317.8193 | 592.526 | 560.9113 | 595.3072 | 269.4553 | 640.7853
1159.4071 | 1069.4071 | 317.5717 | 592.9877 | 561.3587 | 595.0563 | 269.1689 | 646.6398
1160.4086 | 1070.4086 | 317.3463 | 593.4921 | 561.7713 | 594.9459 | 269.0623 | 647.9153
1161.41 | 1071.41 | 317.017 | 594.1043 | 562.2018 | 595.0594 | 268.1191 | 648.8326
1162.4115 | 1072.4115 | 316.7195 | 594.7521 | 562.67 | 595.0483 | 267.0288 | 650.016
1163.4129 | 1073.4129 | 316.3748 | 595.2293 | 563.1303 | 595.0961 | 266.5941 | 650.7647
1164.4043 | 1074.4043 | 316.0438 | 595.6994 | 563.5993 | 595.3604 | 266.3465 | 653.1988
1165.4058 | 1075.4058 | 315.7224 | 596.1894 | 564.0359 | 595.4577 | 266.5922 | 653.8419
1166.4072 | 1076.4072 | 315.3928 | 596.7399 | 564.5077 | 595.7007 | 266.4239 | 652.9227
1167.4087 | 1077.4087 | 315.0662 | 597.1825 | 564.9413 | 595.5646 | 265.6488 | 651.9214
1168.4101 | 1078.4101 | 314.6418 | 597.5908 | 565.4067 | 595.2036 | 265.4848 | 639.8099
1169.4115 | 1079.4115 | 314.3071 | 598.1348 | 565.8717 | 594.8983 | 265.1186 | 624.0609
1170.413 | 1080.413 | 313.8908 | 598.8144 | 566.2786 | 595.7539 | 264.8181 | 615.3811
1171.4044 | 1081.4044 | 313.4986 | 599.6423 | 566.7666 | 596.3124 | 263.5016 | 614.7949
1172.4058 | 1082.4058 | 313.2227 | 600.3609 | 567.2325 | 595.9779 | 262.8169 | 605.7564
1173.4073 | 1083.4073 | 312.949 | 600.9892 | 567.7203 | 596.2711 | 262.1496 | 602.4055
1174.4087 | 1084.4087 | 312.6591 | 601.563 | 568.2204 | 596.7481 | 261.7472 | 595.0238
1175.4102 | 1085.4102 | 312.3034 | 602.1631 | 568.737 | 597.4917 | 260.6428 | 589.1663
1176.4116 | 1086.4116 | 311.8519 | 602.6586 | 569.2573 | 597.7389 | 260.2706 | 583.5341
1177.403 | 1087.403 | 311.3868 | 603.1013 | 569.7412 | 598.9169 | 259.8857 | 578.8705
1178.4045 | 1088.4045 | 311.1057 | 603.567 | 570.2239 | 599.5401 | 259.7969 | 573.9461
1179.4059 | 1089.4059 | 310.8238 | 604.0262 | 570.6967 | 600.1754 | 259.6995 | 569.1808
1180.4073 | 1090.4073 | 310.5547 | 604.4733 | 571.1637 | 600.5313 | 259.2798 | 564.5827
1181.4088 | 1091.4088 | 310.2586 | 605.0018 | 571.6002 | 600.0057 | 258.8076 | 560.4346
1182.4102 | 1092.4102 | 309.9689 | 605.5308 | 572.0891 | 600.1037 | 258.9879 | 557.3031
1183.4016 | 1093.4016 | 309.7051 | 605.9732 | 572.5428 | 601.0148 | 258.9499 | 553.876
1184.4031 | 1094.4031 | 309.4171 | 606.4554 | 573.0126 | 601.531 | 258.43 | 551.0795
1185.4045 | 1095.4045 | 309.137 | 606.8989 | 573.5094 | 602.1702 | 258.0625 | 547.8832
1186.406 | 1096.406 | 308.8507 | 607.3417 | 574.0398 | 602.6216 | 257.3832 | 544.816
1187.4074 | 1097.4074 | 308.5637 | 607.9328 | 574.5073 | 602.8352 | 257.461 | 541.8512
1188.4088 | 1098.4088 | 308.2663 | 608.4027 | 574.9786 | 602.5868 | 256.7803 | 539.5069
1189.4103 | 1099.4103 | 307.9788 | 608.9948 | 575.4258 | 602.6341 | 256.5296 | 537.2637
1190.4117 | 1100.4117 | 307.6537 | 609.6388 | 575.8905 | 602.8502 | 255.8487 | 534.7633
1191.4032 | 1101.4032 | 307.2913 | 610.2923 | 576.3698 | 603.3078 | 255.6459 | 532.4754
1192.4046 | 1102.4046 | 307 | 610.8109 | 576.8228 | 603.6679 | 254.4495 | 529.9016
1193.406 | 1103.406 | 306.7178 | 611.38 | 577.2902 | 603.5928 | 254.4311 | 527.6999
1194.4075 | 1104.4075 | 306.4721 | 611.7901 | 577.745 | 603.9986 | 253.6789 | 525.6629
1195.4089 | 1105.4089 | 306.1673 | 612.2309 | 578.2323 | 604.5285 | 253.2555 | 523.4415
1196.4104 | 1106.4104 | 305.8641 | 612.7039 | 578.7045 | 604.6693 | 253.6186 | 520.7955
1197.4118 | 1107.4118 | 305.5607 | 613.2268 | 579.1847 | 604.6853 | 253.2781 | 518.5596
1198.4032 | 1108.4032 | 305.3524 | 613.6957 | 579.6859 | 605.3762 | 253.0504 | 516.6947
1199.4047 | 1109.4047 | 305.1482 | 614.3633 | 580.1668 | 605.0476 | 253.4017 | 514.6421
1200.4061 | 1110.4061 | 304.8115 | 614.9545 | 580.6386 | 604.5313 | 253.2695 | 513.0381
1201.4075 | 1111.4075 | 304.463 | 615.5495 | 581.1016 | 604.6413 | 252.9404 | 511.1113
1202.409 | 1112.409 | 304.1632 | 616.2139 | 581.5538 | 605.0255 | 251.9111 | 509.1686
1203.4104 | 1113.4104 | 303.8217 | 616.663 | 582.0235 | 605.4451 | 251.814 | 507.1189
1204.4119 | 1114.4119 | 303.526 | 617.1476 | 582.4705 | 606.3958 | 251.0882 | 505.0847
1205.4133 | 1115.4133 | 303.2085 | 617.585 | 582.9116 | 606.4999 | 251.2325 | 503.35
1206.4047 | 1116.4047 | 302.8424 | 617.9749 | 583.3763 | 606.3646 | 250.5881 | 501.8554
1207.4062 | 1117.4062 | 302.5362 | 618.3342 | 583.8788 | 606.0989 | 250.7542 | 500.5955
1208.4076 | 1118.4076 | 302.1997 | 618.609 | 584.3383 | 605.336 | 250.5316 | 499.0086
1209.409 | 1119.409 | 301.8904 | 619.0225 | 584.7849 | 605.3502 | 249.9156 | 497.4183
1210.4105 | 1120.4105 | 301.5685 | 619.422 | 585.2783 | 605.7089 | 249.5617 | 495.4813
1211.4119 | 1121.4119 | 301.2359 | 619.882 | 585.7509 | 605.3151 | 249.6199 | 494.164
1212.4134 | 1122.4134 | 301.0037 | 620.4812 | 586.1998 | 605.0771 | 249.6651 | 493.0163
1213.4048 | 1123.4048 | 300.7122 | 620.9929 | 586.6589 | 605.2673 | 249.8742 | 491.2733
1214.4062 | 1124.4062 | 300.4152 | 621.4693 | 587.107 | 605.853 | 249.3738 | 490.229
1215.4077 | 1125.4077 | 300.0414 | 622.1089 | 587.5619 | 606.3963 | 248.8037 | 489.1607
1216.4091 | 1126.4091 | 299.6828 | 622.8208 | 588.0181 | 606.949 | 248.3068 | 487.5597
1217.4106 | 1127.4106 | 299.3537 | 623.3879 | 588.4875 | 607.3198 | 248.0469 | 485.8953
1218.412 | 1128.412 | 299.0916 | 623.9093 | 588.922 | 607.5617 | 247.8522 | 484.5844
1219.4034 | 1129.4034 | 298.7129 | 624.3143 | 589.345 | 607.6494 | 247.537 | 483.0874
1220.4049 | 1130.4049 | 298.3739 | 624.5976 | 589.7818 | 608.0642 | 247.0122 | 481.8973
1221.4063 | 1131.4063 | 298.1136 | 624.761 | 590.1919 | 608.2032 | 246.6894 | 480.5897
1222.4077 | 1132.4077 | 297.7816 | 625.0718 | 590.5835 | 608.3976 | 246.1221 | 479.5689
1223.4092 | 1133.4092 | 297.3957 | 625.437 | 591.0183 | 608.7839 | 245.5873 | 479.0059
1224.4106 | 1134.4106 | 297.0139 | 625.8136 | 591.4238 | 609.3984 | 244.8469 | 478.5224
1225.402 | 1135.402 | 296.727 | 626.0877 | 591.881 | 609.3256 | 244.9404 | 477.2313
1226.4135 | 1136.4135 | 296.4823 | 626.4512 | 592.3463 | 610.1265 | 244.4157 | 476.3105
1227.4049 | 1137.4049 | 296.2335 | 626.9163 | 592.7669 | 610.9846 | 243.9017 | 475.514
1228.4064 | 1138.4064 | 295.9819 | 627.42 | 593.1904 | 611.1066 | 244.0901 | 474.7959
1229.4078 | 1139.4078 | 295.6447 | 627.9568 | 593.5938 | 610.8131 | 244.0293 | 473.6428
1230.4092 | 1140.4092 | 295.3345 | 628.3771 | 594.0236 | 610.6683 | 244.2566 | 472.8186
1231.4107 | 1141.4107 | 295.0675 | 628.872 | 594.4586 | 610.8326 | 243.4738 | 471.9172
1232.4121 | 1142.4121 | 294.7629 | 629.2536 | 594.8568 | 611.0525 | 242.6882 | 471.7507
1233.4035 | 1143.4035 | 294.4056 | 629.5564 | 595.2809 | 611.1074 | 242.1843 | 470.3959
1234.405 | 1144.405 | 294.1083 | 629.9386 | 595.6719 | 610.4098 | 242.0789 | 469.2461
1235.4064 | 1145.4064 | 293.8227 | 630.2469 | 596.1078 | 610.3232 | 241.5544 | 468.5747
1236.4079 | 1146.4079 | 293.4976 | 630.5401 | 596.518 | 610.6126 | 241.4903 | 468.1813
1237.4093 | 1147.4093 | 293.1799 | 630.829 | 596.9168 | 610.6916 | 241.2664 | 467.8413
1238.4107 | 1148.4107 | 292.8801 | 631.2024 | 597.3484 | 610.7011 | 241.2357 | 467.0238
1239.4122 | 1149.4122 | 292.5945 | 631.5663 | 597.761 | 610.9885 | 240.5261 | 466.3746
1240.4036 | 1150.4036 | 292.3314 | 631.8929 | 598.1829 | 610.5093 | 240.3552 | 465.3514
1241.4051 | 1151.4051 | 292.0514 | 632.1597 | 598.6199 | 610.2381 | 240.0482 | 465.0569
1242.4065 | 1152.4065 | 291.7843 | 632.4821 | 599.0533 | 610.2786 | 239.9965 | 463.9632
1243.4079 | 1153.4079 | 291.4738 | 632.7854 | 599.4619 | 610.468 | 239.311 | 463.1941
1244.4094 | 1154.4094 | 291.2246 | 633.0892 | 599.8931 | 610.8772 | 239.2956 | 462.2028
1245.4108 | 1155.4108 | 290.8828 | 633.4103 | 600.3171 | 611.2635 | 238.9992 | 461.7628
1246.4123 | 1156.4123 | 290.5818 | 633.6974 | 600.7418 | 611.6865 | 238.4085 | 461.37
1247.4037 | 1157.4037 | 290.3449 | 634.0064 | 601.2267 | 612.1863 | 238.0779 | 461.0917
1248.4051 | 1158.4051 | 290.0796 | 634.2422 | 601.6766 | 612.4247 | 237.8799 | 460.2559
1249.4066 | 1159.4066 | 289.8059 | 634.4535 | 602.0759 | 612.4295 | 237.6377 | 459.4025
1250.408 | 1160.408 | 289.5433 | 634.767 | 602.5054 | 612.4597 | 237.037 | 459.1428
1251.4094 | 1161.4094 | 289.2569 | 635.1763 | 602.876 | 612.4875 | 236.4475 | 458.482
1252.4109 | 1162.4109 | 289.0038 | 635.5301 | 603.2559 | 612.3213 | 236.299 | 457.8938
1253.4123 | 1163.4123 | 288.7503 | 635.899 | 603.6504 | 612.6075 | 236.1553 | 458.0618
1254.4037 | 1164.4037 | 288.4156 | 636.2436 | 604.1262 | 612.8238 | 236.1801 | 457.3487
1255.4052 | 1165.4052 | 288.0084 | 636.5942 | 604.5388 | 612.8533 | 236.071 | 456.6941
1256.4066 | 1166.4066 | 287.6321 | 636.9237 | 604.9585 | 613.2395 | 236.0014 | 456.7613
1257.4081 | 1167.4081 | 287.262 | 637.197 | 605.3767 | 613.4242 | 235.3258 | 456.9002
1258.4095 | 1168.4095 | 286.9386 | 637.4441 | 605.769 | 613.5583 | 235.204 | 456.2811
1259.4109 | 1169.4109 | 286.5437 | 637.714 | 606.1515 | 613.7763 | 235.1014 | 456.3584
1260.4124 | 1170.4124 | 286.1746 | 637.9602 | 606.5376 | 613.5539 | 234.5297 | 456.203
1261.4038 | 1171.4038 | 285.8292 | 638.2654 | 606.9554 | 613.7373 | 234.4942 | 455.1787
1262.4052 | 1172.4052 | 285.5164 | 638.5306 | 607.3332 | 614.0922 | 234.2825 | 454.9485
1263.4067 | 1173.4067 | 285.2228 | 638.8889 | 607.6867 | 614.2179 | 234.3116 | 454.4023
1264.4081 | 1174.4081 | 284.9246 | 639.2741 | 608.0694 | 614.3724 | 234.2214 | 453.4146
1265.4096 | 1175.4096 | 284.658 | 639.6366 | 608.46 | 614.2282 | 233.654 | 453.4613
1266.411 | 1176.411 | 284.3798 | 639.9988 | 608.8556 | 614.1177 | 233.0126 | 453.2264
1267.4024 | 1177.4024 | 284.0926 | 640.3318 | 609.2516 | 614.0857 | 232.966 | 452.4454
1268.4039 | 1178.4039 | 283.8524 | 640.7593 | 609.6376 | 614.0567 | 233.1549 | 452.5891
1269.4053 | 1179.4053 | 283.6295 | 641.1459 | 610.004 | 614.6244 | 232.9583 | 452.4381
1270.4068 | 1180.4068 | 283.3763 | 641.5557 | 610.3938 | 615.004 | 232.5142 | 451.7167
1271.4082 | 1181.4082 | 283.1359 | 642.0016 | 610.7247 | 615.3962 | 232.1233 | 451.3117
1272.4096 | 1182.4096 | 282.9434 | 642.4077 | 611.0868 | 615.5026 | 232.0088 | 450.6462
1273.4111 | 1183.4111 | 282.7115 | 642.7901 | 611.3939 | 615.6629 | 231.4822 | 449.9858
1274.4025 | 1184.4025 | 282.341 | 643.0556 | 611.7491 | 615.8116 | 231.7731 | 449.4392
1275.4039 | 1185.4039 | 282.0226 | 643.3458 | 612.1175 | 615.7392 | 231.847 | 448.9986
1276.4054 | 1186.4054 | 281.7542 | 643.5202 | 612.4365 | 615.8589 | 231.3097 | 448.8916
1277.4068 | 1187.4068 | 281.5618 | 643.7849 | 612.7375 | 616.1897 | 231.0775 | 448.3747
1278.4083 | 1188.4083 | 281.2568 | 644.1213 | 613.1059 | 616.2852 | 230.4006 | 447.5448
1279.4097 | 1189.4097 | 280.9311 | 644.4034 | 613.4351 | 615.9264 | 230.1231 | 447.1965
1280.4111 | 1190.4111 | 280.6457 | 644.6062 | 613.7738 | 615.9538 | 229.7866 | 447.0016
1281.4126 | 1191.4126 | 280.2963 | 644.8083 | 614.1154 | 615.9191 | 229.7595 | 446.8332
1282.404 | 1192.404 | 279.9455 | 645.1964 | 614.4316 | 615.7817 | 229.6715 | 446.4606
1283.4054 | 1193.4054 | 279.6093 | 645.5569 | 614.7825 | 615.7799 | 229.4662 | 445.9166
1284.4069 | 1194.4069 | 279.2478 | 645.89 | 615.1264 | 615.566 | 229.1288 | 445.3399
1285.4083 | 1195.4083 | 278.9133 | 646.2254 | 615.4626 | 615.3512 | 228.0273 | 445.1825
1286.4098 | 1196.4098 | 278.6073 | 646.4102 | 615.7622 | 615.465 | 227.7841 | 445.3418
1287.4112 | 1197.4112 | 278.2965 | 646.5748 | 616.0729 | 615.8516 | 226.994 | 444.8543
1288.4026 | 1198.4026 | 277.9718 | 646.7575 | 616.396 | 616.1466 | 226.4142 | 444.1533
1289.4041 | 1199.4041 | 277.67 | 646.9056 | 616.6738 | 616.1107 | 225.9103 | 443.6497
1290.4055 | 1200.4055 | 277.4183 | 647.1275 | 616.9774 | 616.1213 | 225.5294 | 443.4731
1291.407 | 1201.407 | 277.0988 | 647.3612 | 617.3036 | 616.0394 | 225.3278 | 443.0981
1292.4084 | 1202.4084 | 276.7425 | 647.5242 | 617.6189 | 615.9798 | 225.2494 | 442.4696
1293.4098 | 1203.4098 | 276.4646 | 647.7388 | 617.9019 | 615.4249 | 224.987 | 441.9997
1294.4113 | 1204.4113 | 276.1881 | 647.9981 | 618.1903 | 615.3553 | 224.5631 | 441.9323
1295.4127 | 1205.4127 | 275.8861 | 648.2483 | 618.4634 | 615.4171 | 224.2841 | 442.1514
1296.4041 | 1206.4041 | 275.5854 | 648.4053 | 618.7293 | 615.6395 | 224.3587 | 442.1009
1297.4056 | 1207.4056 | 275.3545 | 648.5858 | 619.0477 | 615.701 | 224.306 | 441.9271
1298.407 | 1208.407 | 275.142 | 648.8239 | 619.3227 | 615.6786 | 223.7141 | 441.3392
1299.4085 | 1209.4085 | 274.8196 | 649.0356 | 619.6049 | 615.2855 | 223.7341 | 441.1283
1300.4099 | 1210.4099 | 274.5031 | 649.253 | 619.923 | 615.0757 | 223.4621 | 440.7066
1301.4113 | 1211.4113 | 274.2163 | 649.6509 | 620.2394 | 614.6642 | 222.9156 | 440.3002
1302.4128 | 1212.4128 | 273.9893 | 649.9597 | 620.5192 | 614.0027 | 222.6636 | 440.1048
1303.4042 | 1213.4042 | 273.7829 | 650.2274 | 620.876 | 613.6864 | 222.4491 | 439.7219
1304.4056 | 1214.4056 | 273.5851 | 650.5798 | 621.1445 | 613.6185 | 222.1459 | 439.4719
1305.4071 | 1215.4071 | 273.2402 | 650.9038 | 621.4641 | 614.0195 | 221.4486 | 439.0599
1306.4085 | 1216.4085 | 272.8882 | 651.0926 | 621.7487 | 614.3562 | 221.0436 | 438.7858
1307.41 | 1217.41 | 272.5973 | 651.289 | 621.9994 | 614.6747 | 220.8082 | 438.3563
1308.4014 | 1218.4014 | 272.2914 | 651.5003 | 622.3075 | 614.7865 | 220.578 | 438.4663
1309.4028 | 1219.4028 | 271.9613 | 651.7051 | 622.6102 | 615.2354 | 220 | 437.7138
1310.4043 | 1220.4043 | 271.6332 | 651.8693 | 622.8885 | 615.6904 | 219.5812 | 437.5238
1311.4057 | 1221.4057 | 271.29 | 652.056 | 623.1341 | 615.7929 | 218.9124 | 437.0574
1312.4071 | 1222.4071 | 270.9916 | 652.1459 | 623.3676 | 615.7314 | 218.461 | 436.8282
1313.4086 | 1223.4086 | 270.6933 | 652.1756 | 623.6614 | 615.8742 | 217.4897 | 436.5966
1314.41 | 1224.41 | 270.3343 | 652.4019 | 623.9091 | 615.9278 | 217.704 | 437.1154
1315.4115 | 1225.4115 | 270.0513 | 652.5663 | 624.1802 | 615.9921 | 217.1987 | 436.8395
1316.4029 | 1226.4029 | 269.7741 | 652.7263 | 624.4786 | 616.1369 | 217.3318 | 436.1225
1317.4043 | 1227.4043 | 269.5152 | 652.9008 | 624.8092 | 616.222 | 216.7482 | 435.8352
1318.4058 | 1228.4058 | 269.2835 | 653.1521 | 625.0954 | 616.6027 | 216.339 | 435.5801
1319.4072 | 1229.4072 | 269.0497 | 653.3033 | 625.3679 | 616.7648 | 216.2619 | 435.2239
1320.4087 | 1230.4087 | 268.7821 | 653.4432 | 625.6124 | 616.856 | 215.8765 | 435.129
1321.4101 | 1231.4101 | 268.4993 | 653.638 | 625.8872 | 617.0831 | 215.4618 | 434.5866
1322.4115 | 1232.4115 | 268.1557 | 653.8458 | 626.174 | 617.1429 | 214.8257 | 434.2647
1323.413 | 1233.413 | 267.9204 | 653.9807 | 626.4207 | 617.0924 | 214.5629 | 434.0469
1324.4044 | 1234.4044 | 267.725 | 654.1958 | 626.7248 | 617.2604 | 214.3463 | 433.9015
1325.4058 | 1235.4058 | 267.5187 | 654.4119 | 627.0042 | 617.1584 | 214.4708 | 433.4613
1326.4073 | 1236.4073 | 267.2888 | 654.6756 | 627.2399 | 617.2138 | 214.3516 | 432.9795
1327.4087 | 1237.4087 | 267.0167 | 655.0056 | 627.4673 | 617.3026 | 214.0821 | 432.4882
1328.4102 | 1238.4102 | 266.8 | 655.3558 | 627.6905 | 617.2705 | 214.1209 | 432.0607
1329.4116 | 1239.4116 | 266.6804 | 655.5586 | 627.9327 | 616.9233 | 213.6336 | 431.4897
1330.403 | 1240.403 | 266.4817 | 655.8444 | 628.1741 | 616.3589 | 213.5326 | 430.6261
1331.4045 | 1241.4045 | 266.2349 | 656.0501 | 628.4849 | 615.8688 | 212.9541 | 430.0963
1332.4059 | 1242.4059 | 265.9551 | 656.2364 | 628.7861 | 615.5782 | 212.5298 | 429.8533
1333.4073 | 1243.4073 | 265.6848 | 656.3857 | 629.0345 | 614.9863 | 211.9568 | 429.6449
1334.4088 | 1244.4088 | 265.4189 | 656.7342 | 629.3178 | 614.2259 | 211.6408 | 429.4502
1335.4102 | 1245.4102 | 265.2059 | 656.9261 | 629.5988 | 614.0481 | 211.7228 | 429.5073
1336.4117 | 1246.4117 | 265.0415 | 657.0556 | 629.8311 | 613.6343 | 211.2565 | 429.1872
1337.4131 | 1247.4131 | 264.8565 | 657.177 | 630.0541 | 613.1106 | 211.2436 | 428.6096
1338.4045 | 1248.4045 | 264.6258 | 657.3751 | 630.2856 | 613.2103 | 211.1145 | 428.5926
1339.406 | 1249.406 | 264.3404 | 657.5425 | 630.5093 | 613.4964 | 210.8866 | 428.2053
1340.4074 | 1250.4074 | 264.1479 | 657.7504 | 630.7309 | 613.3001 | 210.6899 | 427.7241
1341.4089 | 1251.4089 | 263.9332 | 657.9883 | 631.0066 | 612.7293 | 210.6396 | 427.528
1342.4103 | 1252.4103 | 263.6674 | 658.1856 | 631.2819 | 612.2314 | 210.6646 | 427.4156
1343.4117 | 1253.4117 | 263.3348 | 658.371 | 631.5293 | 611.6994 | 210.0368 | 427.7143
1344.4132 | 1254.4132 | 263.0073 | 658.5618 | 631.7587 | 611.8495 | 209.3477 | 428.1781
1345.4046 | 1255.4046 | 262.7319 | 658.7001 | 631.9728 | 612.3878 | 208.7115 | 427.9989
1346.406 | 1256.406 | 262.4033 | 658.8284 | 632.1899 | 613.0583 | 208.5665 | 427.7224
1347.4075 | 1257.4075 | 262.0415 | 658.9646 | 632.4201 | 613.5941 | 208.3059 | 427.6752
1348.4089 | 1258.4089 | 261.722 | 659.1276 | 632.657 | 614.1839 | 208.3427 | 427.8155
1349.4104 | 1259.4104 | 261.3977 | 659.328 | 632.9121 | 614.4103 | 207.5962 | 427.9772
1350.4118 | 1260.4118 | 261.1351 | 659.5044 | 633.1411 | 614.6195 | 207.5135 | 427.3679
1351.4032 | 1261.4032 | 260.8376 | 659.6685 | 633.3526 | 614.9828 | 207.2437 | 427.5594
1352.4047 | 1262.4047 | 260.5274 | 659.8647 | 633.5506 | 615.325 | 207.2697 | 427.3507
1353.4061 | 1263.4061 | 260.2553 | 660.1529 | 633.7368 | 615.4869 | 206.9875 | 426.6473
1354.4075 | 1264.4075 | 259.9264 | 660.4052 | 633.9357 | 615.5553 | 206.696 | 426.2025
1355.409 | 1265.409 | 259.5724 | 660.5356 | 634.114 | 615.7446 | 206.3957 | 425.6143
1356.4104 | 1266.4104 | 259.2286 | 660.7519 | 634.2417 | 615.6878 | 206.2702 | 424.775
1357.4018 | 1267.4018 | 258.9365 | 661.0098 | 634.4669 | 615.9938 | 205.7026 | 424.7164
1358.4033 | 1268.4033 | 258.6724 | 661.2814 | 634.607 | 616.4468 | 205.5173 | 424.6642
1359.4047 | 1269.4047 | 258.391 | 661.5429 | 634.76 | 616.6028 | 204.8532 | 423.961
1360.4062 | 1270.4062 | 258.1746 | 661.7159 | 634.9065 | 616.7 | 204.9362 | 423.4316
1361.4076 | 1271.4076 | 257.8963 | 661.86 | 635.0746 | 616.6863 | 204.8562 | 422.7542
1362.409 | 1272.409 | 257.5763 | 661.9558 | 635.2629 | 616.8656 | 204.3802 | 422.148
1363.4105 | 1273.4105 | 257.2536 | 662.1907 | 635.379 | 617.0839 | 204.5268 | 421.8779
1364.4119 | 1274.4119 | 256.9284 | 662.4306 | 635.5011 | 617.3478 | 203.8319 | 421.7313
1365.4034 | 1275.4034 | 256.6721 | 662.7234 | 635.6227 | 617.5662 | 203.5871 | 421.1099
1366.4048 | 1276.4048 | 256.4004 | 663.0076 | 635.7486 | 617.4463 | 203.3707 | 420.4501
1367.4062 | 1277.4062 | 256.1015 | 663.2215 | 635.9134 | 617.5024 | 202.9455 | 420.1564
1368.4077 | 1278.4077 | 255.8093 | 663.3796 | 636.0558 | 617.4865 | 203.1752 | 419.9034
1369.4091 | 1279.4091 | 255.598 | 663.621 | 636.2194 | 617.4486 | 202.5676 | 419.5021
1370.4106 | 1280.4106 | 255.3306 | 663.8687 | 636.3641 | 617.281 | 202.3922 | 419.1937
1371.412 | 1281.412 | 255.0774 | 664.061 | 636.4943 | 616.8113 | 201.8299 | 419.1387
1372.4034 | 1282.4034 | 254.7769 | 664.3937 | 636.6249 | 616.4346 | 201.5184 | 418.7001
1373.4049 | 1283.4049 | 254.4698 | 664.555 | 636.7491 | 616.2497 | 200.9065 | 418.3398
1374.4063 | 1284.4063 | 254.2317 | 664.7245 | 636.8956 | 616.2208 | 200.9801 | 418.19
1375.4077 | 1285.4077 | 253.9918 | 665.1202 | 637.0105 | 616.4326 | 201.0738 | 418.3171
1376.4092 | 1286.4092 | 253.7528 | 665.3986 | 637.1519 | 616.4928 | 200.7431 | 418.2217
1377.4106 | 1287.4106 | 253.4367 | 665.5283 | 637.3522 | 616.1955 | 200.6394 | 417.8648
1378.4121 | 1288.4121 | 253.0855 | 665.6304 | 637.4497 | 615.7245 | 199.8506 | 417.5828
1379.4135 | 1289.4135 | 252.8101 | 665.7228 | 637.6091 | 615.2556 | 199.2117 | 417.1374
1380.4049 | 1290.4049 | 252.5184 | 665.702 | 637.7182 | 615.0696 | 199.2365 | 416.9851
1381.4064 | 1291.4064 | 252.293 | 665.7182 | 637.8794 | 615.2099 | 199.0649 | 416.4589
1382.4078 | 1292.4078 | 252.159 | 665.9248 | 638.0781 | 615.1722 | 198.8353 | 416.2041
1383.4092 | 1293.4092 | 251.8915 | 666.3064 | 638.2498 | 614.7603 | 198.5481 | 416.1066
1384.4107 | 1294.4107 | 251.6922 | 666.5042 | 638.362 | 614.6654 | 198.1617 | 415.8242
1385.4121 | 1295.4121 | 251.4457 | 666.7491 | 638.4849 | 614.4348 | 198.1616 | 415.2157
1386.4136 | 1296.4136 | 251.17 | 667.0683 | 638.5543 | 614.1778 | 197.7538 | 414.736
1387.405 | 1297.405 | 250.8483 | 667.5287 | 638.6089 | 613.8767 | 197.5983 | 414.3456
1388.4064 | 1298.4064 | 250.6173 | 667.9134 | 638.6934 | 613.8193 | 197.2775 | 414.1896
1389.4079 | 1299.4079 | 250.4123 | 668.1658 | 638.7941 | 613.4001 | 196.8954 | 413.7359
1390.4093 | 1300.4093 | 250.2165 | 668.506 | 638.9523 | 612.9704 | 196.632 | 413.8044
1391.4108 | 1301.4108 | 250.0111 | 668.811 | 639.1136 | 612.7221 | 196.1655 | 413.1865
1392.4122 | 1302.4122 | 249.7755 | 668.9683 | 639.2624 | 612.5847 | 196.3188 | 412.6948
1393.4036 | 1303.4036 | 249.4768 | 669.2895 | 639.4103 | 612.673 | 196.0802 | 412.2535
1394.4051 | 1304.4051 | 249.2466 | 669.454 | 639.5869 | 612.6491 | 195.9151 | 411.7437
1395.4065 | 1305.4065 | 249.0576 | 669.6038 | 639.6862 | 612.7143 | 195.7076 | 411.9132
1396.4079 | 1306.4079 | 248.9051 | 669.8908 | 639.7679 | 613.0072 | 195.3397 | 411.7097
1397.4094 | 1307.4094 | 248.779 | 670.1257 | 639.8762 | 612.9987 | 194.9161 | 411.2257
1398.4108 | 1308.4108 | 248.5729 | 670.269 | 639.9816 | 612.9275 | 194.4632 | 410.7827
1399.4123 | 1309.4123 | 248.3085 | 670.2911 | 640.0307 | 612.7874 | 194.0878 | 410.5353
1400.4037 | 1310.4037 | 248.0899 | 670.7322 | 640.105 | 612.2979 | 194.1949 | 409.9677
1401.4051 | 1311.4051 | 247.8977 | 670.9422 | 640.209 | 612.0973 | 193.944 | 409.5506
1402.4066 | 1312.4066 | 247.6434 | 671.2877 | 640.3437 | 612.1712 | 193.3511 | 409.0054
1403.408 | 1313.408 | 247.4662 | 671.6418 | 640.4268 | 612.1215 | 192.7982 | 408.5644
1404.4094 | 1314.4094 | 247.2377 | 671.8281 | 640.5253 | 612.0373 | 192.6247 | 407.6489
1405.4109 | 1315.4109 | 246.9575 | 671.9954 | 640.6923 | 612.022 | 192.6027 | 407.3584
1406.4123 | 1316.4123 | 246.7079 | 672.2392 | 640.8588 | 611.862 | 191.8082 | 407.3517
1407.4138 | 1317.4138 | 246.5148 | 672.5101 | 640.9949 | 611.6748 | 191.543 | 407.2361
1408.4052 | 1318.4052 | 246.3119 | 672.8401 | 641.131 | 611.3287 | 191.4601 | 407.12
1409.4066 | 1319.4066 | 246.0068 | 673.0985 | 641.1744 | 611.4873 | 191.5017 | 406.7133
1410.4081 | 1320.4081 | 245.7083 | 673.1148 | 641.2125 | 611.3173 | 191.249 | 406.8226
1411.4095 | 1321.4095 | 245.432 | 673.1441 | 641.3256 | 611.1746 | 190.7738 | 406.8934
1412.4109 | 1322.4109 | 245.1795 | 673.2455 | 641.465 | 610.8102 | 190.8247 | 406.444
1413.4124 | 1323.4124 | 244.9021 | 673.2915 | 641.6053 | 610.6804 | 190.2959 | 406.1052
1414.4038 | 1324.4038 | 244.5799 | 673.0379 | 641.6777 | 610.3801 | 189.7647 | 405.6155
1415.4053 | 1325.4053 | 244.3187 | 672.8187 | 641.766 | 610.0416 | 189.3314 | 405.3912
1416.4067 | 1326.4067 | 244.0775 | 672.7657 | 641.8224 | 609.855 | 188.9343 | 404.955
1417.4081 | 1327.4081 | 243.8892 | 672.8282 | 641.9343 | 609.7991 | 188.6918 | 404.8432
1418.4096 | 1328.4096 | 243.6954 | 672.9608 | 642.0955 | 609.8638 | 188.2074 | 404.4883
1419.411 | 1329.411 | 243.4273 | 672.9997 | 642.2492 | 609.8348 | 188.1827 | 404.3069
1420.4125 | 1330.4125 | 243.1079 | 673.0835 | 642.352 | 609.7328 | 187.8237 | 403.9266
1421.4039 | 1331.4039 | 242.9029 | 673.1862 | 642.4438 | 609.3554 | 187.4638 | 403.7069
1422.4053 | 1332.4053 | 242.7744 | 673.2829 | 642.4938 | 609.5487 | 187.1043 | 403.3715
1423.4068 | 1333.4068 | 242.4982 | 673.5173 | 642.5684 | 609.5347 | 186.7393 | 403.8597
1424.4082 | 1334.4082 | 242.2367 | 673.6101 | 642.6747 | 609.3123 | 186.648 | 403.1326
1425.4096 | 1335.4096 | 241.9995 | 673.7788 | 642.8045 | 609.4 | 186.3137 | 402.9209
1426.4111 | 1336.4111 | 241.761 | 673.7665 | 642.8946 | 609.3651 | 186.3129 | 402.6952
1427.4125 | 1337.4125 | 241.4785 | 674.0534 | 642.9425 | 609.2848 | 186.2465 | 402.8857
1428.414 | 1338.414 | 241.1892 | 674.1475 | 643.0251 | 609.1277 | 185.9906 | 402.4936
1429.4054 | 1339.4054 | 240.9562 | 674.2891 | 643.1178 | 609.0554 | 185.9114 | 402.2655
1430.4068 | 1340.4068 | 240.7393 | 674.2981 | 643.2408 | 608.9947 | 185.6132 | 402.1989
1431.4083 | 1341.4083 | 240.4632 | 674.4054 | 643.3427 | 608.7604 | 185.1214 | 401.8033
1432.4097 | 1342.4097 | 240.2267 | 674.5217 | 643.4205 | 608.7133 | 185.2224 | 401.2903
1433.4111 | 1343.4111 | 239.9959 | 674.6558 | 643.4906 | 608.6192 | 185.0288 | 400.838
1434.4126 | 1344.4126 | 239.748 | 674.7835 | 643.5798 | 608.5438 | 184.451 | 400.2261
1435.404 | 1345.404 | 239.4506 | 674.8398 | 643.6608 | 608.5807 | 184.4702 | 400.0651
1436.4054 | 1346.4054 | 239.1516 | 674.8114 | 643.688 | 608.6431 | 184.0266 | 400.0393
1437.4069 | 1347.4069 | 238.878 | 674.658 | 643.7767 | 608.7632 | 183.6059 | 399.8872
1438.4083 | 1348.4083 | 238.6317 | 674.4154 | 643.8181 | 608.7404 | 183.1621 | 399.491
1439.4098 | 1349.4098 | 238.4174 | 674.4731 | 643.8787 | 608.7823 | 183.3455 | 399.078
1440.4112 | 1350.4112 | 238.1445 | 674.8904 | 643.9992 | 608.8648 | 183.3659 | 398.8744
1441.4026 | 1351.4026 | 237.7842 | 675.0001 | 644.091 | 608.8289 | 183.2738 | 398.7357
1442.4041 | 1352.4041 | 237.4388 | 674.9726 | 644.1575 | 608.77 | 182.8785 | 398.3953
1443.4055 | 1353.4055 | 237.1548 | 674.8235 | 644.2071 | 608.5444 | 182.5331 | 397.7811
1444.407 | 1354.407 | 236.9113 | 674.6814 | 644.2585 | 608.2006 | 182.0037 | 397.6794
1445.4084 | 1355.4084 | 236.6908 | 674.727 | 644.3204 | 607.4803 | 181.537 | 396.99
1446.4098 | 1356.4098 | 236.4796 | 674.6316 | 644.4344 | 606.945 | 181.1139 | 396.8806
1447.4113 | 1357.4113 | 236.2322 | 674.6697 | 644.4314 | 606.8168 | 181.144 | 396.8098
1448.4127 | 1358.4127 | 236.1046 | 674.7007 | 644.4094 | 606.7339 | 181.0842 | 396.4816
1449.4041 | 1359.4041 | 235.9754 | 674.8531 | 644.5029 | 606.9158 | 180.7999 | 396.2928
1450.4056 | 1360.4056 | 235.8397 | 675.0675 | 644.6225 | 606.941 | 180.562 | 396.0949
1451.407 | 1361.407 | 235.7191 | 675.4698 | 644.6536 | 606.6846 | 180.1723 | 395.7286
1452.4085 | 1362.4085 | 235.5094 | 675.894 | 644.7487 | 606.4405 | 180.2679 | 395.2192
1453.4099 | 1363.4099 | 235.2588 | 675.7923 | 644.7831 | 606.1836 | 180.3257 | 394.7851
1454.4113 | 1364.4113 | 235.0636 | 675.8043 | 644.839 | 605.9354 | 180.2777 | 394.8086
1455.4128 | 1365.4128 | 234.8066 | 675.7199 | 644.8992 | 605.7055 | 180.3216 | 394.389
1456.4042 | 1366.4042 | 234.6597 | 675.6132 | 645.0416 | 605.5333 | 180.3989 | 394.0736
1457.4056 | 1367.4056 | 234.5309 | 675.687 | 645.1477 | 605.553 | 180.3404 | 394.5495
1458.4071 | 1368.4071 | 234.3155 | 675.8874 | 645.1804 | 605.4991 | 180.3451 | 394.5529
1459.4085 | 1369.4085 | 234.1309 | 676.1566 | 645.227 | 605.4335 | 180.0377 | 393.8854
1460.41 | 1370.41 | 233.8843 | 676.0749 | 645.2744 | 605.2625 | 179.9 | 393.3832
1461.4014 | 1371.4014 | 233.6334 | 675.8178 | 645.2971 | 605.1993 | 179.8717 | 393.0949
1462.4028 | 1372.4028 | 233.3512 | 675.4505 | 645.2767 | 605.2342 | 179.4696 | 392.6533
1463.4043 | 1373.4043 | 233.1528 | 675.2216 | 645.2805 | 604.8731 | 179.4833 | 391.8996
1464.4057 | 1374.4057 | 232.9271 | 675.0275 | 645.3486 | 604.4953 | 178.8512 | 391.3821
1465.4072 | 1375.4072 | 232.6238 | 674.8502 | 645.4502 | 604.225 | 178.3559 | 390.976
1466.4086 | 1376.4086 | 232.3467 | 674.5173 | 645.5166 | 603.7985 | 178.0876 | 390.6707
1467.41 | 1377.41 | 232.1499 | 674.2279 | 645.5626 | 603.3275 | 177.6309 | 389.9594
1468.4115 | 1378.4115 | 231.9794 | 674.031 | 645.6433 | 602.8717 | 177.4353 | 390.0038
1469.4129 | 1379.4129 | 231.73 | 673.8917 | 645.7368 | 602.5163 | 177.3306 | 390.005
1470.4043 | 1380.4043 | 231.4692 | 673.6565 | 645.8094 | 602.3197 | 177.3422 | 389.9958
1471.4058 | 1381.4058 | 231.2187 | 673.383 | 645.8392 | 602.2601 | 177.2304 | 389.904
1472.4072 | 1382.4072 | 231.0079 | 673.0106 | 645.9064 | 601.8901 | 176.6898 | 389.8298
1473.4087 | 1383.4087 | 230.7944 | 672.7071 | 645.9264 | 601.4952 | 176.7825 | 389.7783
1474.4101 | 1384.4101 | 230.5129 | 672.3215 | 645.9617 | 601.2323 | 176.5271 | 389.6342
1475.4115 | 1385.4115 | 230.2341 | 672.1085 | 646.0481 | 600.8285 | 176.2744 | 389.3458
1476.413 | 1386.413 | 230.0028 | 671.9277 | 646.1627 | 600.5642 | 176.137 | 389.3388
1477.4044 | 1387.4044 | 229.7643 | 671.6676 | 646.2858 | 600.2775 | 175.9614 | 389.154
1478.4058 | 1388.4058 | 229.4914 | 671.2299 | 646.3024 | 600.0306 | 175.8876 | 389.3345
1479.4073 | 1389.4073 | 229.2555 | 670.9584 | 646.3453 | 599.8608 | 175.659 | 389.1066
1480.4087 | 1390.4087 | 229.0941 | 670.7688 | 646.3276 | 599.605 | 175.8648 | 389.0054
1481.4102 | 1391.4102 | 228.8896 | 670.5072 | 646.3093 | 599.3122 | 175.8576 | 388.3728
1482.4016 | 1392.4016 | 228.6542 | 670.277 | 646.3618 | 599.0376 | 176.0522 | 387.912
1483.403 | 1393.403 | 228.3718 | 669.9417 | 646.386 | 598.6492 | 176.1594 | 387.2901
1484.4045 | 1394.4045 | 228.0917 | 669.6114 | 646.4009 | 598.241 | 175.8045 | 387.0728
1485.4059 | 1395.4059 | 227.9293 | 669.3524 | 646.4466 | 597.9096 | 175.6547 | 386.7884
1486.4073 | 1396.4073 | 227.7756 | 669.0614 | 646.4897 | 597.479 | 175.4985 | 386.2169
1487.4088 | 1397.4088 | 227.6036 | 668.7796 | 646.5347 | 597.0254 | 175.2356 | 385.8363
1488.4102 | 1398.4102 | 227.4223 | 668.4375 | 646.6766 | 596.533 | 175.2336 | 385.9353
1489.4017 | 1399.4017 | 227.2149 | 668.0718 | 646.6834 | 596.0805 | 174.9696 | 385.7666
1490.4031 | 1400.4031 | 227.0166 | 667.759 | 646.6733 | 595.6004 | 174.5766 | 385.4222
1491.4446 | 1401.4446 | 226.8166 | 667.3029 | 646.6509 | 595.1071 | 174.3044 | 384.8482
1492.406 | 1402.406 | 226.5737 | 666.9537 | 646.646 | 594.6371 | 173.7519 | 384.7478
1493.4074 | 1403.4074 | 226.2928 | 666.517 | 646.6115 | 594.1968 | 173.4446 | 384.3807
1494.4089 | 1404.4089 | 225.9964 | 666.0559 | 646.6187 | 593.8093 | 173.4254 | 384.4404
1495.4103 | 1405.4103 | 225.7367 | 665.6135 | 646.6226 | 593.3281 | 173.0895 | 384.342
1496.4117 | 1406.4117 | 225.5526 | 665.1957 | 646.5857 | 592.904 | 173.0455 | 384.2071
1497.4132 | 1407.4132 | 225.2891 | 664.9271 | 646.6067 | 592.476 | 172.6487 | 384.0503
1498.4046 | 1408.4046 | 225.0605 | 664.5899 | 646.6167 | 592.0867 | 172.377 | 383.7101
1499.406 | 1409.406 | 224.8333 | 664.1965 | 646.5686 | 591.7018 | 172.2945 | 383.4426
1500.4075 | 1410.4075 | 224.6083 | 663.7933 | 646.543 | 591.3209 | 172.2248 | 383.2025
1501.4089 | 1411.4089 | 224.369 | 663.3477 | 646.5658 | 590.9161 | 172.1163 | 383.2571
1502.4104 | 1412.4104 | 224.191 | 662.849 | 646.5195 | 590.5498 | 171.6862 | 382.8332
1503.4018 | 1413.4018 | 223.9682 | 662.5583 | 646.5494 | 590.174 | 171.7151 | 382.8149
1504.4132 | 1414.4132 | 223.7241 | 662.0365 | 646.5193 | 589.8324 | 171.6188 | 382.3925
1505.4047 | 1415.4047 | 223.4814 | 661.4397 | 646.5779 | 589.4748 | 171.2916 | 382.439
1506.4061 | 1416.4061 | 223.244 | 660.8702 | 646.607 | 589.1151 | 171.0516 | 382.2515
1507.4075 | 1417.4075 | 223.0127 | 660.588 | 646.6155 | 588.806 | 170.9988 | 382.0226
1508.409 | 1418.409 | 222.7531 | 660.2082 | 646.6022 | 588.4319 | 170.8307 | 381.9618
1509.4104 | 1419.4104 | 222.5386 | 659.6715 | 646.6037 | 588.0643 | 170.7698 | 381.7958
1510.4119 | 1420.4119 | 222.2982 | 659.1479 | 646.5002 | 587.7381 | 170.1617 | 381.269
1511.4133 | 1421.4133 | 222.0594 | 658.6537 | 646.4425 | 587.4758 | 170.0919 | 380.5982
1512.4047 | 1422.4047 | 221.879 | 658.1353 | 646.4063 | 587.1818 | 170.021 | 380.5015
1513.4062 | 1423.4062 | 221.6969 | 657.6797 | 646.3173 | 586.9187 | 169.5702 | 380.1467
1514.4076 | 1424.4076 | 221.5167 | 657.0804 | 646.2624 | 586.6621 | 169.3483 | 380.0891
1515.4091 | 1425.4091 | 221.3166 | 656.5395 | 646.2105 | 586.366 | 169.4413 | 379.5609
1516.4105 | 1426.4105 | 221.1267 | 656.1433 | 646.2083 | 586.0215 | 168.9113 | 379.3988
1517.4119 | 1427.4119 | 220.8776 | 655.6176 | 646.2093 | 585.6964 | 168.8898 | 379.0594
1518.4034 | 1428.4034 | 220.6587 | 654.9228 | 646.2567 | 585.4237 | 168.7945 | 378.8682
1519.4048 | 1429.4048 | 220.4136 | 654.2969 | 646.3128 | 585.1685 | 168.4551 | 378.6714
1520.4062 | 1430.4062 | 220.156 | 653.712 | 646.4001 | 584.8929 | 168.2835 | 378.648
1521.4077 | 1431.4077 | 219.8953 | 653.1289 | 646.4815 | 584.5789 | 168.0831 | 378.2568
1522.4091 | 1432.4091 | 219.6512 | 652.5156 | 646.5581 | 584.2338 | 167.9291 | 378.5238
1523.4106 | 1433.4106 | 219.4537 | 651.9694 | 646.5565 | 583.9663 | 167.7602 | 378.6655

## C3-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 144.4066 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38903.5889 | 1 | 0 | 38903.5889 | 1 | 0 | -80.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5891 | 1 | 0 | 38903.5891 | 1 | 0 | -69.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5892 | 1 | 0 | 38903.5892 | 1 | 0 | -58.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5893 | 1 | 0 | 38903.5893 | 1 | 0 | -47.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5894 | 1 | 0 | 38903.5894 | 1 | 0 | -37.5 | 52.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5895 | 1 | 0 | 38903.5896 | 1 | 0 | -26.5 | 63.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5897 | 1 | 0 | 38903.5897 | 1 | 0 | -15.5 | 74.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5898 | 1 | 0 | 38903.5898 | 1 | 0 | -4.5 | 85.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5899 | 1 | 0 | 38903.5899 | 1 | 0 | 6.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.59 | 1 | 0 | 38903.5901 | 1 | 0 | 16.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5902 | 1 | 0 | 38903.5902 | 1 | 0 | 27.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5903 | 1 | 0 | 38903.5903 | 1 | 0 | 38.5 | 128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5904 | 1 | 0 | 38903.5904 | 1 | 0 | 49.5 | 139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5906 | 1 | 0 | 38903.5906 | 1 | 0 | 60.5 | 150.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5907 | 1 | 0 | 38903.5907 | 1 | 0 | 70.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5908 | 2 | 0 | 38903.5908 | 1 | 0 | 81.5 | 171.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118169 | 236438 | 118168.9988
38903.5909 | 1 | 0 | 38903.5909 | 1 | 0 | 92.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5911 | 1 | 0 | 38903.5911 | 1 | 0 | 103.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5912 | 1 | 1 | 38903.5912 | 1 | 0 | 114.5 | 204.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 559029278.44 | 236438 | 236238.0846
38903.5913 | 1 | 0 | 38903.5913 | 2 | 0 | 124.5 | 214.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 236438 | 118169 | 236437.9994
38903.5914 | 1 | 0 | 38903.5914 | 1 | 0 | 135.5 | 225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5916 | 1 | 0 | 38903.5916 | 1 | 0 | 146.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5917 | 1 | 0 | 38903.5917 | 1 | 0 | 157.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5918 | 1 | 0 | 38903.5918 | 1 | 0 | 168.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5919 | 1 | 0 | 38903.5919 | 1 | 0 | 178.5 | 268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.592 | 1 | 0 | 38903.5921 | 1 | 0 | 189.5 | 279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5922 | 1 | 0 | 38903.5922 | 1 | 0 | 200.5 | 290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5923 | 1 | 0 | 38903.5923 | 1 | 0 | 211.5 | 301.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5924 | 1 | 0 | 38903.5924 | 1 | 0 | 222.5 | 312.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5925 | 1 | 0 | 38903.5926 | 1 | 0 | 233 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5927 | 1 | 0 | 38903.5927 | 1 | 0 | 243.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5928 | 1 | 0 | 38903.5928 | 1 | 0 | 254.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5929 | 1 | 0 | 38903.5929 | 1 | 0 | 265.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5931 | 1 | 0 | 38903.5931 | 1 | 0 | 276.5 | 366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5932 | 1 | 0 | 38903.5932 | 1 | 0 | 286.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5933 | 1 | 0 | 38903.5933 | 1 | 0 | 297.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5934 | 1 | 0 | 38903.5934 | 1 | 0 | 308.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5936 | 1 | 0 | 38903.5936 | 1 | 0 | 319.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5937 | 1 | 0 | 38903.5937 | 1 | 0 | 330.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5938 | 1 | 0 | 38903.5938 | 1 | 0 | 340.5 | 430.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5939 | 1 | 0 | 38903.5939 | 1 | 0 | 351.5 | 441.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5941 | 1 | 0 | 38903.5941 | 1 | 0 | 362.5 | 452.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5942 | 1 | 0 | 38903.5942 | 1 | 0 | 373.5 | 463.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5943 | 1 | 0 | 38903.5943 | 1 | 0 | 384.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5944 | 1 | 0 | 38903.5944 | 1 | 0 | 394.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5945 | 1 | 0 | 38903.5946 | 1 | 0 | 405.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5947 | 1 | 0 | 38903.5947 | 1 | 0 | 416.5 | 506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5948 | 1 | 0 | 38903.5948 | 1 | 0 | 427.5 | 517.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5949 | 1 | 0 | 38903.5949 | 1 | 0 | 438.5 | 528.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.595 | 1 | 0 | 38903.5951 | 1 | 0 | 448.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5952 | 1 | 0 | 38903.5952 | 1 | 0 | 459.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5953 | 1 | 0 | 38903.5953 | 1 | 0 | 470.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5954 | 1 | 0 | 38903.5954 | 1 | 0 | 481.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5956 | 1 | 0 | 38903.5956 | 1 | 0 | 492.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5957 | 1 | 0 | 38903.5957 | 1 | 0 | 502.5 | 592.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5958 | 1 | 0 | 38903.5958 | 1 | 0 | 513.5 | 603.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5959 | 1 | 0 | 38903.5959 | 1 | 0 | 524.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5961 | 2 | 0 | 38903.5961 | 1 | 0 | 535.5 | 625.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118169 | 236438 | 118168.9988
38903.5962 | 1 | 0 | 38903.5962 | 1 | 0 | 546 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5963 | 1 | 0 | 38903.5963 | 1 | 0 | 556.5 | 646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5964 | 1 | 0 | 38903.5964 | 1 | 0 | 567.5 | 657.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5966 | 1 | 0 | 38903.5966 | 1 | 0 | 578.5 | 668.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5967 | 1 | 0 | 38903.5967 | 2 | 0 | 589.5 | 679.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 236438 | 118169 | 236437.9994
38903.5968 | 1 | 0 | 38903.5968 | 1 | 0 | 600.5 | 690.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5969 | 1 | 0 | 38903.5969 | 1 | 0 | 610.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.597 | 1 | 0 | 38903.5971 | 1 | 0 | 621.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5972 | 1 | 0 | 38903.5972 | 1 | 0 | 632.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5973 | 1 | 0 | 38903.5973 | 1 | 0 | 643.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5974 | 1 | 0 | 38903.5974 | 1 | 0 | 654 | 744 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5975 | 1 | 0 | 38903.5976 | 1 | 0 | 664.5 | 754.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5977 | 1 | 0 | 38903.5977 | 1 | 0 | 675.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5978 | 1 | 0 | 38903.5978 | 1 | 0 | 686.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5979 | 1 | 0 | 38903.5979 | 1 | 0 | 697.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5981 | 1 | 0 | 38903.5981 | 1 | 0 | 708.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5982 | 1 | 0 | 38903.5982 | 1 | 0 | 718.5 | 808.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5983 | 1 | 0 | 38903.5983 | 1 | 0 | 729.5 | 819.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5984 | 1 | 0 | 38903.5984 | 1 | 0 | 740.5 | 830.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5986 | 1 | 0 | 38903.5986 | 1 | 0 | 751.5 | 841.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5987 | 1 | 0 | 38903.5987 | 1 | 0 | 762 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236438 | 236438 | 236437.9994
38903.5988 | 1 | 0 | 38903.5988 | 20 | 0 | 772.5 | 862.5 | 0.06105 | 0 | 1.221 | 0 | 0.0006105 | 0 | 0.01221 | 0 | 0.0006105 | 0.01221 | 236438 | 11726.9 | 236437.9994
38903.5989 | 1 | 0 | 38903.5989 | 71 | 0 | 783.5 | 873.5 | 0.06105 | 0 | 4.3346 | 0 | 0.0006105 | 0 | 0.043346 | 0 | 0.0006105 | 0.043346 | 236438 | 3231.5211 | 236437.9994
38903.5991 | 1 | 0 | 38903.5991 | 164 | 0 | 794.5 | 884.5 | 0.06105 | 0 | 10.0122 | 0 | 0.0006105 | 0 | 0.10012 | 0 | 0.0006105 | 0.10012 | 236438 | 1342.3049 | 236437.9994
38903.5992 | 149 | 95 | 38903.5992 | 434 | 137 | 805.5 | 895.5 | 9.0965 | 5.7998 | 26.4957 | 8.3639 | 0.090965 | 0.057998 | 0.26496 | 0.083639 | 0.032967 | 0.18132 | 5609.4689 | 655.6882 | 1937.5351
38903.5993 | 194 | 130 | 38903.5993 | 430 | 167 | 816 | 906 | 11.8437 | 7.9365 | 26.2515 | 10.1954 | 0.11844 | 0.079365 | 0.26252 | 0.10195 | 0.039072 | 0.16056 | 4662.1323 | 746.0471 | 1384.6889
38903.5994 | 374 | 303 | 38903.5994 | 517 | 274 | 826.5 | 916.5 | 22.8327 | 18.4982 | 31.5629 | 16.7277 | 0.22833 | 0.18498 | 0.31563 | 0.16728 | 0.043346 | 0.14835 | 6245.5408 | 774.6355 | 493.5122
38903.5995 | 439 | 310 | 38903.5996 | 734 | 398 | 837.5 | 927.5 | 26.801 | 18.9255 | 44.8107 | 24.2979 | 0.26801 | 0.18926 | 0.44811 | 0.24298 | 0.078755 | 0.20513 | 2840.6567 | 506.6568 | 435.4643
38903.5997 | 503 | 361 | 38903.5997 | 671 | 330 | 848.5 | 938.5 | 30.7082 | 22.0391 | 40.9646 | 20.1465 | 0.30708 | 0.22039 | 0.40965 | 0.20147 | 0.086691 | 0.20818 | 2584.1912 | 516.2172 | 348.4032
38903.5998 | 1023 | 771 | 38903.5998 | 1229 | 950 | 859.5 | 949.5 | 62.4542 | 47.0696 | 75.0305 | 57.9976 | 0.62454 | 0.4707 | 0.75031 | 0.57998 | 0.15385 | 0.17033 | 1112.8509 | 586.8711 | 63.3196
38903.5999 | 1141 | 879 | 38903.5999 | 1048 | 768 | 870.5 | 960.5 | 69.6581 | 53.663 | 63.9805 | 46.8864 | 0.69658 | 0.53663 | 0.6398 | 0.46886 | 0.15995 | 0.17094 | 947.0544 | 662.3113 | 34.138
38903.6 | 1191 | 994 | 38903.6001 | 1164 | 879 | 880.5 | 970.5 | 72.7106 | 60.6838 | 71.0623 | 53.663 | 0.72711 | 0.60684 | 0.71062 | 0.53663 | 0.12027 | 0.17399 | 1152.2353 | 1045.4563 | 16.5626
38903.6002 | 1204 | 1012 | 38903.6002 | 1275 | 969 | 891.5 | 981.5 | 73.5043 | 61.7827 | 77.8388 | 59.1575 | 0.73504 | 0.61783 | 0.77839 | 0.59158 | 0.11722 | 0.18681 | 284.8089 | 469.0066 | 12.1667
38903.6003 | 1041 | 818 | 38903.6003 | 1076 | 790 | 902.5 | 992.5 | 63.5531 | 49.9389 | 65.6899 | 48.2295 | 0.63553 | 0.49939 | 0.6569 | 0.4823 | 0.13614 | 0.1746 | 1980.8417 | 523.887 | 51.9822
38903.6004 | 1272 | 929 | 38903.6004 | 1368 | 1013 | 913.5 | 1003.5 | 77.6557 | 56.7155 | 83.5165 | 61.8437 | 0.77656 | 0.56716 | 0.83516 | 0.61844 | 0.2094 | 0.21673 | 1214.32 | 367.2525 | 13.9074
38903.6005 | 1292 | 926 | 38903.6006 | 1379 | 1007 | 923.5 | 1013.5 | 78.8767 | 56.5324 | 84.188 | 61.4774 | 0.78877 | 0.56532 | 0.84188 | 0.61477 | 0.22344 | 0.22711 | 763.3316 | 410.8576 | 12.8003
38903.6007 | 1217 | 835 | 38903.6007 | 1174 | 762 | 934.5 | 1024.5 | 74.2979 | 50.9768 | 71.6728 | 46.5201 | 0.74298 | 0.50977 | 0.71673 | 0.4652 | 0.23321 | 0.25153 | 658.8403 | 402.0284 | 30.0548
38903.6008 | 1207 | 801 | 38903.6008 | 1105 | 732 | 945.5 | 1035.5 | 73.6874 | 48.9011 | 67.4603 | 44.6886 | 0.73687 | 0.48901 | 0.6746 | 0.44689 | 0.24786 | 0.22772 | 410.2854 | 647.7185 | 38.6497
38903.6009 | 1334 | 837 | 38903.6009 | 1458 | 714 | 956.5 | 1046.5 | 81.4408 | 51.0989 | 89.011 | 43.5897 | 0.81441 | 0.51099 | 0.89011 | 0.4359 | 0.30342 | 0.45421 | 196.9232 | 3129.2881 | 22.5043
38903.6011 | 1334 | 758 | 38903.6011 | 1157 | 731 | 967.5 | 1057.5 | 81.4408 | 46.2759 | 70.6349 | 44.6276 | 0.81441 | 0.46276 | 0.70635 | 0.44628 | 0.35165 | 0.26007 | 185.5175 | 3780.065 | 35.1364
38903.6012 | 1239 | 655 | 38903.6012 | 1440 | 838 | 978 | 1068 | 75.641 | 39.9878 | 87.9121 | 51.16 | 0.75641 | 0.39988 | 0.87912 | 0.5116 | 0.35653 | 0.36752 | 337.7134 | 261.5098 | 52.0592
38903.6013 | 1272 | 683 | 38903.6013 | 1318 | 813 | 988.5 | 1078.5 | 77.6557 | 41.6972 | 80.464 | 49.6337 | 0.77656 | 0.41697 | 0.80464 | 0.49634 | 0.35958 | 0.3083 | 216.8835 | 804.7833 | 53.4441
38903.6014 | 1608 | 727 | 38903.6014 | 1581 | 722 | 999.5 | 1089.5 | 98.1685 | 44.3834 | 96.5201 | 44.0781 | 0.98168 | 0.44383 | 0.9652 | 0.44078 | 0.53785 | 0.52442 | 103.9581 | 476.8575 | 3.4544
38903.6016 | 1669 | 311 | 38903.6016 | 1690 | 445 | 1010.5 | 1100.5 | 101.8926 | 18.9866 | 103.1746 | 27.1673 | 1.0189 | 0.18987 | 1.0317 | 0.27167 | 0.82906 | 0.76007 | 62.631 | 126.3599 | 69.1733
38903.6017 | 1486 | 543 | 38903.6017 | 1718 | 709 | 1021.5 | 1111.5 | 90.7204 | 33.1502 | 104.884 | 43.2845 | 0.9072 | 0.3315 | 1.0488 | 0.43284 | 0.5757 | 0.616 | 294.4546 | 84.2706 | 28.3302
38903.6018 | 1269 | 826 | 38903.6018 | 1464 | 731 | 1031.5 | 1121.5 | 77.4725 | 50.4274 | 89.3773 | 44.6276 | 0.77473 | 0.50427 | 0.89377 | 0.44628 | 0.27045 | 0.4475 | 186.493 | 570.0738 | 27.8486
38903.6019 | 1151 | 728 | 38903.6019 | 1180 | 687 | 1042.5 | 1132.5 | 70.2686 | 44.4444 | 72.0391 | 41.9414 | 0.70269 | 0.44444 | 0.72039 | 0.41941 | 0.25824 | 0.30098 | 659.1497 | 304.9014 | 50.31
38903.602 | 1274 | 804 | 38903.6021 | 1386 | 816 | 1053.5 | 1143.5 | 77.7778 | 49.0842 | 84.6154 | 49.8168 | 0.77778 | 0.49084 | 0.84615 | 0.49817 | 0.28694 | 0.34799 | 20349.5881 | 173.0384 | 22.6527
38903.6022 | 1678 | 386 | 38903.6022 | 1487 | 504 | 1064.5 | 1154.5 | 102.442 | 23.5653 | 90.7814 | 30.7692 | 1.0244 | 0.23565 | 0.90781 | 0.30769 | 0.78877 | 0.60012 | 54.1728 | 1668.547 | 73.6629
38903.6023 | 1715 | 527 | 38903.6023 | 1541 | 523 | 1075.5 | 1165.5 | 104.7009 | 32.1734 | 94.0781 | 31.9292 | 1.047 | 0.32173 | 0.94078 | 0.31929 | 0.72527 | 0.62149 | 58.8288 | 639.1588 | 20.2444
38903.6024 | 1360 | 561 | 38903.6024 | 1686 | 624 | 1086 | 1176 | 83.0281 | 34.2491 | 102.9304 | 38.0952 | 0.83028 | 0.34249 | 1.0293 | 0.38095 | 0.48779 | 0.64835 | 628.7529 | 87.7798 | 37.0286
38903.6025 | 1672 | 416 | 38903.6026 | 1894 | 472 | 1096.5 | 1186.5 | 102.0757 | 25.3968 | 115.6288 | 28.8156 | 1.0208 | 0.25397 | 1.1563 | 0.28816 | 0.76679 | 0.86813 | 26032.0508 | 33.1914 | 16.6162
38903.6027 | 1753 | 546 | 38903.6027 | 1835 | 484 | 1107.5 | 1197.5 | 107.0208 | 33.3333 | 112.0269 | 29.5482 | 1.0702 | 0.33333 | 1.1203 | 0.29548 | 0.73687 | 0.82479 | 62.0966 | 247.2527 | 8.6565
38903.6028 | 1703 | 516 | 38903.6028 | 1577 | 453 | 1118.5 | 1208.5 | 103.9683 | 31.5018 | 96.2759 | 27.6557 | 1.0397 | 0.31502 | 0.96276 | 0.27656 | 0.72466 | 0.6862 | 81.0681 | 139.4842 | 16.5227
38903.6029 | 1505 | 431 | 38903.6029 | 1669 | 502 | 1129.5 | 1219.5 | 91.8803 | 26.3126 | 101.8926 | 30.6471 | 0.9188 | 0.26313 | 1.0189 | 0.30647 | 0.65568 | 0.71245 | 156.282 | 82.3353 | 44.9862
38903.6031 | 1766 | 640 | 38903.6031 | 1704 | 685 | 1140 | 1230 | 107.8144 | 39.072 | 104.0293 | 41.8193 | 1.0781 | 0.39072 | 1.0403 | 0.41819 | 0.68742 | 0.6221 | 45.3596 | 327.539 | 4.8624
38903.6032 | 2086 | 58 | 38903.6032 | 2324 | 70 | 1150.5 | 1240.5 | 127.3504 | 3.5409 | 141.8803 | 4.2735 | 1.2735 | 0.035409 | 1.4188 | 0.042735 | 1.2381 | 1.3761 | 16.0227 | 20.3978 | 64.6659
38903.6033 | 1841 | 53 | 38903.6033 | 2060 | 58 | 1161.5 | 1251.5 | 112.3932 | 3.2357 | 125.7631 | 3.5409 | 1.1239 | 0.032357 | 1.2576 | 0.035409 | 1.0916 | 1.2222 | 35.7027 | 16.6008 | 126.6261
38903.6034 | 2107 | 63 | 38903.6034 | 2307 | 70 | 1172.5 | 1262.5 | 128.6325 | 3.8462 | 140.8425 | 4.2735 | 1.2863 | 0.038462 | 1.4084 | 0.042735 | 1.2479 | 1.3657 | 49.4125 | 4.1418 | 12.3339
38903.6036 | 2122 | 78 | 38903.6036 | 2217 | 70 | 1183.5 | 1273.5 | 129.5482 | 4.7619 | 135.348 | 4.2735 | 1.2955 | 0.047619 | 1.3535 | 0.042735 | 1.2479 | 1.3107 | 22.5682 | 8.0781 | 15.8474
| 2197 | 84 | 38903.6037 | 2329 | 64 | 1194 | 1284 | 134.127 | 5.1282 | 142.1856 | 3.9072 | 1.3413 | 0.051282 | 1.4219 | 0.039072 | 1.29 | 1.3828 | 0.66114 | 0.35967 | 0.36
38903.6038 | 2271 | 90 | 38903.6038 | 2236 | 70 | 1204.5 | 1294.5 | 138.6447 | 5.4945 | 136.5079 | 4.2735 | 1.3864 | 0.054945 | 1.3651 | 0.042735 | 1.3315 | 1.3223 | 6.7756 | 11.4204 | 0.49883
38903.6039 | 2100 | 88 | 38903.6039 | 2004 | 85 | 1215.5 | 1305.5 | 128.2051 | 5.3724 | 122.3443 | 5.1893 | 1.2821 | 0.053724 | 1.2234 | 0.051893 | 1.2283 | 1.1716 | 15.84 | 26.1418 | 41.7732
38903.6041 | 2013 | 94 | 38903.6041 | 1847 | 79 | 1226.5 | 1316.5 | 122.8938 | 5.7387 | 112.7595 | 4.823 | 1.2289 | 0.057387 | 1.1276 | 0.04823 | 1.1716 | 1.0794 | 21.1495 | 37.174 | 74.4901
38903.6042 | 2094 | 102 | 38903.6042 | 2075 | 100 | 1237.5 | 1327.5 | 127.8388 | 6.2271 | 126.6789 | 6.105 | 1.2784 | 0.062271 | 1.2668 | 0.06105 | 1.2161 | 1.2057 | 18.1978 | 20.3706 | 28.1026
38903.6043 | 2057 | 100 | 38903.6043 | 2284 | 119 | 1247.5 | 1337.5 | 125.58 | 6.105 | 139.4383 | 7.265 | 1.2558 | 0.06105 | 1.3944 | 0.07265 | 1.1947 | 1.3217 | 23.054 | 16.1457 | 28.9675
38903.6044 | 2286 | 121 | 38903.6044 | 2095 | 108 | 1258.5 | 1348.5 | 139.5604 | 7.3871 | 127.8999 | 6.5934 | 1.3956 | 0.073871 | 1.279 | 0.065934 | 1.3217 | 1.2131 | 2.4336 | 11.0324 | 3.4177
38903.6045 | 2276 | 120 | 38903.6046 | 2040 | 108 | 1269.5 | 1359.5 | 138.9499 | 7.326 | 124.5421 | 6.5934 | 1.3895 | 0.07326 | 1.2454 | 0.065934 | 1.3162 | 1.1795 | 3.4327 | 26.7967 | 5.3926
38903.6047 | 2279 | 126 | 38903.6047 | 1928 | 103 | 1280.5 | 1370.5 | 139.1331 | 7.6923 | 117.7045 | 6.2882 | 1.3913 | 0.076923 | 1.177 | 0.062882 | 1.3144 | 1.1142 | 3.4849 | 38.6847 | 8.7711
38903.6048 | 2186 | 122 | 38903.6048 | 2042 | 115 | 1291.5 | 1381.5 | 133.4554 | 7.4481 | 124.6642 | 7.0208 | 1.3346 | 0.074481 | 1.2466 | 0.070208 | 1.2601 | 1.1764 | 10.1715 | 40.6055 | 13.5826
38903.6049 | 2039 | 126 | 38903.6049 | 2141 | 121 | 1301.5 | 1391.5 | 124.4811 | 7.6923 | 130.7082 | 7.3871 | 1.2448 | 0.076923 | 1.3071 | 0.073871 | 1.1679 | 1.2332 | 33.1888 | 13.5543 | 18.9826
38903.605 | 1850 | 100 | 38903.6051 | 2000 | 106 | 1312.5 | 1402.5 | 112.9426 | 6.105 | 122.1001 | 6.4713 | 1.1294 | 0.06105 | 1.221 | 0.064713 | 1.0684 | 1.1563 | 39.4897 | 22.477 | 76.2305
38903.6052 | 1852 | 112 | 38903.6052 | 1754 | 109 | 1323.5 | 1413.5 | 113.0647 | 6.8376 | 107.0818 | 6.6545 | 1.1306 | 0.068376 | 1.0708 | 0.066545 | 1.0623 | 1.0043 | 34.2969 | 46.0658 | 113.0233
38903.6053 | 2134 | 101 | 38903.6053 | 1974 | 102 | 1334.5 | 1424.5 | 130.2808 | 6.1661 | 120.5128 | 6.2271 | 1.3028 | 0.061661 | 1.2051 | 0.062271 | 1.2411 | 1.1429 | 13.2303 | 35.5463 | 33.8529
38903.6054 | 1986 | 81 | 38903.6054 | 1995 | 93 | 1345.5 | 1435.5 | 121.2454 | 4.9451 | 121.7949 | 5.6777 | 1.2125 | 0.049451 | 1.2179 | 0.056777 | 1.163 | 1.1612 | 24.1122 | 24.4265 | 72.3158
38903.6056 | 2282 | 104 | 38903.6056 | 2308 | 101 | 1356 | 1446 | 139.3162 | 6.3492 | 140.9035 | 6.1661 | 1.3932 | 0.063492 | 1.409 | 0.061661 | 1.3297 | 1.3474 | 5.4705 | 15.9063 | 2.7209
38903.6057 | 2162 | 89 | 38903.6057 | 1954 | 87 | 1366.5 | 1456.5 | 131.9902 | 5.4335 | 119.2918 | 5.3114 | 1.3199 | 0.054335 | 1.1929 | 0.053114 | 1.2656 | 1.1398 | 11.0574 | 38.0837 | 35.4452
38903.6058 | 1975 | 90 | 38903.6058 | 2106 | 98 | 1377.5 | 1467.5 | 120.5739 | 5.4945 | 128.5714 | 5.9829 | 1.2057 | 0.054945 | 1.2857 | 0.059829 | 1.1508 | 1.2259 | 29.9914 | 15.4279 | 44.6092
38903.6059 | 2188 | 94 | 38903.6059 | 2294 | 101 | 1388.5 | 1478.5 | 133.5775 | 5.7387 | 140.0488 | 6.1661 | 1.3358 | 0.057387 | 1.4005 | 0.061661 | 1.2784 | 1.3388 | 5.5889 | 8.7056 | 7.1036
38903.6061 | 2223 | 101 | 38903.6061 | 2254 | 82 | 1399.5 | 1489.5 | 135.7143 | 6.1661 | 137.6068 | 5.0061 | 1.3571 | 0.061661 | 1.3761 | 0.050061 | 1.2955 | 1.326 | 44.6284 | 5.6019 | 2.1734
38903.6062 | 2267 | 80 | 38903.6062 | 1873 | 77 | 1409.5 | 1499.5 | 138.4005 | 4.884 | 114.3468 | 4.7009 | 1.384 | 0.04884 | 1.1435 | 0.047009 | 1.3352 | 1.0965 | 4.5309 | 509.9252 | 19.2081
38903.6063 | 2004 | 84 | 38903.6063 | 1860 | 76 | 1420.5 | 1510.5 | 122.3443 | 5.1282 | 113.5531 | 4.6398 | 1.2234 | 0.051282 | 1.1355 | 0.046398 | 1.1722 | 1.0891 | 21.4815 | 35.3361 | 86.2186
38903.6064 | 1895 | 79 | 38903.6064 | 1818 | 63 | 1431.5 | 1521.5 | 115.6899 | 4.823 | 110.989 | 3.8462 | 1.1569 | 0.04823 | 1.1099 | 0.038462 | 1.1087 | 1.0714 | 29.5184 | 35.5079 | 129.817
38903.6066 | 2056 | 57 | 38903.6066 | 2349 | 69 | 1442.5 | 1532.5 | 125.5189 | 3.4799 | 143.4066 | 4.2125 | 1.2552 | 0.034799 | 1.4341 | 0.042125 | 1.2204 | 1.3919 | 1.1671 | 0.23257 | 1.0274

## C2-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 143.6129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38903.5889 | 1 | 0 | 38903.5889 | 1 | 0 | -82 | 8 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.589 | 1 | 0 | 38903.589 | 1 | 0 | -71.5 | 18.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5892 | 1 | 0 | 38903.5892 | 1 | 0 | -60.5 | 29.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5893 | 1 | 0 | 38903.5893 | 1 | 0 | -49.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5894 | 1 | 0 | 38903.5894 | 1 | 0 | -38.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5895 | 1 | 0 | 38903.5895 | 1 | 0 | -28.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5897 | 1 | 0 | 38903.5897 | 1 | 0 | -17.5 | 72.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5898 | 3 | 0 | 38903.5898 | 1 | 0 | -6.5 | 83.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 78312.6667 | 235138 | 78312.6648
38903.5899 | 1 | 0 | 38903.5899 | 1 | 0 | 4.5 | 94.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.59 | 1 | 0 | 38903.59 | 1 | 0 | 15.5 | 105.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5902 | 1 | 0 | 38903.5902 | 1 | 0 | 26 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5903 | 1 | 0 | 38903.5903 | 1 | 0 | 36.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5904 | 1 | 0 | 38903.5904 | 1 | 0 | 47.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5905 | 1 | 0 | 38903.5905 | 1 | 0 | 58.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5907 | 1 | 0 | 38903.5907 | 1 | 0 | 69.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5908 | 2 | 1 | 38903.5908 | 1 | 0 | 79.5 | 169.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 234838.1275
38903.5909 | 1 | 0 | 38903.5909 | 1 | 0 | 90.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.591 | 1 | 0 | 38903.591 | 1 | 0 | 101.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5912 | 1 | 0 | 38903.5912 | 1 | 0 | 112.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5913 | 1 | 0 | 38903.5913 | 1 | 0 | 123.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5914 | 1 | 0 | 38903.5914 | 1 | 0 | 133.5 | 223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5915 | 1 | 0 | 38903.5915 | 1 | 0 | 144.5 | 234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5917 | 1 | 0 | 38903.5917 | 1 | 0 | 155.5 | 245.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5918 | 1 | 0 | 38903.5918 | 1 | 0 | 166.5 | 256.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5919 | 1 | 0 | 38903.5919 | 1 | 0 | 177.5 | 267.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.592 | 1 | 0 | 38903.592 | 1 | 0 | 187.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5922 | 1 | 0 | 38903.5922 | 1 | 0 | 198.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5923 | 1 | 0 | 38903.5923 | 1 | 0 | 209.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5924 | 1 | 0 | 38903.5924 | 1 | 0 | 220.5 | 310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5925 | 1 | 0 | 38903.5925 | 1 | 0 | 231.5 | 321.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5927 | 1 | 0 | 38903.5927 | 1 | 0 | 241.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5928 | 1 | 0 | 38903.5928 | 1 | 0 | 252.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5929 | 1 | 0 | 38903.5929 | 1 | 0 | 263.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.593 | 1 | 0 | 38903.593 | 1 | 0 | 274.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5932 | 1 | 0 | 38903.5932 | 1 | 0 | 285.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5933 | 1 | 0 | 38903.5933 | 1 | 0 | 295.5 | 385.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5934 | 2 | 0 | 38903.5934 | 1 | 0 | 306.5 | 396.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117519 | 235138 | 117518.9988
38903.5935 | 1 | 0 | 38903.5935 | 1 | 0 | 317.5 | 407.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5937 | 1 | 0 | 38903.5937 | 1 | 0 | 328.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5938 | 1 | 0 | 38903.5938 | 1 | 0 | 339.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5939 | 1 | 0 | 38903.5939 | 1 | 0 | 349.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.594 | 1 | 0 | 38903.594 | 1 | 0 | 360.5 | 450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5942 | 1 | 0 | 38903.5942 | 1 | 0 | 371.5 | 461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5943 | 1 | 0 | 38903.5943 | 1 | 0 | 382.5 | 472.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5944 | 1 | 0 | 38903.5944 | 1 | 0 | 393.5 | 483.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5945 | 1 | 0 | 38903.5945 | 1 | 0 | 403.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5947 | 1 | 0 | 38903.5947 | 1 | 0 | 414.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5948 | 1 | 0 | 38903.5948 | 1 | 0 | 425.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5949 | 1 | 0 | 38903.5949 | 1 | 0 | 436.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.595 | 1 | 0 | 38903.595 | 1 | 0 | 447 | 537 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5952 | 1 | 0 | 38903.5952 | 1 | 0 | 457.5 | 547.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5953 | 1 | 0 | 38903.5953 | 1 | 0 | 468.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5954 | 1 | 0 | 38903.5954 | 1 | 0 | 479.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5955 | 1 | 0 | 38903.5955 | 1 | 0 | 490.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5957 | 1 | 0 | 38903.5957 | 1 | 0 | 501.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5958 | 1 | 0 | 38903.5958 | 1 | 0 | 511.5 | 601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5959 | 1 | 0 | 38903.5959 | 1 | 0 | 522.5 | 612.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.596 | 1 | 0 | 38903.596 | 1 | 0 | 533.5 | 623.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5962 | 1 | 1 | 38903.5962 | 1 | 0 | 544.5 | 634.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 552898790.44 | 235138 | 234938.085
38903.5963 | 1 | 0 | 38903.5963 | 1 | 0 | 555 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5964 | 1 | 0 | 38903.5964 | 1 | 0 | 565.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5965 | 1 | 0 | 38903.5965 | 1 | 0 | 576.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5967 | 1 | 0 | 38903.5967 | 1 | 0 | 587.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5968 | 1 | 1 | 38903.5968 | 1 | 0 | 598.5 | 688.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 552898790.44 | 235138 | 234938.085
38903.5969 | 1 | 0 | 38903.5969 | 1 | 0 | 609.5 | 699.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.597 | 1 | 0 | 38903.597 | 1 | 0 | 619.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5972 | 1 | 0 | 38903.5972 | 1 | 0 | 630.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5973 | 1 | 0 | 38903.5973 | 1 | 0 | 641.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5974 | 1 | 0 | 38903.5974 | 1 | 0 | 652.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5975 | 1 | 0 | 38903.5975 | 1 | 0 | 663 | 753 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5977 | 1 | 0 | 38903.5977 | 1 | 0 | 673.5 | 763.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5978 | 1 | 0 | 38903.5978 | 1 | 0 | 684.5 | 774.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5979 | 1 | 0 | 38903.5979 | 1 | 0 | 695.5 | 785.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.598 | 1 | 0 | 38903.598 | 1 | 0 | 706.5 | 796.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5982 | 1 | 0 | 38903.5982 | 1 | 0 | 717.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5983 | 1 | 0 | 38903.5983 | 1 | 0 | 727.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5984 | 1 | 0 | 38903.5984 | 1 | 0 | 738.5 | 828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5985 | 1 | 0 | 38903.5985 | 1 | 0 | 749.5 | 839.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5987 | 1 | 0 | 38903.5987 | 1 | 0 | 760.5 | 850.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235138 | 235138 | 235137.9994
38903.5988 | 1 | 0 | 38903.5988 | 8 | 0 | 771 | 861 | 0.06105 | 0 | 0.4884 | 0 | 0.0006105 | 0 | 0.004884 | 0 | 0.0006105 | 0.004884 | 235138 | 29304.75 | 235137.9994
38903.5989 | 1 | 0 | 38903.5989 | 57 | 0 | 781.5 | 871.5 | 0.06105 | 0 | 3.4799 | 0 | 0.0006105 | 0 | 0.034799 | 0 | 0.0006105 | 0.034799 | 235138 | 4026.9825 | 235137.9994
38903.599 | 1 | 0 | 38903.599 | 109 | 0 | 792.5 | 882.5 | 0.06105 | 0 | 6.6545 | 0 | 0.0006105 | 0 | 0.066545 | 0 | 0.0006105 | 0.066545 | 235138 | 2058.1468 | 235137.9994
38903.5992 | 1 | 1 | 38903.5992 | 223 | 1 | 803.5 | 893.5 | 0.06105 | 0.06105 | 13.6142 | 0.06105 | 0.0006105 | 0.0006105 | 0.13614 | 0.0006105 | 0 | 0.13553 | 2255396.6416 | 959.18 | 212847.4373
38903.5993 | 444 | 352 | 38903.5993 | 408 | 157 | 814.5 | 904.5 | 27.1062 | 21.4896 | 24.9084 | 9.5849 | 0.27106 | 0.2149 | 0.24908 | 0.095849 | 0.056166 | 0.15324 | 4037.6816 | 786.8428 | 392.2964
38903.5994 | 419 | 309 | 38903.5994 | 477 | 241 | 825.5 | 915.5 | 25.58 | 18.8645 | 29.1209 | 14.7131 | 0.2558 | 0.18864 | 0.29121 | 0.14713 | 0.067155 | 0.14408 | 2662.8265 | 826.3425 | 468.9404
38903.5995 | 439 | 342 | 38903.5995 | 651 | 297 | 835.5 | 925.5 | 26.801 | 20.8791 | 39.7436 | 18.1319 | 0.26801 | 0.20879 | 0.39744 | 0.18132 | 0.059219 | 0.21612 | 7173.3214 | 486.3036 | 381.101
38903.5997 | 553 | 397 | 38903.5997 | 584 | 299 | 846.5 | 936.5 | 33.7607 | 24.2369 | 35.6532 | 18.254 | 0.33761 | 0.24237 | 0.35653 | 0.18254 | 0.095238 | 0.17399 | 1882.5232 | 657.1044 | 306.587
38903.5998 | 540 | 366 | 38903.5998 | 599 | 317 | 857.5 | 947.5 | 32.967 | 22.3443 | 36.569 | 19.3529 | 0.32967 | 0.22344 | 0.36569 | 0.19353 | 0.10623 | 0.17216 | 1516.6573 | 671.539 | 343.9653
38903.5999 | 566 | 436 | 38903.5999 | 1271 | 985 | 868.5 | 958.5 | 34.5543 | 26.6178 | 77.5946 | 60.1343 | 0.34554 | 0.26618 | 0.77595 | 0.60134 | 0.079365 | 0.1746 | 9458.2747 | 392.3932 | 246.8192
38903.6 | 1305 | 1040 | 38903.6 | 1320 | 1027 | 879 | 969 | 79.6703 | 63.4921 | 80.5861 | 62.6984 | 0.7967 | 0.63492 | 0.80586 | 0.62698 | 0.16178 | 0.17888 | 42.4357 | 47.2049 | 0.22756
38903.6002 | 1087 | 876 | 38903.6002 | 1329 | 1021 | 889.5 | 979.5 | 66.3614 | 53.4799 | 81.1355 | 62.3321 | 0.66361 | 0.5348 | 0.81136 | 0.62332 | 0.12882 | 0.18803 | 743.5173 | 2146.4477 | 42.4711
38903.6003 | 1149 | 921 | 38903.6003 | 1336 | 1009 | 900.5 | 990.5 | 70.1465 | 56.2271 | 81.5629 | 61.5995 | 0.70147 | 0.56227 | 0.81563 | 0.616 | 0.13919 | 0.19963 | 423.149 | 1633.3611 | 28.8913
38903.6004 | 1249 | 917 | 38903.6004 | 1040 | 799 | 911.5 | 1001.5 | 76.2515 | 55.9829 | 63.4921 | 48.779 | 0.76252 | 0.55983 | 0.63492 | 0.48779 | 0.20269 | 0.14713 | 333.1751 | 110639.1853 | 20.3066
38903.6005 | 1288 | 921 | 38903.6005 | 1236 | 973 | 922.5 | 1012.5 | 78.6325 | 56.2271 | 75.4579 | 59.4017 | 0.78632 | 0.56227 | 0.75458 | 0.59402 | 0.22405 | 0.16056 | 174.4117 | 378.594 | 12.315
38903.6007 | 1226 | 843 | 38903.6007 | 1109 | 750 | 933 | 1023 | 74.8474 | 51.4652 | 67.7045 | 45.7875 | 0.74847 | 0.51465 | 0.67705 | 0.45788 | 0.23382 | 0.21917 | 442.6082 | 655.9645 | 29.1689
38903.6008 | 1145 | 763 | 38903.6008 | 1075 | 748 | 943.5 | 1033.5 | 69.9023 | 46.5812 | 65.6288 | 45.6654 | 0.69902 | 0.46581 | 0.65629 | 0.45665 | 0.23321 | 0.19963 | 407.4338 | 890.7073 | 52.3624
38903.6009 | 1239 | 784 | 38903.6009 | 1103 | 727 | 954.5 | 1044.5 | 75.641 | 47.8632 | 67.3382 | 44.3834 | 0.75641 | 0.47863 | 0.67338 | 0.44383 | 0.27778 | 0.22955 | 300.0055 | 934.6673 | 37.9522
38903.601 | 1437 | 823 | 38903.601 | 1232 | 697 | 965.5 | 1055.5 | 87.7289 | 50.2442 | 75.2137 | 42.5519 | 0.87729 | 0.50244 | 0.75214 | 0.42552 | 0.37485 | 0.32662 | 182.5231 | 731.6501 | 9.8751
38903.6012 | 1506 | 826 | 38903.6012 | 1459 | 783 | 976.5 | 1066.5 | 91.9414 | 50.4274 | 89.072 | 47.8022 | 0.91941 | 0.50427 | 0.89072 | 0.47802 | 0.41514 | 0.4127 | 222.6702 | 275.4294 | 1.8101
38903.6013 | 1306 | 747 | 38903.6013 | 1450 | 835 | 987 | 1077 | 79.7314 | 45.6044 | 88.5226 | 50.9768 | 0.79731 | 0.45604 | 0.88523 | 0.50977 | 0.34127 | 0.37546 | 711.7921 | 181.3135 | 25.831
38903.6014 | 1316 | 692 | 38903.6014 | 1303 | 607 | 997.5 | 1087.5 | 80.3419 | 42.2466 | 79.5482 | 37.0574 | 0.80342 | 0.42247 | 0.79548 | 0.37057 | 0.38095 | 0.42491 | 385.4418 | 194.8643 | 32.8883
38903.6015 | 1809 | 473 | 38903.6015 | 1784 | 463 | 1008.5 | 1098.5 | 110.4396 | 28.8767 | 108.9133 | 28.2662 | 1.1044 | 0.28877 | 1.0891 | 0.28266 | 0.81563 | 0.80647 | 66.7897 | 90.5381 | 7.0703
38903.6017 | 1687 | 571 | 38903.6017 | 1413 | 449 | 1019.5 | 1109.5 | 102.9915 | 34.8596 | 86.2637 | 27.4115 | 1.0299 | 0.3486 | 0.86264 | 0.27411 | 0.68132 | 0.58852 | 74.0435 | 262.6903 | 11.9716
38903.6018 | 1547 | 654 | 38903.6018 | 1557 | 477 | 1030.5 | 1120.5 | 94.4444 | 39.9267 | 95.0549 | 29.1209 | 0.94444 | 0.39927 | 0.95055 | 0.29121 | 0.54518 | 0.65934 | 8310.4929 | 74.0398 | 9.8471
38903.6019 | 1137 | 689 | 38903.6019 | 1168 | 736 | 1041 | 1131 | 69.4139 | 42.0635 | 71.3065 | 44.9328 | 0.69414 | 0.42063 | 0.71306 | 0.44933 | 0.2735 | 0.26374 | 400.2364 | 477.3633 | 63.1655
38903.602 | 1133 | 769 | 38903.602 | 1194 | 872 | 1051.5 | 1141.5 | 69.1697 | 46.9475 | 72.8938 | 53.2357 | 0.6917 | 0.46947 | 0.72894 | 0.53236 | 0.22222 | 0.19658 | 426.3216 | 986.1945 | 53.175
38903.6022 | 1461 | 549 | 38903.6022 | 1731 | 422 | 1062.5 | 1152.5 | 89.1941 | 33.5165 | 105.6777 | 25.7631 | 0.89194 | 0.33516 | 1.0568 | 0.25763 | 0.55678 | 0.79915 | 212.0591 | 111.6637 | 32.9004
38903.6023 | 1348 | 503 | 38903.6023 | 1648 | 592 | 1073.5 | 1163.5 | 82.2955 | 30.7082 | 100.6105 | 36.1416 | 0.82295 | 0.30708 | 1.0061 | 0.36142 | 0.51587 | 0.64469 | 639.8084 | 73.1085 | 42.0967
38903.6024 | 1427 | 471 | 38903.6024 | 1722 | 688 | 1084.5 | 1174.5 | 87.1184 | 28.7546 | 105.1282 | 42.0024 | 0.87118 | 0.28755 | 1.0513 | 0.42002 | 0.58364 | 0.63126 | 224.2451 | 86.6868 | 44.7958
38903.6025 | 1747 | 425 | 38903.6025 | 1577 | 342 | 1095 | 1185 | 106.6545 | 25.9463 | 96.2759 | 20.8791 | 1.0665 | 0.25946 | 0.96276 | 0.20879 | 0.80708 | 0.75397 | 64.7869 | 109.6539 | 22.1983
38903.6027 | 1815 | 546 | 38903.6027 | 1347 | 497 | 1105.5 | 1195.5 | 110.8059 | 33.3333 | 82.2344 | 30.3419 | 1.1081 | 0.33333 | 0.82234 | 0.30342 | 0.77473 | 0.51893 | 33.128 | 154.6166 | 0.9587
38903.6028 | 1753 | 523 | 38903.6028 | 1465 | 471 | 1116.5 | 1206.5 | 107.0208 | 31.9292 | 89.4383 | 28.7546 | 1.0702 | 0.31929 | 0.89438 | 0.28755 | 0.75092 | 0.60684 | 49.954 | 1735.4423 | 13.8085
38903.6029 | 1790 | 526 | 38903.6029 | 1788 | 494 | 1127.5 | 1217.5 | 109.2796 | 32.1123 | 109.1575 | 30.1587 | 1.0928 | 0.32112 | 1.0916 | 0.30159 | 0.77167 | 0.78999 | 175.8263 | 55.7115 | 2.4746
38903.603 | 1438 | 509 | 38903.603 | 1336 | 551 | 1138.5 | 1228.5 | 87.79 | 31.0745 | 81.5629 | 33.6386 | 0.8779 | 0.31074 | 0.81563 | 0.33639 | 0.56716 | 0.47924 | 119.14 | 315.138 | 60.4579
38903.6032 | 2058 | 57 | 38903.6032 | 1994 | 55 | 1149 | 1239 | 125.641 | 3.4799 | 121.7338 | 3.3578 | 1.2564 | 0.034799 | 1.2173 | 0.033578 | 1.2216 | 1.1838 | 16.8753 | 22.2171 | 75.7051
38903.6033 | 1964 | 55 | 38903.6033 | 2336 | 67 | 1159.5 | 1249.5 | 119.9023 | 3.3578 | 142.6129 | 4.0904 | 1.199 | 0.033578 | 1.4261 | 0.040904 | 1.1654 | 1.3852 | 2.862 | 0.47164 | 2.8454
38903.6034 | 2057 | 66 | 38903.6034 | 2328 | 54 | 1170.5 | 1260.5 | 125.58 | 4.0293 | 142.1245 | 3.2967 | 1.2558 | 0.040293 | 1.4212 | 0.032967 | 1.2155 | 1.3883 | 3.5821 | 1.0551 | 3.6288
38903.6035 | 1837 | 61 | 38903.6035 | 2255 | 75 | 1181.5 | 1271.5 | 112.149 | 3.7241 | 137.6679 | 4.5788 | 1.1215 | 0.037241 | 1.3767 | 0.045788 | 1.0842 | 1.3309 | 114.1263 | 4.6058 | 32.7975
38903.6037 | 2155 | 66 | 38903.6037 | 2087 | 69 | 1192.5 | 1282.5 | 131.5629 | 4.0293 | 127.4115 | 4.2125 | 1.3156 | 0.040293 | 1.2741 | 0.042125 | 1.2753 | 1.232 | 11.3551 | 18.8167 | 31.5247
38903.6038 | 2187 | 81 | 38903.6038 | 1815 | 69 | 1203 | 1293 | 133.5165 | 4.9451 | 110.8059 | 4.2125 | 1.3352 | 0.049451 | 1.1081 | 0.042125 | 1.2857 | 1.0659 | 8.4099 | 58.0614 | 38.2663
38903.6039 | 2161 | 86 | 38903.6039 | 1806 | 68 | 1213.5 | 1303.5 | 131.9292 | 5.2503 | 110.2564 | 4.1514 | 1.3193 | 0.052503 | 1.1026 | 0.041514 | 1.2668 | 1.0611 | 10.0296 | 51.545 | 41.6778
38903.604 | 2189 | 99 | 38903.604 | 1998 | 87 | 1224.5 | 1314.5 | 133.6386 | 6.044 | 121.978 | 5.3114 | 1.3364 | 0.06044 | 1.2198 | 0.053114 | 1.2759 | 1.1667 | 8.9372 | 37.7988 | 17.8381
38903.6042 | 2025 | 108 | 38903.6042 | 1957 | 90 | 1235.5 | 1325.5 | 123.6264 | 6.5934 | 119.475 | 5.4945 | 1.2363 | 0.065934 | 1.1947 | 0.054945 | 1.1703 | 1.1398 | 21.5204 | 27.2903 | 43.5498
38903.6043 | 2253 | 113 | 38903.6043 | 1843 | 91 | 1246.5 | 1336.5 | 137.5458 | 6.8987 | 112.5153 | 5.5556 | 1.3755 | 0.068987 | 1.1252 | 0.055556 | 1.3065 | 1.0696 | 4.5218 | 195.5722 | 7.9752
38903.6044 | 1771 | 92 | 38903.6044 | 2271 | 116 | 1256.5 | 1346.5 | 108.1197 | 5.6166 | 138.6447 | 7.0818 | 1.0812 | 0.056166 | 1.3864 | 0.070818 | 1.025 | 1.3156 | 59.4595 | 13.1199 | 61.695
38903.6045 | 2266 | 128 | 38903.6045 | 1780 | 94 | 1267.5 | 1357.5 | 138.3394 | 7.8144 | 108.6691 | 5.7387 | 1.3834 | 0.078144 | 1.0867 | 0.057387 | 1.3053 | 1.0293 | 3.7115 | 67.6063 | 13.1156
38903.6047 | 1957 | 101 | 38903.6047 | 2257 | 128 | 1278.5 | 1368.5 | 119.475 | 6.1661 | 137.79 | 7.8144 | 1.1947 | 0.061661 | 1.3779 | 0.078144 | 1.1331 | 1.2998 | 65.2129 | 8.0819 | 21.7945
38903.6048 | 2183 | 125 | 38903.6048 | 1763 | 99 | 1289.5 | 1379.5 | 133.2723 | 7.6313 | 107.6313 | 6.044 | 1.3327 | 0.076313 | 1.0763 | 0.06044 | 1.2564 | 1.0159 | 8.7024 | 111.9681 | 18.7543
38903.6049 | 1731 | 103 | 38903.6049 | 2203 | 135 | 1300.5 | 1390.5 | 105.6777 | 6.2882 | 134.4933 | 8.2418 | 1.0568 | 0.062882 | 1.3449 | 0.082418 | 0.99389 | 1.2625 | 261.4294 | 7.4084 | 34.7134
38903.605 | 1923 | 169 | 38903.605 | 2014 | 213 | 1310.5 | 1400.5 | 117.3993 | 10.3175 | 122.9548 | 13.0037 | 1.174 | 0.10317 | 1.2295 | 0.13004 | 1.0708 | 1.0995 | 37.7993 | 27.3439 | 33.0829
38903.6052 | 2259 | 132 | 38903.6052 | 1814 | 106 | 1321.5 | 1411.5 | 137.9121 | 8.0586 | 110.7448 | 6.4713 | 1.3791 | 0.080586 | 1.1074 | 0.064713 | 1.2985 | 1.0427 | 3.9451 | 54.9985 | 10.3815
38903.6053 | 2195 | 100 | 38903.6053 | 1902 | 93 | 1332.5 | 1422.5 | 134.0049 | 6.105 | 116.1172 | 5.6777 | 1.34 | 0.06105 | 1.1612 | 0.056777 | 1.279 | 1.1044 | 8.0746 | 68.5256 | 23.3318
38903.6054 | 2246 | 101 | 38903.6054 | 1947 | 89 | 1343.5 | 1433.5 | 137.1184 | 6.1661 | 118.8645 | 5.4335 | 1.3712 | 0.061661 | 1.1886 | 0.054335 | 1.3095 | 1.1343 | 5.006 | 505.7804 | 4.4474
38903.6055 | 1866 | 85 | 38903.6055 | 1883 | 89 | 1354.5 | 1444.5 | 113.9194 | 5.1893 | 114.9573 | 5.4335 | 1.1392 | 0.051893 | 1.1496 | 0.054335 | 1.0873 | 1.0952 | 32.2955 | 30.9124 | 111.5036
38903.6056 | 2277 | 85 | 38903.6057 | 2304 | 102 | 1364.5 | 1454.5 | 139.011 | 5.1893 | 140.6593 | 6.2271 | 1.3901 | 0.051893 | 1.4066 | 0.062271 | 1.3382 | 1.3443 | 6.1921 | 8.7211 | 0.90785
38903.6058 | 2114 | 105 | 38903.6058 | 2007 | 91 | 1375.5 | 1465.5 | 129.0598 | 6.4103 | 122.5275 | 5.5556 | 1.2906 | 0.064103 | 1.2253 | 0.055556 | 1.2265 | 1.1697 | 14.7713 | 26.5689 | 26.6654
38903.6059 | 1980 | 98 | 38903.6059 | 2216 | 94 | 1386.5 | 1476.5 | 120.8791 | 5.9829 | 135.2869 | 5.7387 | 1.2088 | 0.059829 | 1.3529 | 0.057387 | 1.149 | 1.2955 | 85.3463 | 6.7788 | 17.7744
38903.606 | 1950 | 82 | 38903.606 | 2238 | 100 | 1397.5 | 1487.5 | 119.0476 | 5.0061 | 136.63 | 6.105 | 1.1905 | 0.050061 | 1.3663 | 0.06105 | 1.1404 | 1.3053 | 98.6397 | 5.6162 | 20.776
38903.6062 | 2068 | 93 | 38903.6062 | 2304 | 106 | 1408.5 | 1498.5 | 126.2515 | 5.6777 | 140.6593 | 6.4713 | 1.2625 | 0.056777 | 1.4066 | 0.064713 | 1.2057 | 1.3419 | 3.5827 | 1.5598 | 3.1604
38903.6063 | 1897 | 65 | 38903.6063 | 2103 | 75 | 1418.5 | 1508.5 | 115.812 | 3.9683 | 128.3883 | 4.5788 | 1.1581 | 0.039683 | 1.2839 | 0.045788 | 1.1184 | 1.2381 | 33.4378 | 13.826 | 72.9507
38903.6064 | 1780 | 77 | 38903.6064 | 2109 | 92 | 1429.5 | 1519.5 | 108.6691 | 4.7009 | 128.7546 | 5.6166 | 1.0867 | 0.047009 | 1.2875 | 0.056166 | 1.0397 | 1.2314 | 51.018 | 13.2511 | 75.2764
38903.6065 | 1968 | 74 | 38903.6065 | 2287 | 70 | 1440.5 | 1530.5 | 120.1465 | 4.5177 | 139.6215 | 4.2735 | 1.2015 | 0.045177 | 1.3962 | 0.042735 | 1.1563 | 1.3535 | 49.5939 | 6.6134 | 26.018

## C2-3
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 143.3077 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38903.5889 | 1 | 0 | 38903.5889 | 1 | 0 | -83.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.589 | 1 | 0 | 38903.589 | 1 | 0 | -73 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5891 | 1 | 0 | 38903.5891 | 1 | 0 | -62.5 | 27.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5893 | 1 | 0 | 38903.5893 | 1 | 0 | -51.5 | 38.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5894 | 1 | 0 | 38903.5894 | 1 | 0 | -40.5 | 49.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5895 | 1 | 0 | 38903.5895 | 1 | 0 | -29.5 | 60.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5896 | 1 | 0 | 38903.5896 | 1 | 0 | -19.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5898 | 1 | 0 | 38903.5898 | 1 | 0 | -8.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5899 | 1 | 0 | 38903.5899 | 1 | 0 | 2.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.59 | 1 | 0 | 38903.59 | 1 | 0 | 13.5 | 103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5901 | 1 | 0 | 38903.5902 | 1 | 0 | 24.5 | 114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5903 | 1 | 0 | 38903.5903 | 1 | 0 | 35 | 125 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5904 | 1 | 0 | 38903.5904 | 1 | 0 | 45.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5905 | 1 | 1 | 38903.5905 | 1 | 0 | 56.5 | 146.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 550549910.44 | 234638 | 234438.0852
38903.5906 | 1 | 0 | 38903.5906 | 1 | 0 | 67.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5908 | 1 | 0 | 38903.5908 | 1 | 0 | 78.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5909 | 1 | 0 | 38903.5909 | 1 | 0 | 89 | 179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.591 | 1 | 0 | 38903.591 | 1 | 0 | 99.5 | 189.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5911 | 1 | 0 | 38903.5911 | 1 | 0 | 110.5 | 200.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5913 | 1 | 0 | 38903.5913 | 1 | 0 | 121.5 | 211.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5914 | 1 | 0 | 38903.5914 | 1 | 0 | 132.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5915 | 1 | 0 | 38903.5915 | 1 | 0 | 143 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5916 | 1 | 0 | 38903.5916 | 1 | 0 | 153.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5918 | 1 | 0 | 38903.5918 | 1 | 0 | 164.5 | 254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5919 | 1 | 0 | 38903.5919 | 1 | 0 | 175.5 | 265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.592 | 1 | 0 | 38903.592 | 1 | 0 | 186.5 | 276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5921 | 1 | 0 | 38903.5921 | 1 | 0 | 196.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5923 | 1 | 0 | 38903.5923 | 1 | 0 | 207.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5924 | 2 | 0 | 38903.5924 | 1 | 0 | 218.5 | 308.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117269 | 234638 | 117268.9988
38903.5925 | 1 | 1 | 38903.5925 | 1 | 0 | 229.5 | 319.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 550549910.44 | 234638 | 234438.0852
38903.5926 | 1 | 0 | 38903.5927 | 1 | 0 | 240.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5928 | 1 | 0 | 38903.5928 | 1 | 0 | 250.5 | 340.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5929 | 1 | 0 | 38903.5929 | 1 | 0 | 261.5 | 351.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.593 | 1 | 0 | 38903.593 | 1 | 0 | 272.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5931 | 1 | 0 | 38903.5931 | 1 | 0 | 283.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5933 | 1 | 0 | 38903.5933 | 1 | 0 | 294.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5934 | 1 | 0 | 38903.5934 | 2 | 0 | 304.5 | 394.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 234638 | 117269 | 234637.9994
38903.5935 | 2 | 0 | 38903.5935 | 1 | 0 | 315.5 | 405.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117269 | 234638 | 117268.9988
38903.5936 | 1 | 0 | 38903.5936 | 1 | 0 | 326.5 | 416.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5938 | 1 | 0 | 38903.5938 | 1 | 0 | 337.5 | 427.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5939 | 1 | 0 | 38903.5939 | 1 | 0 | 348.5 | 438.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.594 | 1 | 0 | 38903.594 | 1 | 0 | 358.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5941 | 1 | 0 | 38903.5941 | 1 | 0 | 369.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5943 | 1 | 0 | 38903.5943 | 1 | 0 | 380.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5944 | 1 | 0 | 38903.5944 | 1 | 0 | 391.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5945 | 2 | 0 | 38903.5945 | 1 | 0 | 402.5 | 492.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117269 | 234638 | 117268.9988
38903.5946 | 1 | 0 | 38903.5946 | 1 | 0 | 412.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5948 | 1 | 0 | 38903.5948 | 1 | 0 | 423.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5949 | 1 | 0 | 38903.5949 | 1 | 0 | 434.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.595 | 1 | 0 | 38903.595 | 1 | 0 | 445.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5951 | 1 | 0 | 38903.5951 | 1 | 0 | 456 | 546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5953 | 1 | 0 | 38903.5953 | 1 | 0 | 466.5 | 556.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5954 | 1 | 0 | 38903.5954 | 1 | 0 | 477.5 | 567.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5955 | 1 | 0 | 38903.5955 | 1 | 0 | 488.5 | 578.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5956 | 1 | 0 | 38903.5956 | 1 | 0 | 499.5 | 589.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5958 | 1 | 0 | 38903.5958 | 1 | 0 | 510 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5959 | 1 | 0 | 38903.5959 | 1 | 0 | 520.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.596 | 1 | 0 | 38903.596 | 1 | 0 | 531.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5961 | 1 | 0 | 38903.5961 | 1 | 0 | 542.5 | 632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5963 | 1 | 0 | 38903.5963 | 1 | 0 | 553.5 | 643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5964 | 1 | 0 | 38903.5964 | 2 | 0 | 564.5 | 654.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 234638 | 117269 | 234637.9994
38903.5965 | 1 | 0 | 38903.5965 | 1 | 0 | 574.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5966 | 1 | 0 | 38903.5966 | 1 | 0 | 585.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5968 | 1 | 0 | 38903.5968 | 1 | 0 | 596.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5969 | 1 | 0 | 38903.5969 | 1 | 0 | 607.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.597 | 1 | 0 | 38903.597 | 1 | 0 | 618.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5971 | 1 | 0 | 38903.5971 | 1 | 0 | 628.5 | 718.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5973 | 1 | 0 | 38903.5973 | 1 | 0 | 639.5 | 729.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5974 | 1 | 0 | 38903.5974 | 1 | 0 | 650.5 | 740.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5975 | 1 | 0 | 38903.5975 | 1 | 0 | 661.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5976 | 1 | 0 | 38903.5976 | 1 | 0 | 672 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5978 | 1 | 0 | 38903.5978 | 1 | 0 | 682.5 | 772.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5979 | 1 | 0 | 38903.5979 | 1 | 0 | 693.5 | 783.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.598 | 1 | 0 | 38903.598 | 1 | 0 | 704.5 | 794.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5981 | 1 | 0 | 38903.5981 | 1 | 0 | 715.5 | 805.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5983 | 1 | 0 | 38903.5983 | 1 | 0 | 726.5 | 816.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5984 | 1 | 0 | 38903.5984 | 1 | 0 | 736.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5985 | 1 | 0 | 38903.5985 | 1 | 0 | 747.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5986 | 1 | 0 | 38903.5986 | 1 | 0 | 758.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5988 | 1 | 0 | 38903.5988 | 1 | 0 | 769.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.5989 | 1 | 0 | 38903.5989 | 1 | 0 | 780.5 | 870.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234637.9994
38903.599 | 2 | 1 | 38903.599 | 1 | 0 | 790.5 | 880.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234638 | 234638 | 234338.1278
38903.5991 | 4 | 12 | 38903.5991 | 38 | 2 | 801.5 | 891.5 | 0.2442 | 0.7326 | 2.3199 | 0.1221 | 0.002442 | 0.007326 | 0.023199 | 0.001221 | 0.004884 | 0.021978 | 29993.454 | 6416.1329 | 19130.0118
38903.5993 | 40 | 17 | 38903.5993 | 95 | 8 | 812.5 | 902.5 | 2.442 | 1.0379 | 5.7998 | 0.4884 | 0.02442 | 0.010379 | 0.057998 | 0.004884 | 0.014042 | 0.053114 | 10326.6451 | 2591.2499 | 12972.2077
38903.5994 | 196 | 51 | 38903.5994 | 215 | 63 | 823.5 | 913.5 | 11.9658 | 3.1136 | 13.1258 | 3.8462 | 0.11966 | 0.031136 | 0.13126 | 0.038462 | 0.088523 | 0.092796 | 1520.8 | 1442.1864 | 3851.3432
| 261 | 100 | 38903.5995 | 371 | 223 | 835 | 925 | 15.9341 | 6.105 | 22.6496 | 13.6142 | 0.15934 | 0.06105 | 0.2265 | 0.13614 | 0.098291 | 0.090354 | 1351.7527 | 1502.9174 | 1862.4572
38903.5996 | 326 | 148 | 38903.5996 | 382 | 199 | 844.5 | 934.5 | 19.9023 | 9.0354 | 23.3211 | 12.149 | 0.19902 | 0.090354 | 0.23321 | 0.12149 | 0.10867 | 0.11172 | 1221.7764 | 1178.9056 | 1166.8223
38903.5998 | 496 | 285 | 38903.5998 | 512 | 262 | 855.5 | 945.5 | 30.2808 | 17.3993 | 31.2576 | 15.9951 | 0.30281 | 0.17399 | 0.31258 | 0.15995 | 0.12882 | 0.15263 | 1051.6317 | 815.4116 | 489.5677
38903.5999 | 530 | 409 | 38903.5999 | 583 | 299 | 866.5 | 956.5 | 32.3565 | 24.9695 | 35.5922 | 18.254 | 0.32357 | 0.24969 | 0.35592 | 0.18254 | 0.073871 | 0.17338 | 3168.7371 | 642.6114 | 297.9774
38903.6 | 1306 | 1055 | 38903.6 | 1048 | 804 | 877.5 | 967.5 | 79.7314 | 64.4078 | 63.9805 | 49.0842 | 0.79731 | 0.64408 | 0.6398 | 0.49084 | 0.15324 | 0.14896 | 734.715 | 965.5806 | 1.1698
38903.6001 | 1129 | 845 | 38903.6001 | 1329 | 1023 | 888 | 978 | 68.9255 | 51.5873 | 81.1355 | 62.4542 | 0.68926 | 0.51587 | 0.81136 | 0.62454 | 0.17338 | 0.18681 | 1227.8623 | 457.3197 | 36.2585
38903.6003 | 1095 | 872 | 38903.6003 | 1292 | 973 | 898.5 | 988.5 | 66.8498 | 53.2357 | 78.8767 | 59.4017 | 0.6685 | 0.53236 | 0.78877 | 0.59402 | 0.13614 | 0.19475 | 1105.3247 | 794.9261 | 38.7472
38903.6004 | 1227 | 901 | 38903.6004 | 1299 | 947 | 909.5 | 999.5 | 74.9084 | 55.0061 | 79.304 | 57.8144 | 0.74908 | 0.55006 | 0.79304 | 0.57814 | 0.19902 | 0.2149 | 1305.1931 | 375.1668 | 19.2243
38903.6005 | 1354 | 988 | 38903.6005 | 1227 | 871 | 920.5 | 1010.5 | 82.6618 | 60.3175 | 74.9084 | 53.1746 | 0.82662 | 0.60317 | 0.74908 | 0.53175 | 0.22344 | 0.21734 | 432.7283 | 724.1388 | 0.47846
38903.6006 | 1182 | 814 | 38903.6006 | 1256 | 860 | 931.5 | 1021.5 | 72.1612 | 49.6947 | 76.6789 | 52.5031 | 0.72161 | 0.49695 | 0.76679 | 0.52503 | 0.22466 | 0.24176 | 721.2471 | 394.3387 | 34.4348
38903.6008 | 1350 | 919 | 38903.6008 | 1402 | 959 | 942 | 1032 | 82.4176 | 56.105 | 85.5922 | 58.547 | 0.82418 | 0.56105 | 0.85592 | 0.58547 | 0.26313 | 0.27045 | 18018.0538 | 215.9992 | 5.8298
38903.6009 | 1322 | 854 | 38903.6009 | 1420 | 920 | 952.5 | 1042.5 | 80.7082 | 52.1368 | 86.6911 | 56.1661 | 0.80708 | 0.52137 | 0.86691 | 0.56166 | 0.28571 | 0.30525 | 2355.8693 | 201.1895 | 13.405
38903.601 | 1130 | 702 | 38903.601 | 1272 | 722 | 963.5 | 1053.5 | 68.9866 | 42.8571 | 77.6557 | 44.0781 | 0.68987 | 0.42857 | 0.77656 | 0.44078 | 0.26129 | 0.33578 | 1081.8144 | 222.5261 | 50.6532
38903.6011 | 1509 | 848 | 38903.6011 | 1432 | 776 | 974.5 | 1064.5 | 92.1245 | 51.7705 | 87.4237 | 47.3748 | 0.92125 | 0.5177 | 0.87424 | 0.47375 | 0.40354 | 0.40049 | 224.2566 | 295.3145 | 0.84746
38903.6013 | 1237 | 650 | 38903.6013 | 1206 | 625 | 985.5 | 1075.5 | 75.5189 | 39.6825 | 73.6264 | 38.1563 | 0.75519 | 0.39683 | 0.73626 | 0.38156 | 0.35836 | 0.3547 | 294.5595 | 309.4691 | 53.5302
38903.6014 | 1222 | 698 | 38903.6014 | 1395 | 667 | 996 | 1086 | 74.6032 | 42.6129 | 85.1648 | 40.7204 | 0.74603 | 0.42613 | 0.85165 | 0.4072 | 0.3199 | 0.44444 | 6664.0805 | 137.642 | 35.4639
38903.6015 | 1882 | 470 | 38903.6015 | 1477 | 362 | 1006.5 | 1096.5 | 114.8962 | 28.6935 | 90.1709 | 22.1001 | 1.149 | 0.28694 | 0.90171 | 0.221 | 0.86203 | 0.68071 | 33.3251 | 3029.3557 | 0.95157
38903.6016 | 1438 | 576 | 38903.6016 | 1723 | 540 | 1017.5 | 1107.5 | 87.79 | 35.1648 | 105.1893 | 32.967 | 0.8779 | 0.35165 | 1.0519 | 0.32967 | 0.52625 | 0.72222 | 179.3102 | 162.3242 | 35.8148
38903.6018 | 1662 | 620 | 38903.6018 | 1709 | 787 | 1028.5 | 1118.5 | 101.4652 | 37.851 | 104.3346 | 48.0464 | 1.0147 | 0.37851 | 1.0433 | 0.48046 | 0.63614 | 0.56288 | 53.8814 | 269.5468 | 7.6916
38903.6019 | 1255 | 739 | 38903.6019 | 1429 | 860 | 1039.5 | 1129.5 | 76.6178 | 45.116 | 87.2405 | 52.5031 | 0.76618 | 0.45116 | 0.87241 | 0.52503 | 0.31502 | 0.34737 | 688.6285 | 206.7892 | 32.2319
38903.602 | 1130 | 725 | 38903.602 | 1462 | 857 | 1050 | 1140 | 68.9866 | 44.2613 | 89.2552 | 52.3199 | 0.68987 | 0.44261 | 0.89255 | 0.5232 | 0.24725 | 0.36935 | 570.32 | 378.5023 | 53.7213
38903.6021 | 1755 | 442 | 38903.6021 | 1568 | 436 | 1060.5 | 1150.5 | 107.1429 | 26.9841 | 95.7265 | 26.6178 | 1.0714 | 0.26984 | 0.95726 | 0.26618 | 0.80159 | 0.69109 | 51.4314 | 274.1695 | 24.9298
38903.6023 | 1846 | 525 | 38903.6023 | 1633 | 486 | 1071.5 | 1161.5 | 112.6984 | 32.0513 | 99.6947 | 29.6703 | 1.127 | 0.32051 | 0.99695 | 0.2967 | 0.80647 | 0.70024 | 30.1668 | 153.9465 | 2.7274
38903.6024 | 1642 | 525 | 38903.6024 | 1747 | 569 | 1082.5 | 1172.5 | 100.2442 | 32.0513 | 106.6545 | 34.7375 | 1.0024 | 0.32051 | 1.0665 | 0.34737 | 0.68193 | 0.71917 | 239.142 | 63.8657 | 13.3909
38903.6025 | 1752 | 450 | 38903.6025 | 1592 | 362 | 1093.5 | 1183.5 | 106.9597 | 27.4725 | 97.1917 | 22.1001 | 1.0696 | 0.27473 | 0.97192 | 0.221 | 0.79487 | 0.75092 | 66.7058 | 109.9025 | 16.9154
38903.6026 | 1460 | 466 | 38903.6026 | 1644 | 569 | 1104 | 1194 | 89.1331 | 28.4493 | 100.3663 | 34.7375 | 0.89133 | 0.28449 | 1.0037 | 0.34737 | 0.60684 | 0.65629 | 181.127 | 92.4459 | 43.4377
38903.6028 | 1368 | 492 | 38903.6028 | 1586 | 550 | 1114.5 | 1204.5 | 83.5165 | 30.0366 | 96.8254 | 33.5775 | 0.83516 | 0.30037 | 0.96825 | 0.33578 | 0.5348 | 0.63248 | 302.1046 | 89.1604 | 46.6922
38903.6029 | 1370 | 503 | 38903.6029 | 1686 | 609 | 1125.5 | 1215.5 | 83.6386 | 30.7082 | 102.9304 | 37.1795 | 0.83639 | 0.30708 | 1.0293 | 0.37179 | 0.5293 | 0.65751 | 1073.3396 | 64.8246 | 37.0916
38903.603 | 1779 | 570 | 38903.603 | 1401 | 490 | 1136.5 | 1226.5 | 108.6081 | 34.7985 | 85.5311 | 29.9145 | 1.0861 | 0.34799 | 0.85531 | 0.29915 | 0.7381 | 0.55617 | 41.3829 | 346.5799 | 0.22057
38903.6031 | 2320 | 65 | 38903.6031 | 2273 | 61 | 1147.5 | 1237.5 | 141.6361 | 3.9683 | 138.7668 | 3.7241 | 1.4164 | 0.039683 | 1.3877 | 0.037241 | 1.3767 | 1.3504 | 8.0531 | 3.3942 | 1.9
38903.6033 | 1871 | 53 | 38903.6033 | 1867 | 54 | 1158 | 1248 | 114.2247 | 3.2357 | 113.9805 | 3.2967 | 1.1422 | 0.032357 | 1.1398 | 0.032967 | 1.1099 | 1.1068 | 29.0748 | 29.5206 | 182.0709
38903.6034 | 1966 | 57 | 38903.6034 | 1925 | 54 | 1168.5 | 1258.5 | 120.0244 | 3.4799 | 117.5214 | 3.2967 | 1.2002 | 0.034799 | 1.1752 | 0.032967 | 1.1654 | 1.1422 | 22.5832 | 25.883 | 117.0109
38903.6035 | 2004 | 61 | 38903.6035 | 1873 | 63 | 1179.5 | 1269.5 | 122.3443 | 3.7241 | 114.3468 | 3.8462 | 1.2234 | 0.037241 | 1.1435 | 0.038462 | 1.1862 | 1.105 | 19.604 | 31.8667 | 111.8681
38903.6036 | 2331 | 73 | 38903.6036 | 1914 | 56 | 1190.5 | 1280.5 | 142.3077 | 4.4567 | 116.8498 | 3.4188 | 1.4231 | 0.044567 | 1.1685 | 0.034188 | 1.3785 | 1.1343 | 0.35718 | 3.1358 | 2.3582
38903.6038 | 2041 | 68 | 38903.6038 | 1841 | 64 | 1201.5 | 1291.5 | 124.6032 | 4.1514 | 112.3932 | 3.9072 | 1.246 | 0.041514 | 1.1239 | 0.039072 | 1.2045 | 1.0849 | 17.1696 | 36.0606 | 92.9097
38903.6039 | 2125 | 90 | 38903.6039 | 2223 | 96 | 1212 | 1302 | 129.7314 | 5.4945 | 135.7143 | 5.8608 | 1.2973 | 0.054945 | 1.3571 | 0.058608 | 1.2424 | 1.2985 | 30.8343 | 6.8504 | 9.4302
38903.604 | 2060 | 90 | 38903.604 | 2041 | 88 | 1222.5 | 1312.5 | 125.7631 | 5.4945 | 124.6032 | 5.3724 | 1.2576 | 0.054945 | 1.246 | 0.053724 | 1.2027 | 1.1923 | 18.7302 | 20.6571 | 37.5472
38903.6041 | 1931 | 90 | 38903.6041 | 2179 | 104 | 1233.5 | 1323.5 | 117.8877 | 5.4945 | 133.0281 | 6.3492 | 1.1789 | 0.054945 | 1.3303 | 0.063492 | 1.1239 | 1.2668 | 49.2951 | 9.0331 | 30.0442
38903.6043 | 1900 | 95 | 38903.6043 | 2132 | 109 | 1244.5 | 1334.5 | 115.9951 | 5.7998 | 130.1587 | 6.6545 | 1.16 | 0.057998 | 1.3016 | 0.066545 | 1.102 | 1.235 | 43.7499 | 12.1419 | 40.1612
38903.6044 | 2024 | 101 | 38903.6044 | 2256 | 112 | 1255.5 | 1345.5 | 123.5653 | 6.1661 | 137.7289 | 6.8376 | 1.2357 | 0.061661 | 1.3773 | 0.068376 | 1.174 | 1.3089 | 44.6799 | 8.4221 | 17.1031
38903.6045 | 1932 | 96 | 38903.6045 | 1834 | 91 | 1266 | 1356 | 117.9487 | 5.8608 | 111.9658 | 5.5556 | 1.1795 | 0.058608 | 1.1197 | 0.055556 | 1.1209 | 1.0641 | 26.3805 | 36.7212 | 89.3547
38903.6046 | 2019 | 108 | 38903.6046 | 1772 | 97 | 1276.5 | 1366.5 | 123.2601 | 6.5934 | 108.1807 | 5.9219 | 1.2326 | 0.065934 | 1.0818 | 0.059219 | 1.1667 | 1.0226 | 19.4271 | 48.9395 | 67.0499
38903.6048 | 1887 | 110 | 38903.6048 | 2108 | 121 | 1287.5 | 1377.5 | 115.2015 | 6.7155 | 128.6935 | 7.3871 | 1.152 | 0.067155 | 1.2869 | 0.073871 | 1.0849 | 1.2131 | 46.8529 | 13.847 | 38.742
38903.6049 | 2206 | 138 | 38903.6049 | 2206 | 141 | 1298.5 | 1388.5 | 134.6764 | 8.4249 | 134.6764 | 8.6081 | 1.3468 | 0.084249 | 1.3468 | 0.086081 | 1.2625 | 1.2607 | 7.1626 | 146.6144 | 1.4561
38903.605 | 1799 | 152 | 38903.605 | 1691 | 156 | 1309.5 | 1399.5 | 109.8291 | 9.2796 | 103.2357 | 9.5238 | 1.0983 | 0.092796 | 1.0324 | 0.095238 | 1.0055 | 0.93712 | 39.6625 | 57.4924 | 95.1961
38903.6051 | 1908 | 104 | 38903.6051 | 1950 | 103 | 1320 | 1410 | 116.4835 | 6.3492 | 119.0476 | 6.2882 | 1.1648 | 0.063492 | 1.1905 | 0.062882 | 1.1013 | 1.1276 | 31.2297 | 26.1919 | 66.9329
38903.6053 | 1763 | 76 | 38903.6053 | 2079 | 88 | 1330.5 | 1420.5 | 107.6313 | 4.6398 | 126.9231 | 5.3724 | 1.0763 | 0.046398 | 1.2692 | 0.053724 | 1.0299 | 1.2155 | 49.81 | 14.7922 | 86.1979
38903.6054 | 2037 | 95 | 38903.6054 | 1817 | 89 | 1341.5 | 1431.5 | 124.359 | 5.7998 | 110.928 | 5.4335 | 1.2436 | 0.057998 | 1.1093 | 0.054335 | 1.1856 | 1.0549 | 18.0362 | 42.9615 | 68.1305
38903.6055 | 1837 | 80 | 38903.6055 | 1901 | 88 | 1352.5 | 1442.5 | 112.149 | 4.884 | 116.0562 | 5.3724 | 1.1215 | 0.04884 | 1.1606 | 0.053724 | 1.0726 | 1.1068 | 34.5379 | 28.647 | 119.7959
38903.6056 | 2050 | 88 | 38903.6056 | 2254 | 89 | 1363.5 | 1453.5 | 125.1526 | 5.3724 | 137.6068 | 5.4335 | 1.2515 | 0.053724 | 1.3761 | 0.054335 | 1.1978 | 1.3217 | 272.7989 | 4.7491 | 10.7873
| 2178 | 95 | 38903.6058 | 1978 | 97 | 1374 | 1464 | 132.967 | 5.7998 | 120.757 | 5.9219 | 1.3297 | 0.057998 | 1.2076 | 0.059219 | 1.2717 | 1.1484 | 9.0314 | 45.7738 | 24.585
38903.6059 | 2305 | 101 | 38903.6059 | 2256 | 100 | 1384.5 | 1474.5 | 140.7204 | 6.1661 | 137.7289 | 6.105 | 1.4072 | 0.061661 | 1.3773 | 0.06105 | 1.3455 | 1.3162 | 38.0771 | 4.8263 | 2.6722
38903.606 | 1942 | 85 | 38903.606 | 2303 | 102 | 1395.5 | 1485.5 | 118.5592 | 5.1893 | 140.5983 | 6.2271 | 1.1856 | 0.051893 | 1.406 | 0.062271 | 1.1337 | 1.3437 | 8.9048 | 3.1535 | 11.5229
38903.6061 | 2168 | 95 | 38903.6061 | 1861 | 81 | 1406.5 | 1496.5 | 132.3565 | 5.7998 | 113.6142 | 4.9451 | 1.3236 | 0.057998 | 1.1361 | 0.049451 | 1.2656 | 1.0867 | 9.4799 | 52.5499 | 30.5968
38903.6063 | 1987 | 83 | 38903.6063 | 2095 | 93 | 1417.5 | 1507.5 | 121.3065 | 5.0672 | 127.8999 | 5.6777 | 1.2131 | 0.050672 | 1.279 | 0.056777 | 1.1624 | 1.2222 | 26.4767 | 15.2888 | 44.3184
38903.6064 | 1847 | 66 | 38903.6064 | 1923 | 70 | 1428 | 1518 | 112.7595 | 4.0293 | 117.3993 | 4.2735 | 1.1276 | 0.040293 | 1.174 | 0.042735 | 1.0873 | 1.1313 | 32.7899 | 25.8844 | 135.3294
38903.6065 | 2163 | 86 | 38903.6065 | 2257 | 66 | 1438.5 | 1528.5 | 132.0513 | 5.2503 | 137.79 | 4.0293 | 1.3205 | 0.052503 | 1.3779 | 0.040293 | 1.268 | 1.3376 | 1554.7817 | 4.1644 | 4.5734

## C1-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 144.2845 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38903.5889 | 1 | 0 | 38903.5889 | 1 | 0 | -85.5 | 4.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.589 | 1 | 0 | 38903.589 | 1 | 0 | -74.5 | 15.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5891 | 1 | 0 | 38903.5891 | 1 | 0 | -64.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5892 | 1 | 0 | 38903.5892 | 1 | 0 | -53.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5894 | 1 | 0 | 38903.5894 | 1 | 0 | -42.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5895 | 1 | 0 | 38903.5895 | 1 | 0 | -31.5 | 58.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5896 | 1 | 0 | 38903.5896 | 1 | 0 | -20.5 | 69.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5897 | 1 | 0 | 38903.5897 | 1 | 0 | -10 | 80 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5899 | 1 | 0 | 38903.5899 | 1 | 0 | 0.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.59 | 1 | 0 | 38903.59 | 1 | 0 | 11.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5901 | 1 | 0 | 38903.5901 | 1 | 0 | 22.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5902 | 1 | 0 | 38903.5903 | 1 | 0 | 33.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5904 | 1 | 0 | 38903.5904 | 1 | 0 | 44 | 134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5905 | 1 | 0 | 38903.5905 | 1 | 0 | 54.5 | 144.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5906 | 1 | 0 | 38903.5906 | 1 | 0 | 65.5 | 155.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5907 | 1 | 0 | 38903.5908 | 1 | 0 | 76.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5909 | 2 | 0 | 38903.5909 | 1 | 0 | 87.5 | 177.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118069 | 236238 | 118068.9988
38903.591 | 1 | 0 | 38903.591 | 1 | 0 | 98 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5911 | 1 | 0 | 38903.5911 | 1 | 0 | 108.5 | 198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5912 | 1 | 0 | 38903.5912 | 1 | 0 | 119.5 | 209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5914 | 1 | 0 | 38903.5914 | 1 | 0 | 130.5 | 220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5915 | 1 | 0 | 38903.5915 | 1 | 0 | 141.5 | 231.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5916 | 1 | 0 | 38903.5916 | 1 | 0 | 152 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5917 | 1 | 0 | 38903.5917 | 1 | 0 | 162.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5919 | 1 | 0 | 38903.5919 | 2 | 0 | 173.5 | 263.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 236238 | 118069 | 236237.9994
38903.592 | 1 | 0 | 38903.592 | 1 | 0 | 184.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5921 | 1 | 0 | 38903.5921 | 1 | 0 | 195.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5922 | 1 | 0 | 38903.5922 | 1 | 0 | 206 | 296 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5924 | 1 | 0 | 38903.5924 | 1 | 0 | 216.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5925 | 1 | 0 | 38903.5925 | 1 | 0 | 227.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5926 | 1 | 0 | 38903.5926 | 1 | 0 | 238.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5927 | 1 | 0 | 38903.5928 | 1 | 0 | 249.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5929 | 2 | 0 | 38903.5929 | 1 | 0 | 259.5 | 349.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 118069 | 236238 | 118068.9988
38903.593 | 1 | 0 | 38903.593 | 1 | 0 | 270.5 | 360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5931 | 1 | 0 | 38903.5931 | 2 | 0 | 281.5 | 371.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 236238 | 118069 | 236237.9994
38903.5932 | 1 | 0 | 38903.5933 | 1 | 0 | 292.5 | 382.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5934 | 1 | 0 | 38903.5934 | 1 | 0 | 303.5 | 393.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5935 | 1 | 0 | 38903.5935 | 1 | 0 | 313.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5936 | 1 | 0 | 38903.5936 | 1 | 0 | 324.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5937 | 1 | 0 | 38903.5938 | 1 | 0 | 335.5 | 425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5939 | 1 | 0 | 38903.5939 | 1 | 0 | 346.5 | 436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.594 | 1 | 0 | 38903.594 | 1 | 0 | 357.5 | 447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5941 | 1 | 0 | 38903.5941 | 1 | 0 | 367.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5942 | 1 | 0 | 38903.5942 | 1 | 0 | 378.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5944 | 1 | 0 | 38903.5944 | 1 | 0 | 389.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5945 | 1 | 0 | 38903.5945 | 1 | 0 | 400.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5946 | 1 | 0 | 38903.5946 | 1 | 0 | 411 | 501 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5947 | 1 | 0 | 38903.5947 | 1 | 0 | 421.5 | 511.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5949 | 1 | 0 | 38903.5949 | 1 | 0 | 432.5 | 522.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.595 | 1 | 0 | 38903.595 | 1 | 0 | 443.5 | 533.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5951 | 1 | 0 | 38903.5951 | 1 | 0 | 454.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5952 | 1 | 0 | 38903.5953 | 1 | 0 | 465.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5954 | 1 | 0 | 38903.5954 | 1 | 0 | 475.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5955 | 1 | 0 | 38903.5955 | 1 | 0 | 486.5 | 576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5956 | 1 | 0 | 38903.5956 | 1 | 0 | 497.5 | 587.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5957 | 1 | 0 | 38903.5958 | 1 | 0 | 508.5 | 598.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5959 | 1 | 0 | 38903.5959 | 1 | 0 | 519 | 609 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.596 | 1 | 0 | 38903.596 | 1 | 0 | 529.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5961 | 1 | 0 | 38903.5961 | 1 | 0 | 540.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5962 | 1 | 0 | 38903.5963 | 1 | 0 | 551.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5964 | 1 | 0 | 38903.5964 | 1 | 0 | 562.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5965 | 1 | 0 | 38903.5965 | 1 | 0 | 573 | 663 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5966 | 1 | 0 | 38903.5966 | 1 | 0 | 583.5 | 673.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5967 | 1 | 0 | 38903.5967 | 1 | 0 | 594.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5969 | 2 | 0 | 38903.5969 | 2 | 0 | 605.5 | 695.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 118069 | 118069 | 118068.9988
38903.597 | 1 | 0 | 38903.597 | 1 | 0 | 616.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5971 | 1 | 0 | 38903.5971 | 1 | 0 | 627.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5972 | 1 | 0 | 38903.5972 | 1 | 0 | 637.5 | 727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5974 | 1 | 0 | 38903.5974 | 1 | 0 | 648.5 | 738.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5975 | 1 | 0 | 38903.5975 | 1 | 0 | 659.5 | 749.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5976 | 1 | 0 | 38903.5976 | 1 | 0 | 670.5 | 760.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5977 | 1 | 0 | 38903.5978 | 1 | 0 | 681.5 | 771.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5979 | 1 | 0 | 38903.5979 | 1 | 0 | 691.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.598 | 1 | 0 | 38903.598 | 1 | 0 | 702.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5981 | 1 | 0 | 38903.5981 | 1 | 0 | 713.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5982 | 1 | 0 | 38903.5983 | 1 | 0 | 724.5 | 814.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5984 | 1 | 0 | 38903.5984 | 1 | 0 | 735.5 | 825.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5985 | 1 | 0 | 38903.5985 | 1 | 0 | 745.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5986 | 1 | 0 | 38903.5986 | 1 | 0 | 756.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236238 | 236238 | 236237.9994
38903.5987 | 15 | 0 | 38903.5987 | 26 | 0 | 767.5 | 857.5 | 0.91575 | 0 | 1.5873 | 0 | 0.0091575 | 0 | 0.015873 | 0 | 0.0091575 | 0.015873 | 15655.8667 | 8989.9231 | 15655.8575
38903.5989 | 147 | 78 | 38903.5989 | 210 | 81 | 778.5 | 868.5 | 8.9744 | 4.7619 | 12.8205 | 4.9451 | 0.089744 | 0.047619 | 0.12821 | 0.049451 | 0.042125 | 0.078755 | 3440.9099 | 1700.3146 | 2589.2332
38903.599 | 347 | 249 | 38903.599 | 389 | 186 | 789.5 | 879.5 | 21.1844 | 15.2015 | 23.7485 | 11.3553 | 0.21184 | 0.15201 | 0.23748 | 0.11355 | 0.059829 | 0.12393 | 2752.7107 | 1006.0893 | 645.6199
38903.5991 | 993 | 819 | 38903.5991 | 554 | 314 | 799.5 | 889.5 | 60.6227 | 50 | 33.8217 | 19.1697 | 0.60623 | 0.5 | 0.33822 | 0.1917 | 0.10623 | 0.14652 | 1879.033 | 810.33 | 59.9281
38903.5992 | 717 | 552 | 38903.5992 | 672 | 427 | 810.5 | 900.5 | 43.7729 | 33.6996 | 41.0256 | 26.0684 | 0.43773 | 0.337 | 0.41026 | 0.26068 | 0.10073 | 0.14957 | 1772.1016 | 765.6618 | 175.3549
38903.5994 | 676 | 567 | 38903.5994 | 1145 | 906 | 821.5 | 911.5 | 41.2698 | 34.6154 | 69.9023 | 55.3114 | 0.4127 | 0.34615 | 0.69902 | 0.55311 | 0.066545 | 0.14591 | 56915.3907 | 534.7277 | 166.4668
38903.5995 | 569 | 434 | 38903.5995 | 577 | 358 | 832.5 | 922.5 | 34.7375 | 26.4957 | 35.2259 | 21.8559 | 0.34737 | 0.26496 | 0.35226 | 0.21856 | 0.082418 | 0.1337 | 2087.4423 | 885.0045 | 281.6293
38903.5996 | 918 | 688 | 38903.5996 | 1135 | 875 | 843 | 933 | 56.044 | 42.0024 | 69.2918 | 53.4188 | 0.56044 | 0.42002 | 0.69292 | 0.53419 | 0.14042 | 0.15873 | 1132.1807 | 672.291 | 95.8301
38903.5997 | 772 | 647 | 38903.5997 | 881 | 583 | 853.5 | 943.5 | 47.1306 | 39.4994 | 53.7851 | 35.5922 | 0.47131 | 0.39499 | 0.53785 | 0.35592 | 0.076313 | 0.18193 | 26394.4714 | 543.831 | 123.2919
38903.5999 | 729 | 509 | 38903.5999 | 798 | 557 | 864.5 | 954.5 | 44.5055 | 31.0745 | 48.7179 | 34.0049 | 0.44505 | 0.31074 | 0.48718 | 0.34005 | 0.13431 | 0.14713 | 1026.0546 | 838.3821 | 197.5348
38903.6 | 1206 | 921 | 38903.6 | 1119 | 838 | 875.5 | 965.5 | 73.6264 | 56.2271 | 68.315 | 51.16 | 0.73626 | 0.56227 | 0.68315 | 0.5116 | 0.17399 | 0.17155 | 697.3827 | 773.6929 | 22.728
38903.6001 | 1168 | 882 | 38903.6001 | 1034 | 788 | 886.5 | 976.5 | 71.3065 | 53.8462 | 63.1258 | 48.1074 | 0.71306 | 0.53846 | 0.63126 | 0.48107 | 0.1746 | 0.15018 | 547.7514 | 1301.5387 | 32.9955
38903.6002 | 1205 | 899 | 38903.6002 | 1335 | 1014 | 897 | 987 | 73.5653 | 54.884 | 81.5018 | 61.9048 | 0.73565 | 0.54884 | 0.81502 | 0.61905 | 0.18681 | 0.19597 | 1071.3113 | 454.3325 | 23.6472
38903.6004 | 1355 | 1028 | 38903.6004 | 1301 | 962 | 907.5 | 997.5 | 82.7228 | 62.7595 | 79.4261 | 58.7302 | 0.82723 | 0.62759 | 0.79426 | 0.5873 | 0.19963 | 0.20696 | 7528.914 | 327.7993 | 1.4624
38903.6005 | 1235 | 890 | 38903.6005 | 1205 | 776 | 918.5 | 1008.5 | 75.3968 | 54.3346 | 73.5653 | 47.3748 | 0.75397 | 0.54335 | 0.73565 | 0.47375 | 0.21062 | 0.2619 | 3457.1778 | 284.9265 | 19.826
38903.6006 | 1353 | 958 | 38903.6006 | 1099 | 758 | 929.5 | 1019.5 | 82.6007 | 58.486 | 67.094 | 46.2759 | 0.82601 | 0.58486 | 0.67094 | 0.46276 | 0.24115 | 0.20818 | 319.1511 | 1221.6827 | 5.054
38903.6007 | 1180 | 856 | 38903.6008 | 1247 | 846 | 940.5 | 1030.5 | 72.0391 | 52.2589 | 76.1294 | 51.6484 | 0.72039 | 0.52259 | 0.76129 | 0.51648 | 0.1978 | 0.24481 | 3235.1736 | 297.8205 | 28.6316
38903.6009 | 1286 | 907 | 38903.6009 | 1215 | 888 | 951 | 1041 | 78.5104 | 55.3724 | 74.1758 | 54.2125 | 0.7851 | 0.55372 | 0.74176 | 0.54212 | 0.23138 | 0.19963 | 311.4569 | 2741.5308 | 18.1239
38903.601 | 1256 | 745 | 38903.601 | 1445 | 859 | 961.5 | 1051.5 | 76.6789 | 45.4823 | 88.2173 | 52.442 | 0.76679 | 0.45482 | 0.88217 | 0.52442 | 0.31197 | 0.35775 | 1152.2479 | 179.564 | 31.2425
38903.6011 | 1229 | 680 | 38903.6011 | 1425 | 790 | 972.5 | 1062.5 | 75.0305 | 41.514 | 86.9963 | 48.2295 | 0.75031 | 0.41514 | 0.86996 | 0.4823 | 0.33516 | 0.38767 | 632.4524 | 183.9638 | 43.2892
38903.6012 | 1281 | 676 | 38903.6012 | 1354 | 709 | 983.5 | 1073.5 | 78.2051 | 41.2698 | 82.6618 | 43.2845 | 0.78205 | 0.4127 | 0.82662 | 0.43284 | 0.36935 | 0.39377 | 351.1203 | 227.8125 | 41.777
38903.6014 | 1372 | 738 | 38903.6014 | 1414 | 801 | 994.5 | 1084.5 | 83.7607 | 45.0549 | 86.3248 | 48.9011 | 0.83761 | 0.45055 | 0.86325 | 0.48901 | 0.38706 | 0.37424 | 234.1325 | 350.4721 | 26.7117
38903.6015 | 1889 | 445 | 38903.6015 | 1655 | 391 | 1005 | 1095 | 115.3236 | 27.1673 | 101.0379 | 23.8706 | 1.1532 | 0.27167 | 1.0104 | 0.23871 | 0.88156 | 0.77167 | 35.1953 | 462.8265 | 5.4292
38903.6016 | 1428 | 531 | 38903.6016 | 1400 | 439 | 1015.5 | 1105.5 | 87.1795 | 32.4176 | 85.4701 | 26.801 | 0.87179 | 0.32418 | 0.8547 | 0.26801 | 0.54762 | 0.58669 | 188.7797 | 132.25 | 43.3646
38903.6017 | 1398 | 667 | 38903.6017 | 1454 | 579 | 1026.5 | 1116.5 | 85.348 | 40.7204 | 88.7668 | 35.348 | 0.85348 | 0.4072 | 0.88767 | 0.35348 | 0.44628 | 0.53419 | 606.0563 | 116.6673 | 24.0879
38903.6019 | 1420 | 833 | 38903.6019 | 1208 | 705 | 1037.5 | 1127.5 | 86.6911 | 50.8547 | 73.7485 | 43.0403 | 0.86691 | 0.50855 | 0.73748 | 0.4304 | 0.35836 | 0.30708 | 193.9351 | 828.3698 | 11.8236
38903.602 | 1199 | 701 | 38903.602 | 1473 | 917 | 1048.5 | 1138.5 | 73.199 | 42.7961 | 89.9267 | 55.9829 | 0.73199 | 0.42796 | 0.89927 | 0.55983 | 0.30403 | 0.33944 | 734.2029 | 206.5355 | 44.5383
38903.6021 | 1856 | 540 | 38903.6021 | 1751 | 465 | 1059 | 1149 | 113.3089 | 32.967 | 106.8987 | 28.3883 | 1.1331 | 0.32967 | 1.069 | 0.28388 | 0.80342 | 0.7851 | 53.4843 | 146.9997 | 3.5951
38903.6022 | 1449 | 392 | 38903.6022 | 1650 | 444 | 1069.5 | 1159.5 | 88.4615 | 23.9316 | 100.7326 | 27.1062 | 0.88462 | 0.23932 | 1.0073 | 0.27106 | 0.6453 | 0.73626 | 170.0207 | 75.5015 | 57.3291
38903.6024 | 1767 | 591 | 38903.6024 | 1388 | 521 | 1080.5 | 1170.5 | 107.8755 | 36.0806 | 84.7375 | 31.8071 | 1.0788 | 0.36081 | 0.84737 | 0.31807 | 0.71795 | 0.5293 | 43.1397 | 286.2837 | 0.67466
38903.6025 | 1972 | 415 | 38903.6025 | 1500 | 354 | 1091.5 | 1181.5 | 120.3907 | 25.3358 | 91.5751 | 21.6117 | 1.2039 | 0.25336 | 0.91575 | 0.21612 | 0.95055 | 0.69963 | 21.987 | 186.057 | 3.7019
38903.6026 | 1803 | 541 | 38903.6026 | 1588 | 558 | 1102.5 | 1192.5 | 110.0733 | 33.0281 | 96.9475 | 34.0659 | 1.1007 | 0.33028 | 0.96947 | 0.34066 | 0.77045 | 0.62882 | 31.481 | 104.4289 | 1.8299
38903.6027 | 1492 | 603 | 38903.6027 | 1691 | 650 | 1113 | 1203 | 91.0867 | 36.8132 | 103.2357 | 39.6825 | 0.91087 | 0.36813 | 1.0324 | 0.39683 | 0.54274 | 0.63553 | 646.9871 | 79.9398 | 19.7728
38903.6029 | 1471 | 524 | 38903.6029 | 1723 | 624 | 1123.5 | 1213.5 | 89.8046 | 31.9902 | 105.1893 | 38.0952 | 0.89805 | 0.3199 | 1.0519 | 0.38095 | 0.57814 | 0.67094 | 799.9196 | 62.7213 | 27.0979
38903.603 | 1849 | 583 | 38903.603 | 1599 | 655 | 1134.5 | 1224.5 | 112.8816 | 35.5922 | 97.619 | 39.9878 | 1.1288 | 0.35592 | 0.97619 | 0.39988 | 0.77289 | 0.57631 | 2.7116 | 3.2931 | 0.37524
38903.6031 | 1800 | 54 | 38903.6031 | 2340 | 57 | 1145.5 | 1235.5 | 109.8901 | 3.2967 | 142.8571 | 3.4799 | 1.0989 | 0.032967 | 1.4286 | 0.034799 | 1.0659 | 1.3938 | 12.2408 | 1.8904 | 17.5016
38903.6032 | 2154 | 55 | 38903.6033 | 2088 | 65 | 1156.5 | 1246.5 | 131.5018 | 3.3578 | 127.4725 | 3.9683 | 1.315 | 0.033578 | 1.2747 | 0.039683 | 1.2814 | 1.235 | 11.5872 | 18.8354 | 44.4895
38903.6034 | 2347 | 71 | 38903.6034 | 1845 | 56 | 1166.5 | 1256.5 | 143.2845 | 4.3346 | 112.6374 | 3.4188 | 1.4328 | 0.043346 | 1.1264 | 0.034188 | 1.3895 | 1.0922 | 0.42886 | 4.6001 | 3.3832
38903.6035 | 1936 | 57 | 38903.6035 | 1791 | 60 | 1177.5 | 1267.5 | 118.1929 | 3.4799 | 109.3407 | 3.663 | 1.1819 | 0.034799 | 1.0934 | 0.03663 | 1.1471 | 1.0568 | 24.6924 | 38.4661 | 180.5127
38903.6036 | 2276 | 71 | 38903.6036 | 1878 | 59 | 1188.5 | 1278.5 | 138.9499 | 4.3346 | 114.652 | 3.602 | 1.3895 | 0.043346 | 1.1465 | 0.03602 | 1.3462 | 1.1105 | 4.0615 | 132.4941 | 13.1474
38903.6037 | 2116 | 65 | 38903.6038 | 2017 | 67 | 1199.5 | 1289.5 | 129.1819 | 3.9683 | 123.138 | 4.0904 | 1.2918 | 0.039683 | 1.2314 | 0.040904 | 1.2521 | 1.1905 | 13.9345 | 23.5764 | 53.5311
38903.6039 | 1943 | 77 | 38903.6039 | 2052 | 92 | 1210.5 | 1300.5 | 118.6203 | 4.7009 | 125.2747 | 5.6166 | 1.1862 | 0.047009 | 1.2527 | 0.056166 | 1.1392 | 1.1966 | 28.7862 | 18.9819 | 71.1449
38903.604 | 2227 | 96 | 38903.604 | 2260 | 99 | 1220.5 | 1310.5 | 135.9585 | 5.8608 | 137.9731 | 6.044 | 1.3596 | 0.058608 | 1.3797 | 0.06044 | 1.301 | 1.3193 | 35.7674 | 5.4866 | 2.1878
38903.6041 | 1951 | 93 | 38903.6041 | 1783 | 89 | 1231.5 | 1321.5 | 119.1087 | 5.6777 | 108.8523 | 5.4335 | 1.1911 | 0.056777 | 1.0885 | 0.054335 | 1.1343 | 1.0342 | 25.0933 | 43.3338 | 103.8253
38903.6042 | 2072 | 101 | 38903.6042 | 1944 | 104 | 1242.5 | 1332.5 | 126.4957 | 6.1661 | 118.6813 | 6.3492 | 1.265 | 0.061661 | 1.1868 | 0.063492 | 1.2033 | 1.1233 | 17.4317 | 33.7289 | 47.5419
38903.6044 | 2228 | 113 | 38903.6044 | 2021 | 110 | 1253.5 | 1343.5 | 136.0195 | 6.8987 | 123.3822 | 6.7155 | 1.3602 | 0.068987 | 1.2338 | 0.067155 | 1.2912 | 1.1667 | 6.6749 | 130.1607 | 11.2003
38903.6045 | 1969 | 101 | 38903.6045 | 1839 | 96 | 1264.5 | 1354.5 | 120.2076 | 6.1661 | 112.2711 | 5.8608 | 1.2021 | 0.061661 | 1.1227 | 0.058608 | 1.1404 | 1.0641 | 24.5313 | 38.7952 | 81.1918
38903.6046 | 1902 | 103 | 38903.6046 | 1786 | 98 | 1274.5 | 1364.5 | 116.1172 | 6.2882 | 109.0354 | 5.9829 | 1.1612 | 0.062882 | 1.0904 | 0.059829 | 1.0983 | 1.0305 | 29.6352 | 42.5385 | 103.838
38903.6047 | 1788 | 99 | 38903.6047 | 1901 | 105 | 1285.5 | 1375.5 | 109.1575 | 6.044 | 116.0562 | 6.4103 | 1.0916 | 0.06044 | 1.1606 | 0.064103 | 1.0311 | 1.0965 | 42.3853 | 29.8643 | 110.6574
38903.6049 | 1876 | 109 | 38903.6049 | 1912 | 111 | 1296.5 | 1386.5 | 114.5299 | 6.6545 | 116.7277 | 6.7766 | 1.1453 | 0.066545 | 1.1673 | 0.067766 | 1.0788 | 1.0995 | 34.5754 | 30.4994 | 81.1306
38903.605 | 2245 | 121 | 38903.605 | 1792 | 149 | 1307.5 | 1397.5 | 137.0574 | 7.3871 | 109.4017 | 9.0965 | 1.3706 | 0.073871 | 1.094 | 0.090965 | 1.2967 | 1.0031 | 4.8887 | 40.6722 | 0.62604
38903.6051 | 2111 | 112 | 38903.6051 | 2223 | 120 | 1318.5 | 1408.5 | 128.8767 | 6.8376 | 135.7143 | 7.326 | 1.2888 | 0.068376 | 1.3571 | 0.07326 | 1.2204 | 1.2839 | 48.774 | 7.5596 | 8.8092
38903.6052 | 2139 | 130 | 38903.6052 | 1785 | 77 | 1329 | 1419 | 130.5861 | 7.9365 | 108.9744 | 4.7009 | 1.3059 | 0.079365 | 1.0897 | 0.047009 | 1.2265 | 1.0427 | 12.7422 | 52.4034 | 24.9633
38903.6054 | 2026 | 92 | 38903.6054 | 2176 | 106 | 1339.5 | 1429.5 | 123.6874 | 5.6166 | 132.8449 | 6.4713 | 1.2369 | 0.056166 | 1.3284 | 0.064713 | 1.1807 | 1.2637 | 31.0935 | 10.8369 | 26.0779
38903.6055 | 1915 | 86 | 38903.6055 | 2311 | 71 | 1350.5 | 1440.5 | 116.9109 | 5.2503 | 141.0867 | 4.3346 | 1.1691 | 0.052503 | 1.4109 | 0.043346 | 1.1166 | 1.3675 | 17.9478 | 12.8504 | 47.9821
38903.6056 | 2031 | 74 | 38903.6056 | 2209 | 91 | 1361.5 | 1451.5 | 123.9927 | 4.5177 | 134.8596 | 5.5556 | 1.2399 | 0.045177 | 1.3486 | 0.055556 | 1.1947 | 1.293 | 30.6616 | 8.4768 | 27.2848
38903.6057 | 1946 | 96 | 38903.6058 | 2126 | 116 | 1372.5 | 1462.5 | 118.8034 | 5.8608 | 129.7924 | 7.0818 | 1.188 | 0.058608 | 1.2979 | 0.070818 | 1.1294 | 1.2271 | 35.7206 | 14.0857 | 41.3328
38903.6059 | 2298 | 104 | 38903.6059 | 1816 | 82 | 1382.5 | 1472.5 | 140.293 | 6.3492 | 110.8669 | 5.0061 | 1.4029 | 0.063492 | 1.1087 | 0.050061 | 1.3394 | 1.0586 | 2.6709 | 40.968 | 10.792
38903.606 | 1886 | 84 | 38903.606 | 2241 | 104 | 1393.5 | 1483.5 | 115.1404 | 5.1282 | 136.8132 | 6.3492 | 1.1514 | 0.051282 | 1.3681 | 0.063492 | 1.1001 | 1.3046 | 121.1235 | 5.9664 | 26.3682
38903.6061 | 1850 | 105 | 38903.6061 | 1819 | 66 | 1404.5 | 1494.5 | 112.9426 | 6.4103 | 111.0501 | 4.0293 | 1.1294 | 0.064103 | 1.1105 | 0.040293 | 1.0653 | 1.0702 | 35.5858 | 34.7285 | 100.2539
38903.6062 | 2342 | 72 | 38903.6062 | 1839 | 62 | 1415.5 | 1505.5 | 142.9792 | 4.3956 | 112.2711 | 3.7851 | 1.4298 | 0.043956 | 1.1227 | 0.037851 | 1.3858 | 1.0849 | 0.6351 | 6.5668 | 4.3323
38903.6064 | 2139 | 71 | 38903.6064 | 2240 | 82 | 1426.5 | 1516.5 | 130.5861 | 4.3346 | 136.7521 | 5.0061 | 1.3059 | 0.043346 | 1.3675 | 0.050061 | 1.2625 | 1.3175 | 21.4477 | 6.9483 | 14.0352
38903.6065 | 2307 | 78 | 38903.6065 | 1823 | 77 | 1436.5 | 1526.5 | 140.8425 | 4.7619 | 111.2943 | 4.7009 | 1.4084 | 0.047619 | 1.1129 | 0.047009 | 1.3608 | 1.0659 | 2.2896 | 33.4191 | 6.9429

## C1-3
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 143.4298 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38903.5888 | 1 | 0 | 38903.5889 | 1 | 0 | -87.5 | 2.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.589 | 1 | 0 | 38903.589 | 1 | 0 | -76.5 | 13.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5891 | 1 | 0 | 38903.5891 | 1 | 0 | -65.5 | 24.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5892 | 1 | 0 | 38903.5892 | 1 | 0 | -55.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5893 | 1 | 0 | 38903.5894 | 1 | 0 | -44.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5895 | 1 | 0 | 38903.5895 | 1 | 0 | -33.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5896 | 1 | 0 | 38903.5896 | 1 | 0 | -22.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5897 | 1 | 0 | 38903.5897 | 1 | 0 | -11.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5898 | 1 | 0 | 38903.5898 | 1 | 0 | -1.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.59 | 1 | 0 | 38903.59 | 1 | 0 | 9.5 | 99.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5901 | 1 | 0 | 38903.5901 | 1 | 0 | 20.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5902 | 1 | 0 | 38903.5902 | 1 | 0 | 31.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5903 | 1 | 0 | 38903.5904 | 1 | 0 | 42.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5905 | 1 | 0 |  | 1 | 0 | 53 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5906 | 1 | 0 | 38903.5906 | 1 | 0 | 63.5 | 153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5907 | 1 | 0 | 38903.5907 | 1 | 0 | 74.5 | 164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5908 | 2 | 0 | 38903.5909 | 1 | 0 | 85.5 | 175.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117369 | 234838 | 117368.9988
38903.591 | 1 | 0 | 38903.591 | 1 | 0 | 96.5 | 186.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5911 | 1 | 0 | 38903.5911 | 1 | 0 | 107 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5912 | 1 | 0 | 38903.5912 | 1 | 0 | 117.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5913 | 1 | 0 | 38903.5914 | 1 | 0 | 128.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5915 | 1 | 0 | 38903.5915 | 1 | 0 | 139.5 | 229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5916 | 1 | 0 | 38903.5916 | 1 | 0 | 150.5 | 240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5917 | 1 | 0 | 38903.5917 | 1 | 0 | 161 | 251 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5918 | 1 | 0 | 38903.5919 | 1 | 0 | 171.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.592 | 2 | 0 | 38903.592 | 1 | 0 | 182.5 | 272.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117369 | 234838 | 117368.9988
38903.5921 | 1 | 0 | 38903.5921 | 2 | 0 | 193.5 | 283.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 234838 | 117369 | 234837.9994
38903.5922 | 1 | 0 | 38903.5922 | 1 | 0 | 204.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5923 | 1 | 0 | 38903.5923 | 1 | 0 | 215 | 305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5925 | 2 | 0 | 38903.5925 | 1 | 0 | 225.5 | 315.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117369 | 234838 | 117368.9988
38903.5926 | 1 | 0 | 38903.5926 | 1 | 0 | 236.5 | 326.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5927 | 1 | 0 | 38903.5927 | 1 | 0 | 247.5 | 337.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5928 | 1 | 0 | 38903.5929 | 1 | 0 | 258.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.593 | 1 | 0 | 38903.593 | 1 | 0 | 268.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5931 | 1 | 0 | 38903.5931 | 1 | 0 | 279.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5932 | 1 | 0 | 38903.5932 | 1 | 0 | 290.5 | 380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5933 | 1 | 0 | 38903.5934 | 1 | 0 | 301.5 | 391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5935 | 1 | 0 | 38903.5935 | 1 | 0 | 312.5 | 402.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5936 | 1 | 0 | 38903.5936 | 2 | 0 | 322.5 | 412.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 234838 | 117369 | 234837.9994
38903.5937 | 1 | 0 | 38903.5937 | 1 | 0 | 333.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5938 | 1 | 0 | 38903.5939 | 1 | 0 | 344.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.594 | 1 | 0 | 38903.594 | 1 | 0 | 355.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5941 | 1 | 0 | 38903.5941 | 1 | 0 | 366.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5942 | 1 | 0 | 38903.5942 | 1 | 0 | 376.5 | 466.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5943 | 1 | 0 | 38903.5944 | 1 | 0 | 387.5 | 477.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5945 | 1 | 0 | 38903.5945 | 1 | 0 | 398.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5946 | 1 | 0 | 38903.5946 | 1 | 0 | 409.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5947 | 1 | 0 | 38903.5947 | 1 | 0 | 420.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5948 | 1 | 0 | 38903.5948 | 1 | 0 | 430.5 | 520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.595 | 1 | 0 | 38903.595 | 1 | 0 | 441.5 | 531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5951 | 1 | 0 | 38903.5951 | 1 | 0 | 452.5 | 542.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5952 | 1 | 0 | 38903.5952 | 1 | 0 | 463.5 | 553.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5953 | 2 | 0 | 38903.5954 | 1 | 0 | 474.5 | 564.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 117369 | 234838 | 117368.9988
38903.5955 | 1 | 0 | 38903.5955 | 1 | 0 | 484.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5956 | 1 | 0 | 38903.5956 | 1 | 0 | 495.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5957 | 1 | 0 | 38903.5957 | 1 | 0 | 506.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5958 | 1 | 0 | 38903.5959 | 1 | 0 | 517.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.596 | 1 | 0 | 38903.596 | 1 | 0 | 528 | 618 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5961 | 1 | 0 | 38903.5961 | 1 | 0 | 538.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5962 | 1 | 0 | 38903.5962 | 1 | 0 | 549.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5963 | 1 | 0 | 38903.5964 | 1 | 0 | 560.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5965 | 1 | 0 | 38903.5965 | 1 | 0 | 571.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5966 | 1 | 0 | 38903.5966 | 1 | 0 | 582.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5967 | 1 | 0 | 38903.5967 | 1 | 0 | 592.5 | 682.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5968 | 1 | 0 | 38903.5969 | 1 | 0 | 603.5 | 693.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.597 | 1 | 0 | 38903.597 | 2 | 0 | 614.5 | 704.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 234838 | 117369 | 234837.9994
38903.5971 | 1 | 0 | 38903.5971 | 1 | 0 | 625.5 | 715.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5972 | 1 | 1 | 38903.5972 | 1 | 0 | 636.5 | 726.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 551488862.44 | 234838 | 234638.0851
38903.5973 | 1 | 0 | 38903.5973 | 1 | 0 | 646.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5975 | 1 | 0 | 38903.5975 | 1 | 0 | 657.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5976 | 1 | 0 | 38903.5976 | 1 | 0 | 668.5 | 758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5977 | 1 | 0 | 38903.5977 | 1 | 0 | 679.5 | 769.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5978 | 1 | 0 | 38903.5979 | 1 | 0 | 690.5 | 780.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.598 | 1 | 0 | 38903.598 | 1 | 0 | 700.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5981 | 1 | 0 | 38903.5981 | 1 | 0 | 711.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5982 | 1 | 0 | 38903.5982 | 1 | 0 | 722.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5983 | 1 | 0 | 38903.5984 | 1 | 0 | 733.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5985 | 1 | 0 | 38903.5985 | 1 | 0 | 744 | 834 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5986 | 1 | 0 | 38903.5986 | 1 | 0 | 754.5 | 844.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5987 | 1 | 0 | 38903.5987 | 1 | 0 | 765.5 | 855.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234838 | 234838 | 234837.9994
38903.5988 | 11 | 0 | 38903.5989 | 1 | 0 | 776.5 | 866.5 | 0.67155 | 0 | 0.06105 | 0 | 0.0067155 | 0 | 0.0006105 | 0 | 0.0067155 | 0.0006105 | 21258 | 234838 | 21257.9933
38903.599 | 50 | 0 | 38903.599 | 1 | 0 | 787.5 | 877.5 | 3.0525 | 0 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.030525 | 0.0006105 | 4598.76 | 234838 | 4598.7295
38903.5991 | 96 | 0 | 38903.5991 | 2 | 0 | 798 | 888 | 5.8608 | 0 | 0.1221 | 0 | 0.058608 | 0 | 0.001221 | 0 | 0.058608 | 0.001221 | 2347.2708 | 117369 | 2347.2122
38903.5992 | 397 | 116 | 38903.5992 | 202 | 118 | 808.5 | 898.5 | 24.2369 | 7.0818 | 12.3321 | 7.2039 | 0.24237 | 0.070818 | 0.12332 | 0.072039 | 0.17155 | 0.051282 | 703.8953 | 3193.7882 | 1535.0234
38903.5993 | 463 | 173 | 38903.5994 | 235 | 151 | 819.5 | 909.5 | 28.2662 | 10.5617 | 14.3468 | 9.2186 | 0.28266 | 0.10562 | 0.14347 | 0.092186 | 0.17705 | 0.051282 | 661.9025 | 3455.6049 | 962.5386
38903.5995 | 536 | 264 | 38903.5995 | 445 | 257 | 830.5 | 920.5 | 32.7228 | 16.1172 | 27.1673 | 15.6899 | 0.32723 | 0.16117 | 0.27167 | 0.1569 | 0.16606 | 0.11477 | 722.8459 | 1249.2154 | 543.388
38903.5996 | 668 | 387 | 38903.5996 | 514 | 372 | 841.5 | 931.5 | 40.7814 | 23.6264 | 31.3797 | 22.7106 | 0.40781 | 0.23626 | 0.3138 | 0.22711 | 0.17155 | 0.086691 | 638.4734 | 2191.8644 | 319.8715
38903.5997 | 556 | 300 | 38903.5997 | 452 | 305 | 852 | 942 | 33.9438 | 18.315 | 27.5946 | 18.6203 | 0.33944 | 0.18315 | 0.27595 | 0.1862 | 0.15629 | 0.089744 | 749.7744 | 1784.5753 | 471.3792
38903.5998 | 664 | 446 | 38903.5998 | 786 | 553 | 862.5 | 952.5 | 40.5372 | 27.2283 | 47.9853 | 33.7607 | 0.40537 | 0.27228 | 0.47985 | 0.33761 | 0.13309 | 0.14225 | 1008.1313 | 877.5834 | 249.4619
38903.6 | 1033 | 909 | 38903.6 | 1148 | 866 | 873.5 | 963.5 | 63.0647 | 55.4945 | 70.0855 | 52.8694 | 0.63065 | 0.55495 | 0.70085 | 0.52869 | 0.075702 | 0.17216 | 739.7799 | 1685.1398 | 42.3058
38903.6001 | 1330 | 1052 | 38903.6001 | 1088 | 813 | 884.5 | 974.5 | 81.1966 | 64.2247 | 66.4225 | 49.6337 | 0.81197 | 0.64225 | 0.66422 | 0.49634 | 0.16972 | 0.16789 | 701.6363 | 792.6826 | 2.7534
38903.6002 | 1302 | 992 | 38903.6002 | 1042 | 773 | 895.5 | 985.5 | 79.4872 | 60.5617 | 63.6142 | 47.1917 | 0.79487 | 0.60562 | 0.63614 | 0.47192 | 0.18926 | 0.16422 | 435.2128 | 1430.6174 | 5.2179
38903.6003 | 1097 | 799 | 38903.6003 | 1201 | 885 | 906 | 996 | 66.9719 | 48.779 | 73.3211 | 54.0293 | 0.66972 | 0.48779 | 0.73321 | 0.54029 | 0.18193 | 0.19292 | 814.7406 | 553.7658 | 48.064
38903.6005 | 1358 | 967 | 38903.6005 | 1161 | 829 | 916.5 | 1006.5 | 82.906 | 59.0354 | 70.8791 | 50.6105 | 0.82906 | 0.59035 | 0.70879 | 0.50611 | 0.23871 | 0.20269 | 262.1589 | 7531.1285 | 2.4882
38903.6006 | 1092 | 761 | 38903.6006 | 1168 | 813 | 927.5 | 1017.5 | 66.6667 | 46.4591 | 71.3065 | 49.6337 | 0.66667 | 0.46459 | 0.71306 | 0.49634 | 0.20208 | 0.21673 | 717.0233 | 488.9523 | 54.1522
38903.6007 | 1146 | 775 | 38903.6007 | 1376 | 984 | 938.5 | 1028.5 | 69.9634 | 47.3138 | 84.0049 | 60.0733 | 0.69963 | 0.47314 | 0.84005 | 0.60073 | 0.2265 | 0.23932 | 713.0454 | 383.2199 | 43.836
38903.6008 | 1200 | 744 | 38903.6009 | 1408 | 932 | 949.5 | 1039.5 | 73.2601 | 45.4212 | 85.9585 | 56.8987 | 0.7326 | 0.45421 | 0.85958 | 0.56899 | 0.27839 | 0.2906 | 517.2631 | 318.2263 | 41.4586
38903.601 | 1442 | 882 | 38903.601 | 1214 | 789 | 960 | 1050 | 88.0342 | 53.8462 | 74.1148 | 48.1685 | 0.88034 | 0.53846 | 0.74115 | 0.48168 | 0.34188 | 0.25946 | 128.1114 | 594.8439 | 2.4634
38903.6011 | 1401 | 779 | 38903.6011 | 1483 | 658 | 970.5 | 1060.5 | 85.5311 | 47.558 | 90.5372 | 40.1709 | 0.85531 | 0.47558 | 0.90537 | 0.40171 | 0.37973 | 0.50366 | 297.7989 | 256.6411 | 15.6466
38903.6012 | 1312 | 745 | 38903.6012 | 1556 | 832 | 981.5 | 1071.5 | 80.0977 | 45.4823 | 94.9939 | 50.7937 | 0.80098 | 0.45482 | 0.94994 | 0.50794 | 0.34615 | 0.442 | 226.9502 | 677.8636 | 34.2003
38903.6013 | 1416 | 784 | 38903.6014 | 1256 | 675 | 992.5 | 1082.5 | 86.4469 | 47.8632 | 76.6789 | 41.2088 | 0.86447 | 0.47863 | 0.76679 | 0.41209 | 0.38584 | 0.3547 | 208.6258 | 424.6892 | 15.4222
38903.6015 | 1859 | 469 | 38903.6015 | 1706 | 421 | 1003.5 | 1093.5 | 113.4921 | 28.6325 | 104.1514 | 25.7021 | 1.1349 | 0.28632 | 1.0415 | 0.25702 | 0.8486 | 0.78449 | 40.4795 | 262.6388 | 3.3016
| 1562 | 532 | 38903.6016 | 1733 | 548 | 1014 | 1104 | 95.3602 | 32.4786 | 105.7998 | 33.4554 | 0.9536 | 0.32479 | 1.058 | 0.33455 | 0.62882 | 0.72344 | 4353.4458 | 52.5737 | 16.5411
38903.6017 | 1264 | 595 | 38903.6017 | 1375 | 621 | 1024.5 | 1114.5 | 77.1673 | 36.3248 | 83.9438 | 37.9121 | 0.77167 | 0.36325 | 0.83944 | 0.37912 | 0.40842 | 0.46032 | 338.5705 | 170.7696 | 51.9788
38903.6018 | 1199 | 761 | 38903.6019 | 1451 | 860 | 1035.5 | 1125.5 | 73.199 | 46.4591 | 88.5836 | 52.5031 | 0.73199 | 0.46459 | 0.88584 | 0.52503 | 0.2674 | 0.36081 | 673.684 | 284.7623 | 37.8686
38903.602 | 1242 | 614 | 38903.602 | 1614 | 790 | 1046.5 | 1136.5 | 75.8242 | 37.4847 | 98.5348 | 48.2295 | 0.75824 | 0.37485 | 0.98535 | 0.4823 | 0.38339 | 0.50305 | 746.3844 | 128.0143 | 45.1138
38903.6021 | 1465 | 381 | 38903.6021 | 1850 | 543 | 1057.5 | 1147.5 | 89.4383 | 23.2601 | 112.9426 | 33.1502 | 0.89438 | 0.2326 | 1.1294 | 0.3315 | 0.66178 | 0.79792 | 541.4061 | 41.3837 | 38.6724
38903.6022 | 1552 | 447 | 38903.6022 | 1714 | 501 | 1068 | 1158 | 94.7497 | 27.2894 | 104.6398 | 30.5861 | 0.9475 | 0.27289 | 1.0464 | 0.30586 | 0.6746 | 0.74054 | 176.811 | 68.3464 | 31.8232
38903.6023 | 1532 | 449 | 38903.6023 | 1802 | 506 | 1078.5 | 1168.5 | 93.5287 | 27.4115 | 110.0122 | 30.8913 | 0.93529 | 0.27411 | 1.1001 | 0.30891 | 0.66117 | 0.79121 | 2018.817 | 43.0691 | 24.6984
38903.6025 | 1534 | 354 | 38903.6025 | 1598 | 367 | 1089.5 | 1179.5 | 93.6508 | 21.6117 | 97.558 | 22.4054 | 0.93651 | 0.21612 | 0.97558 | 0.22405 | 0.72039 | 0.75153 | 107.0728 | 84.5918 | 59.7271
38903.6026 | 1823 | 344 | 38903.6026 | 1845 | 471 | 1100.5 | 1190.5 | 111.2943 | 21.0012 | 112.6374 | 28.7546 | 1.1129 | 0.21001 | 1.1264 | 0.28755 | 0.90293 | 0.83883 | 37.857 | 388.4487 | 42.1632
38903.6027 | 1441 | 513 | 38903.6027 | 1722 | 657 | 1111.5 | 1201.5 | 87.9731 | 31.3187 | 105.1282 | 40.1099 | 0.87973 | 0.31319 | 1.0513 | 0.4011 | 0.56654 | 0.65018 | 649.2884 | 65.0936 | 30.3882
38903.6028 | 1810 | 541 | 38903.6028 | 1399 | 446 | 1122 | 1212 | 110.5006 | 33.0281 | 85.409 | 27.2283 | 1.105 | 0.33028 | 0.85409 | 0.27228 | 0.77473 | 0.58181 | 39.297 | 522.3423 | 0.25133
38903.603 | 1767 | 549 | 38903.603 | 1657 | 615 | 1132.5 | 1222.5 | 107.8755 | 33.5165 | 101.16 | 37.5458 | 1.0788 | 0.33516 | 1.0116 | 0.37546 | 0.74359 | 0.63614 | 24.1809 | 46.1177 | 1.919
38903.6031 | 2267 | 68 | 38903.6031 | 1893 | 56 | 1143.5 | 1233.5 | 138.4005 | 4.1514 | 115.5678 | 3.4188 | 1.384 | 0.041514 | 1.1557 | 0.034188 | 1.3425 | 1.1215 | 3.8455 | 119.8684 | 11.529
38903.6032 | 1938 | 53 | 38903.6032 | 2306 | 64 | 1154.5 | 1244.5 | 118.315 | 3.2357 | 140.7814 | 3.9072 | 1.1832 | 0.032357 | 1.4078 | 0.039072 | 1.1508 | 1.3687 | 39.0063 | 6.3829 | 40.5706
38903.6033 | 1846 | 58 | 38903.6034 | 2061 | 61 | 1165.5 | 1255.5 | 112.6984 | 3.5409 | 125.8242 | 3.7241 | 1.127 | 0.035409 | 1.2582 | 0.037241 | 1.0916 | 1.221 | 35.44 | 15.7768 | 104.6403
38903.6035 | 2322 | 73 | 38903.6035 | 2333 | 72 | 1176 | 1266 | 141.7582 | 4.4567 | 142.4298 | 4.3956 | 1.4176 | 0.044567 | 1.4243 | 0.043956 | 1.373 | 1.3803 | 3.7496 | 4.8065 | 2.866
38903.6036 | 2262 | 70 | 38903.6036 | 2095 | 65 | 1186.5 | 1276.5 | 138.0952 | 4.2735 | 127.8999 | 3.9683 | 1.381 | 0.042735 | 1.279 | 0.039683 | 1.3382 | 1.2393 | 4.2546 | 50.6505 | 8.3477
38903.6037 | 2027 | 66 | 38903.6037 | 2017 | 61 | 1197.5 | 1287.5 | 123.7485 | 4.0293 | 123.138 | 3.7241 | 1.2375 | 0.040293 | 1.2314 | 0.037241 | 1.1972 | 1.1941 | 19.7296 | 20.1831 | 65.2357
38903.6038 | 2171 | 94 | 38903.6039 | 2263 | 78 | 1208.5 | 1298.5 | 132.5397 | 5.7387 | 138.1563 | 4.7619 | 1.3254 | 0.057387 | 1.3816 | 0.047619 | 1.268 | 1.3339 | 31.0887 | 6.2532 | 5.2829
38903.604 | 2290 | 87 | 38903.604 | 1995 | 90 | 1219.5 | 1309.5 | 139.8046 | 5.3114 | 121.7949 | 5.4945 | 1.398 | 0.053114 | 1.2179 | 0.054945 | 1.3449 | 1.163 | 2.1486 | 15.5172 | 4.2645
38903.6041 | 1819 | 88 | 38903.6041 | 2163 | 101 | 1230 | 1320 | 111.0501 | 5.3724 | 132.0513 | 6.1661 | 1.1105 | 0.053724 | 1.3205 | 0.061661 | 1.0568 | 1.2589 | 63.7286 | 9.7914 | 44.8319
38903.6042 | 1756 | 89 | 38903.6042 | 1974 | 94 | 1240.5 | 1330.5 | 107.2039 | 5.4335 | 120.5128 | 5.7387 | 1.072 | 0.054335 | 1.2051 | 0.057387 | 1.0177 | 1.1477 | 46.7624 | 22.3576 | 103.5527
38903.6043 | 2020 | 100 | 38903.6044 | 2108 | 118 | 1251.5 | 1341.5 | 123.3211 | 6.105 | 128.6935 | 7.2039 | 1.2332 | 0.06105 | 1.2869 | 0.072039 | 1.1722 | 1.2149 | 25.6025 | 15.7857 | 31.2726
38903.6045 | 1955 | 96 | 38903.6045 | 2270 | 120 | 1262.5 | 1352.5 | 119.3529 | 5.8608 | 138.5836 | 7.326 | 1.1935 | 0.058608 | 1.3858 | 0.07326 | 1.1349 | 1.3126 | 33.6308 | 13.9875 | 38.1401
38903.6046 | 2110 | 114 | 38903.6046 | 2267 | 100 | 1273.5 | 1363.5 | 128.8156 | 6.9597 | 138.4005 | 6.105 | 1.2882 | 0.069597 | 1.384 | 0.06105 | 1.2186 | 1.323 | 10.0719 | 29.9434 | 25.3437
38903.6047 | 2119 | 116 | 38903.6047 | 2220 | 125 | 1283.5 | 1373.5 | 129.3651 | 7.0818 | 135.5311 | 7.6313 | 1.2937 | 0.070818 | 1.3553 | 0.076313 | 1.2228 | 1.279 | 94.9059 | 6.59 | 6.0962
38903.6048 | 2006 | 110 | 38903.6048 | 2257 | 126 | 1294.5 | 1384.5 | 122.4664 | 6.7155 | 137.79 | 7.6923 | 1.2247 | 0.067155 | 1.3779 | 0.076923 | 1.1575 | 1.301 | 30.1421 | 14.535 | 26.9245
38903.605 | 2153 | 143 | 38903.605 | 1933 | 146 | 1305.5 | 1395.5 | 131.4408 | 8.7302 | 118.0098 | 8.9133 | 1.3144 | 0.087302 | 1.1801 | 0.089133 | 1.2271 | 1.091 | 10.4734 | 105.9502 | 19.2036
38903.6051 | 2184 | 123 | 38903.6051 | 1812 | 105 | 1316.5 | 1406.5 | 133.3333 | 7.5092 | 110.6227 | 6.4103 | 1.3333 | 0.075092 | 1.1062 | 0.064103 | 1.2582 | 1.0421 | 8.4624 | 115.2632 | 18.4492
38903.6052 | 2093 | 140 | 38903.6052 | 1832 | 133 | 1327.5 | 1417.5 | 127.7778 | 8.547 | 111.8437 | 8.1197 | 1.2778 | 0.08547 | 1.1184 | 0.081197 | 1.1923 | 1.0372 | 14.759 | 64.8462 | 32.7006
38903.6053 | 1965 | 95 | 38903.6053 | 2153 | 114 | 1338 | 1428 | 119.9634 | 5.7998 | 131.4408 | 6.9597 | 1.1996 | 0.057998 | 1.3144 | 0.069597 | 1.1416 | 1.2448 | 37.2594 | 11.3316 | 31.0039
38903.6055 | 2165 | 103 | 38903.6055 | 2034 | 88 | 1348.5 | 1438.5 | 132.1734 | 6.2882 | 124.1758 | 5.3724 | 1.3217 | 0.062882 | 1.2418 | 0.053724 | 1.2589 | 1.188 | 10.911 | 27.6777 | 17.1276
38903.6056 | 2195 | 99 | 38903.6056 | 1796 | 73 | 1359.5 | 1449.5 | 134.0049 | 6.044 | 109.6459 | 4.4567 | 1.34 | 0.06044 | 1.0965 | 0.044567 | 1.2796 | 1.0519 | 7.9049 | 69.2138 | 22.881
38903.6057 | 2127 | 106 | 38903.6057 | 2276 | 102 | 1370.5 | 1460.5 | 129.8535 | 6.4713 | 138.9499 | 6.2271 | 1.2985 | 0.064713 | 1.3895 | 0.062271 | 1.2338 | 1.3272 | 6.7032 | 8.1759 | 8.298
38903.6058 | 2180 | 101 | 38903.6059 | 2327 | 68 | 1381.5 | 1471.5 | 133.0891 | 6.1661 | 142.0635 | 4.1514 | 1.3309 | 0.061661 | 1.4206 | 0.041514 | 1.2692 | 1.3791 | 1.6942 | 1.2755 | 0.85269
38903.606 | 2061 | 93 | 38903.606 | 1821 | 82 | 1392 | 1482 | 125.8242 | 5.6777 | 111.1722 | 5.0061 | 1.2582 | 0.056777 | 1.1117 | 0.050061 | 1.2015 | 1.0617 | 16.4838 | 42.5584 | 62.7176
38903.6061 | 1763 | 87 | 38903.6061 | 1911 | 94 | 1402.5 | 1492.5 | 107.6313 | 5.3114 | 116.6667 | 5.7387 | 1.0763 | 0.053114 | 1.1667 | 0.057387 | 1.0232 | 1.1093 | 43.1598 | 27.4124 | 123.4943
38903.6062 | 2154 | 70 | 38903.6062 | 2329 | 71 | 1413.5 | 1503.5 | 131.5018 | 4.2735 | 142.1856 | 4.3346 | 1.315 | 0.042735 | 1.4219 | 0.043346 | 1.2723 | 1.3785 | 0.85489 | 0.33702 | 0.60162
38903.6063 | 2296 | 77 | 38903.6064 | 1965 | 84 | 1424.5 | 1514.5 | 140.1709 | 4.7009 | 119.9634 | 5.1282 | 1.4017 | 0.047009 | 1.1996 | 0.051282 | 1.3547 | 1.1484 | 1.9842 | 16.3397 | 4.3083
38903.6065 | 1991 | 74 | 38903.6065 | 2283 | 82 | 1435.5 | 1525.5 | 121.5507 | 4.5177 | 139.3773 | 5.0061 | 1.2155 | 0.045177 | 1.3938 | 0.050061 | 1.1703 | 1.3437 | 49.7459 | 6.1843 | 22.3819

## C1-2
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 141.7204 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38903.5888 | 1 | 1 | 38903.5888 | 1 | 0 | -89.5 | 0.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 538416334.44 | 232038 | 231838.0862
38903.5889 | 1 | 0 | 38903.589 | 1 | 0 | -78.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5891 | 1 | 0 | 38903.5891 | 1 | 0 | -67.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5892 | 1 | 0 | 38903.5892 | 1 | 0 | -56.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5893 | 1 | 0 | 38903.5893 | 1 | 0 | -46.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5894 | 1 | 0 | 38903.5895 | 1 | 0 | -35.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5896 | 1 | 0 | 38903.5896 | 1 | 0 | -24.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5897 | 1 | 0 | 38903.5897 | 1 | 0 | -13.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5898 | 1 | 0 | 38903.5898 | 1 | 0 | -2.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5899 | 1 | 0 | 38903.59 | 1 | 0 | 7.5 | 97.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5901 | 1 | 0 | 38903.5901 | 1 | 0 | 18.5 | 108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5902 | 1 | 0 | 38903.5902 | 1 | 0 | 29.5 | 119.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5903 | 1 | 0 | 38903.5903 | 1 | 0 | 40.5 | 130.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5905 | 1 | 0 | 38903.5905 | 1 | 0 | 51.5 | 141.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5906 | 1 | 0 | 38903.5906 | 1 | 0 | 61.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5907 | 1 | 0 | 38903.5907 | 1 | 0 | 72.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5908 | 1 | 0 | 38903.5908 | 2 | 0 | 83.5 | 173.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 232038 | 115969 | 232037.9994
38903.5909 | 1 | 0 | 38903.591 | 1 | 0 | 94.5 | 184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5911 | 1 | 0 | 38903.5911 | 1 | 0 | 105.5 | 195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5912 | 2 | 0 | 38903.5912 | 1 | 0 | 115.5 | 205.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115969 | 232038 | 115968.9988
38903.5913 | 1 | 0 | 38903.5913 | 1 | 0 | 126.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5914 | 1 | 0 | 38903.5915 | 1 | 0 | 137.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5916 | 1 | 0 | 38903.5916 | 1 | 0 | 148.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5917 | 1 | 0 | 38903.5917 | 1 | 0 | 159.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5918 | 1 | 0 | 38903.5918 | 2 | 0 | 170 | 260 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 232038 | 115969 | 232037.9994
38903.5919 | 1 | 0 | 38903.592 | 1 | 0 | 180.5 | 270.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5921 | 1 | 0 | 38903.5921 | 1 | 0 | 191.5 | 281.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5922 | 1 | 0 | 38903.5922 | 1 | 0 | 202.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5923 | 1 | 0 | 38903.5923 | 1 | 0 | 213.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5925 | 1 | 0 | 38903.5925 | 1 | 0 | 224 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5926 | 1 | 0 | 38903.5926 | 1 | 0 | 234.5 | 324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5927 | 1 | 0 | 38903.5927 | 1 | 0 | 245.5 | 335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5928 | 1 | 0 | 38903.5928 | 1 | 0 | 256.5 | 346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.593 | 1 | 0 | 38903.593 | 1 | 0 | 267.5 | 357.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5931 | 1 | 0 | 38903.5931 | 1 | 0 | 277.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5932 | 1 | 0 | 38903.5932 | 1 | 0 | 288.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5933 | 1 | 0 | 38903.5933 | 1 | 0 | 299.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5934 | 1 | 0 | 38903.5935 | 1 | 0 | 310.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5936 | 1 | 0 | 38903.5936 | 1 | 0 | 321.5 | 411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5937 | 1 | 0 | 38903.5937 | 1 | 0 | 331.5 | 421.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5938 | 1 | 0 | 38903.5938 | 1 | 0 | 342.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5939 | 1 | 0 | 38903.594 | 1 | 0 | 353.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5941 | 1 | 0 | 38903.5941 | 1 | 0 | 364.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5942 | 1 | 0 | 38903.5942 | 1 | 0 | 375.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5943 | 1 | 0 | 38903.5943 | 1 | 0 | 385.5 | 475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5944 | 1 | 0 | 38903.5945 | 1 | 0 | 396.5 | 486.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5946 | 1 | 0 | 38903.5946 | 1 | 0 | 407.5 | 497.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5947 | 1 | 0 | 38903.5947 | 1 | 0 | 418.5 | 508.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5948 | 1 | 0 | 38903.5948 | 1 | 0 | 429.5 | 519.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5949 | 1 | 0 | 38903.595 | 1 | 0 | 439.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5951 | 1 | 0 | 38903.5951 | 1 | 0 | 450.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5952 | 1 | 0 | 38903.5952 | 1 | 0 | 461.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5953 | 1 | 0 | 38903.5953 | 1 | 0 | 472.5 | 562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5955 | 1 | 0 | 38903.5955 | 1 | 0 | 483.5 | 573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5956 | 1 | 0 | 38903.5956 | 1 | 0 | 493.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5957 | 1 | 0 | 38903.5957 | 1 | 0 | 504.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5958 | 1 | 0 | 38903.5958 | 2 | 0 | 515.5 | 605.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 232038 | 115969 | 232037.9994
38903.5959 | 1 | 0 | 38903.596 | 1 | 0 | 526.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5961 | 1 | 0 | 38903.5961 | 2 | 0 | 537 | 627 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 232038 | 115969 | 232037.9994
38903.5962 | 2 | 0 | 38903.5962 | 1 | 0 | 547.5 | 637.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 115969 | 232038 | 115968.9988
38903.5963 | 1 | 0 | 38903.5963 | 1 | 0 | 558.5 | 648.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5964 | 1 | 0 | 38903.5965 | 1 | 0 | 569.5 | 659.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5966 | 1 | 0 | 38903.5966 | 1 | 0 | 580.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5967 | 1 | 0 | 38903.5967 | 1 | 0 | 591.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5968 | 1 | 0 | 38903.5968 | 1 | 0 | 601.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5969 | 1 | 0 | 38903.597 | 1 | 0 | 612.5 | 702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5971 | 1 | 0 | 38903.5971 | 1 | 0 | 623.5 | 713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5972 | 1 | 0 | 38903.5972 | 1 | 0 | 634.5 | 724.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5973 | 1 | 0 | 38903.5973 | 1 | 0 | 645.5 | 735.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5974 | 1 | 0 | 38903.5975 | 1 | 0 | 655.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5976 | 1 | 0 | 38903.5976 | 1 | 0 | 666.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5977 | 1 | 0 | 38903.5977 | 1 | 0 | 677.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5978 | 1 | 0 | 38903.5978 | 1 | 0 | 688.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.598 | 1 | 0 | 38903.598 | 1 | 0 | 699.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5981 | 1 | 0 | 38903.5981 | 1 | 0 | 709.5 | 799.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5982 | 1 | 0 | 38903.5982 | 1 | 0 | 720.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5983 | 1 | 0 | 38903.5983 | 1 | 0 | 731.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5984 | 1 | 0 | 38903.5985 | 1 | 0 | 742.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5986 | 1 | 0 | 38903.5986 | 1 | 0 | 753 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5987 | 1 | 0 | 38903.5987 | 1 | 0 | 763.5 | 853.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232038 | 232038 | 232037.9994
38903.5988 | 5 | 0 | 38903.5988 | 1 | 0 | 774.5 | 864.5 | 0.30525 | 0 | 0.06105 | 0 | 0.0030525 | 0 | 0.0006105 | 0 | 0.0030525 | 0.0006105 | 46327.6 | 232038 | 46327.5969
38903.5989 | 38 | 0 | 38903.599 | 1 | 0 | 785.5 | 875.5 | 2.3199 | 0 | 0.06105 | 0 | 0.023199 | 0 | 0.0006105 | 0 | 0.023199 | 0.0006105 | 6008.8947 | 232038 | 6008.8715
38903.5991 | 84 | 0 | 38903.5991 | 1 | 0 | 796.5 | 886.5 | 5.1282 | 0 | 0.06105 | 0 | 0.051282 | 0 | 0.0006105 | 0 | 0.051282 | 0.0006105 | 2663.5476 | 232038 | 2663.4963
38903.5992 | 199 | 1 | 38903.5992 | 8 | 1 | 807 | 897 | 12.149 | 0.06105 | 0.4884 | 0.06105 | 0.12149 | 0.0006105 | 0.004884 | 0.0006105 | 0.12088 | 0.0042735 | 1071.9253 | 33494.6744 | 211506.5368
38903.5993 | 365 | 104 | 38903.5993 | 309 | 186 | 817.5 | 907.5 | 22.2833 | 6.3492 | 18.8645 | 11.3553 | 0.22283 | 0.063492 | 0.18864 | 0.11355 | 0.15934 | 0.075092 | 764.5075 | 2039.4928 | 1697.8843
38903.5994 | 500 | 159 | 38903.5995 | 308 | 189 | 828.5 | 918.5 | 30.525 | 9.707 | 18.8034 | 11.5385 | 0.30525 | 0.09707 | 0.18803 | 0.11538 | 0.20818 | 0.07265 | 544.7652 | 2388.1768 | 1003.5024
38903.5996 | 527 | 228 | 38903.5996 | 423 | 307 | 839.5 | 929.5 | 32.1734 | 13.9194 | 25.8242 | 18.7424 | 0.32173 | 0.13919 | 0.25824 | 0.18742 | 0.18254 | 0.070818 | 616.5223 | 2867.446 | 663.8573
38903.5997 | 496 | 227 | 38903.5997 | 501 | 330 | 850.5 | 940.5 | 30.2808 | 13.8584 | 30.5861 | 20.1465 | 0.30281 | 0.13858 | 0.30586 | 0.20147 | 0.16422 | 0.1044 | 720.3872 | 1454.0787 | 658.8235
38903.5998 | 557 | 279 | 38903.5998 | 562 | 344 | 861 | 951 | 34.0049 | 17.033 | 34.3101 | 21.0012 | 0.34005 | 0.17033 | 0.3431 | 0.21001 | 0.16972 | 0.13309 | 702.3908 | 1040.9029 | 485.73
38903.5999 | 1043 | 770 | 38903.6 | 1232 | 949 | 871.5 | 961.5 | 63.6752 | 47.0085 | 75.2137 | 57.9365 | 0.63675 | 0.47009 | 0.75214 | 0.57937 | 0.16667 | 0.17277 | 832.6902 | 644.4813 | 57.155
38903.6001 | 1282 | 1047 | 38903.6001 | 1224 | 934 | 882.5 | 972.5 | 78.2662 | 63.9194 | 74.7253 | 57.0208 | 0.78266 | 0.63919 | 0.74725 | 0.57021 | 0.14347 | 0.17705 | 355.6549 | 1829.0136 | 0.69006
38903.6002 | 1343 | 801 | 38903.6002 | 1190 | 893 | 893.5 | 983.5 | 81.9902 | 48.9011 | 72.6496 | 54.5177 | 0.8199 | 0.48901 | 0.7265 | 0.54518 | 0.33089 | 0.18132 | 104.3472 | 202.4672 | 14.8234
38903.6003 | 1043 | 812 | 38903.6003 | 1309 | 952 | 904.5 | 994.5 | 63.6752 | 49.5726 | 79.9145 | 58.1197 | 0.63675 | 0.49573 | 0.79915 | 0.5812 | 0.14103 | 0.21795 | 930.2804 | 867.6955 | 51.5006
38903.6005 | 1235 | 889 | 38903.6005 | 1304 | 999 | 915 | 1005 | 75.3968 | 54.2735 | 79.6093 | 60.989 | 0.75397 | 0.54274 | 0.79609 | 0.60989 | 0.21123 | 0.1862 | 268.5228 | 1517.6738 | 20.83
38903.6006 | 1343 | 951 | 38903.6006 | 1315 | 992 | 925.5 | 1015.5 | 81.9902 | 58.0586 | 80.2808 | 60.5617 | 0.8199 | 0.58059 | 0.80281 | 0.60562 | 0.23932 | 0.19719 | 47.2129 | 56.598 | 1.0406
38903.6007 | 1100 | 739 | 38903.6007 | 1130 | 822 | 936.5 | 1026.5 | 67.1551 | 45.116 | 68.9866 | 50.1832 | 0.67155 | 0.45116 | 0.68987 | 0.50183 | 0.22039 | 0.18803 | 418.6516 | 1067.0157 | 59.6814
38903.6008 | 1149 | 812 | 38903.6008 | 1400 | 938 | 947.5 | 1037.5 | 70.1465 | 49.5726 | 85.4701 | 57.265 | 0.70147 | 0.49573 | 0.8547 | 0.57265 | 0.20574 | 0.28205 | 492.8167 | 819.3225 | 39.5541
38903.6009 | 1280 | 875 | 38903.601 | 1369 | 840 | 958.5 | 1048.5 | 78.1441 | 53.4188 | 83.5775 | 51.2821 | 0.78144 | 0.53419 | 0.83578 | 0.51282 | 0.24725 | 0.32295 | 332.7966 | 950.239 | 17.2043
38903.6011 | 1197 | 763 | 38903.6011 | 1206 | 716 | 969 | 1059 | 73.0769 | 46.5812 | 73.6264 | 43.7118 | 0.73077 | 0.46581 | 0.73626 | 0.43712 | 0.26496 | 0.29915 | 642.2608 | 294.6696 | 35.3624
38903.6012 | 1436 | 824 | 38903.6012 | 1463 | 811 | 979.5 | 1069.5 | 87.6679 | 50.3053 | 89.3162 | 49.5116 | 0.87668 | 0.50305 | 0.89316 | 0.49512 | 0.37363 | 0.39805 | 769.5704 | 165.811 | 4.6467
38903.6013 | 1226 | 675 | 38903.6013 | 1212 | 674 | 990.5 | 1080.5 | 74.8474 | 41.2088 | 73.9927 | 41.1477 | 0.74847 | 0.41209 | 0.73993 | 0.41148 | 0.33639 | 0.32845 | 306.4032 | 348.8305 | 48.4028
38903.6014 | 1461 | 564 | 38903.6015 | 1437 | 514 | 1001.5 | 1091.5 | 89.1941 | 34.4322 | 87.7289 | 31.3797 | 0.89194 | 0.34432 | 0.87729 | 0.3138 | 0.54762 | 0.56349 | 172.7091 | 141.4126 | 30.7821
38903.6016 | 1451 | 454 | 38903.6016 | 1384 | 443 | 1012.5 | 1102.5 | 88.5836 | 27.7167 | 84.4933 | 27.0452 | 0.88584 | 0.27717 | 0.84493 | 0.27045 | 0.60867 | 0.57448 | 121.1688 | 162.9108 | 56.8297
38903.6017 | 1519 | 526 | 38903.6017 | 1696 | 550 | 1023 | 1113 | 92.735 | 32.1123 | 103.5409 | 33.5775 | 0.92735 | 0.32112 | 1.0354 | 0.33578 | 0.60623 | 0.69963 | 1167.1341 | 56.9109 | 19.0574
38903.6018 | 1402 | 877 | 38903.6018 | 1359 | 953 | 1033.5 | 1123.5 | 85.5922 | 53.5409 | 82.967 | 58.1807 | 0.85592 | 0.53541 | 0.82967 | 0.58181 | 0.32051 | 0.24786 | 32.8526 | 38.5748 | 1.3452
38903.6019 | 1303 | 737 | 38903.602 | 1524 | 842 | 1044.5 | 1134.5 | 79.5482 | 44.9939 | 93.0403 | 51.4042 | 0.79548 | 0.44994 | 0.9304 | 0.51404 | 0.34554 | 0.41636 | 373.1359 | 251.4712 | 27.3164
38903.6021 | 1583 | 477 | 38903.6021 | 1650 | 504 | 1055.5 | 1145.5 | 96.6422 | 29.1209 | 100.7326 | 30.7692 | 0.96642 | 0.29121 | 1.0073 | 0.30769 | 0.67521 | 0.69963 | 130.3318 | 88.4215 | 25.7147
38903.6022 | 1558 | 540 | 38903.6022 | 1843 | 543 | 1066.5 | 1156.5 | 95.116 | 32.967 | 112.5153 | 33.1502 | 0.95116 | 0.32967 | 1.1252 | 0.3315 | 0.62149 | 0.79365 | 33.471 | 42.7648 | 12.3913
38903.6023 | 1764 | 522 | 38903.6023 | 1489 | 413 | 1077 | 1167 | 107.6923 | 31.8681 | 90.9035 | 25.2137 | 1.0769 | 0.31868 | 0.90904 | 0.25214 | 0.75824 | 0.6569 | 52.6039 | 286.1528 | 5.0226
38903.6024 | 1501 | 669 | 38903.6025 | 1639 | 704 | 1087.5 | 1177.5 | 91.6361 | 40.8425 | 100.0611 | 42.9792 | 0.91636 | 0.40842 | 1.0006 | 0.42979 | 0.50794 | 0.57082 | 153.7605 | 224.1536 | 15.6472
38903.6026 | 1752 | 416 | 38903.6026 | 1599 | 411 | 1098.5 | 1188.5 | 106.9597 | 25.3968 | 97.619 | 25.0916 | 1.0696 | 0.25397 | 0.97619 | 0.25092 | 0.81563 | 0.72527 | 51.0378 | 188.7517 | 24.1014
38903.6027 | 1801 | 574 | 38903.6027 | 1766 | 409 | 1109.5 | 1199.5 | 109.9512 | 35.0427 | 107.8144 | 24.9695 | 1.0995 | 0.35043 | 1.0781 | 0.24969 | 0.74908 | 0.82845 | 55.6525 | 196.611 | 6.1921
38903.6028 | 1612 | 546 | 38903.6028 | 1703 | 430 | 1120.5 | 1210.5 | 98.4127 | 33.3333 | 103.9683 | 26.2515 | 0.98413 | 0.33333 | 1.0397 | 0.26252 | 0.65079 | 0.77717 | 568.4842 | 58.0101 | 10.9856
38903.603 | 1770 | 650 | 38903.603 | 1320 | 528 | 1131 | 1221 | 108.0586 | 39.6825 | 80.5861 | 32.2344 | 1.0806 | 0.39683 | 0.80586 | 0.32234 | 0.68376 | 0.48352 | 34.4363 | 135.0908 | 8.7185
38903.6031 | 1535 | 432 | 38903.6031 | 2176 | 73 | 1141.5 | 1231.5 | 93.7118 | 26.3736 | 132.8449 | 4.4567 | 0.93712 | 0.26374 | 1.3284 | 0.044567 | 0.67338 | 1.2839 | 11.0658 | 7.1959 | 5.5067
38903.6032 | 2305 | 66 | 38903.6032 | 2050 | 57 | 1152.5 | 1242.5 | 140.7204 | 4.0293 | 125.1526 | 3.4799 | 1.4072 | 0.040293 | 1.2515 | 0.034799 | 1.3669 | 1.2167 | 0.14351 | 0.71933 | 0.53694
38903.6033 | 2250 | 65 | 38903.6033 | 2112 | 60 | 1163.5 | 1253.5 | 137.3626 | 3.9683 | 128.9377 | 3.663 | 1.3736 | 0.039683 | 1.2894 | 0.03663 | 1.3339 | 1.2527 | 3.4079 | 71.8561 | 4.104
38903.6034 | 1948 | 59 | 38903.6035 | 2262 | 74 | 1174.5 | 1264.5 | 118.9255 | 3.602 | 138.0952 | 4.5177 | 1.1893 | 0.03602 | 1.381 | 0.045177 | 1.1532 | 1.3358 | 105.2125 | 3.8459 | 19.7336
38903.6036 | 2283 | 73 | 38903.6036 | 2027 | 72 | 1184.5 | 1274.5 | 139.3773 | 4.4567 | 123.7485 | 4.3956 | 1.3938 | 0.044567 | 1.2375 | 0.043956 | 1.3492 | 1.1935 | 1.1897 | 7.1858 | 3.1794
38903.6037 | 1965 | 65 | 38903.6037 | 2245 | 70 | 1195.5 | 1285.5 | 119.9634 | 3.9683 | 137.0574 | 4.2735 | 1.1996 | 0.039683 | 1.3706 | 0.042735 | 1.16 | 1.3278 | 605.0255 | 3.5305 | 15.2867
38903.6038 | 2066 | 77 | 38903.6038 | 1858 | 80 | 1206.5 | 1296.5 | 126.1294 | 4.7009 | 113.431 | 4.884 | 1.2613 | 0.047009 | 1.1343 | 0.04884 | 1.2143 | 1.0855 | 14.2946 | 38.0334 | 63.8318
38903.6039 | 2003 | 81 | 38903.604 | 2203 | 99 | 1217.5 | 1307.5 | 122.2833 | 4.9451 | 134.4933 | 6.044 | 1.2228 | 0.049451 | 1.3449 | 0.06044 | 1.1734 | 1.2845 | 51.9608 | 6.1867 | 17.0744
38903.6041 | 2055 | 92 | 38903.6041 | 2074 | 95 | 1228.5 | 1318.5 | 125.4579 | 5.6166 | 126.6178 | 5.7998 | 1.2546 | 0.056166 | 1.2662 | 0.057998 | 1.1984 | 1.2082 | 18.8302 | 16.7773 | 27.2316
38903.6042 | 1871 | 87 | 38903.6042 | 2212 | 111 | 1239 | 1329 | 114.2247 | 5.3114 | 135.0427 | 6.7766 | 1.1422 | 0.053114 | 1.3504 | 0.067766 | 1.0891 | 1.2827 | 320.7728 | 5.2933 | 20.9974
38903.6043 | 1829 | 95 | 38903.6043 | 1891 | 95 | 1249.5 | 1339.5 | 111.6606 | 5.7998 | 115.4457 | 5.7998 | 1.1166 | 0.057998 | 1.1545 | 0.057998 | 1.0586 | 1.0965 | 35.244 | 28.1948 | 91.9986
38903.6044 | 1981 | 102 | 38903.6045 | 1763 | 90 | 1260.5 | 1350.5 | 120.9402 | 6.2271 | 107.6313 | 5.4945 | 1.2094 | 0.062271 | 1.0763 | 0.054945 | 1.1471 | 1.0214 | 20.5886 | 45.1813 | 72.7307
38903.6046 | 2057 | 108 | 38903.6046 | 1915 | 100 | 1271.5 | 1361.5 | 125.58 | 6.5934 | 116.9109 | 6.105 | 1.2558 | 0.065934 | 1.1691 | 0.06105 | 1.1899 | 1.1081 | 16.2142 | 33.9143 | 36.6702
38903.6047 | 1861 | 96 | 38903.6047 | 2209 | 126 | 1282.5 | 1372.5 | 113.6142 | 5.8608 | 134.8596 | 7.6923 | 1.1361 | 0.058608 | 1.3486 | 0.076923 | 1.0775 | 1.2717 | 2451.0916 | 5.4976 | 19.7794
38903.6048 | 2271 | 124 | 38903.6048 | 2188 | 123 | 1292.5 | 1382.5 | 138.6447 | 7.5702 | 133.5775 | 7.5092 | 1.3864 | 0.075702 | 1.3358 | 0.075092 | 1.3107 | 1.2607 | 28.1531 | 6.3007 | 3.519
38903.6049 | 1782 | 98 | 38903.605 | 2125 | 118 | 1303.5 | 1393.5 | 108.7912 | 5.9829 | 129.7314 | 7.2039 | 1.0879 | 0.059829 | 1.2973 | 0.072039 | 1.0281 | 1.2253 | 70.4081 | 10.6763 | 43.4462
38903.6051 | 1883 | 94 | 38903.6051 | 1992 | 99 | 1314.5 | 1404.5 | 114.9573 | 5.7387 | 121.6117 | 6.044 | 1.1496 | 0.057387 | 1.2161 | 0.06044 | 1.0922 | 1.1557 | 32.8426 | 20.6954 | 62.8193
38903.6052 | 1757 | 129 | 38903.6052 | 1815 | 148 | 1325.5 | 1415.5 | 107.265 | 7.8755 | 110.8059 | 9.0354 | 1.0726 | 0.078755 | 1.1081 | 0.090354 | 0.99389 | 1.0177 | 43.7682 | 38.1065 | 93.1244
38903.6053 | 2265 | 123 | 38903.6053 | 2278 | 123 | 1336.5 | 1426.5 | 138.2784 | 7.5092 | 139.072 | 7.5092 | 1.3828 | 0.075092 | 1.3907 | 0.075092 | 1.3077 | 1.3156 | 7.3678 | 8.9339 | 4.442
38903.6055 | 2253 | 104 | 38903.6055 | 1776 | 85 | 1347 | 1437 | 137.5458 | 6.3492 | 108.4249 | 5.1893 | 1.3755 | 0.063492 | 1.0842 | 0.051893 | 1.312 | 1.0324 | 2.8563 | 42.4455 | 10.2057
38903.6056 | 2210 | 101 | 38903.6056 | 1831 | 71 | 1357.5 | 1447.5 | 134.9206 | 6.1661 | 111.7827 | 4.3346 | 1.3492 | 0.061661 | 1.1178 | 0.043346 | 1.2875 | 1.0745 | 5.54 | 102.501 | 5.2021
38903.6057 | 1895 | 87 | 38903.6057 | 1865 | 72 | 1368.5 | 1458.5 | 115.6899 | 5.3114 | 113.8584 | 4.3956 | 1.1569 | 0.053114 | 1.1386 | 0.043956 | 1.1038 | 1.0946 | 28.1445 | 29.6895 | 89.3028
38903.6058 | 2305 | 105 | 38903.6058 | 1963 | 85 | 1379.5 | 1469.5 | 140.7204 | 6.4103 | 119.8413 | 5.1893 | 1.4072 | 0.064103 | 1.1984 | 0.051893 | 1.3431 | 1.1465 | 0.51666 | 10.8207 | 8.241
38903.6059 | 2166 | 93 | 38903.606 | 1817 | 66 | 1390.5 | 1480.5 | 132.2344 | 5.6777 | 110.928 | 4.0293 | 1.3223 | 0.056777 | 1.1093 | 0.040293 | 1.2656 | 1.069 | 8.1828 | 53.4058 | 23.3512
38903.6061 | 2108 | 97 | 38903.6061 | 1902 | 91 | 1401 | 1491 | 128.6935 | 5.9219 | 116.1172 | 5.5556 | 1.2869 | 0.059219 | 1.1612 | 0.055556 | 1.2277 | 1.1056 | 12.0802 | 39.6501 | 34.0651
38903.6062 | 1946 | 88 | 38903.6062 | 1806 | 61 | 1411.5 | 1501.5 | 118.8034 | 5.3724 | 110.2564 | 3.7241 | 1.188 | 0.053724 | 1.1026 | 0.037241 | 1.1343 | 1.0653 | 23.3945 | 34.7232 | 84.1687
38903.6063 | 2026 | 83 | 38903.6063 | 2303 | 109 | 1422.5 | 1512.5 | 123.6874 | 5.0672 | 140.5983 | 6.6545 | 1.2369 | 0.050672 | 1.406 | 0.066545 | 1.1862 | 1.3394 | 2.4714 | 0.82927 | 2.1045
38903.6064 | 2035 | 78 | 38903.6065 | 1878 | 76 | 1433.5 | 1523.5 | 124.2369 | 4.7619 | 114.652 | 4.6398 | 1.2424 | 0.047619 | 1.1465 | 0.046398 | 1.1947 | 1.1001 | 16.6471 | 32.9537 | 66.2164

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 3 |  |  | 2006-07-05 | 14:09
XLPE | 3-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-87.5 | 179629136.8133 |  | -85 | 233938 | -83.8333 | 235304.6667 | -82.6667 | 235938 | -87.5 | 233938
-76.5 | 234371.3333 |  | -74.3333 | 233938 | -73 | 235304.6667 | -71.8333 | 235938 | -76.5 | 233938
-65.8333 | 234371.3333 |  | -63.5 | 233938 | -62.1667 | 235304.6667 | -61.1667 | 235938 | -65.8333 | 233938
-55.1667 | 234371.3333 |  | -52.5 | 233938 | -51.5 | 235304.6667 | -50.1667 | 235938 | -55.1667 | 233938
-44.5 | 234371.3333 |  | -41.8333 | 233938 | -40.8333 | 235304.6667 | -39.5 | 235938 | -44.5 | 233938
-33.5 | 234371.3333 |  | -31.1667 | 233938 | -29.8333 | 235304.6667 | -28.8333 | 235938 | -33.5 | 233938
-22.5 | 234371.3333 |  | -20.5 | 233938 | -19.1667 | 235304.6667 | -17.8333 | 235938 | -22.5 | 233938
-11.6667 | 234371.3333 |  | -9.5 | 181662.8889 | -8.1667 | 235304.6667 | -7 | 235938 | -11.6667 | 181662.8889
-1.1667 | 234371.3333 |  | 1.5 | 233938 | 2.5 | 235304.6667 | 3.8333 | 235938 | -1.1667 | 233938
9.5 | 234371.3333 |  | 12.1667 | 233938 | 13.1667 | 235304.6667 | 14.5 | 235938 | 9.5 | 233938
20.5 | 234371.3333 |  | 23 | 233938 | 24.1667 | 235304.6667 | 25.3333 | 235938 | 20.5 | 233938
31.5 | 234371.3333 |  | 33.6667 | 233938 | 35 | 235304.6667 | 36.1667 | 235938 | 31.5 | 233938
42.3333 | 234371.3333 |  | 44.5 | 233938 | 45.8333 | 235304.6667 | 47 | 235938 | 42.3333 | 233938
53 | 234371.3333 |  | 55.5 | 183672362.1467 | 56.6667 | 235304.6667 | 57.8333 | 235938 | 53 | 234371.3333
63.5 | 234371.3333 |  | 66.1667 | 233938 | 67.1667 | 235304.6667 | 68.5 | 235938 | 63.5 | 233938
74.5 | 234371.3333 |  | 76.8333 | 233938 | 78.1667 | 195881.6667 | 79.1667 | 235938 | 74.5 | 195881.6667
85.5 | 155825.3333 |  | 87.6667 | 195248.3333 | 89 | 235304.6667 | 90.1667 | 235938 | 85.5 | 155825.3333
96.3333 | 234371.3333 |  | 98.5 | 233938 | 99.8333 | 235304.6667 | 101 | 235938 | 96.3333 | 233938
107 | 234371.3333 |  | 109.5 | 233938 | 110.6667 | 186499584.8133 | 111.8333 | 235938 | 107 | 233938
117.5 | 195681.6667 |  | 120.1667 | 233938 | 121.1667 | 235304.6667 | 122.5 | 196515 | 117.5 | 195681.6667
128.5 | 234371.3333 |  | 130.8333 | 233938 | 132.1667 | 235304.6667 | 133.1667 | 235938 | 128.5 | 233938
139.5 | 234371.3333 |  | 141.6667 | 233938 | 143 | 235304.6667 | 144.1667 | 235938 | 139.5 | 233938
150.3333 | 234371.3333 |  | 152.5 | 233938 | 153.8333 | 235304.6667 | 155 | 235938 | 150.3333 | 233938
161 | 234371.3333 |  | 163.5 | 233938 | 164.6667 | 235304.6667 | 165.8333 | 235938 | 161 | 233938
171.6667 | 234371.3333 |  | 174.3333 | 195248.3333 | 175.1667 | 235304.6667 | 176.5 | 196548.3333 | 171.6667 | 195248.3333
182.5 | 195215 |  | 184.8333 | 233938 | 186.1667 | 235304.6667 | 187.1667 | 235938 | 182.5 | 195215
193.5 | 234371.3333 |  | 195.5 | 233938 | 196.8333 | 196148.3333 | 198.1667 | 235938 | 193.5 | 196148.3333
204.3333 | 234371.3333 |  | 206.5 | 233938 | 207.8333 | 235304.6667 | 209 | 235938 | 204.3333 | 233938
215 | 234371.3333 |  | 217.5 | 194815 | 218.6667 | 235304.6667 | 219.8333 | 235938 | 215 | 194815
225.6667 | 195215 |  | 228.3333 | 183672362.1467 | 229.3333 | 235304.6667 | 230.6667 | 235938 | 225.6667 | 195215
236.5 | 234371.3333 |  | 238.8333 | 233938 | 240.1667 | 235304.6667 | 241.1667 | 235938 | 236.5 | 233938
247.5 | 234371.3333 |  | 249.5 | 233938 | 250.8333 | 235304.6667 | 252.1667 | 235938 | 247.5 | 233938
258.1667 | 194981.6667 |  | 260.5 | 233938 | 261.8333 | 235304.6667 | 262.8333 | 235938 | 258.1667 | 194981.6667
268.8333 | 234371.3333 |  | 271.5 | 233938 | 272.5 | 235304.6667 | 273.8333 | 235938 | 268.8333 | 233938
279.5 | 234371.3333 |  | 282.1667 | 233938 | 283.1667 | 235304.6667 | 284.5 | 196548.3333 | 279.5 | 196548.3333
290.5 | 234371.3333 |  | 292.8333 | 233938 | 294.1667 | 235304.6667 | 295.1667 | 235938 | 290.5 | 233938
301.5 | 234371.3333 |  | 303.5 | 194731.6667 | 304.8333 | 196181.6667 | 306.1667 | 235938 | 301.5 | 194731.6667
312.1667 | 234371.3333 |  | 314.5 | 194815 | 315.8333 | 235304.6667 | 316.8333 | 235938 | 312.1667 | 194815
322.8333 | 234371.3333 |  | 325.5 | 233938 | 326.5 | 196148.3333 | 327.8333 | 235938 | 322.8333 | 196148.3333
333.5 | 234371.3333 |  | 336.1667 | 233938 | 337.1667 | 235304.6667 | 338.5 | 235938 | 333.5 | 233938
344.5 | 234371.3333 |  | 346.8333 | 233938 | 348.1667 | 235304.6667 | 349.1667 | 235938 | 344.5 | 233938
355.5 | 234371.3333 |  | 357.5 | 233938 | 358.8333 | 235304.6667 | 360.1667 | 235938 | 355.5 | 233938
366.1667 | 234371.3333 |  | 368.5 | 233938 | 369.8333 | 235304.6667 | 370.8333 | 235938 | 366.1667 | 233938
376.8333 | 234371.3333 |  | 379.5 | 233938 | 380.5 | 235304.6667 | 381.8333 | 235938 | 376.8333 | 233938
387.5 | 234371.3333 |  | 390.1667 | 233938 | 391.1667 | 235304.6667 | 392.5 | 235938 | 387.5 | 233938
398.5 | 234371.3333 |  | 400.8333 | 194815 | 402.1667 | 235304.6667 | 403.1667 | 235938 | 398.5 | 194815
409.3333 | 234371.3333 |  | 411.5 | 233938 | 412.8333 | 235304.6667 | 414 | 235938 | 409.3333 | 233938
420.1667 | 234371.3333 |  | 422.5 | 233938 | 423.8333 | 235304.6667 | 424.8333 | 235938 | 420.1667 | 233938
430.8333 | 234371.3333 |  | 433.5 | 233938 | 434.5 | 235304.6667 | 435.8333 | 235938 | 430.8333 | 233938
441.5 | 234371.3333 |  | 444 | 233938 | 445.1667 | 235304.6667 | 446.3333 | 235938 | 441.5 | 233938
452.5 | 234371.3333 |  | 454.6667 | 233938 | 456 | 235304.6667 | 457.1667 | 235938 | 452.5 | 233938
463.5 | 234371.3333 |  | 465.5 | 233938 | 466.8333 | 235304.6667 | 468.1667 | 235938 | 463.5 | 233938
474.1667 | 195215 |  | 476.5 | 233938 | 477.8333 | 235304.6667 | 478.8333 | 235938 | 474.1667 | 195215
484.8333 | 234371.3333 |  | 487.5 | 233938 | 488.5 | 235304.6667 | 489.8333 | 235938 | 484.8333 | 233938
495.5 | 234371.3333 |  | 498.1667 | 233938 | 499.1667 | 235304.6667 | 500.5 | 235938 | 495.5 | 233938
506.5 | 234371.3333 |  | 508.6667 | 233938 | 510 | 235304.6667 | 511.1667 | 235938 | 506.5 | 233938
517.3333 | 234371.3333 |  | 519.5 | 195248.3333 | 520.8333 | 235304.6667 | 522 | 235938 | 517.3333 | 195248.3333
528 | 234371.3333 |  | 530.5 | 233938 | 531.6667 | 195881.6667 | 532.8333 | 235938 | 528 | 195881.6667
538.6667 | 234371.3333 |  | 541.3333 | 184416465.8133 | 542.3333 | 235304.6667 | 543.6667 | 235938 | 538.6667 | 234371.3333
549.5 | 195681.6667 |  | 552 | 233938 | 553.1667 | 235304.6667 | 554.3333 | 235938 | 549.5 | 195681.6667
560.5 | 234371.3333 |  | 562.8333 | 233938 | 564.1667 | 196181.6667 | 565.1667 | 235938 | 560.5 | 196181.6667
571.3333 | 234371.3333 |  | 573.5 | 233938 | 574.8333 | 235304.6667 | 576 | 235938 | 571.3333 | 233938
582.1667 | 234371.3333 |  | 584.5 | 233938 | 585.8333 | 235304.6667 | 586.8333 | 196515 | 582.1667 | 196515
592.8333 | 234371.3333 |  | 595.5 | 184455155.48 | 596.5 | 235304.6667 | 597.8333 | 235938 | 592.8333 | 234371.3333
603.5 | 194981.6667 |  | 606.1667 | 233938 | 607.1667 | 235304.6667 | 608.5 | 196548.3333 | 603.5 | 194981.6667
614.5 | 234371.3333 |  | 616.8333 | 233938 | 618.1667 | 196148.3333 | 619.1667 | 235938 | 614.5 | 196148.3333
625.5 | 234371.3333 |  | 627.5 | 233938 | 628.8333 | 235304.6667 | 630.1667 | 235938 | 625.5 | 233938
636.1667 | 183985712.8133 |  | 638.5 | 233938 | 639.8333 | 235304.6667 | 640.8333 | 235938 | 636.1667 | 233938
646.8333 | 234371.3333 |  | 649.5 | 233938 | 650.3333 | 235304.6667 | 651.6667 | 235938 | 646.8333 | 233938
657.5 | 234371.3333 |  | 660 | 233938 | 661.1667 | 235304.6667 | 662.3333 | 235938 | 657.5 | 233938
668.5 | 234371.3333 |  | 670.6667 | 233938 | 672 | 235304.6667 | 673.1667 | 235938 | 668.5 | 233938
679.5 | 234371.3333 |  | 681.5 | 233938 | 682.8333 | 235304.6667 | 684.1667 | 235938 | 679.5 | 233938
690.1667 | 234371.3333 |  | 692.5 | 233938 | 693.8333 | 235304.6667 | 694.8333 | 235938 | 690.1667 | 233938
700.8333 | 234371.3333 |  | 703.5 | 233938 | 704.5 | 235304.6667 | 705.8333 | 235938 | 700.8333 | 233938
711.5 | 234371.3333 |  | 714.1667 | 233938 | 715.1667 | 235304.6667 | 716.5 | 235938 | 711.5 | 233938
722.5 | 234371.3333 |  | 724.8333 | 233938 | 726.1667 | 235304.6667 | 727.1667 | 235938 | 722.5 | 233938
733.5 | 234371.3333 |  | 735.5 | 233938 | 736.8333 | 235304.6667 | 738.1667 | 235938 | 733.5 | 233938
744 | 234371.3333 |  | 746.5 | 233938 | 747.6667 | 235304.6667 | 748.8333 | 235938 | 744 | 233938
754.6667 | 234371.3333 |  | 757.3333 | 233938 | 758.3333 | 235304.6667 | 759.6667 | 235938 | 754.6667 | 233938
765.5 | 160843.9556 |  | 768 | 233938 | 769.1667 | 235304.6667 | 770.3333 | 16673.8577 | 765.5 | 16673.8577
776.5 | 23675.5033 |  | 778.8333 | 233938 | 780.1667 | 235304.6667 | 781.1667 | 2986.2727 | 776.5 | 2986.2727
787.5 | 4453.4551 |  | 789.5 | 233938 | 790.8333 | 235304.6667 | 792.1667 | 1468.847 | 787.5 | 1468.847
798 | 2296.6172 |  | 800.5 | 839142.6985 | 801.6667 | 43131.5339 | 802.8333 | 808.3994 | 798 | 808.3994
808.6667 | 1182.6407 |  | 811.3333 | 15953.0004 | 812.3333 | 3482.3901 | 813.6667 | 766.1839 | 808.6667 | 766.1839
819.5 | 19447.2669 |  | 822.1667 | 2074.3731 | 823.1667 | 3714.444 | 824.5 | 711.9019 | 819.5 | 711.9019
830.5 | 1118.3511 |  | 833 | 3637.7503 | 834.3333 | 1864.2632 | 835.1667 | 625.9883 | 830.5 | 625.9883
841.3333 | 795.7255 |  | 843.5 | 1990.5819 | 844.8333 | 1984.9871 | 846 | 615.2042 | 841.3333 | 615.2042
852 | 9288.211 |  | 854.5 | 1340.7892 | 855.6667 | 1237.6126 | 856.8333 | 600.747 | 852 | 600.747
862.6667 | 912.1922 |  | 865.3333 | 4555.9716 | 866.5 | 822.4164 | 867.8333 | 631.0289 | 862.6667 | 631.0289
873.5 | 756.6176 |  | 876 | 473.8773 | 877.1667 | 1267.6519 | 878.3333 | 622.118 | 873.5 | 473.8773
884.5 | 535.0142 |  | 886.6667 | 1266.7977 | 888 | 511.6037 | 889.1667 | 1305.6643 | 884.5 | 511.6037
895.3333 | 536.9571 |  | 897.5 | 576.9803 | 898.8333 | 1402.1284 | 900 | 870.5269 | 895.3333 | 536.9571
906 | 3091.3117 |  | 908.5 | 835.3546 | 909.6667 | 714.4175 | 910.8333 | 37111.4124 | 906 | 714.4175
916.6667 | 1329.2865 |  | 919.3333 | 708.2713 | 920.1667 | 3006.1996 | 921.5 | 358.126 | 916.6667 | 358.126
927.5 | 361.1291 |  | 930 | 406.8178 | 931.1667 | 514.0438 | 932.3333 | 759.8919 | 927.5 | 361.1291
938.5 | 1455.6235 |  | 940.6667 | 6497.5011 | 942 | 336.5015 | 943.1667 | 612.0821 | 938.5 | 336.5015
949.3333 | 440.5122 |  | 951.5 | 1158.3991 | 952.8333 | 238.7797 | 954 | 2268.4954 | 949.3333 | 238.7797
960 | 537.7186 |  | 962.5 | 738.1922 | 963.6667 | 334.2958 | 964.8333 | 1563.7597 | 960 | 334.2958
970.6667 | 524.1707 |  | 973.3333 | 247.1988 | 974.3333 | 296.5563 | 975.6667 | 240.301 | 970.6667 | 240.301
981.5 | 449.2136 |  | 984 | 390.7209 | 985.1667 | 401.4054 | 986.3333 | 404.6364 | 981.5 | 390.7209
992.5 | 249.7205 |  | 994.6667 | 2466.1176 | 996 | 222.0964 | 997.1667 | 340.7313 | 992.5 | 222.0964
1003.3333 | 82.7946 |  | 1005.5 | 80.5091 | 1006.8333 | 1118.2085 | 1008 | 226.5749 | 1003.3333 | 80.5091
1014 | 1554.4648 |  | 1016.5 | 138.7549 | 1017.6667 | 169.7842 | 1018.8333 | 159.737 | 1014 | 138.7549
1024.6667 | 703.9203 |  | 1027.3333 | 2807.0951 | 1028.1667 | 208.9364 | 1029.5 | 253.5936 | 1024.6667 | 208.9364
1035.5 | 300.1572 |  | 1038 | 375.8132 | 1039.1667 | 383.5671 | 1040.3333 | 536.8782 | 1035.5 | 300.1572
1046.5 | 617.9078 |  | 1048.6667 | 416.0376 | 1050 | 6952.0349 | 1051.1667 | 455.2561 | 1046.5 | 416.0376
1057.3333 | 241.7407 |  | 1059.5 | 117.304 | 1060.8333 | 123.242 | 1062 | 642.4035 | 1057.3333 | 117.304
1068 | 126.7676 |  | 1070.5 | 237.58 | 1071.6667 | 93.7072 | 1072.8333 | 262.5896 | 1068 | 93.7072
1078.6667 | 704.8535 |  | 1081.3333 | 249.8466 | 1082.3333 | 245.2292 | 1083.6667 | 153.5834 | 1078.6667 | 153.5834
1089.5 | 94.2734 |  | 1092 | 118.5488 | 1093.1667 | 8742.1817 | 1094.3333 | 109.6341 | 1089.5 | 94.2734
1100.5 | 40.1253 |  | 1102.6667 | 134.3356 | 1104 | 180.9971 | 1105.1667 | 168.766 | 1100.5 | 40.1253
1111.3333 | 450.6426 |  | 1113.5 | 182.8899 | 1114.8333 | 78.4407 | 1116 | 651.6221 | 1111.3333 | 78.4407
1122 | 469.2336 |  | 1124.5 | 435.7253 | 1125.6667 | 247.8163 | 1126.8333 | 66.9227 | 1122 | 66.9227
1132.6667 | 20.4429 |  | 1135.3333 | 98.5379 | 1136.3333 | 146.0191 | 1137.6667 | 215.3234 | 1132.6667 | 20.4429
1143.5 | 9.0507 |  | 1146 | 10.7081 | 1147.1667 | 46.4284 | 1148.3333 | 14.8351 | 1143.5 | 9.0507
1154.5 | 16.9123 |  | 1156.6667 | 10.8854 | 1158 | 23.8687 | 1159.1667 | 11.9693 | 1154.5 | 10.8854
1165.1667 | 13.0923 |  | 1167.5 | 32.6738 | 1168.8333 | 30.3574 | 1169.8333 | 3.2657 | 1165.1667 | 3.2657
1176 | 44.5515 |  | 1178.5 | 45.8587 | 1179.6667 | 19.7471 | 1180.8333 | 17.05 | 1176 | 17.05
1186.5 | 3.1686 |  | 1189.1667 | 6.2994 | 1190.3333 | 18.1491 | 1191.6667 | 50.5568 | 1186.5 | 3.1686
1197.5 | 212.8965 |  | 1200 | 9.7033 | 1201.1667 | 21.0064 | 1202.3333 | 31.0194 | 1197.5 | 9.7033
1208.5 | 24.7232 |  | 1210.6667 | 26.2991 | 1212 | 9.6479 | 1213.1667 | 32.2229 | 1208.5 | 9.6479
1219.1667 | 29.9589 |  | 1221.5 | 11.2847 | 1222.8333 | 19.108 | 1223.8333 | 26.8198 | 1219.1667 | 11.2847
1230 | 35.884 |  | 1232.5 | 29.1976 | 1233.6667 | 12.3408 | 1234.8333 | 30.3316 | 1230 | 12.3408
1240.6667 | 128.3223 |  | 1243.3333 | 17.855 | 1244.1667 | 19.1845 | 1245.5 | 81.8156 | 1240.6667 | 17.855
1251.5 | 22.5072 |  | 1253.8333 | 44.1114 | 1255.1667 | 8.8805 | 1256.1667 | 51.4377 | 1251.5 | 8.8805
1262.5 | 26.2503 |  | 1264.6667 | 25.0911 | 1266 | 18.0471 | 1267.1667 | 44.3994 | 1262.5 | 18.0471
1273.1667 | 18.6404 |  | 1275.5 | 39.5181 | 1276.8333 | 27.4559 | 1277.8333 | 29.7684 | 1273.1667 | 18.6404
1283.8333 | 862.7943 |  | 1286.5 | 20.351 | 1287.5 | 10.2028 | 1288.8333 | 60.8126 | 1283.8333 | 10.2028
1294.5 | 30.9568 |  | 1297.1667 | 91.6309 | 1298.1667 | 64.7794 | 1299.5 | 17.154 | 1294.5 | 17.154
1305.5 | 28.5901 |  | 1307.8333 | 29.3794 | 1309.1667 | 67.6441 | 1310.1667 | 30.1643 | 1305.5 | 28.5901
1316.5 | 30.0263 |  | 1318.6667 | 18.6234 | 1320 | 58.584 | 1321.1667 | 36.208 | 1316.5 | 18.6234
1327.3333 | 23.7565 |  | 1329.5 | 31.9971 | 1330.8333 | 30.9562 | 1332 | 52.1584 | 1327.3333 | 23.7565
1338 | 25.2402 |  | 1340.5 | 10.6587 | 1341.6667 | 26.1351 | 1342.8333 | 180.3479 | 1338 | 10.6587
1348.6667 | 10.5717 |  | 1351.3333 | 36.4263 | 1352.3333 | 20.5984 | 1353.6667 | 19.8897 | 1348.6667 | 10.5717
1359.5 | 14.7022 |  | 1361.8333 | 127.164 | 1363.1667 | 28.3401 | 1364.1667 | 18.4272 | 1359.5 | 14.7022
1370.5 | 23.5228 |  | 1372.6667 | 17.8307 | 1374 | 27.9803 | 1375.1667 | 18.6942 | 1370.5 | 17.8307
1381.1667 | 1.6273 |  | 1383.5 | 44.7481 | 1384.8333 | 3.8969 | 1385.8333 | 18.8175 | 1381.1667 | 1.6273
1392 | 48.5967 |  | 1394.5 | 53.6501 | 1395.6667 | 30.1135 | 1396.8333 | 5.7282 | 1392 | 5.7282
1402.6667 | 30.2753 |  | 1405.3333 | 17.5709 | 1406.1667 | 28.1644 | 1407.5 | 182.0711 | 1402.6667 | 17.5709
1413.5 | 8.2948 |  | 1415.8333 | 31.5459 | 1417.1667 | 12.3691 | 1418.1667 | 18.5763 | 1413.5 | 8.2948
1424.5 | 8.6344 |  | 1426.6667 | 28.2124 | 1428 | 23.9142 | 1429.1667 | 18.5691 | 1424.5 | 8.6344
1435.1667 | 22.8942 |  | 1437.5 | 545.7764 | 1438.8333 | 3.8386 | 1439.8333 | 13.4217 | 1435.1667 | 3.8386

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 3 |  |  | 2006-07-05 | 14:09
38903.5888 | 1 | 1 | 1 | XLPE | 3-C | Tray
38903.5889 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38903.5891 | 1 | 0 | 1
38903.5892 | 1 | 0 | 1
38903.5893 | 1 | 0 | 1
38903.5894 | 1 | 0 | 1
38903.5896 | 1 | 0 | 1
38903.5897 | 1 | 0 | 1
38903.5898 | 1 | 0 | 1
38903.5899 | 1 | 0 | 1
38903.5901 | 1 | 0 | 1
38903.5902 | 1 | 0 | 1
38903.5903 | 1 | 0 | 1
38903.5905 | 1 | 0 | 1
38903.5906 | 1 | 0 | 1
38903.5907 | 1 | 0 | 1
38903.5908 | 1 | 0 | 1
38903.5909 | 1 | 0 | 1
38903.5911 | 1 | 0 | 1
38903.5912 | 2 | 0 | 1
38903.5913 | 1 | 0 | 1
38903.5914 | 1 | 0 | 1
38903.5916 | 1 | 0 | 1
38903.5917 | 1 | 0 | 1
38903.5918 | 1 | 0 | 1
38903.5919 | 1 | 0 | 1
38903.5921 | 1 | 0 | 1
38903.5922 | 1 | 0 | 1
38903.5923 | 1 | 0 | 1
38903.5925 | 1 | 0 | 1
38903.5926 | 1 | 0 | 1
38903.5927 | 1 | 0 | 1
38903.5928 | 1 | 0 | 1
38903.593 | 1 | 0 | 1
38903.5931 | 1 | 0 | 1
38903.5932 | 1 | 0 | 1
38903.5933 | 1 | 0 | 1
38903.5934 | 1 | 0 | 1
38903.5936 | 1 | 0 | 1
38903.5937 | 1 | 0 | 1
38903.5938 | 1 | 0 | 1
38903.5939 | 1 | 0 | 1
38903.5941 | 1 | 0 | 1
38903.5942 | 1 | 0 | 1
38903.5943 | 1 | 0 | 1
38903.5944 | 1 | 0 | 1
38903.5946 | 1 | 0 | 1
38903.5947 | 1 | 0 | 1
38903.5948 | 1 | 0 | 1
38903.5949 | 1 | 0 | 1
38903.5951 | 1 | 0 | 1
38903.5952 | 1 | 0 | 1
38903.5953 | 1 | 0 | 1
38903.5955 | 1 | 0 | 1
38903.5956 | 1 | 0 | 1
38903.5957 | 1 | 0 | 1
38903.5958 | 1 | 0 | 1
38903.5959 | 1 | 0 | 1
38903.5961 | 1 | 0 | 1
38903.5962 | 2 | 0 | 1
38903.5963 | 1 | 0 | 1
38903.5964 | 1 | 0 | 1
38903.5966 | 1 | 0 | 1
38903.5967 | 1 | 0 | 1
38903.5968 | 1 | 0 | 1
38903.5969 | 1 | 0 | 1
38903.5971 | 1 | 0 | 1
38903.5972 | 1 | 0 | 1
38903.5973 | 1 | 0 | 1
38903.5974 | 1 | 0 | 1
38903.5976 | 1 | 0 | 1
38903.5977 | 1 | 0 | 1
38903.5978 | 1 | 0 | 1
38903.598 | 1 | 0 | 1
38903.5981 | 1 | 0 | 1
38903.5982 | 1 | 0 | 1
38903.5983 | 1 | 0 | 1
38903.5984 | 1 | 0 | 1
38903.5986 | 1 | 0 | 1
38903.5987 | 1 | 0 | 1
38903.5988 | 5 | 0 | 1
38903.5989 | 38 | 0 | 1
38903.5991 | 84 | 0 | 1
38903.5992 | 199 | 1 | 1
38903.5993 | 365 | 104 | 1
38903.5994 | 500 | 159 | 1
38903.5996 | 527 | 228 | 1
38903.5997 | 496 | 227 | 1
38903.5998 | 557 | 279 | 1
38903.5999 | 1043 | 770 | 1
38903.6001 | 1282 | 1047 | 1
38903.6002 | 1343 | 801 | 1
38903.6003 | 1043 | 812 | 1
38903.6005 | 1235 | 889 | 1
38903.6006 | 1343 | 951 | 1
38903.6007 | 1100 | 739 | 1
38903.6008 | 1149 | 812 | 1
38903.6009 | 1280 | 875 | 1
38903.6011 | 1197 | 763 | 1
38903.6012 | 1436 | 824 | 1
38903.6013 | 1226 | 675 | 1
38903.6014 | 1461 | 564 | 1
38903.6016 | 1451 | 454 | 1
38903.6017 | 1519 | 526 | 1
38903.6018 | 1402 | 877 | 1
38903.6019 | 1303 | 737 | 1
38903.6021 | 1583 | 477 | 1
38903.6022 | 1558 | 540 | 1
38903.6023 | 1764 | 522 | 1
38903.6024 | 1501 | 669 | 1
38903.6026 | 1752 | 416 | 1
38903.6027 | 1801 | 574 | 1
38903.6028 | 1612 | 546 | 1
38903.603 | 1770 | 650 | 1
38903.6031 | 1535 | 432 | 1
38903.6032 | 2305 | 66 | 1
38903.6033 | 2250 | 65 | 1
38903.6034 | 1948 | 59 | 1
38903.6036 | 2283 | 73 | 1
38903.6037 | 1965 | 65 | 1
38903.6038 | 2066 | 77 | 1
38903.6039 | 2003 | 81 | 1
38903.6041 | 2055 | 92 | 1
38903.6042 | 1871 | 87 | 1
38903.6043 | 1829 | 95 | 1
38903.6044 | 1981 | 102 | 1
38903.6046 | 2057 | 108 | 1
38903.6047 | 1861 | 96 | 1
38903.6048 | 2271 | 124 | 1
38903.6049 | 1782 | 98 | 1
38903.6051 | 1883 | 94 | 1
38903.6052 | 1757 | 129 | 1
38903.6053 | 2265 | 123 | 1
38903.6055 | 2253 | 104 | 1
38903.6056 | 2210 | 101 | 1
38903.6057 | 1895 | 87 | 1
38903.6058 | 2305 | 105 | 1
38903.6059 | 2166 | 93 | 1
38903.6061 | 2108 | 97 | 1
38903.6062 | 1946 | 88 | 1
38903.6063 | 2026 | 83 | 1
38903.6064 | 2035 | 78 | 1
38903.5888 | 1 | 0 | 2
38903.589 | 1 | 0 | 2
38903.5891 | 1 | 0 | 2
38903.5892 | 1 | 0 | 2
38903.5893 | 1 | 0 | 2
38903.5895 | 1 | 0 | 2
38903.5896 | 1 | 0 | 2
38903.5897 | 1 | 0 | 2
38903.5898 | 1 | 0 | 2
38903.59 | 1 | 0 | 2
38903.5901 | 1 | 0 | 2
38903.5902 | 1 | 0 | 2
38903.5903 | 1 | 0 | 2
38903.5905 | 1 | 0 | 2
38903.5906 | 1 | 0 | 2
38903.5907 | 1 | 0 | 2
38903.5908 | 2 | 0 | 2
38903.591 | 1 | 0 | 2
38903.5911 | 1 | 0 | 2
38903.5912 | 1 | 0 | 2
38903.5913 | 1 | 0 | 2
38903.5915 | 1 | 0 | 2
38903.5916 | 1 | 0 | 2
38903.5917 | 1 | 0 | 2
38903.5918 | 2 | 0 | 2
38903.592 | 1 | 0 | 2
38903.5921 | 1 | 0 | 2
38903.5922 | 1 | 0 | 2
38903.5923 | 1 | 0 | 2
38903.5925 | 1 | 0 | 2
38903.5926 | 1 | 0 | 2
38903.5927 | 1 | 0 | 2
38903.5928 | 1 | 0 | 2
38903.593 | 1 | 0 | 2
38903.5931 | 1 | 0 | 2
38903.5932 | 1 | 0 | 2
38903.5933 | 1 | 0 | 2
38903.5935 | 1 | 0 | 2
38903.5936 | 1 | 0 | 2
38903.5937 | 1 | 0 | 2
38903.5938 | 1 | 0 | 2
38903.594 | 1 | 0 | 2
38903.5941 | 1 | 0 | 2
38903.5942 | 1 | 0 | 2
38903.5943 | 1 | 0 | 2
38903.5945 | 1 | 0 | 2
38903.5946 | 1 | 0 | 2
38903.5947 | 1 | 0 | 2
38903.5948 | 1 | 0 | 2
38903.595 | 1 | 0 | 2
38903.5951 | 1 | 0 | 2
38903.5952 | 1 | 0 | 2
38903.5953 | 1 | 0 | 2
38903.5955 | 1 | 0 | 2
38903.5956 | 1 | 0 | 2
38903.5957 | 1 | 0 | 2
38903.5958 | 2 | 0 | 2
38903.596 | 1 | 0 | 2
38903.5961 | 2 | 0 | 2
38903.5962 | 1 | 0 | 2
38903.5963 | 1 | 0 | 2
38903.5965 | 1 | 0 | 2
38903.5966 | 1 | 0 | 2
38903.5967 | 1 | 1 | 2
38903.5968 | 1 | 0 | 2
38903.597 | 1 | 0 | 2
38903.5971 | 1 | 0 | 2
38903.5972 | 1 | 0 | 2
38903.5973 | 1 | 0 | 2
38903.5975 | 1 | 0 | 2
38903.5976 | 1 | 0 | 2
38903.5977 | 1 | 0 | 2
38903.5978 | 1 | 0 | 2
38903.598 | 1 | 0 | 2
38903.5981 | 1 | 0 | 2
38903.5982 | 1 | 0 | 2
38903.5983 | 1 | 0 | 2
38903.5985 | 1 | 0 | 2
38903.5986 | 1 | 0 | 2
38903.5987 | 1 | 0 | 2
38903.5988 | 1 | 0 | 2
38903.599 | 1 | 0 | 2
38903.5991 | 1 | 0 | 2
38903.5992 | 8 | 1 | 2
38903.5993 | 309 | 186 | 2
38903.5995 | 308 | 189 | 2
38903.5996 | 423 | 307 | 2
38903.5997 | 501 | 330 | 2
38903.5998 | 562 | 344 | 2
38903.6 | 1232 | 949 | 2
38903.6001 | 1224 | 934 | 2
38903.6002 | 1190 | 893 | 2
38903.6003 | 1309 | 952 | 2
38903.6005 | 1304 | 999 | 2
38903.6006 | 1315 | 992 | 2
38903.6007 | 1130 | 822 | 2
38903.6008 | 1400 | 938 | 2
38903.601 | 1369 | 840 | 2
38903.6011 | 1206 | 716 | 2
38903.6012 | 1463 | 811 | 2
38903.6013 | 1212 | 674 | 2
38903.6015 | 1437 | 514 | 2
38903.6016 | 1384 | 443 | 2
38903.6017 | 1696 | 550 | 2
38903.6018 | 1359 | 953 | 2
38903.602 | 1524 | 842 | 2
38903.6021 | 1650 | 504 | 2
38903.6022 | 1843 | 543 | 2
38903.6023 | 1489 | 413 | 2
38903.6025 | 1639 | 704 | 2
38903.6026 | 1599 | 411 | 2
38903.6027 | 1766 | 409 | 2
38903.6028 | 1703 | 430 | 2
38903.603 | 1320 | 528 | 2
38903.6031 | 2176 | 73 | 2
38903.6032 | 2050 | 57 | 2
38903.6033 | 2112 | 60 | 2
38903.6035 | 2262 | 74 | 2
38903.6036 | 2027 | 72 | 2
38903.6037 | 2245 | 70 | 2
38903.6038 | 1858 | 80 | 2
38903.604 | 2203 | 99 | 2
38903.6041 | 2074 | 95 | 2
38903.6042 | 2212 | 111 | 2
38903.6043 | 1891 | 95 | 2
38903.6045 | 1763 | 90 | 2
38903.6046 | 1915 | 100 | 2
38903.6047 | 2209 | 126 | 2
38903.6048 | 2188 | 123 | 2
38903.605 | 2125 | 118 | 2
38903.6051 | 1992 | 99 | 2
38903.6052 | 1815 | 148 | 2
38903.6053 | 2278 | 123 | 2
38903.6055 | 1776 | 85 | 2
38903.6056 | 1831 | 71 | 2
38903.6057 | 1865 | 72 | 2
38903.6058 | 1963 | 85 | 2
38903.606 | 1817 | 66 | 2
38903.6061 | 1902 | 91 | 2
38903.6062 | 1806 | 61 | 2
38903.6063 | 2303 | 109 | 2
38903.6065 | 1878 | 76 | 2
38903.5888 | 1 | 0 | 3
38903.589 | 1 | 0 | 3
38903.5891 | 1 | 0 | 3
38903.5892 | 1 | 0 | 3
38903.5893 | 1 | 0 | 3
38903.5895 | 1 | 0 | 3
38903.5896 | 1 | 0 | 3
38903.5897 | 1 | 0 | 3
38903.5898 | 1 | 0 | 3
38903.59 | 1 | 0 | 3
38903.5901 | 1 | 0 | 3
38903.5902 | 1 | 0 | 3
38903.5903 | 1 | 0 | 3
38903.5905 | 1 | 0 | 3
38903.5906 | 1 | 0 | 3
38903.5907 | 1 | 0 | 3
38903.5908 | 2 | 0 | 3
38903.591 | 1 | 0 | 3
38903.5911 | 1 | 0 | 3
38903.5912 | 1 | 0 | 3
38903.5913 | 1 | 0 | 3
38903.5915 | 1 | 0 | 3
38903.5916 | 1 | 0 | 3
38903.5917 | 1 | 0 | 3
38903.5918 | 1 | 0 | 3
38903.592 | 2 | 0 | 3
38903.5921 | 1 | 0 | 3
38903.5922 | 1 | 0 | 3
38903.5923 | 1 | 0 | 3
38903.5925 | 2 | 0 | 3
38903.5926 | 1 | 0 | 3
38903.5927 | 1 | 0 | 3
38903.5928 | 1 | 0 | 3
38903.593 | 1 | 0 | 3
38903.5931 | 1 | 0 | 3
38903.5932 | 1 | 0 | 3
38903.5933 | 1 | 0 | 3
38903.5935 | 1 | 0 | 3
38903.5936 | 1 | 0 | 3
38903.5937 | 1 | 0 | 3
38903.5938 | 1 | 0 | 3
38903.594 | 1 | 0 | 3
38903.5941 | 1 | 0 | 3
38903.5942 | 1 | 0 | 3
38903.5943 | 1 | 0 | 3
38903.5945 | 1 | 0 | 3
38903.5946 | 1 | 0 | 3
38903.5947 | 1 | 0 | 3
38903.5948 | 1 | 0 | 3
38903.595 | 1 | 0 | 3
38903.5951 | 1 | 0 | 3
38903.5952 | 1 | 0 | 3
38903.5953 | 2 | 0 | 3
38903.5955 | 1 | 0 | 3
38903.5956 | 1 | 0 | 3
38903.5957 | 1 | 0 | 3
38903.5958 | 1 | 0 | 3
38903.596 | 1 | 0 | 3
38903.5961 | 1 | 0 | 3
38903.5962 | 1 | 0 | 3
38903.5963 | 1 | 0 | 3
38903.5965 | 1 | 0 | 3
38903.5966 | 1 | 0 | 3
38903.5967 | 1 | 0 | 3
38903.5968 | 1 | 0 | 3
38903.597 | 1 | 0 | 3
38903.5971 | 1 | 0 | 3
38903.5972 | 1 | 1 | 3
38903.5973 | 1 | 0 | 3
38903.5975 | 1 | 0 | 3
38903.5976 | 1 | 0 | 3
38903.5977 | 1 | 0 | 3
38903.5978 | 1 | 0 | 3
38903.598 | 1 | 0 | 3
38903.5981 | 1 | 0 | 3
38903.5982 | 1 | 0 | 3
38903.5983 | 1 | 0 | 3
38903.5985 | 1 | 0 | 3
38903.5986 | 1 | 0 | 3
38903.5987 | 1 | 0 | 3
38903.5988 | 11 | 0 | 3
38903.599 | 50 | 0 | 3
38903.5991 | 96 | 0 | 3
38903.5992 | 397 | 116 | 3
38903.5993 | 463 | 173 | 3
38903.5995 | 536 | 264 | 3
38903.5996 | 668 | 387 | 3
38903.5997 | 556 | 300 | 3
38903.5998 | 664 | 446 | 3
38903.6 | 1033 | 909 | 3
38903.6001 | 1330 | 1052 | 3
38903.6002 | 1302 | 992 | 3
38903.6003 | 1097 | 799 | 3
38903.6005 | 1358 | 967 | 3
38903.6006 | 1092 | 761 | 3
38903.6007 | 1146 | 775 | 3
38903.6008 | 1200 | 744 | 3
38903.601 | 1442 | 882 | 3
38903.6011 | 1401 | 779 | 3
38903.6012 | 1312 | 745 | 3
38903.6013 | 1416 | 784 | 3
38903.6015 | 1859 | 469 | 3
38903.6017 | 1264 | 595 | 3
38903.6018 | 1199 | 761 | 3
38903.602 | 1242 | 614 | 3
38903.6021 | 1465 | 381 | 3
38903.6022 | 1552 | 447 | 3
38903.6023 | 1532 | 449 | 3
38903.6025 | 1534 | 354 | 3
38903.6026 | 1823 | 344 | 3
38903.6027 | 1441 | 513 | 3
38903.6028 | 1810 | 541 | 3
38903.603 | 1767 | 549 | 3
38903.6031 | 2267 | 68 | 3
38903.6032 | 1938 | 53 | 3
38903.6033 | 1846 | 58 | 3
38903.6035 | 2322 | 73 | 3
38903.6036 | 2262 | 70 | 3
38903.6037 | 2027 | 66 | 3
38903.6038 | 2171 | 94 | 3
38903.604 | 2290 | 87 | 3
38903.6041 | 1819 | 88 | 3
38903.6042 | 1756 | 89 | 3
38903.6043 | 2020 | 100 | 3
38903.6045 | 1955 | 96 | 3
38903.6046 | 2110 | 114 | 3
38903.6047 | 2119 | 116 | 3
38903.6048 | 2006 | 110 | 3
38903.605 | 2153 | 143 | 3
38903.6051 | 2184 | 123 | 3
38903.6052 | 2093 | 140 | 3
38903.6053 | 1965 | 95 | 3
38903.6055 | 2165 | 103 | 3
38903.6056 | 2195 | 99 | 3
38903.6057 | 2127 | 106 | 3
38903.6058 | 2180 | 101 | 3
38903.606 | 2061 | 93 | 3
38903.6061 | 1763 | 87 | 3
38903.6062 | 2154 | 70 | 3
38903.6063 | 2296 | 77 | 3
38903.6065 | 1991 | 74 | 3
38903.5889 | 1 | 0 | 4
38903.589 | 1 | 0 | 4
38903.5891 | 1 | 0 | 4
38903.5892 | 1 | 0 | 4
38903.5894 | 1 | 0 | 4
38903.5895 | 1 | 1 | 4
38903.5896 | 1 | 0 | 4
38903.5897 | 1 | 0 | 4
38903.5898 | 1 | 0 | 4
38903.59 | 1 | 0 | 4
38903.5901 | 1 | 0 | 4
38903.5902 | 1 | 0 | 4
38903.5904 | 1 | 0 | 4
38903.5906 | 1 | 0 | 4
38903.5907 | 1 | 0 | 4
38903.5909 | 1 | 0 | 4
38903.591 | 1 | 0 | 4
38903.5911 | 1 | 0 | 4
38903.5912 | 1 | 0 | 4
38903.5914 | 1 | 0 | 4
38903.5915 | 1 | 0 | 4
38903.5916 | 1 | 0 | 4
38903.5917 | 1 | 0 | 4
38903.5919 | 1 | 0 | 4
38903.592 | 1 | 0 | 4
38903.5921 | 2 | 0 | 4
38903.5922 | 1 | 0 | 4
38903.5923 | 1 | 0 | 4
38903.5925 | 1 | 0 | 4
38903.5926 | 1 | 0 | 4
38903.5927 | 1 | 0 | 4
38903.5929 | 1 | 0 | 4
38903.593 | 1 | 0 | 4
38903.5931 | 1 | 0 | 4
38903.5932 | 1 | 0 | 4
38903.5934 | 1 | 0 | 4
38903.5935 | 1 | 0 | 4
38903.5936 | 2 | 0 | 4
38903.5937 | 1 | 0 | 4
38903.5939 | 1 | 0 | 4
38903.594 | 1 | 0 | 4
38903.5941 | 1 | 0 | 4
38903.5942 | 1 | 0 | 4
38903.5944 | 1 | 0 | 4
38903.5945 | 1 | 0 | 4
38903.5946 | 1 | 0 | 4
38903.5947 | 1 | 0 | 4
38903.5948 | 1 | 0 | 4
38903.595 | 1 | 0 | 4
38903.5951 | 1 | 0 | 4
38903.5952 | 1 | 0 | 4
38903.5954 | 1 | 0 | 4
38903.5955 | 1 | 0 | 4
38903.5956 | 1 | 0 | 4
38903.5957 | 1 | 0 | 4
38903.5959 | 1 | 0 | 4
38903.596 | 1 | 0 | 4
38903.5961 | 1 | 0 | 4
38903.5962 | 1 | 0 | 4
38903.5964 | 1 | 0 | 4
38903.5965 | 1 | 0 | 4
38903.5966 | 1 | 0 | 4
38903.5967 | 1 | 0 | 4
38903.5969 | 1 | 0 | 4
38903.597 | 2 | 0 | 4
38903.5971 | 1 | 0 | 4
38903.5972 | 1 | 0 | 4
38903.5973 | 1 | 0 | 4
38903.5975 | 1 | 0 | 4
38903.5976 | 1 | 0 | 4
38903.5977 | 1 | 0 | 4
38903.5979 | 1 | 0 | 4
38903.598 | 1 | 0 | 4
38903.5981 | 1 | 0 | 4
38903.5982 | 1 | 0 | 4
38903.5984 | 1 | 0 | 4
38903.5985 | 1 | 0 | 4
38903.5986 | 1 | 0 | 4
38903.5987 | 1 | 0 | 4
38903.5989 | 1 | 0 | 4
38903.599 | 1 | 0 | 4
38903.5991 | 2 | 0 | 4
38903.5992 | 202 | 118 | 4
38903.5994 | 235 | 151 | 4
38903.5995 | 445 | 257 | 4
38903.5996 | 514 | 372 | 4
38903.5997 | 452 | 305 | 4
38903.5998 | 786 | 553 | 4
38903.6 | 1148 | 866 | 4
38903.6001 | 1088 | 813 | 4
38903.6002 | 1042 | 773 | 4
38903.6003 | 1201 | 885 | 4
38903.6005 | 1161 | 829 | 4
38903.6006 | 1168 | 813 | 4
38903.6007 | 1376 | 984 | 4
38903.6009 | 1408 | 932 | 4
38903.601 | 1214 | 789 | 4
38903.6011 | 1483 | 658 | 4
38903.6012 | 1556 | 832 | 4
38903.6014 | 1256 | 675 | 4
38903.6015 | 1706 | 421 | 4
38903.6016 | 1733 | 548 | 4
38903.6017 | 1375 | 621 | 4
38903.6019 | 1451 | 860 | 4
38903.602 | 1614 | 790 | 4
38903.6021 | 1850 | 543 | 4
38903.6022 | 1714 | 501 | 4
38903.6023 | 1802 | 506 | 4
38903.6025 | 1598 | 367 | 4
38903.6026 | 1845 | 471 | 4
38903.6027 | 1722 | 657 | 4
38903.6028 | 1399 | 446 | 4
38903.603 | 1657 | 615 | 4
38903.6031 | 1893 | 56 | 4
38903.6032 | 2306 | 64 | 4
38903.6034 | 2061 | 61 | 4
38903.6035 | 2333 | 72 | 4
38903.6036 | 2095 | 65 | 4
38903.6037 | 2017 | 61 | 4
38903.6039 | 2263 | 78 | 4
38903.604 | 1995 | 90 | 4
38903.6041 | 2163 | 101 | 4
38903.6042 | 1974 | 94 | 4
38903.6044 | 2108 | 118 | 4
38903.6045 | 2270 | 120 | 4
38903.6046 | 2267 | 100 | 4
38903.6047 | 2220 | 125 | 4
38903.6048 | 2257 | 126 | 4
38903.605 | 1933 | 146 | 4
38903.6051 | 1812 | 105 | 4
38903.6052 | 1832 | 133 | 4
38903.6053 | 2153 | 114 | 4
38903.6055 | 2034 | 88 | 4
38903.6056 | 1796 | 73 | 4
38903.6057 | 2276 | 102 | 4
38903.6059 | 2327 | 68 | 4
38903.606 | 1821 | 82 | 4
38903.6061 | 1911 | 94 | 4
38903.6062 | 2329 | 71 | 4
38903.6064 | 1965 | 84 | 4
38903.6065 | 2283 | 82 | 4
38903.5889 | 1 | 0 | 5
38903.589 | 1 | 0 | 5
38903.5891 | 1 | 0 | 5
38903.5892 | 1 | 0 | 5
38903.5894 | 1 | 0 | 5
38903.5895 | 1 | 0 | 5
38903.5896 | 1 | 0 | 5
38903.5897 | 1 | 0 | 5
38903.5899 | 1 | 0 | 5
38903.59 | 1 | 0 | 5
38903.5901 | 1 | 0 | 5
38903.5902 | 1 | 0 | 5
38903.5904 | 1 | 0 | 5
38903.5905 | 1 | 0 | 5
38903.5906 | 1 | 0 | 5
38903.5907 | 1 | 0 | 5
38903.5909 | 2 | 0 | 5
38903.591 | 1 | 0 | 5
38903.5911 | 1 | 0 | 5
38903.5912 | 1 | 0 | 5
38903.5914 | 1 | 0 | 5
38903.5915 | 1 | 0 | 5
38903.5916 | 1 | 0 | 5
38903.5917 | 1 | 0 | 5
38903.5919 | 1 | 0 | 5
38903.592 | 1 | 0 | 5
38903.5921 | 1 | 0 | 5
38903.5922 | 1 | 0 | 5
38903.5924 | 1 | 0 | 5
38903.5925 | 1 | 0 | 5
38903.5926 | 1 | 0 | 5
38903.5927 | 1 | 0 | 5
38903.5929 | 2 | 0 | 5
38903.593 | 1 | 0 | 5
38903.5931 | 1 | 0 | 5
38903.5932 | 1 | 0 | 5
38903.5934 | 1 | 0 | 5
38903.5935 | 1 | 0 | 5
38903.5936 | 1 | 0 | 5
38903.5937 | 1 | 0 | 5
38903.5939 | 1 | 0 | 5
38903.594 | 1 | 0 | 5
38903.5941 | 1 | 0 | 5
38903.5942 | 1 | 0 | 5
38903.5944 | 1 | 0 | 5
38903.5945 | 1 | 0 | 5
38903.5946 | 1 | 0 | 5
38903.5947 | 1 | 0 | 5
38903.5949 | 1 | 0 | 5
38903.595 | 1 | 0 | 5
38903.5951 | 1 | 0 | 5
38903.5952 | 1 | 0 | 5
38903.5954 | 1 | 0 | 5
38903.5955 | 1 | 0 | 5
38903.5956 | 1 | 0 | 5
38903.5957 | 1 | 0 | 5
38903.5959 | 1 | 0 | 5
38903.596 | 1 | 0 | 5
38903.5961 | 1 | 0 | 5
38903.5962 | 1 | 0 | 5
38903.5964 | 1 | 0 | 5
38903.5965 | 1 | 0 | 5
38903.5966 | 1 | 0 | 5
38903.5967 | 1 | 0 | 5
38903.5969 | 2 | 0 | 5
38903.597 | 1 | 0 | 5
38903.5971 | 1 | 0 | 5
38903.5972 | 1 | 0 | 5
38903.5974 | 1 | 0 | 5
38903.5975 | 1 | 0 | 5
38903.5976 | 1 | 0 | 5
38903.5977 | 1 | 0 | 5
38903.5979 | 1 | 0 | 5
38903.598 | 1 | 0 | 5
38903.5981 | 1 | 0 | 5
38903.5982 | 1 | 0 | 5
38903.5984 | 1 | 0 | 5
38903.5985 | 1 | 0 | 5
38903.5986 | 1 | 0 | 5
38903.5987 | 15 | 0 | 5
38903.5989 | 147 | 78 | 5
38903.599 | 347 | 249 | 5
38903.5991 | 993 | 819 | 5
38903.5992 | 717 | 552 | 5
38903.5994 | 676 | 567 | 5
38903.5995 | 569 | 434 | 5
38903.5996 | 918 | 688 | 5
38903.5997 | 772 | 647 | 5
38903.5999 | 729 | 509 | 5
38903.6 | 1206 | 921 | 5
38903.6001 | 1168 | 882 | 5
38903.6002 | 1205 | 899 | 5
38903.6004 | 1355 | 1028 | 5
38903.6005 | 1235 | 890 | 5
38903.6006 | 1353 | 958 | 5
38903.6007 | 1180 | 856 | 5
38903.6009 | 1286 | 907 | 5
38903.601 | 1256 | 745 | 5
38903.6011 | 1229 | 680 | 5
38903.6012 | 1281 | 676 | 5
38903.6014 | 1372 | 738 | 5
38903.6015 | 1889 | 445 | 5
38903.6016 | 1428 | 531 | 5
38903.6017 | 1398 | 667 | 5
38903.6019 | 1420 | 833 | 5
38903.602 | 1199 | 701 | 5
38903.6021 | 1856 | 540 | 5
38903.6022 | 1449 | 392 | 5
38903.6024 | 1767 | 591 | 5
38903.6025 | 1972 | 415 | 5
38903.6026 | 1803 | 541 | 5
38903.6027 | 1492 | 603 | 5
38903.6029 | 1471 | 524 | 5
38903.603 | 1849 | 583 | 5
38903.6031 | 1800 | 54 | 5
38903.6032 | 2154 | 55 | 5
38903.6034 | 2347 | 71 | 5
38903.6035 | 1936 | 57 | 5
38903.6036 | 2276 | 71 | 5
38903.6037 | 2116 | 65 | 5
38903.6039 | 1943 | 77 | 5
38903.604 | 2227 | 96 | 5
38903.6041 | 1951 | 93 | 5
38903.6042 | 2072 | 101 | 5
38903.6044 | 2228 | 113 | 5
38903.6045 | 1969 | 101 | 5
38903.6046 | 1902 | 103 | 5
38903.6047 | 1788 | 99 | 5
38903.6049 | 1876 | 109 | 5
38903.605 | 2245 | 121 | 5
38903.6051 | 2111 | 112 | 5
38903.6052 | 2139 | 130 | 5
38903.6054 | 2026 | 92 | 5
38903.6055 | 1915 | 86 | 5
38903.6056 | 2031 | 74 | 5
38903.6057 | 1946 | 96 | 5
38903.6059 | 2298 | 104 | 5
38903.606 | 1886 | 84 | 5
38903.6061 | 1850 | 105 | 5
38903.6062 | 2342 | 72 | 5
38903.6064 | 2139 | 71 | 5
38903.6065 | 2307 | 78 | 5
38903.5889 | 1 | 0 | 6
38903.589 | 1 | 0 | 6
38903.5891 | 1 | 0 | 6
38903.5892 | 1 | 0 | 6
38903.5894 | 1 | 0 | 6
38903.5895 | 1 | 0 | 6
38903.5896 | 1 | 0 | 6
38903.5897 | 1 | 0 | 6
38903.5899 | 1 | 0 | 6
38903.59 | 1 | 0 | 6
38903.5901 | 1 | 0 | 6
38903.5903 | 1 | 0 | 6
38903.5904 | 1 | 0 | 6
38903.5905 | 1 | 0 | 6
38903.5906 | 1 | 1 | 6
38903.5908 | 1 | 0 | 6
38903.5909 | 1 | 0 | 6
38903.591 | 1 | 1 | 6
38903.5911 | 1 | 0 | 6
38903.5912 | 1 | 0 | 6
38903.5914 | 1 | 0 | 6
38903.5915 | 1 | 0 | 6
38903.5916 | 1 | 0 | 6
38903.5917 | 1 | 0 | 6
38903.5919 | 2 | 0 | 6
38903.592 | 1 | 0 | 6
38903.5921 | 1 | 0 | 6
38903.5922 | 1 | 0 | 6
38903.5924 | 1 | 0 | 6
38903.5925 | 1 | 0 | 6
38903.5926 | 1 | 0 | 6
38903.5928 | 1 | 0 | 6
38903.5929 | 1 | 0 | 6
38903.593 | 1 | 0 | 6
38903.5931 | 2 | 0 | 6
38903.5933 | 1 | 0 | 6
38903.5934 | 1 | 0 | 6
38903.5935 | 1 | 0 | 6
38903.5936 | 1 | 0 | 6
38903.5938 | 1 | 0 | 6
38903.5939 | 1 | 0 | 6
38903.594 | 1 | 0 | 6
38903.5941 | 1 | 0 | 6
38903.5942 | 1 | 0 | 6
38903.5944 | 1 | 0 | 6
38903.5945 | 1 | 0 | 6
38903.5946 | 1 | 0 | 6
38903.5947 | 1 | 0 | 6
38903.5949 | 1 | 0 | 6
38903.595 | 1 | 0 | 6
38903.5951 | 1 | 0 | 6
38903.5953 | 1 | 0 | 6
38903.5954 | 1 | 0 | 6
38903.5955 | 1 | 0 | 6
38903.5956 | 1 | 0 | 6
38903.5958 | 1 | 0 | 6
38903.5959 | 1 | 0 | 6
38903.596 | 1 | 0 | 6
38903.5961 | 1 | 0 | 6
38903.5963 | 1 | 0 | 6
38903.5964 | 1 | 0 | 6
38903.5965 | 1 | 1 | 6
38903.5966 | 1 | 0 | 6
38903.5967 | 1 | 0 | 6
38903.5969 | 2 | 0 | 6
38903.597 | 1 | 0 | 6
38903.5971 | 1 | 0 | 6
38903.5972 | 1 | 0 | 6
38903.5974 | 1 | 0 | 6
38903.5975 | 1 | 0 | 6
38903.5976 | 1 | 0 | 6
38903.5978 | 1 | 0 | 6
38903.5979 | 1 | 0 | 6
38903.598 | 1 | 0 | 6
38903.5981 | 1 | 0 | 6
38903.5983 | 1 | 0 | 6
38903.5984 | 1 | 0 | 6
38903.5985 | 1 | 0 | 6
38903.5986 | 1 | 0 | 6
38903.5987 | 26 | 0 | 6
38903.5989 | 210 | 81 | 6
38903.599 | 389 | 186 | 6
38903.5991 | 554 | 314 | 6
38903.5992 | 672 | 427 | 6
38903.5994 | 1145 | 906 | 6
38903.5995 | 577 | 358 | 6
38903.5996 | 1135 | 875 | 6
38903.5997 | 881 | 583 | 6
38903.5999 | 798 | 557 | 6
38903.6 | 1119 | 838 | 6
38903.6001 | 1034 | 788 | 6
38903.6002 | 1335 | 1014 | 6
38903.6004 | 1301 | 962 | 6
38903.6005 | 1205 | 776 | 6
38903.6006 | 1099 | 758 | 6
38903.6008 | 1247 | 846 | 6
38903.6009 | 1215 | 888 | 6
38903.601 | 1445 | 859 | 6
38903.6011 | 1425 | 790 | 6
38903.6012 | 1354 | 709 | 6
38903.6014 | 1414 | 801 | 6
38903.6015 | 1655 | 391 | 6
38903.6016 | 1400 | 439 | 6
38903.6017 | 1454 | 579 | 6
38903.6019 | 1208 | 705 | 6
38903.602 | 1473 | 917 | 6
38903.6021 | 1751 | 465 | 6
38903.6022 | 1650 | 444 | 6
38903.6024 | 1388 | 521 | 6
38903.6025 | 1500 | 354 | 6
38903.6026 | 1588 | 558 | 6
38903.6027 | 1691 | 650 | 6
38903.6029 | 1723 | 624 | 6
38903.603 | 1599 | 655 | 6
38903.6031 | 2340 | 57 | 6
38903.6033 | 2088 | 65 | 6
38903.6034 | 1845 | 56 | 6
38903.6035 | 1791 | 60 | 6
38903.6036 | 1878 | 59 | 6
38903.6038 | 2017 | 67 | 6
38903.6039 | 2052 | 92 | 6
38903.604 | 2260 | 99 | 6
38903.6041 | 1783 | 89 | 6
38903.6042 | 1944 | 104 | 6
38903.6044 | 2021 | 110 | 6
38903.6045 | 1839 | 96 | 6
38903.6046 | 1786 | 98 | 6
38903.6047 | 1901 | 105 | 6
38903.6049 | 1912 | 111 | 6
38903.605 | 1792 | 149 | 6
38903.6051 | 2223 | 120 | 6
38903.6052 | 1785 | 77 | 6
38903.6054 | 2176 | 106 | 6
38903.6055 | 2311 | 71 | 6
38903.6056 | 2209 | 91 | 6
38903.6058 | 2126 | 116 | 6
38903.6059 | 1816 | 82 | 6
38903.606 | 2241 | 104 | 6
38903.6061 | 1819 | 66 | 6
38903.6062 | 1839 | 62 | 6
38903.6064 | 2240 | 82 | 6
38903.6065 | 1823 | 77 | 6
38903.5889 | 1 | 0 | 7
38903.589 | 1 | 0 | 7
38903.5891 | 1 | 0 | 7
38903.5893 | 1 | 0 | 7
38903.5894 | 1 | 0 | 7
38903.5895 | 1 | 0 | 7
38903.5896 | 1 | 0 | 7
38903.5898 | 1 | 0 | 7
38903.5899 | 1 | 0 | 7
38903.59 | 1 | 0 | 7
38903.5901 | 1 | 0 | 7
38903.5903 | 1 | 0 | 7
38903.5904 | 1 | 0 | 7
38903.5905 | 1 | 1 | 7
38903.5906 | 1 | 0 | 7
38903.5908 | 1 | 0 | 7
38903.5909 | 1 | 0 | 7
38903.591 | 1 | 0 | 7
38903.5911 | 1 | 0 | 7
38903.5913 | 1 | 0 | 7
38903.5914 | 1 | 0 | 7
38903.5915 | 1 | 0 | 7
38903.5916 | 1 | 0 | 7
38903.5918 | 1 | 0 | 7
38903.5919 | 1 | 0 | 7
38903.592 | 1 | 0 | 7
38903.5921 | 1 | 0 | 7
38903.5923 | 1 | 0 | 7
38903.5924 | 2 | 0 | 7
38903.5925 | 1 | 1 | 7
38903.5926 | 1 | 0 | 7
38903.5928 | 1 | 0 | 7
38903.5929 | 1 | 0 | 7
38903.593 | 1 | 0 | 7
38903.5931 | 1 | 0 | 7
38903.5933 | 1 | 0 | 7
38903.5934 | 1 | 0 | 7
38903.5935 | 2 | 0 | 7
38903.5936 | 1 | 0 | 7
38903.5938 | 1 | 0 | 7
38903.5939 | 1 | 0 | 7
38903.594 | 1 | 0 | 7
38903.5941 | 1 | 0 | 7
38903.5943 | 1 | 0 | 7
38903.5944 | 1 | 0 | 7
38903.5945 | 2 | 0 | 7
38903.5946 | 1 | 0 | 7
38903.5948 | 1 | 0 | 7
38903.5949 | 1 | 0 | 7
38903.595 | 1 | 0 | 7
38903.5951 | 1 | 0 | 7
38903.5953 | 1 | 0 | 7
38903.5954 | 1 | 0 | 7
38903.5955 | 1 | 0 | 7
38903.5956 | 1 | 0 | 7
38903.5958 | 1 | 0 | 7
38903.5959 | 1 | 0 | 7
38903.596 | 1 | 0 | 7
38903.5961 | 1 | 0 | 7
38903.5963 | 1 | 0 | 7
38903.5964 | 1 | 0 | 7
38903.5965 | 1 | 0 | 7
38903.5966 | 1 | 0 | 7
38903.5968 | 1 | 0 | 7
38903.5969 | 1 | 0 | 7
38903.597 | 1 | 0 | 7
38903.5971 | 1 | 0 | 7
38903.5973 | 1 | 0 | 7
38903.5974 | 1 | 0 | 7
38903.5975 | 1 | 0 | 7
38903.5976 | 1 | 0 | 7
38903.5978 | 1 | 0 | 7
38903.5979 | 1 | 0 | 7
38903.598 | 1 | 0 | 7
38903.5981 | 1 | 0 | 7
38903.5983 | 1 | 0 | 7
38903.5984 | 1 | 0 | 7
38903.5985 | 1 | 0 | 7
38903.5986 | 1 | 0 | 7
38903.5988 | 1 | 0 | 7
38903.5989 | 1 | 0 | 7
38903.599 | 2 | 1 | 7
38903.5991 | 4 | 12 | 7
38903.5993 | 40 | 17 | 7
38903.5994 | 196 | 51 | 7
38903.5996 | 326 | 148 | 7
38903.5998 | 496 | 285 | 7
38903.5999 | 530 | 409 | 7
38903.6 | 1306 | 1055 | 7
38903.6001 | 1129 | 845 | 7
38903.6003 | 1095 | 872 | 7
38903.6004 | 1227 | 901 | 7
38903.6005 | 1354 | 988 | 7
38903.6006 | 1182 | 814 | 7
38903.6008 | 1350 | 919 | 7
38903.6009 | 1322 | 854 | 7
38903.601 | 1130 | 702 | 7
38903.6011 | 1509 | 848 | 7
38903.6013 | 1237 | 650 | 7
38903.6014 | 1222 | 698 | 7
38903.6015 | 1882 | 470 | 7
38903.6016 | 1438 | 576 | 7
38903.6018 | 1662 | 620 | 7
38903.6019 | 1255 | 739 | 7
38903.602 | 1130 | 725 | 7
38903.6021 | 1755 | 442 | 7
38903.6023 | 1846 | 525 | 7
38903.6024 | 1642 | 525 | 7
38903.6025 | 1752 | 450 | 7
38903.6026 | 1460 | 466 | 7
38903.6028 | 1368 | 492 | 7
38903.6029 | 1370 | 503 | 7
38903.603 | 1779 | 570 | 7
38903.6031 | 2320 | 65 | 7
38903.6033 | 1871 | 53 | 7
38903.6034 | 1966 | 57 | 7
38903.6035 | 2004 | 61 | 7
38903.6036 | 2331 | 73 | 7
38903.6038 | 2041 | 68 | 7
38903.6039 | 2125 | 90 | 7
38903.604 | 2060 | 90 | 7
38903.6041 | 1931 | 90 | 7
38903.6043 | 1900 | 95 | 7
38903.6044 | 2024 | 101 | 7
38903.6045 | 1932 | 96 | 7
38903.6046 | 2019 | 108 | 7
38903.6048 | 1887 | 110 | 7
38903.6049 | 2206 | 138 | 7
38903.605 | 1799 | 152 | 7
38903.6051 | 1908 | 104 | 7
38903.6053 | 1763 | 76 | 7
38903.6054 | 2037 | 95 | 7
38903.6055 | 1837 | 80 | 7
38903.6056 | 2050 | 88 | 7
38903.6059 | 2305 | 101 | 7
38903.606 | 1942 | 85 | 7
38903.6061 | 2168 | 95 | 7
38903.6063 | 1987 | 83 | 7
38903.6064 | 1847 | 66 | 7
38903.6065 | 2163 | 86 | 7
38903.5889 | 1 | 0 | 8
38903.589 | 1 | 0 | 8
38903.5891 | 1 | 0 | 8
38903.5893 | 1 | 0 | 8
38903.5894 | 1 | 0 | 8
38903.5895 | 0 | 0 | 8
38903.5896 | 1 | 0 | 8
38903.5898 | 1 | 0 | 8
38903.5899 | 1 | 0 | 8
38903.59 | 1 | 0 | 8
38903.5902 | 1 | 0 | 8
38903.5903 | 1 | 0 | 8
38903.5904 | 1 | 0 | 8
38903.5905 | 1 | 0 | 8
38903.5906 | 1 | 0 | 8
38903.5908 | 1 | 0 | 8
38903.5909 | 1 | 0 | 8
38903.591 | 1 | 0 | 8
38903.5911 | 1 | 0 | 8
38903.5913 | 1 | 0 | 8
38903.5914 | 1 | 0 | 8
38903.5915 | 1 | 0 | 8
38903.5916 | 1 | 0 | 8
38903.5918 | 1 | 0 | 8
38903.5919 | 1 | 0 | 8
38903.592 | 1 | 0 | 8
38903.5921 | 1 | 0 | 8
38903.5923 | 1 | 0 | 8
38903.5924 | 1 | 0 | 8
38903.5925 | 1 | 0 | 8
38903.5927 | 1 | 0 | 8
38903.5928 | 1 | 0 | 8
38903.5929 | 1 | 0 | 8
38903.593 | 1 | 0 | 8
38903.5931 | 1 | 0 | 8
38903.5933 | 1 | 0 | 8
38903.5934 | 2 | 0 | 8
38903.5935 | 1 | 0 | 8
38903.5936 | 1 | 0 | 8
38903.5938 | 1 | 0 | 8
38903.5939 | 1 | 0 | 8
38903.594 | 1 | 0 | 8
38903.5941 | 1 | 0 | 8
38903.5943 | 1 | 0 | 8
38903.5944 | 1 | 0 | 8
38903.5945 | 1 | 0 | 8
38903.5946 | 1 | 0 | 8
38903.5948 | 1 | 0 | 8
38903.5949 | 1 | 0 | 8
38903.595 | 1 | 0 | 8
38903.5951 | 1 | 0 | 8
38903.5953 | 1 | 0 | 8
38903.5954 | 1 | 0 | 8
38903.5955 | 1 | 0 | 8
38903.5956 | 1 | 0 | 8
38903.5958 | 1 | 0 | 8
38903.5959 | 1 | 0 | 8
38903.596 | 1 | 0 | 8
38903.5961 | 1 | 0 | 8
38903.5963 | 1 | 0 | 8
38903.5964 | 2 | 0 | 8
38903.5965 | 1 | 0 | 8
38903.5966 | 1 | 0 | 8
38903.5968 | 1 | 0 | 8
38903.5969 | 1 | 0 | 8
38903.597 | 1 | 0 | 8
38903.5971 | 1 | 0 | 8
38903.5973 | 1 | 0 | 8
38903.5974 | 1 | 0 | 8
38903.5975 | 1 | 0 | 8
38903.5976 | 1 | 0 | 8
38903.5978 | 1 | 0 | 8
38903.5979 | 1 | 0 | 8
38903.598 | 1 | 0 | 8
38903.5981 | 1 | 0 | 8
38903.5983 | 1 | 0 | 8
38903.5984 | 1 | 0 | 8
38903.5985 | 1 | 0 | 8
38903.5986 | 1 | 0 | 8
38903.5988 | 1 | 0 | 8
38903.5989 | 1 | 0 | 8
38903.599 | 1 | 0 | 8
38903.5991 | 38 | 2 | 8
38903.5993 | 95 | 8 | 8
38903.5994 | 215 | 63 | 8
38903.5995 | 371 | 223 | 8
38903.5996 | 382 | 199 | 8
38903.5998 | 512 | 262 | 8
38903.5999 | 583 | 299 | 8
38903.6 | 1048 | 804 | 8
38903.6001 | 1329 | 1023 | 8
38903.6003 | 1292 | 973 | 8
38903.6004 | 1299 | 947 | 8
38903.6005 | 1227 | 871 | 8
38903.6006 | 1256 | 860 | 8
38903.6008 | 1402 | 959 | 8
38903.6009 | 1420 | 920 | 8
38903.601 | 1272 | 722 | 8
38903.6011 | 1432 | 776 | 8
38903.6013 | 1206 | 625 | 8
38903.6014 | 1395 | 667 | 8
38903.6015 | 1477 | 362 | 8
38903.6016 | 1723 | 540 | 8
38903.6018 | 1709 | 787 | 8
38903.6019 | 1429 | 860 | 8
38903.602 | 1462 | 857 | 8
38903.6021 | 1568 | 436 | 8
38903.6023 | 1633 | 486 | 8
38903.6024 | 1747 | 569 | 8
38903.6025 | 1592 | 362 | 8
38903.6026 | 1644 | 569 | 8
38903.6028 | 1586 | 550 | 8
38903.6029 | 1686 | 609 | 8
38903.603 | 1401 | 490 | 8
38903.6031 | 2273 | 61 | 8
38903.6033 | 1867 | 54 | 8
38903.6034 | 1925 | 54 | 8
38903.6035 | 1873 | 63 | 8
38903.6036 | 1914 | 56 | 8
38903.6038 | 1841 | 64 | 8
38903.6039 | 2223 | 96 | 8
38903.604 | 2041 | 88 | 8
38903.6041 | 2179 | 104 | 8
38903.6043 | 2132 | 109 | 8
38903.6044 | 2256 | 112 | 8
38903.6045 | 1834 | 91 | 8
38903.6046 | 1772 | 97 | 8
38903.6048 | 2108 | 121 | 8
38903.6049 | 2206 | 141 | 8
38903.605 | 1691 | 156 | 8
38903.6051 | 1950 | 103 | 8
38903.6053 | 2079 | 88 | 8
38903.6054 | 1817 | 89 | 8
38903.6055 | 1901 | 88 | 8
38903.6056 | 2254 | 89 | 8
38903.6058 | 1978 | 97 | 8
38903.6059 | 2256 | 100 | 8
38903.606 | 2303 | 102 | 8
38903.6061 | 1861 | 81 | 8
38903.6063 | 2095 | 93 | 8
38903.6064 | 1923 | 70 | 8
38903.6065 | 2257 | 66 | 8
38903.5889 | 1 | 0 | 9
38903.589 | 1 | 0 | 9
38903.5892 | 1 | 0 | 9
38903.5893 | 1 | 0 | 9
38903.5894 | 1 | 0 | 9
38903.5895 | 1 | 0 | 9
38903.5897 | 1 | 0 | 9
38903.5898 | 3 | 0 | 9
38903.5899 | 1 | 0 | 9
38903.59 | 1 | 0 | 9
38903.5902 | 1 | 0 | 9
38903.5903 | 1 | 0 | 9
38903.5904 | 1 | 0 | 9
38903.5905 | 1 | 0 | 9
38903.5907 | 1 | 0 | 9
38903.5908 | 2 | 1 | 9
38903.5909 | 1 | 0 | 9
38903.591 | 1 | 0 | 9
38903.5912 | 1 | 0 | 9
38903.5913 | 1 | 0 | 9
38903.5914 | 1 | 0 | 9
38903.5915 | 1 | 0 | 9
38903.5917 | 1 | 0 | 9
38903.5918 | 1 | 0 | 9
38903.5919 | 1 | 0 | 9
38903.592 | 1 | 0 | 9
38903.5922 | 1 | 0 | 9
38903.5923 | 1 | 0 | 9
38903.5924 | 1 | 0 | 9
38903.5925 | 1 | 0 | 9
38903.5927 | 1 | 0 | 9
38903.5928 | 1 | 0 | 9
38903.5929 | 1 | 0 | 9
38903.593 | 1 | 0 | 9
38903.5932 | 1 | 0 | 9
38903.5933 | 1 | 0 | 9
38903.5934 | 2 | 0 | 9
38903.5935 | 1 | 0 | 9
38903.5937 | 1 | 0 | 9
38903.5938 | 1 | 0 | 9
38903.5939 | 1 | 0 | 9
38903.594 | 1 | 0 | 9
38903.5942 | 1 | 0 | 9
38903.5943 | 1 | 0 | 9
38903.5944 | 1 | 0 | 9
38903.5945 | 1 | 0 | 9
38903.5947 | 1 | 0 | 9
38903.5948 | 1 | 0 | 9
38903.5949 | 1 | 0 | 9
38903.595 | 1 | 0 | 9
38903.5952 | 1 | 0 | 9
38903.5953 | 1 | 0 | 9
38903.5954 | 1 | 0 | 9
38903.5955 | 1 | 0 | 9
38903.5957 | 1 | 0 | 9
38903.5958 | 1 | 0 | 9
38903.5959 | 1 | 0 | 9
38903.596 | 1 | 0 | 9
38903.5962 | 1 | 1 | 9
38903.5963 | 1 | 0 | 9
38903.5964 | 1 | 0 | 9
38903.5965 | 1 | 0 | 9
38903.5967 | 1 | 0 | 9
38903.5968 | 1 | 1 | 9
38903.5969 | 1 | 0 | 9
38903.597 | 1 | 0 | 9
38903.5972 | 1 | 0 | 9
38903.5973 | 1 | 0 | 9
38903.5974 | 1 | 0 | 9
38903.5975 | 1 | 0 | 9
38903.5977 | 1 | 0 | 9
38903.5978 | 1 | 0 | 9
38903.5979 | 1 | 0 | 9
38903.598 | 1 | 0 | 9
38903.5982 | 1 | 0 | 9
38903.5983 | 1 | 0 | 9
38903.5984 | 1 | 0 | 9
38903.5985 | 1 | 0 | 9
38903.5987 | 1 | 0 | 9
38903.5988 | 1 | 0 | 9
38903.5989 | 1 | 0 | 9
38903.599 | 1 | 0 | 9
38903.5992 | 1 | 1 | 9
38903.5993 | 444 | 352 | 9
38903.5994 | 419 | 309 | 9
38903.5995 | 439 | 342 | 9
38903.5997 | 553 | 397 | 9
38903.5998 | 540 | 366 | 9
38903.5999 | 566 | 436 | 9
38903.6 | 1305 | 1040 | 9
38903.6002 | 1087 | 876 | 9
38903.6003 | 1149 | 921 | 9
38903.6004 | 1249 | 917 | 9
38903.6005 | 1288 | 921 | 9
38903.6007 | 1226 | 843 | 9
38903.6008 | 1145 | 763 | 9
38903.6009 | 1239 | 784 | 9
38903.601 | 1437 | 823 | 9
38903.6012 | 1506 | 826 | 9
38903.6013 | 1306 | 747 | 9
38903.6014 | 1316 | 692 | 9
38903.6015 | 1809 | 473 | 9
38903.6017 | 1687 | 571 | 9
38903.6018 | 1547 | 654 | 9
38903.6019 | 1137 | 689 | 9
38903.602 | 1133 | 769 | 9
38903.6022 | 1461 | 549 | 9
38903.6023 | 1348 | 503 | 9
38903.6024 | 1427 | 471 | 9
38903.6025 | 1747 | 425 | 9
38903.6027 | 1815 | 546 | 9
38903.6028 | 1753 | 523 | 9
38903.6029 | 1790 | 526 | 9
38903.603 | 1438 | 509 | 9
38903.6032 | 2058 | 57 | 9
38903.6033 | 1964 | 55 | 9
38903.6034 | 2057 | 66 | 9
38903.6035 | 1837 | 61 | 9
38903.6037 | 2155 | 66 | 9
38903.6038 | 2187 | 81 | 9
38903.6039 | 2161 | 86 | 9
38903.604 | 2189 | 99 | 9
38903.6042 | 2025 | 108 | 9
38903.6043 | 2253 | 113 | 9
38903.6044 | 1771 | 92 | 9
38903.6045 | 2266 | 128 | 9
38903.6047 | 1957 | 101 | 9
38903.6048 | 2183 | 125 | 9
38903.6049 | 1731 | 103 | 9
38903.605 | 1923 | 169 | 9
38903.6052 | 2259 | 132 | 9
38903.6053 | 2195 | 100 | 9
38903.6054 | 2246 | 101 | 9
38903.6055 | 1866 | 85 | 9
38903.6056 | 2277 | 85 | 9
38903.6058 | 2114 | 105 | 9
38903.6059 | 1980 | 98 | 9
38903.606 | 1950 | 82 | 9
38903.6062 | 2068 | 93 | 9
38903.6063 | 1897 | 65 | 9
38903.6064 | 1780 | 77 | 9
38903.6065 | 1968 | 74 | 9
38903.5889 | 1 | 0 | 10
38903.589 | 1 | 0 | 10
38903.5892 | 1 | 0 | 10
38903.5893 | 1 | 0 | 10
38903.5894 | 1 | 0 | 10
38903.5895 | 1 | 0 | 10
38903.5897 | 1 | 0 | 10
38903.5898 | 1 | 0 | 10
38903.5899 | 1 | 0 | 10
38903.59 | 1 | 0 | 10
38903.5902 | 1 | 0 | 10
38903.5903 | 1 | 0 | 10
38903.5904 | 1 | 0 | 10
38903.5905 | 1 | 0 | 10
38903.5907 | 1 | 0 | 10
38903.5908 | 1 | 0 | 10
38903.5909 | 1 | 0 | 10
38903.591 | 1 | 0 | 10
38903.5912 | 1 | 0 | 10
38903.5913 | 1 | 0 | 10
38903.5914 | 1 | 1 | 10
38903.5915 | 1 | 0 | 10
38903.5917 | 1 | 0 | 10
38903.5918 | 1 | 0 | 10
38903.5919 | 1 | 0 | 10
38903.592 | 1 | 0 | 10
38903.5922 | 1 | 0 | 10
38903.5923 | 1 | 0 | 10
38903.5924 | 1 | 0 | 10
38903.5925 | 1 | 0 | 10
38903.5927 | 1 | 0 | 10
38903.5928 | 1 | 0 | 10
38903.5929 | 1 | 0 | 10
38903.593 | 1 | 0 | 10
38903.5932 | 1 | 0 | 10
38903.5933 | 1 | 0 | 10
38903.5934 | 1 | 0 | 10
38903.5935 | 1 | 0 | 10
38903.5937 | 1 | 0 | 10
38903.5938 | 1 | 0 | 10
38903.5939 | 1 | 0 | 10
38903.594 | 1 | 0 | 10
38903.5942 | 1 | 0 | 10
38903.5943 | 1 | 0 | 10
38903.5944 | 1 | 0 | 10
38903.5945 | 1 | 0 | 10
38903.5947 | 1 | 0 | 10
38903.5948 | 1 | 0 | 10
38903.5949 | 1 | 0 | 10
38903.595 | 1 | 0 | 10
38903.5952 | 1 | 0 | 10
38903.5953 | 1 | 0 | 10
38903.5954 | 1 | 0 | 10
38903.5955 | 1 | 0 | 10
38903.5957 | 1 | 0 | 10
38903.5958 | 1 | 0 | 10
38903.5959 | 1 | 0 | 10
38903.596 | 1 | 0 | 10
38903.5962 | 1 | 0 | 10
38903.5963 | 1 | 0 | 10
38903.5964 | 1 | 0 | 10
38903.5965 | 1 | 0 | 10
38903.5967 | 1 | 0 | 10
38903.5968 | 1 | 0 | 10
38903.5969 | 1 | 0 | 10
38903.597 | 1 | 0 | 10
38903.5972 | 1 | 0 | 10
38903.5973 | 1 | 0 | 10
38903.5974 | 1 | 0 | 10
38903.5975 | 1 | 0 | 10
38903.5977 | 1 | 0 | 10
38903.5978 | 1 | 0 | 10
38903.5979 | 1 | 0 | 10
38903.598 | 1 | 0 | 10
38903.5982 | 1 | 0 | 10
38903.5983 | 1 | 0 | 10
38903.5984 | 1 | 0 | 10
38903.5985 | 1 | 0 | 10
38903.5987 | 1 | 0 | 10
38903.5988 | 8 | 0 | 10
38903.5989 | 57 | 0 | 10
38903.599 | 109 | 0 | 10
38903.5992 | 223 | 1 | 10
38903.5993 | 408 | 157 | 10
38903.5994 | 477 | 241 | 10
38903.5995 | 651 | 297 | 10
38903.5997 | 584 | 299 | 10
38903.5998 | 599 | 317 | 10
38903.5999 | 1271 | 985 | 10
38903.6 | 1320 | 1027 | 10
38903.6002 | 1329 | 1021 | 10
38903.6003 | 1336 | 1009 | 10
38903.6004 | 1040 | 799 | 10
38903.6005 | 1236 | 973 | 10
38903.6007 | 1109 | 750 | 10
38903.6008 | 1075 | 748 | 10
38903.6009 | 1103 | 727 | 10
38903.601 | 1232 | 697 | 10
38903.6012 | 1459 | 783 | 10
38903.6013 | 1450 | 835 | 10
38903.6014 | 1303 | 607 | 10
38903.6015 | 1784 | 463 | 10
38903.6017 | 1413 | 449 | 10
38903.6018 | 1557 | 477 | 10
38903.6019 | 1168 | 736 | 10
38903.602 | 1194 | 872 | 10
38903.6022 | 1731 | 422 | 10
38903.6023 | 1648 | 592 | 10
38903.6024 | 1722 | 688 | 10
38903.6025 | 1577 | 342 | 10
38903.6027 | 1347 | 497 | 10
38903.6028 | 1465 | 471 | 10
38903.6029 | 1788 | 494 | 10
38903.603 | 1336 | 551 | 10
38903.6032 | 1994 | 55 | 10
38903.6033 | 2336 | 67 | 10
38903.6034 | 2328 | 54 | 10
38903.6035 | 2255 | 75 | 10
38903.6037 | 2087 | 69 | 10
38903.6038 | 1815 | 69 | 10
38903.6039 | 1806 | 68 | 10
38903.604 | 1998 | 87 | 10
38903.6042 | 1957 | 90 | 10
38903.6043 | 1843 | 91 | 10
38903.6044 | 2271 | 116 | 10
38903.6045 | 1780 | 94 | 10
38903.6047 | 2257 | 128 | 10
38903.6048 | 1763 | 99 | 10
38903.6049 | 2203 | 135 | 10
38903.605 | 2014 | 213 | 10
38903.6052 | 1814 | 106 | 10
38903.6053 | 1902 | 93 | 10
38903.6054 | 1947 | 89 | 10
38903.6055 | 1883 | 89 | 10
38903.6057 | 2304 | 102 | 10
38903.6058 | 2007 | 91 | 10
38903.6059 | 2216 | 94 | 10
38903.606 | 2238 | 100 | 10
38903.6062 | 2304 | 106 | 10
38903.6063 | 2103 | 75 | 10
38903.6064 | 2109 | 92 | 10
38903.6065 | 2287 | 70 | 10
38903.5889 | 1 | 0 | 11
38903.5891 | 1 | 0 | 11
38903.5892 | 1 | 0 | 11
38903.5893 | 1 | 0 | 11
38903.5894 | 1 | 0 | 11
38903.5895 | 1 | 0 | 11
38903.5897 | 1 | 0 | 11
38903.5898 | 1 | 0 | 11
38903.5899 | 1 | 0 | 11
38903.59 | 1 | 0 | 11
38903.5902 | 1 | 0 | 11
38903.5903 | 1 | 0 | 11
38903.5904 | 1 | 0 | 11
38903.5906 | 1 | 0 | 11
38903.5907 | 1 | 0 | 11
38903.5908 | 2 | 0 | 11
38903.5909 | 1 | 0 | 11
38903.5911 | 1 | 0 | 11
38903.5912 | 1 | 1 | 11
38903.5913 | 1 | 0 | 11
38903.5914 | 1 | 0 | 11
38903.5916 | 1 | 0 | 11
38903.5917 | 1 | 0 | 11
38903.5918 | 1 | 0 | 11
38903.5919 | 1 | 0 | 11
38903.592 | 1 | 0 | 11
38903.5922 | 1 | 0 | 11
38903.5923 | 1 | 0 | 11
38903.5924 | 1 | 0 | 11
38903.5925 | 1 | 0 | 11
38903.5927 | 1 | 0 | 11
38903.5928 | 1 | 0 | 11
38903.5929 | 1 | 0 | 11
38903.5931 | 1 | 0 | 11
38903.5932 | 1 | 0 | 11
38903.5933 | 1 | 0 | 11
38903.5934 | 1 | 0 | 11
38903.5936 | 1 | 0 | 11
38903.5937 | 1 | 0 | 11
38903.5938 | 1 | 0 | 11
38903.5939 | 1 | 0 | 11
38903.5941 | 1 | 0 | 11
38903.5942 | 1 | 0 | 11
38903.5943 | 1 | 0 | 11
38903.5944 | 1 | 0 | 11
38903.5945 | 1 | 0 | 11
38903.5947 | 1 | 0 | 11
38903.5948 | 1 | 0 | 11
38903.5949 | 1 | 0 | 11
38903.595 | 1 | 0 | 11
38903.5952 | 1 | 0 | 11
38903.5953 | 1 | 0 | 11
38903.5954 | 1 | 0 | 11
38903.5956 | 1 | 0 | 11
38903.5957 | 1 | 0 | 11
38903.5958 | 1 | 0 | 11
38903.5959 | 1 | 0 | 11
38903.5961 | 2 | 0 | 11
38903.5962 | 1 | 0 | 11
38903.5963 | 1 | 0 | 11
38903.5964 | 1 | 0 | 11
38903.5966 | 1 | 0 | 11
38903.5967 | 1 | 0 | 11
38903.5968 | 1 | 0 | 11
38903.5969 | 1 | 0 | 11
38903.597 | 1 | 0 | 11
38903.5972 | 1 | 0 | 11
38903.5973 | 1 | 0 | 11
38903.5974 | 1 | 0 | 11
38903.5975 | 1 | 0 | 11
38903.5977 | 1 | 0 | 11
38903.5978 | 1 | 0 | 11
38903.5979 | 1 | 0 | 11
38903.5981 | 1 | 0 | 11
38903.5982 | 1 | 0 | 11
38903.5983 | 1 | 0 | 11
38903.5984 | 1 | 0 | 11
38903.5986 | 1 | 0 | 11
38903.5987 | 1 | 0 | 11
38903.5988 | 1 | 0 | 11
38903.5989 | 1 | 0 | 11
38903.5991 | 1 | 0 | 11
38903.5992 | 149 | 95 | 11
38903.5993 | 194 | 130 | 11
38903.5994 | 374 | 303 | 11
38903.5995 | 439 | 310 | 11
38903.5997 | 503 | 361 | 11
38903.5998 | 1023 | 771 | 11
38903.5999 | 1141 | 879 | 11
38903.6 | 1191 | 994 | 11
38903.6002 | 1204 | 1012 | 11
38903.6003 | 1041 | 818 | 11
38903.6004 | 1272 | 929 | 11
38903.6005 | 1292 | 926 | 11
38903.6007 | 1217 | 835 | 11
38903.6008 | 1207 | 801 | 11
38903.6009 | 1334 | 837 | 11
38903.6011 | 1334 | 758 | 11
38903.6012 | 1239 | 655 | 11
38903.6013 | 1272 | 683 | 11
38903.6014 | 1608 | 727 | 11
38903.6016 | 1669 | 311 | 11
38903.6017 | 1486 | 543 | 11
38903.6018 | 1269 | 826 | 11
38903.6019 | 1151 | 728 | 11
38903.602 | 1274 | 804 | 11
38903.6022 | 1678 | 386 | 11
38903.6023 | 1715 | 527 | 11
38903.6024 | 1360 | 561 | 11
38903.6025 | 1672 | 416 | 11
38903.6027 | 1753 | 546 | 11
38903.6028 | 1703 | 516 | 11
38903.6029 | 1505 | 431 | 11
38903.6031 | 1766 | 640 | 11
38903.6032 | 2086 | 58 | 11
38903.6033 | 1841 | 53 | 11
38903.6034 | 2107 | 63 | 11
38903.6036 | 2122 | 78 | 11
38903.6038 | 2271 | 90 | 11
38903.6039 | 2100 | 88 | 11
38903.6041 | 2013 | 94 | 11
38903.6042 | 2094 | 102 | 11
38903.6043 | 2057 | 100 | 11
38903.6044 | 2286 | 121 | 11
38903.6045 | 2276 | 120 | 11
38903.6047 | 2279 | 126 | 11
38903.6048 | 2186 | 122 | 11
38903.6049 | 2039 | 126 | 11
38903.605 | 1850 | 100 | 11
38903.6052 | 1852 | 112 | 11
38903.6053 | 2134 | 101 | 11
38903.6054 | 1986 | 81 | 11
38903.6056 | 2282 | 104 | 11
38903.6057 | 2162 | 89 | 11
38903.6058 | 1975 | 90 | 11
38903.6059 | 2188 | 94 | 11
38903.6061 | 2223 | 101 | 11
38903.6062 | 2267 | 80 | 11
38903.6063 | 2004 | 84 | 11
38903.6064 | 1895 | 79 | 11
38903.6066 | 2056 | 57 | 11
38903.5889 | 1 | 0 | 12
38903.5891 | 1 | 0 | 12
38903.5892 | 1 | 0 | 12
38903.5893 | 1 | 0 | 12
38903.5894 | 1 | 0 | 12
38903.5896 | 1 | 0 | 12
38903.5897 | 1 | 0 | 12
38903.5898 | 1 | 0 | 12
38903.5899 | 1 | 0 | 12
38903.5901 | 1 | 0 | 12
38903.5902 | 1 | 0 | 12
38903.5903 | 1 | 0 | 12
38903.5904 | 1 | 0 | 12
38903.5906 | 1 | 0 | 12
38903.5907 | 1 | 0 | 12
38903.5908 | 1 | 0 | 12
38903.5909 | 1 | 0 | 12
38903.5911 | 1 | 1 | 12
38903.5912 | 1 | 0 | 12
38903.5913 | 2 | 0 | 12
38903.5914 | 1 | 0 | 12
38903.5916 | 1 | 0 | 12
38903.5917 | 1 | 0 | 12
38903.5918 | 1 | 0 | 12
38903.5919 | 1 | 0 | 12
38903.5921 | 1 | 0 | 12
38903.5922 | 1 | 0 | 12
38903.5923 | 1 | 0 | 12
38903.5924 | 1 | 0 | 12
38903.5926 | 1 | 0 | 12
38903.5927 | 1 | 0 | 12
38903.5928 | 1 | 0 | 12
38903.5929 | 1 | 0 | 12
38903.5931 | 1 | 0 | 12
38903.5932 | 1 | 0 | 12
38903.5933 | 1 | 0 | 12
38903.5934 | 1 | 0 | 12
38903.5936 | 1 | 0 | 12
38903.5937 | 1 | 0 | 12
38903.5938 | 1 | 0 | 12
38903.5939 | 1 | 0 | 12
38903.5941 | 1 | 0 | 12
38903.5942 | 1 | 0 | 12
38903.5943 | 1 | 0 | 12
38903.5944 | 1 | 0 | 12
38903.5946 | 1 | 0 | 12
38903.5947 | 1 | 0 | 12
38903.5948 | 1 | 0 | 12
38903.5949 | 1 | 0 | 12
38903.5951 | 1 | 0 | 12
38903.5952 | 1 | 0 | 12
38903.5953 | 1 | 0 | 12
38903.5954 | 1 | 0 | 12
38903.5956 | 1 | 0 | 12
38903.5957 | 1 | 0 | 12
38903.5958 | 1 | 0 | 12
38903.5959 | 1 | 0 | 12
38903.5961 | 1 | 0 | 12
38903.5962 | 1 | 0 | 12
38903.5963 | 1 | 0 | 12
38903.5964 | 1 | 0 | 12
38903.5966 | 1 | 0 | 12
38903.5967 | 2 | 0 | 12
38903.5968 | 1 | 0 | 12
38903.5969 | 1 | 0 | 12
38903.5971 | 1 | 0 | 12
38903.5972 | 1 | 0 | 12
38903.5973 | 1 | 0 | 12
38903.5974 | 1 | 0 | 12
38903.5976 | 1 | 0 | 12
38903.5977 | 1 | 0 | 12
38903.5978 | 1 | 0 | 12
38903.5979 | 1 | 0 | 12
38903.5981 | 1 | 0 | 12
38903.5982 | 1 | 0 | 12
38903.5983 | 1 | 0 | 12
38903.5984 | 1 | 0 | 12
38903.5986 | 1 | 0 | 12
38903.5987 | 1 | 0 | 12
38903.5988 | 20 | 0 | 12
38903.5989 | 71 | 0 | 12
38903.5991 | 164 | 0 | 12
38903.5992 | 434 | 137 | 12
38903.5993 | 430 | 167 | 12
38903.5994 | 517 | 274 | 12
38903.5996 | 734 | 398 | 12
38903.5997 | 671 | 330 | 12
38903.5998 | 1229 | 950 | 12
38903.5999 | 1048 | 768 | 12
38903.6001 | 1164 | 879 | 12
38903.6002 | 1275 | 969 | 12
38903.6003 | 1076 | 790 | 12
38903.6004 | 1368 | 1013 | 12
38903.6006 | 1379 | 1007 | 12
38903.6007 | 1174 | 762 | 12
38903.6008 | 1105 | 732 | 12
38903.6009 | 1458 | 714 | 12
38903.6011 | 1157 | 731 | 12
38903.6012 | 1440 | 838 | 12
38903.6013 | 1318 | 813 | 12
38903.6014 | 1581 | 722 | 12
38903.6016 | 1690 | 445 | 12
38903.6017 | 1718 | 709 | 12
38903.6018 | 1464 | 731 | 12
38903.6019 | 1180 | 687 | 12
38903.6021 | 1386 | 816 | 12
38903.6022 | 1487 | 504 | 12
38903.6023 | 1541 | 523 | 12
38903.6024 | 1686 | 624 | 12
38903.6026 | 1894 | 472 | 12
38903.6027 | 1835 | 484 | 12
38903.6028 | 1577 | 453 | 12
38903.6029 | 1669 | 502 | 12
38903.6031 | 1704 | 685 | 12
38903.6032 | 2324 | 70 | 12
38903.6033 | 2060 | 58 | 12
38903.6034 | 2307 | 70 | 12
38903.6036 | 2217 | 70 | 12
38903.6037 | 2329 | 64 | 12
38903.6038 | 2236 | 70 | 12
38903.6039 | 2004 | 85 | 12
38903.6041 | 1847 | 79 | 12
38903.6042 | 2075 | 100 | 12
38903.6043 | 2284 | 119 | 12
38903.6044 | 2095 | 108 | 12
38903.6046 | 2040 | 108 | 12
38903.6047 | 1928 | 103 | 12
38903.6048 | 2042 | 115 | 12
38903.6049 | 2141 | 121 | 12
38903.6051 | 2000 | 106 | 12
38903.6052 | 1754 | 109 | 12
38903.6053 | 1974 | 102 | 12
38903.6054 | 1995 | 93 | 12
38903.6056 | 2308 | 101 | 12
38903.6057 | 1954 | 87 | 12
38903.6058 | 2106 | 98 | 12
38903.6059 | 2294 | 101 | 12
38903.6061 | 2254 | 82 | 12
38903.6062 | 1873 | 77 | 12
38903.6063 | 1860 | 76 | 12
38903.6064 | 1818 | 63 | 12
38903.6066 | 2349 | 69 | 12