## Test Facts
Last Row in IR Data sets: | 92
Power On | 67

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 5
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, PVC insulated, PVC jacketed, industrial grade General Cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 300C, nominal 6.1 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 67 seconds of baseline data monitoring. Special Note: Test setup and exposure conditions were identical to Penlight Test 4.
DAQ Time | Penlight Time | Event | Interpretation
67 | 0 | Initiate Penlight Heating
833-838 | 766-771 | Conductor 3 shorts to ground (32) and to conductor 4 (31) at less than 100 ohms | First short circuit indications are between conductor 3 and ground
965 | 898 | Conductor 2 shorts to ground at less than 100 ohms (80)
1000-1004 | 933-937 | Conductor 2 shorts to conductors 3 and 4, respectively at less than 100 ohms (27, 25)
1070-1082 | 1003-1015 | Conductors 1 & 4 short to ground (873, 2) and to each other (17)
1086 | 1019 | The short between conductor 4 and ground degrades to less than 100 ohms (7)
1110 | 1043 | The short between conductor 1 and conductor 2 degrades to less than 100 ohms (<1) | All conductors have shorted to each other and external ground at less than 100 ohms.
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | The initial shorting fault occurred between an insulated conductor and ground rather than between the uninsulated drain wire and ground, and occurred 766 seconds after start of heating (vs. 590 seconds in Test 4).

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 5 |  |  | 2006-07-06 | 10:42
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-63.1667 | 128919 |  | -59.5 | 257738 | -57.5 | 257738 | -55.8333 | 258338 | -63.1667 | 128919
-46.5 | 258338 |  | -42.8333 | 257738 | -41 | 257738 | -39 | 258338 | -46.5 | 257738
-29.6667 | 257938 |  | -26 | 257738 | -24 | 257738 | -22.3333 | 258338 | -29.6667 | 257738
-12.8333 | 257938 |  | -9.1667 | 257738 | -7.3333 | 257738 | -5.3333 | 258338 | -12.8333 | 257738
3.8333 | 257938 |  | 7.6667 | 257738 | 9.5 | 257738 | 11.3333 | 258338 | 3.8333 | 257738
20.6667 | 257938 |  | 24.5 | 257738 | 26.3333 | 257738 | 28.1667 | 258338 | 20.6667 | 257738
37.5 | 257938 |  | 41.1667 | 257738 | 43 | 129319 | 45 | 129169 | 37.5 | 129169
54.3333 | 128919 |  | 58 | 128919 | 60 | 257738 | 61.6667 | 258338 | 54.3333 | 128919
71.1667 | 257938 |  | 74.8333 | 257738 | 76.6667 | 257738 | 78.6667 | 258338 | 71.1667 | 257738
87.8333 | 257938 |  | 91.6667 | 257738 | 93.5 | 257738 | 95.3333 | 258338 | 87.8333 | 257738
104.6667 | 257938 |  | 108.5 | 257738 | 110.3333 | 257738 | 112.1667 | 258338 | 104.6667 | 257738
121.5 | 257938 |  | 125.1667 | 257738 | 127 | 257738 | 129 | 258338 | 121.5 | 257738
138.3333 | 257938 |  | 142 | 257738 | 144 | 257738 | 145.6667 | 258338 | 138.3333 | 257738
155.1667 | 257938 |  | 158.8333 | 257738 | 160.6667 | 257738 | 162.6667 | 258338 | 155.1667 | 257738
171.8333 | 257938 |  | 175.6667 | 257738 | 177.5 | 257738 | 179.3333 | 258338 | 171.8333 | 257738
188.6667 | 257938 |  | 192.5 | 257738 | 194.3333 | 257738 | 196.1667 | 258338 | 188.6667 | 257738
205.5 | 257938 |  | 209.1667 | 257738 | 211 | 257738 | 213 | 258338 | 205.5 | 257738
222.3333 | 257938 |  | 226 | 257738 | 228 | 257738 | 229.6667 | 258338 | 222.3333 | 257738
239.1667 | 257938 |  | 242.8333 | 257738 | 244.6667 | 257738 | 246.6667 | 258338 | 239.1667 | 257738
255.8333 | 257938 |  | 259.6667 | 257738 | 261.5 | 257738 | 263.3333 | 258338 | 255.8333 | 257738
272.6667 | 257938 |  | 276.5 | 257738 | 278.3333 | 257738 | 280.1667 | 258338 | 272.6667 | 257738
289.5 | 257938 |  | 293.1667 | 257738 | 295 | 257738 | 297 | 258338 | 289.5 | 257738
306.3333 | 257938 |  | 310 | 257738 | 312 | 257738 | 313.6667 | 258338 | 306.3333 | 257738
323.1667 | 257938 |  | 326.8333 | 257738 | 328.6667 | 257738 | 330.6667 | 258338 | 323.1667 | 257738
339.8333 | 257938 |  | 343.6667 | 257738 | 345.5 | 257738 | 347.3333 | 258338 | 339.8333 | 257738
356.6667 | 257938 |  | 360.6667 | 257738 | 362.3333 | 257738 | 364.3333 | 258338 | 356.6667 | 257738
373.5 | 257938 |  | 377.1667 | 257738 | 379 | 257738 | 381 | 258338 | 373.5 | 257738
390.3333 | 257938 |  | 394 | 257738 | 396 | 257738 | 397.6667 | 258338 | 390.3333 | 257738
407.1667 | 257938 |  | 410.8333 | 257738 | 412.6667 | 257738 | 414.6667 | 258338 | 407.1667 | 257738
423.8333 | 257938 |  | 427.6667 | 257738 | 429.5 | 257738 | 431.3333 | 258338 | 423.8333 | 257738
440.6667 | 257938 |  | 444.5 | 257738 | 446.3333 | 257738 | 448.1667 | 258338 | 440.6667 | 257738
457.5 | 257938 |  | 461.1667 | 257738 | 463 | 257738 | 465 | 258338 | 457.5 | 257738
474.3333 | 257938 |  | 478 | 257738 | 480 | 257738 | 481.6667 | 258338 | 474.3333 | 257738
491.1667 | 257938 |  | 494.8333 | 257738 | 496.6667 | 257738 | 498.6667 | 258338 | 491.1667 | 257738
507.8333 | 257938 |  | 511.5 | 257738 | 513.5 | 257738 | 515.1667 | 258338 | 507.8333 | 257738
524.6667 | 257938 |  | 528.5 | 257738 | 530.3333 | 257738 | 532.1667 | 258338 | 524.6667 | 257738
541.5 | 257938 |  | 545.1667 | 257738 | 547 | 257738 | 549 | 258338 | 541.5 | 257738
558.3333 | 257938 |  | 562 | 257738 | 564 | 257738 | 565.6667 | 258338 | 558.3333 | 257738
575.1667 | 257938 |  | 578.8333 | 257738 | 580.5 | 257738 | 582.5 | 258338 | 575.1667 | 257738
591.8333 | 257938 |  | 595.6667 | 257738 | 597.5 | 257738 | 599.3333 | 258338 | 591.8333 | 257738
608.5 | 257938 |  | 612.3333 | 257738 | 614.3333 | 257738 | 616.1667 | 258338 | 608.5 | 257738
625.5 | 257938 |  | 629.1667 | 257738 | 631 | 129319 | 633 | 258338 | 625.5 | 129319
642.3333 | 257938 |  | 646 | 257738 | 648 | 257738 | 649.6667 | 258338 | 642.3333 | 257738
659.1667 | 257938 |  | 662.8333 | 257738 | 664.6667 | 257738 | 666.6667 | 258338 | 659.1667 | 257738
675.6667 | 257938 |  | 679.6667 | 257738 | 681.3333 | 257738 | 683.3333 | 258338 | 675.6667 | 257738
692.6667 | 257938 |  | 696.3333 | 257738 | 698.1667 | 257738 | 700.1667 | 258338 | 692.6667 | 257738
709.5 | 257938 |  | 713.1667 | 257738 | 715 | 257738 | 717 | 258338 | 709.5 | 257738
726.3333 | 257938 |  | 730 | 257738 | 732 | 257738 | 733.6667 | 258338 | 726.3333 | 257738
743.1667 | 257938 |  | 746.8333 | 257738 | 748.5 | 257738 | 750.5 | 258338 | 743.1667 | 257738
759.8333 | 257938 |  | 763.6667 | 64534.5 | 765.5 | 32.1276 | 767.3333 | 19810.6154 | 759.8333 | 32.1276
776.6667 | 18359.8571 |  | 780.6667 | 18367 | 782.3333 | 5.8448 | 784.3333 | 17155.8667 | 776.6667 | 5.8448
793.3333 | 18359.8571 |  | 797.1667 | 17135.8667 | 799 | 7.0311 | 800.8333 | 17155.8667 | 793.3333 | 7.0311
810.1667 | 17129.2 |  | 813.8333 | 17135.8667 | 815.6667 | 3.7995 | 817.6667 | 17155.8667 | 810.1667 | 3.7995
827.1667 | 17129.2 |  | 830.8333 | 17135.8667 | 832.5 | 10.2343 | 834.5 | 17155.8667 | 827.1667 | 10.2343
843.8333 | 17129.2 |  | 847.5 | 17135.8667 | 849.5 | 2.3093 | 851.1667 | 17155.8667 | 843.8333 | 2.3093
860.6667 | 17129.2 |  | 864.3333 | 17135.8667 | 866.1667 | 2.5914 | 868.1667 | 18388.4286 | 860.6667 | 2.5914
877.3333 | 17129.2 |  | 881 | 2019.1639 | 883 | 2.6425 | 884.6667 | 17155.8667 | 877.3333 | 2.6425
894.3333 | 17129.2 |  | 897.8333 | 80.0541 | 899.8333 | 7.343 | 901.6667 | 17155.8667 | 894.3333 | 7.343
911.1667 | 18359.8571 |  | 914.8333 | 36.2595 | 916.5 | 6.8752 | 918.5 | 17135.8667 | 911.1667 | 6.8752
927.6667 | 18331.2857 |  | 931.6667 | 26.6722 | 933.3333 | 5.8257 | 935.3333 | 18367 | 927.6667 | 5.8257
944.5 | 18331.2857 |  | 948.3333 | 6.8537 | 950.1667 | 9.9567 | 952 | 18359.8571 | 944.5 | 6.8537
961.5 | 18331.2857 |  | 965 | 3.4566 | 967 | 22.4884 | 968.8333 | 18367 | 961.5 | 3.4566
978.3333 | 18359.8571 |  | 981.8333 | 5.8281 | 983.8333 | 1.586 | 985.6667 | 13523.0526 | 978.3333 | 1.586
995 | 14281.3289 |  | 998.6667 | 2.2338 | 1000.5 | 2.92 | 1002.5 | 872.9146 | 995 | 2.2338
1011.6667 | 2.1741 |  | 1015.6667 | 12.8421 | 1017.3333 | 10.9558 | 1019.3333 | 6.5495 | 1011.6667 | 2.1741
1028.6667 | 4.7156 |  | 1032.3333 | 1.6384 | 1034 | 3.591 | 1036 | 19.9712 | 1028.6667 | 1.6384
1045.3333 | 1.7901 |  | 1049 | 14.8878 | 1051 | 5.0905 | 1052.6667 | 9.6935 | 1045.3333 | 1.7901
1062.1667 | 6.6109 |  | 1065.8333 | 2.0276 | 1067.6667 | 12.8888 | 1069.6667 | 16.3087 | 1062.1667 | 2.0276
1079 | 1.7472 |  | 1082.8333 | 5.6983 | 1084.5 | 5.3043 | 1086.3333 | 1.4676 | 1079 | 1.4676
1095.8333 | 3.4966 |  | 1099.6667 | 3.3325 | 1101.5 | 2.8883 | 1103.3333 | 15.3981 | 1095.8333 | 2.8883
1112.5 | 3.8738 |  | 1116.3333 | 0.67679 | 1118.1667 | 17.6536 | 1120 | 6.1783 | 1112.5 | 0.67679
1129.5 | 8.1263 |  | 1133 | 1.189 | 1135 | 0.87285 | 1136.8333 | 8.0878 | 1129.5 | 0.87285
1146.3333 | 3.829 |  | 1149.8333 | 1.6311 | 1151.8333 | 0.87559 | 1153.6667 | 11.1083 | 1146.3333 | 0.87559
1162.8333 | 1.2708 |  | 1166.6667 | 2.8062 | 1168.5 | 11.4734 | 1170.3333 | 0.63785 | 1162.8333 | 0.63785
1179.6667 | 2.8791 |  | 1183.6667 | 0.63885 | 1185.3333 | 11.9058 | 1187.3333 | 4.0394 | 1179.6667 | 0.63885
1196.5 | 16.466 |  | 1200.1667 | 3.9976 | 1202 | 1.4665 | 1204 | 1.189 | 1196.5 | 1.189
1213.3333 | 7.8557 |  | 1217 | 2.4367 | 1219 | 0.95086 | 1220.6667 | 1.1495 | 1213.3333 | 0.95086
1230.1667 | 1.0699 |  | 1234 | 5.6234 | 1235.8333 | 2.3075 | 1237.6667 | 10.3022 | 1230.1667 | 1.0699
1246.8333 | 15.7735 |  | 1250.6667 | 4.3843 | 1252.5 | 2.8062 | 1254.3333 | 11.472 | 1246.8333 | 2.8062
1263.5 | 11.3192 |  | 1267.5 | 7.3878 | 1269.1667 | 0.79672 | 1271.1667 | 2.7167 | 1263.5 | 0.79672
1280.5 | 10.4818 |  | 1284.3333 | 0.79454 | 1286.1667 | 10.9458 | 1288 | 10.1099 | 1280.5 | 0.79454
1297.3333 | 0.99102 |  | 1301 | 5.2357 | 1303 | 4.9627 | 1304.6667 | 16.9932 | 1297.3333 | 0.99102
1314.1667 | 3.7965 |  | 1317.8333 | 0.83385 | 1319.6667 | 7.3187 | 1321.6667 | 12.7565 | 1314.1667 | 0.83385
1330.8333 | 5.0947 |  | 1334.6667 | 0.6376 | 1336.5 | 0.63934 | 1338.3333 | 12.948 | 1330.8333 | 0.6376
1347.6667 | 0.63735 |  | 1351.5 | 8.5105 | 1353.3333 | 0.71573 | 1355.1667 | 0.63686 | 1347.6667 | 0.63686
1364.5 | 18.9314 |  | 1368.1667 | 10.1872 | 1370 | 13.886 | 1372 | 4.4123 | 1364.5 | 4.4123
1381.3333 | 5.4508 |  | 1385 | 2.4793 | 1387 | 12.9311 | 1388.6667 | 10.063 | 1381.3333 | 2.4793

## C-C
Conductor to Conductor Resistances
Penlight Test 5 |  |  | 2006-07-06 | 10:42
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-66 | 128918.9988 | -63 | 258537.9994 | -60.5 | 258337.9994 | -57.5 | 257737.9994 | -55 | 258437.9994 | -52 | 258737.9994 | -66 | 128918.9988
-49.5 | 257738.0775 | -46.5 | 258537.9994 | -43.5 | 258337.9994 | -41 | 257737.9994 | -38 | 258437.9994 | -35.5 | 258737.9994 | -49.5 | 257737.9994
-32.5 | 257937.9994 | -29.5 | 258537.9994 | -27 | 258337.9994 | -24 | 257737.9994 | -21.5 | 258437.9994 | -18.5 | 258737.9994 | -32.5 | 257737.9994
-15.5 | 257937.9994 | -13 | 258537.9994 | -10 | 258337.9994 | -7.5 | 257737.9994 | -4.5 | 258437.9994 | -1.5 | 258737.9994 | -15.5 | 257737.9994
1 | 257937.9994 | 4 | 258537.9994 | 6.5 | 258337.9994 | 9.5 | 257737.9994 | 12.5 | 258437.9994 | 15 | 258737.9994 | 1 | 257737.9994
18 | 257937.9994 | 20.5 | 258537.9994 | 23.5 | 258337.9994 | 26.5 | 257737.9994 | 29 | 258437.9994 | 32 | 258737.9994 | 18 | 257737.9994
34.5 | 257937.9994 | 37.5 | 258537.9994 | 40.5 | 258337.9994 | 43 | 257737.9994 | 46 | 258437.9994 | 48.5 | 129318.9988 | 34.5 | 129318.9988
51.5 | 128918.9988 | 54.5 | 258537.9994 | 57 | 258337.9994 | 60 | 257737.9994 | 62.5 | 258437.9994 | 65.5 | 258737.9994 | 51.5 | 128918.9988
68.5 | 257937.9994 | 71 | 258537.9994 | 74 | 258337.9994 | 76.5 | 257737.9994 | 79.5 | 258437.9994 | 82.5 | 258737.9994 | 68.5 | 257737.9994
85 | 257937.9994 | 88 | 258537.9994 | 90.5 | 258337.9994 | 93.5 | 257737.9994 | 96.5 | 258437.9994 | 99 | 258737.9994 | 85 | 257737.9994
102 | 257937.9994 | 104.5 | 258537.9994 | 107.5 | 258337.9994 | 110.5 | 257737.9994 | 113 | 258437.9994 | 116 | 258737.9994 | 102 | 257737.9994
118.5 | 257937.9994 | 121.5 | 258537.9994 | 124.5 | 258337.9994 | 127 | 257737.9994 | 130 | 258437.9994 | 132.5 | 258737.9994 | 118.5 | 257737.9994
135.5 | 257937.9994 | 138.5 | 258537.9994 | 141 | 258337.9994 | 144 | 257737.9994 | 146.5 | 258437.9994 | 149.5 | 258737.9994 | 135.5 | 257737.9994
152.5 | 257937.9994 | 155 | 258537.9994 | 158 | 258337.9994 | 160.5 | 257737.9994 | 163.5 | 258437.9994 | 166.5 | 258737.9994 | 152.5 | 257737.9994
169 | 257937.9994 | 172 | 258537.9994 | 174.5 | 258337.9994 | 177.5 | 257737.9994 | 180.5 | 258437.9994 | 183 | 258737.9994 | 169 | 257737.9994
186 | 257937.9994 | 188.5 | 258537.9994 | 191.5 | 258337.9994 | 194.5 | 257737.9994 | 197 | 258437.9994 | 200 | 258737.9994 | 186 | 257737.9994
202.5 | 257937.9994 | 205.5 | 258537.9994 | 208.5 | 258337.9994 | 211 | 257737.9994 | 214 | 258437.9994 | 216.5 | 258737.9994 | 202.5 | 257737.9994
219.5 | 257937.9994 | 222.5 | 258537.9994 | 225 | 258337.9994 | 228 | 257737.9994 | 230.5 | 258437.9994 | 233.5 | 258737.9994 | 219.5 | 257737.9994
236.5 | 257937.9994 | 239 | 258537.9994 | 242 | 258337.9994 | 244.5 | 257737.9994 | 247.5 | 258437.9994 | 250.5 | 258737.9994 | 236.5 | 257737.9994
253 | 257937.9994 | 256 | 258537.9994 | 258.5 | 258337.9994 | 261.5 | 257737.9994 | 264.5 | 258437.9994 | 267 | 258737.9994 | 253 | 257737.9994
270 | 257937.9994 | 272.5 | 258537.9994 | 275.5 | 258337.9994 | 278.5 | 257737.9994 | 281 | 258437.9994 | 284 | 258737.9994 | 270 | 257737.9994
286.5 | 257937.9994 | 289.5 | 258537.9994 | 292.5 | 258337.9994 | 295 | 257737.9994 | 298 | 258437.9994 | 300.5 | 258737.9994 | 286.5 | 257737.9994
303.5 | 257937.9994 | 306.5 | 258537.9994 | 309 | 258337.9994 | 312 | 257737.9994 | 314.5 | 258437.9994 | 317.5 | 258737.9994 | 303.5 | 257737.9994
320.5 | 257937.9994 | 323 | 258537.9994 | 326 | 258337.9994 | 328.5 | 257737.9994 | 331.5 | 258437.9994 | 334.5 | 258737.9994 | 320.5 | 257737.9994
337 | 257937.9994 | 340 | 258537.9994 | 342.5 | 258337.9994 | 345.5 | 257737.9994 | 348.5 | 258437.9994 | 351 | 258737.9994 | 337 | 257737.9994
354 | 257937.9994 | 356.5 | 258537.9994 | 359.5 | 258337.9994 | 362.5 | 257737.9994 | 365.5 | 258437.9994 | 368 | 258737.9994 | 354 | 257737.9994
370.5 | 257937.9994 | 373.5 | 258537.9994 | 376.5 | 258337.9994 | 379 | 257737.9994 | 382 | 258437.9994 | 384.5 | 258737.9994 | 370.5 | 257737.9994
387.5 | 257937.9994 | 390.5 | 258537.9994 | 393 | 258337.9994 | 396 | 257737.9994 | 398.5 | 258437.9994 | 401.5 | 258737.9994 | 387.5 | 257737.9994
404.5 | 257937.9994 | 407 | 258537.9994 | 410 | 258337.9994 | 412.5 | 257737.9994 | 415.5 | 258437.9994 | 418.5 | 258737.9994 | 404.5 | 257737.9994
421 | 257937.9994 | 424 | 258537.9994 | 426.5 | 258337.9994 | 429.5 | 257737.9994 | 432.5 | 258437.9994 | 435 | 258737.9994 | 421 | 257737.9994
438 | 257937.9994 | 440.5 | 258537.9994 | 443.5 | 258337.9994 | 446.5 | 257737.9994 | 449 | 258437.9994 | 452 | 258737.9994 | 438 | 257737.9994
454.5 | 257937.9994 | 457.5 | 258537.9994 | 460.5 | 258337.9994 | 463 | 257737.9994 | 466 | 258437.9994 | 468.5 | 258737.9994 | 454.5 | 257737.9994
471.5 | 257937.9994 | 474.5 | 258537.9994 | 477 | 258337.9994 | 480 | 257737.9994 | 482.5 | 258437.9994 | 485.5 | 258737.9994 | 471.5 | 257737.9994
488.5 | 257937.9994 | 491 | 258338.0773 | 494 | 258337.9994 | 496.5 | 257737.9994 | 499.5 | 258437.9994 | 502.5 | 258737.9994 | 488.5 | 257737.9994
505 | 257937.9994 | 508 | 258537.9994 | 510.5 | 258337.9994 | 513.5 | 257737.9994 | 516 | 258437.9994 | 519 | 258737.9994 | 505 | 257737.9994
522 | 257937.9994 | 524.5 | 258537.9994 | 527.5 | 258337.9994 | 530.5 | 257737.9994 | 533 | 258437.9994 | 536 | 258737.9994 | 522 | 257737.9994
538.5 | 257937.9994 | 541.5 | 258537.9994 | 544.5 | 258337.9994 | 547 | 257737.9994 | 550 | 258437.9994 | 552.5 | 258737.9994 | 538.5 | 257737.9994
555.5 | 257937.9994 | 558.5 | 258537.9994 | 561 | 258337.9994 | 564 | 257737.9994 | 566.5 | 258437.9994 | 569.5 | 258737.9994 | 555.5 | 257737.9994
572.5 | 257937.9994 | 575 | 258537.9994 | 578 | 258337.9994 | 580.5 | 257737.9994 | 583.5 | 258437.9994 | 586 | 258737.9994 | 572.5 | 257737.9994
589 | 257937.9994 | 592 | 258537.9994 | 594.5 | 258337.9994 | 597.5 | 257737.9994 | 600.5 | 258437.9994 | 603 | 258737.9994 | 589 | 257737.9994
605.5 | 257937.9994 | 608.5 | 258537.9994 | 611.5 | 258337.9994 | 614.5 | 257737.9994 | 617 | 258437.9994 | 620 | 258737.9994 | 605.5 | 257737.9994
622.5 | 257937.9994 | 625.5 | 258537.9994 | 628.5 | 258337.9994 | 631 | 257737.9994 | 634 | 258437.9994 | 636.5 | 129318.9988 | 622.5 | 129318.9988
639.5 | 257937.9994 | 642.5 | 258537.9994 | 645 | 258337.9994 | 648 | 257737.9994 | 650.5 | 258437.9994 | 653.5 | 258737.9994 | 639.5 | 257737.9994
656.5 | 257937.9994 | 659 | 258537.9994 | 662 | 258337.9994 | 664.5 | 257737.9994 | 667.5 | 258437.9994 | 670.5 | 258737.9994 | 656.5 | 257737.9994
673 | 257937.9994 | 675.5 | 258537.9994 | 678.5 | 258337.9994 | 681.5 | 257737.9994 | 684.5 | 258437.9994 | 687 | 258737.9994 | 673 | 257737.9994
690 | 257937.9994 | 692.5 | 258537.9994 | 695.5 | 258337.9994 | 698 | 257737.9994 | 701 | 258437.9994 | 704 | 258737.9994 | 690 | 257737.9994
706.5 | 257937.9994 | 709.5 | 258537.9994 | 712.5 | 258337.9994 | 715 | 257737.9994 | 718 | 258437.9994 | 720.5 | 258737.9994 | 706.5 | 257737.9994
723.5 | 257937.9994 | 726.5 | 258537.9994 | 729 | 258138.0774 | 732 | 257737.9994 | 734.5 | 258437.9994 | 737.5 | 258737.9994 | 723.5 | 257737.9994
740.5 | 257937.9994 | 743 | 258537.9994 | 746 | 258337.9994 | 748.5 | 257737.9994 | 751.5 | 258437.9994 | 754 | 258737.9994 | 740.5 | 257737.9994
757 | 257937.9994 | 760 | 258537.9994 | 762.5 | 258337.9994 | 765.5 | 257737.9994 | 768.5 | 64534.4976 | 771 | 30.9316 | 757 | 30.9316
774 | 25703.7939 | 776.5 | 64559.4976 | 779.5 | 18359.8486 | 782.5 | 42872.9963 | 785.5 | 18366.9915 | 788 | 26.7764 | 774 | 26.7764
790.5 | 23357.9933 | 793.5 | 36848.2814 | 796 | 18359.8486 | 799 | 32129.7451 | 802 | 17135.8575 | 804.5 | 14.8676 | 790.5 | 14.8676
807.5 | 21403.1593 | 810 | 36848.2814 | 813 | 17129.1908 | 815.5 | 28548.6612 | 818.5 | 17135.8575 | 821.5 | 6.5208 | 807.5 | 6.5208
824.5 | 23357.9933 | 827 | 36848.2814 | 830 | 17129.1908 | 832.5 | 32129.7451 | 835.5 | 17135.8575 | 838 | 17.8443 | 824.5 | 17.8443
841 | 21403.1593 | 844 | 36848.2814 | 846.5 | 17129.1908 | 849.5 | 32129.7451 | 852 | 17135.8575 | 855 | 8.2834 | 841 | 8.2834
858 | 21403.1593 | 860.5 | 36848.2814 | 863.5 | 17129.1908 | 866 | 32129.7451 | 869 | 17135.8575 | 872 | 1.0511 | 858 | 1.0511
874.5 | 21403.1593 | 877.5 | 32229.7451 | 880 | 17129.1908 | 883 | 32129.7451 | 885.5 | 2019.0895 | 888.5 | 26.585 | 874.5 | 26.585
891.5 | 21403.1593 | 894.5 | 36848.2814 | 897 | 17129.1908 | 899.5 | 1255.7071 | 902.5 | 3347.1275 | 905.5 | 21.7965 | 891.5 | 21.7965
908.5 | 21403.1593 | 911 | 32229.7451 | 914 | 18359.8486 | 916.5 | 18440.292 | 919.5 | 11273.8756 | 922 | 22.7498 | 908.5 | 22.7498
925 | 18331.2772 | 927.5 | 18374.1343 | 930.5 | 18359.8486 | 933.5 | 26.601 | 936.5 | 25.4262 | 939 | 23.6569 | 925 | 23.6569
941.5 | 18331.2772 | 944.5 | 18374.1343 | 947.5 | 18359.8486 | 950.5 | 5.3806 | 953 | 9.4898 | 955.5 | 8.5196 | 941.5 | 5.3806
958.5 | 18331.2772 | 961.5 | 19795.2228 | 964.5 | 18359.8486 | 967 | 26.9861 | 969.5 | 1.9309 | 972.5 | 25.5732 | 958.5 | 1.9309
975.5 | 19749.069 | 978.5 | 18374.1343 | 981 | 18359.8486 | 983.5 | 25.7113 | 986.5 | 4.3366 | 989.5 | 12.4874 | 975.5 | 4.3366
992 | 19749.069 | 995 | 19795.2228 | 998 | 247329.9099 | 1000.5 | 276.5161 | 1003.5 | 8955.03 | 1006 | 41934.084 | 992 | 276.5161
1009 | 19749.069 | 1011.5 | 6706.24 | 1014.5 | 16.6079 | 1017.5 | 2536.1984 | 1020.5 | 1791.0769 | 1023 | 7841.1943 | 1009 | 16.6079
1026 | 300.4513 | 1028.5 | 4.8631 | 1031.5 | 3.2088 | 1034 | 28.8798 | 1037 | 9.1056 | 1039.5 | 9.9088 | 1026 | 3.2088
1042.5 | 0.24252 | 1045.5 | 10.0655 | 1048 | 8.8241 | 1051 | 16.8886 | 1053.5 | 29.366 | 1056.5 | 3.5869 | 1042.5 | 0.24252
1059.5 | 10.5399 | 1062 | 5.1298 | 1065 | 22.9792 | 1067.5 | 10.159 | 1070.5 | 0.48062 | 1073.5 | 17.3471 | 1059.5 | 0.48062
1076.5 | 22.3067 | 1079 | 12.4501 | 1081.5 | 0.19657 | 1084.5 | 20.9099 | 1087.5 | 4.205 | 1090 | 3.8037 | 1076.5 | 0.19657
1093 | 7.9443 | 1096 | 1.971 | 1098.5 | 11.8073 | 1101.5 | 26.4094 | 1104.5 | 1.8051 | 1107 | 16.4188 | 1093 | 1.8051
1109.5 | 14.8251 | 1112.5 | 4.4655 | 1115.5 | 2.3549 | 1118.5 | 27.8283 | 1121 | 0.89097 | 1123.5 | 16.3105 | 1109.5 | 0.89097
1126.5 | 14.2458 | 1129.5 | 6.6659 | 1132.5 | 9.1586 | 1135 | 15.856 | 1137.5 | 0.37079 | 1140.5 | 15.3447 | 1126.5 | 0.37079
1143.5 | 17.6977 | 1146.5 | 2.3082 | 1149 | 11.8073 | 1151.5 | 0.08222 | 1154.5 | 1.7213 | 1157.5 | 4.065 | 1143.5 | 0.08222
1160 | 0.28475 | 1163 | 18.2532 | 1165.5 | 18.7218 | 1168.5 | 1.2751 | 1171.5 | 5.0886 | 1174 | 25.3227 | 1160 | 0.28475
1177 | 6.782 | 1179.5 | 1.3443 | 1182.5 | 23.8909 | 1185.5 | 7.299 | 1188.5 | 0.89097 | 1191 | 10.4937 | 1177 | 0.89097
1193.5 | 20.7126 | 1196.5 | 23.6822 | 1199.5 | 15.1113 | 1202 | 4.0063 | 1205 | 2.4799 | 1207.5 | 18.626 | 1193.5 | 2.4799
1210.5 | 26.8284 | 1213.5 | 6.3917 | 1216 | 20.4943 | 1219 | 5.8766 | 1221.5 | 9.3454 | 1224.5 | 0.61447 | 1210.5 | 0.61447
1227.5 | 17.5867 | 1230 | 0.49232 | 1233 | 27.998 | 1236 | 30.0156 | 1238.5 | 22.9067 | 1241.5 | 0.76294 | 1227.5 | 0.49232
1244 | 16.2713 | 1247 | 14.4096 | 1249.5 | 30.186 | 1252.5 | 13.0152 | 1255.5 | 19.6771 | 1258 | 24.2688 | 1244 | 13.0152
1261 | 9.9041 | 1263 | 18.9842 | 1266.5 | 10.5167 | 1269.5 | 5.9219 | 1272 | 28.572 | 1275 | 15.9869 | 1261 | 5.9219
1277.5 | 16.2171 | 1280.5 | 9.0527 | 1283.5 | 20.3784 | 1286.5 | 27.7631 | 1289 | 0.77139 | 1291.5 | 21.7965 | 1277.5 | 0.77139
1294.5 | 8.6535 | 1297.5 | 0.57247 | 1300 | 18.3285 | 1303 | 21.794 | 1305.5 | 14.4173 | 1308.5 | 3.4572 | 1294.5 | 0.57247
1311.5 | 2.2788 | 1314 | 11.2455 | 1317 | 28.4561 | 1319.5 | 14.5239 | 1322.5 | 0.73147 | 1325.5 | 21.0908 | 1311.5 | 0.73147
1328 | 20.2479 | 1331 | 3.5922 | 1333.5 | 16.8349 | 1336.5 | 22.2707 | 1339.5 | 0.93077 | 1342 | 7.8142 | 1328 | 0.93077
1345 | 29.7811 | 1347.5 | 0.93163 | 1350.5 | 4.1641 | 1353.5 | 24.7714 | 1356 | 28.8356 | 1359 | 2.9844 | 1345 | 0.93163
1361.5 | 19.7868 | 1364.5 | 19.3245 | 1367.5 | 17.6048 | 1370 | 8.7586 | 1373 | 12.3554 | 1375.5 | 27.2254 | 1361.5 | 8.7586
1378.5 | 3.9569 | 1381.5 | 6.2551 | 1384 | 28.4561 | 1387 | 0.94331 | 1389.5 | 1.6377 | 1392.5 | 11.5318 | 1378.5 | 0.94331

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5
0 | -67 | 24.2386 | 22.0951 | 22.1163 | 22.0962 | 22.2474 | 22.2557
0.6309 | -66.3691 | 24.2328 | 22.0897 | 22.1214 | 22.0954 | 22.2546 | 22.2551
1.362 | -65.638 | 24.2361 | 22.092 | 22.1116 | 22.0968 | 22.2415 | 22.256
2.3634 | -64.6366 | 24.231 | 22.0892 | 22.1154 | 22.0932 | 22.2507 | 22.2482
3.3548 | -63.6452 | 24.2321 | 22.0883 | 22.1107 | 22.0966 | 22.2503 | 22.2527
4.3563 | -62.6437 | 24.2325 | 22.0837 | 22.1168 | 22.0908 | 22.2486 | 22.2515
5.3577 | -61.6423 | 24.2294 | 22.0877 | 22.0981 | 22.0908 | 22.235 | 22.2517
6.3591 | -60.6409 | 24.2356 | 22.0836 | 22.1189 | 22.091 | 22.2397 | 22.254
7.3606 | -59.6394 | 24.2294 | 22.0924 | 22.1149 | 22.0836 | 22.2419 | 22.254
8.362 | -58.638 | 24.2238 | 22.0838 | 22.1134 | 22.0907 | 22.2508 | 22.2511
9.3534 | -57.6466 | 24.2358 | 22.0889 | 22.1149 | 22.0922 | 22.2338 | 22.2545
10.3549 | -56.6451 | 24.2322 | 22.0939 | 22.1192 | 22.0927 | 22.2443 | 22.2503
11.3563 | -55.6437 | 24.2315 | 22.0912 | 22.1136 | 22.0885 | 22.2539 | 22.2504
12.3578 | -54.6422 | 24.232 | 22.0941 | 22.1092 | 22.0884 | 22.2514 | 22.2498
13.3592 | -53.6408 | 24.235 | 22.0914 | 22.1125 | 22.09 | 22.249 | 22.2514
14.3606 | -52.6394 | 24.2345 | 22.0908 | 22.1116 | 22.0903 | 22.2471 | 22.2526
15.3621 | -51.6379 | 24.2304 | 22.0938 | 22.1113 | 22.0943 | 22.2466 | 22.2559
16.3635 | -50.6365 | 24.2336 | 22.0919 | 22.1179 | 22.0916 | 22.2527 | 22.2488
17.355 | -49.645 | 24.2283 | 22.0975 | 22.1155 | 22.0907 | 22.243 | 22.2558
18.3564 | -48.6436 | 24.2349 | 22.0919 | 22.1179 | 22.0912 | 22.2553 | 22.2511
19.3578 | -47.6422 | 24.236 | 22.0915 | 22.117 | 22.0946 | 22.2466 | 22.2526
20.3593 | -46.6407 | 24.2371 | 22.0954 | 22.1109 | 22.0946 | 22.2545 | 22.2577
21.3607 | -45.6393 | 24.2398 | 22.091 | 22.1149 | 22.0993 | 22.2523 | 22.2581
22.3622 | -44.6378 | 24.244 | 22.0934 | 22.1227 | 22.0882 | 22.2474 | 22.255
23.3636 | -43.6364 | 24.233 | 22.091 | 22.1108 | 22.09 | 22.2665 | 22.2552
24.355 | -42.645 | 24.2409 | 22.0874 | 22.1203 | 22.0959 | 22.256 | 22.2566
25.3565 | -41.6435 | 24.2429 | 22.0862 | 22.1198 | 22.0945 | 22.2655 | 22.2554
26.3579 | -40.6421 | 24.2417 | 22.0973 | 22.1183 | 22.0964 | 22.243 | 22.2601
27.3593 | -39.6407 | 24.2414 | 22.0943 | 22.1148 | 22.0917 | 22.2437 | 22.2597
28.3608 | -38.6392 | 24.2392 | 22.0933 | 22.1226 | 22.0904 | 22.2513 | 22.2566
29.3622 | -37.6378 | 24.2393 | 22.0865 | 22.1168 | 22.0932 | 22.2483 | 22.2569
30.3637 | -36.6363 | 24.2424 | 22.0968 | 22.1213 | 22.0967 | 22.2566 | 22.2614
31.3551 | -35.6449 | 24.2376 | 22.0955 | 22.1161 | 22.0955 | 22.2474 | 22.2621
32.3565 | -34.6435 | 24.24 | 22.0986 | 22.1132 | 22.0882 | 22.2573 | 22.2605
33.358 | -33.642 | 24.2509 | 22.0854 | 22.1197 | 22.0918 | 22.2572 | 22.2539
34.3594 | -32.6406 | 24.2434 | 22.0957 | 22.1167 | 22.0871 | 22.2603 | 22.2544
35.3608 | -31.6392 | 24.2439 | 22.0948 | 22.1227 | 22.0951 | 22.2495 | 22.2562
36.3623 | -30.6377 | 24.2491 | 22.0922 | 22.1099 | 22.0941 | 22.2637 | 22.2611
37.3537 | -29.6463 | 24.2485 | 22.0913 | 22.1163 | 22.091 | 22.2599 | 22.2626
38.3652 | -28.6348 | 24.2446 | 22.0947 | 22.1129 | 22.091 | 22.2594 | 22.2538
39.3566 | -27.6434 | 24.2457 | 22.0941 | 22.1094 | 22.0986 | 22.2613 | 22.2569
40.358 | -26.642 | 24.2431 | 22.0911 | 22.1133 | 22.0885 | 22.2635 | 22.2499
41.3595 | -25.6405 | 24.244 | 22.0915 | 22.1115 | 22.0907 | 22.2606 | 22.2599
42.3609 | -24.6391 | 24.2483 | 22.0909 | 22.1202 | 22.0965 | 22.2631 | 22.2589
43.3624 | -23.6376 | 24.2447 | 22.0983 | 22.1134 | 22.0907 | 22.2586 | 22.2613
44.3638 | -22.6362 | 24.2428 | 22.0902 | 22.1181 | 22.0952 | 22.2524 | 22.2658
45.3552 | -21.6448 | 24.2412 | 22.0941 | 22.1168 | 22.0948 | 22.2542 | 22.2548
46.3567 | -20.6433 | 24.2393 | 22.0931 | 22.1254 | 22.0893 | 22.2567 | 22.2551
47.3581 | -19.6419 | 24.2415 | 22.0909 | 22.1283 | 22.0968 | 22.2557 | 22.2632
48.3595 | -18.6405 | 24.2383 | 22.0928 | 22.1199 | 22.092 | 22.2564 | 22.2608
49.361 | -17.639 | 24.2409 | 22.0888 | 22.1264 | 22.0978 | 22.2588 | 22.2558
50.3624 | -16.6376 | 24.2406 | 22.0941 | 22.1167 | 22.0905 | 22.2681 | 22.2651
51.3639 | -15.6361 | 24.2417 | 22.0951 | 22.1159 | 22.0953 | 22.2661 | 22.261
52.3553 | -14.6447 | 24.2419 | 22.0963 | 22.1143 | 22.0935 | 22.2498 | 22.2598
53.3567 | -13.6433 | 24.2425 | 22.0946 | 22.1146 | 22.0941 | 22.2599 | 22.2567
54.3582 | -12.6418 | 24.2407 | 22.094 | 22.1151 | 22.0962 | 22.257 | 22.258
55.3596 | -11.6404 | 24.2459 | 22.095 | 22.1215 | 22.0929 | 22.257 | 22.2569
56.361 | -10.639 | 24.2432 | 22.0961 | 22.1105 | 22.093 | 22.2628 | 22.2613
57.3625 | -9.6375 | 24.2466 | 22.0923 | 22.1183 | 22.1015 | 22.2657 | 22.2598
58.3639 | -8.6361 | 24.2442 | 22.1025 | 22.1242 | 22.0928 | 22.2662 | 22.2615
59.3553 | -7.6447 | 24.2448 | 22.0984 | 22.1326 | 22.1048 | 22.2589 | 22.255
60.3568 | -6.6432 | 24.2453 | 22.1014 | 22.1153 | 22.1005 | 22.2736 | 22.2701
61.3582 | -5.6418 | 24.2482 | 22.0966 | 22.134 | 22.0976 | 22.2563 | 22.2687
62.3597 | -4.6403 | 24.2517 | 22.1023 | 22.128 | 22.1037 | 22.2636 | 22.2613
63.3611 | -3.6389 | 24.2485 | 22.0954 | 22.1299 | 22.1025 | 22.2645 | 22.2729
64.3625 | -2.6375 | 24.2552 | 22.1003 | 22.1256 | 22.1062 | 22.2746 | 22.2697
65.354 | -1.646 | 24.2712 | 22.0997 | 22.1259 | 22.1011 | 22.2659 | 22.2689
66.3554 | -0.6446 | 24.5351 | 22.1003 | 22.1189 | 22.0991 | 22.2587 | 22.2685
67.3569 | 0.3569 | 25.3182 | 22.0995 | 22.1227 | 22.1023 | 22.2634 | 22.2668
68.3583 | 1.3583 | 26.7007 | 22.0981 | 22.1246 | 22.1016 | 22.2625 | 22.2609
69.3597 | 2.3597 | 28.6282 | 22.101 | 22.1206 | 22.1028 | 22.263 | 22.2664
70.3612 | 3.3612 | 31.0221 | 22.1037 | 22.1136 | 22.107 | 22.27 | 22.2693
71.3626 | 4.3626 | 33.8081 | 22.1057 | 22.1324 | 22.1171 | 22.2743 | 22.2768
72.354 | 5.354 | 36.94 | 22.1051 | 22.1337 | 22.1219 | 22.2854 | 22.2883
73.3555 | 6.3555 | 40.3684 | 22.1177 | 22.1252 | 22.1286 | 22.2918 | 22.3011
74.3569 | 7.3569 | 44.0392 | 22.1258 | 22.1383 | 22.1473 | 22.3124 | 22.3132
75.3584 | 8.3584 | 47.9668 | 22.1396 | 22.1537 | 22.1708 | 22.3335 | 22.3395
76.3598 | 9.3598 | 52.0553 | 22.165 | 22.1742 | 22.1954 | 22.3645 | 22.3678
77.3612 | 10.3612 | 56.3197 | 22.1877 | 22.2043 | 22.2313 | 22.3945 | 22.4005
78.3627 | 11.3627 | 60.7095 | 22.2213 | 22.2305 | 22.2732 | 22.4285 | 22.4352
79.3641 | 12.3641 | 65.2527 | 22.255 | 22.2538 | 22.3356 | 22.4665 | 22.481
80.3656 | 13.3656 | 69.9307 | 22.2939 | 22.2896 | 22.3903 | 22.5129 | 22.5298
81.357 | 14.357 | 74.7365 | 22.3463 | 22.3336 | 22.4776 | 22.5642 | 22.5913
82.3584 | 15.3584 | 79.6742 | 22.4109 | 22.3866 | 22.5572 | 22.6285 | 22.6597
83.3599 | 16.3599 | 84.7 | 22.4767 | 22.4403 | 22.6594 | 22.6974 | 22.7399
84.3613 | 17.3613 | 89.8301 | 22.561 | 22.5005 | 22.761 | 22.7857 | 22.8147
85.3627 | 18.3627 | 95.0984 | 22.6522 | 22.5713 | 22.8735 | 22.8688 | 22.9023
86.4643 | 19.4643 | 101.0082 | 22.7527 | 22.6484 | 23.0086 | 22.9963 | 23.014
87.3556 | 20.3556 | 105.8078 | 22.859 | 22.7124 | 23.1303 | 23.0926 | 23.1103
88.3571 | 21.3571 | 111.2051 | 22.979 | 22.7992 | 23.2824 | 23.218 | 23.229
89.3585 | 22.3585 | 116.656 | 23.1097 | 22.9057 | 23.4451 | 23.3582 | 23.3638
90.3599 | 23.3599 | 122.196 | 23.2634 | 23.0137 | 23.6187 | 23.5208 | 23.5016
91.3614 | 24.3614 | 127.7708 | 23.4224 | 23.1371 | 23.8006 | 23.6616 | 23.6528
92.3628 | 25.3628 | 133.3857 | 23.6033 | 23.2646 | 24.0005 | 23.8513 | 23.8134
93.3542 | 26.3542 | 139.0014 | 23.7876 | 23.3989 | 24.2224 | 24.0367 | 23.9955
94.3557 | 27.3557 | 144.6129 | 24.001 | 23.5512 | 24.4525 | 24.2479 | 24.1822
95.3571 | 28.3571 | 150.212 | 24.2136 | 23.7114 | 24.6942 | 24.4723 | 24.3836
96.3586 | 29.3586 | 155.811 | 24.4509 | 23.8762 | 24.9555 | 24.7069 | 24.6015
97.36 | 30.36 | 161.354 | 24.7075 | 24.0453 | 25.2385 | 24.9424 | 24.8238
98.3614 | 31.3614 | 166.8859 | 24.9738 | 24.2625 | 25.5318 | 25.2061 | 25.0725
99.3629 | 32.3629 | 172.4009 | 25.2638 | 24.4747 | 25.8456 | 25.4831 | 25.3306
100.3543 | 33.3543 | 177.8545 | 25.5745 | 24.6832 | 26.1727 | 25.7708 | 25.598
101.3557 | 34.3557 | 183.2823 | 25.9019 | 24.912 | 26.5215 | 26.08 | 25.883
102.3572 | 35.3572 | 188.7177 | 26.2465 | 25.1608 | 26.8877 | 26.3979 | 26.1882
103.3586 | 36.3586 | 194.2704 | 26.6144 | 25.417 | 27.2859 | 26.7214 | 26.5083
104.3601 | 37.3601 | 199.8246 | 26.9993 | 25.6839 | 27.6897 | 27.0876 | 26.8416
105.3615 | 38.3615 | 205.3832 | 27.4211 | 25.9772 | 28.1235 | 27.4682 | 27.1897
106.3629 | 39.3629 | 210.9549 | 27.847 | 26.267 | 28.5666 | 27.8531 | 27.5658
107.3644 | 40.3644 | 216.4558 | 28.2878 | 26.5799 | 29.0336 | 28.247 | 27.9474
108.3558 | 41.3558 | 221.9456 | 28.7662 | 26.9027 | 29.5208 | 28.6683 | 28.3403
109.3572 | 42.3572 | 227.3237 | 29.2541 | 27.2451 | 30.0294 | 29.1047 | 28.7582
110.3587 | 43.3587 | 232.7423 | 29.768 | 27.5926 | 30.5579 | 29.5594 | 29.1971
111.3601 | 44.3601 | 238.2134 | 30.2986 | 27.9541 | 31.1051 | 30.0287 | 29.6471
112.3616 | 45.3616 | 243.6912 | 30.858 | 28.3594 | 31.6737 | 30.5286 | 30.1155
113.363 | 46.363 | 249.1853 | 31.4355 | 28.7694 | 32.2671 | 31.0368 | 30.5983
114.3544 | 47.3544 | 254.5866 | 32.0527 | 29.1836 | 32.8753 | 31.5664 | 31.1122
115.3559 | 48.3559 | 260.0756 | 32.6846 | 29.626 | 33.5093 | 32.1156 | 31.6426
116.3573 | 49.3573 | 265.4212 | 33.3447 | 30.0735 | 34.1649 | 32.6937 | 32.1931
117.3588 | 50.3588 | 270.7011 | 34.0244 | 30.5518 | 34.8506 | 33.2837 | 32.7703
118.3602 | 51.3602 | 275.951 | 34.737 | 31.0235 | 35.5481 | 33.897 | 33.3651
119.3616 | 52.3616 | 280.9286 | 35.4702 | 31.5367 | 36.2799 | 34.5339 | 33.9654
120.3631 | 53.3631 | 285.5093 | 36.2353 | 32.0453 | 37.0456 | 35.1672 | 34.6008
121.3545 | 54.3545 | 289.8102 | 37.0405 | 32.5813 | 37.8185 | 35.8388 | 35.2379
122.3559 | 55.3559 | 293.8736 | 37.8587 | 33.1492 | 38.6193 | 36.5173 | 35.9046
123.3574 | 56.3574 | 297.7539 | 38.6928 | 33.7229 | 39.4239 | 37.2352 | 36.5797
124.3588 | 57.3588 | 301.3656 | 39.5453 | 34.3048 | 40.2636 | 37.9498 | 37.2744
125.3603 | 58.3603 | 304.7512 | 40.4284 | 34.899 | 41.1128 | 38.6741 | 37.9792
126.3617 | 59.3617 | 307.8866 | 41.3264 | 35.5174 | 41.9672 | 39.4172 | 38.6857
127.3631 | 60.3631 | 310.9906 | 42.239 | 36.1396 | 42.853 | 40.1675 | 39.4107
128.3646 | 61.3646 | 313.7636 | 43.1643 | 36.7746 | 43.7393 | 40.9413 | 40.1384
129.356 | 62.356 | 316.1991 | 44.1014 | 37.4234 | 44.6471 | 41.7127 | 40.8746
130.3574 | 63.3574 | 318.5198 | 45.0531 | 38.0865 | 45.5606 | 42.5201 | 41.6253
131.3589 | 64.3589 | 320.5112 | 46.0223 | 38.7406 | 46.4978 | 43.299 | 42.3712
132.3603 | 65.3603 | 322.3237 | 47.0147 | 39.4269 | 47.4286 | 44.1062 | 43.1233
133.3618 | 66.3618 | 323.729 | 47.9853 | 40.1006 | 48.3695 | 44.9175 | 43.8839
134.3532 | 67.3532 | 325.0155 | 48.9843 | 40.7879 | 49.3054 | 45.7407 | 44.6262
135.3546 | 68.3546 | 326.0058 | 49.9843 | 41.464 | 50.2544 | 46.5231 | 45.3812
136.3561 | 69.3561 | 326.7386 | 50.9854 | 42.1392 | 51.2062 | 47.3409 | 46.1353
137.3575 | 70.3575 | 327.4106 | 51.9977 | 42.8445 | 52.1452 | 48.166 | 46.8906
138.359 | 71.359 | 327.9883 | 53.0009 | 43.5197 | 53.0758 | 48.9669 | 47.6318
139.3604 | 72.3604 | 328.4681 | 54.0006 | 44.1988 | 54.0028 | 49.7689 | 48.3734
140.3618 | 73.3618 | 328.7569 | 54.999 | 44.8805 | 54.9165 | 50.5891 | 49.1134
141.3633 | 74.3633 | 328.9322 | 55.9969 | 45.5517 | 55.8473 | 51.3978 | 49.8409
142.3547 | 75.3547 | 329.0458 | 56.9844 | 46.2307 | 56.7661 | 52.2086 | 50.5657
143.3561 | 76.3561 | 329.1802 | 57.9649 | 46.9004 | 57.6699 | 53.0143 | 51.2843
144.3576 | 77.3576 | 329.1889 | 58.9443 | 47.56 | 58.5685 | 53.8169 | 51.9892
145.359 | 78.359 | 329.2782 | 59.9119 | 48.2209 | 59.4634 | 54.6061 | 52.69
146.3605 | 79.3605 | 329.2499 | 60.8804 | 48.8673 | 60.3549 | 55.384 | 53.3803
147.3619 | 80.3619 | 329.1728 | 61.8302 | 49.5245 | 61.2348 | 56.1867 | 54.0652
148.3633 | 81.3633 | 328.9194 | 62.7703 | 50.1491 | 62.1079 | 56.9613 | 54.7407
149.3548 | 82.3548 | 328.7229 | 63.7122 | 50.8045 | 62.9844 | 57.7253 | 55.4022
150.3562 | 83.3562 | 328.5342 | 64.6335 | 51.442 | 63.8428 | 58.494 | 56.073
151.3576 | 84.3576 | 328.276 | 65.5572 | 52.0848 | 64.7034 | 59.2524 | 56.7356
152.3591 | 85.3591 | 328.0524 | 66.4608 | 52.69 | 65.5565 | 59.9968 | 57.3778
153.3705 | 86.3705 | 327.699 | 67.3637 | 53.3266 | 66.4067 | 60.7437 | 58.0194
154.362 | 87.362 | 327.3502 | 68.2382 | 53.9423 | 67.2385 | 61.4563 | 58.6613
155.3534 | 88.3534 | 326.9728 | 69.1042 | 54.5581 | 68.0557 | 62.1786 | 59.2807
156.3548 | 89.3548 | 326.542 | 69.986 | 55.1652 | 68.8833 | 62.8927 | 59.9115
157.3563 | 90.3563 | 326.1269 | 70.8335 | 55.7716 | 69.6792 | 63.6103 | 60.5323
158.3577 | 91.3577 | 325.6831 | 71.6789 | 56.3764 | 70.4832 | 64.3086 | 61.1372
159.3591 | 92.3591 | 325.4608 | 72.5165 | 56.9689 | 71.2595 | 64.9948 | 61.7479
160.3606 | 93.3606 | 325.2534 | 73.3341 | 57.5515 | 72.0288 | 65.69 | 62.3402
161.362 | 94.362 | 324.9186 | 74.1453 | 58.1218 | 72.7809 | 66.358 | 62.9373
162.3535 | 95.3535 | 324.6114 | 74.9546 | 58.7028 | 73.5305 | 67.0138 | 63.5171
163.3549 | 96.3549 | 324.244 | 75.7452 | 59.2656 | 74.2579 | 67.6794 | 64.0931
164.3563 | 97.3563 | 323.8414 | 76.5211 | 59.8266 | 74.9826 | 68.3379 | 64.6655
165.3578 | 98.3578 | 323.3961 | 77.2966 | 60.3747 | 75.6894 | 68.9872 | 65.2334
166.3592 | 99.3592 | 322.8547 | 78.0502 | 60.9249 | 76.3859 | 69.6253 | 65.8003
167.3607 | 100.3607 | 322.3269 | 78.7841 | 61.468 | 77.0779 | 70.258 | 66.3498
168.3621 | 101.3621 | 321.8842 | 79.5304 | 62.0024 | 77.7529 | 70.8786 | 66.9059
169.3635 | 102.3635 | 321.4636 | 80.25 | 62.5389 | 78.4166 | 71.5145 | 67.4418
170.355 | 103.355 | 321.1392 | 80.9651 | 63.0584 | 79.0795 | 72.133 | 67.9786
171.3564 | 104.3564 | 320.6703 | 81.6644 | 63.597 | 79.7167 | 72.7446 | 68.5142
172.3578 | 105.3578 | 320.0392 | 82.3529 | 64.1102 | 80.3507 | 73.3489 | 69.0278
173.3593 | 106.3593 | 319.6202 | 83.0305 | 64.6303 | 80.9768 | 73.9326 | 69.5486
174.3607 | 107.3607 | 319.279 | 83.7051 | 65.1478 | 81.5851 | 74.5242 | 70.056
175.3622 | 108.3622 | 318.821 | 84.3772 | 65.6542 | 82.1982 | 75.1116 | 70.5561
176.3636 | 109.3636 | 318.2642 | 85.0264 | 66.1577 | 82.7904 | 75.6897 | 71.0489
177.355 | 110.355 | 317.7254 | 85.668 | 66.6626 | 83.38 | 76.2412 | 71.543
178.3565 | 111.3565 | 317.2424 | 86.3057 | 67.1426 | 83.9694 | 76.8089 | 72.0177
179.3579 | 112.3579 | 316.7692 | 86.9235 | 67.6326 | 84.5531 | 77.3662 | 72.4967
180.3593 | 113.3593 | 316.317 | 87.5413 | 68.1058 | 85.1251 | 77.909 | 72.9708
181.3608 | 114.3608 | 315.7501 | 88.1522 | 68.5772 | 85.6688 | 78.4703 | 73.426
182.3622 | 115.3622 | 315.2599 | 88.7549 | 69.0471 | 86.19 | 79.0071 | 73.8779
183.3637 | 116.3637 | 314.8125 | 89.3385 | 69.4929 | 86.6978 | 79.55 | 74.326
184.3551 | 117.3551 | 314.3945 | 89.9129 | 69.9265 | 87.2001 | 80.0536 | 74.7804
185.3565 | 118.3565 | 314.0594 | 90.4832 | 70.3966 | 87.6964 | 80.5706 | 75.2189
186.358 | 119.358 | 313.5801 | 91.0408 | 70.8306 | 88.1821 | 81.0796 | 75.6492
187.3594 | 120.3594 | 313.0643 | 91.5855 | 71.2852 | 88.6718 | 81.5705 | 76.0828
188.3608 | 121.3608 | 312.5623 | 92.1195 | 71.7156 | 89.1466 | 82.0682 | 76.5049
189.3623 | 122.3623 | 312.0051 | 92.6446 | 72.1489 | 89.6208 | 82.5381 | 76.9138
190.3537 | 123.3537 | 311.3941 | 93.1647 | 72.5891 | 90.0791 | 83.0119 | 77.3218
191.3552 | 124.3552 | 310.8694 | 93.69 | 73.0132 | 90.5408 | 83.4848 | 77.7307
192.3566 | 125.3566 | 310.3626 | 94.1929 | 73.4445 | 90.99 | 83.9512 | 78.1279
193.358 | 126.358 | 309.8741 | 94.6973 | 73.8628 | 91.4372 | 84.4136 | 78.5274
194.3595 | 127.3595 | 309.4753 | 95.1823 | 74.2886 | 91.872 | 84.8546 | 78.9142
195.3609 | 128.3609 | 309.1126 | 95.6665 | 74.7001 | 92.2952 | 85.3048 | 79.2897
196.3624 | 129.3624 | 308.4866 | 96.1514 | 75.1143 | 92.7364 | 85.7447 | 79.6748
197.3638 | 130.3638 | 307.9412 | 96.6235 | 75.5128 | 93.168 | 86.171 | 80.0391
198.3552 | 131.3552 | 307.4393 | 97.0877 | 75.9293 | 93.5797 | 86.6078 | 80.4058
199.3567 | 132.3567 | 306.9615 | 97.5546 | 76.3266 | 93.9791 | 87.0235 | 80.7696
200.3581 | 133.3581 | 306.4169 | 98.0164 | 76.7145 | 94.3626 | 87.4581 | 81.1225
201.3595 | 134.3595 | 305.9537 | 98.4701 | 77.0913 | 94.7308 | 87.8751 | 81.4771
202.361 | 135.361 | 305.4325 | 98.9093 | 77.468 | 95.1052 | 88.2621 | 81.8241
203.3624 | 136.3624 | 304.9564 | 99.3419 | 77.8196 | 95.4662 | 88.6713 | 82.1701
204.3538 | 137.3538 | 304.3377 | 99.7664 | 78.207 | 95.833 | 89.0692 | 82.5117
205.3553 | 138.3553 | 303.7723 | 100.1923 | 78.5641 | 96.1913 | 89.4598 | 82.8453
206.3567 | 139.3567 | 303.2477 | 100.6039 | 78.9511 | 96.5362 | 89.8377 | 83.1682
207.3582 | 140.3582 | 302.7729 | 101.0078 | 79.2958 | 96.8807 | 90.2153 | 83.5041
208.3596 | 141.3596 | 302.2759 | 101.4058 | 79.6508 | 97.2174 | 90.5864 | 83.8269
209.361 | 142.361 | 301.8498 | 101.8112 | 79.9964 | 97.5558 | 90.934 | 84.1498
210.3625 | 143.3625 | 301.5327 | 102.1919 | 80.3321 | 97.8884 | 91.3118 | 84.4688
211.3539 | 144.3539 | 301.1804 | 102.5775 | 80.659 | 98.2286 | 91.6655 | 84.7739
212.3554 | 145.3554 | 300.6516 | 102.9654 | 80.9898 | 98.552 | 92.0307 | 85.0799
213.3568 | 146.3568 | 300.168 | 103.3371 | 81.3242 | 98.8792 | 92.379 | 85.3786
214.3582 | 147.3582 | 299.63 | 103.7054 | 81.6315 | 99.2115 | 92.7306 | 85.671
215.3597 | 148.3597 | 299.1533 | 104.0754 | 81.9434 | 99.5195 | 93.0762 | 85.961
216.3611 | 149.3611 | 298.5863 | 104.432 | 82.2692 | 99.8094 | 93.4207 | 86.2428
217.3626 | 150.3626 | 298.0586 | 104.7852 | 82.5807 | 100.089 | 93.7471 | 86.5237
218.364 | 151.364 | 297.6014 | 105.1245 | 82.8962 | 100.365 | 94.0823 | 86.8031
219.3554 | 152.3554 | 297.1609 | 105.4581 | 83.1984 | 100.6478 | 94.3977 | 87.0821
220.3569 | 153.3569 | 296.7236 | 105.7981 | 83.5157 | 100.923 | 94.7208 | 87.3482
221.3583 | 154.3583 | 296.3135 | 106.1233 | 83.8223 | 101.1872 | 95.0405 | 87.6169
222.3597 | 155.3597 | 295.9847 | 106.4503 | 84.1287 | 101.4523 | 95.3424 | 87.8884
223.3612 | 156.3612 | 295.7387 | 106.7725 | 84.4431 | 101.7133 | 95.6482 | 88.1442
224.3626 | 157.3626 | 295.4865 | 107.0919 | 84.7523 | 101.9703 | 95.9598 | 88.4126
225.3641 | 158.3641 | 295.2514 | 107.398 | 85.0518 | 102.2456 | 96.2684 | 88.6666
226.3555 | 159.3555 | 295.0361 | 107.7165 | 85.343 | 102.5029 | 96.5599 | 88.926
227.3569 | 160.3569 | 294.9308 | 108.0302 | 85.6523 | 102.7698 | 96.8703 | 89.18
228.3584 | 161.3584 | 294.9609 | 108.3408 | 85.9479 | 103.0217 | 97.1515 | 89.4311
229.3798 | 162.3798 | 295.0231 | 108.6439 | 86.2627 | 103.2854 | 97.4677 | 89.6888
230.3612 | 163.3612 | 295.1182 | 108.9313 | 86.5479 | 103.537 | 97.7505 | 89.9245
231.3627 | 164.3627 | 295.3357 | 109.2284 | 86.8463 | 103.7952 | 98.0351 | 90.1728
232.3541 | 165.3541 | 295.4462 | 109.5173 | 87.1376 | 104.0604 | 98.3311 | 90.4167
233.3555 | 166.3555 | 295.6692 | 109.814 | 87.4274 | 104.3275 | 98.6266 | 90.6598
234.357 | 167.357 | 295.9839 | 110.0958 | 87.7294 | 104.6064 | 98.8987 | 90.9072
235.3584 | 168.3584 | 296.3758 | 110.3776 | 88.011 | 104.8859 | 99.2008 | 91.1545
236.3599 | 169.3599 | 296.7257 | 110.6566 | 88.2846 | 105.1593 | 99.493 | 91.395
237.3613 | 170.3613 | 297.0794 | 110.926 | 88.5842 | 105.4287 | 99.7818 | 91.6415
238.3627 | 171.3627 | 297.4353 | 111.2052 | 88.8724 | 105.7043 | 100.0823 | 91.8929
239.3642 | 172.3642 | 297.7093 | 111.4711 | 89.1705 | 105.9947 | 100.3782 | 92.1375
240.3556 | 173.3556 | 298.0374 | 111.7438 | 89.4612 | 106.2783 | 100.671 | 92.387
241.3571 | 174.3571 | 298.3951 | 112.0287 | 89.752 | 106.5641 | 100.9566 | 92.6373
242.3585 | 175.3585 | 298.6898 | 112.3185 | 90.0492 | 106.8445 | 101.2595 | 92.8897
243.3599 | 176.3599 | 299.0043 | 112.6024 | 90.3422 | 107.1369 | 101.5487 | 93.1442
244.3614 | 177.3614 | 299.3626 | 112.8925 | 90.6302 | 107.4283 | 101.8527 | 93.3984
245.3628 | 178.3628 | 299.8251 | 113.1746 | 90.9335 | 107.7279 | 102.1488 | 93.6585
246.3643 | 179.3643 | 300.3673 | 113.4789 | 91.2287 | 108.0344 | 102.4546 | 93.9097
247.3557 | 180.3557 | 300.8326 | 113.7779 | 91.5162 | 108.3436 | 102.758 | 94.1655
248.3571 | 181.3571 | 301.2524 | 114.0711 | 91.817 | 108.6516 | 103.0537 | 94.4129
249.3586 | 182.3586 | 301.6442 | 114.3675 | 92.1189 | 108.9726 | 103.3679 | 94.6762
250.36 | 183.36 | 302.0184 | 114.6681 | 92.427 | 109.2929 | 103.6737 | 94.9244
251.3614 | 184.3614 | 302.4511 | 114.9755 | 92.7208 | 109.6278 | 103.9767 | 95.1754
252.3629 | 185.3629 | 302.8087 | 115.2897 | 93.0336 | 109.9522 | 104.2883 | 95.4412
253.3543 | 186.3543 | 303.1117 | 115.5999 | 93.3485 | 110.2631 | 104.6028 | 95.6953
254.3557 | 187.3557 | 303.494 | 115.9175 | 93.6417 | 110.5673 | 104.9134 | 95.9517
255.3572 | 188.3572 | 303.7467 | 116.2383 | 93.9558 | 110.8702 | 105.2138 | 96.2055
256.3586 | 189.3586 | 304.0524 | 116.5613 | 94.2734 | 111.1825 | 105.5355 | 96.4617
257.3601 | 190.3601 | 304.2685 | 116.8829 | 94.5719 | 111.4839 | 105.8554 | 96.7164
258.3615 | 191.3615 | 304.3966 | 117.2139 | 94.8835 | 111.7831 | 106.1626 | 96.9712
259.3629 | 192.3629 | 304.4944 | 117.5402 | 95.1983 | 112.093 | 106.488 | 97.2272
260.3644 | 193.3644 | 304.6222 | 117.8768 | 95.5196 | 112.3921 | 106.8003 | 97.4881
261.3558 | 194.3558 | 304.8959 | 118.2033 | 95.8256 | 112.6849 | 107.128 | 97.741
262.3573 | 195.3573 | 305.0208 | 118.5302 | 96.143 | 112.9756 | 107.4381 | 97.9939
263.3587 | 196.3587 | 305.1871 | 118.8691 | 96.4615 | 113.2666 | 107.7582 | 98.2575
264.3601 | 197.3601 | 305.3721 | 119.1985 | 96.7806 | 113.5657 | 108.0779 | 98.5124
265.3616 | 198.3616 | 305.551 | 119.535 | 97.1054 | 113.8839 | 108.3896 | 98.7579
266.363 | 199.363 | 305.6799 | 119.8643 | 97.4372 | 114.1937 | 108.7052 | 99.0088
267.3544 | 200.3544 | 305.781 | 120.201 | 97.7659 | 114.5248 | 109.0105 | 99.2592
268.3559 | 201.3559 | 305.8801 | 120.5314 | 98.0751 | 114.8489 | 109.3289 | 99.5104
269.3573 | 202.3573 | 306.0779 | 120.86 | 98.4266 | 115.1804 | 109.6452 | 99.7682
270.3588 | 203.3588 | 306.0718 | 121.1917 | 98.7565 | 115.5084 | 109.9683 | 100.0115
271.3602 | 204.3602 | 306.066 | 121.5298 | 99.0878 | 115.8371 | 110.288 | 100.2675
272.3616 | 205.3616 | 306.3179 | 121.8744 | 99.4121 | 116.1508 | 110.609 | 100.5102
273.3631 | 206.3631 | 306.6603 | 122.2131 | 99.7265 | 116.4786 | 110.9426 | 100.7622
274.3545 | 207.3545 | 306.8875 | 122.5503 | 100.0611 | 116.7915 | 111.2695 | 100.9953
275.3559 | 208.3559 | 307.0129 | 122.8815 | 100.3905 | 117.1027 | 111.604 | 101.2496
276.3574 | 209.3574 | 306.9429 | 123.2236 | 100.7046 | 117.4236 | 111.9249 | 101.4903
277.3588 | 210.3588 | 306.7935 | 123.5591 | 101.0355 | 117.7354 | 112.26 | 101.7305
278.3603 | 211.3603 | 306.7511 | 123.9008 | 101.3569 | 118.0439 | 112.5977 | 101.9682
279.3617 | 212.3617 | 306.715 | 124.2231 | 101.6787 | 118.3507 | 112.9193 | 102.217
280.3631 | 213.3631 | 306.6505 | 124.5382 | 102.0027 | 118.6572 | 113.2374 | 102.4523
281.3646 | 214.3646 | 306.5466 | 124.8494 | 102.3114 | 118.9653 | 113.5398 | 102.695
282.356 | 215.356 | 306.4654 | 125.1617 | 102.6139 | 119.2731 | 113.8522 | 102.9464
283.3574 | 216.3574 | 306.3866 | 125.4681 | 102.9251 | 119.5858 | 114.1601 | 103.1788
284.3589 | 217.3589 | 306.2681 | 125.7797 | 103.2331 | 119.8944 | 114.4576 | 103.4154
285.3603 | 218.3603 | 306.179 | 126.0952 | 103.55 | 120.2173 | 114.7638 | 103.6544
286.3618 | 219.3618 | 305.9931 | 126.4088 | 103.854 | 120.5224 | 115.0635 | 103.8762
287.3532 | 220.3532 | 305.9491 | 126.7235 | 104.159 | 120.8313 | 115.3618 | 104.1079
288.3546 | 221.3546 | 305.8456 | 127.0263 | 104.4501 | 121.1233 | 115.666 | 104.3407
289.3561 | 222.3561 | 305.7323 | 127.3356 | 104.7441 | 121.4303 | 115.9624 | 104.5754
290.3575 | 223.3575 | 305.6626 | 127.6447 | 105.0502 | 121.729 | 116.2582 | 104.8014
291.359 | 224.359 | 305.5821 | 127.9566 | 105.3516 | 122.0449 | 116.5486 | 105.0333
292.3604 | 225.3604 | 305.5767 | 128.2567 | 105.6502 | 122.3551 | 116.8363 | 105.2606
293.3618 | 226.3618 | 305.4883 | 128.5625 | 105.9591 | 122.68 | 117.1212 | 105.4891
294.3633 | 227.3633 | 305.3847 | 128.8621 | 106.2756 | 123.0058 | 117.4065 | 105.7161
295.3547 | 228.3547 | 305.4431 | 129.1698 | 106.5794 | 123.3291 | 117.6946 | 105.9527
296.3561 | 229.3561 | 305.4936 | 129.471 | 106.8984 | 123.6675 | 117.9746 | 106.1715
297.3576 | 230.3576 | 305.4382 | 129.7753 | 107.2055 | 123.9959 | 118.2619 | 106.3963
298.359 | 231.359 | 305.44 | 130.0782 | 107.5156 | 124.3195 | 118.5468 | 106.6236
299.3605 | 232.3605 | 305.454 | 130.3768 | 107.8371 | 124.6579 | 118.8383 | 106.8437
300.3619 | 233.3619 | 305.3791 | 130.6702 | 108.1469 | 124.9936 | 119.1192 | 107.0591
301.3633 | 234.3633 | 305.3423 | 130.9744 | 108.4647 | 125.3288 | 119.4149 | 107.2828
302.3648 | 235.3648 | 305.4413 | 131.2702 | 108.7823 | 125.6661 | 119.7067 | 107.4939
303.3562 | 236.3562 | 305.5107 | 131.5784 | 109.0866 | 126.0073 | 119.9927 | 107.7282
304.3576 | 237.3576 | 305.549 | 131.866 | 109.4026 | 126.3527 | 120.2843 | 107.9452
305.3591 | 238.3591 | 305.6344 | 132.1641 | 109.7046 | 126.6923 | 120.5877 | 108.1691
306.3605 | 239.3605 | 305.6299 | 132.4583 | 110.0067 | 127.0295 | 120.8783 | 108.3824
307.362 | 240.362 | 305.6688 | 132.7414 | 110.3251 | 127.3655 | 121.1748 | 108.6086
308.3534 | 241.3534 | 305.7361 | 133.0326 | 110.6333 | 127.699 | 121.465 | 108.8296
309.3648 | 242.3648 | 305.8874 | 133.3169 | 110.9389 | 128.0285 | 121.7729 | 109.0479
310.3563 | 243.3563 | 305.9116 | 133.6107 | 111.2239 | 128.3562 | 122.0568 | 109.2626
311.3577 | 244.3577 | 305.9503 | 133.8988 | 111.5328 | 128.6758 | 122.3556 | 109.479
312.3592 | 245.3592 | 305.9931 | 134.1859 | 111.8396 | 128.9888 | 122.6453 | 109.697
313.3606 | 246.3606 | 306.0241 | 134.4703 | 112.1397 | 129.305 | 122.9316 | 109.9156
314.362 | 247.362 | 306.0534 | 134.7639 | 112.4343 | 129.6241 | 123.2144 | 110.1265
315.3635 | 248.3635 | 306.1812 | 135.0598 | 112.7345 | 129.9362 | 123.5054 | 110.3457
316.3549 | 249.3549 | 306.2608 | 135.3405 | 113.0413 | 130.2509 | 123.7886 | 110.5529
317.3563 | 250.3563 | 306.2967 | 135.6449 | 113.3388 | 130.5651 | 124.0687 | 110.766
318.3578 | 251.3578 | 306.4304 | 135.9295 | 113.6287 | 130.8717 | 124.3528 | 110.9789
319.3592 | 252.3592 | 306.5309 | 136.2175 | 113.9316 | 131.1746 | 124.6309 | 111.1873
320.3607 | 253.3607 | 306.6312 | 136.5039 | 114.2133 | 131.488 | 124.9217 | 111.3945
321.3621 | 254.3621 | 306.5509 | 136.7971 | 114.5068 | 131.7829 | 125.2067 | 111.6005
322.3635 | 255.3635 | 306.4913 | 137.0853 | 114.7889 | 132.08 | 125.4887 | 111.8048
323.355 | 256.355 | 306.4019 | 137.372 | 115.0879 | 132.3775 | 125.781 | 112.0091
324.3564 | 257.3564 | 306.3504 | 137.6593 | 115.3678 | 132.663 | 126.0754 | 112.2134
325.3578 | 258.3578 | 306.2991 | 137.9502 | 115.6535 | 132.9497 | 126.352 | 112.4236
326.3593 | 259.3593 | 306.3447 | 138.2205 | 115.9402 | 133.2322 | 126.6534 | 112.6264
327.3607 | 260.3607 | 306.3197 | 138.5053 | 116.2325 | 133.5197 | 126.9387 | 112.8363
328.3622 | 261.3622 | 306.2168 | 138.7813 | 116.5186 | 133.8056 | 127.2493 | 113.0368
329.3536 | 262.3536 | 306.114 | 139.0519 | 116.8031 | 134.0812 | 127.5641 | 113.2366
330.355 | 263.355 | 306.0738 | 139.3188 | 117.0761 | 134.3503 | 127.8556 | 113.4455
331.3565 | 264.3565 | 305.9979 | 139.583 | 117.3551 | 134.6212 | 128.1554 | 113.6474
332.3579 | 265.3579 | 305.9235 | 139.8451 | 117.6259 | 134.8702 | 128.459 | 113.8488
333.3593 | 266.3593 | 305.9738 | 140.11 | 117.9046 | 135.1256 | 128.7556 | 114.0464
334.3608 | 267.3608 | 306.1463 | 140.3632 | 118.1772 | 135.3682 | 129.0526 | 114.2535
335.3622 | 268.3622 | 306.3445 | 140.6221 | 118.4558 | 135.6269 | 129.3506 | 114.4472
336.3537 | 269.3537 | 306.4322 | 140.867 | 118.723 | 135.8677 | 129.6319 | 114.6556
337.3551 | 270.3551 | 306.4078 | 141.1247 | 118.9895 | 136.115 | 129.9188 | 114.8575
338.3565 | 271.3565 | 306.3063 | 141.3651 | 119.2547 | 136.351 | 130.2093 | 115.0613
339.358 | 272.358 | 306.1849 | 141.5982 | 119.5138 | 136.589 | 130.491 | 115.2646
340.3594 | 273.3594 | 306.0617 | 141.8362 | 119.7938 | 136.8295 | 130.7757 | 115.4712
341.3609 | 274.3609 | 305.9896 | 142.061 | 120.0495 | 137.0738 | 131.0555 | 115.673
342.3623 | 275.3623 | 305.9181 | 142.2933 | 120.3215 | 137.3059 | 131.3438 | 115.8775
343.3637 | 276.3637 | 305.9079 | 142.5301 | 120.5691 | 137.5403 | 131.6258 | 116.0841
344.3552 | 277.3552 | 306.0317 | 142.7563 | 120.8141 | 137.7624 | 131.9101 | 116.2819
345.3566 | 278.3566 | 306.0479 | 143.0005 | 121.0535 | 137.9925 | 132.1875 | 116.4936
346.358 | 279.358 | 305.9389 | 143.2356 | 121.3115 | 138.2181 | 132.4478 | 116.6857
347.3595 | 280.3595 | 305.785 | 143.4673 | 121.5454 | 138.4531 | 132.7275 | 116.8882
348.3609 | 281.3609 | 305.7631 | 143.7114 | 121.803 | 138.702 | 133.0022 | 117.0873
349.3624 | 282.3624 | 305.6747 | 143.9516 | 122.0552 | 138.9406 | 133.2625 | 117.2875
350.3538 | 283.3538 | 305.5974 | 144.1877 | 122.3127 | 139.1858 | 133.5291 | 117.4883
351.3552 | 284.3552 | 305.4695 | 144.4262 | 122.5697 | 139.429 | 133.7868 | 117.6759
352.3567 | 285.3567 | 305.315 | 144.6732 | 122.8265 | 139.6828 | 134.0479 | 117.8818
353.3581 | 286.3581 | 305.3244 | 144.9147 | 123.0871 | 139.93 | 134.3047 | 118.0908
354.3595 | 287.3595 | 305.3205 | 145.1518 | 123.3577 | 140.1734 | 134.5664 | 118.2809
355.361 | 288.361 | 305.2944 | 145.39 | 123.6248 | 140.4333 | 134.8398 | 118.4868
356.3624 | 289.3624 | 305.3792 | 145.6234 | 123.874 | 140.6856 | 135.1129 | 118.6837
357.3538 | 290.3538 | 305.4255 | 145.8612 | 124.1333 | 140.9373 | 135.3744 | 118.8792
358.3553 | 291.3553 | 305.5132 | 146.1021 | 124.3837 | 141.1914 | 135.6357 | 119.0735
359.3567 | 292.3567 | 305.5517 | 146.3341 | 124.6332 | 141.4321 | 135.8985 | 119.2754
360.3582 | 293.3582 | 305.5032 | 146.577 | 124.897 | 141.6729 | 136.1576 | 119.4705
361.3596 | 294.3596 | 305.4585 | 146.8075 | 125.1351 | 141.9025 | 136.4239 | 119.6597
362.361 | 295.361 | 305.4161 | 147.0532 | 125.3797 | 142.1326 | 136.6759 | 119.8571
363.3625 | 296.3625 | 305.3528 | 147.2867 | 125.6102 | 142.3559 | 136.9468 | 120.0515
364.3539 | 297.3539 | 305.37 | 147.5276 | 125.8491 | 142.5645 | 137.206 | 120.2409
365.3554 | 298.3554 | 305.2759 | 147.7656 | 126.09 | 142.7683 | 137.4625 | 120.4282
366.3568 | 299.3568 | 305.307 | 147.9963 | 126.328 | 142.976 | 137.7094 | 120.6196
367.3582 | 300.3582 | 305.2892 | 148.2305 | 126.5672 | 143.1808 | 137.9619 | 120.8069
368.3597 | 301.3597 | 305.1974 | 148.4569 | 126.8021 | 143.3885 | 138.2017 | 120.9962
369.3611 | 302.3611 | 305.2443 | 148.686 | 127.0503 | 143.5947 | 138.4396 | 121.1815
370.3626 | 303.3626 | 305.2296 | 148.9039 | 127.29 | 143.8218 | 138.6666 | 121.367
371.354 | 304.354 | 305.324 | 149.1308 | 127.54 | 144.0393 | 138.9132 | 121.559
372.3554 | 305.3554 | 305.3985 | 149.3492 | 127.7887 | 144.2552 | 139.1424 | 121.7449
373.3569 | 306.3569 | 305.479 | 149.579 | 128.0381 | 144.4812 | 139.3793 | 121.9324
374.3583 | 307.3583 | 305.5846 | 149.7912 | 128.2786 | 144.7089 | 139.6125 | 122.1174
375.3597 | 308.3597 | 305.5718 | 150.0107 | 128.5155 | 144.9317 | 139.855 | 122.3097
376.3612 | 309.3612 | 305.5389 | 150.2382 | 128.7739 | 145.1583 | 140.101 | 122.4879
377.3626 | 310.3626 | 305.4966 | 150.464 | 129.0112 | 145.3762 | 140.3336 | 122.6713
378.354 | 311.354 | 305.5701 | 150.6941 | 129.2628 | 145.5954 | 140.5786 | 122.8528
379.3555 | 312.3555 | 305.6938 | 150.9295 | 129.49 | 145.8095 | 140.8108 | 123.0342
380.3569 | 313.3569 | 305.8202 | 151.1553 | 129.7526 | 146.0349 | 141.0408 | 123.2125
381.3584 | 314.3584 | 305.9267 | 151.3814 | 129.9969 | 146.2478 | 141.2744 | 123.3872
382.3598 | 315.3598 | 305.9408 | 151.6205 | 130.2378 | 146.4737 | 141.5186 | 123.5744
383.3612 | 316.3612 | 306.0612 | 151.8412 | 130.4833 | 146.7004 | 141.7435 | 123.7506
384.3627 | 317.3627 | 306.1576 | 152.0624 | 130.7322 | 146.9316 | 141.9599 | 123.9313
385.3641 | 318.3641 | 306.2793 | 152.2978 | 130.966 | 147.1639 | 142.1907 | 124.1131
386.3556 | 319.3556 | 306.265 | 152.5143 | 131.2154 | 147.3959 | 142.4219 | 124.2922
387.357 | 320.357 | 306.3119 | 152.7448 | 131.452 | 147.6106 | 142.6381 | 124.4746
388.3584 | 321.3584 | 306.332 | 152.9687 | 131.7056 | 147.8151 | 142.8707 | 124.6582
389.3599 | 322.3599 | 306.2819 | 153.1908 | 131.9449 | 148.0071 | 143.1021 | 124.8389
390.3613 | 323.3613 | 306.2415 | 153.4045 | 132.1935 | 148.2019 | 143.3307 | 125.0121
391.3628 | 324.3628 | 306.245 | 153.6187 | 132.4421 | 148.3968 | 143.5596 | 125.1988
392.3542 | 325.3542 | 306.2369 | 153.8406 | 132.6851 | 148.605 | 143.7739 | 125.3795
393.3556 | 326.3556 | 306.2932 | 154.0723 | 132.9273 | 148.8053 | 144.0106 | 125.5617
394.3571 | 327.3571 | 306.4607 | 154.2912 | 133.1634 | 149.0198 | 144.2467 | 125.7434
395.3585 | 328.3585 | 306.4866 | 154.5215 | 133.4155 | 149.2395 | 144.4801 | 125.9241
396.37 | 329.37 | 306.53 | 154.7519 | 133.6689 | 149.4439 | 144.7102 | 126.1001
397.3614 | 330.3614 | 306.5587 | 154.975 | 133.915 | 149.6715 | 144.9366 | 126.2834
398.3628 | 331.3628 | 306.5328 | 155.2042 | 134.1531 | 149.8894 | 145.1796 | 126.4593
399.3542 | 332.3542 | 306.5148 | 155.4239 | 134.399 | 150.1249 | 145.4142 | 126.6449
400.3557 | 333.3557 | 306.5235 | 155.6449 | 134.6453 | 150.3543 | 145.6381 | 126.817
401.3571 | 334.3571 | 306.4434 | 155.8605 | 134.8878 | 150.5913 | 145.8592 | 127.001
402.3586 | 335.3586 | 306.3656 | 156.071 | 135.1411 | 150.8408 | 146.0672 | 127.1789
403.36 | 336.36 | 306.3907 | 156.2953 | 135.3872 | 151.0897 | 146.3023 | 127.351
404.3614 | 337.3614 | 306.3826 | 156.5208 | 135.6403 | 151.3257 | 146.5198 | 127.5348
405.3629 | 338.3629 | 306.4107 | 156.7411 | 135.9127 | 151.5698 | 146.739 | 127.7167
406.3643 | 339.3643 | 306.4668 | 156.9602 | 136.1555 | 151.8111 | 146.9563 | 127.8892
407.3658 | 340.3658 | 306.4832 | 157.176 | 136.4203 | 152.063 | 147.1703 | 128.0714
408.3572 | 341.3572 | 306.4116 | 157.3986 | 136.6631 | 152.3097 | 147.383 | 128.2472
409.3586 | 342.3586 | 306.3659 | 157.6129 | 136.9285 | 152.5557 | 147.5799 | 128.4279
410.3601 | 343.3601 | 306.3247 | 157.8301 | 137.1836 | 152.7826 | 147.7961 | 128.6054
411.3615 | 344.3615 | 306.2771 | 158.0438 | 137.4238 | 153.0024 | 148.0064 | 128.7911
412.3629 | 345.3629 | 306.3458 | 158.2523 | 137.668 | 153.2037 | 148.2262 | 128.965
413.3544 | 346.3544 | 306.3642 | 158.4649 | 137.9021 | 153.4056 | 148.4302 | 129.144
414.3558 | 347.3558 | 306.221 | 158.6805 | 138.1411 | 153.6051 | 148.6194 | 129.3206
415.3573 | 348.3573 | 306.2346 | 158.8882 | 138.3583 | 153.7859 | 148.8407 | 129.488
416.3587 | 349.3587 | 306.2736 | 159.1019 | 138.6 | 153.9602 | 149.0426 | 129.6689
417.3601 | 350.3601 | 306.2105 | 159.3029 | 138.8278 | 154.1307 | 149.2454 | 129.8283
418.3616 | 351.3616 | 306.2472 | 159.5158 | 139.0824 | 154.3204 | 149.4441 | 129.9976
419.363 | 352.363 | 306.2652 | 159.7203 | 139.2942 | 154.5153 | 149.6404 | 130.1621
420.3544 | 353.3544 | 306.2355 | 159.9188 | 139.5241 | 154.709 | 149.8413 | 130.3306
421.3559 | 354.3559 | 306.221 | 160.1222 | 139.7766 | 154.9041 | 150.0412 | 130.4973
422.3573 | 355.3573 | 306.2335 | 160.3184 | 140.0023 | 155.09 | 150.253 | 130.6653
423.3588 | 356.3588 | 306.3195 | 160.5259 | 140.236 | 155.283 | 150.438 | 130.8201
424.3602 | 357.3602 | 306.3756 | 160.719 | 140.4656 | 155.4629 | 150.6408 | 130.9839
425.3616 | 358.3616 | 306.2945 | 160.9182 | 140.6739 | 155.6329 | 150.8518 | 131.1519
426.3631 | 359.3631 | 306.2591 | 161.1189 | 140.8971 | 155.7932 | 151.0466 | 131.3052
427.3645 | 360.3645 | 306.1329 | 161.3148 | 141.1098 | 155.9555 | 151.2603 | 131.4718
428.3559 | 361.3559 | 306.0369 | 161.5058 | 141.3277 | 156.1296 | 151.4632 | 131.6363
429.3574 | 362.3574 | 305.9633 | 161.7065 | 141.5357 | 156.2952 | 151.6503 | 131.7916
430.3588 | 363.3588 | 305.8661 | 161.8977 | 141.7506 | 156.4538 | 151.8519 | 131.9455
431.3603 | 364.3603 | 305.7965 | 162.0807 | 141.9614 | 156.6033 | 152.0386 | 132.1119
432.3617 | 365.3617 | 305.7632 | 162.2789 | 142.1745 | 156.7561 | 152.229 | 132.2711
433.3631 | 366.3631 | 305.7269 | 162.4599 | 142.3908 | 156.9231 | 152.4239 | 132.436
434.3646 | 367.3646 | 305.6341 | 162.6535 | 142.6083 | 157.0901 | 152.6193 | 132.6037
435.356 | 368.356 | 305.6823 | 162.845 | 142.8116 | 157.2699 | 152.8056 | 132.7643
436.3575 | 369.3575 | 305.6477 | 163.0392 | 143.0388 | 157.4561 | 153.0046 | 132.9362
437.3589 | 370.3589 | 305.5429 | 163.2349 | 143.2587 | 157.6326 | 153.2006 | 133.1006
438.3603 | 371.3603 | 305.5586 | 163.4206 | 143.4787 | 157.8314 | 153.3907 | 133.2758
439.3618 | 372.3618 | 305.5767 | 163.6061 | 143.6924 | 158.0313 | 153.5621 | 133.4387
440.3532 | 373.3532 | 305.5676 | 163.7897 | 143.9147 | 158.2247 | 153.7418 | 133.6038
441.3546 | 374.3546 | 305.5682 | 163.9726 | 144.145 | 158.4121 | 153.913 | 133.7702
442.3561 | 375.3561 | 305.5198 | 164.1567 | 144.3606 | 158.5969 | 154.0848 | 133.9343
443.3575 | 376.3575 | 305.417 | 164.3406 | 144.5799 | 158.7708 | 154.2622 | 134.103
444.359 | 377.359 | 305.3496 | 164.5193 | 144.7768 | 158.9567 | 154.4413 | 134.2605
445.3604 | 378.3604 | 305.4343 | 164.6914 | 144.9945 | 159.1411 | 154.6236 | 134.4253
446.3618 | 379.3618 | 305.4947 | 164.8723 | 145.2187 | 159.3394 | 154.8158 | 134.5817
447.3933 | 380.3933 | 305.5074 | 165.0629 | 145.4257 | 159.5431 | 155.0205 | 134.7488
448.3547 | 381.3547 | 305.561 | 165.2389 | 145.623 | 159.7315 | 155.2093 | 134.9012
449.3561 | 382.3561 | 305.6604 | 165.4192 | 145.8362 | 159.9275 | 155.4083 | 135.0542
450.3576 | 383.3576 | 305.7009 | 165.5945 | 146.0473 | 160.1147 | 155.6007 | 135.21
451.359 | 384.359 | 305.6741 | 165.7921 | 146.2497 | 160.2926 | 155.8045 | 135.36
452.3605 | 385.3605 | 305.7294 | 165.9672 | 146.4542 | 160.4444 | 156.0069 | 135.5114
453.3619 | 386.3619 | 305.6266 | 166.1434 | 146.6736 | 160.5935 | 156.2104 | 135.6735
454.3633 | 387.3633 | 305.661 | 166.3183 | 146.8793 | 160.7573 | 156.3932 | 135.8217
455.3648 | 388.3648 | 305.6033 | 166.4906 | 147.0766 | 160.9268 | 156.5894 | 135.9717
456.3562 | 389.3562 | 305.4962 | 166.6725 | 147.2997 | 161.1149 | 156.7867 | 136.1187
457.3576 | 390.3576 | 305.5237 | 166.8478 | 147.5077 | 161.3211 | 156.9788 | 136.2735
458.3591 | 391.3591 | 305.4417 | 167.0235 | 147.7396 | 161.5223 | 157.1768 | 136.4205
459.3605 | 392.3605 | 305.3608 | 167.1927 | 147.9575 | 161.7244 | 157.376 | 136.5758
460.362 | 393.362 | 305.4298 | 167.3597 | 148.1761 | 161.9262 | 157.5596 | 136.727
461.3634 | 394.3634 | 305.4791 | 167.5385 | 148.395 | 162.1303 | 157.7394 | 136.8747
462.3548 | 395.3548 | 305.431 | 167.7115 | 148.6035 | 162.3045 | 157.9328 | 137.0339
463.3563 | 396.3563 | 305.3206 | 167.8804 | 148.8254 | 162.4688 | 158.108 | 137.1828
464.3577 | 397.3577 | 305.224 | 168.0557 | 149.0366 | 162.6331 | 158.288 | 137.3318
465.3592 | 398.3592 | 305.1134 | 168.2226 | 149.2281 | 162.8008 | 158.4597 | 137.4824
466.3606 | 399.3606 | 305.031 | 168.3949 | 149.448 | 162.9782 | 158.6349 | 137.6311
467.362 | 400.362 | 305.0298 | 168.5608 | 149.6538 | 163.1538 | 158.7935 | 137.7787
468.3535 | 401.3535 | 304.9233 | 168.7293 | 149.8545 | 163.3442 | 158.9735 | 137.9196
469.3649 | 402.3649 | 304.8636 | 168.902 | 150.0689 | 163.5389 | 159.132 | 138.0705
470.3563 | 403.3563 | 304.8528 | 169.0687 | 150.2669 | 163.7262 | 159.3006 | 138.2137
471.3578 | 404.3578 | 304.8811 | 169.2384 | 150.4926 | 163.9205 | 159.4504 | 138.364
472.3592 | 405.3592 | 304.9394 | 169.4076 | 150.6926 | 164.1207 | 159.605 | 138.5085
473.3607 | 406.3607 | 304.9816 | 169.5792 | 150.9123 | 164.3188 | 159.7521 | 138.6588
474.3621 | 407.3621 | 304.9587 | 169.7565 | 151.1285 | 164.5087 | 159.8975 | 138.8004
475.3635 | 408.3635 | 304.9371 | 169.9312 | 151.3568 | 164.7152 | 160.0533 | 138.9456
476.355 | 409.355 | 304.9432 | 170.1083 | 151.5532 | 164.9074 | 160.2069 | 139.0845
477.3564 | 410.3564 | 304.9578 | 170.3042 | 151.7687 | 165.128 | 160.3719 | 139.2196
478.3578 | 411.3578 | 304.9373 | 170.4791 | 151.9845 | 165.3325 | 160.5427 | 139.3575
479.3593 | 412.3593 | 304.8683 | 170.6515 | 152.2025 | 165.5536 | 160.7134 | 139.5011
480.3607 | 413.3607 | 304.7977 | 170.8272 | 152.4162 | 165.7904 | 160.9013 | 139.6395
481.3622 | 414.3622 | 304.7662 | 171.0107 | 152.6394 | 166.0152 | 161.0606 | 139.7829
482.3636 | 415.3636 | 304.8095 | 171.1895 | 152.8553 | 166.2241 | 161.2312 | 139.9168
483.355 | 416.355 | 304.7673 | 171.3745 | 153.0553 | 166.407 | 161.4007 | 140.0642
484.3565 | 417.3565 | 304.7034 | 171.5473 | 153.2712 | 166.5707 | 161.5887 | 140.2067
485.3579 | 418.3579 | 304.7168 | 171.7294 | 153.48 | 166.7308 | 161.7737 | 140.3361
486.3594 | 419.3594 | 304.795 | 171.9103 | 153.682 | 166.887 | 161.9539 | 140.4721
487.3608 | 420.3608 | 304.785 | 172.0846 | 153.8954 | 167.0459 | 162.1397 | 140.611
488.3622 | 421.3622 | 304.906 | 172.2624 | 154.0973 | 167.2072 | 162.3179 | 140.7389
489.3537 | 422.3537 | 305.0613 | 172.4446 | 154.2989 | 167.3754 | 162.5087 | 140.8774
490.3551 | 423.3551 | 305.1573 | 172.6167 | 154.4868 | 167.552 | 162.7 | 141.0102
491.3565 | 424.3565 | 305.221 | 172.7905 | 154.6824 | 167.7233 | 162.8715 | 141.1542
492.358 | 425.358 | 305.3149 | 172.962 | 154.8878 | 167.9087 | 163.0333 | 141.2899
493.3594 | 426.3594 | 305.3847 | 173.1346 | 155.0848 | 168.0857 | 163.2156 | 141.4338
494.3609 | 427.3609 | 305.4794 | 173.2884 | 155.2938 | 168.2604 | 163.3831 | 141.5718
495.3623 | 428.3623 | 305.3794 | 173.4554 | 155.471 | 168.4469 | 163.5434 | 141.7105
496.3637 | 429.3637 | 305.4566 | 173.6112 | 155.6581 | 168.6321 | 163.6971 | 141.8462
497.3552 | 430.3552 | 305.5418 | 173.7678 | 155.8612 | 168.8153 | 163.8478 | 141.9909
498.3566 | 431.3566 | 305.4967 | 173.9268 | 156.053 | 169.0028 | 164.0019 | 142.1232
499.358 | 432.358 | 305.4703 | 174.0785 | 156.2308 | 169.194 | 164.1725 | 142.263
500.3595 | 433.3595 | 305.4931 | 174.2306 | 156.4333 | 169.3864 | 164.3285 | 142.403
501.3609 | 434.3609 | 305.457 | 174.3925 | 156.616 | 169.5629 | 164.4833 | 142.5528
502.3624 | 435.3624 | 305.4017 | 174.539 | 156.8097 | 169.7458 | 164.6569 | 142.683
503.3538 | 436.3538 | 305.3413 | 174.6915 | 156.9973 | 169.9345 | 164.8142 | 142.8288
504.3552 | 437.3552 | 305.3113 | 174.8372 | 157.1937 | 170.1185 | 164.982 | 142.9674
505.3567 | 438.3567 | 305.3802 | 174.9851 | 157.3867 | 170.3002 | 165.1687 | 143.1068
506.3581 | 439.3581 | 305.4703 | 175.13 | 157.58 | 170.4748 | 165.3376 | 143.2493
507.3595 | 440.3595 | 305.5633 | 175.2774 | 157.7727 | 170.6239 | 165.5336 | 143.3927
508.361 | 441.361 | 305.6639 | 175.442 | 157.9669 | 170.7753 | 165.7167 | 143.5323
509.3624 | 442.3624 | 305.7649 | 175.5899 | 158.1649 | 170.9219 | 165.9115 | 143.684
510.3539 | 443.3539 | 305.7493 | 175.734 | 158.3501 | 171.0781 | 166.0986 | 143.8274
511.3553 | 444.3553 | 305.7342 | 175.8842 | 158.5404 | 171.2247 | 166.2812 | 143.9703
512.3567 | 445.3567 | 305.7172 | 176.0366 | 158.7225 | 171.3833 | 166.4696 | 144.1094
513.3582 | 446.3582 | 305.77 | 176.1949 | 158.9197 | 171.5439 | 166.6569 | 144.2573
514.3596 | 447.3596 | 305.802 | 176.3375 | 159.0946 | 171.7021 | 166.8357 | 144.398
515.3611 | 448.3611 | 305.781 | 176.4797 | 159.2724 | 171.8334 | 167.0132 | 144.5467
516.3625 | 449.3625 | 305.7464 | 176.6189 | 159.4324 | 171.9537 | 167.1879 | 144.683
517.3639 | 450.3639 | 305.745 | 176.7647 | 159.5876 | 172.0632 | 167.3706 | 144.8281
518.3554 | 451.3554 | 305.7542 | 176.9091 | 159.762 | 172.1841 | 167.5417 | 144.9674
519.3568 | 452.3568 | 305.8152 | 177.054 | 159.9369 | 172.3237 | 167.6816 | 145.1065
520.3582 | 453.3582 | 305.93 | 177.2019 | 160.1107 | 172.4647 | 167.8555 | 145.2443
521.3597 | 454.3597 | 305.8869 | 177.3372 | 160.2793 | 172.6097 | 168.0059 | 145.3857
522.3611 | 455.3611 | 305.8651 | 177.4922 | 160.4629 | 172.7709 | 168.1512 | 145.5205
523.3626 | 456.3626 | 305.9262 | 177.6271 | 160.6449 | 172.9425 | 168.299 | 145.653
524.354 | 457.354 | 305.9501 | 177.781 | 160.8233 | 173.1046 | 168.47 | 145.7905
525.3554 | 458.3554 | 305.9258 | 177.9358 | 161.0077 | 173.2814 | 168.6292 | 145.927
526.3569 | 459.3569 | 305.9446 | 178.0835 | 161.192 | 173.4653 | 168.7881 | 146.0694
527.3583 | 460.3583 | 305.959 | 178.2347 | 161.3818 | 173.6375 | 168.9487 | 146.2091
528.3597 | 461.3597 | 306.0497 | 178.3913 | 161.5558 | 173.8198 | 169.1206 | 146.3485
529.3812 | 462.3812 | 306.0747 | 178.5396 | 161.7441 | 174.0055 | 169.2808 | 146.4844
530.3626 | 463.3626 | 306.0409 | 178.6859 | 161.933 | 174.1851 | 169.4726 | 146.6107
531.354 | 464.354 | 306.0098 | 178.8377 | 162.1176 | 174.358 | 169.6357 | 146.7485
532.3555 | 465.3555 | 306.029 | 178.9841 | 162.3099 | 174.5365 | 169.8017 | 146.8775
533.3569 | 466.3569 | 306.0334 | 179.1344 | 162.4917 | 174.7123 | 169.9732 | 146.9976
534.3584 | 467.3584 | 305.9973 | 179.2895 | 162.6807 | 174.8834 | 170.1318 | 147.1385
535.3598 | 468.3598 | 305.9225 | 179.4326 | 162.8753 | 175.0293 | 170.3068 | 147.2631
536.3612 | 469.3612 | 305.8813 | 179.5902 | 163.0549 | 175.1843 | 170.4528 | 147.3872
537.3627 | 470.3627 | 305.867 | 179.7448 | 163.2496 | 175.3267 | 170.5823 | 147.5242
538.3641 | 471.3641 | 305.8573 | 179.9014 | 163.4095 | 175.4787 | 170.7343 | 147.6513
539.3556 | 472.3556 | 305.8938 | 180.0503 | 163.6024 | 175.6453 | 170.8855 | 147.7799
540.357 | 473.357 | 305.8788 | 180.1901 | 163.7978 | 175.8204 | 171.0209 | 147.8994
541.3584 | 474.3584 | 305.8088 | 180.3372 | 163.9676 | 175.9949 | 171.1742 | 148.0258
542.3599 | 475.3599 | 305.7523 | 180.4855 | 164.1368 | 176.1831 | 171.3324 | 148.1536
543.3613 | 476.3613 | 305.844 | 180.6206 | 164.3273 | 176.3819 | 171.4922 | 148.2755
544.3628 | 477.3628 | 305.9669 | 180.7648 | 164.514 | 176.5783 | 171.6591 | 148.4019
545.3542 | 478.3542 | 306.0183 | 180.9128 | 164.6824 | 176.7657 | 171.825 | 148.522
546.3556 | 479.3556 | 305.9857 | 181.0664 | 164.8761 | 176.9424 | 172.0059 | 148.6488
547.3571 | 480.3571 | 305.9249 | 181.2158 | 165.0426 | 177.1007 | 172.1693 | 148.7836
548.3585 | 481.3585 | 305.859 | 181.3633 | 165.226 | 177.2486 | 172.3213 | 148.905
549.3599 | 482.3599 | 305.8236 | 181.5124 | 165.415 | 177.3877 | 172.4746 | 149.0291
550.3614 | 483.3614 | 305.7747 | 181.6654 | 165.578 | 177.4961 | 172.633 | 149.1587
551.3628 | 484.3628 | 305.7358 | 181.816 | 165.7495 | 177.5858 | 172.783 | 149.2693
552.3542 | 485.3542 | 305.7167 | 181.9707 | 165.9267 | 177.6739 | 172.9306 | 149.4052
553.3557 | 486.3557 | 305.7165 | 182.1165 | 166.0953 | 177.7629 | 173.0777 | 149.5199
554.3571 | 487.3571 | 305.6944 | 182.2754 | 166.2601 | 177.8719 | 173.2367 | 149.6449
555.3586 | 488.3586 | 305.5808 | 182.4259 | 166.4277 | 177.9967 | 173.3902 | 149.7689
556.36 | 489.36 | 305.5397 | 182.5732 | 166.5797 | 178.1511 | 173.5543 | 149.8862
557.3614 | 490.3614 | 305.425 | 182.7123 | 166.7517 | 178.3029 | 173.7205 | 150.0111
558.3629 | 491.3629 | 305.3753 | 182.8584 | 166.9061 | 178.469 | 173.8562 | 150.1369
559.3643 | 492.3643 | 305.3849 | 183.0031 | 167.0856 | 178.6362 | 174.0175 | 150.2571
560.3558 | 493.3558 | 305.2791 | 183.1358 | 167.2553 | 178.8087 | 174.1885 | 150.3769
561.3572 | 494.3572 | 305.1499 | 183.2618 | 167.4194 | 178.9772 | 174.3387 | 150.4999
562.3586 | 495.3586 | 305.1049 | 183.3895 | 167.586 | 179.1394 | 174.4957 | 150.6175
563.3601 | 496.3601 | 305.0898 | 183.5153 | 167.7418 | 179.2732 | 174.6519 | 150.7423
564.3615 | 497.3615 | 305.0202 | 183.6387 | 167.9106 | 179.379 | 174.7941 | 150.8604
565.363 | 498.363 | 304.9322 | 183.7689 | 168.0773 | 179.4591 | 174.9495 | 150.9925
566.3544 | 499.3544 | 304.7965 | 183.8931 | 168.2239 | 179.5222 | 175.0841 | 151.1097
567.3558 | 500.3558 | 304.6711 | 184.015 | 168.3777 | 179.5822 | 175.2111 | 151.2302
568.3573 | 501.3573 | 304.6339 | 184.1349 | 168.5271 | 179.6382 | 175.352 | 151.35
569.3587 | 502.3587 | 304.6853 | 184.2561 | 168.6853 | 179.711 | 175.47 | 151.4704
570.3601 | 503.3601 | 304.6897 | 184.3739 | 168.8382 | 179.7897 | 175.5839 | 151.5948
571.3616 | 504.3616 | 304.7215 | 184.4901 | 168.9768 | 179.8891 | 175.6811 | 151.722
572.363 | 505.363 | 304.7545 | 184.5999 | 169.1358 | 179.997 | 175.8155 | 151.8334
573.3544 | 506.3544 | 304.6672 | 184.7189 | 169.3016 | 180.1282 | 175.9351 | 151.9528
574.3559 | 507.3559 | 304.5027 | 184.8335 | 169.4421 | 180.2433 | 176.0707 | 152.0648
575.3573 | 508.3573 | 304.4269 | 184.9433 | 169.5961 | 180.3663 | 176.2081 | 152.1862
576.3588 | 509.3588 | 304.4068 | 185.0625 | 169.7381 | 180.4882 | 176.353 | 152.2959
577.3602 | 510.3602 | 304.3571 | 185.1718 | 169.9022 | 180.59 | 176.4868 | 152.4113
578.3616 | 511.3616 | 304.3026 | 185.2816 | 170.0491 | 180.6614 | 176.6128 | 152.5235
579.3631 | 512.3631 | 304.2967 | 185.4001 | 170.1915 | 180.7243 | 176.7584 | 152.6284
580.3645 | 513.3645 | 304.2598 | 185.5173 | 170.3398 | 180.7799 | 176.8927 | 152.7358
581.3559 | 514.3559 | 304.2114 | 185.6238 | 170.4929 | 180.8198 | 177.0309 | 152.8476
582.3574 | 515.3574 | 304.2038 | 185.7421 | 170.6571 | 180.8381 | 177.1647 | 152.9583
583.3588 | 516.3588 | 304.2054 | 185.8496 | 170.7972 | 180.8452 | 177.3015 | 153.0599
584.3603 | 517.3603 | 304.1896 | 185.966 | 170.9454 | 180.848 | 177.4386 | 153.1746
585.3617 | 518.3617 | 304.203 | 186.0775 | 171.1026 | 180.8659 | 177.5711 | 153.2881
586.3631 | 519.3631 | 304.2561 | 186.1942 | 171.2447 | 180.8853 | 177.7207 | 153.4083
587.3546 | 520.3546 | 304.2305 | 186.3044 | 171.3779 | 180.926 | 177.8539 | 153.5162
588.356 | 521.356 | 304.1945 | 186.4215 | 171.5266 | 180.9958 | 177.9841 | 153.6401
589.3575 | 522.3575 | 304.1775 | 186.5324 | 171.6622 | 181.0778 | 178.1183 | 153.761
590.3589 | 523.3589 | 304.1534 | 186.6411 | 171.8209 | 181.1813 | 178.2444 | 153.8803
591.3603 | 524.3603 | 304.1924 | 186.7592 | 171.9622 | 181.3064 | 178.3708 | 153.9974
592.3618 | 525.3618 | 304.2236 | 186.8608 | 172.1189 | 181.4434 | 178.4787 | 154.1134
593.3632 | 526.3632 | 304.1908 | 186.9818 | 172.2617 | 181.6071 | 178.6175 | 154.2306
594.3546 | 527.3546 | 304.1997 | 187.0833 | 172.4036 | 181.7759 | 178.758 | 154.3533
595.3561 | 528.3561 | 304.2255 | 187.1984 | 172.558 | 181.9281 | 178.9011 | 154.4595
596.3575 | 529.3575 | 304.326 | 187.3176 | 172.7115 | 182.1055 | 179.0424 | 154.5709
597.359 | 530.359 | 304.4234 | 187.4323 | 172.8584 | 182.2709 | 179.1708 | 154.6833
598.3604 | 531.3604 | 304.4814 | 187.5562 | 173.0122 | 182.443 | 179.3137 | 154.8017
599.3618 | 532.3618 | 304.5109 | 187.6818 | 173.1396 | 182.6133 | 179.46 | 154.9102
600.3633 | 533.3633 | 304.6426 | 187.8061 | 173.3095 | 182.7697 | 179.5965 | 155.0225
601.3647 | 534.3647 | 304.7088 | 187.9282 | 173.4479 | 182.9302 | 179.7171 | 155.1323
602.3561 | 535.3561 | 304.807 | 188.0634 | 173.5964 | 183.0913 | 179.8447 | 155.2407
603.3576 | 536.3576 | 304.9896 | 188.1914 | 173.7414 | 183.2631 | 179.9659 | 155.3608
604.359 | 537.359 | 305.09 | 188.3258 | 173.8851 | 183.432 | 180.0887 | 155.4687
605.3605 | 538.3605 | 305.2861 | 188.4632 | 174.0196 | 183.6149 | 180.221 | 155.584
606.3619 | 539.3619 | 305.4278 | 188.6005 | 174.1613 | 183.7908 | 180.3516 | 155.7048
607.3633 | 540.3633 | 305.5169 | 188.7367 | 174.3042 | 183.972 | 180.4647 | 155.82
608.3548 | 541.3548 | 305.5611 | 188.8691 | 174.4382 | 184.1445 | 180.5984 | 155.9435
609.3562 | 542.3562 | 305.5661 | 189.0092 | 174.582 | 184.3128 | 180.7306 | 156.0606
610.3577 | 543.3577 | 305.5218 | 189.142 | 174.727 | 184.477 | 180.8551 | 156.1797
611.3591 | 544.3591 | 305.4725 | 189.2749 | 174.8634 | 184.6455 | 180.9865 | 156.3012
612.3605 | 545.3605 | 305.3758 | 189.3972 | 175.0081 | 184.8022 | 181.1356 | 156.4265
613.362 | 546.362 | 305.2644 | 189.5282 | 175.1563 | 184.9765 | 181.2716 | 156.5464
614.3534 | 547.3534 | 305.2835 | 189.6474 | 175.2916 | 185.1487 | 181.3905 | 156.6626
615.3548 | 548.3548 | 305.3159 | 189.7745 | 175.4454 | 185.3229 | 181.4993 | 156.7691
616.3563 | 549.3563 | 305.2458 | 189.9087 | 175.5898 | 185.5075 | 181.6161 | 156.8878
617.3577 | 550.3577 | 305.1698 | 190.0282 | 175.7286 | 185.7078 | 181.7198 | 156.9967
618.3592 | 551.3592 | 305.1151 | 190.1442 | 175.8821 | 185.9038 | 181.8447 | 157.1124
619.3606 | 552.3606 | 305.0685 | 190.2774 | 176.0235 | 186.0919 | 181.9422 | 157.2224
620.362 | 553.362 | 305.0561 | 190.3987 | 176.1778 | 186.2871 | 182.0688 | 157.3296
621.3635 | 554.3635 | 305.0418 | 190.5219 | 176.3347 | 186.4842 | 182.2102 | 157.4371
622.3649 | 555.3649 | 305.012 | 190.6457 | 176.4696 | 186.6748 | 182.3419 | 157.5465
623.3563 | 556.3563 | 305.0477 | 190.7842 | 176.6301 | 186.8623 | 182.4887 | 157.6466
624.3578 | 557.3578 | 305.1299 | 190.9127 | 176.7863 | 187.0532 | 182.6421 | 157.7601
625.3592 | 558.3592 | 305.2073 | 191.0478 | 176.9323 | 187.2236 | 182.7841 | 157.8598
626.3607 | 559.3607 | 305.2147 | 191.1786 | 177.0831 | 187.4015 | 182.94 | 157.9734
627.3621 | 560.3621 | 305.255 | 191.3129 | 177.2459 | 187.5784 | 183.0951 | 158.0723
628.3936 | 561.3936 | 305.291 | 191.4424 | 177.4016 | 187.7414 | 183.21 | 158.1722
629.355 | 562.355 | 305.3334 | 191.5614 | 177.5407 | 187.8961 | 183.3317 | 158.2738
630.3564 | 563.3564 | 305.2948 | 191.6962 | 177.6936 | 188.0481 | 183.4016 | 158.3755
631.3578 | 564.3578 | 305.288 | 191.8213 | 177.8486 | 188.1912 | 183.4389 | 158.4794
632.3593 | 565.3593 | 305.3756 | 191.9459 | 177.9914 | 188.3266 | 183.4864 | 158.5722
633.3607 | 566.3607 | 305.3838 | 192.0742 | 178.1256 | 188.4704 | 183.5627 | 158.6847
634.3622 | 567.3622 | 305.2142 | 192.1952 | 178.261 | 188.6171 | 183.6341 | 158.7774
635.3536 | 568.3536 | 305.0861 | 192.3076 | 178.3943 | 188.7493 | 183.741 | 158.8736
636.355 | 569.355 | 305.0248 | 192.4194 | 178.5277 | 188.8939 | 183.8321 | 158.9682
637.3565 | 570.3565 | 304.9262 | 192.5235 | 178.6581 | 189.0382 | 183.9694 | 159.0631
638.3579 | 571.3579 | 304.8334 | 192.6321 | 178.7918 | 189.1855 | 184.1062 | 159.1629
639.3594 | 572.3594 | 304.7144 | 192.743 | 178.9254 | 189.3401 | 184.2441 | 159.2563
640.3608 | 573.3608 | 304.7123 | 192.855 | 179.0522 | 189.4944 | 184.3499 | 159.3652
641.3622 | 574.3622 | 304.7781 | 192.9731 | 179.1992 | 189.662 | 184.4895 | 159.4626
642.3637 | 575.3637 | 304.7953 | 193.079 | 179.3152 | 189.8243 | 184.6107 | 159.5582
643.3551 | 576.3551 | 304.7734 | 193.1987 | 179.4606 | 190.0016 | 184.707 | 159.6629
644.3565 | 577.3565 | 304.8571 | 193.3146 | 179.5931 | 190.1789 | 184.8428 | 159.7694
645.358 | 578.358 | 305.0017 | 193.4315 | 179.7191 | 190.3556 | 184.9636 | 159.8671
646.3594 | 579.3594 | 305.1422 | 193.541 | 179.8742 | 190.5171 | 185.0893 | 159.9624
647.3609 | 580.3609 | 305.2382 | 193.6567 | 180.0122 | 190.6828 | 185.2003 | 160.0491
648.3623 | 581.3623 | 305.2644 | 193.7734 | 180.1404 | 190.8456 | 185.3003 | 160.1481
649.3637 | 582.3637 | 305.2875 | 193.8892 | 180.2722 | 191.0221 | 185.4021 | 160.2425
650.3552 | 583.3552 | 305.3178 | 194.0047 | 180.4081 | 191.1828 | 185.5157 | 160.3353
651.3566 | 584.3566 | 305.3558 | 194.1183 | 180.5409 | 191.3512 | 185.6127 | 160.4331
652.358 | 585.358 | 305.4016 | 194.2238 | 180.6867 | 191.5144 | 185.7313 | 160.5249
653.3595 | 586.3595 | 305.6054 | 194.3462 | 180.814 | 191.6754 | 185.8226 | 160.6101
654.3609 | 587.3609 | 305.7355 | 194.4643 | 180.9686 | 191.84 | 185.9456 | 160.7051
655.3624 | 588.3624 | 305.8536 | 194.5883 | 181.1107 | 192.0124 | 186.065 | 160.8102
656.3638 | 589.3638 | 305.9278 | 194.722 | 181.2583 | 192.19 | 186.1889 | 160.9009
657.3552 | 590.3552 | 305.9619 | 194.8326 | 181.3938 | 192.3707 | 186.3221 | 160.9836
658.3567 | 591.3567 | 306.01 | 194.9673 | 181.5443 | 192.5431 | 186.451 | 161.0821
659.3581 | 592.3581 | 306.0483 | 195.0912 | 181.6914 | 192.7038 | 186.613 | 161.1788
660.3596 | 593.3596 | 306.1452 | 195.2265 | 181.8354 | 192.8628 | 186.7612 | 161.278
661.361 | 594.361 | 306.1357 | 195.3495 | 181.9743 | 193.0048 | 186.8898 | 161.3736
662.3624 | 595.3624 | 306.1671 | 195.4705 | 182.1216 | 193.1406 | 187.0289 | 161.4661
663.3539 | 596.3539 | 306.2746 | 195.5992 | 182.2523 | 193.2661 | 187.1816 | 161.5681
664.3653 | 597.3653 | 306.2698 | 195.718 | 182.3867 | 193.3994 | 187.3069 | 161.6782
665.3567 | 598.3567 | 306.2546 | 195.8439 | 182.5147 | 193.5128 | 187.4556 | 161.7743
666.3582 | 599.3582 | 306.1842 | 195.976 | 182.6531 | 193.6276 | 187.5921 | 161.8737
667.3596 | 600.3596 | 306.0975 | 196.1113 | 182.7836 | 193.7366 | 187.7455 | 161.9757
668.3611 | 601.3611 | 306.1873 | 196.2446 | 182.9071 | 193.8579 | 187.8737 | 162.0842
669.3625 | 602.3625 | 306.2268 | 196.3818 | 183.0404 | 194.0002 | 188.0093 | 162.1854
670.3639 | 603.3639 | 306.3832 | 196.5121 | 183.1891 | 194.1582 | 188.1401 | 162.2848
671.3554 | 604.3554 | 306.3584 | 196.6517 | 183.3236 | 194.3089 | 188.2639 | 162.391
672.3568 | 605.3568 | 306.2817 | 196.7797 | 183.4658 | 194.4675 | 188.402 | 162.4842
673.3582 | 606.3582 | 306.24 | 196.9133 | 183.6127 | 194.6286 | 188.5378 | 162.5937
674.3597 | 607.3597 | 306.2343 | 197.0278 | 183.7525 | 194.7787 | 188.6986 | 162.6867
675.3611 | 608.3611 | 306.2425 | 197.1431 | 183.8964 | 194.8986 | 188.8604 | 162.7844
676.3626 | 609.3626 | 306.2903 | 197.2601 | 184.0371 | 195.0452 | 188.9953 | 162.8798
677.354 | 610.354 | 306.3992 | 197.3865 | 184.1854 | 195.1443 | 189.1225 | 162.9748
678.3554 | 611.3554 | 306.5205 | 197.4932 | 184.3338 | 195.191 | 189.2525 | 163.0656
679.3569 | 612.3569 | 306.5208 | 197.6109 | 184.479 | 195.2588 | 189.3874 | 163.1542
680.3583 | 613.3583 | 306.5228 | 197.7351 | 184.6164 | 195.3074 | 189.4935 | 163.255
681.3597 | 614.3597 | 306.3879 | 197.8482 | 184.7686 | 195.3693 | 189.5821 | 163.3429
682.3612 | 615.3612 | 306.2625 | 197.9593 | 184.9047 | 195.4507 | 189.6855 | 163.435
683.3626 | 616.3626 | 306.1347 | 198.0651 | 185.054 | 195.5355 | 189.7806 | 163.5434
684.3641 | 617.3641 | 305.9332 | 198.169 | 185.2046 | 195.6388 | 189.8531 | 163.6283
685.3655 | 618.3655 | 305.6904 | 198.266 | 185.3315 | 195.7303 | 189.9415 | 163.7101
686.3569 | 619.3569 | 305.5014 | 198.3601 | 185.4728 | 195.8264 | 190.0321 | 163.8019
687.3584 | 620.3584 | 305.3427 | 198.4622 | 185.6207 | 195.9577 | 190.0568 | 163.8962
688.3598 | 621.3598 | 305.2649 | 198.5622 | 185.752 | 196.0828 | 190.0996 | 163.9798
689.3613 | 622.3613 | 305.2582 | 198.6553 | 185.8928 | 196.2223 | 190.0914 | 164.0663
690.3627 | 623.3627 | 305.1671 | 198.7357 | 186.0291 | 196.3688 | 190.1102 | 164.1601
691.3641 | 624.3641 | 305.0707 | 198.824 | 186.1631 | 196.5199 | 190.0989 | 164.2521
692.3556 | 625.3556 | 304.9298 | 198.9032 | 186.2787 | 196.671 | 190.1187 | 164.3371
693.357 | 626.357 | 304.7592 | 198.9934 | 186.4273 | 196.8285 | 190.1336 | 164.4255
694.3584 | 627.3584 | 304.5997 | 199.0769 | 186.562 | 196.991 | 190.1751 | 164.5105
695.3599 | 628.3599 | 304.5152 | 199.1685 | 186.6988 | 197.154 | 190.2166 | 164.601
696.3613 | 629.3613 | 304.3845 | 199.2634 | 186.8399 | 197.3191 | 190.294 | 164.6803
697.3628 | 630.3628 | 304.2659 | 199.3585 | 186.9635 | 197.475 | 190.3507 | 164.7573
698.3542 | 631.3542 | 304.1878 | 199.4487 | 187.0973 | 197.6395 | 190.435 | 164.8407
699.3556 | 632.3556 | 304.1909 | 199.5333 | 187.2204 | 197.7988 | 190.5317 | 164.9214
700.3571 | 633.3571 | 304.2672 | 199.6371 | 187.3485 | 197.9612 | 190.6425 | 165.0015
701.3585 | 634.3585 | 304.2793 | 199.7386 | 187.4647 | 198.1142 | 190.7606 | 165.0907
702.3599 | 635.3599 | 304.2525 | 199.8328 | 187.5812 | 198.2669 | 190.8811 | 165.1698
703.3614 | 636.3614 | 304.2121 | 199.9392 | 187.7083 | 198.4221 | 190.9943 | 165.2568
704.3628 | 637.3628 | 304.1537 | 200.0421 | 187.829 | 198.5773 | 191.0987 | 165.3433
705.3542 | 638.3542 | 304.1968 | 200.1372 | 187.9479 | 198.7371 | 191.1834 | 165.4226
706.3557 | 639.3557 | 304.2589 | 200.2513 | 188.0707 | 198.8727 | 191.2762 | 165.5023
707.3571 | 640.3571 | 304.3401 | 200.3569 | 188.181 | 198.996 | 191.3814 | 165.5792
708.3586 | 641.3586 | 304.4578 | 200.4602 | 188.2945 | 199.1151 | 191.4905 | 165.6683
709.36 | 642.36 | 304.4651 | 200.577 | 188.4019 | 199.2374 | 191.5868 | 165.7535
710.3614 | 643.3614 | 304.5278 | 200.6892 | 188.5137 | 199.3611 | 191.7075 | 165.8327
711.3629 | 644.3629 | 304.5484 | 200.7902 | 188.6305 | 199.482 | 191.7717 | 165.9296
712.3643 | 645.3643 | 304.6261 | 200.9035 | 188.737 | 199.5913 | 191.8591 | 166.0132
713.3558 | 646.3558 | 304.6733 | 201.0142 | 188.85 | 199.7099 | 191.9227 | 166.0974
714.3572 | 647.3572 | 304.8166 | 201.1166 | 188.9614 | 199.8319 | 192.0058 | 166.1918
715.3586 | 648.3586 | 304.9045 | 201.226 | 189.0837 | 199.9588 | 192.0397 | 166.2835
716.3601 | 649.3601 | 305.0595 | 201.3277 | 189.1864 | 200.0772 | 192.1012 | 166.3784
717.3615 | 650.3615 | 305.1626 | 201.435 | 189.3051 | 200.208 | 192.1642 | 166.4654
718.363 | 651.363 | 305.246 | 201.5316 | 189.4262 | 200.2977 | 192.2655 | 166.5607
719.3544 | 652.3544 | 305.2976 | 201.639 | 189.5355 | 200.3934 | 192.3608 | 166.6542
720.3558 | 653.3558 | 305.449 | 201.7405 | 189.6455 | 200.4779 | 192.4658 | 166.7426
721.3573 | 654.3573 | 305.7197 | 201.8435 | 189.7558 | 200.5451 | 192.5615 | 166.8278
722.3587 | 655.3587 | 305.9314 | 201.9601 | 189.8616 | 200.5959 | 192.6563 | 166.9162
723.3601 | 656.3601 | 305.9968 | 202.06 | 189.9796 | 200.6459 | 192.7549 | 167.0011
724.3616 | 657.3616 | 306.0011 | 202.1635 | 190.0732 | 200.691 | 192.8523 | 167.0964
725.363 | 658.363 | 306.079 | 202.2756 | 190.1879 | 200.749 | 192.9721 | 167.1877
726.3544 | 659.3544 | 306.1773 | 202.3872 | 190.2994 | 200.8053 | 193.0834 | 167.2721
727.3559 | 660.3559 | 306.3069 | 202.493 | 190.4094 | 200.8859 | 193.1974 | 167.3564
728.3573 | 661.3573 | 306.3846 | 202.5968 | 190.5345 | 200.9886 | 193.289 | 167.4497
729.3588 | 662.3588 | 306.4206 | 202.6994 | 190.6569 | 201.1066 | 193.4139 | 167.5378
730.3602 | 663.3602 | 306.5471 | 202.8047 | 190.7794 | 201.2323 | 193.5202 | 167.6287
731.3616 | 664.3616 | 306.7025 | 202.9048 | 190.8983 | 201.3244 | 193.6508 | 167.723
732.3631 | 665.3631 | 306.6526 | 203.01 | 191.0042 | 201.4256 | 193.7525 | 167.8148
733.3645 | 666.3645 | 306.605 | 203.117 | 191.1281 | 201.5186 | 193.8633 | 167.9056
734.356 | 667.356 | 306.5174 | 203.2339 | 191.2221 | 201.607 | 193.9447 | 167.9996
735.3574 | 668.3574 | 306.4497 | 203.3426 | 191.3539 | 201.715 | 194.0684 | 168.0938
736.3588 | 669.3588 | 306.3974 | 203.4567 | 191.4649 | 201.8452 | 194.1347 | 168.1748
737.3603 | 670.3603 | 306.3725 | 203.5696 | 191.5687 | 201.9773 | 194.2082 | 168.267
738.3617 | 671.3617 | 306.3682 | 203.686 | 191.6767 | 202.1052 | 194.3021 | 168.3467
739.3632 | 672.3632 | 306.2904 | 203.7963 | 191.7922 | 202.2153 | 194.402 | 168.4226
740.3546 | 673.3546 | 306.2661 | 203.8995 | 191.9068 | 202.3341 | 194.4922 | 168.507
741.356 | 674.356 | 306.2265 | 204.0026 | 192.0208 | 202.4624 | 194.5813 | 168.5789
742.3575 | 675.3575 | 306.1801 | 204.1045 | 192.1444 | 202.6102 | 194.6893 | 168.6694
743.3589 | 676.3589 | 306.1735 | 204.2065 | 192.2671 | 202.7422 | 194.7879 | 168.7492
744.3603 | 677.3603 | 306.2032 | 204.3033 | 192.3882 | 202.8582 | 194.8961 | 168.8275
745.3618 | 678.3618 | 306.261 | 204.4026 | 192.5032 | 202.9268 | 195.0027 | 168.9156
746.3532 | 679.3532 | 306.3581 | 204.5015 | 192.6223 | 202.9883 | 195.1043 | 169.0023
747.3546 | 680.3546 | 306.47 | 204.5939 | 192.7435 | 203.0252 | 195.2002 | 169.0914
748.3561 | 681.3561 | 306.6078 | 204.6818 | 192.8495 | 203.0374 | 195.2925 | 169.1703
749.3575 | 682.3575 | 306.7392 | 204.7715 | 192.965 | 203.039 | 195.3841 | 169.2563
750.359 | 683.359 | 306.7616 | 204.8669 | 193.0778 | 203.0091 | 195.4903 | 169.3474
751.3604 | 684.3604 | 306.8062 | 204.9602 | 193.1853 | 202.9589 | 195.5844 | 169.4304
752.3618 | 685.3618 | 306.9146 | 205.0563 | 193.2849 | 202.9354 | 195.6981 | 169.5187
753.3633 | 686.3633 | 306.8281 | 205.1518 | 193.3861 | 202.9285 | 195.7933 | 169.615
754.3647 | 687.3647 | 306.8157 | 205.2557 | 193.472 | 202.9521 | 195.9087 | 169.703
755.3561 | 688.3561 | 306.709 | 205.3465 | 193.5795 | 203.0041 | 196.0181 | 169.7941
756.3576 | 689.3576 | 306.7492 | 205.4414 | 193.6891 | 203.0886 | 196.1271 | 169.8887
757.359 | 690.359 | 306.7931 | 205.5342 | 193.7738 | 203.2065 | 196.2459 | 169.9743
758.3605 | 691.3605 | 306.753 | 205.6322 | 193.8942 | 203.3211 | 196.3722 | 170.0716
759.3619 | 692.3619 | 306.6996 | 205.7306 | 193.9926 | 203.4598 | 196.4846 | 170.1596
760.3633 | 693.3633 | 306.6333 | 205.8208 | 194.108 | 203.5903 | 196.5914 | 170.236
761.3548 | 694.3548 | 306.5414 | 205.9081 | 194.2165 | 203.7378 | 196.6871 | 170.3191
762.3562 | 695.3562 | 306.4895 | 205.9982 | 194.3099 | 203.9092 | 196.7679 | 170.4048
763.3577 | 696.3577 | 306.5157 | 206.0842 | 194.4292 | 204.0979 | 196.8468 | 170.4998
764.3591 | 697.3591 | 306.4923 | 206.1688 | 194.5479 | 204.2789 | 196.9282 | 170.5824
765.3605 | 698.3605 | 306.5563 | 206.2525 | 194.669 | 204.4425 | 197.012 | 170.6612
766.362 | 699.362 | 306.5122 | 206.3377 | 194.7906 | 204.5902 | 197.1017 | 170.7434
767.3634 | 700.3634 | 306.4046 | 206.4214 | 194.8994 | 204.7426 | 197.1893 | 170.8234
768.3548 | 701.3548 | 306.2856 | 206.5037 | 195.0184 | 204.8884 | 197.2861 | 170.9029
769.3563 | 702.3563 | 306.3032 | 206.5963 | 195.139 | 205.0346 | 197.3945 | 170.9803
770.3577 | 703.3577 | 306.307 | 206.6872 | 195.2729 | 205.1711 | 197.5042 | 171.053
771.3592 | 704.3592 | 306.1925 | 206.7744 | 195.3771 | 205.3014 | 197.6101 | 171.1383
772.3606 | 705.3606 | 306.0378 | 206.8783 | 195.5095 | 205.4169 | 197.7166 | 171.2218
773.362 | 706.362 | 305.9273 | 206.971 | 195.6353 | 205.5409 | 197.8233 | 171.3044
774.3635 | 707.3635 | 305.7505 | 207.0643 | 195.7531 | 205.6742 | 197.9518 | 171.3754
775.3649 | 708.3649 | 305.6973 | 207.1525 | 195.8637 | 205.8244 | 198.0769 | 171.457
776.3563 | 709.3563 | 305.7504 | 207.2499 | 195.9766 | 205.9757 | 198.1853 | 171.5371
777.3578 | 710.3578 | 305.7989 | 207.3511 | 196.0907 | 206.1339 | 198.3018 | 171.6101
778.3592 | 711.3592 | 305.8661 | 207.4429 | 196.2118 | 206.2749 | 198.3892 | 171.6842
779.3607 | 712.3607 | 305.8662 | 207.5388 | 196.3243 | 206.4124 | 198.4874 | 171.7589
780.3621 | 713.3621 | 305.8214 | 207.6315 | 196.4338 | 206.5443 | 198.5798 | 171.8278
781.3635 | 714.3635 | 305.6869 | 207.7198 | 196.556 | 206.6621 | 198.6489 | 171.9092
782.355 | 715.355 | 305.5521 | 207.8071 | 196.6637 | 206.7908 | 198.728 | 171.9752
783.3564 | 716.3564 | 305.4576 | 207.8922 | 196.7745 | 206.9312 | 198.8071 | 172.0557
784.3579 | 717.3579 | 305.4214 | 207.9763 | 196.8729 | 207.0763 | 198.9137 | 172.1302
785.3593 | 718.3593 | 305.4583 | 208.0574 | 196.9923 | 207.2332 | 199.0117 | 172.2116
786.3607 | 719.3607 | 305.6685 | 208.1389 | 197.1072 | 207.389 | 199.1064 | 172.2799
787.3622 | 720.3622 | 305.8123 | 208.2234 | 197.2218 | 207.538 | 199.2127 | 172.354
788.3536 | 721.3536 | 305.8865 | 208.3163 | 197.3379 | 207.6524 | 199.3735 | 172.4356
789.355 | 722.355 | 306.0192 | 208.3963 | 197.4577 | 207.7525 | 199.4983 | 172.5143
790.3565 | 723.3565 | 306.1121 | 208.4878 | 197.5709 | 207.8608 | 199.6388 | 172.5846
791.3579 | 724.3579 | 306.1271 | 208.5519 | 197.694 | 207.9732 | 199.7893 | 172.6623
792.3594 | 725.3594 | 306.2063 | 208.6253 | 197.8091 | 208.1093 | 199.9396 | 172.7299
793.3608 | 726.3608 | 306.1785 | 208.7011 | 197.9294 | 208.2353 | 200.0703 | 172.8063
794.3622 | 727.3622 | 306.0201 | 208.7793 | 198.0653 | 208.3728 | 200.2111 | 172.8684
795.3637 | 728.3637 | 305.9548 | 208.8562 | 198.1734 | 208.5002 | 200.3411 | 172.9388
796.3651 | 729.3651 | 305.9408 | 208.9424 | 198.3072 | 208.6341 | 200.4882 | 173.0025
797.3565 | 730.3565 | 305.9147 | 209.0275 | 198.4166 | 208.7566 | 200.625 | 173.0651
798.358 | 731.358 | 305.8963 | 209.1035 | 198.5326 | 208.8802 | 200.7559 | 173.141
799.3594 | 732.3594 | 305.7034 | 209.1807 | 198.6427 | 208.9932 | 200.8359 | 173.1974
800.3609 | 733.3609 | 305.5657 | 209.2545 | 198.7673 | 209.1154 | 200.9356 | 173.2697
801.3623 | 734.3623 | 305.48 | 209.332 | 198.8957 | 209.2476 | 201.0005 | 173.3299
802.3637 | 735.3637 | 305.3777 | 209.411 | 199.0033 | 209.3785 | 201.0782 | 173.4
803.3552 | 736.3552 | 305.399 | 209.4927 | 199.1259 | 209.5129 | 201.1601 | 173.4661
804.3566 | 737.3566 | 305.4968 | 209.5681 | 199.239 | 209.6269 | 201.25 | 173.5372
805.358 | 738.358 | 305.5347 | 209.6544 | 199.3558 | 209.7311 | 201.356 | 173.6017
806.3595 | 739.3595 | 305.4585 | 209.7303 | 199.4546 | 209.822 | 201.4587 | 173.6704
807.3609 | 740.3609 | 305.4563 | 209.8095 | 199.5759 | 209.9029 | 201.5787 | 173.7328
808.3724 | 741.3724 | 305.3979 | 209.891 | 199.6807 | 209.9882 | 201.6824 | 173.79
809.3538 | 742.3538 | 305.4362 | 209.9796 | 199.8043 | 210.0914 | 201.7704 | 173.8575
810.3552 | 743.3552 | 305.4314 | 210.0614 | 199.9228 | 210.2086 | 201.8504 | 173.9209
811.3567 | 744.3567 | 305.4466 | 210.1433 | 200.0304 | 210.3322 | 201.9474 | 173.9824
812.3581 | 745.3581 | 305.4402 | 210.2291 | 200.1431 | 210.4606 | 202.0065 | 174.0554
813.3596 | 746.3596 | 305.3873 | 210.3139 | 200.2641 | 210.5923 | 202.0695 | 174.1122
814.361 | 747.361 | 305.2553 | 210.4002 | 200.364 | 210.7051 | 202.109 | 174.1771
815.3624 | 748.3624 | 305.0817 | 210.4762 | 200.4836 | 210.8023 | 202.1506 | 174.2399
816.3639 | 749.3639 | 304.822 | 210.551 | 200.5736 | 210.8978 | 202.1996 | 174.303
817.3653 | 750.3653 | 304.7269 | 210.6195 | 200.6718 | 210.9891 | 202.2409 | 174.3673
818.3567 | 751.3567 | 304.582 | 210.6943 | 200.7716 | 211.0687 | 202.2885 | 174.4316
819.3582 | 752.3582 | 304.4384 | 210.7628 | 200.8719 | 211.1398 | 202.3411 | 174.4993
820.3596 | 753.3596 | 304.3199 | 210.8439 | 200.9649 | 211.2431 | 202.3776 | 174.5634
821.3611 | 754.3611 | 304.2832 | 210.911 | 201.0549 | 211.3719 | 202.4015 | 174.626
822.3625 | 755.3625 | 304.2847 | 210.9795 | 201.1587 | 211.5124 | 202.4319 | 174.6898
823.3539 | 756.3539 | 304.3281 | 211.0498 | 201.2567 | 211.6594 | 202.4385 | 174.7592
824.3554 | 757.3554 | 304.3643 | 211.1204 | 201.3458 | 211.8007 | 202.4654 | 174.8209
825.3568 | 758.3568 | 304.3648 | 211.1957 | 201.4399 | 211.9538 | 202.4957 | 174.8878
826.3582 | 759.3582 | 304.3894 | 211.2598 | 201.5225 | 212.1068 | 202.5275 | 174.953
827.3597 | 760.3597 | 304.4147 | 211.3283 | 201.6172 | 212.2415 | 202.5672 | 175.0124
828.3611 | 761.3611 | 304.4951 | 211.3969 | 201.7107 | 212.3572 | 202.5975 | 175.0736
829.3726 | 762.3726 | 304.5204 | 211.4708 | 201.7827 | 212.4507 | 202.647 | 175.1305
830.354 | 763.354 | 304.5167 | 211.5394 | 201.8928 | 212.5446 | 202.6864 | 175.1871
831.3554 | 764.3554 | 304.5497 | 211.6058 | 201.9706 | 212.6472 | 202.7756 | 175.2451
832.3569 | 765.3569 | 304.537 | 211.679 | 202.0678 | 212.7651 | 202.8382 | 175.3008 | Time of first failure
833.3583 | 766.3583 | 304.5724 | 211.7388 | 202.1619 | 212.8901 | 202.91 | 175.3592 | 766 | 0
834.3598 | 767.3598 | 304.6245 | 211.806 | 202.2595 | 213.0258 | 202.9893 | 175.4144 | 766 | 900
835.3612 | 768.3612 | 304.6161 | 211.8723 | 202.3543 | 213.1504 | 203.0666 | 175.4604
836.3626 | 769.3626 | 304.5968 | 211.9361 | 202.4543 | 213.2663 | 203.1275 | 175.5225
837.3641 | 770.3641 | 304.6334 | 212.0006 | 202.554 | 213.3767 | 203.2031 | 175.5827
838.3655 | 771.3655 | 304.6803 | 212.069 | 202.6538 | 213.4941 | 203.2757 | 175.6439
839.3569 | 772.3569 | 304.737 | 212.13 | 202.7509 | 213.5952 | 203.3773 | 175.704
840.3584 | 773.3584 | 304.9227 | 212.1953 | 202.8421 | 213.6817 | 203.4382 | 175.7607
841.3598 | 774.3598 | 305.1247 | 212.2531 | 202.9459 | 213.7607 | 203.5114 | 175.8223
842.3613 | 775.3613 | 305.2867 | 212.3173 | 203.0304 | 213.8477 | 203.5662 | 175.8846
843.3627 | 776.3627 | 305.4095 | 212.3844 | 203.1389 | 213.9435 | 203.6303 | 175.9409
844.3641 | 777.3641 | 305.5869 | 212.4521 | 203.2311 | 214.035 | 203.7167 | 176.0074
845.3556 | 778.3556 | 305.7086 | 212.5111 | 203.3265 | 214.1394 | 203.7925 | 176.0725
846.357 | 779.357 | 305.8047 | 212.5742 | 203.4241 | 214.25 | 203.8607 | 176.137
847.3584 | 780.3584 | 305.9043 | 212.6359 | 203.5231 | 214.355 | 203.9412 | 176.2049
848.3599 | 781.3599 | 305.9365 | 212.6827 | 203.6162 | 214.4691 | 204.0283 | 176.274
849.3613 | 782.3613 | 305.9466 | 212.7409 | 203.7072 | 214.5993 | 204.0999 | 176.3472
850.3628 | 783.3628 | 305.9278 | 212.7886 | 203.8067 | 214.7254 | 204.1818 | 176.4246
851.3542 | 784.3542 | 305.9135 | 212.8457 | 203.8921 | 214.8553 | 204.2529 | 176.5039
852.3556 | 785.3556 | 305.9604 | 212.9023 | 204.0056 | 214.9856 | 204.3275 | 176.5786
853.3571 | 786.3571 | 306.095 | 212.9531 | 204.1075 | 215.111 | 204.3805 | 176.6561
854.3585 | 787.3585 | 306.1374 | 213.0185 | 204.2029 | 215.2361 | 204.4396 | 176.7317
855.3599 | 788.3599 | 306.0936 | 213.0678 | 204.2859 | 215.36 | 204.5195 | 176.8089
856.3614 | 789.3614 | 306.1311 | 213.1293 | 204.3959 | 215.4885 | 204.5833 | 176.8891
857.3628 | 790.3628 | 306.1918 | 213.187 | 204.4911 | 215.5958 | 204.6761 | 176.973
858.3643 | 791.3643 | 306.2267 | 213.2523 | 204.5921 | 215.7018 | 204.7608 | 177.0505
859.3557 | 792.3557 | 306.2313 | 213.314 | 204.6844 | 215.8121 | 204.8472 | 177.13
860.3571 | 793.3571 | 306.2131 | 213.3766 | 204.7701 | 215.9078 | 204.8737 | 177.2111
861.3586 | 794.3586 | 306.2598 | 213.4368 | 204.8564 | 216.0176 | 204.858 | 177.2891
862.36 | 795.36 | 306.2002 | 213.4996 | 204.9494 | 216.1291 | 204.7666 | 177.3695
863.3615 | 796.3615 | 306.1731 | 213.5639 | 205.0273 | 216.2463 | 204.6916 | 177.4398
864.3629 | 797.3629 | 306.2159 | 213.6193 | 205.1108 | 216.3773 | 204.6204 | 177.5228
865.3543 | 798.3543 | 306.273 | 213.6846 | 205.1962 | 216.5083 | 204.5953 | 177.5981
866.3558 | 799.3558 | 306.279 | 213.7454 | 205.2834 | 216.6229 | 204.6508 | 177.6776
867.3572 | 800.3572 | 306.2302 | 213.8058 | 205.3842 | 216.736 | 204.7549 | 177.7623
868.3586 | 801.3586 | 306.3042 | 213.8651 | 205.4615 | 216.8366 | 204.8472 | 177.8316
869.3601 | 802.3601 | 306.3989 | 213.9293 | 205.5507 | 216.9521 | 204.9814 | 177.902
870.3615 | 803.3615 | 306.3542 | 213.9835 | 205.6354 | 217.0658 | 205.1109 | 177.9721
871.363 | 804.363 | 306.2889 | 214.0432 | 205.7285 | 217.1842 | 205.2461 | 178.045
872.3544 | 805.3544 | 306.188 | 214.0968 | 205.8098 | 217.2924 | 205.3412 | 178.1002
873.3558 | 806.3558 | 306.1279 | 214.1443 | 205.9029 | 217.3992 | 205.4448 | 178.1698
874.3573 | 807.3573 | 306.0877 | 214.1943 | 205.9763 | 217.5195 | 205.5056 | 178.2307
875.3587 | 808.3587 | 305.965 | 214.2614 | 206.0629 | 217.6358 | 205.5753 | 178.2889
876.3601 | 809.3601 | 305.8727 | 214.3152 | 206.1473 | 217.7672 | 205.6234 | 178.3438
877.3616 | 810.3616 | 305.7568 | 214.3619 | 206.2251 | 217.8711 | 205.6857 | 178.4002
878.363 | 811.363 | 305.6741 | 214.4114 | 206.3099 | 217.9676 | 205.7315 | 178.4618
879.3645 | 812.3645 | 305.6176 | 214.4641 | 206.3849 | 218.0544 | 205.7588 | 178.5276
880.3559 | 813.3559 | 305.5943 | 214.5046 | 206.463 | 218.1427 | 205.7823 | 178.5896
881.3573 | 814.3573 | 305.5389 | 214.5492 | 206.5324 | 218.2347 | 205.8422 | 178.6543
882.3588 | 815.3588 | 305.4691 | 214.6052 | 206.615 | 218.3087 | 205.8886 | 178.7139
883.3602 | 816.3602 | 305.4032 | 214.6531 | 206.6845 | 218.3887 | 205.9514 | 178.7704
884.3616 | 817.3616 | 305.3911 | 214.6932 | 206.7465 | 218.4677 | 206.0258 | 178.8395
885.3631 | 818.3631 | 305.3659 | 214.7401 | 206.825 | 218.554 | 206.1265 | 178.9076
886.3645 | 819.3645 | 305.3926 | 214.7808 | 206.8897 | 218.6329 | 206.1892 | 178.9697
887.356 | 820.356 | 305.3835 | 214.8277 | 206.9686 | 218.7242 | 206.2685 | 179.0383
888.3574 | 821.3574 | 305.4001 | 214.8705 | 207.0403 | 218.8004 | 206.3291 | 179.1109
889.3588 | 822.3588 | 305.4286 | 214.9135 | 207.1136 | 218.8856 | 206.3914 | 179.1794
890.3603 | 823.3603 | 305.5709 | 214.9582 | 207.1955 | 218.949 | 206.4259 | 179.2366
891.3617 | 824.3617 | 305.654 | 215.009 | 207.2617 | 218.9658 | 206.4874 | 179.3029
892.3632 | 825.3632 | 305.6827 | 215.0595 | 207.3323 | 218.9873 | 206.5622 | 179.3653
893.3546 | 826.3546 | 305.7559 | 215.1043 | 207.3923 | 219.0126 | 206.6312 | 179.4358
894.356 | 827.356 | 305.7745 | 215.1517 | 207.4514 | 219.0269 | 206.687 | 179.5056
895.3575 | 828.3575 | 305.7984 | 215.1897 | 207.5121 | 219.0397 | 206.7472 | 179.576
896.3589 | 829.3589 | 305.8358 | 215.2381 | 207.5771 | 219.0692 | 206.8022 | 179.6471
897.3603 | 830.3603 | 305.75 | 215.2834 | 207.637 | 219.0989 | 206.8738 | 179.7288
898.3618 | 831.3618 | 305.6012 | 215.3328 | 207.6758 | 219.1327 | 206.954 | 179.7937
899.3632 | 832.3632 | 305.5487 | 215.3782 | 207.7306 | 219.1592 | 207.0538 | 179.8751
900.3647 | 833.3647 | 305.5268 | 215.4338 | 207.781 | 219.1661 | 207.1569 | 179.9395
901.3561 | 834.3561 | 305.4527 | 215.4895 | 207.8273 | 219.1788 | 207.2679 | 180.0045
902.3575 | 835.3575 | 305.4716 | 215.548 | 207.8698 | 219.2116 | 207.3475 | 180.0728
903.359 | 836.359 | 305.4333 | 215.6041 | 207.9263 | 219.2677 | 207.4393 | 180.1266
904.3604 | 837.3604 | 305.4738 | 215.6596 | 207.9669 | 219.3246 | 207.5208 | 180.1874
905.3618 | 838.3618 | 305.5345 | 215.7239 | 207.9984 | 219.3596 | 207.6073 | 180.2299
906.3633 | 839.3633 | 305.6328 | 215.7786 | 208.05 | 219.3761 | 207.7046 | 180.3054
907.3547 | 840.3547 | 305.7187 | 215.8251 | 208.0709 | 219.3876 | 207.7874 | 180.3703
908.3562 | 841.3562 | 305.7016 | 215.8778 | 208.1099 | 219.4061 | 207.8499 | 180.4242
909.3576 | 842.3576 | 305.6932 | 215.9309 | 208.1583 | 219.4466 | 207.8043 | 180.4916
910.359 | 843.359 | 305.7125 | 215.9812 | 208.1969 | 219.513 | 207.7743 | 180.5519
911.3605 | 844.3605 | 305.7908 | 216.0189 | 208.2475 | 219.588 | 207.8195 | 180.6108
912.3619 | 845.3619 | 305.8136 | 216.0727 | 208.2854 | 219.64 | 207.8855 | 180.6739
913.3634 | 846.3634 | 305.8088 | 216.1208 | 208.3468 | 219.6763 | 207.9609 | 180.7356
914.3548 | 847.3548 | 305.8165 | 216.1703 | 208.3928 | 219.7309 | 208.0587 | 180.8106
915.3562 | 848.3562 | 305.867 | 216.2099 | 208.4441 | 219.7906 | 208.1541 | 180.8606
916.3577 | 849.3577 | 305.9149 | 216.2669 | 208.5156 | 219.8649 | 208.2534 | 180.9308
917.3591 | 850.3591 | 305.8218 | 216.3154 | 208.5692 | 219.9523 | 208.362 | 181.001
918.3605 | 851.3605 | 305.7637 | 216.3715 | 208.6283 | 220.0348 | 208.4616 | 181.0648
919.362 | 852.362 | 305.7714 | 216.4257 | 208.6957 | 220.1192 | 208.5699 | 181.1292
920.3634 | 853.3634 | 305.8619 | 216.4814 | 208.7627 | 220.2143 | 208.7231 | 181.1823
921.3649 | 854.3649 | 305.9783 | 216.5294 | 208.8432 | 220.3233 | 208.8335 | 181.2473
922.3563 | 855.3563 | 306.0911 | 216.5917 | 208.9044 | 220.4303 | 208.9607 | 181.295
923.3577 | 856.3577 | 306.1972 | 216.6448 | 208.9877 | 220.5361 | 209.0815 | 181.3563
924.3592 | 857.3592 | 306.1777 | 216.7036 | 209.0676 | 220.6214 | 209.1935 | 181.4061
925.3606 | 858.3606 | 306.0481 | 216.7672 | 209.143 | 220.6973 | 209.3005 | 181.4673
926.362 | 859.362 | 305.947 | 216.8183 | 209.2161 | 220.7728 | 209.4058 | 181.5304
927.3635 | 860.3635 | 305.8882 | 216.8783 | 209.2927 | 220.8517 | 209.5054 | 181.5912
928.3549 | 861.3549 | 305.8206 | 216.9348 | 209.3772 | 220.9367 | 209.6037 | 181.653
929.3563 | 862.3563 | 305.8258 | 216.9994 | 209.4605 | 221.0371 | 209.6706 | 181.7113
930.3578 | 863.3578 | 305.8627 | 217.0485 | 209.5293 | 221.1208 | 209.6591 | 181.7744
931.3592 | 864.3592 | 305.7854 | 217.109 | 209.6094 | 221.2044 | 209.6614 | 181.8187
932.3607 | 865.3607 | 305.6655 | 217.1672 | 209.6977 | 221.2818 | 209.7175 | 181.8727
933.3621 | 866.3621 | 305.6393 | 217.2293 | 209.7831 | 221.3609 | 209.7702 | 181.9267
934.3635 | 867.3635 | 305.7237 | 217.2905 | 209.8559 | 221.442 | 209.7869 | 181.973
935.355 | 868.355 | 305.8873 | 217.3475 | 209.9303 | 221.5316 | 209.8297 | 182.0269
936.3564 | 869.3564 | 305.9461 | 217.4073 | 209.9986 | 221.6223 | 209.9053 | 182.0703
937.3579 | 870.3579 | 305.8941 | 217.4578 | 210.0931 | 221.7102 | 209.9928 | 182.1142
938.3593 | 871.3593 | 305.8317 | 217.5126 | 210.1672 | 221.8038 | 210.0546 | 182.1704
939.3607 | 872.3607 | 305.7886 | 217.5649 | 210.2516 | 221.9147 | 210.104 | 182.2128
940.3622 | 873.3622 | 305.7276 | 217.6156 | 210.3326 | 222.0178 | 210.1217 | 182.2613
941.3636 | 874.3636 | 305.6188 | 217.6674 | 210.404 | 222.1358 | 210.1719 | 182.3253
942.3651 | 875.3651 | 305.545 | 217.7128 | 210.4862 | 222.2598 | 210.2291 | 182.3776
943.3565 | 876.3565 | 305.4724 | 217.7598 | 210.5298 | 222.3591 | 210.2955 | 182.4359
944.3579 | 877.3579 | 305.3794 | 217.7916 | 210.6347 | 222.4533 | 210.3937 | 182.5022
945.3594 | 878.3594 | 305.3433 | 217.8364 | 210.7117 | 222.5374 | 210.4857 | 182.5644
946.3608 | 879.3608 | 305.2148 | 217.8763 | 210.7862 | 222.6024 | 210.5495 | 182.6341
947.3622 | 880.3622 | 305.1154 | 217.9253 | 210.8546 | 222.675 | 210.616 | 182.6963
948.3637 | 881.3637 | 304.9971 | 217.9637 | 210.9326 | 222.7293 | 210.6987 | 182.7573
949.3751 | 882.3751 | 304.9995 | 218.0073 | 210.9968 | 222.7904 | 210.78 | 182.8148
950.3565 | 883.3565 | 305.124 | 218.0463 | 211.0715 | 222.8137 | 210.8818 | 182.8673
951.358 | 884.358 | 305.1887 | 218.0873 | 211.1411 | 222.8401 | 210.9555 | 182.9211
952.3594 | 885.3594 | 305.3033 | 218.1296 | 211.1971 | 222.8831 | 211.0231 | 182.9668
953.3609 | 886.3609 | 305.325 | 218.1697 | 211.2566 | 222.9256 | 211.0821 | 183.0141
954.3623 | 887.3623 | 305.3745 | 218.2153 | 211.3248 | 222.9767 | 211.1582 | 183.0663
955.3637 | 888.3637 | 305.4256 | 218.2499 | 211.3902 | 222.9871 | 211.1971 | 183.119
956.3552 | 889.3552 | 305.5215 | 218.2933 | 211.447 | 223.0072 | 211.2558 | 183.1741
957.3566 | 890.3566 | 305.6313 | 218.3266 | 211.5063 | 223.049 | 211.3027 | 183.2238
958.3581 | 891.3581 | 305.6268 | 218.3706 | 211.574 | 223.1157 | 211.3473 | 183.2802
959.3595 | 892.3595 | 305.5586 | 218.4029 | 211.6341 | 223.1893 | 211.3731 | 183.3328
960.3609 | 893.3609 | 305.4009 | 218.4428 | 211.6907 | 223.2796 | 211.4211 | 183.3831
961.3624 | 894.3624 | 305.3913 | 218.4795 | 211.7527 | 223.3744 | 211.4638 | 183.4379
962.3538 | 895.3538 | 305.417 | 218.5143 | 211.8147 | 223.4397 | 211.5254 | 183.4868
963.3653 | 896.3653 | 305.4498 | 218.5463 | 211.8789 | 223.5115 | 211.5584 | 183.5483
964.3567 | 897.3567 | 305.3997 | 218.5852 | 211.9385 | 223.6055 | 211.6223 | 183.5869
965.3581 | 898.3581 | 305.2934 | 218.6182 | 211.9987 | 223.6748 | 211.6734 | 183.6325
966.3596 | 899.3596 | 305.2056 | 218.6499 | 212.0581 | 223.7297 | 211.7386 | 183.6773
967.361 | 900.361 | 305.1145 | 218.6784 | 212.1349 | 223.8117 | 211.812 | 183.7155
968.3624 | 901.3624 | 305.0691 | 218.7143 | 212.2037 | 223.8959 | 211.897 | 183.757
969.3639 | 902.3639 | 305.0905 | 218.7455 | 212.2757 | 223.9792 | 211.9613 | 183.7968
970.3553 | 903.3553 | 305.1855 | 218.7642 | 212.3592 | 224.0847 | 212.1283 | 183.8906
971.3567 | 904.3567 | 305.2732 | 218.8141 | 212.422 | 224.2184 | 212.1609 | 183.8639
972.3582 | 905.3582 | 305.4169 | 218.8474 | 212.4898 | 224.3358 | 212.2675 | 183.8964
973.3596 | 906.3596 | 305.4173 | 218.8758 | 212.5818 | 224.4324 | 212.3856 | 183.9546
974.3611 | 907.3611 | 305.4502 | 218.9188 | 212.6475 | 224.5294 | 212.4527 | 183.9577
975.3625 | 908.3625 | 305.319 | 218.9511 | 212.7269 | 224.6104 | 212.5257 | 184.0033
976.3639 | 909.3639 | 305.2614 | 218.9892 | 212.7923 | 224.6796 | 212.6086 | 184.0354
977.3554 | 910.3554 | 305.3289 | 219.0192 | 212.875 | 224.7548 | 212.6827 | 184.0716
978.3568 | 911.3568 | 305.4697 | 219.0571 | 212.9607 | 224.8502 | 212.7314 | 184.1078
979.3582 | 912.3582 | 305.6315 | 219.0897 | 213.0295 | 224.8953 | 212.8151 | 184.1482
980.3597 | 913.3597 | 305.7773 | 219.1161 | 213.1243 | 224.9132 | 212.9809 | 184.2175
981.3611 | 914.3611 | 305.7275 | 219.1725 | 213.1972 | 224.9709 | 212.9996 | 184.2229
982.3626 | 915.3626 | 305.7036 | 219.2137 | 213.278 | 225.009 | 213.0813 | 184.2617
983.364 | 916.364 | 305.6814 | 219.2528 | 213.3504 | 225.0636 | 213.1626 | 184.3067
984.3554 | 917.3554 | 305.6382 | 219.2876 | 213.4375 | 225.1331 | 213.2261 | 184.3445
985.3569 | 918.3569 | 305.5476 | 219.3319 | 213.5077 | 225.1594 | 213.3036 | 184.381
986.3583 | 919.3583 | 305.54 | 219.368 | 213.584 | 225.2094 | 213.36 | 184.4164
987.3598 | 920.3598 | 305.5368 | 219.3539 | 213.6722 | 225.2882 | 213.5537 | 184.5516
988.3612 | 921.3612 | 305.5694 | 219.433 | 213.7331 | 225.401 | 213.4629 | 184.4722
989.4828 | 922.4828 | 305.5551 | 219.4211 | 213.8374 | 225.4984 | 213.6278 | 184.6085
990.3641 | 923.3641 | 305.5278 | 219.479 | 213.8926 | 225.6114 | 213.5539 | 184.5516
991.3655 | 924.3655 | 305.5646 | 219.5077 | 213.9882 | 225.7202 | 213.5508 | 184.5767
992.3569 | 925.3569 | 305.5423 | 219.5458 | 214.0649 | 225.8146 | 213.5862 | 184.6184
993.3584 | 926.3584 | 305.4794 | 219.5681 | 214.1412 | 225.829 | 213.6168 | 184.653
994.3598 | 927.3598 | 305.4625 | 219.5913 | 214.2272 | 225.8339 | 213.5841 | 184.6972
995.3613 | 928.3613 | 305.474 | 219.6173 | 214.3088 | 225.9084 | 213.5878 | 184.737
996.3627 | 929.3627 | 305.4109 | 219.572 | 214.4112 | 225.9445 | 213.8565 | 184.9629
997.3641 | 930.3641 | 305.3774 | 219.6655 | 214.4592 | 226.0648 | 213.6281 | 184.8156
998.3556 | 931.3556 | 305.2939 | 219.6864 | 214.5275 | 226.1778 | 213.6635 | 184.8414
999.357 | 932.357 | 305.2717 | 219.6972 | 214.6019 | 226.2674 | 213.6593 | 184.8845
1000.3584 | 933.3584 | 305.2448 | 219.7134 | 214.6878 | 226.3712 | 213.6938 | 184.9232
1001.3599 | 934.3599 | 305.1737 | 219.7324 | 214.7594 | 226.3573 | 213.7153 | 184.9581
1002.3613 | 935.3613 | 305.1304 | 219.7364 | 214.8355 | 226.4077 | 213.7426 | 184.9987
1003.3628 | 936.3628 | 305.0665 | 219.7474 | 214.8959 | 226.4338 | 213.7842 | 185.0333
1004.3542 | 937.3542 | 305.0999 | 219.7601 | 214.96 | 226.5169 | 213.8603 | 185.0712
1005.3556 | 938.3556 | 305.2241 | 219.7725 | 215.0304 | 226.565 | 213.9649 | 185.1049
1006.3571 | 939.3571 | 305.2321 | 219.7834 | 215.0924 | 226.538 | 214.0141 | 185.1294
1007.3585 | 940.3585 | 305.2373 | 219.7958 | 215.1555 | 226.4347 | 214.0823 | 185.171
1008.36 | 941.36 | 305.2537 | 219.8193 | 215.2273 | 226.2974 | 214.1052 | 185.1964
1009.3614 | 942.3614 | 305.2691 | 219.8295 | 215.2824 | 226.3339 | 214.1178 | 185.2293
1010.3628 | 943.3628 | 305.2204 | 219.8438 | 215.3467 | 226.4207 | 214.1616 | 185.2616
1011.3643 | 944.3643 | 305.1962 | 219.8577 | 215.402 | 226.5248 | 214.1717 | 185.2997
1012.3557 | 945.3557 | 305.1807 | 219.8656 | 215.4627 | 226.6421 | 214.1635 | 185.3303
1013.3571 | 946.3571 | 305.1831 | 219.8814 | 215.5198 | 226.7236 | 214.2042 | 185.3722
1014.3586 | 947.3586 | 305.1431 | 219.8915 | 215.5995 | 226.5769 | 214.2041 | 185.4157
1015.36 | 948.36 | 305.0555 | 219.8942 | 215.6545 | 226.5898 | 214.2206 | 185.445
1016.3615 | 949.3615 | 305.0216 | 219.9024 | 215.7155 | 226.6776 | 214.2488 | 185.4817
1017.3629 | 950.3629 | 304.9943 | 219.9102 | 215.7846 | 226.7569 | 214.2951 | 185.5174
1018.3643 | 951.3643 | 304.8792 | 219.9157 | 215.8424 | 226.724 | 214.3729 | 185.547
1019.3558 | 952.3558 | 304.7729 | 219.9309 | 215.8915 | 226.7875 | 214.4428 | 185.5755
1020.3572 | 953.3572 | 304.6519 | 219.9384 | 215.9505 | 226.8414 | 214.4912 | 185.6081
1021.3586 | 954.3586 | 304.6114 | 219.9506 | 216.0183 | 226.9035 | 214.5039 | 185.6435
1022.3601 | 955.3601 | 304.5672 | 219.9629 | 216.0775 | 226.98 | 214.5436 | 185.6769
1023.3615 | 956.3615 | 304.521 | 219.9721 | 216.1487 | 227.0957 | 214.5663 | 185.7
1024.363 | 957.363 | 304.5446 | 219.9826 | 216.2158 | 227.2239 | 214.5966 | 185.7225
1025.3544 | 958.3544 | 304.5504 | 219.9975 | 216.2847 | 227.3818 | 214.6419 | 185.7621
1026.3558 | 959.3558 | 304.5114 | 220.0038 | 216.3522 | 227.5412 | 214.6764 | 185.7803
1027.3573 | 960.3573 | 304.5081 | 220.0137 | 216.4137 | 227.611 | 214.7194 | 185.8058
1028.3587 | 961.3587 | 304.6373 | 220.0125 | 216.4807 | 227.7812 | 214.7857 | 185.8294
1029.3601 | 962.3601 | 304.751 | 220.0226 | 216.5614 | 227.7493 | 214.8403 | 185.852
1030.3616 | 963.3616 | 304.7813 | 220.0219 | 216.6448 | 227.8452 | 214.9211 | 185.8797
1031.363 | 964.363 | 304.8406 | 220.0205 | 216.7035 | 227.9295 | 215.0095 | 185.9047
1032.3645 | 965.3645 | 304.8263 | 220.0199 | 216.7949 | 228.0838 | 215.057 | 185.9314
1033.3559 | 966.3559 | 304.7805 | 220.0138 | 216.8721 | 228.1766 | 215.0168 | 185.9563
1034.3573 | 967.3573 | 304.7209 | 220.0104 | 216.9364 | 228.2442 | 214.9499 | 185.9762
1035.3588 | 968.3588 | 304.7871 | 220.0022 | 217.0157 | 228.3343 | 214.8624 | 186.0048
1036.3602 | 969.3602 | 304.8562 | 219.993 | 217.102 | 228.341 | 214.8603 | 186.0452
1037.3617 | 970.3617 | 304.907 | 219.9788 | 217.1624 | 228.4513 | 214.8185 | 186.0705
1038.3631 | 971.3631 | 304.8982 | 219.9638 | 217.2336 | 228.6115 | 214.8446 | 186.113
1039.3545 | 972.3545 | 304.9287 | 219.9523 | 217.3083 | 228.6914 | 214.8474 | 186.1525
1040.356 | 973.356 | 304.9846 | 219.9301 | 217.3716 | 228.7961 | 214.8708 | 186.1936
1041.3574 | 974.3574 | 305.0549 | 219.9067 | 217.4539 | 228.8366 | 214.8984 | 186.2238
1042.3588 | 975.3588 | 305.2058 | 219.8705 | 217.534 | 228.9621 | 214.9655 | 186.2597
1043.3603 | 976.3603 | 305.3743 | 219.8332 | 217.6057 | 228.9888 | 215.0417 | 186.2888
1044.3617 | 977.3617 | 305.4221 | 219.7811 | 217.6732 | 228.9091 | 215.11 | 186.3256
1045.3632 | 978.3632 | 305.3924 | 219.718 | 217.7581 | 228.926 | 215.1496 | 186.357
1046.3546 | 979.3546 | 305.3708 | 219.6593 | 217.8266 | 228.9526 | 215.1801 | 186.3886
1047.356 | 980.356 | 305.4295 | 219.6194 | 217.871 | 228.9627 | 215.2635 | 186.4191
1048.3575 | 981.3575 | 305.4902 | 219.6257 | 217.9412 | 228.9686 | 215.3313 | 186.45
1049.3589 | 982.3589 | 305.4685 | 219.6348 | 218.0099 | 229.0101 | 215.4262 | 186.4979
1050.3603 | 983.3603 | 305.4352 | 219.6598 | 218.077 | 229.0953 | 215.471 | 186.5285
1051.3618 | 984.3618 | 305.4013 | 219.6933 | 218.1395 | 229.2326 | 215.5442 | 186.5712
1052.3632 | 985.3632 | 305.3534 | 219.7214 | 218.188 | 229.2436 | 215.603 | 186.609
1053.3747 | 986.3747 | 305.2485 | 219.768 | 218.2665 | 229.3189 | 215.6404 | 186.6528
1054.3561 | 987.3561 | 305.1914 | 219.7984 | 218.3254 | 229.3199 | 215.6425 | 186.697
1055.3575 | 988.3575 | 305.2017 | 219.8454 | 218.3981 | 229.4498 | 215.6366 | 186.7362
1056.359 | 989.359 | 305.1953 | 219.8904 | 218.4588 | 229.1942 | 215.6959 | 186.7841
1057.3604 | 990.3604 | 305.1282 | 219.9324 | 218.536 | 229.0661 | 215.7731 | 186.8284
1058.3618 | 991.3618 | 305.0464 | 219.9778 | 218.5942 | 228.9704 | 215.8443 | 186.8667
1059.3633 | 992.3633 | 304.9254 | 220.0232 | 218.6395 | 229.069 | 215.8821 | 186.9122
1060.3647 | 993.3647 | 304.8242 | 220.0723 | 218.7052 | 228.9128 | 215.847 | 186.9501
1061.3562 | 994.3562 | 304.8351 | 220.1247 | 218.7681 | 228.9567 | 215.8326 | 186.9863
1062.3576 | 995.3576 | 304.818 | 220.1724 | 218.8167 | 229.1372 | 215.8823 | 187.0207
1063.359 | 996.359 | 304.8631 | 220.213 | 218.8659 | 229.2821 | 215.9417 | 187.0575
1064.3605 | 997.3605 | 304.9378 | 220.259 | 218.9215 | 229.1089 | 216.0127 | 187.095
1065.3619 | 998.3619 | 304.9503 | 220.3075 | 218.9766 | 228.8662 | 216.0881 | 187.1478
1066.3634 | 999.3634 | 305.037 | 220.3585 | 219.0106 | 228.622 | 216.1454 | 187.1779
1067.3548 | 1000.3548 | 304.9792 | 220.4085 | 219.0911 | 228.6291 | 216.1744 | 187.2139
1068.3562 | 1001.3562 | 304.9134 | 220.4535 | 219.1435 | 228.4572 | 216.2054 | 187.2549
1069.3577 | 1002.3577 | 304.9087 | 220.4944 | 219.1926 | 228.5365 | 216.1957 | 187.2941
1070.3591 | 1003.3591 | 304.9379 | 220.5291 | 219.2426 | 228.4826 | 216.234 | 187.3309
1071.3605 | 1004.3605 | 304.9879 | 220.556 | 219.2933 | 228.4458 | 216.2607 | 187.3768
1072.362 | 1005.362 | 305.0176 | 220.5852 | 219.3412 | 228.3582 | 216.3579 | 187.4131
1073.3634 | 1006.3634 | 304.9877 | 220.6199 | 219.3921 | 228.6132 | 216.4473 | 187.4523
1074.3548 | 1007.3548 | 304.9566 | 220.6609 | 219.4419 | 228.7071 | 216.5337 | 187.4986
1075.3563 | 1008.3563 | 304.9366 | 220.6888 | 219.4957 | 228.8476 | 216.5562 | 187.5518
1076.3577 | 1009.3577 | 305.0034 | 220.7602 | 219.5494 | 228.9392 | 216.5605 | 187.5776
1077.3592 | 1010.3592 | 305.0743 | 220.8004 | 219.5938 | 229.0909 | 216.5292 | 187.6139
1078.3606 | 1011.3606 | 305.1965 | 220.8412 | 219.652 | 229.2134 | 216.5798 | 187.6489
1079.362 | 1012.362 | 305.2715 | 220.899 | 219.7253 | 229.3585 | 216.6111 | 187.6831
1080.3635 | 1013.3635 | 305.2617 | 220.9509 | 219.776 | 229.4059 | 216.6193 | 187.7178
1081.3549 | 1014.3549 | 305.3295 | 221.0091 | 219.8416 | 229.4999 | 216.6444 | 187.7604
1082.3564 | 1015.3564 | 305.3587 | 221.0546 | 219.9123 | 229.6139 | 216.6633 | 187.7955
1083.3578 | 1016.3578 | 305.3205 | 221.1159 | 219.9772 | 229.8523 | 216.7041 | 187.8264
1084.3592 | 1017.3592 | 305.2553 | 221.1521 | 220.0255 | 229.9132 | 216.7495 | 187.8556
1085.3607 | 1018.3607 | 305.2028 | 221.1815 | 220.098 | 230.0549 | 216.8004 | 187.8907
1086.3621 | 1019.3621 | 305.207 | 221.2185 | 220.1661 | 230.1083 | 216.8351 | 187.921
1087.3636 | 1020.3636 | 305.2823 | 221.2714 | 220.2145 | 230.2412 | 216.9251 | 187.9561
1088.355 | 1021.355 | 305.3198 | 221.3061 | 220.2948 | 230.3279 | 216.952 | 187.986
1089.3564 | 1022.3564 | 305.3485 | 221.3432 | 220.3599 | 230.4661 | 216.8821 | 188.011
1090.3579 | 1023.3579 | 305.4286 | 221.3733 | 220.4145 | 230.55 | 216.8331 | 188.0424
1091.3593 | 1024.3593 | 305.5204 | 221.3925 | 220.4899 | 230.7618 | 216.8698 | 188.0772
1092.3607 | 1025.3607 | 305.4557 | 221.4062 | 220.5461 | 230.5681 | 216.8532 | 188.1008
1093.3622 | 1026.3622 | 305.3688 | 221.4253 | 220.6089 | 230.4179 | 216.7196 | 188.1382
1094.3536 | 1027.3536 | 305.2845 | 221.435 | 220.665 | 230.6143 | 216.7409 | 188.1677
1095.355 | 1028.355 | 305.2622 | 221.4455 | 220.7202 | 230.6525 | 216.7472 | 188.1948
1096.3565 | 1029.3565 | 305.2931 | 221.4357 | 220.7759 | 230.7796 | 216.8269 | 188.2334
1097.3579 | 1030.3579 | 305.2601 | 221.4538 | 220.833 | 230.8727 | 216.9069 | 188.2638
1098.3594 | 1031.3594 | 305.3613 | 221.4632 | 220.8976 | 230.9265 | 216.9571 | 188.3029
1099.3608 | 1032.3608 | 305.3759 | 221.4835 | 220.9552 | 231.1059 | 217.0031 | 188.3427
1100.3622 | 1033.3622 | 305.3998 | 221.5009 | 221.0091 | 231.2409 | 217.063 | 188.3749
1101.3637 | 1034.3637 | 305.3804 | 221.4994 | 221.0715 | 231.3856 | 217.1292 | 188.4157
1102.3651 | 1035.3651 | 305.4172 | 221.4939 | 221.126 | 231.42 | 217.2218 | 188.4651
1103.3565 | 1036.3565 | 305.4981 | 221.4404 | 221.1863 | 231.5352 | 217.3299 | 188.5078
1104.358 | 1037.358 | 305.5277 | 221.3464 | 221.2613 | 231.4453 | 217.3814 | 188.5488
1105.3594 | 1038.3594 | 305.6026 | 221.279 | 221.3182 | 231.5926 | 217.468 | 188.6027
1106.3609 | 1039.3609 | 305.7901 | 221.2531 | 221.3916 | 231.6086 | 217.5185 | 188.6435
1107.3623 | 1040.3623 | 305.8676 | 221.2655 | 221.4358 | 231.5401 | 217.6328 | 188.6868
1108.3637 | 1041.3637 | 306.0087 | 221.2912 | 221.4927 | 231.596 | 217.7353 | 188.717
1109.3552 | 1042.3552 | 306.161 | 221.3273 | 221.5561 | 231.5682 | 217.771 | 188.7609
1110.3566 | 1043.3566 | 306.245 | 221.3558 | 221.608 | 231.7055 | 217.8263 | 188.7941
1111.3581 | 1044.3581 | 306.2731 | 221.3944 | 221.671 | 231.7676 | 217.8502 | 188.8246
1112.3595 | 1045.3595 | 306.3614 | 221.4277 | 221.7236 | 231.9039 | 217.9154 | 188.8608
1113.3609 | 1046.3609 | 306.2896 | 221.4714 | 221.7941 | 232.0171 | 218.0171 | 188.9033
1114.3624 | 1047.3624 | 306.3299 | 221.5243 | 221.8465 | 231.7787 | 218.0862 | 188.9331
1115.3538 | 1048.3538 | 306.4658 | 221.5893 | 221.9007 | 231.8503 | 218.1444 | 188.9685
1116.3552 | 1049.3552 | 306.558 | 221.6597 | 221.973 | 231.9396 | 218.2146 | 189.0007
1117.3567 | 1050.3567 | 306.596 | 221.7286 | 222.0243 | 231.9456 | 218.2242 | 189.038
1118.3581 | 1051.3581 | 306.5477 | 221.7847 | 222.0818 | 231.9306 | 218.2334 | 189.078
1119.3596 | 1052.3596 | 306.4822 | 221.8445 | 222.1405 | 231.9243 | 218.251 | 189.1089
1120.361 | 1053.361 | 306.4202 | 221.9047 | 222.2085 | 231.9479 | 218.2868 | 189.136
1121.3624 | 1054.3624 | 306.3509 | 221.9484 | 222.2646 | 231.8282 | 218.3515 | 189.1555
1122.3539 | 1055.3539 | 306.2181 | 222.002 | 222.3215 | 231.6854 | 218.4039 | 189.1827
1123.3553 | 1056.3553 | 306.1695 | 222.0641 | 222.3732 | 231.2648 | 218.4801 | 189.2105
1124.3567 | 1057.3567 | 306.1117 | 222.1298 | 222.4234 | 231.4024 | 218.5314 | 189.2349
1125.3582 | 1058.3582 | 306.1841 | 222.1844 | 222.4776 | 231.4356 | 218.5635 | 189.2534
1126.3596 | 1059.3596 | 306.1966 | 222.2319 | 222.5343 | 231.5058 | 218.6758 | 189.2856
1127.3611 | 1060.3611 | 306.1536 | 222.2896 | 222.581 | 231.6419 | 218.7405 | 189.3077
1128.3625 | 1061.3625 | 306.2 | 222.3251 | 222.6193 | 231.8628 | 218.815 | 189.3427
1129.3639 | 1062.3639 | 306.1757 | 222.3942 | 222.6654 | 231.8405 | 218.8597 | 189.3701
1130.3554 | 1063.3554 | 306.1497 | 222.5041 | 222.7023 | 231.99 | 218.8846 | 189.4029
1131.3568 | 1064.3568 | 306.016 | 222.6151 | 222.7502 | 232.0259 | 218.9002 | 189.4351
1132.3583 | 1065.3583 | 305.8712 | 222.7177 | 222.8028 | 232.0587 | 218.9631 | 189.4701
1133.3597 | 1066.3597 | 305.9099 | 222.8147 | 222.8557 | 232.0263 | 219.0281 | 189.51
1134.3611 | 1067.3611 | 306.0484 | 222.9094 | 222.9033 | 232.1411 | 219.0539 | 189.5436
1135.3626 | 1068.3626 | 305.969 | 223.005 | 222.9757 | 232.2182 | 219.1316 | 189.5806
1136.354 | 1069.354 | 305.8174 | 223.0846 | 223.0162 | 232.3104 | 219.2068 | 189.6164
1137.3554 | 1070.3554 | 305.6858 | 223.1608 | 223.0948 | 232.4293 | 219.2855 | 189.6518
1138.3569 | 1071.3569 | 305.6458 | 223.2438 | 223.1373 | 232.3826 | 219.3817 | 189.6736
1139.3583 | 1072.3583 | 305.6199 | 223.3203 | 223.2026 | 232.3806 | 219.4511 | 189.7048
1140.3598 | 1073.3598 | 305.4934 | 223.3868 | 223.263 | 232.1962 | 219.4944 | 189.7219
1141.3612 | 1074.3612 | 305.3299 | 223.4585 | 223.321 | 232.2793 | 219.5655 | 189.7363
1142.3626 | 1075.3626 | 305.213 | 223.5162 | 223.3846 | 232.4079 | 219.5023 | 189.7577
1143.3641 | 1076.3641 | 305.1568 | 223.5719 | 223.4301 | 232.545 | 219.366 | 189.7834
1144.3555 | 1077.3555 | 305.0995 | 223.6312 | 223.4977 | 232.5228 | 219.3488 | 189.8021
1145.3569 | 1078.3569 | 304.9836 | 223.6979 | 223.5443 | 232.3901 | 219.3581 | 189.8234
1146.3584 | 1079.3584 | 304.9736 | 223.7383 | 223.6084 | 232.4843 | 219.4116 | 189.8534
1147.3598 | 1080.3598 | 305.0099 | 223.781 | 223.6614 | 232.525 | 219.4274 | 189.8816
1148.3613 | 1081.3613 | 304.9022 | 223.8447 | 223.7263 | 232.2749 | 219.4456 | 189.9045
1149.3627 | 1082.3627 | 304.8627 | 223.9165 | 223.7954 | 232.5655 | 219.5621 | 189.9281
1150.3641 | 1083.3641 | 304.853 | 223.9861 | 223.848 | 232.7652 | 219.6531 | 189.9624
1151.3556 | 1084.3556 | 304.936 | 224.0539 | 223.9069 | 232.9141 | 219.7488 | 189.9911
1152.357 | 1085.357 | 304.92 | 224.0947 | 223.9737 | 232.7841 | 219.8075 | 190.0186
1153.3584 | 1086.3584 | 304.7619 | 224.1312 | 224.0432 | 232.9753 | 219.8929 | 190.0517
1154.3599 | 1087.3599 | 304.5161 | 224.1756 | 224.104 | 233.0853 | 219.9151 | 190.0819
1155.3613 | 1088.3613 | 304.3519 | 224.2306 | 224.1602 | 233.1465 | 219.9398 | 190.1046
1156.3628 | 1089.3628 | 304.1949 | 224.2874 | 224.2227 | 233.0574 | 219.9307 | 190.1361
1157.3542 | 1090.3542 | 304.0065 | 224.3262 | 224.2769 | 233.1229 | 219.9273 | 190.1639
1158.3556 | 1091.3556 | 303.7683 | 224.3282 | 224.355 | 233.042 | 219.9879 | 190.1881
1159.3571 | 1092.3571 | 303.6143 | 224.3172 | 224.4096 | 233.0663 | 220.0272 | 190.2126
1160.3585 | 1093.3585 | 303.4341 | 224.3502 | 224.468 | 232.9123 | 220.0493 | 190.237
1161.36 | 1094.36 | 303.2147 | 224.4247 | 224.524 | 232.9556 | 220.0624 | 190.2579
1162.3614 | 1095.3614 | 302.9584 | 224.4927 | 224.5885 | 233.1052 | 220.0454 | 190.2808
1163.3628 | 1096.3628 | 302.6097 | 224.5674 | 224.639 | 233.2602 | 220.0924 | 190.3081
1164.3543 | 1097.3543 | 302.3084 | 224.6078 | 224.7034 | 233.3404 | 220.1301 | 190.3168
1165.3557 | 1098.3557 | 302.0641 | 224.6506 | 224.7545 | 233.1722 | 220.2119 | 190.3313
1166.3571 | 1099.3571 | 301.7023 | 224.7192 | 224.8184 | 233.2148 | 220.2243 | 190.3491
1167.3586 | 1100.3586 | 301.3411 | 224.7774 | 224.8695 | 233.1876 | 220.2636 | 190.3533
1168.36 | 1101.36 | 301.0055 | 224.8321 | 224.9176 | 233.0394 | 220.3094 | 190.3683
1169.3615 | 1102.3615 | 300.6465 | 224.8768 | 224.9801 | 233.0736 | 220.2574 | 190.3738
1170.3629 | 1103.3629 | 300.2284 | 224.927 | 225.0227 | 232.9258 | 220.2808 | 190.3787
1171.3643 | 1104.3643 | 299.7595 | 224.9646 | 225.0757 | 232.91 | 220.2656 | 190.3839
1172.3558 | 1105.3558 | 299.3171 | 225.0186 | 225.1236 | 232.7021 | 220.2476 | 190.3923
1173.3572 | 1106.3572 | 298.9699 | 225.0619 | 225.1647 | 232.7842 | 220.2242 | 190.3945
1174.3586 | 1107.3586 | 298.6429 | 225.1077 | 225.2044 | 232.665 | 220.1752 | 190.3886
1175.3601 | 1108.3601 | 298.2637 | 225.1451 | 225.2485 | 232.3772 | 220.1275 | 190.3846
1176.3615 | 1109.3615 | 297.7674 | 225.1652 | 225.2927 | 232.2847 | 220.1642 | 190.3821
1177.363 | 1110.363 | 297.3581 | 225.181 | 225.3218 | 232.1363 | 220.1696 | 190.3714
1178.3544 | 1111.3544 | 297.0407 | 225.1929 | 225.3678 | 231.958 | 220.1317 | 190.365
1179.3558 | 1112.3558 | 296.7308 | 225.2125 | 225.3988 | 231.1758 | 220.0754 | 190.3604
1180.3573 | 1113.3573 | 296.408 | 225.2277 | 225.4227 | 230.8308 | 219.9705 | 190.3432
1181.3587 | 1114.3587 | 296.0582 | 225.2709 | 225.4549 | 230.9556 | 219.9263 | 190.3331
1182.3602 | 1115.3602 | 295.6572 | 225.3059 | 225.468 | 230.7531 | 219.8536 | 190.3213
1183.3616 | 1116.3616 | 295.3351 | 225.3416 | 225.4836 | 230.5955 | 219.6208 | 190.3062
1184.363 | 1117.363 | 295.0485 | 225.3552 | 225.4979 | 230.6223 | 219.5261 | 190.3037
1185.3645 | 1118.3645 | 294.6704 | 225.3771 | 225.4949 | 230.6806 | 219.5277 | 190.3083
1186.3559 | 1119.3559 | 294.3907 | 225.3839 | 225.4899 | 230.7463 | 219.3259 | 190.3061
1187.3573 | 1120.3573 | 294.0018 | 225.3894 | 225.5011 | 230.5172 | 219.1676 | 190.3238
1188.3588 | 1121.3588 | 293.5952 | 225.3912 | 225.51 | 230.1564 | 219.061 | 190.3357
1189.3602 | 1122.3602 | 293.0923 | 225.3903 | 225.5101 | 229.6683 | 218.9704 | 190.3517
1190.3617 | 1123.3617 | 292.5765 | 225.3902 | 225.509 | 229.6814 | 218.6365 | 190.3712
1191.3631 | 1124.3631 | 292.1056 | 225.3865 | 225.511 | 229.4274 | 218.5877 | 190.3916
1192.3645 | 1125.3645 | 291.7556 | 225.3943 | 225.5038 | 229.3211 | 218.5176 | 190.4056
1193.356 | 1126.356 | 291.3851 | 225.3903 | 225.507 | 229.2022 | 218.4177 | 190.4217
1194.3574 | 1127.3574 | 290.8985 | 225.3981 | 225.4854 | 229.3385 | 218.2444 | 190.4331
1195.3588 | 1128.3588 | 290.4165 | 225.3956 | 225.4815 | 229.212 | 218.2452 | 190.438
1196.3603 | 1129.3603 | 290.0134 | 225.3938 | 225.4648 | 229.1664 | 218.1727 | 190.4541
1197.3617 | 1130.3617 | 289.5766 | 225.4073 | 225.4472 | 229.0171 | 218.0646 | 190.4581
1198.3632 | 1131.3632 | 289.1179 | 225.4133 | 225.4468 | 229.0822 | 217.8569 | 190.452
1199.3546 | 1132.3546 | 288.6387 | 225.416 | 225.419 | 229.1212 | 217.7877 | 190.4402
1200.356 | 1133.356 | 288.2066 | 225.4217 | 225.4055 | 229.0067 | 217.7808 | 190.423
1201.3575 | 1134.3575 | 287.7624 | 225.4185 | 225.393 | 228.927 | 217.6819 | 190.4214
1202.3589 | 1135.3589 | 287.3921 | 225.4153 | 225.3967 | 228.7868 | 217.6338 | 190.4051
1203.3603 | 1136.3603 | 287.0127 | 225.4146 | 225.3742 | 228.2486 | 217.5127 | 190.395
1204.3618 | 1137.3618 | 286.643 | 225.4129 | 225.3644 | 227.8602 | 217.411 | 190.3924
1205.3632 | 1138.3632 | 286.2405 | 225.404 | 225.3453 | 227.5577 | 217.37 | 190.3774
1206.3547 | 1139.3547 | 285.8519 | 225.3829 | 225.3344 | 227.6034 | 217.2028 | 190.355
1207.3561 | 1140.3561 | 285.4344 | 225.3511 | 225.3182 | 227.5621 | 217.1413 | 190.3475
1208.3575 | 1141.3575 | 285.0703 | 225.314 | 225.2982 | 227.6785 | 217.0487 | 190.3321
1209.359 | 1142.359 | 284.7036 | 225.2498 | 225.2778 | 227.7485 | 216.9475 | 190.3185
1210.3604 | 1143.3604 | 284.2537 | 225.1993 | 225.2565 | 227.4081 | 216.9473 | 190.2963
1211.3619 | 1144.3619 | 283.7642 | 225.1874 | 225.2413 | 227.4239 | 216.9415 | 190.2755
1212.3633 | 1145.3633 | 283.4149 | 225.185 | 225.2137 | 227.4229 | 216.8629 | 190.2439
1213.3647 | 1146.3647 | 282.9404 | 225.1815 | 225.1929 | 227.3176 | 216.7753 | 190.2184
1214.3562 | 1147.3562 | 282.4378 | 225.1812 | 225.1772 | 227.0422 | 216.7099 | 190.1816
1215.3576 | 1148.3576 | 282.0719 | 225.1743 | 225.1674 | 226.8619 | 216.6165 | 190.1505
1216.359 | 1149.359 | 281.7001 | 225.1725 | 225.1564 | 226.901 | 216.5249 | 190.1088
1217.3605 | 1150.3605 | 281.3674 | 225.1619 | 225.1339 | 226.8175 | 216.4729 | 190.0793
1218.3619 | 1151.3619 | 281.0846 | 225.1653 | 225.1096 | 226.9116 | 216.4072 | 190.0426
1219.3634 | 1152.3634 | 280.8022 | 225.1587 | 225.099 | 226.7253 | 216.3184 | 190.01
1220.3548 | 1153.3548 | 280.5275 | 225.1515 | 225.0911 | 226.7212 | 216.276 | 189.9782
1221.3562 | 1154.3562 | 280.1956 | 225.1525 | 225.0693 | 226.27 | 216.2098 | 189.9359
1222.3577 | 1155.3577 | 279.6846 | 225.1456 | 225.0553 | 226.2053 | 216.1083 | 189.8841
1223.3591 | 1156.3591 | 279.1317 | 225.1391 | 225.0356 | 225.8521 | 216.0598 | 189.8315
1224.3605 | 1157.3605 | 278.598 | 225.131 | 225.0146 | 225.7212 | 215.829 | 189.7808
1225.362 | 1158.362 | 278.1692 | 225.1278 | 224.988 | 225.8067 | 215.7004 | 189.7225
1226.3634 | 1159.3634 | 277.8118 | 225.1106 | 224.9663 | 224.964 | 215.6005 | 189.6551
1227.3649 | 1160.3649 | 277.4496 | 225.1033 | 224.9327 | 224.9086 | 215.5285 | 189.6038
1228.3563 | 1161.3563 | 277.1664 | 225.0892 | 224.9099 | 225.0602 | 215.4217 | 189.5419
1229.3577 | 1162.3577 | 276.9144 | 225.0723 | 224.8841 | 224.7451 | 215.163 | 189.4818
1230.3592 | 1163.3592 | 276.5876 | 225.049 | 224.8639 | 224.4454 | 215.0144 | 189.4254
1231.3606 | 1164.3606 | 276.162 | 225.043 | 224.842 | 224.3736 | 214.9573 | 189.3714
1232.362 | 1165.362 | 275.7277 | 225.0211 | 224.7962 | 224.2727 | 214.7899 | 189.3057
1233.3635 | 1166.3635 | 275.2656 | 225.0067 | 224.7718 | 224.2628 | 214.5095 | 189.2388
1234.3549 | 1167.3549 | 274.8718 | 224.9829 | 224.7304 | 223.9813 | 214.3703 | 189.1697
1235.3564 | 1168.3564 | 274.5039 | 224.962 | 224.6888 | 223.8225 | 214.2531 | 189.1082
1236.3578 | 1169.3578 | 274.0771 | 224.9388 | 224.6671 | 223.5742 | 214.0311 | 189.0387
1237.3592 | 1170.3592 | 273.6445 | 224.9149 | 224.6309 | 223.3843 | 213.9733 | 188.9666
1238.3607 | 1171.3607 | 273.2684 | 224.8906 | 224.5926 | 223.3743 | 213.7712 | 188.9066
1239.3621 | 1172.3621 | 272.8918 | 224.8575 | 224.5662 | 223.1309 | 213.6132 | 188.8566
1240.3636 | 1173.3636 | 272.4827 | 224.8268 | 224.5248 | 222.946 | 213.4861 | 188.7979
1241.355 | 1174.355 | 272.1084 | 224.805 | 224.4976 | 222.7954 | 213.3111 | 188.7428
1242.3564 | 1175.3564 | 271.7619 | 224.77 | 224.4533 | 222.573 | 213.1121 | 188.6889
1243.3579 | 1176.3579 | 271.3994 | 224.7373 | 224.4166 | 222.2185 | 212.8682 | 188.6417
1244.3593 | 1177.3593 | 271.0439 | 224.7028 | 224.3858 | 222.0954 | 212.7236 | 188.5844
1245.3607 | 1178.3607 | 270.6562 | 224.6552 | 224.3275 | 221.8604 | 212.557 | 188.5348
1246.3622 | 1179.3622 | 270.2232 | 224.6228 | 224.2906 | 221.771 | 212.4952 | 188.4847
1247.3636 | 1180.3636 | 269.7976 | 224.5815 | 224.24 | 221.5958 | 212.453 | 188.4286
1248.3651 | 1181.3651 | 269.3954 | 224.5331 | 224.2002 | 221.5398 | 212.3829 | 188.361
1249.3565 | 1182.3565 | 268.9468 | 224.4907 | 224.1423 | 221.4136 | 212.2428 | 188.2972
1250.3579 | 1183.3579 | 268.5239 | 224.4391 | 224.0931 | 221.0611 | 211.9967 | 188.2305
1251.3594 | 1184.3594 | 268.0649 | 224.3945 | 224.0605 | 220.7335 | 211.8605 | 188.1619
1252.3608 | 1185.3608 | 267.6819 | 224.3374 | 224.0145 | 220.0821 | 211.6831 | 188.0888
1253.3622 | 1186.3622 | 267.3199 | 224.2882 | 223.9672 | 219.6723 | 211.5773 | 188.0145
1254.3537 | 1187.3537 | 266.9684 | 224.2398 | 223.9146 | 219.0692 | 211.398 | 187.9512
1255.3551 | 1188.3551 | 266.5545 | 224.1905 | 223.8598 | 219.186 | 211.1986 | 187.8808
1256.3566 | 1189.3566 | 266.1174 | 224.1384 | 223.7929 | 219.0255 | 211.0121 | 187.8141
1257.358 | 1190.358 | 265.719 | 224.0837 | 223.7349 | 218.7221 | 210.8718 | 187.7452
1258.3594 | 1191.3594 | 265.3394 | 224.0281 | 223.662 | 217.7259 | 210.7182 | 187.6916
1259.3609 | 1192.3609 | 264.9063 | 223.9773 | 223.5948 | 217.7061 | 210.537 | 187.6287
1260.3623 | 1193.3623 | 264.5322 | 223.9232 | 223.5264 | 216.9397 | 210.3978 | 187.5766
1261.3638 | 1194.3638 | 264.1442 | 223.8702 | 223.4509 | 216.9429 | 210.2534 | 187.5127
1262.3552 | 1195.3552 | 263.7687 | 223.8145 | 223.3686 | 216.9471 | 210.0916 | 187.4599
1263.3566 | 1196.3566 | 263.41 | 223.7533 | 223.2925 | 216.6359 | 209.9704 | 187.3959
1264.3581 | 1197.3581 | 263.0877 | 223.699 | 223.2 | 216.0154 | 209.8557 | 187.3301
1265.3595 | 1198.3595 | 262.7515 | 223.6432 | 223.133 | 216.1365 | 209.6826 | 187.2662
1266.3609 | 1199.3609 | 262.3164 | 223.5799 | 223.0602 | 216.151 | 209.5343 | 187.2036
1267.3624 | 1200.3624 | 261.8407 | 223.5298 | 222.9847 | 216.1663 | 209.3208 | 187.1246
1268.3638 | 1201.3638 | 261.4181 | 223.4658 | 222.9201 | 215.9158 | 209.1008 | 187.0488
1269.3552 | 1202.3552 | 261.0604 | 223.4141 | 222.8317 | 215.8305 | 208.8987 | 186.9744
1270.3567 | 1203.3567 | 260.6269 | 223.3541 | 222.7698 | 215.7513 | 208.7906 | 186.8815
1271.3581 | 1204.3581 | 260.2704 | 223.2935 | 222.6866 | 215.6573 | 208.6098 | 186.7949
1272.3596 | 1205.3596 | 259.9676 | 223.2313 | 222.6282 | 215.4556 | 208.4933 | 186.7086
1273.361 | 1206.361 | 259.627 | 223.1731 | 222.5443 | 215.431 | 208.308 | 186.6204
1274.3624 | 1207.3624 | 259.2346 | 223.1114 | 222.4837 | 215.2655 | 208.1796 | 186.5201
1275.3639 | 1208.3639 | 258.8213 | 223.0547 | 222.4125 | 215.2571 | 208.011 | 186.4298
1276.3653 | 1209.3653 | 258.4126 | 222.9964 | 222.3542 | 215.0539 | 207.8653 | 186.3403
1277.3567 | 1210.3567 | 258.0122 | 222.9238 | 222.2878 | 214.8687 | 207.6174 | 186.2508
1278.3582 | 1211.3582 | 257.5713 | 222.8527 | 222.2148 | 214.544 | 207.3591 | 186.1613
1279.3596 | 1212.3596 | 257.1624 | 222.7815 | 222.1601 | 214.3492 | 207.1507 | 186.0767
1280.3611 | 1213.3611 | 256.7876 | 222.7074 | 222.0884 | 214.0975 | 207.0282 | 185.9942
1281.3625 | 1214.3625 | 256.4101 | 222.6322 | 222.0131 | 213.7664 | 206.9143 | 185.9056
1282.3639 | 1215.3639 | 256.0649 | 222.5707 | 221.9461 | 213.719 | 206.767 | 185.8332
1283.3554 | 1216.3554 | 255.7797 | 222.4957 | 221.8804 | 213.5071 | 206.5484 | 185.7522
1284.3568 | 1217.3568 | 255.4558 | 222.4195 | 221.7984 | 213.2698 | 206.4077 | 185.669
1285.3583 | 1218.3583 | 255.0976 | 222.3567 | 221.7192 | 212.9412 | 206.2413 | 185.5895
1286.3597 | 1219.3597 | 254.6744 | 222.2809 | 221.6417 | 212.5063 | 206.0268 | 185.5188
1287.3611 | 1220.3611 | 254.2999 | 222.2057 | 221.5508 | 212.1137 | 205.7545 | 185.4383
1288.3626 | 1221.3626 | 253.9514 | 222.1361 | 221.4663 | 211.6235 | 205.5503 | 185.3714
1289.364 | 1222.364 | 253.6255 | 222.0608 | 221.3721 | 211.467 | 205.4332 | 185.2919
1290.3554 | 1223.3554 | 253.2587 | 221.9881 | 221.2825 | 211.3536 | 205.3077 | 185.2139
1291.3569 | 1224.3569 | 252.9285 | 221.9099 | 221.191 | 211.301 | 205.1667 | 185.1333
1292.3583 | 1225.3583 | 252.5218 | 221.8367 | 221.0997 | 211.0455 | 205.082 | 185.0494
1293.3598 | 1226.3598 | 252.2244 | 221.7579 | 221.0038 | 211.0762 | 204.9604 | 184.9591
1294.3612 | 1227.3612 | 251.9778 | 221.6755 | 220.9059 | 210.4871 | 204.836 | 184.8771
1295.3626 | 1228.3626 | 251.6613 | 221.5993 | 220.8162 | 210.1631 | 204.6151 | 184.788
1296.3541 | 1229.3541 | 251.3269 | 221.5264 | 220.7186 | 210.1343 | 204.3525 | 184.6992
1297.3555 | 1230.3555 | 250.9117 | 221.4485 | 220.6155 | 209.9416 | 204.1384 | 184.6045
1298.3569 | 1231.3569 | 250.475 | 221.369 | 220.5186 | 209.6149 | 204.0464 | 184.5168
1299.3584 | 1232.3584 | 250.1014 | 221.2864 | 220.434 | 209.5342 | 203.7511 | 184.4292
1300.3598 | 1233.3598 | 249.7968 | 221.2036 | 220.3223 | 209.5689 | 203.6227 | 184.3397
1301.3613 | 1234.3613 | 249.4674 | 221.1172 | 220.2281 | 209.4729 | 203.5697 | 184.2543
1302.3627 | 1235.3627 | 249.1488 | 221.0359 | 220.1343 | 209.4313 | 203.336 | 184.1654
1303.3641 | 1236.3641 | 248.7596 | 220.9548 | 220.055 | 209.2573 | 203.2483 | 184.0752
1304.3556 | 1237.3556 | 248.3884 | 220.8706 | 219.9665 | 208.7845 | 202.9881 | 183.9833
1305.357 | 1238.357 | 248.0331 | 220.7894 | 219.8755 | 208.713 | 202.9304 | 183.8902
1306.3585 | 1239.3585 | 247.6199 | 220.7128 | 219.778 | 208.4256 | 202.7245 | 183.7999
1307.3599 | 1240.3599 | 247.2265 | 220.6306 | 219.6841 | 208.2228 | 202.5511 | 183.7129
1308.3613 | 1241.3613 | 246.8875 | 220.5514 | 219.6094 | 207.9696 | 202.3886 | 183.6116
1309.3628 | 1242.3628 | 246.5009 | 220.4726 | 219.5165 | 207.6552 | 202.2172 | 183.5213
1310.3642 | 1243.3642 | 246.1461 | 220.3793 | 219.4248 | 207.6093 | 202.0896 | 183.4248
1311.3556 | 1244.3556 | 245.7548 | 220.2989 | 219.3398 | 207.2767 | 201.8694 | 183.331
1312.3571 | 1245.3571 | 245.3168 | 220.207 | 219.2507 | 207.3254 | 201.6367 | 183.2445
1313.3585 | 1246.3585 | 244.9272 | 220.1115 | 219.1524 | 207.0648 | 201.4209 | 183.1492
1314.36 | 1247.36 | 244.5606 | 220.0211 | 219.0742 | 206.9747 | 201.1692 | 183.0678
1315.3614 | 1248.3614 | 244.1864 | 219.9224 | 218.9778 | 206.7329 | 201.0156 | 182.9783
1316.3628 | 1249.3628 | 243.8227 | 219.8236 | 218.8825 | 206.276 | 200.8658 | 182.8896
1317.3643 | 1250.3643 | 243.4738 | 219.7264 | 218.8028 | 205.9025 | 200.7362 | 182.7935
1318.3657 | 1251.3657 | 243.138 | 219.6349 | 218.698 | 205.7871 | 200.431 | 182.7004
1319.3571 | 1252.3571 | 242.8622 | 219.5309 | 218.6054 | 205.6894 | 200.2359 | 182.5989
1320.3586 | 1253.3586 | 242.6371 | 219.4266 | 218.5036 | 205.3931 | 200.0641 | 182.503
1321.36 | 1254.36 | 242.2998 | 219.3311 | 218.4106 | 205.1446 | 199.9254 | 182.4091
1322.3615 | 1255.3615 | 241.9449 | 219.2233 | 218.309 | 204.4965 | 199.7855 | 182.3186
1323.3629 | 1256.3629 | 241.5821 | 219.117 | 218.217 | 204.3549 | 199.6221 | 182.2305
1324.3643 | 1257.3643 | 241.2501 | 219.0168 | 218.1166 | 203.8039 | 199.4808 | 182.1427
1325.3558 | 1258.3558 | 240.927 | 218.9051 | 218.0034 | 203.4837 | 199.3933 | 182.06
1326.3572 | 1259.3572 | 240.6243 | 218.802 | 217.9132 | 203.2635 | 199.0732 | 181.9787
1327.3586 | 1260.3586 | 240.3566 | 218.6961 | 217.8168 | 203.0702 | 198.9022 | 181.8899
1328.3601 | 1261.3601 | 240.1596 | 218.5838 | 217.6982 | 202.8356 | 198.6914 | 181.8106
1329.3615 | 1262.3615 | 239.914 | 218.4766 | 217.5941 | 202.6741 | 198.5701 | 181.7251
1330.363 | 1263.363 | 239.579 | 218.3706 | 217.4952 | 202.5891 | 198.4321 | 181.6402
1331.3544 | 1264.3544 | 239.247 | 218.257 | 217.3915 | 202.358 | 198.3226 | 181.5552
1332.3558 | 1265.3558 | 238.9136 | 218.1491 | 217.269 | 202.2155 | 198.207 | 181.477
1333.3573 | 1266.3573 | 238.4864 | 218.0351 | 217.1369 | 202.0202 | 198.1135 | 181.3888
1334.3587 | 1267.3587 | 238.1626 | 217.9267 | 217.0331 | 201.9428 | 197.9872 | 181.3075
1335.3602 | 1268.3602 | 237.9049 | 217.8168 | 216.9256 | 201.2367 | 197.78 | 181.2098
1336.3616 | 1269.3616 | 237.6106 | 217.7184 | 216.8065 | 200.7274 | 197.5304 | 181.119
1337.363 | 1270.363 | 237.2736 | 217.6037 | 216.6839 | 200.877 | 197.3427 | 181.0221
1338.3545 | 1271.3545 | 236.983 | 217.496 | 216.5766 | 201.0211 | 197.1895 | 180.9322
1339.3559 | 1272.3559 | 236.6269 | 217.3845 | 216.4486 | 200.7951 | 196.9608 | 180.8421
1340.3573 | 1273.3573 | 236.2887 | 217.2709 | 216.3407 | 200.6828 | 196.7988 | 180.7452
1341.3588 | 1274.3588 | 235.9022 | 217.1636 | 216.2069 | 200.4896 | 196.6795 | 180.6521
1342.3602 | 1275.3602 | 235.5023 | 217.0475 | 216.0929 | 200.5751 | 196.594 | 180.5457
1343.3617 | 1276.3617 | 235.1742 | 216.9323 | 215.9707 | 200.2953 | 196.3208 | 180.4416
1344.3631 | 1277.3631 | 234.8661 | 216.8286 | 215.8568 | 200.2344 | 196.0745 | 180.3296
1345.3645 | 1278.3645 | 234.5785 | 216.7055 | 215.7469 | 200.203 | 195.724 | 180.2259
1346.356 | 1279.356 | 234.3592 | 216.593 | 215.6276 | 200.0342 | 195.5831 | 180.1202
1347.3574 | 1280.3574 | 234.0883 | 216.4814 | 215.5248 | 199.8865 | 195.3801 | 180.0194
1348.3588 | 1281.3588 | 233.7486 | 216.3733 | 215.4281 | 199.6131 | 195.1594 | 179.9067
1349.3603 | 1282.3603 | 233.421 | 216.2559 | 215.3212 | 199.391 | 194.9761 | 179.8047
1350.3617 | 1283.3617 | 233.047 | 216.1346 | 215.2016 | 199.2795 | 194.7625 | 179.6991
1351.3532 | 1284.3532 | 232.6734 | 216.0227 | 215.1074 | 199.1191 | 194.5558 | 179.5886
1352.3646 | 1285.3646 | 232.3776 | 215.9119 | 214.9906 | 198.9246 | 194.4166 | 179.4876
1353.356 | 1286.356 | 231.9861 | 215.7935 | 214.8993 | 198.7018 | 194.3204 | 179.3804
1354.3575 | 1287.3575 | 231.6202 | 215.6852 | 214.7914 | 198.5752 | 194.0924 | 179.2871
1355.3589 | 1288.3589 | 231.2905 | 215.5712 | 214.6788 | 198.2084 | 193.9693 | 179.1776
1356.3604 | 1289.3604 | 230.9739 | 215.445 | 214.572 | 197.7171 | 193.8273 | 179.0838
1357.3618 | 1290.3618 | 230.6727 | 215.3253 | 214.4612 | 197.5817 | 193.5928 | 178.9793
1358.3632 | 1291.3632 | 230.4059 | 215.2121 | 214.3586 | 197.4753 | 193.313 | 178.8759
1359.3647 | 1292.3647 | 230.0671 | 215.0902 | 214.2509 | 197.0946 | 193.2252 | 178.7728
1360.3561 | 1293.3561 | 229.7574 | 214.9715 | 214.1408 | 196.9922 | 193.0865 | 178.6687
1361.3575 | 1294.3575 | 229.4185 | 214.8419 | 214.0337 | 196.7625 | 192.9523 | 178.5555
1362.359 | 1295.359 | 229.0954 | 214.7181 | 213.9122 | 196.3627 | 192.7405 | 178.45
1363.3604 | 1296.3604 | 228.8222 | 214.6012 | 213.8012 | 196.1508 | 192.547 | 178.3482
1364.3619 | 1297.3619 | 228.4535 | 214.4745 | 213.6725 | 195.9763 | 192.4414 | 178.2453
1365.3633 | 1298.3633 | 228.0835 | 214.3588 | 213.5613 | 195.9631 | 192.2291 | 178.1265
1366.3647 | 1299.3647 | 227.7836 | 214.2382 | 213.4613 | 195.7601 | 191.9231 | 178.0207
1367.3562 | 1300.3562 | 227.4375 | 214.1114 | 213.3418 | 195.5531 | 191.8116 | 177.8984
1368.3576 | 1301.3576 | 227.1139 | 213.9888 | 213.2258 | 195.3673 | 191.6393 | 177.7888
1369.359 | 1302.359 | 226.813 | 213.8645 | 213.1179 | 195.153 | 191.464 | 177.6771
1370.3605 | 1303.3605 | 226.5425 | 213.74 | 213.0056 | 194.9922 | 191.3482 | 177.5604
1371.3619 | 1304.3619 | 226.3215 | 213.6236 | 212.8813 | 194.8789 | 191.1813 | 177.457
1372.3634 | 1305.3634 | 226.0975 | 213.5013 | 212.7696 | 194.6647 | 190.9599 | 177.3412
1373.3648 | 1306.3648 | 225.8696 | 213.387 | 212.6558 | 194.5362 | 190.7211 | 177.2391
1374.3562 | 1307.3562 | 225.5619 | 213.2563 | 212.5402 | 194.441 | 190.5914 | 177.1399
1375.3577 | 1308.3577 | 225.2379 | 213.1292 | 212.4263 | 194.0917 | 190.4728 | 177.0285
1376.3591 | 1309.3591 | 224.9685 | 213.0106 | 212.3075 | 193.9125 | 190.327 | 176.932
1377.3605 | 1310.3605 | 224.6775 | 212.8818 | 212.2038 | 193.8522 | 190.2548 | 176.8426
1378.362 | 1311.362 | 224.3532 | 212.7535 | 212.0802 | 193.6053 | 190.0475 | 176.7392
1379.3634 | 1312.3634 | 224.0026 | 212.6255 | 211.9679 | 193.1856 | 189.8799 | 176.6465
1380.3549 | 1313.3549 | 223.6511 | 212.502 | 211.8467 | 192.5535 | 189.5371 | 176.5525
1381.3563 | 1314.3563 | 223.3326 | 212.3748 | 211.7385 | 192.3896 | 189.4114 | 176.4499
1382.3577 | 1315.3577 | 222.9896 | 212.2502 | 211.6191 | 192.3218 | 189.2594 | 176.3586
1383.3592 | 1316.3592 | 222.7024 | 212.1132 | 211.4991 | 192.0623 | 189.1643 | 176.2533
1384.3606 | 1317.3606 | 222.4987 | 211.9842 | 211.3684 | 191.8457 | 188.9714 | 176.1516
1385.3621 | 1318.3621 | 222.2675 | 211.8578 | 211.2541 | 191.6365 | 188.7293 | 176.0458
1386.3635 | 1319.3635 | 221.9852 | 211.7333 | 211.1298 | 191.4323 | 188.5 | 175.9424
1387.3549 | 1320.3549 | 221.6772 | 211.5981 | 211.0078 | 191.2362 | 188.4634 | 175.8421
1388.3564 | 1321.3564 | 221.3456 | 211.4747 | 210.8881 | 190.8791 | 188.2844 | 175.7362
1389.3578 | 1322.3578 | 220.9949 | 211.3369 | 210.7606 | 190.4093 | 188.019 | 175.6226
1390.3592 | 1323.3592 | 220.6941 | 211.2185 | 210.6316 | 190.0242 | 187.8605 | 175.5198
1391.3607 | 1324.3607 | 220.4374 | 211.0775 | 210.5105 | 190.027 | 187.7513 | 175.4121
1392.3621 | 1325.3621 | 220.1549 | 210.9428 | 210.376 | 189.8163 | 187.5703 | 175.3011
1393.3636 | 1326.3636 | 219.8347 | 210.81 | 210.2479 | 189.414 | 187.4386 | 175.199
1394.355 | 1327.355 | 219.5493 | 210.6738 | 210.1 | 189.3833 | 187.385 | 175.0815
1395.3564 | 1328.3564 | 219.2545 | 210.5333 | 209.9639 | 189.1509 | 187.2456 | 174.9788
1396.3579 | 1329.3579 | 218.9621 | 210.4071 | 209.8403 | 188.8548 | 187.0703 | 174.8701
1397.3593 | 1330.3593 | 218.6761 | 210.2765 | 209.7068 | 188.67 | 186.9606 | 174.7633
1398.3607 | 1331.3607 | 218.4038 | 210.1497 | 209.5711 | 187.7501 | 186.7295 | 174.6658
1399.3622 | 1332.3622 | 218.1394 | 210.0093 | 209.4373 | 187.7881 | 186.5279 | 174.564
1400.3636 | 1333.3636 | 217.8256 | 209.8781 | 209.2953 | 187.1429 | 186.4401 | 174.4607
1401.3651 | 1334.3651 | 217.5935 | 209.746 | 209.1651 | 187.1278 | 186.3134 | 174.3515
1402.3565 | 1335.3565 | 217.2887 | 209.6117 | 209.0338 | 186.8159 | 186.1333 | 174.2498
1403.3579 | 1336.3579 | 216.9633 | 209.4732 | 208.885 | 186.5942 | 185.9856 | 174.1578
1404.3594 | 1337.3594 | 216.6616 | 209.3368 | 208.7541 | 186.0837 | 185.7591 | 174.0502
1405.3608 | 1338.3608 | 216.3436 | 209.205 | 208.6062 | 186.141 | 185.4478 | 173.9455
1406.3622 | 1339.3622 | 216.0125 | 209.0606 | 208.4686 | 186.1234 | 185.3326 | 173.8516
1407.3637 | 1340.3637 | 215.7064 | 208.9304 | 208.3172 | 186.0584 | 185.2684 | 173.7536
1408.3651 | 1341.3651 | 215.4194 | 208.7901 | 208.1912 | 185.9058 | 185.1462 | 173.6631
1409.3566 | 1342.3566 | 215.1599 | 208.6439 | 208.0443 | 185.6187 | 184.9694 | 173.5674
1410.358 | 1343.358 | 214.8793 | 208.5025 | 207.9003 | 185.6407 | 184.7868 | 173.4798
1411.3594 | 1344.3594 | 214.589 | 208.3675 | 207.7476 | 185.5013 | 184.7018 | 173.3952
1412.3609 | 1345.3609 | 214.3015 | 208.2203 | 207.6089 | 185.4722 | 184.6036 | 173.3192
1413.3623 | 1346.3623 | 214.0848 | 208.0781 | 207.4769 | 185.416 | 184.4243 | 173.2323
1414.3638 | 1347.3638 | 213.874 | 207.9465 | 207.33 | 185.308 | 184.3473 | 173.1318
1415.3552 | 1348.3552 | 213.5804 | 207.819 | 207.1898 | 185.1653 | 184.2681 | 173.037
1416.3566 | 1349.3566 | 213.2946 | 207.6825 | 207.0458 | 184.9415 | 184.0988 | 172.9453
1417.3581 | 1350.3581 | 213.0193 | 207.542 | 206.906 | 184.7662 | 184.0155 | 172.8375
1418.3595 | 1351.3595 | 212.7188 | 207.4113 | 206.7691 | 184.5793 | 183.8649 | 172.7407
1419.3609 | 1352.3609 | 212.3992 | 207.2719 | 206.632 | 184.0554 | 183.666 | 172.6299
1420.3624 | 1353.3624 | 212.0473 | 207.1331 | 206.4815 | 183.4497 | 183.3049 | 172.5293
1421.3538 | 1354.3538 | 211.7113 | 206.9941 | 206.3493 | 182.9441 | 183.0707 | 172.4256
1422.3552 | 1355.3552 | 211.4445 | 206.853 | 206.2056 | 182.9598 | 182.8158 | 172.3202
1423.3567 | 1356.3567 | 211.1209 | 206.7089 | 206.0545 | 182.578 | 182.6532 | 172.2195
1424.3581 | 1357.3581 | 210.8846 | 206.5697 | 205.9124 | 182.7149 | 182.4404 | 172.1212
1425.3596 | 1358.3596 | 210.6397 | 206.421 | 205.7588 | 182.6768 | 182.2315 | 172.0125
1426.361 | 1359.361 | 210.3811 | 206.2699 | 205.614 | 182.5169 | 182.0225 | 171.9072
1427.3624 | 1360.3624 | 210.0951 | 206.1271 | 205.4612 | 182.3275 | 181.7799 | 171.7929
1428.3539 | 1361.3539 | 209.8314 | 205.9806 | 205.3194 | 182.3667 | 181.5725 | 171.6814
1429.3553 | 1362.3553 | 209.6069 | 205.8273 | 205.1727 | 181.8802 | 181.5219 | 171.5851
1430.3568 | 1363.3568 | 209.438 | 205.6859 | 205.0391 | 181.3575 | 181.3533 | 171.4865
1431.3582 | 1364.3582 | 209.2292 | 205.5404 | 204.8859 | 181.3613 | 181.1849 | 171.3902
1432.3596 | 1365.3596 | 208.9258 | 205.394 | 204.7537 | 181.3442 | 181.0181 | 171.2901
1433.3611 | 1366.3611 | 208.6684 | 205.2566 | 204.6172 | 181.0864 | 180.7213 | 171.1922
1434.3625 | 1367.3625 | 208.4722 | 205.1116 | 204.4765 | 181.0194 | 180.57 | 171.0869
1435.364 | 1368.364 | 208.2811 | 204.9709 | 204.3293 | 180.9329 | 180.4513 | 170.995
1436.3554 | 1369.3554 | 208.073 | 204.8153 | 204.2031 | 180.7542 | 180.3961 | 170.8936
1437.3568 | 1370.3568 | 207.8582 | 204.673 | 204.0655 | 180.4591 | 180.1955 | 170.8007
1438.3583 | 1371.3583 | 207.6692 | 204.5213 | 203.9283 | 180.4642 | 180.1334 | 170.6979
1439.3597 | 1372.3597 | 207.4503 | 204.369 | 203.7984 | 180.0562 | 180.0572 | 170.598
1440.3611 | 1373.3611 | 207.2027 | 204.2231 | 203.6536 | 179.959 | 179.933 | 170.5039
1441.3526 | 1374.3526 | 206.9523 | 204.0771 | 203.5297 | 179.6875 | 179.7573 | 170.4036
1442.364 | 1375.364 | 206.6675 | 203.9317 | 203.3926 | 179.6768 | 179.5884 | 170.2991
1443.3655 | 1376.3655 | 206.3807 | 203.7926 | 203.2482 | 179.4789 | 179.4918 | 170.2003
1444.3569 | 1377.3569 | 206.0527 | 203.6496 | 203.1144 | 179.2741 | 179.3798 | 170.0909
1445.3583 | 1378.3583 | 205.7677 | 203.5115 | 202.9769 | 178.8328 | 179.3128 | 169.9843
1446.3598 | 1379.3598 | 205.5373 | 203.3711 | 202.8472 | 178.5175 | 179.2377 | 169.8847
1447.3612 | 1380.3612 | 205.2874 | 203.2344 | 202.6992 | 178.625 | 178.9941 | 169.7756
1448.3626 | 1381.3626 | 205.0246 | 203.0938 | 202.5531 | 178.4956 | 178.6936 | 169.6669
1449.3641 | 1382.3641 | 204.7201 | 202.9662 | 202.4097 | 178.0525 | 178.5167 | 169.5515
1450.3655 | 1383.3655 | 204.4927 | 202.8245 | 202.2637 | 177.8982 | 178.4056 | 169.441
1451.3569 | 1384.3569 | 204.2558 | 202.6964 | 202.1182 | 177.5382 | 178.2595 | 169.3289
1452.3584 | 1385.3584 | 204.0255 | 202.5622 | 201.9653 | 177.2143 | 177.9338 | 169.2275
1453.3598 | 1386.3598 | 203.7463 | 202.4291 | 201.8328 | 177.0603 | 177.8385 | 169.1285
1454.3613 | 1387.3613 | 203.4833 | 202.2876 | 201.6787 | 177.1127 | 177.7668 | 169.0374
1455.3627 | 1388.3627 | 203.2279 | 202.1432 | 201.5237 | 176.827 | 177.72 | 168.9306
1456.3641 | 1389.3641 | 202.9637 | 202.0099 | 201.376 | 176.653 | 177.6369 | 168.8264
1457.3556 | 1390.3556 | 202.6928 | 201.8662 | 201.2356 | 176.452 | 177.42 | 168.7249
1458.357 | 1391.357 | 202.4811 | 201.7252 | 201.0832 | 176.1163 | 177.2153 | 168.625
1459.3585 | 1392.3585 | 202.2495 | 201.5752 | 200.9242 | 175.8992 | 177.0839 | 168.5148
1460.3599 | 1393.3599 | 201.9849 | 201.4348 | 200.7655 | 175.2842 | 176.9513 | 168.4126
1461.3613 | 1394.3613 | 201.7243 | 201.2906 | 200.6275 | 174.8375 | 176.6876 | 168.312
1462.3628 | 1395.3628 | 201.4474 | 201.15 | 200.4757 | 174.5381 | 176.3654 | 168.2018
1463.3542 | 1396.3542 | 201.1454 | 201.0106 | 200.3034 | 174.4134 | 176.1298 | 168.097
1464.3556 | 1397.3556 | 200.8733 | 200.8645 | 200.156 | 174.491 | 175.7482 | 167.986
1465.3571 | 1398.3571 | 200.6245 | 200.7207 | 199.9961 | 174.2154 | 175.334 | 167.8854
1466.3585 | 1399.3585 | 200.3549 | 200.5766 | 199.8541 | 174.0654 | 175.2902 | 167.7728
1467.36 | 1400.36 | 200.1249 | 200.4287 | 199.6984 | 173.8343 | 175.1223 | 167.6694
1468.3614 | 1401.3614 | 199.9198 | 200.296 | 199.5522 | 173.6342 | 174.9905 | 167.5723
1469.3628 | 1402.3628 | 199.6816 | 200.1445 | 199.3949 | 173.6329 | 174.664 | 167.4657
1470.3543 | 1403.3543 | 199.4077 | 199.9952 | 199.246 | 173.4091 | 174.4627 | 167.3537
1471.3557 | 1404.3557 | 199.1678 | 199.8351 | 199.1102 | 173.0714 | 174.2889 | 167.2508

## C3-4
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 158.0208 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38904.4455 | 1 | 0 | 38904.4455 | 1 | 0 | -52 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4457 | 1 | 0 | 38904.4457 | 1 | 0 | -35.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4459 | 1 | 0 | 38904.4459 | 1 | 0 | -18.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4461 | 1 | 0 | 38904.4461 | 1 | 0 | -1.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4463 | 1 | 0 | 38904.4463 | 1 | 0 | 15 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4465 | 1 | 0 | 38904.4465 | 1 | 0 | 32 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4467 | 2 | 0 | 38904.4467 | 1 | 0 | 48.5 | 115.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129319 | 258738 | 129318.9988
38904.4469 | 1 | 0 | 38904.4469 | 1 | 0 | 65.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4471 | 1 | 0 | 38904.4471 | 1 | 0 | 82.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4472 | 1 | 0 | 38904.4473 | 1 | 0 | 99 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4474 | 1 | 0 | 38904.4475 | 1 | 0 | 116 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4476 | 1 | 0 | 38904.4477 | 1 | 0 | 132.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4478 | 1 | 0 | 38904.4478 | 1 | 0 | 149.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.448 | 1 | 0 | 38904.448 | 1 | 0 | 166.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4482 | 1 | 0 | 38904.4482 | 1 | 0 | 183 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4484 | 1 | 0 | 38904.4484 | 1 | 0 | 200 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4486 | 1 | 0 | 38904.4486 | 1 | 0 | 216.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4488 | 1 | 0 | 38904.4488 | 1 | 0 | 233.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.449 | 1 | 0 | 38904.449 | 1 | 0 | 250.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4492 | 1 | 0 | 38904.4492 | 1 | 0 | 267 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4494 | 1 | 0 | 38904.4494 | 1 | 0 | 284 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4496 | 1 | 0 | 38904.4496 | 1 | 0 | 300.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4498 | 1 | 0 | 38904.4498 | 1 | 0 | 317.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.45 | 1 | 0 | 38904.45 | 1 | 0 | 334.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4502 | 1 | 0 | 38904.4502 | 1 | 0 | 351 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4504 | 1 | 0 | 38904.4504 | 1 | 0 | 368 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4506 | 1 | 0 | 38904.4506 | 1 | 0 | 384.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4508 | 1 | 0 | 38904.4508 | 1 | 0 | 401.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4509 | 1 | 0 | 38904.451 | 1 | 0 | 418.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4511 | 1 | 0 | 38904.4512 | 1 | 0 | 435 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4513 | 1 | 0 | 38904.4514 | 1 | 0 | 452 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4515 | 1 | 0 | 38904.4515 | 1 | 0 | 468.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4517 | 1 | 0 | 38904.4517 | 1 | 0 | 485.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4519 | 1 | 0 | 38904.4519 | 1 | 0 | 502.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4521 | 1 | 0 | 38904.4521 | 1 | 0 | 519 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4523 | 1 | 0 | 38904.4523 | 1 | 0 | 536 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4525 | 1 | 0 | 38904.4525 | 1 | 0 | 552.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4527 | 1 | 0 | 38904.4527 | 1 | 0 | 569.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4529 | 1 | 0 | 38904.4529 | 1 | 0 | 586 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4531 | 1 | 0 | 38904.4531 | 1 | 0 | 603 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4533 | 1 | 0 | 38904.4533 | 1 | 0 | 620 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4535 | 2 | 0 | 38904.4535 | 1 | 0 | 636.5 | 703.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129319 | 258738 | 129318.9988
38904.4537 | 1 | 0 | 38904.4537 | 1 | 0 | 653.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4539 | 1 | 0 | 38904.4539 | 1 | 0 | 670.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4541 | 1 | 0 | 38904.4541 | 1 | 0 | 687 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4542 | 1 | 0 | 38904.4543 | 1 | 0 | 704 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4544 | 1 | 0 | 38904.4545 | 1 | 0 | 720.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4546 | 1 | 0 | 38904.4547 | 1 | 0 | 737.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.4548 | 1 | 0 | 38904.4548 | 1 | 0 | 754 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38904.455 | 1959 | 0 | 38904.455 | 13 | 0 | 771 | 838 | 119.5971 | 0 | 0.79365 | 0 | 1.196 | 0 | 0.0079365 | 0 | 1.196 | 0.0079365 | 32.1276 | 19810.6154 | 30.9316
38904.4552 | 2022 | 0 | 38904.4552 | 15 | 0 | 788 | 855 | 123.4432 | 0 | 0.91575 | 0 | 1.2344 | 0 | 0.0091575 | 0 | 1.2344 | 0.0091575 | 28.0109 | 17155.8667 | 26.7764
38904.4554 | 2227 | 0 | 38904.4554 | 15 | 0 | 804.5 | 871.5 | 135.9585 | 0 | 0.91575 | 0 | 1.3596 | 0 | 0.0091575 | 0 | 1.3596 | 0.0091575 | 16.2272 | 17155.8667 | 14.8676
38904.4556 | 2397 | 0 | 38904.4556 | 15 | 0 | 821.5 | 888.5 | 146.337 | 0 | 0.91575 | 0 | 1.4634 | 0 | 0.0091575 | 0 | 1.4634 | 0.0091575 | 7.9841 | 17155.8667 | 6.5208
38904.4558 | 2172 | 0 | 38904.4558 | 15 | 0 | 838 | 905 | 132.6007 | 0 | 0.91575 | 0 | 1.326 | 0 | 0.0091575 | 0 | 1.326 | 0.0091575 | 19.1703 | 17155.8667 | 17.8443
38904.456 | 2359 | 0 | 38904.456 | 15 | 0 | 855 | 922 | 144.0171 | 0 | 0.91575 | 0 | 1.4402 | 0 | 0.0091575 | 0 | 1.4402 | 0.0091575 | 9.7236 | 17155.8667 | 8.2834
38904.4562 | 2523 | 0 | 38904.4562 | 14 | 0 | 872 | 939 | 154.0293 | 0 | 0.8547 | 0 | 1.5403 | 0 | 0.008547 | 0 | 1.5403 | 0.008547 | 2.5914 | 18388.4286 | 1.0511
38904.4564 | 2025 | 0 | 38904.4564 | 15 | 0 | 888.5 | 955.5 | 123.6264 | 0 | 0.91575 | 0 | 1.2363 | 0 | 0.0091575 | 0 | 1.2363 | 0.0091575 | 27.8212 | 17155.8667 | 26.585
38904.4566 | 2103 | 0 | 38904.4566 | 15 | 0 | 905.5 | 972.5 | 128.3883 | 0 | 0.91575 | 0 | 1.2839 | 0 | 0.0091575 | 0 | 1.2839 | 0.0091575 | 23.0804 | 17155.8667 | 21.7965
38904.4568 | 2087 | 0 | 38904.4568 | 15 | 0 | 922 | 989 | 127.4115 | 0 | 0.91575 | 0 | 1.2741 | 0 | 0.0091575 | 0 | 1.2741 | 0.0091575 | 24.024 | 17155.8667 | 22.7498
38904.457 | 2072 | 0 | 38904.457 | 14 | 0 | 939 | 1006 | 126.4957 | 0 | 0.8547 | 0 | 1.265 | 0 | 0.008547 | 0 | 1.265 | 0.008547 | 24.9218 | 18388.4286 | 23.6569
38904.4572 | 2354 | 0 | 38904.4572 | 14 | 0 | 955.5 | 1022.5 | 143.7118 | 0 | 0.8547 | 0 | 1.4371 | 0 | 0.008547 | 0 | 1.4371 | 0.008547 | 9.9567 | 18388.4286 | 8.5196
38904.4574 | 2041 | 0 | 38904.4574 | 13 | 0 | 972.5 | 1039.5 | 124.6032 | 0 | 0.79365 | 0 | 1.246 | 0 | 0.0079365 | 0 | 1.246 | 0.0079365 | 26.8192 | 19810.6154 | 25.5732
38904.4576 | 2273 | 0 | 38904.4576 | 19 | 0 | 989.5 | 1056.5 | 138.7668 | 0 | 1.16 | 0 | 1.3877 | 0 | 0.0116 | 0 | 1.3877 | 0.0116 | 13.8751 | 13523.0526 | 12.4874
38904.4577 | 2120 | 1 | 38904.4578 | 271 | 1 | 1006 | 1073 | 129.4261 | 0.06105 | 16.5446 | 0.06105 | 1.2943 | 0.0006105 | 0.16545 | 0.0006105 | 1.2937 | 0.16484 | 22.105 | 872.9146 | 41934.084
38904.4579 | 2164 | 1 | 38904.458 | 2109 | 0 | 1023 | 1090 | 132.1123 | 0.06105 | 128.7546 | 0 | 1.3211 | 0.0006105 | 1.2875 | 0 | 1.3205 | 1.2875 | 19.66 | 22.7302 | 7841.1943
38904.4581 | 2325 | 0 | 38904.4581 | 1987 | 0 | 1039.5 | 1106.5 | 141.9414 | 0 | 121.3065 | 0 | 1.4194 | 0 | 1.2131 | 0 | 1.4194 | 1.2131 | 11.3282 | 30.2657 | 9.9088
38904.4583 | 2463 | 0 | 38904.4583 | 2302 | 0 | 1056.5 | 1123.5 | 150.3663 | 0 | 140.5372 | 0 | 1.5037 | 0 | 1.4054 | 0 | 1.5037 | 1.4054 | 5.0905 | 12.4405 | 3.5869
38904.4585 | 2181 | 0 | 38904.4585 | 2145 | 0 | 1073.5 | 1140.5 | 133.1502 | 0 | 130.9524 | 0 | 1.3315 | 0 | 1.3095 | 0 | 1.3315 | 1.3095 | 18.6786 | 20.6704 | 17.3471
38904.4587 | 2458 | 0 | 38904.4587 | 2527 | 0 | 1090 | 1157 | 150.0611 | 0 | 154.2735 | 0 | 1.5006 | 0 | 1.5427 | 0 | 1.5006 | 1.5427 | 5.3043 | 2.429 | 3.8037
38904.4589 | 2198 | 0 | 38904.4589 | 2243 | 0 | 1107 | 1174 | 134.188 | 0 | 136.9353 | 0 | 1.3419 | 0 | 1.3694 | 0 | 1.3419 | 1.3694 | 17.7607 | 15.3981 | 16.4188
38904.4591 | 2200 | 0 | 38904.4591 | 1973 | 0 | 1123.5 | 1190.5 | 134.3101 | 0 | 120.4518 | 0 | 1.3431 | 0 | 1.2045 | 0 | 1.3431 | 1.2045 | 17.6536 | 31.1901 | 16.3105
38904.4593 | 2218 | 0 | 38904.4593 | 2261 | 0 | 1140.5 | 1207.5 | 135.409 | 0 | 138.0342 | 0 | 1.3541 | 0 | 1.3803 | 0 | 1.3541 | 1.3803 | 16.6988 | 14.4794 | 15.3447
38904.4595 | 2452 | 0 | 38904.4595 | 2014 | 0 | 1157.5 | 1224.5 | 149.6947 | 0 | 122.9548 | 0 | 1.4969 | 0 | 1.2295 | 0 | 1.4969 | 1.2295 | 5.562 | 28.5194 | 4.065
38904.4597 | 2045 | 0 | 38904.4597 | 2198 | 0 | 1174 | 1241 | 124.8474 | 0 | 134.188 | 0 | 1.2485 | 0 | 1.3419 | 0 | 1.2485 | 1.3419 | 26.5711 | 17.7607 | 25.3227
38904.4599 | 2313 | 0 | 38904.4599 | 2158 | 0 | 1191 | 1258 | 141.2088 | 0 | 131.746 | 0 | 1.4121 | 0 | 1.3175 | 0 | 1.4121 | 1.3175 | 11.9058 | 19.9435 | 10.4937
38904.4601 | 2158 | 0 | 38904.4601 | 2488 | 0 | 1207.5 | 1274.5 | 131.746 | 0 | 151.8926 | 0 | 1.3175 | 0 | 1.5189 | 0 | 1.3175 | 1.5189 | 19.9435 | 4.0346 | 18.626
38904.4603 | 2564 | 0 | 38904.4603 | 2189 | 0 | 1224.5 | 1291.5 | 156.5324 | 0 | 133.6386 | 0 | 1.5653 | 0 | 1.3364 | 0 | 1.5653 | 1.3364 | 0.95086 | 18.2449 | 0.61447
38904.4605 | 2530 | 0 | 38904.4605 | 2177 | 0 | 1241.5 | 1308.5 | 154.4567 | 0 | 132.906 | 0 | 1.5446 | 0 | 1.3291 | 0 | 1.5446 | 1.3291 | 2.3075 | 18.8966 | 0.76294
38904.4607 | 2062 | 0 | 38904.4607 | 2322 | 0 | 1258 | 1325 | 125.8852 | 0 | 141.7582 | 0 | 1.2589 | 0 | 1.4176 | 0 | 1.2589 | 1.4176 | 25.5276 | 11.472 | 24.2688
38904.4609 | 2206 | 0 | 38904.4609 | 2094 | 0 | 1275 | 1342 | 134.6764 | 0 | 127.8388 | 0 | 1.3468 | 0 | 1.2784 | 0 | 1.3468 | 1.2784 | 17.3336 | 23.6094 | 15.9869
38904.4611 | 2103 | 0 | 38904.4611 | 2222 | 0 | 1291.5 | 1358.5 | 128.3883 | 0 | 135.6532 | 0 | 1.2839 | 0 | 1.3565 | 0 | 1.2839 | 1.3565 | 23.0804 | 16.4887 | 21.7965
38904.4613 | 2466 | 0 | 38904.4613 | 2011 | 0 | 1308.5 | 1375.5 | 150.5495 | 0 | 122.7717 | 0 | 1.5055 | 0 | 1.2277 | 0 | 1.5055 | 1.2277 | 4.9627 | 28.7111 | 3.4572
38904.4614 | 2115 | 0 | 38904.4615 | 1971 | 0 | 1325.5 | 1392.5 | 129.1209 | 0 | 120.3297 | 0 | 1.2912 | 0 | 1.2033 | 0 | 1.2912 | 1.2033 | 22.382 | 31.3232 | 21.0908
38904.4616 | 2369 | 0 | 38904.4617 | 1998 | 0 | 1342 | 1409 | 144.6276 | 0 | 121.978 | 0 | 1.4463 | 0 | 1.2198 | 0 | 1.4463 | 1.2198 | 9.2604 | 29.5485 | 7.8142
38904.4618 | 2477 | 0 | 38904.4619 | 2572 | 0 | 1359 | 1426 | 151.221 | 0 | 157.0208 | 0 | 1.5122 | 0 | 1.5702 | 0 | 1.5122 | 1.5702 | 4.4966 | 0.63686 | 2.9844
38904.462 | 2015 | 0 | 38904.462 | 2479 | 0 | 1375.5 | 1442.5 | 123.0159 | 0 | 151.3431 | 0 | 1.2302 | 0 | 1.5134 | 0 | 1.2302 | 1.5134 | 28.4556 | 4.4123 | 27.2254
38904.4622 | 2292 | 0 | 38904.4622 | 2013 | 0 | 1392.5 | 1459.5 | 139.9267 | 0 | 122.8938 | 0 | 1.3993 | 0 | 1.2289 | 0 | 1.3993 | 1.2289 | 12.9311 | 28.5832 | 11.5318

## C2-4
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 157.8376 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38904.4455 | 1 | 0 | 38904.4455 | 1 | 0 | -55 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4457 | 1 | 0 | 38904.4457 | 1 | 0 | -38 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4459 | 1 | 0 | 38904.4459 | 1 | 0 | -21.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4461 | 1 | 0 | 38904.4461 | 1 | 0 | -4.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4463 | 1 | 0 | 38904.4463 | 1 | 0 | 12.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4464 | 1 | 0 | 38904.4465 | 1 | 0 | 29 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4466 | 1 | 0 | 38904.4467 | 2 | 0 | 46 | 113 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 258438 | 129169 | 258437.9994
38904.4468 | 1 | 0 | 38904.4468 | 1 | 0 | 62.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.447 | 1 | 0 | 38904.447 | 1 | 0 | 79.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4472 | 1 | 0 | 38904.4472 | 1 | 0 | 96.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4474 | 1 | 0 | 38904.4474 | 1 | 0 | 113 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4476 | 1 | 0 | 38904.4476 | 1 | 0 | 130 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4478 | 1 | 0 | 38904.4478 | 1 | 0 | 146.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.448 | 1 | 0 | 38904.448 | 1 | 0 | 163.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4482 | 1 | 0 | 38904.4482 | 1 | 0 | 180.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4484 | 1 | 0 | 38904.4484 | 1 | 0 | 197 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4486 | 1 | 0 | 38904.4486 | 1 | 0 | 214 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4488 | 1 | 0 | 38904.4488 | 1 | 0 | 230.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.449 | 1 | 0 | 38904.449 | 1 | 0 | 247.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4492 | 1 | 0 | 38904.4492 | 1 | 0 | 264.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4494 | 1 | 0 | 38904.4494 | 1 | 0 | 281 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4495 | 1 | 0 | 38904.4496 | 1 | 0 | 298 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4497 | 1 | 0 | 38904.4498 | 1 | 0 | 314.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4499 | 1 | 0 | 38904.45 | 1 | 0 | 331.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4501 | 1 | 0 | 38904.4502 | 1 | 0 | 348.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4503 | 1 | 0 | 38904.4503 | 1 | 0 | 365.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4505 | 1 | 0 | 38904.4505 | 1 | 0 | 382 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4507 | 1 | 0 | 38904.4507 | 1 | 0 | 398.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4509 | 1 | 0 | 38904.4509 | 1 | 0 | 415.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4511 | 1 | 0 | 38904.4511 | 1 | 0 | 432.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4513 | 1 | 0 | 38904.4513 | 1 | 0 | 449 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4515 | 1 | 0 | 38904.4515 | 1 | 0 | 466 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4517 | 1 | 0 | 38904.4517 | 1 | 0 | 482.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4519 | 1 | 0 | 38904.4519 | 1 | 0 | 499.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4521 | 1 | 0 | 38904.4521 | 1 | 0 | 516 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4523 | 1 | 0 | 38904.4523 | 1 | 0 | 533 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4525 | 1 | 0 | 38904.4525 | 1 | 0 | 550 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4527 | 1 | 0 | 38904.4527 | 1 | 0 | 566.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4529 | 1 | 0 | 38904.4529 | 1 | 0 | 583.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4531 | 1 | 0 | 38904.4531 | 1 | 0 | 600.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4532 | 1 | 0 | 38904.4533 | 1 | 0 | 617 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4534 | 1 | 0 | 38904.4535 | 1 | 0 | 634 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4536 | 1 | 0 | 38904.4536 | 1 | 0 | 650.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4538 | 1 | 0 | 38904.4538 | 1 | 0 | 667.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.454 | 1 | 0 | 38904.454 | 1 | 0 | 684.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4542 | 1 | 0 | 38904.4542 | 1 | 0 | 701 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4544 | 1 | 0 | 38904.4544 | 1 | 0 | 718 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4546 | 1 | 0 | 38904.4546 | 1 | 0 | 734.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.4548 | 1 | 0 | 38904.4548 | 1 | 0 | 751.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
38904.455 | 4 | 0 | 38904.455 | 2 | 0 | 768.5 | 835.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 64534.5 | 129169 | 64534.4976
38904.4552 | 14 | 0 | 38904.4552 | 11 | 0 | 785.5 | 852.5 | 0.8547 | 0 | 0.67155 | 0 | 0.008547 | 0 | 0.0067155 | 0 | 0.008547 | 0.0067155 | 18367 | 23403.4545 | 18366.9915
38904.4554 | 15 | 0 | 38904.4554 | 11 | 0 | 802 | 869 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17135.8667 | 23403.4545 | 17135.8575
38904.4556 | 15 | 0 | 38904.4556 | 11 | 0 | 818.5 | 885.5 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17135.8667 | 23403.4545 | 17135.8575
38904.4558 | 15 | 0 | 38904.4558 | 10 | 0 | 835.5 | 902.5 | 0.91575 | 0 | 0.6105 | 0 | 0.0091575 | 0 | 0.006105 | 0 | 0.0091575 | 0.006105 | 17135.8667 | 25753.8 | 17135.8575
38904.456 | 15 | 0 | 38904.456 | 11 | 0 | 852 | 919 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17135.8667 | 23403.4545 | 17135.8575
38904.4562 | 15 | 0 | 38904.4562 | 11 | 0 | 869 | 936 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17135.8667 | 23403.4545 | 17135.8575
38904.4564 | 122 | 0 | 38904.4564 | 11 | 0 | 885.5 | 952.5 | 7.4481 | 0 | 0.67155 | 0 | 0.074481 | 0 | 0.0067155 | 0 | 0.074481 | 0.0067155 | 2019.1639 | 23403.4545 | 2019.0895
38904.4566 | 75 | 0 | 38904.4566 | 13 | 0 | 902.5 | 969.5 | 4.5788 | 0 | 0.79365 | 0 | 0.045788 | 0 | 0.0079365 | 0 | 0.045788 | 0.0079365 | 3347.1733 | 19787.5385 | 3347.1275
38904.4567 | 1899 | 6 | 38904.4568 | 15 | 0 | 919.5 | 986.5 | 115.9341 | 0.3663 | 0.91575 | 0 | 1.1593 | 0.003663 | 0.0091575 | 0 | 1.1557 | 0.0091575 | 36.2595 | 17135.8667 | 11273.8756
38904.4569 | 2041 | 0 | 38904.457 | 14 | 0 | 936.5 | 1003.5 | 124.6032 | 0 | 0.8547 | 0 | 1.246 | 0 | 0.008547 | 0 | 1.246 | 0.008547 | 26.6722 | 18367 | 25.4262
38904.4571 | 2331 | 0 | 38904.4572 | 14 | 0 | 953 | 1020 | 142.3077 | 0 | 0.8547 | 0 | 1.4231 | 0 | 0.008547 | 0 | 1.4231 | 0.008547 | 10.9129 | 18367 | 9.4898
38904.4573 | 2499 | 0 | 38904.4573 | 14 | 0 | 969.5 | 1036.5 | 152.5641 | 0 | 0.8547 | 0 | 1.5256 | 0 | 0.008547 | 0 | 1.5256 | 0.008547 | 3.4566 | 18367 | 1.9309
38904.4575 | 2443 | 0 | 38904.4575 | 13 | 0 | 986.5 | 1053.5 | 149.1453 | 0 | 0.79365 | 0 | 1.4915 | 0 | 0.0079365 | 0 | 1.4915 | 0.0079365 | 5.8281 | 19787.5385 | 4.3366
38904.4577 | 2129 | 5 | 38904.4577 | 32 | 2 | 1003.5 | 1070.5 | 129.9756 | 0.30525 | 1.9536 | 0.1221 | 1.2998 | 0.0030525 | 0.019536 | 0.001221 | 1.2967 | 0.018315 | 21.4872 | 12339.8518 | 8955.03
38904.4579 | 2293 | 1 | 38904.4579 | 2427 | 1 | 1020.5 | 1087.5 | 139.9878 | 0.06105 | 148.1685 | 0.06105 | 1.3999 | 0.0006105 | 1.4817 | 0.0006105 | 1.3993 | 1.4811 | 12.8421 | 6.5495 | 1791.0769
38904.4581 | 2339 | 0 | 38904.4581 | 2155 | 0 | 1037 | 1104 | 142.7961 | 0 | 131.5629 | 0 | 1.428 | 0 | 1.3156 | 0 | 1.428 | 1.3156 | 10.5336 | 19.9712 | 9.1056
38904.4583 | 1980 | 0 | 38904.4583 | 2157 | 0 | 1053.5 | 1120.5 | 120.8791 | 0 | 131.685 | 0 | 1.2088 | 0 | 1.3168 | 0 | 1.2088 | 1.3168 | 30.5747 | 19.86 | 29.366
38904.4585 | 2534 | 0 | 38904.4585 | 1997 | 0 | 1070.5 | 1137.5 | 154.7009 | 0 | 121.917 | 0 | 1.547 | 0 | 1.2192 | 0 | 1.547 | 1.2192 | 2.0276 | 29.4632 | 0.48062
38904.4587 | 2446 | 0 | 38904.4587 | 1984 | 0 | 1087.5 | 1154.5 | 149.3284 | 0 | 121.1233 | 0 | 1.4933 | 0 | 1.2112 | 0 | 1.4933 | 1.2112 | 5.6983 | 30.3115 | 4.205
38904.4589 | 2502 | 0 | 38904.4589 | 2070 | 0 | 1104.5 | 1171.5 | 152.7473 | 0 | 126.3736 | 0 | 1.5275 | 0 | 1.2637 | 0 | 1.5275 | 1.2637 | 3.3325 | 24.8976 | 1.8051
38904.4591 | 2568 | 0 | 38904.4591 | 2015 | 0 | 1121 | 1188 | 156.7766 | 0 | 123.0159 | 0 | 1.5678 | 0 | 1.2302 | 0 | 1.5678 | 1.2302 | 0.67679 | 28.3067 | 0.89097
38904.4593 | 2555 | 0 | 38904.4593 | 2013 | 0 | 1137.5 | 1204.5 | 155.9829 | 0 | 122.8938 | 0 | 1.5598 | 0 | 1.2289 | 0 | 1.5598 | 1.2289 | 1.189 | 28.4342 | 0.37079
38904.4595 | 2504 | 0 | 38904.4595 | 2165 | 0 | 1154.5 | 1221.5 | 152.8694 | 0 | 132.1734 | 0 | 1.5287 | 0 | 1.3217 | 0 | 1.5287 | 1.3217 | 3.25 | 19.4171 | 1.7213
38904.4597 | 2426 | 0 | 38904.4597 | 2480 | 0 | 1171.5 | 1238.5 | 148.1074 | 0 | 151.4042 | 0 | 1.4811 | 0 | 1.514 | 0 | 1.4811 | 1.514 | 6.5697 | 4.2492 | 5.0886
38904.4599 | 2568 | 0 | 38904.4599 | 2485 | 0 | 1188.5 | 1255.5 | 156.7766 | 0 | 151.7094 | 0 | 1.5678 | 0 | 1.5171 | 0 | 1.5678 | 1.5171 | 0.67679 | 4.0394 | 0.89097
38904.46 | 2486 | 0 | 38904.4601 | 2555 | 0 | 1205 | 1272 | 151.7705 | 0 | 155.9829 | 0 | 1.5177 | 0 | 1.5598 | 0 | 1.5177 | 1.5598 | 3.9976 | 1.189 | 2.4799
38904.4602 | 2334 | 0 | 38904.4603 | 2556 | 0 | 1221.5 | 1288.5 | 142.4908 | 0 | 156.044 | 0 | 1.4249 | 0 | 1.5604 | 0 | 1.4249 | 1.5604 | 10.7704 | 1.1495 | 9.3454
38904.4604 | 2082 | 0 | 38904.4605 | 2012 | 0 | 1238.5 | 1305.5 | 127.1062 | 0 | 122.8327 | 0 | 1.2711 | 0 | 1.2283 | 0 | 1.2711 | 1.2283 | 24.1777 | 28.498 | 22.9067
38904.4606 | 2137 | 0 | 38904.4606 | 2102 | 0 | 1255.5 | 1322.5 | 130.464 | 0 | 128.3272 | 0 | 1.3046 | 0 | 1.2833 | 0 | 1.3046 | 1.2833 | 20.9818 | 22.9962 | 19.6771
38904.4608 | 1992 | 0 | 38904.4608 | 2517 | 0 | 1272 | 1339 | 121.6117 | 0 | 153.663 | 0 | 1.2161 | 0 | 1.5366 | 0 | 1.2161 | 1.5366 | 29.7882 | 2.7167 | 28.572
38904.461 | 2565 | 0 | 38904.461 | 2348 | 0 | 1289 | 1356 | 156.5934 | 0 | 143.3455 | 0 | 1.5659 | 0 | 1.4335 | 0 | 1.5659 | 1.4335 | 0.79454 | 10.1099 | 0.77139
38904.4612 | 2233 | 0 | 38904.4612 | 2203 | 0 | 1305.5 | 1372.5 | 136.3248 | 0 | 134.4933 | 0 | 1.3632 | 0 | 1.3449 | 0 | 1.3632 | 1.3449 | 15.7806 | 17.3572 | 14.4173
38904.4614 | 2564 | 0 | 38904.4614 | 2117 | 0 | 1322.5 | 1389.5 | 156.5324 | 0 | 129.243 | 0 | 1.5653 | 0 | 1.2924 | 0 | 1.5653 | 1.2924 | 0.83385 | 22.1247 | 0.73147
38904.4616 | 2569 | 0 | 38904.4616 | 2289 | 0 | 1339.5 | 1406.5 | 156.8376 | 0 | 139.7436 | 0 | 1.5684 | 0 | 1.3974 | 0 | 1.5684 | 1.3974 | 0.6376 | 12.948 | 0.93077
38904.4618 | 1988 | 0 | 38904.4618 | 2109 | 0 | 1356 | 1423 | 121.3675 | 0 | 128.7546 | 0 | 1.2137 | 0 | 1.2875 | 0 | 1.2137 | 1.2875 | 30.0493 | 22.588 | 28.8356
38904.462 | 2273 | 0 | 38904.462 | 1967 | 0 | 1373 | 1440 | 138.7668 | 0 | 120.0855 | 0 | 1.3877 | 0 | 1.2009 | 0 | 1.3877 | 1.2009 | 13.7431 | 31.4377 | 12.3554
38904.4622 | 2506 | 0 | 38904.4622 | 2349 | 0 | 1389.5 | 1456.5 | 152.9915 | 0 | 143.4066 | 0 | 1.5299 | 0 | 1.4341 | 0 | 1.5299 | 1.4341 | 3.1676 | 10.063 | 1.6377

## C2-3
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 157.4103 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38904.4454 | 1 | 0 | 38904.4455 | 1 | 0 | -57.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4456 | 1 | 0 | 38904.4456 | 1 | 0 | -41 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4458 | 1 | 0 | 38904.4458 | 1 | 0 | -24 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.446 | 1 | 0 | 38904.446 | 1 | 0 | -7.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4462 | 1 | 0 | 38904.4462 | 1 | 0 | 9.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4464 | 1 | 0 | 38904.4464 | 1 | 0 | 26.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4466 | 1 | 0 | 38904.4466 | 1 | 0 | 43 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4468 | 1 | 0 | 38904.4468 | 1 | 0 | 60 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.447 | 1 | 0 | 38904.447 | 1 | 0 | 76.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4472 | 1 | 0 | 38904.4472 | 1 | 0 | 93.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4474 | 1 | 0 | 38904.4474 | 1 | 0 | 110.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4476 | 1 | 0 | 38904.4476 | 1 | 0 | 127 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4478 | 1 | 0 | 38904.4478 | 1 | 0 | 144 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.448 | 1 | 0 | 38904.448 | 1 | 0 | 160.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4482 | 1 | 0 | 38904.4482 | 1 | 0 | 177.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4484 | 1 | 0 | 38904.4484 | 1 | 0 | 194.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4485 | 1 | 0 | 38904.4486 | 1 | 0 | 211 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4487 | 1 | 0 | 38904.4488 | 1 | 0 | 228 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4489 | 1 | 0 | 38904.4489 | 1 | 0 | 244.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4491 | 1 | 0 | 38904.4491 | 1 | 0 | 261.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4493 | 1 | 0 | 38904.4493 | 1 | 0 | 278.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4495 | 1 | 0 | 38904.4495 | 1 | 0 | 295 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4497 | 1 | 0 | 38904.4497 | 1 | 0 | 312 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4499 | 1 | 0 | 38904.4499 | 1 | 0 | 328.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4501 | 1 | 0 | 38904.4501 | 1 | 0 | 345.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4503 | 1 | 0 | 38904.4503 | 1 | 0 | 362.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4505 | 1 | 0 | 38904.4505 | 1 | 0 | 379 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4507 | 1 | 0 | 38904.4507 | 1 | 0 | 396 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4509 | 1 | 0 | 38904.4509 | 1 | 0 | 412.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4511 | 1 | 0 | 38904.4511 | 1 | 0 | 429.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4513 | 1 | 0 | 38904.4513 | 1 | 0 | 446.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4515 | 1 | 0 | 38904.4515 | 1 | 0 | 463 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4517 | 1 | 0 | 38904.4517 | 1 | 0 | 480 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4519 | 1 | 0 | 38904.4519 | 1 | 0 | 496.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.452 | 1 | 0 | 38904.4521 | 1 | 0 | 513.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4522 | 1 | 0 | 38904.4523 | 1 | 0 | 530.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4524 | 1 | 0 | 38904.4525 | 1 | 0 | 547 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4526 | 1 | 0 | 38904.4527 | 1 | 0 | 564 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4528 | 1 | 0 | 38904.4528 | 1 | 0 | 580.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.453 | 1 | 0 | 38904.453 | 1 | 0 | 597.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4532 | 1 | 0 | 38904.4532 | 1 | 0 | 614.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4534 | 1 | 0 | 38904.4534 | 1 | 0 | 631 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4536 | 1 | 0 | 38904.4536 | 1 | 0 | 648 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4538 | 1 | 0 | 38904.4538 | 1 | 0 | 664.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.454 | 1 | 0 | 38904.454 | 1 | 0 | 681.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4542 | 1 | 0 | 38904.4542 | 1 | 0 | 698 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4544 | 1 | 0 | 38904.4544 | 1 | 0 | 715 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4546 | 1 | 0 | 38904.4546 | 1 | 0 | 732 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.4548 | 1 | 0 | 38904.4548 | 1 | 0 | 748.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38904.455 | 1 | 0 | 38904.455 | 69 | 0 | 765.5 | 832.5 | 0.06105 | 0 | 4.2125 | 0 | 0.0006105 | 0 | 0.042125 | 0 | 0.0006105 | 0.042125 | 257738 | 3636.7826 | 257737.9994
38904.4552 | 6 | 0 | 38904.4552 | 2436 | 0 | 782.5 | 849.5 | 0.3663 | 0 | 148.7179 | 0 | 0.003663 | 0 | 1.4872 | 0 | 0.003663 | 1.4872 | 42873 | 5.8448 | 42872.9963
38904.4553 | 8 | 0 | 38904.4554 | 2409 | 0 | 799 | 866 | 0.4884 | 0 | 147.0696 | 0 | 0.004884 | 0 | 1.4707 | 0 | 0.004884 | 1.4707 | 32129.75 | 7.0311 | 32129.7451
38904.4555 | 9 | 0 | 38904.4556 | 2484 | 0 | 815.5 | 882.5 | 0.54945 | 0 | 151.6484 | 0 | 0.0054945 | 0 | 1.5165 | 0 | 0.0054945 | 1.5165 | 28548.6667 | 3.7995 | 28548.6612
38904.4557 | 8 | 0 | 38904.4558 | 2339 | 0 | 832.5 | 899.5 | 0.4884 | 0 | 142.7961 | 0 | 0.004884 | 0 | 1.428 | 0 | 0.004884 | 1.428 | 32129.75 | 10.2343 | 32129.7451
38904.4559 | 8 | 0 | 38904.4559 | 1996 | 0 | 849.5 | 916.5 | 0.4884 | 0 | 121.8559 | 0 | 0.004884 | 0 | 1.2186 | 0 | 0.004884 | 1.2186 | 32129.75 | 29.1774 | 32129.7451
38904.4561 | 8 | 0 | 38904.4561 | 2070 | 0 | 866 | 933 | 0.4884 | 0 | 126.3736 | 0 | 0.004884 | 0 | 1.2637 | 0 | 0.004884 | 1.2637 | 32129.75 | 24.5594 | 32129.7451
38904.4563 | 8 | 0 | 38904.4563 | 2512 | 0 | 883 | 950 | 0.4884 | 0 | 153.3578 | 0 | 0.004884 | 0 | 1.5336 | 0 | 0.004884 | 1.5336 | 32129.75 | 2.6425 | 32129.7451
38904.4565 | 1471 | 6 | 38904.4565 | 2402 | 0 | 899.5 | 966.5 | 89.8046 | 0.3663 | 146.6422 | 0 | 0.89805 | 0.003663 | 1.4664 | 0 | 0.89438 | 1.4664 | 80.0541 | 7.343 | 1255.7071
38904.4567 | 265 | 3 | 38904.4567 | 1961 | 0 | 916.5 | 983.5 | 16.1783 | 0.18315 | 119.7192 | 0 | 0.16178 | 0.0018315 | 1.1972 | 0 | 0.15995 | 1.1972 | 916.2953 | 31.4829 | 18440.292
38904.4569 | 2017 | 0 | 38904.4569 | 2350 | 0 | 933.5 | 1000.5 | 123.138 | 0 | 143.4676 | 0 | 1.2314 | 0 | 1.4347 | 0 | 1.2314 | 1.4347 | 27.8324 | 9.7183 | 26.601
38904.4571 | 2413 | 0 | 38904.4571 | 2213 | 0 | 950.5 | 1017.5 | 147.3138 | 0 | 135.1038 | 0 | 1.4731 | 0 | 1.351 | 0 | 1.4731 | 1.351 | 6.8537 | 16.5106 | 5.3806
38904.4573 | 2011 | 0 | 38904.4573 | 2105 | 0 | 967 | 1034 | 122.7717 | 0 | 128.5104 | 0 | 1.2277 | 0 | 1.2851 | 0 | 1.2277 | 1.2851 | 28.2138 | 22.4884 | 26.9861
38904.4575 | 2031 | 0 | 38904.4575 | 2123 | 0 | 983.5 | 1050.5 | 123.9927 | 0 | 129.6093 | 0 | 1.2399 | 0 | 1.2961 | 0 | 1.2399 | 1.2961 | 26.9513 | 21.4498 | 25.7113
38904.4577 | 2262 | 21 | 38904.4577 | 2093 | 14 | 1000.5 | 1067.5 | 138.0952 | 1.2821 | 127.7778 | 0.8547 | 1.381 | 0.012821 | 1.2778 | 0.008547 | 1.3681 | 1.2692 | 14.68 | 24.4693 | 276.5161
38904.4579 | 2010 | 3 | 38904.4579 | 2232 | 1 | 1017.5 | 1084.5 | 122.7106 | 0.18315 | 136.2637 | 0.06105 | 1.2271 | 0.0018315 | 1.3626 | 0.0006105 | 1.2253 | 1.362 | 28.5947 | 15.5501 | 2536.1984
38904.4581 | 1982 | 0 | 38904.4581 | 2489 | 0 | 1034 | 1101 | 121.0012 | 0 | 151.9536 | 0 | 1.21 | 0 | 1.5195 | 0 | 1.21 | 1.5195 | 30.0898 | 3.591 | 28.8798
38904.4583 | 2181 | 0 | 38904.4583 | 2062 | 0 | 1051 | 1118 | 133.1502 | 0 | 125.8852 | 0 | 1.3315 | 0 | 1.2589 | 0 | 1.3315 | 1.2589 | 18.2201 | 25.0427 | 16.8886
38904.4585 | 2311 | 0 | 38904.4585 | 2284 | 0 | 1067.5 | 1134.5 | 141.0867 | 0 | 139.4383 | 0 | 1.4109 | 0 | 1.3944 | 0 | 1.4109 | 1.3944 | 11.5699 | 12.8888 | 10.159
38904.4587 | 2110 | 0 | 38904.4587 | 2292 | 0 | 1084.5 | 1151.5 | 128.8156 | 0 | 139.9267 | 0 | 1.2882 | 0 | 1.3993 | 0 | 1.2882 | 1.3993 | 22.1981 | 12.4948 | 20.9099
38904.4589 | 2020 | 0 | 38904.4589 | 2506 | 0 | 1101.5 | 1168.5 | 123.3211 | 0 | 152.9915 | 0 | 1.2332 | 0 | 1.5299 | 0 | 1.2332 | 1.5299 | 27.6426 | 2.8883 | 26.4094
38904.4591 | 1998 | 0 | 38904.4591 | 1968 | 0 | 1118.5 | 1185.5 | 121.978 | 0 | 120.1465 | 0 | 1.2198 | 0 | 1.2015 | 0 | 1.2198 | 1.2015 | 29.048 | 31.0152 | 27.8283
38904.4592 | 2200 | 0 | 38904.4593 | 2548 | 0 | 1135 | 1202 | 134.3101 | 0 | 155.5556 | 0 | 1.3431 | 0 | 1.5556 | 0 | 1.3431 | 1.5556 | 17.1991 | 1.1923 | 15.856
38904.4594 | 2537 | 0 | 38904.4594 | 2556 | 0 | 1151.5 | 1218.5 | 154.884 | 0 | 156.044 | 0 | 1.5488 | 0 | 1.5604 | 0 | 1.5488 | 1.5604 | 1.6311 | 0.87559 | 0.08222
38904.4596 | 2508 | 0 | 38904.4596 | 2313 | 0 | 1168.5 | 1235.5 | 153.1136 | 0 | 141.2088 | 0 | 1.5311 | 0 | 1.4121 | 0 | 1.5311 | 1.4121 | 2.8062 | 11.4734 | 1.2751
38904.4598 | 2371 | 0 | 38904.4598 | 2165 | 0 | 1185.5 | 1252.5 | 144.7497 | 0 | 132.1734 | 0 | 1.4475 | 0 | 1.3217 | 0 | 1.4475 | 1.3217 | 8.7465 | 19.0938 | 7.299
38904.46 | 2444 | 0 | 38904.46 | 2534 | 0 | 1202 | 1269 | 149.2063 | 0 | 154.7009 | 0 | 1.4921 | 0 | 1.547 | 0 | 1.4921 | 1.547 | 5.4984 | 1.7514 | 4.0063
38904.4602 | 2402 | 0 | 38904.4602 | 2026 | 0 | 1219 | 1286 | 146.6422 | 0 | 123.6874 | 0 | 1.4664 | 0 | 1.2369 | 0 | 1.4664 | 1.2369 | 7.343 | 27.2646 | 5.8766
38904.4604 | 1965 | 0 | 38904.4604 | 2415 | 0 | 1236 | 1303 | 119.9634 | 0 | 147.4359 | 0 | 1.1996 | 0 | 1.4744 | 0 | 1.1996 | 1.4744 | 31.2153 | 6.7652 | 30.0156
38904.4606 | 2254 | 0 | 38904.4606 | 2508 | 0 | 1252.5 | 1319.5 | 137.6068 | 0 | 153.1136 | 0 | 1.3761 | 0 | 1.5311 | 0 | 1.3761 | 1.5311 | 14.3913 | 2.8062 | 13.0152
38904.4608 | 2401 | 0 | 38904.4608 | 2558 | 0 | 1269.5 | 1336.5 | 146.5812 | 0 | 156.1661 | 0 | 1.4658 | 0 | 1.5617 | 0 | 1.4658 | 1.5617 | 7.3878 | 0.79672 | 5.9219
38904.461 | 1999 | 0 | 38904.461 | 2324 | 0 | 1286.5 | 1353.5 | 122.0391 | 0 | 141.8803 | 0 | 1.2204 | 0 | 1.4188 | 0 | 1.2204 | 1.4188 | 28.9835 | 10.9458 | 27.7631
38904.4612 | 2095 | 0 | 38904.4612 | 2328 | 0 | 1303 | 1370 | 127.8999 | 0 | 142.1245 | 0 | 1.279 | 0 | 1.4212 | 0 | 1.279 | 1.4212 | 23.073 | 10.7552 | 21.794
38904.4614 | 2225 | 0 | 38904.4614 | 2083 | 0 | 1319.5 | 1386.5 | 135.8364 | 0 | 127.1673 | 0 | 1.3584 | 0 | 1.2717 | 0 | 1.3584 | 1.2717 | 15.8822 | 23.782 | 14.5239
38904.4616 | 2087 | 0 | 38904.4616 | 2562 | 0 | 1336.5 | 1403.5 | 127.4115 | 0 | 156.4103 | 0 | 1.2741 | 0 | 1.5641 | 0 | 1.2741 | 1.5641 | 23.5448 | 0.63934 | 22.2707
38904.4618 | 2046 | 0 | 38904.4618 | 2556 | 0 | 1353.5 | 1420.5 | 124.9084 | 0 | 156.044 | 0 | 1.2491 | 0 | 1.5604 | 0 | 1.2491 | 1.5604 | 26.0205 | 0.87559 | 24.7714
38904.462 | 2340 | 0 | 38904.462 | 2264 | 0 | 1370 | 1437 | 142.8571 | 0 | 138.2173 | 0 | 1.4286 | 0 | 1.3822 | 0 | 1.4286 | 1.3822 | 10.1872 | 13.886 | 8.7586
38904.4622 | 2516 | 0 | 38904.4622 | 2150 | 0 | 1387 | 1454 | 153.602 | 0 | 131.2576 | 0 | 1.536 | 0 | 1.3126 | 0 | 1.536 | 1.3126 | 2.4793 | 19.9247 | 0.94331

## C1-4
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 157.7766 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38904.4454 | 1 | 0 | 38904.4454 | 1 | 0 | -60.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4456 | 1 | 0 | 38904.4456 | 1 | 0 | -43.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4458 | 1 | 0 | 38904.4458 | 1 | 0 | -27 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.446 | 1 | 0 | 38904.446 | 1 | 0 | -10 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4462 | 1 | 0 | 38904.4462 | 1 | 0 | 6.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4464 | 1 | 0 | 38904.4464 | 1 | 0 | 23.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4466 | 1 | 0 | 38904.4466 | 1 | 0 | 40.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4468 | 1 | 0 | 38904.4468 | 1 | 0 | 57 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.447 | 1 | 0 | 38904.447 | 1 | 0 | 74 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4472 | 1 | 0 | 38904.4472 | 1 | 0 | 90.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4473 | 1 | 0 | 38904.4474 | 1 | 0 | 107.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4475 | 1 | 0 | 38904.4476 | 1 | 0 | 124.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4477 | 1 | 0 | 38904.4478 | 1 | 0 | 141 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4479 | 1 | 0 | 38904.448 | 1 | 0 | 158 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4481 | 1 | 0 | 38904.4481 | 1 | 0 | 174.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4483 | 1 | 0 | 38904.4483 | 1 | 0 | 191.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4485 | 1 | 0 | 38904.4485 | 1 | 0 | 208.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4487 | 1 | 0 | 38904.4487 | 1 | 0 | 225 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4489 | 1 | 0 | 38904.4489 | 1 | 0 | 242 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4491 | 1 | 0 | 38904.4491 | 1 | 0 | 258.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4493 | 1 | 0 | 38904.4493 | 1 | 0 | 275.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4495 | 1 | 0 | 38904.4495 | 1 | 0 | 292.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4497 | 1 | 0 | 38904.4497 | 1 | 0 | 309 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4499 | 1 | 0 | 38904.4499 | 1 | 0 | 326 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4501 | 1 | 0 | 38904.4501 | 1 | 0 | 342.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4503 | 1 | 0 | 38904.4503 | 1 | 0 | 359.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4505 | 1 | 0 | 38904.4505 | 1 | 0 | 376.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4506 | 1 | 0 | 38904.4507 | 1 | 0 | 393 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4508 | 1 | 0 | 38904.4509 | 1 | 0 | 410 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.451 | 1 | 0 | 38904.4511 | 1 | 0 | 426.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4512 | 1 | 0 | 38904.4512 | 1 | 0 | 443.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4514 | 1 | 0 | 38904.4514 | 1 | 0 | 460.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4516 | 1 | 0 | 38904.4516 | 1 | 0 | 477 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4518 | 1 | 0 | 38904.4518 | 1 | 0 | 494 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.452 | 1 | 0 | 38904.452 | 1 | 0 | 510.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4522 | 1 | 0 | 38904.4522 | 1 | 0 | 527.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4524 | 1 | 0 | 38904.4524 | 1 | 0 | 544.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4526 | 1 | 0 | 38904.4526 | 1 | 0 | 561 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4528 | 1 | 0 | 38904.4528 | 1 | 0 | 578 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.453 | 1 | 0 | 38904.453 | 1 | 0 | 594.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4532 | 1 | 0 | 38904.4532 | 1 | 0 | 611.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4534 | 1 | 0 | 38904.4534 | 1 | 0 | 628.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4536 | 1 | 0 | 38904.4536 | 1 | 0 | 645 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4538 | 1 | 0 | 38904.4538 | 1 | 0 | 662 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.454 | 1 | 0 | 38904.454 | 1 | 0 | 678.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4542 | 1 | 0 | 38904.4542 | 1 | 0 | 695.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4544 | 1 | 0 | 38904.4544 | 1 | 0 | 712.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4545 | 1 | 1 | 38904.4546 | 1 | 0 | 729 | 796 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 667385222.44 | 258338 | 258138.0774
38904.4547 | 1 | 0 | 38904.4548 | 1 | 0 | 746 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4549 | 1 | 0 | 38904.4549 | 1 | 0 | 762.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38904.4551 | 14 | 0 | 38904.4551 | 10 | 0 | 779.5 | 846.5 | 0.8547 | 0 | 0.6105 | 0 | 0.008547 | 0 | 0.006105 | 0 | 0.008547 | 0.006105 | 18359.8571 | 25743.8 | 18359.8486
38904.4553 | 14 | 0 | 38904.4553 | 11 | 0 | 796 | 863 | 0.8547 | 0 | 0.67155 | 0 | 0.008547 | 0 | 0.0067155 | 0 | 0.008547 | 0.0067155 | 18359.8571 | 23394.3636 | 18359.8486
38904.4555 | 15 | 0 | 38904.4555 | 12 | 0 | 813 | 880 | 0.91575 | 0 | 0.7326 | 0 | 0.0091575 | 0 | 0.007326 | 0 | 0.0091575 | 0.007326 | 17129.2 | 21436.5 | 17129.1908
38904.4557 | 15 | 0 | 38904.4557 | 11 | 0 | 830 | 897 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17129.2 | 23394.3636 | 17129.1908
38904.4559 | 15 | 0 | 38904.4559 | 11 | 0 | 846.5 | 913.5 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17129.2 | 23394.3636 | 17129.1908
38904.4561 | 15 | 0 | 38904.4561 | 11 | 0 | 863.5 | 930.5 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17129.2 | 23394.3636 | 17129.1908
38904.4563 | 15 | 0 | 38904.4563 | 11 | 0 | 880 | 947 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17129.2 | 23394.3636 | 17129.1908
38904.4565 | 15 | 0 | 38904.4565 | 11 | 0 | 897 | 964 | 0.91575 | 0 | 0.67155 | 0 | 0.0091575 | 0 | 0.0067155 | 0 | 0.0091575 | 0.0067155 | 17129.2 | 23394.3636 | 17129.1908
38904.4567 | 14 | 0 | 38904.4567 | 12 | 0 | 914 | 981 | 0.8547 | 0 | 0.7326 | 0 | 0.008547 | 0 | 0.007326 | 0 | 0.008547 | 0.007326 | 18359.8571 | 21436.5 | 18359.8486
38904.4569 | 14 | 0 | 38904.4569 | 13 | 0 | 930.5 | 997.5 | 0.8547 | 0 | 0.79365 | 0 | 0.008547 | 0 | 0.0079365 | 0 | 0.008547 | 0.0079365 | 18359.8571 | 19779.8462 | 18359.8486
38904.4571 | 14 | 0 | 38904.4571 | 14 | 0 | 947.5 | 1014.5 | 0.8547 | 0 | 0.8547 | 0 | 0.008547 | 0 | 0.008547 | 0 | 0.008547 | 0.008547 | 18359.8571 | 18359.8571 | 18359.8486
38904.4573 | 14 | 0 | 38904.4573 | 13 | 0 | 964.5 | 1031.5 | 0.8547 | 0 | 0.79365 | 0 | 0.008547 | 0 | 0.0079365 | 0 | 0.008547 | 0.0079365 | 18359.8571 | 19779.8462 | 18359.8486
38904.4575 | 14 | 0 | 38904.4575 | 13 | 0 | 981 | 1048 | 0.8547 | 0 | 0.79365 | 0 | 0.008547 | 0 | 0.0079365 | 0 | 0.008547 | 0.0079365 | 18359.8571 | 19779.8462 | 18359.8486
38904.4577 | 19 | 1 | 38904.4577 | 1199 | 1140 | 998 | 1065 | 1.16 | 0.06105 | 73.199 | 69.5971 | 0.0116 | 0.0006105 | 0.73199 | 0.69597 | 0.010989 | 0.03602 | 14281.3289 | 2715.4969 | 247329.9099
38904.4578 | 2532 | 32 | 38904.4579 | 2033 | 10 | 1014.5 | 1081.5 | 154.5788 | 1.9536 | 124.1148 | 0.6105 | 1.5458 | 0.019536 | 1.2411 | 0.006105 | 1.5263 | 1.235 | 2.1741 | 35.2762 | 16.6079
38904.458 | 2468 | 0 | 38904.4581 | 2050 | 0 | 1031.5 | 1098.5 | 150.6716 | 0 | 125.1526 | 0 | 1.5067 | 0 | 1.2515 | 0 | 1.5067 | 1.2515 | 4.7156 | 26.0673 | 3.2088
38904.4582 | 2344 | 0 | 38904.4583 | 2356 | 0 | 1048 | 1115 | 143.1013 | 0 | 143.8339 | 0 | 1.431 | 0 | 1.4383 | 0 | 1.431 | 1.4383 | 10.2551 | 9.6935 | 8.8241
38904.4584 | 2080 | 0 | 38904.4584 | 2222 | 0 | 1065 | 1132 | 126.9841 | 0 | 135.6532 | 0 | 1.2698 | 0 | 1.3565 | 0 | 1.2698 | 1.3565 | 24.249 | 16.3087 | 22.9792
38904.4586 | 2540 | 0 | 38904.4586 | 2547 | 0 | 1081.5 | 1148.5 | 155.0672 | 0 | 155.4945 | 0 | 1.5507 | 0 | 1.5549 | 0 | 1.5507 | 1.5549 | 1.7472 | 1.4676 | 0.19657
38904.4588 | 2283 | 0 | 38904.4588 | 2120 | 0 | 1098.5 | 1165.5 | 139.3773 | 0 | 129.4261 | 0 | 1.3938 | 0 | 1.2943 | 0 | 1.3938 | 1.2943 | 13.2011 | 21.9047 | 11.8073
38904.459 | 2488 | 0 | 38904.459 | 2434 | 0 | 1115.5 | 1182.5 | 151.8926 | 0 | 148.5958 | 0 | 1.5189 | 0 | 1.486 | 0 | 1.5189 | 1.486 | 3.8738 | 6.1783 | 2.3549
38904.4592 | 2337 | 0 | 38904.4592 | 2391 | 0 | 1132.5 | 1199.5 | 142.674 | 0 | 145.9707 | 0 | 1.4267 | 0 | 1.4597 | 0 | 1.4267 | 1.4597 | 10.5854 | 8.0878 | 9.1586
38904.4594 | 2283 | 0 | 38904.4594 | 2326 | 0 | 1149 | 1216 | 139.3773 | 0 | 142.0024 | 0 | 1.3938 | 0 | 1.42 | 0 | 1.3938 | 1.42 | 13.2011 | 11.1083 | 11.8073
38904.4596 | 2153 | 0 | 38904.4596 | 2568 | 0 | 1165.5 | 1232.5 | 131.4408 | 0 | 156.7766 | 0 | 1.3144 | 0 | 1.5678 | 0 | 1.3144 | 1.5678 | 20.0362 | 0.63785 | 18.7218
38904.4598 | 2065 | 0 | 38904.4598 | 2265 | 0 | 1182.5 | 1249.5 | 126.0684 | 0 | 138.2784 | 0 | 1.2607 | 0 | 1.3828 | 0 | 1.2607 | 1.3828 | 25.1516 | 14.1007 | 23.8909
38904.46 | 2219 | 0 | 38904.46 | 2219 | 7 | 1199.5 | 1266.5 | 135.4701 | 0 | 135.4701 | 0.42735 | 1.3547 | 0 | 1.3547 | 0.0042735 | 1.3547 | 1.3504 | 16.466 | 16.8345 | 15.1113
38904.4602 | 2122 | 0 | 38904.4602 | 2479 | 0 | 1216 | 1283 | 129.5482 | 0 | 151.3431 | 0 | 1.2955 | 0 | 1.5134 | 0 | 1.2955 | 1.5134 | 21.7898 | 4.2509 | 20.4943
38904.4604 | 2000 | 0 | 38904.4604 | 2343 | 0 | 1233 | 1300 | 122.1001 | 0 | 143.0403 | 0 | 1.221 | 0 | 1.4304 | 0 | 1.221 | 1.4304 | 29.219 | 10.3022 | 27.998
38904.4606 | 1967 | 0 | 38904.4606 | 2314 | 0 | 1249.5 | 1316.5 | 120.0855 | 0 | 141.2698 | 0 | 1.2009 | 0 | 1.4127 | 0 | 1.2009 | 1.4127 | 31.3869 | 11.6845 | 30.186
38904.4608 | 2309 | 0 | 38904.4608 | 2327 | 0 | 1266.5 | 1333.5 | 140.9646 | 0 | 142.0635 | 0 | 1.4096 | 0 | 1.4206 | 0 | 1.4096 | 1.4206 | 11.9264 | 11.0606 | 10.5167
38904.461 | 2124 | 0 | 38904.461 | 2311 | 0 | 1283.5 | 1350.5 | 129.6703 | 0 | 141.0867 | 0 | 1.2967 | 0 | 1.4109 | 0 | 1.2967 | 1.4109 | 21.6751 | 11.8295 | 20.3784
38904.4611 | 2160 | 0 | 38904.4612 | 2209 | 0 | 1300 | 1367 | 131.8681 | 0 | 134.8596 | 0 | 1.3187 | 0 | 1.3486 | 0 | 1.3187 | 1.3486 | 19.6472 | 16.9932 | 18.3285
38904.4613 | 1993 | 0 | 38904.4614 | 2292 | 0 | 1317 | 1384 | 121.6728 | 0 | 139.9267 | 0 | 1.2167 | 0 | 1.3993 | 0 | 1.2167 | 1.3993 | 29.6729 | 12.7565 | 28.4561
38904.4615 | 2187 | 0 | 38904.4616 | 2045 | 0 | 1333.5 | 1400.5 | 133.5165 | 0 | 124.8474 | 0 | 1.3352 | 0 | 1.2485 | 0 | 1.3352 | 1.2485 | 18.1701 | 26.3756 | 16.8349
38904.4617 | 2446 | 0 | 38904.4617 | 2416 | 0 | 1350.5 | 1417.5 | 149.3284 | 0 | 147.4969 | 0 | 1.4933 | 0 | 1.475 | 0 | 1.4933 | 1.475 | 5.6574 | 6.9694 | 4.1641
38904.4619 | 2173 | 0 | 38904.4619 | 2266 | 0 | 1367.5 | 1434.5 | 132.6618 | 0 | 138.3394 | 0 | 1.3266 | 0 | 1.3834 | 0 | 1.3266 | 1.3834 | 18.9314 | 14.0503 | 17.6048
38904.4621 | 1993 | 0 | 38904.4621 | 2308 | 0 | 1384 | 1451 | 121.6728 | 0 | 140.9035 | 0 | 1.2167 | 0 | 1.409 | 0 | 1.2167 | 1.409 | 29.6729 | 11.9749 | 28.4561

## C1-3
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 157.8987 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38904.4454 | 1 | 0 | 38904.4454 | 1 | 0 | -63 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4456 | 1 | 0 | 38904.4456 | 1 | 0 | -46.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4458 | 1 | 0 | 38904.4458 | 1 | 0 | -29.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4459 | 1 | 0 | 38904.446 | 1 | 0 | -13 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4461 | 1 | 0 | 38904.4462 | 1 | 0 | 4 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4463 | 1 | 0 | 38904.4464 | 1 | 0 | 20.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4465 | 1 | 0 | 38904.4466 | 1 | 0 | 37.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4467 | 1 | 0 | 38904.4467 | 1 | 0 | 54.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4469 | 1 | 0 | 38904.4469 | 1 | 0 | 71 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4471 | 1 | 0 | 38904.4471 | 1 | 0 | 88 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4473 | 1 | 0 | 38904.4473 | 1 | 0 | 104.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4475 | 1 | 0 | 38904.4475 | 1 | 0 | 121.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4477 | 1 | 0 | 38904.4477 | 1 | 0 | 138.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4479 | 1 | 0 | 38904.4479 | 1 | 0 | 155 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4481 | 1 | 0 | 38904.4481 | 1 | 0 | 172 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4483 | 1 | 0 | 38904.4483 | 1 | 0 | 188.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4485 | 1 | 0 | 38904.4485 | 1 | 0 | 205.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4487 | 1 | 0 | 38904.4487 | 1 | 0 | 222.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4489 | 1 | 0 | 38904.4489 | 1 | 0 | 239 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4491 | 1 | 0 | 38904.4491 | 1 | 0 | 256 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4493 | 1 | 0 | 38904.4493 | 1 | 0 | 272.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4495 | 1 | 0 | 38904.4495 | 1 | 0 | 289.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4497 | 1 | 0 | 38904.4497 | 1 | 0 | 306.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4498 | 1 | 0 | 38904.4499 | 1 | 0 | 323 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.45 | 1 | 0 | 38904.4501 | 1 | 0 | 340 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4502 | 1 | 0 | 38904.4502 | 1 | 0 | 356.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4504 | 1 | 0 | 38904.4504 | 1 | 0 | 373.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4506 | 1 | 0 | 38904.4506 | 1 | 0 | 390.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4508 | 1 | 0 | 38904.4508 | 1 | 0 | 407 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.451 | 1 | 0 | 38904.451 | 1 | 0 | 424 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4512 | 1 | 0 | 38904.4512 | 1 | 0 | 440.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4514 | 1 | 0 | 38904.4514 | 1 | 0 | 457.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4516 | 1 | 0 | 38904.4516 | 1 | 0 | 474.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4518 | 1 | 1 | 38904.4518 | 1 | 0 | 491 | 558 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 668418974.44 | 258538 | 258338.0773
38904.452 | 1 | 0 | 38904.452 | 1 | 0 | 508 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4522 | 1 | 0 | 38904.4522 | 1 | 0 | 524.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4524 | 1 | 0 | 38904.4524 | 1 | 0 | 541.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4526 | 1 | 0 | 38904.4526 | 1 | 0 | 558.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4528 | 1 | 0 | 38904.4528 | 1 | 0 | 575 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.453 | 1 | 0 | 38904.453 | 1 | 0 | 592 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4531 | 1 | 0 | 38904.4532 | 1 | 0 | 608.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4533 | 1 | 0 | 38904.4534 | 1 | 0 | 625.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4535 | 1 | 0 | 38904.4536 | 1 | 0 | 642.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4537 | 1 | 0 | 38904.4538 | 1 | 0 | 659 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4539 | 1 | 0 | 38904.4539 | 1 | 0 | 675.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4541 | 1 | 0 | 38904.4541 | 1 | 0 | 692.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4543 | 1 | 0 | 38904.4543 | 1 | 0 | 709.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4545 | 1 | 0 | 38904.4545 | 1 | 0 | 726.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4547 | 1 | 0 | 38904.4547 | 1 | 0 | 743 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4549 | 1 | 0 | 38904.4549 | 1 | 0 | 760 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
38904.4551 | 4 | 0 | 38904.4551 | 2263 | 0 | 776.5 | 843.5 | 0.2442 | 0 | 138.1563 | 0 | 0.002442 | 0 | 1.3816 | 0 | 0.002442 | 1.3816 | 64559.5 | 14.2899 | 64559.4976
38904.4553 | 7 | 0 | 38904.4553 | 2024 | 0 | 793.5 | 860.5 | 0.42735 | 0 | 123.5653 | 0 | 0.0042735 | 0 | 1.2357 | 0 | 0.0042735 | 1.2357 | 36848.2857 | 27.7856 | 36848.2814
38904.4555 | 7 | 0 | 38904.4555 | 2014 | 0 | 810 | 877 | 0.42735 | 0 | 122.9548 | 0 | 0.0042735 | 0 | 1.2295 | 0 | 0.0042735 | 1.2295 | 36848.2857 | 28.4201 | 36848.2814
38904.4557 | 7 | 0 | 38904.4557 | 2035 | 0 | 827 | 894 | 0.42735 | 0 | 124.2369 | 0 | 0.0042735 | 0 | 1.2424 | 0 | 0.0042735 | 1.2424 | 36848.2857 | 27.0948 | 36848.2814
38904.4559 | 7 | 0 | 38904.4559 | 2528 | 0 | 844 | 911 | 0.42735 | 0 | 154.3346 | 0 | 0.0042735 | 0 | 1.5433 | 0 | 0.0042735 | 1.5433 | 36848.2857 | 2.3093 | 36848.2814
38904.4561 | 7 | 0 | 38904.4561 | 2395 | 0 | 860.5 | 927.5 | 0.42735 | 0 | 146.2149 | 0 | 0.0042735 | 0 | 1.4621 | 0 | 0.0042735 | 1.4621 | 36848.2857 | 7.9908 | 36848.2814
38904.4563 | 8 | 0 | 38904.4563 | 2510 | 0 | 877.5 | 944.5 | 0.4884 | 0 | 153.2357 | 0 | 0.004884 | 0 | 1.5324 | 0 | 0.004884 | 1.5324 | 32229.75 | 3.043 | 32229.7451
38904.4565 | 7 | 0 | 38904.4565 | 2120 | 0 | 894.5 | 961.5 | 0.42735 | 0 | 129.4261 | 0 | 0.0042735 | 0 | 1.2943 | 0 | 0.0042735 | 1.2943 | 36848.2857 | 21.9991 | 36848.2814
38904.4566 | 8 | 0 | 38904.4567 | 2420 | 0 | 911 | 978 | 0.4884 | 0 | 147.7411 | 0 | 0.004884 | 0 | 1.4774 | 0 | 0.004884 | 1.4774 | 32229.75 | 6.8752 | 32229.7451
38904.4568 | 14 | 0 | 38904.4569 | 2444 | 0 | 927.5 | 994.5 | 0.8547 | 0 | 149.2063 | 0 | 0.008547 | 0 | 1.4921 | 0 | 0.008547 | 1.4921 | 18374.1429 | 5.8257 | 18374.1343
38904.457 | 14 | 0 | 38904.457 | 2066 | 0 | 944.5 | 1011.5 | 0.8547 | 0 | 126.1294 | 0 | 0.008547 | 0 | 1.2613 | 0 | 0.008547 | 1.2613 | 18374.1429 | 25.1878 | 18374.1343
38904.4572 | 13 | 0 | 38904.4572 | 2089 | 0 | 961.5 | 1028.5 | 0.79365 | 0 | 127.5336 | 0 | 0.0079365 | 0 | 1.2753 | 0 | 0.0079365 | 1.2753 | 19795.2308 | 23.8095 | 19795.2228
38904.4574 | 14 | 0 | 38904.4574 | 2546 | 0 | 978.5 | 1045.5 | 0.8547 | 0 | 155.4335 | 0 | 0.008547 | 0 | 1.5543 | 0 | 0.008547 | 1.5543 | 18374.1429 | 1.586 | 18374.1343
38904.4576 | 13 | 0 | 38904.4576 | 2513 | 0 | 995 | 1062 | 0.79365 | 0 | 153.4188 | 0 | 0.0079365 | 0 | 1.5342 | 0 | 0.0079365 | 1.5342 | 19795.2308 | 2.92 | 19795.2228
38904.4578 | 38 | 0 | 38904.4578 | 2331 | 0 | 1011.5 | 1078.5 | 2.3199 | 0 | 142.3077 | 0 | 0.023199 | 0 | 1.4231 | 0 | 0.023199 | 1.4231 | 6706.2632 | 10.9558 | 6706.24
38904.458 | 2432 | 0 | 38904.458 | 1948 | 0 | 1028.5 | 1095.5 | 148.4737 | 0 | 118.9255 | 0 | 1.4847 | 0 | 1.1893 | 0 | 1.4847 | 1.1893 | 6.3479 | 32.771 | 4.8631
38904.4582 | 2320 | 0 | 38904.4582 | 1950 | 0 | 1045.5 | 1112.5 | 141.6361 | 0 | 119.0476 | 0 | 1.4164 | 0 | 1.1905 | 0 | 1.4164 | 1.1905 | 11.4819 | 32.6349 | 10.0655
38904.4584 | 2426 | 0 | 38904.4584 | 2230 | 0 | 1062 | 1129 | 148.1074 | 0 | 136.1416 | 0 | 1.4811 | 0 | 1.3614 | 0 | 1.4811 | 1.3614 | 6.6109 | 15.9812 | 5.1298
38904.4586 | 2272 | 0 | 38904.4586 | 2297 | 0 | 1079 | 1146 | 138.7057 | 0 | 140.232 | 0 | 1.3871 | 0 | 1.4023 | 0 | 1.3871 | 1.4023 | 13.8371 | 12.5982 | 12.4501
38904.4588 | 2499 | 0 | 38904.4588 | 2127 | 0 | 1096 | 1163 | 152.5641 | 0 | 129.8535 | 0 | 1.5256 | 0 | 1.2985 | 0 | 1.5256 | 1.2985 | 3.4966 | 21.5976 | 1.971
38904.459 | 2441 | 0 | 38904.459 | 2140 | 0 | 1112.5 | 1179.5 | 149.0232 | 0 | 130.6471 | 0 | 1.4902 | 0 | 1.3065 | 0 | 1.4902 | 1.3065 | 5.9558 | 20.8589 | 4.4655
38904.4592 | 2392 | 0 | 38904.4592 | 2564 | 0 | 1129.5 | 1196.5 | 146.0317 | 0 | 156.5324 | 0 | 1.4603 | 0 | 1.5653 | 0 | 1.4603 | 1.5653 | 8.1263 | 0.87285 | 6.6659
38904.4594 | 2491 | 0 | 38904.4594 | 2230 | 0 | 1146.5 | 1213.5 | 152.0757 | 0 | 136.1416 | 0 | 1.5208 | 0 | 1.3614 | 0 | 1.5208 | 1.3614 | 3.829 | 15.9812 | 2.3082
38904.4596 | 2163 | 0 | 38904.4596 | 2002 | 0 | 1163 | 1230 | 132.0513 | 0 | 122.2222 | 0 | 1.3205 | 0 | 1.2222 | 0 | 1.3205 | 1.2222 | 19.5737 | 29.1898 | 18.2532
38904.4598 | 2514 | 0 | 38904.4598 | 1974 | 0 | 1179.5 | 1246.5 | 153.4799 | 0 | 120.5128 | 0 | 1.5348 | 0 | 1.2051 | 0 | 1.5348 | 1.2051 | 2.8791 | 31.0223 | 1.3443
38904.46 | 2070 | 0 | 38904.46 | 2549 | 0 | 1196.5 | 1263.5 | 126.3736 | 0 | 155.6166 | 0 | 1.2637 | 0 | 1.5562 | 0 | 1.2637 | 1.5562 | 24.9459 | 1.4665 | 23.6822
38904.4602 | 2398 | 0 | 38904.4602 | 2118 | 0 | 1213.5 | 1280.5 | 146.398 | 0 | 129.304 | 0 | 1.464 | 0 | 1.293 | 0 | 1.464 | 1.293 | 7.8557 | 22.1143 | 6.3917
38904.4603 | 2559 | 0 | 38904.4604 | 2035 | 0 | 1230 | 1297 | 156.2271 | 0 | 124.2369 | 0 | 1.5623 | 0 | 1.2424 | 0 | 1.5623 | 1.2424 | 1.0699 | 27.0948 | 0.49232
38904.4605 | 2234 | 0 | 38904.4606 | 2372 | 0 | 1247 | 1314 | 136.3858 | 0 | 144.8107 | 0 | 1.3639 | 0 | 1.4481 | 0 | 1.3639 | 1.4481 | 15.7735 | 9.0379 | 14.4096
38904.4607 | 2150 | 0 |  | 2265 | 0 | 1263 | 1330 | 131.2576 | 0 | 138.2784 | 0 | 1.3126 | 0 | 1.3828 | 0 | 1.3126 | 1.3828 | 20.2967 | 14.189 | 18.9842
38904.4609 | 2341 | 0 | 38904.4609 | 2158 | 0 | 1280.5 | 1347.5 | 142.9182 | 0 | 131.746 | 0 | 1.4292 | 0 | 1.3175 | 0 | 1.4292 | 1.3175 | 10.4818 | 19.8508 | 9.0527
38904.4611 | 2561 | 0 | 38904.4611 | 2326 | 0 | 1297.5 | 1364.5 | 156.3492 | 0 | 142.0024 | 0 | 1.5635 | 0 | 1.42 | 0 | 1.5635 | 1.42 | 0.99102 | 11.1943 | 0.57247
38904.4613 | 2296 | 0 | 38904.4613 | 2410 | 0 | 1314 | 1381 | 140.1709 | 0 | 147.1306 | 0 | 1.4017 | 0 | 1.4713 | 0 | 1.4017 | 1.4713 | 12.6472 | 7.3187 | 11.2455
38904.4615 | 2461 | 0 | 38904.4615 | 2015 | 0 | 1331 | 1398 | 150.2442 | 0 | 123.0159 | 0 | 1.5024 | 0 | 1.2302 | 0 | 1.5024 | 1.2302 | 5.0947 | 28.3563 | 3.5922
38904.4617 | 2570 | 0 | 38904.4617 | 2568 | 0 | 1347.5 | 1414.5 | 156.8987 | 0 | 156.7766 | 0 | 1.569 | 0 | 1.5678 | 0 | 1.569 | 1.5678 | 0.63735 | 0.71573 | 0.93163
38904.4619 | 2144 | 0 | 38904.4619 | 2032 | 0 | 1364.5 | 1431.5 | 130.8913 | 0 | 124.0537 | 0 | 1.3089 | 0 | 1.2405 | 0 | 1.3089 | 1.2405 | 20.6334 | 27.2825 | 19.3245
38904.4621 | 2401 | 0 | 38904.4621 | 2171 | 0 | 1381.5 | 1448.5 | 146.5812 | 0 | 132.5397 | 0 | 1.4658 | 0 | 1.3254 | 0 | 1.4658 | 1.3254 | 7.7209 | 19.1331 | 6.2551

## C1-2
Penlight Test 5 |  |  | 2006-07-06 | 10:42 |  | Vs = |  | 157.5324 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38904.4453 | 2 | 0 | 38904.4454 | 1 | 0 | -66 | 1 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128919 | 257938 | 128918.9988
38904.4455 | 1 | 1 | 38904.4455 | 1 | 0 | -49.5 | 17.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 665320118.44 | 257938 | 257738.0775
38904.4457 | 1 | 0 | 38904.4457 | 1 | 0 | -32.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4459 | 1 | 0 | 38904.4459 | 1 | 0 | -15.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4461 | 1 | 0 | 38904.4461 | 1 | 0 | 1 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4463 | 1 | 0 | 38904.4463 | 1 | 0 | 18 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4465 | 1 | 0 | 38904.4465 | 1 | 0 | 34.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4467 | 2 | 0 | 38904.4467 | 2 | 0 | 51.5 | 118.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128919 | 128919 | 128918.9988
38904.4469 | 1 | 0 | 38904.4469 | 1 | 0 | 68.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4471 | 1 | 0 | 38904.4471 | 1 | 0 | 85 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4473 | 1 | 0 | 38904.4473 | 1 | 0 | 102 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4475 | 1 | 0 | 38904.4475 | 1 | 0 | 118.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4477 | 1 | 0 | 38904.4477 | 1 | 0 | 135.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4479 | 1 | 0 | 38904.4479 | 1 | 0 | 152.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4481 | 1 | 0 | 38904.4481 | 1 | 0 | 169 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4483 | 1 | 0 | 38904.4483 | 1 | 0 | 186 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4484 | 1 | 0 | 38904.4485 | 1 | 0 | 202.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4486 | 1 | 0 | 38904.4487 | 1 | 0 | 219.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4488 | 1 | 0 | 38904.4489 | 1 | 0 | 236.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.449 | 1 | 0 | 38904.4491 | 1 | 0 | 253 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4492 | 1 | 0 | 38904.4492 | 1 | 0 | 270 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4494 | 1 | 0 | 38904.4494 | 1 | 0 | 286.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4496 | 1 | 0 | 38904.4496 | 1 | 0 | 303.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4498 | 1 | 0 | 38904.4498 | 1 | 0 | 320.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.45 | 1 | 0 | 38904.45 | 1 | 0 | 337 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4502 | 1 | 0 | 38904.4502 | 1 | 0 | 354 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4504 | 1 | 0 | 38904.4504 | 1 | 0 | 370.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4506 | 1 | 0 | 38904.4506 | 1 | 0 | 387.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4508 | 1 | 0 | 38904.4508 | 1 | 0 | 404.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.451 | 1 | 0 | 38904.451 | 1 | 0 | 421 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4512 | 1 | 0 | 38904.4512 | 1 | 0 | 438 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4514 | 1 | 0 | 38904.4514 | 1 | 0 | 454.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4516 | 1 | 0 | 38904.4516 | 1 | 0 | 471.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4518 | 1 | 0 | 38904.4518 | 1 | 0 | 488.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4519 | 1 | 0 | 38904.452 | 1 | 0 | 505 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4521 | 1 | 0 | 38904.4522 | 1 | 0 | 522 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4523 | 1 | 0 | 38904.4523 | 1 | 0 | 538.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4525 | 1 | 0 | 38904.4525 | 1 | 0 | 555.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4527 | 1 | 0 | 38904.4527 | 1 | 0 | 572.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4529 | 1 | 0 | 38904.4529 | 1 | 0 | 589 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4531 | 1 | 0 | 38904.4531 | 1 | 0 | 605.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4533 | 1 | 0 | 38904.4533 | 1 | 0 | 622.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4535 | 1 | 0 | 38904.4535 | 1 | 0 | 639.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4537 | 1 | 0 | 38904.4537 | 1 | 0 | 656.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4539 | 1 | 0 | 38904.4539 | 1 | 0 | 673 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4541 | 1 | 0 | 38904.4541 | 1 | 0 | 690 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4543 | 1 | 0 | 38904.4543 | 1 | 0 | 706.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4545 | 1 | 0 | 38904.4545 | 1 | 0 | 723.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4547 | 1 | 0 | 38904.4547 | 1 | 0 | 740.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4549 | 1 | 0 | 38904.4549 | 1 | 0 | 757 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38904.4551 | 10 | 0 | 38904.4551 | 6 | 0 | 774 | 841 | 0.6105 | 0 | 0.3663 | 0 | 0.006105 | 0 | 0.003663 | 0 | 0.006105 | 0.003663 | 25703.8 | 42906.3333 | 25703.7939
38904.4553 | 11 | 0 | 38904.4553 | 10 | 0 | 790.5 | 857.5 | 0.67155 | 0 | 0.6105 | 0 | 0.0067155 | 0 | 0.006105 | 0 | 0.0067155 | 0.006105 | 23358 | 25703.8 | 23357.9933
38904.4555 | 12 | 0 | 38904.4555 | 10 | 0 | 807.5 | 874.5 | 0.7326 | 0 | 0.6105 | 0 | 0.007326 | 0 | 0.006105 | 0 | 0.007326 | 0.006105 | 21403.1667 | 25703.8 | 21403.1593
38904.4556 | 11 | 0 | 38904.4557 | 10 | 0 | 824.5 | 891.5 | 0.67155 | 0 | 0.6105 | 0 | 0.0067155 | 0 | 0.006105 | 0 | 0.0067155 | 0.006105 | 23358 | 25703.8 | 23357.9933
38904.4558 | 12 | 0 | 38904.4559 | 10 | 0 | 841 | 908 | 0.7326 | 0 | 0.6105 | 0 | 0.007326 | 0 | 0.006105 | 0 | 0.007326 | 0.006105 | 21403.1667 | 25703.8 | 21403.1593
38904.456 | 12 | 0 | 38904.4561 | 9 | 0 | 858 | 925 | 0.7326 | 0 | 0.54945 | 0 | 0.007326 | 0 | 0.0054945 | 0 | 0.007326 | 0.0054945 | 21403.1667 | 28570.8889 | 21403.1593
38904.4562 | 12 | 0 | 38904.4562 | 10 | 0 | 874.5 | 941.5 | 0.7326 | 0 | 0.6105 | 0 | 0.007326 | 0 | 0.006105 | 0 | 0.007326 | 0.006105 | 21403.1667 | 25703.8 | 21403.1593
38904.4564 | 12 | 0 | 38904.4564 | 513 | 0 | 891.5 | 958.5 | 0.7326 | 0 | 31.3187 | 0 | 0.007326 | 0 | 0.31319 | 0 | 0.007326 | 0.31319 | 21403.1667 | 402.9981 | 21403.1593
38904.4566 | 12 | 0 | 38904.4566 | 1523 | 7 | 908.5 | 975.5 | 0.7326 | 0 | 92.9792 | 0.42735 | 0.007326 | 0 | 0.92979 | 0.0042735 | 0.007326 | 0.92552 | 21403.1667 | 70.2098 | 21403.1593
38904.4568 | 14 | 0 | 38904.4568 | 1946 | 0 | 925 | 992 | 0.8547 | 0 | 118.8034 | 0 | 0.008547 | 0 | 1.188 | 0 | 0.008547 | 1.188 | 18331.2857 | 32.5992 | 18331.2772
38904.457 | 14 | 0 | 38904.457 | 2368 | 0 | 941.5 | 1008.5 | 0.8547 | 0 | 144.5665 | 0 | 0.008547 | 0 | 1.4457 | 0 | 0.008547 | 1.4457 | 18331.2857 | 8.9688 | 18331.2772
38904.4572 | 14 | 0 | 38904.4572 | 2131 | 0 | 958.5 | 1025.5 | 0.8547 | 0 | 130.0977 | 0 | 0.008547 | 0 | 1.301 | 0 | 0.008547 | 1.301 | 18331.2857 | 21.0878 | 18331.2772
38904.4574 | 13 | 0 | 38904.4574 | 2302 | 0 | 975.5 | 1042.5 | 0.79365 | 0 | 140.5372 | 0 | 0.0079365 | 0 | 1.4054 | 0 | 0.0079365 | 1.4054 | 19749.0769 | 12.093 | 19749.069
38904.4576 | 13 | 0 | 38904.4576 | 2524 | 0 | 992 | 1059 | 0.79365 | 0 | 154.0904 | 0 | 0.0079365 | 0 | 1.5409 | 0 | 0.0079365 | 1.5409 | 19749.0769 | 2.2338 | 19749.069
38904.4578 | 13 | 0 | 38904.4578 | 2142 | 0 | 1009 | 1076 | 0.79365 | 0 | 130.7692 | 0 | 0.0079365 | 0 | 1.3077 | 0 | 0.0079365 | 1.3077 | 19749.0769 | 20.4659 | 19749.069
38904.458 | 2393 | 1 | 38904.458 | 2539 | 1 | 1026 | 1093 | 146.0928 | 0.06105 | 155.0061 | 0.06105 | 1.4609 | 0.0006105 | 1.5501 | 0.0006105 | 1.4603 | 1.5495 | 8.0387 | 1.6384 | 300.4513
38904.4582 | 2535 | 0 | 38904.4582 | 2246 | 0 | 1042.5 | 1109.5 | 154.7619 | 0 | 137.1184 | 0 | 1.5476 | 0 | 1.3712 | 0 | 1.5476 | 1.3712 | 1.7901 | 14.8878 | 0.24252
38904.4584 | 2305 | 0 | 38904.4584 | 2482 | 0 | 1059.5 | 1126.5 | 140.7204 | 0 | 151.5263 | 0 | 1.4072 | 0 | 1.5153 | 0 | 1.4072 | 1.5153 | 11.9471 | 3.9637 | 10.5399
38904.4586 | 2088 | 0 | 38904.4586 | 2386 | 0 | 1076.5 | 1143.5 | 127.4725 | 0 | 145.6654 | 0 | 1.2747 | 0 | 1.4567 | 0 | 1.2747 | 1.4567 | 23.5814 | 8.1467 | 22.3067
38904.4587 | 2359 | 0 | 38904.4588 | 1963 | 0 | 1093 | 1160 | 144.0171 | 0 | 119.8413 | 0 | 1.4402 | 0 | 1.1984 | 0 | 1.4402 | 1.1984 | 9.3845 | 31.4508 | 7.9443
38904.4589 | 2221 | 0 | 38904.459 | 2384 | 0 | 1109.5 | 1176.5 | 135.5922 | 0 | 145.5433 | 0 | 1.3559 | 0 | 1.4554 | 0 | 1.3559 | 1.4554 | 16.181 | 8.2374 | 14.8251
38904.4591 | 2232 | 0 | 38904.4592 | 2497 | 0 | 1126.5 | 1193.5 | 136.2637 | 0 | 152.442 | 0 | 1.3626 | 0 | 1.5244 | 0 | 1.3626 | 1.5244 | 15.6084 | 3.3392 | 14.2458
38904.4593 | 2168 | 0 | 38904.4594 | 1991 | 0 | 1143.5 | 1210.5 | 132.3565 | 0 | 121.5507 | 0 | 1.3236 | 0 | 1.2155 | 0 | 1.3236 | 1.2155 | 19.0212 | 29.6022 | 17.6977
38904.4595 | 2548 | 0 | 38904.4595 | 2188 | 0 | 1160 | 1227 | 155.5556 | 0 | 133.5775 | 0 | 1.5556 | 0 | 1.3358 | 0 | 1.5556 | 1.3358 | 1.2708 | 17.9333 | 0.28475
38904.4597 | 2384 | 0 | 38904.4597 | 2564 | 0 | 1177 | 1244 | 145.5433 | 0 | 156.5324 | 0 | 1.4554 | 0 | 1.5653 | 0 | 1.4554 | 1.5653 | 8.2374 | 0.63885 | 6.782
38904.4599 | 2115 | 0 | 38904.4599 | 2358 | 0 | 1193.5 | 1260.5 | 129.1209 | 0 | 143.956 | 0 | 1.2912 | 0 | 1.4396 | 0 | 1.2912 | 1.4396 | 22.0038 | 9.4309 | 20.7126
38904.4601 | 2015 | 0 | 38904.4601 | 2519 | 0 | 1210.5 | 1277.5 | 123.0159 | 0 | 153.7851 | 0 | 1.2302 | 0 | 1.5379 | 0 | 1.2302 | 1.5379 | 28.0586 | 2.4367 | 26.8284
38904.4603 | 2170 | 0 | 38904.4603 | 2443 | 0 | 1227.5 | 1294.5 | 132.4786 | 0 | 149.1453 | 0 | 1.3248 | 0 | 1.4915 | 0 | 1.3248 | 1.4915 | 18.9115 | 5.6234 | 17.5867
38904.4605 | 2194 | 0 | 38904.4605 | 2472 | 0 | 1244 | 1311 | 133.9438 | 0 | 150.9158 | 0 | 1.3394 | 0 | 1.5092 | 0 | 1.3394 | 1.5092 | 17.6108 | 4.3843 | 16.2713
38904.4607 | 2318 | 0 | 38904.4607 | 2172 | 0 | 1261 | 1328 | 141.514 | 0 | 132.6007 | 0 | 1.4151 | 0 | 1.326 | 0 | 1.4151 | 1.326 | 11.3192 | 18.802 | 9.9041
38904.4609 | 2195 | 0 | 38904.4609 | 2098 | 0 | 1277.5 | 1344.5 | 134.0049 | 0 | 128.083 | 0 | 1.34 | 0 | 1.2808 | 0 | 1.34 | 1.2808 | 17.5572 | 22.9924 | 16.2171
38904.4611 | 2344 | 0 | 38904.4611 | 2452 | 0 | 1294.5 | 1361.5 | 143.1013 | 0 | 149.6947 | 0 | 1.431 | 0 | 1.4969 | 0 | 1.431 | 1.4969 | 10.0845 | 5.2357 | 8.6535
38904.4613 | 2486 | 0 | 38904.4613 | 2183 | 0 | 1311.5 | 1378.5 | 151.7705 | 0 | 133.2723 | 0 | 1.5177 | 0 | 1.3327 | 0 | 1.5177 | 1.3327 | 3.7965 | 18.2034 | 2.2788
38904.4615 | 2123 | 0 | 38904.4615 | 2451 | 0 | 1328 | 1395 | 129.6093 | 0 | 149.6337 | 0 | 1.2961 | 0 | 1.4963 | 0 | 1.2961 | 1.4963 | 21.544 | 5.2787 | 20.2479
38904.4617 | 1970 | 0 | 38904.4617 | 2378 | 0 | 1345 | 1412 | 120.2686 | 0 | 145.177 | 0 | 1.2027 | 0 | 1.4518 | 0 | 1.2027 | 1.4518 | 30.9838 | 8.5105 | 29.7811
38904.4619 | 2131 | 0 | 38904.4619 | 2331 | 0 | 1361.5 | 1428.5 | 130.0977 | 0 | 142.3077 | 0 | 1.301 | 0 | 1.4231 | 0 | 1.301 | 1.4231 | 21.0878 | 10.6984 | 19.7868
38904.4621 | 2447 | 0 | 38904.4621 | 2249 | 0 | 1378.5 | 1445.5 | 149.3895 | 0 | 137.3016 | 0 | 1.4939 | 0 | 1.373 | 0 | 1.4939 | 1.373 | 5.4508 | 14.7345 | 3.9569

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 5 |  |  | 2006-07-06 | 10:42
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-63.1667 | 215265 |  | -59.5 | 258038 | -57.5 | 258338 | -55.8333 | 258504.6667 | -63.1667 | 215265
-46.5 | 221945664.8133 |  | -42.8333 | 258038 | -41 | 258338 | -39 | 258504.6667 | -46.5 | 258038
-29.6667 | 258271.3333 |  | -26 | 258038 | -24 | 258338 | -22.3333 | 258504.6667 | -29.6667 | 258038
-12.8333 | 258271.3333 |  | -9.1667 | 258038 | -7.3333 | 258338 | -5.3333 | 258504.6667 | -12.8333 | 258038
3.8333 | 258271.3333 |  | 7.6667 | 258038 | 9.5 | 258338 | 11.3333 | 258504.6667 | 3.8333 | 258038
20.6667 | 258271.3333 |  | 24.5 | 258038 | 26.3333 | 258338 | 28.1667 | 258504.6667 | 20.6667 | 258038
37.5 | 258271.3333 |  | 41.1667 | 258038 | 43 | 215198.3333 | 45 | 215415 | 37.5 | 215198.3333
54.3333 | 215265 |  | 58 | 215031.6667 | 60 | 258338 | 61.6667 | 258504.6667 | 54.3333 | 215031.6667
71.1667 | 258271.3333 |  | 74.8333 | 258038 | 76.6667 | 258338 | 78.6667 | 258504.6667 | 71.1667 | 258038
87.8333 | 258271.3333 |  | 91.6667 | 258038 | 93.5 | 258338 | 95.3333 | 258504.6667 | 87.8333 | 258038
104.6667 | 258271.3333 |  | 108.5 | 258038 | 110.3333 | 258338 | 112.1667 | 258504.6667 | 104.6667 | 258038
121.5 | 258271.3333 |  | 125.1667 | 258038 | 127 | 258338 | 129 | 258504.6667 | 121.5 | 258038
138.3333 | 258271.3333 |  | 142 | 258038 | 144 | 258338 | 145.6667 | 258504.6667 | 138.3333 | 258038
155.1667 | 258271.3333 |  | 158.8333 | 258038 | 160.6667 | 258338 | 162.6667 | 258504.6667 | 155.1667 | 258038
171.8333 | 258271.3333 |  | 175.6667 | 258038 | 177.5 | 258338 | 179.3333 | 258504.6667 | 171.8333 | 258038
188.6667 | 258271.3333 |  | 192.5 | 258038 | 194.3333 | 258338 | 196.1667 | 258504.6667 | 188.6667 | 258038
205.5 | 258271.3333 |  | 209.1667 | 258038 | 211 | 258338 | 213 | 258504.6667 | 205.5 | 258038
222.3333 | 258271.3333 |  | 226 | 258038 | 228 | 258338 | 229.6667 | 258504.6667 | 222.3333 | 258038
239.1667 | 258271.3333 |  | 242.8333 | 258038 | 244.6667 | 258338 | 246.6667 | 258504.6667 | 239.1667 | 258038
255.8333 | 258271.3333 |  | 259.6667 | 258038 | 261.5 | 258338 | 263.3333 | 258504.6667 | 255.8333 | 258038
272.6667 | 258271.3333 |  | 276.5 | 258038 | 278.3333 | 258338 | 280.1667 | 258504.6667 | 272.6667 | 258038
289.5 | 258271.3333 |  | 293.1667 | 258038 | 295 | 258338 | 297 | 258504.6667 | 289.5 | 258038
306.3333 | 258271.3333 |  | 310 | 258038 | 312 | 258338 | 313.6667 | 258504.6667 | 306.3333 | 258038
323.1667 | 258271.3333 |  | 326.8333 | 258038 | 328.6667 | 258338 | 330.6667 | 258504.6667 | 323.1667 | 258038
339.8333 | 258271.3333 |  | 343.6667 | 258038 | 345.5 | 258338 | 347.3333 | 258504.6667 | 339.8333 | 258038
356.6667 | 258271.3333 |  | 360.6667 | 258038 | 362.3333 | 258338 | 364.3333 | 258504.6667 | 356.6667 | 258038
373.5 | 258271.3333 |  | 377.1667 | 258038 | 379 | 258338 | 381 | 258504.6667 | 373.5 | 258038
390.3333 | 258271.3333 |  | 394 | 258038 | 396 | 258338 | 397.6667 | 258504.6667 | 390.3333 | 258038
407.1667 | 258271.3333 |  | 410.8333 | 258038 | 412.6667 | 258338 | 414.6667 | 258504.6667 | 407.1667 | 258038
423.8333 | 258271.3333 |  | 427.6667 | 258038 | 429.5 | 258338 | 431.3333 | 258504.6667 | 423.8333 | 258038
440.6667 | 258271.3333 |  | 444.5 | 258038 | 446.3333 | 258338 | 448.1667 | 258504.6667 | 440.6667 | 258038
457.5 | 258271.3333 |  | 461.1667 | 258038 | 463 | 258338 | 465 | 258504.6667 | 457.5 | 258038
474.3333 | 258271.3333 |  | 478 | 258038 | 480 | 258338 | 481.6667 | 258504.6667 | 474.3333 | 258038
491.1667 | 222978416.8133 |  | 494.8333 | 258038 | 496.6667 | 258338 | 498.6667 | 258504.6667 | 491.1667 | 258038
507.8333 | 258271.3333 |  | 511.5 | 258038 | 513.5 | 258338 | 515.1667 | 258504.6667 | 507.8333 | 258038
524.6667 | 258271.3333 |  | 528.5 | 258038 | 530.3333 | 258338 | 532.1667 | 258504.6667 | 524.6667 | 258038
541.5 | 258271.3333 |  | 545.1667 | 258038 | 547 | 258338 | 549 | 258504.6667 | 541.5 | 258038
558.3333 | 258271.3333 |  | 562 | 258038 | 564 | 258338 | 565.6667 | 258504.6667 | 558.3333 | 258038
575.1667 | 258271.3333 |  | 578.8333 | 258038 | 580.5 | 258338 | 582.5 | 258504.6667 | 575.1667 | 258038
591.8333 | 258271.3333 |  | 595.6667 | 258038 | 597.5 | 258338 | 599.3333 | 258504.6667 | 591.8333 | 258038
608.5 | 258271.3333 |  | 612.3333 | 258038 | 614.3333 | 258338 | 616.1667 | 258504.6667 | 608.5 | 258038
625.5 | 258271.3333 |  | 629.1667 | 258038 | 631 | 215198.3333 | 633 | 258504.6667 | 625.5 | 215198.3333
642.3333 | 258271.3333 |  | 646 | 258038 | 648 | 258338 | 649.6667 | 258504.6667 | 642.3333 | 258038
659.1667 | 258271.3333 |  | 662.8333 | 258038 | 664.6667 | 258338 | 666.6667 | 258504.6667 | 659.1667 | 258038
675.6667 | 258271.3333 |  | 679.6667 | 258038 | 681.3333 | 258338 | 683.3333 | 258504.6667 | 675.6667 | 258038
692.6667 | 258271.3333 |  | 696.3333 | 258038 | 698.1667 | 258338 | 700.1667 | 258504.6667 | 692.6667 | 258038
709.5 | 258271.3333 |  | 713.1667 | 258038 | 715 | 258338 | 717 | 258504.6667 | 709.5 | 258038
726.3333 | 222633899.48 |  | 730 | 258038 | 732 | 258338 | 733.6667 | 258504.6667 | 726.3333 | 258038
743.1667 | 258271.3333 |  | 746.8333 | 258038 | 748.5 | 258338 | 750.5 | 258504.6667 | 743.1667 | 258038
759.8333 | 258271.3333 |  | 763.6667 | 193403.5 | 765.5 | 87402.3034 | 767.3333 | 135772.5385 | 759.8333 | 87402.3034
776.6667 | 36207.719 |  | 780.6667 | 34715.4444 | 782.3333 | 16.0485 | 784.3333 | 22101.0404 | 776.6667 | 16.0485
793.3333 | 26188.7143 |  | 797.1667 | 24989.8056 | 799 | 17.0146 | 800.8333 | 21317.8949 | 793.3333 | 17.0146
810.1667 | 25126.8841 |  | 813.8333 | 23796.1111 | 815.6667 | 13.4012 | 817.6667 | 20665.2737 | 810.1667 | 13.4012
827.1667 | 25778.4952 |  | 830.8333 | 24989.8056 | 832.5 | 18.8332 | 834.5 | 22101.3434 | 827.1667 | 18.8332
843.8333 | 25126.8841 |  | 847.5 | 24989.8056 | 849.5 | 13.7368 | 851.1667 | 21317.8949 | 843.8333 | 13.7368
860.6667 | 25126.8841 |  | 864.3333 | 25945.5019 | 866.1667 | 11.7139 | 868.1667 | 21728.7489 | 860.6667 | 11.7139
877.3333 | 23587.3722 |  | 881 | 19950.9046 | 883 | 11.1689 | 884.6667 | 21317.8949 | 877.3333 | 11.1689
894.3333 | 25126.8841 |  | 897.8333 | 1276.7418 | 899.8333 | 17.4742 | 901.6667 | 20112.5896 | 894.3333 | 17.4742
911.1667 | 23997.5913 |  | 914.8333 | 340.9215 | 916.5 | 20.794 | 918.5 | 18576.0778 | 911.1667 | 20.794
927.6667 | 18355.0952 |  | 931.6667 | 29.0346 | 933.3333 | 13.4886 | 935.3333 | 18845.0916 | 927.6667 | 13.4886
944.5 | 18355.0952 |  | 948.3333 | 8.9118 | 950.1667 | 17.2184 | 952 | 18371.7619 | 944.5 | 8.9118
961.5 | 18828.7912 |  | 965 | 17.5861 | 967 | 24.3723 | 968.8333 | 19319.1538 | 961.5 | 17.5861
978.3333 | 18827.6923 |  | 981.8333 | 14.9574 | 983.8333 | 12.3036 | 985.6667 | 17696.8124 | 978.3333 | 12.3036
995 | 17941.8789 |  | 998.6667 | 12.8003 | 1000.5 | 16.4981 | 1002.5 | 5309.4211 | 995 | 12.8003
1011.6667 | 8819.1714 |  | 1015.6667 | 20.6343 | 1017.3333 | 15.3886 | 1019.3333 | 21.5186 | 1011.6667 | 15.3886
1028.6667 | 6.3674 |  | 1032.3333 | 14.0873 | 1034 | 15.8967 | 1036 | 25.4348 | 1028.6667 | 6.3674
1045.3333 | 7.8424 |  | 1049 | 21.2275 | 1051 | 20.9227 | 1052.6667 | 13.998 | 1045.3333 | 7.8424
1062.1667 | 14.269 |  | 1065.8333 | 5.8537 | 1067.6667 | 15.8495 | 1069.6667 | 22.1474 | 1062.1667 | 5.8537
1079 | 13.0553 |  | 1082.8333 | 12.0144 | 1084.5 | 10.1324 | 1086.3333 | 11.4027 | 1079 | 10.1324
1095.8333 | 8.694 |  | 1099.6667 | 20.8086 | 1101.5 | 14.0822 | 1103.3333 | 20.7335 | 1095.8333 | 8.694
1112.5 | 8.6702 |  | 1116.3333 | 12.6541 | 1118.1667 | 23.1759 | 1120 | 21.8917 | 1112.5 | 8.6702
1129.5 | 11.44 |  | 1133 | 7.2424 | 1135 | 6.2547 | 1136.8333 | 17.0005 | 1129.5 | 6.2547
1146.3333 | 12.0171 |  | 1149.8333 | 11.4944 | 1151.8333 | 7.4729 | 1153.6667 | 19.6816 | 1146.3333 | 7.4729
1162.8333 | 13.6269 |  | 1166.6667 | 9.1031 | 1168.5 | 22.4115 | 1170.3333 | 7.5492 | 1162.8333 | 7.5492
1179.6667 | 12.0894 |  | 1183.6667 | 3.3541 | 1185.3333 | 20.6739 | 1187.3333 | 12.6945 | 1179.6667 | 3.3541
1196.5 | 21.1386 |  | 1200.1667 | 6.3089 | 1202 | 7.7204 | 1204 | 7.3527 | 1196.5 | 6.3089
1213.3333 | 19.2347 |  | 1217 | 6.85 | 1219 | 16.7766 | 1220.6667 | 7.8817 | 1213.3333 | 6.85
1230.1667 | 16.4002 |  | 1234 | 20.3388 | 1235.8333 | 12.0559 | 1237.6667 | 19.2323 | 1230.1667 | 12.0559
1246.8333 | 21.5904 |  | 1250.6667 | 13.2525 | 1252.5 | 12.4573 | 1254.3333 | 15.3842 | 1246.8333 | 12.4573
1263.5 | 14.5141 |  | 1267.5 | 18.6593 | 1269.1667 | 10.7731 | 1271.1667 | 12.4622 | 1263.5 | 10.7731
1280.5 | 16.5714 |  | 1284.3333 | 17.5901 | 1286.1667 | 17.959 | 1288 | 12.8094 | 1280.5 | 12.8094
1297.3333 | 10.2409 |  | 1301 | 14.6964 | 1303 | 8.9707 | 1304.6667 | 21.0205 | 1297.3333 | 8.9707
1314.1667 | 15.3722 |  | 1317.8333 | 11.6398 | 1319.6667 | 17.8276 | 1321.6667 | 22.0681 | 1314.1667 | 11.6398
1330.8333 | 14.9363 |  | 1334.6667 | 9.8204 | 1336.5 | 12.752 | 1338.3333 | 22.9574 | 1330.8333 | 9.8204
1347.6667 | 12.4262 |  | 1351.5 | 21.5268 | 1353.3333 | 2.0293 | 1355.1667 | 10.0647 | 1347.6667 | 2.0293
1364.5 | 20.2175 |  | 1368.1667 | 11.5429 | 1370 | 23.208 | 1372 | 16.6334 | 1364.5 | 11.5429
1381.3333 | 14.2815 |  | 1385 | 6.7938 | 1387 | 17.3296 | 1388.6667 | 16.8737 | 1381.3333 | 6.7938

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 5 |  |  | 2006-07-06 | 10:42
38904.4453 | 2 | 0 | 1 | PVC | 3-C | Tray
38904.4455 | 1 | 1 | 1 | 300 C | 6.1 kW/m2 |  | Conductors
38904.4457 | 1 | 0 | 1
38904.4459 | 1 | 0 | 1
38904.4461 | 1 | 0 | 1
38904.4463 | 1 | 0 | 1
38904.4465 | 1 | 0 | 1
38904.4467 | 2 | 0 | 1
38904.4469 | 1 | 0 | 1
38904.4471 | 1 | 0 | 1
38904.4473 | 1 | 0 | 1
38904.4475 | 1 | 0 | 1
38904.4477 | 1 | 0 | 1
38904.4479 | 1 | 0 | 1
38904.4481 | 1 | 0 | 1
38904.4483 | 1 | 0 | 1
38904.4484 | 1 | 0 | 1
38904.4486 | 1 | 0 | 1
38904.4488 | 1 | 0 | 1
38904.449 | 1 | 0 | 1
38904.4492 | 1 | 0 | 1
38904.4494 | 1 | 0 | 1
38904.4496 | 1 | 0 | 1
38904.4498 | 1 | 0 | 1
38904.45 | 1 | 0 | 1
38904.4502 | 1 | 0 | 1
38904.4504 | 1 | 0 | 1
38904.4506 | 1 | 0 | 1
38904.4508 | 1 | 0 | 1
38904.451 | 1 | 0 | 1
38904.4512 | 1 | 0 | 1
38904.4514 | 1 | 0 | 1
38904.4516 | 1 | 0 | 1
38904.4518 | 1 | 0 | 1
38904.4519 | 1 | 0 | 1
38904.4521 | 1 | 0 | 1
38904.4523 | 1 | 0 | 1
38904.4525 | 1 | 0 | 1
38904.4527 | 1 | 0 | 1
38904.4529 | 1 | 0 | 1
38904.4531 | 1 | 0 | 1
38904.4533 | 1 | 0 | 1
38904.4535 | 1 | 0 | 1
38904.4537 | 1 | 0 | 1
38904.4539 | 1 | 0 | 1
38904.4541 | 1 | 0 | 1
38904.4543 | 1 | 0 | 1
38904.4545 | 1 | 0 | 1
38904.4547 | 1 | 0 | 1
38904.4549 | 1 | 0 | 1
38904.4551 | 10 | 0 | 1
38904.4553 | 11 | 0 | 1
38904.4555 | 12 | 0 | 1
38904.4556 | 11 | 0 | 1
38904.4558 | 12 | 0 | 1
38904.456 | 12 | 0 | 1
38904.4562 | 12 | 0 | 1
38904.4564 | 12 | 0 | 1
38904.4566 | 12 | 0 | 1
38904.4568 | 14 | 0 | 1
38904.457 | 14 | 0 | 1
38904.4572 | 14 | 0 | 1
38904.4574 | 13 | 0 | 1
38904.4576 | 13 | 0 | 1
38904.4578 | 13 | 0 | 1
38904.458 | 2393 | 1 | 1
38904.4582 | 2535 | 0 | 1
38904.4584 | 2305 | 0 | 1
38904.4586 | 2088 | 0 | 1
38904.4587 | 2359 | 0 | 1
38904.4589 | 2221 | 0 | 1
38904.4591 | 2232 | 0 | 1
38904.4593 | 2168 | 0 | 1
38904.4595 | 2548 | 0 | 1
38904.4597 | 2384 | 0 | 1
38904.4599 | 2115 | 0 | 1
38904.4601 | 2015 | 0 | 1
38904.4603 | 2170 | 0 | 1
38904.4605 | 2194 | 0 | 1
38904.4607 | 2318 | 0 | 1
38904.4609 | 2195 | 0 | 1
38904.4611 | 2344 | 0 | 1
38904.4613 | 2486 | 0 | 1
38904.4615 | 2123 | 0 | 1
38904.4617 | 1970 | 0 | 1
38904.4619 | 2131 | 0 | 1
38904.4621 | 2447 | 0 | 1
38904.4454 | 1 | 0 | 2
38904.4455 | 1 | 0 | 2
38904.4457 | 1 | 0 | 2
38904.4459 | 1 | 0 | 2
38904.4461 | 1 | 0 | 2
38904.4463 | 1 | 0 | 2
38904.4465 | 1 | 0 | 2
38904.4467 | 2 | 0 | 2
38904.4469 | 1 | 0 | 2
38904.4471 | 1 | 0 | 2
38904.4473 | 1 | 0 | 2
38904.4475 | 1 | 0 | 2
38904.4477 | 1 | 0 | 2
38904.4479 | 1 | 0 | 2
38904.4481 | 1 | 0 | 2
38904.4483 | 1 | 0 | 2
38904.4485 | 1 | 0 | 2
38904.4487 | 1 | 0 | 2
38904.4489 | 1 | 0 | 2
38904.4491 | 1 | 0 | 2
38904.4492 | 1 | 0 | 2
38904.4494 | 1 | 0 | 2
38904.4496 | 1 | 0 | 2
38904.4498 | 1 | 0 | 2
38904.45 | 1 | 0 | 2
38904.4502 | 1 | 0 | 2
38904.4504 | 1 | 0 | 2
38904.4506 | 1 | 0 | 2
38904.4508 | 1 | 0 | 2
38904.451 | 1 | 0 | 2
38904.4512 | 1 | 0 | 2
38904.4514 | 1 | 0 | 2
38904.4516 | 1 | 0 | 2
38904.4518 | 1 | 0 | 2
38904.452 | 1 | 0 | 2
38904.4522 | 1 | 0 | 2
38904.4523 | 1 | 0 | 2
38904.4525 | 1 | 0 | 2
38904.4527 | 1 | 1 | 2
38904.4529 | 1 | 0 | 2
38904.4531 | 1 | 0 | 2
38904.4533 | 1 | 0 | 2
38904.4535 | 1 | 0 | 2
38904.4537 | 1 | 0 | 2
38904.4539 | 1 | 0 | 2
38904.4541 | 1 | 0 | 2
38904.4543 | 1 | 0 | 2
38904.4545 | 1 | 0 | 2
38904.4547 | 1 | 0 | 2
38904.4549 | 1 | 0 | 2
38904.4551 | 6 | 0 | 2
38904.4553 | 10 | 0 | 2
38904.4555 | 10 | 0 | 2
38904.4557 | 10 | 0 | 2
38904.4559 | 10 | 0 | 2
38904.4561 | 9 | 0 | 2
38904.4562 | 10 | 0 | 2
38904.4564 | 513 | 0 | 2
38904.4566 | 1523 | 7 | 2
38904.4568 | 1946 | 0 | 2
38904.457 | 2368 | 0 | 2
38904.4572 | 2131 | 0 | 2
38904.4574 | 2302 | 0 | 2
38904.4576 | 2524 | 0 | 2
38904.4578 | 2142 | 0 | 2
38904.458 | 2539 | 1 | 2
38904.4582 | 2246 | 0 | 2
38904.4584 | 2482 | 0 | 2
38904.4586 | 2386 | 0 | 2
38904.4588 | 1963 | 0 | 2
38904.459 | 2384 | 0 | 2
38904.4592 | 2497 | 0 | 2
38904.4594 | 1991 | 0 | 2
38904.4595 | 2188 | 0 | 2
38904.4597 | 2564 | 0 | 2
38904.4599 | 2358 | 0 | 2
38904.4601 | 2519 | 0 | 2
38904.4603 | 2443 | 0 | 2
38904.4605 | 2472 | 0 | 2
38904.4607 | 2172 | 0 | 2
38904.4609 | 2098 | 0 | 2
38904.4611 | 2452 | 0 | 2
38904.4613 | 2183 | 0 | 2
38904.4615 | 2451 | 0 | 2
38904.4617 | 2378 | 0 | 2
38904.4619 | 2331 | 0 | 2
38904.4621 | 2249 | 0 | 2
38904.4454 | 1 | 0 | 3
38904.4456 | 1 | 0 | 3
38904.4458 | 1 | 0 | 3
38904.4459 | 1 | 0 | 3
38904.4461 | 1 | 0 | 3
38904.4463 | 1 | 0 | 3
38904.4465 | 1 | 0 | 3
38904.4467 | 1 | 0 | 3
38904.4469 | 1 | 0 | 3
38904.4471 | 1 | 0 | 3
38904.4473 | 1 | 0 | 3
38904.4475 | 1 | 0 | 3
38904.4477 | 1 | 0 | 3
38904.4479 | 1 | 0 | 3
38904.4481 | 1 | 0 | 3
38904.4483 | 1 | 0 | 3
38904.4485 | 1 | 0 | 3
38904.4487 | 1 | 0 | 3
38904.4489 | 1 | 0 | 3
38904.4491 | 1 | 0 | 3
38904.4493 | 1 | 0 | 3
38904.4495 | 1 | 0 | 3
38904.4497 | 1 | 0 | 3
38904.4498 | 1 | 0 | 3
38904.45 | 1 | 0 | 3
38904.4502 | 1 | 0 | 3
38904.4504 | 1 | 0 | 3
38904.4506 | 1 | 0 | 3
38904.4508 | 1 | 0 | 3
38904.451 | 1 | 0 | 3
38904.4512 | 1 | 0 | 3
38904.4514 | 1 | 0 | 3
38904.4516 | 1 | 0 | 3
38904.4518 | 1 | 1 | 3
38904.452 | 1 | 0 | 3
38904.4522 | 1 | 0 | 3
38904.4524 | 1 | 0 | 3
38904.4526 | 1 | 0 | 3
38904.4528 | 1 | 0 | 3
38904.453 | 1 | 0 | 3
38904.4531 | 1 | 0 | 3
38904.4533 | 1 | 0 | 3
38904.4535 | 1 | 0 | 3
38904.4537 | 1 | 0 | 3
38904.4539 | 1 | 0 | 3
38904.4541 | 1 | 0 | 3
38904.4543 | 1 | 0 | 3
38904.4545 | 1 | 0 | 3
38904.4547 | 1 | 0 | 3
38904.4549 | 1 | 0 | 3
38904.4551 | 4 | 0 | 3
38904.4553 | 7 | 0 | 3
38904.4555 | 7 | 0 | 3
38904.4557 | 7 | 0 | 3
38904.4559 | 7 | 0 | 3
38904.4561 | 7 | 0 | 3
38904.4563 | 8 | 0 | 3
38904.4565 | 7 | 0 | 3
38904.4566 | 8 | 0 | 3
38904.4568 | 14 | 0 | 3
38904.457 | 14 | 0 | 3
38904.4572 | 13 | 0 | 3
38904.4574 | 14 | 0 | 3
38904.4576 | 13 | 0 | 3
38904.4578 | 38 | 0 | 3
38904.458 | 2432 | 0 | 3
38904.4582 | 2320 | 0 | 3
38904.4584 | 2426 | 0 | 3
38904.4586 | 2272 | 0 | 3
38904.4588 | 2499 | 0 | 3
38904.459 | 2441 | 0 | 3
38904.4592 | 2392 | 0 | 3
38904.4594 | 2491 | 0 | 3
38904.4596 | 2163 | 0 | 3
38904.4598 | 2514 | 0 | 3
38904.46 | 2070 | 0 | 3
38904.4602 | 2398 | 0 | 3
38904.4603 | 2559 | 0 | 3
38904.4605 | 2234 | 0 | 3
38904.4607 | 2150 | 0 | 3
38904.4609 | 2341 | 0 | 3
38904.4611 | 2561 | 0 | 3
38904.4613 | 2296 | 0 | 3
38904.4615 | 2461 | 0 | 3
38904.4617 | 2570 | 0 | 3
38904.4619 | 2144 | 0 | 3
38904.4621 | 2401 | 0 | 3
38904.4454 | 1 | 0 | 4
38904.4456 | 1 | 0 | 4
38904.4458 | 1 | 0 | 4
38904.446 | 1 | 0 | 4
38904.4462 | 1 | 0 | 4
38904.4464 | 1 | 0 | 4
38904.4466 | 1 | 0 | 4
38904.4467 | 1 | 0 | 4
38904.4469 | 1 | 0 | 4
38904.4471 | 1 | 0 | 4
38904.4473 | 1 | 0 | 4
38904.4475 | 1 | 0 | 4
38904.4477 | 1 | 0 | 4
38904.4479 | 1 | 0 | 4
38904.4481 | 1 | 0 | 4
38904.4483 | 1 | 0 | 4
38904.4485 | 1 | 0 | 4
38904.4487 | 1 | 0 | 4
38904.4489 | 1 | 0 | 4
38904.4491 | 1 | 0 | 4
38904.4493 | 1 | 0 | 4
38904.4495 | 1 | 0 | 4
38904.4497 | 1 | 0 | 4
38904.4499 | 1 | 0 | 4
38904.4501 | 1 | 0 | 4
38904.4502 | 1 | 0 | 4
38904.4504 | 1 | 0 | 4
38904.4506 | 1 | 0 | 4
38904.4508 | 1 | 0 | 4
38904.451 | 1 | 0 | 4
38904.4512 | 1 | 0 | 4
38904.4514 | 1 | 0 | 4
38904.4516 | 1 | 0 | 4
38904.4518 | 1 | 0 | 4
38904.452 | 1 | 0 | 4
38904.4522 | 1 | 0 | 4
38904.4524 | 1 | 0 | 4
38904.4526 | 1 | 0 | 4
38904.4528 | 1 | 0 | 4
38904.453 | 1 | 0 | 4
38904.4532 | 1 | 0 | 4
38904.4534 | 1 | 0 | 4
38904.4536 | 1 | 0 | 4
38904.4538 | 1 | 0 | 4
38904.4539 | 1 | 0 | 4
38904.4541 | 1 | 0 | 4
38904.4543 | 1 | 0 | 4
38904.4545 | 1 | 0 | 4
38904.4547 | 1 | 0 | 4
38904.4549 | 1 | 0 | 4
38904.4551 | 2263 | 0 | 4
38904.4553 | 2024 | 0 | 4
38904.4555 | 2014 | 0 | 4
38904.4557 | 2035 | 0 | 4
38904.4559 | 2528 | 0 | 4
38904.4561 | 2395 | 0 | 4
38904.4563 | 2510 | 0 | 4
38904.4565 | 2120 | 0 | 4
38904.4567 | 2420 | 0 | 4
38904.4569 | 2444 | 0 | 4
38904.457 | 2066 | 0 | 4
38904.4572 | 2089 | 0 | 4
38904.4574 | 2546 | 0 | 4
38904.4576 | 2513 | 0 | 4
38904.4578 | 2331 | 0 | 4
38904.458 | 1948 | 0 | 4
38904.4582 | 1950 | 0 | 4
38904.4584 | 2230 | 0 | 4
38904.4586 | 2297 | 0 | 4
38904.4588 | 2127 | 0 | 4
38904.459 | 2140 | 0 | 4
38904.4592 | 2564 | 0 | 4
38904.4594 | 2230 | 0 | 4
38904.4596 | 2002 | 0 | 4
38904.4598 | 1974 | 0 | 4
38904.46 | 2549 | 0 | 4
38904.4602 | 2118 | 0 | 4
38904.4604 | 2035 | 0 | 4
38904.4606 | 2372 | 0 | 4
38904.4609 | 2158 | 0 | 4
38904.4611 | 2326 | 0 | 4
38904.4613 | 2410 | 0 | 4
38904.4615 | 2015 | 0 | 4
38904.4617 | 2568 | 0 | 4
38904.4619 | 2032 | 0 | 4
38904.4621 | 2171 | 0 | 4
38904.4454 | 1 | 0 | 5
38904.4456 | 1 | 0 | 5
38904.4458 | 1 | 0 | 5
38904.446 | 1 | 0 | 5
38904.4462 | 1 | 0 | 5
38904.4464 | 1 | 0 | 5
38904.4466 | 1 | 0 | 5
38904.4468 | 1 | 0 | 5
38904.447 | 1 | 0 | 5
38904.4472 | 1 | 0 | 5
38904.4473 | 1 | 0 | 5
38904.4475 | 1 | 0 | 5
38904.4477 | 1 | 0 | 5
38904.4479 | 1 | 0 | 5
38904.4481 | 1 | 0 | 5
38904.4483 | 1 | 0 | 5
38904.4485 | 1 | 0 | 5
38904.4487 | 1 | 0 | 5
38904.4489 | 1 | 0 | 5
38904.4491 | 1 | 0 | 5
38904.4493 | 1 | 0 | 5
38904.4495 | 1 | 0 | 5
38904.4497 | 1 | 0 | 5
38904.4499 | 1 | 0 | 5
38904.4501 | 1 | 0 | 5
38904.4503 | 1 | 0 | 5
38904.4505 | 1 | 0 | 5
38904.4506 | 1 | 0 | 5
38904.4508 | 1 | 0 | 5
38904.451 | 1 | 0 | 5
38904.4512 | 1 | 0 | 5
38904.4514 | 1 | 0 | 5
38904.4516 | 1 | 0 | 5
38904.4518 | 1 | 0 | 5
38904.452 | 1 | 0 | 5
38904.4522 | 1 | 0 | 5
38904.4524 | 1 | 0 | 5
38904.4526 | 1 | 0 | 5
38904.4528 | 1 | 0 | 5
38904.453 | 1 | 0 | 5
38904.4532 | 1 | 0 | 5
38904.4534 | 1 | 0 | 5
38904.4536 | 1 | 0 | 5
38904.4538 | 1 | 0 | 5
38904.454 | 1 | 0 | 5
38904.4542 | 1 | 0 | 5
38904.4544 | 1 | 0 | 5
38904.4545 | 1 | 1 | 5
38904.4547 | 1 | 0 | 5
38904.4549 | 1 | 0 | 5
38904.4551 | 14 | 0 | 5
38904.4553 | 14 | 0 | 5
38904.4555 | 15 | 0 | 5
38904.4557 | 15 | 0 | 5
38904.4559 | 15 | 0 | 5
38904.4561 | 15 | 0 | 5
38904.4563 | 15 | 0 | 5
38904.4565 | 15 | 0 | 5
38904.4567 | 14 | 0 | 5
38904.4569 | 14 | 0 | 5
38904.4571 | 14 | 0 | 5
38904.4573 | 14 | 0 | 5
38904.4575 | 14 | 0 | 5
38904.4577 | 19 | 1 | 5
38904.4578 | 2532 | 32 | 5
38904.458 | 2468 | 0 | 5
38904.4582 | 2344 | 0 | 5
38904.4584 | 2080 | 0 | 5
38904.4586 | 2540 | 0 | 5
38904.4588 | 2283 | 0 | 5
38904.459 | 2488 | 0 | 5
38904.4592 | 2337 | 0 | 5
38904.4594 | 2283 | 0 | 5
38904.4596 | 2153 | 0 | 5
38904.4598 | 2065 | 0 | 5
38904.46 | 2219 | 0 | 5
38904.4602 | 2122 | 0 | 5
38904.4604 | 2000 | 0 | 5
38904.4606 | 1967 | 0 | 5
38904.4608 | 2309 | 0 | 5
38904.461 | 2124 | 0 | 5
38904.4611 | 2160 | 0 | 5
38904.4613 | 1993 | 0 | 5
38904.4615 | 2187 | 0 | 5
38904.4617 | 2446 | 0 | 5
38904.4619 | 2173 | 0 | 5
38904.4621 | 1993 | 0 | 5
38904.4454 | 1 | 0 | 6
38904.4456 | 1 | 0 | 6
38904.4458 | 1 | 0 | 6
38904.446 | 1 | 0 | 6
38904.4462 | 1 | 0 | 6
38904.4464 | 1 | 0 | 6
38904.4466 | 1 | 0 | 6
38904.4468 | 1 | 0 | 6
38904.447 | 1 | 0 | 6
38904.4472 | 1 | 0 | 6
38904.4474 | 1 | 0 | 6
38904.4476 | 1 | 0 | 6
38904.4478 | 1 | 0 | 6
38904.448 | 1 | 0 | 6
38904.4481 | 1 | 0 | 6
38904.4483 | 1 | 0 | 6
38904.4485 | 1 | 0 | 6
38904.4487 | 1 | 0 | 6
38904.4489 | 1 | 0 | 6
38904.4491 | 1 | 0 | 6
38904.4493 | 1 | 0 | 6
38904.4495 | 1 | 0 | 6
38904.4497 | 1 | 1 | 6
38904.4499 | 1 | 0 | 6
38904.4501 | 1 | 0 | 6
38904.4503 | 1 | 0 | 6
38904.4505 | 1 | 0 | 6
38904.4507 | 1 | 0 | 6
38904.4509 | 1 | 0 | 6
38904.4511 | 1 | 0 | 6
38904.4512 | 1 | 0 | 6
38904.4514 | 1 | 0 | 6
38904.4516 | 1 | 0 | 6
38904.4518 | 1 | 0 | 6
38904.452 | 1 | 0 | 6
38904.4522 | 1 | 0 | 6
38904.4524 | 1 | 0 | 6
38904.4526 | 1 | 0 | 6
38904.4528 | 1 | 0 | 6
38904.453 | 1 | 0 | 6
38904.4532 | 1 | 0 | 6
38904.4534 | 1 | 0 | 6
38904.4536 | 1 | 0 | 6
38904.4538 | 1 | 0 | 6
38904.454 | 1 | 0 | 6
38904.4542 | 1 | 0 | 6
38904.4544 | 1 | 0 | 6
38904.4546 | 1 | 0 | 6
38904.4548 | 1 | 0 | 6
38904.4549 | 1 | 0 | 6
38904.4551 | 10 | 0 | 6
38904.4553 | 11 | 0 | 6
38904.4555 | 12 | 0 | 6
38904.4557 | 11 | 0 | 6
38904.4559 | 11 | 0 | 6
38904.4561 | 11 | 0 | 6
38904.4563 | 11 | 0 | 6
38904.4565 | 11 | 0 | 6
38904.4567 | 12 | 0 | 6
38904.4569 | 13 | 0 | 6
38904.4571 | 14 | 0 | 6
38904.4573 | 13 | 0 | 6
38904.4575 | 13 | 0 | 6
38904.4577 | 1199 | 1140 | 6
38904.4579 | 2033 | 10 | 6
38904.4581 | 2050 | 0 | 6
38904.4583 | 2356 | 0 | 6
38904.4584 | 2222 | 0 | 6
38904.4586 | 2547 | 0 | 6
38904.4588 | 2120 | 0 | 6
38904.459 | 2434 | 0 | 6
38904.4592 | 2391 | 0 | 6
38904.4594 | 2326 | 0 | 6
38904.4596 | 2568 | 0 | 6
38904.4598 | 2265 | 0 | 6
38904.46 | 2219 | 7 | 6
38904.4602 | 2479 | 0 | 6
38904.4604 | 2343 | 0 | 6
38904.4606 | 2314 | 0 | 6
38904.4608 | 2327 | 0 | 6
38904.461 | 2311 | 0 | 6
38904.4612 | 2209 | 0 | 6
38904.4614 | 2292 | 0 | 6
38904.4616 | 2045 | 0 | 6
38904.4617 | 2416 | 0 | 6
38904.4619 | 2266 | 0 | 6
38904.4621 | 2308 | 0 | 6
38904.4454 | 1 | 0 | 7
38904.4456 | 1 | 0 | 7
38904.4458 | 1 | 0 | 7
38904.446 | 1 | 0 | 7
38904.4462 | 1 | 0 | 7
38904.4464 | 1 | 0 | 7
38904.4466 | 1 | 0 | 7
38904.4468 | 1 | 0 | 7
38904.447 | 1 | 0 | 7
38904.4472 | 1 | 0 | 7
38904.4474 | 1 | 0 | 7
38904.4476 | 1 | 0 | 7
38904.4478 | 1 | 0 | 7
38904.448 | 1 | 0 | 7
38904.4482 | 1 | 0 | 7
38904.4484 | 1 | 0 | 7
38904.4485 | 1 | 0 | 7
38904.4487 | 1 | 0 | 7
38904.4489 | 1 | 0 | 7
38904.4491 | 1 | 0 | 7
38904.4493 | 1 | 0 | 7
38904.4495 | 1 | 0 | 7
38904.4497 | 1 | 0 | 7
38904.4499 | 1 | 0 | 7
38904.4501 | 1 | 0 | 7
38904.4503 | 1 | 0 | 7
38904.4505 | 1 | 0 | 7
38904.4507 | 1 | 0 | 7
38904.4509 | 1 | 0 | 7
38904.4511 | 1 | 0 | 7
38904.4513 | 1 | 0 | 7
38904.4515 | 1 | 0 | 7
38904.4517 | 1 | 0 | 7
38904.4519 | 1 | 0 | 7
38904.452 | 1 | 0 | 7
38904.4522 | 1 | 0 | 7
38904.4524 | 1 | 0 | 7
38904.4526 | 1 | 0 | 7
38904.4528 | 1 | 0 | 7
38904.453 | 1 | 0 | 7
38904.4532 | 1 | 0 | 7
38904.4534 | 1 | 0 | 7
38904.4536 | 1 | 0 | 7
38904.4538 | 1 | 0 | 7
38904.454 | 1 | 0 | 7
38904.4542 | 1 | 0 | 7
38904.4544 | 1 | 0 | 7
38904.4546 | 1 | 0 | 7
38904.4548 | 1 | 0 | 7
38904.455 | 1 | 0 | 7
38904.4552 | 6 | 0 | 7
38904.4553 | 8 | 0 | 7
38904.4555 | 9 | 0 | 7
38904.4557 | 8 | 0 | 7
38904.4559 | 8 | 0 | 7
38904.4561 | 8 | 0 | 7
38904.4563 | 8 | 0 | 7
38904.4565 | 1471 | 6 | 7
38904.4567 | 265 | 3 | 7
38904.4569 | 2017 | 0 | 7
38904.4571 | 2413 | 0 | 7
38904.4573 | 2011 | 0 | 7
38904.4575 | 2031 | 0 | 7
38904.4577 | 2262 | 21 | 7
38904.4579 | 2010 | 3 | 7
38904.4581 | 1982 | 0 | 7
38904.4583 | 2181 | 0 | 7
38904.4585 | 2311 | 0 | 7
38904.4587 | 2110 | 0 | 7
38904.4589 | 2020 | 0 | 7
38904.4591 | 1998 | 0 | 7
38904.4592 | 2200 | 0 | 7
38904.4594 | 2537 | 0 | 7
38904.4596 | 2508 | 0 | 7
38904.4598 | 2371 | 0 | 7
38904.46 | 2444 | 0 | 7
38904.4602 | 2402 | 0 | 7
38904.4604 | 1965 | 0 | 7
38904.4606 | 2254 | 0 | 7
38904.4608 | 2401 | 0 | 7
38904.461 | 1999 | 0 | 7
38904.4612 | 2095 | 0 | 7
38904.4614 | 2225 | 0 | 7
38904.4616 | 2087 | 0 | 7
38904.4618 | 2046 | 0 | 7
38904.462 | 2340 | 0 | 7
38904.4622 | 2516 | 0 | 7
38904.4455 | 1 | 0 | 8
38904.4456 | 1 | 0 | 8
38904.4458 | 1 | 0 | 8
38904.446 | 1 | 0 | 8
38904.4462 | 1 | 0 | 8
38904.4464 | 1 | 0 | 8
38904.4466 | 1 | 0 | 8
38904.4468 | 1 | 0 | 8
38904.447 | 1 | 0 | 8
38904.4472 | 1 | 0 | 8
38904.4474 | 1 | 0 | 8
38904.4476 | 1 | 0 | 8
38904.4478 | 1 | 0 | 8
38904.448 | 1 | 0 | 8
38904.4482 | 1 | 0 | 8
38904.4484 | 1 | 0 | 8
38904.4486 | 1 | 0 | 8
38904.4488 | 1 | 0 | 8
38904.4489 | 1 | 0 | 8
38904.4491 | 1 | 0 | 8
38904.4493 | 1 | 0 | 8
38904.4495 | 1 | 0 | 8
38904.4497 | 1 | 0 | 8
38904.4499 | 1 | 0 | 8
38904.4501 | 1 | 0 | 8
38904.4503 | 1 | 0 | 8
38904.4505 | 1 | 0 | 8
38904.4507 | 1 | 0 | 8
38904.4509 | 1 | 0 | 8
38904.4511 | 1 | 0 | 8
38904.4513 | 1 | 0 | 8
38904.4515 | 1 | 0 | 8
38904.4517 | 1 | 0 | 8
38904.4519 | 1 | 0 | 8
38904.4521 | 1 | 0 | 8
38904.4523 | 1 | 0 | 8
38904.4525 | 1 | 0 | 8
38904.4527 | 1 | 0 | 8
38904.4528 | 1 | 0 | 8
38904.453 | 1 | 0 | 8
38904.4532 | 1 | 0 | 8
38904.4534 | 1 | 0 | 8
38904.4536 | 1 | 0 | 8
38904.4538 | 1 | 0 | 8
38904.454 | 1 | 0 | 8
38904.4542 | 1 | 0 | 8
38904.4544 | 1 | 0 | 8
38904.4546 | 1 | 0 | 8
38904.4548 | 1 | 0 | 8
38904.455 | 69 | 0 | 8
38904.4552 | 2436 | 0 | 8
38904.4554 | 2409 | 0 | 8
38904.4556 | 2484 | 0 | 8
38904.4558 | 2339 | 0 | 8
38904.4559 | 1996 | 0 | 8
38904.4561 | 2070 | 0 | 8
38904.4563 | 2512 | 0 | 8
38904.4565 | 2402 | 0 | 8
38904.4567 | 1961 | 0 | 8
38904.4569 | 2350 | 0 | 8
38904.4571 | 2213 | 0 | 8
38904.4573 | 2105 | 0 | 8
38904.4575 | 2123 | 0 | 8
38904.4577 | 2093 | 14 | 8
38904.4579 | 2232 | 1 | 8
38904.4581 | 2489 | 0 | 8
38904.4583 | 2062 | 0 | 8
38904.4585 | 2284 | 0 | 8
38904.4587 | 2292 | 0 | 8
38904.4589 | 2506 | 0 | 8
38904.4591 | 1968 | 0 | 8
38904.4593 | 2548 | 0 | 8
38904.4594 | 2556 | 0 | 8
38904.4596 | 2313 | 0 | 8
38904.4598 | 2165 | 0 | 8
38904.46 | 2534 | 0 | 8
38904.4602 | 2026 | 0 | 8
38904.4604 | 2415 | 0 | 8
38904.4606 | 2508 | 0 | 8
38904.4608 | 2558 | 0 | 8
38904.461 | 2324 | 0 | 8
38904.4612 | 2328 | 0 | 8
38904.4614 | 2083 | 0 | 8
38904.4616 | 2562 | 0 | 8
38904.4618 | 2556 | 0 | 8
38904.462 | 2264 | 0 | 8
38904.4622 | 2150 | 0 | 8
38904.4455 | 1 | 0 | 9
38904.4457 | 1 | 0 | 9
38904.4459 | 1 | 0 | 9
38904.4461 | 1 | 0 | 9
38904.4463 | 1 | 0 | 9
38904.4464 | 1 | 0 | 9
38904.4466 | 1 | 0 | 9
38904.4468 | 1 | 0 | 9
38904.447 | 1 | 0 | 9
38904.4472 | 1 | 0 | 9
38904.4474 | 1 | 0 | 9
38904.4476 | 1 | 0 | 9
38904.4478 | 1 | 0 | 9
38904.448 | 1 | 0 | 9
38904.4482 | 1 | 0 | 9
38904.4484 | 1 | 0 | 9
38904.4486 | 1 | 0 | 9
38904.4488 | 1 | 0 | 9
38904.449 | 1 | 0 | 9
38904.4492 | 1 | 0 | 9
38904.4494 | 1 | 0 | 9
38904.4495 | 1 | 0 | 9
38904.4497 | 1 | 0 | 9
38904.4499 | 1 | 0 | 9
38904.4501 | 1 | 0 | 9
38904.4503 | 1 | 0 | 9
38904.4505 | 1 | 0 | 9
38904.4507 | 1 | 0 | 9
38904.4509 | 1 | 0 | 9
38904.4511 | 1 | 0 | 9
38904.4513 | 1 | 0 | 9
38904.4515 | 1 | 0 | 9
38904.4517 | 1 | 0 | 9
38904.4519 | 1 | 0 | 9
38904.4521 | 1 | 0 | 9
38904.4523 | 1 | 0 | 9
38904.4525 | 1 | 0 | 9
38904.4527 | 1 | 0 | 9
38904.4529 | 1 | 0 | 9
38904.4531 | 1 | 0 | 9
38904.4532 | 1 | 0 | 9
38904.4534 | 1 | 0 | 9
38904.4536 | 1 | 0 | 9
38904.4538 | 1 | 0 | 9
38904.454 | 1 | 0 | 9
38904.4542 | 1 | 0 | 9
38904.4544 | 1 | 0 | 9
38904.4546 | 1 | 0 | 9
38904.4548 | 1 | 0 | 9
38904.455 | 4 | 0 | 9
38904.4552 | 14 | 0 | 9
38904.4554 | 15 | 0 | 9
38904.4556 | 15 | 0 | 9
38904.4558 | 15 | 0 | 9
38904.456 | 15 | 0 | 9
38904.4562 | 15 | 0 | 9
38904.4564 | 122 | 0 | 9
38904.4566 | 75 | 0 | 9
38904.4567 | 1899 | 6 | 9
38904.4569 | 2041 | 0 | 9
38904.4571 | 2331 | 0 | 9
38904.4573 | 2499 | 0 | 9
38904.4575 | 2443 | 0 | 9
38904.4577 | 2129 | 5 | 9
38904.4579 | 2293 | 1 | 9
38904.4581 | 2339 | 0 | 9
38904.4583 | 1980 | 0 | 9
38904.4585 | 2534 | 0 | 9
38904.4587 | 2446 | 0 | 9
38904.4589 | 2502 | 0 | 9
38904.4591 | 2568 | 0 | 9
38904.4593 | 2555 | 0 | 9
38904.4595 | 2504 | 0 | 9
38904.4597 | 2426 | 0 | 9
38904.4599 | 2568 | 0 | 9
38904.46 | 2486 | 0 | 9
38904.4602 | 2334 | 0 | 9
38904.4604 | 2082 | 0 | 9
38904.4606 | 2137 | 0 | 9
38904.4608 | 1992 | 0 | 9
38904.461 | 2565 | 0 | 9
38904.4612 | 2233 | 0 | 9
38904.4614 | 2564 | 0 | 9
38904.4616 | 2569 | 0 | 9
38904.4618 | 1988 | 0 | 9
38904.462 | 2273 | 0 | 9
38904.4622 | 2506 | 0 | 9
38904.4455 | 1 | 0 | 10
38904.4457 | 1 | 0 | 10
38904.4459 | 1 | 0 | 10
38904.4461 | 1 | 0 | 10
38904.4463 | 1 | 0 | 10
38904.4465 | 1 | 0 | 10
38904.4467 | 2 | 0 | 10
38904.4468 | 1 | 0 | 10
38904.447 | 1 | 0 | 10
38904.4472 | 1 | 0 | 10
38904.4474 | 1 | 0 | 10
38904.4476 | 1 | 0 | 10
38904.4478 | 1 | 0 | 10
38904.448 | 1 | 0 | 10
38904.4482 | 1 | 0 | 10
38904.4484 | 1 | 0 | 10
38904.4486 | 1 | 0 | 10
38904.4488 | 1 | 0 | 10
38904.449 | 1 | 0 | 10
38904.4492 | 1 | 0 | 10
38904.4494 | 1 | 0 | 10
38904.4496 | 1 | 0 | 10
38904.4498 | 1 | 0 | 10
38904.45 | 1 | 0 | 10
38904.4502 | 1 | 0 | 10
38904.4503 | 1 | 0 | 10
38904.4505 | 1 | 0 | 10
38904.4507 | 1 | 0 | 10
38904.4509 | 1 | 0 | 10
38904.4511 | 1 | 0 | 10
38904.4513 | 1 | 0 | 10
38904.4515 | 1 | 0 | 10
38904.4517 | 1 | 0 | 10
38904.4519 | 1 | 0 | 10
38904.4521 | 1 | 0 | 10
38904.4523 | 1 | 0 | 10
38904.4525 | 1 | 0 | 10
38904.4527 | 1 | 0 | 10
38904.4529 | 1 | 0 | 10
38904.4531 | 1 | 0 | 10
38904.4533 | 1 | 0 | 10
38904.4535 | 1 | 0 | 10
38904.4536 | 1 | 0 | 10
38904.4538 | 1 | 0 | 10
38904.454 | 1 | 0 | 10
38904.4542 | 1 | 0 | 10
38904.4544 | 1 | 0 | 10
38904.4546 | 1 | 0 | 10
38904.4548 | 1 | 0 | 10
38904.455 | 2 | 0 | 10
38904.4552 | 11 | 0 | 10
38904.4554 | 11 | 0 | 10
38904.4556 | 11 | 0 | 10
38904.4558 | 10 | 0 | 10
38904.456 | 11 | 0 | 10
38904.4562 | 11 | 0 | 10
38904.4564 | 11 | 0 | 10
38904.4566 | 13 | 0 | 10
38904.4568 | 15 | 0 | 10
38904.457 | 14 | 0 | 10
38904.4572 | 14 | 0 | 10
38904.4573 | 14 | 0 | 10
38904.4575 | 13 | 0 | 10
38904.4577 | 32 | 2 | 10
38904.4579 | 2427 | 1 | 10
38904.4581 | 2155 | 0 | 10
38904.4583 | 2157 | 0 | 10
38904.4585 | 1997 | 0 | 10
38904.4587 | 1984 | 0 | 10
38904.4589 | 2070 | 0 | 10
38904.4591 | 2015 | 0 | 10
38904.4593 | 2013 | 0 | 10
38904.4595 | 2165 | 0 | 10
38904.4597 | 2480 | 0 | 10
38904.4599 | 2485 | 0 | 10
38904.4601 | 2555 | 0 | 10
38904.4603 | 2556 | 0 | 10
38904.4605 | 2012 | 0 | 10
38904.4606 | 2102 | 0 | 10
38904.4608 | 2517 | 0 | 10
38904.461 | 2348 | 0 | 10
38904.4612 | 2203 | 0 | 10
38904.4614 | 2117 | 0 | 10
38904.4616 | 2289 | 0 | 10
38904.4618 | 2109 | 0 | 10
38904.462 | 1967 | 0 | 10
38904.4622 | 2349 | 0 | 10
38904.4455 | 1 | 0 | 11
38904.4457 | 1 | 0 | 11
38904.4459 | 1 | 0 | 11
38904.4461 | 1 | 0 | 11
38904.4463 | 1 | 0 | 11
38904.4465 | 1 | 0 | 11
38904.4467 | 2 | 0 | 11
38904.4469 | 1 | 0 | 11
38904.4471 | 1 | 0 | 11
38904.4472 | 1 | 0 | 11
38904.4474 | 1 | 0 | 11
38904.4476 | 1 | 0 | 11
38904.4478 | 1 | 0 | 11
38904.448 | 1 | 0 | 11
38904.4482 | 1 | 0 | 11
38904.4484 | 1 | 0 | 11
38904.4486 | 1 | 0 | 11
38904.4488 | 1 | 0 | 11
38904.449 | 1 | 0 | 11
38904.4492 | 1 | 0 | 11
38904.4494 | 1 | 0 | 11
38904.4496 | 1 | 0 | 11
38904.4498 | 1 | 0 | 11
38904.45 | 1 | 0 | 11
38904.4502 | 1 | 0 | 11
38904.4504 | 1 | 0 | 11
38904.4506 | 1 | 0 | 11
38904.4508 | 1 | 0 | 11
38904.4509 | 1 | 0 | 11
38904.4511 | 1 | 0 | 11
38904.4513 | 1 | 0 | 11
38904.4515 | 1 | 0 | 11
38904.4517 | 1 | 0 | 11
38904.4519 | 1 | 0 | 11
38904.4521 | 1 | 0 | 11
38904.4523 | 1 | 0 | 11
38904.4525 | 1 | 0 | 11
38904.4527 | 1 | 0 | 11
38904.4529 | 1 | 0 | 11
38904.4531 | 1 | 0 | 11
38904.4533 | 1 | 0 | 11
38904.4535 | 2 | 0 | 11
38904.4537 | 1 | 0 | 11
38904.4539 | 1 | 0 | 11
38904.4541 | 1 | 0 | 11
38904.4542 | 1 | 0 | 11
38904.4544 | 1 | 0 | 11
38904.4546 | 1 | 0 | 11
38904.4548 | 1 | 0 | 11
38904.455 | 1959 | 0 | 11
38904.4552 | 2022 | 0 | 11
38904.4554 | 2227 | 0 | 11
38904.4556 | 2397 | 0 | 11
38904.4558 | 2172 | 0 | 11
38904.456 | 2359 | 0 | 11
38904.4562 | 2523 | 0 | 11
38904.4564 | 2025 | 0 | 11
38904.4566 | 2103 | 0 | 11
38904.4568 | 2087 | 0 | 11
38904.457 | 2072 | 0 | 11
38904.4572 | 2354 | 0 | 11
38904.4574 | 2041 | 0 | 11
38904.4576 | 2273 | 0 | 11
38904.4577 | 2120 | 1 | 11
38904.4579 | 2164 | 1 | 11
38904.4581 | 2325 | 0 | 11
38904.4583 | 2463 | 0 | 11
38904.4585 | 2181 | 0 | 11
38904.4587 | 2458 | 0 | 11
38904.4589 | 2198 | 0 | 11
38904.4591 | 2200 | 0 | 11
38904.4593 | 2218 | 0 | 11
38904.4595 | 2452 | 0 | 11
38904.4597 | 2045 | 0 | 11
38904.4599 | 2313 | 0 | 11
38904.4601 | 2158 | 0 | 11
38904.4603 | 2564 | 0 | 11
38904.4605 | 2530 | 0 | 11
38904.4607 | 2062 | 0 | 11
38904.4609 | 2206 | 0 | 11
38904.4611 | 2103 | 0 | 11
38904.4613 | 2466 | 0 | 11
38904.4614 | 2115 | 0 | 11
38904.4616 | 2369 | 0 | 11
38904.4618 | 2477 | 0 | 11
38904.462 | 2015 | 0 | 11
38904.4622 | 2292 | 0 | 11
38904.4455 | 1 | 0 | 12
38904.4457 | 1 | 0 | 12
38904.4459 | 1 | 0 | 12
38904.4461 | 1 | 0 | 12
38904.4463 | 1 | 0 | 12
38904.4465 | 1 | 0 | 12
38904.4467 | 1 | 0 | 12
38904.4469 | 1 | 0 | 12
38904.4471 | 1 | 0 | 12
38904.4473 | 1 | 0 | 12
38904.4475 | 1 | 0 | 12
38904.4477 | 1 | 0 | 12
38904.4478 | 1 | 0 | 12
38904.448 | 1 | 0 | 12
38904.4482 | 1 | 0 | 12
38904.4484 | 1 | 0 | 12
38904.4486 | 1 | 0 | 12
38904.4488 | 1 | 0 | 12
38904.449 | 1 | 0 | 12
38904.4492 | 1 | 0 | 12
38904.4494 | 1 | 0 | 12
38904.4496 | 1 | 0 | 12
38904.4498 | 1 | 0 | 12
38904.45 | 1 | 0 | 12
38904.4502 | 1 | 0 | 12
38904.4504 | 1 | 0 | 12
38904.4506 | 1 | 0 | 12
38904.4508 | 1 | 0 | 12
38904.451 | 1 | 0 | 12
38904.4512 | 1 | 0 | 12
38904.4514 | 1 | 0 | 12
38904.4515 | 1 | 0 | 12
38904.4517 | 1 | 0 | 12
38904.4519 | 1 | 0 | 12
38904.4521 | 1 | 0 | 12
38904.4523 | 1 | 0 | 12
38904.4525 | 1 | 0 | 12
38904.4527 | 1 | 0 | 12
38904.4529 | 1 | 0 | 12
38904.4531 | 1 | 0 | 12
38904.4533 | 1 | 0 | 12
38904.4535 | 1 | 0 | 12
38904.4537 | 1 | 0 | 12
38904.4539 | 1 | 0 | 12
38904.4541 | 1 | 0 | 12
38904.4543 | 1 | 0 | 12
38904.4545 | 1 | 0 | 12
38904.4547 | 1 | 0 | 12
38904.4548 | 1 | 0 | 12
38904.455 | 13 | 0 | 12
38904.4552 | 15 | 0 | 12
38904.4554 | 15 | 0 | 12
38904.4556 | 15 | 0 | 12
38904.4558 | 15 | 0 | 12
38904.456 | 15 | 0 | 12
38904.4562 | 14 | 0 | 12
38904.4564 | 15 | 0 | 12
38904.4566 | 15 | 0 | 12
38904.4568 | 15 | 0 | 12
38904.457 | 14 | 0 | 12
38904.4572 | 14 | 0 | 12
38904.4574 | 13 | 0 | 12
38904.4576 | 19 | 0 | 12
38904.4578 | 271 | 1 | 12
38904.458 | 2109 | 0 | 12
38904.4581 | 1987 | 0 | 12
38904.4583 | 2302 | 0 | 12
38904.4585 | 2145 | 0 | 12
38904.4587 | 2527 | 0 | 12
38904.4589 | 2243 | 0 | 12
38904.4591 | 1973 | 0 | 12
38904.4593 | 2261 | 0 | 12
38904.4595 | 2014 | 0 | 12
38904.4597 | 2198 | 0 | 12
38904.4599 | 2158 | 0 | 12
38904.4601 | 2488 | 0 | 12
38904.4603 | 2189 | 0 | 12
38904.4605 | 2177 | 0 | 12
38904.4607 | 2322 | 0 | 12
38904.4609 | 2094 | 0 | 12
38904.4611 | 2222 | 0 | 12
38904.4613 | 2011 | 0 | 12
38904.4615 | 1971 | 0 | 12
38904.4617 | 1998 | 0 | 12
38904.4619 | 2572 | 0 | 12
38904.462 | 2479 | 0 | 12
38904.4622 | 2013 | 0 | 12