## Test Facts
Last Row in IR Data sets: | 89
Power On | 105

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 6
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, PVC insulated, PVC jacketed, industrial grade General Cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 300C, nominal 6.1 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 105 seconds of baseline data monitoring. Special Note: Test setup and exposure conditions were identical to Penlight Tests 4 and 5.
DAQ Time | Penlight Time | Event | Interpretation
105 | 0 | Initiate Penlight Heating
881-886 | 776-781 | Conductor 2 shorts to ground at less than 100 ohms (4), then shorts to conductors 3 & 4 (20, 3) | First short circuit indications are between three conductors and ground
1068 | 963 | Conductor 3 shorts to ground at less than 1000 ohms (402)
1084-1090 | 979-985 | Conductors 3 & 4 short together: <100 ohms (21) and both short to ground (22, 23)
1093-1099 | 988-994 | Conductor 1 shorts to ground and to all of the other conductors at less than 100 ohms (2, 18, <1, & 21) | All conductors have shorted to ground at less than 100 ohms
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | The initial shorting fault occurred between an insulated conductor and ground rather than between the uninsulated drain wire and ground, and occurred 776 seconds after start of heating (vs. 590 seconds in Test 4, but close to the 766 seconds in Test 5).

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 6 |  |  | 2006-07-06 | 12:53
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-101.1667 | 255838 |  | -97.3333 | 256138 | -95.5 | 255838 | -93.6667 | 256138 | -101.1667 | 255838
-84.3333 | 255838 |  | -80.5 | 256138 | -78.6667 | 255838 | -76.8333 | 256138 | -84.3333 | 255838
-67.5 | 255838 |  | -63.8333 | 256138 | -62 | 255838 | -60 | 128119 | -67.5 | 128119
-50.6667 | 255838 |  | -47 | 128069 | -45 | 255838 | -43.3333 | 256138 | -50.6667 | 128069
-33.8333 | 255838 |  | -30.1667 | 256138 | -28.3333 | 255838 | -26.3333 | 256138 | -33.8333 | 255838
-17.1667 | 255838 |  | -13.3333 | 256138 | -11.5 | 255838 | -9.6667 | 63959.5 | -17.1667 | 63959.5
-0.33333 | 255838 |  | 3.5 | 256138 | 5.3333 | 255838 | 7.1667 | 256138 | -0.33333 | 255838
16.5 | 255838 |  | 20.1667 | 256138 | 22 | 255838 | 24 | 256138 | 16.5 | 255838
33.3333 | 255838 |  | 37 | 256138 | 39 | 255838 | 40.6667 | 256138 | 33.3333 | 255838
50 | 128019 |  | 53.8333 | 128019 | 55.6667 | 127869 | 57.5 | 256138 | 50 | 127869
66.8333 | 255838 |  | 70.6667 | 256138 | 72.5 | 255838 | 74.3333 | 256138 | 66.8333 | 255838
83.5 | 255838 |  | 87.3333 | 256138 | 89.3333 | 255838 | 91.1667 | 256138 | 83.5 | 255838
100.5 | 255838 |  | 104.1667 | 256138 | 106 | 128169 | 108 | 256138 | 100.5 | 128169
117.3333 | 255838 |  | 121 | 256138 | 123 | 255838 | 124.6667 | 256138 | 117.3333 | 255838
134.1667 | 255838 |  | 137.8333 | 256138 | 139.6667 | 255838 | 141.6667 | 256138 | 134.1667 | 255838
150.8333 | 128119 |  | 154.6667 | 256138 | 156.5 | 255838 | 158.3333 | 128169 | 150.8333 | 128119
167.6667 | 255838 |  | 171.3333 | 128069 | 173.1667 | 255838 | 175.1667 | 256138 | 167.6667 | 128069
184.3333 | 255838 |  | 188.1667 | 256138 | 190.1667 | 255838 | 192 | 256138 | 184.3333 | 255838
201.3333 | 255838 |  | 204.8333 | 256138 | 206.8333 | 255838 | 208.6667 | 256138 | 201.3333 | 255838
218 | 255838 |  | 221.8333 | 256138 | 223.6667 | 128169 | 225.5 | 256138 | 218 | 128169
234.6667 | 255838 |  | 238.6667 | 256138 | 240.3333 | 255838 | 242.3333 | 256138 | 234.6667 | 255838
251.6667 | 255838 |  | 255.5 | 256138 | 257.3333 | 255838 | 259.1667 | 256138 | 251.6667 | 255838
268.5 | 255838 |  | 272.1667 | 256138 | 274 | 255838 | 276 | 256138 | 268.5 | 255838
285.1667 | 255838 |  | 289 | 256138 | 290.8333 | 255838 | 292.6667 | 256138 | 285.1667 | 255838
302 | 255838 |  | 305.6667 | 256138 | 307.6667 | 255838 | 309.6667 | 256138 | 302 | 255838
318.8333 | 255838 |  | 322.5 | 256138 | 324.5 | 255838 | 326.1667 | 256138 | 318.8333 | 255838
335.6667 | 255838 |  | 339.5 | 256138 | 341.1667 | 255838 | 343 | 256138 | 335.6667 | 255838
352.5 | 255838 |  | 356.1667 | 256138 | 358 | 255838 | 360 | 256138 | 352.5 | 255838
369.1667 | 255838 |  | 373 | 256138 | 374.8333 | 255838 | 376.6667 | 256138 | 369.1667 | 255838
385.8333 | 255838 |  | 389.6667 | 256138 | 391.6667 | 255838 | 393.5 | 256138 | 385.8333 | 255838
402.8333 | 255838 |  | 406.5 | 256138 | 408.5 | 255838 | 410.1667 | 256138 | 402.8333 | 255838
419.5 | 255838 |  | 423.3333 | 128069 | 425.1667 | 255838 | 427 | 256138 | 419.5 | 128069
436.5 | 255838 |  | 440 | 256138 | 442 | 255838 | 443.8333 | 256138 | 436.5 | 255838
453.3333 | 255838 |  | 456.8333 | 256138 | 458.8333 | 255838 | 460.6667 | 256138 | 453.3333 | 255838
470 | 255838 |  | 473.6667 | 256138 | 475.5 | 255838 | 477.5 | 256138 | 470 | 255838
486.8333 | 255838 |  | 490.5 | 256138 | 492.5 | 255838 | 494.1667 | 256138 | 486.8333 | 255838
503.5 | 255838 |  | 507.1667 | 256138 | 509.1667 | 255838 | 511.1667 | 256138 | 503.5 | 255838
520.3333 | 255838 |  | 524 | 256138 | 526 | 127869 | 527.6667 | 256138 | 520.3333 | 127869
537.3333 | 255838 |  | 540.8333 | 256138 | 542.8333 | 255838 | 544.6667 | 128019 | 537.3333 | 128019
553.8333 | 255838 |  | 557.6667 | 256138 | 559.5 | 255838 | 561.3333 | 128119 | 553.8333 | 128119
570.6667 | 255838 |  | 574.6667 | 256138 | 576.3333 | 255838 | 578.3333 | 256138 | 570.6667 | 255838
587.5 | 255838 |  | 591.1667 | 256138 | 593.1667 | 255838 | 595.1667 | 256138 | 587.5 | 255838
604.3333 | 255838 |  | 608 | 256138 | 610 | 127869 | 611.6667 | 256138 | 604.3333 | 127869
621.1667 | 255838 |  | 624.8333 | 256138 | 626.6667 | 255838 | 628.6667 | 256138 | 621.1667 | 255838
637.8333 | 255838 |  | 641.6667 | 256138 | 643.5 | 255838 | 645.3333 | 256138 | 637.8333 | 255838
654.6667 | 255838 |  | 658.6667 | 256138 | 660.3333 | 255838 | 662.3333 | 256138 | 654.6667 | 255838
671.5 | 255838 |  | 675.1667 | 256138 | 677 | 255838 | 679 | 256138 | 671.5 | 255838
688.3333 | 255838 |  | 692 | 256138 | 694 | 255838 | 695.6667 | 256138 | 688.3333 | 255838
705.1667 | 255838 |  | 708.8333 | 256138 | 710.6667 | 255838 | 712.6667 | 256138 | 705.1667 | 255838
721.8333 | 255838 |  | 725.6667 | 256138 | 727.5 | 255838 | 729.3333 | 256138 | 721.8333 | 255838
738.6667 | 255838 |  | 742.5 | 256138 | 744.3333 | 255838 | 746.1667 | 256138 | 738.6667 | 255838
755.5 | 255838 |  | 759.1667 | 256138 | 761 | 255838 | 763 | 256138 | 755.5 | 255838
772.3333 | 31892.25 |  | 776 | 4.3739 | 778 | 25533.8 | 779.6667 | 25523.8 | 772.3333 | 4.3739
789.1667 | 23167.0909 |  | 792.8333 | 0.9606 | 794.6667 | 25533.8 | 796.6667 | 25523.8 | 789.1667 | 0.9606
805.8333 | 25493.8 |  | 809.6667 | 1.8427 | 811.5 | 23203.4545 | 813.3333 | 23194.3636 | 805.8333 | 1.8427
822.6667 | 25493.8 |  | 826.5 | 5.9711 | 828.3333 | 23203.4545 | 830.1667 | 23194.3636 | 822.6667 | 5.9711
839.5 | 25493.8 |  | 843.1667 | 10.4429 | 845 | 21261.5 | 847 | 25523.8 | 839.5 | 10.4429
856.3333 | 23167.0909 |  | 860 | 3.3218 | 862 | 23203.4545 | 863.6667 | 21253.1667 | 856.3333 | 3.3218
873.1667 | 23167.0909 |  | 876.8333 | 1.8839 | 878.6667 | 21261.5 | 880.6667 | 23194.3636 | 873.1667 | 1.8839
889.8333 | 21228.1667 |  | 893.6667 | 18.2455 | 895.5 | 19618.3077 | 897.3333 | 19610.6154 | 889.8333 | 18.2455
906.6667 | 19587.5385 |  | 910.5 | 10.9736 | 912.3333 | 9394 | 914.1667 | 23194.3636 | 906.6667 | 10.9736
923.5 | 23167.0909 |  | 927.1667 | 2.5362 | 929 | 6477.8974 | 931 | 19610.6154 | 923.5 | 2.5362
940.3333 | 23167.0909 |  | 944 | 2.3724 | 946 | 358.5653 | 947.6667 | 19610.6154 | 940.3333 | 2.3724
957.1667 | 21228.1667 |  | 960.8333 | 12.8305 | 962.6667 | 401.8392 | 964.6667 | 21253.1667 | 957.1667 | 12.8305
973.8333 | 17086.3066 |  | 977.6667 | 3.3218 | 979.5 | 22.4525 | 981.3333 | 23.4543 | 973.8333 | 3.3218
990.6667 | 1.6838 |  | 994.5 | 10.3523 | 996.3333 | 8.0228 | 998.1667 | 11.2047 | 990.6667 | 1.6838
1007.5 | 2.5362 |  | 1011.1667 | 4.1195 | 1013 | 2.6152 | 1015 | 10.2441 | 1007.5 | 2.5362
1024.3333 | 5.585 |  | 1028 | 2.1683 | 1030 | 1.2384 | 1031.6667 | 1.8824 | 1024.3333 | 1.2384
1041.1667 | 1.5206 |  | 1044.8333 | 0.9606 | 1046.6667 | 8.016 | 1048.6667 | 2.6152 | 1041.1667 | 0.9606
1057.8333 | 2.6162 |  | 1061.6667 | 1.36 | 1063.5 | 1.9267 | 1065.3333 | 0.76209 | 1057.8333 | 0.76209
1074.6667 | 5.4911 |  | 1078.5 | 0.64336 | 1080.3333 | 12.8632 | 1082.1667 | 2.5742 | 1074.6667 | 0.64336
1091.3333 | 0.64286 |  | 1095.1667 | 20.7531 | 1097 | 4.8806 | 1098.8333 | 2.2498 | 1091.3333 | 0.64286
1108.3333 | 3.0761 |  | 1112 | 1.1998 | 1114 | 15.4536 | 1115.6667 | 0.64336 | 1108.3333 | 0.64336
1125.1667 | 1.4804 |  | 1128.8333 | 1.5206 | 1130.6667 | 13.9156 | 1132.6667 | 7.2065 | 1125.1667 | 1.4804
1141.8333 | 11.9328 |  | 1145.6667 | 7.2126 | 1147.5 | 0.96174 | 1149.3333 | 4.1567 | 1141.8333 | 0.96174
1158.6667 | 4.8497 |  | 1162.5 | 0.68264 | 1164.3333 | 17.1406 | 1166.1667 | 5.2248 | 1158.6667 | 0.68264
1175.5 | 10.8775 |  | 1179.1667 | 1.8434 | 1181 | 14.0294 | 1183 | 7.2126 | 1175.5 | 1.8434
1192.3333 | 6.4191 |  | 1196 | 1.12 | 1198 | 0.64311 | 1199.6667 | 12.2705 | 1192.3333 | 0.64311
1209.1667 | 3.9505 |  | 1212.8333 | 1.3199 | 1214.6667 | 6.5411 | 1216.6667 | 2.2879 | 1209.1667 | 1.3199
1225.8333 | 5.8397 |  | 1229.6667 | 7.4792 | 1231.5 | 2.3287 | 1233.3333 | 0.6426 | 1225.8333 | 0.6426
1242.6667 | 5.281 |  | 1246.5 | 12.4838 | 1248.3333 | 0.72163 | 1250.1667 | 7.7018 | 1242.6667 | 0.72163
1259.5 | 2.6627 |  | 1263.1667 | 0.84107 | 1265 | 3.2788 | 1267 | 6.8937 | 1259.5 | 0.84107
1276.3333 | 7.8443 |  | 1280 | 1.6811 | 1282 | 3.3594 | 1283.6667 | 7.6986 | 1276.3333 | 1.6811
1293.1667 | 0.64412 |  | 1296.8333 | 6.9412 | 1298.6667 | 3.7867 | 1300.6667 | 2.8621 | 1293.1667 | 0.64412

## C-C
Conductor to Conductor Resistances
Penlight Test 6 |  |  | 2006-07-06 | 12:53
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-104 | 256137.9994 | -101 | 255837.9994 | -98.5 | 256337.9994 | -95.5 | 256237.9994 | -92.5 | 256137.9994 | -90 | 256437.9994 | -104 | 255837.9994
-87 | 256137.9994 | -84.5 | 255837.9994 | -81.5 | 256337.9994 | -78.5 | 256237.9994 | -76 | 256137.9994 | -73 | 256437.9994 | -87 | 255837.9994
-70.5 | 256137.9994 | -67.5 | 255837.9994 | -64.5 | 256337.9994 | -62 | 256237.9994 | -59 | 256137.9994 | -56.5 | 256437.9994 | -70.5 | 255837.9994
-53.5 | 256137.9994 | -50.5 | 255837.9994 | -48 | 256337.9994 | -45 | 128068.9988 | -42.5 | 256137.9994 | -39.5 | 256437.9994 | -53.5 | 128068.9988
-36.5 | 256137.9994 | -34 | 255837.9994 | -31 | 256337.9994 | -28.5 | 256237.9994 | -25.5 | 256137.9994 | -22.5 | 256437.9994 | -36.5 | 255837.9994
-20 | 256137.9994 | -17 | 255837.9994 | -14.5 | 256337.9994 | -11.5 | 256237.9994 | -8.5 | 256137.9994 | -6 | 256437.9994 | -20 | 255837.9994
-3 | 256137.9994 | -0.5 | 255837.9994 | 2.5 | 256337.9994 | 5.5 | 256237.9994 | 8 | 256137.9994 | 11 | 256437.9994 | -3 | 255837.9994
13.5 | 256137.9994 | 16.5 | 255837.9994 | 19.5 | 256337.9994 | 22 | 256237.9994 | 25 | 256137.9994 | 27.5 | 256437.9994 | 13.5 | 255837.9994
30.5 | 256137.9994 | 33.5 | 255837.9994 | 36 | 256337.9994 | 39 | 256237.9994 | 41.5 | 256137.9994 | 44.5 | 256437.9994 | 30.5 | 255837.9994
47.5 | 128018.9988 | 50 | 255837.9994 | 52.5 | 256337.9994 | 55.5 | 256237.9994 | 58.5 | 256137.9994 | 61.5 | 256437.9994 | 47.5 | 128018.9988
64 | 256137.9994 | 67 | 255837.9994 | 69.5 | 256337.9994 | 72.5 | 256237.9994 | 75.5 | 256137.9994 | 78 | 256437.9994 | 64 | 255837.9994
80.5 | 256137.9994 | 83.5 | 255837.9994 | 86.5 | 256337.9994 | 89.5 | 256237.9994 | 92 | 255938.0781 | 95 | 256437.9994 | 80.5 | 255837.9994
97.5 | 256137.9994 | 100.5 | 255837.9994 | 103.5 | 256337.9994 | 106 | 256237.9994 | 109 | 256137.9994 | 111.5 | 128168.9988 | 97.5 | 128168.9988
114.5 | 255938.0781 | 117.5 | 255837.9994 | 120 | 256337.9994 | 123 | 256237.9994 | 125.5 | 256137.9994 | 128.5 | 256437.9994 | 114.5 | 255837.9994
131.5 | 256137.9994 | 134 | 255837.9994 | 137 | 256337.9994 | 139.5 | 256237.9994 | 142.5 | 256137.9994 | 145.5 | 256437.9994 | 131.5 | 255837.9994
148 | 256137.9994 | 151 | 255837.9994 | 153.5 | 128118.9988 | 156.5 | 256237.9994 | 159.5 | 256137.9994 | 162 | 256437.9994 | 148 | 128118.9988
165 | 255938.0781 | 167.5 | 255837.9994 | 170.5 | 256337.9994 | 173 | 128068.9988 | 176 | 256137.9994 | 179 | 256437.9994 | 165 | 128068.9988
181.5 | 256137.9994 | 184.5 | 255837.9994 | 187 | 256337.9994 | 190 | 256237.9994 | 193 | 256137.9994 | 196 | 256437.9994 | 181.5 | 255837.9994
198.5 | 256137.9994 | 201.5 | 255837.9994 | 204 | 256337.9994 | 206.5 | 256237.9994 | 209.5 | 256137.9994 | 212.5 | 256437.9994 | 198.5 | 255837.9994
215.5 | 256137.9994 | 218 | 255837.9994 | 220.5 | 256337.9994 | 223.5 | 256237.9994 | 226.5 | 256137.9994 | 229.5 | 128168.9988 | 215.5 | 128168.9988
232 | 256137.9994 | 234.5 | 255837.9994 | 237.5 | 256337.9994 | 240.5 | 256237.9994 | 243.5 | 256137.9994 | 246 | 256437.9994 | 232 | 255837.9994
249 | 256137.9994 | 251.5 | 255837.9994 | 254.5 | 256337.9994 | 257.5 | 256237.9994 | 260 | 256137.9994 | 263 | 256437.9994 | 249 | 255837.9994
265.5 | 256137.9994 | 268.5 | 255837.9994 | 271.5 | 256337.9994 | 274 | 256237.9994 | 277 | 256137.9994 | 279.5 | 256437.9994 | 265.5 | 255837.9994
282.5 | 256137.9994 | 285 | 255837.9994 | 288 | 256337.9994 | 291 | 256237.9994 | 293.5 | 256137.9994 | 296.5 | 256437.9994 | 282.5 | 255837.9994
299 | 256137.9994 | 302 | 255837.9994 | 305 | 256337.9994 | 307.5 | 256237.9994 | 310.5 | 256137.9994 | 313.5 | 256437.9994 | 299 | 255837.9994
316 | 256137.9994 | 319 | 255837.9994 | 321.5 | 256337.9994 | 324.5 | 256237.9994 | 327 | 256137.9994 | 330 | 256437.9994 | 316 | 255837.9994
333 | 255938.0781 | 335.5 | 255837.9994 | 338.5 | 256337.9994 | 341.5 | 256237.9994 | 344 | 256137.9994 | 346.5 | 256437.9994 | 333 | 255837.9994
349.5 | 256137.9994 | 352.5 | 255837.9994 | 355.5 | 256337.9994 | 358 | 256237.9994 | 361 | 256137.9994 | 363.5 | 256437.9994 | 349.5 | 255837.9994
366.5 | 256137.9994 | 369 | 255837.9994 | 372 | 256337.9994 | 375 | 256237.9994 | 377.5 | 256137.9994 | 380.5 | 256437.9994 | 366.5 | 255837.9994
383 | 256137.9994 | 386 | 255837.9994 | 388.5 | 256337.9994 | 391.5 | 256237.9994 | 394.5 | 256137.9994 | 397.5 | 256437.9994 | 383 | 255837.9994
400 | 256137.9994 | 403 | 255837.9994 | 405.5 | 256337.9994 | 408.5 | 256237.9994 | 411 | 256137.9994 | 414 | 256437.9994 | 400 | 255837.9994
416.5 | 256137.9994 | 419.5 | 255837.9994 | 422.5 | 256337.9994 | 425.5 | 128068.9988 | 428 | 256137.9994 | 430.5 | 256437.9994 | 416.5 | 128068.9988
433.5 | 256137.9994 | 436.5 | 255837.9994 | 439.5 | 256337.9994 | 442 | 256237.9994 | 444.5 | 256137.9994 | 447.5 | 256437.9994 | 433.5 | 255837.9994
450.5 | 256137.9994 | 453.5 | 255837.9994 | 456 | 256337.9994 | 458.5 | 256237.9994 | 461.5 | 256137.9994 | 464.5 | 256437.9994 | 450.5 | 255837.9994
467 | 256137.9994 | 470 | 255837.9994 | 473 | 256337.9994 | 475.5 | 256237.9994 | 478.5 | 256137.9994 | 481 | 256437.9994 | 467 | 255837.9994
484 | 256137.9994 | 487 | 255837.9994 | 489.5 | 256337.9994 | 492.5 | 256237.9994 | 495 | 256137.9994 | 498 | 256437.9994 | 484 | 255837.9994
500.5 | 256137.9994 | 503.5 | 255837.9994 | 506.5 | 256337.9994 | 509 | 256237.9994 | 512 | 256137.9994 | 515 | 256437.9994 | 500.5 | 255837.9994
517.5 | 256137.9994 | 520.5 | 255837.9994 | 523 | 256337.9994 | 526 | 256237.9994 | 528.5 | 256137.9994 | 531.5 | 256437.9994 | 517.5 | 255837.9994
534.5 | 256137.9994 | 537.5 | 255837.9994 | 540 | 256337.9994 | 542.5 | 256237.9994 | 545.5 | 256137.9994 | 548.5 | 256437.9994 | 534.5 | 255837.9994
551 | 256137.9994 | 554 | 255837.9994 | 556.5 | 256337.9994 | 559.5 | 256237.9994 | 562.5 | 256137.9994 | 565 | 256437.9994 | 551 | 255837.9994
568 | 256137.9994 | 570.5 | 255837.9994 | 573.5 | 256337.9994 | 576.5 | 256237.9994 | 579.5 | 256137.9994 | 582 | 256437.9994 | 568 | 255837.9994
584.5 | 256137.9994 | 587.5 | 255837.9994 | 590.5 | 256337.9994 | 593 | 256237.9994 | 596 | 256137.9994 | 599 | 256437.9994 | 584.5 | 255837.9994
601.5 | 256137.9994 | 604.5 | 255837.9994 | 607 | 256337.9994 | 610 | 256237.9994 | 612.5 | 256137.9994 | 615.5 | 256437.9994 | 601.5 | 255837.9994
618.5 | 256137.9994 | 621 | 255837.9994 | 624 | 256337.9994 | 626.5 | 256237.9994 | 629.5 | 256137.9994 | 632.5 | 256437.9994 | 618.5 | 255837.9994
635 | 256137.9994 | 638 | 255837.9994 | 640.5 | 256337.9994 | 643.5 | 256237.9994 | 646.5 | 256137.9994 | 649 | 256437.9994 | 635 | 255837.9994
652 | 256137.9994 | 654.5 | 255837.9994 | 657.5 | 256337.9994 | 660.5 | 256237.9994 | 663.5 | 256137.9994 | 666 | 256437.9994 | 652 | 255837.9994
668.5 | 256137.9994 | 671.5 | 255837.9994 | 674.5 | 256337.9994 | 677 | 256237.9994 | 680 | 256137.9994 | 682.5 | 256437.9994 | 668.5 | 255837.9994
685.5 | 256137.9994 | 688.5 | 255837.9994 | 691 | 256337.9994 | 694 | 256237.9994 | 696.5 | 256137.9994 | 699.5 | 256437.9994 | 685.5 | 255837.9994
702.5 | 256137.9994 | 705 | 255837.9994 | 708 | 256337.9994 | 710.5 | 256237.9994 | 713.5 | 256137.9994 | 716.5 | 256437.9994 | 702.5 | 255837.9994
719 | 256137.9994 | 722 | 255837.9994 | 724.5 | 256337.9994 | 727.5 | 256237.9994 | 730.5 | 256137.9994 | 733 | 256437.9994 | 719 | 255837.9994
736 | 256137.9994 | 738.5 | 255837.9994 | 741.5 | 256337.9994 | 744.5 | 256237.9994 | 747 | 256137.9994 | 750 | 256437.9994 | 736 | 255837.9994
752.5 | 256137.9994 | 755.5 | 255837.9994 | 758.5 | 256337.9994 | 761 | 256237.9994 | 764 | 256137.9994 | 766.5 | 256437.9994 | 752.5 | 255837.9994
769.5 | 256137.9994 | 772.5 | 31892.2451 | 775 | 85379.3315 | 778 | 19.5047 | 780.5 | 2.8752 | 783.5 | 31967.2451 | 769.5 | 2.8752
786.5 | 51147.5969 | 789 | 23167.0842 | 792 | 42639.663 | 794.5 | 7.7395 | 797.5 | 3.1779 | 800.5 | 25553.7939 | 786.5 | 3.1779
803 | 31929.7451 | 806 | 25493.7939 | 808.5 | 36533.9957 | 811.5 | 0.30604 | 814.5 | 13.8048 | 817 | 25553.7939 | 803 | 0.30604
820 | 31929.7451 | 822.5 | 25493.7939 | 825.5 | 31954.7451 | 828.5 | 16.4192 | 831 | 4.4949 | 834 | 25553.7939 | 820 | 4.4949
836.5 | 31929.7451 | 839.5 | 25493.7939 | 842.5 | 31954.7451 | 845 | 9.0259 | 848 | 27.6787 | 850.5 | 25553.7939 | 836.5 | 9.0259
853.5 | 36505.4243 | 856.5 | 23167.0842 | 859 | 31954.7451 | 862 | 27.0775 | 864.5 | 6.21 | 867.5 | 28404.2167 | 853.5 | 6.21
870.5 | 31929.7451 | 873 | 23167.0842 | 876 | 31954.7451 | 878.5 | 13.3801 | 881.5 | 0.34849 | 884.5 | 25553.7939 | 870.5 | 0.34849
887 | 31929.7451 | 890 | 21228.1593 | 892.5 | 31954.7451 | 895.5 | 22.2696 | 898.5 | 16.9225 | 901 | 21278.1593 | 887 | 16.9225
904 | 31929.7451 | 906.5 | 19587.5305 | 909.5 | 23212.5387 | 912.5 | 11.237 | 915 | 23.6811 | 918 | 21278.1593 | 904 | 11.237
920.5 | 28370.8834 | 923.5 | 23167.0842 | 926.5 | 31954.7451 | 929 | 3.6543 | 932 | 1.0106 | 934.5 | 6477.8736 | 920.5 | 1.0106
937.5 | 28370.8834 | 940.5 | 23167.0842 | 943 | 28393.1056 | 946 | 2.358 | 948.5 | 24.5483 | 951.5 | 14152.1001 | 937.5 | 2.358
954.5 | 28370.8834 | 957 | 21228.1593 | 960 | 28393.1056 | 962.5 | 21.1962 | 965.5 | 27.6787 | 968.5 | 3275.4536 | 954.5 | 21.1962
971 | 28370.8834 | 974 | 25493.7939 | 976.5 | 35607.4428 | 979.5 | 19.4472 | 982.5 | 1.8077 | 985 | 21.1735 | 971 | 1.8077
988 | 17.7559 | 990.5 | 0.14712 | 993.5 | 20.7139 | 996.5 | 10.9871 | 999 | 14.278 | 1002 | 21.8266 | 988 | 0.14712
1004.5 | 1.0106 | 1007.5 | 3.534 | 1010.5 | 26.2259 | 1013 | 30.8113 | 1016 | 7.2747 | 1018.5 | 1.0889 | 1004.5 | 1.0106
1021.5 | 12.6638 | 1024.5 | 4.1051 | 1027 | 17.9609 | 1030 | 0.71838 | 1032.5 | 30.3498 | 1035.5 | 0.30865 | 1021.5 | 0.30865
1038.5 | 0.020301 | 1041 | 0.18815 | 1044 | 27.8448 | 1046.5 | 3.2187 | 1049.5 | 30.2817 | 1052.5 | 6.5661 | 1038.5 | 0.020301
1055 | 1.8923 | 1058 | 17.9527 | 1060.5 | 1.0906 | 1063.5 | 20.9601 | 1066.5 | 0.18338 | 1069 | 27.568 | 1055 | 0.18338
1072 | 4.0082 | 1074.5 | 27.7898 | 1077.5 | 4.8004 | 1080.5 | 0.8717 | 1083 | 29.8069 | 1086 | 11.4755 | 1072 | 0.8717
1088.5 | 4.8068 | 1091.5 | 15.8544 | 1094 | 0.9127 | 1097 | 20.725 | 1100 | 23.0688 | 1102.5 | 3.3873 | 1088.5 | 0.9127
1105.5 | 13.9621 | 1108.5 | 1.5602 | 1111 | 28.9689 | 1114 | 4.2259 | 1116.5 | 0.34595 | 1119.5 | 14.0971 | 1105.5 | 0.34595
1122.5 | 0.061118 | 1125 | 18.2907 | 1128 | 0.18167 | 1130.5 | 23.6068 | 1133.5 | 15.1823 | 1136.5 | 12.5408 | 1122.5 | 0.061118
1139 | 25.1749 | 1142 | 13.6177 | 1144.5 | 10.5341 | 1147.5 | 22.39 | 1150.5 | 29.2684 | 1153 | 19.4839 | 1139 | 10.5341
1156 | 12.5099 | 1158.5 | 3.3594 | 1161.5 | 17.4026 | 1164.5 | 0.8717 | 1167 | 29.3355 | 1170 | 15.8036 | 1156 | 0.8717
1172.5 | 9.4667 | 1175.5 | 17.2822 | 1178.5 | 23.5941 | 1181 | 13.5362 | 1184 | 0.30738 | 1186.5 | 22.1857 | 1172.5 | 0.30738
1189.5 | 11.093 | 1192.5 | 4.9509 | 1195 | 27.7138 | 1198 | 11.0869 | 1200.5 | 0.42704 | 1203.5 | 22.7282 | 1189.5 | 0.42704
1206.5 | 2.4456 | 1209 | 29.721 | 1212 | 2.6125 | 1214.5 | 6.3898 | 1217.5 | 0.22407 | 1220.5 | 15.9662 | 1206.5 | 0.22407
1223 | 4.3617 | 1226 | 24.5881 | 1228.5 | 712.3548 | 1231.5 | 6.0232 | 1234.5 | 10.3481 | 1237 | 0.79815 | 1223 | 0.79815
1240 | 18.3744 | 1242.5 | 3.7968 | 1245.5 | 24.6464 | 1248.5 | 25.9847 | 1251 | 11.093 | 1254 | 0.83331 | 1240 | 0.83331
1256.5 | 13.4393 | 1259.5 | 1.1407 | 1262.5 | 21.7786 | 1265 | 0.71082 | 1268 | 29.8745 | 1270.5 | 9.3054 | 1256.5 | 0.71082
1273.5 | 6.3937 | 1276.5 | 21.9568 | 1279 | 21.5404 | 1282 | 0.14201 | 1284.5 | 27.5479 | 1287.5 | 1.8441 | 1273.5 | 0.14201
1290.5 | 21.9814 | 1293 | 0.90838 | 1296 | 0.18567 | 1298.5 | 5.4778 | 1301.5 | 6.902 | 1304.5 | 22.4262 | 1290.5 | 0.18567

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5
0 | -105 | 29.0817 | 26.1133 | 26.185 | 26.0444 | 25.9916 | 25.586
0.661 | -104.339 | 29.0887 | 26.1078 | 26.1753 | 26.0488 | 25.9854 | 25.5839
1.5122 | -103.4878 | 29.0839 | 26.1077 | 26.1749 | 26.0451 | 25.99 | 25.5839
2.5136 | -102.4864 | 29.0865 | 26.1032 | 26.169 | 26.0423 | 25.9829 | 25.5804
3.5151 | -101.4849 | 29.0876 | 26.1017 | 26.1732 | 26.0455 | 25.9826 | 25.586
4.5165 | -100.4835 | 29.088 | 26.1059 | 26.1767 | 26.0433 | 25.9776 | 25.5855
5.5179 | -99.4821 | 29.0871 | 26.1023 | 26.1711 | 26.0425 | 25.9756 | 25.5835
6.5194 | -98.4806 | 29.0895 | 26.0985 | 26.1787 | 26.0416 | 25.9763 | 25.5776
7.5108 | -97.4892 | 29.0853 | 26.1045 | 26.1795 | 26.0448 | 25.9774 | 25.5786
8.5122 | -96.4878 | 29.0907 | 26.1028 | 26.1752 | 26.0353 | 25.965 | 25.5812
9.5137 | -95.4863 | 29.0912 | 26.102 | 26.1751 | 26.0458 | 25.973 | 25.5799
10.5151 | -94.4849 | 29.0892 | 26.1055 | 26.1763 | 26.0404 | 25.9744 | 25.5818
11.5166 | -93.4834 | 29.096 | 26.1074 | 26.1695 | 26.0461 | 25.9683 | 25.5827
12.518 | -92.482 | 29.0909 | 26.1024 | 26.1743 | 26.0415 | 25.9793 | 25.5777
13.5194 | -91.4806 | 29.0929 | 26.103 | 26.1713 | 26.0437 | 25.9624 | 25.5818
14.5209 | -90.4791 | 29.0969 | 26.1025 | 26.165 | 26.0395 | 25.9655 | 25.5837
15.5123 | -89.4877 | 29.0981 | 26.1044 | 26.1709 | 26.0367 | 25.9669 | 25.5786
16.5137 | -88.4863 | 29.0903 | 26.1012 | 26.1677 | 26.0358 | 25.9554 | 25.58
17.5152 | -87.4848 | 29.0865 | 26.0994 | 26.1656 | 26.0382 | 25.9543 | 25.5789
18.5166 | -86.4834 | 29.0924 | 26.1006 | 26.1647 | 26.0425 | 25.9497 | 25.5747
19.5181 | -85.4819 | 29.0884 | 26.0986 | 26.1653 | 26.041 | 25.9533 | 25.5732
20.5195 | -84.4805 | 29.0881 | 26.0993 | 26.1625 | 26.0292 | 25.9469 | 25.5784
21.5209 | -83.4791 | 29.0801 | 26.1011 | 26.1676 | 26.0341 | 25.9497 | 25.5727
22.5124 | -82.4876 | 29.0883 | 26.0985 | 26.1465 | 26.0361 | 25.9574 | 25.5719
23.5138 | -81.4862 | 29.0892 | 26.1005 | 26.1682 | 26.042 | 25.9578 | 25.5732
24.5153 | -80.4847 | 29.0856 | 26.1005 | 26.154 | 26.0368 | 25.9519 | 25.5758
25.5167 | -79.4833 | 29.0941 | 26.0988 | 26.1519 | 26.0421 | 25.9545 | 25.5793
26.5181 | -78.4819 | 29.0892 | 26.0946 | 26.1748 | 26.0341 | 25.9405 | 25.5772
27.5196 | -77.4804 | 29.0823 | 26.0962 | 26.1622 | 26.0358 | 25.9445 | 25.5788
28.511 | -76.489 | 29.0799 | 26.0969 | 26.1651 | 26.0346 | 25.933 | 25.5781
29.5225 | -75.4775 | 29.0798 | 26.0995 | 26.1606 | 26.0383 | 25.9452 | 25.5731
30.5139 | -74.4861 | 29.0827 | 26.0935 | 26.1548 | 26.0335 | 25.9371 | 25.5735
31.5153 | -73.4847 | 29.0749 | 26.0952 | 26.157 | 26.0289 | 25.9396 | 25.5821
32.5168 | -72.4832 | 29.0764 | 26.0926 | 26.161 | 26.0364 | 25.9312 | 25.5858
33.5182 | -71.4818 | 29.0728 | 26.0927 | 26.1537 | 26.0362 | 25.9441 | 25.576
34.5196 | -70.4804 | 29.0761 | 26.0928 | 26.1505 | 26.0392 | 25.9283 | 25.5794
35.5211 | -69.4789 | 29.0711 | 26.0913 | 26.1536 | 26.0288 | 25.9333 | 25.5747
36.5125 | -68.4875 | 29.0715 | 26.0958 | 26.1588 | 26.0318 | 25.9246 | 25.5803
37.5139 | -67.4861 | 29.0687 | 26.0904 | 26.1481 | 26.0261 | 25.9229 | 25.5772
38.5955 | -66.4045 | 29.0709 | 26.094 | 26.1532 | 26.0284 | 25.9214 | 25.5729
39.5469 | -65.4531 | 29.0726 | 26.0922 | 26.1528 | 26.0283 | 25.9158 | 25.5822
40.5183 | -64.4817 | 29.0761 | 26.095 | 26.149 | 26.0272 | 25.9152 | 25.5712
41.5197 | -63.4803 | 29.0769 | 26.092 | 26.1491 | 26.0254 | 25.9295 | 25.5817
42.5211 | -62.4789 | 29.0721 | 26.0916 | 26.1576 | 26.0288 | 25.9156 | 25.5775
43.5126 | -61.4874 | 29.0774 | 26.0922 | 26.1556 | 26.0296 | 25.9183 | 25.5743
44.514 | -60.486 | 29.0731 | 26.0981 | 26.153 | 26.024 | 25.9264 | 25.5755
45.5154 | -59.4846 | 29.0723 | 26.0871 | 26.1562 | 26.021 | 25.9114 | 25.5801
46.5169 | -58.4831 | 29.0741 | 26.0933 | 26.153 | 26.0256 | 25.9145 | 25.5823
47.5183 | -57.4817 | 29.0642 | 26.0917 | 26.149 | 26.0216 | 25.9148 | 25.5731
48.5198 | -56.4802 | 29.0649 | 26.0928 | 26.152 | 26.0241 | 25.9086 | 25.5776
49.5112 | -55.4888 | 29.0603 | 26.0905 | 26.1515 | 26.0182 | 25.9138 | 25.5757
50.5126 | -54.4874 | 29.0581 | 26.0888 | 26.1529 | 26.0189 | 25.9078 | 25.5721
51.5141 | -53.4859 | 29.0655 | 26.0873 | 26.1495 | 26.0198 | 25.9201 | 25.5683
52.5155 | -52.4845 | 29.0593 | 26.0871 | 26.1534 | 26.0255 | 25.9201 | 25.5735
53.517 | -51.483 | 29.0646 | 26.0876 | 26.1512 | 26.0219 | 25.9149 | 25.5749
54.5184 | -50.4816 | 29.0675 | 26.081 | 26.1413 | 26.0087 | 25.9182 | 25.5728
55.5198 | -49.4802 | 29.0607 | 26.0859 | 26.1501 | 26.0158 | 25.9296 | 25.5723
56.5213 | -48.4787 | 29.0641 | 26.0871 | 26.1489 | 26.0144 | 25.9142 | 25.5683
57.5127 | -47.4873 | 29.065 | 26.087 | 26.1478 | 26.0145 | 25.9205 | 25.5682
58.5141 | -46.4859 | 29.0591 | 26.0807 | 26.1453 | 26.0182 | 25.9111 | 25.5673
59.5156 | -45.4844 | 29.0697 | 26.0861 | 26.1404 | 26.0181 | 25.913 | 25.565
60.517 | -44.483 | 29.0648 | 26.0869 | 26.142 | 26.016 | 25.9081 | 25.5671
61.5185 | -43.4815 | 29.0699 | 26.0859 | 26.1377 | 26.0212 | 25.9127 | 25.5619
62.5199 | -42.4801 | 29.0657 | 26.0822 | 26.1409 | 26.0156 | 25.9123 | 25.57
63.5213 | -41.4787 | 29.0579 | 26.084 | 26.1515 | 26.0214 | 25.9069 | 25.5659
64.5128 | -40.4872 | 29.0607 | 26.0861 | 26.1526 | 26.0158 | 25.9113 | 25.5612
65.5142 | -39.4858 | 29.0654 | 26.0777 | 26.1416 | 26.0189 | 25.8998 | 25.5676
66.5156 | -38.4844 | 29.0604 | 26.0813 | 26.1532 | 26.0133 | 25.9013 | 25.5649
67.5171 | -37.4829 | 29.066 | 26.0845 | 26.1387 | 26.0134 | 25.905 | 25.5579
68.5185 | -36.4815 | 29.0652 | 26.0755 | 26.1488 | 26.0096 | 25.896 | 25.5621
69.52 | -35.48 | 29.065 | 26.0822 | 26.1399 | 26.0146 | 25.9027 | 25.5591
70.5214 | -34.4786 | 29.0669 | 26.0801 | 26.1423 | 26.0119 | 25.9025 | 25.5561
71.5228 | -33.4772 | 29.0667 | 26.0774 | 26.1368 | 26.0112 | 25.8929 | 25.5586
72.5143 | -32.4857 | 29.064 | 26.0826 | 26.1451 | 26.0137 | 25.8984 | 25.5579
73.5157 | -31.4843 | 29.0661 | 26.0789 | 26.1423 | 26.005 | 25.9081 | 25.5598
74.5172 | -30.4828 | 29.0661 | 26.0732 | 26.1295 | 26.0047 | 25.9052 | 25.5562
75.5186 | -29.4814 | 29.0611 | 26.0805 | 26.1442 | 26.0028 | 25.901 | 25.5582
76.52 | -28.48 | 29.0644 | 26.0784 | 26.1411 | 26.0047 | 25.9069 | 25.5601
77.5215 | -27.4785 | 29.0626 | 26.0737 | 26.1402 | 26.0054 | 25.9057 | 25.5582
78.5129 | -26.4871 | 29.0669 | 26.0741 | 26.1225 | 26.0005 | 25.9112 | 25.5615
79.5143 | -25.4857 | 29.0635 | 26.0748 | 26.1489 | 26.0014 | 25.9111 | 25.5614
80.5158 | -24.4842 | 29.06 | 26.0739 | 26.1201 | 26.0056 | 25.904 | 25.5647
81.5172 | -23.4828 | 29.0581 | 26.0753 | 26.1439 | 26.0014 | 25.909 | 25.5586
82.5187 | -22.4813 | 29.0667 | 26.0725 | 26.1269 | 26.0035 | 25.9076 | 25.5607
83.5201 | -21.4799 | 29.071 | 26.0754 | 26.1326 | 25.9996 | 25.9032 | 25.5662
84.5115 | -20.4885 | 29.0621 | 26.0742 | 26.1426 | 25.997 | 25.9046 | 25.5658
85.513 | -19.487 | 29.056 | 26.0721 | 26.1435 | 26.001 | 25.9136 | 25.5601
86.5144 | -18.4856 | 29.0585 | 26.0769 | 26.1361 | 26.0021 | 25.9075 | 25.5586
87.5158 | -17.4842 | 29.0564 | 26.0703 | 26.1427 | 25.9985 | 25.9069 | 25.5669
88.5173 | -16.4827 | 29.0574 | 26.0822 | 26.14 | 26.0045 | 25.9133 | 25.5639
89.5187 | -15.4813 | 29.0528 | 26.0774 | 26.1241 | 25.9955 | 25.9125 | 25.5624
90.5202 | -14.4798 | 29.0585 | 26.0692 | 26.1378 | 25.9997 | 25.9161 | 25.5636
91.5116 | -13.4884 | 29.0552 | 26.0764 | 26.1389 | 25.9999 | 25.9175 | 25.5673
92.513 | -12.487 | 29.062 | 26.0711 | 26.1203 | 25.9993 | 25.9062 | 25.5586
93.5145 | -11.4855 | 29.0665 | 26.0744 | 26.1265 | 26.0031 | 25.9072 | 25.5624
94.5159 | -10.4841 | 29.0614 | 26.0719 | 26.1295 | 26.0004 | 25.9118 | 25.5595
95.5173 | -9.4827 | 29.0561 | 26.0682 | 26.1284 | 25.9998 | 25.9095 | 25.5634
96.5188 | -8.4812 | 29.0575 | 26.0689 | 26.1264 | 26.0063 | 25.9141 | 25.559
97.5202 | -7.4798 | 29.0572 | 26.0752 | 26.1337 | 25.9954 | 25.9113 | 25.5635
98.5217 | -6.4783 | 29.0539 | 26.0772 | 26.1411 | 26.0038 | 25.9041 | 25.5636
99.5131 | -5.4869 | 29.0606 | 26.0728 | 26.1367 | 26.0078 | 25.9058 | 25.554
100.5145 | -4.4855 | 29.0528 | 26.0669 | 26.1346 | 26.0006 | 25.9051 | 25.5587
101.516 | -3.484 | 29.0598 | 26.0638 | 26.1258 | 25.9991 | 25.8977 | 25.5688
102.5174 | -2.4826 | 29.0577 | 26.0685 | 26.1289 | 26 | 25.9041 | 25.5691
103.5189 | -1.4811 | 29.1137 | 26.0739 | 26.1293 | 25.9964 | 25.9038 | 25.5605
104.5103 | -0.4897 | 29.5339 | 26.0783 | 26.1354 | 26.0018 | 25.8939 | 25.5612
105.5117 | 0.5117 | 30.5101 | 26.0708 | 26.1299 | 26.0009 | 25.9 | 25.5647
106.5132 | 1.5132 | 32.0886 | 26.0731 | 26.1285 | 26.0046 | 25.8957 | 25.5601
107.5146 | 2.5146 | 34.1743 | 26.0747 | 26.1338 | 25.9986 | 25.8885 | 25.5584
108.516 | 3.516 | 36.7021 | 26.074 | 26.1212 | 26.0029 | 25.8973 | 25.5621
109.5175 | 4.5175 | 39.6063 | 26.0858 | 26.1346 | 26.0124 | 25.9044 | 25.5748
110.5189 | 5.5189 | 42.8518 | 26.0934 | 26.1398 | 26.0291 | 25.907 | 25.5687
111.5204 | 6.5204 | 46.3835 | 26.0971 | 26.1381 | 26.043 | 25.9161 | 25.5835
112.5118 | 7.5118 | 50.1393 | 26.1037 | 26.1428 | 26.0626 | 25.9237 | 25.5941
113.5132 | 8.5132 | 54.1101 | 26.1195 | 26.165 | 26.0999 | 25.9521 | 25.6014
114.5147 | 9.5147 | 58.2386 | 26.1392 | 26.1866 | 26.1387 | 25.9665 | 25.6265
115.5161 | 10.5161 | 62.5437 | 26.1574 | 26.2124 | 26.1756 | 25.9831 | 25.6434
116.5175 | 11.5175 | 67.0208 | 26.1814 | 26.2352 | 26.2381 | 26.0329 | 25.6728
117.519 | 12.519 | 71.6664 | 26.2159 | 26.2794 | 26.2981 | 26.051 | 25.6984
118.5204 | 13.5204 | 76.4275 | 26.2597 | 26.3208 | 26.376 | 26.0877 | 25.7426
119.5219 | 14.5219 | 81.315 | 26.3019 | 26.3686 | 26.4567 | 26.1361 | 25.7813
120.5133 | 15.5133 | 86.3087 | 26.3512 | 26.4277 | 26.5573 | 26.1991 | 25.825
121.5147 | 16.5147 | 91.3925 | 26.4097 | 26.5006 | 26.6693 | 26.2604 | 25.8833
122.5162 | 17.5162 | 96.5202 | 26.478 | 26.5739 | 26.7841 | 26.3335 | 25.9455
123.5176 | 18.5176 | 101.7125 | 26.5412 | 26.6607 | 26.9214 | 26.4012 | 26.0094
124.519 | 19.519 | 107.0433 | 26.6253 | 26.7561 | 27.0694 | 26.494 | 26.0775
125.5205 | 20.5205 | 112.4229 | 26.7188 | 26.8692 | 27.2407 | 26.6078 | 26.1664
126.5119 | 21.5119 | 117.9031 | 26.823 | 26.9953 | 27.413 | 26.7158 | 26.2508
127.5134 | 22.5134 | 123.4273 | 26.9238 | 27.1273 | 27.6123 | 26.8414 | 26.3559
128.5148 | 23.5148 | 128.9569 | 27.0453 | 27.2761 | 27.8205 | 26.9671 | 26.4593
129.5162 | 24.5162 | 134.5399 | 27.1734 | 27.425 | 28.0447 | 27.1071 | 26.5776
130.5177 | 25.5177 | 140.1185 | 27.3119 | 27.6006 | 28.2929 | 27.2538 | 26.6993
131.5191 | 26.5191 | 145.7082 | 27.4575 | 27.7918 | 28.5578 | 27.4293 | 26.8289
132.5105 | 27.5105 | 151.4063 | 27.6194 | 27.9948 | 28.8503 | 27.6082 | 26.9753
133.512 | 28.512 | 157.007 | 27.7912 | 28.2165 | 29.1498 | 27.8064 | 27.1206
134.5134 | 29.5134 | 162.5668 | 27.9718 | 28.4432 | 29.4754 | 28.0165 | 27.2702
135.5149 | 30.5149 | 168.2102 | 28.1612 | 28.7021 | 29.82 | 28.24 | 27.4352
136.5163 | 31.5163 | 173.7781 | 28.3701 | 28.9625 | 30.1905 | 28.4798 | 27.62
137.5177 | 32.5177 | 179.3302 | 28.588 | 29.2583 | 30.5769 | 28.7441 | 27.8066
138.5192 | 33.5192 | 184.8443 | 28.8397 | 29.5715 | 30.9879 | 29.0102 | 27.9906
139.5206 | 34.5206 | 190.343 | 29.0841 | 29.8901 | 31.4142 | 29.3073 | 28.2069
140.512 | 35.512 | 195.925 | 29.3421 | 30.2317 | 31.8682 | 29.6029 | 28.4303
141.5135 | 36.5135 | 201.5356 | 29.6192 | 30.5978 | 32.3335 | 29.9129 | 28.6592
142.5149 | 37.5149 | 207.0074 | 29.9073 | 30.9665 | 32.8165 | 30.2489 | 28.9001
143.5164 | 38.5164 | 212.495 | 30.227 | 31.3694 | 33.3336 | 30.5805 | 29.1653
144.5178 | 39.5178 | 218.0085 | 30.5369 | 31.7946 | 33.867 | 30.9523 | 29.4391
145.5192 | 40.5192 | 223.5362 | 30.8851 | 32.2212 | 34.4206 | 31.3173 | 29.7174
146.5107 | 41.5107 | 228.9351 | 31.2422 | 32.679 | 34.9919 | 31.7167 | 30.0186
147.5121 | 42.5121 | 234.4031 | 31.6109 | 33.1489 | 35.5862 | 32.132 | 30.3232
148.5136 | 43.5136 | 239.9142 | 32.0019 | 33.6446 | 36.1964 | 32.558 | 30.6407
149.515 | 44.515 | 245.3325 | 32.4123 | 34.1766 | 36.8376 | 32.9968 | 30.9727
150.5164 | 45.5164 | 250.6578 | 32.8364 | 34.7099 | 37.503 | 33.4614 | 31.3222
151.5179 | 46.5179 | 256.038 | 33.2813 | 35.2717 | 38.1882 | 33.9302 | 31.6824
152.5193 | 47.5193 | 261.4375 | 33.7422 | 35.8608 | 38.9003 | 34.4286 | 32.0533
153.5107 | 48.5107 | 266.9061 | 34.2274 | 36.467 | 39.6403 | 34.9511 | 32.4555
154.5122 | 49.5122 | 272.3618 | 34.7265 | 37.0976 | 40.4091 | 35.4698 | 32.8588
155.5136 | 50.5136 | 277.6954 | 35.245 | 37.7522 | 41.1936 | 36.0241 | 33.2789
156.5151 | 51.5151 | 282.5395 | 35.7826 | 38.4316 | 42.0173 | 36.5979 | 33.7159
157.5165 | 52.5165 | 286.9694 | 36.3236 | 39.1416 | 42.864 | 37.1803 | 34.173
158.5179 | 53.5179 | 291.1356 | 36.9056 | 39.873 | 43.7354 | 37.7969 | 34.6357
159.5194 | 54.5194 | 295.0171 | 37.4991 | 40.6088 | 44.6436 | 38.4284 | 35.1052
160.5108 | 55.5108 | 298.7643 | 38.1044 | 41.3819 | 45.5623 | 39.0735 | 35.586
161.5223 | 56.5223 | 302.5865 | 38.7386 | 42.1836 | 46.5029 | 39.7175 | 36.0792
162.5137 | 57.5137 | 306.1747 | 39.374 | 42.9982 | 47.4651 | 40.3936 | 36.5767
163.5151 | 58.5151 | 309.4691 | 40.0272 | 43.8447 | 48.449 | 41.0716 | 37.0821
164.5166 | 59.5166 | 312.578 | 40.6976 | 44.6914 | 49.4484 | 41.7756 | 37.6247
165.518 | 60.518 | 315.2779 | 41.3827 | 45.5753 | 50.4553 | 42.4675 | 38.1771
166.5194 | 61.5194 | 317.6952 | 42.0808 | 46.4547 | 51.4951 | 43.198 | 38.7499
167.5209 | 62.5209 | 319.8024 | 42.7953 | 47.3666 | 52.5537 | 43.9135 | 39.3278
168.5123 | 63.5123 | 321.5792 | 43.5083 | 48.2773 | 53.6331 | 44.6572 | 39.9109
169.5137 | 64.5137 | 323.0327 | 44.2386 | 49.2121 | 54.7207 | 45.4017 | 40.5277
170.5152 | 65.5152 | 324.2922 | 44.9827 | 50.1587 | 55.8121 | 46.1394 | 41.1881
171.5166 | 66.5166 | 325.3461 | 45.7218 | 51.0977 | 56.8962 | 46.8848 | 41.7921
172.5181 | 67.5181 | 326.2213 | 46.4732 | 52.0451 | 58.0095 | 47.6379 | 42.4157
173.5195 | 68.5195 | 327.0727 | 47.2208 | 53.007 | 59.096 | 48.3828 | 43.12
174.5109 | 69.5109 | 327.8038 | 47.9862 | 53.9607 | 60.1773 | 49.1328 | 43.7565
175.5124 | 70.5124 | 328.2822 | 48.7361 | 54.9117 | 61.2654 | 49.8617 | 44.3814
176.5138 | 71.5138 | 328.7317 | 49.4871 | 55.8665 | 62.3574 | 50.6094 | 45.0044
177.5153 | 72.5153 | 329.0627 | 50.2373 | 56.8075 | 63.4255 | 51.3396 | 45.6024
178.5167 | 73.5167 | 329.1808 | 50.9755 | 57.7551 | 64.4799 | 52.0609 | 46.2131
179.5181 | 74.5181 | 329.2943 | 51.7296 | 58.6937 | 65.5295 | 52.7809 | 46.8298
180.5196 | 75.5196 | 329.3546 | 52.4807 | 59.612 | 66.5702 | 53.4985 | 47.3288
181.511 | 76.511 | 329.4439 | 53.2242 | 60.5447 | 67.5968 | 54.2056 | 47.8796
182.5124 | 77.5124 | 329.4972 | 53.9701 | 61.4548 | 68.6146 | 54.9096 | 48.5513
183.5139 | 78.5139 | 329.442 | 54.7194 | 62.3593 | 69.6154 | 55.598 | 49.2224
184.5153 | 79.5153 | 329.2443 | 55.4535 | 63.2595 | 70.6066 | 56.2682 | 50.0288
185.5168 | 80.5168 | 329.1306 | 56.1874 | 64.1445 | 71.5891 | 56.959 | 50.7504
186.5182 | 81.5182 | 328.9447 | 56.9163 | 65.0274 | 72.5533 | 57.6191 | 51.4357
187.5196 | 82.5196 | 328.7081 | 57.6571 | 65.8879 | 73.4989 | 58.2937 | 51.9956
188.5211 | 83.5211 | 328.4876 | 58.3743 | 66.7505 | 74.4357 | 58.9352 | 52.5547
189.5125 | 84.5125 | 328.2571 | 59.1021 | 67.6022 | 75.3461 | 59.6017 | 53.1201
190.5139 | 85.5139 | 327.8917 | 59.8028 | 68.4411 | 76.2369 | 60.2259 | 53.7022
191.5154 | 86.5154 | 327.6118 | 60.4994 | 69.2573 | 77.1208 | 60.8591 | 54.439
192.5168 | 87.5168 | 327.2211 | 61.2049 | 70.0649 | 77.991 | 61.4698 | 55.1897
193.5183 | 88.5183 | 326.8886 | 61.907 | 70.8726 | 78.8519 | 62.0846 | 56.0115
194.5197 | 89.5197 | 326.6269 | 62.6046 | 71.6543 | 79.692 | 62.7055 | 56.8627
195.5111 | 90.5111 | 326.3783 | 63.3035 | 72.4529 | 80.521 | 63.3141 | 57.5929
196.5126 | 91.5126 | 326.1052 | 64.0023 | 73.203 | 81.3351 | 63.9184 | 58.215
197.514 | 92.514 | 325.7031 | 64.6972 | 73.9816 | 82.1375 | 64.5179 | 58.747
198.5155 | 93.5155 | 325.3438 | 65.3841 | 74.7179 | 82.9298 | 65.1087 | 59.4087
199.5169 | 94.5169 | 324.9142 | 66.0676 | 75.4694 | 83.7087 | 65.678 | 60.1613
200.5183 | 95.5183 | 324.4899 | 66.7615 | 76.1901 | 84.4644 | 66.263 | 60.8015
201.5198 | 96.5198 | 324.0561 | 67.4405 | 76.9159 | 85.2087 | 66.8208 | 61.4429
202.5112 | 97.5112 | 323.6408 | 68.1149 | 77.6248 | 85.9515 | 67.3932 | 62.1485
203.5126 | 98.5126 | 323.2663 | 68.7822 | 78.3225 | 86.6649 | 67.9354 | 62.8588
204.5141 | 99.5141 | 322.8531 | 69.4527 | 79.007 | 87.3728 | 68.4802 | 63.4865
205.5155 | 100.5155 | 322.4005 | 70.1201 | 79.6887 | 88.0609 | 69.0225 | 64.083
206.517 | 101.517 | 321.9827 | 70.7828 | 80.3564 | 88.7488 | 69.5551 | 64.7576
207.5184 | 102.5184 | 321.5142 | 71.4419 | 81.0118 | 89.4282 | 70.077 | 65.404
208.5198 | 103.5198 | 321.0991 | 72.1066 | 81.6655 | 90.0993 | 70.5926 | 66.0137
209.5213 | 104.5213 | 320.6619 | 72.7632 | 82.312 | 90.7645 | 71.1098 | 66.6017
210.5127 | 105.5127 | 320.24 | 73.4003 | 82.9374 | 91.4107 | 71.6198 | 67.1397
211.5141 | 106.5141 | 319.7112 | 74.0376 | 83.5672 | 92.0535 | 72.1304 | 67.5887
212.5156 | 107.5156 | 319.2615 | 74.6603 | 84.1824 | 92.6716 | 72.6283 | 68.0422
213.517 | 108.517 | 318.8818 | 75.2728 | 84.7827 | 93.2847 | 73.1182 | 68.5183
214.5185 | 109.5185 | 318.4387 | 75.8712 | 85.3675 | 93.8901 | 73.5989 | 69.0133
215.5199 | 110.5199 | 317.9773 | 76.4689 | 85.9492 | 94.4877 | 74.0814 | 69.5019
216.5213 | 111.5213 | 317.4797 | 77.0504 | 86.5252 | 95.0814 | 74.5464 | 70.0298
217.5128 | 112.5128 | 317.0344 | 77.6224 | 87.0783 | 95.6583 | 75.0094 | 70.5537
218.5342 | 113.5342 | 316.6129 | 78.1932 | 87.6327 | 96.241 | 75.4703 | 71.0173
219.5156 | 114.5156 | 316.096 | 78.7365 | 88.1703 | 96.7975 | 75.9029 | 71.5304
220.5571 | 115.5571 | 315.5654 | 79.3136 | 88.719 | 97.381 | 76.3613 | 72.0464
221.5185 | 116.5185 | 315.0269 | 79.8364 | 89.2138 | 97.9099 | 76.7783 | 72.5516
222.52 | 117.52 | 314.4917 | 80.3919 | 89.7311 | 98.4631 | 77.2019 | 73.0586
223.5114 | 118.5114 | 313.9874 | 80.9328 | 90.2407 | 99.0134 | 77.6228 | 73.5183
224.5128 | 119.5128 | 313.468 | 81.4804 | 90.7431 | 99.5533 | 78.0217 | 73.9018
225.5143 | 120.5143 | 312.9343 | 82.0217 | 91.2521 | 100.101 | 78.4284 | 74.4102
226.5157 | 121.5157 | 312.3609 | 82.5587 | 91.7266 | 100.6242 | 78.8343 | 74.9946
227.5172 | 122.5172 | 311.7995 | 83.0917 | 92.219 | 101.1387 | 79.2308 | 75.5944
228.5186 | 123.5186 | 311.2003 | 83.6114 | 92.6834 | 101.6511 | 79.6253 | 76.1474
229.52 | 124.52 | 310.7036 | 84.126 | 93.1613 | 102.1579 | 80.0078 | 76.6846
230.5215 | 125.5215 | 310.178 | 84.6441 | 93.6129 | 102.655 | 80.3963 | 77.1945
231.5129 | 126.5129 | 309.6856 | 85.1514 | 94.0615 | 103.1465 | 80.7877 | 77.7851
232.5143 | 127.5143 | 309.1374 | 85.6674 | 94.5315 | 103.6325 | 81.1713 | 78.3371
233.5158 | 128.5158 | 308.6182 | 86.1715 | 94.9787 | 104.0966 | 81.535 | 78.8465
234.5172 | 129.5172 | 308.2332 | 86.6753 | 95.4114 | 104.5758 | 81.9283 | 79.3348
235.5187 | 130.5187 | 307.8244 | 87.163 | 95.8569 | 105.0397 | 82.2947 | 79.8244
236.5201 | 131.5201 | 307.3435 | 87.6625 | 96.2875 | 105.5006 | 82.6405 | 80.2701
237.5115 | 132.5115 | 306.7094 | 88.1469 | 96.7159 | 105.9643 | 83.0255 | 80.6948
238.513 | 133.513 | 306.1647 | 88.6324 | 97.1266 | 106.4117 | 83.3829 | 81.1172
239.5144 | 134.5144 | 305.6444 | 89.1123 | 97.5388 | 106.8638 | 83.7294 | 81.5101
240.5158 | 135.5158 | 305.2452 | 89.5955 | 97.9439 | 107.3039 | 84.078 | 81.8939
241.5173 | 136.5173 | 304.7489 | 90.0727 | 98.3516 | 107.7462 | 84.4219 | 82.2481
242.5187 | 137.5187 | 304.2436 | 90.545 | 98.7562 | 108.1883 | 84.7538 | 82.5757
243.5202 | 138.5202 | 303.7443 | 91.0087 | 99.1466 | 108.6124 | 85.1027 | 82.916
244.5116 | 139.5116 | 303.3402 | 91.4694 | 99.543 | 109.0335 | 85.4282 | 83.3061
245.513 | 140.513 | 302.9534 | 91.9234 | 99.9339 | 109.4508 | 85.7493 | 83.6939
246.5145 | 141.5145 | 302.5185 | 92.3744 | 100.306 | 109.8586 | 86.0895 | 84.0664
247.5159 | 142.5159 | 301.9815 | 92.8137 | 100.6899 | 110.2405 | 86.4201 | 84.4237
248.5174 | 143.5174 | 301.5391 | 93.2505 | 101.0458 | 110.6087 | 86.7242 | 84.7862
249.5188 | 144.5188 | 301.0474 | 93.6808 | 101.4136 | 110.9748 | 87.0336 | 85.1443
250.5202 | 145.5202 | 300.5405 | 94.0993 | 101.7607 | 111.3286 | 87.3378 | 85.5358
251.5217 | 146.5217 | 299.9704 | 94.5134 | 102.1054 | 111.6774 | 87.6382 | 85.9472
252.5131 | 147.5131 | 299.4244 | 94.9272 | 102.4384 | 112.0264 | 87.934 | 86.3544
253.5145 | 148.5145 | 298.8731 | 95.3501 | 102.7808 | 112.3834 | 88.2351 | 86.785
254.516 | 149.516 | 298.2862 | 95.7652 | 103.108 | 112.7299 | 88.5177 | 87.2099
255.5174 | 150.5174 | 297.7834 | 96.1744 | 103.4418 | 113.0671 | 88.7966 | 87.6152
256.5189 | 151.5189 | 297.2745 | 96.5811 | 103.7619 | 113.3866 | 89.0842 | 87.977
257.5103 | 152.5103 | 296.7939 | 96.9757 | 104.0766 | 113.7176 | 89.3569 | 88.311
258.5117 | 153.5117 | 296.4026 | 97.374 | 104.393 | 114.0561 | 89.6294 | 88.6436
259.5132 | 154.5132 | 296.0267 | 97.7742 | 104.7115 | 114.3738 | 89.9017 | 88.9556
260.5146 | 155.5146 | 295.7633 | 98.1554 | 105.0188 | 114.6948 | 90.1713 | 89.3147
261.516 | 156.516 | 295.6602 | 98.5441 | 105.3323 | 115.0081 | 90.4303 | 89.6325
262.5175 | 157.5175 | 295.587 | 98.9173 | 105.6271 | 115.3206 | 90.7029 | 89.9252
263.5189 | 158.5189 | 295.5445 | 99.2904 | 105.9254 | 115.624 | 90.9576 | 90.2465
264.5204 | 159.5204 | 295.3851 | 99.6625 | 106.2334 | 115.9062 | 91.2225 | 90.6315
265.5118 | 160.5118 | 295.3152 | 100.0275 | 106.5247 | 116.1865 | 91.508 | 90.9896
266.5132 | 161.5132 | 295.3305 | 100.3836 | 106.8172 | 116.4643 | 91.7719 | 91.2709
267.5147 | 162.5147 | 295.3684 | 100.7318 | 107.0965 | 116.7426 | 92.03 | 91.5295
268.5161 | 163.5161 | 295.4958 | 101.0801 | 107.3868 | 117.0193 | 92.2672 | 91.8372
269.5175 | 164.5175 | 295.7118 | 101.4328 | 107.6687 | 117.3027 | 92.5107 | 92.0865
270.519 | 165.519 | 295.8828 | 101.7858 | 107.9572 | 117.5931 | 92.7633 | 92.2659
271.5204 | 166.5204 | 296.0814 | 102.1589 | 108.2368 | 117.8777 | 93.0019 | 92.485
272.5219 | 167.5219 | 296.4098 | 102.509 | 108.5052 | 118.1639 | 93.2608 | 92.7833
273.5133 | 168.5133 | 296.8046 | 102.8687 | 108.794 | 118.4552 | 93.5106 | 93.1044
274.5147 | 169.5147 | 297.1809 | 103.2206 | 109.0744 | 118.7567 | 93.7523 | 93.4266
275.5162 | 170.5162 | 297.5718 | 103.5879 | 109.3544 | 119.0546 | 94.0205 | 93.7737
276.5176 | 171.5176 | 297.995 | 103.9526 | 109.6352 | 119.3501 | 94.2863 | 94.143
277.5191 | 172.5191 | 298.3936 | 104.3166 | 109.9165 | 119.6534 | 94.549 | 94.4971
278.5105 | 173.5105 | 298.8266 | 104.6881 | 110.1997 | 119.9496 | 94.8104 | 94.8934
279.5119 | 174.5119 | 299.3326 | 105.0534 | 110.4866 | 120.2566 | 95.068 | 95.284
280.5134 | 175.5134 | 299.8153 | 105.4143 | 110.7578 | 120.5517 | 95.3291 | 95.6051
281.5148 | 176.5148 | 300.2959 | 105.7816 | 111.0445 | 120.8606 | 95.5913 | 95.842
282.5162 | 177.5162 | 300.825 | 106.141 | 111.3309 | 121.181 | 95.8615 | 96.0521
283.5177 | 178.5177 | 301.477 | 106.5112 | 111.6232 | 121.4991 | 96.1366 | 96.3088
284.5191 | 179.5191 | 301.9122 | 106.882 | 111.9156 | 121.8354 | 96.3883 | 96.6071
285.5206 | 180.5206 | 302.3706 | 107.2474 | 112.212 | 122.1648 | 96.6556 | 96.9263
286.522 | 181.522 | 302.8567 | 107.6206 | 112.493 | 122.5094 | 96.9191 | 97.2557
287.5134 | 182.5134 | 303.3951 | 107.9948 | 112.8061 | 122.8446 | 97.1992 | 97.6158
288.5149 | 183.5149 | 303.938 | 108.3616 | 113.1022 | 123.1852 | 97.4691 | 97.9275
289.5163 | 184.5163 | 304.442 | 108.7414 | 113.4118 | 123.5425 | 97.7462 | 98.1657
290.5177 | 185.5177 | 304.8121 | 109.1243 | 113.721 | 123.8925 | 98.0304 | 98.3253
291.5192 | 186.5192 | 305.11 | 109.5089 | 114.0291 | 124.2298 | 98.3115 | 98.3818
292.5206 | 187.5206 | 305.3737 | 109.8866 | 114.3451 | 124.5734 | 98.5913 | 98.5622
293.512 | 188.512 | 305.6482 | 110.2698 | 114.662 | 124.9314 | 98.8783 | 98.9409
294.5135 | 189.5135 | 305.8595 | 110.6492 | 114.988 | 125.2835 | 99.1644 | 99.5173
295.5149 | 190.5149 | 305.8612 | 111.0318 | 115.2965 | 125.6339 | 99.4469 | 100.0486
296.5164 | 191.5164 | 305.8269 | 111.4111 | 115.6222 | 125.9944 | 99.7537 | 100.4927
297.5178 | 192.5178 | 305.9204 | 111.7869 | 115.9429 | 126.361 | 100.0282 | 100.8299
298.5192 | 193.5192 | 306.1809 | 112.1646 | 116.2578 | 126.7205 | 100.3429 | 101.1604
299.5207 | 194.5207 | 306.3206 | 112.55 | 116.5881 | 127.0781 | 100.6172 | 101.4889
300.5121 | 195.5121 | 306.4845 | 112.9272 | 116.8961 | 127.4378 | 100.9076 | 101.8614
301.5136 | 196.5136 | 306.5858 | 113.3048 | 117.2269 | 127.792 | 101.2031 | 102.3129
302.515 | 197.515 | 306.6536 | 113.6865 | 117.5421 | 128.1525 | 101.4908 | 102.7978
303.5164 | 198.5164 | 306.7462 | 114.0688 | 117.8587 | 128.5245 | 101.7738 | 103.2349
304.5179 | 199.5179 | 306.8479 | 114.4448 | 118.1746 | 128.8747 | 102.0723 | 103.6344
305.5193 | 200.5193 | 306.9399 | 114.8237 | 118.4948 | 129.2276 | 102.3603 | 104.04
306.5107 | 201.5107 | 307.0204 | 115.2029 | 118.8099 | 129.5822 | 102.6274 | 104.4667
307.5122 | 202.5122 | 307.1542 | 115.5721 | 119.1214 | 129.937 | 102.9183 | 104.9646
308.5136 | 203.5136 | 307.1862 | 115.9471 | 119.4329 | 130.2983 | 103.1867 | 105.4183
309.5151 | 204.5151 | 307.1248 | 116.3167 | 119.7433 | 130.6517 | 103.4607 | 105.8638
310.5165 | 205.5165 | 307.1176 | 116.6702 | 120.0714 | 131.0079 | 103.7405 | 106.2552
311.5179 | 206.5179 | 307.0772 | 117.0288 | 120.3784 | 131.3586 | 104.0101 | 106.6322
312.5194 | 207.5194 | 307.1982 | 117.3796 | 120.6948 | 131.7099 | 104.2683 | 106.947
313.5108 | 208.5108 | 307.2616 | 117.7391 | 121.0149 | 132.0628 | 104.526 | 107.1581
314.5122 | 209.5122 | 307.3133 | 118.0864 | 121.3286 | 132.425 | 104.7981 | 107.4896
315.5137 | 210.5137 | 307.2581 | 118.4414 | 121.6482 | 132.7925 | 105.0605 | 107.8161
316.5151 | 211.5151 | 307.1644 | 118.7823 | 121.9677 | 133.1603 | 105.3327 | 108.0734
317.5166 | 212.5166 | 307.1012 | 119.1209 | 122.2935 | 133.5142 | 105.6012 | 108.5233
318.518 | 213.518 | 307.0135 | 119.4647 | 122.6121 | 133.8603 | 105.8533 | 108.9473
319.5194 | 214.5194 | 306.9172 | 119.806 | 122.9313 | 134.1895 | 106.1074 | 109.3319
320.5209 | 215.5209 | 306.8571 | 120.1513 | 123.2422 | 134.5285 | 106.3598 | 109.7265
321.5123 | 216.5123 | 306.7652 | 120.4867 | 123.5587 | 134.8576 | 106.6241 | 110.2031
322.5138 | 217.5138 | 306.6954 | 120.829 | 123.8706 | 135.1835 | 106.8641 | 110.5932
323.5352 | 218.5352 | 306.621 | 121.183 | 124.2029 | 135.526 | 107.1265 | 110.9127
324.5166 | 219.5166 | 306.525 | 121.5248 | 124.5064 | 135.8493 | 107.3744 | 111.3674
325.5181 | 220.5181 | 306.4914 | 121.8752 | 124.8205 | 136.1758 | 107.6224 | 111.907
326.5195 | 221.5195 | 306.4265 | 122.2245 | 125.1321 | 136.5122 | 107.8655 | 112.5684
327.521 | 222.521 | 306.4693 | 122.5794 | 125.4335 | 136.8531 | 108.133 | 113.1579
328.5124 | 223.5124 | 306.5377 | 122.9151 | 125.742 | 137.1788 | 108.3647 | 113.7025
329.5138 | 224.5138 | 306.5455 | 123.2611 | 126.0496 | 137.5064 | 108.6289 | 114.2243
330.5153 | 225.5153 | 306.5795 | 123.6082 | 126.3637 | 137.8247 | 108.8706 | 114.7182
331.5167 | 226.5167 | 306.5408 | 123.9547 | 126.6618 | 138.1342 | 109.1298 | 115.1831
332.5181 | 227.5181 | 306.4428 | 124.2967 | 126.9755 | 138.4418 | 109.3727 | 115.6346
333.5196 | 228.5196 | 306.3038 | 124.6366 | 127.2667 | 138.7481 | 109.6388 | 116.0786
334.521 | 229.521 | 306.2212 | 124.9784 | 127.5685 | 139.0661 | 109.8803 | 116.5091
335.5124 | 230.5124 | 306.2197 | 125.3116 | 127.8687 | 139.377 | 110.1257 | 116.9282
336.5139 | 231.5139 | 306.1933 | 125.6559 | 128.1593 | 139.6913 | 110.3768 | 117.3337
337.5153 | 232.5153 | 306.1886 | 125.9907 | 128.4735 | 140.0096 | 110.6129 | 117.7265
338.5668 | 233.5668 | 306.2636 | 126.3487 | 128.7736 | 140.3276 | 110.8775 | 118.1351
339.5182 | 234.5182 | 306.3513 | 126.6674 | 129.0539 | 140.6049 | 111.1073 | 118.5019
340.5196 | 235.5196 | 306.3696 | 127.0003 | 129.3567 | 140.8935 | 111.3335 | 118.8841
341.5211 | 236.5211 | 306.345 | 127.3432 | 129.6297 | 141.1725 | 111.5661 | 119.2617
342.5125 | 237.5125 | 306.3383 | 127.6769 | 129.9187 | 141.4463 | 111.8014 | 119.6357
343.5139 | 238.5139 | 306.3451 | 128.0096 | 130.2047 | 141.7329 | 112.0345 | 120.0074
344.5154 | 239.5154 | 306.2467 | 128.3513 | 130.4794 | 142.0059 | 112.2772 | 120.3744
345.5168 | 240.5168 | 306.1514 | 128.6957 | 130.7436 | 142.2769 | 112.5133 | 120.7308
346.5183 | 241.5183 | 306.0578 | 129.0276 | 131.0309 | 142.5617 | 112.738 | 121.0878
347.5197 | 242.5197 | 306.15 | 129.3725 | 131.3031 | 142.8494 | 112.9924 | 121.4503
348.5111 | 243.5111 | 306.2625 | 129.7148 | 131.5677 | 143.1312 | 113.2246 | 121.7944
349.5126 | 244.5126 | 306.3901 | 130.0605 | 131.842 | 143.4169 | 113.4799 | 122.1423
350.514 | 245.514 | 306.4757 | 130.4097 | 132.1195 | 143.6998 | 113.7173 | 122.4957
351.5155 | 246.5155 | 306.4162 | 130.7423 | 132.3909 | 143.9857 | 113.9337 | 122.8406
352.5169 | 247.5169 | 306.4036 | 131.0808 | 132.657 | 144.2772 | 114.1734 | 123.183
353.5183 | 248.5183 | 306.3508 | 131.4091 | 132.9335 | 144.579 | 114.4044 | 123.5229
354.5198 | 249.5198 | 306.4041 | 131.7236 | 133.1981 | 144.8553 | 114.6343 | 123.8681
355.5112 | 250.5112 | 306.5101 | 132.0331 | 133.4832 | 145.1312 | 114.857 | 124.1998
356.5126 | 251.5126 | 306.6435 | 132.3295 | 133.7579 | 145.398 | 115.0773 | 124.5325
357.5141 | 252.5141 | 306.651 | 132.6203 | 134.0255 | 145.6726 | 115.2901 | 124.8658
358.5155 | 253.5155 | 306.6374 | 132.9057 | 134.2976 | 145.9461 | 115.5106 | 125.192
359.517 | 254.517 | 306.5556 | 133.2066 | 134.5696 | 146.2199 | 115.7305 | 125.5228
360.5184 | 255.5184 | 306.5269 | 133.4946 | 134.8462 | 146.4894 | 115.9508 | 125.8539
361.5198 | 256.5198 | 306.5261 | 133.783 | 135.1142 | 146.7708 | 116.1707 | 126.1795
362.5213 | 257.5213 | 306.4374 | 134.0676 | 135.3854 | 147.0506 | 116.3908 | 126.5071
363.5127 | 258.5127 | 306.5119 | 134.3555 | 135.6545 | 147.3194 | 116.6095 | 126.828
364.5141 | 259.5141 | 306.4757 | 134.6354 | 135.926 | 147.6076 | 116.8226 | 127.1421
365.5156 | 260.5156 | 306.3592 | 134.9198 | 136.1992 | 147.9043 | 117.0443 | 127.4706
366.517 | 261.517 | 306.2737 | 135.209 | 136.4667 | 148.1968 | 117.2702 | 127.7846
367.5185 | 262.5185 | 306.3075 | 135.4912 | 136.7372 | 148.489 | 117.4921 | 128.1055
368.5199 | 263.5199 | 306.3559 | 135.7763 | 136.991 | 148.78 | 117.7044 | 128.4199
369.5113 | 264.5113 | 306.3791 | 136.0737 | 137.2461 | 149.0613 | 117.927 | 128.7349
370.5128 | 265.5128 | 306.3995 | 136.3693 | 137.5328 | 149.3413 | 118.1467 | 129.05
371.5142 | 266.5142 | 306.4086 | 136.667 | 137.7926 | 149.6159 | 118.3647 | 129.359
372.5157 | 267.5157 | 306.3464 | 136.9657 | 138.06 | 149.8831 | 118.5897 | 129.6713
373.5171 | 268.5171 | 306.1686 | 137.2586 | 138.335 | 150.1589 | 118.8188 | 129.9811
374.5185 | 269.5185 | 306.074 | 137.5546 | 138.6006 | 150.4267 | 119.0465 | 130.284
375.52 | 270.52 | 305.9583 | 137.8631 | 138.8676 | 150.6954 | 119.2657 | 130.5926
376.5214 | 271.5214 | 305.8412 | 138.1523 | 139.1345 | 150.9699 | 119.4842 | 130.8883
377.5128 | 272.5128 | 305.8157 | 138.4513 | 139.382 | 151.2398 | 119.7175 | 131.1802
378.5143 | 273.5143 | 305.781 | 138.7531 | 139.6557 | 151.507 | 119.9334 | 131.4743
379.5157 | 274.5157 | 305.7583 | 139.0573 | 139.923 | 151.7771 | 120.1519 | 131.7692
380.5172 | 275.5172 | 305.7172 | 139.3605 | 140.1853 | 152.02 | 120.3614 | 132.0628
381.5186 | 276.5186 | 305.7711 | 139.6626 | 140.4508 | 152.28 | 120.5822 | 132.3574
382.52 | 277.52 | 305.7355 | 139.9678 | 140.7156 | 152.5327 | 120.8053 | 132.6513
383.5215 | 278.5215 | 305.678 | 140.2657 | 140.9788 | 152.7908 | 121.0247 | 132.9436
384.5129 | 279.5129 | 305.7317 | 140.5659 | 141.2419 | 153.0364 | 121.245 | 133.2444
385.5143 | 280.5143 | 305.6909 | 140.8597 | 141.5015 | 153.2793 | 121.4641 | 133.5402
386.5158 | 281.5158 | 305.6373 | 141.156 | 141.908 | 153.5123 | 121.6634 | 133.8333
387.5172 | 282.5172 | 305.6612 | 141.4442 | 142.2446 | 153.757 | 121.8885 | 134.1183
388.5187 | 283.5187 | 305.6287 | 141.7369 | 142.5679 | 153.9955 | 122.1003 | 134.4129
389.5201 | 284.5201 | 305.6345 | 142.0117 | 142.8625 | 154.2261 | 122.319 | 134.6996
390.5115 | 285.5115 | 305.6723 | 142.2922 | 143.1584 | 154.4572 | 122.5204 | 134.9865
391.513 | 286.513 | 305.6467 | 142.5547 | 143.4494 | 154.6893 | 122.728 | 135.2736
392.5144 | 287.5144 | 305.5765 | 142.8391 | 143.7304 | 154.9144 | 122.9203 | 135.5588
393.5158 | 288.5158 | 305.5003 | 143.1125 | 143.9935 | 155.14 | 123.1259 | 135.844
394.5173 | 289.5173 | 305.4672 | 143.3837 | 144.2426 | 155.3769 | 123.3228 | 136.1236
395.5187 | 290.5187 | 305.6149 | 143.6495 | 144.5091 | 155.6067 | 123.537 | 136.4078
396.5202 | 291.5202 | 305.6453 | 143.9205 | 144.76 | 155.8461 | 123.7446 | 136.6805
397.5116 | 292.5116 | 305.8044 | 144.1948 | 145.0125 | 156.09 | 123.943 | 136.963
398.513 | 293.513 | 305.8989 | 144.4705 | 145.2458 | 156.3317 | 124.158 | 137.2457
399.5145 | 294.5145 | 305.9932 | 144.755 | 145.5002 | 156.5816 | 124.3644 | 137.521
400.5159 | 295.5159 | 306.141 | 145.037 | 145.7355 | 156.8339 | 124.5809 | 137.8034
401.5174 | 296.5174 | 306.1443 | 145.3232 | 145.9812 | 157.0937 | 124.7883 | 138.0752
402.5188 | 297.5188 | 306.1721 | 145.6132 | 146.2238 | 157.3274 | 125.0017 | 138.3637
403.5202 | 298.5202 | 306.163 | 145.8954 | 146.4651 | 157.5643 | 125.2133 | 138.6307
404.5217 | 299.5217 | 306.2146 | 146.1817 | 146.7165 | 157.7968 | 125.4326 | 138.9086
405.5131 | 300.5131 | 306.1155 | 146.4701 | 146.9736 | 158.0337 | 125.6365 | 139.1782
406.5145 | 301.5145 | 306.0506 | 146.7557 | 147.2118 | 158.2574 | 125.8538 | 139.44
407.516 | 302.516 | 306.0047 | 147.0386 | 147.4709 | 158.4848 | 126.0512 | 139.7143
408.5174 | 303.5174 | 305.9386 | 147.3248 | 147.6991 | 158.7077 | 126.2604 | 139.9715
409.5189 | 304.5189 | 305.8803 | 147.6029 | 147.9509 | 158.93 | 126.4743 | 140.2503
410.5103 | 305.5103 | 305.798 | 147.8707 | 148.1987 | 159.1586 | 126.6706 | 140.5097
411.5117 | 306.5117 | 305.8314 | 148.1396 | 148.424 | 159.3936 | 126.8734 | 140.7696
412.5132 | 307.5132 | 305.8312 | 148.3966 | 148.6655 | 159.6261 | 127.0731 | 141.0353
413.5146 | 308.5146 | 305.7928 | 148.6633 | 148.9065 | 159.8688 | 127.2718 | 141.2962
414.516 | 309.516 | 305.7877 | 148.9183 | 149.1363 | 160.098 | 127.4716 | 141.559
415.5175 | 310.5175 | 305.7016 | 149.1775 | 149.3813 | 160.3331 | 127.6584 | 141.8226
416.5189 | 311.5189 | 305.699 | 149.4396 | 149.6277 | 160.5674 | 127.8711 | 142.0846
417.5204 | 312.5204 | 305.7473 | 149.6959 | 149.8549 | 160.7959 | 128.0756 | 142.3461
418.5218 | 313.5218 | 305.7705 | 149.9616 | 150.1076 | 161.0264 | 128.2815 | 142.6117
419.5132 | 314.5132 | 305.8788 | 150.2197 | 150.3414 | 161.2604 | 128.4893 | 142.8697
420.5147 | 315.5147 | 305.9746 | 150.4826 | 150.5862 | 161.502 | 128.6915 | 143.141
421.5161 | 316.5161 | 305.9995 | 150.7416 | 150.8258 | 161.7473 | 128.9043 | 143.405
422.5175 | 317.5175 | 305.9996 | 150.9975 | 151.0679 | 161.9991 | 129.1134 | 143.6706
423.519 | 318.519 | 306.0969 | 151.2557 | 151.3091 | 162.2555 | 129.3243 | 143.9225
424.5204 | 319.5204 | 306.0552 | 151.515 | 151.5564 | 162.5025 | 129.532 | 144.1883
425.5219 | 320.5219 | 306.032 | 151.7758 | 151.8291 | 162.7321 | 129.7367 | 144.4551
426.5133 | 321.5133 | 306.0501 | 152.0351 | 152.0996 | 162.9751 | 129.9307 | 144.7066
427.5147 | 322.5147 | 306.1528 | 152.2874 | 152.3496 | 163.2049 | 130.1357 | 144.9666
428.5162 | 323.5162 | 306.2325 | 152.552 | 152.5982 | 163.4346 | 130.3358 | 145.2224
429.5176 | 324.5176 | 306.2959 | 152.8098 | 152.8478 | 163.6622 | 130.543 | 145.4752
430.5191 | 325.5191 | 306.3629 | 153.0737 | 153.1108 | 163.8947 | 130.7553 | 145.7336
431.5205 | 326.5205 | 306.3128 | 153.3309 | 153.3465 | 164.1098 | 130.9452 | 145.9843
432.5119 | 327.5119 | 306.2713 | 153.5792 | 153.5835 | 164.3161 | 131.1439 | 146.2392
433.5134 | 328.5134 | 306.263 | 153.8157 | 153.8127 | 164.524 | 131.3397 | 146.4864
434.5148 | 329.5148 | 306.2274 | 154.0488 | 154.0564 | 164.7196 | 131.5386 | 146.7472
435.5162 | 330.5162 | 306.2783 | 154.2712 | 154.2971 | 164.9229 | 131.7338 | 146.9981
436.5177 | 331.5177 | 306.3336 | 154.4972 | 154.5363 | 165.1375 | 131.907 | 147.245
437.5191 | 332.5191 | 306.2966 | 154.7047 | 154.796 | 165.3498 | 132.1026 | 147.4907
438.5105 | 333.5105 | 306.4012 | 154.9134 | 155.0456 | 165.5569 | 132.2789 | 147.7405
439.512 | 334.512 | 306.4735 | 155.108 | 155.3067 | 165.7635 | 132.4488 | 147.9906
440.5134 | 335.5134 | 306.5185 | 155.3112 | 155.549 | 165.9668 | 132.6267 | 148.2366
441.5149 | 336.5149 | 306.5263 | 155.5129 | 155.7857 | 166.1661 | 132.8049 | 148.483
442.5163 | 337.5163 | 306.5657 | 155.7195 | 156.0175 | 166.3712 | 132.9798 | 148.7262
443.5177 | 338.5177 | 306.6118 | 155.9263 | 156.2646 | 166.5728 | 133.1259 | 148.9689
444.5192 | 339.5192 | 306.661 | 156.1394 | 156.5105 | 166.7816 | 133.3079 | 149.2078
445.5206 | 340.5206 | 306.726 | 156.3555 | 156.7433 | 166.9824 | 133.4806 | 149.4555
446.5121 | 341.5121 | 306.6987 | 156.5667 | 156.9723 | 167.1856 | 133.6538 | 149.693
447.5135 | 342.5135 | 306.6311 | 156.791 | 157.4466 | 167.3791 | 133.8284 | 149.9337
448.5149 | 343.5149 | 306.5452 | 157.0087 | 157.879 | 167.5614 | 133.9988 | 150.1753
449.5164 | 344.5164 | 306.4004 | 157.2206 | 158.2299 | 167.7561 | 134.1829 | 150.4073
450.5178 | 345.5178 | 306.3303 | 157.437 | 158.5705 | 167.9515 | 134.3496 | 150.6459
451.5193 | 346.5193 | 306.2923 | 157.6452 | 158.876 | 168.135 | 134.5197 | 150.8818
452.5107 | 347.5107 | 306.3016 | 157.8514 | 159.171 | 168.329 | 134.6981 | 151.1128
453.5121 | 348.5121 | 306.2589 | 158.0673 | 159.4627 | 168.5268 | 134.8771 | 151.3456
454.5136 | 349.5136 | 306.3501 | 158.2708 | 159.7669 | 168.7199 | 135.0639 | 151.5912
455.515 | 350.515 | 306.4447 | 158.4824 | 160.0529 | 168.9112 | 135.227 | 151.8182
456.5164 | 351.5164 | 306.496 | 158.6805 | 160.3399 | 169.1021 | 135.4051 | 152.0529
457.5179 | 352.5179 | 306.478 | 158.8935 | 160.6137 | 169.293 | 135.5898 | 152.2787
458.5193 | 353.5193 | 306.445 | 159.0946 | 160.8666 | 169.4893 | 135.7651 | 152.513
459.5107 | 354.5107 | 306.4657 | 159.2915 | 161.1367 | 169.6882 | 135.9412 | 152.7465
460.5222 | 355.5222 | 306.466 | 159.4899 | 161.4052 | 169.8915 | 136.1141 | 152.9736
461.5136 | 356.5136 | 306.4076 | 159.698 | 161.6613 | 170.1035 | 136.2947 | 153.1974
462.5151 | 357.5151 | 306.3296 | 159.8932 | 161.9405 | 170.3212 | 136.4715 | 153.4176
463.5165 | 358.5165 | 306.2063 | 160.0958 | 162.2022 | 170.553 | 136.6436 | 153.6487
464.5179 | 359.5179 | 306.1647 | 160.2937 | 162.4684 | 170.7851 | 136.8366 | 153.8692
465.5194 | 360.5194 | 306.0116 | 160.4851 | 162.6745 | 171.0152 | 137.0088 | 154.0872
466.5208 | 361.5208 | 305.9715 | 160.6852 | 162.7251 | 171.2485 | 137.203 | 154.313
467.5122 | 362.5122 | 305.9877 | 160.8831 | 162.8749 | 171.4811 | 137.3733 | 154.5262
468.5137 | 363.5137 | 305.8912 | 161.0734 | 163.0676 | 171.7024 | 137.5584 | 154.7415
469.5151 | 364.5151 | 305.8568 | 161.2793 | 163.2773 | 171.9177 | 137.732 | 154.9579
470.5166 | 365.5166 | 305.7838 | 161.4729 | 163.5053 | 172.1385 | 137.932 | 155.1777
471.518 | 366.518 | 305.6305 | 161.6729 | 163.7448 | 172.341 | 138.1128 | 155.3894
472.5194 | 367.5194 | 305.61 | 161.8666 | 163.9801 | 172.5531 | 138.2882 | 155.6063
473.5109 | 368.5109 | 305.5244 | 162.0721 | 164.1984 | 172.7663 | 138.461 | 155.8278
474.5123 | 369.5123 | 305.5351 | 162.2819 | 164.4324 | 172.9721 | 138.6275 | 156.0324
475.5138 | 370.5138 | 305.563 | 162.4925 | 164.6658 | 173.1863 | 138.817 | 156.249
476.5152 | 371.5152 | 305.5696 | 162.7067 | 164.8881 | 173.3854 | 138.9988 | 156.4624
477.5166 | 372.5166 | 305.5403 | 162.9206 | 165.1205 | 173.5907 | 139.1659 | 156.6683
478.5181 | 373.5181 | 305.5588 | 163.1368 | 165.3531 | 173.7947 | 139.3509 | 156.8701
479.5195 | 374.5195 | 305.6279 | 163.3529 | 165.5749 | 173.9987 | 139.5228 | 157.0768
480.5109 | 375.5109 | 305.6358 | 163.5654 | 165.7978 | 174.2009 | 139.7028 | 157.276
481.5124 | 376.5124 | 305.5361 | 163.7744 | 166.0284 | 174.398 | 139.8769 | 157.4751
482.5138 | 377.5138 | 305.5294 | 163.9797 | 166.2531 | 174.6162 | 140.0664 | 157.6732
483.5153 | 378.5153 | 305.6132 | 164.1833 | 166.475 | 174.8229 | 140.2448 | 157.8667
484.5167 | 379.5167 | 305.5495 | 164.3939 | 166.6806 | 175.0242 | 140.4166 | 158.0577
485.5181 | 380.5181 | 305.652 | 164.595 | 166.9301 | 175.2366 | 140.5905 | 158.2509
486.5196 | 381.5196 | 305.7154 | 164.7983 | 167.1597 | 175.4409 | 140.7849 | 158.4453
487.511 | 382.511 | 305.8 | 165.0096 | 167.39 | 175.6276 | 140.9639 | 158.6351
488.5124 | 383.5124 | 305.912 | 165.2201 | 167.6126 | 175.8063 | 141.133 | 158.826
489.5139 | 384.5139 | 305.9077 | 165.4364 | 167.8563 | 175.9809 | 141.3106 | 159.011
490.5153 | 385.5153 | 305.9101 | 165.6462 | 168.097 | 176.1498 | 141.4864 | 159.2026
491.5168 | 386.5168 | 305.9373 | 165.8604 | 168.3269 | 176.312 | 141.6638 | 159.3903
492.5182 | 387.5182 | 305.9646 | 166.0673 | 168.5588 | 176.464 | 141.8271 | 159.5688
493.5196 | 388.5196 | 305.969 | 166.2618 | 168.7896 | 176.6157 | 142.0082 | 159.7537
494.5111 | 389.5111 | 305.9175 | 166.4615 | 168.9969 | 176.7595 | 142.1654 | 159.9336
495.5125 | 390.5125 | 305.9722 | 166.6614 | 169.2286 | 176.9046 | 142.3456 | 160.1179
496.514 | 391.514 | 306.0758 | 166.8477 | 169.4387 | 177.0427 | 142.5055 | 160.2954
497.5154 | 392.5154 | 306.1317 | 167.0519 | 169.6471 | 177.1936 | 142.6678 | 160.4874
498.5168 | 393.5168 | 306.18 | 167.237 | 169.8429 | 177.3342 | 142.8329 | 160.6674
499.5183 | 394.5183 | 306.1637 | 167.4282 | 170.0478 | 177.4512 | 142.9773 | 160.8516
500.5197 | 395.5197 | 306.0615 | 167.5973 | 170.2421 | 177.5842 | 143.131 | 161.0345
501.5111 | 396.5111 | 305.9451 | 167.7835 | 170.4573 | 177.7132 | 143.2955 | 161.2189
502.5126 | 397.5126 | 305.8094 | 167.9631 | 170.6805 | 177.8479 | 143.447 | 161.4007
503.514 | 398.514 | 305.8011 | 168.1532 | 170.874 | 177.9802 | 143.6 | 161.5921
504.5155 | 399.5155 | 305.6628 | 168.3393 | 171.0887 | 178.1163 | 143.7618 | 161.781
505.5169 | 400.5169 | 305.6065 | 168.5353 | 171.2915 | 178.2597 | 143.9132 | 161.9663
506.5183 | 401.5183 | 305.6245 | 168.717 | 171.4939 | 178.4081 | 144.0506 | 162.1472
507.5198 | 402.5198 | 305.7269 | 168.9131 | 171.7108 | 178.5725 | 144.1902 | 162.3261
508.5212 | 403.5212 | 305.605 | 169.098 | 171.914 | 178.7422 | 144.3488 | 162.51
509.5126 | 404.5126 | 305.5547 | 169.2866 | 172.1159 | 178.9194 | 144.4971 | 162.6869
510.5141 | 405.5141 | 305.5481 | 169.4748 | 172.3234 | 179.1001 | 144.6483 | 162.8684
511.5155 | 406.5155 | 305.5692 | 169.6501 | 172.5424 | 179.2749 | 144.8011 | 163.0383
512.517 | 407.517 | 305.5129 | 169.8343 | 172.7518 | 179.4589 | 144.946 | 163.2103
513.5184 | 408.5184 | 305.3914 | 170.0033 | 172.952 | 179.6469 | 145.1004 | 163.3908
514.5198 | 409.5198 | 305.3012 | 170.1624 | 173.1537 | 179.8258 | 145.2612 | 163.557
515.5113 | 410.5113 | 305.286 | 170.33 | 173.3596 | 180.0041 | 145.4079 | 163.7293
516.5127 | 411.5127 | 305.3364 | 170.4889 | 173.5656 | 180.1876 | 145.5518 | 163.8994
517.5141 | 412.5141 | 305.3911 | 170.6446 | 173.7651 | 180.3746 | 145.6977 | 164.0785
518.5256 | 413.5256 | 305.4829 | 170.813 | 173.9806 | 180.5735 | 145.8416 | 164.2476
519.517 | 414.517 | 305.5671 | 170.9701 | 174.1566 | 180.7635 | 145.9601 | 164.4118
520.5185 | 415.5185 | 305.5074 | 171.1354 | 174.366 | 180.9621 | 146.1047 | 164.5808
521.5199 | 416.5199 | 305.4381 | 171.3062 | 174.557 | 181.1596 | 146.2354 | 164.7504
522.5113 | 417.5113 | 305.4346 | 171.465 | 174.741 | 181.3657 | 146.3631 | 164.9109
523.5128 | 418.5128 | 305.3979 | 171.6331 | 174.9331 | 181.5577 | 146.5103 | 165.075
524.5142 | 419.5142 | 305.3545 | 171.7843 | 175.1104 | 181.7666 | 146.6326 | 165.242
525.5157 | 420.5157 | 305.26 | 171.9433 | 175.3046 | 181.9616 | 146.7845 | 165.4108
526.5171 | 421.5171 | 305.1644 | 172.1055 | 175.4987 | 182.1582 | 146.9121 | 165.5794
527.5185 | 422.5185 | 305.1288 | 172.2587 | 175.6806 | 182.3465 | 147.0592 | 165.7356
528.52 | 423.52 | 305.1434 | 172.4232 | 175.8689 | 182.5143 | 147.1874 | 165.9098
529.5114 | 424.5114 | 305.1695 | 172.5932 | 176.0593 | 182.6893 | 147.3391 | 166.0739
530.5128 | 425.5128 | 305.1758 | 172.7523 | 176.2328 | 182.8729 | 147.4924 | 166.2378
531.5143 | 426.5143 | 305.1026 | 172.9193 | 176.4353 | 183.0416 | 147.6381 | 166.4087
532.5157 | 427.5157 | 305.0316 | 173.0822 | 176.6297 | 183.2123 | 147.781 | 166.5721
533.5172 | 428.5172 | 304.9383 | 173.257 | 176.8162 | 183.3759 | 147.9408 | 166.7289
534.5186 | 429.5186 | 304.9896 | 173.4246 | 177.0144 | 183.5427 | 148.0754 | 166.8984
535.52 | 430.52 | 305.0966 | 173.597 | 177.1965 | 183.7062 | 148.2473 | 167.0639
536.5115 | 431.5115 | 305.0899 | 173.7741 | 177.3881 | 183.8623 | 148.3921 | 167.2199
537.5129 | 432.5129 | 305.1129 | 173.9525 | 177.5799 | 184.017 | 148.5462 | 167.3833
538.5143 | 433.5143 | 305.1778 | 174.1286 | 177.7536 | 184.1647 | 148.6967 | 167.548
539.5158 | 434.5158 | 305.0399 | 174.3053 | 177.9256 | 184.3017 | 148.8546 | 167.6972
540.5172 | 435.5172 | 305.0585 | 174.4725 | 178.1059 | 184.4497 | 148.9995 | 167.8458
541.5187 | 436.5187 | 305.2475 | 174.6468 | 178.2803 | 184.6049 | 149.1621 | 167.9973
542.5201 | 437.5201 | 305.4152 | 174.809 | 178.4459 | 184.7577 | 149.309 | 168.1381
543.5115 | 438.5115 | 305.4699 | 174.9766 | 178.608 | 184.9043 | 149.4691 | 168.2913
544.513 | 439.513 | 305.444 | 175.1451 | 178.7686 | 185.0516 | 149.6062 | 168.4393
545.5144 | 440.5144 | 305.4932 | 175.3012 | 178.9363 | 185.2062 | 149.7653 | 168.5945
546.5159 | 441.5159 | 305.6507 | 175.4733 | 179.0978 | 185.3554 | 149.9324 | 168.7374
547.5173 | 442.5173 | 305.754 | 175.6398 | 179.2641 | 185.5103 | 150.0852 | 168.8813
548.5187 | 443.5187 | 305.7383 | 175.8159 | 179.4404 | 185.6686 | 150.2305 | 169.0287
549.5202 | 444.5202 | 305.7476 | 175.9867 | 179.6151 | 185.8248 | 150.3946 | 169.1788
550.5216 | 445.5216 | 305.8318 | 176.1635 | 179.798 | 185.9863 | 150.5606 | 169.3395
551.513 | 446.513 | 305.8846 | 176.3298 | 179.9744 | 186.1214 | 150.7203 | 169.4844
552.5145 | 447.5145 | 305.8992 | 176.4903 | 180.1575 | 186.278 | 150.876 | 169.6412
553.5159 | 448.5159 | 305.9645 | 176.6589 | 180.3343 | 186.4197 | 151.0515 | 169.7851
554.5174 | 449.5174 | 306.1387 | 176.8153 | 180.5218 | 186.5691 | 151.2085 | 169.937
555.5188 | 450.5188 | 306.2427 | 176.9663 | 180.6965 | 186.72 | 151.3827 | 170.0884
556.5202 | 451.5202 | 306.2569 | 177.1312 | 180.8917 | 186.8538 | 151.5485 | 170.2341
557.5117 | 452.5117 | 306.302 | 177.2885 | 181.0543 | 187.0024 | 151.7164 | 170.3827
558.5131 | 453.5131 | 306.2044 | 177.4435 | 181.2204 | 187.1415 | 151.8725 | 170.5228
559.5145 | 454.5145 | 306.021 | 177.6009 | 181.3941 | 187.2911 | 152.0455 | 170.675
560.516 | 455.516 | 306.0195 | 177.7536 | 181.5538 | 187.435 | 152.2029 | 170.8218
561.5174 | 456.5174 | 306.0527 | 177.9054 | 181.7305 | 187.5402 | 152.3756 | 170.9666
562.5189 | 457.5189 | 306.1796 | 178.0607 | 181.906 | 187.6877 | 152.5316 | 171.1113
563.5103 | 458.5103 | 306.2588 | 178.2191 | 182.0592 | 187.8206 | 152.6978 | 171.2543
564.5117 | 459.5117 | 306.2278 | 178.3719 | 182.2226 | 187.9456 | 152.8502 | 171.4034
565.5132 | 460.5132 | 306.1234 | 178.5236 | 182.3908 | 188.0635 | 153.0154 | 171.5423
566.5146 | 461.5146 | 306.0337 | 178.6827 | 182.5618 | 188.1936 | 153.1888 | 171.682
567.516 | 462.516 | 306.0201 | 178.8353 | 182.7257 | 188.3236 | 153.3592 | 171.8233
568.5175 | 463.5175 | 306.0207 | 178.9961 | 182.8835 | 188.4415 | 153.5129 | 171.9728
569.5189 | 464.5189 | 305.9549 | 179.1499 | 183.0499 | 188.5763 | 153.6831 | 172.1192
570.5204 | 465.5204 | 305.9123 | 179.3085 | 183.2103 | 188.6975 | 153.8301 | 172.2601
571.5118 | 466.5118 | 305.8689 | 179.4583 | 183.3798 | 188.8189 | 153.9776 | 172.4055
572.5132 | 467.5132 | 305.7975 | 179.6117 | 183.5349 | 188.9361 | 154.1225 | 172.5397
573.5147 | 468.5147 | 305.7798 | 179.7717 | 183.6893 | 189.047 | 154.2816 | 172.6805
574.5161 | 469.5161 | 305.7771 | 179.9146 | 183.843 | 189.1578 | 154.4205 | 172.8188
575.5176 | 470.5176 | 305.7689 | 180.0576 | 183.9818 | 189.2641 | 154.5746 | 172.9586
576.519 | 471.519 | 305.6897 | 180.2052 | 184.1167 | 189.3854 | 154.7149 | 173.091
577.5204 | 472.5204 | 305.6731 | 180.3359 | 184.2635 | 189.5096 | 154.8515 | 173.2379
578.5219 | 473.5219 | 305.6685 | 180.4767 | 184.4001 | 189.6115 | 154.9911 | 173.3653
579.5133 | 474.5133 | 305.7174 | 180.6068 | 184.5369 | 189.7338 | 155.1266 | 173.5081
580.5147 | 475.5147 | 305.7817 | 180.7318 | 184.6809 | 189.877 | 155.2645 | 173.6495
581.6464 | 476.6464 | 305.808 | 180.8816 | 184.8332 | 190.0123 | 155.4083 | 173.8114
582.5176 | 477.5176 | 305.8549 | 180.9868 | 184.9484 | 190.1361 | 155.5245 | 173.9351
583.5191 | 478.5191 | 305.9184 | 181.1021 | 185.086 | 190.268 | 155.6557 | 174.0656
584.5205 | 479.5205 | 305.8809 | 181.2205 | 185.2314 | 190.4136 | 155.7926 | 174.1961
585.5119 | 480.5119 | 305.8876 | 181.3348 | 185.3603 | 190.5578 | 155.919 | 174.3373
586.5134 | 481.5134 | 305.8501 | 181.4419 | 185.5121 | 190.7108 | 156.0476 | 174.4639
587.5148 | 482.5148 | 305.8393 | 181.5453 | 185.6664 | 190.8318 | 156.1818 | 174.6018
588.5162 | 483.5162 | 305.8178 | 181.6503 | 185.8123 | 190.9684 | 156.3053 | 174.7328
589.5177 | 484.5177 | 305.8611 | 181.7582 | 185.9647 | 191.1009 | 156.4262 | 174.8733
590.5191 | 485.5191 | 305.903 | 181.8703 | 186.1116 | 191.2459 | 156.5272 | 175.0077
591.5206 | 486.5206 | 305.9319 | 181.9754 | 186.2562 | 191.3847 | 156.6568 | 175.1488
592.512 | 487.512 | 305.9445 | 182.082 | 186.3994 | 191.5339 | 156.7779 | 175.2792
593.5134 | 488.5134 | 305.885 | 182.1815 | 186.5553 | 191.6578 | 156.9009 | 175.4223
594.5149 | 489.5149 | 305.8848 | 182.2866 | 186.6971 | 191.7903 | 157.0146 | 175.5583
595.5163 | 490.5163 | 305.8934 | 182.3909 | 186.8542 | 191.9436 | 157.1354 | 175.6984
596.5178 | 491.5178 | 305.9121 | 182.4985 | 186.9941 | 192.0772 | 157.2422 | 175.8367
597.5192 | 492.5192 | 305.917 | 182.6075 | 187.1375 | 192.2057 | 157.358 | 175.9781
598.5206 | 493.5206 | 305.9395 | 182.7212 | 187.2869 | 192.3193 | 157.4822 | 176.109
599.5221 | 494.5221 | 306.0282 | 182.8435 | 187.4302 | 192.4494 | 157.5958 | 176.2493
600.5135 | 495.5135 | 306.0943 | 182.9761 | 187.5612 | 192.5547 | 157.7128 | 176.3838
601.5149 | 496.5149 | 306.0864 | 183.1079 | 187.6859 | 192.6693 | 157.8186 | 176.5278
602.5164 | 497.5164 | 306.0393 | 183.2423 | 187.8227 | 192.7875 | 157.9477 | 176.6599
603.5178 | 498.5178 | 305.979 | 183.3818 | 187.9713 | 192.9014 | 158.0698 | 176.7929
604.5193 | 499.5193 | 306.0321 | 183.5067 | 188.1094 | 193.0008 | 158.1733 | 176.9264
605.5107 | 500.5107 | 306.0793 | 183.62 | 188.2361 | 193.1153 | 158.2963 | 177.0475
606.5121 | 501.5121 | 306.1216 | 183.7443 | 188.37 | 193.2291 | 158.4315 | 177.1673
607.5136 | 502.5136 | 306.0718 | 183.8573 | 188.5009 | 193.3366 | 158.5551 | 177.2947
608.515 | 503.515 | 306.0086 | 183.9874 | 188.6375 | 193.4529 | 158.6712 | 177.4248
609.5164 | 504.5164 | 305.9616 | 184.1109 | 188.7687 | 193.5408 | 158.7899 | 177.549
610.5179 | 505.5179 | 306.0149 | 184.2354 | 188.9022 | 193.6424 | 158.9192 | 177.6698
611.5193 | 506.5193 | 306.0317 | 184.3662 | 189.0383 | 193.7448 | 159.0374 | 177.792
612.5107 | 507.5107 | 305.9794 | 184.4941 | 189.1735 | 193.8283 | 159.1527 | 177.9114
613.5122 | 508.5122 | 305.9812 | 184.6251 | 189.2974 | 193.9486 | 159.2631 | 178.0289
614.5136 | 509.5136 | 306.0521 | 184.7511 | 189.4307 | 194.0483 | 159.3824 | 178.1568
615.5151 | 510.5151 | 306.0219 | 184.8913 | 189.5609 | 194.1479 | 159.5001 | 178.2743
616.5165 | 511.5165 | 306.0993 | 185.0184 | 189.6989 | 194.2567 | 159.6016 | 178.394
617.5179 | 512.5179 | 306.1427 | 185.1545 | 189.8318 | 194.3574 | 159.7183 | 178.5056
618.5194 | 513.5194 | 306.0547 | 185.2931 | 189.9678 | 194.4618 | 159.8395 | 178.6154
619.5208 | 514.5208 | 306.0056 | 185.4183 | 190.116 | 194.5756 | 159.9487 | 178.7331
620.5123 | 515.5123 | 305.9678 | 185.5509 | 190.2463 | 194.6893 | 160.0692 | 178.8445
621.5137 | 516.5137 | 305.8965 | 185.6658 | 190.3844 | 194.7997 | 160.1989 | 178.9515
622.5151 | 517.5151 | 305.825 | 185.7838 | 190.5298 | 194.894 | 160.315 | 179.0735
623.5166 | 518.5166 | 305.7406 | 185.8884 | 190.6641 | 194.9524 | 160.4311 | 179.1863
624.518 | 519.518 | 305.7516 | 185.9903 | 190.8056 | 195.0454 | 160.5324 | 179.3001
625.5195 | 520.5195 | 305.7079 | 186.0954 | 190.9456 | 195.1326 | 160.6345 | 179.4104
626.5109 | 521.5109 | 305.6532 | 186.1842 | 191.0778 | 195.2263 | 160.7662 | 179.5175
627.5123 | 522.5123 | 305.5493 | 186.2974 | 191.2121 | 195.3286 | 160.8816 | 179.6381
628.5138 | 523.5138 | 305.5085 | 186.3998 | 191.3457 | 195.429 | 160.9867 | 179.7479
629.5152 | 524.5152 | 305.3612 | 186.5013 | 191.4774 | 195.5391 | 161.0864 | 179.8616
630.5166 | 525.5166 | 305.2662 | 186.5969 | 191.6109 | 195.6662 | 161.2012 | 179.9677
631.5181 | 526.5181 | 305.1948 | 186.7061 | 191.7505 | 195.7783 | 161.3233 | 180.0776
632.5195 | 527.5195 | 305.1653 | 186.8149 | 191.8919 | 195.8686 | 161.4398 | 180.1875
633.521 | 528.521 | 305.1188 | 186.9263 | 192.0196 | 195.9784 | 161.5484 | 180.2992
634.5224 | 529.5224 | 305.1315 | 187.0254 | 192.1667 | 196.0846 | 161.6501 | 180.4026
635.5138 | 530.5138 | 305.1254 | 187.1241 | 192.2967 | 196.1926 | 161.7544 | 180.5139
636.5153 | 531.5153 | 305.1615 | 187.2201 | 192.4349 | 196.2954 | 161.8588 | 180.6196
637.5167 | 532.5167 | 305.1413 | 187.3015 | 192.5516 | 196.3833 | 161.9621 | 180.7249
638.5282 | 533.5282 | 305.0601 | 187.3673 | 192.6798 | 196.4202 | 162.0689 | 180.832
639.5196 | 534.5196 | 305.0107 | 187.4524 | 192.8007 | 196.5182 | 162.1801 | 180.9341
640.521 | 535.521 | 305.0375 | 187.535 | 192.9126 | 196.5993 | 162.2766 | 181.0362
641.5124 | 536.5124 | 305.0534 | 187.6146 | 193.0065 | 196.6636 | 162.3626 | 181.1368
642.5139 | 537.5139 | 305.0884 | 187.7121 | 193.1267 | 196.7434 | 162.4724 | 181.2455
643.5153 | 538.5153 | 305.0501 | 187.8045 | 193.2395 | 196.8079 | 162.585 | 181.352
644.5168 | 539.5168 | 305.0752 | 187.9029 | 193.3431 | 196.9091 | 162.6717 | 181.4588
645.5182 | 540.5182 | 305.1976 | 188.0019 | 193.449 | 197.0105 | 162.7825 | 181.5707
646.5196 | 541.5196 | 305.4032 | 188.0967 | 193.5393 | 197.1076 | 162.8878 | 181.6741
647.5111 | 542.5111 | 305.5244 | 188.187 | 193.6554 | 197.1812 | 162.9883 | 181.7835
648.5125 | 543.5125 | 305.5459 | 188.2728 | 193.7617 | 197.3039 | 163.0954 | 181.8924
649.514 | 544.514 | 305.5732 | 188.3627 | 193.8523 | 197.4286 | 163.2001 | 182.0079
650.5154 | 545.5154 | 305.5402 | 188.4484 | 193.9525 | 197.493 | 163.3052 | 182.12
651.5168 | 546.5168 | 305.55 | 188.5342 | 194.0427 | 197.5898 | 163.4094 | 182.2297
652.5183 | 547.5183 | 305.5502 | 188.6335 | 194.1379 | 197.7005 | 163.5134 | 182.3319
653.5197 | 548.5197 | 305.5265 | 188.725 | 194.2275 | 197.7908 | 163.6234 | 182.4398
654.5111 | 549.5111 | 305.4334 | 188.8192 | 194.33 | 197.8957 | 163.7271 | 182.5486
655.5126 | 550.5126 | 305.4334 | 188.9166 | 194.435 | 197.9136 | 163.8194 | 182.6472
656.514 | 551.514 | 305.4315 | 189.0113 | 194.5443 | 198.0106 | 163.9327 | 182.7565
657.5155 | 552.5155 | 305.5067 | 189.1036 | 194.6339 | 198.0535 | 164.0404 | 182.8645
658.5169 | 553.5169 | 305.632 | 189.1862 | 194.7376 | 198.0738 | 164.1366 | 182.9694
659.5183 | 554.5183 | 305.7415 | 189.271 | 194.8258 | 198.1536 | 164.2348 | 183.0831
660.5198 | 555.5198 | 305.8395 | 189.346 | 194.9234 | 198.1687 | 164.3367 | 183.1843
661.5212 | 556.5212 | 305.9957 | 189.418 | 195.018 | 198.2597 | 164.4252 | 183.2978
662.5126 | 557.5126 | 305.9843 | 189.4926 | 195.117 | 198.3302 | 164.5181 | 183.4064
663.5141 | 558.5141 | 305.9959 | 189.5721 | 195.2303 | 198.4297 | 164.6219 | 183.5164
664.5155 | 559.5155 | 306.0509 | 189.6622 | 195.3338 | 198.557 | 164.7285 | 183.6313
665.517 | 560.517 | 306.1214 | 189.748 | 195.4452 | 198.6759 | 164.8298 | 183.7313
666.5184 | 561.5184 | 306.2176 | 189.8322 | 195.5449 | 198.7968 | 164.9178 | 183.8515
667.5198 | 562.5198 | 306.324 | 189.9249 | 195.6593 | 198.9484 | 165.0306 | 183.961
668.5113 | 563.5113 | 306.4391 | 190.0167 | 195.7773 | 199.1088 | 165.1361 | 184.0654
669.5127 | 564.5127 | 306.4058 | 190.1101 | 195.8855 | 199.2763 | 165.24 | 184.1767
670.5142 | 565.5142 | 306.3769 | 190.2077 | 196.0012 | 199.4349 | 165.3355 | 184.2858
671.5156 | 566.5156 | 306.4707 | 190.3001 | 196.1265 | 199.5622 | 165.4513 | 184.3835
672.517 | 567.517 | 306.5404 | 190.3978 | 196.2468 | 199.7151 | 165.5601 | 184.489
673.5185 | 568.5185 | 306.5989 | 190.4949 | 196.3676 | 199.8098 | 165.6711 | 184.5779
674.5199 | 569.5199 | 306.6705 | 190.5861 | 196.4808 | 199.9472 | 165.7788 | 184.671
675.5214 | 570.5214 | 306.6911 | 190.6746 | 196.5966 | 200.0415 | 165.8934 | 184.7742
676.5128 | 571.5128 | 306.6471 | 190.7761 | 196.7082 | 200.1535 | 166.0167 | 184.8698
677.5142 | 572.5142 | 306.7019 | 190.8561 | 196.8239 | 200.2208 | 166.1331 | 184.963
678.5157 | 573.5157 | 306.7115 | 190.9386 | 196.939 | 200.3247 | 166.265 | 185.0679
679.5171 | 574.5171 | 306.6836 | 191.0233 | 197.029 | 200.4356 | 166.3779 | 185.1576
680.5185 | 575.5185 | 306.6468 | 191.0999 | 197.1412 | 200.53 | 166.5136 | 185.2608
681.52 | 576.52 | 306.6826 | 191.2013 | 197.2387 | 200.6495 | 166.6186 | 185.3448
682.5214 | 577.5214 | 306.7289 | 191.2832 | 197.3249 | 200.7843 | 166.758 | 185.4358
683.5128 | 578.5128 | 306.6904 | 191.3848 | 197.4174 | 200.887 | 166.8737 | 185.5286
684.5143 | 579.5143 | 306.6606 | 191.4827 | 197.5298 | 200.9655 | 166.9945 | 185.6153
685.5157 | 580.5157 | 306.6512 | 191.5902 | 197.6347 | 201.0553 | 167.1163 | 185.7018
686.5172 | 581.5172 | 306.5854 | 191.6916 | 197.7269 | 201.1274 | 167.2561 | 185.7857
687.5186 | 582.5186 | 306.52 | 191.7917 | 197.8447 | 201.1548 | 167.3818 | 185.8719
688.52 | 583.52 | 306.5081 | 191.8938 | 197.9472 | 201.2074 | 167.5077 | 185.9563
689.5115 | 584.5115 | 306.4348 | 191.9909 | 198.0555 | 201.2954 | 167.642 | 186.052
690.5129 | 585.5129 | 306.3644 | 192.087 | 198.1516 | 201.332 | 167.7728 | 186.1354
691.5143 | 586.5143 | 306.4561 | 192.1833 | 198.266 | 201.3489 | 167.8777 | 186.2165
692.5158 | 587.5158 | 306.52 | 192.2902 | 198.3634 | 201.42 | 168.0064 | 186.303
693.5172 | 588.5172 | 306.6014 | 192.3831 | 198.4771 | 201.4431 | 168.1105 | 186.387
694.5187 | 589.5187 | 306.5322 | 192.4725 | 198.5825 | 201.5015 | 168.247 | 186.4645
695.5201 | 590.5201 | 306.4297 | 192.5711 | 198.6911 | 201.5218 | 168.3657 | 186.5522
696.5115 | 591.5115 | 306.5211 | 192.6708 | 198.8051 | 201.6224 | 168.4807 | 186.6312
697.513 | 592.513 | 306.636 | 192.7575 | 198.9201 | 201.7145 | 168.6054 | 186.7087
698.5144 | 593.5144 | 306.6895 | 192.8666 | 199.0378 | 201.7971 | 168.7301 | 186.7888
699.5159 | 594.5159 | 306.6869 | 192.9624 | 199.1393 | 201.9245 | 168.8548 | 186.8741
700.5173 | 595.5173 | 306.7232 | 193.063 | 199.2584 | 201.9647 | 168.9795 | 186.9514
701.5187 | 596.5187 | 306.6239 | 193.161 | 199.3722 | 202.0509 | 169.0979 | 187.025
702.5202 | 597.5202 | 306.6198 | 193.2574 | 199.4993 | 202.1482 | 169.2274 | 187.09
703.5216 | 598.5216 | 306.5792 | 193.3421 | 199.6145 | 202.2371 | 169.349 | 187.1642
704.513 | 599.513 | 306.5306 | 193.4281 | 199.7307 | 202.3392 | 169.4681 | 187.224
705.5145 | 600.5145 | 306.5555 | 193.5096 | 199.8712 | 202.3464 | 169.6005 | 187.2996
706.5159 | 601.5159 | 306.4832 | 193.5889 | 199.9985 | 202.4396 | 169.7123 | 187.3674
707.5174 | 602.5174 | 306.506 | 193.6803 | 200.113 | 202.554 | 169.8417 | 187.4453
708.5188 | 603.5188 | 306.474 | 193.7648 | 200.2409 | 202.6425 | 169.9728 | 187.5123
709.5202 | 604.5202 | 306.2967 | 193.8506 | 200.356 | 202.7059 | 170.0817 | 187.5789
710.5117 | 605.5117 | 306.1111 | 193.9471 | 200.4601 | 202.8204 | 170.2019 | 187.6458
711.5131 | 606.5131 | 306.0473 | 194.0396 | 200.5666 | 202.9116 | 170.3224 | 187.7154
712.5145 | 607.5145 | 305.9389 | 194.1363 | 200.6702 | 202.9906 | 170.4457 | 187.7764
713.516 | 608.516 | 305.9238 | 194.224 | 200.7845 | 203.0875 | 170.5686 | 187.8505
714.5174 | 609.5174 | 305.9602 | 194.3205 | 200.8873 | 203.1864 | 170.6794 | 187.9168
715.5189 | 610.5189 | 306.0373 | 194.408 | 200.9963 | 203.2634 | 170.7822 | 187.9763
716.5103 | 611.5103 | 306.0238 | 194.4983 | 201.0931 | 203.3213 | 170.8947 | 188.0371
717.5117 | 612.5117 | 305.9515 | 194.5906 | 201.2147 | 203.4433 | 171.009 | 188.1092
718.5132 | 613.5132 | 305.9136 | 194.664 | 201.3173 | 203.5405 | 171.1115 | 188.1628
719.5146 | 614.5146 | 305.8779 | 194.7589 | 201.416 | 203.6753 | 171.223 | 188.2435
720.5161 | 615.5161 | 305.7561 | 194.8289 | 201.5282 | 203.7929 | 171.3246 | 188.2999
721.5175 | 616.5175 | 305.602 | 194.9063 | 201.6377 | 203.9156 | 171.442 | 188.3661
722.5189 | 617.5189 | 305.3914 | 194.9791 | 201.7494 | 204.0374 | 171.5513 | 188.4284
723.5204 | 618.5204 | 305.1923 | 195.0531 | 201.8572 | 204.1399 | 171.6769 | 188.4896
724.5218 | 619.5218 | 305.1346 | 195.1379 | 201.9784 | 204.2594 | 171.7936 | 188.5572
725.5132 | 620.5132 | 305.0704 | 195.2121 | 202.0885 | 204.3559 | 171.9047 | 188.6176
726.5147 | 621.5147 | 305.0293 | 195.2899 | 202.2127 | 204.4164 | 172.0191 | 188.6875
727.5161 | 622.5161 | 305.0098 | 195.3752 | 202.3094 | 204.5196 | 172.1359 | 188.739
728.5176 | 623.5176 | 305.0262 | 195.4459 | 202.4395 | 204.5766 | 172.2435 | 188.8122
729.519 | 624.519 | 305.0186 | 195.5168 | 202.5513 | 204.6383 | 172.3675 | 188.8625
730.5204 | 625.5204 | 304.8573 | 195.5942 | 202.6673 | 204.7073 | 172.4932 | 188.9269
731.5119 | 626.5119 | 304.8078 | 195.6672 | 202.7545 | 204.7883 | 172.6077 | 188.9911
732.5133 | 627.5133 | 304.8456 | 195.7438 | 202.8782 | 204.8663 | 172.7322 | 189.0493
733.5147 | 628.5147 | 304.6763 | 195.8117 | 202.9786 | 204.9539 | 172.8404 | 189.108
734.5162 | 629.5162 | 304.5622 | 195.9017 | 203.0814 | 205.0405 | 172.9571 | 189.1721
735.5176 | 630.5176 | 304.5485 | 195.9912 | 203.1801 | 205.0357 | 173.0715 | 189.2305
736.5191 | 631.5191 | 304.5844 | 196.0739 | 203.2742 | 205.1615 | 173.1809 | 189.2847
737.5105 | 632.5105 | 304.6356 | 196.1523 | 203.3745 | 205.2282 | 173.2887 | 189.3402
738.5119 | 633.5119 | 304.6164 | 196.2296 | 203.4572 | 205.2846 | 173.4057 | 189.4023
739.5134 | 634.5134 | 304.5608 | 196.316 | 203.558 | 205.4014 | 173.5202 | 189.4445
740.5148 | 635.5148 | 304.4769 | 196.3801 | 203.6547 | 205.4885 | 173.6205 | 189.5
741.5162 | 636.5162 | 304.4452 | 196.4502 | 203.7563 | 205.6098 | 173.7079 | 189.561
742.5177 | 637.5177 | 304.402 | 196.5113 | 203.8459 | 205.7597 | 173.8068 | 189.618
743.5191 | 638.5191 | 304.4219 | 196.5739 | 203.9504 | 205.8782 | 173.894 | 189.6861
744.5206 | 639.5206 | 304.391 | 196.6317 | 204.0503 | 205.9648 | 173.9871 | 189.7423
745.522 | 640.522 | 304.4265 | 196.6526 | 204.142 | 206.1133 | 174.0792 | 189.8147
746.5134 | 641.5134 | 304.5204 | 196.6899 | 204.2524 | 206.2256 | 174.1757 | 189.8848
747.5149 | 642.5149 | 304.5474 | 196.724 | 204.3549 | 206.3574 | 174.2456 | 189.9543
748.5163 | 643.5163 | 304.6329 | 196.7479 | 204.4601 | 206.4306 | 174.325 | 190.0254
749.5178 | 644.5178 | 304.7426 | 196.785 | 204.5536 | 206.4976 | 174.4043 | 190.0995
750.5192 | 645.5192 | 304.8514 | 196.8151 | 204.6692 | 206.6556 | 174.4786 | 190.1681
751.5206 | 646.5206 | 304.8805 | 196.8618 | 204.7781 | 206.7161 | 174.5353 | 190.2389
752.5121 | 647.5121 | 304.9874 | 196.9172 | 204.8815 | 206.8574 | 174.6057 | 190.3151
753.5135 | 648.5135 | 305.1233 | 196.9505 | 204.9932 | 206.9897 | 174.6724 | 190.3878
754.5149 | 649.5149 | 305.224 | 197.0246 | 205.104 | 207.0969 | 174.7472 | 190.462
755.5164 | 650.5164 | 305.3627 | 197.0861 | 205.2159 | 207.2137 | 174.8182 | 190.5373
756.5178 | 651.5178 | 305.367 | 197.1466 | 205.328 | 207.2929 | 174.8868 | 190.6208
757.5193 | 652.5193 | 305.449 | 197.2238 | 205.4321 | 207.4122 | 174.9712 | 190.689
758.5107 | 653.5107 | 305.606 | 197.2882 | 205.5524 | 207.4682 | 175.0554 | 190.7652
759.5121 | 654.5121 | 305.781 | 197.3564 | 205.652 | 207.5123 | 175.1418 | 190.8413
760.5136 | 655.5136 | 305.8578 | 197.4377 | 205.7649 | 207.5751 | 175.2366 | 190.9116
761.515 | 656.515 | 306.0284 | 197.5058 | 205.8727 | 207.6826 | 175.3202 | 190.979
762.5164 | 657.5164 | 306.1604 | 197.5841 | 205.9874 | 207.812 | 175.4146 | 191.0496
763.5179 | 658.5179 | 306.2704 | 197.6672 | 206.0902 | 207.8829 | 175.5103 | 191.121
764.5193 | 659.5193 | 306.3889 | 197.7387 | 206.2011 | 207.9218 | 175.6231 | 191.1923
765.5208 | 660.5208 | 306.5604 | 197.8151 | 206.3058 | 207.9943 | 175.7193 | 191.264
766.5222 | 661.5222 | 306.6609 | 197.8994 | 206.4198 | 208.0809 | 175.8136 | 191.3433
767.5136 | 662.5136 | 306.7637 | 197.9856 | 206.5207 | 208.1165 | 175.9077 | 191.401
768.5151 | 663.5151 | 306.7739 | 198.0692 | 206.6234 | 208.1477 | 176.0094 | 191.4655
769.5165 | 664.5165 | 306.836 | 198.1461 | 206.7265 | 208.2253 | 176.1055 | 191.5267
770.518 | 665.518 | 306.9254 | 198.198 | 206.8223 | 208.3573 | 176.1816 | 191.5941
771.5194 | 666.5194 | 307.0777 | 198.2764 | 206.9135 | 208.4675 | 176.2742 | 191.6567
772.5208 | 667.5208 | 307.1383 | 198.3379 | 207.0095 | 208.5328 | 176.3486 | 191.7206
773.5123 | 668.5123 | 307.2485 | 198.4242 | 207.1006 | 208.69 | 176.4449 | 191.7864
774.5137 | 669.5137 | 307.2994 | 198.49 | 207.205 | 208.8184 | 176.5149 | 191.8595
775.5151 | 670.5151 | 307.3517 | 198.5279 | 207.2952 | 208.9017 | 176.6047 | 191.9222
776.5166 | 671.5166 | 307.3619 | 198.6225 | 207.3966 | 208.993 | 176.6877 | 191.9951
777.518 | 672.518 | 307.3921 | 198.6956 | 207.4987 | 209.1082 | 176.7682 | 192.0755
778.5195 | 673.5195 | 307.3182 | 198.7564 | 207.6075 | 209.2634 | 176.8426 | 192.1575
779.5109 | 674.5109 | 307.2456 | 198.8358 | 207.7149 | 209.2427 | 176.9161 | 192.2267
780.5123 | 675.5123 | 307.1769 | 198.915 | 207.8414 | 209.331 | 176.9961 | 192.2967
781.5138 | 676.5138 | 307.2054 | 198.9813 | 207.9578 | 209.4363 | 177.0648 | 192.368
782.5152 | 677.5152 | 307.2082 | 199.0648 | 208.0762 | 209.492 | 177.1442 | 192.4454
783.5166 | 678.5166 | 307.1008 | 199.124 | 208.1903 | 209.6101 | 177.2125 | 192.5173
784.5181 | 679.5181 | 307.0216 | 199.181 | 208.3057 | 209.7571 | 177.2842 | 192.5894
785.5195 | 680.5195 | 307.0299 | 199.2527 | 208.4194 | 209.8986 | 177.3531 | 192.665
786.5109 | 681.5109 | 307.0308 | 199.2916 | 208.5342 | 209.9967 | 177.4182 | 192.7321
787.5224 | 682.5224 | 307.0225 | 199.3279 | 208.659 | 210.1186 | 177.4965 | 192.8006
788.5138 | 683.5138 | 306.9161 | 199.3747 | 208.7755 | 210.2077 | 177.5803 | 192.8601
789.5153 | 684.5153 | 306.7982 | 199.447 | 208.8841 | 210.3194 | 177.6708 | 192.9246
790.5167 | 685.5167 | 306.7614 | 199.5108 | 209.0104 | 210.4245 | 177.7449 | 192.9863
791.5181 | 686.5181 | 306.6639 | 199.5727 | 209.1116 | 210.5277 | 177.846 | 193.0504
792.5196 | 687.5196 | 306.5293 | 199.6313 | 209.2286 | 210.6102 | 177.9581 | 193.104
793.521 | 688.521 | 306.4925 | 199.7171 | 209.341 | 210.708 | 178.0511 | 193.1501
794.5125 | 689.5125 | 306.476 | 199.7768 | 209.4544 | 210.6201 | 178.1502 | 193.2034
795.5139 | 690.5139 | 306.4335 | 199.8609 | 209.544 | 210.7025 | 178.251 | 193.2531
796.5153 | 691.5153 | 306.4087 | 199.9426 | 209.6414 | 210.7215 | 178.3479 | 193.2934
797.5168 | 692.5168 | 306.4218 | 200.0239 | 209.7413 | 210.706 | 178.4555 | 193.3342
798.5182 | 693.5182 | 306.3157 | 200.101 | 209.854 | 210.8182 | 178.5627 | 193.379
799.5197 | 694.5197 | 306.2048 | 200.1688 | 209.9393 | 210.9142 | 178.6634 | 193.4219
800.5111 | 695.5111 | 306.0118 | 200.2515 | 210.0459 | 210.9453 | 178.7593 | 193.4627
801.5125 | 696.5125 | 305.8626 | 200.3443 | 210.1497 | 211.0429 | 178.8582 | 193.5074
802.514 | 697.514 | 305.6861 | 200.4123 | 210.253 | 211.0525 | 178.9458 | 193.5511
803.5154 | 698.5154 | 305.5154 | 200.4624 | 210.346 | 211.0735 | 179.0315 | 193.5858
804.5168 | 699.5168 | 305.4864 | 200.5413 | 210.4459 | 211.0878 | 179.0974 | 193.6214
805.5183 | 700.5183 | 305.4354 | 200.5829 | 210.5372 | 211.062 | 179.1829 | 193.6522
806.5197 | 701.5197 | 305.3841 | 200.665 | 210.6327 | 211.1736 | 179.2531 | 193.6781
807.5111 | 702.5111 | 305.3784 | 200.7402 | 210.717 | 211.2406 | 179.3308 | 193.7118
808.5126 | 703.5126 | 305.3321 | 200.8069 | 210.8188 | 211.366 | 179.3918 | 193.7418
809.514 | 704.514 | 305.2657 | 200.8667 | 210.9016 | 211.4209 | 179.4639 | 193.7683
810.5155 | 705.5155 | 305.235 | 200.9383 | 211.0002 | 211.5316 | 179.5329 | 193.7982
811.5169 | 706.5169 | 305.2726 | 201.0021 | 211.0932 | 211.6465 | 179.608 | 193.8263
812.5183 | 707.5183 | 305.3678 | 201.0849 | 211.1852 | 211.7203 | 179.6723 | 193.8531
813.5198 | 708.5198 | 305.386 | 201.1199 | 211.2715 | 211.7605 | 179.7481 | 193.876
814.5212 | 709.5212 | 305.4016 | 201.157 | 211.3721 | 211.6434 | 179.8158 | 193.9117
815.5126 | 710.5126 | 305.4199 | 201.2208 | 211.4897 | 211.7532 | 179.8835 | 193.9443
816.5141 | 711.5141 | 305.4577 | 201.2845 | 211.5961 | 211.6554 | 179.9711 | 193.972
817.5155 | 712.5155 | 305.5415 | 201.3319 | 211.6927 | 211.847 | 180.0265 | 194.003
818.527 | 713.527 | 305.5977 | 201.4407 | 211.7801 | 211.8051 | 180.1136 | 194.0362
819.5184 | 714.5184 | 305.6804 | 201.5349 | 211.862 | 211.9948 | 180.186 | 194.064
820.5198 | 715.5198 | 305.7781 | 201.6126 | 211.9417 | 212.1418 | 180.2542 | 194.1024
821.5113 | 716.5113 | 305.9458 | 201.6707 | 212.008 | 212.2676 | 180.3265 | 194.1224
822.5127 | 717.5127 | 305.9382 | 201.7522 | 212.0677 | 212.3932 | 180.4028 | 194.1472
823.5142 | 718.5142 | 305.9938 | 201.8484 | 212.148 | 212.4923 | 180.4884 | 194.1734
824.5156 | 719.5156 | 306.139 | 201.9206 | 212.2265 | 212.5692 | 180.5772 | 194.2048
825.517 | 720.517 | 306.1576 | 202.0232 | 212.2956 | 212.6586 | 180.6677 | 194.2228
826.5185 | 721.5185 | 306.2371 | 202.1326 | 212.3668 | 212.6408 | 180.7704 | 194.2434
827.5199 | 722.5199 | 306.3157 | 202.2403 | 212.4331 | 212.721 | 180.8601 | 194.2436
828.5214 | 723.5214 | 306.4638 | 202.2681 | 212.5143 | 212.8103 | 180.9654 | 194.2496
829.5128 | 724.5128 | 306.6499 | 202.3382 | 212.5872 | 212.8351 | 181.0674 | 194.2617
830.5142 | 725.5142 | 306.7119 | 202.4162 | 212.6546 | 212.7961 | 181.1744 | 194.2846
831.5157 | 726.5157 | 306.7609 | 202.5099 | 212.7302 | 212.9199 | 181.2668 | 194.2966
832.5171 | 727.5171 | 306.7221 | 202.5817 | 212.8204 | 212.9201 | 181.3978 | 194.2968
833.5185 | 728.5185 | 306.5766 | 202.6824 | 212.8884 | 213.0442 | 181.5171 | 194.3016
834.52 | 729.52 | 306.4659 | 202.7872 | 212.978 | 213.1186 | 181.6444 | 194.3113
835.5214 | 730.5214 | 306.4224 | 202.8838 | 213.0568 | 213.1049 | 181.7569 | 194.3104
836.5128 | 731.5128 | 306.4826 | 202.9592 | 213.1513 | 213.06 | 181.89 | 194.3117
837.5143 | 732.5143 | 306.3837 | 203.0542 | 213.2281 | 213.0588 | 182.0131 | 194.3176
838.5157 | 733.5157 | 306.2359 | 203.1278 | 213.3236 | 213.1179 | 182.1409 | 194.3325
839.5172 | 734.5172 | 306.1314 | 203.2111 | 213.3947 | 213.2656 | 182.2798 | 194.3473
840.5186 | 735.5186 | 305.8866 | 203.2996 | 213.491 | 213.3286 | 182.4139 | 194.3674
841.52 | 736.52 | 305.7701 | 203.4049 | 213.5747 | 213.3429 | 182.5438 | 194.3869
842.5115 | 737.5115 | 305.7209 | 203.4946 | 213.6623 | 213.4802 | 182.6878 | 194.4142
843.5129 | 738.5129 | 305.5881 | 203.5166 | 213.7399 | 213.4955 | 182.818 | 194.4339
844.5144 | 739.5144 | 305.4939 | 203.5488 | 213.8434 | 213.6751 | 182.9541 | 194.4736
845.5158 | 740.5158 | 305.4278 | 203.6073 | 213.9288 | 213.6942 | 183.0725 | 194.5194
846.5172 | 741.5172 | 305.3431 | 203.6979 | 214.0196 | 213.7778 | 183.2177 | 194.5527
847.5187 | 742.5187 | 305.2639 | 203.8001 | 214.097 | 213.8743 | 183.3475 | 194.6013
848.5201 | 743.5201 | 305.2836 | 203.8834 | 214.1949 | 213.8402 | 183.4706 | 194.6559
849.5115 | 744.5115 | 305.327 | 203.9778 | 214.2829 | 213.8666 | 183.5938 | 194.696
850.513 | 745.513 | 305.4199 | 204.0562 | 214.3809 | 213.67 | 183.7046 | 194.7388
851.5144 | 746.5144 | 305.58 | 204.1605 | 214.4524 | 213.6086 | 183.8147 | 194.7826
852.5159 | 747.5159 | 305.7069 | 204.2429 | 214.5417 | 213.8984 | 183.9393 | 194.8298
853.5173 | 748.5173 | 305.7751 | 204.3493 | 214.6218 | 213.9043 | 184.0495 | 194.8846
854.5187 | 749.5187 | 305.7543 | 204.4523 | 214.7158 | 214.0175 | 184.1481 | 194.9467
855.5202 | 750.5202 | 305.7192 | 204.5221 | 214.7971 | 214.1707 | 184.2558 | 194.998
856.5216 | 751.5216 | 305.67 | 204.5265 | 214.8839 | 214.2701 | 184.3468 | 195.0518
857.513 | 752.513 | 305.6028 | 204.6174 | 214.9571 | 214.3164 | 184.4551 | 195.0992
858.5145 | 753.5145 | 305.6735 | 204.6805 | 215.0512 | 214.4536 | 184.5629 | 195.1457
859.5159 | 754.5159 | 305.7506 | 204.6822 | 215.1329 | 214.4728 | 184.6653 | 195.1872
860.5174 | 755.5174 | 305.7702 | 204.7794 | 215.2216 | 214.6029 | 184.7682 | 195.2285
861.5188 | 756.5188 | 305.7528 | 204.875 | 215.3013 | 214.7276 | 184.8743 | 195.2779
862.5202 | 757.5202 | 305.7663 | 204.9481 | 215.3833 | 214.8231 | 184.9852 | 195.3182
863.5117 | 758.5117 | 305.7252 | 205.0058 | 215.4765 | 214.3486 | 185.0968 | 195.3655
864.5131 | 759.5131 | 305.6399 | 205.1302 | 215.5672 | 214.2712 | 185.2019 | 195.4047
865.5145 | 760.5145 | 305.6453 | 205.2021 | 215.6465 | 214.428 | 185.3116 | 195.4536
866.516 | 761.516 | 305.5963 | 205.269 | 215.7203 | 214.6769 | 185.424 | 195.4845
867.5174 | 762.5174 | 305.6122 | 205.3621 | 215.8019 | 214.7896 | 185.5192 | 195.5263
868.5189 | 763.5189 | 305.6813 | 205.4289 | 215.8989 | 214.7799 | 185.6374 | 195.5707
869.5203 | 764.5203 | 305.6981 | 205.5237 | 215.9828 | 214.9504 | 185.7403 | 195.6258
870.5117 | 765.5117 | 305.6347 | 205.5707 | 216.0428 | 214.9707 | 185.839 | 195.6727
871.5132 | 766.5132 | 305.6692 | 205.5917 | 216.1359 | 215.0063 | 185.9583 | 195.7281
872.5146 | 767.5146 | 305.7539 | 205.7163 | 216.2147 | 215.0609 | 186.0486 | 195.7759
873.5161 | 768.5161 | 305.7576 | 205.7323 | 216.2805 | 215.0297 | 186.1417 | 195.8202
874.5175 | 769.5175 | 305.7217 | 205.8323 | 216.357 | 215.1633 | 186.2431 | 195.8694
875.5189 | 770.5189 | 305.6595 | 205.8269 | 216.4284 | 215.2903 | 186.3306 | 195.932
876.5204 | 771.5204 | 305.6736 | 205.9173 | 216.5002 | 215.4283 | 186.414 | 195.9922
877.5218 | 772.5218 | 305.6968 | 205.957 | 216.576 | 215.4817 | 186.5075 | 196.0659
878.5132 | 773.5132 | 305.761 | 206.0299 | 216.6513 | 215.5785 | 186.588 | 196.143
879.5147 | 774.5147 | 305.8303 | 206.0665 | 216.7163 | 215.5375 | 186.6716 | 196.2042
880.5161 | 775.5161 | 305.8404 | 206.0682 | 216.7926 | 215.6851 | 186.7452 | 196.2681 | Time of first failure
881.5176 | 776.5176 | 305.9047 | 206.1466 | 216.8402 | 215.7574 | 186.8242 | 196.3273 | 776 | 0
882.519 | 777.519 | 305.9354 | 206.2038 | 216.9206 | 215.9153 | 186.9188 | 196.4071 | 776 | 900
883.5204 | 778.5204 | 305.9764 | 206.159 | 216.9721 | 216.1356 | 186.9997 | 196.4822
884.5119 | 779.5119 | 306.1872 | 206.1908 | 217.0394 | 216.091 | 187.0896 | 196.5477
885.5133 | 780.5133 | 306.3185 | 206.2306 | 217.0946 | 216.1457 | 187.1798 | 196.6296
886.5147 | 781.5147 | 306.3023 | 206.233 | 217.1418 | 216.2279 | 187.2399 | 196.712
887.5162 | 782.5162 | 306.3338 | 206.1638 | 217.1919 | 216.3076 | 187.3172 | 196.7921
888.5176 | 783.5176 | 306.4432 | 206.1473 | 217.2382 | 216.4183 | 187.3861 | 196.8703
889.5191 | 784.5191 | 306.3996 | 206.1543 | 217.2819 | 216.5108 | 187.4666 | 196.9541
890.5205 | 785.5205 | 306.4127 | 206.1848 | 217.3292 | 216.5042 | 187.5397 | 197.0309
891.5119 | 786.5119 | 306.5081 | 206.1576 | 217.3854 | 216.5708 | 187.6105 | 197.11
892.5134 | 787.5134 | 306.5511 | 206.1879 | 217.4469 | 216.5596 | 187.6829 | 197.1884
893.5148 | 788.5148 | 306.6288 | 206.2708 | 217.505 | 216.7475 | 187.7576 | 197.2647
894.5163 | 789.5163 | 306.7021 | 206.3559 | 217.5657 | 216.7975 | 187.815 | 197.3375
895.5177 | 790.5177 | 306.6534 | 206.421 | 217.609 | 216.7878 | 187.8855 | 197.4183
896.5191 | 791.5191 | 306.7079 | 206.543 | 217.692 | 216.7698 | 187.955 | 197.4889
897.5206 | 792.5206 | 306.6843 | 206.5724 | 217.751 | 216.5495 | 188.0303 | 197.5668
898.522 | 793.522 | 306.6927 | 206.644 | 217.8019 | 216.4983 | 188.0996 | 197.638
899.5134 | 794.5134 | 306.6352 | 206.7606 | 217.8736 | 216.4157 | 188.1814 | 197.714
900.5149 | 795.5149 | 306.6296 | 206.8718 | 217.9292 | 216.3492 | 188.2762 | 197.7875
901.5163 | 796.5163 | 306.664 | 206.9713 | 217.9861 | 216.5651 | 188.3561 | 197.8461
902.5178 | 797.5178 | 306.708 | 207.0329 | 218.0284 | 216.4746 | 188.4501 | 197.9186
903.5192 | 798.5192 | 306.7082 | 207.0747 | 218.0798 | 216.569 | 188.5359 | 197.9836
904.5206 | 799.5206 | 306.7009 | 207.153 | 218.1391 | 216.5478 | 188.6294 | 198.0446
905.5121 | 800.5121 | 306.6837 | 207.1194 | 218.1721 | 216.6312 | 188.7365 | 198.1044
906.5135 | 801.5135 | 306.6254 | 207.1914 | 218.2164 | 216.7387 | 188.8254 | 198.173
907.5149 | 802.5149 | 306.657 | 207.2209 | 218.2612 | 216.7104 | 188.9199 | 198.2259
908.5164 | 803.5164 | 306.7512 | 207.2558 | 218.3241 | 216.7032 | 189.0103 | 198.2897
909.5178 | 804.5178 | 306.7829 | 207.4044 | 218.3624 | 216.6759 | 189.0999 | 198.3518
910.5193 | 805.5193 | 306.7626 | 207.4716 | 218.4218 | 216.5479 | 189.1777 | 198.4186
911.5107 | 806.5107 | 306.7177 | 207.5048 | 218.4663 | 216.3757 | 189.2618 | 198.4693
912.5121 | 807.5121 | 306.7138 | 207.619 | 218.5096 | 216.007 | 189.3364 | 198.5378
913.5136 | 808.5136 | 306.7431 | 207.7103 | 218.5601 | 216.1811 | 189.4157 | 198.5995
914.515 | 809.515 | 306.769 | 207.7333 | 218.6059 | 215.6485 | 189.4768 | 198.6631
915.5164 | 810.5164 | 306.747 | 207.7821 | 218.6512 | 215.8573 | 189.5538 | 198.727
916.5179 | 811.5179 | 306.758 | 207.8837 | 218.6913 | 215.8994 | 189.6368 | 198.7937
917.5193 | 812.5193 | 306.7006 | 208.0045 | 218.7203 | 215.9066 | 189.7284 | 198.8503
918.5208 | 813.5208 | 306.7526 | 208.0887 | 218.7471 | 215.9132 | 189.8088 | 198.9104
919.5222 | 814.5222 | 306.7866 | 208.1793 | 218.761 | 216.136 | 189.9094 | 198.9728
920.5136 | 815.5136 | 306.6842 | 208.2663 | 218.7908 | 216.2464 | 189.9777 | 199.017
921.5151 | 816.5151 | 306.597 | 208.306 | 218.8164 | 216.1439 | 190.0614 | 199.0629
922.5165 | 817.5165 | 306.5798 | 208.4112 | 218.8409 | 215.6494 | 190.161 | 199.0978
923.518 | 818.518 | 306.4847 | 208.5674 | 218.8573 | 215.9243 | 190.2445 | 199.1391
924.5194 | 819.5194 | 306.4679 | 208.6702 | 218.8765 | 215.9604 | 190.3304 | 199.1812
925.5208 | 820.5208 | 306.486 | 208.7701 | 218.9149 | 215.6792 | 190.4158 | 199.2374
926.5123 | 821.5123 | 306.4267 | 208.8619 | 218.9419 | 215.7364 | 190.5126 | 199.2743
927.5137 | 822.5137 | 306.4064 | 208.9259 | 218.9629 | 215.2558 | 190.603 | 199.3115
928.5151 | 823.5151 | 306.2894 | 209.017 | 218.9985 | 215.5255 | 190.6965 | 199.3582
929.5166 | 824.5166 | 306.2009 | 209.0707 | 219.0217 | 215.8506 | 190.8 | 199.4146
930.518 | 825.518 | 306.092 | 209.14 | 219.0438 | 216.0977 | 190.9103 | 199.4807
931.5195 | 826.5195 | 305.932 | 209.249 | 219.0664 | 216.3183 | 191.0008 | 199.5325
932.5209 | 827.5209 | 305.8449 | 209.3075 | 219.0972 | 216.0336 | 191.0909 | 199.5889
933.5123 | 828.5123 | 305.7449 | 209.4219 | 219.1427 | 216.1735 | 191.193 | 199.6473
934.5138 | 829.5138 | 305.7097 | 209.5131 | 219.1756 | 216.1548 | 191.2733 | 199.7117
935.5152 | 830.5152 | 305.7205 | 209.5604 | 219.2261 | 216.1245 | 191.3519 | 199.7691
936.5166 | 831.5166 | 305.6243 | 209.6745 | 219.2624 | 215.8572 | 191.4221 | 199.8293
937.5181 | 832.5181 | 305.5093 | 209.7919 | 219.3019 | 215.9115 | 191.5015 | 199.8804
938.5195 | 833.5195 | 305.4413 | 209.7691 | 219.3376 | 215.7285 | 191.5693 | 199.9398
939.511 | 834.511 | 305.4497 | 209.8638 | 219.3872 | 215.5764 | 191.6461 | 200.0025
940.5224 | 835.5224 | 305.521 | 209.9472 | 219.4301 | 215.7161 | 191.7176 | 200.0759
941.5138 | 836.5138 | 305.5233 | 210.0057 | 219.4692 | 215.8722 | 191.7894 | 200.1292
942.5353 | 837.5353 | 305.634 | 210.1045 | 219.5132 | 215.955 | 191.8761 | 200.1854
943.5167 | 838.5167 | 305.7759 | 210.2023 | 219.541 | 216.0118 | 191.9544 | 200.2414
944.5182 | 839.5182 | 305.7482 | 210.2611 | 219.5873 | 216.1258 | 192.036 | 200.2933
945.5196 | 840.5196 | 305.7645 | 210.3387 | 219.6329 | 216.1133 | 192.1226 | 200.3496
946.521 | 841.521 | 305.7438 | 210.4307 | 219.6743 | 216.0514 | 192.1884 | 200.3982
947.5125 | 842.5125 | 305.8592 | 210.4986 | 219.7015 | 215.9738 | 192.2794 | 200.4741
948.5139 | 843.5139 | 305.9587 | 210.5687 | 219.7473 | 216.0175 | 192.3811 | 200.5287
949.5153 | 844.5153 | 306.0007 | 210.6075 | 219.7864 | 216.0856 | 192.4705 | 200.5885
950.5168 | 845.5168 | 305.9682 | 210.5618 | 219.8256 | 216.3278 | 192.5578 | 200.6543
951.5182 | 846.5182 | 305.9783 | 210.6629 | 219.8764 | 216.3587 | 192.6435 | 200.7127
952.5197 | 847.5197 | 305.9884 | 210.8113 | 219.9169 | 216.7091 | 192.7339 | 200.7763
953.5111 | 848.5111 | 305.9825 | 210.8156 | 219.967 | 216.7381 | 192.8229 | 200.8371
954.5125 | 849.5125 | 306.0647 | 210.8356 | 220.0204 | 216.9833 | 192.9045 | 200.8993
955.514 | 850.514 | 306.1921 | 210.8774 | 220.0691 | 217.1424 | 192.9828 | 200.9728
956.5154 | 851.5154 | 306.3114 | 210.8813 | 220.128 | 217.0318 | 193.0544 | 201.0456
957.5168 | 852.5168 | 306.392 | 210.9038 | 220.1936 | 217.3094 | 193.1347 | 201.1121
958.5183 | 853.5183 | 306.395 | 210.8927 | 220.2633 | 217.6558 | 193.2021 | 201.1659
959.5197 | 854.5197 | 306.3593 | 210.9686 | 220.3252 | 218.0126 | 193.2723 | 201.2427
960.5212 | 855.5212 | 306.3683 | 211.0147 | 220.3923 | 218.2227 | 193.3412 | 201.317
961.5226 | 856.5226 | 306.3101 | 211.0773 | 220.4534 | 218.422 | 193.3954 | 201.3948
962.514 | 857.514 | 306.3302 | 211.1043 | 220.5259 | 218.6273 | 193.4439 | 201.464
963.5155 | 858.5155 | 306.2908 | 211.2056 | 220.6006 | 218.5325 | 193.5079 | 201.5477
964.5169 | 859.5169 | 306.281 | 211.2641 | 220.6617 | 218.5415 | 193.5453 | 201.6286
965.5183 | 860.5183 | 306.3532 | 211.3206 | 220.7333 | 218.6746 | 193.6082 | 201.7053
966.5198 | 861.5198 | 306.3934 | 211.396 | 220.814 | 218.8062 | 193.6619 | 201.7838
967.5212 | 862.5212 | 306.4412 | 211.4528 | 220.8844 | 218.8011 | 193.7126 | 201.8593
968.5127 | 863.5127 | 306.5316 | 211.5742 | 220.9476 | 218.8482 | 193.774 | 201.9375
969.5141 | 864.5141 | 306.6043 | 211.6245 | 221.0158 | 218.9114 | 193.8306 | 201.9869
970.5155 | 865.5155 | 306.6957 | 211.6842 | 221.0773 | 218.7488 | 193.9042 | 202.0547
971.517 | 866.517 | 306.8042 | 211.7933 | 221.1218 | 218.9218 | 193.9738 | 202.1301
972.5184 | 867.5184 | 306.8601 | 211.8428 | 221.1912 | 218.5555 | 194.0507 | 202.1939
973.5199 | 868.5199 | 306.8293 | 211.9013 | 221.2379 | 218.7013 | 194.1237 | 202.2515
974.5113 | 869.5113 | 306.8359 | 211.9999 | 221.2803 | 218.7943 | 194.214 | 202.3091
975.5127 | 870.5127 | 306.9231 | 212.0723 | 221.3259 | 218.7827 | 194.3169 | 202.36
976.5142 | 871.5142 | 306.9696 | 212.0918 | 221.362 | 218.9036 | 194.4193 | 202.4046
977.5156 | 872.5156 | 306.9988 | 212.1878 | 221.4037 | 218.6896 | 194.5194 | 202.4669
978.517 | 873.517 | 306.9617 | 212.2286 | 221.4353 | 218.7476 | 194.6278 | 202.5173
979.5185 | 874.5185 | 306.8888 | 212.3241 | 221.487 | 218.7799 | 194.7229 | 202.5716
980.5199 | 875.5199 | 306.8043 | 212.3485 | 221.535 | 218.8624 | 194.8514 | 202.6218
981.5214 | 876.5214 | 306.7381 | 212.3244 | 221.5684 | 218.661 | 194.9592 | 202.6718
982.5128 | 877.5128 | 306.7524 | 212.4316 | 221.6227 | 218.8152 | 195.0837 | 202.7289
983.5142 | 878.5142 | 306.5845 | 212.5162 | 221.6732 | 218.36 | 195.1867 | 202.782
984.5157 | 879.5157 | 306.4648 | 212.5545 | 221.7255 | 218.539 | 195.2907 | 202.8432
985.5171 | 880.5171 | 306.3516 | 212.3817 | 221.79 | 218.5652 | 195.4037 | 202.8943
986.5185 | 881.5185 | 306.2879 | 212.5115 | 221.8347 | 218.4954 | 195.5 | 202.9513
987.52 | 882.52 | 306.3636 | 212.6116 | 221.8892 | 218.4276 | 195.5932 | 202.9946
988.5214 | 883.5214 | 306.3319 | 212.6788 | 221.943 | 218.5736 | 195.6876 | 203.0414
989.5128 | 884.5128 | 306.3318 | 212.6915 | 221.9856 | 218.6234 | 195.7891 | 203.1052
990.5143 | 885.5143 | 306.3705 | 212.7535 | 222.0246 | 218.6591 | 195.8541 | 203.1504
991.5157 | 886.5157 | 306.3517 | 212.8452 | 222.0967 | 218.1102 | 195.9433 | 203.1901
992.5172 | 887.5172 | 306.3209 | 212.8943 | 222.1462 | 218.3586 | 196.021 | 203.2332
993.5186 | 888.5186 | 306.1958 | 212.9208 | 222.187 | 218.4083 | 196.1117 | 203.2859
994.52 | 889.52 | 306.1506 | 212.9178 | 222.2542 | 218.4981 | 196.201 | 203.3344
995.5115 | 890.5115 | 306.0784 | 212.9541 | 222.3005 | 218.2715 | 196.2995 | 203.3939
996.5129 | 891.5129 | 306.0234 | 213.0045 | 222.3529 | 218.0388 | 196.3798 | 203.438
997.5144 | 892.5144 | 306.0123 | 213.0041 | 222.4062 | 218.2361 | 196.4891 | 203.4783
998.5158 | 893.5158 | 305.8735 | 213.0695 | 222.4658 | 218.321 | 196.5679 | 203.5284
999.5172 | 894.5172 | 305.8058 | 213.0909 | 222.5123 | 218.4502 | 196.6516 | 203.5805
1000.5187 | 895.5187 | 305.7382 | 213.0975 | 222.5656 | 218.6354 | 196.7372 | 203.6146
1001.5201 | 896.5201 | 305.7094 | 212.8947 | 222.6159 | 218.699 | 196.8257 | 203.6667
1002.5216 | 897.5216 | 305.6198 | 212.9689 | 222.6812 | 218.7943 | 196.9152 | 203.7202
1003.513 | 898.513 | 305.6076 | 213.0006 | 222.709 | 218.4638 | 196.983 | 203.7736
1004.5144 | 899.5144 | 305.568 | 212.9436 | 222.7679 | 218.6097 | 197.0751 | 203.8183
1005.5159 | 900.5159 | 305.5841 | 212.8718 | 222.8079 | 218.513 | 197.1669 | 203.8764
1006.5173 | 901.5173 | 305.6658 | 213.0018 | 222.8627 | 218.7561 | 197.2385 | 203.9335
1007.5187 | 902.5187 | 305.6245 | 213.0427 | 222.9096 | 218.7162 | 197.3121 | 203.9888
1008.5202 | 903.5202 | 305.6255 | 213.1714 | 222.9582 | 218.3358 | 197.3797 | 204.0394
1009.5216 | 904.5216 | 305.6849 | 213.2756 | 223.0285 | 218.5396 | 197.4496 | 204.0954
1010.5231 | 905.5231 | 305.761 | 213.302 | 223.0823 | 218.6128 | 197.5176 | 204.1414
1011.5145 | 906.5145 | 305.7924 | 213.2409 | 223.1528 | 218.7684 | 197.5723 | 204.1901
1012.5159 | 907.5159 | 305.8042 | 213.3855 | 223.2266 | 218.8546 | 197.6332 | 204.2528
1013.5174 | 908.5174 | 305.8247 | 213.2527 | 223.2987 | 218.6435 | 197.7143 | 204.3095
1014.5188 | 909.5188 | 305.8615 | 213.3413 | 223.3513 | 218.5354 | 197.792 | 204.3554
1015.5202 | 910.5202 | 305.8529 | 213.4127 | 223.4192 | 218.1121 | 197.8612 | 204.4037
1016.5117 | 911.5117 | 305.8281 | 213.4884 | 223.4871 | 218.3167 | 197.9555 | 204.4595
1017.5131 | 912.5131 | 305.795 | 213.4883 | 223.5416 | 218.301 | 198.0387 | 204.5062
1018.5146 | 913.5146 | 305.6606 | 213.5906 | 223.5999 | 218.3033 | 198.1384 | 204.5555
1019.516 | 914.516 | 305.6918 | 213.5883 | 223.6642 | 218.539 | 198.2241 | 204.6114
1020.5174 | 915.5174 | 305.7451 | 213.5916 | 223.7043 | 218.1887 | 198.3229 | 204.6585
1021.5189 | 916.5189 | 305.7807 | 213.5865 | 223.7504 | 218.4454 | 198.4079 | 204.7082
1022.5203 | 917.5203 | 305.6869 | 213.5822 | 223.7852 | 218.4664 | 198.4894 | 204.7549
1023.5117 | 918.5117 | 305.6777 | 213.6484 | 223.8247 | 218.7277 | 198.573 | 204.8195
1024.5132 | 919.5132 | 305.7621 | 213.6405 | 223.8573 | 219.0214 | 198.6504 | 204.8671
1025.5146 | 920.5146 | 305.8228 | 213.5074 | 223.9119 | 219.0587 | 198.7277 | 204.9136
1026.5161 | 921.5161 | 305.8272 | 213.5308 | 223.9552 | 219.2818 | 198.7918 | 204.9595
1027.5175 | 922.5175 | 305.8483 | 213.2947 | 224.0075 | 219.3183 | 198.8726 | 205.0064
1028.5189 | 923.5189 | 305.9195 | 213.1663 | 224.0632 | 219.4666 | 198.9431 | 205.0466
1029.5204 | 924.5204 | 305.9077 | 213.2282 | 224.1316 | 219.6085 | 198.9983 | 205.0884
1030.5218 | 925.5218 | 305.8265 | 213.1724 | 224.1961 | 219.4702 | 199.0542 | 205.1316
1031.5132 | 926.5132 | 305.812 | 213.2551 | 224.2619 | 219.7623 | 199.1158 | 205.177
1032.5147 | 927.5147 | 305.7609 | 213.2455 | 224.3382 | 219.908 | 199.1823 | 205.2289
1033.5161 | 928.5161 | 305.6776 | 213.2087 | 224.4138 | 219.9821 | 199.2227 | 205.2761
1034.5176 | 929.5176 | 305.726 | 213.2047 | 224.4861 | 220.1717 | 199.2732 | 205.3276
1035.519 | 930.519 | 305.7478 | 213.2568 | 224.5665 | 220.2843 | 199.3098 | 205.3798
1036.5204 | 931.5204 | 305.7499 | 213.3086 | 224.6471 | 220.3223 | 199.3615 | 205.4372
1037.5119 | 932.5119 | 305.669 | 213.2022 | 224.7135 | 220.1621 | 199.4024 | 205.4826
1038.5133 | 933.5133 | 305.6408 | 213.3916 | 224.7941 | 219.769 | 199.4474 | 205.5297
1039.5147 | 934.5147 | 305.6349 | 213.4506 | 224.8671 | 219.798 | 199.4853 | 205.5873
1040.5162 | 935.5162 | 305.5826 | 213.462 | 224.9422 | 220.0729 | 199.533 | 205.6271
1041.5176 | 936.5176 | 305.5496 | 213.5629 | 225.0029 | 219.9592 | 199.5734 | 205.6879
1042.5191 | 937.5191 | 305.5633 | 213.6605 | 225.0849 | 219.7914 | 199.6229 | 205.7298
1043.5205 | 938.5205 | 305.6414 | 213.6589 | 225.1484 | 219.6534 | 199.6675 | 205.7822
1044.5219 | 939.5219 | 305.8397 | 213.6106 | 225.2164 | 219.93 | 199.7154 | 205.8363
1045.5134 | 940.5134 | 305.9288 | 213.6884 | 225.2804 | 219.813 | 199.7765 | 205.892
1046.5148 | 941.5148 | 305.9526 | 213.7643 | 225.3219 | 219.7006 | 199.8438 | 205.9455
1047.5163 | 942.5163 | 305.9785 | 213.8439 | 225.3673 | 219.7558 | 199.9081 | 205.9942
1048.5177 | 943.5177 | 306.0132 | 213.9168 | 225.4156 | 220.0149 | 199.9765 | 206.0449
1049.5191 | 944.5191 | 306.1006 | 214.0167 | 225.4498 | 220.0496 | 200.0278 | 206.0933
1050.5206 | 945.5206 | 306.1451 | 214.0921 | 225.4911 | 220.1338 | 200.1011 | 206.1575
1051.522 | 946.522 | 306.141 | 214.1363 | 225.5389 | 220.3763 | 200.1709 | 206.2058
1052.5134 | 947.5134 | 306.1218 | 214.184 | 225.5806 | 220.3986 | 200.2429 | 206.2529
1053.5149 | 948.5149 | 306.1353 | 214.2069 | 225.6093 | 220.2882 | 200.3144 | 206.2922
1054.5163 | 949.5163 | 306.1394 | 214.2903 | 225.6496 | 220.1712 | 200.3896 | 206.3411
1055.5178 | 950.5178 | 306.2244 | 214.4124 | 225.6903 | 219.9946 | 200.4656 | 206.3796
1056.5192 | 951.5192 | 306.3304 | 214.445 | 225.7315 | 219.9002 | 200.5474 | 206.4394
1057.5206 | 952.5206 | 306.3697 | 214.5533 | 225.7637 | 219.9919 | 200.62 | 206.4827
1058.5121 | 953.5121 | 306.4668 | 214.5587 | 225.8043 | 220.0028 | 200.6884 | 206.5384
1059.5135 | 954.5135 | 306.521 | 214.6397 | 225.8419 | 220.0478 | 200.7712 | 206.5878
1060.5149 | 955.5149 | 306.5606 | 214.7228 | 225.8852 | 219.812 | 200.8453 | 206.6367
1061.5164 | 956.5164 | 306.5223 | 214.8211 | 225.9272 | 220.0493 | 200.9284 | 206.6876
1062.5178 | 957.5178 | 306.506 | 214.9038 | 225.9616 | 220.4587 | 200.9899 | 206.7417
1063.5193 | 958.5193 | 306.5045 | 214.988 | 225.992 | 220.6921 | 201.0761 | 206.8066
1064.5107 | 959.5107 | 306.4834 | 214.9709 | 226.0477 | 220.8392 | 201.1375 | 206.8382
1065.5221 | 960.5221 | 306.4823 | 215.0151 | 226.0866 | 221.0238 | 201.2113 | 206.8781
1066.5136 | 961.5136 | 306.5195 | 215.018 | 226.1447 | 220.8559 | 201.2716 | 206.9191
1067.515 | 962.515 | 306.4539 | 215.0509 | 226.2044 | 221.0614 | 201.3499 | 206.9741
1068.5165 | 963.5165 | 306.4073 | 214.9452 | 226.2689 | 220.9175 | 201.3997 | 207.0163
1069.5179 | 964.5179 | 306.3377 | 214.8506 | 226.32 | 220.9366 | 201.4574 | 207.0685
1070.5193 | 965.5193 | 306.3625 | 214.971 | 226.3952 | 221.0355 | 201.5231 | 207.1162
1071.5208 | 966.5208 | 306.3969 | 214.8681 | 226.4573 | 221.0851 | 201.5896 | 207.1677
1072.5222 | 967.5222 | 306.4052 | 214.894 | 226.5172 | 221.2443 | 201.648 | 207.2282
1073.5136 | 968.5136 | 306.4767 | 214.9934 | 226.583 | 221.3602 | 201.6949 | 207.2745
1074.5151 | 969.5151 | 306.5202 | 214.9177 | 226.6505 | 221.0922 | 201.7528 | 207.3253
1075.5165 | 970.5165 | 306.5215 | 214.8189 | 226.7287 | 221.2773 | 201.8063 | 207.3837
1076.518 | 971.518 | 306.5636 | 214.7234 | 226.7882 | 221.4356 | 201.8647 | 207.4258
1077.5194 | 972.5194 | 306.5695 | 214.7632 | 226.8452 | 221.6711 | 201.9416 | 207.4905
1078.5208 | 973.5208 | 306.545 | 214.8909 | 226.9115 | 221.8025 | 201.9767 | 207.5401
1079.5123 | 974.5123 | 306.451 | 214.9724 | 226.9835 | 221.906 | 202.053 | 207.5853
1080.5137 | 975.5137 | 306.4377 | 214.9651 | 227.0433 | 221.7431 | 202.1157 | 207.648
1081.5151 | 976.5151 | 306.5092 | 214.8345 | 227.0954 | 222.0192 | 202.1644 | 207.6821
1082.5166 | 977.5166 | 306.5228 | 214.8268 | 227.1648 | 222.241 | 202.2156 | 207.7338
1083.518 | 978.518 | 306.512 | 214.8646 | 227.2143 | 222.0714 | 202.2769 | 207.7714
1084.5195 | 979.5195 | 306.4907 | 214.7357 | 227.2909 | 221.9226 | 202.3354 | 207.8194
1085.5109 | 980.5109 | 306.57 | 214.6674 | 227.3466 | 222.2472 | 202.3873 | 207.8633
1086.5223 | 981.5223 | 306.6143 | 214.7106 | 227.4023 | 222.3454 | 202.4297 | 207.8952
1087.5138 | 982.5138 | 306.6333 | 214.7955 | 227.4609 | 222.3807 | 202.4902 | 207.9457
1088.5152 | 983.5152 | 306.539 | 214.8678 | 227.5155 | 222.219 | 202.5389 | 207.9831
1089.5166 | 984.5166 | 306.4922 | 214.9039 | 227.5718 | 222.2664 | 202.5796 | 208.0414
1090.5181 | 985.5181 | 306.443 | 214.9961 | 227.6201 | 222.3222 | 202.6423 | 208.0822
1091.5195 | 986.5195 | 306.4262 | 214.9447 | 227.6707 | 222.2915 | 202.6794 | 208.1364
1092.521 | 987.521 | 306.4845 | 214.6652 | 227.8115 | 222.3958 | 203.944 | 208.9069
1093.5224 | 988.5224 | 306.4244 | 215.1108 | 227.7626 | 222.2426 | 202.7781 | 208.2138
1094.5138 | 989.5138 | 306.4243 | 215.1664 | 227.8139 | 222.3755 | 202.8353 | 208.2459
1095.5153 | 990.5153 | 306.4406 | 215.1572 | 227.8749 | 222.0397 | 202.8892 | 208.295
1096.5167 | 991.5167 | 306.4399 | 215.2399 | 227.9167 | 222.4649 | 202.9447 | 208.3395
1097.5182 | 992.5182 | 306.3927 | 215.2761 | 227.9658 | 222.779 | 203.0051 | 208.385
1098.5196 | 993.5196 | 306.342 | 215.3941 | 228.0171 | 222.4505 | 203.058 | 208.4405
1099.521 | 994.521 | 306.3378 | 215.28 | 228.0615 | 222.8401 | 203.1132 | 208.4835
1100.5125 | 995.5125 | 306.3419 | 215.1509 | 228.0998 | 222.7363 | 203.1714 | 208.5405
1101.5139 | 996.5139 | 306.3495 | 215.2572 | 228.1638 | 222.4303 | 203.2269 | 208.5911
1102.5153 | 997.5153 | 306.3597 | 215.3184 | 228.2068 | 222.6313 | 203.2835 | 208.6308
1103.5168 | 998.5168 | 306.2981 | 215.3678 | 228.2675 | 222.4707 | 203.3408 | 208.6678
1104.5182 | 999.5182 | 306.2946 | 215.5135 | 228.3114 | 222.475 | 203.4016 | 208.7105
1105.5197 | 1000.5197 | 306.428 | 215.5743 | 228.3613 | 222.7206 | 203.4559 | 208.7519
1106.5111 | 1001.5111 | 306.5044 | 215.6632 | 228.3942 | 222.9246 | 203.5256 | 208.7888
1107.5125 | 1002.5125 | 306.5264 | 215.7971 | 228.4374 | 222.8372 | 203.605 | 208.8051
1108.514 | 1003.514 | 306.523 | 215.832 | 228.4914 | 222.7689 | 203.6858 | 208.8446
1109.5154 | 1004.5154 | 306.6578 | 215.8277 | 228.5179 | 222.9056 | 203.7588 | 208.8894
1110.5168 | 1005.5168 | 306.6549 | 215.8164 | 228.5404 | 223.0256 | 203.851 | 208.9349
1111.5183 | 1006.5183 | 306.5743 | 215.8122 | 228.573 | 223.2882 | 203.945 | 208.9819
1112.5197 | 1007.5197 | 306.4725 | 215.8128 | 228.5972 | 223.537 | 204.034 | 209.0099
1113.5212 | 1008.5212 | 306.3713 | 215.9276 | 228.6266 | 223.6686 | 204.1331 | 209.0539
1114.5226 | 1009.5226 | 306.3298 | 215.8853 | 228.6507 | 223.8144 | 204.2296 | 209.1044
1115.514 | 1010.514 | 306.3181 | 215.9732 | 228.6778 | 223.8804 | 204.3147 | 209.1513
1116.5155 | 1011.5155 | 306.3266 | 216.0852 | 228.7152 | 223.9918 | 204.4174 | 209.1873
1117.5169 | 1012.5169 | 306.3156 | 215.987 | 228.7398 | 223.8144 | 204.5001 | 209.2261
1118.5284 | 1013.5284 | 306.3338 | 216.1598 | 228.7664 | 224.0696 | 204.6012 | 209.2769
1119.5198 | 1014.5198 | 306.3862 | 216.1607 | 228.7968 | 224.3198 | 204.6847 | 209.3151
1120.5112 | 1015.5112 | 306.3798 | 216.2858 | 228.8258 | 224.2121 | 204.7649 | 209.369
1121.5127 | 1016.5127 | 306.5352 | 216.3558 | 228.8591 | 224.0468 | 204.822 | 209.408
1122.5141 | 1017.5141 | 306.7546 | 216.4027 | 228.8805 | 224.0922 | 204.8852 | 209.4497
1123.5155 | 1018.5155 | 306.938 | 216.499 | 228.923 | 223.9335 | 204.9344 | 209.4682
1124.517 | 1019.517 | 307.075 | 216.5804 | 228.9612 | 224.0521 | 205.0031 | 209.5021
1125.5184 | 1020.5184 | 307.2172 | 216.6653 | 228.9869 | 223.4971 | 205.0657 | 209.5477
1126.5199 | 1021.5199 | 307.3042 | 216.6816 | 229.0048 | 222.8137 | 205.1436 | 209.5957
1127.5113 | 1022.5113 | 307.3671 | 216.7628 | 229.0353 | 222.6424 | 205.2028 | 209.6361
1128.5127 | 1023.5127 | 307.3583 | 216.8167 | 229.0426 | 222.8907 | 205.269 | 209.673
1129.5142 | 1024.5142 | 307.3095 | 216.884 | 229.0661 | 223.2512 | 205.3484 | 209.7145
1130.5156 | 1025.5156 | 307.1771 | 217.0172 | 229.0741 | 223.231 | 205.4241 | 209.758
1131.517 | 1026.517 | 307.1934 | 217.0736 | 229.1098 | 223.1795 | 205.5036 | 209.8017
1132.5185 | 1027.5185 | 307.2277 | 217.1736 | 229.1239 | 223.4215 | 205.6093 | 209.8283
1133.5199 | 1028.5199 | 307.3483 | 217.2048 | 229.151 | 223.4173 | 205.6845 | 209.8741
1134.5214 | 1029.5214 | 307.4372 | 217.3172 | 229.1691 | 223.1175 | 205.7767 | 209.8916
1135.5228 | 1030.5228 | 307.5219 | 217.365 | 229.1907 | 222.9136 | 205.8709 | 209.9292
1136.5142 | 1031.5142 | 307.5114 | 217.4677 | 229.2111 | 223.2514 | 205.9514 | 209.9705
1137.5157 | 1032.5157 | 307.485 | 217.5076 | 229.2288 | 222.9502 | 206.0491 | 209.9957
1138.5171 | 1033.5171 | 307.4461 | 217.4908 | 229.251 | 222.9029 | 206.1504 | 210.0351
1139.5185 | 1034.5185 | 307.4917 | 217.5072 | 229.2618 | 223.0649 | 206.2457 | 210.0563
1140.52 | 1035.52 | 307.5169 | 217.5189 | 229.2728 | 223.3329 | 206.3503 | 210.0842
1141.5214 | 1036.5214 | 307.5145 | 217.6079 | 229.296 | 223.3582 | 206.4315 | 210.137
1142.5129 | 1037.5129 | 307.4411 | 217.6826 | 229.3207 | 223.3092 | 206.5266 | 210.1638
1143.5143 | 1038.5143 | 307.3698 | 217.7569 | 229.3308 | 223.0287 | 206.6223 | 210.1954
1144.5157 | 1039.5157 | 307.4056 | 217.734 | 229.3447 | 223.1877 | 206.7006 | 210.2321
1145.5172 | 1040.5172 | 307.3095 | 217.8388 | 229.3576 | 223.3607 | 206.7826 | 210.2654
1146.5186 | 1041.5186 | 307.1681 | 217.8332 | 229.3884 | 223.5215 | 206.8596 | 210.2864
1147.5201 | 1042.5201 | 306.9854 | 217.7741 | 229.3948 | 223.7766 | 206.9286 | 210.3316
1148.5115 | 1043.5115 | 306.8396 | 217.8995 | 229.4199 | 223.9228 | 207.0001 | 210.3618
1149.5129 | 1044.5129 | 306.6871 | 217.8536 | 229.4386 | 224.0563 | 207.0737 | 210.3915
1150.5144 | 1045.5144 | 306.5182 | 217.8383 | 229.4571 | 224.2353 | 207.1442 | 210.4194
1151.5158 | 1046.5158 | 306.4704 | 217.7985 | 229.4842 | 224.4708 | 207.1982 | 210.4674
1152.5172 | 1047.5172 | 306.4196 | 217.8692 | 229.513 | 224.5111 | 207.2703 | 210.4997
1153.5187 | 1048.5187 | 306.2557 | 218.0092 | 229.555 | 223.9293 | 207.317 | 210.5403
1154.5201 | 1049.5201 | 306.1619 | 218.0472 | 229.5718 | 224.0137 | 207.3678 | 210.5641
1155.5216 | 1050.5216 | 306.1493 | 218.118 | 229.6026 | 223.8698 | 207.4221 | 210.5994
1156.513 | 1051.513 | 305.9637 | 218.1164 | 229.6216 | 223.9685 | 207.4853 | 210.6208
1157.5144 | 1052.5144 | 305.6959 | 218.211 | 229.6416 | 224.1275 | 207.5242 | 210.6469
1158.5159 | 1053.5159 | 305.4299 | 218.2152 | 229.6654 | 224.0651 | 207.5894 | 210.6678
1159.5173 | 1054.5173 | 305.1247 | 218.2584 | 229.6741 | 224.0724 | 207.6398 | 210.6647
1160.5187 | 1055.5187 | 304.8262 | 218.2907 | 229.6751 | 224.3168 | 207.6954 | 210.6778
1161.5202 | 1056.5202 | 304.5761 | 218.3538 | 229.6883 | 223.8941 | 207.7614 | 210.6877
1162.5216 | 1057.5216 | 304.2289 | 218.4114 | 229.6815 | 224.1421 | 207.8244 | 210.6942
1163.513 | 1058.513 | 303.8077 | 218.4242 | 229.6707 | 224.3756 | 207.8492 | 210.7121
1164.5145 | 1059.5145 | 303.4076 | 218.4986 | 229.6641 | 224.3766 | 207.8931 | 210.7152
1165.5159 | 1060.5159 | 303.0353 | 218.5009 | 229.6508 | 223.817 | 207.9345 | 210.725
1166.5174 | 1061.5174 | 302.7212 | 218.5738 | 229.6392 | 224.1806 | 207.9794 | 210.7164
1167.5188 | 1062.5188 | 302.3976 | 218.5084 | 229.6188 | 224.2229 | 208.0167 | 210.6965
1168.5202 | 1063.5202 | 301.9496 | 218.5116 | 229.6038 | 224.4304 | 208.0502 | 210.6948
1169.5117 | 1064.5117 | 301.5752 | 218.3674 | 229.5698 | 224.4848 | 208.0786 | 210.6782
1170.5131 | 1065.5131 | 301.2297 | 218.4664 | 229.5715 | 224.6014 | 208.1067 | 210.6768
1171.5146 | 1066.5146 | 300.8172 | 218.5094 | 229.5495 | 224.6396 | 208.1456 | 210.6557
1172.516 | 1067.516 | 300.4207 | 218.5903 | 229.5222 | 224.6284 | 208.1724 | 210.6242
1173.5174 | 1068.5174 | 300.0911 | 218.548 | 229.4986 | 224.2236 | 208.1986 | 210.6113
1174.5189 | 1069.5189 | 299.7672 | 218.5709 | 229.4842 | 224.2798 | 208.212 | 210.599
1175.5203 | 1070.5203 | 299.5812 | 218.5899 | 229.4669 | 224.3076 | 208.2455 | 210.575
1176.5218 | 1071.5218 | 299.3297 | 218.657 | 229.4392 | 224.3613 | 208.2702 | 210.558
1177.5132 | 1072.5132 | 299.0152 | 218.6815 | 229.4326 | 224.403 | 208.2945 | 210.5338
1178.5146 | 1073.5146 | 298.726 | 218.7164 | 229.4173 | 224.4173 | 208.3205 | 210.5148
1179.5161 | 1074.5161 | 298.2623 | 218.7716 | 229.4018 | 224.284 | 208.3423 | 210.4945
1180.5175 | 1075.5175 | 297.7917 | 218.8144 | 229.3853 | 223.8349 | 208.3717 | 210.4653
1181.5189 | 1076.5189 | 297.3763 | 218.8409 | 229.3563 | 223.7496 | 208.4099 | 210.4376
1182.5204 | 1077.5204 | 297.0458 | 218.8726 | 229.3267 | 223.7133 | 208.4551 | 210.3935
1183.5218 | 1078.5218 | 296.7655 | 218.9036 | 229.3043 | 223.7198 | 208.5071 | 210.361
1184.5132 | 1079.5132 | 296.3752 | 218.9583 | 229.2798 | 223.7372 | 208.5702 | 210.3282
1185.5147 | 1080.5147 | 296.007 | 218.9716 | 229.2488 | 223.1657 | 208.6329 | 210.29
1186.5161 | 1081.5161 | 295.6004 | 218.9378 | 229.214 | 223.1926 | 208.7099 | 210.2528
1187.5176 | 1082.5176 | 295.2794 | 218.9738 | 229.1845 | 223.5351 | 208.7769 | 210.2065
1188.519 | 1083.519 | 294.8964 | 218.9516 | 229.1618 | 223.5976 | 208.839 | 210.1727
1189.5204 | 1084.5204 | 294.4253 | 218.9545 | 229.1158 | 223.5635 | 208.9016 | 210.1298
1190.5119 | 1085.5119 | 294.0321 | 218.9189 | 229.0965 | 223.551 | 208.9652 | 210.0951
1191.5133 | 1086.5133 | 293.6402 | 218.9154 | 229.0712 | 223.5702 | 209.0313 | 210.0544
1192.5148 | 1087.5148 | 293.2044 | 218.928 | 229.0261 | 223.1608 | 209.0798 | 210.0243
1193.5162 | 1088.5162 | 292.7259 | 218.934 | 228.9956 | 223.1765 | 209.12 | 209.9958
1194.5176 | 1089.5176 | 292.2162 | 218.9165 | 228.9509 | 223.2308 | 209.1472 | 209.9563
1195.5191 | 1090.5191 | 291.7871 | 218.9439 | 228.9127 | 223.128 | 209.1647 | 209.9272
1196.5105 | 1091.5105 | 291.3897 | 218.9584 | 228.8652 | 222.8551 | 209.173 | 209.8867
1197.522 | 1092.522 | 290.9561 | 218.9526 | 228.8123 | 222.9207 | 209.1718 | 209.8479
1198.5134 | 1093.5134 | 290.6119 | 218.9131 | 228.7558 | 222.9867 | 209.1835 | 209.8006
1199.5148 | 1094.5148 | 290.1842 | 218.8448 | 228.7126 | 222.928 | 209.185 | 209.7659
1200.5163 | 1095.5163 | 289.7639 | 218.8029 | 228.6569 | 222.8487 | 209.1825 | 209.718
1201.5177 | 1096.5177 | 289.3743 | 218.7969 | 228.6159 | 222.8062 | 209.1827 | 209.6896
1202.5191 | 1097.5191 | 289.0479 | 218.8181 | 228.5712 | 222.7102 | 209.1639 | 209.6403
1203.5206 | 1098.5206 | 288.6777 | 218.8055 | 228.5257 | 222.38 | 209.1506 | 209.5977
1204.512 | 1099.512 | 288.3648 | 218.7968 | 228.4748 | 222.4527 | 209.1193 | 209.55
1205.5134 | 1100.5134 | 288.0386 | 218.7745 | 228.4442 | 222.301 | 209.0915 | 209.5037
1206.5149 | 1101.5149 | 287.5951 | 218.6574 | 228.3975 | 222.2985 | 209.0697 | 209.4643
1207.5163 | 1102.5163 | 287.1239 | 218.6315 | 228.3537 | 221.7745 | 209.0257 | 209.4241
1208.5178 | 1103.5178 | 286.7322 | 218.5001 | 228.2948 | 221.6128 | 208.9848 | 209.3839
1209.5192 | 1104.5192 | 286.3084 | 218.5064 | 228.249 | 221.7633 | 208.9157 | 209.344
1210.5206 | 1105.5206 | 285.9168 | 218.4734 | 228.1972 | 221.5138 | 208.8747 | 209.2881
1211.5121 | 1106.5121 | 285.4679 | 218.4169 | 228.1477 | 221.5507 | 208.8083 | 209.2564
1212.5135 | 1107.5135 | 285.0154 | 218.3217 | 228.0829 | 221.5389 | 208.7348 | 209.2095
1213.5149 | 1108.5149 | 284.6465 | 218.2847 | 228.0328 | 221.464 | 208.6596 | 209.1661
1214.5164 | 1109.5164 | 284.2146 | 218.0376 | 227.9883 | 221.376 | 208.5911 | 209.1154
1215.5178 | 1110.5178 | 283.8303 | 217.9709 | 227.9268 | 221.4104 | 208.4878 | 209.0802
1216.5193 | 1111.5193 | 283.4414 | 217.9994 | 227.8728 | 221.269 | 208.3874 | 209.0369
1217.5107 | 1112.5107 | 283.0347 | 218.0059 | 227.8146 | 221.3495 | 208.2803 | 208.9872
1218.5221 | 1113.5221 | 282.7643 | 217.9792 | 227.772 | 221.3421 | 208.1919 | 208.9324
1219.5136 | 1114.5136 | 282.4299 | 217.9849 | 227.7293 | 221.1729 | 208.0909 | 208.8688
1220.515 | 1115.515 | 281.9926 | 217.9223 | 227.6748 | 220.9063 | 208.0016 | 208.817
1221.5165 | 1116.5165 | 281.5451 | 217.9061 | 227.6198 | 220.6495 | 207.9267 | 208.7415
1222.5179 | 1117.5179 | 281.193 | 217.8257 | 227.5749 | 220.6202 | 207.8335 | 208.6804
1223.5293 | 1118.5293 | 280.7647 | 217.6495 | 227.5124 | 220.6209 | 207.764 | 208.6069
1224.5208 | 1119.5208 | 280.2113 | 217.4634 | 227.458 | 220.5574 | 207.6905 | 208.5369
1225.5222 | 1120.5222 | 279.7723 | 217.4773 | 227.3861 | 220.1198 | 207.6116 | 208.4587
1226.5136 | 1121.5136 | 279.3345 | 217.4681 | 227.324 | 220.1029 | 207.5303 | 208.3796
1227.5151 | 1122.5151 | 278.8591 | 217.3025 | 227.2623 | 219.9696 | 207.4496 | 208.2951
1228.5165 | 1123.5165 | 278.4139 | 217.3063 | 227.1984 | 219.8291 | 207.3792 | 208.2209
1229.518 | 1124.518 | 277.8327 | 217.1768 | 227.1197 | 219.8625 | 207.2853 | 208.1211
1230.5194 | 1125.5194 | 277.3553 | 217.1084 | 227.0338 | 219.7291 | 207.1784 | 208.0433
1231.5208 | 1126.5208 | 276.9757 | 217.0098 | 226.961 | 219.4686 | 207.0817 | 207.9573
1232.5123 | 1127.5123 | 276.607 | 216.6964 | 226.8534 | 219.4269 | 206.9882 | 207.8716
1233.5137 | 1128.5137 | 276.2088 | 216.7565 | 226.7726 | 219.3763 | 206.9127 | 207.7671
1234.5151 | 1129.5151 | 275.7464 | 216.7444 | 226.6786 | 219.1819 | 206.851 | 207.6635
1235.5166 | 1130.5166 | 275.271 | 216.6921 | 226.5978 | 218.9238 | 206.7617 | 207.5566
1236.518 | 1131.518 | 274.828 | 216.6568 | 226.5165 | 218.5053 | 206.6709 | 207.4546
1237.5195 | 1132.5195 | 274.4994 | 216.5285 | 226.4271 | 218.5485 | 206.5727 | 207.3324
1238.5209 | 1133.5209 | 274.138 | 216.428 | 226.3257 | 217.9533 | 206.4657 | 207.2251
1239.5123 | 1134.5123 | 273.7252 | 216.3981 | 226.2596 | 217.9576 | 206.3621 | 207.1085
1240.5138 | 1135.5138 | 273.1912 | 216.2995 | 226.1817 | 218.0897 | 206.2274 | 206.9945
1241.5152 | 1136.5152 | 272.7289 | 216.1527 | 226.0988 | 218.1647 | 206.1212 | 206.8902
1242.5167 | 1137.5167 | 272.3335 | 216.1969 | 226.0458 | 218.0987 | 206.0145 | 206.7982
1243.5181 | 1138.5181 | 271.8754 | 216.1469 | 225.9706 | 217.7632 | 205.896 | 206.6817
1244.5195 | 1139.5195 | 271.4283 | 216.0145 | 225.9084 | 217.7994 | 205.7832 | 206.5773
1245.511 | 1140.511 | 271.0114 | 216.0187 | 225.8345 | 217.6044 | 205.6393 | 206.4803
1246.5124 | 1141.5124 | 270.6113 | 215.8898 | 225.7756 | 217.5848 | 205.502 | 206.3787
1247.5138 | 1142.5138 | 270.2125 | 215.7836 | 225.7232 | 217.4757 | 205.344 | 206.28
1248.5153 | 1143.5153 | 269.8675 | 215.6798 | 225.6607 | 217.3033 | 205.2149 | 206.1824
1249.5167 | 1144.5167 | 269.5468 | 215.5581 | 225.5957 | 217.318 | 205.0901 | 206.0833
1250.5182 | 1145.5182 | 269.1846 | 215.5066 | 225.5326 | 217.1948 | 204.9613 | 205.9855
1251.5196 | 1146.5196 | 268.874 | 215.4139 | 225.4581 | 217.1056 | 204.854 | 205.8771
1252.511 | 1147.511 | 268.56 | 215.3039 | 225.3882 | 217.0631 | 204.7464 | 205.7782
1253.5125 | 1148.5125 | 268.2334 | 215.2255 | 225.3025 | 216.6983 | 204.6349 | 205.6761
1254.5139 | 1149.5139 | 267.8616 | 215.1674 | 225.232 | 216.6382 | 204.5373 | 205.5626
1255.5153 | 1150.5153 | 267.4038 | 215.1519 | 225.1284 | 216.5177 | 204.4065 | 205.4493
1256.5168 | 1151.5168 | 267.0075 | 215.0814 | 225.0389 | 216.4016 | 204.3013 | 205.3478
1257.5182 | 1152.5182 | 266.6813 | 214.9723 | 224.9552 | 216.37 | 204.1926 | 205.2248
1258.5197 | 1153.5197 | 266.3034 | 214.7517 | 224.8604 | 216.3941 | 204.1118 | 205.1256
1259.5211 | 1154.5211 | 265.9117 | 214.7293 | 224.7644 | 216.2907 | 204.0057 | 205.0143
1260.5225 | 1155.5225 | 265.4809 | 214.6816 | 224.6833 | 216.1501 | 203.9199 | 204.9109
1261.514 | 1156.514 | 265.098 | 214.6192 | 224.5955 | 215.8686 | 203.8338 | 204.8112
1262.5154 | 1157.5154 | 264.8033 | 214.5042 | 224.4991 | 215.6835 | 203.7395 | 204.7043
1263.5168 | 1158.5168 | 264.5364 | 214.4531 | 224.4183 | 215.3881 | 203.6418 | 204.5869
1264.5183 | 1159.5183 | 264.1791 | 214.3499 | 224.3298 | 214.9575 | 203.5433 | 204.4598
1265.5197 | 1160.5197 | 263.7747 | 214.2227 | 224.2369 | 214.803 | 203.4053 | 204.3554
1266.5212 | 1161.5212 | 263.388 | 214.1581 | 224.1426 | 214.7833 | 203.2941 | 204.2475
1267.5126 | 1162.5126 | 262.9831 | 214.0247 | 224.0501 | 214.5845 | 203.188 | 204.1529
1268.514 | 1163.514 | 262.585 | 213.8431 | 223.9582 | 214.3223 | 203.0894 | 204.0536
1269.5155 | 1164.5155 | 262.1707 | 213.4833 | 223.8611 | 214.1451 | 202.9925 | 203.9324
1270.5169 | 1165.5169 | 261.766 | 213.3535 | 223.7615 | 213.9912 | 202.9131 | 203.8025
1271.5184 | 1166.5184 | 261.3585 | 213.3378 | 223.6702 | 213.862 | 202.8201 | 203.6867
1272.5198 | 1167.5198 | 260.9349 | 213.2139 | 223.5618 | 213.6002 | 202.7131 | 203.5684
1273.5212 | 1168.5212 | 260.544 | 213.1835 | 223.4718 | 213.4457 | 202.6067 | 203.4418
1274.5127 | 1169.5127 | 260.1402 | 213.0939 | 223.3646 | 213.1372 | 202.5073 | 203.3326
1275.5141 | 1170.5141 | 259.7755 | 212.954 | 223.2688 | 213.1657 | 202.4093 | 203.2072
1276.5155 | 1171.5155 | 259.3931 | 212.6923 | 223.1741 | 212.9822 | 202.2871 | 203.0774
1277.517 | 1172.517 | 259.0014 | 212.4925 | 223.0754 | 213.0804 | 202.1531 | 202.9716
1278.5184 | 1173.5184 | 258.6305 | 212.4334 | 222.9763 | 213.0084 | 202.0009 | 202.8603
1279.5199 | 1174.5199 | 258.241 | 212.3788 | 222.8894 | 212.9127 | 201.8694 | 202.7303
1280.5213 | 1175.5213 | 257.8569 | 212.1716 | 222.8075 | 212.8785 | 201.6946 | 202.612
1281.5127 | 1176.5127 | 257.4654 | 212.1941 | 222.7128 | 212.8794 | 201.5472 | 202.4851
1282.5142 | 1177.5142 | 257.0893 | 212.126 | 222.6343 | 212.7861 | 201.3851 | 202.3723
1283.5156 | 1178.5156 | 256.73 | 211.9778 | 222.5381 | 212.6072 | 201.1817 | 202.2488
1284.517 | 1179.517 | 256.3833 | 211.885 | 222.4594 | 212.4452 | 201.0017 | 202.126
1285.5185 | 1180.5185 | 255.9833 | 211.8394 | 222.3792 | 212.5042 | 200.7885 | 201.9999
1286.5199 | 1181.5199 | 255.5991 | 211.6621 | 222.3191 | 212.4563 | 200.5934 | 201.8849
1287.5114 | 1182.5114 | 255.3115 | 211.6866 | 222.2305 | 212.2941 | 200.3763 | 201.777
1288.5128 | 1183.5128 | 255.008 | 211.4968 | 222.1636 | 212.2363 | 200.1827 | 201.6655
1289.5142 | 1184.5142 | 254.6435 | 211.496 | 222.0793 | 212.2264 | 199.9933 | 201.5538
1290.5157 | 1185.5157 | 254.2915 | 211.3988 | 222.0014 | 212.1569 | 199.7924 | 201.4159
1291.5171 | 1186.5171 | 253.9481 | 211.1823 | 221.9126 | 212.093 | 199.609 | 201.2961
1292.5186 | 1187.5186 | 253.6306 | 211.1954 | 221.8476 | 212.1068 | 199.3951 | 201.1617
1293.52 | 1188.52 | 253.2715 | 211.0466 | 221.7739 | 211.9944 | 199.245 | 201.0345
1294.5214 | 1189.5214 | 252.9392 | 210.9084 | 221.6941 | 211.7946 | 199.0364 | 200.9106
1295.5129 | 1190.5129 | 252.6528 | 210.6584 | 221.6309 | 211.709 | 198.8583 | 200.7849
1296.5143 | 1191.5143 | 252.2678 | 210.6494 | 221.5539 | 211.6477 | 198.69 | 200.6646
1297.5157 | 1192.5157 | 251.8985 | 210.5376 | 221.4611 | 211.4294 | 198.5276 | 200.5289
1298.5172 | 1193.5172 | 251.542 | 210.3198 | 221.3832 | 211.4363 | 198.3696 | 200.3999
1299.5186 | 1194.5186 | 251.1844 | 210.196 | 221.2959 | 211.2192 | 198.1979 | 200.2546
1300.5201 | 1195.5201 | 250.8152 | 209.9356 | 221.2059 | 211.1644 | 198.0406 | 200.126
1301.5115 | 1196.5115 | 250.4434 | 209.7103 | 221.1193 | 210.9026 | 197.9001 | 199.9865
1302.5129 | 1197.5129 | 250.1735 | 209.6872 | 221.0398 | 210.8353 | 197.7623 | 199.8542
1303.5544 | 1198.5544 | 249.8097 | 209.5664 | 220.9406 | 210.6081 | 197.599 | 199.7057
1304.5158 | 1199.5158 | 249.4732 | 209.5223 | 220.8384 | 210.4619 | 197.484 | 199.5879
1305.5172 | 1200.5172 | 249.1346 | 209.2581 | 220.7303 | 210.3603 | 197.342 | 199.4517
1306.5187 | 1201.5187 | 248.7899 | 209.3035 | 220.6284 | 210.0517 | 197.1592 | 199.3235
1307.5201 | 1202.5201 | 248.3804 | 209.1669 | 220.5186 | 209.598 | 197.0104 | 199.2022
1308.5216 | 1203.5216 | 247.9895 | 209.0501 | 220.3929 | 209.636 | 196.8848 | 199.0818
1309.513 | 1204.513 | 247.6517 | 208.8307 | 220.3082 | 209.647 | 196.7167 | 198.9548
1310.5144 | 1205.5144 | 247.3172 | 208.687 | 220.2008 | 209.5371 | 196.5622 | 198.8311
1311.5159 | 1206.5159 | 246.8978 | 208.6038 | 220.1028 | 209.4262 | 196.396 | 198.6902
1312.5173 | 1207.5173 | 246.5756 | 208.454 | 219.9978 | 209.3366 | 196.2402 | 198.5609
1313.5187 | 1208.5187 | 246.2998 | 208.3649 | 219.8954 | 209.2946 | 196.1093 | 198.4267
1314.5202 | 1209.5202 | 245.987 | 208.2526 | 219.789 | 209.1743 | 195.9425 | 198.298
1315.5216 | 1210.5216 | 245.6813 | 208.0775 | 219.6825 | 208.9932 | 195.8142 | 198.1529
1316.5131 | 1211.5131 | 245.3368 | 207.9432 | 219.5685 | 208.6686 | 195.6825 | 197.9995
1317.5145 | 1212.5145 | 244.9643 | 207.8938 | 219.4507 | 208.5114 | 195.5748 | 197.8708
1318.5159 | 1213.5159 | 244.5352 | 207.7384 | 219.3496 | 208.1857 | 195.4417 | 197.7402
1319.5174 | 1214.5174 | 244.1483 | 207.6059 | 219.226 | 207.9746 | 195.3069 | 197.6072
1320.5188 | 1215.5188 | 243.8469 | 207.4297 | 219.1034 | 207.8388 | 195.213 | 197.4783
1321.5203 | 1216.5203 | 243.4663 | 207.373 | 218.9705 | 207.6854 | 195.0654 | 197.3357
1322.5117 | 1217.5117 | 243.128 | 207.2674 | 218.854 | 207.5269 | 194.9192 | 197.1922
1323.5131 | 1218.5131 | 242.8456 | 207.0971 | 218.7226 | 207.4333 | 194.7934 | 197.0533
1324.5146 | 1219.5146 | 242.6106 | 207.0047 | 218.5963 | 207.1217 | 194.6765 | 196.9283
1325.516 | 1220.516 | 242.3041 | 206.859 | 218.4693 | 207.0098 | 194.5749 | 196.7881
1326.5174 | 1221.5174 | 241.9269 | 206.6959 | 218.3379 | 206.6637 | 194.436 | 196.6564
1327.5189 | 1222.5189 | 241.6014 | 206.615 | 218.2062 | 206.608 | 194.3089 | 196.51
1328.5203 | 1223.5203 | 241.28 | 206.4423 | 218.0682 | 206.5141 | 194.1502 | 196.3719
1329.5218 | 1224.5218 | 240.9497 | 206.2044 | 217.9319 | 206.2573 | 194.0534 | 196.2378
1330.5132 | 1225.5132 | 240.6144 | 206.0468 | 217.8065 | 206.2522 | 193.9296 | 196.1174
1331.5146 | 1226.5146 | 240.2232 | 205.7444 | 217.6705 | 206.0194 | 193.8173 | 195.9898
1332.5161 | 1227.5161 | 239.9148 | 205.4291 | 217.5573 | 205.7999 | 193.6871 | 195.8405
1333.5175 | 1228.5175 | 239.6605 | 205.2849 | 217.4284 | 205.851 | 193.5689 | 195.7202
1334.5189 | 1229.5189 | 239.3623 | 205.1963 | 217.318 | 205.8043 | 193.4119 | 195.5828
1335.5204 | 1230.5204 | 239.035 | 205.1831 | 217.2067 | 205.5633 | 193.2715 | 195.4534
1336.5218 | 1231.5218 | 238.7279 | 204.8854 | 217.1076 | 205.4664 | 193.1662 | 195.3195
1337.5132 | 1232.5132 | 238.4705 | 204.6934 | 217.0101 | 205.267 | 193.0193 | 195.1898
1338.5147 | 1233.5147 | 238.1924 | 204.6341 | 216.9098 | 205.1684 | 192.8649 | 195.0813
1339.5161 | 1234.5161 | 237.9153 | 204.4006 | 216.7991 | 205.0986 | 192.7139 | 194.9527
1340.5176 | 1235.5176 | 237.6819 | 204.2064 | 216.7161 | 205.1001 | 192.5487 | 194.8254
1341.519 | 1236.519 | 237.3703 | 204.0973 | 216.6128 | 204.7397 | 192.3846 | 194.7167
1342.5204 | 1237.5204 | 237.0338 | 204.1032 | 216.5141 | 204.6014 | 192.2458 | 194.5873
1343.5119 | 1238.5119 | 236.6539 | 204.0203 | 216.4227 | 204.5807 | 192.0896 | 194.4554
1344.5133 | 1239.5133 | 236.2829 | 203.965 | 216.333 | 204.5499 | 191.9022 | 194.3332
1345.5148 | 1240.5148 | 235.9635 | 203.8745 | 216.2325 | 204.4668 | 191.6975 | 194.2172
1346.5162 | 1241.5162 | 235.6509 | 203.7382 | 216.1356 | 204.3922 | 191.4672 | 194.0879
1347.5176 | 1242.5176 | 235.3121 | 203.677 | 216.0416 | 204.2676 | 191.2563 | 193.9584
1348.5191 | 1243.5191 | 234.9314 | 203.5276 | 215.9419 | 203.9677 | 191.0985 | 193.8453
1349.5205 | 1244.5205 | 234.6204 | 203.2498 | 215.8427 | 203.8196 | 190.9163 | 193.7151
1350.522 | 1245.522 | 234.2832 | 203.0391 | 215.7464 | 203.2985 | 190.7432 | 193.5995
1351.5134 | 1246.5134 | 233.9208 | 202.8973 | 215.6412 | 203.4304 | 190.5839 | 193.4727
1352.5148 | 1247.5148 | 233.5614 | 202.806 | 215.54 | 203.4395 | 190.4095 | 193.3575
1353.5163 | 1248.5163 | 233.2432 | 202.6892 | 215.4452 | 203.3248 | 190.2388 | 193.2484
1354.5177 | 1249.5177 | 232.9633 | 202.3927 | 215.3411 | 203.1947 | 190.0789 | 193.1219
1355.5191 | 1250.5191 | 232.7108 | 202.1871 | 215.2434 | 203.1507 | 189.941 | 193.0001
1356.5206 | 1251.5206 | 232.3824 | 202.0589 | 215.1493 | 202.964 | 189.804 | 192.8803
1357.512 | 1252.512 | 232.0533 | 201.9908 | 215.0515 | 202.8059 | 189.6815 | 192.7654
1358.5134 | 1253.5134 | 231.7996 | 201.8152 | 214.9324 | 202.7138 | 189.4927 | 192.6248
1359.5149 | 1254.5149 | 231.5372 | 201.7383 | 214.8388 | 202.3754 | 189.3255 | 192.5032
1360.5163 | 1255.5163 | 231.2056 | 201.5353 | 214.7181 | 202.3056 | 189.158 | 192.3777
1361.5178 | 1256.5178 | 230.8615 | 201.2873 | 214.5923 | 202.2409 | 188.9844 | 192.2488
1362.5192 | 1257.5192 | 230.5246 | 201.1662 | 214.4689 | 202.1312 | 188.8314 | 192.1218
1363.5206 | 1258.5206 | 230.2234 | 200.947 | 214.3525 | 201.9834 | 188.6588 | 192.0024
1364.5121 | 1259.5121 | 229.9294 | 200.7593 | 214.2376 | 201.8457 | 188.4685 | 191.8844
1365.5135 | 1260.5135 | 229.6204 | 200.5707 | 214.1238 | 201.7409 | 188.3213 | 191.7519
1366.515 | 1261.515 | 229.2705 | 200.3859 | 214.0119 | 201.5774 | 188.1469 | 191.6311
1367.5164 | 1262.5164 | 228.9484 | 200.3202 | 213.8848 | 201.4645 | 187.9675 | 191.5117
1368.5178 | 1263.5178 | 228.6249 | 200.1916 | 213.7594 | 201.2806 | 187.7257 | 191.3956
1369.5193 | 1264.5193 | 228.3024 | 199.9746 | 213.6456 | 201.1383 | 187.564 | 191.2926
1370.5207 | 1265.5207 | 228.0059 | 199.9675 | 213.5187 | 200.8952 | 187.4074 | 191.1719
1371.5222 | 1266.5222 | 227.6256 | 199.7835 | 213.3937 | 200.5829 | 187.2228 | 191.0472
1372.5136 | 1267.5136 | 227.3106 | 199.6868 | 213.2589 | 200.3275 | 187.0579 | 190.9172
1373.515 | 1268.515 | 227.0396 | 199.5108 | 213.1464 | 200.3592 | 186.8668 | 190.8003
1374.5165 | 1269.5165 | 226.7499 | 199.4431 | 213.0166 | 200.3099 | 186.7157 | 190.6742
1375.5179 | 1270.5179 | 226.4247 | 199.2929 | 212.8922 | 200.1513 | 186.5302 | 190.5535
1376.5193 | 1271.5193 | 226.1222 | 199.2031 | 212.7583 | 200.0498 | 186.3632 | 190.4268
1377.5108 | 1272.5108 | 225.8604 | 199.0849 | 212.6295 | 199.8435 | 186.2177 | 190.3092
1378.5122 | 1273.5122 | 225.6403 | 198.9108 | 212.5051 | 199.7255 | 186.075 | 190.2023
1379.5136 | 1274.5136 | 225.4136 | 198.5897 | 212.3513 | 199.6328 | 185.9049 | 190.079
1380.5151 | 1275.5151 | 225.1765 | 198.4831 | 212.2335 | 199.2991 | 185.7395 | 189.9356
1381.5165 | 1276.5165 | 224.8783 | 198.425 | 212.1079 | 199.0015 | 185.6121 | 189.807
1382.518 | 1277.518 | 224.5299 | 198.3102 | 211.9706 | 199.0374 | 185.4449 | 189.6715
1383.5194 | 1278.5194 | 224.224 | 198.1489 | 211.8328 | 198.9727 | 185.2269 | 189.5431
1384.5208 | 1279.5208 | 223.8855 | 198.051 | 211.688 | 198.8426 | 185.1048 | 189.4482
1385.5123 | 1280.5123 | 223.5203 | 197.9175 | 211.5665 | 198.7268 | 184.9498 | 189.3094
1386.5137 | 1281.5137 | 223.2547 | 197.7489 | 211.4313 | 198.5564 | 184.7781 | 189.1878
1387.5151 | 1282.5151 | 222.9529 | 197.4966 | 211.3081 | 198.4093 | 184.5941 | 189.0568
1388.5166 | 1283.5166 | 222.6386 | 197.4316 | 211.1874 | 198.3087 | 184.4177 | 188.9309
1389.518 | 1284.518 | 222.3714 | 197.2149 | 211.0509 | 198.206 | 184.2308 | 188.8274
1390.5195 | 1285.5195 | 222.0979 | 197.0857 | 210.9372 | 198.1932 | 184.103 | 188.7301
1391.5209 | 1286.5209 | 221.7323 | 196.9429 | 210.8135 | 197.9292 | 183.9704 | 188.6102
1392.5223 | 1287.5223 | 221.3817 | 196.7856 | 210.6906 | 197.6886 | 183.8459 | 188.4854
1393.5138 | 1288.5138 | 221.139 | 196.6639 | 210.5326 | 197.4722 | 183.6989 | 188.3525
1394.5152 | 1289.5152 | 220.926 | 196.5365 | 210.4228 | 197.1784 | 183.5501 | 188.214
1395.5167 | 1290.5167 | 220.7109 | 196.4605 | 210.2829 | 197.1602 | 183.4488 | 188.0859
1396.5181 | 1291.5181 | 220.4829 | 196.27 | 210.1428 | 197.0257 | 183.3608 | 187.9578
1397.5195 | 1292.5195 | 220.1993 | 196.2121 | 209.9965 | 196.5868 | 183.2606 | 187.819
1398.521 | 1293.521 | 219.8931 | 196.0697 | 209.8449 | 196.2782 | 183.1492 | 187.691
1399.5224 | 1294.5224 | 219.5689 | 195.8939 | 209.6928 | 196.3138 | 183.0494 | 187.5488
1400.5138 | 1295.5138 | 219.265 | 195.8129 | 209.5389 | 196.1993 | 182.9297 | 187.3841
1401.5153 | 1296.5153 | 218.9705 | 195.763 | 209.3689 | 195.9934 | 182.8528 | 187.2719
1402.5167 | 1297.5167 | 218.6957 | 195.6773 | 209.2341 | 195.7232 | 182.7833 | 187.1563
1403.5182 | 1298.5182 | 218.419 | 195.4683 | 209.0867 | 195.5698 | 182.6845 | 187.0444
1404.5196 | 1299.5196 | 218.0702 | 195.1489 | 208.9293 | 195.1218 | 182.5885 | 186.9188
1405.521 | 1300.521 | 217.7645 | 194.9714 | 208.7829 | 194.973 | 182.4733 | 186.7773
1406.5125 | 1301.5125 | 217.4918 | 194.8849 | 208.6235 | 194.9915 | 182.371 | 186.65
1407.5139 | 1302.5139 | 217.1958 | 194.8123 | 208.477 | 194.8816 | 182.2809 | 186.5066
1408.5153 | 1303.5153 | 216.9085 | 194.6662 | 208.3237 | 194.7931 | 182.1521 | 186.3602
1409.5168 | 1304.5168 | 216.6902 | 194.5913 | 208.1688 | 194.7483 | 182.0252 | 186.2418
1410.5182 | 1305.5182 | 216.5132 | 194.4645 | 208.021 | 194.3805 | 181.8798 | 186.1198
1411.5197 | 1306.5197 | 216.2782 | 194.2692 | 207.8548 | 194.1671 | 181.756 | 185.9921
1412.5211 | 1307.5211 | 215.9503 | 194.1611 | 207.7356 | 194.1147 | 181.6004 | 185.8439
1413.5225 | 1308.5225 | 215.643 | 194.0629 | 207.5782 | 193.7529 | 181.4883 | 185.7093
1414.514 | 1309.514 | 215.3734 | 193.9516 | 207.4426 | 193.6041 | 181.3712 | 185.5975
1415.5154 | 1310.5154 | 215.0911 | 193.8863 | 207.3131 | 193.4528 | 181.2405 | 185.4739
1416.5169 | 1311.5169 | 214.7841 | 193.5804 | 207.1676 | 193.2636 | 181.1026 | 185.3205
1417.5183 | 1312.5183 | 214.4579 | 193.2684 | 207.0376 | 193.1181 | 180.9303 | 185.1794
1418.5197 | 1313.5197 | 214.1681 | 193.0087 | 206.8815 | 192.8786 | 180.7954 | 185.0464

## C3-4
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.6166 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38904.5359 | 1 | 0 | 38904.5359 | 1 | 0 | -90 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5361 | 1 | 0 | 38904.5361 | 1 | 0 | -73 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5363 | 1 | 0 | 38904.5363 | 1 | 0 | -56.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5365 | 1 | 0 | 38904.5365 | 1 | 0 | -39.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5367 | 1 | 0 | 38904.5367 | 1 | 0 | -22.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5369 | 1 | 0 | 38904.5369 | 1 | 0 | -6 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5371 | 1 | 0 | 38904.5371 | 1 | 0 | 11 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5373 | 1 | 0 | 38904.5373 | 1 | 0 | 27.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5375 | 1 | 0 | 38904.5375 | 1 | 0 | 44.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5377 | 1 | 0 | 38904.5377 | 1 | 0 | 61.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5379 | 1 | 0 | 38904.5379 | 1 | 0 | 78 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5381 | 1 | 0 | 38904.5381 | 1 | 0 | 95 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5383 | 2 | 0 | 38904.5383 | 1 | 0 | 111.5 | 216.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128169 | 256438 | 128168.9988
38904.5384 | 1 | 0 | 38904.5385 | 1 | 0 | 128.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5386 | 1 | 0 | 38904.5387 | 1 | 0 | 145.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5388 | 1 | 0 | 38904.5389 | 2 | 0 | 162 | 267 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256438 | 128169 | 256437.9994
38904.539 | 1 | 0 | 38904.5391 | 1 | 0 | 179 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
| 1 | 0 | 38904.5392 | 1 | 0 | 196 | 301 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5394 | 1 | 0 | 38904.5394 | 1 | 0 | 212.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5396 | 2 | 0 | 38904.5396 | 1 | 0 | 229.5 | 334.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128169 | 256438 | 128168.9988
38904.5398 | 1 | 0 | 38904.5398 | 1 | 0 | 246 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.54 | 1 | 0 | 38904.54 | 1 | 0 | 263 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5402 | 1 | 0 | 38904.5402 | 1 | 0 | 279.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5404 | 1 | 0 | 38904.5404 | 1 | 0 | 296.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5406 | 1 | 0 | 38904.5406 | 1 | 0 | 313.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5408 | 1 | 0 | 38904.5408 | 1 | 0 | 330 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.541 | 1 | 0 | 38904.541 | 1 | 0 | 346.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5412 | 1 | 0 | 38904.5412 | 1 | 0 | 363.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5414 | 1 | 0 | 38904.5414 | 1 | 0 | 380.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5416 | 1 | 0 | 38904.5416 | 1 | 0 | 397.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5417 | 1 | 0 | 38904.5418 | 1 | 0 | 414 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5419 | 1 | 0 | 38904.542 | 1 | 0 | 430.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5421 | 1 | 0 | 38904.5422 | 1 | 0 | 447.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5423 | 1 | 0 | 38904.5423 | 1 | 0 | 464.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5425 | 1 | 0 | 38904.5425 | 1 | 0 | 481 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5427 | 1 | 0 | 38904.5427 | 1 | 0 | 498 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5429 | 1 | 0 | 38904.5429 | 1 | 0 | 515 | 620 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5431 | 1 | 0 | 38904.5431 | 1 | 0 | 531.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5433 | 1 | 0 | 38904.5433 | 1 | 0 | 548.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5435 | 1 | 0 | 38904.5435 | 1 | 0 | 565 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5437 | 1 | 0 | 38904.5437 | 1 | 0 | 582 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5439 | 1 | 0 | 38904.5439 | 1 | 0 | 599 | 704 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5441 | 1 | 0 | 38904.5441 | 1 | 0 | 615.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5443 | 1 | 0 | 38904.5443 | 1 | 0 | 632.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5445 | 1 | 0 | 38904.5445 | 1 | 0 | 649 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5447 | 1 | 0 | 38904.5447 | 1 | 0 | 666 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5449 | 1 | 0 | 38904.5449 | 1 | 0 | 682.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5451 | 1 | 0 | 38904.5451 | 1 | 0 | 699.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5453 | 1 | 0 | 38904.5453 | 1 | 0 | 716.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5454 | 1 | 0 | 38904.5455 | 1 | 0 | 733 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5456 | 1 | 0 | 38904.5457 | 1 | 0 | 750 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.5458 | 1 | 0 | 38904.5458 | 1 | 0 | 766.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38904.546 | 8 | 0 | 38904.546 | 7 | 0 | 783.5 | 888.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31967.25 | 36548.2857 | 31967.2451
38904.5462 | 10 | 0 | 38904.5462 | 8 | 0 | 800.5 | 905.5 | 0.6105 | 0 | 0.4884 | 0 | 0.006105 | 0 | 0.004884 | 0 | 0.006105 | 0.004884 | 25553.8 | 31967.25 | 25553.7939
38904.5464 | 10 | 0 | 38904.5464 | 9 | 0 | 817 | 922 | 0.6105 | 0 | 0.54945 | 0 | 0.006105 | 0 | 0.0054945 | 0 | 0.006105 | 0.0054945 | 25553.8 | 28404.2222 | 25553.7939
38904.5466 | 10 | 0 | 38904.5466 | 10 | 0 | 834 | 939 | 0.6105 | 0 | 0.6105 | 0 | 0.006105 | 0 | 0.006105 | 0 | 0.006105 | 0.006105 | 25553.8 | 25553.8 | 25553.7939
38904.5468 | 10 | 0 | 38904.5468 | 9 | 0 | 850.5 | 955.5 | 0.6105 | 0 | 0.54945 | 0 | 0.006105 | 0 | 0.0054945 | 0 | 0.006105 | 0.0054945 | 25553.8 | 28404.2222 | 25553.7939
38904.547 | 9 | 0 | 38904.547 | 10 | 0 | 867.5 | 972.5 | 0.54945 | 0 | 0.6105 | 0 | 0.0054945 | 0 | 0.006105 | 0 | 0.0054945 | 0.006105 | 28404.2222 | 25553.8 | 28404.2167
38904.5472 | 10 | 0 | 38904.5472 | 9 | 0 | 884.5 | 989.5 | 0.6105 | 0 | 0.54945 | 0 | 0.006105 | 0 | 0.0054945 | 0 | 0.006105 | 0.0054945 | 25553.8 | 28404.2222 | 25553.7939
38904.5474 | 12 | 0 | 38904.5474 | 9 | 0 | 901 | 1006 | 0.7326 | 0 | 0.54945 | 0 | 0.007326 | 0 | 0.0054945 | 0 | 0.007326 | 0.0054945 | 21278.1667 | 28404.2222 | 21278.1593
38904.5476 | 12 | 0 | 38904.5476 | 9 | 0 | 918 | 1023 | 0.7326 | 0 | 0.54945 | 0 | 0.007326 | 0 | 0.0054945 | 0 | 0.007326 | 0.0054945 | 21278.1667 | 28404.2222 | 21278.1593
38904.5478 | 39 | 0 | 38904.5478 | 9 | 0 | 934.5 | 1039.5 | 2.381 | 0 | 0.54945 | 0 | 0.02381 | 0 | 0.0054945 | 0 | 0.02381 | 0.0054945 | 6477.8974 | 28404.2222 | 6477.8736
38904.548 | 18 | 0 | 38904.548 | 10 | 0 | 951.5 | 1056.5 | 1.0989 | 0 | 0.6105 | 0 | 0.010989 | 0 | 0.006105 | 0 | 0.010989 | 0.006105 | 14152.1111 | 25553.8 | 14152.1001
38904.5482 | 76 | 0 | 38904.5482 | 10 | 0 | 968.5 | 1073.5 | 4.6398 | 0 | 0.6105 | 0 | 0.046398 | 0 | 0.006105 | 0 | 0.046398 | 0.006105 | 3275.5 | 25553.8 | 3275.4536
38904.5484 | 2095 | 0 | 38904.5484 | 2078 | 0 | 985 | 1090 | 127.8999 | 0 | 126.862 | 0 | 1.279 | 0 | 1.2686 | 0 | 1.279 | 1.2686 | 22.4525 | 23.4543 | 21.1735
38904.5486 | 2084 | 0 | 38904.5486 | 2168 | 0 | 1002 | 1107 | 127.2283 | 0 | 132.3565 | 0 | 1.2723 | 0 | 1.3236 | 0 | 1.2723 | 1.3236 | 23.0988 | 18.3293 | 21.8266
38904.5488 | 2500 | 0 | 38904.5488 | 2327 | 0 | 1018.5 | 1123.5 | 152.6252 | 0 | 142.0635 | 0 | 1.5263 | 0 | 1.4206 | 0 | 1.5263 | 1.4206 | 2.6152 | 10.2441 | 1.0889
38904.5489 | 2534 | 0 | 38904.549 | 2114 | 0 | 1035.5 | 1140.5 | 154.7009 | 0 | 129.0598 | 0 | 1.547 | 0 | 1.2906 | 0 | 1.547 | 1.2906 | 1.2384 | 21.3519 | 0.30865
38904.5491 | 2375 | 0 | 38904.5492 | 2500 | 0 | 1052.5 | 1157.5 | 144.9939 | 0 | 152.6252 | 0 | 1.4499 | 0 | 1.5263 | 0 | 1.4499 | 1.5263 | 8.016 | 2.6152 | 6.5661
38904.5493 | 1992 | 0 | 38904.5494 | 1978 | 0 | 1069 | 1174 | 121.6117 | 0 | 120.757 | 0 | 1.2161 | 0 | 1.2076 | 0 | 1.2161 | 1.2076 | 28.7841 | 29.6957 | 27.568
38904.5495 | 2273 | 0 | 38904.5495 | 2501 | 0 | 1086 | 1191 | 138.7668 | 0 | 152.6862 | 0 | 1.3877 | 0 | 1.5269 | 0 | 1.3877 | 1.5269 | 12.8632 | 2.5742 | 11.4755
38904.5497 | 2446 | 0 | 38904.5497 | 2069 | 0 | 1102.5 | 1207.5 | 149.3284 | 0 | 126.3126 | 0 | 1.4933 | 0 | 1.2631 | 0 | 1.4933 | 1.2631 | 4.8806 | 23.9913 | 3.3873
38904.5499 | 2222 | 0 | 38904.5499 | 2330 | 0 | 1119.5 | 1224.5 | 135.6532 | 0 | 142.2466 | 0 | 1.3565 | 0 | 1.4225 | 0 | 1.3565 | 1.4225 | 15.4536 | 10.1021 | 14.0971
38904.5501 | 2252 | 0 | 38904.5501 | 1962 | 0 | 1136.5 | 1241.5 | 137.4847 | 0 | 119.7802 | 0 | 1.3748 | 0 | 1.1978 | 0 | 1.3748 | 1.1978 | 13.9156 | 30.7533 | 12.5408
38904.5503 | 2124 | 0 | 38904.5503 | 2463 | 0 | 1153 | 1258 | 129.6703 | 0 | 150.3663 | 0 | 1.2967 | 0 | 1.5037 | 0 | 1.2967 | 1.5037 | 20.7806 | 4.1567 | 19.4839
38904.5505 | 2190 | 0 | 38904.5505 | 2438 | 0 | 1170 | 1275 | 133.6996 | 0 | 148.84 | 0 | 1.337 | 0 | 1.4884 | 0 | 1.337 | 1.4884 | 17.1406 | 5.2248 | 15.8036
38904.5507 | 2078 | 0 | 38904.5507 | 2207 | 0 | 1186.5 | 1291.5 | 126.862 | 0 | 134.7375 | 0 | 1.2686 | 0 | 1.3474 | 0 | 1.2686 | 1.3474 | 23.4543 | 16.2383 | 22.1857
38904.5509 | 2069 | 0 | 38904.5509 | 2285 | 0 | 1203.5 | 1308.5 | 126.3126 | 0 | 139.4994 | 0 | 1.2631 | 0 | 1.395 | 0 | 1.2631 | 1.395 | 23.9913 | 12.2705 | 22.7282
38904.5511 | 2187 | 0 | 38904.5511 | 2508 | 0 | 1220.5 | 1325.5 | 133.5165 | 0 | 153.1136 | 0 | 1.3352 | 0 | 1.5311 | 0 | 1.3352 | 1.5311 | 17.3013 | 2.2879 | 15.9662
38904.5513 | 2507 | 0 | 38904.5513 | 2549 | 0 | 1237 | 1342 | 153.0525 | 0 | 155.6166 | 0 | 1.5305 | 0 | 1.5562 | 0 | 1.5305 | 1.5562 | 2.3287 | 0.6426 | 0.79815
38904.5515 | 2547 | 0 | 38904.5515 | 2158 | 0 | 1254 | 1359 | 155.4945 | 0 | 131.746 | 0 | 1.5549 | 0 | 1.3175 | 0 | 1.5549 | 1.3175 | 0.72163 | 18.8777 | 0.83331
38904.5517 | 2317 | 0 | 38904.5517 | 2189 | 0 | 1270.5 | 1375.5 | 141.453 | 0 | 133.6386 | 0 | 1.4145 | 0 | 1.3364 | 0 | 1.4145 | 1.3364 | 10.7199 | 17.1942 | 9.3054
38904.5519 | 2482 | 0 | 38904.5519 | 2382 | 0 | 1287.5 | 1392.5 | 151.5263 | 0 | 145.4212 | 0 | 1.5153 | 0 | 1.4542 | 0 | 1.5153 | 1.4542 | 3.3594 | 7.6986 | 1.8441
38904.5521 | 2074 | 0 | 38904.5521 | 2494 | 0 | 1304.5 | 1409.5 | 126.6178 | 0 | 152.2589 | 0 | 1.2662 | 0 | 1.5226 | 0 | 1.2662 | 1.5226 | 23.6924 | 2.8621 | 22.4262

## C2-4
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.4335 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38904.5359 | 1 | 0 | 38904.5359 | 1 | 0 | -92.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5361 | 1 | 0 | 38904.5361 | 1 | 0 | -76 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5363 | 1 | 0 | 38904.5363 | 1 | 0 | -59 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5365 | 1 | 0 | 38904.5365 | 1 | 0 | -42.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5367 | 1 | 0 | 38904.5367 | 1 | 0 | -25.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5369 | 1 | 0 | 38904.5369 | 4 | 0 | -8.5 | 96.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 256138 | 63959.5 | 256137.9994
38904.537 | 1 | 0 | 38904.5371 | 1 | 0 | 8 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5372 | 1 | 0 | 38904.5373 | 1 | 0 | 25 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5374 | 1 | 0 | 38904.5375 | 1 | 0 | 41.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5376 | 1 | 0 | 38904.5377 | 1 | 0 | 58.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5378 | 1 | 0 | 38904.5378 | 1 | 0 | 75.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.538 | 1 | 1 | 38904.538 | 1 | 0 | 92 | 197 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38904.5382 | 1 | 0 | 38904.5382 | 1 | 0 | 109 | 214 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5384 | 1 | 0 | 38904.5384 | 1 | 0 | 125.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5386 | 1 | 0 | 38904.5386 | 1 | 0 | 142.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5388 | 1 | 0 | 38904.5388 | 1 | 0 | 159.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.539 | 1 | 0 | 38904.539 | 1 | 0 | 176 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5392 | 1 | 0 | 38904.5392 | 1 | 0 | 193 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5394 | 1 | 0 | 38904.5394 | 1 | 0 | 209.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5396 | 1 | 0 | 38904.5396 | 1 | 0 | 226.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5398 | 1 | 0 | 38904.5398 | 1 | 0 | 243.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.54 | 1 | 0 | 38904.54 | 1 | 0 | 260 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5402 | 1 | 0 | 38904.5402 | 1 | 0 | 277 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5404 | 1 | 0 | 38904.5404 | 1 | 0 | 293.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5406 | 1 | 0 | 38904.5406 | 1 | 0 | 310.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5407 | 1 | 0 | 38904.5408 | 1 | 0 | 327 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5409 | 1 | 0 | 38904.541 | 1 | 0 | 344 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5411 | 1 | 0 | 38904.5412 | 1 | 0 | 361 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5413 | 1 | 0 | 38904.5413 | 1 | 0 | 377.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5415 | 1 | 0 | 38904.5415 | 1 | 0 | 394.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5417 | 1 | 0 | 38904.5417 | 1 | 0 | 411 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5419 | 1 | 0 | 38904.5419 | 1 | 0 | 428 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5421 | 1 | 0 | 38904.5421 | 1 | 0 | 444.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5423 | 1 | 0 | 38904.5423 | 1 | 0 | 461.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5425 | 1 | 0 | 38904.5425 | 1 | 0 | 478.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5427 | 1 | 0 | 38904.5427 | 1 | 0 | 495 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5429 | 1 | 0 | 38904.5429 | 1 | 0 | 512 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5431 | 1 | 0 | 38904.5431 | 1 | 0 | 528.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5433 | 1 | 0 | 38904.5433 | 2 | 0 | 545.5 | 650.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256138 | 128019 | 256137.9994
38904.5435 | 1 | 0 | 38904.5435 | 1 | 0 | 562.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5437 | 1 | 0 | 38904.5437 | 1 | 0 | 579.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5439 | 1 | 0 | 38904.5439 | 1 | 0 | 596 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5441 | 1 | 0 | 38904.5441 | 1 | 0 | 612.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5442 | 1 | 0 | 38904.5443 | 1 | 0 | 629.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5444 | 1 | 0 | 38904.5445 | 1 | 0 | 646.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5446 | 1 | 0 | 38904.5447 | 1 | 0 | 663.5 | 768.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5448 | 1 | 0 | 38904.5448 | 1 | 0 | 680 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.545 | 1 | 0 | 38904.545 | 1 | 0 | 696.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5452 | 1 | 0 | 38904.5452 | 1 | 0 | 713.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5454 | 1 | 0 | 38904.5454 | 1 | 0 | 730.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5456 | 1 | 0 | 38904.5456 | 1 | 0 | 747 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5458 | 1 | 0 | 38904.5458 | 1 | 0 | 764 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.546 | 2455 | 0 | 38904.546 | 10 | 0 | 780.5 | 885.5 | 149.8779 | 0 | 0.6105 | 0 | 1.4988 | 0 | 0.006105 | 0 | 1.4988 | 0.006105 | 4.3739 | 25523.8 | 2.8752
38904.5462 | 2448 | 0 | 38904.5462 | 10 | 0 | 797.5 | 902.5 | 149.4505 | 0 | 0.6105 | 0 | 1.4945 | 0 | 0.006105 | 0 | 1.4945 | 0.006105 | 4.6724 | 25523.8 | 3.1779
38904.5464 | 2225 | 0 | 38904.5464 | 11 | 0 | 814.5 | 919.5 | 135.8364 | 0 | 0.67155 | 0 | 1.3584 | 0 | 0.0067155 | 0 | 1.3584 | 0.0067155 | 15.1631 | 23194.3636 | 13.8048
38904.5466 | 2418 | 0 | 38904.5466 | 11 | 0 | 831 | 936 | 147.619 | 0 | 0.67155 | 0 | 1.4762 | 0 | 0.0067155 | 0 | 1.4762 | 0.0067155 | 5.9711 | 23194.3636 | 4.4949
38904.5468 | 1988 | 0 | 38904.5468 | 10 | 0 | 848 | 953 | 121.3675 | 0 | 0.6105 | 0 | 1.2137 | 0 | 0.006105 | 0 | 1.2137 | 0.006105 | 28.8924 | 25523.8 | 27.6787
38904.547 | 2380 | 0 | 38904.547 | 12 | 0 | 864.5 | 969.5 | 145.2991 | 0 | 0.7326 | 0 | 1.453 | 0 | 0.007326 | 0 | 1.453 | 0.007326 | 7.663 | 21253.1667 | 6.21
38904.5472 | 2515 | 0 | 38904.5472 | 11 | 0 | 881.5 | 986.5 | 153.5409 | 0 | 0.67155 | 0 | 1.5354 | 0 | 0.0067155 | 0 | 1.5354 | 0.0067155 | 1.8839 | 23194.3636 | 0.34849
38904.5474 | 2167 | 0 | 38904.5474 | 13 | 0 | 898.5 | 1003.5 | 132.2955 | 0 | 0.79365 | 0 | 1.323 | 0 | 0.0079365 | 0 | 1.323 | 0.0079365 | 18.2455 | 19610.6154 | 16.9225
38904.5475 | 2051 | 0 | 38904.5476 | 11 | 0 | 915 | 1020 | 125.2137 | 0 | 0.67155 | 0 | 1.2521 | 0 | 0.0067155 | 0 | 1.2521 | 0.0067155 | 24.9332 | 23194.3636 | 23.6811
38904.5477 | 2499 | 0 | 38904.5478 | 13 | 0 | 932 | 1037 | 152.5641 | 0 | 0.79365 | 0 | 1.5256 | 0 | 0.0079365 | 0 | 1.5256 | 0.0079365 | 2.5362 | 19610.6154 | 1.0106
38904.5479 | 2037 | 0 | 38904.548 | 13 | 0 | 948.5 | 1053.5 | 124.359 | 0 | 0.79365 | 0 | 1.2436 | 0 | 0.0079365 | 0 | 1.2436 | 0.0079365 | 25.7919 | 19610.6154 | 24.5483
38904.5481 | 1988 | 0 | 38904.5481 | 12 | 0 | 965.5 | 1070.5 | 121.3675 | 0 | 0.7326 | 0 | 1.2137 | 0 | 0.007326 | 0 | 1.2137 | 0.007326 | 28.8924 | 21253.1667 | 27.6787
38904.5483 | 2480 | 0 | 38904.5483 | 466 | 11 | 982.5 | 1087.5 | 151.4042 | 0 | 28.4493 | 0.67155 | 1.514 | 0 | 0.28449 | 0.0067155 | 1.514 | 0.27778 | 3.3218 | 463.1604 | 1.8077
38904.5485 | 2216 | 0 | 38904.5485 | 2196 | 0 | 999 | 1104 | 135.2869 | 0 | 134.0659 | 0 | 1.3529 | 0 | 1.3407 | 0 | 1.3529 | 1.3407 | 15.6309 | 16.684 | 14.278
38904.5487 | 2357 | 0 | 38904.5487 | 2036 | 0 | 1016 | 1121 | 143.895 | 0 | 124.2979 | 0 | 1.4389 | 0 | 1.243 | 0 | 1.4389 | 1.243 | 8.7136 | 25.8536 | 7.2747
38904.5489 | 1948 | 0 | 38904.5489 | 2211 | 0 | 1032.5 | 1137.5 | 118.9255 | 0 | 134.9817 | 0 | 1.1893 | 0 | 1.3498 | 0 | 1.1893 | 1.3498 | 31.539 | 15.8924 | 30.3498
38904.5491 | 1949 | 0 | 38904.5491 | 2160 | 0 | 1049.5 | 1154.5 | 118.9866 | 0 | 131.8681 | 0 | 1.1899 | 0 | 1.3187 | 0 | 1.1899 | 1.3187 | 31.4715 | 18.6287 | 30.2817
38904.5493 | 2528 | 0 | 38904.5493 | 2543 | 0 | 1066.5 | 1171.5 | 154.3346 | 0 | 155.2503 | 0 | 1.5433 | 0 | 1.5525 | 0 | 1.5433 | 1.5525 | 1.36 | 0.76209 | 0.18338
38904.5495 | 1956 | 0 | 38904.5495 | 2279 | 0 | 1083 | 1188 | 119.4139 | 0 | 139.1331 | 0 | 1.1941 | 0 | 1.3913 | 0 | 1.1941 | 1.3913 | 31.001 | 12.4344 | 29.8069
38904.5497 | 2061 | 0 | 38904.5497 | 2506 | 0 | 1100 | 1205 | 125.8242 | 0 | 152.9915 | 0 | 1.2582 | 0 | 1.5299 | 0 | 1.2582 | 1.5299 | 24.327 | 2.2498 | 23.0688
38904.5499 | 2532 | 0 | 38904.5499 | 2546 | 0 | 1116.5 | 1221.5 | 154.5788 | 0 | 155.4335 | 0 | 1.5458 | 0 | 1.5543 | 0 | 1.5458 | 1.5543 | 1.1998 | 0.64336 | 0.34595
38904.5501 | 2199 | 0 | 38904.5501 | 2314 | 0 | 1133.5 | 1238.5 | 134.2491 | 0 | 141.2698 | 0 | 1.3425 | 0 | 1.4127 | 0 | 1.3425 | 1.4127 | 16.5248 | 10.7338 | 15.1823
38904.5503 | 1964 | 0 | 38904.5503 | 2111 | 0 | 1150.5 | 1255.5 | 119.9023 | 0 | 128.8767 | 0 | 1.199 | 0 | 1.2888 | 0 | 1.199 | 1.2888 | 30.4674 | 21.3823 | 29.2684
38904.5505 | 1963 | 0 | 38904.5505 | 2346 | 0 | 1167 | 1272 | 119.8413 | 0 | 143.2234 | 0 | 1.1984 | 0 | 1.4322 | 0 | 1.1984 | 1.4322 | 30.5339 | 9.2234 | 29.3355
38904.5507 | 2516 | 0 | 38904.5507 | 2390 | 0 | 1184 | 1289 | 153.602 | 0 | 145.9096 | 0 | 1.536 | 0 | 1.4591 | 0 | 1.536 | 1.4591 | 1.8434 | 7.2126 | 0.30738
38904.5509 | 2534 | 0 | 38904.5509 | 2125 | 0 | 1200.5 | 1305.5 | 154.7009 | 0 | 129.7314 | 0 | 1.547 | 0 | 1.2973 | 0 | 1.547 | 1.2973 | 1.12 | 20.5826 | 0.42704
38904.5511 | 2529 | 0 | 38904.5511 | 2119 | 0 | 1217.5 | 1322.5 | 154.3956 | 0 | 129.3651 | 0 | 1.544 | 0 | 1.2937 | 0 | 1.544 | 1.2937 | 1.3199 | 20.924 | 0.22407
38904.5512 | 2293 | 0 | 38904.5513 | 2341 | 0 | 1234.5 | 1339.5 | 139.9878 | 0 | 142.9182 | 0 | 1.3999 | 0 | 1.4292 | 0 | 1.3999 | 1.4292 | 11.7479 | 9.4566 | 10.3481
38904.5514 | 2278 | 0 | 38904.5515 | 2298 | 0 | 1251 | 1356 | 139.072 | 0 | 140.293 | 0 | 1.3907 | 0 | 1.4029 | 0 | 1.3907 | 1.4029 | 12.4838 | 11.5048 | 11.093
38904.5516 | 1955 | 0 | 38904.5517 | 2002 | 0 | 1268 | 1373 | 119.3529 | 0 | 122.2222 | 0 | 1.1935 | 0 | 1.2222 | 0 | 1.1935 | 1.2222 | 31.068 | 27.991 | 29.8745
38904.5518 | 1990 | 0 | 38904.5518 | 2202 | 0 | 1284.5 | 1389.5 | 121.4896 | 0 | 134.4322 | 0 | 1.2149 | 0 | 1.3443 | 0 | 1.2149 | 1.3443 | 28.7628 | 16.366 | 27.5479
38904.552 | 2365 | 0 | 38904.552 | 2015 | 0 | 1301.5 | 1406.5 | 144.3834 | 0 | 123.0159 | 0 | 1.4438 | 0 | 1.2302 | 0 | 1.4438 | 1.2302 | 8.3459 | 27.1653 | 6.902

## C2-3
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.4945 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38904.5359 | 1 | 0 | 38904.5359 | 1 | 0 | -95.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5361 | 1 | 0 | 38904.5361 | 1 | 0 | -78.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5362 | 1 | 0 | 38904.5363 | 1 | 0 | -62 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5364 | 2 | 0 | 38904.5365 | 1 | 0 | -45 | 60 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128069 | 256238 | 128068.9988
38904.5366 | 1 | 0 | 38904.5366 | 1 | 0 | -28.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5368 | 1 | 0 | 38904.5368 | 1 | 0 | -11.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.537 | 1 | 0 | 38904.537 | 1 | 0 | 5.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5372 | 1 | 0 | 38904.5372 | 1 | 0 | 22 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5374 | 1 | 0 | 38904.5374 | 1 | 0 | 39 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5376 | 1 | 0 | 38904.5376 | 1 | 0 | 55.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5378 | 1 | 0 | 38904.5378 | 1 | 0 | 72.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.538 | 1 | 0 | 38904.538 | 1 | 0 | 89.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5382 | 1 | 0 | 38904.5382 | 1 | 0 | 106 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5384 | 1 | 0 | 38904.5384 | 1 | 0 | 123 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5386 | 1 | 0 | 38904.5386 | 1 | 0 | 139.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5388 | 1 | 0 | 38904.5388 | 1 | 0 | 156.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.539 | 2 | 0 | 38904.539 | 1 | 0 | 173 | 278 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128069 | 256238 | 128068.9988
38904.5392 | 1 | 0 | 38904.5392 | 1 | 0 | 190 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5394 | 1 | 0 | 38904.5394 | 1 | 0 | 206.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5395 | 1 | 0 | 38904.5396 | 1 | 0 | 223.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5397 | 1 | 0 | 38904.5398 | 1 | 0 | 240.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5399 | 1 | 0 | 38904.54 | 1 | 0 | 257.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5401 | 1 | 0 | 38904.5402 | 1 | 0 | 274 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5403 | 1 | 0 | 38904.5403 | 1 | 0 | 291 | 396 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5405 | 1 | 0 | 38904.5405 | 1 | 0 | 307.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5407 | 1 | 0 | 38904.5407 | 1 | 0 | 324.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5409 | 1 | 0 | 38904.5409 | 1 | 0 | 341.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5411 | 1 | 0 | 38904.5411 | 1 | 0 | 358 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5413 | 1 | 0 | 38904.5413 | 1 | 0 | 375 | 480 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5415 | 1 | 0 | 38904.5415 | 1 | 0 | 391.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5417 | 1 | 0 | 38904.5417 | 1 | 0 | 408.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5419 | 2 | 0 | 38904.5419 | 1 | 0 | 425.5 | 530.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128069 | 256238 | 128068.9988
38904.5421 | 1 | 0 | 38904.5421 | 1 | 0 | 442 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5423 | 1 | 0 | 38904.5423 | 1 | 0 | 458.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5425 | 1 | 0 | 38904.5425 | 1 | 0 | 475.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5427 | 1 | 0 | 38904.5427 | 1 | 0 | 492.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5428 | 1 | 0 | 38904.5429 | 1 | 0 | 509 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.543 | 1 | 0 | 38904.5431 | 1 | 0 | 526 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5432 | 1 | 0 | 38904.5433 | 1 | 0 | 542.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5434 | 1 | 0 | 38904.5434 | 1 | 0 | 559.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5436 | 1 | 0 | 38904.5436 | 1 | 0 | 576.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5438 | 1 | 0 | 38904.5438 | 1 | 0 | 593 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.544 | 1 | 0 | 38904.544 | 1 | 0 | 610 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5442 | 1 | 0 | 38904.5442 | 1 | 0 | 626.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5444 | 1 | 0 | 38904.5444 | 1 | 0 | 643.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5446 | 1 | 0 | 38904.5446 | 1 | 0 | 660.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5448 | 1 | 0 | 38904.5448 | 1 | 0 | 677 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.545 | 1 | 0 | 38904.545 | 1 | 0 | 694 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5452 | 1 | 0 | 38904.5452 | 1 | 0 | 710.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5454 | 1 | 0 | 38904.5454 | 1 | 0 | 727.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5456 | 1 | 0 | 38904.5456 | 1 | 0 | 744.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.5458 | 1 | 0 | 38904.5458 | 1 | 0 | 761 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256238 | 256238 | 256237.9994
38904.546 | 2122 | 0 | 38904.546 | 10 | 0 | 778 | 883 | 129.5482 | 0 | 0.6105 | 0 | 1.2955 | 0 | 0.006105 | 0 | 1.2955 | 0.006105 | 20.8002 | 25533.8 | 19.5047
38904.5462 | 2348 | 0 | 38904.5462 | 10 | 0 | 794.5 | 899.5 | 143.3455 | 0 | 0.6105 | 0 | 1.4335 | 0 | 0.006105 | 0 | 1.4335 | 0.006105 | 9.1729 | 25533.8 | 7.7395
38904.5464 | 2517 | 0 | 38904.5464 | 11 | 0 | 811.5 | 916.5 | 153.663 | 0 | 0.67155 | 0 | 1.5366 | 0 | 0.0067155 | 0 | 1.5366 | 0.0067155 | 1.8427 | 23203.4545 | 0.30604
38904.5466 | 2177 | 0 | 38904.5466 | 11 | 0 | 828.5 | 933.5 | 132.906 | 0 | 0.67155 | 0 | 1.3291 | 0 | 0.0067155 | 0 | 1.3291 | 0.0067155 | 17.7483 | 23203.4545 | 16.4192
38904.5467 | 2321 | 0 | 38904.5468 | 12 | 0 | 845 | 950 | 141.6972 | 0 | 0.7326 | 0 | 1.417 | 0 | 0.007326 | 0 | 1.417 | 0.007326 | 10.4429 | 21261.5 | 9.0259
38904.5469 | 1998 | 0 | 38904.547 | 11 | 0 | 862 | 967 | 121.978 | 0 | 0.67155 | 0 | 1.2198 | 0 | 0.0067155 | 0 | 1.2198 | 0.0067155 | 28.2973 | 23203.4545 | 27.0775
38904.5471 | 2234 | 0 | 38904.5471 | 12 | 0 | 878.5 | 983.5 | 136.3858 | 0 | 0.7326 | 0 | 1.3639 | 0 | 0.007326 | 0 | 1.3639 | 0.007326 | 14.744 | 21261.5 | 13.3801
38904.5473 | 2075 | 0 | 38904.5473 | 13 | 0 | 895.5 | 1000.5 | 126.6789 | 0 | 0.79365 | 0 | 1.2668 | 0 | 0.0079365 | 0 | 1.2668 | 0.0079365 | 23.5364 | 19618.3077 | 22.2696
38904.5475 | 2276 | 0 | 38904.5475 | 27 | 0 | 912.5 | 1017.5 | 138.9499 | 0 | 1.6484 | 0 | 1.3895 | 0 | 0.016484 | 0 | 1.3895 | 0.016484 | 12.6265 | 9394 | 11.237
38904.5477 | 2438 | 0 | 38904.5477 | 12 | 0 | 929 | 1034 | 148.84 | 0 | 0.7326 | 0 | 1.4884 | 0 | 0.007326 | 0 | 1.4884 | 0.007326 | 5.1427 | 21261.5 | 3.6543
38904.5479 | 2468 | 0 | 38904.5479 | 559 | 0 | 946 | 1051 | 150.6716 | 0 | 34.127 | 0 | 1.5067 | 0 | 0.34127 | 0 | 1.5067 | 0.34127 | 3.8647 | 358.5653 | 2.358
38904.5481 | 2093 | 0 | 38904.5481 | 27 | 0 | 962.5 | 1067.5 | 127.7778 | 0 | 1.6484 | 0 | 1.2778 | 0 | 0.016484 | 0 | 1.2778 | 0.016484 | 22.474 | 9394 | 21.1962
38904.5483 | 2123 | 0 | 38904.5483 | 99 | 0 | 979.5 | 1084.5 | 129.6093 | 0 | 6.044 | 0 | 1.2961 | 0 | 0.06044 | 0 | 1.2961 | 0.06044 | 20.7433 | 2489.2727 | 19.4472
38904.5485 | 2281 | 0 | 38904.5485 | 2374 | 1 | 996.5 | 1101.5 | 139.2552 | 0 | 144.9328 | 0.06105 | 1.3926 | 0 | 1.4493 | 0.0006105 | 1.3926 | 1.4487 | 12.3797 | 8.0228 | 10.9871
38904.5487 | 1942 | 0 | 38904.5487 | 2241 | 0 | 1013 | 1118 | 118.5592 | 0 | 136.8132 | 0 | 1.1856 | 0 | 1.3681 | 0 | 1.1856 | 1.3681 | 31.9969 | 14.3855 | 30.8113
38904.5489 | 2507 | 0 | 38904.5489 | 2203 | 0 | 1030 | 1135 | 153.0525 | 0 | 134.4933 | 0 | 1.5305 | 0 | 1.3449 | 0 | 1.5305 | 1.3449 | 2.2489 | 16.3586 | 0.71838
38904.5491 | 2448 | 0 | 38904.5491 | 2021 | 0 | 1046.5 | 1151.5 | 149.4505 | 0 | 123.3822 | 0 | 1.4945 | 0 | 1.2338 | 0 | 1.4945 | 1.2338 | 4.7132 | 26.8372 | 3.2187
38904.5493 | 2097 | 0 | 38904.5493 | 2078 | 0 | 1063.5 | 1168.5 | 128.022 | 0 | 126.862 | 0 | 1.2802 | 0 | 1.2686 | 0 | 1.2802 | 1.2686 | 22.2403 | 23.358 | 20.9601
38904.5495 | 2546 | 0 | 38904.5495 | 2059 | 0 | 1080.5 | 1185.5 | 155.4335 | 0 | 125.7021 | 0 | 1.5543 | 0 | 1.257 | 0 | 1.5543 | 1.257 | 0.68264 | 24.4964 | 0.8717
38904.5497 | 2101 | 0 | 38904.5497 | 2174 | 0 | 1097 | 1202 | 128.2662 | 0 | 132.7228 | 0 | 1.2827 | 0 | 1.3272 | 0 | 1.2827 | 1.3272 | 22.0076 | 17.9108 | 20.725
38904.5498 | 2425 | 0 | 38904.5499 | 1970 | 0 | 1114 | 1219 | 148.0464 | 0 | 120.2686 | 0 | 1.4805 | 0 | 1.2027 | 0 | 1.4805 | 1.2027 | 5.7064 | 30.1208 | 4.2259
38904.55 | 2053 | 0 | 38904.5501 | 1961 | 0 | 1130.5 | 1235.5 | 125.3358 | 0 | 119.7192 | 0 | 1.2534 | 0 | 1.1972 | 0 | 1.2534 | 1.1972 | 24.8602 | 30.718 | 23.6068
38904.5502 | 2073 | 0 | 38904.5503 | 2525 | 0 | 1147.5 | 1252.5 | 126.5568 | 0 | 154.1514 | 0 | 1.2656 | 0 | 1.5415 | 0 | 1.2656 | 1.5415 | 23.6556 | 1.52 | 22.39
38904.5504 | 2546 | 0 | 38904.5505 | 2170 | 0 | 1164.5 | 1269.5 | 155.4335 | 0 | 132.4786 | 0 | 1.5543 | 0 | 1.3248 | 0 | 1.5543 | 1.3248 | 0.68264 | 18.1281 | 0.8717
38904.5506 | 2231 | 0 | 38904.5506 | 2248 | 0 | 1181 | 1286 | 136.2027 | 0 | 137.2405 | 0 | 1.362 | 0 | 1.3724 | 0 | 1.362 | 1.3724 | 14.8983 | 14.0294 | 13.5362
38904.5508 | 2279 | 0 | 38904.5508 | 2547 | 0 | 1198 | 1303 | 139.1331 | 0 | 155.4945 | 0 | 1.3913 | 0 | 1.5549 | 0 | 1.3913 | 1.5549 | 12.4783 | 0.64311 | 11.0869
38904.551 | 2377 | 0 | 38904.551 | 2406 | 0 | 1214.5 | 1319.5 | 145.116 | 0 | 146.8864 | 0 | 1.4512 | 0 | 1.4689 | 0 | 1.4512 | 1.4689 | 7.841 | 6.5411 | 6.3898
38904.5512 | 2385 | 0 | 38904.5512 | 1952 | 0 | 1231.5 | 1336.5 | 145.6044 | 0 | 119.1697 | 0 | 1.456 | 0 | 1.1917 | 0 | 1.456 | 1.1917 | 7.4792 | 31.3207 | 6.0232
38904.5514 | 2015 | 0 | 38904.5514 | 2336 | 0 | 1248.5 | 1353.5 | 123.0159 | 0 | 142.6129 | 0 | 1.2302 | 0 | 1.4261 | 0 | 1.2302 | 1.4261 | 27.2149 | 9.7337 | 25.9847
38904.5516 | 2542 | 0 | 38904.5516 | 2482 | 0 | 1265 | 1370 | 155.1893 | 0 | 151.5263 | 0 | 1.5519 | 0 | 1.5153 | 0 | 1.5519 | 1.5153 | 0.84107 | 3.2788 | 0.71082
38904.5518 | 2521 | 0 | 38904.5518 | 2092 | 0 | 1282 | 1387 | 153.9072 | 0 | 127.7167 | 0 | 1.5391 | 0 | 1.2772 | 0 | 1.5391 | 1.2772 | 1.6811 | 22.5325 | 0.14201
38904.552 | 2397 | 0 | 38904.552 | 2292 | 0 | 1298.5 | 1403.5 | 146.337 | 0 | 139.9267 | 0 | 1.4634 | 0 | 1.3993 | 0 | 1.4634 | 1.3993 | 6.9412 | 11.8403 | 5.4778

## C1-4
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.5556 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38904.5358 | 1 | 0 | 38904.5358 | 1 | 0 | -98.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.536 | 1 | 0 | 38904.536 | 1 | 0 | -81.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5362 | 1 | 0 | 38904.5362 | 2 | 0 | -64.5 | 40.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256338 | 128119 | 256337.9994
38904.5364 | 1 | 0 | 38904.5364 | 1 | 0 | -48 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5366 | 1 | 0 | 38904.5366 | 1 | 0 | -31 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5368 | 1 | 0 | 38904.5368 | 1 | 0 | -14.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.537 | 1 | 0 | 38904.537 | 1 | 0 | 2.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5372 | 1 | 0 | 38904.5372 | 1 | 0 | 19.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5374 | 1 | 0 | 38904.5374 | 1 | 0 | 36 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5376 | 1 | 0 | 38904.5376 | 1 | 0 | 52.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5378 | 1 | 0 | 38904.5378 | 1 | 0 | 69.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.538 | 1 | 0 | 38904.538 | 1 | 0 | 86.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5382 | 1 | 0 | 38904.5382 | 1 | 0 | 103.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5383 | 1 | 0 | 38904.5384 | 1 | 0 | 120 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5385 | 1 | 0 | 38904.5386 | 1 | 0 | 137 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5387 | 2 | 0 | 38904.5387 | 1 | 0 | 153.5 | 258.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128119 | 256338 | 128118.9988
38904.5389 | 1 | 0 | 38904.5389 | 1 | 0 | 170.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5391 | 1 | 0 | 38904.5391 | 1 | 0 | 187 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5393 | 1 | 0 | 38904.5393 | 1 | 0 | 204 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5395 | 1 | 0 | 38904.5395 | 1 | 0 | 220.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5397 | 1 | 0 | 38904.5397 | 1 | 0 | 237.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5399 | 1 | 0 | 38904.5399 | 1 | 0 | 254.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5401 | 1 | 0 | 38904.5401 | 1 | 0 | 271.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5403 | 1 | 0 | 38904.5403 | 1 | 0 | 288 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5405 | 1 | 0 | 38904.5405 | 1 | 0 | 305 | 410 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5407 | 1 | 0 | 38904.5407 | 1 | 0 | 321.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5409 | 1 | 0 | 38904.5409 | 1 | 0 | 338.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5411 | 1 | 0 | 38904.5411 | 1 | 0 | 355.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5413 | 1 | 0 | 38904.5413 | 1 | 0 | 372 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5415 | 1 | 0 | 38904.5415 | 1 | 0 | 388.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5417 | 1 | 0 | 38904.5417 | 1 | 0 | 405.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5419 | 1 | 0 | 38904.5419 | 1 | 0 | 422.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.542 | 1 | 0 | 38904.5421 | 1 | 0 | 439.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5422 | 1 | 0 | 38904.5423 | 1 | 0 | 456 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5424 | 1 | 0 | 38904.5425 | 1 | 0 | 473 | 578 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5426 | 1 | 0 | 38904.5426 | 1 | 0 | 489.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5428 | 1 | 0 | 38904.5428 | 1 | 0 | 506.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.543 | 1 | 0 | 38904.543 | 1 | 0 | 523 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5432 | 1 | 0 | 38904.5432 | 1 | 0 | 540 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5434 | 1 | 0 | 38904.5434 | 2 | 0 | 556.5 | 661.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256338 | 128119 | 256337.9994
38904.5436 | 1 | 0 | 38904.5436 | 1 | 0 | 573.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5438 | 1 | 0 | 38904.5438 | 1 | 0 | 590.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.544 | 1 | 0 | 38904.544 | 1 | 0 | 607 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5442 | 1 | 0 | 38904.5442 | 1 | 0 | 624 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5444 | 1 | 0 | 38904.5444 | 1 | 0 | 640.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5446 | 1 | 0 | 38904.5446 | 1 | 0 | 657.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5448 | 1 | 0 | 38904.5448 | 1 | 0 | 674.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.545 | 1 | 0 | 38904.545 | 1 | 0 | 691 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5452 | 1 | 0 | 38904.5452 | 1 | 0 | 708 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5453 | 1 | 0 | 38904.5454 | 1 | 0 | 724.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5455 | 1 | 0 | 38904.5456 | 1 | 0 | 741.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5457 | 1 | 0 | 38904.5458 | 1 | 0 | 758.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38904.5459 | 3 | 0 | 38904.5459 | 2 | 0 | 775 | 880 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 85379.3333 | 128119 | 85379.3315
38904.5461 | 6 | 0 | 38904.5461 | 5 | 0 | 792 | 897 | 0.3663 | 0 | 0.30525 | 0 | 0.003663 | 0 | 0.0030525 | 0 | 0.003663 | 0.0030525 | 42639.6667 | 51187.6 | 42639.663
38904.5463 | 7 | 0 | 38904.5463 | 6 | 0 | 808.5 | 913.5 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 36534 | 42639.6667 | 36533.9957
38904.5465 | 8 | 0 | 38904.5465 | 7 | 0 | 825.5 | 930.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31954.75 | 36534 | 31954.7451
38904.5467 | 8 | 0 | 38904.5467 | 8 | 0 | 842.5 | 947.5 | 0.4884 | 0 | 0.4884 | 0 | 0.004884 | 0 | 0.004884 | 0 | 0.004884 | 0.004884 | 31954.75 | 31954.75 | 31954.7451
38904.5469 | 8 | 0 | 38904.5469 | 7 | 0 | 859 | 964 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31954.75 | 36534 | 31954.7451
38904.5471 | 8 | 0 | 38904.5471 | 7 | 0 | 876 | 981 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31954.75 | 36534 | 31954.7451
38904.5473 | 8 | 0 | 38904.5473 | 8 | 0 | 892.5 | 997.5 | 0.4884 | 0 | 0.4884 | 0 | 0.004884 | 0 | 0.004884 | 0 | 0.004884 | 0.004884 | 31954.75 | 31954.75 | 31954.7451
38904.5475 | 11 | 0 | 38904.5475 | 7 | 0 | 909.5 | 1014.5 | 0.67155 | 0 | 0.42735 | 0 | 0.0067155 | 0 | 0.0042735 | 0 | 0.0067155 | 0.0042735 | 23212.5455 | 36534 | 23212.5387
38904.5477 | 8 | 0 | 38904.5477 | 7 | 0 | 926.5 | 1031.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31954.75 | 36534 | 31954.7451
38904.5479 | 9 | 0 | 38904.5479 | 8 | 0 | 943 | 1048 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 28393.1111 | 31954.75 | 28393.1056
38904.5481 | 9 | 0 | 38904.5481 | 8 | 0 | 960 | 1065 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 28393.1111 | 31954.75 | 28393.1056
38904.5483 | 22 | 7 | 38904.5483 | 163 | 121 | 976.5 | 1081.5 | 1.3431 | 0.42735 | 9.9512 | 7.3871 | 0.013431 | 0.0042735 | 0.099512 | 0.073871 | 0.0091575 | 0.025641 | 17086.3066 | 5815.6298 | 35607.4428
38904.5485 | 2102 | 0 | 38904.5485 | 2306 | 0 | 993.5 | 1098.5 | 128.3272 | 0 | 140.7814 | 0 | 1.2833 | 0 | 1.4078 | 0 | 1.2833 | 1.4078 | 21.9971 | 11.2047 | 20.7139
38904.5487 | 2012 | 0 | 38904.5487 | 1943 | 0 | 1010.5 | 1115.5 | 122.8327 | 0 | 118.6203 | 0 | 1.2283 | 0 | 1.1862 | 0 | 1.2283 | 1.1862 | 27.4543 | 31.9804 | 26.2259
38904.5488 | 2150 | 0 | 38904.5489 | 2517 | 0 | 1027 | 1132 | 131.2576 | 0 | 153.663 | 0 | 1.3126 | 0 | 1.5366 | 0 | 1.3126 | 1.5366 | 19.2735 | 1.8824 | 17.9609
38904.549 | 1987 | 0 | 38904.5491 | 2365 | 0 | 1044 | 1149 | 121.3065 | 0 | 144.3834 | 0 | 1.2131 | 0 | 1.4438 | 0 | 1.2131 | 1.4438 | 29.0579 | 8.4304 | 27.8448
38904.5492 | 2499 | 0 | 38904.5492 | 2522 | 0 | 1060.5 | 1165.5 | 152.5641 | 0 | 153.9683 | 0 | 1.5256 | 0 | 1.5397 | 0 | 1.5256 | 1.5397 | 2.6162 | 1.6804 | 1.0906
38904.5494 | 2413 | 0 | 38904.5494 | 2406 | 0 | 1077.5 | 1182.5 | 147.3138 | 0 | 146.8864 | 0 | 1.4731 | 0 | 1.4689 | 0 | 1.4731 | 1.4689 | 6.2735 | 6.5827 | 4.8004
38904.5496 | 2548 | 0 |  | 2345 | 0 | 1094 | 1199 | 155.5556 | 0 | 143.1624 | 0 | 1.5556 | 0 | 1.4316 | 0 | 1.5556 | 1.4316 | 0.64286 | 9.3552 | 0.9127
38904.5498 | 1970 | 0 | 38904.5498 | 2283 | 0 | 1111 | 1216 | 120.2686 | 0 | 139.3773 | 0 | 1.2027 | 0 | 1.3938 | 0 | 1.2027 | 1.3938 | 30.1716 | 12.325 | 28.9689
38904.55 | 2521 | 0 | 38904.55 | 2392 | 0 | 1128 | 1233 | 153.9072 | 0 | 146.0317 | 0 | 1.5391 | 0 | 1.4603 | 0 | 1.5391 | 1.4603 | 1.7207 | 7.2065 | 0.18167
38904.5502 | 2291 | 0 | 38904.5502 | 2067 | 0 | 1144.5 | 1249.5 | 139.8657 | 0 | 126.1905 | 0 | 1.3987 | 0 | 1.2619 | 0 | 1.3987 | 1.2619 | 11.9328 | 24.0629 | 10.5341
38904.5504 | 2160 | 0 | 38904.5504 | 2376 | 0 | 1161.5 | 1266.5 | 131.8681 | 0 | 145.0549 | 0 | 1.3187 | 0 | 1.4505 | 0 | 1.3187 | 1.4505 | 18.7213 | 7.9285 | 17.4026
38904.5506 | 2054 | 0 | 38904.5506 | 2344 | 0 | 1178.5 | 1283.5 | 125.3968 | 0 | 143.1013 | 0 | 1.254 | 0 | 1.431 | 0 | 1.254 | 1.431 | 24.8481 | 9.4019 | 23.5941
38904.5508 | 1989 | 0 | 38904.5508 | 2237 | 0 | 1195 | 1300 | 121.4286 | 0 | 136.569 | 0 | 1.2143 | 0 | 1.3657 | 0 | 1.2143 | 1.3657 | 28.9281 | 14.6348 | 27.7138
38904.551 | 2463 | 0 | 38904.551 | 2304 | 0 | 1212 | 1317 | 150.3663 | 0 | 140.6593 | 0 | 1.5037 | 0 | 1.4066 | 0 | 1.5037 | 1.4066 | 4.1161 | 11.3012 | 2.6125
38904.5512 | 2359 | 1 | 38904.5512 | 2475 | 0 | 1228.5 | 1333.5 | 144.0171 | 0.06105 | 151.0989 | 0 | 1.4402 | 0.0006105 | 1.511 | 0 | 1.4396 | 1.511 | 8.8134 | 3.6113 | 712.3548
38904.5514 | 2037 | 0 | 38904.5514 | 2381 | 0 | 1245.5 | 1350.5 | 124.359 | 0 | 145.3602 | 0 | 1.2436 | 0 | 1.4536 | 0 | 1.2436 | 1.4536 | 25.89 | 7.7018 | 24.6464
38904.5516 | 2084 | 0 | 38904.5516 | 2399 | 0 | 1262.5 | 1367.5 | 127.2283 | 0 | 146.4591 | 0 | 1.2723 | 0 | 1.4646 | 0 | 1.2723 | 1.4646 | 23.0509 | 6.8937 | 21.7786
38904.5518 | 2088 | 0 | 38904.5518 | 2146 | 0 | 1279 | 1384 | 127.4725 | 0 | 131.0134 | 0 | 1.2747 | 0 | 1.3101 | 0 | 1.2747 | 1.3101 | 22.8151 | 19.4958 | 21.5404
38904.552 | 2530 | 0 | 38904.552 | 2181 | 0 | 1296 | 1401 | 154.4567 | 0 | 133.1502 | 0 | 1.5446 | 0 | 1.3315 | 0 | 1.5446 | 1.3315 | 1.3589 | 17.5782 | 0.18567

## C1-3
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.2503 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38904.5358 | 1 | 0 | 38904.5358 | 1 | 0 | -101 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.536 | 1 | 0 | 38904.536 | 1 | 0 | -84.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5362 | 1 | 0 | 38904.5362 | 1 | 0 | -67.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5364 | 1 | 0 | 38904.5364 | 1 | 0 | -50.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5366 | 1 | 0 | 38904.5366 | 1 | 0 | -34 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5368 | 1 | 0 | 38904.5368 | 1 | 0 | -17 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.537 | 1 | 0 | 38904.537 | 1 | 0 | -0.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5372 | 1 | 0 | 38904.5372 | 1 | 0 | 16.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5373 | 1 | 0 | 38904.5374 | 1 | 0 | 33.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5375 | 1 | 0 | 38904.5376 | 2 | 0 | 50 | 155 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255838 | 127869 | 255837.9994
38904.5377 | 1 | 0 | 38904.5378 | 1 | 0 | 67 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5379 | 1 | 0 | 38904.5379 | 1 | 0 | 83.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5381 | 1 | 0 | 38904.5381 | 1 | 0 | 100.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5383 | 1 | 0 | 38904.5383 | 1 | 0 | 117.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5385 | 1 | 0 | 38904.5385 | 1 | 0 | 134 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5387 | 1 | 0 | 38904.5387 | 1 | 0 | 151 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5389 | 1 | 0 | 38904.5389 | 1 | 0 | 167.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5391 | 1 | 0 | 38904.5391 | 1 | 0 | 184.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5393 | 1 | 0 | 38904.5393 | 1 | 0 | 201.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5395 | 1 | 0 | 38904.5395 | 1 | 0 | 218 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5397 | 1 | 0 | 38904.5397 | 1 | 0 | 234.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5399 | 1 | 0 | 38904.5399 | 1 | 0 | 251.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5401 | 1 | 0 | 38904.5401 | 1 | 0 | 268.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5403 | 1 | 0 | 38904.5403 | 1 | 0 | 285 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5405 | 1 | 0 | 38904.5405 | 1 | 0 | 302 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5406 | 1 | 0 | 38904.5407 | 1 | 0 | 319 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5408 | 1 | 0 | 38904.5409 | 1 | 0 | 335.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.541 | 1 | 0 | 38904.5411 | 1 | 0 | 352.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5412 | 1 | 0 | 38904.5413 | 1 | 0 | 369 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5414 | 1 | 0 | 38904.5414 | 1 | 0 | 386 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5416 | 1 | 0 | 38904.5416 | 1 | 0 | 403 | 508 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5418 | 1 | 0 | 38904.5418 | 1 | 0 | 419.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.542 | 1 | 0 | 38904.542 | 1 | 0 | 436.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5422 | 1 | 0 | 38904.5422 | 1 | 0 | 453.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5424 | 1 | 0 | 38904.5424 | 1 | 0 | 470 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5426 | 1 | 0 | 38904.5426 | 1 | 0 | 487 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5428 | 1 | 0 | 38904.5428 | 1 | 0 | 503.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.543 | 1 | 0 | 38904.543 | 2 | 0 | 520.5 | 625.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255838 | 127869 | 255837.9994
38904.5432 | 1 | 0 | 38904.5432 | 1 | 0 | 537.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5434 | 1 | 0 | 38904.5434 | 1 | 0 | 554 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5436 | 1 | 0 | 38904.5436 | 1 | 0 | 570.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5438 | 1 | 0 | 38904.5438 | 1 | 0 | 587.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.544 | 1 | 0 | 38904.544 | 2 | 0 | 604.5 | 709.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255838 | 127869 | 255837.9994
38904.5441 | 1 | 0 | 38904.5442 | 1 | 0 | 621 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5443 | 1 | 0 | 38904.5444 | 1 | 0 | 638 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5445 | 1 | 0 | 38904.5445 | 1 | 0 | 654.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5447 | 1 | 0 | 38904.5447 | 1 | 0 | 671.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5449 | 1 | 0 | 38904.5449 | 1 | 0 | 688.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5451 | 1 | 0 | 38904.5451 | 1 | 0 | 705 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5453 | 1 | 0 | 38904.5453 | 1 | 0 | 722 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5455 | 1 | 0 | 38904.5455 | 1 | 0 | 738.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5457 | 1 | 0 | 38904.5457 | 1 | 0 | 755.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38904.5459 | 8 | 0 | 38904.5459 | 4 | 0 | 772.5 | 877.5 | 0.4884 | 0 | 0.2442 | 0 | 0.004884 | 0 | 0.002442 | 0 | 0.004884 | 0.002442 | 31892.25 | 63884.5 | 31892.2451
38904.5461 | 11 | 0 | 38904.5461 | 9 | 0 | 789 | 894 | 0.67155 | 0 | 0.54945 | 0 | 0.0067155 | 0 | 0.0054945 | 0 | 0.0067155 | 0.0054945 | 23167.0909 | 28337.5556 | 23167.0842
38904.5463 | 10 | 0 | 38904.5463 | 10 | 0 | 806 | 911 | 0.6105 | 0 | 0.6105 | 0 | 0.006105 | 0 | 0.006105 | 0 | 0.006105 | 0.006105 | 25493.8 | 25493.8 | 25493.7939
38904.5465 | 10 | 0 | 38904.5465 | 9 | 0 | 822.5 | 927.5 | 0.6105 | 0 | 0.54945 | 0 | 0.006105 | 0 | 0.0054945 | 0 | 0.006105 | 0.0054945 | 25493.8 | 28337.5556 | 25493.7939
38904.5467 | 10 | 0 | 38904.5467 | 10 | 0 | 839.5 | 944.5 | 0.6105 | 0 | 0.6105 | 0 | 0.006105 | 0 | 0.006105 | 0 | 0.006105 | 0.006105 | 25493.8 | 25493.8 | 25493.7939
38904.5469 | 11 | 0 | 38904.5469 | 10 | 0 | 856.5 | 961.5 | 0.67155 | 0 | 0.6105 | 0 | 0.0067155 | 0 | 0.006105 | 0 | 0.0067155 | 0.006105 | 23167.0909 | 25493.8 | 23167.0842
38904.5471 | 11 | 0 | 38904.5471 | 9 | 0 | 873 | 978 | 0.67155 | 0 | 0.54945 | 0 | 0.0067155 | 0 | 0.0054945 | 0 | 0.0067155 | 0.0054945 | 23167.0909 | 28337.5556 | 23167.0842
38904.5473 | 12 | 0 | 38904.5473 | 10 | 0 | 890 | 995 | 0.7326 | 0 | 0.6105 | 0 | 0.007326 | 0 | 0.006105 | 0 | 0.007326 | 0.006105 | 21228.1667 | 25493.8 | 21228.1593
38904.5475 | 13 | 0 | 38904.5475 | 9 | 0 | 906.5 | 1011.5 | 0.79365 | 0 | 0.54945 | 0 | 0.0079365 | 0 | 0.0054945 | 0 | 0.0079365 | 0.0054945 | 19587.5385 | 28337.5556 | 19587.5305
38904.5477 | 11 | 0 | 38904.5477 | 10 | 0 | 923.5 | 1028.5 | 0.67155 | 0 | 0.6105 | 0 | 0.0067155 | 0 | 0.006105 | 0 | 0.0067155 | 0.006105 | 23167.0909 | 25493.8 | 23167.0842
38904.5478 | 11 | 0 | 38904.5479 | 48 | 0 | 940.5 | 1045.5 | 0.67155 | 0 | 2.9304 | 0 | 0.0067155 | 0 | 0.029304 | 0 | 0.0067155 | 0.029304 | 23167.0909 | 5232.0417 | 23167.0842
38904.548 | 12 | 0 | 38904.5481 | 510 | 0 | 957 | 1062 | 0.7326 | 0 | 31.1355 | 0 | 0.007326 | 0 | 0.31136 | 0 | 0.007326 | 0.31136 | 21228.1667 | 401.8392 | 21228.1593
38904.5482 | 10 | 0 | 38904.5483 | 83 | 0 | 974 | 1079 | 0.6105 | 0 | 5.0672 | 0 | 0.006105 | 0 | 0.050672 | 0 | 0.006105 | 0.050672 | 25493.8 | 2983.5904 | 25493.7939
38904.5484 | 2517 | 0 | 38904.5484 | 1952 | 0 | 990.5 | 1095.5 | 153.663 | 0 | 119.1697 | 0 | 1.5366 | 0 | 1.1917 | 0 | 1.5366 | 1.1917 | 1.6838 | 31.1158 | 0.14712
38904.5486 | 2437 | 0 | 38904.5486 | 2430 | 0 | 1007.5 | 1112.5 | 148.779 | 0 | 148.3516 | 0 | 1.4878 | 0 | 1.4835 | 0 | 1.4878 | 1.4835 | 5.0217 | 5.3243 | 3.534
38904.5488 | 2424 | 0 | 38904.5488 | 2195 | 0 | 1024.5 | 1129.5 | 147.9853 | 0 | 134.0049 | 0 | 1.4799 | 0 | 1.34 | 0 | 1.4799 | 1.34 | 5.585 | 16.6005 | 4.1051
38904.549 | 2516 | 0 | 38904.549 | 2054 | 0 | 1041 | 1146 | 153.602 | 0 | 125.3968 | 0 | 1.536 | 0 | 1.254 | 0 | 1.536 | 1.254 | 1.7242 | 24.6047 | 0.18815
38904.5492 | 2146 | 0 | 38904.5492 | 2511 | 0 | 1058 | 1163 | 131.0134 | 0 | 153.2967 | 0 | 1.3101 | 0 | 1.533 | 0 | 1.3101 | 1.533 | 19.2628 | 1.9267 | 17.9527
38904.5494 | 1984 | 0 | 38904.5494 | 1949 | 0 | 1074.5 | 1179.5 | 121.1233 | 0 | 118.9866 | 0 | 1.2112 | 0 | 1.1899 | 0 | 1.2112 | 1.1899 | 29.001 | 31.3176 | 27.7898
38904.5496 | 2184 | 0 | 38904.5496 | 1983 | 0 | 1091.5 | 1196.5 | 133.3333 | 0 | 121.0623 | 0 | 1.3333 | 0 | 1.2106 | 0 | 1.3333 | 1.2106 | 17.1877 | 29.0661 | 15.8544
38904.5498 | 2483 | 0 | 38904.5498 | 2019 | 0 | 1108.5 | 1213.5 | 151.5873 | 0 | 123.2601 | 0 | 1.5159 | 0 | 1.2326 | 0 | 1.5159 | 1.2326 | 3.0761 | 26.7647 | 1.5602
38904.55 | 2140 | 0 | 38904.55 | 2048 | 0 | 1125 | 1230 | 130.6471 | 0 | 125.0305 | 0 | 1.3065 | 0 | 1.2503 | 0 | 1.3065 | 1.2503 | 19.5972 | 24.9697 | 18.2907
38904.5502 | 2226 | 0 | 38904.5502 | 2535 | 0 | 1142 | 1247 | 135.8974 | 0 | 154.7619 | 0 | 1.359 | 0 | 1.5476 | 0 | 1.359 | 1.5476 | 14.9766 | 0.96174 | 13.6177
38904.5504 | 2441 | 0 | 38904.5504 | 2074 | 0 | 1158.5 | 1263.5 | 149.0232 | 0 | 126.6178 | 0 | 1.4902 | 0 | 1.2662 | 0 | 1.4902 | 1.2662 | 4.8497 | 23.4031 | 3.3594
38904.5506 | 2158 | 0 | 38904.5506 | 2133 | 0 | 1175.5 | 1280.5 | 131.746 | 0 | 130.2198 | 0 | 1.3175 | 0 | 1.3022 | 0 | 1.3175 | 1.3022 | 18.5996 | 19.9897 | 17.2822
38904.5508 | 2405 | 0 | 38904.5508 | 2473 | 0 | 1192.5 | 1297.5 | 146.8254 | 0 | 150.9768 | 0 | 1.4683 | 0 | 1.5098 | 0 | 1.4683 | 1.5098 | 6.4191 | 3.4929 | 4.9509
38904.5509 | 1955 | 0 | 38904.551 | 2397 | 0 | 1209 | 1314 | 119.3529 | 0 | 146.337 | 0 | 1.1935 | 0 | 1.4634 | 0 | 1.1935 | 1.4634 | 30.9146 | 6.7743 | 29.721
38904.5511 | 2034 | 0 | 38904.5512 | 2011 | 0 | 1226 | 1331 | 124.1758 | 0 | 122.7717 | 0 | 1.2418 | 0 | 1.2277 | 0 | 1.2418 | 1.2277 | 25.8299 | 27.269 | 24.5881
38904.5513 | 2431 | 0 | 38904.5514 | 2421 | 0 | 1242.5 | 1347.5 | 148.4127 | 0 | 147.8022 | 0 | 1.4841 | 0 | 1.478 | 0 | 1.4841 | 1.478 | 5.281 | 5.7158 | 3.7968
38904.5515 | 2493 | 0 | 38904.5516 | 1989 | 0 | 1259.5 | 1364.5 | 152.1978 | 0 | 121.4286 | 0 | 1.522 | 0 | 1.2143 | 0 | 1.522 | 1.2143 | 2.6627 | 28.6767 | 1.1407
38904.5517 | 2077 | 0 | 38904.5517 | 2047 | 0 | 1276.5 | 1381.5 | 126.801 | 0 | 124.9695 | 0 | 1.268 | 0 | 1.2497 | 0 | 1.268 | 1.2497 | 23.2248 | 25.0308 | 21.9568
38904.5519 | 2543 | 0 | 38904.5519 | 2466 | 0 | 1293 | 1398 | 155.2503 | 0 | 150.5495 | 0 | 1.5525 | 0 | 1.5055 | 0 | 1.5525 | 1.5055 | 0.64412 | 3.7867 | 0.90838

## C1-2
Penlight Test 6 |  |  | 2006-07-06 | 12:53 |  | Vs = |  | 156.4335 |  | R = | 100
PVC | 3-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38904.5358 | 1 | 0 | 38904.5358 | 1 | 0 | -104 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5359 | 1 | 0 | 38904.536 | 1 | 0 | -87 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5361 | 1 | 0 | 38904.5362 | 1 | 0 | -70.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5363 | 1 | 0 | 38904.5364 | 1 | 0 | -53.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5365 | 1 | 0 | 38904.5366 | 1 | 0 | -36.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5367 | 1 | 0 | 38904.5367 | 1 | 0 | -20 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5369 | 1 | 0 | 38904.5369 | 1 | 0 | -3 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5371 | 1 | 0 | 38904.5371 | 1 | 0 | 13.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5373 | 1 | 0 | 38904.5373 | 1 | 0 | 30.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5375 | 2 | 0 | 38904.5375 | 2 | 0 | 47.5 | 152.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 128018.9988
38904.5377 | 1 | 0 | 38904.5377 | 1 | 0 | 64 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5379 | 1 | 0 | 38904.5379 | 1 | 0 | 80.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5381 | 1 | 0 | 38904.5381 | 1 | 0 | 97.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5383 | 1 | 1 | 38904.5383 | 1 | 0 | 114.5 | 219.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38904.5385 | 1 | 0 | 38904.5385 | 1 | 0 | 131.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5387 | 1 | 0 | 38904.5387 | 1 | 0 | 148 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5389 | 1 | 1 | 38904.5389 | 1 | 0 | 165 | 270 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38904.5391 | 1 | 0 | 38904.5391 | 1 | 0 | 181.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5393 | 1 | 0 | 38904.5393 | 1 | 0 | 198.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5395 | 1 | 0 | 38904.5395 | 1 | 0 | 215.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5396 | 1 | 0 | 38904.5397 | 1 | 0 | 232 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5398 | 1 | 0 | 38904.5399 | 1 | 0 | 249 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.54 | 1 | 0 | 38904.54 | 1 | 0 | 265.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5402 | 1 | 0 | 38904.5402 | 1 | 0 | 282.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5404 | 1 | 0 | 38904.5404 | 1 | 0 | 299 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5406 | 1 | 0 | 38904.5406 | 1 | 0 | 316 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5408 | 1 | 1 | 38904.5408 | 1 | 0 | 333 | 438 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38904.541 | 1 | 0 | 38904.541 | 1 | 0 | 349.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5412 | 1 | 0 | 38904.5412 | 1 | 0 | 366.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5414 | 1 | 0 | 38904.5414 | 1 | 0 | 383 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5416 | 1 | 0 | 38904.5416 | 1 | 0 | 400 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5418 | 1 | 0 | 38904.5418 | 1 | 0 | 416.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.542 | 1 | 0 | 38904.542 | 1 | 0 | 433.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5422 | 1 | 0 | 38904.5422 | 1 | 0 | 450.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5424 | 1 | 0 | 38904.5424 | 1 | 0 | 467 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5426 | 1 | 0 | 38904.5426 | 1 | 0 | 484 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5428 | 1 | 0 | 38904.5428 | 1 | 0 | 500.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.543 | 1 | 0 | 38904.543 | 1 | 0 | 517.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5431 | 1 | 0 | 38904.5432 | 1 | 0 | 534.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5433 | 1 | 0 | 38904.5434 | 1 | 0 | 551 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5435 | 1 | 0 | 38904.5436 | 1 | 0 | 568 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5437 | 1 | 0 | 38904.5437 | 1 | 0 | 584.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5439 | 1 | 0 | 38904.5439 | 1 | 0 | 601.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5441 | 1 | 0 | 38904.5441 | 1 | 0 | 618.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5443 | 1 | 0 | 38904.5443 | 1 | 0 | 635 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5445 | 1 | 0 | 38904.5445 | 1 | 0 | 652 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5447 | 1 | 0 | 38904.5447 | 1 | 0 | 668.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5449 | 1 | 0 | 38904.5449 | 1 | 0 | 685.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5451 | 1 | 0 | 38904.5451 | 1 | 0 | 702.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5453 | 1 | 0 | 38904.5453 | 1 | 0 | 719 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5455 | 1 | 0 | 38904.5455 | 1 | 0 | 736 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5457 | 1 | 0 | 38904.5457 | 1 | 0 | 752.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38904.5459 | 1 | 0 | 38904.5459 | 2085 | 0 | 769.5 | 874.5 | 0.06105 | 0 | 127.2894 | 0 | 0.0006105 | 0 | 1.2729 | 0 | 0.0006105 | 1.2729 | 256138 | 22.8959 | 256137.9994
38904.5461 | 5 | 0 | 38904.5461 | 2538 | 0 | 786.5 | 891.5 | 0.30525 | 0 | 154.9451 | 0 | 0.0030525 | 0 | 1.5495 | 0 | 0.0030525 | 1.5495 | 51147.6 | 0.9606 | 51147.5969
38904.5462 | 8 | 0 | 38904.5463 | 1960 | 0 | 803 | 908 | 0.4884 | 0 | 119.6581 | 0 | 0.004884 | 0 | 1.1966 | 0 | 0.004884 | 1.1966 | 31929.75 | 30.7337 | 31929.7451
38904.5464 | 8 | 0 | 38904.5465 | 2244 | 0 | 820 | 925 | 0.4884 | 0 | 136.9963 | 0 | 0.004884 | 0 | 1.37 | 0 | 0.004884 | 1.37 | 31929.75 | 14.1881 | 31929.7451
38904.5466 | 8 | 0 | 38904.5467 | 1951 | 0 | 836.5 | 941.5 | 0.4884 | 0 | 119.1087 | 0 | 0.004884 | 0 | 1.1911 | 0 | 0.004884 | 1.1911 | 31929.75 | 31.3368 | 31929.7451
38904.5468 | 7 | 0 | 38904.5469 | 2480 | 0 | 853.5 | 958.5 | 0.42735 | 0 | 151.4042 | 0 | 0.0042735 | 0 | 1.514 | 0 | 0.0042735 | 1.514 | 36505.4286 | 3.3218 | 36505.4243
38904.547 | 8 | 0 | 38904.547 | 2152 | 0 | 870.5 | 975.5 | 0.4884 | 0 | 131.3797 | 0 | 0.004884 | 0 | 1.3138 | 0 | 0.004884 | 1.3138 | 31929.75 | 19.0697 | 31929.7451
38904.5472 | 8 | 0 | 38904.5472 | 2152 | 0 | 887 | 992 | 0.4884 | 0 | 131.3797 | 0 | 0.004884 | 0 | 1.3138 | 0 | 0.004884 | 1.3138 | 31929.75 | 19.0697 | 31929.7451
38904.5474 | 8 | 0 | 38904.5474 | 2309 | 0 | 904 | 1009 | 0.4884 | 0 | 140.9646 | 0 | 0.004884 | 0 | 1.4096 | 0 | 0.004884 | 1.4096 | 31929.75 | 10.9736 | 31929.7451
38904.5476 | 9 | 0 | 38904.5476 | 2384 | 0 | 920.5 | 1025.5 | 0.54945 | 0 | 145.5433 | 0 | 0.0054945 | 0 | 1.4554 | 0 | 0.0054945 | 1.4554 | 28370.8889 | 7.4824 | 28370.8834
38904.5478 | 9 | 0 | 38904.5478 | 2503 | 0 | 937.5 | 1042.5 | 0.54945 | 0 | 152.8083 | 0 | 0.0054945 | 0 | 1.5281 | 0 | 0.0054945 | 1.5281 | 28370.8889 | 2.3724 | 28370.8834
38904.548 | 9 | 0 | 38904.548 | 2271 | 0 | 954.5 | 1059.5 | 0.54945 | 0 | 138.6447 | 0 | 0.0054945 | 0 | 1.3864 | 0 | 0.0054945 | 1.3864 | 28370.8889 | 12.8305 | 28370.8834
38904.5482 | 9 | 0 | 38904.5482 | 2200 | 0 | 971 | 1076 | 0.54945 | 0 | 134.3101 | 0 | 0.0054945 | 0 | 1.3431 | 0 | 0.0054945 | 1.3431 | 28370.8889 | 16.4718 | 28370.8834
38904.5484 | 2152 | 0 | 38904.5484 | 2322 | 0 | 988 | 1093 | 131.3797 | 0 | 141.7582 | 0 | 1.3138 | 0 | 1.4176 | 0 | 1.3138 | 1.4176 | 19.0697 | 10.3523 | 17.7559
38904.5486 | 2499 | 0 | 38904.5486 | 2461 | 0 | 1004.5 | 1109.5 | 152.5641 | 0 | 150.2442 | 0 | 1.5256 | 0 | 1.5024 | 0 | 1.5256 | 1.5024 | 2.5362 | 4.1195 | 1.0106
38904.5488 | 2247 | 0 | 38904.5488 | 2508 | 0 | 1021.5 | 1126.5 | 137.1795 | 0 | 153.1136 | 0 | 1.3718 | 0 | 1.5311 | 0 | 1.3718 | 1.5311 | 14.0356 | 2.1683 | 12.6638
38904.549 | 2524 | 0 | 38904.549 | 2538 | 0 | 1038.5 | 1143.5 | 154.0904 | 0 | 154.9451 | 0 | 1.5409 | 0 | 1.5495 | 0 | 1.5409 | 1.5495 | 1.5206 | 0.9606 | 0.020301
38904.5492 | 2478 | 0 | 38904.5492 | 2175 | 0 | 1055 | 1160 | 151.2821 | 0 | 132.7839 | 0 | 1.5128 | 0 | 1.3278 | 0 | 1.5128 | 1.3278 | 3.4052 | 17.8106 | 1.8923
38904.5494 | 2429 | 0 | 38904.5494 | 2546 | 0 | 1072 | 1177 | 148.2906 | 0 | 155.4335 | 0 | 1.4829 | 0 | 1.5543 | 0 | 1.4829 | 1.5543 | 5.4911 | 0.64336 | 4.0082
38904.5496 | 2411 | 0 | 38904.5496 | 2122 | 0 | 1088.5 | 1193.5 | 147.1917 | 0 | 129.5482 | 0 | 1.4719 | 0 | 1.2955 | 0 | 1.4719 | 1.2955 | 6.2787 | 20.7531 | 4.8068
38904.5498 | 2222 | 0 | 38904.5498 | 2505 | 0 | 1105.5 | 1210.5 | 135.6532 | 0 | 152.9304 | 0 | 1.3565 | 0 | 1.5293 | 0 | 1.3565 | 1.5293 | 15.3186 | 2.2906 | 13.9621
38904.55 | 2525 | 0 | 38904.55 | 2524 | 0 | 1122.5 | 1227.5 | 154.1514 | 0 | 154.0904 | 0 | 1.5415 | 0 | 1.5409 | 0 | 1.5415 | 1.5409 | 1.4804 | 1.5206 | 0.061118
38904.5501 | 2027 | 0 | 38904.5502 | 2390 | 0 | 1139 | 1244 | 123.7485 | 0 | 145.9096 | 0 | 1.2375 | 0 | 1.4591 | 0 | 1.2375 | 1.4591 | 26.4124 | 7.2126 | 25.1749
38904.5503 | 2250 | 0 | 38904.5504 | 2528 | 0 | 1156 | 1261 | 137.3626 | 0 | 154.3346 | 0 | 1.3736 | 0 | 1.5433 | 0 | 1.3736 | 1.5433 | 13.8836 | 1.36 | 12.5099
38904.5505 | 2311 | 0 | 38904.5505 | 2197 | 0 | 1172.5 | 1277.5 | 141.0867 | 0 | 134.127 | 0 | 1.4109 | 0 | 1.3413 | 0 | 1.4109 | 1.3413 | 10.8775 | 16.6309 | 9.4667
38904.5507 | 2278 | 0 | 38904.5507 | 2253 | 0 | 1189.5 | 1294.5 | 139.072 | 0 | 137.5458 | 0 | 1.3907 | 0 | 1.3755 | 0 | 1.3907 | 1.3755 | 12.4838 | 13.7319 | 11.093
38904.5509 | 2465 | 0 | 38904.5509 | 2033 | 0 | 1206.5 | 1311.5 | 150.4884 | 0 | 124.1148 | 0 | 1.5049 | 0 | 1.2411 | 0 | 1.5049 | 1.2411 | 3.9505 | 26.0394 | 2.4456
38904.5511 | 2421 | 0 | 38904.5511 | 2177 | 0 | 1223 | 1328 | 147.8022 | 0 | 132.906 | 0 | 1.478 | 0 | 1.3291 | 0 | 1.478 | 1.3291 | 5.8397 | 17.7023 | 4.3617
38904.5513 | 2141 | 0 | 38904.5513 | 2157 | 0 | 1240 | 1345 | 130.7082 | 0 | 131.685 | 0 | 1.3071 | 0 | 1.3168 | 0 | 1.3071 | 1.3168 | 19.6815 | 18.7937 | 18.3744
38904.5515 | 2232 | 0 | 38904.5515 | 2447 | 0 | 1256.5 | 1361.5 | 136.2637 | 0 | 149.3895 | 0 | 1.3626 | 0 | 1.4939 | 0 | 1.3626 | 1.4939 | 14.802 | 4.7152 | 13.4393
38904.5517 | 2376 | 0 | 38904.5517 | 2497 | 0 | 1273.5 | 1378.5 | 145.0549 | 0 | 152.442 | 0 | 1.4505 | 0 | 1.5244 | 0 | 1.4505 | 1.5244 | 7.8443 | 2.6183 | 6.3937
38904.5519 | 2079 | 0 | 38904.5519 | 2127 | 0 | 1290.5 | 1395.5 | 126.9231 | 0 | 129.8535 | 0 | 1.2692 | 0 | 1.2985 | 0 | 1.2692 | 1.2985 | 23.2506 | 20.4692 | 21.9814

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 6 |  |  | 2006-07-06 | 12:53
PVC | 3-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-101.1667 | 256104.6667 |  | -97.3333 | 256171.3333 | -95.5 | 256171.3333 | -93.6667 | 256304.6667 | -101.1667 | 256104.6667
-84.3333 | 256104.6667 |  | -80.5 | 256171.3333 | -78.6667 | 256171.3333 | -76.8333 | 256304.6667 | -84.3333 | 256104.6667
-67.5 | 256104.6667 |  | -63.8333 | 256171.3333 | -62 | 256171.3333 | -60 | 213565 | -67.5 | 213565
-50.6667 | 256104.6667 |  | -47 | 213448.3333 | -45 | 256171.3333 | -43.3333 | 256304.6667 | -50.6667 | 213448.3333
-33.8333 | 256104.6667 |  | -30.1667 | 256171.3333 | -28.3333 | 256171.3333 | -26.3333 | 256304.6667 | -33.8333 | 256104.6667
-17.1667 | 256104.6667 |  | -13.3333 | 256171.3333 | -11.5 | 256171.3333 | -9.6667 | 192245.1667 | -17.1667 | 192245.1667
-0.33333 | 256104.6667 |  | 3.5 | 256171.3333 | 5.3333 | 256171.3333 | 7.1667 | 256304.6667 | -0.33333 | 256104.6667
16.5 | 256104.6667 |  | 20.1667 | 256171.3333 | 22 | 256171.3333 | 24 | 256304.6667 | 16.5 | 256104.6667
33.3333 | 256104.6667 |  | 37 | 256171.3333 | 39 | 256171.3333 | 40.6667 | 256304.6667 | 33.3333 | 256104.6667
50 | 213398.3333 |  | 53.8333 | 213465 | 55.6667 | 213515 | 57.5 | 256304.6667 | 50 | 213398.3333
66.8333 | 256104.6667 |  | 70.6667 | 256171.3333 | 72.5 | 256171.3333 | 74.3333 | 256304.6667 | 66.8333 | 256104.6667
83.5 | 256104.6667 |  | 87.3333 | 218859708.8133 | 89.3333 | 256171.3333 | 91.1667 | 256304.6667 | 83.5 | 256104.6667
100.5 | 256104.6667 |  | 104.1667 | 256171.3333 | 106 | 213415 | 108 | 256304.6667 | 100.5 | 213415
117.3333 | 218859642.1467 |  | 121 | 256171.3333 | 123 | 256171.3333 | 124.6667 | 256304.6667 | 117.3333 | 256171.3333
134.1667 | 256104.6667 |  | 137.8333 | 256171.3333 | 139.6667 | 256171.3333 | 141.6667 | 256304.6667 | 134.1667 | 256104.6667
150.8333 | 213365 |  | 154.6667 | 256171.3333 | 156.5 | 256171.3333 | 158.3333 | 213548.3333 | 150.8333 | 213365
167.6667 | 218859642.1467 |  | 171.3333 | 213448.3333 | 173.1667 | 256171.3333 | 175.1667 | 256304.6667 | 167.6667 | 213448.3333
184.3333 | 256104.6667 |  | 188.1667 | 256171.3333 | 190.1667 | 256171.3333 | 192 | 256304.6667 | 184.3333 | 256104.6667
201.3333 | 256104.6667 |  | 204.8333 | 256171.3333 | 206.8333 | 256171.3333 | 208.6667 | 256304.6667 | 201.3333 | 256104.6667
218 | 256104.6667 |  | 221.8333 | 256171.3333 | 223.6667 | 213415 | 225.5 | 256304.6667 | 218 | 213415
234.6667 | 256104.6667 |  | 238.6667 | 256171.3333 | 240.3333 | 256171.3333 | 242.3333 | 256304.6667 | 234.6667 | 256104.6667
251.6667 | 256104.6667 |  | 255.5 | 256171.3333 | 257.3333 | 256171.3333 | 259.1667 | 256304.6667 | 251.6667 | 256104.6667
268.5 | 256104.6667 |  | 272.1667 | 256171.3333 | 274 | 256171.3333 | 276 | 256304.6667 | 268.5 | 256104.6667
285.1667 | 256104.6667 |  | 289 | 256171.3333 | 290.8333 | 256171.3333 | 292.6667 | 256304.6667 | 285.1667 | 256104.6667
302 | 256104.6667 |  | 305.6667 | 256171.3333 | 307.6667 | 256171.3333 | 309.6667 | 256304.6667 | 302 | 256104.6667
318.8333 | 256104.6667 |  | 322.5 | 256171.3333 | 324.5 | 256171.3333 | 326.1667 | 256304.6667 | 318.8333 | 256104.6667
335.6667 | 218859642.1467 |  | 339.5 | 256171.3333 | 341.1667 | 256171.3333 | 343 | 256304.6667 | 335.6667 | 256171.3333
352.5 | 256104.6667 |  | 356.1667 | 256171.3333 | 358 | 256171.3333 | 360 | 256304.6667 | 352.5 | 256104.6667
369.1667 | 256104.6667 |  | 373 | 256171.3333 | 374.8333 | 256171.3333 | 376.6667 | 256304.6667 | 369.1667 | 256104.6667
385.8333 | 256104.6667 |  | 389.6667 | 256171.3333 | 391.6667 | 256171.3333 | 393.5 | 256304.6667 | 385.8333 | 256104.6667
402.8333 | 256104.6667 |  | 406.5 | 256171.3333 | 408.5 | 256171.3333 | 410.1667 | 256304.6667 | 402.8333 | 256104.6667
419.5 | 256104.6667 |  | 423.3333 | 213448.3333 | 425.1667 | 256171.3333 | 427 | 256304.6667 | 419.5 | 213448.3333
436.5 | 256104.6667 |  | 440 | 256171.3333 | 442 | 256171.3333 | 443.8333 | 256304.6667 | 436.5 | 256104.6667
453.3333 | 256104.6667 |  | 456.8333 | 256171.3333 | 458.8333 | 256171.3333 | 460.6667 | 256304.6667 | 453.3333 | 256104.6667
470 | 256104.6667 |  | 473.6667 | 256171.3333 | 475.5 | 256171.3333 | 477.5 | 256304.6667 | 470 | 256104.6667
486.8333 | 256104.6667 |  | 490.5 | 256171.3333 | 492.5 | 256171.3333 | 494.1667 | 256304.6667 | 486.8333 | 256104.6667
503.5 | 256104.6667 |  | 507.1667 | 256171.3333 | 509.1667 | 256171.3333 | 511.1667 | 256304.6667 | 503.5 | 256104.6667
520.3333 | 256104.6667 |  | 524 | 256171.3333 | 526 | 213515 | 527.6667 | 256304.6667 | 520.3333 | 213515
537.3333 | 256104.6667 |  | 540.8333 | 256171.3333 | 542.8333 | 256171.3333 | 544.6667 | 213598.3333 | 537.3333 | 213598.3333
553.8333 | 256104.6667 |  | 557.6667 | 256171.3333 | 559.5 | 256171.3333 | 561.3333 | 213565 | 553.8333 | 213565
570.6667 | 256104.6667 |  | 574.6667 | 256171.3333 | 576.3333 | 256171.3333 | 578.3333 | 256304.6667 | 570.6667 | 256104.6667
587.5 | 256104.6667 |  | 591.1667 | 256171.3333 | 593.1667 | 256171.3333 | 595.1667 | 256304.6667 | 587.5 | 256104.6667
604.3333 | 256104.6667 |  | 608 | 256171.3333 | 610 | 213515 | 611.6667 | 256304.6667 | 604.3333 | 213515
621.1667 | 256104.6667 |  | 624.8333 | 256171.3333 | 626.6667 | 256171.3333 | 628.6667 | 256304.6667 | 621.1667 | 256104.6667
637.8333 | 256104.6667 |  | 641.6667 | 256171.3333 | 643.5 | 256171.3333 | 645.3333 | 256304.6667 | 637.8333 | 256104.6667
654.6667 | 256104.6667 |  | 658.6667 | 256171.3333 | 660.3333 | 256171.3333 | 662.3333 | 256304.6667 | 654.6667 | 256104.6667
671.5 | 256104.6667 |  | 675.1667 | 256171.3333 | 677 | 256171.3333 | 679 | 256304.6667 | 671.5 | 256104.6667
688.3333 | 256104.6667 |  | 692 | 256171.3333 | 694 | 256171.3333 | 695.6667 | 256304.6667 | 688.3333 | 256104.6667
705.1667 | 256104.6667 |  | 708.8333 | 256171.3333 | 710.6667 | 256171.3333 | 712.6667 | 256304.6667 | 705.1667 | 256104.6667
721.8333 | 256104.6667 |  | 725.6667 | 256171.3333 | 727.5 | 256171.3333 | 729.3333 | 256304.6667 | 721.8333 | 256104.6667
738.6667 | 256104.6667 |  | 742.5 | 256171.3333 | 744.3333 | 256171.3333 | 746.1667 | 256304.6667 | 738.6667 | 256104.6667
755.5 | 256104.6667 |  | 759.1667 | 256171.3333 | 761 | 256171.3333 | 763 | 256304.6667 | 755.5 | 256104.6667
772.3333 | 124469.8611 |  | 776 | 16.0233 | 778 | 40461.85 | 779.6667 | 63397.0286 | 772.3333 | 16.0233
789.1667 | 38984.7859 |  | 792.8333 | 4.9353 | 794.6667 | 26475.0519 | 796.6667 | 36226.2167 | 789.1667 | 4.9353
805.8333 | 31319.1833 |  | 809.6667 | 15.9132 | 811.5 | 24750.3515 | 813.3333 | 31412.7508 | 805.8333 | 15.9132
822.6667 | 29792.7667 |  | 826.5 | 12.6358 | 828.3333 | 25698.27 | 830.1667 | 28427.3879 | 822.6667 | 12.6358
839.5 | 29792.7667 |  | 843.1667 | 23.5573 | 845 | 24103.0333 | 847 | 28627.5907 | 839.5 | 23.5573
856.3333 | 30542.4232 |  | 860 | 13.094 | 862 | 25700.4923 | 863.6667 | 27780.3222 | 856.3333 | 13.094
873.1667 | 29017.197 |  | 876.8333 | 11.8992 | 878.6667 | 25050.9519 | 880.6667 | 29377.5286 | 873.1667 | 11.8992
889.8333 | 28370.8889 |  | 893.6667 | 20.2839 | 895.5 | 22130.0915 | 897.3333 | 26656.5292 | 889.8333 | 20.2839
906.6667 | 24909.9446 |  | 910.5 | 16.1778 | 912.3333 | 19669.9074 | 914.1667 | 29377.5286 | 906.6667 | 16.1778
923.5 | 27830.9099 |  | 927.1667 | 5.0538 | 929 | 17744.3991 | 931 | 28182.9459 | 923.5 | 5.0538
940.3333 | 26643.697 |  | 944 | 10.6763 | 946 | 6580.906 | 947.6667 | 25706.3885 | 940.3333 | 10.6763
957.1667 | 25997.3889 |  | 960.8333 | 21.3989 | 962.6667 | 4357.1131 | 964.6667 | 26253.9056 | 957.1667 | 21.3989
973.8333 | 23650.3318 |  | 977.6667 | 13.5123 | 979.5 | 1831.7719 | 981.3333 | 2100.7482 | 973.8333 | 13.5123
990.6667 | 14.2502 |  | 994.5 | 12.7876 | 996.3333 | 20.7458 | 998.1667 | 15.406 | 990.6667 | 12.7876
1007.5 | 11.6707 |  | 1011.1667 | 14.9433 | 1013 | 7.4417 | 1015 | 22.6927 | 1007.5 | 7.4417
1024.3333 | 12.9647 |  | 1028 | 11.9854 | 1030 | 11.3991 | 1031.6667 | 13.0422 | 1024.3333 | 11.3991
1041.1667 | 10.7675 |  | 1044.8333 | 12.3818 | 1046.6667 | 19.8193 | 1048.6667 | 9.8914 | 1041.1667 | 9.8914
1057.8333 | 8.4281 |  | 1061.6667 | 13.8036 | 1063.5 | 18.023 | 1065.3333 | 10.7127 | 1057.8333 | 8.4281
1074.6667 | 13.5886 |  | 1078.5 | 10.7757 | 1080.3333 | 22.8924 | 1082.1667 | 7.1971 | 1074.6667 | 7.1971
1091.3333 | 8.0364 |  | 1095.1667 | 22.3626 | 1097 | 17.2858 | 1098.8333 | 11.8654 | 1091.3333 | 8.0364
1108.3333 | 16.1888 |  | 1112 | 3.0656 | 1114 | 24.1131 | 1115.6667 | 7.6902 | 1108.3333 | 3.0656
1125.1667 | 7.5994 |  | 1128.8333 | 14.3019 | 1130.6667 | 23.2011 | 1132.6667 | 16.2312 | 1125.1667 | 7.5994
1141.8333 | 17.774 |  | 1145.6667 | 20.4452 | 1147.5 | 7.7541 | 1149.3333 | 16.534 | 1141.8333 | 7.7541
1158.6667 | 12.4848 |  | 1162.5 | 10.8588 | 1164.3333 | 19.5573 | 1166.1667 | 7.4589 | 1158.6667 | 7.4589
1175.5 | 18.1084 |  | 1179.1667 | 11.1242 | 1181 | 19.1578 | 1183 | 10.9509 | 1175.5 | 10.9509
1192.3333 | 15.9437 |  | 1196 | 9.1101 | 1198 | 9.3758 | 1199.6667 | 15.8293 | 1192.3333 | 9.1101
1209.1667 | 12.9937 |  | 1212.8333 | 11.7334 | 1214.6667 | 10.2056 | 1216.6667 | 11.5044 | 1209.1667 | 10.2056
1225.8333 | 13.4944 |  | 1229.6667 | 12.3098 | 1231.5 | 20.3061 | 1233.3333 | 4.5702 | 1225.8333 | 4.5702
1242.6667 | 16.9508 |  | 1246.5 | 19.4974 | 1248.3333 | 5.3904 | 1250.1667 | 12.6948 | 1242.6667 | 5.3904
1259.5 | 13.5052 |  | 1263.1667 | 12.2081 | 1265 | 14.2251 | 1267 | 17.3596 | 1259.5 | 12.2081
1276.3333 | 17.9614 |  | 1280 | 11.0207 | 1282 | 16.9742 | 1283.6667 | 14.5201 | 1276.3333 | 11.0207
1293.1667 | 8.4179 |  | 1296.8333 | 11.9188 | 1298.6667 | 13.1065 | 1300.6667 | 15.8685 | 1293.1667 | 8.4179

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 6 |  |  | 2006-07-06 | 12:53
38904.5358 | 1 | 0 | 1 | PVC | 3-C | Tray
38904.5359 | 1 | 0 | 1 | 300 C | 6.1 kW/m2 |  | Conductors
38904.5361 | 1 | 0 | 1
38904.5363 | 1 | 0 | 1
38904.5365 | 1 | 0 | 1
38904.5367 | 1 | 0 | 1
38904.5369 | 1 | 0 | 1
38904.5371 | 1 | 0 | 1
38904.5373 | 1 | 0 | 1
38904.5375 | 2 | 0 | 1
38904.5377 | 1 | 0 | 1
38904.5379 | 1 | 0 | 1
38904.5381 | 1 | 0 | 1
38904.5383 | 1 | 1 | 1
38904.5385 | 1 | 0 | 1
38904.5387 | 1 | 0 | 1
38904.5389 | 1 | 1 | 1
38904.5391 | 1 | 0 | 1
38904.5393 | 1 | 0 | 1
38904.5395 | 1 | 0 | 1
38904.5396 | 1 | 0 | 1
38904.5398 | 1 | 0 | 1
38904.54 | 1 | 0 | 1
38904.5402 | 1 | 0 | 1
38904.5404 | 1 | 0 | 1
38904.5406 | 1 | 0 | 1
38904.5408 | 1 | 1 | 1
38904.541 | 1 | 0 | 1
38904.5412 | 1 | 0 | 1
38904.5414 | 1 | 0 | 1
38904.5416 | 1 | 0 | 1
38904.5418 | 1 | 0 | 1
38904.542 | 1 | 0 | 1
38904.5422 | 1 | 0 | 1
38904.5424 | 1 | 0 | 1
38904.5426 | 1 | 0 | 1
38904.5428 | 1 | 0 | 1
38904.543 | 1 | 0 | 1
38904.5431 | 1 | 0 | 1
38904.5433 | 1 | 0 | 1
38904.5435 | 1 | 0 | 1
38904.5437 | 1 | 0 | 1
38904.5439 | 1 | 0 | 1
38904.5441 | 1 | 0 | 1
38904.5443 | 1 | 0 | 1
38904.5445 | 1 | 0 | 1
38904.5447 | 1 | 0 | 1
38904.5449 | 1 | 0 | 1
38904.5451 | 1 | 0 | 1
38904.5453 | 1 | 0 | 1
38904.5455 | 1 | 0 | 1
38904.5457 | 1 | 0 | 1
38904.5459 | 1 | 0 | 1
38904.5461 | 5 | 0 | 1
38904.5462 | 8 | 0 | 1
38904.5464 | 8 | 0 | 1
38904.5466 | 8 | 0 | 1
38904.5468 | 7 | 0 | 1
38904.547 | 8 | 0 | 1
38904.5472 | 8 | 0 | 1
38904.5474 | 8 | 0 | 1
38904.5476 | 9 | 0 | 1
38904.5478 | 9 | 0 | 1
38904.548 | 9 | 0 | 1
38904.5482 | 9 | 0 | 1
38904.5484 | 2152 | 0 | 1
38904.5486 | 2499 | 0 | 1
38904.5488 | 2247 | 0 | 1
38904.549 | 2524 | 0 | 1
38904.5492 | 2478 | 0 | 1
38904.5494 | 2429 | 0 | 1
38904.5496 | 2411 | 0 | 1
38904.5498 | 2222 | 0 | 1
38904.55 | 2525 | 0 | 1
38904.5501 | 2027 | 0 | 1
38904.5503 | 2250 | 0 | 1
38904.5505 | 2311 | 0 | 1
38904.5507 | 2278 | 0 | 1
38904.5509 | 2465 | 0 | 1
38904.5511 | 2421 | 0 | 1
38904.5513 | 2141 | 0 | 1
38904.5515 | 2232 | 0 | 1
38904.5517 | 2376 | 0 | 1
38904.5519 | 2079 | 0 | 1
38904.5358 | 1 | 0 | 2
38904.536 | 1 | 0 | 2
38904.5362 | 1 | 0 | 2
38904.5364 | 1 | 0 | 2
38904.5366 | 1 | 0 | 2
38904.5367 | 1 | 0 | 2
38904.5369 | 1 | 0 | 2
38904.5371 | 1 | 0 | 2
38904.5373 | 1 | 0 | 2
38904.5375 | 2 | 0 | 2
38904.5377 | 1 | 0 | 2
38904.5379 | 1 | 0 | 2
38904.5381 | 1 | 0 | 2
38904.5383 | 1 | 0 | 2
38904.5385 | 1 | 0 | 2
38904.5387 | 1 | 0 | 2
38904.5389 | 1 | 0 | 2
38904.5391 | 1 | 0 | 2
38904.5393 | 1 | 0 | 2
38904.5395 | 1 | 0 | 2
38904.5397 | 1 | 0 | 2
38904.5399 | 1 | 0 | 2
38904.54 | 1 | 0 | 2
38904.5402 | 1 | 0 | 2
38904.5404 | 1 | 0 | 2
38904.5406 | 1 | 0 | 2
38904.5408 | 1 | 0 | 2
38904.541 | 1 | 0 | 2
38904.5412 | 1 | 0 | 2
38904.5414 | 1 | 0 | 2
38904.5416 | 1 | 0 | 2
38904.5418 | 1 | 0 | 2
38904.542 | 1 | 0 | 2
38904.5422 | 1 | 0 | 2
38904.5424 | 1 | 0 | 2
38904.5426 | 1 | 0 | 2
38904.5428 | 1 | 0 | 2
38904.543 | 1 | 0 | 2
38904.5432 | 1 | 0 | 2
38904.5434 | 1 | 0 | 2
38904.5436 | 1 | 0 | 2
38904.5437 | 1 | 0 | 2
38904.5439 | 1 | 0 | 2
38904.5441 | 1 | 0 | 2
38904.5443 | 1 | 0 | 2
38904.5445 | 1 | 0 | 2
38904.5447 | 1 | 0 | 2
38904.5449 | 1 | 0 | 2
38904.5451 | 1 | 0 | 2
38904.5453 | 1 | 0 | 2
38904.5455 | 1 | 0 | 2
38904.5457 | 1 | 0 | 2
38904.5459 | 2085 | 0 | 2
38904.5461 | 2538 | 0 | 2
38904.5463 | 1960 | 0 | 2
38904.5465 | 2244 | 0 | 2
38904.5467 | 1951 | 0 | 2
38904.5469 | 2480 | 0 | 2
38904.547 | 2152 | 0 | 2
38904.5472 | 2152 | 0 | 2
38904.5474 | 2309 | 0 | 2
38904.5476 | 2384 | 0 | 2
38904.5478 | 2503 | 0 | 2
38904.548 | 2271 | 0 | 2
38904.5482 | 2200 | 0 | 2
38904.5484 | 2322 | 0 | 2
38904.5486 | 2461 | 0 | 2
38904.5488 | 2508 | 0 | 2
38904.549 | 2538 | 0 | 2
38904.5492 | 2175 | 0 | 2
38904.5494 | 2546 | 0 | 2
38904.5496 | 2122 | 0 | 2
38904.5498 | 2505 | 0 | 2
38904.55 | 2524 | 0 | 2
38904.5502 | 2390 | 0 | 2
38904.5504 | 2528 | 0 | 2
38904.5505 | 2197 | 0 | 2
38904.5507 | 2253 | 0 | 2
38904.5509 | 2033 | 0 | 2
38904.5511 | 2177 | 0 | 2
38904.5513 | 2157 | 0 | 2
38904.5515 | 2447 | 0 | 2
38904.5517 | 2497 | 0 | 2
38904.5519 | 2127 | 0 | 2
38904.5358 | 1 | 0 | 3
38904.536 | 1 | 0 | 3
38904.5362 | 1 | 0 | 3
38904.5364 | 1 | 0 | 3
38904.5366 | 1 | 0 | 3
38904.5368 | 1 | 0 | 3
38904.537 | 1 | 0 | 3
38904.5372 | 1 | 0 | 3
38904.5373 | 1 | 0 | 3
38904.5375 | 1 | 0 | 3
38904.5377 | 1 | 0 | 3
38904.5379 | 1 | 0 | 3
38904.5381 | 1 | 0 | 3
38904.5383 | 1 | 0 | 3
38904.5385 | 1 | 0 | 3
38904.5387 | 1 | 0 | 3
38904.5389 | 1 | 0 | 3
38904.5391 | 1 | 0 | 3
38904.5393 | 1 | 0 | 3
38904.5395 | 1 | 0 | 3
38904.5397 | 1 | 0 | 3
38904.5399 | 1 | 0 | 3
38904.5401 | 1 | 0 | 3
38904.5403 | 1 | 0 | 3
38904.5405 | 1 | 0 | 3
38904.5406 | 1 | 0 | 3
38904.5408 | 1 | 0 | 3
38904.541 | 1 | 0 | 3
38904.5412 | 1 | 0 | 3
38904.5414 | 1 | 0 | 3
38904.5416 | 1 | 0 | 3
38904.5418 | 1 | 0 | 3
38904.542 | 1 | 0 | 3
38904.5422 | 1 | 0 | 3
38904.5424 | 1 | 0 | 3
38904.5426 | 1 | 0 | 3
38904.5428 | 1 | 0 | 3
38904.543 | 1 | 0 | 3
38904.5432 | 1 | 0 | 3
38904.5434 | 1 | 0 | 3
38904.5436 | 1 | 0 | 3
38904.5438 | 1 | 0 | 3
38904.544 | 1 | 0 | 3
38904.5441 | 1 | 0 | 3
38904.5443 | 1 | 0 | 3
38904.5445 | 1 | 0 | 3
38904.5447 | 1 | 0 | 3
38904.5449 | 1 | 0 | 3
38904.5451 | 1 | 0 | 3
38904.5453 | 1 | 0 | 3
38904.5455 | 1 | 0 | 3
38904.5457 | 1 | 0 | 3
38904.5459 | 8 | 0 | 3
38904.5461 | 11 | 0 | 3
38904.5463 | 10 | 0 | 3
38904.5465 | 10 | 0 | 3
38904.5467 | 10 | 0 | 3
38904.5469 | 11 | 0 | 3
38904.5471 | 11 | 0 | 3
38904.5473 | 12 | 0 | 3
38904.5475 | 13 | 0 | 3
38904.5477 | 11 | 0 | 3
38904.5478 | 11 | 0 | 3
38904.548 | 12 | 0 | 3
38904.5482 | 10 | 0 | 3
38904.5484 | 2517 | 0 | 3
38904.5486 | 2437 | 0 | 3
38904.5488 | 2424 | 0 | 3
38904.549 | 2516 | 0 | 3
38904.5492 | 2146 | 0 | 3
38904.5494 | 1984 | 0 | 3
38904.5496 | 2184 | 0 | 3
38904.5498 | 2483 | 0 | 3
38904.55 | 2140 | 0 | 3
38904.5502 | 2226 | 0 | 3
38904.5504 | 2441 | 0 | 3
38904.5506 | 2158 | 0 | 3
38904.5508 | 2405 | 0 | 3
38904.5509 | 1955 | 0 | 3
38904.5511 | 2034 | 0 | 3
38904.5513 | 2431 | 0 | 3
38904.5515 | 2493 | 0 | 3
38904.5517 | 2077 | 0 | 3
38904.5519 | 2543 | 0 | 3
38904.5358 | 1 | 0 | 4
38904.536 | 1 | 0 | 4
38904.5362 | 1 | 0 | 4
38904.5364 | 1 | 0 | 4
38904.5366 | 1 | 0 | 4
38904.5368 | 1 | 0 | 4
38904.537 | 1 | 0 | 4
38904.5372 | 1 | 0 | 4
38904.5374 | 1 | 0 | 4
38904.5376 | 2 | 0 | 4
38904.5378 | 1 | 0 | 4
38904.5379 | 1 | 0 | 4
38904.5381 | 1 | 0 | 4
38904.5383 | 1 | 0 | 4
38904.5385 | 1 | 0 | 4
38904.5387 | 1 | 0 | 4
38904.5389 | 1 | 0 | 4
38904.5391 | 1 | 0 | 4
38904.5393 | 1 | 0 | 4
38904.5395 | 1 | 0 | 4
38904.5397 | 1 | 0 | 4
38904.5399 | 1 | 0 | 4
38904.5401 | 1 | 0 | 4
38904.5403 | 1 | 0 | 4
38904.5405 | 1 | 0 | 4
38904.5407 | 1 | 0 | 4
38904.5409 | 1 | 0 | 4
38904.5411 | 1 | 0 | 4
38904.5413 | 1 | 0 | 4
38904.5414 | 1 | 0 | 4
38904.5416 | 1 | 0 | 4
38904.5418 | 1 | 0 | 4
38904.542 | 1 | 0 | 4
38904.5422 | 1 | 0 | 4
38904.5424 | 1 | 0 | 4
38904.5426 | 1 | 0 | 4
38904.5428 | 1 | 0 | 4
38904.543 | 2 | 0 | 4
38904.5432 | 1 | 0 | 4
38904.5434 | 1 | 0 | 4
38904.5436 | 1 | 0 | 4
38904.5438 | 1 | 0 | 4
38904.544 | 2 | 0 | 4
38904.5442 | 1 | 0 | 4
38904.5444 | 1 | 0 | 4
38904.5445 | 1 | 0 | 4
38904.5447 | 1 | 0 | 4
38904.5449 | 1 | 0 | 4
38904.5451 | 1 | 0 | 4
38904.5453 | 1 | 0 | 4
38904.5455 | 1 | 0 | 4
38904.5457 | 1 | 0 | 4
38904.5459 | 4 | 0 | 4
38904.5461 | 9 | 0 | 4
38904.5463 | 10 | 0 | 4
38904.5465 | 9 | 0 | 4
38904.5467 | 10 | 0 | 4
38904.5469 | 10 | 0 | 4
38904.5471 | 9 | 0 | 4
38904.5473 | 10 | 0 | 4
38904.5475 | 9 | 0 | 4
38904.5477 | 10 | 0 | 4
38904.5479 | 48 | 0 | 4
38904.5481 | 510 | 0 | 4
38904.5483 | 83 | 0 | 4
38904.5484 | 1952 | 0 | 4
38904.5486 | 2430 | 0 | 4
38904.5488 | 2195 | 0 | 4
38904.549 | 2054 | 0 | 4
38904.5492 | 2511 | 0 | 4
38904.5494 | 1949 | 0 | 4
38904.5496 | 1983 | 0 | 4
38904.5498 | 2019 | 0 | 4
38904.55 | 2048 | 0 | 4
38904.5502 | 2535 | 0 | 4
38904.5504 | 2074 | 0 | 4
38904.5506 | 2133 | 0 | 4
38904.5508 | 2473 | 0 | 4
38904.551 | 2397 | 0 | 4
38904.5512 | 2011 | 0 | 4
38904.5514 | 2421 | 0 | 4
38904.5516 | 1989 | 0 | 4
38904.5517 | 2047 | 0 | 4
38904.5519 | 2466 | 0 | 4
38904.5358 | 1 | 0 | 5
38904.536 | 1 | 0 | 5
38904.5362 | 1 | 0 | 5
38904.5364 | 1 | 0 | 5
38904.5366 | 1 | 0 | 5
38904.5368 | 1 | 0 | 5
38904.537 | 1 | 0 | 5
38904.5372 | 1 | 0 | 5
38904.5374 | 1 | 0 | 5
38904.5376 | 1 | 0 | 5
38904.5378 | 1 | 0 | 5
38904.538 | 1 | 0 | 5
38904.5382 | 1 | 0 | 5
38904.5383 | 1 | 0 | 5
38904.5385 | 1 | 0 | 5
38904.5387 | 2 | 0 | 5
38904.5389 | 1 | 0 | 5
38904.5391 | 1 | 0 | 5
38904.5393 | 1 | 0 | 5
38904.5395 | 1 | 0 | 5
38904.5397 | 1 | 0 | 5
38904.5399 | 1 | 0 | 5
38904.5401 | 1 | 0 | 5
38904.5403 | 1 | 0 | 5
38904.5405 | 1 | 0 | 5
38904.5407 | 1 | 0 | 5
38904.5409 | 1 | 0 | 5
38904.5411 | 1 | 0 | 5
38904.5413 | 1 | 0 | 5
38904.5415 | 1 | 0 | 5
38904.5417 | 1 | 0 | 5
38904.5419 | 1 | 0 | 5
38904.542 | 1 | 0 | 5
38904.5422 | 1 | 0 | 5
38904.5424 | 1 | 0 | 5
38904.5426 | 1 | 0 | 5
38904.5428 | 1 | 0 | 5
38904.543 | 1 | 0 | 5
38904.5432 | 1 | 0 | 5
38904.5434 | 1 | 0 | 5
38904.5436 | 1 | 0 | 5
38904.5438 | 1 | 0 | 5
38904.544 | 1 | 0 | 5
38904.5442 | 1 | 0 | 5
38904.5444 | 1 | 0 | 5
38904.5446 | 1 | 0 | 5
38904.5448 | 1 | 0 | 5
38904.545 | 1 | 0 | 5
38904.5452 | 1 | 0 | 5
38904.5453 | 1 | 0 | 5
38904.5455 | 1 | 0 | 5
38904.5457 | 1 | 0 | 5
38904.5459 | 3 | 0 | 5
38904.5461 | 6 | 0 | 5
38904.5463 | 7 | 0 | 5
38904.5465 | 8 | 0 | 5
38904.5467 | 8 | 0 | 5
38904.5469 | 8 | 0 | 5
38904.5471 | 8 | 0 | 5
38904.5473 | 8 | 0 | 5
38904.5475 | 11 | 0 | 5
38904.5477 | 8 | 0 | 5
38904.5479 | 9 | 0 | 5
38904.5481 | 9 | 0 | 5
38904.5483 | 22 | 7 | 5
38904.5485 | 2102 | 0 | 5
38904.5487 | 2012 | 0 | 5
38904.5488 | 2150 | 0 | 5
38904.549 | 1987 | 0 | 5
38904.5492 | 2499 | 0 | 5
38904.5494 | 2413 | 0 | 5
38904.5496 | 2548 | 0 | 5
38904.5498 | 1970 | 0 | 5
38904.55 | 2521 | 0 | 5
38904.5502 | 2291 | 0 | 5
38904.5504 | 2160 | 0 | 5
38904.5506 | 2054 | 0 | 5
38904.5508 | 1989 | 0 | 5
38904.551 | 2463 | 0 | 5
38904.5512 | 2359 | 1 | 5
38904.5514 | 2037 | 0 | 5
38904.5516 | 2084 | 0 | 5
38904.5518 | 2088 | 0 | 5
38904.552 | 2530 | 0 | 5
38904.5358 | 1 | 0 | 6
38904.536 | 1 | 0 | 6
38904.5362 | 2 | 0 | 6
38904.5364 | 1 | 0 | 6
38904.5366 | 1 | 0 | 6
38904.5368 | 1 | 0 | 6
38904.537 | 1 | 0 | 6
38904.5372 | 1 | 0 | 6
38904.5374 | 1 | 0 | 6
38904.5376 | 1 | 0 | 6
38904.5378 | 1 | 0 | 6
38904.538 | 1 | 0 | 6
38904.5382 | 1 | 0 | 6
38904.5384 | 1 | 0 | 6
38904.5386 | 1 | 0 | 6
38904.5387 | 1 | 0 | 6
38904.5389 | 1 | 0 | 6
38904.5391 | 1 | 0 | 6
38904.5393 | 1 | 0 | 6
38904.5395 | 1 | 0 | 6
38904.5397 | 1 | 0 | 6
38904.5399 | 1 | 0 | 6
38904.5401 | 1 | 1 | 6
38904.5403 | 1 | 0 | 6
38904.5405 | 1 | 0 | 6
38904.5407 | 1 | 0 | 6
38904.5409 | 1 | 0 | 6
38904.5411 | 1 | 0 | 6
38904.5413 | 1 | 0 | 6
38904.5415 | 1 | 0 | 6
38904.5417 | 1 | 0 | 6
38904.5419 | 1 | 0 | 6
38904.5421 | 1 | 0 | 6
38904.5423 | 1 | 0 | 6
38904.5425 | 1 | 0 | 6
38904.5426 | 1 | 0 | 6
38904.5428 | 1 | 0 | 6
38904.543 | 1 | 0 | 6
38904.5432 | 1 | 0 | 6
38904.5434 | 2 | 0 | 6
38904.5436 | 1 | 0 | 6
38904.5438 | 1 | 0 | 6
38904.544 | 1 | 0 | 6
38904.5442 | 1 | 0 | 6
38904.5444 | 1 | 0 | 6
38904.5446 | 1 | 0 | 6
38904.5448 | 1 | 0 | 6
38904.545 | 1 | 0 | 6
38904.5452 | 1 | 0 | 6
38904.5454 | 1 | 0 | 6
38904.5456 | 1 | 0 | 6
38904.5458 | 1 | 0 | 6
38904.5459 | 2 | 0 | 6
38904.5461 | 5 | 0 | 6
38904.5463 | 6 | 0 | 6
38904.5465 | 7 | 0 | 6
38904.5467 | 8 | 0 | 6
38904.5469 | 7 | 0 | 6
38904.5471 | 7 | 0 | 6
38904.5473 | 8 | 0 | 6
38904.5475 | 7 | 0 | 6
38904.5477 | 7 | 0 | 6
38904.5479 | 8 | 0 | 6
38904.5481 | 8 | 0 | 6
38904.5483 | 163 | 121 | 6
38904.5485 | 2306 | 0 | 6
38904.5487 | 1943 | 0 | 6
38904.5489 | 2517 | 0 | 6
38904.5491 | 2365 | 0 | 6
38904.5492 | 2522 | 0 | 6
38904.5494 | 2406 | 0 | 6
38904.5498 | 2283 | 0 | 6
38904.55 | 2392 | 0 | 6
38904.5502 | 2067 | 0 | 6
38904.5504 | 2376 | 0 | 6
38904.5506 | 2344 | 0 | 6
38904.5508 | 2237 | 0 | 6
38904.551 | 2304 | 0 | 6
38904.5512 | 2475 | 0 | 6
38904.5514 | 2381 | 0 | 6
38904.5516 | 2399 | 0 | 6
38904.5518 | 2146 | 0 | 6
38904.552 | 2181 | 0 | 6
38904.5359 | 1 | 0 | 7
38904.5361 | 1 | 0 | 7
38904.5362 | 1 | 0 | 7
38904.5364 | 2 | 0 | 7
38904.5366 | 1 | 0 | 7
38904.5368 | 1 | 0 | 7
38904.537 | 1 | 0 | 7
38904.5372 | 1 | 0 | 7
38904.5374 | 1 | 0 | 7
38904.5376 | 1 | 0 | 7
38904.5378 | 1 | 0 | 7
38904.538 | 1 | 0 | 7
38904.5382 | 1 | 0 | 7
38904.5384 | 1 | 0 | 7
38904.5386 | 1 | 0 | 7
38904.5388 | 1 | 0 | 7
38904.539 | 2 | 0 | 7
38904.5392 | 1 | 0 | 7
38904.5394 | 1 | 0 | 7
38904.5395 | 1 | 0 | 7
38904.5397 | 1 | 0 | 7
38904.5399 | 1 | 0 | 7
38904.5401 | 1 | 0 | 7
38904.5403 | 1 | 0 | 7
38904.5405 | 1 | 0 | 7
38904.5407 | 1 | 0 | 7
38904.5409 | 1 | 0 | 7
38904.5411 | 1 | 0 | 7
38904.5413 | 1 | 0 | 7
38904.5415 | 1 | 0 | 7
38904.5417 | 1 | 0 | 7
38904.5419 | 2 | 0 | 7
38904.5421 | 1 | 0 | 7
38904.5423 | 1 | 0 | 7
38904.5425 | 1 | 0 | 7
38904.5427 | 1 | 0 | 7
38904.5428 | 1 | 0 | 7
38904.543 | 1 | 0 | 7
38904.5432 | 1 | 0 | 7
38904.5434 | 1 | 0 | 7
38904.5436 | 1 | 0 | 7
38904.5438 | 1 | 0 | 7
38904.544 | 1 | 0 | 7
38904.5442 | 1 | 0 | 7
38904.5444 | 1 | 0 | 7
38904.5446 | 1 | 0 | 7
38904.5448 | 1 | 0 | 7
38904.545 | 1 | 0 | 7
38904.5452 | 1 | 0 | 7
38904.5454 | 1 | 0 | 7
38904.5456 | 1 | 0 | 7
38904.5458 | 1 | 0 | 7
38904.546 | 2122 | 0 | 7
38904.5462 | 2348 | 0 | 7
38904.5464 | 2517 | 0 | 7
38904.5466 | 2177 | 0 | 7
38904.5467 | 2321 | 0 | 7
38904.5469 | 1998 | 0 | 7
38904.5471 | 2234 | 0 | 7
38904.5473 | 2075 | 0 | 7
38904.5475 | 2276 | 0 | 7
38904.5477 | 2438 | 0 | 7
38904.5479 | 2468 | 0 | 7
38904.5481 | 2093 | 0 | 7
38904.5483 | 2123 | 0 | 7
38904.5485 | 2281 | 0 | 7
38904.5487 | 1942 | 0 | 7
38904.5489 | 2507 | 0 | 7
38904.5491 | 2448 | 0 | 7
38904.5493 | 2097 | 0 | 7
38904.5495 | 2546 | 0 | 7
38904.5497 | 2101 | 0 | 7
38904.5498 | 2425 | 0 | 7
38904.55 | 2053 | 0 | 7
38904.5502 | 2073 | 0 | 7
38904.5504 | 2546 | 0 | 7
38904.5506 | 2231 | 0 | 7
38904.5508 | 2279 | 0 | 7
38904.551 | 2377 | 0 | 7
38904.5512 | 2385 | 0 | 7
38904.5514 | 2015 | 0 | 7
38904.5516 | 2542 | 0 | 7
38904.5518 | 2521 | 0 | 7
38904.552 | 2397 | 0 | 7
38904.5359 | 1 | 0 | 8
38904.5361 | 1 | 0 | 8
38904.5363 | 1 | 0 | 8
38904.5365 | 1 | 0 | 8
38904.5366 | 1 | 0 | 8
38904.5368 | 1 | 0 | 8
38904.537 | 1 | 0 | 8
38904.5372 | 1 | 0 | 8
38904.5374 | 1 | 0 | 8
38904.5376 | 1 | 0 | 8
38904.5378 | 1 | 0 | 8
38904.538 | 1 | 0 | 8
38904.5382 | 1 | 0 | 8
38904.5384 | 1 | 0 | 8
38904.5386 | 1 | 0 | 8
38904.5388 | 1 | 0 | 8
38904.539 | 1 | 0 | 8
38904.5392 | 1 | 0 | 8
38904.5394 | 1 | 0 | 8
38904.5396 | 1 | 0 | 8
38904.5398 | 1 | 0 | 8
38904.54 | 1 | 0 | 8
38904.5402 | 1 | 0 | 8
38904.5403 | 1 | 0 | 8
38904.5405 | 1 | 0 | 8
38904.5407 | 1 | 0 | 8
38904.5409 | 1 | 0 | 8
38904.5411 | 1 | 0 | 8
38904.5413 | 1 | 0 | 8
38904.5415 | 1 | 0 | 8
38904.5417 | 1 | 0 | 8
38904.5419 | 1 | 0 | 8
38904.5421 | 1 | 0 | 8
38904.5423 | 1 | 0 | 8
38904.5425 | 1 | 0 | 8
38904.5427 | 1 | 0 | 8
38904.5429 | 1 | 0 | 8
38904.5431 | 1 | 0 | 8
38904.5433 | 1 | 0 | 8
38904.5434 | 1 | 0 | 8
38904.5436 | 1 | 0 | 8
38904.5438 | 1 | 0 | 8
38904.544 | 1 | 0 | 8
38904.5442 | 1 | 0 | 8
38904.5444 | 1 | 0 | 8
38904.5446 | 1 | 0 | 8
38904.5448 | 1 | 0 | 8
38904.545 | 1 | 0 | 8
38904.5452 | 1 | 0 | 8
38904.5454 | 1 | 0 | 8
38904.5456 | 1 | 0 | 8
38904.5458 | 1 | 0 | 8
38904.546 | 10 | 0 | 8
38904.5462 | 10 | 0 | 8
38904.5464 | 11 | 0 | 8
38904.5466 | 11 | 0 | 8
38904.5468 | 12 | 0 | 8
38904.547 | 11 | 0 | 8
38904.5471 | 12 | 0 | 8
38904.5473 | 13 | 0 | 8
38904.5475 | 27 | 0 | 8
38904.5477 | 12 | 0 | 8
38904.5479 | 559 | 0 | 8
38904.5481 | 27 | 0 | 8
38904.5483 | 99 | 0 | 8
38904.5485 | 2374 | 1 | 8
38904.5487 | 2241 | 0 | 8
38904.5489 | 2203 | 0 | 8
38904.5491 | 2021 | 0 | 8
38904.5493 | 2078 | 0 | 8
38904.5495 | 2059 | 0 | 8
38904.5497 | 2174 | 0 | 8
38904.5499 | 1970 | 0 | 8
38904.5501 | 1961 | 0 | 8
38904.5503 | 2525 | 0 | 8
38904.5505 | 2170 | 0 | 8
38904.5506 | 2248 | 0 | 8
38904.5508 | 2547 | 0 | 8
38904.551 | 2406 | 0 | 8
38904.5512 | 1952 | 0 | 8
38904.5514 | 2336 | 0 | 8
38904.5516 | 2482 | 0 | 8
38904.5518 | 2092 | 0 | 8
38904.552 | 2292 | 0 | 8
38904.5359 | 1 | 0 | 9
38904.5361 | 1 | 0 | 9
38904.5363 | 1 | 0 | 9
38904.5365 | 1 | 0 | 9
38904.5367 | 1 | 0 | 9
38904.5369 | 1 | 0 | 9
38904.537 | 1 | 0 | 9
38904.5372 | 1 | 0 | 9
38904.5374 | 1 | 0 | 9
38904.5376 | 1 | 0 | 9
38904.5378 | 1 | 0 | 9
38904.538 | 1 | 1 | 9
38904.5382 | 1 | 0 | 9
38904.5384 | 1 | 0 | 9
38904.5386 | 1 | 0 | 9
38904.5388 | 1 | 0 | 9
38904.539 | 1 | 0 | 9
38904.5392 | 1 | 0 | 9
38904.5394 | 1 | 0 | 9
38904.5396 | 1 | 0 | 9
38904.5398 | 1 | 0 | 9
38904.54 | 1 | 0 | 9
38904.5402 | 1 | 0 | 9
38904.5404 | 1 | 0 | 9
38904.5406 | 1 | 0 | 9
38904.5407 | 1 | 0 | 9
38904.5409 | 1 | 0 | 9
38904.5411 | 1 | 0 | 9
38904.5413 | 1 | 0 | 9
38904.5415 | 1 | 0 | 9
38904.5417 | 1 | 0 | 9
38904.5419 | 1 | 0 | 9
38904.5421 | 1 | 0 | 9
38904.5423 | 1 | 0 | 9
38904.5425 | 1 | 0 | 9
38904.5427 | 1 | 0 | 9
38904.5429 | 1 | 0 | 9
38904.5431 | 1 | 0 | 9
38904.5433 | 1 | 0 | 9
38904.5435 | 1 | 0 | 9
38904.5437 | 1 | 0 | 9
38904.5439 | 1 | 0 | 9
38904.5441 | 1 | 0 | 9
38904.5442 | 1 | 0 | 9
38904.5444 | 1 | 0 | 9
38904.5446 | 1 | 0 | 9
38904.5448 | 1 | 0 | 9
38904.545 | 1 | 0 | 9
38904.5452 | 1 | 0 | 9
38904.5454 | 1 | 0 | 9
38904.5456 | 1 | 0 | 9
38904.5458 | 1 | 0 | 9
38904.546 | 2455 | 0 | 9
38904.5462 | 2448 | 0 | 9
38904.5464 | 2225 | 0 | 9
38904.5466 | 2418 | 0 | 9
38904.5468 | 1988 | 0 | 9
38904.547 | 2380 | 0 | 9
38904.5472 | 2515 | 0 | 9
38904.5474 | 2167 | 0 | 9
38904.5475 | 2051 | 0 | 9
38904.5477 | 2499 | 0 | 9
38904.5479 | 2037 | 0 | 9
38904.5481 | 1988 | 0 | 9
38904.5483 | 2480 | 0 | 9
38904.5485 | 2216 | 0 | 9
38904.5487 | 2357 | 0 | 9
38904.5489 | 1948 | 0 | 9
38904.5491 | 1949 | 0 | 9
38904.5493 | 2528 | 0 | 9
38904.5495 | 1956 | 0 | 9
38904.5497 | 2061 | 0 | 9
38904.5499 | 2532 | 0 | 9
38904.5501 | 2199 | 0 | 9
38904.5503 | 1964 | 0 | 9
38904.5505 | 1963 | 0 | 9
38904.5507 | 2516 | 0 | 9
38904.5509 | 2534 | 0 | 9
38904.5511 | 2529 | 0 | 9
38904.5512 | 2293 | 0 | 9
38904.5514 | 2278 | 0 | 9
38904.5516 | 1955 | 0 | 9
38904.5518 | 1990 | 0 | 9
38904.552 | 2365 | 0 | 9
38904.5359 | 1 | 0 | 10
38904.5361 | 1 | 0 | 10
38904.5363 | 1 | 0 | 10
38904.5365 | 1 | 0 | 10
38904.5367 | 1 | 0 | 10
38904.5369 | 4 | 0 | 10
38904.5371 | 1 | 0 | 10
38904.5373 | 1 | 0 | 10
38904.5375 | 1 | 0 | 10
38904.5377 | 1 | 0 | 10
38904.5378 | 1 | 0 | 10
38904.538 | 1 | 0 | 10
38904.5382 | 1 | 0 | 10
38904.5384 | 1 | 0 | 10
38904.5386 | 1 | 0 | 10
38904.5388 | 1 | 0 | 10
38904.539 | 1 | 0 | 10
38904.5392 | 1 | 0 | 10
38904.5394 | 1 | 0 | 10
38904.5396 | 1 | 0 | 10
38904.5398 | 1 | 0 | 10
38904.54 | 1 | 0 | 10
38904.5402 | 1 | 0 | 10
38904.5404 | 1 | 0 | 10
38904.5406 | 1 | 0 | 10
38904.5408 | 1 | 0 | 10
38904.541 | 1 | 0 | 10
38904.5412 | 1 | 0 | 10
38904.5413 | 1 | 0 | 10
38904.5415 | 1 | 0 | 10
38904.5417 | 1 | 0 | 10
38904.5419 | 1 | 0 | 10
38904.5421 | 1 | 0 | 10
38904.5423 | 1 | 0 | 10
38904.5425 | 1 | 0 | 10
38904.5427 | 1 | 0 | 10
38904.5429 | 1 | 0 | 10
38904.5431 | 1 | 0 | 10
38904.5433 | 2 | 0 | 10
38904.5435 | 1 | 0 | 10
38904.5437 | 1 | 0 | 10
38904.5439 | 1 | 0 | 10
38904.5441 | 1 | 0 | 10
38904.5443 | 1 | 0 | 10
38904.5445 | 1 | 0 | 10
38904.5447 | 1 | 0 | 10
38904.5448 | 1 | 0 | 10
38904.545 | 1 | 0 | 10
38904.5452 | 1 | 0 | 10
38904.5454 | 1 | 0 | 10
38904.5456 | 1 | 0 | 10
38904.5458 | 1 | 0 | 10
38904.546 | 10 | 0 | 10
38904.5462 | 10 | 0 | 10
38904.5464 | 11 | 0 | 10
38904.5466 | 11 | 0 | 10
38904.5468 | 10 | 0 | 10
38904.547 | 12 | 0 | 10
38904.5472 | 11 | 0 | 10
38904.5474 | 13 | 0 | 10
38904.5476 | 11 | 0 | 10
38904.5478 | 13 | 0 | 10
38904.548 | 13 | 0 | 10
38904.5481 | 12 | 0 | 10
38904.5483 | 466 | 11 | 10
38904.5485 | 2196 | 0 | 10
38904.5487 | 2036 | 0 | 10
38904.5489 | 2211 | 0 | 10
38904.5491 | 2160 | 0 | 10
38904.5493 | 2543 | 0 | 10
38904.5495 | 2279 | 0 | 10
38904.5497 | 2506 | 0 | 10
38904.5499 | 2546 | 0 | 10
38904.5501 | 2314 | 0 | 10
38904.5503 | 2111 | 0 | 10
38904.5505 | 2346 | 0 | 10
38904.5507 | 2390 | 0 | 10
38904.5509 | 2125 | 0 | 10
38904.5511 | 2119 | 0 | 10
38904.5513 | 2341 | 0 | 10
38904.5515 | 2298 | 0 | 10
38904.5517 | 2002 | 0 | 10
38904.5518 | 2202 | 0 | 10
38904.552 | 2015 | 0 | 10
38904.5359 | 1 | 0 | 11
38904.5361 | 1 | 0 | 11
38904.5363 | 1 | 0 | 11
38904.5365 | 1 | 0 | 11
38904.5367 | 1 | 0 | 11
38904.5369 | 1 | 0 | 11
38904.5371 | 1 | 0 | 11
38904.5373 | 1 | 0 | 11
38904.5375 | 1 | 0 | 11
38904.5377 | 1 | 0 | 11
38904.5379 | 1 | 0 | 11
38904.5381 | 1 | 0 | 11
38904.5383 | 2 | 0 | 11
38904.5384 | 1 | 0 | 11
38904.5386 | 1 | 0 | 11
38904.5388 | 1 | 0 | 11
38904.539 | 1 | 0 | 11
38904.5394 | 1 | 0 | 11
38904.5396 | 2 | 0 | 11
38904.5398 | 1 | 0 | 11
38904.54 | 1 | 0 | 11
38904.5402 | 1 | 0 | 11
38904.5404 | 1 | 0 | 11
38904.5406 | 1 | 0 | 11
38904.5408 | 1 | 0 | 11
38904.541 | 1 | 0 | 11
38904.5412 | 1 | 0 | 11
38904.5414 | 1 | 0 | 11
38904.5416 | 1 | 0 | 11
38904.5417 | 1 | 0 | 11
38904.5419 | 1 | 0 | 11
38904.5421 | 1 | 0 | 11
38904.5423 | 1 | 0 | 11
38904.5425 | 1 | 0 | 11
38904.5427 | 1 | 0 | 11
38904.5429 | 1 | 0 | 11
38904.5431 | 1 | 0 | 11
38904.5433 | 1 | 0 | 11
38904.5435 | 1 | 0 | 11
38904.5437 | 1 | 0 | 11
38904.5439 | 1 | 0 | 11
38904.5441 | 1 | 0 | 11
38904.5443 | 1 | 0 | 11
38904.5445 | 1 | 0 | 11
38904.5447 | 1 | 0 | 11
38904.5449 | 1 | 0 | 11
38904.5451 | 1 | 0 | 11
38904.5453 | 1 | 0 | 11
38904.5454 | 1 | 0 | 11
38904.5456 | 1 | 0 | 11
38904.5458 | 1 | 0 | 11
38904.546 | 8 | 0 | 11
38904.5462 | 10 | 0 | 11
38904.5464 | 10 | 0 | 11
38904.5466 | 10 | 0 | 11
38904.5468 | 10 | 0 | 11
38904.547 | 9 | 0 | 11
38904.5472 | 10 | 0 | 11
38904.5474 | 12 | 0 | 11
38904.5476 | 12 | 0 | 11
38904.5478 | 39 | 0 | 11
38904.548 | 18 | 0 | 11
38904.5482 | 76 | 0 | 11
38904.5484 | 2095 | 0 | 11
38904.5486 | 2084 | 0 | 11
38904.5488 | 2500 | 0 | 11
38904.5489 | 2534 | 0 | 11
38904.5491 | 2375 | 0 | 11
38904.5493 | 1992 | 0 | 11
38904.5495 | 2273 | 0 | 11
38904.5497 | 2446 | 0 | 11
38904.5499 | 2222 | 0 | 11
38904.5501 | 2252 | 0 | 11
38904.5503 | 2124 | 0 | 11
38904.5505 | 2190 | 0 | 11
38904.5507 | 2078 | 0 | 11
38904.5509 | 2069 | 0 | 11
38904.5511 | 2187 | 0 | 11
38904.5513 | 2507 | 0 | 11
38904.5515 | 2547 | 0 | 11
38904.5517 | 2317 | 0 | 11
38904.5519 | 2482 | 0 | 11
38904.5521 | 2074 | 0 | 11
38904.5359 | 1 | 0 | 12
38904.5361 | 1 | 0 | 12
38904.5363 | 1 | 0 | 12
38904.5365 | 1 | 0 | 12
38904.5367 | 1 | 0 | 12
38904.5369 | 1 | 0 | 12
38904.5371 | 1 | 0 | 12
38904.5373 | 1 | 0 | 12
38904.5375 | 1 | 0 | 12
38904.5377 | 1 | 0 | 12
38904.5379 | 1 | 0 | 12
38904.5381 | 1 | 0 | 12
38904.5383 | 1 | 0 | 12
38904.5385 | 1 | 0 | 12
38904.5387 | 1 | 0 | 12
38904.5389 | 2 | 0 | 12
38904.5391 | 1 | 0 | 12
38904.5392 | 1 | 0 | 12
38904.5394 | 1 | 0 | 12
38904.5396 | 1 | 0 | 12
38904.5398 | 1 | 0 | 12
38904.54 | 1 | 0 | 12
38904.5402 | 1 | 0 | 12
38904.5404 | 1 | 0 | 12
38904.5406 | 1 | 0 | 12
38904.5408 | 1 | 0 | 12
38904.541 | 1 | 0 | 12
38904.5412 | 1 | 0 | 12
38904.5414 | 1 | 0 | 12
38904.5416 | 1 | 0 | 12
38904.5418 | 1 | 0 | 12
38904.542 | 1 | 0 | 12
38904.5422 | 1 | 0 | 12
38904.5423 | 1 | 0 | 12
38904.5425 | 1 | 0 | 12
38904.5427 | 1 | 0 | 12
38904.5429 | 1 | 0 | 12
38904.5431 | 1 | 0 | 12
38904.5433 | 1 | 0 | 12
38904.5435 | 1 | 0 | 12
38904.5437 | 1 | 0 | 12
38904.5439 | 1 | 0 | 12
38904.5441 | 1 | 0 | 12
38904.5443 | 1 | 0 | 12
38904.5445 | 1 | 0 | 12
38904.5447 | 1 | 0 | 12
38904.5449 | 1 | 0 | 12
38904.5451 | 1 | 0 | 12
38904.5453 | 1 | 0 | 12
38904.5455 | 1 | 0 | 12
38904.5457 | 1 | 0 | 12
38904.5458 | 1 | 0 | 12
38904.546 | 7 | 0 | 12
38904.5462 | 8 | 0 | 12
38904.5464 | 9 | 0 | 12
38904.5466 | 10 | 0 | 12
38904.5468 | 9 | 0 | 12
38904.547 | 10 | 0 | 12
38904.5472 | 9 | 0 | 12
38904.5474 | 9 | 0 | 12
38904.5476 | 9 | 0 | 12
38904.5478 | 9 | 0 | 12
38904.548 | 10 | 0 | 12
38904.5482 | 10 | 0 | 12
38904.5484 | 2078 | 0 | 12
38904.5486 | 2168 | 0 | 12
38904.5488 | 2327 | 0 | 12
38904.549 | 2114 | 0 | 12
38904.5492 | 2500 | 0 | 12
38904.5494 | 1978 | 0 | 12
38904.5495 | 2501 | 0 | 12
38904.5497 | 2069 | 0 | 12
38904.5499 | 2330 | 0 | 12
38904.5501 | 1962 | 0 | 12
38904.5503 | 2463 | 0 | 12
38904.5505 | 2438 | 0 | 12
38904.5507 | 2207 | 0 | 12
38904.5509 | 2285 | 0 | 12
38904.5511 | 2508 | 0 | 12
38904.5513 | 2549 | 0 | 12
38904.5515 | 2158 | 0 | 12
38904.5517 | 2189 | 0 | 12
38904.5519 | 2382 | 0 | 12
38904.5521 | 2494 | 0 | 12