## Test Facts
Last row in IRMS data sheets: | 214
Time when Penlight power was initiated: | 147
Conduit dimensions/material: | OD = 2 - 7/8" (2.875") (73.0 mm)
ID = 2-1/2" (2.5") (63 mm)
wall thickness = 3/16" (0.1875") (4.76 mm)
Material = Hot-dipped galvinized steel standard rigid metal conduit
Length = 5' (1524 mm)

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 7
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures, and four cable temperatures (see maps). Shroud power: Initiated after 147 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
147 | 0 | Initiate Penlight Heating
2481 | 2334 | C2 shorts to drain wire at less than 1000 ohms (335) | All conductors initially showed interactions with the un-insulated drain wire beginning with conductor 2 followed by conductor 1 within 30 seconds.
2497 | 2350 | C2-Drain Short drops below 100 ohms and holds there
2509 | 2362 | C1-Drain short below 1000 ohms
2520 | 2373 | C1-C2-Drain have formed mutual short below 100 ohms
2546 | 2399 | C3 joins intra-cable short group at less than 1000 ohms | Eventually the three conductors and drain formed an intra-cable short independent of the external ground.
2556 | 2409 | C3 to group resistance below 100 ohms, all intra-cable conductors have shorted together with drain wire - resistances are less than 100 ohms
2577-2808 | 2430-2661 | All conductors and drain wire showing intermitent shorts to external ground at less than 1000 ohms | Intermitent shorts to the external ground at between 100 and 1000 ohms were detected beginning approximately 80 seconds after formation of the first solid (less than 100 ohm) intra-cable short.
2825 | 2678 | The drain wire and all conductors except #3 showing steady short to ground at less than 100 ohms. Conductor 3 never forms a hard short (less than 100 ohms) to ground. | Hard shorts (less than 100 ohms) to the external ground were detected approximately 328 seconds (5.5 minutes) after the first intra-cable short circuit of less than 100 ohms had formed.
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | This test followed an expected behavior that has been observed in previous testing (NUREG/CR-5546). The drain wire is within the cable jacket, but is not insulated. This makes it more likely that intra-cable shorting will occur between a conductor and the drain wire rather than between two insulated conductors simply because there is less electrical insulation separating the wires.

## Thermocouple Maps
Locations for Thermocouples on conduit, on cable, and within cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Conduit outer surface, outboard from center
| TC2 | = | Conduit 2 | Conduit outer surface, center
| TC3 | = | Conduit 3 | Conduit ourter surface, outboard from center opposite side
| TC4 | = | Cable 4 | Within cable just below cable jacket, center position
| TC5 | = | Cable 5 | At cable core between conductors, center position
| TC6 | = | Cable 6 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC7 | = | Cable 7 | On outer cable surface, outboard from cable center
| TC8 | = | Cable 8 | On outer cable surface, outboard from cable center

## C-G Min
Minimum Conductor to Ground Resistances
Penlight Test 7 |  |  | 2006-07-06 | 14:56
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 | [5 empty] | 4 is Drain Wire
Penlight Time | Minimum C1-G | Penlight Time | Minimum C2-G |  | Penlight Time | Minimum C3-G | Penlight Time | Minimum C4-G | Penlight Time | Minimum Overall
-143.6667 | 242838 | -140 | 245038 |  | -138 | 242838 | -136.3333 | 244038 | -143.6667 | 242838
-126.8333 | 122669 | -123.1667 | 245038 |  | -121.3333 | 242838 | -119.3333 | 244038 | -126.8333 | 122669
-110.3333 | 242838 | -106.3333 | 245038 |  | -104.6667 | 242838 | -102.6667 | 122719 | -110.3333 | 122719
-93.3333 | 242838 | -89.6667 | 245038 |  | -87.8333 | 121369 | -85.8333 | 244038 | -93.3333 | 121369
-76.5 | 242838 | -72.8333 | 122919 |  | -71 | 242838 | -69 | 244038 | -76.5 | 122919
-59.6667 | 242838 | -56.1667 | 245038 |  | -54.1667 | 242838 | -52.3333 | 244038 | -59.6667 | 242838
-42.8333 | 242838 | -39.1667 | 245038 |  | -37.3333 | 242838 | -35.3333 | 121969 | -42.8333 | 121969
-26.1667 | 242838 | -22.5 | 245038 |  | -20.5 | 122469 | -18.8333 | 244038 | -26.1667 | 122469
-9.3333 | 121369 | -5.6667 | 245038 |  | -3.8333 | 242838 | -1.8333 | 244038 | -9.3333 | 121369
7.3333 | 242838 | 11.1667 | 245038 |  | 13 | 242838 | 14.8333 | 244038 | 7.3333 | 242838
24.1667 | 242838 | 27.8333 | 245038 |  | 29.6667 | 242838 | 31.6667 | 122919 | 24.1667 | 122919
41.1667 | 242838 | 44.8333 | 245038 |  | 46.5 | 242838 | 48.5 | 121969 | 41.1667 | 121969
57.8333 | 242838 | 61.6667 | 245038 |  | 63.5 | 242838 | 65.3333 | 244038 | 57.8333 | 242838
74.6667 | 242838 | 78.3333 | 245038 |  | 80.1667 | 242838 | 82.1667 | 244038 | 74.6667 | 242838
91.5 | 122719 | 95 | 245038 |  | 97 | 242838 | 98.8333 | 244038 | 91.5 | 122719
108.1667 | 242838 | 112 | 122919 |  | 113.8333 | 242838 | 115.6667 | 244038 | 108.1667 | 122919
125.1667 | 242838 | 128.8333 | 122919 |  | 130.5 | 242838 | 132.5 | 244038 | 125.1667 | 122919
141.8333 | 242838 | 145.6667 | 245038 |  | 147.5 | 242838 | 149.3333 | 244038 | 141.8333 | 242838
158.5 | 242838 | 162.3333 | 245038 |  | 164.1667 | 242838 | 166 | 244038 | 158.5 | 242838
175.5 | 242838 | 179.1667 | 245038 |  | 181 | 242838 | 183 | 244038 | 175.5 | 242838
192.1667 | 242838 | 196 | 245038 |  | 197.8333 | 242838 | 199.6667 | 121969 | 192.1667 | 121969
209 | 242838 | 212.8333 | 245038 |  | 214.6667 | 242838 | 216.5 | 244038 | 209 | 242838
225.8333 | 242838 | 229.5 | 245038 |  | 231.5 | 242838 | 233.1667 | 244038 | 225.8333 | 242838
242.6667 | 242838 | 246.5 | 245038 |  | 248.3333 | 242838 | 250.1667 | 244038 | 242.6667 | 242838
259.3333 | 242838 | 263.1667 | 245038 |  | 265 | 242838 | 266.8333 | 244038 | 259.3333 | 242838
276.1667 | 242838 | 279.8333 | 245038 |  | 281.6667 | 242838 | 283.6667 | 244038 | 276.1667 | 242838
293 | 242838 | 296.8333 | 245038 |  | 298.5 | 122469 | 300.3333 | 244038 | 293 | 122469
309.8333 | 242838 | 313.6667 | 245038 |  | 315.5 | 242838 | 317.3333 | 244038 | 309.8333 | 242838
326.5 | 242838 | 330.3333 | 245038 |  | 332.1667 | 242838 | 334 | 244038 | 326.5 | 242838
343.5 | 122669 | 347 | 245038 |  | 349 | 242838 | 350.8333 | 244038 | 343.5 | 122669
360.1667 | 242838 | 363.8333 | 245038 |  | 365.6667 | 242838 | 367.6667 | 244038 | 360.1667 | 242838
377 | 242838 | 380.8333 | 245038 |  | 382.6667 | 242838 | 384.5 | 244038 | 377 | 242838
393.6667 | 242838 | 397.5 | 245038 |  | 399.3333 | 242838 | 401.1667 | 244038 | 393.6667 | 242838
410.6667 | 242838 | 414.3333 | 245038 |  | 416 | 242838 | 418 | 244038 | 410.6667 | 242838
427.5 | 242838 | 431 | 122919 |  | 433 | 242838 | 434.8333 | 244038 | 427.5 | 122919
444.1667 | 242838 | 448 | 245038 |  | 449.8333 | 242838 | 451.6667 | 244038 | 444.1667 | 242838
461 | 242838 | 464.6667 | 245038 |  | 466.5 | 242838 | 468.5 | 244038 | 461 | 242838
477.6667 | 242838 | 481.5 | 245038 |  | 483.3333 | 242838 | 485.1667 | 244038 | 477.6667 | 242838
494.6667 | 242838 | 498.3333 | 245038 |  | 500 | 242838 | 502 | 244038 | 494.6667 | 242838
511.3333 | 122669 | 515 | 122919 |  | 517 | 121969 | 518.6667 | 244038 | 511.3333 | 121969
528.3333 | 242838 | 531.8333 | 245038 |  | 533.8333 | 242838 | 535.6667 | 244038 | 528.3333 | 242838
545 | 242838 | 548.8333 | 122669 |  | 550.6667 | 242838 | 552.5 | 244038 | 545 | 122669
561.6667 | 242838 | 565.5 | 245038 |  | 567.3333 | 242838 | 569.1667 | 244038 | 561.6667 | 242838
578.5 | 242838 | 582.1667 | 245038 |  | 584 | 242838 | 586 | 244038 | 578.5 | 242838
595.3333 | 242838 | 599 | 245038 |  | 601 | 242838 | 602.6667 | 244038 | 595.3333 | 242838
612.1667 | 242838 | 616 | 245038 |  | 617.8333 | 242838 | 619.6667 | 244038 | 612.1667 | 242838
628.8333 | 242838 | 632.6667 | 122669 |  | 634.5 | 242838 | 636.3333 | 244038 | 628.8333 | 122669
645.6667 | 242838 | 649.5 | 245038 |  | 651.3333 | 121369 | 653.1667 | 122919 | 645.6667 | 121369
662.5 | 242838 | 666.1667 | 245038 |  | 668 | 242838 | 670 | 244038 | 662.5 | 242838
679.3333 | 242838 | 683 | 245038 |  | 685 | 242838 | 686.6667 | 244038 | 679.3333 | 242838
696.1667 | 242838 | 699.8333 | 245038 |  | 701.6667 | 242838 | 703.6667 | 244038 | 696.1667 | 242838
712.8333 | 242838 | 716.6667 | 245038 |  | 718.5 | 242838 | 720.3333 | 244038 | 712.8333 | 242838
729.6667 | 242838 | 733.5 | 245038 |  | 735.3333 | 242838 | 737.1667 | 244038 | 729.6667 | 242838
746.5 | 242838 | 750.1667 | 245038 |  | 752 | 242838 | 754 | 244038 | 746.5 | 242838
763.3333 | 242838 | 767 | 245038 |  | 769 | 242838 | 770.6667 | 244038 | 763.3333 | 242838
780.1667 | 242838 | 783.8333 | 245038 |  | 785.6667 | 242838 | 787.6667 | 122919 | 780.1667 | 122919
796.8333 | 242838 | 800.6667 | 245038 |  | 802.5 | 242838 | 804.3333 | 122719 | 796.8333 | 122719
813.6667 | 242838 | 817.5 | 245038 |  | 819.3333 | 242838 | 821.1667 | 244038 | 813.6667 | 242838
830.5 | 242838 | 834.1667 | 245038 |  | 836 | 242838 | 838 | 244038 | 830.5 | 242838
847.3333 | 242838 | 851 | 245038 |  | 853 | 242838 | 854.6667 | 244038 | 847.3333 | 242838
864.1667 | 242838 | 867.8333 | 245038 |  | 869.6667 | 242838 | 871.6667 | 244038 | 864.1667 | 242838
880.8333 | 242838 | 884.6667 | 245038 |  | 886.5 | 242838 | 888.3333 | 244038 | 880.8333 | 242838
897.6667 | 242838 | 901.5 | 245038 |  | 903.3333 | 242838 | 905.1667 | 244038 | 897.6667 | 242838
914.5 | 121369 | 918.1667 | 245038 |  | 920 | 242838 | 922 | 244038 | 914.5 | 121369
931.3333 | 242838 | 935 | 245038 |  | 937 | 242838 | 938.6667 | 244038 | 931.3333 | 242838
948.1667 | 242838 | 951.8333 | 245038 |  | 953.6667 | 242838 | 955.6667 | 244038 | 948.1667 | 242838
965 | 242838 | 968.8333 | 245038 |  | 970.5 | 242838 | 972.3333 | 244038 | 965 | 242838
981.6667 | 242838 | 985.5 | 245038 |  | 987.3333 | 242838 | 989.1667 | 244038 | 981.6667 | 242838
998.5 | 242838 | 1002.1667 | 245038 |  | 1004 | 242838 | 1006 | 244038 | 998.5 | 242838
1015.3333 | 242838 | 1019 | 245038 |  | 1021 | 242838 | 1022.6667 | 244038 | 1015.3333 | 242838
1032.1667 | 242838 | 1035.8333 | 245038 |  | 1037.6667 | 242838 | 1039.6667 | 244038 | 1032.1667 | 242838
1048.8333 | 242838 | 1052.6667 | 245038 |  | 1054.5 | 242838 | 1056.3333 | 244038 | 1048.8333 | 242838
1065.6667 | 242838 | 1069.5 | 245038 |  | 1071.3333 | 242838 | 1073.1667 | 244038 | 1065.6667 | 242838
1082.5 | 242838 | 1086.1667 | 245038 |  | 1088 | 242838 | 1090 | 244038 | 1082.5 | 242838
1099.3333 | 242838 | 1103 | 245038 |  | 1105 | 242838 | 1106.6667 | 122919 | 1099.3333 | 122919
1116.1667 | 242838 | 1119.8333 | 245438 |  | 1121.6667 | 242838 | 1123.6667 | 244038 | 1116.1667 | 242838
1132.8333 | 242838 | 1136.6667 | 245038 |  | 1138.5 | 242838 | 1140.3333 | 244038 | 1132.8333 | 242838
1149.6667 | 242838 | 1153.5 | 245038 |  | 1155.3333 | 242838 | 1157.1667 | 122719 | 1149.6667 | 122719
1166.5 | 242838 | 1170.1667 | 245038 |  | 1172 | 242838 | 1174 | 244038 | 1166.5 | 242838
1183.3333 | 242838 | 1187 | 245038 |  | 1189 | 242838 | 1190.6667 | 244038 | 1183.3333 | 242838
1200.1667 | 242838 | 1203.8333 | 245038 |  | 1205.6667 | 242838 | 1207.6667 | 244038 | 1200.1667 | 242838
1216.8333 | 242838 | 1220.6667 | 245038 |  | 1222.5 | 122469 | 1224.3333 | 244038 | 1216.8333 | 122469
1233.6667 | 242838 | 1237.5 | 245038 |  | 1239.3333 | 242838 | 1241.1667 | 244038 | 1233.6667 | 242838
1250.5 | 242838 | 1254.1667 | 245038 |  | 1256 | 242838 | 1258 | 244038 | 1250.5 | 242838
1267.1667 | 242838 | 1271 | 245038 |  | 1272.8333 | 242838 | 1274.6667 | 244038 | 1267.1667 | 242838
1284.1667 | 242838 | 1287.8333 | 245038 |  | 1289.6667 | 242838 | 1291.6667 | 244038 | 1284.1667 | 242838
1300.6667 | 242838 | 1304.6667 | 122469 |  | 1306.3333 | 242838 | 1308.3333 | 122919 | 1300.6667 | 122469
1317.5 | 242838 | 1321.3333 | 245038 |  | 1323.1667 | 122469 | 1325 | 244038 | 1317.5 | 122469
1334.5 | 242838 | 1338 | 245038 |  | 1340 | 242838 | 1341.8333 | 244038 | 1334.5 | 242838
1351.3333 | 242838 | 1355 | 245038 |  | 1357 | 242838 | 1358.6667 | 244038 | 1351.3333 | 242838
1368.1667 | 242838 | 1371.8333 | 245038 |  | 1373.5 | 242838 | 1375.5 | 244038 | 1368.1667 | 242838
1385 | 242838 | 1389 | 245038 |  | 1390.3333 | 242838 | 1392.3333 | 122919 | 1385 | 122919
1401.5 | 242838 | 1405.3333 | 245038 |  | 1407.3333 | 242838 | 1409.1667 | 244038 | 1401.5 | 242838
1418.5 | 242838 | 1422.1667 | 245038 |  | 1424 | 242838 | 1426 | 244038 | 1418.5 | 242838
1435.1667 | 242838 | 1439 | 245038 |  | 1440.8333 | 242838 | 1442.6667 | 244038 | 1435.1667 | 242838
1452 | 242838 | 1455.6667 | 245038 |  | 1457.5 | 242838 | 1459.5 | 244038 | 1452 | 242838
1468.8333 | 242838 | 1472.5 | 245038 |  | 1474.5 | 242838 | 1476.1667 | 244038 | 1468.8333 | 242838
1485.6667 | 242838 | 1489.5 | 245038 |  | 1491.1667 | 242838 | 1493 | 244038 | 1485.6667 | 242838
1502.3333 | 242838 | 1506.1667 | 245038 |  | 1508 | 242838 | 1509.8333 | 244038 | 1502.3333 | 242838
1519.3333 | 242838 | 1522.8333 | 245038 |  | 1524.8333 | 242838 | 1526.6667 | 244038 | 1519.3333 | 242838
1536 | 242838 | 1539.8333 | 245038 |  | 1541.6667 | 242838 | 1543.5 | 244038 | 1536 | 242838
1552.6667 | 242838 | 1556.5 | 245038 |  | 1558.3333 | 242838 | 1560.1667 | 244038 | 1552.6667 | 242838
1569.5 | 242838 | 1573.3333 | 245038 |  | 1575.1667 | 242838 | 1577 | 244038 | 1569.5 | 242838
1586.3333 | 242838 | 1590.1667 | 245038 |  | 1592 | 242838 | 1593.8333 | 244038 | 1586.3333 | 242838
1603.1667 | 242838 | 1607 | 245438 |  | 1608.8333 | 242838 | 1610.6667 | 244038 | 1603.1667 | 242838
1619.8333 | 242838 | 1623.6667 | 245038 |  | 1625.5 | 242838 | 1627.3333 | 244038 | 1619.8333 | 242838
1636.8333 | 242838 | 1640.5 | 245038 |  | 1642.5 | 242838 | 1644.1667 | 244038 | 1636.8333 | 242838
1653.3333 | 242838 | 1657.1667 | 245038 |  | 1659 | 242838 | 1660.8333 | 244038 | 1653.3333 | 242838
1670.3333 | 242838 | 1674 | 122669 |  | 1676 | 242838 | 1677.6667 | 244038 | 1670.3333 | 122669
1687.1667 | 242838 | 1690.8333 | 245038 |  | 1692.6667 | 242838 | 1694.6667 | 244038 | 1687.1667 | 242838
1703.8333 | 242838 | 1707.6667 | 245038 |  | 1709.5 | 242838 | 1711.3333 | 244038 | 1703.8333 | 242838
1720.8333 | 242838 | 1724.5 | 245038 |  | 1726.5 | 242838 | 1728.1667 | 244038 | 1720.8333 | 242838
1737.6667 | 242838 | 1741.5 | 245438 |  | 1743.1667 | 242838 | 1745 | 244038 | 1737.6667 | 242838
1754.5 | 242838 | 1758 | 245038 |  | 1760 | 242838 | 1761.8333 | 244038 | 1754.5 | 242838
1771.1667 | 242838 | 1774.8333 | 245038 |  | 1776.6667 | 242838 | 1778.6667 | 244038 | 1771.1667 | 242838
1788 | 242838 | 1791.6667 | 245038 |  | 1793.5 | 242838 | 1795.5 | 244038 | 1788 | 242838
1804.6667 | 242838 | 1808.5 | 122919 |  | 1810.3333 | 242838 | 1812.1667 | 244038 | 1804.6667 | 122919
1821.6667 | 242838 | 1825.3333 | 245038 |  | 1827 | 242838 | 1829 | 244038 | 1821.6667 | 242838
1838.5 | 242838 | 1842 | 245038 |  | 1844 | 242838 | 1845.8333 | 244038 | 1838.5 | 242838
1855.1667 | 242838 | 1858.6667 | 245038 |  | 1860.5 | 242838 | 1862.6667 | 244038 | 1855.1667 | 242838
1871.8333 | 242838 | 1875.6667 | 245038 |  | 1877.5 | 242838 | 1879.3333 | 244038 | 1871.8333 | 242838
1888.6667 | 242838 | 1892.5 | 245038 |  | 1894.3333 | 242838 | 1896.1667 | 244038 | 1888.6667 | 242838
1905.5 | 242838 | 1909.1667 | 245038 |  | 1911 | 242838 | 1913 | 244038 | 1905.5 | 242838
1922.3333 | 242838 | 1926 | 245038 |  | 1928 | 242838 | 1929.6667 | 244038 | 1922.3333 | 242838
1939.1667 | 242838 | 1942.8333 | 245038 |  | 1944.6667 | 242838 | 1946.6667 | 244038 | 1939.1667 | 242838
1955.8333 | 242838 | 1959.6667 | 245038 |  | 1961.5 | 242838 | 1963.3333 | 244038 | 1955.8333 | 242838
1972.6667 | 242838 | 1976.5 | 245038 |  | 1978.3333 | 242838 | 1980.1667 | 244038 | 1972.6667 | 242838
1989.5 | 242838 | 1993.1667 | 245038 |  | 1995 | 242838 | 1997 | 244038 | 1989.5 | 242838
2006.3333 | 242838 | 2010 | 245038 |  | 2012 | 242838 | 2013.6667 | 244038 | 2006.3333 | 242838
2023.1667 | 242838 | 2026.8333 | 245038 |  | 2028.6667 | 242838 | 2030.6667 | 244038 | 2023.1667 | 242838
2039.8333 | 242838 | 2043.6667 | 245038 |  | 2045.5 | 242838 | 2047.3333 | 244038 | 2039.8333 | 242838
2056.6667 | 242838 | 2060.5 | 245038 |  | 2062.3333 | 242838 | 2064.1667 | 244038 | 2056.6667 | 242838
2073.5 | 242838 | 2077.1667 | 245038 |  | 2079 | 242838 | 2081 | 244038 | 2073.5 | 242838
2090.3333 | 242838 | 2094 | 245038 |  | 2096 | 242838 | 2097.6667 | 244038 | 2090.3333 | 242838
2107.1667 | 242838 | 2110.8333 | 245038 |  | 2112.6667 | 122469 | 2114.6667 | 244038 | 2107.1667 | 122469
2123.8333 | 242838 | 2127.6667 | 245038 |  | 2129.5 | 242838 | 2131.3333 | 244038 | 2123.8333 | 242838
2140.6667 | 242838 | 2144.5 | 245038 |  | 2146.3333 | 242838 | 2148.1667 | 244038 | 2140.6667 | 242838
2157.5 | 242838 | 2161.1667 | 245038 |  | 2163 | 121969 | 2165 | 244038 | 2157.5 | 121969
2174.3333 | 242838 | 2178 | 245038 |  | 2180 | 121969 | 2181.6667 | 244038 | 2174.3333 | 121969
2191.1667 | 242838 | 2194.8333 | 245038 |  | 2196.6667 | 242838 | 2198.6667 | 244038 | 2191.1667 | 242838
2207.8333 | 242838 | 2211.6667 | 245038 |  | 2213.5 | 242838 | 2215.3333 | 244038 | 2207.8333 | 242838
2224.6667 | 242838 | 2228.5 | 245038 |  | 2230.3333 | 242838 | 2232.1667 | 244038 | 2224.6667 | 242838
2241.5 | 242838 | 2245.1667 | 245038 |  | 2247 | 242838 | 2249 | 244038 | 2241.5 | 242838
2258.3333 | 242838 | 2262 | 245038 |  | 2264 | 242838 | 2265.6667 | 122719 | 2258.3333 | 122719
2275.1667 | 242838 | 2278.6667 | 245038 |  | 2280.5 | 242838 | 2282.6667 | 244038 | 2275.1667 | 242838
2291.8333 | 242838 | 2295.6667 | 245038 |  | 2297.5 | 242838 | 2299.3333 | 122719 | 2291.8333 | 122719
2308.6667 | 122669 | 2312.5 | 245038 |  | 2314.3333 | 242838 | 2316.1667 | 9012.5185 | 2308.6667 | 9012.5185
2325.5 | 242838 | 2329.1667 | 5345.2097 |  | 2331 | 27131.2093 | 2333 | 15256.6878 | 2325.5 | 5345.2097
2342.3333 | 242838 | 2346 | 33715.8178 |  | 2348 | 18839.3646 | 2349.6667 | 9117.2943 | 2342.3333 | 9117.2943
2359.1667 | 9752.5345 | 2362.8333 | 2425.3671 |  | 2364.6667 | 20421.0452 | 2366.6667 | 2706.4695 | 2359.1667 | 2425.3671
2375.8333 | 1826.6402 | 2379.6667 | 4535.5138 |  | 2381.5 | 20446.3546 | 2383.3333 | 2787.3372 | 2375.8333 | 1826.6402
2392.6667 | 2016.5487 | 2396.5 | 4438.4362 |  | 2398.3333 | 2030.7946 | 2400.1667 | 3720.7632 | 2392.6667 | 2016.5487
2409.5 | 1860.883 | 2413.1667 | 1226.7203 |  | 2415 | 2772.3279 | 2417 | 2247.9487 | 2409.5 | 1226.7203
2426.3333 | 2864.0083 | 2430 | 626.9302 |  | 2432 | 1028.5311 | 2433.6667 | 486.7165 | 2426.3333 | 486.7165
2443.1667 | 565.1146 | 2446.8333 | 1223.883 |  | 2448.6667 | 1802.8776 | 2450.6667 | 629.3077 | 2443.1667 | 565.1146
2459.8333 | 606.2004 | 2463.6667 | 1112.2804 |  | 2465.5 | 913.3735 | 2467.3333 | 1497.1099 | 2459.8333 | 606.2004
2476.6667 | 1519.5577 | 2480.5 | 1090.4939 |  | 2482.3333 | 630.3016 | 2484.1667 | 854.8162 | 2476.6667 | 630.3016
2493.5 | 172.3416 | 2497.1667 | 280.0936 |  | 2499 | 212.8667 | 2501 | 766.4378 | 2493.5 | 172.3416
2510.3333 | 1713.9116 | 2514 | 2845.7197 |  | 2516 | 2069.7848 | 2517.6667 | 1912.5099 | 2510.3333 | 1713.9116
2527.1667 | 1356.9196 | 2530.8333 | 2603.1092 |  | 2532.6667 | 368.5522 | 2534.6667 | 468.7996 | 2527.1667 | 368.5522
2543.8333 | 340.6223 | 2547.6667 | 996.2335 |  | 2549.5 | 2945.1225 | 2551.3333 | 895.7178 | 2543.8333 | 340.6223
2560.6667 | 466.8092 | 2564.5 | 1148.9155 |  | 2566.3333 | 799.6176 | 2568.1667 | 475.5254 | 2560.6667 | 466.8092
2577.5 | 350.2142 | 2581.1667 | 2016.3623 |  | 2583 | 421.9206 | 2585 | 590.6084 | 2577.5 | 350.2142
2594.3333 | 2639.0789 | 2598 | 1196.0906 |  | 2600 | 1304.5117 | 2601.6667 | 851.3238 | 2594.3333 | 851.3238
2611.1667 | 330.8986 | 2614.6667 | 734.1018 |  | 2616.6667 | 1118.3153 | 2618.5 | 239.899 | 2611.1667 | 239.899
2627.8333 | 1165.3145 | 2631.6667 | 257.9792 |  | 2633.5 | 439.174 | 2635.3333 | 1385.7685 | 2627.8333 | 257.9792
2644.6667 | 521.3504 | 2648.5 | 509.2961 |  | 2650.3333 | 803.7534 | 2652.1667 | 706.8134 | 2644.6667 | 509.2961
2661.5 | 259.8308 | 2665 | 1607.755 |  | 2667 | 1397.6706 | 2668.8333 | 670.2822 | 2661.5 | 259.8308
2678.3333 | 30.4542 | 2682 | 7.8987 |  | 2684 | 392.8894 | 2685.6667 | 2.9576 | 2678.3333 | 2.9576
2695.1667 | 3.1327 | 2698.8333 | 5.9331 |  | 2700.6667 | 407.4561 | 2702.6667 | 4.4146 | 2695.1667 | 3.1327
2711.8333 | 7.8319 | 2715.6667 | 2.9276 |  | 2717.5 | 520.6684 | 2719.3333 | 17.9368 | 2711.8333 | 2.9276
2728.6667 | 2.8041 | 2732.3333 | 9.7153 |  | 2734.1667 | 987.5948 | 2736.1667 | 1.3177 | 2728.6667 | 1.3177
2745.3333 | 6.5735 | 2749.1667 | 4.0168 |  | 2751 | 1240.273 | 2752.8333 | 23.8696 | 2745.3333 | 4.0168
2762.3333 | 1.7375 | 2766 | 2.166 |  | 2768 | 527.2703 | 2769.6667 | 11.5941 | 2762.3333 | 1.7375
2779 | 1.7799 | 2782.8333 | 2.5311 |  | 2784.6667 | 724.4734 | 2786.5 | 2.8721 | 2779 | 1.7799
2795.8333 | 7.3205 | 2799.6667 | 12.6321 |  | 2801.5 | 3600.7841 | 2803.3333 | 24.5674 | 2795.8333 | 7.3205
2812.6667 | 5.3617 | 2816.3333 | 1.559 |  | 2818 | 370.1666 | 2820 | 1.4451 | 2812.6667 | 1.4451
2829.5 | 8.2805 | 2833 | 1.1311 |  | 2835 | 721.9873 | 2836.8333 | 11.4959 | 2829.5 | 1.1311
2846.3333 | 2.8803 | 2849.8333 | 3.5372 |  | 2851.8333 | 117.7268 | 2853.6667 | 17.9099 | 2846.3333 | 2.8803
2863.1667 | 4.5206 | 2866.8333 | 0.8982 |  | 2868.6667 | 12616.3795 | 2870.6667 | 23.5571 | 2863.1667 | 0.8982
2879.6667 | 8.6983 | 2883.5 | 1.9882 |  | 2885.3333 | 34026.6803 | 2887.1667 | 1.0236 | 2879.6667 | 1.0236
2896.6667 | 5.676 | 2900.3333 | 0.674 |  | 2902.1667 | 5915.5247 | 2904.1667 | 2.6829 | 2896.6667 | 0.674
2913.3333 | 7.7398 | 2917 | 13.6076 |  | 2919 | 11095.8966 | 2920.6667 | 2.0049 | 2913.3333 | 2.0049
2930.3333 | 5.1956 | 2933.8333 | 10.7357 |  | 2935.8333 | 910.3135 | 2937.6667 | 9.1919 | 2930.3333 | 5.1956
2946.8333 | 2.6515 | 2950.6667 | 1.7274 |  | 2952.6667 | 8019.8204 | 2954.5 | 1.7145 | 2946.8333 | 1.7145
2963.6667 | 9.7325 | 2967.6667 | 0.75562 |  | 2969.3333 | 13814.2938 | 2971.3333 | 6.7883 | 2963.6667 | 0.75562
2980.5 | 10.0353 | 2984.1667 | 0.92136 |  | 2986 | 2251.9538 | 2988 | 0.71827 | 2980.5 | 0.71827
2997.5 | 1.8473 | 3001 | 0.83916 |  | 3003 | 44794.4474 | 3004.8333 | 8.3674 | 2997.5 | 0.83916
3014.3333 | 2.0154 | 3017.8333 | 8.6161 |  | 3019.8333 | 32163.1909 | 3021.6667 | 6.6909 | 3014.3333 | 2.0154
3031 | 2.1186 | 3034.8333 | 1.7271 |  | 3036.5 | 5742.3867 | 3038.3333 | 7.0632 | 3031 | 1.7271
3047.6667 | 5.2557 | 3051.5 | 0.8812 |  | 3053.3333 | 1589.0062 | 3055.1667 | 18.5684 | 3047.6667 | 0.8812
3064.5 | 1.1825 | 3068.1667 | 24.1988 |  | 3070 | 3045.6811 | 3072 | 21.3419 | 3064.5 | 1.1825
3081.3333 | 2.2692 | 3085.1667 | 5.0763 |  | 3087 | 16636.0028 | 3088.8333 | 2.7362 | 3081.3333 | 2.2692
3098.1667 | 3.6883 | 3102 | 4.2271 |  | 3103.8333 | 10959.1416 | 3105.6667 | 12.5688 | 3098.1667 | 3.6883
3114.8333 | 2.2264 | 3118.6667 | 18.2821 |  | 3120.5 | 5738.4334 | 3122.3333 | 2.671 | 3114.8333 | 2.2264
3131.6667 | 0.67909 | 3135.6667 | 5.9784 |  | 3137.3333 | 1703.5305 | 3139.3333 | 15.8054 | 3131.6667 | 0.67909
3148.5 | 12.6336 | 3152.1667 | 1.0651 |  | 3154 | 61918.8006 | 3156 | 0.7097 | 3148.5 | 0.7097
3165.3333 | 15086.299 | 3169.1667 | 0.67295 |  | 3171 | 1691.8321 | 3172.8333 | 10.3208 | 3165.3333 | 0.67295
3182.5 | 4619.7346 | 3185.8333 | 4.0059 |  | 3188 | 7670.2603 | 3189.6667 | 3.6018 | 3182.5 | 3.6018
3198.8333 | 25122.5518 | 3202.6667 | 5.8937 |  | 3204.5 | 18865.7098 | 3206.3333 | 11.7752 | 3198.8333 | 5.8937
3215.6667 | 36139.0019 | 3219.5 | 9.0997 |  | 3221.3333 | 24518.6121 | 3223.1667 | 15.2233 | 3215.6667 | 9.0997
3232.6667 | 2368.3295 | 3236.3333 | 11.6933 |  | 3238 | 48487.6 | 3240 | 1.7174 | 3232.6667 | 1.7174
3249.3333 | 1788.9836 | 3253 | 10.0683 |  | 3255 | 14363.6149 | 3256.6667 | 0.67322 | 3249.3333 | 0.67322
3266.1667 | 748.2538 | 3269.8333 | 11.0276 |  | 3271.6667 | 48269.8515 | 3273.6667 | 1.3358 | 3266.1667 | 1.3358
3282.8333 | 10999.8869 | 3286.6667 | 1.7142 |  | 3288.5 | 24583.1582 | 3290.3333 | 5.1828 | 3282.8333 | 1.7142
3299.6667 | 13388.3961 | 3303.5 | 9.7622 |  | 3305.3333 | 48487.6 | 3307.1667 | 3.8724 | 3299.6667 | 3.8724
3316.5 | 3920.9492 | 3320.1667 | 4.4048 |  | 3322 | 1692.0603 | 3324 | 0.71434 | 3316.5 | 0.71434
3333.3333 | 6105.1644 | 3337 | 8.1075 |  | 3339 | 34507.9971 | 3340.6667 | 1.8471 | 3333.3333 | 1.8471
3350.1667 | 3233.0181 | 3353.8333 | 1.5912 |  | 3355.6667 | 48927.6 | 3357.6667 | 1.3923 | 3350.1667 | 1.3923

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 7 |  |  | 2006-07-06 | 14:56
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 | [10 empty] | All Including Drain Wire |  | Excluding Drain Wire |  | Conductor to Drain Only
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums | Penlight Time | Minimums (Cond-Cond) | Penlight Time | Minimum (Cond-Drain)
-146.5 | 245437.9994 | -143.5 | 242837.9994 | -141 | 245537.9994 | -138 | 245037.9994 | -135.5 | 245937.9994 | -132.5 | 244037.9994 | -146.5 | 242837.9994 | -146.5 | 242837.9994 | -146.5 | 244037.9994
-129.5 | 122668.9988 | -127 | 242837.9994 | -124 | 245537.9994 | -121.5 | 245037.9994 | -118.5 | 245937.9994 | -115.5 | 244037.9994 | -129.5 | 122668.9988 | -129.5 | 122668.9988 | -129.5 | 244037.9994
-113 | 245437.9994 | -110.5 | 242837.9994 | -107.5 | 245537.9994 | -104.5 | 245037.9994 | -101.5 | 245937.9994 | -99 | 244037.9994 | -113 | 242837.9994 | -113 | 242837.9994 | -113 | 244037.9994
-96 | 245437.9994 | -93.5 | 242837.9994 | -90.5 | 245537.9994 | -88 | 245037.9994 | -85 | 245937.9994 | -82 | 244037.9994 | -96 | 242837.9994 | -96 | 242837.9994 | -96 | 244037.9994
-79.5 | 245437.9994 | -76.5 | 242837.9994 | -73.5 | 245537.9994 | -71 | 245037.9994 | -68 | 122918.9988 | -65.5 | 244037.9994 | -79.5 | 122918.9988 | -79.5 | 242837.9994 | -79.5 | 122918.9988
-62.5 | 245437.9994 | -59.5 | 242837.9994 | -57 | 245537.9994 | -54.5 | 245037.9994 | -51.5 | 245937.9994 | -48.5 | 244037.9994 | -62.5 | 242837.9994 | -62.5 | 242837.9994 | -62.5 | 244037.9994
-45.5 | 245437.9994 | -43 | 242837.9994 | -40 | 245537.9994 | -37.5 | 245037.9994 | -34.5 | 245937.9994 | -31.5 | 244037.9994 | -45.5 | 242837.9994 | -45.5 | 242837.9994 | -45.5 | 244037.9994
-29 | 245437.9994 | -26 | 242837.9994 | -23.5 | 245537.9994 | -20.5 | 245037.9994 | -18 | 245937.9994 | -15 | 244037.9994 | -29 | 242837.9994 | -29 | 242837.9994 | -29 | 244037.9994
-12 | 245437.9994 | -9.5 | 121368.9988 | -6.5 | 245537.9994 | -4 | 245037.9994 | -1 | 245937.9994 | 2 | 244037.9994 | -12 | 121368.9988 | -12 | 121368.9988 | -12 | 244037.9994
4.5 | 245437.9994 | 7.5 | 242837.9994 | 10 | 245537.9994 | 13 | 245037.9994 | 16 | 245937.9994 | 18.5 | 244037.9994 | 4.5 | 242837.9994 | 4.5 | 242837.9994 | 4.5 | 244037.9994
21.5 | 245437.9994 | 24 | 242837.9994 | 27 | 245537.9994 | 29.5 | 245037.9994 | 32.5 | 245937.9994 | 35.5 | 244037.9994 | 21.5 | 242837.9994 | 21.5 | 242837.9994 | 21.5 | 244037.9994
38.5 | 245437.9994 | 41 | 242837.9994 | 44 | 245537.9994 | 46.5 | 245037.9994 | 49.5 | 245937.9994 | 52 | 244037.9994 | 38.5 | 242837.9994 | 38.5 | 242837.9994 | 38.5 | 244037.9994
55 | 245437.9994 | 58 | 242837.9994 | 60.5 | 245537.9994 | 63.5 | 245037.9994 | 66.5 | 245937.9994 | 69 | 244037.9994 | 55 | 242837.9994 | 55 | 242837.9994 | 55 | 244037.9994
72 | 245437.9994 | 74.5 | 242837.9994 | 77.5 | 245537.9994 | 80 | 245037.9994 | 83 | 245937.9994 | 86 | 244037.9994 | 72 | 242837.9994 | 72 | 242837.9994 | 72 | 244037.9994
88.5 | 245437.9994 | 91.5 | 242837.9994 | 94.5 | 122718.9988 | 97 | 245037.9994 | 99.5 | 245937.9994 | 102.5 | 244037.9994 | 88.5 | 122718.9988 | 88.5 | 242837.9994 | 88.5 | 122718.9988
105.5 | 245437.9994 | 108 | 242837.9994 | 111 | 245537.9994 | 114 | 245037.9994 | 116.5 | 122918.9988 | 119.5 | 244037.9994 | 105.5 | 122918.9988 | 105.5 | 242837.9994 | 105.5 | 122918.9988
122.5 | 245437.9994 | 125 | 242837.9994 | 128 | 245537.9994 | 130.5 | 245037.9994 | 133.5 | 122918.9988 | 136 | 244037.9994 | 122.5 | 122918.9988 | 122.5 | 242837.9994 | 122.5 | 122918.9988
139 | 245437.9994 | 142 | 242837.9994 | 144.5 | 245537.9994 | 147.5 | 245037.9994 | 150.5 | 245937.9994 | 153 | 244037.9994 | 139 | 242837.9994 | 139 | 242837.9994 | 139 | 244037.9994
155.5 | 245437.9994 | 158.5 | 242837.9994 | 161.5 | 245537.9994 | 164.5 | 245037.9994 | 167 | 245937.9994 | 169.5 | 244037.9994 | 155.5 | 242837.9994 | 155.5 | 242837.9994 | 155.5 | 244037.9994
172.5 | 245437.9994 | 175.5 | 242837.9994 | 178.5 | 245537.9994 | 181 | 245037.9994 | 184 | 245937.9994 | 186.5 | 244037.9994 | 172.5 | 242837.9994 | 172.5 | 242837.9994 | 172.5 | 244037.9994
189.5 | 245437.9994 | 192 | 242837.9994 | 195 | 245537.9994 | 198 | 245037.9994 | 200.5 | 245937.9994 | 203.5 | 244037.9994 | 189.5 | 242837.9994 | 189.5 | 242837.9994 | 189.5 | 244037.9994
206.5 | 245437.9994 | 209 | 242837.9994 | 211.5 | 245238.1221 | 214.5 | 245037.9994 | 217.5 | 245937.9994 | 220.5 | 244037.9994 | 206.5 | 242837.9994 | 206.5 | 242837.9994 | 206.5 | 244037.9994
223 | 245437.9994 | 226 | 242837.9994 | 228.5 | 245537.9994 | 231.5 | 245037.9994 | 234 | 245937.9994 | 237 | 244037.9994 | 223 | 242837.9994 | 223 | 242837.9994 | 223 | 244037.9994
240 | 245437.9994 | 242.5 | 242837.9994 | 245.5 | 245537.9994 | 248.5 | 245037.9994 | 251 | 245937.9994 | 254 | 244037.9994 | 240 | 242837.9994 | 240 | 242837.9994 | 240 | 244037.9994
256.5 | 245437.9994 | 259.5 | 242837.9994 | 262 | 245537.9994 | 265 | 245037.9994 | 268 | 245937.9994 | 270.5 | 244037.9994 | 256.5 | 242837.9994 | 256.5 | 242837.9994 | 256.5 | 244037.9994
273.5 | 245437.9994 | 276 | 242837.9994 | 279 | 245537.9994 | 281.5 | 245037.9994 | 284.5 | 245937.9994 | 287.5 | 244037.9994 | 273.5 | 242837.9994 | 273.5 | 242837.9994 | 273.5 | 244037.9994
290.5 | 245437.9994 | 293 | 242837.9994 | 295.5 | 245537.9994 | 298.5 | 245037.9994 | 301.5 | 245937.9994 | 304 | 244037.9994 | 290.5 | 242837.9994 | 290.5 | 242837.9994 | 290.5 | 244037.9994
307 | 245437.9994 | 310 | 242837.9994 | 312.5 | 245537.9994 | 315.5 | 245037.9994 | 318.5 | 245937.9994 | 321 | 244037.9994 | 307 | 242837.9994 | 307 | 242837.9994 | 307 | 244037.9994
323.5 | 245437.9994 | 326.5 | 242837.9994 | 329.5 | 245537.9994 | 332.5 | 245037.9994 | 335 | 245937.9994 | 337.5 | 244037.9994 | 323.5 | 242837.9994 | 323.5 | 242837.9994 | 323.5 | 244037.9994
340.5 | 122668.9988 | 343.5 | 242837.9994 | 346.5 | 245537.9994 | 349 | 245037.9994 | 351.5 | 245937.9994 | 354.5 | 244037.9994 | 340.5 | 122668.9988 | 340.5 | 122668.9988 | 340.5 | 244037.9994
357.5 | 245437.9994 | 360 | 242837.9994 | 363 | 245537.9994 | 365.5 | 245037.9994 | 368.5 | 245937.9994 | 371.5 | 244037.9994 | 357.5 | 242837.9994 | 357.5 | 242837.9994 | 357.5 | 244037.9994
374.5 | 245437.9994 | 377 | 242837.9994 | 379.5 | 245537.9994 | 382.5 | 245037.9994 | 385.5 | 245937.9994 | 388.5 | 244037.9994 | 374.5 | 242837.9994 | 374.5 | 242837.9994 | 374.5 | 244037.9994
391 | 245437.9994 | 393.5 | 242837.9994 | 396.5 | 245537.9994 | 399.5 | 245037.9994 | 402 | 245937.9994 | 405 | 244037.9994 | 391 | 242837.9994 | 391 | 242837.9994 | 391 | 244037.9994
408 | 245437.9994 | 410.5 | 242837.9994 | 413.5 | 245537.9994 | 416 | 245037.9994 | 419 | 245937.9994 | 421.5 | 244037.9994 | 408 | 242837.9994 | 408 | 242837.9994 | 408 | 244037.9994
424.5 | 245437.9994 | 427.5 | 242837.9994 | 430.5 | 245537.9994 | 433 | 245037.9994 | 435.5 | 122918.9988 | 438.5 | 244037.9994 | 424.5 | 122918.9988 | 424.5 | 242837.9994 | 424.5 | 122918.9988
441.5 | 245437.9994 | 444 | 242837.9994 | 447 | 245537.9994 | 450 | 245037.9994 | 452.5 | 245937.9994 | 455.5 | 244037.9994 | 441.5 | 242837.9994 | 441.5 | 242837.9994 | 441.5 | 244037.9994
458 | 245437.9994 | 461 | 242837.9994 | 464 | 245537.9994 | 466.5 | 245037.9994 | 469.5 | 245937.9994 | 472 | 244037.9994 | 458 | 242837.9994 | 458 | 242837.9994 | 458 | 244037.9994
475 | 245437.9994 | 477.5 | 242837.9994 | 480.5 | 245537.9994 | 483.5 | 245037.9994 | 486 | 245937.9994 | 489 | 244037.9994 | 475 | 242837.9994 | 475 | 242837.9994 | 475 | 244037.9994
492 | 245437.9994 | 494.5 | 242837.9994 | 497.5 | 245537.9994 | 500 | 245037.9994 | 503 | 245937.9994 | 505.5 | 244037.9994 | 492 | 242837.9994 | 492 | 242837.9994 | 492 | 244037.9994
508.5 | 122668.9988 | 511.5 | 242837.9994 | 514 | 245537.9994 | 517 | 245037.9994 | 519.5 | 122918.9988 | 522.5 | 121968.9988 | 508.5 | 121968.9988 | 508.5 | 122668.9988 | 508.5 | 121968.9988
525.5 | 245437.9994 | 528.5 | 242837.9994 | 531 | 245537.9994 | 533.5 | 245037.9994 | 536.5 | 245937.9994 | 539.5 | 244037.9994 | 525.5 | 242837.9994 | 525.5 | 242837.9994 | 525.5 | 244037.9994
542.5 | 245437.9994 | 545 | 242837.9994 | 547.5 | 245537.9994 | 550.5 | 245037.9994 | 553.5 | 245937.9994 | 556.5 | 244037.9994 | 542.5 | 242837.9994 | 542.5 | 242837.9994 | 542.5 | 244037.9994
559 | 245437.9994 | 561.5 | 242837.9994 | 564.5 | 245537.9994 | 567.5 | 245037.9994 | 570 | 245937.9994 | 573 | 244037.9994 | 559 | 242837.9994 | 559 | 242837.9994 | 559 | 244037.9994
575.5 | 245437.9994 | 578.5 | 242837.9994 | 581.5 | 245537.9994 | 584 | 245037.9994 | 587 | 245937.9994 | 589.5 | 244037.9994 | 575.5 | 242837.9994 | 575.5 | 242837.9994 | 575.5 | 244037.9994
592.5 | 245437.9994 | 595.5 | 242837.9994 | 598 | 245537.9994 | 601 | 245037.9994 | 603.5 | 245937.9994 | 606.5 | 244037.9994 | 592.5 | 242837.9994 | 592.5 | 242837.9994 | 592.5 | 244037.9994
609.5 | 245437.9994 | 612 | 242837.9994 | 615 | 245537.9994 | 618 | 245037.9994 | 620.5 | 245937.9994 | 623.5 | 244037.9994 | 609.5 | 242837.9994 | 609.5 | 242837.9994 | 609.5 | 244037.9994
626 | 245437.9994 | 629 | 242837.9994 | 631.5 | 245537.9994 | 634.5 | 245037.9994 | 637.5 | 245937.9994 | 640 | 244037.9994 | 626 | 242837.9994 | 626 | 242837.9994 | 626 | 244037.9994
643 | 245437.9994 | 645.5 | 242837.9994 | 648.5 | 245537.9994 | 651.5 | 245037.9994 | 654 | 245937.9994 | 657 | 244037.9994 | 643 | 242837.9994 | 643 | 242837.9994 | 643 | 244037.9994
659.5 | 245437.9994 | 662.5 | 242837.9994 | 665.5 | 245537.9994 | 668 | 245037.9994 | 671 | 245937.9994 | 673.5 | 244037.9994 | 659.5 | 242837.9994 | 659.5 | 242837.9994 | 659.5 | 244037.9994
676.5 | 245437.9994 | 679.5 | 242837.9994 | 682 | 245537.9994 | 685 | 245037.9994 | 687.5 | 245937.9994 | 690.5 | 244037.9994 | 676.5 | 242837.9994 | 676.5 | 242837.9994 | 676.5 | 244037.9994
693.5 | 245437.9994 | 696 | 242837.9994 | 699 | 245537.9994 | 701.5 | 245037.9994 | 704.5 | 245937.9994 | 707.5 | 244037.9994 | 693.5 | 242837.9994 | 693.5 | 242837.9994 | 693.5 | 244037.9994
710 | 245437.9994 | 713 | 242837.9994 | 715.5 | 245537.9994 | 718.5 | 245037.9994 | 721.5 | 245937.9994 | 724 | 244037.9994 | 710 | 242837.9994 | 710 | 242837.9994 | 710 | 244037.9994
727 | 245437.9994 | 729.5 | 242837.9994 | 732.5 | 245537.9994 | 735.5 | 245037.9994 | 738 | 245937.9994 | 741 | 244037.9994 | 727 | 242837.9994 | 727 | 242837.9994 | 727 | 244037.9994
743.5 | 245437.9994 | 746.5 | 242837.9994 | 749.5 | 245537.9994 | 752 | 245037.9994 | 755 | 245937.9994 | 757.5 | 244037.9994 | 743.5 | 242837.9994 | 743.5 | 242837.9994 | 743.5 | 244037.9994
760.5 | 245437.9994 | 763.5 | 242837.9994 | 766 | 245537.9994 | 769 | 245037.9994 | 771.5 | 245937.9994 | 774.5 | 244037.9994 | 760.5 | 242837.9994 | 760.5 | 242837.9994 | 760.5 | 244037.9994
777.5 | 245437.9994 | 780 | 242837.9994 | 783 | 245537.9994 | 785.5 | 245037.9994 | 788.5 | 245937.9994 | 791.5 | 244037.9994 | 777.5 | 242837.9994 | 777.5 | 242837.9994 | 777.5 | 244037.9994
794 | 245437.9994 | 797 | 242837.9994 | 799.5 | 245537.9994 | 802.5 | 245037.9994 | 805.5 | 245937.9994 | 808 | 244037.9994 | 794 | 242837.9994 | 794 | 242837.9994 | 794 | 244037.9994
811 | 245437.9994 | 813.5 | 242837.9994 | 816.5 | 245537.9994 | 819.5 | 245037.9994 | 822 | 245937.9994 | 825 | 244037.9994 | 811 | 242837.9994 | 811 | 242837.9994 | 811 | 244037.9994
827.5 | 245437.9994 | 830.5 | 242837.9994 | 833.5 | 245537.9994 | 836 | 245037.9994 | 839 | 245937.9994 | 841.5 | 244037.9994 | 827.5 | 242837.9994 | 827.5 | 242837.9994 | 827.5 | 244037.9994
844.5 | 245437.9994 | 847.5 | 242837.9994 | 850 | 245537.9994 | 853 | 245037.9994 | 855.5 | 245937.9994 | 858.5 | 244037.9994 | 844.5 | 242837.9994 | 844.5 | 242837.9994 | 844.5 | 244037.9994
861.5 | 245437.9994 | 864 | 242837.9994 | 867 | 245537.9994 | 869.5 | 245037.9994 | 872.5 | 245937.9994 | 875.5 | 244037.9994 | 861.5 | 242837.9994 | 861.5 | 242837.9994 | 861.5 | 244037.9994
878 | 245437.9994 | 881 | 242837.9994 | 883.5 | 245537.9994 | 886.5 | 245037.9994 | 889.5 | 245937.9994 | 892 | 244037.9994 | 878 | 242837.9994 | 878 | 242837.9994 | 878 | 244037.9994
895 | 245437.9994 | 897.5 | 242837.9994 | 900.5 | 245537.9994 | 903.5 | 245037.9994 | 906 | 245937.9994 | 909 | 244037.9994 | 895 | 242837.9994 | 895 | 242837.9994 | 895 | 244037.9994
911.5 | 245437.9994 | 914.5 | 121368.9988 | 917.5 | 245537.9994 | 920 | 245037.9994 | 923 | 245937.9994 | 925.5 | 244037.9994 | 911.5 | 121368.9988 | 911.5 | 121368.9988 | 911.5 | 244037.9994
928.5 | 245437.9994 | 931.5 | 242837.9994 | 934 | 245537.9994 | 937 | 245037.9994 | 939.5 | 245937.9994 | 942.5 | 244037.9994 | 928.5 | 242837.9994 | 928.5 | 242837.9994 | 928.5 | 244037.9994
945.5 | 245437.9994 | 948 | 242837.9994 | 951 | 245537.9994 | 953.5 | 245037.9994 | 956.5 | 245937.9994 | 959.5 | 244037.9994 | 945.5 | 242837.9994 | 945.5 | 242837.9994 | 945.5 | 244037.9994
962.5 | 245437.9994 | 965 | 242837.9994 | 967.5 | 245537.9994 | 970.5 | 245037.9994 | 973.5 | 245937.9994 | 976 | 244037.9994 | 962.5 | 242837.9994 | 962.5 | 242837.9994 | 962.5 | 244037.9994
979 | 245437.9994 | 981.5 | 242837.9994 | 984.5 | 245537.9994 | 987.5 | 245037.9994 | 990 | 245937.9994 | 993 | 244037.9994 | 979 | 242837.9994 | 979 | 242837.9994 | 979 | 244037.9994
995.5 | 245437.9994 | 998.5 | 242837.9994 | 1001.5 | 245537.9994 | 1004 | 245037.9994 | 1007 | 245937.9994 | 1009.5 | 244037.9994 | 995.5 | 242837.9994 | 995.5 | 242837.9994 | 995.5 | 244037.9994
1012.5 | 245437.9994 | 1015.5 | 242837.9994 | 1018 | 245537.9994 | 1021 | 245037.9994 | 1023.5 | 245937.9994 | 1026.5 | 244037.9994 | 1012.5 | 242837.9994 | 1012.5 | 242837.9994 | 1012.5 | 244037.9994
1029.5 | 245437.9994 | 1032 | 242837.9994 | 1035 | 245537.9994 | 1037.5 | 245037.9994 | 1040.5 | 245937.9994 | 1043.5 | 244037.9994 | 1029.5 | 242837.9994 | 1029.5 | 242837.9994 | 1029.5 | 244037.9994
1046 | 245437.9994 | 1049 | 242837.9994 | 1051.5 | 245537.9994 | 1054.5 | 245037.9994 | 1057.5 | 245937.9994 | 1060 | 244037.9994 | 1046 | 242837.9994 | 1046 | 242837.9994 | 1046 | 244037.9994
1063 | 245437.9994 | 1065.5 | 242837.9994 | 1068.5 | 245537.9994 | 1071.5 | 245037.9994 | 1074 | 245937.9994 | 1077 | 244037.9994 | 1063 | 242837.9994 | 1063 | 242837.9994 | 1063 | 244037.9994
1079.5 | 245437.9994 | 1082.5 | 242837.9994 | 1085.5 | 245537.9994 | 1088 | 245037.9994 | 1091 | 245937.9994 | 1093.5 | 244037.9994 | 1079.5 | 242837.9994 | 1079.5 | 242837.9994 | 1079.5 | 244037.9994
1096.5 | 245437.9994 | 1099.5 | 242837.9994 | 1102 | 245537.9994 | 1105 | 245037.9994 | 1107.5 | 245937.9994 | 1110.5 | 244037.9994 | 1096.5 | 242837.9994 | 1096.5 | 242837.9994 | 1096.5 | 244037.9994
1113.5 | 245437.9994 | 1116 | 242837.9994 | 1119 | 245537.9994 | 1121.5 | 244838.0816 | 1124.5 | 245937.9994 | 1127.5 | 244037.9994 | 1113.5 | 242837.9994 | 1113.5 | 242837.9994 | 1113.5 | 244037.9994
1130 | 245437.9994 | 1133 | 242837.9994 | 1135.5 | 245537.9994 | 1138.5 | 245037.9994 | 1141.5 | 245937.9994 | 1144 | 244037.9994 | 1130 | 242837.9994 | 1130 | 242837.9994 | 1130 | 244037.9994
1147 | 245437.9994 | 1149.5 | 242837.9994 | 1152.5 | 245537.9994 | 1155.5 | 245037.9994 | 1158 | 245937.9994 | 1161 | 244037.9994 | 1147 | 242837.9994 | 1147 | 242837.9994 | 1147 | 244037.9994
1163.5 | 245437.9994 | 1166.5 | 242837.9994 | 1169.5 | 245537.9994 | 1172 | 245037.9994 | 1175 | 245937.9994 | 1177.5 | 244037.9994 | 1163.5 | 242837.9994 | 1163.5 | 242837.9994 | 1163.5 | 244037.9994
1180.5 | 245437.9994 | 1183.5 | 242837.9994 | 1186 | 245537.9994 | 1189 | 245037.9994 | 1191.5 | 245937.9994 | 1194.5 | 244037.9994 | 1180.5 | 242837.9994 | 1180.5 | 242837.9994 | 1180.5 | 244037.9994
1197.5 | 245437.9994 | 1200 | 242837.9994 | 1203 | 245537.9994 | 1205.5 | 245037.9994 | 1208.5 | 245937.9994 | 1211.5 | 244037.9994 | 1197.5 | 242837.9994 | 1197.5 | 242837.9994 | 1197.5 | 244037.9994
1214 | 245437.9994 | 1217 | 242837.9994 | 1219.5 | 245537.9994 | 1222.5 | 245037.9994 | 1225.5 | 245937.9994 | 1228 | 244037.9994 | 1214 | 242837.9994 | 1214 | 242837.9994 | 1214 | 244037.9994
1231 | 245437.9994 | 1233.5 | 242837.9994 | 1236.5 | 245537.9994 | 1239.5 | 245037.9994 | 1242 | 245937.9994 | 1245 | 244037.9994 | 1231 | 242837.9994 | 1231 | 242837.9994 | 1231 | 244037.9994
1247.5 | 245437.9994 | 1250.5 | 242837.9994 | 1253.5 | 245537.9994 | 1256 | 245037.9994 | 1259 | 245937.9994 | 1261.5 | 244037.9994 | 1247.5 | 242837.9994 | 1247.5 | 242837.9994 | 1247.5 | 244037.9994
1264.5 | 245437.9994 | 1267 | 242837.9994 | 1270 | 245537.9994 | 1273 | 245037.9994 | 1275.5 | 245937.9994 | 1278.5 | 244037.9994 | 1264.5 | 242837.9994 | 1264.5 | 242837.9994 | 1264.5 | 244037.9994
1281.5 | 245437.9994 | 1284 | 242837.9994 | 1287 | 245537.9994 | 1289.5 | 245037.9994 | 1292.5 | 245937.9994 | 1295.5 | 244037.9994 | 1281.5 | 242837.9994 | 1281.5 | 242837.9994 | 1281.5 | 244037.9994
1298 | 245437.9994 | 1300.5 | 242837.9994 | 1303.5 | 245537.9994 | 1306.5 | 122468.9988 | 1309.5 | 245937.9994 | 1312 | 244037.9994 | 1298 | 122468.9988 | 1298 | 122468.9988 | 1298 | 244037.9994
1314.5 | 245437.9994 | 1317.5 | 242837.9994 | 1320.5 | 245537.9994 | 1323.5 | 245037.9994 | 1326 | 245937.9994 | 1328.5 | 244037.9994 | 1314.5 | 242837.9994 | 1314.5 | 242837.9994 | 1314.5 | 244037.9994
1331.5 | 245437.9994 | 1334.5 | 242837.9994 | 1337.5 | 245537.9994 | 1340 | 245037.9994 | 1342.5 | 245937.9994 | 1345.5 | 244037.9994 | 1331.5 | 242837.9994 | 1331.5 | 242837.9994 | 1331.5 | 244037.9994
1348.5 | 245437.9994 | 1351.5 | 242837.9994 | 1354 | 245537.9994 | 1357 | 245037.9994 | 1359.5 | 245937.9994 | 1362.5 | 244037.9994 | 1348.5 | 242837.9994 | 1348.5 | 242837.9994 | 1348.5 | 244037.9994
1365.5 | 245437.9994 | 1368 | 242837.9994 | 1371 | 245537.9994 | 1373.5 | 245037.9994 | 1376.5 | 245937.9994 | 1379 | 244037.9994 | 1365.5 | 242837.9994 | 1365.5 | 242837.9994 | 1365.5 | 244037.9994
1383 | 245437.9994 | 1384.5 | 242837.9994 | 1387.5 | 245537.9994 | 1390.5 | 245037.9994 | 1393.5 | 245937.9994 | 1396 | 244037.9994 | 1383 | 242837.9994 | 1383 | 242837.9994 | 1383 | 244037.9994
1398.5 | 245437.9994 | 1401.5 | 242837.9994 | 1404.5 | 245537.9994 | 1407.5 | 245037.9994 | 1410 | 245937.9994 | 1413 | 244037.9994 | 1398.5 | 242837.9994 | 1398.5 | 242837.9994 | 1398.5 | 244037.9994
1415.5 | 245437.9994 | 1418.5 | 242837.9994 | 1421.5 | 245537.9994 | 1424 | 245037.9994 | 1427 | 245937.9994 | 1429.5 | 244037.9994 | 1415.5 | 242837.9994 | 1415.5 | 242837.9994 | 1415.5 | 244037.9994
1432.5 | 245437.9994 | 1435 | 242837.9994 | 1438 | 245537.9994 | 1441 | 245037.9994 | 1443.5 | 245937.9994 | 1446.5 | 244037.9994 | 1432.5 | 242837.9994 | 1432.5 | 242837.9994 | 1432.5 | 244037.9994
1449 | 245437.9994 | 1452 | 242837.9994 | 1455 | 245537.9994 | 1457.5 | 245037.9994 | 1460.5 | 245937.9994 | 1463 | 244037.9994 | 1449 | 242837.9994 | 1449 | 242837.9994 | 1449 | 244037.9994
1466 | 245437.9994 | 1469 | 242837.9994 | 1471.5 | 245537.9994 | 1474.5 | 245037.9994 | 1477 | 245937.9994 | 1480 | 244037.9994 | 1466 | 242837.9994 | 1466 | 242837.9994 | 1466 | 244037.9994
1483 | 245437.9994 | 1485.5 | 242837.9994 | 1488.5 | 245537.9994 | 1491.5 | 245037.9994 | 1494 | 245738.0813 | 1496.5 | 244037.9994 | 1483 | 242837.9994 | 1483 | 242837.9994 | 1483 | 244037.9994
1499.5 | 245437.9994 | 1502.5 | 242837.9994 | 1505 | 245537.9994 | 1508 | 245037.9994 | 1511 | 245937.9994 | 1513.5 | 244037.9994 | 1499.5 | 242837.9994 | 1499.5 | 242837.9994 | 1499.5 | 244037.9994
1516.5 | 245437.9994 | 1519.5 | 242837.9994 | 1522 | 245537.9994 | 1524.5 | 245037.9994 | 1527.5 | 245937.9994 | 1530.5 | 244037.9994 | 1516.5 | 242837.9994 | 1516.5 | 242837.9994 | 1516.5 | 244037.9994
1533.5 | 245437.9994 | 1536 | 242837.9994 | 1538.5 | 245537.9994 | 1541.5 | 245037.9994 | 1544.5 | 245937.9994 | 1547.5 | 244037.9994 | 1533.5 | 242837.9994 | 1533.5 | 242837.9994 | 1533.5 | 244037.9994
1550 | 245437.9994 | 1552.5 | 242837.9994 | 1555.5 | 245537.9994 | 1558.5 | 245037.9994 | 1561 | 245937.9994 | 1564 | 244037.9994 | 1550 | 242837.9994 | 1550 | 242837.9994 | 1550 | 244037.9994
1566.5 | 245437.9994 | 1569.5 | 242837.9994 | 1572.5 | 245537.9994 | 1575.5 | 245037.9994 | 1578 | 245937.9994 | 1580.5 | 244037.9994 | 1566.5 | 242837.9994 | 1566.5 | 242837.9994 | 1566.5 | 244037.9994
1583.5 | 245437.9994 | 1586.5 | 242837.9994 | 1589 | 245537.9994 | 1592 | 245037.9994 | 1595 | 245937.9994 | 1597.5 | 244037.9994 | 1583.5 | 242837.9994 | 1583.5 | 242837.9994 | 1583.5 | 244037.9994
1600.5 | 245437.9994 | 1603 | 242837.9994 | 1606 | 245537.9994 | 1609 | 244838.0816 | 1611.5 | 245937.9994 | 1614.5 | 244037.9994 | 1600.5 | 242837.9994 | 1600.5 | 242837.9994 | 1600.5 | 244037.9994
1617 | 245437.9994 | 1620 | 242837.9994 | 1622.5 | 245537.9994 | 1625.5 | 245037.9994 | 1628.5 | 245937.9994 | 1631 | 244037.9994 | 1617 | 242837.9994 | 1617 | 242837.9994 | 1617 | 244037.9994
1634 | 245437.9994 | 1637 | 242837.9994 | 1639.5 | 245537.9994 | 1642.5 | 245037.9994 | 1645 | 245937.9994 | 1648 | 244037.9994 | 1634 | 242837.9994 | 1634 | 242837.9994 | 1634 | 244037.9994
1650.5 | 245437.9994 | 1653.5 | 242837.9994 | 1656 | 245537.9994 | 1659 | 245037.9994 | 1662 | 245937.9994 | 1664.5 | 244037.9994 | 1650.5 | 242837.9994 | 1650.5 | 242837.9994 | 1650.5 | 244037.9994
1667.5 | 245437.9994 | 1670.5 | 242837.9994 | 1673 | 245537.9994 | 1676 | 245037.9994 | 1678.5 | 245937.9994 | 1681.5 | 244037.9994 | 1667.5 | 242837.9994 | 1667.5 | 242837.9994 | 1667.5 | 244037.9994
1684.5 | 245437.9994 | 1687 | 242837.9994 | 1690 | 245537.9994 | 1692.5 | 245037.9994 | 1695.5 | 245937.9994 | 1698.5 | 244037.9994 | 1684.5 | 242837.9994 | 1684.5 | 242837.9994 | 1684.5 | 244037.9994
1701 | 245437.9994 | 1704 | 242837.9994 | 1706.5 | 245537.9994 | 1709.5 | 245037.9994 | 1712.5 | 245937.9994 | 1715 | 244037.9994 | 1701 | 242837.9994 | 1701 | 242837.9994 | 1701 | 244037.9994
1718 | 245437.9994 | 1721 | 242837.9994 | 1723.5 | 245537.9994 | 1726.5 | 245037.9994 | 1729 | 245937.9994 | 1732 | 244037.9994 | 1718 | 242837.9994 | 1718 | 242837.9994 | 1718 | 244037.9994
1735 | 245437.9994 | 1737.5 | 242837.9994 | 1740.5 | 245537.9994 | 1743.5 | 244838.0816 | 1746 | 245937.9994 | 1748.5 | 244037.9994 | 1735 | 242837.9994 | 1735 | 242837.9994 | 1735 | 244037.9994
1751.5 | 245437.9994 | 1754.5 | 242837.9994 | 1757.5 | 245537.9994 | 1760 | 245037.9994 | 1762.5 | 245937.9994 | 1765.5 | 244037.9994 | 1751.5 | 242837.9994 | 1751.5 | 242837.9994 | 1751.5 | 244037.9994
1768.5 | 245437.9994 | 1771 | 242837.9994 | 1774 | 245338.0814 | 1776.5 | 245037.9994 | 1779.5 | 245937.9994 | 1782.5 | 244037.9994 | 1768.5 | 242837.9994 | 1768.5 | 242837.9994 | 1768.5 | 244037.9994
1785 | 245437.9994 | 1788 | 242837.9994 | 1791 | 245537.9994 | 1793.5 | 245037.9994 | 1796.5 | 245937.9994 | 1799 | 244037.9994 | 1785 | 242837.9994 | 1785 | 242837.9994 | 1785 | 244037.9994
1802 | 245437.9994 | 1804.5 | 242837.9994 | 1807.5 | 245537.9994 | 1810.5 | 245037.9994 | 1813 | 122918.9988 | 1816 | 244037.9994 | 1802 | 122918.9988 | 1802 | 242837.9994 | 1802 | 122918.9988
1819 | 245437.9994 | 1821.5 | 242837.9994 | 1824.5 | 245537.9994 | 1827 | 245037.9994 | 1830 | 245937.9994 | 1832.5 | 244037.9994 | 1819 | 242837.9994 | 1819 | 242837.9994 | 1819 | 244037.9994
1835.5 | 245437.9994 | 1838.5 | 242837.9994 | 1841.5 | 245537.9994 | 1844 | 245037.9994 | 1846.5 | 245937.9994 | 1849.5 | 244037.9994 | 1835.5 | 242837.9994 | 1835.5 | 242837.9994 | 1835.5 | 244037.9994
1852.5 | 245437.9994 | 1855 | 242837.9994 | 1858 | 245537.9994 | 1860 | 245037.9994 | 1863.5 | 245937.9994 | 1866.5 | 244037.9994 | 1852.5 | 242837.9994 | 1852.5 | 242837.9994 | 1852.5 | 244037.9994
1869 | 245437.9994 | 1872 | 242837.9994 | 1874.5 | 245537.9994 | 1877.5 | 245037.9994 | 1880.5 | 245937.9994 | 1883 | 244037.9994 | 1869 | 242837.9994 | 1869 | 242837.9994 | 1869 | 244037.9994
1886 | 245437.9994 | 1888.5 | 242837.9994 | 1891.5 | 245537.9994 | 1894.5 | 245037.9994 | 1897 | 245937.9994 | 1900 | 244037.9994 | 1886 | 242837.9994 | 1886 | 242837.9994 | 1886 | 244037.9994
1902.5 | 245437.9994 | 1905.5 | 242837.9994 | 1908.5 | 245537.9994 | 1911 | 245037.9994 | 1914 | 245937.9994 | 1916.5 | 244037.9994 | 1902.5 | 242837.9994 | 1902.5 | 242837.9994 | 1902.5 | 244037.9994
1919.5 | 245437.9994 | 1922.5 | 242837.9994 | 1925 | 245537.9994 | 1928 | 245037.9994 | 1930.5 | 245937.9994 | 1933.5 | 244037.9994 | 1919.5 | 242837.9994 | 1919.5 | 242837.9994 | 1919.5 | 244037.9994
1936.5 | 245437.9994 | 1939 | 242837.9994 | 1942 | 245537.9994 | 1944.5 | 245037.9994 | 1947.5 | 245937.9994 | 1950.5 | 244037.9994 | 1936.5 | 242837.9994 | 1936.5 | 242837.9994 | 1936.5 | 244037.9994
1953 | 245437.9994 | 1956 | 242837.9994 | 1958.5 | 245537.9994 | 1961.5 | 245037.9994 | 1964.5 | 245937.9994 | 1967 | 244037.9994 | 1953 | 242837.9994 | 1953 | 242837.9994 | 1953 | 244037.9994
1970 | 245437.9994 | 1972.5 | 242837.9994 | 1975.5 | 245537.9994 | 1978.5 | 245037.9994 | 1981 | 245937.9994 | 1984 | 244037.9994 | 1970 | 242837.9994 | 1970 | 242837.9994 | 1970 | 244037.9994
1986.5 | 245437.9994 | 1989.5 | 242837.9994 | 1992.5 | 245537.9994 | 1995 | 245037.9994 | 1998 | 245937.9994 | 2000.5 | 244037.9994 | 1986.5 | 242837.9994 | 1986.5 | 242837.9994 | 1986.5 | 244037.9994
2003.5 | 245437.9994 | 2006.5 | 242837.9994 | 2009 | 245537.9994 | 2012 | 245037.9994 | 2014.5 | 245937.9994 | 2017.5 | 244037.9994 | 2003.5 | 242837.9994 | 2003.5 | 242837.9994 | 2003.5 | 244037.9994
2020.5 | 245437.9994 | 2023 | 242837.9994 | 2026 | 245537.9994 | 2028.5 | 245037.9994 | 2031.5 | 245937.9994 | 2034.5 | 244037.9994 | 2020.5 | 242837.9994 | 2020.5 | 242837.9994 | 2020.5 | 244037.9994
2037 | 245437.9994 | 2040 | 242837.9994 | 2042.5 | 245537.9994 | 2045.5 | 245037.9994 | 2048.5 | 245937.9994 | 2051 | 244037.9994 | 2037 | 242837.9994 | 2037 | 242837.9994 | 2037 | 244037.9994
2054 | 245437.9994 | 2056.5 | 242837.9994 | 2059.5 | 245537.9994 | 2062.5 | 245037.9994 | 2065 | 245937.9994 | 2068 | 244037.9994 | 2054 | 242837.9994 | 2054 | 242837.9994 | 2054 | 244037.9994
2070.5 | 245437.9994 | 2073.5 | 242837.9994 | 2076.5 | 245537.9994 | 2079 | 245037.9994 | 2082 | 245937.9994 | 2084.5 | 244037.9994 | 2070.5 | 242837.9994 | 2070.5 | 242837.9994 | 2070.5 | 244037.9994
2087.5 | 245437.9994 | 2090.5 | 242837.9994 | 2093 | 245537.9994 | 2096 | 245037.9994 | 2098.5 | 245937.9994 | 2101.5 | 244037.9994 | 2087.5 | 242837.9994 | 2087.5 | 242837.9994 | 2087.5 | 244037.9994
2104.5 | 245437.9994 | 2107 | 242837.9994 | 2110 | 245537.9994 | 2112.5 | 245037.9994 | 2115.5 | 245937.9994 | 2118.5 | 244037.9994 | 2104.5 | 242837.9994 | 2104.5 | 242837.9994 | 2104.5 | 244037.9994
2121 | 245437.9994 | 2124 | 242837.9994 | 2126.5 | 245537.9994 | 2129.5 | 245037.9994 | 2132.5 | 245937.9994 | 2135 | 244037.9994 | 2121 | 242837.9994 | 2121 | 242837.9994 | 2121 | 244037.9994
2138 | 245437.9994 | 2140.5 | 242837.9994 | 2143.5 | 245537.9994 | 2146.5 | 245037.9994 | 2149 | 245937.9994 | 2152 | 244037.9994 | 2138 | 242837.9994 | 2138 | 242837.9994 | 2138 | 244037.9994
2154.5 | 245437.9994 | 2157.5 | 242837.9994 | 2160.5 | 245537.9994 | 2163 | 245037.9994 | 2166 | 245937.9994 | 2168.5 | 121968.9988 | 2154.5 | 121968.9988 | 2154.5 | 242837.9994 | 2154.5 | 121968.9988
2171.5 | 245437.9994 | 2174.5 | 242837.9994 | 2177 | 245537.9994 | 2180 | 245037.9994 | 2182.5 | 245937.9994 | 2185.5 | 121968.9988 | 2171.5 | 121968.9988 | 2171.5 | 242837.9994 | 2171.5 | 121968.9988
2188.5 | 245437.9994 | 2191 | 242837.9994 | 2194 | 245537.9994 | 2196.5 | 245037.9994 | 2199.5 | 245937.9994 | 2202.5 | 244037.9994 | 2188.5 | 242837.9994 | 2188.5 | 242837.9994 | 2188.5 | 244037.9994
2205 | 245437.9994 | 2208 | 242837.9994 | 2210.5 | 245537.9994 | 2213.5 | 245037.9994 | 2216.5 | 245937.9994 | 2219 | 244037.9994 | 2205 | 242837.9994 | 2205 | 242837.9994 | 2205 | 244037.9994
2222 | 245437.9994 | 2224.5 | 242837.9994 | 2227.5 | 245537.9994 | 2230.5 | 245037.9994 | 2233 | 245937.9994 | 2236 | 244037.9994 | 2222 | 242837.9994 | 2222 | 242837.9994 | 2222 | 244037.9994
2238.5 | 245437.9994 | 2241.5 | 242837.9994 | 2244.5 | 245537.9994 | 2247 | 245037.9994 | 2250 | 245937.9994 | 2252.5 | 244037.9994 | 2238.5 | 242837.9994 | 2238.5 | 242837.9994 | 2238.5 | 244037.9994
2255.5 | 245437.9994 | 2258.5 | 242837.9994 | 2261 | 245537.9994 | 2264 | 245037.9994 | 2266.5 | 245937.9994 | 2269.5 | 244037.9994 | 2255.5 | 242837.9994 | 2255.5 | 242837.9994 | 2255.5 | 244037.9994
2272.5 | 245437.9994 | 2275 | 242837.9994 | 2278 | 245537.9994 | 2280 | 245037.9994 | 2283.5 | 245937.9994 | 2286.5 | 244037.9994 | 2272.5 | 242837.9994 | 2272.5 | 242837.9994 | 2272.5 | 244037.9994
2289 | 245437.9994 | 2292 | 242837.9994 | 2294.5 | 245537.9994 | 2297.5 | 245037.9994 | 2300.5 | 245937.9994 | 2303 | 244037.9994 | 2289 | 242837.9994 | 2289 | 242837.9994 | 2289 | 244037.9994
2306 | 122668.9988 | 2308.5 | 242837.9994 | 2311.5 | 245537.9994 | 2314.5 | 245037.9994 | 2317 | 245937.9994 | 2320 | 244037.9994 | 2306 | 122668.9988 | 2306 | 122668.9988 | 2306 | 244037.9994
2322.5 | 245437.9994 | 2325.5 | 242837.9994 | 2328.5 | 245537.9994 | 2331 | 245037.9994 | 2334 | 335.799 | 2336.5 | 22058.23 | 2322.5 | 335.799 | 2322.5 | 242837.9994 | 2322.5 | 335.799
2339.5 | 122469.1222 | 2342.5 | 242538.1235 | 2345 | 244338.8549 | 2348 | 81612.6648 | 2350.5 | 58.024 | 2353.5 | 14185.5415 | 2339.5 | 58.024 | 2339.5 | 81612.6648 | 2339.5 | 58.024
2356.5 | 2426.5576 | 2359 | 80746.0686 | 2362 | 664.5116 | 2364.5 | 16163.2493 | 2367.5 | 26.9793 | 2370.5 | 14173.8936 | 2356.5 | 26.9793 | 2356.5 | 2426.5576 | 2356.5 | 26.9793
2373 | 40.3545 | 2376 | 14073.8595 | 2378.5 | 27.6157 | 2381.5 | 13397.6822 | 2384.5 | 52.8932 | 2387 | 13363.8654 | 2373 | 27.6157 | 2373 | 40.3545 | 2373 | 27.6157
2390 | 58.3464 | 2392.5 | 10247.9413 | 2395.5 | 51.4121 | 2398.5 | 471.0988 | 2401 | 27.5223 | 2404 | 694.3131 | 2390 | 27.5223 | 2390 | 58.3464 | 2390 | 27.5223
2406.5 | 60.8767 | 2409.5 | 39.6137 | 2412.5 | 61.5721 | 2415 | 27.7784 | 2418 | 69.7058 | 2420.5 | 24.8396 | 2406.5 | 24.8396 | 2406.5 | 27.7784 | 2406.5 | 24.8396
2423.5 | 87.0398 | 2426.5 | 23.2466 | 2429 | 63.3202 | 2432 | 80.2494 | 2434.5 | 24.3827 | 2437.5 | 9.4819 | 2423.5 | 9.4819 | 2423.5 | 23.2466 | 2423.5 | 9.4819
2440.5 | 40.5669 | 2443 | 46.3491 | 2446 | 10.9959 | 2448.5 | 24.0546 | 2451.5 | 63.2984 | 2454.5 | 18.3379 | 2440.5 | 10.9959 | 2440.5 | 24.0546 | 2440.5 | 10.9959
2457 | 80.9681 | 2460 | 21.6993 | 2462.5 | 15.9842 | 2465.5 | 78.7789 | 2468.5 | 50.5454 | 2471 | 12.028 | 2457 | 12.028 | 2457 | 21.6993 | 2457 | 12.028
2474 | 57.5718 | 2476.5 | 26.1702 | 2479.5 | 45.1905 | 2482.5 | 21.4494 | 2485 | 21.9022 | 2488 | 8.8878 | 2474 | 8.8878 | 2474 | 21.4494 | 2474 | 8.8878
2490.5 | 78.0518 | 2493.5 | 26.1328 | 2496.5 | 8.6103 | 2499 | 35.3046 | 2502 | 17.7338 | 2504.5 | 42.863 | 2490.5 | 8.6103 | 2490.5 | 26.1328 | 2490.5 | 8.6103
2507.5 | 88.9052 | 2510.5 | 61.8347 | 2513 | 12.5427 | 2516 | 78.3552 | 2518.5 | 21.688 | 2521.5 | 70.4352 | 2507.5 | 12.5427 | 2507.5 | 61.8347 | 2507.5 | 12.5427
2524.5 | 47.5967 | 2527 | 26.6471 | 2530 | 34.9208 | 2532.5 | 26.2237 | 2535.5 | 47.7989 | 2538.5 | 8.5287 | 2524.5 | 8.5287 | 2524.5 | 26.2237 | 2524.5 | 8.5287
2541 | 55.0092 | 2544 | 35.8749 | 2546.5 | 66.4389 | 2549.5 | 40.9886 | 2552.5 | 61.5255 | 2555 | 45.5022 | 2541 | 35.8749 | 2541 | 35.8749 | 2541 | 45.5022
2558 | 19.2123 | 2560.5 | 48.2623 | 2563.5 | 11.8209 | 2566.5 | 67.3998 | 2569 | 25.0763 | 2572 | 57.273 | 2558 | 11.8209 | 2558 | 19.2123 | 2558 | 11.8209
2574.5 | 51.3805 | 2577.5 | 10.8642 | 2580.5 | 26.9964 | 2583 | 23.7561 | 2586 | 65.561 | 2588.5 | 13.7674 | 2574.5 | 10.8642 | 2574.5 | 10.8642 | 2574.5 | 13.7674
2591.5 | 82.754 | 2594.5 | 27.3391 | 2597 | 66.4274 | 2600 | 45.1902 | 2602.5 | 56.7153 | 2605.5 | 34.7383 | 2591.5 | 27.3391 | 2591.5 | 27.3391 | 2591.5 | 34.7383
2608.5 | 19.3017 | 2611 | 44.045 | 2614 | 35.2082 | 2616.5 | 20.2493 | 2619 | 19.566 | 2622.5 | 23.4344 | 2608.5 | 19.3017 | 2608.5 | 19.3017 | 2608.5 | 19.566
2625 | 58.4163 | 2628 | 62.0418 | 2630.5 | 44.2125 | 2633.5 | 36.9161 | 2636.5 | 51.4263 | 2639 | 10.1532 | 2625 | 10.1532 | 2625 | 36.9161 | 2625 | 10.1532
2642 | 78.7779 | 2644.5 | 12.4217 | 2647.5 | 52.6206 | 2650.5 | 25.7684 | 2653 | 59.8603 | 2656 | 11.7624 | 2642 | 11.7624 | 2642 | 12.4217 | 2642 | 11.7624
2658.5 | 78.2169 | 2661.5 | 47.9512 | 2664.5 | 38.9941 | 2667 | 80.0814 | 2669.5 | 19.2377 | 2672.5 | 1736.3082 | 2658.5 | 19.2377 | 2658.5 | 47.9512 | 2658.5 | 19.2377
2675.5 | 42.2036 | 2678.5 | 33.0714 | 2681 | 10.3344 | 2684 | 935.9958 | 2686.5 | 394.0477 | 2689.5 | 385.6278 | 2675.5 | 10.3344 | 2675.5 | 33.0714 | 2675.5 | 10.3344
2692.5 | 165.0309 | 2695 | 247.0374 | 2698 | 445.4645 | 2700.5 | 2196.2401 | 2703.5 | 60.2199 | 2706.5 | 2930.667 | 2692.5 | 60.2199 | 2692.5 | 165.0309 | 2692.5 | 60.2199
2709 | 576.0101 | 2712 | 921.8091 | 2714.5 | 427.8574 | 2717.5 | 304.1232 | 2720.5 | 427.5337 | 2723 | 3350.8657 | 2709 | 304.1232 | 2709 | 304.1232 | 2709 | 427.5337
2726 | 176.0761 | 2728.5 | 683.5052 | 2731.5 | 84.7619 | 2734 | 2335.6193 | 2737 | 52.3673 | 2740 | 4661.9649 | 2726 | 52.3673 | 2726 | 176.0761 | 2726 | 52.3673
2742.5 | 289.2754 | 2745.5 | 1674.0169 | 2748 | 931.8013 | 2751 | 999.1881 | 2754 | 493.922 | 2756.5 | 5844.5212 | 2742.5 | 289.2754 | 2742.5 | 289.2754 | 2742.5 | 493.922
2759.5 | 136.0508 | 2762.5 | 350.7316 | 2765 | 247.8184 | 2768 | 755.2743 | 2770.5 | 697.2098 | 2773.5 | 4331.3497 | 2759.5 | 136.0508 | 2759.5 | 136.0508 | 2759.5 | 247.8184
2776.5 | 74 | 2779 | 444.1254 | 2781.5 | 41.1547 | 2784.5 | 839.2012 | 2787.5 | 813.6098 | 2790.5 | 1129.953 | 2776.5 | 41.1547 | 2776.5 | 74 | 2776.5 | 41.1547
2793 | 1895.4428 | 2796 | 3120.9265 | 2798.5 | 1503.5073 | 2801.5 | 5303.9183 | 2804.5 | 1663.5626 | 2807 | 9586.469 | 2793 | 1503.5073 | 2793 | 1895.4428 | 2793 | 1503.5073
2810 | 159.4566 | 2812.5 | 2299.6249 | 2815.5 | 82.4943 | 2818 | 2900.8416 | 2821 | 2190.9602 | 2823.5 | 74515.586 | 2810 | 82.4943 | 2810 | 159.4566 | 2810 | 82.4943
2826.5 | 253.0869 | 2829.5 | 11965.4359 | 2832.5 | 575.6692 | 2835 | 513.3918 | 2837.5 | 217.5024 | 2840.5 | 21514.911 | 2826.5 | 217.5024 | 2826.5 | 253.0869 | 2826.5 | 217.5024
2843.5 | 1481.2957 | 2846.5 | 6333.557 | 2849 | 119.6371 | 2851.5 | 7700.3771 | 2854.5 | 406.9762 | 2857.5 | 8135.5059 | 2843.5 | 119.6371 | 2843.5 | 1481.2957 | 2843.5 | 119.6371
2860.5 | 34.2373 | 2863 | 12444.6872 | 2866 | 504.4695 | 2868.5 | 9470.9315 | 2871.5 | 5189.505 | 2874.5 | 39459.1618 | 2860.5 | 34.2373 | 2860.5 | 34.2373 | 2860.5 | 504.4695
2877 | 373.0922 | 2879.5 | 24308.3508 | 2882.5 | 1913.5009 | 2885.5 | 17118.6904 | 2888 | 62.5044 | 2891 | 106516.3796 | 2877 | 62.5044 | 2877 | 373.0922 | 2877 | 62.5044
2894 | 352.4067 | 2896.5 | 6339.8666 | 2899.5 | 229.0819 | 2902 | 4886.3971 | 2905 | 2887.4138 | 2908 | 70914.1619 | 2894 | 229.0819 | 2894 | 352.4067 | 2894 | 229.0819
2910.5 | 3230.384 | 2913.5 | 8542.0164 | 2916 | 111.3975 | 2919 | 14505.5431 | 2921.5 | 6160.863 | 2924.5 | 46922.3572 | 2910.5 | 111.3975 | 2910.5 | 3230.384 | 2910.5 | 111.3975
2927.5 | 12199.869 | 2930.5 | 20560.3941 | 2933 | 611.666 | 2935.5 | 55479.083 | 2938.5 | 1989.8642 | 2941.5 | 51645.63 | 2927.5 | 611.666 | 2927.5 | 12199.869 | 2927.5 | 611.666
2944 | 49.5676 | 2947 | 26915.9843 | 2949.5 | 883.9092 | 2952.5 | 6358.7125 | 2955.5 | 738.9324 | 2958.5 | 42134.1538 | 2944 | 49.5676 | 2944 | 49.5676 | 2944 | 738.9324
2961 | 380.5124 | 2963.5 | 21283.9282 | 2966.5 | 677.605 | 2969.5 | 20388.5501 | 2972.5 | 6467.7973 | 2975 | 52230.1991 | 2961 | 380.5124 | 2961 | 380.5124 | 2961 | 677.605
2977.5 | 256.2542 | 2980.5 | 10946.5737 | 2983.5 | 2652.6267 | 2986 | 57021.4167 | 2989 | 19.5259 | 2991.5 | 2337.4865 | 2977.5 | 19.5259 | 2977.5 | 256.2542 | 2977.5 | 19.5259
2994.5 | 143.7083 | 2997.5 | 42432.8999 | 3000.5 | 59.2687 | 3003 | 43032.3746 | 3005.5 | 10655.8598 | 3008.5 | 169431.8683 | 2994.5 | 59.2687 | 2994.5 | 143.7083 | 2994.5 | 59.2687
3011.5 | 733.6846 | 3014.5 | 33607.5339 | 3017 | 434.8813 | 3019.5 | 19278.0617 | 3022.5 | 8225.3109 | 3025.5 | 47787.5203 | 3011.5 | 434.8813 | 3011.5 | 733.6846 | 3011.5 | 434.8813
3028.5 | 447.1704 | 3031 | 4853.4797 | 3033.5 | 436.328 | 3036.5 | 49117.4442 | 3039.5 | 8529.3143 | 3042 | 16066.6575 | 3028.5 | 436.328 | 3028.5 | 447.1704 | 3028.5 | 436.328
3045 | 2718.2189 | 3047.5 | 30927.481 | 3050.5 | 2187.2066 | 3053.5 | 18684.4565 | 3056 | 151.7505 | 3059 | 48392.5405 | 3045 | 151.7505 | 3045 | 2718.2189 | 3045 | 151.7505
3061.5 | 9067.4146 | 3064.5 | 2650.96 | 3067.5 | 2257.3659 | 3070 | 52824.4285 | 3073 | 10353.6325 | 3075.5 | 75484.2124 | 3061.5 | 2257.3659 | 3061.5 | 2650.96 | 3061.5 | 2257.3659
3078.5 | 1176.8217 | 3081.5 | 21583.0614 | 3084 | 1907.8568 | 3087 | 11667.8638 | 3090 | 1151.5857 | 3092.5 | 56420.219 | 3078.5 | 1151.5857 | 3078.5 | 1176.8217 | 3078.5 | 1151.5857
3095.5 | 2276.6767 | 3098 | 8460.7969 | 3101 | 1589.3433 | 3104 | 9759.5814 | 3106.5 | 1518.9281 | 3109.5 | 52718.1292 | 3095.5 | 1518.9281 | 3095.5 | 2276.6767 | 3095.5 | 1518.9281
3112 | 1187.7903 | 3115 | 39619.8441 | 3117.5 | 3497.591 | 3120.5 | 46032.1485 | 3123.5 | 6466.6183 | 3126 | 6332.9664 | 3112 | 1187.7903 | 3112 | 1187.7903 | 3112 | 3497.591
3129 | 7944.7607 | 3131.5 | 1452.7228 | 3134.5 | 1243.2665 | 3137.5 | 40036.2827 | 3140.5 | 1875 | 3143 | 54104.6623 | 3129 | 1243.2665 | 3129 | 1452.7228 | 3129 | 1243.2665
3145.5 | 9823.217 | 3148.5 | 27094.2423 | 3151.5 | 1726.7785 | 3154 | 29398.3953 | 3157 | 46.771 | 3159.5 | 51631.9985 | 3145.5 | 46.771 | 3145.5 | 9823.217 | 3145.5 | 46.771
3162.5 | 20009.9852 | 3165.5 | 241938.9879 | 3168 | 22923.9105 | 3171 | 1452.1661 | 3174 | 21.4882 | 3176.5 | 52330.5649 | 3162.5 | 21.4882 | 3162.5 | 1452.1661 | 3162.5 | 21.4882
3179.5 | 59868.878 | 3183 | 241839.1937 | 3185 | 21375.3045 | 3187.5 | 9262.386 | 3190.5 | 9487.4013 | 3193.5 | 8466.7697 | 3179.5 | 8466.7697 | 3179.5 | 9262.386 | 3179.5 | 8466.7697
3196 | 49416.9075 | 3199 | 241839.1937 | 3201.5 | 36260.6312 | 3204.5 | 13466.6185 | 3207.5 | 3332.9666 | 3210 | 56248.1351 | 3196 | 3332.9666 | 3196 | 13466.6185 | 3196 | 3332.9666
3213 | 133654.222 | 3215.5 | 241839.2349 | 3218.5 | 64770.0728 | 3221.5 | 20280.0595 | 3224 | 6227.8845 | 3227 | 35107.8187 | 3213 | 6227.8845 | 3213 | 20280.0595 | 3213 | 6227.8845
3230 | 49444.657 | 3232.5 | 241839.2349 | 3235.5 | 50313.5673 | 3238 | 57197.6187 | 3241 | 422.7438 | 3243.5 | 48727.5969 | 3230 | 422.7438 | 3230 | 49444.657 | 3230 | 422.7438
3246.5 | 53879.7231 | 3249.5 | 241839.1937 | 3252 | 18314.2748 | 3255 | 22482.836 | 3257.5 | 140.6858 | 3260.5 | 16276.033 | 3246.5 | 140.6858 | 3246.5 | 22482.836 | 3246.5 | 140.6858
3263.5 | 42002.5497 | 3266 | 241839.2349 | 3269 | 49027.5969 | 3271.5 | 24187.8903 | 3274.5 | 774.3009 | 3277.5 | 79210.6163 | 3263.5 | 774.3009 | 3263.5 | 24187.8903 | 3263.5 | 774.3009
3280 | 40822.9963 | 3283 | 40389.663 | 3285.5 | 12078.9809 | 3288.5 | 1.5023 | 3291.5 | 7463.0595 | 3294 | 30782.4416 | 3280 | 1.5023 | 3280 | 1.5023 | 3280 | 7463.0595
3297 | 49007.5969 | 3299.5 | 241839.2349 | 3302.5 | 16005.3705 | 3305.5 | 55524.517 | 3308 | 978.1686 | 3311 | 68644.6183 | 3297 | 978.1686 | 3297 | 49007.5969 | 3297 | 978.1686
3313.5 | 70057.105 | 3316.5 | 40389.663 | 3319.5 | 4116.8973 | 3322 | 10217.1179 | 3325 | 18.8262 | 3327.5 | 1727.3552 | 3313.5 | 18.8262 | 3313.5 | 10217.1179 | 3313.5 | 18.8262
3330.5 | 218784.5353 | 3333.5 | 48487.5969 | 3336 | 6595.4534 | 3339 | 40321.1542 | 3341.5 | 325.3263 | 3344.5 | 48727.5969 | 3330.5 | 325.3263 | 3330.5 | 40321.1542 | 3330.5 | 325.3263
3347.5 | 30609.6542 | 3350 | 241938.9879 | 3353 | 3364.8311 | 3355.5 | 3730.3757 | 3358.5 | 292.9289 | 3361.5 | 96531.5763 | 3347.5 | 292.9289 | 3347.5 | 3730.3757 | 3347.5 | 292.9289

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 4 | Cable 5 | Cable 6 | Cable 7 | Cable 8
0 | -147 | 31.3387 | 26.9184 | 27.235 | 26.7517 | 26.9701 | 26.9312 | 26.8322 | 26.774 | 26.7834
0.6409 | -146.3591 | 31.3273 | 26.9158 | 27.2302 | 26.7553 | 26.9671 | 26.9255 | 26.8303 | 26.7728 | 26.7914
1.6323 | -145.3677 | 31.3328 | 26.9142 | 27.2343 | 26.7601 | 26.9671 | 26.9268 | 26.8261 | 26.7698 | 26.8012
2.6238 | -144.3762 | 31.326 | 26.9113 | 27.2163 | 26.7602 | 26.9586 | 26.9267 | 26.8279 | 26.7693 | 26.8119
3.6252 | -143.3748 | 31.3304 | 26.9085 | 27.2253 | 26.7574 | 26.9696 | 26.93 | 26.8315 | 26.7773 | 26.786
4.6267 | -142.3733 | 31.327 | 26.9074 | 27.2339 | 26.7587 | 26.9676 | 26.9223 | 26.8292 | 26.7722 | 26.787
5.6281 | -141.3719 | 31.3303 | 26.9109 | 27.2333 | 26.7617 | 26.9683 | 26.9274 | 26.832 | 26.7741 | 26.7766
6.6295 | -140.3705 | 31.3262 | 26.9109 | 27.2296 | 26.7565 | 26.9671 | 26.9321 | 26.8296 | 26.762 | 26.7891
7.631 | -139.369 | 31.3308 | 26.9126 | 27.2303 | 26.7594 | 26.9648 | 26.927 | 26.8301 | 26.7729 | 26.808
8.6324 | -138.3676 | 31.3323 | 26.9105 | 27.2353 | 26.7596 | 26.9677 | 26.924 | 26.8354 | 26.7704 | 26.7727
9.6238 | -137.3762 | 31.3296 | 26.9113 | 27.237 | 26.7602 | 26.9755 | 26.9283 | 26.8262 | 26.7702 | 26.7954
10.6253 | -136.3747 | 31.3379 | 26.9112 | 27.2362 | 26.7587 | 26.9735 | 26.9322 | 26.8264 | 26.7649 | 26.7875
11.6267 | -135.3733 | 31.3283 | 26.9101 | 27.2403 | 26.7562 | 26.9692 | 26.9248 | 26.8265 | 26.7636 | 26.79
12.6282 | -134.3718 | 31.328 | 26.9071 | 27.2369 | 26.756 | 26.9619 | 26.9248 | 26.8282 | 26.7731 | 26.7778
13.6296 | -133.3704 | 31.3289 | 26.9055 | 27.2284 | 26.7586 | 26.9713 | 26.9305 | 26.8247 | 26.7729 | 26.7794
14.631 | -132.369 | 31.3281 | 26.916 | 27.2377 | 26.7554 | 26.9729 | 26.9273 | 26.834 | 26.7633 | 26.7963
15.6325 | -131.3675 | 31.3271 | 26.9085 | 27.237 | 26.7637 | 26.9673 | 26.9236 | 26.8338 | 26.7742 | 26.7857
16.6339 | -130.3661 | 31.3304 | 26.909 | 27.2387 | 26.7605 | 26.9683 | 26.9265 | 26.8339 | 26.775 | 26.7926
17.6253 | -129.3747 | 31.3248 | 26.915 | 27.2381 | 26.7665 | 26.9686 | 26.932 | 26.8309 | 26.7619 | 26.8038
18.6268 | -128.3732 | 31.3297 | 26.9149 | 27.2454 | 26.7627 | 26.9688 | 26.9336 | 26.8346 | 26.7691 | 26.8056
19.6282 | -127.3718 | 31.325 | 26.9189 | 27.2387 | 26.7685 | 26.9682 | 26.929 | 26.8322 | 26.7662 | 26.7836
20.6297 | -126.3703 | 31.3196 | 26.9185 | 27.2327 | 26.7638 | 26.9704 | 26.9369 | 26.837 | 26.7621 | 26.8144
21.6311 | -125.3689 | 31.3204 | 26.9105 | 27.2492 | 26.774 | 26.9679 | 26.9334 | 26.8342 | 26.7762 | 26.7608
22.6325 | -124.3675 | 31.3248 | 26.9136 | 27.2379 | 26.7651 | 26.9778 | 26.9301 | 26.8382 | 26.7621 | 26.8052
23.624 | -123.376 | 31.3235 | 26.9134 | 27.2474 | 26.7684 | 26.9677 | 26.9271 | 26.8307 | 26.7782 | 26.7739
24.6254 | -122.3746 | 31.3296 | 26.9114 | 27.252 | 26.7705 | 26.9797 | 26.9303 | 26.8372 | 26.7659 | 26.7943
25.6268 | -121.3732 | 31.3272 | 26.9144 | 27.2444 | 26.7697 | 26.9758 | 26.9307 | 26.8313 | 26.7788 | 26.7882
26.6283 | -120.3717 | 31.3263 | 26.9178 | 27.2376 | 26.7754 | 26.974 | 26.9353 | 26.8365 | 26.7671 | 26.8102
27.6297 | -119.3703 | 31.322 | 26.9239 | 27.2416 | 26.7747 | 26.9733 | 26.9383 | 26.8367 | 26.7715 | 26.782
28.6312 | -118.3688 | 31.325 | 26.9264 | 27.2467 | 26.7816 | 26.9701 | 26.936 | 26.8422 | 26.777 | 26.788
29.6326 | -117.3674 | 31.3171 | 26.9207 | 27.2401 | 26.7776 | 26.9727 | 26.9366 | 26.8402 | 26.7752 | 26.777
30.624 | -116.376 | 31.3171 | 26.9227 | 27.248 | 26.7737 | 26.9754 | 26.9268 | 26.8426 | 26.7722 | 26.7924
31.6255 | -115.3745 | 31.3186 | 26.9274 | 27.2534 | 26.7709 | 26.9636 | 26.9381 | 26.8374 | 26.7694 | 26.7794
32.6269 | -114.3731 | 31.3207 | 26.9281 | 27.2526 | 26.7817 | 26.9798 | 26.9415 | 26.8419 | 26.7587 | 26.7971
33.6284 | -113.3716 | 31.3147 | 26.9316 | 27.2547 | 26.776 | 26.9826 | 26.9337 | 26.8433 | 26.7679 | 26.8015
34.6298 | -112.3702 | 31.3212 | 26.9282 | 27.2563 | 26.779 | 26.9851 | 26.9391 | 26.8373 | 26.7727 | 26.7868
35.6312 | -111.3688 | 31.3142 | 26.9293 | 27.2593 | 26.7794 | 26.977 | 26.939 | 26.839 | 26.7639 | 26.7995
36.6327 | -110.3673 | 31.3223 | 26.9246 | 27.2579 | 26.7825 | 26.9792 | 26.9369 | 26.8434 | 26.7678 | 26.7972
37.6341 | -109.3659 | 31.3166 | 26.9231 | 27.2606 | 26.7798 | 26.9753 | 26.9401 | 26.8378 | 26.7803 | 26.7737
38.6255 | -108.3745 | 31.324 | 26.9196 | 27.2576 | 26.7803 | 26.9843 | 26.9427 | 26.8388 | 26.7712 | 26.7947
39.627 | -107.373 | 31.322 | 26.9209 | 27.2702 | 26.7818 | 26.9806 | 26.9402 | 26.8436 | 26.7784 | 26.7644
40.6284 | -106.3716 | 31.3214 | 26.9181 | 27.2589 | 26.7837 | 26.9693 | 26.9452 | 26.846 | 26.7822 | 26.7691
41.6299 | -105.3701 | 31.3253 | 26.9211 | 27.2598 | 26.7813 | 26.9828 | 26.9393 | 26.8446 | 26.7782 | 26.7776
42.6313 | -104.3687 | 31.3259 | 26.9255 | 27.2654 | 26.7867 | 26.9836 | 26.9423 | 26.8405 | 26.7726 | 26.7976
43.6327 | -103.3673 | 31.3316 | 26.9288 | 27.2668 | 26.785 | 26.9747 | 26.9404 | 26.8445 | 26.775 | 26.7726
44.6342 | -102.3658 | 31.3295 | 26.9251 | 27.2716 | 26.7877 | 26.9777 | 26.944 | 26.8445 | 26.7814 | 26.7726
45.6256 | -101.3744 | 31.3286 | 26.926 | 27.2711 | 26.7872 | 26.9902 | 26.9388 | 26.8393 | 26.7755 | 26.8066
46.627 | -100.373 | 31.3294 | 26.9239 | 27.2779 | 26.7893 | 26.9832 | 26.9433 | 26.8417 | 26.7816 | 26.7729
47.6285 | -99.3715 | 31.3264 | 26.9279 | 27.2614 | 26.7886 | 26.9846 | 26.948 | 26.8459 | 26.7826 | 26.7637
48.6299 | -98.3701 | 31.3283 | 26.9312 | 27.2694 | 26.7916 | 26.986 | 26.9468 | 26.8452 | 26.7835 | 26.7665
49.6314 | -97.3686 | 31.3287 | 26.9227 | 27.2682 | 26.7907 | 26.9808 | 26.9428 | 26.8471 | 26.7842 | 26.7775
50.6328 | -96.3672 | 31.3265 | 26.9222 | 27.2555 | 26.7899 | 26.9873 | 26.942 | 26.8492 | 26.7771 | 26.8027
51.6242 | -95.3758 | 31.3194 | 26.9261 | 27.2634 | 26.7925 | 26.9797 | 26.9443 | 26.8486 | 26.7773 | 26.8024
52.6257 | -94.3743 | 31.3295 | 26.9266 | 27.2702 | 26.7906 | 26.9889 | 26.9467 | 26.8522 | 26.7784 | 26.7774
53.6271 | -93.3729 | 31.323 | 26.9221 | 27.2761 | 26.7875 | 26.9842 | 26.9467 | 26.8481 | 26.7723 | 26.8001
54.6286 | -92.3714 | 31.33 | 26.9221 | 27.2728 | 26.7905 | 26.9787 | 26.9452 | 26.8474 | 26.7784 | 26.7972
55.63 | -91.37 | 31.3231 | 26.9231 | 27.2736 | 26.7921 | 26.9833 | 26.9456 | 26.8527 | 26.7804 | 26.7921
56.6314 | -90.3686 | 31.3269 | 26.9199 | 27.2709 | 26.7966 | 26.9943 | 26.9482 | 26.8549 | 26.7817 | 26.7814
57.6329 | -89.3671 | 31.327 | 26.9218 | 27.2735 | 26.7948 | 26.9872 | 26.9492 | 26.8504 | 26.7637 | 26.8066
58.6343 | -88.3657 | 31.3287 | 26.9216 | 27.2579 | 26.8071 | 26.9955 | 26.9518 | 26.8545 | 26.7614 | 26.8187
59.6257 | -87.3743 | 31.325 | 26.9186 | 27.274 | 26.7986 | 26.9913 | 26.9506 | 26.8564 | 26.781 | 26.8038
60.6272 | -86.3728 | 31.325 | 26.9264 | 27.2705 | 26.7984 | 26.9953 | 26.9535 | 26.8515 | 26.7888 | 26.7579
61.6286 | -85.3714 | 31.3241 | 26.9303 | 27.2683 | 26.8028 | 26.9934 | 26.9518 | 26.8547 | 26.7685 | 26.8057
62.6301 | -84.3699 | 31.3286 | 26.9263 | 27.2742 | 26.8058 | 26.9886 | 26.9539 | 26.8542 | 26.7769 | 26.7863
63.6315 | -83.3685 | 31.3217 | 26.9274 | 27.2875 | 26.798 | 26.9939 | 26.9552 | 26.8548 | 26.7792 | 26.8141
64.6329 | -82.3671 | 31.3253 | 26.9202 | 27.2905 | 26.801 | 26.9901 | 26.9519 | 26.8557 | 26.7905 | 26.7789
65.6244 | -81.3756 | 31.3264 | 26.9197 | 27.2756 | 26.7978 | 26.9877 | 26.9548 | 26.8556 | 26.7824 | 26.791
66.6258 | -80.3742 | 31.3208 | 26.9207 | 27.2806 | 26.8036 | 26.9918 | 26.9514 | 26.8503 | 26.7721 | 26.8069
67.6272 | -79.3728 | 31.322 | 26.9244 | 27.2883 | 26.8096 | 26.9924 | 26.9506 | 26.8578 | 26.7727 | 26.7936
68.6287 | -78.3713 | 31.3264 | 26.9274 | 27.2762 | 26.8034 | 26.9991 | 26.9514 | 26.8588 | 26.7839 | 26.7794
69.6301 | -77.3699 | 31.3199 | 26.9257 | 27.2781 | 26.8038 | 26.9963 | 26.9545 | 26.8557 | 26.7785 | 26.8065
70.6316 | -76.3684 | 31.3227 | 26.9259 | 27.2827 | 26.8097 | 26.9915 | 26.9488 | 26.859 | 26.7803 | 26.817
71.633 | -75.367 | 31.3298 | 26.9176 | 27.2764 | 26.8095 | 27.0005 | 26.9547 | 26.8647 | 26.7725 | 26.7994
72.6244 | -74.3756 | 31.3262 | 26.9229 | 27.2795 | 26.8121 | 26.9916 | 26.9562 | 26.8506 | 26.7863 | 26.7983
73.6259 | -73.3741 | 31.3246 | 26.9289 | 27.2815 | 26.808 | 26.9987 | 26.9529 | 26.8594 | 26.7658 | 26.8028
74.6273 | -72.3727 | 31.321 | 26.9283 | 27.2825 | 26.8118 | 26.992 | 26.9528 | 26.8609 | 26.7808 | 26.8086
75.6287 | -71.3713 | 31.3222 | 26.927 | 27.2921 | 26.8118 | 26.9825 | 26.956 | 26.8585 | 26.7874 | 26.7708
76.6302 | -70.3698 | 31.3227 | 26.9232 | 27.2927 | 26.8126 | 27.002 | 26.9538 | 26.8624 | 26.7847 | 26.7912
77.6316 | -69.3684 | 31.3209 | 26.9267 | 27.2947 | 26.8155 | 26.995 | 26.9496 | 26.8606 | 26.7906 | 26.7962
78.6331 | -68.3669 | 31.3193 | 26.9323 | 27.2877 | 26.8187 | 26.9932 | 26.9559 | 26.8607 | 26.7912 | 26.7839
79.6245 | -67.3755 | 31.3205 | 26.925 | 27.2901 | 26.8213 | 26.992 | 26.9597 | 26.8583 | 26.7761 | 26.8074
80.6259 | -66.3741 | 31.3212 | 26.9267 | 27.2946 | 26.8181 | 27.002 | 26.9541 | 26.861 | 26.7856 | 26.7943
81.6274 | -65.3726 | 31.3216 | 26.9278 | 27.2844 | 26.8255 | 26.9979 | 26.9559 | 26.8595 | 26.7749 | 26.8005
82.6288 | -64.3712 | 31.3206 | 26.9255 | 27.2925 | 26.8174 | 27.0056 | 26.9569 | 26.8655 | 26.7734 | 26.8153
83.6303 | -63.3697 | 31.3208 | 26.9246 | 27.2923 | 26.8209 | 27.0015 | 26.959 | 26.8643 | 26.7908 | 26.7759
84.6317 | -62.3683 | 31.3224 | 26.9225 | 27.2772 | 26.8207 | 27.0041 | 26.9614 | 26.8627 | 26.7592 | 26.8174
85.6331 | -61.3669 | 31.3217 | 26.9271 | 27.3028 | 26.8185 | 27.0019 | 26.9623 | 26.8657 | 26.7943 | 26.7624
86.6246 | -60.3754 | 31.3238 | 26.922 | 27.2951 | 26.8199 | 26.9945 | 26.9588 | 26.8629 | 26.7873 | 26.795
87.626 | -59.374 | 31.3209 | 26.9218 | 27.303 | 26.8198 | 26.9969 | 26.9671 | 26.8632 | 26.8031 | 26.776
88.6274 | -58.3726 | 31.3217 | 26.9283 | 27.304 | 26.8248 | 26.9984 | 26.9639 | 26.8645 | 26.7933 | 26.782
89.6289 | -57.3711 | 31.3188 | 26.928 | 27.29 | 26.8224 | 27.0024 | 26.9693 | 26.8698 | 26.7846 | 26.8038
90.6303 | -56.3697 | 31.3189 | 26.935 | 27.2947 | 26.8278 | 27.0016 | 26.9633 | 26.8702 | 26.7996 | 26.7781
91.6318 | -55.3682 | 31.3176 | 26.9256 | 27.295 | 26.8255 | 27.0103 | 26.965 | 26.8703 | 26.7775 | 26.8017
92.6332 | -54.3668 | 31.3152 | 26.9248 | 27.297 | 26.8294 | 26.9971 | 26.9664 | 26.8711 | 26.8 | 26.7768
93.6246 | -53.3754 | 31.3158 | 26.9285 | 27.3033 | 26.8307 | 27.0019 | 26.9634 | 26.8703 | 26.7898 | 26.8135
94.6261 | -52.3739 | 31.3181 | 26.9295 | 27.2993 | 26.8324 | 27.0041 | 26.9628 | 26.8704 | 26.7997 | 26.7749
95.6275 | -51.3725 | 31.32 | 26.9249 | 27.3008 | 26.8243 | 27.0134 | 26.9711 | 26.8738 | 26.7817 | 26.8012
96.6289 | -50.3711 | 31.3175 | 26.9285 | 27.3061 | 26.8401 | 27.0085 | 26.9648 | 26.8748 | 26.8039 | 26.7767
97.6304 | -49.3696 | 31.3248 | 26.9292 | 27.3021 | 26.8281 | 27.0099 | 26.9674 | 26.8665 | 26.7949 | 26.781
98.6519 | -48.3481 | 31.3238 | 26.9263 | 27.2975 | 26.8391 | 26.9981 | 26.9652 | 26.8722 | 26.8008 | 26.7847
99.6333 | -47.3667 | 31.3226 | 26.9301 | 27.3046 | 26.8353 | 27.0068 | 26.9643 | 26.8707 | 26.7876 | 26.796
100.6247 | -46.3753 | 31.3217 | 26.9251 | 27.3055 | 26.8294 | 27.0098 | 26.9666 | 26.8702 | 26.7958 | 26.7823
101.6361 | -45.3639 | 31.3122 | 26.9312 | 27.3072 | 26.8266 | 27.0037 | 26.9692 | 26.8735 | 26.7845 | 26.8047
102.6276 | -44.3724 | 31.3167 | 26.9278 | 27.3116 | 26.8284 | 27.006 | 26.9677 | 26.8742 | 26.7922 | 26.7997
103.629 | -43.371 | 31.3148 | 26.9237 | 27.3119 | 26.8332 | 27.003 | 26.9624 | 26.8796 | 26.8019 | 26.7835
104.6305 | -42.3695 | 31.3148 | 26.9255 | 27.3095 | 26.8364 | 27.0041 | 26.9694 | 26.8784 | 26.7896 | 26.8112
105.6319 | -41.3681 | 31.3111 | 26.93 | 27.3144 | 26.8416 | 27.0064 | 26.9649 | 26.885 | 26.8082 | 26.7643
106.6333 | -40.3667 | 31.316 | 26.9273 | 27.3042 | 26.8385 | 27.0123 | 26.9703 | 26.876 | 26.7926 | 26.814
107.6248 | -39.3752 | 31.3187 | 26.9209 | 27.3093 | 26.8346 | 27.0096 | 26.9704 | 26.8745 | 26.7875 | 26.8031
108.6262 | -38.3738 | 31.3106 | 26.9274 | 27.3116 | 26.8421 | 27.0148 | 26.9699 | 26.8815 | 26.7819 | 26.8214
109.6276 | -37.3724 | 31.306 | 26.9209 | 27.3003 | 26.8393 | 26.9999 | 26.9742 | 26.8775 | 26.8 | 26.7948
110.6291 | -36.3709 | 31.3086 | 26.9262 | 27.3127 | 26.8442 | 27.0116 | 26.9764 | 26.8732 | 26.8058 | 26.7893
111.6305 | -35.3695 | 31.3037 | 26.9233 | 27.3179 | 26.8409 | 27.0085 | 26.9752 | 26.8765 | 26.794 | 26.802
112.632 | -34.368 | 31.3024 | 26.9256 | 27.3129 | 26.8373 | 27.0174 | 26.9709 | 26.8769 | 26.7926 | 26.8112
113.6334 | -33.3666 | 31.3059 | 26.9257 | 27.3057 | 26.8442 | 27.0187 | 26.9679 | 26.88 | 26.8101 | 26.7909
114.6248 | -32.3752 | 31.3027 | 26.9287 | 27.3238 | 26.8441 | 27.0123 | 26.9752 | 26.8835 | 26.7872 | 26.8128
115.6263 | -31.3737 | 31.306 | 26.9321 | 27.3095 | 26.8534 | 27.0058 | 26.9748 | 26.881 | 26.8012 | 26.799
116.6277 | -30.3723 | 31.3067 | 26.9335 | 27.321 | 26.8449 | 27.0144 | 26.9776 | 26.8838 | 26.8145 | 26.7885
117.6291 | -29.3709 | 31.3076 | 26.9292 | 27.3219 | 26.8484 | 27.009 | 26.9771 | 26.8772 | 26.7952 | 26.7888
118.6306 | -28.3694 | 31.3041 | 26.9328 | 27.3173 | 26.8518 | 27.0013 | 26.9798 | 26.8808 | 26.7998 | 26.8134
119.632 | -27.368 | 31.3042 | 26.9308 | 27.3073 | 26.8517 | 27.0205 | 26.9787 | 26.879 | 26.8053 | 26.7947
120.6335 | -26.3665 | 31.3062 | 26.9313 | 27.3254 | 26.8508 | 27.0208 | 26.9776 | 26.8803 | 26.7976 | 26.8055
121.6249 | -25.3751 | 31.2999 | 26.9314 | 27.3225 | 26.8546 | 27.0164 | 26.9748 | 26.8869 | 26.8 | 26.8004
122.6263 | -24.3737 | 31.2972 | 26.9289 | 27.3206 | 26.8544 | 27.0124 | 26.9751 | 26.8853 | 26.8057 | 26.7786
123.6278 | -23.3722 | 31.2976 | 26.9325 | 27.3214 | 26.8505 | 27.0155 | 26.9808 | 26.8844 | 26.8067 | 26.7757
124.6292 | -22.3708 | 31.2943 | 26.9282 | 27.3159 | 26.8537 | 27.0108 | 26.986 | 26.8891 | 26.7961 | 26.8078
125.6306 | -21.3694 | 31.3003 | 26.9287 | 27.3271 | 26.8562 | 27.0174 | 26.9783 | 26.8915 | 26.7961 | 26.7925
126.6321 | -20.3679 | 31.3066 | 26.9329 | 27.3206 | 26.8641 | 27.0124 | 26.9791 | 26.8837 | 26.7954 | 26.8076
127.6335 | -19.3665 | 31.3053 | 26.93 | 27.3267 | 26.8574 | 27.0225 | 26.9869 | 26.8836 | 26.8073 | 26.795
128.625 | -18.375 | 31.3029 | 26.9302 | 27.3236 | 26.8624 | 27.0128 | 26.9786 | 26.8914 | 26.8071 | 26.811
129.6264 | -17.3736 | 31.3066 | 26.9267 | 27.334 | 26.8565 | 27.0228 | 26.9833 | 26.8903 | 26.801 | 26.8181
130.6278 | -16.3722 | 31.3133 | 26.9333 | 27.3139 | 26.8621 | 27.0076 | 26.9854 | 26.8916 | 26.8179 | 26.7751
131.6293 | -15.3707 | 31.3121 | 26.9261 | 27.3272 | 26.8658 | 27.0247 | 26.9827 | 26.8867 | 26.7977 | 26.8156
132.6307 | -14.3693 | 31.3146 | 26.9321 | 27.3342 | 26.8666 | 27.0293 | 26.9838 | 26.8886 | 26.8085 | 26.8096
133.6322 | -13.3678 | 31.3157 | 26.9276 | 27.3255 | 26.8586 | 27.0289 | 26.9854 | 26.8886 | 26.7851 | 26.8016
134.6336 | -12.3664 | 31.316 | 26.9301 | 27.3266 | 26.8677 | 27.0165 | 26.9884 | 26.8911 | 26.819 | 26.7706
135.625 | -11.375 | 31.3176 | 26.927 | 27.3216 | 26.8679 | 27.0179 | 26.99 | 26.8866 | 26.8102 | 26.7887
136.6265 | -10.3735 | 31.314 | 26.9225 | 27.3383 | 26.8714 | 27.0282 | 26.9867 | 26.8905 | 26.8114 | 26.797
137.6279 | -9.3721 | 31.3198 | 26.9281 | 27.3307 | 26.8588 | 27.0364 | 26.9953 | 26.8911 | 26.8129 | 26.7997
138.6293 | -8.3707 | 31.3188 | 26.9306 | 27.332 | 26.8667 | 27.0269 | 26.9851 | 26.8929 | 26.8036 | 26.7972
139.6308 | -7.3692 | 31.319 | 26.942 | 27.3373 | 26.8659 | 27.0237 | 26.9885 | 26.8968 | 26.7908 | 26.8169
140.6322 | -6.3678 | 31.3169 | 26.9401 | 27.3358 | 26.8694 | 27.0297 | 26.9957 | 26.8963 | 26.8063 | 26.8069
141.6337 | -5.3663 | 31.3156 | 26.9433 | 27.3362 | 26.8632 | 27.0257 | 26.9905 | 26.8965 | 26.8098 | 26.8027
142.6351 | -4.3649 | 31.3134 | 26.942 | 27.3368 | 26.8614 | 27.0161 | 26.9885 | 26.8968 | 26.796 | 26.8053
143.6265 | -3.3735 | 31.3182 | 26.839 | 27.3241 | 26.8147 | 27.1213 | 27.1295 | 26.8706 | 26.7861 | 26.8473
144.628 | -2.372 | 31.3205 | 26.8509 | 27.3323 | 26.8272 | 27.1304 | 27.1247 | 26.8687 | 26.7975 | 26.8593
145.6294 | -1.3706 | 31.3484 | 26.8782 | 27.3461 | 26.853 | 27.1025 | 27.0886 | 26.8825 | 26.7874 | 26.863
146.6308 | -0.3692 | 31.6753 | 26.9008 | 27.3551 | 26.8537 | 27.0865 | 27.0723 | 26.8799 | 26.8067 | 26.8448
147.6323 | 0.6323 | 32.5618 | 26.9132 | 27.3502 | 26.8602 | 27.0955 | 27.0577 | 26.8951 | 26.7985 | 26.847
148.6337 | 1.6337 | 34.0303 | 26.9127 | 27.3665 | 26.8689 | 27.0819 | 27.0615 | 26.8869 | 26.804 | 26.8369
149.6252 | 2.6252 | 36.0244 | 26.9174 | 27.3857 | 26.8734 | 27.0761 | 27.0601 | 26.8936 | 26.8032 | 26.8283
150.6266 | 3.6266 | 38.4852 | 26.9267 | 27.3887 | 26.8878 | 27.0812 | 27.0509 | 26.8852 | 26.8186 | 26.828
151.628 | 4.628 | 41.3322 | 26.9287 | 27.4124 | 26.9007 | 27.0827 | 27.0556 | 26.8882 | 26.8086 | 26.8333
152.6295 | 5.6295 | 44.5262 | 26.9523 | 27.4232 | 26.9111 | 27.0832 | 27.0483 | 26.8927 | 26.8069 | 26.8316
153.6309 | 6.6309 | 48.0047 | 26.9622 | 27.4532 | 26.9163 | 27.0785 | 27.0525 | 26.8931 | 26.8083 | 26.8408
154.6324 | 7.6324 | 51.7429 | 26.9779 | 27.4781 | 26.9419 | 27.0704 | 27.047 | 26.8926 | 26.8069 | 26.8193
155.6238 | 8.6238 | 55.7093 | 26.994 | 27.4972 | 26.9677 | 27.083 | 27.0558 | 26.895 | 26.8048 | 26.8399
156.6252 | 9.6252 | 59.8476 | 27.0079 | 27.5727 | 26.9927 | 27.0849 | 27.0511 | 26.8906 | 26.8095 | 26.8357
157.6267 | 10.6267 | 64.1899 | 27.0323 | 27.634 | 27.0166 | 27.0863 | 27.0594 | 26.8956 | 26.8009 | 26.8534
158.6281 | 11.6281 | 68.6936 | 27.0752 | 27.6723 | 27.0511 | 27.0784 | 27.0526 | 26.8961 | 26.8082 | 26.8485
159.6295 | 12.6295 | 73.3368 | 27.1143 | 27.7094 | 27.0941 | 27.0773 | 27.057 | 26.8955 | 26.8095 | 26.8451
160.631 | 13.631 | 78.0715 | 27.144 | 27.7573 | 27.1307 | 27.0944 | 27.0561 | 26.9013 | 26.7926 | 26.8636
161.6324 | 14.6324 | 82.9394 | 27.1463 | 27.8263 | 27.1754 | 27.0808 | 27.0567 | 26.8986 | 26.8168 | 26.8118
162.6238 | 15.6238 | 87.934 | 27.1728 | 27.8935 | 27.2449 | 27.0738 | 27.0578 | 26.8944 | 26.803 | 26.856
163.6253 | 16.6253 | 93.059 | 27.2122 | 27.9862 | 27.3008 | 27.075 | 27.0575 | 26.8994 | 26.8304 | 26.8034
164.6267 | 17.6267 | 98.2689 | 27.2556 | 28.0529 | 27.3711 | 27.0902 | 27.0584 | 26.8955 | 26.8008 | 26.8439
165.6282 | 18.6282 | 103.5391 | 27.3207 | 28.1337 | 27.4399 | 27.0834 | 27.0574 | 26.8969 | 26.8142 | 26.8304
166.6296 | 19.6296 | 108.8847 | 27.3546 | 28.2213 | 27.4618 | 27.0916 | 27.0592 | 26.9006 | 26.8177 | 26.8195
167.631 | 20.631 | 114.3218 | 27.4305 | 28.338 | 27.505 | 27.0852 | 27.0614 | 26.9051 | 26.8186 | 26.8252
168.6325 | 21.6325 | 119.8676 | 27.479 | 28.4541 | 27.5705 | 27.0947 | 27.0602 | 26.9035 | 26.8104 | 26.8507
169.6339 | 22.6339 | 125.4166 | 27.5115 | 28.5941 | 27.6343 | 27.0965 | 27.0655 | 26.9102 | 26.8141 | 26.8423
170.6253 | 23.6253 | 130.9706 | 27.579 | 28.6812 | 27.7175 | 27.0867 | 27.0577 | 26.9125 | 26.823 | 26.8397
171.6268 | 24.6268 | 136.5129 | 27.632 | 28.8386 | 27.7874 | 27.1095 | 27.0701 | 26.9046 | 26.8106 | 26.8455
172.6282 | 25.6282 | 142.0557 | 27.7005 | 28.9817 | 27.8698 | 27.0953 | 27.0667 | 26.9112 | 26.8297 | 26.8197
173.6297 | 26.6297 | 147.6474 | 27.8021 | 29.1708 | 27.9676 | 27.0996 | 27.0753 | 26.9138 | 26.8184 | 26.8551
174.6311 | 27.6311 | 153.277 | 27.8789 | 29.2934 | 28.064 | 27.1003 | 27.068 | 26.9136 | 26.8142 | 26.8408
175.6325 | 28.6325 | 158.9185 | 27.9287 | 29.5196 | 28.1579 | 27.0985 | 27.0822 | 26.917 | 26.8159 | 26.855
176.624 | 29.624 | 164.4866 | 28.0161 | 29.6924 | 28.2528 | 27.1094 | 27.0728 | 26.9238 | 26.8176 | 26.8359
177.6254 | 30.6254 | 170.0962 | 28.0912 | 29.8572 | 28.3753 | 27.1039 | 27.0793 | 26.9252 | 26.8055 | 26.8594
178.6269 | 31.6269 | 175.7149 | 28.2055 | 30.048 | 28.4912 | 27.1184 | 27.0761 | 26.9298 | 26.8247 | 26.8574
179.6283 | 32.6283 | 181.3338 | 28.3183 | 30.263 | 28.6302 | 27.1047 | 27.0742 | 26.9288 | 26.8221 | 26.8371
180.6297 | 33.6297 | 187.0732 | 28.4082 | 30.4592 | 28.7478 | 27.1065 | 27.0779 | 26.9367 | 26.8222 | 26.8274
181.6312 | 34.6312 | 192.802 | 28.5071 | 30.6926 | 28.8887 | 27.1155 | 27.077 | 26.9396 | 26.8371 | 26.8288
182.6326 | 35.6326 | 198.5416 | 28.6309 | 30.9283 | 29.0158 | 27.1178 | 27.0916 | 26.9391 | 26.8333 | 26.8446
183.624 | 36.624 | 204.2916 | 28.7498 | 31.1935 | 29.1542 | 27.1093 | 27.0881 | 26.9506 | 26.825 | 26.8528
184.6355 | 37.6355 | 210.001 | 28.8661 | 31.4565 | 29.3077 | 27.1339 | 27.0973 | 26.9543 | 26.8395 | 26.8267
185.6269 | 38.6269 | 215.8062 | 29.0033 | 31.7493 | 29.4794 | 27.1268 | 27.0919 | 26.9592 | 26.8399 | 26.8583
186.6284 | 39.6284 | 221.5189 | 29.1765 | 32.0557 | 29.6383 | 27.1335 | 27.0997 | 26.9628 | 26.8388 | 26.8515
187.6298 | 40.6298 | 227.1 | 29.3294 | 32.3363 | 29.7909 | 27.1431 | 27.1067 | 26.975 | 26.8418 | 26.8618
188.6312 | 41.6312 | 232.7668 | 29.4451 | 32.6598 | 29.9664 | 27.1444 | 27.1111 | 26.981 | 26.8491 | 26.8419
189.6327 | 42.6327 | 238.3976 | 29.6061 | 32.9613 | 30.1597 | 27.1605 | 27.1164 | 26.9835 | 26.8501 | 26.8408
190.6341 | 43.6341 | 243.9743 | 29.7646 | 33.2559 | 30.3455 | 27.1433 | 27.115 | 26.996 | 26.8482 | 26.8501
191.6255 | 44.6255 | 249.5464 | 29.9409 | 33.5824 | 30.5258 | 27.157 | 27.1232 | 27.0019 | 26.8446 | 26.8576
192.627 | 45.627 | 255.0942 | 30.1042 | 33.9232 | 30.728 | 27.1615 | 27.1297 | 27.0173 | 26.8608 | 26.847
193.6284 | 46.6284 | 260.7556 | 30.2681 | 34.2939 | 30.9457 | 27.1698 | 27.1368 | 27.0253 | 26.8643 | 26.8466
194.6299 | 47.6299 | 266.2251 | 30.4819 | 34.622 | 31.1712 | 27.1708 | 27.1365 | 27.0409 | 26.8516 | 26.8791
195.6313 | 48.6313 | 271.7364 | 30.6472 | 34.9831 | 31.4217 | 27.1947 | 27.148 | 27.0471 | 26.868 | 26.8665
196.6327 | 49.6327 | 277.4086 | 30.8351 | 35.4312 | 31.6426 | 27.1953 | 27.1585 | 27.0633 | 26.8608 | 26.8702
197.6342 | 50.6342 | 282.999 | 31.0653 | 35.85 | 31.8908 | 27.2033 | 27.1625 | 27.0751 | 26.8677 | 26.8796
198.6256 | 51.6256 | 288.4716 | 31.2471 | 36.266 | 32.1342 | 27.2149 | 27.1769 | 27.0902 | 26.878 | 26.8801
199.627 | 52.627 | 293.9622 | 31.4483 | 36.6842 | 32.3912 | 27.2266 | 27.1761 | 27.1074 | 26.878 | 26.8756
200.6285 | 53.6285 | 299.3664 | 31.6552 | 37.1863 | 32.6549 | 27.2524 | 27.1915 | 27.1215 | 26.8745 | 26.8862
201.6299 | 54.6299 | 304.909 | 31.9139 | 37.6628 | 32.9273 | 27.2406 | 27.2 | 27.1419 | 26.895 | 26.8794
202.6314 | 55.6314 | 310.4199 | 32.1196 | 38.133 | 33.2293 | 27.262 | 27.2134 | 27.1618 | 26.9002 | 26.8909
203.6328 | 56.6328 | 315.8599 | 32.4668 | 38.6328 | 33.4984 | 27.2724 | 27.2257 | 27.1774 | 26.9138 | 26.8817
204.6242 | 57.6242 | 321.2957 | 32.648 | 39.1347 | 33.802 | 27.2987 | 27.2397 | 27.2058 | 26.9201 | 26.9061
205.6257 | 58.6257 | 326.609 | 32.8917 | 39.6953 | 34.0995 | 27.3219 | 27.2497 | 27.2241 | 26.9209 | 26.9008
206.6271 | 59.6271 | 332.0064 | 33.2001 | 40.2625 | 34.4285 | 27.3262 | 27.2661 | 27.2546 | 26.9283 | 26.8903
207.6286 | 60.6286 | 337.3973 | 33.424 | 40.8174 | 34.7697 | 27.3515 | 27.2843 | 27.2754 | 26.9275 | 26.9003
208.63 | 61.63 | 342.7571 | 33.7111 | 41.4402 | 35.0959 | 27.3794 | 27.2992 | 27.3073 | 26.9433 | 26.9119
209.6314 | 62.6314 | 348.0959 | 34.0162 | 41.9741 | 35.4306 | 27.3971 | 27.3181 | 27.3387 | 26.9519 | 26.9148
210.6329 | 63.6329 | 353.4355 | 34.3447 | 42.6358 | 35.7917 | 27.4163 | 27.3333 | 27.3711 | 26.9562 | 26.9319
211.6343 | 64.6343 | 358.7042 | 34.6331 | 43.2434 | 36.1771 | 27.4427 | 27.3574 | 27.41 | 26.9741 | 26.9277
212.6257 | 65.6257 | 363.949 | 34.9936 | 43.895 | 36.5384 | 27.4527 | 27.3636 | 27.4424 | 26.987 | 26.9303
213.6272 | 66.6272 | 369.2963 | 35.3242 | 44.6106 | 36.9508 | 27.5194 | 27.4076 | 27.4817 | 26.9977 | 26.9367
214.6286 | 67.6286 | 374.5609 | 35.7187 | 45.316 | 37.3769 | 27.5285 | 27.4135 | 27.5236 | 27.0069 | 26.9345
215.6301 | 68.6301 | 379.8117 | 35.9843 | 45.9752 | 37.7947 | 27.5856 | 27.4618 | 27.5647 | 27.0201 | 26.9503
216.6315 | 69.6315 | 384.8723 | 36.3539 | 46.6725 | 38.1304 | 27.6145 | 27.4901 | 27.6139 | 27.0241 | 26.9663
217.6329 | 70.6329 | 390.067 | 36.7514 | 47.3943 | 38.5484 | 27.6607 | 27.5139 | 27.6606 | 27.0359 | 26.968
218.7145 | 71.7145 | 395.7815 | 37.0814 | 48.2709 | 39.0687 | 27.6991 | 27.5506 | 27.7112 | 27.0726 | 26.9415
219.6258 | 72.6258 | 400.3844 | 37.4985 | 48.9902 | 39.4719 | 27.7453 | 27.5799 | 27.7612 | 27.0835 | 26.9529
220.6272 | 73.6272 | 405.3789 | 37.8918 | 49.7893 | 39.9513 | 27.7954 | 27.6149 | 27.8233 | 27.1014 | 26.9802
221.6287 | 74.6287 | 410.5467 | 38.2997 | 50.5588 | 40.4661 | 27.8452 | 27.6487 | 27.8769 | 27.113 | 27.0005
222.6301 | 75.6301 | 415.7579 | 38.6432 | 51.3824 | 40.9757 | 27.9059 | 27.6922 | 27.931 | 27.1216 | 27.0096
223.6316 | 76.6316 | 420.8959 | 39.1064 | 52.2612 | 41.4612 | 27.9451 | 27.7276 | 28.002 | 27.1403 | 27.0191
224.633 | 77.633 | 425.8933 | 39.5343 | 53.191 | 41.9663 | 28.0176 | 27.7827 | 28.0667 | 27.1575 | 27.0299
225.6244 | 78.6244 | 430.7543 | 40.0032 | 53.9985 | 42.4741 | 28.1018 | 27.8587 | 28.1309 | 27.1877 | 27.0373
226.6259 | 79.6259 | 435.6431 | 40.4044 | 54.9087 | 42.9759 | 28.2555 | 27.9988 | 28.1803 | 27.1728 | 27.104
227.6273 | 80.6273 | 440.3441 | 40.9376 | 55.8244 | 43.5024 | 28.2654 | 27.9892 | 28.2771 | 27.2311 | 27.0364
228.6288 | 81.6288 | 444.7393 | 41.4155 | 56.7813 | 44.003 | 28.388 | 28.0924 | 28.3384 | 27.2401 | 27.0827
229.6302 | 82.6302 | 448.6518 | 41.8699 | 57.6676 | 44.5618 | 28.4395 | 28.1288 | 28.4299 | 27.2622 | 27.0741
230.6316 | 83.6316 | 452.3227 | 42.3156 | 58.5802 | 45.1266 | 28.5272 | 28.1846 | 28.5092 | 27.2934 | 27.1011
231.6331 | 84.6331 | 455.6378 | 42.8593 | 59.5836 | 45.6936 | 28.6891 | 28.319 | 28.5794 | 27.2922 | 27.1843
232.6345 | 85.6345 | 458.7229 | 43.3433 | 60.5333 | 46.2437 | 28.6998 | 28.2967 | 28.692 | 27.3585 | 27.1193
233.636 | 86.636 | 461.583 | 43.8513 | 61.4626 | 46.8297 | 28.8347 | 28.3933 | 28.7765 | 27.3873 | 27.1306
234.6274 | 87.6274 | 464.54 | 44.328 | 62.4109 | 47.349 | 28.9071 | 28.4671 | 28.8748 | 27.4086 | 27.1484
235.6288 | 88.6288 | 467.433 | 44.7761 | 63.3843 | 47.9173 | 29.0137 | 28.5542 | 28.9647 | 27.4382 | 27.1602
236.6303 | 89.6303 | 470.1509 | 45.3015 | 64.363 | 48.5101 | 29.0925 | 28.5735 | 29.0668 | 27.4849 | 27.1418
237.6317 | 90.6317 | 472.6532 | 45.7282 | 65.3629 | 49.0526 | 29.2066 | 28.6574 | 29.1836 | 27.5059 | 27.1845
238.6331 | 91.6331 | 474.817 | 46.2742 | 66.2619 | 49.6196 | 29.3406 | 28.7632 | 29.2738 | 27.5583 | 27.2091
239.6246 | 92.6246 | 476.8195 | 46.8042 | 67.2752 | 50.1536 | 29.4463 | 28.8404 | 29.3882 | 27.5958 | 27.2127
240.626 | 93.626 | 478.5491 | 47.2605 | 68.2439 | 50.7236 | 29.5914 | 28.9506 | 29.4856 | 27.6385 | 27.244
241.6274 | 94.6274 | 479.9155 | 47.767 | 69.1766 | 51.2727 | 29.6971 | 29.0281 | 29.6024 | 27.6807 | 27.251
242.6289 | 95.6289 | 480.9108 | 48.2676 | 70.1339 | 51.8403 | 29.8424 | 29.1599 | 29.7098 | 27.7226 | 27.3141
243.6303 | 96.6303 | 481.7482 | 48.7646 | 71.0396 | 52.3693 | 29.9558 | 29.2352 | 29.8235 | 27.7651 | 27.3186
244.6318 | 97.6318 | 482.3846 | 49.2779 | 71.9503 | 52.8641 | 30.1019 | 29.3454 | 29.939 | 27.8198 | 27.3331
245.6332 | 98.6332 | 482.8631 | 49.7146 | 72.8406 | 53.4002 | 30.2318 | 29.45 | 30.0511 | 27.8743 | 27.3487
246.6246 | 99.6246 | 483.2032 | 50.189 | 73.7929 | 53.9263 | 30.3703 | 29.5604 | 30.169 | 27.9154 | 27.3929
247.6261 | 100.6261 | 483.2383 | 50.6368 | 74.6658 | 54.4114 | 30.5212 | 29.6721 | 30.2907 | 27.9745 | 27.4146
248.6275 | 101.6275 | 483.1925 | 51.1656 | 75.5776 | 54.9106 | 30.6646 | 29.785 | 30.4073 | 28.0231 | 27.457
249.6289 | 102.6289 | 482.963 | 51.5705 | 76.4282 | 55.4224 | 30.8153 | 29.9051 | 30.5283 | 28.0965 | 27.4746
250.6304 | 103.6304 | 482.7606 | 52.1076 | 77.2542 | 55.9283 | 30.9569 | 30.0181 | 30.6527 | 28.1479 | 27.5021
251.6318 | 104.6318 | 482.4505 | 52.5389 | 78.1003 | 56.4389 | 31.0968 | 30.1323 | 30.7683 | 28.2117 | 27.5324
252.6333 | 105.6333 | 482.2799 | 52.963 | 78.9483 | 56.935 | 31.2365 | 30.2454 | 30.8987 | 28.274 | 27.5395
253.6347 | 106.6347 | 481.9401 | 53.3467 | 79.7552 | 57.3937 | 31.3982 | 30.391 | 31.0184 | 28.3344 | 27.6178
254.6261 | 107.6261 | 481.59 | 53.7875 | 80.5671 | 57.8896 | 31.5253 | 30.4856 | 31.1472 | 28.4056 | 27.6129
255.6276 | 108.6276 | 481.0391 | 54.2263 | 81.3925 | 58.3225 | 31.6737 | 30.6092 | 31.2668 | 28.4685 | 27.6535
256.629 | 109.629 | 480.3903 | 54.7004 | 82.2164 | 58.8086 | 31.8011 | 30.7077 | 31.3947 | 28.5339 | 27.673
257.6305 | 110.6305 | 479.799 | 55.1217 | 83.0285 | 59.3162 | 31.9423 | 30.8236 | 31.5258 | 28.6053 | 27.7202
258.6319 | 111.6319 | 479.3016 | 55.5411 | 83.8326 | 59.7245 | 32.0625 | 30.9355 | 31.659 | 28.6965 | 27.7291
259.6333 | 112.6333 | 478.6174 | 55.9893 | 84.6134 | 60.2278 | 32.2131 | 31.0384 | 31.7886 | 28.744 | 27.7783
260.6248 | 113.6248 | 478.0203 | 56.3696 | 85.4424 | 60.6687 | 32.3696 | 31.1637 | 31.9118 | 28.8404 | 27.7952
261.6262 | 114.6262 | 477.4544 | 56.7742 | 86.219 | 61.1179 | 32.5017 | 31.2723 | 32.0362 | 28.8928 | 27.8721
262.6276 | 115.6276 | 476.9282 | 57.2193 | 87.0012 | 61.6275 | 32.6472 | 31.3898 | 32.1647 | 28.9959 | 27.8851
263.6291 | 116.6291 | 476.3617 | 57.6351 | 87.7866 | 62.0601 | 32.766 | 31.4949 | 32.311 | 29.0803 | 27.935
264.6305 | 117.6305 | 475.7465 | 58.0636 | 88.5903 | 62.5353 | 32.9209 | 31.6185 | 32.434 | 29.1578 | 27.9753
265.632 | 118.632 | 475.2847 | 58.4434 | 89.4089 | 63.0239 | 33.0412 | 31.72 | 32.5676 | 29.2508 | 28.0326
266.6334 | 119.6334 | 474.8891 | 58.811 | 90.1454 | 63.4254 | 33.1878 | 31.8309 | 32.7056 | 29.3252 | 28.064
267.6248 | 120.6248 | 474.4693 | 59.2788 | 90.9099 | 63.8604 | 33.3022 | 31.9307 | 32.8381 | 29.4169 | 28.1359
268.6263 | 121.6263 | 473.8365 | 59.6353 | 91.667 | 64.3032 | 33.4483 | 32.0469 | 32.9691 | 29.5001 | 28.1737
269.6277 | 122.6277 | 473.3238 | 60.0384 | 92.3974 | 64.7449 | 33.5892 | 32.1521 | 33.1014 | 29.6029 | 28.2067
270.6291 | 123.6291 | 472.8311 | 60.4482 | 93.0831 | 65.1561 | 33.7179 | 32.2594 | 33.2413 | 29.6965 | 28.2609
271.6306 | 124.6306 | 472.4198 | 60.8555 | 93.8581 | 65.6028 | 33.8553 | 32.3721 | 33.377 | 29.7869 | 28.2999
272.632 | 125.632 | 472.2375 | 61.2782 | 94.673 | 66.109 | 33.9824 | 32.4682 | 33.5154 | 29.8869 | 28.3506
273.6335 | 126.6335 | 472.2399 | 61.6751 | 95.4743 | 66.5288 | 34.1266 | 32.5985 | 33.6449 | 29.9755 | 28.4207
274.6349 | 127.6349 | 472.081 | 62.1105 | 96.2196 | 66.9566 | 34.2482 | 32.6772 | 33.7924 | 30.0868 | 28.45
275.6263 | 128.6263 | 471.8136 | 62.4499 | 96.9821 | 67.3904 | 34.3946 | 32.8146 | 33.9186 | 30.1836 | 28.5378
276.6278 | 129.6278 | 471.6348 | 62.8841 | 97.7186 | 67.7774 | 34.5004 | 32.8962 | 34.0688 | 30.2964 | 28.5681
277.6292 | 130.6292 | 471.4793 | 63.2777 | 98.5213 | 68.2433 | 34.6378 | 33.0069 | 34.2103 | 30.3937 | 28.632
278.6307 | 131.6307 | 471.5023 | 63.6872 | 99.2458 | 68.6813 | 34.7656 | 33.1126 | 34.35 | 30.497 | 28.694
279.6321 | 132.6321 | 471.5704 | 64.0578 | 99.9185 | 69.1236 | 34.9016 | 33.2217 | 34.4934 | 30.6016 | 28.7412
280.6335 | 133.6335 | 471.6795 | 64.4341 | 100.6583 | 69.5471 | 35.0359 | 33.3384 | 34.6327 | 30.705 | 28.8219
281.625 | 134.625 | 471.8217 | 64.7958 | 101.5357 | 69.9658 | 35.1606 | 33.4375 | 34.7755 | 30.8353 | 28.8426
282.6264 | 135.6264 | 471.8806 | 65.2201 | 102.2636 | 70.3709 | 35.3335 | 33.6039 | 34.903 | 30.9166 | 28.9579
283.6278 | 136.6278 | 472.1639 | 65.6619 | 103.018 | 70.8095 | 35.4157 | 33.6659 | 35.0649 | 31.044 | 28.9724
284.6293 | 137.6293 | 472.4628 | 66.0445 | 103.8021 | 71.2427 | 35.5876 | 33.8197 | 35.1965 | 31.1585 | 29.0737
285.6307 | 138.6307 | 472.6073 | 66.458 | 104.5506 | 71.7016 | 35.6768 | 33.8936 | 35.356 | 31.2739 | 29.1153
286.6322 | 139.6322 | 472.8159 | 66.831 | 105.3183 | 72.1668 | 35.8069 | 34.0071 | 35.4995 | 31.3895 | 29.1657
287.6236 | 140.6236 | 473.1102 | 67.2623 | 105.9892 | 72.6037 | 35.9401 | 34.1222 | 35.6498 | 31.4784 | 29.2534
288.625 | 141.625 | 473.3697 | 67.6537 | 106.7409 | 73.0416 | 36.0763 | 34.2425 | 35.7921 | 31.6111 | 29.301
289.6265 | 142.6265 | 473.6792 | 68.062 | 107.4861 | 73.488 | 36.1956 | 34.3496 | 35.9386 | 31.7332 | 29.3555
290.6279 | 143.6279 | 473.915 | 68.4494 | 108.2106 | 73.8819 | 36.3378 | 34.4593 | 36.0858 | 31.8406 | 29.4365
291.6293 | 144.6293 | 474.0677 | 68.8626 | 108.9835 | 74.2788 | 36.4515 | 34.5913 | 36.2371 | 31.9623 | 29.4634
292.6308 | 145.6308 | 474.2717 | 69.2474 | 109.75 | 74.7822 | 36.5887 | 34.7018 | 36.384 | 32.0772 | 29.5519
293.6322 | 146.6322 | 474.3593 | 69.6711 | 110.5452 | 75.2212 | 36.7238 | 34.8292 | 36.5397 | 32.1826 | 29.6382
294.6337 | 147.6337 | 474.603 | 70.0567 | 111.3119 | 75.6455 | 36.8481 | 34.9432 | 36.6839 | 32.3072 | 29.6902
295.6351 | 148.6351 | 474.8435 | 70.4646 | 112.0063 | 76.1183 | 36.991 | 35.0767 | 36.8401 | 32.4288 | 29.7618
296.6265 | 149.6265 | 475.077 | 70.864 | 112.7624 | 76.5414 | 37.1126 | 35.1943 | 36.9921 | 32.5561 | 29.8201
297.628 | 150.628 | 475.2049 | 71.2861 | 113.4855 | 76.9663 | 37.2459 | 35.3119 | 37.1494 | 32.6727 | 29.9067
298.6294 | 151.6294 | 475.3273 | 71.6612 | 114.2771 | 77.4084 | 37.3644 | 35.4318 | 37.2974 | 32.7897 | 29.9685
299.6308 | 152.6308 | 475.3977 | 72.049 | 115.025 | 77.8902 | 37.5057 | 35.5514 | 37.4609 | 32.9118 | 30.0407
300.6323 | 153.6323 | 475.5439 | 72.4464 | 115.7925 | 78.3077 | 37.6451 | 35.6897 | 37.6092 | 33.0424 | 30.0842
301.6337 | 154.6337 | 475.6685 | 72.893 | 116.5216 | 78.751 | 37.7716 | 35.8103 | 37.7684 | 33.1539 | 30.1902
302.6252 | 155.6252 | 475.5623 | 73.2744 | 117.2355 | 79.1756 | 37.9114 | 35.9408 | 37.9236 | 33.2871 | 30.2342
303.7668 | 156.7668 | 475.6722 | 73.715 | 118.0862 | 79.6798 | 38.0589 | 36.0764 | 38.0982 | 33.4314 | 30.3143
304.628 | 157.628 | 475.8202 | 74.0809 | 118.7554 | 80.0372 | 38.1967 | 36.1995 | 38.2384 | 33.5284 | 30.3862
305.6295 | 158.6295 | 476.0537 | 74.4889 | 119.4924 | 80.471 | 38.3151 | 36.3223 | 38.4062 | 33.6542 | 30.4722
306.6309 | 159.6309 | 476.1442 | 74.8786 | 120.2084 | 80.917 | 38.4506 | 36.4517 | 38.5636 | 33.7717 | 30.5319
307.6324 | 160.6324 | 476.2952 | 75.3008 | 120.9427 | 81.3774 | 38.589 | 36.5771 | 38.7205 | 33.9047 | 30.6058
308.6238 | 161.6238 | 476.4842 | 75.669 | 121.6915 | 81.8064 | 38.7313 | 36.712 | 38.8777 | 34.0187 | 30.704
309.6252 | 162.6252 | 476.5881 | 76.0924 | 122.3643 | 82.2822 | 38.8576 | 36.8373 | 39.0483 | 34.1535 | 30.7537
310.6267 | 163.6267 | 476.6289 | 76.4909 | 123.1163 | 82.7065 | 39.0064 | 36.9801 | 39.2082 | 34.2844 | 30.8312
311.6281 | 164.6281 | 476.6888 | 76.8986 | 123.8232 | 83.1041 | 39.1489 | 37.1133 | 39.3638 | 34.3891 | 30.9105
312.6295 | 165.6295 | 476.7686 | 77.3044 | 124.5398 | 83.5413 | 39.2801 | 37.2387 | 39.5363 | 34.5159 | 30.9795
313.631 | 166.631 | 476.9581 | 77.7219 | 125.2266 | 83.9971 | 39.4251 | 37.3802 | 39.6985 | 34.6634 | 31.0224
314.6324 | 167.6324 | 477.0391 | 78.1219 | 125.957 | 84.4439 | 39.5666 | 37.5114 | 39.867 | 34.7844 | 31.112
315.6238 | 168.6238 | 476.9871 | 78.4955 | 126.6756 | 84.8809 | 39.7002 | 37.6464 | 40.0325 | 34.9237 | 31.1639
316.6353 | 169.6353 | 476.9009 | 78.9178 | 127.3641 | 85.3258 | 39.8315 | 37.7811 | 40.2104 | 35.0408 | 31.2543
317.6267 | 170.6267 | 476.9353 | 79.3523 | 128.077 | 85.7581 | 39.9831 | 37.9169 | 40.3762 | 35.1624 | 31.3449
318.6282 | 171.6282 | 476.9138 | 79.7347 | 128.7998 | 86.2108 | 40.1255 | 38.0605 | 40.5388 | 35.2872 | 31.429
319.6296 | 172.6296 | 477.0161 | 80.1528 | 129.5353 | 86.6264 | 40.2695 | 38.195 | 40.7084 | 35.4119 | 31.4828
320.631 | 173.631 | 477.0264 | 80.5722 | 130.2286 | 87.0868 | 40.4157 | 38.34 | 40.8778 | 35.5353 | 31.5534
321.6525 | 174.6525 | 477.1519 | 81.0022 | 130.9329 | 87.529 | 40.5647 | 38.4751 | 41.0481 | 35.6702 | 31.6297
322.6339 | 175.6339 | 477.1472 | 81.379 | 131.6648 | 87.9707 | 40.7115 | 38.62 | 41.2193 | 35.7842 | 31.6988
323.6254 | 176.6254 | 477.0719 | 81.7638 | 132.3571 | 88.418 | 40.8369 | 38.7557 | 41.391 | 35.9108 | 31.775
324.6268 | 177.6268 | 477.067 | 82.2059 | 133.0513 | 88.858 | 40.9974 | 38.8971 | 41.5584 | 36.0334 | 31.8333
325.6282 | 178.6282 | 477.1222 | 82.627 | 133.7514 | 89.3387 | 41.1383 | 39.0369 | 41.7346 | 36.1817 | 31.8773
326.6297 | 179.6297 | 477.2283 | 83.0139 | 134.3935 | 89.7782 | 41.2928 | 39.1843 | 41.9075 | 36.3029 | 31.9444
327.6311 | 180.6311 | 477.3754 | 83.4458 | 135.1116 | 90.2038 | 41.4333 | 39.3371 | 42.079 | 36.4202 | 32.0424
328.6326 | 181.6326 | 477.5662 | 83.8413 | 135.8066 | 90.6539 | 41.577 | 39.4764 | 42.2468 | 36.5406 | 32.1085
329.624 | 182.624 | 477.6446 | 84.2138 | 136.5426 | 91.0869 | 41.7207 | 39.6227 | 42.4221 | 36.6569 | 32.1858
330.6254 | 183.6254 | 477.7483 | 84.6603 | 137.1961 | 91.5126 | 41.8783 | 39.7706 | 42.5987 | 36.7856 | 32.2421
331.6269 | 184.6269 | 477.8194 | 85.0183 | 137.8556 | 91.9361 | 42.0229 | 39.9278 | 42.7776 | 36.9084 | 32.3171
332.6283 | 185.6283 | 477.8745 | 85.3986 | 138.5245 | 92.4149 | 42.1716 | 40.0745 | 42.95 | 37.0411 | 32.3672
333.6297 | 186.6297 | 477.8971 | 85.8228 | 139.2385 | 92.854 | 42.3185 | 40.2273 | 43.1254 | 37.1665 | 32.4258
334.6312 | 187.6312 | 477.8543 | 86.2454 | 139.9297 | 93.2701 | 42.4659 | 40.3689 | 43.2999 | 37.2666 | 32.5142
335.6326 | 188.6326 | 477.9219 | 86.6612 | 140.6142 | 93.7379 | 42.6235 | 40.5286 | 43.478 | 37.388 | 32.5862
336.6341 | 189.6341 | 477.8835 | 87.0732 | 141.2728 | 94.1894 | 42.766 | 40.6767 | 43.6641 | 37.5239 | 32.6418
337.6355 | 190.6355 | 477.8227 | 87.4814 | 141.9381 | 94.6315 | 42.9264 | 40.8258 | 43.8369 | 37.6334 | 32.718
338.6269 | 191.6269 | 477.7849 | 87.8822 | 142.6294 | 95.0599 | 43.0729 | 40.9803 | 44.0212 | 37.7673 | 32.7813
339.6284 | 192.6284 | 477.638 | 88.3134 | 143.2592 | 95.4905 | 43.2254 | 41.1346 | 44.1975 | 37.8819 | 32.8404
340.6298 | 193.6298 | 477.5864 | 88.676 | 143.9802 | 95.9405 | 43.3795 | 41.2888 | 44.3736 | 38.0134 | 32.9003
341.6312 | 194.6312 | 477.7353 | 89.0694 | 144.616 | 96.4238 | 43.533 | 41.4421 | 44.5539 | 38.1237 | 32.9568
342.6327 | 195.6327 | 477.8607 | 89.5059 | 145.293 | 96.837 | 43.6879 | 41.5905 | 44.7425 | 38.2389 | 33.0212
343.6341 | 196.6341 | 477.8867 | 89.842 | 145.9458 | 97.2847 | 43.841 | 41.7497 | 44.9205 | 38.3838 | 33.0733
344.6255 | 197.6255 | 477.9534 | 90.2637 | 146.5703 | 97.7163 | 43.9911 | 41.9008 | 45.1014 | 38.4961 | 33.1245
345.627 | 198.627 | 477.9499 | 90.7089 | 147.2467 | 98.1474 | 44.1444 | 42.0609 | 45.2859 | 38.6114 | 33.1858
346.6284 | 199.6284 | 477.8898 | 91.1249 | 147.8767 | 98.5964 | 44.304 | 42.2143 | 45.4739 | 38.733 | 33.2358
347.6299 | 200.6299 | 478.0053 | 91.5729 | 148.5656 | 99.0307 | 44.4659 | 42.3715 | 45.6579 | 38.8544 | 33.2997
348.6313 | 201.6313 | 478.2905 | 91.9207 | 149.2261 | 99.4357 | 44.6174 | 42.5285 | 45.8367 | 38.9672 | 33.3705
349.6327 | 202.6327 | 478.3476 | 92.3343 | 149.8945 | 99.8944 | 44.77 | 42.6892 | 46.0288 | 39.0931 | 33.4242
350.6242 | 203.6242 | 478.611 | 92.7344 | 150.5573 | 100.3164 | 44.9453 | 42.8539 | 46.2177 | 39.2045 | 33.4851
351.6256 | 204.6256 | 478.8328 | 93.1502 | 151.2246 | 100.7533 | 45.0846 | 43.0157 | 46.4105 | 39.3251 | 33.5428
352.6271 | 205.6271 | 478.9775 | 93.5455 | 151.8972 | 101.2066 | 45.2599 | 43.1774 | 46.6026 | 39.4422 | 33.6086
353.6285 | 206.6285 | 479.027 | 93.9325 | 152.549 | 101.6516 | 45.4066 | 43.3343 | 46.7885 | 39.5591 | 33.6649
354.6299 | 207.6299 | 479.0512 | 94.3081 | 153.1853 | 102.0847 | 45.5766 | 43.4973 | 46.9897 | 39.6929 | 33.6994
355.6314 | 208.6314 | 478.9436 | 94.7754 | 153.8215 | 102.5295 | 45.7343 | 43.6538 | 47.1808 | 39.8182 | 33.7695
356.6328 | 209.6328 | 478.9395 | 95.2113 | 154.4737 | 102.9539 | 45.8922 | 43.8185 | 47.3821 | 39.9351 | 33.8243
357.6343 | 210.6343 | 478.9992 | 95.5461 | 155.1731 | 103.4046 | 46.049 | 43.9748 | 47.576 | 40.0445 | 33.8877
358.6357 | 211.6357 | 479.1463 | 95.9594 | 155.7769 | 103.8462 | 46.2204 | 44.1356 | 47.7866 | 40.175 | 33.9628
359.6271 | 212.6271 | 479.3377 | 96.4047 | 156.4338 | 104.2836 | 46.3815 | 44.2951 | 47.9801 | 40.2947 | 33.999
360.6286 | 213.6286 | 479.5435 | 96.7653 | 157.0951 | 104.7199 | 46.5337 | 44.4589 | 48.1882 | 40.4027 | 34.0596
361.63 | 214.63 | 479.5698 | 97.1506 | 157.8247 | 105.1602 | 46.7049 | 44.6074 | 48.3888 | 40.5409 | 34.1153
362.6314 | 215.6314 | 479.4949 | 97.5808 | 158.3971 | 105.5677 | 46.8625 | 44.7653 | 48.5981 | 40.6595 | 34.1774
363.6329 | 216.6329 | 479.5073 | 98.0006 | 158.984 | 106.0081 | 47.0369 | 44.921 | 48.7987 | 40.7775 | 34.2194
364.6343 | 217.6343 | 479.5004 | 98.4184 | 159.6676 | 106.399 | 47.1942 | 45.0792 | 49.0048 | 40.8746 | 34.3002
365.6257 | 218.6257 | 479.4862 | 98.806 | 160.3409 | 106.8298 | 47.3661 | 45.2428 | 49.2131 | 41.0019 | 34.3328
366.6272 | 219.6272 | 479.4042 | 99.2306 | 161.004 | 107.2663 | 47.5187 | 45.3917 | 49.4202 | 41.1176 | 34.4096
367.6286 | 220.6286 | 479.2472 | 99.5682 | 161.5852 | 107.7161 | 47.6914 | 45.5583 | 49.6404 | 41.2351 | 34.4536
368.6301 | 221.6301 | 479.12 | 99.9576 | 162.2356 | 108.1362 | 47.8587 | 45.7154 | 49.8429 | 41.3641 | 34.4935
369.6315 | 222.6315 | 479.0105 | 100.328 | 162.869 | 108.5594 | 48.0336 | 45.8732 | 50.0619 | 41.4882 | 34.548
370.6329 | 223.6329 | 479.0395 | 100.7402 | 163.5447 | 108.9698 | 48.2022 | 46.0294 | 50.2703 | 41.5861 | 34.6216
371.6244 | 224.6244 | 479.0042 | 101.1618 | 164.1337 | 109.37 | 48.3763 | 46.1931 | 50.4842 | 41.7075 | 34.672
372.6258 | 225.6258 | 478.9773 | 101.5739 | 164.7303 | 109.8297 | 48.5493 | 46.3508 | 50.6976 | 41.8188 | 34.7342
373.6272 | 226.6272 | 478.9489 | 101.9672 | 165.3605 | 110.2424 | 48.7213 | 46.5009 | 50.9045 | 41.932 | 34.7942
374.6287 | 227.6287 | 478.9485 | 102.3878 | 165.9961 | 110.6423 | 48.914 | 46.6704 | 51.1232 | 42.0565 | 34.8454
375.6301 | 228.6301 | 478.8008 | 102.7613 | 166.6358 | 111.0512 | 49.0843 | 46.826 | 51.3404 | 42.1857 | 34.8776
376.6316 | 229.6316 | 478.5311 | 103.1353 | 167.2652 | 111.5172 | 49.2568 | 46.978 | 51.5561 | 42.2812 | 34.9658
377.633 | 230.633 | 478.4096 | 103.5091 | 167.8515 | 111.976 | 49.4565 | 47.1307 | 51.773 | 42.4114 | 34.9993
378.6244 | 231.6244 | 478.3345 | 103.8996 | 168.4791 | 112.3598 | 49.6543 | 47.2933 | 51.9904 | 42.5097 | 35.0725
379.6359 | 232.6359 | 478.0884 | 104.2963 | 169.097 | 112.7912 | 49.8377 | 47.451 | 52.204 | 42.6499 | 35.0932
380.6273 | 233.6273 | 478.0175 | 104.7092 | 169.7005 | 113.2185 | 50.0359 | 47.6046 | 52.4219 | 42.7603 | 35.1622
381.6288 | 234.6288 | 478.0848 | 105.0737 | 170.3098 | 113.6294 | 50.2341 | 47.7548 | 52.64 | 42.875 | 35.2143
382.6302 | 235.6302 | 478.1208 | 105.4785 | 170.9053 | 114.0768 | 50.4397 | 47.9156 | 52.857 | 42.9857 | 35.2692
383.6316 | 236.6316 | 478.2366 | 105.8972 | 171.5388 | 114.4846 | 50.6479 | 48.0686 | 53.0765 | 43.091 | 35.3387
384.6331 | 237.6331 | 478.2128 | 106.2628 | 172.2054 | 114.8799 | 50.8655 | 48.2249 | 53.2998 | 43.203 | 35.3975
385.6345 | 238.6345 | 478.3849 | 106.6274 | 172.7922 | 115.3022 | 51.0872 | 48.3778 | 53.5265 | 43.3246 | 35.4331
386.6259 | 239.6259 | 478.5035 | 107.0355 | 173.379 | 115.7108 | 51.3106 | 48.5252 | 53.744 | 43.427 | 35.516
387.6274 | 240.6274 | 478.5299 | 107.4472 | 174.0082 | 116.1423 | 51.5481 | 48.6866 | 53.9664 | 43.5658 | 35.5392
388.6288 | 241.6288 | 478.6217 | 107.8208 | 174.6392 | 116.5651 | 51.7797 | 48.8394 | 54.1915 | 43.6622 | 35.6357
389.6303 | 242.6303 | 478.8137 | 108.2298 | 175.2386 | 116.984 | 52.0213 | 48.9972 | 54.4136 | 43.7914 | 35.6715
390.6317 | 243.6317 | 479.0669 | 108.6435 | 175.8417 | 117.3875 | 52.2582 | 49.153 | 54.6362 | 43.9127 | 35.7364
391.6331 | 244.6331 | 479.2355 | 109.0283 | 176.4742 | 117.7846 | 52.5114 | 49.3202 | 54.8627 | 44.0136 | 35.7946
392.6246 | 245.6246 | 479.3819 | 109.3903 | 177.0386 | 118.2043 | 52.7627 | 49.4779 | 55.0916 | 44.1395 | 35.8604
393.626 | 246.626 | 479.4574 | 109.7975 | 177.6423 | 118.6728 | 53.0074 | 49.6413 | 55.3217 | 44.2619 | 35.9271
394.6274 | 247.6274 | 479.5344 | 110.1269 | 178.2711 | 119.0721 | 53.2705 | 49.8008 | 55.5555 | 44.3789 | 35.979
395.6289 | 248.6289 | 479.632 | 110.542 | 178.885 | 119.4955 | 53.5252 | 49.9636 | 55.7774 | 44.5142 | 36.0396
396.6303 | 249.6303 | 479.7593 | 110.9886 | 179.4599 | 119.9014 | 53.7838 | 50.1377 | 56.0087 | 44.6497 | 36.0796
397.6318 | 250.6318 | 479.6871 | 111.3591 | 180.0755 | 120.3011 | 54.0449 | 50.3009 | 56.2338 | 44.7818 | 36.1411
398.6733 | 251.6733 | 479.694 | 111.7509 | 180.7101 | 120.7321 | 54.3152 | 50.4852 | 56.4838 | 44.9155 | 36.2462
399.6246 | 252.6246 | 479.8132 | 112.0987 | 181.3263 | 121.1065 | 54.5676 | 50.6588 | 56.7032 | 45.0418 | 36.2914
400.6261 | 253.6261 | 480.0033 | 112.4909 | 181.8771 | 121.503 | 54.8238 | 50.834 | 56.9391 | 45.2009 | 36.3333
401.6275 | 254.6275 | 479.9305 | 112.9106 | 182.4798 | 121.8391 | 55.0806 | 51.0146 | 57.1745 | 45.33 | 36.4171
402.629 | 255.629 | 479.8683 | 113.2778 | 183.0535 | 122.2744 | 55.3402 | 51.2033 | 57.4095 | 45.4904 | 36.4486
403.6304 | 256.6304 | 479.8079 | 113.67 | 183.618 | 122.7546 | 55.6079 | 51.4014 | 57.6506 | 45.626 | 36.5425
404.6318 | 257.6318 | 479.8567 | 114.0351 | 184.2423 | 123.1212 | 55.8624 | 51.5928 | 57.889 | 45.7778 | 36.5913
405.6333 | 258.6333 | 479.8637 | 114.4274 | 184.8295 | 123.5277 | 56.1167 | 51.8101 | 58.1245 | 45.9246 | 36.6673
406.6347 | 259.6347 | 479.9047 | 114.7822 | 185.4027 | 123.9539 | 56.3772 | 52.0166 | 58.3697 | 46.0824 | 36.7243
407.6261 | 260.6261 | 479.8323 | 115.1798 | 185.9927 | 124.3839 | 56.6408 | 52.2345 | 58.6104 | 46.2474 | 36.7739
408.6276 | 261.6276 | 479.8114 | 115.5615 | 186.5338 | 124.7643 | 56.9011 | 52.4525 | 58.8511 | 46.403 | 36.8403
409.629 | 262.629 | 479.6096 | 115.9756 | 187.1037 | 125.1934 | 57.1764 | 52.683 | 59.1027 | 46.5481 | 36.9328
410.6305 | 263.6305 | 479.3572 | 116.3082 | 187.6847 | 125.5889 | 57.4248 | 52.919 | 59.3473 | 46.7108 | 36.982
411.6319 | 264.6319 | 479.2318 | 116.714 | 188.2853 | 126.0048 | 57.6963 | 53.1658 | 59.5857 | 46.8708 | 37.0462
412.6333 | 265.6333 | 479.2132 | 117.097 | 188.8691 | 126.4024 | 57.9498 | 53.4039 | 59.8309 | 47.0316 | 37.1021
413.6248 | 266.6248 | 479.1669 | 117.4068 | 189.427 | 126.7787 | 58.2127 | 53.6629 | 60.0799 | 47.2011 | 37.1418
414.6262 | 267.6262 | 479.0013 | 117.808 | 189.9827 | 127.1758 | 58.4933 | 53.9177 | 60.3251 | 47.3661 | 37.2178
415.6276 | 268.6276 | 478.8896 | 118.1539 | 190.5765 | 127.5772 | 58.765 | 54.181 | 60.5762 | 47.5257 | 37.2964
416.6291 | 269.6291 | 478.8351 | 118.545 | 191.1322 | 127.9625 | 59.0437 | 54.4452 | 60.822 | 47.6882 | 37.3393
417.6305 | 270.6305 | 478.771 | 118.9634 | 191.7221 | 128.3847 | 59.3329 | 54.7168 | 61.0687 | 47.8463 | 37.4262
418.632 | 271.632 | 478.609 | 119.2995 | 192.2848 | 128.765 | 59.6072 | 54.998 | 61.3098 | 48.0243 | 37.4725
419.6334 | 272.6334 | 478.6066 | 119.6922 | 192.8401 | 129.1762 | 59.8938 | 55.2657 | 61.5613 | 48.174 | 37.5803
420.6248 | 273.6248 | 478.5034 | 120.0535 | 193.4448 | 129.5517 | 60.1805 | 55.5471 | 61.8171 | 48.3423 | 37.6473
421.6263 | 274.6263 | 478.3898 | 120.4059 | 194.0062 | 129.9597 | 60.4635 | 55.8219 | 62.0624 | 48.5237 | 37.7106
422.6277 | 275.6277 | 478.312 | 120.7774 | 194.5977 | 130.3533 | 60.7601 | 56.1075 | 62.3125 | 48.6989 | 37.7495
423.6291 | 276.6291 | 478.1313 | 121.1659 | 195.1304 | 130.7338 | 61.0545 | 56.3809 | 62.5631 | 48.8743 | 37.8231
424.6306 | 277.6306 | 478.0181 | 121.5308 | 195.6854 | 131.118 | 61.3467 | 56.6631 | 62.8141 | 49.0368 | 37.9206
425.632 | 278.632 | 477.9287 | 121.8933 | 196.2051 | 131.5126 | 61.643 | 56.9492 | 63.065 | 49.2256 | 37.9749
426.6335 | 279.6335 | 478.0157 | 122.2437 | 196.7627 | 131.9057 | 61.9371 | 57.2301 | 63.3165 | 49.4053 | 38.0223
427.6349 | 280.6349 | 477.9058 | 122.6117 | 197.3391 | 132.2956 | 62.243 | 57.501 | 63.5741 | 49.5743 | 38.107
428.6263 | 281.6263 | 477.9347 | 122.9618 | 197.9095 | 132.6655 | 62.5479 | 57.7897 | 63.8326 | 49.7587 | 38.1715
429.6278 | 282.6278 | 477.9927 | 123.3308 | 198.4566 | 133.047 | 62.8503 | 58.0729 | 64.0783 | 49.9441 | 38.2381
430.6292 | 283.6292 | 477.9143 | 123.7154 | 199.0221 | 133.4597 | 63.1547 | 58.3508 | 64.3368 | 50.1248 | 38.3053
431.6307 | 284.6307 | 477.7832 | 124.0464 | 199.6145 | 133.8291 | 63.4609 | 58.6524 | 64.5843 | 50.2968 | 38.3782
432.6321 | 285.6321 | 477.7374 | 124.4651 | 200.1497 | 134.2434 | 63.7708 | 58.9429 | 64.8448 | 50.4865 | 38.4479
433.6335 | 286.6335 | 477.9408 | 124.8478 | 200.7076 | 134.6502 | 64.0778 | 59.2326 | 65.0958 | 50.6719 | 38.5362
434.625 | 287.625 | 478.0922 | 125.2092 | 201.2808 | 135.0439 | 64.3821 | 59.5053 | 65.363 | 50.8545 | 38.5963
435.6264 | 288.6264 | 478.064 | 125.5431 | 201.8292 | 135.4348 | 64.7044 | 59.7936 | 65.6118 | 51.0416 | 38.6622
436.6278 | 289.6278 | 477.9484 | 125.9227 | 202.3725 | 135.811 | 65.0026 | 60.0864 | 65.8669 | 51.2265 | 38.7376
437.6293 | 290.6293 | 477.9206 | 126.2455 | 202.937 | 136.2046 | 65.3088 | 60.366 | 66.128 | 51.4055 | 38.8116
438.6307 | 291.6307 | 477.9661 | 126.6072 | 203.5127 | 136.5613 | 65.6275 | 60.6522 | 66.391 | 51.5875 | 38.9007
439.6322 | 292.6322 | 478.0527 | 126.9749 | 204.0414 | 136.9138 | 65.918 | 60.9402 | 66.6454 | 51.7721 | 38.946
440.6236 | 293.6236 | 478.1252 | 127.3523 | 204.5507 | 137.3261 | 66.2409 | 61.2337 | 66.9043 | 51.9546 | 39.0374
441.625 | 294.625 | 478.294 | 127.7309 | 205.1155 | 137.7189 | 66.5427 | 61.5133 | 67.1621 | 52.1502 | 39.0889
442.6265 | 295.6265 | 478.422 | 128.0926 | 205.7054 | 138.0924 | 66.8666 | 61.8062 | 67.4238 | 52.3321 | 39.1712
443.6279 | 296.6279 | 478.5135 | 128.4561 | 206.2246 | 138.5034 | 67.1719 | 62.0913 | 67.6761 | 52.5333 | 39.2596
444.6293 | 297.6293 | 478.5976 | 128.8024 | 206.7569 | 138.8926 | 67.4833 | 62.3812 | 67.9453 | 52.7012 | 39.3479
445.6308 | 298.6308 | 478.6603 | 129.1374 | 207.3369 | 139.262 | 67.8051 | 62.6613 | 68.2026 | 52.9021 | 39.3924
446.6322 | 299.6322 | 478.7294 | 129.5293 | 207.9099 | 139.659 | 68.1274 | 62.9562 | 68.469 | 53.0804 | 39.4998
447.6337 | 300.6337 | 478.7231 | 129.9155 | 208.452 | 140.0465 | 68.4303 | 63.2507 | 68.7387 | 53.2937 | 39.5454
448.6351 | 301.6351 | 478.8312 | 130.2487 | 208.9872 | 140.4227 | 68.7735 | 63.5423 | 69.0092 | 53.4673 | 39.6148
449.6265 | 302.6265 | 479.0456 | 130.606 | 209.54 | 140.8087 | 69.078 | 63.8387 | 69.2635 | 53.6672 | 39.6827
450.628 | 303.628 | 479.1467 | 130.9819 | 210.092 | 141.2079 | 69.3978 | 64.1192 | 69.5331 | 53.8516 | 39.7875
451.6294 | 304.6294 | 479.2785 | 131.3479 | 210.6312 | 141.5765 | 69.7155 | 64.415 | 69.7928 | 54.0362 | 39.8843
452.6309 | 305.6309 | 479.3821 | 131.7122 | 211.1635 | 141.967 | 70.0375 | 64.6968 | 70.0601 | 54.2245 | 39.9367
453.6323 | 306.6323 | 479.3509 | 132.0475 | 211.6985 | 142.3488 | 70.3633 | 64.9934 | 70.3254 | 54.4372 | 40.012
454.6337 | 307.6337 | 479.3385 | 132.4029 | 212.2434 | 142.7027 | 70.6914 | 65.2906 | 70.5925 | 54.6067 | 40.1076
455.6252 | 308.6252 | 479.4671 | 132.7523 | 212.8089 | 143.1346 | 71.0069 | 65.5918 | 70.8613 | 54.8215 | 40.1359
456.6266 | 309.6266 | 479.5619 | 133.1389 | 213.3212 | 143.4698 | 71.3374 | 65.877 | 71.1322 | 55.0049 | 40.2379
457.628 | 310.628 | 479.6179 | 133.4605 | 213.8771 | 143.8572 | 71.6607 | 66.1676 | 71.3953 | 55.203 | 40.3035
458.6295 | 311.6295 | 479.6862 | 133.8324 | 214.4103 | 144.2405 | 71.9909 | 66.463 | 71.6719 | 55.392 | 40.4051
459.6309 | 312.6309 | 479.6207 | 134.1806 | 214.964 | 144.6371 | 72.3139 | 66.764 | 71.9431 | 55.5592 | 40.4983
460.6324 | 313.6324 | 479.506 | 134.532 | 215.5226 | 145.0123 | 72.6425 | 67.0557 | 72.2082 | 55.7725 | 40.5574
461.6238 | 314.6238 | 479.5011 | 134.8893 | 216.0232 | 145.3952 | 72.9705 | 67.3425 | 72.4822 | 55.9623 | 40.6083
462.6252 | 315.6252 | 479.4494 | 135.2647 | 216.5422 | 145.7602 | 73.2971 | 67.6506 | 72.7601 | 56.1461 | 40.741
463.6267 | 316.6267 | 479.3102 | 135.5969 | 217.0882 | 146.1543 | 73.6258 | 67.9435 | 73.0301 | 56.3264 | 40.8181
464.6281 | 317.6281 | 479.1876 | 135.9436 | 217.6514 | 146.5209 | 73.9541 | 68.2519 | 73.3025 | 56.5344 | 40.8862
465.6295 | 318.6295 | 478.9459 | 136.312 | 218.2215 | 146.8766 | 74.2853 | 68.5459 | 73.5763 | 56.7412 | 40.9348
466.631 | 319.631 | 478.8043 | 136.6427 | 218.738 | 147.2636 | 74.6121 | 68.8452 | 73.8573 | 56.9334 | 41.0332
467.6324 | 320.6324 | 478.6916 | 137.0066 | 219.26 | 147.6266 | 74.948 | 69.1395 | 74.1274 | 57.1151 | 41.1283
468.6238 | 321.6238 | 478.6756 | 137.3553 | 219.7426 | 148.0022 | 75.2816 | 69.4334 | 74.3978 | 57.311 | 41.1911
469.6353 | 322.6353 | 478.6545 | 137.6945 | 220.2685 | 148.3655 | 75.6091 | 69.7281 | 74.6718 | 57.5057 | 41.2792
470.6267 | 323.6267 | 478.6372 | 138.0502 | 220.7865 | 148.7142 | 75.9513 | 70.0312 | 74.9507 | 57.6983 | 41.3744
471.6282 | 324.6282 | 478.5363 | 138.3605 | 221.3131 | 149.0963 | 76.2738 | 70.322 | 75.2297 | 57.9045 | 41.4207
472.6296 | 325.6296 | 478.3753 | 138.7214 | 221.8478 | 149.4345 | 76.6117 | 70.6291 | 75.5028 | 58.1016 | 41.5189
473.631 | 326.631 | 478.2402 | 139.075 | 222.3702 | 149.8061 | 76.9623 | 70.922 | 75.7708 | 58.3018 | 41.599
474.6325 | 327.6325 | 478.2363 | 139.386 | 222.8752 | 150.158 | 77.2969 | 71.2312 | 76.0491 | 58.4981 | 41.6952
475.6339 | 328.6339 | 478.1613 | 139.7528 | 223.4298 | 150.537 | 77.6235 | 71.5244 | 76.3232 | 58.7046 | 41.7761
476.6254 | 329.6254 | 478.1205 | 140.0836 | 223.9182 | 150.8948 | 77.9743 | 71.8352 | 76.598 | 58.906 | 41.8514
477.6268 | 330.6268 | 478.0785 | 140.4385 | 224.4507 | 151.2755 | 78.3132 | 72.1393 | 76.8748 | 59.1055 | 41.9475
478.6282 | 331.6282 | 478.1557 | 140.7768 | 224.962 | 151.6206 | 78.6534 | 72.439 | 77.1479 | 59.3293 | 42.0115
479.6297 | 332.6297 | 478.2175 | 141.1317 | 225.5026 | 151.9622 | 78.996 | 72.743 | 77.4214 | 59.5249 | 42.113
480.6311 | 333.6311 | 478.2173 | 141.4523 | 226.0161 | 152.3382 | 79.3353 | 73.0518 | 77.6949 | 59.7486 | 42.1815
481.6326 | 334.6326 | 478.2475 | 141.8035 | 226.5361 | 152.6907 | 79.6716 | 73.3558 | 77.9831 | 59.9457 | 42.2797
482.634 | 335.634 | 478.2905 | 142.1483 | 227.0589 | 153.0705 | 80.0212 | 73.6615 | 78.2446 | 60.1603 | 42.361
483.6254 | 336.6254 | 478.5279 | 142.495 | 227.566 | 153.4398 | 80.3585 | 73.9745 | 78.5217 | 60.3873 | 42.4454
484.6269 | 337.6269 | 478.7094 | 142.8453 | 228.0969 | 153.8097 | 80.7032 | 74.2721 | 78.798 | 60.6016 | 42.5167
485.6283 | 338.6283 | 478.6909 | 143.2095 | 228.6148 | 154.1849 | 81.0356 | 74.5772 | 79.0738 | 60.8371 | 42.5983
486.6297 | 339.6297 | 478.7402 | 143.5299 | 229.1467 | 154.5514 | 81.3831 | 74.8902 | 79.3424 | 61.043 | 42.6854
487.6312 | 340.6312 | 478.885 | 143.8838 | 229.6411 | 154.8877 | 81.736 | 75.2023 | 79.6149 | 61.269 | 42.7679
488.6326 | 341.6326 | 479.0348 | 144.2056 | 230.1505 | 155.2555 | 82.0817 | 75.5067 | 79.8848 | 61.4824 | 42.8792
489.624 | 342.624 | 479.1215 | 144.5784 | 230.6892 | 155.6202 | 82.4218 | 75.8144 | 80.1667 | 61.6946 | 42.9647
490.6355 | 343.6355 | 479.1029 | 144.9029 | 231.1869 | 155.9662 | 82.7737 | 76.1263 | 80.4276 | 61.9343 | 43.0321
491.6269 | 344.6269 | 479.1156 | 145.2241 | 231.705 | 156.3305 | 83.114 | 76.4366 | 80.7093 | 62.1589 | 43.1134
492.6284 | 345.6284 | 479.1313 | 145.5876 | 232.2243 | 156.687 | 83.4492 | 76.7452 | 80.9823 | 62.3793 | 43.209
493.6298 | 346.6298 | 479.1574 | 145.8802 | 232.7471 | 157.0591 | 83.7989 | 77.0545 | 81.2502 | 62.601 | 43.2858
494.6312 | 347.6312 | 479.349 | 146.2311 | 233.2208 | 157.4146 | 84.1523 | 77.3705 | 81.5246 | 62.8244 | 43.3775
495.6327 | 348.6327 | 479.5312 | 146.5775 | 233.7342 | 157.7079 | 84.4953 | 77.6851 | 81.799 | 63.0462 | 43.458
496.6341 | 349.6341 | 479.5344 | 146.9099 | 234.2501 | 158.072 | 84.861 | 77.9998 | 82.0719 | 63.2754 | 43.5396
497.6256 | 350.6256 | 479.5014 | 147.249 | 234.7602 | 158.4441 | 85.206 | 78.3139 | 82.3552 | 63.4945 | 43.6417
498.627 | 351.627 | 479.4241 | 147.5929 | 235.2931 | 158.799 | 85.5506 | 78.6199 | 82.6265 | 63.7312 | 43.7053
499.6284 | 352.6284 | 479.3204 | 147.9031 | 235.7732 | 159.1706 | 85.9001 | 78.9328 | 82.8967 | 63.9416 | 43.7954
500.6299 | 353.6299 | 479.183 | 148.2366 | 236.2789 | 159.5329 | 86.2592 | 79.2505 | 83.1732 | 64.1683 | 43.8864
501.6313 | 354.6313 | 479.0233 | 148.6159 | 236.7793 | 159.8944 | 86.6019 | 79.5645 | 83.4421 | 64.4071 | 43.9615
502.6328 | 355.6328 | 478.8883 | 148.9201 | 237.307 | 160.2525 | 86.9691 | 79.8801 | 83.723 | 64.6273 | 44.0448
503.6342 | 356.6342 | 478.8637 | 149.2549 | 237.782 | 160.6276 | 87.3269 | 80.1935 | 83.9946 | 64.8513 | 44.1263
504.6256 | 357.6256 | 478.8047 | 149.5579 | 238.2851 | 160.9657 | 87.6758 | 80.5125 | 84.2696 | 65.0723 | 44.2411
505.6271 | 358.6271 | 478.704 | 149.8981 | 238.7747 | 161.2897 | 88.019 | 80.8222 | 84.5437 | 65.3068 | 44.307
506.6285 | 359.6285 | 478.6114 | 150.2518 | 239.2911 | 161.6464 | 88.377 | 81.1494 | 84.8241 | 65.5229 | 44.4219
507.6299 | 360.6299 | 478.7394 | 150.5538 | 239.7808 | 162.0031 | 88.734 | 81.4706 | 85.0958 | 65.7619 | 44.4864
508.6314 | 361.6314 | 478.7618 | 150.8834 | 240.2911 | 162.354 | 89.0916 | 81.7914 | 85.3697 | 65.978 | 44.5948
509.6328 | 362.6328 | 478.7551 | 151.2117 | 240.7831 | 162.7026 | 89.442 | 82.1185 | 85.6454 | 66.2164 | 44.6648
510.6343 | 363.6343 | 478.8068 | 151.5404 | 241.2957 | 163.071 | 89.8003 | 82.4367 | 85.9279 | 66.4508 | 44.775
511.6257 | 364.6257 | 478.8763 | 151.9013 | 241.7754 | 163.4152 | 90.1665 | 82.7626 | 86.1973 | 66.6811 | 44.8641
512.6271 | 365.6271 | 478.9258 | 152.2186 | 242.2706 | 163.7769 | 90.5149 | 83.0932 | 86.4795 | 66.9039 | 44.9688
513.6286 | 366.6286 | 478.9299 | 152.5405 | 242.7812 | 164.1166 | 90.8754 | 83.4152 | 86.7556 | 67.1435 | 45.0412
514.63 | 367.63 | 478.9101 | 152.8375 | 243.2754 | 164.4766 | 91.2369 | 83.737 | 87.0352 | 67.3767 | 45.14
515.6314 | 368.6314 | 478.8862 | 153.1818 | 243.7551 | 164.8333 | 91.5934 | 84.0609 | 87.3196 | 67.6009 | 45.2351
516.6329 | 369.6329 | 478.8227 | 153.4928 | 244.2552 | 165.1822 | 91.9543 | 84.3919 | 87.5935 | 67.8401 | 45.324
517.6343 | 370.6343 | 478.7887 | 153.8335 | 244.7369 | 165.5347 | 92.3197 | 84.7159 | 87.8689 | 68.0708 | 45.4565
518.6658 | 371.6658 | 478.8286 | 154.1746 | 245.2432 | 165.8721 | 92.6967 | 85.0602 | 88.1595 | 68.3268 | 45.5373
519.6272 | 372.6272 | 478.8542 | 154.4746 | 245.7389 | 166.2177 | 93.0572 | 85.368 | 88.4304 | 68.5559 | 45.6427
520.6286 | 373.6286 | 478.8113 | 154.798 | 246.2198 | 166.5413 | 93.4163 | 85.701 | 88.7017 | 68.7777 | 45.7768
521.6301 | 374.6301 | 478.8837 | 155.1542 | 246.6989 | 166.8991 | 93.774 | 86.0354 | 88.9787 | 69.0223 | 45.8703
522.6315 | 375.6315 | 478.9775 | 155.4979 | 247.192 | 167.2193 | 94.1458 | 86.3633 | 89.2623 | 69.2552 | 45.9947
523.6329 | 376.6329 | 478.8921 | 155.8097 | 247.686 | 167.5599 | 94.5186 | 86.7042 | 89.5452 | 69.4866 | 46.1334
524.6244 | 377.6244 | 478.8744 | 156.1286 | 248.1289 | 167.884 | 94.8779 | 87.0339 | 89.8202 | 69.7358 | 46.2403
525.6258 | 378.6258 | 478.9738 | 156.4505 | 248.6085 | 168.2271 | 95.2557 | 87.3683 | 90.0991 | 69.9688 | 46.364
526.6273 | 379.6273 | 479.1113 | 156.7503 | 249.1058 | 168.5572 | 95.6181 | 87.7056 | 90.3776 | 70.21 | 46.4858
527.6287 | 380.6287 | 479.2905 | 157.0595 | 249.5512 | 168.8919 | 95.9614 | 88.0413 | 90.6516 | 70.444 | 46.6079
528.6301 | 381.6301 | 479.2934 | 157.3876 | 250.0203 | 169.219 | 96.3396 | 88.3707 | 90.9345 | 70.6762 | 46.7706
529.6316 | 382.6316 | 479.2466 | 157.6835 | 250.5269 | 169.5511 | 96.7296 | 88.7065 | 91.2075 | 70.922 | 46.8907
530.633 | 383.633 | 479.0643 | 158.0013 | 251.0007 | 169.8517 | 97.094 | 89.0487 | 91.4948 | 71.1681 | 47.0214
531.6244 | 384.6244 | 479.0393 | 158.3315 | 251.458 | 170.2123 | 97.4537 | 89.3782 | 91.7784 | 71.4061 | 47.1843
532.6359 | 385.6359 | 478.893 | 158.6417 | 251.9418 | 170.5689 | 97.8435 | 89.717 | 92.0661 | 71.6544 | 47.2968
533.6273 | 386.6273 | 478.8315 | 158.9597 | 252.398 | 170.9194 | 98.1961 | 90.0448 | 92.3492 | 71.9042 | 47.4364
534.6288 | 387.6288 | 478.8482 | 159.2597 | 252.8557 | 171.2152 | 98.5691 | 90.3875 | 92.6211 | 72.1318 | 47.6139
535.6302 | 388.6302 | 478.9651 | 159.5926 | 253.3107 | 171.5699 | 98.9296 | 90.7263 | 92.9066 | 72.3774 | 47.7525
536.6316 | 389.6316 | 478.8642 | 159.915 | 253.7888 | 171.8999 | 99.3086 | 91.0644 | 93.187 | 72.6255 | 47.8992
537.6331 | 390.6331 | 478.8186 | 160.2399 | 254.2611 | 172.237 | 99.6722 | 91.3975 | 93.4712 | 72.8827 | 48.0454
538.6345 | 391.6345 | 478.7939 | 160.5373 | 254.7111 | 172.5667 | 100.0394 | 91.7426 | 93.7569 | 73.1169 | 48.2095
539.6259 | 392.6259 | 478.7501 | 160.8302 | 255.1792 | 172.8806 | 100.421 | 92.0754 | 94.0361 | 73.3633 | 48.3628
540.6274 | 393.6274 | 478.6111 | 161.1789 | 255.6328 | 173.2362 | 100.7913 | 92.4177 | 94.3195 | 73.6338 | 48.4787
541.6288 | 394.6288 | 478.5544 | 161.4463 | 256.099 | 173.5864 | 101.1567 | 92.7523 | 94.5987 | 73.879 | 48.6768
542.6303 | 395.6303 | 478.5906 | 161.7572 | 256.5668 | 173.8911 | 101.5362 | 93.0999 | 94.8876 | 74.1275 | 48.8147
543.6317 | 396.6317 | 478.534 | 162.0832 | 257.0256 | 174.2333 | 101.9229 | 93.442 | 95.1671 | 74.3667 | 48.9915
544.6331 | 397.6331 | 478.4887 | 162.4064 | 257.5015 | 174.5481 | 102.2909 | 93.7877 | 95.4516 | 74.6208 | 49.1492
545.6246 | 398.6246 | 478.5208 | 162.6953 | 257.9418 | 174.8808 | 102.6725 | 94.1262 | 95.7379 | 74.8692 | 49.3144
546.626 | 399.626 | 478.4493 | 163.0186 | 258.4086 | 175.1954 | 103.0417 | 94.4728 | 96.0251 | 75.125 | 49.4722
547.6274 | 400.6274 | 478.4365 | 163.2948 | 258.847 | 175.5544 | 103.421 | 94.8094 | 96.3012 | 75.3822 | 49.6203
548.6289 | 401.6289 | 478.412 | 163.6194 | 259.3213 | 175.8675 | 103.7977 | 95.1539 | 96.5935 | 75.6352 | 49.785
549.6303 | 402.6303 | 478.4223 | 163.9314 | 259.7574 | 176.1881 | 104.1919 | 95.4965 | 96.8832 | 75.8775 | 49.9502
550.6318 | 403.6318 | 478.4686 | 164.2323 | 260.1964 | 176.486 | 104.5593 | 95.839 | 97.1664 | 76.1301 | 50.107
551.6332 | 404.6332 | 478.4279 | 164.5261 | 260.673 | 176.798 | 104.9381 | 96.1775 | 97.4524 | 76.3953 | 50.2578
552.6246 | 405.6246 | 478.4113 | 164.8106 | 261.1015 | 177.1269 | 105.3185 | 96.5382 | 97.735 | 76.6448 | 50.433
553.6261 | 406.6261 | 478.588 | 165.1495 | 261.5625 | 177.4692 | 105.7008 | 96.8723 | 98.0216 | 76.9114 | 50.5955
554.6275 | 407.6275 | 478.5404 | 165.4249 | 262.0128 | 177.7735 | 106.0702 | 97.2216 | 98.3069 | 77.16 | 50.7448
555.629 | 408.629 | 478.638 | 165.7213 | 262.4581 | 178.0993 | 106.4582 | 97.5667 | 98.5906 | 77.4287 | 50.9049
556.6304 | 409.6304 | 478.7827 | 166.0362 | 262.9288 | 178.4077 | 106.8434 | 97.9138 | 98.8732 | 77.6941 | 51.074
557.6318 | 410.6318 | 478.7512 | 166.348 | 263.3751 | 178.7002 | 107.2148 | 98.2602 | 99.1612 | 77.9542 | 51.2207
558.6333 | 411.6333 | 478.7284 | 166.6557 | 263.8067 | 179.0329 | 107.5874 | 98.5987 | 99.4465 | 78.2004 | 51.4194
559.6347 | 412.6347 | 478.6971 | 166.9363 | 264.2484 | 179.3335 | 107.9693 | 98.9508 | 99.73 | 78.4664 | 51.5843
560.6261 | 413.6261 | 478.8044 | 167.2232 | 264.6887 | 179.6568 | 108.3384 | 99.2825 | 100.012 | 78.739 | 51.7379
561.6276 | 414.6276 | 478.7934 | 167.5367 | 265.1275 | 179.9614 | 108.7156 | 99.6296 | 100.3082 | 79.0087 | 51.8922
562.629 | 415.629 | 478.8558 | 167.8279 | 265.5657 | 180.2886 | 109.0985 | 99.9717 | 100.5924 | 79.2648 | 52.0737
563.6305 | 416.6305 | 478.7375 | 168.138 | 266.0165 | 180.6117 | 109.4706 | 100.3179 | 100.8699 | 79.5202 | 52.2331
564.6319 | 417.6319 | 478.738 | 168.4294 | 266.484 | 180.924 | 109.8392 | 100.6673 | 101.1628 | 79.7818 | 52.3966
565.6333 | 418.6333 | 478.872 | 168.755 | 266.9283 | 181.2249 | 110.2305 | 101.0135 | 101.4545 | 80.0658 | 52.5469
566.6248 | 419.6248 | 479.0479 | 169.0328 | 267.3568 | 181.5235 | 110.5965 | 101.3648 | 101.7382 | 80.3131 | 52.723
567.6262 | 420.6262 | 479.1056 | 169.3407 | 267.7997 | 181.8623 | 110.9648 | 101.7143 | 102.0273 | 80.5778 | 52.9013
568.6276 | 421.6276 | 479.154 | 169.6149 | 268.2282 | 182.1668 | 111.365 | 102.0604 | 102.3131 | 80.8654 | 53.0432
569.6291 | 422.6291 | 479.1691 | 169.9074 | 268.655 | 182.482 | 111.7352 | 102.4003 | 102.5968 | 81.1242 | 53.2135
570.6305 | 423.6305 | 479.2097 | 170.1935 | 269.0984 | 182.7923 | 112.1065 | 102.7446 | 102.8891 | 81.3845 | 53.3732
571.632 | 424.632 | 479.3428 | 170.5074 | 269.5615 | 183.1017 | 112.4828 | 103.0888 | 103.1712 | 81.6609 | 53.5365
572.6334 | 425.6334 | 479.4001 | 170.7823 | 269.9875 | 183.3999 | 112.8651 | 103.4465 | 103.4511 | 81.9296 | 53.7109
573.6248 | 426.6248 | 479.4759 | 171.096 | 270.4216 | 183.7037 | 113.2479 | 103.7925 | 103.7395 | 82.1761 | 53.9037
574.6263 | 427.6263 | 479.5126 | 171.3846 | 270.8652 | 183.9615 | 113.6346 | 104.1442 | 104.0253 | 82.458 | 54.0533
575.6277 | 428.6277 | 479.5415 | 171.693 | 271.2809 | 184.3071 | 114.0126 | 104.4807 | 104.3179 | 82.7411 | 54.2111
576.6292 | 429.6292 | 479.647 | 171.9854 | 271.7264 | 184.6236 | 114.3958 | 104.8291 | 104.5964 | 83.0063 | 54.3639
577.6306 | 430.6306 | 479.7875 | 172.2733 | 272.1984 | 184.9296 | 114.7704 | 105.1805 | 104.8742 | 83.2792 | 54.5511
578.632 | 431.632 | 479.8199 | 172.5657 | 272.6288 | 185.2321 | 115.1441 | 105.5249 | 105.1675 | 83.5611 | 54.7026
579.6335 | 432.6335 | 479.8777 | 172.847 | 273.0224 | 185.5331 | 115.5294 | 105.8811 | 105.448 | 83.8247 | 54.8747
580.6349 | 433.6349 | 479.9563 | 173.1294 | 273.4771 | 185.8565 | 115.9012 | 106.218 | 105.7322 | 84.0963 | 55.037
581.6263 | 434.6263 | 479.9467 | 173.4725 | 273.8984 | 186.1855 | 116.2953 | 106.5714 | 106.0198 | 84.3644 | 55.2018
582.6278 | 435.6278 | 480.0498 | 173.7271 | 274.3075 | 186.4809 | 116.6592 | 106.9069 | 106.3177 | 84.6546 | 55.3629
583.6292 | 436.6292 | 480.0716 | 174.0117 | 274.7155 | 186.7957 | 117.0569 | 107.2712 | 106.6008 | 84.9123 | 55.5556
584.6307 | 437.6307 | 480.023 | 174.3007 | 275.1429 | 187.0965 | 117.4058 | 107.6032 | 106.8954 | 85.1916 | 55.7101
585.6321 | 438.6321 | 479.8687 | 174.6017 | 275.6106 | 187.4143 | 117.8022 | 107.9599 | 107.1791 | 85.4687 | 55.8506
586.6335 | 439.6335 | 479.6697 | 174.8663 | 276.0298 | 187.7088 | 118.1726 | 108.2908 | 107.4672 | 85.7526 | 56.0371
587.625 | 440.625 | 479.5856 | 175.138 | 276.4459 | 188.0242 | 118.5529 | 108.6416 | 107.7565 | 86.0328 | 56.1811
588.6264 | 441.6264 | 479.6425 | 175.4364 | 276.8936 | 188.3131 | 118.9216 | 108.9862 | 108.0509 | 86.3079 | 56.3655
589.6278 | 442.6278 | 479.6066 | 175.7414 | 277.3034 | 188.6907 | 119.3037 | 109.3284 | 108.3462 | 86.5859 | 56.5259
590.6293 | 443.6293 | 479.5487 | 176.0392 | 277.6679 | 188.9442 | 119.6862 | 109.6786 | 108.6352 | 86.8694 | 56.7008
591.6307 | 444.6307 | 479.5977 | 176.3126 | 278.097 | 189.2454 | 120.0662 | 110.0131 | 108.9237 | 87.1342 | 56.8863
592.6322 | 445.6322 | 479.5781 | 176.596 | 278.5552 | 189.5317 | 120.4401 | 110.3668 | 109.2046 | 87.4188 | 57.0537
593.6236 | 446.6236 | 479.5759 | 176.8619 | 278.9231 | 189.866 | 120.8151 | 110.7106 | 109.5028 | 87.6952 | 57.2156
594.625 | 447.625 | 479.5166 | 177.1586 | 279.2986 | 190.1687 | 121.1968 | 111.0551 | 109.7905 | 87.9713 | 57.3822
595.6265 | 448.6265 | 479.481 | 177.4499 | 279.7354 | 190.4485 | 121.5721 | 111.394 | 110.0866 | 88.275 | 57.5253
596.6279 | 449.6279 | 479.4344 | 177.7137 | 280.1628 | 190.7528 | 121.9502 | 111.7463 | 110.3774 | 88.5502 | 57.7094
597.6293 | 450.6293 | 479.3533 | 177.9913 | 280.5854 | 191.0751 | 122.3273 | 112.0855 | 110.6715 | 88.8377 | 57.8682
598.6308 | 451.6308 | 479.408 | 178.2634 | 281.0124 | 191.3675 | 122.7042 | 112.4283 | 110.9663 | 89.1061 | 58.0464
599.6322 | 452.6322 | 479.4728 | 178.5556 | 281.4092 | 191.6562 | 123.0804 | 112.7735 | 111.256 | 89.3854 | 58.2319
600.6337 | 453.6337 | 479.5411 | 178.8228 | 281.7943 | 191.9651 | 123.4596 | 113.1166 | 111.5442 | 89.6844 | 58.3898
601.6351 | 454.6351 | 479.5266 | 179.0967 | 282.249 | 192.2802 | 123.8328 | 113.4713 | 111.8336 | 89.9593 | 58.5556
602.6265 | 455.6265 | 479.4074 | 179.3676 | 282.6485 | 192.5879 | 124.1998 | 113.8106 | 112.1203 | 90.2465 | 58.7263
603.628 | 456.628 | 479.2994 | 179.6447 | 283.0217 | 192.882 | 124.5875 | 114.1562 | 112.4097 | 90.5321 | 58.8984
604.6294 | 457.6294 | 479.2002 | 179.9365 | 283.4315 | 193.167 | 124.9539 | 114.4988 | 112.7056 | 90.8084 | 59.0801
605.6309 | 458.6309 | 479.043 | 180.2245 | 283.8379 | 193.4639 | 125.3269 | 114.8461 | 112.9921 | 91.0976 | 59.252
606.6323 | 459.6323 | 478.911 | 180.484 | 284.2394 | 193.7793 | 125.7119 | 115.1883 | 113.2816 | 91.3935 | 59.4209
607.6337 | 460.6337 | 478.6872 | 180.7782 | 284.6703 | 194.084 | 126.0692 | 115.5481 | 113.5723 | 91.6637 | 59.6317
608.6252 | 461.6252 | 478.6567 | 181.0453 | 285.0327 | 194.4077 | 126.4582 | 115.8931 | 113.8567 | 91.9604 | 59.7915
609.6266 | 462.6266 | 478.6056 | 181.3091 | 285.4167 | 194.7033 | 126.8207 | 116.2525 | 114.1448 | 92.2458 | 59.9615
610.628 | 463.628 | 478.5401 | 181.6063 | 285.8229 | 194.9866 | 127.1949 | 116.623 | 114.4384 | 92.5221 | 60.1519
611.6295 | 464.6295 | 478.6327 | 181.8705 | 286.2162 | 195.2859 | 127.5662 | 116.9829 | 114.7258 | 92.8146 | 60.3298
612.6309 | 465.6309 | 478.7072 | 182.1377 | 286.6173 | 195.5812 | 127.9483 | 117.3425 | 115.0096 | 93.1168 | 60.4733
613.6324 | 466.6324 | 478.6506 | 182.4122 | 287.0139 | 195.8783 | 128.3172 | 117.693 | 115.2931 | 93.3979 | 60.6639
614.6238 | 467.6238 | 478.6189 | 182.6579 | 287.3946 | 196.1621 | 128.6681 | 118.0434 | 115.5844 | 93.6601 | 60.8604
615.6252 | 468.6252 | 478.5938 | 182.9598 | 287.7882 | 196.4251 | 129.0567 | 118.3945 | 115.8766 | 93.9763 | 61.0316
616.6267 | 469.6267 | 478.4437 | 183.2364 | 288.1779 | 196.752 | 129.4142 | 118.7515 | 116.1521 | 94.2576 | 61.2065
617.6281 | 470.6281 | 478.2502 | 183.4993 | 288.5728 | 197.0754 | 129.7832 | 119.0968 | 116.4345 | 94.5578 | 61.3771
618.6295 | 471.6295 | 478.1722 | 183.7291 | 288.9533 | 197.3352 | 130.1368 | 119.4464 | 116.7173 | 94.8506 | 61.5348
619.631 | 472.631 | 478.0687 | 183.9694 | 289.3086 | 197.6543 | 130.4945 | 119.797 | 116.9873 | 95.1462 | 61.7275
620.6324 | 473.6324 | 477.953 | 184.2939 | 289.6809 | 197.9474 | 130.8659 | 120.1376 | 117.2801 | 95.4324 | 61.9176
621.6339 | 474.6339 | 477.8733 | 184.5727 | 290.126 | 198.2018 | 131.2226 | 120.4906 | 117.5528 | 95.7275 | 62.0688
622.6253 | 475.6253 | 477.842 | 184.8185 | 290.4766 | 198.5097 | 131.5653 | 120.8351 | 117.8232 | 96.0228 | 62.2684
623.6267 | 476.6267 | 477.7875 | 185.0794 | 290.8646 | 198.7862 | 131.9224 | 121.178 | 118.0908 | 96.3237 | 62.4517
624.6282 | 477.6282 | 477.7426 | 185.3747 | 291.2477 | 199.0661 | 132.2899 | 121.5253 | 118.3667 | 96.6146 | 62.632
625.6296 | 478.6296 | 477.7527 | 185.6595 | 291.6322 | 199.3839 | 132.6367 | 121.8634 | 118.6332 | 96.9018 | 62.8268
626.6311 | 479.6311 | 477.7783 | 185.8951 | 291.9685 | 199.6579 | 132.9719 | 122.2027 | 118.9 | 97.2054 | 63.0176
627.6325 | 480.6325 | 477.8689 | 186.1594 | 292.3682 | 199.9876 | 133.3249 | 122.5486 | 119.1737 | 97.5035 | 63.1924
628.6339 | 481.6339 | 477.8831 | 186.4504 | 292.7351 | 200.2946 | 133.6763 | 122.8855 | 119.4291 | 97.7966 | 63.3835
629.6254 | 482.6254 | 477.8029 | 186.7287 | 293.1117 | 200.5512 | 134.0112 | 123.2275 | 119.6981 | 98.0951 | 63.5671
630.6268 | 483.6268 | 477.7269 | 186.9846 | 293.4959 | 200.8641 | 134.3437 | 123.5655 | 119.9622 | 98.3945 | 63.7568
631.6282 | 484.6282 | 477.7143 | 187.2642 | 293.8808 | 201.1775 | 134.6859 | 123.8876 | 120.2281 | 98.6852 | 63.9304
632.6297 | 485.6297 | 477.7335 | 187.522 | 294.2531 | 201.5147 | 135.0382 | 124.2315 | 120.4884 | 98.9888 | 64.1182
633.6311 | 486.6311 | 477.6774 | 187.785 | 294.6378 | 201.8144 | 135.3736 | 124.5588 | 120.7509 | 99.2831 | 64.3119
634.6326 | 487.6326 | 477.8984 | 188.0783 | 295.028 | 202.148 | 135.6995 | 124.9015 | 121.0144 | 99.5792 | 64.5036
635.624 | 488.624 | 478.0154 | 188.357 | 295.3682 | 202.4624 | 136.037 | 125.2398 | 121.2773 | 99.8814 | 64.6898
636.6254 | 489.6254 | 478.1625 | 188.616 | 295.7455 | 202.7776 | 136.3793 | 125.57 | 121.5299 | 100.1881 | 64.8533
637.6269 | 490.6269 | 478.1924 | 188.8776 | 296.1189 | 203.0537 | 136.7067 | 125.8992 | 121.7986 | 100.4562 | 65.0669
638.6283 | 491.6283 | 478.331 | 189.1298 | 296.5063 | 203.373 | 137.0351 | 126.228 | 122.054 | 100.7701 | 65.2598
639.6297 | 492.6297 | 478.5409 | 189.4009 | 296.8385 | 203.686 | 137.3805 | 126.5622 | 122.3148 | 101.0896 | 65.4303
640.6312 | 493.6312 | 478.6309 | 189.6825 | 297.2395 | 203.9848 | 137.7038 | 126.8852 | 122.5742 | 101.3865 | 65.6317
641.6326 | 494.6326 | 478.8177 | 189.9546 | 297.6164 | 204.2916 | 138.0426 | 127.2209 | 122.8355 | 101.6711 | 65.8495
642.6341 | 495.6341 | 478.9892 | 190.2206 | 297.9963 | 204.5879 | 138.3621 | 127.5475 | 123.104 | 101.9851 | 66.0113
643.6355 | 496.6355 | 479.0289 | 190.4921 | 298.3653 | 204.914 | 138.6931 | 127.8824 | 123.3682 | 102.2812 | 66.2232
644.6269 | 497.6269 | 479.205 | 190.7724 | 298.7059 | 205.217 | 139.0166 | 128.2122 | 123.6242 | 102.5806 | 66.4043
645.6284 | 498.6284 | 479.3114 | 191.0515 | 299.0671 | 205.5455 | 139.3488 | 128.5385 | 123.8905 | 102.8795 | 66.5968
646.6298 | 499.6298 | 479.2688 | 191.3242 | 299.4433 | 205.8428 | 139.6491 | 128.8682 | 124.1553 | 103.1857 | 66.7888
647.6312 | 500.6312 | 479.347 | 191.5869 | 299.8066 | 206.1319 | 139.9982 | 129.2017 | 124.4187 | 103.4861 | 66.9777
648.6327 | 501.6327 | 479.3441 | 191.8809 | 300.2059 | 206.4493 | 140.3135 | 129.5334 | 124.6814 | 103.7765 | 67.1915
649.6341 | 502.6341 | 479.2591 | 192.1399 | 300.5651 | 206.7407 | 140.6313 | 129.8578 | 124.9556 | 104.0805 | 67.3721
650.6256 | 503.6256 | 479.1239 | 192.4117 | 300.9278 | 207.0444 | 140.9561 | 130.1892 | 125.2295 | 104.3873 | 67.5557
651.627 | 504.627 | 478.9882 | 192.6925 | 301.2482 | 207.3489 | 141.2745 | 130.5164 | 125.4954 | 104.6805 | 67.7478
652.6284 | 505.6284 | 478.8568 | 193.0035 | 301.6169 | 207.6651 | 141.6199 | 130.8429 | 125.7688 | 104.9735 | 67.9628
653.6299 | 506.6299 | 478.8062 | 193.2449 | 301.9492 | 207.9413 | 141.9205 | 131.1679 | 126.0348 | 105.2875 | 68.1609
654.6313 | 507.6313 | 478.6748 | 193.4815 | 302.3485 | 208.231 | 142.2785 | 131.499 | 126.3098 | 105.5951 | 68.3312
655.6328 | 508.6328 | 478.4807 | 193.7607 | 302.6661 | 208.5289 | 142.5975 | 131.8186 | 126.5734 | 105.8857 | 68.5435
656.6342 | 509.6342 | 478.3924 | 194.0196 | 302.9759 | 208.8211 | 142.9427 | 132.1511 | 126.8525 | 106.1984 | 68.7118
657.6256 | 510.6256 | 478.2845 | 194.2817 | 303.3625 | 209.1426 | 143.2796 | 132.4833 | 127.1174 | 106.4828 | 68.9315
658.6271 | 511.6271 | 478.212 | 194.539 | 303.7034 | 209.4472 | 143.6002 | 132.8165 | 127.3911 | 106.7872 | 69.118
659.6285 | 512.6285 | 478.2579 | 194.8001 | 304.0607 | 209.7218 | 143.9315 | 133.1521 | 127.6613 | 107.1016 | 69.3185
660.6299 | 513.6299 | 478.4114 | 195.0633 | 304.36 | 210.0277 | 144.278 | 133.4896 | 127.9324 | 107.3866 | 69.5201
661.6314 | 514.6314 | 478.5609 | 195.3684 | 304.7294 | 210.3335 | 144.6083 | 133.8231 | 128.2133 | 107.6902 | 69.7275
662.6328 | 515.6328 | 478.6083 | 195.6451 | 305.0533 | 210.6145 | 144.9462 | 134.1611 | 128.4846 | 108.0044 | 69.9051
663.6343 | 516.6343 | 478.475 | 195.9046 | 305.3825 | 210.903 | 145.2982 | 134.5081 | 128.7701 | 108.304 | 70.0885
664.6657 | 517.6657 | 478.3445 | 196.1631 | 305.7656 | 211.2158 | 145.638 | 134.8577 | 129.0614 | 108.6029 | 70.3126
665.6271 | 518.6271 | 478.2931 | 196.4405 | 306.0497 | 211.4901 | 145.9556 | 135.1872 | 129.3284 | 108.8974 | 70.4916
666.6286 | 519.6286 | 478.148 | 196.6835 | 306.3859 | 211.7747 | 146.2961 | 135.5323 | 129.6084 | 109.1985 | 70.6804
667.63 | 520.63 | 478.0615 | 196.9712 | 306.7478 | 212.0599 | 146.6372 | 135.8678 | 129.8893 | 109.499 | 70.8899
668.6314 | 521.6314 | 477.8638 | 197.2307 | 307.0666 | 212.3454 | 146.9847 | 136.219 | 130.1781 | 109.7934 | 71.0889
669.6329 | 522.6329 | 477.7255 | 197.5156 | 307.402 | 212.6429 | 147.3194 | 136.5696 | 130.4654 | 110.1074 | 71.2664
670.6243 | 523.6243 | 477.7224 | 197.7732 | 307.7208 | 212.9426 | 147.6724 | 136.9185 | 130.7549 | 110.4021 | 71.4584
671.6258 | 524.6258 | 477.6359 | 198.0341 | 308.0864 | 213.2454 | 148.0164 | 137.2583 | 131.042 | 110.7054 | 71.6574
672.6272 | 525.6272 | 477.5888 | 198.3128 | 308.4075 | 213.5154 | 148.3597 | 137.614 | 131.34 | 111.0163 | 71.8046
673.6286 | 526.6286 | 477.495 | 198.5723 | 308.7216 | 213.8175 | 148.7037 | 137.9582 | 131.6382 | 111.2988 | 72.0536
674.6301 | 527.6301 | 477.3508 | 198.8206 | 309.0751 | 214.0938 | 149.0696 | 138.3182 | 131.9303 | 111.6241 | 72.209
675.6315 | 528.6315 | 477.2187 | 199.0748 | 309.4244 | 214.3664 | 149.4227 | 138.6852 | 132.2291 | 111.9187 | 72.4401
676.633 | 529.633 | 477.1874 | 199.3363 | 309.7754 | 214.6542 | 149.7758 | 139.0308 | 132.5212 | 112.2115 | 72.6119
677.6344 | 530.6344 | 477.2254 | 199.6183 | 310.0754 | 214.941 | 150.1421 | 139.3897 | 132.8246 | 112.5089 | 72.8148
678.6258 | 531.6258 | 477.2757 | 199.8831 | 310.3747 | 215.2314 | 150.5021 | 139.7473 | 133.1252 | 112.8037 | 72.9998
679.6273 | 532.6273 | 477.421 | 200.1722 | 310.6958 | 215.5365 | 150.8777 | 140.1203 | 133.4278 | 113.1145 | 73.2067
680.6287 | 533.6287 | 477.5205 | 200.4609 | 310.984 | 215.8389 | 151.2294 | 140.4649 | 133.7308 | 113.4065 | 73.3981
681.6301 | 534.6301 | 477.6225 | 200.7559 | 311.2957 | 216.0979 | 151.601 | 140.8407 | 134.0362 | 113.7059 | 73.5927
682.6316 | 535.6316 | 477.7536 | 200.984 | 311.684 | 216.3859 | 151.9644 | 141.2007 | 134.3491 | 114.0028 | 73.7869
683.633 | 536.633 | 477.8559 | 201.2605 | 311.971 | 216.6703 | 152.3482 | 141.5685 | 134.6496 | 114.3059 | 73.9606
684.6345 | 537.6345 | 477.8158 | 201.5387 | 312.3203 | 216.9885 | 152.7137 | 141.9406 | 134.9686 | 114.616 | 74.1504
685.6359 | 538.6359 | 477.8588 | 201.8117 | 312.6006 | 217.2905 | 153.0846 | 142.3091 | 135.2824 | 114.9068 | 74.3397
686.6273 | 539.6273 | 477.9753 | 202.0817 | 312.9489 | 217.5727 | 153.4599 | 142.6909 | 135.6028 | 115.2174 | 74.5246
687.6288 | 540.6288 | 478.1323 | 202.3482 | 313.2937 | 217.8546 | 153.8331 | 143.0626 | 135.9165 | 115.5051 | 74.7263
688.6302 | 541.6302 | 478.2492 | 202.6288 | 313.6145 | 218.178 | 154.2218 | 143.4427 | 136.2355 | 115.8201 | 74.9118
689.6316 | 542.6316 | 478.5161 | 202.8901 | 313.9144 | 218.4569 | 154.599 | 143.8071 | 136.5579 | 116.1072 | 75.1273
690.6331 | 543.6331 | 478.7499 | 203.162 | 314.283 | 218.7596 | 154.9701 | 144.2121 | 136.8792 | 116.3866 | 75.3117
691.6345 | 544.6345 | 478.8535 | 203.4405 | 314.626 | 219.0701 | 155.347 | 144.5823 | 137.198 | 116.715 | 75.4858
692.6259 | 545.6259 | 478.9877 | 203.7183 | 314.9374 | 219.3738 | 155.7211 | 144.9661 | 137.5225 | 117.0101 | 75.6888
693.6274 | 546.6274 | 479.137 | 203.9723 | 315.2589 | 219.6634 | 156.095 | 145.361 | 137.8518 | 117.3136 | 75.876
694.6288 | 547.6288 | 479.2895 | 204.2615 | 315.5677 | 219.9558 | 156.4739 | 145.739 | 138.1836 | 117.6034 | 76.0714
695.6303 | 548.6303 | 479.336 | 204.5489 | 315.8893 | 220.23 | 156.8507 | 146.1331 | 138.512 | 117.9074 | 76.2427
696.6317 | 549.6317 | 479.3535 | 204.8308 | 316.2183 | 220.5272 | 157.2234 | 146.5206 | 138.8432 | 118.2139 | 76.4332
697.6331 | 550.6331 | 479.3064 | 205.0963 | 316.5257 | 220.8041 | 157.6155 | 146.9179 | 139.1721 | 118.508 | 76.6233
698.6746 | 551.6746 | 479.1105 | 205.3363 | 316.8666 | 221.1146 | 157.992 | 147.3181 | 139.5327 | 118.8157 | 76.8617
699.626 | 552.626 | 479.0526 | 205.587 | 317.1546 | 221.3633 | 158.3812 | 147.7163 | 139.8306 | 119.1072 | 77.0263
700.6275 | 553.6275 | 478.9471 | 205.8842 | 317.4567 | 221.6696 | 158.7382 | 148.0969 | 140.1794 | 119.402 | 77.2021
701.6289 | 554.6289 | 478.8467 | 206.1502 | 317.7873 | 221.9665 | 159.1272 | 148.4985 | 140.5079 | 119.6989 | 77.4046
702.6303 | 555.6303 | 478.7787 | 206.4288 | 318.0885 | 222.268 | 159.4992 | 148.8772 | 140.8448 | 120.0125 | 77.5999
703.6318 | 556.6318 | 478.8314 | 206.7093 | 318.382 | 222.5516 | 159.8828 | 149.278 | 141.1856 | 120.3144 | 77.7735
704.6332 | 557.6332 | 478.9668 | 206.9499 | 318.718 | 222.8392 | 160.2509 | 149.6718 | 141.5261 | 120.603 | 77.9742
705.6347 | 558.6347 | 478.934 | 207.2382 | 319.0439 | 223.1284 | 160.6306 | 150.0749 | 141.8625 | 120.9073 | 78.1723
706.6261 | 559.6261 | 478.8938 | 207.4584 | 319.3626 | 223.4321 | 161.0155 | 150.4705 | 142.1958 | 121.2077 | 78.3304
707.6275 | 560.6275 | 478.8588 | 207.731 | 319.6368 | 223.7199 | 161.3844 | 150.8525 | 142.532 | 121.5139 | 78.5213
708.629 | 561.629 | 478.8225 | 207.9985 | 319.9542 | 224.013 | 161.7841 | 151.2643 | 142.8597 | 121.805 | 78.7338
709.6304 | 562.6304 | 478.7883 | 208.2719 | 320.2239 | 224.3028 | 162.1519 | 151.6524 | 143.193 | 122.1057 | 78.8964
710.6318 | 563.6318 | 478.7933 | 208.5551 | 320.52 | 224.5855 | 162.5428 | 152.0504 | 143.5208 | 122.4033 | 79.1088
711.6333 | 564.6333 | 478.6384 | 208.8144 | 320.8103 | 224.8629 | 162.9319 | 152.4522 | 143.8602 | 122.7014 | 79.2916
712.6347 | 565.6347 | 478.6533 | 209.055 | 321.087 | 225.1451 | 163.3255 | 152.8758 | 144.1808 | 122.9984 | 79.4743
713.6261 | 566.6261 | 478.7927 | 209.3274 | 321.4181 | 225.433 | 163.7066 | 153.2862 | 144.5157 | 123.2967 | 79.6806
714.6276 | 567.6276 | 478.7906 | 209.5918 | 321.6697 | 225.7157 | 164.1181 | 153.7056 | 144.841 | 123.5979 | 79.8411
715.629 | 568.629 | 478.7561 | 209.8558 | 322.0013 | 226.0091 | 164.5131 | 154.1257 | 145.1723 | 123.8964 | 80.0314
716.6305 | 569.6305 | 478.7518 | 210.1175 | 322.3226 | 226.3155 | 164.9065 | 154.5316 | 145.4923 | 124.1966 | 80.2294
717.6319 | 570.6319 | 478.8102 | 210.3709 | 322.6535 | 226.5902 | 165.2931 | 154.9415 | 145.8149 | 124.4839 | 80.4164
718.6233 | 571.6233 | 478.7622 | 210.6362 | 322.9424 | 226.8605 | 165.6954 | 155.3484 | 146.1399 | 124.7883 | 80.6132
719.6248 | 572.6248 | 478.6613 | 210.932 | 323.1459 | 227.1339 | 166.1057 | 155.7661 | 146.4643 | 125.098 | 80.7902
720.6262 | 573.6262 | 478.5342 | 211.149 | 323.4686 | 227.4093 | 166.4942 | 156.1769 | 146.7941 | 125.399 | 80.9617
721.6276 | 574.6276 | 478.5044 | 211.4135 | 323.7533 | 227.6777 | 166.8931 | 156.5972 | 147.1165 | 125.7035 | 81.1602
722.6291 | 575.6291 | 478.6057 | 211.6886 | 324.0922 | 227.9664 | 167.2814 | 157.0066 | 147.4354 | 126.0101 | 81.3451
723.6305 | 576.6305 | 478.4456 | 211.9328 | 324.3612 | 228.257 | 167.6734 | 157.4141 | 147.7621 | 126.3116 | 81.5119
724.632 | 577.632 | 478.365 | 212.2148 | 324.6093 | 228.5475 | 168.0681 | 157.8286 | 148.093 | 126.5937 | 81.7369
725.6334 | 578.6334 | 478.203 | 212.4654 | 324.8969 | 228.832 | 168.4783 | 158.2429 | 148.4156 | 126.9017 | 81.9164
726.6348 | 579.6348 | 478.0965 | 212.7182 | 325.161 | 229.1102 | 168.8962 | 158.6602 | 148.744 | 127.1997 | 82.1147
727.6263 | 580.6263 | 478.0146 | 212.9773 | 325.4703 | 229.3662 | 169.291 | 159.0747 | 149.0786 | 127.5034 | 82.297
728.6277 | 581.6277 | 478.0248 | 213.2531 | 325.7505 | 229.6519 | 169.6939 | 159.4897 | 149.4108 | 127.8146 | 82.4774
729.6292 | 582.6292 | 478.1102 | 213.5049 | 326.0128 | 229.9299 | 170.0851 | 159.897 | 149.7406 | 128.1088 | 82.657
730.6306 | 583.6306 | 478.1352 | 213.7411 | 326.2788 | 230.1822 | 170.4835 | 160.3065 | 150.0669 | 128.4172 | 82.8352
731.632 | 584.632 | 478.1388 | 214.0022 | 326.5902 | 230.4297 | 170.8762 | 160.7156 | 150.3944 | 128.72 | 83.0433
732.6335 | 585.6335 | 478.1305 | 214.2449 | 326.9198 | 230.6984 | 171.2805 | 161.1371 | 150.7229 | 129.0235 | 83.2323
733.6349 | 586.6349 | 478.0918 | 214.4967 | 327.1085 | 231.0021 | 171.666 | 161.5374 | 151.0548 | 129.3346 | 83.4184
734.6263 | 587.6263 | 478.0032 | 214.773 | 327.419 | 231.2644 | 172.0588 | 161.9507 | 151.3799 | 129.6625 | 83.5779
735.6278 | 588.6278 | 478.1269 | 215.0456 | 327.6964 | 231.546 | 172.4601 | 162.3626 | 151.7094 | 129.9457 | 83.7912
736.6292 | 589.6292 | 478.3338 | 215.2905 | 327.9132 | 231.8185 | 172.8565 | 162.7784 | 152.0344 | 130.2827 | 83.9425
737.6307 | 590.6307 | 478.4239 | 215.5361 | 328.191 | 232.0987 | 173.2649 | 163.1914 | 152.3612 | 130.56 | 84.1683
738.6321 | 591.6321 | 478.5832 | 215.7852 | 328.4271 | 232.4121 | 173.6522 | 163.5987 | 152.6907 | 130.8839 | 84.3468
739.6335 | 592.6335 | 478.6651 | 216.0585 | 328.7442 | 232.71 | 174.0623 | 164.0304 | 153.0205 | 131.1923 | 84.5419
740.625 | 593.625 | 478.5737 | 216.326 | 328.9615 | 232.9978 | 174.4609 | 164.4436 | 153.3555 | 131.5023 | 84.683
741.6264 | 594.6264 | 478.4538 | 216.5985 | 329.2927 | 233.2345 | 174.8534 | 164.8885 | 153.6833 | 131.8069 | 84.9041
742.6278 | 595.6278 | 478.3462 | 216.8267 | 329.5376 | 233.5246 | 175.2498 | 165.3173 | 154.0185 | 132.1128 | 85.0747
743.6293 | 596.6293 | 478.2716 | 217.0604 | 329.769 | 233.8097 | 175.6522 | 165.7701 | 154.3602 | 132.4058 | 85.2856
744.6307 | 597.6307 | 478.131 | 217.3213 | 330.0045 | 234.0716 | 176.0488 | 166.2078 | 154.6993 | 132.7091 | 85.4665
745.6322 | 598.6322 | 478.0287 | 217.5538 | 330.2817 | 234.3499 | 176.4505 | 166.6384 | 155.0375 | 133.0121 | 85.6601
746.6236 | 599.6236 | 477.9072 | 217.8122 | 330.5378 | 234.6208 | 176.8507 | 167.0667 | 155.3721 | 133.3271 | 85.8376
747.635 | 600.635 | 477.6566 | 218.065 | 330.808 | 234.8923 | 177.2664 | 167.5071 | 155.7117 | 133.6212 | 86.0227
748.6265 | 601.6265 | 477.4932 | 218.3142 | 331.0845 | 235.1673 | 177.6751 | 167.9373 | 156.0477 | 133.9377 | 86.1839
749.6279 | 602.6279 | 477.2765 | 218.5739 | 331.3361 | 235.4129 | 178.0825 | 168.3594 | 156.376 | 134.2215 | 86.3899
750.6294 | 603.6294 | 477.2143 | 218.8135 | 331.6598 | 235.6908 | 178.5016 | 168.7888 | 156.706 | 134.5303 | 86.5841
751.6308 | 604.6308 | 477.1264 | 219.0649 | 331.9416 | 235.9828 | 178.8958 | 169.2014 | 157.0298 | 134.815 | 86.7797
752.6322 | 605.6322 | 477.249 | 219.3064 | 332.2039 | 236.2642 | 179.3097 | 169.6157 | 157.3508 | 135.1418 | 86.9391
753.6337 | 606.6337 | 477.3502 | 219.5836 | 332.4361 | 236.5313 | 179.7037 | 170.0025 | 157.6754 | 135.4233 | 87.1485
754.6251 | 607.6251 | 477.3373 | 219.8136 | 332.6811 | 236.8005 | 180.1402 | 170.4185 | 157.9907 | 135.7225 | 87.3314
755.6265 | 608.6265 | 477.3286 | 220.0603 | 332.9979 | 237.0656 | 180.5345 | 170.8143 | 158.3194 | 136.0094 | 87.5186
756.628 | 609.628 | 477.3655 | 220.3119 | 333.2282 | 237.3406 | 180.9492 | 171.2157 | 158.6317 | 136.3201 | 87.6634
757.6294 | 610.6294 | 477.4307 | 220.5602 | 333.4687 | 237.6211 | 181.3589 | 171.6092 | 158.94 | 136.5986 | 87.8873
758.6309 | 611.6309 | 477.4385 | 220.8213 | 333.7724 | 237.8987 | 181.7585 | 172.0033 | 159.2382 | 136.8986 | 88.0704
759.6323 | 612.6323 | 477.4908 | 221.0643 | 334.0387 | 238.1782 | 182.1626 | 172.3938 | 159.5399 | 137.1938 | 88.2507
760.6237 | 613.6237 | 477.4334 | 221.3084 | 334.2907 | 238.4424 | 182.5902 | 172.7782 | 159.8481 | 137.4802 | 88.4297
761.6252 | 614.6252 | 477.501 | 221.5393 | 334.5238 | 238.7206 | 182.9871 | 173.1548 | 160.1449 | 137.7664 | 88.6329
762.6266 | 615.6266 | 477.6418 | 221.7824 | 334.7955 | 238.9903 | 183.3939 | 173.5302 | 160.4512 | 138.0695 | 88.7877
763.628 | 616.628 | 477.6725 | 222.0664 | 335.0305 | 239.2802 | 183.8354 | 173.9091 | 160.748 | 138.3507 | 88.9902
764.6295 | 617.6295 | 477.6747 | 222.3247 | 335.299 | 239.5216 | 184.2565 | 174.2694 | 161.0553 | 138.6304 | 89.1908
765.6309 | 618.6309 | 477.6866 | 222.5934 | 335.5005 | 239.8044 | 184.6809 | 174.6496 | 161.3553 | 138.9341 | 89.3601
766.6324 | 619.6324 | 477.8034 | 222.8166 | 335.7978 | 240.0543 | 185.0935 | 175.0085 | 161.6411 | 139.2281 | 89.5376
767.6238 | 620.6238 | 477.9166 | 223.0699 | 335.9761 | 240.3529 | 185.5185 | 175.3717 | 161.9381 | 139.5075 | 89.732
768.6352 | 621.6352 | 477.9863 | 223.3211 | 336.2361 | 240.6032 | 185.9337 | 175.743 | 162.2356 | 139.8107 | 89.8936
769.6267 | 622.6267 | 478.1452 | 223.5765 | 336.4967 | 240.9044 | 186.3394 | 176.1065 | 162.5339 | 140.0771 | 90.1138
770.6281 | 623.6281 | 478.3034 | 223.8173 | 336.7891 | 241.1829 | 186.7707 | 176.4805 | 162.8264 | 140.3708 | 90.2953
771.6295 | 624.6295 | 478.4306 | 224.0676 | 337.0175 | 241.4606 | 187.1769 | 176.8706 | 163.1167 | 140.6512 | 90.48
772.631 | 625.631 | 478.4953 | 224.312 | 337.2775 | 241.7329 | 187.5964 | 177.2728 | 163.3941 | 140.9334 | 90.6886
773.6324 | 626.6324 | 478.5974 | 224.5445 | 337.5108 | 241.996 | 188.0137 | 177.652 | 163.6843 | 141.2428 | 90.8428
774.6339 | 627.6339 | 478.7001 | 224.8027 | 337.8036 | 242.2614 | 188.4273 | 178.0476 | 163.9632 | 141.527 | 91.0099
775.6253 | 628.6253 | 478.7591 | 225.0503 | 338.0712 | 242.5168 | 188.841 | 178.4237 | 164.2434 | 141.8156 | 91.208
776.6267 | 629.6267 | 478.7725 | 225.3174 | 338.3347 | 242.8027 | 189.2603 | 178.794 | 164.5071 | 142.0829 | 91.4279
777.6282 | 630.6282 | 478.7245 | 225.5581 | 338.5351 | 243.0714 | 189.6882 | 179.1497 | 164.7842 | 142.3807 | 91.5903
778.6296 | 631.6296 | 478.6897 | 225.7963 | 338.7878 | 243.3135 | 190.1051 | 179.5091 | 165.0537 | 142.6526 | 91.7903
779.6311 | 632.6311 | 478.803 | 226.0507 | 339.0404 | 243.5981 | 190.5188 | 179.8724 | 165.3186 | 142.9294 | 91.9768
780.6325 | 633.6325 | 478.8636 | 226.3018 | 339.3003 | 243.8852 | 190.9311 | 180.2453 | 165.5809 | 143.2468 | 92.1461
781.6339 | 634.6339 | 478.8713 | 226.5416 | 339.4972 | 244.1417 | 191.3498 | 180.6187 | 165.8396 | 143.5332 | 92.3263
782.6254 | 635.6254 | 478.7648 | 226.787 | 339.7347 | 244.3843 | 191.7675 | 180.9918 | 166.0972 | 143.8051 | 92.519
783.6268 | 636.6268 | 478.7003 | 227.0512 | 339.9906 | 244.6486 | 192.1923 | 181.3828 | 166.3434 | 144.09 | 92.7209
784.6282 | 637.6282 | 478.5488 | 227.2981 | 340.2656 | 244.92 | 192.5923 | 181.7699 | 166.5926 | 144.3822 | 92.8938
785.6297 | 638.6297 | 478.4707 | 227.5352 | 340.5139 | 245.18 | 193.0249 | 182.1664 | 166.831 | 144.6643 | 93.0615
786.6311 | 639.6311 | 478.3603 | 227.7862 | 340.6882 | 245.4372 | 193.4461 | 182.5517 | 167.0742 | 144.9472 | 93.2676
787.6326 | 640.6326 | 478.1831 | 227.9982 | 340.9547 | 245.6857 | 193.8694 | 182.9534 | 167.2815 | 145.2292 | 93.461
788.624 | 641.624 | 478.1002 | 228.2678 | 341.1986 | 245.923 | 194.2825 | 183.36 | 167.507 | 145.5032 | 93.6553
789.6354 | 642.6354 | 478.1005 | 228.5234 | 341.482 | 246.1909 | 194.7015 | 183.7737 | 167.7179 | 145.7952 | 93.8154
790.6269 | 643.6269 | 478.1285 | 228.7591 | 341.7472 | 246.4697 | 195.1265 | 184.1805 | 167.9016 | 146.088 | 93.9981
791.6283 | 644.6283 | 478.3178 | 228.9993 | 341.9734 | 246.7437 | 195.5443 | 184.5832 | 168.0908 | 146.3649 | 94.1762
792.6297 | 645.6297 | 478.5322 | 229.2434 | 342.1927 | 246.9763 | 195.9672 | 184.9945 | 168.2753 | 146.6362 | 94.3934
793.6312 | 646.6312 | 478.5505 | 229.5061 | 342.3946 | 247.2519 | 196.3753 | 185.41 | 168.4698 | 146.9267 | 94.5638
794.6326 | 647.6326 | 478.3783 | 229.7211 | 342.6557 | 247.5001 | 196.8012 | 185.8218 | 168.6629 | 147.2144 | 94.7581
795.6241 | 648.6241 | 478.2916 | 229.9659 | 342.8661 | 247.7645 | 197.2169 | 186.224 | 168.8736 | 147.4832 | 94.9593
796.6255 | 649.6255 | 478.171 | 230.1982 | 343.1192 | 248.0239 | 197.6361 | 186.6414 | 169.0677 | 147.798 | 95.1196
797.6269 | 650.6269 | 478.1338 | 230.4464 | 343.3402 | 248.2852 | 198.0451 | 187.0462 | 169.2845 | 148.0762 | 95.3115
798.6284 | 651.6284 | 478.1141 | 230.6803 | 343.5295 | 248.5303 | 198.4706 | 187.4704 | 169.4845 | 148.3728 | 95.4782
799.6298 | 652.6298 | 477.9897 | 230.9192 | 343.7969 | 248.8136 | 198.8902 | 187.9052 | 169.6989 | 148.6544 | 95.6592
800.6313 | 653.6313 | 477.9171 | 231.1729 | 344.0659 | 249.0519 | 199.3069 | 188.3483 | 169.9123 | 148.9428 | 95.8746
801.6327 | 654.6327 | 477.8544 | 231.3947 | 344.3056 | 249.2938 | 199.7131 | 188.7688 | 170.1182 | 149.2268 | 96.0375
802.6341 | 655.6341 | 477.8238 | 231.6477 | 344.5048 | 249.5792 | 200.134 | 189.1973 | 170.3378 | 149.5108 | 96.2471
803.6256 | 656.6256 | 477.8241 | 231.889 | 344.7434 | 249.8324 | 200.5446 | 189.6186 | 170.5488 | 149.8016 | 96.4424
804.627 | 657.627 | 477.882 | 232.1295 | 344.9162 | 250.0877 | 200.9633 | 190.0299 | 170.7745 | 150.0825 | 96.6213
805.6284 | 658.6284 | 478.0518 | 232.3814 | 345.1329 | 250.3157 | 201.368 | 190.4273 | 170.99 | 150.3868 | 96.7904
806.6299 | 659.6299 | 478.0698 | 232.5942 | 345.4049 | 250.5792 | 201.7971 | 190.7994 | 171.2254 | 150.6621 | 97.0039
807.6313 | 660.6313 | 478.0431 | 232.8289 | 345.6723 | 250.8382 | 202.2075 | 191.1475 | 171.4515 | 150.9596 | 97.1759
808.6328 | 661.6328 | 478.0379 | 233.0884 | 345.8284 | 251.0343 | 202.6289 | 191.4652 | 171.685 | 151.2601 | 97.3496
809.6342 | 662.6342 | 477.8951 | 233.3359 | 345.9932 | 251.2844 | 203.0672 | 191.7858 | 171.9251 | 151.5369 | 97.5506
810.6356 | 663.6356 | 477.8171 | 233.5606 | 346.2802 | 251.5483 | 203.4896 | 192.0911 | 172.1625 | 151.829 | 97.7364
811.6271 | 664.6271 | 477.7834 | 233.7862 | 346.5509 | 251.8302 | 203.901 | 192.4098 | 172.4139 | 152.1176 | 97.8936
812.6285 | 665.6285 | 477.7928 | 234.0292 | 346.781 | 252.078 | 204.3251 | 192.7721 | 172.6612 | 152.3952 | 98.1096
813.6299 | 666.6299 | 477.7716 | 234.2696 | 346.9984 | 252.3365 | 204.7433 | 193.1509 | 172.9188 | 152.6878 | 98.3
814.6314 | 667.6314 | 477.6924 | 234.5157 | 347.1907 | 252.6097 | 205.1652 | 193.5079 | 173.1836 | 152.971 | 98.4798
815.6328 | 668.6328 | 477.625 | 234.7496 | 347.411 | 252.8419 | 205.5747 | 193.8864 | 173.4658 | 153.2607 | 98.6661
816.6343 | 669.6343 | 477.755 | 234.9986 | 347.6658 | 253.0938 | 206.0034 | 194.2472 | 173.7519 | 153.5579 | 98.8486
817.6357 | 670.6357 | 477.8816 | 235.2374 | 347.897 | 253.3503 | 206.4171 | 194.6039 | 174.0381 | 153.8567 | 99.0284
818.7072 | 671.7072 | 478.0305 | 235.4813 | 348.1028 | 253.6114 | 206.8593 | 194.998 | 174.3522 | 154.1728 | 99.2238
819.6286 | 672.6286 | 478.248 | 235.7047 | 348.295 | 253.8514 | 207.2585 | 195.3288 | 174.6257 | 154.4411 | 99.3891
820.63 | 673.63 | 478.4202 | 235.9267 | 348.5394 | 254.1007 | 207.6697 | 195.6853 | 174.9248 | 154.7163 | 99.604
821.6314 | 674.6314 | 478.5967 | 236.1795 | 348.7657 | 254.3598 | 208.1008 | 196.0409 | 175.2229 | 155.0057 | 99.7841
822.6329 | 675.6329 | 478.634 | 236.4442 | 349.0032 | 254.6041 | 208.5198 | 196.3856 | 175.5314 | 155.3138 | 99.9363
823.6243 | 676.6243 | 478.7655 | 236.6358 | 349.2148 | 254.8418 | 208.9416 | 196.7397 | 175.8294 | 155.6074 | 100.1317
824.6258 | 677.6258 | 478.8522 | 236.8833 | 349.4686 | 255.0854 | 209.3573 | 197.085 | 176.1344 | 155.8788 | 100.3327
825.6272 | 678.6272 | 478.8988 | 237.1189 | 349.705 | 255.3361 | 209.7731 | 197.4297 | 176.4286 | 156.1834 | 100.5143
826.6286 | 679.6286 | 478.9539 | 237.3647 | 349.9302 | 255.5892 | 210.196 | 197.7579 | 176.7302 | 156.4807 | 100.6885
827.6301 | 680.6301 | 478.846 | 237.5712 | 350.1501 | 255.8299 | 210.6145 | 198.1037 | 177.0301 | 156.7729 | 100.8657
828.6315 | 681.6315 | 478.8723 | 237.81 | 350.3801 | 256.075 | 211.0439 | 198.4534 | 177.3312 | 157.0609 | 101.0808
829.633 | 682.633 | 478.8566 | 238.052 | 350.5695 | 256.3244 | 211.4549 | 198.8166 | 177.6223 | 157.3668 | 101.2263
830.6344 | 683.6344 | 478.7431 | 238.3044 | 350.7513 | 256.5761 | 211.8757 | 199.1895 | 177.9267 | 157.6403 | 101.4486
831.6258 | 684.6258 | 478.8599 | 238.5541 | 351.0013 | 256.7967 | 212.2914 | 199.5556 | 178.224 | 157.9479 | 101.6072
832.6273 | 685.6273 | 479.0386 | 238.774 | 351.2195 | 257.0515 | 212.7181 | 199.9178 | 178.5154 | 158.2397 | 101.7974
833.6287 | 686.6287 | 479.0793 | 239.0046 | 351.4175 | 257.3003 | 213.1418 | 200.2673 | 178.8154 | 158.5302 | 101.9959
834.6301 | 687.6301 | 479.0652 | 239.2275 | 351.6266 | 257.5554 | 213.5678 | 200.6147 | 179.1091 | 158.8286 | 102.1856
835.6316 | 688.6316 | 479.0662 | 239.4821 | 351.9239 | 257.7938 | 213.9868 | 200.9629 | 179.4013 | 159.1186 | 102.3654
836.633 | 689.633 | 479.0183 | 239.677 | 352.049 | 258.0493 | 214.4037 | 201.3085 | 179.6922 | 159.4068 | 102.5482
837.6244 | 690.6244 | 478.8898 | 239.9134 | 352.2667 | 258.2701 | 214.8221 | 201.6462 | 179.9882 | 159.6925 | 102.734
838.6259 | 691.6259 | 478.8036 | 240.1463 | 352.4451 | 258.5307 | 215.2389 | 201.9868 | 180.2815 | 159.9932 | 102.9227
839.6273 | 692.6273 | 478.7354 | 240.3699 | 352.6537 | 258.7604 | 215.6572 | 202.3161 | 180.5821 | 160.2674 | 103.1148
840.6288 | 693.6288 | 478.6884 | 240.5976 | 352.9049 | 258.9917 | 216.0672 | 202.6786 | 180.8682 | 160.5723 | 103.2586
841.6302 | 694.6302 | 478.6165 | 240.8409 | 353.1217 | 259.232 | 216.4947 | 203.0561 | 181.1599 | 160.8522 | 103.4765
842.6316 | 695.6316 | 478.4683 | 241.0427 | 353.3172 | 259.4893 | 216.9073 | 203.4327 | 181.4614 | 161.1283 | 103.6607
843.6331 | 696.6331 | 478.3823 | 241.2824 | 353.5248 | 259.7047 | 217.3301 | 203.8178 | 181.7493 | 161.4022 | 103.8459
844.6245 | 697.6245 | 478.2135 | 241.5215 | 353.7439 | 259.9355 | 217.734 | 204.2017 | 182.0452 | 161.6899 | 104.0203
845.646 | 698.646 | 478.0613 | 241.7369 | 353.8958 | 260.1764 | 218.1712 | 204.598 | 182.3494 | 161.9687 | 104.2159
846.6274 | 699.6274 | 477.9252 | 241.9447 | 354.1317 | 260.4128 | 218.5995 | 204.9727 | 182.6379 | 162.2382 | 104.3848
847.6288 | 700.6288 | 477.8101 | 242.1841 | 354.3722 | 260.6659 | 219.0429 | 205.3553 | 182.9298 | 162.5259 | 104.5545
848.6303 | 701.6303 | 477.8001 | 242.405 | 354.5854 | 260.8828 | 219.489 | 205.7345 | 183.2091 | 162.7754 | 104.7637
849.6317 | 702.6317 | 477.661 | 242.6307 | 354.7511 | 261.1195 | 219.8916 | 206.1014 | 183.4837 | 163.0476 | 104.9279
850.6332 | 703.6332 | 477.5809 | 242.8453 | 354.946 | 261.3472 | 220.3171 | 206.4689 | 183.7181 | 163.3039 | 105.1326
851.6246 | 704.6246 | 477.4884 | 243.0684 | 355.1369 | 261.5746 | 220.7566 | 206.8279 | 183.9662 | 163.5907 | 105.3026
852.626 | 705.626 | 477.3238 | 243.2817 | 355.3566 | 261.8094 | 221.1797 | 207.1903 | 184.2163 | 163.84 | 105.4839
853.6275 | 706.6275 | 477.2488 | 243.5025 | 355.5682 | 262.0388 | 221.5924 | 207.541 | 184.48 | 164.1084 | 105.6635
854.6289 | 707.6289 | 477.162 | 243.7274 | 355.7109 | 262.234 | 222.031 | 207.9083 | 184.7477 | 164.3612 | 105.86
855.6303 | 708.6303 | 476.9916 | 243.9589 | 355.9032 | 262.4644 | 222.4524 | 208.249 | 185.0211 | 164.6118 | 106.0551
856.6318 | 709.6318 | 476.9262 | 244.15 | 356.0324 | 262.7037 | 222.898 | 208.6096 | 185.2996 | 164.8405 | 106.2642
857.6332 | 710.6332 | 476.9235 | 244.365 | 356.2821 | 262.9309 | 223.2986 | 208.9561 | 185.5908 | 165.0944 | 106.4275
858.6347 | 711.6347 | 476.8586 | 244.5914 | 356.543 | 263.1651 | 223.738 | 209.3112 | 185.875 | 165.3412 | 106.6302
859.6261 | 712.6261 | 476.9412 | 244.8134 | 356.7485 | 263.3859 | 224.1777 | 209.6533 | 186.1709 | 165.5927 | 106.8038
860.6275 | 713.6275 | 477.0948 | 245.0281 | 356.9716 | 263.6342 | 224.5927 | 210.0035 | 186.4592 | 165.8273 | 106.9933
861.629 | 714.629 | 477.2899 | 245.2591 | 357.1039 | 263.8532 | 225.0494 | 210.3587 | 186.7567 | 166.0736 | 107.1446
862.6304 | 715.6304 | 477.3183 | 245.4901 | 357.2695 | 264.1001 | 225.4651 | 210.7045 | 187.0613 | 166.301 | 107.3606
863.6318 | 716.6318 | 477.4937 | 245.6893 | 357.556 | 264.3097 | 225.9119 | 211.0382 | 187.3596 | 166.5224 | 107.5464
864.6333 | 717.6333 | 477.7648 | 245.9339 | 357.7625 | 264.578 | 226.3396 | 211.3772 | 187.6597 | 166.7633 | 107.7138
865.6347 | 718.6347 | 477.8441 | 246.1485 | 357.9682 | 264.784 | 226.7775 | 211.7165 | 187.9753 | 166.9937 | 107.8908
866.6261 | 719.6261 | 477.8636 | 246.3826 | 358.168 | 264.9921 | 227.2168 | 212.0585 | 188.2944 | 167.2155 | 108.1003
867.6276 | 720.6276 | 477.9288 | 246.6128 | 358.3555 | 265.2289 | 227.6516 | 212.4115 | 188.6007 | 167.4466 | 108.2866
868.629 | 721.629 | 478.125 | 246.821 | 358.5572 | 265.4674 | 228.0814 | 212.7576 | 188.9215 | 167.6743 | 108.4356
869.6305 | 722.6305 | 478.2301 | 247.0173 | 358.7473 | 265.6956 | 228.5279 | 213.0978 | 189.24 | 167.8839 | 108.6455
870.6319 | 723.6319 | 478.2157 | 247.2659 | 358.8607 | 265.9313 | 228.9574 | 213.4403 | 189.5575 | 168.1286 | 108.811
871.6233 | 724.6233 | 478.3049 | 247.4605 | 359.1119 | 266.1735 | 229.4082 | 213.775 | 189.8802 | 168.3432 | 109.0086
872.6248 | 725.6248 | 478.3776 | 247.6674 | 359.3017 | 266.3817 | 229.8605 | 214.122 | 190.1999 | 168.5591 | 109.1999
873.6262 | 726.6262 | 478.3956 | 247.9138 | 359.5376 | 266.5861 | 230.3089 | 214.4641 | 190.5339 | 168.7669 | 109.399
874.6277 | 727.6277 | 478.4384 | 248.1061 | 359.7312 | 266.7975 | 230.7497 | 214.8084 | 190.8572 | 168.9933 | 109.5466
875.6291 | 728.6291 | 478.421 | 248.3258 | 359.9476 | 267.0539 | 231.1866 | 215.1452 | 191.1801 | 169.2149 | 109.7322
876.6305 | 729.6305 | 478.3811 | 248.5415 | 360.1737 | 267.2812 | 231.6354 | 215.4988 | 191.4975 | 169.4212 | 109.9246
877.632 | 730.632 | 478.3868 | 248.7598 | 360.4115 | 267.5097 | 232.057 | 215.831 | 191.8269 | 169.6178 | 110.137
878.6334 | 731.6334 | 478.3185 | 248.9874 | 360.5918 | 267.7367 | 232.4969 | 216.1744 | 192.1522 | 169.8227 | 110.3107
879.6248 | 732.6248 | 478.4591 | 249.1822 | 360.7639 | 267.9728 | 232.929 | 216.5041 | 192.4742 | 170.0243 | 110.502
880.6263 | 733.6263 | 478.4948 | 249.4548 | 360.9695 | 268.1777 | 233.3655 | 216.8253 | 192.7928 | 170.2228 | 110.7117
881.6277 | 734.6277 | 478.5126 | 249.6327 | 361.1127 | 268.415 | 233.7526 | 217.1505 | 193.1107 | 170.4452 | 110.8718
882.6292 | 735.6292 | 478.4572 | 249.8493 | 361.3279 | 268.6422 | 234.1666 | 217.4798 | 193.4492 | 170.636 | 111.0612
883.6306 | 736.6306 | 478.3739 | 250.0568 | 361.5159 | 268.8407 | 234.5816 | 217.8075 | 193.7692 | 170.8483 | 111.2415
884.632 | 737.632 | 478.2921 | 250.2849 | 361.7217 | 269.0882 | 235.0032 | 218.1469 | 194.0945 | 171.0557 | 111.4274
885.6335 | 738.6335 | 478.2146 | 250.4957 | 361.8774 | 269.3116 | 235.4233 | 218.482 | 194.4148 | 171.2512 | 111.5966
886.6349 | 739.6349 | 478.1382 | 250.6951 | 362.1264 | 269.542 | 235.8318 | 218.8154 | 194.7479 | 171.4359 | 111.8023
887.6263 | 740.6263 | 478.0948 | 250.9028 | 362.2764 | 269.7651 | 236.2711 | 219.1358 | 195.0686 | 171.6335 | 111.9698
888.6278 | 741.6278 | 478.0786 | 251.1314 | 362.4894 | 269.9836 | 236.7004 | 219.4622 | 195.4 | 171.8266 | 112.1785
889.6292 | 742.6292 | 478.1188 | 251.3561 | 362.739 | 270.2063 | 237.1243 | 219.7867 | 195.7334 | 172.0188 | 112.3316
890.6307 | 743.6307 | 478.1735 | 251.5677 | 362.9029 | 270.4219 | 237.5367 | 220.0981 | 196.065 | 172.1997 | 112.5382
891.6321 | 744.6321 | 478.1359 | 251.7463 | 363.0836 | 270.6424 | 237.9596 | 220.4234 | 196.3757 | 172.3787 | 112.7381
892.6235 | 745.6235 | 478.067 | 251.9745 | 363.2783 | 270.8551 | 238.3541 | 220.7555 | 196.6914 | 172.5577 | 112.9124
893.625 | 746.625 | 478.0259 | 252.1827 | 363.4779 | 271.0898 | 238.7443 | 221.0846 | 196.9955 | 172.7356 | 113.0995
894.6264 | 747.6264 | 478.0621 | 252.3953 | 363.6626 | 271.3164 | 239.1521 | 221.4131 | 197.3057 | 172.9003 | 113.3091
895.6278 | 748.6278 | 478.1002 | 252.594 | 363.7978 | 271.5351 | 239.5575 | 221.7484 | 197.6055 | 173.07 | 113.4675
896.6293 | 749.6293 | 478.1064 | 252.8042 | 364.0726 | 271.7391 | 239.9609 | 222.0867 | 197.9021 | 173.2394 | 113.6837
897.6307 | 750.6307 | 478.0606 | 253.0216 | 364.3065 | 271.9638 | 240.3752 | 222.4491 | 198.1964 | 173.406 | 113.8719
898.6322 | 751.6322 | 478.0903 | 253.2409 | 364.561 | 272.2114 | 240.7855 | 222.8202 | 198.4892 | 173.5698 | 114.0406
899.6236 | 752.6236 | 478.1204 | 253.4383 | 364.736 | 272.4285 | 241.1765 | 223.1952 | 198.8099 | 173.7451 | 114.2056
900.635 | 753.635 | 478.2153 | 253.6325 | 364.8541 | 272.6288 | 241.5802 | 223.5714 | 199.1431 | 173.8803 | 114.3997
901.6265 | 754.6265 | 478.3033 | 253.8394 | 365.0449 | 272.8636 | 241.9678 | 223.9489 | 199.5091 | 174.0437 | 114.5763
902.6279 | 755.6279 | 478.2859 | 254.0411 | 365.2461 | 273.0742 | 242.359 | 224.341 | 199.8626 | 174.1857 | 114.7779
903.6294 | 756.6294 | 478.2666 | 254.2652 | 365.4192 | 273.2694 | 242.7308 | 224.7189 | 200.2048 | 174.3374 | 114.9502
904.6308 | 757.6308 | 478.3751 | 254.4633 | 365.6063 | 273.5024 | 243.1096 | 225.1187 | 200.583 | 174.4676 | 115.1628
905.6322 | 758.6322 | 478.3643 | 254.6658 | 365.8104 | 273.6971 | 243.4954 | 225.5155 | 200.9471 | 174.6139 | 115.3363
906.6337 | 759.6337 | 478.1796 | 254.8912 | 366.0539 | 273.9178 | 243.8731 | 225.9227 | 201.2885 | 174.7324 | 115.5426
907.6251 | 760.6251 | 478.0215 | 255.0781 | 366.2242 | 274.1218 | 244.2582 | 226.3327 | 201.6513 | 174.8725 | 115.709
908.6265 | 761.6265 | 477.8785 | 255.2775 | 366.2692 | 274.3446 | 244.6227 | 226.7462 | 202.0034 | 175.0006 | 115.8968
909.628 | 762.628 | 477.6933 | 255.4986 | 366.3777 | 274.5488 | 245.0248 | 227.1633 | 202.3511 | 175.1167 | 116.091
910.6294 | 763.6294 | 477.6699 | 255.6886 | 366.6072 | 274.7618 | 245.4319 | 227.5823 | 202.6934 | 175.2512 | 116.2565
911.6309 | 764.6309 | 477.8268 | 255.9022 | 366.8107 | 274.9665 | 245.8283 | 228.0116 | 203.0342 | 175.3783 | 116.454
912.6323 | 765.6323 | 477.8669 | 256.1029 | 367.0324 | 275.1687 | 246.2167 | 228.448 | 203.3626 | 175.504 | 116.6341
913.6237 | 766.6237 | 477.8763 | 256.3177 | 367.2421 | 275.3853 | 246.6005 | 228.8954 | 203.6894 | 175.6371 | 116.8271
914.6252 | 767.6252 | 477.9873 | 256.5363 | 367.3936 | 275.5957 | 247.0035 | 229.3517 | 204.0132 | 175.763 | 117.0214
915.6266 | 768.6266 | 478.1168 | 256.7299 | 367.5923 | 275.8111 | 247.366 | 229.8233 | 204.3358 | 175.8944 | 117.1694
916.628 | 769.628 | 478.1778 | 256.9161 | 367.7863 | 276.02 | 247.7314 | 230.2991 | 204.6506 | 176.0172 | 117.3869
917.6295 | 770.6295 | 478.1775 | 257.1052 | 367.996 | 276.2517 | 248.0966 | 230.8078 | 204.9609 | 176.1495 | 117.571
918.6309 | 771.6309 | 478.1733 | 257.3294 | 368.1319 | 276.4498 | 248.4522 | 231.321 | 205.2675 | 176.2914 | 117.7584
919.6324 | 772.6324 | 478.2721 | 257.5147 | 368.2537 | 276.6488 | 248.8191 | 231.8539 | 205.5576 | 176.4189 | 117.9297
920.6238 | 773.6238 | 478.3489 | 257.7265 | 368.5351 | 276.8629 | 249.1983 | 232.4124 | 205.8432 | 176.5553 | 118.0867
921.6252 | 774.6252 | 478.3347 | 257.925 | 368.6513 | 277.101 | 249.5815 | 232.9682 | 206.1332 | 176.6735 | 118.2767
922.6267 | 775.6267 | 478.39 | 258.1118 | 368.9031 | 277.2953 | 249.9617 | 233.5249 | 206.4216 | 176.7991 | 118.4882
923.6281 | 776.6281 | 478.3734 | 258.3105 | 369.0651 | 277.5243 | 250.3251 | 234.0801 | 206.7263 | 176.9698 | 118.6378
924.6296 | 777.6296 | 478.3343 | 258.5362 | 369.2097 | 277.698 | 250.6742 | 234.628 | 207.0368 | 177.1198 | 118.8316
925.631 | 778.631 | 478.4007 | 258.7375 | 369.4137 | 277.9434 | 251.0725 | 235.1864 | 207.3674 | 177.3021 | 118.9944
926.6324 | 779.6324 | 478.4692 | 258.9282 | 369.5548 | 278.1448 | 251.4535 | 235.7524 | 207.6954 | 177.4754 | 119.1849
927.6339 | 780.6339 | 478.5782 | 259.1269 | 369.779 | 278.3498 | 251.8016 | 236.3225 | 208.0457 | 177.6584 | 119.3407
928.6253 | 781.6253 | 478.5874 | 259.3314 | 369.9455 | 278.5223 | 252.111 | 236.9768 | 208.3943 | 177.8538 | 119.5123
929.6267 | 782.6267 | 478.5592 | 259.5144 | 370.1522 | 278.7596 | 252.3883 | 237.8032 | 208.7547 | 178.03 | 119.7022
930.6282 | 783.6282 | 478.544 | 259.7255 | 370.3177 | 278.9675 | 252.6153 | 238.7036 | 209.1026 | 178.2232 | 119.8703
931.6296 | 784.6296 | 478.5456 | 259.9239 | 370.4636 | 279.163 | 252.8425 | 240.0861 | 209.4396 | 178.4151 | 120.0679
932.6311 | 785.6311 | 478.6525 | 260.11 | 370.5576 | 279.3827 | 253.1903 | 241.9193 | 209.7668 | 178.6195 | 120.1912
933.6325 | 786.6325 | 478.7792 | 260.3139 | 370.862 | 279.5611 | 253.4646 | 243.2965 | 210.0878 | 178.8039 | 120.3965
934.6339 | 787.6339 | 478.8091 | 260.5057 | 371.0801 | 279.7864 | 253.6764 | 244.3265 | 210.4116 | 178.9761 | 120.5711
935.6254 | 788.6254 | 478.927 | 260.7298 | 371.2126 | 279.9864 | 253.9171 | 245.185 | 210.7323 | 179.139 | 120.7563
936.6268 | 789.6268 | 478.7514 | 260.9368 | 371.3618 | 280.1907 | 254.1329 | 245.9109 | 211.0533 | 179.2957 | 120.9431
937.6282 | 790.6282 | 478.6991 | 261.1264 | 371.5777 | 280.4106 | 254.3617 | 246.5805 | 211.3688 | 179.4976 | 121.1074
938.6297 | 791.6297 | 478.6562 | 261.3117 | 371.7199 | 280.6162 | 254.6198 | 247.1371 | 211.7034 | 179.6896 | 121.2606
939.6311 | 792.6311 | 478.6831 | 261.5148 | 371.9633 | 280.8479 | 254.882 | 247.7025 | 212.0431 | 179.8719 | 121.4462
940.6326 | 793.6326 | 478.5988 | 261.706 | 372.1305 | 281.0185 | 255.1504 | 248.2741 | 212.3951 | 180.0457 | 121.6391
941.624 | 794.624 | 478.5986 | 261.8977 | 372.2684 | 281.2342 | 255.4093 | 248.8333 | 212.74 | 180.2558 | 121.7935
942.6354 | 795.6354 | 478.5679 | 262.0693 | 372.4226 | 281.4075 | 255.7072 | 249.3266 | 213.0642 | 180.4572 | 121.985
943.6269 | 796.6269 | 478.6276 | 262.2795 | 372.6414 | 281.6298 | 255.9892 | 249.8716 | 213.3933 | 180.6526 | 122.1608
944.6283 | 797.6283 | 478.6104 | 262.479 | 372.8446 | 281.8282 | 256.1581 | 250.3524 | 213.7298 | 180.8629 | 122.3101
945.6297 | 798.6297 | 478.5546 | 262.6823 | 373.117 | 282.0341 | 255.9736 | 250.7592 | 214.0618 | 181.0751 | 122.4818
946.6312 | 799.6312 | 478.4346 | 262.8643 | 373.1986 | 282.2409 | 256.1031 | 251.1832 | 214.3811 | 181.2863 | 122.6479
947.6326 | 800.6326 | 478.4115 | 263.0332 | 373.4292 | 282.4021 | 256.3576 | 251.5616 | 214.7496 | 181.4921 | 122.8329
948.6341 | 801.6341 | 478.3796 | 263.2213 | 373.5643 | 282.6147 | 256.7032 | 251.898 | 215.1255 | 181.7265 | 122.9776
949.6255 | 802.6255 | 478.3554 | 263.4316 | 373.761 | 282.7914 | 257.0504 | 252.2396 | 215.507 | 181.9505 | 123.1637
950.6269 | 803.6269 | 478.3733 | 263.6301 | 373.9552 | 283.0073 | 257.452 | 252.6067 | 215.8779 | 182.1875 | 123.3298
951.6284 | 804.6284 | 478.5233 | 263.7993 | 374.1555 | 283.2039 | 257.8472 | 252.9622 | 216.2563 | 182.422 | 123.4984
952.6298 | 805.6298 | 478.4855 | 263.9976 | 374.3065 | 283.3822 | 258.2626 | 253.3823 | 216.6405 | 182.6665 | 123.645
953.6313 | 806.6313 | 478.4449 | 264.1845 | 374.4882 | 283.5948 | 258.6807 | 253.8067 | 216.9771 | 182.8941 | 123.8345
954.6327 | 807.6327 | 478.3785 | 264.377 | 374.6411 | 283.8111 | 259.0732 | 254.1988 | 217.2968 | 183.1317 | 124.0167
955.6341 | 808.6341 | 478.3043 | 264.5755 | 374.8713 | 283.9621 | 259.4807 | 254.583 | 217.5976 | 183.3545 | 124.18
956.6256 | 809.6256 | 478.1176 | 264.7547 | 375.0505 | 284.1644 | 259.8794 | 254.9293 | 217.8882 | 183.5918 | 124.3515
957.627 | 810.627 | 477.9788 | 264.9667 | 375.2136 | 284.3677 | 260.2504 | 255.2862 | 218.1731 | 183.8244 | 124.5083
958.6284 | 811.6284 | 477.8934 | 265.1397 | 375.3868 | 284.5958 | 260.6617 | 255.612 | 218.471 | 184.0644 | 124.6904
959.6299 | 812.6299 | 477.7836 | 265.3365 | 375.5382 | 284.7647 | 261.0577 | 255.8615 | 218.7692 | 184.2868 | 124.8536
960.6313 | 813.6313 | 477.7808 | 265.5204 | 375.7654 | 284.9628 | 261.4394 | 256.1564 | 219.0957 | 184.5299 | 125.024
961.6328 | 814.6328 | 477.8175 | 265.6614 | 375.9306 | 285.142 | 261.8387 | 256.4998 | 219.3889 | 184.7724 | 125.1873
962.6342 | 815.6342 | 477.8284 | 265.8894 | 376.0558 | 285.3409 | 262.2176 | 256.8251 | 219.6746 | 184.9959 | 125.3598
963.6356 | 816.6356 | 477.8169 | 266.0963 | 376.2298 | 285.4891 | 262.59 | 257.1979 | 219.9796 | 185.2157 | 125.532
964.6271 | 817.6271 | 477.7052 | 266.2681 | 376.4262 | 285.7279 | 262.9669 | 257.6463 | 220.2632 | 185.4452 | 125.692
965.6285 | 818.6285 | 477.5589 | 266.4367 | 376.5489 | 285.8914 | 263.3268 | 257.9605 | 220.5342 | 185.6562 | 125.8406
966.6299 | 819.6299 | 477.5152 | 266.6012 | 376.6699 | 286.11 | 263.6623 | 258.2815 | 220.8111 | 185.8381 | 126.0292
967.6314 | 820.6314 | 477.3934 | 266.7808 | 376.8909 | 286.286 | 264.0079 | 258.5494 | 221.1086 | 186.034 | 126.1681
968.6328 | 821.6328 | 477.3721 | 266.9643 | 377.0496 | 286.4654 | 264.3662 | 258.8487 | 221.3798 | 186.2324 | 126.3504
969.6343 | 822.6343 | 477.3997 | 267.1602 | 377.223 | 286.6561 | 264.7104 | 259.1238 | 221.6856 | 186.4219 | 126.4986
970.6257 | 823.6257 | 477.4457 | 267.3522 | 377.3893 | 286.8262 | 265.0308 | 259.407 | 221.9807 | 186.5882 | 126.6716
971.6271 | 824.6271 | 477.3145 | 267.5296 | 377.5902 | 287.0444 | 265.3498 | 259.7338 | 222.2944 | 186.7725 | 126.8284
972.6286 | 825.6286 | 477.1845 | 267.7118 | 377.6997 | 287.2375 | 265.6603 | 260.1286 | 222.6113 | 186.9585 | 127.0072
973.63 | 826.63 | 477.2118 | 267.8972 | 377.8327 | 287.4135 | 265.9582 | 260.4506 | 222.9148 | 187.1503 | 127.1762
974.6315 | 827.6315 | 477.3252 | 268.0732 | 378.0201 | 287.611 | 266.2461 | 260.7581 | 223.2443 | 187.3625 | 127.3233
975.6329 | 828.6329 | 477.4444 | 268.2797 | 378.1708 | 287.7625 | 266.5257 | 261.0813 | 223.5728 | 187.5692 | 127.4878
976.6343 | 829.6343 | 477.5304 | 268.453 | 378.3506 | 287.9952 | 266.8244 | 261.3756 | 223.9187 | 187.7861 | 127.6573
977.6258 | 830.6258 | 477.6939 | 268.6185 | 378.4422 | 288.1768 | 267.0982 | 261.6916 | 224.2403 | 188.0185 | 127.795
978.6272 | 831.6272 | 477.7396 | 268.8231 | 378.6677 | 288.3568 | 267.3253 | 262.014 | 224.5681 | 188.2474 | 127.9717
979.6286 | 832.6286 | 477.7593 | 268.9903 | 378.7992 | 288.5462 | 267.6677 | 262.3882 | 224.8896 | 188.4721 | 128.1429
980.6301 | 833.6301 | 477.6794 | 269.1741 | 378.9863 | 288.6818 | 267.9103 | 262.7088 | 225.218 | 188.707 | 128.3313
981.6315 | 834.6315 | 477.5692 | 269.3637 | 379.1834 | 288.9109 | 268.1303 | 263.0072 | 225.5537 | 188.9397 | 128.4834
982.633 | 835.633 | 477.5799 | 269.5451 | 379.3255 | 289.1037 | 268.4028 | 263.405 | 225.8654 | 189.2086 | 128.6426
983.6244 | 836.6244 | 477.6736 | 269.7293 | 379.5203 | 289.2988 | 268.6576 | 263.8304 | 226.1856 | 189.4541 | 128.8141
984.6258 | 837.6258 | 477.7224 | 269.9052 | 379.7228 | 289.5006 | 268.8639 | 264.2069 | 226.4812 | 189.7121 | 128.9829
985.6273 | 838.6273 | 477.8334 | 270.0957 | 379.8524 | 289.6674 | 269.0576 | 264.6136 | 226.7997 | 189.9716 | 129.1295
986.6287 | 839.6287 | 477.9639 | 270.2974 | 379.9731 | 289.8312 | 269.3243 | 265.0155 | 227.1332 | 190.2356 | 129.3197
987.6301 | 840.6301 | 478.0209 | 270.4625 | 380.1764 | 290.0133 | 269.5727 | 265.361 | 227.4833 | 190.5102 | 129.4988
988.6316 | 841.6316 | 478.1205 | 270.6473 | 380.2959 | 290.1913 | 269.7683 | 265.6819 | 227.8412 | 190.7767 | 129.6473
989.633 | 842.633 | 478.0876 | 270.8276 | 380.4872 | 290.4097 | 270.0238 | 265.9923 | 228.2029 | 191.0336 | 129.8565
990.6345 | 843.6345 | 478.165 | 271.0058 | 380.665 | 290.5832 | 270.2541 | 266.3332 | 228.5405 | 191.3224 | 129.995
991.6359 | 844.6359 | 478.2068 | 271.1952 | 380.7826 | 290.741 | 270.5135 | 266.6381 | 228.8726 | 191.5767 | 130.1974
992.6273 | 845.6273 | 478.1446 | 271.3544 | 380.976 | 290.9579 | 270.7683 | 267.0093 | 229.2506 | 191.8601 | 130.3475
993.6288 | 846.6288 | 478.2287 | 271.5468 | 381.1362 | 291.1187 | 270.9536 | 267.1259 | 229.6102 | 192.1178 | 130.5117
994.6302 | 847.6302 | 478.3034 | 271.7364 | 381.3361 | 291.3289 | 271.1486 | 267.2323 | 229.9479 | 192.4005 | 130.655
995.6316 | 848.6316 | 478.3351 | 271.8993 | 381.5153 | 291.5073 | 271.3722 | 267.4311 | 230.2598 | 192.6565 | 130.8599
996.6331 | 849.6331 | 478.5419 | 272.1105 | 381.6145 | 291.6706 | 271.6457 | 267.7354 | 230.575 | 192.9311 | 131.0321
997.6345 | 850.6345 | 478.6889 | 272.291 | 381.8386 | 291.8471 | 271.8809 | 268.0133 | 230.8636 | 193.2082 | 131.1808
998.636 | 851.636 | 478.8153 | 272.4674 | 381.9945 | 292.0237 | 272.0671 | 268.4796 | 231.1366 | 193.4793 | 131.3694
999.6274 | 852.6274 | 478.8569 | 272.63 | 382.1953 | 292.225 | 272.1758 | 268.9507 | 231.3992 | 193.7341 | 131.5485
1000.6288 | 853.6288 | 478.9501 | 272.8043 | 382.3316 | 292.3993 | 272.2257 | 269.4861 | 231.6784 | 194.0124 | 131.6878
1001.6303 | 854.6303 | 478.9171 | 273.0006 | 382.5186 | 292.5425 | 272.389 | 269.4547 | 231.9771 | 194.2661 | 131.9056
1002.6317 | 855.6317 | 478.8303 | 273.1692 | 382.665 | 292.7303 | 272.6933 | 269.4829 | 232.2886 | 194.5639 | 132.0402
1003.6332 | 856.6332 | 478.8411 | 273.354 | 382.8096 | 292.9299 | 273.0252 | 269.4577 | 232.5865 | 194.8353 | 132.209
1004.6246 | 857.6246 | 478.9143 | 273.5174 | 382.9423 | 293.0784 | 273.3252 | 269.5207 | 232.9001 | 195.1031 | 132.4172
1005.626 | 858.626 | 478.8198 | 273.6884 | 383.0382 | 293.2633 | 273.6276 | 269.6666 | 233.2309 | 195.3767 | 132.58
1006.6275 | 859.6275 | 478.7861 | 273.8703 | 383.2552 | 293.4862 | 273.9173 | 269.9312 | 233.5454 | 195.6573 | 132.7422
1007.6289 | 860.6289 | 478.7859 | 274.0385 | 383.2983 | 293.6924 | 274.2544 | 270.1573 | 233.8305 | 195.9357 | 132.9274
1008.6303 | 861.6303 | 478.664 | 274.2122 | 383.4981 | 293.8396 | 274.5347 | 270.3043 | 234.1073 | 196.2137 | 133.1023
1009.6318 | 862.6318 | 478.68 | 274.404 | 383.7218 | 294.0478 | 274.8314 | 270.4547 | 234.3997 | 196.499 | 133.2734
1010.6332 | 863.6332 | 478.705 | 274.5772 | 383.9192 | 294.2264 | 275.1475 | 270.8478 | 234.6839 | 196.7618 | 133.4851
1011.6246 | 864.6246 | 478.7285 | 274.7548 | 384.0114 | 294.3996 | 275.4211 | 271.1454 | 234.9165 | 197.0518 | 133.6543
1012.6261 | 865.6261 | 478.7851 | 274.931 | 384.1846 | 294.5995 | 275.6367 | 271.2157 | 235.1524 | 197.3583 | 133.8074
1013.6275 | 866.6275 | 478.795 | 275.0775 | 384.4006 | 294.7839 | 275.9078 | 271.381 | 235.3953 | 197.6412 | 133.9952
1014.629 | 867.629 | 478.8423 | 275.2628 | 384.519 | 294.9652 | 276.1399 | 271.6147 | 235.6444 | 197.9251 | 134.1611
1015.6304 | 868.6304 | 478.8519 | 275.4406 | 384.6368 | 295.1339 | 276.3331 | 271.9807 | 235.8624 | 198.2072 | 134.3541
1016.6318 | 869.6318 | 478.8566 | 275.616 | 384.8399 | 295.3188 | 276.5011 | 272.2401 | 236.0727 | 198.4872 | 134.5317
1017.6333 | 870.6333 | 478.9106 | 275.8196 | 385.0002 | 295.4747 | 276.6458 | 272.4519 | 236.3095 | 198.7691 | 134.7246
1018.6347 | 871.6347 | 478.8867 | 276.0069 | 385.167 | 295.6247 | 276.7866 | 272.9711 | 236.5655 | 199.0579 | 134.9128
1019.6262 | 872.6262 | 478.9096 | 276.159 | 385.3734 | 295.8224 | 276.9239 | 273.3323 | 236.8261 | 199.359 | 135.087
1020.6276 | 873.6276 | 479.0351 | 276.3556 | 385.5128 | 296.0105 | 277.0531 | 273.4555 | 237.0927 | 199.6575 | 135.2774
1021.629 | 874.629 | 479.0144 | 276.5076 | 385.6603 | 296.1971 | 277.1919 | 273.4138 | 237.3534 | 199.9546 | 135.4428
1022.6305 | 875.6305 | 478.9021 | 276.6758 | 385.8303 | 296.3702 | 277.3322 | 273.4851 | 237.618 | 200.2448 | 135.6363
1023.6319 | 876.6319 | 478.7957 | 276.8606 | 385.9342 | 296.539 | 277.5037 | 273.7626 | 237.8794 | 200.5501 | 135.8127
1024.6334 | 877.6334 | 478.6419 | 277.0264 | 386.0924 | 296.7307 | 277.695 | 273.9412 | 238.1049 | 200.8316 | 136.0005
1025.6448 | 878.6448 | 478.564 | 277.1798 | 386.2245 | 296.9074 | 277.8453 | 274.1697 | 238.3614 | 201.1265 | 136.2123
1026.6262 | 879.6262 | 478.3884 | 277.3659 | 386.3396 | 297.0861 | 278.0437 | 274.5019 | 238.5889 | 201.412 | 136.3895
1027.6277 | 880.6277 | 478.3786 | 277.5301 | 386.5108 | 297.2478 | 278.1805 | 274.6414 | 238.8151 | 201.6978 | 136.5762
1028.6291 | 881.6291 | 478.3014 | 277.7129 | 386.7158 | 297.4353 | 278.3424 | 274.9544 | 239.0433 | 201.9759 | 136.7782
1029.6305 | 882.6305 | 478.404 | 277.8777 | 386.8123 | 297.6112 | 278.5222 | 275.2224 | 239.2629 | 202.2898 | 136.9503
1030.632 | 883.632 | 478.5584 | 278.0694 | 386.9269 | 297.7894 | 278.7718 | 275.3784 | 239.4703 | 202.5979 | 137.1561
1031.6334 | 884.6334 | 478.61 | 278.2243 | 387.053 | 297.9624 | 278.9406 | 275.4866 | 239.6871 | 202.9029 | 137.3266
1032.6349 | 885.6349 | 478.4969 | 278.4145 | 387.232 | 298.1297 | 279.0846 | 275.5207 | 239.9151 | 203.2093 | 137.5067
1033.6263 | 886.6263 | 478.3594 | 278.6017 | 387.3923 | 298.2929 | 279.2551 | 275.4946 | 240.0969 | 203.5247 | 137.6767
1034.6277 | 887.6277 | 478.2804 | 278.7703 | 387.5386 | 298.4643 | 279.4441 | 275.6742 | 240.289 | 203.8238 | 137.881
1035.6292 | 888.6292 | 478.2097 | 278.9343 | 387.7034 | 298.6719 | 279.5765 | 276.2091 | 240.464 | 204.1296 | 138.0673
1036.6306 | 889.6306 | 478.2435 | 279.0982 | 387.6889 | 298.8386 | 279.6991 | 276.7691 | 240.6529 | 204.4365 | 138.2815
1037.632 | 890.632 | 478.181 | 279.2721 | 387.8707 | 299.0072 | 279.8128 | 277.1194 | 240.8398 | 204.7612 | 138.4684
1038.6335 | 891.6335 | 478.0358 | 279.4623 | 388.0369 | 299.1807 | 279.9126 | 277.3381 | 241.0248 | 205.0725 | 138.689
1039.6349 | 892.6349 | 477.9221 | 279.6186 | 388.1956 | 299.3837 | 280.0432 | 277.5768 | 241.2037 | 205.4069 | 138.8767
1040.6263 | 893.6263 | 477.9125 | 279.7802 | 388.354 | 299.5375 | 280.208 | 277.5756 | 241.4539 | 205.7261 | 139.0776
1041.6278 | 894.6278 | 477.8506 | 279.9504 | 388.5401 | 299.6834 | 280.3765 | 277.9205 | 241.7145 | 206.0578 | 139.264
1042.6292 | 895.6292 | 477.7434 | 280.1128 | 388.695 | 299.873 | 280.5262 | 278.2618 | 241.9461 | 206.3826 | 139.4903
1043.6307 | 896.6307 | 477.6901 | 280.3174 | 388.7741 | 300.0358 | 280.6462 | 278.4693 | 242.1832 | 206.7127 | 139.6706
1044.6321 | 897.6321 | 477.6457 | 280.4957 | 388.9467 | 300.1936 | 280.791 | 278.2032 | 242.419 | 207.0141 | 139.8988
1045.6235 | 898.6235 | 477.6279 | 280.6362 | 388.9564 | 300.3942 | 280.9669 | 278.2458 | 242.6463 | 207.3392 | 140.0918
1046.625 | 899.625 | 477.5756 | 280.8052 | 389.1182 | 300.5448 | 281.0991 | 278.431 | 242.8656 | 207.6632 | 140.2849
1047.6264 | 900.6264 | 477.477 | 280.9858 | 389.2948 | 300.7206 | 281.1023 | 278.6236 | 243.1392 | 207.994 | 140.4882
1048.6279 | 901.6279 | 477.4341 | 281.1612 | 389.3932 | 300.8735 | 281.2777 | 278.7769 | 243.3924 | 208.3174 | 140.6711
1049.6293 | 902.6293 | 477.5005 | 281.3018 | 389.6215 | 301.0514 | 281.4637 | 278.9721 | 243.6205 | 208.6431 | 140.8866
1050.6307 | 903.6307 | 477.4091 | 281.4677 | 389.7435 | 301.2273 | 281.6042 | 279.2117 | 243.8876 | 208.9564 | 141.0729
1051.6322 | 904.6322 | 477.3114 | 281.6459 | 389.8799 | 301.394 | 281.7553 | 279.3935 | 244.145 | 209.2614 | 141.2979
1052.6336 | 905.6336 | 477.2879 | 281.7944 | 389.9919 | 301.5868 | 281.9237 | 279.632 | 244.4064 | 209.5778 | 141.5078
1053.625 | 906.625 | 477.2754 | 281.9757 | 390.1937 | 301.7594 | 282.1031 | 279.8768 | 244.686 | 209.89 | 141.7123
1054.6265 | 907.6265 | 477.2834 | 282.1465 | 390.3012 | 301.913 | 282.2392 | 280.1894 | 244.9587 | 210.2052 | 141.9159
1055.6279 | 908.6279 | 477.4235 | 282.3189 | 390.418 | 302.0608 | 282.3965 | 280.5199 | 245.2356 | 210.5189 | 142.1028
1056.6294 | 909.6294 | 477.392 | 282.4888 | 390.5871 | 302.2372 | 282.6032 | 280.8147 | 245.4913 | 210.8327 | 142.3212
1057.6308 | 910.6308 | 477.3136 | 282.6543 | 390.6315 | 302.413 | 282.7812 | 281.0961 | 245.7499 | 211.1525 | 142.5481
1058.6322 | 911.6322 | 477.3274 | 282.8413 | 390.7633 | 302.5555 | 282.9568 | 281.4976 | 246.0042 | 211.4477 | 142.7522
1059.6337 | 912.6337 | 477.3602 | 282.9953 | 390.9147 | 302.7198 | 283.134 | 281.7061 | 246.228 | 211.7703 | 142.9216
1060.6351 | 913.6351 | 477.298 | 283.185 | 391.0459 | 302.8909 | 283.2994 | 281.8934 | 246.4547 | 212.0708 | 143.1589
1061.6265 | 914.6265 | 477.2099 | 283.3557 | 391.203 | 303.0462 | 283.4576 | 282.3375 | 246.6859 | 212.3944 | 143.3582
1062.628 | 915.628 | 477.1843 | 283.5018 | 391.3614 | 303.1908 | 283.6128 | 282.5981 | 246.9294 | 212.7011 | 143.5656
1063.6294 | 916.6294 | 476.9793 | 283.6814 | 391.421 | 303.3764 | 283.8608 | 282.7182 | 247.1622 | 213.0002 | 143.7876
1064.6309 | 917.6309 | 476.9318 | 283.8368 | 391.6172 | 303.557 | 283.9909 | 282.8202 | 247.401 | 213.3145 | 143.992
1065.6323 | 918.6323 | 476.9505 | 283.991 | 391.6762 | 303.7224 | 284.2219 | 282.6797 | 247.6445 | 213.6633 | 144.1448
1066.6237 | 919.6237 | 476.9381 | 284.1437 | 391.7553 | 303.8827 | 284.3055 | 282.5333 | 247.8761 | 213.9814 | 144.3589
1067.6252 | 920.6252 | 477.0176 | 284.3213 | 391.8329 | 304.0631 | 284.4056 | 283.023 | 248.1137 | 214.2944 | 144.5782
1068.6266 | 921.6266 | 476.9099 | 284.4885 | 391.9866 | 304.204 | 284.5966 | 283.4968 | 248.3407 | 214.6067 | 144.786
1069.628 | 922.628 | 476.8389 | 284.6494 | 392.0757 | 304.374 | 284.8169 | 283.8146 | 248.5737 | 214.9122 | 145.0121
1070.6295 | 923.6295 | 477.001 | 284.8063 | 392.2635 | 304.5622 | 285.0631 | 284.1171 | 248.799 | 215.2301 | 145.209
1071.6309 | 924.6309 | 477.2438 | 284.9891 | 392.4594 | 304.7061 | 285.2553 | 284.4624 | 249.0324 | 215.5483 | 145.4105
1072.6324 | 925.6324 | 477.4366 | 285.12 | 392.5506 | 304.873 | 285.3994 | 284.9018 | 249.2448 | 215.8657 | 145.6273
1073.6338 | 926.6338 | 477.6326 | 285.2911 | 392.7005 | 305.0483 | 285.5728 | 285.4736 | 249.4786 | 216.1952 | 145.8127
1074.6352 | 927.6352 | 477.7354 | 285.4778 | 392.8176 | 305.2206 | 285.6756 | 285.8126 | 249.666 | 216.5068 | 146.0427
1075.6267 | 928.6267 | 477.6449 | 285.6038 | 393.0073 | 305.4109 | 285.8287 | 286.1205 | 249.8204 | 216.8329 | 146.2426
1076.6281 | 929.6281 | 477.6681 | 285.7951 | 393.0296 | 305.57 | 286.0456 | 286.4146 | 250.0037 | 217.1446 | 146.4594
1077.6296 | 930.6296 | 477.6833 | 285.93 | 393.1755 | 305.7179 | 286.2621 | 286.8693 | 250.2288 | 217.4786 | 146.6656
1078.631 | 931.631 | 477.682 | 286.1072 | 393.3313 | 305.8753 | 286.4859 | 287.0942 | 250.4783 | 217.7954 | 146.886
1079.6324 | 932.6324 | 477.5862 | 286.2601 | 393.4779 | 306.0294 | 286.7248 | 287.4111 | 250.7217 | 218.1306 | 147.0875
1080.6339 | 933.6339 | 477.5732 | 286.4205 | 393.6123 | 306.1716 | 286.9475 | 287.4564 | 250.9461 | 218.4624 | 147.2945
1081.6253 | 934.6253 | 477.4265 | 286.5588 | 393.6926 | 306.3427 | 287.1763 | 287.5961 | 251.1878 | 218.769 | 147.4986
1082.6267 | 935.6267 | 477.3323 | 286.7263 | 393.7184 | 306.4846 | 287.3463 | 288.0483 | 251.4824 | 219.0927 | 147.7248
1083.6282 | 936.6282 | 477.3615 | 286.8933 | 393.8278 | 306.6866 | 287.5882 | 288.4372 | 251.7766 | 219.4071 | 147.9262
1084.6296 | 937.6296 | 477.4627 | 287.0396 | 393.9351 | 306.8281 | 287.7674 | 288.7533 | 252.0529 | 219.7141 | 148.1648
1085.6311 | 938.6311 | 477.5265 | 287.1787 | 394.0219 | 306.9844 | 287.9158 | 289.0108 | 252.3157 | 220.0343 | 148.3377
1086.6325 | 939.6325 | 477.4613 | 287.3592 | 394.1782 | 307.1436 | 288.047 | 289.1379 | 252.5832 | 220.3323 | 148.561
1087.6339 | 940.6339 | 477.2765 | 287.5194 | 394.3306 | 307.3067 | 288.2543 | 289.2922 | 252.8654 | 220.6579 | 148.772
1088.6254 | 941.6254 | 477.1331 | 287.6718 | 394.3672 | 307.4437 | 288.3755 | 289.5292 | 253.1455 | 220.9439 | 148.9938
1089.6268 | 942.6268 | 477.0311 | 287.8177 | 394.5412 | 307.6065 | 288.5999 | 289.7905 | 253.3856 | 221.2486 | 149.2114
1090.6282 | 943.6282 | 476.8928 | 287.9854 | 394.6905 | 307.7828 | 288.8894 | 290.1547 | 253.6074 | 221.5467 | 149.4173
1091.6297 | 944.6297 | 476.8018 | 288.1347 | 394.7913 | 307.9475 | 289.1199 | 290.4827 | 253.8263 | 221.8883 | 149.5931
1092.6311 | 945.6311 | 476.7986 | 288.2815 | 394.8726 | 308.0721 | 289.3848 | 290.8103 | 254.0421 | 222.2023 | 149.8334
1093.6326 | 946.6326 | 476.6544 | 288.4422 | 395.0253 | 308.239 | 289.6327 | 291.0761 | 254.2605 | 222.5221 | 150.0336
1094.624 | 947.624 | 476.5755 | 288.5982 | 395.1207 | 308.4255 | 289.9495 | 291.2688 | 254.4604 | 222.8664 | 150.2317
1095.6254 | 948.6254 | 476.4039 | 288.7728 | 395.1298 | 308.5679 | 290.1418 | 291.6373 | 254.67 | 223.1985 | 150.4639
1096.6269 | 949.6269 | 476.4763 | 288.9059 | 395.2833 | 308.7278 | 290.363 | 292.003 | 254.8986 | 223.5155 | 150.6664
1097.6283 | 950.6283 | 476.5579 | 289.0687 | 395.4184 | 308.8704 | 290.627 | 292.3953 | 255.1514 | 223.8539 | 150.8617
1098.6298 | 951.6298 | 476.6013 | 289.2323 | 395.5402 | 309.0367 | 290.8664 | 292.7316 | 255.3978 | 224.1599 | 151.0934
1099.6312 | 952.6312 | 476.6873 | 289.3927 | 395.6518 | 309.1822 | 291.0189 | 293.1004 | 255.6239 | 224.4891 | 151.2854
1100.6326 | 953.6326 | 476.7854 | 289.5464 | 395.7718 | 309.3726 | 291.1882 | 293.4417 | 255.8365 | 224.8004 | 151.5045
1101.6241 | 954.6241 | 476.925 | 289.7184 | 395.8078 | 309.5182 | 291.5626 | 293.7235 | 256.0371 | 225.1224 | 151.7092
1102.6255 | 955.6255 | 476.9858 | 289.8591 | 395.9486 | 309.6589 | 291.7217 | 294.0509 | 256.2452 | 225.4557 | 151.9181
1103.6269 | 956.6269 | 477.0472 | 289.987 | 396.036 | 309.8102 | 292.1767 | 294.3609 | 256.4733 | 225.7861 | 152.1147
1104.6284 | 957.6284 | 477.1614 | 290.1589 | 396.1977 | 309.9814 | 292.6065 | 294.639 | 256.6733 | 226.1012 | 152.348
1105.6298 | 958.6298 | 477.1957 | 290.3095 | 396.3053 | 310.1213 | 292.8156 | 294.6627 | 256.8592 | 226.4426 | 152.5547
1106.6313 | 959.6313 | 477.2541 | 290.4853 | 396.4943 | 310.2888 | 292.9376 | 294.612 | 257.082 | 226.7943 | 152.7285
1107.6327 | 960.6327 | 477.4042 | 290.62 | 396.5431 | 310.4334 | 293.0636 | 294.9301 | 257.3301 | 227.1272 | 152.9708
1108.6241 | 961.6241 | 477.4288 | 290.7509 | 396.6623 | 310.5576 | 293.314 | 295.2852 | 257.5766 | 227.4527 | 153.158
1109.6256 | 962.6256 | 477.6567 | 290.906 | 396.7581 | 310.7231 | 293.5202 | 295.4387 | 257.825 | 227.7945 | 153.3443
1110.627 | 963.627 | 477.7558 | 291.0776 | 396.8655 | 310.8368 | 293.8038 | 295.5495 | 258.0662 | 228.1103 | 153.5714
1111.6284 | 964.6284 | 477.9387 | 291.2561 | 396.9363 | 311.039 | 294.1127 | 295.7131 | 258.2677 | 228.4179 | 153.7826
1112.6299 | 965.6299 | 478.0144 | 291.4197 | 397.0345 | 311.1601 | 293.9394 | 295.8497 | 258.4884 | 228.7148 | 154.0189
1113.6313 | 966.6313 | 478.1152 | 291.5523 | 397.2341 | 311.3289 | 293.9302 | 295.8541 | 258.7291 | 229.0213 | 154.1893
1114.6328 | 967.6328 | 478.0888 | 291.6997 | 397.3245 | 311.4736 | 294.2118 | 295.6921 | 258.9777 | 229.3036 | 154.3888
1115.6342 | 968.6342 | 478.2193 | 291.857 | 397.4349 | 311.6145 | 294.5563 | 295.9948 | 259.241 | 229.5869 | 154.5957
1116.6256 | 969.6256 | 478.2567 | 292.0311 | 397.5522 | 311.7704 | 295.0896 | 296.2672 | 259.5052 | 229.8727 | 154.8204
1117.6271 | 970.6271 | 478.2029 | 292.1829 | 397.7417 | 311.9193 | 295.4792 | 296.8336 | 259.7676 | 230.1575 | 155.0286
1118.6586 | 971.6586 | 478.1315 | 292.311 | 397.8893 | 312.0804 | 295.7355 | 297.1602 | 259.9938 | 230.4772 | 155.2354
1119.6299 | 972.6299 | 478.1589 | 292.4638 | 398.014 | 312.2124 | 295.7605 | 296.987 | 260.2181 | 230.7728 | 155.407
1120.6314 | 973.6314 | 478.1127 | 292.6143 | 398.0705 | 312.3396 | 295.8759 | 296.8866 | 260.4446 | 231.0859 | 155.6391
1121.6328 | 974.6328 | 478.159 | 292.7652 | 398.1493 | 312.5174 | 296.1169 | 297.5246 | 260.664 | 231.3677 | 155.9196
1122.6343 | 975.6343 | 478.2721 | 292.9129 | 398.3023 | 312.6788 | 296.6018 | 297.8342 | 260.9081 | 231.6923 | 156.1619
1123.6257 | 976.6257 | 478.413 | 293.0708 | 398.399 | 312.8113 | 296.937 | 298.2471 | 261.1383 | 232.019 | 156.3993
1124.6271 | 977.6271 | 478.4851 | 293.2386 | 398.4775 | 312.9684 | 297.3043 | 298.634 | 261.4038 | 232.3202 | 156.6454
1125.6286 | 978.6286 | 478.5862 | 293.3678 | 398.5579 | 313.1086 | 297.3733 | 299.2828 | 261.6667 | 232.6288 | 156.9079
1126.63 | 979.63 | 478.553 | 293.5128 | 398.7022 | 313.2423 | 297.4665 | 299.627 | 261.9897 | 232.9203 | 157.1706
1127.6315 | 980.6315 | 478.3913 | 293.6671 | 398.8444 | 313.4193 | 297.6942 | 299.7046 | 262.3265 | 233.2408 | 157.4127
1128.6329 | 981.6329 | 478.2691 | 293.7839 | 398.9065 | 313.5552 | 298.1126 | 300.0273 | 262.6489 | 233.5441 | 157.6342
1129.6243 | 982.6243 | 478.1925 | 293.9523 | 399.0263 | 313.7112 | 298.6587 | 300.5204 | 262.9026 | 233.8486 | 157.8404
1130.6258 | 983.6258 | 478.1676 | 294.0991 | 399.1696 | 313.8334 | 299.1945 | 300.6255 | 263.1508 | 234.1434 | 158.0658
1131.6272 | 984.6272 | 478.026 | 294.2439 | 399.353 | 313.971 | 299.4848 | 300.8499 | 263.3984 | 234.4228 | 158.2691
1132.6286 | 985.6286 | 477.7399 | 294.3912 | 399.3684 | 314.1193 | 299.606 | 301.0476 | 263.6572 | 234.7046 | 158.4815
1133.6301 | 986.6301 | 477.5293 | 294.5109 | 399.4536 | 314.2456 | 299.7488 | 301.2592 | 263.9256 | 235.0075 | 158.6492
1134.6315 | 987.6315 | 477.4587 | 294.625 | 399.5636 | 314.3851 | 299.8827 | 301.5406 | 264.186 | 235.326 | 158.8391
1135.633 | 988.633 | 477.4987 | 294.8316 | 399.6895 | 314.5421 | 300.13 | 301.5493 | 264.4648 | 235.6398 | 159.0332
1136.6244 | 989.6244 | 477.4505 | 295.0027 | 399.7959 | 314.6639 | 300.2065 | 301.5297 | 264.7288 | 235.898 | 159.2144
1137.6258 | 990.6258 | 477.3607 | 295.1265 | 399.9228 | 314.788 | 300.5716 | 301.6893 | 265.0027 | 236.2052 | 159.4009
1138.6273 | 991.6273 | 477.2934 | 295.2593 | 399.9819 | 314.932 | 300.986 | 301.9814 | 265.275 | 236.4913 | 159.6061
1139.6287 | 992.6287 | 477.1698 | 295.4043 | 400.1411 | 315.0677 | 301.211 | 302.1491 | 265.5175 | 236.8093 | 159.7785
1140.6301 | 993.6301 | 477.1831 | 295.5521 | 400.2104 | 315.2164 | 301.4337 | 302.3764 | 265.7823 | 237.1944 | 159.946
1141.6316 | 994.6316 | 477.1992 | 295.6951 | 400.3245 | 315.3371 | 301.5608 | 302.525 | 266.063 | 237.5803 | 160.1347
1142.633 | 995.633 | 477.2205 | 295.8316 | 400.4035 | 315.4786 | 301.9295 | 302.6592 | 266.284 | 237.9307 | 160.3382
1143.6245 | 996.6245 | 477.2181 | 296 | 400.5114 | 315.6104 | 302.2615 | 302.8374 | 266.4713 | 238.3013 | 160.5399
1144.6259 | 997.6259 | 477.1678 | 296.1408 | 400.6452 | 315.7415 | 302.6942 | 302.7952 | 266.6491 | 238.6837 | 160.7244
1145.6273 | 998.6273 | 477.1929 | 296.3009 | 400.7023 | 315.8759 | 302.9503 | 302.9426 | 266.8604 | 239.0507 | 160.9074
1146.6288 | 999.6288 | 477.2448 | 296.4528 | 400.8275 | 316.0038 | 303.3772 | 303.116 | 267.0566 | 239.4437 | 161.0521
1147.6302 | 1000.6302 | 477.2578 | 296.5992 | 400.9143 | 316.1337 | 303.5297 | 303.4115 | 267.2976 | 239.7889 | 161.2554
1148.6317 | 1001.6317 | 477.2534 | 296.7579 | 400.9347 | 316.2442 | 303.7032 | 303.4869 | 267.5004 | 240.1224 | 161.4062
1149.6331 | 1002.6331 | 477.3341 | 296.8995 | 401.1107 | 316.3718 | 303.9668 | 303.6742 | 267.6634 | 240.4728 | 161.6005
1150.6245 | 1003.6245 | 477.3882 | 297.0626 | 401.2024 | 316.5002 | 304.2084 | 303.9179 | 267.8949 | 240.8157 | 161.7676
1151.626 | 1004.626 | 477.322 | 297.1908 | 401.2751 | 316.6009 | 304.5354 | 304.1375 | 268.1599 | 241.1091 | 161.9787
1152.6274 | 1005.6274 | 477.293 | 297.3221 | 401.3068 | 316.7613 | 304.7976 | 304.3239 | 268.3799 | 241.3985 | 162.1422
1153.6288 | 1006.6288 | 477.3286 | 297.4933 | 401.4471 | 316.9134 | 304.9462 | 304.5398 | 268.547 | 241.7058 | 162.3006
1154.6303 | 1007.6303 | 477.3517 | 297.617 | 401.5727 | 317.0438 | 305.2342 | 304.756 | 268.6927 | 242.0132 | 162.4719
1155.6317 | 1008.6317 | 477.3595 | 297.7547 | 401.6844 | 317.1528 | 305.7136 | 305.0547 | 268.8905 | 242.3694 | 162.6185
1156.6332 | 1009.6332 | 477.3579 | 297.9006 | 401.7525 | 317.2683 | 305.9995 | 305.2628 | 269.1509 | 242.6155 | 162.8458
1157.6346 | 1010.6346 | 477.3744 | 298.0907 | 401.8114 | 317.4144 | 306.106 | 305.5381 | 269.4086 | 242.8166 | 162.9875
1158.626 | 1011.626 | 477.3868 | 298.2311 | 401.9711 | 317.5502 | 306.3471 | 305.8475 | 269.6945 | 242.9944 | 163.2007
1159.6275 | 1012.6275 | 477.6082 | 298.3797 | 402.1012 | 317.6623 | 306.6595 | 306.0803 | 269.9229 | 243.1465 | 163.3549
1160.6289 | 1013.6289 | 477.7689 | 298.5176 | 402.1605 | 317.7481 | 306.9293 | 306.2301 | 270.099 | 243.2774 | 163.5216
1161.6303 | 1014.6303 | 477.8756 | 298.6954 | 402.2605 | 317.9319 | 307.2745 | 306.4167 | 270.3712 | 243.3953 | 163.7337
1162.6318 | 1015.6318 | 477.9984 | 298.8235 | 402.3009 | 318.0481 | 307.4491 | 306.539 | 270.6239 | 243.5354 | 163.9012
1163.6332 | 1016.6332 | 478.1251 | 298.979 | 402.4836 | 318.2013 | 307.8424 | 306.7384 | 270.7901 | 243.6552 | 164.0944
1164.6347 | 1017.6347 | 478.2926 | 299.1161 | 402.6067 | 318.3439 | 308.1779 | 306.9207 | 270.9593 | 243.8146 | 164.2633
1165.6261 | 1018.6261 | 478.3676 | 299.2943 | 402.7029 | 318.4695 | 308.5495 | 306.9759 | 271.1287 | 243.953 | 164.456
1166.6275 | 1019.6275 | 478.3503 | 299.4257 | 402.7246 | 318.6049 | 308.9991 | 306.985 | 271.354 | 244.0984 | 164.6489
1167.629 | 1020.629 | 478.3964 | 299.5865 | 402.8536 | 318.72 | 309.2395 | 307.0999 | 271.5631 | 244.256 | 164.8261
1168.6304 | 1021.6304 | 478.4501 | 299.7098 | 402.9116 | 318.8471 | 309.4148 | 307.3258 | 271.7449 | 244.4385 | 164.9868
1169.6318 | 1022.6318 | 478.4545 | 299.8724 | 402.9331 | 318.992 | 309.6791 | 307.5586 | 271.9462 | 244.5856 | 165.1902
1170.6333 | 1023.6333 | 478.4604 | 299.9973 | 403.1192 | 319.1192 | 310.0066 | 307.736 | 272.1838 | 244.7463 | 165.3608
1171.6247 | 1024.6247 | 478.4046 | 300.1479 | 403.2068 | 319.2437 | 310.374 | 307.8615 | 272.5337 | 244.9134 | 165.5446
1172.6262 | 1025.6262 | 478.3843 | 300.3108 | 403.2505 | 319.3668 | 310.7665 | 307.8584 | 272.8158 | 245.0754 | 165.7201
1173.6276 | 1026.6276 | 478.3189 | 300.4582 | 403.3734 | 319.4807 | 311.1065 | 307.9191 | 273.003 | 245.2314 | 165.9408
1174.629 | 1027.629 | 478.1987 | 300.58 | 403.4693 | 319.6141 | 311.3396 | 308.099 | 273.1902 | 245.4139 | 166.1031
1175.6305 | 1028.6305 | 477.9968 | 300.7131 | 403.6013 | 319.7397 | 311.7667 | 308.257 | 273.364 | 245.5401 | 166.3073
1176.6319 | 1029.6319 | 477.7401 | 300.8558 | 403.6315 | 319.8607 | 312.2122 | 308.4657 | 273.5476 | 245.6744 | 166.4798
1177.6233 | 1030.6233 | 477.5168 | 300.9973 | 403.6798 | 319.9897 | 312.553 | 308.6582 | 273.7045 | 245.8094 | 166.6462
1178.6248 | 1031.6248 | 477.4783 | 301.1182 | 403.8475 | 320.1079 | 312.9646 | 308.7136 | 273.8358 | 245.9145 | 166.8688
1179.6262 | 1032.6262 | 477.5071 | 301.2688 | 404.0038 | 320.2129 | 313.3464 | 308.8175 | 273.9888 | 246.0458 | 167.0252
1180.6277 | 1033.6277 | 477.4789 | 301.4089 | 404.0945 | 320.3472 | 313.7467 | 309.0476 | 274.1274 | 246.1944 | 167.234
1181.6291 | 1034.6291 | 477.5238 | 301.542 | 404.1959 | 320.482 | 313.9927 | 309.2715 | 274.2905 | 246.375 | 167.4036
1182.6305 | 1035.6305 | 477.4592 | 301.6873 | 404.2482 | 320.5918 | 314.2748 | 309.5562 | 274.4265 | 246.5182 | 167.627
1183.632 | 1036.632 | 477.2905 | 301.8143 | 404.3252 | 320.689 | 314.5756 | 309.8754 | 274.5405 | 246.6957 | 167.7887
1184.6334 | 1037.6334 | 477.0874 | 301.982 | 404.4324 | 320.7919 | 314.9601 | 310.0992 | 274.7268 | 246.8135 | 167.9741
1185.6248 | 1038.6248 | 476.7845 | 302.1106 | 404.5144 | 320.9162 | 315.0376 | 310.3241 | 275.0692 | 246.9128 | 168.1588
1186.6263 | 1039.6263 | 476.6365 | 302.1862 | 404.5548 | 321.0386 | 315.3432 | 310.5403 | 275.3226 | 247.0147 | 168.3648
1187.6277 | 1040.6277 | 476.4408 | 302.3572 | 404.5773 | 321.1514 | 315.656 | 310.7361 | 275.4984 | 247.1515 | 168.5773
1188.6292 | 1041.6292 | 476.2328 | 302.5032 | 404.7339 | 321.2798 | 315.9401 | 310.988 | 275.6206 | 247.2822 | 168.7496
1189.6306 | 1042.6306 | 476.105 | 302.6242 | 404.8519 | 321.3955 | 316.2764 | 311.1638 | 275.8051 | 247.4543 | 168.9456
1190.632 | 1043.632 | 475.9187 | 302.7806 | 404.9162 | 321.4823 | 316.5825 | 311.3109 | 276.0104 | 247.5871 | 169.1373
1191.6335 | 1044.6335 | 475.7887 | 302.9102 | 405.0252 | 321.5832 | 316.7222 | 311.5501 | 276.1853 | 247.7399 | 169.3295
1192.6349 | 1045.6349 | 475.7926 | 303.0279 | 405.1962 | 321.6691 | 316.9136 | 311.6411 | 276.3245 | 247.8611 | 169.5381
1193.6264 | 1046.6264 | 475.8875 | 303.1763 | 405.201 | 321.791 | 317.3129 | 311.7188 | 276.5261 | 248.0371 | 169.7187
1194.6278 | 1047.6278 | 476.0129 | 303.3201 | 405.2754 | 321.9341 | 317.7689 | 311.7653 | 276.786 | 248.1961 | 169.9145
1195.6292 | 1048.6292 | 476.0439 | 303.4526 | 405.2471 | 322.0484 | 318.0616 | 311.9555 | 277.0245 | 248.3473 | 170.1267
1196.6307 | 1049.6307 | 476.16 | 303.5519 | 405.3101 | 322.1389 | 318.3964 | 312.2231 | 277.186 | 248.4699 | 170.3594
1197.6321 | 1050.6321 | 476.3455 | 303.7237 | 405.3489 | 322.2692 | 318.6405 | 312.2551 | 277.3371 | 248.6139 | 170.5526
1198.6336 | 1051.6336 | 476.5553 | 303.7999 | 405.4963 | 322.3942 | 318.6807 | 312.167 | 277.4996 | 248.7637 | 170.7775
1199.625 | 1052.625 | 476.7327 | 303.9813 | 405.7019 | 322.5035 | 318.9553 | 312.4269 | 277.6966 | 248.9462 | 170.9462
1200.6264 | 1053.6264 | 476.9483 | 304.0777 | 405.7729 | 322.6462 | 319.0937 | 312.8353 | 277.8989 | 249.1042 | 171.2035
1201.6279 | 1054.6279 | 477.22 | 304.2566 | 405.8244 | 322.7559 | 319.4168 | 313.2485 | 278.0678 | 249.2676 | 171.4325
1202.6293 | 1055.6293 | 477.4367 | 304.3863 | 405.9536 | 322.8674 | 319.8153 | 313.6268 | 278.2258 | 249.4819 | 171.6424
1203.6307 | 1056.6307 | 477.6892 | 304.5257 | 406.0527 | 322.9813 | 320.3697 | 313.8763 | 278.3602 | 249.6864 | 171.8273
1204.6322 | 1057.6322 | 477.8143 | 304.6813 | 406.1407 | 323.0985 | 320.6373 | 314.0886 | 278.5128 | 249.8619 | 172.0627
1205.6336 | 1058.6336 | 477.8011 | 304.7953 | 406.1463 | 323.1971 | 320.8894 | 314.426 | 278.7152 | 250.0526 | 172.3172
1206.7152 | 1059.7152 | 477.8954 | 304.9599 | 406.3005 | 323.3361 | 321.2716 | 314.4678 | 278.9044 | 250.2366 | 172.5569
1207.6265 | 1060.6265 | 477.9285 | 305.0966 | 406.4044 | 323.4474 | 321.6384 | 314.5898 | 279.0303 | 250.427 | 172.7351
1208.6279 | 1061.6279 | 477.8822 | 305.2518 | 406.5211 | 323.5417 | 321.8897 | 314.8584 | 279.1906 | 250.5885 | 172.9823
1209.6294 | 1062.6294 | 477.9974 | 305.3409 | 406.5646 | 323.6126 | 322.176 | 315.0889 | 279.2761 | 250.7588 | 173.2054
1210.6308 | 1063.6308 | 478.1684 | 305.4819 | 406.7312 | 323.7379 | 322.4697 | 315.1397 | 279.4651 | 250.9143 | 173.4267
1211.6322 | 1064.6322 | 478.3354 | 305.592 | 406.7759 | 323.8543 | 322.7052 | 315.1892 | 279.7202 | 251.0858 | 173.6546
1212.6337 | 1065.6337 | 478.365 | 305.7173 | 406.8334 | 323.9985 | 323.0504 | 315.34 | 280.0895 | 251.2439 | 173.856
1213.6351 | 1066.6351 | 478.4347 | 305.8467 | 406.9403 | 324.1187 | 323.6455 | 315.5981 | 280.4596 | 251.3987 | 174.1058
1214.6265 | 1067.6265 | 478.5263 | 305.9624 | 407.0111 | 324.2781 | 323.7964 | 315.7793 | 280.7185 | 251.57 | 174.3202
1215.628 | 1068.628 | 478.5301 | 306.0903 | 407.0271 | 324.3894 | 323.8937 | 315.8709 | 280.921 | 251.7501 | 174.5493
1216.6294 | 1069.6294 | 478.6108 | 306.233 | 407.1494 | 324.4893 | 324.3068 | 316.1734 | 281.1467 | 251.9396 | 174.7443
1217.6309 | 1070.6309 | 478.5495 | 306.3513 | 407.1835 | 324.5837 | 324.5686 | 316.4159 | 281.3739 | 252.1088 | 174.963
1218.6323 | 1071.6323 | 478.5823 | 306.4973 | 407.2402 | 324.6942 | 324.2195 | 316.5879 | 281.579 | 252.2951 | 175.1846
1219.6337 | 1072.6337 | 478.5921 | 306.603 | 407.3924 | 324.8435 | 324.6825 | 316.7998 | 281.7436 | 252.4837 | 175.3941
1220.6252 | 1073.6252 | 478.6068 | 306.7225 | 407.4711 | 324.9541 | 325.2298 | 317.1457 | 281.9099 | 252.6674 | 175.6344
1221.6567 | 1074.6567 | 478.5937 | 306.8527 | 407.5732 | 325.0397 | 325.5995 | 317.4077 | 282.1065 | 252.8493 | 175.8651
1222.6281 | 1075.6281 | 478.5774 | 306.9726 | 407.662 | 325.1159 | 325.867 | 317.7643 | 282.2927 | 253.0011 | 176.0922
1223.6295 | 1076.6295 | 478.7062 | 307.0775 | 407.7893 | 325.2082 | 325.8734 | 318.107 | 282.4542 | 253.2011 | 176.2866
1224.6309 | 1077.6309 | 478.7997 | 307.2048 | 407.9504 | 325.3525 | 326.2303 | 318.3828 | 282.6185 | 253.3703 | 176.523
1225.6324 | 1078.6324 | 478.8054 | 307.3046 | 407.9814 | 325.4868 | 326.5339 | 318.8494 | 282.8835 | 253.5189 | 176.7435
1226.6338 | 1079.6338 | 478.7891 | 307.4333 | 408.0263 | 325.6195 | 326.7619 | 319.1193 | 283.1338 | 253.6684 | 176.9882
1227.6252 | 1080.6252 | 478.8559 | 307.5548 | 408.1607 | 325.7575 | 327.0629 | 319.5117 | 283.2473 | 253.8495 | 177.229
1228.6267 | 1081.6267 | 478.9658 | 307.6681 | 408.2613 | 325.8713 | 327.3226 | 319.5361 | 283.3657 | 254.0596 | 177.4434
1229.6281 | 1082.6281 | 479.0102 | 307.7849 | 408.282 | 325.9515 | 327.6125 | 319.6029 | 283.399 | 254.2703 | 177.6968
1230.6296 | 1083.6296 | 479.0171 | 307.9187 | 408.3683 | 326.0633 | 328.0882 | 319.8388 | 283.3675 | 254.4709 | 177.9036
1231.631 | 1084.631 | 478.8324 | 308.0458 | 408.4452 | 326.1561 | 328.0808 | 320.1157 | 283.4755 | 254.6995 | 178.1078
1232.6324 | 1085.6324 | 478.7573 | 308.1417 | 408.4793 | 326.3024 | 328.0938 | 320.3356 | 283.7362 | 254.8588 | 178.3879
1233.6339 | 1086.6339 | 478.6394 | 308.2529 | 408.5798 | 326.4008 | 328.3909 | 320.2345 | 284.1427 | 255.0532 | 178.5877
1234.6253 | 1087.6253 | 478.5547 | 308.3828 | 408.7433 | 326.4498 | 328.6375 | 320.2882 | 284.3933 | 255.2077 | 178.8295
1235.6267 | 1088.6267 | 478.4331 | 308.4636 | 408.8609 | 326.5963 | 328.9143 | 320.3307 | 284.5891 | 255.3843 | 179.0425
1236.6282 | 1089.6282 | 478.3752 | 308.6023 | 408.8748 | 326.7516 | 329.2363 | 320.5654 | 284.7245 | 255.5669 | 179.3242
1237.6296 | 1090.6296 | 478.429 | 308.72 | 408.9556 | 326.8536 | 329.6864 | 320.6697 | 284.8633 | 255.7512 | 179.5545
1238.6311 | 1091.6311 | 478.3876 | 308.8391 | 408.9571 | 326.9939 | 329.7323 | 320.7049 | 284.9837 | 255.961 | 179.7647
1239.6325 | 1092.6325 | 478.2073 | 308.9478 | 409.0762 | 327.1252 | 329.8343 | 321.1211 | 285.1482 | 256.1357 | 179.9997
1240.6339 | 1093.6339 | 478.0419 | 309.0592 | 409.1219 | 327.2414 | 329.9714 | 321.3522 | 285.3574 | 256.3072 | 180.2472
1241.6354 | 1094.6354 | 478.0314 | 309.1704 | 409.1009 | 327.3378 | 330.2995 | 321.4636 | 285.5732 | 256.4884 | 180.4839
1242.6268 | 1095.6268 | 477.9033 | 309.2738 | 409.2522 | 327.4632 | 330.6251 | 321.7316 | 285.7957 | 256.6529 | 180.6974
1243.6282 | 1096.6282 | 477.8331 | 309.366 | 409.3172 | 327.5514 | 331.018 | 321.8297 | 285.9143 | 256.8486 | 180.9224
1244.6297 | 1097.6297 | 477.6589 | 309.4986 | 409.3586 | 327.6497 | 331.4242 | 321.8309 | 285.9816 | 257.0827 | 181.156
1245.6311 | 1098.6311 | 477.6451 | 309.5783 | 409.462 | 327.7483 | 331.6816 | 321.7029 | 286.0445 | 257.3226 | 181.3941
1246.6326 | 1099.6326 | 477.5849 | 309.6976 | 409.5353 | 327.9028 | 331.9469 | 321.8205 | 286.1257 | 257.5026 | 181.6203
1247.634 | 1100.634 | 477.589 | 309.8211 | 409.7333 | 328.0171 | 332.2729 | 322.1452 | 286.2771 | 257.6247 | 181.8814
1248.6354 | 1101.6354 | 477.6649 | 309.9383 | 409.7758 | 328.0862 | 332.5238 | 322.4661 | 286.5145 | 257.821 | 182.0943
1249.6269 | 1102.6269 | 477.8087 | 310.048 | 409.7684 | 328.1866 | 332.7869 | 322.6581 | 286.723 | 258.0997 | 182.3322
1250.6283 | 1103.6283 | 477.8537 | 310.154 | 409.7921 | 328.2722 | 333.0233 | 322.7598 | 286.9618 | 258.527 | 182.5956
1251.6298 | 1104.6298 | 477.8405 | 310.2714 | 409.9015 | 328.3885 | 333.192 | 322.7831 | 287.1816 | 258.6777 | 182.7832
1252.6312 | 1105.6312 | 477.799 | 310.3524 | 409.9862 | 328.4941 | 333.5019 | 322.9656 | 287.3562 | 258.8386 | 183.0247
1253.6326 | 1106.6326 | 477.7198 | 310.5111 | 410.1013 | 328.562 | 333.6888 | 323.0366 | 287.5588 | 259.0676 | 183.2796
1254.6341 | 1107.6341 | 477.6821 | 310.637 | 410.1455 | 328.6651 | 333.8436 | 323.2108 | 287.7704 | 259.1944 | 183.4944
1255.6255 | 1108.6255 | 477.7186 | 310.7582 | 410.207 | 328.7744 | 334.0258 | 323.4806 | 287.9496 | 259.3069 | 183.6829
1256.6269 | 1109.6269 | 477.8104 | 310.832 | 410.3083 | 328.9178 | 334.1996 | 323.7229 | 288.1181 | 259.3968 | 183.948
1257.6284 | 1110.6284 | 477.8124 | 310.9492 | 410.3577 | 329.0563 | 334.384 | 323.7785 | 288.2863 | 259.5192 | 184.1594
1258.6298 | 1111.6298 | 477.8161 | 311.0844 | 410.3847 | 329.1515 | 334.6263 | 323.8338 | 288.5848 | 259.6613 | 184.3763
1259.6313 | 1112.6313 | 477.7322 | 311.1628 | 410.3671 | 329.2941 | 334.8519 | 323.8317 | 288.7974 | 259.7874 | 184.6324
1260.6327 | 1113.6327 | 477.6812 | 311.3051 | 410.4464 | 329.3823 | 335.158 | 323.9717 | 288.8617 | 259.9304 | 184.8308
1261.6241 | 1114.6241 | 477.7543 | 311.4238 | 410.5379 | 329.4629 | 335.3523 | 324.0188 | 288.8101 | 260.0655 | 185.036
1262.6256 | 1115.6256 | 477.7636 | 311.544 | 410.5872 | 329.5868 | 335.5258 | 324.2591 | 288.9021 | 260.1921 | 185.2595
1263.627 | 1116.627 | 477.8355 | 311.6543 | 410.7589 | 329.7058 | 335.7087 | 324.3215 | 289.0949 | 260.3242 | 185.4742
1264.6284 | 1117.6284 | 477.8407 | 311.7603 | 410.822 | 329.8181 | 335.9262 | 324.5325 | 289.3579 | 260.4778 | 185.7092
1265.6299 | 1118.6299 | 477.8494 | 311.868 | 410.893 | 329.9163 | 336.2606 | 324.6383 | 289.7014 | 260.6705 | 185.9264
1266.6313 | 1119.6313 | 477.9013 | 311.979 | 411.0484 | 330.0142 | 336.5448 | 324.6325 | 289.9098 | 260.8469 | 186.1046
1267.6328 | 1120.6328 | 478.0075 | 312.0842 | 411.046 | 330.1203 | 336.6774 | 324.78 | 289.9707 | 260.9931 | 186.339
1268.6242 | 1121.6242 | 478.0074 | 312.2058 | 411.1146 | 330.2227 | 336.8848 | 324.9309 | 290.0596 | 261.1455 | 186.5355
1269.6256 | 1122.6256 | 477.9386 | 312.3249 | 411.1707 | 330.3423 | 337.087 | 325.0968 | 290.1283 | 261.2845 | 186.7607
1270.6271 | 1123.6271 | 477.8817 | 312.432 | 411.2614 | 330.4739 | 336.9771 | 325.1963 | 290.2214 | 261.4199 | 186.9527
1271.6285 | 1124.6285 | 477.8646 | 312.5371 | 411.3473 | 330.5663 | 337.0844 | 325.3832 | 290.431 | 261.5477 | 187.1537
1272.63 | 1125.63 | 477.8972 | 312.648 | 411.3971 | 330.6841 | 337.1959 | 325.4325 | 290.7326 | 261.6636 | 187.3416
1273.6314 | 1126.6314 | 477.9748 | 312.75 | 411.4883 | 330.7686 | 337.4737 | 325.596 | 291.1267 | 261.7994 | 187.5547
1274.6328 | 1127.6328 | 478.03 | 312.8636 | 411.6513 | 330.8903 | 337.7622 | 325.7911 | 291.4064 | 261.9004 | 187.8086
1275.6343 | 1128.6343 | 477.9881 | 312.9661 | 411.6626 | 331.0134 | 338.1854 | 325.923 | 291.3543 | 262.0431 | 187.9909
1276.6357 | 1129.6357 | 477.993 | 313.0839 | 411.7722 | 331.1059 | 338.3958 | 325.9684 | 291.4198 | 262.1702 | 188.1906
1277.6271 | 1130.6271 | 478.1708 | 313.1833 | 411.7913 | 331.2296 | 338.7068 | 325.9919 | 291.7166 | 262.2882 | 188.4144
1278.6286 | 1131.6286 | 478.107 | 313.2867 | 411.8632 | 331.3272 | 338.4768 | 326.0667 | 291.9969 | 262.4434 | 188.6198
1279.63 | 1132.63 | 478.0501 | 313.403 | 411.9395 | 331.441 | 338.5652 | 326.1157 | 292.2832 | 262.5874 | 188.8454
1280.6315 | 1133.6315 | 478.0527 | 313.4943 | 412.0113 | 331.5322 | 338.2857 | 326.2008 | 292.5328 | 262.7297 | 189.0581
1281.6329 | 1134.6329 | 478.062 | 313.5623 | 412.1067 | 331.6655 | 338.4083 | 326.3393 | 292.8404 | 262.8708 | 189.2526
1282.6243 | 1135.6243 | 478.0948 | 313.6528 | 412.1438 | 331.7709 | 338.7498 | 326.528 | 293.0038 | 262.9901 | 189.4733
1283.6258 | 1136.6258 | 478.1622 | 313.824 | 412.2829 | 331.8788 | 339.12 | 326.7102 | 293.1795 | 263.1264 | 189.6884
1284.6272 | 1137.6272 | 478.3035 | 313.9385 | 412.3392 | 331.9767 | 339.4238 | 326.9126 | 293.2463 | 263.2508 | 189.9146
1285.6286 | 1138.6286 | 478.2151 | 314.0275 | 412.4112 | 332.0589 | 339.7262 | 326.9995 | 293.3863 | 263.4162 | 190.1172
1286.6301 | 1139.6301 | 478.0343 | 314.1557 | 412.3764 | 332.1503 | 339.9163 | 327.102 | 293.5638 | 263.5663 | 190.3162
1287.6315 | 1140.6315 | 477.8668 | 314.271 | 412.3931 | 332.2484 | 340.2876 | 327.3102 | 293.6564 | 263.7006 | 190.5279
1288.633 | 1141.633 | 477.8509 | 314.354 | 412.492 | 332.3793 | 340.3791 | 327.4165 | 293.7816 | 263.8822 | 190.7193
1289.6344 | 1142.6344 | 477.754 | 314.4523 | 412.6104 | 332.4782 | 340.5688 | 327.6757 | 294.0703 | 264.0715 | 190.9475
1290.6258 | 1143.6258 | 477.6108 | 314.5084 | 412.7004 | 332.5848 | 340.8437 | 327.7949 | 294.3717 | 264.2712 | 191.1267
1291.6273 | 1144.6273 | 477.5314 | 314.657 | 412.6902 | 332.6612 | 340.9156 | 327.9671 | 294.5924 | 264.4529 | 191.3669
1292.6287 | 1145.6287 | 477.4461 | 314.7724 | 412.7444 | 332.7813 | 341.0607 | 327.9126 | 294.764 | 264.6255 | 191.5735
1293.6301 | 1146.6301 | 477.3569 | 314.8653 | 412.8282 | 332.8695 | 341.3305 | 327.9376 | 295.0072 | 264.7971 | 191.7798
1294.6316 | 1147.6316 | 477.2999 | 314.9596 | 412.6937 | 332.9881 | 341.6201 | 328.164 | 295.208 | 264.9557 | 192.0085
1295.633 | 1148.633 | 477.3273 | 315.0786 | 412.8251 | 333.0741 | 341.7722 | 328.2404 | 295.5981 | 265.1219 | 192.2014
1296.6345 | 1149.6345 | 477.24 | 315.1354 | 412.9922 | 333.1716 | 342.0215 | 328.4524 | 295.861 | 265.2652 | 192.4572
1297.6359 | 1150.6359 | 477.198 | 315.2612 | 413.0764 | 333.281 | 342.2312 | 328.5438 | 295.7071 | 265.4388 | 192.6615
1298.6474 | 1151.6474 | 477.1512 | 315.3669 | 413.0271 | 333.3813 | 342.5025 | 328.6743 | 295.7565 | 265.5945 | 192.9086
1299.6288 | 1152.6288 | 477.1684 | 315.5198 | 413.1702 | 333.4677 | 342.7519 | 328.9801 | 295.9929 | 265.7462 | 193.0852
1300.6302 | 1153.6302 | 477.0497 | 315.5991 | 413.2048 | 333.5565 | 342.9174 | 329.1427 | 296.303 | 265.8816 | 193.3346
1301.6317 | 1154.6317 | 476.9237 | 315.7042 | 413.3495 | 333.6773 | 343.1206 | 329.251 | 296.5388 | 266.0215 | 193.5209
1302.6331 | 1155.6331 | 476.8301 | 315.7928 | 413.342 | 333.7737 | 343.2978 | 329.2815 | 296.6734 | 266.1661 | 193.7363
1303.6245 | 1156.6245 | 476.7276 | 315.8592 | 413.3021 | 333.8354 | 343.4933 | 329.4364 | 296.8434 | 266.2972 | 193.972
1304.626 | 1157.626 | 476.7077 | 316.023 | 413.3675 | 333.9721 | 343.5212 | 329.7212 | 297.1669 | 266.4565 | 194.1555
1305.6274 | 1158.6274 | 476.6538 | 316.0919 | 413.4498 | 334.0903 | 343.5724 | 330.0411 | 297.2689 | 266.6017 | 194.3967
1306.6288 | 1159.6288 | 476.572 | 316.2184 | 413.5647 | 334.2185 | 343.5668 | 330.1634 | 297.5241 | 266.7446 | 194.5803
1307.6303 | 1160.6303 | 476.5858 | 316.3066 | 413.666 | 334.3338 | 343.7342 | 330.4523 | 297.6523 | 266.9117 | 194.8133
1308.6317 | 1161.6317 | 476.6032 | 316.3746 | 413.6967 | 334.4219 | 343.9384 | 330.6504 | 297.755 | 267.102 | 194.9747
1309.6332 | 1162.6332 | 476.716 | 316.4957 | 413.7702 | 334.5148 | 344.1753 | 330.772 | 298.0524 | 267.2863 | 195.2027
1310.6246 | 1163.6246 | 476.6947 | 316.6235 | 413.9224 | 334.6122 | 344.302 | 330.8855 | 298.4338 | 267.4985 | 195.3608
1311.626 | 1164.626 | 476.7457 | 316.7169 | 413.9349 | 334.6996 | 344.5796 | 330.9187 | 298.6282 | 267.6777 | 195.5561
1312.6275 | 1165.6275 | 476.6983 | 316.8272 | 413.9908 | 334.7977 | 344.8291 | 330.9772 | 298.9128 | 267.882 | 195.7427
1313.6289 | 1166.6289 | 476.753 | 316.935 | 414.0074 | 334.8962 | 344.9736 | 331.1376 | 299.0432 | 268.0883 | 195.9491
1314.6303 | 1167.6303 | 476.7798 | 317.0211 | 414.1529 | 334.9738 | 345.039 | 331.3394 | 299.1378 | 268.2537 | 196.1643
1315.6318 | 1168.6318 | 476.8234 | 317.1251 | 414.2139 | 335.0743 | 345.1817 | 331.3761 | 299.223 | 268.4386 | 196.3006
1316.6332 | 1169.6332 | 476.8722 | 317.2062 | 414.2642 | 335.1718 | 345.2371 | 331.5499 | 299.2755 | 268.6035 | 196.5306
1317.6347 | 1170.6347 | 476.8645 | 317.3525 | 414.3163 | 335.3122 | 345.4143 | 331.8659 | 299.4025 | 268.7687 | 196.729
1318.6261 | 1171.6261 | 476.8744 | 317.461 | 414.2905 | 335.4022 | 345.6003 | 332.1637 | 299.4917 | 268.9256 | 196.9314
1319.6275 | 1172.6275 | 476.9074 | 317.5642 | 414.3922 | 335.4951 | 345.7552 | 332.1471 | 299.4773 | 269.0817 | 197.1332
1320.629 | 1173.629 | 476.9529 | 317.6743 | 414.3441 | 335.5578 | 345.9804 | 332.1121 | 299.7195 | 269.2317 | 197.324
1321.6304 | 1174.6304 | 476.9314 | 317.7482 | 414.4645 | 335.6913 | 346.0535 | 332.1773 | 300.0165 | 269.3468 | 197.5334
1322.6319 | 1175.6319 | 476.88 | 317.8952 | 414.6551 | 335.789 | 345.9882 | 332.4424 | 300.4356 | 269.444 | 197.7254
1323.6333 | 1176.6333 | 476.8431 | 318.0018 | 414.659 | 335.8835 | 346.2251 | 332.5167 | 300.6539 | 269.5541 | 197.9096
1324.6247 | 1177.6247 | 476.8118 | 318.1115 | 414.621 | 336.0012 | 346.1517 | 332.5764 | 300.8197 | 269.6231 | 198.1277
1325.6262 | 1178.6262 | 476.7892 | 318.1678 | 414.6902 | 336.0883 | 346.3254 | 332.7001 | 300.916 | 269.7451 | 198.3134
1326.6276 | 1179.6276 | 476.7891 | 318.276 | 414.7654 | 336.1941 | 346.5086 | 332.9782 | 301.0173 | 269.8682 | 198.4761
1327.629 | 1180.629 | 476.8551 | 318.3529 | 414.9584 | 336.2942 | 346.5979 | 333.3189 | 301.1435 | 269.9796 | 198.717
1328.6305 | 1181.6305 | 476.8098 | 318.4875 | 414.97 | 336.4107 | 346.6289 | 333.4975 | 301.3607 | 270.1031 | 198.8732
1329.6319 | 1182.6319 | 476.7485 | 318.5642 | 415.0981 | 336.4995 | 346.7469 | 333.6534 | 301.4823 | 270.208 | 199.0924
1330.6334 | 1183.6334 | 476.7598 | 318.6647 | 415.1337 | 336.6197 | 346.854 | 333.7835 | 301.8698 | 270.3456 | 199.2674
1331.6348 | 1184.6348 | 476.6832 | 318.7691 | 415.1725 | 336.6955 | 347.0494 | 333.8661 | 302.1013 | 270.4835 | 199.4658
1332.6262 | 1185.6262 | 476.7572 | 318.9061 | 415.1771 | 336.8026 | 347.1941 | 334.0091 | 302.1228 | 270.5894 | 199.6615
1333.6277 | 1186.6277 | 476.8203 | 318.9768 | 415.291 | 336.9009 | 347.4213 | 334.1857 | 302.1209 | 270.6674 | 199.8164
1334.6291 | 1187.6291 | 476.7925 | 319.0783 | 415.4126 | 336.9966 | 347.6255 | 334.271 | 302.293 | 270.7773 | 200.0559
1335.6305 | 1188.6305 | 476.8169 | 319.2105 | 415.3643 | 337.0825 | 347.8328 | 334.2693 | 302.7065 | 270.9261 | 200.2072
1336.632 | 1189.632 | 476.9114 | 319.2647 | 415.517 | 337.1828 | 348.0359 | 334.3831 | 302.8153 | 271.1357 | 200.4279
1337.6334 | 1190.6334 | 476.9379 | 319.3452 | 415.5215 | 337.2784 | 348.1736 | 334.3198 | 302.9562 | 271.3167 | 200.5887
1338.6349 | 1191.6349 | 476.9885 | 319.4596 | 415.4945 | 337.332 | 348.3473 | 334.3557 | 303.0863 | 271.4642 | 200.8081
1339.6263 | 1192.6263 | 477.0688 | 319.5975 | 415.5401 | 337.4435 | 348.4788 | 334.4676 | 303.3123 | 271.6237 | 200.9674
1340.6277 | 1193.6277 | 477.1804 | 319.677 | 415.6406 | 337.5182 | 348.7396 | 334.3757 | 303.5135 | 271.7879 | 201.1637
1341.6292 | 1194.6292 | 477.2703 | 319.7993 | 415.7484 | 337.5876 | 348.9874 | 334.528 | 303.6735 | 271.9576 | 201.3528
1342.6306 | 1195.6306 | 477.1859 | 319.8933 | 415.7455 | 337.7021 | 349.1073 | 334.6597 | 303.8771 | 272.1004 | 201.523
1343.632 | 1196.632 | 477.1569 | 319.9949 | 415.7653 | 337.7936 | 348.8813 | 334.7809 | 304.0607 | 272.2458 | 201.724
1344.6335 | 1197.6335 | 477.213 | 320.107 | 415.8942 | 337.9001 | 349.008 | 334.7099 | 304.296 | 272.3863 | 201.8927
1345.6249 | 1198.6249 | 477.2637 | 320.1712 | 415.8917 | 337.9817 | 349.3189 | 334.7728 | 304.5061 | 272.5042 | 202.1254
1346.6264 | 1199.6264 | 477.2555 | 320.3229 | 415.9974 | 338.0918 | 349.5258 | 334.7743 | 304.6499 | 272.6733 | 202.2734
1347.6278 | 1200.6278 | 477.265 | 320.3861 | 416.1311 | 338.1361 | 349.7935 | 334.7212 | 304.9079 | 272.8047 | 202.4898
1348.6292 | 1201.6292 | 477.3011 | 320.5252 | 416.1771 | 338.2609 | 349.9167 | 334.9109 | 305.1117 | 272.9478 | 202.6526
1349.6307 | 1202.6307 | 477.2389 | 320.601 | 416.2442 | 338.3167 | 350.0546 | 335.0038 | 305.3644 | 273.0868 | 202.8548
1350.6321 | 1203.6321 | 477.2639 | 320.6986 | 416.2983 | 338.4082 | 350.2128 | 335.139 | 305.669 | 273.2582 | 203.0369
1351.6235 | 1204.6235 | 477.2102 | 320.7957 | 416.3428 | 338.4984 | 350.4851 | 335.127 | 305.8901 | 273.4315 | 203.2062
1352.625 | 1205.625 | 477.1447 | 320.8949 | 416.4023 | 338.6101 | 350.6665 | 335.2364 | 306.166 | 273.5982 | 203.3963
1353.6264 | 1206.6264 | 477.0664 | 320.997 | 416.3933 | 338.6715 | 350.6037 | 335.3154 | 306.3408 | 273.7526 | 203.5687
1354.6279 | 1207.6279 | 477.0102 | 321.0737 | 416.466 | 338.7439 | 350.8465 | 335.2877 | 306.481 | 273.9273 | 203.7455
1355.6293 | 1208.6293 | 476.9898 | 321.1764 | 416.5117 | 338.8428 | 351.0362 | 335.6627 | 306.6104 | 274.0997 | 203.9239
1356.6307 | 1209.6307 | 477.0181 | 321.2195 | 416.5792 | 338.9319 | 351.281 | 335.9672 | 306.693 | 274.2674 | 204.1518
1357.6322 | 1210.6322 | 477.1812 | 321.3627 | 416.682 | 339.0247 | 351.4416 | 336.2464 | 306.9198 | 274.4618 | 204.2704
1358.6336 | 1211.6336 | 477.1505 | 321.4727 | 416.742 | 339.0913 | 351.6999 | 336.6328 | 307.0114 | 274.6194 | 204.4637
1359.625 | 1212.625 | 477.0951 | 321.6017 | 416.7868 | 339.1768 | 351.9284 | 336.9695 | 307.1393 | 274.7763 | 204.6776
1360.6265 | 1213.6265 | 477.0733 | 321.6693 | 416.8766 | 339.2777 | 352.1019 | 337.1197 | 307.4219 | 274.9351 | 204.8782
1361.6279 | 1214.6279 | 477.0433 | 321.7687 | 416.9293 | 339.376 | 352.3426 | 337.1445 | 307.7683 | 275.0896 | 205.0552
1362.6294 | 1215.6294 | 477.0194 | 321.8736 | 416.9939 | 339.4725 | 352.4979 | 337.4288 | 307.8967 | 275.253 | 205.2289
1363.6308 | 1216.6308 | 477.0198 | 321.9839 | 416.8768 | 339.5463 | 352.7146 | 337.7409 | 308.1258 | 275.3777 | 205.4265
1364.6322 | 1217.6322 | 476.9677 | 322.0242 | 416.7824 | 339.625 | 352.8862 | 338.0698 | 308.5172 | 275.5496 | 205.5802
1365.6337 | 1218.6337 | 476.8739 | 322.1102 | 416.9284 | 339.671 | 353.0522 | 338.368 | 308.706 | 275.7208 | 205.7828
1366.6251 | 1219.6251 | 476.8234 | 322.2633 | 417.0504 | 339.7532 | 353.2271 | 338.6021 | 308.8211 | 275.9387 | 205.9535
1367.6266 | 1220.6266 | 476.7367 | 322.2932 | 417.1635 | 339.7961 | 353.4605 | 338.93 | 308.9438 | 276.152 | 206.1203
1368.628 | 1221.628 | 476.7149 | 322.4343 | 417.1996 | 339.9075 | 353.5774 | 339.1785 | 309.1323 | 276.3785 | 206.2651
1369.6294 | 1222.6294 | 476.7015 | 322.5303 | 417.2335 | 340.0151 | 353.6565 | 339.3679 | 309.3931 | 276.5398 | 206.4922
1370.6309 | 1223.6309 | 476.6349 | 322.5966 | 417.3354 | 340.1068 | 353.7495 | 339.5074 | 309.7474 | 276.7383 | 206.6667
1371.6323 | 1224.6323 | 476.6151 | 322.704 | 417.3243 | 340.15 | 353.9217 | 339.7593 | 310.01 | 276.8996 | 206.8488
1372.6338 | 1225.6338 | 476.6448 | 322.8145 | 417.4278 | 340.2023 | 354.0484 | 339.9321 | 310.1857 | 277.0696 | 207.0008
1373.6352 | 1226.6352 | 476.628 | 322.9474 | 417.3825 | 340.319 | 354.1492 | 340.1089 | 310.3442 | 277.2013 | 207.186
1374.6266 | 1227.6266 | 476.6252 | 323.0313 | 417.5218 | 340.4203 | 354.2721 | 340.4274 | 310.5028 | 277.3752 | 207.3689
1375.6281 | 1228.6281 | 476.5602 | 323.0863 | 417.5528 | 340.4911 | 354.3245 | 340.5636 | 310.5827 | 277.5255 | 207.5321
1376.6295 | 1229.6295 | 476.734 | 323.2139 | 417.5411 | 340.5757 | 354.4335 | 340.8086 | 310.6262 | 277.6847 | 207.7309
1377.6309 | 1230.6309 | 476.887 | 323.3384 | 417.5928 | 340.6549 | 354.52 | 340.904 | 310.7429 | 277.8415 | 207.9008
1378.6324 | 1231.6324 | 476.8897 | 323.411 | 417.7685 | 340.72 | 354.7365 | 341.1052 | 310.9703 | 278.0055 | 208.0811
1379.6338 | 1232.6338 | 476.9265 | 323.5693 | 417.6989 | 340.7995 | 354.9054 | 341.3011 | 311.1729 | 278.1474 | 208.2671
1380.6353 | 1233.6353 | 476.9967 | 323.6096 | 417.8586 | 340.8891 | 354.9712 | 341.672 | 311.4397 | 278.3028 | 208.4495
1381.6267 | 1234.6267 | 477.0427 | 323.7241 | 417.8932 | 340.9472 | 355.0575 | 342.0001 | 311.8339 | 278.428 | 208.6458
1382.6281 | 1235.6281 | 477.0717 | 323.7894 | 417.9208 | 341.0572 | 355.2617 | 342.2751 | 312.0157 | 278.5709 | 208.8111
1383.6296 | 1236.6296 | 477.1244 | 323.9073 | 417.9631 | 341.1162 | 355.482 | 342.4216 | 312.0746 | 278.6999 | 209.0124
1384.631 | 1237.631 | 477.185 | 323.9589 | 418.0482 | 341.1929 | 355.6627 | 342.6471 | 312.1482 | 278.871 | 209.156
1385.6324 | 1238.6324 | 477.1668 | 324.0473 | 418.1031 | 341.2711 | 355.8208 | 342.9606 | 312.5334 | 279.0403 | 209.3214
1386.6439 | 1239.6439 | 477.2089 | 324.1526 | 418.1574 | 341.3275 | 355.9405 | 343.0911 | 312.7045 | 279.1931 | 209.5262
1387.6253 | 1240.6253 | 477.231 | 324.2595 | 418.22 | 341.4232 | 356.1281 | 343.0995 | 312.8633 | 279.3735 | 209.6977
1388.6267 | 1241.6267 | 477.2962 | 324.4017 | 418.2691 | 341.5395 | 356.3253 | 343.3082 | 313.0712 | 279.5298 | 209.8919
1389.6282 | 1242.6282 | 477.2858 | 324.4734 | 418.3609 | 341.5699 | 356.3954 | 343.4899 | 313.2957 | 279.6994 | 210.0445
1390.6296 | 1243.6296 | 477.2658 | 324.5696 | 418.4318 | 341.6337 | 356.4659 | 343.7209 | 313.4728 | 279.8562 | 210.2077
1391.6311 | 1244.6311 | 477.2968 | 324.6331 | 418.5137 | 341.7242 | 356.4911 | 343.841 | 313.6537 | 279.9903 | 210.4033
1392.6325 | 1245.6325 | 477.3989 | 324.7806 | 418.5439 | 341.8079 | 356.6505 | 344.0362 | 313.7816 | 280.1267 | 210.6012
1393.6239 | 1246.6239 | 477.4406 | 324.8508 | 418.5946 | 341.8506 | 356.8496 | 344.2678 | 313.9049 | 280.292 | 210.7752
1394.6254 | 1247.6254 | 477.398 | 324.9744 | 418.6408 | 341.957 | 357.0421 | 344.3689 | 314.0818 | 280.4418 | 210.9523
1395.6268 | 1248.6268 | 477.4646 | 325.0463 | 418.5595 | 342.0492 | 357.1841 | 344.4571 | 314.2704 | 280.5977 | 211.1361
1396.6283 | 1249.6283 | 477.4774 | 325.1382 | 418.6605 | 342.0857 | 357.3713 | 344.7199 | 314.4846 | 280.7371 | 211.281
1397.6297 | 1250.6297 | 477.3938 | 325.2098 | 418.6948 | 342.1979 | 357.534 | 344.6338 | 314.714 | 280.88 | 211.4685
1398.6311 | 1251.6311 | 477.3772 | 325.3672 | 418.7438 | 342.2477 | 357.6582 | 344.821 | 314.9924 | 281.0417 | 211.6413
1399.6326 | 1252.6326 | 477.348 | 325.4385 | 418.828 | 342.3474 | 357.8438 | 345.1051 | 315.4079 | 281.2385 | 211.7912
1400.624 | 1253.624 | 477.4186 | 325.5259 | 418.8334 | 342.4122 | 358.0162 | 345.3466 | 315.7831 | 281.4221 | 211.9851
1401.6254 | 1254.6254 | 477.4568 | 325.6248 | 418.9163 | 342.4245 | 358.2199 | 345.6701 | 316.1182 | 281.588 | 212.156
1402.6269 | 1255.6269 | 477.5304 | 325.7419 | 418.9443 | 342.4236 | 358.3291 | 345.8615 | 316.2046 | 281.7896 | 212.3387
1403.6283 | 1256.6283 | 477.5341 | 325.8139 | 418.9923 | 342.5312 | 358.4935 | 346.004 | 316.2429 | 281.9528 | 212.5102
1404.6298 | 1257.6298 | 477.4992 | 325.8824 | 419.0846 | 342.6075 | 358.5302 | 346.2071 | 316.3949 | 282.148 | 212.6868
1405.6312 | 1258.6312 | 477.5229 | 325.9804 | 419.1661 | 342.6348 | 358.7034 | 346.4189 | 316.4718 | 282.3337 | 212.8396
1406.6326 | 1259.6326 | 477.5263 | 326.0701 | 419.2046 | 342.7377 | 358.857 | 346.614 | 316.5919 | 282.49 | 213.0385
1407.6341 | 1260.6341 | 477.4271 | 326.1854 | 419.156 | 342.7818 | 359.0413 | 346.9004 | 316.8268 | 282.6711 | 213.1925
1408.6255 | 1261.6255 | 477.4156 | 326.2859 | 419.2767 | 342.893 | 359.1417 | 347.1167 | 317.0083 | 282.8338 | 213.3788
1409.6269 | 1262.6269 | 477.4449 | 326.3548 | 419.275 | 342.9893 | 359.3 | 347.4031 | 317.1465 | 282.9841 | 213.551
1410.6284 | 1263.6284 | 477.5495 | 326.4604 | 419.4033 | 343.0652 | 359.4628 | 347.2847 | 317.2372 | 283.1641 | 213.6977
1411.6298 | 1264.6298 | 477.6101 | 326.577 | 419.4854 | 343.184 | 359.624 | 347.4612 | 317.5638 | 283.3364 | 213.8685
1412.6313 | 1265.6313 | 477.6612 | 326.6046 | 419.4955 | 343.2736 | 359.7779 | 347.6598 | 317.8466 | 283.5004 | 214.032
1413.6327 | 1266.6327 | 477.8037 | 326.7375 | 419.524 | 343.3364 | 359.8678 | 347.876 | 318.0793 | 283.6432 | 214.2004
1414.6341 | 1267.6341 | 477.8422 | 326.828 | 419.6275 | 343.4294 | 360.0602 | 347.9667 | 318.3147 | 283.803 | 214.3633
1415.6256 | 1268.6256 | 477.871 | 326.9385 | 419.6005 | 343.4751 | 360.1882 | 348.0736 | 318.495 | 283.9705 | 214.5307
1416.627 | 1269.627 | 477.8525 | 327.0607 | 419.6447 | 343.5692 | 360.3187 | 348.186 | 318.6307 | 284.1183 | 214.6906
1417.6284 | 1270.6284 | 477.7912 | 327.0931 | 419.7553 | 343.6535 | 360.3475 | 348.3433 | 318.85 | 284.2549 | 214.8443
1418.68 | 1271.68 | 477.8447 | 327.2023 | 419.8559 | 343.7244 | 360.4477 | 348.4524 | 319.069 | 284.4252 | 214.9955
1419.6313 | 1272.6313 | 477.8947 | 327.2915 | 419.8911 | 343.7604 | 360.5973 | 348.6956 | 319.2611 | 284.5906 | 215.1616
1420.6328 | 1273.6328 | 477.943 | 327.3611 | 419.9857 | 343.852 | 360.7232 | 348.9121 | 319.4501 | 284.776 | 215.327
1421.6342 | 1274.6342 | 477.9357 | 327.4798 | 420.0379 | 343.9209 | 360.8454 | 349.1039 | 319.5436 | 284.9547 | 215.4893
1422.6356 | 1275.6356 | 477.8556 | 327.5732 | 420.0795 | 343.9731 | 360.966 | 349.3069 | 319.7063 | 285.1275 | 215.6532
1423.6271 | 1276.6271 | 477.8159 | 327.6574 | 420.1592 | 344.0835 | 361.0862 | 349.5853 | 319.841 | 285.274 | 215.8029
1424.6285 | 1277.6285 | 477.8071 | 327.7836 | 420.2929 | 344.204 | 361.2736 | 349.8306 | 319.9887 | 285.4193 | 215.9887
1425.63 | 1278.63 | 477.9428 | 327.8735 | 420.2403 | 344.2656 | 361.3523 | 350.0499 | 320.1866 | 285.6158 | 216.1136
1426.6314 | 1279.6314 | 477.9501 | 327.9661 | 420.3091 | 344.363 | 361.4717 | 350.2865 | 320.4372 | 285.7839 | 216.3136
1427.6328 | 1280.6328 | 477.9371 | 328.0319 | 420.356 | 344.4092 | 361.5533 | 350.4688 | 320.6518 | 285.9505 | 216.4619
1428.6343 | 1281.6343 | 477.9369 | 328.1603 | 420.3508 | 344.4824 | 361.6569 | 350.635 | 320.8354 | 286.1072 | 216.5902
1429.6257 | 1282.6257 | 477.9434 | 328.219 | 420.2938 | 344.546 | 361.7869 | 350.9045 | 321.0223 | 286.2393 | 216.7633
1430.6271 | 1283.6271 | 477.9641 | 328.3499 | 420.4155 | 344.6132 | 361.8999 | 351.06 | 321.2008 | 286.3821 | 216.9396
1431.6286 | 1284.6286 | 477.9506 | 328.4091 | 420.4019 | 344.685 | 362.0121 | 351.2562 | 321.4437 | 286.5329 | 217.1006
1432.63 | 1285.63 | 477.8471 | 328.5155 | 420.5204 | 344.743 | 362.1629 | 351.4894 | 321.6518 | 286.6712 | 217.2544
1433.6315 | 1286.6315 | 477.8171 | 328.5904 | 420.5877 | 344.8303 | 362.2909 | 351.5151 | 321.8341 | 286.817 | 217.451
1434.6329 | 1287.6329 | 477.7831 | 328.6994 | 420.6768 | 344.8397 | 362.375 | 351.6742 | 322.103 | 286.9485 | 217.6016
1435.6243 | 1288.6243 | 477.6758 | 328.7862 | 420.7399 | 344.8985 | 362.5136 | 351.8151 | 322.3441 | 287.1233 | 217.7621
1436.6258 | 1289.6258 | 477.7139 | 328.8669 | 420.762 | 344.9154 | 362.69 | 352.025 | 322.6259 | 287.3016 | 217.9277
1437.6272 | 1290.6272 | 477.7461 | 328.9453 | 420.7587 | 345.0173 | 362.8539 | 352.3207 | 322.7273 | 287.4807 | 218.0837
1438.6286 | 1291.6286 | 477.7473 | 329.0579 | 420.842 | 345.1126 | 362.9911 | 352.4422 | 322.8311 | 287.6483 | 218.2715
1439.6301 | 1292.6301 | 477.6851 | 329.1284 | 420.8562 | 345.1818 | 363.0888 | 352.3313 | 322.9516 | 287.8067 | 218.416
1440.6315 | 1293.6315 | 477.6167 | 329.2604 | 420.9575 | 345.2961 | 363.1216 | 352.6266 | 323.1153 | 287.9816 | 218.5456
1441.633 | 1294.633 | 477.5887 | 329.3046 | 421.0306 | 345.3819 | 363.2731 | 352.938 | 323.3235 | 288.1307 | 218.7164
1442.6244 | 1295.6244 | 477.6373 | 329.3895 | 421.006 | 345.445 | 363.3934 | 353.1946 | 323.5256 | 288.2791 | 218.8856
1443.6258 | 1296.6258 | 477.7574 | 329.5075 | 420.9938 | 345.4971 | 363.5491 | 353.3639 | 323.8942 | 288.4109 | 219.0508
1444.6273 | 1297.6273 | 477.7113 | 329.5987 | 421.0824 | 345.5712 | 363.7002 | 353.6477 | 324.1149 | 288.5351 | 219.2025
1445.6287 | 1298.6287 | 477.5751 | 329.6793 | 421.1418 | 345.6473 | 363.7845 | 353.8966 | 324.2663 | 288.6764 | 219.3693
1446.6302 | 1299.6302 | 477.5184 | 329.7441 | 421.1134 | 345.7441 | 363.8153 | 354.2539 | 324.4489 | 288.8404 | 219.4884
1447.6316 | 1300.6316 | 477.5743 | 329.8127 | 421.1558 | 345.8542 | 363.944 | 354.4819 | 324.6392 | 289.0007 | 219.6645
1448.633 | 1301.633 | 477.5751 | 329.9067 | 421.2192 | 345.9063 | 364.0634 | 354.6525 | 324.7669 | 289.1079 | 219.8161
1449.6345 | 1302.6345 | 477.5453 | 329.9776 | 421.3084 | 345.9629 | 364.2017 | 354.95 | 325.0738 | 289.271 | 219.9997
1450.6259 | 1303.6259 | 477.5361 | 330.1046 | 421.2323 | 346.0386 | 364.37 | 355.1324 | 325.2604 | 289.4734 | 220.1563
1451.6273 | 1304.6273 | 477.5579 | 330.1998 | 421.3322 | 346.1442 | 364.5194 | 355.2966 | 325.3335 | 289.6554 | 220.2841
1452.6288 | 1305.6288 | 477.5418 | 330.2779 | 421.4661 | 346.2368 | 364.6914 | 355.5407 | 325.4282 | 289.832 | 220.4479
1453.6302 | 1306.6302 | 477.5318 | 330.3484 | 421.577 | 346.3171 | 364.7654 | 355.6889 | 325.5789 | 290.0082 | 220.6245
1454.6317 | 1307.6317 | 477.5356 | 330.4648 | 421.6835 | 346.3993 | 364.9327 | 355.7607 | 325.7981 | 290.1802 | 220.74
1455.6331 | 1308.6331 | 477.6184 | 330.546 | 421.5749 | 346.4924 | 365.039 | 355.8501 | 325.985 | 290.3091 | 220.925
1456.6245 | 1309.6245 | 477.7211 | 330.6181 | 421.6204 | 346.4924 | 365.1175 | 356.0277 | 326.1868 | 290.4671 | 221.0988
1457.626 | 1310.626 | 477.7524 | 330.7613 | 421.6609 | 346.6058 | 365.1689 | 356.0597 | 326.4034 | 290.6385 | 221.2515
1458.6274 | 1311.6274 | 477.7714 | 330.8419 | 421.7782 | 346.6445 | 365.3258 | 356.2098 | 326.5801 | 290.8085 | 221.4014
1459.6288 | 1312.6288 | 477.8621 | 330.9423 | 421.8352 | 346.6864 | 365.4943 | 356.3444 | 326.8225 | 290.9743 | 221.5571
1460.6303 | 1313.6303 | 477.8653 | 331.0255 | 421.7927 | 346.8289 | 365.6255 | 356.4646 | 327.0363 | 291.161 | 221.6965
1461.6317 | 1314.6317 | 477.8597 | 331.0918 | 421.9329 | 346.9139 | 365.7698 | 356.6191 | 327.2966 | 291.3299 | 221.849
1462.6332 | 1315.6332 | 477.9639 | 331.1822 | 421.9608 | 346.9852 | 365.8822 | 356.8418 | 327.4874 | 291.4996 | 222.0406
1463.6346 | 1316.6346 | 478.1548 | 331.2644 | 422.0261 | 347.0554 | 366.0076 | 357.0464 | 327.6412 | 291.7011 | 222.1651
1464.626 | 1317.626 | 478.294 | 331.3835 | 422.0927 | 347.1443 | 366.2005 | 357.1011 | 327.7725 | 291.8571 | 222.3149
1465.6275 | 1318.6275 | 478.4325 | 331.4747 | 422.0611 | 347.1698 | 366.401 | 357.1345 | 327.9333 | 291.9804 | 222.5109
1466.6289 | 1319.6289 | 478.5431 | 331.5818 | 422.0769 | 347.2313 | 366.5765 | 357.3755 | 328.1085 | 292.113 | 222.6635
1467.6303 | 1320.6303 | 478.6782 | 331.6828 | 422.1065 | 347.3465 | 366.7406 | 357.6047 | 328.2605 | 292.2644 | 222.817
1468.6318 | 1321.6318 | 478.6973 | 331.7459 | 422.1855 | 347.4297 | 366.8913 | 357.8065 | 328.4055 | 292.4252 | 222.9751
1469.6332 | 1322.6332 | 478.889 | 331.8236 | 422.2573 | 347.5026 | 367.0662 | 357.9818 | 328.5796 | 292.5635 | 223.136
1470.6347 | 1323.6347 | 478.852 | 331.9135 | 422.3395 | 347.5903 | 367.2129 | 358.1858 | 328.6431 | 292.7166 | 223.264
1471.6261 | 1324.6261 | 478.8703 | 332.017 | 422.3123 | 347.6826 | 367.3787 | 358.2656 | 328.8672 | 292.8708 | 223.4423
1472.6275 | 1325.6275 | 478.9712 | 332.1431 | 422.4246 | 347.8039 | 367.5378 | 358.4229 | 329.1538 | 293.0464 | 223.5842
1473.629 | 1326.629 | 478.9222 | 332.1979 | 422.4908 | 347.8706 | 367.6947 | 358.6241 | 329.3649 | 293.1618 | 223.7437
1474.6304 | 1327.6304 | 478.8551 | 332.3042 | 422.4287 | 347.9572 | 367.8016 | 358.803 | 329.6456 | 293.3125 | 223.8944
1475.6319 | 1328.6319 | 478.8073 | 332.3778 | 422.4634 | 347.9948 | 367.8606 | 359.0172 | 329.9395 | 293.5181 | 224.0522
1476.6333 | 1329.6333 | 478.7953 | 332.4608 | 422.5178 | 348.0926 | 368.0132 | 359.2959 | 330.042 | 293.7321 | 224.1964
1477.6247 | 1330.6247 | 478.8562 | 332.562 | 422.6096 | 348.1583 | 368.1749 | 359.536 | 330.1734 | 293.9057 | 224.3648
1478.6262 | 1331.6262 | 478.7245 | 332.655 | 422.5619 | 348.2215 | 368.2928 | 359.7473 | 330.2786 | 294.0551 | 224.4816
1479.6276 | 1332.6276 | 478.7156 | 332.7396 | 422.6979 | 348.3112 | 368.3729 | 359.7832 | 330.3598 | 294.2018 | 224.6427
1480.629 | 1333.629 | 478.6981 | 332.8074 | 422.7141 | 348.4223 | 368.5409 | 359.8527 | 330.5375 | 294.3756 | 224.8213
1481.6305 | 1334.6305 | 478.5588 | 332.9032 | 422.8068 | 348.4976 | 368.7265 | 359.9136 | 330.6924 | 294.5616 | 224.9584
1482.6319 | 1335.6319 | 478.5551 | 332.935 | 422.7688 | 348.5328 | 368.9083 | 359.8744 | 330.8362 | 294.7317 | 225.1132
1483.6334 | 1336.6334 | 478.5236 | 333.0523 | 422.8057 | 348.6088 | 369.0833 | 359.9934 | 331.0156 | 294.8881 | 225.2569
1484.6248 | 1337.6248 | 478.5366 | 333.13 | 422.7984 | 348.7089 | 369.1908 | 360.2059 | 331.269 | 295.0409 | 225.3978
1485.6262 | 1338.6262 | 478.5732 | 333.2234 | 422.9321 | 348.7534 | 369.3514 | 360.4567 | 331.4757 | 295.1926 | 225.5707
1486.6277 | 1339.6277 | 478.5857 | 333.3287 | 422.9808 | 348.8417 | 369.5276 | 360.6741 | 331.6548 | 295.3454 | 225.7013
1487.6291 | 1340.6291 | 478.6423 | 333.4323 | 423.0776 | 348.8692 | 369.7065 | 360.8139 | 331.7496 | 295.423 | 225.8607
1488.6305 | 1341.6305 | 478.562 | 333.4722 | 423.1699 | 348.9898 | 369.8771 | 360.9859 | 331.8758 | 295.5484 | 226.0139
1489.632 | 1342.632 | 478.4521 | 333.5769 | 423.1892 | 349.1118 | 370.0632 | 361.2085 | 331.9948 | 295.7167 | 226.121
1490.6334 | 1343.6334 | 478.3709 | 333.6577 | 423.1413 | 349.1485 | 370.1813 | 361.4322 | 332.2675 | 295.8625 | 226.274
1491.6349 | 1344.6349 | 478.3559 | 333.7657 | 423.3075 | 349.2189 | 370.3493 | 361.5884 | 332.4842 | 296.0364 | 226.4315
1492.6363 | 1345.6363 | 478.3933 | 333.8196 | 423.3492 | 349.3146 | 370.5454 | 361.7038 | 332.6766 | 296.2436 | 226.5966
1493.6277 | 1346.6277 | 478.3239 | 333.9345 | 423.3214 | 349.406 | 370.7182 | 361.8451 | 332.7379 | 296.4003 | 226.7617
1494.6292 | 1347.6292 | 478.3613 | 334.013 | 423.2356 | 349.5279 | 370.8202 | 361.9292 | 332.8507 | 296.5721 | 226.9253
1495.6306 | 1348.6306 | 478.3403 | 334.0588 | 423.3227 | 349.6134 | 370.9232 | 362.0692 | 333.0196 | 296.7224 | 227.0481
1496.6321 | 1349.6321 | 478.3198 | 334.1503 | 423.3707 | 349.7077 | 371.1131 | 362.1566 | 333.1819 | 296.8847 | 227.2022
1497.6335 | 1350.6335 | 478.2097 | 334.2452 | 423.4317 | 349.8202 | 371.2223 | 362.3216 | 333.3647 | 297.0218 | 227.3442
1498.6249 | 1351.6249 | 478.1969 | 334.3193 | 423.4429 | 349.8606 | 371.3906 | 362.5179 | 333.5449 | 297.1866 | 227.4883
1499.6264 | 1352.6264 | 478.1598 | 334.435 | 423.5062 | 349.9239 | 371.5408 | 362.6963 | 333.7476 | 297.382 | 227.6336
1500.6278 | 1353.6278 | 478.1275 | 334.5367 | 423.4775 | 350.0172 | 371.6552 | 362.8151 | 333.9336 | 297.5976 | 227.7874
1501.6292 | 1354.6292 | 478.1262 | 334.6217 | 423.5276 | 350.0669 | 371.778 | 363.076 | 334.1148 | 297.7389 | 227.9374
1502.6307 | 1355.6307 | 478.1395 | 334.7246 | 423.5875 | 350.1173 | 371.9593 | 363.2912 | 334.3433 | 297.871 | 228.1244
1503.6321 | 1356.6321 | 478.1413 | 334.7899 | 423.6921 | 350.1474 | 372.1355 | 363.508 | 334.5478 | 298.0822 | 228.2355
1504.6336 | 1357.6336 | 478.265 | 334.8708 | 423.6469 | 350.237 | 372.3192 | 363.7206 | 334.6216 | 298.2647 | 228.3629
1505.635 | 1358.635 | 478.3626 | 334.9454 | 423.7169 | 350.244 | 372.505 | 363.9164 | 334.7775 | 298.4191 | 228.5393
1506.6264 | 1359.6264 | 478.4162 | 335.0587 | 423.8099 | 350.2057 | 372.6751 | 364.1699 | 335.0168 | 298.5583 | 228.681
1507.6279 | 1360.6279 | 478.4468 | 335.1321 | 423.8429 | 350.3204 | 372.8507 | 364.3854 | 335.375 | 298.7579 | 228.8283
1508.6293 | 1361.6293 | 478.4613 | 335.2108 | 423.8743 | 350.4799 | 373.0199 | 364.6175 | 335.7342 | 298.862 | 228.9983
1509.6307 | 1362.6307 | 478.6382 | 335.2778 | 423.9639 | 350.575 | 373.2183 | 364.8326 | 335.7757 | 298.9898 | 229.1276
1510.6322 | 1363.6322 | 478.6916 | 335.3831 | 423.9369 | 350.6574 | 373.3996 | 365.0579 | 335.8263 | 299.1306 | 229.2794
1511.6336 | 1364.6336 | 478.702 | 335.4692 | 424.038 | 350.7337 | 373.531 | 365.147 | 335.9404 | 299.2919 | 229.4304
1512.6351 | 1365.6351 | 478.8203 | 335.5527 | 424.1137 | 350.851 | 373.7243 | 365.3312 | 336.0329 | 299.4614 | 229.5725
1513.6265 | 1366.6265 | 478.8862 | 335.6383 | 424.2074 | 350.93 | 373.8841 | 365.5434 | 336.1965 | 299.6372 | 229.7338
1514.6279 | 1367.6279 | 478.9934 | 335.7197 | 424.2345 | 351.0119 | 374.0446 | 365.7405 | 336.2682 | 299.8066 | 229.8986
1515.6294 | 1368.6294 | 479.0501 | 335.7912 | 424.2881 | 351.1 | 374.204 | 365.9983 | 336.3976 | 300.0021 | 230.0567
1516.6308 | 1369.6308 | 479.0251 | 335.8994 | 424.2415 | 351.1624 | 374.3572 | 366.2277 | 336.7856 | 300.1909 | 230.2155
1517.6322 | 1370.6322 | 478.9107 | 336.0005 | 424.353 | 351.1804 | 374.5192 | 366.4914 | 337.1649 | 300.3836 | 230.3542
1518.6337 | 1371.6337 | 478.9314 | 336.0791 | 424.3905 | 351.293 | 374.7023 | 366.6982 | 337.2563 | 300.5295 | 230.5151
1519.6251 | 1372.6251 | 478.9214 | 336.17 | 424.4383 | 351.3152 | 374.8436 | 366.8959 | 337.3354 | 300.6602 | 230.7003
1520.6266 | 1373.6266 | 478.7761 | 336.2942 | 424.4813 | 351.3911 | 374.9762 | 367.1149 | 337.5198 | 300.8234 | 230.8478
1521.628 | 1374.628 | 478.6803 | 336.3741 | 424.4683 | 351.4326 | 375.1269 | 367.4245 | 337.6319 | 300.9986 | 231.0305
1522.6294 | 1375.6294 | 478.5719 | 336.4405 | 424.4713 | 351.5624 | 375.1882 | 367.7114 | 337.6848 | 301.1688 | 231.1653
1523.6309 | 1376.6309 | 478.5321 | 336.53 | 424.4409 | 351.6542 | 375.3513 | 367.9628 | 337.77 | 301.3001 | 231.3209
1524.6323 | 1377.6323 | 478.5361 | 336.5349 | 424.5743 | 351.6748 | 375.5151 | 368.1468 | 337.9682 | 301.4014 | 231.4897
1525.6237 | 1378.6237 | 478.4995 | 336.6399 | 424.6158 | 351.8281 | 375.6749 | 368.2957 | 338.2461 | 301.5973 | 231.6489
1526.6252 | 1379.6252 | 478.3459 | 336.7659 | 424.728 | 351.9197 | 375.8322 | 368.4672 | 338.4777 | 301.8061 | 231.8004
1527.6266 | 1380.6266 | 478.2979 | 336.8321 | 424.7794 | 352.0089 | 376.0114 | 368.647 | 338.682 | 301.9847 | 231.9474
1528.6281 | 1381.6281 | 478.3532 | 336.9601 | 424.7403 | 352.0662 | 376.1639 | 368.7352 | 338.7275 | 302.1515 | 232.1408
1529.6295 | 1382.6295 | 478.3477 | 337.019 | 424.7854 | 352.1423 | 376.2444 | 368.8799 | 338.8142 | 302.3271 | 232.2698
1530.6309 | 1383.6309 | 478.367 | 337.0608 | 424.6997 | 352.2402 | 376.398 | 369.0972 | 338.9826 | 302.4735 | 232.4256
1531.6324 | 1384.6324 | 478.3515 | 337.1399 | 424.7588 | 352.2766 | 376.5479 | 369.3455 | 339.2856 | 302.5737 | 232.6041
1532.6338 | 1385.6338 | 478.3397 | 337.225 | 424.9187 | 352.3649 | 376.6883 | 369.5998 | 339.3369 | 302.7249 | 232.7615
1533.6252 | 1386.6252 | 478.3033 | 337.3089 | 424.9511 | 352.4391 | 376.8624 | 369.874 | 339.4619 | 302.9232 | 232.9277
1534.6267 | 1387.6267 | 478.3195 | 337.4251 | 424.9715 | 352.5064 | 377.0227 | 370.0562 | 339.5557 | 303.1609 | 233.0667
1535.6281 | 1388.6281 | 478.2982 | 337.4948 | 425.0841 | 352.6107 | 377.1706 | 370.293 | 339.7888 | 303.3365 | 233.2255
1536.6296 | 1389.6296 | 478.2163 | 337.5534 | 425.0626 | 352.7157 | 377.328 | 370.5156 | 339.9685 | 303.5548 | 233.3713
1537.631 | 1390.631 | 478.1644 | 337.6604 | 425.1421 | 352.786 | 377.4924 | 370.7505 | 340.0928 | 303.7675 | 233.5567
1538.6324 | 1391.6324 | 478.123 | 337.7157 | 425.1942 | 352.8726 | 377.6377 | 370.9747 | 340.2562 | 303.9597 | 233.7245
1539.6339 | 1392.6339 | 478.1144 | 337.8346 | 425.2438 | 352.9389 | 377.7722 | 371.2074 | 340.5533 | 304.113 | 233.8879
1540.6253 | 1393.6253 | 478.1512 | 337.89 | 425.2145 | 352.9585 | 377.9 | 371.398 | 340.8104 | 304.2496 | 234.0451
1541.6268 | 1394.6268 | 478.1057 | 337.998 | 425.2743 | 352.9777 | 378.0523 | 371.6353 | 340.9013 | 304.3821 | 234.2068
1542.6382 | 1395.6382 | 478.1064 | 338.0555 | 425.2577 | 353.1034 | 378.1675 | 371.8192 | 340.9286 | 304.5688 | 234.3496
1543.6296 | 1396.6296 | 478.0251 | 338.1681 | 425.27 | 353.183 | 378.2828 | 371.9521 | 341.0911 | 304.747 | 234.5518
1544.6311 | 1397.6311 | 477.992 | 338.1827 | 425.4452 | 353.282 | 378.3942 | 372.1634 | 341.3193 | 304.9305 | 234.6704
1545.6325 | 1398.6325 | 477.9182 | 338.2853 | 425.415 | 353.2738 | 378.5037 | 372.3839 | 341.4424 | 305.0728 | 234.8476
1546.634 | 1399.634 | 478.02 | 338.3662 | 425.3987 | 353.3033 | 378.6145 | 372.6231 | 341.5264 | 305.1704 | 234.9903
1547.6354 | 1400.6354 | 478.1367 | 338.4262 | 425.4519 | 353.3552 | 378.6973 | 372.7844 | 341.6543 | 305.2999 | 235.168
1548.6268 | 1401.6268 | 478.1736 | 338.4767 | 425.4968 | 353.4043 | 378.8225 | 372.9647 | 341.8323 | 305.4759 | 235.3131
1549.6283 | 1402.6283 | 478.2415 | 338.5383 | 425.5687 | 353.5186 | 378.9813 | 373.1216 | 341.9846 | 305.6535 | 235.4927
1550.6297 | 1403.6297 | 478.2874 | 338.6489 | 425.7029 | 353.5976 | 379.1055 | 373.2824 | 342.1664 | 305.8075 | 235.668
1551.6311 | 1404.6311 | 478.3062 | 338.7548 | 425.7166 | 353.6759 | 379.2332 | 373.4005 | 342.2633 | 306.0247 | 235.7895
1552.6326 | 1405.6326 | 478.1843 | 338.8389 | 425.877 | 353.729 | 379.3479 | 373.5872 | 342.4539 | 306.2165 | 235.9656
1553.634 | 1406.634 | 478.2232 | 338.9417 | 425.9109 | 353.8268 | 379.4896 | 373.8506 | 342.6606 | 306.407 | 236.1757
1554.6355 | 1407.6355 | 478.2502 | 338.9981 | 425.9288 | 353.8926 | 379.6097 | 374.0864 | 342.8259 | 306.6207 | 236.326
1555.6269 | 1408.6269 | 478.2603 | 339.0289 | 425.9372 | 353.9716 | 379.7569 | 374.3294 | 342.9597 | 306.8351 | 236.483
1556.6283 | 1409.6283 | 478.2348 | 339.1383 | 426.0008 | 354.0631 | 379.8935 | 374.5819 | 343.0838 | 306.9583 | 236.6338
1557.6298 | 1410.6298 | 478.2215 | 339.2235 | 425.8872 | 354.1241 | 380.0222 | 374.7483 | 343.2113 | 307.0711 | 236.8054
1558.6312 | 1411.6312 | 478.2288 | 339.31 | 425.9468 | 354.2098 | 380.1639 | 374.931 | 343.4411 | 307.2785 | 236.9314
1559.6326 | 1412.6326 | 478.2445 | 339.3862 | 426.0895 | 354.2765 | 380.2723 | 375.1104 | 343.7374 | 307.5046 | 237.1022
1560.6341 | 1413.6341 | 478.2034 | 339.4961 | 426.0342 | 354.2641 | 380.3997 | 375.2829 | 343.8436 | 307.6753 | 237.2303
1561.6255 | 1414.6255 | 478.1435 | 339.5463 | 426.0938 | 354.3184 | 380.5056 | 375.4984 | 343.9311 | 307.7985 | 237.3711
1562.6269 | 1415.6269 | 478.1521 | 339.6438 | 426.0803 | 354.4674 | 380.6549 | 375.683 | 344.0439 | 307.9291 | 237.5566
1563.6284 | 1416.6284 | 477.9577 | 339.7218 | 426.2645 | 354.493 | 380.7846 | 375.881 | 344.2485 | 308.1086 | 237.6856
1564.6298 | 1417.6298 | 477.8541 | 339.7916 | 426.2879 | 354.5749 | 380.897 | 376.1042 | 344.4212 | 308.2793 | 237.8214
1565.6313 | 1418.6313 | 477.7749 | 339.847 | 426.2494 | 354.6375 | 381.0316 | 376.3047 | 344.5661 | 308.4079 | 237.9465
1566.6327 | 1419.6327 | 477.8413 | 339.9488 | 426.2336 | 354.7084 | 381.1646 | 376.4541 | 344.7132 | 308.5845 | 238.09
1567.7243 | 1420.7243 | 477.7714 | 340.0387 | 426.2862 | 354.767 | 381.3009 | 376.6674 | 344.8755 | 308.8482 | 238.2422
1568.6256 | 1421.6256 | 477.8144 | 340.0989 | 426.2773 | 354.832 | 381.4005 | 376.8032 | 345.0318 | 309.0402 | 238.4061
1569.627 | 1422.627 | 477.8103 | 340.2144 | 426.3015 | 354.8233 | 381.5244 | 376.955 | 345.1843 | 309.2821 | 238.525
1570.6285 | 1423.6285 | 477.6788 | 340.2722 | 426.3701 | 354.8898 | 381.6494 | 377.1073 | 345.3031 | 309.484 | 238.7043
1571.6299 | 1424.6299 | 477.605 | 340.3537 | 426.3477 | 354.953 | 381.7764 | 377.319 | 345.4397 | 309.7013 | 238.8382
1572.6313 | 1425.6313 | 477.7431 | 340.4352 | 426.4467 | 355.033 | 381.8901 | 377.5292 | 345.5864 | 309.866 | 239.026
1573.6328 | 1426.6328 | 477.8626 | 340.5273 | 426.478 | 355.1322 | 382.0037 | 377.6587 | 345.7968 | 310.0272 | 239.1794
1574.6342 | 1427.6342 | 477.8236 | 340.6007 | 426.5914 | 355.2316 | 382.1257 | 377.8085 | 345.9378 | 310.1874 | 239.3355
1575.6357 | 1428.6357 | 477.6813 | 340.6789 | 426.6658 | 355.2545 | 382.245 | 377.9163 | 346.0982 | 310.2903 | 239.5144
1576.6271 | 1429.6271 | 477.6998 | 340.7474 | 426.6397 | 355.2975 | 382.3423 | 378.0352 | 346.2343 | 310.4935 | 239.6872
1577.6285 | 1430.6285 | 477.7319 | 340.8254 | 426.7746 | 355.3181 | 382.4772 | 378.2175 | 346.4216 | 310.7258 | 239.8521
1578.63 | 1431.63 | 477.9149 | 340.8736 | 426.8105 | 355.3793 | 382.5735 | 378.3588 | 346.6193 | 310.8506 | 240.0472
1579.6314 | 1432.6314 | 477.963 | 340.9894 | 426.7824 | 355.4162 | 382.6973 | 378.5652 | 346.7442 | 310.9742 | 240.2286
1580.6328 | 1433.6328 | 477.9746 | 341.0683 | 426.8335 | 355.5189 | 382.8127 | 378.7575 | 346.941 | 311.0807 | 240.4095
1581.6343 | 1434.6343 | 478.054 | 341.1332 | 426.8832 | 355.5943 | 382.9193 | 378.9037 | 347.0466 | 311.1702 | 240.5839
1582.6257 | 1435.6257 | 478.198 | 341.1858 | 426.8841 | 355.6542 | 383.0305 | 379.0238 | 347.2425 | 311.3779 | 240.7487
1583.6271 | 1436.6271 | 478.281 | 341.3062 | 427.0192 | 355.7295 | 383.1237 | 379.217 | 347.3585 | 311.5804 | 240.9343
1584.6286 | 1437.6286 | 478.333 | 341.3725 | 426.9806 | 355.7956 | 383.2285 | 379.3548 | 347.5073 | 311.7774 | 241.0861
1585.63 | 1438.63 | 478.4088 | 341.4874 | 426.9726 | 355.8604 | 383.3464 | 379.4979 | 347.6331 | 312.0164 | 241.2411
1586.6315 | 1439.6315 | 478.4028 | 341.5073 | 426.9482 | 355.8939 | 383.4541 | 379.6506 | 347.7776 | 312.228 | 241.4351
1587.6329 | 1440.6329 | 478.3191 | 341.5919 | 427.0159 | 355.9806 | 383.5402 | 379.8186 | 347.8917 | 312.3839 | 241.587
1588.6343 | 1441.6343 | 478.3342 | 341.6728 | 427.0585 | 356.0406 | 383.6315 | 379.9636 | 348.0531 | 312.5395 | 241.7557
1589.6258 | 1442.6258 | 478.3203 | 341.7633 | 427.1341 | 356.0875 | 383.7241 | 380.1232 | 348.2321 | 312.6735 | 241.9348
1590.6272 | 1443.6272 | 478.3539 | 341.8223 | 427.1778 | 356.1681 | 383.8359 | 380.2889 | 348.3965 | 312.7627 | 242.1497
1591.6286 | 1444.6286 | 478.3902 | 341.9272 | 427.1303 | 356.3002 | 383.9222 | 380.4426 | 348.5379 | 312.8926 | 242.296
1592.6301 | 1445.6301 | 478.3486 | 342.0018 | 427.2663 | 356.311 | 384.0208 | 380.6437 | 348.6887 | 313.076 | 242.4916
1593.6315 | 1446.6315 | 478.3224 | 342.081 | 427.3963 | 356.4251 | 384.1365 | 380.8139 | 348.8135 | 313.2396 | 242.652
1594.633 | 1447.633 | 478.2269 | 342.162 | 427.3235 | 356.5023 | 384.2204 | 380.9602 | 348.9602 | 313.3662 | 242.8161
1595.6344 | 1448.6344 | 478.3226 | 342.2284 | 427.4777 | 356.552 | 384.3253 | 381.1601 | 349.1057 | 313.5085 | 242.9977
1596.6358 | 1449.6358 | 478.3649 | 342.3149 | 427.4878 | 356.5758 | 384.4018 | 381.2978 | 349.2436 | 313.6335 | 243.1973
1597.6273 | 1450.6273 | 478.3157 | 342.372 | 427.6033 | 356.5927 | 384.4964 | 381.4697 | 349.411 | 313.8093 | 243.3704
1598.6588 | 1451.6588 | 478.2712 | 342.4822 | 427.6262 | 356.7528 | 384.5877 | 381.5707 | 349.5983 | 313.957 | 243.5393
1599.6302 | 1452.6302 | 478.2249 | 342.481 | 427.6478 | 356.819 | 384.6808 | 381.6722 | 349.7497 | 314.1279 | 243.6997
1600.6316 | 1453.6316 | 478.2357 | 342.5887 | 427.6026 | 356.8818 | 384.7756 | 381.8382 | 349.9059 | 314.309 | 243.8517
1601.633 | 1454.633 | 478.1841 | 342.6829 | 427.756 | 356.9384 | 384.8516 | 381.9224 | 350.0534 | 314.4802 | 244.0468
1602.6345 | 1455.6345 | 478.1153 | 342.759 | 427.7641 | 356.9913 | 384.9367 | 382.0658 | 350.1644 | 314.6194 | 244.2007
1603.6259 | 1456.6259 | 478.1117 | 342.8291 | 427.7285 | 357.0895 | 385.0195 | 382.1822 | 350.3348 | 314.815 | 244.3372
1604.6273 | 1457.6273 | 477.99 | 342.9071 | 427.7645 | 357.1332 | 385.1154 | 382.2813 | 350.4628 | 315.0154 | 244.5202
1605.6288 | 1458.6288 | 477.9338 | 342.9897 | 427.6369 | 357.1921 | 385.1999 | 382.349 | 350.6155 | 315.2094 | 244.6833
1606.6302 | 1459.6302 | 477.8972 | 343.0308 | 427.7465 | 357.184 | 385.2993 | 382.4848 | 350.7588 | 315.3743 | 244.8582
1607.6317 | 1460.6317 | 477.82 | 343.1007 | 427.8743 | 357.2176 | 385.3878 | 382.6669 | 350.8709 | 315.5667 | 245.0131
1608.6331 | 1461.6331 | 477.7328 | 343.1906 | 427.926 | 357.369 | 385.4682 | 382.7536 | 351.0445 | 315.8013 | 245.1714
1609.6245 | 1462.6245 | 477.5456 | 343.2859 | 427.9359 | 357.4298 | 385.5427 | 382.8341 | 351.2073 | 316.0031 | 245.3465
1610.626 | 1463.626 | 477.42 | 343.3682 | 428.0116 | 357.5244 | 385.632 | 382.8624 | 351.3653 | 316.129 | 245.5078
1611.6274 | 1464.6274 | 477.4353 | 343.4521 | 428.052 | 357.5768 | 385.7276 | 382.9989 | 351.5119 | 316.1926 | 245.6784
1612.6288 | 1465.6288 | 477.5063 | 343.4162 | 427.9897 | 357.634 | 385.8113 | 383.0878 | 351.6219 | 316.2661 | 245.7878
1613.6303 | 1466.6303 | 477.4807 | 343.5319 | 428.1105 | 357.7077 | 385.8926 | 383.1265 | 351.8061 | 316.4051 | 245.9691
1614.6317 | 1467.6317 | 477.485 | 343.6602 | 428.0592 | 357.7936 | 385.9759 | 383.2242 | 352.0204 | 316.6906 | 246.1942
1615.6332 | 1468.6332 | 477.5181 | 343.7371 | 428.0693 | 357.8659 | 386.0598 | 383.3365 | 352.1951 | 316.9023 | 246.3663
1616.6346 | 1469.6346 | 477.5302 | 343.7826 | 428.1887 | 357.9113 | 386.1308 | 383.4864 | 352.3343 | 317.0489 | 246.5924
1617.626 | 1470.626 | 477.5057 | 343.8675 | 428.2595 | 357.9815 | 386.2275 | 383.5844 | 352.4724 | 317.2142 | 246.8011
1618.6275 | 1471.6275 | 477.4701 | 343.9756 | 428.3512 | 358.0339 | 386.2984 | 383.6586 | 352.6097 | 317.3978 | 246.997
1619.6289 | 1472.6289 | 477.3984 | 344.0324 | 428.3515 | 358.0915 | 386.3733 | 383.7321 | 352.7361 | 317.582 | 247.2221
1620.6304 | 1473.6304 | 477.3678 | 344.0981 | 428.368 | 358.1602 | 386.4526 | 383.8721 | 352.8872 | 317.6699 | 247.4135
1621.6318 | 1474.6318 | 477.2315 | 344.2045 | 428.4214 | 358.2017 | 386.5348 | 383.9632 | 353.0131 | 317.7753 | 247.6667
1622.6332 | 1475.6332 | 477.0642 | 344.289 | 428.4872 | 358.2769 | 386.6074 | 384.0783 | 353.1491 | 317.9384 | 247.8091
1623.6347 | 1476.6347 | 477.0552 | 344.3286 | 428.5098 | 358.3488 | 386.6973 | 384.219 | 353.3025 | 318.0911 | 248.0211
1624.6261 | 1477.6261 | 476.9714 | 344.4097 | 428.5056 | 358.4169 | 386.7684 | 384.3167 | 353.4508 | 318.1654 | 248.1926
1625.6275 | 1478.6275 | 476.9627 | 344.4747 | 428.4695 | 358.4259 | 386.8509 | 384.3219 | 353.5858 | 318.2854 | 248.4307
1626.629 | 1479.629 | 476.9501 | 344.549 | 428.498 | 358.5185 | 386.9225 | 384.338 | 353.7659 | 318.5132 | 248.607
1627.6304 | 1480.6304 | 476.8541 | 344.6288 | 428.5191 | 358.5531 | 386.9932 | 384.4372 | 353.9031 | 318.708 | 248.7675
1628.6319 | 1481.6319 | 476.8556 | 344.7004 | 428.6027 | 358.6205 | 387.0673 | 384.5633 | 354.0975 | 318.8712 | 248.9319
1629.6333 | 1482.6333 | 476.7802 | 344.7522 | 428.6201 | 358.7153 | 387.1412 | 384.6864 | 354.2714 | 319.0219 | 249.0543
1630.6247 | 1483.6247 | 476.7102 | 344.8328 | 428.6419 | 358.7709 | 387.2157 | 384.8223 | 354.4265 | 319.1049 | 249.2316
1631.6262 | 1484.6262 | 476.5619 | 344.9345 | 428.7708 | 358.8238 | 387.2835 | 384.947 | 354.6178 | 319.1687 | 249.368
1632.6276 | 1485.6276 | 476.4726 | 344.9562 | 428.7944 | 358.8946 | 387.3596 | 384.9638 | 354.7686 | 319.2609 | 249.5299
1633.629 | 1486.629 | 476.4217 | 345.0552 | 428.8002 | 358.9474 | 387.4444 | 384.9992 | 354.9284 | 319.5875 | 249.6546
1634.6305 | 1487.6305 | 476.4266 | 345.1312 | 428.8091 | 358.9942 | 387.5211 | 385.085 | 355.0666 | 319.7819 | 249.8145
1635.6319 | 1488.6319 | 476.5953 | 345.1666 | 428.7872 | 359.0623 | 387.6052 | 385.2171 | 355.2167 | 319.9191 | 249.957
1636.6334 | 1489.6334 | 476.8833 | 345.1859 | 428.9072 | 359.1177 | 387.6791 | 385.3072 | 355.3549 | 320.1066 | 250.0751
1637.6348 | 1490.6348 | 477.0119 | 345.3111 | 428.9475 | 359.1975 | 387.7629 | 385.4252 | 355.4968 | 320.2333 | 250.2277
1638.6262 | 1491.6262 | 477.1803 | 345.3772 | 428.9308 | 359.2987 | 387.827 | 385.523 | 355.659 | 320.3335 | 250.3569
1639.6277 | 1492.6277 | 477.1997 | 345.4603 | 428.9725 | 359.3458 | 387.913 | 385.658 | 355.8039 | 320.4374 | 250.5178
1640.6291 | 1493.6291 | 477.2537 | 345.5451 | 429.0596 | 359.3813 | 387.9868 | 385.6956 | 355.9554 | 320.5506 | 250.5302
1641.6305 | 1494.6305 | 477.3168 | 345.6347 | 429.0725 | 359.4589 | 388.0682 | 385.7184 | 356.1118 | 320.6813 | 250.6459
1642.632 | 1495.632 | 477.3333 | 345.7496 | 429.0837 | 359.4738 | 388.1367 | 385.8041 | 356.2595 | 320.8825 | 250.8257
1643.6334 | 1496.6334 | 477.4663 | 345.7892 | 429.1084 | 359.5436 | 388.1953 | 385.911 | 356.4169 | 321.0373 | 251.0123
1644.6349 | 1497.6349 | 477.6191 | 345.8681 | 429.1833 | 359.6168 | 388.2659 | 386.0188 | 356.5449 | 321.1133 | 251.1778
1645.6263 | 1498.6263 | 477.7319 | 345.9041 | 429.2287 | 359.616 | 388.3342 | 386.0909 | 356.6842 | 321.2177 | 251.3302
1646.6277 | 1499.6277 | 477.7224 | 345.9858 | 429.263 | 359.7446 | 388.4205 | 386.2049 | 356.8578 | 321.3335 | 251.4705
1647.6292 | 1500.6292 | 477.8909 | 346.0698 | 429.2454 | 359.858 | 388.4886 | 386.3292 | 357.0159 | 321.4915 | 251.5595
1648.6306 | 1501.6306 | 477.9453 | 346.0984 | 429.2174 | 359.9168 | 388.568 | 386.4326 | 357.1468 | 321.7039 | 251.678
1649.6321 | 1502.6321 | 477.9588 | 346.1855 | 429.2569 | 359.9683 | 388.6331 | 386.4998 | 357.2597 | 321.9386 | 251.8387
1650.6335 | 1503.6335 | 478.024 | 346.2874 | 429.3189 | 360.0107 | 388.6993 | 386.5051 | 357.389 | 322.1425 | 251.9822
1651.6249 | 1504.6249 | 477.9933 | 346.3729 | 429.4377 | 360.1176 | 388.7743 | 386.6152 | 357.5382 | 322.2745 | 252.0633
1652.6264 | 1505.6264 | 478.0003 | 346.4539 | 429.531 | 360.1787 | 388.8306 | 386.7673 | 357.6657 | 322.3442 | 252.1696
1653.6278 | 1506.6278 | 478.088 | 346.5127 | 429.4848 | 360.2384 | 388.9061 | 386.8437 | 357.7977 | 322.3749 | 252.2211
1654.6292 | 1507.6292 | 478.1615 | 346.5806 | 429.3801 | 360.3371 | 388.9755 | 386.9189 | 357.9396 | 322.5121 | 252.304
1655.6307 | 1508.6307 | 478.1753 | 346.623 | 429.5334 | 360.3894 | 389.0446 | 387.0154 | 358.0901 | 322.6456 | 252.5022
1656.6321 | 1509.6321 | 478.1527 | 346.718 | 429.5719 | 360.4324 | 389.1121 | 387.1227 | 358.2096 | 322.8115 | 252.6679
1657.6336 | 1510.6336 | 478.1414 | 346.7798 | 429.5407 | 360.4998 | 389.1762 | 387.1611 | 358.3572 | 322.9535 | 252.8371
1658.625 | 1511.625 | 478.2003 | 346.8468 | 429.4814 | 360.5288 | 389.2476 | 387.2235 | 358.4965 | 323.0567 | 253.0263
1659.6264 | 1512.6264 | 478.2001 | 346.9143 | 429.691 | 360.6052 | 389.3194 | 387.2964 | 358.6186 | 323.3128 | 253.2181
1660.6279 | 1513.6279 | 478.1445 | 346.9989 | 429.6985 | 360.6737 | 389.3811 | 387.453 | 358.7517 | 323.4748 | 253.3313
1661.6293 | 1514.6293 | 478.2627 | 347.1033 | 429.77 | 360.7496 | 389.4562 | 387.5338 | 358.8829 | 323.5143 | 253.488
1662.6307 | 1515.6307 | 478.2963 | 347.1892 | 429.7979 | 360.8222 | 389.5166 | 387.5961 | 359.0752 | 323.5754 | 253.6655
1663.6322 | 1516.6322 | 478.2724 | 347.2705 | 429.8876 | 360.8605 | 389.5924 | 387.6771 | 359.2375 | 323.7358 | 253.7994
1664.6336 | 1517.6336 | 478.3135 | 347.3355 | 429.9479 | 360.9296 | 389.6485 | 387.7481 | 359.3778 | 323.909 | 253.9056
1665.6351 | 1518.6351 | 478.3775 | 347.3886 | 429.9738 | 360.9767 | 389.7164 | 387.7991 | 359.4985 | 324.0546 | 254.0651
1666.6265 | 1519.6265 | 478.5439 | 347.4749 | 429.9515 | 361.0679 | 389.7864 | 387.8498 | 359.6372 | 324.2121 | 254.1576
1667.6279 | 1520.6279 | 478.5264 | 347.5499 | 429.9999 | 361.1406 | 389.8466 | 387.9705 | 359.8018 | 324.3456 | 254.2789
1668.6294 | 1521.6294 | 478.4339 | 347.6119 | 430.0162 | 361.2005 | 389.9168 | 388.1248 | 359.9426 | 324.4753 | 254.3897
1669.6308 | 1522.6308 | 478.3468 | 347.6924 | 430.045 | 361.2998 | 389.9761 | 388.2042 | 360.0708 | 324.5244 | 254.4819
1670.6323 | 1523.6323 | 478.2872 | 347.7529 | 430.1224 | 361.3178 | 390.0445 | 388.2387 | 360.2129 | 324.6273 | 254.5894
1671.6337 | 1524.6337 | 478.2477 | 347.801 | 430.0857 | 361.4073 | 390.1112 | 388.3029 | 360.3517 | 324.7454 | 254.6721
1672.6251 | 1525.6251 | 478.3421 | 347.8791 | 430.1673 | 361.4288 | 390.1813 | 388.3956 | 360.5001 | 324.9231 | 254.7746
1673.6266 | 1526.6266 | 478.3799 | 347.9684 | 430.1513 | 361.4889 | 390.2648 | 388.4885 | 360.6347 | 325.0809 | 254.8498
1674.628 | 1527.628 | 478.4213 | 348.026 | 430.1855 | 361.5937 | 390.3463 | 388.5548 | 360.7652 | 325.2475 | 254.9801
1675.6294 | 1528.6294 | 478.4917 | 348.1217 | 430.2309 | 361.6404 | 390.4304 | 388.5998 | 360.8926 | 325.4297 | 255.0624
1676.6309 | 1529.6309 | 478.5144 | 348.1825 | 430.2802 | 361.7232 | 390.5089 | 388.6229 | 361.0233 | 325.5294 | 255.1867
1677.6323 | 1530.6323 | 478.4565 | 348.2709 | 430.2598 | 361.7803 | 390.5796 | 388.7343 | 361.1534 | 325.6649 | 255.3175
1678.6338 | 1531.6338 | 478.3523 | 348.3045 | 430.2828 | 361.874 | 390.6609 | 388.805 | 361.2764 | 325.7425 | 255.4365
1679.6352 | 1532.6352 | 478.2421 | 348.3781 | 430.3096 | 361.9295 | 390.7399 | 388.8809 | 361.3999 | 325.8762 | 255.5091
1680.6266 | 1533.6266 | 478.1957 | 348.4319 | 430.3601 | 362.0003 | 390.8174 | 388.9652 | 361.5431 | 326.0602 | 255.624
1681.6281 | 1534.6281 | 478.0212 | 348.5446 | 430.4193 | 362.0487 | 390.8961 | 389.0182 | 361.6854 | 326.1777 | 255.7436
1682.6295 | 1535.6295 | 477.9607 | 348.6093 | 430.4904 | 362.1533 | 390.9761 | 389.0001 | 361.8227 | 326.302 | 255.7883
1683.6309 | 1536.6309 | 477.9136 | 348.6898 | 430.5288 | 362.1887 | 391.0579 | 389.0348 | 361.9558 | 326.5331 | 255.9026
1684.6324 | 1537.6324 | 477.908 | 348.7272 | 430.5554 | 362.2813 | 391.127 | 389.0483 | 362.0877 | 326.5805 | 256.0564
1685.6338 | 1538.6338 | 477.9184 | 348.818 | 430.607 | 362.3343 | 391.2048 | 389.1029 | 362.2068 | 326.607 | 256.1944
1686.6353 | 1539.6353 | 477.9167 | 348.8715 | 430.6247 | 362.4097 | 391.2928 | 389.2119 | 362.3381 | 326.7111 | 256.3202
1687.6267 | 1540.6267 | 477.8983 | 348.9652 | 430.6563 | 362.4546 | 391.3624 | 389.2696 | 362.4576 | 326.8468 | 256.4518
1688.6281 | 1541.6281 | 477.9101 | 349.0487 | 430.5994 | 362.5637 | 391.4515 | 389.3408 | 362.5757 | 326.9733 | 256.6089
1689.6296 | 1542.6296 | 477.8267 | 349.1067 | 430.7352 | 362.632 | 391.5322 | 389.3661 | 362.7097 | 327.1258 | 256.7379
1690.631 | 1543.631 | 477.6498 | 349.1607 | 430.7305 | 362.6977 | 391.6158 | 389.4126 | 362.8363 | 327.2236 | 256.9171
1691.6324 | 1544.6324 | 477.5953 | 349.2573 | 430.7707 | 362.7494 | 391.6854 | 389.4224 | 362.9585 | 327.3096 | 257.044
1692.6339 | 1545.6339 | 477.5092 | 349.2788 | 430.8181 | 362.824 | 391.7734 | 389.5161 | 363.0737 | 327.4179 | 257.1634
1693.6253 | 1546.6253 | 477.4854 | 349.3886 | 430.8291 | 362.8787 | 391.8588 | 389.6014 | 363.2283 | 327.5444 | 257.324
1694.6268 | 1547.6268 | 477.5688 | 349.4505 | 430.8938 | 362.96 | 391.942 | 389.6041 | 363.3458 | 327.6892 | 257.4892
1695.6282 | 1548.6282 | 477.4974 | 349.532 | 430.9238 | 362.9759 | 392.0262 | 389.6448 | 363.4576 | 327.866 | 257.6977
1696.6296 | 1549.6296 | 477.3777 | 349.5801 | 431.0055 | 363.064 | 392.1014 | 389.6659 | 363.5803 | 328.0561 | 257.8745
1697.6311 | 1550.6311 | 477.3849 | 349.6443 | 431.033 | 363.1547 | 392.184 | 389.68 | 363.6992 | 328.2367 | 258.0424
1698.6325 | 1551.6325 | 477.3653 | 349.6831 | 431.1091 | 363.22 | 392.2461 | 389.6735 | 363.8295 | 328.351 | 258.1771
1699.6239 | 1552.6239 | 477.2821 | 349.7321 | 431.0919 | 363.2478 | 392.3547 | 389.7157 | 363.9425 | 328.4155 | 258.3031
1700.6254 | 1553.6254 | 477.2303 | 349.8045 | 431.1283 | 363.331 | 392.402 | 389.7952 | 364.0372 | 328.5169 | 258.4137
1701.6268 | 1554.6268 | 477.3127 | 349.8656 | 431.1758 | 363.3887 | 392.5125 | 389.8807 | 364.154 | 328.6391 | 258.5523
1702.6283 | 1555.6283 | 477.3862 | 349.9943 | 431.2162 | 363.4736 | 392.5992 | 389.9757 | 364.2928 | 328.8105 | 258.6681
1703.6297 | 1556.6297 | 477.3477 | 350.0427 | 431.2126 | 363.5279 | 392.6747 | 390.0879 | 364.3981 | 328.9779 | 258.7185
1704.6311 | 1557.6311 | 477.2685 | 350.0974 | 431.162 | 363.5762 | 392.764 | 390.1643 | 364.5066 | 329.0858 | 258.8296
1705.6326 | 1558.6326 | 477.3046 | 350.1638 | 431.1084 | 363.6292 | 392.8532 | 390.2857 | 364.6439 | 329.2099 | 258.8963
1706.634 | 1559.634 | 477.267 | 350.253 | 431.1394 | 363.676 | 392.9222 | 390.4011 | 364.7532 | 329.3195 | 259.0168
1707.6355 | 1560.6355 | 477.3177 | 350.3046 | 431.2262 | 363.7885 | 393.0031 | 390.5642 | 364.8706 | 329.453 | 259.1391
1708.6269 | 1561.6269 | 477.3136 | 350.2979 | 431.2094 | 363.8056 | 393.086 | 390.7352 | 364.9747 | 329.5673 | 259.2498
1709.6283 | 1562.6283 | 477.4268 | 350.4665 | 431.3129 | 363.8865 | 393.1722 | 390.8469 | 365.1114 | 329.7905 | 259.3317
1710.6298 | 1563.6298 | 477.5655 | 350.4946 | 431.2517 | 363.9368 | 393.2369 | 390.9828 | 365.2305 | 329.894 | 259.5245
1711.6312 | 1564.6312 | 477.5408 | 350.573 | 431.343 | 363.9326 | 393.3407 | 391.0366 | 365.3486 | 330.0896 | 259.6435
1712.6326 | 1565.6326 | 477.5876 | 350.6498 | 431.418 | 364.0297 | 393.4301 | 391.0966 | 365.4586 | 330.1589 | 259.8596
1713.6341 | 1566.6341 | 477.479 | 350.7331 | 431.3069 | 364.0704 | 393.4908 | 391.0716 | 365.5695 | 330.2217 | 259.9468
1714.6255 | 1567.6255 | 477.4605 | 350.7727 | 431.3187 | 364.1567 | 393.585 | 391.1853 | 365.6859 | 330.3686 | 260.0317
1715.627 | 1568.627 | 477.532 | 350.8359 | 431.3977 | 364.2187 | 393.6583 | 391.386 | 365.7961 | 330.4971 | 260.087
1716.6284 | 1569.6284 | 477.6989 | 350.9148 | 431.4136 | 364.29 | 393.7367 | 391.4586 | 365.9099 | 330.5745 | 260.1552
1717.6298 | 1570.6298 | 477.6195 | 350.9757 | 431.4493 | 364.3865 | 393.8275 | 391.5474 | 366.0269 | 330.7113 | 260.1971
1718.7114 | 1571.7114 | 477.5797 | 351.0643 | 431.4865 | 364.4457 | 393.9032 | 391.5821 | 366.159 | 330.8706 | 260.3051
1719.6327 | 1572.6327 | 477.5303 | 351.1123 | 431.5627 | 364.4883 | 393.9737 | 391.7151 | 366.2636 | 331.009 | 260.4983
1720.6342 | 1573.6342 | 477.4888 | 351.19 | 431.5601 | 364.5695 | 394.0577 | 391.9516 | 366.3816 | 331.1589 | 260.6487
1721.6356 | 1574.6356 | 477.4162 | 351.1743 | 431.6089 | 364.6056 | 394.1443 | 392.0668 | 366.4997 | 331.2682 | 260.8336
1722.627 | 1575.627 | 477.4557 | 351.2793 | 431.5204 | 364.6587 | 394.2014 | 392.1477 | 366.6143 | 331.3188 | 261.0298
1723.6285 | 1576.6285 | 477.5467 | 351.3727 | 431.5455 | 364.6456 | 394.2915 | 392.2469 | 366.7246 | 331.5677 | 261.1782
1724.6299 | 1577.6299 | 477.547 | 351.4287 | 431.6518 | 364.6876 | 394.3462 | 392.2946 | 366.8365 | 331.7719 | 261.3588
1725.6313 | 1578.6313 | 477.5205 | 351.482 | 431.6741 | 364.7206 | 394.441 | 392.2842 | 366.9333 | 331.96 | 261.4676
1726.6328 | 1579.6328 | 477.5586 | 351.5381 | 431.6434 | 364.7085 | 394.5076 | 392.3484 | 367.054 | 332.0747 | 261.5755
1727.6342 | 1580.6342 | 477.6234 | 351.6059 | 431.7352 | 364.8203 | 394.6054 | 392.4509 | 367.1558 | 332.177 | 261.6353
1728.6357 | 1581.6357 | 477.6116 | 351.7236 | 431.772 | 364.8838 | 394.6696 | 392.5353 | 367.2626 | 332.2893 | 261.7669
1729.6271 | 1582.6271 | 477.451 | 351.7599 | 431.8755 | 364.9113 | 394.7443 | 392.5716 | 367.3769 | 332.4003 | 261.8797
1730.6285 | 1583.6285 | 477.3613 | 351.8031 | 431.7279 | 365.0256 | 394.8144 | 392.7062 | 367.4801 | 332.4724 | 262.0003
1731.63 | 1584.63 | 477.258 | 351.9142 | 431.7458 | 365.1159 | 394.8937 | 392.8045 | 367.5863 | 332.6062 | 262.0854
1732.6314 | 1585.6314 | 477.1901 | 351.9665 | 431.7772 | 365.1708 | 394.973 | 392.8259 | 367.6841 | 332.7048 | 262.2213
1733.6328 | 1586.6328 | 477.074 | 351.9895 | 431.8411 | 365.2453 | 395.0433 | 392.9142 | 367.782 | 332.8602 | 262.3559
1734.6243 | 1587.6243 | 476.956 | 351.9774 | 431.8984 | 365.2882 | 395.1242 | 393.0186 | 367.8828 | 333.0224 | 262.4576
1735.6257 | 1588.6257 | 476.9456 | 352.1303 | 432.0072 | 365.2902 | 395.1986 | 393.088 | 367.9983 | 333.1665 | 262.5469
1736.6271 | 1589.6271 | 477.0645 | 352.1828 | 431.9406 | 365.4313 | 395.2899 | 393.1059 | 368.0909 | 333.2603 | 262.6789
1737.6286 | 1590.6286 | 477.057 | 352.281 | 432.0186 | 365.5046 | 395.3601 | 393.0856 | 368.1996 | 333.3875 | 262.8131
1738.63 | 1591.63 | 477.0649 | 352.3331 | 431.954 | 365.5364 | 395.4415 | 393.1372 | 368.2831 | 333.5226 | 262.9523
1739.6315 | 1592.6315 | 477.106 | 352.3542 | 432.0583 | 365.6229 | 395.5292 | 393.1801 | 368.3853 | 333.6072 | 263.0799
1740.6329 | 1593.6329 | 477.1929 | 352.4107 | 432.0528 | 365.6945 | 395.6037 | 393.2087 | 368.498 | 333.7501 | 263.2392
1741.6243 | 1594.6243 | 477.1895 | 352.5215 | 432.0452 | 365.7429 | 395.6822 | 393.3241 | 368.5927 | 333.8628 | 263.4137
1742.6258 | 1595.6258 | 477.2638 | 352.5299 | 432.1631 | 365.8505 | 395.7644 | 393.4952 | 368.699 | 333.9672 | 263.581
1743.6272 | 1596.6272 | 477.3091 | 352.5923 | 432.2211 | 365.8645 | 395.8219 | 393.5349 | 368.8 | 334.0875 | 263.7135
1744.6287 | 1597.6287 | 477.1959 | 352.7178 | 432.2322 | 365.8737 | 395.8919 | 393.471 | 368.9066 | 334.2114 | 263.8673
1745.6301 | 1598.6301 | 477.2495 | 352.752 | 432.1781 | 365.9271 | 395.9591 | 393.4858 | 369.0056 | 334.3725 | 264.0012
1746.6315 | 1599.6315 | 477.3169 | 352.8567 | 432.2348 | 365.999 | 396.034 | 393.5282 | 369.1108 | 334.587 | 264.1129
1747.633 | 1600.633 | 477.3633 | 352.9627 | 432.2969 | 366.0796 | 396.105 | 393.5754 | 369.2041 | 334.7574 | 264.2336
1748.6244 | 1601.6244 | 477.3804 | 352.9573 | 432.3822 | 366.1657 | 396.1837 | 393.5239 | 369.3115 | 334.8536 | 264.3423
1749.6359 | 1602.6359 | 477.4482 | 352.9938 | 432.358 | 366.2163 | 396.2532 | 393.5407 | 369.4061 | 335.0005 | 264.4384
1750.6273 | 1603.6273 | 477.6395 | 353.1329 | 432.3533 | 366.2911 | 396.3236 | 393.484 | 369.4931 | 335.1029 | 264.5278
1751.6287 | 1604.6287 | 477.8843 | 353.1702 | 432.3196 | 366.3109 | 396.384 | 393.5143 | 369.5971 | 335.2049 | 264.6361
1752.6302 | 1605.6302 | 477.9216 | 353.2 | 432.3548 | 366.3851 | 396.4707 | 393.5511 | 369.6876 | 335.3047 | 264.8002
1753.6316 | 1606.6316 | 477.9102 | 353.282 | 432.438 | 366.4859 | 396.5394 | 393.5345 | 369.7826 | 335.4123 | 264.8975
1754.633 | 1607.633 | 477.9271 | 353.3871 | 432.518 | 366.5553 | 396.6227 | 393.6216 | 369.8779 | 335.5261 | 265.0412
1755.6345 | 1608.6345 | 478.0008 | 353.4781 | 432.4508 | 366.5954 | 396.6865 | 393.5961 | 369.9813 | 335.6853 | 265.1393
1756.6259 | 1609.6259 | 478.0454 | 353.5437 | 432.4849 | 366.6372 | 396.7662 | 393.655 | 370.0663 | 335.7801 | 265.3147
1757.6273 | 1610.6273 | 478.1195 | 353.5858 | 432.5505 | 366.655 | 396.8297 | 393.7516 | 370.1473 | 335.7758 | 265.4645
1758.6288 | 1611.6288 | 478.1441 | 353.6849 | 432.5367 | 366.7473 | 396.9045 | 393.7347 | 370.2462 | 335.8753 | 265.576
1759.6302 | 1612.6302 | 478.1319 | 353.7216 | 432.566 | 366.8262 | 396.9875 | 393.8029 | 370.3309 | 336.1073 | 265.6419
1760.6317 | 1613.6317 | 478.0931 | 353.835 | 432.6707 | 366.9279 | 397.0448 | 393.8541 | 370.4273 | 336.3048 | 265.7756
1761.6331 | 1614.6331 | 478.0976 | 353.8373 | 432.7236 | 366.9658 | 397.1183 | 393.8876 | 370.5179 | 336.4717 | 265.8196
1762.6245 | 1615.6245 | 478.1405 | 353.8761 | 432.75 | 367.0372 | 397.1869 | 393.9596 | 370.6013 | 336.6027 | 265.9131
1763.626 | 1616.626 | 478.0165 | 353.9561 | 432.7807 | 367.0969 | 397.2673 | 394.2187 | 370.6743 | 336.6797 | 266.0991
1764.6274 | 1617.6274 | 477.942 | 354.0479 | 432.7903 | 367.1681 | 397.3246 | 394.5077 | 370.7643 | 336.7959 | 266.2805
1765.6288 | 1618.6288 | 477.8575 | 354.1281 | 432.8799 | 367.227 | 397.402 | 394.5842 | 370.8425 | 336.8701 | 266.4608
1766.6303 | 1619.6303 | 477.8478 | 354.1996 | 432.8243 | 367.2676 | 397.4648 | 394.5342 | 370.9304 | 336.9918 | 266.5965
1767.6317 | 1620.6317 | 477.7126 | 354.2641 | 432.9479 | 367.3084 | 397.5381 | 394.5915 | 371.0123 | 337.1492 | 266.713
1768.6332 | 1621.6332 | 477.7249 | 354.3248 | 432.9988 | 367.4119 | 397.609 | 394.6896 | 371.0898 | 337.2627 | 266.8366
1769.6346 | 1622.6346 | 477.8472 | 354.4166 | 432.9891 | 367.4695 | 397.6614 | 394.6861 | 371.1635 | 337.4183 | 266.8968
1770.626 | 1623.626 | 477.8269 | 354.5034 | 433.0259 | 367.5169 | 397.7294 | 394.5918 | 371.2472 | 337.4986 | 267.015
1771.6275 | 1624.6275 | 477.7807 | 354.5685 | 432.8757 | 367.5848 | 397.7881 | 394.6938 | 371.3151 | 337.6279 | 267.1128
1772.6289 | 1625.6289 | 477.7303 | 354.6082 | 432.8925 | 367.6327 | 397.8645 | 394.6982 | 371.3965 | 337.7498 | 267.2743
1773.6304 | 1626.6304 | 477.7986 | 354.684 | 433.063 | 367.6947 | 397.9319 | 394.6268 | 371.4698 | 337.9096 | 267.3824
1774.6318 | 1627.6318 | 477.8479 | 354.7262 | 433.0545 | 367.7366 | 397.9975 | 394.6743 | 371.5403 | 338.0431 | 267.5039
1775.6332 | 1628.6332 | 477.7227 | 354.823 | 433.0495 | 367.8085 | 398.0632 | 394.6734 | 371.6253 | 338.1224 | 267.5858
1776.6347 | 1629.6347 | 477.6012 | 354.888 | 433.1482 | 367.8875 | 398.1447 | 394.6398 | 371.6945 | 338.2541 | 267.6489
1777.6261 | 1630.6261 | 477.5708 | 354.9721 | 433.2019 | 367.9624 | 398.2001 | 394.621 | 371.7641 | 338.4854 | 267.6779
1778.6275 | 1631.6275 | 477.4855 | 355.0217 | 433.1855 | 368.009 | 398.2713 | 394.6584 | 371.832 | 338.6418 | 267.7275
1779.629 | 1632.629 | 477.3488 | 355.0726 | 433.118 | 368.0579 | 398.3311 | 394.6931 | 371.9091 | 338.7425 | 267.8512
1780.6304 | 1633.6304 | 477.2217 | 355.1089 | 433.1532 | 368.0733 | 398.4131 | 394.7188 | 371.9776 | 338.8168 | 267.9871
1781.6319 | 1634.6319 | 477.0136 | 355.179 | 433.22 | 368.149 | 398.4685 | 394.812 | 372.0432 | 338.9048 | 268.0907
1782.6333 | 1635.6333 | 476.9651 | 355.1909 | 433.2522 | 368.2199 | 398.5517 | 395.0828 | 372.1183 | 339.0197 | 268.2352
1783.6247 | 1636.6247 | 476.9205 | 355.2619 | 433.2955 | 368.2609 | 398.6157 | 395.1796 | 372.1824 | 339.1281 | 268.3496
1784.6262 | 1637.6262 | 476.7981 | 355.3706 | 433.3531 | 368.3285 | 398.6747 | 395.3359 | 372.2498 | 339.2211 | 268.4247
1785.6276 | 1638.6276 | 476.7936 | 355.4134 | 433.3941 | 368.3563 | 398.7468 | 395.4961 | 372.3132 | 339.3358 | 268.5353
1786.629 | 1639.629 | 476.8222 | 355.5038 | 433.3554 | 368.3772 | 398.8176 | 395.5872 | 372.369 | 339.5145 | 268.6808
1787.6305 | 1640.6305 | 476.9195 | 355.5587 | 433.3205 | 368.4927 | 398.8799 | 395.6797 | 372.4252 | 339.6451 | 268.8268
1788.6319 | 1641.6319 | 476.8855 | 355.6029 | 433.3905 | 368.5559 | 398.9435 | 395.8045 | 372.4847 | 339.7539 | 268.9208
1789.6334 | 1642.6334 | 476.9539 | 355.6766 | 433.5007 | 368.6018 | 399.0179 | 396.0522 | 372.544 | 339.8266 | 269.0228
1790.6348 | 1643.6348 | 476.8767 | 355.7586 | 433.5249 | 368.68 | 399.0803 | 396.3091 | 372.6103 | 339.9256 | 269.0945
1791.6262 | 1644.6262 | 476.7305 | 355.8225 | 433.6346 | 368.7679 | 399.1512 | 396.4596 | 372.6734 | 340.05 | 269.0856
1792.6277 | 1645.6277 | 476.7649 | 355.868 | 433.6263 | 368.7886 | 399.2141 | 396.5151 | 372.7345 | 340.1284 | 269.2182
1793.6291 | 1646.6291 | 476.8403 | 355.953 | 433.5745 | 368.8492 | 399.2835 | 396.5797 | 372.7937 | 340.2365 | 269.342
1794.6306 | 1647.6306 | 476.7507 | 356.0261 | 433.5924 | 368.9099 | 399.3355 | 396.5491 | 372.8632 | 340.3216 | 269.4989
1795.632 | 1648.632 | 476.6331 | 356.0904 | 433.564 | 368.9294 | 399.4098 | 396.4617 | 372.9142 | 340.4362 | 269.6283
1796.6334 | 1649.6334 | 476.6736 | 356.1741 | 433.5532 | 368.9941 | 399.4792 | 396.4872 | 372.9927 | 340.5343 | 269.7339
1797.6349 | 1650.6349 | 476.8364 | 356.2147 | 433.635 | 369.0363 | 399.5505 | 396.4598 | 373.0514 | 340.658 | 269.8252
1798.6263 | 1651.6263 | 476.7734 | 356.3042 | 433.645 | 369.0958 | 399.6019 | 396.5675 | 373.1252 | 340.7773 | 269.9727
1799.6277 | 1652.6277 | 476.7458 | 356.3184 | 433.6255 | 369.1125 | 399.6768 | 396.569 | 373.1893 | 340.8886 | 270.1075
1800.6292 | 1653.6292 | 476.7945 | 356.4021 | 433.6972 | 369.1915 | 399.7432 | 396.6856 | 373.2535 | 340.9766 | 270.3395
1801.6306 | 1654.6306 | 476.8748 | 356.4312 | 433.6242 | 369.2758 | 399.8034 | 396.674 | 373.3251 | 341.0646 | 270.4188
1802.6321 | 1655.6321 | 476.803 | 356.5168 | 433.6368 | 369.3274 | 399.8621 | 396.6425 | 373.3811 | 341.153 | 270.4449
1803.6335 | 1656.6335 | 476.8458 | 356.5802 | 433.6458 | 369.4314 | 399.9394 | 396.5389 | 373.4215 | 341.3533 | 270.4918
1804.6349 | 1657.6349 | 476.8051 | 356.6853 | 433.6912 | 369.4809 | 399.9995 | 396.4872 | 373.4683 | 341.5639 | 270.5972
1805.6264 | 1658.6264 | 476.8796 | 356.7099 | 433.7077 | 369.5146 | 400.0642 | 396.5092 | 373.5189 | 341.6997 | 270.7579
1806.6278 | 1659.6278 | 477.0181 | 356.758 | 433.7816 | 369.5819 | 400.1366 | 396.5161 | 373.5603 | 341.784 | 270.8696
1807.6292 | 1660.6292 | 477.1068 | 356.8439 | 433.8502 | 369.6614 | 400.1976 | 396.5079 | 373.6052 | 341.8562 | 270.9739
1808.6307 | 1661.6307 | 477.3466 | 356.9102 | 433.8556 | 369.6996 | 400.2569 | 396.4913 | 373.6622 | 341.961 | 271.1
1809.6321 | 1662.6321 | 477.4826 | 356.9932 | 433.8601 | 369.7736 | 400.3342 | 396.4678 | 373.7113 | 342.0586 | 271.1823
1810.6336 | 1663.6336 | 477.5879 | 357.0453 | 433.9079 | 369.8345 | 400.3914 | 396.6643 | 373.7669 | 342.1816 | 271.2481
1811.635 | 1664.635 | 477.6901 | 357.084 | 433.9182 | 369.8774 | 400.4474 | 396.7855 | 373.8107 | 342.2862 | 271.2739
1812.6264 | 1665.6264 | 477.5983 | 357.1423 | 434.0116 | 369.9327 | 400.5087 | 396.7806 | 373.855 | 342.3897 | 271.3144
1813.6279 | 1666.6279 | 477.584 | 357.2167 | 433.9263 | 370.002 | 400.5748 | 396.808 | 373.8987 | 342.4573 | 271.4335
1814.6293 | 1667.6293 | 477.5405 | 357.2382 | 433.9435 | 370.0782 | 400.6327 | 396.8351 | 373.9598 | 342.5485 | 271.5194
1815.6307 | 1668.6307 | 477.4825 | 357.3004 | 433.9963 | 370.1236 | 400.6964 | 396.8065 | 374.0076 | 342.6772 | 271.659
1816.6322 | 1669.6322 | 477.3975 | 357.3744 | 433.9916 | 370.1574 | 400.7536 | 396.8504 | 374.0596 | 342.8066 | 271.7524
1817.6336 | 1670.6336 | 477.3669 | 357.4479 | 433.9856 | 370.2342 | 400.8259 | 396.978 | 374.1053 | 342.9195 | 271.9272
1818.6251 | 1671.6251 | 477.3342 | 357.5316 | 434.0443 | 370.2758 | 400.8832 | 397.0565 | 374.1564 | 343.0533 | 272.007
1819.6265 | 1672.6265 | 477.3407 | 357.5573 | 433.9989 | 370.3092 | 400.9566 | 397.1354 | 374.1929 | 343.1656 | 272.0562
1820.6279 | 1673.6279 | 477.1259 | 357.6301 | 434.0149 | 370.3733 | 401.0102 | 397.1719 | 374.2402 | 343.2369 | 272.1766
1821.6294 | 1674.6294 | 477.0983 | 357.6855 | 434.0276 | 370.4345 | 401.0679 | 397.1087 | 374.2773 | 343.3398 | 272.3113
1822.6308 | 1675.6308 | 476.99 | 357.6868 | 433.9992 | 370.5139 | 401.1456 | 397.1626 | 374.3215 | 343.4119 | 272.4587
1823.6323 | 1676.6323 | 477.009 | 357.7749 | 434.01 | 370.5731 | 401.1848 | 397.2125 | 374.3652 | 343.4497 | 272.5402
1824.6337 | 1677.6337 | 477.1611 | 357.8581 | 434.1158 | 370.6334 | 401.2572 | 397.1507 | 374.4041 | 343.5781 | 272.6555
1825.6251 | 1678.6251 | 477.2726 | 357.936 | 434.2734 | 370.7032 | 401.3184 | 397.0946 | 374.4417 | 343.7249 | 272.6585
1826.6266 | 1679.6266 | 477.1495 | 357.9809 | 434.2017 | 370.7417 | 401.3766 | 397.1526 | 374.4795 | 343.8517 | 272.8054
1827.628 | 1680.628 | 476.9536 | 358.0177 | 434.204 | 370.7957 | 401.4364 | 397.2093 | 374.5339 | 343.958 | 272.9591
1828.6294 | 1681.6294 | 476.9594 | 358.1165 | 434.2767 | 370.8571 | 401.4907 | 397.3055 | 374.5807 | 344.0304 | 273.0849
1829.6309 | 1682.6309 | 477.054 | 358.1879 | 434.2727 | 370.8955 | 401.5508 | 397.3134 | 374.6207 | 344.1044 | 273.198
1830.6323 | 1683.6323 | 477.113 | 358.2408 | 434.2491 | 370.9838 | 401.6136 | 397.4025 | 374.6601 | 344.177 | 273.289
1831.6338 | 1684.6338 | 477.2011 | 358.3 | 434.187 | 371.0186 | 401.6796 | 397.4068 | 374.7015 | 344.3333 | 273.27
1832.6352 | 1685.6352 | 477.2467 | 358.356 | 434.1842 | 371.0461 | 401.7271 | 397.4229 | 374.7492 | 344.5108 | 273.3049
1833.6266 | 1686.6266 | 477.3688 | 358.423 | 434.2938 | 371.0381 | 401.7973 | 397.4384 | 374.7783 | 344.6326 | 273.4293
1834.6281 | 1687.6281 | 477.4216 | 358.5039 | 434.3377 | 371.0746 | 401.847 | 397.442 | 374.8148 | 344.7562 | 273.5061
1835.6295 | 1688.6295 | 477.5101 | 358.5411 | 434.3507 | 371.154 | 401.9212 | 397.5186 | 374.8502 | 344.8452 | 273.6254
1836.6309 | 1689.6309 | 477.5715 | 358.5904 | 434.2741 | 371.2078 | 401.9779 | 397.51 | 374.8955 | 344.9192 | 273.6419
1837.6324 | 1690.6324 | 477.4796 | 358.6222 | 434.3492 | 371.2615 | 402.0397 | 397.5631 | 374.9313 | 344.9699 | 273.7191
1838.6338 | 1691.6338 | 477.4572 | 358.6678 | 434.3302 | 371.3254 | 402.1013 | 397.6079 | 374.9713 | 345.0502 | 273.6974
1839.6353 | 1692.6353 | 477.4366 | 358.7381 | 434.4085 | 371.3684 | 402.165 | 397.7183 | 375.0097 | 345.1881 | 273.7679
1840.6267 | 1693.6267 | 477.4829 | 358.7423 | 434.459 | 371.4318 | 402.2162 | 397.9564 | 375.0511 | 345.2856 | 273.862
1841.6281 | 1694.6281 | 477.414 | 358.8045 | 434.356 | 371.4726 | 402.2764 | 398.2448 | 375.1003 | 345.4316 | 273.9028
1842.6296 | 1695.6296 | 477.3191 | 358.9348 | 434.3494 | 371.5487 | 402.3367 | 398.4374 | 375.1425 | 345.603 | 273.9898
1843.631 | 1696.631 | 477.2714 | 358.9565 | 434.4555 | 371.6496 | 402.3888 | 398.6199 | 375.1823 | 345.6995 | 274.1284
1844.6325 | 1697.6325 | 477.3036 | 359.0049 | 434.505 | 371.7377 | 402.4518 | 398.7625 | 375.217 | 345.7844 | 274.2502
1845.6339 | 1698.6339 | 477.2356 | 359.0345 | 434.4854 | 371.7919 | 402.5061 | 398.9422 | 375.2518 | 345.8664 | 274.38
1846.6253 | 1699.6253 | 477.1547 | 359.1243 | 434.4657 | 371.8578 | 402.5811 | 399.039 | 375.2899 | 345.9098 | 274.4515
1847.6268 | 1700.6268 | 477.121 | 359.2093 | 434.4344 | 371.8961 | 402.6362 | 399.0519 | 375.3339 | 345.9956 | 274.5037
1848.6282 | 1701.6282 | 477.2164 | 359.2793 | 434.4881 | 371.9697 | 402.68 | 399.0245 | 375.3752 | 346.0445 | 274.5569
1849.6296 | 1702.6296 | 477.1938 | 359.3657 | 434.5121 | 371.9998 | 402.7421 | 399.0554 | 375.4189 | 346.1219 | 274.5905
1850.6311 | 1703.6311 | 477.2319 | 359.4093 | 434.5454 | 372.0389 | 402.7893 | 399.0292 | 375.4616 | 346.2916 | 274.6012
1851.6325 | 1704.6325 | 477.2255 | 359.4794 | 434.6298 | 372.073 | 402.8462 | 399.1081 | 375.5004 | 346.4366 | 274.6996
1852.634 | 1705.634 | 477.2492 | 359.5477 | 434.6452 | 372.1423 | 402.8935 | 399.038 | 375.5411 | 346.587 | 274.7914
1853.6254 | 1706.6254 | 477.3026 | 359.5721 | 434.7683 | 372.2192 | 402.951 | 399.0555 | 375.5895 | 346.6807 | 274.8693
1854.6268 | 1707.6268 | 477.4918 | 359.6277 | 434.7732 | 372.2552 | 403.0117 | 399.0489 | 375.6366 | 346.743 | 274.9288
1855.6283 | 1708.6283 | 477.6019 | 359.6613 | 434.7717 | 372.2914 | 403.0732 | 399.0275 | 375.6685 | 346.7067 | 274.9508
1856.6297 | 1709.6297 | 477.5992 | 359.7503 | 434.7788 | 372.3691 | 403.1185 | 399.0045 | 375.7314 | 346.7683 | 274.9943
1857.6311 | 1710.6311 | 477.6664 | 359.8375 | 434.7985 | 372.4408 | 403.1702 | 399.0467 | 375.7763 | 346.8939 | 275.0336
1858.6326 | 1711.6326 | 477.7781 | 359.869 | 434.9556 | 372.464 | 403.2344 | 399.0591 | 375.8202 | 347.07 | 275.0742
1859.634 | 1712.634 | 477.7297 | 359.9349 | 434.9255 | 372.5168 | 403.2812 | 399.1061 | 375.8645 | 347.2306 | 275.1872
1860.6254 | 1713.6254 | 477.7391 | 359.9985 | 434.9283 | 372.5965 | 403.3421 | 399.1838 | 375.909 | 347.3388 | 275.2625
1861.6269 | 1714.6269 | 477.9029 | 360.0353 | 434.9313 | 372.6637 | 403.3959 | 399.3632 | 375.9549 | 347.4233 | 275.3187
1862.6283 | 1715.6283 | 477.8926 | 360.1052 | 434.8414 | 372.6743 | 403.4524 | 399.5488 | 375.9944 | 347.5202 | 275.4121
1863.6298 | 1716.6298 | 477.9977 | 360.1693 | 434.9397 | 372.7415 | 403.4933 | 399.6411 | 376.0401 | 347.5944 | 275.5432
1864.6312 | 1717.6312 | 478.1788 | 360.2441 | 434.9145 | 372.8114 | 403.55 | 399.8205 | 376.0797 | 347.7027 | 275.6471
1865.6326 | 1718.6326 | 478.3595 | 360.2565 | 434.9579 | 372.8801 | 403.6039 | 400.0039 | 376.1198 | 347.8086 | 275.6712
1866.6341 | 1719.6341 | 478.4341 | 360.3571 | 434.9996 | 372.9081 | 403.6786 | 400.0524 | 376.1633 | 347.9084 | 275.7082
1867.6255 | 1720.6255 | 478.3347 | 360.3895 | 435.0317 | 372.9786 | 403.7225 | 400.0697 | 376.1958 | 347.9857 | 275.796
1868.627 | 1721.627 | 478.4012 | 360.4766 | 435.0281 | 373.0141 | 403.7715 | 399.9803 | 376.2501 | 348.1526 | 275.8508
1869.6284 | 1722.6284 | 478.4469 | 360.541 | 435.0313 | 373.0627 | 403.8341 | 399.8845 | 376.2896 | 348.3102 | 275.927
1870.6298 | 1723.6298 | 478.4343 | 360.5944 | 435.061 | 373.1462 | 403.8757 | 399.8303 | 376.3352 | 348.4113 | 276.0548
1871.6313 | 1724.6313 | 478.3869 | 360.6296 | 435.1554 | 373.2129 | 403.9406 | 399.8675 | 376.3834 | 348.466 | 276.1479
1872.6327 | 1725.6327 | 478.4099 | 360.7131 | 435.2272 | 373.2688 | 403.9884 | 399.8471 | 376.4378 | 348.4944 | 276.2021
1873.6342 | 1726.6342 | 478.4211 | 360.7557 | 435.217 | 373.2937 | 404.0457 | 399.8538 | 376.4719 | 348.5489 | 276.3227
1874.6356 | 1727.6356 | 478.3867 | 360.8082 | 435.2287 | 373.3432 | 404.092 | 400.0025 | 376.5214 | 348.5744 | 276.3635
1875.627 | 1728.627 | 478.414 | 360.8857 | 435.2474 | 373.399 | 404.1466 | 400.2291 | 376.5729 | 348.6396 | 276.4621
1876.6285 | 1729.6285 | 478.4184 | 360.9418 | 435.1196 | 373.4636 | 404.189 | 400.4057 | 376.6233 | 348.7849 | 276.5308
1877.6299 | 1730.6299 | 478.3792 | 360.9856 | 435.1177 | 373.5196 | 404.2465 | 400.4413 | 376.6632 | 348.897 | 276.6237
1878.6313 | 1731.6313 | 478.3229 | 361.0477 | 435.1369 | 373.6023 | 404.2891 | 400.4936 | 376.7182 | 348.9559 | 276.6712
1879.6328 | 1732.6328 | 478.2782 | 361.0798 | 435.316 | 373.6407 | 404.3375 | 400.6431 | 376.7731 | 349.0638 | 276.7002
1880.6342 | 1733.6342 | 478.1583 | 361.1064 | 435.2944 | 373.7127 | 404.3964 | 400.6521 | 376.8283 | 349.1512 | 276.7668
1881.6357 | 1734.6357 | 478.0637 | 361.1857 | 435.2136 | 373.752 | 404.4401 | 400.744 | 376.8679 | 349.2622 | 276.843
1882.6271 | 1735.6271 | 477.9018 | 361.2492 | 435.3304 | 373.8119 | 404.4971 | 400.7913 | 376.9122 | 349.3604 | 276.9433
1883.6285 | 1736.6285 | 477.7393 | 361.2442 | 435.4693 | 373.8475 | 404.545 | 400.8896 | 376.9621 | 349.4669 | 276.9565
1884.63 | 1737.63 | 477.6382 | 361.3928 | 435.4394 | 373.9169 | 404.5867 | 400.9097 | 377.0072 | 349.5548 | 277.0416
1885.6314 | 1738.6314 | 477.4892 | 361.4454 | 435.3494 | 373.9343 | 404.6456 | 400.7616 | 377.0586 | 349.5979 | 277.1331
1886.6328 | 1739.6328 | 477.2514 | 361.4739 | 435.4039 | 373.9791 | 404.6841 | 400.7515 | 377.1043 | 349.7262 | 277.1888
1887.6343 | 1740.6343 | 477.1932 | 361.5345 | 435.378 | 374.0321 | 404.7467 | 400.8583 | 377.1602 | 349.8421 | 277.2636
1888.6257 | 1741.6257 | 477.2216 | 361.5615 | 435.4486 | 374.0952 | 404.781 | 400.9281 | 377.2071 | 349.9698 | 277.325
1889.6272 | 1742.6272 | 477.2062 | 361.6282 | 435.4255 | 374.1595 | 404.8281 | 401.0012 | 377.2653 | 350.0896 | 277.4024
1890.6286 | 1743.6286 | 477.0995 | 361.6822 | 435.4429 | 374.2166 | 404.8783 | 401.0736 | 377.3001 | 350.1546 | 277.4665
1891.63 | 1744.63 | 477.0374 | 361.6916 | 435.4796 | 374.2836 | 404.9319 | 401.054 | 377.3573 | 350.2365 | 277.4939
1892.6315 | 1745.6315 | 476.9591 | 361.7491 | 435.5946 | 374.3428 | 405.0042 | 400.9987 | 377.3945 | 350.2416 | 277.5583
1893.6329 | 1746.6329 | 476.9 | 361.8138 | 435.6481 | 374.3714 | 405.0457 | 400.9415 | 377.4591 | 350.3892 | 277.6568
1894.6344 | 1747.6344 | 476.8053 | 361.8758 | 435.5857 | 374.4276 | 405.0923 | 400.9087 | 377.5062 | 350.5753 | 277.6823
1895.6258 | 1748.6258 | 476.9252 | 361.9563 | 435.6739 | 374.4805 | 405.1279 | 400.9426 | 377.5487 | 350.6956 | 277.7769
1896.6272 | 1749.6272 | 476.9607 | 361.962 | 435.664 | 374.5166 | 405.1938 | 400.9422 | 377.6117 | 350.757 | 277.8729
1897.6287 | 1750.6287 | 476.9007 | 362.0537 | 435.6865 | 374.5724 | 405.2364 | 400.9274 | 377.6475 | 350.8354 | 277.9554
1898.6601 | 1751.6601 | 476.8748 | 362.0788 | 435.6159 | 374.6437 | 405.2977 | 400.9047 | 377.7036 | 350.884 | 278.0048
1899.6315 | 1752.6315 | 476.7222 | 362.1289 | 435.5495 | 374.6962 | 405.3353 | 400.9109 | 377.7498 | 350.9333 | 278.0647
1900.633 | 1753.633 | 476.673 | 362.1855 | 435.6089 | 374.7332 | 405.3827 | 400.8784 | 377.8176 | 351.037 | 278.1756
1901.6344 | 1754.6344 | 476.5437 | 362.1915 | 435.5966 | 374.7805 | 405.4302 | 400.8722 | 377.8732 | 351.1632 | 278.2438
1902.6258 | 1755.6258 | 476.5196 | 362.2235 | 435.6377 | 374.8363 | 405.4796 | 400.8488 | 377.9169 | 351.2864 | 278.3633
1903.6273 | 1756.6273 | 476.5684 | 362.3517 | 435.6141 | 374.837 | 405.5295 | 400.8455 | 377.9746 | 351.4394 | 278.3766
1904.6287 | 1757.6287 | 476.5327 | 362.3779 | 435.6666 | 374.8691 | 405.584 | 400.9034 | 378.0207 | 351.505 | 278.429
1905.6302 | 1758.6302 | 476.6427 | 362.4327 | 435.6887 | 374.9161 | 405.6299 | 401.0157 | 378.0694 | 351.5678 | 278.5171
1906.6316 | 1759.6316 | 476.763 | 362.5184 | 435.6728 | 374.9801 | 405.6703 | 401.0063 | 378.1269 | 351.6484 | 278.5964
1907.633 | 1760.633 | 476.7487 | 362.5532 | 435.7191 | 375.0266 | 405.7151 | 401.0481 | 378.1741 | 351.7456 | 278.6602
1908.6345 | 1761.6345 | 476.7935 | 362.5938 | 435.7074 | 375.0786 | 405.7868 | 401.0585 | 378.2266 | 351.8504 | 278.7102
1909.6259 | 1762.6259 | 476.8729 | 362.6541 | 435.6525 | 375.1392 | 405.8275 | 401.1744 | 378.2752 | 351.9934 | 278.7994
1910.6273 | 1763.6273 | 476.837 | 362.7218 | 435.6851 | 375.2188 | 405.8972 | 401.2593 | 378.3309 | 352.0406 | 278.883
1911.6288 | 1764.6288 | 476.7972 | 362.7767 | 435.7296 | 375.2729 | 405.945 | 401.2809 | 378.3853 | 352.1018 | 278.943
1912.6302 | 1765.6302 | 476.8659 | 362.8156 | 435.6646 | 375.3333 | 405.9814 | 401.2688 | 378.4434 | 352.1271 | 279.0403
1913.6317 | 1766.6317 | 476.9338 | 362.845 | 435.707 | 375.3604 | 406.0408 | 401.3314 | 378.4953 | 352.1742 | 279.1282
1914.6331 | 1767.6331 | 477.0003 | 362.9177 | 435.7605 | 375.4319 | 406.0914 | 401.3529 | 378.5427 | 352.2186 | 279.1621
1915.6245 | 1768.6245 | 477.0096 | 362.9615 | 435.7512 | 375.4756 | 406.1286 | 401.312 | 378.5901 | 352.2131 | 279.3057
1916.626 | 1769.626 | 477.0166 | 363.026 | 435.78 | 375.5436 | 406.168 | 401.3316 | 378.6438 | 352.3639 | 279.367
1917.6274 | 1770.6274 | 476.9548 | 363.0376 | 435.8474 | 375.5734 | 406.2276 | 401.4473 | 378.6957 | 352.5273 | 279.4824
1918.6289 | 1771.6289 | 476.8369 | 363.1204 | 435.8325 | 375.6159 | 406.2555 | 401.51 | 378.7364 | 352.7062 | 279.59
1919.6303 | 1772.6303 | 476.7345 | 363.1555 | 435.8187 | 375.6988 | 406.3267 | 401.5171 | 378.7955 | 352.8576 | 279.6489
1920.6317 | 1773.6317 | 476.564 | 363.2506 | 435.8066 | 375.7021 | 406.3681 | 401.6498 | 378.8579 | 352.8811 | 279.7699
1921.6332 | 1774.6332 | 476.6188 | 363.2626 | 435.8677 | 375.7391 | 406.4146 | 401.7413 | 378.9098 | 352.9052 | 279.8118
1922.6346 | 1775.6346 | 476.6242 | 363.348 | 435.7542 | 375.7597 | 406.4656 | 401.7351 | 378.9642 | 352.9611 | 279.9271
1923.626 | 1776.626 | 476.7638 | 363.4083 | 435.7835 | 375.7493 | 406.5235 | 401.763 | 379.0198 | 353.0463 | 280.0102
1924.6275 | 1777.6275 | 476.7899 | 363.4276 | 435.6425 | 375.8211 | 406.5741 | 401.7737 | 379.0741 | 353.1109 | 280.0741
1925.6289 | 1778.6289 | 476.8215 | 363.4454 | 435.8382 | 375.9134 | 406.612 | 401.8435 | 379.1326 | 353.2406 | 280.0975
1926.6304 | 1779.6304 | 476.982 | 363.4561 | 435.8369 | 375.9475 | 406.6585 | 401.8383 | 379.1959 | 353.3842 | 280.2164
1927.6318 | 1780.6318 | 476.9945 | 363.5978 | 435.8296 | 375.9366 | 406.6887 | 401.8184 | 379.2371 | 353.4729 | 280.2583
1928.6633 | 1781.6633 | 477.1539 | 363.6457 | 435.8896 | 376.0313 | 406.7381 | 401.9155 | 379.2957 | 353.4835 | 280.3744
1929.6347 | 1782.6347 | 477.1912 | 363.6914 | 435.8982 | 376.0126 | 406.7971 | 401.9454 | 379.3409 | 353.5486 | 280.4417
1930.6261 | 1783.6261 | 477.2741 | 363.7369 | 435.9567 | 376.0133 | 406.8429 | 401.9508 | 379.3883 | 353.6449 | 280.5072
1931.6275 | 1784.6275 | 477.3883 | 363.7948 | 435.9385 | 376.113 | 406.895 | 401.937 | 379.4436 | 353.766 | 280.5704
1932.629 | 1785.629 | 477.4289 | 363.8471 | 435.9469 | 376.1467 | 406.9365 | 401.9945 | 379.497 | 353.8219 | 280.5916
1933.6304 | 1786.6304 | 477.3612 | 363.9223 | 435.9399 | 376.2527 | 406.9775 | 402.1625 | 379.5496 | 353.8983 | 280.615
1934.6319 | 1787.6319 | 477.4567 | 363.9804 | 435.9994 | 376.3476 | 407.0309 | 402.2535 | 379.5989 | 353.9591 | 280.6575
1935.6333 | 1788.6333 | 477.4528 | 364.0318 | 436.0849 | 376.3438 | 407.086 | 402.2829 | 379.652 | 354.0393 | 280.7555
1936.6347 | 1789.6347 | 477.4712 | 364.0849 | 436.0934 | 376.4272 | 407.1377 | 402.3809 | 379.7032 | 354.0644 | 280.8443
1937.6262 | 1790.6262 | 477.5423 | 364.1127 | 436.0926 | 376.4843 | 407.1944 | 402.4462 | 379.759 | 354.1746 | 280.9086
1938.6276 | 1791.6276 | 477.5911 | 364.169 | 436.1614 | 376.5383 | 407.2468 | 402.4352 | 379.8146 | 354.2176 | 280.9827
1939.629 | 1792.629 | 477.5311 | 364.1869 | 436.1501 | 376.5723 | 407.2937 | 402.5585 | 379.8601 | 354.3522 | 281.1241
1940.6305 | 1793.6305 | 477.5291 | 364.2783 | 436.0429 | 376.6303 | 407.351 | 402.6791 | 379.9157 | 354.3927 | 281.201
1941.6319 | 1794.6319 | 477.4988 | 364.3479 | 436.1352 | 376.7055 | 407.4015 | 402.7154 | 379.9747 | 354.4351 | 281.2518
1942.6334 | 1795.6334 | 477.53 | 364.4152 | 436.2211 | 376.7271 | 407.4552 | 402.6996 | 380.0301 | 354.4898 | 281.3453
1943.6348 | 1796.6348 | 477.5303 | 364.4443 | 436.2202 | 376.7741 | 407.508 | 402.7319 | 380.0784 | 354.5717 | 281.4261
1944.6262 | 1797.6262 | 477.5141 | 364.5247 | 436.2762 | 376.8238 | 407.557 | 402.7398 | 380.1353 | 354.6435 | 281.5676
1945.6277 | 1798.6277 | 477.4484 | 364.5516 | 436.3653 | 376.8851 | 407.6074 | 402.7462 | 380.1936 | 354.7678 | 281.6237
1946.6291 | 1799.6291 | 477.3824 | 364.5877 | 436.2639 | 376.9216 | 407.6519 | 402.8357 | 380.2385 | 354.8908 | 281.698
1947.6306 | 1800.6306 | 477.3369 | 364.6412 | 436.3488 | 376.9896 | 407.7028 | 402.8747 | 380.2935 | 354.9057 | 281.7972
1948.632 | 1801.632 | 477.2925 | 364.6835 | 436.3601 | 377.0309 | 407.7561 | 403.0112 | 380.3459 | 354.99 | 281.8611
1949.6334 | 1802.6334 | 477.3189 | 364.7808 | 436.4495 | 377.0462 | 407.8016 | 403.03 | 380.4038 | 355.0474 | 281.9343
1950.6349 | 1803.6349 | 477.3199 | 364.8026 | 436.4047 | 377.0881 | 407.8514 | 403.0807 | 380.45 | 355.1244 | 281.9872
1951.6263 | 1804.6263 | 477.3268 | 364.8686 | 436.4698 | 377.1626 | 407.8912 | 403.1755 | 380.5149 | 355.2139 | 282.0166
1952.6277 | 1805.6277 | 477.212 | 364.8954 | 436.4053 | 377.2058 | 407.9518 | 403.1308 | 380.5592 | 355.3238 | 282.0796
1953.6292 | 1806.6292 | 477.1945 | 364.9562 | 436.4198 | 377.2313 | 407.9979 | 403.1273 | 380.6171 | 355.3243 | 282.2069
1954.6306 | 1807.6306 | 477.1538 | 364.9861 | 436.4757 | 377.2602 | 408.0576 | 403.1848 | 380.6723 | 355.3866 | 282.2922
1955.6321 | 1808.6321 | 477.1535 | 365.0806 | 436.4485 | 377.336 | 408.1097 | 403.2115 | 380.7272 | 355.4673 | 282.4153
1956.6335 | 1809.6335 | 476.9362 | 365.0868 | 436.3648 | 377.374 | 408.134 | 403.2319 | 380.7799 | 355.5143 | 282.4863
1957.6349 | 1810.6349 | 476.8029 | 365.1823 | 436.4271 | 377.4037 | 408.1983 | 403.2794 | 380.8318 | 355.5525 | 282.5599
1958.6264 | 1811.6264 | 476.8054 | 365.2027 | 436.4617 | 377.4462 | 408.2514 | 403.3298 | 380.8948 | 355.7446 | 282.6358
1959.6278 | 1812.6278 | 476.8721 | 365.2627 | 436.367 | 377.4911 | 408.3114 | 403.4093 | 380.9429 | 355.7912 | 282.7274
1960.6292 | 1813.6292 | 476.8954 | 365.2933 | 436.403 | 377.5578 | 408.3421 | 403.4488 | 381.0002 | 355.7922 | 282.7561
1961.6307 | 1814.6307 | 476.9213 | 365.3215 | 436.4096 | 377.5964 | 408.3929 | 403.5312 | 381.0533 | 355.8356 | 282.8216
1962.6321 | 1815.6321 | 476.9117 | 365.4223 | 436.4953 | 377.6377 | 408.4361 | 403.5991 | 381.1157 | 355.8837 | 282.8671
1963.6336 | 1816.6336 | 476.8283 | 365.4769 | 436.5308 | 377.6867 | 408.4954 | 403.7154 | 381.1744 | 355.9748 | 282.9417
1964.635 | 1817.635 | 476.7124 | 365.4797 | 436.6111 | 377.7457 | 408.5539 | 403.8674 | 381.2257 | 356.0256 | 283.033
1965.6264 | 1818.6264 | 476.7573 | 365.509 | 436.7496 | 377.7502 | 408.5999 | 403.9326 | 381.2886 | 356.0897 | 283.1564
1966.6279 | 1819.6279 | 476.7608 | 365.6321 | 436.7161 | 377.7844 | 408.6549 | 403.9229 | 381.3482 | 356.1897 | 283.2452
1967.6293 | 1820.6293 | 476.9864 | 365.6963 | 436.7011 | 377.8512 | 408.7029 | 403.9312 | 381.4125 | 356.2638 | 283.3104
1968.6308 | 1821.6308 | 477.2425 | 365.7034 | 436.7107 | 377.8831 | 408.7569 | 403.9963 | 381.4735 | 356.3305 | 283.351
1969.6322 | 1822.6322 | 477.3048 | 365.7148 | 436.7521 | 377.9231 | 408.7935 | 404.0515 | 381.5285 | 356.3953 | 283.3797
1970.6336 | 1823.6336 | 477.2661 | 365.7878 | 436.7909 | 377.9996 | 408.8546 | 404.1272 | 381.5898 | 356.48 | 283.4502
1971.6351 | 1824.6351 | 477.3286 | 365.8495 | 436.7386 | 378.026 | 408.912 | 404.182 | 381.6513 | 356.5661 | 283.5502
1972.6265 | 1825.6265 | 477.4215 | 365.9017 | 436.777 | 378.0811 | 408.9709 | 404.2294 | 381.7163 | 356.6083 | 283.6464
1973.6279 | 1826.6279 | 477.5912 | 365.9447 | 436.8088 | 378.1444 | 409.0018 | 404.2954 | 381.768 | 356.6682 | 283.7685
1974.6294 | 1827.6294 | 477.6793 | 365.9737 | 436.7966 | 378.1822 | 409.071 | 404.3653 | 381.8226 | 356.7484 | 283.8785
1975.6308 | 1828.6308 | 477.7394 | 366.0485 | 436.9044 | 378.2209 | 409.1174 | 404.4372 | 381.888 | 356.8108 | 284.0033
1976.6323 | 1829.6323 | 477.9266 | 366.054 | 436.8586 | 378.275 | 409.1764 | 404.5583 | 381.9427 | 356.8675 | 284.0719
1977.6337 | 1830.6337 | 477.9966 | 366.1139 | 436.8499 | 378.2901 | 409.2252 | 404.6397 | 381.999 | 356.9324 | 284.176
1978.6351 | 1831.6351 | 478.0818 | 366.2048 | 436.7947 | 378.2516 | 409.2754 | 404.6762 | 382.0637 | 357.003 | 284.2226
1979.6266 | 1832.6266 | 478.0901 | 366.2438 | 436.8392 | 378.2942 | 409.3338 | 404.7534 | 382.1207 | 357.0807 | 284.2889
1980.628 | 1833.628 | 478.1207 | 366.2901 | 436.9401 | 378.3957 | 409.3768 | 404.845 | 382.1868 | 357.1863 | 284.3853
1981.6294 | 1834.6294 | 478.1201 | 366.3143 | 436.8926 | 378.4723 | 409.4372 | 404.94 | 382.2316 | 357.2051 | 284.4555
1982.6309 | 1835.6309 | 478.1248 | 366.3705 | 436.9054 | 378.4991 | 409.4738 | 404.9477 | 382.2965 | 357.27 | 284.5728
1983.6323 | 1836.6323 | 478.2645 | 366.4571 | 436.971 | 378.5158 | 409.5215 | 404.9837 | 382.3492 | 357.3829 | 284.6471
1984.6338 | 1837.6338 | 478.3637 | 366.5042 | 436.9672 | 378.5972 | 409.5797 | 405.0641 | 382.4183 | 357.407 | 284.7403
1985.6352 | 1838.6352 | 478.3472 | 366.5529 | 436.9682 | 378.6693 | 409.6318 | 405.1085 | 382.4774 | 357.3939 | 284.8323
1986.6266 | 1839.6266 | 478.3085 | 366.6038 | 436.9928 | 378.7357 | 409.6828 | 405.1079 | 382.5413 | 357.514 | 284.9349
1987.6281 | 1840.6281 | 478.2854 | 366.6627 | 436.9529 | 378.7476 | 409.7316 | 405.1333 | 382.5897 | 357.5562 | 285.0409
1988.6295 | 1841.6295 | 478.3448 | 366.707 | 436.9263 | 378.8209 | 409.8018 | 405.2082 | 382.652 | 357.6574 | 285.1066
1989.6309 | 1842.6309 | 478.3109 | 366.7806 | 437.0579 | 378.8263 | 409.8496 | 405.2534 | 382.7064 | 357.7585 | 285.1722
1990.6324 | 1843.6324 | 478.3301 | 366.8217 | 437.0826 | 378.8601 | 409.9083 | 405.3536 | 382.7626 | 357.7899 | 285.2506
1991.6338 | 1844.6338 | 478.3724 | 366.8783 | 437.0224 | 378.8643 | 409.9449 | 405.4219 | 382.8254 | 357.8352 | 285.2937
1992.6253 | 1845.6253 | 478.3396 | 366.9545 | 437.0448 | 378.9358 | 410.0057 | 405.5566 | 382.8826 | 357.8885 | 285.4024
1993.6267 | 1846.6267 | 478.3915 | 366.9689 | 437.0923 | 378.9894 | 410.0646 | 405.6499 | 382.9387 | 357.9556 | 285.5123
1994.6281 | 1847.6281 | 478.4541 | 367.0081 | 437.119 | 378.9975 | 410.1068 | 405.8101 | 383.0005 | 358.029 | 285.6188
1995.6296 | 1848.6296 | 478.4011 | 367.0687 | 437.1954 | 379.0256 | 410.1643 | 405.9067 | 383.0564 | 358.0983 | 285.7068
1996.631 | 1849.631 | 478.3382 | 367.1151 | 437.1698 | 379.0645 | 410.2117 | 405.9569 | 383.1211 | 358.1409 | 285.8039
1997.6325 | 1850.6325 | 478.3975 | 367.1551 | 437.1353 | 379.0901 | 410.2691 | 406.0398 | 383.1773 | 358.1646 | 285.8807
1998.6339 | 1851.6339 | 478.5142 | 367.2069 | 437.2461 | 379.0817 | 410.3239 | 406.1018 | 383.2405 | 358.2357 | 285.9549
1999.6253 | 1852.6253 | 478.5057 | 367.2203 | 437.1841 | 379.1636 | 410.3783 | 406.1358 | 383.3017 | 358.3726 | 286.0215
2000.6268 | 1853.6268 | 478.568 | 367.3315 | 437.2355 | 379.234 | 410.4183 | 406.1871 | 383.3644 | 358.4079 | 286.0837
2001.6282 | 1854.6282 | 478.6226 | 367.3318 | 437.2529 | 379.3096 | 410.4753 | 406.2448 | 383.4211 | 358.4428 | 286.1516
2002.6296 | 1855.6296 | 478.6011 | 367.4219 | 437.2206 | 379.3399 | 410.5223 | 406.2984 | 383.4881 | 358.4784 | 286.2531
2003.6311 | 1856.6311 | 478.5688 | 367.3923 | 437.3092 | 379.3658 | 410.5717 | 406.3699 | 383.5424 | 358.5561 | 286.327
2004.6325 | 1857.6325 | 478.7172 | 367.4615 | 437.3667 | 379.4061 | 410.6195 | 406.4347 | 383.6058 | 358.572 | 286.4234
2005.634 | 1858.634 | 478.7115 | 367.5101 | 437.4042 | 379.4203 | 410.6776 | 406.445 | 383.6747 | 358.6181 | 286.5146
2006.6254 | 1859.6254 | 478.7334 | 367.5449 | 437.3461 | 379.4338 | 410.7249 | 406.5754 | 383.7325 | 358.6621 | 286.5694
2007.6268 | 1860.6268 | 478.6765 | 367.6368 | 437.3008 | 379.5823 | 410.7803 | 406.5852 | 383.7905 | 358.7029 | 286.7027
2008.6283 | 1861.6283 | 478.7332 | 367.7176 | 437.2808 | 379.6207 | 410.8245 | 406.6933 | 383.8593 | 358.8204 | 286.7659
2009.6297 | 1862.6297 | 478.8384 | 367.7519 | 437.2895 | 379.6307 | 410.875 | 406.8157 | 383.915 | 358.9124 | 286.8946
2010.6311 | 1863.6311 | 478.6879 | 367.7974 | 437.3847 | 379.6188 | 410.952 | 406.8345 | 383.9778 | 358.9136 | 286.9554
2011.6326 | 1864.6326 | 478.6649 | 367.8672 | 437.39 | 379.6765 | 410.994 | 406.7973 | 384.0428 | 358.964 | 287.0519
2012.634 | 1865.634 | 478.6905 | 367.9093 | 437.4286 | 379.7685 | 411.0486 | 406.8095 | 384.0986 | 359.0162 | 287.1534
2013.6355 | 1866.6355 | 478.6708 | 367.9968 | 437.543 | 379.8098 | 411.0953 | 406.8815 | 384.1587 | 359.0965 | 287.205
2014.6269 | 1867.6269 | 478.5938 | 368.0362 | 437.487 | 379.8632 | 411.1505 | 407.0173 | 384.218 | 359.1746 | 287.2906
2015.6283 | 1868.6283 | 478.6293 | 368.0618 | 437.5013 | 379.8965 | 411.1982 | 407.0509 | 384.2916 | 359.2152 | 287.3823
2016.6298 | 1869.6298 | 478.6468 | 368.0637 | 437.4236 | 379.9612 | 411.2592 | 407.1304 | 384.3483 | 359.2585 | 287.4447
2017.6312 | 1870.6312 | 478.65 | 368.093 | 437.4778 | 379.9857 | 411.3061 | 407.1307 | 384.414 | 359.2649 | 287.5385
2018.6827 | 1871.6827 | 478.6551 | 368.1946 | 437.5755 | 380.0388 | 411.3527 | 407.1616 | 384.4823 | 359.3113 | 287.5967
2019.6341 | 1872.6341 | 478.6253 | 368.2403 | 437.5203 | 380.0881 | 411.4123 | 407.2223 | 384.5358 | 359.3721 | 287.7061
2020.6255 | 1873.6255 | 478.5916 | 368.2508 | 437.5536 | 380.1693 | 411.4563 | 407.3286 | 384.5911 | 359.4319 | 287.8498
2021.627 | 1874.627 | 478.5511 | 368.3078 | 437.6271 | 380.1632 | 411.4978 | 407.4049 | 384.6512 | 359.5371 | 287.9246
2022.6284 | 1875.6284 | 478.5779 | 368.4003 | 437.6508 | 380.2096 | 411.5426 | 407.3754 | 384.7217 | 359.5929 | 287.9903
2023.6298 | 1876.6298 | 478.6313 | 368.4348 | 437.6697 | 380.2592 | 411.6039 | 407.3578 | 384.7831 | 359.6352 | 288.0914
2024.6313 | 1877.6313 | 478.72 | 368.4807 | 437.7651 | 380.3123 | 411.6344 | 407.3967 | 384.8511 | 359.6373 | 288.1672
2025.6327 | 1878.6327 | 478.8029 | 368.526 | 437.7543 | 380.3745 | 411.7048 | 407.4768 | 384.9207 | 359.7019 | 288.2449
2026.6342 | 1879.6342 | 478.692 | 368.558 | 437.657 | 380.3879 | 411.7491 | 407.4936 | 384.9773 | 359.7903 | 288.2959
2027.6356 | 1880.6356 | 478.5117 | 368.5028 | 437.7195 | 380.4239 | 411.8079 | 407.4951 | 385.0512 | 359.8694 | 288.3435
2028.627 | 1881.627 | 478.4177 | 368.6064 | 437.7223 | 380.4641 | 411.8549 | 407.4521 | 385.1201 | 359.884 | 288.4301
2029.6285 | 1882.6285 | 478.3638 | 368.654 | 437.728 | 380.452 | 411.902 | 407.5498 | 385.1767 | 359.9332 | 288.5372
2030.6299 | 1883.6299 | 478.2891 | 368.7179 | 437.7072 | 380.5412 | 411.942 | 407.6765 | 385.2316 | 359.9704 | 288.6409
2031.6313 | 1884.6313 | 478.1894 | 368.7961 | 437.8158 | 380.5921 | 411.9865 | 407.6989 | 385.3129 | 360.0209 | 288.6848
2032.6328 | 1885.6328 | 478.1585 | 368.8288 | 437.7505 | 380.5933 | 412.0529 | 407.6364 | 385.3717 | 360.0557 | 288.7625
2033.6242 | 1886.6242 | 478.1961 | 368.8243 | 437.8133 | 380.6194 | 412.0966 | 407.6396 | 385.4404 | 360.1187 | 288.8422
2034.6256 | 1887.6256 | 478.1411 | 368.8179 | 437.8712 | 380.7032 | 412.1495 | 407.7598 | 385.4948 | 360.1836 | 288.937
2035.6271 | 1888.6271 | 478.054 | 368.9381 | 437.8534 | 380.7339 | 412.1892 | 407.9261 | 385.5616 | 360.2365 | 288.9755
2036.6285 | 1889.6285 | 477.7912 | 368.9787 | 437.8056 | 380.7928 | 412.2477 | 408.0242 | 385.6302 | 360.3069 | 289.0532
2037.63 | 1890.63 | 477.6051 | 369.0364 | 437.7223 | 380.7997 | 412.2911 | 408.0227 | 385.705 | 360.3315 | 289.141
2038.6314 | 1891.6314 | 477.4879 | 369.1256 | 437.7472 | 380.8184 | 412.342 | 407.9843 | 385.7722 | 360.3685 | 289.2535
2039.6328 | 1892.6328 | 477.4033 | 369.127 | 437.8021 | 380.9101 | 412.3958 | 407.9139 | 385.8418 | 360.3974 | 289.376
2040.6343 | 1893.6343 | 477.2811 | 369.1989 | 437.7305 | 380.9023 | 412.4452 | 407.9163 | 385.9171 | 360.4509 | 289.4651
2041.6257 | 1894.6257 | 477.1774 | 369.2454 | 437.7937 | 380.9191 | 412.4829 | 408.0596 | 385.9824 | 360.4987 | 289.5298
2042.6272 | 1895.6272 | 477.1061 | 369.295 | 437.6902 | 380.946 | 412.5392 | 408.1471 | 386.0558 | 360.5624 | 289.5676
2043.6286 | 1896.6286 | 477.1926 | 369.3208 | 437.8416 | 381.0683 | 412.5817 | 408.1576 | 386.1332 | 360.611 | 289.6607
2044.63 | 1897.63 | 477.1936 | 369.3705 | 437.766 | 381.0884 | 412.6283 | 408.2198 | 386.1995 | 360.5995 | 289.7945
2045.6315 | 1898.6315 | 477.1425 | 369.3632 | 437.8831 | 381.0875 | 412.6754 | 408.3353 | 386.2654 | 360.6906 | 289.8291
2046.6329 | 1899.6329 | 477.0931 | 369.4454 | 437.9274 | 381.124 | 412.7197 | 408.4306 | 386.3401 | 360.7188 | 289.9385
2047.6344 | 1900.6344 | 476.8876 | 369.4712 | 437.8939 | 381.1563 | 412.7622 | 408.5828 | 386.4175 | 360.7169 | 290.0418
2048.6258 | 1901.6258 | 476.8267 | 369.5255 | 437.873 | 381.1779 | 412.7985 | 408.5583 | 386.4825 | 360.7392 | 290.1314
2049.6272 | 1902.6272 | 476.8236 | 369.5287 | 437.8743 | 381.2101 | 412.8416 | 408.5851 | 386.5521 | 360.7765 | 290.199
2050.6287 | 1903.6287 | 476.6897 | 369.5432 | 437.9188 | 381.2346 | 412.891 | 408.6041 | 386.6105 | 360.791 | 290.2989
2051.6301 | 1904.6301 | 476.7441 | 369.547 | 438.053 | 381.3202 | 412.925 | 408.769 | 386.6734 | 360.839 | 290.3845
2052.6315 | 1905.6315 | 476.789 | 369.6549 | 437.9357 | 381.3458 | 412.9785 | 408.7455 | 386.7353 | 360.8769 | 290.5051
2053.633 | 1906.633 | 476.8405 | 369.6679 | 437.9756 | 381.4165 | 413.0163 | 408.6723 | 386.807 | 360.9248 | 290.5837
2054.6344 | 1907.6344 | 476.8468 | 369.7484 | 438.1036 | 381.4207 | 413.0799 | 408.6907 | 386.8566 | 360.9642 | 290.5725
2055.6359 | 1908.6359 | 476.7304 | 369.797 | 437.9704 | 381.4751 | 413.1242 | 408.7196 | 386.9362 | 360.9688 | 290.674
2056.6273 | 1909.6273 | 476.7368 | 369.8503 | 438.0564 | 381.5247 | 413.1796 | 408.7661 | 386.9848 | 361.0164 | 290.7044
2057.6287 | 1910.6287 | 476.9977 | 369.9046 | 438.0787 | 381.6009 | 413.2365 | 408.8171 | 387.0544 | 361.1013 | 290.7788
2058.6302 | 1911.6302 | 477.2694 | 369.9096 | 438.0682 | 381.644 | 413.2872 | 408.9586 | 387.1033 | 361.126 | 290.8785
2059.6316 | 1912.6316 | 477.4266 | 369.9473 | 438.0161 | 381.6948 | 413.3342 | 408.9767 | 387.1697 | 361.1263 | 290.9909
2060.633 | 1913.633 | 477.5194 | 370.0152 | 438.0374 | 381.7125 | 413.3734 | 408.9988 | 387.2378 | 361.2029 | 290.9818
2061.6345 | 1914.6345 | 477.7663 | 370.0831 | 438.0705 | 381.6975 | 413.423 | 409.0187 | 387.296 | 361.2399 | 291.0907
2062.6259 | 1915.6259 | 478.0232 | 370.1133 | 438.1539 | 381.7092 | 413.4695 | 409.0524 | 387.3579 | 361.2691 | 291.2218
2063.6274 | 1916.6274 | 478.1752 | 370.153 | 438.1633 | 381.7599 | 413.5312 | 409.1893 | 387.4202 | 361.3306 | 291.3157
2064.6288 | 1917.6288 | 478.2731 | 370.2075 | 438.1769 | 381.7829 | 413.5809 | 409.1889 | 387.4816 | 361.335 | 291.3633
2065.6302 | 1918.6302 | 478.1518 | 370.2486 | 438.2095 | 381.7985 | 413.6368 | 409.158 | 387.5493 | 361.3518 | 291.4479
2066.6317 | 1919.6317 | 477.9344 | 370.2847 | 438.2549 | 381.8708 | 413.6792 | 409.253 | 387.6149 | 361.4099 | 291.5314
2067.6331 | 1920.6331 | 477.8797 | 370.3488 | 438.2082 | 381.904 | 413.7296 | 409.2642 | 387.6778 | 361.4485 | 291.6415
2068.6346 | 1921.6346 | 477.9006 | 370.3756 | 438.3105 | 381.9487 | 413.7625 | 409.1771 | 387.7507 | 361.4808 | 291.6962
2069.626 | 1922.626 | 477.9595 | 370.416 | 438.3197 | 381.9792 | 413.8245 | 409.1825 | 387.8018 | 361.5368 | 291.7526
2070.6274 | 1923.6274 | 477.8429 | 370.4615 | 438.2666 | 381.9975 | 413.8677 | 409.2061 | 387.8724 | 361.5826 | 291.8503
2071.6289 | 1924.6289 | 477.6295 | 370.4848 | 438.3524 | 382.0371 | 413.9127 | 409.2836 | 387.9323 | 361.6169 | 291.9533
2072.6303 | 1925.6303 | 477.4152 | 370.525 | 438.374 | 382.1088 | 413.9639 | 409.2958 | 387.9976 | 361.6576 | 292.0364
2073.6317 | 1926.6317 | 477.1915 | 370.5617 | 438.3784 | 382.1293 | 414.006 | 409.2578 | 388.0633 | 361.7147 | 292.1345
2074.6332 | 1927.6332 | 477.042 | 370.5929 | 438.3274 | 382.172 | 414.0372 | 409.3427 | 388.1245 | 361.733 | 292.2282
2075.6246 | 1928.6246 | 476.9975 | 370.6281 | 438.3679 | 382.1969 | 414.0782 | 409.4592 | 388.1929 | 361.7782 | 292.3408
2076.626 | 1929.626 | 477.1034 | 370.6552 | 438.3685 | 382.2263 | 414.1268 | 409.4523 | 388.2508 | 361.8404 | 292.4064
2077.6275 | 1930.6275 | 477.0636 | 370.6866 | 438.3582 | 382.2694 | 414.167 | 409.4862 | 388.3172 | 361.8359 | 292.4493
2078.6289 | 1931.6289 | 477.1874 | 370.7597 | 438.4207 | 382.3054 | 414.2134 | 409.5568 | 388.386 | 361.8825 | 292.5279
2079.6304 | 1932.6304 | 477.2337 | 370.7895 | 438.4257 | 382.3302 | 414.2599 | 409.5336 | 388.4508 | 361.9434 | 292.6168
2080.6318 | 1933.6318 | 477.0709 | 370.802 | 438.4422 | 382.355 | 414.3078 | 409.5524 | 388.514 | 361.9737 | 292.7291
2081.6332 | 1934.6332 | 476.8965 | 370.8529 | 438.4849 | 382.3881 | 414.3335 | 409.629 | 388.5727 | 362.0033 | 292.7806
2082.6347 | 1935.6347 | 476.7533 | 370.92 | 438.4139 | 382.435 | 414.3892 | 409.7517 | 388.6365 | 362.0659 | 292.7987
2083.6261 | 1936.6261 | 476.644 | 370.9308 | 438.4356 | 382.4863 | 414.4364 | 409.8154 | 388.6971 | 362.1276 | 292.9031
2084.6275 | 1937.6275 | 476.708 | 370.9871 | 438.4855 | 382.4898 | 414.4901 | 409.7399 | 388.7569 | 362.1604 | 293.0133
2085.629 | 1938.629 | 476.5764 | 371.0225 | 438.4958 | 382.5056 | 414.5557 | 409.7254 | 388.8139 | 362.2051 | 293.0947
2086.6304 | 1939.6304 | 476.5587 | 371.07 | 438.517 | 382.5682 | 414.5929 | 409.8141 | 388.8851 | 362.2331 | 293.1381
2087.6319 | 1940.6319 | 476.5107 | 371.0972 | 438.5289 | 382.6019 | 414.6461 | 409.8655 | 388.9486 | 362.2621 | 293.2553
2088.6333 | 1941.6333 | 476.436 | 371.1138 | 438.4963 | 382.6199 | 414.6921 | 409.9192 | 389.0084 | 362.3319 | 293.3321
2089.6347 | 1942.6347 | 476.3559 | 371.1391 | 438.5286 | 382.6377 | 414.7389 | 410.027 | 389.0685 | 362.3341 | 293.409
2090.6262 | 1943.6262 | 476.3969 | 371.2331 | 438.5246 | 382.6819 | 414.7813 | 410.1535 | 389.1328 | 362.3639 | 293.5028
2091.6276 | 1944.6276 | 476.3409 | 371.2568 | 438.5256 | 382.6934 | 414.8382 | 410.2054 | 389.1839 | 362.4213 | 293.6023
2092.6291 | 1945.6291 | 476.28 | 371.2783 | 438.55 | 382.7631 | 414.8983 | 410.1685 | 389.2466 | 362.4378 | 293.7467
2093.6305 | 1946.6305 | 476.256 | 371.3225 | 438.5264 | 382.7544 | 414.9472 | 410.2136 | 389.311 | 362.5077 | 293.7941
2094.6319 | 1947.6319 | 476.1512 | 371.3521 | 438.5063 | 382.8073 | 414.9917 | 410.2757 | 389.3722 | 362.5319 | 293.9104
2095.6334 | 1948.6334 | 476.2053 | 371.4084 | 438.4876 | 382.8329 | 415.0424 | 410.3321 | 389.4381 | 362.6118 | 293.9624
2096.6348 | 1949.6348 | 476.2091 | 371.4481 | 438.5393 | 382.8946 | 415.0728 | 410.257 | 389.4906 | 362.6518 | 294.0574
2097.6262 | 1950.6262 | 476.1586 | 371.4985 | 438.6092 | 382.9023 | 415.1258 | 410.2365 | 389.5452 | 362.6909 | 294.1268
2098.6277 | 1951.6277 | 476.1317 | 371.5315 | 438.5967 | 382.9192 | 415.1697 | 410.2799 | 389.6109 | 362.7051 | 294.2227
2099.6291 | 1952.6291 | 476.2333 | 371.5829 | 438.6373 | 382.9045 | 415.2297 | 410.3486 | 389.6683 | 362.7618 | 294.2915
2100.6306 | 1953.6306 | 476.2472 | 371.6116 | 438.5225 | 382.938 | 415.2767 | 410.3618 | 389.7263 | 362.7932 | 294.3753
2101.632 | 1954.632 | 476.202 | 371.6096 | 438.5172 | 383.0119 | 415.3401 | 410.3884 | 389.7809 | 362.8326 | 294.4145
2102.6334 | 1955.6334 | 476.1846 | 371.6688 | 438.5564 | 383.0547 | 415.3923 | 410.4887 | 389.8456 | 362.8802 | 294.4921
2103.6349 | 1956.6349 | 476.3306 | 371.6874 | 438.5097 | 383.0932 | 415.4377 | 410.5265 | 389.9086 | 362.8903 | 294.5573
2104.6263 | 1957.6263 | 476.4205 | 371.7808 | 438.5366 | 383.1457 | 415.4939 | 410.4629 | 389.9707 | 362.9549 | 294.5392
2105.6277 | 1958.6277 | 476.3994 | 371.8 | 438.6244 | 383.1774 | 415.5479 | 410.4717 | 390.022 | 363.008 | 294.641
2106.6292 | 1959.6292 | 476.4058 | 371.852 | 438.5552 | 383.2356 | 415.6133 | 410.5373 | 390.0908 | 363.0168 | 294.7719
2107.6306 | 1960.6306 | 476.4678 | 371.8866 | 438.6156 | 383.2593 | 415.645 | 410.597 | 390.1403 | 363.0651 | 294.8439
2108.6321 | 1961.6321 | 476.5642 | 371.9304 | 438.5818 | 383.3016 | 415.7096 | 410.6351 | 390.2 | 363.1107 | 294.9362
2109.6736 | 1962.6736 | 476.6126 | 371.9798 | 438.5858 | 383.3351 | 415.7605 | 410.6684 | 390.2685 | 363.125 | 295.0592
2110.6349 | 1963.6349 | 476.5405 | 372.0037 | 438.5888 | 383.3352 | 415.8138 | 410.6987 | 390.3216 | 363.1853 | 295.0998
2111.6264 | 1964.6264 | 476.4527 | 372.0288 | 438.5984 | 383.4029 | 415.8597 | 410.7048 | 390.3828 | 363.2202 | 295.1951
2112.6278 | 1965.6278 | 476.4494 | 372.0611 | 438.53 | 383.4125 | 415.8956 | 410.6638 | 390.4389 | 363.258 | 295.2777
2113.6292 | 1966.6292 | 476.3329 | 372.0694 | 438.5941 | 383.4321 | 415.9696 | 410.614 | 390.4993 | 363.288 | 295.3703
2114.6307 | 1967.6307 | 476.2781 | 372.1492 | 438.5745 | 383.4746 | 416.0309 | 410.6663 | 390.5625 | 363.2862 | 295.4634
2115.6321 | 1968.6321 | 476.2615 | 372.1942 | 438.5509 | 383.4973 | 416.0676 | 410.697 | 390.6089 | 363.3146 | 295.523
2116.6236 | 1969.6236 | 476.2668 | 372.2255 | 438.606 | 383.5193 | 416.1146 | 410.7056 | 390.6698 | 363.3935 | 295.5708
2117.625 | 1970.625 | 476.3862 | 372.2228 | 438.6829 | 383.5563 | 416.1556 | 410.7156 | 390.7237 | 363.4323 | 295.6447
2118.6264 | 1971.6264 | 476.3532 | 372.2179 | 438.77 | 383.5779 | 416.2064 | 410.7344 | 390.7755 | 363.4619 | 295.7051
2119.6279 | 1972.6279 | 476.3014 | 372.267 | 438.7764 | 383.6231 | 416.2608 | 410.7765 | 390.8399 | 363.4991 | 295.7773
2120.6293 | 1973.6293 | 476.3041 | 372.3537 | 438.7897 | 383.6336 | 416.2841 | 410.8374 | 390.8997 | 363.5382 | 295.855
2121.6508 | 1974.6508 | 476.3543 | 372.4288 | 438.8045 | 383.6922 | 416.3381 | 410.8423 | 390.9565 | 363.5818 | 295.9199
2122.6322 | 1975.6322 | 476.34 | 372.4632 | 438.7892 | 383.7219 | 416.4039 | 410.8177 | 391.013 | 363.5935 | 296.0306
2123.6336 | 1976.6336 | 476.4517 | 372.5049 | 438.7883 | 383.7383 | 416.4355 | 410.8672 | 391.0674 | 363.6563 | 296.0586
2124.6351 | 1977.6351 | 476.7145 | 372.5348 | 438.7881 | 383.8037 | 416.4922 | 410.9824 | 391.1366 | 363.6801 | 296.1891
2125.6265 | 1978.6265 | 476.8819 | 372.5921 | 438.8215 | 383.8365 | 416.5287 | 411.0189 | 391.1852 | 363.71 | 296.2489
2126.6279 | 1979.6279 | 476.9111 | 372.5793 | 438.8515 | 383.8441 | 416.5811 | 411.0122 | 391.2455 | 363.7294 | 296.3706
2127.6294 | 1980.6294 | 477.0467 | 372.6379 | 438.9049 | 383.9018 | 416.62 | 410.9945 | 391.2975 | 363.7961 | 296.374
2128.6308 | 1981.6308 | 476.9133 | 372.6356 | 438.8911 | 383.9239 | 416.6647 | 411.0556 | 391.344 | 363.8324 | 296.4581
2129.6323 | 1982.6323 | 476.9155 | 372.7188 | 438.827 | 383.9479 | 416.7093 | 411.1009 | 391.4008 | 363.8603 | 296.5689
2130.6337 | 1983.6337 | 477.0051 | 372.7538 | 438.8958 | 384.0084 | 416.7646 | 411.1296 | 391.4583 | 363.9364 | 296.6396
2131.6351 | 1984.6351 | 477.0568 | 372.7379 | 438.9433 | 384.0016 | 416.8049 | 411.1199 | 391.513 | 363.9766 | 296.7324
2132.6266 | 1985.6266 | 477.19 | 372.8404 | 438.9014 | 384.0944 | 416.8551 | 411.1324 | 391.5655 | 364.0031 | 296.8014
2133.628 | 1986.628 | 477.3208 | 372.8431 | 438.9018 | 384.14 | 416.9069 | 411.141 | 391.6188 | 364.0422 | 296.916
2134.6294 | 1987.6294 | 477.3573 | 372.9182 | 438.907 | 384.1309 | 416.9504 | 411.1617 | 391.6745 | 364.0957 | 296.9462
2135.6309 | 1988.6309 | 477.4188 | 372.946 | 438.9165 | 384.167 | 417.0082 | 411.2403 | 391.7226 | 364.1106 | 297.043
2136.6323 | 1989.6323 | 477.4766 | 372.9889 | 438.9062 | 384.1951 | 417.039 | 411.2514 | 391.7832 | 364.1506 | 297.1392
2137.6338 | 1990.6338 | 477.4531 | 373.0465 | 438.9968 | 384.1684 | 417.0943 | 411.3014 | 391.838 | 364.2022 | 297.2166
2138.6352 | 1991.6352 | 477.5513 | 373.0826 | 438.8709 | 384.1464 | 417.1449 | 411.3341 | 391.8889 | 364.2689 | 297.3376
2139.6266 | 1992.6266 | 477.661 | 373.1441 | 438.935 | 384.1988 | 417.1828 | 411.3678 | 391.9401 | 364.2948 | 297.3978
2140.6281 | 1993.6281 | 477.7465 | 373.1707 | 438.8629 | 384.2602 | 417.2332 | 411.3789 | 391.9942 | 364.3233 | 297.495
2141.6295 | 1994.6295 | 477.8933 | 373.2078 | 438.9269 | 384.3003 | 417.2723 | 411.3799 | 392.05 | 364.3316 | 297.5955
2142.631 | 1995.631 | 478.0434 | 373.2638 | 439.0799 | 384.2995 | 417.3159 | 411.4088 | 392.0993 | 364.375 | 297.6373
2143.6324 | 1996.6324 | 478.2581 | 373.274 | 439.1484 | 384.2111 | 417.3677 | 411.4381 | 392.1526 | 364.4122 | 297.6725
2144.6338 | 1997.6338 | 478.3033 | 373.3231 | 439.1458 | 384.353 | 417.4093 | 411.4501 | 392.1991 | 364.4695 | 297.7651
2145.6253 | 1998.6253 | 478.3292 | 373.3625 | 439.173 | 384.4215 | 417.4591 | 411.4963 | 392.2511 | 364.4931 | 297.8891
2146.6267 | 1999.6267 | 478.437 | 373.346 | 439.0786 | 384.3914 | 417.5015 | 411.5045 | 392.308 | 364.5451 | 297.9391
2147.6281 | 2000.6281 | 478.4893 | 373.4585 | 439.0826 | 384.4756 | 417.5418 | 411.506 | 392.3586 | 364.563 | 298.0408
2148.6296 | 2001.6296 | 478.4148 | 373.4889 | 439.16 | 384.4482 | 417.5977 | 411.5054 | 392.4059 | 364.5658 | 298.1366
2149.631 | 2002.631 | 478.3841 | 373.4722 | 439.1865 | 384.5523 | 417.6425 | 411.5074 | 392.4539 | 364.6694 | 298.1576
2150.6325 | 2003.6325 | 478.2921 | 373.5138 | 439.1882 | 384.595 | 417.6785 | 411.4994 | 392.5061 | 364.6986 | 298.1881
2151.6339 | 2004.6339 | 478.2081 | 373.5367 | 439.1545 | 384.6654 | 417.7235 | 411.4947 | 392.5588 | 364.7277 | 298.2652
2152.6353 | 2005.6353 | 478.2808 | 373.6195 | 439.2195 | 384.6915 | 417.76 | 411.4847 | 392.6212 | 364.7547 | 298.3719
2153.6268 | 2006.6268 | 478.2643 | 373.6727 | 439.1164 | 384.7179 | 417.8054 | 411.4864 | 392.6691 | 364.8006 | 298.4719
2154.6282 | 2007.6282 | 478.2486 | 373.6684 | 439.2333 | 384.7528 | 417.8417 | 411.4675 | 392.7204 | 364.8229 | 298.5363
2155.6296 | 2008.6296 | 478.1592 | 373.7335 | 439.1824 | 384.7636 | 417.8856 | 411.4553 | 392.7722 | 364.8483 | 298.5828
2156.6311 | 2009.6311 | 478.0772 | 373.775 | 439.2613 | 384.8195 | 417.9234 | 411.4559 | 392.8394 | 364.9046 | 298.6842
2157.6325 | 2010.6325 | 478.0874 | 373.8278 | 439.2404 | 384.8524 | 417.9786 | 411.4604 | 392.8778 | 364.9509 | 298.7882
2158.634 | 2011.634 | 478.1947 | 373.8285 | 439.2779 | 384.8784 | 418.0149 | 411.4446 | 392.9319 | 365.0195 | 298.8338
2159.6254 | 2012.6254 | 478.3195 | 373.9064 | 439.201 | 384.8856 | 418.0797 | 411.45 | 392.9721 | 365.0564 | 298.8765
2160.6268 | 2013.6268 | 478.3854 | 373.909 | 439.2593 | 384.9244 | 418.1059 | 411.4776 | 393.0237 | 365.0872 | 298.9737
2161.6283 | 2014.6283 | 478.5168 | 373.9771 | 439.2697 | 384.9736 | 418.1528 | 411.4882 | 393.0724 | 365.0902 | 299.0673
2162.6297 | 2015.6297 | 478.5183 | 373.9987 | 439.3614 | 385.0054 | 418.195 | 411.5167 | 393.1213 | 365.1531 | 299.1343
2163.6311 | 2016.6311 | 478.4835 | 374.0255 | 439.2736 | 385.0423 | 418.2363 | 411.5235 | 393.1675 | 365.1967 | 299.2312
2164.6326 | 2017.6326 | 478.3612 | 374.0775 | 439.3437 | 385.0789 | 418.2793 | 411.517 | 393.2157 | 365.2438 | 299.3017
2165.624 | 2018.624 | 478.2587 | 374.067 | 439.3288 | 385.0822 | 418.3281 | 411.5153 | 393.2745 | 365.2912 | 299.3377
2166.6255 | 2019.6255 | 478.3326 | 374.1196 | 439.3225 | 385.1357 | 418.3737 | 411.5586 | 393.3184 | 365.3366 | 299.3692
2167.6269 | 2020.6269 | 478.2015 | 374.153 | 439.2955 | 385.1334 | 418.4203 | 411.5767 | 393.367 | 365.3464 | 299.4502
2168.6283 | 2021.6283 | 478.1154 | 374.1908 | 439.3537 | 385.202 | 418.4605 | 411.6472 | 393.3997 | 365.3854 | 299.5566
2169.6298 | 2022.6298 | 478.07 | 374.2014 | 439.4054 | 385.2271 | 418.5042 | 411.7315 | 393.4495 | 365.443 | 299.6562
2170.6312 | 2023.6312 | 477.9466 | 374.262 | 439.3273 | 385.2887 | 418.5605 | 411.7628 | 393.4997 | 365.4757 | 299.7705
2171.6327 | 2024.6327 | 477.8379 | 374.3032 | 439.4839 | 385.2643 | 418.5958 | 411.7921 | 393.5462 | 365.5165 | 299.8519
2172.6341 | 2025.6341 | 477.7329 | 374.3547 | 439.45 | 385.3045 | 418.6213 | 411.8244 | 393.5835 | 365.5658 | 299.9425
2173.6255 | 2026.6255 | 477.6449 | 374.3354 | 439.479 | 385.3183 | 418.6688 | 411.8458 | 393.6346 | 365.6155 | 300.029
2174.627 | 2027.627 | 477.5375 | 374.3849 | 439.42 | 385.3555 | 418.7225 | 411.8605 | 393.6906 | 365.6578 | 300.0712
2175.6284 | 2028.6284 | 477.45 | 374.4453 | 439.4513 | 385.3855 | 418.7667 | 411.8879 | 393.7345 | 365.7128 | 300.1508
2176.6298 | 2029.6298 | 477.2845 | 374.4705 | 439.4328 | 385.4251 | 418.8032 | 411.9152 | 393.7838 | 365.7503 | 300.2361
2177.6313 | 2030.6313 | 477.0041 | 374.4964 | 439.4221 | 385.4446 | 418.8541 | 411.958 | 393.8284 | 365.7996 | 300.2516
2178.6327 | 2031.6327 | 476.8676 | 374.5367 | 439.4435 | 385.4531 | 418.8964 | 411.9918 | 393.8826 | 365.8488 | 300.2726
2179.6342 | 2032.6342 | 476.7932 | 374.5744 | 439.4306 | 385.5151 | 418.9386 | 412.0097 | 393.9151 | 365.8979 | 300.3801
2180.6356 | 2033.6356 | 476.7445 | 374.5841 | 439.4699 | 385.5601 | 418.9852 | 412.0087 | 393.9677 | 365.9553 | 300.4856
2181.627 | 2034.627 | 476.6216 | 374.5838 | 439.4772 | 385.5763 | 419.0252 | 412.019 | 394.0108 | 365.9913 | 300.6044
2182.6285 | 2035.6285 | 476.5894 | 374.5936 | 439.4952 | 385.5888 | 419.0676 | 412.0391 | 394.0563 | 366.0367 | 300.6796
2183.6299 | 2036.6299 | 476.6692 | 374.6563 | 439.5244 | 385.6112 | 419.1153 | 412.0794 | 394.1103 | 366.0517 | 300.7782
2184.6313 | 2037.6313 | 476.6692 | 374.6935 | 439.5106 | 385.642 | 419.1612 | 412.0864 | 394.1582 | 366.1202 | 300.8467
2185.6328 | 2038.6328 | 476.5738 | 374.7336 | 439.5063 | 385.6643 | 419.1864 | 412.1132 | 394.1978 | 366.1445 | 300.941
2186.6342 | 2039.6342 | 476.5366 | 374.7896 | 439.6074 | 385.6461 | 419.2332 | 412.1406 | 394.2402 | 366.2175 | 300.9507
2187.6357 | 2040.6357 | 476.5252 | 374.7654 | 439.5585 | 385.7316 | 419.2614 | 412.1758 | 394.2873 | 366.2625 | 301.0007
2188.6271 | 2041.6271 | 476.5111 | 374.842 | 439.5593 | 385.7578 | 419.3046 | 412.2347 | 394.3355 | 366.2815 | 301.1219
2189.6285 | 2042.6285 | 476.4817 | 374.8855 | 439.3826 | 385.7843 | 419.3507 | 412.2664 | 394.3883 | 366.3169 | 301.1722
2190.63 | 2043.63 | 476.573 | 374.8861 | 439.4946 | 385.8041 | 419.4013 | 412.3085 | 394.4249 | 366.3913 | 301.204
2191.6314 | 2044.6314 | 476.6223 | 374.9621 | 439.4214 | 385.8483 | 419.4444 | 412.3518 | 394.4672 | 366.4109 | 301.3082
2192.6329 | 2045.6329 | 476.6575 | 374.9801 | 439.3821 | 385.881 | 419.4816 | 412.3913 | 394.5103 | 366.4638 | 301.4028
2193.6343 | 2046.6343 | 476.8351 | 374.9962 | 439.4168 | 385.8892 | 419.535 | 412.4272 | 394.5548 | 366.5365 | 301.4646
2194.6257 | 2047.6257 | 476.9396 | 375.0592 | 439.4727 | 385.9233 | 419.577 | 412.4684 | 394.5991 | 366.5793 | 301.5779
2195.6272 | 2048.6272 | 476.9377 | 375.1029 | 439.5101 | 385.9423 | 419.6171 | 412.5022 | 394.6374 | 366.6042 | 301.6321
2196.6286 | 2049.6286 | 476.9202 | 375.1586 | 439.5141 | 385.9707 | 419.6666 | 412.4987 | 394.6788 | 366.6405 | 301.7431
2197.63 | 2050.63 | 476.7736 | 375.1668 | 439.5305 | 386.0047 | 419.7069 | 412.5312 | 394.7326 | 366.695 | 301.7407
2198.6315 | 2051.6315 | 476.9108 | 375.1767 | 439.5797 | 386.0325 | 419.7483 | 412.539 | 394.7803 | 366.7213 | 301.8009
2199.6329 | 2052.6329 | 476.9558 | 375.2305 | 439.5409 | 386.0593 | 419.7979 | 412.5605 | 394.8256 | 366.7647 | 301.8633
2200.6344 | 2053.6344 | 476.8976 | 375.2871 | 439.4589 | 386.0764 | 419.8194 | 412.603 | 394.8671 | 366.8207 | 301.9367
2201.6258 | 2054.6258 | 476.7673 | 375.3215 | 439.6027 | 386.0874 | 419.8733 | 412.6221 | 394.916 | 366.8485 | 302.0437
2202.6272 | 2055.6272 | 476.5855 | 375.3363 | 439.6196 | 386.0843 | 419.9031 | 412.6573 | 394.9536 | 366.901 | 302.0928
2203.6287 | 2056.6287 | 476.5564 | 375.3735 | 439.6529 | 386.1434 | 419.9302 | 412.6659 | 394.9941 | 366.9478 | 302.096
2204.6301 | 2057.6301 | 476.5879 | 375.4439 | 439.6309 | 386.1743 | 419.9816 | 412.7057 | 395.0331 | 366.9722 | 302.1611
2205.6315 | 2058.6315 | 476.5847 | 375.4321 | 439.7135 | 386.224 | 420.0357 | 412.6825 | 395.0856 | 367.0212 | 302.2557
2206.633 | 2059.633 | 476.5934 | 375.4834 | 439.5279 | 386.2476 | 420.0964 | 412.6898 | 395.1248 | 367.0637 | 302.3391
2207.6244 | 2060.6244 | 476.5811 | 375.5182 | 439.5769 | 386.2689 | 420.1133 | 412.6925 | 395.161 | 367.0842 | 302.4075
2208.6258 | 2061.6258 | 476.5897 | 375.546 | 439.6534 | 386.2976 | 420.1609 | 412.6998 | 395.201 | 367.1282 | 302.5206
2209.6273 | 2062.6273 | 476.6427 | 375.5861 | 439.6239 | 386.3306 | 420.2122 | 412.7007 | 395.2461 | 367.1962 | 302.5923
2210.6287 | 2063.6287 | 476.6118 | 375.5815 | 439.6777 | 386.3596 | 420.2562 | 412.6951 | 395.2886 | 367.2368 | 302.675
2211.6302 | 2064.6302 | 476.7893 | 375.6415 | 439.6696 | 386.4106 | 420.3053 | 412.7087 | 395.3281 | 367.291 | 302.7687
2212.6316 | 2065.6316 | 476.806 | 375.6502 | 439.6967 | 386.4431 | 420.3457 | 412.7155 | 395.3684 | 367.3401 | 302.8105
2213.633 | 2066.633 | 476.7599 | 375.7043 | 439.6442 | 386.4183 | 420.3923 | 412.7206 | 395.4147 | 367.3952 | 302.8601
2214.6345 | 2067.6345 | 476.7754 | 375.7645 | 439.7035 | 386.4266 | 420.4367 | 412.704 | 395.46 | 367.4352 | 302.9188
2215.6259 | 2068.6259 | 476.8099 | 375.7842 | 439.7077 | 386.4275 | 420.4678 | 412.7033 | 395.5005 | 367.4867 | 302.9921
2216.6274 | 2069.6274 | 476.7958 | 375.8219 | 439.6288 | 386.4501 | 420.5158 | 412.7105 | 395.5421 | 367.5224 | 303.0907
2217.6288 | 2070.6288 | 476.846 | 375.7956 | 439.6938 | 386.4803 | 420.5583 | 412.7475 | 395.5853 | 367.5784 | 303.1385
2218.6302 | 2071.6302 | 476.8013 | 375.8096 | 439.7342 | 386.4603 | 420.5802 | 412.7701 | 395.6298 | 367.6173 | 303.229
2219.6317 | 2072.6317 | 476.7603 | 375.8383 | 439.7797 | 386.4511 | 420.6204 | 412.7862 | 395.6681 | 367.678 | 303.2425
2220.6331 | 2073.6331 | 476.8607 | 375.8988 | 439.7307 | 386.5376 | 420.6447 | 412.7938 | 395.7061 | 367.7179 | 303.2585
2221.6245 | 2074.6245 | 476.8937 | 375.8971 | 439.7562 | 386.55 | 420.6865 | 412.8021 | 395.7454 | 367.7641 | 303.3129
2222.626 | 2075.626 | 476.9164 | 375.9385 | 439.8786 | 386.6038 | 420.7174 | 412.8026 | 395.7862 | 367.7965 | 303.4249
2223.6274 | 2076.6274 | 476.8469 | 376.0255 | 439.8861 | 386.5273 | 420.7626 | 412.8214 | 395.8301 | 367.859 | 303.4944
2224.6289 | 2077.6289 | 476.7084 | 376.0599 | 439.9229 | 386.6307 | 420.805 | 412.8349 | 395.8687 | 367.9152 | 303.5621
2225.6303 | 2078.6303 | 476.6505 | 376.0761 | 439.7208 | 386.7016 | 420.8496 | 412.8197 | 395.9028 | 367.9662 | 303.6656
2226.6317 | 2079.6317 | 476.6126 | 376.0831 | 439.711 | 386.7028 | 420.8948 | 412.8095 | 395.9486 | 368.0052 | 303.7365
2227.6332 | 2080.6332 | 476.6941 | 376.1627 | 439.714 | 386.7434 | 420.9308 | 412.8221 | 395.9826 | 368.0628 | 303.7411
2228.6346 | 2081.6346 | 476.7438 | 376.1612 | 439.7301 | 386.7576 | 420.9715 | 412.8193 | 396.0295 | 368.0852 | 303.7817
2229.626 | 2082.626 | 476.9106 | 376.2253 | 439.9051 | 386.7247 | 421.0144 | 412.8211 | 396.0606 | 368.1399 | 303.8476
2230.6275 | 2083.6275 | 476.9967 | 376.2475 | 439.9093 | 386.7681 | 421.0464 | 412.8283 | 396.1008 | 368.1877 | 303.9342
2231.6289 | 2084.6289 | 477.1278 | 376.2671 | 439.9436 | 386.753 | 421.062 | 412.8234 | 396.1394 | 368.2348 | 304.0011
2232.6304 | 2085.6304 | 477.0828 | 376.3266 | 439.9079 | 386.7533 | 421.1005 | 412.8365 | 396.1701 | 368.2736 | 304.0916
2233.6318 | 2086.6318 | 477.0498 | 376.3711 | 439.8407 | 386.8245 | 421.1378 | 412.8325 | 396.2182 | 368.2917 | 304.1421
2234.6332 | 2087.6332 | 477.1757 | 376.3954 | 439.9477 | 386.8614 | 421.161 | 412.8359 | 396.2505 | 368.3511 | 304.199
2235.6347 | 2088.6347 | 477.1398 | 376.4697 | 439.932 | 386.9166 | 421.1936 | 412.8544 | 396.2844 | 368.3806 | 304.3614
2236.6261 | 2089.6261 | 477.1134 | 376.4591 | 439.9226 | 386.9246 | 421.2162 | 412.8508 | 396.3265 | 368.4222 | 304.3961
2237.6276 | 2090.6276 | 477.2115 | 376.4887 | 439.9739 | 386.9609 | 421.2252 | 412.8714 | 396.363 | 368.4831 | 304.4607
2238.629 | 2091.629 | 477.2709 | 376.5542 | 439.9265 | 386.9481 | 421.2631 | 412.862 | 396.4003 | 368.5506 | 304.5612
2239.6304 | 2092.6304 | 477.3871 | 376.5929 | 440.0008 | 386.9872 | 421.3045 | 412.8828 | 396.4289 | 368.5725 | 304.63
2240.6319 | 2093.6319 | 477.4095 | 376.6397 | 440.0489 | 387.0549 | 421.3439 | 412.8937 | 396.4785 | 368.6245 | 304.7306
2241.6333 | 2094.6333 | 477.3369 | 376.6329 | 440.0386 | 387.1056 | 421.3847 | 412.9093 | 396.5077 | 368.6606 | 304.7947
2242.6348 | 2095.6348 | 477.3395 | 376.6195 | 440.0195 | 387.1185 | 421.4369 | 412.9219 | 396.5423 | 368.718 | 304.8494
2243.6262 | 2096.6262 | 477.4767 | 376.6528 | 440.0828 | 387.1633 | 421.478 | 412.9268 | 396.5806 | 368.772 | 304.9001
2244.6276 | 2097.6276 | 477.7391 | 376.6831 | 440.0522 | 387.1895 | 421.5149 | 412.9366 | 396.6163 | 368.8109 | 304.9682
2245.6291 | 2098.6291 | 477.8947 | 376.7816 | 440.0619 | 387.239 | 421.5418 | 412.9566 | 396.658 | 368.8492 | 305.0758
2246.6305 | 2099.6305 | 477.8377 | 376.8178 | 440.0866 | 387.2992 | 421.5775 | 412.9664 | 396.6941 | 368.9068 | 305.1214
2247.6319 | 2100.6319 | 477.7615 | 376.8629 | 440.0691 | 387.3116 | 421.6023 | 412.9507 | 396.7371 | 368.9383 | 305.2608
2248.6334 | 2101.6334 | 477.7185 | 376.8817 | 440.0515 | 387.3175 | 421.6484 | 412.9598 | 396.7619 | 368.9936 | 305.3184
2249.6248 | 2102.6248 | 477.641 | 376.9308 | 440.041 | 387.3099 | 421.6713 | 412.9611 | 396.8025 | 369.0469 | 305.3546
2250.6262 | 2103.6262 | 477.6012 | 376.9273 | 440.0084 | 387.3551 | 421.7131 | 412.996 | 396.844 | 369.094 | 305.4246
2251.6277 | 2104.6277 | 477.6225 | 376.9622 | 440.0009 | 387.3766 | 421.7466 | 413.0167 | 396.879 | 369.1369 | 305.4682
2252.6291 | 2105.6291 | 477.6346 | 376.9773 | 439.9919 | 387.4166 | 421.7769 | 413.0502 | 396.9126 | 369.1774 | 305.4672
2253.6306 | 2106.6306 | 477.6988 | 377.0429 | 440.0991 | 387.4164 | 421.8374 | 413.0397 | 396.9428 | 369.2215 | 305.5625
2254.632 | 2107.632 | 477.6403 | 377.063 | 440.0797 | 387.4938 | 421.8949 | 413.0073 | 396.9795 | 369.2638 | 305.6497
2255.6334 | 2108.6334 | 477.4794 | 377.0945 | 440.1305 | 387.5103 | 421.9269 | 413.0152 | 397.0184 | 369.3067 | 305.6582
2256.6349 | 2109.6349 | 477.2916 | 377.0744 | 440.0582 | 387.5179 | 421.9704 | 413.0365 | 397.0476 | 369.3558 | 305.7439
2257.6263 | 2110.6263 | 477.2031 | 377.1156 | 440.0543 | 387.5101 | 422.0149 | 413.0639 | 397.0948 | 369.4152 | 305.8347
2258.6277 | 2111.6277 | 477.1323 | 377.1279 | 440.0388 | 387.5389 | 422.0357 | 413.0709 | 397.1285 | 369.4566 | 305.9156
2259.6292 | 2112.6292 | 477.1561 | 377.1195 | 440.0601 | 387.5665 | 422.0633 | 413.0824 | 397.1683 | 369.4981 | 305.9734
2260.6306 | 2113.6306 | 477.2168 | 377.2103 | 440.1194 | 387.6029 | 422.104 | 413.0833 | 397.196 | 369.5264 | 305.978
2261.6321 | 2114.6321 | 477.3889 | 377.2698 | 440.1085 | 387.6129 | 422.1311 | 413.0951 | 397.2289 | 369.543 | 306.0401
2262.6335 | 2115.6335 | 477.4993 | 377.3514 | 440.1447 | 387.6621 | 422.1768 | 413.1061 | 397.2657 | 369.5857 | 306.1211
2263.6349 | 2116.6349 | 477.5037 | 377.3882 | 440.1681 | 387.6897 | 422.2163 | 413.1388 | 397.2956 | 369.6579 | 306.1806
2264.6264 | 2117.6264 | 477.5521 | 377.3733 | 440.1354 | 387.7156 | 422.2443 | 413.147 | 397.3314 | 369.7027 | 306.27
2265.6278 | 2118.6278 | 477.5504 | 377.39 | 440.1782 | 387.7529 | 422.2674 | 413.1424 | 397.3758 | 369.7491 | 306.3619
2266.6293 | 2119.6293 | 477.5568 | 377.4726 | 440.1612 | 387.7933 | 422.3019 | 413.1332 | 397.4055 | 369.778 | 306.4651
2267.6307 | 2120.6307 | 477.4192 | 377.4807 | 440.1422 | 387.8201 | 422.3277 | 413.1388 | 397.4497 | 369.8458 | 306.5123
2268.6321 | 2121.6321 | 477.3371 | 377.4978 | 440.2385 | 387.8365 | 422.3791 | 413.1515 | 397.4752 | 369.8942 | 306.5758
2269.6336 | 2122.6336 | 477.237 | 377.5366 | 440.2401 | 387.9073 | 422.392 | 413.1408 | 397.515 | 369.937 | 306.6335
2270.635 | 2123.635 | 477.0804 | 377.468 | 440.219 | 387.8923 | 422.4321 | 413.1697 | 397.5444 | 369.9731 | 306.7366
2271.6264 | 2124.6264 | 477.0126 | 377.5616 | 440.0525 | 387.8713 | 422.4522 | 413.1737 | 397.5754 | 369.9978 | 306.7714
2272.6279 | 2125.6279 | 477.0693 | 377.6038 | 440.0934 | 387.9213 | 422.4767 | 413.175 | 397.6181 | 370.0638 | 306.8483
2273.6293 | 2126.6293 | 477.0126 | 377.6572 | 440.0529 | 387.8805 | 422.5091 | 413.1603 | 397.6551 | 370.1137 | 306.849
2274.6308 | 2127.6308 | 476.8976 | 377.6562 | 440.1761 | 387.9232 | 422.5247 | 413.1807 | 397.6912 | 370.1521 | 306.9306
2275.6322 | 2128.6322 | 476.8588 | 377.6824 | 440.254 | 387.9815 | 422.5471 | 413.1772 | 397.7295 | 370.2106 | 306.9327
2276.6336 | 2129.6336 | 476.9303 | 377.6834 | 440.1862 | 387.9193 | 422.5709 | 413.1893 | 397.7556 | 370.2366 | 307.0169
2277.6351 | 2130.6351 | 476.9312 | 377.7192 | 440.1404 | 387.9771 | 422.5911 | 413.2006 | 397.7918 | 370.2894 | 307.1158
2278.6265 | 2131.6265 | 476.9177 | 377.7147 | 440.3668 | 387.9447 | 422.6067 | 413.2193 | 397.8264 | 370.336 | 307.2184
2279.6279 | 2132.6279 | 476.8519 | 377.7764 | 440.2816 | 387.9996 | 422.6448 | 413.2194 | 397.8671 | 370.3832 | 307.2529
2280.6294 | 2133.6294 | 476.8975 | 377.81 | 440.2266 | 388.0535 | 422.654 | 413.2156 | 397.9013 | 370.4057 | 307.3397
2281.6308 | 2134.6308 | 476.8161 | 377.8866 | 440.327 | 388.1035 | 422.6929 | 413.2227 | 397.9351 | 370.442 | 307.4161
2282.6323 | 2135.6323 | 476.8942 | 377.9043 | 440.3115 | 388.147 | 422.6943 | 413.2261 | 397.9722 | 370.4896 | 307.4471
2283.6337 | 2136.6337 | 476.9357 | 377.927 | 440.4848 | 388.1803 | 422.7403 | 413.2471 | 397.9958 | 370.5144 | 307.4533
2284.6351 | 2137.6351 | 476.8925 | 377.9683 | 440.4768 | 388.1831 | 422.762 | 413.2562 | 398.027 | 370.5685 | 307.5089
2285.6366 | 2138.6366 | 476.9961 | 378.0189 | 440.4026 | 388.2249 | 422.7849 | 413.2727 | 398.0603 | 370.622 | 307.581
2286.628 | 2139.628 | 477.1743 | 378.0483 | 440.3669 | 388.2508 | 422.832 | 413.3033 | 398.0955 | 370.657 | 307.6776
2287.6294 | 2140.6294 | 477.2101 | 378.0634 | 440.4232 | 388.291 | 422.8661 | 413.3253 | 398.1298 | 370.6989 | 307.7399
2288.6309 | 2141.6309 | 477.2039 | 378.0635 | 440.4525 | 388.3013 | 422.8995 | 413.318 | 398.1638 | 370.7335 | 307.791
2289.6423 | 2142.6423 | 477.1988 | 378.1016 | 440.3967 | 388.3178 | 422.9184 | 413.299 | 398.195 | 370.7709 | 307.8763
2290.6238 | 2143.6238 | 477.1596 | 378.1626 | 440.4184 | 388.3678 | 422.9493 | 413.2921 | 398.2244 | 370.8106 | 307.9539
2291.6252 | 2144.6252 | 477.1638 | 378.1981 | 440.4367 | 388.4221 | 422.9625 | 413.2803 | 398.2641 | 370.855 | 308.0257
2292.6266 | 2145.6266 | 477.149 | 378.1994 | 440.4959 | 388.4369 | 422.9795 | 413.3099 | 398.29 | 370.9087 | 308.0756
2293.6281 | 2146.6281 | 477.2627 | 378.2535 | 440.543 | 388.4169 | 423.0224 | 413.3139 | 398.3265 | 370.9474 | 308.1579
2294.6295 | 2147.6295 | 477.4093 | 378.2633 | 440.4968 | 388.4967 | 423.0477 | 413.3119 | 398.3559 | 370.9969 | 308.2185
2295.631 | 2148.631 | 477.4729 | 378.3244 | 440.5308 | 388.5115 | 423.0617 | 413.3111 | 398.3852 | 371.0269 | 308.3168
2296.6324 | 2149.6324 | 477.4358 | 378.353 | 440.5641 | 388.5455 | 423.0813 | 413.3179 | 398.4255 | 371.1091 | 308.3519
2297.6338 | 2150.6338 | 477.3658 | 378.3853 | 440.5616 | 388.5524 | 423.1153 | 413.3361 | 398.4507 | 371.1401 | 308.398
2298.6253 | 2151.6253 | 477.4739 | 378.4205 | 440.562 | 388.5907 | 423.1409 | 413.3363 | 398.4912 | 371.176 | 308.4751
2299.6267 | 2152.6267 | 477.4781 | 378.4386 | 440.5575 | 388.6203 | 423.1776 | 413.3622 | 398.5135 | 371.2204 | 308.5329
2300.6281 | 2153.6281 | 477.4413 | 378.5058 | 440.557 | 388.6252 | 423.2032 | 413.3908 | 398.5414 | 371.2743 | 308.5711
2301.6296 | 2154.6296 | 477.5815 | 378.4799 | 440.6477 | 388.6734 | 423.215 | 413.3873 | 398.5739 | 371.3162 | 308.6541
2302.631 | 2155.631 | 477.5856 | 378.5528 | 440.5867 | 388.688 | 423.2431 | 413.3778 | 398.6102 | 371.3568 | 308.7261
2303.6325 | 2156.6325 | 477.5719 | 378.5925 | 440.5926 | 388.7322 | 423.2589 | 413.3859 | 398.6492 | 371.3961 | 308.8039
2304.6339 | 2157.6339 | 477.4611 | 378.6103 | 440.6253 | 388.7351 | 423.2725 | 413.3991 | 398.6714 | 371.4495 | 308.8013
2305.6353 | 2158.6353 | 477.5888 | 378.6619 | 440.6266 | 388.7921 | 423.2706 | 413.406 | 398.7037 | 371.4769 | 308.8661
2306.6268 | 2159.6268 | 477.5719 | 378.6858 | 440.7087 | 388.8347 | 423.305 | 413.4163 | 398.7449 | 371.4988 | 308.9265
2307.6282 | 2160.6282 | 477.4165 | 378.7101 | 440.6756 | 388.8499 | 423.3025 | 413.428 | 398.7659 | 371.5528 | 308.9946
2308.6296 | 2161.6296 | 477.3976 | 378.7024 | 440.7025 | 388.8701 | 423.3386 | 413.4405 | 398.7936 | 371.5939 | 309.0711
2309.6311 | 2162.6311 | 477.3841 | 378.7226 | 440.645 | 388.8869 | 423.3586 | 413.4416 | 398.8327 | 371.6409 | 309.1196
2310.6325 | 2163.6325 | 477.3624 | 378.73 | 440.6021 | 388.8972 | 423.3819 | 413.4656 | 398.8529 | 371.7077 | 309.1401
2311.634 | 2164.634 | 477.3858 | 378.8185 | 440.6564 | 388.9292 | 423.3904 | 413.4651 | 398.8937 | 371.7405 | 309.2689
2312.6354 | 2165.6354 | 477.3998 | 378.8371 | 440.5946 | 388.939 | 423.3996 | 413.4698 | 398.9204 | 371.7823 | 309.3531
2313.6268 | 2166.6268 | 477.3582 | 378.8922 | 440.689 | 388.9645 | 423.4198 | 413.4758 | 398.9508 | 371.8249 | 309.4365
2314.6283 | 2167.6283 | 477.2472 | 378.8722 | 440.719 | 388.9484 | 423.4348 | 413.4997 | 398.982 | 371.8604 | 309.4798
2315.6297 | 2168.6297 | 477.1065 | 378.9473 | 440.6793 | 389.0451 | 423.466 | 413.5079 | 399.0022 | 371.8945 | 309.5391
2316.6312 | 2169.6312 | 476.964 | 378.9729 | 440.7047 | 389.0858 | 423.5263 | 413.5209 | 399.0297 | 371.9231 | 309.6288
2317.6326 | 2170.6326 | 476.9637 | 379.0037 | 440.7813 | 389.0956 | 423.6026 | 413.5342 | 399.0548 | 371.9585 | 309.7216
2318.644 | 2171.644 | 476.9861 | 379.0123 | 440.782 | 389.0838 | 423.6558 | 413.5304 | 399.091 | 372.0116 | 309.788
2319.6355 | 2172.6355 | 477.0259 | 379.0298 | 440.7214 | 389.1577 | 423.6961 | 413.5271 | 399.1123 | 372.0785 | 309.8394
2320.6269 | 2173.6269 | 477.199 | 379.0331 | 440.7147 | 389.1457 | 423.738 | 413.5125 | 399.1381 | 372.1201 | 309.9218
2321.6283 | 2174.6283 | 477.2454 | 379.0953 | 440.785 | 389.2109 | 423.7767 | 413.5115 | 399.1742 | 372.15 | 309.985
2322.6298 | 2175.6298 | 477.236 | 379.1335 | 440.7511 | 389.2339 | 423.8126 | 413.4882 | 399.2148 | 372.2046 | 310.0159
2323.6312 | 2176.6312 | 477.3222 | 379.2069 | 440.8403 | 389.2395 | 423.8283 | 413.4859 | 399.2443 | 372.2556 | 310.0913
2324.6327 | 2177.6327 | 477.4725 | 379.2057 | 440.8517 | 389.2582 | 423.8303 | 413.4741 | 399.2734 | 372.2964 | 310.1708
2325.6341 | 2178.6341 | 477.7266 | 379.183 | 440.8337 | 389.3008 | 423.8185 | 413.4759 | 399.3068 | 372.3451 | 310.2359
2326.6255 | 2179.6255 | 477.7533 | 379.2726 | 440.8191 | 389.3053 | 423.8181 | 413.4623 | 399.3351 | 372.393 | 310.2735
2327.627 | 2180.627 | 477.6492 | 379.293 | 440.7829 | 389.3519 | 423.8447 | 413.4547 | 399.3683 | 372.4204 | 310.3724
2328.6284 | 2181.6284 | 477.6684 | 379.3248 | 440.7716 | 389.3769 | 423.8704 | 413.451 | 399.405 | 372.4788 | 310.3973
2329.6298 | 2182.6298 | 477.5467 | 379.3663 | 440.7644 | 389.3477 | 423.8968 | 413.4564 | 399.439 | 372.5233 | 310.3773
2330.6313 | 2183.6313 | 477.4847 | 379.3534 | 440.7719 | 389.3086 | 423.9364 | 413.4659 | 399.462 | 372.5562 | 310.4308
2331.6327 | 2184.6327 | 477.4101 | 379.3886 | 440.8656 | 389.3773 | 423.9444 | 413.4563 | 399.4942 | 372.6128 | 310.4712
2332.6241 | 2185.6241 | 477.4518 | 379.3694 | 440.9032 | 389.3992 | 423.9739 | 413.4601 | 399.5279 | 372.6514 | 310.5568
2333.6256 | 2186.6256 | 477.486 | 379.42 | 440.8653 | 389.3991 | 424.0113 | 413.4791 | 399.5546 | 372.6986 | 310.6153
2334.627 | 2187.627 | 477.5532 | 379.5109 | 440.8567 | 389.4204 | 424.0224 | 413.5015 | 399.5824 | 372.7352 | 310.7149
2335.6285 | 2188.6285 | 477.6282 | 379.5677 | 440.8274 | 389.4961 | 424.0045 | 413.5054 | 399.6144 | 372.7643 | 310.7957
2336.6299 | 2189.6299 | 477.7726 | 379.6018 | 440.9046 | 389.5238 | 424.0147 | 413.5147 | 399.6459 | 372.8216 | 310.8336
2337.6313 | 2190.6313 | 477.9229 | 379.63 | 440.9487 | 389.554 | 424.0431 | 413.5261 | 399.6638 | 372.8951 | 310.8553
2338.6328 | 2191.6328 | 478.0695 | 379.6189 | 440.9308 | 389.5986 | 424.0558 | 413.5338 | 399.6908 | 372.9394 | 310.897
2339.6242 | 2192.6242 | 478.1729 | 379.7054 | 440.9806 | 389.6183 | 424.0665 | 413.5299 | 399.7154 | 372.9578 | 311.0256
2340.6357 | 2193.6357 | 478.3114 | 379.7634 | 441.0078 | 389.664 | 424.0841 | 413.5107 | 399.7429 | 372.9695 | 311.0254
2341.6271 | 2194.6271 | 478.3705 | 379.7687 | 441.0025 | 389.6896 | 424.1228 | 413.5148 | 399.7717 | 373.0204 | 311.0672
2342.6285 | 2195.6285 | 478.2331 | 379.8293 | 440.9953 | 389.6996 | 424.1146 | 413.511 | 399.8027 | 373.0742 | 311.1197
2343.63 | 2196.63 | 478.2534 | 379.8063 | 440.9844 | 389.7213 | 424.123 | 413.5274 | 399.8265 | 373.1278 | 311.1898
2344.6314 | 2197.6314 | 478.1679 | 379.8572 | 440.9263 | 389.742 | 424.1224 | 413.5081 | 399.8614 | 373.15 | 311.2202
2345.6329 | 2198.6329 | 478.1541 | 379.9203 | 441.0309 | 389.7588 | 424.143 | 413.5156 | 399.8922 | 373.2122 | 311.2663
2346.6343 | 2199.6343 | 478.0207 | 379.9113 | 441.0045 | 389.7895 | 424.1467 | 413.5288 | 399.9213 | 373.2557 | 311.3313
2347.6257 | 2200.6257 | 478.029 | 379.9666 | 441.0425 | 389.8024 | 424.1562 | 413.5374 | 399.9523 | 373.3058 | 311.4229
2348.6272 | 2201.6272 | 478.0899 | 379.9871 | 441.0022 | 389.8044 | 424.1444 | 413.5475 | 399.9822 | 373.3465 | 311.4878
2349.6286 | 2202.6286 | 478.175 | 380.0326 | 440.9546 | 389.7805 | 424.1339 | 413.5523 | 400.0149 | 373.3925 | 311.5659
2350.63 | 2203.63 | 478.1381 | 380.0479 | 441.0455 | 389.841 | 424.1435 | 413.5276 | 400.0288 | 373.4168 | 311.6169
2351.6315 | 2204.6315 | 478.1483 | 380.0859 | 441.1208 | 389.8921 | 424.1549 | 413.5208 | 400.0648 | 373.4587 | 311.6375
2352.6329 | 2205.6329 | 478.1775 | 380.0763 | 441.1634 | 389.8977 | 424.1346 | 413.5288 | 400.0856 | 373.5031 | 311.7018
2353.6344 | 2206.6344 | 478.0679 | 380.1303 | 441.2163 | 389.9258 | 424.1445 | 413.5248 | 400.1123 | 373.5583 | 311.767
2354.6258 | 2207.6258 | 477.9737 | 380.1605 | 441.1884 | 389.9671 | 424.1601 | 413.5125 | 400.1401 | 373.5946 | 311.8253
2355.6272 | 2208.6272 | 477.9591 | 380.182 | 441.1812 | 389.9983 | 424.1776 | 413.5072 | 400.1679 | 373.6545 | 311.83
2356.6287 | 2209.6287 | 477.9747 | 380.2327 | 441.1823 | 390.0347 | 424.1918 | 413.5061 | 400.1943 | 373.6892 | 311.9029
2357.6301 | 2210.6301 | 478.1189 | 380.2542 | 441.1495 | 390.0485 | 424.1897 | 413.4975 | 400.2148 | 373.7263 | 311.9776
2358.6315 | 2211.6315 | 478.1164 | 380.2915 | 441.2685 | 390.071 | 424.2013 | 413.5181 | 400.2432 | 373.7609 | 312.0798
2359.633 | 2212.633 | 478.0776 | 380.3526 | 441.1324 | 390.106 | 424.2026 | 413.5232 | 400.2759 | 373.8137 | 312.1097
2360.6344 | 2213.6344 | 477.9994 | 380.334 | 441.1119 | 390.144 | 424.2129 | 413.557 | 400.2995 | 373.8551 | 312.1729
2361.6359 | 2214.6359 | 477.9347 | 380.3831 | 441.1694 | 390.1627 | 424.2211 | 413.5691 | 400.3295 | 373.8775 | 312.2739
2362.6273 | 2215.6273 | 477.8195 | 380.3902 | 441.1839 | 390.1483 | 424.2332 | 413.5839 | 400.3581 | 373.8915 | 312.3476
2363.6287 | 2216.6287 | 477.612 | 380.4213 | 441.259 | 390.1893 | 424.2278 | 413.581 | 400.3882 | 373.9255 | 312.402
2364.6302 | 2217.6302 | 477.52 | 380.4693 | 441.2191 | 390.2024 | 424.2537 | 413.5812 | 400.4076 | 373.9897 | 312.4249
2365.6316 | 2218.6316 | 477.6382 | 380.4777 | 441.3647 | 390.2026 | 424.2426 | 413.5719 | 400.4376 | 374.018 | 312.5082
2366.6331 | 2219.6331 | 477.5275 | 380.4492 | 441.3624 | 390.2229 | 424.2188 | 413.5627 | 400.4657 | 374.0661 | 312.5448
2367.6345 | 2220.6345 | 477.3967 | 380.5171 | 441.3146 | 390.2268 | 424.2455 | 413.554 | 400.4898 | 374.1198 | 312.5963
2368.6259 | 2221.6259 | 477.2843 | 380.5328 | 441.2522 | 390.296 | 424.256 | 413.551 | 400.5204 | 374.1637 | 312.6239
2369.6274 | 2222.6274 | 477.2171 | 380.5579 | 441.3329 | 390.3353 | 424.262 | 413.5613 | 400.5416 | 374.2237 | 312.6525
2370.6288 | 2223.6288 | 477.2412 | 380.5889 | 441.2846 | 390.3304 | 424.2826 | 413.5486 | 400.5848 | 374.259 | 312.7291
2371.6302 | 2224.6302 | 477.1278 | 380.6636 | 441.3062 | 390.3127 | 424.2886 | 413.516 | 400.606 | 374.2764 | 312.7994
2372.6317 | 2225.6317 | 476.9474 | 380.6946 | 441.3268 | 390.3211 | 424.2868 | 413.5012 | 400.6322 | 374.3186 | 312.8549
2373.6331 | 2226.6331 | 476.7395 | 380.7093 | 441.3809 | 390.3194 | 424.2889 | 413.5033 | 400.6552 | 374.3636 | 312.9256
2374.6245 | 2227.6245 | 476.672 | 380.6875 | 441.4024 | 390.3191 | 424.2878 | 413.4913 | 400.6877 | 374.3892 | 312.9923
2375.626 | 2228.626 | 476.5404 | 380.7288 | 441.3426 | 390.3795 | 424.3091 | 413.509 | 400.7178 | 374.4626 | 313.0199
2376.6274 | 2229.6274 | 476.312 | 380.7756 | 441.3267 | 390.4067 | 424.3064 | 413.5091 | 400.7416 | 374.5028 | 313.099
2377.6289 | 2230.6289 | 476.216 | 380.7724 | 441.33 | 390.3909 | 424.2938 | 413.501 | 400.7746 | 374.5316 | 313.1944
2378.6303 | 2231.6303 | 476.2438 | 380.7797 | 441.3838 | 390.4489 | 424.2921 | 413.5152 | 400.7959 | 374.5609 | 313.2561
2379.6317 | 2232.6317 | 476.2707 | 380.8525 | 441.3942 | 390.4799 | 424.2872 | 413.5158 | 400.8247 | 374.6217 | 313.3079
2380.6332 | 2233.6332 | 476.3007 | 380.8726 | 441.4431 | 390.5144 | 424.274 | 413.5269 | 400.8519 | 374.664 | 313.3775
2381.6246 | 2234.6246 | 476.2399 | 380.8688 | 441.2591 | 390.5376 | 424.2714 | 413.5049 | 400.8832 | 374.699 | 313.3849
2382.626 | 2235.626 | 476.3626 | 380.8759 | 441.3158 | 390.5483 | 424.2719 | 413.5061 | 400.9047 | 374.7653 | 313.3813
2383.6275 | 2236.6275 | 476.622 | 380.8936 | 441.3153 | 390.5974 | 424.2782 | 413.5054 | 400.946 | 374.7841 | 313.4743
2384.6289 | 2237.6289 | 476.8665 | 380.9285 | 441.2623 | 390.6036 | 424.2742 | 413.5115 | 400.9637 | 374.8375 | 313.5545
2385.6304 | 2238.6304 | 477.0082 | 381.0125 | 441.2553 | 390.6352 | 424.2539 | 413.5158 | 400.9966 | 374.873 | 313.5857
2386.6318 | 2239.6318 | 477.0101 | 381.0692 | 441.285 | 390.6522 | 424.2221 | 413.5133 | 401.0264 | 374.8959 | 313.6086
2387.6332 | 2240.6332 | 476.9846 | 381.1297 | 441.3054 | 390.6721 | 424.167 | 413.5119 | 401.0506 | 374.9329 | 313.6801
2388.6347 | 2241.6347 | 476.9837 | 381.1761 | 441.3242 | 390.732 | 424.1539 | 413.499 | 401.0781 | 374.9764 | 313.7437
2389.6261 | 2242.6261 | 476.9659 | 381.175 | 441.2712 | 390.74 | 424.1399 | 413.4954 | 401.1073 | 375.0072 | 313.8443
2390.6276 | 2243.6276 | 476.8887 | 381.1437 | 441.3647 | 390.7257 | 424.1516 | 413.4891 | 401.1448 | 375.0639 | 313.8801
2391.629 | 2244.629 | 476.7922 | 381.1784 | 441.34 | 390.7301 | 424.1364 | 413.5033 | 401.1731 | 375.1145 | 313.942
2392.6304 | 2245.6304 | 476.8503 | 381.2487 | 441.4185 | 390.7574 | 424.1152 | 413.5103 | 401.2029 | 375.1617 | 313.9963
2393.6319 | 2246.6319 | 476.9129 | 381.2561 | 441.4699 | 390.7898 | 424.0898 | 413.5374 | 401.2275 | 375.2046 | 314.0389
2394.6333 | 2247.6333 | 476.9351 | 381.3222 | 441.4775 | 390.8536 | 424.0998 | 413.5037 | 401.2523 | 375.253 | 314.1128
2395.6348 | 2248.6348 | 476.8265 | 381.3346 | 441.4585 | 390.858 | 424.1202 | 413.507 | 401.2673 | 375.2815 | 314.2144
2396.6262 | 2249.6262 | 476.7172 | 381.3667 | 441.3881 | 390.8668 | 424.0868 | 413.502 | 401.289 | 375.3393 | 314.254
2397.6276 | 2250.6276 | 476.6948 | 381.3795 | 441.4711 | 390.9183 | 424.0883 | 413.5195 | 401.3031 | 375.3754 | 314.321
2398.6291 | 2251.6291 | 476.6271 | 381.3952 | 441.5166 | 390.9299 | 424.1068 | 413.5545 | 401.3303 | 375.3728 | 314.3912
2399.6305 | 2252.6305 | 476.5911 | 381.4611 | 441.568 | 390.9913 | 424.0581 | 413.5681 | 401.3494 | 375.426 | 314.4147
2400.6319 | 2253.6319 | 476.5706 | 381.4937 | 441.5061 | 390.9825 | 424.1195 | 413.5794 | 401.3771 | 375.4357 | 314.4694
2401.6334 | 2254.6334 | 476.533 | 381.413 | 441.5111 | 390.9986 | 424.1531 | 413.556 | 401.4013 | 375.5033 | 314.4493
2402.6348 | 2255.6348 | 476.5395 | 381.5242 | 441.552 | 391.0037 | 424.1814 | 413.566 | 401.4225 | 375.5329 | 314.5448
2403.6262 | 2256.6262 | 476.5825 | 381.5556 | 441.5379 | 391.0848 | 424.1743 | 413.5488 | 401.4483 | 375.5661 | 314.5781
2404.6277 | 2257.6277 | 476.6361 | 381.5256 | 441.6133 | 391.075 | 424.2053 | 413.5733 | 401.4702 | 375.6264 | 314.6032
2405.6291 | 2258.6291 | 476.6458 | 381.5735 | 441.6363 | 391.1077 | 424.2121 | 413.5654 | 401.4978 | 375.6654 | 314.6569
2406.6306 | 2259.6306 | 476.7819 | 381.6167 | 441.6097 | 391.1258 | 424.2296 | 413.5537 | 401.5185 | 375.7096 | 314.7423
2407.632 | 2260.632 | 477.0564 | 381.6735 | 441.6652 | 391.1341 | 424.2455 | 413.5656 | 401.5417 | 375.7508 | 314.8006
2408.6334 | 2261.6334 | 477.2138 | 381.7004 | 441.5901 | 391.1483 | 424.2718 | 413.5687 | 401.5724 | 375.7832 | 314.8714
2409.6349 | 2262.6349 | 477.1877 | 381.6709 | 441.6062 | 391.1604 | 424.296 | 413.618 | 401.5922 | 375.8332 | 314.9332
2410.6263 | 2263.6263 | 477.3475 | 381.7339 | 441.6574 | 391.2043 | 424.3084 | 413.629 | 401.6162 | 375.887 | 314.9984
2411.6278 | 2264.6278 | 477.4634 | 381.7253 | 441.5982 | 391.21 | 424.3078 | 413.6582 | 401.6366 | 375.9002 | 315.0878
2412.6292 | 2265.6292 | 477.5785 | 381.8166 | 441.6959 | 391.2293 | 424.2839 | 413.6349 | 401.6623 | 375.9421 | 315.118
2413.6306 | 2266.6306 | 477.5588 | 381.8133 | 441.6503 | 391.2648 | 424.2734 | 413.6363 | 401.6836 | 375.9938 | 315.0819
2414.6321 | 2267.6321 | 477.483 | 381.8377 | 441.6637 | 391.2688 | 424.2785 | 413.6545 | 401.7122 | 376.0203 | 315.1111
2415.6235 | 2268.6235 | 477.5226 | 381.846 | 441.5007 | 391.3441 | 424.2755 | 413.6876 | 401.7363 | 376.0633 | 315.1903
2416.6249 | 2269.6249 | 477.3726 | 381.8942 | 441.607 | 391.3257 | 424.3063 | 413.6934 | 401.7572 | 376.0848 | 315.2878
2417.6264 | 2270.6264 | 477.3228 | 381.9117 | 441.6054 | 391.3541 | 424.3193 | 413.6923 | 401.7918 | 376.1263 | 315.3483
2418.6278 | 2271.6278 | 477.2755 | 381.9553 | 441.6139 | 391.3698 | 424.324 | 413.703 | 401.804 | 376.1718 | 315.4101
2419.6293 | 2272.6293 | 477.2142 | 381.951 | 441.6286 | 391.4162 | 424.3194 | 413.6975 | 401.8394 | 376.2168 | 315.4843
2420.6307 | 2273.6307 | 477.1883 | 381.9808 | 441.6942 | 391.4023 | 424.3362 | 413.7096 | 401.8598 | 376.2406 | 315.5442
2421.6321 | 2274.6321 | 477.2136 | 381.9972 | 441.6511 | 391.4453 | 424.2899 | 413.716 | 401.8956 | 376.2876 | 315.5216
2422.6336 | 2275.6336 | 477.1416 | 382.0401 | 441.5577 | 391.4489 | 424.293 | 413.7152 | 401.9138 | 376.3299 | 315.5884
2423.625 | 2276.625 | 477.027 | 382.0419 | 441.7105 | 391.4563 | 424.29 | 413.692 | 401.9422 | 376.3527 | 315.677
2424.6264 | 2277.6264 | 477.0827 | 382.0582 | 441.6953 | 391.4819 | 424.311 | 413.6861 | 401.9691 | 376.3505 | 315.7764
2425.6279 | 2278.6279 | 477.0662 | 382.075 | 441.7281 | 391.5308 | 424.3065 | 413.7213 | 401.9954 | 376.4077 | 315.8408
2426.6293 | 2279.6293 | 477.014 | 382.1382 | 441.7288 | 391.5279 | 424.2777 | 413.7121 | 402.0127 | 376.4677 | 315.8815
2427.6308 | 2280.6308 | 476.9762 | 382.151 | 441.7455 | 391.5458 | 424.2879 | 413.698 | 402.0388 | 376.4805 | 315.8981
2428.6322 | 2281.6322 | 476.8816 | 382.1768 | 441.7204 | 391.5648 | 424.279 | 413.6665 | 402.0683 | 376.5367 | 315.9798
2429.6336 | 2282.6336 | 476.9518 | 382.179 | 441.5804 | 391.5765 | 424.25 | 413.6695 | 402.078 | 376.5453 | 316.0698
2430.6351 | 2283.6351 | 476.9516 | 382.1927 | 441.701 | 391.5999 | 424.2411 | 413.6646 | 402.1066 | 376.6268 | 316.0962
2431.6265 | 2284.6265 | 476.8806 | 382.2342 | 441.7426 | 391.6007 | 424.2628 | 413.671 | 402.1281 | 376.655 | 316.1659
2432.6279 | 2285.6279 | 476.8274 | 382.2522 | 441.7036 | 391.6313 | 424.2912 | 413.6663 | 402.1553 | 376.685 | 316.1896
2433.6294 | 2286.6294 | 476.8378 | 382.2465 | 441.6952 | 391.6235 | 424.2403 | 413.6622 | 402.1824 | 376.745 | 316.2449
2434.6308 | 2287.6308 | 476.7356 | 382.1597 | 441.6657 | 391.643 | 424.1826 | 413.6475 | 402.2124 | 376.791 | 316.3097
2435.6323 | 2288.6323 | 476.6536 | 382.2873 | 441.7155 | 391.6596 | 424.1277 | 413.6422 | 402.233 | 376.8128 | 316.3739
2436.6337 | 2289.6337 | 476.6065 | 382.3259 | 441.732 | 391.6802 | 424.0965 | 413.6598 | 402.2504 | 376.8537 | 316.4136
2437.6251 | 2290.6251 | 476.5348 | 382.3395 | 441.7573 | 391.7099 | 424.1174 | 413.6506 | 402.2733 | 376.8872 | 316.4818
2438.6266 | 2291.6266 | 476.5285 | 382.3937 | 441.7956 | 391.6796 | 424.1465 | 413.6556 | 402.2846 | 376.924 | 316.5831
2439.628 | 2292.628 | 476.3895 | 382.399 | 441.7908 | 391.7121 | 424.1554 | 413.6341 | 402.3218 | 376.9745 | 316.6409
2440.6295 | 2293.6295 | 476.1984 | 382.4413 | 441.7447 | 391.7448 | 424.1653 | 413.6354 | 402.343 | 376.9964 | 316.707
2441.6309 | 2294.6309 | 476.2364 | 382.4865 | 441.8007 | 391.7717 | 424.1731 | 413.6292 | 402.379 | 377.0178 | 316.7408
2442.6323 | 2295.6323 | 476.3688 | 382.5218 | 441.702 | 391.789 | 424.1417 | 413.6171 | 402.4017 | 377.0581 | 316.759
2443.6338 | 2296.6338 | 476.3329 | 382.5021 | 441.6941 | 391.7641 | 424.1241 | 413.6153 | 402.4288 | 377.1032 | 316.8362
2444.6352 | 2297.6352 | 476.3828 | 382.5349 | 441.6394 | 391.7869 | 424.0667 | 413.6317 | 402.443 | 377.1519 | 316.8615
2445.6266 | 2298.6266 | 476.4741 | 382.5558 | 441.6542 | 391.7766 | 424.0539 | 413.6458 | 402.4754 | 377.2075 | 316.9162
2446.6281 | 2299.6281 | 476.5131 | 382.5391 | 441.6672 | 391.6815 | 424.0335 | 413.6379 | 402.4993 | 377.2114 | 317.0004
2447.6295 | 2300.6295 | 476.7545 | 382.5962 | 441.7347 | 391.7719 | 424.0373 | 413.6774 | 402.5242 | 377.2633 | 317.0758
2448.631 | 2301.631 | 477.0966 | 382.607 | 441.7384 | 391.7954 | 424.0231 | 413.6956 | 402.551 | 377.2873 | 317.1339
2449.6324 | 2302.6324 | 477.2805 | 382.684 | 441.6783 | 391.7575 | 424.0023 | 413.721 | 402.5781 | 377.3364 | 317.1722
2450.6338 | 2303.6338 | 477.4619 | 382.6821 | 441.7034 | 391.8264 | 423.9896 | 413.7241 | 402.6004 | 377.3767 | 317.2042
2451.6253 | 2304.6253 | 477.6208 | 382.6466 | 441.7619 | 391.808 | 423.9678 | 413.7345 | 402.625 | 377.4121 | 317.2872
2452.6267 | 2305.6267 | 477.7125 | 382.759 | 441.7937 | 391.8137 | 423.9312 | 413.7405 | 402.6551 | 377.4773 | 317.301
2453.6281 | 2306.6281 | 477.8423 | 382.7896 | 441.7944 | 391.9214 | 423.9232 | 413.7162 | 402.6665 | 377.4961 | 317.3374
2454.6296 | 2307.6296 | 477.9605 | 382.8302 | 441.7447 | 391.9551 | 423.8849 | 413.7035 | 402.6886 | 377.5641 | 317.3665
2455.631 | 2308.631 | 478.036 | 382.8905 | 441.8126 | 391.981 | 423.825 | 413.6828 | 402.7171 | 377.6036 | 317.4293
2456.6325 | 2309.6325 | 478.0992 | 382.9205 | 441.7725 | 392.0071 | 423.8062 | 413.6822 | 402.7425 | 377.6347 | 317.4669
2457.6239 | 2310.6239 | 478.2364 | 382.9753 | 441.7938 | 392.0471 | 423.7927 | 413.6944 | 402.7727 | 377.6832 | 317.5069
2458.6253 | 2311.6253 | 478.4058 | 382.9834 | 441.8208 | 392.0292 | 423.7861 | 413.7162 | 402.794 | 377.7152 | 317.5907
2459.6268 | 2312.6268 | 478.6002 | 382.983 | 441.8984 | 392.0216 | 423.7682 | 413.7348 | 402.8134 | 377.7531 | 317.6297
2460.6282 | 2313.6282 | 478.7746 | 383.0513 | 441.8652 | 392.0084 | 423.8016 | 413.7613 | 402.838 | 377.775 | 317.7351
2461.6296 | 2314.6296 | 478.9923 | 383.0669 | 441.9343 | 392.0587 | 423.8175 | 413.7544 | 402.8656 | 377.8086 | 317.8177
2462.6311 | 2315.6311 | 479.0378 | 383.1216 | 442.0724 | 392.0625 | 423.8014 | 413.7726 | 402.8901 | 377.8609 | 317.8686
2463.6325 | 2316.6325 | 478.9965 | 383.1093 | 441.9456 | 392.0382 | 423.7968 | 413.7725 | 402.9113 | 377.8837 | 317.9454
2464.634 | 2317.634 | 479.0083 | 383.1101 | 442.0053 | 392.1075 | 423.8366 | 413.787 | 402.9378 | 377.9167 | 317.9836
2465.6254 | 2318.6254 | 478.9453 | 383.1619 | 441.9558 | 392.1718 | 423.8158 | 413.8082 | 402.9545 | 377.9366 | 318.0517
2466.6268 | 2319.6268 | 478.935 | 383.1 | 441.9006 | 392.2276 | 423.8103 | 413.8322 | 402.9856 | 378.0039 | 318.088
2467.6283 | 2320.6283 | 478.907 | 383.1868 | 441.9818 | 392.2122 | 423.7998 | 413.8314 | 403.0071 | 378.0331 | 318.1318
2468.6297 | 2321.6297 | 478.8859 | 383.2075 | 441.9983 | 392.2417 | 423.7584 | 413.8254 | 403.0277 | 378.0761 | 318.1495
2469.6312 | 2322.6312 | 478.9249 | 383.2842 | 441.9045 | 392.262 | 423.768 | 413.8424 | 403.0452 | 378.1097 | 318.2357
2470.7528 | 2323.7528 | 478.7954 | 383.2833 | 441.9412 | 392.2967 | 423.7728 | 413.8341 | 403.0866 | 378.1585 | 318.2506
2471.634 | 2324.634 | 478.615 | 383.3177 | 441.8871 | 392.3357 | 423.8067 | 413.8338 | 403.1071 | 378.1944 | 318.3025
2472.6355 | 2325.6355 | 478.5835 | 383.3835 | 441.9753 | 392.3548 | 423.8106 | 413.8064 | 403.1368 | 378.251 | 318.3481
2473.6269 | 2326.6269 | 478.5151 | 383.3099 | 441.9502 | 392.3683 | 423.779 | 413.8254 | 403.1617 | 378.2744 | 318.3746
2474.6283 | 2327.6283 | 478.4215 | 383.3825 | 441.9602 | 392.4329 | 423.7493 | 413.819 | 403.1864 | 378.3072 | 318.4179
2475.6298 | 2328.6298 | 478.3271 | 383.4535 | 441.9952 | 392.4289 | 423.74 | 413.849 | 403.2213 | 378.3392 | 318.4919
2476.6312 | 2329.6312 | 478.2746 | 383.4767 | 441.9928 | 392.4355 | 423.752 | 413.8606 | 403.2422 | 378.3713 | 318.5481
2477.6327 | 2330.6327 | 478.2088 | 383.4833 | 442.0816 | 392.3448 | 423.6982 | 413.8512 | 403.2618 | 378.4253 | 318.5914
2478.6341 | 2331.6341 | 478.1389 | 383.488 | 442.0808 | 392.4276 | 423.6617 | 413.8651 | 403.2841 | 378.4687 | 318.6465
2479.6255 | 2332.6255 | 478.1499 | 383.4943 | 442.1048 | 392.4825 | 423.6339 | 413.8889 | 403.3127 | 378.4813 | 318.7199
2480.627 | 2333.627 | 478.2304 | 383.5807 | 442.1497 | 392.5091 | 423.6758 | 413.9292 | 403.3312 | 378.5234 | 318.7619 | Time of first failure
2481.6284 | 2334.6284 | 478.2966 | 383.5751 | 442.1202 | 392.5048 | 423.7232 | 413.9294 | 403.3666 | 378.5662 | 318.8198 | 2334 | 0
2482.6298 | 2335.6298 | 478.2983 | 383.6347 | 442.0534 | 392.543 | 423.7195 | 413.9332 | 403.3896 | 378.592 | 318.8559 | 2334 | 900
2483.6313 | 2336.6313 | 478.3291 | 383.6349 | 442.1012 | 392.5678 | 423.656 | 413.9137 | 403.4141 | 378.6254 | 318.9045
2484.6327 | 2337.6327 | 478.3683 | 383.6839 | 442.0071 | 392.61 | 423.6243 | 413.9048 | 403.4481 | 378.6797 | 318.9518
2485.6342 | 2338.6342 | 478.2074 | 383.7039 | 441.8961 | 392.6172 | 423.6189 | 413.9028 | 403.4752 | 378.6956 | 318.9935
2486.6356 | 2339.6356 | 478.187 | 383.7296 | 441.965 | 392.6259 | 423.673 | 413.9033 | 403.5092 | 378.7331 | 319.0688
2487.627 | 2340.627 | 478.2522 | 383.7424 | 441.9838 | 392.6381 | 423.6469 | 413.9136 | 403.536 | 378.7634 | 319.1374
2488.6285 | 2341.6285 | 478.2375 | 383.7808 | 442.0607 | 392.6368 | 423.6102 | 413.9022 | 403.5634 | 378.8151 | 319.1329
2489.6299 | 2342.6299 | 478.1813 | 383.8175 | 442.0803 | 392.6811 | 423.5914 | 413.8934 | 403.5812 | 378.8512 | 319.1856
2490.6314 | 2343.6314 | 478.1667 | 383.8178 | 442.0342 | 392.6764 | 423.5729 | 413.8817 | 403.6109 | 378.8712 | 319.2472
2491.6328 | 2344.6328 | 478.2054 | 383.8497 | 441.9655 | 392.716 | 423.6038 | 413.9214 | 403.6298 | 378.916 | 319.2849
2492.6342 | 2345.6342 | 478.1288 | 383.8566 | 441.8626 | 392.7616 | 423.589 | 413.9185 | 403.6561 | 378.9458 | 319.342
2493.6357 | 2346.6357 | 478.0737 | 383.873 | 441.9452 | 392.7703 | 423.6123 | 413.9349 | 403.6815 | 378.9682 | 319.4051
2494.6271 | 2347.6271 | 478.058 | 383.9012 | 441.997 | 392.789 | 423.632 | 413.956 | 403.7056 | 379.0104 | 319.4425
2495.6285 | 2348.6285 | 477.8709 | 383.9531 | 442.0369 | 392.8137 | 423.6829 | 413.9908 | 403.7212 | 379.0481 | 319.4998
2496.63 | 2349.63 | 477.6813 | 383.9647 | 441.9852 | 392.8031 | 423.6706 | 413.9872 | 403.7493 | 379.0948 | 319.5632
2497.6314 | 2350.6314 | 477.6703 | 384.0041 | 442.0085 | 392.8338 | 423.6559 | 413.9982 | 403.7784 | 379.1177 | 319.6279
2498.6529 | 2351.6529 | 477.627 | 383.9812 | 442.0249 | 392.8628 | 423.7064 | 414.0187 | 403.8007 | 379.1574 | 319.6565
2499.6243 | 2352.6243 | 477.6381 | 383.9677 | 442.0709 | 392.8828 | 423.7013 | 414.0222 | 403.8171 | 379.1656 | 319.738
2500.6257 | 2353.6257 | 477.5135 | 383.9493 | 442.0168 | 392.899 | 423.7513 | 414.0507 | 403.8291 | 379.2192 | 319.8038
2501.6272 | 2354.6272 | 477.5022 | 383.9927 | 442.0485 | 392.9019 | 423.7598 | 414.0238 | 403.8463 | 379.2468 | 319.8271
2502.6286 | 2355.6286 | 477.4307 | 383.9593 | 442.092 | 392.9444 | 423.8053 | 414.0202 | 403.8747 | 379.2844 | 319.8621
2503.63 | 2356.63 | 477.4361 | 383.991 | 442.1571 | 392.9558 | 423.8266 | 414.0284 | 403.9076 | 379.3063 | 319.892
2504.6315 | 2357.6315 | 477.3425 | 384.1022 | 442.1414 | 392.9934 | 423.8721 | 414.0623 | 403.927 | 379.3473 | 319.9238
2505.6329 | 2358.6329 | 477.2223 | 384.1502 | 442.333 | 393.0334 | 423.8743 | 414.0708 | 403.9549 | 379.3615 | 319.8951
2506.6344 | 2359.6344 | 477.0983 | 384.1775 | 442.2698 | 393.0528 | 423.8683 | 414.142 | 403.9741 | 379.4011 | 319.9143
2507.6258 | 2360.6258 | 476.9557 | 384.2084 | 442.1461 | 393.0852 | 423.8315 | 414.1675 | 404.0035 | 379.4595 | 319.924
2508.6272 | 2361.6272 | 476.9065 | 384.1668 | 442.1648 | 393.0504 | 423.7964 | 414.2014 | 404.0209 | 379.4754 | 319.9888
2509.6287 | 2362.6287 | 476.9467 | 384.2684 | 442.1775 | 393.116 | 423.7948 | 414.2496 | 404.0462 | 379.5313 | 320.0519
2510.6301 | 2363.6301 | 477.0482 | 384.2967 | 442.2222 | 393.1085 | 423.7705 | 414.2624 | 404.0681 | 379.5469 | 320.14
2511.6315 | 2364.6315 | 477.095 | 384.3217 | 442.1845 | 393.1353 | 423.7566 | 414.2828 | 404.079 | 379.5927 | 320.1819
2512.633 | 2365.633 | 477.0768 | 384.3462 | 442.2214 | 393.1335 | 423.7632 | 414.2995 | 404.1143 | 379.5957 | 320.2812
2513.6344 | 2366.6344 | 477.036 | 384.4071 | 442.2207 | 393.1613 | 423.7507 | 414.3565 | 404.1391 | 379.6446 | 320.2947
2514.6359 | 2367.6359 | 476.9917 | 384.4355 | 442.1736 | 393.1795 | 423.7655 | 414.4238 | 404.152 | 379.6912 | 320.3177
2515.6273 | 2368.6273 | 477.1387 | 384.3941 | 442.1943 | 393.2193 | 423.776 | 414.4763 | 404.1699 | 379.7068 | 320.3968
2516.6287 | 2369.6287 | 477.1645 | 384.4494 | 442.1847 | 393.221 | 423.7579 | 414.505 | 404.2011 | 379.7355 | 320.4473
2517.6302 | 2370.6302 | 477.2814 | 384.4855 | 442.2025 | 393.2312 | 423.7654 | 414.4985 | 404.2303 | 379.7702 | 320.4768
2518.6316 | 2371.6316 | 477.4387 | 384.4817 | 442.2428 | 393.2433 | 423.7839 | 414.5024 | 404.2572 | 379.8256 | 320.5307
2519.6331 | 2372.6331 | 477.6458 | 384.5256 | 442.2266 | 393.2582 | 423.7792 | 414.5049 | 404.2902 | 379.8484 | 320.6212
2520.6245 | 2373.6245 | 477.6388 | 384.5152 | 442.2761 | 393.2598 | 423.7256 | 414.5313 | 404.3153 | 379.8879 | 320.6537
2521.6259 | 2374.6259 | 477.5136 | 384.5485 | 442.1783 | 393.31 | 423.6558 | 414.5499 | 404.3435 | 379.9207 | 320.6892
2522.6274 | 2375.6274 | 477.4244 | 384.5741 | 442.025 | 393.3202 | 423.565 | 414.5802 | 404.3575 | 379.9413 | 320.7649
2523.6288 | 2376.6288 | 477.303 | 384.6396 | 442.1923 | 393.3556 | 423.5284 | 414.5751 | 404.3849 | 379.9797 | 320.7947
2524.6302 | 2377.6302 | 477.1181 | 384.6348 | 442.3057 | 393.3542 | 423.5426 | 414.5744 | 404.4079 | 380.0028 | 320.8615
2525.6317 | 2378.6317 | 477.0479 | 384.6534 | 442.2147 | 393.377 | 423.5626 | 414.5635 | 404.4383 | 380.0456 | 320.9035
2526.6331 | 2379.6331 | 476.9891 | 384.6689 | 442.0869 | 393.4087 | 423.5946 | 414.5586 | 404.4646 | 380.0815 | 320.9581
2527.6346 | 2380.6346 | 477.021 | 384.683 | 442.2264 | 393.408 | 423.5563 | 414.5414 | 404.486 | 380.1136 | 320.988
2528.626 | 2381.626 | 477.0254 | 384.7566 | 442.1771 | 393.4011 | 423.5017 | 414.5068 | 404.5092 | 380.1529 | 321.0499
2529.6274 | 2382.6274 | 476.9473 | 384.7193 | 442.0929 | 393.4236 | 423.4876 | 414.5439 | 404.5343 | 380.1843 | 321.0858
2530.6289 | 2383.6289 | 476.9706 | 384.7874 | 442.2142 | 393.4471 | 423.4946 | 414.5484 | 404.5587 | 380.216 | 321.1455
2531.6303 | 2384.6303 | 476.9092 | 384.7362 | 442.2162 | 393.4444 | 423.5182 | 414.5691 | 404.5672 | 380.2531 | 321.1743
2532.6317 | 2385.6317 | 476.8505 | 384.8079 | 442.2069 | 393.4877 | 423.4731 | 414.571 | 404.5965 | 380.2752 | 321.2378
2533.6332 | 2386.6332 | 476.8041 | 384.7923 | 442.2337 | 393.5079 | 423.4913 | 414.5623 | 404.6195 | 380.3179 | 321.3003
2534.6346 | 2387.6346 | 476.8159 | 384.8178 | 442.3043 | 393.5091 | 423.5114 | 414.5456 | 404.6426 | 380.3546 | 321.3489
2535.6361 | 2388.6361 | 476.8949 | 384.8734 | 442.324 | 393.5303 | 423.5377 | 414.5278 | 404.6624 | 380.3947 | 321.3884
2536.6275 | 2389.6275 | 476.8271 | 384.8622 | 442.2697 | 393.5295 | 423.5293 | 414.5405 | 404.6842 | 380.4299 | 321.4676
2537.6289 | 2390.6289 | 476.7695 | 384.9148 | 442.315 | 393.5395 | 423.4557 | 414.5534 | 404.7175 | 380.4685 | 321.5096
2538.6304 | 2391.6304 | 476.6637 | 384.9348 | 442.318 | 393.5754 | 423.3914 | 414.5783 | 404.737 | 380.5076 | 321.5556
2539.6318 | 2392.6318 | 476.5873 | 384.9345 | 442.2631 | 393.6022 | 423.367 | 414.5992 | 404.7554 | 380.5329 | 321.6162
2540.6333 | 2393.6333 | 476.6071 | 384.9248 | 442.3433 | 393.5941 | 423.3849 | 414.6817 | 404.7841 | 380.5438 | 321.6478
2541.6347 | 2394.6347 | 476.5758 | 384.9335 | 442.3234 | 393.6267 | 423.3934 | 414.6813 | 404.8083 | 380.571 | 321.7148
2542.6261 | 2395.6261 | 476.5728 | 385.0096 | 442.172 | 393.6372 | 423.3676 | 414.6544 | 404.8348 | 380.63 | 321.7131
2543.6276 | 2396.6276 | 476.6696 | 385.0388 | 442.2207 | 393.6826 | 423.278 | 414.6221 | 404.8504 | 380.6411 | 321.7759
2544.629 | 2397.629 | 476.7638 | 385.0511 | 442.3765 | 393.7008 | 423.2468 | 414.628 | 404.8696 | 380.6828 | 321.8236
2545.6304 | 2398.6304 | 476.8775 | 385.0307 | 442.3763 | 393.7261 | 423.2346 | 414.651 | 404.8992 | 380.7007 | 321.8931
2546.6319 | 2399.6319 | 476.7949 | 385.1112 | 442.2784 | 393.7333 | 423.2341 | 414.6437 | 404.9167 | 380.7321 | 321.9264
2547.6333 | 2400.6333 | 476.7183 | 385.0519 | 442.3687 | 393.7423 | 423.2387 | 414.6085 | 404.9266 | 380.7613 | 321.9899
2548.6247 | 2401.6247 | 476.6923 | 385.0788 | 442.3247 | 393.7538 | 423.3652 | 414.5706 | 404.9548 | 380.7941 | 322.0182
2549.6262 | 2402.6262 | 476.7437 | 385.1268 | 442.3435 | 393.7028 | 423.4021 | 414.5719 | 404.9728 | 380.8174 | 322.0704
2550.6276 | 2403.6276 | 476.7126 | 385.1925 | 442.4045 | 393.7732 | 423.4096 | 414.5602 | 405.0007 | 380.8535 | 322.08
2551.6291 | 2404.6291 | 476.7343 | 385.2522 | 442.4601 | 393.8168 | 423.4318 | 414.5781 | 405.0267 | 380.8863 | 322.1202
2552.6305 | 2405.6305 | 476.7792 | 385.2147 | 442.318 | 393.8126 | 423.413 | 414.5537 | 405.0513 | 380.9245 | 322.1365
2553.6319 | 2406.6319 | 476.7923 | 385.2475 | 442.3791 | 393.7925 | 423.4528 | 414.5555 | 405.0725 | 380.9412 | 322.182
2554.6334 | 2407.6334 | 476.8694 | 385.3146 | 442.2942 | 393.8337 | 423.3977 | 414.5641 | 405.1026 | 380.971 | 322.231
2555.6348 | 2408.6348 | 476.9388 | 385.3388 | 442.4301 | 393.8507 | 423.32 | 414.5526 | 405.1253 | 381.0199 | 322.2221
2556.6363 | 2409.6363 | 476.9935 | 385.3489 | 442.4369 | 393.8686 | 423.2478 | 414.5285 | 405.1398 | 381.029 | 322.2692
2557.6277 | 2410.6277 | 477.0281 | 385.3628 | 442.453 | 393.8176 | 423.331 | 414.5167 | 405.1691 | 381.0533 | 322.3318
2558.6291 | 2411.6291 | 477.0945 | 385.4335 | 442.4753 | 393.8287 | 423.397 | 414.5172 | 405.1836 | 381.1026 | 322.3769
2559.6306 | 2412.6306 | 477.1079 | 385.4492 | 442.419 | 393.8913 | 423.3875 | 414.5365 | 405.2158 | 381.1299 | 322.4088
2560.632 | 2413.632 | 477.0149 | 385.4161 | 442.4356 | 393.9274 | 423.3913 | 414.5781 | 405.236 | 381.1858 | 322.455
2561.6334 | 2414.6334 | 476.9957 | 385.4837 | 442.3743 | 393.864 | 423.3475 | 414.5938 | 405.2682 | 381.207 | 322.5015
2562.6349 | 2415.6349 | 477.0442 | 385.5299 | 442.4175 | 393.8558 | 423.4235 | 414.5983 | 405.2903 | 381.2219 | 322.5269
2563.6263 | 2416.6263 | 477.2146 | 385.5409 | 442.3969 | 393.876 | 423.486 | 414.56 | 405.317 | 381.2653 | 322.5512
2564.6278 | 2417.6278 | 477.2813 | 385.545 | 442.4731 | 393.9347 | 423.5493 | 414.5642 | 405.3291 | 381.2721 | 322.6347
2565.6292 | 2418.6292 | 477.2718 | 385.5345 | 442.437 | 393.9422 | 423.5793 | 414.5868 | 405.3484 | 381.3094 | 322.7089
2566.6306 | 2419.6306 | 477.2332 | 385.6377 | 442.3685 | 393.8863 | 423.5771 | 414.5877 | 405.3725 | 381.3508 | 322.7492
2567.6321 | 2420.6321 | 477.3177 | 385.6252 | 442.4078 | 393.9037 | 423.6345 | 414.6325 | 405.3901 | 381.4102 | 322.7919
2568.6335 | 2421.6335 | 477.3867 | 385.5914 | 442.4016 | 393.9674 | 423.676 | 414.6405 | 405.4152 | 381.4449 | 322.8745
2569.635 | 2422.635 | 477.4424 | 385.638 | 442.4321 | 394.0409 | 423.6982 | 414.6299 | 405.4299 | 381.4696 | 322.9122
2570.6264 | 2423.6264 | 477.5712 | 385.7078 | 442.4875 | 394.0681 | 423.7404 | 414.5725 | 405.4476 | 381.5034 | 322.9363
2571.6278 | 2424.6278 | 477.7482 | 385.6692 | 442.4946 | 394.0898 | 423.7998 | 414.5828 | 405.4608 | 381.5124 | 322.9635
2572.6293 | 2425.6293 | 477.815 | 385.715 | 442.5074 | 394.0947 | 423.8121 | 414.6035 | 405.4791 | 381.5475 | 323.0158
2573.6307 | 2426.6307 | 477.8892 | 385.6442 | 442.4997 | 394.1238 | 423.7909 | 414.5942 | 405.4969 | 381.588 | 323.0642
2574.6321 | 2427.6321 | 477.9013 | 385.7465 | 442.5816 | 394.1441 | 423.7644 | 414.6184 | 405.5164 | 381.6116 | 323.1318
2575.6336 | 2428.6336 | 477.8436 | 385.7566 | 442.4644 | 394.1431 | 423.7788 | 414.6138 | 405.5402 | 381.6644 | 323.1733
2576.635 | 2429.635 | 477.81 | 385.7938 | 442.4193 | 394.183 | 423.8207 | 414.5909 | 405.5568 | 381.6735 | 323.2665
2577.6264 | 2430.6264 | 477.9373 | 385.83 | 442.4968 | 394.1948 | 423.8651 | 414.5627 | 405.5679 | 381.7308 | 323.3005
2578.6279 | 2431.6279 | 478.0424 | 385.8507 | 442.5414 | 394.2308 | 423.882 | 414.5294 | 405.5869 | 381.754 | 323.3689
2579.6293 | 2432.6293 | 478.1732 | 385.8614 | 442.5882 | 394.2437 | 423.8219 | 414.488 | 405.6029 | 381.7871 | 323.3966
2580.6308 | 2433.6308 | 478.2693 | 385.868 | 442.6334 | 394.2553 | 423.8776 | 414.4829 | 405.6141 | 381.8372 | 323.4461
2581.6322 | 2434.6322 | 478.1705 | 385.8847 | 442.4254 | 394.2826 | 423.9104 | 414.4773 | 405.6426 | 381.8435 | 323.4931
2582.6336 | 2435.6336 | 478.1556 | 385.9017 | 442.5616 | 394.272 | 423.9756 | 414.5254 | 405.6515 | 381.8967 | 323.5038
2583.6351 | 2436.6351 | 478.0253 | 385.9318 | 442.5169 | 394.32 | 423.9399 | 414.5155 | 405.6752 | 381.9181 | 323.5665
2584.6265 | 2437.6265 | 477.9972 | 385.9502 | 442.4909 | 394.3333 | 423.8681 | 414.4997 | 405.6935 | 381.9548 | 323.5979
2585.628 | 2438.628 | 477.8301 | 385.9404 | 442.537 | 394.3449 | 423.9248 | 414.4979 | 405.7113 | 381.9883 | 323.62
2586.6294 | 2439.6294 | 477.7659 | 385.9613 | 442.6226 | 394.3512 | 424.0615 | 414.4947 | 405.7292 | 382.0159 | 323.6509
2587.6308 | 2440.6308 | 477.6411 | 385.9801 | 442.593 | 394.3634 | 424.0881 | 414.461 | 405.7389 | 382.0515 | 323.6932
2588.6323 | 2441.6323 | 477.5271 | 385.9949 | 442.6321 | 394.373 | 424.1176 | 414.4405 | 405.7613 | 382.0736 | 323.7459
2589.6237 | 2442.6237 | 477.4452 | 385.9724 | 442.6401 | 394.4164 | 424.172 | 414.4256 | 405.7751 | 382.1102 | 323.7865
2590.6251 | 2443.6251 | 477.3059 | 386.0372 | 442.7051 | 394.3993 | 424.1775 | 414.3688 | 405.7898 | 382.1273 | 323.8271
2591.6266 | 2444.6266 | 477.1494 | 385.9918 | 442.5412 | 394.4335 | 424.1935 | 414.3615 | 405.8086 | 382.145 | 323.8895
2592.628 | 2445.628 | 477.0391 | 386.0495 | 442.5791 | 394.4595 | 424.16 | 414.3434 | 405.8361 | 382.1907 | 323.9133
2593.6295 | 2446.6295 | 477.1033 | 386.0789 | 442.64 | 394.4653 | 424.1755 | 414.3215 | 405.8587 | 382.1937 | 323.9828
2594.6309 | 2447.6309 | 477.1316 | 386.0581 | 442.7065 | 394.4947 | 424.2257 | 414.2913 | 405.8812 | 382.2324 | 324.0106
2595.6323 | 2448.6323 | 477.2417 | 386.1178 | 442.6606 | 394.4858 | 424.2596 | 414.2813 | 405.8904 | 382.2694 | 324.0821
2596.6338 | 2449.6338 | 477.257 | 386.1173 | 442.6028 | 394.5268 | 424.3057 | 414.2646 | 405.9146 | 382.313 | 324.0627
2597.6352 | 2450.6352 | 477.1955 | 385.9998 | 442.599 | 394.5446 | 424.3739 | 414.2328 | 405.9414 | 382.3379 | 324.0823
2598.6367 | 2451.6367 | 477.2391 | 386.0524 | 442.5566 | 394.5583 | 424.422 | 414.1766 | 405.9627 | 382.3441 | 324.1401
2599.6281 | 2452.6281 | 477.2258 | 386.1395 | 442.6004 | 394.5272 | 424.4538 | 414.1467 | 405.9845 | 382.3836 | 324.1564
2600.6295 | 2453.6295 | 477.174 | 386.1294 | 442.5422 | 394.5341 | 424.5093 | 414.1294 | 405.9997 | 382.4102 | 324.2155
2601.631 | 2454.631 | 477.1759 | 386.1987 | 442.5575 | 394.545 | 424.5365 | 414.1062 | 406.0201 | 382.4413 | 324.2598
2602.6324 | 2455.6324 | 477.129 | 386.1749 | 442.4962 | 394.5178 | 424.5419 | 414.0897 | 406.0322 | 382.4922 | 324.2966
2603.6338 | 2456.6338 | 476.9358 | 386.1849 | 442.4433 | 394.5558 | 424.5054 | 414.0288 | 406.0584 | 382.5162 | 324.3405
2604.6353 | 2457.6353 | 476.8826 | 386.2118 | 442.4936 | 394.5788 | 424.5059 | 413.9932 | 406.0713 | 382.5261 | 324.4255
2605.6267 | 2458.6267 | 476.9257 | 386.2422 | 442.4962 | 394.6156 | 424.5033 | 413.9407 | 406.0869 | 382.5645 | 324.44
2606.6281 | 2459.6281 | 477.0554 | 386.2243 | 442.5433 | 394.6159 | 424.557 | 413.8863 | 406.1128 | 382.6043 | 324.4651
2607.6296 | 2460.6296 | 477.042 | 386.271 | 442.6103 | 394.6115 | 424.6453 | 413.8305 | 406.1223 | 382.6447 | 324.5218
2608.631 | 2461.631 | 477.1022 | 386.2561 | 442.57 | 394.6735 | 424.671 | 413.7708 | 406.1425 | 382.6751 | 324.5381
2609.6325 | 2462.6325 | 477.1274 | 386.215 | 442.5923 | 394.6632 | 424.5871 | 413.7351 | 406.1627 | 382.6739 | 324.6093
2610.6339 | 2463.6339 | 477.0716 | 386.2431 | 442.6117 | 394.7056 | 424.5465 | 413.7137 | 406.1738 | 382.7197 | 324.6398
2611.6253 | 2464.6253 | 477.0583 | 386.2201 | 442.7064 | 394.6901 | 424.5326 | 413.707 | 406.1875 | 382.7617 | 324.6403
2612.6268 | 2465.6268 | 477.1727 | 386.2794 | 442.6659 | 394.7276 | 424.5339 | 413.6854 | 406.1938 | 382.7773 | 324.6723
2613.6282 | 2466.6282 | 477.2431 | 386.2495 | 442.6148 | 394.6882 | 424.5438 | 413.6663 | 406.1892 | 382.8357 | 324.6889
2614.6297 | 2467.6297 | 477.2623 | 386.3534 | 442.6443 | 394.7285 | 424.5578 | 413.6384 | 406.2039 | 382.8688 | 324.6942
2615.6311 | 2468.6311 | 477.2958 | 386.3878 | 442.6081 | 394.8037 | 424.5834 | 413.6514 | 406.2009 | 382.8809 | 324.7824
2616.6325 | 2469.6325 | 477.3785 | 386.3533 | 442.5689 | 394.8034 | 424.5855 | 413.6611 | 406.2087 | 382.9264 | 324.8164
2617.634 | 2470.634 | 477.402 | 386.3801 | 442.6474 | 394.801 | 424.5529 | 413.6437 | 406.2196 | 382.9525 | 324.8482
2618.6254 | 2471.6254 | 477.418 | 386.4129 | 442.613 | 394.8603 | 424.5955 | 413.6519 | 406.2259 | 382.9776 | 324.9241
2619.6268 | 2472.6268 | 477.393 | 386.4407 | 442.5815 | 394.8243 | 424.573 | 413.6424 | 406.2298 | 383.0177 | 324.9294
2620.6283 | 2473.6283 | 477.3612 | 386.4488 | 442.6513 | 394.897 | 424.5823 | 413.6441 | 406.2344 | 383.0444 | 324.958
2621.6297 | 2474.6297 | 477.4309 | 386.5017 | 442.6375 | 394.9121 | 424.5665 | 413.6302 | 406.2494 | 383.0785 | 324.9685
2622.6312 | 2475.6312 | 477.4646 | 386.4767 | 442.7467 | 394.9165 | 424.5873 | 413.657 | 406.2421 | 383.0988 | 325.0191
2623.6326 | 2476.6326 | 477.6148 | 386.5263 | 442.7696 | 394.958 | 424.5872 | 413.6683 | 406.2605 | 383.1215 | 325.0516
2624.634 | 2477.634 | 477.8365 | 386.5261 | 442.7624 | 394.9005 | 424.6302 | 413.6787 | 406.2607 | 383.1518 | 325.08
2625.6355 | 2478.6355 | 478.0362 | 386.5682 | 442.7487 | 394.9355 | 424.6614 | 413.7077 | 406.2694 | 383.1821 | 325.156
2626.6269 | 2479.6269 | 478.2332 | 386.5626 | 442.7939 | 394.9974 | 424.7173 | 413.7455 | 406.2779 | 383.2076 | 325.1891
2627.6283 | 2480.6283 | 478.3535 | 386.5268 | 442.7602 | 395.0064 | 424.7488 | 413.7712 | 406.2873 | 383.2356 | 325.237
2628.6298 | 2481.6298 | 478.4919 | 386.5552 | 442.6983 | 394.9423 | 424.6965 | 413.7458 | 406.3001 | 383.2675 | 325.2819
2629.6312 | 2482.6312 | 478.6266 | 386.6078 | 442.7972 | 394.908 | 424.6864 | 413.6999 | 406.309 | 383.3137 | 325.3071
2630.6327 | 2483.6327 | 478.8371 | 386.6068 | 442.7954 | 394.9714 | 424.6501 | 413.6572 | 406.3285 | 383.3141 | 325.353
2631.6241 | 2484.6241 | 478.7809 | 386.5824 | 442.8396 | 395.0271 | 424.637 | 413.64 | 406.3344 | 383.3447 | 325.4131
2632.6255 | 2485.6255 | 478.6166 | 386.6092 | 442.8013 | 395.0405 | 424.5727 | 413.6106 | 406.3548 | 383.3946 | 325.4013
2633.627 | 2486.627 | 478.5437 | 386.6627 | 442.7392 | 395.0581 | 424.6253 | 413.6066 | 406.3626 | 383.4208 | 325.4332
2634.6284 | 2487.6284 | 478.5679 | 386.6981 | 442.6659 | 395.0938 | 424.6685 | 413.5891 | 406.3755 | 383.4346 | 325.4584
2635.6298 | 2488.6298 | 478.4463 | 386.7204 | 442.778 | 395.1191 | 424.7281 | 413.6001 | 406.3781 | 383.466 | 325.496
2636.6313 | 2489.6313 | 478.3989 | 386.744 | 442.7877 | 395.1392 | 424.7759 | 413.6005 | 406.3994 | 383.4964 | 325.5632
2637.6327 | 2490.6327 | 478.406 | 386.7353 | 442.8069 | 395.1514 | 424.801 | 413.6068 | 406.4045 | 383.514 | 325.6315
2638.6242 | 2491.6242 | 478.3927 | 386.7451 | 442.8198 | 395.177 | 424.8463 | 413.6256 | 406.4197 | 383.5406 | 325.646
2639.6256 | 2492.6256 | 478.2805 | 386.8207 | 442.8109 | 395.1907 | 424.877 | 413.6376 | 406.4415 | 383.5636 | 325.6879
2640.627 | 2493.627 | 478.0592 | 386.798 | 442.8929 | 395.2119 | 424.9587 | 413.689 | 406.4442 | 383.5928 | 325.7338
2641.6285 | 2494.6285 | 477.9091 | 386.7602 | 442.8588 | 395.2244 | 424.9428 | 413.7093 | 406.4636 | 383.6224 | 325.7848
2642.6299 | 2495.6299 | 477.8642 | 386.7711 | 442.9545 | 395.2382 | 424.9457 | 413.7483 | 406.4695 | 383.6394 | 325.8246
2643.6314 | 2496.6314 | 477.8747 | 386.8512 | 442.8594 | 395.2508 | 424.9251 | 413.7562 | 406.4897 | 383.6924 | 325.8085
2644.6328 | 2497.6328 | 477.9104 | 386.8314 | 442.9151 | 395.2465 | 424.9145 | 413.7758 | 406.5014 | 383.7265 | 325.8469
2645.6342 | 2498.6342 | 477.9871 | 386.9213 | 442.9357 | 395.2736 | 424.9044 | 413.7601 | 406.5154 | 383.7394 | 325.9108
2646.6357 | 2499.6357 | 478.0751 | 386.9465 | 442.8421 | 395.2778 | 424.9151 | 413.8087 | 406.5234 | 383.742 | 325.9776
2647.6271 | 2500.6271 | 478.1747 | 386.9498 | 442.8618 | 395.2824 | 424.9394 | 413.8415 | 406.5418 | 383.7899 | 326.0038
2648.6285 | 2501.6285 | 478.1688 | 386.9517 | 442.9005 | 395.3128 | 424.9586 | 413.8445 | 406.5603 | 383.8214 | 326.0806
2649.63 | 2502.63 | 478.0419 | 386.9491 | 442.9548 | 395.3245 | 424.9809 | 413.8485 | 406.5786 | 383.8538 | 326.1203
2650.6314 | 2503.6314 | 477.9998 | 386.9857 | 442.9074 | 395.355 | 424.9824 | 413.8422 | 406.5758 | 383.8639 | 326.1802
2651.6329 | 2504.6329 | 477.9268 | 387.0045 | 442.9621 | 395.3327 | 425.0112 | 413.8568 | 406.5861 | 383.8901 | 326.2238
2652.6243 | 2505.6243 | 477.6666 | 386.9906 | 442.8935 | 395.3661 | 425.0165 | 413.8544 | 406.5953 | 383.9399 | 326.2493
2653.6257 | 2506.6257 | 477.5153 | 387.0087 | 442.9599 | 395.3978 | 424.9891 | 413.8759 | 406.6046 | 383.9655 | 326.2607
2654.6272 | 2507.6272 | 477.5577 | 387.0207 | 442.8854 | 395.4104 | 425.0041 | 413.8641 | 406.6258 | 383.9919 | 326.2972
2655.6286 | 2508.6286 | 477.6771 | 387.0575 | 442.9763 | 395.445 | 425.0049 | 413.892 | 406.6359 | 384.003 | 326.3262
2656.63 | 2509.63 | 477.5899 | 387.0888 | 442.9505 | 395.4615 | 424.9833 | 413.9109 | 406.6467 | 384.0306 | 326.2997
2657.6315 | 2510.6315 | 477.4102 | 387.0624 | 442.9245 | 395.4589 | 424.9913 | 413.9284 | 406.668 | 384.0601 | 326.2573
2658.6329 | 2511.6329 | 477.3363 | 387.1221 | 442.8818 | 395.4848 | 425.0112 | 413.94 | 406.6824 | 384.0859 | 326.2945
2659.6344 | 2512.6344 | 477.2243 | 387.0894 | 442.9629 | 395.4667 | 424.9889 | 413.9594 | 406.6975 | 384.1318 | 326.3182
2660.6358 | 2513.6358 | 477.2345 | 387.1456 | 442.9024 | 395.4934 | 425.0132 | 413.9842 | 406.7115 | 384.1495 | 326.4176
2661.6272 | 2514.6272 | 477.1601 | 387.0934 | 442.9634 | 395.4958 | 425.0109 | 413.9895 | 406.7294 | 384.1691 | 326.4392
2662.6287 | 2515.6287 | 477.0785 | 387.1749 | 442.9582 | 395.5383 | 424.9974 | 414.0095 | 406.745 | 384.2003 | 326.4876
2663.6301 | 2516.6301 | 476.9243 | 387.2098 | 442.9698 | 395.537 | 424.9576 | 414.0227 | 406.7548 | 384.221 | 326.5306
2664.6316 | 2517.6316 | 476.8851 | 387.1813 | 442.9878 | 395.5533 | 425.0109 | 414.0651 | 406.7638 | 384.2627 | 326.5325
2665.633 | 2518.633 | 476.9383 | 387.1975 | 443.0013 | 395.5746 | 425.0578 | 414.0769 | 406.7761 | 384.2997 | 326.544
2666.6344 | 2519.6344 | 476.9487 | 387.2145 | 442.9886 | 395.5962 | 425.0795 | 414.0887 | 406.7931 | 384.3038 | 326.5783
2667.6359 | 2520.6359 | 476.7767 | 387.2341 | 442.9858 | 395.5904 | 425.0515 | 414.1168 | 406.8 | 384.3325 | 326.6246
2668.6273 | 2521.6273 | 476.6521 | 387.2254 | 442.9448 | 395.586 | 424.9571 | 414.1442 | 406.8206 | 384.3573 | 326.6732
2669.6287 | 2522.6287 | 476.6942 | 387.27 | 442.9909 | 395.598 | 424.9152 | 414.1872 | 406.8281 | 384.4062 | 326.6974
2670.6302 | 2523.6302 | 476.685 | 387.2278 | 442.9901 | 395.6336 | 424.8649 | 414.1853 | 406.8542 | 384.4057 | 326.7912
2671.6316 | 2524.6316 | 476.7122 | 387.2265 | 442.9658 | 395.6436 | 424.8193 | 414.2038 | 406.8582 | 384.4485 | 326.7494
2672.6331 | 2525.6331 | 476.6296 | 387.3125 | 442.978 | 395.6719 | 424.7716 | 414.1998 | 406.8723 | 384.4623 | 326.8075
2673.6245 | 2526.6245 | 476.456 | 387.3271 | 443.0075 | 395.7021 | 424.7676 | 414.2069 | 406.8828 | 384.5061 | 326.8542
2674.6259 | 2527.6259 | 476.3934 | 387.3254 | 442.9748 | 395.6986 | 424.7605 | 414.1849 | 406.9091 | 384.5171 | 326.9466
2675.6274 | 2528.6274 | 476.4165 | 387.3552 | 442.9927 | 395.7119 | 424.7679 | 414.193 | 406.9198 | 384.5352 | 326.9927
2676.6288 | 2529.6288 | 476.5245 | 387.3481 | 443.0083 | 395.7128 | 424.7932 | 414.203 | 406.9352 | 384.552 | 327.0385
2677.6302 | 2530.6302 | 476.528 | 387.402 | 443.0026 | 395.7217 | 424.7746 | 414.2148 | 406.9471 | 384.5756 | 327.1023
2678.6317 | 2531.6317 | 476.4877 | 387.4459 | 443.0121 | 395.7359 | 424.7745 | 414.205 | 406.9537 | 384.6086 | 327.1198
2679.6331 | 2532.6331 | 476.4014 | 387.3915 | 443.0083 | 395.7614 | 424.7657 | 414.1984 | 406.963 | 384.6292 | 327.1179
2680.6245 | 2533.6245 | 476.3879 | 387.4561 | 443.0133 | 395.7574 | 424.7603 | 414.2 | 406.973 | 384.651 | 327.1392
2681.626 | 2534.626 | 476.3496 | 387.4778 | 443.0099 | 395.7834 | 424.7583 | 414.2016 | 406.9996 | 384.6766 | 327.1566
2682.6274 | 2535.6274 | 476.2883 | 387.4726 | 442.9192 | 395.8106 | 424.7763 | 414.235 | 406.9983 | 384.7092 | 327.2147
2683.6289 | 2536.6289 | 476.4181 | 387.5072 | 442.8905 | 395.839 | 424.7733 | 414.2746 | 407.0169 | 384.7487 | 327.2367
2684.6303 | 2537.6303 | 476.492 | 387.4979 | 443.0333 | 395.8105 | 424.806 | 414.3109 | 407.0384 | 384.7696 | 327.2265
2685.6317 | 2538.6317 | 476.5191 | 387.5451 | 443.0747 | 395.8444 | 424.8277 | 414.3108 | 407.0464 | 384.7729 | 327.2764
2686.6332 | 2539.6332 | 476.5019 | 387.5424 | 443.0091 | 395.8601 | 424.8511 | 414.3295 | 407.0619 | 384.805 | 327.3175
2687.6346 | 2540.6346 | 476.5564 | 387.549 | 442.9806 | 395.8638 | 424.8581 | 414.3262 | 407.0739 | 384.832 | 327.3683
2688.6361 | 2541.6361 | 476.5737 | 387.5706 | 443.0697 | 395.8705 | 424.7844 | 414.3441 | 407.0924 | 384.8604 | 327.4141
2689.6275 | 2542.6275 | 476.6261 | 387.5743 | 443.0324 | 395.8237 | 424.784 | 414.352 | 407.1007 | 384.8811 | 327.4297
2690.6289 | 2543.6289 | 476.6567 | 387.6064 | 443.0254 | 395.8092 | 424.7678 | 414.3831 | 407.1181 | 384.8967 | 327.482
2691.6304 | 2544.6304 | 476.8661 | 387.6429 | 443.01 | 395.7448 | 424.7739 | 414.4249 | 407.1322 | 384.9273 | 327.5366
2692.6318 | 2545.6318 | 477.0244 | 387.6919 | 443.0721 | 395.8402 | 424.7718 | 414.4448 | 407.1743 | 384.9555 | 327.5504
2693.6333 | 2546.6333 | 477.1017 | 387.6431 | 443.0448 | 395.8678 | 424.7901 | 414.478 | 407.1852 | 384.959 | 327.582
2694.6247 | 2547.6247 | 477.119 | 387.6783 | 443.0076 | 395.9174 | 424.8005 | 414.4824 | 407.1972 | 385.0012 | 327.6153
2695.6261 | 2548.6261 | 477.1815 | 387.6821 | 443.0336 | 395.93 | 424.816 | 414.5211 | 407.2064 | 385.0423 | 327.6586
2696.6276 | 2549.6276 | 477.2672 | 387.7465 | 443.0665 | 395.9435 | 424.8095 | 414.5232 | 407.2155 | 385.0655 | 327.6925
2697.629 | 2550.629 | 477.2491 | 387.7547 | 443.1238 | 395.9926 | 424.8339 | 414.5373 | 407.2677 | 385.0937 | 327.7604
2698.6304 | 2551.6304 | 477.2828 | 387.7766 | 443.0501 | 395.9767 | 424.7171 | 414.5098 | 407.2618 | 385.1303 | 327.7846
2699.6319 | 2552.6319 | 477.3855 | 387.8031 | 443.1629 | 396.0455 | 424.684 | 414.4906 | 407.2652 | 385.158 | 327.8088
2700.6333 | 2553.6333 | 477.4541 | 387.78 | 443.1792 | 396.0495 | 424.6952 | 414.4897 | 407.2785 | 385.1694 | 327.8606
2701.6348 | 2554.6348 | 477.5065 | 387.8268 | 443.1671 | 396.0726 | 424.7017 | 414.4829 | 407.3141 | 385.2023 | 327.8983
2702.6262 | 2555.6262 | 477.4613 | 387.8481 | 443.0768 | 396.117 | 424.7184 | 414.5213 | 407.3298 | 385.2274 | 327.9226
2703.6276 | 2556.6276 | 477.4082 | 387.8322 | 443.1493 | 396.0879 | 424.7433 | 414.5356 | 407.3403 | 385.2548 | 327.9376
2704.6291 | 2557.6291 | 477.3495 | 387.8599 | 443.0928 | 396.0256 | 424.7715 | 414.5808 | 407.335 | 385.2675 | 328.0073
2705.6305 | 2558.6305 | 477.3527 | 387.8717 | 443.1164 | 396.0584 | 424.7787 | 414.553 | 407.3546 | 385.3019 | 328.0222
2706.6319 | 2559.6319 | 477.4091 | 387.9054 | 443.1752 | 396.0857 | 424.8138 | 414.5386 | 407.3787 | 385.3182 | 328.0849
2707.6334 | 2560.6334 | 477.3829 | 387.9222 | 443.1414 | 396.1263 | 424.8389 | 414.5092 | 407.3901 | 385.3376 | 328.1056
2708.6348 | 2561.6348 | 477.3187 | 387.9252 | 443.2016 | 396.1257 | 424.8493 | 414.4754 | 407.4538 | 385.3666 | 328.1125
2709.6363 | 2562.6363 | 477.3108 | 387.9119 | 443.1381 | 396.1678 | 424.8368 | 414.441 | 407.4356 | 385.3798 | 328.1542
2710.6277 | 2563.6277 | 477.2953 | 387.947 | 443.208 | 396.2038 | 424.8289 | 414.3546 | 407.4493 | 385.426 | 328.1612
2711.6291 | 2564.6291 | 477.1406 | 387.9849 | 443.1595 | 396.1701 | 424.8238 | 414.2981 | 407.4636 | 385.4319 | 328.1798
2712.6306 | 2565.6306 | 477.105 | 387.9949 | 443.2344 | 396.174 | 424.806 | 414.2451 | 407.5038 | 385.4657 | 328.1981
2713.632 | 2566.632 | 477.0556 | 388.0084 | 443.193 | 396.1296 | 424.8305 | 414.2439 | 407.5028 | 385.4792 | 328.2652
2714.6335 | 2567.6335 | 477.1568 | 388.061 | 443.2189 | 396.1677 | 424.8197 | 414.2201 | 407.5045 | 385.5271 | 328.2794
2715.6249 | 2568.6249 | 477.1496 | 388.0704 | 443.083 | 396.1827 | 424.8523 | 414.2245 | 407.5093 | 385.5355 | 328.3232
2716.6263 | 2569.6263 | 477.0909 | 388.0923 | 443.0796 | 396.1607 | 424.8817 | 414.2734 | 407.5185 | 385.5742 | 328.3393
2717.6278 | 2570.6278 | 476.9929 | 388.0879 | 443.1582 | 396.235 | 424.8586 | 414.2658 | 407.5401 | 385.5775 | 328.4345
2718.6292 | 2571.6292 | 476.9778 | 388.0985 | 443.166 | 396.2893 | 424.8411 | 414.1688 | 407.5638 | 385.5938 | 328.4685
2719.6306 | 2572.6306 | 477.0784 | 388.1245 | 443.2026 | 396.3395 | 424.8381 | 414.1353 | 407.5848 | 385.6268 | 328.5197
2720.6321 | 2573.6321 | 477.1897 | 388.1672 | 443.2416 | 396.2982 | 424.8405 | 414.1942 | 407.5975 | 385.6539 | 328.5353
2721.6335 | 2574.6335 | 477.3088 | 388.1828 | 443.1938 | 396.3373 | 424.8362 | 414.1999 | 407.6061 | 385.6675 | 328.5572
2722.635 | 2575.635 | 477.4795 | 388.1513 | 443.255 | 396.3416 | 424.867 | 414.1718 | 407.6157 | 385.6876 | 328.593
2723.6264 | 2576.6264 | 477.5243 | 388.1795 | 443.2001 | 396.3557 | 424.878 | 414.1325 | 407.629 | 385.714 | 328.6167
2724.6278 | 2577.6278 | 477.5558 | 388.2297 | 443.2167 | 396.3672 | 424.9224 | 414.1352 | 407.6456 | 385.7284 | 328.7027
2725.6293 | 2578.6293 | 477.5394 | 388.1801 | 443.2704 | 396.3941 | 424.9047 | 414.1462 | 407.6555 | 385.7617 | 328.7505
2726.6307 | 2579.6307 | 477.4965 | 388.2118 | 443.323 | 396.4276 | 424.8671 | 414.3311 | 407.6592 | 385.7873 | 328.7802
2727.6321 | 2580.6321 | 477.4777 | 388.2272 | 443.265 | 396.4318 | 424.8846 | 414.2729 | 407.6745 | 385.8273 | 328.7877
2728.6336 | 2581.6336 | 477.4672 | 388.2623 | 443.2057 | 396.4097 | 424.895 | 414.1687 | 407.6912 | 385.8309 | 328.8491
2729.635 | 2582.635 | 477.3677 | 388.2532 | 443.278 | 396.4133 | 424.8797 | 414.1286 | 407.7117 | 385.8461 | 328.8834
2730.6365 | 2583.6365 | 477.2472 | 388.27 | 443.3369 | 396.4373 | 424.888 | 414.1212 | 407.7379 | 385.8744 | 328.932
2731.6279 | 2584.6279 | 477.181 | 388.3026 | 443.3376 | 396.4357 | 424.9083 | 414.1005 | 407.7449 | 385.898 | 328.9517
2732.6293 | 2585.6293 | 477.0965 | 388.2962 | 443.3312 | 396.4766 | 424.9127 | 414.0997 | 407.7606 | 385.9271 | 328.9776
2733.6308 | 2586.6308 | 476.753 | 388.2735 | 443.3743 | 396.4553 | 424.9431 | 414.0688 | 407.7803 | 385.9366 | 329.0249
2734.6322 | 2587.6322 | 476.4601 | 388.2859 | 443.33 | 396.4708 | 424.9459 | 414.0626 | 407.7953 | 385.9723 | 329.026
2735.6336 | 2588.6336 | 476.3371 | 388.2781 | 443.3443 | 396.4654 | 424.9724 | 414.0784 | 407.8165 | 385.9822 | 329.0675
2736.6351 | 2589.6351 | 476.3238 | 388.301 | 443.3396 | 396.4848 | 424.9735 | 414.1083 | 407.8408 | 386.0089 | 329.0387
2737.6265 | 2590.6265 | 476.1989 | 388.2879 | 443.2469 | 396.491 | 425.0168 | 414.0908 | 407.859 | 386.0262 | 329.1347
2738.628 | 2591.628 | 476.118 | 388.3141 | 443.2771 | 396.5135 | 425.0523 | 414.0477 | 407.8751 | 386.0413 | 329.2056
2739.6294 | 2592.6294 | 476.0675 | 388.3063 | 443.277 | 396.5152 | 425.0868 | 414.0462 | 407.8958 | 386.0778 | 329.2274
2740.6308 | 2593.6308 | 476.0708 | 388.3234 | 443.2187 | 396.5246 | 425.127 | 414.0603 | 407.9103 | 386.1131 | 329.2372
2741.6323 | 2594.6323 | 476.1102 | 388.3372 | 443.1697 | 396.5092 | 425.1565 | 414.0876 | 407.9214 | 386.1323 | 329.2789
2742.6337 | 2595.6337 | 476.0491 | 388.3601 | 443.2688 | 396.5287 | 425.1885 | 414.1347 | 407.932 | 386.1341 | 329.3358
2743.6352 | 2596.6352 | 475.9965 | 388.3637 | 443.1482 | 396.5411 | 425.2162 | 414.1661 | 407.9542 | 386.1736 | 329.3557
2744.6266 | 2597.6266 | 475.9685 | 388.371 | 443.3448 | 396.5436 | 425.241 | 414.1907 | 407.977 | 386.2028 | 329.387
2745.628 | 2598.628 | 476.0412 | 388.3949 | 443.2373 | 396.5305 | 425.2812 | 414.1832 | 407.9975 | 386.2319 | 329.3945
2746.6295 | 2599.6295 | 476.0693 | 388.4019 | 443.2449 | 396.4997 | 425.3309 | 414.1615 | 408.0107 | 386.2448 | 329.4584
2747.6309 | 2600.6309 | 476.1322 | 388.4197 | 443.2105 | 396.5357 | 425.3693 | 414.1853 | 408.0176 | 386.294 | 329.4875
2748.6323 | 2601.6323 | 476.1757 | 388.4422 | 443.1613 | 396.4513 | 425.4054 | 414.1279 | 408.0376 | 386.3068 | 329.5297
2749.6338 | 2602.6338 | 476.1956 | 388.4693 | 443.2336 | 396.398 | 425.3974 | 414.1373 | 408.0506 | 386.3282 | 329.5837
2750.6352 | 2603.6352 | 476.2436 | 388.4688 | 443.1599 | 396.4776 | 425.4071 | 414.126 | 408.0628 | 386.3332 | 329.6289
2751.6367 | 2604.6367 | 476.2014 | 388.4911 | 443.1519 | 396.5377 | 425.4072 | 414.1879 | 408.0879 | 386.3815 | 329.629
2752.6281 | 2605.6281 | 476.3142 | 388.4504 | 443.1778 | 396.5843 | 425.407 | 414.1669 | 408.1189 | 386.3958 | 329.6727
2753.6295 | 2606.6295 | 476.5873 | 388.4596 | 443.0344 | 396.5677 | 425.4153 | 414.1601 | 408.1364 | 386.4295 | 329.6945
2754.631 | 2607.631 | 476.736 | 388.4484 | 443.2417 | 396.5495 | 425.4197 | 414.1086 | 408.1577 | 386.4618 | 329.6985
2755.6324 | 2608.6324 | 476.9138 | 388.5314 | 443.1605 | 396.5223 | 425.4594 | 414.1304 | 408.1606 | 386.4802 | 329.7555
2756.6338 | 2609.6338 | 477.1836 | 388.5857 | 443.109 | 396.5533 | 425.4781 | 414.127 | 408.1757 | 386.5025 | 329.7775
2757.6253 | 2610.6253 | 477.2738 | 388.6193 | 443.086 | 396.5197 | 425.507 | 414.1501 | 408.1813 | 386.5161 | 329.8274
2758.6267 | 2611.6267 | 477.2734 | 388.6231 | 443.1103 | 396.5935 | 425.4401 | 414.2564 | 408.1994 | 386.5328 | 329.8882
2759.6282 | 2612.6282 | 477.3179 | 388.6653 | 443.1873 | 396.6418 | 425.3875 | 414.3354 | 408.2126 | 386.5544 | 329.9356
2760.6296 | 2613.6296 | 477.4687 | 388.6769 | 443.3301 | 396.6898 | 425.386 | 414.3206 | 408.2152 | 386.5952 | 329.9412
2761.631 | 2614.631 | 477.5036 | 388.7113 | 443.2712 | 396.7068 | 425.4162 | 414.3024 | 408.2328 | 386.6156 | 329.9487
2762.6325 | 2615.6325 | 477.6135 | 388.6721 | 443.197 | 396.7321 | 425.4461 | 414.3402 | 408.2381 | 386.6362 | 329.9628
2763.6239 | 2616.6239 | 477.6612 | 388.7993 | 443.2642 | 396.758 | 425.4917 | 414.3415 | 408.2494 | 386.6554 | 329.9801
2764.6253 | 2617.6253 | 477.7204 | 388.7894 | 443.3083 | 396.7712 | 425.5429 | 414.3695 | 408.2549 | 386.6772 | 330.0473
2765.6268 | 2618.6268 | 477.7815 | 388.7861 | 443.2913 | 396.779 | 425.5819 | 414.4012 | 408.266 | 386.7072 | 330.0799
2766.6282 | 2619.6282 | 477.7692 | 388.816 | 443.2624 | 396.7962 | 425.6373 | 414.4729 | 408.2875 | 386.7083 | 330.134
2767.6297 | 2620.6297 | 477.7811 | 388.8739 | 443.1758 | 396.7892 | 425.6685 | 414.4508 | 408.2987 | 386.7338 | 330.1522
2768.6311 | 2621.6311 | 477.7383 | 388.8807 | 443.2261 | 396.7837 | 425.6613 | 414.384 | 408.324 | 386.7651 | 330.1572
2769.6325 | 2622.6325 | 477.6477 | 388.8967 | 443.2141 | 396.8026 | 425.6511 | 414.3213 | 408.344 | 386.7831 | 330.2128
2770.634 | 2623.634 | 477.6815 | 388.9616 | 443.1725 | 396.8283 | 425.6436 | 414.2833 | 408.3697 | 386.8052 | 330.2639
2771.6354 | 2624.6354 | 477.6461 | 388.9385 | 443.2523 | 396.8318 | 425.7074 | 414.3377 | 408.3864 | 386.8268 | 330.3366
2772.6369 | 2625.6369 | 477.6547 | 388.9835 | 443.2362 | 396.8722 | 425.743 | 414.3385 | 408.408 | 386.8454 | 330.3776
2773.6283 | 2626.6283 | 477.566 | 388.9822 | 443.2653 | 396.8526 | 425.7436 | 414.2992 | 408.4232 | 386.8804 | 330.4021
2774.6297 | 2627.6297 | 477.4857 | 389.0172 | 443.1713 | 396.8792 | 425.7131 | 414.2804 | 408.4588 | 386.8792 | 330.4445
2775.6312 | 2628.6312 | 477.4382 | 389.0393 | 443.2833 | 396.8589 | 425.7254 | 414.3226 | 408.4821 | 386.9373 | 330.4225
2776.6326 | 2629.6326 | 477.3836 | 389.0639 | 443.2091 | 396.8652 | 425.7334 | 414.3602 | 408.4978 | 386.9553 | 330.4457
2777.634 | 2630.634 | 477.3111 | 389.0291 | 443.2233 | 396.8983 | 425.7556 | 414.3912 | 408.5279 | 386.9672 | 330.4928
2778.6255 | 2631.6255 | 477.1999 | 389.09 | 443.1647 | 396.9153 | 425.8006 | 414.4261 | 408.5333 | 386.971 | 330.5547
2779.6269 | 2632.6269 | 477.1168 | 389.1183 | 443.1889 | 396.9286 | 425.8071 | 414.4227 | 408.566 | 387.0011 | 330.588
2780.6283 | 2633.6283 | 477.0928 | 389.1076 | 443.2239 | 396.9387 | 425.859 | 414.4653 | 408.5863 | 387.0343 | 330.6274
2781.6298 | 2634.6298 | 477.1375 | 389.1085 | 443.2242 | 396.9439 | 425.8858 | 414.5075 | 408.5875 | 387.0504 | 330.6444
2782.6312 | 2635.6312 | 477.1195 | 389.1458 | 443.2944 | 396.9653 | 425.9272 | 414.5148 | 408.6063 | 387.0811 | 330.6797
2783.6627 | 2636.6627 | 477.0056 | 389.1603 | 443.3231 | 396.984 | 425.9666 | 414.4987 | 408.6211 | 387.1032 | 330.7229
2784.6341 | 2637.6341 | 476.836 | 389.2259 | 443.2913 | 396.9778 | 425.9998 | 414.4848 | 408.6447 | 387.1277 | 330.7502
2785.6255 | 2638.6255 | 476.6654 | 389.2358 | 443.3223 | 396.9976 | 426.0099 | 414.4512 | 408.6566 | 387.1166 | 330.8217
2786.627 | 2639.627 | 476.5543 | 389.252 | 443.3393 | 397.0215 | 426.0294 | 414.4417 | 408.6615 | 387.1462 | 330.8419
2787.6284 | 2640.6284 | 476.3479 | 389.2587 | 443.3122 | 397.0074 | 426.0698 | 414.4551 | 408.6731 | 387.166 | 330.9299
2788.6299 | 2641.6299 | 476.1549 | 389.2381 | 443.2345 | 397.0135 | 426.075 | 414.4826 | 408.6908 | 387.2007 | 330.9548
2789.6313 | 2642.6313 | 476.0415 | 389.2521 | 443.36 | 396.9902 | 426.0948 | 414.5087 | 408.7054 | 387.1977 | 331.0504
2790.6327 | 2643.6327 | 475.9661 | 389.2934 | 443.2619 | 397.0384 | 426.1277 | 414.5131 | 408.7274 | 387.2274 | 331.0781
2791.6542 | 2644.6542 | 475.8928 | 389.3354 | 443.267 | 397.0556 | 426.1691 | 414.5502 | 408.7487 | 387.2584 | 331.1183
2792.6356 | 2645.6356 | 475.7611 | 389.3303 | 443.2426 | 397.0428 | 426.1987 | 414.5961 | 408.7563 | 387.2779 | 331.1428
2793.6371 | 2646.6371 | 475.7933 | 389.3832 | 443.2924 | 397.0832 | 426.2418 | 414.6433 | 408.7645 | 387.295 | 331.1039
2794.6285 | 2647.6285 | 475.8946 | 389.3985 | 443.3168 | 397.0942 | 426.2498 | 414.678 | 408.787 | 387.2934 | 331.1531
2795.6299 | 2648.6299 | 475.9479 | 389.3879 | 443.2625 | 397.0809 | 426.268 | 414.7402 | 408.7968 | 387.3136 | 331.1477
2796.6314 | 2649.6314 | 476.0535 | 389.3856 | 443.2177 | 397.0964 | 426.3071 | 414.7915 | 408.8104 | 387.3214 | 331.1718
2797.6328 | 2650.6328 | 475.9656 | 389.4222 | 443.3206 | 397.1149 | 426.3291 | 414.9022 | 408.8102 | 387.3469 | 331.1925
2798.6443 | 2651.6443 | 476.0528 | 389.4925 | 443.2063 | 397.1394 | 426.3689 | 414.9521 | 408.8173 | 387.3837 | 331.2132
2799.6357 | 2652.6357 | 476.0671 | 389.4831 | 443.2866 | 397.1418 | 426.3926 | 414.8975 | 408.8363 | 387.3897 | 331.2861
2800.6271 | 2653.6271 | 475.9857 | 389.5117 | 443.3533 | 397.1571 | 426.4033 | 414.848 | 408.8469 | 387.4313 | 331.3219
2801.6285 | 2654.6285 | 475.9716 | 389.4701 | 443.3156 | 397.1962 | 426.4193 | 414.738 | 408.8564 | 387.4594 | 331.3433
2802.63 | 2655.63 | 476.0929 | 389.5036 | 443.4003 | 397.1763 | 426.4346 | 414.6975 | 408.8625 | 387.4705 | 331.4185
2803.6314 | 2656.6314 | 476.2424 | 389.5054 | 443.4202 | 397.1623 | 426.4195 | 414.6994 | 408.8775 | 387.503 | 331.4328
2804.6329 | 2657.6329 | 476.3998 | 389.5634 | 443.3696 | 397.1985 | 426.4068 | 414.6547 | 408.8975 | 387.5052 | 331.4482
2805.6343 | 2658.6343 | 476.4143 | 389.6289 | 443.3398 | 397.2515 | 426.3936 | 414.6394 | 408.9258 | 387.5286 | 331.4846
2806.6257 | 2659.6257 | 476.4185 | 389.6185 | 443.3332 | 397.2667 | 426.3951 | 414.7045 | 408.944 | 387.5786 | 331.4668
2807.6272 | 2660.6272 | 476.5103 | 389.6674 | 443.3007 | 397.171 | 426.3979 | 414.7704 | 408.9587 | 387.5958 | 331.535
2808.6286 | 2661.6286 | 476.6329 | 389.6682 | 443.2932 | 397.2037 | 426.3935 | 414.7002 | 408.9799 | 387.6238 | 331.5626
2809.63 | 2662.63 | 476.7752 | 389.7091 | 443.3223 | 397.2717 | 426.4261 | 414.6918 | 408.9947 | 387.6341 | 331.6264
2810.6315 | 2663.6315 | 476.8593 | 389.7522 | 443.3174 | 397.2795 | 426.4408 | 414.7158 | 409.0011 | 387.6614 | 331.6688
2811.6329 | 2664.6329 | 476.9899 | 389.7421 | 443.3328 | 397.3124 | 426.412 | 414.7249 | 408.9845 | 387.68 | 331.6917
2812.6344 | 2665.6344 | 477.212 | 389.7459 | 443.3487 | 397.3402 | 426.4372 | 414.7695 | 408.9975 | 387.6942 | 331.7409
2813.6258 | 2666.6258 | 477.2724 | 389.7898 | 443.3977 | 397.3309 | 426.4689 | 414.8585 | 409.0135 | 387.7196 | 331.7612
2814.6773 | 2667.6773 | 477.4135 | 389.8063 | 443.4426 | 397.3367 | 426.5076 | 414.8783 | 409.0331 | 387.7241 | 331.8521
2815.6287 | 2668.6287 | 477.4833 | 389.7903 | 443.427 | 397.3662 | 426.561 | 414.8139 | 409.0538 | 387.7549 | 331.8837
2816.6301 | 2669.6301 | 477.5518 | 389.8409 | 443.4482 | 397.4093 | 426.5844 | 414.8087 | 409.0875 | 387.7777 | 331.9238
2817.6316 | 2670.6316 | 477.6942 | 389.8679 | 443.3934 | 397.3964 | 426.6285 | 414.8175 | 409.1227 | 387.7879 | 332.0023
2818.633 | 2671.633 | 477.7877 | 389.8756 | 443.3842 | 397.4157 | 426.6708 | 414.8856 | 409.137 | 387.8051 | 332.0213
2819.6344 | 2672.6344 | 477.8192 | 389.89 | 443.4298 | 397.4387 | 426.7117 | 414.8991 | 409.1527 | 387.828 | 332.0251
2820.6359 | 2673.6359 | 477.9918 | 389.8262 | 443.4525 | 397.4398 | 426.7502 | 414.9703 | 409.1773 | 387.8352 | 332.0518
2821.6273 | 2674.6273 | 478.2778 | 389.8139 | 443.4659 | 397.4673 | 426.7836 | 415.0336 | 409.1964 | 387.8754 | 332.0572
2822.6287 | 2675.6287 | 478.2443 | 389.846 | 443.4515 | 397.5001 | 426.8232 | 415.1223 | 409.2201 | 387.8792 | 332.0636
2823.6302 | 2676.6302 | 478.1207 | 389.8862 | 443.5073 | 397.5115 | 426.842 | 415.1148 | 409.2466 | 387.9165 | 332.0733
2824.6316 | 2677.6316 | 478.1994 | 389.9317 | 443.4094 | 397.5602 | 426.8812 | 415.1588 | 409.2559 | 387.9394 | 332.1096
2825.6331 | 2678.6331 | 478.2681 | 389.9516 | 443.4762 | 397.5681 | 426.9051 | 415.1865 | 409.2715 | 387.9471 | 332.1797
2826.6245 | 2679.6245 | 478.2303 | 389.9682 | 443.5123 | 397.5514 | 426.9382 | 415.2255 | 409.2837 | 387.9577 | 332.1813
2827.6259 | 2680.6259 | 478.1332 | 389.986 | 443.4629 | 397.531 | 426.959 | 415.2086 | 409.2976 | 387.9857 | 332.1993
2828.6274 | 2681.6274 | 478.0611 | 389.9802 | 443.4767 | 397.5055 | 426.9904 | 415.2121 | 409.3194 | 387.9976 | 332.2592
2829.6288 | 2682.6288 | 477.8536 | 389.9834 | 443.3704 | 397.5669 | 427.017 | 415.1792 | 409.3485 | 388.0253 | 332.2371
2830.6302 | 2683.6302 | 477.6559 | 390.0056 | 443.5722 | 397.5576 | 427.013 | 415.1535 | 409.363 | 388.0411 | 332.2574
2831.6517 | 2684.6517 | 477.5533 | 390.069 | 443.5163 | 397.5913 | 426.9774 | 415.1517 | 409.3837 | 388.0545 | 332.3257
2832.6331 | 2685.6331 | 477.4138 | 390.0784 | 443.5216 | 397.614 | 426.9375 | 415.1516 | 409.387 | 388.0736 | 332.3844
2833.6346 | 2686.6346 | 477.4002 | 390.0849 | 443.566 | 397.6208 | 426.9037 | 415.1937 | 409.3906 | 388.1008 | 332.4292
2834.636 | 2687.636 | 477.4505 | 390.0926 | 443.5022 | 397.5547 | 426.865 | 415.134 | 409.4118 | 388.1186 | 332.4996
2835.6274 | 2688.6274 | 477.4306 | 390.0943 | 443.501 | 397.5504 | 426.8647 | 415.1314 | 409.4327 | 388.1129 | 332.5758
2836.6289 | 2689.6289 | 477.4582 | 390.1376 | 443.4429 | 397.5828 | 426.8897 | 415.1746 | 409.4398 | 388.1539 | 332.5798
2837.6303 | 2690.6303 | 477.3292 | 390.1216 | 443.4689 | 397.6097 | 426.9183 | 415.2438 | 409.4389 | 388.1775 | 332.622
2838.6318 | 2691.6318 | 477.3088 | 390.1539 | 443.5302 | 397.6521 | 426.9705 | 415.4664 | 409.4478 | 388.1987 | 332.6473
2839.6332 | 2692.6332 | 477.3786 | 390.1567 | 443.4699 | 397.6475 | 427.0307 | 415.68 | 409.452 | 388.2228 | 332.6636
2840.6346 | 2693.6346 | 477.305 | 390.1624 | 443.323 | 397.6679 | 427.0899 | 415.7467 | 409.4579 | 388.2455 | 332.6876
2841.6361 | 2694.6361 | 477.3012 | 390.1631 | 443.4549 | 397.6817 | 427.1482 | 415.776 | 409.4667 | 388.2676 | 332.7047
2842.6275 | 2695.6275 | 477.3053 | 390.2158 | 443.4933 | 397.6952 | 427.1884 | 415.7339 | 409.4852 | 388.2833 | 332.7406
2843.6289 | 2696.6289 | 477.3404 | 390.2254 | 443.4495 | 397.705 | 427.247 | 415.6715 | 409.5058 | 388.2958 | 332.7639
2844.6304 | 2697.6304 | 477.359 | 390.222 | 443.439 | 397.6879 | 427.2988 | 415.7085 | 409.5212 | 388.3273 | 332.7721
2845.6318 | 2698.6318 | 477.2565 | 390.2591 | 443.4779 | 397.7315 | 427.3447 | 415.6907 | 409.5433 | 388.3397 | 332.8317
2846.6433 | 2699.6433 | 477.1718 | 390.25 | 443.4889 | 397.7109 | 427.3768 | 415.743 | 409.5834 | 388.3705 | 332.8636
2847.6347 | 2700.6347 | 477.2202 | 390.3063 | 443.4733 | 397.7249 | 427.4218 | 415.8015 | 409.6093 | 388.3722 | 332.8926
2848.6261 | 2701.6261 | 477.1755 | 390.2486 | 443.501 | 397.736 | 427.4063 | 415.8252 | 409.6364 | 388.3926 | 332.9229
2849.6276 | 2702.6276 | 477.1796 | 390.3207 | 443.5806 | 397.7471 | 427.3953 | 415.8388 | 409.6629 | 388.3886 | 332.9766
2850.629 | 2703.629 | 477.0867 | 390.226 | 443.6481 | 397.7443 | 427.3812 | 415.7995 | 409.6876 | 388.4088 | 332.9978
2851.6304 | 2704.6304 | 477.0212 | 390.1928 | 443.5994 | 397.7631 | 427.3746 | 415.7858 | 409.7093 | 388.4422 | 333.0031
2852.6319 | 2705.6319 | 477.0105 | 390.3256 | 443.5455 | 397.7837 | 427.3903 | 415.7567 | 409.7222 | 388.4571 | 333.0419
2853.6333 | 2706.6333 | 476.9842 | 390.3447 | 443.6683 | 397.7915 | 427.3871 | 415.6646 | 409.7406 | 388.4851 | 333.0682
2854.6247 | 2707.6247 | 476.9281 | 390.3452 | 443.7276 | 397.7969 | 427.3767 | 415.6626 | 409.7588 | 388.5029 | 333.0929
2855.6262 | 2708.6262 | 476.9654 | 390.3555 | 443.6084 | 397.837 | 427.2771 | 415.6453 | 409.7914 | 388.5091 | 333.1119
2856.6276 | 2709.6276 | 476.8982 | 390.3756 | 443.6575 | 397.8277 | 427.203 | 415.6604 | 409.8022 | 388.5532 | 333.1187
2857.6291 | 2710.6291 | 476.8863 | 390.3777 | 443.6039 | 397.8477 | 427.1667 | 415.7096 | 409.8147 | 388.561 | 333.1355
2858.6305 | 2711.6305 | 476.8579 | 390.4373 | 443.5501 | 397.8225 | 427.1616 | 415.7625 | 409.8078 | 388.6039 | 333.1588
2859.6319 | 2712.6319 | 476.895 | 390.3645 | 443.5984 | 397.8903 | 427.1466 | 415.8312 | 409.8157 | 388.6037 | 333.2358
2860.6334 | 2713.6334 | 476.8849 | 390.3949 | 443.5864 | 397.8821 | 427.1406 | 415.9955 | 409.8254 | 388.6371 | 333.2489
2861.6348 | 2714.6348 | 476.7663 | 390.4512 | 443.6138 | 397.8838 | 427.1979 | 415.9388 | 409.8368 | 388.6499 | 333.2995
2862.6363 | 2715.6363 | 476.6973 | 390.3527 | 443.5679 | 397.9186 | 427.2278 | 415.9593 | 409.8352 | 388.6755 | 333.3198
2863.6277 | 2716.6277 | 476.5475 | 390.4392 | 443.5978 | 397.92 | 427.2364 | 416.0774 | 409.8467 | 388.706 | 333.3173
2864.6291 | 2717.6291 | 476.4538 | 390.4369 | 443.7117 | 397.9405 | 427.2705 | 416.1206 | 409.8712 | 388.7309 | 333.3747
2865.6306 | 2718.6306 | 476.4093 | 390.5181 | 443.6445 | 397.9281 | 427.2885 | 416.115 | 409.8918 | 388.7293 | 333.4195
2866.632 | 2719.632 | 476.4056 | 390.4925 | 443.5876 | 397.9294 | 427.3236 | 416.0083 | 409.905 | 388.7467 | 333.4539
2867.6335 | 2720.6335 | 476.4169 | 390.5278 | 443.5973 | 397.974 | 427.3608 | 416.0064 | 409.9213 | 388.7868 | 333.4528
2868.6249 | 2721.6249 | 476.4443 | 390.5466 | 443.6125 | 397.9676 | 427.3994 | 416.0151 | 409.9404 | 388.8046 | 333.5283
2869.6263 | 2722.6263 | 476.3318 | 390.5467 | 443.5414 | 397.9591 | 427.4337 | 416.0405 | 409.969 | 388.8296 | 333.5569
2870.6278 | 2723.6278 | 476.2755 | 390.4708 | 443.5569 | 398.007 | 427.4605 | 416.0857 | 409.9976 | 388.8531 | 333.6007
2871.6292 | 2724.6292 | 476.3309 | 390.5446 | 443.5793 | 397.9794 | 427.4875 | 416.2683 | 410.0165 | 388.8637 | 333.6176
2872.6306 | 2725.6306 | 476.3316 | 390.5247 | 443.5056 | 397.9674 | 427.5088 | 416.3235 | 410.0463 | 388.9011 | 333.6479
2873.6321 | 2726.6321 | 476.4087 | 390.5178 | 443.4509 | 397.987 | 427.5353 | 416.3631 | 410.0812 | 388.9114 | 333.6937
2874.6335 | 2727.6335 | 476.546 | 390.5784 | 443.5277 | 397.989 | 427.5615 | 416.4083 | 410.0962 | 388.9355 | 333.7329
2875.635 | 2728.635 | 476.5755 | 390.6332 | 443.5678 | 398.0085 | 427.5488 | 416.4134 | 410.1311 | 388.9587 | 333.7704
2876.6264 | 2729.6264 | 476.7526 | 390.6138 | 443.5503 | 398.0434 | 427.5752 | 416.4355 | 410.1573 | 388.9694 | 333.8131
2877.6278 | 2730.6278 | 476.9764 | 390.6581 | 443.5939 | 398.0273 | 427.5933 | 416.4451 | 410.1642 | 388.9773 | 333.8555
2878.6293 | 2731.6293 | 477.0706 | 390.6654 | 443.6572 | 398.0813 | 427.6327 | 416.3825 | 410.1534 | 389.0078 | 333.8601
2879.6307 | 2732.6307 | 477.0777 | 390.6804 | 443.6683 | 398.0841 | 427.64 | 416.3681 | 410.1463 | 389.038 | 333.8793
2880.6321 | 2733.6321 | 477.1911 | 390.7072 | 443.5714 | 398.0759 | 427.6469 | 416.4127 | 410.1288 | 389.0646 | 333.8932
2881.6336 | 2734.6336 | 477.317 | 390.6959 | 443.5802 | 398.1032 | 427.6876 | 416.387 | 410.1182 | 389.0829 | 333.9602
2882.635 | 2735.635 | 477.479 | 390.7563 | 443.574 | 398.1204 | 427.6925 | 416.3842 | 410.1254 | 389.1033 | 333.9278
2883.6365 | 2736.6365 | 477.5392 | 390.746 | 443.6481 | 398.1463 | 427.7048 | 416.4587 | 410.1392 | 389.1235 | 333.977
2884.6279 | 2737.6279 | 477.5068 | 390.7915 | 443.6038 | 398.1479 | 427.7093 | 416.4594 | 410.1517 | 389.1331 | 334.0329
2885.6293 | 2738.6293 | 477.3444 | 390.7827 | 443.5915 | 398.1556 | 427.7116 | 416.5414 | 410.1729 | 389.155 | 334.0514
2886.6308 | 2739.6308 | 477.3309 | 390.8133 | 443.6058 | 398.1677 | 427.7178 | 416.6223 | 410.2102 | 389.183 | 334.0677
2887.6322 | 2740.6322 | 477.4367 | 390.8639 | 443.6425 | 398.2013 | 427.7364 | 416.6035 | 410.2526 | 389.1901 | 334.1131
2888.6337 | 2741.6337 | 477.4881 | 390.8693 | 443.6939 | 398.2206 | 427.7511 | 416.5556 | 410.2691 | 389.2312 | 334.1305
2889.6251 | 2742.6251 | 477.4031 | 390.9069 | 443.6166 | 398.1831 | 427.773 | 416.5581 | 410.2933 | 389.2261 | 334.2079
2890.6265 | 2743.6265 | 477.3654 | 390.8961 | 443.6147 | 398.2072 | 427.7989 | 416.6454 | 410.297 | 389.2619 | 334.2274
2891.628 | 2744.628 | 477.317 | 390.9112 | 443.5548 | 398.2152 | 427.8225 | 416.7093 | 410.3042 | 389.272 | 334.2549
2892.6294 | 2745.6294 | 477.4034 | 390.9338 | 443.6643 | 398.1802 | 427.8448 | 416.6462 | 410.3141 | 389.2894 | 334.3065
2893.6308 | 2746.6308 | 477.4218 | 390.9699 | 443.6826 | 398.2194 | 427.8692 | 416.6285 | 410.3366 | 389.3074 | 334.3048
2894.6323 | 2747.6323 | 477.4611 | 390.9784 | 443.6636 | 398.2153 | 427.8745 | 416.6796 | 410.3482 | 389.3272 | 334.3489
2895.6337 | 2748.6337 | 477.4611 | 390.9214 | 443.7196 | 398.2499 | 427.8874 | 416.8672 | 410.3683 | 389.3669 | 334.3499
2896.6352 | 2749.6352 | 477.4247 | 390.9818 | 443.7158 | 398.2704 | 427.9184 | 416.9338 | 410.4017 | 389.3746 | 334.4263
2897.6266 | 2750.6266 | 477.4456 | 390.9644 | 443.6823 | 398.2749 | 427.9363 | 417.0138 | 410.4192 | 389.3811 | 334.4644
2898.628 | 2751.628 | 477.3674 | 391.0014 | 443.7051 | 398.2628 | 427.9533 | 417.0245 | 410.4424 | 389.4054 | 334.483
2899.6295 | 2752.6295 | 477.2576 | 391.0085 | 443.7448 | 398.3134 | 427.9661 | 417.0709 | 410.447 | 389.4325 | 334.5028
2900.6309 | 2753.6309 | 477.3028 | 391.0516 | 443.791 | 398.3101 | 427.9896 | 417.0854 | 410.465 | 389.446 | 334.5748
2901.6323 | 2754.6323 | 477.1415 | 391.0658 | 443.7187 | 398.339 | 428.0066 | 417.0076 | 410.4703 | 389.4805 | 334.5648
2902.6338 | 2755.6338 | 477.0134 | 391.0638 | 443.7224 | 398.3209 | 428.0208 | 416.846 | 410.48 | 389.4995 | 334.5752
2903.6352 | 2756.6352 | 476.9432 | 391.1262 | 443.723 | 398.3525 | 428.0541 | 416.8365 | 410.4926 | 389.506 | 334.6436
2904.6367 | 2757.6367 | 476.9556 | 391.1428 | 443.7228 | 398.3786 | 428.0766 | 416.8681 | 410.5024 | 389.5159 | 334.6792
2905.6281 | 2758.6281 | 476.9802 | 391.1083 | 443.7092 | 398.3882 | 428.0851 | 416.9645 | 410.5059 | 389.5549 | 334.7081
2906.6295 | 2759.6295 | 477.0894 | 391.1663 | 443.6846 | 398.3828 | 428.0806 | 416.9625 | 410.5183 | 389.5622 | 334.6983
2907.631 | 2760.631 | 477.1641 | 391.1779 | 443.7276 | 398.3898 | 428.0648 | 416.9043 | 410.5406 | 389.5892 | 334.709
2908.6324 | 2761.6324 | 477.2125 | 391.1497 | 443.6721 | 398.3841 | 428.0472 | 416.909 | 410.5363 | 389.5675 | 334.7692
2909.6338 | 2762.6338 | 477.253 | 391.1819 | 443.7535 | 398.407 | 428.0266 | 416.9417 | 410.5364 | 389.597 | 334.8083
2910.6253 | 2763.6253 | 477.2472 | 391.2006 | 443.7901 | 398.4399 | 428.0049 | 417.0079 | 410.5415 | 389.6182 | 334.8226
2911.6267 | 2764.6267 | 477.4123 | 391.2509 | 443.807 | 398.4423 | 428.03 | 417.1033 | 410.5379 | 389.637 | 334.8742
2912.6282 | 2765.6282 | 477.4664 | 391.2612 | 443.8139 | 398.4406 | 428.0454 | 417.1634 | 410.5372 | 389.6508 | 334.9049
2913.6296 | 2766.6296 | 477.4231 | 391.292 | 443.7986 | 398.4496 | 428.0623 | 417.2567 | 410.5487 | 389.6714 | 334.899
2914.631 | 2767.631 | 477.3091 | 391.3065 | 443.7692 | 398.4673 | 428.0715 | 417.4086 | 410.5512 | 389.6856 | 334.9339
2915.6325 | 2768.6325 | 477.1968 | 391.3637 | 443.8438 | 398.5242 | 428.0992 | 417.4493 | 410.5563 | 389.7288 | 334.9713
2916.6339 | 2769.6339 | 477.2722 | 391.3383 | 443.746 | 398.4906 | 428.114 | 417.3646 | 410.5726 | 389.7596 | 335.0413
2917.6354 | 2770.6354 | 477.2966 | 391.3795 | 443.8145 | 398.4571 | 428.1277 | 417.3285 | 410.5974 | 389.8075 | 335.0399
2918.6268 | 2771.6268 | 477.2219 | 391.3788 | 443.8826 | 398.4396 | 428.131 | 417.3571 | 410.6255 | 389.8652 | 335.0985
2919.6282 | 2772.6282 | 477.1647 | 391.4323 | 443.8643 | 398.4473 | 428.1445 | 417.3501 | 410.6462 | 389.8826 | 335.0987
2920.6297 | 2773.6297 | 477.1625 | 391.4346 | 443.8385 | 398.4728 | 428.1348 | 417.3142 | 410.6625 | 390.0321 | 335.1233
2921.6311 | 2774.6311 | 477.1851 | 391.4818 | 443.8534 | 398.4792 | 428.1268 | 417.3432 | 410.6804 | 389.9696 | 335.1607
2922.6325 | 2775.6325 | 477.1518 | 391.4465 | 443.8494 | 398.5211 | 428.1397 | 417.375 | 410.6985 | 389.9356 | 335.1987
2923.634 | 2776.634 | 477.1953 | 391.451 | 443.9408 | 398.5261 | 428.1755 | 417.3969 | 410.7247 | 389.942 | 335.2458
2924.6354 | 2777.6354 | 477.1199 | 391.5132 | 443.8527 | 398.5072 | 428.1743 | 417.4297 | 410.7521 | 389.9652 | 335.2145
2925.6268 | 2778.6268 | 477.0122 | 391.5373 | 443.8137 | 398.5216 | 428.189 | 417.5495 | 410.761 | 389.9834 | 335.2848
2926.6283 | 2779.6283 | 476.9331 | 391.5379 | 443.8375 | 398.5792 | 428.1881 | 417.5918 | 410.7716 | 390.0207 | 335.3124
2927.6297 | 2780.6297 | 476.906 | 391.5354 | 443.826 | 398.6103 | 428.2208 | 417.6284 | 410.7742 | 390.0277 | 335.3678
2928.6312 | 2781.6312 | 476.8791 | 391.5593 | 443.8009 | 398.6078 | 428.2021 | 417.6027 | 410.7829 | 390.0296 | 335.3738
2929.6326 | 2782.6326 | 476.8726 | 391.5593 | 443.7898 | 398.6363 | 428.2195 | 417.6041 | 410.7792 | 390.0533 | 335.4024
2930.634 | 2783.634 | 476.8344 | 391.5265 | 443.7612 | 398.594 | 428.1979 | 417.6559 | 410.785 | 390.0967 | 335.4421
2931.6255 | 2784.6255 | 476.8466 | 391.6062 | 443.7211 | 398.6422 | 428.1982 | 417.7783 | 410.7873 | 390.1024 | 335.4314
2932.6269 | 2785.6269 | 476.996 | 391.6026 | 443.8072 | 398.6601 | 428.2319 | 417.9663 | 410.7937 | 390.0904 | 335.4712
2933.6284 | 2786.6284 | 477.0331 | 391.609 | 443.8432 | 398.6611 | 428.2527 | 418.0632 | 410.8055 | 390.1584 | 335.5054
2934.6298 | 2787.6298 | 477.0232 | 391.6583 | 443.8404 | 398.685 | 428.2709 | 417.9404 | 410.8298 | 390.1968 | 335.5006
2935.6312 | 2788.6312 | 477.0385 | 391.6186 | 443.8715 | 398.6663 | 428.2748 | 417.6437 | 410.8594 | 390.1704 | 335.5582
2936.6327 | 2789.6327 | 476.8885 | 391.648 | 443.7994 | 398.6552 | 428.3162 | 417.5761 | 410.865 | 390.2041 | 335.5406
2937.6241 | 2790.6241 | 476.8465 | 391.6345 | 443.8058 | 398.6845 | 428.3199 | 417.5694 | 410.8728 | 390.2178 | 335.5845
2938.6356 | 2791.6356 | 476.8955 | 391.6988 | 443.8546 | 398.6938 | 428.3552 | 417.6594 | 410.8781 | 390.2128 | 335.606
2939.627 | 2792.627 | 476.9841 | 391.7191 | 443.8867 | 398.7471 | 428.3721 | 417.7867 | 410.8798 | 390.2112 | 335.6507
2940.6284 | 2793.6284 | 476.951 | 391.7208 | 443.8518 | 398.7303 | 428.3704 | 417.9547 | 410.9093 | 390.27 | 335.6839
2941.6299 | 2794.6299 | 476.9391 | 391.6941 | 443.9383 | 398.7486 | 428.3648 | 417.9454 | 410.9377 | 390.3077 | 335.7067
2942.6313 | 2795.6313 | 476.7893 | 391.7542 | 443.9426 | 398.7582 | 428.3741 | 417.9112 | 410.9454 | 390.3248 | 335.7419
2943.6327 | 2796.6327 | 476.7586 | 391.7153 | 443.9282 | 398.7627 | 428.3919 | 417.9194 | 410.95 | 390.3203 | 335.8019
2944.6342 | 2797.6342 | 476.8168 | 391.7701 | 443.8903 | 398.7947 | 428.335 | 417.8566 | 410.9561 | 390.3138 | 335.8004
2945.6356 | 2798.6356 | 476.624 | 391.744 | 443.8612 | 398.8032 | 428.3027 | 417.7659 | 410.9481 | 390.3121 | 335.8473
2946.6371 | 2799.6371 | 476.5989 | 391.7735 | 443.878 | 398.7988 | 428.2912 | 417.6732 | 410.9492 | 390.3073 | 335.8682
2947.6285 | 2800.6285 | 476.6398 | 391.8441 | 443.9205 | 398.8113 | 428.2827 | 417.6667 | 410.9438 | 390.367 | 335.8605
2948.6299 | 2801.6299 | 476.6524 | 391.8637 | 443.786 | 398.8308 | 428.263 | 417.7659 | 410.9579 | 390.3603 | 335.8781
2949.6314 | 2802.6314 | 476.6204 | 391.8298 | 443.7937 | 398.8478 | 428.2767 | 417.784 | 410.9735 | 390.3633 | 335.8889
2950.6328 | 2803.6328 | 476.5857 | 391.8969 | 443.8087 | 398.8206 | 428.3039 | 417.6997 | 410.9899 | 390.4119 | 335.9725
2951.6342 | 2804.6342 | 476.5271 | 391.8723 | 443.8047 | 398.8539 | 428.3046 | 417.6866 | 411.0172 | 390.4542 | 336.0141
2952.6257 | 2805.6257 | 476.4299 | 391.8528 | 443.8709 | 398.8712 | 428.3502 | 417.7794 | 411.0514 | 390.4625 | 336.0548
2953.6271 | 2806.6271 | 476.267 | 391.872 | 443.7785 | 398.8648 | 428.3837 | 417.9053 | 411.0625 | 390.4516 | 336.1184
2954.6285 | 2807.6285 | 476.0721 | 391.9069 | 443.8541 | 398.8613 | 428.4123 | 417.8535 | 411.0774 | 390.5135 | 336.1174
2955.63 | 2808.63 | 476.0437 | 391.8874 | 443.8233 | 398.8764 | 428.4173 | 417.7821 | 411.088 | 390.4949 | 336.1443
2956.6314 | 2809.6314 | 476.0699 | 391.8913 | 443.8377 | 398.857 | 428.4423 | 417.7353 | 411.0975 | 390.5072 | 336.2068
2957.6329 | 2810.6329 | 476.1992 | 391.9077 | 443.7156 | 398.8506 | 428.4166 | 417.755 | 411.1015 | 390.5266 | 336.2375
2958.6343 | 2811.6343 | 476.2043 | 391.9211 | 443.8145 | 398.8735 | 428.3621 | 417.6586 | 411.1054 | 390.5723 | 336.1899
2959.6357 | 2812.6357 | 476.2732 | 391.9071 | 443.7871 | 398.8983 | 428.3441 | 417.7686 | 411.1396 | 390.5784 | 336.2077
2960.6272 | 2813.6272 | 476.3292 | 391.9094 | 443.8256 | 398.9361 | 428.3604 | 417.7385 | 411.158 | 390.5891 | 336.2358
2961.6286 | 2814.6286 | 476.2371 | 391.9363 | 443.861 | 398.8493 | 428.3295 | 417.674 | 411.178 | 390.5879 | 336.2239
2962.6301 | 2815.6301 | 476.245 | 391.9521 | 443.9095 | 398.7373 | 428.287 | 417.776 | 411.2041 | 390.5704 | 336.2886
2963.6315 | 2816.6315 | 476.2408 | 391.9655 | 443.8849 | 398.805 | 428.2929 | 417.7754 | 411.1798 | 390.6117 | 336.2839
2964.6329 | 2817.6329 | 476.213 | 391.9964 | 443.8742 | 398.8243 | 428.3083 | 417.8034 | 411.1608 | 390.6541 | 336.3442
2965.6344 | 2818.6344 | 476.0754 | 392.0094 | 443.7643 | 398.8216 | 428.3186 | 417.8388 | 411.1515 | 390.6328 | 336.3798
2966.6358 | 2819.6358 | 476.1445 | 391.9906 | 443.8287 | 398.9015 | 428.3561 | 417.9308 | 411.1369 | 390.6784 | 336.3751
2967.6272 | 2820.6272 | 476.2131 | 392.0305 | 443.7562 | 398.9297 | 428.4003 | 417.961 | 411.1299 | 390.698 | 336.3972
2968.6287 | 2821.6287 | 476.2573 | 392.0389 | 443.8665 | 398.9353 | 428.4529 | 417.8899 | 411.1341 | 390.7398 | 336.4404
2969.6301 | 2822.6301 | 476.3925 | 392.0489 | 443.8037 | 398.9377 | 428.4674 | 417.8544 | 411.1514 | 390.7451 | 336.4362
2970.6316 | 2823.6316 | 476.527 | 392.0678 | 443.7294 | 398.9583 | 428.4839 | 417.9431 | 411.156 | 390.7484 | 336.4716
2971.633 | 2824.633 | 476.6621 | 392.1111 | 443.7824 | 398.9761 | 428.4845 | 417.9783 | 411.1818 | 390.7928 | 336.5001
2972.6344 | 2825.6344 | 476.8145 | 392.091 | 443.8763 | 399.0059 | 428.4807 | 417.9403 | 411.2191 | 390.7773 | 336.5208
2973.6259 | 2826.6259 | 476.9912 | 392.1035 | 443.8078 | 398.9908 | 428.5145 | 417.9543 | 411.248 | 390.8063 | 336.5284
2974.6273 | 2827.6273 | 477.0332 | 392.1408 | 443.8062 | 399.0294 | 428.5457 | 418.0275 | 411.2709 | 390.8259 | 336.5649
2975.6287 | 2828.6287 | 477.0644 | 392.1219 | 443.8295 | 399.0328 | 428.5798 | 418.0743 | 411.2864 | 390.8706 | 336.6261
2976.6302 | 2829.6302 | 477.0984 | 392.1213 | 443.8799 | 399.0238 | 428.5925 | 418.0399 | 411.3072 | 390.8822 | 336.6388
2977.6316 | 2830.6316 | 477.1844 | 392.1474 | 443.9175 | 399.0281 | 428.6272 | 418.0503 | 411.3362 | 390.8841 | 336.6803
2978.6331 | 2831.6331 | 477.1921 | 392.1794 | 443.914 | 399.054 | 428.6892 | 418.034 | 411.3859 | 390.8858 | 336.7007
2979.6245 | 2832.6245 | 477.3025 | 392.1745 | 443.9343 | 399.0692 | 428.716 | 418.057 | 411.4096 | 390.887 | 336.7523
2980.6259 | 2833.6259 | 477.3862 | 392.1937 | 443.9352 | 399.0846 | 428.7601 | 418.1298 | 411.411 | 390.9121 | 336.7583
2981.6274 | 2834.6274 | 477.5541 | 392.1905 | 443.9778 | 399.0938 | 428.8127 | 418.2041 | 411.3988 | 390.932 | 336.8068
2982.6288 | 2835.6288 | 477.7422 | 392.1691 | 443.9658 | 399.0953 | 428.8378 | 418.1037 | 411.4104 | 390.9406 | 336.8
2983.6302 | 2836.6302 | 477.8839 | 392.2275 | 443.9761 | 399.1084 | 428.8686 | 418.0917 | 411.4237 | 390.9762 | 336.8361
2984.6317 | 2837.6317 | 477.9325 | 392.23 | 444.0209 | 399.1143 | 428.9051 | 418.1914 | 411.4404 | 391.0099 | 336.8364
2985.6331 | 2838.6331 | 477.8992 | 392.2546 | 443.9247 | 399.1518 | 428.9473 | 418.1172 | 411.4582 | 391.0185 | 336.8783
2986.6346 | 2839.6346 | 477.9714 | 392.2635 | 443.9393 | 399.1432 | 428.9741 | 418.0539 | 411.4925 | 391.0314 | 336.8897
2987.626 | 2840.626 | 477.977 | 392.2889 | 443.8169 | 399.1576 | 428.9875 | 418.1446 | 411.533 | 391.06 | 336.9003
2988.6274 | 2841.6274 | 477.9179 | 392.2499 | 443.9242 | 399.1464 | 428.9766 | 418.2407 | 411.5521 | 391.0671 | 336.9803
2989.6289 | 2842.6289 | 477.7786 | 392.2866 | 443.9245 | 399.1876 | 428.9558 | 418.248 | 411.5668 | 391.0668 | 336.9566
2990.6303 | 2843.6303 | 477.689 | 392.2751 | 443.9083 | 399.2088 | 428.9508 | 418.273 | 411.576 | 391.1081 | 336.9794
2991.6318 | 2844.6318 | 477.6133 | 392.3126 | 443.8477 | 399.1896 | 428.9564 | 418.3154 | 411.59 | 391.129 | 337.0063
2992.6332 | 2845.6332 | 477.6748 | 392.3283 | 443.8668 | 399.2093 | 428.972 | 418.4254 | 411.5776 | 391.1553 | 337.0502
2993.6346 | 2846.6346 | 477.6737 | 392.3752 | 443.8678 | 399.2377 | 428.9757 | 418.6354 | 411.5622 | 391.1458 | 337.0749
2994.6261 | 2847.6261 | 477.5731 | 392.3425 | 443.8476 | 399.2457 | 428.9987 | 418.7324 | 411.5388 | 391.1525 | 337.0154
2995.6275 | 2848.6275 | 477.5694 | 392.3773 | 443.9546 | 399.252 | 429.0333 | 418.6979 | 411.5286 | 391.1531 | 337.0558
2996.6289 | 2849.6289 | 477.511 | 392.3748 | 443.9746 | 399.2759 | 429.0529 | 418.7161 | 411.5002 | 391.1463 | 337.1028
2997.6304 | 2850.6304 | 477.4721 | 392.3453 | 444.0349 | 399.2794 | 429.0813 | 418.6675 | 411.4876 | 391.215 | 337.1211
2998.6318 | 2851.6318 | 477.3539 | 392.4108 | 443.9624 | 399.3062 | 429.0979 | 418.7021 | 411.5024 | 391.237 | 337.1443
2999.6333 | 2852.6333 | 477.1446 | 392.3738 | 444.0711 | 399.2828 | 429.1619 | 418.7879 | 411.5459 | 391.225 | 337.2094
3000.6347 | 2853.6347 | 477.1739 | 392.4636 | 444.1176 | 399.2882 | 429.1582 | 418.9111 | 411.6047 | 391.2799 | 337.2141
3001.6261 | 2854.6261 | 477.3078 | 392.4323 | 444.062 | 399.3013 | 429.1985 | 418.9541 | 411.6387 | 391.2654 | 337.2884
3002.6276 | 2855.6276 | 477.2172 | 392.4422 | 443.9887 | 399.3163 | 429.2146 | 418.9549 | 411.658 | 391.2804 | 337.3189
3003.629 | 2856.629 | 477.2706 | 392.3688 | 443.8911 | 399.2812 | 429.2498 | 418.891 | 411.671 | 391.2953 | 337.3245
3004.6304 | 2857.6304 | 477.3307 | 392.4082 | 443.8691 | 399.3202 | 429.2591 | 418.742 | 411.6727 | 391.3372 | 337.3112
3005.6319 | 2858.6319 | 477.2854 | 392.39 | 443.9483 | 399.3201 | 429.2972 | 418.6004 | 411.687 | 391.3493 | 337.3359
3006.6333 | 2859.6333 | 477.1825 | 392.4504 | 443.8885 | 399.3372 | 429.3471 | 418.6003 | 411.6976 | 391.3319 | 337.3917
3007.6348 | 2860.6348 | 477.0915 | 392.472 | 443.9142 | 399.3857 | 429.3702 | 418.7104 | 411.701 | 391.3862 | 337.419
3008.6262 | 2861.6262 | 476.9904 | 392.4882 | 443.9794 | 399.3603 | 429.3681 | 418.654 | 411.7064 | 391.3928 | 337.4552
3009.6276 | 2862.6276 | 477.0089 | 392.4991 | 443.9529 | 399.3706 | 429.3947 | 418.5369 | 411.7065 | 391.4193 | 337.4708
3010.6291 | 2863.6291 | 477.041 | 392.5148 | 443.9739 | 399.3699 | 429.4207 | 418.5079 | 411.7025 | 391.4311 | 337.4594
3011.6305 | 2864.6305 | 476.9286 | 392.5166 | 443.9999 | 399.3676 | 429.4044 | 418.4642 | 411.7191 | 391.4424 | 337.4922
3012.632 | 2865.632 | 476.8241 | 392.4917 | 443.9559 | 399.3837 | 429.4251 | 418.4151 | 411.714 | 391.4241 | 337.5682
3013.6334 | 2866.6334 | 476.6784 | 392.5058 | 443.9753 | 399.3508 | 429.4499 | 418.4275 | 411.7357 | 391.4493 | 337.5924
3014.6348 | 2867.6348 | 476.58 | 392.5257 | 443.9238 | 399.3571 | 429.4587 | 418.5672 | 411.7794 | 391.4936 | 337.6213
3015.6363 | 2868.6363 | 476.3842 | 392.5366 | 443.9132 | 399.3594 | 429.4598 | 418.619 | 411.7923 | 391.4898 | 337.5908
3016.6277 | 2869.6277 | 476.3507 | 392.5436 | 443.9113 | 399.3411 | 429.4934 | 418.7281 | 411.8032 | 391.5063 | 337.628
3017.6291 | 2870.6291 | 476.3581 | 392.565 | 443.9357 | 399.4045 | 429.5097 | 418.6604 | 411.8191 | 391.5492 | 337.6603
3018.6306 | 2871.6306 | 476.2572 | 392.5733 | 443.9978 | 399.3847 | 429.5177 | 418.6159 | 411.8244 | 391.5862 | 337.6431
3019.632 | 2872.632 | 476.2734 | 392.607 | 443.9771 | 399.3852 | 429.5415 | 418.6941 | 411.8007 | 391.5866 | 337.724
3020.6335 | 2873.6335 | 476.2564 | 392.5945 | 443.9875 | 399.4433 | 429.5755 | 418.8111 | 411.8372 | 391.593 | 337.7585
3021.6449 | 2874.6449 | 476.2879 | 392.6279 | 444.0159 | 399.4456 | 429.5893 | 418.8704 | 411.8989 | 391.6161 | 337.772
3022.6263 | 2875.6263 | 476.3597 | 392.671 | 444.0192 | 399.4686 | 429.6003 | 418.7989 | 411.9352 | 391.6315 | 337.7558
3023.6278 | 2876.6278 | 476.3727 | 392.6531 | 443.9674 | 399.4674 | 429.6263 | 418.848 | 411.9653 | 391.6214 | 337.8257
3024.6292 | 2877.6292 | 476.4653 | 392.6689 | 444.0166 | 399.4749 | 429.6396 | 418.9541 | 411.9737 | 391.678 | 337.8396
3025.6306 | 2878.6306 | 476.4483 | 392.7025 | 444.0005 | 399.4632 | 429.6583 | 418.9663 | 411.95 | 391.6973 | 337.8568
3026.6321 | 2879.6321 | 476.592 | 392.6701 | 443.9949 | 399.4946 | 429.6666 | 418.9739 | 411.9207 | 391.7022 | 337.912
3027.6335 | 2880.6335 | 476.612 | 392.6833 | 443.9577 | 399.5182 | 429.6834 | 419.1232 | 411.988 | 391.7042 | 337.9445
3028.6249 | 2881.6249 | 476.7331 | 392.7232 | 444.0015 | 399.5019 | 429.696 | 419.3816 | 412.0498 | 391.718 | 337.9465
3029.6264 | 2882.6264 | 476.8872 | 392.6073 | 443.9898 | 399.51 | 429.7074 | 419.2932 | 411.9528 | 391.7319 | 337.9788
3030.6278 | 2883.6278 | 477.0844 | 392.7077 | 444.0264 | 399.5157 | 429.7225 | 419.2295 | 411.9153 | 391.7353 | 337.9807
3031.6293 | 2884.6293 | 477.2101 | 392.6936 | 444.0467 | 399.5219 | 429.683 | 419.1208 | 411.9161 | 391.8037 | 337.9794
3032.6307 | 2885.6307 | 477.4016 | 392.7868 | 444.063 | 399.5206 | 429.663 | 419.0289 | 411.9369 | 391.7904 | 338.0449
3033.6321 | 2886.6321 | 477.4698 | 392.7866 | 443.9754 | 399.5396 | 429.677 | 419.0341 | 411.96 | 391.8032 | 338.068
3034.6336 | 2887.6336 | 477.4769 | 392.8006 | 443.9778 | 399.5644 | 429.6986 | 418.9701 | 411.9793 | 391.8273 | 338.1031
3035.635 | 2888.635 | 477.4739 | 392.8284 | 443.9982 | 399.5727 | 429.7162 | 418.8384 | 411.9867 | 391.8806 | 338.0916
3036.6365 | 2889.6365 | 477.3606 | 392.8269 | 443.9947 | 399.5683 | 429.7294 | 418.796 | 412.0191 | 391.8708 | 338.1184
3037.6279 | 2890.6279 | 477.152 | 392.8092 | 444.0115 | 399.5785 | 429.7541 | 418.8431 | 412.0407 | 391.8692 | 338.1174
3038.6293 | 2891.6293 | 477.0266 | 392.8455 | 443.9774 | 399.5826 | 429.7774 | 418.8526 | 412.066 | 391.9199 | 338.1211
3039.6308 | 2892.6308 | 476.9093 | 392.8567 | 444.0607 | 399.6284 | 429.7928 | 418.8295 | 412.0799 | 391.9015 | 338.1797
3040.6322 | 2893.6322 | 476.9653 | 392.9016 | 443.9763 | 399.5607 | 429.8183 | 418.8323 | 412.0789 | 391.8842 | 338.2265
3041.6337 | 2894.6337 | 477.0113 | 392.8625 | 443.8926 | 399.5187 | 429.8451 | 418.8792 | 412.0356 | 391.9202 | 338.2532
3042.6251 | 2895.6251 | 477.1376 | 392.9079 | 444.0635 | 399.6027 | 429.8642 | 418.8981 | 412.0196 | 391.9701 | 338.2383
3043.6265 | 2896.6265 | 477.2563 | 392.9592 | 444.1436 | 399.5938 | 429.888 | 419.0001 | 412.0337 | 391.9664 | 338.265
3044.628 | 2897.628 | 477.2488 | 392.9309 | 444.1425 | 399.5925 | 429.9582 | 419.0506 | 412.017 | 391.9816 | 338.3126
3045.6294 | 2898.6294 | 477.2766 | 392.9819 | 444.1336 | 399.6366 | 429.9573 | 419.0934 | 411.9727 | 391.9914 | 338.2995
3046.6308 | 2899.6308 | 477.4015 | 392.9765 | 444.206 | 399.6272 | 429.9789 | 419.2568 | 412.041 | 391.9921 | 338.3198
3047.6323 | 2900.6323 | 477.4115 | 392.9976 | 444.1544 | 399.651 | 429.9993 | 419.1449 | 412.0048 | 391.9958 | 338.36
3048.6337 | 2901.6337 | 477.3796 | 392.9682 | 444.1247 | 399.663 | 430.0296 | 419.1519 | 411.9956 | 392.03 | 338.4011
3049.6352 | 2902.6352 | 477.4202 | 393.0217 | 444.1113 | 399.6633 | 430.0536 | 419.2804 | 411.99 | 392.0197 | 338.4326
3050.6266 | 2903.6266 | 477.332 | 393.0532 | 444.0898 | 399.685 | 430.0548 | 419.396 | 412.0219 | 392.0751 | 338.4185
3051.628 | 2904.628 | 477.3968 | 393.0534 | 444.1957 | 399.6747 | 430.0739 | 419.3974 | 412.0517 | 392.0849 | 338.4813
3052.6295 | 2905.6295 | 477.444 | 393.0892 | 444.1096 | 399.6615 | 430.0624 | 419.3413 | 412.1033 | 392.1149 | 338.5298
3053.6309 | 2906.6309 | 477.4278 | 393.108 | 444.0713 | 399.7086 | 430.0274 | 419.1512 | 412.1456 | 392.1266 | 338.5329
3054.6323 | 2907.6323 | 477.4361 | 393.0955 | 444.1253 | 399.6972 | 430.0079 | 419.0725 | 412.1975 | 392.1377 | 338.5446
3055.6338 | 2908.6338 | 477.5059 | 393.1213 | 444.1523 | 399.6929 | 430.0221 | 419.1545 | 412.2695 | 392.1412 | 338.5866
3056.6352 | 2909.6352 | 477.4868 | 393.1661 | 444.1307 | 399.7325 | 430.0293 | 419.2057 | 412.3227 | 392.1708 | 338.5718
3057.6367 | 2910.6367 | 477.4132 | 393.1964 | 444.0907 | 399.7287 | 430.0514 | 419.1644 | 412.3604 | 392.1787 | 338.6424
3058.6281 | 2911.6281 | 477.3862 | 393.1942 | 444.0454 | 399.7816 | 430.0915 | 419.3023 | 412.3597 | 392.1858 | 338.6776
3059.6295 | 2912.6295 | 477.4113 | 393.2008 | 444.1135 | 399.7667 | 430.0958 | 419.3585 | 412.3589 | 392.2455 | 338.6614
3060.631 | 2913.631 | 477.3663 | 393.2338 | 444.1167 | 399.7704 | 430.0999 | 419.3995 | 412.3803 | 392.2338 | 338.7185
3061.6324 | 2914.6324 | 477.3955 | 393.2297 | 444.1137 | 399.7678 | 430.123 | 419.2951 | 412.3668 | 392.2392 | 338.728
3062.6339 | 2915.6339 | 477.3366 | 393.2177 | 444.1105 | 399.7875 | 430.1229 | 419.2956 | 412.3252 | 392.2441 | 338.7517
3063.6253 | 2916.6253 | 477.215 | 393.2671 | 444.0792 | 399.8113 | 430.1282 | 419.2954 | 412.2629 | 392.2664 | 338.7773
3064.6267 | 2917.6267 | 477.1227 | 393.2582 | 444.0164 | 399.7931 | 430.1146 | 419.3032 | 412.2357 | 392.2645 | 338.8162
3065.6282 | 2918.6282 | 476.9668 | 393.2579 | 444.0975 | 399.8055 | 430.1196 | 419.3994 | 412.2285 | 392.2925 | 338.8312
3066.6296 | 2919.6296 | 476.7808 | 393.2773 | 444.0658 | 399.8071 | 430.1101 | 419.4068 | 412.2323 | 392.2995 | 338.8269
3067.631 | 2920.631 | 476.7292 | 393.3068 | 444.0665 | 399.8415 | 430.0777 | 419.5508 | 412.2249 | 392.331 | 338.8892
3068.6325 | 2921.6325 | 476.713 | 393.299 | 443.9506 | 399.8736 | 430.0789 | 419.7061 | 412.245 | 392.3519 | 338.9173
3069.6339 | 2922.6339 | 476.5467 | 393.3313 | 443.9922 | 399.8811 | 430.0821 | 419.7453 | 412.2696 | 392.3894 | 338.9358
3070.6354 | 2923.6354 | 476.4283 | 393.3768 | 444.0918 | 399.8907 | 430.0986 | 419.7046 | 412.2555 | 392.3845 | 338.9766
3071.6368 | 2924.6368 | 476.483 | 393.3877 | 444.0807 | 399.9135 | 430.0826 | 419.6521 | 412.2802 | 392.4076 | 338.996
3072.6282 | 2925.6282 | 476.4928 | 393.3717 | 444.1125 | 399.8912 | 430.1382 | 419.6798 | 412.3432 | 392.4359 | 339.0396
3073.6297 | 2926.6297 | 476.5794 | 393.3787 | 444.0968 | 399.9 | 430.1503 | 419.8693 | 412.3926 | 392.4273 | 339.0576
3074.6311 | 2927.6311 | 476.4224 | 393.397 | 444.1458 | 399.8839 | 430.1612 | 419.9443 | 412.4522 | 392.4404 | 339.0517
3075.6325 | 2928.6325 | 476.3533 | 393.4614 | 444.1062 | 399.8721 | 430.1793 | 419.9728 | 412.4979 | 392.4741 | 339.0272
3076.634 | 2929.634 | 476.3398 | 393.4571 | 444.1111 | 399.9174 | 430.2086 | 419.7965 | 412.513 | 392.4969 | 339.0795
3077.6354 | 2930.6354 | 476.4824 | 393.4461 | 444.0867 | 399.9608 | 430.2152 | 419.7101 | 412.5 | 392.5081 | 339.0723
3078.6369 | 2931.6369 | 476.5458 | 393.4789 | 444.1129 | 399.9135 | 430.1994 | 419.724 | 412.4614 | 392.5067 | 339.1121
3079.6283 | 2932.6283 | 476.6417 | 393.4556 | 444.1103 | 399.9647 | 430.1801 | 419.9232 | 412.4258 | 392.5002 | 339.1707
3080.6297 | 2933.6297 | 476.8133 | 393.4927 | 444.0775 | 399.9455 | 430.1491 | 419.9838 | 412.4105 | 392.5074 | 339.1726
3081.6312 | 2934.6312 | 476.7522 | 393.5664 | 444.154 | 399.9487 | 430.1352 | 419.7771 | 412.3635 | 392.553 | 339.1483
3082.6326 | 2935.6326 | 476.7862 | 393.5553 | 444.204 | 399.9694 | 430.1234 | 419.795 | 412.3026 | 392.5662 | 339.1684
3083.634 | 2936.634 | 476.9183 | 393.5866 | 444.2317 | 399.9215 | 430.1504 | 419.7682 | 412.2772 | 392.5545 | 339.215
3084.6355 | 2937.6355 | 477.0059 | 393.6001 | 444.1665 | 399.9296 | 430.1398 | 419.6607 | 412.2988 | 392.599 | 339.2455
3085.6269 | 2938.6269 | 477.0371 | 393.6082 | 444.1345 | 399.975 | 430.1537 | 419.539 | 412.318 | 392.6419 | 339.2482
3086.6284 | 2939.6284 | 477.0865 | 393.6497 | 444.0903 | 399.9604 | 430.1675 | 419.5544 | 412.3654 | 392.6257 | 339.3155
3087.6298 | 2940.6298 | 477.1466 | 393.6163 | 444.1425 | 399.9613 | 430.1862 | 419.7002 | 412.4037 | 392.6341 | 339.3511
3088.6312 | 2941.6312 | 477.2894 | 393.6597 | 444.0876 | 399.9643 | 430.1986 | 419.8363 | 412.4491 | 392.6538 | 339.3735
3089.6327 | 2942.6327 | 477.2708 | 393.6802 | 444.023 | 399.9766 | 430.2401 | 419.8267 | 412.4929 | 392.6688 | 339.3626
3090.6341 | 2943.6341 | 477.2661 | 393.6785 | 444.1517 | 399.9136 | 430.2519 | 420.0361 | 412.5307 | 392.6628 | 339.3764
3091.6356 | 2944.6356 | 477.223 | 393.7127 | 444.1491 | 399.9487 | 430.2675 | 420.0985 | 412.6142 | 392.7025 | 339.3548
3092.627 | 2945.627 | 477.2235 | 393.734 | 444.0981 | 399.9924 | 430.2972 | 420.0499 | 412.6558 | 392.7012 | 339.4238
3093.6284 | 2946.6284 | 477.2523 | 393.7815 | 444.1298 | 399.9759 | 430.332 | 419.9019 | 412.6578 | 392.7168 | 339.4517
3094.6299 | 2947.6299 | 477.2825 | 393.8133 | 444.1339 | 400.0072 | 430.3778 | 419.8477 | 412.6775 | 392.704 | 339.508
3095.6313 | 2948.6313 | 477.2819 | 393.79 | 444.1969 | 399.9728 | 430.3727 | 419.6612 | 412.6633 | 392.721 | 339.5194
3096.6327 | 2949.6327 | 477.3877 | 393.7916 | 444.2372 | 399.9548 | 430.3723 | 419.6223 | 412.6494 | 392.738 | 339.5099
3097.6342 | 2950.6342 | 477.5227 | 393.7852 | 444.1452 | 399.9961 | 430.3826 | 419.7117 | 412.6392 | 392.7377 | 339.5467
3098.6356 | 2951.6356 | 477.5734 | 393.8358 | 444.0224 | 400.0144 | 430.4009 | 419.9337 | 412.6563 | 392.7813 | 339.5574
3099.627 | 2952.627 | 477.5662 | 393.883 | 443.9989 | 400.0717 | 430.4217 | 419.9859 | 412.6431 | 392.7814 | 339.5657
3100.6285 | 2953.6285 | 477.553 | 393.8557 | 444.1384 | 400.0926 | 430.4322 | 420.0946 | 412.5796 | 392.7707 | 339.6075
3101.6299 | 2954.6299 | 477.5977 | 393.9017 | 444.1643 | 400.0754 | 430.4455 | 420.2858 | 412.5562 | 392.8227 | 339.6203
3102.6314 | 2955.6314 | 477.6352 | 393.886 | 444.1103 | 400.0899 | 430.4516 | 420.1191 | 412.5557 | 392.8575 | 339.6438
3103.6328 | 2956.6328 | 477.6349 | 393.8374 | 444.1112 | 400.1199 | 430.4709 | 419.9637 | 412.5909 | 392.8512 | 339.7245
3104.6342 | 2957.6342 | 477.6579 | 393.8438 | 444.1897 | 400.1315 | 430.4984 | 420.0059 | 412.6115 | 392.8734 | 339.7419
3105.6257 | 2958.6257 | 477.725 | 394.0332 | 444.1115 | 400.1795 | 430.3693 | 419.8485 | 412.6253 | 392.9207 | 339.6574
3106.6271 | 2959.6271 | 477.6614 | 394.0005 | 444.168 | 400.1482 | 430.3692 | 419.9337 | 412.636 | 392.931 | 339.6805
3107.6286 | 2960.6286 | 477.504 | 394.0047 | 444.1169 | 400.1822 | 430.4006 | 419.9742 | 412.6311 | 392.9144 | 339.7271
3108.63 | 2961.63 | 477.2466 | 394.0191 | 444.1591 | 400.2002 | 430.4199 | 420.0926 | 412.6688 | 392.9508 | 339.7987
3109.6314 | 2962.6314 | 476.9443 | 394.0279 | 444.0238 | 400.2043 | 430.439 | 420.1665 | 412.7179 | 392.9702 | 339.7615
3110.6329 | 2963.6329 | 476.4275 | 393.9997 | 443.963 | 400.1856 | 430.4618 | 420.0769 | 412.7437 | 392.9841 | 339.7722
3111.6343 | 2964.6343 | 475.7851 | 394.044 | 444.0385 | 400.1822 | 430.476 | 420.0413 | 412.7712 | 393.0006 | 339.7771
3112.6257 | 2965.6257 | 475.1289 | 394.0211 | 444.0964 | 400.19 | 430.4766 | 420.0674 | 412.7788 | 392.9697 | 339.8253
3113.6272 | 2966.6272 | 474.5637 | 394.0316 | 444.0648 | 400.1133 | 430.4996 | 420.0206 | 412.7958 | 392.9882 | 339.8587
3114.6286 | 2967.6286 | 473.9988 | 394.0095 | 443.9653 | 400.119 | 430.4999 | 420.0344 | 412.8148 | 393.0067 | 339.8562
3115.6301 | 2968.6301 | 473.3614 | 394.0051 | 444.0832 | 400.0889 | 430.4971 | 420.0756 | 412.8483 | 393.0506 | 339.8705
3116.6315 | 2969.6315 | 472.7738 | 394.0128 | 444.0632 | 400.1305 | 430.5041 | 420.2535 | 412.8693 | 393.0531 | 339.8778
3117.6329 | 2970.6329 | 472.1625 | 393.9527 | 443.9456 | 400.0867 | 430.4994 | 420.315 | 412.8685 | 393.0409 | 339.9513
3118.6344 | 2971.6344 | 471.4131 | 393.869 | 443.8851 | 400.067 | 430.4868 | 420.3055 | 412.806 | 393.0856 | 339.98
3119.6358 | 2972.6358 | 470.6775 | 393.9192 | 443.8647 | 400.0288 | 430.4936 | 420.2995 | 412.8139 | 393.1262 | 339.9868
3120.6272 | 2973.6272 | 470.039 | 393.9211 | 443.8436 | 400.0435 | 430.5111 | 420.3892 | 412.8493 | 393.111 | 340.0204
3121.6287 | 2974.6287 | 469.3013 | 393.9163 | 443.6431 | 399.9908 | 430.523 | 420.3898 | 412.8858 | 393.1128 | 340.0443
3122.6301 | 2975.6301 | 468.582 | 393.7986 | 443.6255 | 399.9957 | 430.5369 | 420.4616 | 412.9033 | 393.1819 | 340.0433
3123.6316 | 2976.6316 | 467.7422 | 393.8335 | 443.6027 | 399.9587 | 430.5435 | 420.4482 | 412.9501 | 393.1581 | 340.0726
3124.633 | 2977.633 | 466.8758 | 393.7868 | 443.6089 | 399.9363 | 430.543 | 420.3618 | 413.0201 | 393.1523 | 340.1146
3125.6344 | 2978.6344 | 465.9787 | 393.6685 | 443.61 | 399.9191 | 430.5557 | 420.3275 | 413.0765 | 393.1916 | 340.1533
3126.6259 | 2979.6259 | 465.1768 | 393.6833 | 443.4656 | 399.8737 | 430.5655 | 420.1609 | 413.1108 | 393.2401 | 340.1564
3127.6273 | 2980.6273 | 464.4483 | 393.698 | 443.5287 | 399.8285 | 430.583 | 420.0873 | 413.1401 | 393.22 | 340.2067
3128.6287 | 2981.6287 | 463.7522 | 393.638 | 443.4152 | 399.7695 | 430.5839 | 420.1694 | 413.1559 | 393.229 | 340.1948
3129.6302 | 2982.6302 | 462.9193 | 393.6624 | 443.3988 | 399.6989 | 430.5746 | 420.3523 | 413.182 | 393.2181 | 340.1982
3130.6316 | 2983.6316 | 462.1365 | 393.6142 | 443.2573 | 399.6172 | 430.5773 | 420.3716 | 413.2331 | 393.2268 | 340.2524
3131.6331 | 2984.6331 | 461.4376 | 393.591 | 443.0325 | 399.5803 | 430.5774 | 420.2629 | 413.2709 | 393.236 | 340.2706
3132.6345 | 2985.6345 | 460.5502 | 393.5342 | 442.9472 | 399.5536 | 430.5673 | 420.1999 | 413.3158 | 393.2898 | 340.2879
3133.6259 | 2986.6259 | 459.7388 | 393.5023 | 443.0068 | 399.5386 | 430.5805 | 420.1223 | 413.3612 | 393.2517 | 340.3104
3134.6274 | 2987.6274 | 459 | 393.456 | 442.9508 | 399.4556 | 430.5912 | 420.0722 | 413.3864 | 393.2865 | 340.3185
3135.6288 | 2988.6288 | 458.2238 | 393.4499 | 442.8503 | 399.4431 | 430.5894 | 420.0758 | 413.4087 | 393.3301 | 340.3745
3136.6303 | 2989.6303 | 457.4512 | 393.3538 | 442.7274 | 399.3638 | 430.5808 | 420.1238 | 413.4252 | 393.4038 | 340.3681
3137.6317 | 2990.6317 | 456.6079 | 393.3822 | 442.6651 | 399.3201 | 430.5821 | 420.1073 | 413.4519 | 393.3735 | 340.4002
3138.6331 | 2991.6331 | 455.685 | 393.2976 | 442.5735 | 399.2523 | 430.5895 | 420.2816 | 413.4576 | 393.3651 | 340.39
3139.6346 | 2992.6346 | 454.8828 | 393.2567 | 442.5274 | 399.2169 | 430.5921 | 420.263 | 413.4437 | 393.4102 | 340.4306
3140.626 | 2993.626 | 454.2254 | 393.2135 | 442.4395 | 399.1388 | 430.5877 | 420.2064 | 413.4292 | 393.3769 | 340.4406
3141.6274 | 2994.6274 | 453.4895 | 393.121 | 442.3832 | 399.0971 | 430.5842 | 420.0769 | 413.457 | 393.3885 | 340.4685
3142.6289 | 2995.6289 | 452.7225 | 393.0877 | 442.2575 | 399.0452 | 430.5807 | 419.9876 | 413.4497 | 393.4415 | 340.4809
3143.6303 | 2996.6303 | 451.9169 | 393.0253 | 442.1079 | 398.9571 | 430.581 | 420.0201 | 413.4495 | 393.4913 | 340.5193
3144.6318 | 2997.6318 | 451.1218 | 392.9873 | 441.931 | 398.8864 | 430.5975 | 420.1407 | 413.4471 | 393.4882 | 340.5154
3145.6332 | 2998.6332 | 450.4098 | 392.9238 | 441.8656 | 398.8812 | 430.5974 | 420.3141 | 413.4637 | 393.4567 | 340.574
3146.6346 | 2999.6346 | 449.661 | 392.8572 | 441.8249 | 398.8092 | 430.5859 | 420.3418 | 413.4675 | 393.4587 | 340.5844
3147.6261 | 3000.6261 | 448.8918 | 392.7915 | 441.6336 | 398.7314 | 430.5953 | 420.3358 | 413.4629 | 393.4455 | 340.6224
3148.6275 | 3001.6275 | 448.1912 | 392.7797 | 441.5225 | 398.6429 | 430.5617 | 420.3533 | 413.4333 | 393.4762 | 340.6182
3149.6289 | 3002.6289 | 447.4112 | 392.7051 | 441.4749 | 398.5487 | 430.5883 | 420.3955 | 413.434 | 393.5093 | 340.6534
3150.6304 | 3003.6304 | 446.6094 | 392.6005 | 441.4305 | 398.4946 | 430.5695 | 420.383 | 413.445 | 393.4988 | 340.6401
3151.6318 | 3004.6318 | 445.7588 | 392.536 | 441.302 | 398.4281 | 430.5511 | 420.3028 | 413.459 | 393.5343 | 340.6802
3152.6333 | 3005.6333 | 444.9349 | 392.482 | 441.1328 | 398.3452 | 430.5345 | 420.2127 | 413.4396 | 393.5406 | 340.7399
3153.6347 | 3006.6347 | 444.1989 | 392.3163 | 440.9794 | 398.2854 | 430.52 | 420.1543 | 413.4454 | 393.6105 | 340.6943
3154.6261 | 3007.6261 | 443.4561 | 392.2445 | 440.9003 | 398.1899 | 430.5114 | 420.1194 | 413.4447 | 393.5622 | 340.714
3155.6276 | 3008.6276 | 442.6469 | 392.1644 | 440.72 | 398.0943 | 430.4932 | 420.0605 | 413.4462 | 393.5753 | 340.742
3156.629 | 3009.629 | 441.84 | 392.1463 | 440.5793 | 398 | 430.4842 | 420.029 | 413.4505 | 393.6106 | 340.7642
3157.6304 | 3010.6304 | 441.0258 | 392.0714 | 440.49 | 397.9289 | 430.4677 | 419.905 | 413.4482 | 393.563 | 340.7882
3158.6319 | 3011.6319 | 440.1918 | 392.003 | 440.3639 | 397.8848 | 430.4363 | 419.9408 | 413.4325 | 393.627 | 340.7665
3159.6333 | 3012.6333 | 439.3759 | 391.9353 | 440.2643 | 397.736 | 430.4316 | 420.025 | 413.4323 | 393.6453 | 340.7866
3160.6348 | 3013.6348 | 438.5325 | 391.8336 | 440.0974 | 397.6628 | 430.3948 | 420.0605 | 413.4448 | 393.6915 | 340.8165
3161.6262 | 3014.6262 | 437.692 | 391.7642 | 440.0342 | 397.5989 | 430.3539 | 420.0833 | 413.4665 | 393.6388 | 340.868
3162.6276 | 3015.6276 | 436.8455 | 391.6716 | 439.8676 | 397.4869 | 430.3435 | 420.1537 | 413.472 | 393.6308 | 340.8725
3163.6291 | 3016.6291 | 436.0454 | 391.5878 | 439.7329 | 397.4667 | 430.311 | 420.1924 | 413.4859 | 393.6081 | 340.8711
3164.6305 | 3017.6305 | 435.1832 | 391.527 | 439.5941 | 397.3298 | 430.29 | 420.2026 | 413.4705 | 393.6058 | 340.8822
3165.632 | 3018.632 | 434.3487 | 391.4612 | 439.3777 | 397.166 | 430.2587 | 420.1359 | 413.4545 | 393.6657 | 340.8388
3166.6334 | 3019.6334 | 433.5034 | 391.3384 | 439.1314 | 397.0418 | 430.2278 | 420.1281 | 413.4311 | 393.6837 | 340.8567
3167.6348 | 3020.6348 | 432.7869 | 391.2613 | 439.0184 | 396.9557 | 430.2105 | 420.1203 | 413.4091 | 393.6254 | 340.9158
3168.6263 | 3021.6263 | 432.2115 | 391.189 | 438.9254 | 396.8741 | 430.2013 | 420.1307 | 413.3929 | 393.7195 | 340.9017
3169.6277 | 3022.6277 | 431.4758 | 391.0709 | 438.7382 | 396.7439 | 430.1767 | 420.0666 | 413.388 | 393.7286 | 340.9296
3170.6291 | 3023.6291 | 430.6565 | 390.9891 | 438.449 | 396.5936 | 430.1475 | 419.9926 | 413.3674 | 393.7516 | 340.9746
3171.6306 | 3024.6306 | 429.9001 | 390.876 | 438.3375 | 396.4543 | 430.1185 | 419.971 | 413.3922 | 393.7131 | 340.9538
3172.632 | 3025.632 | 429.1155 | 390.7735 | 438.3099 | 396.4105 | 430.0891 | 419.8908 | 413.4037 | 393.7204 | 340.9979
3173.6335 | 3026.6335 | 428.2961 | 390.706 | 438.1927 | 396.3452 | 430.075 | 419.7871 | 413.3998 | 393.7332 | 341.0058
3174.6349 | 3027.6349 | 427.547 | 390.5912 | 437.9582 | 396.246 | 430.0453 | 419.7317 | 413.3988 | 393.6755 | 341.0124
3175.6263 | 3028.6263 | 426.7864 | 390.5012 | 437.8229 | 396.0737 | 430.0285 | 419.7439 | 413.3754 | 393.7309 | 340.9625
3176.6278 | 3029.6278 | 425.967 | 390.3709 | 437.6593 | 395.9674 | 429.9936 | 419.8128 | 413.3477 | 393.7255 | 340.9784
3177.6292 | 3030.6292 | 425.1783 | 390.2953 | 437.4766 | 395.8482 | 429.9725 | 419.9228 | 413.3345 | 393.7292 | 341.0314
3178.6306 | 3031.6306 | 424.3535 | 390.1563 | 437.3344 | 395.7513 | 429.9427 | 419.9344 | 413.3316 | 393.6992 | 341.0173
3179.6321 | 3032.6321 | 423.5979 | 390.076 | 437.0698 | 395.6378 | 429.8976 | 419.9337 | 413.3231 | 393.6466 | 341.0486
3180.6335 | 3033.6335 | 422.8593 | 389.9457 | 436.917 | 395.5237 | 429.839 | 419.905 | 413.3151 | 393.6141 | 341.0394
3181.635 | 3034.635 | 422.0378 | 389.8411 | 436.8131 | 395.4085 | 429.7847 | 419.8577 | 413.3056 | 393.6177 | 341.0323
3182.6264 | 3035.6264 | 421.185 | 389.7786 | 436.6391 | 395.2744 | 429.757 | 419.7631 | 413.3153 | 393.6695 | 341.069
3183.6278 | 3036.6278 | 420.4144 | 389.6592 | 436.3985 | 395.1262 | 429.7141 | 419.7025 | 413.2932 | 393.6652 | 341.0503
3184.6293 | 3037.6293 | 419.7108 | 389.5781 | 436.2236 | 395.0254 | 429.6875 | 419.6908 | 413.2449 | 393.615 | 341.0624
3185.6307 | 3038.6307 | 419.0828 | 389.3812 | 436.0385 | 394.9622 | 429.6301 | 419.638 | 413.1941 | 393.688 | 341.0842
3186.6322 | 3039.6322 | 418.3832 | 389.3266 | 435.884 | 394.8995 | 429.5842 | 419.7585 | 413.1355 | 393.6963 | 341.0871
3187.6336 | 3040.6336 | 417.5822 | 389.2229 | 435.7086 | 394.7898 | 429.5451 | 419.6789 | 413.0931 | 393.6956 | 341.1263
3188.635 | 3041.635 | 416.8169 | 389.075 | 435.4882 | 394.6069 | 429.4971 | 419.605 | 413.0616 | 393.6935 | 341.1034
3189.6265 | 3042.6265 | 416.0795 | 389.0011 | 435.4532 | 394.4308 | 429.4582 | 419.5386 | 413.0488 | 393.8281 | 341.1349
3190.6279 | 3043.6279 | 415.3842 | 388.9238 | 435.0085 | 394.3225 | 429.4075 | 419.5133 | 413.0467 | 393.7973 | 341.0997
3191.6293 | 3044.6293 | 414.6441 | 388.7958 | 434.8893 | 394.101 | 429.3714 | 419.5334 | 413.0538 | 393.6823 | 341.1389
3192.6508 | 3045.6508 | 413.9902 | 388.6607 | 434.8137 | 393.979 | 429.3194 | 419.5782 | 413.0691 | 393.8424 | 341.1459
3193.6322 | 3046.6322 | 413.3506 | 388.5979 | 434.5289 | 393.8912 | 429.2863 | 419.5577 | 413.0558 | 393.843 | 341.1372
3194.6337 | 3047.6337 | 412.5542 | 388.4574 | 434.3817 | 393.7702 | 429.2353 | 419.5041 | 413.0554 | 393.801 | 341.1254
3195.6351 | 3048.6351 | 411.8119 | 388.3282 | 434.2471 | 393.6712 | 429.1852 | 419.4662 | 413.0575 | 393.7402 | 341.1168
3196.6265 | 3049.6265 | 411.2072 | 388.1861 | 434.0193 | 393.5427 | 429.1225 | 419.4653 | 413.0377 | 393.6544 | 341.1342
3197.628 | 3050.628 | 410.5293 | 388.1079 | 433.925 | 393.4274 | 429.0803 | 419.4508 | 413.0216 | 393.621 | 341.1202
3198.6294 | 3051.6294 | 409.8677 | 388.0011 | 433.6205 | 393.215 | 429.0196 | 419.4116 | 412.9813 | 393.5914 | 341.1528
3199.6308 | 3052.6308 | 409.2013 | 387.8345 | 433.497 | 393.0616 | 428.9683 | 419.3474 | 412.9474 | 393.7452 | 341.1507
3200.6323 | 3053.6323 | 408.4703 | 387.7341 | 433.2284 | 392.9291 | 428.9 | 419.2849 | 412.9139 | 393.6485 | 341.1647
3201.6337 | 3054.6337 | 407.7562 | 387.6416 | 433.1661 | 392.7875 | 428.8605 | 419.2836 | 412.8983 | 393.5984 | 341.1765
3202.6352 | 3055.6352 | 407.0757 | 387.4781 | 432.9336 | 392.6689 | 428.7989 | 419.2336 | 412.8748 | 393.6995 | 341.1575
3203.6266 | 3056.6266 | 406.4608 | 387.3377 | 432.8495 | 392.4888 | 428.7375 | 419.1984 | 412.8448 | 393.7637 | 341.1516
3204.628 | 3057.628 | 405.7566 | 387.2264 | 432.6632 | 392.3476 | 428.6885 | 419.1847 | 412.8191 | 393.6737 | 341.1806
3205.6295 | 3058.6295 | 405.0409 | 387.155 | 432.4752 | 392.2116 | 428.6268 | 419.1268 | 412.8051 | 393.5891 | 341.1926
3206.6309 | 3059.6309 | 404.3031 | 387.0181 | 432.1936 | 392.0894 | 428.5566 | 419.0448 | 412.7943 | 393.7026 | 341.1719
3207.6323 | 3060.6323 | 403.5708 | 386.7797 | 432.0294 | 391.9826 | 428.4966 | 419.016 | 412.7659 | 393.5742 | 341.2175
3208.6338 | 3061.6338 | 402.9195 | 386.7136 | 431.858 | 391.8509 | 428.4493 | 418.987 | 412.7407 | 393.5245 | 341.2189
3209.6352 | 3062.6352 | 402.3032 | 386.5555 | 431.699 | 391.6868 | 428.371 | 418.9795 | 412.7106 | 393.6197 | 341.1881
3210.6267 | 3063.6267 | 401.6192 | 386.3271 | 431.4467 | 391.5419 | 428.3108 | 418.9616 | 412.6814 | 393.6354 | 341.2137
3211.6281 | 3064.6281 | 400.8831 | 386.3092 | 431.0891 | 391.4146 | 428.2462 | 418.9699 | 412.6701 | 393.5801 | 341.1841
3212.6295 | 3065.6295 | 400.1657 | 386.1678 | 430.874 | 391.2961 | 428.1977 | 418.9524 | 412.6495 | 393.4918 | 341.2102
3213.631 | 3066.631 | 399.4357 | 386.0597 | 430.7686 | 391.0813 | 428.1144 | 418.8715 | 412.6084 | 393.3986 | 341.2021
3214.6324 | 3067.6324 | 398.7097 | 385.8853 | 430.5497 | 390.9711 | 428.0292 | 418.8242 | 412.5732 | 393.3618 | 341.1973
3215.6339 | 3068.6339 | 398.0182 | 385.8086 | 430.3662 | 390.8466 | 427.9747 | 418.7631 | 412.5385 | 393.334 | 341.2195
3216.6253 | 3069.6253 | 397.3537 | 385.672 | 430.203 | 390.6951 | 427.8941 | 418.7101 | 412.49 | 393.4524 | 341.1996
3217.6267 | 3070.6267 | 396.6387 | 385.5501 | 430.0387 | 390.5393 | 427.8342 | 418.6655 | 412.4423 | 393.3359 | 341.2389
3218.6382 | 3071.6382 | 395.9983 | 385.4561 | 429.7928 | 390.346 | 427.7656 | 418.6583 | 412.3947 | 393.3307 | 341.174
3219.6296 | 3072.6296 | 395.3384 | 385.2942 | 429.5664 | 390.207 | 427.6972 | 418.6402 | 412.3649 | 393.3752 | 341.1749
3220.631 | 3073.631 | 394.6425 | 385.1609 | 429.3424 | 390.0423 | 427.6258 | 418.6212 | 412.3082 | 393.4355 | 341.2023
3221.6325 | 3074.6325 | 394.0302 | 385.0766 | 429.1925 | 389.8666 | 427.5551 | 418.5725 | 412.2757 | 393.3271 | 341.1723
3222.6339 | 3075.6339 | 393.3277 | 384.9243 | 428.9847 | 389.7254 | 427.4721 | 418.489 | 412.2316 | 393.2585 | 341.1514
3223.6354 | 3076.6354 | 392.6539 | 384.7224 | 428.7323 | 389.6019 | 427.3976 | 418.4321 | 412.1816 | 393.3527 | 341.146
3224.6268 | 3077.6268 | 391.8866 | 384.6012 | 428.6173 | 389.4507 | 427.3247 | 418.4022 | 412.1325 | 393.2093 | 341.159
3225.6282 | 3078.6282 | 391.2475 | 384.4674 | 428.3041 | 389.3133 | 427.2552 | 418.335 | 412.0872 | 393.1747 | 341.1561
3226.6297 | 3079.6297 | 390.6003 | 384.3198 | 428.0151 | 389.1656 | 427.1739 | 418.357 | 412.0557 | 393.2049 | 341.1713
3227.6311 | 3080.6311 | 389.9607 | 384.1713 | 427.809 | 388.968 | 427.0981 | 418.3462 | 412.0179 | 393.2678 | 341.1478
3228.6325 | 3081.6325 | 389.2905 | 384.043 | 427.6856 | 388.7992 | 427.0051 | 418.2998 | 411.9948 | 393.1477 | 341.169
3229.634 | 3082.634 | 388.5309 | 383.8999 | 427.4036 | 388.6877 | 426.9133 | 418.2239 | 411.9604 | 393.0663 | 341.1207
3230.6354 | 3083.6354 | 387.8273 | 383.8066 | 427.1669 | 388.533 | 426.8519 | 418.1128 | 411.9157 | 392.9895 | 341.0854
3231.6269 | 3084.6269 | 387.1514 | 383.6341 | 427.0186 | 388.3817 | 426.7663 | 418.0275 | 411.8626 | 392.9344 | 341.1395
3232.6283 | 3085.6283 | 386.435 | 383.5203 | 426.7946 | 388.2308 | 426.6908 | 417.9867 | 411.8201 | 392.9305 | 341.1043
3233.6297 | 3086.6297 | 385.841 | 383.3523 | 426.4908 | 388.0271 | 426.6304 | 417.9474 | 411.772 | 392.9806 | 341.1058
3234.6312 | 3087.6312 | 385.3401 | 383.25 | 426.2155 | 387.8733 | 426.5239 | 417.8944 | 411.7151 | 392.8794 | 341.0652
3235.6326 | 3088.6326 | 384.8021 | 383.0695 | 425.9911 | 387.7122 | 426.4235 | 417.8497 | 411.6571 | 392.9303 | 341.046
3236.6341 | 3089.6341 | 384.2594 | 382.9189 | 425.7759 | 387.5724 | 426.3482 | 417.8016 | 411.5929 | 392.8833 | 341.0892
3237.6255 | 3090.6255 | 383.6357 | 382.7605 | 425.5618 | 387.3857 | 426.2532 | 417.7644 | 411.5349 | 392.9681 | 341.057
3238.6269 | 3091.6269 | 383.0608 | 382.6274 | 425.3739 | 387.1951 | 426.18 | 417.6926 | 411.4831 | 392.8314 | 341.0437
3239.6284 | 3092.6284 | 382.445 | 382.4493 | 425.121 | 387.0667 | 426.0858 | 417.6328 | 411.4353 | 392.7978 | 341.0603
3240.6298 | 3093.6298 | 381.8638 | 382.2821 | 424.8546 | 386.9225 | 426.0211 | 417.5766 | 411.3986 | 392.8219 | 341.0567
3241.6312 | 3094.6312 | 381.1468 | 382.1271 | 424.6311 | 386.7473 | 425.9229 | 417.5123 | 411.3478 | 392.6755 | 341.006
3242.6327 | 3095.6327 | 380.5463 | 381.974 | 424.4005 | 386.5726 | 425.8263 | 417.4719 | 411.298 | 392.6942 | 340.9783
3243.6341 | 3096.6341 | 379.9864 | 381.8809 | 424.2278 | 386.3541 | 425.7309 | 417.4185 | 411.2403 | 392.6772 | 340.9569
3244.6356 | 3097.6356 | 379.4277 | 381.686 | 424.1223 | 386.1272 | 425.6482 | 417.3544 | 411.1798 | 392.7131 | 340.9765
3245.627 | 3098.627 | 378.7518 | 381.5435 | 423.9382 | 385.9909 | 425.5526 | 417.3067 | 411.1092 | 392.587 | 340.9462
3246.6284 | 3099.6284 | 378.1342 | 381.4309 | 423.5552 | 385.7984 | 425.4594 | 417.267 | 411.0384 | 392.4987 | 340.9398
3247.6299 | 3100.6299 | 377.5418 | 381.2562 | 423.3512 | 385.5753 | 425.3746 | 417.1884 | 410.9809 | 392.4072 | 340.9522
3248.6313 | 3101.6313 | 376.9193 | 381.0583 | 423.1647 | 385.5168 | 425.2758 | 417.1323 | 410.9319 | 392.368 | 340.9031
3249.6327 | 3102.6327 | 376.3859 | 380.9353 | 422.9674 | 385.35 | 425.1907 | 417.0764 | 410.8789 | 392.3861 | 340.9546
3250.6342 | 3103.6342 | 375.7903 | 380.7697 | 422.6806 | 385.1789 | 425.0929 | 417.0154 | 410.8192 | 392.3633 | 340.9328
3251.6356 | 3104.6356 | 375.1741 | 380.6209 | 422.5194 | 385.016 | 424.9921 | 416.9546 | 410.727 | 392.2596 | 340.8953
3252.6371 | 3105.6371 | 374.5031 | 380.507 | 422.2506 | 384.8039 | 424.8856 | 416.9126 | 410.6512 | 392.3373 | 340.9002
3253.6285 | 3106.6285 | 373.8606 | 380.3244 | 421.9843 | 384.6556 | 424.7938 | 416.8485 | 410.5775 | 392.3419 | 340.8759
3254.6299 | 3107.6299 | 373.2182 | 380.1846 | 421.7698 | 384.4168 | 424.7081 | 416.7892 | 410.5197 | 392.3196 | 340.852
3255.6314 | 3108.6314 | 372.561 | 380.0165 | 421.6244 | 384.259 | 424.5875 | 416.7131 | 410.4458 | 392.1993 | 340.848
3256.6328 | 3109.6328 | 371.8408 | 379.8896 | 421.3237 | 384.0872 | 424.4867 | 416.6458 | 410.3824 | 392.2023 | 340.8387
3257.6342 | 3110.6342 | 371.1863 | 379.7308 | 421.0886 | 383.9067 | 424.3985 | 416.5748 | 410.3372 | 392.1489 | 340.7956
3258.6257 | 3111.6257 | 370.614 | 379.564 | 420.7888 | 383.7418 | 424.299 | 416.4982 | 410.288 | 392.0144 | 340.8064
3259.6271 | 3112.6271 | 370.0381 | 379.2709 | 420.5502 | 383.5813 | 424.1883 | 416.4565 | 410.2361 | 392.0592 | 340.7556
3260.6286 | 3113.6286 | 369.501 | 379.218 | 420.3424 | 383.426 | 424.0817 | 416.3828 | 410.1846 | 392.027 | 340.7195
3261.63 | 3114.63 | 368.9433 | 379.0049 | 420.1153 | 383.2284 | 423.9766 | 416.2865 | 410.1255 | 392.0186 | 340.6887
3262.6314 | 3115.6314 | 368.3749 | 378.9231 | 419.8234 | 383.0359 | 423.8662 | 416.1883 | 410.0579 | 391.883 | 340.6712
3263.6329 | 3116.6329 | 367.837 | 378.7579 | 419.6999 | 382.8806 | 423.7678 | 416.0966 | 410.0028 | 391.7599 | 340.6883
3264.6343 | 3117.6343 | 367.2785 | 378.6322 | 419.3634 | 382.6759 | 423.6405 | 416.0147 | 409.9231 | 391.6641 | 340.6435
3265.6257 | 3118.6257 | 366.719 | 378.3999 | 419.026 | 382.5244 | 423.54 | 415.9551 | 409.8501 | 391.6294 | 340.5926
3266.6272 | 3119.6272 | 366.1508 | 378.2725 | 418.827 | 382.331 | 423.4366 | 415.8926 | 409.776 | 391.7176 | 340.5722
3267.6286 | 3120.6286 | 365.5746 | 378.1407 | 418.5137 | 382.1716 | 423.3307 | 415.8387 | 409.6822 | 391.6083 | 340.5788
3268.6301 | 3121.6301 | 364.9158 | 377.9997 | 418.2983 | 382.0017 | 423.2128 | 415.7898 | 409.6113 | 391.4975 | 340.5317
3269.6315 | 3122.6315 | 364.2528 | 377.8482 | 418.06 | 381.8674 | 423.0968 | 415.7277 | 409.5334 | 391.6374 | 340.5257
3270.6329 | 3123.6329 | 363.7201 | 377.6581 | 417.8799 | 381.6701 | 422.9809 | 415.662 | 409.4582 | 391.5998 | 340.5146
3271.6344 | 3124.6344 | 363.2426 | 377.5191 | 417.6793 | 381.5164 | 422.8767 | 415.5924 | 409.3677 | 391.5389 | 340.4722
3272.6358 | 3125.6358 | 362.7978 | 377.3612 | 417.3109 | 381.3374 | 422.7685 | 415.5032 | 409.2837 | 391.3931 | 340.4502
3273.6272 | 3126.6272 | 362.2708 | 377.2082 | 416.9835 | 381.1245 | 422.6374 | 415.4172 | 409.2075 | 391.4301 | 340.4209
3274.6287 | 3127.6287 | 361.6968 | 377.0232 | 416.8478 | 380.944 | 422.5327 | 415.3357 | 409.143 | 391.2969 | 340.4178
3275.6301 | 3128.6301 | 361.1157 | 376.8563 | 416.6537 | 380.7674 | 422.4201 | 415.2385 | 409.0863 | 391.1656 | 340.3685
3276.6316 | 3129.6316 | 360.5938 | 376.7298 | 416.5094 | 380.5575 | 422.291 | 415.149 | 409.036 | 391.2292 | 340.3359
3277.633 | 3130.633 | 360.0823 | 376.5292 | 416.239 | 380.3957 | 422.1752 | 415.0781 | 408.9802 | 391.1895 | 340.2913
3278.6344 | 3131.6344 | 359.5397 | 376.3025 | 415.9691 | 380.2054 | 422.056 | 415.0043 | 408.9126 | 391.0996 | 340.2812
3279.6259 | 3132.6259 | 359.0078 | 376.1974 | 415.7322 | 380.0121 | 421.9453 | 414.9413 | 408.8509 | 390.9621 | 340.2578
3280.6273 | 3133.6273 | 358.3621 | 376.0089 | 415.4912 | 379.8384 | 421.8145 | 414.8727 | 408.7865 | 390.8436 | 340.2432
3281.6288 | 3134.6288 | 357.7429 | 375.8506 | 415.2684 | 379.6847 | 421.6955 | 414.7879 | 408.7174 | 390.7555 | 340.2302
3282.6302 | 3135.6302 | 357.24 | 375.6627 | 415.0257 | 379.4898 | 421.5743 | 414.6706 | 408.6384 | 390.6912 | 340.2276
3283.6316 | 3136.6316 | 356.699 | 375.5662 | 414.8114 | 379.3069 | 421.439 | 414.5713 | 408.5563 | 390.7865 | 340.1919
3284.6331 | 3137.6331 | 356.1417 | 375.3786 | 414.585 | 379.0772 | 421.3303 | 414.475 | 408.4791 | 390.6392 | 340.1317
3285.6345 | 3138.6345 | 355.6247 | 375.1725 | 414.2387 | 378.8847 | 421.2019 | 414.3862 | 408.4042 | 390.5487 | 340.1249
3286.6259 | 3139.6259 | 355.0545 | 374.9434 | 414.0019 | 378.6915 | 421.0774 | 414.3068 | 408.3207 | 390.6928 | 340.0941
3287.6274 | 3140.6274 | 354.5044 | 374.8719 | 413.7459 | 378.5012 | 420.9535 | 414.2338 | 408.2456 | 390.7216 | 340.0729
3288.6288 | 3141.6288 | 353.9634 | 374.6565 | 413.5354 | 378.3916 | 420.8252 | 414.1829 | 408.1628 | 390.5481 | 340.0841
3289.6303 | 3142.6303 | 353.4045 | 374.4483 | 413.3297 | 378.1215 | 420.707 | 414.116 | 408.0836 | 390.4223 | 340.013
3290.6317 | 3143.6317 | 352.924 | 374.3361 | 413 | 377.9659 | 420.5683 | 414.0482 | 408.0088 | 390.4964 | 340.0028
3291.6331 | 3144.6331 | 352.4573 | 374.1831 | 412.7545 | 377.7495 | 420.4439 | 413.9655 | 407.919 | 390.2902 | 339.9957
3292.6346 | 3145.6346 | 351.8757 | 374.006 | 412.5368 | 377.575 | 420.3048 | 413.8714 | 407.8409 | 390.1643 | 339.9374
3293.626 | 3146.626 | 351.3203 | 373.7748 | 412.2302 | 377.376 | 420.1746 | 413.7765 | 407.7542 | 390.2038 | 339.8916
3294.6274 | 3147.6274 | 350.841 | 373.6621 | 411.9405 | 377.2093 | 420.0498 | 413.6567 | 407.6804 | 390.1864 | 339.8387
3295.6289 | 3148.6289 | 350.2975 | 373.4716 | 411.7446 | 377.0336 | 419.9181 | 413.5885 | 407.5924 | 390.0523 | 339.8137
3296.6303 | 3149.6303 | 349.7669 | 373.331 | 411.5159 | 376.7983 | 419.8086 | 413.5262 | 407.4912 | 389.8988 | 339.8248
3297.6318 | 3150.6318 | 349.1808 | 373.1464 | 411.1884 | 376.6352 | 419.6712 | 413.42 | 407.4131 | 389.7848 | 339.7666
3298.6332 | 3151.6332 | 348.5248 | 372.9891 | 411.0372 | 376.4482 | 419.5254 | 413.3004 | 407.339 | 389.6969 | 339.7378
3299.6346 | 3152.6346 | 347.9616 | 372.8083 | 410.7383 | 376.2727 | 419.4027 | 413.1886 | 407.2687 | 389.6336 | 339.6926
3300.6261 | 3153.6261 | 347.4521 | 372.6775 | 410.5328 | 376.0457 | 419.2517 | 413.0796 | 407.1896 | 389.7541 | 339.6687
3301.6275 | 3154.6275 | 346.9125 | 372.4666 | 410.2673 | 375.907 | 419.1301 | 412.9938 | 407.114 | 389.5639 | 339.641
3302.6289 | 3155.6289 | 346.3841 | 372.3458 | 410.1317 | 375.718 | 419.0046 | 412.9218 | 407.0425 | 389.4982 | 339.5801
3303.6304 | 3156.6304 | 345.8548 | 372.1597 | 409.7498 | 375.5176 | 418.8606 | 412.8365 | 406.9589 | 389.5602 | 339.529
3304.6318 | 3157.6318 | 345.4071 | 371.9739 | 409.5145 | 375.2588 | 418.7264 | 412.7558 | 406.8844 | 389.662 | 339.5299
3305.6333 | 3158.6333 | 344.9464 | 371.8133 | 409.2862 | 375.103 | 418.5856 | 412.6537 | 406.7888 | 389.4352 | 339.4805
3306.6347 | 3159.6347 | 344.389 | 371.639 | 409.0136 | 374.9314 | 418.4394 | 412.5171 | 406.6969 | 389.2797 | 339.4591
3307.6261 | 3160.6261 | 343.8023 | 371.468 | 408.7152 | 374.762 | 418.3101 | 412.4028 | 406.6064 | 389.334 | 339.4284
3308.6276 | 3161.6276 | 343.2294 | 371.2957 | 408.5241 | 374.5655 | 418.1666 | 412.32 | 406.5202 | 389.1181 | 339.3572
3309.629 | 3162.629 | 342.6304 | 371.0515 | 408.2683 | 374.3803 | 418.0375 | 412.2305 | 406.4267 | 389.0396 | 339.323
3310.6305 | 3163.6305 | 342.1035 | 370.9601 | 407.986 | 374.1709 | 417.8839 | 412.1327 | 406.3311 | 389.0379 | 339.2862
3311.6319 | 3164.6319 | 341.547 | 370.7998 | 407.7422 | 373.9026 | 417.7475 | 412.0417 | 406.2482 | 389.0503 | 339.2542
3312.6333 | 3165.6333 | 340.9778 | 370.6141 | 407.5089 | 373.7608 | 417.5961 | 411.9512 | 406.1637 | 388.8628 | 339.1869
3313.6348 | 3166.6348 | 340.4384 | 370.4183 | 407.2478 | 373.5752 | 417.4646 | 411.8471 | 406.0821 | 388.6925 | 339.166
3314.6262 | 3167.6262 | 339.9688 | 370.2655 | 406.9174 | 373.3856 | 417.3275 | 411.6826 | 406.0088 | 388.5677 | 339.1237
3315.6276 | 3168.6276 | 339.5405 | 370.0919 | 406.6938 | 373.1751 | 417.1817 | 411.5329 | 405.9245 | 388.4539 | 339.127
3316.6291 | 3169.6291 | 339.0662 | 369.9184 | 406.5034 | 372.988 | 417.0381 | 411.4415 | 405.8332 | 388.426 | 339.0833
3317.6305 | 3170.6305 | 338.5662 | 369.7067 | 406.2521 | 372.8128 | 416.9014 | 411.3193 | 405.7411 | 388.419 | 339.0344
3318.632 | 3171.632 | 338.1003 | 369.5098 | 406.0475 | 372.6039 | 416.7575 | 411.2227 | 405.6496 | 388.2508 | 338.9837
3319.6334 | 3172.6334 | 337.5984 | 369.3764 | 405.8251 | 372.3813 | 416.5947 | 411.1474 | 405.5693 | 388.2495 | 338.937
3320.6348 | 3173.6348 | 337.0829 | 369.2117 | 405.5662 | 372.211 | 416.4521 | 411.0462 | 405.47 | 388.1933 | 338.884
3321.6263 | 3174.6263 | 336.5965 | 369.022 | 405.2515 | 371.9948 | 416.3105 | 410.9518 | 405.3771 | 388.1845 | 338.8225
3322.6277 | 3175.6277 | 336.0917 | 368.8459 | 404.9273 | 371.7773 | 416.1703 | 410.8431 | 405.2891 | 388.0012 | 338.8041
3323.6291 | 3176.6291 | 335.5601 | 368.6845 | 404.7059 | 371.6314 | 416.0286 | 410.7127 | 405.1916 | 387.9096 | 338.7603
3324.6306 | 3177.6306 | 335.0587 | 368.4799 | 404.4528 | 371.4357 | 415.8661 | 410.6441 | 405.101 | 387.877 | 338.6867
3325.632 | 3178.632 | 334.5441 | 368.2604 | 404.186 | 371.2057 | 415.7047 | 410.5819 | 405.0019 | 387.6907 | 338.6752
3326.6335 | 3179.6335 | 334.0668 | 368.058 | 404.021 | 371.0272 | 415.5678 | 410.4787 | 404.9009 | 387.6521 | 338.628
3327.6349 | 3180.6349 | 333.5199 | 367.8745 | 403.6218 | 370.7776 | 415.4207 | 410.3888 | 404.7978 | 387.5855 | 338.5754
3328.6263 | 3181.6263 | 332.9808 | 367.6699 | 403.4002 | 370.5796 | 415.2634 | 410.2609 | 404.7086 | 387.5488 | 338.5376
3329.6278 | 3182.6278 | 332.4026 | 367.5195 | 403.1822 | 370.3973 | 415.1115 | 410.0725 | 404.6063 | 387.4071 | 338.5002
3330.6292 | 3183.6292 | 331.9771 | 367.3965 | 402.915 | 370.1912 | 414.9596 | 409.9333 | 404.5013 | 387.2679 | 338.4224
3331.6306 | 3184.6306 | 331.6282 | 367.2561 | 402.649 | 369.97 | 414.8073 | 409.8762 | 404.3969 | 387.1322 | 338.3815
3332.6321 | 3185.6321 | 331.2744 | 367.0854 | 402.362 | 369.7984 | 414.6652 | 409.7741 | 404.2877 | 387.047 | 338.3616
3333.6335 | 3186.6335 | 330.807 | 366.883 | 402.1508 | 369.5635 | 414.5063 | 409.641 | 404.178 | 387.0337 | 338.3224
3334.635 | 3187.635 | 330.3679 | 366.6488 | 401.9117 | 369.3797 | 414.3582 | 409.4923 | 404.0825 | 386.9578 | 338.2638
3335.6264 | 3188.6264 | 329.9451 | 366.5206 | 401.6814 | 369.1219 | 414.1945 | 409.3666 | 403.9668 | 386.8174 | 338.2129
3336.6278 | 3189.6278 | 329.4637 | 366.3953 | 401.4111 | 368.977 | 414.0432 | 409.1644 | 403.8568 | 386.8463 | 338.1517
3337.6293 | 3190.6293 | 328.9551 | 366.2275 | 401.0836 | 368.8213 | 413.8877 | 408.9953 | 403.7532 | 386.762 | 338.0871
3338.6307 | 3191.6307 | 328.4765 | 366.0443 | 400.8111 | 368.5902 | 413.7446 | 408.857 | 403.6438 | 386.6924 | 338.0671
3339.6322 | 3192.6322 | 328.0026 | 365.8981 | 400.5453 | 368.4143 | 413.5753 | 408.7499 | 403.5365 | 386.5233 | 338.0286
3340.6336 | 3193.6336 | 327.6611 | 365.6352 | 400.3915 | 368.2172 | 413.419 | 408.6353 | 403.4391 | 386.4944 | 338.0034
3341.635 | 3194.635 | 327.303 | 365.5205 | 400.0986 | 368.0157 | 413.2672 | 408.5051 | 403.3319 | 386.3807 | 337.9317
3342.6265 | 3195.6265 | 326.8592 | 365.3941 | 399.8939 | 367.8012 | 413.1004 | 408.3574 | 403.2234 | 386.2108 | 337.8997
3343.6279 | 3196.6279 | 326.2972 | 365.2172 | 399.6024 | 367.6302 | 412.9548 | 408.2719 | 403.1202 | 386.211 | 337.8247
3344.6293 | 3197.6293 | 325.7508 | 365.032 | 399.4004 | 367.4139 | 412.7888 | 408.1964 | 403.0226 | 386.1109 | 337.7952
3345.6308 | 3198.6308 | 325.3367 | 364.8284 | 399.069 | 367.2335 | 412.6469 | 408.1088 | 402.9195 | 386.0309 | 337.7739
3346.6322 | 3199.6322 | 324.8902 | 364.6619 | 398.7397 | 366.9848 | 412.4692 | 407.9904 | 402.8139 | 385.8851 | 337.711
3347.6337 | 3200.6337 | 324.4567 | 364.5159 | 398.4682 | 366.8173 | 412.3114 | 407.8708 | 402.7166 | 385.7306 | 337.676
3348.6351 | 3201.6351 | 324.094 | 364.3449 | 398.3028 | 366.512 | 412.1572 | 407.7377 | 402.6043 | 385.6049 | 337.6285
3349.6265 | 3202.6265 | 323.6835 | 364.1768 | 398.0351 | 366.3943 | 412.0005 | 407.6296 | 402.5043 | 385.5273 | 337.5464
3350.628 | 3203.628 | 323.2627 | 364.0295 | 397.8552 | 366.2297 | 411.8468 | 407.5275 | 402.41 | 385.5387 | 337.4873
3351.6294 | 3204.6294 | 322.7778 | 363.8491 | 397.6081 | 366.0243 | 411.6765 | 407.4442 | 402.3008 | 385.408 | 337.4628
3352.6308 | 3205.6308 | 322.3206 | 363.6592 | 397.278 | 365.8421 | 411.5123 | 407.3462 | 402.2001 | 385.2541 | 337.3983
3353.6323 | 3206.6323 | 321.9324 | 363.4864 | 397.0036 | 365.6371 | 411.3395 | 407.2078 | 402.0869 | 385.2805 | 337.2726
3354.6237 | 3207.6237 | 321.462 | 363.3203 | 396.8265 | 365.416 | 411.196 | 407.0615 | 401.973 | 385.2145 | 337.2194
3355.6352 | 3208.6352 | 321.0662 | 363.1522 | 396.5068 | 365.2254 | 411.0214 | 406.9403 | 401.8593 | 385.083 | 337.1996
3356.6266 | 3209.6266 | 320.6746 | 362.9439 | 396.3399 | 365.0128 | 410.8557 | 406.8381 | 401.7446 | 384.9231 | 337.1663
3357.628 | 3210.628 | 320.3664 | 362.7856 | 396.0323 | 364.8122 | 410.6953 | 406.7217 | 401.6344 | 384.8761 | 337.1219
3358.6295 | 3211.6295 | 319.9922 | 362.6151 | 395.8407 | 364.6549 | 410.5236 | 406.618 | 401.5067 | 384.7486 | 337.0555
3359.6309 | 3212.6309 | 319.4918 | 362.4396 | 395.5885 | 364.4292 | 410.3707 | 406.4714 | 401.3824 | 384.5889 | 337.0267
3360.6324 | 3213.6324 | 318.954 | 362.2809 | 395.371 | 364.2305 | 410.1982 | 406.3171 | 401.2596 | 384.5638 | 336.9891
3361.6338 | 3214.6338 | 318.5152 | 362.1135 | 395.1628 | 364.0288 | 410.0451 | 406.1303 | 401.1562 | 384.4914 | 336.9151
3362.6352 | 3215.6352 | 318.0746 | 361.9221 | 394.8325 | 363.7667 | 409.8698 | 405.9248 | 401.04 | 384.3605 | 336.9045
3363.6267 | 3216.6267 | 317.5683 | 361.7701 | 394.568 | 363.6254 | 409.708 | 405.7352 | 400.9218 | 384.2305 | 336.7919
3364.6281 | 3217.6281 | 317.1071 | 361.6171 | 394.3044 | 363.4637 | 409.5493 | 405.5856 | 400.8049 | 384.0748 | 336.7366
3365.6295 | 3218.6295 | 316.7216 | 361.4725 | 394.0561 | 363.2471 | 409.3821 | 405.4063 | 400.6693 | 383.9717 | 336.659
3366.631 | 3219.631 | 316.3141 | 361.2962 | 393.8168 | 363.0318 | 409.2048 | 405.279 | 400.5464 | 383.8481 | 336.6713
3367.6324 | 3220.6324 | 315.8827 | 361.1252 | 393.6181 | 362.8538 | 409.0382 | 405.1162 | 400.4185 | 383.8346 | 336.5707
3368.6339 | 3221.6339 | 315.4184 | 360.9316 | 393.3304 | 362.6489 | 408.8731 | 404.9591 | 400.28 | 383.687 | 336.5158
3369.6253 | 3222.6253 | 314.9994 | 360.7588 | 393.1031 | 362.4399 | 408.7097 | 404.889 | 400.1516 | 383.5449 | 336.5232
3370.6267 | 3223.6267 | 314.6214 | 360.5965 | 392.8116 | 362.2437 | 408.5381 | 404.7849 | 400.0318 | 383.546 | 336.4338
3371.6282 | 3224.6282 | 314.1968 | 360.4243 | 392.534 | 362.0212 | 408.3579 | 404.6747 | 399.9028 | 383.4775 | 336.3715
3372.6296 | 3225.6296 | 313.7293 | 360.1945 | 392.2874 | 361.8124 | 408.197 | 404.5013 | 399.7756 | 383.3189 | 336.3437
3373.6911 | 3226.6911 | 313.2572 | 360.0581 | 392.0706 | 361.608 | 408.0174 | 404.3627 | 399.6438 | 383.1579 | 336.2885
3374.6325 | 3227.6325 | 312.8191 | 359.8882 | 391.7717 | 361.4145 | 407.8593 | 404.2409 | 399.5228 | 383.1514 | 336.2129
3375.6339 | 3228.6339 | 312.3445 | 359.7214 | 391.5648 | 361.2239 | 407.6869 | 404.1132 | 399.3919 | 382.9822 | 336.1819
3376.6354 | 3229.6354 | 311.9529 | 359.53 | 391.2652 | 361.0127 | 407.5088 | 403.9981 | 399.2606 | 382.8506 | 336.1232
3377.6268 | 3230.6268 | 311.5386 | 359.3638 | 391.076 | 360.8161 | 407.3549 | 403.8922 | 399.1359 | 382.7763 | 336.0761
3378.6282 | 3231.6282 | 311.0783 | 359.1683 | 390.8129 | 360.6478 | 407.1736 | 403.765 | 399.0138 | 382.716 | 336.0028
3379.6297 | 3232.6297 | 310.571 | 358.991 | 390.5363 | 360.4332 | 407.0021 | 403.6284 | 398.8863 | 382.5676 | 335.9464
3380.6311 | 3233.6311 | 310.1458 | 358.851 | 390.2593 | 360.2244 | 406.8384 | 403.4733 | 398.7752 | 382.4273 | 335.9162
3381.6325 | 3234.6325 | 309.7988 | 358.6607 | 390.1359 | 360.0101 | 406.6507 | 403.2474 | 398.6542 | 382.2888 | 335.8392
3382.634 | 3235.634 | 309.3467 | 358.4796 | 389.8223 | 359.8152 | 406.4703 | 403.1159 | 398.5439 | 382.1553 | 335.7837
3383.6354 | 3236.6354 | 308.9602 | 358.3154 | 389.6173 | 359.6246 | 406.3066 | 402.9993 | 398.4226 | 382.0442 | 335.7333
3384.6269 | 3237.6269 | 308.6252 | 358.1437 | 389.2222 | 359.431 | 406.1345 | 402.8621 | 398.303 | 382.0021 | 335.6778
3385.6283 | 3238.6283 | 308.3334 | 357.9622 | 388.9912 | 359.2088 | 405.9598 | 402.6854 | 398.1727 | 381.8461 | 335.6154
3386.6297 | 3239.6297 | 308.0262 | 357.7878 | 388.7357 | 359.0109 | 405.78 | 402.5263 | 398.0542 | 381.7659 | 335.5597
3387.6312 | 3240.6312 | 307.6645 | 357.5811 | 388.6024 | 358.7869 | 405.6114 | 402.3809 | 397.9324 | 381.7083 | 335.5066
3388.6326 | 3241.6326 | 307.3115 | 357.416 | 388.3044 | 358.5845 | 405.4281 | 402.2716 | 397.828 | 381.6621 | 335.4516
3389.6341 | 3242.6341 | 306.9015 | 357.2198 | 388.0958 | 358.3661 | 405.2565 | 402.1405 | 397.7101 | 381.5057 | 335.3831
3390.6255 | 3243.6255 | 306.5093 | 357.0663 | 387.8619 | 358.1449 | 405.0662 | 402.024 | 397.5942 | 381.3499 | 335.3437
3391.6269 | 3244.6269 | 306.1023 | 356.9022 | 387.5674 | 357.8964 | 404.9071 | 401.8027 | 397.4537 | 381.34 | 335.2513
3392.6284 | 3245.6284 | 305.6557 | 356.7345 | 387.2807 | 357.7186 | 404.7173 | 401.6625 | 397.3131 | 381.16 | 335.1709
3393.6298 | 3246.6298 | 305.2284 | 356.5854 | 387.0578 | 357.4795 | 404.5368 | 401.497 | 397.1736 | 380.9947 | 335.1001
3394.6312 | 3247.6312 | 304.8564 | 356.3306 | 386.8276 | 357.3447 | 404.3723 | 401.3648 | 397.038 | 380.8802 | 335.0014
3395.6327 | 3248.6327 | 304.4143 | 356.0985 | 386.4546 | 357.1181 | 404.187 | 401.2241 | 396.8941 | 380.9573 | 334.9548
3396.6341 | 3249.6341 | 303.9666 | 355.9667 | 386.2209 | 356.9555 | 403.9972 | 401.0755 | 396.7644 | 380.7772 | 334.8891
3397.6356 | 3250.6356 | 303.5936 | 355.787 | 386.032 | 356.741 | 403.8222 | 400.9425 | 396.6202 | 380.6087 | 334.8649
3398.627 | 3251.627 | 303.1441 | 355.6518 | 385.785 | 356.5552 | 403.6473 | 400.8115 | 396.4749 | 380.4699 | 334.8158
3399.6284 | 3252.6284 | 302.6653 | 355.4179 | 385.4777 | 356.3465 | 403.4694 | 400.6455 | 396.328 | 380.3403 | 334.7939
3400.6299 | 3253.6299 | 302.2809 | 355.2113 | 385.2269 | 356.147 | 403.2842 | 400.4747 | 396.1923 | 380.2912 | 334.71
3401.6313 | 3254.6313 | 301.8665 | 355.0591 | 384.9822 | 355.9581 | 403.1279 | 400.3481 | 396.0483 | 380.2698 | 334.6296
3402.6327 | 3255.6327 | 301.4073 | 354.8663 | 384.775 | 355.7423 | 402.9326 | 400.1986 | 395.9077 | 380.0555 | 334.5891
3403.6342 | 3256.6342 | 300.9389 | 354.7253 | 384.523 | 355.5316 | 402.7515 | 400.0194 | 395.7724 | 380.0383 | 334.493
3404.6356 | 3257.6356 | 300.4359 | 354.5371 | 384.2521 | 355.3575 | 402.566 | 399.8376 | 395.6238 | 379.9054 | 334.4697
3405.6271 | 3258.6271 | 299.9869 | 354.3528 | 383.987 | 355.1561 | 402.3882 | 399.6037 | 395.4906 | 379.7316 | 334.4035
3406.6285 | 3259.6285 | 299.5909 | 354.1826 | 383.7065 | 354.9504 | 402.2122 | 399.3515 | 395.3431 | 379.5725 | 334.3366
3407.6299 | 3260.6299 | 299.1591 | 354.0067 | 383.4385 | 354.7378 | 402.0224 | 399.2486 | 395.21 | 379.4382 | 334.2612
3408.6314 | 3261.6314 | 298.6817 | 353.8457 | 383.3029 | 354.5208 | 401.8501 | 399.1467 | 395.064 | 379.2962 | 334.2145
3409.6328 | 3262.6328 | 298.3059 | 353.6918 | 383.046 | 354.3338 | 401.6591 | 398.9785 | 394.9141 | 379.1682 | 334.148
3410.6343 | 3263.6343 | 297.9471 | 353.4726 | 382.7878 | 354.0955 | 401.4855 | 398.8392 | 394.7707 | 379.034 | 334.0952
3411.6257 | 3264.6257 | 297.5724 | 353.2852 | 382.5515 | 353.9131 | 401.3056 | 398.7072 | 394.6224 | 378.9513 | 334.0412
3412.6271 | 3265.6271 | 297.1646 | 353.0452 | 382.292 | 353.7047 | 401.1142 | 398.5764 | 394.4838 | 379.2886 | 333.9983
3413.6286 | 3266.6286 | 296.7833 | 352.8781 | 382.057 | 353.5195 | 400.937 | 398.4386 | 394.3341 | 379.0305 | 333.9413
3414.63 | 3267.63 | 296.4225 | 352.7668 | 381.8049 | 353.3114 | 400.7454 | 398.34 | 394.1861 | 378.7741 | 333.8833
3415.6314 | 3268.6314 | 296.0542 | 352.5395 | 381.574 | 353.1156 | 400.5708 | 398.2336 | 394.0367 | 378.5738 | 333.8051
3416.6329 | 3269.6329 | 295.6877 | 352.3435 | 381.291 | 352.9197 | 400.3872 | 398.1128 | 393.8848 | 378.4908 | 333.7279
3417.6343 | 3270.6343 | 295.3845 | 352.0296 | 380.9974 | 352.7239 | 400.2082 | 397.9932 | 393.7389 | 378.6902 | 333.6799
3418.6257 | 3271.6257 | 295.1027 | 351.8569 | 380.7684 | 352.5245 | 400.0274 | 397.8285 | 393.5829 | 378.6117 | 333.6219
3419.6272 | 3272.6272 | 294.8225 | 351.7478 | 380.5222 | 352.3182 | 399.8443 | 397.5986 | 393.4282 | 378.2766 | 333.5671
3420.6286 | 3273.6286 | 294.4756 | 351.5337 | 380.3029 | 352.1072 | 399.6604 | 397.4178 | 393.2748 | 378.6966 | 333.5196
3421.6301 | 3274.6301 | 294.1234 | 351.3551 | 379.9058 | 351.9143 | 399.4799 | 397.2402 | 393.1294 | 378.4089 | 333.4131
3422.6315 | 3275.6315 | 293.6795 | 351.1771 | 379.764 | 351.6979 | 399.2884 | 397.0517 | 392.9755 | 378.03 | 333.3502
3423.6329 | 3276.6329 | 293.184 | 350.9809 | 379.5066 | 351.4546 | 399.0943 | 396.8485 | 392.8148 | 377.8874 | 333.3018
3424.6344 | 3277.6344 | 292.8038 | 350.7812 | 379.2734 | 351.2571 | 398.9317 | 396.6933 | 392.6602 | 377.6271 | 333.255
3425.6358 | 3278.6358 | 292.4482 | 350.602 | 378.9788 | 351.0872 | 398.7332 | 396.5485 | 392.5015 | 377.437 | 333.2042
3426.6272 | 3279.6272 | 292.1136 | 350.4435 | 378.7598 | 350.8701 | 398.5595 | 396.361 | 392.3523 | 377.2503 | 333.1137
3427.6287 | 3280.6287 | 291.7886 | 350.2301 | 378.5341 | 350.6444 | 398.3687 | 396.2089 | 392.1889 | 377.1451 | 333.0397
3428.6301 | 3281.6301 | 291.4021 | 350.0593 | 378.3111 | 350.4326 | 398.19 | 396.0411 | 392.0347 | 377.154 | 332.9447
3429.6316 | 3282.6316 | 291.1316 | 349.8815 | 378.0716 | 350.2575 | 398.0123 | 395.8771 | 391.8815 | 377.3049 | 332.8656
3430.633 | 3283.633 | 290.8281 | 349.6924 | 377.8684 | 350.041 | 397.8234 | 395.6924 | 391.7258 | 377.0357 | 332.7854
3431.6344 | 3284.6344 | 290.3964 | 349.4935 | 377.5711 | 349.812 | 397.6261 | 395.5391 | 391.5725 | 376.7664 | 332.6946
3432.6259 | 3285.6259 | 289.9981 | 349.3037 | 377.324 | 349.6374 | 397.4472 | 395.3447 | 391.4212 | 376.5735 | 332.6159
3433.6273 | 3286.6273 | 289.6057 | 349.1204 | 377.1273 | 349.4782 | 397.2618 | 395.1943 | 391.2682 | 376.4626 | 332.5711
3434.6288 | 3287.6288 | 289.226 | 348.9035 | 376.9697 | 349.2592 | 397.0814 | 395.0537 | 391.1119 | 376.6853 | 332.5119
3435.6302 | 3288.6302 | 288.8518 | 348.704 | 376.687 | 349.0458 | 396.8883 | 394.9039 | 390.9678 | 376.415 | 332.4533
3436.6316 | 3289.6316 | 288.4822 | 348.4846 | 376.376 | 348.8661 | 396.7059 | 394.7526 | 390.8101 | 376.1418 | 332.3557
3437.6331 | 3290.6331 | 288.082 | 348.3987 | 376.2181 | 348.6589 | 396.5187 | 394.6061 | 390.6605 | 376.3676 | 332.2653
3438.6245 | 3291.6245 | 287.7433 | 348.1899 | 375.8576 | 348.4873 | 396.3223 | 394.4232 | 390.5054 | 376.0152 | 332.2248
3439.6259 | 3292.6259 | 287.3655 | 347.9745 | 375.6006 | 348.2555 | 396.1368 | 394.2394 | 390.3516 | 375.7685 | 332.1148
3440.6274 | 3293.6274 | 287.0213 | 347.8245 | 375.3724 | 348.0255 | 395.9498 | 394.0741 | 390.2047 | 375.5837 | 332.0697
3441.6288 | 3294.6288 | 286.7069 | 347.6065 | 375.1703 | 347.7214 | 395.7591 | 393.8974 | 390.0496 | 375.3998 | 331.9716
3442.6303 | 3295.6303 | 286.3639 | 347.4466 | 374.8757 | 347.4978 | 395.5673 | 393.7604 | 389.9015 | 375.2119 | 331.9295
3443.6317 | 3296.6317 | 286.0001 | 347.2393 | 374.6088 | 347.3287 | 395.3777 | 393.6499 | 389.7561 | 375.0719 | 331.8329
3444.6331 | 3297.6331 | 285.56 | 347.0209 | 374.2773 | 347.1656 | 395.1975 | 393.4531 | 389.5992 | 374.9122 | 331.7525
3445.6346 | 3298.6346 | 285.2101 | 346.8207 | 374.1564 | 346.9977 | 394.9998 | 393.2735 | 389.4516 | 375.09 | 331.6509
3446.636 | 3299.636 | 284.8755 | 346.6487 | 373.8683 | 346.7824 | 394.8125 | 393.1017 | 389.2899 | 375.0185 | 331.5803
3447.6274 | 3300.6274 | 284.5129 | 346.4926 | 373.6519 | 346.5841 | 394.6236 | 392.9548 | 389.139 | 374.7705 | 331.4969
3448.6289 | 3301.6289 | 284.1669 | 346.2473 | 373.4184 | 346.4089 | 394.4178 | 392.8066 | 388.9754 | 374.5542 | 331.3684
3449.6303 | 3302.6303 | 283.8153 | 346.0686 | 373.1568 | 346.2183 | 394.2495 | 392.6519 | 388.8162 | 374.3712 | 331.2809
3450.6318 | 3303.6318 | 283.4215 | 345.8368 | 372.8527 | 345.9807 | 394.0442 | 392.4742 | 388.6712 | 374.2261 | 331.1952
3451.6332 | 3304.6332 | 283.0766 | 345.7154 | 372.7154 | 345.7752 | 393.8617 | 392.3253 | 388.5025 | 374.5636 | 331.0819
3452.6346 | 3305.6346 | 282.7332 | 345.4995 | 372.4629 | 345.5638 | 393.6713 | 392.1618 | 388.3405 | 374.2148 | 330.9425
3453.6261 | 3306.6261 | 282.3493 | 345.3132 | 372.2211 | 345.3613 | 393.4834 | 392.0007 | 388.1825 | 374.0164 | 330.8409
3454.6275 | 3307.6275 | 281.9487 | 345.1276 | 371.9712 | 345.1255 | 393.2963 | 391.7771 | 388.0263 | 374.2985 | 330.7701
3455.629 | 3308.629 | 281.6672 | 344.9476 | 371.7061 | 344.8885 | 393.1009 | 391.6328 | 387.8592 | 373.8902 | 330.6907
3456.6304 | 3309.6304 | 281.3306 | 344.7912 | 371.5211 | 344.7334 | 392.9095 | 391.4805 | 387.693 | 373.6181 | 330.5939
3457.6318 | 3310.6318 | 280.9958 | 344.6179 | 371.2558 | 344.5286 | 392.7108 | 391.3084 | 387.533 | 373.434 | 330.5196
3458.6333 | 3311.6333 | 280.6501 | 344.3838 | 370.9388 | 344.3295 | 392.5089 | 391.1406 | 387.3862 | 373.1884 | 330.4644
3459.6347 | 3312.6347 | 280.3038 | 344.2077 | 370.7494 | 344.1221 | 392.3249 | 390.9828 | 387.2281 | 373.0201 | 330.3233
3460.6261 | 3313.6261 | 279.9605 | 344.0154 | 370.5164 | 343.8844 | 392.1319 | 390.8568 | 387.0612 | 372.8231 | 330.2403
3461.6276 | 3314.6276 | 279.6116 | 343.7768 | 370.3207 | 343.7276 | 391.9411 | 390.7449 | 386.9085 | 372.6818 | 330.1483
3462.629 | 3315.629 | 279.2322 | 343.6189 | 370.0898 | 343.5425 | 391.7507 | 390.5936 | 386.7552 | 373.0906 | 330.054
3463.6305 | 3316.6305 | 278.8263 | 343.3266 | 369.791 | 343.3673 | 391.5554 | 390.429 | 386.5976 | 372.8599 | 329.9602
3464.6319 | 3317.6319 | 278.498 | 343.1943 | 369.545 | 343.1369 | 391.3618 | 390.1953 | 386.4335 | 372.5667 | 329.8833
3465.6333 | 3318.6333 | 278.1374 | 343.0764 | 369.333 | 342.9394 | 391.17 | 389.8179 | 386.2654 | 372.3243 | 329.7779
3466.6348 | 3319.6348 | 277.7586 | 342.8816 | 369.0987 | 342.7493 | 390.9616 | 389.6864 | 386.0976 | 372.1228 | 329.7309
3467.6262 | 3320.6262 | 277.367 | 342.6792 | 368.7798 | 342.5674 | 390.7815 | 389.5433 | 385.9261 | 372.0189 | 329.6029
3468.6276 | 3321.6276 | 276.9792 | 342.4913 | 368.5614 | 342.3642 | 390.5913 | 389.3741 | 385.7602 | 372.2408 | 329.5261
3469.6291 | 3322.6291 | 276.5754 | 342.2878 | 368.4235 | 342.1672 | 390.4016 | 389.1815 | 385.5909 | 371.8876 | 329.4329
3470.6305 | 3323.6305 | 276.2735 | 342.115 | 368.1453 | 341.9506 | 390.2053 | 388.9609 | 385.4269 | 371.8058 | 329.3529
3471.632 | 3324.632 | 275.9315 | 341.9121 | 367.8576 | 341.751 | 390.0079 | 388.7779 | 385.2506 | 371.8926 | 329.2219
3472.6334 | 3325.6334 | 275.6123 | 341.7394 | 367.6324 | 341.5158 | 389.8205 | 388.6168 | 385.0898 | 371.5113 | 329.1505
3473.6348 | 3326.6348 | 275.2934 | 341.5118 | 367.4269 | 341.3353 | 389.6185 | 388.4462 | 384.9241 | 371.2983 | 329.0535
3474.6263 | 3327.6263 | 274.9813 | 341.3321 | 367.2106 | 341.1122 | 389.4405 | 388.2659 | 384.7514 | 371.0902 | 328.9495
3475.6277 | 3328.6277 | 274.6746 | 341.1468 | 367.04 | 340.9407 | 389.2447 | 388.0293 | 384.5874 | 370.8989 | 328.8334
3476.6291 | 3329.6291 | 274.3061 | 340.9655 | 366.7762 | 340.7058 | 389.0493 | 387.8266 | 384.4081 | 370.7082 | 328.7635
3477.6306 | 3330.6306 | 273.9753 | 340.7601 | 366.5479 | 340.5387 | 388.8761 | 387.6656 | 384.2318 | 370.5379 | 328.6639
3478.632 | 3331.632 | 273.6988 | 340.5948 | 366.2761 | 340.2522 | 388.6635 | 387.5004 | 384.0598 | 370.384 | 328.5914
3479.6335 | 3332.6335 | 273.3833 | 340.4543 | 366.1302 | 339.9918 | 388.4708 | 387.3426 | 383.8958 | 370.7439 | 328.4742
3480.6249 | 3333.6249 | 273.027 | 340.2455 | 365.9916 | 339.8321 | 388.2788 | 387.1686 | 383.7237 | 370.4457 | 328.3757
3481.6263 | 3334.6263 | 272.7185 | 340.0447 | 365.6863 | 339.6595 | 388.0891 | 386.9907 | 383.5473 | 370.1804 | 328.2871
3482.6278 | 3335.6278 | 272.3468 | 339.8586 | 365.4401 | 339.4236 | 387.8993 | 386.8258 | 383.3825 | 369.9488 | 328.1899
3483.6292 | 3336.6292 | 272.0174 | 339.6016 | 365.1791 | 339.2703 | 387.6983 | 386.6589 | 383.2073 | 369.807 | 328.0748
3484.6307 | 3337.6307 | 271.6631 | 339.3928 | 364.9742 | 339.0674 | 387.5138 | 386.48 | 383.0558 | 369.7912 | 327.9556
3485.6321 | 3338.6321 | 271.3606 | 339.2115 | 364.6905 | 338.8549 | 387.314 | 386.3212 | 382.8776 | 369.8285 | 327.8611
3486.6335 | 3339.6335 | 271.0601 | 339.1491 | 364.2809 | 338.7063 | 387.111 | 386.1464 | 382.7157 | 369.5274 | 327.7543
3487.635 | 3340.635 | 270.7992 | 338.9045 | 364.1405 | 338.4858 | 386.9165 | 385.9711 | 382.5546 | 369.5449 | 327.6778
3488.6264 | 3341.6264 | 270.4977 | 338.7435 | 363.9355 | 338.3136 | 386.7211 | 385.8065 | 382.3905 | 369.4226 | 327.5704
3489.6278 | 3342.6278 | 270.1949 | 338.5127 | 363.6667 | 338.1258 | 386.5207 | 385.5988 | 382.2212 | 369.0948 | 327.4936
3490.6293 | 3343.6293 | 269.8451 | 338.3447 | 363.4703 | 337.9183 | 386.3339 | 385.3988 | 382.0597 | 368.8956 | 327.4073
3491.6307 | 3344.6307 | 269.5384 | 338.1174 | 363.1693 | 337.7028 | 386.1444 | 385.2197 | 381.8882 | 368.6868 | 327.3011
3492.6322 | 3345.6322 | 269.2141 | 337.9807 | 362.8082 | 337.5386 | 385.9404 | 385.0445 | 381.7169 | 368.5062 | 327.1872
3493.6336 | 3346.6336 | 268.8903 | 337.7223 | 362.7087 | 337.3442 | 385.7446 | 384.813 | 381.5624 | 368.338 | 327.0588
3494.635 | 3347.635 | 268.5963 | 337.5582 | 362.4715 | 337.1381 | 385.544 | 384.6643 | 381.4023 | 368.1449 | 327.0072
3495.6265 | 3348.6265 | 268.3117 | 337.3697 | 362.1622 | 336.9187 | 385.3487 | 384.5223 | 381.2401 | 368.0654 | 326.9105
3496.6279 | 3349.6279 | 268.0043 | 337.1838 | 361.9269 | 336.7379 | 385.1464 | 384.3766 | 381.0757 | 368.6736 | 326.7909
3497.6293 | 3350.6293 | 267.6637 | 337.0497 | 361.6782 | 336.5269 | 384.9636 | 384.2142 | 380.9209 | 368.345 | 326.6959
3498.6308 | 3351.6308 | 267.3795 | 336.798 | 361.4274 | 336.3187 | 384.7549 | 384.0449 | 380.749 | 367.9714 | 326.6133
3499.6322 | 3352.6322 | 267.0954 | 336.6738 | 361.322 | 336.0872 | 384.5498 | 383.8817 | 380.5755 | 367.7017 | 326.4692
3500.6337 | 3353.6337 | 266.8083 | 336.458 | 361.0613 | 335.8098 | 384.3616 | 383.7129 | 380.3989 | 367.6292 | 326.3577
3501.6351 | 3354.6351 | 266.5278 | 336.3123 | 360.7733 | 335.6012 | 384.175 | 383.5358 | 380.2374 | 367.6343 | 326.2383
3502.6265 | 3355.6265 | 266.204 | 336.022 | 360.5603 | 335.4806 | 383.9664 | 383.351 | 380.0636 | 367.4981 | 326.1231
3503.628 | 3356.628 | 265.9159 | 335.8825 | 360.2671 | 335.2536 | 383.7662 | 383.1764 | 379.8945 | 367.1624 | 326.0373
3504.6294 | 3357.6294 | 265.5966 | 335.7418 | 359.9682 | 335.0325 | 383.5508 | 383.0033 | 379.7137 | 367.2858 | 325.9098
3505.6308 | 3358.6308 | 265.3311 | 335.5936 | 359.8221 | 334.8601 | 383.3704 | 382.8376 | 379.547 | 367.0121 | 325.8265
3506.6323 | 3359.6323 | 265.0896 | 335.4038 | 359.5818 | 334.6435 | 383.1679 | 382.647 | 379.3677 | 366.7308 | 325.7041
3507.6337 | 3360.6337 | 264.7582 | 335.1711 | 359.4278 | 334.3885 | 382.9583 | 382.4694 | 379.1978 | 366.5044 | 325.6078
3508.6352 | 3361.6352 | 264.4683 | 335.0077 | 359.1402 | 334.2041 | 382.7754 | 382.3098 | 379.0307 | 366.306 | 325.4913
3509.6266 | 3362.6266 | 264.1332 | 334.8251 | 358.8035 | 333.986 | 382.5732 | 382.1405 | 378.8538 | 366.1108 | 325.3677
3510.628 | 3363.628 | 263.7642 | 334.6475 | 358.5928 | 333.8537 | 382.3765 | 381.7565 | 378.6757 | 365.9148 | 325.2771
3511.6295 | 3364.6295 | 263.4452 | 334.4696 | 358.4164 | 333.6817 | 382.186 | 381.5222 | 378.5066 | 365.7538 | 325.1583
3512.6309 | 3365.6309 | 263.102 | 334.2951 | 358.1104 | 333.4957 | 381.9796 | 381.3882 | 378.3376 | 365.7521 | 325.0384
3513.6324 | 3366.6324 | 262.7346 | 334.104 | 357.9097 | 333.2801 | 381.7964 | 381.2711 | 378.1622 | 365.8385 | 324.9586
3514.6338 | 3367.6338 | 262.39 | 333.9094 | 357.7244 | 333.0971 | 381.5701 | 381.1354 | 377.9929 | 365.5763 | 324.8393
3515.6352 | 3368.6352 | 262.1147 | 333.6775 | 357.5282 | 332.9187 | 381.3874 | 381.0002 | 377.8188 | 365.3268 | 324.7185
3516.6267 | 3369.6267 | 261.8996 | 333.5214 | 357.2671 | 332.7189 | 381.1925 | 380.8527 | 377.6553 | 365.1231 | 324.6181
3517.6281 | 3370.6281 | 261.6164 | 333.3051 | 357.1423 | 332.5162 | 380.996 | 380.69 | 377.479 | 364.9697 | 324.5165
3518.6396 | 3371.6396 | 261.3655 | 333.0484 | 357.0106 | 332.3343 | 380.7901 | 380.5366 | 377.3065 | 365.2457 | 324.4066
3519.631 | 3372.631 | 261.0607 | 332.8944 | 356.745 | 332.124 | 380.5848 | 380.3712 | 377.1326 | 365.0032 | 324.3225
3520.6324 | 3373.6324 | 260.7463 | 332.7685 | 356.5251 | 331.9503 | 380.399 | 380.2149 | 376.9649 | 364.6865 | 324.2179
3521.6339 | 3374.6339 | 260.4185 | 332.5877 | 356.3379 | 331.7387 | 380.1889 | 380.0533 | 376.7943 | 365.0128 | 324.1036
3522.6353 | 3375.6353 | 260.1217 | 332.4483 | 356.0923 | 331.5337 | 379.99 | 379.9051 | 376.6229 | 364.6304 | 323.9951
3523.6367 | 3376.6367 | 259.8901 | 332.2252 | 355.7773 | 331.3456 | 379.795 | 379.7391 | 376.4511 | 364.3212 | 323.8651
3524.6282 | 3377.6282 | 259.5883 | 332.0771 | 355.4721 | 331.1502 | 379.5924 | 379.5471 | 376.2747 | 364.1216 | 323.7609
3525.6296 | 3378.6296 | 259.2905 | 331.8829 | 355.2462 | 330.9454 | 379.3968 | 379.3617 | 376.099 | 363.8728 | 323.6478
3526.631 | 3379.631 | 258.9826 | 331.7002 | 355.0927 | 330.7826 | 379.2031 | 379.18 | 375.9267 | 363.6759 | 323.5313
3527.6325 | 3380.6325 | 258.6712 | 331.5348 | 355.0531 | 330.5576 | 379.0162 | 379.0246 | 375.7595 | 363.4887 | 323.458
3528.6339 | 3381.6339 | 258.4069 | 331.366 | 354.799 | 330.3738 | 378.7942 | 378.8354 | 375.5809 | 363.3032 | 323.337
3529.6354 | 3382.6354 | 258.093 | 331.2026 | 354.478 | 330.1562 | 378.6033 | 378.6405 | 375.4088 | 363.594 | 323.2325
3530.6268 | 3383.6268 | 257.7958 | 331.0365 | 354.2467 | 329.9777 | 378.3955 | 378.4597 | 375.2403 | 363.5916 | 323.1451
3531.6282 | 3384.6282 | 257.5363 | 330.8706 | 354.0484 | 329.6696 | 378.1993 | 378.2902 | 375.0569 | 363.2783 | 323.0073
3532.6297 | 3385.6297 | 257.2655 | 330.6641 | 353.8273 | 329.4954 | 378.0124 | 378.1169 | 374.8778 | 362.967 | 322.9043
3533.6311 | 3386.6311 | 256.9704 | 330.4542 | 353.5692 | 329.3499 | 377.7956 | 377.8645 | 374.7013 | 362.7384 | 322.8007
3534.6326 | 3387.6326 | 256.7495 | 330.2073 | 353.3136 | 329.1634 | 377.6114 | 377.6211 | 374.5256 | 362.5791 | 322.6773
3535.634 | 3388.634 | 256.4842 | 330.1048 | 353.1343 | 328.9971 | 377.4101 | 377.4642 | 374.3512 | 363.0239 | 322.5669
3536.6354 | 3389.6354 | 256.0963 | 329.9211 | 352.8802 | 328.7868 | 377.2143 | 377.2897 | 374.1707 | 362.5886 | 322.4769
3537.6269 | 3390.6269 | 255.7476 | 329.7666 | 352.6629 | 328.6089 | 377.0097 | 377.1037 | 373.9841 | 362.3615 | 322.3716
3538.6283 | 3391.6283 | 255.3893 | 329.5625 | 352.4247 | 328.4233 | 376.8254 | 376.9246 | 373.8032 | 362.8437 | 322.2121
3539.6297 | 3392.6297 | 255.0741 | 329.4042 | 352.1406 | 328.2283 | 376.6176 | 376.7429 | 373.6266 | 362.2659 | 322.1203
3540.6312 | 3393.6312 | 254.721 | 329.2176 | 351.9626 | 328.0359 | 376.4335 | 376.559 | 373.451 | 361.924 | 322.0162
3541.6326 | 3394.6326 | 254.438 | 329.0416 | 351.7285 | 327.8338 | 376.2404 | 376.3865 | 373.2718 | 361.7253 | 321.8865
3542.6341 | 3395.6341 | 254.1883 | 328.8503 | 351.5953 | 327.6523 | 376.0456 | 376.199 | 373.0976 | 361.4265 | 321.824
3543.6255 | 3396.6255 | 253.8508 | 328.6494 | 351.3617 | 327.4656 | 375.8462 | 376.0265 | 372.9187 | 361.2038 | 321.6966
3544.6269 | 3397.6269 | 253.5577 | 328.4867 | 351.1067 | 327.2849 | 375.6528 | 375.8511 | 372.7417 | 360.9876 | 321.605
3545.6284 | 3398.6284 | 253.2239 | 328.2787 | 350.8917 | 327.0947 | 375.4468 | 375.6641 | 372.5657 | 360.8071 | 321.4837
3546.6298 | 3399.6298 | 252.931 | 328.1098 | 350.604 | 326.9112 | 375.2625 | 375.4853 | 372.3965 | 361.1396 | 321.3744
3547.6312 | 3400.6312 | 252.6161 | 327.9317 | 350.4558 | 326.6985 | 375.0715 | 375.302 | 372.2166 | 360.9018 | 321.2818
3548.6327 | 3401.6327 | 252.2879 | 327.7125 | 350.2356 | 326.4765 | 374.8961 | 375.1423 | 372.0436 | 360.5911 | 321.1919
3549.6341 | 3402.6341 | 251.9629 | 327.5513 | 350.0292 | 326.3019 | 374.6928 | 374.9659 | 371.873 | 360.3212 | 321.0506
3550.6356 | 3403.6356 | 251.7283 | 327.3727 | 349.7038 | 326.1328 | 374.4977 | 374.7862 | 371.701 | 360.116 | 320.9197
3551.627 | 3404.627 | 251.4873 | 327.1629 | 349.4442 | 325.9183 | 374.3023 | 374.6199 | 371.5271 | 359.9878 | 320.8113
3552.6284 | 3405.6284 | 251.2143 | 326.9644 | 349.2716 | 325.7357 | 374.1123 | 374.4389 | 371.3574 | 360.2156 | 320.7143
3553.6399 | 3406.6399 | 250.989 | 326.7487 | 349.0758 | 325.5405 | 373.9288 | 374.2146 | 371.1824 | 359.8363 | 320.5858
3554.6313 | 3407.6313 | 250.7204 | 326.5422 | 348.8461 | 325.3419 | 373.7356 | 374.0345 | 371.0093 | 359.7414 | 320.4902
3555.6327 | 3408.6327 | 250.4399 | 326.4328 | 348.6193 | 325.175 | 373.5648 | 373.8683 | 370.8389 | 359.8005 | 320.3775
3556.6342 | 3409.6342 | 250.1071 | 326.2154 | 348.4341 | 324.9653 | 373.3644 | 373.6801 | 370.6706 | 359.4246 | 320.2424
3557.6356 | 3410.6356 | 249.7454 | 326.0176 | 348.153 | 324.7687 | 373.1664 | 373.4998 | 370.4948 | 359.1669 | 320.1032
3558.6271 | 3411.6271 | 249.4359 | 325.8148 | 347.9214 | 324.5763 | 372.9909 | 373.3025 | 370.3242 | 358.9284 | 319.9992
3559.6285 | 3412.6285 | 249.178 | 325.6354 | 347.8249 | 324.4087 | 372.7969 | 373.1047 | 370.1496 | 358.7154 | 319.8685
3560.6299 | 3413.6299 | 248.8773 | 325.4139 | 347.4901 | 324.1942 | 372.6054 | 372.891 | 369.9721 | 358.5152 | 319.7674
3561.6314 | 3414.6314 | 248.5391 | 325.246 | 347.2747 | 324.0187 | 372.4122 | 372.7157 | 369.804 | 358.3212 | 319.6481
3562.6328 | 3415.6328 | 248.2372 | 325.0657 | 347.0198 | 323.8398 | 372.2352 | 372.5502 | 369.6349 | 358.1409 | 319.535
3563.6343 | 3416.6343 | 247.938 | 324.8827 | 346.8227 | 323.633 | 372.0536 | 372.3788 | 369.4691 | 358.4715 | 319.4427
3564.6257 | 3417.6257 | 247.686 | 324.7296 | 346.6381 | 323.4294 | 371.8668 | 372.2091 | 369.2863 | 358.1594 | 319.3143
3565.6271 | 3418.6271 | 247.4377 | 324.5399 | 346.3817 | 323.2603 | 371.6717 | 372.0051 | 369.1145 | 357.8704 | 319.216
3566.6286 | 3419.6286 | 247.1674 | 324.3401 | 346.1705 | 323.0663 | 371.474 | 371.8249 | 368.9431 | 357.6378 | 319.0954
3567.63 | 3420.63 | 246.889 | 324.166 | 345.9932 | 322.8766 | 371.3103 | 371.6335 | 368.7693 | 357.4524 | 318.9994
3568.6314 | 3421.6314 | 246.5735 | 323.9536 | 345.7206 | 322.7371 | 371.1128 | 371.4612 | 368.6005 | 357.4253 | 318.8599
3569.6329 | 3422.6329 | 246.3148 | 323.7815 | 345.6444 | 322.4865 | 370.9363 | 371.2969 | 368.4282 | 357.5177 | 318.757
3570.6243 | 3423.6243 | 246.1054 | 323.6186 | 345.3476 | 322.2899 | 370.7351 | 371.098 | 368.2499 | 357.1586 | 318.6459
3571.6358 | 3424.6358 | 245.8789 | 323.4433 | 345.1659 | 322.1129 | 370.5541 | 370.9211 | 368.0822 | 357.2148 | 318.5292
3572.6272 | 3425.6272 | 245.5988 | 323.307 | 344.8799 | 321.9189 | 370.375 | 370.7454 | 367.9071 | 357.1234 | 318.4042
3573.6286 | 3426.6286 | 245.3995 | 323.1087 | 344.639 | 321.7383 | 370.1863 | 370.5746 | 367.724 | 356.7453 | 318.2872
3574.6301 | 3427.6301 | 245.1817 | 322.9239 | 344.5223 | 321.5369 | 370.0006 | 370.3855 | 367.5577 | 356.4972 | 318.1796
3575.6315 | 3428.6315 | 244.9275 | 322.7342 | 344.3098 | 321.3698 | 369.8253 | 370.2145 | 367.3821 | 356.269 | 318.0678
3576.6329 | 3429.6329 | 244.7322 | 322.5154 | 344.1243 | 321.1785 | 369.65 | 370.0493 | 367.2059 | 356.0449 | 317.9369
3577.6344 | 3430.6344 | 244.5215 | 322.3437 | 343.9065 | 320.9898 | 369.449 | 369.8475 | 367.0361 | 355.8444 | 317.8056
3578.6358 | 3431.6358 | 244.2672 | 322.1633 | 343.6926 | 320.7967 | 369.2663 | 369.6596 | 366.8615 | 355.6559 | 317.668
3579.6273 | 3432.6273 | 243.9671 | 322.0073 | 343.4446 | 320.6333 | 369.0736 | 369.4798 | 366.6898 | 355.5386 | 317.5146
3580.6287 | 3433.6287 | 243.6368 | 321.7915 | 343.1142 | 320.4413 | 368.8938 | 369.3116 | 366.5129 | 355.7972 | 317.4295
3581.6301 | 3434.6301 | 243.3336 | 321.6581 | 342.9254 | 320.2392 | 368.7176 | 369.1334 | 366.3391 | 355.4761 | 317.3214
3582.6316 | 3435.6316 | 243.0469 | 321.4986 | 342.7403 | 320.0426 | 368.5303 | 368.9442 | 366.167 | 355.2002 | 317.1827
3583.633 | 3436.633 | 242.6989 | 321.3013 | 342.5041 | 319.7545 | 368.3417 | 368.7704 | 365.9913 | 354.9561 | 317.0736
3584.6345 | 3437.6345 | 242.3726 | 321.109 | 342.3377 | 319.5977 | 368.1549 | 368.5906 | 365.8135 | 354.791 | 316.9651
3585.6259 | 3438.6259 | 242.0421 | 320.9509 | 342.1588 | 319.4348 | 367.9749 | 368.4177 | 365.6434 | 354.8666 | 316.8566
3586.6273 | 3439.6273 | 241.8136 | 320.7573 | 341.9052 | 319.2603 | 367.7827 | 368.2332 | 365.4641 | 354.8035 | 316.7452
3587.6288 | 3440.6288 | 241.5766 | 320.5699 | 341.6875 | 319.0743 | 367.5933 | 368.0472 | 365.3007 | 354.4632 | 316.6268
3588.6302 | 3441.6302 | 241.3142 | 320.3841 | 341.4631 | 318.8277 | 367.4019 | 367.8746 | 365.1199 | 354.6135 | 316.5164
3589.6316 | 3442.6316 | 241.0981 | 320.2106 | 341.2569 | 318.7003 | 367.2101 | 367.7004 | 364.9312 | 354.3512 | 316.3974
3590.6331 | 3443.6331 | 240.8657 | 320.0236 | 341.0434 | 318.5384 | 367.0261 | 367.5204 | 364.7635 | 354.0125 | 316.2939
3591.6345 | 3444.6345 | 240.6334 | 319.8672 | 340.9156 | 318.3292 | 366.8436 | 367.3355 | 364.5837 | 353.8222 | 316.1552
3592.6259 | 3445.6259 | 240.4578 | 319.6677 | 340.5984 | 318.0706 | 366.6516 | 367.1555 | 364.4161 | 353.5664 | 316.0667
3593.6274 | 3446.6274 | 240.2059 | 319.5023 | 340.3348 | 317.8907 | 366.4707 | 366.9739 | 364.2415 | 353.3604 | 315.9493
3594.6288 | 3447.6288 | 239.9236 | 319.2957 | 340.1652 | 317.7677 | 366.2881 | 366.8179 | 364.0667 | 353.1659 | 315.8011
3595.6303 | 3448.6303 | 239.6494 | 319.1312 | 339.9965 | 317.5437 | 366.0898 | 366.6494 | 363.8955 | 352.9662 | 315.7239
3596.6317 | 3449.6317 | 239.3833 | 318.9475 | 339.7583 | 317.3882 | 365.9092 | 366.4426 | 363.7223 | 352.9834 | 315.591
3597.6331 | 3450.6331 | 239.1317 | 318.7464 | 339.6177 | 317.2052 | 365.7167 | 366.187 | 363.5542 | 353.0927 | 315.4836
3598.6346 | 3451.6346 | 238.905 | 318.5699 | 339.2578 | 317.0192 | 365.5252 | 365.9938 | 363.3803 | 352.7808 | 315.3698
3599.636 | 3452.636 | 238.6523 | 318.3792 | 339.0513 | 316.8444 | 365.3466 | 365.8159 | 363.2021 | 352.5175 | 315.2464
3600.6274 | 3453.6274 | 238.4186 | 318.241 | 338.9965 | 316.6313 | 365.1593 | 365.6562 | 363.0302 | 352.2685 | 315.1502
3601.6289 | 3454.6289 | 238.1495 | 318.058 | 338.7687 | 316.4509 | 364.9802 | 365.4746 | 362.8561 | 352.1155 | 315.0048
3602.6303 | 3455.6303 | 237.8366 | 317.8638 | 338.554 | 316.2686 | 364.7881 | 365.3043 | 362.6878 | 352.4482 | 314.8942
3603.6318 | 3456.6318 | 237.5585 | 317.6734 | 338.3515 | 316.085 | 364.6088 | 365.124 | 362.507 | 352.1248 | 314.7949
3604.6332 | 3457.6332 | 237.2857 | 317.4971 | 338.1204 | 315.8998 | 364.4134 | 364.955 | 362.342 | 351.7844 | 314.6568

## C3-4
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 149.0464 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38904.6217 | 1 | 0 | 38904.6217 | 1 | 0 | -132.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6219 | 1 | 0 | 38904.6219 | 1 | 0 | -115.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6221 | 1 | 0 | 38904.6221 | 1 | 0 | -99 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6223 | 1 | 0 | 38904.6223 | 1 | 0 | -82 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6225 | 1 | 0 | 38904.6225 | 1 | 0 | -65.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6227 | 1 | 0 | 38904.6227 | 1 | 0 | -48.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6229 | 1 | 0 | 38904.6229 | 2 | 0 | -31.5 | 115.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244038 | 121969 | 244037.9994
38904.6231 | 1 | 0 | 38904.6231 | 1 | 0 | -15 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6233 | 1 | 0 | 38904.6233 | 1 | 0 | 2 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6234 | 1 | 0 | 38904.6235 | 1 | 0 | 18.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6236 | 1 | 0 | 38904.6237 | 1 | 0 | 35.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6238 | 1 | 0 | 38904.6239 | 2 | 0 | 52 | 199 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244038 | 121969 | 244037.9994
38904.624 | 1 | 0 | 38904.6241 | 1 | 0 | 69 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6242 | 1 | 0 | 38904.6242 | 1 | 0 | 86 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6244 | 1 | 0 | 38904.6244 | 1 | 0 | 102.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6246 | 1 | 0 | 38904.6246 | 1 | 0 | 119.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6248 | 1 | 0 | 38904.6248 | 1 | 0 | 136 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.625 | 1 | 0 | 38904.625 | 1 | 0 | 153 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6252 | 1 | 0 | 38904.6252 | 1 | 0 | 169.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6254 | 1 | 0 | 38904.6254 | 1 | 0 | 186.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6256 | 1 | 0 | 38904.6256 | 2 | 0 | 203.5 | 350.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 244038 | 121969 | 244037.9994
38904.6258 | 1 | 0 | 38904.6258 | 1 | 0 | 220.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.626 | 1 | 0 | 38904.626 | 1 | 0 | 237 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6262 | 1 | 0 | 38904.6262 | 1 | 0 | 254 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6264 | 1 | 0 | 38904.6264 | 1 | 0 | 270.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6266 | 1 | 0 | 38904.6266 | 1 | 0 | 287.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6267 | 1 | 0 | 38904.6268 | 1 | 0 | 304 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6269 | 1 | 0 | 38904.627 | 1 | 0 | 321 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6271 | 1 | 0 | 38904.6272 | 1 | 0 | 337.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6273 | 1 | 0 | 38904.6273 | 1 | 0 | 354.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6275 | 1 | 0 | 38904.6275 | 1 | 0 | 371.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6277 | 1 | 0 | 38904.6277 | 1 | 0 | 388.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6279 | 1 | 0 | 38904.6279 | 1 | 0 | 405 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6281 | 1 | 0 | 38904.6281 | 1 | 0 | 421.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6283 | 1 | 0 | 38904.6283 | 1 | 0 | 438.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6285 | 1 | 0 | 38904.6285 | 1 | 0 | 455.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6287 | 1 | 0 | 38904.6287 | 1 | 0 | 472 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6289 | 1 | 0 | 38904.6289 | 1 | 0 | 489 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6291 | 1 | 0 | 38904.6291 | 1 | 0 | 505.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6293 | 2 | 0 | 38904.6293 | 1 | 0 | 522.5 | 669.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121969 | 244038 | 121968.9988
38904.6295 | 1 | 0 | 38904.6295 | 1 | 0 | 539.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6297 | 1 | 0 | 38904.6297 | 1 | 0 | 556.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6299 | 1 | 0 | 38904.6299 | 1 | 0 | 573 | 720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6301 | 1 | 0 | 38904.6301 | 1 | 0 | 589.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6303 | 1 | 0 | 38904.6303 | 1 | 0 | 606.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6305 | 1 | 0 | 38904.6305 | 1 | 0 | 623.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6306 | 1 | 0 | 38904.6307 | 1 | 0 | 640 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6308 | 1 | 0 | 38904.6309 | 1 | 0 | 657 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.631 | 1 | 0 | 38904.631 | 1 | 0 | 673.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6312 | 1 | 0 | 38904.6312 | 1 | 0 | 690.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6314 | 1 | 0 | 38904.6314 | 1 | 0 | 707.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6316 | 1 | 0 | 38904.6316 | 1 | 0 | 724 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6318 | 1 | 0 | 38904.6318 | 1 | 0 | 741 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.632 | 1 | 0 | 38904.632 | 1 | 0 | 757.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6322 | 1 | 0 | 38904.6322 | 1 | 0 | 774.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6324 | 1 | 0 | 38904.6324 | 1 | 0 | 791.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6326 | 1 | 0 | 38904.6326 | 1 | 0 | 808 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6328 | 1 | 0 | 38904.6328 | 1 | 0 | 825 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.633 | 1 | 0 | 38904.633 | 1 | 0 | 841.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6332 | 1 | 0 | 38904.6332 | 1 | 0 | 858.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6334 | 1 | 0 | 38904.6334 | 1 | 0 | 875.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6336 | 1 | 0 | 38904.6336 | 1 | 0 | 892 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6338 | 1 | 0 | 38904.6338 | 1 | 0 | 909 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6339 | 1 | 0 | 38904.634 | 1 | 0 | 925.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6341 | 1 | 0 | 38904.6342 | 1 | 0 | 942.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6343 | 1 | 0 | 38904.6344 | 1 | 0 | 959.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6345 | 1 | 0 | 38904.6345 | 1 | 0 | 976 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6347 | 1 | 0 | 38904.6347 | 1 | 0 | 993 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6349 | 1 | 0 | 38904.6349 | 1 | 0 | 1009.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6351 | 1 | 0 | 38904.6351 | 1 | 0 | 1026.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6353 | 1 | 0 | 38904.6353 | 1 | 0 | 1043.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6355 | 1 | 0 | 38904.6355 | 1 | 0 | 1060 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6357 | 1 | 0 | 38904.6357 | 1 | 0 | 1077 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6359 | 1 | 0 | 38904.6359 | 1 | 0 | 1093.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6361 | 1 | 0 | 38904.6361 | 1 | 0 | 1110.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6363 | 1 | 0 | 38904.6363 | 1 | 0 | 1127.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6365 | 1 | 0 | 38904.6365 | 1 | 0 | 1144 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6367 | 1 | 0 | 38904.6367 | 1 | 0 | 1161 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6369 | 1 | 0 | 38904.6369 | 1 | 0 | 1177.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6371 | 1 | 0 | 38904.6371 | 1 | 0 | 1194.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6373 | 1 | 0 | 38904.6373 | 1 | 0 | 1211.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6374 | 1 | 0 | 38904.6375 | 1 | 0 | 1228 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6376 | 1 | 0 | 38904.6377 | 1 | 0 | 1245 | 1392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6378 | 1 | 0 | 38904.6378 | 1 | 0 | 1261.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.638 | 1 | 0 | 38904.638 | 1 | 0 | 1278.5 | 1425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6382 | 1 | 0 | 38904.6382 | 1 | 0 | 1295.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6384 | 1 | 0 | 38904.6384 | 1 | 0 | 1312 | 1459 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6386 | 1 | 0 | 38904.6386 | 1 | 0 | 1328.5 | 1475.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6388 | 1 | 0 | 38904.6388 | 1 | 0 | 1345.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.639 | 1 | 0 | 38904.639 | 1 | 0 | 1362.5 | 1509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6392 | 1 | 0 | 38904.6392 | 1 | 0 | 1379 | 1526 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6394 | 1 | 0 | 38904.6394 | 1 | 0 | 1396 | 1543 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6396 | 1 | 0 | 38904.6396 | 1 | 0 | 1413 | 1560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6398 | 1 | 0 | 38904.6398 | 1 | 0 | 1429.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.64 | 1 | 0 | 38904.64 | 1 | 0 | 1446.5 | 1593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6402 | 1 | 0 | 38904.6402 | 1 | 0 | 1463 | 1610 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6404 | 1 | 0 | 38904.6404 | 1 | 0 | 1480 | 1627 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6406 | 1 | 0 | 38904.6406 | 1 | 0 | 1496.5 | 1643.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6408 | 1 | 0 | 38904.6408 | 1 | 0 | 1513.5 | 1660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6409 | 1 | 0 | 38904.641 | 1 | 0 | 1530.5 | 1677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6411 | 1 | 0 | 38904.6412 | 1 | 0 | 1547.5 | 1694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6413 | 1 | 0 | 38904.6414 | 1 | 0 | 1564 | 1711 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6415 | 1 | 0 | 38904.6415 | 1 | 0 | 1580.5 | 1727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6417 | 1 | 0 | 38904.6417 | 1 | 0 | 1597.5 | 1744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6419 | 1 | 0 | 38904.6419 | 1 | 0 | 1614.5 | 1761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6421 | 1 | 0 | 38904.6421 | 1 | 0 | 1631 | 1778 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6423 | 1 | 0 | 38904.6423 | 1 | 0 | 1648 | 1795 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6425 | 1 | 0 | 38904.6425 | 1 | 0 | 1664.5 | 1811.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6427 | 1 | 0 | 38904.6427 | 1 | 0 | 1681.5 | 1828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6429 | 1 | 0 | 38904.6429 | 1 | 0 | 1698.5 | 1845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6431 | 1 | 0 | 38904.6431 | 1 | 0 | 1715 | 1862 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6433 | 1 | 0 | 38904.6433 | 1 | 0 | 1732 | 1879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6435 | 1 | 0 | 38904.6435 | 1 | 0 | 1748.5 | 1895.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6437 | 1 | 0 | 38904.6437 | 1 | 0 | 1765.5 | 1912.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6439 | 1 | 0 | 38904.6439 | 1 | 0 | 1782.5 | 1929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6441 | 1 | 0 | 38904.6441 | 1 | 0 | 1799 | 1946 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6442 | 1 | 0 | 38904.6443 | 1 | 0 | 1816 | 1963 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6444 | 1 | 0 | 38904.6445 | 1 | 0 | 1832.5 | 1979.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6446 | 1 | 0 | 38904.6447 | 1 | 0 | 1849.5 | 1996.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6448 | 1 | 0 | 38904.6448 | 1 | 0 | 1866.5 | 2013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.645 | 1 | 0 | 38904.645 | 1 | 0 | 1883 | 2030 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6452 | 1 | 0 | 38904.6452 | 1 | 0 | 1900 | 2047 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6454 | 1 | 0 | 38904.6454 | 1 | 0 | 1916.5 | 2063.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6456 | 1 | 0 | 38904.6456 | 1 | 0 | 1933.5 | 2080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6458 | 1 | 0 | 38904.6458 | 1 | 0 | 1950.5 | 2097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.646 | 1 | 0 | 38904.646 | 1 | 0 | 1967 | 2114 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6462 | 1 | 0 | 38904.6462 | 1 | 0 | 1984 | 2131 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6464 | 1 | 0 | 38904.6464 | 1 | 0 | 2000.5 | 2147.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6466 | 1 | 0 | 38904.6466 | 1 | 0 | 2017.5 | 2164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6468 | 1 | 0 | 38904.6468 | 1 | 0 | 2034.5 | 2181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.647 | 1 | 0 | 38904.647 | 1 | 0 | 2051 | 2198 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6472 | 1 | 0 | 38904.6472 | 1 | 0 | 2068 | 2215 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6474 | 1 | 0 | 38904.6474 | 1 | 0 | 2084.5 | 2231.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6476 | 1 | 0 | 38904.6476 | 1 | 0 | 2101.5 | 2248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6478 | 1 | 0 | 38904.6478 | 1 | 0 | 2118.5 | 2265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6479 | 1 | 0 | 38904.648 | 1 | 0 | 2135 | 2282 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6481 | 1 | 0 | 38904.6482 | 1 | 0 | 2152 | 2299 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6483 | 2 | 0 | 38904.6483 | 1 | 0 | 2168.5 | 2315.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121969 | 244038 | 121968.9988
38904.6485 | 2 | 0 | 38904.6485 | 1 | 0 | 2185.5 | 2332.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121969 | 244038 | 121968.9988
38904.6487 | 1 | 0 | 38904.6487 | 1 | 0 | 2202.5 | 2349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6489 | 1 | 0 | 38904.6489 | 1 | 0 | 2219 | 2366 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6491 | 1 | 0 | 38904.6491 | 1 | 0 | 2236 | 2383 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6493 | 1 | 0 | 38904.6493 | 1 | 0 | 2252.5 | 2399.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6495 | 1 | 0 | 38904.6495 | 1 | 0 | 2269.5 | 2416.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6497 | 1 | 0 | 38904.6497 | 1 | 0 | 2286.5 | 2433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6499 | 1 | 0 | 38904.6499 | 1 | 0 | 2303 | 2450 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6501 | 1 | 0 | 38904.6501 | 1 | 0 | 2320 | 2467 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38904.6503 | 2 | 11 | 38904.6503 | 2 | 4 | 2336.5 | 2483.5 | 0.1221 | 0.67155 | 0.1221 | 0.2442 | 0.001221 | 0.0067155 | 0.001221 | 0.002442 | 0.0054945 | 0.001221 | 27131.2093 | 122874.7818 | 22058.23
38904.6505 | 4 | 17 | 38904.6505 | 3 | 12 | 2353.5 | 2500.5 | 0.2442 | 1.0379 | 0.18315 | 0.7326 | 0.002442 | 0.010379 | 0.0018315 | 0.007326 | 0.0079365 | 0.0054945 | 18839.3646 | 27286.2261 | 14185.5415
38904.6507 | 5 | 17 | 38904.6507 | 4 | 14 | 2370.5 | 2517.5 | 0.30525 | 1.0379 | 0.2442 | 0.8547 | 0.0030525 | 0.010379 | 0.002442 | 0.008547 | 0.007326 | 0.006105 | 20421.0452 | 24542.0523 | 14173.8936
38904.6509 | 6 | 18 | 38904.6509 | 57 | 45 | 2387 | 2534 | 0.3663 | 1.0989 | 3.4799 | 2.7473 | 0.003663 | 0.010989 | 0.034799 | 0.027473 | 0.007326 | 0.007326 | 20446.3546 | 20241.0682 | 13363.8654
38904.6511 | 287 | 265 | 38904.6511 | 210 | 149 | 2404 | 2551 | 17.5214 | 16.1783 | 12.8205 | 9.0965 | 0.17521 | 0.16178 | 0.12821 | 0.090965 | 0.013431 | 0.037241 | 14480.496 | 3720.7632 | 694.3131
38904.6513 | 1124 | 1046 | 38904.6513 | 948 | 861 | 2420.5 | 2567.5 | 68.6203 | 63.8584 | 57.8755 | 52.5641 | 0.6862 | 0.63858 | 0.57875 | 0.52564 | 0.047619 | 0.053114 | 4186.3198 | 2247.9487 | 24.8396
38904.6514 | 1206 | 1125 | 38904.6515 | 1200 | 1133 | 2437.5 | 2584.5 | 73.6264 | 68.6813 | 73.2601 | 69.1697 | 0.73626 | 0.68681 | 0.7326 | 0.6917 | 0.049451 | 0.040904 | 1028.5311 | 2876.4218 | 9.4819
38904.6516 | 1129 | 1107 | 38904.6517 | 936 | 900 | 2454.5 | 2601.5 | 68.9255 | 67.5824 | 57.1429 | 54.9451 | 0.68926 | 0.67582 | 0.57143 | 0.54945 | 0.013431 | 0.021978 | 14543.8515 | 8530.876 | 18.3379
38904.6518 | 1163 | 1133 | 38904.6519 | 1041 | 952 | 2471 | 2618 | 71.0012 | 69.1697 | 63.5531 | 58.1197 | 0.71001 | 0.6917 | 0.63553 | 0.5812 | 0.018315 | 0.054335 | 1209.6805 | 1497.1099 | 12.028
38904.652 | 1197 | 1132 | 38904.652 | 1095 | 1081 | 2488 | 2635 | 73.0769 | 69.1087 | 66.8498 | 65.9951 | 0.73077 | 0.69109 | 0.6685 | 0.65995 | 0.039683 | 0.008547 | 630.3016 | 854.8162 | 8.8878
38904.6522 | 1049 | 954 | 38904.6522 | 1181 | 1070 | 2504.5 | 2651.5 | 64.0415 | 58.2418 | 72.1001 | 65.3236 | 0.64042 | 0.58242 | 0.721 | 0.65324 | 0.057998 | 0.067766 | 5303.7321 | 1387.6936 | 42.863
38904.6524 | 937 | 864 | 38904.6524 | 1065 | 975 | 2521.5 | 2668.5 | 57.2039 | 52.7473 | 65.0183 | 59.5238 | 0.57204 | 0.52747 | 0.65018 | 0.59524 | 0.044567 | 0.054945 | 5406.8172 | 1912.5099 | 70.4352
38904.6526 | 1211 | 1115 | 38904.6526 | 1148 | 1120 | 2538.5 | 2685.5 | 73.9316 | 68.0708 | 70.0855 | 68.3761 | 0.73932 | 0.68071 | 0.70085 | 0.68376 | 0.058608 | 0.017094 | 368.5522 | 468.7996 | 8.5287
38904.6528 | 1042 | 939 | 38904.6528 | 1210 | 1091 | 2555 | 2702 | 63.6142 | 57.326 | 73.8706 | 66.6056 | 0.63614 | 0.57326 | 0.73871 | 0.66606 | 0.062882 | 0.07265 | 4629.9984 | 1290.2641 | 45.5022
38904.653 | 1010 | 889 | 38904.653 | 952 | 977 | 2572 | 2719 | 61.6606 | 54.2735 | 58.1197 | 59.6459 | 0.61661 | 0.54274 | 0.5812 | 0.59646 | 0.073871 | 0.015263 | 799.6176 | 1532.5457 | 57.273
38904.6532 | 1191 | 1077 | 38904.6532 | 1053 | 1072 | 2588.5 | 2735.5 | 72.7106 | 65.7509 | 64.2857 | 65.4457 | 0.72711 | 0.65751 | 0.64286 | 0.65446 | 0.069597 | 0.0116 | 421.9206 | 590.6084 | 13.7674
38904.6534 | 1101 | 985 | 38904.6534 | 1024 | 916 | 2605.5 | 2752.5 | 67.2161 | 60.1343 | 62.5153 | 55.9219 | 0.67216 | 0.60134 | 0.62515 | 0.55922 | 0.070818 | 0.065934 | 1718.8752 | 2590.7461 | 34.7383
38904.6536 | 1106 | 1075 | 38904.6536 | 1046 | 1052 | 2622.5 | 2769.5 | 67.5214 | 65.6288 | 63.8584 | 64.2247 | 0.67521 | 0.65629 | 0.63858 | 0.64225 | 0.018926 | 0.003663 | 1990.0207 | 2977.5239 | 23.4344
38904.6538 | 1200 | 1120 | 38904.6538 | 1208 | 1119 | 2639 | 2786 | 73.2601 | 68.3761 | 73.7485 | 68.315 | 0.7326 | 0.68376 | 0.73748 | 0.68315 | 0.04884 | 0.054335 | 27517.1617 | 1483.6656 | 10.1532
38904.654 | 1211 | 1094 | 38904.654 | 1057 | 935 | 2656 | 2803 | 73.9316 | 66.7888 | 64.5299 | 57.0818 | 0.73932 | 0.66789 | 0.6453 | 0.57082 | 0.071429 | 0.074481 | 2387.0772 | 1671.3356 | 11.7624
38904.6542 | 131 | 119 | 38904.6542 | 315 | 15 | 2672.5 | 2819.5 | 7.9976 | 7.265 | 19.2308 | 0.91575 | 0.079976 | 0.07265 | 0.19231 | 0.0091575 | 0.007326 | 0.18315 | 48224.9694 | 1650.6772 | 1736.3082
38904.6544 | 7 | 18 | 38904.6544 | 2374 | 18 | 2689.5 | 2836.5 | 0.42735 | 1.0989 | 144.9328 | 1.0989 | 0.0042735 | 0.010989 | 1.4493 | 0.010989 | 0.0067155 | 1.4383 | 392.8894 | 2.9576 | 385.6278
38904.6546 | 8 | 17 | 38904.6546 | 2031 | 17 | 2706.5 | 2853.5 | 0.4884 | 1.0379 | 123.9927 | 1.0379 | 0.004884 | 0.010379 | 1.2399 | 0.010379 | 0.0054945 | 1.2295 | 3268.408 | 25.9734 | 2930.667
38904.6547 | 20 | 14 | 38904.6548 | 2036 | 14 | 2723 | 2870 | 1.221 | 0.8547 | 124.2979 | 0.8547 | 0.01221 | 0.008547 | 1.243 | 0.008547 | 0.003663 | 1.2344 | 3792.6791 | 24.2032 | 3350.8657
38904.6549 | 7 | 10 | 38904.655 | 2022 | 9 | 2740 | 2887 | 0.42735 | 0.6105 | 123.4432 | 0.54945 | 0.0042735 | 0.006105 | 1.2344 | 0.0054945 | 0.0018315 | 1.2289 | 5409.3252 | 23.8076 | 4661.9649
38904.6551 | 7 | 8 | 38904.6552 | 1994 | 8 | 2756.5 | 2903.5 | 0.42735 | 0.4884 | 121.7338 | 0.4884 | 0.0042735 | 0.004884 | 1.2173 | 0.004884 | 0.0006105 | 1.2125 | 7053.0129 | 23.8696 | 5844.5212
38904.6553 | 8 | 6 | 38904.6553 | 2198 | 6 | 2773.5 | 2920.5 | 0.4884 | 0.3663 | 134.188 | 0.3663 | 0.004884 | 0.003663 | 1.3419 | 0.003663 | 0.001221 | 1.3382 | 4675.79 | 11.9899 | 4331.3497
38904.6555 | 7 | 6 | 38904.6555 | 2374 | 6 | 2790.5 | 2937.5 | 0.42735 | 0.3663 | 144.9328 | 0.3663 | 0.0042735 | 0.003663 | 1.4493 | 0.003663 | 0.0006105 | 1.4457 | 1159.7265 | 2.8721 | 1129.953
38904.6557 | 6 | 5 | 38904.6557 | 1996 | 5 | 2807 | 2954 | 0.3663 | 0.30525 | 121.8559 | 0.30525 | 0.003663 | 0.0030525 | 1.2186 | 0.0030525 | 0.0006105 | 1.2155 | 11405.7612 | 24.5674 | 9586.469
38904.6559 | 8 | 3 | 38904.6559 | 1890 | 4 | 2823.5 | 2970.5 | 0.4884 | 0.18315 | 115.3846 | 0.2442 | 0.004884 | 0.0018315 | 1.1538 | 0.002442 | 0.0030525 | 1.1514 | 46248.1495 | 1146.9087 | 74515.586
38904.6561 | 8 | 4 | 38904.6561 | 1936 | 4 | 2840.5 | 2987.5 | 0.4884 | 0.2442 | 118.1929 | 0.2442 | 0.004884 | 0.002442 | 1.1819 | 0.002442 | 0.002442 | 1.1795 | 21550.3355 | 54.8576 | 21514.911
38904.6563 | 1130 | 3 | 38904.6563 | 1987 | 3 | 2857.5 | 3004.5 | 68.9866 | 0.18315 | 121.3065 | 0.18315 | 0.68987 | 0.0018315 | 1.2131 | 0.0018315 | 0.68803 | 1.2112 | 117.7268 | 22.9317 | 8135.5059
38904.6565 | 6 | 2 | 38904.6565 | 2097 | 2 | 2874.5 | 3021.5 | 0.3663 | 0.1221 | 128.022 | 0.1221 | 0.003663 | 0.001221 | 1.2802 | 0.001221 | 0.002442 | 1.279 | 29820.3779 | 47.9981 | 39459.1618
38904.6567 | 6 | 2 | 38904.6567 | 1967 | 2 | 2891 | 3038 | 0.3663 | 0.1221 | 120.0855 | 0.1221 | 0.003663 | 0.001221 | 1.2009 | 0.001221 | 0.002442 | 1.1996 | 56841.4727 | 702.9568 | 106516.3796
38904.6569 | 6 | 2 | 38904.6569 | 1872 | 2 | 2908 | 3055 | 0.3663 | 0.1221 | 114.2857 | 0.1221 | 0.003663 | 0.001221 | 1.1429 | 0.001221 | 0.002442 | 1.1416 | 94815.154 | 139.719 | 70914.1619
38904.6571 | 6 | 1 | 38904.6571 | 1971 | 1 | 2924.5 | 3071.5 | 0.3663 | 0.06105 | 120.3297 | 0.06105 | 0.003663 | 0.0006105 | 1.2033 | 0.0006105 | 0.0030525 | 1.2027 | 299961.5199 | 23.8772 | 46922.3572
38904.6573 | 5 | 2 | 38904.6573 | 1986 | 2 | 2941.5 | 3088.5 | 0.30525 | 0.1221 | 121.2454 | 0.1221 | 0.0030525 | 0.001221 | 1.2125 | 0.001221 | 0.0018315 | 1.2112 | 42641.5996 | 73.7022 | 51645.63
38904.6575 | 6 | 1 | 38904.6575 | 2019 | 1 | 2958.5 | 3105.5 | 0.3663 | 0.06105 | 123.2601 | 0.06105 | 0.003663 | 0.0006105 | 1.2326 | 0.0006105 | 0.0030525 | 1.232 | 1095479.0249 | 20.9306 | 42134.1538
38904.6577 | 6 | 1 | 38904.6577 | 2109 | 2 | 2975 | 3122 | 0.3663 | 0.06105 | 128.7546 | 0.1221 | 0.003663 | 0.0006105 | 1.2875 | 0.001221 | 0.0030525 | 1.2863 | 181862.4139 | 27.3159 | 52230.1991
38904.6579 | 6 | 1 | 38904.6579 | 2420 | 1 | 2991.5 | 3138.5 | 0.3663 | 0.06105 | 147.7411 | 0.06105 | 0.003663 | 0.0006105 | 1.4774 | 0.0006105 | 0.0030525 | 1.4768 | 2251.9538 | 0.96951 | 2337.4865
38904.6581 | 6 | 1 | 38904.6581 | 2228 | 1 | 3008.5 | 3155.5 | 0.3663 | 0.06105 | 136.0195 | 0.06105 | 0.003663 | 0.0006105 | 1.3602 | 0.0006105 | 0.0030525 | 1.3596 | 44794.4474 | 228.943 | 169431.8683
38904.6583 | 6 | 1 | 38904.6583 | 2088 | 1 | 3025.5 | 3172.5 | 0.3663 | 0.06105 | 127.4725 | 0.06105 | 0.003663 | 0.0006105 | 1.2747 | 0.0006105 | 0.0030525 | 1.2741 | 268857.7271 | 24.4249 | 47787.5203
38904.6584 | 5 | 1 | 38904.6585 | 2336 | 1 | 3042 | 3189 | 0.30525 | 0.06105 | 142.6129 | 0.06105 | 0.0030525 | 0.0006105 | 1.4261 | 0.0006105 | 0.002442 | 1.4255 | 13417.6853 | 7.0632 | 16066.6575
38904.6586 | 149 | 1 | 38904.6587 | 1926 | 1 | 3059 | 3206 | 9.0965 | 0.06105 | 117.5824 | 0.06105 | 0.090965 | 0.0006105 | 1.1758 | 0.0006105 | 0.090354 | 1.1752 | 1589.0062 | 26.7739 | 48392.5405
38904.6588 | 5 | 1 | 38904.6588 | 2224 | 1 | 3075.5 | 3222.5 | 0.30525 | 0.06105 | 135.7753 | 0.06105 | 0.0030525 | 0.0006105 | 1.3578 | 0.0006105 | 0.002442 | 1.3571 | 39130.1892 | 44.9167 | 75484.2124
38904.659 | 5 | 1 | 38904.659 | 2012 | 1 | 3092.5 | 3239.5 | 0.30525 | 0.06105 | 122.8327 | 0.06105 | 0.0030525 | 0.0006105 | 1.2283 | 0.0006105 | 0.002442 | 1.2277 | 356457.6272 | 30.1522 | 56420.219
38904.6592 | 5 | 1 | 38904.6592 | 2248 | 1 | 3109.5 | 3256.5 | 0.30525 | 0.06105 | 137.2405 | 0.06105 | 0.0030525 | 0.0006105 | 1.3724 | 0.0006105 | 0.002442 | 1.3718 | 31975.0634 | 27.6272 | 52718.1292
38904.6594 | 6 | 1 | 38904.6594 | 2391 | 1 | 3126 | 3273 | 0.3663 | 0.06105 | 145.9707 | 0.06105 | 0.003663 | 0.0006105 | 1.4597 | 0.0006105 | 0.0030525 | 1.4591 | 5738.4334 | 2.671 | 6332.9664
38904.6596 | 6 | 1 | 38904.6596 | 1899 | 1 | 3143 | 3290 | 0.3663 | 0.06105 | 115.9341 | 0.06105 | 0.003663 | 0.0006105 | 1.1593 | 0.0006105 | 0.0030525 | 1.1587 | 162292.7146 | 28.5764 | 54104.6623
38904.6598 | 5 | 1 | 38904.6598 | 1924 | 1 | 3159.5 | 3306.5 | 0.30525 | 0.06105 | 117.4603 | 0.06105 | 0.0030525 | 0.0006105 | 1.1746 | 0.0006105 | 0.002442 | 1.174 | 860314.8269 | 26.9048 | 51631.9985
38904.66 | 5 | 1 | 38904.66 | 1917 | 1 | 3176.5 | 3323.5 | 0.30525 | 0.06105 | 117.033 | 0.06105 | 0.0030525 | 0.0006105 | 1.1703 | 0.0006105 | 0.002442 | 1.1697 | 703827.6468 | 27.3685 | 52330.5649
38904.6602 | 5 | 1 | 38904.6602 | 2375 | 1 | 3193.5 | 3340.5 | 0.30525 | 0.06105 | 144.9939 | 0.06105 | 0.0030525 | 0.0006105 | 1.4499 | 0.0006105 | 0.002442 | 1.4493 | 7670.2603 | 3.6018 | 8466.7697
38904.6604 | 5 | 1 | 38904.6604 | 2011 | 1 | 3210 | 3357 | 0.30525 | 0.06105 | 122.7717 | 0.06105 | 0.0030525 | 0.0006105 | 1.2277 | 0.0006105 | 0.002442 | 1.2271 | 363480.3884 | 30.0327 | 56248.1351
38904.6606 | 5 | 1 | 38904.6606 | 2278 | 1 | 3227 | 3374 | 0.30525 | 0.06105 | 139.072 | 0.06105 | 0.0030525 | 0.0006105 | 1.3907 | 0.0006105 | 0.002442 | 1.3901 | 24518.6121 | 16.8439 | 35107.8187
38904.6608 | 5 | 0 | 38904.6608 | 2224 | 1 | 3243.5 | 3390.5 | 0.30525 | 0 | 135.7753 | 0.06105 | 0.0030525 | 0 | 1.3578 | 0.0006105 | 0.0030525 | 1.3571 | 48727.6 | 9.8237 | 48727.5969
38904.661 | 4 | 1 | 38904.661 | 2325 | 1 | 3260.5 | 3407.5 | 0.2442 | 0.06105 | 141.9414 | 0.06105 | 0.002442 | 0.0006105 | 1.4194 | 0.0006105 | 0.0018315 | 1.4188 | 14363.6149 | 7.1586 | 16276.033
38904.6612 | 6 | 1 | 38904.6612 | 2168 | 1 | 3277.5 | 3424.5 | 0.3663 | 0.06105 | 132.3565 | 0.06105 | 0.003663 | 0.0006105 | 1.3236 | 0.0006105 | 0.0030525 | 1.323 | 83212.4965 | 48.2323 | 79210.6163
38904.6614 | 4 | 1 | 38904.6614 | 2266 | 1 | 3294 | 3441 | 0.2442 | 0.06105 | 138.3394 | 0.06105 | 0.002442 | 0.0006105 | 1.3834 | 0.0006105 | 0.0018315 | 1.3828 | 24583.1582 | 14.4617 | 30782.4416
38904.6616 | 5 | 1 | 38904.6616 | 2063 | 0 | 3311 | 3458 | 0.30525 | 0.06105 | 125.9463 | 0 | 0.0030525 | 0.0006105 | 1.2595 | 0 | 0.002442 | 1.2595 | 167772.7059 | 39.2494 | 68644.6183
38904.6617 | 5 | 1 | 38904.6618 | 2425 | 1 | 3327.5 | 3474.5 | 0.30525 | 0.06105 | 148.0464 | 0.06105 | 0.0030525 | 0.0006105 | 1.4805 | 0.0006105 | 0.002442 | 1.4799 | 1692.0603 | 0.71434 | 1727.3552
38904.6619 | 5 | 0 | 38904.662 | 1971 | 1 | 3344.5 | 3491.5 | 0.30525 | 0 | 120.3297 | 0.06105 | 0.0030525 | 0 | 1.2033 | 0.0006105 | 0.0030525 | 1.2027 | 48727.6 | 23.9279 | 48727.5969
38904.6621 | 5 | 1 | 38904.6622 | 2115 | 1 | 3361.5 | 3508.5 | 0.30525 | 0.06105 | 129.1209 | 0.06105 | 0.0030525 | 0.0006105 | 1.2912 | 0.0006105 | 0.002442 | 1.2906 | 98355.5195 | 65.6649 | 96531.5763

## C2-4
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 150.2063 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38904.6217 | 1 | 0 | 38904.6217 | 1 | 0 | -135.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6219 | 1 | 0 | 38904.6219 | 1 | 0 | -118.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6221 | 1 | 0 | 38904.6221 | 1 | 0 | -101.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6222 | 1 | 0 | 38904.6223 | 1 | 0 | -85 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6224 | 2 | 0 | 38904.6225 | 1 | 0 | -68 | 79 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.6226 | 1 | 0 | 38904.6227 | 1 | 0 | -51.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6228 | 1 | 0 | 38904.6228 | 1 | 0 | -34.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.623 | 1 | 0 | 38904.623 | 1 | 0 | -18 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6232 | 1 | 0 | 38904.6232 | 1 | 0 | -1 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6234 | 1 | 0 | 38904.6234 | 1 | 0 | 16 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6236 | 1 | 0 | 38904.6236 | 2 | 0 | 32.5 | 179.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6238 | 1 | 0 | 38904.6238 | 1 | 0 | 49.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.624 | 1 | 0 | 38904.624 | 1 | 0 | 66.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6242 | 1 | 0 | 38904.6242 | 1 | 0 | 83 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6244 | 1 | 0 | 38904.6244 | 1 | 0 | 99.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6246 | 2 | 0 | 38904.6246 | 1 | 0 | 116.5 | 263.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.6248 | 2 | 0 | 38904.6248 | 1 | 0 | 133.5 | 280.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.625 | 1 | 0 | 38904.625 | 1 | 0 | 150.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6252 | 1 | 0 | 38904.6252 | 1 | 0 | 167 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6254 | 1 | 0 | 38904.6254 | 1 | 0 | 184 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6256 | 1 | 0 | 38904.6256 | 1 | 0 | 200.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6258 | 1 | 0 | 38904.6258 | 1 | 0 | 217.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6259 | 1 | 0 | 38904.626 | 1 | 0 | 234 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6261 | 1 | 0 | 38904.6262 | 1 | 0 | 251 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6263 | 1 | 0 | 38904.6264 | 1 | 0 | 268 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6265 | 1 | 0 | 38904.6265 | 1 | 0 | 284.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6267 | 1 | 0 | 38904.6267 | 1 | 0 | 301.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6269 | 1 | 0 | 38904.6269 | 1 | 0 | 318.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6271 | 1 | 0 | 38904.6271 | 1 | 0 | 335 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6273 | 1 | 0 | 38904.6273 | 1 | 0 | 351.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6275 | 1 | 0 | 38904.6275 | 1 | 0 | 368.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6277 | 1 | 0 | 38904.6277 | 1 | 0 | 385.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6279 | 1 | 0 | 38904.6279 | 1 | 0 | 402 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6281 | 1 | 0 | 38904.6281 | 1 | 0 | 419 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6283 | 2 | 0 | 38904.6283 | 1 | 0 | 435.5 | 582.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.6285 | 1 | 0 | 38904.6285 | 1 | 0 | 452.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6287 | 1 | 0 | 38904.6287 | 1 | 0 | 469.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6289 | 1 | 0 | 38904.6289 | 1 | 0 | 486 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6291 | 1 | 0 | 38904.6291 | 1 | 0 | 503 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6292 | 2 | 0 | 38904.6293 | 1 | 0 | 519.5 | 666.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.6294 | 1 | 0 | 38904.6295 | 1 | 0 | 536.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6296 | 1 | 0 | 38904.6297 | 1 | 0 | 553.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6298 | 1 | 0 | 38904.6298 | 1 | 0 | 570 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.63 | 1 | 0 | 38904.63 | 1 | 0 | 587 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6302 | 1 | 0 | 38904.6302 | 1 | 0 | 603.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6304 | 1 | 0 | 38904.6304 | 1 | 0 | 620.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6306 | 1 | 0 | 38904.6306 | 1 | 0 | 637.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6308 | 1 | 0 | 38904.6308 | 2 | 0 | 654 | 801 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.631 | 1 | 0 | 38904.631 | 1 | 0 | 671 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6312 | 1 | 0 | 38904.6312 | 1 | 0 | 687.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6314 | 1 | 0 | 38904.6314 | 1 | 0 | 704.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6316 | 1 | 0 | 38904.6316 | 1 | 0 | 721.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6318 | 1 | 0 | 38904.6318 | 1 | 0 | 738 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.632 | 1 | 0 | 38904.632 | 1 | 0 | 755 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6322 | 1 | 0 | 38904.6322 | 1 | 0 | 771.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6324 | 1 | 0 | 38904.6324 | 2 | 0 | 788.5 | 935.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6326 | 1 | 0 | 38904.6326 | 1 | 0 | 805.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6327 | 1 | 0 | 38904.6328 | 1 | 0 | 822 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6329 | 1 | 0 | 38904.633 | 1 | 0 | 839 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6331 | 1 | 0 | 38904.6331 | 1 | 0 | 855.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6333 | 1 | 0 | 38904.6333 | 1 | 0 | 872.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6335 | 1 | 0 | 38904.6335 | 1 | 0 | 889.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6337 | 1 | 0 | 38904.6337 | 1 | 0 | 906 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6339 | 1 | 0 | 38904.6339 | 1 | 0 | 923 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6341 | 1 | 0 | 38904.6341 | 1 | 0 | 939.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6343 | 1 | 0 | 38904.6343 | 1 | 0 | 956.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6345 | 1 | 0 | 38904.6345 | 1 | 0 | 973.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6347 | 1 | 0 | 38904.6347 | 1 | 0 | 990 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6349 | 1 | 0 | 38904.6349 | 1 | 0 | 1007 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6351 | 1 | 0 | 38904.6351 | 1 | 0 | 1023.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6353 | 1 | 0 | 38904.6353 | 1 | 0 | 1040.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6355 | 1 | 0 | 38904.6355 | 1 | 0 | 1057.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6357 | 1 | 0 | 38904.6357 | 1 | 0 | 1074 | 1221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6359 | 1 | 0 | 38904.6359 | 1 | 0 | 1091 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6361 | 1 | 0 | 38904.6361 | 2 | 0 | 1107.5 | 1254.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6363 | 1 | 0 | 38904.6363 | 1 | 0 | 1124.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6364 | 1 | 0 | 38904.6365 | 1 | 0 | 1141.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6366 | 1 | 0 | 38904.6367 | 1 | 0 | 1158 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6368 | 1 | 0 | 38904.6369 | 1 | 0 | 1175 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.637 | 1 | 0 | 38904.637 | 1 | 0 | 1191.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6372 | 1 | 0 | 38904.6372 | 1 | 0 | 1208.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6374 | 1 | 0 | 38904.6374 | 1 | 0 | 1225.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6376 | 1 | 0 | 38904.6376 | 1 | 0 | 1242 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6378 | 1 | 0 | 38904.6378 | 1 | 0 | 1259 | 1406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.638 | 1 | 0 | 38904.638 | 1 | 0 | 1275.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6382 | 1 | 0 | 38904.6382 | 1 | 0 | 1292.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6384 | 1 | 0 | 38904.6384 | 2 | 0 | 1309.5 | 1456.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6386 | 1 | 0 | 38904.6386 | 1 | 0 | 1326 | 1473 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6388 | 1 | 0 | 38904.6388 | 1 | 0 | 1342.5 | 1489.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.639 | 1 | 0 | 38904.639 | 1 | 0 | 1359.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6392 | 1 | 0 | 38904.6392 | 1 | 0 | 1376.5 | 1523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6394 | 1 | 0 | 38904.6394 | 2 | 0 | 1393.5 | 1540.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6395 | 1 | 0 | 38904.6396 | 1 | 0 | 1410 | 1557 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6397 | 1 | 0 | 38904.6398 | 1 | 0 | 1427 | 1574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6399 | 1 | 0 | 38904.64 | 1 | 0 | 1443.5 | 1590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6401 | 1 | 0 | 38904.6402 | 1 | 0 | 1460.5 | 1607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6403 | 1 | 0 | 38904.6403 | 1 | 0 | 1477 | 1624 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6405 | 1 | 1 | 38904.6405 | 1 | 0 | 1494 | 1641 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 604854998.44 | 245938 | 245738.0813
38904.6407 | 1 | 0 | 38904.6407 | 1 | 0 | 1511 | 1658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6409 | 1 | 0 | 38904.6409 | 1 | 0 | 1527.5 | 1674.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6411 | 1 | 0 | 38904.6411 | 1 | 0 | 1544.5 | 1691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6413 | 1 | 0 | 38904.6413 | 1 | 0 | 1561 | 1708 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6415 | 1 | 0 | 38904.6415 | 1 | 0 | 1578 | 1725 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6417 | 1 | 0 | 38904.6417 | 1 | 0 | 1595 | 1742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6419 | 1 | 0 | 38904.6419 | 1 | 0 | 1611.5 | 1758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6421 | 1 | 0 | 38904.6421 | 1 | 0 | 1628.5 | 1775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6423 | 1 | 0 | 38904.6423 | 1 | 0 | 1645 | 1792 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6425 | 1 | 0 | 38904.6425 | 1 | 0 | 1662 | 1809 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6427 | 1 | 0 | 38904.6427 | 1 | 0 | 1678.5 | 1825.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6429 | 1 | 0 | 38904.6429 | 1 | 0 | 1695.5 | 1842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6431 | 1 | 0 | 38904.6431 | 1 | 0 | 1712.5 | 1859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6432 | 1 | 0 | 38904.6433 | 1 | 0 | 1729 | 1876 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6434 | 1 | 0 | 38904.6435 | 1 | 0 | 1746 | 1893 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6436 | 1 | 0 | 38904.6436 | 1 | 0 | 1762.5 | 1909.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6438 | 1 | 0 | 38904.6438 | 1 | 0 | 1779.5 | 1926.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.644 | 1 | 0 | 38904.644 | 1 | 0 | 1796.5 | 1943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6442 | 2 | 0 | 38904.6442 | 1 | 0 | 1813 | 1960 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38904.6444 | 1 | 0 | 38904.6444 | 1 | 0 | 1830 | 1977 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6446 | 1 | 0 | 38904.6446 | 1 | 0 | 1846.5 | 1993.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6448 | 1 | 0 | 38904.6448 | 1 | 0 | 1863.5 | 2010.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.645 | 1 | 0 | 38904.645 | 1 | 0 | 1880.5 | 2027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6452 | 1 | 0 | 38904.6452 | 1 | 0 | 1897 | 2044 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6454 | 1 | 0 | 38904.6454 | 1 | 0 | 1914 | 2061 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6456 | 1 | 0 | 38904.6456 | 1 | 0 | 1930.5 | 2077.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6458 | 1 | 0 | 38904.6458 | 1 | 0 | 1947.5 | 2094.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.646 | 1 | 0 | 38904.646 | 1 | 0 | 1964.5 | 2111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6462 | 1 | 0 | 38904.6462 | 1 | 0 | 1981 | 2128 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6464 | 1 | 0 | 38904.6464 | 1 | 0 | 1998 | 2145 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6466 | 1 | 0 | 38904.6466 | 1 | 0 | 2014.5 | 2161.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6467 | 1 | 0 | 38904.6468 | 1 | 0 | 2031.5 | 2178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6469 | 1 | 0 | 38904.647 | 1 | 0 | 2048.5 | 2195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6471 | 1 | 0 | 38904.6472 | 1 | 0 | 2065 | 2212 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6473 | 1 | 0 | 38904.6473 | 1 | 0 | 2082 | 2229 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6475 | 1 | 0 | 38904.6475 | 1 | 0 | 2098.5 | 2245.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6477 | 1 | 0 | 38904.6477 | 1 | 0 | 2115.5 | 2262.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6479 | 1 | 0 | 38904.6479 | 1 | 0 | 2132.5 | 2279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6481 | 1 | 0 | 38904.6481 | 1 | 0 | 2149 | 2296 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6483 | 1 | 0 | 38904.6483 | 1 | 0 | 2166 | 2313 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6485 | 1 | 0 | 38904.6485 | 1 | 0 | 2182.5 | 2329.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6487 | 1 | 0 | 38904.6487 | 1 | 0 | 2199.5 | 2346.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6489 | 1 | 0 | 38904.6489 | 1 | 0 | 2216.5 | 2363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6491 | 1 | 0 | 38904.6491 | 1 | 0 | 2233 | 2380 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6493 | 1 | 0 | 38904.6493 | 1 | 0 | 2250 | 2397 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6495 | 1 | 0 | 38904.6495 | 2 | 0 | 2266.5 | 2413.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245938 | 122919 | 245937.9994
38904.6497 | 1 | 0 | 38904.6497 | 1 | 0 | 2283.5 | 2430.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.6499 | 1 | 0 | 38904.6499 | 1 | 0 | 2300.5 | 2447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38904.65 | 1 | 0 | 38904.6501 | 117 | 90 | 2317 | 2464 | 0.06105 | 0 | 7.1429 | 5.4945 | 0.0006105 | 0 | 0.071429 | 0.054945 | 0.0006105 | 0.016484 | 245938 | 9012.5185 | 245937.9994
38904.6502 | 485 | 451 | 38904.6503 | 719 | 717 | 2334 | 2481 | 29.6093 | 27.5336 | 43.895 | 43.7729 | 0.29609 | 0.27534 | 0.43895 | 0.43773 | 0.020757 | 0.001221 | 5345.2097 | 15256.6878 | 335.799
38904.6504 | 942 | 957 | 38904.6505 | 1005 | 1024 | 2350.5 | 2497.5 | 57.5092 | 58.4249 | 61.3553 | 62.5153 | 0.57509 | 0.58425 | 0.61355 | 0.62515 | 0.0091575 | 0.0116 | 33715.8178 | 9117.2943 | 58.024
38904.6506 | 1099 | 1067 | 38904.6506 | 918 | 1004 | 2367.5 | 2514.5 | 67.094 | 65.1404 | 56.044 | 61.2943 | 0.67094 | 0.6514 | 0.56044 | 0.61294 | 0.019536 | 0.052503 | 2425.3671 | 4421.7194 | 26.9793
38904.6508 | 964 | 976 | 38904.6508 | 1018 | 1039 | 2384.5 | 2531.5 | 58.8523 | 59.5849 | 62.149 | 63.431 | 0.58852 | 0.59585 | 0.62149 | 0.63431 | 0.007326 | 0.012821 | 35899.8 | 12462.034 | 52.8932
38904.651 | 1063 | 1090 | 38904.651 | 1044 | 1079 | 2401 | 2548 | 64.8962 | 66.5446 | 63.7363 | 65.873 | 0.64896 | 0.66545 | 0.63736 | 0.65873 | 0.016484 | 0.021368 | 870486.7596 | 4061.1828 | 27.5223
38904.6512 | 949 | 877 | 38904.6512 | 1155 | 1078 | 2418 | 2565 | 57.9365 | 53.5409 | 70.5128 | 65.812 | 0.57937 | 0.53541 | 0.70513 | 0.65812 | 0.043956 | 0.047009 | 3883.5333 | 2650.9606 | 69.7058
38904.6514 | 1072 | 1073 | 38904.6514 | 1166 | 1068 | 2434.5 | 2581.5 | 65.4457 | 65.5067 | 71.1844 | 65.2015 | 0.65446 | 0.65507 | 0.71184 | 0.65201 | 0.0006105 | 0.059829 | 626.9302 | 486.7165 | 24.3827
38904.6516 | 982 | 893 | 38904.6516 | 1134 | 1092 | 2451.5 | 2598.5 | 59.9512 | 54.5177 | 69.2308 | 66.6667 | 0.59951 | 0.54518 | 0.69231 | 0.66667 | 0.054335 | 0.025641 | 1223.883 | 2808.6863 | 63.2984
38904.6518 | 1025 | 939 | 38904.6518 | 1136 | 1098 | 2468.5 | 2615.5 | 62.5763 | 57.326 | 69.3529 | 67.033 | 0.62576 | 0.57326 | 0.69353 | 0.67033 | 0.052503 | 0.023199 | 1112.2804 | 2181.2661 | 50.5454
38904.652 | 1101 | 1094 | 38904.652 | 998 | 905 | 2485 | 2632 | 67.2161 | 66.7888 | 60.928 | 55.2503 | 0.67216 | 0.66789 | 0.60928 | 0.5525 | 0.0042735 | 0.056777 | 1090.4939 | 929.8192 | 21.9022
38904.6522 | 1175 | 1082 | 38904.6522 | 1056 | 951 | 2502 | 2649 | 71.7338 | 66.0562 | 64.4689 | 58.0586 | 0.71734 | 0.66056 | 0.64469 | 0.58059 | 0.056777 | 0.064103 | 4566.479 | 1668.4185 | 17.7338
38904.6524 | 1150 | 1067 | 38904.6524 | 1092 | 1000 | 2518.5 | 2665.5 | 70.2076 | 65.1404 | 66.6667 | 61.0501 | 0.70208 | 0.6514 | 0.66667 | 0.6105 | 0.050672 | 0.056166 | 4711.3902 | 1933.4271 | 21.688
38904.6526 | 1005 | 976 | 38904.6526 | 963 | 866 | 2535.5 | 2682.5 | 61.3553 | 59.5849 | 58.7912 | 52.8694 | 0.61355 | 0.59585 | 0.58791 | 0.52869 | 0.017705 | 0.059219 | 2603.1092 | 3626.9997 | 47.7989
38904.6528 | 916 | 941 | 38904.6528 | 997 | 895 | 2552.5 | 2699.5 | 55.9219 | 57.4481 | 60.8669 | 54.6398 | 0.55922 | 0.57448 | 0.60867 | 0.5464 | 0.015263 | 0.062271 | 2387.0025 | 2370.3036 | 61.5255
38904.653 | 1139 | 1043 | 38904.653 | 1129 | 1021 | 2569 | 2716 | 69.536 | 63.6752 | 68.9255 | 62.3321 | 0.69536 | 0.63675 | 0.68926 | 0.62332 | 0.058608 | 0.065934 | 4577.6235 | 1553.6108 | 25.0763
38904.6532 | 980 | 871 | 38904.6532 | 1151 | 1028 | 2586 | 2733 | 59.8291 | 53.1746 | 70.2686 | 62.7595 | 0.59829 | 0.53175 | 0.70269 | 0.62759 | 0.066545 | 0.075092 | 2930.6237 | 1489.2494 | 65.561
38904.6534 | 923 | 941 | 38904.6534 | 1195 | 1089 | 2602.5 | 2749.5 | 56.3492 | 57.4481 | 72.9548 | 66.4835 | 0.56349 | 0.57448 | 0.72955 | 0.66484 | 0.010989 | 0.064713 | 1196.0906 | 851.3238 | 56.7153
38904.6536 | 1179 | 1065 |  | 1112 | 1003 | 2619 | 2766 | 71.978 | 65.0183 | 67.8877 | 61.2332 | 0.71978 | 0.65018 | 0.67888 | 0.61233 | 0.069597 | 0.066545 | 1752.821 | 2604.1584 | 19.566
38904.6537 | 1037 | 925 | 38904.6538 | 1028 | 916 | 2636.5 | 2783.5 | 63.3089 | 56.4713 | 62.7595 | 55.9219 | 0.63309 | 0.56471 | 0.62759 | 0.55922 | 0.068376 | 0.068376 | 2096.7679 | 2096.7679 | 51.4263
38904.6539 | 1023 | 856 | 38904.654 | 1008 | 1011 | 2653 | 2800 | 62.4542 | 52.2589 | 61.5385 | 61.7216 | 0.62454 | 0.52259 | 0.61538 | 0.61722 | 0.10195 | 0.0018315 | 509.2961 | 742.8701 | 59.8603
38904.6541 | 1182 | 1058 | 38904.6541 | 1137 | 999 | 2669.5 | 2816.5 | 72.1612 | 64.591 | 69.4139 | 60.989 | 0.72161 | 0.64591 | 0.69414 | 0.60989 | 0.075702 | 0.084249 | 3508.3521 | 1208.2893 | 19.2377
38904.6543 | 1857 | 19 | 38904.6543 | 2154 | 18 | 2686.5 | 2833.5 | 113.37 | 1.16 | 131.5018 | 1.0989 | 1.1337 | 0.0116 | 1.315 | 0.010989 | 1.1221 | 1.304 | 35.3123 | 14.6943 | 394.0477
38904.6545 | 2186 | 18 | 38904.6545 | 2362 | 18 | 2703.5 | 2850.5 | 133.4554 | 1.0989 | 144.2002 | 1.0989 | 1.3346 | 0.010989 | 1.442 | 0.010989 | 1.3236 | 1.431 | 15.5875 | 4.4146 | 60.2199
38904.6547 | 2103 | 15 | 38904.6547 | 2017 | 14 | 2720.5 | 2867.5 | 128.3883 | 0.91575 | 123.138 | 0.8547 | 1.2839 | 0.0091575 | 1.2314 | 0.008547 | 1.2747 | 1.2228 | 17.6666 | 23.0476 | 427.5337
38904.6549 | 2089 | 9 | 38904.6549 | 2429 | 10 | 2737 | 2884 | 127.5336 | 0.54945 | 148.2906 | 0.6105 | 1.2753 | 0.0054945 | 1.4829 | 0.006105 | 1.2698 | 1.4768 | 26.5841 | 1.3177 | 52.3673
38904.6551 | 2268 | 8 | 38904.6551 | 1952 | 7 | 2754 | 2901 | 138.4615 | 0.4884 | 119.1697 | 0.42735 | 1.3846 | 0.004884 | 1.1917 | 0.0042735 | 1.3797 | 1.1874 | 8.6243 | 27.276 | 493.922
38904.6553 | 2190 | 6 | 38904.6553 | 2081 | 7 | 2770.5 | 2917.5 | 133.6996 | 0.3663 | 127.0452 | 0.42735 | 1.337 | 0.003663 | 1.2705 | 0.0042735 | 1.3333 | 1.2662 | 12.5637 | 18.7972 | 697.2098
38904.6555 | 2078 | 6 | 38904.6555 | 2147 | 7 | 2787.5 | 2934.5 | 126.862 | 0.3663 | 131.0745 | 0.42735 | 1.2686 | 0.003663 | 1.3107 | 0.0042735 | 1.265 | 1.3065 | 18.8203 | 14.9029 | 813.6098
38904.6557 | 2043 | 5 | 38904.6557 | 1970 | 5 | 2804.5 | 2951.5 | 124.7253 | 0.30525 | 120.2686 | 0.30525 | 1.2473 | 0.0030525 | 1.2027 | 0.0030525 | 1.2442 | 1.1996 | 20.6807 | 25.2666 | 1663.5626
38904.6559 | 1999 | 4 | 38904.6559 | 1993 | 4 | 2821 | 2968 | 122.0391 | 0.2442 | 121.6728 | 0.2442 | 1.2204 | 0.002442 | 1.2167 | 0.002442 | 1.2179 | 1.2143 | 23.3241 | 23.7026 | 2190.9602
38904.6561 | 2372 | 4 | 38904.6561 | 2218 | 4 | 2837.5 | 2984.5 | 144.8107 | 0.2442 | 135.409 | 0.2442 | 1.4481 | 0.002442 | 1.3541 | 0.002442 | 1.4457 | 1.3516 | 3.7879 | 11.4959 | 217.5024
38904.6563 | 2377 | 3 | 38904.6563 | 2100 | 3 | 2854.5 | 3001.5 | 145.116 | 0.18315 | 128.2051 | 0.18315 | 1.4512 | 0.0018315 | 1.2821 | 0.0018315 | 1.4493 | 1.2802 | 3.5372 | 17.9099 | 406.9762
38904.6565 | 1914 | 2 | 38904.6565 | 1993 | 2 | 2871.5 | 3018.5 | 116.8498 | 0.1221 | 121.6728 | 0.1221 | 1.1685 | 0.001221 | 1.2167 | 0.001221 | 1.1673 | 1.2155 | 28.7038 | 23.5571 | 5189.505
38904.6567 | 2335 | 2 | 38904.6567 | 2436 | 3 | 2888 | 3035 | 142.5519 | 0.1221 | 148.7179 | 0.18315 | 1.4255 | 0.001221 | 1.4872 | 0.0018315 | 1.4243 | 1.4853 | 5.8654 | 1.0236 | 62.5044
38904.6569 | 2021 | 2 | 38904.6569 | 2137 | 2 | 2905 | 3052 | 123.3822 | 0.1221 | 130.464 | 0.1221 | 1.2338 | 0.001221 | 1.3046 | 0.001221 | 1.2326 | 1.3034 | 21.9049 | 15.2117 | 2887.4138
38904.657 | 1871 | 2 | 38904.6571 | 1946 | 2 | 2921.5 | 3068.5 | 114.2247 | 0.1221 | 118.8034 | 0.1221 | 1.1422 | 0.001221 | 1.188 | 0.001221 | 1.141 | 1.1868 | 31.6621 | 26.5461 | 6160.863
38904.6572 | 2223 | 1 | 38904.6573 | 2255 | 2 | 2938.5 | 3085.5 | 135.7143 | 0.06105 | 137.6679 | 0.1221 | 1.3571 | 0.0006105 | 1.3767 | 0.001221 | 1.3565 | 1.3755 | 10.7357 | 9.1919 | 1989.8642
38904.6574 | 2021 | 1 | 38904.6575 | 2419 | 1 | 2955.5 | 3102.5 | 123.3822 | 0.06105 | 147.6801 | 0.06105 | 1.2338 | 0.0006105 | 1.4768 | 0.0006105 | 1.2332 | 1.4762 | 22.3982 | 1.7145 | 738.9324
38904.6576 | 1912 | 2 | 38904.6577 | 1880 | 2 | 2972.5 | 3119.5 | 116.7277 | 0.1221 | 114.7741 | 0.1221 | 1.1673 | 0.001221 | 1.1477 | 0.001221 | 1.1661 | 1.1465 | 28.8082 | 31.0188 | 6467.7973
38904.6578 | 2432 | 1 | 38904.6578 | 2444 | 2 | 2989 | 3136 | 148.4737 | 0.06105 | 149.2063 | 0.1221 | 1.4847 | 0.0006105 | 1.4921 | 0.001221 | 1.4841 | 1.4908 | 1.2383 | 0.71827 | 19.5259
38904.658 | 1918 | 1 | 38904.658 | 1977 | 1 | 3005.5 | 3152.5 | 117.094 | 0.06105 | 120.696 | 0.06105 | 1.1709 | 0.0006105 | 1.207 | 0.0006105 | 1.1703 | 1.2063 | 28.3535 | 24.5063 | 10655.8598
38904.6582 | 2046 | 1 | 38904.6582 | 1972 | 1 | 3022.5 | 3169.5 | 124.9084 | 0.06105 | 120.3907 | 0.06105 | 1.2491 | 0.0006105 | 1.2039 | 0.0006105 | 1.2485 | 1.2033 | 20.303 | 24.8404 | 8225.3109
38904.6584 | 1913 | 1 | 38904.6584 | 2077 | 1 | 3039.5 | 3186.5 | 116.7888 | 0.06105 | 126.801 | 0.06105 | 1.1679 | 0.0006105 | 1.268 | 0.0006105 | 1.1673 | 1.2674 | 28.7098 | 18.4983 | 8529.3143
38904.6586 | 2439 | 2 | 38904.6586 | 2093 | 1 | 3056 | 3203 | 148.9011 | 0.1221 | 127.7778 | 0.06105 | 1.489 | 0.001221 | 1.2778 | 0.0006105 | 1.4878 | 1.2772 | 0.8812 | 18.5684 | 151.7505
38904.6588 | 1913 | 1 | 38904.6588 | 1995 | 1 | 3073 | 3220 | 116.7888 | 0.06105 | 121.7949 | 0.06105 | 1.1679 | 0.0006105 | 1.2179 | 0.0006105 | 1.1673 | 1.2173 | 28.6928 | 23.3799 | 10353.6325
38904.659 | 2027 | 1 | 38904.659 | 2395 | 1 | 3090 | 3237 | 123.7485 | 0.06105 | 146.2149 | 0.06105 | 1.2375 | 0.0006105 | 1.4621 | 0.0006105 | 1.2369 | 1.4615 | 21.7839 | 2.7362 | 1151.5857
38904.6592 | 2338 | 1 | 38904.6592 | 2155 | 1 | 3106.5 | 3253.5 | 142.735 | 0.06105 | 131.5629 | 0.06105 | 1.4274 | 0.0006105 | 1.3156 | 0.0006105 | 1.4267 | 1.315 | 5.2523 | 14.3038 | 1518.9281
38904.6594 | 2081 | 1 | 38904.6594 | 2041 | 1 | 3123.5 | 3270.5 | 127.0452 | 0.06105 | 124.6032 | 0.06105 | 1.2705 | 0.0006105 | 1.246 | 0.0006105 | 1.2698 | 1.2454 | 18.2821 | 20.6131 | 6466.6183
38904.6596 | 2322 | 1 | 38904.6596 | 2127 | 1 | 3140.5 | 3287.5 | 141.7582 | 0.06105 | 129.8535 | 0.06105 | 1.4176 | 0.0006105 | 1.2985 | 0.0006105 | 1.417 | 1.2979 | 5.9784 | 15.8054 | 1875
38904.6598 | 2435 | 1 | 38904.6598 | 2415 | 1 | 3157 | 3304 | 148.6569 | 0.06105 | 147.4359 | 0.06105 | 1.4866 | 0.0006105 | 1.4744 | 0.0006105 | 1.486 | 1.4737 | 1.0651 | 1.9559 | 46.771
38904.66 | 2005 | 0 | 38904.66 | 2211 | 1 | 3174 | 3321 | 122.4054 | 0 | 134.9817 | 0.06105 | 1.2241 | 0 | 1.3498 | 0.0006105 | 1.2241 | 1.3492 | 22.7122 | 11.3294 | 21.4882
38904.6602 | 2026 | 1 | 38904.6602 | 1923 | 1 | 3190.5 | 3337.5 | 123.6874 | 0.06105 | 117.3993 | 0.06105 | 1.2369 | 0.0006105 | 1.174 | 0.0006105 | 1.2363 | 1.1734 | 21.4887 | 28.0273 | 9487.4013
38904.6604 | 2143 | 1 | 38904.6604 | 2202 | 1 | 3207.5 | 3354.5 | 130.8303 | 0.06105 | 134.4322 | 0.06105 | 1.3083 | 0.0006105 | 1.3443 | 0.0006105 | 1.3077 | 1.3437 | 14.876 | 11.7752 | 3332.9666
38904.6605 | 1988 | 1 | 38904.6606 | 2136 | 1 | 3224 | 3371 | 121.3675 | 0.06105 | 130.4029 | 0.06105 | 1.2137 | 0.0006105 | 1.304 | 0.0006105 | 1.2131 | 1.3034 | 23.8524 | 15.2233 | 6227.8845
38904.6607 | 2209 | 1 | 38904.6608 | 2419 | 1 | 3241 | 3388 | 134.8596 | 0.06105 | 147.6801 | 0.06105 | 1.3486 | 0.0006105 | 1.4768 | 0.0006105 | 1.348 | 1.4762 | 11.6933 | 1.7174 | 422.7438
38904.6609 | 2249 | 1 | 38904.6609 | 2444 | 1 | 3257.5 | 3404.5 | 137.3016 | 0.06105 | 149.2063 | 0.06105 | 1.373 | 0.0006105 | 1.4921 | 0.0006105 | 1.3724 | 1.4915 | 10.0683 | 0.67322 | 140.6858
38904.6611 | 1872 | 1 | 38904.6611 | 2428 | 1 | 3274.5 | 3421.5 | 114.2857 | 0.06105 | 148.2295 | 0.06105 | 1.1429 | 0.0006105 | 1.4823 | 0.0006105 | 1.1422 | 1.4817 | 32.758 | 1.3358 | 774.3009
38904.6613 | 1880 | 1 | 38904.6613 | 2144 | 1 | 3291.5 | 3438.5 | 114.7741 | 0.06105 | 130.8913 | 0.06105 | 1.1477 | 0.0006105 | 1.3089 | 0.0006105 | 1.1471 | 1.3083 | 30.9993 | 14.7857 | 7463.0595
38904.6615 | 2197 | 1 | 38904.6615 | 2369 | 1 | 3308 | 3455 | 134.127 | 0.06105 | 144.6276 | 0.06105 | 1.3413 | 0.0006105 | 1.4463 | 0.0006105 | 1.3407 | 1.4457 | 12.1363 | 3.8724 | 978.1686
38904.6617 | 2049 | 0 | 38904.6617 | 2087 | 0 | 3325 | 3472 | 125.0916 | 0 | 127.4115 | 0 | 1.2509 | 0 | 1.2741 | 0 | 1.2509 | 1.2741 | 20.0771 | 17.8908 | 18.8262
38904.6619 | 2280 | 1 | 38904.6619 | 2416 | 1 | 3341.5 | 3488.5 | 139.1941 | 0.06105 | 147.4969 | 0.06105 | 1.3919 | 0.0006105 | 1.475 | 0.0006105 | 1.3913 | 1.4744 | 8.1075 | 1.8471 | 325.3263
38904.6621 | 2341 | 1 | 38904.6621 | 2400 | 1 | 3358.5 | 3505.5 | 142.9182 | 0.06105 | 146.5201 | 0.06105 | 1.4292 | 0.0006105 | 1.4652 | 0.0006105 | 1.4286 | 1.4646 | 5.1891 | 2.5373 | 292.9289

## C2-3
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 149.6569 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38904.6216 | 1 | 0 | 38904.6217 | 1 | 0 | -138 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6218 | 1 | 0 | 38904.6218 | 1 | 0 | -121.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.622 | 1 | 0 | 38904.622 | 1 | 0 | -104.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6222 | 1 | 0 | 38904.6222 | 1 | 0 | -88 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6224 | 1 | 0 | 38904.6224 | 1 | 0 | -71 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6226 | 1 | 0 | 38904.6226 | 1 | 0 | -54.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6228 | 1 | 0 | 38904.6228 | 1 | 0 | -37.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.623 | 1 | 0 | 38904.623 | 2 | 0 | -20.5 | 126.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38904.6232 | 1 | 0 | 38904.6232 | 1 | 0 | -4 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6234 | 1 | 0 | 38904.6234 | 1 | 0 | 13 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6236 | 1 | 0 | 38904.6236 | 1 | 0 | 29.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6238 | 1 | 0 | 38904.6238 | 1 | 0 | 46.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.624 | 1 | 0 | 38904.624 | 1 | 0 | 63.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6242 | 1 | 0 | 38904.6242 | 1 | 0 | 80 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6244 | 1 | 0 | 38904.6244 | 1 | 0 | 97 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6245 | 1 | 0 | 38904.6246 | 1 | 0 | 114 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6247 | 1 | 0 | 38904.6248 | 1 | 0 | 130.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6249 | 1 | 0 | 38904.625 | 1 | 0 | 147.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6251 | 1 | 0 | 38904.6252 | 1 | 0 | 164.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6253 | 1 | 0 | 38904.6253 | 1 | 0 | 181 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6255 | 1 | 0 | 38904.6255 | 1 | 0 | 198 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6257 | 1 | 0 | 38904.6257 | 1 | 0 | 214.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6259 | 1 | 0 | 38904.6259 | 1 | 0 | 231.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6261 | 1 | 0 | 38904.6261 | 1 | 0 | 248.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6263 | 1 | 0 | 38904.6263 | 1 | 0 | 265 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6265 | 1 | 0 | 38904.6265 | 1 | 0 | 281.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6267 | 1 | 0 | 38904.6267 | 2 | 0 | 298.5 | 445.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38904.6269 | 1 | 0 | 38904.6269 | 1 | 0 | 315.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6271 | 1 | 0 | 38904.6271 | 1 | 0 | 332.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6273 | 1 | 0 | 38904.6273 | 1 | 0 | 349 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6275 | 1 | 0 | 38904.6275 | 1 | 0 | 365.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6277 | 1 | 0 | 38904.6277 | 1 | 0 | 382.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6279 | 1 | 0 | 38904.6279 | 1 | 0 | 399.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.628 | 1 | 0 | 38904.6281 | 1 | 0 | 416 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6282 | 1 | 0 | 38904.6283 | 1 | 0 | 433 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6284 | 1 | 0 | 38904.6285 | 1 | 0 | 450 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6286 | 1 | 0 | 38904.6286 | 1 | 0 | 466.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6288 | 1 | 0 | 38904.6288 | 1 | 0 | 483.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.629 | 1 | 0 | 38904.629 | 1 | 0 | 500 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6292 | 1 | 0 | 38904.6292 | 1 | 0 | 517 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6294 | 1 | 0 | 38904.6294 | 1 | 0 | 533.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6296 | 1 | 0 | 38904.6296 | 1 | 0 | 550.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6298 | 1 | 0 | 38904.6298 | 1 | 0 | 567.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.63 | 1 | 0 | 38904.63 | 1 | 0 | 584 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6302 | 1 | 0 | 38904.6302 | 1 | 0 | 601 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6304 | 1 | 0 | 38904.6304 | 1 | 0 | 618 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6306 | 1 | 0 | 38904.6306 | 1 | 0 | 634.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6308 | 1 | 0 | 38904.6308 | 1 | 0 | 651.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.631 | 1 | 0 | 38904.631 | 1 | 0 | 668 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6312 | 1 | 0 | 38904.6312 | 1 | 0 | 685 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6314 | 1 | 0 | 38904.6314 | 1 | 0 | 701.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6316 | 1 | 0 | 38904.6316 | 1 | 0 | 718.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6317 | 1 | 0 | 38904.6318 | 1 | 0 | 735.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6319 | 1 | 0 | 38904.632 | 1 | 0 | 752 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6321 | 1 | 0 | 38904.6322 | 1 | 0 | 769 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6323 | 1 | 0 | 38904.6323 | 1 | 0 | 785.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6325 | 1 | 0 | 38904.6325 | 1 | 0 | 802.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6327 | 1 | 0 | 38904.6327 | 1 | 0 | 819.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6329 | 1 | 0 | 38904.6329 | 1 | 0 | 836 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6331 | 1 | 0 | 38904.6331 | 1 | 0 | 853 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6333 | 1 | 0 | 38904.6333 | 1 | 0 | 869.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6335 | 1 | 0 | 38904.6335 | 1 | 0 | 886.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6337 | 1 | 0 | 38904.6337 | 1 | 0 | 903.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6339 | 1 | 0 | 38904.6339 | 1 | 0 | 920 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6341 | 1 | 0 | 38904.6341 | 1 | 0 | 937 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6343 | 1 | 0 | 38904.6343 | 1 | 0 | 953.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6345 | 1 | 0 | 38904.6345 | 1 | 0 | 970.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6347 | 1 | 0 | 38904.6347 | 1 | 0 | 987.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6348 | 1 | 0 | 38904.6349 | 1 | 0 | 1004 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.635 | 1 | 0 | 38904.6351 | 1 | 0 | 1021 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6352 | 1 | 0 | 38904.6353 | 1 | 0 | 1037.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6354 | 1 | 0 | 38904.6355 | 1 | 0 | 1054.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6356 | 1 | 0 | 38904.6356 | 1 | 0 | 1071.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6358 | 1 | 0 | 38904.6358 | 1 | 0 | 1088 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.636 | 1 | 0 | 38904.636 | 1 | 0 | 1105 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6362 | 1 | 1 | 38904.6362 | 1 | 0 | 1121.5 | 1268.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38904.6364 | 1 | 0 | 38904.6364 | 1 | 0 | 1138.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6366 | 1 | 0 | 38904.6366 | 1 | 0 | 1155.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6368 | 1 | 0 | 38904.6368 | 1 | 0 | 1172 | 1319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.637 | 1 | 0 | 38904.637 | 1 | 0 | 1189 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6372 | 1 | 0 | 38904.6372 | 1 | 0 | 1205.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6374 | 1 | 0 | 38904.6374 | 2 | 0 | 1222.5 | 1369.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38904.6376 | 1 | 0 | 38904.6376 | 1 | 0 | 1239.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6378 | 1 | 0 | 38904.6378 | 1 | 0 | 1256 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.638 | 1 | 0 | 38904.638 | 1 | 0 | 1273 | 1420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6382 | 1 | 0 | 38904.6382 | 1 | 0 | 1289.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6384 | 2 | 0 | 38904.6384 | 1 | 0 | 1306.5 | 1453.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122469 | 245038 | 122468.9988
38904.6386 | 1 | 0 | 38904.6386 | 2 | 0 | 1323.5 | 1470.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38904.6387 | 1 | 0 | 38904.6388 | 1 | 0 | 1340 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6389 | 1 | 0 | 38904.639 | 1 | 0 | 1357 | 1504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6391 | 1 | 0 | 38904.6391 | 1 | 0 | 1373.5 | 1520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6393 | 1 | 0 | 38904.6393 | 1 | 0 | 1390.5 | 1537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6395 | 1 | 0 | 38904.6395 | 1 | 0 | 1407.5 | 1554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6397 | 1 | 0 | 38904.6397 | 1 | 0 | 1424 | 1571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6399 | 1 | 0 | 38904.6399 | 1 | 0 | 1441 | 1588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6401 | 1 | 0 | 38904.6401 | 1 | 0 | 1457.5 | 1604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6403 | 1 | 0 | 38904.6403 | 1 | 0 | 1474.5 | 1621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6405 | 1 | 0 | 38904.6405 | 1 | 0 | 1491.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6407 | 1 | 0 | 38904.6407 | 1 | 0 | 1508 | 1655 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6409 | 1 | 0 | 38904.6409 | 1 | 0 | 1524.5 | 1671.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6411 | 1 | 0 | 38904.6411 | 1 | 0 | 1541.5 | 1688.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6413 | 1 | 0 | 38904.6413 | 1 | 0 | 1558.5 | 1705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6415 | 1 | 0 | 38904.6415 | 1 | 0 | 1575.5 | 1722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6417 | 1 | 0 | 38904.6417 | 1 | 0 | 1592 | 1739 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6419 | 1 | 1 | 38904.6419 | 1 | 0 | 1609 | 1756 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38904.642 | 1 | 0 | 38904.6421 | 1 | 0 | 1625.5 | 1772.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6422 | 1 | 0 | 38904.6423 | 1 | 0 | 1642.5 | 1789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6424 | 1 | 0 | 38904.6425 | 1 | 0 | 1659 | 1806 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6426 | 1 | 0 | 38904.6427 | 1 | 0 | 1676 | 1823 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6428 | 1 | 0 | 38904.6428 | 1 | 0 | 1692.5 | 1839.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.643 | 1 | 0 | 38904.643 | 1 | 0 | 1709.5 | 1856.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6432 | 1 | 0 | 38904.6432 | 1 | 0 | 1726.5 | 1873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6434 | 1 | 1 | 38904.6434 | 1 | 0 | 1743.5 | 1890.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 600436214.44 | 245038 | 244838.0816
38904.6436 | 1 | 0 | 38904.6436 | 1 | 0 | 1760 | 1907 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6438 | 1 | 0 | 38904.6438 | 1 | 0 | 1776.5 | 1923.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.644 | 1 | 0 | 38904.644 | 1 | 0 | 1793.5 | 1940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6442 | 1 | 0 | 38904.6442 | 1 | 0 | 1810.5 | 1957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6444 | 1 | 0 | 38904.6444 | 1 | 0 | 1827 | 1974 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6446 | 1 | 0 | 38904.6446 | 1 | 0 | 1844 | 1991 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6448 | 1 | 0 |  | 1 | 0 | 1860 | 2007 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.645 | 1 | 0 | 38904.645 | 1 | 0 | 1877.5 | 2024.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6452 | 1 | 0 | 38904.6452 | 1 | 0 | 1894.5 | 2041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6453 | 1 | 0 | 38904.6454 | 1 | 0 | 1911 | 2058 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6455 | 1 | 0 | 38904.6456 | 1 | 0 | 1928 | 2075 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6457 | 1 | 0 | 38904.6458 | 1 | 0 | 1944.5 | 2091.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6459 | 1 | 0 | 38904.6459 | 1 | 0 | 1961.5 | 2108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6461 | 1 | 0 | 38904.6461 | 1 | 0 | 1978.5 | 2125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6463 | 1 | 0 | 38904.6463 | 1 | 0 | 1995 | 2142 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6465 | 1 | 0 | 38904.6465 | 1 | 0 | 2012 | 2159 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6467 | 1 | 0 | 38904.6467 | 1 | 0 | 2028.5 | 2175.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6469 | 1 | 0 | 38904.6469 | 1 | 0 | 2045.5 | 2192.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6471 | 1 | 0 | 38904.6471 | 1 | 0 | 2062.5 | 2209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6473 | 1 | 0 | 38904.6473 | 1 | 0 | 2079 | 2226 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6475 | 1 | 0 | 38904.6475 | 1 | 0 | 2096 | 2243 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6477 | 1 | 0 | 38904.6477 | 2 | 0 | 2112.5 | 2259.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245038 | 122469 | 245037.9994
38904.6479 | 1 | 0 | 38904.6479 | 1 | 0 | 2129.5 | 2276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6481 | 1 | 0 | 38904.6481 | 1 | 0 | 2146.5 | 2293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6483 | 1 | 0 | 38904.6483 | 1 | 0 | 2163 | 2310 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6485 | 1 | 0 | 38904.6485 | 1 | 0 | 2180 | 2327 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6487 | 1 | 0 | 38904.6487 | 1 | 0 | 2196.5 | 2343.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6489 | 1 | 0 | 38904.6489 | 1 | 0 | 2213.5 | 2360.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6491 | 1 | 0 | 38904.6491 | 1 | 0 | 2230.5 | 2377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6492 | 1 | 0 | 38904.6493 | 1 | 0 | 2247 | 2394 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6494 | 1 | 0 | 38904.6495 | 1 | 0 | 2264 | 2411 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6496 | 1 | 0 |  | 1 | 0 | 2280 | 2427 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6498 | 1 | 0 | 38904.6498 | 1 | 0 | 2297.5 | 2444.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.65 | 1 | 0 | 38904.65 | 1 | 0 | 2314.5 | 2461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6502 | 1 | 0 | 38904.6502 | 1 | 0 | 2331 | 2478 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38904.6504 | 3 | 0 | 38904.6504 | 1 | 0 | 2348 | 2495 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 81612.6667 | 245038 | 81612.6648
38904.6506 | 5 | 15 | 38904.6506 | 2 | 9 | 2364.5 | 2511.5 | 0.30525 | 0.91575 | 0.1221 | 0.54945 | 0.0030525 | 0.0091575 | 0.001221 | 0.0054945 | 0.006105 | 0.0042735 | 24568.5694 | 35175.2207 | 16163.2493
38904.6508 | 11 | 18 | 38904.6508 | 4 | 15 | 2381.5 | 2528.5 | 0.67155 | 1.0989 | 0.2442 | 0.91575 | 0.0067155 | 0.010989 | 0.002442 | 0.0091575 | 0.0042735 | 0.0067155 | 35268.6141 | 22335.2668 | 13397.6822
38904.651 | 407 | 344 | 38904.651 | 201 | 319 | 2398.5 | 2545.5 | 24.8474 | 21.0012 | 12.2711 | 19.475 | 0.24847 | 0.21001 | 0.12271 | 0.19475 | 0.038462 | 0.072039 | 4438.4362 | 2030.7946 | 471.0988
38904.6512 | 1073 | 1072 | 38904.6512 | 872 | 843 | 2415 | 2562 | 65.5067 | 65.4457 | 53.2357 | 51.4652 | 0.65507 | 0.65446 | 0.53236 | 0.51465 | 0.0006105 | 0.017705 | 4314.9758 | 3464.3119 | 27.7784
38904.6514 | 895 | 841 | 38904.6514 | 1124 | 1042 | 2432 | 2579 | 54.6398 | 51.3431 | 68.6203 | 63.6142 | 0.5464 | 0.51343 | 0.6862 | 0.63614 | 0.032967 | 0.050061 | 43790.7943 | 1667.1334 | 80.2494
38904.6516 | 1142 | 1047 | 38904.6516 | 1016 | 920 | 2448.5 | 2595.5 | 69.7192 | 63.9194 | 62.0269 | 56.1661 | 0.69719 | 0.63919 | 0.62027 | 0.56166 | 0.057998 | 0.058608 | 2555.7625 | 2392.1838 | 24.0546
38904.6518 | 886 | 862 | 38904.6518 | 1086 | 996 | 2465.5 | 2612.5 | 54.0904 | 52.6252 | 66.3004 | 60.8059 | 0.5409 | 0.52625 | 0.663 | 0.60806 | 0.014652 | 0.054945 | 2853.7412 | 2793.8386 | 78.7789
38904.652 | 1139 | 1069 | 38904.652 | 1089 | 1002 | 2482.5 | 2629.5 | 69.536 | 65.2625 | 66.4835 | 61.1722 | 0.69536 | 0.65263 | 0.66484 | 0.61172 | 0.042735 | 0.053114 | 30327.5624 | 1627.7705 | 21.4494
38904.6522 | 1152 | 904 | 38904.6522 | 1142 | 1072 | 2499 | 2646 | 70.3297 | 55.1893 | 69.7192 | 65.4457 | 0.7033 | 0.55189 | 0.69719 | 0.65446 | 0.1514 | 0.042735 | 280.0936 | 418.6945 | 35.3046
38904.6523 | 927 | 840 | 38904.6524 | 945 | 855 | 2516 | 2663 | 56.5934 | 51.2821 | 57.6923 | 52.1978 | 0.56593 | 0.51282 | 0.57692 | 0.52198 | 0.053114 | 0.054945 | 2845.7197 | 2512.5229 | 78.3552
38904.6525 | 1102 | 1067 | 38904.6526 | 954 | 923 | 2532.5 | 2679.5 | 67.2772 | 65.1404 | 58.2418 | 56.3492 | 0.67277 | 0.6514 | 0.58242 | 0.56349 | 0.021368 | 0.018926 | 5357.5995 | 10872.5335 | 26.2237
38904.6527 | 1029 | 999 | 38904.6528 | 985 | 887 | 2549.5 | 2696.5 | 62.8205 | 60.989 | 60.1343 | 54.1514 | 0.62821 | 0.60989 | 0.60134 | 0.54151 | 0.018315 | 0.059829 | 2225.2332 | 2945.1225 | 40.9886
38904.6529 | 973 | 872 | 38904.653 | 901 | 933 | 2566.5 | 2713.5 | 59.4017 | 53.2357 | 55.0061 | 56.9597 | 0.59402 | 0.53236 | 0.55006 | 0.5696 | 0.061661 | 0.019536 | 1148.9155 | 3150.7295 | 67.3998
38904.6531 | 1127 | 1061 | 38904.6531 | 957 | 850 | 2583 | 2730 | 68.8034 | 64.7741 | 58.4249 | 51.8926 | 0.68803 | 0.64774 | 0.58425 | 0.51893 | 0.040293 | 0.065324 | 7231.0563 | 2225.0261 | 23.7561
38904.6533 | 1002 | 975 | 38904.6533 | 1058 | 940 | 2600 | 2747 | 61.1722 | 59.5238 | 64.591 | 57.3871 | 0.61172 | 0.59524 | 0.64591 | 0.57387 | 0.016484 | 0.072039 | 1424.5836 | 1304.5117 | 45.1902
38904.6535 | 1149 | 1067 | 38904.6535 | 1047 | 1032 | 2616.5 | 2763.5 | 70.1465 | 65.1404 | 63.9194 | 63.0037 | 0.70147 | 0.6514 | 0.63919 | 0.63004 | 0.050061 | 0.0091575 | 734.1018 | 1118.3153 | 20.2493
38904.6537 | 1174 | 879 | 38904.6537 | 933 | 959 | 2633.5 | 2780.5 | 71.6728 | 53.663 | 56.9597 | 58.547 | 0.71673 | 0.53663 | 0.5696 | 0.58547 | 0.1801 | 0.015873 | 257.9792 | 439.174 | 36.9161
38904.6539 | 1141 | 1016 | 38904.6539 | 1051 | 1028 | 2650.5 | 2797.5 | 69.6581 | 62.0269 | 64.1636 | 62.7595 | 0.69658 | 0.62027 | 0.64164 | 0.62759 | 0.076313 | 0.014042 | 521.2187 | 803.7534 | 25.7684
38904.6541 | 898 | 836 | 38904.6541 | 964 | 851 | 2667 | 2814 | 54.823 | 51.0379 | 58.8523 | 51.9536 | 0.54823 | 0.51038 | 0.58852 | 0.51954 | 0.037851 | 0.068987 | 71054.1203 | 1397.6706 | 80.0814
38904.6543 | 2273 | 16 | 38904.6543 | 28 | 17 | 2684 | 2831 | 138.7668 | 0.9768 | 1.7094 | 1.0379 | 1.3877 | 0.009768 | 0.017094 | 0.010379 | 1.3779 | 0.0067155 | 7.8987 | 1186.6198 | 935.9958
38904.6545 | 2002 | 19 | 38904.6545 | 15 | 18 | 2700.5 | 2847.5 | 122.2222 | 1.16 | 0.91575 | 1.0989 | 1.2222 | 0.0116 | 0.0091575 | 0.010989 | 1.2106 | 0.0018315 | 22.6548 | 3186.7551 | 2196.2401
38904.6547 | 2382 | 15 | 38904.6547 | 70 | 15 | 2717.5 | 2864.5 | 145.4212 | 0.91575 | 4.2735 | 0.91575 | 1.4542 | 0.0091575 | 0.042735 | 0.0091575 | 1.4451 | 0.033578 | 2.9276 | 520.6684 | 304.1232
38904.6549 | 2177 | 11 | 38904.6549 | 28 | 10 | 2734 | 2881 | 132.906 | 0.67155 | 1.7094 | 0.6105 | 1.3291 | 0.0067155 | 0.017094 | 0.006105 | 1.3223 | 0.010989 | 12.666 | 3975.9024 | 2335.6193
38904.6551 | 2357 | 8 | 38904.6551 | 6 | 8 | 2751 | 2898 | 143.895 | 0.4884 | 0.3663 | 0.4884 | 1.4389 | 0.004884 | 0.003663 | 0.004884 | 1.4341 | 0.001221 | 4.0168 | 1240.273 | 999.1881
38904.6553 | 2386 | 7 | 38904.6553 | 7 | 7 | 2768 | 2915 | 145.6654 | 0.42735 | 0.42735 | 0.42735 | 1.4567 | 0.0042735 | 0.0042735 | 0.0042735 | 1.4524 | 0 | 2.7474 | 959.3741 | 755.2743
38904.6555 | 2391 | 6 | 38904.6555 | 7 | 5 | 2784.5 | 2931.5 | 145.9707 | 0.3663 | 0.42735 | 0.30525 | 1.4597 | 0.003663 | 0.0042735 | 0.0030525 | 1.456 | 0.001221 | 2.5311 | 1250.0734 | 839.2012
38904.6557 | 2177 | 5 | 38904.6557 | 6 | 5 | 2801.5 | 2948.5 | 132.906 | 0.30525 | 0.3663 | 0.30525 | 1.3291 | 0.0030525 | 0.003663 | 0.0030525 | 1.326 | 0.0006105 | 12.6321 | 6338.2056 | 5303.9183
38904.6558 | 2300 | 4 | 38904.6559 | 585 | 5 | 2818 | 2965 | 140.4151 | 0.2442 | 35.7143 | 0.30525 | 1.4042 | 0.002442 | 0.35714 | 0.0030525 | 1.4017 | 0.35409 | 6.5963 | 370.1666 | 2900.8416
38904.656 | 2424 | 4 | 38904.6561 | 21 | 4 | 2835 | 2982 | 147.9853 | 0.2442 | 1.2821 | 0.2442 | 1.4799 | 0.002442 | 0.012821 | 0.002442 | 1.4774 | 0.010379 | 1.1311 | 721.9873 | 513.3918
38904.6562 | 2215 | 3 | 38904.6562 | 6 | 3 | 2851.5 | 2998.5 | 135.2259 | 0.18315 | 0.3663 | 0.18315 | 1.3523 | 0.0018315 | 0.003663 | 0.0018315 | 1.3504 | 0.0018315 | 10.6861 | 9752.7177 | 7700.3771
38904.6564 | 2162 | 3 | 38904.6564 | 6 | 3 | 2868.5 | 3015.5 | 131.9902 | 0.18315 | 0.3663 | 0.18315 | 1.3199 | 0.0018315 | 0.003663 | 0.0018315 | 1.3181 | 0.0018315 | 13.4033 | 12616.3795 | 9470.9315
38904.6566 | 2106 | 2 | 38904.6566 | 7 | 2 | 2885.5 | 3032.5 | 128.5714 | 0.1221 | 0.42735 | 0.1221 | 1.2857 | 0.001221 | 0.0042735 | 0.001221 | 1.2845 | 0.0030525 | 16.4154 | 34026.6803 | 17118.6904
38904.6568 | 2350 | 2 | 38904.6568 | 7 | 2 | 2902 | 3049 | 143.4676 | 0.1221 | 0.42735 | 0.1221 | 1.4347 | 0.001221 | 0.0042735 | 0.001221 | 1.4335 | 0.0030525 | 4.3177 | 5915.5247 | 4886.3971
38904.657 | 2158 | 2 | 38904.657 | 6 | 2 | 2919 | 3066 | 131.746 | 0.1221 | 0.3663 | 0.1221 | 1.3175 | 0.001221 | 0.003663 | 0.001221 | 1.3162 | 0.002442 | 13.6076 | 22858.8866 | 14505.5431
38904.6572 | 1895 | 1 | 38904.6572 | 7 | 1 | 2935.5 | 3082.5 | 115.6899 | 0.06105 | 0.42735 | 0.06105 | 1.1569 | 0.0006105 | 0.0042735 | 0.0006105 | 1.1563 | 0.003663 | 29.3759 | 94164.7841 | 55479.083
38904.6574 | 2386 | 1 | 38904.6574 | 7 | 1 | 2952.5 | 3099.5 | 145.6654 | 0.06105 | 0.42735 | 0.06105 | 1.4567 | 0.0006105 | 0.0042735 | 0.0006105 | 1.456 | 0.003663 | 2.7413 | 8019.8204 | 6358.7125
38904.6576 | 2246 | 1 | 38904.6576 | 6 | 1 | 2969.5 | 3116.5 | 137.1184 | 0.06105 | 0.3663 | 0.06105 | 1.3712 | 0.0006105 | 0.003663 | 0.0006105 | 1.3706 | 0.0030525 | 9.1483 | 41230.699 | 20388.5501
38904.6578 | 1880 | 1 | 38904.6578 | 5 | 1 | 2986 | 3133 | 114.7741 | 0.06105 | 0.30525 | 0.06105 | 1.1477 | 0.0006105 | 0.0030525 | 0.0006105 | 1.1471 | 0.002442 | 30.4087 | 343848.1757 | 57021.4167
38904.658 | 2020 | 1 | 38904.658 | 6 | 1 | 3003 | 3150 | 123.3211 | 0.06105 | 0.3663 | 0.06105 | 1.2332 | 0.0006105 | 0.003663 | 0.0006105 | 1.2326 | 0.0030525 | 21.366 | 764965.2107 | 43032.3746
38904.6582 | 2257 | 1 | 38904.6582 | 5 | 1 | 3019.5 | 3166.5 | 137.79 | 0.06105 | 0.30525 | 0.06105 | 1.3779 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3773 | 0.002442 | 8.6161 | 32163.1909 | 19278.0617
38904.6584 | 1959 | 1 | 38904.6584 | 6 | 1 | 3036.5 | 3183.5 | 119.5971 | 0.06105 | 0.3663 | 0.06105 | 1.196 | 0.0006105 | 0.003663 | 0.0006105 | 1.1954 | 0.0030525 | 25.1471 | 238947.2527 | 49117.4442
38904.6586 | 2263 | 1 | 38904.6586 | 6 | 1 | 3053.5 | 3200.5 | 138.1563 | 0.06105 | 0.3663 | 0.06105 | 1.3816 | 0.0006105 | 0.003663 | 0.0006105 | 1.381 | 0.0030525 | 8.328 | 34895.8173 | 18684.4565
38904.6588 | 1922 | 1 | 38904.6588 | 4 | 1 | 3070 | 3217 | 117.3382 | 0.06105 | 0.2442 | 0.06105 | 1.1734 | 0.0006105 | 0.002442 | 0.0006105 | 1.1728 | 0.0018315 | 27.5575 | 389230.6141 | 52824.4285
38904.659 | 2333 | 1 | 38904.659 | 6 | 1 | 3087 | 3234 | 142.4298 | 0.06105 | 0.3663 | 0.06105 | 1.4243 | 0.0006105 | 0.003663 | 0.0006105 | 1.4237 | 0.0030525 | 5.0763 | 16636.0028 | 11667.8638
38904.6592 | 2352 | 1 | 38904.6592 | 5 | 1 | 3104 | 3251 | 143.5897 | 0.06105 | 0.30525 | 0.06105 | 1.4359 | 0.0006105 | 0.0030525 | 0.0006105 | 1.4353 | 0.002442 | 4.2271 | 12445.4944 | 9759.5814
38904.6594 | 1990 | 1 | 38904.6594 | 5 | 1 | 3120.5 | 3267.5 | 121.4896 | 0.06105 | 0.30525 | 0.06105 | 1.2149 | 0.0006105 | 0.0030525 | 0.0006105 | 1.2143 | 0.002442 | 23.1966 | 786666.995 | 46032.1485
38904.6595 | 2050 | 1 | 38904.6596 | 6 | 1 | 3137.5 | 3284.5 | 125.1526 | 0.06105 | 0.3663 | 0.06105 | 1.2515 | 0.0006105 | 0.003663 | 0.0006105 | 1.2509 | 0.0030525 | 19.5891 | 2331414.7821 | 40036.2827
38904.6597 | 2156 | 1 | 38904.6598 | 5 | 1 | 3154 | 3301 | 131.6239 | 0.06105 | 0.30525 | 0.06105 | 1.3162 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3156 | 0.002442 | 13.7067 | 74229.6426 | 29398.3953
38904.6599 | 2435 | 1 | 38904.66 | 5 | 1 | 3171 | 3318 | 148.6569 | 0.06105 | 0.30525 | 0.06105 | 1.4866 | 0.0006105 | 0.0030525 | 0.0006105 | 1.486 | 0.002442 | 0.67295 | 1691.8321 | 1452.1661
38904.6601 | 2357 | 1 | 38904.6601 | 6 | 1 | 3187.5 | 3334.5 | 143.895 | 0.06105 | 0.3663 | 0.06105 | 1.4389 | 0.0006105 | 0.003663 | 0.0006105 | 1.4383 | 0.0030525 | 4.0059 | 12249.5602 | 9262.386
38904.6603 | 2315 | 1 | 38904.6603 | 5 | 1 | 3204.5 | 3351.5 | 141.3309 | 0.06105 | 0.30525 | 0.06105 | 1.4133 | 0.0006105 | 0.0030525 | 0.0006105 | 1.4127 | 0.002442 | 5.8937 | 18865.7098 | 13466.6185
38904.6605 | 2247 | 1 | 38904.6605 | 5 | 1 | 3221.5 | 3368.5 | 137.1795 | 0.06105 | 0.30525 | 0.06105 | 1.3718 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3712 | 0.002442 | 9.0997 | 35001.5502 | 20280.0595
38904.6607 | 1878 | 1 | 38904.6607 | 6 | 1 | 3238 | 3385 | 114.652 | 0.06105 | 0.3663 | 0.06105 | 1.1465 | 0.0006105 | 0.003663 | 0.0006105 | 1.1459 | 0.0030525 | 30.5477 | 141643.6998 | 57197.6187
38904.6609 | 2225 | 1 | 38904.6609 | 6 | 0 | 3255 | 3402 | 135.8364 | 0.06105 | 0.3663 | 0 | 1.3584 | 0.0006105 | 0.003663 | 0 | 1.3578 | 0.003663 | 10.179 | 40756.3333 | 22482.836
38904.6611 | 2208 | 1 | 38904.6611 | 5 | 1 | 3271.5 | 3418.5 | 134.7985 | 0.06105 | 0.30525 | 0.06105 | 1.348 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3474 | 0.002442 | 11.0276 | 48269.8515 | 24187.8903
38904.6613 | 2381 | 0 | 38904.6613 | 5 | 1 | 3288.5 | 3435.5 | 145.3602 | 0 | 0.30525 | 0.06105 | 1.4536 | 0 | 0.0030525 | 0.0006105 | 1.4536 | 0.002442 | 2.9559 | 61184.5 | 1.5023
38904.6615 | 1894 | 1 | 38904.6615 | 5 | 0 | 3305.5 | 3452.5 | 115.6288 | 0.06105 | 0.30525 | 0 | 1.1563 | 0.0006105 | 0.0030525 | 0 | 1.1557 | 0.0030525 | 29.4443 | 48927.6 | 55524.517
38904.6617 | 2348 | 1 | 38904.6617 | 5 | 0 | 3322 | 3469 | 143.3455 | 0.06105 | 0.30525 | 0 | 1.4335 | 0.0006105 | 0.0030525 | 0 | 1.4328 | 0.0030525 | 4.4048 | 48927.6 | 10217.1179
38904.6619 | 2046 | 1 | 38904.6619 | 5 | 2 | 3339 | 3486 | 124.9084 | 0.06105 | 0.30525 | 0.1221 | 1.2491 | 0.0006105 | 0.0030525 | 0.001221 | 1.2485 | 0.0018315 | 19.823 | 34507.9971 | 40321.1542
38904.6621 | 2413 | 1 | 38904.6621 | 5 | 0 | 3355.5 | 3502.5 | 147.3138 | 0.06105 | 0.30525 | 0 | 1.4731 | 0.0006105 | 0.0030525 | 0 | 1.4725 | 0.0030525 | 1.5912 | 48927.6 | 3730.3757

## C1-4
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 149.9621 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38904.6216 | 1 | 0 | 38904.6216 | 1 | 0 | -141 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994 | 0.0006105 | 245538 | #DIV/0! | 1
38904.6218 | 1 | 0 | 38904.6218 | 1 | 0 | -124 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.622 | 1 | 0 | 38904.622 | 2 | 0 | -107.5 | 39.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.6222 | 1 | 0 | 38904.6222 | 1 | 0 | -90.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6224 | 1 | 0 | 38904.6224 | 1 | 0 | -73.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6226 | 1 | 0 | 38904.6226 | 1 | 0 | -57 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6228 | 1 | 0 | 38904.6228 | 1 | 0 | -40 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.623 | 1 | 0 | 38904.623 | 1 | 0 | -23.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6232 | 1 | 0 | 38904.6232 | 1 | 0 | -6.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6233 | 1 | 0 | 38904.6234 | 1 | 0 | 10 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6235 | 1 | 0 | 38904.6236 | 1 | 0 | 27 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6237 | 1 | 0 | 38904.6238 | 1 | 0 | 44 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6239 | 1 | 0 | 38904.6239 | 1 | 0 | 60.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6241 | 1 | 0 | 38904.6241 | 1 | 0 | 77.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6243 | 2 | 0 | 38904.6243 | 1 | 0 | 94.5 | 241.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122719 | 245538 | 122718.9988
38904.6245 | 1 | 0 | 38904.6245 | 1 | 0 | 111 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6247 | 1 | 0 | 38904.6247 | 1 | 0 | 128 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6249 | 1 | 0 | 38904.6249 | 1 | 0 | 144.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6251 | 1 | 0 | 38904.6251 | 1 | 0 | 161.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6253 | 1 | 0 | 38904.6253 | 1 | 0 | 178.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6255 | 1 | 0 | 38904.6255 | 1 | 0 | 195 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6257 | 2 | 1 | 38904.6257 | 1 | 0 | 211.5 | 358.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245238.1221
38904.6259 | 1 | 0 | 38904.6259 | 1 | 0 | 228.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6261 | 1 | 0 | 38904.6261 | 1 | 0 | 245.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6263 | 1 | 0 | 38904.6263 | 1 | 0 | 262 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6265 | 1 | 0 | 38904.6265 | 1 | 0 | 279 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6267 | 1 | 0 | 38904.6267 | 1 | 0 | 295.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6269 | 1 | 0 | 38904.6269 | 1 | 0 | 312.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.627 | 1 | 0 | 38904.6271 | 1 | 0 | 329.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6272 | 1 | 0 | 38904.6273 | 1 | 0 | 346.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6274 | 1 | 0 | 38904.6275 | 1 | 0 | 363 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6276 | 1 | 0 | 38904.6276 | 1 | 0 | 379.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6278 | 1 | 0 | 38904.6278 | 1 | 0 | 396.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.628 | 1 | 0 | 38904.628 | 1 | 0 | 413.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6282 | 1 | 0 | 38904.6282 | 1 | 0 | 430.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6284 | 1 | 0 | 38904.6284 | 1 | 0 | 447 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6286 | 1 | 0 | 38904.6286 | 1 | 0 | 464 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6288 | 1 | 0 | 38904.6288 | 1 | 0 | 480.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.629 | 1 | 0 | 38904.629 | 1 | 0 | 497.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6292 | 1 | 0 | 38904.6292 | 1 | 0 | 514 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6294 | 1 | 0 | 38904.6294 | 1 | 0 | 531 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6296 | 1 | 0 | 38904.6296 | 1 | 0 | 547.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6298 | 1 | 0 | 38904.6298 | 1 | 0 | 564.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.63 | 1 | 0 | 38904.63 | 1 | 0 | 581.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6302 | 1 | 0 | 38904.6302 | 1 | 0 | 598 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6303 | 1 | 0 | 38904.6304 | 1 | 0 | 615 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6305 | 1 | 0 | 38904.6306 | 1 | 0 | 631.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6307 | 1 | 0 | 38904.6308 | 1 | 0 | 648.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6309 | 1 | 0 | 38904.6309 | 1 | 0 | 665.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6311 | 1 | 0 | 38904.6311 | 1 | 0 | 682 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6313 | 1 | 0 | 38904.6313 | 1 | 0 | 699 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6315 | 1 | 0 | 38904.6315 | 1 | 0 | 715.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6317 | 1 | 0 | 38904.6317 | 1 | 0 | 732.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6319 | 1 | 0 | 38904.6319 | 1 | 0 | 749.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6321 | 1 | 0 | 38904.6321 | 1 | 0 | 766 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6323 | 1 | 0 | 38904.6323 | 1 | 0 | 783 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6325 | 1 | 0 | 38904.6325 | 2 | 0 | 799.5 | 946.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.6327 | 1 | 0 | 38904.6327 | 1 | 0 | 816.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6329 | 1 | 0 | 38904.6329 | 1 | 0 | 833.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6331 | 1 | 0 | 38904.6331 | 1 | 0 | 850 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6333 | 1 | 0 | 38904.6333 | 1 | 0 | 867 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6335 | 1 | 0 | 38904.6335 | 1 | 0 | 883.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6337 | 1 | 0 | 38904.6337 | 1 | 0 | 900.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6339 | 1 | 0 | 38904.6339 | 1 | 0 | 917.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.634 | 1 | 0 | 38904.6341 | 1 | 0 | 934 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6342 | 1 | 0 | 38904.6343 | 1 | 0 | 951 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6344 | 1 | 0 | 38904.6344 | 1 | 0 | 967.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6346 | 1 | 0 | 38904.6346 | 1 | 0 | 984.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6348 | 1 | 0 | 38904.6348 | 1 | 0 | 1001.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.635 | 1 | 0 | 38904.635 | 1 | 0 | 1018 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6352 | 1 | 0 | 38904.6352 | 1 | 0 | 1035 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6354 | 1 | 0 | 38904.6354 | 1 | 0 | 1051.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6356 | 1 | 0 | 38904.6356 | 1 | 0 | 1068.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6358 | 1 | 0 | 38904.6358 | 1 | 0 | 1085.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.636 | 1 | 0 | 38904.636 | 1 | 0 | 1102 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6362 | 1 | 0 | 38904.6362 | 1 | 0 | 1119 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6364 | 1 | 0 | 38904.6364 | 1 | 0 | 1135.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6366 | 1 | 0 | 38904.6366 | 2 | 0 | 1152.5 | 1299.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.6368 | 1 | 0 | 38904.6368 | 1 | 0 | 1169.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.637 | 1 | 0 | 38904.637 | 1 | 0 | 1186 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6372 | 1 | 0 | 38904.6372 | 1 | 0 | 1203 | 1350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6373 | 1 | 0 | 38904.6374 | 1 | 0 | 1219.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6375 | 1 | 0 | 38904.6376 | 1 | 0 | 1236.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6377 | 1 | 0 | 38904.6378 | 1 | 0 | 1253.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6379 | 1 | 0 | 38904.638 | 1 | 0 | 1270 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6381 | 1 | 0 | 38904.6381 | 1 | 0 | 1287 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6383 | 1 | 0 | 38904.6383 | 1 | 0 | 1303.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6385 | 1 | 0 | 38904.6385 | 1 | 0 | 1320.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6387 | 1 | 0 | 38904.6387 | 1 | 0 | 1337.5 | 1484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6389 | 1 | 0 | 38904.6389 | 1 | 0 | 1354 | 1501 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6391 | 1 | 0 | 38904.6391 | 1 | 0 | 1371 | 1518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6393 | 1 | 0 | 38904.6393 | 1 | 0 | 1387.5 | 1534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6395 | 1 | 0 | 38904.6395 | 1 | 0 | 1404.5 | 1551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6397 | 1 | 0 | 38904.6397 | 1 | 0 | 1421.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6399 | 1 | 0 | 38904.6399 | 1 | 0 | 1438 | 1585 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6401 | 1 | 0 | 38904.6401 | 1 | 0 | 1455 | 1602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6403 | 1 | 0 | 38904.6403 | 1 | 0 | 1471.5 | 1618.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6405 | 1 | 0 | 38904.6405 | 1 | 0 | 1488.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6406 | 1 | 0 | 38904.6407 | 1 | 0 | 1505 | 1652 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6408 | 1 | 0 | 38904.6409 | 1 | 0 | 1522 | 1669 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.641 | 1 | 0 | 38904.6411 | 1 | 0 | 1538.5 | 1685.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6412 | 1 | 0 | 38904.6413 | 1 | 0 | 1555.5 | 1702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6414 | 1 | 0 | 38904.6414 | 1 | 0 | 1572.5 | 1719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6416 | 1 | 0 | 38904.6416 | 1 | 0 | 1589 | 1736 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6418 | 1 | 0 | 38904.6418 | 1 | 0 | 1606 | 1753 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.642 | 1 | 0 | 38904.642 | 1 | 0 | 1622.5 | 1769.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6422 | 1 | 0 | 38904.6422 | 1 | 0 | 1639.5 | 1786.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6424 | 1 | 0 |  | 1 | 0 | 1656 | 1803 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6426 | 1 | 0 | 38904.6426 | 1 | 0 | 1673 | 1820 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6428 | 1 | 0 | 38904.6428 | 1 | 0 | 1690 | 1837 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.643 | 1 | 0 | 38904.643 | 1 | 0 | 1706.5 | 1853.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6432 | 1 | 0 | 38904.6432 | 1 | 0 | 1723.5 | 1870.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6434 | 1 | 0 | 38904.6434 | 1 | 0 | 1740.5 | 1887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6436 | 1 | 0 | 38904.6436 | 1 | 0 | 1757.5 | 1904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6438 | 1 | 1 | 38904.6438 | 1 | 0 | 1774 | 1921 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 602889094.44 | 245538 | 245338.0814
38904.644 | 1 | 0 | 38904.644 | 1 | 0 | 1791 | 1938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6442 | 1 | 0 | 38904.6442 | 1 | 0 | 1807.5 | 1954.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6444 | 1 | 0 | 38904.6444 | 1 | 0 | 1824.5 | 1971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6445 | 1 | 0 | 38904.6446 | 1 | 0 | 1841.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6447 | 1 | 0 | 38904.6448 | 1 | 0 | 1858 | 2005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6449 | 1 | 0 | 38904.6449 | 1 | 0 | 1874.5 | 2021.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6451 | 1 | 0 | 38904.6451 | 1 | 0 | 1891.5 | 2038.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6453 | 1 | 0 | 38904.6453 | 1 | 0 | 1908.5 | 2055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6455 | 1 | 0 | 38904.6455 | 1 | 0 | 1925 | 2072 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6457 | 1 | 0 | 38904.6457 | 1 | 0 | 1942 | 2089 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6459 | 1 | 0 | 38904.6459 | 1 | 0 | 1958.5 | 2105.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6461 | 1 | 0 | 38904.6461 | 1 | 0 | 1975.5 | 2122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6463 | 1 | 0 | 38904.6463 | 1 | 0 | 1992.5 | 2139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6465 | 1 | 0 | 38904.6465 | 1 | 0 | 2009 | 2156 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6467 | 1 | 0 | 38904.6467 | 1 | 0 | 2026 | 2173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6469 | 1 | 0 | 38904.6469 | 1 | 0 | 2042.5 | 2189.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6471 | 1 | 0 | 38904.6471 | 1 | 0 | 2059.5 | 2206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6473 | 1 | 0 | 38904.6473 | 1 | 0 | 2076.5 | 2223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6475 | 1 | 0 | 38904.6475 | 1 | 0 | 2093 | 2240 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6477 | 1 | 0 | 38904.6477 | 1 | 0 | 2110 | 2257 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6478 | 1 | 0 | 38904.6479 | 1 | 0 | 2126.5 | 2273.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.648 | 1 | 0 | 38904.6481 | 1 | 0 | 2143.5 | 2290.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6482 | 1 | 0 | 38904.6483 | 1 | 0 | 2160.5 | 2307.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6484 | 1 | 0 | 38904.6484 | 1 | 0 | 2177 | 2324 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6486 | 1 | 0 | 38904.6486 | 1 | 0 | 2194 | 2341 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6488 | 1 | 0 | 38904.6488 | 1 | 0 | 2210.5 | 2357.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.649 | 1 | 0 | 38904.649 | 1 | 0 | 2227.5 | 2374.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6492 | 1 | 0 | 38904.6492 | 1 | 0 | 2244.5 | 2391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6494 | 1 | 0 | 38904.6494 | 2 | 0 | 2261 | 2408 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.6496 | 1 | 0 | 38904.6496 | 1 | 0 | 2278 | 2425 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6498 | 1 | 0 | 38904.6498 | 2 | 0 | 2294.5 | 2441.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.65 | 1 | 0 | 38904.65 | 1 | 0 | 2311.5 | 2458.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245538 | 245538 | 245537.9994
38904.6502 | 1 | 0 | 38904.6502 | 2 | 0 | 2328.5 | 2475.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245538 | 122719 | 245537.9994
38904.6504 | 2 | 1 | 38904.6504 | 11 | 1 | 2345 | 2492 | 0.1221 | 0.06105 | 0.67155 | 0.06105 | 0.001221 | 0.0006105 | 0.0067155 | 0.0006105 | 0.0006105 | 0.006105 | 246445.7606 | 24454.7923 | 244338.8549
38904.6506 | 247 | 280 | 38904.6506 | 940 | 875 | 2362 | 2509 | 15.0794 | 17.094 | 57.3871 | 53.4188 | 0.15079 | 0.17094 | 0.57387 | 0.53419 | 0.020147 | 0.039683 | 9752.5345 | 2706.4695 | 664.5116
38904.6508 | 1061 | 1085 | 38904.6508 | 1137 | 1080 | 2378.5 | 2525.5 | 64.7741 | 66.2393 | 69.4139 | 65.9341 | 0.64774 | 0.66239 | 0.69414 | 0.65934 | 0.014652 | 0.034799 | 2217.4921 | 2787.3372 | 27.6157
38904.651 | 924 | 1009 | 38904.651 | 1061 | 999 | 2395.5 | 2542.5 | 56.4103 | 61.5995 | 64.7741 | 60.989 | 0.5641 | 0.616 | 0.64774 | 0.60989 | 0.051893 | 0.037851 | 2016.5487 | 11198.9565 | 51.4121
38904.6512 | 980 | 909 | 38904.6512 | 1186 | 1124 | 2412.5 | 2559.5 | 59.8291 | 55.4945 | 72.4054 | 68.6203 | 0.59829 | 0.55495 | 0.72405 | 0.6862 | 0.043346 | 0.037851 | 2523.2664 | 7278.2104 | 61.5721
38904.6513 | 927 | 932 | 38904.6514 | 941 | 916 | 2429 | 2576 | 56.5934 | 56.8987 | 57.4481 | 55.9219 | 0.56593 | 0.56899 | 0.57448 | 0.55922 | 0.0030525 | 0.015263 | 9310.3769 | 8156.3944 | 63.3202
38904.6515 | 1179 | 1133 | 38904.6516 | 1203 | 1096 | 2446 | 2593 | 71.978 | 69.1697 | 73.4432 | 66.9109 | 0.71978 | 0.6917 | 0.73443 | 0.66911 | 0.028083 | 0.065324 | 565.1146 | 629.3077 | 10.9959
38904.6517 | 1184 | 1090 | 38904.6517 | 1207 | 1136 | 2462.5 | 2609.5 | 72.2833 | 66.5446 | 73.6874 | 69.3529 | 0.72283 | 0.66545 | 0.73687 | 0.69353 | 0.057387 | 0.043346 | 877.4807 | 2137.0976 | 15.9842
38904.6519 | 1042 | 956 | 38904.6519 | 1156 | 1056 | 2479.5 | 2626.5 | 63.6142 | 58.3639 | 70.5739 | 64.4689 | 0.63614 | 0.58364 | 0.70574 | 0.64469 | 0.052503 | 0.06105 | 5111.2661 | 1639.0017 | 45.1905
38904.6521 | 1212 | 1134 | 38904.6521 | 1069 | 1085 | 2496.5 | 2643.5 | 73.9927 | 69.2308 | 65.2625 | 66.2393 | 0.73993 | 0.69231 | 0.65263 | 0.66239 | 0.047619 | 0.009768 | 550.7149 | 766.4378 | 8.6103
38904.6523 | 1208 | 1106 | 38904.6523 | 1218 | 1120 | 2513 | 2660 | 73.7485 | 67.5214 | 74.359 | 68.3761 | 0.73748 | 0.67521 | 0.74359 | 0.68376 | 0.062271 | 0.059829 | 1713.9116 | 3792.6148 | 12.5427
38904.6525 | 1049 | 1023 | 38904.6525 | 1207 | 1132 | 2530 | 2677 | 64.0415 | 62.4542 | 73.6874 | 69.1087 | 0.64042 | 0.62454 | 0.73687 | 0.69109 | 0.015873 | 0.045788 | 1356.9196 | 1316.2847 | 34.9208
38904.6527 | 956 | 863 | 38904.6527 | 1179 | 871 | 2546.5 | 2693.5 | 58.3639 | 52.6862 | 71.978 | 53.1746 | 0.58364 | 0.52686 | 0.71978 | 0.53175 | 0.056777 | 0.18803 | 792.3957 | 895.7178 | 66.4389
38904.6529 | 1167 | 1128 | 38904.6529 | 1209 | 1095 | 2563.5 | 2710.5 | 71.2454 | 68.8645 | 73.8095 | 66.8498 | 0.71245 | 0.68864 | 0.7381 | 0.6685 | 0.02381 | 0.069597 | 466.8092 | 475.5254 | 11.8209
38904.6531 | 1140 | 1024 | 38904.6531 | 997 | 875 | 2580.5 | 2727.5 | 69.5971 | 62.5153 | 60.8669 | 53.4188 | 0.69597 | 0.62515 | 0.60867 | 0.53419 | 0.070818 | 0.074481 | 2310.8584 | 1734.5636 | 26.9964
38904.6533 | 975 | 871 | 38904.6533 | 1038 | 925 | 2597 | 2744 | 59.5238 | 53.1746 | 63.37 | 56.4713 | 0.59524 | 0.53175 | 0.6337 | 0.56471 | 0.063492 | 0.068987 | 2639.0789 | 1819.6048 | 66.4274
38904.6535 | 1004 | 969 | 38904.6535 | 1229 | 901 | 2614 | 2761 | 61.2943 | 59.1575 | 75.0305 | 55.0061 | 0.61294 | 0.59158 | 0.75031 | 0.55006 | 0.021368 | 0.20024 | 330.8986 | 239.899 | 35.2082
38904.6537 | 1059 | 948 | 38904.6537 | 1187 | 1063 | 2630.5 | 2777.5 | 64.652 | 57.8755 | 72.4664 | 64.8962 | 0.64652 | 0.57875 | 0.72466 | 0.64896 | 0.067766 | 0.075702 | 3280.9813 | 1385.7685 | 44.2125
38904.6539 | 1035 | 888 | 38904.6539 | 1150 | 1120 | 2647.5 | 2794.5 | 63.1868 | 54.2125 | 70.2076 | 68.3761 | 0.63187 | 0.54212 | 0.70208 | 0.68376 | 0.089744 | 0.018315 | 521.3504 | 706.8134 | 52.6206
38904.6541 | 1211 | 860 | 38904.6541 | 987 | 871 | 2664.5 | 2811.5 | 73.9316 | 52.5031 | 60.2564 | 53.1746 | 0.73932 | 0.52503 | 0.60256 | 0.53175 | 0.21429 | 0.070818 | 259.8308 | 670.2822 | 38.9941
38904.6543 | 1026 | 871 | 38904.6543 | 2029 | 154 | 2681 | 2828 | 62.6374 | 53.1746 | 123.8706 | 9.4017 | 0.62637 | 0.53175 | 1.2387 | 0.094017 | 0.094628 | 1.1447 | 30.4542 | 19.1773 | 10.3344
38904.6545 | 1903 | 23 | 38904.6545 | 1999 | 21 | 2698 | 2845 | 116.1783 | 1.4042 | 122.0391 | 1.2821 | 1.1618 | 0.014042 | 1.2204 | 0.012821 | 1.1477 | 1.2076 | 31.0201 | 23.9428 | 445.4645
38904.6547 | 1932 | 18 | 38904.6547 | 2095 | 18 | 2714.5 | 2861.5 | 117.9487 | 1.0989 | 127.8999 | 1.0989 | 1.1795 | 0.010989 | 1.279 | 0.010989 | 1.1685 | 1.268 | 28.913 | 17.9368 | 427.8574
38904.6548 | 2391 | 15 | 38904.6549 | 1966 | 14 | 2731.5 | 2878.5 | 145.9707 | 0.91575 | 120.0244 | 0.8547 | 1.4597 | 0.0091575 | 1.2002 | 0.008547 | 1.4505 | 1.1917 | 2.8041 | 33.7556 | 84.7619
38904.655 | 1918 | 12 | 38904.6551 | 1945 | 11 | 2748 | 2895 | 117.094 | 0.7326 | 118.7424 | 0.67155 | 1.1709 | 0.007326 | 1.1874 | 0.0067155 | 1.1636 | 1.1807 | 28.9217 | 26.972 | 931.8013
38904.6552 | 2183 | 11 | 38904.6553 | 2211 | 11 | 2765 | 2912 | 133.2723 | 0.67155 | 134.9817 | 0.67155 | 1.3327 | 0.0067155 | 1.3498 | 0.0067155 | 1.326 | 1.3431 | 13.1615 | 11.5941 | 247.8184
38904.6554 | 2363 | 11 | 38904.6554 | 2336 | 11 | 2781.5 | 2928.5 | 144.2613 | 0.67155 | 142.6129 | 0.67155 | 1.4426 | 0.0067155 | 1.4261 | 0.0067155 | 1.4359 | 1.4194 | 4.3175 | 5.8148 | 41.1547
38904.6556 | 1849 | 9 | 38904.6556 | 1909 | 9 | 2798.5 | 2945.5 | 112.8816 | 0.54945 | 116.5446 | 0.54945 | 1.1288 | 0.0054945 | 1.1654 | 0.0054945 | 1.1233 | 1.16 | 33.5717 | 29.2218 | 1503.5073
38904.6558 | 2044 | 7 | 38904.6558 | 2422 | 9 | 2815.5 | 2962.5 | 124.7863 | 0.42735 | 147.8632 | 0.54945 | 1.2479 | 0.0042735 | 1.4786 | 0.0054945 | 1.2436 | 1.4731 | 26.5607 | 1.4451 | 82.4943
38904.656 | 2130 | 9 | 38904.656 | 2065 | 8 | 2832.5 | 2979.5 | 130.0366 | 0.54945 | 126.0684 | 0.4884 | 1.3004 | 0.0054945 | 1.2607 | 0.004884 | 1.2949 | 1.2558 | 15.7302 | 19.5091 | 575.6692
38904.6562 | 2389 | 8 | 38904.6562 | 2095 | 6 | 2849 | 2996 | 145.8486 | 0.4884 | 127.8999 | 0.3663 | 1.4585 | 0.004884 | 1.279 | 0.003663 | 1.4536 | 1.2753 | 2.8803 | 19.2153 | 119.6371
38904.6564 | 2351 | 5 | 38904.6564 | 1874 | 6 | 2866 | 3013 | 143.5287 | 0.30525 | 114.4078 | 0.3663 | 1.4353 | 0.0030525 | 1.1441 | 0.003663 | 1.4322 | 1.1404 | 4.5206 | 33.5613 | 504.4695
38904.6566 | 1919 | 5 | 38904.6566 | 2019 | 5 | 2882.5 | 3029.5 | 117.1551 | 0.30525 | 123.2601 | 0.30525 | 1.1716 | 0.0030525 | 1.2326 | 0.0030525 | 1.1685 | 1.2295 | 28.4151 | 21.9084 | 1913.5009
38904.6568 | 2013 | 5 | 38904.6568 | 2393 | 6 | 2899.5 | 3046.5 | 122.8938 | 0.30525 | 146.0928 | 0.3663 | 1.2289 | 0.0030525 | 1.4609 | 0.003663 | 1.2259 | 1.4573 | 24.3397 | 2.6829 | 229.0819
38904.657 | 2168 | 5 | 38904.657 | 2409 | 6 | 2916 | 3063 | 132.3565 | 0.30525 | 147.0696 | 0.3663 | 1.3236 | 0.0030525 | 1.4707 | 0.003663 | 1.3205 | 1.467 | 15.0699 | 2.0049 | 111.3975
38904.6572 | 2336 | 4 | 38904.6572 | 1957 | 4 | 2933 | 3080 | 142.6129 | 0.2442 | 119.475 | 0.2442 | 1.4261 | 0.002442 | 1.1947 | 0.002442 | 1.4237 | 1.1923 | 5.1956 | 26.6192 | 611.666
38904.6574 | 2153 | 4 | 38904.6574 | 2171 | 5 | 2949.5 | 3096.5 | 131.4408 | 0.2442 | 132.5397 | 0.30525 | 1.3144 | 0.002442 | 1.3254 | 0.0030525 | 1.312 | 1.3223 | 14.3163 | 13.3914 | 883.9092
38904.6576 | 2026 | 4 | 38904.6576 | 2302 | 5 | 2966.5 | 3113.5 | 123.6874 | 0.2442 | 140.5372 | 0.30525 | 1.2369 | 0.002442 | 1.4054 | 0.0030525 | 1.2344 | 1.4023 | 21.9238 | 6.7883 | 677.605
38904.6578 | 1874 | 5 | 38904.6578 | 1895 | 3 | 2983.5 | 3130.5 | 114.4078 | 0.30525 | 115.6899 | 0.18315 | 1.1441 | 0.0030525 | 1.1569 | 0.0018315 | 1.141 | 1.1551 | 31.442 | 29.8216 | 2652.6267
38904.658 | 2413 | 5 | 38904.658 | 2288 | 5 | 3000.5 | 3147.5 | 147.3138 | 0.30525 | 139.6825 | 0.30525 | 1.4731 | 0.0030525 | 1.3968 | 0.0030525 | 1.4701 | 1.3938 | 1.8473 | 8.3674 | 59.2687
38904.6581 | 2175 | 4 | 38904.6582 | 2305 | 5 | 3017 | 3164 | 132.7839 | 0.2442 | 140.7204 | 0.30525 | 1.3278 | 0.002442 | 1.4072 | 0.0030525 | 1.3254 | 1.4042 | 13.3279 | 6.6909 | 434.8813
38904.6583 | 2359 | 5 | 38904.6584 | 1894 | 3 | 3033.5 | 3180.5 | 144.0171 | 0.30525 | 115.6288 | 0.18315 | 1.4402 | 0.0030525 | 1.1563 | 0.0018315 | 1.4371 | 1.1545 | 4.1654 | 30.9174 | 436.328
38904.6585 | 2018 | 4 | 38904.6586 | 1965 | 3 | 3050.5 | 3197.5 | 123.199 | 0.2442 | 119.9634 | 0.18315 | 1.232 | 0.002442 | 1.1996 | 0.0018315 | 1.2295 | 1.1978 | 21.9394 | 25.2206 | 2187.2066
38904.6587 | 1939 | 4 | 38904.6588 | 2026 | 2 | 3067.5 | 3214.5 | 118.3761 | 0.2442 | 123.6874 | 0.1221 | 1.1838 | 0.002442 | 1.2369 | 0.001221 | 1.1813 | 1.2357 | 26.9995 | 21.3419 | 2257.3659
38904.6589 | 2111 | 4 | 38904.6589 | 1912 | 3 | 3084 | 3231 | 128.8767 | 0.2442 | 116.7277 | 0.18315 | 1.2888 | 0.002442 | 1.1673 | 0.0018315 | 1.2863 | 1.1654 | 16.5008 | 28.7907 | 1907.8568
38904.6591 | 1883 | 4 | 38904.6591 | 2184 | 4 | 3101 | 3248 | 114.9573 | 0.2442 | 133.3333 | 0.2442 | 1.1496 | 0.002442 | 1.3333 | 0.002442 | 1.1471 | 1.3309 | 31.0409 | 12.5688 | 1589.3433
38904.6593 | 1857 | 4 | 38904.6593 | 1883 | 4 | 3117.5 | 3264.5 | 113.37 | 0.2442 | 114.9573 | 0.2442 | 1.1337 | 0.002442 | 1.1496 | 0.002442 | 1.1313 | 1.1471 | 32.5754 | 30.7159 | 3497.591
38904.6595 | 2154 | 4 | 38904.6595 | 2051 | 3 | 3134.5 | 3281.5 | 131.5018 | 0.2442 | 125.2137 | 0.18315 | 1.315 | 0.002442 | 1.2521 | 0.0018315 | 1.3126 | 1.2503 | 14.1962 | 20.0003 | 1243.2665
38904.6597 | 5 | 1 | 38904.6597 | 2440 | 1 | 3151.5 | 3298.5 | 0.30525 | 0.06105 | 148.9621 | 0.06105 | 0.0030525 | 0.0006105 | 1.4896 | 0.0006105 | 0.002442 | 1.489 | 1691.7187 | 0.7097 | 1726.7785
38904.6599 | 5 | 1 | 38904.6599 | 2325 | 1 | 3168 | 3315 | 0.30525 | 0.06105 | 141.9414 | 0.06105 | 0.0030525 | 0.0006105 | 1.4194 | 0.0006105 | 0.002442 | 1.4188 | 17907.4165 | 10.3208 | 22923.9105
38904.6601 | 63 | 1 | 38904.6601 | 2237 | 1 | 3185 | 3332 | 3.8462 | 0.06105 | 136.569 | 0.06105 | 0.038462 | 0.0006105 | 1.3657 | 0.0006105 | 0.037851 | 1.3651 | 4619.7346 | 9.8114 | 21375.3045
38904.6603 | 5 | 1 | 38904.6603 | 2290 | 1 | 3201.5 | 3348.5 | 0.30525 | 0.06105 | 139.8046 | 0.06105 | 0.0030525 | 0.0006105 | 1.398 | 0.0006105 | 0.002442 | 1.3974 | 25122.5518 | 17.3681 | 36260.6312
38904.6605 | 5 | 1 | 38904.6605 | 2248 | 1 | 3218.5 | 3365.5 | 0.30525 | 0.06105 | 137.2405 | 0.06105 | 0.0030525 | 0.0006105 | 1.3724 | 0.0006105 | 0.002442 | 1.3718 | 36139.0019 | 35.9299 | 64770.0728
38904.6607 | 104 | 1 | 38904.6607 | 1931 | 1 | 3235.5 | 3382.5 | 6.3492 | 0.06105 | 117.8877 | 0.06105 | 0.063492 | 0.0006105 | 1.1789 | 0.0006105 | 0.062882 | 1.1783 | 2368.3295 | 27.2224 | 50313.5673
38904.6609 | 142 | 1 | 38904.6609 | 2262 | 1 | 3252 | 3399 | 8.6691 | 0.06105 | 138.0952 | 0.06105 | 0.086691 | 0.0006105 | 1.381 | 0.0006105 | 0.086081 | 1.3803 | 1788.9836 | 8.5973 | 18314.2748
38904.6611 | 5 | 0 | 38904.6611 | 1909 | 1 | 3269 | 3416 | 0.30525 | 0 | 116.5446 | 0.06105 | 0.0030525 | 0 | 1.1654 | 0.0006105 | 0.0030525 | 1.1648 | 49027.6 | 28.7411 | 49027.5969
38904.6613 | 4 | 1 | 38904.6613 | 2363 | 1 | 3285.5 | 3432.5 | 0.2442 | 0.06105 | 144.2613 | 0.06105 | 0.002442 | 0.0006105 | 1.4426 | 0.0006105 | 0.0018315 | 1.442 | 10999.8869 | 5.1828 | 12078.9809
38904.6615 | 5 | 1 | 38904.6615 | 2351 | 0 | 3302.5 | 3449.5 | 0.30525 | 0.06105 | 143.5287 | 0 | 0.0030525 | 0.0006105 | 1.4353 | 0 | 0.002442 | 1.4353 | 13388.3961 | 6.9882 | 16005.3705
38904.6617 | 5 | 1 | 38904.6617 | 2420 | 0 | 3319.5 | 3466.5 | 0.30525 | 0.06105 | 147.7411 | 0 | 0.0030525 | 0.0006105 | 1.4774 | 0 | 0.002442 | 1.4774 | 3920.9492 | 1.7088 | 4116.8973
38904.6618 | 5 | 1 | 38904.6619 | 2402 | 1 | 3336 | 3483 | 0.30525 | 0.06105 | 146.6422 | 0.06105 | 0.0030525 | 0.0006105 | 1.4664 | 0.0006105 | 0.002442 | 1.4658 | 6105.1644 | 2.7661 | 6595.4534
38904.662 | 5 | 1 | 38904.6621 | 2426 | 1 | 3353 | 3500 | 0.30525 | 0.06105 | 148.1074 | 0.06105 | 0.0030525 | 0.0006105 | 1.4811 | 0.0006105 | 0.002442 | 1.4805 | 3233.0181 | 1.3923 | 3364.8311

## C1-3
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 148.3138 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38904.6216 | 1 | 0 | 38904.6216 | 1 | 0 | -143.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6218 | 1 | 0 | 38904.6218 | 1 | 0 | -127 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.622 | 1 | 0 | 38904.622 | 1 | 0 | -110.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6222 | 1 | 0 | 38904.6222 | 2 | 0 | -93.5 | 53.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 242838 | 121369 | 242837.9994
38904.6223 | 1 | 0 | 38904.6224 | 1 | 0 | -76.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6225 | 1 | 0 | 38904.6226 | 1 | 0 | -59.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6227 | 1 | 0 | 38904.6228 | 1 | 0 | -43 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6229 | 1 | 0 | 38904.623 | 1 | 0 | -26 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6231 | 2 | 0 | 38904.6231 | 1 | 0 | -9.5 | 137.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121369 | 242838 | 121368.9988
38904.6233 | 1 | 0 | 38904.6233 | 1 | 0 | 7.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6235 | 1 | 0 | 38904.6235 | 1 | 0 | 24 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6237 | 1 | 0 | 38904.6237 | 1 | 0 | 41 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6239 | 1 | 0 | 38904.6239 | 1 | 0 | 58 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6241 | 1 | 0 | 38904.6241 | 1 | 0 | 74.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6243 | 1 | 0 | 38904.6243 | 1 | 0 | 91.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6245 | 1 | 0 | 38904.6245 | 1 | 0 | 108 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6247 | 1 | 0 | 38904.6247 | 1 | 0 | 125 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6249 | 1 | 0 | 38904.6249 | 1 | 0 | 142 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6251 | 1 | 0 | 38904.6251 | 1 | 0 | 158.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6253 | 1 | 0 | 38904.6253 | 1 | 0 | 175.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6255 | 1 | 0 | 38904.6255 | 1 | 0 | 192 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6256 | 1 | 0 | 38904.6257 | 1 | 0 | 209 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6258 | 1 | 0 | 38904.6259 | 1 | 0 | 226 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.626 | 1 | 0 | 38904.6261 | 1 | 0 | 242.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6262 | 1 | 0 | 38904.6263 | 1 | 0 | 259.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6264 | 1 | 0 | 38904.6264 | 1 | 0 | 276 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6266 | 1 | 0 | 38904.6266 | 1 | 0 | 293 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6268 | 1 | 0 | 38904.6268 | 1 | 0 | 310 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.627 | 1 | 0 | 38904.627 | 1 | 0 | 326.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6272 | 1 | 0 | 38904.6272 | 1 | 0 | 343.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6274 | 1 | 0 | 38904.6274 | 1 | 0 | 360 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6276 | 1 | 0 | 38904.6276 | 1 | 0 | 377 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6278 | 1 | 0 | 38904.6278 | 1 | 0 | 393.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.628 | 1 | 0 | 38904.628 | 1 | 0 | 410.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6282 | 1 | 0 | 38904.6282 | 1 | 0 | 427.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6284 | 1 | 0 | 38904.6284 | 1 | 0 | 444 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6286 | 1 | 0 | 38904.6286 | 1 | 0 | 461 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6288 | 1 | 0 | 38904.6288 | 1 | 0 | 477.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.629 | 1 | 0 | 38904.629 | 1 | 0 | 494.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6292 | 1 | 0 | 38904.6292 | 1 | 0 | 511.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6294 | 1 | 0 | 38904.6294 | 1 | 0 | 528.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6295 | 1 | 0 | 38904.6296 | 1 | 0 | 545 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6297 | 1 | 0 | 38904.6297 | 1 | 0 | 561.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6299 | 1 | 0 | 38904.6299 | 1 | 0 | 578.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6301 | 1 | 0 | 38904.6301 | 1 | 0 | 595.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6303 | 1 | 0 | 38904.6303 | 1 | 0 | 612 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6305 | 1 | 0 | 38904.6305 | 1 | 0 | 629 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6307 | 1 | 0 | 38904.6307 | 2 | 0 | 645.5 | 792.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 242838 | 121369 | 242837.9994
38904.6309 | 1 | 0 | 38904.6309 | 1 | 0 | 662.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6311 | 1 | 0 | 38904.6311 | 1 | 0 | 679.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6313 | 1 | 0 | 38904.6313 | 1 | 0 | 696 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6315 | 1 | 0 | 38904.6315 | 1 | 0 | 713 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6317 | 1 | 0 | 38904.6317 | 1 | 0 | 729.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6319 | 1 | 0 | 38904.6319 | 1 | 0 | 746.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6321 | 1 | 0 | 38904.6321 | 1 | 0 | 763.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6323 | 1 | 0 | 38904.6323 | 1 | 0 | 780 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6325 | 1 | 0 | 38904.6325 | 1 | 0 | 797 | 944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6327 | 1 | 0 | 38904.6327 | 1 | 0 | 813.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6328 | 1 | 0 | 38904.6329 | 1 | 0 | 830.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.633 | 1 | 0 | 38904.6331 | 1 | 0 | 847.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6332 | 1 | 0 | 38904.6333 | 1 | 0 | 864 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6334 | 1 | 0 | 38904.6334 | 1 | 0 | 881 | 1028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6336 | 1 | 0 | 38904.6336 | 1 | 0 | 897.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6338 | 2 | 0 | 38904.6338 | 1 | 0 | 914.5 | 1061.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121369 | 242838 | 121368.9988
38904.634 | 1 | 0 | 38904.634 | 1 | 0 | 931.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6342 | 1 | 0 | 38904.6342 | 1 | 0 | 948 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6344 | 1 | 0 | 38904.6344 | 1 | 0 | 965 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6346 | 1 | 0 | 38904.6346 | 1 | 0 | 981.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6348 | 1 | 0 | 38904.6348 | 1 | 0 | 998.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.635 | 1 | 0 | 38904.635 | 1 | 0 | 1015.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6352 | 1 | 0 | 38904.6352 | 1 | 0 | 1032 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6354 | 1 | 0 | 38904.6354 | 1 | 0 | 1049 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6356 | 1 | 0 | 38904.6356 | 1 | 0 | 1065.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6358 | 1 | 0 | 38904.6358 | 1 | 0 | 1082.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.636 | 1 | 0 | 38904.636 | 1 | 0 | 1099.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6361 | 1 | 0 | 38904.6362 | 1 | 0 | 1116 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6363 | 1 | 0 | 38904.6364 | 1 | 0 | 1133 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6365 | 1 | 0 | 38904.6366 | 1 | 0 | 1149.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6367 | 1 | 0 | 38904.6367 | 1 | 0 | 1166.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6369 | 1 | 0 | 38904.6369 | 1 | 0 | 1183.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6371 | 1 | 0 | 38904.6371 | 1 | 0 | 1200 | 1347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6373 | 1 | 0 | 38904.6373 | 1 | 0 | 1217 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6375 | 1 | 0 | 38904.6375 | 1 | 0 | 1233.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6377 | 1 | 0 | 38904.6377 | 1 | 0 | 1250.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6379 | 1 | 0 | 38904.6379 | 1 | 0 | 1267 | 1414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6381 | 1 | 0 | 38904.6381 | 1 | 0 | 1284 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6383 | 1 | 0 | 38904.6383 | 1 | 0 | 1300.5 | 1447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6385 | 1 | 0 | 38904.6385 | 1 | 0 | 1317.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6387 | 1 | 0 | 38904.6387 | 1 | 0 | 1334.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6389 | 1 | 0 | 38904.6389 | 1 | 0 | 1351.5 | 1498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6391 | 1 | 0 | 38904.6391 | 1 | 0 | 1368 | 1515 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6393 | 1 | 0 | 38904.6393 | 1 | 0 | 1384.5 | 1531.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6395 | 1 | 0 | 38904.6395 | 1 | 0 | 1401.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6397 | 1 | 0 | 38904.6397 | 1 | 0 | 1418.5 | 1565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6398 | 1 | 0 | 38904.6399 | 1 | 0 | 1435 | 1582 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.64 | 1 | 0 | 38904.6401 | 1 | 0 | 1452 | 1599 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6402 | 1 | 0 | 38904.6403 | 1 | 0 | 1469 | 1616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6404 | 1 | 0 | 38904.6404 | 1 | 0 | 1485.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6406 | 1 | 0 | 38904.6406 | 1 | 0 | 1502.5 | 1649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6408 | 1 | 0 | 38904.6408 | 1 | 0 | 1519.5 | 1666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.641 | 1 | 0 | 38904.641 | 1 | 0 | 1536 | 1683 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6412 | 1 | 0 | 38904.6412 | 1 | 0 | 1552.5 | 1699.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6414 | 1 | 0 | 38904.6414 | 1 | 0 | 1569.5 | 1716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6416 | 1 | 0 | 38904.6416 | 1 | 0 | 1586.5 | 1733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6418 | 1 | 0 | 38904.6418 | 1 | 0 | 1603 | 1750 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.642 | 1 | 0 | 38904.642 | 1 | 0 | 1620 | 1767 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6422 | 1 | 0 | 38904.6422 | 1 | 0 | 1637 | 1784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6424 | 1 | 0 | 38904.6424 | 1 | 0 | 1653.5 | 1800.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6426 | 1 | 0 | 38904.6426 | 1 | 0 | 1670.5 | 1817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6428 | 1 | 0 | 38904.6428 | 1 | 0 | 1687 | 1834 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.643 | 1 | 0 | 38904.643 | 1 | 0 | 1704 | 1851 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6431 | 1 | 0 | 38904.6432 | 1 | 0 | 1721 | 1868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6433 | 1 | 0 | 38904.6434 | 1 | 0 | 1737.5 | 1884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6435 | 1 | 0 | 38904.6436 | 1 | 0 | 1754.5 | 1901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6437 | 1 | 0 | 38904.6438 | 1 | 0 | 1771 | 1918 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6439 | 1 | 0 | 38904.6439 | 1 | 0 | 1788 | 1935 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6441 | 1 | 0 | 38904.6441 | 1 | 0 | 1804.5 | 1951.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6443 | 1 | 0 | 38904.6443 | 1 | 0 | 1821.5 | 1968.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6445 | 1 | 0 | 38904.6445 | 1 | 0 | 1838.5 | 1985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6447 | 1 | 0 | 38904.6447 | 1 | 0 | 1855 | 2002 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6449 | 1 | 0 | 38904.6449 | 1 | 0 | 1872 | 2019 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6451 | 1 | 0 | 38904.6451 | 1 | 0 | 1888.5 | 2035.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6453 | 1 | 0 | 38904.6453 | 1 | 0 | 1905.5 | 2052.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6455 | 1 | 0 | 38904.6455 | 1 | 0 | 1922.5 | 2069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6457 | 1 | 0 | 38904.6457 | 1 | 0 | 1939 | 2086 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6459 | 1 | 0 | 38904.6459 | 1 | 0 | 1956 | 2103 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6461 | 1 | 0 | 38904.6461 | 1 | 0 | 1972.5 | 2119.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6463 | 1 | 0 | 38904.6463 | 1 | 0 | 1989.5 | 2136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6465 | 1 | 0 | 38904.6465 | 1 | 0 | 2006.5 | 2153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6466 | 1 | 0 | 38904.6467 | 1 | 0 | 2023 | 2170 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6468 | 1 | 0 | 38904.6469 | 1 | 0 | 2040 | 2187 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.647 | 1 | 0 | 38904.647 | 1 | 0 | 2056.5 | 2203.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6472 | 1 | 0 | 38904.6472 | 1 | 0 | 2073.5 | 2220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6474 | 1 | 0 | 38904.6474 | 1 | 0 | 2090.5 | 2237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6476 | 1 | 0 | 38904.6476 | 1 | 0 | 2107 | 2254 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6478 | 1 | 0 | 38904.6478 | 1 | 0 | 2124 | 2271 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.648 | 1 | 0 | 38904.648 | 1 | 0 | 2140.5 | 2287.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6482 | 1 | 0 | 38904.6482 | 1 | 0 | 2157.5 | 2304.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6484 | 1 | 0 | 38904.6484 | 1 | 0 | 2174.5 | 2321.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6486 | 1 | 0 | 38904.6486 | 1 | 0 | 2191 | 2338 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6488 | 1 | 0 | 38904.6488 | 1 | 0 | 2208 | 2355 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.649 | 1 | 0 | 38904.649 | 1 | 0 | 2224.5 | 2371.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6492 | 1 | 0 | 38904.6492 | 1 | 0 | 2241.5 | 2388.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6494 | 1 | 0 | 38904.6494 | 1 | 0 | 2258.5 | 2405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6496 | 1 | 0 | 38904.6496 | 1 | 0 | 2275 | 2422 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6498 | 1 | 0 | 38904.6498 | 1 | 0 | 2292 | 2439 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.65 | 1 | 0 | 38904.65 | 1 | 0 | 2308.5 | 2455.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6502 | 1 | 0 | 38904.6502 | 1 | 0 | 2325.5 | 2472.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38904.6503 | 2 | 1 | 38904.6504 | 2 | 1 | 2342.5 | 2489.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242538.1235
38904.6505 | 3 | 3 | 38904.6506 | 2 | 3 | 2359 | 2506 | 0.18315 | 0.18315 | 0.1221 | 0.18315 | 0.0018315 | 0.0018315 | 0.001221 | 0.0018315 | 0 | 0.0006105 | 196324576.1467 | 242737.6291 | 80746.0686
38904.6507 | 10 | 17 | 38904.6508 | 3 | 13 | 2376 | 2523 | 0.6105 | 1.0379 | 0.18315 | 0.79365 | 0.006105 | 0.010379 | 0.0018315 | 0.0079365 | 0.0042735 | 0.006105 | 34910.6925 | 24354.4909 | 14073.8595
38904.6509 | 49 | 23 | 38904.6509 | 58 | 59 | 2392.5 | 2539.5 | 2.9915 | 1.4042 | 3.5409 | 3.602 | 0.029915 | 0.014042 | 0.035409 | 0.03602 | 0.015873 | 0.0006105 | 9156.5225 | 666772.4337 | 10247.9413
38904.6511 | 971 | 1034 | 38904.6511 | 944 | 875 | 2409.5 | 2556.5 | 59.2796 | 63.1258 | 57.6313 | 53.4188 | 0.5928 | 0.63126 | 0.57631 | 0.53419 | 0.038462 | 0.042125 | 5674.0066 | 2772.3279 | 39.6137
38904.6513 | 1131 | 1046 | 38904.6513 | 1039 | 953 | 2426.5 | 2573.5 | 69.0476 | 63.8584 | 63.431 | 58.1807 | 0.69048 | 0.63858 | 0.63431 | 0.58181 | 0.051893 | 0.052503 | 2864.0083 | 2637.0434 | 23.2466
38904.6515 | 1034 | 937 | 38904.6515 | 1008 | 982 | 2443 | 2590 | 63.1258 | 57.2039 | 61.5385 | 59.9512 | 0.63126 | 0.57204 | 0.61538 | 0.59951 | 0.059219 | 0.015873 | 936.6697 | 1802.8776 | 46.3491
38904.6517 | 1139 | 1040 | 38904.6517 | 1030 | 1050 | 2460 | 2607 | 69.536 | 63.4921 | 62.8816 | 64.1026 | 0.69536 | 0.63492 | 0.62882 | 0.64103 | 0.06044 | 0.01221 | 606.2004 | 913.3735 | 21.6993
38904.6519 | 1067 | 1078 | 38904.6519 | 1000 | 984 | 2476.5 | 2623.5 | 65.1404 | 65.812 | 61.0501 | 60.0733 | 0.6514 | 0.65812 | 0.6105 | 0.60073 | 0.0067155 | 0.009768 | 58145.0089 | 12452.4557 | 26.1702
38904.6521 | 1192 | 894 | 38904.6521 | 1117 | 1097 | 2493.5 | 2640.5 | 72.7717 | 54.5788 | 68.1929 | 66.9719 | 0.72772 | 0.54579 | 0.68193 | 0.66972 | 0.18193 | 0.01221 | 172.3416 | 212.8667 | 26.1328
38904.6523 | 974 | 883 | 38904.6523 | 999 | 900 | 2510.5 | 2657.5 | 59.4628 | 53.9072 | 60.989 | 54.9451 | 0.59463 | 0.53907 | 0.60989 | 0.54945 | 0.055556 | 0.06044 | 3010.8054 | 2069.7848 | 61.8347
38904.6525 | 1065 | 1076 | 38904.6525 | 916 | 928 | 2527 | 2674 | 65.0183 | 65.6899 | 55.9219 | 56.6545 | 0.65018 | 0.6569 | 0.55922 | 0.56654 | 0.0067155 | 0.007326 | 28547.4168 | 17297.2184 | 26.6471
38904.6527 | 1042 | 1014 | 38904.6527 | 1141 | 1106 | 2544 | 2691 | 63.6142 | 61.9048 | 69.6581 | 67.5214 | 0.63614 | 0.61905 | 0.69658 | 0.67521 | 0.017094 | 0.021368 | 113914.3138 | 3786.1131 | 35.8749
38904.6529 | 991 | 954 | 38904.6529 | 1114 | 1004 | 2560.5 | 2707.5 | 60.5006 | 58.2418 | 68.0098 | 61.2943 | 0.60501 | 0.58242 | 0.6801 | 0.61294 | 0.022589 | 0.067155 | 1660.1825 | 1921.8421 | 48.2623
38904.6531 | 1201 | 1085 | 38904.6531 | 1078 | 1066 | 2577.5 | 2724.5 | 73.3211 | 66.2393 | 65.812 | 65.0794 | 0.73321 | 0.66239 | 0.65812 | 0.65079 | 0.070818 | 0.007326 | 350.2142 | 462.1917 | 10.8642
38904.6533 | 1120 | 1013 | 38904.6533 | 1128 | 1009 | 2594.5 | 2741.5 | 68.3761 | 61.8437 | 68.8645 | 61.5995 | 0.68376 | 0.61844 | 0.68864 | 0.616 | 0.065324 | 0.07265 | 3646.3095 | 1424.9489 | 27.3391
38904.6534 | 971 | 1005 | 38904.6535 | 999 | 958 | 2611 | 2758 | 59.2796 | 61.3553 | 60.989 | 58.486 | 0.5928 | 0.61355 | 0.60989 | 0.58486 | 0.020757 | 0.025031 | 15121.9666 | 4126.313 | 44.045
38904.6536 | 1009 | 870 | 38904.6537 | 952 | 850 | 2628 | 2775 | 61.5995 | 53.1136 | 58.1197 | 51.8926 | 0.616 | 0.53114 | 0.5812 | 0.51893 | 0.08486 | 0.062271 | 1165.3145 | 5084.1902 | 62.0418
38904.6538 | 1201 | 1082 | 38904.6539 | 1189 | 1059 | 2644.5 | 2791.5 | 73.3211 | 66.0562 | 72.5885 | 64.652 | 0.73321 | 0.66056 | 0.72589 | 0.64652 | 0.07265 | 0.079365 | 5440.0002 | 1122.1798 | 12.4217
38904.654 | 1040 | 925 | 38904.6541 | 1041 | 928 | 2661.5 | 2808.5 | 63.4921 | 56.4713 | 63.5531 | 56.6545 | 0.63492 | 0.56471 | 0.63553 | 0.56654 | 0.070208 | 0.068987 | 1941.6261 | 2129.2535 | 47.9512
38904.6542 | 1130 | 972 | 38904.6542 | 1057 | 713 | 2678.5 | 2825.5 | 68.9866 | 59.3407 | 64.5299 | 43.5287 | 0.68987 | 0.59341 | 0.6453 | 0.43529 | 0.096459 | 0.21001 | 927.5835 | 5424.7914 | 33.0714
38904.6544 | 2356 | 18 | 38904.6544 | 7 | 19 | 2695 | 2842 | 143.8339 | 1.0989 | 0.42735 | 1.16 | 1.4383 | 0.010989 | 0.0042735 | 0.0116 | 1.4274 | 0.007326 | 3.1327 | 407.4561 | 247.0374
38904.6546 | 2254 | 16 | 38904.6546 | 7 | 16 | 2712 | 2859 | 137.6068 | 0.9768 | 0.42735 | 0.9768 | 1.3761 | 0.009768 | 0.0042735 | 0.009768 | 1.3663 | 0.0054945 | 7.8319 | 1240.3921 | 921.8091
38904.6548 | 2310 | 14 | 38904.6548 | 8 | 13 | 2728.5 | 2875.5 | 141.0256 | 0.8547 | 0.4884 | 0.79365 | 1.4103 | 0.008547 | 0.004884 | 0.0079365 | 1.4017 | 0.0030525 | 5.1963 | 987.5948 | 683.5052
38904.655 | 2280 | 8 | 38904.655 | 7 | 9 | 2745.5 | 2892.5 | 139.1941 | 0.4884 | 0.42735 | 0.54945 | 1.3919 | 0.004884 | 0.0042735 | 0.0054945 | 1.3871 | 0.001221 | 6.5735 | 1795.5175 | 1674.0169
38904.6552 | 2388 | 8 | 38904.6552 | 7 | 8 | 2762.5 | 2909.5 | 145.7875 | 0.4884 | 0.42735 | 0.4884 | 1.4579 | 0.004884 | 0.0042735 | 0.004884 | 1.453 | 0.0006105 | 1.7375 | 527.2703 | 350.7316
38904.6554 | 2387 | 7 | 38904.6554 | 9 | 6 | 2779 | 2926 | 145.7265 | 0.42735 | 0.54945 | 0.3663 | 1.4573 | 0.0042735 | 0.0054945 | 0.003663 | 1.453 | 0.0018315 | 1.7799 | 724.4734 | 444.1254
38904.6556 | 2264 | 5 | 38904.6556 | 6 | 5 | 2796 | 2943 | 138.2173 | 0.30525 | 0.3663 | 0.30525 | 1.3822 | 0.0030525 | 0.003663 | 0.0030525 | 1.3791 | 0.0006105 | 7.3205 | 3600.7841 | 3120.9265
38904.6558 | 2306 | 5 | 38904.6558 | 7 | 4 | 2812.5 | 2959.5 | 140.7814 | 0.30525 | 0.42735 | 0.2442 | 1.4078 | 0.0030525 | 0.0042735 | 0.002442 | 1.4048 | 0.0018315 | 5.3617 | 3383.0426 | 2299.6249
38904.656 | 1944 | 4 | 38904.656 | 6 | 4 | 2829.5 | 2976.5 | 118.6813 | 0.2442 | 0.3663 | 0.2442 | 1.1868 | 0.002442 | 0.003663 | 0.002442 | 1.1844 | 0.001221 | 25.0193 | 17325.1231 | 11965.4359
38904.6562 | 2234 | 3 | 38904.6562 | 7 | 3 | 2846.5 | 2993.5 | 136.3858 | 0.18315 | 0.42735 | 0.18315 | 1.3639 | 0.0018315 | 0.0042735 | 0.0018315 | 1.362 | 0.002442 | 8.7574 | 8006.0426 | 6333.557
38904.6564 | 2051 | 3 | 38904.6564 | 6 | 3 | 2863 | 3010 | 125.2137 | 0.18315 | 0.3663 | 0.18315 | 1.2521 | 0.0018315 | 0.003663 | 0.0018315 | 1.2503 | 0.0018315 | 18.4754 | 18306.5513 | 12444.6872
38904.6566 | 1941 | 2 | 38904.6566 | 11 | 2 | 2879.5 | 3026.5 | 118.4982 | 0.1221 | 0.67155 | 0.1221 | 1.185 | 0.001221 | 0.0067155 | 0.001221 | 1.1838 | 0.0054945 | 25.1872 | 228264.1615 | 24308.3508
38904.6568 | 2299 | 2 | 38904.6568 | 7 | 2 | 2896.5 | 3043.5 | 140.3541 | 0.1221 | 0.42735 | 0.1221 | 1.4035 | 0.001221 | 0.0042735 | 0.001221 | 1.4023 | 0.0030525 | 5.676 | 8011.6157 | 6339.8666
38904.657 | 2255 | 2 | 38904.657 | 6 | 2 | 2913.5 | 3060.5 | 137.6679 | 0.1221 | 0.3663 | 0.1221 | 1.3767 | 0.001221 | 0.003663 | 0.001221 | 1.3755 | 0.002442 | 7.7398 | 11095.8966 | 8542.0164
38904.6572 | 1971 | 2 | 38904.6572 | 250 | 2 | 2930.5 | 3077.5 | 120.3297 | 0.1221 | 15.2625 | 0.1221 | 1.2033 | 0.001221 | 0.15263 | 0.001221 | 1.2021 | 0.1514 | 23.2824 | 910.3135 | 20560.3941
38904.6573 | 2159 | 1 | 38904.6574 | 7 | 1 | 2947 | 3094 | 131.8071 | 0.06105 | 0.42735 | 0.06105 | 1.3181 | 0.0006105 | 0.0042735 | 0.0006105 | 1.3175 | 0.003663 | 12.5292 | 122258.2887 | 26915.9843
38904.6575 | 2214 | 1 | 38904.6575 | 5 | 2 | 2963.5 | 3110.5 | 135.1648 | 0.06105 | 0.30525 | 0.1221 | 1.3516 | 0.0006105 | 0.0030525 | 0.001221 | 1.351 | 0.0018315 | 9.7325 | 13814.2938 | 21283.9282
38904.6577 | 2208 | 2 | 38904.6577 | 6 | 1 | 2980.5 | 3127.5 | 134.7985 | 0.1221 | 0.3663 | 0.06105 | 1.348 | 0.001221 | 0.003663 | 0.0006105 | 1.3468 | 0.0030525 | 10.0353 | 48811.3788 | 10946.5737
38904.6579 | 2004 | 1 | 38904.6579 | 6 | 1 | 2997.5 | 3144.5 | 122.3443 | 0.06105 | 0.3663 | 0.06105 | 1.2234 | 0.0006105 | 0.003663 | 0.0006105 | 1.2228 | 0.0030525 | 21.2371 | 832006.7678 | 42432.8999
38904.6581 | 2092 | 1 | 38904.6581 | 5 | 1 | 3014.5 | 3161.5 | 127.7167 | 0.06105 | 0.30525 | 0.06105 | 1.2772 | 0.0006105 | 0.0030525 | 0.0006105 | 1.2766 | 0.002442 | 16.1349 | 110311.3131 | 33607.5339
38904.6583 | 2379 | 1 | 38904.6583 | 6 | 1 | 3031 | 3178 | 145.2381 | 0.06105 | 0.3663 | 0.06105 | 1.4524 | 0.0006105 | 0.003663 | 0.0006105 | 1.4518 | 0.0030525 | 2.1186 | 5742.3867 | 4853.4797
38904.6585 | 2119 | 1 | 38904.6585 | 7 | 1 | 3047.5 | 3194.5 | 129.3651 | 0.06105 | 0.42735 | 0.06105 | 1.2937 | 0.0006105 | 0.0042735 | 0.0006105 | 1.293 | 0.003663 | 14.6544 | 294015.8395 | 30927.481
38904.6587 | 2401 | 1 | 38904.6587 | 6 | 1 | 3064.5 | 3211.5 | 146.5812 | 0.06105 | 0.3663 | 0.06105 | 1.4658 | 0.0006105 | 0.003663 | 0.0006105 | 1.4652 | 0.0030525 | 1.1825 | 3045.6811 | 2650.96
38904.6589 | 2212 | 1 | 38904.6589 | 5 | 1 | 3081.5 | 3228.5 | 135.0427 | 0.06105 | 0.30525 | 0.06105 | 1.3504 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3498 | 0.002442 | 9.8317 | 39285.7683 | 21583.0614
38904.6591 | 2343 | 1 | 38904.6591 | 6 | 1 | 3098 | 3245 | 143.0403 | 0.06105 | 0.3663 | 0.06105 | 1.4304 | 0.0006105 | 0.003663 | 0.0006105 | 1.4298 | 0.0030525 | 3.6883 | 10959.1416 | 8460.7969
38904.6593 | 2032 | 1 | 38904.6593 | 5 | 1 | 3115 | 3262 | 124.0537 | 0.06105 | 0.30525 | 0.06105 | 1.2405 | 0.0006105 | 0.0030525 | 0.0006105 | 1.2399 | 0.002442 | 19.5657 | 218220.3327 | 39619.8441
38904.6595 | 2413 | 1 | 38904.6595 | 6 | 1 | 3131.5 | 3278.5 | 147.3138 | 0.06105 | 0.3663 | 0.06105 | 1.4731 | 0.0006105 | 0.003663 | 0.0006105 | 1.4725 | 0.0030525 | 0.67909 | 1703.5305 | 1452.7228
38904.6597 | 2157 | 1 | 38904.6597 | 5 | 1 | 3148.5 | 3295.5 | 131.685 | 0.06105 | 0.30525 | 0.06105 | 1.3168 | 0.0006105 | 0.0030525 | 0.0006105 | 1.3162 | 0.002442 | 12.6336 | 61918.8006 | 27094.2423
38904.6599 | 5 | 1 | 38904.6599 | 5 | 1 | 3165.5 | 3312.5 | 0.30525 | 0.06105 | 0.30525 | 0.06105 | 0.0030525 | 0.0006105 | 0.0030525 | 0.0006105 | 0.002442 | 0.002442 | 60634.5 | 60634.5 | 241938.9879
| 5 | 1 | 38904.6601 | 6 | 1 | 3183 | 3330 | 0.30525 | 0.06105 | 0.3663 | 0.06105 | 0.0030525 | 0.0006105 | 0.003663 | 0.0006105 | 0.002442 | 0.0030525 | 60640.7687 | 48483.5904 | 241839.1937
38904.6603 | 6 | 1 | 38904.6603 | 5 | 1 | 3199 | 3346 | 0.3663 | 0.06105 | 0.30525 | 0.06105 | 0.003663 | 0.0006105 | 0.0030525 | 0.0006105 | 0.0030525 | 0.002442 | 48483.5904 | 60640.7687 | 241839.1937
38904.6605 | 5 | 1 | 38904.6605 | 5 | 0 | 3215.5 | 3362.5 | 0.30525 | 0.06105 | 0.30525 | 0 | 0.0030525 | 0.0006105 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 60640.7661 | 48487.6 | 241839.2349
38904.6606 | 5 | 1 | 38904.6607 | 5 | 0 | 3232.5 | 3379.5 | 0.30525 | 0.06105 | 0.30525 | 0 | 0.0030525 | 0.0006105 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 60640.7661 | 48487.6 | 241839.2349
38904.6608 | 6 | 1 | 38904.6609 | 5 | 1 | 3249.5 | 3396.5 | 0.3663 | 0.06105 | 0.30525 | 0.06105 | 0.003663 | 0.0006105 | 0.0030525 | 0.0006105 | 0.0030525 | 0.002442 | 48483.5904 | 60640.7687 | 241839.1937
38904.661 | 5 | 1 | 38904.6611 | 5 | 0 | 3266 | 3413 | 0.30525 | 0.06105 | 0.30525 | 0 | 0.0030525 | 0.0006105 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 60640.7661 | 48487.6 | 241839.2349
38904.6612 | 6 | 0 | 38904.6612 | 5 | 0 | 3283 | 3430 | 0.3663 | 0 | 0.30525 | 0 | 0.003663 | 0 | 0.0030525 | 0 | 0.003663 | 0.0030525 | 40389.6667 | 48487.6 | 40389.663
38904.6614 | 5 | 1 | 38904.6614 | 5 | 0 | 3299.5 | 3446.5 | 0.30525 | 0.06105 | 0.30525 | 0 | 0.0030525 | 0.0006105 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 60640.7661 | 48487.6 | 241839.2349
38904.6616 | 6 | 0 | 38904.6616 | 4 | 1 | 3316.5 | 3463.5 | 0.3663 | 0 | 0.2442 | 0.06105 | 0.003663 | 0 | 0.002442 | 0.0006105 | 0.003663 | 0.0018315 | 40389.6667 | 80879.3333 | 40389.663
38904.6618 | 5 | 0 | 38904.6618 | 5 | 0 | 3333.5 | 3480.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 48487.6 | 48487.6 | 48487.5969
38904.662 | 5 | 1 | 38904.662 | 5 | 1 | 3350 | 3497 | 0.30525 | 0.06105 | 0.30525 | 0.06105 | 0.0030525 | 0.0006105 | 0.0030525 | 0.0006105 | 0.002442 | 0.002442 | 60634.5 | 60634.5 | 241938.9879

## C1-2
Penlight Test 7 |  |  | 2006-07-06 | 14:56 |  | Vs = |  | 149.9011 |  | R = | 100
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38904.6215 | 1 | 0 | 38904.6216 | 1 | 0 | -146.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6217 | 2 | 0 | 38904.6217 | 1 | 0 | -129.5 | 17.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122669 | 245438 | 122668.9988
38904.6219 | 1 | 0 | 38904.6219 | 1 | 0 | -113 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6221 | 1 | 0 | 38904.6221 | 1 | 0 | -96 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6223 | 1 | 0 | 38904.6223 | 1 | 0 | -79.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6225 | 1 | 0 | 38904.6225 | 1 | 0 | -62.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6227 | 1 | 0 | 38904.6227 | 1 | 0 | -45.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6229 | 1 | 0 | 38904.6229 | 1 | 0 | -29 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6231 | 1 | 0 | 38904.6231 | 1 | 0 | -12 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6233 | 1 | 0 | 38904.6233 | 1 | 0 | 4.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6235 | 1 | 0 | 38904.6235 | 1 | 0 | 21.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6237 | 1 | 0 | 38904.6237 | 1 | 0 | 38.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6239 | 1 | 0 | 38904.6239 | 1 | 0 | 55 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6241 | 1 | 0 | 38904.6241 | 1 | 0 | 72 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6243 | 1 | 0 | 38904.6243 | 1 | 0 | 88.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6245 | 1 | 0 | 38904.6245 | 1 | 0 | 105.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6247 | 1 | 0 | 38904.6247 | 1 | 0 | 122.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6248 | 1 | 0 | 38904.6249 | 1 | 0 | 139 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.625 | 1 | 0 | 38904.625 | 1 | 0 | 155.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6252 | 1 | 0 | 38904.6252 | 1 | 0 | 172.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6254 | 1 | 0 | 38904.6254 | 1 | 0 | 189.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6256 | 1 | 0 | 38904.6256 | 1 | 0 | 206.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6258 | 1 | 0 | 38904.6258 | 1 | 0 | 223 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.626 | 1 | 0 | 38904.626 | 1 | 0 | 240 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6262 | 1 | 0 | 38904.6262 | 1 | 0 | 256.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6264 | 1 | 0 | 38904.6264 | 1 | 0 | 273.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6266 | 1 | 0 | 38904.6266 | 1 | 0 | 290.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6268 | 1 | 0 | 38904.6268 | 1 | 0 | 307 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.627 | 1 | 0 | 38904.627 | 1 | 0 | 323.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6272 | 2 | 0 | 38904.6272 | 1 | 0 | 340.5 | 487.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122669 | 245438 | 122668.9988
38904.6274 | 1 | 0 | 38904.6274 | 1 | 0 | 357.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6276 | 1 | 0 | 38904.6276 | 1 | 0 | 374.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6278 | 1 | 0 | 38904.6278 | 1 | 0 | 391 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.628 | 1 | 0 | 38904.628 | 1 | 0 | 408 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6281 | 1 | 0 | 38904.6282 | 1 | 0 | 424.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6283 | 1 | 0 | 38904.6284 | 1 | 0 | 441.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6285 | 1 | 0 | 38904.6286 | 1 | 0 | 458 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6287 | 1 | 0 | 38904.6288 | 1 | 0 | 475 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6289 | 1 | 0 | 38904.6289 | 1 | 0 | 492 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6291 | 2 | 0 | 38904.6291 | 1 | 0 | 508.5 | 655.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122669 | 245438 | 122668.9988
38904.6293 | 1 | 0 | 38904.6293 | 1 | 0 | 525.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6295 | 1 | 0 | 38904.6295 | 2 | 0 | 542.5 | 689.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245438 | 122669 | 245437.9994
38904.6297 | 1 | 0 | 38904.6297 | 1 | 0 | 559 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6299 | 1 | 0 | 38904.6299 | 1 | 0 | 575.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6301 | 1 | 0 | 38904.6301 | 1 | 0 | 592.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6303 | 1 | 0 | 38904.6303 | 1 | 0 | 609.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6305 | 1 | 0 | 38904.6305 | 2 | 0 | 626 | 773 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245438 | 122669 | 245437.9994
38904.6307 | 1 | 0 | 38904.6307 | 1 | 0 | 643 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6309 | 1 | 0 | 38904.6309 | 1 | 0 | 659.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6311 | 1 | 0 | 38904.6311 | 1 | 0 | 676.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6313 | 1 | 0 | 38904.6313 | 1 | 0 | 693.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6314 | 1 | 0 | 38904.6315 | 1 | 0 | 710 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6316 | 1 | 0 | 38904.6317 | 1 | 0 | 727 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6318 | 1 | 0 | 38904.6319 | 1 | 0 | 743.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.632 | 1 | 0 | 38904.632 | 1 | 0 | 760.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6322 | 1 | 0 | 38904.6322 | 1 | 0 | 777.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6324 | 1 | 0 | 38904.6324 | 1 | 0 | 794 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6326 | 1 | 0 | 38904.6326 | 1 | 0 | 811 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6328 | 1 | 0 | 38904.6328 | 1 | 0 | 827.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.633 | 1 | 0 | 38904.633 | 1 | 0 | 844.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6332 | 1 | 0 | 38904.6332 | 1 | 0 | 861.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6334 | 1 | 0 | 38904.6334 | 1 | 0 | 878 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6336 | 1 | 0 | 38904.6336 | 1 | 0 | 895 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6338 | 1 | 0 | 38904.6338 | 1 | 0 | 911.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.634 | 1 | 0 | 38904.634 | 1 | 0 | 928.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6342 | 1 | 0 | 38904.6342 | 1 | 0 | 945.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6344 | 1 | 0 | 38904.6344 | 1 | 0 | 962.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6346 | 1 | 0 | 38904.6346 | 1 | 0 | 979 | 1126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6348 | 1 | 0 | 38904.6348 | 1 | 0 | 995.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.635 | 1 | 0 | 38904.635 | 1 | 0 | 1012.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6352 | 1 | 0 | 38904.6352 | 1 | 0 | 1029.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6353 | 1 | 0 | 38904.6354 | 1 | 0 | 1046 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6355 | 1 | 0 | 38904.6356 | 1 | 0 | 1063 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6357 | 1 | 0 | 38904.6357 | 1 | 0 | 1079.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6359 | 1 | 0 | 38904.6359 | 1 | 0 | 1096.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6361 | 1 | 0 | 38904.6361 | 1 | 0 | 1113.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6363 | 1 | 0 | 38904.6363 | 1 | 0 | 1130 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6365 | 1 | 0 | 38904.6365 | 1 | 0 | 1147 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6367 | 1 | 0 | 38904.6367 | 1 | 0 | 1163.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6369 | 1 | 0 | 38904.6369 | 1 | 0 | 1180.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6371 | 1 | 0 | 38904.6371 | 1 | 0 | 1197.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6373 | 1 | 0 | 38904.6373 | 1 | 0 | 1214 | 1361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6375 | 1 | 0 | 38904.6375 | 1 | 0 | 1231 | 1378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6377 | 1 | 0 | 38904.6377 | 1 | 0 | 1247.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6379 | 1 | 0 | 38904.6379 | 1 | 0 | 1264.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6381 | 1 | 0 | 38904.6381 | 1 | 0 | 1281.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6383 | 1 | 0 | 38904.6383 | 1 | 0 | 1298 | 1445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6384 | 1 | 0 | 38904.6385 | 1 | 0 | 1314.5 | 1461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6386 | 1 | 0 | 38904.6387 | 1 | 0 | 1331.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6388 | 1 | 0 | 38904.6389 | 1 | 0 | 1348.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.639 | 1 | 0 | 38904.6391 | 1 | 0 | 1365.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
| 1 | 0 | 38904.6392 | 1 | 0 | 1383 | 1530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6394 | 1 | 0 | 38904.6394 | 1 | 0 | 1398.5 | 1545.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6396 | 1 | 0 | 38904.6396 | 1 | 0 | 1415.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6398 | 1 | 0 | 38904.6398 | 1 | 0 | 1432.5 | 1579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.64 | 1 | 0 | 38904.64 | 1 | 0 | 1449 | 1596 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6402 | 1 | 0 | 38904.6402 | 1 | 0 | 1466 | 1613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6404 | 1 | 0 | 38904.6404 | 1 | 0 | 1483 | 1630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6406 | 1 | 0 | 38904.6406 | 1 | 0 | 1499.5 | 1646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6408 | 1 | 0 | 38904.6408 | 1 | 0 | 1516.5 | 1663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.641 | 1 | 0 | 38904.641 | 1 | 0 | 1533.5 | 1680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6412 | 1 | 0 | 38904.6412 | 1 | 0 | 1550 | 1697 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6414 | 1 | 0 | 38904.6414 | 1 | 0 | 1566.5 | 1713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6416 | 1 | 0 | 38904.6416 | 1 | 0 | 1583.5 | 1730.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6418 | 1 | 0 | 38904.6418 | 1 | 0 | 1600.5 | 1747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6419 | 1 | 0 | 38904.642 | 1 | 0 | 1617 | 1764 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6421 | 1 | 0 | 38904.6422 | 1 | 0 | 1634 | 1781 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6423 | 1 | 0 | 38904.6423 | 1 | 0 | 1650.5 | 1797.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6425 | 1 | 0 | 38904.6425 | 2 | 0 | 1667.5 | 1814.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245438 | 122669 | 245437.9994
38904.6427 | 1 | 0 | 38904.6427 | 1 | 0 | 1684.5 | 1831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6429 | 1 | 0 | 38904.6429 | 1 | 0 | 1701 | 1848 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6431 | 1 | 0 | 38904.6431 | 1 | 0 | 1718 | 1865 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6433 | 1 | 0 | 38904.6433 | 1 | 0 | 1735 | 1882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6435 | 1 | 0 | 38904.6435 | 1 | 0 | 1751.5 | 1898.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6437 | 1 | 0 | 38904.6437 | 1 | 0 | 1768.5 | 1915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6439 | 1 | 0 | 38904.6439 | 1 | 0 | 1785 | 1932 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6441 | 1 | 0 | 38904.6441 | 1 | 0 | 1802 | 1949 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6443 | 1 | 0 | 38904.6443 | 1 | 0 | 1819 | 1966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6445 | 1 | 0 | 38904.6445 | 1 | 0 | 1835.5 | 1982.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6447 | 1 | 0 | 38904.6447 | 1 | 0 | 1852.5 | 1999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6449 | 1 | 0 | 38904.6449 | 1 | 0 | 1869 | 2016 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6451 | 1 | 0 | 38904.6451 | 1 | 0 | 1886 | 2033 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6453 | 1 | 0 | 38904.6453 | 1 | 0 | 1902.5 | 2049.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6455 | 1 | 0 | 38904.6455 | 1 | 0 | 1919.5 | 2066.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6456 | 1 | 0 | 38904.6457 | 1 | 0 | 1936.5 | 2083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6458 | 1 | 0 | 38904.6459 | 1 | 0 | 1953 | 2100 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.646 | 1 | 0 | 38904.6461 | 1 | 0 | 1970 | 2117 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6462 | 1 | 0 | 38904.6462 | 1 | 0 | 1986.5 | 2133.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6464 | 1 | 0 | 38904.6464 | 1 | 0 | 2003.5 | 2150.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6466 | 1 | 0 | 38904.6466 | 1 | 0 | 2020.5 | 2167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6468 | 1 | 0 | 38904.6468 | 1 | 0 | 2037 | 2184 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.647 | 1 | 0 | 38904.647 | 1 | 0 | 2054 | 2201 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6472 | 1 | 0 | 38904.6472 | 1 | 0 | 2070.5 | 2217.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6474 | 1 | 0 | 38904.6474 | 1 | 0 | 2087.5 | 2234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6476 | 1 | 0 | 38904.6476 | 1 | 0 | 2104.5 | 2251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6478 | 1 | 0 | 38904.6478 | 1 | 0 | 2121 | 2268 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.648 | 1 | 0 | 38904.648 | 1 | 0 | 2138 | 2285 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6482 | 1 | 0 | 38904.6482 | 1 | 0 | 2154.5 | 2301.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6484 | 1 | 0 | 38904.6484 | 1 | 0 | 2171.5 | 2318.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6486 | 1 | 0 | 38904.6486 | 1 | 0 | 2188.5 | 2335.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6488 | 1 | 0 | 38904.6488 | 1 | 0 | 2205 | 2352 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6489 | 1 | 0 | 38904.649 | 1 | 0 | 2222 | 2369 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6491 | 1 | 0 | 38904.6492 | 1 | 0 | 2238.5 | 2385.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6493 | 1 | 0 | 38904.6494 | 1 | 0 | 2255.5 | 2402.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6495 | 1 | 0 | 38904.6495 | 1 | 0 | 2272.5 | 2419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6497 | 1 | 0 | 38904.6497 | 1 | 0 | 2289 | 2436 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245438 | 245438 | 245437.9994
38904.6499 | 2 | 0 | 38904.6499 | 1 | 0 | 2306 | 2453 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122669 | 245438 | 122668.9988
38904.6501 | 1 | 0 | 38904.6501 | 2 | 0 | 2322.5 | 2469.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245438 | 122669 | 245437.9994
38904.6503 | 2 | 2 | 38904.6503 | 3 | 1 | 2339.5 | 2486.5 | 0.1221 | 0.1221 | 0.18315 | 0.06105 | 0.001221 | 0.001221 | 0.0018315 | 0.0006105 | 0 | 0.001221 | 150415451.11 | 122618.9592 | 122469.1222
38904.6505 | 89 | 92 | 38904.6505 | 335 | 295 | 2356.5 | 2503.5 | 5.4335 | 5.6166 | 20.4518 | 18.0098 | 0.054335 | 0.056166 | 0.20452 | 0.1801 | 0.0018315 | 0.02442 | 186132.9444 | 5322.0371 | 2426.5576
38904.6507 | 1050 | 995 | 38904.6507 | 1025 | 1051 | 2373 | 2520 | 64.1026 | 60.7448 | 62.5763 | 64.1636 | 0.64103 | 0.60745 | 0.62576 | 0.64164 | 0.033578 | 0.015873 | 1826.6402 | 4535.5138 | 40.3545
38904.6509 | 984 | 922 | 38904.6509 | 991 | 933 | 2390 | 2537 | 60.0733 | 56.2882 | 60.5006 | 56.9597 | 0.60073 | 0.56288 | 0.60501 | 0.5696 | 0.037851 | 0.035409 | 3468.8839 | 4708.0511 | 58.3464
38904.6511 | 928 | 921 | 38904.6511 | 1113 | 1039 | 2406.5 | 2553.5 | 56.6545 | 56.2271 | 67.9487 | 63.431 | 0.56654 | 0.56227 | 0.67949 | 0.63431 | 0.0042735 | 0.045177 | 1860.883 | 1226.7203 | 60.8767
38904.6513 | 900 | 818 | 38904.6513 | 1031 | 948 | 2423.5 | 2570.5 | 54.9451 | 49.9389 | 62.9426 | 57.8755 | 0.54945 | 0.49939 | 0.62943 | 0.57875 | 0.050061 | 0.050672 | 2944.4504 | 2803.6858 | 87.0398
38904.6515 | 1012 | 1023 | 38904.6515 | 897 | 935 | 2440.5 | 2587.5 | 61.7827 | 62.4542 | 54.7619 | 57.0818 | 0.61783 | 0.62454 | 0.54762 | 0.57082 | 0.0067155 | 0.023199 | 5949.0163 | 7713.4787 | 40.5669
38904.6517 | 895 | 860 | 38904.6517 | 1086 | 992 | 2457 | 2604 | 54.6398 | 52.5031 | 66.3004 | 60.5617 | 0.5464 | 0.52503 | 0.663 | 0.60562 | 0.021368 | 0.057387 | 3900.2335 | 17174.7607 | 80.9681
38904.6519 | 1008 | 917 | 38904.6519 | 1145 | 1080 | 2474 | 2621 | 61.5385 | 55.9829 | 69.9023 | 65.9341 | 0.61538 | 0.55983 | 0.69902 | 0.65934 | 0.055556 | 0.039683 | 1519.5577 | 21576.0256 | 57.5718
38904.6521 | 930 | 844 | 38904.6521 | 928 | 844 | 2490.5 | 2637.5 | 56.7766 | 51.5263 | 56.6545 | 51.5263 | 0.56777 | 0.51526 | 0.56654 | 0.51526 | 0.052503 | 0.051282 | 2675.3791 | 2911.8982 | 78.0518
38904.6523 | 908 | 818 | 38904.6523 | 909 | 856 | 2507.5 | 2654.5 | 55.4335 | 49.9389 | 55.4945 | 52.2589 | 0.55433 | 0.49939 | 0.55495 | 0.52259 | 0.054945 | 0.032357 | 1766.4642 | 34049.1212 | 88.9052
38904.6525 | 1045 | 953 | 38904.6525 | 894 | 847 | 2524.5 | 2671.5 | 63.7973 | 58.1807 | 54.5788 | 51.7094 | 0.63797 | 0.58181 | 0.54579 | 0.51709 | 0.056166 | 0.028694 | 1411.0916 | 11988.0658 | 47.5967
38904.6526 | 1131 | 825 | 38904.6527 | 908 | 822 | 2541 | 2688 | 69.0476 | 50.3663 | 55.4335 | 50.1832 | 0.69048 | 0.50366 | 0.55433 | 0.50183 | 0.18681 | 0.052503 | 340.6223 | 996.2335 | 55.0092
38904.6528 | 1160 | 1077 | 38904.6529 | 970 | 872 | 2558 | 2705 | 70.8181 | 65.7509 | 59.2186 | 53.2357 | 0.70818 | 0.65751 | 0.59219 | 0.53236 | 0.050672 | 0.059829 | 5552.1847 | 1804.9572 | 19.2123
38904.653 | 1030 | 926 | 38904.653 | 1059 | 951 | 2574.5 | 2721.5 | 62.8816 | 56.5324 | 64.652 | 58.0586 | 0.62882 | 0.56532 | 0.64652 | 0.58059 | 0.063492 | 0.065934 | 2454.3478 | 2016.3623 | 51.3805
38904.6532 | 912 | 826 | 38904.6532 | 969 | 870 | 2591.5 | 2738.5 | 55.6777 | 50.4274 | 59.1575 | 53.1136 | 0.55678 | 0.50427 | 0.59158 | 0.53114 | 0.052503 | 0.06044 | 3420.7797 | 2020.4384 | 82.754
38904.6534 | 1175 | 1064 | 38904.6534 | 963 | 922 | 2608.5 | 2755.5 | 71.7338 | 64.9573 | 58.7912 | 56.2882 | 0.71734 | 0.64957 | 0.58791 | 0.56288 | 0.067766 | 0.025031 | 761.9472 | 1865.3406 | 19.3017
38904.6536 | 972 | 929 | 38904.6536 | 1023 | 977 | 2625 | 2772 | 59.3407 | 56.7155 | 62.4542 | 59.6459 | 0.59341 | 0.56716 | 0.62454 | 0.59646 | 0.026252 | 0.028083 | 6454.072 | 4641.2011 | 58.4163
38904.6538 | 936 | 832 | 38904.6538 | 1176 | 1069 | 2642 | 2789 | 57.1429 | 50.7937 | 71.7949 | 65.2625 | 0.57143 | 0.50794 | 0.71795 | 0.65263 | 0.063492 | 0.065324 | 2394.7763 | 2051.565 | 78.7779
38904.654 | 912 | 843 | 38904.654 | 925 | 821 | 2658.5 | 2805.5 | 55.6777 | 51.4652 | 56.4713 | 50.1221 | 0.55678 | 0.51465 | 0.56471 | 0.50122 | 0.042125 | 0.063492 | 9316.1928 | 1607.755 | 78.2169
38904.6542 | 1129 | 776 | 38904.6542 | 1589 | 629 | 2675.5 | 2822.5 | 68.9255 | 47.3748 | 97.0085 | 38.4005 | 0.68926 | 0.47375 | 0.97009 | 0.384 | 0.21551 | 0.58608 | 150.5359 | 146.9404 | 42.2036
38904.6544 | 1907 | 18 | 38904.6544 | 2322 | 19 | 2692.5 | 2839.5 | 116.4225 | 1.0989 | 141.7582 | 1.16 | 1.1642 | 0.010989 | 1.4176 | 0.0116 | 1.1532 | 1.406 | 34.5846 | 5.9331 | 165.0309
38904.6546 | 1909 | 17 | 38904.6546 | 2014 | 16 | 2709 | 2856 | 116.5446 | 1.0379 | 122.9548 | 0.9768 | 1.1654 | 0.010379 | 1.2295 | 0.009768 | 1.1551 | 1.2198 | 30.0689 | 22.6955 | 576.0101
38904.6548 | 2163 | 14 | 38904.6548 | 2247 | 13 | 2726 | 2873 | 132.0513 | 0.8547 | 137.1795 | 0.79365 | 1.3205 | 0.008547 | 1.3718 | 0.0079365 | 1.312 | 1.3639 | 14.5833 | 9.7153 | 176.0761
38904.655 | 2066 | 9 | 38904.655 | 2291 | 9 | 2742.5 | 2889.5 | 126.1294 | 0.54945 | 139.8657 | 0.54945 | 1.2613 | 0.0054945 | 1.3987 | 0.0054945 | 1.2558 | 1.3932 | 20.1281 | 7.3473 | 289.2754
38904.6552 | 1934 | 8 | 38904.6552 | 2404 | 8 | 2759.5 | 2906.5 | 118.0708 | 0.4884 | 146.7643 | 0.4884 | 1.1807 | 0.004884 | 1.4676 | 0.004884 | 1.1758 | 1.4628 | 33.4936 | 2.166 | 136.0508
38904.6554 | 2380 | 7 | 38904.6554 | 2286 | 7 | 2776.5 | 2923.5 | 145.2991 | 0.42735 | 139.5604 | 0.42735 | 1.453 | 0.0042735 | 1.3956 | 0.0042735 | 1.4487 | 1.3913 | 3.2952 | 8.1962 | 74
38904.6556 | 1880 | 6 | 38904.6556 | 1970 | 6 | 2793 | 2940 | 114.7741 | 0.3663 | 120.2686 | 0.3663 | 1.1477 | 0.003663 | 1.2027 | 0.003663 | 1.1441 | 1.199 | 31.1023 | 24.959 | 1895.4428
38904.6558 | 1931 | 5 | 38904.6558 | 2418 | 5 | 2810 | 2957 | 117.8877 | 0.30525 | 147.619 | 0.30525 | 1.1789 | 0.0030525 | 1.4762 | 0.0030525 | 1.1758 | 1.4731 | 32.6659 | 1.559 | 159.4566
38904.6559 | 2273 | 4 | 38904.656 | 2319 | 4 | 2826.5 | 2973.5 | 138.7668 | 0.2442 | 141.5751 | 0.2442 | 1.3877 | 0.002442 | 1.4158 | 0.002442 | 1.3852 | 1.4133 | 8.2805 | 6.0167 | 253.0869
38904.6561 | 1859 | 4 | 38904.6562 | 2211 | 3 | 2843.5 | 2990.5 | 113.4921 | 0.2442 | 134.9817 | 0.18315 | 1.1349 | 0.002442 | 1.3498 | 0.0018315 | 1.1325 | 1.348 | 32.786 | 11.114 | 1481.2957
38904.6563 | 2337 | 3 | 38904.6564 | 2434 | 3 | 2860.5 | 3007.5 | 142.674 | 0.18315 | 148.5958 | 0.18315 | 1.4267 | 0.0018315 | 1.486 | 0.0018315 | 1.4249 | 1.4841 | 5.919 | 0.8982 | 34.2373
38904.6565 | 2263 | 1 | 38904.6566 | 2408 | 2 | 2877 | 3024 | 138.1563 | 0.06105 | 147.0085 | 0.1221 | 1.3816 | 0.0006105 | 1.4701 | 0.001221 | 1.381 | 1.4689 | 8.6983 | 1.9882 | 373.0922
38904.6567 | 1928 | 1 | 38904.6567 | 2439 | 2 | 2894 | 3041 | 117.7045 | 0.06105 | 148.9011 | 0.1221 | 1.177 | 0.0006105 | 1.489 | 0.001221 | 1.1764 | 1.4878 | 29.6509 | 0.674 | 352.4067
38904.6569 | 1929 | 2 | 38904.6569 | 2154 | 2 | 2910.5 | 3057.5 | 117.7656 | 0.1221 | 131.5018 | 0.1221 | 1.1777 | 0.001221 | 1.315 | 0.001221 | 1.1764 | 1.3138 | 27.5193 | 14.0521 | 3230.384
38904.6571 | 1847 | 1 | 38904.6571 | 1963 | 1 | 2927.5 | 3074.5 | 112.7595 | 0.06105 | 119.8413 | 0.06105 | 1.1276 | 0.0006105 | 1.1984 | 0.0006105 | 1.127 | 1.1978 | 33.0278 | 25.1346 | 12199.869
38904.6573 | 2395 | 2 | 38904.6573 | 2415 | 2 | 2944 | 3091 | 146.2149 | 0.1221 | 147.4359 | 0.1221 | 1.4621 | 0.001221 | 1.4744 | 0.001221 | 1.4609 | 1.4731 | 2.6515 | 1.7274 | 49.5676
38904.6575 | 1947 | 1 | 38904.6575 | 2437 | 1 | 2961 | 3108 | 118.8645 | 0.06105 | 148.779 | 0.06105 | 1.1886 | 0.0006105 | 1.4878 | 0.0006105 | 1.188 | 1.4872 | 28.0306 | 0.75562 | 380.5124
38904.6577 | 1892 | 2 | 38904.6577 | 2433 | 1 | 2977.5 | 3124.5 | 115.5067 | 0.1221 | 148.5348 | 0.06105 | 1.1551 | 0.001221 | 1.4853 | 0.0006105 | 1.1538 | 1.4847 | 33.6763 | 0.92136 | 256.2542
38904.6579 | 2108 | 2 | 38904.6579 | 2435 | 1 | 2994.5 | 3141.5 | 128.6935 | 0.1221 | 148.6569 | 0.06105 | 1.2869 | 0.001221 | 1.4866 | 0.0006105 | 1.2857 | 1.486 | 18.5997 | 0.83916 | 143.7083
38904.6581 | 2407 | 1 | 38904.6581 | 2083 | 1 | 3011.5 | 3158.5 | 146.9475 | 0.06105 | 127.1673 | 0.06105 | 1.4695 | 0.0006105 | 1.2717 | 0.0006105 | 1.4689 | 1.2711 | 2.0154 | 18.3223 | 733.6846
38904.6583 | 2191 | 1 | 38904.6583 | 2414 | 2 | 3028.5 | 3175.5 | 133.7607 | 0.06105 | 147.3748 | 0.1221 | 1.3376 | 0.0006105 | 1.4737 | 0.001221 | 1.337 | 1.4725 | 12.4 | 1.7271 | 447.1704
38904.6585 | 2333 | 1 | 38904.6585 | 1910 | 1 | 3045 | 3192 | 142.4298 | 0.06105 | 116.6056 | 0.06105 | 1.4243 | 0.0006105 | 1.1661 | 0.0006105 | 1.4237 | 1.1654 | 5.2557 | 28.8565 | 2718.2189
38904.6587 | 1989 | 1 | 38904.6587 | 1978 | 1 | 3061.5 | 3208.5 | 121.4286 | 0.06105 | 120.757 | 0.06105 | 1.2143 | 0.0006105 | 1.2076 | 0.0006105 | 1.2137 | 1.207 | 23.5086 | 24.1988 | 9067.4146
38904.6589 | 2401 | 1 | 38904.6589 | 1924 | 1 | 3078.5 | 3225.5 | 146.5812 | 0.06105 | 117.4603 | 0.06105 | 1.4658 | 0.0006105 | 1.1746 | 0.0006105 | 1.4652 | 1.174 | 2.2692 | 28.281 | 1176.8217
38904.6591 | 1991 | 1 | 38904.6591 | 2335 | 1 | 3095.5 | 3242.5 | 121.5507 | 0.06105 | 142.5519 | 0.06105 | 1.2155 | 0.0006105 | 1.4255 | 0.0006105 | 1.2149 | 1.4249 | 23.5649 | 5.1671 | 2276.6767
38904.6592 | 2402 | 1 | 38904.6593 | 1909 | 1 | 3112 | 3259 | 146.6422 | 0.06105 | 116.5446 | 0.06105 | 1.4664 | 0.0006105 | 1.1654 | 0.0006105 | 1.4658 | 1.1648 | 2.2264 | 29.3266 | 1187.7903
38904.6594 | 1988 | 1 | 38904.6595 | 2038 | 1 | 3129 | 3276 | 121.3675 | 0.06105 | 124.42 | 0.06105 | 1.2137 | 0.0006105 | 1.2442 | 0.0006105 | 1.2131 | 1.2436 | 23.5797 | 20.5327 | 7944.7607
38904.6596 | 1948 | 1 | 38904.6597 | 1980 | 1 | 3145.5 | 3292.5 | 118.9255 | 0.06105 | 120.8791 | 0.06105 | 1.1893 | 0.0006105 | 1.2088 | 0.0006105 | 1.1886 | 1.2082 | 26.1153 | 24.0678 | 9823.217
38904.6598 | 6 | 1 | 38904.6598 | 2345 | 1 | 3162.5 | 3309.5 | 0.3663 | 0.06105 | 143.1624 | 0.06105 | 0.003663 | 0.0006105 | 1.4316 | 0.0006105 | 0.0030525 | 1.431 | 15086.299 | 8.9001 | 20009.9852
38904.66 | 5 | 1 | 38904.66 | 2040 | 1 | 3179.5 | 3326.5 | 0.30525 | 0.06105 | 124.5421 | 0.06105 | 0.0030525 | 0.0006105 | 1.2454 | 0.0006105 | 0.002442 | 1.2448 | 269640.2046 | 32.3495 | 59868.878
38904.6602 | 6 | 1 | 38904.6602 | 1960 | 1 | 3196 | 3343 | 0.3663 | 0.06105 | 119.6581 | 0.06105 | 0.003663 | 0.0006105 | 1.1966 | 0.0006105 | 0.0030525 | 1.196 | 234287.0949 | 25.2874 | 49416.9075
38904.6604 | 6 | 1 | 38904.6604 | 2214 | 1 | 3213 | 3360 | 0.3663 | 0.06105 | 135.1648 | 0.06105 | 0.003663 | 0.0006105 | 1.3516 | 0.0006105 | 0.0030525 | 1.351 | 58764.5706 | 120.2102 | 133654.222
38904.6606 | 5 | 1 | 38904.6606 | 1969 | 1 | 3230 | 3377 | 0.30525 | 0.06105 | 120.2076 | 0.06105 | 0.0030525 | 0.0006105 | 1.2021 | 0.0006105 | 0.002442 | 1.2015 | 5301667.3683 | 25.2922 | 49444.657
38904.6608 | 8 | 1 | 38904.6608 | 2323 | 1 | 3246.5 | 3393.5 | 0.4884 | 0.06105 | 141.8193 | 0.06105 | 0.004884 | 0.0006105 | 1.4182 | 0.0006105 | 0.0042735 | 1.4176 | 23218.9405 | 28.245 | 53879.7231
38904.661 | 294 | 1 | 38904.661 | 1978 | 0 | 3263.5 | 3410.5 | 17.9487 | 0.06105 | 120.757 | 0 | 0.17949 | 0.0006105 | 1.2076 | 0 | 0.17888 | 1.2076 | 748.2538 | 24.1345 | 42002.5497
38904.6612 | 6 | 0 | 38904.6612 | 2415 | 1 | 3280 | 3427 | 0.3663 | 0 | 147.4359 | 0.06105 | 0.003663 | 0 | 1.4744 | 0.0006105 | 0.003663 | 1.4737 | 40823 | 1.7142 | 40822.9963
38904.6614 | 5 | 0 | 38904.6614 | 2237 | 0 | 3297 | 3444 | 0.30525 | 0 | 136.569 | 0 | 0.0030525 | 0 | 1.3657 | 0 | 0.0030525 | 1.3657 | 49007.6 | 9.7622 | 49007.5969
38904.6616 | 5 | 1 | 38904.6616 | 2078 | 1 | 3313.5 | 3460.5 | 0.30525 | 0.06105 | 126.862 | 0.06105 | 0.0030525 | 0.0006105 | 1.2686 | 0.0006105 | 0.002442 | 1.268 | 162952.5982 | 40.0599 | 70057.105
38904.6618 | 5 | 1 | 38904.6618 | 2179 | 1 | 3330.5 | 3477.5 | 0.30525 | 0.06105 | 133.0281 | 0.06105 | 0.0030525 | 0.0006105 | 1.3303 | 0.0006105 | 0.002442 | 1.3297 | 63146.6344 | 836.5413 | 218784.5353
38904.662 | 5 | 1 | 38904.662 | 2302 | 1 | 3347.5 | 3494.5 | 0.30525 | 0.06105 | 140.5372 | 0.06105 | 0.0030525 | 0.0006105 | 1.4054 | 0.0006105 | 0.002442 | 1.4048 | 22272.1623 | 14.2817 | 30609.6542

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 7 |  |  | 2006-07-06 | 14:56
XLPE | 3-C | Conduit
470 C | 17.3 kW/m2 | [5 empty] | 4 is Drain Wire |  |  |  | Excluding Drain Wire
Penlight Time | Average C1-G |  | Penlight Time | Average C2-G | Penlight Time | Average C3-G | Penlight Time | Average C4-G | Penlight Time | Minimums on Average | Penlight Time | Minimums
-143.6667 | 244604.6667 |  | -140 | 245471.3333 | -138 | 243971.3333 | -136.3333 | 245171.3333 | -143.6667 | 243971.3333 | -143.6667 | 243971.3333
-126.8333 | 203681.6667 |  | -123.1667 | 245471.3333 | -121.3333 | 243971.3333 | -119.3333 | 245171.3333 | -126.8333 | 203681.6667 | -126.8333 | 203681.6667
-110.3333 | 244604.6667 |  | -106.3333 | 245471.3333 | -104.6667 | 243971.3333 | -102.6667 | 204231.6667 | -110.3333 | 204231.6667 | -110.3333 | 243971.3333
-93.3333 | 244604.6667 |  | -89.6667 | 245471.3333 | -87.8333 | 203481.6667 | -85.8333 | 245171.3333 | -93.3333 | 203481.6667 | -93.3333 | 203481.6667
-76.5 | 244604.6667 |  | -72.8333 | 204465 | -71 | 243971.3333 | -69 | 245171.3333 | -76.5 | 204465 | -76.5 | 204465
-59.6667 | 244604.6667 |  | -56.1667 | 245471.3333 | -54.1667 | 243971.3333 | -52.3333 | 245171.3333 | -59.6667 | 243971.3333 | -59.6667 | 243971.3333
-42.8333 | 244604.6667 |  | -39.1667 | 245471.3333 | -37.3333 | 243971.3333 | -35.3333 | 204481.6667 | -42.8333 | 204481.6667 | -42.8333 | 243971.3333
-26.1667 | 244604.6667 |  | -22.5 | 245471.3333 | -20.5 | 203115 | -18.8333 | 245171.3333 | -26.1667 | 203115 | -26.1667 | 203115
-9.3333 | 204115 |  | -5.6667 | 245471.3333 | -3.8333 | 243971.3333 | -1.8333 | 245171.3333 | -9.3333 | 204115 | -9.3333 | 204115
7.3333 | 244604.6667 |  | 11.1667 | 245471.3333 | 13 | 243971.3333 | 14.8333 | 245171.3333 | 7.3333 | 243971.3333 | 7.3333 | 243971.3333
24.1667 | 244604.6667 |  | 27.8333 | 245471.3333 | 29.6667 | 243971.3333 | 31.6667 | 204165 | 24.1667 | 204165 | 24.1667 | 243971.3333
41.1667 | 244604.6667 |  | 44.8333 | 245471.3333 | 46.5 | 243971.3333 | 48.5 | 204481.6667 | 41.1667 | 204481.6667 | 41.1667 | 243971.3333
57.8333 | 244604.6667 |  | 61.6667 | 245471.3333 | 63.5 | 243971.3333 | 65.3333 | 245171.3333 | 57.8333 | 243971.3333 | 57.8333 | 243971.3333
74.6667 | 244604.6667 |  | 78.3333 | 245471.3333 | 80.1667 | 243971.3333 | 82.1667 | 245171.3333 | 74.6667 | 243971.3333 | 74.6667 | 243971.3333
91.5 | 203665 |  | 95 | 245471.3333 | 97 | 243971.3333 | 98.8333 | 245171.3333 | 91.5 | 203665 | 91.5 | 203665
108.1667 | 244604.6667 |  | 112 | 204465 | 113.8333 | 243971.3333 | 115.6667 | 245171.3333 | 108.1667 | 204465 | 108.1667 | 204465
125.1667 | 244604.6667 |  | 128.8333 | 204465 | 130.5 | 243971.3333 | 132.5 | 245171.3333 | 125.1667 | 204465 | 125.1667 | 204465
141.8333 | 244604.6667 |  | 145.6667 | 245471.3333 | 147.5 | 243971.3333 | 149.3333 | 245171.3333 | 141.8333 | 243971.3333 | 141.8333 | 243971.3333
158.5 | 244604.6667 |  | 162.3333 | 245471.3333 | 164.1667 | 243971.3333 | 166 | 245171.3333 | 158.5 | 243971.3333 | 158.5 | 243971.3333
175.5 | 244604.6667 |  | 179.1667 | 245471.3333 | 181 | 243971.3333 | 183 | 245171.3333 | 175.5 | 243971.3333 | 175.5 | 243971.3333
192.1667 | 244604.6667 |  | 196 | 245471.3333 | 197.8333 | 243971.3333 | 199.6667 | 204481.6667 | 192.1667 | 204481.6667 | 192.1667 | 243971.3333
209 | 244604.6667 |  | 212.8333 | 245471.3333 | 214.6667 | 243971.3333 | 216.5 | 245171.3333 | 209 | 243971.3333 | 209 | 243971.3333
225.8333 | 244604.6667 |  | 229.5 | 245471.3333 | 231.5 | 243971.3333 | 233.1667 | 245171.3333 | 225.8333 | 243971.3333 | 225.8333 | 243971.3333
242.6667 | 244604.6667 |  | 246.5 | 245471.3333 | 248.3333 | 243971.3333 | 250.1667 | 245171.3333 | 242.6667 | 243971.3333 | 242.6667 | 243971.3333
259.3333 | 244604.6667 |  | 263.1667 | 245471.3333 | 265 | 243971.3333 | 266.8333 | 245171.3333 | 259.3333 | 243971.3333 | 259.3333 | 243971.3333
276.1667 | 244604.6667 |  | 279.8333 | 245471.3333 | 281.6667 | 243971.3333 | 283.6667 | 245171.3333 | 276.1667 | 243971.3333 | 276.1667 | 243971.3333
293 | 244604.6667 |  | 296.8333 | 245471.3333 | 298.5 | 203115 | 300.3333 | 245171.3333 | 293 | 203115 | 293 | 203115
309.8333 | 244604.6667 |  | 313.6667 | 245471.3333 | 315.5 | 243971.3333 | 317.3333 | 245171.3333 | 309.8333 | 243971.3333 | 309.8333 | 243971.3333
326.5 | 244604.6667 |  | 330.3333 | 245471.3333 | 332.1667 | 243971.3333 | 334 | 245171.3333 | 326.5 | 243971.3333 | 326.5 | 243971.3333
343.5 | 203681.6667 |  | 347 | 245471.3333 | 349 | 243971.3333 | 350.8333 | 245171.3333 | 343.5 | 203681.6667 | 343.5 | 203681.6667
360.1667 | 244604.6667 |  | 363.8333 | 245471.3333 | 365.6667 | 243971.3333 | 367.6667 | 245171.3333 | 360.1667 | 243971.3333 | 360.1667 | 243971.3333
377 | 244604.6667 |  | 380.8333 | 245471.3333 | 382.6667 | 243971.3333 | 384.5 | 245171.3333 | 377 | 243971.3333 | 377 | 243971.3333
393.6667 | 244604.6667 |  | 397.5 | 245471.3333 | 399.3333 | 243971.3333 | 401.1667 | 245171.3333 | 393.6667 | 243971.3333 | 393.6667 | 243971.3333
410.6667 | 244604.6667 |  | 414.3333 | 245471.3333 | 416 | 243971.3333 | 418 | 245171.3333 | 410.6667 | 243971.3333 | 410.6667 | 243971.3333
427.5 | 244604.6667 |  | 431 | 204465 | 433 | 243971.3333 | 434.8333 | 245171.3333 | 427.5 | 204465 | 427.5 | 204465
444.1667 | 244604.6667 |  | 448 | 245471.3333 | 449.8333 | 243971.3333 | 451.6667 | 245171.3333 | 444.1667 | 243971.3333 | 444.1667 | 243971.3333
461 | 244604.6667 |  | 464.6667 | 245471.3333 | 466.5 | 243971.3333 | 468.5 | 245171.3333 | 461 | 243971.3333 | 461 | 243971.3333
477.6667 | 244604.6667 |  | 481.5 | 245471.3333 | 483.3333 | 243971.3333 | 485.1667 | 245171.3333 | 477.6667 | 243971.3333 | 477.6667 | 243971.3333
494.6667 | 244604.6667 |  | 498.3333 | 245471.3333 | 500 | 243971.3333 | 502 | 245171.3333 | 494.6667 | 243971.3333 | 494.6667 | 243971.3333
511.3333 | 203681.6667 |  | 515 | 204465 | 517 | 203281.6667 | 518.6667 | 245171.3333 | 511.3333 | 203281.6667 | 511.3333 | 203281.6667
528.3333 | 244604.6667 |  | 531.8333 | 245471.3333 | 533.8333 | 243971.3333 | 535.6667 | 245171.3333 | 528.3333 | 243971.3333 | 528.3333 | 243971.3333
545 | 244604.6667 |  | 548.8333 | 204548.3333 | 550.6667 | 243971.3333 | 552.5 | 245171.3333 | 545 | 204548.3333 | 545 | 204548.3333
561.6667 | 244604.6667 |  | 565.5 | 245471.3333 | 567.3333 | 243971.3333 | 569.1667 | 245171.3333 | 561.6667 | 243971.3333 | 561.6667 | 243971.3333
578.5 | 244604.6667 |  | 582.1667 | 245471.3333 | 584 | 243971.3333 | 586 | 245171.3333 | 578.5 | 243971.3333 | 578.5 | 243971.3333
595.3333 | 244604.6667 |  | 599 | 245471.3333 | 601 | 243971.3333 | 602.6667 | 245171.3333 | 595.3333 | 243971.3333 | 595.3333 | 243971.3333
612.1667 | 244604.6667 |  | 616 | 245471.3333 | 617.8333 | 243971.3333 | 619.6667 | 245171.3333 | 612.1667 | 243971.3333 | 612.1667 | 243971.3333
628.8333 | 244604.6667 |  | 632.6667 | 204548.3333 | 634.5 | 243971.3333 | 636.3333 | 245171.3333 | 628.8333 | 204548.3333 | 628.8333 | 204548.3333
645.6667 | 244604.6667 |  | 649.5 | 245471.3333 | 651.3333 | 203481.6667 | 653.1667 | 204165 | 645.6667 | 203481.6667 | 645.6667 | 203481.6667
662.5 | 244604.6667 |  | 666.1667 | 245471.3333 | 668 | 243971.3333 | 670 | 245171.3333 | 662.5 | 243971.3333 | 662.5 | 243971.3333
679.3333 | 244604.6667 |  | 683 | 245471.3333 | 685 | 243971.3333 | 686.6667 | 245171.3333 | 679.3333 | 243971.3333 | 679.3333 | 243971.3333
696.1667 | 244604.6667 |  | 699.8333 | 245471.3333 | 701.6667 | 243971.3333 | 703.6667 | 245171.3333 | 696.1667 | 243971.3333 | 696.1667 | 243971.3333
712.8333 | 244604.6667 |  | 716.6667 | 245471.3333 | 718.5 | 243971.3333 | 720.3333 | 245171.3333 | 712.8333 | 243971.3333 | 712.8333 | 243971.3333
729.6667 | 244604.6667 |  | 733.5 | 245471.3333 | 735.3333 | 243971.3333 | 737.1667 | 245171.3333 | 729.6667 | 243971.3333 | 729.6667 | 243971.3333
746.5 | 244604.6667 |  | 750.1667 | 245471.3333 | 752 | 243971.3333 | 754 | 245171.3333 | 746.5 | 243971.3333 | 746.5 | 243971.3333
763.3333 | 244604.6667 |  | 767 | 245471.3333 | 769 | 243971.3333 | 770.6667 | 245171.3333 | 763.3333 | 243971.3333 | 763.3333 | 243971.3333
780.1667 | 244604.6667 |  | 783.8333 | 245471.3333 | 785.6667 | 243971.3333 | 787.6667 | 204165 | 780.1667 | 204165 | 780.1667 | 243971.3333
796.8333 | 244604.6667 |  | 800.6667 | 245471.3333 | 802.5 | 243971.3333 | 804.3333 | 204231.6667 | 796.8333 | 204231.6667 | 796.8333 | 243971.3333
813.6667 | 244604.6667 |  | 817.5 | 245471.3333 | 819.3333 | 243971.3333 | 821.1667 | 245171.3333 | 813.6667 | 243971.3333 | 813.6667 | 243971.3333
830.5 | 244604.6667 |  | 834.1667 | 245471.3333 | 836 | 243971.3333 | 838 | 245171.3333 | 830.5 | 243971.3333 | 830.5 | 243971.3333
847.3333 | 244604.6667 |  | 851 | 245471.3333 | 853 | 243971.3333 | 854.6667 | 245171.3333 | 847.3333 | 243971.3333 | 847.3333 | 243971.3333
864.1667 | 244604.6667 |  | 867.8333 | 245471.3333 | 869.6667 | 243971.3333 | 871.6667 | 245171.3333 | 864.1667 | 243971.3333 | 864.1667 | 243971.3333
880.8333 | 244604.6667 |  | 884.6667 | 245471.3333 | 886.5 | 243971.3333 | 888.3333 | 245171.3333 | 880.8333 | 243971.3333 | 880.8333 | 243971.3333
897.6667 | 244604.6667 |  | 901.5 | 245471.3333 | 903.3333 | 243971.3333 | 905.1667 | 245171.3333 | 897.6667 | 243971.3333 | 897.6667 | 243971.3333
914.5 | 204115 |  | 918.1667 | 245471.3333 | 920 | 243971.3333 | 922 | 245171.3333 | 914.5 | 204115 | 914.5 | 204115
931.3333 | 244604.6667 |  | 935 | 245471.3333 | 937 | 243971.3333 | 938.6667 | 245171.3333 | 931.3333 | 243971.3333 | 931.3333 | 243971.3333
948.1667 | 244604.6667 |  | 951.8333 | 245471.3333 | 953.6667 | 243971.3333 | 955.6667 | 245171.3333 | 948.1667 | 243971.3333 | 948.1667 | 243971.3333
965 | 244604.6667 |  | 968.8333 | 245471.3333 | 970.5 | 243971.3333 | 972.3333 | 245171.3333 | 965 | 243971.3333 | 965 | 243971.3333
981.6667 | 244604.6667 |  | 985.5 | 245471.3333 | 987.3333 | 243971.3333 | 989.1667 | 245171.3333 | 981.6667 | 243971.3333 | 981.6667 | 243971.3333
998.5 | 244604.6667 |  | 1002.1667 | 245471.3333 | 1004 | 243971.3333 | 1006 | 245171.3333 | 998.5 | 243971.3333 | 998.5 | 243971.3333
1015.3333 | 244604.6667 |  | 1019 | 245471.3333 | 1021 | 243971.3333 | 1022.6667 | 245171.3333 | 1015.3333 | 243971.3333 | 1015.3333 | 243971.3333
1032.1667 | 244604.6667 |  | 1035.8333 | 245471.3333 | 1037.6667 | 243971.3333 | 1039.6667 | 245171.3333 | 1032.1667 | 243971.3333 | 1032.1667 | 243971.3333
1048.8333 | 244604.6667 |  | 1052.6667 | 245471.3333 | 1054.5 | 243971.3333 | 1056.3333 | 245171.3333 | 1048.8333 | 243971.3333 | 1048.8333 | 243971.3333
1065.6667 | 244604.6667 |  | 1069.5 | 245471.3333 | 1071.3333 | 243971.3333 | 1073.1667 | 245171.3333 | 1065.6667 | 243971.3333 | 1065.6667 | 243971.3333
1082.5 | 244604.6667 |  | 1086.1667 | 245471.3333 | 1088 | 243971.3333 | 1090 | 245171.3333 | 1082.5 | 243971.3333 | 1082.5 | 243971.3333
1099.3333 | 244604.6667 |  | 1103 | 245471.3333 | 1105 | 243971.3333 | 1106.6667 | 204165 | 1099.3333 | 204165 | 1099.3333 | 243971.3333
1116.1667 | 244604.6667 |  | 1119.8333 | 200309196.8133 | 1121.6667 | 243971.3333 | 1123.6667 | 245171.3333 | 1116.1667 | 243971.3333 | 1116.1667 | 243971.3333
1132.8333 | 244604.6667 |  | 1136.6667 | 245471.3333 | 1138.5 | 243971.3333 | 1140.3333 | 245171.3333 | 1132.8333 | 243971.3333 | 1132.8333 | 243971.3333
1149.6667 | 244604.6667 |  | 1153.5 | 245471.3333 | 1155.3333 | 243971.3333 | 1157.1667 | 204231.6667 | 1149.6667 | 204231.6667 | 1149.6667 | 243971.3333
1166.5 | 244604.6667 |  | 1170.1667 | 245471.3333 | 1172 | 243971.3333 | 1174 | 245171.3333 | 1166.5 | 243971.3333 | 1166.5 | 243971.3333
1183.3333 | 244604.6667 |  | 1187 | 245471.3333 | 1189 | 243971.3333 | 1190.6667 | 245171.3333 | 1183.3333 | 243971.3333 | 1183.3333 | 243971.3333
1200.1667 | 244604.6667 |  | 1203.8333 | 245471.3333 | 1205.6667 | 243971.3333 | 1207.6667 | 245171.3333 | 1200.1667 | 243971.3333 | 1200.1667 | 243971.3333
1216.8333 | 244604.6667 |  | 1220.6667 | 245471.3333 | 1222.5 | 203115 | 1224.3333 | 245171.3333 | 1216.8333 | 203115 | 1216.8333 | 203115
1233.6667 | 244604.6667 |  | 1237.5 | 245471.3333 | 1239.3333 | 243971.3333 | 1241.1667 | 245171.3333 | 1233.6667 | 243971.3333 | 1233.6667 | 243971.3333
1250.5 | 244604.6667 |  | 1254.1667 | 245471.3333 | 1256 | 243971.3333 | 1258 | 245171.3333 | 1250.5 | 243971.3333 | 1250.5 | 243971.3333
1267.1667 | 244604.6667 |  | 1271 | 245471.3333 | 1272.8333 | 243971.3333 | 1274.6667 | 245171.3333 | 1267.1667 | 243971.3333 | 1267.1667 | 243971.3333
1284.1667 | 244604.6667 |  | 1287.8333 | 245471.3333 | 1289.6667 | 243971.3333 | 1291.6667 | 245171.3333 | 1284.1667 | 243971.3333 | 1284.1667 | 243971.3333
1300.6667 | 244604.6667 |  | 1304.6667 | 204615 | 1306.3333 | 243971.3333 | 1308.3333 | 204165 | 1300.6667 | 204165 | 1300.6667 | 204615
1317.5 | 244604.6667 |  | 1321.3333 | 245471.3333 | 1323.1667 | 203115 | 1325 | 245171.3333 | 1317.5 | 203115 | 1317.5 | 203115
1334.5 | 244604.6667 |  | 1338 | 245471.3333 | 1340 | 243971.3333 | 1341.8333 | 245171.3333 | 1334.5 | 243971.3333 | 1334.5 | 243971.3333
1351.3333 | 244604.6667 |  | 1355 | 245471.3333 | 1357 | 243971.3333 | 1358.6667 | 245171.3333 | 1351.3333 | 243971.3333 | 1351.3333 | 243971.3333
1368.1667 | 244604.6667 |  | 1371.8333 | 245471.3333 | 1373.5 | 243971.3333 | 1375.5 | 245171.3333 | 1368.1667 | 243971.3333 | 1368.1667 | 243971.3333
1385 | 244604.6667 |  | 1389 | 245471.3333 | 1390.3333 | 243971.3333 | 1392.3333 | 204165 | 1385 | 204165 | 1385 | 243971.3333
1401.5 | 244604.6667 |  | 1405.3333 | 245471.3333 | 1407.3333 | 243971.3333 | 1409.1667 | 245171.3333 | 1401.5 | 243971.3333 | 1401.5 | 243971.3333
1418.5 | 244604.6667 |  | 1422.1667 | 245471.3333 | 1424 | 243971.3333 | 1426 | 245171.3333 | 1418.5 | 243971.3333 | 1418.5 | 243971.3333
1435.1667 | 244604.6667 |  | 1439 | 245471.3333 | 1440.8333 | 243971.3333 | 1442.6667 | 245171.3333 | 1435.1667 | 243971.3333 | 1435.1667 | 243971.3333
1452 | 244604.6667 |  | 1455.6667 | 245471.3333 | 1457.5 | 243971.3333 | 1459.5 | 245171.3333 | 1452 | 243971.3333 | 1452 | 243971.3333
1468.8333 | 244604.6667 |  | 1472.5 | 245471.3333 | 1474.5 | 243971.3333 | 1476.1667 | 245171.3333 | 1468.8333 | 243971.3333 | 1468.8333 | 243971.3333
1485.6667 | 244604.6667 |  | 1489.5 | 201781824.8133 | 1491.1667 | 243971.3333 | 1493 | 245171.3333 | 1485.6667 | 243971.3333 | 1485.6667 | 243971.3333
1502.3333 | 244604.6667 |  | 1506.1667 | 245471.3333 | 1508 | 243971.3333 | 1509.8333 | 245171.3333 | 1502.3333 | 243971.3333 | 1502.3333 | 243971.3333
1519.3333 | 244604.6667 |  | 1522.8333 | 245471.3333 | 1524.8333 | 243971.3333 | 1526.6667 | 245171.3333 | 1519.3333 | 243971.3333 | 1519.3333 | 243971.3333
1536 | 244604.6667 |  | 1539.8333 | 245471.3333 | 1541.6667 | 243971.3333 | 1543.5 | 245171.3333 | 1536 | 243971.3333 | 1536 | 243971.3333
1552.6667 | 244604.6667 |  | 1556.5 | 245471.3333 | 1558.3333 | 243971.3333 | 1560.1667 | 245171.3333 | 1552.6667 | 243971.3333 | 1552.6667 | 243971.3333
1569.5 | 244604.6667 |  | 1573.3333 | 245471.3333 | 1575.1667 | 243971.3333 | 1577 | 245171.3333 | 1569.5 | 243971.3333 | 1569.5 | 243971.3333
1586.3333 | 244604.6667 |  | 1590.1667 | 245471.3333 | 1592 | 243971.3333 | 1593.8333 | 245171.3333 | 1586.3333 | 243971.3333 | 1586.3333 | 243971.3333
1603.1667 | 244604.6667 |  | 1607 | 200309196.8133 | 1608.8333 | 243971.3333 | 1610.6667 | 245171.3333 | 1603.1667 | 243971.3333 | 1603.1667 | 243971.3333
1619.8333 | 244604.6667 |  | 1623.6667 | 245471.3333 | 1625.5 | 243971.3333 | 1627.3333 | 245171.3333 | 1619.8333 | 243971.3333 | 1619.8333 | 243971.3333
1636.8333 | 244604.6667 |  | 1640.5 | 245471.3333 | 1642.5 | 243971.3333 | 1644.1667 | 245171.3333 | 1636.8333 | 243971.3333 | 1636.8333 | 243971.3333
1653.3333 | 244604.6667 |  | 1657.1667 | 245471.3333 | 1659 | 243971.3333 | 1660.8333 | 245171.3333 | 1653.3333 | 243971.3333 | 1653.3333 | 243971.3333
1670.3333 | 244604.6667 |  | 1674 | 204548.3333 | 1676 | 243971.3333 | 1677.6667 | 245171.3333 | 1670.3333 | 204548.3333 | 1670.3333 | 204548.3333
1687.1667 | 244604.6667 |  | 1690.8333 | 245471.3333 | 1692.6667 | 243971.3333 | 1694.6667 | 245171.3333 | 1687.1667 | 243971.3333 | 1687.1667 | 243971.3333
1703.8333 | 244604.6667 |  | 1707.6667 | 245471.3333 | 1709.5 | 243971.3333 | 1711.3333 | 245171.3333 | 1703.8333 | 243971.3333 | 1703.8333 | 243971.3333
1720.8333 | 244604.6667 |  | 1724.5 | 245471.3333 | 1726.5 | 243971.3333 | 1728.1667 | 245171.3333 | 1720.8333 | 243971.3333 | 1720.8333 | 243971.3333
1737.6667 | 244604.6667 |  | 1741.5 | 200309196.8133 | 1743.1667 | 243971.3333 | 1745 | 245171.3333 | 1737.6667 | 243971.3333 | 1737.6667 | 243971.3333
1754.5 | 244604.6667 |  | 1758 | 245471.3333 | 1760 | 243971.3333 | 1761.8333 | 245171.3333 | 1754.5 | 243971.3333 | 1754.5 | 243971.3333
1771.1667 | 201125790.1467 |  | 1774.8333 | 245471.3333 | 1776.6667 | 243971.3333 | 1778.6667 | 245171.3333 | 1771.1667 | 243971.3333 | 1771.1667 | 243971.3333
1788 | 244604.6667 |  | 1791.6667 | 245471.3333 | 1793.5 | 243971.3333 | 1795.5 | 245171.3333 | 1788 | 243971.3333 | 1788 | 243971.3333
1804.6667 | 244604.6667 |  | 1808.5 | 204465 | 1810.3333 | 243971.3333 | 1812.1667 | 245171.3333 | 1804.6667 | 204465 | 1804.6667 | 204465
1821.6667 | 244604.6667 |  | 1825.3333 | 245471.3333 | 1827 | 243971.3333 | 1829 | 245171.3333 | 1821.6667 | 243971.3333 | 1821.6667 | 243971.3333
1838.5 | 244604.6667 |  | 1842 | 245471.3333 | 1844 | 243971.3333 | 1845.8333 | 245171.3333 | 1838.5 | 243971.3333 | 1838.5 | 243971.3333
1855.1667 | 244604.6667 |  | 1858.6667 | 245471.3333 | 1860.5 | 243971.3333 | 1862.6667 | 245171.3333 | 1855.1667 | 243971.3333 | 1855.1667 | 243971.3333
1871.8333 | 244604.6667 |  | 1875.6667 | 245471.3333 | 1877.5 | 243971.3333 | 1879.3333 | 245171.3333 | 1871.8333 | 243971.3333 | 1871.8333 | 243971.3333
1888.6667 | 244604.6667 |  | 1892.5 | 245471.3333 | 1894.3333 | 243971.3333 | 1896.1667 | 245171.3333 | 1888.6667 | 243971.3333 | 1888.6667 | 243971.3333
1905.5 | 244604.6667 |  | 1909.1667 | 245471.3333 | 1911 | 243971.3333 | 1913 | 245171.3333 | 1905.5 | 243971.3333 | 1905.5 | 243971.3333
1922.3333 | 244604.6667 |  | 1926 | 245471.3333 | 1928 | 243971.3333 | 1929.6667 | 245171.3333 | 1922.3333 | 243971.3333 | 1922.3333 | 243971.3333
1939.1667 | 244604.6667 |  | 1942.8333 | 245471.3333 | 1944.6667 | 243971.3333 | 1946.6667 | 245171.3333 | 1939.1667 | 243971.3333 | 1939.1667 | 243971.3333
1955.8333 | 244604.6667 |  | 1959.6667 | 245471.3333 | 1961.5 | 243971.3333 | 1963.3333 | 245171.3333 | 1955.8333 | 243971.3333 | 1955.8333 | 243971.3333
1972.6667 | 244604.6667 |  | 1976.5 | 245471.3333 | 1978.3333 | 243971.3333 | 1980.1667 | 245171.3333 | 1972.6667 | 243971.3333 | 1972.6667 | 243971.3333
1989.5 | 244604.6667 |  | 1993.1667 | 245471.3333 | 1995 | 243971.3333 | 1997 | 245171.3333 | 1989.5 | 243971.3333 | 1989.5 | 243971.3333
2006.3333 | 244604.6667 |  | 2010 | 245471.3333 | 2012 | 243971.3333 | 2013.6667 | 245171.3333 | 2006.3333 | 243971.3333 | 2006.3333 | 243971.3333
2023.1667 | 244604.6667 |  | 2026.8333 | 245471.3333 | 2028.6667 | 243971.3333 | 2030.6667 | 245171.3333 | 2023.1667 | 243971.3333 | 2023.1667 | 243971.3333
2039.8333 | 244604.6667 |  | 2043.6667 | 245471.3333 | 2045.5 | 243971.3333 | 2047.3333 | 245171.3333 | 2039.8333 | 243971.3333 | 2039.8333 | 243971.3333
2056.6667 | 244604.6667 |  | 2060.5 | 245471.3333 | 2062.3333 | 243971.3333 | 2064.1667 | 245171.3333 | 2056.6667 | 243971.3333 | 2056.6667 | 243971.3333
2073.5 | 244604.6667 |  | 2077.1667 | 245471.3333 | 2079 | 243971.3333 | 2081 | 245171.3333 | 2073.5 | 243971.3333 | 2073.5 | 243971.3333
2090.3333 | 244604.6667 |  | 2094 | 245471.3333 | 2096 | 243971.3333 | 2097.6667 | 245171.3333 | 2090.3333 | 243971.3333 | 2090.3333 | 243971.3333
2107.1667 | 244604.6667 |  | 2110.8333 | 245471.3333 | 2112.6667 | 203115 | 2114.6667 | 245171.3333 | 2107.1667 | 203115 | 2107.1667 | 203115
2123.8333 | 244604.6667 |  | 2127.6667 | 245471.3333 | 2129.5 | 243971.3333 | 2131.3333 | 245171.3333 | 2123.8333 | 243971.3333 | 2123.8333 | 243971.3333
2140.6667 | 244604.6667 |  | 2144.5 | 245471.3333 | 2146.3333 | 243971.3333 | 2148.1667 | 245171.3333 | 2140.6667 | 243971.3333 | 2140.6667 | 243971.3333
2157.5 | 244604.6667 |  | 2161.1667 | 245471.3333 | 2163 | 203281.6667 | 2165 | 245171.3333 | 2157.5 | 203281.6667 | 2157.5 | 203281.6667
2174.3333 | 244604.6667 |  | 2178 | 245471.3333 | 2180 | 203281.6667 | 2181.6667 | 245171.3333 | 2174.3333 | 203281.6667 | 2174.3333 | 203281.6667
2191.1667 | 244604.6667 |  | 2194.8333 | 245471.3333 | 2196.6667 | 243971.3333 | 2198.6667 | 245171.3333 | 2191.1667 | 243971.3333 | 2191.1667 | 243971.3333
2207.8333 | 244604.6667 |  | 2211.6667 | 245471.3333 | 2213.5 | 243971.3333 | 2215.3333 | 245171.3333 | 2207.8333 | 243971.3333 | 2207.8333 | 243971.3333
2224.6667 | 244604.6667 |  | 2228.5 | 245471.3333 | 2230.3333 | 243971.3333 | 2232.1667 | 245171.3333 | 2224.6667 | 243971.3333 | 2224.6667 | 243971.3333
2241.5 | 244604.6667 |  | 2245.1667 | 245471.3333 | 2247 | 243971.3333 | 2249 | 245171.3333 | 2241.5 | 243971.3333 | 2241.5 | 243971.3333
2258.3333 | 244604.6667 |  | 2262 | 245471.3333 | 2264 | 243971.3333 | 2265.6667 | 163225.3333 | 2258.3333 | 163225.3333 | 2258.3333 | 243971.3333
2275.1667 | 244604.6667 |  | 2278.6667 | 245471.3333 | 2280.5 | 243971.3333 | 2282.6667 | 245171.3333 | 2275.1667 | 243971.3333 | 2275.1667 | 243971.3333
2291.8333 | 244604.6667 |  | 2295.6667 | 245471.3333 | 2297.5 | 243971.3333 | 2299.3333 | 204231.6667 | 2291.8333 | 204231.6667 | 2291.8333 | 243971.3333
2308.6667 | 203681.6667 |  | 2312.5 | 245471.3333 | 2314.3333 | 243971.3333 | 2316.1667 | 166196.1728 | 2308.6667 | 166196.1728 | 2308.6667 | 203681.6667
2325.5 | 244604.6667 |  | 2329.1667 | 124350.7366 | 2331 | 171669.0698 | 2333 | 86950.1565 | 2325.5 | 86950.1565 | 2325.5 | 124350.7366
2342.3333 | 50301578.2902 |  | 2346 | 79315.8146 | 2348 | 168905.1215 | 2349.6667 | 20286.1042 | 2342.3333 | 20286.1042 | 2342.3333 | 79315.8146
2359.1667 | 65506820.5418 |  | 2362.8333 | 10771.9912 | 2364.6667 | 99444.6317 | 2366.6667 | 10556.747 | 2359.1667 | 10556.747 | 2359.1667 | 10771.9912
2375.8333 | 12984.9416 |  | 2379.6667 | 25234.6426 | 2381.5 | 22378.7041 | 2383.3333 | 11830.1465 | 2375.8333 | 11830.1465 | 2375.8333 | 12984.9416
2392.6667 | 4880.6517 |  | 2396.5 | 293211.0823 | 2398.3333 | 227761.2414 | 2400.1667 | 6326.9675 | 2392.6667 | 4880.6517 | 2392.6667 | 4880.6517
2409.5 | 3352.7187 |  | 2413.1667 | 3141.7431 | 2415 | 3474.3199 | 2417 | 4059.0399 | 2409.5 | 3141.7431 | 2409.5 | 3141.7431
2426.3333 | 5039.6119 |  | 2430 | 15740.4701 | 2432 | 1777.5693 | 2433.6667 | 3839.8443 | 2426.3333 | 1777.5693 | 2426.3333 | 1777.5693
2443.1667 | 2483.6002 |  | 2446.8333 | 3831.0414 | 2448.6667 | 6246.3043 | 2450.6667 | 3989.6233 | 2443.1667 | 2483.6002 | 2443.1667 | 2483.6002
2459.8333 | 1794.6382 |  | 2463.6667 | 7046.9274 | 2465.5 | 1638.9642 | 2467.3333 | 1938.4912 | 2459.8333 | 1638.9642 | 2459.8333 | 1638.9642
2476.6667 | 21591.9442 |  | 2480.5 | 17664.694 | 2482.3333 | 4903.5093 | 2484.1667 | 1141.2124 | 2476.6667 | 1141.2124 | 2476.6667 | 4903.5093
2493.5 | 1132.8119 |  | 2497.1667 | 2586.157 | 2499 | 1978.4311 | 2501 | 1274.1833 | 2493.5 | 1132.8119 | 2493.5 | 1132.8119
2510.3333 | 2163.7271 |  | 2514 | 13868.7437 | 2516 | 3329.7083 | 2517.6667 | 2546.1839 | 2510.3333 | 2163.7271 | 2510.3333 | 2163.7271
2527.1667 | 10438.476 |  | 2530.8333 | 6649.5915 | 2532.6667 | 9512.768 | 2534.6667 | 1804.028 | 2527.1667 | 1804.028 | 2527.1667 | 6649.5915
2543.8333 | 38349.1106 |  | 2547.6667 | 1869.4897 | 2549.5 | 3787.078 | 2551.3333 | 1518.7618 | 2543.8333 | 1518.7618 | 2543.8333 | 1869.4897
2560.6667 | 2559.7255 |  | 2564.5 | 2510.4987 | 2566.3333 | 1957.3964 | 2568.1667 | 1187.2273 | 2560.6667 | 1187.2273 | 2560.6667 | 1957.3964
2577.5 | 1705.1401 |  | 2581.1667 | 4059.3474 | 2583 | 1036.3795 | 2585 | 1271.4738 | 2577.5 | 1036.3795 | 2577.5 | 1036.3795
2594.3333 | 3235.3894 |  | 2598 | 1547.0375 | 2600 | 1482.7786 | 2601.6667 | 1753.8916 | 2594.3333 | 1482.7786 | 2594.3333 | 1482.7786
2611.1667 | 5404.9375 |  | 2614.6667 | 1450.7545 | 2616.6667 | 2411.5497 | 2618.5 | 1940.5271 | 2611.1667 | 1450.7545 | 2611.1667 | 1450.7545
2627.8333 | 3633.4559 |  | 2631.6667 | 2331.9827 | 2633.5 | 11013.5086 | 2635.3333 | 1655.4007 | 2627.8333 | 1655.4007 | 2627.8333 | 2331.9827
2644.6667 | 2785.3756 |  | 2648.5 | 1027.3599 | 2650.3333 | 1437.6701 | 2652.1667 | 1040.3397 | 2644.6667 | 1027.3599 | 2644.6667 | 1027.3599
2661.5 | 3839.2166 |  | 2665 | 25390.0758 | 2667 | 17250.6312 | 2668.8333 | 1176.4163 | 2661.5 | 1176.4163 | 2661.5 | 3839.2166
2678.3333 | 369.5246 |  | 2682 | 63.3838 | 2684 | 2334.7669 | 2685.6667 | 12.2764 | 2678.3333 | 12.2764 | 2678.3333 | 63.3838
2695.1667 | 22.9125 |  | 2698.8333 | 14.7251 | 2700.6667 | 2287.5397 | 2702.6667 | 18.1103 | 2695.1667 | 14.7251 | 2695.1667 | 14.7251
2711.8333 | 22.2713 |  | 2715.6667 | 14.4299 | 2717.5 | 1851.2465 | 2719.3333 | 21.7292 | 2711.8333 | 14.4299 | 2711.8333 | 14.4299
2728.6667 | 7.5279 |  | 2732.3333 | 16.3218 | 2734.1667 | 3457.6075 | 2736.1667 | 19.627 | 2728.6667 | 7.5279 | 2728.6667 | 7.5279
2745.3333 | 18.5411 |  | 2749.1667 | 6.6628 | 2751 | 3362.9345 | 2752.8333 | 26.0392 | 2745.3333 | 6.6628 | 2745.3333 | 6.6628
2762.3333 | 16.1309 |  | 2766 | 5.8257 | 2768 | 2054.1448 | 2769.6667 | 14.1271 | 2762.3333 | 5.8257 | 2762.3333 | 5.8257
2779 | 3.1309 |  | 2782.8333 | 9.8492 | 2784.6667 | 1044.7578 | 2786.5 | 7.8633 | 2779 | 3.1309 | 2779 | 3.1309
2795.8333 | 23.9982 |  | 2799.6667 | 19.4239 | 2801.5 | 7114.917 | 2803.3333 | 26.3519 | 2795.8333 | 19.4239 | 2795.8333 | 19.4239
2812.6667 | 21.5294 |  | 2816.3333 | 10.4931 | 2818 | 16667.1195 | 2820 | 390.6855 | 2812.6667 | 10.4931 | 2812.6667 | 10.4931
2829.5 | 16.3433 |  | 2833 | 3.6453 | 2835 | 13199.1486 | 2836.8333 | 28.6209 | 2829.5 | 3.6453 | 2829.5 | 3.6453
2846.3333 | 14.8079 |  | 2849.8333 | 8.4458 | 2851.8333 | 5958.829 | 2853.6667 | 20.019 | 2846.3333 | 8.4458 | 2846.3333 | 8.4458
2863.1667 | 9.6384 |  | 2866.8333 | 14.3351 | 2868.6667 | 20247.7696 | 2870.6667 | 35.0388 | 2863.1667 | 9.6384 | 2863.1667 | 9.6384
2879.6667 | 20.7669 |  | 2883.5 | 8.0897 | 2885.3333 | 106377.4381 | 2887.1667 | 241.9629 | 2879.6667 | 8.0897 | 2879.6667 | 8.0897
2896.6667 | 19.8889 |  | 2900.3333 | 8.9655 | 2902.1667 | 36247.4315 | 2904.1667 | 52.5379 | 2896.6667 | 8.9655 | 2896.6667 | 8.9655
2913.3333 | 16.7764 |  | 2917 | 19.7739 | 2919 | 111305.4344 | 2920.6667 | 17.4761 | 2913.3333 | 16.7764 | 2913.3333 | 16.7764
2930.3333 | 20.502 |  | 2933.8333 | 21.7488 | 2935.8333 | 45905.5658 | 2937.6667 | 36.5044 | 2930.3333 | 20.502 | 2930.3333 | 20.502
2946.8333 | 9.8323 |  | 2950.6667 | 8.9556 | 2952.6667 | 408585.7113 | 2954.5 | 12.0122 | 2946.8333 | 8.9556 | 2946.8333 | 8.9556
2963.6667 | 19.8956 |  | 2967.6667 | 12.9041 | 2969.3333 | 78969.1356 | 2971.3333 | 21.7077 | 2963.6667 | 12.9041 | 2963.6667 | 12.9041
2980.5 | 25.0512 |  | 2984.1667 | 10.8561 | 2986 | 131637.1694 | 2988 | 10.5031 | 2980.5 | 10.5031 | 2980.5 | 10.8561
2997.5 | 13.8947 |  | 3001 | 16.8529 | 3003 | 547255.4753 | 3004.8333 | 87.2722 | 2997.5 | 13.8947 | 2997.5 | 13.8947
3014.3333 | 10.4927 |  | 3017.8333 | 15.7472 | 3019.8333 | 137110.7437 | 3021.6667 | 18.6521 | 3014.3333 | 10.4927 | 3014.3333 | 10.4927
3031 | 6.228 |  | 3034.8333 | 18.528 | 3036.5 | 86035.7749 | 3038.3333 | 18.8263 | 3031 | 6.228 | 3031 | 6.228
3047.6667 | 13.9498 |  | 3051.5 | 12.6886 | 3053.3333 | 110166.8877 | 3055.1667 | 23.521 | 3047.6667 | 12.6886 | 3047.6667 | 12.6886
3064.5 | 17.2302 |  | 3068.1667 | 26.8164 | 3070 | 143802.1615 | 3072 | 29.8795 | 3064.5 | 17.2302 | 3064.5 | 17.2302
3081.3333 | 9.5339 |  | 3085.1667 | 18.3804 | 3087 | 137459.7994 | 3088.8333 | 20.5597 | 3081.3333 | 9.5339 | 3081.3333 | 9.5339
3098.1667 | 19.4314 |  | 3102 | 4.8822 | 3103.8333 | 18459.8998 | 3105.6667 | 18.1666 | 3098.1667 | 4.8822 | 3098.1667 | 4.8822
3114.8333 | 18.1225 |  | 3118.6667 | 23.6018 | 3120.5 | 336875.2537 | 3122.3333 | 18 | 3114.8333 | 18 | 3114.8333 | 18.1225
3131.6667 | 12.8183 |  | 3135.6667 | 15.3667 | 3137.3333 | 831803.6758 | 3139.3333 | 21.4607 | 3131.6667 | 12.8183 | 3131.6667 | 12.8183
3148.5 | 576.8225 |  | 3152.1667 | 12.9465 | 3154 | 332154.4234 | 3156 | 9.8568 | 3148.5 | 9.8568 | 3148.5 | 12.9465
3165.3333 | 31209.4052 |  | 3169.1667 | 10.7618 | 3171 | 255384.6596 | 3172.8333 | 16.3396 | 3165.3333 | 10.7618 | 3165.3333 | 10.7618
3182.5 | 111633.5693 |  | 3185.8333 | 19.2814 | 3188 | 22801.137 | 3189.6667 | 13.8135 | 3182.5 | 13.8135 | 3182.5 | 19.2814
3198.8333 | 102631.079 |  | 3202.6667 | 15.3523 | 3204.5 | 147662.289 | 3206.3333 | 19.7253 | 3198.8333 | 15.3523 | 3198.8333 | 15.3523
3215.6667 | 51848.1129 |  | 3219.5 | 51.0541 | 3221.3333 | 36002.5875 | 3223.1667 | 22.6657 | 3215.6667 | 22.6657 | 3215.6667 | 51.0541
3232.6667 | 1788225.488 |  | 3236.3333 | 22.5111 | 3238 | 79619.6333 | 3240 | 12.9211 | 3232.6667 | 12.9211 | 3232.6667 | 22.5111
3249.3333 | 24497.1715 |  | 3253 | 16.1641 | 3255 | 38586.9056 | 3256.6667 | 5.4764 | 3249.3333 | 5.4764 | 3249.3333 | 16.1641
3266.1667 | 36805.54 |  | 3269.8333 | 22.64 | 3271.6667 | 59989.9827 | 3273.6667 | 26.1031 | 3266.1667 | 22.64 | 3266.1667 | 22.64
3282.8333 | 30737.5178 |  | 3286.6667 | 11.8898 | 3288.5 | 44751.7527 | 3290.3333 | 11.4767 | 3282.8333 | 11.4767 | 3282.8333 | 11.8898
3299.6667 | 41012.2541 |  | 3303.5 | 17.1143 | 3305.3333 | 88395.9686 | 3307.1667 | 16.7034 | 3299.6667 | 16.7034 | 3299.6667 | 17.1143
3316.5 | 69087.738 |  | 3320.1667 | 21.5139 | 3322 | 43832.9979 | 3324 | 6.7713 | 3316.5 | 6.7713 | 3316.5 | 21.5139
3333.3333 | 39246.4663 |  | 3337 | 288.1572 | 3339 | 43907.7324 | 3340.6667 | 9.5137 | 3333.3333 | 9.5137 | 3333.3333 | 288.1572
3350.1667 | 28713.2268 |  | 3353.8333 | 7.0207 | 3355.6667 | 69305.8732 | 3357.6667 | 23.1981 | 3350.1667 | 7.0207 | 3350.1667 | 7.0207

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 7 |  |  | 2006-07-06 | 14:56
38904.6215 | 1 | 0 | 1 | XLPE | 3-C | Conduit
38904.6217 | 2 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38904.6219 | 1 | 0 | 1
38904.6221 | 1 | 0 | 1
38904.6223 | 1 | 0 | 1
38904.6225 | 1 | 0 | 1
38904.6227 | 1 | 0 | 1
38904.6229 | 1 | 0 | 1
38904.6231 | 1 | 0 | 1
38904.6233 | 1 | 0 | 1
38904.6235 | 1 | 0 | 1
38904.6237 | 1 | 0 | 1
38904.6239 | 1 | 0 | 1
38904.6241 | 1 | 0 | 1
38904.6243 | 1 | 0 | 1
38904.6245 | 1 | 0 | 1
38904.6247 | 1 | 0 | 1
38904.6248 | 1 | 0 | 1
38904.625 | 1 | 0 | 1
38904.6252 | 1 | 0 | 1
38904.6254 | 1 | 0 | 1
38904.6256 | 1 | 0 | 1
38904.6258 | 1 | 0 | 1
38904.626 | 1 | 0 | 1
38904.6262 | 1 | 0 | 1
38904.6264 | 1 | 0 | 1
38904.6266 | 1 | 0 | 1
38904.6268 | 1 | 0 | 1
38904.627 | 1 | 0 | 1
38904.6272 | 2 | 0 | 1
38904.6274 | 1 | 0 | 1
38904.6276 | 1 | 0 | 1
38904.6278 | 1 | 0 | 1
38904.628 | 1 | 0 | 1
38904.6281 | 1 | 0 | 1
38904.6283 | 1 | 0 | 1
38904.6285 | 1 | 0 | 1
38904.6287 | 1 | 0 | 1
38904.6289 | 1 | 0 | 1
38904.6291 | 2 | 0 | 1
38904.6293 | 1 | 0 | 1
38904.6295 | 1 | 0 | 1
38904.6297 | 1 | 0 | 1
38904.6299 | 1 | 0 | 1
38904.6301 | 1 | 0 | 1
38904.6303 | 1 | 0 | 1
38904.6305 | 1 | 0 | 1
38904.6307 | 1 | 0 | 1
38904.6309 | 1 | 0 | 1
38904.6311 | 1 | 0 | 1
38904.6313 | 1 | 0 | 1
38904.6314 | 1 | 0 | 1
38904.6316 | 1 | 0 | 1
38904.6318 | 1 | 0 | 1
38904.632 | 1 | 0 | 1
38904.6322 | 1 | 0 | 1
38904.6324 | 1 | 0 | 1
38904.6326 | 1 | 0 | 1
38904.6328 | 1 | 0 | 1
38904.633 | 1 | 0 | 1
38904.6332 | 1 | 0 | 1
38904.6334 | 1 | 0 | 1
38904.6336 | 1 | 0 | 1
38904.6338 | 1 | 0 | 1
38904.634 | 1 | 0 | 1
38904.6342 | 1 | 0 | 1
38904.6344 | 1 | 0 | 1
38904.6346 | 1 | 0 | 1
38904.6348 | 1 | 0 | 1
38904.635 | 1 | 0 | 1
38904.6352 | 1 | 0 | 1
38904.6353 | 1 | 0 | 1
38904.6355 | 1 | 0 | 1
38904.6357 | 1 | 0 | 1
38904.6359 | 1 | 0 | 1
38904.6361 | 1 | 0 | 1
38904.6363 | 1 | 0 | 1
38904.6365 | 1 | 0 | 1
38904.6367 | 1 | 0 | 1
38904.6369 | 1 | 0 | 1
38904.6371 | 1 | 0 | 1
38904.6373 | 1 | 0 | 1
38904.6375 | 1 | 0 | 1
38904.6377 | 1 | 0 | 1
38904.6379 | 1 | 0 | 1
38904.6381 | 1 | 0 | 1
38904.6383 | 1 | 0 | 1
38904.6384 | 1 | 0 | 1
38904.6386 | 1 | 0 | 1
38904.6388 | 1 | 0 | 1
38904.639 | 1 | 0 | 1
38904.6394 | 1 | 0 | 1
38904.6396 | 1 | 0 | 1
38904.6398 | 1 | 0 | 1
38904.64 | 1 | 0 | 1
38904.6402 | 1 | 0 | 1
38904.6404 | 1 | 0 | 1
38904.6406 | 1 | 0 | 1
38904.6408 | 1 | 0 | 1
38904.641 | 1 | 0 | 1
38904.6412 | 1 | 0 | 1
38904.6414 | 1 | 0 | 1
38904.6416 | 1 | 0 | 1
38904.6418 | 1 | 0 | 1
38904.6419 | 1 | 0 | 1
38904.6421 | 1 | 0 | 1
38904.6423 | 1 | 0 | 1
38904.6425 | 1 | 0 | 1
38904.6427 | 1 | 0 | 1
38904.6429 | 1 | 0 | 1
38904.6431 | 1 | 0 | 1
38904.6433 | 1 | 0 | 1
38904.6435 | 1 | 0 | 1
38904.6437 | 1 | 0 | 1
38904.6439 | 1 | 0 | 1
38904.6441 | 1 | 0 | 1
38904.6443 | 1 | 0 | 1
38904.6445 | 1 | 0 | 1
38904.6447 | 1 | 0 | 1
38904.6449 | 1 | 0 | 1
38904.6451 | 1 | 0 | 1
38904.6453 | 1 | 0 | 1
38904.6455 | 1 | 0 | 1
38904.6456 | 1 | 0 | 1
38904.6458 | 1 | 0 | 1
38904.646 | 1 | 0 | 1
38904.6462 | 1 | 0 | 1
38904.6464 | 1 | 0 | 1
38904.6466 | 1 | 0 | 1
38904.6468 | 1 | 0 | 1
38904.647 | 1 | 0 | 1
38904.6472 | 1 | 0 | 1
38904.6474 | 1 | 0 | 1
38904.6476 | 1 | 0 | 1
38904.6478 | 1 | 0 | 1
38904.648 | 1 | 0 | 1
38904.6482 | 1 | 0 | 1
38904.6484 | 1 | 0 | 1
38904.6486 | 1 | 0 | 1
38904.6488 | 1 | 0 | 1
38904.6489 | 1 | 0 | 1
38904.6491 | 1 | 0 | 1
38904.6493 | 1 | 0 | 1
38904.6495 | 1 | 0 | 1
38904.6497 | 1 | 0 | 1
38904.6499 | 2 | 0 | 1
38904.6501 | 1 | 0 | 1
38904.6503 | 2 | 2 | 1
38904.6505 | 89 | 92 | 1
38904.6507 | 1050 | 995 | 1
38904.6509 | 984 | 922 | 1
38904.6511 | 928 | 921 | 1
38904.6513 | 900 | 818 | 1
38904.6515 | 1012 | 1023 | 1
38904.6517 | 895 | 860 | 1
38904.6519 | 1008 | 917 | 1
38904.6521 | 930 | 844 | 1
38904.6523 | 908 | 818 | 1
38904.6525 | 1045 | 953 | 1
38904.6526 | 1131 | 825 | 1
38904.6528 | 1160 | 1077 | 1
38904.653 | 1030 | 926 | 1
38904.6532 | 912 | 826 | 1
38904.6534 | 1175 | 1064 | 1
38904.6536 | 972 | 929 | 1
38904.6538 | 936 | 832 | 1
38904.654 | 912 | 843 | 1
38904.6542 | 1129 | 776 | 1
38904.6544 | 1907 | 18 | 1
38904.6546 | 1909 | 17 | 1
38904.6548 | 2163 | 14 | 1
38904.655 | 2066 | 9 | 1
38904.6552 | 1934 | 8 | 1
38904.6554 | 2380 | 7 | 1
38904.6556 | 1880 | 6 | 1
38904.6558 | 1931 | 5 | 1
38904.6559 | 2273 | 4 | 1
38904.6561 | 1859 | 4 | 1
38904.6563 | 2337 | 3 | 1
38904.6565 | 2263 | 1 | 1
38904.6567 | 1928 | 1 | 1
38904.6569 | 1929 | 2 | 1
38904.6571 | 1847 | 1 | 1
38904.6573 | 2395 | 2 | 1
38904.6575 | 1947 | 1 | 1
38904.6577 | 1892 | 2 | 1
38904.6579 | 2108 | 2 | 1
38904.6581 | 2407 | 1 | 1
38904.6583 | 2191 | 1 | 1
38904.6585 | 2333 | 1 | 1
38904.6587 | 1989 | 1 | 1
38904.6589 | 2401 | 1 | 1
38904.6591 | 1991 | 1 | 1
38904.6592 | 2402 | 1 | 1
38904.6594 | 1988 | 1 | 1
38904.6596 | 1948 | 1 | 1
38904.6598 | 6 | 1 | 1
38904.66 | 5 | 1 | 1
38904.6602 | 6 | 1 | 1
38904.6604 | 6 | 1 | 1
38904.6606 | 5 | 1 | 1
38904.6608 | 8 | 1 | 1
38904.661 | 294 | 1 | 1
38904.6612 | 6 | 0 | 1
38904.6614 | 5 | 0 | 1
38904.6616 | 5 | 1 | 1
38904.6618 | 5 | 1 | 1
38904.662 | 5 | 1 | 1
38904.6216 | 1 | 0 | 2
38904.6217 | 1 | 0 | 2
38904.6219 | 1 | 0 | 2
38904.6221 | 1 | 0 | 2
38904.6223 | 1 | 0 | 2
38904.6225 | 1 | 0 | 2
38904.6227 | 1 | 0 | 2
38904.6229 | 1 | 0 | 2
38904.6231 | 1 | 0 | 2
38904.6233 | 1 | 0 | 2
38904.6235 | 1 | 0 | 2
38904.6237 | 1 | 0 | 2
38904.6239 | 1 | 0 | 2
38904.6241 | 1 | 0 | 2
38904.6243 | 1 | 0 | 2
38904.6245 | 1 | 0 | 2
38904.6247 | 1 | 0 | 2
38904.6249 | 1 | 0 | 2
38904.625 | 1 | 0 | 2
38904.6252 | 1 | 0 | 2
38904.6254 | 1 | 0 | 2
38904.6256 | 1 | 0 | 2
38904.6258 | 1 | 0 | 2
38904.626 | 1 | 0 | 2
38904.6262 | 1 | 0 | 2
38904.6264 | 1 | 0 | 2
38904.6266 | 1 | 0 | 2
38904.6268 | 1 | 0 | 2
38904.627 | 1 | 0 | 2
38904.6272 | 1 | 0 | 2
38904.6274 | 1 | 0 | 2
38904.6276 | 1 | 0 | 2
38904.6278 | 1 | 0 | 2
38904.628 | 1 | 0 | 2
38904.6282 | 1 | 0 | 2
38904.6284 | 1 | 0 | 2
38904.6286 | 1 | 0 | 2
38904.6288 | 1 | 0 | 2
38904.6289 | 1 | 0 | 2
38904.6291 | 1 | 0 | 2
38904.6293 | 1 | 0 | 2
38904.6295 | 2 | 0 | 2
38904.6297 | 1 | 0 | 2
38904.6299 | 1 | 0 | 2
38904.6301 | 1 | 0 | 2
38904.6303 | 1 | 0 | 2
38904.6305 | 2 | 0 | 2
38904.6307 | 1 | 0 | 2
38904.6309 | 1 | 0 | 2
38904.6311 | 1 | 0 | 2
38904.6313 | 1 | 0 | 2
38904.6315 | 1 | 0 | 2
38904.6317 | 1 | 0 | 2
38904.6319 | 1 | 0 | 2
38904.632 | 1 | 0 | 2
38904.6322 | 1 | 0 | 2
38904.6324 | 1 | 0 | 2
38904.6326 | 1 | 0 | 2
38904.6328 | 1 | 0 | 2
38904.633 | 1 | 0 | 2
38904.6332 | 1 | 0 | 2
38904.6334 | 1 | 0 | 2
38904.6336 | 1 | 0 | 2
38904.6338 | 1 | 0 | 2
38904.634 | 1 | 0 | 2
38904.6342 | 1 | 0 | 2
38904.6344 | 1 | 0 | 2
38904.6346 | 1 | 0 | 2
38904.6348 | 1 | 0 | 2
38904.635 | 1 | 0 | 2
38904.6352 | 1 | 0 | 2
38904.6354 | 1 | 0 | 2
38904.6356 | 1 | 0 | 2
38904.6357 | 1 | 0 | 2
38904.6359 | 1 | 0 | 2
38904.6361 | 1 | 0 | 2
38904.6363 | 1 | 0 | 2
38904.6365 | 1 | 0 | 2
38904.6367 | 1 | 0 | 2
38904.6369 | 1 | 0 | 2
38904.6371 | 1 | 0 | 2
38904.6373 | 1 | 0 | 2
38904.6375 | 1 | 0 | 2
38904.6377 | 1 | 0 | 2
38904.6379 | 1 | 0 | 2
38904.6381 | 1 | 0 | 2
38904.6383 | 1 | 0 | 2
38904.6385 | 1 | 0 | 2
38904.6387 | 1 | 0 | 2
38904.6389 | 1 | 0 | 2
38904.6391 | 1 | 0 | 2
38904.6392 | 1 | 0 | 2
38904.6394 | 1 | 0 | 2
38904.6396 | 1 | 0 | 2
38904.6398 | 1 | 0 | 2
38904.64 | 1 | 0 | 2
38904.6402 | 1 | 0 | 2
38904.6404 | 1 | 0 | 2
38904.6406 | 1 | 0 | 2
38904.6408 | 1 | 0 | 2
38904.641 | 1 | 0 | 2
38904.6412 | 1 | 0 | 2
38904.6414 | 1 | 0 | 2
38904.6416 | 1 | 0 | 2
38904.6418 | 1 | 0 | 2
38904.642 | 1 | 0 | 2
38904.6422 | 1 | 0 | 2
38904.6423 | 1 | 0 | 2
38904.6425 | 2 | 0 | 2
38904.6427 | 1 | 0 | 2
38904.6429 | 1 | 0 | 2
38904.6431 | 1 | 0 | 2
38904.6433 | 1 | 0 | 2
38904.6435 | 1 | 0 | 2
38904.6437 | 1 | 0 | 2
38904.6439 | 1 | 0 | 2
38904.6441 | 1 | 0 | 2
38904.6443 | 1 | 0 | 2
38904.6445 | 1 | 0 | 2
38904.6447 | 1 | 0 | 2
38904.6449 | 1 | 0 | 2
38904.6451 | 1 | 0 | 2
38904.6453 | 1 | 0 | 2
38904.6455 | 1 | 1 | 2
38904.6457 | 1 | 0 | 2
38904.6459 | 1 | 0 | 2
38904.6461 | 1 | 0 | 2
38904.6462 | 1 | 0 | 2
38904.6464 | 1 | 0 | 2
38904.6466 | 1 | 0 | 2
38904.6468 | 1 | 0 | 2
38904.647 | 1 | 0 | 2
38904.6472 | 1 | 0 | 2
38904.6474 | 1 | 0 | 2
38904.6476 | 1 | 0 | 2
38904.6478 | 1 | 0 | 2
38904.648 | 1 | 0 | 2
38904.6482 | 1 | 0 | 2
38904.6484 | 1 | 0 | 2
38904.6486 | 1 | 0 | 2
38904.6488 | 1 | 0 | 2
38904.649 | 1 | 0 | 2
38904.6492 | 1 | 0 | 2
38904.6494 | 1 | 0 | 2
38904.6495 | 1 | 0 | 2
38904.6497 | 1 | 0 | 2
38904.6499 | 1 | 0 | 2
38904.6501 | 2 | 0 | 2
38904.6503 | 3 | 1 | 2
38904.6505 | 335 | 295 | 2
38904.6507 | 1025 | 1051 | 2
38904.6509 | 991 | 933 | 2
38904.6511 | 1113 | 1039 | 2
38904.6513 | 1031 | 948 | 2
38904.6515 | 897 | 935 | 2
38904.6517 | 1086 | 992 | 2
38904.6519 | 1145 | 1080 | 2
38904.6521 | 928 | 844 | 2
38904.6523 | 909 | 856 | 2
38904.6525 | 894 | 847 | 2
38904.6527 | 908 | 822 | 2
38904.6529 | 970 | 872 | 2
38904.653 | 1059 | 951 | 2
38904.6532 | 969 | 870 | 2
38904.6534 | 963 | 922 | 2
38904.6536 | 1023 | 977 | 2
38904.6538 | 1176 | 1069 | 2
38904.654 | 925 | 821 | 2
38904.6542 | 1589 | 629 | 2
38904.6544 | 2322 | 19 | 2
38904.6546 | 2014 | 16 | 2
38904.6548 | 2247 | 13 | 2
38904.655 | 2291 | 9 | 2
38904.6552 | 2404 | 8 | 2
38904.6554 | 2286 | 7 | 2
38904.6556 | 1970 | 6 | 2
38904.6558 | 2418 | 5 | 2
38904.656 | 2319 | 4 | 2
38904.6562 | 2211 | 3 | 2
38904.6564 | 2434 | 3 | 2
38904.6566 | 2408 | 2 | 2
38904.6567 | 2439 | 2 | 2
38904.6569 | 2154 | 2 | 2
38904.6571 | 1963 | 1 | 2
38904.6573 | 2415 | 2 | 2
38904.6575 | 2437 | 1 | 2
38904.6577 | 2433 | 1 | 2
38904.6579 | 2435 | 1 | 2
38904.6581 | 2083 | 1 | 2
38904.6583 | 2414 | 2 | 2
38904.6585 | 1910 | 1 | 2
38904.6587 | 1978 | 1 | 2
38904.6589 | 1924 | 1 | 2
38904.6591 | 2335 | 1 | 2
38904.6593 | 1909 | 1 | 2
38904.6595 | 2038 | 1 | 2
38904.6597 | 1980 | 1 | 2
38904.6598 | 2345 | 1 | 2
38904.66 | 2040 | 1 | 2
38904.6602 | 1960 | 1 | 2
38904.6604 | 2214 | 1 | 2
38904.6606 | 1969 | 1 | 2
38904.6608 | 2323 | 1 | 2
38904.661 | 1978 | 0 | 2
38904.6612 | 2415 | 1 | 2
38904.6614 | 2237 | 0 | 2
38904.6616 | 2078 | 1 | 2
38904.6618 | 2179 | 1 | 2
38904.662 | 2302 | 1 | 2
38904.6216 | 1 | 0 | 3
38904.6218 | 1 | 0 | 3
38904.622 | 1 | 0 | 3
38904.6222 | 1 | 0 | 3
38904.6223 | 1 | 0 | 3
38904.6225 | 1 | 0 | 3
38904.6227 | 1 | 0 | 3
38904.6229 | 1 | 0 | 3
38904.6231 | 2 | 0 | 3
38904.6233 | 1 | 0 | 3
38904.6235 | 1 | 0 | 3
38904.6237 | 1 | 0 | 3
38904.6239 | 1 | 0 | 3
38904.6241 | 1 | 0 | 3
38904.6243 | 1 | 0 | 3
38904.6245 | 1 | 0 | 3
38904.6247 | 1 | 0 | 3
38904.6249 | 1 | 0 | 3
38904.6251 | 1 | 0 | 3
38904.6253 | 1 | 0 | 3
38904.6255 | 1 | 0 | 3
38904.6256 | 1 | 0 | 3
38904.6258 | 1 | 0 | 3
38904.626 | 1 | 0 | 3
38904.6262 | 1 | 0 | 3
38904.6264 | 1 | 0 | 3
38904.6266 | 1 | 0 | 3
38904.6268 | 1 | 0 | 3
38904.627 | 1 | 0 | 3
38904.6272 | 1 | 0 | 3
38904.6274 | 1 | 0 | 3
38904.6276 | 1 | 0 | 3
38904.6278 | 1 | 0 | 3
38904.628 | 1 | 0 | 3
38904.6282 | 1 | 0 | 3
38904.6284 | 1 | 0 | 3
38904.6286 | 1 | 0 | 3
38904.6288 | 1 | 0 | 3
38904.629 | 1 | 0 | 3
38904.6292 | 1 | 0 | 3
38904.6294 | 1 | 0 | 3
38904.6295 | 1 | 0 | 3
38904.6297 | 1 | 0 | 3
38904.6299 | 1 | 0 | 3
38904.6301 | 1 | 0 | 3
38904.6303 | 1 | 0 | 3
38904.6305 | 1 | 0 | 3
38904.6307 | 1 | 0 | 3
38904.6309 | 1 | 0 | 3
38904.6311 | 1 | 0 | 3
38904.6313 | 1 | 0 | 3
38904.6315 | 1 | 0 | 3
38904.6317 | 1 | 0 | 3
38904.6319 | 1 | 0 | 3
38904.6321 | 1 | 0 | 3
38904.6323 | 1 | 0 | 3
38904.6325 | 1 | 0 | 3
38904.6327 | 1 | 0 | 3
38904.6328 | 1 | 0 | 3
38904.633 | 1 | 0 | 3
38904.6332 | 1 | 0 | 3
38904.6334 | 1 | 0 | 3
38904.6336 | 1 | 0 | 3
38904.6338 | 2 | 0 | 3
38904.634 | 1 | 0 | 3
38904.6342 | 1 | 0 | 3
38904.6344 | 1 | 0 | 3
38904.6346 | 1 | 0 | 3
38904.6348 | 1 | 0 | 3
38904.635 | 1 | 0 | 3
38904.6352 | 1 | 0 | 3
38904.6354 | 1 | 0 | 3
38904.6356 | 1 | 0 | 3
38904.6358 | 1 | 0 | 3
38904.636 | 1 | 0 | 3
38904.6361 | 1 | 0 | 3
38904.6363 | 1 | 0 | 3
38904.6365 | 1 | 0 | 3
38904.6367 | 1 | 0 | 3
38904.6369 | 1 | 0 | 3
38904.6371 | 1 | 0 | 3
38904.6373 | 1 | 0 | 3
38904.6375 | 1 | 0 | 3
38904.6377 | 1 | 0 | 3
38904.6379 | 1 | 0 | 3
38904.6381 | 1 | 0 | 3
38904.6383 | 1 | 0 | 3
38904.6385 | 1 | 0 | 3
38904.6387 | 1 | 0 | 3
38904.6389 | 1 | 0 | 3
38904.6391 | 1 | 0 | 3
38904.6393 | 1 | 0 | 3
38904.6395 | 1 | 0 | 3
38904.6397 | 1 | 0 | 3
38904.6398 | 1 | 0 | 3
38904.64 | 1 | 0 | 3
38904.6402 | 1 | 0 | 3
38904.6404 | 1 | 0 | 3
38904.6406 | 1 | 0 | 3
38904.6408 | 1 | 0 | 3
38904.641 | 1 | 0 | 3
38904.6412 | 1 | 0 | 3
38904.6414 | 1 | 0 | 3
38904.6416 | 1 | 0 | 3
38904.6418 | 1 | 0 | 3
38904.642 | 1 | 0 | 3
38904.6422 | 1 | 0 | 3
38904.6424 | 1 | 0 | 3
38904.6426 | 1 | 0 | 3
38904.6428 | 1 | 0 | 3
38904.643 | 1 | 0 | 3
38904.6431 | 1 | 0 | 3
38904.6433 | 1 | 0 | 3
38904.6435 | 1 | 0 | 3
38904.6437 | 1 | 0 | 3
38904.6439 | 1 | 0 | 3
38904.6441 | 1 | 0 | 3
38904.6443 | 1 | 0 | 3
38904.6445 | 1 | 0 | 3
38904.6447 | 1 | 0 | 3
38904.6449 | 1 | 0 | 3
38904.6451 | 1 | 0 | 3
38904.6453 | 1 | 0 | 3
38904.6455 | 1 | 0 | 3
38904.6457 | 1 | 0 | 3
38904.6459 | 1 | 0 | 3
38904.6461 | 1 | 0 | 3
38904.6463 | 1 | 0 | 3
38904.6465 | 1 | 0 | 3
38904.6466 | 1 | 0 | 3
38904.6468 | 1 | 0 | 3
38904.647 | 1 | 0 | 3
38904.6472 | 1 | 0 | 3
38904.6474 | 1 | 0 | 3
38904.6476 | 1 | 0 | 3
38904.6478 | 1 | 0 | 3
38904.648 | 1 | 0 | 3
38904.6482 | 1 | 0 | 3
38904.6484 | 1 | 0 | 3
38904.6486 | 1 | 0 | 3
38904.6488 | 1 | 0 | 3
38904.649 | 1 | 0 | 3
38904.6492 | 1 | 0 | 3
38904.6494 | 1 | 0 | 3
38904.6496 | 1 | 0 | 3
38904.6498 | 1 | 0 | 3
38904.65 | 1 | 0 | 3
38904.6502 | 1 | 0 | 3
38904.6503 | 2 | 1 | 3
38904.6505 | 3 | 3 | 3
38904.6507 | 10 | 17 | 3
38904.6509 | 49 | 23 | 3
38904.6511 | 971 | 1034 | 3
38904.6513 | 1131 | 1046 | 3
38904.6515 | 1034 | 937 | 3
38904.6517 | 1139 | 1040 | 3
38904.6519 | 1067 | 1078 | 3
38904.6521 | 1192 | 894 | 3
38904.6523 | 974 | 883 | 3
38904.6525 | 1065 | 1076 | 3
38904.6527 | 1042 | 1014 | 3
38904.6529 | 991 | 954 | 3
38904.6531 | 1201 | 1085 | 3
38904.6533 | 1120 | 1013 | 3
38904.6534 | 971 | 1005 | 3
38904.6536 | 1009 | 870 | 3
38904.6538 | 1201 | 1082 | 3
38904.654 | 1040 | 925 | 3
38904.6542 | 1130 | 972 | 3
38904.6544 | 2356 | 18 | 3
38904.6546 | 2254 | 16 | 3
38904.6548 | 2310 | 14 | 3
38904.655 | 2280 | 8 | 3
38904.6552 | 2388 | 8 | 3
38904.6554 | 2387 | 7 | 3
38904.6556 | 2264 | 5 | 3
38904.6558 | 2306 | 5 | 3
38904.656 | 1944 | 4 | 3
38904.6562 | 2234 | 3 | 3
38904.6564 | 2051 | 3 | 3
38904.6566 | 1941 | 2 | 3
38904.6568 | 2299 | 2 | 3
38904.657 | 2255 | 2 | 3
38904.6572 | 1971 | 2 | 3
38904.6573 | 2159 | 1 | 3
38904.6575 | 2214 | 1 | 3
38904.6577 | 2208 | 2 | 3
38904.6579 | 2004 | 1 | 3
38904.6581 | 2092 | 1 | 3
38904.6583 | 2379 | 1 | 3
38904.6585 | 2119 | 1 | 3
38904.6587 | 2401 | 1 | 3
38904.6589 | 2212 | 1 | 3
38904.6591 | 2343 | 1 | 3
38904.6593 | 2032 | 1 | 3
38904.6595 | 2413 | 1 | 3
38904.6597 | 2157 | 1 | 3
38904.6599 | 5 | 1 | 3
38904.6603 | 6 | 1 | 3
38904.6605 | 5 | 1 | 3
38904.6606 | 5 | 1 | 3
38904.6608 | 6 | 1 | 3
38904.661 | 5 | 1 | 3
38904.6612 | 6 | 0 | 3
38904.6614 | 5 | 1 | 3
38904.6616 | 6 | 0 | 3
38904.6618 | 5 | 0 | 3
38904.662 | 5 | 1 | 3
38904.6216 | 1 | 0 | 4
38904.6218 | 1 | 0 | 4
38904.622 | 1 | 0 | 4
38904.6222 | 2 | 0 | 4
38904.6224 | 1 | 0 | 4
38904.6226 | 1 | 0 | 4
38904.6228 | 1 | 0 | 4
38904.623 | 1 | 0 | 4
38904.6231 | 1 | 0 | 4
38904.6233 | 1 | 0 | 4
38904.6235 | 1 | 0 | 4
38904.6237 | 1 | 0 | 4
38904.6239 | 1 | 0 | 4
38904.6241 | 1 | 0 | 4
38904.6243 | 1 | 0 | 4
38904.6245 | 1 | 0 | 4
38904.6247 | 1 | 0 | 4
38904.6249 | 1 | 0 | 4
38904.6251 | 1 | 0 | 4
38904.6253 | 1 | 0 | 4
38904.6255 | 1 | 0 | 4
38904.6257 | 1 | 0 | 4
38904.6259 | 1 | 0 | 4
38904.6261 | 1 | 0 | 4
38904.6263 | 1 | 0 | 4
38904.6264 | 1 | 0 | 4
38904.6266 | 1 | 0 | 4
38904.6268 | 1 | 0 | 4
38904.627 | 1 | 0 | 4
38904.6272 | 1 | 0 | 4
38904.6274 | 1 | 0 | 4
38904.6276 | 1 | 0 | 4
38904.6278 | 1 | 0 | 4
38904.628 | 1 | 0 | 4
38904.6282 | 1 | 0 | 4
38904.6284 | 1 | 0 | 4
38904.6286 | 1 | 0 | 4
38904.6288 | 1 | 0 | 4
38904.629 | 1 | 0 | 4
38904.6292 | 1 | 0 | 4
38904.6294 | 1 | 0 | 4
38904.6296 | 1 | 0 | 4
38904.6297 | 1 | 0 | 4
38904.6299 | 1 | 0 | 4
38904.6301 | 1 | 0 | 4
38904.6303 | 1 | 0 | 4
38904.6305 | 1 | 0 | 4
38904.6307 | 2 | 0 | 4
38904.6309 | 1 | 0 | 4
38904.6311 | 1 | 0 | 4
38904.6313 | 1 | 0 | 4
38904.6315 | 1 | 0 | 4
38904.6317 | 1 | 0 | 4
38904.6319 | 1 | 0 | 4
38904.6321 | 1 | 0 | 4
38904.6323 | 1 | 0 | 4
38904.6325 | 1 | 0 | 4
38904.6327 | 1 | 0 | 4
38904.6329 | 1 | 0 | 4
38904.6331 | 1 | 0 | 4
38904.6333 | 1 | 0 | 4
38904.6334 | 1 | 0 | 4
38904.6336 | 1 | 0 | 4
38904.6338 | 1 | 0 | 4
38904.634 | 1 | 0 | 4
38904.6342 | 1 | 0 | 4
38904.6344 | 1 | 0 | 4
38904.6346 | 1 | 0 | 4
38904.6348 | 1 | 0 | 4
38904.635 | 1 | 0 | 4
38904.6352 | 1 | 0 | 4
38904.6354 | 1 | 0 | 4
38904.6356 | 1 | 0 | 4
38904.6358 | 1 | 0 | 4
38904.636 | 1 | 0 | 4
38904.6362 | 1 | 0 | 4
38904.6364 | 1 | 0 | 4
38904.6366 | 1 | 0 | 4
38904.6367 | 1 | 0 | 4
38904.6369 | 1 | 0 | 4
38904.6371 | 1 | 0 | 4
38904.6373 | 1 | 0 | 4
38904.6375 | 1 | 0 | 4
38904.6377 | 1 | 0 | 4
38904.6379 | 1 | 0 | 4
38904.6381 | 1 | 0 | 4
38904.6383 | 1 | 0 | 4
38904.6385 | 1 | 0 | 4
38904.6387 | 1 | 0 | 4
38904.6389 | 1 | 0 | 4
38904.6391 | 1 | 0 | 4
38904.6393 | 1 | 0 | 4
38904.6395 | 1 | 0 | 4
38904.6397 | 1 | 0 | 4
38904.6399 | 1 | 0 | 4
38904.6401 | 1 | 0 | 4
38904.6403 | 1 | 0 | 4
38904.6404 | 1 | 0 | 4
38904.6406 | 1 | 0 | 4
38904.6408 | 1 | 0 | 4
38904.641 | 1 | 0 | 4
38904.6412 | 1 | 0 | 4
38904.6414 | 1 | 0 | 4
38904.6416 | 1 | 0 | 4
38904.6418 | 1 | 0 | 4
38904.642 | 1 | 0 | 4
38904.6422 | 1 | 0 | 4
38904.6424 | 1 | 0 | 4
38904.6426 | 1 | 0 | 4
38904.6428 | 1 | 0 | 4
38904.643 | 1 | 0 | 4
38904.6432 | 1 | 0 | 4
38904.6434 | 1 | 0 | 4
38904.6436 | 1 | 0 | 4
38904.6438 | 1 | 0 | 4
38904.6439 | 1 | 0 | 4
38904.6441 | 1 | 0 | 4
38904.6443 | 1 | 0 | 4
38904.6445 | 1 | 0 | 4
38904.6447 | 1 | 0 | 4
38904.6449 | 1 | 0 | 4
38904.6451 | 1 | 0 | 4
38904.6453 | 1 | 0 | 4
38904.6455 | 1 | 0 | 4
38904.6457 | 1 | 0 | 4
38904.6459 | 1 | 0 | 4
38904.6461 | 1 | 0 | 4
38904.6463 | 1 | 0 | 4
38904.6465 | 1 | 0 | 4
38904.6467 | 1 | 0 | 4
38904.6469 | 1 | 0 | 4
38904.647 | 1 | 0 | 4
38904.6472 | 1 | 0 | 4
38904.6474 | 1 | 0 | 4
38904.6476 | 1 | 0 | 4
38904.6478 | 1 | 0 | 4
38904.648 | 1 | 0 | 4
38904.6482 | 1 | 0 | 4
38904.6484 | 1 | 0 | 4
38904.6486 | 1 | 0 | 4
38904.6488 | 1 | 0 | 4
38904.649 | 1 | 0 | 4
38904.6492 | 1 | 0 | 4
38904.6494 | 1 | 0 | 4
38904.6496 | 1 | 0 | 4
38904.6498 | 1 | 0 | 4
38904.65 | 1 | 0 | 4
38904.6502 | 1 | 0 | 4
38904.6504 | 2 | 1 | 4
38904.6506 | 2 | 3 | 4
38904.6508 | 3 | 13 | 4
38904.6509 | 58 | 59 | 4
38904.6511 | 944 | 875 | 4
38904.6513 | 1039 | 953 | 4
38904.6515 | 1008 | 982 | 4
38904.6517 | 1030 | 1050 | 4
38904.6519 | 1000 | 984 | 4
38904.6521 | 1117 | 1097 | 4
38904.6523 | 999 | 900 | 4
38904.6525 | 916 | 928 | 4
38904.6527 | 1141 | 1106 | 4
38904.6529 | 1114 | 1004 | 4
38904.6531 | 1078 | 1066 | 4
38904.6533 | 1128 | 1009 | 4
38904.6535 | 999 | 958 | 4
38904.6537 | 952 | 850 | 4
38904.6539 | 1189 | 1059 | 4
38904.6541 | 1041 | 928 | 4
38904.6542 | 1057 | 713 | 4
38904.6544 | 7 | 19 | 4
38904.6546 | 7 | 16 | 4
38904.6548 | 8 | 13 | 4
38904.655 | 7 | 9 | 4
38904.6552 | 7 | 8 | 4
38904.6554 | 9 | 6 | 4
38904.6556 | 6 | 5 | 4
38904.6558 | 7 | 4 | 4
38904.656 | 6 | 4 | 4
38904.6562 | 7 | 3 | 4
38904.6564 | 6 | 3 | 4
38904.6566 | 11 | 2 | 4
38904.6568 | 7 | 2 | 4
38904.657 | 6 | 2 | 4
38904.6572 | 250 | 2 | 4
38904.6574 | 7 | 1 | 4
38904.6575 | 5 | 2 | 4
38904.6577 | 6 | 1 | 4
38904.6579 | 6 | 1 | 4
38904.6581 | 5 | 1 | 4
38904.6583 | 6 | 1 | 4
38904.6585 | 7 | 1 | 4
38904.6587 | 6 | 1 | 4
38904.6589 | 5 | 1 | 4
38904.6591 | 6 | 1 | 4
38904.6593 | 5 | 1 | 4
38904.6595 | 6 | 1 | 4
38904.6597 | 5 | 1 | 4
38904.6599 | 5 | 1 | 4
38904.6601 | 6 | 1 | 4
38904.6603 | 5 | 1 | 4
38904.6605 | 5 | 0 | 4
38904.6607 | 5 | 0 | 4
38904.6609 | 5 | 1 | 4
38904.6611 | 5 | 0 | 4
38904.6612 | 5 | 0 | 4
38904.6614 | 5 | 0 | 4
38904.6616 | 4 | 1 | 4
38904.6618 | 5 | 0 | 4
38904.662 | 5 | 1 | 4
38904.6216 | 1 | 0 | 5
38904.6218 | 1 | 0 | 5
38904.622 | 1 | 0 | 5
38904.6222 | 1 | 0 | 5
38904.6224 | 1 | 0 | 5
38904.6226 | 1 | 0 | 5
38904.6228 | 1 | 0 | 5
38904.623 | 1 | 0 | 5
38904.6232 | 1 | 0 | 5
38904.6233 | 1 | 0 | 5
38904.6235 | 1 | 0 | 5
38904.6237 | 1 | 0 | 5
38904.6239 | 1 | 0 | 5
38904.6241 | 1 | 0 | 5
38904.6243 | 2 | 0 | 5
38904.6245 | 1 | 0 | 5
38904.6247 | 1 | 0 | 5
38904.6249 | 1 | 0 | 5
38904.6251 | 1 | 0 | 5
38904.6253 | 1 | 0 | 5
38904.6255 | 1 | 0 | 5
38904.6257 | 2 | 1 | 5
38904.6259 | 1 | 0 | 5
38904.6261 | 1 | 0 | 5
38904.6263 | 1 | 0 | 5
38904.6265 | 1 | 0 | 5
38904.6267 | 1 | 0 | 5
38904.6269 | 1 | 0 | 5
38904.627 | 1 | 0 | 5
38904.6272 | 1 | 0 | 5
38904.6274 | 1 | 0 | 5
38904.6276 | 1 | 0 | 5
38904.6278 | 1 | 0 | 5
38904.628 | 1 | 0 | 5
38904.6282 | 1 | 0 | 5
38904.6284 | 1 | 0 | 5
38904.6286 | 1 | 0 | 5
38904.6288 | 1 | 0 | 5
38904.629 | 1 | 0 | 5
38904.6292 | 1 | 0 | 5
38904.6294 | 1 | 0 | 5
38904.6296 | 1 | 0 | 5
38904.6298 | 1 | 0 | 5
38904.63 | 1 | 0 | 5
38904.6302 | 1 | 0 | 5
38904.6303 | 1 | 0 | 5
38904.6305 | 1 | 0 | 5
38904.6307 | 1 | 0 | 5
38904.6309 | 1 | 0 | 5
38904.6311 | 1 | 0 | 5
38904.6313 | 1 | 0 | 5
38904.6315 | 1 | 0 | 5
38904.6317 | 1 | 0 | 5
38904.6319 | 1 | 0 | 5
38904.6321 | 1 | 0 | 5
38904.6323 | 1 | 0 | 5
38904.6325 | 1 | 0 | 5
38904.6327 | 1 | 0 | 5
38904.6329 | 1 | 0 | 5
38904.6331 | 1 | 0 | 5
38904.6333 | 1 | 0 | 5
38904.6335 | 1 | 0 | 5
38904.6337 | 1 | 0 | 5
38904.6339 | 1 | 0 | 5
38904.634 | 1 | 0 | 5
38904.6342 | 1 | 0 | 5
38904.6344 | 1 | 0 | 5
38904.6346 | 1 | 0 | 5
38904.6348 | 1 | 0 | 5
38904.635 | 1 | 0 | 5
38904.6352 | 1 | 0 | 5
38904.6354 | 1 | 0 | 5
38904.6356 | 1 | 0 | 5
38904.6358 | 1 | 0 | 5
38904.636 | 1 | 0 | 5
38904.6362 | 1 | 0 | 5
38904.6364 | 1 | 0 | 5
38904.6366 | 1 | 0 | 5
38904.6368 | 1 | 0 | 5
38904.637 | 1 | 0 | 5
38904.6372 | 1 | 0 | 5
38904.6373 | 1 | 0 | 5
38904.6375 | 1 | 0 | 5
38904.6377 | 1 | 0 | 5
38904.6379 | 1 | 0 | 5
38904.6381 | 1 | 0 | 5
38904.6383 | 1 | 0 | 5
38904.6385 | 1 | 0 | 5
38904.6387 | 1 | 0 | 5
38904.6389 | 1 | 0 | 5
38904.6391 | 1 | 0 | 5
38904.6393 | 1 | 0 | 5
38904.6395 | 1 | 0 | 5
38904.6397 | 1 | 0 | 5
38904.6399 | 1 | 0 | 5
38904.6401 | 1 | 0 | 5
38904.6403 | 1 | 0 | 5
38904.6405 | 1 | 0 | 5
38904.6406 | 1 | 0 | 5
38904.6408 | 1 | 0 | 5
38904.641 | 1 | 0 | 5
38904.6412 | 1 | 0 | 5
38904.6414 | 1 | 0 | 5
38904.6416 | 1 | 0 | 5
38904.6418 | 1 | 0 | 5
38904.642 | 1 | 0 | 5
38904.6422 | 1 | 0 | 5
38904.6424 | 1 | 0 | 5
38904.6426 | 1 | 0 | 5
38904.6428 | 1 | 0 | 5
38904.643 | 1 | 0 | 5
38904.6432 | 1 | 0 | 5
38904.6434 | 1 | 0 | 5
38904.6436 | 1 | 0 | 5
38904.6438 | 1 | 1 | 5
38904.644 | 1 | 0 | 5
38904.6442 | 1 | 0 | 5
38904.6444 | 1 | 0 | 5
38904.6445 | 1 | 0 | 5
38904.6447 | 1 | 0 | 5
38904.6449 | 1 | 0 | 5
38904.6451 | 1 | 0 | 5
38904.6453 | 1 | 0 | 5
38904.6455 | 1 | 0 | 5
38904.6457 | 1 | 0 | 5
38904.6459 | 1 | 0 | 5
38904.6461 | 1 | 0 | 5
38904.6463 | 1 | 0 | 5
38904.6465 | 1 | 0 | 5
38904.6467 | 1 | 0 | 5
38904.6469 | 1 | 0 | 5
38904.6471 | 1 | 0 | 5
38904.6473 | 1 | 0 | 5
38904.6475 | 1 | 0 | 5
38904.6477 | 1 | 0 | 5
38904.6478 | 1 | 0 | 5
38904.648 | 1 | 0 | 5
38904.6482 | 1 | 0 | 5
38904.6484 | 1 | 0 | 5
38904.6486 | 1 | 0 | 5
38904.6488 | 1 | 0 | 5
38904.649 | 1 | 0 | 5
38904.6492 | 1 | 0 | 5
38904.6494 | 1 | 0 | 5
38904.6496 | 1 | 0 | 5
38904.6498 | 1 | 0 | 5
38904.65 | 1 | 0 | 5
38904.6502 | 1 | 0 | 5
38904.6504 | 2 | 1 | 5
38904.6506 | 247 | 280 | 5
38904.6508 | 1061 | 1085 | 5
38904.651 | 924 | 1009 | 5
38904.6512 | 980 | 909 | 5
38904.6513 | 927 | 932 | 5
38904.6515 | 1179 | 1133 | 5
38904.6517 | 1184 | 1090 | 5
38904.6519 | 1042 | 956 | 5
38904.6521 | 1212 | 1134 | 5
38904.6523 | 1208 | 1106 | 5
38904.6525 | 1049 | 1023 | 5
38904.6527 | 956 | 863 | 5
38904.6529 | 1167 | 1128 | 5
38904.6531 | 1140 | 1024 | 5
38904.6533 | 975 | 871 | 5
38904.6535 | 1004 | 969 | 5
38904.6537 | 1059 | 948 | 5
38904.6539 | 1035 | 888 | 5
38904.6541 | 1211 | 860 | 5
38904.6543 | 1026 | 871 | 5
38904.6545 | 1903 | 23 | 5
38904.6547 | 1932 | 18 | 5
38904.6548 | 2391 | 15 | 5
38904.655 | 1918 | 12 | 5
38904.6552 | 2183 | 11 | 5
38904.6554 | 2363 | 11 | 5
38904.6556 | 1849 | 9 | 5
38904.6558 | 2044 | 7 | 5
38904.656 | 2130 | 9 | 5
38904.6562 | 2389 | 8 | 5
38904.6564 | 2351 | 5 | 5
38904.6566 | 1919 | 5 | 5
38904.6568 | 2013 | 5 | 5
38904.657 | 2168 | 5 | 5
38904.6572 | 2336 | 4 | 5
38904.6574 | 2153 | 4 | 5
38904.6576 | 2026 | 4 | 5
38904.6578 | 1874 | 5 | 5
38904.658 | 2413 | 5 | 5
38904.6581 | 2175 | 4 | 5
38904.6583 | 2359 | 5 | 5
38904.6585 | 2018 | 4 | 5
38904.6587 | 1939 | 4 | 5
38904.6589 | 2111 | 4 | 5
38904.6591 | 1883 | 4 | 5
38904.6593 | 1857 | 4 | 5
38904.6595 | 2154 | 4 | 5
38904.6597 | 5 | 1 | 5
38904.6599 | 5 | 1 | 5
38904.6601 | 63 | 1 | 5
38904.6603 | 5 | 1 | 5
38904.6605 | 5 | 1 | 5
38904.6607 | 104 | 1 | 5
38904.6609 | 142 | 1 | 5
38904.6611 | 5 | 0 | 5
38904.6613 | 4 | 1 | 5
38904.6615 | 5 | 1 | 5
38904.6617 | 5 | 1 | 5
38904.6618 | 5 | 1 | 5
38904.662 | 5 | 1 | 5
38904.6216 | 1 | 0 | 6
38904.6218 | 1 | 0 | 6
38904.622 | 2 | 0 | 6
38904.6222 | 1 | 0 | 6
38904.6224 | 1 | 0 | 6
38904.6226 | 1 | 0 | 6
38904.6228 | 1 | 0 | 6
38904.623 | 1 | 0 | 6
38904.6232 | 1 | 0 | 6
38904.6234 | 1 | 0 | 6
38904.6236 | 1 | 0 | 6
38904.6238 | 1 | 0 | 6
38904.6239 | 1 | 0 | 6
38904.6241 | 1 | 0 | 6
38904.6243 | 1 | 0 | 6
38904.6245 | 1 | 0 | 6
38904.6247 | 1 | 0 | 6
38904.6249 | 1 | 0 | 6
38904.6251 | 1 | 0 | 6
38904.6253 | 1 | 0 | 6
38904.6255 | 1 | 0 | 6
38904.6257 | 1 | 0 | 6
38904.6259 | 1 | 0 | 6
38904.6261 | 1 | 0 | 6
38904.6263 | 1 | 0 | 6
38904.6265 | 1 | 0 | 6
38904.6267 | 1 | 0 | 6
38904.6269 | 1 | 0 | 6
38904.6271 | 1 | 0 | 6
38904.6273 | 1 | 0 | 6
38904.6275 | 1 | 0 | 6
38904.6276 | 1 | 0 | 6
38904.6278 | 1 | 0 | 6
38904.628 | 1 | 0 | 6
38904.6282 | 1 | 0 | 6
38904.6284 | 1 | 0 | 6
38904.6286 | 1 | 0 | 6
38904.6288 | 1 | 0 | 6
38904.629 | 1 | 0 | 6
38904.6292 | 1 | 0 | 6
38904.6294 | 1 | 0 | 6
38904.6296 | 1 | 0 | 6
38904.6298 | 1 | 0 | 6
38904.63 | 1 | 0 | 6
38904.6302 | 1 | 0 | 6
38904.6304 | 1 | 0 | 6
38904.6306 | 1 | 0 | 6
38904.6308 | 1 | 0 | 6
38904.6309 | 1 | 0 | 6
38904.6311 | 1 | 0 | 6
38904.6313 | 1 | 0 | 6
38904.6315 | 1 | 0 | 6
38904.6317 | 1 | 0 | 6
38904.6319 | 1 | 0 | 6
38904.6321 | 1 | 0 | 6
38904.6323 | 1 | 0 | 6
38904.6325 | 2 | 0 | 6
38904.6327 | 1 | 0 | 6
38904.6329 | 1 | 0 | 6
38904.6331 | 1 | 0 | 6
38904.6333 | 1 | 0 | 6
38904.6335 | 1 | 0 | 6
38904.6337 | 1 | 0 | 6
38904.6339 | 1 | 0 | 6
38904.6341 | 1 | 0 | 6
38904.6343 | 1 | 0 | 6
38904.6344 | 1 | 0 | 6
38904.6346 | 1 | 0 | 6
38904.6348 | 1 | 0 | 6
38904.635 | 1 | 0 | 6
38904.6352 | 1 | 0 | 6
38904.6354 | 1 | 0 | 6
38904.6356 | 1 | 0 | 6
38904.6358 | 1 | 0 | 6
38904.636 | 1 | 0 | 6
38904.6362 | 1 | 0 | 6
38904.6364 | 1 | 0 | 6
38904.6366 | 2 | 0 | 6
38904.6368 | 1 | 0 | 6
38904.637 | 1 | 0 | 6
38904.6372 | 1 | 0 | 6
38904.6374 | 1 | 0 | 6
38904.6376 | 1 | 0 | 6
38904.6378 | 1 | 0 | 6
38904.638 | 1 | 0 | 6
38904.6381 | 1 | 0 | 6
38904.6383 | 1 | 1 | 6
38904.6385 | 1 | 0 | 6
38904.6387 | 1 | 0 | 6
38904.6389 | 1 | 0 | 6
38904.6391 | 1 | 0 | 6
38904.6393 | 1 | 0 | 6
38904.6395 | 1 | 0 | 6
38904.6397 | 1 | 0 | 6
38904.6399 | 1 | 0 | 6
38904.6401 | 1 | 0 | 6
38904.6403 | 1 | 0 | 6
38904.6405 | 1 | 0 | 6
38904.6407 | 1 | 0 | 6
38904.6409 | 1 | 0 | 6
38904.6411 | 1 | 0 | 6
38904.6413 | 1 | 0 | 6
38904.6414 | 1 | 0 | 6
38904.6416 | 1 | 0 | 6
38904.6418 | 1 | 0 | 6
38904.642 | 1 | 0 | 6
38904.6422 | 1 | 0 | 6
38904.6426 | 1 | 0 | 6
38904.6428 | 1 | 0 | 6
38904.643 | 1 | 0 | 6
38904.6432 | 1 | 0 | 6
38904.6434 | 1 | 0 | 6
38904.6436 | 1 | 0 | 6
38904.6438 | 1 | 0 | 6
38904.644 | 1 | 0 | 6
38904.6442 | 1 | 0 | 6
38904.6444 | 1 | 0 | 6
38904.6446 | 1 | 0 | 6
38904.6448 | 1 | 0 | 6
38904.6449 | 1 | 0 | 6
38904.6451 | 1 | 0 | 6
38904.6453 | 1 | 0 | 6
38904.6455 | 1 | 0 | 6
38904.6457 | 1 | 0 | 6
38904.6459 | 1 | 0 | 6
38904.6461 | 1 | 0 | 6
38904.6463 | 1 | 0 | 6
38904.6465 | 1 | 0 | 6
38904.6467 | 1 | 0 | 6
38904.6469 | 1 | 0 | 6
38904.6471 | 1 | 0 | 6
38904.6473 | 1 | 0 | 6
38904.6475 | 1 | 0 | 6
38904.6477 | 1 | 0 | 6
38904.6479 | 1 | 0 | 6
38904.6481 | 1 | 0 | 6
38904.6483 | 1 | 0 | 6
38904.6484 | 1 | 0 | 6
38904.6486 | 1 | 0 | 6
38904.6488 | 1 | 0 | 6
38904.649 | 1 | 0 | 6
38904.6492 | 1 | 0 | 6
38904.6494 | 2 | 0 | 6
38904.6496 | 1 | 0 | 6
38904.6498 | 2 | 0 | 6
38904.65 | 1 | 0 | 6
38904.6502 | 2 | 0 | 6
38904.6504 | 11 | 1 | 6
38904.6506 | 940 | 875 | 6
38904.6508 | 1137 | 1080 | 6
38904.651 | 1061 | 999 | 6
38904.6512 | 1186 | 1124 | 6
38904.6514 | 941 | 916 | 6
38904.6516 | 1203 | 1096 | 6
38904.6517 | 1207 | 1136 | 6
38904.6519 | 1156 | 1056 | 6
38904.6521 | 1069 | 1085 | 6
38904.6523 | 1218 | 1120 | 6
38904.6525 | 1207 | 1132 | 6
38904.6527 | 1179 | 871 | 6
38904.6529 | 1209 | 1095 | 6
38904.6531 | 997 | 875 | 6
38904.6533 | 1038 | 925 | 6
38904.6535 | 1229 | 901 | 6
38904.6537 | 1187 | 1063 | 6
38904.6539 | 1150 | 1120 | 6
38904.6541 | 987 | 871 | 6
38904.6543 | 2029 | 154 | 6
38904.6545 | 1999 | 21 | 6
38904.6547 | 2095 | 18 | 6
38904.6549 | 1966 | 14 | 6
38904.6551 | 1945 | 11 | 6
38904.6553 | 2211 | 11 | 6
38904.6554 | 2336 | 11 | 6
38904.6556 | 1909 | 9 | 6
38904.6558 | 2422 | 9 | 6
38904.656 | 2065 | 8 | 6
38904.6562 | 2095 | 6 | 6
38904.6564 | 1874 | 6 | 6
38904.6566 | 2019 | 5 | 6
38904.6568 | 2393 | 6 | 6
38904.657 | 2409 | 6 | 6
38904.6572 | 1957 | 4 | 6
38904.6574 | 2171 | 5 | 6
38904.6576 | 2302 | 5 | 6
38904.6578 | 1895 | 3 | 6
38904.658 | 2288 | 5 | 6
38904.6582 | 2305 | 5 | 6
38904.6584 | 1894 | 3 | 6
38904.6586 | 1965 | 3 | 6
38904.6588 | 2026 | 2 | 6
38904.6589 | 1912 | 3 | 6
38904.6591 | 2184 | 4 | 6
38904.6593 | 1883 | 4 | 6
38904.6595 | 2051 | 3 | 6
38904.6597 | 2440 | 1 | 6
38904.6599 | 2325 | 1 | 6
38904.6601 | 2237 | 1 | 6
38904.6603 | 2290 | 1 | 6
38904.6605 | 2248 | 1 | 6
38904.6607 | 1931 | 1 | 6
38904.6609 | 2262 | 1 | 6
38904.6611 | 1909 | 1 | 6
38904.6613 | 2363 | 1 | 6
38904.6615 | 2351 | 0 | 6
38904.6617 | 2420 | 0 | 6
38904.6619 | 2402 | 1 | 6
38904.6621 | 2426 | 1 | 6
38904.6216 | 1 | 0 | 7
38904.6218 | 1 | 0 | 7
38904.622 | 1 | 0 | 7
38904.6222 | 1 | 0 | 7
38904.6224 | 1 | 0 | 7
38904.6226 | 1 | 0 | 7
38904.6228 | 1 | 0 | 7
38904.623 | 1 | 0 | 7
38904.6232 | 1 | 0 | 7
38904.6234 | 1 | 0 | 7
38904.6236 | 1 | 0 | 7
38904.6238 | 1 | 0 | 7
38904.624 | 1 | 0 | 7
38904.6242 | 1 | 0 | 7
38904.6244 | 1 | 0 | 7
38904.6245 | 1 | 0 | 7
38904.6247 | 1 | 0 | 7
38904.6249 | 1 | 0 | 7
38904.6251 | 1 | 0 | 7
38904.6253 | 1 | 0 | 7
38904.6255 | 1 | 0 | 7
38904.6257 | 1 | 0 | 7
38904.6259 | 1 | 0 | 7
38904.6261 | 1 | 0 | 7
38904.6263 | 1 | 0 | 7
38904.6265 | 1 | 0 | 7
38904.6267 | 1 | 0 | 7
38904.6269 | 1 | 0 | 7
38904.6271 | 1 | 0 | 7
38904.6273 | 1 | 0 | 7
38904.6275 | 1 | 0 | 7
38904.6277 | 1 | 0 | 7
38904.6279 | 1 | 0 | 7
38904.628 | 1 | 0 | 7
38904.6282 | 1 | 0 | 7
38904.6284 | 1 | 0 | 7
38904.6286 | 1 | 0 | 7
38904.6288 | 1 | 0 | 7
38904.629 | 1 | 0 | 7
38904.6292 | 1 | 0 | 7
38904.6294 | 1 | 0 | 7
38904.6296 | 1 | 0 | 7
38904.6298 | 1 | 0 | 7
38904.63 | 1 | 0 | 7
38904.6302 | 1 | 0 | 7
38904.6304 | 1 | 0 | 7
38904.6306 | 1 | 0 | 7
38904.6308 | 1 | 0 | 7
38904.631 | 1 | 0 | 7
38904.6312 | 1 | 0 | 7
38904.6314 | 1 | 0 | 7
38904.6316 | 1 | 0 | 7
38904.6317 | 1 | 0 | 7
38904.6319 | 1 | 0 | 7
38904.6321 | 1 | 0 | 7
38904.6323 | 1 | 0 | 7
38904.6325 | 1 | 0 | 7
38904.6327 | 1 | 0 | 7
38904.6329 | 1 | 0 | 7
38904.6331 | 1 | 0 | 7
38904.6333 | 1 | 0 | 7
38904.6335 | 1 | 0 | 7
38904.6337 | 1 | 0 | 7
38904.6339 | 1 | 0 | 7
38904.6341 | 1 | 0 | 7
38904.6343 | 1 | 0 | 7
38904.6345 | 1 | 0 | 7
38904.6347 | 1 | 0 | 7
38904.6348 | 1 | 0 | 7
38904.635 | 1 | 0 | 7
38904.6352 | 1 | 0 | 7
38904.6354 | 1 | 0 | 7
38904.6356 | 1 | 0 | 7
38904.6358 | 1 | 0 | 7
38904.636 | 1 | 0 | 7
38904.6362 | 1 | 1 | 7
38904.6364 | 1 | 0 | 7
38904.6366 | 1 | 0 | 7
38904.6368 | 1 | 0 | 7
38904.637 | 1 | 0 | 7
38904.6372 | 1 | 0 | 7
38904.6374 | 1 | 0 | 7
38904.6376 | 1 | 0 | 7
38904.6378 | 1 | 0 | 7
38904.638 | 1 | 0 | 7
38904.6382 | 1 | 0 | 7
38904.6384 | 2 | 0 | 7
38904.6386 | 1 | 0 | 7
38904.6387 | 1 | 0 | 7
38904.6389 | 1 | 0 | 7
38904.6391 | 1 | 0 | 7
38904.6393 | 1 | 0 | 7
38904.6395 | 1 | 0 | 7
38904.6397 | 1 | 0 | 7
38904.6399 | 1 | 0 | 7
38904.6401 | 1 | 0 | 7
38904.6403 | 1 | 0 | 7
38904.6405 | 1 | 0 | 7
38904.6407 | 1 | 0 | 7
38904.6409 | 1 | 0 | 7
38904.6411 | 1 | 0 | 7
38904.6413 | 1 | 0 | 7
38904.6415 | 1 | 0 | 7
38904.6417 | 1 | 0 | 7
38904.6419 | 1 | 1 | 7
38904.642 | 1 | 0 | 7
38904.6422 | 1 | 0 | 7
38904.6424 | 1 | 0 | 7
38904.6426 | 1 | 0 | 7
38904.6428 | 1 | 0 | 7
38904.643 | 1 | 0 | 7
38904.6432 | 1 | 0 | 7
38904.6434 | 1 | 1 | 7
38904.6436 | 1 | 0 | 7
38904.6438 | 1 | 0 | 7
38904.644 | 1 | 0 | 7
38904.6442 | 1 | 0 | 7
38904.6444 | 1 | 0 | 7
38904.6446 | 1 | 0 | 7
38904.6448 | 1 | 0 | 7
38904.645 | 1 | 0 | 7
38904.6452 | 1 | 0 | 7
38904.6453 | 1 | 0 | 7
38904.6455 | 1 | 0 | 7
38904.6457 | 1 | 0 | 7
38904.6459 | 1 | 0 | 7
38904.6461 | 1 | 0 | 7
38904.6463 | 1 | 0 | 7
38904.6465 | 1 | 0 | 7
38904.6467 | 1 | 0 | 7
38904.6469 | 1 | 0 | 7
38904.6471 | 1 | 0 | 7
38904.6473 | 1 | 0 | 7
38904.6475 | 1 | 0 | 7
38904.6477 | 1 | 0 | 7
38904.6479 | 1 | 0 | 7
38904.6481 | 1 | 0 | 7
38904.6483 | 1 | 0 | 7
38904.6485 | 1 | 0 | 7
38904.6487 | 1 | 0 | 7
38904.6489 | 1 | 0 | 7
38904.6491 | 1 | 0 | 7
38904.6492 | 1 | 0 | 7
38904.6494 | 1 | 0 | 7
38904.6496 | 1 | 0 | 7
38904.6498 | 1 | 0 | 7
38904.65 | 1 | 0 | 7
38904.6502 | 1 | 0 | 7
38904.6504 | 3 | 0 | 7
38904.6506 | 5 | 15 | 7
38904.6508 | 11 | 18 | 7
38904.651 | 407 | 344 | 7
38904.6512 | 1073 | 1072 | 7
38904.6514 | 895 | 841 | 7
38904.6516 | 1142 | 1047 | 7
38904.6518 | 886 | 862 | 7
38904.652 | 1139 | 1069 | 7
38904.6522 | 1152 | 904 | 7
38904.6523 | 927 | 840 | 7
38904.6525 | 1102 | 1067 | 7
38904.6527 | 1029 | 999 | 7
38904.6529 | 973 | 872 | 7
38904.6531 | 1127 | 1061 | 7
38904.6533 | 1002 | 975 | 7
38904.6535 | 1149 | 1067 | 7
38904.6537 | 1174 | 879 | 7
38904.6539 | 1141 | 1016 | 7
38904.6541 | 898 | 836 | 7
38904.6543 | 2273 | 16 | 7
38904.6545 | 2002 | 19 | 7
38904.6547 | 2382 | 15 | 7
38904.6549 | 2177 | 11 | 7
38904.6551 | 2357 | 8 | 7
38904.6553 | 2386 | 7 | 7
38904.6555 | 2391 | 6 | 7
38904.6557 | 2177 | 5 | 7
38904.6558 | 2300 | 4 | 7
38904.656 | 2424 | 4 | 7
38904.6562 | 2215 | 3 | 7
38904.6564 | 2162 | 3 | 7
38904.6566 | 2106 | 2 | 7
38904.6568 | 2350 | 2 | 7
38904.657 | 2158 | 2 | 7
38904.6572 | 1895 | 1 | 7
38904.6574 | 2386 | 1 | 7
38904.6576 | 2246 | 1 | 7
38904.6578 | 1880 | 1 | 7
38904.658 | 2020 | 1 | 7
38904.6582 | 2257 | 1 | 7
38904.6584 | 1959 | 1 | 7
38904.6586 | 2263 | 1 | 7
38904.6588 | 1922 | 1 | 7
38904.659 | 2333 | 1 | 7
38904.6592 | 2352 | 1 | 7
38904.6594 | 1990 | 1 | 7
38904.6595 | 2050 | 1 | 7
38904.6597 | 2156 | 1 | 7
38904.6599 | 2435 | 1 | 7
38904.6601 | 2357 | 1 | 7
38904.6603 | 2315 | 1 | 7
38904.6605 | 2247 | 1 | 7
38904.6607 | 1878 | 1 | 7
38904.6609 | 2225 | 1 | 7
38904.6611 | 2208 | 1 | 7
38904.6613 | 2381 | 0 | 7
38904.6615 | 1894 | 1 | 7
38904.6617 | 2348 | 1 | 7
38904.6619 | 2046 | 1 | 7
38904.6621 | 2413 | 1 | 7
38904.6217 | 1 | 0 | 8
38904.6218 | 1 | 0 | 8
38904.622 | 1 | 0 | 8
38904.6222 | 1 | 0 | 8
38904.6224 | 1 | 0 | 8
38904.6226 | 1 | 0 | 8
38904.6228 | 1 | 0 | 8
38904.623 | 2 | 0 | 8
38904.6232 | 1 | 0 | 8
38904.6234 | 1 | 0 | 8
38904.6236 | 1 | 0 | 8
38904.6238 | 1 | 0 | 8
38904.624 | 1 | 0 | 8
38904.6242 | 1 | 0 | 8
38904.6244 | 1 | 0 | 8
38904.6246 | 1 | 0 | 8
38904.6248 | 1 | 0 | 8
38904.625 | 1 | 0 | 8
38904.6252 | 1 | 0 | 8
38904.6253 | 1 | 0 | 8
38904.6255 | 1 | 0 | 8
38904.6257 | 1 | 0 | 8
38904.6259 | 1 | 1 | 8
38904.6261 | 1 | 0 | 8
38904.6263 | 1 | 0 | 8
38904.6265 | 1 | 0 | 8
38904.6267 | 2 | 0 | 8
38904.6269 | 1 | 0 | 8
38904.6271 | 1 | 1 | 8
38904.6273 | 1 | 0 | 8
38904.6275 | 1 | 0 | 8
38904.6277 | 1 | 0 | 8
38904.6279 | 1 | 0 | 8
38904.6281 | 1 | 0 | 8
38904.6283 | 1 | 0 | 8
38904.6285 | 1 | 0 | 8
38904.6286 | 1 | 0 | 8
38904.6288 | 1 | 0 | 8
38904.629 | 1 | 0 | 8
38904.6292 | 1 | 0 | 8
38904.6294 | 1 | 0 | 8
38904.6296 | 1 | 0 | 8
38904.6298 | 1 | 0 | 8
38904.63 | 1 | 0 | 8
38904.6302 | 1 | 0 | 8
38904.6304 | 1 | 0 | 8
38904.6306 | 1 | 0 | 8
38904.6308 | 1 | 0 | 8
38904.631 | 1 | 0 | 8
38904.6312 | 1 | 0 | 8
38904.6314 | 1 | 0 | 8
38904.6316 | 1 | 0 | 8
38904.6318 | 1 | 0 | 8
38904.632 | 1 | 0 | 8
38904.6322 | 1 | 0 | 8
38904.6323 | 1 | 0 | 8
38904.6325 | 1 | 0 | 8
38904.6327 | 1 | 0 | 8
38904.6329 | 1 | 0 | 8
38904.6331 | 1 | 0 | 8
38904.6333 | 1 | 0 | 8
38904.6335 | 1 | 0 | 8
38904.6337 | 1 | 0 | 8
38904.6339 | 1 | 0 | 8
38904.6341 | 1 | 0 | 8
38904.6343 | 1 | 0 | 8
38904.6345 | 1 | 0 | 8
38904.6347 | 1 | 0 | 8
38904.6349 | 1 | 0 | 8
38904.6351 | 1 | 0 | 8
38904.6353 | 1 | 0 | 8
38904.6355 | 1 | 0 | 8
38904.6356 | 1 | 0 | 8
38904.6358 | 1 | 0 | 8
38904.636 | 1 | 0 | 8
38904.6362 | 1 | 0 | 8
38904.6364 | 1 | 0 | 8
38904.6366 | 1 | 0 | 8
38904.6368 | 1 | 0 | 8
38904.637 | 1 | 0 | 8
38904.6372 | 1 | 0 | 8
38904.6374 | 2 | 0 | 8
38904.6376 | 1 | 0 | 8
38904.6378 | 1 | 0 | 8
38904.638 | 1 | 0 | 8
38904.6382 | 1 | 0 | 8
38904.6384 | 1 | 0 | 8
38904.6386 | 2 | 0 | 8
38904.6388 | 1 | 0 | 8
38904.639 | 1 | 0 | 8
38904.6391 | 1 | 0 | 8
38904.6393 | 1 | 0 | 8
38904.6395 | 1 | 0 | 8
38904.6397 | 1 | 0 | 8
38904.6399 | 1 | 0 | 8
38904.6401 | 1 | 0 | 8
38904.6403 | 1 | 0 | 8
38904.6405 | 1 | 0 | 8
38904.6407 | 1 | 0 | 8
38904.6409 | 1 | 0 | 8
38904.6411 | 1 | 0 | 8
38904.6413 | 1 | 0 | 8
38904.6415 | 1 | 0 | 8
38904.6417 | 1 | 0 | 8
38904.6419 | 1 | 0 | 8
38904.6421 | 1 | 0 | 8
38904.6423 | 1 | 0 | 8
38904.6425 | 1 | 0 | 8
38904.6427 | 1 | 0 | 8
38904.6428 | 1 | 0 | 8
38904.643 | 1 | 0 | 8
38904.6432 | 1 | 0 | 8
38904.6434 | 1 | 0 | 8
38904.6436 | 1 | 0 | 8
38904.6438 | 1 | 0 | 8
38904.644 | 1 | 0 | 8
38904.6442 | 1 | 0 | 8
38904.6444 | 1 | 0 | 8
38904.6446 | 1 | 0 | 8
38904.645 | 1 | 0 | 8
38904.6452 | 1 | 0 | 8
38904.6454 | 1 | 0 | 8
38904.6456 | 1 | 0 | 8
38904.6458 | 1 | 0 | 8
38904.6459 | 1 | 0 | 8
38904.6461 | 1 | 0 | 8
38904.6463 | 1 | 0 | 8
38904.6465 | 1 | 0 | 8
38904.6467 | 1 | 0 | 8
38904.6469 | 1 | 0 | 8
38904.6471 | 1 | 0 | 8
38904.6473 | 1 | 0 | 8
38904.6475 | 1 | 0 | 8
38904.6477 | 2 | 0 | 8
38904.6479 | 1 | 0 | 8
38904.6481 | 1 | 0 | 8
38904.6483 | 1 | 0 | 8
38904.6485 | 1 | 0 | 8
38904.6487 | 1 | 0 | 8
38904.6489 | 1 | 0 | 8
38904.6491 | 1 | 0 | 8
38904.6493 | 1 | 0 | 8
38904.6495 | 1 | 0 | 8
38904.6498 | 1 | 0 | 8
38904.65 | 1 | 0 | 8
38904.6502 | 1 | 0 | 8
38904.6504 | 1 | 0 | 8
38904.6506 | 2 | 9 | 8
38904.6508 | 4 | 15 | 8
38904.651 | 201 | 319 | 8
38904.6512 | 872 | 843 | 8
38904.6514 | 1124 | 1042 | 8
38904.6516 | 1016 | 920 | 8
38904.6518 | 1086 | 996 | 8
38904.652 | 1089 | 1002 | 8
38904.6522 | 1142 | 1072 | 8
38904.6524 | 945 | 855 | 8
38904.6526 | 954 | 923 | 8
38904.6528 | 985 | 887 | 8
38904.653 | 901 | 933 | 8
38904.6531 | 957 | 850 | 8
38904.6533 | 1058 | 940 | 8
38904.6535 | 1047 | 1032 | 8
38904.6537 | 933 | 959 | 8
38904.6539 | 1051 | 1028 | 8
38904.6541 | 964 | 851 | 8
38904.6543 | 28 | 17 | 8
38904.6545 | 15 | 18 | 8
38904.6547 | 70 | 15 | 8
38904.6549 | 28 | 10 | 8
38904.6551 | 6 | 8 | 8
38904.6553 | 7 | 7 | 8
38904.6555 | 7 | 5 | 8
38904.6557 | 6 | 5 | 8
38904.6559 | 585 | 5 | 8
38904.6561 | 21 | 4 | 8
38904.6562 | 6 | 3 | 8
38904.6564 | 6 | 3 | 8
38904.6566 | 7 | 2 | 8
38904.6568 | 7 | 2 | 8
38904.657 | 6 | 2 | 8
38904.6572 | 7 | 1 | 8
38904.6574 | 7 | 1 | 8
38904.6576 | 6 | 1 | 8
38904.6578 | 5 | 1 | 8
38904.658 | 6 | 1 | 8
38904.6582 | 5 | 1 | 8
38904.6584 | 6 | 1 | 8
38904.6586 | 6 | 1 | 8
38904.6588 | 4 | 1 | 8
38904.659 | 6 | 1 | 8
38904.6592 | 5 | 1 | 8
38904.6594 | 5 | 1 | 8
38904.6596 | 6 | 1 | 8
38904.6598 | 5 | 1 | 8
38904.66 | 5 | 1 | 8
38904.6601 | 6 | 1 | 8
38904.6603 | 5 | 1 | 8
38904.6605 | 5 | 1 | 8
38904.6607 | 6 | 1 | 8
38904.6609 | 6 | 0 | 8
38904.6611 | 5 | 1 | 8
38904.6613 | 5 | 1 | 8
38904.6615 | 5 | 0 | 8
38904.6617 | 5 | 0 | 8
38904.6619 | 5 | 2 | 8
38904.6621 | 5 | 0 | 8
38904.6217 | 1 | 0 | 9
38904.6219 | 1 | 0 | 9
38904.6221 | 1 | 0 | 9
38904.6222 | 1 | 0 | 9
38904.6224 | 2 | 0 | 9
38904.6226 | 1 | 0 | 9
38904.6228 | 1 | 0 | 9
38904.623 | 1 | 0 | 9
38904.6232 | 1 | 0 | 9
38904.6234 | 1 | 0 | 9
38904.6236 | 1 | 0 | 9
38904.6238 | 1 | 0 | 9
38904.624 | 1 | 0 | 9
38904.6242 | 1 | 0 | 9
38904.6244 | 1 | 0 | 9
38904.6246 | 2 | 0 | 9
38904.6248 | 2 | 0 | 9
38904.625 | 1 | 0 | 9
38904.6252 | 1 | 0 | 9
38904.6254 | 1 | 0 | 9
38904.6256 | 1 | 0 | 9
38904.6258 | 1 | 0 | 9
38904.6259 | 1 | 0 | 9
38904.6261 | 1 | 0 | 9
38904.6263 | 1 | 0 | 9
38904.6265 | 1 | 0 | 9
38904.6267 | 1 | 0 | 9
38904.6269 | 1 | 0 | 9
38904.6271 | 1 | 0 | 9
38904.6273 | 1 | 0 | 9
38904.6275 | 1 | 0 | 9
38904.6277 | 1 | 0 | 9
38904.6279 | 1 | 0 | 9
38904.6281 | 1 | 0 | 9
38904.6283 | 2 | 0 | 9
38904.6285 | 1 | 0 | 9
38904.6287 | 1 | 0 | 9
38904.6289 | 1 | 0 | 9
38904.6291 | 1 | 0 | 9
38904.6292 | 2 | 0 | 9
38904.6294 | 1 | 0 | 9
38904.6296 | 1 | 0 | 9
38904.6298 | 1 | 0 | 9
38904.63 | 1 | 0 | 9
38904.6302 | 1 | 0 | 9
38904.6304 | 1 | 0 | 9
38904.6306 | 1 | 0 | 9
38904.6308 | 1 | 0 | 9
38904.631 | 1 | 0 | 9
38904.6312 | 1 | 0 | 9
38904.6314 | 1 | 0 | 9
38904.6316 | 1 | 0 | 9
38904.6318 | 1 | 0 | 9
38904.632 | 1 | 0 | 9
38904.6322 | 1 | 0 | 9
38904.6324 | 1 | 0 | 9
38904.6326 | 1 | 0 | 9
38904.6327 | 1 | 0 | 9
38904.6329 | 1 | 0 | 9
38904.6331 | 1 | 0 | 9
38904.6333 | 1 | 0 | 9
38904.6335 | 1 | 0 | 9
38904.6337 | 1 | 0 | 9
38904.6339 | 1 | 0 | 9
38904.6341 | 1 | 0 | 9
38904.6343 | 1 | 0 | 9
38904.6345 | 1 | 0 | 9
38904.6347 | 1 | 0 | 9
38904.6349 | 1 | 0 | 9
38904.6351 | 1 | 0 | 9
38904.6353 | 1 | 0 | 9
38904.6355 | 1 | 0 | 9
38904.6357 | 1 | 0 | 9
38904.6359 | 1 | 0 | 9
38904.6361 | 1 | 0 | 9
38904.6363 | 1 | 0 | 9
38904.6364 | 1 | 0 | 9
38904.6366 | 1 | 0 | 9
38904.6368 | 1 | 0 | 9
38904.637 | 1 | 0 | 9
38904.6372 | 1 | 0 | 9
38904.6374 | 1 | 0 | 9
38904.6376 | 1 | 0 | 9
38904.6378 | 1 | 0 | 9
38904.638 | 1 | 0 | 9
38904.6382 | 1 | 0 | 9
38904.6384 | 1 | 0 | 9
38904.6386 | 1 | 0 | 9
38904.6388 | 1 | 0 | 9
38904.639 | 1 | 0 | 9
38904.6392 | 1 | 0 | 9
38904.6394 | 1 | 0 | 9
38904.6395 | 1 | 0 | 9
38904.6397 | 1 | 0 | 9
38904.6399 | 1 | 0 | 9
38904.6401 | 1 | 0 | 9
38904.6403 | 1 | 0 | 9
38904.6405 | 1 | 1 | 9
38904.6407 | 1 | 0 | 9
38904.6409 | 1 | 0 | 9
38904.6411 | 1 | 0 | 9
38904.6413 | 1 | 0 | 9
38904.6415 | 1 | 0 | 9
38904.6417 | 1 | 0 | 9
38904.6419 | 1 | 0 | 9
38904.6421 | 1 | 0 | 9
38904.6423 | 1 | 0 | 9
38904.6425 | 1 | 0 | 9
38904.6427 | 1 | 0 | 9
38904.6429 | 1 | 0 | 9
38904.6431 | 1 | 0 | 9
38904.6432 | 1 | 0 | 9
38904.6434 | 1 | 0 | 9
38904.6436 | 1 | 0 | 9
38904.6438 | 1 | 0 | 9
38904.644 | 1 | 0 | 9
38904.6442 | 2 | 0 | 9
38904.6444 | 1 | 0 | 9
38904.6446 | 1 | 0 | 9
38904.6448 | 1 | 0 | 9
38904.645 | 1 | 0 | 9
38904.6452 | 1 | 0 | 9
38904.6454 | 1 | 0 | 9
38904.6456 | 1 | 0 | 9
38904.6458 | 1 | 0 | 9
38904.646 | 1 | 0 | 9
38904.6462 | 1 | 0 | 9
38904.6464 | 1 | 0 | 9
38904.6466 | 1 | 0 | 9
38904.6467 | 1 | 0 | 9
38904.6469 | 1 | 0 | 9
38904.6471 | 1 | 0 | 9
38904.6473 | 1 | 0 | 9
38904.6475 | 1 | 0 | 9
38904.6477 | 1 | 0 | 9
38904.6479 | 1 | 0 | 9
38904.6481 | 1 | 0 | 9
38904.6483 | 1 | 0 | 9
38904.6485 | 1 | 0 | 9
38904.6487 | 1 | 0 | 9
38904.6489 | 1 | 0 | 9
38904.6491 | 1 | 0 | 9
38904.6493 | 1 | 0 | 9
38904.6495 | 1 | 0 | 9
38904.6497 | 1 | 0 | 9
38904.6499 | 1 | 0 | 9
38904.65 | 1 | 0 | 9
38904.6502 | 485 | 451 | 9
38904.6504 | 942 | 957 | 9
38904.6506 | 1099 | 1067 | 9
38904.6508 | 964 | 976 | 9
38904.651 | 1063 | 1090 | 9
38904.6512 | 949 | 877 | 9
38904.6514 | 1072 | 1073 | 9
38904.6516 | 982 | 893 | 9
38904.6518 | 1025 | 939 | 9
38904.652 | 1101 | 1094 | 9
38904.6522 | 1175 | 1082 | 9
38904.6524 | 1150 | 1067 | 9
38904.6526 | 1005 | 976 | 9
38904.6528 | 916 | 941 | 9
38904.653 | 1139 | 1043 | 9
38904.6532 | 980 | 871 | 9
38904.6534 | 923 | 941 | 9
38904.6536 | 1179 | 1065 | 9
38904.6537 | 1037 | 925 | 9
38904.6539 | 1023 | 856 | 9
38904.6541 | 1182 | 1058 | 9
38904.6543 | 1857 | 19 | 9
38904.6545 | 2186 | 18 | 9
38904.6547 | 2103 | 15 | 9
38904.6549 | 2089 | 9 | 9
38904.6551 | 2268 | 8 | 9
38904.6553 | 2190 | 6 | 9
38904.6555 | 2078 | 6 | 9
38904.6557 | 2043 | 5 | 9
38904.6559 | 1999 | 4 | 9
38904.6561 | 2372 | 4 | 9
38904.6563 | 2377 | 3 | 9
38904.6565 | 1914 | 2 | 9
38904.6567 | 2335 | 2 | 9
38904.6569 | 2021 | 2 | 9
38904.657 | 1871 | 2 | 9
38904.6572 | 2223 | 1 | 9
38904.6574 | 2021 | 1 | 9
38904.6576 | 1912 | 2 | 9
38904.6578 | 2432 | 1 | 9
38904.658 | 1918 | 1 | 9
38904.6582 | 2046 | 1 | 9
38904.6584 | 1913 | 1 | 9
38904.6586 | 2439 | 2 | 9
38904.6588 | 1913 | 1 | 9
38904.659 | 2027 | 1 | 9
38904.6592 | 2338 | 1 | 9
38904.6594 | 2081 | 1 | 9
38904.6596 | 2322 | 1 | 9
38904.6598 | 2435 | 1 | 9
38904.66 | 2005 | 0 | 9
38904.6602 | 2026 | 1 | 9
38904.6604 | 2143 | 1 | 9
38904.6605 | 1988 | 1 | 9
38904.6607 | 2209 | 1 | 9
38904.6609 | 2249 | 1 | 9
38904.6611 | 1872 | 1 | 9
38904.6613 | 1880 | 1 | 9
38904.6615 | 2197 | 1 | 9
38904.6617 | 2049 | 0 | 9
38904.6619 | 2280 | 1 | 9
38904.6621 | 2341 | 1 | 9
38904.6217 | 1 | 0 | 10
38904.6219 | 1 | 0 | 10
38904.6221 | 1 | 0 | 10
38904.6223 | 1 | 0 | 10
38904.6225 | 1 | 0 | 10
38904.6227 | 1 | 0 | 10
38904.6228 | 1 | 0 | 10
38904.623 | 1 | 0 | 10
38904.6232 | 1 | 0 | 10
38904.6234 | 1 | 0 | 10
38904.6236 | 2 | 0 | 10
38904.6238 | 1 | 0 | 10
38904.624 | 1 | 0 | 10
38904.6242 | 1 | 0 | 10
38904.6244 | 1 | 0 | 10
38904.6246 | 1 | 0 | 10
38904.6248 | 1 | 0 | 10
38904.625 | 1 | 0 | 10
38904.6252 | 1 | 0 | 10
38904.6254 | 1 | 0 | 10
38904.6256 | 1 | 0 | 10
38904.6258 | 1 | 0 | 10
38904.626 | 1 | 0 | 10
38904.6262 | 1 | 0 | 10
38904.6264 | 1 | 0 | 10
38904.6265 | 1 | 0 | 10
38904.6267 | 1 | 0 | 10
38904.6269 | 1 | 0 | 10
38904.6271 | 1 | 0 | 10
38904.6273 | 1 | 0 | 10
38904.6275 | 1 | 0 | 10
38904.6277 | 1 | 0 | 10
38904.6279 | 1 | 0 | 10
38904.6281 | 1 | 0 | 10
38904.6283 | 1 | 0 | 10
38904.6285 | 1 | 0 | 10
38904.6287 | 1 | 0 | 10
38904.6289 | 1 | 0 | 10
38904.6291 | 1 | 0 | 10
38904.6293 | 1 | 0 | 10
38904.6295 | 1 | 0 | 10
38904.6297 | 1 | 0 | 10
38904.6298 | 1 | 0 | 10
38904.63 | 1 | 0 | 10
38904.6302 | 1 | 0 | 10
38904.6304 | 1 | 0 | 10
38904.6306 | 1 | 0 | 10
38904.6308 | 2 | 0 | 10
38904.631 | 1 | 0 | 10
38904.6312 | 1 | 0 | 10
38904.6314 | 1 | 0 | 10
38904.6316 | 1 | 0 | 10
38904.6318 | 1 | 0 | 10
38904.632 | 1 | 0 | 10
38904.6322 | 1 | 0 | 10
38904.6324 | 2 | 0 | 10
38904.6326 | 1 | 0 | 10
38904.6328 | 1 | 0 | 10
38904.633 | 1 | 0 | 10
38904.6331 | 1 | 0 | 10
38904.6333 | 1 | 0 | 10
38904.6335 | 1 | 0 | 10
38904.6337 | 1 | 0 | 10
38904.6339 | 1 | 0 | 10
38904.6341 | 1 | 0 | 10
38904.6343 | 1 | 0 | 10
38904.6345 | 1 | 0 | 10
38904.6347 | 1 | 0 | 10
38904.6349 | 1 | 0 | 10
38904.6351 | 1 | 0 | 10
38904.6353 | 1 | 0 | 10
38904.6355 | 1 | 0 | 10
38904.6357 | 1 | 0 | 10
38904.6359 | 1 | 0 | 10
38904.6361 | 2 | 0 | 10
38904.6363 | 1 | 0 | 10
38904.6365 | 1 | 0 | 10
38904.6367 | 1 | 0 | 10
38904.6369 | 1 | 0 | 10
38904.637 | 1 | 0 | 10
38904.6372 | 1 | 0 | 10
38904.6374 | 1 | 0 | 10
38904.6376 | 1 | 0 | 10
38904.6378 | 1 | 0 | 10
38904.638 | 1 | 0 | 10
38904.6382 | 1 | 0 | 10
38904.6384 | 2 | 0 | 10
38904.6386 | 1 | 0 | 10
38904.6388 | 1 | 0 | 10
38904.639 | 1 | 0 | 10
38904.6392 | 1 | 0 | 10
38904.6394 | 2 | 0 | 10
38904.6396 | 1 | 0 | 10
38904.6398 | 1 | 0 | 10
38904.64 | 1 | 0 | 10
38904.6402 | 1 | 0 | 10
38904.6403 | 1 | 0 | 10
38904.6405 | 1 | 0 | 10
38904.6407 | 1 | 0 | 10
38904.6409 | 1 | 0 | 10
38904.6411 | 1 | 0 | 10
38904.6413 | 1 | 0 | 10
38904.6415 | 1 | 0 | 10
38904.6417 | 1 | 0 | 10
38904.6419 | 1 | 0 | 10
38904.6421 | 1 | 0 | 10
38904.6423 | 1 | 0 | 10
38904.6425 | 1 | 0 | 10
38904.6427 | 1 | 0 | 10
38904.6429 | 1 | 0 | 10
38904.6431 | 1 | 0 | 10
38904.6433 | 1 | 0 | 10
38904.6435 | 1 | 0 | 10
38904.6436 | 1 | 0 | 10
38904.6438 | 1 | 0 | 10
38904.644 | 1 | 0 | 10
38904.6442 | 1 | 0 | 10
38904.6444 | 1 | 0 | 10
38904.6446 | 1 | 0 | 10
38904.6448 | 1 | 0 | 10
38904.645 | 1 | 0 | 10
38904.6452 | 1 | 0 | 10
38904.6454 | 1 | 0 | 10
38904.6456 | 1 | 0 | 10
38904.6458 | 1 | 0 | 10
38904.646 | 1 | 0 | 10
38904.6462 | 1 | 0 | 10
38904.6464 | 1 | 0 | 10
38904.6466 | 1 | 0 | 10
38904.6468 | 1 | 0 | 10
38904.647 | 1 | 0 | 10
38904.6472 | 1 | 0 | 10
38904.6473 | 1 | 0 | 10
38904.6475 | 1 | 0 | 10
38904.6477 | 1 | 0 | 10
38904.6479 | 1 | 0 | 10
38904.6481 | 1 | 0 | 10
38904.6483 | 1 | 0 | 10
38904.6485 | 1 | 0 | 10
38904.6487 | 1 | 0 | 10
38904.6489 | 1 | 0 | 10
38904.6491 | 1 | 0 | 10
38904.6493 | 1 | 0 | 10
38904.6495 | 2 | 0 | 10
38904.6497 | 1 | 0 | 10
38904.6499 | 1 | 0 | 10
38904.6501 | 117 | 90 | 10
38904.6503 | 719 | 717 | 10
38904.6505 | 1005 | 1024 | 10
38904.6506 | 918 | 1004 | 10
38904.6508 | 1018 | 1039 | 10
38904.651 | 1044 | 1079 | 10
38904.6512 | 1155 | 1078 | 10
38904.6514 | 1166 | 1068 | 10
38904.6516 | 1134 | 1092 | 10
38904.6518 | 1136 | 1098 | 10
38904.652 | 998 | 905 | 10
38904.6522 | 1056 | 951 | 10
38904.6524 | 1092 | 1000 | 10
38904.6526 | 963 | 866 | 10
38904.6528 | 997 | 895 | 10
38904.653 | 1129 | 1021 | 10
38904.6532 | 1151 | 1028 | 10
38904.6534 | 1195 | 1089 | 10
38904.6538 | 1028 | 916 | 10
38904.654 | 1008 | 1011 | 10
38904.6541 | 1137 | 999 | 10
38904.6543 | 2154 | 18 | 10
38904.6545 | 2362 | 18 | 10
38904.6547 | 2017 | 14 | 10
38904.6549 | 2429 | 10 | 10
38904.6551 | 1952 | 7 | 10
38904.6553 | 2081 | 7 | 10
38904.6555 | 2147 | 7 | 10
38904.6557 | 1970 | 5 | 10
38904.6559 | 1993 | 4 | 10
38904.6561 | 2218 | 4 | 10
38904.6563 | 2100 | 3 | 10
38904.6565 | 1993 | 2 | 10
38904.6567 | 2436 | 3 | 10
38904.6569 | 2137 | 2 | 10
38904.6571 | 1946 | 2 | 10
38904.6573 | 2255 | 2 | 10
38904.6575 | 2419 | 1 | 10
38904.6577 | 1880 | 2 | 10
38904.6578 | 2444 | 2 | 10
38904.658 | 1977 | 1 | 10
38904.6582 | 1972 | 1 | 10
38904.6584 | 2077 | 1 | 10
38904.6586 | 2093 | 1 | 10
38904.6588 | 1995 | 1 | 10
38904.659 | 2395 | 1 | 10
38904.6592 | 2155 | 1 | 10
38904.6594 | 2041 | 1 | 10
38904.6596 | 2127 | 1 | 10
38904.6598 | 2415 | 1 | 10
38904.66 | 2211 | 1 | 10
38904.6602 | 1923 | 1 | 10
38904.6604 | 2202 | 1 | 10
38904.6606 | 2136 | 1 | 10
38904.6608 | 2419 | 1 | 10
38904.6609 | 2444 | 1 | 10
38904.6611 | 2428 | 1 | 10
38904.6613 | 2144 | 1 | 10
38904.6615 | 2369 | 1 | 10
38904.6617 | 2087 | 0 | 10
38904.6619 | 2416 | 1 | 10
38904.6621 | 2400 | 1 | 10
38904.6217 | 1 | 0 | 11
38904.6219 | 1 | 0 | 11
38904.6221 | 1 | 0 | 11
38904.6223 | 1 | 0 | 11
38904.6225 | 1 | 0 | 11
38904.6227 | 1 | 0 | 11
38904.6229 | 1 | 0 | 11
38904.6231 | 1 | 0 | 11
38904.6233 | 1 | 0 | 11
38904.6234 | 1 | 0 | 11
38904.6236 | 1 | 0 | 11
38904.6238 | 1 | 0 | 11
38904.624 | 1 | 0 | 11
38904.6242 | 1 | 0 | 11
38904.6244 | 1 | 0 | 11
38904.6246 | 1 | 0 | 11
38904.6248 | 1 | 0 | 11
38904.625 | 1 | 0 | 11
38904.6252 | 1 | 0 | 11
38904.6254 | 1 | 0 | 11
38904.6256 | 1 | 0 | 11
38904.6258 | 1 | 0 | 11
38904.626 | 1 | 0 | 11
38904.6262 | 1 | 0 | 11
38904.6264 | 1 | 0 | 11
38904.6266 | 1 | 0 | 11
38904.6267 | 1 | 0 | 11
38904.6269 | 1 | 0 | 11
38904.6271 | 1 | 0 | 11
38904.6273 | 1 | 0 | 11
38904.6275 | 1 | 0 | 11
38904.6277 | 1 | 0 | 11
38904.6279 | 1 | 0 | 11
38904.6281 | 1 | 0 | 11
38904.6283 | 1 | 0 | 11
38904.6285 | 1 | 0 | 11
38904.6287 | 1 | 0 | 11
38904.6289 | 1 | 0 | 11
38904.6291 | 1 | 0 | 11
38904.6293 | 2 | 0 | 11
38904.6295 | 1 | 0 | 11
38904.6297 | 1 | 0 | 11
38904.6299 | 1 | 0 | 11
38904.6301 | 1 | 0 | 11
38904.6303 | 1 | 0 | 11
38904.6305 | 1 | 0 | 11
38904.6306 | 1 | 0 | 11
38904.6308 | 1 | 0 | 11
38904.631 | 1 | 0 | 11
38904.6312 | 1 | 0 | 11
38904.6314 | 1 | 0 | 11
38904.6316 | 1 | 0 | 11
38904.6318 | 1 | 0 | 11
38904.632 | 1 | 0 | 11
38904.6322 | 1 | 0 | 11
38904.6324 | 1 | 0 | 11
38904.6326 | 1 | 0 | 11
38904.6328 | 1 | 0 | 11
38904.633 | 1 | 0 | 11
38904.6332 | 1 | 0 | 11
38904.6334 | 1 | 0 | 11
38904.6336 | 1 | 0 | 11
38904.6338 | 1 | 0 | 11
38904.6339 | 1 | 0 | 11
38904.6341 | 1 | 0 | 11
38904.6343 | 1 | 0 | 11
38904.6345 | 1 | 0 | 11
38904.6347 | 1 | 0 | 11
38904.6349 | 1 | 0 | 11
38904.6351 | 1 | 0 | 11
38904.6353 | 1 | 0 | 11
38904.6355 | 1 | 0 | 11
38904.6357 | 1 | 0 | 11
38904.6359 | 1 | 0 | 11
38904.6361 | 1 | 0 | 11
38904.6363 | 1 | 0 | 11
38904.6365 | 1 | 0 | 11
38904.6367 | 1 | 0 | 11
38904.6369 | 1 | 0 | 11
38904.6371 | 1 | 0 | 11
38904.6373 | 1 | 0 | 11
38904.6374 | 1 | 0 | 11
38904.6376 | 1 | 0 | 11
38904.6378 | 1 | 0 | 11
38904.638 | 1 | 0 | 11
38904.6382 | 1 | 0 | 11
38904.6384 | 1 | 0 | 11
38904.6386 | 1 | 0 | 11
38904.6388 | 1 | 0 | 11
38904.639 | 1 | 0 | 11
38904.6392 | 1 | 0 | 11
38904.6394 | 1 | 0 | 11
38904.6396 | 1 | 0 | 11
38904.6398 | 1 | 0 | 11
38904.64 | 1 | 0 | 11
38904.6402 | 1 | 0 | 11
38904.6404 | 1 | 0 | 11
38904.6406 | 1 | 0 | 11
38904.6408 | 1 | 0 | 11
38904.6409 | 1 | 0 | 11
38904.6411 | 1 | 0 | 11
38904.6413 | 1 | 0 | 11
38904.6415 | 1 | 0 | 11
38904.6417 | 1 | 0 | 11
38904.6419 | 1 | 0 | 11
38904.6421 | 1 | 0 | 11
38904.6423 | 1 | 0 | 11
38904.6425 | 1 | 0 | 11
38904.6427 | 1 | 0 | 11
38904.6429 | 1 | 0 | 11
38904.6431 | 1 | 0 | 11
38904.6433 | 1 | 0 | 11
38904.6435 | 1 | 0 | 11
38904.6437 | 1 | 0 | 11
38904.6439 | 1 | 0 | 11
38904.6441 | 1 | 0 | 11
38904.6442 | 1 | 0 | 11
38904.6444 | 1 | 0 | 11
38904.6446 | 1 | 0 | 11
38904.6448 | 1 | 0 | 11
38904.645 | 1 | 0 | 11
38904.6452 | 1 | 0 | 11
38904.6454 | 1 | 0 | 11
38904.6456 | 1 | 0 | 11
38904.6458 | 1 | 0 | 11
38904.646 | 1 | 0 | 11
38904.6462 | 1 | 0 | 11
38904.6464 | 1 | 0 | 11
38904.6466 | 1 | 0 | 11
38904.6468 | 1 | 0 | 11
38904.647 | 1 | 0 | 11
38904.6472 | 1 | 0 | 11
38904.6474 | 1 | 0 | 11
38904.6476 | 1 | 0 | 11
38904.6478 | 1 | 0 | 11
38904.6479 | 1 | 0 | 11
38904.6481 | 1 | 0 | 11
38904.6483 | 2 | 0 | 11
38904.6485 | 2 | 0 | 11
38904.6487 | 1 | 0 | 11
38904.6489 | 1 | 0 | 11
38904.6491 | 1 | 0 | 11
38904.6493 | 1 | 0 | 11
38904.6495 | 1 | 0 | 11
38904.6497 | 1 | 0 | 11
38904.6499 | 1 | 0 | 11
38904.6501 | 1 | 0 | 11
38904.6503 | 2 | 11 | 11
38904.6505 | 4 | 17 | 11
38904.6507 | 5 | 17 | 11
38904.6509 | 6 | 18 | 11
38904.6511 | 287 | 265 | 11
38904.6513 | 1124 | 1046 | 11
38904.6514 | 1206 | 1125 | 11
38904.6516 | 1129 | 1107 | 11
38904.6518 | 1163 | 1133 | 11
38904.652 | 1197 | 1132 | 11
38904.6522 | 1049 | 954 | 11
38904.6524 | 937 | 864 | 11
38904.6526 | 1211 | 1115 | 11
38904.6528 | 1042 | 939 | 11
38904.653 | 1010 | 889 | 11
38904.6532 | 1191 | 1077 | 11
38904.6534 | 1101 | 985 | 11
38904.6536 | 1106 | 1075 | 11
38904.6538 | 1200 | 1120 | 11
38904.654 | 1211 | 1094 | 11
38904.6542 | 131 | 119 | 11
38904.6544 | 7 | 18 | 11
38904.6546 | 8 | 17 | 11
38904.6547 | 20 | 14 | 11
38904.6549 | 7 | 10 | 11
38904.6551 | 7 | 8 | 11
38904.6553 | 8 | 6 | 11
38904.6555 | 7 | 6 | 11
38904.6557 | 6 | 5 | 11
38904.6559 | 8 | 3 | 11
38904.6561 | 8 | 4 | 11
38904.6563 | 1130 | 3 | 11
38904.6565 | 6 | 2 | 11
38904.6567 | 6 | 2 | 11
38904.6569 | 6 | 2 | 11
38904.6571 | 6 | 1 | 11
38904.6573 | 5 | 2 | 11
38904.6575 | 6 | 1 | 11
38904.6577 | 6 | 1 | 11
38904.6579 | 6 | 1 | 11
38904.6581 | 6 | 1 | 11
38904.6583 | 6 | 1 | 11
38904.6584 | 5 | 1 | 11
38904.6586 | 149 | 1 | 11
38904.6588 | 5 | 1 | 11
38904.659 | 5 | 1 | 11
38904.6592 | 5 | 1 | 11
38904.6594 | 6 | 1 | 11
38904.6596 | 6 | 1 | 11
38904.6598 | 5 | 1 | 11
38904.66 | 5 | 1 | 11
38904.6602 | 5 | 1 | 11
38904.6604 | 5 | 1 | 11
38904.6606 | 5 | 1 | 11
38904.6608 | 5 | 0 | 11
38904.661 | 4 | 1 | 11
38904.6612 | 6 | 1 | 11
38904.6614 | 4 | 1 | 11
38904.6616 | 5 | 1 | 11
38904.6617 | 5 | 1 | 11
38904.6619 | 5 | 0 | 11
38904.6621 | 5 | 1 | 11
38904.6217 | 1 | 0 | 12
38904.6219 | 1 | 0 | 12
38904.6221 | 1 | 0 | 12
38904.6223 | 1 | 0 | 12
38904.6225 | 1 | 0 | 12
38904.6227 | 1 | 0 | 12
38904.6229 | 2 | 0 | 12
38904.6231 | 1 | 0 | 12
38904.6233 | 1 | 0 | 12
38904.6235 | 1 | 0 | 12
38904.6237 | 1 | 0 | 12
38904.6239 | 2 | 0 | 12
38904.6241 | 1 | 0 | 12
38904.6242 | 1 | 0 | 12
38904.6244 | 1 | 0 | 12
38904.6246 | 1 | 0 | 12
38904.6248 | 1 | 0 | 12
38904.625 | 1 | 0 | 12
38904.6252 | 1 | 0 | 12
38904.6254 | 1 | 0 | 12
38904.6256 | 2 | 0 | 12
38904.6258 | 1 | 0 | 12
38904.626 | 1 | 0 | 12
38904.6262 | 1 | 0 | 12
38904.6264 | 1 | 0 | 12
38904.6266 | 1 | 0 | 12
38904.6268 | 1 | 0 | 12
38904.627 | 1 | 0 | 12
38904.6272 | 1 | 0 | 12
38904.6273 | 1 | 0 | 12
38904.6275 | 1 | 0 | 12
38904.6277 | 1 | 0 | 12
38904.6279 | 1 | 0 | 12
38904.6281 | 1 | 0 | 12
38904.6283 | 1 | 0 | 12
38904.6285 | 1 | 0 | 12
38904.6287 | 1 | 0 | 12
38904.6289 | 1 | 0 | 12
38904.6291 | 1 | 0 | 12
38904.6293 | 1 | 0 | 12
38904.6295 | 1 | 0 | 12
38904.6297 | 1 | 0 | 12
38904.6299 | 1 | 0 | 12
38904.6301 | 1 | 0 | 12
38904.6303 | 1 | 0 | 12
38904.6305 | 1 | 0 | 12
38904.6307 | 1 | 0 | 12
38904.6309 | 1 | 0 | 12
38904.631 | 1 | 0 | 12
38904.6312 | 1 | 0 | 12
38904.6314 | 1 | 0 | 12
38904.6316 | 1 | 0 | 12
38904.6318 | 1 | 0 | 12
38904.632 | 1 | 0 | 12
38904.6322 | 1 | 0 | 12
38904.6324 | 1 | 0 | 12
38904.6326 | 1 | 0 | 12
38904.6328 | 1 | 0 | 12
38904.633 | 1 | 0 | 12
38904.6332 | 1 | 0 | 12
38904.6334 | 1 | 0 | 12
38904.6336 | 1 | 0 | 12
38904.6338 | 1 | 0 | 12
38904.634 | 1 | 0 | 12
38904.6342 | 1 | 0 | 12
38904.6344 | 1 | 0 | 12
38904.6345 | 1 | 0 | 12
38904.6347 | 1 | 0 | 12
38904.6349 | 1 | 0 | 12
38904.6351 | 1 | 0 | 12
38904.6353 | 1 | 0 | 12
38904.6355 | 1 | 0 | 12
38904.6357 | 1 | 0 | 12
38904.6359 | 1 | 0 | 12
38904.6361 | 1 | 0 | 12
38904.6363 | 1 | 0 | 12
38904.6365 | 1 | 0 | 12
38904.6367 | 1 | 0 | 12
38904.6369 | 1 | 0 | 12
38904.6371 | 1 | 0 | 12
38904.6373 | 1 | 0 | 12
38904.6375 | 1 | 0 | 12
38904.6377 | 1 | 0 | 12
38904.6378 | 1 | 0 | 12
38904.638 | 1 | 0 | 12
38904.6382 | 1 | 0 | 12
38904.6384 | 1 | 0 | 12
38904.6386 | 1 | 0 | 12
38904.6388 | 1 | 0 | 12
38904.639 | 1 | 0 | 12
38904.6392 | 1 | 0 | 12
38904.6394 | 1 | 0 | 12
38904.6396 | 1 | 0 | 12
38904.6398 | 1 | 0 | 12
38904.64 | 1 | 0 | 12
38904.6402 | 1 | 0 | 12
38904.6404 | 1 | 0 | 12
38904.6406 | 1 | 0 | 12
38904.6408 | 1 | 0 | 12
38904.641 | 1 | 0 | 12
38904.6412 | 1 | 0 | 12
38904.6414 | 1 | 0 | 12
38904.6415 | 1 | 0 | 12
38904.6417 | 1 | 0 | 12
38904.6419 | 1 | 0 | 12
38904.6421 | 1 | 0 | 12
38904.6423 | 1 | 0 | 12
38904.6425 | 1 | 0 | 12
38904.6427 | 1 | 0 | 12
38904.6429 | 1 | 0 | 12
38904.6431 | 1 | 0 | 12
38904.6433 | 1 | 0 | 12
38904.6435 | 1 | 0 | 12
38904.6437 | 1 | 0 | 12
38904.6439 | 1 | 0 | 12
38904.6441 | 1 | 0 | 12
38904.6443 | 1 | 0 | 12
38904.6445 | 1 | 0 | 12
38904.6447 | 1 | 0 | 12
38904.6448 | 1 | 0 | 12
38904.645 | 1 | 0 | 12
38904.6452 | 1 | 0 | 12
38904.6454 | 1 | 0 | 12
38904.6456 | 1 | 0 | 12
38904.6458 | 1 | 0 | 12
38904.646 | 1 | 0 | 12
38904.6462 | 1 | 0 | 12
38904.6464 | 1 | 0 | 12
38904.6466 | 1 | 0 | 12
38904.6468 | 1 | 0 | 12
38904.647 | 1 | 0 | 12
38904.6472 | 1 | 0 | 12
38904.6474 | 1 | 0 | 12
38904.6476 | 1 | 0 | 12
38904.6478 | 1 | 0 | 12
38904.648 | 1 | 0 | 12
38904.6482 | 1 | 0 | 12
38904.6483 | 1 | 0 | 12
38904.6485 | 1 | 0 | 12
38904.6487 | 1 | 0 | 12
38904.6489 | 1 | 0 | 12
38904.6491 | 1 | 0 | 12
38904.6493 | 1 | 0 | 12
38904.6495 | 1 | 0 | 12
38904.6497 | 1 | 0 | 12
38904.6499 | 1 | 0 | 12
38904.6501 | 1 | 0 | 12
38904.6503 | 2 | 4 | 12
38904.6505 | 3 | 12 | 12
38904.6507 | 4 | 14 | 12
38904.6509 | 57 | 45 | 12
38904.6511 | 210 | 149 | 12
38904.6513 | 948 | 861 | 12
38904.6515 | 1200 | 1133 | 12
38904.6517 | 936 | 900 | 12
38904.6519 | 1041 | 952 | 12
38904.652 | 1095 | 1081 | 12
38904.6522 | 1181 | 1070 | 12
38904.6524 | 1065 | 975 | 12
38904.6526 | 1148 | 1120 | 12
38904.6528 | 1210 | 1091 | 12
38904.653 | 952 | 977 | 12
38904.6532 | 1053 | 1072 | 12
38904.6534 | 1024 | 916 | 12
38904.6536 | 1046 | 1052 | 12
38904.6538 | 1208 | 1119 | 12
38904.654 | 1057 | 935 | 12
38904.6542 | 315 | 15 | 12
38904.6544 | 2374 | 18 | 12
38904.6546 | 2031 | 17 | 12
38904.6548 | 2036 | 14 | 12
38904.655 | 2022 | 9 | 12
38904.6552 | 1994 | 8 | 12
38904.6553 | 2198 | 6 | 12
38904.6555 | 2374 | 6 | 12
38904.6557 | 1996 | 5 | 12
38904.6559 | 1890 | 4 | 12
38904.6561 | 1936 | 4 | 12
38904.6563 | 1987 | 3 | 12
38904.6565 | 2097 | 2 | 12
38904.6567 | 1967 | 2 | 12
38904.6569 | 1872 | 2 | 12
38904.6571 | 1971 | 1 | 12
38904.6573 | 1986 | 2 | 12
38904.6575 | 2019 | 1 | 12
38904.6577 | 2109 | 2 | 12
38904.6579 | 2420 | 1 | 12
38904.6581 | 2228 | 1 | 12
38904.6583 | 2088 | 1 | 12
38904.6585 | 2336 | 1 | 12
38904.6587 | 1926 | 1 | 12
38904.6588 | 2224 | 1 | 12
38904.659 | 2012 | 1 | 12
38904.6592 | 2248 | 1 | 12
38904.6594 | 2391 | 1 | 12
38904.6596 | 1899 | 1 | 12
38904.6598 | 1924 | 1 | 12
38904.66 | 1917 | 1 | 12
38904.6602 | 2375 | 1 | 12
38904.6604 | 2011 | 1 | 12
38904.6606 | 2278 | 1 | 12
38904.6608 | 2224 | 1 | 12
38904.661 | 2325 | 1 | 12
38904.6612 | 2168 | 1 | 12
38904.6614 | 2266 | 1 | 12
38904.6616 | 2063 | 0 | 12
38904.6618 | 2425 | 1 | 12
38904.662 | 1971 | 1 | 12
38904.6622 | 2115 | 1 | 12