## Test Facts
Last row in IRMS data sheets: | 151
Time when Penlight power was initiated: | 110
Conduit dimensions/material: | OD = 2 - 7/8" (2.875") (73.0 mm)
ID = 2-1/2" (2.5") (63 mm)
wall thickness = 3/16" (0.1875") (4.76 mm)
Material = Hot-dipped galvinized steel standard rigid metal conduit
Length = 5' (1524 mm)

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 8
Test conditions: Cable: 3-conductor plus drain wire, 8AWG, PVC insulated, PVC jacketed, industrial grade General Cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 300C, nominal 6.1 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures, and four cable temperatures (see maps). Shroud power: Initiated after 110 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
110 | 0 | Initiate Penlight Heating
1355 | 1245 | The drain wire (conductor 4) shorts to external ground at less than 100 ohms (43)
1765 | 1655 | Conductor 1 shorts to conductor 2 at less than 100 ohms (10) | Very erratic conductor to conductor shorting behavior
1767-1771 | 1657-1661 | Conductor 1 shorts to conductor 3 (7), ground (7), and conductor 4 (314)
1773-1778 | 1663-1668 | Conductor 3 shorts to ground (5) and to conductor 4 (70) at less than 100 ohms
1888 | 1778 | Conductor 2 shorts to ground at less than 100 ohms (86)
1893-1907 | 1783-1797 | Conductor 2 shorts to conductor 4 (85) and conductor 3 (26) at less than 100 ohms
1907-2447 | 1797-2337 | All conductors and drain wire showing intermitent shorts to other conductors but stable hard shorts (< 100 ohms) to external ground
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).

## Thermocouple Maps
Locations for Thermocouples on conduit, on cable, and within cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Conduit outer surface, outboard from center
| TC2 | = | Conduit 2 | Conduit outer surface, center
| TC3 | = | Conduit 3 | Conduit ourter surface, outboard from center opposite side
| TC4 | = | Cable 4 | Within cable just below cable jacket, center position
| TC5 | = | Cable 5 | At cable core between conductors, center position
| TC6 | = | Cable 6 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC7 | = | Cable 7 | On outer cable surface, outboard from cable center
| TC8 | = | Cable 8 | On outer cable surface, outboard from cable center

## C-G Min
Minimum Conductor to Ground Resistances
Penlight Test 8 |  |  | 2006-07-07 | 12:58
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 | [5 empty] | 4 is Drain Wire
Penlight Time | Minimum C1-G | Penlight Time | Minimum C2-G |  | Penlight Time | Minimum C3-G | Penlight Time | Minimum C4-G | Penlight Time | Minimum Overall
-106.1667 | 248438 | -102.3333 | 249038 |  | -100.3333 | 249538 | -98.5 | 248438 | -106.1667 | 248438
-89.3333 | 248438 | -85.5 | 249038 |  | -83.6667 | 249538 | -81.8333 | 248438 | -89.3333 | 248438
-72.5 | 248438 | -69 | 249038 |  | -67 | 249538 | -65.1667 | 248438 | -72.5 | 248438
-55.6667 | 248438 | -52 | 249038 |  | -50 | 249538 | -48.3333 | 248438 | -55.6667 | 248438
-38.8333 | 248438 | -35.1667 | 249038 |  | -33.3333 | 249538 | -31.3333 | 248438 | -38.8333 | 248438
-22.1667 | 248438 | -18.3333 | 249038 |  | -16.5 | 249538 | -14.6667 | 248438 | -22.1667 | 248438
-5.3333 | 248438 | -1.6667 | 249038 |  | 0.16667 | 249538 | 2.1667 | 248438 | -5.3333 | 248438
11.3333 | 248438 | 15.1667 | 249038 |  | 17 | 249538 | 18.8333 | 248438 | 11.3333 | 248438
28.3333 | 248438 | 32 | 249038 |  | 34 | 249538 | 35.6667 | 248438 | 28.3333 | 248438
45 | 248438 | 48.6667 | 124469 |  | 50.6667 | 249538 | 52.6667 | 124169 | 45 | 124169
61.6667 | 248438 | 65.6667 | 249038 |  | 67.3333 | 249538 | 69.3333 | 124469 | 61.6667 | 124469
78.5 | 248438 | 82.3333 | 249038 |  | 84.3333 | 249538 | 86.1667 | 248438 | 78.5 | 248438
95.3333 | 248438 | 99 | 249038 |  | 101 | 249538 | 102.6667 | 248438 | 95.3333 | 248438
112.3333 | 248438 | 116 | 249038 |  | 118 | 249538 | 119.6667 | 248438 | 112.3333 | 248438
129 | 248438 | 132.6667 | 249038 |  | 134.5 | 249538 | 136.5 | 248438 | 129 | 248438
145.8333 | 248438 | 149.6667 | 249038 |  | 151.5 | 249538 | 153.3333 | 248438 | 145.8333 | 248438
162.5 | 248438 | 166.3333 | 249038 |  | 168.1667 | 249538 | 170 | 248438 | 162.5 | 248438
179.5 | 248438 | 183 | 249038 |  | 185 | 249538 | 186.8333 | 248438 | 179.5 | 248438
196.1667 | 248438 | 200 | 249038 |  | 201.8333 | 249538 | 203.6667 | 248438 | 196.1667 | 248438
213.1667 | 248438 | 216.8333 | 249038 |  | 218.5 | 249538 | 220.5 | 248438 | 213.1667 | 248438
229.6667 | 248438 | 233.6667 | 249038 |  | 235.3333 | 249538 | 237.3333 | 248438 | 229.6667 | 248438
246.5 | 248438 | 250.3333 | 249038 |  | 252.1667 | 249538 | 254 | 124869 | 246.5 | 124869
263.3333 | 248438 | 267.1667 | 249038 |  | 269 | 249538 | 270.8333 | 248438 | 263.3333 | 248438
280.1667 | 248438 | 283.8333 | 249038 |  | 285.6667 | 249538 | 287.6667 | 248438 | 280.1667 | 248438
297 | 248438 | 300.8333 | 249038 |  | 302.6667 | 249538 | 304.5 | 248438 | 297 | 248438
313.6667 | 248438 | 317.5 | 249038 |  | 319.3333 | 249538 | 321.1667 | 248438 | 313.6667 | 248438
330.5 | 248438 | 334.3333 | 249038 |  | 336.1667 | 249538 | 338 | 248438 | 330.5 | 248438
347.3333 | 248438 | 351 | 249038 |  | 353 | 249538 | 354.6667 | 248438 | 347.3333 | 248438
364.1667 | 248438 | 367.8333 | 249038 |  | 369.6667 | 249538 | 371.6667 | 248438 | 364.1667 | 248438
380.8333 | 248438 | 384.8333 | 124469 |  | 386.5 | 249538 | 388.1667 | 248438 | 380.8333 | 124469
397.6667 | 248438 | 401.5 | 249038 |  | 403.3333 | 249538 | 405.1667 | 248438 | 397.6667 | 248438
414.6667 | 248438 | 418.3333 | 249038 |  | 420 | 249538 | 422 | 248438 | 414.6667 | 248438
431.5 | 248438 | 435 | 249038 |  | 437 | 249538 | 438.8333 | 248438 | 431.5 | 248438
448.1667 | 248438 | 451.8333 | 249038 |  | 453.6667 | 249538 | 455.6667 | 248438 | 448.1667 | 248438
464.8333 | 124169 | 468.6667 | 249038 |  | 470.6667 | 249538 | 472.5 | 248438 | 464.8333 | 124169
481.6667 | 248438 | 485.5 | 249038 |  | 487.3333 | 249538 | 489.1667 | 248438 | 481.6667 | 248438
498.5 | 248438 | 502.1667 | 249038 |  | 504 | 249538 | 506 | 248438 | 498.5 | 248438
515.3333 | 248438 | 519 | 249038 |  | 521 | 249538 | 522.6667 | 248438 | 515.3333 | 248438
532.1667 | 248438 | 535.8333 | 250138 |  | 537.6667 | 249538 | 539.6667 | 248438 | 532.1667 | 248438
549 | 248438 | 552.6667 | 249038 |  | 554.5 | 249538 | 556.5 | 248438 | 549 | 248438
565.6667 | 248438 | 569.5 | 249038 |  | 571.3333 | 249538 | 573.1667 | 248438 | 565.6667 | 248438
582.5 | 248438 | 586.1667 | 249038 |  | 588 | 249538 | 590 | 248438 | 582.5 | 248438
599.3333 | 248438 | 603 | 249038 |  | 605 | 249538 | 606.6667 | 248438 | 599.3333 | 248438
616.3333 | 248438 | 619.8333 | 249038 |  | 621.8333 | 249538 | 623.6667 | 248438 | 616.3333 | 248438
633 | 248438 | 636.8333 | 249038 |  | 638.5 | 249538 | 640.3333 | 248438 | 633 | 248438
649.6667 | 248438 | 653.5 | 249038 |  | 655.3333 | 249538 | 657.1667 | 248438 | 649.6667 | 248438
666.5 | 248438 | 670.1667 | 249038 |  | 672 | 249538 | 674 | 248438 | 666.5 | 248438
683.3333 | 248438 | 687 | 249038 |  | 689 | 249538 | 690.6667 | 248438 | 683.3333 | 248438
700.1667 | 248438 | 703.8333 | 249038 |  | 705.6667 | 249538 | 707.6667 | 248438 | 700.1667 | 248438
716.8333 | 248438 | 720.6667 | 249038 |  | 722.5 | 249538 | 724.3333 | 248438 | 716.8333 | 248438
733.6667 | 248438 | 737.5 | 249038 |  | 739.3333 | 249538 | 741.1667 | 248438 | 733.6667 | 248438
750.5 | 248438 | 754.1667 | 249038 |  | 756 | 249538 | 758 | 248438 | 750.5 | 248438
767.3333 | 248438 | 771 | 249038 |  | 773 | 249538 | 774.6667 | 248438 | 767.3333 | 248438
784.1667 | 248438 | 787.8333 | 249038 |  | 789.6667 | 124869 | 791.6667 | 248438 | 784.1667 | 124869
800.8333 | 248438 | 804.6667 | 249038 |  | 806.5 | 249538 | 808.3333 | 248438 | 800.8333 | 248438
817.6667 | 248438 | 821.5 | 125119 |  | 823.3333 | 249538 | 825.1667 | 248438 | 817.6667 | 125119
834.5 | 248438 | 838.1667 | 249038 |  | 840 | 249538 | 842 | 248438 | 834.5 | 248438
851.3333 | 248438 | 855 | 249038 |  | 857 | 249538 | 858.6667 | 248438 | 851.3333 | 248438
868.1667 | 248438 | 871.8333 | 249038 |  | 873.6667 | 249538 | 875.6667 | 248438 | 868.1667 | 248438
884.8333 | 248438 | 888.6667 | 249038 |  | 890.5 | 249538 | 892.3333 | 248438 | 884.8333 | 248438
901.6667 | 248438 | 905.5 | 249038 |  | 907.3333 | 249538 | 909.1667 | 248438 | 901.6667 | 248438
918.5 | 248438 | 922.1667 | 249038 |  | 924 | 249538 | 926 | 248438 | 918.5 | 248438
935.3333 | 248438 | 939 | 249038 |  | 941 | 249538 | 942.6667 | 248438 | 935.3333 | 248438
952.1667 | 248438 | 955.8333 | 249038 |  | 957.6667 | 249538 | 959.6667 | 248438 | 952.1667 | 248438
968.8333 | 248438 | 972.6667 | 249038 |  | 974.5 | 249538 | 976.3333 | 248438 | 968.8333 | 248438
985.6667 | 248438 | 989.5 | 249038 |  | 991.3333 | 249538 | 993.1667 | 248438 | 985.6667 | 248438
1002.5 | 248438 | 1006.1667 | 249038 |  | 1008 | 249538 | 1010 | 248438 | 1002.5 | 248438
1019.3333 | 248438 | 1023 | 249038 |  | 1025 | 249538 | 1026.6667 | 248438 | 1019.3333 | 248438
1036.1667 | 248438 | 1039.8333 | 249038 |  | 1041.6667 | 249538 | 1043.6667 | 248438 | 1036.1667 | 248438
1052.8333 | 248438 | 1056.6667 | 249038 |  | 1058.5 | 249538 | 1060.3333 | 248438 | 1052.8333 | 248438
1069.6667 | 248438 | 1073.5 | 249038 |  | 1075.3333 | 249538 | 1077.1667 | 248438 | 1069.6667 | 248438
1086.5 | 248438 | 1090.1667 | 249038 |  | 1092 | 249538 | 1094 | 248438 | 1086.5 | 248438
1103.3333 | 248438 | 1107 | 249038 |  | 1109 | 249538 | 1110.6667 | 248438 | 1103.3333 | 248438
1120.1667 | 248438 | 1123.8333 | 249038 |  | 1125.6667 | 249538 | 1127.6667 | 248438 | 1120.1667 | 248438
1136.8333 | 248438 | 1140.6667 | 249038 |  | 1142.5 | 249538 | 1144.3333 | 248438 | 1136.8333 | 248438
1153.6667 | 248438 | 1157.5 | 249038 |  | 1159.3333 | 249538 | 1161.1667 | 248438 | 1153.6667 | 248438
1170.5 | 248438 | 1174 | 249038 |  | 1176 | 249538 | 1177.8333 | 248438 | 1170.5 | 248438
1187.3333 | 248438 | 1191 | 249038 |  | 1193 | 249538 | 1194.6667 | 248438 | 1187.3333 | 248438
1204.1667 | 248438 | 1207.8333 | 249038 |  | 1209.6667 | 249538 | 1211.6667 | 248438 | 1204.1667 | 248438
1220.8333 | 248438 | 1224.6667 | 249038 |  | 1226.5 | 249538 | 1228.3333 | 248438 | 1220.8333 | 248438
1237.6667 | 248438 | 1241.5 | 249038 |  | 1243.3333 | 62384.5 | 1245.1667 | 42.609 | 1237.6667 | 42.609
1254.5 | 35676.8571 | 1258 | 35648.2857 |  | 1260 | 31142.25 | 1261.8333 | 59.092 | 1254.5 | 59.092
1271.3333 | 27726.4444 | 1275 | 27704.2222 |  | 1277 | 27670.8889 | 1278.6667 | 47.0708 | 1271.3333 | 47.0708
1288.1667 | 31204.75 | 1292 | 31179.75 |  | 1293.6667 | 41606.3333 | 1295.5 | 32.3123 | 1288.1667 | 32.3123
1304.8333 | 31204.75 | 1308.6667 | 27704.2222 |  | 1310.5 | 27670.8889 | 1312.3333 | 22.4867 | 1304.8333 | 22.4867
1321.6667 | 27726.4444 | 1325.3333 | 27704.2222 |  | 1327.1667 | 27670.8889 | 1329.1667 | 7.1561 | 1321.6667 | 7.1561
1338.5 | 27726.4444 | 1342 | 27704.2222 |  | 1344 | 27670.8889 | 1345.8333 | 3.4197 | 1338.5 | 3.4197
1355.3333 | 27726.4444 | 1359 | 27704.2222 |  | 1361 | 27670.8889 | 1362.6667 | 15.7067 | 1355.3333 | 15.7067
1372.1667 | 27726.4444 | 1375.8333 | 27704.2222 |  | 1377.5 | 27670.8889 | 1379.5 | 20.7649 | 1372.1667 | 20.7649
1388.8333 | 27726.4444 | 1392.6667 | 27704.2222 |  | 1394.5 | 27670.8889 | 1396.3333 | 4.2418 | 1388.8333 | 4.2418
1405.6667 | 27726.4444 | 1409.3333 | 24923.8 |  | 1411.1667 | 27670.8889 | 1413.1667 | 3.3422 | 1405.6667 | 3.3422
1422.3333 | 27726.4444 | 1426.1667 | 27704.2222 |  | 1428 | 27670.8889 | 1429.8333 | 5.3127 | 1422.3333 | 5.3127
1439.3333 | 27726.4444 | 1442.8333 | 27704.2222 |  | 1444.8333 | 27670.8889 | 1446.6667 | 17.3418 | 1439.3333 | 17.3418
1456 | 27726.4444 | 1459.8333 | 27704.2222 |  | 1461.6667 | 27670.8889 | 1463.5 | 5.6565 | 1456 | 5.6565
1472.6667 | 27726.4444 | 1476.6667 | 31179.75 |  | 1478.3333 | 31142.25 | 1480.3333 | 7.3408 | 1472.6667 | 7.3408
1489.5 | 27726.4444 | 1493.3333 | 27704.2222 |  | 1495.3333 | 24893.8 | 1497.1667 | 7.6391 | 1489.5 | 7.6391
1506.3333 | 27726.4444 | 1510.1667 | 27704.2222 |  | 1512 | 27670.8889 | 1513.8333 | 7.454 | 1506.3333 | 7.454
1523.1667 | 27726.4444 | 1527 | 27704.2222 |  | 1528.8333 | 27670.8889 | 1530.6667 | 5.402 | 1523.1667 | 5.402
1540 | 27726.4444 | 1543.6667 | 27704.2222 |  | 1545.5 | 27670.8889 | 1547.5 | 5.5811 | 1540 | 5.5811
1556.8333 | 27726.4444 | 1560.5 | 27704.2222 |  | 1562.5 | 27670.8889 | 1564.1667 | 5.896 | 1556.8333 | 5.896
1573.5 | 27726.4444 | 1577.3333 | 27704.2222 |  | 1579.3333 | 27670.8889 | 1581.1667 | 15.1817 | 1573.5 | 15.1817
1590.3333 | 24943.8 | 1594 | 27704.2222 |  | 1596 | 27670.8889 | 1597.6667 | 12.6862 | 1590.3333 | 12.6862
1607.3333 | 27726.4444 | 1610.8333 | 27704.2222 |  | 1612.8333 | 27670.8889 | 1614.6667 | 3.2135 | 1607.3333 | 3.2135
1624 | 27726.4444 | 1627.6667 | 27704.2222 |  | 1629.5 | 27670.8889 | 1631.5 | 3.494 | 1624 | 3.494
1640.8333 | 27726.4444 | 1644.6667 | 27704.2222 |  | 1646.5 | 27670.8889 | 1648.3333 | 8.339 | 1640.8333 | 8.339
1657.5 | 7.4246 | 1661.3333 | 27582 |  | 1663.1667 | 5.1107 | 1665 | 7.724 | 1657.5 | 5.1107
1674.5 | 5.8952 | 1678 | 27582 |  | 1680 | 20.9445 | 1681.8333 | 6.0972 | 1674.5 | 5.8952
1691.1667 | 5.492 | 1694.8333 | 27582 |  | 1696.6667 | 10.9152 | 1698.6667 | 8.4835 | 1691.1667 | 5.492
1708 | 5.886 | 1711.8333 | 27704.2222 |  | 1713.5 | 9.5235 | 1715.3333 | 16.6925 | 1708 | 5.886
1724.6667 | 10.3737 | 1728.5 | 27582 |  | 1730.3333 | 15.6368 | 1732.1667 | 13.173 | 1724.6667 | 10.3737
1741.6667 | 5.007 | 1745.3333 | 27726.4444 |  | 1747 | 2.6407 | 1749 | 15.2096 | 1741.6667 | 2.6407
1758.3333 | 19.0861 | 1762 | 27726.4444 |  | 1764 | 5.3275 | 1765.6667 | 6.9721 | 1758.3333 | 5.3275
1775.3333 | 2.6806 | 1778.8333 | 85.7852 |  | 1780.8333 | 2.0634 | 1782.6667 | 17.0004 | 1775.3333 | 2.0634
1791.8333 | 2.8644 | 1795.6667 | 23.6417 |  | 1797.5 | 2.8094 | 1799.3333 | 1.689 | 1791.8333 | 1.689
1808.6667 | 2.9748 | 1812.5 | 21.5718 |  | 1814.3333 | 4.0746 | 1816.1667 | 1.8534 | 1808.6667 | 1.8534
1825.5 | 15.569 | 1829.1667 | 43.3532 |  | 1831 | 1.6472 | 1833 | 1.1523 | 1825.5 | 1.1523
1842.5 | 14.4603 | 1846 | 47.5936 |  | 1848 | 10.8247 | 1849.8333 | 5.0171 | 1842.5 | 5.0171
1859.1667 | 9.4801 | 1862.8333 | 12.6302 |  | 1864.6667 | 9.8188 | 1866.6667 | 14.4936 | 1859.1667 | 9.4801
1875.8333 | 0.83243 | 1879.6667 | 2.305 |  | 1881.5 | 11.1675 | 1883.3333 | 6.3492 | 1875.8333 | 0.83243
1892.6667 | 12.5359 | 1896.5 | 15.986 |  | 1898.3333 | 4.1863 | 1900.1667 | 0.74323 | 1892.6667 | 0.74323
1909.5 | 17.679 | 1913.1667 | 1.7595 |  | 1915 | 3.6733 | 1917 | 2.5443 | 1909.5 | 1.7595
1926.3333 | 1.157 | 1930 | 13.606 |  | 1932 | 4.4948 | 1933.6667 | 14.9161 | 1926.3333 | 1.157
1943.1667 | 9.993 | 1946.8333 | 11.5832 |  | 1948.6667 | 2.1895 | 1950.6667 | 3.3042 | 1943.1667 | 2.1895
1959.8333 | 2.8215 | 1963.6667 | 1.4609 |  | 1965.5 | 23.7813 | 1967.3333 | 1.967 | 1959.8333 | 1.4609
1976.6667 | 5.4069 | 1980.5 | 5.1801 |  | 1982.3333 | 11.3629 | 1984.1667 | 4.5901 | 1976.6667 | 4.5901
1993.5 | 4.773 | 1997.1667 | 2.4011 |  | 1999 | 2.0856 | 2001 | 4.0238 | 1993.5 | 2.0856
2010.3333 | 6.7392 | 2014 | 6.7014 |  | 2016 | 2.1544 | 2017.6667 | 20.8374 | 2010.3333 | 2.1544
2027.1667 | 7.8127 | 2030.8333 | 19.6782 |  | 2032.6667 | 3.4486 | 2034.6667 | 12.8299 | 2027.1667 | 3.4486
2043.8333 | 3.4862 | 2047.6667 | 3.1334 |  | 2049.5 | 3.9467 | 2051.3333 | 7.0195 | 2043.8333 | 3.1334
2060.6667 | 6.0625 | 2064.5 | 9.0038 |  | 2066.3333 | 3.1868 | 2068.1667 | 6.9344 | 2060.6667 | 3.1868
2077.5 | 7.6777 | 2081.1667 | 3.1139 |  | 2083 | 6.3037 | 2085 | 9.243 | 2077.5 | 3.1139
2094.3333 | 2.8271 | 2098 | 6.2592 |  | 2100 | 4.9302 | 2101.6667 | 8.9635 | 2094.3333 | 2.8271
2111.1667 | 4.7942 | 2114.8333 | 7.4204 |  | 2116.6667 | 6.4354 | 2118.6667 | 14.9972 | 2111.1667 | 4.7942
2127.8333 | 8.3476 | 2131.6667 | 11.052 |  | 2133.5 | 4.4189 | 2135.3333 | 4.4186 | 2127.8333 | 4.4186
2144.6667 | 3.3334 | 2148.5 | 9.8502 |  | 2150.3333 | 5.1391 | 2152.1667 | 13.552 | 2144.6667 | 3.3334
2161.5 | 5.8475 | 2165.1667 | 17.5107 |  | 2167 | 6.7266 | 2169 | 8.759 | 2161.5 | 5.8475
2178.3333 | 3.7635 | 2181.6667 | 13.9465 |  | 2183.6667 | 7.2698 | 2185.6667 | 16.984 | 2178.3333 | 3.7635
2195.1667 | 13.2955 | 2198.8333 | 7.7953 |  | 2200.6667 | 5.2311 | 2202.6667 | 15.6585 | 2195.1667 | 5.2311
2211.8333 | 3.9292 | 2215.6667 | 5.67 |  | 2217.5 | 1.4376 | 2219.3333 | 2.7797 | 2211.8333 | 1.4376
2228.6667 | 0.66181 | 2232.5 | 4.5273 |  | 2234.3333 | 2.8939 | 2236.1667 | 0.66805 | 2228.6667 | 0.66181
2245.5 | 0.66827 | 2249.1667 | 12.1532 |  | 2251 | 14.6829 | 2253 | 4.9278 | 2245.5 | 0.66827
2262.3333 | 9.0122 | 2266 | 8.469 |  | 2268 | 9.6219 | 2269.6667 | 0.70421 | 2262.3333 | 0.70421
2279.1667 | 12.7497 | 2282.8333 | 0.65952 |  | 2284.6667 | 0.65889 | 2286.6667 | 3.1823 | 2279.1667 | 0.65889
2295.8333 | 10.8025 | 2299.6667 | 1.5976 |  | 2301.5 | 3.5233 | 2303.3333 | 2.1529 | 2295.8333 | 1.5976
2312.6667 | 8.2273 | 2316.5 | 6.4335 |  | 2318.3333 | 5.2371 | 2320.1667 | 8.716 | 2312.6667 | 5.2371
2329.5 | 1.8309 | 2333.1667 | 12.2749 |  | 2335 | 12.9073 | 2337 | 0.65969 | 2329.5 | 0.65969

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 8 |  |  | 2006-07-07 | 12:58
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 | [10 empty] | All Including Drain Wire |  | Excluding Drain Wire |  | Conductor to Drain Only
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums | Penlight Time | Minimums (Cond-Cond) | Penlight Time | Minimum (Cond-Drain)
-109 | 250337.9994 | -106 | 249537.9994 | -103.5 | 248437.9994 | -100.5 | 250137.9994 | -97.5 | 249037.9994 | -94.5 | 249837.9994 | -109 | 248437.9994 | -109 | 249537.9994 | -109 | 248437.9994
-92 | 250337.9994 | -89.5 | 249537.9994 | -86.5 | 248437.9994 | -83.5 | 250137.9994 | -81 | 249037.9994 | -78 | 249837.9994 | -92 | 248437.9994 | -92 | 249537.9994 | -92 | 248437.9994
-75.5 | 250337.9994 | -72.5 | 249537.9994 | -69.5 | 248437.9994 | -67 | 250137.9994 | -64.5 | 249037.9994 | -61.5 | 249837.9994 | -75.5 | 248437.9994 | -75.5 | 249537.9994 | -75.5 | 248437.9994
-58.5 | 250337.9994 | -55.5 | 249537.9994 | -53 | 248437.9994 | -50 | 250137.9994 | -47.5 | 249037.9994 | -44.5 | 249837.9994 | -58.5 | 248437.9994 | -58.5 | 249537.9994 | -58.5 | 248437.9994
-41.5 | 250337.9994 | -39 | 249537.9994 | -36 | 248437.9994 | -33.5 | 250137.9994 | -30.5 | 249037.9994 | -27.5 | 249837.9994 | -41.5 | 248437.9994 | -41.5 | 249537.9994 | -41.5 | 248437.9994
-25 | 250337.9994 | -22 | 249537.9994 | -19.5 | 248437.9994 | -16.5 | 250137.9994 | -13.5 | 249037.9994 | -11 | 249837.9994 | -25 | 248437.9994 | -25 | 249537.9994 | -25 | 248437.9994
-8 | 250337.9994 | -5.5 | 249537.9994 | -2.5 | 248437.9994 | -6.8918e-07 | 250137.9994 | 3 | 249037.9994 | 6 | 249837.9994 | -8 | 248437.9994 | -8 | 249537.9994 | -8 | 248437.9994
8.5 | 250337.9994 | 11.5 | 249537.9994 | 14 | 248437.9994 | 17 | 250137.9994 | 20 | 249037.9994 | 22.5 | 249837.9994 | 8.5 | 248437.9994 | 8.5 | 249537.9994 | 8.5 | 248437.9994
25.5 | 250337.9994 | 28.5 | 249537.9994 | 31 | 248437.9994 | 34 | 250137.9994 | 36.5 | 249037.9994 | 39.5 | 249837.9994 | 25.5 | 248437.9994 | 25.5 | 249537.9994 | 25.5 | 248437.9994
42 | 250337.9994 | 45 | 249537.9994 | 48 | 248437.9994 | 50.5 | 125018.9988 | 53.5 | 124468.9988 | 56.5 | 249837.9994 | 42 | 124468.9988 | 42 | 125018.9988 | 42 | 124468.9988
59 | 250337.9994 | 61.5 | 249537.9994 | 64.5 | 248437.9994 | 67.5 | 250137.9994 | 70.5 | 249037.9994 | 73 | 249837.9994 | 59 | 248437.9994 | 59 | 249537.9994 | 59 | 248437.9994
75.5 | 250337.9994 | 78.5 | 249537.9994 | 81.5 | 248437.9994 | 84.5 | 250137.9994 | 87 | 249037.9994 | 90 | 249837.9994 | 75.5 | 248437.9994 | 75.5 | 249537.9994 | 75.5 | 248437.9994
92.5 | 250337.9994 | 95.5 | 249537.9994 | 98 | 248437.9994 | 101 | 250137.9994 | 103.5 | 249037.9994 | 106.5 | 249837.9994 | 92.5 | 248437.9994 | 92.5 | 249537.9994 | 92.5 | 248437.9994
109.5 | 250337.9994 | 112.5 | 249537.9994 | 115 | 248437.9994 | 118 | 249938.0799 | 120.5 | 249037.9994 | 123.5 | 249837.9994 | 109.5 | 248437.9994 | 109.5 | 249537.9994 | 109.5 | 248437.9994
126 | 250337.9994 | 129 | 249537.9994 | 132 | 248437.9994 | 134.5 | 250137.9994 | 137.5 | 249037.9994 | 140 | 249837.9994 | 126 | 248437.9994 | 126 | 249537.9994 | 126 | 248437.9994
143 | 250337.9994 | 146 | 249537.9994 | 148.5 | 248437.9994 | 151.5 | 250137.9994 | 154.5 | 249037.9994 | 157 | 249837.9994 | 143 | 248437.9994 | 143 | 249537.9994 | 143 | 248437.9994
159.5 | 250337.9994 | 162.5 | 249537.9994 | 165.5 | 248437.9994 | 168.5 | 250137.9994 | 171 | 249037.9994 | 173.5 | 249837.9994 | 159.5 | 248437.9994 | 159.5 | 249537.9994 | 159.5 | 248437.9994
176.5 | 250337.9994 | 179.5 | 249537.9994 | 182.5 | 248437.9994 | 185 | 250137.9994 | 187.5 | 249037.9994 | 190.5 | 249837.9994 | 176.5 | 248437.9994 | 176.5 | 249537.9994 | 176.5 | 248437.9994
193.5 | 250337.9994 | 196 | 249537.9994 | 199 | 248437.9994 | 202 | 250137.9994 | 204.5 | 249037.9994 | 207.5 | 249837.9994 | 193.5 | 248437.9994 | 193.5 | 249537.9994 | 193.5 | 248437.9994
210.5 | 250337.9994 | 213 | 249537.9994 | 216 | 248437.9994 | 218.5 | 250137.9994 | 221.5 | 249037.9994 | 224 | 249837.9994 | 210.5 | 248437.9994 | 210.5 | 249537.9994 | 210.5 | 248437.9994
227 | 250337.9994 | 229.5 | 249537.9994 | 232.5 | 248437.9994 | 235.5 | 250137.9994 | 238.5 | 249037.9994 | 241 | 249837.9994 | 227 | 248437.9994 | 227 | 249537.9994 | 227 | 248437.9994
243.5 | 250337.9994 | 246.5 | 249537.9994 | 249.5 | 248437.9994 | 252.5 | 250137.9994 | 255 | 249037.9994 | 257.5 | 249837.9994 | 243.5 | 248437.9994 | 243.5 | 249537.9994 | 243.5 | 248437.9994
260.5 | 250337.9994 | 263.5 | 249537.9994 | 266 | 248437.9994 | 269 | 250137.9994 | 272 | 249037.9994 | 274.5 | 249837.9994 | 260.5 | 248437.9994 | 260.5 | 249537.9994 | 260.5 | 248437.9994
277.5 | 250337.9994 | 280 | 249537.9994 | 283 | 248437.9994 | 285.5 | 250137.9994 | 288.5 | 249037.9994 | 291.5 | 249837.9994 | 277.5 | 248437.9994 | 277.5 | 249537.9994 | 277.5 | 248437.9994
294.5 | 250337.9994 | 297 | 249537.9994 | 299.5 | 248437.9994 | 302.5 | 250137.9994 | 305.5 | 249037.9994 | 308.5 | 249837.9994 | 294.5 | 248437.9994 | 294.5 | 249537.9994 | 294.5 | 248437.9994
311 | 250337.9994 | 313.5 | 249537.9994 | 316.5 | 248437.9994 | 319.5 | 250137.9994 | 322 | 249037.9994 | 325 | 249837.9994 | 311 | 248437.9994 | 311 | 249537.9994 | 311 | 248437.9994
327.5 | 250337.9994 | 330.5 | 249537.9994 | 333.5 | 248437.9994 | 336.5 | 250137.9994 | 339 | 249037.9994 | 341.5 | 249837.9994 | 327.5 | 248437.9994 | 327.5 | 249537.9994 | 327.5 | 248437.9994
344.5 | 250337.9994 | 347.5 | 249537.9994 | 350 | 248437.9994 | 353 | 250137.9994 | 355.5 | 249037.9994 | 358.5 | 249837.9994 | 344.5 | 248437.9994 | 344.5 | 249537.9994 | 344.5 | 248437.9994
361.5 | 250337.9994 | 364 | 249537.9994 | 367 | 248437.9994 | 369.5 | 250137.9994 | 372.5 | 249037.9994 | 375.5 | 249837.9994 | 361.5 | 248437.9994 | 361.5 | 249537.9994 | 361.5 | 248437.9994
378.5 | 250337.9994 | 381 | 249537.9994 | 383 | 248437.9994 | 386.5 | 250137.9994 | 389.5 | 124468.9988 | 392 | 249837.9994 | 378.5 | 124468.9988 | 378.5 | 249537.9994 | 378.5 | 124468.9988
395 | 250337.9994 | 397.5 | 249537.9994 | 400.5 | 248437.9994 | 403.5 | 250137.9994 | 406 | 249037.9994 | 409 | 249837.9994 | 395 | 248437.9994 | 395 | 249537.9994 | 395 | 248437.9994
412 | 250337.9994 | 414.5 | 249537.9994 | 417.5 | 248437.9994 | 420 | 249938.0799 | 423 | 249037.9994 | 425.5 | 249837.9994 | 412 | 248437.9994 | 412 | 249537.9994 | 412 | 248437.9994
428.5 | 250337.9994 | 431.5 | 249537.9994 | 434.5 | 248437.9994 | 437 | 250137.9994 | 439.5 | 249037.9994 | 442.5 | 249837.9994 | 428.5 | 248437.9994 | 428.5 | 249537.9994 | 428.5 | 248437.9994
445.5 | 250337.9994 | 448 | 249537.9994 | 451 | 248437.9994 | 453.5 | 250137.9994 | 456.5 | 249037.9994 | 459.5 | 249837.9994 | 445.5 | 248437.9994 | 445.5 | 249537.9994 | 445.5 | 248437.9994
462 | 250337.9994 | 465 | 249537.9994 | 467.5 | 124168.9988 | 470.5 | 250137.9994 | 473.5 | 249037.9994 | 476.5 | 249837.9994 | 462 | 124168.9988 | 462 | 249537.9994 | 462 | 124168.9988
479 | 250337.9994 | 481.5 | 249537.9994 | 484.5 | 248437.9994 | 487.5 | 250137.9994 | 490 | 249037.9994 | 493 | 249837.9994 | 479 | 248437.9994 | 479 | 249537.9994 | 479 | 248437.9994
495.5 | 250337.9994 | 498.5 | 249537.9994 | 501.5 | 248437.9994 | 504 | 250137.9994 | 507 | 249037.9994 | 509.5 | 249837.9994 | 495.5 | 248437.9994 | 495.5 | 249537.9994 | 495.5 | 248437.9994
512.5 | 250337.9994 | 515.5 | 249537.9994 | 518 | 248437.9994 | 521 | 250137.9994 | 523.5 | 249037.9994 | 526.5 | 249837.9994 | 512.5 | 248437.9994 | 512.5 | 249537.9994 | 512.5 | 248437.9994
529.5 | 250337.9994 | 532 | 249537.9994 | 535 | 248437.9994 | 537.5 | 250137.9994 | 540.5 | 248838.0803 | 543.5 | 249837.9994 | 529.5 | 248437.9994 | 529.5 | 249537.9994 | 529.5 | 248437.9994
546 | 250337.9994 | 549 | 249537.9994 | 552 | 248437.9994 | 554.5 | 250137.9994 | 557.5 | 249037.9994 | 560 | 249837.9994 | 546 | 248437.9994 | 546 | 249537.9994 | 546 | 248437.9994
563 | 250337.9994 | 565.5 | 249537.9994 | 568.5 | 248437.9994 | 571.5 | 250137.9994 | 574 | 249037.9994 | 577 | 249837.9994 | 563 | 248437.9994 | 563 | 249537.9994 | 563 | 248437.9994
579.5 | 250337.9994 | 582.5 | 249537.9994 | 585.5 | 248437.9994 | 588 | 250137.9994 | 591 | 249037.9994 | 593.5 | 249837.9994 | 579.5 | 248437.9994 | 579.5 | 249537.9994 | 579.5 | 248437.9994
596.5 | 250337.9994 | 599.5 | 249537.9994 | 602 | 248437.9994 | 605 | 250137.9994 | 607.5 | 249037.9994 | 610.5 | 249837.9994 | 596.5 | 248437.9994 | 596.5 | 249537.9994 | 596.5 | 248437.9994
613.5 | 250337.9994 | 616.5 | 249537.9994 | 619 | 248437.9994 | 621.5 | 250137.9994 | 624.5 | 249037.9994 | 627.5 | 249837.9994 | 613.5 | 248437.9994 | 613.5 | 249537.9994 | 613.5 | 248437.9994
630.5 | 250337.9994 | 633 | 249537.9994 | 635.5 | 248437.9994 | 638.5 | 250137.9994 | 641.5 | 249037.9994 | 644 | 249837.9994 | 630.5 | 248437.9994 | 630.5 | 249537.9994 | 630.5 | 248437.9994
647 | 250337.9994 | 649.5 | 249537.9994 | 652.5 | 248437.9994 | 655.5 | 250137.9994 | 658 | 249037.9994 | 661 | 249837.9994 | 647 | 248437.9994 | 647 | 249537.9994 | 647 | 248437.9994
663.5 | 250337.9994 | 666.5 | 249537.9994 | 669.5 | 248437.9994 | 672 | 250137.9994 | 675 | 249037.9994 | 677.5 | 249837.9994 | 663.5 | 248437.9994 | 663.5 | 249537.9994 | 663.5 | 248437.9994
680.5 | 250337.9994 | 683.5 | 249537.9994 | 686 | 248437.9994 | 689 | 250137.9994 | 691.5 | 249037.9994 | 694.5 | 249837.9994 | 680.5 | 248437.9994 | 680.5 | 249537.9994 | 680.5 | 248437.9994
697.5 | 250337.9994 | 700 | 249537.9994 | 703 | 248437.9994 | 705.5 | 250137.9994 | 708.5 | 249037.9994 | 711.5 | 249837.9994 | 697.5 | 248437.9994 | 697.5 | 249537.9994 | 697.5 | 248437.9994
714 | 250337.9994 | 717 | 249537.9994 | 719.5 | 248437.9994 | 722.5 | 250137.9994 | 725.5 | 249037.9994 | 728 | 249837.9994 | 714 | 248437.9994 | 714 | 249537.9994 | 714 | 248437.9994
731 | 250337.9994 | 733.5 | 249537.9994 | 736.5 | 248437.9994 | 739.5 | 250137.9994 | 742 | 249037.9994 | 745 | 249837.9994 | 731 | 248437.9994 | 731 | 249537.9994 | 731 | 248437.9994
747.5 | 250337.9994 | 750.5 | 249537.9994 | 753.5 | 248437.9994 | 756 | 250137.9994 | 759 | 249037.9994 | 761.5 | 249837.9994 | 747.5 | 248437.9994 | 747.5 | 249537.9994 | 747.5 | 248437.9994
764.5 | 250337.9994 | 767.5 | 249537.9994 | 770 | 248437.9994 | 773 | 250137.9994 | 775.5 | 249037.9994 | 778.5 | 249837.9994 | 764.5 | 248437.9994 | 764.5 | 249537.9994 | 764.5 | 248437.9994
781.5 | 250337.9994 | 784 | 249537.9994 | 787 | 248437.9994 | 789.5 | 250137.9994 | 792.5 | 249037.9994 | 795.5 | 124868.9988 | 781.5 | 124868.9988 | 781.5 | 249537.9994 | 781.5 | 124868.9988
798 | 250337.9994 | 801 | 249537.9994 | 803.5 | 248437.9994 | 806.5 | 250137.9994 | 809.5 | 249037.9994 | 812 | 249837.9994 | 798 | 248437.9994 | 798 | 249537.9994 | 798 | 248437.9994
815 | 250337.9994 | 817.5 | 249537.9994 | 820.5 | 248437.9994 | 823.5 | 250137.9994 | 826 | 249037.9994 | 829 | 249837.9994 | 815 | 248437.9994 | 815 | 249537.9994 | 815 | 248437.9994
831.5 | 250337.9994 | 834.5 | 249537.9994 | 837.5 | 248437.9994 | 840 | 250137.9994 | 843 | 249037.9994 | 845.5 | 249837.9994 | 831.5 | 248437.9994 | 831.5 | 249537.9994 | 831.5 | 248437.9994
848.5 | 250337.9994 | 851.5 | 249537.9994 | 854 | 248437.9994 | 857 | 250137.9994 | 859.5 | 249037.9994 | 862.5 | 249837.9994 | 848.5 | 248437.9994 | 848.5 | 249537.9994 | 848.5 | 248437.9994
865.5 | 250337.9994 | 868 | 249537.9994 | 871 | 248437.9994 | 873.5 | 250137.9994 | 876.5 | 249037.9994 | 879.5 | 249837.9994 | 865.5 | 248437.9994 | 865.5 | 249537.9994 | 865.5 | 248437.9994
882 | 250337.9994 | 885 | 249537.9994 | 887.5 | 248437.9994 | 890.5 | 250137.9994 | 893.5 | 249037.9994 | 896 | 249837.9994 | 882 | 248437.9994 | 882 | 249537.9994 | 882 | 248437.9994
899 | 250337.9994 | 901.5 | 249537.9994 | 904.5 | 248437.9994 | 907.5 | 250137.9994 | 910 | 249037.9994 | 913 | 249837.9994 | 899 | 248437.9994 | 899 | 249537.9994 | 899 | 248437.9994
915.5 | 250337.9994 | 918.5 | 249537.9994 | 921.5 | 248437.9994 | 924 | 250137.9994 | 927 | 249037.9994 | 929.5 | 249837.9994 | 915.5 | 248437.9994 | 915.5 | 249537.9994 | 915.5 | 248437.9994
932.5 | 250337.9994 | 935.5 | 249537.9994 | 938 | 248437.9994 | 941 | 250137.9994 | 943.5 | 249037.9994 | 946.5 | 249837.9994 | 932.5 | 248437.9994 | 932.5 | 249537.9994 | 932.5 | 248437.9994
949.5 | 250337.9994 | 952 | 249537.9994 | 955 | 248437.9994 | 957.5 | 250137.9994 | 960.5 | 249037.9994 | 963.5 | 249837.9994 | 949.5 | 248437.9994 | 949.5 | 249537.9994 | 949.5 | 248437.9994
966 | 250337.9994 | 969 | 249338.0801 | 971.5 | 248437.9994 | 974.5 | 250137.9994 | 977.5 | 249037.9994 | 980 | 249837.9994 | 966 | 248437.9994 | 966 | 249338.0801 | 966 | 248437.9994
983 | 250337.9994 | 985.5 | 249537.9994 | 988.5 | 248437.9994 | 991.5 | 250137.9994 | 994 | 249037.9994 | 997 | 249837.9994 | 983 | 248437.9994 | 983 | 249537.9994 | 983 | 248437.9994
999.5 | 250337.9994 | 1002.5 | 249537.9994 | 1005.5 | 248437.9994 | 1008 | 250137.9994 | 1011 | 249037.9994 | 1013.5 | 249837.9994 | 999.5 | 248437.9994 | 999.5 | 249537.9994 | 999.5 | 248437.9994
1016.5 | 250337.9994 | 1019.5 | 249537.9994 | 1022 | 248437.9994 | 1025 | 250137.9994 | 1027.5 | 249037.9994 | 1030.5 | 249837.9994 | 1016.5 | 248437.9994 | 1016.5 | 249537.9994 | 1016.5 | 248437.9994
1033.5 | 250337.9994 | 1036 | 249537.9994 | 1039 | 248437.9994 | 1041.5 | 250137.9994 | 1044.5 | 249037.9994 | 1047.5 | 249837.9994 | 1033.5 | 248437.9994 | 1033.5 | 249537.9994 | 1033.5 | 248437.9994
1050 | 250337.9994 | 1053 | 249537.9994 | 1055.5 | 248437.9994 | 1058.5 | 250137.9994 | 1061.5 | 249037.9994 | 1064 | 249837.9994 | 1050 | 248437.9994 | 1050 | 249537.9994 | 1050 | 248437.9994
1067 | 250337.9994 | 1069.5 | 249537.9994 | 1072.5 | 248437.9994 | 1075.5 | 250137.9994 | 1078 | 249037.9994 | 1081 | 249638.08 | 1067 | 248437.9994 | 1067 | 249537.9994 | 1067 | 248437.9994
1083.5 | 250337.9994 | 1086.5 | 249537.9994 | 1089.5 | 248437.9994 | 1092 | 250137.9994 | 1095 | 249037.9994 | 1097.5 | 249837.9994 | 1083.5 | 248437.9994 | 1083.5 | 249537.9994 | 1083.5 | 248437.9994
1100.5 | 250337.9994 | 1103.5 | 249537.9994 | 1106 | 248437.9994 | 1109 | 250137.9994 | 1111.5 | 249037.9994 | 1114.5 | 249837.9994 | 1100.5 | 248437.9994 | 1100.5 | 249537.9994 | 1100.5 | 248437.9994
1117.5 | 250337.9994 | 1120 | 249537.9994 | 1123 | 248437.9994 | 1125.5 | 250137.9994 | 1128.5 | 249037.9994 | 1131.5 | 249837.9994 | 1117.5 | 248437.9994 | 1117.5 | 249537.9994 | 1117.5 | 248437.9994
1134 | 250337.9994 | 1137 | 249537.9994 | 1139.5 | 248437.9994 | 1142.5 | 250137.9994 | 1145.5 | 249037.9994 | 1148 | 249837.9994 | 1134 | 248437.9994 | 1134 | 249537.9994 | 1134 | 248437.9994
1151 | 250337.9994 | 1153.5 | 249537.9994 | 1156.5 | 248437.9994 | 1159.5 | 250137.9994 | 1162 | 249037.9994 | 1165 | 249837.9994 | 1151 | 248437.9994 | 1151 | 249537.9994 | 1151 | 248437.9994
1167.5 | 250337.9994 | 1170.5 | 249537.9994 | 1173.5 | 248437.9994 | 1176 | 250137.9994 | 1178.5 | 249037.9994 | 1181.5 | 249837.9994 | 1167.5 | 248437.9994 | 1167.5 | 249537.9994 | 1167.5 | 248437.9994
1184.5 | 250337.9994 | 1187.5 | 249537.9994 | 1190 | 248437.9994 | 1193 | 250137.9994 | 1195.5 | 249037.9994 | 1198.5 | 249837.9994 | 1184.5 | 248437.9994 | 1184.5 | 249537.9994 | 1184.5 | 248437.9994
1201.5 | 250337.9994 | 1204 | 249537.9994 | 1207 | 248437.9994 | 1209.5 | 250137.9994 | 1212.5 | 249037.9994 | 1215.5 | 249837.9994 | 1201.5 | 248437.9994 | 1201.5 | 249537.9994 | 1201.5 | 248437.9994
1218 | 250337.9994 | 1221 | 249537.9994 | 1223.5 | 248437.9994 | 1226.5 | 250137.9994 | 1229.5 | 249037.9994 | 1232 | 249837.9994 | 1218 | 248437.9994 | 1218 | 249537.9994 | 1218 | 248437.9994
1235 | 250337.9994 | 1237.5 | 249537.9994 | 1240.5 | 248437.9994 | 1243.5 | 250137.9994 | 1246 | 249037.9994 | 1249 | 62384.4976 | 1235 | 62384.4976 | 1235 | 249537.9994 | 1235 | 62384.4976
1251.5 | 35676.8529 | 1254.5 | 83112.6648 | 1257.5 | 124168.9988 | 1260 | 35648.2814 | 1262.5 | 62184.4976 | 1265.5 | 31142.2451 | 1251.5 | 31142.2451 | 1251.5 | 35648.2814 | 1251.5 | 31142.2451
1268.5 | 27726.4389 | 1271.5 | 62309.4976 | 1274 | 82745.9982 | 1277 | 27704.2167 | 1279.5 | 62184.4976 | 1282.5 | 27670.8834 | 1268.5 | 27670.8834 | 1268.5 | 27704.2167 | 1268.5 | 27670.8834
1286 | 31204.7451 | 1288 | 41506.3297 | 1290.5 | 62034.4976 | 1293.5 | 31179.7451 | 1296.5 | 62184.4976 | 1299.5 | 60793.7874 | 1286 | 31179.7451 | 1286 | 31179.7451 | 1286 | 60793.7874
1302 | 31204.7451 | 1305 | 41506.3297 | 1307.5 | 82745.9982 | 1310.5 | 27704.2167 | 1313.5 | 62184.4976 | 1316 | 27670.8834 | 1302 | 27670.8834 | 1302 | 27704.2167 | 1302 | 27670.8834
1319 | 27726.4389 | 1321.5 | 41506.3297 | 1324.5 | 82745.9982 | 1327 | 27704.2167 | 1330 | 49727.5969 | 1333 | 27670.8834 | 1319 | 27670.8834 | 1319 | 27704.2167 | 1319 | 27670.8834
1335.5 | 27726.4389 | 1338.5 | 31104.7451 | 1341.5 | 49607.5969 | 1344 | 27704.2167 | 1346.5 | 41422.9963 | 1349.5 | 27670.8834 | 1335.5 | 27670.8834 | 1335.5 | 27704.2167 | 1335.5 | 27670.8834
1352.5 | 27726.4389 | 1355.5 | 31104.7451 | 1358 | 41322.9963 | 1361 | 27704.2167 | 1363.5 | 41422.9963 | 1366.5 | 27670.8834 | 1352.5 | 27670.8834 | 1352.5 | 27704.2167 | 1352.5 | 27670.8834
1369.5 | 27726.4389 | 1372 | 31104.7451 | 1375 | 41322.9963 | 1377.5 | 27704.2167 | 1380.5 | 35491.1386 | 1383 | 27670.8834 | 1369.5 | 27670.8834 | 1369.5 | 27704.2167 | 1369.5 | 27670.8834
1386 | 27726.4389 | 1389 | 35562.5672 | 1391.5 | 41322.9963 | 1394.5 | 27704.2167 | 1397.5 | 41422.9963 | 1400 | 27670.8834 | 1386 | 27670.8834 | 1386 | 27704.2167 | 1386 | 27670.8834
1403 | 27726.4389 | 1405.5 | 31104.7451 | 1408.5 | 41322.9963 | 1411 | 24923.7939 | 1414 | 35491.1386 | 1417 | 27670.8834 | 1403 | 24923.7939 | 1403 | 24923.7939 | 1403 | 27670.8834
1419.5 | 27726.4389 | 1422.5 | 31104.7451 | 1425 | 41322.9963 | 1428 | 27704.2167 | 1431 | 35491.1386 | 1433.5 | 27670.8834 | 1419.5 | 27670.8834 | 1419.5 | 27704.2167 | 1419.5 | 27670.8834
1436.5 | 27726.4389 | 1439.5 | 35562.5672 | 1442 | 63315.9165 | 1444.5 | 27704.2167 | 1447.5 | 35491.1386 | 1450.5 | 27670.8834 | 1436.5 | 27670.8834 | 1436.5 | 27704.2167 | 1436.5 | 27670.8834
1453.5 | 27726.4389 | 1456 | 31104.7451 | 1458.5 | 41322.9963 | 1461.5 | 27704.2167 | 1464.5 | 41422.9963 | 1467.5 | 27670.8834 | 1453.5 | 27670.8834 | 1453.5 | 27704.2167 | 1453.5 | 27670.8834
1470 | 27726.4389 | 1472.5 | 31104.7451 | 1475.5 | 41322.9963 | 1478.5 | 31179.7451 | 1481.5 | 41422.9963 | 1484 | 31142.2451 | 1470 | 27726.4389 | 1470 | 27726.4389 | 1470 | 31142.2451
1486.5 | 27726.4389 | 1489.5 | 31104.7451 | 1492.5 | 41322.9963 | 1495.5 | 27704.2167 | 1498 | 35491.1386 | 1501 | 24893.7939 | 1486.5 | 24893.7939 | 1486.5 | 27704.2167 | 1486.5 | 24893.7939
1503.5 | 27726.4389 | 1506.5 | 35562.5672 | 1509 | 49607.5969 | 1512 | 27704.2167 | 1515 | 35491.1386 | 1517.5 | 27670.8834 | 1503.5 | 27670.8834 | 1503.5 | 27704.2167 | 1503.5 | 27670.8834
1520.5 | 27726.4389 | 1523 | 31104.7451 | 1526 | 49607.5969 | 1529 | 27704.2167 | 1531.5 | 35491.1386 | 1534.5 | 27670.8834 | 1520.5 | 27670.8834 | 1520.5 | 27704.2167 | 1520.5 | 27670.8834
1537 | 27726.4389 | 1540 | 35562.5672 | 1543 | 49607.5969 | 1545.5 | 27704.2167 | 1548.5 | 41422.9963 | 1551 | 27670.8834 | 1537 | 27670.8834 | 1537 | 27704.2167 | 1537 | 27670.8834
1554 | 27726.4389 | 1557 | 31104.7451 | 1559.5 | 49607.5969 | 1562.5 | 27704.2167 | 1565 | 41422.9963 | 1568 | 27670.8834 | 1554 | 27670.8834 | 1554 | 27704.2167 | 1554 | 27670.8834
1570.5 | 27726.4389 | 1573.5 | 35562.5672 | 1576.5 | 49607.5969 | 1579.5 | 27704.2167 | 1582 | 35491.1386 | 1585 | 27670.8834 | 1570.5 | 27670.8834 | 1570.5 | 27704.2167 | 1570.5 | 27670.8834
1587.5 | 24943.7939 | 1590.5 | 35562.5672 | 1593 | 41322.9963 | 1596 | 27704.2167 | 1598.5 | 41422.9963 | 1601.5 | 27670.8834 | 1587.5 | 24943.7939 | 1587.5 | 24943.7939 | 1587.5 | 27670.8834
1604.5 | 27726.4389 | 1607.5 | 31104.7451 | 1610 | 41322.9963 | 1612.5 | 27704.2167 | 1615.5 | 41422.9963 | 1618.5 | 27670.8834 | 1604.5 | 27670.8834 | 1604.5 | 27704.2167 | 1604.5 | 27670.8834
1621 | 27726.4389 | 1624 | 35562.5672 | 1627 | 41322.9963 | 1629.5 | 27704.2167 | 1632.5 | 41422.9963 | 1635 | 27670.8834 | 1621 | 27670.8834 | 1621 | 27704.2167 | 1621 | 27670.8834
1638 | 27726.4389 | 1641 | 35562.5672 | 1643.5 | 41322.9963 | 1646.5 | 27704.2167 | 1649.5 | 41422.9963 | 1652 | 27670.8834 | 1638 | 27670.8834 | 1638 | 27704.2167 | 1638 | 27670.8834
1654.5 | 9.7322 | 1657.5 | 6.9432 | 1660.5 | 314.1658 | 1663.5 | 31179.7451 | 1666 | 27581.9945 | 1668.5 | 70.3763 | 1654.5 | 6.9432 | 1654.5 | 6.9432 | 1654.5 | 70.3763
1671.5 | 24.3149 | 1674.5 | 327.2168 | 1677.5 | 40.474 | 1680 | 27704.2167 | 1682.5 | 27581.9945 | 1685.5 | 69.2018 | 1671.5 | 24.3149 | 1671.5 | 24.3149 | 1671.5 | 40.474
1688.5 | 4.0427 | 1691 | 312.5209 | 1694 | 107.6504 | 1696.5 | 27704.2167 | 1699.5 | 27581.9945 | 1702.5 | 143.58 | 1688.5 | 4.0427 | 1688.5 | 4.0427 | 1688.5 | 107.6504
1705.5 | 10.8917 | 1708 | 335.5996 | 1710.5 | 968.2866 | 1713.5 | 27704.2167 | 1716.5 | 31042.2451 | 1719 | 7639.4652 | 1705.5 | 10.8917 | 1705.5 | 10.8917 | 1705.5 | 968.2866
1722 | 8.9885 | 1724.5 | 10943.2933 | 1727.5 | 5654.4176 | 1730.5 | 27704.2167 | 1733 | 27581.9945 | 1736 | 6231.6664 | 1722 | 8.9885 | 1722 | 8.9885 | 1722 | 5654.4176
1739 | 23.119 | 1741.5 | 849.5045 | 1744.5 | 9018.4899 | 1747 | 31179.7451 | 1750 | 31042.2451 | 1752.5 | 7477.1593 | 1739 | 23.119 | 1739 | 23.119 | 1739 | 7477.1593
1755.5 | 17.8022 | 1758.5 | 1354.1509 | 1761 | 11812.1448 | 1764 | 31179.7451 | 1766.5 | 31042.2451 | 1769.5 | 600.5273 | 1755.5 | 17.8022 | 1755.5 | 17.8022 | 1755.5 | 600.5273
1772.5 | 1.1916 | 1775.5 | 1114.7303 | 1778 | 6950.9678 | 1780.5 | 24923.7939 | 1783.5 | 84.9666 | 1786.5 | 5397.4611 | 1772.5 | 1.1916 | 1772.5 | 1.1916 | 1772.5 | 84.9666
1789 | 8.0119 | 1792 | 1401.7451 | 1794.5 | 6096.0796 | 1797.5 | 25.5618 | 1800.5 | 22.4115 | 1803 | 10583.4961 | 1789 | 8.0119 | 1789 | 8.0119 | 1789 | 22.4115
1806 | 10.4857 | 1808.5 | 275.5432 | 1811.5 | 1704.5379 | 1814.5 | 35.8512 | 1817 | 22.5977 | 1820 | 812.2456 | 1806 | 10.4857 | 1806 | 10.4857 | 1806 | 22.5977
1822.5 | 14.246 | 1825.5 | 23.0958 | 1828.5 | 12710.4766 | 1831 | 44.8644 | 1834 | 63.9604 | 1836.5 | 515.8169 | 1822.5 | 14.246 | 1822.5 | 14.246 | 1822.5 | 63.9604
1839.5 | 25.0819 | 1842.5 | 13.1288 | 1845.5 | 2189.8735 | 1848 | 48.7333 | 1850.5 | 46.5631 | 1853.5 | 116.3552 | 1839.5 | 13.1288 | 1839.5 | 13.1288 | 1839.5 | 46.5631
1856.5 | 33.7279 | 1859 | 222.2208 | 1862 | 160.6026 | 1864.5 | 25.4323 | 1867.5 | 11.2798 | 1870.5 | 219.5362 | 1856.5 | 11.2798 | 1856.5 | 25.4323 | 1856.5 | 11.2798
1873 | 17.5737 | 1876 | 408.9862 | 1878.5 | 115.7008 | 1881.5 | 0.8117 | 1884.5 | 21.8562 | 1887 | 25.4747 | 1873 | 0.8117 | 1873 | 0.8117 | 1873 | 21.8562
1890 | 15.1155 | 1892.5 | 19.3932 | 1895.5 | 6409.4386 | 1898.5 | 5704.7924 | 1901 | 14.6747 | 1904 | 8546.3349 | 1890 | 14.6747 | 1890 | 15.1155 | 1890 | 14.6747
1906.5 | 21.8841 | 1909.5 | 24.1042 | 1912.5 | 16.3896 | 1915 | 29.8486 | 1918 | 102.6702 | 1920.5 | 1759.8502 | 1906.5 | 16.3896 | 1906.5 | 21.8841 | 1906.5 | 16.3896
1923.5 | 19.0162 | 1926.5 | 10.9407 | 1929 | 650.3876 | 1932 | 30.3348 | 1934.5 | 12.2672 | 1937.5 | 5261.7355 | 1923.5 | 10.9407 | 1923.5 | 10.9407 | 1923.5 | 12.2672
1940.5 | 14511.4178 | 1943 | 24.4226 | 1946 | 4860.4923 | 1948.5 | 23.8349 | 1951.5 | 813.648 | 1954.5 | 656.4406 | 1940.5 | 23.8349 | 1940.5 | 23.8349 | 1940.5 | 656.4406
1957 | 20.0762 | 1960 | 1496.5856 | 1962.5 | 14358.2818 | 1965.5 | 6554.9087 | 1968.5 | 31.231 | 1971 | 11361.7827 | 1957 | 20.0762 | 1957 | 20.0762 | 1957 | 31.231
1974 | 306.2843 | 1976.5 | 1610.6364 | 1979.5 | 677.5255 | 1982.5 | 3564.4077 | 1985 | 4414.8811 | 1988 | 4019.4966 | 1974 | 306.2843 | 1974 | 306.2843 | 1974 | 677.5255
1990.5 | 294.3106 | 1993.5 | 13215.4313 | 1996.5 | 476.5164 | 1999 | 55.548 | 2002 | 9201.1473 | 2004.5 | 1452.843 | 1990.5 | 55.548 | 1990.5 | 55.548 | 1990.5 | 476.5164
2007.5 | 5501.1389 | 2010.5 | 397.9347 | 2013 | 1803.7717 | 2016 | 8916.0128 | 2018.5 | 875.8871 | 2021.5 | 2833.7589 | 2007.5 | 397.9347 | 2007.5 | 397.9347 | 2007.5 | 875.8871
2024.5 | 4885.8393 | 2027 | 190.4393 | 2030 | 3094.2001 | 2032.5 | 2167.1565 | 2035.5 | 3484.5848 | 2038.5 | 2324.9178 | 2024.5 | 190.4393 | 2024.5 | 190.4393 | 2024.5 | 2324.9178
2041 | 415.6008 | 2044 | 373.4061 | 2046.5 | 216.947 | 2049.5 | 543.3102 | 2052.5 | 314.0459 | 2055 | 274.059 | 2041 | 216.947 | 2041 | 373.4061 | 2041 | 216.947
2058 | 652.5078 | 2060.5 | 589.517 | 2063.5 | 1205.6331 | 2066.5 | 880.1216 | 2069 | 676.4734 | 2072 | 52.9965 | 2058 | 52.9965 | 2058 | 589.517 | 2058 | 52.9965
2074.5 | 710.8764 | 2077.5 | 118.88 | 2080.5 | 2044.8443 | 2083 | 724.5352 | 2086 | 68.0895 | 2088.5 | 2023.02 | 2074.5 | 68.0895 | 2074.5 | 118.88 | 2074.5 | 68.0895
2091.5 | 989.1252 | 2094.5 | 98.8674 | 2097 | 168.6046 | 2100 | 110.2044 | 2102.5 | 127.3955 | 2105.5 | 92.9209 | 2091.5 | 92.9209 | 2091.5 | 98.8674 | 2091.5 | 92.9209
2108.5 | 219.5522 | 2111 | 253.8326 | 2114 | 1136.0929 | 2116.5 | 203.8149 | 2119.5 | 288.4812 | 2122.5 | 610.5978 | 2108.5 | 203.8149 | 2108.5 | 203.8149 | 2108.5 | 288.4812
2125 | 202.1761 | 2128 | 72.8719 | 2130.5 | 521.6019 | 2133.5 | 233.2524 | 2136.5 | 114.7408 | 2139 | 55.8705 | 2125 | 55.8705 | 2125 | 72.8719 | 2125 | 55.8705
2142 | 712.1844 | 2144.5 | 474.4058 | 2147.5 | 117.4668 | 2150.5 | 282.3395 | 2153 | 145.7368 | 2156 | 134.6876 | 2142 | 117.4668 | 2142 | 282.3395 | 2142 | 117.4668
2158.5 | 369.8295 | 2161.5 | 31.6331 | 2164.5 | 919.8326 | 2167 | 184.0289 | 2170 | 318.3075 | 2172.5 | 484.8955 | 2158.5 | 31.6331 | 2158.5 | 31.6331 | 2158.5 | 318.3075
2175.5 | 852.7581 | 2178.5 | 108.8587 | 2181 | 400.1171 | 2183 | 173.6052 | 2186.5 | 567.6702 | 2189.5 | 169.584 | 2175.5 | 108.8587 | 2175.5 | 108.8587 | 2175.5 | 169.584
2192.5 | 194.0183 | 2195 | 402.3629 | 2198 | 125.5284 | 2200.5 | 66.4073 | 2203.5 | 1633.7234 | 2206.5 | 23.9376 | 2192.5 | 23.9376 | 2192.5 | 66.4073 | 2192.5 | 23.9376
2209 | 14.1382 | 2212 | 2.4628 | 2214.5 | 25.4129 | 2217.5 | 16.3498 | 2220.5 | 29.4797 | 2223 | 17.2226 | 2209 | 2.4628 | 2209 | 2.4628 | 2209 | 17.2226
2226 | 8.7428 | 2228.5 | 310.1284 | 2231.5 | 29.0273 | 2234.5 | 341.384 | 2237 | 66.6139 | 2240 | 24.1912 | 2226 | 8.7428 | 2226 | 8.7428 | 2226 | 24.1912
2242.5 | 27.9074 | 2245.5 | 1293.3089 | 2248.5 | 85.8872 | 2251 | 28.7504 | 2254 | 14.7293 | 2256.5 | 18.4274 | 2242.5 | 14.7293 | 2242.5 | 27.9074 | 2242.5 | 14.7293
2259.5 | 14.8969 | 2262.5 | 7.6142 | 2265 | 16.8419 | 2268 | 7.0606 | 2270.5 | 27.5722 | 2273.5 | 8.23 | 2259.5 | 7.0606 | 2259.5 | 7.0606 | 2259.5 | 8.23
2276.5 | 352.7438 | 2279 | 28.3032 | 2282 | 852.3962 | 2284.5 | 1.0669 | 2287.5 | 16.0558 | 2290.5 | 529.3242 | 2276.5 | 1.0669 | 2276.5 | 1.0669 | 2276.5 | 16.0558
2293 | 22.9944 | 2296 | 9.427 | 2298.5 | 27.0614 | 2301.5 | 2.0569 | 2304.5 | 12.3721 | 2307 | 414.9351 | 2293 | 2.0569 | 2293 | 2.0569 | 2293 | 12.3721
2310 | 6.8146 | 2312.5 | 25.1287 | 2315.5 | 20.1061 | 2318.5 | 13.6172 | 2321 | 25.2633 | 2324 | 3.7871 | 2310 | 3.7871 | 2310 | 6.8146 | 2310 | 3.7871
2326.5 | 10.2838 | 2329.5 | 24.2313 | 2332.5 | 253.7473 | 2335 | 25.6267 | 2338 | 10.9202 | 2340.5 | 16.5448 | 2326.5 | 10.2838 | 2326.5 | 10.2838 | 2326.5 | 10.9202

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 4 | Cable 5 | Cable 6 | Cable 7 | Cable 8
0 | -110 | 32.2874 | 32.4943 | 33.9423 | 33.5995 | 29.4489 | 28.7211 | 28.6751 | 29.4918 | 28.2132
0.7511 | -109.2489 | 32.287 | 32.4931 | 33.931 | 33.5994 | 29.4458 | 28.7199 | 28.6838 | 29.4866 | 28.2346
1.7826 | -108.2174 | 32.285 | 32.4769 | 33.9277 | 33.6036 | 29.441 | 28.7284 | 28.6852 | 29.4969 | 28.2174
2.754 | -107.246 | 32.2899 | 32.4813 | 33.9288 | 33.5881 | 29.4515 | 28.7332 | 28.6896 | 29.4809 | 28.2444
3.7554 | -106.2446 | 32.2873 | 32.4801 | 33.9259 | 33.5855 | 29.4565 | 28.7572 | 28.6905 | 29.486 | 28.255
4.7468 | -105.2532 | 32.2912 | 32.4655 | 33.9201 | 33.5805 | 29.4633 | 28.7405 | 28.6945 | 29.4933 | 28.2427
5.7483 | -104.2517 | 32.2909 | 32.4589 | 33.9102 | 33.5737 | 29.4618 | 28.763 | 28.6935 | 29.4939 | 28.2476
6.7497 | -103.2503 | 32.2877 | 32.4632 | 33.9018 | 33.574 | 29.4708 | 28.7593 | 28.7037 | 29.5001 | 28.2557
7.7511 | -102.2489 | 32.29 | 32.4498 | 33.9099 | 33.5646 | 29.4771 | 28.7405 | 28.7044 | 29.5045 | 28.2276
8.7526 | -101.2474 | 32.2864 | 32.4483 | 33.9028 | 33.5692 | 29.4622 | 28.7665 | 28.7085 | 29.4988 | 28.2619
9.754 | -100.246 | 32.2924 | 32.4485 | 33.8913 | 33.5635 | 29.4664 | 28.7799 | 28.7109 | 29.4936 | 28.2675
10.7555 | -99.2445 | 32.2835 | 32.4532 | 33.8967 | 33.5553 | 29.4793 | 28.7731 | 28.7146 | 29.5089 | 28.2517
11.7469 | -98.2531 | 32.2827 | 32.4424 | 33.889 | 33.5551 | 29.477 | 28.7568 | 28.7222 | 29.5077 | 28.2609
12.7483 | -97.2517 | 32.2851 | 32.4338 | 33.8874 | 33.5493 | 29.4766 | 28.7891 | 28.7227 | 29.5193 | 28.2523
13.7498 | -96.2502 | 32.2833 | 32.4329 | 33.8875 | 33.5435 | 29.4945 | 28.797 | 28.7227 | 29.5147 | 28.2719
14.7512 | -95.2488 | 32.2861 | 32.4207 | 33.8762 | 33.5413 | 29.494 | 28.7798 | 28.7312 | 29.5165 | 28.2723
15.7527 | -94.2473 | 32.2798 | 32.4212 | 33.8784 | 33.5402 | 29.5073 | 28.7989 | 28.7357 | 29.519 | 28.2416
16.7541 | -93.2459 | 32.2854 | 32.4164 | 33.8789 | 33.5408 | 29.4992 | 28.8082 | 28.7436 | 29.5167 | 28.2753
17.7555 | -92.2445 | 32.2814 | 32.417 | 33.8739 | 33.5395 | 29.4927 | 28.8029 | 28.7405 | 29.5234 | 28.267
18.747 | -91.253 | 32.2779 | 32.4051 | 33.875 | 33.5305 | 29.4958 | 28.791 | 28.7422 | 29.5193 | 28.2638
19.7484 | -90.2516 | 32.2772 | 32.4025 | 33.866 | 33.5267 | 29.4977 | 28.8183 | 28.749 | 29.5253 | 28.2979
20.7498 | -89.2502 | 32.2761 | 32.4005 | 33.867 | 33.5195 | 29.5055 | 28.8202 | 28.7589 | 29.5336 | 28.2723
21.7513 | -88.2487 | 32.2799 | 32.3942 | 33.865 | 33.5189 | 29.5052 | 28.8022 | 28.7562 | 29.5192 | 28.2887
22.7527 | -87.2473 | 32.282 | 32.3913 | 33.8654 | 33.5233 | 29.5126 | 28.8188 | 28.7599 | 29.5414 | 28.281
23.7542 | -86.2458 | 32.2788 | 32.3916 | 33.8605 | 33.5135 | 29.5117 | 28.8259 | 28.7646 | 29.5393 | 28.2745
24.7556 | -85.2444 | 32.2753 | 32.3855 | 33.8544 | 33.5158 | 29.5182 | 28.8424 | 28.7775 | 29.5341 | 28.3119
25.747 | -84.253 | 32.2777 | 32.3777 | 33.8517 | 33.5094 | 29.5111 | 28.8129 | 28.7657 | 29.5454 | 28.2974
26.7485 | -83.2515 | 32.2729 | 32.3794 | 33.8458 | 33.5022 | 29.5216 | 28.8427 | 28.7739 | 29.5394 | 28.3117
27.7499 | -82.2501 | 32.2763 | 32.371 | 33.8446 | 33.4985 | 29.5169 | 28.8424 | 28.7809 | 29.5458 | 28.3014
28.7513 | -81.2487 | 32.2652 | 32.3699 | 33.8438 | 33.4984 | 29.5248 | 28.8216 | 28.7794 | 29.5461 | 28.3033
29.7528 | -80.2472 | 32.2625 | 32.3631 | 33.8395 | 33.4944 | 29.5276 | 28.8463 | 28.7848 | 29.5449 | 28.304
30.7542 | -79.2458 | 32.2662 | 32.3639 | 33.8389 | 33.4996 | 29.5333 | 28.8586 | 28.7903 | 29.5506 | 28.3161
31.7456 | -78.2544 | 32.2676 | 32.357 | 33.8257 | 33.4906 | 29.5245 | 28.8562 | 28.7942 | 29.5573 | 28.3014
32.7471 | -77.2529 | 32.261 | 32.3562 | 33.8313 | 33.4877 | 29.5244 | 28.8366 | 28.7986 | 29.5552 | 28.3122
33.7485 | -76.2515 | 32.2644 | 32.3586 | 33.8252 | 33.4807 | 29.5414 | 28.8724 | 28.7977 | 29.5387 | 28.3278
34.75 | -75.25 | 32.2608 | 32.349 | 33.8228 | 33.4816 | 29.5416 | 28.8782 | 28.8089 | 29.5575 | 28.3084
35.7514 | -74.2486 | 32.269 | 32.3513 | 33.815 | 33.4813 | 29.5488 | 28.8572 | 28.8025 | 29.5598 | 28.3178
36.7528 | -73.2472 | 32.2658 | 32.3381 | 33.8174 | 33.4746 | 29.5406 | 28.8723 | 28.8094 | 29.5539 | 28.3352
37.7543 | -72.2457 | 32.2663 | 32.3467 | 33.8114 | 33.47 | 29.545 | 28.8854 | 28.8123 | 29.563 | 28.3071
38.7457 | -71.2543 | 32.2626 | 32.3379 | 33.8102 | 33.4624 | 29.5421 | 28.8876 | 28.8188 | 29.5578 | 28.3421
39.7472 | -70.2528 | 32.2657 | 32.3391 | 33.7942 | 33.465 | 29.551 | 28.865 | 28.8219 | 29.5688 | 28.3084
40.7486 | -69.2514 | 32.2697 | 32.3451 | 33.7918 | 33.4581 | 29.5568 | 28.888 | 28.8244 | 29.5694 | 28.3491
41.75 | -68.25 | 32.2638 | 32.3448 | 33.7961 | 33.4622 | 29.5553 | 28.9046 | 28.8262 | 29.5733 | 28.3247
42.7515 | -67.2485 | 32.2637 | 32.3447 | 33.8069 | 33.4528 | 29.5609 | 28.8836 | 28.8346 | 29.5713 | 28.3329
43.7529 | -66.2471 | 32.2648 | 32.3374 | 33.7991 | 33.4536 | 29.5603 | 28.8922 | 28.8432 | 29.5767 | 28.3434
44.7544 | -65.2456 | 32.2555 | 32.3393 | 33.7987 | 33.4458 | 29.5644 | 28.9065 | 28.8431 | 29.582 | 28.3376
45.7558 | -64.2442 | 32.2532 | 32.3307 | 33.79 | 33.4429 | 29.5665 | 28.9015 | 28.8445 | 29.5742 | 28.3473
46.7472 | -63.2528 | 32.2569 | 32.322 | 33.7826 | 33.4411 | 29.572 | 28.8867 | 28.8469 | 29.5822 | 28.3308
47.7487 | -62.2513 | 32.2572 | 32.3179 | 33.7737 | 33.4419 | 29.5706 | 28.9167 | 28.8578 | 29.5861 | 28.3453
48.7501 | -61.2499 | 32.2496 | 32.3121 | 33.7661 | 33.4303 | 29.5693 | 28.9231 | 28.8567 | 29.5843 | 28.3449
49.7515 | -60.2485 | 32.2508 | 32.3025 | 33.7741 | 33.4277 | 29.5757 | 28.8923 | 28.8577 | 29.5871 | 28.3586
50.753 | -59.247 | 32.2579 | 32.3027 | 33.7717 | 33.4223 | 29.5743 | 28.9116 | 28.8572 | 29.5942 | 28.3562
51.7544 | -58.2456 | 32.2513 | 32.2998 | 33.7694 | 33.4245 | 29.5878 | 28.9272 | 28.866 | 29.5919 | 28.3624
52.7458 | -57.2542 | 32.2533 | 32.2958 | 33.758 | 33.424 | 29.5744 | 28.9329 | 28.8711 | 29.5947 | 28.3574
53.7473 | -56.2527 | 32.2574 | 32.2934 | 33.7652 | 33.4165 | 29.5793 | 28.9129 | 28.8718 | 29.5992 | 28.3525
54.7487 | -55.2513 | 32.2529 | 32.2964 | 33.7529 | 33.4152 | 29.5808 | 28.9365 | 28.8694 | 29.593 | 28.3705
55.7602 | -54.2398 | 32.2537 | 32.2929 | 33.752 | 33.4097 | 29.5969 | 28.9408 | 28.8772 | 29.5831 | 28.38
56.7516 | -53.2484 | 32.2527 | 32.2829 | 33.7514 | 33.4095 | 29.5831 | 28.9258 | 28.886 | 29.599 | 28.3803
57.753 | -52.247 | 32.252 | 32.2835 | 33.7452 | 33.4059 | 29.591 | 28.9392 | 28.888 | 29.5984 | 28.3713
58.7545 | -51.2455 | 32.2517 | 32.2809 | 33.7431 | 33.4015 | 29.5929 | 28.9627 | 28.8871 | 29.6191 | 28.3645
59.7459 | -50.2541 | 32.245 | 32.269 | 33.7434 | 33.3989 | 29.596 | 28.9552 | 28.8883 | 29.6097 | 28.3678
60.7474 | -49.2526 | 32.2475 | 32.2681 | 33.735 | 33.3996 | 29.5936 | 28.9385 | 28.8947 | 29.6039 | 28.3965
61.7488 | -48.2512 | 32.2422 | 32.268 | 33.7373 | 33.3897 | 29.6049 | 28.9679 | 28.8972 | 29.6118 | 28.3725
62.7502 | -47.2498 | 32.2435 | 32.2647 | 33.7297 | 33.3895 | 29.6072 | 28.9702 | 28.8972 | 29.6146 | 28.3774
63.7517 | -46.2483 | 32.2445 | 32.2561 | 33.727 | 33.3872 | 29.6134 | 28.9404 | 28.9017 | 29.6199 | 28.3756
64.7531 | -45.2469 | 32.2489 | 32.2579 | 33.7232 | 33.3859 | 29.6083 | 28.9676 | 28.9077 | 29.612 | 28.4101
65.7545 | -44.2455 | 32.2523 | 32.2523 | 33.7209 | 33.3811 | 29.6115 | 28.978 | 28.9107 | 29.6088 | 28.409
66.756 | -43.244 | 32.2504 | 32.2464 | 33.73 | 33.3764 | 29.6169 | 28.9771 | 28.917 | 29.6203 | 28.3821
67.7474 | -42.2526 | 32.2416 | 32.2419 | 33.7168 | 33.377 | 29.6158 | 28.9598 | 28.9188 | 29.627 | 28.3726
68.7489 | -41.2511 | 32.2487 | 32.2348 | 33.7181 | 33.3748 | 29.615 | 28.9927 | 28.9152 | 29.6286 | 28.3942
69.7503 | -40.2497 | 32.2459 | 32.2398 | 33.7016 | 33.3739 | 29.6229 | 28.9923 | 28.9214 | 29.619 | 28.4044
70.7517 | -39.2483 | 32.2491 | 32.2341 | 33.7051 | 33.3709 | 29.6252 | 28.9758 | 28.9303 | 29.628 | 28.3957
71.7532 | -38.2468 | 32.2465 | 32.2299 | 33.699 | 33.369 | 29.6363 | 28.9838 | 28.9308 | 29.6223 | 28.3976
72.7546 | -37.2454 | 32.2438 | 32.2264 | 33.695 | 33.3685 | 29.6316 | 28.9979 | 28.9298 | 29.6209 | 28.4039
73.746 | -36.254 | 32.2435 | 32.2341 | 33.694 | 33.3661 | 29.6271 | 29.0035 | 28.9284 | 29.6288 | 28.4171
74.7475 | -35.2525 | 32.2406 | 32.2295 | 33.6953 | 33.3557 | 29.6284 | 28.9827 | 28.9372 | 29.632 | 28.4033
75.7489 | -34.2511 | 32.2434 | 32.2286 | 33.6848 | 33.3565 | 29.6397 | 29.0105 | 28.9432 | 29.6288 | 28.4019
76.7504 | -33.2496 | 32.2421 | 32.229 | 33.6725 | 33.3454 | 29.6385 | 29.022 | 28.9419 | 29.6358 | 28.4261
77.7518 | -32.2482 | 32.2405 | 32.2207 | 33.6776 | 33.3499 | 29.6419 | 28.9938 | 28.9495 | 29.641 | 28.4206
78.7532 | -31.2468 | 32.2396 | 32.2067 | 33.6711 | 33.3467 | 29.6434 | 29.0081 | 28.944 | 29.6447 | 28.4084
79.7547 | -30.2453 | 32.2418 | 32.2066 | 33.6769 | 33.341 | 29.6426 | 29.0233 | 28.955 | 29.6413 | 28.4072
80.7461 | -29.2539 | 32.2367 | 32.2094 | 33.6691 | 33.3389 | 29.6494 | 29.0306 | 28.9629 | 29.6298 | 28.4389
81.7475 | -28.2525 | 32.2402 | 32.2074 | 33.6678 | 33.3362 | 29.6487 | 29.0028 | 28.9649 | 29.6411 | 28.4175
82.749 | -27.251 | 32.2441 | 32.2009 | 33.6697 | 33.3339 | 29.653 | 29.0312 | 28.9633 | 29.6515 | 28.4256
83.7504 | -26.2496 | 32.2378 | 32.2069 | 33.6729 | 33.33 | 29.6492 | 29.0339 | 28.9679 | 29.6481 | 28.4378
84.7519 | -25.2481 | 32.2403 | 32.2007 | 33.6508 | 33.3274 | 29.6568 | 29.015 | 28.9744 | 29.6485 | 28.4273
85.7533 | -24.2467 | 32.2351 | 32.1924 | 33.6545 | 33.3259 | 29.6636 | 29.0257 | 28.9732 | 29.6503 | 28.4221
86.7547 | -23.2453 | 32.2335 | 32.1887 | 33.6473 | 33.3189 | 29.6597 | 29.0413 | 28.977 | 29.6445 | 28.4393
87.7462 | -22.2538 | 32.2318 | 32.1856 | 33.6482 | 33.3132 | 29.6617 | 29.0427 | 28.9826 | 29.6682 | 28.4346
88.7476 | -21.2524 | 32.236 | 32.1775 | 33.6441 | 33.3106 | 29.6713 | 29.023 | 28.983 | 29.6514 | 28.4347
89.7491 | -20.2509 | 32.2344 | 32.1763 | 33.6492 | 33.3121 | 29.6618 | 29.0573 | 28.9803 | 29.6548 | 28.4469
90.7505 | -19.2495 | 32.2292 | 32.168 | 33.6343 | 33.2998 | 29.6659 | 29.0589 | 28.9847 | 29.6616 | 28.4348
91.7519 | -18.2481 | 32.2279 | 32.1691 | 33.6438 | 33.2962 | 29.6708 | 29.0378 | 28.9921 | 29.654 | 28.4354
92.7534 | -17.2466 | 32.2241 | 32.1543 | 33.637 | 33.2857 | 29.6783 | 29.0529 | 28.9886 | 29.669 | 28.4342
93.7548 | -16.2452 | 32.2239 | 32.1621 | 33.6357 | 33.2856 | 29.6775 | 29.0655 | 28.9972 | 29.6661 | 28.4303
94.7462 | -15.2538 | 32.2204 | 32.1585 | 33.6302 | 33.2841 | 29.6849 | 29.0635 | 29.0004 | 29.6509 | 28.4731
95.7477 | -14.2523 | 32.2225 | 32.1581 | 33.6191 | 33.2846 | 29.6782 | 29.0424 | 28.9995 | 29.6689 | 28.4536
96.7491 | -13.2509 | 32.2144 | 32.1591 | 33.6248 | 33.2751 | 29.6775 | 29.0745 | 29.0066 | 29.6645 | 28.4487
97.7506 | -12.2494 | 32.2099 | 32.144 | 33.6268 | 33.2827 | 29.6896 | 29.0767 | 29.0084 | 29.6698 | 28.4526
98.752 | -11.248 | 32.2152 | 32.1404 | 33.6154 | 33.2758 | 29.6776 | 29.0496 | 29.0145 | 29.6688 | 28.4507
99.7534 | -10.2466 | 32.215 | 32.1394 | 33.6187 | 33.2711 | 29.6933 | 29.071 | 29.013 | 29.6645 | 28.4626
100.7549 | -9.2451 | 32.2124 | 32.138 | 33.6116 | 33.2685 | 29.6944 | 29.0844 | 29.0163 | 29.6833 | 28.4635
101.7463 | -8.2537 | 32.2063 | 32.1441 | 33.6023 | 33.2727 | 29.6858 | 29.0922 | 29.0208 | 29.6697 | 28.4754
102.7477 | -7.2523 | 32.204 | 32.1315 | 33.6082 | 33.266 | 29.6969 | 29.0691 | 29.0185 | 29.6862 | 28.4446
103.7492 | -6.2508 | 32.2004 | 32.1349 | 33.5993 | 33.2597 | 29.708 | 29.0967 | 29.0258 | 29.6775 | 28.4757
104.7506 | -5.2494 | 32.1947 | 32.1363 | 33.5965 | 33.2637 | 29.7026 | 29.097 | 29.0258 | 29.6881 | 28.4689
105.7521 | -4.2479 | 32.1995 | 32.1275 | 33.5906 | 33.2587 | 29.6995 | 29.0743 | 29.03 | 29.6806 | 28.4792
106.7535 | -3.2465 | 32.1904 | 31.9734 | 33.5883 | 33.1891 | 29.7256 | 29.128 | 29.0223 | 29.6886 | 28.471
107.7549 | -2.2451 | 32.1965 | 31.9858 | 33.5825 | 33.1931 | 29.7259 | 29.14 | 29.0308 | 29.6731 | 28.4976
108.7564 | -1.2436 | 32.2188 | 32.0227 | 33.5979 | 33.2206 | 29.7245 | 29.1285 | 29.0419 | 29.6853 | 28.4783
109.7478 | -0.2522 | 32.5367 | 32.0517 | 33.5992 | 33.2228 | 29.7173 | 29.1018 | 29.0399 | 29.6852 | 28.4864
110.7492 | 0.7492 | 33.4051 | 32.063 | 33.5981 | 33.2282 | 29.7195 | 29.1235 | 29.043 | 29.6953 | 28.4799
111.7507 | 1.7507 | 34.8706 | 32.0661 | 33.596 | 33.2304 | 29.7117 | 29.1294 | 29.0493 | 29.6794 | 28.4938
112.7521 | 2.7521 | 36.8688 | 32.0746 | 33.6093 | 33.2361 | 29.7241 | 29.097 | 29.0485 | 29.7009 | 28.4544
113.7536 | 3.7536 | 39.3411 | 32.0845 | 33.6156 | 33.238 | 29.729 | 29.1213 | 29.0514 | 29.6889 | 28.4939
114.755 | 4.755 | 42.2132 | 32.0966 | 33.623 | 33.24 | 29.7251 | 29.1355 | 29.0623 | 29.689 | 28.5044
115.7464 | 5.7464 | 45.4218 | 32.1025 | 33.6284 | 33.2536 | 29.7341 | 29.1337 | 29.0642 | 29.7091 | 28.4934
116.7479 | 6.7479 | 48.9012 | 32.1115 | 33.6517 | 33.2734 | 29.7288 | 29.1098 | 29.0662 | 29.6885 | 28.5022
117.7493 | 7.7493 | 52.6308 | 32.125 | 33.6682 | 33.2817 | 29.7275 | 29.1417 | 29.0642 | 29.701 | 28.4889
118.7508 | 8.7508 | 56.6033 | 32.1459 | 33.7081 | 33.3061 | 29.7264 | 29.1499 | 29.0717 | 29.7018 | 28.5009
119.7522 | 9.7522 | 60.773 | 32.1734 | 33.7297 | 33.3216 | 29.7381 | 29.1274 | 29.0673 | 29.7041 | 28.5129
120.7536 | 10.7536 | 65.103 | 32.1994 | 33.7522 | 33.3493 | 29.7344 | 29.1346 | 29.0762 | 29.7168 | 28.4722
121.7551 | 11.7551 | 69.5785 | 32.2269 | 33.8059 | 33.378 | 29.7497 | 29.1609 | 29.073 | 29.6965 | 28.505
122.7465 | 12.7465 | 74.2101 | 32.2557 | 33.8639 | 33.4229 | 29.7404 | 29.1553 | 29.0814 | 29.7034 | 28.5028
123.7479 | 13.7479 | 79.0459 | 32.2913 | 33.9056 | 33.4601 | 29.7433 | 29.1346 | 29.0851 | 29.7149 | 28.4981
124.7494 | 14.7494 | 83.9852 | 32.3373 | 33.9539 | 33.5094 | 29.739 | 29.1565 | 29.0835 | 29.7137 | 28.5063
125.7508 | 15.7508 | 89.0025 | 32.3758 | 34.0139 | 33.5476 | 29.7541 | 29.1626 | 29.0962 | 29.7206 | 28.4952
126.7523 | 16.7523 | 94.1085 | 32.4206 | 34.0891 | 33.5949 | 29.7451 | 29.1369 | 29.0917 | 29.728 | 28.5089
127.7537 | 17.7537 | 99.3405 | 32.4814 | 34.1718 | 33.644 | 29.7607 | 29.1605 | 29.0986 | 29.7124 | 28.5209
128.7551 | 18.7551 | 104.621 | 32.5134 | 34.2579 | 33.7024 | 29.7531 | 29.1748 | 29.0926 | 29.7259 | 28.5163
129.7466 | 19.7466 | 110.0394 | 32.5839 | 34.3681 | 33.7824 | 29.7555 | 29.1742 | 29.1049 | 29.7316 | 28.5124
130.748 | 20.748 | 115.5325 | 32.6652 | 34.4357 | 33.8763 | 29.7529 | 29.1529 | 29.1058 | 29.7294 | 28.5241
131.7494 | 21.7494 | 121.0464 | 32.7257 | 34.5338 | 33.9391 | 29.7663 | 29.1809 | 29.1041 | 29.741 | 28.5088
132.7509 | 22.7509 | 126.592 | 32.8117 | 34.645 | 34.0075 | 29.7747 | 29.1818 | 29.1126 | 29.7355 | 28.5045
133.7523 | 23.7523 | 132.1672 | 32.8835 | 34.7605 | 34.1052 | 29.7653 | 29.1649 | 29.1197 | 29.7348 | 28.5201
134.7538 | 24.7538 | 137.7873 | 32.9693 | 34.8993 | 34.1905 | 29.7752 | 29.1792 | 29.1274 | 29.7426 | 28.534
135.7552 | 25.7552 | 143.4563 | 33.0578 | 35.0214 | 34.2747 | 29.779 | 29.1953 | 29.1247 | 29.7316 | 28.5322
136.7466 | 26.7466 | 149.1855 | 33.1542 | 35.1411 | 34.3823 | 29.7832 | 29.1948 | 29.1274 | 29.7477 | 28.5298
137.7481 | 27.7481 | 154.9826 | 33.2653 | 35.2976 | 34.4814 | 29.7784 | 29.1785 | 29.1309 | 29.7574 | 28.5274
138.7495 | 28.7495 | 160.7269 | 33.3785 | 35.4799 | 34.602 | 29.7834 | 29.2063 | 29.1337 | 29.767 | 28.5262
139.751 | 29.751 | 166.351 | 33.5024 | 35.6232 | 34.7463 | 29.803 | 29.2094 | 29.1411 | 29.7702 | 28.5315
140.7524 | 30.7524 | 171.9783 | 33.6245 | 35.7597 | 34.881 | 29.7936 | 29.1963 | 29.1388 | 29.7747 | 28.5504
141.7538 | 31.7538 | 177.5534 | 33.7549 | 35.9591 | 35.0116 | 29.8023 | 29.2047 | 29.1482 | 29.7598 | 28.5607
142.7553 | 32.7553 | 183.1313 | 33.9082 | 36.1512 | 35.1668 | 29.8146 | 29.2231 | 29.1499 | 29.7782 | 28.5405
143.7467 | 33.7467 | 188.755 | 34.0394 | 36.3434 | 35.3063 | 29.8132 | 29.2215 | 29.1633 | 29.7881 | 28.5509
144.7481 | 34.7481 | 194.2681 | 34.1897 | 36.5609 | 35.4672 | 29.8143 | 29.2024 | 29.1625 | 29.7915 | 28.5689
145.7496 | 35.7496 | 199.8516 | 34.3534 | 36.7921 | 35.6439 | 29.824 | 29.2337 | 29.1706 | 29.8001 | 28.5586
146.751 | 36.751 | 205.498 | 34.5307 | 37.056 | 35.7993 | 29.8252 | 29.2335 | 29.1732 | 29.8039 | 28.5754
147.7525 | 37.7525 | 211.1135 | 34.7664 | 37.2749 | 35.9983 | 29.8266 | 29.2142 | 29.1758 | 29.81 | 28.5652
148.7539 | 38.7539 | 216.7648 | 34.8929 | 37.5359 | 36.1738 | 29.8354 | 29.2277 | 29.1858 | 29.8199 | 28.5799
149.7553 | 39.7553 | 222.4056 | 35.049 | 37.8035 | 36.3896 | 29.8577 | 29.2412 | 29.1959 | 29.8265 | 28.5875
150.7568 | 40.7568 | 228.1553 | 35.2746 | 38.0657 | 36.6002 | 29.8517 | 29.2384 | 29.196 | 29.832 | 28.583
151.7482 | 41.7482 | 233.7993 | 35.4491 | 38.4202 | 36.8195 | 29.8564 | 29.2292 | 29.2028 | 29.8376 | 28.5934
152.7496 | 42.7496 | 239.364 | 35.657 | 38.6923 | 37.0205 | 29.8682 | 29.2535 | 29.2101 | 29.8541 | 28.6064
153.7511 | 43.7511 | 244.9036 | 35.903 | 39.0883 | 37.2608 | 29.873 | 29.2574 | 29.219 | 29.8611 | 28.6261
154.7525 | 44.7525 | 250.4676 | 36.1076 | 39.3789 | 37.5105 | 29.8938 | 29.2386 | 29.228 | 29.8821 | 28.6143
155.754 | 45.754 | 256.0684 | 36.3737 | 39.7251 | 37.7859 | 29.8938 | 29.25 | 29.2349 | 29.8951 | 28.6158
156.7554 | 46.7554 | 261.7005 | 36.6686 | 40.1696 | 38.0645 | 29.9143 | 29.2696 | 29.246 | 29.9102 | 28.6309
157.7468 | 47.7468 | 267.3306 | 36.7834 | 40.5009 | 38.2641 | 29.9332 | 29.3056 | 29.2514 | 29.9151 | 28.663
158.7483 | 48.7483 | 272.8379 | 37.032 | 40.8491 | 38.5456 | 29.9538 | 29.2848 | 29.2605 | 29.9357 | 28.633
159.7497 | 49.7497 | 278.0032 | 37.2468 | 41.2767 | 38.8385 | 29.9706 | 29.3228 | 29.2693 | 29.9478 | 28.6717
160.7511 | 50.7511 | 282.8905 | 37.6245 | 41.7682 | 39.1708 | 29.9722 | 29.3117 | 29.2775 | 29.9774 | 28.6774
161.7526 | 51.7526 | 287.4304 | 37.8397 | 42.1329 | 39.4403 | 29.9985 | 29.3081 | 29.2878 | 29.9778 | 28.7013
162.754 | 52.754 | 291.7463 | 38.1923 | 42.5257 | 39.7583 | 30.0077 | 29.319 | 29.3053 | 29.9974 | 28.6895
163.7455 | 53.7455 | 295.8128 | 38.4273 | 42.9556 | 40.0669 | 30.0195 | 29.3454 | 29.3159 | 30.0277 | 28.7007
164.7469 | 54.7469 | 299.6719 | 38.7075 | 43.3843 | 40.3722 | 30.0436 | 29.3408 | 29.3264 | 30.0314 | 28.7342
165.7483 | 55.7483 | 303.4225 | 39.0846 | 43.8269 | 40.7095 | 30.0638 | 29.3384 | 29.3449 | 30.0626 | 28.7332
166.7498 | 56.7498 | 307.1388 | 39.4087 | 44.2317 | 41.056 | 30.0881 | 29.3601 | 29.3537 | 30.0881 | 28.7552
167.7512 | 57.7512 | 310.5116 | 39.7443 | 44.6566 | 41.3862 | 30.1008 | 29.3623 | 29.3618 | 30.1124 | 28.751
168.7527 | 58.7527 | 313.5719 | 40.0631 | 45.1276 | 41.7018 | 30.114 | 29.3574 | 29.3837 | 30.1336 | 28.7866
169.7541 | 59.7541 | 316.363 | 40.3848 | 45.6139 | 42.0536 | 30.1529 | 29.3723 | 29.3997 | 30.1618 | 28.7926
170.7555 | 60.7555 | 318.798 | 40.6818 | 46.0674 | 42.3792 | 30.1719 | 29.3911 | 29.4159 | 30.1963 | 28.8161
171.747 | 61.747 | 320.8275 | 40.9875 | 46.5235 | 42.7194 | 30.1914 | 29.3972 | 29.4313 | 30.2163 | 28.8358
172.7484 | 62.7484 | 322.5653 | 41.2931 | 46.9763 | 43.0355 | 30.2031 | 29.3668 | 29.4463 | 30.2454 | 28.8528
173.7498 | 63.7498 | 324.1079 | 41.6244 | 47.4316 | 43.3676 | 30.2422 | 29.4026 | 29.4637 | 30.2876 | 28.8413
174.7513 | 64.7513 | 325.4442 | 41.9953 | 47.9049 | 43.7042 | 30.2591 | 29.4004 | 29.4884 | 30.318 | 28.8556
175.7527 | 65.7527 | 326.5474 | 42.3992 | 48.3808 | 44.0918 | 30.2739 | 29.3783 | 29.503 | 30.3521 | 28.8918
176.7542 | 66.7542 | 327.6211 | 42.6951 | 48.7939 | 44.4204 | 30.3152 | 29.391 | 29.5267 | 30.3807 | 28.9205
177.7556 | 67.7556 | 328.4548 | 43.006 | 49.2393 | 44.7361 | 30.3537 | 29.4122 | 29.5427 | 30.4207 | 28.9327
178.747 | 68.747 | 329.0485 | 43.3265 | 49.6983 | 45.059 | 30.36 | 29.4271 | 29.5682 | 30.4607 | 28.9286
179.7485 | 69.7485 | 329.5939 | 43.6489 | 50.1316 | 45.3602 | 30.41 | 29.4142 | 29.5913 | 30.4861 | 28.9686
180.7499 | 70.7499 | 330.0948 | 43.931 | 50.5655 | 45.6889 | 30.449 | 29.4424 | 29.6113 | 30.5397 | 28.986
181.7513 | 71.7513 | 330.5722 | 44.2546 | 51.0034 | 46.0131 | 30.4878 | 29.4655 | 29.6303 | 30.5695 | 29.0218
182.7528 | 72.7528 | 330.9572 | 44.5544 | 51.4409 | 46.3248 | 30.5164 | 29.4524 | 29.6528 | 30.6289 | 29.0236
183.7642 | 73.7642 | 331.2452 | 44.8538 | 51.898 | 46.6473 | 30.5595 | 29.4694 | 29.6785 | 30.6531 | 29.0583
184.7457 | 74.7457 | 331.5468 | 45.1585 | 52.276 | 46.9634 | 30.5967 | 29.5064 | 29.712 | 30.7115 | 29.0738
185.7471 | 75.7471 | 331.6777 | 45.4672 | 52.6771 | 47.2805 | 30.6379 | 29.5041 | 29.7292 | 30.7508 | 29.1132
186.7485 | 76.7485 | 331.6746 | 45.7523 | 53.1166 | 47.5919 | 30.6848 | 29.4998 | 29.7616 | 30.808 | 29.1293
187.75 | 77.75 | 331.5665 | 46.0419 | 53.5467 | 47.9138 | 30.7217 | 29.5382 | 29.7856 | 30.8517 | 29.1409
188.7514 | 78.7514 | 331.4244 | 46.3568 | 53.9692 | 48.2337 | 30.7672 | 29.5564 | 29.8102 | 30.8906 | 29.1829
189.7529 | 79.7529 | 331.3812 | 46.627 | 54.3937 | 48.5246 | 30.8033 | 29.5444 | 29.8417 | 30.9378 | 29.225
190.7543 | 80.7543 | 331.2716 | 46.9351 | 54.8223 | 48.8232 | 30.8536 | 29.568 | 29.8664 | 30.9974 | 29.246
191.7457 | 81.7457 | 331.1319 | 47.2129 | 55.169 | 49.1217 | 30.9065 | 29.6014 | 29.8942 | 31.0503 | 29.2625
192.7572 | 82.7572 | 331.0192 | 47.5151 | 55.5525 | 49.4206 | 30.9512 | 29.6099 | 29.9328 | 31.0968 | 29.3225
193.7486 | 83.7486 | 331.003 | 47.8065 | 56.0003 | 49.7322 | 30.9983 | 29.6008 | 29.9548 | 31.1594 | 29.325
194.75 | 84.75 | 330.9087 | 48.1047 | 56.4114 | 50.0254 | 31.0546 | 29.6502 | 29.9942 | 31.2072 | 29.3698
195.7515 | 85.7515 | 330.6452 | 48.3793 | 56.7786 | 50.3258 | 31.1096 | 29.6684 | 30.0195 | 31.2595 | 29.3932
196.7529 | 86.7529 | 330.4059 | 48.6671 | 57.2266 | 50.6153 | 31.1561 | 29.6605 | 30.0631 | 31.3291 | 29.4291
197.7544 | 87.7544 | 330.1664 | 48.9426 | 57.6304 | 50.9067 | 31.2078 | 29.6902 | 30.0873 | 31.3834 | 29.471
198.7558 | 88.7558 | 329.8739 | 49.2303 | 58.032 | 51.1971 | 31.2538 | 29.7238 | 30.1217 | 31.4531 | 29.4945
199.7472 | 89.7472 | 329.4623 | 49.5233 | 58.3952 | 51.4959 | 31.3189 | 29.7427 | 30.1539 | 31.5198 | 29.5017
200.7487 | 90.7487 | 329.1237 | 49.7936 | 58.8144 | 51.7776 | 31.3719 | 29.7307 | 30.1941 | 31.5717 | 29.5616
201.7501 | 91.7501 | 328.8279 | 50.063 | 59.2333 | 52.0672 | 31.4372 | 29.7814 | 30.2291 | 31.6143 | 29.6126
202.7515 | 92.7515 | 328.5277 | 50.3359 | 59.5996 | 52.3481 | 31.4911 | 29.7995 | 30.2558 | 31.6891 | 29.6161
203.753 | 93.753 | 328.1452 | 50.6187 | 59.9804 | 52.6486 | 31.5512 | 29.8002 | 30.3005 | 31.7607 | 29.6445
204.7544 | 94.7544 | 327.8268 | 50.8736 | 60.3665 | 52.9067 | 31.613 | 29.8399 | 30.336 | 31.8171 | 29.7047
205.7458 | 95.7458 | 327.5046 | 51.1422 | 60.752 | 53.1965 | 31.6702 | 29.8693 | 30.3778 | 31.89 | 29.7115
206.7473 | 96.7473 | 327.0613 | 51.4482 | 61.1106 | 53.4649 | 31.7407 | 29.8917 | 30.4134 | 31.9379 | 29.781
207.7487 | 97.7487 | 326.6527 | 51.7034 | 61.5344 | 53.7366 | 31.7982 | 29.8903 | 30.4521 | 32.0203 | 29.8132
208.7502 | 98.7502 | 326.2301 | 51.9575 | 61.9092 | 54.0198 | 31.8644 | 29.9368 | 30.4942 | 32.0921 | 29.8381
209.7516 | 99.7516 | 325.7624 | 52.2504 | 62.2482 | 54.2905 | 31.9249 | 29.965 | 30.5369 | 32.1514 | 29.8848
210.753 | 100.753 | 325.465 | 52.504 | 62.5958 | 54.5667 | 31.9962 | 29.9624 | 30.5701 | 32.2159 | 29.9119
211.7545 | 101.7545 | 325.0793 | 52.7614 | 62.9857 | 54.8377 | 32.0522 | 29.9926 | 30.6158 | 32.2768 | 29.9609
212.7459 | 102.7459 | 324.6307 | 53.0108 | 63.3573 | 55.1012 | 32.1383 | 30.0368 | 30.6571 | 32.3422 | 30.018
213.7574 | 103.7574 | 324.2218 | 53.2732 | 63.8126 | 55.3725 | 32.2121 | 30.0616 | 30.7 | 32.4326 | 30.0301
214.7488 | 104.7488 | 323.9144 | 53.5505 | 64.1688 | 55.6616 | 32.2736 | 30.0626 | 30.7452 | 32.495 | 30.064
215.7502 | 105.7502 | 323.4952 | 53.8152 | 64.4642 | 55.926 | 32.3444 | 30.1171 | 30.7884 | 32.5536 | 30.1272
216.7517 | 106.7517 | 323.028 | 54.0459 | 64.8046 | 56.2027 | 32.4218 | 30.1456 | 30.8361 | 32.6354 | 30.1564
217.7531 | 107.7531 | 322.688 | 54.317 | 65.1544 | 56.4556 | 32.4809 | 30.1465 | 30.8753 | 32.7104 | 30.1984
218.7546 | 108.7546 | 322.4158 | 54.5871 | 65.5037 | 56.7116 | 32.5533 | 30.188 | 30.9233 | 32.7884 | 30.2413
219.756 | 109.756 | 322.1528 | 54.811 | 65.8708 | 56.9547 | 32.6355 | 30.2225 | 30.9608 | 32.8493 | 30.2944
220.7474 | 110.7474 | 321.818 | 55.0758 | 66.1809 | 57.2329 | 32.7088 | 30.2529 | 31.0107 | 32.9312 | 30.3111
221.7489 | 111.7489 | 321.3074 | 55.3219 | 66.4838 | 57.488 | 32.7838 | 30.2611 | 31.0556 | 33.0079 | 30.3765
222.7503 | 112.7503 | 320.9307 | 55.5716 | 66.8531 | 57.7439 | 32.8586 | 30.3156 | 31.1152 | 33.0832 | 30.4105
223.7517 | 113.7517 | 320.5045 | 55.8126 | 67.1811 | 57.9941 | 32.936 | 30.3474 | 31.1554 | 33.1497 | 30.4794
224.7532 | 114.7532 | 320.0041 | 56.0795 | 67.5205 | 58.2516 | 33.0105 | 30.3539 | 31.2014 | 33.2377 | 30.4947
225.7546 | 115.7546 | 319.4939 | 56.3034 | 67.8736 | 58.5062 | 33.0915 | 30.3958 | 31.2504 | 33.3081 | 30.5431
226.746 | 116.746 | 319.0186 | 56.5514 | 68.2198 | 58.7444 | 33.1652 | 30.4335 | 31.3016 | 33.3857 | 30.601
227.7475 | 117.7475 | 318.5429 | 56.8034 | 68.548 | 59.0132 | 33.2441 | 30.4734 | 31.3539 | 33.4742 | 30.6284
228.7489 | 118.7489 | 317.9965 | 57.038 | 68.867 | 59.2591 | 33.321 | 30.476 | 31.4035 | 33.5478 | 30.6909
229.7504 | 119.7504 | 317.4885 | 57.2754 | 69.1927 | 59.4862 | 33.3996 | 30.5343 | 31.4486 | 33.6343 | 30.7239
230.7518 | 120.7518 | 316.973 | 57.5112 | 69.5493 | 59.7198 | 33.5021 | 30.5737 | 31.5091 | 33.7034 | 30.7793
231.7532 | 121.7532 | 316.4947 | 57.7541 | 69.9172 | 59.9738 | 33.5672 | 30.5856 | 31.5569 | 33.7887 | 30.8346
232.7547 | 122.7547 | 316.0949 | 58.0279 | 70.235 | 60.2239 | 33.655 | 30.6312 | 31.6038 | 33.8688 | 30.8623
233.7461 | 123.7461 | 315.6638 | 58.2429 | 70.5284 | 60.4423 | 33.7283 | 30.68 | 31.6555 | 33.9458 | 30.9264
234.7576 | 124.7576 | 315.1434 | 58.4632 | 70.8413 | 60.688 | 33.8174 | 30.709 | 31.707 | 34.0303 | 30.9453
235.749 | 125.749 | 314.6544 | 58.6874 | 71.1555 | 60.9368 | 33.9005 | 30.7183 | 31.7611 | 34.1081 | 31.0044
236.8406 | 126.8406 | 314.1354 | 58.9466 | 71.4696 | 61.1696 | 33.9975 | 30.7905 | 31.8233 | 34.1973 | 31.061
237.7519 | 127.7519 | 313.6395 | 59.1627 | 71.7626 | 61.401 | 34.0799 | 30.8252 | 31.8763 | 34.2638 | 31.1196
238.7533 | 128.7533 | 313.1887 | 59.3855 | 72.0742 | 61.6276 | 34.1591 | 30.841 | 31.9231 | 34.357 | 31.1594
239.7548 | 129.7548 | 312.6739 | 59.5978 | 72.3938 | 61.8621 | 34.2552 | 30.8883 | 31.9797 | 34.4395 | 31.1966
240.7562 | 130.7562 | 312.2651 | 59.8119 | 72.6797 | 62.0969 | 34.3299 | 30.9386 | 32.0332 | 34.5207 | 31.2567
241.7476 | 131.7476 | 311.8132 | 60.0522 | 72.9812 | 62.3458 | 34.4173 | 30.9783 | 32.096 | 34.6065 | 31.3143
242.7491 | 132.7491 | 311.3011 | 60.275 | 73.3108 | 62.5607 | 34.5088 | 30.9895 | 32.1485 | 34.6962 | 31.3501
243.7505 | 133.7505 | 310.7501 | 60.5005 | 73.5849 | 62.7971 | 34.5938 | 31.0586 | 32.2015 | 34.7751 | 31.4168
244.7519 | 134.7519 | 310.2517 | 60.6995 | 73.9111 | 63.022 | 34.6859 | 31.0983 | 32.2627 | 34.8598 | 31.4522
245.7534 | 135.7534 | 309.7824 | 60.9303 | 74.2139 | 63.2374 | 34.7787 | 31.1169 | 32.3195 | 34.953 | 31.503
246.7548 | 136.7548 | 309.2874 | 61.1442 | 74.4961 | 63.4582 | 34.8592 | 31.1585 | 32.3759 | 35.0382 | 31.5636
247.7563 | 137.7563 | 308.8223 | 61.363 | 74.78 | 63.6796 | 34.952 | 31.2227 | 32.4386 | 35.1119 | 31.6195
248.7477 | 138.7477 | 308.3976 | 61.5875 | 75.072 | 63.9102 | 35.0482 | 31.26 | 32.5027 | 35.2001 | 31.6653
249.7491 | 139.7491 | 307.9509 | 61.8057 | 75.3842 | 64.1246 | 35.1334 | 31.2776 | 32.5547 | 35.2743 | 31.7259
250.7506 | 140.7506 | 307.4804 | 62.0182 | 75.6912 | 64.3347 | 35.2232 | 31.3479 | 32.6195 | 35.3739 | 31.7663
251.752 | 141.752 | 307.1048 | 62.2157 | 75.9736 | 64.5604 | 35.3234 | 31.3911 | 32.6758 | 35.4574 | 31.8412
252.7534 | 142.7534 | 306.6951 | 62.4218 | 76.2602 | 64.7783 | 35.4156 | 31.4156 | 32.7324 | 35.5529 | 31.8668
253.7549 | 143.7549 | 306.3163 | 62.6296 | 76.5382 | 64.9798 | 35.4951 | 31.4719 | 32.7975 | 35.6384 | 31.9287
254.7463 | 144.7463 | 305.8053 | 62.8542 | 76.8192 | 65.197 | 35.5924 | 31.5238 | 32.8567 | 35.7262 | 31.9839
255.7578 | 145.7578 | 305.2726 | 63.0355 | 77.1052 | 65.4053 | 35.6922 | 31.5702 | 32.9203 | 35.8221 | 32.0373
256.7492 | 146.7492 | 304.7877 | 63.2519 | 77.3698 | 65.6374 | 35.7921 | 31.594 | 32.9826 | 35.8966 | 32.0972
257.7506 | 147.7506 | 304.2296 | 63.4455 | 77.6727 | 65.8445 | 35.879 | 31.6582 | 33.0467 | 35.9797 | 32.1682
258.7521 | 148.7521 | 303.6618 | 63.6568 | 77.9662 | 66.0578 | 35.9707 | 31.7083 | 33.1049 | 36.0875 | 32.1877
259.7535 | 149.7535 | 303.2092 | 63.8615 | 78.1863 | 66.2627 | 36.0698 | 31.7284 | 33.1649 | 36.155 | 32.2604
260.7549 | 150.7549 | 302.8658 | 64.0564 | 78.476 | 66.4935 | 36.1654 | 31.7871 | 33.2357 | 36.2604 | 32.3
261.7464 | 151.7464 | 302.4419 | 64.2611 | 78.7424 | 66.6741 | 36.2523 | 31.8481 | 33.3001 | 36.348 | 32.3584
262.7478 | 152.7478 | 301.8925 | 64.4747 | 79.0331 | 66.8794 | 36.35 | 31.8971 | 33.3617 | 36.4232 | 32.4269
263.7493 | 153.7493 | 301.4062 | 64.5165 | 79.3252 | 67.0052 | 36.4643 | 31.9479 | 33.4229 | 36.5135 | 32.4879
264.7507 | 154.7507 | 301.0123 | 64.7131 | 79.5495 | 67.2016 | 36.557 | 32.024 | 33.4896 | 36.6177 | 32.5223
265.7521 | 155.7521 | 300.6452 | 64.8951 | 79.7896 | 67.3983 | 36.6599 | 32.0694 | 33.5593 | 36.7073 | 32.5688
266.7536 | 156.7536 | 300.1399 | 65.0775 | 80.058 | 67.6129 | 36.7555 | 32.1012 | 33.6175 | 36.7857 | 32.6559
267.755 | 157.755 | 299.6072 | 65.2869 | 80.3223 | 67.8058 | 36.8478 | 32.1654 | 33.6829 | 36.8889 | 32.7044
268.7464 | 158.7464 | 299.1274 | 65.4468 | 80.5818 | 67.9968 | 36.9575 | 32.2341 | 33.7517 | 36.9789 | 32.7705
269.7479 | 159.7479 | 298.6908 | 65.6949 | 80.8202 | 68.2119 | 37.0537 | 32.2786 | 33.8193 | 37.0561 | 32.8367
270.7493 | 160.7493 | 298.2715 | 65.8537 | 81.0819 | 68.4027 | 37.1375 | 32.3164 | 33.8812 | 37.154 | 32.8743
271.7508 | 161.7508 | 297.7982 | 66.0635 | 81.3333 | 68.5983 | 37.2582 | 32.3815 | 33.9504 | 37.2599 | 32.9234
272.7522 | 162.7522 | 297.305 | 66.2331 | 81.5829 | 68.7937 | 37.3453 | 32.4439 | 34.0165 | 37.3538 | 32.9891
273.7536 | 163.7536 | 296.9406 | 66.4456 | 81.8502 | 68.9835 | 37.4384 | 32.4666 | 34.0878 | 37.4592 | 33.0197
274.7551 | 164.7551 | 296.6286 | 66.6268 | 82.0817 | 69.1671 | 37.5349 | 32.5256 | 34.155 | 37.5375 | 33.1007
275.7465 | 165.7465 | 296.2467 | 66.8177 | 82.3334 | 69.3564 | 37.6513 | 32.5909 | 34.2232 | 37.6308 | 33.1531
276.7479 | 166.7479 | 295.8427 | 66.9845 | 82.5968 | 69.5369 | 37.7387 | 32.643 | 34.2968 | 37.7165 | 33.22
277.7494 | 167.7494 | 295.4138 | 67.1856 | 82.8415 | 69.7259 | 37.8416 | 32.678 | 34.3556 | 37.8243 | 33.2417
278.7508 | 168.7508 | 295.0744 | 67.3794 | 83.0853 | 69.924 | 37.9389 | 32.7551 | 34.4205 | 37.919 | 33.3146
279.7523 | 169.7523 | 294.9113 | 67.5606 | 83.3324 | 70.1148 | 38.0426 | 32.8042 | 34.4929 | 37.9963 | 33.3744
280.7537 | 170.7537 | 294.7324 | 67.7348 | 83.5785 | 70.3014 | 38.1349 | 32.8402 | 34.5618 | 38.093 | 33.4442
281.7551 | 171.7551 | 294.6459 | 67.9456 | 83.8339 | 70.5007 | 38.2371 | 32.9085 | 34.6314 | 38.1938 | 33.4918
282.7566 | 172.7566 | 294.7586 | 68.1211 | 84.0939 | 70.6846 | 38.3457 | 32.9702 | 34.7022 | 38.2931 | 33.546
283.748 | 173.748 | 294.9551 | 68.311 | 84.3456 | 70.8819 | 38.4517 | 33.032 | 34.7708 | 38.3729 | 33.6199
284.7494 | 174.7494 | 295.0446 | 68.4974 | 84.5925 | 71.0698 | 38.5328 | 33.0638 | 34.8457 | 38.4676 | 33.6794
285.7509 | 175.7509 | 295.2115 | 68.686 | 84.8579 | 71.255 | 38.6393 | 33.1481 | 34.9175 | 38.5747 | 33.7322
286.7523 | 176.7523 | 295.4983 | 68.8816 | 85.0819 | 71.4419 | 38.7534 | 33.1979 | 34.9894 | 38.6539 | 33.8096
287.7538 | 177.7538 | 295.8398 | 69.0713 | 85.342 | 71.6396 | 38.8671 | 33.2397 | 35.0636 | 38.7386 | 33.8677
288.7552 | 178.7552 | 296.208 | 69.2603 | 85.5716 | 71.8185 | 38.9602 | 33.2993 | 35.1292 | 38.8464 | 33.9053
289.7466 | 179.7466 | 296.4631 | 69.4376 | 85.8555 | 72.0081 | 39.0659 | 33.369 | 35.2007 | 38.9416 | 33.9812
290.7481 | 180.7481 | 296.7918 | 69.6487 | 86.1229 | 72.2213 | 39.1673 | 33.4341 | 35.2725 | 39.0441 | 34.0121
291.7495 | 181.7495 | 297.1841 | 69.8363 | 86.3774 | 72.4218 | 39.2692 | 33.4633 | 35.3449 | 39.1227 | 34.0951
292.751 | 182.751 | 297.6161 | 70.0353 | 86.6412 | 72.6126 | 39.3723 | 33.5491 | 35.4173 | 39.2375 | 34.1395
293.7524 | 183.7524 | 297.963 | 70.2434 | 86.8859 | 72.8257 | 39.4743 | 33.6104 | 35.4918 | 39.3094 | 34.2237
294.7538 | 184.7538 | 298.392 | 70.425 | 87.1465 | 73.0068 | 39.5744 | 33.6414 | 35.5685 | 39.4094 | 34.2764
295.7553 | 185.7553 | 298.865 | 70.6099 | 87.4121 | 73.2115 | 39.6745 | 33.7152 | 35.6415 | 39.5142 | 34.3117
296.7467 | 186.7467 | 299.2487 | 70.8022 | 87.678 | 73.4164 | 39.778 | 33.7897 | 35.721 | 39.6021 | 34.4063
297.7481 | 187.7481 | 299.5826 | 71.0047 | 87.9336 | 73.621 | 39.8854 | 33.8474 | 35.7884 | 39.6867 | 34.4726
298.7496 | 188.7496 | 300.1534 | 71.1852 | 88.2034 | 73.8006 | 39.9897 | 33.8934 | 35.8648 | 39.7957 | 34.5023
299.751 | 189.751 | 300.6516 | 71.4093 | 88.4666 | 74.0149 | 40.0987 | 33.9712 | 35.9363 | 39.8995 | 34.5704
300.7525 | 190.7525 | 301.1318 | 71.6148 | 88.7472 | 74.2172 | 40.2098 | 34.0386 | 36.0106 | 39.9654 | 34.6537
301.7539 | 191.7539 | 301.6168 | 71.8015 | 89.0237 | 74.4337 | 40.301 | 34.0722 | 36.0858 | 40.0787 | 34.6852
302.7553 | 192.7553 | 302.0916 | 71.9953 | 89.2942 | 74.6447 | 40.4096 | 34.1505 | 36.1645 | 40.1647 | 34.7707
303.7468 | 193.7468 | 302.5126 | 72.2011 | 89.567 | 74.8417 | 40.5119 | 34.2248 | 36.2368 | 40.2819 | 34.7979
304.7482 | 194.7482 | 302.8952 | 72.4008 | 89.8253 | 75.0315 | 40.6107 | 34.2877 | 36.3184 | 40.3621 | 34.8902
305.7496 | 195.7496 | 303.4615 | 72.5967 | 90.0964 | 75.2275 | 40.7135 | 34.3267 | 36.3971 | 40.4668 | 34.958
306.7511 | 196.7511 | 304.0229 | 72.8341 | 90.3676 | 75.4447 | 40.8206 | 34.4138 | 36.4663 | 40.5594 | 35.001
307.7525 | 197.7525 | 304.438 | 73.0132 | 90.6462 | 75.6427 | 40.9287 | 34.4821 | 36.5438 | 40.6571 | 35.0781
308.754 | 198.754 | 304.795 | 73.2217 | 90.9606 | 75.8569 | 41.0313 | 34.5127 | 36.6255 | 40.7581 | 35.1279
309.7554 | 199.7554 | 305.191 | 73.4004 | 91.2061 | 76.0504 | 41.1455 | 34.5873 | 36.7023 | 40.8628 | 35.2006
310.7468 | 200.7468 | 305.5362 | 73.6069 | 91.4614 | 76.2756 | 41.2562 | 34.6684 | 36.7784 | 40.9606 | 35.2697
311.7483 | 201.7483 | 305.8552 | 73.7913 | 91.7271 | 76.476 | 41.3624 | 34.7388 | 36.8591 | 41.0638 | 35.308
312.7497 | 202.7497 | 306.1403 | 74.0027 | 92.0054 | 76.6822 | 41.4559 | 34.7729 | 36.9338 | 41.164 | 35.3825
313.7512 | 203.7512 | 306.3467 | 74.2007 | 92.3177 | 76.8837 | 41.5673 | 34.8689 | 37.0135 | 41.2808 | 35.4289
314.7526 | 204.7526 | 306.5647 | 74.4196 | 92.5551 | 77.0965 | 41.6736 | 34.9395 | 37.0943 | 41.3681 | 35.5009
315.754 | 205.754 | 306.912 | 74.624 | 92.8358 | 77.3028 | 41.7649 | 34.9773 | 37.1693 | 41.4659 | 35.5555
316.7555 | 206.7555 | 307.1179 | 74.8227 | 93.0876 | 77.4816 | 41.8974 | 35.0507 | 37.2543 | 41.5677 | 35.6366
317.7469 | 207.7469 | 307.2753 | 75.0282 | 93.3751 | 77.7103 | 41.9988 | 35.1289 | 37.3297 | 41.6798 | 35.6777
318.7483 | 208.7483 | 307.41 | 75.216 | 93.6397 | 77.9095 | 42.1024 | 35.1995 | 37.4055 | 41.7778 | 35.763
319.7498 | 209.7498 | 307.4986 | 75.4248 | 93.9007 | 78.12 | 42.2137 | 35.2379 | 37.4892 | 41.8816 | 35.8208
320.7512 | 210.7512 | 307.5514 | 75.6134 | 94.1825 | 78.321 | 42.3313 | 35.334 | 37.5702 | 41.9967 | 35.8591
321.7527 | 211.7527 | 307.4959 | 75.8208 | 94.4169 | 78.5237 | 42.433 | 35.4057 | 37.6499 | 42.0935 | 35.9286
322.7541 | 212.7541 | 307.4694 | 75.9945 | 94.694 | 78.7275 | 42.5387 | 35.4562 | 37.7306 | 42.1957 | 36.0032
323.7555 | 213.7555 | 307.375 | 76.2229 | 94.9545 | 78.9374 | 42.6488 | 35.5267 | 37.8164 | 42.2993 | 36.0573
324.747 | 214.747 | 307.2896 | 76.3994 | 95.2214 | 79.127 | 42.7706 | 35.6089 | 37.8914 | 42.3988 | 36.1427
325.7484 | 215.7484 | 307.2455 | 76.5992 | 95.494 | 79.3393 | 42.868 | 35.6767 | 37.9794 | 42.5055 | 36.2056
326.7498 | 216.7498 | 307.3077 | 76.8174 | 95.7478 | 79.5313 | 42.9866 | 35.7275 | 38.0665 | 42.6113 | 36.2622
327.7513 | 217.7513 | 307.3582 | 77.0134 | 96.0148 | 79.7416 | 43.0975 | 35.824 | 38.1443 | 42.7134 | 36.3438
328.7527 | 218.7527 | 307.3851 | 77.2202 | 96.2512 | 79.9458 | 43.2098 | 35.8853 | 38.2219 | 42.8088 | 36.4131
329.7542 | 219.7542 | 307.4084 | 77.3717 | 96.5417 | 80.1221 | 43.3194 | 35.9389 | 38.3129 | 42.9168 | 36.4647
330.7556 | 220.7556 | 307.4128 | 77.6009 | 96.7933 | 80.3372 | 43.418 | 36.0193 | 38.3904 | 43.0038 | 36.5578
331.747 | 221.747 | 307.2908 | 77.7708 | 97.0508 | 80.532 | 43.5522 | 36.1114 | 38.4769 | 43.127 | 36.5762
332.7485 | 222.7485 | 307.2188 | 78.0036 | 97.3102 | 80.734 | 43.6539 | 36.1777 | 38.5643 | 43.2253 | 36.6572
333.7499 | 223.7499 | 307.1826 | 78.1746 | 97.5736 | 80.9211 | 43.773 | 36.2299 | 38.6497 | 43.3226 | 36.7311
334.7513 | 224.7513 | 307.1646 | 78.374 | 97.8159 | 81.1236 | 43.8933 | 36.3225 | 38.74 | 43.4211 | 36.8177
335.7528 | 225.7528 | 307.1376 | 78.5805 | 98.0873 | 81.3145 | 43.9983 | 36.3926 | 38.8264 | 43.5365 | 36.869
336.7542 | 226.7542 | 307.1184 | 78.7537 | 98.3525 | 81.5077 | 44.1052 | 36.4495 | 38.9137 | 43.6363 | 36.9286
337.7457 | 227.7457 | 307.0344 | 78.9641 | 98.59 | 81.716 | 44.21 | 36.523 | 39.0014 | 43.742 | 37.0175
338.7471 | 228.7471 | 306.9679 | 79.1322 | 98.8423 | 81.8986 | 44.3391 | 36.627 | 39.085 | 43.83 | 37.0923
339.7485 | 229.7485 | 307.0059 | 79.3511 | 99.0986 | 82.1085 | 44.4406 | 36.6899 | 39.175 | 43.9329 | 37.1703
340.75 | 230.75 | 307.0507 | 79.5104 | 99.3714 | 82.297 | 44.5566 | 36.7444 | 39.2624 | 44.0496 | 37.2098
341.7514 | 231.7514 | 306.9671 | 79.7272 | 99.6244 | 82.4967 | 44.6872 | 36.8411 | 39.3524 | 44.1611 | 37.2558
342.7529 | 232.7529 | 306.818 | 79.9054 | 99.8656 | 82.6881 | 44.7994 | 36.9204 | 39.439 | 44.2658 | 37.3474
343.7543 | 233.7543 | 306.7304 | 80.0966 | 100.1225 | 82.8882 | 44.9042 | 36.9674 | 39.5321 | 44.3692 | 37.4185
344.7557 | 234.7557 | 306.6997 | 80.3005 | 100.3855 | 83.0732 | 45.0231 | 37.0514 | 39.6191 | 44.4575 | 37.5057
345.7472 | 235.7472 | 306.6918 | 80.4698 | 100.6546 | 83.2654 | 45.144 | 37.1471 | 39.7027 | 44.5829 | 37.5735
346.7486 | 236.7486 | 306.6992 | 80.6764 | 100.9019 | 83.4639 | 45.2534 | 37.2161 | 39.7925 | 44.6786 | 37.6504
347.75 | 237.75 | 306.5624 | 80.8558 | 101.1419 | 83.6613 | 45.3704 | 37.2758 | 39.8861 | 44.7878 | 37.7238
348.7515 | 238.7515 | 306.5423 | 81.076 | 101.3971 | 83.8468 | 45.4932 | 37.3784 | 39.9829 | 44.9004 | 37.7664
349.7529 | 239.7529 | 306.4844 | 81.2442 | 101.657 | 84.0305 | 45.6074 | 37.4593 | 40.0629 | 45.0063 | 37.8443
350.7544 | 240.7544 | 306.4773 | 81.4266 | 101.9264 | 84.2259 | 45.7196 | 37.505 | 40.1581 | 45.1152 | 37.9191
351.7558 | 241.7558 | 306.4324 | 81.6118 | 102.1652 | 84.4074 | 45.8309 | 37.5942 | 40.2471 | 45.2152 | 38.0029
352.7472 | 242.7472 | 306.4535 | 81.8094 | 102.4213 | 84.6154 | 45.9537 | 37.6882 | 40.3362 | 45.3357 | 38.0597
353.7487 | 243.7487 | 306.5317 | 81.9857 | 102.6618 | 84.8022 | 46.0664 | 37.7669 | 40.4271 | 45.435 | 38.1394
354.7501 | 244.7501 | 306.5016 | 82.1749 | 102.9183 | 84.9922 | 46.1769 | 37.819 | 40.5145 | 45.5419 | 38.2084
355.7515 | 245.7515 | 306.4661 | 82.3839 | 103.173 | 85.1826 | 46.302 | 37.9258 | 40.6117 | 45.6577 | 38.2748
356.753 | 246.753 | 306.5146 | 82.5671 | 103.3956 | 85.3724 | 46.4168 | 38.0003 | 40.697 | 45.775 | 38.3507
357.7544 | 247.7544 | 306.4497 | 82.7529 | 103.652 | 85.5699 | 46.5459 | 38.0606 | 40.7853 | 45.8699 | 38.4331
358.7459 | 248.7459 | 306.3684 | 82.9173 | 103.9095 | 85.756 | 46.6483 | 38.1455 | 40.8762 | 45.9934 | 38.4935
359.7473 | 249.7473 | 306.2446 | 83.1056 | 104.1453 | 85.9468 | 46.7753 | 38.2389 | 40.968 | 46.1024 | 38.5645
360.7487 | 250.7487 | 306.1697 | 83.312 | 104.3994 | 86.1432 | 46.8922 | 38.3223 | 41.0613 | 46.217 | 38.6348
361.7502 | 251.7502 | 306.1148 | 83.4922 | 104.6345 | 86.3352 | 47.0015 | 38.3745 | 41.1541 | 46.3168 | 38.7259
362.7516 | 252.7516 | 306.1131 | 83.6704 | 104.9005 | 86.5357 | 47.1109 | 38.4866 | 41.2431 | 46.4371 | 38.7862
363.7531 | 253.7531 | 306.1301 | 83.8743 | 105.1519 | 86.7154 | 47.2445 | 38.5724 | 41.338 | 46.5395 | 38.8503
364.7545 | 254.7545 | 306.1369 | 84.0391 | 105.3885 | 86.9053 | 47.3656 | 38.6305 | 41.4334 | 46.653 | 38.9249
365.7559 | 255.7559 | 305.9999 | 84.2186 | 105.6273 | 87.098 | 47.4851 | 38.7273 | 41.5298 | 46.7557 | 39.0079
366.7574 | 256.7574 | 305.868 | 84.4186 | 105.8735 | 87.2819 | 47.6007 | 38.8215 | 41.6259 | 46.8805 | 39.0755
367.7488 | 257.7488 | 305.7929 | 84.5837 | 106.1137 | 87.4541 | 47.7234 | 38.9025 | 41.715 | 46.9926 | 39.1354
368.7502 | 258.7502 | 305.6496 | 84.7835 | 106.3509 | 87.6437 | 47.8509 | 38.953 | 41.8157 | 47.0912 | 39.2254
369.7517 | 259.7517 | 305.6659 | 84.9747 | 106.5797 | 87.8349 | 47.9635 | 39.0674 | 41.9069 | 47.1994 | 39.3045
370.7531 | 260.7531 | 305.6914 | 85.1293 | 106.8304 | 88.0282 | 48.0885 | 39.1522 | 42.0044 | 47.3115 | 39.3576
371.7546 | 261.7546 | 305.6637 | 85.3101 | 107.0782 | 88.2065 | 48.2049 | 39.2211 | 42.1037 | 47.4143 | 39.46
372.756 | 262.756 | 305.6194 | 85.5054 | 107.3059 | 88.4015 | 48.3295 | 39.3015 | 42.2 | 47.5222 | 39.5164
373.7474 | 263.7474 | 305.5335 | 85.7044 | 107.5565 | 88.5754 | 48.4635 | 39.4074 | 42.2931 | 47.6191 | 39.6202
374.7489 | 264.7489 | 305.5478 | 85.8894 | 107.7941 | 88.7541 | 48.5791 | 39.4875 | 42.3981 | 47.7481 | 39.6706
375.7503 | 265.7503 | 305.5754 | 86.0446 | 108.0278 | 88.9379 | 48.7011 | 39.5509 | 42.4898 | 47.8644 | 39.755
376.7517 | 266.7517 | 305.6911 | 86.2599 | 108.2538 | 89.1382 | 48.8073 | 39.6645 | 42.5886 | 47.9808 | 39.8185
377.7532 | 267.7532 | 305.7874 | 86.4358 | 108.5095 | 89.3184 | 48.9444 | 39.745 | 42.6854 | 48.0899 | 39.8866
378.7546 | 268.7546 | 305.7693 | 86.6047 | 108.7285 | 89.5007 | 49.0719 | 39.8075 | 42.781 | 48.1953 | 39.9817
379.746 | 269.746 | 305.6707 | 86.7872 | 108.9664 | 89.6811 | 49.194 | 39.9026 | 42.8803 | 48.3006 | 40.0512
380.7475 | 270.7475 | 305.5789 | 86.9698 | 109.2078 | 89.8688 | 49.3093 | 40.0022 | 42.9843 | 48.4136 | 40.1333
381.7489 | 271.7489 | 305.4594 | 87.1519 | 109.4474 | 90.06 | 49.4236 | 40.0899 | 43.0813 | 48.5331 | 40.1993
382.7504 | 272.7504 | 305.5007 | 87.3124 | 109.706 | 90.2432 | 49.5541 | 40.154 | 43.1831 | 48.6391 | 40.2629
383.7518 | 273.7518 | 305.557 | 87.519 | 109.9233 | 90.4402 | 49.6813 | 40.2686 | 43.2801 | 48.7258 | 40.3859
384.7532 | 274.7532 | 305.5753 | 87.6772 | 110.1728 | 90.6075 | 49.8029 | 40.3623 | 43.3848 | 48.8544 | 40.4315
385.7847 | 275.7847 | 305.5943 | 87.8747 | 110.4046 | 90.8082 | 49.9282 | 40.4284 | 43.4834 | 48.9648 | 40.5224
386.7461 | 276.7461 | 305.5682 | 88.0382 | 110.6283 | 90.9639 | 50.0478 | 40.5165 | 43.5807 | 49.0717 | 40.6014
387.7476 | 277.7476 | 305.6556 | 88.2322 | 110.8598 | 91.162 | 50.1594 | 40.6211 | 43.6825 | 49.1803 | 40.6856
388.749 | 278.749 | 305.656 | 88.4024 | 111.1001 | 91.34 | 50.297 | 40.7054 | 43.787 | 49.2856 | 40.7744
389.7504 | 279.7504 | 305.5988 | 88.5883 | 111.3377 | 91.5172 | 50.4131 | 40.7703 | 43.8882 | 49.4092 | 40.8178
390.7519 | 280.7519 | 305.6051 | 88.7786 | 111.5723 | 91.7106 | 50.5245 | 40.8825 | 43.9892 | 49.5026 | 40.9247
391.7533 | 281.7533 | 305.7911 | 88.943 | 111.7958 | 91.8889 | 50.67 | 40.9774 | 44.0927 | 49.6169 | 40.9956
392.7548 | 282.7548 | 305.8929 | 89.1188 | 112.0383 | 92.0817 | 50.7787 | 41.0408 | 44.1919 | 49.7319 | 41.069
393.7562 | 283.7562 | 305.9424 | 89.3086 | 112.2627 | 92.2442 | 50.9035 | 41.1366 | 44.2989 | 49.8409 | 41.1273
394.7476 | 284.7476 | 305.9724 | 89.467 | 112.4993 | 92.4192 | 51.034 | 41.2422 | 44.3984 | 49.9393 | 41.2459
395.7491 | 285.7491 | 305.9061 | 89.6234 | 112.7296 | 92.5934 | 51.1568 | 41.3324 | 44.499 | 50.0492 | 41.3236
396.7505 | 286.7505 | 305.8062 | 89.8332 | 112.9572 | 92.7916 | 51.2768 | 41.3954 | 44.6067 | 50.1578 | 41.3866
397.7519 | 287.7519 | 305.8169 | 90.0239 | 113.1892 | 92.9758 | 51.3964 | 41.5119 | 44.7094 | 50.2585 | 41.494
398.7534 | 288.7534 | 305.8821 | 90.2119 | 113.4327 | 93.1591 | 51.5238 | 41.6096 | 44.8207 | 50.3746 | 41.5379
399.7548 | 289.7548 | 305.8969 | 90.3886 | 113.6365 | 93.3305 | 51.6439 | 41.6736 | 44.9138 | 50.474 | 41.65
400.7563 | 290.7563 | 305.8146 | 90.5414 | 113.8808 | 93.5148 | 51.7863 | 41.7685 | 45.0201 | 50.5897 | 41.7258
401.7477 | 291.7477 | 305.7407 | 90.7298 | 114.1218 | 93.7009 | 51.8939 | 41.8825 | 45.1319 | 50.6955 | 41.8075
402.7491 | 292.7491 | 305.7824 | 90.8928 | 114.3578 | 93.8698 | 52.0253 | 41.9778 | 45.231 | 50.7978 | 41.8929
403.7506 | 293.7506 | 305.8367 | 91.098 | 114.5818 | 94.0579 | 52.1445 | 42.0423 | 45.3354 | 50.9171 | 41.9685
404.752 | 294.752 | 305.9251 | 91.2545 | 114.8112 | 94.2309 | 52.2864 | 42.1711 | 45.4515 | 51.0251 | 42.0491
405.7534 | 295.7534 | 306.0242 | 91.4634 | 115.0436 | 94.416 | 52.3886 | 42.2511 | 45.5504 | 51.1217 | 42.1417
406.7549 | 296.7549 | 306.0892 | 91.6273 | 115.2815 | 94.5886 | 52.5257 | 42.3308 | 45.66 | 51.2493 | 42.2033
407.7463 | 297.7463 | 306.184 | 91.8034 | 115.5073 | 94.7666 | 52.6483 | 42.4211 | 45.768 | 51.3372 | 42.3069
408.7578 | 298.7578 | 306.2865 | 91.9682 | 115.7432 | 94.9399 | 52.7805 | 42.536 | 45.8737 | 51.4699 | 42.3924
409.7492 | 299.7492 | 306.4394 | 92.154 | 115.9704 | 95.1465 | 52.9068 | 42.6283 | 45.9802 | 51.5665 | 42.4803
410.7506 | 300.7506 | 306.5148 | 92.3326 | 116.1962 | 95.3138 | 53.0354 | 42.6912 | 46.0879 | 51.6878 | 42.5567
411.7521 | 301.7521 | 306.5361 | 92.4964 | 116.4282 | 95.476 | 53.1597 | 42.8202 | 46.1972 | 51.8062 | 42.625
412.7535 | 302.7535 | 306.6758 | 92.6817 | 116.6456 | 95.6828 | 53.2852 | 42.9094 | 46.3006 | 51.9109 | 42.7275
413.755 | 303.755 | 306.5928 | 92.8601 | 116.8661 | 95.8557 | 53.4067 | 42.9909 | 46.4025 | 52.0157 | 42.7985
414.7564 | 304.7564 | 306.5081 | 93.0361 | 117.0971 | 96.0269 | 53.5375 | 43.0834 | 46.5157 | 52.1359 | 42.8892
415.7478 | 305.7478 | 306.5085 | 93.2004 | 117.3325 | 96.2117 | 53.6804 | 43.2074 | 46.6171 | 52.2554 | 42.9751
416.7493 | 306.7493 | 306.6683 | 93.3802 | 117.5642 | 96.3817 | 53.791 | 43.2922 | 46.7357 | 52.3827 | 43.0327
417.7507 | 307.7507 | 306.7413 | 93.5583 | 117.7925 | 96.56 | 53.9236 | 43.3647 | 46.8407 | 52.4838 | 43.1301
418.7521 | 308.7521 | 306.7232 | 93.7364 | 118.0234 | 96.7531 | 54.0503 | 43.4833 | 46.951 | 52.6041 | 43.2061
419.7536 | 309.7536 | 306.8385 | 93.8913 | 118.2791 | 96.9195 | 54.173 | 43.5892 | 47.062 | 52.7158 | 43.2747
420.755 | 310.755 | 306.7903 | 94.094 | 118.4686 | 97.0919 | 54.3022 | 43.658 | 47.1661 | 52.827 | 43.3867
421.7464 | 311.7464 | 306.8098 | 94.2386 | 118.6899 | 97.2713 | 54.4219 | 43.7568 | 47.2801 | 52.9491 | 43.4571
422.7479 | 312.7479 | 306.8762 | 94.4306 | 118.9259 | 97.4263 | 54.5633 | 43.871 | 47.3866 | 53.0584 | 43.5486
423.7493 | 313.7493 | 306.9817 | 94.6072 | 119.1569 | 97.596 | 54.6902 | 43.9689 | 47.4963 | 53.1725 | 43.6219
424.7508 | 314.7508 | 306.9914 | 94.7862 | 119.3834 | 97.767 | 54.8105 | 44.0434 | 47.6032 | 53.3036 | 43.6964
425.7522 | 315.7522 | 306.9585 | 94.9682 | 119.5987 | 97.965 | 54.9377 | 44.1648 | 47.7125 | 53.4136 | 43.7885
426.7536 | 316.7536 | 306.9862 | 95.1273 | 119.8203 | 98.1372 | 55.0566 | 44.2689 | 47.8195 | 53.5294 | 43.8606
427.7551 | 317.7551 | 306.9715 | 95.3219 | 120.0711 | 98.322 | 55.1947 | 44.336 | 47.9263 | 53.6496 | 43.9464
428.7465 | 318.7465 | 307.0303 | 95.4872 | 120.2762 | 98.5018 | 55.3201 | 44.4432 | 48.0358 | 53.7725 | 44.0255
429.7479 | 319.7479 | 306.9342 | 95.6672 | 120.4892 | 98.6837 | 55.453 | 44.5581 | 48.1418 | 53.8873 | 44.1095
430.7494 | 320.7494 | 306.8171 | 95.8268 | 120.723 | 98.8604 | 55.583 | 44.6615 | 48.2541 | 54.0015 | 44.2152
431.7508 | 321.7508 | 306.6834 | 95.9993 | 120.9355 | 99.0429 | 55.7022 | 44.7335 | 48.372 | 54.1305 | 44.2759
432.7523 | 322.7523 | 306.5953 | 96.183 | 121.1567 | 99.1994 | 55.8327 | 44.8566 | 48.4858 | 54.2352 | 44.3793
433.7537 | 323.7537 | 306.5376 | 96.3456 | 121.3687 | 99.3845 | 55.9619 | 44.9497 | 48.5914 | 54.3597 | 44.4404
434.7551 | 324.7551 | 306.4673 | 96.5181 | 121.5952 | 99.5681 | 56.0933 | 45.0301 | 48.7097 | 54.4725 | 44.5396
435.7466 | 325.7466 | 306.5107 | 96.6683 | 121.8241 | 99.7287 | 56.2258 | 45.1299 | 48.8136 | 54.5749 | 44.6373
436.748 | 326.748 | 306.5563 | 96.8594 | 122.0442 | 99.907 | 56.3498 | 45.2537 | 48.9195 | 54.7022 | 44.7036
437.7495 | 327.7495 | 306.5142 | 97.0244 | 122.2557 | 100.0663 | 56.4867 | 45.3572 | 49.0366 | 54.8171 | 44.7824
438.7509 | 328.7509 | 306.528 | 97.2003 | 122.4557 | 100.2498 | 56.6125 | 45.4225 | 49.1496 | 54.93 | 44.888
439.7523 | 329.7523 | 306.5616 | 97.3487 | 122.693 | 100.4068 | 56.7517 | 45.5587 | 49.257 | 55.0421 | 44.9721
440.7538 | 330.7538 | 306.5733 | 97.538 | 122.9138 | 100.5948 | 56.8735 | 45.6527 | 49.3783 | 55.1677 | 45.0585
441.7552 | 331.7552 | 306.5217 | 97.6964 | 123.1283 | 100.7711 | 56.9989 | 45.7322 | 49.4881 | 55.2859 | 45.1519
442.7466 | 332.7466 | 306.5137 | 97.8839 | 123.3475 | 100.9383 | 57.1289 | 45.8312 | 49.6007 | 55.4084 | 45.2236
443.7481 | 333.7481 | 306.5808 | 98.0379 | 123.5646 | 101.1092 | 57.2539 | 45.9578 | 49.7031 | 55.5374 | 45.304
444.7495 | 334.7495 | 306.6168 | 98.2044 | 123.7775 | 101.2767 | 57.3765 | 46.0521 | 49.8161 | 55.6536 | 45.3909
445.751 | 335.751 | 306.4912 | 98.3817 | 123.9882 | 101.468 | 57.5069 | 46.1307 | 49.9341 | 55.7704 | 45.478
446.7524 | 336.7524 | 306.3689 | 98.5415 | 124.2157 | 101.6213 | 57.6496 | 46.2633 | 50.0427 | 55.8962 | 45.5508
447.7538 | 337.7538 | 306.2034 | 98.7134 | 124.4117 | 101.803 | 57.7839 | 46.3583 | 50.147 | 56.0127 | 45.6466
448.7553 | 338.7553 | 306.0865 | 98.8664 | 124.6364 | 101.9604 | 57.9189 | 46.4496 | 50.2664 | 56.1298 | 45.7388
449.7467 | 339.7467 | 306.0063 | 99.0684 | 124.8561 | 102.1296 | 58.0421 | 46.55 | 50.3844 | 56.2457 | 45.8172
450.7481 | 340.7481 | 305.9407 | 99.2237 | 125.0648 | 102.3086 | 58.1752 | 46.6706 | 50.4914 | 56.3554 | 45.9251
451.7496 | 341.7496 | 305.8793 | 99.3901 | 125.2814 | 102.4693 | 58.3034 | 46.769 | 50.6064 | 56.4856 | 45.9809
452.751 | 342.751 | 305.8277 | 99.5323 | 125.4852 | 102.63 | 58.4398 | 46.8479 | 50.7205 | 56.5958 | 46.0705
453.7525 | 343.7525 | 305.7238 | 99.7599 | 125.7 | 102.8095 | 58.5686 | 46.97 | 50.8316 | 56.7129 | 46.1718
454.7539 | 344.7539 | 305.6523 | 99.9341 | 125.9013 | 102.9801 | 58.6936 | 47.0674 | 50.9523 | 56.8325 | 46.2388
455.7553 | 345.7553 | 305.6184 | 100.0726 | 126.125 | 103.1429 | 58.8262 | 47.1553 | 51.0624 | 56.9373 | 46.35
456.7568 | 346.7568 | 305.6304 | 100.2228 | 126.3284 | 103.3102 | 58.9577 | 47.2639 | 51.176 | 57.0609 | 46.4338
457.7482 | 347.7482 | 305.6037 | 100.404 | 126.5475 | 103.4823 | 59.0924 | 47.3863 | 51.293 | 57.1844 | 46.5091
458.7496 | 348.7496 | 305.5602 | 100.5863 | 126.7438 | 103.6534 | 59.2208 | 47.4869 | 51.404 | 57.2956 | 46.6055
459.7511 | 349.7511 | 305.5125 | 100.7013 | 126.9609 | 103.8076 | 59.3542 | 47.581 | 51.5294 | 57.421 | 46.6901
460.7525 | 350.7525 | 305.4836 | 100.8757 | 127.1673 | 103.9815 | 59.4699 | 47.6998 | 51.6392 | 57.54 | 46.771
461.754 | 351.754 | 305.5451 | 101.0492 | 127.3858 | 104.1239 | 59.6131 | 47.8153 | 51.755 | 57.6523 | 46.8739
462.7554 | 352.7554 | 305.5966 | 101.209 | 127.5991 | 104.2936 | 59.7467 | 47.8966 | 51.8717 | 57.7671 | 46.964
463.7468 | 353.7468 | 305.6634 | 101.3628 | 127.7963 | 104.4709 | 59.8784 | 48.0007 | 51.9868 | 57.8837 | 47.0503
464.7483 | 354.7483 | 305.771 | 101.5229 | 128.0083 | 104.6359 | 60.0162 | 48.1406 | 52.113 | 57.994 | 47.1515
465.7497 | 355.7497 | 305.745 | 101.7166 | 128.2149 | 104.8109 | 60.1422 | 48.235 | 52.2286 | 58.1143 | 47.2325
466.7512 | 356.7512 | 305.7088 | 101.8467 | 128.4213 | 104.9549 | 60.2827 | 48.324 | 52.3446 | 58.2398 | 47.3146
467.7526 | 357.7526 | 305.714 | 102.0325 | 128.6318 | 105.1399 | 60.4107 | 48.451 | 52.456 | 58.3462 | 47.4305
468.754 | 358.754 | 305.7484 | 102.1686 | 128.8478 | 105.2994 | 60.532 | 48.5643 | 52.5767 | 58.4696 | 47.5027
469.7555 | 359.7555 | 305.7254 | 102.3591 | 129.0495 | 105.4674 | 60.6637 | 48.6437 | 52.6946 | 58.5952 | 47.5918
470.7469 | 360.7469 | 305.7797 | 102.4979 | 129.2453 | 105.6268 | 60.8052 | 48.7538 | 52.8132 | 58.7021 | 47.6881
471.7483 | 361.7483 | 305.8661 | 102.6657 | 129.4648 | 105.7913 | 60.9403 | 48.8787 | 52.9253 | 58.8366 | 47.7647
472.7498 | 362.7498 | 305.9659 | 102.845 | 129.663 | 105.9614 | 61.0718 | 48.9796 | 53.0447 | 58.9553 | 47.8732
473.7512 | 363.7512 | 305.9598 | 102.9981 | 129.8798 | 106.1327 | 61.1922 | 49.0597 | 53.1651 | 59.0857 | 47.9305
474.7527 | 364.7527 | 305.9469 | 103.1838 | 130.078 | 106.306 | 61.3238 | 49.1915 | 53.2735 | 59.2103 | 48.0374
475.7541 | 365.7541 | 306.033 | 103.3122 | 130.2715 | 106.4587 | 61.4687 | 49.3073 | 53.3885 | 59.3238 | 48.1332
476.7555 | 366.7555 | 306.0972 | 103.5021 | 130.4707 | 106.6276 | 61.5939 | 49.3921 | 53.5082 | 59.4568 | 48.2125
477.747 | 367.747 | 306.1126 | 103.6323 | 130.6949 | 106.794 | 61.7459 | 49.5033 | 53.6262 | 59.565 | 48.3177
478.7484 | 368.7484 | 306.0771 | 103.8262 | 130.8924 | 106.9642 | 61.8603 | 49.6171 | 53.7415 | 59.7163 | 48.3583
479.7498 | 369.7498 | 306.0078 | 103.9541 | 131.0964 | 107.1153 | 62.0017 | 49.7297 | 53.8516 | 59.8226 | 48.4812
480.7513 | 370.7513 | 305.8599 | 104.1347 | 131.3097 | 107.29 | 62.1308 | 49.808 | 53.9665 | 59.9553 | 48.5539
481.7527 | 371.7527 | 305.7678 | 104.2887 | 131.5039 | 107.4403 | 62.2611 | 49.9446 | 54.0844 | 60.0719 | 48.6648
482.7542 | 372.7542 | 305.7145 | 104.451 | 131.6991 | 107.5941 | 62.4001 | 50.0547 | 54.2034 | 60.1953 | 48.7451
483.7556 | 373.7556 | 305.6298 | 104.6384 | 131.9043 | 107.7599 | 62.527 | 50.1383 | 54.3251 | 60.3184 | 48.8304
484.747 | 374.747 | 305.5002 | 104.7659 | 132.0942 | 107.9183 | 62.6517 | 50.2543 | 54.4394 | 60.439 | 48.9111
485.7485 | 375.7485 | 305.518 | 104.9484 | 132.301 | 108.0835 | 62.7909 | 50.3787 | 54.5524 | 60.5617 | 49.0337
486.7499 | 376.7499 | 305.4445 | 105.0858 | 132.5021 | 108.2309 | 62.9234 | 50.4975 | 54.6705 | 60.6861 | 49.092
487.7514 | 377.7514 | 305.3867 | 105.2562 | 132.6987 | 108.4047 | 63.0545 | 50.5712 | 54.7921 | 60.8154 | 49.1919
488.7528 | 378.7528 | 305.2036 | 105.389 | 132.906 | 108.5595 | 63.1985 | 50.7107 | 54.9071 | 60.9319 | 49.2946
489.7542 | 379.7542 | 305.1265 | 105.5785 | 133.0991 | 108.7251 | 63.3293 | 50.8151 | 55.0209 | 61.0456 | 49.3852
490.7457 | 380.7457 | 305.1654 | 105.7291 | 133.3062 | 108.8816 | 63.4489 | 50.9029 | 55.1332 | 61.1721 | 49.4698
491.7471 | 381.7471 | 305.2648 | 105.8761 | 133.5004 | 109.0476 | 63.5833 | 51.0171 | 55.2551 | 61.2868 | 49.576
492.7485 | 382.7485 | 305.3183 | 106.0489 | 133.7038 | 109.2155 | 63.7167 | 51.1359 | 55.3711 | 61.4238 | 49.6387
493.75 | 383.75 | 305.3316 | 106.1813 | 133.898 | 109.3636 | 63.857 | 51.2593 | 55.487 | 61.5465 | 49.7571
494.7514 | 384.7514 | 305.4205 | 106.3765 | 134.1039 | 109.5328 | 63.9945 | 51.3345 | 55.6148 | 61.6638 | 49.834
495.7529 | 385.7529 | 305.4839 | 106.4943 | 134.3113 | 109.6851 | 64.1326 | 51.482 | 55.7279 | 61.8036 | 49.9126
496.7543 | 386.7543 | 305.4803 | 106.6874 | 134.4967 | 109.8631 | 64.2626 | 51.5789 | 55.8425 | 61.9137 | 50.0197
497.7557 | 387.7557 | 305.5116 | 106.8259 | 134.6952 | 110.0064 | 64.3943 | 51.6714 | 55.9633 | 62.0418 | 50.1176
498.7572 | 388.7572 | 305.4555 | 106.9939 | 134.8999 | 110.1836 | 64.5172 | 51.783 | 56.0751 | 62.1698 | 50.1991
499.7486 | 389.7486 | 305.4341 | 107.146 | 135.0915 | 110.3334 | 64.6665 | 51.9129 | 56.1945 | 62.2757 | 50.3103
500.75 | 390.75 | 305.3738 | 107.2808 | 135.2774 | 110.4909 | 64.803 | 52.0223 | 56.3152 | 62.4135 | 50.3648
501.7515 | 391.7515 | 305.3019 | 107.4665 | 135.4727 | 110.6549 | 64.9267 | 52.1027 | 56.4334 | 62.5447 | 50.4492
502.7529 | 392.7529 | 305.2366 | 107.5883 | 135.6834 | 110.8035 | 65.0585 | 52.2451 | 56.5532 | 62.6671 | 50.5475
503.7544 | 393.7544 | 305.2583 | 107.7744 | 135.8657 | 110.9835 | 65.192 | 52.3522 | 56.6673 | 62.7818 | 50.6482
504.7558 | 394.7558 | 305.2133 | 107.8822 | 136.0661 | 111.1168 | 65.3337 | 52.4453 | 56.7879 | 62.8885 | 50.7615
505.7472 | 395.7472 | 305.1258 | 108.0814 | 136.242 | 111.2832 | 65.4728 | 52.5529 | 56.9104 | 63.0249 | 50.8248
506.7487 | 396.7487 | 305.1289 | 108.2251 | 136.4349 | 111.4395 | 65.6032 | 52.6852 | 57.0345 | 63.1314 | 50.9461
507.7501 | 397.7501 | 305.0536 | 108.3816 | 136.6321 | 111.6049 | 65.7391 | 52.7977 | 57.1553 | 63.2487 | 51.0419
508.7515 | 398.7515 | 304.9897 | 108.5295 | 136.8277 | 111.756 | 65.8728 | 52.8849 | 57.2782 | 63.3808 | 51.107
509.753 | 399.753 | 304.9355 | 108.6992 | 137.0252 | 111.9014 | 66.0039 | 53.0234 | 57.4007 | 63.4938 | 51.217
510.7544 | 400.7544 | 304.8886 | 108.853 | 137.2182 | 112.0666 | 66.1479 | 53.1405 | 57.5228 | 63.6248 | 51.2899
511.7559 | 401.7559 | 304.9174 | 109.0042 | 137.3993 | 112.224 | 66.272 | 53.2205 | 57.6411 | 63.7347 | 51.3882
512.7473 | 402.7473 | 304.8667 | 109.1629 | 137.5971 | 112.3626 | 66.4132 | 53.342 | 57.7747 | 63.8586 | 51.4868
513.7487 | 403.7487 | 304.8246 | 109.311 | 137.7907 | 112.5195 | 66.5444 | 53.4776 | 57.8953 | 63.9586 | 51.601
514.7502 | 404.7502 | 304.759 | 109.4699 | 137.9836 | 112.6857 | 66.6865 | 53.5859 | 58.0102 | 64.0822 | 51.6969
515.7516 | 405.7516 | 304.7857 | 109.6149 | 138.1852 | 112.841 | 66.8098 | 53.6658 | 58.1374 | 64.2086 | 51.7807
516.7531 | 406.7531 | 304.9845 | 109.794 | 138.3676 | 112.9994 | 66.9612 | 53.8079 | 58.2598 | 64.3256 | 51.876
517.7545 | 407.7545 | 305.1376 | 109.9318 | 138.5588 | 113.1563 | 67.0879 | 53.9249 | 58.3871 | 64.447 | 51.9654
518.7459 | 408.7459 | 305.2143 | 110.0977 | 138.7326 | 113.3135 | 67.2276 | 54.0107 | 58.5086 | 64.5694 | 52.064
519.7474 | 409.7474 | 305.3517 | 110.2434 | 138.931 | 113.4693 | 67.3631 | 54.1338 | 58.6302 | 64.6824 | 52.1542
520.7488 | 410.7488 | 305.3747 | 110.4081 | 139.1208 | 113.6385 | 67.5083 | 54.2652 | 58.7521 | 64.7917 | 52.2728
521.7502 | 411.7502 | 305.311 | 110.5569 | 139.3175 | 113.7964 | 67.6494 | 54.3686 | 58.8772 | 64.9109 | 52.3616
522.7517 | 412.7517 | 305.3275 | 110.7043 | 139.5228 | 113.9372 | 67.7818 | 54.4584 | 59.0008 | 65.0307 | 52.4584
523.7531 | 413.7531 | 305.2625 | 110.8704 | 139.695 | 114.1104 | 67.9287 | 54.6041 | 59.1269 | 65.1568 | 52.5256
524.7546 | 414.7546 | 305.3714 | 111.0097 | 139.8837 | 114.2697 | 68.0666 | 54.724 | 59.2454 | 65.2568 | 52.6396
525.756 | 415.756 | 305.5262 | 111.1712 | 140.0827 | 114.4184 | 68.1912 | 54.8069 | 59.3736 | 65.3875 | 52.7346
526.7474 | 416.7474 | 305.5632 | 111.3029 | 140.2753 | 114.5625 | 68.3317 | 54.9317 | 59.4951 | 65.5166 | 52.8312
527.7489 | 417.7489 | 305.7259 | 111.4721 | 140.4669 | 114.7269 | 68.4581 | 55.0583 | 59.6161 | 65.6194 | 52.9498
528.7503 | 418.7503 | 305.8495 | 111.6025 | 140.6582 | 114.8715 | 68.6084 | 55.1751 | 59.7433 | 65.7356 | 53.0266
529.7517 | 419.7517 | 305.9791 | 111.7923 | 140.8467 | 115.0348 | 68.729 | 55.2596 | 59.8715 | 65.865 | 53.1121
530.7532 | 420.7532 | 306.0274 | 111.9224 | 141.0328 | 115.1754 | 68.8798 | 55.4007 | 59.9933 | 65.9857 | 53.21
531.7546 | 421.7546 | 306.1406 | 112.0749 | 141.224 | 115.3241 | 69.0077 | 55.5224 | 60.1181 | 66.1034 | 53.3183
532.7461 | 422.7461 | 306.2086 | 112.22 | 141.4088 | 115.4715 | 69.1476 | 55.6132 | 60.242 | 66.2294 | 53.4133
533.7475 | 423.7475 | 306.2698 | 112.4003 | 141.5933 | 115.6381 | 69.2908 | 55.7253 | 60.3645 | 66.3446 | 53.5124
534.7489 | 424.7489 | 306.4233 | 112.5448 | 141.7869 | 115.7872 | 69.4254 | 55.8654 | 60.4822 | 66.4862 | 53.5911
535.7504 | 425.7504 | 306.5618 | 112.683 | 141.9707 | 115.9451 | 69.5732 | 55.9802 | 60.6053 | 66.595 | 53.7129
536.7518 | 426.7518 | 306.6442 | 112.8483 | 142.1654 | 116.097 | 69.6981 | 56.0727 | 60.7303 | 66.7339 | 53.7717
537.7533 | 427.7533 | 306.6637 | 112.9978 | 142.355 | 116.2552 | 69.8369 | 56.2118 | 60.8493 | 66.8492 | 53.901
538.7547 | 428.7547 | 306.5521 | 113.1531 | 142.5382 | 116.413 | 69.9693 | 56.3213 | 60.9735 | 66.9821 | 53.9848
539.7561 | 429.7561 | 306.5441 | 113.3004 | 142.7179 | 116.5713 | 70.1202 | 56.4231 | 61.0893 | 67.1158 | 54.0422
540.7576 | 430.7576 | 306.515 | 113.4616 | 142.9031 | 116.7161 | 70.2474 | 56.5415 | 61.2166 | 67.2335 | 54.166
541.749 | 431.749 | 306.5714 | 113.6152 | 143.0742 | 116.8742 | 70.3942 | 56.6728 | 61.3465 | 67.3539 | 54.2546
542.7504 | 432.7504 | 306.5898 | 113.7425 | 143.2835 | 117.0184 | 70.5269 | 56.7865 | 61.4648 | 67.4786 | 54.3581
543.7519 | 433.7519 | 306.6172 | 113.917 | 143.4781 | 117.1771 | 70.6635 | 56.8799 | 61.5849 | 67.5953 | 54.4606
544.7533 | 434.7533 | 306.6084 | 114.0536 | 143.6567 | 117.3362 | 70.8031 | 57.0215 | 61.7104 | 67.7253 | 54.5457
545.7548 | 435.7548 | 306.5301 | 114.2061 | 143.8255 | 117.4867 | 70.9441 | 57.1394 | 61.8242 | 67.8393 | 54.664
546.7562 | 436.7562 | 306.4749 | 114.3632 | 144.0069 | 117.6436 | 71.0857 | 57.2331 | 61.9503 | 67.9752 | 54.7427
547.7476 | 437.7476 | 306.43 | 114.5162 | 144.1897 | 117.7889 | 71.2146 | 57.3563 | 62.0781 | 68.0994 | 54.8334
548.7491 | 438.7491 | 306.4788 | 114.6535 | 144.3702 | 117.9374 | 71.3445 | 57.492 | 62.2011 | 68.2082 | 54.9446
549.7505 | 439.7505 | 306.4862 | 114.8015 | 144.5607 | 118.0764 | 71.4918 | 57.6054 | 62.3246 | 68.3454 | 55.0349
550.7519 | 440.7519 | 306.4774 | 114.951 | 144.7396 | 118.2386 | 71.6217 | 57.7032 | 62.4493 | 68.4634 | 55.1173
551.7534 | 441.7534 | 306.4668 | 115.0985 | 144.926 | 118.3771 | 71.7701 | 57.8439 | 62.5666 | 68.6034 | 55.2096
552.7548 | 442.7548 | 306.3709 | 115.2489 | 145.081 | 118.5283 | 71.9039 | 57.9651 | 62.6946 | 68.7195 | 55.3242
553.7462 | 443.7462 | 306.2271 | 115.407 | 145.28 | 118.6972 | 72.0445 | 58.0573 | 62.8165 | 68.8543 | 55.4094
554.7477 | 444.7477 | 306.1339 | 115.5364 | 145.4597 | 118.85 | 72.19 | 58.1817 | 62.9423 | 68.9741 | 55.4872
555.7491 | 445.7491 | 306.1147 | 115.6946 | 145.6444 | 118.9953 | 72.3244 | 58.3143 | 63.0634 | 69.0947 | 55.6121
556.7506 | 446.7506 | 306.1795 | 115.8334 | 145.8259 | 119.1313 | 72.4732 | 58.4317 | 63.1891 | 69.2007 | 55.7145
557.752 | 447.752 | 306.0794 | 115.9819 | 146.0041 | 119.2746 | 72.6078 | 58.5222 | 63.3148 | 69.336 | 55.7804
558.7534 | 448.7534 | 306.0183 | 116.1326 | 146.1839 | 119.4289 | 72.7586 | 58.6719 | 63.4392 | 69.4407 | 55.9151
559.7549 | 449.7549 | 305.9846 | 116.2669 | 146.354 | 119.5676 | 72.8839 | 58.7897 | 63.5657 | 69.5581 | 55.9916
560.7463 | 450.7463 | 305.9315 | 116.4194 | 146.5176 | 119.7163 | 73.0185 | 58.8811 | 63.6973 | 69.6707 | 56.1031
561.7478 | 451.7478 | 305.8286 | 116.5632 | 146.6983 | 119.8611 | 73.1602 | 59.008 | 63.8259 | 69.8032 | 56.1909
562.7492 | 452.7492 | 305.8817 | 116.7303 | 146.8732 | 120.0163 | 73.2986 | 59.1444 | 63.9501 | 69.9153 | 56.3003
563.7506 | 453.7506 | 305.8556 | 116.8595 | 147.0647 | 120.1551 | 73.4446 | 59.2627 | 64.0815 | 70.0253 | 56.3892
564.7521 | 454.7521 | 305.9362 | 117.0098 | 147.2423 | 120.3048 | 73.5834 | 59.3548 | 64.2092 | 70.1536 | 56.4941
565.7535 | 455.7535 | 306.0273 | 117.1429 | 147.4212 | 120.4449 | 73.7181 | 59.5044 | 64.3343 | 70.2699 | 56.5872
566.755 | 456.755 | 306.0539 | 117.2982 | 147.5978 | 120.5926 | 73.8638 | 59.6208 | 64.4649 | 70.3809 | 56.6853
567.7564 | 457.7564 | 306.1102 | 117.4443 | 147.7757 | 120.7491 | 74.0021 | 59.7241 | 64.5938 | 70.4958 | 56.7835
568.7478 | 458.7478 | 306.1323 | 117.5915 | 147.9573 | 120.8974 | 74.145 | 59.8424 | 64.7224 | 70.6229 | 56.8854
569.7493 | 459.7493 | 306.1759 | 117.7337 | 148.1435 | 121.0492 | 74.2867 | 59.9791 | 64.8522 | 70.7529 | 56.9762
570.7507 | 460.7507 | 306.2627 | 117.8751 | 148.2928 | 121.2075 | 74.4266 | 60.0994 | 64.9739 | 70.8779 | 57.0746
571.7521 | 461.7521 | 306.3621 | 118.038 | 148.4882 | 121.3521 | 74.5587 | 60.1933 | 65.1014 | 70.9962 | 57.1697
572.7536 | 462.7536 | 306.4108 | 118.1657 | 148.6552 | 121.4854 | 74.6982 | 60.3392 | 65.2246 | 71.1168 | 57.2737
573.755 | 463.755 | 306.3626 | 118.32 | 148.8374 | 121.6314 | 74.8346 | 60.457 | 65.353 | 71.2472 | 57.3571
574.7464 | 464.7464 | 306.353 | 118.4622 | 149.0291 | 121.7814 | 74.9812 | 60.5532 | 65.4823 | 71.3761 | 57.4649
575.7479 | 465.7479 | 306.2655 | 118.6068 | 149.1814 | 121.9306 | 75.126 | 60.6766 | 65.6096 | 71.4985 | 57.547
576.7493 | 466.7493 | 306.157 | 118.7467 | 149.3691 | 122.0706 | 75.2519 | 60.8169 | 65.7366 | 71.6086 | 57.6827
577.7508 | 467.7508 | 306.1018 | 118.8871 | 149.4876 | 122.2038 | 75.4048 | 60.9305 | 65.8633 | 71.7305 | 57.7667
578.7522 | 468.7522 | 306.0789 | 119.0319 | 149.6993 | 122.3679 | 75.5388 | 61.0335 | 65.9926 | 71.8491 | 57.8821
579.7536 | 469.7536 | 306.1286 | 119.166 | 149.8688 | 122.5088 | 75.6894 | 61.1859 | 66.1152 | 71.9807 | 57.9643
580.7551 | 470.7551 | 306.1833 | 119.3239 | 150.0534 | 122.6479 | 75.8242 | 61.3004 | 66.2405 | 72.1047 | 58.0635
581.7565 | 471.7565 | 306.1554 | 119.4648 | 150.209 | 122.7788 | 75.9684 | 61.4012 | 66.3737 | 72.2217 | 58.157
582.748 | 472.748 | 306.0743 | 119.6041 | 150.3947 | 122.9222 | 76.0976 | 61.5236 | 66.5 | 72.319 | 58.2812
583.7494 | 473.7494 | 306.0467 | 119.7535 | 150.5707 | 123.0768 | 76.2428 | 61.6648 | 66.6323 | 72.4662 | 58.3734
584.7508 | 474.7508 | 305.9818 | 119.8966 | 150.711 | 123.2221 | 76.3823 | 61.7847 | 66.7621 | 72.5718 | 58.4722
585.7523 | 475.7523 | 305.9376 | 120.0397 | 150.9176 | 123.3859 | 76.5158 | 61.8781 | 66.8845 | 72.7017 | 58.5669
586.7537 | 476.7537 | 306.085 | 120.1589 | 151.0793 | 123.5383 | 76.6788 | 62.0336 | 67.0137 | 72.8176 | 58.6769
587.7552 | 477.7552 | 306.2689 | 120.3059 | 151.2567 | 123.6763 | 76.8143 | 62.1527 | 67.1372 | 72.9348 | 58.7743
588.7566 | 478.7566 | 306.3368 | 120.4453 | 151.4383 | 123.8062 | 76.9538 | 62.2588 | 67.2823 | 73.0697 | 58.8667
589.748 | 479.748 | 306.3679 | 120.6066 | 151.5872 | 123.9499 | 77.0967 | 62.3735 | 67.4152 | 73.1821 | 58.9689
590.7495 | 480.7495 | 306.4451 | 120.7317 | 151.7697 | 124.0884 | 77.2276 | 62.521 | 67.541 | 73.2986 | 59.0573
591.7509 | 481.7509 | 306.5423 | 120.8789 | 151.9453 | 124.2373 | 77.3715 | 62.6386 | 67.6703 | 73.4083 | 59.1784
592.7523 | 482.7523 | 306.5393 | 121.0319 | 152.1058 | 124.3839 | 77.5131 | 62.7366 | 67.8077 | 73.5361 | 59.2901
593.7538 | 483.7538 | 306.5338 | 121.1685 | 152.2949 | 124.5212 | 77.6584 | 62.8841 | 67.9334 | 73.6601 | 59.3858
594.7552 | 484.7552 | 306.4656 | 121.3082 | 152.4471 | 124.6736 | 77.8075 | 63.0126 | 68.0588 | 73.7791 | 59.4841
595.7466 | 485.7466 | 306.4547 | 121.4288 | 152.6404 | 124.8114 | 77.9494 | 63.1171 | 68.1906 | 73.8942 | 59.594
596.7481 | 486.7481 | 306.5044 | 121.6023 | 152.7934 | 124.9677 | 78.0851 | 63.2315 | 68.3278 | 74.008 | 59.6941
597.8397 | 487.8397 | 306.5772 | 121.7372 | 153.01 | 125.1138 | 78.2297 | 63.3905 | 68.4677 | 74.1429 | 59.8078
598.751 | 488.751 | 306.5511 | 121.8803 | 153.1488 | 125.2447 | 78.3562 | 63.4948 | 68.5869 | 74.2383 | 59.9042
599.7524 | 489.7524 | 306.5211 | 122.0266 | 153.3212 | 125.3941 | 78.4987 | 63.5983 | 68.7244 | 74.3633 | 59.9963
600.7538 | 490.7538 | 306.397 | 122.1651 | 153.4779 | 125.5327 | 78.6487 | 63.7473 | 68.857 | 74.4692 | 60.1083
601.7553 | 491.7553 | 306.395 | 122.3059 | 153.6641 | 125.6825 | 78.7859 | 63.8704 | 68.9889 | 74.5964 | 60.2041
602.7467 | 492.7467 | 306.3397 | 122.4256 | 153.8319 | 125.816 | 78.939 | 63.9766 | 69.1207 | 74.7141 | 60.2967
603.7481 | 493.7481 | 306.2592 | 122.5967 | 153.9951 | 125.9616 | 79.0753 | 64.0973 | 69.2559 | 74.8187 | 60.4164
604.7496 | 494.7496 | 306.1907 | 122.6966 | 154.1709 | 126.0891 | 79.221 | 64.2451 | 69.3838 | 74.9531 | 60.5253
605.751 | 495.751 | 306.1784 | 122.868 | 154.3381 | 126.2484 | 79.3685 | 64.3707 | 69.5143 | 75.0667 | 60.6086
606.7525 | 496.7525 | 306.2504 | 123.0071 | 154.4984 | 126.3806 | 79.5068 | 64.459 | 69.6511 | 75.1735 | 60.7429
607.7539 | 497.7539 | 306.3192 | 123.1433 | 154.6869 | 126.5147 | 79.646 | 64.6114 | 69.7839 | 75.3131 | 60.8217
608.7553 | 498.7553 | 306.3616 | 123.2832 | 154.8417 | 126.6526 | 79.7903 | 64.7404 | 69.9138 | 75.426 | 60.9161
609.7568 | 499.7568 | 306.3341 | 123.4201 | 155.0005 | 126.8035 | 79.9322 | 64.851 | 70.0494 | 75.5486 | 61.0515
610.7482 | 500.7482 | 306.3581 | 123.5745 | 155.1835 | 126.9401 | 80.0708 | 64.9728 | 70.1751 | 75.6647 | 61.1316
611.7497 | 501.7497 | 306.367 | 123.6995 | 155.3504 | 127.0666 | 80.2187 | 65.1252 | 70.3115 | 75.7859 | 61.2563
612.7511 | 502.7511 | 306.4586 | 123.8639 | 155.5089 | 127.2276 | 80.3495 | 65.2469 | 70.4389 | 75.909 | 61.3449
613.7525 | 503.7525 | 306.5678 | 123.9696 | 155.673 | 127.3556 | 80.4994 | 65.3402 | 70.5731 | 76.0328 | 61.4369
614.754 | 504.754 | 306.5662 | 124.1288 | 155.8319 | 127.5014 | 80.6494 | 65.4926 | 70.7072 | 76.1549 | 61.544
615.7554 | 505.7554 | 306.5181 | 124.2503 | 156.0102 | 127.6174 | 80.788 | 65.6242 | 70.832 | 76.2813 | 61.6686
616.7468 | 506.7468 | 306.509 | 124.4006 | 156.1786 | 127.7728 | 80.931 | 65.7192 | 70.9721 | 76.3949 | 61.7575
617.7483 | 507.7483 | 306.5501 | 124.5323 | 156.3078 | 127.9015 | 81.0812 | 65.8451 | 71.0971 | 76.5136 | 61.8751
618.7497 | 508.7497 | 306.5892 | 124.6705 | 156.486 | 128.0559 | 81.2149 | 65.9971 | 71.2245 | 76.6589 | 61.9734
619.7512 | 509.7512 | 306.5579 | 124.8018 | 156.6424 | 128.1906 | 81.3622 | 66.1197 | 71.3645 | 76.7745 | 62.0845
620.7526 | 510.7526 | 306.502 | 124.9368 | 156.8176 | 128.3217 | 81.5072 | 66.2198 | 71.4952 | 76.8988 | 62.1772
621.754 | 511.754 | 306.4931 | 125.0898 | 156.9462 | 128.4659 | 81.646 | 66.3686 | 71.6251 | 77.0226 | 62.2886
622.7555 | 512.7555 | 306.5804 | 125.2035 | 157.1408 | 128.5996 | 81.8053 | 66.5081 | 71.7518 | 77.1468 | 62.3904
623.7569 | 513.7569 | 306.5999 | 125.3656 | 157.3 | 128.7362 | 81.9268 | 66.6076 | 71.8873 | 77.2746 | 62.4643
624.7483 | 514.7483 | 306.605 | 125.4816 | 157.4638 | 128.8663 | 82.0735 | 66.7394 | 72.0179 | 77.4061 | 62.5752
625.7498 | 515.7498 | 306.5578 | 125.6291 | 157.6263 | 129.0132 | 82.2191 | 66.8764 | 72.1478 | 77.5337 | 62.6803
626.7512 | 516.7512 | 306.6691 | 125.7555 | 157.8093 | 129.1509 | 82.3564 | 67.0135 | 72.2794 | 77.6581 | 62.8
627.7527 | 517.7527 | 306.6888 | 125.8999 | 157.9596 | 129.2841 | 82.5092 | 67.1166 | 72.4139 | 77.7667 | 62.9068
628.7541 | 518.7541 | 306.6559 | 126.0232 | 158.1261 | 129.4192 | 82.6435 | 67.2695 | 72.5317 | 77.9131 | 62.9974
629.7555 | 519.7555 | 306.6524 | 126.1549 | 158.3017 | 129.5653 | 82.7976 | 67.3956 | 72.6699 | 78.051 | 63.0947
630.757 | 520.757 | 306.7842 | 126.309 | 158.4492 | 129.7091 | 82.935 | 67.4994 | 72.7955 | 78.1819 | 63.1839
631.7484 | 521.7484 | 306.8638 | 126.4365 | 158.6281 | 129.8395 | 83.0735 | 67.6307 | 72.9284 | 78.3127 | 63.2984
632.7498 | 522.7498 | 306.8944 | 126.5798 | 158.7739 | 129.9717 | 83.2089 | 67.7744 | 73.0491 | 78.4406 | 63.3841
633.7513 | 523.7513 | 306.8764 | 126.7017 | 158.9174 | 130.1144 | 83.3658 | 67.9027 | 73.1803 | 78.5691 | 63.4981
634.7527 | 524.7527 | 306.8119 | 126.846 | 159.0856 | 130.2535 | 83.4999 | 67.9996 | 73.3076 | 78.6842 | 63.6055
635.7542 | 525.7542 | 306.7532 | 126.9757 | 159.2725 | 130.3812 | 83.649 | 68.1561 | 73.4381 | 78.8321 | 63.6893
636.7556 | 526.7556 | 306.6535 | 127.1155 | 159.4168 | 130.5199 | 83.7873 | 68.2836 | 73.5653 | 78.9572 | 63.7823
637.747 | 527.747 | 306.5828 | 127.2415 | 159.5837 | 130.6431 | 83.9192 | 68.3829 | 73.7051 | 79.0807 | 63.8945
638.7485 | 528.7485 | 306.4925 | 127.3772 | 159.7329 | 130.7856 | 84.0654 | 68.5178 | 73.8326 | 79.2008 | 64.0013
639.7499 | 529.7499 | 306.4578 | 127.5212 | 159.9076 | 130.9196 | 84.2149 | 68.664 | 73.9536 | 79.3248 | 64.1041
640.7514 | 530.7514 | 306.4423 | 127.628 | 160.0684 | 131.0464 | 84.3596 | 68.8009 | 74.0881 | 79.4574 | 64.206
641.7528 | 531.7528 | 306.4503 | 127.7676 | 160.2384 | 131.1999 | 84.5009 | 68.8933 | 74.2194 | 79.5732 | 64.3054
642.7542 | 532.7542 | 306.4135 | 127.902 | 160.3858 | 131.3247 | 84.6348 | 69.0558 | 74.3472 | 79.717 | 64.3742
643.7457 | 533.7457 | 306.3775 | 128.0513 | 160.5333 | 131.4518 | 84.7946 | 69.1781 | 74.4862 | 79.8356 | 64.4883
644.7471 | 534.7471 | 306.4002 | 128.1677 | 160.6854 | 131.5916 | 84.9329 | 69.2868 | 74.6138 | 79.9605 | 64.6214
645.7485 | 535.7485 | 306.4375 | 128.3003 | 160.8573 | 131.7275 | 85.0678 | 69.4087 | 74.7486 | 80.0876 | 64.7061
646.75 | 536.75 | 306.3697 | 128.4357 | 161.0131 | 131.8555 | 85.2093 | 69.5683 | 74.8764 | 80.2097 | 64.832
647.7514 | 537.7514 | 306.3021 | 128.5647 | 161.179 | 131.9892 | 85.3547 | 69.6948 | 75.0102 | 80.3403 | 64.9065
648.7529 | 538.7529 | 306.2589 | 128.7106 | 161.3333 | 132.1251 | 85.5041 | 69.7886 | 75.1398 | 80.4619 | 65.0218
649.7543 | 539.7543 | 306.1747 | 128.8301 | 161.4929 | 132.2519 | 85.6436 | 69.9539 | 75.2758 | 80.5794 | 65.1298
650.7557 | 540.7557 | 306.1481 | 128.9688 | 161.6405 | 132.3885 | 85.7872 | 70.0785 | 75.4057 | 80.7061 | 65.2287
651.7472 | 541.7472 | 306.1143 | 129.0602 | 161.8261 | 132.5121 | 85.9315 | 70.1947 | 75.5409 | 80.8316 | 65.3285
652.7486 | 542.7486 | 306.0732 | 129.2302 | 161.9504 | 132.6458 | 86.0855 | 70.3147 | 75.6732 | 80.9351 | 65.4403
653.75 | 543.75 | 306.0627 | 129.3277 | 162.1254 | 132.7733 | 86.2362 | 70.4726 | 75.8005 | 81.0796 | 65.5363
654.7515 | 544.7515 | 306.17 | 129.4804 | 162.2733 | 132.93 | 86.3788 | 70.5958 | 75.9391 | 81.2046 | 65.6383
655.7529 | 545.7529 | 306.1596 | 129.6038 | 162.4199 | 133.0515 | 86.5214 | 70.7017 | 76.0803 | 81.3206 | 65.7556
656.7544 | 546.7544 | 306.1144 | 129.7452 | 162.5873 | 133.1928 | 86.6621 | 70.8506 | 76.2041 | 81.4465 | 65.8586
657.7558 | 547.7558 | 306.1894 | 129.8733 | 162.6775 | 133.3247 | 86.8093 | 70.9833 | 76.3313 | 81.5658 | 65.9665
658.7472 | 548.7472 | 306.2028 | 130.0061 | 162.8765 | 133.4641 | 86.942 | 71.0941 | 76.4735 | 81.7008 | 66.0624
659.7487 | 549.7487 | 306.1897 | 130.128 | 163.0554 | 133.591 | 87.0936 | 71.2189 | 76.6088 | 81.8307 | 66.1511
660.7501 | 550.7501 | 306.2359 | 130.2635 | 163.1925 | 133.728 | 87.2464 | 71.3791 | 76.7488 | 81.9549 | 66.258
661.7516 | 551.7516 | 306.2432 | 130.4008 | 163.3498 | 133.8531 | 87.384 | 71.5121 | 76.8829 | 82.0737 | 66.3653
662.753 | 552.753 | 306.1973 | 130.5204 | 163.5164 | 133.9807 | 87.526 | 71.6136 | 77.0156 | 82.1931 | 66.4635
663.7544 | 553.7544 | 306.2439 | 130.6596 | 163.6582 | 134.1088 | 87.674 | 71.7718 | 77.1562 | 82.2915 | 66.5989
664.7559 | 554.7559 | 306.2382 | 130.7721 | 163.822 | 134.2353 | 87.8235 | 71.9009 | 77.2942 | 82.4268 | 66.6756
665.7473 | 555.7473 | 306.239 | 130.9179 | 163.9859 | 134.3824 | 87.9595 | 72.0126 | 77.4364 | 82.5365 | 66.7954
666.7487 | 556.7487 | 306.2484 | 131.0519 | 164.1245 | 134.5113 | 88.1009 | 72.1428 | 77.5659 | 82.6578 | 66.8816
667.7502 | 557.7502 | 306.1913 | 131.1675 | 164.3016 | 134.6326 | 88.2391 | 72.2989 | 77.7112 | 82.771 | 67.0023
668.7516 | 558.7516 | 306.1067 | 131.3017 | 164.4274 | 134.7651 | 88.3857 | 72.4214 | 77.8435 | 82.8844 | 67.1322
669.7531 | 559.7531 | 306.0157 | 131.4207 | 164.557 | 134.9007 | 88.5344 | 72.5299 | 77.9885 | 83.011 | 67.2173
670.7545 | 560.7545 | 305.9574 | 131.5657 | 164.7171 | 135.0295 | 88.6867 | 72.6874 | 78.1192 | 83.1271 | 67.3248
671.7559 | 561.7559 | 305.999 | 131.672 | 164.8764 | 135.1483 | 88.8298 | 72.8233 | 78.2558 | 83.2351 | 67.447
672.7474 | 562.7474 | 306.0914 | 131.8231 | 165.0442 | 135.2839 | 88.9626 | 72.9275 | 78.3948 | 83.3689 | 67.5533
673.7488 | 563.7488 | 306.1238 | 131.9174 | 165.1887 | 135.4117 | 89.113 | 73.0631 | 78.5314 | 83.4872 | 67.6473
674.7502 | 564.7502 | 306.2089 | 132.079 | 165.3462 | 135.5578 | 89.2625 | 73.2139 | 78.6689 | 83.6005 | 67.7695
675.7517 | 565.7517 | 306.284 | 132.1834 | 165.4735 | 135.6747 | 89.3994 | 73.3519 | 78.8091 | 83.7183 | 67.8669
676.7531 | 566.7531 | 306.2555 | 132.3368 | 165.637 | 135.8165 | 89.5359 | 73.4466 | 78.9502 | 83.8465 | 67.9548
677.7546 | 567.7546 | 306.1832 | 132.4424 | 165.8016 | 135.9223 | 89.6993 | 73.6231 | 79.0878 | 83.9539 | 68.0728
678.756 | 568.756 | 306.1219 | 132.5905 | 165.939 | 136.0587 | 89.8299 | 73.7502 | 79.225 | 84.0788 | 68.1781
679.7474 | 569.7474 | 306.1 | 132.6888 | 166.0827 | 136.1805 | 89.9756 | 73.8672 | 79.367 | 84.1917 | 68.2803
680.7489 | 570.7489 | 306.0728 | 132.8365 | 166.2349 | 136.3134 | 90.1247 | 73.9907 | 79.5006 | 84.3127 | 68.399
681.7503 | 571.7503 | 306.0173 | 132.9551 | 166.3811 | 136.4387 | 90.2738 | 74.1502 | 79.6383 | 84.4354 | 68.5104
682.7517 | 572.7517 | 305.9407 | 133.0904 | 166.5431 | 136.5634 | 90.4079 | 74.2764 | 79.7797 | 84.5586 | 68.6065
683.7532 | 573.7532 | 305.9178 | 133.2249 | 166.6836 | 136.6915 | 90.5538 | 74.3839 | 79.9133 | 84.6794 | 68.7112
684.7546 | 574.7546 | 305.8719 | 133.3198 | 166.852 | 136.8096 | 90.7031 | 74.547 | 80.0504 | 84.7915 | 68.8281
685.8362 | 575.8362 | 305.757 | 133.4892 | 167.011 | 136.965 | 90.8634 | 74.6867 | 80.1998 | 84.9352 | 68.936
686.7475 | 576.7475 | 305.8583 | 133.5771 | 167.1298 | 137.0781 | 91.0035 | 74.795 | 80.3195 | 85.0374 | 69.0298
687.7489 | 577.7489 | 305.8911 | 133.7263 | 167.2902 | 137.2028 | 91.1495 | 74.9129 | 80.4629 | 85.162 | 69.1393
688.7504 | 578.7504 | 305.8426 | 133.8243 | 167.4371 | 137.3169 | 91.2755 | 75.0729 | 80.6012 | 85.283 | 69.2398
689.7518 | 579.7518 | 305.8385 | 133.9801 | 167.5966 | 137.4459 | 91.4262 | 75.205 | 80.7396 | 85.4017 | 69.355
690.7533 | 580.7533 | 305.8895 | 134.0887 | 167.7122 | 137.5776 | 91.5719 | 75.3162 | 80.8788 | 85.5098 | 69.4575
691.7547 | 581.7547 | 305.9198 | 134.2191 | 167.8648 | 137.695 | 91.7118 | 75.4763 | 81.0176 | 85.6436 | 69.5739
692.7461 | 582.7461 | 305.977 | 134.356 | 168.0089 | 137.8256 | 91.8668 | 75.6038 | 81.1553 | 85.7648 | 69.673
693.7476 | 583.7476 | 305.9424 | 134.4685 | 168.1643 | 137.9327 | 92.0184 | 75.7242 | 81.2994 | 85.8911 | 69.749
694.749 | 584.749 | 305.8911 | 134.6115 | 168.3126 | 138.0746 | 92.1608 | 75.8482 | 81.4356 | 86.0027 | 69.8907
695.7504 | 585.7504 | 305.9873 | 134.7173 | 168.4756 | 138.1851 | 92.3049 | 76.0105 | 81.5759 | 86.1282 | 70.0025
696.7519 | 586.7519 | 306.0523 | 134.8574 | 168.6188 | 138.3264 | 92.4435 | 76.1413 | 81.7146 | 86.2497 | 70.0893
697.7533 | 587.7533 | 306.1519 | 134.9695 | 168.772 | 138.4426 | 92.5898 | 76.2511 | 81.8563 | 86.3761 | 70.1916
698.7548 | 588.7548 | 306.2611 | 135.1049 | 168.9164 | 138.5733 | 92.7396 | 76.4157 | 81.9885 | 86.502 | 70.2976
699.7562 | 589.7562 | 306.1887 | 135.2187 | 169.0643 | 138.685 | 92.8743 | 76.5541 | 82.1258 | 86.619 | 70.4177
700.7476 | 590.7476 | 306.1254 | 135.35 | 169.209 | 138.8149 | 93.0192 | 76.6687 | 82.2632 | 86.7463 | 70.5133
701.7491 | 591.7491 | 306.2035 | 135.4634 | 169.3595 | 138.9345 | 93.1676 | 76.7948 | 82.3967 | 86.8832 | 70.5943
702.7505 | 592.7505 | 306.187 | 135.5935 | 169.4985 | 139.0689 | 93.3152 | 76.9518 | 82.5396 | 86.9965 | 70.7297
703.7519 | 593.7519 | 306.0918 | 135.7098 | 169.6387 | 139.2064 | 93.4609 | 77.0877 | 82.6733 | 87.1209 | 70.8297
704.7534 | 594.7534 | 306.043 | 135.8206 | 169.7877 | 139.3304 | 93.6039 | 77.1925 | 82.8164 | 87.2547 | 70.9346
705.7548 | 595.7548 | 306.0401 | 135.9517 | 169.9377 | 139.4512 | 93.7425 | 77.3544 | 82.9438 | 87.3822 | 71.0299
706.7563 | 596.7563 | 306.0071 | 136.0728 | 170.0723 | 139.573 | 93.894 | 77.4897 | 83.0751 | 87.5122 | 71.1379
707.7477 | 597.7477 | 306.0328 | 136.2039 | 170.1925 | 139.6907 | 94.0369 | 77.6025 | 83.2214 | 87.6352 | 71.2312
708.7491 | 598.7491 | 306.0224 | 136.3268 | 170.3382 | 139.8099 | 94.1724 | 77.7295 | 83.357 | 87.7468 | 71.3502
709.7506 | 599.7506 | 305.9952 | 136.453 | 170.4903 | 139.9394 | 94.3285 | 77.8861 | 83.4919 | 87.8818 | 71.4417
710.752 | 600.752 | 305.968 | 136.5603 | 170.6365 | 140.0556 | 94.4746 | 78.0284 | 83.6325 | 87.9984 | 71.5577
711.7535 | 601.7535 | 305.865 | 136.6907 | 170.7986 | 140.1717 | 94.6087 | 78.132 | 83.7685 | 88.1166 | 71.6642
712.7549 | 602.7549 | 305.7802 | 136.8097 | 170.9503 | 140.2937 | 94.7459 | 78.2943 | 83.9058 | 88.2398 | 71.7874
713.7563 | 603.7563 | 305.7177 | 136.9163 | 171.0941 | 140.4152 | 94.9022 | 78.4348 | 84.0475 | 88.3552 | 71.8992
714.7578 | 604.7578 | 305.7786 | 137.061 | 171.2285 | 140.5477 | 95.0391 | 78.5423 | 84.1839 | 88.4748 | 71.9887
715.7492 | 605.7492 | 305.6821 | 137.1665 | 171.3756 | 140.6525 | 95.1983 | 78.6784 | 84.3232 | 88.6113 | 72.082
716.7506 | 606.7506 | 305.7088 | 137.3095 | 171.5035 | 140.7847 | 95.3257 | 78.8295 | 84.462 | 88.739 | 72.1875
717.7521 | 607.7521 | 305.8137 | 137.4001 | 171.6627 | 140.8956 | 95.4909 | 78.972 | 84.5964 | 88.8518 | 72.2986
718.7535 | 608.7535 | 305.9102 | 137.5385 | 171.7898 | 141.0137 | 95.6363 | 79.0758 | 84.7404 | 88.9722 | 72.4055
719.755 | 609.755 | 305.9998 | 137.6577 | 171.9441 | 141.1478 | 95.778 | 79.2354 | 84.8768 | 89.1055 | 72.5035
720.7664 | 610.7664 | 306.076 | 137.7766 | 172.0711 | 141.2702 | 95.9259 | 79.3786 | 85.0208 | 89.2167 | 72.6294
721.7478 | 611.7478 | 306.1293 | 137.9103 | 172.2094 | 141.3919 | 96.0601 | 79.4809 | 85.1478 | 89.3365 | 72.7364
722.7493 | 612.7493 | 306.1906 | 137.9987 | 172.3402 | 141.4987 | 96.2055 | 79.6211 | 85.2803 | 89.4762 | 72.8201
723.7507 | 613.7507 | 306.278 | 138.1475 | 172.5063 | 141.6344 | 96.356 | 79.7721 | 85.422 | 89.6082 | 72.9094
724.7521 | 614.7521 | 306.3549 | 138.2478 | 172.6325 | 141.7533 | 96.5029 | 79.9096 | 85.5597 | 89.72 | 73.0441
725.7536 | 615.7536 | 306.4094 | 138.3842 | 172.7822 | 141.8817 | 96.6459 | 80.0166 | 85.701 | 89.8555 | 73.1499
726.755 | 616.755 | 306.3367 | 138.4762 | 172.9366 | 141.9963 | 96.7945 | 80.1852 | 85.839 | 89.9858 | 73.2625
727.7464 | 617.7464 | 306.2661 | 138.6114 | 173.0766 | 142.1115 | 96.9389 | 80.3156 | 85.9739 | 90.119 | 73.3507
728.7479 | 618.7479 | 306.195 | 138.7353 | 173.2138 | 142.2206 | 97.0769 | 80.4314 | 86.1166 | 90.2527 | 73.4401
729.7493 | 619.7493 | 306.1738 | 138.8243 | 173.326 | 142.335 | 97.2364 | 80.5651 | 86.2441 | 90.3934 | 73.5443
730.7508 | 620.7508 | 306.2284 | 138.9766 | 173.4916 | 142.4741 | 97.3666 | 80.7224 | 86.3768 | 90.5276 | 73.6511
731.7522 | 621.7522 | 306.2053 | 139.0855 | 173.6276 | 142.588 | 97.5167 | 80.8524 | 86.5146 | 90.6496 | 73.7623
732.7536 | 622.7536 | 306.1648 | 139.2051 | 173.7629 | 142.7092 | 97.6524 | 80.961 | 86.6531 | 90.7742 | 73.8709
733.7551 | 623.7551 | 306.1417 | 139.3247 | 173.8871 | 142.8317 | 97.801 | 81.131 | 86.7875 | 90.9053 | 73.9767
734.7465 | 624.7465 | 306.1362 | 139.4293 | 174.0051 | 142.9537 | 97.9359 | 81.2575 | 86.9198 | 91.0387 | 74.0591
735.748 | 625.748 | 306.0008 | 139.5496 | 174.1516 | 143.0733 | 98.0862 | 81.371 | 87.0643 | 91.1596 | 74.1898
736.7494 | 626.7494 | 305.8673 | 139.6499 | 174.3133 | 143.1739 | 98.2272 | 81.4996 | 87.1902 | 91.2963 | 74.2624
737.7508 | 627.7508 | 305.7702 | 139.7934 | 174.4646 | 143.3157 | 98.3704 | 81.6606 | 87.3306 | 91.4209 | 74.3747
738.7523 | 628.7523 | 305.6671 | 139.8928 | 174.596 | 143.4267 | 98.523 | 81.7926 | 87.4699 | 91.5525 | 74.4698
739.7537 | 629.7537 | 305.5775 | 140.0183 | 174.7187 | 143.5473 | 98.6535 | 81.8975 | 87.6066 | 91.6728 | 74.5711
740.7552 | 630.7552 | 305.5509 | 140.134 | 174.8469 | 143.6615 | 98.8179 | 82.0636 | 87.7371 | 91.788 | 74.6867
741.7566 | 631.7566 | 305.5924 | 140.2494 | 174.9863 | 143.7769 | 98.9536 | 82.1985 | 87.8783 | 91.8993 | 74.8197
742.748 | 632.748 | 305.5116 | 140.3686 | 175.1275 | 143.8879 | 99.0927 | 82.322 | 88.019 | 92.0417 | 74.8879
743.7495 | 633.7495 | 305.4575 | 140.4696 | 175.2407 | 144.0038 | 99.2367 | 82.4443 | 88.1562 | 92.1554 | 75.0046
744.7509 | 634.7509 | 305.4488 | 140.6093 | 175.3915 | 144.1248 | 99.388 | 82.6092 | 88.3 | 92.2724 | 75.1263
745.7523 | 635.7523 | 305.4413 | 140.7035 | 175.5328 | 144.231 | 99.5393 | 82.7492 | 88.4323 | 92.3839 | 75.2391
746.7538 | 636.7538 | 305.3578 | 140.8412 | 175.647 | 144.3581 | 99.6737 | 82.8438 | 88.5751 | 92.5271 | 75.3186
747.7552 | 637.7552 | 305.3763 | 140.9196 | 175.7781 | 144.4536 | 99.8163 | 83.0175 | 88.7102 | 92.6412 | 75.4483
748.7466 | 638.7466 | 305.4272 | 141.0638 | 175.9111 | 144.5866 | 99.9656 | 83.1446 | 88.8453 | 92.7608 | 75.5373
749.7481 | 639.7481 | 305.4587 | 141.1537 | 176.0598 | 144.6954 | 100.1212 | 83.2674 | 88.9919 | 92.8921 | 75.6506
750.7495 | 640.7495 | 305.5344 | 141.2932 | 176.1947 | 144.824 | 100.2626 | 83.3947 | 89.1293 | 93.0071 | 75.7487
751.751 | 641.751 | 305.5931 | 141.4032 | 176.3448 | 144.9378 | 100.4096 | 83.5615 | 89.2635 | 93.1385 | 75.8434
752.7524 | 642.7524 | 305.7228 | 141.5042 | 176.4682 | 145.0397 | 100.5545 | 83.6957 | 89.4068 | 93.2523 | 75.9644
753.7538 | 643.7538 | 305.8251 | 141.6471 | 176.57 | 145.1699 | 100.6912 | 83.7924 | 89.5418 | 93.3642 | 76.0676
754.7553 | 644.7553 | 305.7686 | 141.7376 | 176.7319 | 145.2778 | 100.8471 | 83.9682 | 89.6843 | 93.4898 | 76.1889
755.7567 | 645.7567 | 305.8269 | 141.8765 | 176.862 | 145.3921 | 100.9893 | 84.0967 | 89.8301 | 93.6114 | 76.2894
756.7482 | 646.7482 | 305.9317 | 141.9653 | 177.0148 | 145.4988 | 101.1313 | 84.2089 | 89.9749 | 93.7232 | 76.4221
757.7496 | 647.7496 | 305.9334 | 142.1069 | 177.1234 | 145.6156 | 101.2607 | 84.3395 | 90.1113 | 93.8308 | 76.5312
758.751 | 648.751 | 305.959 | 142.1965 | 177.2699 | 145.7242 | 101.4227 | 84.5066 | 90.2514 | 93.9568 | 76.6494
759.7525 | 649.7525 | 306.0454 | 142.3315 | 177.4075 | 145.8618 | 101.5632 | 84.6385 | 90.398 | 94.0775 | 76.7339
760.7539 | 650.7539 | 306.1686 | 142.4215 | 177.5169 | 145.9624 | 101.7025 | 84.7517 | 90.5394 | 94.1894 | 76.8547
761.7554 | 651.7554 | 306.3065 | 142.5563 | 177.6446 | 146.0726 | 101.8482 | 84.9134 | 90.6823 | 94.3173 | 76.9381
762.7568 | 652.7568 | 306.2914 | 142.6602 | 177.8112 | 146.1871 | 101.9911 | 85.0566 | 90.8251 | 94.4238 | 77.0734
763.7482 | 653.7482 | 306.3846 | 142.7794 | 177.9517 | 146.3015 | 102.1388 | 85.1678 | 90.964 | 94.5613 | 77.1553
764.7497 | 654.7497 | 306.3896 | 142.9033 | 178.0356 | 146.4231 | 102.2787 | 85.2885 | 91.1021 | 94.6811 | 77.2721
765.7511 | 655.7511 | 306.4682 | 142.9973 | 178.2142 | 146.5287 | 102.4245 | 85.4572 | 91.2458 | 94.7905 | 77.401
766.7525 | 656.7525 | 306.4808 | 143.1345 | 178.3096 | 146.6436 | 102.5641 | 85.5879 | 91.3779 | 94.9259 | 77.4699
767.754 | 657.754 | 306.4216 | 143.2251 | 178.4475 | 146.7254 | 102.7064 | 85.7014 | 91.5206 | 95.0446 | 77.6142
768.7454 | 658.7454 | 306.2684 | 143.3573 | 178.5682 | 146.8735 | 102.8611 | 85.873 | 91.6677 | 95.1884 | 77.6813
769.7468 | 659.7468 | 306.1806 | 143.4516 | 178.7129 | 146.968 | 102.9907 | 86.0064 | 91.7942 | 95.3132 | 77.8007
770.7483 | 660.7483 | 306.2144 | 143.5862 | 178.8472 | 147.1037 | 103.1412 | 86.1202 | 91.9337 | 95.4318 | 77.9054
771.7497 | 661.7497 | 306.2528 | 143.6859 | 178.9745 | 147.2003 | 103.2817 | 86.2457 | 92.061 | 95.5559 | 78.0271
772.7512 | 662.7512 | 306.2311 | 143.7955 | 179.1286 | 147.317 | 103.4332 | 86.407 | 92.2079 | 95.6719 | 78.1382
773.7526 | 663.7526 | 306.2481 | 143.9145 | 179.251 | 147.4398 | 103.5721 | 86.5452 | 92.3452 | 95.8065 | 78.2356
774.754 | 664.754 | 306.3153 | 144.0146 | 179.367 | 147.5422 | 103.7115 | 86.6578 | 92.486 | 95.9367 | 78.3329
775.7555 | 665.7555 | 306.3801 | 144.1487 | 179.506 | 147.6607 | 103.8638 | 86.8156 | 92.6223 | 96.0579 | 78.4373
776.7469 | 666.7469 | 306.4183 | 144.2381 | 179.6531 | 147.7718 | 104.0138 | 86.9577 | 92.7599 | 96.1779 | 78.5501
777.7483 | 667.7483 | 306.4326 | 144.3813 | 179.7917 | 147.8985 | 104.1459 | 87.0722 | 92.9017 | 96.3012 | 78.6538
778.7498 | 668.7498 | 306.5043 | 144.4631 | 179.9185 | 147.9994 | 104.2989 | 87.2072 | 93.0399 | 96.4269 | 78.7497
779.7512 | 669.7512 | 306.4774 | 144.603 | 180.0182 | 148.1206 | 104.4256 | 87.3582 | 93.1747 | 96.5607 | 78.861
780.7527 | 670.7527 | 306.429 | 144.7078 | 180.1711 | 148.2242 | 104.5852 | 87.4979 | 93.3082 | 96.6725 | 78.9741
781.7541 | 671.7541 | 306.3941 | 144.8181 | 180.2842 | 148.3335 | 104.7127 | 87.5979 | 93.4533 | 96.8025 | 79.0703
782.7555 | 672.7555 | 306.3004 | 144.9207 | 180.425 | 148.4391 | 104.8787 | 87.7712 | 93.5927 | 96.9248 | 79.1869
783.757 | 673.757 | 306.269 | 145.0386 | 180.5362 | 148.5573 | 105.0196 | 87.9065 | 93.7314 | 97.0602 | 79.2591
784.7484 | 674.7484 | 306.1885 | 145.1339 | 180.6241 | 148.6788 | 105.1671 | 88.0208 | 93.8639 | 97.179 | 79.3916
785.7499 | 675.7499 | 306.143 | 145.2687 | 180.8061 | 148.7811 | 105.3096 | 88.1522 | 94.0076 | 97.3044 | 79.4932
786.7513 | 676.7513 | 306.0674 | 145.3858 | 180.9374 | 148.9048 | 105.447 | 88.3112 | 94.1385 | 97.4251 | 79.6067
787.7527 | 677.7527 | 306.0258 | 145.4657 | 181.0169 | 148.9958 | 105.5963 | 88.4568 | 94.2739 | 97.5482 | 79.7069
788.7542 | 678.7542 | 306.0228 | 145.6004 | 181.1587 | 149.122 | 105.7288 | 88.5548 | 94.4165 | 97.6553 | 79.8313
789.7556 | 679.7556 | 306.0119 | 145.6818 | 181.2893 | 149.2232 | 105.8901 | 88.7207 | 94.5604 | 97.785 | 79.9208
790.747 | 680.747 | 306.1322 | 145.8278 | 181.432 | 149.3473 | 106.0128 | 88.8512 | 94.6965 | 97.9204 | 80.0229
791.7485 | 681.7485 | 306.2337 | 145.9097 | 181.5762 | 149.439 | 106.1725 | 88.9769 | 94.828 | 98.0453 | 80.1171
792.7499 | 682.7499 | 306.3509 | 146.0338 | 181.722 | 149.5586 | 106.3124 | 89.0951 | 94.9706 | 98.1708 | 80.2088
793.7514 | 683.7514 | 306.4221 | 146.1541 | 181.8267 | 149.6755 | 106.456 | 89.2669 | 95.1119 | 98.2908 | 80.3492
794.7528 | 684.7528 | 306.4922 | 146.2559 | 181.9771 | 149.7636 | 106.5904 | 89.3989 | 95.2497 | 98.4103 | 80.4541
795.7542 | 685.7542 | 306.5749 | 146.3768 | 182.097 | 149.8868 | 106.7448 | 89.4963 | 95.389 | 98.5263 | 80.5589
796.7457 | 686.7457 | 306.6283 | 146.4577 | 182.2378 | 149.996 | 106.8842 | 89.6787 | 95.5313 | 98.6599 | 80.6746
797.7571 | 687.7571 | 306.823 | 146.6024 | 182.3576 | 150.1102 | 107.0159 | 89.8069 | 95.6676 | 98.7767 | 80.7755
798.7485 | 688.7485 | 306.915 | 146.6709 | 182.4704 | 150.216 | 107.1671 | 89.9294 | 95.803 | 98.9073 | 80.887
799.75 | 689.75 | 306.8676 | 146.8143 | 182.6123 | 150.3372 | 107.3042 | 90.048 | 95.9475 | 99.0272 | 80.987
800.7514 | 690.7514 | 306.8805 | 146.8969 | 182.7369 | 150.4436 | 107.4573 | 90.2224 | 96.0801 | 99.1513 | 81.0893
801.7529 | 691.7529 | 306.8161 | 147.0285 | 182.8535 | 150.5511 | 107.5968 | 90.3466 | 96.2177 | 99.2673 | 81.2051
802.7543 | 692.7543 | 306.7826 | 147.1282 | 182.9839 | 150.6628 | 107.7258 | 90.4553 | 96.3578 | 99.4156 | 81.306
803.7557 | 693.7557 | 306.8285 | 147.2264 | 183.1179 | 150.7667 | 107.8787 | 90.6298 | 96.494 | 99.5342 | 81.4035
804.7572 | 694.7572 | 306.7419 | 147.3517 | 183.2238 | 150.8807 | 108.0168 | 90.7655 | 96.6334 | 99.6654 | 81.5242
805.7486 | 695.7486 | 306.7005 | 147.4339 | 183.386 | 150.9833 | 108.1664 | 90.8851 | 96.7648 | 99.7894 | 81.6353
806.75 | 696.75 | 306.6894 | 147.5653 | 183.509 | 151.103 | 108.2959 | 91.0044 | 96.9016 | 99.9148 | 81.7408
807.7515 | 697.7515 | 306.5771 | 147.6414 | 183.6132 | 151.1845 | 108.4419 | 91.1695 | 97.0342 | 100.0536 | 81.8367
808.7529 | 698.7529 | 306.5544 | 147.7905 | 183.693 | 151.2933 | 108.5858 | 91.3029 | 97.1725 | 100.1802 | 81.9346
809.7544 | 699.7544 | 306.5093 | 147.8743 | 183.826 | 151.3964 | 108.7299 | 91.4114 | 97.3137 | 100.2822 | 82.0557
810.7558 | 700.7558 | 306.4809 | 147.9938 | 183.9756 | 151.5064 | 108.8775 | 91.5787 | 97.4501 | 100.4148 | 82.1602
811.7472 | 701.7472 | 306.4789 | 148.0788 | 184.1106 | 151.6151 | 109.017 | 91.713 | 97.5808 | 100.5536 | 82.2582
812.7487 | 702.7487 | 306.4343 | 148.1888 | 184.2199 | 151.7279 | 109.1586 | 91.8323 | 97.7218 | 100.689 | 82.3673
813.7501 | 703.7501 | 306.336 | 148.2829 | 184.3363 | 151.8238 | 109.2922 | 91.962 | 97.8532 | 100.8077 | 82.4524
814.7516 | 704.7516 | 306.2014 | 148.4064 | 184.4105 | 151.9452 | 109.4433 | 92.1179 | 97.9864 | 100.9387 | 82.5514
815.753 | 705.753 | 306.053 | 148.5025 | 184.5599 | 152.0324 | 109.5849 | 92.2502 | 98.1246 | 101.0662 | 82.6711
816.7544 | 706.7544 | 306.0075 | 148.5935 | 184.6922 | 152.1352 | 109.731 | 92.3605 | 98.258 | 101.1925 | 82.7845
817.7559 | 707.7559 | 305.9158 | 148.7081 | 184.8021 | 152.2552 | 109.8771 | 92.5245 | 98.3917 | 101.3114 | 82.8714
818.7473 | 708.7473 | 305.777 | 148.8074 | 184.9297 | 152.3366 | 110.0237 | 92.6662 | 98.5257 | 101.4449 | 82.9863
819.7487 | 709.7487 | 305.5936 | 148.9137 | 185.0133 | 152.456 | 110.1483 | 92.7796 | 98.6627 | 101.5681 | 83.0932
820.7502 | 710.7502 | 305.3069 | 149.0023 | 185.1491 | 152.5663 | 110.2978 | 92.9157 | 98.8017 | 101.7045 | 83.1623
821.7516 | 711.7516 | 305.026 | 149.1134 | 185.2714 | 152.675 | 110.4444 | 93.065 | 98.9377 | 101.8193 | 83.2742
822.7531 | 712.7531 | 304.8356 | 149.2096 | 185.3888 | 152.7652 | 110.5786 | 93.2 | 99.0672 | 101.9339 | 83.4097
823.7545 | 713.7545 | 304.68 | 149.3358 | 185.4968 | 152.8828 | 110.7163 | 93.2999 | 99.2069 | 102.0622 | 83.5056
824.7559 | 714.7559 | 304.5642 | 149.4154 | 185.6351 | 152.9716 | 110.876 | 93.478 | 99.3483 | 102.191 | 83.6053
825.7474 | 715.7474 | 304.5387 | 149.538 | 185.759 | 153.0849 | 111.0146 | 93.6066 | 99.4767 | 102.3119 | 83.7146
826.7488 | 716.7488 | 304.5077 | 149.613 | 185.8381 | 153.1776 | 111.1558 | 93.7318 | 99.615 | 102.4199 | 83.8479
827.7502 | 717.7502 | 304.5298 | 149.7228 | 185.9801 | 153.2826 | 111.294 | 93.8523 | 99.7517 | 102.5514 | 83.9305
828.7517 | 718.7517 | 304.5685 | 149.8298 | 186.0652 | 153.4056 | 111.435 | 94.0178 | 99.8893 | 102.6728 | 84.0427
829.7531 | 719.7531 | 304.5675 | 149.922 | 186.2 | 153.494 | 111.5754 | 94.1546 | 100.0312 | 102.7878 | 84.1503
830.7546 | 720.7546 | 304.5173 | 150.0351 | 186.3364 | 153.5947 | 111.7264 | 94.2571 | 100.1757 | 102.903 | 84.2659
831.756 | 721.756 | 304.5298 | 150.1169 | 186.4387 | 153.6921 | 111.8634 | 94.4286 | 100.3108 | 103.0335 | 84.365
832.7474 | 722.7474 | 304.6458 | 150.237 | 186.5459 | 153.7922 | 112.0001 | 94.5533 | 100.4503 | 103.1506 | 84.4641
833.7489 | 723.7489 | 304.7102 | 150.328 | 186.6591 | 153.8896 | 112.1457 | 94.6839 | 100.5836 | 103.2763 | 84.5786
834.7503 | 724.7503 | 304.7159 | 150.4536 | 186.7523 | 153.9962 | 112.2864 | 94.799 | 100.7232 | 103.3891 | 84.6736
835.7518 | 725.7518 | 304.7873 | 150.5414 | 186.8779 | 154.0898 | 112.4268 | 94.9698 | 100.8537 | 103.5118 | 84.7737
836.7532 | 726.7532 | 304.9646 | 150.6441 | 186.9941 | 154.1974 | 112.5606 | 95.0968 | 100.9911 | 103.6256 | 84.8926
837.7546 | 727.7546 | 305.1269 | 150.7405 | 187.1182 | 154.2825 | 112.7075 | 95.2161 | 101.1265 | 103.759 | 84.9969
838.7461 | 728.7461 | 305.2813 | 150.8556 | 187.2576 | 154.3868 | 112.8434 | 95.3794 | 101.2666 | 103.8734 | 85.1062
839.7575 | 729.7575 | 305.3915 | 150.9459 | 187.3354 | 154.4921 | 112.9904 | 95.5175 | 101.4093 | 103.9917 | 85.2303
840.7489 | 730.7489 | 305.4907 | 151.0462 | 187.462 | 154.5988 | 113.1212 | 95.628 | 101.5467 | 104.1129 | 85.315
841.7504 | 731.7504 | 305.6334 | 151.1612 | 187.591 | 154.6909 | 113.272 | 95.7607 | 101.6855 | 104.2308 | 85.4341
842.7518 | 732.7518 | 305.6918 | 151.2419 | 187.7141 | 154.7981 | 113.4173 | 95.9289 | 101.8188 | 104.3533 | 85.5244
843.7533 | 733.7533 | 305.7733 | 151.3626 | 187.8053 | 154.9183 | 113.5451 | 96.0558 | 101.956 | 104.4784 | 85.6449
844.7547 | 734.7547 | 305.863 | 151.4321 | 187.9379 | 155.011 | 113.6881 | 96.1586 | 102.0914 | 104.6107 | 85.7517
845.7561 | 735.7561 | 305.9503 | 151.5576 | 188.0421 | 155.1288 | 113.8267 | 96.3194 | 102.2305 | 104.7349 | 85.8603
846.7576 | 736.7576 | 305.9569 | 151.6156 | 188.1667 | 155.2011 | 113.9753 | 96.4721 | 102.3641 | 104.8507 | 85.9726
847.749 | 737.749 | 306.0792 | 151.7658 | 188.3048 | 155.3034 | 114.1019 | 96.5745 | 102.5056 | 104.9824 | 86.054
848.7504 | 738.7504 | 306.058 | 151.8565 | 188.3654 | 155.405 | 114.2482 | 96.7087 | 102.6395 | 105.0801 | 86.1893
849.7519 | 739.7519 | 306.0434 | 151.9455 | 188.53 | 155.5157 | 114.3918 | 96.8723 | 102.7766 | 105.2164 | 86.2789
850.7533 | 740.7533 | 306.0525 | 152.0771 | 188.6382 | 155.6307 | 114.5385 | 97.003 | 102.9109 | 105.336 | 86.3887
851.7548 | 741.7548 | 306.0791 | 152.1439 | 188.763 | 155.6981 | 114.6904 | 97.1103 | 103.0427 | 105.4702 | 86.47
852.7562 | 742.7562 | 306.14 | 152.2819 | 188.862 | 155.8194 | 114.8227 | 97.272 | 103.1834 | 105.581 | 86.6082
853.7476 | 743.7476 | 306.18 | 152.344 | 188.9737 | 155.906 | 114.9619 | 97.4162 | 103.3169 | 105.6957 | 86.7195
854.7491 | 744.7491 | 306.233 | 152.49 | 189.0909 | 156.0271 | 115.1042 | 97.5224 | 103.4583 | 105.8055 | 86.8195
855.7505 | 745.7505 | 306.2289 | 152.5672 | 189.1964 | 156.1152 | 115.2393 | 97.6559 | 103.5971 | 105.9287 | 86.9291
856.7519 | 746.7519 | 306.3171 | 152.6819 | 189.325 | 156.2267 | 115.3775 | 97.8158 | 103.7363 | 106.0607 | 87.0204
857.7534 | 747.7534 | 306.513 | 152.7772 | 189.4349 | 156.334 | 115.5221 | 97.9491 | 103.8703 | 106.1739 | 87.1266
858.7548 | 748.7548 | 306.6339 | 152.8622 | 189.5743 | 156.4244 | 115.6677 | 98.059 | 104.0094 | 106.2884 | 87.238
859.7463 | 749.7463 | 306.6863 | 152.9941 | 189.6996 | 156.5415 | 115.8026 | 98.2226 | 104.1474 | 106.4045 | 87.3365
860.7477 | 750.7477 | 306.7081 | 153.0722 | 189.8128 | 156.6314 | 115.9399 | 98.3679 | 104.2905 | 106.5149 | 87.4612
861.7491 | 751.7491 | 306.751 | 153.2013 | 189.8931 | 156.7417 | 116.0886 | 98.468 | 104.4277 | 106.6291 | 87.5756
862.7506 | 752.7506 | 306.8235 | 153.2747 | 190.0405 | 156.8406 | 116.2272 | 98.6034 | 104.5691 | 106.7449 | 87.6664
863.752 | 753.752 | 306.8522 | 153.4022 | 190.1472 | 156.9558 | 116.3493 | 98.7648 | 104.7022 | 106.8608 | 87.7713
864.7535 | 754.7535 | 306.9306 | 153.4697 | 190.2495 | 157.0519 | 116.5023 | 98.9004 | 104.8422 | 106.9747 | 87.89
865.7549 | 755.7549 | 306.9405 | 153.6027 | 190.3599 | 157.1642 | 116.6395 | 99.0045 | 104.9878 | 107.0936 | 87.9813
866.7563 | 756.7563 | 306.9769 | 153.6739 | 190.4734 | 157.2517 | 116.7751 | 99.1709 | 105.1301 | 107.1939 | 88.1072
867.7478 | 757.7478 | 307.0302 | 153.7861 | 190.5925 | 157.3569 | 116.9149 | 99.3097 | 105.2716 | 107.3124 | 88.2192
868.7492 | 758.7492 | 307.0364 | 153.9095 | 190.6829 | 157.465 | 117.066 | 99.4256 | 105.4055 | 107.4265 | 88.3193
869.7506 | 759.7506 | 307.0544 | 153.9656 | 190.824 | 157.5564 | 117.1984 | 99.5579 | 105.538 | 107.5598 | 88.4235
870.7521 | 760.7521 | 307.0532 | 154.1088 | 190.9306 | 157.6825 | 117.3298 | 99.705 | 105.6801 | 107.6661 | 88.5407
871.7535 | 761.7535 | 307.0179 | 154.1757 | 191.0315 | 157.7645 | 117.4791 | 99.8519 | 105.8192 | 107.7904 | 88.6355
872.755 | 762.755 | 307.0436 | 154.3106 | 191.1701 | 157.8798 | 117.6126 | 99.9615 | 105.9595 | 107.897 | 88.7532
873.7564 | 763.7564 | 307.0749 | 154.3772 | 191.2889 | 157.9741 | 117.7686 | 100.1313 | 106.0971 | 108.0179 | 88.8691
874.7478 | 764.7478 | 307.0834 | 154.5018 | 191.394 | 158.0744 | 117.8925 | 100.2582 | 106.2313 | 108.1434 | 88.9853
875.7493 | 765.7493 | 307.0195 | 154.5787 | 191.5305 | 158.1697 | 118.0388 | 100.3851 | 106.3669 | 108.268 | 89.0609
876.7507 | 766.7507 | 306.9934 | 154.7126 | 191.638 | 158.2896 | 118.1646 | 100.5118 | 106.5063 | 108.3797 | 89.1739
877.7521 | 767.7521 | 307.0185 | 154.7849 | 191.7472 | 158.3843 | 118.3092 | 100.6677 | 106.6425 | 108.5021 | 89.2808
878.7536 | 768.7536 | 306.982 | 154.894 | 191.8679 | 158.4777 | 118.4415 | 100.8063 | 106.7837 | 108.6109 | 89.3775
879.755 | 769.755 | 306.9254 | 155.0051 | 191.9654 | 158.5942 | 118.5942 | 100.9012 | 106.9238 | 108.7162 | 89.5101
880.7465 | 770.7465 | 306.9368 | 155.0938 | 192.1131 | 158.6754 | 118.728 | 101.0809 | 107.0654 | 108.8215 | 89.6166
881.7479 | 771.7479 | 306.9482 | 155.2062 | 192.1966 | 158.7892 | 118.8578 | 101.2043 | 107.2007 | 108.9363 | 89.7281
882.7493 | 772.7493 | 306.9568 | 155.2759 | 192.3427 | 158.8761 | 119.0114 | 101.3281 | 107.3377 | 109.0517 | 89.83
883.7508 | 773.7508 | 306.926 | 155.4092 | 192.4372 | 158.9808 | 119.1155 | 101.4501 | 107.4772 | 109.1684 | 89.945
884.7522 | 774.7522 | 306.8878 | 155.4741 | 192.5475 | 159.0636 | 119.2813 | 101.6194 | 107.6125 | 109.2888 | 90.0393
885.7537 | 775.7537 | 306.7909 | 155.5945 | 192.6593 | 159.1733 | 119.418 | 101.752 | 107.746 | 109.4121 | 90.1487
886.7551 | 776.7551 | 306.751 | 155.6897 | 192.7835 | 159.271 | 119.5558 | 101.8532 | 107.8912 | 109.5313 | 90.2445
887.7565 | 777.7565 | 306.7708 | 155.76 | 192.9005 | 159.3607 | 119.6934 | 102.0194 | 108.0258 | 109.6437 | 90.3769
888.758 | 778.758 | 306.7258 | 155.8978 | 192.9991 | 159.4735 | 119.8233 | 102.1571 | 108.1667 | 109.7545 | 90.4883
889.7494 | 779.7494 | 306.6537 | 155.9732 | 193.0947 | 159.5461 | 119.9643 | 102.2805 | 108.3079 | 109.878 | 90.5776
890.7508 | 780.7508 | 306.5882 | 156.0966 | 193.1842 | 159.651 | 120.1002 | 102.3967 | 108.4446 | 110.0029 | 90.6775
891.7523 | 781.7523 | 306.5744 | 156.164 | 193.3373 | 159.7451 | 120.2494 | 102.571 | 108.575 | 110.1248 | 90.7783
892.7537 | 782.7537 | 306.6772 | 156.2965 | 193.4185 | 159.8459 | 120.387 | 102.6973 | 108.7138 | 110.231 | 90.9132
893.7552 | 783.7552 | 306.6844 | 156.357 | 193.5467 | 159.9334 | 120.5307 | 102.8029 | 108.8475 | 110.3522 | 91.0272
894.7566 | 784.7566 | 306.6631 | 156.4667 | 193.6617 | 160.0382 | 120.6581 | 102.9687 | 108.9793 | 110.4885 | 91.0986
895.748 | 785.748 | 306.7766 | 156.5614 | 193.7447 | 160.1319 | 120.8059 | 103.1047 | 109.1148 | 110.61 | 91.2057
896.7495 | 786.7495 | 306.7446 | 156.6607 | 193.8567 | 160.2152 | 120.9357 | 103.2212 | 109.2451 | 110.7197 | 91.3218
897.7509 | 787.7509 | 306.6986 | 156.7679 | 193.9691 | 160.3265 | 121.0718 | 103.3428 | 109.3803 | 110.8475 | 91.4168
898.7523 | 788.7523 | 306.6155 | 156.8343 | 194.0799 | 160.4236 | 121.2083 | 103.5122 | 109.5194 | 110.9797 | 91.5147
899.7538 | 789.7538 | 306.5856 | 156.9496 | 194.1919 | 160.5167 | 121.3442 | 103.6331 | 109.6579 | 111.0933 | 91.6196
900.7552 | 790.7552 | 306.5667 | 157.033 | 194.3098 | 160.6147 | 121.4835 | 103.7417 | 109.7891 | 111.2018 | 91.7315
901.7466 | 791.7466 | 306.5657 | 157.1488 | 194.4176 | 160.7092 | 121.6345 | 103.9087 | 109.92 | 111.3274 | 91.8507
902.7481 | 792.7481 | 306.5141 | 157.2423 | 194.5168 | 160.8045 | 121.7567 | 104.0452 | 110.0609 | 111.4373 | 91.9667
903.7495 | 793.7495 | 306.4284 | 157.3319 | 194.6116 | 160.8914 | 121.8894 | 104.1621 | 110.193 | 111.5648 | 92.0565
904.751 | 794.751 | 306.3394 | 157.4319 | 194.6843 | 161.0034 | 122.0315 | 104.2813 | 110.3191 | 111.6826 | 92.1405
905.7524 | 795.7524 | 306.2977 | 157.5156 | 194.809 | 161.096 | 122.1733 | 104.4487 | 110.4569 | 111.8061 | 92.2424
906.7538 | 796.7538 | 306.2375 | 157.6239 | 194.8906 | 161.1928 | 122.3069 | 104.5786 | 110.5917 | 111.8947 | 92.3721
907.7553 | 797.7553 | 306.2347 | 157.6871 | 195.0243 | 161.2702 | 122.4388 | 104.6894 | 110.7299 | 112.0356 | 92.4634
908.7567 | 798.7567 | 306.2041 | 157.8023 | 195.1385 | 161.3617 | 122.5681 | 104.8567 | 110.8591 | 112.1562 | 92.587
909.7482 | 799.7482 | 306.0715 | 157.892 | 195.2347 | 161.4626 | 122.7138 | 104.9885 | 110.9992 | 112.2797 | 92.6877
910.7496 | 800.7496 | 306.067 | 157.9869 | 195.3078 | 161.5552 | 122.8454 | 105.1105 | 111.1294 | 112.3993 | 92.785
911.751 | 801.751 | 306.0145 | 158.0782 | 195.4548 | 161.6554 | 122.9801 | 105.2322 | 111.2615 | 112.5134 | 92.8838
912.7525 | 802.7525 | 305.9656 | 158.1545 | 195.5639 | 161.7577 | 123.1335 | 105.3985 | 111.3933 | 112.6167 | 93.016
913.7539 | 803.7539 | 305.9372 | 158.2751 | 195.6545 | 161.849 | 123.2585 | 105.5282 | 111.5337 | 112.7482 | 93.1008
914.7554 | 804.7554 | 305.8293 | 158.3226 | 195.7697 | 161.9187 | 123.3946 | 105.6373 | 111.6596 | 112.8721 | 93.2104
915.7568 | 805.7568 | 305.7328 | 158.4641 | 195.8455 | 162.024 | 123.5368 | 105.7929 | 111.7902 | 112.9963 | 93.2995
916.7482 | 806.7482 | 305.6855 | 158.5257 | 195.9791 | 162.1118 | 123.6577 | 105.9308 | 111.9228 | 113.1217 | 93.4093
917.7497 | 807.7497 | 305.7297 | 158.6301 | 196.0587 | 162.2136 | 123.8029 | 106.0415 | 112.0555 | 113.2333 | 93.5256
918.7511 | 808.7511 | 305.7557 | 158.7267 | 196.1762 | 162.2927 | 123.9407 | 106.1682 | 112.1874 | 113.3625 | 93.608
919.7525 | 809.7525 | 305.8114 | 158.8155 | 196.2902 | 162.3994 | 124.0923 | 106.3356 | 112.3195 | 113.4802 | 93.716
920.754 | 810.754 | 305.7599 | 158.8997 | 196.323 | 162.48 | 124.2172 | 106.4637 | 112.441 | 113.5932 | 93.8387
921.7454 | 811.7454 | 305.6194 | 158.9914 | 196.4684 | 162.5736 | 124.3574 | 106.5645 | 112.5881 | 113.719 | 93.9079
922.7468 | 812.7468 | 305.6143 | 159.0865 | 196.5683 | 162.673 | 124.4952 | 106.7269 | 112.7138 | 113.8447 | 94.0101
923.7483 | 813.7483 | 305.6023 | 159.1525 | 196.6824 | 162.748 | 124.6213 | 106.8658 | 112.844 | 113.9643 | 94.1257
924.7497 | 814.7497 | 305.5425 | 159.2787 | 196.7574 | 162.859 | 124.7584 | 106.9821 | 112.9785 | 114.0916 | 94.2449
925.7512 | 815.7512 | 305.4949 | 159.3435 | 196.879 | 162.9379 | 124.8895 | 107.1068 | 113.1013 | 114.2121 | 94.3449
926.7526 | 816.7526 | 305.5315 | 159.4536 | 196.9621 | 163.0329 | 125.0338 | 107.2601 | 113.2328 | 114.3381 | 94.4547
927.754 | 817.754 | 305.5011 | 159.539 | 197.0137 | 163.1258 | 125.1675 | 107.3912 | 113.3642 | 114.4653 | 94.5411
928.7555 | 818.7555 | 305.3867 | 159.6364 | 197.1494 | 163.2322 | 125.2989 | 107.4951 | 113.4914 | 114.5789 | 94.6459
929.7569 | 819.7569 | 305.3287 | 159.7131 | 197.2647 | 163.3144 | 125.4295 | 107.6643 | 113.614 | 114.7038 | 94.7422
930.7484 | 820.7484 | 305.3431 | 159.8007 | 197.34 | 163.386 | 125.567 | 107.8032 | 113.7468 | 114.8211 | 94.84
931.7498 | 821.7498 | 305.4373 | 159.8993 | 197.4472 | 163.4933 | 125.6987 | 107.9145 | 113.8807 | 114.9392 | 94.9504
932.7512 | 822.7512 | 305.4764 | 159.9818 | 197.532 | 163.584 | 125.8313 | 108.0291 | 114.0108 | 115.0496 | 95.0622
933.7527 | 823.7527 | 305.5073 | 160.0801 | 197.6374 | 163.6746 | 125.9679 | 108.1886 | 114.1396 | 115.1934 | 95.1367
934.7541 | 824.7541 | 305.4548 | 160.1651 | 197.7475 | 163.7549 | 126.0948 | 108.3243 | 114.2723 | 115.3049 | 95.2707
935.7556 | 825.7556 | 305.4523 | 160.2497 | 197.862 | 163.8492 | 126.236 | 108.429 | 114.4087 | 115.4269 | 95.3642
936.757 | 826.757 | 305.4698 | 160.3668 | 197.9661 | 163.9473 | 126.3713 | 108.5956 | 114.5385 | 115.5291 | 95.4745
937.7484 | 827.7484 | 305.5603 | 160.4308 | 198.0539 | 164.0143 | 126.4926 | 108.7293 | 114.6678 | 115.6712 | 95.5698
938.7499 | 828.7499 | 305.6072 | 160.5382 | 198.1433 | 164.109 | 126.6283 | 108.8308 | 114.7977 | 115.7786 | 95.6764
939.7513 | 829.7513 | 305.58 | 160.6245 | 198.2702 | 164.2097 | 126.7491 | 108.9587 | 114.9321 | 115.9039 | 95.7647
940.7527 | 830.7527 | 305.5501 | 160.724 | 198.3801 | 164.2829 | 126.9031 | 109.1241 | 115.0678 | 116.0299 | 95.8681
941.7542 | 831.7542 | 305.5158 | 160.8061 | 198.4837 | 164.3806 | 127.0279 | 109.2585 | 115.1862 | 116.1372 | 95.9869
942.7456 | 832.7456 | 305.5445 | 160.8713 | 198.5572 | 164.4692 | 127.1546 | 109.3634 | 115.3198 | 116.255 | 96.0848
943.747 | 833.747 | 305.6129 | 160.9823 | 198.6578 | 164.5586 | 127.289 | 109.5246 | 115.4469 | 116.3735 | 96.1848
944.7485 | 834.7485 | 305.7194 | 161.0492 | 198.7948 | 164.6418 | 127.4244 | 109.6649 | 115.5821 | 116.4867 | 96.2991
945.7499 | 835.7499 | 305.7923 | 161.171 | 198.8487 | 164.7505 | 127.5542 | 109.7668 | 115.7141 | 116.6138 | 96.389
946.7514 | 836.7514 | 305.8857 | 161.2606 | 198.947 | 164.8343 | 127.6882 | 109.8922 | 115.8413 | 116.7306 | 96.4866
947.7528 | 837.7528 | 305.8753 | 161.3462 | 199.0469 | 164.9309 | 127.8202 | 110.0532 | 115.9713 | 116.8373 | 96.6125
948.7542 | 838.7542 | 305.7818 | 161.4228 | 199.101 | 165.0302 | 127.9568 | 110.1808 | 116.096 | 116.9651 | 96.6989
949.7457 | 839.7457 | 305.8052 | 161.5159 | 199.2369 | 165.1137 | 128.0926 | 110.2904 | 116.2249 | 117.0751 | 96.8052
950.7471 | 840.7471 | 305.7735 | 161.6098 | 199.3503 | 165.2067 | 128.2223 | 110.4473 | 116.3593 | 117.2111 | 96.8903
951.7485 | 841.7485 | 305.7229 | 161.698 | 199.4367 | 165.2991 | 128.3542 | 110.5793 | 116.4891 | 117.3231 | 96.9983
952.75 | 842.75 | 305.7437 | 161.7876 | 199.5155 | 165.3745 | 128.4783 | 110.697 | 116.6198 | 117.4387 | 97.1021
953.7514 | 843.7514 | 305.7568 | 161.8696 | 199.6255 | 165.4712 | 128.6065 | 110.8202 | 116.7469 | 117.547 | 97.1952
954.7529 | 844.7529 | 305.7711 | 161.9493 | 199.727 | 165.5578 | 128.7524 | 110.9828 | 116.8775 | 117.6479 | 97.3324
955.7543 | 845.7543 | 305.7647 | 162.0537 | 199.7917 | 165.6605 | 128.8875 | 111.112 | 117.0123 | 117.7739 | 97.4324
956.7557 | 846.7557 | 305.8042 | 162.1533 | 199.8834 | 165.7563 | 129.0144 | 111.2082 | 117.147 | 117.8863 | 97.5362
957.7572 | 847.7572 | 305.8469 | 162.2393 | 200.0311 | 165.8389 | 129.1442 | 111.3803 | 117.274 | 118.0115 | 97.6105
958.7586 | 848.7586 | 305.9089 | 162.3198 | 200.1104 | 165.9321 | 129.284 | 111.5115 | 117.4061 | 118.1194 | 97.7279
959.7501 | 849.7501 | 306.0221 | 162.4194 | 200.2077 | 166.0112 | 129.412 | 111.6221 | 117.5426 | 118.2377 | 97.8377
960.7515 | 850.7515 | 306.0585 | 162.5084 | 200.3336 | 166.0922 | 129.5358 | 111.747 | 117.6672 | 118.3572 | 97.935
961.7529 | 851.7529 | 306.1787 | 162.5921 | 200.4182 | 166.1941 | 129.6802 | 111.9102 | 117.801 | 118.4615 | 98.0458
962.7544 | 852.7544 | 306.2391 | 162.6896 | 200.5248 | 166.2667 | 129.8047 | 112.0373 | 117.9272 | 118.5739 | 98.1573
963.7458 | 853.7458 | 306.3586 | 162.775 | 200.5999 | 166.3648 | 129.9318 | 112.1262 | 118.0561 | 118.7028 | 98.2453
964.7472 | 854.7472 | 306.4059 | 162.8609 | 200.7072 | 166.4456 | 130.0699 | 112.2973 | 118.1837 | 118.8018 | 98.3557
965.7487 | 855.7487 | 306.4257 | 162.9516 | 200.8133 | 166.5435 | 130.2067 | 112.4322 | 118.3147 | 118.9304 | 98.4447
966.7501 | 856.7501 | 306.4296 | 163.0092 | 200.8932 | 166.6302 | 130.3299 | 112.5451 | 118.4463 | 119.0523 | 98.5675
967.7516 | 857.7516 | 306.3666 | 163.1146 | 201.0086 | 166.7043 | 130.4612 | 112.6686 | 118.574 | 119.1629 | 98.659
968.753 | 858.753 | 306.3441 | 163.2186 | 201.0931 | 166.7937 | 130.5892 | 112.8273 | 118.7057 | 119.2688 | 98.7755
969.7544 | 859.7544 | 306.4048 | 163.2944 | 201.1848 | 166.8887 | 130.7268 | 112.9684 | 118.8387 | 119.3745 | 98.8764
970.7559 | 860.7559 | 306.5054 | 163.3896 | 201.2785 | 166.9818 | 130.8474 | 113.0504 | 118.9764 | 119.4973 | 98.9605
971.7573 | 861.7573 | 306.5488 | 163.4684 | 201.3361 | 167.0739 | 130.9805 | 113.2212 | 119.1045 | 119.6158 | 99.0724
972.7487 | 862.7487 | 306.523 | 163.5552 | 201.4929 | 167.1581 | 131.113 | 113.3519 | 119.2279 | 119.739 | 99.1804
973.7502 | 863.7502 | 306.4263 | 163.6368 | 201.5591 | 167.2507 | 131.25 | 113.4645 | 119.3467 | 119.8606 | 99.2463
974.7516 | 864.7516 | 306.3799 | 163.7324 | 201.6535 | 167.3396 | 131.3653 | 113.5788 | 119.4829 | 119.9737 | 99.3729
975.7531 | 865.7531 | 306.2609 | 163.8202 | 201.731 | 167.4334 | 131.5066 | 113.7473 | 119.6102 | 120.0875 | 99.4718
976.7545 | 866.7545 | 306.1493 | 163.9236 | 201.8314 | 167.5166 | 131.6376 | 113.8744 | 119.7434 | 120.2004 | 99.5708
977.7559 | 867.7559 | 306.1102 | 163.9717 | 201.9324 | 167.5913 | 131.7689 | 113.9719 | 119.8745 | 120.311 | 99.6744
978.7474 | 868.7474 | 306.0888 | 164.0617 | 202.0584 | 167.6818 | 131.8825 | 114.1417 | 120.0074 | 120.4143 | 99.7871
979.7488 | 869.7488 | 306.0392 | 164.1406 | 202.1717 | 167.7747 | 132.0309 | 114.2786 | 120.1396 | 120.5374 | 99.8849
980.7502 | 870.7502 | 306.0993 | 164.2434 | 202.2701 | 167.8533 | 132.1567 | 114.3853 | 120.2674 | 120.64 | 100.0013
981.7517 | 871.7517 | 306.1805 | 164.3252 | 202.3074 | 167.9417 | 132.2787 | 114.5086 | 120.4031 | 120.7614 | 100.0919
982.7531 | 872.7531 | 306.1533 | 164.4186 | 202.4012 | 168.0134 | 132.4228 | 114.6702 | 120.5303 | 120.8736 | 100.1971
983.7546 | 873.7546 | 306.1699 | 164.4707 | 202.5276 | 168.0854 | 132.5517 | 114.7988 | 120.6607 | 120.98 | 100.3175
984.746 | 874.746 | 306.1011 | 164.5674 | 202.5688 | 168.1774 | 132.6814 | 114.8988 | 120.789 | 121.0918 | 100.423
985.8476 | 875.8476 | 306.048 | 164.6589 | 202.6769 | 168.2745 | 132.8222 | 115.06 | 120.9326 | 121.2333 | 100.5149
986.7489 | 876.7489 | 306.1133 | 164.7427 | 202.7975 | 168.3562 | 132.9396 | 115.1893 | 121.0453 | 121.3387 | 100.6122
987.7503 | 877.7503 | 306.1616 | 164.8125 | 202.8696 | 168.4302 | 133.0694 | 115.3101 | 121.1782 | 121.4445 | 100.7101
988.7518 | 878.7518 | 306.1234 | 164.9211 | 202.9829 | 168.527 | 133.1905 | 115.4209 | 121.3132 | 121.5414 | 100.8341
989.7532 | 879.7532 | 306.0452 | 164.9658 | 203.0741 | 168.6185 | 133.3194 | 115.5855 | 121.4352 | 121.6587 | 100.924
990.7546 | 880.7546 | 306.0707 | 165.0866 | 203.1686 | 168.7194 | 133.4518 | 115.7144 | 121.5786 | 121.7626 | 101.0434
991.7461 | 881.7461 | 305.9729 | 165.1442 | 203.267 | 168.7935 | 133.5707 | 115.8138 | 121.7039 | 121.8788 | 101.117
992.7475 | 882.7475 | 305.9349 | 165.2301 | 203.3199 | 168.8834 | 133.7129 | 115.9727 | 121.837 | 121.9862 | 101.2412
993.7489 | 883.7489 | 305.8266 | 165.315 | 203.444 | 168.9519 | 133.8555 | 116.1062 | 121.9642 | 122.0973 | 101.3274
994.7504 | 884.7504 | 305.8029 | 165.4375 | 203.5407 | 169.0426 | 133.9707 | 116.2154 | 122.0939 | 122.2094 | 101.4263
995.7518 | 885.7518 | 305.7939 | 165.4869 | 203.6388 | 169.1264 | 134.1067 | 116.3398 | 122.2278 | 122.3204 | 101.536
996.7533 | 886.7533 | 305.8259 | 165.5583 | 203.7047 | 169.1923 | 134.2402 | 116.5003 | 122.3608 | 122.4341 | 101.6147
997.7547 | 887.7547 | 305.7813 | 165.6768 | 203.8286 | 169.295 | 134.3595 | 116.6224 | 122.4934 | 122.5351 | 101.7288
998.7561 | 888.7561 | 305.7607 | 165.7193 | 203.9095 | 169.3804 | 134.4918 | 116.7259 | 122.6264 | 122.6534 | 101.8294
999.7476 | 889.7476 | 305.7117 | 165.834 | 204.0174 | 169.4666 | 134.6168 | 116.8845 | 122.7574 | 122.7583 | 101.941
1000.749 | 890.749 | 305.7785 | 165.8929 | 204.0975 | 169.5461 | 134.7545 | 117.0182 | 122.8885 | 122.8628 | 102.0579
1001.7504 | 891.7504 | 305.857 | 166.0131 | 204.1824 | 169.6197 | 134.8807 | 117.1274 | 123.0244 | 122.9728 | 102.1369
1002.7519 | 892.7519 | 305.916 | 166.1024 | 204.2937 | 169.7051 | 134.9948 | 117.2452 | 123.1577 | 123.08 | 102.2591
1003.7533 | 893.7533 | 305.9999 | 166.1761 | 204.3813 | 169.8034 | 135.1297 | 117.4118 | 123.286 | 123.1899 | 102.3605
1004.7548 | 894.7548 | 306.0882 | 166.2618 | 204.4773 | 169.88 | 135.2605 | 117.5362 | 123.419 | 123.2981 | 102.4781
1005.7562 | 895.7562 | 306.1382 | 166.3176 | 204.5671 | 169.9574 | 135.3903 | 117.6359 | 123.5461 | 123.4109 | 102.5651
1006.7476 | 896.7476 | 306.163 | 166.422 | 204.6375 | 170.0636 | 135.5104 | 117.7927 | 123.6792 | 123.5278 | 102.6608
1007.7491 | 897.7491 | 306.1908 | 166.4834 | 204.7631 | 170.1425 | 135.6365 | 117.9317 | 123.8171 | 123.646 | 102.7719
1008.7505 | 898.7505 | 306.2501 | 166.5953 | 204.8233 | 170.2254 | 135.7679 | 118.0374 | 123.9428 | 123.7513 | 102.8783
1009.752 | 899.752 | 306.2233 | 166.6678 | 204.9066 | 170.2932 | 135.904 | 118.1598 | 124.0836 | 123.8454 | 102.9884
1010.7534 | 900.7534 | 306.1761 | 166.7467 | 204.9975 | 170.3811 | 136.023 | 118.31 | 124.209 | 123.9681 | 103.097
1011.7548 | 901.7548 | 306.1287 | 166.8311 | 205.105 | 170.4593 | 136.1532 | 118.4487 | 124.3393 | 124.085 | 103.168
1012.7563 | 902.7563 | 306.1225 | 166.9145 | 205.1909 | 170.5397 | 136.2629 | 118.5393 | 124.4705 | 124.191 | 103.2672
1013.7577 | 903.7577 | 306.0867 | 167.0029 | 205.2702 | 170.6316 | 136.3975 | 118.7051 | 124.6015 | 124.2959 | 103.3723
1014.7491 | 904.7491 | 306.0702 | 167.0607 | 205.3672 | 170.715 | 136.53 | 118.8262 | 124.7362 | 124.3976 | 103.494
1015.7506 | 905.7506 | 306.1054 | 167.1902 | 205.4662 | 170.8019 | 136.6561 | 118.9447 | 124.8701 | 124.5083 | 103.6009
1016.752 | 906.752 | 306.1439 | 167.2386 | 205.5439 | 170.8737 | 136.7851 | 119.0643 | 124.9999 | 124.6004 | 103.6945
1017.7535 | 907.7535 | 306.1142 | 167.3482 | 205.6171 | 170.9644 | 136.9097 | 119.2173 | 125.1349 | 124.7183 | 103.8036
1018.7549 | 908.7549 | 306.1113 | 167.4076 | 205.738 | 171.031 | 137.037 | 119.3578 | 125.264 | 124.8341 | 103.8897
1019.7563 | 909.7563 | 306.1961 | 167.5004 | 205.8242 | 171.1206 | 137.1666 | 119.4388 | 125.3993 | 124.9388 | 103.9982
1020.7478 | 910.7478 | 306.231 | 167.563 | 205.8765 | 171.1894 | 137.2925 | 119.6136 | 125.5312 | 125.0414 | 104.1195
1021.7492 | 911.7492 | 306.3016 | 167.6611 | 205.9836 | 171.2656 | 137.421 | 119.741 | 125.6621 | 125.1491 | 104.1998
1022.7506 | 912.7506 | 306.3494 | 167.7387 | 206.0954 | 171.3517 | 137.5446 | 119.8504 | 125.7922 | 125.269 | 104.3121
1023.7521 | 913.7521 | 306.4207 | 167.814 | 206.2003 | 171.4273 | 137.6719 | 119.9603 | 125.9271 | 125.3781 | 104.4026
1024.7535 | 914.7535 | 306.4717 | 167.9246 | 206.2801 | 171.5032 | 137.7913 | 120.1219 | 126.0533 | 125.488 | 104.5094
1025.755 | 915.755 | 306.4616 | 167.9885 | 206.3669 | 171.5858 | 137.9216 | 120.2531 | 126.1788 | 125.6004 | 104.6223
1026.7464 | 916.7464 | 306.5027 | 168.0898 | 206.4519 | 171.664 | 138.0444 | 120.338 | 126.3134 | 125.7094 | 104.7129
1027.7478 | 917.7478 | 306.6387 | 168.1451 | 206.522 | 171.7351 | 138.1822 | 120.5051 | 126.4373 | 125.8159 | 104.835
1028.7493 | 918.7493 | 306.6813 | 168.2567 | 206.6446 | 171.8469 | 138.2936 | 120.6293 | 126.5603 | 125.9456 | 104.9165
1029.7507 | 919.7507 | 306.7652 | 168.3277 | 206.6848 | 171.9319 | 138.4238 | 120.7438 | 126.6927 | 126.0618 | 105.0127
1030.7521 | 920.7521 | 306.8979 | 168.4118 | 206.8308 | 172.0302 | 138.5508 | 120.8567 | 126.8161 | 126.1711 | 105.114
1031.7536 | 921.7536 | 307.0278 | 168.4939 | 206.84 | 172.1104 | 138.6732 | 121.0151 | 126.9387 | 126.2821 | 105.2075
1032.755 | 922.755 | 307.0847 | 168.5549 | 206.9863 | 172.183 | 138.8133 | 121.1437 | 127.0643 | 126.3966 | 105.3105
1033.7565 | 923.7565 | 307.0566 | 168.6594 | 207.0665 | 172.2585 | 138.9259 | 121.2353 | 127.1989 | 126.5019 | 105.4209
1034.7479 | 924.7479 | 307.0786 | 168.724 | 207.1621 | 172.3134 | 139.0633 | 121.4009 | 127.3219 | 126.6133 | 105.5184
1035.7493 | 925.7493 | 307.0103 | 168.8224 | 207.2301 | 172.4107 | 139.1778 | 121.5189 | 127.4495 | 126.7338 | 105.6143
1036.7508 | 926.7508 | 306.987 | 168.8962 | 207.3436 | 172.4814 | 139.3069 | 121.6388 | 127.5784 | 126.8507 | 105.6917
1037.7522 | 927.7522 | 306.8991 | 168.9628 | 207.3595 | 172.5688 | 139.4343 | 121.7505 | 127.698 | 126.9655 | 105.7901
1038.7537 | 928.7537 | 306.8135 | 169.043 | 207.4871 | 172.643 | 139.5542 | 121.9055 | 127.8217 | 127.0744 | 105.908
1039.7551 | 929.7551 | 306.725 | 169.1276 | 207.5704 | 172.7336 | 139.6792 | 122.0369 | 127.9517 | 127.1708 | 106.0302
1040.7565 | 930.7565 | 306.5734 | 169.2243 | 207.614 | 172.8264 | 139.8008 | 122.1273 | 128.0726 | 127.2844 | 106.0947
1041.748 | 931.748 | 306.5271 | 169.3143 | 207.7402 | 172.91 | 139.9302 | 122.2846 | 128.207 | 127.4161 | 106.1939
1042.7494 | 932.7494 | 306.4764 | 169.3807 | 207.8489 | 172.9791 | 140.0636 | 122.4111 | 128.3307 | 127.5228 | 106.3118
1043.7508 | 933.7508 | 306.5512 | 169.4637 | 207.9483 | 173.0662 | 140.1724 | 122.523 | 128.4604 | 127.6411 | 106.3839
1044.7523 | 934.7523 | 306.5644 | 169.5585 | 208.0075 | 173.135 | 140.3024 | 122.6299 | 128.5868 | 127.7337 | 106.4892
1045.7537 | 935.7537 | 306.6052 | 169.6066 | 208.1194 | 173.2126 | 140.4279 | 122.806 | 128.7087 | 127.8509 | 106.6071
1046.7552 | 936.7552 | 306.5904 | 169.7008 | 208.1539 | 173.2968 | 140.5496 | 122.916 | 128.8365 | 127.9738 | 106.6929
1047.7466 | 937.7466 | 306.5563 | 169.772 | 208.2828 | 173.3772 | 140.668 | 123.006 | 128.9607 | 128.0933 | 106.7971
1048.748 | 938.748 | 306.5327 | 169.8482 | 208.3639 | 173.4601 | 140.8022 | 123.1657 | 129.0833 | 128.2183 | 106.8764
1049.7495 | 939.7495 | 306.5619 | 169.9291 | 208.4354 | 173.5313 | 140.9323 | 123.2953 | 129.205 | 128.3372 | 106.9573
1050.7509 | 940.7509 | 306.4981 | 169.9957 | 208.5184 | 173.6025 | 141.044 | 123.4028 | 129.3263 | 128.4399 | 107.087
1051.7523 | 941.7523 | 306.4371 | 170.0937 | 208.6111 | 173.6946 | 141.1643 | 123.5116 | 129.4464 | 128.566 | 107.1713
1052.7538 | 942.7538 | 306.295 | 170.168 | 208.6985 | 173.7836 | 141.2927 | 123.6663 | 129.5698 | 128.6878 | 107.2625
1053.7552 | 943.7552 | 306.2233 | 170.2507 | 208.7956 | 173.8585 | 141.4114 | 123.7965 | 129.6915 | 128.8013 | 107.3495
1054.7567 | 944.7567 | 306.2272 | 170.3028 | 208.8797 | 173.9168 | 141.5327 | 123.8965 | 129.8177 | 128.908 | 107.4598
1055.7481 | 945.7481 | 306.1737 | 170.4101 | 208.9786 | 174.0073 | 141.6551 | 124.0467 | 129.9436 | 129.0178 | 107.5532
1056.7495 | 946.7495 | 306.1259 | 170.454 | 209.0482 | 174.0761 | 141.7814 | 124.1775 | 130.0598 | 129.128 | 107.6591
1057.751 | 947.751 | 306.0093 | 170.5566 | 209.1314 | 174.1622 | 141.9082 | 124.2879 | 130.1945 | 129.2316 | 107.7599
1058.7524 | 948.7524 | 305.9289 | 170.6198 | 209.1869 | 174.2341 | 142.0253 | 124.3917 | 130.3231 | 129.3381 | 107.8592
1059.7539 | 949.7539 | 305.7731 | 170.715 | 209.2882 | 174.3179 | 142.1503 | 124.5478 | 130.4412 | 129.4584 | 107.9325
1060.7553 | 950.7553 | 305.7117 | 170.7881 | 209.3662 | 174.3935 | 142.2718 | 124.6735 | 130.5692 | 129.5578 | 108.0573
1061.7567 | 951.7567 | 305.6582 | 170.8646 | 209.4411 | 174.4412 | 142.3915 | 124.7663 | 130.6924 | 129.6698 | 108.1474
1062.7482 | 952.7482 | 305.6644 | 170.94 | 209.5252 | 174.5187 | 142.5131 | 124.928 | 130.8203 | 129.7768 | 108.253
1063.7496 | 953.7496 | 305.6422 | 171.0127 | 209.6119 | 174.6041 | 142.6377 | 125.0529 | 130.9527 | 129.8762 | 108.3542
1064.751 | 954.751 | 305.604 | 171.0965 | 209.6894 | 174.6587 | 142.7602 | 125.1592 | 131.0772 | 130.0055 | 108.4378
1065.7525 | 955.7525 | 305.6009 | 171.1692 | 209.7659 | 174.7692 | 142.8932 | 125.2683 | 131.2031 | 130.1285 | 108.5284
1066.7539 | 956.7539 | 305.4997 | 171.2488 | 209.8438 | 174.8412 | 143.0015 | 125.4254 | 131.3262 | 130.2196 | 108.6284
1067.7554 | 957.7554 | 305.4421 | 171.3144 | 209.9253 | 174.9126 | 143.1307 | 125.5501 | 131.4455 | 130.343 | 108.7313
1068.7468 | 958.7468 | 305.507 | 171.3846 | 209.9923 | 174.986 | 143.2518 | 125.6387 | 131.5769 | 130.4471 | 108.8165
1069.7482 | 959.7482 | 305.5409 | 171.479 | 210.0623 | 175.0666 | 143.3831 | 125.7997 | 131.703 | 130.5552 | 108.9344
1070.7497 | 960.7497 | 305.6005 | 171.5306 | 210.1371 | 175.1199 | 143.5119 | 125.9245 | 131.8275 | 130.6705 | 109.0077
1071.7511 | 961.7511 | 305.6947 | 171.6201 | 210.2536 | 175.2061 | 143.6216 | 126.0199 | 131.9509 | 130.7695 | 109.122
1072.7525 | 962.7525 | 305.7545 | 171.6866 | 210.2915 | 175.2901 | 143.7528 | 126.1418 | 132.0756 | 130.8716 | 109.2303
1073.754 | 963.754 | 305.8202 | 171.7713 | 210.3943 | 175.345 | 143.8728 | 126.2926 | 132.2053 | 130.9969 | 109.3003
1074.7454 | 964.7454 | 305.8604 | 171.8484 | 210.4775 | 175.4325 | 143.9799 | 126.4126 | 132.3278 | 131.0996 | 109.4087
1075.7468 | 965.7468 | 305.8214 | 171.9211 | 210.5592 | 175.5096 | 144.1061 | 126.5067 | 132.4541 | 131.2155 | 109.5121
1076.7483 | 966.7483 | 305.9502 | 172.021 | 210.6337 | 175.5742 | 144.2236 | 126.6567 | 132.5685 | 131.3373 | 109.6025
1077.7497 | 967.7497 | 305.9847 | 172.0769 | 210.7183 | 175.6388 | 144.3534 | 126.7807 | 132.6976 | 131.4461 | 109.7055
1078.7512 | 968.7512 | 305.9004 | 172.1614 | 210.7952 | 175.7274 | 144.4582 | 126.896 | 132.8098 | 131.5628 | 109.7916
1079.7526 | 969.7526 | 305.8242 | 172.2109 | 210.8746 | 175.8039 | 144.5907 | 126.9996 | 132.9337 | 131.6763 | 109.8993
1080.754 | 970.754 | 305.8221 | 172.293 | 210.9542 | 175.8774 | 144.699 | 127.1496 | 133.0445 | 131.7914 | 109.9967
1081.7555 | 971.7555 | 305.9192 | 172.3826 | 211.0029 | 175.9552 | 144.8216 | 127.2727 | 133.1662 | 131.9104 | 110.0823
1082.7569 | 972.7569 | 305.8995 | 172.4571 | 211.1118 | 176.0255 | 144.9437 | 127.3623 | 133.2863 | 132.0366 | 110.1651
1083.7584 | 973.7584 | 305.8319 | 172.5371 | 211.1812 | 176.1153 | 145.0618 | 127.5194 | 133.4096 | 132.1332 | 110.2826
1084.7498 | 974.7498 | 305.7862 | 172.623 | 211.2553 | 176.1884 | 145.1871 | 127.638 | 133.5272 | 132.245 | 110.3645
1085.7512 | 975.7512 | 305.7692 | 172.6973 | 211.302 | 176.2666 | 145.2978 | 127.7446 | 133.6547 | 132.3696 | 110.45
1086.7527 | 976.7527 | 305.7459 | 172.7438 | 211.4062 | 176.3413 | 145.4042 | 127.8508 | 133.7791 | 132.4769 | 110.5358
1087.7541 | 977.7541 | 305.8024 | 172.8363 | 211.4693 | 176.4117 | 145.5388 | 128.0108 | 133.8961 | 132.58 | 110.6506
1088.7556 | 978.7556 | 305.8328 | 172.8866 | 211.5932 | 176.4694 | 145.652 | 128.1322 | 134.0221 | 132.6965 | 110.7418
1089.757 | 979.757 | 305.9434 | 172.9681 | 211.7036 | 176.5519 | 145.7763 | 128.2207 | 134.1438 | 132.806 | 110.8289
1090.7484 | 980.7484 | 306.0181 | 173.0433 | 211.7786 | 176.6395 | 145.8892 | 128.3747 | 134.2622 | 132.9193 | 110.9229
1091.7499 | 981.7499 | 306.0485 | 173.1117 | 211.8609 | 176.6996 | 146.0095 | 128.4958 | 134.3858 | 133.0374 | 111.0103
1092.7513 | 982.7513 | 306.0631 | 173.1926 | 211.9138 | 176.7318 | 146.1248 | 128.6047 | 134.5068 | 133.1463 | 111.1063
1093.7527 | 983.7527 | 306.1343 | 173.2651 | 211.9983 | 176.8398 | 146.235 | 128.6998 | 134.6197 | 133.2706 | 111.2016
1094.7542 | 984.7542 | 306.1269 | 173.3357 | 212.0363 | 176.9093 | 146.362 | 128.8602 | 134.7375 | 133.3855 | 111.2942
1095.7556 | 985.7556 | 306.1406 | 173.4051 | 212.1228 | 176.9714 | 146.4855 | 128.9878 | 134.853 | 133.4997 | 111.3784
1096.747 | 986.747 | 306.083 | 173.495 | 212.2233 | 177.0586 | 146.598 | 129.0676 | 134.9741 | 133.6101 | 111.4832
1097.7485 | 987.7485 | 305.9643 | 173.56 | 212.2993 | 177.1103 | 146.7167 | 129.2213 | 135.0871 | 133.7131 | 111.5762
1098.7499 | 988.7499 | 305.8563 | 173.6248 | 212.3688 | 177.1864 | 146.8385 | 129.343 | 135.2186 | 133.7986 | 111.6864
1099.7514 | 989.7514 | 305.8962 | 173.6754 | 212.4566 | 177.2621 | 146.963 | 129.4574 | 135.3313 | 133.9411 | 111.7619
1100.7528 | 990.7528 | 305.9425 | 173.7833 | 212.5383 | 177.3372 | 147.0741 | 129.5568 | 135.4575 | 134.0434 | 111.8499
1101.7542 | 991.7542 | 305.9318 | 173.8354 | 212.6074 | 177.4018 | 147.1792 | 129.7105 | 135.5734 | 134.1404 | 111.9564
1102.7557 | 992.7557 | 305.9882 | 173.9325 | 212.7038 | 177.4679 | 147.3092 | 129.8264 | 135.6986 | 134.2549 | 112.0435
1103.7571 | 993.7571 | 305.929 | 173.9864 | 212.7798 | 177.5526 | 147.425 | 129.9152 | 135.8249 | 134.37 | 112.1437
1104.7486 | 994.7486 | 305.8299 | 174.0686 | 212.8478 | 177.6394 | 147.5407 | 130.0749 | 135.9484 | 134.4745 | 112.2351
1105.75 | 995.75 | 305.7484 | 174.1496 | 212.9264 | 177.7159 | 147.6542 | 130.1933 | 136.0636 | 134.5924 | 112.3322
1106.7514 | 996.7514 | 305.816 | 174.2185 | 213.0308 | 177.7827 | 147.7841 | 130.3009 | 136.1872 | 134.7018 | 112.4332
1107.7529 | 997.7529 | 305.8761 | 174.2998 | 213.0791 | 177.8662 | 147.897 | 130.3945 | 136.3126 | 134.8146 | 112.5184
1108.7543 | 998.7543 | 305.9277 | 174.3557 | 213.1979 | 177.9193 | 148.0088 | 130.5551 | 136.4271 | 134.9243 | 112.6058
1109.7558 | 999.7558 | 306.0283 | 174.4405 | 213.2623 | 177.9994 | 148.1283 | 130.6672 | 136.549 | 135.0284 | 112.7184
1110.7472 | 1000.7472 | 306.1015 | 174.4883 | 213.3306 | 178.079 | 148.2438 | 130.7534 | 136.6715 | 135.1404 | 112.8053
1111.7486 | 1001.7486 | 306.1446 | 174.5947 | 213.4257 | 178.1527 | 148.3672 | 130.9118 | 136.7981 | 135.2464 | 112.8791
1112.7501 | 1002.7501 | 306.1973 | 174.6295 | 213.5011 | 178.2138 | 148.4823 | 131.0346 | 136.918 | 135.3612 | 112.975
1113.7515 | 1003.7515 | 306.2594 | 174.7322 | 213.5545 | 178.2965 | 148.5951 | 131.1307 | 137.0405 | 135.4533 | 113.0808
1114.7529 | 1004.7529 | 306.3087 | 174.8036 | 213.5953 | 178.3689 | 148.7083 | 131.2378 | 137.1617 | 135.5689 | 113.1589
1115.7544 | 1005.7544 | 306.3147 | 174.8571 | 213.7262 | 178.4199 | 148.8306 | 131.3919 | 137.2847 | 135.6605 | 113.2775
1116.7458 | 1006.7458 | 306.2335 | 174.943 | 213.8249 | 178.5104 | 148.9367 | 131.5091 | 137.4053 | 135.7833 | 113.3465
1117.7472 | 1007.7472 | 306.2573 | 174.987 | 213.8707 | 178.5697 | 149.0555 | 131.5988 | 137.5248 | 135.8874 | 113.4396
1118.7487 | 1008.7487 | 306.3387 | 175.082 | 213.9254 | 178.658 | 149.1613 | 131.7367 | 137.6502 | 135.9989 | 113.5441
1119.7501 | 1009.7501 | 306.3369 | 175.1319 | 213.9911 | 178.7113 | 149.3085 | 131.8729 | 137.7664 | 136.0995 | 113.6374
1120.7516 | 1010.7516 | 306.3575 | 175.232 | 214.0985 | 178.8022 | 149.3917 | 131.968 | 137.8864 | 136.2079 | 113.716
1121.753 | 1011.753 | 306.385 | 175.2637 | 214.1733 | 178.8608 | 149.5255 | 132.0813 | 138.0032 | 136.3137 | 113.8301
1122.7544 | 1012.7544 | 306.3938 | 175.3793 | 214.2023 | 178.9418 | 149.633 | 132.2208 | 138.1231 | 136.4266 | 113.91
1123.7559 | 1013.7559 | 306.2268 | 175.4318 | 214.1272 | 179.0174 | 149.7463 | 132.3338 | 138.2414 | 136.546 | 113.999
1124.7573 | 1014.7573 | 306.0679 | 175.485 | 214.2722 | 179.0811 | 149.8625 | 132.4263 | 138.3644 | 136.6485 | 114.0966
1125.7487 | 1015.7487 | 305.9015 | 175.578 | 214.4208 | 179.1594 | 149.9748 | 132.5719 | 138.4878 | 136.7594 | 114.1923
1126.7502 | 1016.7502 | 305.8086 | 175.6166 | 214.5092 | 179.2172 | 150.0939 | 132.6966 | 138.6075 | 136.8646 | 114.2741
1127.7516 | 1017.7516 | 305.7953 | 175.7199 | 214.5781 | 179.3042 | 150.2022 | 132.7985 | 138.7286 | 136.9544 | 114.397
1128.7531 | 1018.7531 | 305.7761 | 175.756 | 214.6572 | 179.3702 | 150.3285 | 132.9022 | 138.8567 | 137.0628 | 114.4633
1129.7545 | 1019.7545 | 305.7597 | 175.8588 | 214.7399 | 179.4366 | 150.4371 | 133.0529 | 138.9807 | 137.1765 | 114.5459
1130.7559 | 1020.7559 | 305.7506 | 175.9086 | 214.7765 | 179.4974 | 150.5673 | 133.1689 | 139.1115 | 137.2626 | 114.6653
1131.7474 | 1021.7474 | 305.7888 | 175.9872 | 214.8943 | 179.5851 | 150.6598 | 133.2534 | 139.2375 | 137.3666 | 114.7424
1132.7488 | 1022.7488 | 305.7593 | 176.0389 | 214.9173 | 179.6543 | 150.7778 | 133.4173 | 139.3602 | 137.4588 | 114.8476
1133.7503 | 1023.7503 | 305.6925 | 176.1164 | 214.9907 | 179.7099 | 150.8929 | 133.5341 | 139.4882 | 137.5631 | 114.925
1134.7517 | 1024.7517 | 305.6153 | 176.1837 | 215.096 | 179.7855 | 151.0154 | 133.6394 | 139.6112 | 137.6603 | 115.0347
1135.7531 | 1025.7531 | 305.5832 | 176.2436 | 215.1553 | 179.8403 | 151.1368 | 133.7292 | 139.7429 | 137.7577 | 115.1185
1136.7546 | 1026.7546 | 305.5914 | 176.3322 | 215.2393 | 179.9217 | 151.2403 | 133.8852 | 139.8701 | 137.8428 | 115.2181
1137.746 | 1027.746 | 305.5544 | 176.3646 | 215.302 | 179.9833 | 151.3708 | 134.0099 | 139.9924 | 137.9466 | 115.325
1138.7474 | 1028.7474 | 305.4806 | 176.4805 | 215.398 | 180.0663 | 151.4592 | 134.079 | 140.1134 | 138.0487 | 115.4029
1139.7889 | 1029.7889 | 305.4137 | 176.515 | 215.4767 | 180.122 | 151.5949 | 134.2446 | 140.2456 | 138.1534 | 115.5067
1140.7503 | 1030.7503 | 305.3235 | 176.6078 | 215.5269 | 180.194 | 151.6983 | 134.3576 | 140.3718 | 138.2251 | 115.6233
1141.7518 | 1031.7518 | 305.3005 | 176.6551 | 215.5672 | 180.2525 | 151.8204 | 134.4651 | 140.4933 | 138.3323 | 115.7106
1142.7532 | 1032.7532 | 305.3664 | 176.7348 | 215.6713 | 180.3279 | 151.9278 | 134.557 | 140.6122 | 138.4425 | 115.7806
1143.7546 | 1033.7546 | 305.4199 | 176.8281 | 215.7348 | 180.4103 | 152.0495 | 134.7047 | 140.7328 | 138.5375 | 115.8902
1144.7561 | 1034.7561 | 305.4472 | 176.8607 | 215.8459 | 180.4513 | 152.163 | 134.8307 | 140.8604 | 138.6272 | 115.9883
1145.7575 | 1035.7575 | 305.5422 | 176.9573 | 215.8939 | 180.5288 | 152.2722 | 134.8994 | 140.9889 | 138.7181 | 116.0976
1146.7489 | 1036.7489 | 305.5977 | 176.975 | 215.9742 | 180.6014 | 152.3887 | 135.0654 | 141.1067 | 138.8211 | 116.1744
1147.7504 | 1037.7504 | 305.5852 | 177.0853 | 216.0257 | 180.6825 | 152.5048 | 135.1799 | 141.234 | 138.9075 | 116.2879
1148.7518 | 1038.7518 | 305.6117 | 177.1338 | 216.1179 | 180.7279 | 152.6174 | 135.2926 | 141.3567 | 139.0147 | 116.3593
1149.7533 | 1039.7533 | 305.6761 | 177.2112 | 216.1597 | 180.8075 | 152.7274 | 135.3772 | 141.4876 | 139.0843 | 116.4802
1150.7547 | 1040.7547 | 305.7082 | 177.2665 | 216.1888 | 180.87 | 152.847 | 135.5347 | 141.5982 | 139.1959 | 116.5614
1151.7561 | 1041.7561 | 305.6731 | 177.3634 | 216.3144 | 180.9465 | 152.9595 | 135.647 | 141.7345 | 139.2915 | 116.6478
1152.7476 | 1042.7476 | 305.7013 | 177.4245 | 216.383 | 181.0111 | 153.0866 | 135.7289 | 141.8539 | 139.3848 | 116.7476
1153.749 | 1043.749 | 305.8286 | 177.4823 | 216.4256 | 181.0635 | 153.1961 | 135.8876 | 141.9821 | 139.4721 | 116.8594
1154.7504 | 1044.7504 | 305.9408 | 177.5728 | 216.5307 | 181.1318 | 153.3071 | 135.994 | 142.1045 | 139.5761 | 116.9428
1155.7519 | 1045.7519 | 306.0142 | 177.6055 | 216.6073 | 181.1932 | 153.4298 | 136.1079 | 142.2301 | 139.6544 | 117.0441
1156.7533 | 1046.7533 | 306.1214 | 177.7124 | 216.6807 | 181.2761 | 153.5349 | 136.2007 | 142.3524 | 139.764 | 117.1449
1157.7548 | 1047.7548 | 306.1474 | 177.7498 | 216.7229 | 181.339 | 153.6418 | 136.3555 | 142.4711 | 139.8601 | 117.2079
1158.7462 | 1048.7462 | 306.2102 | 177.8447 | 216.7828 | 181.4049 | 153.7507 | 136.4567 | 142.6022 | 139.9414 | 117.312
1159.7476 | 1049.7476 | 306.2961 | 177.8928 | 216.8719 | 181.4694 | 153.8786 | 136.5467 | 142.7184 | 140.0476 | 117.4056
1160.7491 | 1050.7491 | 306.3684 | 177.9768 | 216.9452 | 181.5499 | 153.9881 | 136.6866 | 142.8424 | 140.1382 | 117.5121
1161.7505 | 1051.7505 | 306.4741 | 178.0334 | 217.0519 | 181.6187 | 154.111 | 136.8194 | 142.966 | 140.2226 | 117.6104
1162.752 | 1052.752 | 306.6062 | 178.119 | 217.0972 | 181.6946 | 154.2075 | 136.9152 | 143.0888 | 140.3145 | 117.6902
1163.7534 | 1053.7534 | 306.6633 | 178.1851 | 217.2048 | 181.7526 | 154.315 | 137.0138 | 143.2101 | 140.4178 | 117.7769
1164.7548 | 1054.7548 | 306.7135 | 178.2421 | 217.2699 | 181.7547 | 154.437 | 137.164 | 143.3337 | 140.5025 | 117.8935
1165.7563 | 1055.7563 | 306.7559 | 178.3228 | 217.3277 | 181.8319 | 154.5552 | 137.2792 | 143.4544 | 140.6095 | 117.983
1166.7577 | 1056.7577 | 306.7815 | 178.3643 | 217.4105 | 181.9003 | 154.6503 | 137.3625 | 143.58 | 140.7081 | 118.0691
1167.7491 | 1057.7491 | 306.799 | 178.4483 | 217.4472 | 182.0035 | 154.7733 | 137.5053 | 143.6874 | 140.811 | 118.1589
1168.7506 | 1058.7506 | 306.7638 | 178.4799 | 217.5031 | 182.0566 | 154.8875 | 137.6276 | 143.8023 | 140.8945 | 118.2787
1169.752 | 1059.752 | 306.7788 | 178.576 | 217.6009 | 182.1418 | 155.0069 | 137.7293 | 143.9255 | 140.9928 | 118.3574
1170.7535 | 1060.7535 | 306.7184 | 178.6327 | 217.6842 | 182.2096 | 155.1106 | 137.8311 | 144.0373 | 141.1157 | 118.4256
1171.7549 | 1061.7549 | 306.5956 | 178.708 | 217.7606 | 182.2634 | 155.2135 | 137.9725 | 144.1416 | 141.2102 | 118.5429
1172.7563 | 1062.7563 | 306.551 | 178.7846 | 217.8387 | 182.3369 | 155.329 | 138.0855 | 144.2507 | 141.3129 | 118.6104
1173.7478 | 1063.7478 | 306.5836 | 178.8336 | 217.889 | 182.3745 | 155.4402 | 138.1738 | 144.3702 | 141.4157 | 118.7066
1174.7492 | 1064.7492 | 306.5568 | 178.9245 | 217.9711 | 182.4557 | 155.5487 | 138.313 | 144.4768 | 141.5278 | 118.7914
1175.7506 | 1065.7506 | 306.5077 | 178.9574 | 218.0288 | 182.5167 | 155.6652 | 138.4397 | 144.592 | 141.6332 | 118.8877
1176.7521 | 1066.7521 | 306.4118 | 179.0518 | 218.1201 | 182.5935 | 155.7627 | 138.5377 | 144.6964 | 141.7343 | 118.9653
1177.7535 | 1067.7535 | 306.2401 | 179.0884 | 218.169 | 182.6469 | 155.8656 | 138.6264 | 144.8102 | 141.839 | 119.0579
1178.755 | 1068.755 | 306.1775 | 179.1714 | 218.2085 | 182.7353 | 155.9904 | 138.7759 | 144.9205 | 141.9314 | 119.1681
1179.7464 | 1069.7464 | 306.1445 | 179.2245 | 218.2685 | 182.7914 | 156.105 | 138.8916 | 145.0358 | 142.0467 | 119.2211
1180.7478 | 1070.7478 | 306.0258 | 179.3105 | 218.3481 | 182.8685 | 156.1993 | 138.9652 | 145.1467 | 142.1456 | 119.3286
1181.7493 | 1071.7493 | 305.9903 | 179.3468 | 218.461 | 182.9283 | 156.32 | 139.1243 | 145.2513 | 142.238 | 119.4336
1182.7507 | 1072.7507 | 305.9057 | 179.4369 | 218.5075 | 183.0092 | 156.418 | 139.2294 | 145.3546 | 142.347 | 119.4937
1183.7522 | 1073.7522 | 305.9302 | 179.4776 | 218.5588 | 183.0589 | 156.5297 | 139.3391 | 145.4669 | 142.4615 | 119.5793
1184.7536 | 1074.7536 | 305.9002 | 179.5501 | 218.6128 | 183.115 | 156.6375 | 139.4242 | 145.5778 | 142.5616 | 119.663
1185.755 | 1075.755 | 305.8309 | 179.6125 | 218.6513 | 183.192 | 156.7547 | 139.5712 | 145.6834 | 142.6429 | 119.7734
1186.7565 | 1076.7565 | 305.7312 | 179.6686 | 218.747 | 183.2397 | 156.8654 | 139.6933 | 145.7978 | 142.7647 | 119.8447
1187.7479 | 1077.7479 | 305.7084 | 179.7549 | 218.831 | 183.3113 | 156.97 | 139.7659 | 145.9058 | 142.8744 | 119.9204
1188.7493 | 1078.7493 | 305.6856 | 179.7875 | 218.8872 | 183.3664 | 157.0871 | 139.9177 | 146.0155 | 142.96 | 120.0344
1189.7508 | 1079.7508 | 305.6183 | 179.8702 | 218.9303 | 183.4245 | 157.1732 | 140.0223 | 146.1271 | 143.0501 | 120.1273
1190.7522 | 1080.7522 | 305.5519 | 179.9127 | 219.0218 | 183.4503 | 157.3025 | 140.1263 | 146.2376 | 143.1649 | 120.202
1191.7537 | 1081.7537 | 305.5283 | 179.9845 | 219.0619 | 183.5248 | 157.3962 | 140.2154 | 146.3387 | 143.2766 | 120.2677
1192.7551 | 1082.7551 | 305.4019 | 180.0361 | 219.1011 | 183.6022 | 157.5129 | 140.3636 | 146.454 | 143.3756 | 120.3718
1193.7565 | 1083.7565 | 305.3794 | 180.1324 | 219.1219 | 183.6639 | 157.5967 | 140.4632 | 146.5573 | 143.4864 | 120.4456
1194.758 | 1084.758 | 305.3998 | 180.1676 | 219.1804 | 183.7311 | 157.7254 | 140.5561 | 146.657 | 143.5763 | 120.5547
1195.7494 | 1085.7494 | 305.4274 | 180.2364 | 219.3048 | 183.8109 | 157.8296 | 140.6959 | 146.7689 | 143.6762 | 120.6363
1196.7508 | 1086.7508 | 305.5322 | 180.2829 | 219.3766 | 183.84 | 157.9404 | 140.8137 | 146.878 | 143.7811 | 120.7411
1197.7523 | 1087.7523 | 305.6373 | 180.3621 | 219.4228 | 183.9398 | 158.0382 | 140.9102 | 146.9887 | 143.8765 | 120.8141
1198.7537 | 1088.7537 | 305.6809 | 180.4318 | 219.4817 | 184.004 | 158.1513 | 140.9946 | 147.0994 | 143.9726 | 120.892
1199.7552 | 1089.7552 | 305.6694 | 180.4611 | 219.5866 | 184.0427 | 158.2475 | 141.1508 | 147.2068 | 144.0756 | 120.9725
1200.7566 | 1090.7566 | 305.6786 | 180.5522 | 219.6012 | 184.1156 | 158.3622 | 141.2531 | 147.3198 | 144.1702 | 121.0711
1201.748 | 1091.748 | 305.6681 | 180.6072 | 219.7105 | 184.1649 | 158.4707 | 141.3356 | 147.4188 | 144.271 | 121.1388
1202.7495 | 1092.7495 | 305.5509 | 180.6847 | 219.7604 | 184.2442 | 158.5691 | 141.4779 | 147.5336 | 144.356 | 121.2586
1203.7509 | 1093.7509 | 305.5725 | 180.7286 | 219.8624 | 184.3124 | 158.6989 | 141.5962 | 147.6424 | 144.4549 | 121.3418
1204.7523 | 1094.7523 | 305.6215 | 180.7951 | 219.9278 | 184.356 | 158.7859 | 141.6863 | 147.7569 | 144.5602 | 121.4108
1205.7538 | 1095.7538 | 305.726 | 180.8473 | 219.9774 | 184.4365 | 158.8988 | 141.7831 | 147.8712 | 144.6519 | 121.5037
1206.7552 | 1096.7552 | 305.7285 | 180.9145 | 220.0349 | 184.4661 | 158.9922 | 141.9347 | 147.9764 | 144.7479 | 121.5957
1207.7567 | 1097.7567 | 305.7413 | 180.9922 | 220.0821 | 184.5299 | 159.1117 | 142.0355 | 148.0919 | 144.8459 | 121.6813
1208.7481 | 1098.7481 | 305.6936 | 181.0364 | 220.1349 | 184.5836 | 159.2126 | 142.116 | 148.2027 | 144.9377 | 121.7722
1209.7495 | 1099.7495 | 305.5178 | 181.1079 | 220.172 | 184.6737 | 159.3189 | 142.2613 | 148.3119 | 145.032 | 121.8743
1210.751 | 1100.751 | 305.476 | 181.1421 | 220.257 | 184.7531 | 159.4342 | 142.378 | 148.4145 | 145.134 | 121.9416
1211.7524 | 1101.7524 | 305.4978 | 181.2148 | 220.2719 | 184.8041 | 159.5324 | 142.4665 | 148.5217 | 145.2282 | 122.048
1212.7539 | 1102.7539 | 305.4048 | 181.2567 | 220.3661 | 184.8477 | 159.6378 | 142.5592 | 148.6324 | 145.3395 | 122.1123
1213.7553 | 1103.7553 | 305.3375 | 181.3332 | 220.4343 | 184.9297 | 159.7399 | 142.7066 | 148.7341 | 145.4371 | 122.2147
1214.7567 | 1104.7567 | 305.3007 | 181.3693 | 220.5172 | 184.9711 | 159.8384 | 142.8226 | 148.8365 | 145.5263 | 122.3173
1215.7482 | 1105.7482 | 305.3539 | 181.484 | 220.598 | 185.0534 | 159.9446 | 142.8804 | 148.9437 | 145.6338 | 122.3693
1216.7496 | 1106.7496 | 305.4094 | 181.4948 | 220.642 | 185.0878 | 160.0592 | 143.0396 | 149.06 | 145.7306 | 122.4699
1217.751 | 1107.751 | 305.4931 | 181.5736 | 220.6916 | 185.157 | 160.1629 | 143.1563 | 149.1568 | 145.8265 | 122.5407
1218.7525 | 1108.7525 | 305.4617 | 181.6606 | 220.6896 | 185.2083 | 160.2791 | 143.241 | 149.2728 | 145.9234 | 122.6556
1219.7539 | 1109.7539 | 305.4007 | 181.6847 | 220.7371 | 185.2773 | 160.3861 | 143.3435 | 149.3801 | 146.0208 | 122.7154
1220.7554 | 1110.7554 | 305.3697 | 181.7932 | 220.8312 | 185.3378 | 160.4787 | 143.4825 | 149.4859 | 146.1113 | 122.8026
1221.7468 | 1111.7468 | 305.3376 | 181.8236 | 220.9557 | 185.3857 | 160.5949 | 143.5992 | 149.5985 | 146.1954 | 122.9046
1222.7482 | 1112.7482 | 305.4543 | 181.9086 | 221.0062 | 185.4741 | 160.6793 | 143.6592 | 149.7153 | 146.2769 | 122.9873
1223.7497 | 1113.7497 | 305.5069 | 181.9602 | 221.0959 | 185.5252 | 160.8016 | 143.8182 | 149.8293 | 146.3666 | 123.0793
1224.7511 | 1114.7511 | 305.5956 | 182.041 | 221.1296 | 185.603 | 160.9002 | 143.9138 | 149.9465 | 146.4597 | 123.1629
1225.7525 | 1115.7525 | 305.5637 | 182.0635 | 221.2071 | 185.6469 | 161.0029 | 144.0218 | 150.054 | 146.5344 | 123.2552
1226.754 | 1116.754 | 305.5869 | 182.1301 | 221.2458 | 185.7226 | 161.1121 | 144.1 | 150.1706 | 146.625 | 123.3491
1227.7454 | 1117.7454 | 305.6044 | 182.1869 | 221.3398 | 185.7711 | 161.2179 | 144.2503 | 150.2887 | 146.7043 | 123.434
1228.7469 | 1118.7469 | 305.5776 | 182.2591 | 221.3665 | 185.8378 | 161.3184 | 144.3589 | 150.4027 | 146.7966 | 123.5119
1229.7483 | 1119.7483 | 305.572 | 182.3319 | 221.4325 | 185.9093 | 161.4224 | 144.4311 | 150.5199 | 146.8745 | 123.6185
1230.7497 | 1120.7497 | 305.5157 | 182.3782 | 221.5053 | 185.9579 | 161.5303 | 144.5751 | 150.6397 | 146.9657 | 123.7028
1231.7512 | 1121.7512 | 305.4344 | 182.4669 | 221.6035 | 186.0266 | 161.6402 | 144.6862 | 150.7487 | 147.0454 | 123.8074
1232.7526 | 1122.7526 | 305.4063 | 182.4986 | 221.6151 | 186.0736 | 161.7453 | 144.7892 | 150.8735 | 147.1232 | 123.9107
1233.7541 | 1123.7541 | 305.3951 | 182.5922 | 221.7365 | 186.1247 | 161.8431 | 144.8748 | 150.9859 | 147.1989 | 123.9969
1234.7555 | 1124.7555 | 305.3793 | 182.6186 | 221.7912 | 186.1889 | 161.9562 | 145.017 | 151.1026 | 147.2821 | 124.1011
1235.7569 | 1125.7569 | 305.3637 | 182.7068 | 221.8618 | 186.2656 | 162.0534 | 145.1169 | 151.2234 | 147.3605 | 124.1928
1236.7484 | 1126.7484 | 305.3963 | 182.7396 | 221.9373 | 186.3152 | 162.1539 | 145.208 | 151.3389 | 147.4439 | 124.2851
1237.7498 | 1127.7498 | 305.5691 | 182.814 | 221.9567 | 186.3786 | 162.2532 | 145.3365 | 151.4548 | 147.5183 | 124.3692
1238.7512 | 1128.7512 | 305.7741 | 182.8819 | 222.0256 | 186.4582 | 162.378 | 145.4532 | 151.5782 | 147.5899 | 124.478
1239.7527 | 1129.7527 | 305.8159 | 182.9498 | 222.0937 | 186.5062 | 162.4653 | 145.5529 | 151.6969 | 147.688 | 124.5394
1240.7541 | 1130.7541 | 305.807 | 183.0186 | 222.1679 | 186.574 | 162.5807 | 145.6305 | 151.8024 | 147.7661 | 124.6554
1241.7556 | 1131.7556 | 305.7329 | 183.0661 | 222.2228 | 186.6225 | 162.6845 | 145.7788 | 151.9297 | 147.8353 | 124.7401
1242.747 | 1132.747 | 305.7169 | 183.13 | 222.2867 | 186.701 | 162.7931 | 145.8918 | 152.0414 | 147.9362 | 124.8282
1243.7484 | 1133.7484 | 305.657 | 183.1752 | 222.3471 | 186.7584 | 162.9134 | 145.964 | 152.1529 | 148.0158 | 124.9263
1244.7499 | 1134.7499 | 305.6837 | 183.2801 | 222.4105 | 186.8296 | 163.0101 | 146.0994 | 152.2666 | 148.1023 | 124.9977
1245.7513 | 1135.7513 | 305.6955 | 183.3088 | 222.4684 | 186.8714 | 163.1176 | 146.2198 | 152.3918 | 148.1804 | 125.1123
1246.7527 | 1136.7527 | 305.8271 | 183.386 | 222.5302 | 186.953 | 163.2071 | 146.3044 | 152.5027 | 148.2705 | 125.1899
1247.7542 | 1137.7542 | 305.9377 | 183.4045 | 222.6217 | 186.9995 | 163.3266 | 146.4024 | 152.6126 | 148.3497 | 125.2953
1248.7456 | 1138.7456 | 305.9325 | 183.5056 | 222.6386 | 187.0502 | 163.4205 | 146.5367 | 152.7302 | 148.4218 | 125.3768
1249.747 | 1139.747 | 306.0038 | 183.5331 | 222.724 | 187.1152 | 163.535 | 146.6554 | 152.8433 | 148.5148 | 125.4568
1250.7485 | 1140.7485 | 306.1056 | 183.6181 | 222.752 | 187.1496 | 163.6271 | 146.7125 | 152.9615 | 148.5839 | 125.5848
1251.7499 | 1141.7499 | 306.2884 | 183.6925 | 222.8533 | 187.198 | 163.7342 | 146.8629 | 153.0725 | 148.6949 | 125.6505
1252.7514 | 1142.7514 | 306.4332 | 183.7234 | 222.911 | 187.2511 | 163.84 | 146.9664 | 153.1788 | 148.771 | 125.7484
1253.7528 | 1143.7528 | 306.4968 | 183.7976 | 222.9572 | 187.3382 | 163.938 | 147.07 | 153.2848 | 148.8725 | 125.8075
1254.7542 | 1144.7542 | 306.4196 | 183.8376 | 223.0302 | 187.4052 | 164.0367 | 147.158 | 153.3884 | 148.9693 | 125.9039
1255.7557 | 1145.7557 | 306.4218 | 183.9132 | 223.068 | 187.4715 | 164.1483 | 147.2885 | 153.5015 | 149.0469 | 126.0047
1256.7471 | 1146.7471 | 306.5134 | 183.9436 | 223.1463 | 187.5079 | 164.2509 | 147.4083 | 153.6021 | 149.1331 | 126.0831
1257.7486 | 1147.7486 | 306.6774 | 184.0435 | 223.1962 | 187.5772 | 164.3412 | 147.4692 | 153.7145 | 149.2229 | 126.1761
1258.75 | 1148.75 | 306.7284 | 184.0504 | 223.2608 | 187.6212 | 164.4572 | 147.6191 | 153.8194 | 149.3231 | 126.2681
1259.7514 | 1149.7514 | 306.7525 | 184.1539 | 223.3259 | 187.6839 | 164.5452 | 147.7233 | 153.9234 | 149.4165 | 126.3291
1260.7529 | 1150.7529 | 306.8184 | 184.1948 | 223.3895 | 187.7582 | 164.655 | 147.8169 | 154.0428 | 149.5073 | 126.4345
1261.7543 | 1151.7543 | 306.846 | 184.2401 | 223.4605 | 187.7997 | 164.7501 | 147.9065 | 154.1477 | 149.5863 | 126.5018
1262.7558 | 1152.7558 | 306.7901 | 184.31 | 223.544 | 187.8799 | 164.8594 | 148.0524 | 154.2618 | 149.6688 | 126.5995
1263.7472 | 1153.7472 | 306.7202 | 184.354 | 223.6026 | 187.9473 | 164.9563 | 148.1615 | 154.3672 | 149.76 | 126.6864
1264.7486 | 1154.7486 | 306.7124 | 184.4492 | 223.6031 | 188.0199 | 165.0566 | 148.2256 | 154.4771 | 149.839 | 126.7811
1265.7501 | 1155.7501 | 306.7762 | 184.4712 | 223.6854 | 188.0624 | 165.169 | 148.3673 | 154.5859 | 149.936 | 126.8646
1266.7515 | 1156.7515 | 306.8385 | 184.5752 | 223.7655 | 188.117 | 165.2637 | 148.4747 | 154.7007 | 150.0101 | 126.95
1267.7529 | 1157.7529 | 306.8032 | 184.6047 | 223.8047 | 188.1721 | 165.3836 | 148.5802 | 154.8026 | 150.1061 | 127.0247
1268.7544 | 1158.7544 | 306.6988 | 184.696 | 223.8696 | 188.2677 | 165.4601 | 148.6525 | 154.9186 | 150.187 | 127.1017
1269.7458 | 1159.7458 | 306.6548 | 184.7249 | 223.9616 | 188.2911 | 165.574 | 148.8034 | 155.0325 | 150.2659 | 127.2127
1270.7573 | 1160.7573 | 306.6401 | 184.7998 | 224.0305 | 188.3687 | 165.6787 | 148.9019 | 155.1322 | 150.3578 | 127.289
1271.7487 | 1161.7487 | 306.4675 | 184.8756 | 224.0714 | 188.423 | 165.7576 | 148.9713 | 155.2474 | 150.4318 | 127.3823
1272.7501 | 1162.7501 | 306.3502 | 184.9046 | 224.0936 | 188.4573 | 165.8768 | 149.1176 | 155.3504 | 150.5117 | 127.4827
1273.7516 | 1163.7516 | 306.3418 | 184.9932 | 224.1967 | 188.5332 | 165.9678 | 149.2251 | 155.4657 | 150.6051 | 127.5595
1274.753 | 1164.753 | 306.2975 | 185.0133 | 224.1899 | 188.5812 | 166.079 | 149.3199 | 155.5653 | 150.6916 | 127.6511
1275.7544 | 1165.7544 | 306.2005 | 185.1072 | 224.2796 | 188.6401 | 166.1473 | 149.3936 | 155.6803 | 150.7793 | 127.7339
1276.7559 | 1166.7559 | 306.1181 | 185.1346 | 224.3917 | 188.6959 | 166.2839 | 149.5419 | 155.7921 | 150.8552 | 127.8227
1277.7573 | 1167.7573 | 306.0511 | 185.2295 | 224.3982 | 188.7739 | 166.3774 | 149.6399 | 155.8996 | 150.9399 | 127.902
1278.7488 | 1168.7488 | 305.9241 | 185.2244 | 224.4455 | 188.7998 | 166.4817 | 149.7106 | 156.0111 | 151.0294 | 127.9743
1279.7502 | 1169.7502 | 305.7965 | 185.3328 | 224.5226 | 188.8687 | 166.571 | 149.8502 | 156.1092 | 151.1017 | 128.0695
1280.7516 | 1170.7516 | 305.6112 | 185.3745 | 224.5827 | 188.9139 | 166.6817 | 149.9653 | 156.2272 | 151.1689 | 128.1936
1281.7531 | 1171.7531 | 305.5889 | 185.4245 | 224.6757 | 188.9584 | 166.7825 | 150.0603 | 156.3405 | 151.2723 | 128.251
1282.7545 | 1172.7545 | 305.5988 | 185.5008 | 224.6394 | 189.0231 | 166.8725 | 150.1302 | 156.4445 | 151.3497 | 128.3476
1283.7559 | 1173.7559 | 305.4972 | 185.5343 | 224.68 | 189.0697 | 166.9857 | 150.2871 | 156.5567 | 151.4219 | 128.4437
1284.7474 | 1174.7474 | 305.4399 | 185.6224 | 224.7708 | 189.1438 | 167.077 | 150.3734 | 156.6783 | 151.5212 | 128.511
1285.8389 | 1175.8389 | 305.3888 | 185.6416 | 224.8664 | 189.1971 | 167.1862 | 150.4642 | 156.7993 | 151.5895 | 128.6228
1286.7503 | 1176.7503 | 305.3282 | 185.7411 | 224.9252 | 189.2513 | 167.2795 | 150.5896 | 156.9021 | 151.6699 | 128.7051
1287.7517 | 1177.7517 | 305.2909 | 185.7475 | 224.941 | 189.2837 | 167.3893 | 150.7068 | 157.0097 | 151.734 | 128.7768
1288.7531 | 1178.7531 | 305.1825 | 185.8679 | 224.9894 | 189.3778 | 167.4718 | 150.7834 | 157.1176 | 151.8242 | 128.8558
1289.7546 | 1179.7546 | 305.1507 | 185.8627 | 225.0639 | 189.4254 | 167.5855 | 150.8826 | 157.2348 | 151.8754 | 128.9644
1290.756 | 1180.756 | 305.2334 | 185.937 | 225.1519 | 189.495 | 167.6951 | 151.0182 | 157.3479 | 151.9694 | 129.0543
1291.7474 | 1181.7474 | 305.2471 | 186.0109 | 225.1857 | 189.5321 | 167.7753 | 151.1281 | 157.4457 | 152.0496 | 129.1358
1292.7489 | 1182.7489 | 305.1892 | 186.0494 | 225.266 | 189.5852 | 167.8835 | 151.198 | 157.566 | 152.1371 | 129.2354
1293.7503 | 1183.7503 | 305.1949 | 186.1373 | 225.2737 | 189.6587 | 167.9758 | 151.3287 | 157.6644 | 152.2192 | 129.3058
1294.7518 | 1184.7518 | 305.3471 | 186.1645 | 225.34 | 189.7091 | 168.0861 | 151.4443 | 157.7775 | 152.2823 | 129.4106
1295.7532 | 1185.7532 | 305.4707 | 186.2403 | 225.4243 | 189.7775 | 168.1801 | 151.5353 | 157.8798 | 152.3933 | 129.4904
1296.7546 | 1186.7546 | 305.469 | 186.2645 | 225.4765 | 189.8129 | 168.2759 | 151.6185 | 157.9903 | 152.4804 | 129.5461
1297.7561 | 1187.7561 | 305.5666 | 186.3529 | 225.5155 | 189.862 | 168.3733 | 151.7505 | 158.0969 | 152.5694 | 129.6628
1298.7575 | 1188.7575 | 305.5976 | 186.3757 | 225.5772 | 189.8984 | 168.482 | 151.8696 | 158.2047 | 152.6604 | 129.7063
1299.7489 | 1189.7489 | 305.5929 | 186.4613 | 225.6186 | 189.9401 | 168.5689 | 151.92 | 158.3084 | 152.7281 | 129.8244
1300.7504 | 1190.7504 | 305.6425 | 186.5226 | 225.6915 | 189.99 | 168.6782 | 152.0611 | 158.418 | 152.8198 | 129.9078
1301.7518 | 1191.7518 | 305.678 | 186.5582 | 225.7508 | 190.0523 | 168.7629 | 152.1754 | 158.5164 | 152.9097 | 129.9975
1302.7533 | 1192.7533 | 305.7354 | 186.6564 | 225.7539 | 190.1326 | 168.8504 | 152.2637 | 158.6256 | 152.9881 | 130.0813
1303.7547 | 1193.7547 | 305.7956 | 186.6656 | 225.8605 | 190.186 | 168.9623 | 152.3459 | 158.7246 | 153.0646 | 130.1593
1304.7561 | 1194.7561 | 305.7781 | 186.7487 | 225.887 | 190.2617 | 169.0605 | 152.4884 | 158.8265 | 153.1454 | 130.2576
1305.7576 | 1195.7576 | 305.7885 | 186.781 | 225.9721 | 190.3012 | 169.1671 | 152.589 | 158.9307 | 153.2456 | 130.3231
1306.749 | 1196.749 | 305.7355 | 186.8771 | 226.0251 | 190.3747 | 169.2512 | 152.6447 | 159.0327 | 153.3368 | 130.3902
1307.7505 | 1197.7505 | 305.7381 | 186.8896 | 226.105 | 190.405 | 169.3572 | 152.794 | 159.1349 | 153.4351 | 130.4862
1308.7519 | 1198.7519 | 305.7549 | 186.9611 | 226.1759 | 190.4655 | 169.4589 | 152.8986 | 159.2363 | 153.49 | 130.5871
1309.7533 | 1199.7533 | 305.7976 | 187.0205 | 226.237 | 190.5101 | 169.5575 | 152.9975 | 159.3458 | 153.6002 | 130.6572
1310.7548 | 1200.7548 | 305.8042 | 187.0465 | 226.2801 | 190.5512 | 169.634 | 153.0786 | 159.44 | 153.691 | 130.7302
1311.7562 | 1201.7562 | 305.8095 | 187.1369 | 226.3398 | 190.6529 | 169.7467 | 153.2112 | 159.5438 | 153.7795 | 130.8161
1312.7476 | 1202.7476 | 305.6356 | 187.1703 | 226.3777 | 190.6863 | 169.8473 | 153.3227 | 159.6404 | 153.8556 | 130.8965
1313.7491 | 1203.7491 | 305.4922 | 187.2408 | 226.4336 | 190.7434 | 169.9388 | 153.3739 | 159.7398 | 153.9541 | 130.981
1314.7505 | 1204.7505 | 305.4305 | 187.2775 | 226.4923 | 190.7916 | 170.0298 | 153.5161 | 159.8434 | 154.0381 | 131.0444
1315.752 | 1205.752 | 305.3638 | 187.3384 | 226.4933 | 190.836 | 170.1311 | 153.6164 | 159.94 | 154.1166 | 131.139
1316.7534 | 1206.7534 | 305.2684 | 187.3778 | 226.535 | 190.868 | 170.2229 | 153.7109 | 160.0389 | 154.225 | 131.2047
1317.7548 | 1207.7548 | 305.2043 | 187.4294 | 226.616 | 190.9284 | 170.3207 | 153.7956 | 160.1442 | 154.295 | 131.3134
1318.7563 | 1208.7563 | 305.1804 | 187.4949 | 226.6825 | 190.9859 | 170.4004 | 153.931 | 160.2381 | 154.3941 | 131.3929
1319.7577 | 1209.7577 | 305.2195 | 187.5514 | 226.7144 | 191.0254 | 170.514 | 154.0306 | 160.3334 | 154.4854 | 131.4421
1320.7592 | 1210.7592 | 305.254 | 187.6207 | 226.7073 | 191.0981 | 170.6004 | 154.0935 | 160.4373 | 154.5673 | 131.552
1321.7506 | 1211.7506 | 305.163 | 187.6237 | 226.8202 | 191.1446 | 170.6988 | 154.2396 | 160.52 | 154.6617 | 131.6114
1322.752 | 1212.752 | 305.0281 | 187.7175 | 226.8574 | 191.2088 | 170.7972 | 154.339 | 160.6208 | 154.7511 | 131.7045
1323.7535 | 1213.7535 | 305.059 | 187.7386 | 226.9056 | 191.2523 | 170.8929 | 154.4312 | 160.7198 | 154.852 | 131.7579
1324.7549 | 1214.7549 | 305.0685 | 187.8101 | 226.9592 | 191.304 | 170.9798 | 154.5028 | 160.8175 | 154.931 | 131.8452
1325.7463 | 1215.7463 | 305.1245 | 187.848 | 226.9788 | 191.3576 | 171.0851 | 154.6389 | 160.913 | 155.0213 | 131.9308
1326.7478 | 1216.7478 | 305.1689 | 187.9339 | 227.0681 | 191.3985 | 171.1673 | 154.7384 | 161.0153 | 155.0996 | 132.0181
1327.7492 | 1217.7492 | 305.1396 | 187.967 | 227.1284 | 191.4705 | 171.2509 | 154.7997 | 161.1111 | 155.189 | 132.057
1328.7506 | 1218.7506 | 305.2481 | 188.0423 | 227.1997 | 191.5257 | 171.3613 | 154.9348 | 161.2146 | 155.2794 | 132.1637
1329.7521 | 1219.7521 | 305.3231 | 188.084 | 227.2458 | 191.5588 | 171.4492 | 155.0449 | 161.3144 | 155.3465 | 132.2456
1330.7535 | 1220.7535 | 305.4081 | 188.1308 | 227.3025 | 191.6078 | 171.5447 | 155.1373 | 161.4251 | 155.442 | 132.3147
1331.755 | 1221.755 | 305.5364 | 188.1591 | 227.3359 | 191.6633 | 171.6408 | 155.2169 | 161.527 | 155.5102 | 132.4033
1332.7464 | 1222.7464 | 305.6675 | 188.2479 | 227.4144 | 191.7058 | 171.736 | 155.3473 | 161.6289 | 155.5803 | 132.5043
1333.7478 | 1223.7478 | 305.7097 | 188.3056 | 227.4922 | 191.7542 | 171.8356 | 155.4474 | 161.7252 | 155.6666 | 132.5764
1334.7493 | 1224.7493 | 305.821 | 188.3445 | 227.5246 | 191.822 | 171.9224 | 155.5113 | 161.8248 | 155.7452 | 132.6504
1335.7507 | 1225.7507 | 305.9176 | 188.4198 | 227.6297 | 191.8794 | 172.0179 | 155.6389 | 161.9294 | 155.8374 | 132.7191
1336.7522 | 1226.7522 | 306.0638 | 188.4777 | 227.625 | 191.9265 | 172.1088 | 155.748 | 162.0299 | 155.9199 | 132.8127
1337.7536 | 1227.7536 | 306.1835 | 188.5171 | 227.6691 | 191.9677 | 172.1978 | 155.8454 | 162.1258 | 155.9957 | 132.9043
1338.755 | 1228.755 | 306.2023 | 188.5795 | 227.7243 | 192.0288 | 172.3016 | 155.9188 | 162.2329 | 156.0897 | 132.9626
1339.7565 | 1229.7565 | 306.088 | 188.6029 | 227.8004 | 192.0702 | 172.386 | 156.0492 | 162.3237 | 156.1624 | 133.0781
1340.7479 | 1230.7479 | 306.1588 | 188.6691 | 227.8336 | 192.1366 | 172.4879 | 156.1528 | 162.4158 | 156.2617 | 133.119
1341.7493 | 1231.7493 | 306.2466 | 188.7295 | 227.9264 | 192.1751 | 172.59 | 156.2163 | 162.5232 | 156.3468 | 133.213
1342.7508 | 1232.7508 | 306.3268 | 188.784 | 227.9885 | 192.2484 | 172.6804 | 156.3557 | 162.6091 | 156.4427 | 133.2584
1343.7522 | 1233.7522 | 306.3963 | 188.8463 | 228.0032 | 192.2991 | 172.7725 | 156.4655 | 162.7138 | 156.5211 | 133.3806
1344.7537 | 1234.7537 | 306.3634 | 188.8863 | 228.0839 | 192.3501 | 172.8592 | 156.5411 | 162.8103 | 156.6089 | 133.4388
1345.7551 | 1235.7551 | 306.3866 | 188.9326 | 228.1191 | 192.394 | 172.9576 | 156.6143 | 162.905 | 156.7086 | 133.5081
1346.7565 | 1236.7565 | 306.3211 | 188.9997 | 228.1413 | 192.4586 | 173.0494 | 156.7539 | 163.0035 | 156.789 | 133.6101
1347.758 | 1237.758 | 306.2832 | 189.0506 | 228.2338 | 192.5215 | 173.1376 | 156.8607 | 163.0996 | 156.859 | 133.6828
1348.7494 | 1238.7494 | 306.3118 | 189.1121 | 228.3172 | 192.5618 | 173.2304 | 156.9135 | 163.2015 | 156.9425 | 133.7697
1349.7508 | 1239.7508 | 306.41 | 189.1695 | 228.3492 | 192.6332 | 173.3307 | 157.0523 | 163.3013 | 157.0413 | 133.8217
1350.7523 | 1240.7523 | 306.4968 | 189.2186 | 228.3814 | 192.6798 | 173.4182 | 157.1523 | 163.3906 | 157.119 | 133.8998
1351.7537 | 1241.7537 | 306.5863 | 189.2847 | 228.4744 | 192.7212 | 173.4944 | 157.2333 | 163.4905 | 157.1968 | 133.9873
1352.7552 | 1242.7552 | 306.5937 | 189.3237 | 228.4681 | 192.7823 | 173.5948 | 157.3135 | 163.5892 | 157.2803 | 134.0564
1353.7466 | 1243.7466 | 306.5927 | 189.3626 | 228.537 | 192.8132 | 173.6994 | 157.4555 | 163.6857 | 157.3634 | 134.1466
1354.748 | 1244.748 | 306.5788 | 189.3977 | 228.6394 | 192.8677 | 173.7843 | 157.5541 | 163.7883 | 157.4316 | 134.2465 | Time of first failure
1355.7495 | 1245.7495 | 306.5454 | 189.4641 | 228.6819 | 192.9269 | 173.8721 | 157.6093 | 163.8848 | 157.533 | 134.2957 | 1245 | 0
1356.7509 | 1246.7509 | 306.5303 | 189.5066 | 228.7245 | 192.9873 | 173.9654 | 157.7354 | 163.9822 | 157.6093 | 134.3733 | 1245 | 900
1357.7524 | 1247.7524 | 306.492 | 189.5751 | 228.7638 | 193.0293 | 174.0565 | 157.84 | 164.0757 | 157.685 | 134.4669
1358.7538 | 1248.7538 | 306.408 | 189.6092 | 228.8272 | 193.0828 | 174.1526 | 157.9257 | 164.1764 | 157.7694 | 134.5129
1359.7552 | 1249.7552 | 306.352 | 189.6584 | 228.8605 | 193.1246 | 174.2306 | 158.0022 | 164.273 | 157.8572 | 134.6117
1360.7467 | 1250.7467 | 306.3589 | 189.7007 | 228.9352 | 193.1719 | 174.339 | 158.186 | 164.3681 | 157.9355 | 134.7091
1361.7481 | 1251.7481 | 306.4742 | 189.7723 | 228.9208 | 193.2357 | 174.4215 | 158.2286 | 164.4653 | 158.0172 | 134.7656
1362.7495 | 1252.7495 | 306.4379 | 189.8346 | 228.9771 | 193.2849 | 174.5289 | 158.2932 | 164.5674 | 158.0949 | 134.8411
1363.751 | 1253.751 | 306.3835 | 189.841 | 229.0847 | 193.3323 | 174.6091 | 158.4583 | 164.654 | 158.1782 | 134.9245
1364.7524 | 1254.7524 | 306.3667 | 189.9389 | 229.1197 | 193.4075 | 174.6981 | 158.5296 | 164.7616 | 158.2504 | 135.0146
1365.7539 | 1255.7539 | 306.4131 | 189.9797 | 229.1661 | 193.4409 | 174.7942 | 158.623 | 164.8607 | 158.3295 | 135.0708
1366.7553 | 1256.7553 | 306.4767 | 190.0369 | 229.2548 | 193.4988 | 174.8793 | 158.6904 | 164.9646 | 158.4112 | 135.1441
1367.7467 | 1257.7467 | 306.3983 | 190.0724 | 229.2936 | 193.5525 | 174.9673 | 158.8299 | 165.0649 | 158.4554 | 135.2605
1368.7482 | 1258.7482 | 306.3288 | 190.1438 | 229.3523 | 193.6012 | 175.0566 | 158.921 | 165.1647 | 158.5552 | 135.3142
1369.7496 | 1259.7496 | 306.2898 | 190.1701 | 229.3951 | 193.6521 | 175.1599 | 158.9862 | 165.2681 | 158.618 | 135.3897
1370.751 | 1260.751 | 306.3553 | 190.2441 | 229.4684 | 193.6974 | 175.2464 | 159.1116 | 165.3694 | 158.6942 | 135.4988
1371.7525 | 1261.7525 | 306.4257 | 190.2483 | 229.5389 | 193.7327 | 175.3425 | 159.3181 | 165.4661 | 158.7659 | 135.564
1372.7539 | 1262.7539 | 306.4215 | 190.3635 | 229.5128 | 193.8002 | 175.4161 | 159.3012 | 165.5722 | 158.8297 | 135.6422
1373.7554 | 1263.7554 | 306.4188 | 190.3893 | 229.6153 | 193.8565 | 175.4973 | 159.3794 | 165.667 | 158.9025 | 135.7284
1374.7468 | 1264.7468 | 306.3855 | 190.4494 | 229.6433 | 193.9051 | 175.5931 | 159.497 | 165.7672 | 158.9777 | 135.8181
1375.7482 | 1265.7482 | 306.4053 | 190.51 | 229.7056 | 193.952 | 175.6761 | 159.6012 | 165.8646 | 159.0562 | 135.8855
1376.7497 | 1266.7497 | 306.4068 | 190.5511 | 229.7821 | 193.9976 | 175.764 | 159.6751 | 165.9606 | 159.1475 | 135.9594
1377.7511 | 1267.7511 | 306.313 | 190.5704 | 229.8423 | 194.0536 | 175.8989 | 160.1442 | 166.0459 | 159.2104 | 136.0883
1378.7525 | 1268.7525 | 306.2247 | 190.6391 | 229.8245 | 194.0985 | 175.9423 | 159.8743 | 166.1518 | 159.299 | 136.1276
1379.754 | 1269.754 | 306.2237 | 190.6907 | 229.9655 | 194.1493 | 176.0695 | 160.2733 | 166.2345 | 159.3515 | 136.2641
1380.7554 | 1270.7554 | 306.2417 | 190.7437 | 230.0049 | 194.211 | 176.1024 | 160.0857 | 166.3429 | 159.4666 | 136.2568
1381.7569 | 1271.7569 | 306.2746 | 190.8153 | 230.0313 | 194.2694 | 176.1838 | 160.1618 | 166.4403 | 159.5315 | 136.3594
1382.7483 | 1272.7483 | 306.2283 | 190.8467 | 230.1029 | 194.3208 | 176.2767 | 160.2691 | 166.5421 | 159.6062 | 136.444
1383.7497 | 1273.7497 | 306.2091 | 190.9212 | 230.1271 | 194.3753 | 176.3679 | 160.3501 | 166.6434 | 159.6904 | 136.5041
1384.7512 | 1274.7512 | 306.3301 | 190.9622 | 230.1753 | 194.4159 | 176.4623 | 160.4475 | 166.7353 | 159.7712 | 136.563
1385.7526 | 1275.7526 | 306.3471 | 191.0074 | 230.2388 | 194.4625 | 176.5476 | 160.5437 | 166.8257 | 159.8452 | 136.6638
1386.7541 | 1276.7541 | 306.4109 | 191.0777 | 230.3007 | 194.5464 | 176.6336 | 160.6366 | 166.9252 | 159.9271 | 136.7098
1387.7555 | 1277.7555 | 306.49 | 191.1209 | 230.3624 | 194.5536 | 176.7104 | 160.74 | 167.0273 | 159.9972 | 136.7986
1388.7569 | 1278.7569 | 306.4916 | 191.1399 | 230.3883 | 194.6114 | 176.8322 | 161.0861 | 167.1136 | 160.0532 | 136.9397
1389.7484 | 1279.7484 | 306.3992 | 191.2222 | 230.4361 | 194.6757 | 176.8888 | 160.9285 | 167.2257 | 160.1459 | 136.9574
1390.7498 | 1280.7498 | 306.3655 | 191.2656 | 230.4767 | 194.7365 | 176.9913 | 161.0297 | 167.3295 | 160.2096 | 137.0543
1391.7512 | 1281.7512 | 306.4223 | 191.3212 | 230.5756 | 194.794 | 177.071 | 161.1199 | 167.4269 | 160.2904 | 137.1318
1392.7527 | 1282.7527 | 306.3975 | 191.3679 | 230.5999 | 194.83 | 177.1575 | 161.2171 | 167.5255 | 160.355 | 137.1972
1393.7541 | 1283.7541 | 306.3098 | 191.4216 | 230.6731 | 194.8843 | 177.2682 | 161.4856 | 167.6186 | 160.4241 | 137.3099
1394.7556 | 1284.7556 | 306.3155 | 191.458 | 230.7144 | 194.9284 | 177.3409 | 161.4361 | 167.7288 | 160.4923 | 137.3631
1395.747 | 1285.747 | 306.3509 | 191.5196 | 230.7568 | 194.9678 | 177.4132 | 161.5024 | 167.8282 | 160.5589 | 137.4424
1396.7484 | 1286.7484 | 306.4316 | 191.5661 | 230.8244 | 195.0074 | 177.5208 | 161.8176 | 167.9118 | 160.6252 | 137.5385
1397.7499 | 1287.7499 | 306.444 | 191.6411 | 230.85 | 195.0523 | 177.5905 | 161.709 | 168.0222 | 160.7051 | 137.596
1398.7513 | 1288.7513 | 306.4319 | 191.6924 | 230.9341 | 195.1198 | 177.6637 | 161.7983 | 168.1279 | 160.7766 | 137.6843
1399.7527 | 1289.7527 | 306.4025 | 191.7546 | 230.9636 | 195.1488 | 177.7543 | 161.8939 | 168.2221 | 160.8386 | 137.7513
1400.7542 | 1290.7542 | 306.3691 | 191.7856 | 231.0698 | 195.2066 | 177.8438 | 161.9936 | 168.3139 | 160.9233 | 137.8453
1401.7456 | 1291.7456 | 306.3771 | 191.83 | 231.0837 | 195.2355 | 177.9259 | 162.0878 | 168.4123 | 160.9944 | 137.8985
1402.7571 | 1292.7571 | 306.3349 | 191.8641 | 231.1629 | 195.3034 | 178.0141 | 162.1876 | 168.4999 | 161.0737 | 137.9687
1403.7485 | 1293.7485 | 306.2872 | 191.952 | 231.1973 | 195.3582 | 178.0977 | 162.2744 | 168.5963 | 161.1461 | 138.0705
1404.7499 | 1294.7499 | 306.3671 | 191.9755 | 231.2288 | 195.4168 | 178.1878 | 162.3798 | 168.6879 | 161.2282 | 138.1493
1405.7514 | 1295.7514 | 306.4452 | 192.0116 | 231.3117 | 195.4412 | 178.3076 | 162.68 | 168.7726 | 161.2954 | 138.2587
1406.7528 | 1296.7528 | 306.3873 | 192.0994 | 231.3393 | 195.5065 | 178.3739 | 162.5748 | 168.8769 | 161.3831 | 138.3126
1407.7543 | 1297.7543 | 306.3495 | 192.1241 | 231.4219 | 195.5379 | 178.4452 | 162.6832 | 168.9671 | 161.4591 | 138.3872
1408.7557 | 1298.7557 | 306.381 | 192.2019 | 231.4513 | 195.595 | 178.5351 | 162.7703 | 169.0475 | 161.5659 | 138.4242
1409.7471 | 1299.7471 | 306.402 | 192.2346 | 231.4948 | 195.6468 | 178.6287 | 162.8738 | 169.1442 | 161.6498 | 138.5206
1410.7486 | 1300.7486 | 306.4144 | 192.2711 | 231.5853 | 195.6709 | 178.7404 | 163.2469 | 169.2138 | 161.7295 | 138.6122
1411.75 | 1301.75 | 306.4149 | 192.3287 | 231.6142 | 195.7165 | 178.8022 | 163.0594 | 169.3228 | 161.8099 | 138.6549
1412.7514 | 1302.7514 | 306.3265 | 192.3669 | 231.643 | 195.7919 | 178.8886 | 163.1599 | 169.4122 | 161.887 | 138.7377
1413.7529 | 1303.7529 | 306.2156 | 192.4241 | 231.7222 | 195.8361 | 178.9864 | 163.4538 | 169.482 | 161.9728 | 138.8229
1414.7543 | 1304.7543 | 306.2338 | 192.4402 | 231.741 | 195.8653 | 179.0638 | 163.352 | 169.5793 | 162.0536 | 138.8914
1415.7558 | 1305.7558 | 306.2863 | 192.5439 | 231.7591 | 195.916 | 179.1417 | 163.4402 | 169.6748 | 162.134 | 138.9424
1416.7472 | 1306.7472 | 306.321 | 192.5629 | 231.8221 | 195.9416 | 179.2232 | 163.5379 | 169.7624 | 162.2238 | 139.0102
1417.7486 | 1307.7486 | 306.3139 | 192.6433 | 231.8946 | 196.0125 | 179.3146 | 163.6169 | 169.8515 | 162.3059 | 139.0849
1418.7501 | 1308.7501 | 306.3058 | 192.6527 | 231.9149 | 196.0394 | 179.3954 | 163.7246 | 169.9408 | 162.4 | 139.1498
1419.7515 | 1309.7515 | 306.2551 | 192.7314 | 231.9767 | 196.1073 | 179.4795 | 163.8159 | 170.0262 | 162.48 | 139.2447
1420.7529 | 1310.7529 | 306.2737 | 192.76 | 232.0552 | 196.1335 | 179.5657 | 163.909 | 170.1095 | 162.5614 | 139.2961
1421.7544 | 1311.7544 | 306.2181 | 192.7755 | 232.0953 | 196.1688 | 179.6888 | 164.1639 | 170.1964 | 162.6456 | 139.3826
1422.7558 | 1312.7558 | 306.2246 | 192.869 | 232.1437 | 196.236 | 179.7534 | 164.1062 | 170.2874 | 162.7261 | 139.4402
1423.7573 | 1313.7573 | 306.1998 | 192.9065 | 232.222 | 196.291 | 179.8353 | 164.1953 | 170.3695 | 162.819 | 139.5066
1424.7487 | 1314.7487 | 306.0907 | 192.9646 | 232.241 | 196.331 | 179.913 | 164.2921 | 170.4625 | 162.8976 | 139.5741
1425.7501 | 1315.7501 | 305.8495 | 192.9799 | 232.2609 | 196.3799 | 180.0035 | 164.3847 | 170.5458 | 162.9735 | 139.6482
1426.7516 | 1316.7516 | 305.627 | 193.0193 | 232.2465 | 196.4119 | 180.0908 | 164.4754 | 170.6307 | 163.063 | 139.7031
1427.753 | 1317.753 | 305.5286 | 193.0758 | 232.3566 | 196.4443 | 180.1917 | 164.7408 | 170.7117 | 163.1355 | 139.7997
1428.7544 | 1318.7544 | 305.4966 | 193.1338 | 232.3923 | 196.4871 | 180.2703 | 164.6701 | 170.8073 | 163.2174 | 139.8389
1429.7559 | 1319.7559 | 305.3547 | 193.1928 | 232.439 | 196.5423 | 180.3408 | 164.7628 | 170.8882 | 163.2955 | 139.9439
1430.7573 | 1320.7573 | 305.2386 | 193.2174 | 232.5349 | 196.569 | 180.4586 | 165.0573 | 170.9745 | 163.3809 | 140.0118
1431.7488 | 1321.7488 | 305.1634 | 193.2979 | 232.5486 | 196.6504 | 180.525 | 164.9483 | 171.0716 | 163.4702 | 140.043
1432.7502 | 1322.7502 | 305.1131 | 193.3158 | 232.5671 | 196.6528 | 180.5954 | 165.0459 | 171.1552 | 163.5344 | 140.1573
1433.7516 | 1323.7516 | 305.1925 | 193.3692 | 232.6597 | 196.7281 | 180.6935 | 165.1337 | 171.2458 | 163.6257 | 140.1952
1434.7531 | 1324.7531 | 305.284 | 193.4059 | 232.7044 | 196.7752 | 180.7775 | 165.2223 | 171.3304 | 163.699 | 140.2693
1435.7545 | 1325.7545 | 305.3725 | 193.4499 | 232.7285 | 196.8218 | 180.8575 | 165.3208 | 171.413 | 163.7824 | 140.3338
1436.756 | 1326.756 | 305.3914 | 193.5121 | 232.7859 | 196.868 | 180.9412 | 165.4128 | 171.498 | 163.8649 | 140.4087
1437.7474 | 1327.7474 | 305.4659 | 193.5469 | 232.7756 | 196.9084 | 181.0266 | 165.5111 | 171.5864 | 163.9459 | 140.472
1438.7488 | 1328.7488 | 305.5122 | 193.6084 | 232.8399 | 196.9583 | 181.1089 | 165.598 | 171.6739 | 164.0128 | 140.5537
1439.7503 | 1329.7503 | 305.5235 | 193.627 | 232.9116 | 197.0126 | 181.2126 | 165.692 | 171.7585 | 164.092 | 140.601
1440.7517 | 1330.7517 | 305.4953 | 193.6922 | 232.9677 | 197.0473 | 181.2838 | 165.7856 | 171.841 | 164.1772 | 140.6666
1441.7531 | 1331.7531 | 305.4054 | 193.7274 | 233.0673 | 197.0961 | 181.3866 | 165.8734 | 171.9313 | 164.2559 | 140.7526
1442.7546 | 1332.7546 | 305.4171 | 193.7847 | 233.1375 | 197.1434 | 181.4601 | 165.9706 | 172.0179 | 164.3342 | 140.8236
1443.756 | 1333.756 | 305.484 | 193.8363 | 233.1443 | 197.191 | 181.5466 | 166.0641 | 172.0898 | 164.4022 | 140.8886
1444.7474 | 1334.7474 | 305.4616 | 193.8573 | 233.2092 | 197.1783 | 181.6306 | 166.1553 | 172.1873 | 164.4952 | 140.9514
1445.7489 | 1335.7489 | 305.5047 | 193.9352 | 233.2389 | 197.2333 | 181.7102 | 166.2459 | 172.2659 | 164.5624 | 141.0338
1446.7503 | 1336.7503 | 305.598 | 193.9513 | 233.2307 | 197.2525 | 181.8086 | 166.341 | 172.3549 | 164.6406 | 141.1071
1447.7518 | 1337.7518 | 305.6387 | 194.0153 | 233.2676 | 197.3222 | 181.8831 | 166.4301 | 172.4417 | 164.7239 | 141.1701
1448.7532 | 1338.7532 | 305.5922 | 194.0431 | 233.3629 | 197.3584 | 181.9663 | 166.5155 | 172.532 | 164.8 | 141.22
1449.7546 | 1339.7546 | 305.5162 | 194.0878 | 233.359 | 197.4243 | 182.049 | 166.6101 | 172.6174 | 164.885 | 141.288
1450.7561 | 1340.7561 | 305.5506 | 194.1335 | 233.4618 | 197.4852 | 182.1364 | 166.7017 | 172.6972 | 164.9646 | 141.3464
1451.7475 | 1341.7475 | 305.477 | 194.1825 | 233.5167 | 197.5214 | 182.2203 | 166.7992 | 172.7877 | 165.0354 | 141.4296
1452.749 | 1342.749 | 305.3764 | 194.2478 | 233.5252 | 197.5943 | 182.3004 | 166.8794 | 172.8725 | 165.122 | 141.4854
1453.7504 | 1343.7504 | 305.2421 | 194.2713 | 233.5485 | 197.6162 | 182.3956 | 166.9787 | 172.9526 | 165.1819 | 141.5731
1454.7518 | 1344.7518 | 305.1395 | 194.3366 | 233.5947 | 197.6805 | 182.4862 | 167.0622 | 173.0431 | 165.2613 | 141.6507
1455.7533 | 1345.7533 | 305.2139 | 194.3765 | 233.5636 | 197.7104 | 182.5662 | 167.1604 | 173.1264 | 165.3437 | 141.7151
1456.7547 | 1346.7547 | 305.2091 | 194.4189 | 233.7064 | 197.7506 | 182.6494 | 167.2582 | 173.2081 | 165.4327 | 141.758
1457.7461 | 1347.7461 | 305.2208 | 194.4766 | 233.7562 | 197.7808 | 182.7307 | 167.3472 | 173.2957 | 165.5104 | 141.8356
1458.7476 | 1348.7476 | 305.2337 | 194.5024 | 233.8025 | 197.831 | 182.8169 | 167.4306 | 173.3847 | 165.5824 | 141.8889
1459.749 | 1349.749 | 305.2286 | 194.546 | 233.8582 | 197.8608 | 182.9081 | 167.5209 | 173.4584 | 165.6557 | 141.9774
1460.7505 | 1350.7505 | 305.2486 | 194.5873 | 233.8625 | 197.9195 | 182.9919 | 167.6186 | 173.5476 | 165.7383 | 142.0164
1461.7519 | 1351.7519 | 305.3273 | 194.6442 | 233.9571 | 197.965 | 183.0713 | 167.7038 | 173.6358 | 165.8073 | 142.1036
1462.7533 | 1352.7533 | 305.4896 | 194.6809 | 234.0026 | 198.0181 | 183.1519 | 167.7912 | 173.7123 | 165.8898 | 142.1728
1463.7548 | 1353.7548 | 305.5577 | 194.7188 | 234.0319 | 198.0667 | 183.2452 | 167.8871 | 173.8015 | 165.9748 | 142.2249
1464.7462 | 1354.7462 | 305.5935 | 194.7508 | 234.0662 | 198.1267 | 183.328 | 167.9758 | 173.8852 | 166.0486 | 142.3071
1465.7577 | 1355.7577 | 305.542 | 194.8231 | 234.1523 | 198.1655 | 183.4053 | 168.0642 | 173.9684 | 166.1086 | 142.3715
1466.7491 | 1356.7491 | 305.4945 | 194.8454 | 234.1943 | 198.2026 | 183.4811 | 168.1544 | 174.0511 | 166.1947 | 142.433
1467.7505 | 1357.7505 | 305.6191 | 194.9021 | 234.2367 | 198.2448 | 183.5646 | 168.2491 | 174.1302 | 166.2722 | 142.4903
1468.752 | 1358.752 | 305.6826 | 194.95 | 234.2824 | 198.285 | 183.649 | 168.3367 | 174.224 | 166.3409 | 142.5761
1469.7534 | 1359.7534 | 305.7012 | 194.9958 | 234.3316 | 198.3275 | 183.7247 | 168.4182 | 174.3088 | 166.405 | 142.6472
1470.7548 | 1360.7548 | 305.7299 | 195.045 | 234.407 | 198.3929 | 183.8274 | 168.5146 | 174.4021 | 166.4815 | 142.7049
1471.7563 | 1361.7563 | 305.7849 | 195.0762 | 234.4498 | 198.4238 | 183.8936 | 168.614 | 174.4872 | 166.5588 | 142.7737
1472.7577 | 1362.7577 | 305.8021 | 195.1423 | 234.4452 | 198.4709 | 183.9815 | 168.6994 | 174.5754 | 166.6262 | 142.8304
1473.7491 | 1363.7491 | 305.9455 | 195.1676 | 234.5453 | 198.4986 | 184.0594 | 168.7907 | 174.6556 | 166.6984 | 142.9117
1474.7506 | 1364.7506 | 305.9923 | 195.2398 | 234.5744 | 198.5499 | 184.1494 | 168.8692 | 174.7411 | 166.7718 | 142.9621
1475.752 | 1365.752 | 306.1367 | 195.2443 | 234.6182 | 198.5946 | 184.2401 | 168.9707 | 174.8289 | 166.8242 | 143.071
1476.7535 | 1366.7535 | 306.2685 | 195.3324 | 234.6411 | 198.6571 | 184.3134 | 169.0498 | 174.9165 | 166.9183 | 143.1232
1477.7549 | 1367.7549 | 306.4059 | 195.3512 | 234.7053 | 198.6879 | 184.4053 | 169.1401 | 175.0083 | 166.9797 | 143.1928
1478.7563 | 1368.7563 | 306.5469 | 195.3926 | 234.6943 | 198.7347 | 184.477 | 169.2363 | 175.0883 | 167.0548 | 143.2737
1479.7478 | 1369.7478 | 306.7016 | 195.4129 | 234.7569 | 198.7812 | 184.5627 | 169.3247 | 175.1778 | 167.1289 | 143.3377
1480.7492 | 1370.7492 | 306.7892 | 195.5038 | 234.8419 | 198.8536 | 184.6339 | 169.4111 | 175.2647 | 167.2045 | 143.4051
1481.7507 | 1371.7507 | 306.7748 | 195.5226 | 234.8499 | 198.8934 | 184.7277 | 169.5082 | 175.3486 | 167.2582 | 143.4768
1482.7521 | 1372.7521 | 306.7547 | 195.5835 | 234.8572 | 198.9334 | 184.8143 | 169.5881 | 175.4335 | 167.3206 | 143.5621
1483.7535 | 1373.7535 | 306.8127 | 195.6352 | 234.9234 | 198.9714 | 184.8955 | 169.6725 | 175.5173 | 167.4007 | 143.6195
1484.755 | 1374.755 | 306.9307 | 195.6522 | 235.0056 | 199.0156 | 184.9769 | 169.7743 | 175.6084 | 167.4683 | 143.6859
1485.7464 | 1375.7464 | 307.0163 | 195.7205 | 235.0639 | 199.0748 | 185.0569 | 169.8625 | 175.692 | 167.5432 | 143.7328
1486.7478 | 1376.7478 | 307.088 | 195.7474 | 235.1191 | 199.1095 | 185.1347 | 169.9499 | 175.7754 | 167.6217 | 143.801
1487.7493 | 1377.7493 | 307.1445 | 195.8223 | 235.1441 | 199.1427 | 185.2194 | 170.0321 | 175.8661 | 167.6819 | 143.8907
1488.7507 | 1378.7507 | 307.2125 | 195.8352 | 235.1977 | 199.1882 | 185.3041 | 170.1263 | 175.9567 | 167.7598 | 143.9505
1489.7522 | 1379.7522 | 307.276 | 195.9049 | 235.2325 | 199.2415 | 185.3785 | 170.2148 | 176.0465 | 167.8154 | 144.017
1490.7536 | 1380.7536 | 307.2652 | 195.934 | 235.3144 | 199.2711 | 185.4689 | 170.2999 | 176.1353 | 167.8707 | 144.0994
1491.755 | 1381.755 | 307.2651 | 195.9834 | 235.3267 | 199.3189 | 185.5413 | 170.4017 | 176.2286 | 167.945 | 144.1538
1492.7565 | 1382.7565 | 307.2869 | 196.0397 | 235.3366 | 199.3686 | 185.6419 | 170.4813 | 176.3156 | 167.9957 | 144.2367
1493.7479 | 1383.7479 | 307.193 | 196.0747 | 235.4338 | 199.4182 | 185.719 | 170.5737 | 176.4015 | 168.0831 | 144.2846
1494.7493 | 1384.7493 | 307.1148 | 196.1362 | 235.438 | 199.4911 | 185.7924 | 170.6552 | 176.483 | 168.1463 | 144.345
1495.7508 | 1385.7508 | 307.1045 | 196.1333 | 235.4481 | 199.5228 | 185.8846 | 170.7565 | 176.5636 | 168.2135 | 144.4324
1496.7522 | 1386.7522 | 307.1682 | 196.2247 | 235.56 | 199.5727 | 185.9626 | 170.8413 | 176.6607 | 168.2804 | 144.4931
1497.7537 | 1387.7537 | 307.0861 | 196.243 | 235.6142 | 199.5888 | 186.0397 | 170.9314 | 176.7427 | 168.3557 | 144.5642
1498.7551 | 1388.7551 | 307.0902 | 196.2935 | 235.6538 | 199.6386 | 186.1355 | 171.0231 | 176.8312 | 168.4246 | 144.6329
1499.7565 | 1389.7565 | 306.9715 | 196.3218 | 235.6979 | 199.6966 | 186.2186 | 171.1158 | 176.9144 | 168.4928 | 144.6969
1500.8581 | 1390.8581 | 306.9917 | 196.386 | 235.7763 | 199.7433 | 186.3028 | 171.2104 | 177.0039 | 168.5735 | 144.7749
1501.7494 | 1391.7494 | 306.912 | 196.4118 | 235.7813 | 199.77 | 186.3728 | 171.2837 | 177.0779 | 168.6224 | 144.8544
1502.7508 | 1392.7508 | 306.7918 | 196.4642 | 235.8083 | 199.8077 | 186.4515 | 171.3849 | 177.1652 | 168.7012 | 144.8959
1503.7523 | 1393.7523 | 306.7837 | 196.4987 | 235.8969 | 199.8772 | 186.5344 | 171.4635 | 177.2454 | 168.7701 | 144.9766
1504.7537 | 1394.7537 | 306.7205 | 196.562 | 235.9131 | 199.9173 | 186.63 | 171.5568 | 177.3283 | 168.8483 | 145.0429
1505.7452 | 1395.7452 | 306.582 | 196.6169 | 235.9587 | 199.9344 | 186.701 | 171.6451 | 177.4115 | 168.9183 | 145.0945
1506.7466 | 1396.7466 | 306.5142 | 196.6414 | 236.0348 | 199.9631 | 186.7803 | 171.7396 | 177.4901 | 168.9813 | 145.18
1507.748 | 1397.748 | 306.4794 | 196.7063 | 236.0031 | 199.9935 | 186.8659 | 171.8157 | 177.5694 | 169.0645 | 145.2181
1508.7495 | 1398.7495 | 306.4742 | 196.7464 | 236.058 | 200.081 | 186.9458 | 171.9121 | 177.6634 | 169.1207 | 145.3169
1509.7509 | 1399.7509 | 306.5399 | 196.7899 | 236.1381 | 200.1278 | 187.0249 | 172.0027 | 177.7415 | 169.2023 | 145.3456
1510.7524 | 1400.7524 | 306.5731 | 196.808 | 236.2018 | 200.1727 | 187.1099 | 172.0898 | 177.8176 | 169.2544 | 145.433
1511.7538 | 1401.7538 | 306.5388 | 196.8741 | 236.2306 | 200.2285 | 187.1896 | 172.1799 | 177.8956 | 169.3388 | 145.491
1512.7552 | 1402.7552 | 306.4735 | 196.901 | 236.2913 | 200.2492 | 187.2839 | 172.2776 | 177.9842 | 169.4131 | 145.5737
1513.7567 | 1403.7567 | 306.4044 | 196.9345 | 236.3626 | 200.3042 | 187.353 | 172.3774 | 178.0721 | 169.4823 | 145.6019
1514.7481 | 1404.7481 | 306.3015 | 197.0061 | 236.3931 | 200.3505 | 187.4382 | 172.4592 | 178.1556 | 169.55 | 145.6937
1515.7495 | 1405.7495 | 306.2255 | 197.0155 | 236.4215 | 200.3773 | 187.5168 | 172.5495 | 178.2359 | 169.614 | 145.7744
1516.751 | 1406.751 | 306.2377 | 197.0673 | 236.4744 | 200.4374 | 187.6004 | 172.6354 | 178.3199 | 169.7057 | 145.8194
1517.7524 | 1407.7524 | 306.2268 | 197.0961 | 236.509 | 200.4745 | 187.6846 | 172.7266 | 178.4029 | 169.7735 | 145.8912
1518.7539 | 1408.7539 | 306.152 | 197.179 | 236.5299 | 200.5224 | 187.7587 | 172.804 | 178.484 | 169.8526 | 145.9282
1519.7553 | 1409.7553 | 306.1413 | 197.1597 | 236.5856 | 200.5624 | 187.8413 | 172.9013 | 178.5749 | 169.9135 | 146.0131
1520.7567 | 1410.7567 | 306.0192 | 197.2337 | 236.6382 | 200.6059 | 187.9227 | 172.9929 | 178.6637 | 169.9722 | 146.0855
1521.7482 | 1411.7482 | 305.9541 | 197.2826 | 236.6902 | 200.6429 | 187.9925 | 173.075 | 178.7448 | 170.0621 | 146.1272
1522.7496 | 1412.7496 | 305.9678 | 197.3243 | 236.7303 | 200.6992 | 188.0755 | 173.1587 | 178.8233 | 170.1305 | 146.1915
1523.751 | 1413.751 | 305.9385 | 197.3639 | 236.7356 | 200.7267 | 188.1444 | 173.2504 | 178.908 | 170.1945 | 146.2437
1524.7525 | 1414.7525 | 305.9295 | 197.4027 | 236.7842 | 200.7682 | 188.2396 | 173.3319 | 178.9984 | 170.2545 | 146.3259
1525.7539 | 1415.7539 | 305.8828 | 197.4383 | 236.8418 | 200.8112 | 188.3186 | 173.4204 | 179.0877 | 170.3162 | 146.3979
1526.7554 | 1416.7554 | 305.9121 | 197.4573 | 236.8318 | 200.8447 | 188.4048 | 173.5189 | 179.1683 | 170.3886 | 146.4692
1527.7468 | 1417.7468 | 305.8976 | 197.5113 | 236.8848 | 200.9049 | 188.4758 | 173.6063 | 179.2584 | 170.4638 | 146.5098
1528.7482 | 1418.7482 | 305.8706 | 197.5392 | 236.9574 | 200.9242 | 188.559 | 173.6957 | 179.3419 | 170.5174 | 146.5812
1529.7497 | 1419.7497 | 305.8565 | 197.5945 | 236.9496 | 200.9654 | 188.6332 | 173.772 | 179.4342 | 170.5967 | 146.6275
1530.7511 | 1420.7511 | 305.857 | 197.6129 | 236.9678 | 200.9871 | 188.7074 | 173.8707 | 179.5201 | 170.6625 | 146.703
1531.7526 | 1421.7526 | 305.9334 | 197.6727 | 237.0545 | 200.9969 | 188.799 | 173.9596 | 179.6083 | 170.7294 | 146.7715
1532.754 | 1422.754 | 305.9869 | 197.7283 | 237.098 | 201.0527 | 188.8776 | 174.0341 | 179.6905 | 170.7814 | 146.8248
1533.7554 | 1423.7554 | 305.9904 | 197.7754 | 237.1368 | 201.1239 | 188.9563 | 174.1186 | 179.7794 | 170.8442 | 146.9016
1534.7469 | 1424.7469 | 306.0898 | 197.7818 | 237.2212 | 201.1632 | 189.0464 | 174.2085 | 179.8631 | 170.913 | 146.9796
1535.7483 | 1425.7483 | 306.1819 | 197.848 | 237.2369 | 201.2101 | 189.122 | 174.2974 | 179.9537 | 170.9897 | 147.0121
1536.7497 | 1426.7497 | 306.1744 | 197.9019 | 237.2819 | 201.2544 | 189.2029 | 174.3906 | 180.0458 | 171.0447 | 147.0847
1537.7512 | 1427.7512 | 306.2833 | 197.9238 | 237.3385 | 201.2921 | 189.2881 | 174.4702 | 180.1351 | 171.0909 | 147.1739
1538.7526 | 1428.7526 | 306.2982 | 197.962 | 237.3619 | 201.3255 | 189.3671 | 174.5597 | 180.2217 | 171.1696 | 147.2073
1539.7541 | 1429.7541 | 306.2546 | 198.015 | 237.4061 | 201.3859 | 189.44 | 174.6431 | 180.3051 | 171.2178 | 147.2888
1540.7555 | 1430.7555 | 306.3333 | 198.0611 | 237.4584 | 201.4114 | 189.524 | 174.733 | 180.4085 | 171.2777 | 147.3614
1541.7469 | 1431.7469 | 306.2627 | 198.1101 | 237.5001 | 201.4633 | 189.6086 | 174.8128 | 180.4978 | 171.334 | 147.4131
1542.7484 | 1432.7484 | 306.1887 | 198.1361 | 237.5435 | 201.5129 | 189.6859 | 174.9027 | 180.5833 | 171.3922 | 147.5049
1543.7498 | 1433.7498 | 306.1574 | 198.1929 | 237.6119 | 201.5396 | 189.7669 | 174.9903 | 180.6764 | 171.4537 | 147.5611
1544.7512 | 1434.7512 | 306.1268 | 198.2451 | 237.6661 | 201.5978 | 189.8459 | 175.0773 | 180.7566 | 171.5042 | 147.6476
1545.7527 | 1435.7527 | 306.1251 | 198.2845 | 237.6929 | 201.642 | 189.9214 | 175.1592 | 180.8483 | 171.5737 | 147.697
1546.7541 | 1436.7541 | 306.1601 | 198.3437 | 237.7342 | 201.6826 | 190.0043 | 175.2454 | 180.9334 | 171.6207 | 147.7602
1547.7556 | 1437.7556 | 306.1358 | 198.3739 | 237.7353 | 201.739 | 190.0822 | 175.3283 | 181.0268 | 171.6883 | 147.8358
1548.747 | 1438.747 | 306.1519 | 198.3938 | 237.816 | 201.7667 | 190.1734 | 175.4119 | 181.1159 | 171.7456 | 147.8844
1549.7484 | 1439.7484 | 306.157 | 198.4328 | 237.8546 | 201.7872 | 190.2491 | 175.4991 | 181.2006 | 171.8175 | 147.9532
1550.7499 | 1440.7499 | 306.1213 | 198.4762 | 237.8907 | 201.8375 | 190.3263 | 175.5845 | 181.2889 | 171.8737 | 148.0114
1551.7513 | 1441.7513 | 306.0533 | 198.5243 | 237.8953 | 201.8934 | 190.4165 | 175.6698 | 181.3754 | 171.9282 | 148.0972
1552.7527 | 1442.7527 | 305.9074 | 198.5627 | 237.9733 | 201.9373 | 190.4907 | 175.7559 | 181.4706 | 171.9859 | 148.1621
1553.7542 | 1443.7542 | 305.9087 | 198.6101 | 237.9936 | 201.9692 | 190.561 | 175.8329 | 181.5522 | 172.0426 | 148.2352
1554.7556 | 1444.7556 | 305.9063 | 198.647 | 238.0763 | 202.0123 | 190.6517 | 175.9176 | 181.6405 | 172.1117 | 148.2936
1555.7571 | 1445.7571 | 305.9233 | 198.6846 | 238.1135 | 202.0658 | 190.7373 | 176.0098 | 181.7263 | 172.1876 | 148.3369
1556.7485 | 1446.7485 | 305.992 | 198.7401 | 238.1377 | 202.1094 | 190.8144 | 176.0838 | 181.8089 | 172.2341 | 148.4362
1557.7499 | 1447.7499 | 306.0303 | 198.7621 | 238.176 | 202.1307 | 190.9022 | 176.1773 | 181.9037 | 172.2863 | 148.5038
1558.7514 | 1448.7514 | 305.9679 | 198.7727 | 238.2084 | 202.1811 | 190.9777 | 176.2717 | 181.9864 | 172.3489 | 148.5574
1559.7528 | 1449.7528 | 305.8561 | 198.7967 | 238.2543 | 202.2101 | 191.0509 | 176.3429 | 182.0751 | 172.4048 | 148.6179
1560.7543 | 1450.7543 | 305.8131 | 198.8684 | 238.2797 | 202.258 | 191.1341 | 176.4235 | 182.1571 | 172.4679 | 148.6933
1561.7557 | 1451.7557 | 305.7727 | 198.8957 | 238.3533 | 202.2852 | 191.2105 | 176.5149 | 182.2464 | 172.5314 | 148.7473
1562.7571 | 1452.7571 | 305.7164 | 198.9437 | 238.3571 | 202.3344 | 191.3042 | 176.6013 | 182.3422 | 172.5786 | 148.8414
1563.7486 | 1453.7486 | 305.7313 | 198.9888 | 238.3845 | 202.3528 | 191.3713 | 176.6758 | 182.4254 | 172.6507 | 148.8952
1564.75 | 1454.75 | 305.7793 | 199.0421 | 238.375 | 202.414 | 191.4516 | 176.7559 | 182.5057 | 172.7123 | 148.9422
1565.7514 | 1455.7514 | 305.8294 | 199.0695 | 238.4903 | 202.4445 | 191.5325 | 176.8565 | 182.5923 | 172.7757 | 149.0059
1566.7529 | 1456.7529 | 305.8665 | 199.1175 | 238.4955 | 202.4662 | 191.6251 | 176.9279 | 182.668 | 172.837 | 149.067
1567.7543 | 1457.7543 | 305.7885 | 199.1553 | 238.5419 | 202.5229 | 191.6971 | 177.0166 | 182.7548 | 172.9054 | 149.147
1568.7558 | 1458.7558 | 305.7968 | 199.1703 | 238.5908 | 202.5581 | 191.7842 | 177.0998 | 182.8357 | 172.9563 | 149.2043
1569.7472 | 1459.7472 | 305.8782 | 199.2083 | 238.6263 | 202.5756 | 191.8623 | 177.1786 | 182.9153 | 173.0365 | 149.2576
1570.7486 | 1460.7486 | 305.8943 | 199.2507 | 238.619 | 202.6125 | 191.9325 | 177.2674 | 182.9981 | 173.1026 | 149.323
1571.7501 | 1461.7501 | 305.8524 | 199.2978 | 238.7148 | 202.6599 | 192.0006 | 177.336 | 183.0741 | 173.168 | 149.3989
1572.7515 | 1462.7515 | 305.8362 | 199.3174 | 238.7297 | 202.6852 | 192.1028 | 177.4396 | 183.1405 | 173.2374 | 149.4595
1573.7529 | 1463.7529 | 305.8638 | 199.3828 | 238.7361 | 202.7422 | 192.1648 | 177.5028 | 183.2227 | 173.3161 | 149.4967
1574.7544 | 1464.7544 | 305.8385 | 199.3797 | 238.8054 | 202.792 | 192.2558 | 177.5979 | 183.2977 | 173.3975 | 149.5472
1575.7558 | 1465.7558 | 305.7296 | 199.4592 | 238.8267 | 202.8178 | 192.3217 | 177.6695 | 183.3696 | 173.4535 | 149.6134
1576.7473 | 1466.7473 | 305.5784 | 199.4667 | 238.8671 | 202.8367 | 192.4084 | 177.7674 | 183.4467 | 173.5297 | 149.6542
1577.7487 | 1467.7487 | 305.5487 | 199.5268 | 238.9353 | 202.8888 | 192.4884 | 177.8347 | 183.5232 | 173.5996 | 149.7272
1578.7501 | 1468.7501 | 305.568 | 199.5808 | 238.9576 | 202.9261 | 192.5659 | 177.9215 | 183.6009 | 173.6703 | 149.7839
1579.7516 | 1469.7516 | 305.5481 | 199.5883 | 238.9315 | 202.9698 | 192.6395 | 178.0115 | 183.6764 | 173.7405 | 149.8136
1580.753 | 1470.753 | 305.5453 | 199.6656 | 239.0345 | 203.0459 | 192.7144 | 178.087 | 183.7555 | 173.7811 | 149.9164
1581.7545 | 1471.7545 | 305.5357 | 199.6709 | 239.0374 | 203.0648 | 192.7899 | 178.177 | 183.8311 | 173.8631 | 149.9411
1582.7459 | 1472.7459 | 305.4685 | 199.7241 | 239.0988 | 203.0916 | 192.8616 | 178.2482 | 183.9119 | 173.9326 | 149.9853
1583.7473 | 1473.7473 | 305.4699 | 199.7255 | 239.1644 | 203.132 | 192.9409 | 178.3464 | 183.9868 | 173.9938 | 150.0641
1584.7488 | 1474.7488 | 305.4655 | 199.8048 | 239.1377 | 203.1622 | 193.0368 | 178.4053 | 184.0703 | 174.0426 | 150.1305
1585.8003 | 1475.8003 | 305.5515 | 199.8319 | 239.2055 | 203.2071 | 193.1075 | 178.5051 | 184.1537 | 174.1068 | 150.1968
1586.7516 | 1476.7516 | 305.653 | 199.8802 | 239.2259 | 203.2595 | 193.1831 | 178.5773 | 184.2305 | 174.1661 | 150.2568
1587.7531 | 1477.7531 | 305.6413 | 199.8856 | 239.2913 | 203.288 | 193.2612 | 178.6677 | 184.3075 | 174.2354 | 150.2878
1588.7545 | 1478.7545 | 305.6039 | 199.9388 | 239.3029 | 203.3192 | 193.3371 | 178.7491 | 184.3887 | 174.2817 | 150.38
1589.756 | 1479.756 | 305.6359 | 199.9837 | 239.3527 | 203.3439 | 193.4141 | 178.8239 | 184.4694 | 174.3397 | 150.4206
1590.7474 | 1480.7474 | 305.7193 | 199.9817 | 239.4101 | 203.3824 | 193.5015 | 178.9116 | 184.544 | 174.3973 | 150.4975
1591.7488 | 1481.7488 | 305.7543 | 200.0684 | 239.4244 | 203.4395 | 193.5709 | 178.9859 | 184.6239 | 174.4549 | 150.5547
1592.7503 | 1482.7503 | 305.7628 | 200.0702 | 239.4307 | 203.4616 | 193.6486 | 179.0732 | 184.7031 | 174.5283 | 150.5926
1593.7517 | 1483.7517 | 305.8343 | 200.1375 | 239.4445 | 203.4941 | 193.7241 | 179.1506 | 184.7851 | 174.5783 | 150.6711
1594.7531 | 1484.7531 | 305.8574 | 200.16 | 239.5021 | 203.5088 | 193.8094 | 179.235 | 184.8611 | 174.6368 | 150.719
1595.7546 | 1485.7546 | 305.8441 | 200.221 | 239.5397 | 203.5516 | 193.8768 | 179.312 | 184.9415 | 174.7011 | 150.7763
1596.756 | 1486.756 | 305.8647 | 200.2232 | 239.5928 | 203.5519 | 193.9485 | 179.3975 | 185.0198 | 174.7567 | 150.8301
1597.7575 | 1487.7575 | 305.8935 | 200.2746 | 239.5891 | 203.6183 | 194.0383 | 179.4797 | 185.0947 | 174.8136 | 150.9042
1598.7489 | 1488.7489 | 305.948 | 200.3028 | 239.6234 | 203.6372 | 194.1083 | 179.5611 | 185.1768 | 174.8899 | 150.9407
1599.7503 | 1489.7503 | 305.9413 | 200.3359 | 239.6605 | 203.7143 | 194.1798 | 179.6303 | 185.2486 | 174.939 | 151.0175
1600.7518 | 1490.7518 | 305.9449 | 200.3749 | 239.7356 | 203.7414 | 194.2704 | 179.7225 | 185.3256 | 174.9992 | 151.0799
1601.7532 | 1491.7532 | 305.982 | 200.3987 | 239.7886 | 203.7859 | 194.3402 | 179.7976 | 185.3977 | 175.0581 | 151.142
1602.7546 | 1492.7546 | 305.9627 | 200.4544 | 239.8071 | 203.8038 | 194.4089 | 179.869 | 185.4716 | 175.1327 | 151.1903
1603.7561 | 1493.7561 | 305.9737 | 200.4567 | 239.8664 | 203.8311 | 194.4866 | 179.9557 | 185.5469 | 175.191 | 151.2373
1604.7575 | 1494.7575 | 305.9956 | 200.5328 | 239.8189 | 203.8857 | 194.5558 | 180.0247 | 185.6131 | 175.2454 | 151.3049
1605.749 | 1495.749 | 305.881 | 200.5382 | 239.8775 | 203.9135 | 194.6531 | 180.1192 | 185.6902 | 175.3112 | 151.3622
1606.7504 | 1496.7504 | 305.8453 | 200.6005 | 239.9525 | 203.9513 | 194.7186 | 180.1909 | 185.7609 | 175.385 | 151.3993
1607.7518 | 1497.7518 | 305.8655 | 200.6194 | 239.9584 | 203.9875 | 194.8013 | 180.2749 | 185.8387 | 175.4506 | 151.4578
1608.7533 | 1498.7533 | 305.778 | 200.6701 | 240.013 | 204.0587 | 194.8697 | 180.3411 | 185.9093 | 175.5051 | 151.5241
1609.7547 | 1499.7547 | 305.7668 | 200.7048 | 240.0329 | 204.06 | 194.9422 | 180.427 | 185.987 | 175.5649 | 151.5861
1610.7562 | 1500.7562 | 305.7779 | 200.7432 | 240.0956 | 204.1166 | 195.0109 | 180.5053 | 186.0534 | 175.6386 | 151.622
1611.7476 | 1501.7476 | 305.8228 | 200.7671 | 240.1341 | 204.1528 | 195.0974 | 180.5882 | 186.1323 | 175.6837 | 151.7043
1612.749 | 1502.749 | 305.8051 | 200.8062 | 240.1188 | 204.2024 | 195.1708 | 180.6621 | 186.2075 | 175.7557 | 151.732
1613.7505 | 1503.7505 | 305.7684 | 200.8565 | 240.1788 | 204.2532 | 195.2496 | 180.7421 | 186.2762 | 175.8185 | 151.8069
1614.7519 | 1504.7519 | 305.8228 | 200.8796 | 240.2297 | 204.2066 | 195.3189 | 180.8232 | 186.3499 | 175.8776 | 151.8737
1615.7533 | 1505.7533 | 305.8084 | 200.9347 | 240.2821 | 204.2387 | 195.3765 | 180.9006 | 186.4243 | 175.9309 | 151.9006
1616.7548 | 1506.7548 | 305.8293 | 200.9239 | 240.309 | 204.279 | 195.4563 | 180.9716 | 186.4995 | 175.9925 | 151.9656
1617.7562 | 1507.7562 | 305.77 | 201.0055 | 240.336 | 204.3364 | 195.5311 | 181.0527 | 186.5799 | 176.0453 | 152.0104
1618.7476 | 1508.7476 | 305.6449 | 201.0226 | 240.4146 | 204.3773 | 195.6183 | 181.1339 | 186.6493 | 176.1003 | 152.0695
1619.7491 | 1509.7491 | 305.6197 | 201.0664 | 240.3827 | 204.4084 | 195.6915 | 181.1995 | 186.7317 | 176.1622 | 152.1189
1620.7505 | 1510.7505 | 305.5059 | 201.0821 | 240.4315 | 204.4265 | 195.7609 | 181.278 | 186.811 | 176.209 | 152.1818
1621.752 | 1511.752 | 305.5642 | 201.1109 | 240.3667 | 204.4553 | 195.8463 | 181.3706 | 186.8857 | 176.264 | 152.2396
1622.7534 | 1512.7534 | 305.5832 | 201.1524 | 240.442 | 204.5075 | 195.9104 | 181.435 | 186.9611 | 176.3122 | 152.3174
1623.7548 | 1513.7548 | 305.5678 | 201.2095 | 240.4502 | 204.5077 | 195.9948 | 181.5242 | 187.0367 | 176.3725 | 152.3431
1624.7463 | 1514.7463 | 305.5775 | 201.2617 | 240.4695 | 204.5672 | 196.069 | 181.591 | 187.1217 | 176.4221 | 152.4017
1625.7477 | 1515.7477 | 305.5789 | 201.2474 | 240.564 | 204.5947 | 196.153 | 181.6765 | 187.1947 | 176.4629 | 152.4932
1626.7492 | 1516.7492 | 305.5332 | 201.3191 | 240.604 | 204.6578 | 196.2107 | 181.7468 | 187.2794 | 176.5213 | 152.5458
1627.7506 | 1517.7506 | 305.5281 | 201.3391 | 240.6228 | 204.6904 | 196.2929 | 181.8289 | 187.3562 | 176.5897 | 152.5854
1628.752 | 1518.752 | 305.5107 | 201.3787 | 240.6847 | 204.7402 | 196.3757 | 181.9019 | 187.4288 | 176.6312 | 152.6615
1629.7535 | 1519.7535 | 305.6084 | 201.3968 | 240.6404 | 204.7685 | 196.4544 | 181.9864 | 187.5023 | 176.6922 | 152.7113
1630.7549 | 1520.7549 | 305.701 | 201.4525 | 240.7181 | 204.7913 | 196.5116 | 182.0672 | 187.5798 | 176.7368 | 152.7849
1631.7463 | 1521.7463 | 305.7034 | 201.5035 | 240.7617 | 204.8185 | 196.5949 | 182.142 | 187.655 | 176.7993 | 152.8189
1632.7478 | 1522.7478 | 305.6786 | 201.5344 | 240.8188 | 204.8415 | 196.671 | 182.2263 | 187.732 | 176.8485 | 152.8927
1633.7492 | 1523.7492 | 305.7038 | 201.5619 | 240.846 | 204.868 | 196.731 | 182.2894 | 187.8085 | 176.9159 | 152.9436
1634.7507 | 1524.7507 | 305.7678 | 201.597 | 240.891 | 204.9315 | 196.8227 | 182.3738 | 187.8752 | 176.9489 | 152.9996
1635.7521 | 1525.7521 | 305.8011 | 201.6274 | 240.893 | 204.9719 | 196.8948 | 182.4524 | 187.9569 | 177.001 | 153.0578
1636.7535 | 1526.7535 | 305.7666 | 201.661 | 240.9305 | 204.9983 | 196.9575 | 182.5166 | 188.0414 | 177.051 | 153.1183
1637.755 | 1527.755 | 305.7335 | 201.6705 | 241.0379 | 205.0508 | 197.037 | 182.608 | 188.1185 | 177.11 | 153.1515
1638.7564 | 1528.7564 | 305.7318 | 201.7421 | 241.0699 | 205.1008 | 197.1091 | 182.6816 | 188.194 | 177.1515 | 153.2106
1639.7478 | 1529.7478 | 305.6964 | 201.7644 | 241.1221 | 205.1289 | 197.1963 | 182.765 | 188.2698 | 177.1836 | 153.2878
1640.7493 | 1530.7493 | 305.7196 | 201.8184 | 241.1164 | 205.1605 | 197.2594 | 182.8253 | 188.3437 | 177.242 | 153.3478
1641.7507 | 1531.7507 | 305.7079 | 201.844 | 241.1384 | 205.1975 | 197.3451 | 182.9035 | 188.4386 | 177.2881 | 153.4226
1642.7522 | 1532.7522 | 305.6756 | 201.8604 | 241.1897 | 205.2527 | 197.4161 | 182.9867 | 188.5096 | 177.3217 | 153.4543
1643.7536 | 1533.7536 | 305.6659 | 201.9184 | 241.1897 | 205.2962 | 197.482 | 183.0522 | 188.5971 | 177.3683 | 153.5165
1644.755 | 1534.755 | 305.6608 | 201.9535 | 241.2602 | 205.3234 | 197.5534 | 183.1313 | 188.6785 | 177.4053 | 153.5972
1645.7565 | 1535.7565 | 305.7431 | 201.9924 | 241.2857 | 205.3625 | 197.6317 | 183.2065 | 188.7495 | 177.4593 | 153.6179
1646.7479 | 1536.7479 | 305.8425 | 202.0264 | 241.3455 | 205.3892 | 197.7025 | 183.2824 | 188.8291 | 177.485 | 153.7082
1647.7493 | 1537.7493 | 305.806 | 202.0554 | 241.3825 | 205.4379 | 197.7789 | 183.3612 | 188.9228 | 177.5354 | 153.7473
1648.7508 | 1538.7508 | 305.7001 | 202.1077 | 241.4149 | 205.4592 | 197.8542 | 183.4342 | 188.9924 | 177.5759 | 153.8364
1649.7522 | 1539.7522 | 305.6286 | 202.1399 | 241.4568 | 205.4913 | 197.93 | 183.5129 | 189.0802 | 177.6011 | 153.8982
1650.7537 | 1540.7537 | 305.5828 | 202.1589 | 241.4989 | 205.5232 | 198.0141 | 183.589 | 189.1568 | 177.6504 | 153.9668
1651.7551 | 1541.7551 | 305.5608 | 202.2123 | 241.5317 | 205.5636 | 198.0597 | 183.6614 | 189.2335 | 177.7049 | 153.9939
1652.7565 | 1542.7565 | 305.5123 | 202.2344 | 241.5667 | 205.589 | 198.1584 | 183.7348 | 189.3069 | 177.7323 | 154.0685
1653.748 | 1543.748 | 305.4512 | 202.2691 | 241.5499 | 205.5979 | 198.2382 | 183.8173 | 189.3878 | 177.7992 | 154.1218
1654.7494 | 1544.7494 | 305.4009 | 202.3172 | 241.6195 | 205.6719 | 198.2872 | 183.8831 | 189.4652 | 177.8368 | 154.181
1655.7509 | 1545.7509 | 305.4572 | 202.3355 | 241.6336 | 205.6953 | 198.3748 | 183.9676 | 189.5469 | 177.874 | 154.2392
1656.7523 | 1546.7523 | 305.4822 | 202.3905 | 241.6757 | 205.7319 | 198.4374 | 184.0313 | 189.6275 | 177.9331 | 154.2961
1657.7537 | 1547.7537 | 305.499 | 202.3739 | 241.7205 | 205.7587 | 198.5226 | 184.1139 | 189.7025 | 177.9573 | 154.3585
1658.7552 | 1548.7552 | 305.4755 | 202.4495 | 241.7539 | 205.8075 | 198.5827 | 184.1805 | 189.7884 | 177.9992 | 154.4287
1659.7466 | 1549.7466 | 305.4639 | 202.4567 | 241.751 | 205.8197 | 198.6646 | 184.2613 | 189.8668 | 178.0265 | 154.4853
1660.748 | 1550.748 | 305.4758 | 202.5146 | 241.819 | 205.8643 | 198.7343 | 184.3372 | 189.9451 | 178.0845 | 154.5378
1661.7495 | 1551.7495 | 305.4217 | 202.5683 | 241.8558 | 205.9104 | 198.7923 | 184.4077 | 190.0263 | 178.1153 | 154.6183
1662.7509 | 1552.7509 | 305.3825 | 202.5712 | 241.9121 | 205.9587 | 198.8741 | 184.4924 | 190.0984 | 178.1592 | 154.6778
1663.7524 | 1553.7524 | 305.3954 | 202.6247 | 241.9355 | 205.991 | 198.9417 | 184.5592 | 190.1754 | 178.1892 | 154.7491
1664.7538 | 1554.7538 | 305.4393 | 202.627 | 241.9878 | 206.0113 | 199.027 | 184.642 | 190.2577 | 178.2433 | 154.7807
1665.7552 | 1555.7552 | 305.4976 | 202.7083 | 241.948 | 206.0537 | 199.0898 | 184.7041 | 190.3255 | 178.302 | 154.8346
1666.7467 | 1556.7467 | 305.6542 | 202.7091 | 242.0685 | 206.0592 | 199.1668 | 184.7878 | 190.4036 | 178.3502 | 154.8942
1667.7481 | 1557.7481 | 305.7948 | 202.7781 | 242.011 | 206.1146 | 199.2292 | 184.8503 | 190.4727 | 178.3899 | 154.9486
1668.7495 | 1558.7495 | 305.7514 | 202.8051 | 242.0843 | 206.1368 | 199.3089 | 184.9277 | 190.5513 | 178.4377 | 155.0088
1669.751 | 1559.751 | 305.8078 | 202.8608 | 242.1302 | 206.1785 | 199.3606 | 184.9941 | 190.6203 | 178.494 | 155.0693
1670.7524 | 1560.7524 | 305.9057 | 202.8703 | 242.2005 | 206.1675 | 199.4471 | 185.0794 | 190.6913 | 178.5577 | 155.1044
1671.7539 | 1561.7539 | 305.9787 | 202.9162 | 242.204 | 206.2051 | 199.5191 | 185.1508 | 190.7634 | 178.5979 | 155.1527
1672.7553 | 1562.7553 | 305.9275 | 202.9345 | 242.2411 | 206.2231 | 199.5841 | 185.2161 | 190.8435 | 178.6424 | 155.2165
1673.7567 | 1563.7567 | 306.0297 | 202.9548 | 242.2957 | 206.2827 | 199.6537 | 185.2975 | 190.9146 | 178.7064 | 155.277
1674.7482 | 1564.7482 | 306.1393 | 202.9839 | 242.3443 | 206.343 | 199.7182 | 185.3622 | 190.9882 | 178.7528 | 155.3426
1675.7496 | 1565.7496 | 306.1566 | 203.018 | 242.3104 | 206.3938 | 199.7921 | 185.4396 | 191.0665 | 178.7981 | 155.3744
1676.751 | 1566.751 | 306.1953 | 203.0731 | 242.3248 | 206.4488 | 199.8506 | 185.5003 | 191.1367 | 178.8401 | 155.426
1677.7525 | 1567.7525 | 306.2696 | 203.0807 | 242.4071 | 206.4638 | 199.9252 | 185.5919 | 191.2071 | 178.8945 | 155.4684
1678.7539 | 1568.7539 | 306.3279 | 203.1382 | 242.4637 | 206.49 | 200.0022 | 185.6464 | 191.2856 | 178.9484 | 155.5185
1679.7554 | 1569.7554 | 306.3379 | 203.1725 | 242.5154 | 206.5055 | 200.0635 | 185.7328 | 191.3556 | 178.9857 | 155.5857
1680.7568 | 1570.7568 | 306.4037 | 203.2005 | 242.5106 | 206.5466 | 200.1265 | 185.8057 | 191.4332 | 179.0366 | 155.6359
1681.7482 | 1571.7482 | 306.4187 | 203.2525 | 242.5476 | 206.5619 | 200.1955 | 185.8695 | 191.5049 | 179.0846 | 155.6804
1682.7497 | 1572.7497 | 306.3357 | 203.2752 | 242.6013 | 206.6184 | 200.2559 | 185.9521 | 191.5804 | 179.1295 | 155.7403
1683.7511 | 1573.7511 | 306.2512 | 203.345 | 242.5846 | 206.6801 | 200.3301 | 186.0104 | 191.6551 | 179.1689 | 155.798
1684.7526 | 1574.7526 | 306.2385 | 203.343 | 242.6455 | 206.6998 | 200.415 | 186.1017 | 191.7345 | 179.2222 | 155.8351
1685.754 | 1575.754 | 306.246 | 203.3966 | 242.7031 | 206.7388 | 200.4512 | 186.163 | 191.8129 | 179.257 | 155.8973
1686.7554 | 1576.7554 | 306.2256 | 203.4268 | 242.7546 | 206.7633 | 200.5371 | 186.2339 | 191.8864 | 179.3071 | 155.9386
1687.7569 | 1577.7569 | 306.2221 | 203.4843 | 242.7154 | 206.8072 | 200.6098 | 186.3043 | 191.959 | 179.3381 | 155.9859
1688.7483 | 1578.7483 | 306.1935 | 203.5001 | 242.8115 | 206.864 | 200.6703 | 186.3861 | 192.0341 | 179.3776 | 156.0627
1689.7497 | 1579.7497 | 306.2206 | 203.5354 | 242.8435 | 206.8705 | 200.7354 | 186.4484 | 192.1253 | 179.4232 | 156.1038
1690.7512 | 1580.7512 | 306.1573 | 203.5749 | 242.8395 | 206.9324 | 200.7987 | 186.5174 | 192.2059 | 179.4654 | 156.1571
1691.7526 | 1581.7526 | 306.0824 | 203.5908 | 242.9224 | 206.9496 | 200.8875 | 186.6044 | 192.2783 | 179.4951 | 156.196
1692.7541 | 1582.7541 | 306.1199 | 203.6506 | 242.9418 | 206.9892 | 200.9374 | 186.6617 | 192.3524 | 179.5336 | 156.2516
1693.7555 | 1583.7555 | 306.1602 | 203.6729 | 242.9645 | 206.9967 | 201.0019 | 186.7391 | 192.4331 | 179.5561 | 156.3412
1694.7569 | 1584.7569 | 306.0605 | 203.6991 | 243.0047 | 207.0705 | 201.0739 | 186.8031 | 192.5138 | 179.5952 | 156.3808
1695.7484 | 1585.7484 | 305.9754 | 203.7307 | 243.0528 | 207.0907 | 201.1529 | 186.8918 | 192.5893 | 179.6113 | 156.4586
1696.7498 | 1586.7498 | 306.0094 | 203.778 | 243.0719 | 207.1278 | 201.2084 | 186.9469 | 192.6647 | 179.6547 | 156.4996
1697.7512 | 1587.7512 | 306.1089 | 203.8101 | 243.0997 | 207.1698 | 201.2831 | 187.0265 | 192.749 | 179.6966 | 156.551
1698.7527 | 1588.7527 | 306.2354 | 203.8345 | 243.1603 | 207.1721 | 201.3438 | 187.1058 | 192.8227 | 179.7277 | 156.6024
1699.7541 | 1589.7541 | 306.3753 | 203.887 | 243.1717 | 207.2217 | 201.3996 | 187.1599 | 192.8912 | 179.765 | 156.6704
1700.7556 | 1590.7556 | 306.445 | 203.9043 | 243.1665 | 207.2528 | 201.4749 | 187.2371 | 192.9723 | 179.7759 | 156.7343
1701.747 | 1591.747 | 306.4271 | 203.9558 | 243.2034 | 207.3033 | 201.5438 | 187.3028 | 193.046 | 179.8109 | 156.7815
1702.7484 | 1592.7484 | 306.463 | 203.9455 | 243.3149 | 207.3071 | 201.6231 | 187.3817 | 193.124 | 179.8498 | 156.8194
1703.7499 | 1593.7499 | 306.5995 | 204.0346 | 243.2798 | 207.3462 | 201.6749 | 187.4331 | 193.2035 | 179.8658 | 156.9
1704.7513 | 1594.7513 | 306.6488 | 204.077 | 243.3685 | 207.3459 | 201.7509 | 187.5111 | 193.282 | 179.9161 | 156.9515
1705.7528 | 1595.7528 | 306.6711 | 204.0913 | 243.404 | 207.3795 | 201.8176 | 187.5777 | 193.3536 | 179.9448 | 157.0168
1706.7542 | 1596.7542 | 306.6595 | 204.131 | 243.4154 | 207.411 | 201.8783 | 187.6506 | 193.4337 | 179.9895 | 157.0547
1707.7456 | 1597.7456 | 306.6581 | 204.162 | 243.4837 | 207.4414 | 201.9482 | 187.7168 | 193.5048 | 180.0423 | 157.1272
1708.7471 | 1598.7471 | 306.7268 | 204.1926 | 243.441 | 207.4714 | 202.011 | 187.7842 | 193.576 | 180.0786 | 157.1672
1709.7485 | 1599.7485 | 306.6483 | 204.2107 | 243.4436 | 207.4874 | 202.0908 | 187.8582 | 193.6428 | 180.1354 | 157.2142
1710.7499 | 1600.7499 | 306.5933 | 204.2552 | 243.5303 | 207.5735 | 202.1503 | 187.9202 | 193.7263 | 180.1721 | 157.2676
1711.7514 | 1601.7514 | 306.61 | 204.2977 | 243.5572 | 207.6127 | 202.2317 | 187.9871 | 193.7934 | 180.2166 | 157.3389
1712.7528 | 1602.7528 | 306.5662 | 204.3294 | 243.5909 | 207.6439 | 202.2765 | 188.0711 | 193.8665 | 180.2662 | 157.3689
1713.7543 | 1603.7543 | 306.5023 | 204.3489 | 243.5652 | 207.6918 | 202.3513 | 188.1375 | 193.9435 | 180.3094 | 157.4216
1714.7557 | 1604.7557 | 306.451 | 204.4064 | 243.6126 | 207.7105 | 202.4027 | 188.203 | 194.0212 | 180.3563 | 157.4877
1715.7471 | 1605.7471 | 306.3501 | 204.4202 | 243.6488 | 207.7204 | 202.4751 | 188.2741 | 194.0939 | 180.4041 | 157.5352
1716.7486 | 1606.7486 | 306.3094 | 204.4579 | 243.6585 | 207.7288 | 202.5419 | 188.3396 | 194.1666 | 180.4488 | 157.5828
1717.75 | 1607.75 | 306.3625 | 204.4876 | 243.7356 | 207.7902 | 202.6052 | 188.4037 | 194.2402 | 180.5115 | 157.6188
1718.7514 | 1608.7514 | 306.3161 | 204.5304 | 243.7926 | 207.7986 | 202.6716 | 188.462 | 194.3114 | 180.5338 | 157.6823
1719.7529 | 1609.7529 | 306.2731 | 204.5388 | 243.7447 | 207.7632 | 202.7224 | 188.5545 | 194.3824 | 180.595 | 157.7513
1720.7543 | 1610.7543 | 306.2742 | 204.6004 | 243.81 | 207.8672 | 202.7864 | 188.6026 | 194.4608 | 180.6402 | 157.7837
1721.7558 | 1611.7558 | 306.2346 | 204.6099 | 243.8637 | 207.9155 | 202.8567 | 188.6733 | 194.5261 | 180.7125 | 157.8298
1722.7472 | 1612.7472 | 306.2512 | 204.6351 | 243.9179 | 207.9543 | 202.9182 | 188.7429 | 194.6084 | 180.7501 | 157.897
1723.7486 | 1613.7486 | 306.3004 | 204.6701 | 243.9743 | 207.9923 | 202.9862 | 188.8173 | 194.6799 | 180.7985 | 157.9409
1724.7501 | 1614.7501 | 306.2697 | 204.7331 | 243.9549 | 208.0284 | 203.0452 | 188.8847 | 194.7473 | 180.8688 | 157.9828
1725.7515 | 1615.7515 | 306.2589 | 204.7608 | 243.975 | 208.0685 | 203.1077 | 188.95 | 194.8211 | 180.9261 | 158.0283
1726.7529 | 1616.7529 | 306.2231 | 204.7819 | 244.0436 | 208.106 | 203.1615 | 189.021 | 194.8943 | 180.9697 | 158.0871
1727.7544 | 1617.7544 | 306.1731 | 204.8121 | 244.0563 | 208.1269 | 203.223 | 189.0869 | 194.9599 | 181.0207 | 158.1391
1728.7558 | 1618.7558 | 306.081 | 204.8433 | 244.0733 | 208.164 | 203.2886 | 189.1534 | 195.0404 | 181.0619 | 158.1982
1729.7573 | 1619.7573 | 306.0241 | 204.8967 | 244.1009 | 208.21 | 203.35 | 189.2193 | 195.1135 | 181.115 | 158.2398
1730.7487 | 1620.7487 | 306.0269 | 204.9106 | 244.1913 | 208.2404 | 203.4203 | 189.29 | 195.1907 | 181.1773 | 158.2812
1731.7501 | 1621.7501 | 305.9662 | 204.9592 | 244.1742 | 208.269 | 203.4928 | 189.3519 | 195.2616 | 181.216 | 158.3554
1732.7516 | 1622.7516 | 305.8721 | 204.9775 | 244.2346 | 208.2987 | 203.5469 | 189.4194 | 195.3352 | 181.2489 | 158.4271
1733.753 | 1623.753 | 305.7657 | 205.0066 | 244.2791 | 208.338 | 203.6051 | 189.4975 | 195.4019 | 181.3193 | 158.4573
1734.7545 | 1624.7545 | 305.5962 | 205.069 | 244.2899 | 208.3666 | 203.672 | 189.5622 | 195.4822 | 181.3603 | 158.5191
1735.7559 | 1625.7559 | 305.5302 | 205.0879 | 244.3309 | 208.4103 | 203.7305 | 189.6248 | 195.5494 | 181.4108 | 158.5551
1736.7573 | 1626.7573 | 305.632 | 205.1244 | 244.3561 | 208.4377 | 203.8011 | 189.6967 | 195.632 | 181.4519 | 158.6112
1737.7488 | 1627.7488 | 305.7227 | 205.1649 | 244.3869 | 208.48 | 203.8548 | 189.767 | 195.7011 | 181.5126 | 158.661
1738.7502 | 1628.7502 | 305.7989 | 205.2089 | 244.42 | 208.5214 | 203.9237 | 189.8255 | 195.7782 | 181.5532 | 158.7114
1739.7516 | 1629.7516 | 305.8633 | 205.238 | 244.4154 | 208.5517 | 203.974 | 189.8912 | 195.8436 | 181.6026 | 158.7611
1740.7531 | 1630.7531 | 305.8852 | 205.2693 | 244.4857 | 208.5675 | 204.0386 | 189.965 | 195.9214 | 181.6375 | 158.8337
1741.7545 | 1631.7545 | 305.8976 | 205.3027 | 244.5091 | 208.579 | 204.0859 | 190.0233 | 195.9923 | 181.6855 | 158.89
1742.756 | 1632.756 | 305.951 | 205.319 | 244.5581 | 208.6374 | 204.1572 | 190.0943 | 196.0662 | 181.7429 | 158.9151
1743.7474 | 1633.7474 | 305.9699 | 205.3641 | 244.6083 | 208.6735 | 204.2233 | 190.1614 | 196.1402 | 181.7857 | 158.9965
1744.7488 | 1634.7488 | 306.0549 | 205.3948 | 244.6517 | 208.7053 | 204.2759 | 190.2273 | 196.21 | 181.8358 | 159.0446
1745.7503 | 1635.7503 | 306.1836 | 205.4215 | 244.6226 | 208.7289 | 204.3379 | 190.2991 | 196.279 | 181.8878 | 159.1024
1746.7517 | 1636.7517 | 306.2024 | 205.4771 | 244.702 | 208.7548 | 204.3868 | 190.3677 | 196.355 | 181.9641 | 159.147
1747.7531 | 1637.7531 | 306.1782 | 205.4868 | 244.7386 | 208.7978 | 204.4676 | 190.4403 | 196.4125 | 182.0034 | 159.1973
1748.7546 | 1638.7546 | 306.1717 | 205.5173 | 244.7179 | 208.8216 | 204.5266 | 190.5011 | 196.4948 | 182.0635 | 159.251
1749.756 | 1639.756 | 306.1869 | 205.5706 | 244.7665 | 208.8585 | 204.5781 | 190.5569 | 196.5546 | 182.1219 | 159.2969
1750.7475 | 1640.7475 | 306.2709 | 205.5569 | 244.7605 | 208.88 | 204.6448 | 190.6307 | 196.6277 | 182.18 | 159.3364
1751.7489 | 1641.7489 | 306.3566 | 205.615 | 244.7958 | 208.8952 | 204.6947 | 190.7009 | 196.6962 | 182.2277 | 159.3749
1752.7503 | 1642.7503 | 306.3537 | 205.6355 | 244.8143 | 208.9357 | 204.7549 | 190.7541 | 196.7562 | 182.2885 | 159.4162
1753.7518 | 1643.7518 | 306.2774 | 205.6802 | 244.8766 | 208.999 | 204.8104 | 190.8255 | 196.8321 | 182.3281 | 159.489
1754.7532 | 1644.7532 | 306.2836 | 205.6869 | 244.9215 | 209.0254 | 204.879 | 190.8933 | 196.8889 | 182.3966 | 159.5151
1755.7547 | 1645.7547 | 306.2834 | 205.7324 | 244.9492 | 209.0518 | 204.9297 | 190.9565 | 196.9652 | 182.4567 | 159.5629
1756.7461 | 1646.7461 | 306.3076 | 205.769 | 244.9384 | 209.0703 | 204.9997 | 191.0237 | 197.0255 | 182.5108 | 159.617
1757.7475 | 1647.7475 | 306.2835 | 205.7847 | 245.0028 | 209.0927 | 205.0366 | 191.0783 | 197.092 | 182.5466 | 159.6745
1758.749 | 1648.749 | 306.2085 | 205.8306 | 245.013 | 209.1257 | 205.1023 | 191.1523 | 197.1578 | 182.6169 | 159.73
1759.7504 | 1649.7504 | 306.156 | 205.8659 | 245.0535 | 209.1562 | 205.1509 | 191.2098 | 197.2229 | 182.6785 | 159.7541
1760.7518 | 1650.7518 | 306.195 | 205.8624 | 245.0943 | 209.1892 | 205.227 | 191.2975 | 197.2862 | 182.745 | 159.7977
1761.7533 | 1651.7533 | 306.1439 | 205.9119 | 245.1206 | 209.2237 | 205.2684 | 191.345 | 197.3513 | 182.7903 | 159.8649
1762.7547 | 1652.7547 | 306.0739 | 205.9348 | 245.1481 | 209.2708 | 205.3251 | 191.4166 | 197.416 | 182.8642 | 159.8882
1763.7562 | 1653.7562 | 305.9719 | 205.9538 | 245.169 | 209.2895 | 205.3843 | 191.4776 | 197.4815 | 182.9114 | 159.9286
1764.7476 | 1654.7476 | 305.8013 | 205.9107 | 245.188 | 209.2939 | 205.4663 | 191.5998 | 197.5557 | 182.9623 | 159.9693
1765.7891 | 1655.7891 | 305.6429 | 206.0244 | 245.225 | 209.3475 | 205.5086 | 191.6174 | 197.6324 | 183.023 | 160.0148
1766.7505 | 1656.7505 | 305.4273 | 206.0797 | 245.2472 | 209.4038 | 205.5537 | 191.6749 | 197.6937 | 183.0736 | 160.0564
1767.7519 | 1657.7519 | 305.2323 | 206.0928 | 245.2886 | 209.4249 | 205.6039 | 191.7408 | 197.7679 | 183.1034 | 160.1363
1768.7533 | 1658.7533 | 305.1572 | 206.1038 | 245.3124 | 209.4445 | 205.6759 | 191.8043 | 197.8314 | 183.1567 | 160.1799
1769.7548 | 1659.7548 | 305.1526 | 206.1313 | 245.308 | 209.4689 | 205.7248 | 191.8755 | 197.8978 | 183.2179 | 160.2061
1770.7562 | 1660.7562 | 305.1127 | 206.1419 | 245.372 | 209.499 | 205.7835 | 191.9427 | 197.9731 | 183.2667 | 160.2616
1771.7476 | 1661.7476 | 305.2205 | 200.8831 | 246.0734 | 207.5303 | 207.8676 | 198.4679 | 197.5304 | 183.0281 | 161.9811
1772.7491 | 1662.7491 | 305.199 | 206.2349 | 245.4601 | 209.547 | 205.9037 | 192.0875 | 198.1027 | 183.3625 | 160.3571
1773.7505 | 1663.7505 | 305.08 | 206.2821 | 245.4387 | 209.5856 | 205.9621 | 192.1357 | 198.1729 | 183.4012 | 160.4394
1774.752 | 1664.752 | 305.0573 | 206.2826 | 245.4874 | 209.6089 | 206.0117 | 192.203 | 198.238 | 183.4685 | 160.4591
1775.7534 | 1665.7534 | 305.0541 | 206.3287 | 245.5094 | 209.6241 | 206.0718 | 192.2712 | 198.3047 | 183.5038 | 160.5382
1776.7548 | 1666.7548 | 305.0925 | 206.3694 | 245.5755 | 209.6639 | 206.1245 | 192.328 | 198.3729 | 183.5727 | 160.5539
1777.7563 | 1667.7563 | 305.0488 | 206.3918 | 245.5889 | 209.6631 | 206.1852 | 192.3988 | 198.4373 | 183.6185 | 160.6171
1778.7577 | 1668.7577 | 305.0714 | 206.4188 | 245.5974 | 209.7079 | 206.2379 | 192.4519 | 198.5077 | 183.6765 | 160.655
1779.7492 | 1669.7492 | 305.182 | 206.3978 | 245.6322 | 209.7306 | 206.3046 | 192.5288 | 198.5712 | 183.7226 | 160.6969
1780.7506 | 1670.7506 | 305.2805 | 206.497 | 245.6581 | 209.7847 | 206.3528 | 192.5821 | 198.6356 | 183.7647 | 160.7678
1781.752 | 1671.752 | 305.4174 | 206.517 | 245.6572 | 209.7904 | 206.4083 | 192.6556 | 198.7018 | 183.8175 | 160.8247
1782.7535 | 1672.7535 | 305.5481 | 206.5316 | 245.7318 | 209.8214 | 206.471 | 192.7244 | 198.7707 | 183.8834 | 160.8678
1783.7549 | 1673.7549 | 305.6969 | 206.5718 | 245.747 | 209.8551 | 206.5166 | 192.7854 | 198.8276 | 183.9413 | 160.8953
1784.7564 | 1674.7564 | 305.8118 | 206.5929 | 245.7573 | 209.8817 | 206.573 | 192.8571 | 198.8908 | 184.0009 | 160.9485
1785.7478 | 1675.7478 | 305.8872 | 206.6144 | 245.7867 | 209.9322 | 206.6278 | 192.9128 | 198.9526 | 184.0615 | 161.0068
1786.7492 | 1676.7492 | 306.0624 | 206.6411 | 245.8412 | 209.9687 | 206.6736 | 192.978 | 199.0142 | 184.1203 | 161.0499
1787.7507 | 1677.7507 | 306.1354 | 206.6881 | 245.821 | 210.0134 | 206.7266 | 193.0368 | 199.0787 | 184.1789 | 161.0964
1788.7521 | 1678.7521 | 306.1841 | 206.6961 | 245.8737 | 210.0366 | 206.7943 | 193.1138 | 199.1391 | 184.237 | 161.1519
1789.7535 | 1679.7535 | 306.1268 | 206.7419 | 245.8806 | 210.0643 | 206.8473 | 193.1743 | 199.1979 | 184.3113 | 161.1741
1790.755 | 1680.755 | 306.0684 | 206.7449 | 245.928 | 210.1029 | 206.8988 | 193.2452 | 199.261 | 184.3642 | 161.2325
1791.7564 | 1681.7564 | 306.0842 | 206.8184 | 245.9592 | 210.1253 | 206.9443 | 193.3063 | 199.3191 | 184.4254 | 161.2508
1792.7478 | 1682.7478 | 306.0372 | 206.7999 | 245.943 | 210.1213 | 207.0074 | 193.3767 | 199.3809 | 184.4734 | 161.3157
1793.7493 | 1683.7493 | 306.0786 | 206.8325 | 245.9848 | 210.1346 | 207.0529 | 193.4447 | 199.4451 | 184.5374 | 161.3416
1794.7507 | 1684.7507 | 306.1051 | 206.8781 | 245.9873 | 210.1435 | 207.1054 | 193.5026 | 199.506 | 184.5917 | 161.4017
1795.7522 | 1685.7522 | 306.1849 | 206.9089 | 246.0532 | 210.215 | 207.1688 | 193.5638 | 199.5569 | 184.6529 | 161.4479
1796.7536 | 1686.7536 | 306.1747 | 206.9554 | 246.108 | 210.2415 | 207.2201 | 193.6378 | 199.6259 | 184.704 | 161.4763
1797.755 | 1687.755 | 306.2568 | 206.9689 | 246.1049 | 210.2769 | 207.2633 | 193.7045 | 199.6823 | 184.7702 | 161.5019
1798.7465 | 1688.7465 | 306.3834 | 207.0106 | 246.1554 | 210.3002 | 207.3055 | 193.7644 | 199.7441 | 184.8108 | 161.5778
1799.7479 | 1689.7479 | 306.3725 | 207.0277 | 246.2064 | 210.345 | 207.3691 | 193.8365 | 199.7989 | 184.8702 | 161.6127
1800.7494 | 1690.7494 | 306.2625 | 207.0469 | 246.2171 | 210.2794 | 207.4301 | 193.9022 | 199.8539 | 184.9391 | 161.6409
1801.7508 | 1691.7508 | 306.2095 | 207.0798 | 246.2223 | 210.3813 | 207.4717 | 193.9613 | 199.9186 | 185.0036 | 161.6933
1802.7522 | 1692.7522 | 306.2849 | 207.089 | 246.2591 | 210.4062 | 207.5336 | 194.0234 | 199.98 | 185.0409 | 161.7629
1803.7537 | 1693.7537 | 306.2437 | 207.1325 | 246.2863 | 210.4332 | 207.5829 | 194.0901 | 200.0369 | 185.1069 | 161.7878
1804.7551 | 1694.7551 | 306.2286 | 207.1569 | 246.3409 | 210.4457 | 207.637 | 194.1606 | 200.0925 | 185.1617 | 161.8302
1805.7566 | 1695.7566 | 306.048 | 207.199 | 246.3456 | 210.4628 | 207.682 | 194.215 | 200.1509 | 185.2156 | 161.8785
1806.748 | 1696.748 | 306.0264 | 207.1986 | 246.3945 | 210.5055 | 207.7387 | 194.2824 | 200.2083 | 185.2785 | 161.9161
1807.7494 | 1697.7494 | 305.9242 | 207.2393 | 246.3104 | 210.5486 | 207.7914 | 194.337 | 200.2586 | 185.3262 | 161.9609
1808.7509 | 1698.7509 | 305.8599 | 207.2609 | 246.3451 | 210.6044 | 207.8356 | 194.4047 | 200.3214 | 185.3893 | 162.0007
1809.7523 | 1699.7523 | 305.8536 | 207.3041 | 246.3964 | 210.6393 | 207.894 | 194.462 | 200.3773 | 185.4405 | 162.0622
1810.7537 | 1700.7537 | 305.7372 | 207.3387 | 246.4649 | 210.6148 | 207.9488 | 194.5273 | 200.4387 | 185.4814 | 162.0977
1811.7552 | 1701.7552 | 305.7553 | 207.345 | 246.5179 | 210.6616 | 208.0058 | 194.5918 | 200.4922 | 185.5552 | 162.1423
1812.7566 | 1702.7566 | 305.8659 | 207.3723 | 246.5142 | 210.7017 | 208.0402 | 194.6521 | 200.5507 | 185.6029 | 162.1915
1813.748 | 1703.748 | 305.8267 | 207.4059 | 246.5716 | 210.7016 | 208.1056 | 194.7307 | 200.6026 | 185.6636 | 162.2217
1814.7495 | 1704.7495 | 305.7791 | 207.4439 | 246.5621 | 210.7636 | 208.1447 | 194.7947 | 200.6616 | 185.7319 | 162.2752
1815.7509 | 1705.7509 | 305.6707 | 207.4717 | 246.6312 | 210.7668 | 208.2051 | 194.8624 | 200.7154 | 185.7834 | 162.2956
1816.7524 | 1706.7524 | 305.6988 | 207.5142 | 246.5728 | 210.8039 | 208.2455 | 194.9313 | 200.7742 | 185.8535 | 162.3497
1817.7538 | 1707.7538 | 305.6525 | 207.4891 | 246.6363 | 210.837 | 208.3003 | 195.0082 | 200.8186 | 185.8903 | 162.4031
1818.7552 | 1708.7552 | 305.7362 | 207.5626 | 246.6982 | 210.8814 | 208.3569 | 195.0599 | 200.8774 | 185.9651 | 162.4279
1819.7567 | 1709.7567 | 305.8241 | 207.5414 | 246.735 | 210.8739 | 208.3967 | 195.122 | 200.9266 | 186.0237 | 162.4511
1820.7481 | 1710.7481 | 305.8848 | 207.5903 | 246.7239 | 210.9074 | 208.4481 | 195.1874 | 200.985 | 186.0597 | 162.5372
1821.7495 | 1711.7495 | 305.8616 | 207.6175 | 246.7752 | 210.9299 | 208.5003 | 195.2535 | 201.033 | 186.1306 | 162.5661
1822.751 | 1712.751 | 305.8727 | 207.6394 | 246.8107 | 210.9708 | 208.5499 | 195.3179 | 201.0857 | 186.1987 | 162.5796
1823.7524 | 1713.7524 | 305.9044 | 207.6595 | 246.8426 | 211.0029 | 208.6057 | 195.3715 | 201.1393 | 186.2415 | 162.6298
1824.7539 | 1714.7539 | 305.8998 | 207.6513 | 246.9016 | 211.0346 | 208.6596 | 195.4468 | 201.1928 | 186.3044 | 162.6803
1825.7553 | 1715.7553 | 305.8879 | 207.7381 | 246.8795 | 211.0738 | 208.7012 | 195.4973 | 201.2471 | 186.3475 | 162.7221
1826.7567 | 1716.7567 | 305.9237 | 207.7258 | 246.8791 | 211.1022 | 208.752 | 195.5752 | 201.3003 | 186.407 | 162.7679
1827.7482 | 1717.7482 | 305.9768 | 207.7885 | 246.9271 | 211.1223 | 208.7906 | 195.632 | 201.3486 | 186.468 | 162.8098
1828.7496 | 1718.7496 | 305.998 | 207.7951 | 246.9975 | 211.0894 | 208.8481 | 195.7107 | 201.4016 | 186.5204 | 162.8357
1829.7511 | 1719.7511 | 305.9101 | 207.8569 | 247.014 | 211.1518 | 208.8992 | 195.7611 | 201.4508 | 186.5718 | 162.9
1830.7525 | 1720.7525 | 305.8493 | 207.8922 | 246.9813 | 211.181 | 208.9486 | 195.8216 | 201.5025 | 186.6227 | 162.9342
1831.7539 | 1721.7539 | 305.8677 | 207.8785 | 247.0394 | 211.2139 | 209.006 | 195.8987 | 201.5519 | 186.6686 | 162.9806
1832.7554 | 1722.7554 | 305.9121 | 207.9083 | 247.0298 | 211.2384 | 209.0484 | 195.9618 | 201.6053 | 186.7219 | 163.0226
1833.7468 | 1723.7468 | 305.914 | 207.9477 | 247.0663 | 211.2854 | 209.1004 | 196.0131 | 201.6607 | 186.7831 | 163.0633
1834.7482 | 1724.7482 | 305.8243 | 207.9867 | 247.1365 | 211.3039 | 209.1551 | 196.0706 | 201.7052 | 186.8334 | 163.1154
1835.7497 | 1725.7497 | 305.821 | 207.9417 | 247.1997 | 211.338 | 209.207 | 196.1403 | 201.7568 | 186.8831 | 163.149
1836.7511 | 1726.7511 | 305.7642 | 208.0194 | 247.1274 | 211.3713 | 209.2492 | 196.2021 | 201.8088 | 186.9406 | 163.2023
1837.7526 | 1727.7526 | 305.7058 | 208.0637 | 247.2449 | 211.4081 | 209.3026 | 196.2607 | 201.857 | 186.965 | 163.2633
1838.754 | 1728.754 | 305.732 | 208.0705 | 247.2298 | 211.4325 | 209.3503 | 196.3259 | 201.9163 | 187.0434 | 163.293
1839.7554 | 1729.7554 | 305.7061 | 208.1225 | 247.2484 | 211.4497 | 209.3985 | 196.3813 | 201.9664 | 187.0924 | 163.313
1840.7469 | 1730.7469 | 305.5754 | 208.1366 | 247.2766 | 211.5004 | 209.4514 | 196.4451 | 202.022 | 187.1435 | 163.3797
1841.7483 | 1731.7483 | 305.4968 | 208.1728 | 247.2811 | 211.5228 | 209.5068 | 196.5085 | 202.0702 | 187.193 | 163.4121
1842.7497 | 1732.7497 | 305.4929 | 208.1797 | 247.3546 | 211.5287 | 209.5558 | 196.5772 | 202.1173 | 187.2354 | 163.4675
1843.7512 | 1733.7512 | 305.4611 | 208.2447 | 247.4181 | 211.573 | 209.6042 | 196.619 | 202.1686 | 187.2846 | 163.513
1844.7526 | 1734.7526 | 305.4775 | 208.239 | 247.3814 | 211.5932 | 209.6506 | 196.6886 | 202.2237 | 187.3233 | 163.5606
1845.7541 | 1735.7541 | 305.5216 | 208.2654 | 247.4307 | 211.6243 | 209.7015 | 196.743 | 202.2723 | 187.359 | 163.6105
1846.7555 | 1736.7555 | 305.5415 | 208.3341 | 247.3646 | 211.6623 | 209.7457 | 196.805 | 202.3318 | 187.4253 | 163.6414
1847.7569 | 1737.7569 | 305.522 | 208.3481 | 247.4882 | 211.698 | 209.8032 | 196.8627 | 202.3773 | 187.4751 | 163.6897
1848.7484 | 1738.7484 | 305.5818 | 208.377 | 247.4934 | 211.729 | 209.8521 | 196.9109 | 202.4301 | 187.5215 | 163.7461
1849.7498 | 1739.7498 | 305.746 | 208.3894 | 247.5648 | 211.7362 | 209.9097 | 196.9863 | 202.4792 | 187.569 | 163.7887
1850.7512 | 1740.7512 | 305.886 | 208.4514 | 247.5731 | 211.7665 | 209.9512 | 197.0394 | 202.5269 | 187.6082 | 163.8214
1851.7527 | 1741.7527 | 306.0123 | 208.4605 | 247.653 | 211.8015 | 209.9981 | 197.0955 | 202.5782 | 187.6508 | 163.8922
1852.7541 | 1742.7541 | 306.1162 | 208.4803 | 247.6348 | 211.8391 | 210.0474 | 197.1528 | 202.6312 | 187.7093 | 163.9196
1853.7556 | 1743.7556 | 306.1332 | 208.5067 | 247.677 | 211.852 | 210.0893 | 197.2114 | 202.6757 | 187.7474 | 163.9643
1854.757 | 1744.757 | 306.1756 | 208.5329 | 247.712 | 211.9015 | 210.1371 | 197.2641 | 202.7382 | 187.7956 | 163.9893
1855.7484 | 1745.7484 | 306.2087 | 208.5804 | 247.7326 | 211.9071 | 210.1932 | 197.3246 | 202.7855 | 187.8349 | 164.0385
1856.7499 | 1746.7499 | 306.25 | 208.587 | 247.7701 | 211.9349 | 210.2393 | 197.3868 | 202.8322 | 187.8738 | 164.0998
1857.7513 | 1747.7513 | 306.2586 | 208.6379 | 247.7757 | 211.9725 | 210.285 | 197.4336 | 202.8939 | 187.916 | 164.1248
1858.7528 | 1748.7528 | 306.3522 | 208.6292 | 247.8115 | 211.9977 | 210.3445 | 197.5064 | 202.9364 | 187.9654 | 164.177
1859.7542 | 1749.7542 | 306.4822 | 208.6592 | 247.87 | 212.0152 | 210.3929 | 197.5647 | 202.9913 | 187.9985 | 164.2349
1860.7556 | 1750.7556 | 306.4668 | 208.6907 | 247.8798 | 212.045 | 210.4475 | 197.6244 | 203.0395 | 188.0405 | 164.2759
1861.7771 | 1751.7771 | 306.495 | 208.7101 | 247.8514 | 212.0425 | 210.4785 | 197.6817 | 203.0906 | 188.0929 | 164.2986
1862.7485 | 1752.7485 | 306.5036 | 208.7622 | 247.936 | 212.0755 | 210.5341 | 197.7385 | 203.1392 | 188.1423 | 164.3431
1863.7499 | 1753.7499 | 306.5409 | 208.797 | 247.9663 | 212.1255 | 210.5806 | 197.8041 | 203.1805 | 188.1772 | 164.3855
1864.7514 | 1754.7514 | 306.564 | 208.8371 | 247.9783 | 212.1679 | 210.6406 | 197.8579 | 203.2406 | 188.2087 | 164.4641
1865.7528 | 1755.7528 | 306.6003 | 208.8351 | 248.0196 | 212.1879 | 210.687 | 197.9248 | 203.2823 | 188.2474 | 164.4967
1866.7543 | 1756.7543 | 306.5987 | 208.8639 | 248.0537 | 212.1805 | 210.7464 | 197.9921 | 203.3373 | 188.2972 | 164.5279
1867.7557 | 1757.7557 | 306.605 | 208.8975 | 248.0687 | 212.2271 | 210.784 | 198.0407 | 203.391 | 188.3387 | 164.5698
1868.7571 | 1758.7571 | 306.663 | 208.9396 | 248.063 | 212.2673 | 210.8251 | 198.1075 | 203.4388 | 188.3773 | 164.6049
1869.7486 | 1759.7486 | 306.599 | 208.97 | 248.1508 | 212.3065 | 210.8779 | 198.1632 | 203.4819 | 188.4207 | 164.649
1870.75 | 1760.75 | 306.5465 | 208.9913 | 248.162 | 212.3014 | 210.9371 | 198.225 | 203.534 | 188.4443 | 164.7346
1871.7514 | 1761.7514 | 306.6007 | 209.0191 | 248.1802 | 212.3349 | 210.9827 | 198.2835 | 203.583 | 188.4974 | 164.7683
1872.7529 | 1762.7529 | 306.7163 | 209.0356 | 248.2483 | 212.3808 | 211.0272 | 198.3425 | 203.6343 | 188.5399 | 164.8036
1873.7543 | 1763.7543 | 306.755 | 209.0598 | 248.2894 | 212.3863 | 211.0866 | 198.4054 | 203.681 | 188.5807 | 164.8638
1874.7558 | 1764.7558 | 306.7467 | 209.1262 | 248.3195 | 212.4027 | 211.125 | 198.4553 | 203.7329 | 188.6127 | 164.9057
1875.7572 | 1765.7572 | 306.7933 | 209.1466 | 248.3088 | 212.4509 | 211.1729 | 198.5148 | 203.7839 | 188.6675 | 164.9394
1876.7486 | 1766.7486 | 306.8418 | 209.1836 | 248.3624 | 212.4572 | 211.2172 | 198.5712 | 203.8254 | 188.7143 | 164.9902
1877.7501 | 1767.7501 | 306.8259 | 209.1708 | 248.3631 | 212.4774 | 211.2755 | 198.6323 | 203.8783 | 188.7704 | 165.029
1878.7515 | 1768.7515 | 306.7593 | 209.2003 | 248.4505 | 212.4934 | 211.3248 | 198.6888 | 203.9324 | 188.8039 | 165.0766
1879.753 | 1769.753 | 306.7754 | 209.2542 | 248.4687 | 212.5175 | 211.3694 | 198.7338 | 203.9762 | 188.8732 | 165.1037
1880.7544 | 1770.7544 | 306.6324 | 209.2452 | 248.5056 | 212.5361 | 211.4135 | 198.8034 | 204.0205 | 188.9219 | 165.147
1881.7558 | 1771.7558 | 306.5733 | 209.2878 | 248.4944 | 212.5771 | 211.4661 | 198.8564 | 204.0692 | 188.967 | 165.2021
1882.7473 | 1772.7473 | 306.5889 | 209.3012 | 248.54 | 212.6078 | 211.508 | 198.9068 | 204.1173 | 189.0139 | 165.255
1883.7487 | 1773.7487 | 306.4443 | 209.3429 | 248.5229 | 212.6511 | 211.5528 | 198.965 | 204.1605 | 189.0862 | 165.2533
1884.7501 | 1774.7501 | 306.2824 | 209.3394 | 248.5612 | 212.6752 | 211.5944 | 199.0232 | 204.213 | 189.124 | 165.3148
1885.7916 | 1775.7916 | 306.2091 | 209.3916 | 248.6279 | 212.7107 | 211.6342 | 199.0775 | 204.256 | 189.1823 | 165.3508
1886.753 | 1776.753 | 306.2476 | 209.4238 | 248.6151 | 212.7351 | 211.69 | 199.1343 | 204.2995 | 189.2406 | 165.4074
1887.7545 | 1777.7545 | 306.2326 | 209.434 | 248.6218 | 212.7743 | 211.7465 | 199.1903 | 204.3518 | 189.3052 | 165.4061
1888.7459 | 1778.7459 | 306.1178 | 209.4654 | 248.6873 | 212.8004 | 211.7839 | 199.243 | 204.4006 | 189.3429 | 165.4697
1889.7473 | 1779.7473 | 305.9596 | 209.5105 | 248.7194 | 212.7946 | 211.834 | 199.2968 | 204.4472 | 189.4044 | 165.4879
1890.7488 | 1780.7488 | 305.6927 | 209.5033 | 248.7867 | 212.8243 | 211.8905 | 199.3506 | 204.4912 | 189.4558 | 165.5335
1891.7502 | 1781.7502 | 305.3934 | 209.5424 | 248.7906 | 212.8741 | 211.9394 | 199.4101 | 204.5331 | 189.5058 | 165.5556
1892.7516 | 1782.7516 | 305.2404 | 209.5364 | 248.8051 | 212.8812 | 211.97 | 199.4646 | 204.5818 | 189.5463 | 165.6188
1893.7531 | 1783.7531 | 305.1491 | 209.6032 | 248.7858 | 212.9185 | 212.0208 | 199.5132 | 204.6356 | 189.5961 | 165.6466
1894.7545 | 1784.7545 | 305.0636 | 209.5849 | 248.8837 | 212.9273 | 212.0689 | 199.5817 | 204.6771 | 189.6527 | 165.6821
1895.756 | 1785.756 | 304.9146 | 209.6502 | 248.8751 | 212.9612 | 212.1135 | 199.6211 | 204.7303 | 189.6931 | 165.7325
1896.7474 | 1786.7474 | 304.7749 | 209.6517 | 248.8843 | 212.9998 | 212.1575 | 199.6763 | 204.7785 | 189.7325 | 165.7558
1897.7488 | 1787.7488 | 304.6858 | 209.6609 | 248.8903 | 213.0146 | 212.1997 | 199.7329 | 204.8179 | 189.7797 | 165.8017
1898.7503 | 1788.7503 | 304.6024 | 209.6876 | 248.9722 | 213.0513 | 212.2533 | 199.8004 | 204.8668 | 189.8241 | 165.8374
1899.7517 | 1789.7517 | 304.4733 | 209.7028 | 248.9222 | 213.0572 | 212.3063 | 199.8471 | 204.9111 | 189.8632 | 165.8969
1900.7531 | 1790.7531 | 304.387 | 209.7523 | 248.937 | 213.1093 | 212.3443 | 199.896 | 204.9626 | 189.9069 | 165.9388
1901.7546 | 1791.7546 | 304.2989 | 209.7491 | 248.9374 | 213.1109 | 212.3964 | 199.9632 | 205.004 | 189.9553 | 165.9759
1902.756 | 1792.756 | 304.1764 | 209.7974 | 248.9491 | 213.1358 | 212.4398 | 200.0075 | 205.0585 | 189.9984 | 166.0083
1903.7575 | 1793.7575 | 304.1404 | 209.7429 | 249.0289 | 213.1268 | 212.4893 | 200.0998 | 205.0982 | 190.0449 | 166.0489
1904.7489 | 1794.7489 | 304.1709 | 209.8445 | 249.0416 | 213.1708 | 212.5231 | 200.112 | 205.1485 | 190.0953 | 166.0818
1905.7503 | 1795.7503 | 304.2662 | 209.8422 | 249.0694 | 213.1959 | 212.5786 | 200.1745 | 205.192 | 190.1357 | 166.1108
1906.7518 | 1796.7518 | 304.3119 | 209.9057 | 249.0794 | 213.2262 | 212.6177 | 200.2143 | 205.2393 | 190.1845 | 166.1426
1907.7532 | 1797.7532 | 304.3691 | 209.9251 | 249.1018 | 213.1973 | 212.6649 | 200.2635 | 205.2921 | 190.2216 | 166.212
1908.7547 | 1798.7547 | 304.3499 | 209.926 | 249.0931 | 213.249 | 212.708 | 200.33 | 205.3359 | 190.2651 | 166.2499
1909.7561 | 1799.7561 | 304.4422 | 209.9835 | 249.1684 | 213.31 | 212.7605 | 200.376 | 205.3802 | 190.3191 | 166.2879
1910.7575 | 1800.7575 | 304.5636 | 209.9416 | 249.192 | 213.3025 | 212.8191 | 200.5363 | 205.4149 | 190.363 | 166.3421
1911.759 | 1801.759 | 304.7204 | 210.0453 | 249.2039 | 213.3503 | 212.8276 | 200.4817 | 205.4772 | 190.3975 | 166.3782
1912.7504 | 1802.7504 | 304.7766 | 210.0123 | 249.1848 | 213.3756 | 212.8991 | 200.5538 | 205.5219 | 190.4494 | 166.4186
1913.7518 | 1803.7518 | 304.9053 | 210.0292 | 249.243 | 213.3932 | 212.9457 | 200.6732 | 205.5657 | 190.4995 | 166.4467
1914.7533 | 1804.7533 | 305.0427 | 210.0868 | 249.2914 | 213.4306 | 212.9733 | 200.6487 | 205.6117 | 190.5492 | 166.4805
1915.7547 | 1805.7547 | 305.1987 | 210.107 | 249.2737 | 213.4522 | 213.022 | 200.699 | 205.6591 | 190.5894 | 166.5253
1916.7562 | 1806.7562 | 305.2709 | 210.1141 | 249.3223 | 213.4726 | 213.0735 | 200.7581 | 205.7024 | 190.63 | 166.5683
1917.7476 | 1807.7476 | 305.2704 | 210.1636 | 249.3589 | 213.4845 | 213.1019 | 200.801 | 205.7493 | 190.6653 | 166.625
1918.749 | 1808.749 | 305.2788 | 210.1889 | 249.4195 | 213.5316 | 213.1583 | 200.8483 | 205.7994 | 190.7317 | 166.6275
1919.7505 | 1809.7505 | 305.3029 | 210.167 | 249.4667 | 213.5402 | 213.2059 | 200.912 | 205.8383 | 190.7759 | 166.6887
1920.7519 | 1810.7519 | 305.3722 | 210.2164 | 249.456 | 213.5513 | 213.2357 | 201.0432 | 205.8772 | 190.8132 | 166.7215
1921.7533 | 1811.7533 | 305.4739 | 210.2489 | 249.4358 | 213.5743 | 213.2915 | 201.0231 | 205.9331 | 190.853 | 166.7695
1922.7548 | 1812.7548 | 305.6116 | 210.2773 | 249.5097 | 213.6048 | 213.321 | 201.0673 | 205.9775 | 190.9012 | 166.7886
1923.7562 | 1813.7562 | 305.6716 | 210.2632 | 249.4928 | 213.6023 | 213.3783 | 201.1297 | 206.021 | 190.9425 | 166.8316
1924.7477 | 1814.7477 | 305.6257 | 210.3545 | 249.5399 | 213.6491 | 213.4134 | 201.1659 | 206.0655 | 190.9727 | 166.9018
1925.7491 | 1815.7491 | 305.596 | 210.35 | 249.5394 | 213.651 | 213.4633 | 201.2338 | 206.1122 | 191.0324 | 166.9071
1926.7505 | 1816.7505 | 305.6729 | 210.3842 | 249.5459 | 213.7202 | 213.503 | 201.2821 | 206.159 | 191.0642 | 166.9723
1927.752 | 1817.752 | 305.6766 | 210.3299 | 249.6069 | 213.7437 | 213.5712 | 201.422 | 206.2012 | 191.1009 | 167.0191
1928.7534 | 1818.7534 | 305.7308 | 210.445 | 249.6031 | 213.7765 | 213.584 | 201.3891 | 206.2559 | 191.1508 | 167.0382
1929.7549 | 1819.7549 | 305.6859 | 210.4611 | 249.6192 | 213.8155 | 213.6387 | 201.4416 | 206.2875 | 191.196 | 167.0849
1930.7463 | 1820.7463 | 305.6543 | 210.4376 | 249.6444 | 213.8211 | 213.6966 | 201.5509 | 206.3345 | 191.2199 | 167.1532
1931.7477 | 1821.7477 | 305.6715 | 210.5148 | 249.6435 | 213.8464 | 213.7298 | 201.5381 | 206.3858 | 191.2565 | 167.1752
1932.7492 | 1822.7492 | 305.6029 | 210.5039 | 249.7269 | 213.8655 | 213.7736 | 201.6095 | 206.4268 | 191.2912 | 167.1898
1933.7506 | 1823.7506 | 305.455 | 210.5395 | 249.7498 | 213.8977 | 213.8101 | 201.6539 | 206.4762 | 191.3111 | 167.2828
1934.752 | 1824.752 | 305.4306 | 210.5547 | 249.7737 | 213.9194 | 213.8738 | 201.7245 | 206.5251 | 191.3298 | 167.3316
1935.7535 | 1825.7535 | 305.4605 | 210.5972 | 249.771 | 213.9428 | 213.9062 | 201.7663 | 206.5721 | 191.3823 | 167.3767
1936.7549 | 1826.7549 | 305.504 | 210.5994 | 249.8457 | 213.9695 | 213.9567 | 201.8284 | 206.6138 | 191.4091 | 167.4287
1937.7564 | 1827.7564 | 305.5295 | 210.6563 | 249.8748 | 213.9752 | 214.0059 | 201.9142 | 206.661 | 191.4514 | 167.465
1938.7478 | 1828.7478 | 305.5267 | 210.6699 | 249.796 | 214.0162 | 214.0338 | 201.9305 | 206.7123 | 191.4937 | 167.51
1939.7492 | 1829.7492 | 305.4934 | 210.7016 | 249.8175 | 214.0438 | 214.0881 | 201.9842 | 206.7481 | 191.5334 | 167.553
1940.7507 | 1830.7507 | 305.5476 | 210.7087 | 249.892 | 214.0723 | 214.1282 | 202.0406 | 206.7959 | 191.5772 | 167.5865
1941.7521 | 1831.7521 | 305.7294 | 210.7403 | 249.8945 | 214.0913 | 214.1716 | 202.0937 | 206.8444 | 191.6203 | 167.6415
1942.7535 | 1832.7535 | 305.8494 | 210.7942 | 249.9226 | 214.1092 | 214.2186 | 202.1415 | 206.8872 | 191.6653 | 167.6714
1943.755 | 1833.755 | 305.8709 | 210.7972 | 249.9166 | 214.1054 | 214.266 | 202.2044 | 206.9343 | 191.7111 | 167.7071
1944.7564 | 1834.7564 | 305.8431 | 210.8236 | 249.9703 | 214.1586 | 214.2967 | 202.2916 | 206.9797 | 191.7566 | 167.7599
1945.7478 | 1835.7478 | 305.7909 | 210.8279 | 250.0278 | 214.1548 | 214.3449 | 202.3121 | 207.0273 | 191.8043 | 167.7873
1946.7493 | 1836.7493 | 305.7967 | 210.8529 | 250.0028 | 214.1972 | 214.3975 | 202.4337 | 207.0653 | 191.8251 | 167.8705
1947.7507 | 1837.7507 | 305.8688 | 210.8841 | 250.0369 | 214.2086 | 214.4247 | 202.4238 | 207.1172 | 191.8908 | 167.8815
1948.7522 | 1838.7522 | 305.8104 | 210.9302 | 250.0832 | 214.2621 | 214.474 | 202.4661 | 207.1567 | 191.9251 | 167.9353
1949.7536 | 1839.7536 | 305.8342 | 210.9388 | 250.0817 | 214.2804 | 214.5185 | 202.526 | 207.2022 | 191.9741 | 167.9477
1950.755 | 1840.755 | 305.896 | 210.9762 | 250.1133 | 214.2904 | 214.5625 | 202.5732 | 207.2446 | 191.996 | 168.0308
1951.7565 | 1841.7565 | 305.7805 | 210.9926 | 250.1567 | 214.2916 | 214.602 | 202.6228 | 207.2894 | 192.0638 | 168.049
1952.7579 | 1842.7579 | 305.7635 | 211.0085 | 250.2177 | 214.304 | 214.6536 | 202.6869 | 207.3351 | 192.1101 | 168.0735
1953.7494 | 1843.7494 | 305.7483 | 211.0461 | 250.1595 | 214.3436 | 214.6889 | 202.7707 | 207.3763 | 192.1482 | 168.137
1954.7508 | 1844.7508 | 305.8241 | 211.0382 | 250.2219 | 214.3382 | 214.7393 | 202.8027 | 207.4215 | 192.1945 | 168.1704
1955.7522 | 1845.7522 | 305.9909 | 211.1076 | 250.2336 | 214.4095 | 214.7623 | 202.8317 | 207.4663 | 192.2441 | 168.2021
1956.7537 | 1846.7537 | 306.2171 | 211.114 | 250.2994 | 214.4298 | 214.8005 | 202.8957 | 207.5095 | 192.3084 | 168.2313
1957.7551 | 1847.7551 | 306.3578 | 211.1355 | 250.2899 | 214.4717 | 214.85 | 202.9416 | 207.5608 | 192.3545 | 168.2821
1958.7566 | 1848.7566 | 306.3462 | 211.1461 | 250.3027 | 214.5118 | 214.8929 | 203.0034 | 207.604 | 192.4088 | 168.3084
1959.748 | 1849.748 | 306.4323 | 211.2002 | 250.3872 | 214.549 | 214.9275 | 203.0419 | 207.6515 | 192.4535 | 168.3509
1960.7494 | 1850.7494 | 306.535 | 211.2205 | 250.4065 | 214.5486 | 214.9698 | 203.1554 | 207.6913 | 192.5139 | 168.3903
1961.7509 | 1851.7509 | 306.4431 | 211.2674 | 250.4003 | 214.5827 | 214.9906 | 203.1524 | 207.74 | 192.5651 | 168.3978
1962.7523 | 1852.7523 | 306.3797 | 211.3026 | 250.4784 | 214.6165 | 215.0405 | 203.2001 | 207.7798 | 192.6002 | 168.4445
1963.7537 | 1853.7537 | 306.3481 | 211.2835 | 250.4509 | 214.6175 | 215.0879 | 203.2931 | 207.8273 | 192.6623 | 168.4899
1964.7552 | 1854.7552 | 306.2753 | 211.3287 | 250.5292 | 214.6385 | 215.1232 | 203.3139 | 207.8656 | 192.7053 | 168.5002
1965.7466 | 1855.7466 | 306.2878 | 211.3333 | 250.4913 | 214.6426 | 215.1669 | 203.3664 | 207.9164 | 192.7476 | 168.5524
1966.748 | 1856.748 | 306.2744 | 211.4108 | 250.4544 | 214.6853 | 215.2054 | 203.4078 | 207.9592 | 192.77 | 168.6
1967.7495 | 1857.7495 | 306.2647 | 211.4168 | 250.5593 | 214.7008 | 215.2425 | 203.4634 | 208.0019 | 192.8413 | 168.6148
1968.7509 | 1858.7509 | 306.2338 | 211.4315 | 250.5818 | 214.7617 | 215.2855 | 203.5096 | 208.0495 | 192.863 | 168.6863
1969.7524 | 1859.7524 | 306.2072 | 211.4376 | 250.6148 | 214.7766 | 215.3337 | 203.5682 | 208.1023 | 192.9245 | 168.6891
1970.7538 | 1860.7538 | 306.2695 | 211.4835 | 250.6544 | 214.8295 | 215.3607 | 203.6196 | 208.1401 | 192.9662 | 168.7552
1971.7552 | 1861.7552 | 306.2449 | 211.4979 | 250.6853 | 214.8435 | 215.4132 | 203.681 | 208.1788 | 193.0301 | 168.7673
1972.7467 | 1862.7467 | 306.2881 | 211.5061 | 250.6952 | 214.8535 | 215.4389 | 203.7194 | 208.2327 | 193.0695 | 168.8098
1973.7481 | 1863.7481 | 306.2763 | 211.562 | 250.6171 | 214.8849 | 215.4881 | 203.7714 | 208.2777 | 193.1208 | 168.8248
1974.7496 | 1864.7496 | 306.171 | 211.5747 | 250.6452 | 214.9291 | 215.5281 | 203.8287 | 208.3228 | 193.162 | 168.8845
1975.751 | 1865.751 | 306.124 | 211.5905 | 250.7431 | 214.9361 | 215.5643 | 203.886 | 208.3655 | 193.2005 | 168.9142
1976.7524 | 1866.7524 | 306.1954 | 211.618 | 250.7711 | 214.9823 | 215.5987 | 203.9383 | 208.4107 | 193.2398 | 168.9494
1977.7539 | 1867.7539 | 306.2308 | 211.6751 | 250.8122 | 214.9904 | 215.636 | 203.9786 | 208.4561 | 193.2712 | 169.0041
1978.7553 | 1868.7553 | 306.2262 | 211.662 | 250.8245 | 215.0046 | 215.6854 | 204.0445 | 208.4997 | 193.3227 | 169.0434
1979.7568 | 1869.7568 | 306.179 | 211.7269 | 250.8752 | 215.0326 | 215.7084 | 204.0864 | 208.5484 | 193.3666 | 169.0531
1980.7482 | 1870.7482 | 306.1826 | 211.7329 | 250.8853 | 215.0362 | 215.755 | 204.1472 | 208.5913 | 193.4141 | 169.0892
1981.7496 | 1871.7496 | 306.1373 | 211.7704 | 250.8979 | 215.0918 | 215.7941 | 204.1843 | 208.6384 | 193.4434 | 169.1396
1982.7511 | 1872.7511 | 306.0901 | 211.7542 | 250.9068 | 215.0984 | 215.8338 | 204.2529 | 208.6805 | 193.4891 | 169.1863
1983.7625 | 1873.7625 | 306.0373 | 211.8025 | 250.8336 | 215.1446 | 215.8709 | 204.298 | 208.7315 | 193.5245 | 169.2304
1984.7539 | 1874.7539 | 306.0405 | 211.8441 | 250.9229 | 215.1709 | 215.9069 | 204.3418 | 208.7736 | 193.5834 | 169.2444
1985.7554 | 1875.7554 | 306.0042 | 211.8999 | 250.9534 | 215.1996 | 215.9438 | 204.3799 | 208.824 | 193.5991 | 169.3183
1986.7468 | 1876.7468 | 305.9846 | 211.9334 | 250.97 | 215.2229 | 215.9763 | 204.4085 | 208.8699 | 193.6561 | 169.3061
1987.7482 | 1877.7482 | 306.0024 | 212.0625 | 251.0332 | 215.277 | 216.004 | 204.4386 | 208.9236 | 193.6865 | 169.3551
1988.7497 | 1878.7497 | 306.0214 | 212.079 | 251.0453 | 215.2607 | 216.039 | 204.4981 | 208.9644 | 193.7448 | 169.4004
1989.7511 | 1879.7511 | 305.9804 | 212.0928 | 251.0702 | 215.2852 | 216.0777 | 204.5479 | 209.0061 | 193.7747 | 169.4429
1990.7526 | 1880.7526 | 305.838 | 212.1216 | 251.1321 | 215.3194 | 216.1253 | 204.5891 | 209.044 | 193.8107 | 169.4898
1991.754 | 1881.754 | 305.6662 | 212.1318 | 251.0699 | 215.3213 | 216.1594 | 204.6498 | 209.0903 | 193.8639 | 169.5286
1992.7554 | 1882.7554 | 305.4306 | 212.1431 | 251.1515 | 215.3602 | 216.2009 | 204.7024 | 209.1453 | 193.911 | 169.5734
1993.7569 | 1883.7569 | 305.2263 | 212.1668 | 251.1192 | 215.4171 | 216.2362 | 204.7511 | 209.1939 | 193.9429 | 169.6247
1994.7483 | 1884.7483 | 304.9424 | 212.1911 | 251.1608 | 215.4367 | 216.2676 | 204.7991 | 209.2326 | 193.9866 | 169.6567
1995.7497 | 1885.7497 | 304.616 | 212.2235 | 251.1756 | 215.4439 | 216.3076 | 204.8542 | 209.2786 | 194.0432 | 169.6611
1996.7512 | 1886.7512 | 304.3386 | 212.2222 | 251.2219 | 215.4744 | 216.3319 | 204.9031 | 209.3241 | 194.0936 | 169.6966
1997.7526 | 1887.7526 | 304.1239 | 212.2179 | 251.2326 | 215.4874 | 216.382 | 204.9507 | 209.3667 | 194.1227 | 169.7648
1998.7541 | 1888.7541 | 303.8148 | 212.2658 | 251.2529 | 215.4783 | 216.4235 | 205.0021 | 209.4066 | 194.1576 | 169.7928
1999.7555 | 1889.7555 | 303.4918 | 212.2666 | 251.265 | 215.4964 | 216.4639 | 205.0598 | 209.4587 | 194.1887 | 169.8333
2000.7569 | 1890.7569 | 303.1324 | 212.2388 | 251.2826 | 215.5195 | 216.4948 | 205.1036 | 209.5006 | 194.24 | 169.8648
2001.7484 | 1891.7484 | 302.7319 | 212.2933 | 251.2622 | 215.5414 | 216.5272 | 205.157 | 209.5416 | 194.273 | 169.8897
2002.7498 | 1892.7498 | 302.3454 | 212.3017 | 251.3001 | 215.5289 | 216.5736 | 205.2038 | 209.5808 | 194.3003 | 169.9469
2003.7513 | 1893.7513 | 301.973 | 212.3393 | 251.3013 | 215.5532 | 216.6242 | 205.2648 | 209.627 | 194.3124 | 170.0034
2004.7527 | 1894.7527 | 301.6219 | 212.3389 | 251.314 | 215.5692 | 216.6528 | 205.312 | 209.6677 | 194.3564 | 170.0233
2005.7541 | 1895.7541 | 301.2866 | 212.3522 | 251.2854 | 215.5825 | 216.6858 | 205.3631 | 209.7161 | 194.3705 | 170.0777
2006.7556 | 1896.7556 | 300.8899 | 212.3689 | 251.296 | 215.6049 | 216.74 | 205.4139 | 209.7628 | 194.3959 | 170.1111
2007.747 | 1897.747 | 300.444 | 212.3783 | 251.3208 | 215.61 | 216.7815 | 205.4607 | 209.7998 | 194.4193 | 170.1589
2008.7484 | 1898.7484 | 300.0602 | 212.3884 | 251.2976 | 215.6198 | 216.8048 | 205.5077 | 209.8522 | 194.4707 | 170.1747
2009.7499 | 1899.7499 | 299.7441 | 212.378 | 251.308 | 215.618 | 216.8482 | 205.5652 | 209.8949 | 194.4985 | 170.2324
2010.7513 | 1900.7513 | 299.4247 | 212.4147 | 251.2853 | 215.6459 | 216.8869 | 205.6114 | 209.9394 | 194.5281 | 170.2654
2011.7528 | 1901.7528 | 299.0959 | 212.3863 | 251.2419 | 215.6508 | 216.9206 | 205.6681 | 209.9901 | 194.554 | 170.3263
2012.7542 | 1902.7542 | 298.692 | 212.4048 | 251.2823 | 215.6436 | 216.9528 | 205.7153 | 210.0345 | 194.5852 | 170.3608
2013.7456 | 1903.7456 | 298.3363 | 212.4017 | 251.3093 | 215.6403 | 216.9951 | 205.7699 | 210.0735 | 194.6117 | 170.4089
2014.7471 | 1904.7471 | 297.9324 | 212.4489 | 251.3232 | 215.6636 | 217.0189 | 205.8148 | 210.129 | 194.6468 | 170.444
2015.7485 | 1905.7485 | 297.6085 | 212.4187 | 251.2905 | 215.6718 | 217.0646 | 205.8649 | 210.1708 | 194.6729 | 170.4992
2016.7499 | 1906.7499 | 297.3092 | 212.4518 | 251.3413 | 215.6739 | 217.0911 | 205.9189 | 210.2231 | 194.7175 | 170.5406
2017.7514 | 1907.7514 | 296.9744 | 212.4643 | 251.3525 | 215.6902 | 217.1388 | 205.9677 | 210.2697 | 194.7594 | 170.5618
2018.7528 | 1908.7528 | 296.6744 | 212.4561 | 251.2819 | 215.6818 | 217.1741 | 206.0214 | 210.3136 | 194.8091 | 170.5831
2019.7543 | 1909.7543 | 296.3419 | 212.4727 | 251.3045 | 215.6931 | 217.2111 | 206.0656 | 210.3611 | 194.8312 | 170.6569
2020.7557 | 1910.7557 | 295.9996 | 212.4833 | 251.2847 | 215.7026 | 217.245 | 206.1103 | 210.4065 | 194.8684 | 170.6881
2021.7571 | 1911.7571 | 295.6362 | 212.4908 | 251.2961 | 215.6953 | 217.2651 | 206.1629 | 210.4618 | 194.91 | 170.7211
2022.7486 | 1912.7486 | 295.2709 | 212.4846 | 251.3745 | 215.7158 | 217.3128 | 206.2134 | 210.5068 | 194.963 | 170.7411
2023.75 | 1913.75 | 294.8916 | 212.4654 | 251.3055 | 215.7079 | 217.3444 | 206.2703 | 210.5496 | 195.0092 | 170.7773
2024.7514 | 1914.7514 | 294.5446 | 212.4413 | 251.2684 | 215.6781 | 217.3728 | 206.319 | 210.6007 | 195.0451 | 170.8337
2025.7529 | 1915.7529 | 294.2285 | 212.4711 | 251.2736 | 215.6792 | 217.4042 | 206.3601 | 210.6434 | 195.1032 | 170.8593
2026.7543 | 1916.7543 | 293.9 | 212.4644 | 251.267 | 215.6818 | 217.4507 | 206.4172 | 210.6926 | 195.1475 | 170.8853
2027.7558 | 1917.7558 | 293.43 | 212.4842 | 251.2596 | 215.6973 | 217.4764 | 206.4582 | 210.7412 | 195.1891 | 170.9197
2028.7572 | 1918.7572 | 293.0548 | 212.4671 | 251.1952 | 215.68 | 217.5083 | 206.5102 | 210.7826 | 195.2271 | 170.9657
2029.7486 | 1919.7486 | 292.6246 | 212.4524 | 251.1736 | 215.6952 | 217.5409 | 206.5515 | 210.8346 | 195.2665 | 170.9941
2030.7501 | 1920.7501 | 292.1073 | 212.4543 | 251.1982 | 215.6778 | 217.5693 | 206.6062 | 210.8757 | 195.3261 | 171.0027
2031.7515 | 1921.7515 | 291.6633 | 212.472 | 251.1737 | 215.6974 | 217.5944 | 206.6594 | 210.9241 | 195.3665 | 171.0452
2032.753 | 1922.753 | 291.2723 | 212.4684 | 251.1795 | 215.6691 | 217.6242 | 206.6996 | 210.9666 | 195.4287 | 171.0556
2033.7544 | 1923.7544 | 290.9542 | 212.4568 | 251.1573 | 215.6656 | 217.6593 | 206.7507 | 211.0153 | 195.4598 | 171.1075
2034.7558 | 1924.7558 | 290.6439 | 212.4649 | 251.1541 | 215.6566 | 217.6859 | 206.7978 | 211.0664 | 195.507 | 171.1456
2035.7573 | 1925.7573 | 290.3075 | 212.4714 | 251.1414 | 215.6438 | 217.7173 | 206.8434 | 211.1148 | 195.5464 | 171.1614
2036.7487 | 1926.7487 | 289.9512 | 212.4717 | 251.0698 | 215.6772 | 217.743 | 206.8849 | 211.1634 | 195.582 | 171.206
2037.7501 | 1927.7501 | 289.6952 | 212.4568 | 251.0571 | 215.6777 | 217.7737 | 206.9385 | 211.2153 | 195.6145 | 171.2399
2038.7516 | 1928.7516 | 289.3579 | 212.4369 | 251.0439 | 215.6626 | 217.7996 | 206.9836 | 211.2599 | 195.6657 | 171.2503
2039.753 | 1929.753 | 288.9616 | 212.4283 | 251.0312 | 215.6593 | 217.826 | 207.0296 | 211.3051 | 195.7046 | 171.2765
2040.7545 | 1930.7545 | 288.4791 | 212.4168 | 250.9778 | 215.6197 | 217.8629 | 207.0854 | 211.3561 | 195.7338 | 171.3224
2041.7559 | 1931.7559 | 288.0514 | 212.4168 | 250.9913 | 215.6223 | 217.8839 | 207.1281 | 211.4025 | 195.7808 | 171.3329
2042.7473 | 1932.7473 | 287.7324 | 212.4094 | 250.9771 | 215.6128 | 217.9128 | 207.1766 | 211.4539 | 195.801 | 171.3939
2043.7488 | 1933.7488 | 287.2862 | 212.3818 | 250.9059 | 215.5791 | 217.9482 | 207.2231 | 211.5017 | 195.8514 | 171.4077
2044.7502 | 1934.7502 | 286.8605 | 212.3894 | 250.9302 | 215.5774 | 217.9633 | 207.2637 | 211.5462 | 195.8902 | 171.4425
2045.7516 | 1935.7516 | 286.4375 | 212.3665 | 250.9231 | 215.5699 | 217.9958 | 207.3158 | 211.5982 | 195.9335 | 171.4708
2046.7531 | 1936.7531 | 286.034 | 212.367 | 250.8727 | 215.5594 | 218.0259 | 207.361 | 211.6503 | 195.9557 | 171.5161
2047.7545 | 1937.7545 | 285.6551 | 212.3555 | 250.848 | 215.5525 | 218.0482 | 207.4017 | 211.6952 | 196.0091 | 171.5449
2048.756 | 1938.756 | 285.3528 | 212.3581 | 250.8642 | 215.5238 | 218.0743 | 207.4527 | 211.7518 | 196.0489 | 171.5389
2049.7474 | 1939.7474 | 284.9854 | 212.3293 | 250.754 | 215.5171 | 218.1014 | 207.4965 | 211.8044 | 196.0808 | 171.5925
2050.7488 | 1940.7488 | 284.5206 | 212.3261 | 250.7485 | 215.4849 | 218.12 | 207.5407 | 211.8535 | 196.1017 | 171.6501
2051.7503 | 1941.7503 | 284.1021 | 212.297 | 250.7694 | 215.4842 | 218.1469 | 207.5855 | 211.9004 | 196.1617 | 171.6407
2052.7517 | 1942.7517 | 283.7151 | 212.2905 | 250.7283 | 215.4661 | 218.182 | 207.628 | 211.9503 | 196.2002 | 171.674
2053.7532 | 1943.7532 | 283.3182 | 212.261 | 250.7004 | 215.4454 | 218.1903 | 207.6768 | 211.9955 | 196.2198 | 171.7226
2054.7546 | 1944.7546 | 282.9386 | 212.2454 | 250.6242 | 215.4413 | 218.218 | 207.7248 | 212.0527 | 196.2705 | 171.7368
2055.746 | 1945.746 | 282.6638 | 212.2314 | 250.5722 | 215.4004 | 218.2415 | 207.7706 | 212.1005 | 196.316 | 171.7549
2056.7475 | 1946.7475 | 282.3924 | 212.2355 | 250.5615 | 215.3855 | 218.2646 | 207.8192 | 212.1546 | 196.3445 | 171.8021
2057.7489 | 1947.7489 | 281.9462 | 212.1966 | 250.4558 | 215.3828 | 218.2918 | 207.8589 | 212.2033 | 196.3933 | 171.8209
2058.7503 | 1948.7503 | 281.4134 | 212.1796 | 250.4697 | 215.3676 | 218.3059 | 207.9065 | 212.2502 | 196.4487 | 171.8441
2059.7518 | 1949.7518 | 280.9456 | 212.1731 | 250.4023 | 215.3352 | 218.3376 | 207.9481 | 212.3022 | 196.486 | 171.8669
2060.7532 | 1950.7532 | 280.5461 | 212.162 | 250.4071 | 215.3308 | 218.3603 | 207.9932 | 212.3539 | 196.526 | 171.899
2061.7547 | 1951.7547 | 280.0961 | 212.1313 | 250.3771 | 215.3158 | 218.3876 | 208.0313 | 212.4003 | 196.5512 | 171.9535
2062.7561 | 1952.7561 | 279.6932 | 212.1097 | 250.3666 | 215.2961 | 218.3973 | 208.0837 | 212.4514 | 196.6025 | 171.9788
2063.7475 | 1953.7475 | 279.3217 | 212.0687 | 250.2591 | 215.2687 | 218.4195 | 208.1177 | 212.5048 | 196.6385 | 172.0167
2064.749 | 1954.749 | 278.9785 | 212.0759 | 250.2873 | 215.2517 | 218.455 | 208.1792 | 212.5537 | 196.6836 | 172.0165
2065.8005 | 1955.8005 | 278.5614 | 211.9987 | 250.232 | 215.2328 | 218.4717 | 208.215 | 212.608 | 196.7197 | 172.0621
2066.7518 | 1956.7518 | 278.2547 | 212.0094 | 250.2014 | 215.1987 | 218.493 | 208.2625 | 212.6581 | 196.749 | 172.089
2067.7533 | 1957.7533 | 277.8936 | 211.9989 | 250.1106 | 215.1454 | 218.5098 | 208.2968 | 212.6999 | 196.7885 | 172.1195
2068.7547 | 1958.7547 | 277.4657 | 211.9564 | 250.0945 | 215.1222 | 218.5249 | 208.3454 | 212.7428 | 196.8115 | 172.1374
2069.7562 | 1959.7562 | 277.0284 | 211.9308 | 250.1113 | 215.1366 | 218.5582 | 208.3915 | 212.7986 | 196.8419 | 172.186
2070.7476 | 1960.7476 | 276.6285 | 211.9304 | 250.015 | 215.1203 | 218.5728 | 208.4447 | 212.8489 | 196.8697 | 172.2147
2071.749 | 1961.749 | 276.2794 | 211.9138 | 250.0279 | 215.0763 | 218.5958 | 208.4863 | 212.9019 | 196.8971 | 172.2654
2072.7505 | 1962.7505 | 275.8967 | 211.9057 | 249.9416 | 215.0488 | 218.6068 | 208.5254 | 212.9535 | 196.9379 | 172.2915
2073.7519 | 1963.7519 | 275.5183 | 211.8324 | 249.9237 | 214.9919 | 218.625 | 208.5692 | 212.9987 | 196.9553 | 172.35
2074.7533 | 1964.7533 | 275.0656 | 211.787 | 249.8646 | 214.9422 | 218.64 | 208.6092 | 213.045 | 196.9975 | 172.3567
2075.7548 | 1965.7548 | 274.6561 | 211.8208 | 249.8064 | 214.9558 | 218.6616 | 208.6532 | 213.0905 | 197.0251 | 172.3913
2076.7562 | 1966.7562 | 274.2152 | 211.7778 | 249.7841 | 214.9461 | 218.6675 | 208.6989 | 213.1454 | 197.0602 | 172.43
2077.7577 | 1967.7577 | 273.8036 | 211.7617 | 249.7601 | 214.912 | 218.6898 | 208.7434 | 213.1824 | 197.1016 | 172.4613
2078.7491 | 1968.7491 | 273.4297 | 211.7234 | 249.6597 | 214.8735 | 218.7097 | 208.785 | 213.2369 | 197.1465 | 172.4838
2079.7505 | 1969.7505 | 273.0775 | 211.7139 | 249.6059 | 214.8321 | 218.7344 | 208.8271 | 213.2837 | 197.1846 | 172.5052
2080.752 | 1970.752 | 272.8219 | 211.6759 | 249.5255 | 214.7692 | 218.739 | 208.8705 | 213.3323 | 197.2159 | 172.5382
2081.7534 | 1971.7534 | 272.4655 | 211.6376 | 249.5018 | 214.7378 | 218.7508 | 208.9136 | 213.3808 | 197.2591 | 172.5558
2082.7549 | 1972.7549 | 272.1534 | 211.6226 | 249.4407 | 214.7705 | 218.7664 | 208.9566 | 213.4288 | 197.2886 | 172.5975
2083.7563 | 1973.7563 | 271.8565 | 211.5913 | 249.4317 | 214.7435 | 218.7867 | 208.9941 | 213.4747 | 197.3316 | 172.6166
2084.7577 | 1974.7577 | 271.4739 | 211.5603 | 249.4299 | 214.6907 | 218.7923 | 209.0392 | 213.5251 | 197.3716 | 172.6664
2085.7492 | 1975.7492 | 271.0349 | 211.526 | 249.3401 | 214.6724 | 218.8032 | 209.0773 | 213.5724 | 197.4136 | 172.685
2086.7506 | 1976.7506 | 270.7115 | 211.4749 | 249.2755 | 214.6336 | 218.8246 | 209.1133 | 213.6166 | 197.4596 | 172.7091
2087.752 | 1977.752 | 270.3782 | 211.4565 | 249.317 | 214.6002 | 218.8319 | 209.1603 | 213.6646 | 197.5132 | 172.7083
2088.7535 | 1978.7535 | 270.047 | 211.4357 | 249.1792 | 214.5671 | 218.848 | 209.1998 | 213.7113 | 197.5522 | 172.7402
2089.7549 | 1979.7549 | 269.6102 | 211.3726 | 249.1258 | 214.5135 | 218.8571 | 209.2346 | 213.7564 | 197.5971 | 172.7512
2090.7564 | 1980.7564 | 269.183 | 211.3568 | 249.1405 | 214.4997 | 218.8673 | 209.281 | 213.812 | 197.641 | 172.7805
2091.7478 | 1981.7478 | 268.7986 | 211.3215 | 249.0697 | 214.4565 | 218.8911 | 209.3194 | 213.8487 | 197.6733 | 172.7925
2092.7492 | 1982.7492 | 268.4406 | 211.2998 | 248.9655 | 214.4451 | 218.9067 | 209.3639 | 213.8964 | 197.7207 | 172.813
2093.7507 | 1983.7507 | 268.1128 | 211.2545 | 248.9658 | 214.4169 | 218.9042 | 209.3999 | 213.9412 | 197.7553 | 172.8338
2094.7521 | 1984.7521 | 267.8097 | 211.2227 | 248.9019 | 214.3764 | 218.9288 | 209.4329 | 213.9825 | 197.7896 | 172.8533
2095.7535 | 1985.7535 | 267.4988 | 211.2155 | 248.8438 | 214.3203 | 218.9552 | 209.477 | 214.0306 | 197.8336 | 172.8875
2096.755 | 1986.755 | 267.0865 | 211.191 | 248.7692 | 214.2926 | 218.9762 | 209.515 | 214.0649 | 197.8618 | 172.9138
2097.7464 | 1987.7464 | 266.6946 | 211.1241 | 248.6842 | 214.2588 | 218.9916 | 209.552 | 214.1131 | 197.8968 | 172.9369
2098.7479 | 1988.7479 | 266.3242 | 211.1012 | 248.6219 | 214.2283 | 218.9996 | 209.5884 | 214.1542 | 197.9406 | 172.9406
2099.7493 | 1989.7493 | 265.9259 | 211.039 | 248.5842 | 214.1975 | 219.026 | 209.6354 | 214.2023 | 197.9772 | 172.9677
2100.7507 | 1990.7507 | 265.5177 | 210.9929 | 248.5091 | 214.1654 | 219.0375 | 209.6683 | 214.238 | 198.012 | 172.9835
2101.7522 | 1991.7522 | 265.1454 | 210.9704 | 248.463 | 214.0975 | 219.0582 | 209.7076 | 214.284 | 198.0489 | 173.0045
2102.7536 | 1992.7536 | 264.8251 | 210.9386 | 248.4046 | 214.06 | 219.0813 | 209.7465 | 214.3197 | 198.0806 | 173.0384
2103.7551 | 1993.7551 | 264.4909 | 210.9053 | 248.3994 | 213.9989 | 219.0882 | 209.7872 | 214.3696 | 198.1092 | 173.0647
2104.7565 | 1994.7565 | 264.0933 | 210.8777 | 248.3464 | 214.0021 | 219.1084 | 209.8201 | 214.4094 | 198.1496 | 173.0619
2105.7579 | 1995.7579 | 263.7766 | 210.8242 | 248.2588 | 213.9464 | 219.1417 | 209.8524 | 214.4503 | 198.1892 | 173.0807
2106.7494 | 1996.7494 | 263.4565 | 210.8091 | 248.2066 | 213.8928 | 219.1525 | 209.9061 | 214.4934 | 198.2246 | 173.1231
2107.7508 | 1997.7508 | 263.1471 | 210.7689 | 248.1192 | 213.8436 | 219.1695 | 209.9335 | 214.5343 | 198.2613 | 173.1388
2108.7522 | 1998.7522 | 262.8852 | 210.7276 | 248.0442 | 213.8014 | 219.1967 | 209.979 | 214.5719 | 198.3119 | 173.1374
2109.7537 | 1999.7537 | 262.5822 | 210.6597 | 247.9789 | 213.772 | 219.2132 | 210.0142 | 214.6201 | 198.335 | 173.1655
2110.7551 | 2000.7551 | 262.203 | 210.6493 | 247.9369 | 213.7595 | 219.228 | 210.0561 | 214.6563 | 198.3689 | 173.193
2111.7566 | 2001.7566 | 261.8962 | 210.6175 | 247.9046 | 213.7051 | 219.2597 | 210.0869 | 214.6971 | 198.4298 | 173.1774
2112.748 | 2002.748 | 261.4978 | 210.5871 | 247.8191 | 213.6671 | 219.2756 | 210.1228 | 214.7358 | 198.4634 | 173.1797
2113.7494 | 2003.7494 | 261.0857 | 210.5479 | 247.7557 | 213.6107 | 219.2863 | 210.1612 | 214.7788 | 198.4916 | 173.2169
2114.7509 | 2004.7509 | 260.7639 | 210.5017 | 247.6716 | 213.5933 | 219.3159 | 210.1933 | 214.8149 | 198.5233 | 173.2431
2115.7523 | 2005.7523 | 260.4061 | 210.4685 | 247.6049 | 213.5369 | 219.3311 | 210.2377 | 214.8551 | 198.5587 | 173.2569
2116.7537 | 2006.7537 | 260.0198 | 210.405 | 247.564 | 213.5115 | 219.3531 | 210.2694 | 214.8928 | 198.5978 | 173.2679
2117.7552 | 2007.7552 | 259.6681 | 210.3766 | 247.4932 | 213.4635 | 219.3646 | 210.3123 | 214.931 | 198.6268 | 173.2928
2118.7466 | 2008.7466 | 259.2758 | 210.3479 | 247.4334 | 213.4007 | 219.3783 | 210.346 | 214.9739 | 198.666 | 173.2979
2119.748 | 2009.748 | 258.9013 | 210.2937 | 247.3622 | 213.3545 | 219.4008 | 210.384 | 215.0121 | 198.6775 | 173.3268
2120.7495 | 2010.7495 | 258.6029 | 210.2262 | 247.2724 | 213.3288 | 219.4171 | 210.4228 | 215.0503 | 198.7298 | 173.3257
2121.7509 | 2011.7509 | 258.2638 | 210.2042 | 247.2154 | 213.267 | 219.4357 | 210.4544 | 215.092 | 198.7532 | 173.3558
2122.7524 | 2012.7524 | 257.968 | 210.1483 | 247.1706 | 213.199 | 219.4583 | 210.4885 | 215.1293 | 198.7931 | 173.3475
2123.7538 | 2013.7538 | 257.689 | 210.1125 | 247.0991 | 213.1778 | 219.471 | 210.5263 | 215.1656 | 198.8145 | 173.383
2124.7552 | 2014.7552 | 257.3382 | 210.0812 | 247.0235 | 213.1186 | 219.5043 | 210.5651 | 215.197 | 198.856 | 173.3725
2125.7567 | 2015.7567 | 256.9891 | 210.0312 | 246.9474 | 213.1081 | 219.5109 | 210.5941 | 215.2388 | 198.8822 | 173.4126
2126.7481 | 2016.7481 | 256.6285 | 209.9753 | 246.9395 | 213.043 | 219.5288 | 210.6308 | 215.2722 | 198.9133 | 173.4174
2127.7496 | 2017.7496 | 256.2658 | 209.9352 | 246.8365 | 212.9975 | 219.5519 | 210.6645 | 215.312 | 198.9475 | 173.4207
2128.751 | 2018.751 | 255.904 | 209.8956 | 246.7938 | 212.9443 | 219.5679 | 210.6984 | 215.3539 | 198.9781 | 173.4293
2129.7524 | 2019.7524 | 255.5545 | 209.8562 | 246.737 | 212.8956 | 219.5829 | 210.7379 | 215.3844 | 198.9896 | 173.4668
2130.7539 | 2020.7539 | 255.2557 | 209.8086 | 246.5928 | 212.8588 | 219.5996 | 210.7708 | 215.4229 | 199.0331 | 173.4831
2131.7553 | 2021.7553 | 254.8373 | 209.7509 | 246.6084 | 212.807 | 219.618 | 210.8038 | 215.4551 | 199.0558 | 173.5006
2132.7568 | 2022.7568 | 254.4073 | 209.712 | 246.4352 | 212.7377 | 219.6409 | 210.8403 | 215.494 | 199.0865 | 173.5029
2133.7482 | 2023.7482 | 254.0277 | 209.6403 | 246.3005 | 212.6972 | 219.6463 | 210.8795 | 215.5265 | 199.1024 | 173.5434
2134.7496 | 2024.7496 | 253.6381 | 209.5605 | 246.2728 | 212.6571 | 219.673 | 210.9077 | 215.5651 | 199.1242 | 173.5339
2135.7511 | 2025.7511 | 253.2454 | 209.5233 | 246.2404 | 212.6157 | 219.69 | 210.9405 | 215.6038 | 199.1556 | 173.5563
2136.7525 | 2026.7525 | 252.8916 | 209.5092 | 246.1808 | 212.5942 | 219.6994 | 210.9758 | 215.6284 | 199.1753 | 173.5672
2137.7539 | 2027.7539 | 252.5156 | 209.4402 | 246.1329 | 212.5621 | 219.7189 | 211.0122 | 215.6712 | 199.192 | 173.5851
2138.7454 | 2028.7454 | 252.1549 | 209.3808 | 246.0426 | 212.499 | 219.7248 | 211.0448 | 215.7106 | 199.1936 | 173.6153
2139.7468 | 2029.7468 | 251.8382 | 209.3316 | 245.9827 | 212.4326 | 219.7466 | 211.0772 | 215.7363 | 199.2158 | 173.6222
2140.7482 | 2030.7482 | 251.5597 | 209.2564 | 245.9129 | 212.3739 | 219.763 | 211.114 | 215.7686 | 199.2318 | 173.6537
2141.7497 | 2031.7497 | 251.2489 | 209.2473 | 245.858 | 212.3155 | 219.7833 | 211.1411 | 215.8058 | 199.237 | 173.6546
2142.7511 | 2032.7511 | 250.9744 | 209.2065 | 245.6923 | 212.2615 | 219.7963 | 211.1795 | 215.8445 | 199.2514 | 173.6977
2143.7526 | 2033.7526 | 250.6371 | 209.1512 | 245.6663 | 212.1979 | 219.8055 | 211.2168 | 215.8663 | 199.2611 | 173.7226
2144.754 | 2034.754 | 250.3251 | 209.1098 | 245.6097 | 212.1313 | 219.8338 | 211.238 | 215.9083 | 199.2817 | 173.7129
2145.7554 | 2035.7554 | 250.002 | 209.069 | 245.5005 | 212.0897 | 219.8497 | 211.279 | 215.936 | 199.2779 | 173.7621
2146.7569 | 2036.7569 | 249.6601 | 209.0189 | 245.4913 | 212.034 | 219.8561 | 211.3103 | 215.9644 | 199.3033 | 173.758
2147.7483 | 2037.7483 | 249.3124 | 208.9669 | 245.4747 | 211.9832 | 219.8773 | 211.3345 | 215.9911 | 199.3077 | 173.7936
2148.7498 | 2038.7498 | 249.0186 | 208.887 | 245.3857 | 211.9212 | 219.889 | 211.3707 | 216.0297 | 199.3217 | 173.8235
2149.7512 | 2039.7512 | 248.6994 | 208.8099 | 245.3285 | 211.8731 | 219.9051 | 211.4061 | 216.0558 | 199.3433 | 173.8261
2150.7526 | 2040.7526 | 248.2857 | 208.7912 | 245.1669 | 211.8273 | 219.9181 | 211.4391 | 216.0911 | 199.3611 | 173.8527
2151.7541 | 2041.7541 | 247.9456 | 208.742 | 245.1194 | 211.7562 | 219.933 | 211.481 | 216.1225 | 199.3745 | 173.8816
2152.7555 | 2042.7555 | 247.6443 | 208.7055 | 245.0389 | 211.7126 | 219.9522 | 211.5116 | 216.1552 | 199.3954 | 173.8963
2153.757 | 2043.757 | 247.3643 | 208.6487 | 244.9382 | 211.6668 | 219.9601 | 211.5369 | 216.1834 | 199.4298 | 173.8921
2154.7484 | 2044.7484 | 247.064 | 208.5904 | 244.8301 | 211.5754 | 219.9794 | 211.5762 | 216.2112 | 199.4317 | 173.9279
2155.7498 | 2045.7498 | 246.7598 | 208.5464 | 244.78 | 211.5524 | 219.9811 | 211.6081 | 216.2435 | 199.4642 | 173.943
2156.7513 | 2046.7513 | 246.3627 | 208.4943 | 244.6428 | 211.5084 | 219.9951 | 211.6298 | 216.2616 | 199.4802 | 173.9604
2157.7527 | 2047.7527 | 245.9687 | 208.4211 | 244.5848 | 211.4453 | 220 | 211.6647 | 216.2974 | 199.5157 | 173.9613
2158.7541 | 2048.7541 | 245.5309 | 208.3709 | 244.5133 | 211.3684 | 220.0099 | 211.6992 | 216.3233 | 199.5345 | 173.9596
2159.7556 | 2049.7556 | 245.1796 | 208.3191 | 244.4066 | 211.3144 | 220.0233 | 211.7306 | 216.3573 | 199.5605 | 173.9599
2160.747 | 2050.747 | 244.8346 | 208.2437 | 244.3152 | 211.271 | 220.0395 | 211.7542 | 216.3835 | 199.5608 | 173.9993
2161.7484 | 2051.7484 | 244.5212 | 208.167 | 244.2552 | 211.2112 | 220.0416 | 211.7839 | 216.4058 | 199.5994 | 173.9981
2162.7499 | 2052.7499 | 244.1641 | 208.129 | 244.1522 | 211.1356 | 220.0521 | 211.8157 | 216.4311 | 199.6135 | 174.0053
2163.7513 | 2053.7513 | 243.7917 | 208.0849 | 244.0967 | 211.0787 | 220.0668 | 211.8444 | 216.4555 | 199.6323 | 174.0031
2164.7528 | 2054.7528 | 243.5045 | 208.0456 | 243.9546 | 211.0166 | 220.0734 | 211.8725 | 216.4845 | 199.6452 | 174.0351
2165.7542 | 2055.7542 | 243.238 | 207.9955 | 243.9107 | 210.9562 | 220.0911 | 211.9025 | 216.5114 | 199.6637 | 174.054
2166.7556 | 2056.7556 | 242.9107 | 207.9241 | 243.8136 | 210.9056 | 220.0954 | 211.933 | 216.5416 | 199.6873 | 174.0309
2167.7571 | 2057.7571 | 242.5987 | 207.879 | 243.7443 | 210.8429 | 220.1078 | 211.9571 | 216.5612 | 199.6919 | 174.0651
2168.7485 | 2058.7485 | 242.249 | 207.8344 | 243.6681 | 210.7902 | 220.1085 | 211.9801 | 216.5897 | 199.6976 | 174.0765
2169.7499 | 2059.7499 | 241.9747 | 207.7817 | 243.6087 | 210.728 | 220.1222 | 212.0181 | 216.6143 | 199.707 | 174.0836
2170.7514 | 2060.7514 | 241.6933 | 207.7236 | 243.5294 | 210.669 | 220.1341 | 212.0379 | 216.6324 | 199.7245 | 174.0886
2171.7528 | 2061.7528 | 241.3741 | 207.6581 | 243.4198 | 210.5895 | 220.139 | 212.0726 | 216.6606 | 199.7397 | 174.1027
2172.7543 | 2062.7543 | 241.0335 | 207.5858 | 243.2815 | 210.5346 | 220.1389 | 212.0986 | 216.6835 | 199.7443 | 174.1163
2173.7557 | 2063.7557 | 240.6848 | 207.5109 | 243.2837 | 210.4776 | 220.1639 | 212.1256 | 216.7064 | 199.7525 | 174.1229
2174.7571 | 2064.7571 | 240.3152 | 207.48 | 243.1621 | 210.4207 | 220.1672 | 212.1498 | 216.742 | 199.7623 | 174.1388
2175.7486 | 2065.7486 | 239.9606 | 207.4422 | 243.0744 | 210.3656 | 220.1704 | 212.1749 | 216.7571 | 199.76 | 174.158
2176.75 | 2066.75 | 239.6965 | 207.3647 | 243.0244 | 210.3069 | 220.18 | 212.2102 | 216.7807 | 199.768 | 174.1798
2177.7515 | 2067.7515 | 239.4108 | 207.2917 | 242.9648 | 210.2425 | 220.1915 | 212.2334 | 216.8089 | 199.7989 | 174.1792
2178.7529 | 2068.7529 | 239.0626 | 207.2493 | 242.8374 | 210.1675 | 220.1893 | 212.2535 | 216.833 | 199.8088 | 174.1946
2179.7543 | 2069.7543 | 238.8408 | 207.1809 | 242.8199 | 210.1272 | 220.1994 | 212.282 | 216.8534 | 199.8049 | 174.197
2180.7458 | 2070.7458 | 238.6059 | 207.133 | 242.698 | 210.0672 | 220.2075 | 212.3113 | 216.8717 | 199.8276 | 174.2122
2181.7472 | 2071.7472 | 238.3041 | 207.0553 | 242.5663 | 209.9981 | 220.2083 | 212.3404 | 216.8982 | 199.8275 | 174.2329
2182.7486 | 2072.7486 | 237.9419 | 207.0013 | 242.4883 | 209.9298 | 220.2108 | 212.3647 | 216.9137 | 199.8414 | 174.2141
2183.7501 | 2073.7501 | 237.6331 | 206.9491 | 242.3999 | 209.8738 | 220.219 | 212.3868 | 216.9372 | 199.8539 | 174.2284
2184.7515 | 2074.7515 | 237.3071 | 206.8993 | 242.3493 | 209.7972 | 220.2335 | 212.4175 | 216.963 | 199.8634 | 174.2374
2185.793 | 2075.793 | 237.0054 | 206.8396 | 242.2366 | 209.7517 | 220.2371 | 212.4353 | 216.9859 | 199.8587 | 174.2706
2186.7544 | 2076.7544 | 236.7299 | 206.7442 | 242.1983 | 209.6685 | 220.2407 | 212.4585 | 217.0016 | 199.8574 | 174.2845
2187.7458 | 2077.7458 | 236.4714 | 206.704 | 242.1017 | 209.5974 | 220.2455 | 212.4864 | 217.0219 | 199.8706 | 174.2708
2188.7573 | 2078.7573 | 236.2157 | 206.6362 | 242.0113 | 209.5546 | 220.2575 | 212.5114 | 217.0445 | 199.8618 | 174.2994
2189.7487 | 2079.7487 | 235.9299 | 206.5818 | 241.8685 | 209.4847 | 220.2537 | 212.5443 | 217.0638 | 199.8724 | 174.3145
2190.7501 | 2080.7501 | 235.6284 | 206.5135 | 241.776 | 209.4391 | 220.2602 | 212.5622 | 217.0836 | 199.8762 | 174.3146
2191.7516 | 2081.7516 | 235.2964 | 206.4639 | 241.6735 | 209.3642 | 220.2623 | 212.5835 | 217.1028 | 199.8883 | 174.3169
2192.753 | 2082.753 | 234.9703 | 206.3952 | 241.6549 | 209.3045 | 220.2741 | 212.6051 | 217.1198 | 199.8871 | 174.3374
2193.7545 | 2083.7545 | 234.6475 | 206.3422 | 241.5352 | 209.2436 | 220.2737 | 212.6343 | 217.1465 | 199.8929 | 174.3439
2194.7559 | 2084.7559 | 234.3101 | 206.2676 | 241.4402 | 209.1664 | 220.2764 | 212.6632 | 217.1581 | 199.9011 | 174.3505
2195.7573 | 2085.7573 | 234.0745 | 206.2181 | 241.3274 | 209.103 | 220.2807 | 212.6843 | 217.178 | 199.9049 | 174.3447
2196.7488 | 2086.7488 | 233.8395 | 206.1404 | 241.2412 | 209.0387 | 220.2838 | 212.701 | 217.1968 | 199.9321 | 174.3526
2197.7502 | 2087.7502 | 233.5997 | 206.0806 | 241.1571 | 208.9847 | 220.2859 | 212.729 | 217.2177 | 199.9281 | 174.3538
2198.7516 | 2088.7516 | 233.3162 | 206.0187 | 241.0592 | 208.919 | 220.2821 | 212.7526 | 217.2305 | 199.939 | 174.3738
2199.7531 | 2089.7531 | 233.0991 | 205.9679 | 240.9154 | 208.8373 | 220.2819 | 212.7663 | 217.2471 | 199.9428 | 174.3793
2200.7545 | 2090.7545 | 232.7794 | 205.9116 | 240.8852 | 208.7429 | 220.292 | 212.7981 | 217.261 | 199.9446 | 174.3811
2201.756 | 2091.756 | 232.466 | 205.8389 | 240.7959 | 208.7045 | 220.2874 | 212.8171 | 217.2802 | 199.9479 | 174.4013
2202.7474 | 2092.7474 | 232.2309 | 205.7518 | 240.6981 | 208.6379 | 220.2914 | 212.8325 | 217.2968 | 199.9679 | 174.3784
2203.7488 | 2093.7488 | 231.8981 | 205.7162 | 240.6111 | 208.5746 | 220.2851 | 212.8552 | 217.3162 | 199.9776 | 174.4005
2204.7503 | 2094.7503 | 231.5291 | 205.6224 | 240.4967 | 208.4726 | 220.2983 | 212.8822 | 217.3279 | 199.991 | 174.3748
2205.7517 | 2095.7517 | 231.1832 | 205.5731 | 240.3747 | 208.4033 | 220.299 | 212.9008 | 217.3422 | 199.9824 | 174.4003
2206.7532 | 2096.7532 | 230.9049 | 205.5232 | 240.2622 | 208.3722 | 220.292 | 212.9204 | 217.3594 | 199.9871 | 174.4124
2207.7546 | 2097.7546 | 230.5987 | 205.4573 | 240.2802 | 208.2999 | 220.293 | 212.9418 | 217.3718 | 199.9979 | 174.4012
2208.756 | 2098.756 | 230.365 | 205.3994 | 240.1958 | 208.2373 | 220.2847 | 212.9623 | 217.3884 | 199.9962 | 174.4186
2209.7575 | 2099.7575 | 230.1376 | 205.3403 | 240.0636 | 208.1594 | 220.287 | 212.9784 | 217.4009 | 199.9985 | 174.4048
2210.7589 | 2100.7589 | 229.9007 | 205.2776 | 239.967 | 208.0867 | 220.2891 | 213.0005 | 217.4123 | 200.0016 | 174.4123
2211.7503 | 2101.7503 | 229.6563 | 205.1986 | 239.9256 | 208.0168 | 220.2895 | 213.0305 | 217.4295 | 199.9986 | 174.4303
2212.7518 | 2102.7518 | 229.4114 | 205.1158 | 239.7492 | 207.9671 | 220.2938 | 213.0499 | 217.4431 | 200.0211 | 174.4259
2213.7532 | 2103.7532 | 229.1524 | 205.0511 | 239.7085 | 207.865 | 220.2744 | 213.0611 | 217.4591 | 200.0369 | 174.4114
2214.7547 | 2104.7547 | 228.8516 | 204.9974 | 239.5609 | 207.8227 | 220.2812 | 213.0822 | 217.4702 | 200.0332 | 174.4213
2215.7561 | 2105.7561 | 228.5859 | 204.9255 | 239.4681 | 207.7504 | 220.2824 | 213.1086 | 217.4823 | 200.038 | 174.4237
2216.7575 | 2106.7575 | 228.3094 | 204.8417 | 239.4125 | 207.6816 | 220.2718 | 213.1196 | 217.49 | 200.0545 | 174.4073
2217.749 | 2107.749 | 227.9736 | 204.7586 | 239.3341 | 207.6102 | 220.2818 | 213.1382 | 217.505 | 200.0558 | 174.4219
2218.7504 | 2108.7504 | 227.6791 | 204.6876 | 239.232 | 207.5461 | 220.2801 | 213.1579 | 217.5218 | 200.0686 | 174.4014
2219.7518 | 2109.7518 | 227.39 | 204.6372 | 239.1188 | 207.4658 | 220.2715 | 213.1752 | 217.5303 | 200.0711 | 174.3999
2220.7533 | 2110.7533 | 227.0487 | 204.5785 | 239.072 | 207.3694 | 220.2742 | 213.1941 | 217.5453 | 200.0803 | 174.3914
2221.7547 | 2111.7547 | 226.699 | 204.5204 | 238.9526 | 207.3407 | 220.2714 | 213.2162 | 217.5559 | 200.0768 | 174.4032
2222.8263 | 2112.8263 | 226.3868 | 204.4502 | 238.8539 | 207.2483 | 220.2665 | 213.2367 | 217.5737 | 200.083 | 174.4148
2223.7476 | 2113.7476 | 226.1216 | 204.3699 | 238.7301 | 207.1888 | 220.2632 | 213.2534 | 217.5858 | 200.0611 | 174.4218
2224.749 | 2114.749 | 225.8592 | 204.3075 | 238.6193 | 207.1273 | 220.2594 | 213.266 | 217.596 | 200.0701 | 174.4141
2225.7505 | 2115.7505 | 225.5459 | 204.2524 | 238.5755 | 207.0589 | 220.2503 | 213.2866 | 217.6022 | 200.0794 | 174.4034
2226.7519 | 2116.7519 | 225.3089 | 204.1845 | 238.463 | 206.9895 | 220.256 | 213.3099 | 217.6164 | 200.0815 | 174.3902
2227.7534 | 2117.7534 | 225.0262 | 204.1245 | 238.3928 | 206.9182 | 220.2476 | 213.3136 | 217.6262 | 200.0685 | 174.3992
2228.7548 | 2118.7548 | 224.6772 | 204.0485 | 238.2846 | 206.8365 | 220.2473 | 213.3428 | 217.6326 | 200.0761 | 174.3789
2229.7462 | 2119.7462 | 224.3433 | 203.9668 | 238.1981 | 206.7439 | 220.226 | 213.3519 | 217.6417 | 200.0678 | 174.4075
2230.7477 | 2120.7477 | 224.0392 | 203.9084 | 238.0726 | 206.6664 | 220.2354 | 213.3661 | 217.6495 | 200.0571 | 174.3913
2231.7491 | 2121.7491 | 223.7396 | 203.837 | 237.9803 | 206.6186 | 220.2296 | 213.3869 | 217.6643 | 200.0641 | 174.4028
2232.7505 | 2122.7505 | 223.3849 | 203.7726 | 237.876 | 206.5459 | 220.2281 | 213.401 | 217.6666 | 200.0556 | 174.412
2233.752 | 2123.752 | 223.0328 | 203.7208 | 237.7497 | 206.4676 | 220.2182 | 213.4142 | 217.6779 | 200.0493 | 174.4117
2234.7534 | 2124.7534 | 222.7293 | 203.6446 | 237.6804 | 206.3936 | 220.2067 | 213.4202 | 217.6853 | 200.0506 | 174.4031
2235.7549 | 2125.7549 | 222.4716 | 203.5777 | 237.6175 | 206.3308 | 220.202 | 213.4408 | 217.6982 | 200.0528 | 174.397
2236.7563 | 2126.7563 | 222.2651 | 203.5116 | 237.5278 | 206.2606 | 220.2026 | 213.4535 | 217.6964 | 200.0372 | 174.3959
2237.7577 | 2127.7577 | 222.0379 | 203.4395 | 237.4208 | 206.1564 | 220.1823 | 213.4738 | 217.7058 | 200.042 | 174.3777
2238.7492 | 2128.7492 | 221.7672 | 203.3763 | 237.3137 | 206.082 | 220.1844 | 213.4868 | 217.7138 | 200.0301 | 174.3969
2239.7506 | 2129.7506 | 221.4744 | 203.3141 | 237.1993 | 206.0225 | 220.1739 | 213.5054 | 217.7143 | 200.0318 | 174.3905
2240.752 | 2130.752 | 221.1931 | 203.2173 | 237.0787 | 205.9309 | 220.1725 | 213.5227 | 217.719 | 200.0241 | 174.3869
2241.7535 | 2131.7535 | 220.9457 | 203.1466 | 237.0101 | 205.8626 | 220.1718 | 213.5341 | 217.7309 | 200.0324 | 174.3929
2242.7549 | 2132.7549 | 220.694 | 203.0785 | 236.9085 | 205.8031 | 220.164 | 213.5508 | 217.7324 | 200.0294 | 174.3646
2243.7564 | 2133.7564 | 220.5163 | 203.0213 | 236.825 | 205.7359 | 220.1389 | 213.5661 | 217.7321 | 200.0232 | 174.3727
2244.7478 | 2134.7478 | 220.3064 | 202.949 | 236.7111 | 205.6619 | 220.1392 | 213.5757 | 217.7377 | 200.0398 | 174.3501
2245.7492 | 2135.7492 | 220.0598 | 202.874 | 236.7042 | 205.5898 | 220.1284 | 213.5844 | 217.7497 | 200.0244 | 174.3412
2246.7507 | 2136.7507 | 219.8404 | 202.7995 | 236.5082 | 205.4996 | 220.1335 | 213.598 | 217.7462 | 200.0369 | 174.3596
2247.7521 | 2137.7521 | 219.6187 | 202.7016 | 236.4207 | 205.4489 | 220.1105 | 213.6123 | 217.7517 | 200.0288 | 174.3447
2248.7535 | 2138.7535 | 219.3867 | 202.6522 | 236.2958 | 205.3087 | 220.0959 | 213.6279 | 217.7533 | 200.0347 | 174.3262
2249.755 | 2139.755 | 219.1388 | 202.5636 | 236.2253 | 205.2523 | 220.0982 | 213.642 | 217.755 | 200.0295 | 174.3244
2250.7564 | 2140.7564 | 218.851 | 202.5056 | 236.1347 | 205.1922 | 220.0839 | 213.6536 | 217.7502 | 200.0383 | 174.3024
2251.7479 | 2141.7479 | 218.6161 | 202.4388 | 236.0204 | 205.1393 | 220.0774 | 213.6547 | 217.7644 | 200.038 | 174.2901
2252.7493 | 2142.7493 | 218.3802 | 202.3734 | 235.9074 | 205.07 | 220.0542 | 213.6702 | 217.7656 | 200.0333 | 174.2854
2253.7507 | 2143.7507 | 218.0728 | 202.3054 | 235.8309 | 204.9829 | 220.0524 | 213.6904 | 217.7651 | 200.0134 | 174.287
2254.7522 | 2144.7522 | 217.7905 | 202.2369 | 235.6899 | 204.9302 | 220.0365 | 213.6979 | 217.7686 | 200.0276 | 174.2717
2255.7536 | 2145.7536 | 217.4822 | 202.1676 | 235.5804 | 204.843 | 220.0289 | 213.7051 | 217.7622 | 200.0253 | 174.2665
2256.7551 | 2146.7551 | 217.202 | 202.0878 | 235.455 | 204.7886 | 220.0354 | 213.719 | 217.7659 | 200.0063 | 174.2354
2257.7565 | 2147.7565 | 216.9262 | 201.99 | 235.3574 | 204.6886 | 220.0118 | 213.7367 | 217.7551 | 199.9967 | 174.2374
2258.7479 | 2148.7479 | 216.6322 | 201.9436 | 235.2409 | 204.6125 | 219.9979 | 213.7358 | 217.7616 | 199.9849 | 174.2413
2259.7494 | 2149.7494 | 216.4096 | 201.8563 | 235.2179 | 204.5516 | 219.9869 | 213.7431 | 217.7724 | 199.9707 | 174.2307
2260.7508 | 2150.7508 | 216.1455 | 201.7815 | 235.094 | 204.4647 | 219.9891 | 213.7627 | 217.764 | 199.9524 | 174.2279
2261.7522 | 2151.7522 | 215.8461 | 201.7023 | 234.9635 | 204.389 | 219.971 | 213.7723 | 217.7538 | 199.9342 | 174.2294
2262.7537 | 2152.7537 | 215.574 | 201.6364 | 234.8902 | 204.3016 | 219.9557 | 213.7736 | 217.7625 | 199.9286 | 174.2227
2263.7551 | 2153.7551 | 215.2606 | 201.5729 | 234.77 | 204.2472 | 219.9565 | 213.7927 | 217.7505 | 199.9161 | 174.2106
2264.7566 | 2154.7566 | 214.9388 | 201.4721 | 234.7044 | 204.1414 | 219.9371 | 213.8049 | 217.7482 | 199.8896 | 174.2169
2265.748 | 2155.748 | 214.6351 | 201.3907 | 234.637 | 204.0596 | 219.9227 | 213.8081 | 217.7436 | 199.8719 | 174.2003
2266.7494 | 2156.7494 | 214.3782 | 201.3227 | 234.4804 | 203.9945 | 219.9173 | 213.8153 | 217.7471 | 199.8404 | 174.2192
2267.7509 | 2157.7509 | 214.0658 | 201.2565 | 234.3893 | 203.9192 | 219.9038 | 213.8327 | 217.7398 | 199.8405 | 174.1891
2268.7523 | 2158.7523 | 213.8002 | 201.163 | 234.278 | 203.8453 | 219.895 | 213.8423 | 217.7371 | 199.8201 | 174.1972
2269.7537 | 2159.7537 | 213.4804 | 201.0949 | 234.2101 | 203.7691 | 219.877 | 213.8417 | 217.7289 | 199.7957 | 174.2058
2270.7552 | 2160.7552 | 213.1846 | 201.0313 | 234.1636 | 203.6931 | 219.8669 | 213.8508 | 217.7342 | 199.784 | 174.2011
2271.7466 | 2161.7466 | 212.9653 | 200.9613 | 233.9884 | 203.6305 | 219.856 | 213.8668 | 217.7216 | 199.7753 | 174.184
2272.7481 | 2162.7481 | 212.7217 | 200.8888 | 233.8998 | 203.5208 | 219.8509 | 213.8807 | 217.7249 | 199.769 | 174.1821
2273.7495 | 2163.7495 | 212.4603 | 200.8179 | 233.7758 | 203.4254 | 219.8279 | 213.8779 | 217.7152 | 199.7387 | 174.1978
2274.7509 | 2164.7509 | 212.2791 | 200.742 | 233.6854 | 203.3435 | 219.8161 | 213.8884 | 217.7064 | 199.7402 | 174.1697
2275.7524 | 2165.7524 | 212.0997 | 200.678 | 233.6124 | 203.2979 | 219.8004 | 213.8991 | 217.7045 | 199.7426 | 174.1477
2276.7538 | 2166.7538 | 211.8863 | 200.5935 | 233.5353 | 203.1498 | 219.7913 | 213.9011 | 217.6965 | 199.7305 | 174.134
2277.7553 | 2167.7553 | 211.688 | 200.5245 | 233.4 | 203.1148 | 219.7755 | 213.915 | 217.6905 | 199.7225 | 174.1274
2278.7567 | 2168.7567 | 211.4154 | 200.4406 | 233.2422 | 203.0333 | 219.7482 | 213.9183 | 217.6798 | 199.7161 | 174.1317
2279.7481 | 2169.7481 | 211.1742 | 200.3608 | 233.1584 | 202.9717 | 219.7437 | 213.9281 | 217.682 | 199.7181 | 174.0894
2280.7496 | 2170.7496 | 210.9636 | 200.2937 | 233.0926 | 202.9129 | 219.7185 | 213.9316 | 217.6724 | 199.6894 | 174.1157
2281.751 | 2171.751 | 210.7407 | 200.226 | 232.9625 | 202.8486 | 219.6995 | 213.9356 | 217.6646 | 199.7037 | 174.0723
2282.7524 | 2172.7524 | 210.5103 | 200.1489 | 232.844 | 202.7891 | 219.6945 | 213.9439 | 217.6598 | 199.695 | 174.0675
2283.7539 | 2173.7539 | 210.3329 | 200.0599 | 232.6979 | 202.6708 | 219.6714 | 213.9455 | 217.6476 | 199.6885 | 174.0486
2284.7553 | 2174.7553 | 210.1404 | 199.9901 | 232.6312 | 202.571 | 219.6565 | 213.9563 | 217.6401 | 199.7003 | 174.006
2285.7568 | 2175.7568 | 209.954 | 199.9171 | 232.4806 | 202.4547 | 219.6358 | 213.961 | 217.6277 | 199.6879 | 173.9943
2286.7482 | 2176.7482 | 209.7613 | 199.8384 | 232.4682 | 202.4162 | 219.6241 | 213.9678 | 217.625 | 199.6835 | 173.9746
2287.7496 | 2177.7496 | 209.5854 | 199.778 | 232.3148 | 202.3565 | 219.5937 | 213.9634 | 217.6126 | 199.6732 | 173.9586
2288.7511 | 2178.7511 | 209.3875 | 199.6912 | 232.2295 | 202.2743 | 219.5837 | 213.9704 | 217.605 | 199.652 | 173.9679
2289.7525 | 2179.7525 | 209.1717 | 199.6161 | 232.1404 | 202.2064 | 219.5498 | 213.9804 | 217.5917 | 199.6587 | 173.9333
2290.7539 | 2180.7539 | 208.9605 | 199.5519 | 232.0847 | 202.1202 | 219.5454 | 213.9803 | 217.5849 | 199.6524 | 173.8967
2291.7554 | 2181.7554 | 208.7546 | 199.4566 | 231.9376 | 202.0409 | 219.5325 | 213.983 | 217.5715 | 199.6313 | 173.9012
2292.7568 | 2182.7568 | 208.55 | 199.3797 | 231.8107 | 201.9685 | 219.5024 | 213.9868 | 217.5621 | 199.6365 | 173.8535
2293.7482 | 2183.7482 | 208.3063 | 199.3056 | 231.7033 | 201.8909 | 219.4921 | 213.9905 | 217.5446 | 199.6276 | 173.8405
2294.7497 | 2184.7497 | 208.0088 | 199.2387 | 231.5892 | 201.8292 | 219.4689 | 213.9882 | 217.5397 | 199.616 | 173.8186
2295.7511 | 2185.7511 | 207.7712 | 199.1473 | 231.5012 | 201.7411 | 219.4474 | 213.9946 | 217.5228 | 199.5806 | 173.8283
2296.7526 | 2186.7526 | 207.5042 | 199.0861 | 231.4034 | 201.6471 | 219.4371 | 214.0016 | 217.5196 | 199.5817 | 173.7991
2297.754 | 2187.754 | 207.2017 | 199.0009 | 231.2419 | 201.5605 | 219.4048 | 213.9998 | 217.5005 | 199.575 | 173.7714
2298.7554 | 2188.7554 | 206.9518 | 198.916 | 231.1788 | 201.4882 | 219.3908 | 214.0017 | 217.4865 | 199.5516 | 173.7631
2299.7569 | 2189.7569 | 206.6746 | 198.8206 | 231.1113 | 201.4045 | 219.3739 | 214.0074 | 217.4731 | 199.5482 | 173.721
2300.7483 | 2190.7483 | 206.3556 | 198.7541 | 230.916 | 201.3372 | 219.3494 | 214.0069 | 217.4639 | 199.517 | 173.721
2301.7498 | 2191.7498 | 206.0519 | 198.6891 | 230.8509 | 201.252 | 219.3348 | 214.0037 | 217.4424 | 199.5145 | 173.6987
2302.7512 | 2192.7512 | 205.7666 | 198.5963 | 230.7801 | 201.1744 | 219.3267 | 214.0122 | 217.4292 | 199.5044 | 173.6774
2303.7526 | 2193.7526 | 205.5336 | 198.5333 | 230.6895 | 201.0986 | 219.302 | 214.0169 | 217.4171 | 199.4948 | 173.6574
2304.7541 | 2194.7541 | 205.2782 | 198.4683 | 230.5924 | 201.0071 | 219.2843 | 214.0075 | 217.4039 | 199.4749 | 173.6623
2305.7555 | 2195.7555 | 205.0007 | 198.3956 | 230.5367 | 200.9345 | 219.264 | 214.0135 | 217.3805 | 199.465 | 173.617
2306.757 | 2196.757 | 204.6871 | 198.3 | 230.4075 | 200.8777 | 219.2411 | 214.0187 | 217.3704 | 199.4437 | 173.59
2307.7484 | 2197.7484 | 204.3981 | 198.2043 | 230.2552 | 200.7958 | 219.2119 | 214.0032 | 217.3583 | 199.4255 | 173.5917
2308.7498 | 2198.7498 | 204.1278 | 198.14 | 230.1378 | 200.7147 | 219.1845 | 214.0162 | 217.3409 | 199.419 | 173.5262
2309.7513 | 2199.7513 | 203.8615 | 198.083 | 230.0429 | 200.6306 | 219.1828 | 214.0204 | 217.3282 | 199.397 | 173.5212
2310.7527 | 2200.7527 | 203.6092 | 197.9899 | 229.952 | 200.529 | 219.1619 | 214.0244 | 217.3087 | 199.3479 | 173.5374
2311.7541 | 2201.7541 | 203.326 | 197.8771 | 229.8204 | 200.4875 | 219.1362 | 214.0201 | 217.2908 | 199.3459 | 173.5175
2312.7456 | 2202.7456 | 203.0514 | 197.7673 | 229.7681 | 200.3882 | 219.1247 | 214.0186 | 217.2739 | 199.3299 | 173.4683
2313.747 | 2203.747 | 202.791 | 197.7288 | 229.6466 | 200.281 | 219.1004 | 214.0185 | 217.251 | 199.2957 | 173.4859
2314.7484 | 2204.7484 | 202.5417 | 197.6355 | 229.5394 | 200.1958 | 219.0747 | 214.0123 | 217.2386 | 199.2814 | 173.461
2315.7499 | 2205.7499 | 202.285 | 197.579 | 229.4155 | 200.12 | 219.0648 | 214.0069 | 217.2154 | 199.2425 | 173.4525
2316.7513 | 2206.7513 | 202.0335 | 197.5056 | 229.3251 | 200.0595 | 219.0418 | 214.0142 | 217.2007 | 199.2201 | 173.4544
2317.7528 | 2207.7528 | 201.7997 | 197.4294 | 229.2465 | 199.9566 | 219.0042 | 214.0085 | 217.1866 | 199.1781 | 173.4383
2318.7542 | 2208.7542 | 201.5741 | 197.3558 | 229.1091 | 199.8715 | 218.9962 | 214.0042 | 217.1643 | 199.1546 | 173.4258
2319.7556 | 2209.7556 | 201.3429 | 197.2737 | 228.9725 | 199.8152 | 218.9755 | 214.0085 | 217.14 | 199.1321 | 173.4159
2320.7571 | 2210.7571 | 201.1356 | 197.1903 | 228.8926 | 199.7185 | 218.9559 | 214.0038 | 217.1211 | 199.0998 | 173.4096
2321.7485 | 2211.7485 | 200.8683 | 197.0967 | 228.7685 | 199.6508 | 218.9377 | 214.003 | 217.1044 | 199.0777 | 173.3883
2322.75 | 2212.75 | 200.6087 | 197.0041 | 228.7117 | 199.5525 | 218.9191 | 213.9989 | 217.0825 | 199.0522 | 173.3589
2323.7514 | 2213.7514 | 200.364 | 196.9556 | 228.6076 | 199.4787 | 218.8943 | 214.0026 | 217.0676 | 199.017 | 173.3628
2324.7528 | 2214.7528 | 200.1188 | 196.8703 | 228.5129 | 199.3999 | 218.8791 | 213.9953 | 217.0435 | 198.9952 | 173.3522
2325.7543 | 2215.7543 | 199.8761 | 196.769 | 228.3861 | 199.3408 | 218.8568 | 213.9959 | 217.0251 | 198.9717 | 173.3416
2326.7557 | 2216.7557 | 199.7046 | 196.6917 | 228.2952 | 199.2537 | 218.8333 | 213.9932 | 217.0001 | 198.9373 | 173.3308
2327.7572 | 2217.7572 | 199.4618 | 196.6034 | 228.2052 | 199.112 | 218.8138 | 213.9913 | 216.9842 | 198.9051 | 173.3286
2328.7486 | 2218.7486 | 199.225 | 196.5299 | 228.0681 | 199.0239 | 218.7978 | 213.9951 | 216.9623 | 198.8736 | 173.3202
2329.75 | 2219.75 | 199.0661 | 196.4452 | 227.9682 | 198.9469 | 218.7625 | 213.9882 | 216.9392 | 198.849 | 173.3093
2330.7515 | 2220.7515 | 198.8532 | 196.389 | 227.8675 | 198.9055 | 218.7486 | 213.9771 | 216.9187 | 198.8289 | 173.2786
2331.7529 | 2221.7529 | 198.675 | 196.3197 | 227.7509 | 198.8364 | 218.7225 | 213.9717 | 216.8974 | 198.7944 | 173.2911
2332.7543 | 2222.7543 | 198.4568 | 196.2387 | 227.635 | 198.749 | 218.7125 | 213.9723 | 216.8714 | 198.7823 | 173.2526
2333.7558 | 2223.7558 | 198.1966 | 196.1477 | 227.5785 | 198.6603 | 218.6776 | 213.9781 | 216.8482 | 198.7533 | 173.2462
2334.7572 | 2224.7572 | 197.9838 | 196.0714 | 227.4064 | 198.5802 | 218.6623 | 213.9701 | 216.8283 | 198.7169 | 173.2244
2335.7486 | 2225.7486 | 197.8182 | 195.9865 | 227.3321 | 198.4908 | 218.6324 | 213.9647 | 216.7993 | 198.6931 | 173.212
2336.7501 | 2226.7501 | 197.6291 | 195.8966 | 227.2047 | 198.3913 | 218.6162 | 213.9499 | 216.7815 | 198.6662 | 173.1924
2337.7515 | 2227.7515 | 197.4431 | 195.8025 | 227.1473 | 198.3199 | 218.5791 | 213.9493 | 216.7555 | 198.6358 | 173.1956
2338.753 | 2228.753 | 197.1806 | 195.748 | 227.0208 | 198.2528 | 218.5647 | 213.9516 | 216.7369 | 198.6054 | 173.1853
2339.7544 | 2229.7544 | 196.9488 | 195.6484 | 226.984 | 198.1346 | 218.544 | 213.9429 | 216.7068 | 198.5855 | 173.1373
2340.7558 | 2230.7558 | 196.7714 | 195.5819 | 226.8057 | 198.0795 | 218.5177 | 213.9411 | 216.6762 | 198.5467 | 173.1638
2341.7573 | 2231.7573 | 196.6041 | 195.5142 | 226.7073 | 197.9842 | 218.4848 | 213.9343 | 216.6576 | 198.5351 | 173.1403
2342.7487 | 2232.7487 | 196.4035 | 195.4335 | 226.6198 | 197.9084 | 218.4635 | 213.9325 | 216.6311 | 198.5197 | 173.1091
2343.7501 | 2233.7501 | 196.1799 | 195.3581 | 226.5063 | 197.84 | 218.4457 | 213.9194 | 216.604 | 198.4856 | 173.0977
2344.7516 | 2234.7516 | 196.041 | 195.275 | 226.3972 | 197.7463 | 218.4278 | 213.9124 | 216.5734 | 198.4633 | 173.0671
2345.753 | 2235.753 | 195.8761 | 195.1879 | 226.2537 | 197.6705 | 218.4033 | 213.9124 | 216.5475 | 198.444 | 173.0284
2346.7545 | 2236.7545 | 195.6332 | 195.12 | 226.0669 | 197.5729 | 218.3709 | 213.8949 | 216.5307 | 198.4038 | 173.0578
2347.7559 | 2237.7559 | 195.4183 | 195.0492 | 226.0343 | 197.4655 | 218.3425 | 213.8969 | 216.5007 | 198.3836 | 173.0258
2348.7573 | 2238.7573 | 195.2388 | 194.9612 | 225.9223 | 197.4101 | 218.3254 | 213.8888 | 216.4796 | 198.3681 | 173.025
2349.7488 | 2239.7488 | 195.001 | 194.8797 | 225.8511 | 197.347 | 218.3046 | 213.8813 | 216.454 | 198.3282 | 172.9965
2350.7502 | 2240.7502 | 194.749 | 194.8025 | 225.7836 | 197.2466 | 218.2672 | 213.874 | 216.4229 | 198.3063 | 172.9639
2351.7517 | 2241.7517 | 194.5483 | 194.7096 | 225.6201 | 197.1726 | 218.2503 | 213.8678 | 216.3873 | 198.3027 | 172.9424
2352.7531 | 2242.7531 | 194.3402 | 194.6383 | 225.5369 | 197.0874 | 218.2201 | 213.8604 | 216.3658 | 198.2883 | 172.9059
2353.7545 | 2243.7545 | 194.0972 | 194.5617 | 225.4681 | 196.9928 | 218.186 | 213.8485 | 216.3414 | 198.2605 | 172.8848
2354.746 | 2244.746 | 193.846 | 194.4786 | 225.3682 | 196.9194 | 218.1557 | 213.836 | 216.3128 | 198.2344 | 172.8498
2355.7474 | 2245.7474 | 193.5639 | 194.3921 | 225.2131 | 196.8467 | 218.1337 | 213.8286 | 216.2854 | 198.2095 | 172.854
2356.7488 | 2246.7488 | 193.322 | 194.3244 | 225.1075 | 196.7552 | 218.097 | 213.8239 | 216.2555 | 198.1895 | 172.8118
2357.7503 | 2247.7503 | 193.1476 | 194.2468 | 225.0018 | 196.6864 | 218.0663 | 213.8165 | 216.2286 | 198.1563 | 172.8142
2358.7517 | 2248.7517 | 192.9607 | 194.1673 | 224.9057 | 196.5832 | 218.0401 | 213.8071 | 216.1964 | 198.1207 | 172.7948
2359.7532 | 2249.7532 | 192.7848 | 194.0832 | 224.792 | 196.5036 | 218.0146 | 213.7946 | 216.1668 | 198.1103 | 172.7491
2360.7546 | 2250.7546 | 192.568 | 194.0128 | 224.6807 | 196.4032 | 217.9918 | 213.7815 | 216.1379 | 198.0769 | 172.7372
2361.756 | 2251.756 | 192.3758 | 193.9199 | 224.5783 | 196.338 | 217.9628 | 213.7727 | 216.0993 | 198.0504 | 172.7031
2362.7575 | 2252.7575 | 192.1153 | 193.8461 | 224.4677 | 196.2613 | 217.9335 | 213.7673 | 216.08 | 198.0155 | 172.6896
2363.7489 | 2253.7489 | 191.9344 | 193.7714 | 224.4157 | 196.1868 | 217.9063 | 213.7487 | 216.0495 | 197.9954 | 172.6445
2364.7503 | 2254.7503 | 191.7153 | 193.6989 | 224.307 | 196.0823 | 217.8829 | 213.7357 | 216.0189 | 197.9702 | 172.6207
2365.7818 | 2255.7818 | 191.5235 | 193.5961 | 224.1992 | 196.0103 | 217.8559 | 213.7336 | 215.9817 | 197.9342 | 172.6296
2366.7532 | 2256.7532 | 191.3759 | 193.5356 | 224.023 | 195.9348 | 217.8185 | 213.7193 | 215.9561 | 197.8984 | 172.5968
2367.7547 | 2257.7547 | 191.1999 | 193.4474 | 223.9533 | 195.8557 | 217.7976 | 213.7038 | 215.9253 | 197.8863 | 172.573
2368.7561 | 2258.7561 | 191.0087 | 193.3527 | 223.8612 | 195.7634 | 217.7616 | 213.6953 | 215.8916 | 197.8479 | 172.5459
2369.7575 | 2259.7575 | 190.7971 | 193.2761 | 223.6099 | 195.6877 | 217.7371 | 213.6825 | 215.8626 | 197.8241 | 172.5189
2370.749 | 2260.749 | 190.6569 | 193.1991 | 223.5846 | 195.5794 | 217.7082 | 213.6723 | 215.8296 | 197.7881 | 172.5278
2371.7504 | 2261.7504 | 190.5024 | 193.1273 | 223.4947 | 195.4938 | 217.6759 | 213.6576 | 215.8018 | 197.7593 | 172.4673
2372.7518 | 2262.7518 | 190.3148 | 193.0423 | 223.4051 | 195.4085 | 217.6393 | 213.653 | 215.7683 | 197.7268 | 172.465
2373.7533 | 2263.7533 | 190.1173 | 192.9492 | 223.2969 | 195.3118 | 217.6162 | 213.6318 | 215.7328 | 197.7038 | 172.4416
2374.7547 | 2264.7547 | 189.8943 | 192.8751 | 223.1481 | 195.2494 | 217.5791 | 213.6234 | 215.7021 | 197.6914 | 172.385
2375.7562 | 2265.7562 | 189.6779 | 192.7962 | 223.0375 | 195.1792 | 217.5628 | 213.6164 | 215.6684 | 197.6476 | 172.3761
2376.7476 | 2266.7476 | 189.4521 | 192.7037 | 222.9745 | 195.0878 | 217.5296 | 213.5967 | 215.6371 | 197.6333 | 172.3409
2377.749 | 2267.749 | 189.1972 | 192.6398 | 222.8636 | 195.0134 | 217.5019 | 213.5797 | 215.6065 | 197.5926 | 172.3397
2378.7505 | 2268.7505 | 188.9766 | 192.5725 | 222.7376 | 194.9477 | 217.4671 | 213.5675 | 215.568 | 197.5711 | 172.2898
2379.7519 | 2269.7519 | 188.7951 | 192.495 | 222.6727 | 194.8452 | 217.4268 | 213.5604 | 215.5407 | 197.5285 | 172.2911
2380.7534 | 2270.7534 | 188.6739 | 192.3745 | 222.5436 | 194.7542 | 217.4059 | 213.5399 | 215.5048 | 197.5146 | 172.241
2381.7548 | 2271.7548 | 188.4965 | 192.3094 | 222.4102 | 194.6901 | 217.3728 | 213.5267 | 215.4728 | 197.4902 | 172.2132
2382.7562 | 2272.7562 | 188.3046 | 192.228 | 222.3221 | 194.5915 | 217.3402 | 213.5135 | 215.4409 | 197.4441 | 172.2034
2383.7577 | 2273.7577 | 188.1173 | 192.1569 | 222.1932 | 194.5147 | 217.3115 | 213.4994 | 215.403 | 197.4282 | 172.1648
2384.7491 | 2274.7491 | 187.8468 | 192.0764 | 222.0453 | 194.4158 | 217.2793 | 213.4802 | 215.3703 | 197.3906 | 172.1456
2385.7505 | 2275.7505 | 187.6112 | 191.9768 | 221.976 | 194.3506 | 217.2439 | 213.4749 | 215.3386 | 197.3598 | 172.1162
2386.752 | 2276.752 | 187.3873 | 191.9002 | 221.8601 | 194.2775 | 217.2179 | 213.4558 | 215.3017 | 197.3318 | 172.083
2387.7534 | 2277.7534 | 187.1807 | 191.8028 | 221.7795 | 194.1711 | 217.1802 | 213.4399 | 215.2685 | 197.3132 | 172.0452
2388.7549 | 2278.7549 | 186.9629 | 191.7334 | 221.6165 | 194.0761 | 217.1488 | 213.4259 | 215.2319 | 197.2727 | 172.022
2389.7563 | 2279.7563 | 186.8188 | 191.6454 | 221.498 | 194.0162 | 217.1187 | 213.4074 | 215.2027 | 197.2339 | 172.0068
2390.7577 | 2280.7577 | 186.5852 | 191.5732 | 221.3999 | 193.9166 | 217.0863 | 213.3956 | 215.1643 | 197.1863 | 171.9779
2391.7492 | 2281.7492 | 186.3471 | 191.4866 | 221.2442 | 193.8204 | 217.0554 | 213.3761 | 215.1263 | 197.1694 | 171.9698
2392.7506 | 2282.7506 | 186.0587 | 191.3975 | 221.1355 | 193.7576 | 217.0185 | 213.3547 | 215.0929 | 197.124 | 171.9425
2393.752 | 2283.752 | 185.7985 | 191.2999 | 221.0805 | 193.6681 | 216.9948 | 213.3411 | 215.0564 | 197.0849 | 171.9208
2394.7535 | 2284.7535 | 185.623 | 191.2151 | 220.965 | 193.5949 | 216.9702 | 213.3246 | 215.0204 | 197.0445 | 171.899
2395.7549 | 2285.7549 | 185.4322 | 191.0923 | 220.8881 | 193.4786 | 216.9298 | 213.306 | 214.9789 | 197.0158 | 171.8751
2396.7564 | 2286.7564 | 185.2234 | 191.0176 | 220.7532 | 193.4232 | 216.9059 | 213.2897 | 214.9413 | 196.978 | 171.8509
2397.7478 | 2287.7478 | 185.0178 | 190.9848 | 220.6416 | 193.3269 | 216.8691 | 213.2692 | 214.912 | 196.9434 | 171.8197
2398.7492 | 2288.7492 | 184.7862 | 190.8897 | 220.5409 | 193.2474 | 216.8421 | 213.2606 | 214.8696 | 196.9009 | 171.8026
2399.7507 | 2289.7507 | 184.5419 | 190.8109 | 220.4637 | 193.1577 | 216.804 | 213.2312 | 214.8388 | 196.8569 | 171.7887
2400.7521 | 2290.7521 | 184.2661 | 190.7325 | 220.3157 | 193.0736 | 216.7738 | 213.2202 | 214.8012 | 196.8167 | 171.7619
2401.7536 | 2291.7536 | 184.0193 | 190.6536 | 220.2121 | 192.9916 | 216.7385 | 213.2027 | 214.7559 | 196.7844 | 171.7301
2402.755 | 2292.755 | 183.7988 | 190.5776 | 220.0458 | 192.9029 | 216.7098 | 213.1767 | 214.722 | 196.7385 | 171.7221
2403.7965 | 2293.7965 | 183.5772 | 190.4936 | 220.0114 | 192.8351 | 216.6751 | 213.1662 | 214.6873 | 196.7146 | 171.6858
2404.7479 | 2294.7479 | 183.3793 | 190.4108 | 219.8982 | 192.748 | 216.6298 | 213.1484 | 214.6493 | 196.6607 | 171.692
2405.7493 | 2295.7493 | 183.2127 | 190.3326 | 219.7813 | 192.6498 | 216.6066 | 213.128 | 214.6185 | 196.6189 | 171.6702
2406.7507 | 2296.7507 | 183.0387 | 190.2646 | 219.6448 | 192.5742 | 216.5729 | 213.1076 | 214.571 | 196.5826 | 171.6526
2407.7522 | 2297.7522 | 182.8788 | 190.175 | 219.5272 | 192.4905 | 216.5448 | 213.0894 | 214.5369 | 196.551 | 171.606
2408.7536 | 2298.7536 | 182.7031 | 190.082 | 219.4734 | 192.4214 | 216.5011 | 213.0716 | 214.4972 | 196.5103 | 171.5872
2409.7551 | 2299.7551 | 182.4861 | 189.9999 | 219.358 | 192.3223 | 216.466 | 213.0512 | 214.4554 | 196.4736 | 171.5651
2410.7565 | 2300.7565 | 182.2699 | 189.9118 | 219.2506 | 192.2477 | 216.4386 | 213.0319 | 214.4185 | 196.4349 | 171.5362
2411.7579 | 2301.7579 | 182.0381 | 189.8346 | 219.1444 | 192.1655 | 216.4052 | 213.0123 | 214.3834 | 196.3892 | 171.5389
2412.7494 | 2302.7494 | 181.8434 | 189.7267 | 219.0129 | 192.0889 | 216.3692 | 212.9904 | 214.3431 | 196.354 | 171.5082
2413.7508 | 2303.7508 | 181.7008 | 189.6588 | 218.8957 | 191.9921 | 216.3362 | 212.9696 | 214.2937 | 196.3035 | 171.5045
2414.7522 | 2304.7522 | 181.5786 | 189.5822 | 218.8254 | 191.8863 | 216.3048 | 212.9498 | 214.2585 | 196.2646 | 171.4768
2415.7537 | 2305.7537 | 181.3922 | 189.5171 | 218.7055 | 191.7957 | 216.2576 | 212.9349 | 214.225 | 196.2432 | 171.4332
2416.7551 | 2306.7551 | 181.2021 | 189.4114 | 218.5996 | 191.7217 | 216.2351 | 212.9045 | 214.1825 | 196.2101 | 171.4006
2417.7566 | 2307.7566 | 181.0031 | 189.3281 | 218.4755 | 191.6525 | 216.1926 | 212.8902 | 214.1376 | 196.1593 | 171.3813
2418.748 | 2308.748 | 180.8355 | 189.2627 | 218.3332 | 191.5754 | 216.1547 | 212.873 | 214.0978 | 196.1309 | 171.3631
2419.7494 | 2309.7494 | 180.6664 | 189.1685 | 218.2504 | 191.454 | 216.1126 | 212.8472 | 214.0632 | 196.0976 | 171.317
2420.7509 | 2310.7509 | 180.5292 | 189.1032 | 218.1723 | 191.3934 | 216.0839 | 212.8326 | 214.017 | 196.0636 | 171.3092
2421.7523 | 2311.7523 | 180.3665 | 189.0263 | 218.0579 | 191.3292 | 216.0513 | 212.8 | 213.9749 | 196.0182 | 171.2756
2422.7537 | 2312.7537 | 180.2107 | 188.9272 | 217.9459 | 191.2498 | 216.0132 | 212.7782 | 213.9339 | 195.9632 | 171.2712
2423.7552 | 2313.7552 | 180.006 | 188.8547 | 217.7949 | 191.1618 | 215.9693 | 212.7643 | 213.8897 | 195.9478 | 171.2295
2424.7566 | 2314.7566 | 179.8168 | 188.7536 | 217.7373 | 191.0733 | 215.94 | 212.7437 | 213.8508 | 195.9036 | 171.1939
2425.7481 | 2315.7481 | 179.6319 | 188.6641 | 217.6442 | 190.9858 | 215.9082 | 212.7166 | 213.809 | 195.8597 | 171.1901
2426.7495 | 2316.7495 | 179.4746 | 188.5727 | 217.4733 | 190.9107 | 215.8551 | 212.6937 | 213.7659 | 195.8189 | 171.1626
2427.7509 | 2317.7509 | 179.3092 | 188.5017 | 217.3856 | 190.8364 | 215.8227 | 212.671 | 213.7287 | 195.788 | 171.1349
2428.7524 | 2318.7524 | 179.1297 | 188.4357 | 217.2688 | 190.7527 | 215.8017 | 212.6497 | 213.6868 | 195.7566 | 171.099
2429.7538 | 2319.7538 | 178.9255 | 188.3467 | 217.242 | 190.6556 | 215.7539 | 212.6314 | 213.6438 | 195.7211 | 171.0618
2430.7553 | 2320.7553 | 178.7519 | 188.2766 | 217.0948 | 190.5764 | 215.7112 | 212.6042 | 213.6005 | 195.6749 | 171.0426
2431.7567 | 2321.7567 | 178.6158 | 188.1969 | 216.975 | 190.4933 | 215.6796 | 212.5818 | 213.5518 | 195.6353 | 171.0097
2432.7481 | 2322.7481 | 178.4438 | 188.1199 | 216.8619 | 190.3992 | 215.6389 | 212.5558 | 213.5141 | 195.5916 | 171.0008
2433.7496 | 2323.7496 | 178.3077 | 188.0497 | 216.7699 | 190.3237 | 215.6109 | 212.533 | 213.4704 | 195.5475 | 170.9729
2434.751 | 2324.751 | 178.0939 | 187.9502 | 216.6611 | 190.2314 | 215.5632 | 212.5111 | 213.43 | 195.5186 | 170.957
2435.7524 | 2325.7524 | 177.8573 | 187.8386 | 216.5447 | 190.1459 | 215.5385 | 212.4857 | 213.3849 | 195.4736 | 170.9203
2436.7539 | 2326.7539 | 177.6614 | 187.7711 | 216.4317 | 190.0727 | 215.4853 | 212.457 | 213.3345 | 195.4527 | 170.8813
2437.7553 | 2327.7553 | 177.4745 | 187.6762 | 216.3018 | 189.9711 | 215.4481 | 212.4347 | 213.2942 | 195.4153 | 170.8518
2438.7568 | 2328.7568 | 177.3079 | 187.6087 | 216.2177 | 189.8869 | 215.4101 | 212.4093 | 213.2414 | 195.3786 | 170.8077
2439.7482 | 2329.7482 | 177.0505 | 187.5131 | 216.101 | 189.8097 | 215.3749 | 212.3831 | 213.2045 | 195.3334 | 170.7814
2440.7496 | 2330.7496 | 176.8282 | 187.4412 | 216.0458 | 189.7211 | 215.3278 | 212.3592 | 213.1569 | 195.3017 | 170.7478
2441.7511 | 2331.7511 | 176.6334 | 187.3681 | 215.9026 | 189.625 | 215.2887 | 212.3298 | 213.1178 | 195.2488 | 170.7326
2442.7525 | 2332.7525 | 176.4824 | 187.2871 | 215.8179 | 189.538 | 215.2487 | 212.3102 | 213.0711 | 195.217 | 170.7013
2443.7539 | 2333.7539 | 176.3775 | 187.1944 | 215.6867 | 189.4214 | 215.2154 | 212.2898 | 213.0323 | 195.1633 | 170.6922
2444.7554 | 2334.7554 | 176.2437 | 187.1166 | 215.6123 | 189.335 | 215.174 | 212.2555 | 212.9781 | 195.1485 | 170.635
2445.7668 | 2335.7668 | 176.0655 | 187.0433 | 215.5058 | 189.2295 | 215.1341 | 212.2322 | 212.9381 | 195.0872 | 170.6238
2446.7483 | 2336.7483 | 175.858 | 186.9508 | 215.3708 | 189.1791 | 215.0906 | 212.212 | 212.8877 | 195.0572 | 170.5991
2447.7597 | 2337.7597 | 175.6985 | 186.857 | 215.2627 | 189.1133 | 215.0548 | 212.1871 | 212.8452 | 195.0205 | 170.5419
2448.7511 | 2338.7511 | 175.5568 | 186.7733 | 215.1938 | 189.0343 | 215.028 | 212.1555 | 212.7998 | 194.9516 | 170.5369
2449.7526 | 2339.7526 | 175.3492 | 186.6984 | 215.0494 | 188.9441 | 214.97 | 212.1306 | 212.7464 | 194.9204 | 170.5053
2450.754 | 2340.754 | 175.1054 | 186.6155 | 214.9533 | 188.8694 | 214.9351 | 212.1077 | 212.704 | 194.881 | 170.4833
2451.7555 | 2341.7555 | 174.853 | 186.5292 | 214.8659 | 188.7916 | 214.8935 | 212.0735 | 212.6643 | 194.8374 | 170.4591
2452.7569 | 2342.7569 | 174.6318 | 186.4618 | 214.7309 | 188.6917 | 214.8525 | 212.0484 | 212.6109 | 194.7951 | 170.4339
2453.7583 | 2343.7583 | 174.4118 | 186.3806 | 214.6275 | 188.6127 | 214.8224 | 212.023 | 212.5612 | 194.7608 | 170.3872
2454.7498 | 2344.7498 | 174.1476 | 186.2803 | 214.5207 | 188.5189 | 214.773 | 211.9941 | 212.5204 | 194.7096 | 170.3666
2455.7512 | 2345.7512 | 173.9057 | 186.1975 | 214.3652 | 188.4705 | 214.7431 | 211.971 | 212.4703 | 194.671 | 170.3349
2456.7526 | 2346.7526 | 173.6694 | 186.1132 | 214.296 | 188.365 | 214.6915 | 211.943 | 212.4241 | 194.6392 | 170.2997
2457.7541 | 2347.7541 | 173.506 | 186.0446 | 214.1463 | 188.2794 | 214.6541 | 211.9178 | 212.3838 | 194.5757 | 170.2941

## C3-4
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 152.5873 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38905.539 | 1 | 0 | 38905.539 | 1 | 0 | -94.5 | 15.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5392 | 1 | 0 | 38905.5392 | 1 | 0 | -78 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5394 | 1 | 0 | 38905.5394 | 1 | 0 | -61.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5395 | 1 | 0 | 38905.5396 | 1 | 0 | -44.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5397 | 1 | 0 | 38905.5398 | 1 | 0 | -27.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5399 | 1 | 0 | 38905.54 | 1 | 0 | -11 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5401 | 1 | 0 | 38905.5402 | 1 | 0 | 6 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5403 | 1 | 0 | 38905.5403 | 1 | 0 | 22.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5405 | 1 | 0 | 38905.5405 | 1 | 0 | 39.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5407 | 1 | 0 | 38905.5407 | 1 | 0 | 56.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5409 | 1 | 0 | 38905.5409 | 1 | 0 | 73 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5411 | 1 | 0 | 38905.5411 | 1 | 0 | 90 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5413 | 1 | 0 | 38905.5413 | 1 | 0 | 106.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5415 | 1 | 0 | 38905.5415 | 1 | 0 | 123.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5417 | 1 | 0 | 38905.5417 | 1 | 0 | 140 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5419 | 1 | 0 | 38905.5419 | 1 | 0 | 157 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5421 | 1 | 0 | 38905.5421 | 1 | 0 | 173.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5423 | 1 | 0 | 38905.5423 | 1 | 0 | 190.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5425 | 1 | 0 | 38905.5425 | 1 | 0 | 207.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5427 | 1 | 0 | 38905.5427 | 1 | 0 | 224 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5428 | 1 | 0 | 38905.5429 | 1 | 0 | 241 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.543 | 1 | 0 | 38905.5431 | 2 | 0 | 257.5 | 367.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249838 | 124869 | 249837.9994
38905.5432 | 1 | 0 | 38905.5433 | 1 | 0 | 274.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5434 | 1 | 0 | 38905.5434 | 1 | 0 | 291.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5436 | 1 | 0 | 38905.5436 | 1 | 0 | 308.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5438 | 1 | 0 | 38905.5438 | 1 | 0 | 325 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.544 | 1 | 0 | 38905.544 | 1 | 0 | 341.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5442 | 1 | 0 | 38905.5442 | 1 | 0 | 358.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5444 | 1 | 0 | 38905.5444 | 1 | 0 | 375.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5446 | 1 | 0 | 38905.5446 | 1 | 0 | 392 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5448 | 1 | 0 | 38905.5448 | 1 | 0 | 409 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.545 | 1 | 0 | 38905.545 | 1 | 0 | 425.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5452 | 1 | 0 | 38905.5452 | 1 | 0 | 442.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5454 | 1 | 0 | 38905.5454 | 1 | 0 | 459.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5456 | 1 | 0 | 38905.5456 | 1 | 0 | 476.5 | 586.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5458 | 1 | 0 | 38905.5458 | 1 | 0 | 493 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.546 | 1 | 0 | 38905.546 | 1 | 0 | 509.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5462 | 1 | 0 | 38905.5462 | 1 | 0 | 526.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5464 | 1 | 0 | 38905.5464 | 1 | 0 | 543.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5465 | 1 | 0 | 38905.5466 | 1 | 0 | 560 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5467 | 1 | 0 | 38905.5468 | 1 | 0 | 577 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5469 | 1 | 0 | 38905.5469 | 1 | 0 | 593.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5471 | 1 | 0 | 38905.5471 | 1 | 0 | 610.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5473 | 1 | 0 | 38905.5473 | 1 | 0 | 627.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5475 | 1 | 0 | 38905.5475 | 1 | 0 | 644 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5477 | 1 | 0 | 38905.5477 | 1 | 0 | 661 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5479 | 1 | 0 | 38905.5479 | 1 | 0 | 677.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5481 | 1 | 0 | 38905.5481 | 1 | 0 | 694.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5483 | 1 | 0 | 38905.5483 | 1 | 0 | 711.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5485 | 1 | 0 | 38905.5485 | 1 | 0 | 728 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5487 | 1 | 0 | 38905.5487 | 1 | 0 | 745 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5489 | 1 | 0 | 38905.5489 | 1 | 0 | 761.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5491 | 1 | 0 | 38905.5491 | 1 | 0 | 778.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5493 | 2 | 0 | 38905.5493 | 1 | 0 | 795.5 | 905.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124869 | 249838 | 124868.9988
38905.5495 | 1 | 0 | 38905.5495 | 1 | 0 | 812 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5497 | 1 | 0 | 38905.5497 | 1 | 0 | 829 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5498 | 1 | 0 | 38905.5499 | 1 | 0 | 845.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.55 | 1 | 0 | 38905.5501 | 1 | 0 | 862.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5502 | 1 | 0 | 38905.5503 | 1 | 0 | 879.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5504 | 1 | 0 | 38905.5505 | 1 | 0 | 896 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5506 | 1 | 0 | 38905.5506 | 1 | 0 | 913 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5508 | 1 | 0 | 38905.5508 | 1 | 0 | 929.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.551 | 1 | 0 | 38905.551 | 1 | 0 | 946.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5512 | 1 | 0 | 38905.5512 | 1 | 0 | 963.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5514 | 1 | 0 | 38905.5514 | 1 | 0 | 980 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5516 | 1 | 0 | 38905.5516 | 1 | 0 | 997 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5518 | 1 | 0 | 38905.5518 | 1 | 0 | 1013.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.552 | 1 | 0 | 38905.552 | 1 | 0 | 1030.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5522 | 1 | 0 | 38905.5522 | 1 | 0 | 1047.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5524 | 1 | 0 | 38905.5524 | 1 | 0 | 1064 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5526 | 1 | 1 | 38905.5526 | 1 | 0 | 1081 | 1191 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 624190262.44 | 249838 | 249638.08
38905.5528 | 1 | 0 | 38905.5528 | 1 | 0 | 1097.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.553 | 1 | 0 | 38905.553 | 1 | 0 | 1114.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5532 | 1 | 0 | 38905.5532 | 1 | 0 | 1131.5 | 1241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5533 | 1 | 0 | 38905.5534 | 1 | 0 | 1148 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5535 | 1 | 0 | 38905.5536 | 1 | 0 | 1165 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5537 | 1 | 0 | 38905.5537 | 1 | 0 | 1181.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5539 | 1 | 0 | 38905.5539 | 1 | 0 | 1198.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5541 | 1 | 0 | 38905.5541 | 1 | 0 | 1215.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5543 | 1 | 0 | 38905.5543 | 1 | 0 | 1232 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249838 | 249838 | 249837.9994
38905.5545 | 4 | 0 | 38905.5545 | 1514 | 0 | 1249 | 1359 | 0.2442 | 0 | 92.4298 | 0 | 0.002442 | 0 | 0.9243 | 0 | 0.002442 | 0.9243 | 62384.5 | 65.0845 | 62384.4976
38905.5547 | 8 | 0 | 38905.5547 | 1383 | 0 | 1265.5 | 1375.5 | 0.4884 | 0 | 84.4322 | 0 | 0.004884 | 0 | 0.84432 | 0 | 0.004884 | 0.84432 | 31142.25 | 80.7216 | 31142.2451
38905.5549 | 9 | 0 | 38905.5549 | 1364 | 0 | 1282.5 | 1392.5 | 0.54945 | 0 | 83.2723 | 0 | 0.0054945 | 0 | 0.83272 | 0 | 0.0054945 | 0.83272 | 27670.8889 | 83.239 | 27670.8834
38905.5551 | 9 | 1 | 38905.5551 | 1889 | 0 | 1299.5 | 1409.5 | 0.54945 | 0.06105 | 115.3236 | 0 | 0.0054945 | 0.0006105 | 1.1532 | 0 | 0.004884 | 1.1532 | 50770.1348 | 32.3123 | 60793.7874
38905.5553 | 9 | 0 | 38905.5553 | 1601 | 0 | 1316 | 1426 | 0.54945 | 0 | 97.7411 | 0 | 0.0054945 | 0 | 0.97741 | 0 | 0.0054945 | 0.97741 | 27670.8889 | 56.1137 | 27670.8834
38905.5555 | 9 | 0 | 38905.5555 | 1867 | 0 | 1333 | 1443 | 0.54945 | 0 | 113.9805 | 0 | 0.0054945 | 0 | 1.1398 | 0 | 0.0054945 | 1.1398 | 27670.8889 | 33.8715 | 27670.8834
38905.5557 | 9 | 0 | 38905.5557 | 2019 | 0 | 1349.5 | 1459.5 | 0.54945 | 0 | 123.2601 | 0 | 0.0054945 | 0 | 1.2326 | 0 | 0.0054945 | 1.2326 | 27670.8889 | 23.793 | 27670.8834
38905.5559 | 9 | 0 | 38905.5559 | 1939 | 0 | 1366.5 | 1476.5 | 0.54945 | 0 | 118.3761 | 0 | 0.0054945 | 0 | 1.1838 | 0 | 0.0054945 | 1.1838 | 27670.8889 | 28.9005 | 27670.8834
38905.5561 | 9 | 0 | 38905.5561 | 1908 | 0 | 1383 | 1493 | 0.54945 | 0 | 116.4835 | 0 | 0.0054945 | 0 | 1.1648 | 0 | 0.0054945 | 1.1648 | 27670.8889 | 30.9948 | 27670.8834
38905.5563 | 9 | 0 | 38905.5563 | 2043 | 0 | 1400 | 1510 | 0.54945 | 0 | 124.7253 | 0 | 0.0054945 | 0 | 1.2473 | 0 | 0.0054945 | 1.2473 | 27670.8889 | 22.3387 | 27670.8834
38905.5565 | 9 | 0 | 38905.5565 | 2403 | 0 | 1417 | 1527 | 0.54945 | 0 | 146.7033 | 0 | 0.0054945 | 0 | 1.467 | 0 | 0.0054945 | 1.467 | 27670.8889 | 4.0108 | 27670.8834
38905.5567 | 9 | 0 | 38905.5567 | 2228 | 0 | 1433.5 | 1543.5 | 0.54945 | 0 | 136.0195 | 0 | 0.0054945 | 0 | 1.3602 | 0 | 0.0054945 | 1.3602 | 27670.8889 | 12.1804 | 27670.8834
38905.5569 | 9 | 0 | 38905.5569 | 2130 | 0 | 1450.5 | 1560.5 | 0.54945 | 0 | 130.0366 | 0 | 0.0054945 | 0 | 1.3004 | 0 | 0.0054945 | 1.3004 | 27670.8889 | 17.3418 | 27670.8834
38905.557 | 9 | 0 | 38905.5571 | 1837 | 0 | 1467.5 | 1577.5 | 0.54945 | 0 | 112.149 | 0 | 0.0054945 | 0 | 1.1215 | 0 | 0.0054945 | 1.1215 | 27670.8889 | 36.0577 | 27670.8834
38905.5572 | 8 | 0 | 38905.5573 | 1846 | 0 | 1484 | 1594 | 0.4884 | 0 | 112.6984 | 0 | 0.004884 | 0 | 1.127 | 0 | 0.004884 | 1.127 | 31142.25 | 35.3944 | 31142.2451
38905.5574 | 10 | 0 | 38905.5575 | 2322 | 0 | 1501 | 1611 | 0.6105 | 0 | 141.7582 | 0 | 0.006105 | 0 | 1.4176 | 0 | 0.006105 | 1.4176 | 24893.8 | 7.6391 | 24893.7939
38905.5576 | 9 | 0 | 38905.5576 | 2326 | 0 | 1517.5 | 1627.5 | 0.54945 | 0 | 142.0024 | 0 | 0.0054945 | 0 | 1.42 | 0 | 0.0054945 | 1.42 | 27670.8889 | 7.454 | 27670.8834
38905.5578 | 9 | 0 | 38905.5578 | 1994 | 0 | 1534.5 | 1644.5 | 0.54945 | 0 | 121.7338 | 0 | 0.0054945 | 0 | 1.2173 | 0 | 0.0054945 | 1.2173 | 27670.8889 | 25.345 | 27670.8834
38905.558 | 9 | 0 | 38905.558 | 2261 | 0 | 1551 | 1661 | 0.54945 | 0 | 138.0342 | 0 | 0.0054945 | 0 | 1.3803 | 0 | 0.0054945 | 1.3803 | 27670.8889 | 10.5431 | 27670.8834
38905.5582 | 9 | 0 | 38905.5582 | 1834 | 0 | 1568 | 1678 | 0.54945 | 0 | 111.9658 | 0 | 0.0054945 | 0 | 1.1197 | 0 | 0.0054945 | 1.1197 | 27670.8889 | 36.2803 | 27670.8834
38905.5584 | 9 | 0 | 38905.5584 | 1918 | 0 | 1585 | 1695 | 0.54945 | 0 | 117.094 | 0 | 0.0054945 | 0 | 1.1709 | 0 | 0.0054945 | 1.1709 | 27670.8889 | 30.3118 | 27670.8834
38905.5586 | 9 | 0 | 38905.5586 | 2218 | 0 | 1601.5 | 1711.5 | 0.54945 | 0 | 135.409 | 0 | 0.0054945 | 0 | 1.3541 | 0 | 0.0054945 | 1.3541 | 27670.8889 | 12.6862 | 27670.8834
38905.5588 | 9 | 0 | 38905.5588 | 2395 | 1 | 1618.5 | 1728.5 | 0.54945 | 0 | 146.2149 | 0.06105 | 0.0054945 | 0 | 1.4621 | 0.0006105 | 0.0054945 | 1.4615 | 27670.8889 | 4.4018 | 27670.8834
38905.559 | 9 | 0 | 38905.559 | 2415 | 0 | 1635 | 1745 | 0.54945 | 0 | 147.4359 | 0 | 0.0054945 | 0 | 1.4744 | 0 | 0.0054945 | 1.4744 | 27670.8889 | 3.494 | 27670.8834
38905.5592 | 9 | 0 | 38905.5592 | 2307 | 0 | 1652 | 1762 | 0.54945 | 0 | 140.8425 | 0 | 0.0054945 | 0 | 1.4084 | 0 | 0.0054945 | 1.4084 | 27670.8889 | 8.339 | 27670.8834
38905.5594 | 2229 | 25 | 38905.5594 | 2335 | 26 | 1668.5 | 1778.5 | 136.0806 | 1.5263 | 142.5519 | 1.5873 | 1.3608 | 0.015263 | 1.4255 | 0.015873 | 1.3455 | 1.4096 | 14.3794 | 7.724 | 70.3763
38905.5596 | 2069 | 33 | 38905.5596 | 2365 | 36 | 1685.5 | 1795.5 | 126.3126 | 2.0147 | 144.3834 | 2.1978 | 1.2631 | 0.020147 | 1.4438 | 0.021978 | 1.243 | 1.4219 | 28.7925 | 6.0972 | 69.2018
38905.5598 | 2190 | 28 | 38905.5598 | 2171 | 27 | 1702.5 | 1812.5 | 133.6996 | 1.7094 | 132.5397 | 1.6484 | 1.337 | 0.017094 | 1.3254 | 0.016484 | 1.3199 | 1.3089 | 15.5153 | 16.6692 | 143.58
38905.56 | 2081 | 1 | 38905.56 | 2043 | 1 | 1719 | 1829 | 127.0452 | 0.06105 | 124.7253 | 0.06105 | 1.2705 | 0.0006105 | 1.2473 | 0.0006105 | 1.2698 | 1.2466 | 20.1577 | 22.4041 | 7639.4652
38905.5602 | 1963 | 1 | 38905.5602 | 2209 | 1 | 1736 | 1846 | 119.8413 | 0.06105 | 134.8596 | 0.06105 | 1.1984 | 0.0006105 | 1.3486 | 0.0006105 | 1.1978 | 1.348 | 27.4446 | 13.173 | 6231.6664
38905.5603 | 1932 | 1 | 38905.5604 | 2170 | 1 | 1752.5 | 1862.5 | 117.9487 | 0.06105 | 132.4786 | 0.06105 | 1.1795 | 0.0006105 | 1.3248 | 0.0006105 | 1.1789 | 1.3242 | 29.4831 | 15.2096 | 7477.1593
38905.5605 | 2374 | 2 | 38905.5606 | 2258 | 1 | 1769.5 | 1879.5 | 144.9328 | 0.1221 | 137.851 | 0.06105 | 1.4493 | 0.001221 | 1.3785 | 0.0006105 | 1.4481 | 1.3779 | 5.3275 | 10.7844 | 600.5273
38905.5607 | 2140 | 1 | 38905.5608 | 2124 | 1 | 1786.5 | 1896.5 | 130.6471 | 0.06105 | 129.6703 | 0.06105 | 1.3065 | 0.0006105 | 1.2967 | 0.0006105 | 1.3059 | 1.2961 | 16.8457 | 17.7312 | 5397.4611
38905.5609 | 1977 | 1 | 38905.5609 | 1993 | 1 | 1803 | 1913 | 120.696 | 0.06105 | 121.6728 | 0.06105 | 1.207 | 0.0006105 | 1.2167 | 0.0006105 | 1.2063 | 1.2161 | 26.4889 | 25.469 | 10583.4961
38905.5611 | 2052 | 1 | 38905.5611 | 2454 | 1 | 1820 | 1930 | 125.2747 | 0.06105 | 149.8168 | 0.06105 | 1.2527 | 0.0006105 | 1.4982 | 0.0006105 | 1.2521 | 1.4976 | 22.4021 | 1.8534 | 812.2456
38905.5613 | 2459 | 1 | 38905.5613 | 2172 | 0 | 1836.5 | 1946.5 | 150.1221 | 0.06105 | 132.6007 | 0 | 1.5012 | 0.0006105 | 1.326 | 0 | 1.5006 | 1.326 | 1.6472 | 15.0727 | 515.8169
38905.5615 | 2273 | 15 | 38905.5615 | 2304 | 13 | 1853.5 | 1963.5 | 138.7668 | 0.91575 | 140.6593 | 0.79365 | 1.3877 | 0.0091575 | 1.4066 | 0.0079365 | 1.3785 | 1.3987 | 10.8247 | 8.9999 | 116.3552
38905.5617 | 2197 | 25 | 38905.5617 | 2039 | 22 | 1870.5 | 1980.5 | 134.127 | 1.5263 | 124.4811 | 1.3431 | 1.3413 | 0.015263 | 1.2448 | 0.013431 | 1.326 | 1.2314 | 14.6031 | 24.6674 | 219.5362
38905.5619 | 1973 | 0 | 38905.5619 | 2063 | 0 | 1887 | 1997 | 120.4518 | 0 | 125.9463 | 0 | 1.2045 | 0 | 1.2595 | 0 | 1.2045 | 1.2595 | 26.6792 | 21.1527 | 25.4747
38905.5621 | 2399 | 1 | 38905.5621 | 350 | 0 | 1904 | 2014 | 146.4591 | 0.06105 | 21.3675 | 0 | 1.4646 | 0.0006105 | 0.21368 | 0 | 1.464 | 0.21368 | 4.1863 | 614.1086 | 8546.3349
38905.5623 | 2411 | 1 | 38905.5623 | 1996 | 0 | 1920.5 | 2030.5 | 147.1917 | 0.06105 | 121.8559 | 0 | 1.4719 | 0.0006105 | 1.2186 | 0 | 1.4713 | 1.2186 | 3.6733 | 25.2194 | 1759.8502
38905.5625 | 2268 | 1 | 38905.5625 | 1931 | 1 | 1937.5 | 2047.5 | 138.4615 | 0.06105 | 117.8877 | 0.06105 | 1.3846 | 0.0006105 | 1.1789 | 0.0006105 | 1.384 | 1.1783 | 10.2217 | 29.5998 | 5261.7355
38905.5627 | 2446 | 1 | 38905.5627 | 2192 | 1 | 1954.5 | 2064.5 | 149.3284 | 0.06105 | 133.8217 | 0.06105 | 1.4933 | 0.0006105 | 1.3382 | 0.0006105 | 1.4927 | 1.3376 | 2.1895 | 14.3279 | 656.4406
38905.5629 | 2020 | 1 | 38905.5629 | 1907 | 1 | 1971 | 2081 | 123.3211 | 0.06105 | 116.4225 | 0.06105 | 1.2332 | 0.0006105 | 1.1642 | 0.0006105 | 1.2326 | 1.1636 | 23.7813 | 31.1485 | 11361.7827
38905.5631 | 2245 | 1 | 38905.5631 | 2106 | 2 | 1988 | 2098 | 137.0574 | 0.06105 | 128.5714 | 0.1221 | 1.3706 | 0.0006105 | 1.2857 | 0.001221 | 1.37 | 1.2845 | 11.3629 | 18.8545 | 4019.4966
38905.5633 | 2358 | 2 | 38905.5633 | 1982 | 1 | 2004.5 | 2114.5 | 143.956 | 0.1221 | 121.0012 | 0.06105 | 1.4396 | 0.001221 | 1.21 | 0.0006105 | 1.4383 | 1.2094 | 6.0203 | 26.338 | 1452.843
38905.5635 | 2242 | 2 | 38905.5635 | 1949 | 2 | 2021.5 | 2131.5 | 136.8742 | 0.1221 | 118.9866 | 0.1221 | 1.3687 | 0.001221 | 1.1899 | 0.001221 | 1.3675 | 1.1886 | 11.5263 | 28.5223 | 2833.7589
38905.5637 | 1883 | 3 | 38905.5637 | 2217 | 4 | 2038.5 | 2148.5 | 114.9573 | 0.18315 | 135.348 | 0.2442 | 1.1496 | 0.0018315 | 1.3535 | 0.002442 | 1.1477 | 1.351 | 33.1991 | 12.8299 | 2324.9178
38905.5638 | 2338 | 5 | 38905.5639 | 2287 | 5 | 2055 | 2165 | 142.735 | 0.30525 | 139.6215 | 0.30525 | 1.4274 | 0.0030525 | 1.3962 | 0.0030525 | 1.4243 | 1.3932 | 7.0752 | 9.6042 | 274.059
38905.564 | 2426 | 8 | 38905.5641 | 2352 | 7 | 2072 | 2182 | 148.1074 | 0.4884 | 143.5897 | 0.42735 | 1.4811 | 0.004884 | 1.4359 | 0.0042735 | 1.4762 | 1.4316 | 3.1868 | 6.9344 | 52.9965
38905.5642 | 1957 | 6 | 38905.5642 | 1941 | 7 | 2088.5 | 2198.5 | 119.475 | 0.3663 | 118.4982 | 0.42735 | 1.1947 | 0.003663 | 1.185 | 0.0042735 | 1.1911 | 1.1807 | 28.0955 | 29.2486 | 2023.02
38905.5644 | 2380 | 10 | 38905.5644 | 2304 | 10 | 2105.5 | 2215.5 | 145.2991 | 0.6105 | 140.6593 | 0.6105 | 1.453 | 0.006105 | 1.4066 | 0.006105 | 1.4469 | 1.4005 | 5.277 | 9.2839 | 92.9209
38905.5646 | 2069 | 9 | 38905.5646 | 2183 | 13 | 2122.5 | 2232.5 | 126.3126 | 0.54945 | 133.2723 | 0.79365 | 1.2631 | 0.0054945 | 1.3327 | 0.0079365 | 1.2576 | 1.3248 | 21.5191 | 14.9972 | 610.5978
38905.5648 | 2400 | 15 | 38905.5648 | 2284 | 14 | 2139 | 2249 | 146.5201 | 0.91575 | 139.4383 | 0.8547 | 1.4652 | 0.0091575 | 1.3944 | 0.008547 | 1.456 | 1.3858 | 4.4189 | 11.0271 | 55.8705
38905.565 | 2381 | 14 | 38905.565 | 2107 | 16 | 2156 | 2266 | 145.3602 | 0.8547 | 128.6325 | 0.9768 | 1.4536 | 0.008547 | 1.2863 | 0.009768 | 1.4451 | 1.2766 | 5.1391 | 22.048 | 134.6876
38905.5652 | 1969 | 18 | 38905.5652 | 2089 | 20 | 2172.5 | 2282.5 | 120.2076 | 1.0989 | 127.5336 | 1.221 | 1.2021 | 0.010989 | 1.2753 | 0.01221 | 1.1911 | 1.2631 | 28.4641 | 20.532 | 484.8955
38905.5654 | 2157 | 27 | 38905.5654 | 2163 | 27 | 2189.5 | 2299.5 | 131.685 | 1.6484 | 132.0513 | 1.6484 | 1.3168 | 0.016484 | 1.3205 | 0.016484 | 1.3004 | 1.304 | 17.3706 | 16.984 | 169.584
38905.5656 | 1997 | 0 | 38905.5656 | 2162 | 1 | 2206.5 | 2316.5 | 121.917 | 0 | 131.9902 | 0.06105 | 1.2192 | 0 | 1.3199 | 0.0006105 | 1.2192 | 1.3193 | 25.1567 | 15.6585 | 23.9376
38905.5658 | 2109 | 0 | 38905.5658 | 2020 | 0 | 2223 | 2333 | 128.7546 | 0 | 123.3211 | 0 | 1.2875 | 0 | 1.2332 | 0 | 1.2875 | 1.2332 | 18.5102 | 23.7317 | 17.2226
38905.566 | 1993 | 0 | 38905.566 | 2470 | 0 | 2240 | 2350 | 121.6728 | 0 | 150.7937 | 0 | 1.2167 | 0 | 1.5079 | 0 | 1.2167 | 1.5079 | 25.4079 | 1.1895 | 24.1912
38905.5662 | 2088 | 0 | 38905.5662 | 2382 | 0 | 2256.5 | 2366.5 | 127.4725 | 0 | 145.4212 | 0 | 1.2747 | 0 | 1.4542 | 0 | 1.2747 | 1.4542 | 19.7021 | 4.9278 | 18.4274
38905.5664 | 2280 | 0 | 38905.5664 | 2389 | 1 | 2273.5 | 2383.5 | 139.1941 | 0 | 145.8486 | 0.06105 | 1.3919 | 0 | 1.4585 | 0.0006105 | 1.3919 | 1.4579 | 9.6219 | 4.6642 | 8.23
38905.5666 | 2408 | 1 | 38905.5666 | 2353 | 0 | 2290.5 | 2400.5 | 147.0085 | 0.06105 | 143.6508 | 0 | 1.4701 | 0.0006105 | 1.4365 | 0 | 1.4695 | 1.4365 | 3.822 | 6.221 | 529.3242
38905.5668 | 2415 | 1 | 38905.5668 | 2375 | 0 | 2307 | 2417 | 147.4359 | 0.06105 | 144.9939 | 0 | 1.4744 | 0.0006105 | 1.4499 | 0 | 1.4737 | 1.4499 | 3.5233 | 5.2371 | 414.9351
38905.567 | 2375 | 0 | 38905.567 | 2299 | 0 | 2324 | 2434 | 144.9939 | 0 | 140.3541 | 0 | 1.4499 | 0 | 1.4035 | 0 | 1.4499 | 1.4035 | 5.2371 | 8.716 | 3.7871
38905.5672 | 2121 | 0 | 38905.5672 | 2483 | 0 | 2340.5 | 2450.5 | 129.4872 | 0 | 151.5873 | 0 | 1.2949 | 0 | 1.5159 | 0 | 1.2949 | 1.5159 | 17.8397 | 0.65969 | 16.5448

## C2-4
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 152.0989 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38905.5389 | 1 | 0 | 38905.5389 | 1 | 0 | -97.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5391 | 1 | 0 | 38905.5391 | 1 | 0 | -81 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5393 | 1 | 0 | 38905.5393 | 1 | 0 | -64.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5395 | 1 | 0 | 38905.5395 | 1 | 0 | -47.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5397 | 1 | 0 | 38905.5397 | 1 | 0 | -30.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5399 | 1 | 0 | 38905.5399 | 1 | 0 | -13.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5401 | 1 | 0 | 38905.5401 | 1 | 0 | 3 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5403 | 1 | 0 | 38905.5403 | 1 | 0 | 20 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5405 | 1 | 0 | 38905.5405 | 1 | 0 | 36.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5407 | 2 | 0 | 38905.5407 | 1 | 0 | 53.5 | 163.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124469 | 249038 | 124468.9988
38905.5409 | 1 | 0 | 38905.5409 | 2 | 0 | 70.5 | 180.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249038 | 124469 | 249037.9994
38905.5411 | 1 | 0 | 38905.5411 | 1 | 0 | 87 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5413 | 1 | 0 | 38905.5413 | 1 | 0 | 103.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5415 | 1 | 0 | 38905.5415 | 1 | 0 | 120.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5417 | 1 | 0 | 38905.5417 | 1 | 0 | 137.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5419 | 1 | 0 | 38905.5419 | 1 | 0 | 154.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.542 | 1 | 0 | 38905.5421 | 1 | 0 | 171 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5422 | 1 | 0 | 38905.5422 | 1 | 0 | 187.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5424 | 1 | 0 | 38905.5424 | 1 | 0 | 204.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5426 | 1 | 0 | 38905.5426 | 1 | 0 | 221.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5428 | 1 | 0 | 38905.5428 | 1 | 0 | 238.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.543 | 1 | 0 | 38905.543 | 1 | 0 | 255 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5432 | 1 | 0 | 38905.5432 | 1 | 0 | 272 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5434 | 1 | 0 | 38905.5434 | 1 | 0 | 288.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5436 | 1 | 0 | 38905.5436 | 1 | 0 | 305.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5438 | 1 | 0 | 38905.5438 | 1 | 0 | 322 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.544 | 1 | 0 | 38905.544 | 1 | 0 | 339 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5442 | 1 | 0 | 38905.5442 | 1 | 0 | 355.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5444 | 1 | 0 | 38905.5444 | 1 | 0 | 372.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5446 | 2 | 0 | 38905.5446 | 1 | 0 | 389.5 | 499.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124469 | 249038 | 124468.9988
38905.5448 | 1 | 0 | 38905.5448 | 1 | 0 | 406 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.545 | 1 | 0 | 38905.545 | 1 | 0 | 423 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5452 | 1 | 0 | 38905.5452 | 1 | 0 | 439.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5453 | 1 | 0 | 38905.5454 | 1 | 0 | 456.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5455 | 1 | 0 | 38905.5456 | 1 | 0 | 473.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5457 | 1 | 0 | 38905.5458 | 1 | 0 | 490 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5459 | 1 | 0 | 38905.5459 | 1 | 0 | 507 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5461 | 1 | 0 | 38905.5461 | 1 | 0 | 523.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5463 | 1 | 1 | 38905.5463 | 1 | 0 | 540.5 | 650.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 620199254.44 | 249038 | 248838.0803
38905.5465 | 1 | 0 | 38905.5465 | 1 | 0 | 557.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5467 | 1 | 0 | 38905.5467 | 1 | 0 | 574 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5469 | 1 | 0 | 38905.5469 | 1 | 0 | 591 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5471 | 1 | 0 | 38905.5471 | 1 | 0 | 607.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5473 | 1 | 0 | 38905.5473 | 1 | 0 | 624.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5475 | 1 | 0 | 38905.5475 | 1 | 0 | 641.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5477 | 1 | 0 | 38905.5477 | 1 | 0 | 658 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5479 | 1 | 0 | 38905.5479 | 1 | 0 | 675 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5481 | 1 | 0 | 38905.5481 | 1 | 0 | 691.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5483 | 1 | 0 | 38905.5483 | 1 | 0 | 708.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5485 | 1 | 0 | 38905.5485 | 1 | 0 | 725.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5486 | 1 | 0 | 38905.5487 | 1 | 0 | 742 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5488 | 1 | 0 | 38905.5489 | 1 | 0 | 759 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.549 | 1 | 0 | 38905.5491 | 1 | 0 | 775.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5492 | 1 | 0 | 38905.5492 | 1 | 0 | 792.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5494 | 1 | 0 | 38905.5494 | 1 | 0 | 809.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5496 | 1 | 0 | 38905.5496 | 1 | 0 | 826 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5498 | 1 | 0 | 38905.5498 | 1 | 0 | 843 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.55 | 1 | 0 | 38905.55 | 1 | 0 | 859.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5502 | 1 | 0 | 38905.5502 | 1 | 0 | 876.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5504 | 1 | 0 | 38905.5504 | 1 | 0 | 893.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5506 | 1 | 0 | 38905.5506 | 1 | 0 | 910 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5508 | 1 | 0 | 38905.5508 | 1 | 0 | 927 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.551 | 1 | 0 | 38905.551 | 1 | 0 | 943.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5512 | 1 | 0 | 38905.5512 | 1 | 0 | 960.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5514 | 1 | 0 | 38905.5514 | 1 | 0 | 977.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5516 | 1 | 0 | 38905.5516 | 1 | 0 | 994 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5518 | 1 | 0 | 38905.5518 | 1 | 0 | 1011 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.552 | 1 | 0 | 38905.552 | 1 | 0 | 1027.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5522 | 1 | 0 | 38905.5522 | 1 | 0 | 1044.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5523 | 1 | 0 | 38905.5524 | 1 | 0 | 1061.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5525 | 1 | 0 | 38905.5526 | 1 | 0 | 1078 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5527 | 1 | 0 | 38905.5528 | 1 | 0 | 1095 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5529 | 1 | 0 | 38905.5529 | 1 | 0 | 1111.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5531 | 1 | 0 | 38905.5531 | 1 | 0 | 1128.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5533 | 1 | 0 | 38905.5533 | 1 | 0 | 1145.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5535 | 1 | 0 | 38905.5535 | 1 | 0 | 1162 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5537 | 1 | 0 | 38905.5537 | 1 | 0 | 1178.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5539 | 1 | 0 | 38905.5539 | 1 | 0 | 1195.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5541 | 1 | 0 | 38905.5541 | 1 | 0 | 1212.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5543 | 1 | 0 | 38905.5543 | 1 | 0 | 1229.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38905.5545 | 1 | 0 | 38905.5545 | 1747 | 0 | 1246 | 1356 | 0.06105 | 0 | 106.6545 | 0 | 0.0006105 | 0 | 1.0665 | 0 | 0.0006105 | 1.0665 | 249038 | 42.609 | 249037.9994
38905.5547 | 4 | 0 | 38905.5547 | 1566 | 0 | 1262.5 | 1372.5 | 0.2442 | 0 | 95.6044 | 0 | 0.002442 | 0 | 0.95604 | 0 | 0.002442 | 0.95604 | 62184.5 | 59.092 | 62184.4976
38905.5549 | 4 | 0 | 38905.5549 | 1694 | 0 | 1279.5 | 1389.5 | 0.2442 | 0 | 103.4188 | 0 | 0.002442 | 0 | 1.0342 | 0 | 0.002442 | 1.0342 | 62184.5 | 47.0708 | 62184.4976
38905.5551 | 4 | 0 | 38905.5551 | 1533 | 0 | 1296.5 | 1406.5 | 0.2442 | 0 | 93.5897 | 0 | 0.002442 | 0 | 0.9359 | 0 | 0.002442 | 0.9359 | 62184.5 | 62.5166 | 62184.4976
38905.5553 | 4 | 0 | 38905.5553 | 2034 | 0 | 1313.5 | 1423.5 | 0.2442 | 0 | 124.1758 | 0 | 0.002442 | 0 | 1.2418 | 0 | 0.002442 | 1.2418 | 62184.5 | 22.4867 | 62184.4976
38905.5555 | 5 | 0 | 38905.5555 | 2325 | 0 | 1330 | 1440 | 0.30525 | 0 | 141.9414 | 0 | 0.0030525 | 0 | 1.4194 | 0 | 0.0030525 | 1.4194 | 49727.6 | 7.1561 | 49727.5969
38905.5556 | 6 | 0 | 38905.5557 | 2409 | 0 | 1346.5 | 1456.5 | 0.3663 | 0 | 147.0696 | 0 | 0.003663 | 0 | 1.4707 | 0 | 0.003663 | 1.4707 | 41423 | 3.4197 | 41422.9963
38905.5558 | 6 | 0 | 38905.5559 | 2026 | 0 | 1363.5 | 1473.5 | 0.3663 | 0 | 123.6874 | 0 | 0.003663 | 0 | 1.2369 | 0 | 0.003663 | 1.2369 | 41423 | 22.9704 | 41422.9963
38905.556 | 7 | 0 | 38905.5561 | 2063 | 0 | 1380.5 | 1490.5 | 0.42735 | 0 | 125.9463 | 0 | 0.0042735 | 0 | 1.2595 | 0 | 0.0042735 | 1.2595 | 35491.1429 | 20.7649 | 35491.1386
38905.5562 | 6 | 0 | 38905.5563 | 2390 | 0 | 1397.5 | 1507.5 | 0.3663 | 0 | 145.9096 | 0 | 0.003663 | 0 | 1.4591 | 0 | 0.003663 | 1.4591 | 41423 | 4.2418 | 41422.9963
38905.5564 | 7 | 0 | 38905.5564 | 2086 | 0 | 1414 | 1524 | 0.42735 | 0 | 127.3504 | 0 | 0.0042735 | 0 | 1.2735 | 0 | 0.0042735 | 1.2735 | 35491.1429 | 19.4334 | 35491.1386
38905.5566 | 7 | 0 | 38905.5566 | 2124 | 0 | 1431 | 1541 | 0.42735 | 0 | 129.6703 | 0 | 0.0042735 | 0 | 1.2967 | 0 | 0.0042735 | 1.2967 | 35491.1429 | 17.2966 | 35491.1386
38905.5568 | 7 | 0 | 38905.5568 | 2000 | 0 | 1447.5 | 1557.5 | 0.42735 | 0 | 122.1001 | 0 | 0.0042735 | 0 | 1.221 | 0 | 0.0042735 | 1.221 | 35491.1429 | 24.569 | 35491.1386
38905.557 | 6 | 0 | 38905.557 | 2358 | 0 | 1464.5 | 1574.5 | 0.3663 | 0 | 143.956 | 0 | 0.003663 | 0 | 1.4396 | 0 | 0.003663 | 1.4396 | 41423 | 5.6565 | 41422.9963
38905.5572 | 6 | 0 | 38905.5572 | 2321 | 0 | 1481.5 | 1591.5 | 0.3663 | 0 | 141.6972 | 0 | 0.003663 | 0 | 1.417 | 0 | 0.003663 | 1.417 | 41423 | 7.3408 | 41422.9963
38905.5574 | 7 | 0 | 38905.5574 | 2238 | 0 | 1498 | 1608 | 0.42735 | 0 | 136.63 | 0 | 0.0042735 | 0 | 1.3663 | 0 | 0.0042735 | 1.3663 | 35491.1429 | 11.3217 | 35491.1386
38905.5576 | 7 | 0 | 38905.5576 | 2236 | 0 | 1515 | 1625 | 0.42735 | 0 | 136.5079 | 0 | 0.0042735 | 0 | 1.3651 | 0 | 0.0042735 | 1.3651 | 35491.1429 | 11.4213 | 35491.1386
38905.5578 | 7 | 0 | 38905.5578 | 1958 | 0 | 1531.5 | 1641.5 | 0.42735 | 0 | 119.536 | 0 | 0.0042735 | 0 | 1.1954 | 0 | 0.0042735 | 1.1954 | 35491.1429 | 27.2411 | 35491.1386
38905.558 | 6 | 0 | 38905.558 | 2197 | 0 | 1548.5 | 1658.5 | 0.3663 | 0 | 134.127 | 0 | 0.003663 | 0 | 1.3413 | 0 | 0.003663 | 1.3413 | 41423 | 13.3992 | 41422.9963
38905.5582 | 6 | 0 | 38905.5582 | 2187 | 0 | 1565 | 1675 | 0.3663 | 0 | 133.5165 | 0 | 0.003663 | 0 | 1.3352 | 0 | 0.003663 | 1.3352 | 41423 | 13.9177 | 41422.9963
38905.5584 | 7 | 0 | 38905.5584 | 2163 | 0 | 1582 | 1692 | 0.42735 | 0 | 132.0513 | 0 | 0.0042735 | 0 | 1.3205 | 0 | 0.0042735 | 1.3205 | 35491.1429 | 15.1817 | 35491.1386
38905.5586 | 6 | 0 | 38905.5586 | 1880 | 0 | 1598.5 | 1708.5 | 0.3663 | 0 | 114.7741 | 0 | 0.003663 | 0 | 1.1477 | 0 | 0.003663 | 1.1477 | 41423 | 32.5202 | 41422.9963
38905.5588 | 6 | 0 | 38905.5588 | 2189 | 0 | 1615.5 | 1725.5 | 0.3663 | 0 | 133.6386 | 0 | 0.003663 | 0 | 1.3364 | 0 | 0.003663 | 1.3364 | 41423 | 13.8136 | 41422.9963
38905.559 | 6 | 0 | 38905.559 | 2230 | 0 | 1632.5 | 1742.5 | 0.3663 | 0 | 136.1416 | 0 | 0.003663 | 0 | 1.3614 | 0 | 0.003663 | 1.3614 | 41423 | 11.7211 | 41422.9963
38905.5592 | 6 | 0 | 38905.5592 | 2206 | 0 | 1649.5 | 1759.5 | 0.3663 | 0 | 134.6764 | 0 | 0.003663 | 0 | 1.3468 | 0 | 0.003663 | 1.3468 | 41423 | 12.9365 | 41422.9963
38905.5593 | 9 | 0 | 38905.5594 | 2012 | 0 | 1666 | 1776 | 0.54945 | 0 | 122.8327 | 0 | 0.0054945 | 0 | 1.2283 | 0 | 0.0054945 | 1.2283 | 27582 | 23.826 | 27581.9945
38905.5595 | 9 | 0 | 38905.5595 | 2065 | 0 | 1682.5 | 1792.5 | 0.54945 | 0 | 126.0684 | 0 | 0.0054945 | 0 | 1.2607 | 0 | 0.0054945 | 1.2607 | 27582 | 20.6479 | 27581.9945
38905.5597 | 9 | 0 | 38905.5597 | 2237 | 0 | 1699.5 | 1809.5 | 0.54945 | 0 | 136.569 | 0 | 0.0054945 | 0 | 1.3657 | 0 | 0.0054945 | 1.3657 | 27582 | 11.3715 | 27581.9945
38905.5599 | 8 | 0 | 38905.5599 | 1864 | 0 | 1716.5 | 1826.5 | 0.4884 | 0 | 113.7973 | 0 | 0.004884 | 0 | 1.138 | 0 | 0.004884 | 1.138 | 31042.25 | 33.6577 | 31042.2451
38905.5601 | 9 | 0 | 38905.5601 | 1877 | 0 | 1733 | 1843 | 0.54945 | 0 | 114.591 | 0 | 0.0054945 | 0 | 1.1459 | 0 | 0.0054945 | 1.1459 | 27582 | 32.732 | 27581.9945
38905.5603 | 8 | 0 | 38905.5603 | 1919 | 0 | 1750 | 1860 | 0.4884 | 0 | 117.1551 | 0 | 0.004884 | 0 | 1.1716 | 0 | 0.004884 | 1.1716 | 31042.25 | 29.827 | 31042.2451
38905.5605 | 8 | 0 | 38905.5605 | 2329 | 0 | 1766.5 | 1876.5 | 0.4884 | 0 | 142.1856 | 0 | 0.004884 | 0 | 1.4219 | 0 | 0.004884 | 1.4219 | 31042.25 | 6.9721 | 31042.2451
38905.5607 | 1341 | 0 | 38905.5607 | 2120 | 0 | 1783.5 | 1893.5 | 81.8681 | 0 | 129.4261 | 0 | 0.81868 | 0 | 1.2943 | 0 | 0.81868 | 1.2943 | 85.7852 | 17.5179 | 84.9666
38905.5609 | 2015 | 0 | 38905.5609 | 2450 | 0 | 1800.5 | 1910.5 | 123.0159 | 0 | 149.5726 | 0 | 1.2302 | 0 | 1.4957 | 0 | 1.2302 | 1.4957 | 23.6417 | 1.689 | 22.4115
38905.5611 | 2012 | 0 | 38905.5611 | 2067 | 0 | 1817 | 1927 | 122.8327 | 0 | 126.1905 | 0 | 1.2283 | 0 | 1.2619 | 0 | 1.2283 | 1.2619 | 23.826 | 20.5312 | 22.5977
38905.5613 | 1511 | 0 | 38905.5613 | 2463 | 0 | 1834 | 1944 | 92.2466 | 0 | 150.3663 | 0 | 0.92247 | 0 | 1.5037 | 0 | 0.92247 | 1.5037 | 64.8829 | 1.1523 | 63.9604
38905.5615 | 1688 | 0 | 38905.5615 | 2255 | 0 | 1850.5 | 1960.5 | 103.0525 | 0 | 137.6679 | 0 | 1.0305 | 0 | 1.3767 | 0 | 1.0305 | 1.3767 | 47.5936 | 10.4825 | 46.5631
38905.5617 | 2212 | 0 | 38905.5617 | 2176 | 0 | 1867.5 | 1977.5 | 135.0427 | 0 | 132.8449 | 0 | 1.3504 | 0 | 1.3284 | 0 | 1.3504 | 1.3284 | 12.6302 | 14.4936 | 11.2798
38905.5619 | 2024 | 0 | 38905.5619 | 2082 | 0 | 1884.5 | 1994.5 | 123.5653 | 0 | 127.1062 | 0 | 1.2357 | 0 | 1.2711 | 0 | 1.2357 | 1.2711 | 23.0919 | 19.6628 | 21.8562
38905.5621 | 2148 | 0 | 38905.5621 | 2474 | 1 | 1901 | 2011 | 131.1355 | 0 | 151.0379 | 0.06105 | 1.3114 | 0 | 1.5104 | 0.0006105 | 1.3114 | 1.5098 | 15.986 | 0.74323 | 14.6747
38905.5623 | 2449 | 1 | 38905.5623 | 2431 | 1 | 1918 | 2028 | 149.5116 | 0.06105 | 148.4127 | 0.06105 | 1.4951 | 0.0006105 | 1.4841 | 0.0006105 | 1.4945 | 1.4835 | 1.7595 | 2.5443 | 102.6702
38905.5625 | 2193 | 0 | 38905.5625 | 2169 | 1 | 1934.5 | 2044.5 | 133.8828 | 0 | 132.4176 | 0.06105 | 1.3388 | 0 | 1.3242 | 0.0006105 | 1.3388 | 1.3236 | 13.606 | 14.9161 | 12.2672
38905.5627 | 2236 | 1 | 38905.5627 | 2412 | 1 | 1951.5 | 2061.5 | 136.5079 | 0.06105 | 147.2527 | 0.06105 | 1.3651 | 0.0006105 | 1.4725 | 0.0006105 | 1.3645 | 1.4719 | 11.5832 | 3.3042 | 813.648
38905.5628 | 2457 | 2 | 38905.5629 | 2446 | 2 | 1968.5 | 2078.5 | 150 | 0.1221 | 149.3284 | 0.1221 | 1.5 | 0.001221 | 1.4933 | 0.001221 | 1.4988 | 1.4921 | 1.4609 | 1.967 | 31.231
38905.563 | 2137 | 1 | 38905.5631 | 2181 | 1 | 1985 | 2095 | 130.464 | 0.06105 | 133.1502 | 0.06105 | 1.3046 | 0.0006105 | 1.3315 | 0.0006105 | 1.304 | 1.3309 | 16.6454 | 14.277 | 4414.8811
38905.5632 | 2107 | 1 | 38905.5633 | 1895 | 1 | 2002 | 2112 | 128.6325 | 0.06105 | 115.6899 | 0.06105 | 1.2863 | 0.0006105 | 1.1569 | 0.0006105 | 1.2857 | 1.1563 | 18.2791 | 31.5791 | 9201.1473
38905.5634 | 2336 | 3 | 38905.5634 | 2070 | 3 | 2018.5 | 2128.5 | 142.6129 | 0.18315 | 126.3736 | 0.18315 | 1.4261 | 0.0018315 | 1.2637 | 0.0018315 | 1.4243 | 1.2619 | 6.7014 | 20.8374 | 875.8871
38905.5636 | 1975 | 3 | 38905.5636 | 1987 | 3 | 2035.5 | 2145.5 | 120.5739 | 0.18315 | 121.3065 | 0.18315 | 1.2057 | 0.0018315 | 1.2131 | 0.0018315 | 1.2039 | 1.2112 | 26.3423 | 25.5692 | 3484.5848
38905.5638 | 2346 | 5 | 38905.5638 | 2224 | 6 | 2052.5 | 2162.5 | 143.2234 | 0.30525 | 135.7753 | 0.3663 | 1.4322 | 0.0030525 | 1.3578 | 0.003663 | 1.4292 | 1.3541 | 6.3173 | 12.5943 | 314.0459
38905.564 | 2288 | 6 | 38905.564 | 1994 | 6 | 2069 | 2179 | 139.6825 | 0.3663 | 121.7338 | 0.3663 | 1.3968 | 0.003663 | 1.2173 | 0.003663 | 1.3932 | 1.2137 | 9.0038 | 25.8869 | 676.4734
38905.5642 | 2419 | 8 | 38905.5642 | 2303 | 8 | 2086 | 2196 | 147.6801 | 0.4884 | 140.5983 | 0.4884 | 1.4768 | 0.004884 | 1.406 | 0.004884 | 1.4719 | 1.4011 | 3.1139 | 9.243 | 68.0895
38905.5644 | 2343 | 9 | 38905.5644 | 2297 | 8 | 2102.5 | 2212.5 | 143.0403 | 0.54945 | 140.232 | 0.4884 | 1.4304 | 0.0054945 | 1.4023 | 0.004884 | 1.4249 | 1.3974 | 6.6431 | 8.9635 | 127.3955
38905.5646 | 2323 | 13 | 38905.5646 | 1925 | 10 | 2119.5 | 2229.5 | 141.8193 | 0.79365 | 117.5214 | 0.6105 | 1.4182 | 0.0079365 | 1.1752 | 0.006105 | 1.4103 | 1.1691 | 7.4204 | 31.8149 | 288.4812
38905.5648 | 2154 | 12 | 38905.5648 | 2389 | 11 | 2136.5 | 2246.5 | 131.5018 | 0.7326 | 145.8486 | 0.67155 | 1.315 | 0.007326 | 1.4585 | 0.0067155 | 1.3077 | 1.4518 | 18.0376 | 4.4186 | 114.7408
38905.565 | 2280 | 16 | 38905.565 | 2218 | 18 | 2153 | 2263 | 139.1941 | 0.9768 | 135.409 | 1.0989 | 1.3919 | 0.009768 | 1.3541 | 0.010989 | 1.3822 | 1.3431 | 9.8502 | 13.552 | 145.7368
38905.5652 | 1843 | 16 | 38905.5652 | 2297 | 22 | 2170 | 2280 | 112.5153 | 0.9768 | 140.232 | 1.3431 | 1.1252 | 0.009768 | 1.4023 | 0.013431 | 1.1154 | 1.3889 | 39.4312 | 8.759 | 318.3075
38905.5654 | 1995 | 23 | 38905.5654 | 1835 | 23 | 2186.5 | 2296.5 | 121.7949 | 1.4042 | 112.0269 | 1.4042 | 1.2179 | 0.014042 | 1.1203 | 0.014042 | 1.2039 | 1.1062 | 25.9666 | 38.0858 | 567.6702
38905.5656 | 2312 | 2 | 38905.5656 | 2035 | 1 | 2203.5 | 2313.5 | 141.1477 | 0.1221 | 124.2369 | 0.06105 | 1.4115 | 0.001221 | 1.2424 | 0.0006105 | 1.4103 | 1.2418 | 7.7953 | 22.58 | 1633.7234
38905.5658 | 1907 | 0 | 38905.5658 | 2425 | 1 | 2220.5 | 2330.5 | 116.4225 | 0 | 148.0464 | 0.06105 | 1.1642 | 0 | 1.4805 | 0.0006105 | 1.1642 | 1.4799 | 30.6439 | 2.7797 | 29.4797
38905.5659 | 2390 | 1 | 38905.566 | 2475 | 1 | 2237 | 2347 | 145.9096 | 0.06105 | 151.0989 | 0.06105 | 1.4591 | 0.0006105 | 1.511 | 0.0006105 | 1.4585 | 1.5104 | 4.5273 | 0.66805 | 66.6139
38905.5661 | 2147 | 0 | 38905.5662 | 2168 | 0 | 2254 | 2364 | 131.0745 | 0 | 132.3565 | 0 | 1.3107 | 0 | 1.3236 | 0 | 1.3107 | 1.3236 | 16.0401 | 14.9161 | 14.7293
38905.5663 | 1935 | 0 | 38905.5664 | 1938 | 0 | 2270.5 | 2380.5 | 118.1319 | 0 | 118.315 | 0 | 1.1813 | 0 | 1.1832 | 0 | 1.1813 | 1.1832 | 28.7535 | 28.5542 | 27.5722
38905.5665 | 2123 | 0 | 38905.5666 | 2023 | 0 | 2287.5 | 2397.5 | 129.6093 | 0 | 123.5043 | 0 | 1.2961 | 0 | 1.235 | 0 | 1.2961 | 1.235 | 17.3519 | 23.1527 | 16.0558
38905.5667 | 2191 | 0 | 38905.5667 | 2331 | 1 | 2304.5 | 2414.5 | 133.7607 | 0 | 142.3077 | 0.06105 | 1.3376 | 0 | 1.4231 | 0.0006105 | 1.3376 | 1.4225 | 13.7097 | 6.9262 | 12.3721
38905.5669 | 1970 | 0 | 38905.5669 | 1984 | 0 | 2321 | 2431 | 120.2686 | 0 | 121.1233 | 0 | 1.2027 | 0 | 1.2112 | 0 | 1.2027 | 1.2112 | 26.466 | 25.5736 | 25.2633
38905.5671 | 2219 | 0 | 38905.5671 | 2211 | 0 | 2338 | 2448 | 135.4701 | 0 | 134.9817 | 0 | 1.3547 | 0 | 1.3498 | 0 | 1.3547 | 1.3498 | 12.2749 | 12.6811 | 10.9202

## C2-3
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 152.7705 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38905.5389 | 1 | 0 | 38905.5389 | 1 | 0 | -100.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5391 | 1 | 0 | 38905.5391 | 1 | 0 | -83.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5393 | 1 | 0 | 38905.5393 | 1 | 0 | -67 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5395 | 1 | 0 | 38905.5395 | 1 | 0 | -50 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5397 | 1 | 0 | 38905.5397 | 1 | 0 | -33.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5399 | 1 | 0 | 38905.5399 | 1 | 0 | -16.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5401 | 1 | 0 | 38905.5401 | 1 | 0 | -6.8918e-07 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5403 | 1 | 0 | 38905.5403 | 1 | 0 | 17 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5405 | 1 | 0 | 38905.5405 | 1 | 0 | 34 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5406 | 2 | 0 | 38905.5407 | 1 | 0 | 50.5 | 160.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 125019 | 250138 | 125018.9988
38905.5408 | 1 | 0 | 38905.5409 | 1 | 0 | 67.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.541 | 1 | 0 | 38905.5411 | 1 | 0 | 84.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5412 | 1 | 0 | 38905.5413 | 1 | 0 | 101 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5414 | 1 | 1 | 38905.5414 | 1 | 0 | 118 | 228 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 625690190.44 | 250138 | 249938.0799
38905.5416 | 1 | 0 | 38905.5416 | 1 | 0 | 134.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5418 | 1 | 0 | 38905.5418 | 1 | 0 | 151.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.542 | 1 | 0 | 38905.542 | 1 | 0 | 168.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5422 | 1 | 0 | 38905.5422 | 1 | 0 | 185 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5424 | 1 | 0 | 38905.5424 | 1 | 0 | 202 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5426 | 1 | 0 | 38905.5426 | 1 | 0 | 218.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5428 | 1 | 0 | 38905.5428 | 1 | 0 | 235.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.543 | 1 | 0 | 38905.543 | 1 | 0 | 252.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5432 | 1 | 0 | 38905.5432 | 1 | 0 | 269 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5434 | 1 | 0 | 38905.5434 | 1 | 0 | 285.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5436 | 1 | 0 | 38905.5436 | 1 | 0 | 302.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5438 | 1 | 0 | 38905.5438 | 1 | 0 | 319.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.544 | 1 | 0 | 38905.544 | 1 | 0 | 336.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5441 | 1 | 0 | 38905.5442 | 1 | 0 | 353 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5443 | 1 | 0 | 38905.5444 | 1 | 0 | 369.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5445 | 1 | 0 | 38905.5445 | 1 | 0 | 386.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5447 | 1 | 0 | 38905.5447 | 1 | 0 | 403.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5449 | 1 | 1 | 38905.5449 | 1 | 0 | 420 | 530 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 625690190.44 | 250138 | 249938.0799
38905.5451 | 1 | 0 | 38905.5451 | 1 | 0 | 437 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5453 | 1 | 0 | 38905.5453 | 1 | 0 | 453.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5455 | 1 | 0 | 38905.5455 | 1 | 0 | 470.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5457 | 1 | 0 | 38905.5457 | 1 | 0 | 487.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5459 | 1 | 0 | 38905.5459 | 1 | 0 | 504 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5461 | 1 | 0 | 38905.5461 | 1 | 0 | 521 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5463 | 1 | 0 | 38905.5463 | 1 | 0 | 537.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5465 | 1 | 0 | 38905.5465 | 1 | 0 | 554.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5467 | 1 | 0 | 38905.5467 | 1 | 0 | 571.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5469 | 1 | 0 | 38905.5469 | 1 | 0 | 588 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5471 | 1 | 0 | 38905.5471 | 1 | 0 | 605 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5473 | 1 | 0 | 38905.5473 | 1 | 0 | 621.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5475 | 1 | 0 | 38905.5475 | 1 | 0 | 638.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5477 | 1 | 0 | 38905.5477 | 1 | 0 | 655.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5478 | 1 | 0 | 38905.5479 | 1 | 0 | 672 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.548 | 1 | 0 | 38905.5481 | 1 | 0 | 689 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5482 | 1 | 0 | 38905.5482 | 1 | 0 | 705.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5484 | 1 | 0 | 38905.5484 | 1 | 0 | 722.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5486 | 1 | 0 | 38905.5486 | 1 | 0 | 739.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5488 | 1 | 0 | 38905.5488 | 1 | 0 | 756 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.549 | 1 | 0 | 38905.549 | 1 | 0 | 773 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5492 | 1 | 0 | 38905.5492 | 1 | 0 | 789.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5494 | 1 | 0 | 38905.5494 | 1 | 0 | 806.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5496 | 1 | 0 | 38905.5496 | 1 | 0 | 823.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5498 | 1 | 0 | 38905.5498 | 1 | 0 | 840 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.55 | 1 | 0 | 38905.55 | 1 | 0 | 857 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5502 | 1 | 0 | 38905.5502 | 1 | 0 | 873.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5504 | 1 | 0 | 38905.5504 | 1 | 0 | 890.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5506 | 1 | 0 | 38905.5506 | 1 | 0 | 907.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5508 | 1 | 0 | 38905.5508 | 1 | 0 | 924 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5509 | 1 | 0 | 38905.551 | 1 | 0 | 941 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5511 | 1 | 0 | 38905.5512 | 1 | 0 | 957.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5513 | 1 | 0 | 38905.5514 | 1 | 0 | 974.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5515 | 1 | 0 | 38905.5516 | 1 | 0 | 991.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5517 | 1 | 0 | 38905.5517 | 1 | 0 | 1008 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5519 | 1 | 0 | 38905.5519 | 1 | 0 | 1025 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5521 | 1 | 0 | 38905.5521 | 1 | 0 | 1041.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5523 | 1 | 0 | 38905.5523 | 1 | 0 | 1058.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5525 | 1 | 0 | 38905.5525 | 1 | 0 | 1075.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5527 | 1 | 0 | 38905.5527 | 1 | 0 | 1092 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5529 | 1 | 0 | 38905.5529 | 1 | 0 | 1109 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5531 | 1 | 0 | 38905.5531 | 1 | 0 | 1125.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5533 | 1 | 0 | 38905.5533 | 1 | 0 | 1142.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5535 | 1 | 0 | 38905.5535 | 1 | 0 | 1159.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5537 | 1 | 0 | 38905.5537 | 1 | 0 | 1176 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5539 | 1 | 0 | 38905.5539 | 1 | 0 | 1193 | 1303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5541 | 1 | 0 | 38905.5541 | 1 | 0 | 1209.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5543 | 1 | 0 | 38905.5543 | 1 | 0 | 1226.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5545 | 1 | 0 | 38905.5545 | 1 | 0 | 1243.5 | 1353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38905.5546 | 7 | 0 | 38905.5547 | 4 | 0 | 1260 | 1370 | 0.42735 | 0 | 0.2442 | 0 | 0.0042735 | 0 | 0.002442 | 0 | 0.0042735 | 0.002442 | 35648.2857 | 62459.5 | 35648.2814
38905.5548 | 9 | 0 | 38905.5549 | 6 | 0 | 1277 | 1387 | 0.54945 | 0 | 0.3663 | 0 | 0.0054945 | 0 | 0.003663 | 0 | 0.0054945 | 0.003663 | 27704.2222 | 41606.3333 | 27704.2167
38905.555 | 8 | 0 | 38905.555 | 6 | 0 | 1293.5 | 1403.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 31179.75 | 41606.3333 | 31179.7451
38905.5552 | 9 | 0 | 38905.5552 | 7 | 0 | 1310.5 | 1420.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5554 | 9 | 0 | 38905.5554 | 8 | 0 | 1327 | 1437 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5556 | 9 | 0 | 38905.5556 | 8 | 0 | 1344 | 1454 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5558 | 9 | 0 | 38905.5558 | 8 | 0 | 1361 | 1471 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.556 | 9 | 0 | 38905.556 | 7 | 0 | 1377.5 | 1487.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5562 | 9 | 0 | 38905.5562 | 8 | 0 | 1394.5 | 1504.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5564 | 10 | 0 | 38905.5564 | 8 | 0 | 1411 | 1521 | 0.6105 | 0 | 0.4884 | 0 | 0.006105 | 0 | 0.004884 | 0 | 0.006105 | 0.004884 | 24923.8 | 31179.75 | 24923.7939
38905.5566 | 9 | 0 | 38905.5566 | 8 | 0 | 1428 | 1538 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5568 | 9 | 0 | 38905.5568 | 8 | 0 | 1444.5 | 1554.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.557 | 9 | 0 | 38905.557 | 8 | 0 | 1461.5 | 1571.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5572 | 8 | 0 | 38905.5572 | 8 | 0 | 1478.5 | 1588.5 | 0.4884 | 0 | 0.4884 | 0 | 0.004884 | 0 | 0.004884 | 0 | 0.004884 | 0.004884 | 31179.75 | 31179.75 | 31179.7451
38905.5574 | 9 | 0 | 38905.5574 | 8 | 0 | 1495.5 | 1605.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5576 | 9 | 0 | 38905.5576 | 8 | 0 | 1512 | 1622 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5578 | 9 | 0 | 38905.5578 | 7 | 0 | 1529 | 1639 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.558 | 9 | 0 | 38905.558 | 7 | 0 | 1545.5 | 1655.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5581 | 9 | 0 | 38905.5582 | 7 | 0 | 1562.5 | 1672.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5583 | 9 | 0 | 38905.5584 | 7 | 0 | 1579.5 | 1689.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5585 | 9 | 0 | 38905.5586 | 7 | 0 | 1596 | 1706 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5587 | 9 | 0 | 38905.5587 | 7 | 0 | 1612.5 | 1722.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5589 | 9 | 0 | 38905.5589 | 8 | 0 | 1629.5 | 1739.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27704.2222 | 31179.75 | 27704.2167
38905.5591 | 9 | 0 | 38905.5591 | 7 | 0 | 1646.5 | 1756.5 | 0.54945 | 0 | 0.42735 | 0 | 0.0054945 | 0 | 0.0042735 | 0 | 0.0054945 | 0.0042735 | 27704.2222 | 35648.2857 | 27704.2167
38905.5593 | 8 | 0 | 38905.5593 | 2378 | 0 | 1663.5 | 1773.5 | 0.4884 | 0 | 145.177 | 0 | 0.004884 | 0 | 1.4518 | 0 | 0.004884 | 1.4518 | 31179.75 | 5.2304 | 31179.7451
38905.5595 | 9 | 0 | 38905.5595 | 1871 | 0 | 1680 | 1790 | 0.54945 | 0 | 114.2247 | 0 | 0.0054945 | 0 | 1.1422 | 0 | 0.0054945 | 1.1422 | 27704.2222 | 33.7456 | 27704.2167
38905.5597 | 9 | 0 | 38905.5597 | 1888 | 0 | 1696.5 | 1806.5 | 0.54945 | 0 | 115.2625 | 0 | 0.0054945 | 0 | 1.1526 | 0 | 0.0054945 | 1.1526 | 27704.2222 | 32.5413 | 27704.2167
38905.5599 | 9 | 0 | 38905.5599 | 1884 | 0 | 1713.5 | 1823.5 | 0.54945 | 0 | 115.0183 | 0 | 0.0054945 | 0 | 1.1502 | 0 | 0.0054945 | 1.1502 | 27704.2222 | 32.8227 | 27704.2167
38905.5601 | 9 | 0 | 38905.5601 | 2164 | 0 | 1730.5 | 1840.5 | 0.54945 | 0 | 132.1123 | 0 | 0.0054945 | 0 | 1.3211 | 0 | 0.0054945 | 1.3211 | 27704.2222 | 15.6368 | 27704.2167
38905.5603 | 8 | 0 | 38905.5603 | 2438 | 0 | 1747 | 1857 | 0.4884 | 0 | 148.84 | 0 | 0.004884 | 0 | 1.4884 | 0 | 0.004884 | 1.4884 | 31179.75 | 2.6407 | 31179.7451
38905.5605 | 8 | 0 | 38905.5605 | 2028 | 1 | 1764 | 1874 | 0.4884 | 0 | 123.8095 | 0.06105 | 0.004884 | 0 | 1.2381 | 0.0006105 | 0.004884 | 1.2375 | 31179.75 | 23.4524 | 31179.7451
38905.5607 | 10 | 0 | 38905.5607 | 2258 | 0 | 1780.5 | 1890.5 | 0.6105 | 0 | 137.851 | 0 | 0.006105 | 0 | 1.3785 | 0 | 0.006105 | 1.3785 | 24923.8 | 10.8229 | 24923.7939
38905.5609 | 1974 | 0 | 38905.5609 | 2434 | 0 | 1797.5 | 1907.5 | 120.5128 | 0 | 148.5958 | 0 | 1.2051 | 0 | 1.486 | 0 | 1.2051 | 1.486 | 26.767 | 2.8094 | 25.5618
38905.5611 | 1827 | 0 | 38905.5611 | 2169 | 0 | 1814.5 | 1924.5 | 111.5385 | 0 | 132.4176 | 0 | 1.1154 | 0 | 1.3242 | 0 | 1.1154 | 1.3242 | 36.9666 | 15.3702 | 35.8512
38905.5612 | 1715 | 0 | 38905.5613 | 2383 | 0 | 1831 | 1941 | 104.7009 | 0 | 145.4823 | 0 | 1.047 | 0 | 1.4548 | 0 | 1.047 | 1.4548 | 45.9114 | 5.0097 | 44.8644
38905.5614 | 1671 | 0 | 38905.5615 | 1986 | 0 | 1848 | 1958 | 102.0147 | 0 | 121.2454 | 0 | 1.0201 | 0 | 1.2125 | 0 | 1.0201 | 1.2125 | 49.7534 | 26.001 | 48.7333
38905.5616 | 1976 | 0 | 38905.5617 | 2111 | 0 | 1864.5 | 1974.5 | 120.6349 | 0 | 128.8767 | 0 | 1.2063 | 0 | 1.2888 | 0 | 1.2063 | 1.2888 | 26.6387 | 18.54 | 25.4323
38905.5618 | 2446 | 0 | 38905.5619 | 2251 | 0 | 1881.5 | 1991.5 | 149.3284 | 0 | 137.4237 | 0 | 1.4933 | 0 | 1.3742 | 0 | 1.4933 | 1.3742 | 2.305 | 11.1675 | 0.8117
38905.562 | 1900 | 1 | 38905.562 | 2265 | 0 | 1898.5 | 2008.5 | 115.9951 | 0.06105 | 138.2784 | 0 | 1.16 | 0.0006105 | 1.3828 | 0 | 1.1593 | 1.3828 | 31.8811 | 10.4804 | 5704.7924
38905.5622 | 1910 | 0 | 38905.5622 | 2284 | 1 | 1915 | 2025 | 116.6056 | 0 | 139.4383 | 0.06105 | 1.1661 | 0 | 1.3944 | 0.0006105 | 1.1661 | 1.3938 | 31.0147 | 9.6093 | 29.8486
38905.5624 | 1903 | 0 | 38905.5624 | 2340 | 1 | 1932 | 2042 | 116.1783 | 0 | 142.8571 | 0.06105 | 1.1618 | 0 | 1.4286 | 0.0006105 | 1.1618 | 1.428 | 31.4966 | 6.985 | 30.3348
38905.5626 | 2001 | 0 | 38905.5626 | 2335 | 1 | 1948.5 | 2058.5 | 122.1612 | 0 | 142.5519 | 0.06105 | 1.2216 | 0 | 1.4255 | 0.0006105 | 1.2216 | 1.4249 | 25.0565 | 7.2142 | 23.8349
38905.5628 | 2196 | 1 | 38905.5628 | 1967 | 1 | 1965.5 | 2075.5 | 134.0659 | 0.06105 | 120.0855 | 0.06105 | 1.3407 | 0.0006105 | 1.2009 | 0.0006105 | 1.34 | 1.2002 | 13.9814 | 27.3314 | 6554.9087
38905.563 | 2346 | 1 | 38905.563 | 1932 | 1 | 1982.5 | 2092.5 | 143.2234 | 0.06105 | 117.9487 | 0.06105 | 1.4322 | 0.0006105 | 1.1795 | 0.0006105 | 1.4316 | 1.1789 | 6.6782 | 29.7689 | 3564.4077
38905.5632 | 2446 | 2 | 38905.5632 | 2453 | 2 | 1999 | 2109 | 149.3284 | 0.1221 | 149.7558 | 0.1221 | 1.4933 | 0.001221 | 1.4976 | 0.001221 | 1.4921 | 1.4963 | 2.4011 | 2.0856 | 55.548
38905.5634 | 1953 | 1 | 38905.5634 | 2097 | 2 | 2016 | 2126 | 119.2308 | 0.06105 | 128.022 | 0.1221 | 1.1923 | 0.0006105 | 1.2802 | 0.001221 | 1.1917 | 1.279 | 28.2189 | 19.4156 | 8916.0128
38905.5636 | 2094 | 3 | 38905.5636 | 2103 | 2 | 2032.5 | 2142.5 | 127.8388 | 0.18315 | 128.3883 | 0.1221 | 1.2784 | 0.0018315 | 1.2839 | 0.001221 | 1.2766 | 1.2827 | 19.6782 | 19.1014 | 2167.1565
38905.5638 | 1926 | 4 | 38905.5638 | 2408 | 4 | 2049.5 | 2159.5 | 117.5824 | 0.2442 | 147.0085 | 0.2442 | 1.1758 | 0.002442 | 1.4701 | 0.002442 | 1.1734 | 1.4676 | 31.6579 | 3.9467 | 543.3102
38905.564 | 2134 | 5 | 38905.564 | 2205 | 7 | 2066.5 | 2176.5 | 130.2808 | 0.30525 | 134.6154 | 0.42735 | 1.3028 | 0.0030525 | 1.3462 | 0.0042735 | 1.2998 | 1.3419 | 17.603 | 13.7789 | 880.1216
38905.5642 | 2193 | 7 | 38905.5642 | 2092 | 7 | 2083 | 2193 | 133.8828 | 0.42735 | 127.7167 | 0.42735 | 1.3388 | 0.0042735 | 1.2772 | 0.0042735 | 1.3346 | 1.2729 | 14.3813 | 20.153 | 724.5352
38905.5644 | 2362 | 9 | 38905.5644 | 2325 | 9 | 2100 | 2210 | 144.2002 | 0.54945 | 141.9414 | 0.54945 | 1.442 | 0.0054945 | 1.4194 | 0.0054945 | 1.4365 | 1.4139 | 6.2592 | 8.1659 | 110.2044
38905.5646 | 2190 | 9 | 38905.5646 | 2357 | 13 | 2116.5 | 2226.5 | 133.6996 | 0.54945 | 143.895 | 0.79365 | 1.337 | 0.0054945 | 1.4389 | 0.0079365 | 1.3315 | 1.431 | 15.3041 | 6.4354 | 203.8149
38905.5648 | 2263 | 13 | 38905.5648 | 2182 | 11 | 2133.5 | 2243.5 | 138.1563 | 0.79365 | 133.2112 | 0.67155 | 1.3816 | 0.0079365 | 1.3321 | 0.0067155 | 1.3736 | 1.3254 | 11.052 | 15.4663 | 233.2524
38905.565 | 1998 | 14 | 38905.565 | 2307 | 17 | 2150.5 | 2260.5 | 121.978 | 0.8547 | 140.8425 | 1.0379 | 1.2198 | 0.008547 | 1.4084 | 0.010379 | 1.2112 | 1.398 | 27.6476 | 8.7673 | 282.3395
38905.5651 | 2156 | 19 | 38905.5652 | 2243 | 11 | 2167 | 2277 | 131.6239 | 1.16 | 136.9353 | 0.67155 | 1.3162 | 0.0116 | 1.3694 | 0.0067155 | 1.3046 | 1.3626 | 17.5107 | 11.9575 | 184.0289
38905.5653 | 1987 | 22 |  | 2311 | 7 | 2183 | 2293 | 121.3065 | 1.3431 | 141.0867 | 0.42735 | 1.2131 | 0.013431 | 1.4109 | 0.0042735 | 1.1996 | 1.4066 | 30.2666 | 8.3906 | 173.6052
38905.5655 | 2287 | 15 | 38905.5655 | 2379 | 2 | 2200.5 | 2310.5 | 139.6215 | 0.91575 | 145.2381 | 0.1221 | 1.3962 | 0.0091575 | 1.4524 | 0.001221 | 1.3871 | 1.4512 | 10.849 | 5.2311 | 66.4073
38905.5657 | 2127 | 0 | 38905.5657 | 2435 | 1 | 2217.5 | 2327.5 | 129.8535 | 0 | 148.6569 | 0.06105 | 1.2985 | 0 | 1.4866 | 0.0006105 | 1.2985 | 1.486 | 17.6483 | 2.8094 | 16.3498
38905.5659 | 2380 | 1 | 38905.5659 | 2432 | 0 | 2234.5 | 2344.5 | 145.2991 | 0.06105 | 148.4737 | 0 | 1.453 | 0.0006105 | 1.4847 | 0 | 1.4524 | 1.4847 | 5.22 | 2.8939 | 341.384
38905.5661 | 1926 | 0 | 38905.5661 | 2183 | 1 | 2251 | 2361 | 117.5824 | 0 | 133.2723 | 0.06105 | 1.1758 | 0 | 1.3327 | 0.0006105 | 1.1758 | 1.3321 | 29.9263 | 14.6829 | 28.7504
38905.5663 | 2307 | 0 | 38905.5663 | 1964 | 0 | 2268 | 2378 | 140.8425 | 0 | 119.9023 | 0 | 1.4084 | 0 | 1.199 | 0 | 1.4084 | 1.199 | 8.469 | 27.4124 | 7.0606
38905.5665 | 2440 | 0 | 38905.5665 | 2486 | 0 | 2284.5 | 2394.5 | 148.9621 | 0 | 151.7705 | 0 | 1.4896 | 0 | 1.5177 | 0 | 1.4896 | 1.5177 | 2.5566 | 0.65889 | 1.0669
38905.5667 | 2417 | 0 | 38905.5667 | 1991 | 0 | 2301.5 | 2411.5 | 147.558 | 0 | 121.5507 | 0 | 1.4756 | 0 | 1.2155 | 0 | 1.4756 | 1.2155 | 3.5325 | 25.6846 | 2.0569
38905.5669 | 2177 | 0 | 38905.5669 | 2022 | 0 | 2318.5 | 2428.5 | 132.906 | 0 | 123.4432 | 0 | 1.3291 | 0 | 1.2344 | 0 | 1.3291 | 1.2344 | 14.9463 | 23.7577 | 13.6172
38905.5671 | 1973 | 0 | 38905.5671 | 1905 | 0 | 2335 | 2445 | 120.4518 | 0 | 116.3004 | 0 | 1.2045 | 0 | 1.163 | 0 | 1.2045 | 1.163 | 26.8312 | 31.3585 | 25.6267

## C1-4
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 151.7326 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38905.5389 | 1 | 0 | 38905.5389 | 1 | 0 | -103.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994 | 0.0006105 | 248438 | #DIV/0! | 1
38905.5391 | 1 | 0 | 38905.5391 | 1 | 0 | -86.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5393 | 1 | 0 | 38905.5393 | 1 | 0 | -69.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5394 | 1 | 0 | 38905.5395 | 1 | 0 | -53 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5396 | 1 | 0 | 38905.5397 | 1 | 0 | -36 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5398 | 1 | 0 | 38905.5398 | 1 | 0 | -19.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.54 | 1 | 0 | 38905.54 | 1 | 0 | -2.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5402 | 1 | 0 | 38905.5402 | 1 | 0 | 14 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5404 | 1 | 0 | 38905.5404 | 1 | 0 | 31 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5406 | 1 | 0 | 38905.5406 | 2 | 0 | 48 | 158 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248438 | 124169 | 248437.9994
38905.5408 | 1 | 0 | 38905.5408 | 1 | 0 | 64.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.541 | 1 | 0 | 38905.541 | 1 | 0 | 81.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5412 | 1 | 0 | 38905.5412 | 1 | 0 | 98 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5414 | 1 | 0 | 38905.5414 | 1 | 0 | 115 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5416 | 1 | 0 | 38905.5416 | 1 | 0 | 132 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5418 | 1 | 0 | 38905.5418 | 1 | 0 | 148.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.542 | 1 | 0 | 38905.542 | 1 | 0 | 165.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5422 | 1 | 0 | 38905.5422 | 1 | 0 | 182.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5424 | 1 | 0 | 38905.5424 | 1 | 0 | 199 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5426 | 1 | 0 | 38905.5426 | 1 | 0 | 216 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5428 | 1 | 0 | 38905.5428 | 1 | 0 | 232.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.543 | 1 | 0 | 38905.543 | 1 | 0 | 249.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5431 | 1 | 0 | 38905.5432 | 1 | 0 | 266 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5433 | 1 | 0 | 38905.5434 | 1 | 0 | 283 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5435 | 1 | 0 | 38905.5435 | 1 | 0 | 299.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5437 | 1 | 0 | 38905.5437 | 1 | 0 | 316.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5439 | 1 | 0 | 38905.5439 | 1 | 0 | 333.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5441 | 1 | 0 | 38905.5441 | 1 | 0 | 350 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5443 | 1 | 0 | 38905.5443 | 1 | 0 | 367 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5445 | 1 | 0 |  | 1 | 0 | 383 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5447 | 1 | 0 | 38905.5447 | 1 | 0 | 400.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5449 | 1 | 0 | 38905.5449 | 1 | 0 | 417.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5451 | 1 | 0 | 38905.5451 | 1 | 0 | 434.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5453 | 1 | 0 | 38905.5453 | 1 | 0 | 451 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5455 | 2 | 0 | 38905.5455 | 1 | 0 | 467.5 | 577.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124169 | 248438 | 124168.9988
38905.5457 | 1 | 0 | 38905.5457 | 1 | 0 | 484.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5459 | 1 | 0 | 38905.5459 | 1 | 0 | 501.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5461 | 1 | 0 | 38905.5461 | 1 | 0 | 518 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5462 | 1 | 0 | 38905.5463 | 1 | 0 | 535 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5464 | 1 | 0 | 38905.5465 | 1 | 0 | 552 | 662 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5466 | 1 | 0 | 38905.5467 | 1 | 0 | 568.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5468 | 1 | 0 | 38905.5469 | 1 | 0 | 585.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.547 | 1 | 0 | 38905.547 | 1 | 0 | 602 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5472 | 1 | 0 | 38905.5472 | 1 | 0 | 619 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5474 | 1 | 0 | 38905.5474 | 1 | 0 | 635.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5476 | 1 | 0 | 38905.5476 | 1 | 0 | 652.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5478 | 1 | 0 | 38905.5478 | 1 | 0 | 669.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.548 | 1 | 0 | 38905.548 | 1 | 0 | 686 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5482 | 1 | 0 | 38905.5482 | 1 | 0 | 703 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5484 | 1 | 0 | 38905.5484 | 1 | 0 | 719.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5486 | 1 | 0 | 38905.5486 | 1 | 0 | 736.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5488 | 1 | 0 | 38905.5488 | 1 | 0 | 753.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.549 | 1 | 0 | 38905.549 | 1 | 0 | 770 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5492 | 1 | 0 | 38905.5492 | 1 | 0 | 787 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5494 | 1 | 0 | 38905.5494 | 1 | 0 | 803.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5496 | 1 | 0 | 38905.5496 | 1 | 0 | 820.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5498 | 1 | 0 | 38905.5498 | 1 | 0 | 837.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5499 | 1 | 0 | 38905.55 | 1 | 0 | 854 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5501 | 1 | 0 | 38905.5502 | 1 | 0 | 871 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5503 | 1 | 0 | 38905.5503 | 1 | 0 | 887.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5505 | 1 | 0 | 38905.5505 | 1 | 0 | 904.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5507 | 1 | 0 | 38905.5507 | 1 | 0 | 921.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5509 | 1 | 0 | 38905.5509 | 1 | 0 | 938 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5511 | 1 | 0 | 38905.5511 | 1 | 0 | 955 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5513 | 1 | 0 | 38905.5513 | 1 | 0 | 971.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5515 | 1 | 0 | 38905.5515 | 1 | 0 | 988.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5517 | 1 | 0 | 38905.5517 | 1 | 0 | 1005.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5519 | 1 | 0 | 38905.5519 | 1 | 0 | 1022 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5521 | 1 | 0 | 38905.5521 | 1 | 0 | 1039 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5523 | 1 | 0 | 38905.5523 | 1 | 0 | 1055.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5525 | 1 | 0 | 38905.5525 | 1 | 0 | 1072.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5527 | 1 | 0 | 38905.5527 | 1 | 0 | 1089.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5529 | 1 | 0 | 38905.5529 | 1 | 0 | 1106 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5531 | 1 | 0 | 38905.5531 | 1 | 0 | 1123 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5533 | 1 | 0 | 38905.5533 | 1 | 0 | 1139.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5534 | 1 | 0 | 38905.5535 | 1 | 0 | 1156.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5536 | 1 | 0 | 38905.5537 | 1 | 0 | 1173.5 | 1283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5538 | 1 | 0 | 38905.5539 | 1 | 0 | 1190 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.554 | 1 | 0 | 38905.5541 | 1 | 0 | 1207 | 1317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5542 | 1 | 0 | 38905.5542 | 1 | 0 | 1223.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5544 | 1 | 0 | 38905.5544 | 1 | 0 | 1240.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38905.5546 | 2 | 0 | 38905.5546 | 1438 | 0 | 1257.5 | 1367.5 | 0.1221 | 0 | 87.79 | 0 | 0.001221 | 0 | 0.8779 | 0 | 0.001221 | 0.8779 | 124169 | 72.8359 | 124168.9988
38905.5548 | 3 | 0 | 38905.5548 | 1619 | 0 | 1274 | 1384 | 0.18315 | 0 | 98.84 | 0 | 0.0018315 | 0 | 0.9884 | 0 | 0.0018315 | 0.9884 | 82746 | 53.5133 | 82745.9982
38905.555 | 4 | 0 | 38905.555 | 1611 | 0 | 1290.5 | 1400.5 | 0.2442 | 0 | 98.3516 | 0 | 0.002442 | 0 | 0.98352 | 0 | 0.002442 | 0.98352 | 62034.5 | 54.2756 | 62034.4976
38905.5552 | 3 | 0 | 38905.5552 | 1848 | 0 | 1307.5 | 1417.5 | 0.18315 | 0 | 112.8205 | 0 | 0.0018315 | 0 | 1.1282 | 0 | 0.0018315 | 1.1282 | 82746 | 34.4903 | 82745.9982
38905.5554 | 3 | 0 | 38905.5554 | 1941 | 0 | 1324.5 | 1434.5 | 0.18315 | 0 | 118.4982 | 0 | 0.0018315 | 0 | 1.185 | 0 | 0.0018315 | 1.185 | 82746 | 28.0464 | 82745.9982
38905.5556 | 5 | 0 | 38905.5556 | 2381 | 0 | 1341.5 | 1451.5 | 0.30525 | 0 | 145.3602 | 0 | 0.0030525 | 0 | 1.4536 | 0 | 0.0030525 | 1.4536 | 49607.6 | 4.3839 | 49607.5969
38905.5558 | 6 | 0 | 38905.5558 | 2148 | 0 | 1358 | 1468 | 0.3663 | 0 | 131.1355 | 0 | 0.003663 | 0 | 1.3114 | 0 | 0.003663 | 1.3114 | 41323 | 15.7067 | 41322.9963
38905.556 | 6 | 0 | 38905.556 | 1852 | 0 | 1375 | 1485 | 0.3663 | 0 | 113.0647 | 0 | 0.003663 | 0 | 1.1306 | 0 | 0.003663 | 1.1306 | 41323 | 34.1998 | 41322.9963
38905.5562 | 6 | 0 | 38905.5562 | 1892 | 0 | 1391.5 | 1501.5 | 0.3663 | 0 | 115.5067 | 0 | 0.003663 | 0 | 1.1551 | 0 | 0.003663 | 1.1551 | 41323 | 31.3626 | 41322.9963
38905.5564 | 6 | 0 | 38905.5564 | 2405 | 0 | 1408.5 | 1518.5 | 0.3663 | 0 | 146.8254 | 0 | 0.003663 | 0 | 1.4683 | 0 | 0.003663 | 1.4683 | 41323 | 3.3422 | 41322.9963
38905.5566 | 6 | 0 | 38905.5566 | 2360 | 0 | 1425 | 1535 | 0.3663 | 0 | 144.0781 | 0 | 0.003663 | 0 | 1.4408 | 0 | 0.003663 | 1.4408 | 41323 | 5.3127 | 41322.9963
38905.5567 | 6 | 1 | 38905.5568 | 2178 | 0 | 1442 | 1552 | 0.3663 | 0.06105 | 132.967 | 0 | 0.003663 | 0.0006105 | 1.3297 | 0 | 0.0030525 | 1.3297 | 118875.655 | 34.3135 | 63315.9165
38905.5569 | 6 | 0 | 38905.557 | 2111 | 0 | 1458.5 | 1568.5 | 0.3663 | 0 | 128.8767 | 0 | 0.003663 | 0 | 1.2888 | 0 | 0.003663 | 1.2888 | 41323 | 17.7347 | 41322.9963
38905.5571 | 6 | 0 | 38905.5572 | 2141 | 0 | 1475.5 | 1585.5 | 0.3663 | 0 | 130.7082 | 0 | 0.003663 | 0 | 1.3071 | 0 | 0.003663 | 1.3071 | 41323 | 16.085 | 41322.9963
38905.5573 | 6 | 0 | 38905.5573 | 1881 | 0 | 1492.5 | 1602.5 | 0.3663 | 0 | 114.8352 | 0 | 0.003663 | 0 | 1.1484 | 0 | 0.003663 | 1.1484 | 41323 | 32.1308 | 41322.9963
38905.5575 | 5 | 0 | 38905.5575 | 1905 | 0 | 1509 | 1619 | 0.30525 | 0 | 116.3004 | 0 | 0.0030525 | 0 | 1.163 | 0 | 0.0030525 | 1.163 | 49607.6 | 30.4661 | 49607.5969
38905.5577 | 5 | 0 | 38905.5577 | 2358 | 0 | 1526 | 1636 | 0.30525 | 0 | 143.956 | 0 | 0.0030525 | 0 | 1.4396 | 0 | 0.0030525 | 1.4396 | 49607.6 | 5.402 | 49607.5969
38905.5579 | 5 | 0 | 38905.5579 | 2354 | 0 | 1543 | 1653 | 0.30525 | 0 | 143.7118 | 0 | 0.0030525 | 0 | 1.4371 | 0 | 0.0030525 | 1.4371 | 49607.6 | 5.5811 | 49607.5969
38905.5581 | 5 | 0 | 38905.5581 | 2347 | 0 | 1559.5 | 1669.5 | 0.30525 | 0 | 143.2845 | 0 | 0.0030525 | 0 | 1.4328 | 0 | 0.0030525 | 1.4328 | 49607.6 | 5.896 | 49607.5969
38905.5583 | 5 | 0 | 38905.5583 | 1861 | 0 | 1576.5 | 1686.5 | 0.30525 | 0 | 113.6142 | 0 | 0.0030525 | 0 | 1.1361 | 0 | 0.0030525 | 1.1361 | 49607.6 | 33.5508 | 49607.5969
38905.5585 | 6 | 0 | 38905.5585 | 2055 | 0 | 1593 | 1703 | 0.3663 | 0 | 125.4579 | 0 | 0.003663 | 0 | 1.2546 | 0 | 0.003663 | 1.2546 | 41323 | 20.9431 | 41322.9963
38905.5587 | 6 | 0 | 38905.5587 | 2408 | 0 | 1610 | 1720 | 0.3663 | 0 | 147.0085 | 0 | 0.003663 | 0 | 1.4701 | 0 | 0.003663 | 1.4701 | 41323 | 3.2135 | 41322.9963
38905.5589 | 6 | 0 | 38905.5589 | 2261 | 0 | 1627 | 1737 | 0.3663 | 0 | 138.0342 | 0 | 0.003663 | 0 | 1.3803 | 0 | 0.003663 | 1.3803 | 41323 | 9.9239 | 41322.9963
38905.5591 | 6 | 0 | 38905.5591 | 2193 | 0 | 1643.5 | 1753.5 | 0.3663 | 0 | 133.8828 | 0 | 0.003663 | 0 | 1.3388 | 0 | 0.003663 | 1.3388 | 41323 | 13.3324 | 41322.9963
38905.5593 | 2317 | 14 | 38905.5593 | 1835 | 14 | 1660.5 | 1770.5 | 141.453 | 0.8547 | 112.0269 | 0.8547 | 1.4145 | 0.008547 | 1.1203 | 0.008547 | 1.406 | 1.1117 | 7.4246 | 39.841 | 314.1658
38905.5595 | 2360 | 31 | 38905.5595 | 2229 | 31 | 1677.5 | 1787.5 | 144.0781 | 1.8926 | 136.0806 | 1.8926 | 1.4408 | 0.018926 | 1.3608 | 0.018926 | 1.4219 | 1.3419 | 5.8952 | 15.3324 | 40.474
38905.5597 | 2131 | 24 | 38905.5597 | 2304 | 27 | 1694 | 1804 | 130.0977 | 1.4652 | 140.6593 | 1.6484 | 1.301 | 0.014652 | 1.4066 | 0.016484 | 1.2863 | 1.3901 | 19.4277 | 8.4835 | 107.6504
38905.5599 | 2348 | 2 | 38905.5599 | 2135 | 2 | 1710.5 | 1820.5 | 143.3455 | 0.1221 | 130.3419 | 0.1221 | 1.4335 | 0.001221 | 1.3034 | 0.001221 | 1.4322 | 1.3022 | 5.886 | 16.6925 | 968.2866
38905.5601 | 2111 | 1 | 38905.5601 | 2110 | 1 | 1727.5 | 1837.5 | 128.8767 | 0.06105 | 128.8156 | 0.06105 | 1.2888 | 0.0006105 | 1.2882 | 0.0006105 | 1.2882 | 1.2875 | 17.7904 | 17.8465 | 5654.4176
38905.5603 | 1893 | 1 | 38905.5603 | 2107 | 1 | 1744.5 | 1854.5 | 115.5678 | 0.06105 | 128.6325 | 0.06105 | 1.1557 | 0.0006105 | 1.2863 | 0.0006105 | 1.1551 | 1.2857 | 31.402 | 17.994 | 9018.4899
38905.5604 | 1951 | 1 | 38905.5605 | 1936 | 1 | 1761 | 1871 | 119.1087 | 0.06105 | 118.1929 | 0.06105 | 1.1911 | 0.0006105 | 1.1819 | 0.0006105 | 1.1905 | 1.1813 | 27.4536 | 28.4453 | 11812.1448
38905.5606 | 2006 | 1 | 38905.5607 | 2125 | 1 | 1778 | 1888 | 122.4664 | 0.06105 | 129.7314 | 0.06105 | 1.2247 | 0.0006105 | 1.2973 | 0.0006105 | 1.2241 | 1.2967 | 23.9796 | 17.0004 | 6950.9678
38905.5608 | 1945 | 1 | 38905.5608 | 2205 | 1 | 1794.5 | 1904.5 | 118.7424 | 0.06105 | 134.6154 | 0.06105 | 1.1874 | 0.0006105 | 1.3462 | 0.0006105 | 1.1868 | 1.3455 | 27.91 | 12.7421 | 6096.0796
38905.561 | 2348 | 1 | 38905.561 | 2177 | 1 | 1811.5 | 1921.5 | 143.3455 | 0.06105 | 132.906 | 0.06105 | 1.4335 | 0.0006105 | 1.3291 | 0.0006105 | 1.4328 | 1.3284 | 5.8709 | 14.2837 | 1704.5379
38905.5612 | 1891 | 1 | 38905.5612 | 1953 | 0 | 1828.5 | 1938.5 | 115.4457 | 0.06105 | 119.2308 | 0 | 1.1545 | 0.0006105 | 1.1923 | 0 | 1.1538 | 1.1923 | 31.5098 | 27.2596 | 12710.4766
38905.5614 | 2026 | 1 | 38905.5614 | 2371 | 17 | 1845.5 | 1955.5 | 123.6874 | 0.06105 | 144.7497 | 1.0379 | 1.2369 | 0.0006105 | 1.4475 | 0.010379 | 1.2363 | 1.4371 | 22.9109 | 5.0171 | 2189.8735
38905.5616 | 2280 | 23 | 38905.5616 | 1982 | 0 | 1862 | 1972 | 139.1941 | 1.4042 | 121.0012 | 0 | 1.3919 | 0.014042 | 1.21 | 0 | 1.3779 | 1.21 | 9.4801 | 25.3976 | 160.6026
38905.5618 | 2465 | 1 | 38905.5618 | 2337 | 0 | 1878.5 | 1988.5 | 150.4884 | 0.06105 | 142.674 | 0 | 1.5049 | 0.0006105 | 1.4267 | 0 | 1.5043 | 1.4267 | 0.83243 | 6.3492 | 115.7008
38905.562 | 2209 | 1 | 38905.562 | 1909 | 1 | 1895.5 | 2005.5 | 134.8596 | 0.06105 | 116.5446 | 0.06105 | 1.3486 | 0.0006105 | 1.1654 | 0.0006105 | 1.348 | 1.1648 | 12.5359 | 30.3354 | 6409.4386
38905.5622 | 2112 | 0 | 38905.5622 | 2038 | 0 | 1912.5 | 2022.5 | 128.9377 | 0 | 124.42 | 0 | 1.2894 | 0 | 1.2442 | 0 | 1.2894 | 1.2442 | 17.679 | 21.9519 | 16.3896
38905.5624 | 2457 | 1 | 38905.5624 | 1895 | 0 | 1929 | 2039 | 150 | 0.06105 | 115.6899 | 0 | 1.5 | 0.0006105 | 1.1569 | 0 | 1.4994 | 1.1569 | 1.157 | 31.1546 | 650.3876
38905.5626 | 2260 | 1 | 38905.5626 | 1947 | 0 | 1946 | 2056 | 137.9731 | 0.06105 | 118.8645 | 0 | 1.3797 | 0.0006105 | 1.1886 | 0 | 1.3791 | 1.1886 | 9.993 | 27.6518 | 4860.4923
38905.5628 | 1890 | 1 | 38905.5628 | 1886 | 1 | 1962.5 | 2072.5 | 115.3846 | 0.06105 | 115.1404 | 0.06105 | 1.1538 | 0.0006105 | 1.1514 | 0.0006105 | 1.1532 | 1.1508 | 31.5707 | 31.8509 | 14358.2818
38905.563 | 2330 | 1 | 38905.563 | 2377 | 1 | 1979.5 | 2089.5 | 142.2466 | 0.06105 | 145.116 | 0.06105 | 1.4225 | 0.0006105 | 1.4512 | 0.0006105 | 1.4219 | 1.4505 | 6.7345 | 4.5901 | 677.5255
38905.5632 | 2237 | 2 | 38905.5632 | 2390 | 2 | 1996.5 | 2106.5 | 136.569 | 0.1221 | 145.9096 | 0.1221 | 1.3657 | 0.001221 | 1.4591 | 0.001221 | 1.3645 | 1.4579 | 11.366 | 4.0238 | 476.5164
38905.5634 | 2329 | 2 | 38905.5634 | 1912 | 2 | 2013 | 2123 | 142.1856 | 0.1221 | 116.7277 | 0.1221 | 1.4219 | 0.001221 | 1.1673 | 0.001221 | 1.4206 | 1.1661 | 6.7392 | 30.4937 | 1803.7717
38905.5636 | 2011 | 3 | 38905.5636 | 1998 | 2 | 2030 | 2140 | 122.7717 | 0.18315 | 121.978 | 0.1221 | 1.2277 | 0.0018315 | 1.2198 | 0.001221 | 1.2259 | 1.2186 | 23.7693 | 24.5212 | 3094.2001
38905.5638 | 2315 | 5 | 38905.5638 | 2327 | 5 | 2046.5 | 2156.5 | 141.3309 | 0.30525 | 142.0635 | 0.30525 | 1.4133 | 0.0030525 | 1.4206 | 0.0030525 | 1.4103 | 1.4176 | 7.6104 | 7.0195 | 216.947
38905.5639 | 2022 | 5 | 38905.564 | 2162 | 5 | 2063.5 | 2173.5 | 123.4432 | 0.30525 | 131.9902 | 0.30525 | 1.2344 | 0.0030525 | 1.3199 | 0.0030525 | 1.2314 | 1.3168 | 23.3561 | 15.1424 | 1205.6331
38905.5641 | 1909 | 7 | 38905.5642 | 1867 | 6 | 2080.5 | 2190.5 | 116.5446 | 0.42735 | 113.9805 | 0.3663 | 1.1654 | 0.0042735 | 1.1398 | 0.003663 | 1.1612 | 1.1361 | 30.6397 | 33.5817 | 2044.8443
38905.5643 | 2418 | 9 | 38905.5644 | 1915 | 8 | 2097 | 2207 | 147.619 | 0.54945 | 116.9109 | 0.4884 | 1.4762 | 0.0054945 | 1.1691 | 0.004884 | 1.4707 | 1.1642 | 2.8271 | 35.1214 | 168.6046
38905.5645 | 2006 | 8 | 38905.5645 | 2016 | 10 | 2114 | 2224 | 122.4664 | 0.4884 | 123.0769 | 0.6105 | 1.2247 | 0.004884 | 1.2308 | 0.006105 | 1.2198 | 1.2247 | 24.402 | 23.8868 | 1136.0929
38905.5647 | 2117 | 11 | 38905.5647 | 2099 | 12 | 2130.5 | 2240.5 | 129.243 | 0.67155 | 128.1441 | 0.7326 | 1.2924 | 0.0067155 | 1.2814 | 0.007326 | 1.2857 | 1.2741 | 17.9831 | 19.1252 | 521.6019
38905.5649 | 2407 | 13 | 38905.5649 | 1999 | 13 | 2147.5 | 2257.5 | 146.9475 | 0.79365 | 122.0391 | 0.79365 | 1.4695 | 0.0079365 | 1.2204 | 0.0079365 | 1.4615 | 1.2125 | 3.3334 | 30.4748 | 117.4668
38905.5651 | 1913 | 16 | 38905.5651 | 1847 | 17 | 2164.5 | 2274.5 | 116.7888 | 0.9768 | 112.7595 | 1.0379 | 1.1679 | 0.009768 | 1.1276 | 0.010379 | 1.1581 | 1.1172 | 30.8975 | 35.9655 | 919.8326
38905.5653 | 2396 | 5 | 38905.5653 | 2053 | 24 | 2181 | 2291 | 146.2759 | 0.30525 | 125.3358 | 1.4652 | 1.4628 | 0.0030525 | 1.2534 | 0.014652 | 1.4597 | 1.2387 | 3.7635 | 31.0775 | 400.1171
38905.5655 | 2216 | 31 | 38905.5655 | 2120 | 29 | 2198 | 2308 | 135.2869 | 1.8926 | 129.4261 | 1.7705 | 1.3529 | 0.018926 | 1.2943 | 0.017705 | 1.3339 | 1.2766 | 13.2955 | 19.509 | 125.5284
38905.5657 | 1963 | 0 | 38905.5657 | 2362 | 0 | 2214.5 | 2324.5 | 119.8413 | 0 | 144.2002 | 0 | 1.1984 | 0 | 1.442 | 0 | 1.1984 | 1.442 | 26.6113 | 5.2235 | 25.4129
38905.5659 | 1909 | 0 | 38905.5659 | 1912 | 0 | 2231.5 | 2341.5 | 116.5446 | 0 | 116.7277 | 0 | 1.1654 | 0 | 1.1673 | 0 | 1.1654 | 1.1673 | 30.1928 | 29.9885 | 29.0273
38905.5661 | 2469 | 1 | 38905.5661 | 2355 | 1 | 2248.5 | 2358.5 | 150.7326 | 0.06105 | 143.7729 | 0.06105 | 1.5073 | 0.0006105 | 1.4377 | 0.0006105 | 1.5067 | 1.4371 | 0.66827 | 5.9146 | 85.8872
38905.5663 | 2104 | 0 | 38905.5663 | 2468 | 0 | 2265 | 2375 | 128.4493 | 0 | 150.6716 | 0 | 1.2845 | 0 | 1.5067 | 0 | 1.2845 | 1.5067 | 18.1264 | 0.70421 | 16.8419
38905.5665 | 2208 | 1 | 38905.5665 | 2409 | 1 | 2282 | 2392 | 134.7985 | 0.06105 | 147.0696 | 0.06105 | 1.348 | 0.0006105 | 1.4707 | 0.0006105 | 1.3474 | 1.4701 | 12.7497 | 3.1823 | 852.3962
38905.5667 | 1938 | 0 | 38905.5667 | 2434 | 1 | 2298.5 | 2408.5 | 118.315 | 0 | 148.5958 | 0.06105 | 1.1832 | 0 | 1.486 | 0.0006105 | 1.1832 | 1.4853 | 28.2446 | 2.1529 | 27.0614
38905.5669 | 2048 | 0 | 38905.5669 | 2240 | 0 | 2315.5 | 2425.5 | 125.0305 | 0 | 136.7521 | 0 | 1.2503 | 0 | 1.3675 | 0 | 1.2503 | 1.3675 | 21.3564 | 10.9545 | 20.1061
38905.5671 | 2441 | 1 | 38905.5671 | 2340 | 0 | 2332.5 | 2442.5 | 149.0232 | 0.06105 | 142.8571 | 0 | 1.4902 | 0.0006105 | 1.4286 | 0 | 1.4896 | 1.4286 | 1.8309 | 6.2128 | 253.7473

## C1-3
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 152.4042 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38905.5388 | 1 | 0 | 38905.5389 | 1 | 0 | -106 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.539 | 1 | 0 | 38905.539 | 1 | 0 | -89.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5392 | 1 | 0 | 38905.5392 | 1 | 0 | -72.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5394 | 1 | 0 | 38905.5394 | 1 | 0 | -55.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5396 | 1 | 0 | 38905.5396 | 1 | 0 | -39 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5398 | 1 | 0 | 38905.5398 | 1 | 0 | -22 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.54 | 1 | 0 | 38905.54 | 1 | 0 | -5.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5402 | 1 | 0 | 38905.5402 | 1 | 0 | 11.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5404 | 1 | 0 | 38905.5404 | 1 | 0 | 28.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5406 | 1 | 0 | 38905.5406 | 1 | 0 | 45 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5408 | 1 | 0 | 38905.5408 | 1 | 0 | 61.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.541 | 1 | 0 | 38905.541 | 1 | 0 | 78.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5412 | 1 | 0 | 38905.5412 | 1 | 0 | 95.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5414 | 1 | 0 | 38905.5414 | 1 | 0 | 112.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5416 | 1 | 0 | 38905.5416 | 1 | 0 | 129 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5417 | 1 | 0 | 38905.5418 | 1 | 0 | 146 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5419 | 1 | 0 | 38905.542 | 1 | 0 | 162.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5421 | 1 | 0 | 38905.5422 | 1 | 0 | 179.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5423 | 1 | 0 | 38905.5423 | 1 | 0 | 196 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5425 | 1 | 0 | 38905.5425 | 1 | 0 | 213 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5427 | 1 | 0 | 38905.5427 | 1 | 0 | 229.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5429 | 1 | 0 | 38905.5429 | 1 | 0 | 246.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5431 | 1 | 0 | 38905.5431 | 1 | 0 | 263.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5433 | 1 | 0 | 38905.5433 | 1 | 0 | 280 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5435 | 1 | 0 | 38905.5435 | 1 | 0 | 297 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5437 | 1 | 0 | 38905.5437 | 1 | 0 | 313.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5439 | 1 | 0 | 38905.5439 | 1 | 0 | 330.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5441 | 1 | 0 | 38905.5441 | 1 | 0 | 347.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5443 | 1 | 0 | 38905.5443 | 1 | 0 | 364 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5445 | 1 | 0 | 38905.5445 | 1 | 0 | 381 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5447 | 1 | 0 | 38905.5447 | 1 | 0 | 397.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5449 | 1 | 0 | 38905.5449 | 1 | 0 | 414.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5451 | 1 | 0 | 38905.5451 | 1 | 0 | 431.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5452 | 1 | 0 | 38905.5453 | 1 | 0 | 448 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5454 | 1 | 0 | 38905.5455 | 1 | 0 | 465 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5456 | 1 | 0 | 38905.5456 | 1 | 0 | 481.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5458 | 1 | 0 | 38905.5458 | 1 | 0 | 498.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.546 | 1 | 0 | 38905.546 | 1 | 0 | 515.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5462 | 1 | 0 | 38905.5462 | 1 | 0 | 532 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5464 | 1 | 0 | 38905.5464 | 1 | 0 | 549 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5466 | 1 | 0 | 38905.5466 | 1 | 0 | 565.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5468 | 1 | 0 | 38905.5468 | 1 | 0 | 582.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.547 | 1 | 0 | 38905.547 | 1 | 0 | 599.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5472 | 1 | 0 | 38905.5472 | 1 | 0 | 616.5 | 726.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5474 | 1 | 0 | 38905.5474 | 1 | 0 | 633 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5476 | 1 | 0 | 38905.5476 | 1 | 0 | 649.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5478 | 1 | 0 | 38905.5478 | 1 | 0 | 666.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.548 | 1 | 0 | 38905.548 | 1 | 0 | 683.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5482 | 1 | 0 | 38905.5482 | 1 | 0 | 700 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5484 | 1 | 0 | 38905.5484 | 1 | 0 | 717 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5486 | 1 | 0 | 38905.5486 | 1 | 0 | 733.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5488 | 1 | 0 | 38905.5488 | 1 | 0 | 750.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5489 | 1 | 0 | 38905.549 | 1 | 0 | 767.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5491 | 1 | 0 | 38905.5492 | 1 | 0 | 784 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5493 | 1 | 0 | 38905.5494 | 1 | 0 | 801 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5495 | 1 | 0 | 38905.5495 | 1 | 0 | 817.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5497 | 1 | 0 | 38905.5497 | 1 | 0 | 834.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5499 | 1 | 0 | 38905.5499 | 1 | 0 | 851.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5501 | 1 | 0 | 38905.5501 | 1 | 0 | 868 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5503 | 1 | 0 | 38905.5503 | 1 | 0 | 885 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5505 | 1 | 0 | 38905.5505 | 1 | 0 | 901.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5507 | 1 | 0 | 38905.5507 | 1 | 0 | 918.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5509 | 1 | 0 | 38905.5509 | 1 | 0 | 935.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5511 | 1 | 0 | 38905.5511 | 1 | 0 | 952 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5513 | 1 | 1 | 38905.5513 | 1 | 0 | 969 | 1079 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 622692134.44 | 249538 | 249338.0801
38905.5515 | 1 | 0 | 38905.5515 | 1 | 0 | 985.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5517 | 1 | 0 | 38905.5517 | 1 | 0 | 1002.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5519 | 1 | 0 | 38905.5519 | 1 | 0 | 1019.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.552 | 1 | 0 | 38905.5521 | 1 | 0 | 1036 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5522 | 1 | 0 | 38905.5523 | 1 | 0 | 1053 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5524 | 1 | 0 | 38905.5525 | 1 | 0 | 1069.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5526 | 1 | 0 | 38905.5527 | 1 | 0 | 1086.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5528 | 1 | 0 | 38905.5528 | 1 | 0 | 1103.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.553 | 1 | 0 | 38905.553 | 1 | 0 | 1120 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5532 | 1 | 0 | 38905.5532 | 1 | 0 | 1137 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5534 | 1 | 0 | 38905.5534 | 1 | 0 | 1153.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5536 | 1 | 0 | 38905.5536 | 1 | 0 | 1170.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5538 | 1 | 0 | 38905.5538 | 1 | 0 | 1187.5 | 1297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.554 | 1 | 0 | 38905.554 | 1 | 0 | 1204 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5542 | 1 | 0 | 38905.5542 | 1 | 0 | 1221 | 1331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5544 | 1 | 0 | 38905.5544 | 1 | 0 | 1237.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38905.5546 | 3 | 0 | 38905.5546 | 3 | 0 | 1254.5 | 1364.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 83112.6667 | 83112.6667 | 83112.6648
38905.5548 | 4 | 0 | 38905.5548 | 3 | 0 | 1271.5 | 1381.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62309.5 | 83112.6667 | 62309.4976
38905.555 | 6 | 0 | 38905.555 | 4 | 0 | 1288 | 1398 | 0.3663 | 0 | 0.2442 | 0 | 0.003663 | 0 | 0.002442 | 0 | 0.003663 | 0.002442 | 41506.3333 | 62309.5 | 41506.3297
38905.5552 | 6 | 0 | 38905.5552 | 4 | 0 | 1305 | 1415 | 0.3663 | 0 | 0.2442 | 0 | 0.003663 | 0 | 0.002442 | 0 | 0.003663 | 0.002442 | 41506.3333 | 62309.5 | 41506.3297
38905.5554 | 6 | 0 | 38905.5554 | 5 | 0 | 1321.5 | 1431.5 | 0.3663 | 0 | 0.30525 | 0 | 0.003663 | 0 | 0.0030525 | 0 | 0.003663 | 0.0030525 | 41506.3333 | 49827.6 | 41506.3297
38905.5556 | 8 | 0 | 38905.5556 | 6 | 0 | 1338.5 | 1448.5 | 0.4884 | 0 | 0.3663 | 0 | 0.004884 | 0 | 0.003663 | 0 | 0.004884 | 0.003663 | 31104.75 | 41506.3333 | 31104.7451
38905.5558 | 8 | 0 | 38905.5558 | 7 | 0 | 1355.5 | 1465.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5559 | 8 | 0 | 38905.556 | 7 | 0 | 1372 | 1482 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5561 | 7 | 0 | 38905.5562 | 7 | 0 | 1389 | 1499 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5563 | 8 | 0 | 38905.5563 | 7 | 0 | 1405.5 | 1515.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5565 | 8 | 0 | 38905.5565 | 7 | 0 | 1422.5 | 1532.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5567 | 7 | 0 | 38905.5567 | 7 | 0 | 1439.5 | 1549.5 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5569 | 8 | 0 | 38905.5569 | 7 | 0 | 1456 | 1566 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5571 | 8 | 0 | 38905.5571 | 7 | 0 | 1472.5 | 1582.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5573 | 8 | 0 | 38905.5573 | 7 | 0 | 1489.5 | 1599.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5575 | 7 | 0 | 38905.5575 | 7 | 0 | 1506.5 | 1616.5 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5577 | 8 | 0 | 38905.5577 | 7 | 0 | 1523 | 1633 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5579 | 7 | 0 | 38905.5579 | 6 | 0 | 1540 | 1650 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 35562.5714 | 41506.3333 | 35562.5672
38905.5581 | 8 | 0 | 38905.5581 | 7 | 0 | 1557 | 1667 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5583 | 7 | 0 | 38905.5583 | 7 | 0 | 1573.5 | 1683.5 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5585 | 7 | 0 | 38905.5585 | 7 | 0 | 1590.5 | 1700.5 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5587 | 8 | 0 | 38905.5587 | 7 | 0 | 1607.5 | 1717.5 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31104.75 | 35562.5714 | 31104.7451
38905.5589 | 7 | 0 | 38905.5589 | 6 | 0 | 1624 | 1734 | 0.42735 | 0 | 0.3663 | 0 | 0.0042735 | 0 | 0.003663 | 0 | 0.0042735 | 0.003663 | 35562.5714 | 41506.3333 | 35562.5672
38905.5591 | 7 | 0 | 38905.5591 | 7 | 0 | 1641 | 1751 | 0.42735 | 0 | 0.42735 | 0 | 0.0042735 | 0 | 0.0042735 | 0 | 0.0042735 | 0.0042735 | 35562.5714 | 35562.5714 | 35562.5672
38905.5592 | 2304 | 0 | 38905.5593 | 2386 | 11 | 1657.5 | 1767.5 | 140.6593 | 0 | 145.6654 | 0.67155 | 1.4066 | 0 | 1.4567 | 0.0067155 | 1.4066 | 1.4499 | 8.3498 | 5.1107 | 6.9432
38905.5594 | 1999 | 25 | 38905.5595 | 2087 | 28 | 1674.5 | 1784.5 | 122.0391 | 1.5263 | 127.4115 | 1.7094 | 1.2204 | 0.015263 | 1.2741 | 0.017094 | 1.2051 | 1.257 | 26.8182 | 20.9445 | 327.2168
38905.5596 | 1874 | 19 | 38905.5597 | 2262 | 31 | 1691 | 1801 | 114.4078 | 1.16 | 138.0952 | 1.8926 | 1.1441 | 0.0116 | 1.381 | 0.018926 | 1.1325 | 1.362 | 37.0259 | 10.9152 | 312.5209
38905.5598 | 2338 | 4 | 38905.5598 | 2282 | 2 | 1708 | 1818 | 142.735 | 0.2442 | 139.3162 | 0.1221 | 1.4274 | 0.002442 | 1.3932 | 0.001221 | 1.4249 | 1.3919 | 6.9101 | 9.5235 | 335.5996
38905.56 | 1883 | 1 | 38905.56 | 2051 | 1 | 1724.5 | 1834.5 | 114.9573 | 0.06105 | 125.2137 | 0.06105 | 1.1496 | 0.0006105 | 1.2521 | 0.0006105 | 1.149 | 1.2515 | 32.6717 | 21.7583 | 10943.2933
38905.5602 | 2378 | 2 | 38905.5602 | 2135 | 1 | 1741.5 | 1851.5 | 145.177 | 0.1221 | 130.3419 | 0.06105 | 1.4518 | 0.001221 | 1.3034 | 0.0006105 | 1.4505 | 1.3028 | 5.007 | 17.0944 | 849.5045
38905.5604 | 2090 | 2 | 38905.5604 | 2330 | 2 | 1758.5 | 1868.5 | 127.5946 | 0.1221 | 142.2466 | 0.1221 | 1.2759 | 0.001221 | 1.4225 | 0.001221 | 1.2747 | 1.4212 | 19.7259 | 7.1782 | 1354.1509
38905.5606 | 1944 | 1 | 38905.5606 | 2446 | 1 | 1775.5 | 1885.5 | 118.6813 | 0.06105 | 149.3284 | 0.06105 | 1.1868 | 0.0006105 | 1.4933 | 0.0006105 | 1.1862 | 1.4927 | 29.1565 | 2.0634 | 1114.7303
38905.5608 | 2427 | 1 | 38905.5608 | 1992 | 1 | 1792 | 1902 | 148.1685 | 0.06105 | 121.6117 | 0.06105 | 1.4817 | 0.0006105 | 1.2161 | 0.0006105 | 1.4811 | 1.2155 | 2.8644 | 25.7851 | 1401.7451
38905.561 | 2425 | 1 | 38905.561 | 2400 | 1 | 1808.5 | 1918.5 | 148.0464 | 0.06105 | 146.5201 | 0.06105 | 1.4805 | 0.0006105 | 1.4652 | 0.0006105 | 1.4799 | 1.4646 | 2.9748 | 4.0746 | 275.5432
38905.5612 | 2008 | 0 | 38905.5612 | 2093 | 0 | 1825.5 | 1935.5 | 122.5885 | 0 | 127.7778 | 0 | 1.2259 | 0 | 1.2778 | 0 | 1.2259 | 1.2778 | 24.3217 | 19.2728 | 23.0958
38905.5614 | 2181 | 0 | 38905.5614 | 2191 | 1 | 1842.5 | 1952.5 | 133.1502 | 0 | 133.7607 | 0.06105 | 1.3315 | 0 | 1.3376 | 0.0006105 | 1.3315 | 1.337 | 14.4603 | 13.99 | 13.1288
38905.5616 | 2031 | 18 | 38905.5616 | 2282 | 20 | 1859 | 1969 | 123.9927 | 1.0989 | 139.3162 | 1.221 | 1.2399 | 0.010989 | 1.3932 | 0.01221 | 1.2289 | 1.381 | 25.4351 | 9.8188 | 222.2208
38905.5618 | 2088 | 19 | 38905.5618 | 2024 | 22 | 1876 | 1986 | 127.4725 | 1.16 | 123.5653 | 1.3431 | 1.2747 | 0.0116 | 1.2357 | 0.013431 | 1.2631 | 1.2222 | 20.4928 | 24.9324 | 408.9862
38905.562 | 2069 | 0 | 38905.562 | 2329 | 1 | 1892.5 | 2002.5 | 126.3126 | 0 | 142.1856 | 0.06105 | 1.2631 | 0 | 1.4219 | 0.0006105 | 1.2631 | 1.4212 | 20.6564 | 7.2328 | 19.3932
38905.5622 | 1992 | 0 | 38905.5622 | 1971 | 0 | 1909.5 | 2019.5 | 121.6117 | 0 | 120.3297 | 0 | 1.2161 | 0 | 1.2033 | 0 | 1.2161 | 1.2033 | 25.3203 | 26.6555 | 24.1042
38905.5624 | 2223 | 0 | 38905.5624 | 2390 | 1 | 1926.5 | 2036.5 | 135.7143 | 0 | 145.9096 | 0.06105 | 1.3571 | 0 | 1.4591 | 0.0006105 | 1.3571 | 1.4585 | 12.2978 | 4.4948 | 10.9407
38905.5625 | 1987 | 0 | 38905.5626 | 1902 | 1 | 1943 | 2053 | 121.3065 | 0 | 116.1172 | 0.06105 | 1.2131 | 0 | 1.1612 | 0.0006105 | 1.2131 | 1.1606 | 25.6356 | 31.3193 | 24.4226
38905.5627 | 2428 | 1 | 38905.5628 | 1950 | 1 | 1960 | 2070 | 148.2295 | 0.06105 | 119.0476 | 0.06105 | 1.4823 | 0.0006105 | 1.1905 | 0.0006105 | 1.4817 | 1.1899 | 2.8215 | 28.5531 | 1496.5856
38905.5629 | 2346 | 1 | 38905.563 | 2229 | 1 | 1976.5 | 2086.5 | 143.2234 | 0.06105 | 136.0806 | 0.06105 | 1.4322 | 0.0006105 | 1.3608 | 0.0006105 | 1.4316 | 1.3602 | 6.4355 | 12.0852 | 1610.6364
38905.5631 | 1920 | 1 | 38905.5631 | 1924 | 1 | 1993.5 | 2103.5 | 117.2161 | 0.06105 | 117.4603 | 0.06105 | 1.1722 | 0.0006105 | 1.1746 | 0.0006105 | 1.1716 | 1.174 | 30.088 | 29.8165 | 13215.4313
38905.5633 | 2117 | 2 | 38905.5633 | 2444 | 2 | 2010.5 | 2120.5 | 129.243 | 0.1221 | 149.2063 | 0.1221 | 1.2924 | 0.001221 | 1.4921 | 0.001221 | 1.2912 | 1.4908 | 18.7611 | 2.1544 | 397.9347
38905.5635 | 2322 | 3 | 38905.5635 | 2415 | 4 | 2027 | 2137 | 141.7582 | 0.18315 | 147.4359 | 0.2442 | 1.4176 | 0.0018315 | 1.4744 | 0.002442 | 1.4158 | 1.4719 | 7.8127 | 3.4486 | 190.4393
38905.5637 | 2413 | 4 | 38905.5637 | 2049 | 4 | 2044 | 2154 | 147.3138 | 0.2442 | 125.0916 | 0.2442 | 1.4731 | 0.002442 | 1.2509 | 0.002442 | 1.4707 | 1.2485 | 3.4862 | 23.1772 | 373.4061
38905.5639 | 2355 | 6 | 38905.5639 | 1867 | 5 | 2060.5 | 2170.5 | 143.7729 | 0.3663 | 113.9805 | 0.30525 | 1.4377 | 0.003663 | 1.1398 | 0.0030525 | 1.4341 | 1.1368 | 6.0625 | 35.3678 | 589.517
38905.5641 | 2328 | 8 | 38905.5641 | 2355 | 8 | 2077.5 | 2187.5 | 142.1245 | 0.4884 | 143.7729 | 0.4884 | 1.4212 | 0.004884 | 1.4377 | 0.004884 | 1.4164 | 1.4328 | 7.6777 | 6.3037 | 118.88
38905.5643 | 2298 | 9 | 38905.5643 | 2384 | 9 | 2094.5 | 2204.5 | 140.293 | 0.54945 | 145.5433 | 0.54945 | 1.4029 | 0.0054945 | 1.4554 | 0.0054945 | 1.3974 | 1.4499 | 9.4177 | 4.9302 | 98.8674
38905.5645 | 2384 | 11 | 38905.5645 | 1857 | 8 | 2111 | 2221 | 145.5433 | 0.67155 | 113.37 | 0.4884 | 1.4554 | 0.0067155 | 1.1337 | 0.004884 | 1.4487 | 1.1288 | 4.7942 | 38.0101 | 253.8326
38905.5647 | 2291 | 14 | 38905.5647 | 2372 | 15 | 2128 | 2238 | 139.8657 | 0.8547 | 144.8107 | 0.91575 | 1.3987 | 0.008547 | 1.4481 | 0.0091575 | 1.3901 | 1.4389 | 10.1253 | 5.631 | 72.8719
38905.5649 | 2160 | 12 | 38905.5649 | 2076 | 14 | 2144.5 | 2254.5 | 131.8681 | 0.7326 | 126.7399 | 0.8547 | 1.3187 | 0.007326 | 1.2674 | 0.008547 | 1.3114 | 1.2589 | 16.0822 | 21.2856 | 474.4058
38905.5651 | 2376 | 20 | 38905.5651 | 2363 | 21 | 2161.5 | 2271.5 | 145.0549 | 1.221 | 144.2613 | 1.2821 | 1.4505 | 0.01221 | 1.4426 | 0.012821 | 1.4383 | 1.4298 | 5.8475 | 6.7266 | 31.6331
38905.5653 | 2121 | 22 | 38905.5653 | 2337 | 25 | 2178.5 | 2288.5 | 129.4872 | 1.3431 | 142.674 | 1.5263 | 1.2949 | 0.013431 | 1.4267 | 0.015263 | 1.2814 | 1.4115 | 20.8965 | 7.2698 | 108.8587
38905.5655 | 1934 | 28 | 38905.5655 | 1994 | 27 | 2195 | 2305 | 118.0708 | 1.7094 | 121.7338 | 1.6484 | 1.1807 | 0.017094 | 1.2173 | 0.016484 | 1.1636 | 1.2009 | 31.2227 | 26.7149 | 402.3629
38905.5657 | 2402 | 0 | 38905.5657 | 2461 | 0 | 2212 | 2322 | 146.6422 | 0 | 150.2442 | 0 | 1.4664 | 0 | 1.5024 | 0 | 1.4664 | 1.5024 | 3.9292 | 1.4376 | 2.4628
38905.5659 | 2480 | 1 | 38905.5659 | 1993 | 0 | 2228.5 | 2338.5 | 151.4042 | 0.06105 | 121.6728 | 0 | 1.514 | 0.0006105 | 1.2167 | 0 | 1.5134 | 1.2167 | 0.66181 | 25.2574 | 310.1284
38905.5661 | 2429 | 1 | 38905.5661 | 2010 | 0 | 2245.5 | 2355.5 | 148.2906 | 0.06105 | 122.7106 | 0 | 1.4829 | 0.0006105 | 1.2271 | 0 | 1.4823 | 1.2271 | 2.7799 | 24.198 | 1293.3089
38905.5663 | 2290 | 0 | 38905.5663 | 2184 | 0 | 2262.5 | 2372.5 | 139.8046 | 0 | 133.3333 | 0 | 1.398 | 0 | 1.3333 | 0 | 1.398 | 1.3333 | 9.0122 | 14.3031 | 7.6142
38905.5664 | 1928 | 0 | 38905.5665 | 2059 | 0 | 2279 | 2389 | 117.7045 | 0 | 125.7021 | 0 | 1.177 | 0 | 1.257 | 0 | 1.177 | 1.257 | 29.4803 | 21.2424 | 28.3032
38905.5666 | 2253 | 0 | 38905.5667 | 2213 | 0 | 2296 | 2406 | 137.5458 | 0 | 135.1038 | 0 | 1.3755 | 0 | 1.351 | 0 | 1.3755 | 1.351 | 10.8025 | 12.8052 | 9.427
38905.5668 | 1976 | 0 | 38905.5668 | 1977 | 0 | 2312.5 | 2422.5 | 120.6349 | 0 | 120.696 | 0 | 1.2063 | 0 | 1.207 | 0 | 1.2063 | 1.207 | 26.335 | 26.2711 | 25.1287
38905.567 | 1990 | 0 | 38905.567 | 2211 | 0 | 2329.5 | 2439.5 | 121.4896 | 0 | 134.9817 | 0 | 1.2149 | 0 | 1.3498 | 0 | 1.2149 | 1.3498 | 25.4462 | 12.9073 | 24.2313

## C1-2
Penlight Test 8 |  |  | 2006-07-07 | 12:58 |  | Vs = |  | 152.8926 |  | R = | 100
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38905.5388 | 1 | 0 | 38905.5388 | 1 | 0 | -109 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.539 | 1 | 0 | 38905.539 | 1 | 0 | -92 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5392 | 1 | 0 | 38905.5392 | 1 | 0 | -75.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5394 | 1 | 0 | 38905.5394 | 1 | 0 | -58.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5396 | 1 | 0 | 38905.5396 | 1 | 0 | -41.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5398 | 1 | 0 | 38905.5398 | 1 | 0 | -25 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.54 | 1 | 0 | 38905.54 | 1 | 0 | -8 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5402 | 1 | 0 | 38905.5402 | 1 | 0 | 8.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5404 | 1 | 0 | 38905.5404 | 1 | 0 | 25.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5405 | 1 | 0 | 38905.5406 | 1 | 0 | 42 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5407 | 1 | 0 | 38905.5408 | 1 | 0 | 59 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5409 | 1 | 0 | 38905.5409 | 1 | 0 | 75.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5411 | 1 | 0 | 38905.5411 | 1 | 0 | 92.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5413 | 1 | 0 | 38905.5413 | 1 | 0 | 109.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5415 | 1 | 0 | 38905.5415 | 1 | 0 | 126 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5417 | 1 | 0 | 38905.5417 | 1 | 0 | 143 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5419 | 1 | 0 | 38905.5419 | 1 | 0 | 159.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5421 | 1 | 0 | 38905.5421 | 1 | 0 | 176.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5423 | 1 | 0 | 38905.5423 | 1 | 0 | 193.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5425 | 1 | 0 | 38905.5425 | 1 | 0 | 210.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5427 | 1 | 0 | 38905.5427 | 1 | 0 | 227 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5429 | 1 | 0 | 38905.5429 | 1 | 0 | 243.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5431 | 1 | 0 | 38905.5431 | 1 | 0 | 260.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5433 | 1 | 0 | 38905.5433 | 1 | 0 | 277.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5435 | 1 | 0 | 38905.5435 | 1 | 0 | 294.5 | 404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5437 | 1 | 0 | 38905.5437 | 1 | 0 | 311 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5439 | 1 | 0 | 38905.5439 | 1 | 0 | 327.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5441 | 1 | 0 | 38905.5441 | 1 | 0 | 344.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5442 | 1 | 0 | 38905.5443 | 1 | 0 | 361.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5444 | 1 | 0 | 38905.5445 | 1 | 0 | 378.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5446 | 1 | 0 | 38905.5447 | 1 | 0 | 395 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5448 | 1 | 0 | 38905.5448 | 1 | 0 | 412 | 522 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.545 | 1 | 0 | 38905.545 | 1 | 0 | 428.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5452 | 1 | 0 | 38905.5452 | 1 | 0 | 445.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5454 | 1 | 0 | 38905.5454 | 1 | 0 | 462 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5456 | 1 | 0 | 38905.5456 | 1 | 0 | 479 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5458 | 1 | 0 | 38905.5458 | 1 | 0 | 495.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.546 | 1 | 0 | 38905.546 | 1 | 0 | 512.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5462 | 1 | 0 | 38905.5462 | 1 | 0 | 529.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5464 | 1 | 0 | 38905.5464 | 1 | 0 | 546 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5466 | 1 | 0 | 38905.5466 | 1 | 0 | 563 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5468 | 1 | 0 | 38905.5468 | 1 | 0 | 579.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.547 | 1 | 0 | 38905.547 | 1 | 0 | 596.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5472 | 1 | 0 | 38905.5472 | 1 | 0 | 613.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5474 | 1 | 0 | 38905.5474 | 1 | 0 | 630.5 | 740.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5475 | 1 | 0 | 38905.5476 | 1 | 0 | 647 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5477 | 1 | 0 | 38905.5478 | 1 | 0 | 663.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5479 | 1 | 0 | 38905.548 | 1 | 0 | 680.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5481 | 1 | 0 | 38905.5481 | 1 | 0 | 697.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5483 | 1 | 0 | 38905.5483 | 1 | 0 | 714 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5485 | 1 | 0 | 38905.5485 | 1 | 0 | 731 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5487 | 1 | 0 | 38905.5487 | 1 | 0 | 747.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5489 | 1 | 0 | 38905.5489 | 1 | 0 | 764.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5491 | 1 | 0 | 38905.5491 | 1 | 0 | 781.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5493 | 1 | 0 | 38905.5493 | 1 | 0 | 798 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5495 | 1 | 0 | 38905.5495 | 2 | 0 | 815 | 925 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250338 | 125119 | 250337.9994
38905.5497 | 1 | 0 | 38905.5497 | 1 | 0 | 831.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5499 | 1 | 0 | 38905.5499 | 1 | 0 | 848.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5501 | 1 | 0 | 38905.5501 | 1 | 0 | 865.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5503 | 1 | 0 | 38905.5503 | 1 | 0 | 882 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5505 | 1 | 0 | 38905.5505 | 1 | 0 | 899 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5507 | 1 | 0 | 38905.5507 | 1 | 0 | 915.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5509 | 1 | 0 | 38905.5509 | 1 | 0 | 932.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5511 | 1 | 0 | 38905.5511 | 1 | 0 | 949.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5512 | 1 | 0 | 38905.5513 | 1 | 0 | 966 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5514 | 1 | 0 | 38905.5515 | 1 | 0 | 983 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5516 | 1 | 0 | 38905.5516 | 1 | 0 | 999.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5518 | 1 | 0 | 38905.5518 | 1 | 0 | 1016.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.552 | 1 | 0 | 38905.552 | 1 | 0 | 1033.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5522 | 1 | 0 | 38905.5522 | 1 | 0 | 1050 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5524 | 1 | 0 | 38905.5524 | 1 | 0 | 1067 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5526 | 1 | 0 | 38905.5526 | 1 | 0 | 1083.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5528 | 1 | 0 | 38905.5528 | 1 | 0 | 1100.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.553 | 1 | 0 | 38905.553 | 1 | 0 | 1117.5 | 1227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5532 | 1 | 0 | 38905.5532 | 1 | 0 | 1134 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5534 | 1 | 0 | 38905.5534 | 1 | 0 | 1151 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5536 | 1 | 0 | 38905.5536 | 1 | 0 | 1167.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5538 | 1 | 0 | 38905.5538 | 1 | 0 | 1184.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.554 | 1 | 0 | 38905.554 | 1 | 0 | 1201.5 | 1311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5542 | 1 | 0 | 38905.5542 | 1 | 0 | 1218 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5544 | 1 | 0 | 38905.5544 | 1 | 0 | 1235 | 1345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250338 | 250338 | 250337.9994
38905.5545 | 7 | 0 | 38905.5546 | 4 | 0 | 1251.5 | 1361.5 | 0.42735 | 0 | 0.2442 | 0 | 0.0042735 | 0 | 0.002442 | 0 | 0.0042735 | 0.002442 | 35676.8571 | 62509.5 | 35676.8529
38905.5547 | 9 | 0 | 38905.5548 | 6 | 0 | 1268.5 | 1378.5 | 0.54945 | 0 | 0.3663 | 0 | 0.0054945 | 0 | 0.003663 | 0 | 0.0054945 | 0.003663 | 27726.4444 | 41639.6667 | 27726.4389
| 8 | 0 | 38905.555 | 7 | 0 | 1286 | 1396 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31204.75 | 35676.8571 | 31204.7451
38905.5551 | 8 | 0 | 38905.5552 | 7 | 0 | 1302 | 1412 | 0.4884 | 0 | 0.42735 | 0 | 0.004884 | 0 | 0.0042735 | 0 | 0.004884 | 0.0042735 | 31204.75 | 35676.8571 | 31204.7451
38905.5553 | 9 | 0 | 38905.5553 | 8 | 0 | 1319 | 1429 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5555 | 9 | 0 | 38905.5555 | 8 | 0 | 1335.5 | 1445.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5557 | 9 | 0 | 38905.5557 | 9 | 0 | 1352.5 | 1462.5 | 0.54945 | 0 | 0.54945 | 0 | 0.0054945 | 0 | 0.0054945 | 0 | 0.0054945 | 0.0054945 | 27726.4444 | 27726.4444 | 27726.4389
38905.5559 | 9 | 0 | 38905.5559 | 8 | 0 | 1369.5 | 1479.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5561 | 9 | 0 | 38905.5561 | 9 | 0 | 1386 | 1496 | 0.54945 | 0 | 0.54945 | 0 | 0.0054945 | 0 | 0.0054945 | 0 | 0.0054945 | 0.0054945 | 27726.4444 | 27726.4444 | 27726.4389
38905.5563 | 9 | 0 | 38905.5563 | 9 | 0 | 1403 | 1513 | 0.54945 | 0 | 0.54945 | 0 | 0.0054945 | 0 | 0.0054945 | 0 | 0.0054945 | 0.0054945 | 27726.4444 | 27726.4444 | 27726.4389
38905.5565 | 9 | 0 | 38905.5565 | 8 | 0 | 1419.5 | 1529.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5567 | 9 | 0 | 38905.5567 | 8 | 1 | 1436.5 | 1546.5 | 0.54945 | 0 | 0.4884 | 0.06105 | 0.0054945 | 0 | 0.004884 | 0.0006105 | 0.0054945 | 0.0042735 | 27726.4444 | 35676.8571 | 27726.4389
38905.5569 | 9 | 0 | 38905.5569 | 8 | 0 | 1453.5 | 1563.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5571 | 9 | 0 | 38905.5571 | 8 | 0 | 1470 | 1580 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5573 | 9 | 0 | 38905.5573 | 8 | 0 | 1486.5 | 1596.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5575 | 9 | 0 | 38905.5575 | 8 | 0 | 1503.5 | 1613.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5577 | 9 | 0 | 38905.5577 | 8 | 0 | 1520.5 | 1630.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5578 | 9 | 0 | 38905.5579 | 8 | 0 | 1537 | 1647 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.558 | 9 | 0 | 38905.5581 | 8 | 0 | 1554 | 1664 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5582 | 9 | 0 | 38905.5583 | 8 | 0 | 1570.5 | 1680.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5584 | 10 | 0 | 38905.5584 | 8 | 0 | 1587.5 | 1697.5 | 0.6105 | 0 | 0.4884 | 0 | 0.006105 | 0 | 0.004884 | 0 | 0.006105 | 0.004884 | 24943.8 | 31204.75 | 24943.7939
38905.5586 | 9 | 0 | 38905.5586 | 8 | 0 | 1604.5 | 1714.5 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5588 | 9 | 0 | 38905.5588 | 8 | 0 | 1621 | 1731 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.559 | 9 | 0 | 38905.559 | 8 | 0 | 1638 | 1748 | 0.54945 | 0 | 0.4884 | 0 | 0.0054945 | 0 | 0.004884 | 0 | 0.0054945 | 0.004884 | 27726.4444 | 31204.75 | 27726.4389
38905.5592 | 2254 | 0 | 38905.5592 | 9 | 0 | 1654.5 | 1764.5 | 137.6068 | 0 | 0.54945 | 0 | 1.3761 | 0 | 0.0054945 | 0 | 1.3761 | 0.0054945 | 11.1083 | 27726.4444 | 9.7322
38905.5594 | 1995 | 0 | 38905.5594 | 9 | 0 | 1671.5 | 1781.5 | 121.7949 | 0 | 0.54945 | 0 | 1.2179 | 0 | 0.0054945 | 0 | 1.2179 | 0.0054945 | 25.5328 | 27726.4444 | 24.3149
38905.5596 | 2374 | 0 | 38905.5596 | 9 | 0 | 1688.5 | 1798.5 | 144.9328 | 0 | 0.54945 | 0 | 1.4493 | 0 | 0.0054945 | 0 | 1.4493 | 0.0054945 | 5.492 | 27726.4444 | 4.0427
38905.5598 | 2231 | 0 | 38905.5598 | 9 | 0 | 1705.5 | 1815.5 | 136.2027 | 0 | 0.54945 | 0 | 1.362 | 0 | 0.0054945 | 0 | 1.362 | 0.0054945 | 12.2537 | 27726.4444 | 10.8917
38905.56 | 2269 | 0 | 38905.56 | 9 | 0 | 1722 | 1832 | 138.5226 | 0 | 0.54945 | 0 | 1.3852 | 0 | 0.0054945 | 0 | 1.3852 | 0.0054945 | 10.3737 | 27726.4444 | 8.9885
38905.5602 | 2014 | 0 | 38905.5602 | 9 | 0 | 1739 | 1849 | 122.9548 | 0 | 0.54945 | 0 | 1.2295 | 0 | 0.0054945 | 0 | 1.2295 | 0.0054945 | 24.3486 | 27726.4444 | 23.119
38905.5604 | 2103 | 0 | 38905.5604 | 9 | 0 | 1755.5 | 1865.5 | 128.3883 | 0 | 0.54945 | 0 | 1.2839 | 0 | 0.0054945 | 0 | 1.2839 | 0.0054945 | 19.0861 | 27726.4444 | 17.8022
38905.5606 | 2439 | 0 | 38905.5606 | 1254 | 0 | 1772.5 | 1882.5 | 148.9011 | 0 | 76.5568 | 0 | 1.489 | 0 | 0.76557 | 0 | 1.489 | 0.76557 | 2.6806 | 99.7113 | 1.1916
38905.5608 | 2289 | 0 | 38905.5608 | 1039 | 0 | 1789 | 1899 | 139.7436 | 0 | 63.431 | 0 | 1.3974 | 0 | 0.63431 | 0 | 1.3974 | 0.63431 | 9.4093 | 141.0375 | 8.0119
38905.561 | 2239 | 0 | 38905.561 | 2060 | 0 | 1806 | 1916 | 136.6911 | 0 | 125.7631 | 0 | 1.3669 | 0 | 1.2576 | 0 | 1.3669 | 1.2576 | 11.8526 | 21.5718 | 10.4857
38905.5612 | 2167 | 0 | 38905.5612 | 1747 | 0 | 1822.5 | 1932.5 | 132.2955 | 0 | 106.6545 | 0 | 1.323 | 0 | 1.0665 | 0 | 1.323 | 1.0665 | 15.569 | 43.3532 | 14.246
38905.5614 | 1983 | 0 | 38905.5614 | 1658 | 0 | 1839.5 | 1949.5 | 121.0623 | 0 | 101.221 | 0 | 1.2106 | 0 | 1.0122 | 0 | 1.2106 | 1.0122 | 26.2925 | 51.0483 | 25.0819
38905.5616 | 1857 | 0 | 38905.5616 | 1977 | 0 | 1856.5 | 1966.5 | 113.37 | 0 | 120.696 | 0 | 1.1337 | 0 | 1.207 | 0 | 1.1337 | 1.207 | 34.8616 | 26.6758 | 33.7279
38905.5617 | 2107 | 0 | 38905.5618 | 2269 | 0 | 1873 | 1983 | 128.6325 | 0 | 138.5226 | 0 | 1.2863 | 0 | 1.3852 | 0 | 1.2863 | 1.3852 | 18.86 | 10.3737 | 17.5737
38905.5619 | 2151 | 0 | 38905.562 | 2034 | 0 | 1890 | 2000 | 131.3187 | 0 | 124.1758 | 0 | 1.3132 | 0 | 1.2418 | 0 | 1.3132 | 1.2418 | 16.4286 | 23.1259 | 15.1155
38905.5621 | 2034 | 0 | 38905.5621 | 2116 | 0 | 1906.5 | 2016.5 | 124.1758 | 0 | 129.1819 | 0 | 1.2418 | 0 | 1.2918 | 0 | 1.2418 | 1.2918 | 23.1259 | 18.3544 | 21.8841
38905.5623 | 2082 | 0 | 38905.5623 | 2162 | 0 | 1923.5 | 2033.5 | 127.1062 | 0 | 131.9902 | 0 | 1.2711 | 0 | 1.3199 | 0 | 1.2711 | 1.3199 | 20.2872 | 15.8363 | 19.0162
38905.5625 | 1908 | 1 | 38905.5625 | 1895 | 1 | 1940.5 | 2050.5 | 116.4835 | 0.06105 | 115.6899 | 0.06105 | 1.1648 | 0.0006105 | 1.1569 | 0.0006105 | 1.1642 | 1.1563 | 31.3242 | 32.2286 | 14511.4178
38905.5627 | 2064 | 0 | 38905.5627 | 2312 | 1 | 1957 | 2067 | 126.0073 | 0 | 141.1477 | 0.06105 | 1.2601 | 0 | 1.4115 | 0.0006105 | 1.2601 | 1.4109 | 21.3362 | 8.3678 | 20.0762
38905.5629 | 2378 | 2 | 38905.5629 | 2382 | 1 | 1974 | 2084 | 145.177 | 0.1221 | 145.4212 | 0.06105 | 1.4518 | 0.001221 | 1.4542 | 0.0006105 | 1.4505 | 1.4536 | 5.4069 | 5.1801 | 306.2843
38905.5631 | 2392 | 2 | 38905.5631 | 2372 | 1 | 1990.5 | 2100.5 | 146.0317 | 0.1221 | 144.8107 | 0.06105 | 1.4603 | 0.001221 | 1.4481 | 0.0006105 | 1.4591 | 1.4475 | 4.773 | 5.6331 | 294.3106
38905.5633 | 1925 | 1 | 38905.5633 | 2267 | 2 | 2007.5 | 2117.5 | 117.5214 | 0.06105 | 138.4005 | 0.1221 | 1.1752 | 0.0006105 | 1.384 | 0.001221 | 1.1746 | 1.3828 | 30.263 | 10.511 | 5501.1389
38905.5635 | 1996 | 2 | 38905.5635 | 2023 | 2 | 2024.5 | 2134.5 | 121.8559 | 0.1221 | 123.5043 | 0.1221 | 1.2186 | 0.001221 | 1.235 | 0.001221 | 1.2173 | 1.2338 | 25.6029 | 23.9113 | 4885.8393
38905.5637 | 2091 | 3 | 38905.5637 | 2429 | 4 | 2041 | 2151 | 127.6557 | 0.18315 | 148.2906 | 0.2442 | 1.2766 | 0.0018315 | 1.4829 | 0.002442 | 1.2747 | 1.4805 | 20.7493 | 3.1334 | 415.6008
38905.5639 | 2221 | 5 | 38905.5639 | 2218 | 7 | 2058 | 2168 | 135.5922 | 0.30525 | 135.409 | 0.42735 | 1.3559 | 0.0030525 | 1.3541 | 0.0042735 | 1.3529 | 1.3498 | 13.009 | 13.2756 | 652.5078
38905.5641 | 2104 | 7 | 38905.5641 | 2193 | 7 | 2074.5 | 2184.5 | 128.4493 | 0.42735 | 133.8828 | 0.42735 | 1.2845 | 0.0042735 | 1.3388 | 0.0042735 | 1.2802 | 1.3346 | 19.5435 | 14.4816 | 710.8764
38905.5643 | 2003 | 8 | 38905.5643 | 2109 | 8 | 2091.5 | 2201.5 | 122.2833 | 0.4884 | 128.7546 | 0.4884 | 1.2228 | 0.004884 | 1.2875 | 0.004884 | 1.2179 | 1.2827 | 25.6707 | 19.102 | 989.1252
38905.5645 | 2223 | 11 | 38905.5645 | 2289 | 11 | 2108.5 | 2218.5 | 135.7143 | 0.67155 | 139.7436 | 0.67155 | 1.3571 | 0.0067155 | 1.3974 | 0.0067155 | 1.3504 | 1.3907 | 13.4 | 9.8082 | 219.5522
38905.5647 | 2318 | 14 | 38905.5647 | 2123 | 14 | 2125 | 2235 | 141.514 | 0.8547 | 129.6093 | 0.8547 | 1.4151 | 0.008547 | 1.2961 | 0.008547 | 1.4066 | 1.2875 | 8.3476 | 19.6457 | 202.1761
38905.5648 | 1861 | 12 | 38905.5649 | 2172 | 13 | 2142 | 2252 | 113.6142 | 0.7326 | 132.6007 | 0.79365 | 1.1361 | 0.007326 | 1.326 | 0.0079365 | 1.1288 | 1.3181 | 36.301 | 15.6548 | 712.1844
38905.565 | 2161 | 17 | 38905.5651 | 2045 | 17 | 2158.5 | 2268.5 | 131.9292 | 1.0379 | 124.8474 | 1.0379 | 1.3193 | 0.010379 | 1.2485 | 0.010379 | 1.3089 | 1.2381 | 16.5664 | 23.8592 | 369.8295
38905.5652 | 1939 | 8 | 38905.5653 | 2210 | 23 | 2175.5 | 2285.5 | 118.3761 | 0.4884 | 134.9206 | 1.4042 | 1.1838 | 0.004884 | 1.3492 | 0.014042 | 1.1789 | 1.3352 | 30.1755 | 13.9465 | 852.7581
38905.5654 | 1978 | 27 | 38905.5655 | 2256 | 32 | 2192.5 | 2302.5 | 120.757 | 1.6484 | 137.7289 | 1.9536 | 1.2076 | 0.016484 | 1.3773 | 0.019536 | 1.1911 | 1.3578 | 30.5926 | 11.7194 | 194.0183
38905.5656 | 2169 | 0 | 38905.5656 | 2370 | 0 | 2209 | 2319 | 132.4176 | 0 | 144.6886 | 0 | 1.3242 | 0 | 1.4469 | 0 | 1.3242 | 1.4469 | 15.4624 | 5.67 | 14.1382
38905.5658 | 2274 | 0 | 38905.5658 | 2111 | 0 | 2226 | 2336 | 138.8278 | 0 | 128.8767 | 0 | 1.3883 | 0 | 1.2888 | 0 | 1.3883 | 1.2888 | 10.131 | 18.6348 | 8.7428
38905.566 | 1940 | 0 | 38905.566 | 2233 | 0 | 2242.5 | 2352.5 | 118.4371 | 0 | 136.3248 | 0 | 1.1844 | 0 | 1.3632 | 0 | 1.1844 | 1.3632 | 29.0918 | 12.1532 | 27.9074
38905.5662 | 2155 | 0 | 38905.5662 | 1969 | 0 | 2259.5 | 2369.5 | 131.5629 | 0 | 120.2076 | 0 | 1.3156 | 0 | 1.2021 | 0 | 1.3156 | 1.2021 | 16.2125 | 27.1905 | 14.8969
38905.5664 | 1965 | 1 | 38905.5664 | 2488 | 1 | 2276.5 | 2386.5 | 119.9634 | 0.06105 | 151.8926 | 0.06105 | 1.1996 | 0.0006105 | 1.5189 | 0.0006105 | 1.199 | 1.5183 | 29.761 | 0.65952 | 352.7438
38905.5666 | 2016 | 0 | 38905.5666 | 2465 | 0 | 2293 | 2403 | 123.0769 | 0 | 150.4884 | 0 | 1.2308 | 0 | 1.5049 | 0 | 1.2308 | 1.5049 | 24.2252 | 1.5976 | 22.9944
38905.5668 | 2314 | 0 | 38905.5668 | 2353 | 0 | 2310 | 2420 | 141.2698 | 0 | 143.6508 | 0 | 1.4127 | 0 | 1.4365 | 0 | 1.4127 | 1.4365 | 8.2273 | 6.4335 | 6.8146
38905.567 | 2243 | 0 | 38905.567 | 1942 | 0 | 2326.5 | 2436.5 | 136.9353 | 0 | 118.5592 | 0 | 1.3694 | 0 | 1.1856 | 0 | 1.3694 | 1.1856 | 11.6531 | 28.9588 | 10.2838

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 8 |  |  | 2006-07-07 | 12:58
PVC | 3-C | Conduit
300 C | 6.1 kW/m2 | [5 empty] | 4 is Drain Wire |  |  |  | Excluding Drain Wire
Penlight Time | Average C1-G |  | Penlight Time | Average C2-G | Penlight Time | Average C3-G | Penlight Time | Average C4-G | Penlight Time | Minimums on Average | Penlight Time | Minimums
-106.1667 | 249438 |  | -102.3333 | 249838 | -100.3333 | 249838 | -98.5 | 249104.6667 | -106.1667 | 249104.6667 | -106.1667 | 249438
-89.3333 | 249438 |  | -85.5 | 249838 | -83.6667 | 249838 | -81.8333 | 249104.6667 | -89.3333 | 249104.6667 | -89.3333 | 249438
-72.5 | 249438 |  | -69 | 249838 | -67 | 249838 | -65.1667 | 249104.6667 | -72.5 | 249104.6667 | -72.5 | 249438
-55.6667 | 249438 |  | -52 | 249838 | -50 | 249838 | -48.3333 | 249104.6667 | -55.6667 | 249104.6667 | -55.6667 | 249438
-38.8333 | 249438 |  | -35.1667 | 249838 | -33.3333 | 249838 | -31.3333 | 249104.6667 | -38.8333 | 249104.6667 | -38.8333 | 249438
-22.1667 | 249438 |  | -18.3333 | 249838 | -16.5 | 249838 | -14.6667 | 249104.6667 | -22.1667 | 249104.6667 | -22.1667 | 249438
-5.3333 | 249438 |  | -1.6667 | 249838 | 0.16667 | 249838 | 2.1667 | 249104.6667 | -5.3333 | 249104.6667 | -5.3333 | 249438
11.3333 | 249438 |  | 15.1667 | 249838 | 17 | 249838 | 18.8333 | 249104.6667 | 11.3333 | 249104.6667 | 11.3333 | 249438
28.3333 | 249438 |  | 32 | 249838 | 34 | 249838 | 35.6667 | 249104.6667 | 28.3333 | 249104.6667 | 28.3333 | 249438
45 | 249438 |  | 48.6667 | 166608.6667 | 50.6667 | 249838 | 52.6667 | 207681.6667 | 45 | 166608.6667 | 45 | 166608.6667
61.6667 | 249438 |  | 65.6667 | 249838 | 67.3333 | 249838 | 69.3333 | 207581.6667 | 61.6667 | 207581.6667 | 61.6667 | 249438
78.5 | 249438 |  | 82.3333 | 249838 | 84.3333 | 249838 | 86.1667 | 249104.6667 | 78.5 | 249104.6667 | 78.5 | 249438
95.3333 | 249438 |  | 99 | 249838 | 101 | 249838 | 102.6667 | 249104.6667 | 95.3333 | 249104.6667 | 95.3333 | 249438
112.3333 | 249438 |  | 116 | 208729855.48 | 118 | 249838 | 119.6667 | 249104.6667 | 112.3333 | 249104.6667 | 112.3333 | 249438
129 | 249438 |  | 132.6667 | 249838 | 134.5 | 249838 | 136.5 | 249104.6667 | 129 | 249104.6667 | 129 | 249438
145.8333 | 249438 |  | 149.6667 | 249838 | 151.5 | 249838 | 153.3333 | 249104.6667 | 145.8333 | 249104.6667 | 145.8333 | 249438
162.5 | 249438 |  | 166.3333 | 249838 | 168.1667 | 249838 | 170 | 249104.6667 | 162.5 | 249104.6667 | 162.5 | 249438
179.5 | 249438 |  | 183 | 249838 | 185 | 249838 | 186.8333 | 249104.6667 | 179.5 | 249104.6667 | 179.5 | 249438
196.1667 | 249438 |  | 200 | 249838 | 201.8333 | 249838 | 203.6667 | 249104.6667 | 196.1667 | 249104.6667 | 196.1667 | 249438
213.1667 | 249438 |  | 216.8333 | 249838 | 218.5 | 249838 | 220.5 | 249104.6667 | 213.1667 | 249104.6667 | 213.1667 | 249438
229.6667 | 249438 |  | 233.6667 | 249838 | 235.3333 | 249838 | 237.3333 | 249104.6667 | 229.6667 | 249104.6667 | 229.6667 | 249438
246.5 | 249438 |  | 250.3333 | 249838 | 252.1667 | 249838 | 254 | 207448.3333 | 246.5 | 207448.3333 | 246.5 | 249438
263.3333 | 249438 |  | 267.1667 | 249838 | 269 | 249838 | 270.8333 | 249104.6667 | 263.3333 | 249104.6667 | 263.3333 | 249438
280.1667 | 249438 |  | 283.8333 | 249838 | 285.6667 | 249838 | 287.6667 | 249104.6667 | 280.1667 | 249104.6667 | 280.1667 | 249438
297 | 249438 |  | 300.8333 | 249838 | 302.6667 | 249838 | 304.5 | 249104.6667 | 297 | 249104.6667 | 297 | 249438
313.6667 | 249438 |  | 317.5 | 249838 | 319.3333 | 249838 | 321.1667 | 249104.6667 | 313.6667 | 249104.6667 | 313.6667 | 249438
330.5 | 249438 |  | 334.3333 | 249838 | 336.1667 | 249838 | 338 | 249104.6667 | 330.5 | 249104.6667 | 330.5 | 249438
347.3333 | 249438 |  | 351 | 249838 | 353 | 249838 | 354.6667 | 249104.6667 | 347.3333 | 249104.6667 | 347.3333 | 249438
364.1667 | 249438 |  | 367.8333 | 249838 | 369.6667 | 249838 | 371.6667 | 249104.6667 | 364.1667 | 249104.6667 | 364.1667 | 249438
380.8333 | 249438 |  | 384.8333 | 208315 | 386.5 | 249838 | 388.1667 | 249104.6667 | 380.8333 | 208315 | 380.8333 | 208315
397.6667 | 249438 |  | 401.5 | 249838 | 403.3333 | 249838 | 405.1667 | 249104.6667 | 397.6667 | 249104.6667 | 397.6667 | 249438
414.6667 | 249438 |  | 418.3333 | 208729855.48 | 420 | 249838 | 422 | 249104.6667 | 414.6667 | 249104.6667 | 414.6667 | 249438
431.5 | 249438 |  | 435 | 249838 | 437 | 249838 | 438.8333 | 249104.6667 | 431.5 | 249104.6667 | 431.5 | 249438
448.1667 | 249438 |  | 451.8333 | 249838 | 453.6667 | 249838 | 455.6667 | 249104.6667 | 448.1667 | 249104.6667 | 448.1667 | 249438
464.8333 | 208015 |  | 468.6667 | 249838 | 470.6667 | 249838 | 472.5 | 249104.6667 | 464.8333 | 208015 | 464.8333 | 208015
481.6667 | 249438 |  | 485.5 | 249838 | 487.3333 | 249838 | 489.1667 | 249104.6667 | 481.6667 | 249104.6667 | 481.6667 | 249438
498.5 | 249438 |  | 502.1667 | 249838 | 504 | 249838 | 506 | 249104.6667 | 498.5 | 249104.6667 | 498.5 | 249438
515.3333 | 249438 |  | 519 | 249838 | 521 | 249838 | 522.6667 | 249104.6667 | 515.3333 | 249104.6667 | 515.3333 | 249438
532.1667 | 249438 |  | 535.8333 | 206899910.1467 | 537.6667 | 249838 | 539.6667 | 249104.6667 | 532.1667 | 249104.6667 | 532.1667 | 249438
549 | 249438 |  | 552.6667 | 249838 | 554.5 | 249838 | 556.5 | 249104.6667 | 549 | 249104.6667 | 549 | 249438
565.6667 | 249438 |  | 569.5 | 249838 | 571.3333 | 249838 | 573.1667 | 249104.6667 | 565.6667 | 249104.6667 | 565.6667 | 249438
582.5 | 249438 |  | 586.1667 | 249838 | 588 | 249838 | 590 | 249104.6667 | 582.5 | 249104.6667 | 582.5 | 249438
599.3333 | 249438 |  | 603 | 249838 | 605 | 249838 | 606.6667 | 249104.6667 | 599.3333 | 249104.6667 | 599.3333 | 249438
616.3333 | 249438 |  | 619.8333 | 249838 | 621.8333 | 249838 | 623.6667 | 249104.6667 | 616.3333 | 249104.6667 | 616.3333 | 249438
633 | 249438 |  | 636.8333 | 249838 | 638.5 | 249838 | 640.3333 | 249104.6667 | 633 | 249104.6667 | 633 | 249438
649.6667 | 249438 |  | 653.5 | 249838 | 655.3333 | 249838 | 657.1667 | 249104.6667 | 649.6667 | 249104.6667 | 649.6667 | 249438
666.5 | 249438 |  | 670.1667 | 249838 | 672 | 249838 | 674 | 249104.6667 | 666.5 | 249104.6667 | 666.5 | 249438
683.3333 | 249438 |  | 687 | 249838 | 689 | 249838 | 690.6667 | 249104.6667 | 683.3333 | 249104.6667 | 683.3333 | 249438
700.1667 | 249438 |  | 703.8333 | 249838 | 705.6667 | 249838 | 707.6667 | 249104.6667 | 700.1667 | 249104.6667 | 700.1667 | 249438
716.8333 | 249438 |  | 720.6667 | 249838 | 722.5 | 249838 | 724.3333 | 249104.6667 | 716.8333 | 249104.6667 | 716.8333 | 249438
733.6667 | 249438 |  | 737.5 | 249838 | 739.3333 | 249838 | 741.1667 | 249104.6667 | 733.6667 | 249104.6667 | 733.6667 | 249438
750.5 | 249438 |  | 754.1667 | 249838 | 756 | 249838 | 758 | 249104.6667 | 750.5 | 249104.6667 | 750.5 | 249438
767.3333 | 249438 |  | 771 | 249838 | 773 | 249838 | 774.6667 | 249104.6667 | 767.3333 | 249104.6667 | 767.3333 | 249438
784.1667 | 249438 |  | 787.8333 | 249838 | 789.6667 | 208181.6667 | 791.6667 | 249104.6667 | 784.1667 | 208181.6667 | 784.1667 | 208181.6667
800.8333 | 249438 |  | 804.6667 | 249838 | 806.5 | 249838 | 808.3333 | 249104.6667 | 800.8333 | 249104.6667 | 800.8333 | 249438
817.6667 | 249438 |  | 821.5 | 208098.3333 | 823.3333 | 249838 | 825.1667 | 249104.6667 | 817.6667 | 208098.3333 | 817.6667 | 208098.3333
834.5 | 249438 |  | 838.1667 | 249838 | 840 | 249838 | 842 | 249104.6667 | 834.5 | 249104.6667 | 834.5 | 249438
851.3333 | 249438 |  | 855 | 249838 | 857 | 249838 | 858.6667 | 249104.6667 | 851.3333 | 249104.6667 | 851.3333 | 249438
868.1667 | 249438 |  | 871.8333 | 249838 | 873.6667 | 249838 | 875.6667 | 249104.6667 | 868.1667 | 249104.6667 | 868.1667 | 249438
884.8333 | 249438 |  | 888.6667 | 249838 | 890.5 | 249838 | 892.3333 | 249104.6667 | 884.8333 | 249104.6667 | 884.8333 | 249438
901.6667 | 249438 |  | 905.5 | 249838 | 907.3333 | 249838 | 909.1667 | 249104.6667 | 901.6667 | 249104.6667 | 901.6667 | 249438
918.5 | 249438 |  | 922.1667 | 249838 | 924 | 249838 | 926 | 249104.6667 | 918.5 | 249104.6667 | 918.5 | 249438
935.3333 | 249438 |  | 939 | 249838 | 941 | 249838 | 942.6667 | 249104.6667 | 935.3333 | 249104.6667 | 935.3333 | 249438
952.1667 | 249438 |  | 955.8333 | 249838 | 957.6667 | 249838 | 959.6667 | 249104.6667 | 952.1667 | 249104.6667 | 952.1667 | 249438
968.8333 | 207730303.48 |  | 972.6667 | 249838 | 974.5 | 249838 | 976.3333 | 249104.6667 | 968.8333 | 249104.6667 | 968.8333 | 249838
985.6667 | 249438 |  | 989.5 | 249838 | 991.3333 | 249838 | 993.1667 | 249104.6667 | 985.6667 | 249104.6667 | 985.6667 | 249438
1002.5 | 249438 |  | 1006.1667 | 249838 | 1008 | 249838 | 1010 | 249104.6667 | 1002.5 | 249104.6667 | 1002.5 | 249438
1019.3333 | 249438 |  | 1023 | 249838 | 1025 | 249838 | 1026.6667 | 249104.6667 | 1019.3333 | 249104.6667 | 1019.3333 | 249438
1036.1667 | 249438 |  | 1039.8333 | 249838 | 1041.6667 | 249838 | 1043.6667 | 249104.6667 | 1036.1667 | 249104.6667 | 1036.1667 | 249438
1052.8333 | 249438 |  | 1056.6667 | 249838 | 1058.5 | 249838 | 1060.3333 | 249104.6667 | 1052.8333 | 249104.6667 | 1052.8333 | 249438
1069.6667 | 249438 |  | 1073.5 | 249838 | 1075.3333 | 208229979.48 | 1077.1667 | 249104.6667 | 1069.6667 | 249104.6667 | 1069.6667 | 249438
1086.5 | 249438 |  | 1090.1667 | 249838 | 1092 | 249838 | 1094 | 249104.6667 | 1086.5 | 249104.6667 | 1086.5 | 249438
1103.3333 | 249438 |  | 1107 | 249838 | 1109 | 249838 | 1110.6667 | 249104.6667 | 1103.3333 | 249104.6667 | 1103.3333 | 249438
1120.1667 | 249438 |  | 1123.8333 | 249838 | 1125.6667 | 249838 | 1127.6667 | 249104.6667 | 1120.1667 | 249104.6667 | 1120.1667 | 249438
1136.8333 | 249438 |  | 1140.6667 | 249838 | 1142.5 | 249838 | 1144.3333 | 249104.6667 | 1136.8333 | 249104.6667 | 1136.8333 | 249438
1153.6667 | 249438 |  | 1157.5 | 249838 | 1159.3333 | 249838 | 1161.1667 | 249104.6667 | 1153.6667 | 249104.6667 | 1153.6667 | 249438
1170.5 | 249438 |  | 1174 | 249838 | 1176 | 249838 | 1177.8333 | 249104.6667 | 1170.5 | 249104.6667 | 1170.5 | 249438
1187.3333 | 249438 |  | 1191 | 249838 | 1193 | 249838 | 1194.6667 | 249104.6667 | 1187.3333 | 249104.6667 | 1187.3333 | 249438
1204.1667 | 249438 |  | 1207.8333 | 249838 | 1209.6667 | 249838 | 1211.6667 | 249104.6667 | 1204.1667 | 249104.6667 | 1204.1667 | 249438
1220.8333 | 249438 |  | 1224.6667 | 249838 | 1226.5 | 249838 | 1228.3333 | 249104.6667 | 1220.8333 | 249104.6667 | 1220.8333 | 249438
1237.6667 | 249438 |  | 1241.5 | 249838 | 1243.3333 | 187353.5 | 1245.1667 | 82848.5645 | 1237.6667 | 82848.5645 | 1237.6667 | 187353.5
1254.5 | 80986.1746 |  | 1258 | 53447.4286 | 1260 | 58904.8056 | 1261.8333 | 70.8832 | 1254.5 | 70.8832 | 1254.5 | 53447.4286
1271.3333 | 57593.9815 |  | 1275 | 43842.7963 | 1277 | 50796.6296 | 1278.6667 | 61.2744 | 1271.3333 | 61.2744 | 1271.3333 | 43842.7963
1288.1667 | 44915.1944 |  | 1292 | 43013.7024 | 1293.6667 | 51561.9894 | 1295.5 | 49.7015 | 1288.1667 | 49.7015 | 1288.1667 | 43013.7024
1304.8333 | 51819.0278 |  | 1308.6667 | 41855.1931 | 1310.5 | 41876.2249 | 1312.3333 | 37.6969 | 1304.8333 | 37.6969 | 1304.8333 | 41855.1931
1321.6667 | 50659.5926 |  | 1325.3333 | 36212.1907 | 1327.1667 | 36226.0796 | 1329.1667 | 23.0246 | 1321.6667 | 23.0246 | 1321.6667 | 36212.1907
1338.5 | 36146.2648 |  | 1342 | 33443.9907 | 1344 | 33452.3241 | 1345.8333 | 10.5322 | 1338.5 | 10.5322 | 1338.5 | 33443.9907
1355.3333 | 33384.7315 |  | 1359 | 32284.5556 | 1361 | 31471.0701 | 1362.6667 | 22.5259 | 1355.3333 | 22.5259 | 1355.3333 | 31471.0701
1372.1667 | 33384.7315 |  | 1375.8333 | 31466.705 | 1377.5 | 32960.582 | 1379.5 | 28.6531 | 1372.1667 | 28.6531 | 1372.1667 | 31466.705
1388.8333 | 34870.672 |  | 1392.6667 | 32284.5556 | 1394.5 | 31471.0701 | 1396.3333 | 19.3144 | 1388.8333 | 19.3144 | 1388.8333 | 31471.0701
1405.6667 | 33384.7315 |  | 1409.3333 | 29380.4624 | 1411.1667 | 31471.0701 | 1413.1667 | 8.9288 | 1405.6667 | 8.9288 | 1405.6667 | 29380.4624
1422.3333 | 33384.7315 |  | 1426.1667 | 31466.705 | 1428 | 31471.0701 | 1429.8333 | 11.5966 | 1422.3333 | 11.5966 | 1422.3333 | 31466.705
1439.3333 | 60721.557 |  | 1442.8333 | 32957.4074 | 1444.8333 | 31471.0701 | 1446.6667 | 25.4081 | 1439.3333 | 25.4081 | 1439.3333 | 31471.0701
1456 | 33384.7315 |  | 1459.8333 | 33443.9907 | 1461.6667 | 31471.0701 | 1463.5 | 19.8163 | 1456 | 19.8163 | 1456 | 31471.0701
1472.6667 | 33384.7315 |  | 1476.6667 | 34602.5 | 1478.3333 | 32628.1905 | 1480.3333 | 19.6067 | 1472.6667 | 19.6067 | 1472.6667 | 32628.1905
1489.5 | 33384.7315 |  | 1493.3333 | 31466.705 | 1495.3333 | 30545.3738 | 1497.1667 | 17.0305 | 1489.5 | 17.0305 | 1489.5 | 30545.3738
1506.3333 | 37632.2053 |  | 1510.1667 | 31466.705 | 1512 | 31471.0701 | 1513.8333 | 16.4471 | 1506.3333 | 16.4471 | 1506.3333 | 31466.705
1523.1667 | 36146.2648 |  | 1527 | 31466.705 | 1528.8333 | 32960.582 | 1530.6667 | 19.3294 | 1523.1667 | 19.3294 | 1523.1667 | 31466.705
1540 | 37632.2053 |  | 1543.6667 | 33443.9907 | 1545.5 | 34941.836 | 1547.5 | 9.8411 | 1540 | 9.8411 | 1540 | 33443.9907
1556.8333 | 36146.2648 |  | 1560.5 | 33443.9907 | 1562.5 | 32960.582 | 1564.1667 | 18.698 | 1556.8333 | 18.698 | 1556.8333 | 32960.582
1573.5 | 37632.2053 |  | 1577.3333 | 31466.705 | 1579.3333 | 32960.582 | 1581.1667 | 26.3481 | 1573.5 | 26.3481 | 1573.5 | 31466.705
1590.3333 | 33943.1238 |  | 1594 | 33443.9907 | 1596 | 32960.582 | 1597.6667 | 22.0498 | 1590.3333 | 22.0498 | 1590.3333 | 32960.582
1607.3333 | 33384.7315 |  | 1610.8333 | 33443.9907 | 1612.8333 | 32960.582 | 1614.6667 | 7.143 | 1607.3333 | 7.143 | 1607.3333 | 32960.582
1624 | 34870.672 |  | 1627.6667 | 33443.9907 | 1629.5 | 33452.3241 | 1631.5 | 8.3797 | 1624 | 8.3797 | 1624 | 33443.9907
1640.8333 | 34870.672 |  | 1644.6667 | 33443.9907 | 1646.5 | 32960.582 | 1648.3333 | 11.536 | 1640.8333 | 11.536 | 1640.8333 | 32960.582
1657.5 | 8.9609 |  | 1661.3333 | 28829.3981 | 1663.1667 | 8.2402 | 1665 | 23.797 | 1657.5 | 8.2402 | 1657.5 | 8.2402
1674.5 | 19.4154 |  | 1678 | 27670.8889 | 1680 | 27.8275 | 1681.8333 | 14.0258 | 1674.5 | 14.0258 | 1674.5 | 19.4154
1691.1667 | 20.6485 |  | 1694.8333 | 27670.8889 | 1696.6667 | 19.6573 | 1698.6667 | 12.1747 | 1691.1667 | 12.1747 | 1691.1667 | 19.6573
1708 | 8.3499 |  | 1711.8333 | 28824.3056 | 1713.5 | 20.8346 | 1715.3333 | 24.2515 | 1708 | 8.3499 | 1708 | 8.3499
1724.6667 | 20.2786 |  | 1728.5 | 27670.8889 | 1730.3333 | 21.6132 | 1732.1667 | 21.2505 | 1724.6667 | 20.2786 | 1724.6667 | 20.2786
1741.6667 | 20.2525 |  | 1745.3333 | 29982.8148 | 1747 | 16.4061 | 1749 | 21.0102 | 1741.6667 | 16.4061 | 1741.6667 | 16.4061
1758.3333 | 22.0885 |  | 1762 | 29982.8148 | 1764 | 11.986 | 1765.6667 | 15.4006 | 1758.3333 | 11.986 | 1758.3333 | 11.986
1775.3333 | 18.6055 |  | 1778.8333 | 8369.7655 | 1780.8333 | 9.9107 | 1782.6667 | 17.4165 | 1775.3333 | 9.9107 | 1775.3333 | 9.9107
1791.8333 | 13.3946 |  | 1795.6667 | 63.8154 | 1797.5 | 18.3611 | 1799.3333 | 13.3 | 1791.8333 | 13.3 | 1791.8333 | 13.3946
1808.6667 | 6.8995 |  | 1812.5 | 27.4548 | 1814.3333 | 13.949 | 1816.1667 | 12.2227 | 1808.6667 | 6.8995 | 1808.6667 | 6.8995
1825.5 | 23.8002 |  | 1829.1667 | 51.3825 | 1831 | 8.6432 | 1833 | 14.4949 | 1825.5 | 8.6432 | 1825.5 | 8.6432
1842.5 | 21.2213 |  | 1846 | 49.4651 | 1848 | 16.9385 | 1849.8333 | 8.1665 | 1842.5 | 8.1665 | 1842.5 | 16.9385
1859.1667 | 23.2589 |  | 1862.8333 | 21.9815 | 1864.6667 | 14.3206 | 1866.6667 | 21.5195 | 1859.1667 | 14.3206 | 1859.1667 | 14.3206
1875.8333 | 13.3951 |  | 1879.6667 | 11.9235 | 1881.5 | 20.9263 | 1883.3333 | 15.7216 | 1875.8333 | 11.9235 | 1875.8333 | 11.9235
1892.6667 | 16.5403 |  | 1896.5 | 23.6643 | 1898.3333 | 7.2998 | 1900.1667 | 215.0624 | 1892.6667 | 7.2998 | 1892.6667 | 7.2998
1909.5 | 22.0417 |  | 1913.1667 | 17.0429 | 1915 | 13.3127 | 1917 | 16.5719 | 1909.5 | 13.3127 | 1909.5 | 13.3127
1926.3333 | 11.2474 |  | 1930 | 20.313 | 1932 | 7.2338 | 1933.6667 | 25.2235 | 1926.3333 | 7.2338 | 1926.3333 | 7.2338
1943.1667 | 22.3176 |  | 1946.8333 | 22.9561 | 1948.6667 | 13.5743 | 1950.6667 | 15.0946 | 1943.1667 | 13.5743 | 1943.1667 | 13.5743
1959.8333 | 18.5762 |  | 1963.6667 | 7.9367 | 1965.5 | 26.5552 | 1967.3333 | 21.6554 | 1959.8333 | 7.9367 | 1959.8333 | 7.9367
1976.6667 | 6.1923 |  | 1980.5 | 9.5012 | 1982.3333 | 17.739 | 1984.1667 | 12.5739 | 1976.6667 | 6.1923 | 1976.6667 | 6.1923
1993.5 | 15.409 |  | 1997.1667 | 8.7711 | 1999 | 12.6408 | 2001 | 20.6469 | 1993.5 | 8.7711 | 1993.5 | 8.7711
2010.3333 | 18.5878 |  | 2014 | 15.1438 | 2016 | 11.0321 | 2017.6667 | 26.6178 | 2010.3333 | 11.0321 | 2010.3333 | 11.0321
2027.1667 | 19.0616 |  | 2030.8333 | 23.3106 | 2032.6667 | 18.583 | 2034.6667 | 20.9734 | 2027.1667 | 18.583 | 2027.1667 | 18.583
2043.8333 | 10.6153 |  | 2047.6667 | 13.7029 | 2049.5 | 11.3997 | 2051.3333 | 9.7393 | 2043.8333 | 9.7393 | 2043.8333 | 10.6153
2060.6667 | 14.1425 |  | 2064.5 | 13.2941 | 2066.3333 | 17.4445 | 2068.1667 | 15.9879 | 2060.6667 | 13.2941 | 2060.6667 | 13.2941
2077.5 | 19.287 |  | 2081.1667 | 10.6589 | 2083 | 18.1841 | 2085 | 24.0244 | 2077.5 | 10.6589 | 2077.5 | 10.6589
2094.3333 | 12.6385 |  | 2098 | 10.6681 | 2100 | 6.1243 | 2101.6667 | 17.7896 | 2094.3333 | 6.1243 | 2094.3333 | 6.1243
2111.1667 | 14.1988 |  | 2114.8333 | 10.8443 | 2116.6667 | 21.9882 | 2118.6667 | 23.5663 | 2111.1667 | 10.8443 | 2111.1667 | 10.8443
2127.8333 | 12.152 |  | 2131.6667 | 16.2451 | 2133.5 | 8.5054 | 2135.3333 | 11.5236 | 2127.8333 | 8.5054 | 2127.8333 | 8.5054
2144.6667 | 18.5722 |  | 2148.5 | 17.7175 | 2150.3333 | 11.7307 | 2152.1667 | 22.0249 | 2144.6667 | 11.7307 | 2144.6667 | 11.7307
2161.5 | 17.7705 |  | 2165.1667 | 26.9337 | 2167 | 15.7161 | 2169 | 21.7522 | 2161.5 | 15.7161 | 2161.5 | 15.7161
2178.3333 | 18.2785 |  | 2181.6667 | 23.3932 | 2183.6667 | 11.0104 | 2185.6667 | 28.7158 | 2178.3333 | 11.0104 | 2178.3333 | 11.0104
2195.1667 | 25.0369 |  | 2198.8333 | 10.1212 | 2200.6667 | 19.0343 | 2202.6667 | 19.2491 | 2195.1667 | 10.1212 | 2195.1667 | 10.1212
2211.8333 | 15.3343 |  | 2215.6667 | 17.9874 | 2217.5 | 7.5857 | 2219.3333 | 10.5783 | 2211.8333 | 7.5857 | 2211.8333 | 7.5857
2228.6667 | 13.6619 |  | 2232.5 | 9.4607 | 2234.3333 | 17.8531 | 2236.1667 | 10.6153 | 2228.6667 | 9.4607 | 2228.6667 | 9.4607
2245.5 | 10.8466 |  | 2249.1667 | 19.3732 | 2251 | 19.5277 | 2253 | 8.5862 | 2245.5 | 8.5862 | 2245.5 | 10.8466
2262.3333 | 14.4504 |  | 2266 | 21.471 | 2268 | 17.1125 | 2269.6667 | 11.3075 | 2262.3333 | 11.3075 | 2262.3333 | 14.4504
2279.1667 | 23.997 |  | 2282.8333 | 6.856 | 2284.6667 | 8.5744 | 2286.6667 | 10.852 | 2279.1667 | 6.856 | 2279.1667 | 6.856
2295.8333 | 21.0908 |  | 2299.6667 | 6.2799 | 2301.5 | 14.0044 | 2303.3333 | 4.772 | 2295.8333 | 4.772 | 2295.8333 | 6.2799
2312.6667 | 18.6396 |  | 2316.5 | 15.9486 | 2318.3333 | 18.4219 | 2320.1667 | 15.0813 | 2312.6667 | 15.0813 | 2312.6667 | 15.9486
2329.5 | 12.9768 |  | 2333.1667 | 22.6883 | 2335 | 20.7018 | 2337 | 6.5179 | 2329.5 | 6.5179 | 2329.5 | 12.9768

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 8 |  |  | 2006-07-07 | 12:58
38905.5388 | 1 | 0 | 1 | PVC | 3-C | Conduit
38905.539 | 1 | 0 | 1 | 300 C | 6.1 kW/m2 |  | Conductors
38905.5392 | 1 | 0 | 1
38905.5394 | 1 | 0 | 1
38905.5396 | 1 | 0 | 1
38905.5398 | 1 | 0 | 1
38905.54 | 1 | 0 | 1
38905.5402 | 1 | 0 | 1
38905.5404 | 1 | 0 | 1
38905.5405 | 1 | 0 | 1
38905.5407 | 1 | 0 | 1
38905.5409 | 1 | 0 | 1
38905.5411 | 1 | 0 | 1
38905.5413 | 1 | 0 | 1
38905.5415 | 1 | 0 | 1
38905.5417 | 1 | 0 | 1
38905.5419 | 1 | 0 | 1
38905.5421 | 1 | 0 | 1
38905.5423 | 1 | 0 | 1
38905.5425 | 1 | 0 | 1
38905.5427 | 1 | 0 | 1
38905.5429 | 1 | 0 | 1
38905.5431 | 1 | 0 | 1
38905.5433 | 1 | 0 | 1
38905.5435 | 1 | 0 | 1
38905.5437 | 1 | 0 | 1
38905.5439 | 1 | 0 | 1
38905.5441 | 1 | 0 | 1
38905.5442 | 1 | 0 | 1
38905.5444 | 1 | 0 | 1
38905.5446 | 1 | 0 | 1
38905.5448 | 1 | 0 | 1
38905.545 | 1 | 0 | 1
38905.5452 | 1 | 0 | 1
38905.5454 | 1 | 0 | 1
38905.5456 | 1 | 0 | 1
38905.5458 | 1 | 0 | 1
38905.546 | 1 | 0 | 1
38905.5462 | 1 | 0 | 1
38905.5464 | 1 | 0 | 1
38905.5466 | 1 | 0 | 1
38905.5468 | 1 | 0 | 1
38905.547 | 1 | 0 | 1
38905.5472 | 1 | 0 | 1
38905.5474 | 1 | 0 | 1
38905.5475 | 1 | 0 | 1
38905.5477 | 1 | 0 | 1
38905.5479 | 1 | 0 | 1
38905.5481 | 1 | 0 | 1
38905.5483 | 1 | 0 | 1
38905.5485 | 1 | 0 | 1
38905.5487 | 1 | 0 | 1
38905.5489 | 1 | 0 | 1
38905.5491 | 1 | 0 | 1
38905.5493 | 1 | 0 | 1
38905.5495 | 1 | 0 | 1
38905.5497 | 1 | 0 | 1
38905.5499 | 1 | 0 | 1
38905.5501 | 1 | 0 | 1
38905.5503 | 1 | 0 | 1
38905.5505 | 1 | 0 | 1
38905.5507 | 1 | 0 | 1
38905.5509 | 1 | 0 | 1
38905.5511 | 1 | 0 | 1
38905.5512 | 1 | 0 | 1
38905.5514 | 1 | 0 | 1
38905.5516 | 1 | 0 | 1
38905.5518 | 1 | 0 | 1
38905.552 | 1 | 0 | 1
38905.5522 | 1 | 0 | 1
38905.5524 | 1 | 0 | 1
38905.5526 | 1 | 0 | 1
38905.5528 | 1 | 0 | 1
38905.553 | 1 | 0 | 1
38905.5532 | 1 | 0 | 1
38905.5534 | 1 | 0 | 1
38905.5536 | 1 | 0 | 1
38905.5538 | 1 | 0 | 1
38905.554 | 1 | 0 | 1
38905.5542 | 1 | 0 | 1
38905.5544 | 1 | 0 | 1
38905.5545 | 7 | 0 | 1
38905.5547 | 9 | 0 | 1
38905.5551 | 8 | 0 | 1
38905.5553 | 9 | 0 | 1
38905.5555 | 9 | 0 | 1
38905.5557 | 9 | 0 | 1
38905.5559 | 9 | 0 | 1
38905.5561 | 9 | 0 | 1
38905.5563 | 9 | 0 | 1
38905.5565 | 9 | 0 | 1
38905.5567 | 9 | 0 | 1
38905.5569 | 9 | 0 | 1
38905.5571 | 9 | 0 | 1
38905.5573 | 9 | 0 | 1
38905.5575 | 9 | 0 | 1
38905.5577 | 9 | 0 | 1
38905.5578 | 9 | 0 | 1
38905.558 | 9 | 0 | 1
38905.5582 | 9 | 0 | 1
38905.5584 | 10 | 0 | 1
38905.5586 | 9 | 0 | 1
38905.5588 | 9 | 0 | 1
38905.559 | 9 | 0 | 1
38905.5592 | 2254 | 0 | 1
38905.5594 | 1995 | 0 | 1
38905.5596 | 2374 | 0 | 1
38905.5598 | 2231 | 0 | 1
38905.56 | 2269 | 0 | 1
38905.5602 | 2014 | 0 | 1
38905.5604 | 2103 | 0 | 1
38905.5606 | 2439 | 0 | 1
38905.5608 | 2289 | 0 | 1
38905.561 | 2239 | 0 | 1
38905.5612 | 2167 | 0 | 1
38905.5614 | 1983 | 0 | 1
38905.5616 | 1857 | 0 | 1
38905.5617 | 2107 | 0 | 1
38905.5619 | 2151 | 0 | 1
38905.5621 | 2034 | 0 | 1
38905.5623 | 2082 | 0 | 1
38905.5625 | 1908 | 1 | 1
38905.5627 | 2064 | 0 | 1
38905.5629 | 2378 | 2 | 1
38905.5631 | 2392 | 2 | 1
38905.5633 | 1925 | 1 | 1
38905.5635 | 1996 | 2 | 1
38905.5637 | 2091 | 3 | 1
38905.5639 | 2221 | 5 | 1
38905.5641 | 2104 | 7 | 1
38905.5643 | 2003 | 8 | 1
38905.5645 | 2223 | 11 | 1
38905.5647 | 2318 | 14 | 1
38905.5648 | 1861 | 12 | 1
38905.565 | 2161 | 17 | 1
38905.5652 | 1939 | 8 | 1
38905.5654 | 1978 | 27 | 1
38905.5656 | 2169 | 0 | 1
38905.5658 | 2274 | 0 | 1
38905.566 | 1940 | 0 | 1
38905.5662 | 2155 | 0 | 1
38905.5664 | 1965 | 1 | 1
38905.5666 | 2016 | 0 | 1
38905.5668 | 2314 | 0 | 1
38905.567 | 2243 | 0 | 1
38905.5388 | 1 | 0 | 2
38905.539 | 1 | 0 | 2
38905.5392 | 1 | 0 | 2
38905.5394 | 1 | 0 | 2
38905.5396 | 1 | 0 | 2
38905.5398 | 1 | 0 | 2
38905.54 | 1 | 0 | 2
38905.5402 | 1 | 0 | 2
38905.5404 | 1 | 0 | 2
38905.5406 | 1 | 0 | 2
38905.5408 | 1 | 0 | 2
38905.5409 | 1 | 0 | 2
38905.5411 | 1 | 0 | 2
38905.5413 | 1 | 0 | 2
38905.5415 | 1 | 0 | 2
38905.5417 | 1 | 0 | 2
38905.5419 | 1 | 0 | 2
38905.5421 | 1 | 0 | 2
38905.5423 | 1 | 0 | 2
38905.5425 | 1 | 0 | 2
38905.5427 | 1 | 0 | 2
38905.5429 | 1 | 0 | 2
38905.5431 | 1 | 0 | 2
38905.5433 | 1 | 0 | 2
38905.5435 | 1 | 0 | 2
38905.5437 | 1 | 0 | 2
38905.5439 | 1 | 0 | 2
38905.5441 | 1 | 0 | 2
38905.5443 | 1 | 0 | 2
38905.5445 | 1 | 0 | 2
38905.5447 | 1 | 0 | 2
38905.5448 | 1 | 0 | 2
38905.545 | 1 | 0 | 2
38905.5452 | 1 | 0 | 2
38905.5454 | 1 | 0 | 2
38905.5456 | 1 | 0 | 2
38905.5458 | 1 | 0 | 2
38905.546 | 1 | 0 | 2
38905.5462 | 1 | 0 | 2
38905.5464 | 1 | 0 | 2
38905.5466 | 1 | 0 | 2
38905.5468 | 1 | 0 | 2
38905.547 | 1 | 0 | 2
38905.5472 | 1 | 0 | 2
38905.5474 | 1 | 0 | 2
38905.5476 | 1 | 0 | 2
38905.5478 | 1 | 0 | 2
38905.548 | 1 | 0 | 2
38905.5481 | 1 | 0 | 2
38905.5483 | 1 | 0 | 2
38905.5485 | 1 | 0 | 2
38905.5487 | 1 | 0 | 2
38905.5489 | 1 | 0 | 2
38905.5491 | 1 | 0 | 2
38905.5493 | 1 | 0 | 2
38905.5495 | 2 | 0 | 2
38905.5497 | 1 | 0 | 2
38905.5499 | 1 | 0 | 2
38905.5501 | 1 | 0 | 2
38905.5503 | 1 | 0 | 2
38905.5505 | 1 | 0 | 2
38905.5507 | 1 | 0 | 2
38905.5509 | 1 | 0 | 2
38905.5511 | 1 | 0 | 2
38905.5513 | 1 | 0 | 2
38905.5515 | 1 | 0 | 2
38905.5516 | 1 | 0 | 2
38905.5518 | 1 | 0 | 2
38905.552 | 1 | 0 | 2
38905.5522 | 1 | 0 | 2
38905.5524 | 1 | 0 | 2
38905.5526 | 1 | 0 | 2
38905.5528 | 1 | 0 | 2
38905.553 | 1 | 0 | 2
38905.5532 | 1 | 0 | 2
38905.5534 | 1 | 0 | 2
38905.5536 | 1 | 0 | 2
38905.5538 | 1 | 0 | 2
38905.554 | 1 | 0 | 2
38905.5542 | 1 | 0 | 2
38905.5544 | 1 | 0 | 2
38905.5546 | 4 | 0 | 2
38905.5548 | 6 | 0 | 2
38905.555 | 7 | 0 | 2
38905.5552 | 7 | 0 | 2
38905.5553 | 8 | 0 | 2
38905.5555 | 8 | 0 | 2
38905.5557 | 9 | 0 | 2
38905.5559 | 8 | 0 | 2
38905.5561 | 9 | 0 | 2
38905.5563 | 9 | 0 | 2
38905.5565 | 8 | 0 | 2
38905.5567 | 8 | 1 | 2
38905.5569 | 8 | 0 | 2
38905.5571 | 8 | 0 | 2
38905.5573 | 8 | 0 | 2
38905.5575 | 8 | 0 | 2
38905.5577 | 8 | 0 | 2
38905.5579 | 8 | 0 | 2
38905.5581 | 8 | 0 | 2
38905.5583 | 8 | 0 | 2
38905.5584 | 8 | 0 | 2
38905.5586 | 8 | 0 | 2
38905.5588 | 8 | 0 | 2
38905.559 | 8 | 0 | 2
38905.5592 | 9 | 0 | 2
38905.5594 | 9 | 0 | 2
38905.5596 | 9 | 0 | 2
38905.5598 | 9 | 0 | 2
38905.56 | 9 | 0 | 2
38905.5602 | 9 | 0 | 2
38905.5604 | 9 | 0 | 2
38905.5606 | 1254 | 0 | 2
38905.5608 | 1039 | 0 | 2
38905.561 | 2060 | 0 | 2
38905.5612 | 1747 | 0 | 2
38905.5614 | 1658 | 0 | 2
38905.5616 | 1977 | 0 | 2
38905.5618 | 2269 | 0 | 2
38905.562 | 2034 | 0 | 2
38905.5621 | 2116 | 0 | 2
38905.5623 | 2162 | 0 | 2
38905.5625 | 1895 | 1 | 2
38905.5627 | 2312 | 1 | 2
38905.5629 | 2382 | 1 | 2
38905.5631 | 2372 | 1 | 2
38905.5633 | 2267 | 2 | 2
38905.5635 | 2023 | 2 | 2
38905.5637 | 2429 | 4 | 2
38905.5639 | 2218 | 7 | 2
38905.5641 | 2193 | 7 | 2
38905.5643 | 2109 | 8 | 2
38905.5645 | 2289 | 11 | 2
38905.5647 | 2123 | 14 | 2
38905.5649 | 2172 | 13 | 2
38905.5651 | 2045 | 17 | 2
38905.5653 | 2210 | 23 | 2
38905.5655 | 2256 | 32 | 2
38905.5656 | 2370 | 0 | 2
38905.5658 | 2111 | 0 | 2
38905.566 | 2233 | 0 | 2
38905.5662 | 1969 | 0 | 2
38905.5664 | 2488 | 1 | 2
38905.5666 | 2465 | 0 | 2
38905.5668 | 2353 | 0 | 2
38905.567 | 1942 | 0 | 2
38905.5388 | 1 | 0 | 3
38905.539 | 1 | 0 | 3
38905.5392 | 1 | 0 | 3
38905.5394 | 1 | 0 | 3
38905.5396 | 1 | 0 | 3
38905.5398 | 1 | 0 | 3
38905.54 | 1 | 0 | 3
38905.5402 | 1 | 0 | 3
38905.5404 | 1 | 0 | 3
38905.5406 | 1 | 0 | 3
38905.5408 | 1 | 0 | 3
38905.541 | 1 | 0 | 3
38905.5412 | 1 | 0 | 3
38905.5414 | 1 | 0 | 3
38905.5416 | 1 | 0 | 3
38905.5417 | 1 | 0 | 3
38905.5419 | 1 | 0 | 3
38905.5421 | 1 | 0 | 3
38905.5423 | 1 | 0 | 3
38905.5425 | 1 | 0 | 3
38905.5427 | 1 | 0 | 3
38905.5429 | 1 | 0 | 3
38905.5431 | 1 | 0 | 3
38905.5433 | 1 | 0 | 3
38905.5435 | 1 | 0 | 3
38905.5437 | 1 | 0 | 3
38905.5439 | 1 | 0 | 3
38905.5441 | 1 | 0 | 3
38905.5443 | 1 | 0 | 3
38905.5445 | 1 | 0 | 3
38905.5447 | 1 | 0 | 3
38905.5449 | 1 | 0 | 3
38905.5451 | 1 | 0 | 3
38905.5452 | 1 | 0 | 3
38905.5454 | 1 | 0 | 3
38905.5456 | 1 | 0 | 3
38905.5458 | 1 | 0 | 3
38905.546 | 1 | 0 | 3
38905.5462 | 1 | 0 | 3
38905.5464 | 1 | 0 | 3
38905.5466 | 1 | 0 | 3
38905.5468 | 1 | 0 | 3
38905.547 | 1 | 0 | 3
38905.5472 | 1 | 0 | 3
38905.5474 | 1 | 0 | 3
38905.5476 | 1 | 0 | 3
38905.5478 | 1 | 0 | 3
38905.548 | 1 | 0 | 3
38905.5482 | 1 | 0 | 3
38905.5484 | 1 | 0 | 3
38905.5486 | 1 | 0 | 3
38905.5488 | 1 | 0 | 3
38905.5489 | 1 | 0 | 3
38905.5491 | 1 | 0 | 3
38905.5493 | 1 | 0 | 3
38905.5495 | 1 | 0 | 3
38905.5497 | 1 | 0 | 3
38905.5499 | 1 | 0 | 3
38905.5501 | 1 | 0 | 3
38905.5503 | 1 | 0 | 3
38905.5505 | 1 | 0 | 3
38905.5507 | 1 | 0 | 3
38905.5509 | 1 | 0 | 3
38905.5511 | 1 | 0 | 3
38905.5513 | 1 | 1 | 3
38905.5515 | 1 | 0 | 3
38905.5517 | 1 | 0 | 3
38905.5519 | 1 | 0 | 3
38905.552 | 1 | 0 | 3
38905.5522 | 1 | 0 | 3
38905.5524 | 1 | 0 | 3
38905.5526 | 1 | 0 | 3
38905.5528 | 1 | 0 | 3
38905.553 | 1 | 0 | 3
38905.5532 | 1 | 0 | 3
38905.5534 | 1 | 0 | 3
38905.5536 | 1 | 0 | 3
38905.5538 | 1 | 0 | 3
38905.554 | 1 | 0 | 3
38905.5542 | 1 | 0 | 3
38905.5544 | 1 | 0 | 3
38905.5546 | 3 | 0 | 3
38905.5548 | 4 | 0 | 3
38905.555 | 6 | 0 | 3
38905.5552 | 6 | 0 | 3
38905.5554 | 6 | 0 | 3
38905.5556 | 8 | 0 | 3
38905.5558 | 8 | 0 | 3
38905.5559 | 8 | 0 | 3
38905.5561 | 7 | 0 | 3
38905.5563 | 8 | 0 | 3
38905.5565 | 8 | 0 | 3
38905.5567 | 7 | 0 | 3
38905.5569 | 8 | 0 | 3
38905.5571 | 8 | 0 | 3
38905.5573 | 8 | 0 | 3
38905.5575 | 7 | 0 | 3
38905.5577 | 8 | 0 | 3
38905.5579 | 7 | 0 | 3
38905.5581 | 8 | 0 | 3
38905.5583 | 7 | 0 | 3
38905.5585 | 7 | 0 | 3
38905.5587 | 8 | 0 | 3
38905.5589 | 7 | 0 | 3
38905.5591 | 7 | 0 | 3
38905.5592 | 2304 | 0 | 3
38905.5594 | 1999 | 25 | 3
38905.5596 | 1874 | 19 | 3
38905.5598 | 2338 | 4 | 3
38905.56 | 1883 | 1 | 3
38905.5602 | 2378 | 2 | 3
38905.5604 | 2090 | 2 | 3
38905.5606 | 1944 | 1 | 3
38905.5608 | 2427 | 1 | 3
38905.561 | 2425 | 1 | 3
38905.5612 | 2008 | 0 | 3
38905.5614 | 2181 | 0 | 3
38905.5616 | 2031 | 18 | 3
38905.5618 | 2088 | 19 | 3
38905.562 | 2069 | 0 | 3
38905.5622 | 1992 | 0 | 3
38905.5624 | 2223 | 0 | 3
38905.5625 | 1987 | 0 | 3
38905.5627 | 2428 | 1 | 3
38905.5629 | 2346 | 1 | 3
38905.5631 | 1920 | 1 | 3
38905.5633 | 2117 | 2 | 3
38905.5635 | 2322 | 3 | 3
38905.5637 | 2413 | 4 | 3
38905.5639 | 2355 | 6 | 3
38905.5641 | 2328 | 8 | 3
38905.5643 | 2298 | 9 | 3
38905.5645 | 2384 | 11 | 3
38905.5647 | 2291 | 14 | 3
38905.5649 | 2160 | 12 | 3
38905.5651 | 2376 | 20 | 3
38905.5653 | 2121 | 22 | 3
38905.5655 | 1934 | 28 | 3
38905.5657 | 2402 | 0 | 3
38905.5659 | 2480 | 1 | 3
38905.5661 | 2429 | 1 | 3
38905.5663 | 2290 | 0 | 3
38905.5664 | 1928 | 0 | 3
38905.5666 | 2253 | 0 | 3
38905.5668 | 1976 | 0 | 3
38905.567 | 1990 | 0 | 3
38905.5389 | 1 | 0 | 4
38905.539 | 1 | 0 | 4
38905.5392 | 1 | 0 | 4
38905.5394 | 1 | 0 | 4
38905.5396 | 1 | 0 | 4
38905.5398 | 1 | 0 | 4
38905.54 | 1 | 0 | 4
38905.5402 | 1 | 0 | 4
38905.5404 | 1 | 0 | 4
38905.5406 | 1 | 0 | 4
38905.5408 | 1 | 0 | 4
38905.541 | 1 | 0 | 4
38905.5412 | 1 | 0 | 4
38905.5414 | 1 | 0 | 4
38905.5416 | 1 | 0 | 4
38905.5418 | 1 | 0 | 4
38905.542 | 1 | 0 | 4
38905.5422 | 1 | 0 | 4
38905.5423 | 1 | 0 | 4
38905.5425 | 1 | 0 | 4
38905.5427 | 1 | 0 | 4
38905.5429 | 1 | 0 | 4
38905.5431 | 1 | 0 | 4
38905.5433 | 1 | 0 | 4
38905.5435 | 1 | 0 | 4
38905.5437 | 1 | 0 | 4
38905.5439 | 1 | 0 | 4
38905.5441 | 1 | 0 | 4
38905.5443 | 1 | 0 | 4
38905.5445 | 1 | 0 | 4
38905.5447 | 1 | 0 | 4
38905.5449 | 1 | 0 | 4
38905.5451 | 1 | 0 | 4
38905.5453 | 1 | 0 | 4
38905.5455 | 1 | 0 | 4
38905.5456 | 1 | 0 | 4
38905.5458 | 1 | 0 | 4
38905.546 | 1 | 0 | 4
38905.5462 | 1 | 0 | 4
38905.5464 | 1 | 0 | 4
38905.5466 | 1 | 0 | 4
38905.5468 | 1 | 0 | 4
38905.547 | 1 | 0 | 4
38905.5472 | 1 | 0 | 4
38905.5474 | 1 | 0 | 4
38905.5476 | 1 | 0 | 4
38905.5478 | 1 | 0 | 4
38905.548 | 1 | 0 | 4
38905.5482 | 1 | 0 | 4
38905.5484 | 1 | 0 | 4
38905.5486 | 1 | 0 | 4
38905.5488 | 1 | 0 | 4
38905.549 | 1 | 0 | 4
38905.5492 | 1 | 0 | 4
38905.5494 | 1 | 0 | 4
38905.5495 | 1 | 0 | 4
38905.5497 | 1 | 0 | 4
38905.5499 | 1 | 0 | 4
38905.5501 | 1 | 0 | 4
38905.5503 | 1 | 0 | 4
38905.5505 | 1 | 0 | 4
38905.5507 | 1 | 0 | 4
38905.5509 | 1 | 0 | 4
38905.5511 | 1 | 0 | 4
38905.5513 | 1 | 0 | 4
38905.5515 | 1 | 0 | 4
38905.5517 | 1 | 0 | 4
38905.5519 | 1 | 0 | 4
38905.5521 | 1 | 0 | 4
38905.5523 | 1 | 0 | 4
38905.5525 | 1 | 0 | 4
38905.5527 | 1 | 0 | 4
38905.5528 | 1 | 0 | 4
38905.553 | 1 | 0 | 4
38905.5532 | 1 | 0 | 4
38905.5534 | 1 | 0 | 4
38905.5536 | 1 | 0 | 4
38905.5538 | 1 | 0 | 4
38905.554 | 1 | 0 | 4
38905.5542 | 1 | 0 | 4
38905.5544 | 1 | 0 | 4
38905.5546 | 3 | 0 | 4
38905.5548 | 3 | 0 | 4
38905.555 | 4 | 0 | 4
38905.5552 | 4 | 0 | 4
38905.5554 | 5 | 0 | 4
38905.5556 | 6 | 0 | 4
38905.5558 | 7 | 0 | 4
38905.556 | 7 | 0 | 4
38905.5562 | 7 | 0 | 4
38905.5563 | 7 | 0 | 4
38905.5565 | 7 | 0 | 4
38905.5567 | 7 | 0 | 4
38905.5569 | 7 | 0 | 4
38905.5571 | 7 | 0 | 4
38905.5573 | 7 | 0 | 4
38905.5575 | 7 | 0 | 4
38905.5577 | 7 | 0 | 4
38905.5579 | 6 | 0 | 4
38905.5581 | 7 | 0 | 4
38905.5583 | 7 | 0 | 4
38905.5585 | 7 | 0 | 4
38905.5587 | 7 | 0 | 4
38905.5589 | 6 | 0 | 4
38905.5591 | 7 | 0 | 4
38905.5593 | 2386 | 11 | 4
38905.5595 | 2087 | 28 | 4
38905.5597 | 2262 | 31 | 4
38905.5598 | 2282 | 2 | 4
38905.56 | 2051 | 1 | 4
38905.5602 | 2135 | 1 | 4
38905.5604 | 2330 | 2 | 4
38905.5606 | 2446 | 1 | 4
38905.5608 | 1992 | 1 | 4
38905.561 | 2400 | 1 | 4
38905.5612 | 2093 | 0 | 4
38905.5614 | 2191 | 1 | 4
38905.5616 | 2282 | 20 | 4
38905.5618 | 2024 | 22 | 4
38905.562 | 2329 | 1 | 4
38905.5622 | 1971 | 0 | 4
38905.5624 | 2390 | 1 | 4
38905.5626 | 1902 | 1 | 4
38905.5628 | 1950 | 1 | 4
38905.563 | 2229 | 1 | 4
38905.5631 | 1924 | 1 | 4
38905.5633 | 2444 | 2 | 4
38905.5635 | 2415 | 4 | 4
38905.5637 | 2049 | 4 | 4
38905.5639 | 1867 | 5 | 4
38905.5641 | 2355 | 8 | 4
38905.5643 | 2384 | 9 | 4
38905.5645 | 1857 | 8 | 4
38905.5647 | 2372 | 15 | 4
38905.5649 | 2076 | 14 | 4
38905.5651 | 2363 | 21 | 4
38905.5653 | 2337 | 25 | 4
38905.5655 | 1994 | 27 | 4
38905.5657 | 2461 | 0 | 4
38905.5659 | 1993 | 0 | 4
38905.5661 | 2010 | 0 | 4
38905.5663 | 2184 | 0 | 4
38905.5665 | 2059 | 0 | 4
38905.5667 | 2213 | 0 | 4
38905.5668 | 1977 | 0 | 4
38905.567 | 2211 | 0 | 4
38905.5389 | 1 | 0 | 5
38905.5391 | 1 | 0 | 5
38905.5393 | 1 | 0 | 5
38905.5394 | 1 | 0 | 5
38905.5396 | 1 | 0 | 5
38905.5398 | 1 | 0 | 5
38905.54 | 1 | 0 | 5
38905.5402 | 1 | 0 | 5
38905.5404 | 1 | 0 | 5
38905.5406 | 1 | 0 | 5
38905.5408 | 1 | 0 | 5
38905.541 | 1 | 0 | 5
38905.5412 | 1 | 0 | 5
38905.5414 | 1 | 0 | 5
38905.5416 | 1 | 0 | 5
38905.5418 | 1 | 0 | 5
38905.542 | 1 | 0 | 5
38905.5422 | 1 | 0 | 5
38905.5424 | 1 | 0 | 5
38905.5426 | 1 | 0 | 5
38905.5428 | 1 | 0 | 5
38905.543 | 1 | 0 | 5
38905.5431 | 1 | 0 | 5
38905.5433 | 1 | 0 | 5
38905.5435 | 1 | 0 | 5
38905.5437 | 1 | 0 | 5
38905.5439 | 1 | 0 | 5
38905.5441 | 1 | 0 | 5
38905.5443 | 1 | 0 | 5
38905.5445 | 1 | 0 | 5
38905.5447 | 1 | 0 | 5
38905.5449 | 1 | 0 | 5
38905.5451 | 1 | 0 | 5
38905.5453 | 1 | 0 | 5
38905.5455 | 2 | 0 | 5
38905.5457 | 1 | 0 | 5
38905.5459 | 1 | 0 | 5
38905.5461 | 1 | 0 | 5
38905.5462 | 1 | 0 | 5
38905.5464 | 1 | 0 | 5
38905.5466 | 1 | 0 | 5
38905.5468 | 1 | 0 | 5
38905.547 | 1 | 0 | 5
38905.5472 | 1 | 0 | 5
38905.5474 | 1 | 0 | 5
38905.5476 | 1 | 0 | 5
38905.5478 | 1 | 0 | 5
38905.548 | 1 | 0 | 5
38905.5482 | 1 | 0 | 5
38905.5484 | 1 | 0 | 5
38905.5486 | 1 | 0 | 5
38905.5488 | 1 | 0 | 5
38905.549 | 1 | 0 | 5
38905.5492 | 1 | 0 | 5
38905.5494 | 1 | 0 | 5
38905.5496 | 1 | 0 | 5
38905.5498 | 1 | 0 | 5
38905.5499 | 1 | 0 | 5
38905.5501 | 1 | 0 | 5
38905.5503 | 1 | 0 | 5
38905.5505 | 1 | 0 | 5
38905.5507 | 1 | 0 | 5
38905.5509 | 1 | 0 | 5
38905.5511 | 1 | 0 | 5
38905.5513 | 1 | 0 | 5
38905.5515 | 1 | 0 | 5
38905.5517 | 1 | 0 | 5
38905.5519 | 1 | 0 | 5
38905.5521 | 1 | 0 | 5
38905.5523 | 1 | 0 | 5
38905.5525 | 1 | 0 | 5
38905.5527 | 1 | 0 | 5
38905.5529 | 1 | 0 | 5
38905.5531 | 1 | 0 | 5
38905.5533 | 1 | 0 | 5
38905.5534 | 1 | 0 | 5
38905.5536 | 1 | 0 | 5
38905.5538 | 1 | 0 | 5
38905.554 | 1 | 0 | 5
38905.5542 | 1 | 0 | 5
38905.5544 | 1 | 0 | 5
38905.5546 | 2 | 0 | 5
38905.5548 | 3 | 0 | 5
38905.555 | 4 | 0 | 5
38905.5552 | 3 | 0 | 5
38905.5554 | 3 | 0 | 5
38905.5556 | 5 | 0 | 5
38905.5558 | 6 | 0 | 5
38905.556 | 6 | 0 | 5
38905.5562 | 6 | 0 | 5
38905.5564 | 6 | 0 | 5
38905.5566 | 6 | 0 | 5
38905.5567 | 6 | 1 | 5
38905.5569 | 6 | 0 | 5
38905.5571 | 6 | 0 | 5
38905.5573 | 6 | 0 | 5
38905.5575 | 5 | 0 | 5
38905.5577 | 5 | 0 | 5
38905.5579 | 5 | 0 | 5
38905.5581 | 5 | 0 | 5
38905.5583 | 5 | 0 | 5
38905.5585 | 6 | 0 | 5
38905.5587 | 6 | 0 | 5
38905.5589 | 6 | 0 | 5
38905.5591 | 6 | 0 | 5
38905.5593 | 2317 | 14 | 5
38905.5595 | 2360 | 31 | 5
38905.5597 | 2131 | 24 | 5
38905.5599 | 2348 | 2 | 5
38905.5601 | 2111 | 1 | 5
38905.5603 | 1893 | 1 | 5
38905.5604 | 1951 | 1 | 5
38905.5606 | 2006 | 1 | 5
38905.5608 | 1945 | 1 | 5
38905.561 | 2348 | 1 | 5
38905.5612 | 1891 | 1 | 5
38905.5614 | 2026 | 1 | 5
38905.5616 | 2280 | 23 | 5
38905.5618 | 2465 | 1 | 5
38905.562 | 2209 | 1 | 5
38905.5622 | 2112 | 0 | 5
38905.5624 | 2457 | 1 | 5
38905.5626 | 2260 | 1 | 5
38905.5628 | 1890 | 1 | 5
38905.563 | 2330 | 1 | 5
38905.5632 | 2237 | 2 | 5
38905.5634 | 2329 | 2 | 5
38905.5636 | 2011 | 3 | 5
38905.5638 | 2315 | 5 | 5
38905.5639 | 2022 | 5 | 5
38905.5641 | 1909 | 7 | 5
38905.5643 | 2418 | 9 | 5
38905.5645 | 2006 | 8 | 5
38905.5647 | 2117 | 11 | 5
38905.5649 | 2407 | 13 | 5
38905.5651 | 1913 | 16 | 5
38905.5653 | 2396 | 5 | 5
38905.5655 | 2216 | 31 | 5
38905.5657 | 1963 | 0 | 5
38905.5659 | 1909 | 0 | 5
38905.5661 | 2469 | 1 | 5
38905.5663 | 2104 | 0 | 5
38905.5665 | 2208 | 1 | 5
38905.5667 | 1938 | 0 | 5
38905.5669 | 2048 | 0 | 5
38905.5671 | 2441 | 1 | 5
38905.5389 | 1 | 0 | 6
38905.5391 | 1 | 0 | 6
38905.5393 | 1 | 0 | 6
38905.5395 | 1 | 0 | 6
38905.5397 | 1 | 0 | 6
38905.5398 | 1 | 0 | 6
38905.54 | 1 | 0 | 6
38905.5402 | 1 | 0 | 6
38905.5404 | 1 | 0 | 6
38905.5406 | 2 | 0 | 6
38905.5408 | 1 | 0 | 6
38905.541 | 1 | 0 | 6
38905.5412 | 1 | 0 | 6
38905.5414 | 1 | 0 | 6
38905.5416 | 1 | 0 | 6
38905.5418 | 1 | 0 | 6
38905.542 | 1 | 0 | 6
38905.5422 | 1 | 0 | 6
38905.5424 | 1 | 0 | 6
38905.5426 | 1 | 0 | 6
38905.5428 | 1 | 0 | 6
38905.543 | 1 | 0 | 6
38905.5432 | 1 | 0 | 6
38905.5434 | 1 | 0 | 6
38905.5435 | 1 | 0 | 6
38905.5437 | 1 | 0 | 6
38905.5439 | 1 | 0 | 6
38905.5441 | 1 | 0 | 6
38905.5443 | 1 | 0 | 6
38905.5447 | 1 | 0 | 6
38905.5449 | 1 | 0 | 6
38905.5451 | 1 | 0 | 6
38905.5453 | 1 | 0 | 6
38905.5455 | 1 | 0 | 6
38905.5457 | 1 | 0 | 6
38905.5459 | 1 | 0 | 6
38905.5461 | 1 | 0 | 6
38905.5463 | 1 | 0 | 6
38905.5465 | 1 | 0 | 6
38905.5467 | 1 | 0 | 6
38905.5469 | 1 | 0 | 6
38905.547 | 1 | 0 | 6
38905.5472 | 1 | 0 | 6
38905.5474 | 1 | 0 | 6
38905.5476 | 1 | 0 | 6
38905.5478 | 1 | 0 | 6
38905.548 | 1 | 0 | 6
38905.5482 | 1 | 0 | 6
38905.5484 | 1 | 0 | 6
38905.5486 | 1 | 0 | 6
38905.5488 | 1 | 0 | 6
38905.549 | 1 | 0 | 6
38905.5492 | 1 | 0 | 6
38905.5494 | 1 | 0 | 6
38905.5496 | 1 | 0 | 6
38905.5498 | 1 | 0 | 6
38905.55 | 1 | 0 | 6
38905.5502 | 1 | 0 | 6
38905.5503 | 1 | 0 | 6
38905.5505 | 1 | 0 | 6
38905.5507 | 1 | 0 | 6
38905.5509 | 1 | 0 | 6
38905.5511 | 1 | 0 | 6
38905.5513 | 1 | 0 | 6
38905.5515 | 1 | 0 | 6
38905.5517 | 1 | 0 | 6
38905.5519 | 1 | 0 | 6
38905.5521 | 1 | 0 | 6
38905.5523 | 1 | 0 | 6
38905.5525 | 1 | 0 | 6
38905.5527 | 1 | 0 | 6
38905.5529 | 1 | 0 | 6
38905.5531 | 1 | 0 | 6
38905.5533 | 1 | 0 | 6
38905.5535 | 1 | 0 | 6
38905.5537 | 1 | 0 | 6
38905.5539 | 1 | 0 | 6
38905.5541 | 1 | 0 | 6
38905.5542 | 1 | 0 | 6
38905.5544 | 1 | 0 | 6
38905.5546 | 1438 | 0 | 6
38905.5548 | 1619 | 0 | 6
38905.555 | 1611 | 0 | 6
38905.5552 | 1848 | 0 | 6
38905.5554 | 1941 | 0 | 6
38905.5556 | 2381 | 0 | 6
38905.5558 | 2148 | 0 | 6
38905.556 | 1852 | 0 | 6
38905.5562 | 1892 | 0 | 6
38905.5564 | 2405 | 0 | 6
38905.5566 | 2360 | 0 | 6
38905.5568 | 2178 | 0 | 6
38905.557 | 2111 | 0 | 6
38905.5572 | 2141 | 0 | 6
38905.5573 | 1881 | 0 | 6
38905.5575 | 1905 | 0 | 6
38905.5577 | 2358 | 0 | 6
38905.5579 | 2354 | 0 | 6
38905.5581 | 2347 | 0 | 6
38905.5583 | 1861 | 0 | 6
38905.5585 | 2055 | 0 | 6
38905.5587 | 2408 | 0 | 6
38905.5589 | 2261 | 0 | 6
38905.5591 | 2193 | 0 | 6
38905.5593 | 1835 | 14 | 6
38905.5595 | 2229 | 31 | 6
38905.5597 | 2304 | 27 | 6
38905.5599 | 2135 | 2 | 6
38905.5601 | 2110 | 1 | 6
38905.5603 | 2107 | 1 | 6
38905.5605 | 1936 | 1 | 6
38905.5607 | 2125 | 1 | 6
38905.5608 | 2205 | 1 | 6
38905.561 | 2177 | 1 | 6
38905.5612 | 1953 | 0 | 6
38905.5614 | 2371 | 17 | 6
38905.5616 | 1982 | 0 | 6
38905.5618 | 2337 | 0 | 6
38905.562 | 1909 | 1 | 6
38905.5622 | 2038 | 0 | 6
38905.5624 | 1895 | 0 | 6
38905.5626 | 1947 | 0 | 6
38905.5628 | 1886 | 1 | 6
38905.563 | 2377 | 1 | 6
38905.5632 | 2390 | 2 | 6
38905.5634 | 1912 | 2 | 6
38905.5636 | 1998 | 2 | 6
38905.5638 | 2327 | 5 | 6
38905.564 | 2162 | 5 | 6
38905.5642 | 1867 | 6 | 6
38905.5644 | 1915 | 8 | 6
38905.5645 | 2016 | 10 | 6
38905.5647 | 2099 | 12 | 6
38905.5649 | 1999 | 13 | 6
38905.5651 | 1847 | 17 | 6
38905.5653 | 2053 | 24 | 6
38905.5655 | 2120 | 29 | 6
38905.5657 | 2362 | 0 | 6
38905.5659 | 1912 | 0 | 6
38905.5661 | 2355 | 1 | 6
38905.5663 | 2468 | 0 | 6
38905.5665 | 2409 | 1 | 6
38905.5667 | 2434 | 1 | 6
38905.5669 | 2240 | 0 | 6
38905.5671 | 2340 | 0 | 6
38905.5389 | 1 | 0 | 7
38905.5391 | 1 | 0 | 7
38905.5393 | 1 | 0 | 7
38905.5395 | 1 | 0 | 7
38905.5397 | 1 | 0 | 7
38905.5399 | 1 | 0 | 7
38905.5401 | 1 | 0 | 7
38905.5403 | 1 | 0 | 7
38905.5405 | 1 | 0 | 7
38905.5406 | 2 | 0 | 7
38905.5408 | 1 | 0 | 7
38905.541 | 1 | 0 | 7
38905.5412 | 1 | 0 | 7
38905.5414 | 1 | 1 | 7
38905.5416 | 1 | 0 | 7
38905.5418 | 1 | 0 | 7
38905.542 | 1 | 0 | 7
38905.5422 | 1 | 0 | 7
38905.5424 | 1 | 0 | 7
38905.5426 | 1 | 0 | 7
38905.5428 | 1 | 0 | 7
38905.543 | 1 | 0 | 7
38905.5432 | 1 | 0 | 7
38905.5434 | 1 | 0 | 7
38905.5436 | 1 | 0 | 7
38905.5438 | 1 | 0 | 7
38905.544 | 1 | 0 | 7
38905.5441 | 1 | 0 | 7
38905.5443 | 1 | 0 | 7
38905.5445 | 1 | 0 | 7
38905.5447 | 1 | 0 | 7
38905.5449 | 1 | 1 | 7
38905.5451 | 1 | 0 | 7
38905.5453 | 1 | 0 | 7
38905.5455 | 1 | 0 | 7
38905.5457 | 1 | 0 | 7
38905.5459 | 1 | 0 | 7
38905.5461 | 1 | 0 | 7
38905.5463 | 1 | 0 | 7
38905.5465 | 1 | 0 | 7
38905.5467 | 1 | 0 | 7
38905.5469 | 1 | 0 | 7
38905.5471 | 1 | 0 | 7
38905.5473 | 1 | 0 | 7
38905.5475 | 1 | 0 | 7
38905.5477 | 1 | 0 | 7
38905.5478 | 1 | 0 | 7
38905.548 | 1 | 0 | 7
38905.5482 | 1 | 0 | 7
38905.5484 | 1 | 0 | 7
38905.5486 | 1 | 0 | 7
38905.5488 | 1 | 0 | 7
38905.549 | 1 | 0 | 7
38905.5492 | 1 | 0 | 7
38905.5494 | 1 | 0 | 7
38905.5496 | 1 | 0 | 7
38905.5498 | 1 | 0 | 7
38905.55 | 1 | 0 | 7
38905.5502 | 1 | 0 | 7
38905.5504 | 1 | 0 | 7
38905.5506 | 1 | 0 | 7
38905.5508 | 1 | 0 | 7
38905.5509 | 1 | 0 | 7
38905.5511 | 1 | 0 | 7
38905.5513 | 1 | 0 | 7
38905.5515 | 1 | 0 | 7
38905.5517 | 1 | 0 | 7
38905.5519 | 1 | 0 | 7
38905.5521 | 1 | 0 | 7
38905.5523 | 1 | 0 | 7
38905.5525 | 1 | 0 | 7
38905.5527 | 1 | 0 | 7
38905.5529 | 1 | 0 | 7
38905.5531 | 1 | 0 | 7
38905.5533 | 1 | 0 | 7
38905.5535 | 1 | 0 | 7
38905.5537 | 1 | 0 | 7
38905.5539 | 1 | 0 | 7
38905.5541 | 1 | 0 | 7
38905.5543 | 1 | 0 | 7
38905.5545 | 1 | 0 | 7
38905.5546 | 7 | 0 | 7
38905.5548 | 9 | 0 | 7
38905.555 | 8 | 0 | 7
38905.5552 | 9 | 0 | 7
38905.5554 | 9 | 0 | 7
38905.5556 | 9 | 0 | 7
38905.5558 | 9 | 0 | 7
38905.556 | 9 | 0 | 7
38905.5562 | 9 | 0 | 7
38905.5564 | 10 | 0 | 7
38905.5566 | 9 | 0 | 7
38905.5568 | 9 | 0 | 7
38905.557 | 9 | 0 | 7
38905.5572 | 8 | 0 | 7
38905.5574 | 9 | 0 | 7
38905.5576 | 9 | 0 | 7
38905.5578 | 9 | 0 | 7
38905.558 | 9 | 0 | 7
38905.5581 | 9 | 0 | 7
38905.5583 | 9 | 0 | 7
38905.5585 | 9 | 0 | 7
38905.5587 | 9 | 0 | 7
38905.5589 | 9 | 0 | 7
38905.5591 | 9 | 0 | 7
38905.5593 | 8 | 0 | 7
38905.5595 | 9 | 0 | 7
38905.5597 | 9 | 0 | 7
38905.5599 | 9 | 0 | 7
38905.5601 | 9 | 0 | 7
38905.5603 | 8 | 0 | 7
38905.5605 | 8 | 0 | 7
38905.5607 | 10 | 0 | 7
38905.5609 | 1974 | 0 | 7
38905.5611 | 1827 | 0 | 7
38905.5612 | 1715 | 0 | 7
38905.5614 | 1671 | 0 | 7
38905.5616 | 1976 | 0 | 7
38905.5618 | 2446 | 0 | 7
38905.562 | 1900 | 1 | 7
38905.5622 | 1910 | 0 | 7
38905.5624 | 1903 | 0 | 7
38905.5626 | 2001 | 0 | 7
38905.5628 | 2196 | 1 | 7
38905.563 | 2346 | 1 | 7
38905.5632 | 2446 | 2 | 7
38905.5634 | 1953 | 1 | 7
38905.5636 | 2094 | 3 | 7
38905.5638 | 1926 | 4 | 7
38905.564 | 2134 | 5 | 7
38905.5642 | 2193 | 7 | 7
38905.5644 | 2362 | 9 | 7
38905.5646 | 2190 | 9 | 7
38905.5648 | 2263 | 13 | 7
38905.565 | 1998 | 14 | 7
38905.5651 | 2156 | 19 | 7
38905.5653 | 1987 | 22 | 7
38905.5655 | 2287 | 15 | 7
38905.5657 | 2127 | 0 | 7
38905.5659 | 2380 | 1 | 7
38905.5661 | 1926 | 0 | 7
38905.5663 | 2307 | 0 | 7
38905.5665 | 2440 | 0 | 7
38905.5667 | 2417 | 0 | 7
38905.5669 | 2177 | 0 | 7
38905.5671 | 1973 | 0 | 7
38905.5389 | 1 | 0 | 8
38905.5391 | 1 | 0 | 8
38905.5393 | 1 | 0 | 8
38905.5395 | 1 | 0 | 8
38905.5397 | 1 | 0 | 8
38905.5399 | 1 | 0 | 8
38905.5401 | 1 | 0 | 8
38905.5403 | 1 | 0 | 8
38905.5405 | 1 | 0 | 8
38905.5407 | 1 | 0 | 8
38905.5409 | 1 | 0 | 8
38905.5411 | 1 | 0 | 8
38905.5413 | 1 | 0 | 8
38905.5414 | 1 | 0 | 8
38905.5416 | 1 | 0 | 8
38905.5418 | 1 | 0 | 8
38905.542 | 1 | 0 | 8
38905.5422 | 1 | 0 | 8
38905.5424 | 1 | 0 | 8
38905.5426 | 1 | 0 | 8
38905.5428 | 1 | 0 | 8
38905.543 | 1 | 0 | 8
38905.5432 | 1 | 0 | 8
38905.5434 | 1 | 0 | 8
38905.5436 | 1 | 0 | 8
38905.5438 | 1 | 0 | 8
38905.544 | 1 | 0 | 8
38905.5442 | 1 | 0 | 8
38905.5444 | 1 | 0 | 8
38905.5445 | 1 | 0 | 8
38905.5447 | 1 | 0 | 8
38905.5449 | 1 | 0 | 8
38905.5451 | 1 | 0 | 8
38905.5453 | 1 | 0 | 8
38905.5455 | 1 | 0 | 8
38905.5457 | 1 | 0 | 8
38905.5459 | 1 | 0 | 8
38905.5461 | 1 | 0 | 8
38905.5463 | 1 | 0 | 8
38905.5465 | 1 | 0 | 8
38905.5467 | 1 | 0 | 8
38905.5469 | 1 | 0 | 8
38905.5471 | 1 | 0 | 8
38905.5473 | 1 | 0 | 8
38905.5475 | 1 | 0 | 8
38905.5477 | 1 | 0 | 8
38905.5479 | 1 | 0 | 8
38905.5481 | 1 | 0 | 8
38905.5482 | 1 | 0 | 8
38905.5484 | 1 | 0 | 8
38905.5486 | 1 | 0 | 8
38905.5488 | 1 | 0 | 8
38905.549 | 1 | 0 | 8
38905.5492 | 1 | 0 | 8
38905.5494 | 1 | 0 | 8
38905.5496 | 1 | 0 | 8
38905.5498 | 1 | 1 | 8
38905.55 | 1 | 0 | 8
38905.5502 | 1 | 0 | 8
38905.5504 | 1 | 0 | 8
38905.5506 | 1 | 0 | 8
38905.5508 | 1 | 0 | 8
38905.551 | 1 | 0 | 8
38905.5512 | 1 | 0 | 8
38905.5514 | 1 | 0 | 8
38905.5516 | 1 | 0 | 8
38905.5517 | 1 | 0 | 8
38905.5519 | 1 | 0 | 8
38905.5521 | 1 | 0 | 8
38905.5523 | 1 | 0 | 8
38905.5525 | 1 | 0 | 8
38905.5527 | 1 | 0 | 8
38905.5529 | 1 | 0 | 8
38905.5531 | 1 | 0 | 8
38905.5533 | 1 | 0 | 8
38905.5535 | 1 | 0 | 8
38905.5537 | 1 | 0 | 8
38905.5539 | 1 | 0 | 8
38905.5541 | 1 | 0 | 8
38905.5543 | 1 | 0 | 8
38905.5545 | 1 | 0 | 8
38905.5547 | 4 | 0 | 8
38905.5549 | 6 | 0 | 8
38905.555 | 6 | 0 | 8
38905.5552 | 7 | 0 | 8
38905.5554 | 8 | 0 | 8
38905.5556 | 8 | 0 | 8
38905.5558 | 8 | 0 | 8
38905.556 | 7 | 0 | 8
38905.5562 | 8 | 0 | 8
38905.5564 | 8 | 0 | 8
38905.5566 | 8 | 0 | 8
38905.5568 | 8 | 0 | 8
38905.557 | 8 | 0 | 8
38905.5572 | 8 | 0 | 8
38905.5574 | 8 | 0 | 8
38905.5576 | 8 | 0 | 8
38905.5578 | 7 | 0 | 8
38905.558 | 7 | 0 | 8
38905.5582 | 7 | 0 | 8
38905.5584 | 7 | 0 | 8
38905.5586 | 7 | 0 | 8
38905.5587 | 7 | 0 | 8
38905.5589 | 8 | 0 | 8
38905.5591 | 7 | 0 | 8
38905.5593 | 2378 | 0 | 8
38905.5595 | 1871 | 0 | 8
38905.5597 | 1888 | 0 | 8
38905.5599 | 1884 | 0 | 8
38905.5601 | 2164 | 0 | 8
38905.5603 | 2438 | 0 | 8
38905.5605 | 2028 | 1 | 8
38905.5607 | 2258 | 0 | 8
38905.5609 | 2434 | 0 | 8
38905.5611 | 2169 | 0 | 8
38905.5613 | 2383 | 0 | 8
38905.5615 | 1986 | 0 | 8
38905.5617 | 2111 | 0 | 8
38905.5619 | 2251 | 0 | 8
38905.562 | 2265 | 0 | 8
38905.5622 | 2284 | 1 | 8
38905.5624 | 2340 | 1 | 8
38905.5626 | 2335 | 1 | 8
38905.5628 | 1967 | 1 | 8
38905.563 | 1932 | 1 | 8
38905.5632 | 2453 | 2 | 8
38905.5634 | 2097 | 2 | 8
38905.5636 | 2103 | 2 | 8
38905.5638 | 2408 | 4 | 8
38905.564 | 2205 | 7 | 8
38905.5642 | 2092 | 7 | 8
38905.5644 | 2325 | 9 | 8
38905.5646 | 2357 | 13 | 8
38905.5648 | 2182 | 11 | 8
38905.565 | 2307 | 17 | 8
38905.5652 | 2243 | 11 | 8
38905.5655 | 2379 | 2 | 8
38905.5657 | 2435 | 1 | 8
38905.5659 | 2432 | 0 | 8
38905.5661 | 2183 | 1 | 8
38905.5663 | 1964 | 0 | 8
38905.5665 | 2486 | 0 | 8
38905.5667 | 1991 | 0 | 8
38905.5669 | 2022 | 0 | 8
38905.5671 | 1905 | 0 | 8
38905.5389 | 1 | 0 | 9
38905.5391 | 1 | 0 | 9
38905.5393 | 1 | 0 | 9
38905.5395 | 1 | 0 | 9
38905.5397 | 1 | 0 | 9
38905.5399 | 1 | 0 | 9
38905.5401 | 1 | 0 | 9
38905.5403 | 1 | 0 | 9
38905.5405 | 1 | 0 | 9
38905.5407 | 2 | 0 | 9
38905.5409 | 1 | 0 | 9
38905.5411 | 1 | 0 | 9
38905.5413 | 1 | 0 | 9
38905.5415 | 1 | 0 | 9
38905.5417 | 1 | 0 | 9
38905.5419 | 1 | 0 | 9
38905.542 | 1 | 0 | 9
38905.5422 | 1 | 0 | 9
38905.5424 | 1 | 0 | 9
38905.5426 | 1 | 0 | 9
38905.5428 | 1 | 0 | 9
38905.543 | 1 | 0 | 9
38905.5432 | 1 | 0 | 9
38905.5434 | 1 | 0 | 9
38905.5436 | 1 | 0 | 9
38905.5438 | 1 | 0 | 9
38905.544 | 1 | 0 | 9
38905.5442 | 1 | 0 | 9
38905.5444 | 1 | 0 | 9
38905.5446 | 2 | 0 | 9
38905.5448 | 1 | 0 | 9
38905.545 | 1 | 0 | 9
38905.5452 | 1 | 0 | 9
38905.5453 | 1 | 0 | 9
38905.5455 | 1 | 0 | 9
38905.5457 | 1 | 0 | 9
38905.5459 | 1 | 0 | 9
38905.5461 | 1 | 0 | 9
38905.5463 | 1 | 1 | 9
38905.5465 | 1 | 0 | 9
38905.5467 | 1 | 0 | 9
38905.5469 | 1 | 0 | 9
38905.5471 | 1 | 0 | 9
38905.5473 | 1 | 0 | 9
38905.5475 | 1 | 0 | 9
38905.5477 | 1 | 0 | 9
38905.5479 | 1 | 0 | 9
38905.5481 | 1 | 0 | 9
38905.5483 | 1 | 0 | 9
38905.5485 | 1 | 0 | 9
38905.5486 | 1 | 0 | 9
38905.5488 | 1 | 0 | 9
38905.549 | 1 | 0 | 9
38905.5492 | 1 | 0 | 9
38905.5494 | 1 | 0 | 9
38905.5496 | 1 | 0 | 9
38905.5498 | 1 | 0 | 9
38905.55 | 1 | 0 | 9
38905.5502 | 1 | 0 | 9
38905.5504 | 1 | 0 | 9
38905.5506 | 1 | 0 | 9
38905.5508 | 1 | 0 | 9
38905.551 | 1 | 0 | 9
38905.5512 | 1 | 0 | 9
38905.5514 | 1 | 0 | 9
38905.5516 | 1 | 0 | 9
38905.5518 | 1 | 0 | 9
38905.552 | 1 | 0 | 9
38905.5522 | 1 | 0 | 9
38905.5523 | 1 | 0 | 9
38905.5525 | 1 | 0 | 9
38905.5527 | 1 | 0 | 9
38905.5529 | 1 | 0 | 9
38905.5531 | 1 | 0 | 9
38905.5533 | 1 | 0 | 9
38905.5535 | 1 | 0 | 9
38905.5537 | 1 | 0 | 9
38905.5539 | 1 | 0 | 9
38905.5541 | 1 | 0 | 9
38905.5543 | 1 | 0 | 9
38905.5545 | 1 | 0 | 9
38905.5547 | 4 | 0 | 9
38905.5549 | 4 | 0 | 9
38905.5551 | 4 | 0 | 9
38905.5553 | 4 | 0 | 9
38905.5555 | 5 | 0 | 9
38905.5556 | 6 | 0 | 9
38905.5558 | 6 | 0 | 9
38905.556 | 7 | 0 | 9
38905.5562 | 6 | 0 | 9
38905.5564 | 7 | 0 | 9
38905.5566 | 7 | 0 | 9
38905.5568 | 7 | 0 | 9
38905.557 | 6 | 0 | 9
38905.5572 | 6 | 0 | 9
38905.5574 | 7 | 0 | 9
38905.5576 | 7 | 0 | 9
38905.5578 | 7 | 0 | 9
38905.558 | 6 | 0 | 9
38905.5582 | 6 | 0 | 9
38905.5584 | 7 | 0 | 9
38905.5586 | 6 | 0 | 9
38905.5588 | 6 | 0 | 9
38905.559 | 6 | 0 | 9
38905.5592 | 6 | 0 | 9
38905.5593 | 9 | 0 | 9
38905.5595 | 9 | 0 | 9
38905.5597 | 9 | 0 | 9
38905.5599 | 8 | 0 | 9
38905.5601 | 9 | 0 | 9
38905.5603 | 8 | 0 | 9
38905.5605 | 8 | 0 | 9
38905.5607 | 1341 | 0 | 9
38905.5609 | 2015 | 0 | 9
38905.5611 | 2012 | 0 | 9
38905.5613 | 1511 | 0 | 9
38905.5615 | 1688 | 0 | 9
38905.5617 | 2212 | 0 | 9
38905.5619 | 2024 | 0 | 9
38905.5621 | 2148 | 0 | 9
38905.5623 | 2449 | 1 | 9
38905.5625 | 2193 | 0 | 9
38905.5627 | 2236 | 1 | 9
38905.5628 | 2457 | 2 | 9
38905.563 | 2137 | 1 | 9
38905.5632 | 2107 | 1 | 9
38905.5634 | 2336 | 3 | 9
38905.5636 | 1975 | 3 | 9
38905.5638 | 2346 | 5 | 9
38905.564 | 2288 | 6 | 9
38905.5642 | 2419 | 8 | 9
38905.5644 | 2343 | 9 | 9
38905.5646 | 2323 | 13 | 9
38905.5648 | 2154 | 12 | 9
38905.565 | 2280 | 16 | 9
38905.5652 | 1843 | 16 | 9
38905.5654 | 1995 | 23 | 9
38905.5656 | 2312 | 2 | 9
38905.5658 | 1907 | 0 | 9
38905.5659 | 2390 | 1 | 9
38905.5661 | 2147 | 0 | 9
38905.5663 | 1935 | 0 | 9
38905.5665 | 2123 | 0 | 9
38905.5667 | 2191 | 0 | 9
38905.5669 | 1970 | 0 | 9
38905.5671 | 2219 | 0 | 9
38905.5389 | 1 | 0 | 10
38905.5391 | 1 | 0 | 10
38905.5393 | 1 | 0 | 10
38905.5395 | 1 | 0 | 10
38905.5397 | 1 | 0 | 10
38905.5399 | 1 | 0 | 10
38905.5401 | 1 | 0 | 10
38905.5403 | 1 | 0 | 10
38905.5405 | 1 | 0 | 10
38905.5407 | 1 | 0 | 10
38905.5409 | 2 | 0 | 10
38905.5411 | 1 | 0 | 10
38905.5413 | 1 | 0 | 10
38905.5415 | 1 | 0 | 10
38905.5417 | 1 | 0 | 10
38905.5419 | 1 | 0 | 10
38905.5421 | 1 | 0 | 10
38905.5422 | 1 | 0 | 10
38905.5424 | 1 | 0 | 10
38905.5426 | 1 | 0 | 10
38905.5428 | 1 | 0 | 10
38905.543 | 1 | 0 | 10
38905.5432 | 1 | 0 | 10
38905.5434 | 1 | 0 | 10
38905.5436 | 1 | 0 | 10
38905.5438 | 1 | 0 | 10
38905.544 | 1 | 0 | 10
38905.5442 | 1 | 0 | 10
38905.5444 | 1 | 0 | 10
38905.5446 | 1 | 0 | 10
38905.5448 | 1 | 0 | 10
38905.545 | 1 | 0 | 10
38905.5452 | 1 | 0 | 10
38905.5454 | 1 | 0 | 10
38905.5456 | 1 | 0 | 10
38905.5458 | 1 | 0 | 10
38905.5459 | 1 | 0 | 10
38905.5461 | 1 | 0 | 10
38905.5463 | 1 | 0 | 10
38905.5465 | 1 | 0 | 10
38905.5467 | 1 | 0 | 10
38905.5469 | 1 | 0 | 10
38905.5471 | 1 | 0 | 10
38905.5473 | 1 | 0 | 10
38905.5475 | 1 | 0 | 10
38905.5477 | 1 | 0 | 10
38905.5479 | 1 | 0 | 10
38905.5481 | 1 | 0 | 10
38905.5483 | 1 | 0 | 10
38905.5485 | 1 | 0 | 10
38905.5487 | 1 | 0 | 10
38905.5489 | 1 | 0 | 10
38905.5491 | 1 | 0 | 10
38905.5492 | 1 | 0 | 10
38905.5494 | 1 | 0 | 10
38905.5496 | 1 | 0 | 10
38905.5498 | 1 | 0 | 10
38905.55 | 1 | 0 | 10
38905.5502 | 1 | 0 | 10
38905.5504 | 1 | 0 | 10
38905.5506 | 1 | 0 | 10
38905.5508 | 1 | 0 | 10
38905.551 | 1 | 0 | 10
38905.5512 | 1 | 0 | 10
38905.5514 | 1 | 0 | 10
38905.5516 | 1 | 0 | 10
38905.5518 | 1 | 0 | 10
38905.552 | 1 | 0 | 10
38905.5522 | 1 | 0 | 10
38905.5524 | 1 | 0 | 10
38905.5526 | 1 | 0 | 10
38905.5528 | 1 | 0 | 10
38905.5529 | 1 | 0 | 10
38905.5531 | 1 | 0 | 10
38905.5533 | 1 | 0 | 10
38905.5535 | 1 | 0 | 10
38905.5537 | 1 | 0 | 10
38905.5539 | 1 | 0 | 10
38905.5541 | 1 | 0 | 10
38905.5543 | 1 | 0 | 10
38905.5545 | 1747 | 0 | 10
38905.5547 | 1566 | 0 | 10
38905.5549 | 1694 | 0 | 10
38905.5551 | 1533 | 0 | 10
38905.5553 | 2034 | 0 | 10
38905.5555 | 2325 | 0 | 10
38905.5557 | 2409 | 0 | 10
38905.5559 | 2026 | 0 | 10
38905.5561 | 2063 | 0 | 10
38905.5563 | 2390 | 0 | 10
38905.5564 | 2086 | 0 | 10
38905.5566 | 2124 | 0 | 10
38905.5568 | 2000 | 0 | 10
38905.557 | 2358 | 0 | 10
38905.5572 | 2321 | 0 | 10
38905.5574 | 2238 | 0 | 10
38905.5576 | 2236 | 0 | 10
38905.5578 | 1958 | 0 | 10
38905.558 | 2197 | 0 | 10
38905.5582 | 2187 | 0 | 10
38905.5584 | 2163 | 0 | 10
38905.5586 | 1880 | 0 | 10
38905.5588 | 2189 | 0 | 10
38905.559 | 2230 | 0 | 10
38905.5592 | 2206 | 0 | 10
38905.5594 | 2012 | 0 | 10
38905.5595 | 2065 | 0 | 10
38905.5597 | 2237 | 0 | 10
38905.5599 | 1864 | 0 | 10
38905.5601 | 1877 | 0 | 10
38905.5603 | 1919 | 0 | 10
38905.5605 | 2329 | 0 | 10
38905.5607 | 2120 | 0 | 10
38905.5609 | 2450 | 0 | 10
38905.5611 | 2067 | 0 | 10
38905.5613 | 2463 | 0 | 10
38905.5615 | 2255 | 0 | 10
38905.5617 | 2176 | 0 | 10
38905.5619 | 2082 | 0 | 10
38905.5621 | 2474 | 1 | 10
38905.5623 | 2431 | 1 | 10
38905.5625 | 2169 | 1 | 10
38905.5627 | 2412 | 1 | 10
38905.5629 | 2446 | 2 | 10
38905.5631 | 2181 | 1 | 10
38905.5633 | 1895 | 1 | 10
38905.5634 | 2070 | 3 | 10
38905.5636 | 1987 | 3 | 10
38905.5638 | 2224 | 6 | 10
38905.564 | 1994 | 6 | 10
38905.5642 | 2303 | 8 | 10
38905.5644 | 2297 | 8 | 10
38905.5646 | 1925 | 10 | 10
38905.5648 | 2389 | 11 | 10
38905.565 | 2218 | 18 | 10
38905.5652 | 2297 | 22 | 10
38905.5654 | 1835 | 23 | 10
38905.5656 | 2035 | 1 | 10
38905.5658 | 2425 | 1 | 10
38905.566 | 2475 | 1 | 10
38905.5662 | 2168 | 0 | 10
38905.5664 | 1938 | 0 | 10
38905.5666 | 2023 | 0 | 10
38905.5667 | 2331 | 1 | 10
38905.5669 | 1984 | 0 | 10
38905.5671 | 2211 | 0 | 10
38905.539 | 1 | 0 | 11
38905.5392 | 1 | 0 | 11
38905.5394 | 1 | 0 | 11
38905.5395 | 1 | 0 | 11
38905.5397 | 1 | 0 | 11
38905.5399 | 1 | 0 | 11
38905.5401 | 1 | 0 | 11
38905.5403 | 1 | 0 | 11
38905.5405 | 1 | 0 | 11
38905.5407 | 1 | 0 | 11
38905.5409 | 1 | 0 | 11
38905.5411 | 1 | 0 | 11
38905.5413 | 1 | 0 | 11
38905.5415 | 1 | 0 | 11
38905.5417 | 1 | 0 | 11
38905.5419 | 1 | 0 | 11
38905.5421 | 1 | 0 | 11
38905.5423 | 1 | 0 | 11
38905.5425 | 1 | 0 | 11
38905.5427 | 1 | 0 | 11
38905.5428 | 1 | 0 | 11
38905.543 | 1 | 0 | 11
38905.5432 | 1 | 0 | 11
38905.5434 | 1 | 0 | 11
38905.5436 | 1 | 0 | 11
38905.5438 | 1 | 0 | 11
38905.544 | 1 | 0 | 11
38905.5442 | 1 | 0 | 11
38905.5444 | 1 | 0 | 11
38905.5446 | 1 | 0 | 11
38905.5448 | 1 | 0 | 11
38905.545 | 1 | 0 | 11
38905.5452 | 1 | 0 | 11
38905.5454 | 1 | 0 | 11
38905.5456 | 1 | 0 | 11
38905.5458 | 1 | 0 | 11
38905.546 | 1 | 0 | 11
38905.5462 | 1 | 0 | 11
38905.5464 | 1 | 0 | 11
38905.5465 | 1 | 0 | 11
38905.5467 | 1 | 0 | 11
38905.5469 | 1 | 0 | 11
38905.5471 | 1 | 0 | 11
38905.5473 | 1 | 0 | 11
38905.5475 | 1 | 0 | 11
38905.5477 | 1 | 0 | 11
38905.5479 | 1 | 0 | 11
38905.5481 | 1 | 0 | 11
38905.5483 | 1 | 0 | 11
38905.5485 | 1 | 0 | 11
38905.5487 | 1 | 0 | 11
38905.5489 | 1 | 0 | 11
38905.5491 | 1 | 0 | 11
38905.5493 | 2 | 0 | 11
38905.5495 | 1 | 0 | 11
38905.5497 | 1 | 0 | 11
38905.5498 | 1 | 0 | 11
38905.55 | 1 | 0 | 11
38905.5502 | 1 | 0 | 11
38905.5504 | 1 | 0 | 11
38905.5506 | 1 | 0 | 11
38905.5508 | 1 | 0 | 11
38905.551 | 1 | 0 | 11
38905.5512 | 1 | 0 | 11
38905.5514 | 1 | 0 | 11
38905.5516 | 1 | 0 | 11
38905.5518 | 1 | 0 | 11
38905.552 | 1 | 0 | 11
38905.5522 | 1 | 0 | 11
38905.5524 | 1 | 0 | 11
38905.5526 | 1 | 1 | 11
38905.5528 | 1 | 0 | 11
38905.553 | 1 | 0 | 11
38905.5532 | 1 | 0 | 11
38905.5533 | 1 | 0 | 11
38905.5535 | 1 | 0 | 11
38905.5537 | 1 | 0 | 11
38905.5539 | 1 | 0 | 11
38905.5541 | 1 | 0 | 11
38905.5543 | 1 | 0 | 11
38905.5545 | 4 | 0 | 11
38905.5547 | 8 | 0 | 11
38905.5549 | 9 | 0 | 11
38905.5551 | 9 | 1 | 11
38905.5553 | 9 | 0 | 11
38905.5555 | 9 | 0 | 11
38905.5557 | 9 | 0 | 11
38905.5559 | 9 | 0 | 11
38905.5561 | 9 | 0 | 11
38905.5563 | 9 | 0 | 11
38905.5565 | 9 | 0 | 11
38905.5567 | 9 | 0 | 11
38905.5569 | 9 | 0 | 11
38905.557 | 9 | 0 | 11
38905.5572 | 8 | 0 | 11
38905.5574 | 10 | 0 | 11
38905.5576 | 9 | 0 | 11
38905.5578 | 9 | 0 | 11
38905.558 | 9 | 0 | 11
38905.5582 | 9 | 0 | 11
38905.5584 | 9 | 0 | 11
38905.5586 | 9 | 0 | 11
38905.5588 | 9 | 0 | 11
38905.559 | 9 | 0 | 11
38905.5592 | 9 | 0 | 11
38905.5594 | 2229 | 25 | 11
38905.5596 | 2069 | 33 | 11
38905.5598 | 2190 | 28 | 11
38905.56 | 2081 | 1 | 11
38905.5602 | 1963 | 1 | 11
38905.5603 | 1932 | 1 | 11
38905.5605 | 2374 | 2 | 11
38905.5607 | 2140 | 1 | 11
38905.5609 | 1977 | 1 | 11
38905.5611 | 2052 | 1 | 11
38905.5613 | 2459 | 1 | 11
38905.5615 | 2273 | 15 | 11
38905.5617 | 2197 | 25 | 11
38905.5619 | 1973 | 0 | 11
38905.5621 | 2399 | 1 | 11
38905.5623 | 2411 | 1 | 11
38905.5625 | 2268 | 1 | 11
38905.5627 | 2446 | 1 | 11
38905.5629 | 2020 | 1 | 11
38905.5631 | 2245 | 1 | 11
38905.5633 | 2358 | 2 | 11
38905.5635 | 2242 | 2 | 11
38905.5637 | 1883 | 3 | 11
38905.5638 | 2338 | 5 | 11
38905.564 | 2426 | 8 | 11
38905.5642 | 1957 | 6 | 11
38905.5644 | 2380 | 10 | 11
38905.5646 | 2069 | 9 | 11
38905.5648 | 2400 | 15 | 11
38905.565 | 2381 | 14 | 11
38905.5652 | 1969 | 18 | 11
38905.5654 | 2157 | 27 | 11
38905.5656 | 1997 | 0 | 11
38905.5658 | 2109 | 0 | 11
38905.566 | 1993 | 0 | 11
38905.5662 | 2088 | 0 | 11
38905.5664 | 2280 | 0 | 11
38905.5666 | 2408 | 1 | 11
38905.5668 | 2415 | 1 | 11
38905.567 | 2375 | 0 | 11
38905.5672 | 2121 | 0 | 11
38905.539 | 1 | 0 | 12
38905.5392 | 1 | 0 | 12
38905.5394 | 1 | 0 | 12
38905.5396 | 1 | 0 | 12
38905.5398 | 1 | 0 | 12
38905.54 | 1 | 0 | 12
38905.5402 | 1 | 0 | 12
38905.5403 | 1 | 0 | 12
38905.5405 | 1 | 0 | 12
38905.5407 | 1 | 0 | 12
38905.5409 | 1 | 0 | 12
38905.5411 | 1 | 0 | 12
38905.5413 | 1 | 0 | 12
38905.5415 | 1 | 0 | 12
38905.5417 | 1 | 0 | 12
38905.5419 | 1 | 0 | 12
38905.5421 | 1 | 0 | 12
38905.5423 | 1 | 0 | 12
38905.5425 | 1 | 0 | 12
38905.5427 | 1 | 0 | 12
38905.5429 | 1 | 0 | 12
38905.5431 | 2 | 0 | 12
38905.5433 | 1 | 0 | 12
38905.5434 | 1 | 0 | 12
38905.5436 | 1 | 0 | 12
38905.5438 | 1 | 0 | 12
38905.544 | 1 | 0 | 12
38905.5442 | 1 | 0 | 12
38905.5444 | 1 | 0 | 12
38905.5446 | 1 | 0 | 12
38905.5448 | 1 | 0 | 12
38905.545 | 1 | 0 | 12
38905.5452 | 1 | 0 | 12
38905.5454 | 1 | 0 | 12
38905.5456 | 1 | 0 | 12
38905.5458 | 1 | 0 | 12
38905.546 | 1 | 0 | 12
38905.5462 | 1 | 0 | 12
38905.5464 | 1 | 0 | 12
38905.5466 | 1 | 0 | 12
38905.5468 | 1 | 0 | 12
38905.5469 | 1 | 0 | 12
38905.5471 | 1 | 0 | 12
38905.5473 | 1 | 0 | 12
38905.5475 | 1 | 0 | 12
38905.5477 | 1 | 0 | 12
38905.5479 | 1 | 0 | 12
38905.5481 | 1 | 0 | 12
38905.5483 | 1 | 0 | 12
38905.5485 | 1 | 0 | 12
38905.5487 | 1 | 0 | 12
38905.5489 | 1 | 0 | 12
38905.5491 | 1 | 0 | 12
38905.5493 | 1 | 0 | 12
38905.5495 | 1 | 0 | 12
38905.5497 | 1 | 0 | 12
38905.5499 | 1 | 0 | 12
38905.5501 | 1 | 0 | 12
38905.5503 | 1 | 0 | 12
38905.5505 | 1 | 0 | 12
38905.5506 | 1 | 0 | 12
38905.5508 | 1 | 0 | 12
38905.551 | 1 | 0 | 12
38905.5512 | 1 | 0 | 12
38905.5514 | 1 | 0 | 12
38905.5516 | 1 | 0 | 12
38905.5518 | 1 | 0 | 12
38905.552 | 1 | 0 | 12
38905.5522 | 1 | 0 | 12
38905.5524 | 1 | 0 | 12
38905.5526 | 1 | 0 | 12
38905.5528 | 1 | 0 | 12
38905.553 | 1 | 0 | 12
38905.5532 | 1 | 0 | 12
38905.5534 | 1 | 0 | 12
38905.5536 | 1 | 0 | 12
38905.5537 | 1 | 0 | 12
38905.5539 | 1 | 0 | 12
38905.5541 | 1 | 0 | 12
38905.5543 | 1 | 0 | 12
38905.5545 | 1514 | 0 | 12
38905.5547 | 1383 | 0 | 12
38905.5549 | 1364 | 0 | 12
38905.5551 | 1889 | 0 | 12
38905.5553 | 1601 | 0 | 12
38905.5555 | 1867 | 0 | 12
38905.5557 | 2019 | 0 | 12
38905.5559 | 1939 | 0 | 12
38905.5561 | 1908 | 0 | 12
38905.5563 | 2043 | 0 | 12
38905.5565 | 2403 | 0 | 12
38905.5567 | 2228 | 0 | 12
38905.5569 | 2130 | 0 | 12
38905.5571 | 1837 | 0 | 12
38905.5573 | 1846 | 0 | 12
38905.5575 | 2322 | 0 | 12
38905.5576 | 2326 | 0 | 12
38905.5578 | 1994 | 0 | 12
38905.558 | 2261 | 0 | 12
38905.5582 | 1834 | 0 | 12
38905.5584 | 1918 | 0 | 12
38905.5586 | 2218 | 0 | 12
38905.5588 | 2395 | 1 | 12
38905.559 | 2415 | 0 | 12
38905.5592 | 2307 | 0 | 12
38905.5594 | 2335 | 26 | 12
38905.5596 | 2365 | 36 | 12
38905.5598 | 2171 | 27 | 12
38905.56 | 2043 | 1 | 12
38905.5602 | 2209 | 1 | 12
38905.5604 | 2170 | 1 | 12
38905.5606 | 2258 | 1 | 12
38905.5608 | 2124 | 1 | 12
38905.5609 | 1993 | 1 | 12
38905.5611 | 2454 | 1 | 12
38905.5613 | 2172 | 0 | 12
38905.5615 | 2304 | 13 | 12
38905.5617 | 2039 | 22 | 12
38905.5619 | 2063 | 0 | 12
38905.5621 | 350 | 0 | 12
38905.5623 | 1996 | 0 | 12
38905.5625 | 1931 | 1 | 12
38905.5627 | 2192 | 1 | 12
38905.5629 | 1907 | 1 | 12
38905.5631 | 2106 | 2 | 12
38905.5633 | 1982 | 1 | 12
38905.5635 | 1949 | 2 | 12
38905.5637 | 2217 | 4 | 12
38905.5639 | 2287 | 5 | 12
38905.5641 | 2352 | 7 | 12
38905.5642 | 1941 | 7 | 12
38905.5644 | 2304 | 10 | 12
38905.5646 | 2183 | 13 | 12
38905.5648 | 2284 | 14 | 12
38905.565 | 2107 | 16 | 12
38905.5652 | 2089 | 20 | 12
38905.5654 | 2163 | 27 | 12
38905.5656 | 2162 | 1 | 12
38905.5658 | 2020 | 0 | 12
38905.566 | 2470 | 0 | 12
38905.5662 | 2382 | 0 | 12
38905.5664 | 2389 | 1 | 12
38905.5666 | 2353 | 0 | 12
38905.5668 | 2375 | 0 | 12
38905.567 | 2299 | 0 | 12
38905.5672 | 2483 | 0 | 12