## Test Facts
Last row in IRMS data sheets: | 122
Time when Penlight power was initiated: | 115 s
NOTE: The thermocouple labeled Cable 3 appears to have failed at about 1020 seconds (Penlight time) into the test. Data after this time for this one thermocouple is suspect and should be discounted.

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 10
Test conditions: Cable: Item # 5, 3-conductor plus drain wire, 8AWG, PVC insulated, PVC jacketed, General Cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: None. Cables located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 300C, nominal 6.1 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded). Thermal response monitoring: Shroud temperature and five cable temperatures (see maps). Shroud power: Initiated after 115 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
115 | 0 | Initiate Penlight Heating
1288 | 1173 | Conductor 2 shorts to drain wire at less than 100 ohms (19) | The initial failure is by conductor-to-drain wire shorting
1296-1304 | 1181-1189 | Conductors 1 and drain wire short to ground at less than 1000 ohms (602 & 698)
1299 | 1184 | Conductor 1 shorts to the drain wire at less than 100 ohms (6)
1358 | 1243 | Conductor 3 shorts to the drain wire at less than 1000 ohms (405)
1360-1375 | 1245-1260 | Conductor 1 shorts to conductors 2 & 3 at less than 100 ohms (11 & 18); Conductor 2 shorts to conductor 3 at less than 100 ohms (18); the existing short between conductor 3 and the drain wire degrades to less than 100 ohms (1)
1367-1369 | 1252-1254 | Conductors 2 & 3 both short to ground at less than 1000 ohms (429 & 588) | All conductors have shorted to ground.
1610 | 1495 | Power to Penlight is shutoff
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of any external ground.
Observation 2 | Shorts to ground are very erratic and may not be real because there was no raceway providing a ground plane within the Penlight chamber.
Observation 3 | It took 1173 seconds (19.6 min.) after start of heating for the initial failure to occur.
Observation 4 | NOTE: The thermocouple labeled Cable 3 appears to have failed at about 1020 seconds (Penlight time) into the test. Data after this time for this one thermocouple is suspect and should be discounted.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, center position
| TC3 | = | Cable 3 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC4 | = | Cable 4 | On outer cable surface, outboard from cable center
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
NOTE: The thermocouple labeled Cable 3 appears to have failed at about 1020 seconds (Penlight time) into the test. Data after this time for this one thermocouple is suspect and should be discounted.

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 10 |  |  | 2006-07-27 | 15:36
PVC | 3-C | Air Drop (Horizontal Run)
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-111.8333 | 211202 |  | -108.1667 | 211202 | -106.5 | 211202 | -104.5 | 211202 | -111.8333 | 211202
-95.3333 | 211202 |  | -91.5 | 211202 | -89.6667 | 211202 | -87.8333 | 211202 | -95.3333 | 211202
-78.5 | 211202 |  | -74.8333 | 211202 | -73 | 211202 | -71 | 211202 | -78.5 | 211202
-61.6667 | 211202 |  | -58 | 211202 | -56 | 211202 | -54.3333 | 211202 | -61.6667 | 211202
-44.6667 | 211202 |  | -41.1667 | 211202 | -39.1667 | 211202 | -37.3333 | 211202 | -44.6667 | 211202
-28.1667 | 211202 |  | -24.3333 | 211202 | -22.5 | 211202 | -20.6667 | 105551 | -28.1667 | 105551
-11.3333 | 211202 |  | -7.5 | 105551 | -5.6667 | 70334 | -3.8333 | 211202 | -11.3333 | 70334
5.5 | 211202 |  | 9.1667 | 211202 | 11 | 211202 | 13 | 211202 | 5.5 | 211202
22.3333 | 211202 |  | 26 | 211202 | 28 | 211202 | 29.6667 | 211202 | 22.3333 | 211202
39.1667 | 211202 |  | 42.8333 | 211202 | 44.6667 | 211202 | 46.6667 | 211202 | 39.1667 | 211202
55.8333 | 211202 |  | 59.6667 | 211202 | 61.5 | 211202 | 63.3333 | 105551 | 55.8333 | 105551
72.6667 | 211202 |  | 76.5 | 211202 | 78.3333 | 105551 | 80.1667 | 211202 | 72.6667 | 105551
89.5 | 211202 |  | 93.1667 | 211202 | 95 | 211202 | 97 | 211202 | 89.5 | 211202
106.3333 | 211202 |  | 110 | 211202 | 112 | 211202 | 113.6667 | 211202 | 106.3333 | 211202
123.1667 | 211202 |  | 126.8333 | 211202 | 128.6667 | 211202 | 130.6667 | 211202 | 123.1667 | 211202
139.8333 | 211202 |  | 143.6667 | 211202 | 145.5 | 211202 | 147.3333 | 211202 | 139.8333 | 211202
156.6667 | 211202 |  | 160.5 | 211202 | 162.3333 | 211202 | 164.1667 | 211202 | 156.6667 | 211202
173.5 | 211202 |  | 177.1667 | 211202 | 179 | 211202 | 181 | 211202 | 173.5 | 211202
190.3333 | 211202 |  | 194.3333 | 211202 | 196.3333 | 211202 | 197.6667 | 211202 | 190.3333 | 211202
207.1667 | 211202 |  | 210.8333 | 211202 | 212.6667 | 211202 | 214.6667 | 211202 | 207.1667 | 211202
223.8333 | 211202 |  | 227.6667 | 211202 | 229.5 | 211202 | 231.3333 | 211202 | 223.8333 | 211202
240.6667 | 211202 |  | 244.5 | 211202 | 246.3333 | 211202 | 248.1667 | 211202 | 240.6667 | 211202
257.5 | 211202 |  | 261.1667 | 211202 | 263 | 211202 | 265 | 211202 | 257.5 | 211202
274.3333 | 211202 |  | 278 | 211202 | 280 | 211202 | 281.6667 | 211202 | 274.3333 | 211202
291.1667 | 211202 |  | 294.8333 | 211202 | 296.6667 | 211202 | 298.6667 | 211202 | 291.1667 | 211202
307.8333 | 211202 |  | 311.6667 | 211202 | 313.5 | 211202 | 315.3333 | 211202 | 307.8333 | 211202
324.6667 | 211202 |  | 328.5 | 211202 | 330.3333 | 105551 | 332.1667 | 211202 | 324.6667 | 105551
341.5 | 211202 |  | 345.1667 | 211202 | 347 | 211202 | 349 | 211202 | 341.5 | 211202
358.3333 | 211202 |  | 362 | 211202 | 364 | 211202 | 365.6667 | 211202 | 358.3333 | 211202
375.1667 | 211202 |  | 378.8333 | 211202 | 380.6667 | 211202 | 382.6667 | 211202 | 375.1667 | 211202
391.8333 | 211202 |  | 395.6667 | 211202 | 397.5 | 211202 | 399.3333 | 211202 | 391.8333 | 211202
408.6667 | 211202 |  | 412.5 | 211202 | 414.3333 | 211202 | 416.1667 | 211202 | 408.6667 | 211202
425.5 | 211202 |  | 429.1667 | 211202 | 431 | 211202 | 433 | 211202 | 425.5 | 211202
442.3333 | 211202 |  | 446 | 211202 | 448 | 211202 | 449.6667 | 211202 | 442.3333 | 211202
459.1667 | 211202 |  | 462.8333 | 211202 | 464.6667 | 211202 | 466.6667 | 211202 | 459.1667 | 211202
475.8333 | 211202 |  | 479.6667 | 211202 | 481.5 | 211202 | 483.3333 | 211202 | 475.8333 | 211202
492.6667 | 211202 |  | 496.5 | 211202 | 498.3333 | 211202 | 500.1667 | 211202 | 492.6667 | 211202
509.5 | 211202 |  | 513.1667 | 211202 | 515 | 211202 | 517 | 211202 | 509.5 | 211202
526.3333 | 211202 |  | 530 | 211202 | 532 | 211202 | 533.6667 | 211202 | 526.3333 | 211202
543.1667 | 211202 |  | 546.8333 | 211202 | 548.6667 | 211202 | 550.6667 | 211202 | 543.1667 | 211202
559.8333 | 105551 |  | 563.6667 | 211202 | 565.5 | 211202 | 567.3333 | 211202 | 559.8333 | 105551
576.5 | 211202 |  | 580.3333 | 211202 | 582.3333 | 211202 | 584.1667 | 211202 | 576.5 | 211202
593.5 | 211202 |  | 597.1667 | 211202 | 599 | 211202 | 601 | 211202 | 593.5 | 211202
610.3333 | 211202 |  | 614 | 211202 | 616 | 211202 | 617.6667 | 211202 | 610.3333 | 211202
627.1667 | 211202 |  | 630.8333 | 211202 | 632.6667 | 211202 | 634.6667 | 211202 | 627.1667 | 211202
643.6667 | 211202 |  | 647.6667 | 211202 | 649.3333 | 211202 | 651.3333 | 211202 | 643.6667 | 211202
660.6667 | 211202 |  | 664.5 | 211202 | 666.1667 | 211202 | 668 | 211202 | 660.6667 | 211202
677.5 | 211202 |  | 681.1667 | 211202 | 683 | 211202 | 685 | 211202 | 677.5 | 211202
694.3333 | 211202 |  | 698 | 211202 | 700 | 211202 | 701.6667 | 211202 | 694.3333 | 211202
711.1667 | 211202 |  | 714.8333 | 211202 | 716.5 | 211202 | 718.5 | 211202 | 711.1667 | 211202
727.6667 | 211202 |  | 731.5 | 211202 | 733.3333 | 211202 | 735.1667 | 211202 | 727.6667 | 211202
744.6667 | 211202 |  | 748.3333 | 211202 | 750 | 211202 | 752 | 211202 | 744.6667 | 211202
761.3333 | 211202 |  | 765.1667 | 211202 | 767 | 211202 | 768.8333 | 211202 | 761.3333 | 211202
778.3333 | 211202 |  | 782 | 211202 | 784 | 211202 | 785.6667 | 211202 | 778.3333 | 211202
794.8333 | 211202 |  | 798.6667 | 211202 | 800.5 | 211202 | 802.3333 | 211202 | 794.8333 | 211202
811.6667 | 211202 |  | 815.5 | 211202 | 817.3333 | 211202 | 819.1667 | 211202 | 811.6667 | 211202
828.5 | 211202 |  | 832.1667 | 211202 | 834 | 211202 | 836 | 211202 | 828.5 | 211202
845.5 | 211202 |  | 849.1667 | 211202 | 851 | 211202 | 853 | 211202 | 845.5 | 211202
862.3333 | 211202 |  | 866 | 211202 | 868 | 211202 | 869.6667 | 211202 | 862.3333 | 211202
879.1667 | 211202 |  | 882.8333 | 211202 | 884.5 | 211202 | 886.5 | 211202 | 879.1667 | 211202
895.6667 | 211202 |  | 899.6667 | 211202 | 901.3333 | 211202 | 903.3333 | 211202 | 895.6667 | 211202
912.6667 | 211202 |  | 916.3333 | 211202 | 918 | 211202 | 920 | 211202 | 912.6667 | 211202
929.3333 | 211202 |  | 933.1667 | 211202 | 935 | 211202 | 936.8333 | 211202 | 929.3333 | 211202
946.3333 | 211202 |  | 950 | 211202 | 952 | 211202 | 953.6667 | 211202 | 946.3333 | 211202
963 | 211202 |  | 966.6667 | 211202 | 968.5 | 105551 | 970.5 | 211202 | 963 | 105551
979.8333 | 211202 |  | 983.5 | 211202 | 985.5 | 211202 | 987.1667 | 211202 | 979.8333 | 211202
996.5 | 211202 |  | 1000.3333 | 211202 | 1002.1667 | 211202 | 1004 | 211202 | 996.5 | 211202
1013.3333 | 211202 |  | 1017 | 211202 | 1019 | 211202 | 1020.6667 | 211202 | 1013.3333 | 211202
1030.1667 | 211202 |  | 1034 | 211202 | 1035.8333 | 211202 | 1037.6667 | 211202 | 1030.1667 | 211202
1046.8333 | 211202 |  | 1050.6667 | 211202 | 1052.5 | 211202 | 1054.3333 | 211202 | 1046.8333 | 211202
1063.6667 | 211202 |  | 1067.5 | 211202 | 1069.3333 | 211202 | 1071.1667 | 211202 | 1063.6667 | 211202
1080.5 | 211202 |  | 1084.3333 | 211202 | 1086.1667 | 211202 | 1088 | 211202 | 1080.5 | 211202
1097.1667 | 211202 |  | 1100.8333 | 211202 | 1103 | 211202 | 1104.6667 | 211202 | 1097.1667 | 211202
1114.1667 | 211202 |  | 1117.8333 | 211202 | 1119.6667 | 211202 | 1121.6667 | 211202 | 1114.1667 | 211202
1131.1667 | 211202 |  | 1134.8333 | 211202 | 1136.5 | 211202 | 1138.5 | 211202 | 1131.1667 | 211202
1147.6667 | 211202 |  | 1151.5 | 211202 | 1153.3333 | 211202 | 1155.1667 | 211202 | 1147.6667 | 211202
1164.5 | 71449.1127 |  | 1168.1667 | 3430.9532 | 1170 | 211202 | 1172 | 41480.9167 | 1164.5 | 3430.9532
1181.3333 | 601.5191 |  | 1185 | 5084.9971 | 1187 | 53146.3139 | 1188.6667 | 697.8968 | 1181.3333 | 601.5191
1198.1667 | 2693.3608 |  | 1201.8333 | 3502.9345 | 1203.6667 | 42554.2903 | 1205.6667 | 3693.4694 | 1198.1667 | 2693.3608
1214.8333 | 1415.8642 |  | 1218.6667 | 6049.5281 | 1220.5 | 52881.5994 | 1222.3333 | 2338.4667 | 1214.8333 | 1415.8642
1231.6667 | 9795.4823 |  | 1235.5 | 11228.8195 | 1237.3333 | 53731.8907 | 1239.1667 | 5526.8871 | 1231.6667 | 5526.8871
1248.5 | 1633.2462 |  | 1252.1667 | 428.6964 | 1254 | 587.9838 | 1256 | 1941.4637 | 1248.5 | 428.6964
1265.3333 | 335.4915 |  | 1269 | 172.1945 | 1271 | 217.7678 | 1272.6667 | 1017.8796 | 1265.3333 | 172.1945
1282.1667 | 104.1248 |  | 1285.8333 | 91.3765 | 1287.6667 | 154.0398 | 1289.6667 | 624.2303 | 1282.1667 | 91.3765
1298.8333 | 389.9832 |  | 1302.6667 | 47.2916 | 1304.5 | 162.3588 | 1306.3333 | 42.0472 | 1298.8333 | 42.0472
1315.6667 | 205.7088 |  | 1319.5 | 1877.5837 | 1321.3333 | 251.138 | 1323.1667 | 484.1177 | 1315.6667 | 205.7088
1332.5 | 99.9485 |  | 1336.1667 | 114.4508 | 1338 | 106.5388 | 1340 | 98.808 | 1332.5 | 98.808
1349.3333 | 443.9816 |  | 1353 | 2.3384 | 1355 | 2.2443 | 1356.6667 | 383.8161 | 1349.3333 | 2.2443
1366.1667 | 109.3286 |  | 1369.8333 | 49.1865 | 1371.6667 | 288.6634 | 1373.6667 | 63.0916 | 1366.1667 | 49.1865
1382.8333 | 323.9766 |  | 1386.6667 | 104.0849 | 1388.5 | 109.1213 | 1390.3333 | 283.0308 | 1382.8333 | 104.0849
1399.6667 | 391.9274 |  | 1403.5 | 1725.1637 | 1405.3333 | 1348.7556 | 1407.1667 | 495.3552 | 1399.6667 | 391.9274
1416.5 | 56.7823 |  | 1420.1667 | 70.7739 | 1422 | 155.4326 | 1424 | 98.8493 | 1416.5 | 56.7823
1433.3333 | 42.4388 |  | 1437 | 34.4044 | 1439 | 148.3523 | 1440.6667 | 189.8072 | 1433.3333 | 34.4044
1450.1667 | 17.5747 |  | 1453.8333 | 395.7075 | 1455.6667 | 26.1781 | 1457.6667 | 15.4737 | 1450.1667 | 15.4737
1466.8333 | 1130.5566 |  | 1470.6667 | 35.937 | 1472.5 | 37.9431 | 1474.3333 | 1549.5781 | 1466.8333 | 35.937
1483.6667 | 133.3708 |  | 1487.5 | 178.9337 | 1489.3333 | 129.0186 | 1491.1667 | 126.4858 | 1483.6667 | 126.4858
1500.5 | 12.7688 |  | 1504.1667 | 60.7906 | 1506 | 15.4273 | 1508 | 446.8815 | 1500.5 | 12.7688
1517.3333 | 554.4191 |  | 1521 | 345.8884 | 1523 | 1303.3571 | 1524.6667 | 401.6753 | 1517.3333 | 345.8884
1534.1667 | 122.7662 |  | 1537.8333 | 52.9997 | 1539.6667 | 636.5577 | 1541.6667 | 60.2658 | 1534.1667 | 52.9997
1550.8333 | 2170.8797 |  | 1554.6667 | 808.5163 | 1556.5 | 407.3687 | 1558.3333 | 508.5053 | 1550.8333 | 407.3687
1567.6667 | 114.3567 |  | 1571.5 | 67.8635 | 1573.3333 | 84.5382 | 1575.1667 | 1364.7469 | 1567.6667 | 67.8635
1584.5 | 452.603 |  | 1588.1667 | 607.9069 | 1590 | 216.3774 | 1592 | 263.6966 | 1584.5 | 216.3774
1601.3333 | 330.7764 |  | 1605 | 66.5595 | 1607 | 110.6033 | 1608.6667 | 79.966 | 1601.3333 | 66.5595
1617.8333 | 95.9176 |  | 1621.8333 | 79.242 | 1623.6667 | 165.8205 | 1625.3333 | 101.8773 | 1617.8333 | 79.242
1634.8333 | 118.6452 |  | 1638.6667 | 149.916 | 1640.5 | 989.8851 | 1642.3333 | 282.4741 | 1634.8333 | 118.6452
1651.6667 | 361.6466 |  | 1655.5 | 87.251 | 1657.3333 | 99.8272 | 1659.1667 | 81.9896 | 1651.6667 | 81.9896
1668.5 | 24.5404 |  | 1672.1667 | 839.7617 | 1674 | 27.4224 | 1676 | 38.0658 | 1668.5 | 24.5404
1685.3333 | 29.3774 |  | 1689 | 133.4381 | 1691 | 630.508 | 1692.6667 | 36.0657 | 1685.3333 | 29.3774
1702.1667 | 72.65 |  | 1705.8333 | 429.7746 | 1707.6667 | 392.1603 | 1709.6667 | 89.8148 | 1702.1667 | 72.65
1718.8333 | 413.4992 |  | 1722.6667 | 202.1895 | 1724.5 | 219.6366 | 1726.3333 | 214.5653 | 1718.8333 | 202.1895
1735.6667 | 92.1169 |  | 1739.5 | 84.7593 | 1741.3333 | 107.6309 | 1743.1667 | 140.4621 | 1735.6667 | 84.7593
1752.5 | 127.3037 |  | 1756.1667 | 282.5203 | 1758 | 310.1092 | 1760 | 100.0812 | 1752.5 | 100.0812
1769.3333 | 73.1033 |  | 1773 | 70.902 | 1775 | 103.9161 | 1776.6667 | 134.0474 | 1769.3333 | 70.902
1786.1667 | 136.83 |  | 1789.8333 | 122.4699 | 1791.6667 | 1714.7967 | 1793.6667 | 476.3302 | 1786.1667 | 122.4699
1802.8333 | 243.9983 |  | 1806.6667 | 163.4724 | 1808.5 | 148.2467 | 1810.3333 | 379.0177 | 1802.8333 | 148.2467
1819.6667 | 28.1598 |  | 1823.5 | 53.8813 | 1825.1667 | 31.9205 | 1827 | 68.9884 | 1819.6667 | 28.1598
1836.5 | 135.0725 |  | 1840.1667 | 165.1642 | 1842 | 177.3104 | 1844 | 329.4102 | 1836.5 | 135.0725

## C-C
Conductor to Conductor Resistances
Penlight Test 10 |  |  | 2006-07-27 | 15:36
PVC | 3-C | Air Drop (Horizontal Run)
300 C | 6.1 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C3-4 | Penlight Time | Minimums
-114.5 | 211201.9994 | -112 | 211201.9994 | -109 | 211201.9994 | -106.5 | 211201.9994 | -103.5 | 211201.9994 | -101 | 211201.9994 | -114.5 | 211201.9994
-98 | 211201.9994 | -95.5 | 211201.9994 | -92.5 | 211201.9994 | -89.5 | 211201.9994 | -87 | 211201.9994 | -84 | 211201.9994 | -98 | 211201.9994
-81.5 | 211201.9994 | -78.5 | 211201.9994 | -75.5 | 211201.9994 | -73 | 211201.9994 | -70 | 211201.9994 | -67.5 | 211201.9994 | -81.5 | 211201.9994
-64.5 | 211201.9994 | -61.5 | 211201.9994 | -59 | 211201.9994 | -56 | 211201.9994 | -53.5 | 211201.9994 | -50.5 | 211201.9994 | -64.5 | 211201.9994
-47.5 | 211201.9994 | -44.5 | 211201.9994 | -42 | 211201.9994 | -39.5 | 211201.9994 | -36.5 | 211201.9994 | -33.5 | 211201.9994 | -47.5 | 211201.9994
-31 | 211201.9994 | -28 | 211201.9994 | -25.5 | 211201.9994 | -22.5 | 211201.9994 | -19.5 | 211201.9994 | -17 | 211201.9994 | -31 | 211201.9994
-14 | 211201.9994 | -11.5 | 211201.9994 | -8.5 | 211201.9994 | -5.5 | 211201.9994 | -3 | 211201.9994 | -1.4901e-07 | 211201.9994 | -14 | 211201.9994
2.5 | 211201.9994 | 5.5 | 211201.9994 | 8.5 | 211201.9994 | 11 | 211201.9994 | 14 | 211201.9994 | 16.5 | 211201.9994 | 2.5 | 211201.9994
19.5 | 211201.9994 | 22.5 | 211201.9994 | 25 | 211201.9994 | 28 | 211201.9994 | 30.5 | 211201.9994 | 33.5 | 211201.9994 | 19.5 | 211201.9994
36.5 | 211201.9994 | 39 | 211201.9994 | 42 | 211201.9994 | 44.5 | 211201.9994 | 47.5 | 211201.9994 | 50.5 | 211201.9994 | 36.5 | 211201.9994
53 | 211201.9994 | 56 | 211201.9994 | 58.5 | 211201.9994 | 61.5 | 211201.9994 | 64.5 | 211201.9994 | 67 | 211201.9994 | 53 | 211201.9994
70 | 211201.9994 | 72.5 | 211201.9994 | 75.5 | 211201.9994 | 78.5 | 211201.9994 | 81 | 211201.9994 | 84 | 211201.9994 | 70 | 211201.9994
86.5 | 211201.9994 | 89.5 | 211201.9994 | 92.5 | 211201.9994 | 95 | 211201.9994 | 98 | 211201.9994 | 100.5 | 211201.9994 | 86.5 | 211201.9994
103.5 | 211201.9994 | 106.5 | 211201.9994 | 109 | 211201.9994 | 112 | 211201.9994 | 114.5 | 211201.9994 | 117.5 | 211201.9994 | 103.5 | 211201.9994
120.5 | 211201.9994 | 123 | 211201.9994 | 126 | 211201.9994 | 128.5 | 211201.9994 | 131.5 | 211201.9994 | 134.5 | 211201.9994 | 120.5 | 211201.9994
137 | 211201.9994 | 140 | 211201.9994 | 142.5 | 211201.9994 | 145.5 | 211002.0947 | 148.5 | 211201.9994 | 151 | 211201.9994 | 137 | 211002.0947
154 | 211201.9994 | 156.5 | 211201.9994 | 159.5 | 211201.9994 | 162.5 | 211201.9994 | 165 | 211201.9994 | 168 | 211201.9994 | 154 | 211201.9994
170.5 | 211201.9994 | 173.5 | 211201.9994 | 176.5 | 211201.9994 | 179 | 211201.9994 | 182 | 211201.9994 | 184.5 | 211201.9994 | 170.5 | 211201.9994
187.5 | 211201.9994 | 190.5 | 211201.9994 | 193 | 211201.9994 | 197 | 211201.9994 | 198.5 | 211201.9994 | 201.5 | 211201.9994 | 187.5 | 211201.9994
204.5 | 211201.9994 | 207 | 211201.9994 | 210 | 211201.9994 | 212.5 | 211201.9994 | 215.5 | 211201.9994 | 218.5 | 211201.9994 | 204.5 | 211201.9994
221 | 211201.9994 | 224 | 211201.9994 | 226.5 | 211201.9994 | 229.5 | 211201.9994 | 232.5 | 211201.9994 | 235 | 211201.9994 | 221 | 211201.9994
238 | 211201.9994 | 240.5 | 211201.9994 | 243.5 | 211201.9994 | 246.5 | 211201.9994 | 249 | 211201.9994 | 252 | 211201.9994 | 238 | 211201.9994
254.5 | 211201.9994 | 257.5 | 211201.9994 | 260.5 | 211201.9994 | 263 | 211201.9994 | 266 | 211201.9994 | 268.5 | 211201.9994 | 254.5 | 211201.9994
271.5 | 211201.9994 | 274.5 | 211201.9994 | 277 | 211201.9994 | 280 | 211201.9994 | 282.5 | 211201.9994 | 285.5 | 211201.9994 | 271.5 | 211201.9994
288.5 | 211201.9994 | 291 | 211201.9994 | 294 | 211201.9994 | 296.5 | 211201.9994 | 299.5 | 211201.9994 | 302.5 | 211201.9994 | 288.5 | 211201.9994
305 | 211201.9994 | 308 | 211201.9994 | 310.5 | 211201.9994 | 313.5 | 211201.9994 | 316.5 | 211201.9994 | 319 | 211201.9994 | 305 | 211201.9994
322 | 211201.9994 | 324.5 | 211201.9994 | 327.5 | 211201.9994 | 330.5 | 211201.9994 | 333 | 211201.9994 | 336 | 105550.9988 | 322 | 105550.9988
338.5 | 211201.9994 | 341.5 | 211201.9994 | 344.5 | 211201.9994 | 347 | 211201.9994 | 350 | 211201.9994 | 352.5 | 211201.9994 | 338.5 | 211201.9994
355.5 | 211201.9994 | 358.5 | 211201.9994 | 361 | 211201.9994 | 364 | 211201.9994 | 366.5 | 211201.9994 | 369.5 | 211201.9994 | 355.5 | 211201.9994
372.5 | 211201.9994 | 375 | 211201.9994 | 378 | 211201.9994 | 380.5 | 211201.9994 | 383.5 | 211201.9994 | 386.5 | 211201.9994 | 372.5 | 211201.9994
389 | 211201.9994 | 392 | 211201.9994 | 394.5 | 211201.9994 | 397.5 | 211201.9994 | 400.5 | 211201.9994 | 403 | 211201.9994 | 389 | 211201.9994
406 | 211201.9994 | 408.5 | 211201.9994 | 411.5 | 211201.9994 | 414.5 | 211201.9994 | 417 | 211201.9994 | 420 | 211201.9994 | 406 | 211201.9994
422.5 | 211201.9994 | 425.5 | 211201.9994 | 428.5 | 211201.9994 | 431 | 211201.9994 | 434 | 211201.9994 | 436.5 | 211201.9994 | 422.5 | 211201.9994
439.5 | 211201.9994 | 442.5 | 211201.9994 | 445 | 211201.9994 | 448 | 211201.9994 | 450.5 | 211201.9994 | 453.5 | 211201.9994 | 439.5 | 211201.9994
456.5 | 211201.9994 | 459 | 211201.9994 | 462 | 211201.9994 | 464.5 | 211201.9994 | 467.5 | 211201.9994 | 470.5 | 211201.9994 | 456.5 | 211201.9994
473 | 211201.9994 | 476 | 211201.9994 | 478.5 | 211201.9994 | 481.5 | 211201.9994 | 484.5 | 211201.9994 | 487 | 211201.9994 | 473 | 211201.9994
490 | 211201.9994 | 492.5 | 211201.9994 | 495.5 | 211201.9994 | 498.5 | 211201.9994 | 501 | 211201.9994 | 504 | 211201.9994 | 490 | 211201.9994
506.5 | 211201.9994 | 509.5 | 211201.9994 | 512.5 | 211201.9994 | 515 | 211201.9994 | 518 | 211201.9994 | 520.5 | 211201.9994 | 506.5 | 211201.9994
523.5 | 211201.9994 | 526.5 | 211201.9994 | 529 | 211201.9994 | 532 | 211201.9994 | 534.5 | 211201.9994 | 537.5 | 211201.9994 | 523.5 | 211201.9994
540.5 | 211201.9994 | 543 | 211201.9994 | 546 | 211201.9994 | 548.5 | 211201.9994 | 551.5 | 211201.9994 | 554.5 | 211201.9994 | 540.5 | 211201.9994
557 | 211201.9994 | 560 | 105550.9988 | 562.5 | 211201.9994 | 565.5 | 211201.9994 | 568.5 | 211201.9994 | 571 | 211201.9994 | 557 | 105550.9988
573.5 | 211201.9994 | 576.5 | 211201.9994 | 579.5 | 211201.9994 | 582.5 | 211201.9994 | 585 | 211201.9994 | 588 | 211201.9994 | 573.5 | 211201.9994
590.5 | 211201.9994 | 593.5 | 211201.9994 | 596.5 | 211201.9994 | 599 | 211201.9994 | 602 | 211201.9994 | 604.5 | 211201.9994 | 590.5 | 211201.9994
607.5 | 211201.9994 | 610.5 | 211201.9994 | 613 | 211201.9994 | 616 | 211201.9994 | 618.5 | 211201.9994 | 621.5 | 211201.9994 | 607.5 | 211201.9994
624.5 | 211201.9994 | 627 | 211201.9994 | 630 | 211201.9994 | 632.5 | 211201.9994 | 635.5 | 211201.9994 | 638.5 | 211201.9994 | 624.5 | 211201.9994
641 | 211201.9994 | 643.5 | 211201.9994 | 646.5 | 211201.9994 | 649.5 | 211201.9994 | 652.5 | 211201.9994 | 655 | 211201.9994 | 641 | 211201.9994
658 | 211201.9994 | 660.5 | 211201.9994 | 663.5 | 211201.9994 | 666.5 | 211201.9994 | 669 | 211201.9994 | 671.5 | 211201.9994 | 658 | 211201.9994
674.5 | 211201.9994 | 677.5 | 211201.9994 | 680.5 | 211201.9994 | 683 | 211201.9994 | 686 | 211201.9994 | 688.5 | 211201.9994 | 674.5 | 211201.9994
691.5 | 211201.9994 | 694.5 | 211201.9994 | 697 | 211201.9994 | 700 | 211201.9994 | 702.5 | 211201.9994 | 705.5 | 211201.9994 | 691.5 | 211201.9994
708.5 | 211201.9994 | 711 | 211201.9994 | 714 | 211201.9994 | 716.5 | 211201.9994 | 719.5 | 211201.9994 | 722 | 211201.9994 | 708.5 | 211201.9994
725 | 211201.9994 | 727.5 | 211201.9994 | 730.5 | 211201.9994 | 733.5 | 211201.9994 | 736 | 211201.9994 | 739 | 211201.9994 | 725 | 211201.9994
742 | 211201.9994 | 744.5 | 211201.9994 | 747.5 | 211201.9994 | 750 | 211201.9994 | 753 | 211201.9994 | 755.5 | 211201.9994 | 742 | 211201.9994
758.5 | 211201.9994 | 761.5 | 211201.9994 | 764 | 211201.9994 | 767 | 211201.9994 | 770 | 211201.9994 | 772.5 | 211201.9994 | 758.5 | 211201.9994
775.5 | 211201.9994 | 778.5 | 211201.9994 | 781 | 211201.9994 | 784 | 211201.9994 | 786.5 | 211201.9994 | 789.5 | 211201.9994 | 775.5 | 211201.9994
792 | 211201.9994 | 795 | 211201.9994 | 797.5 | 211201.9994 | 800.5 | 211201.9994 | 803.5 | 211201.9994 | 806 | 211201.9994 | 792 | 211201.9994
809 | 211201.9994 | 811.5 | 211201.9994 | 814.5 | 211201.9994 | 817.5 | 211201.9994 | 820 | 211201.9994 | 823 | 211201.9994 | 809 | 211201.9994
825.5 | 211201.9994 | 828.5 | 211201.9994 | 831.5 | 211201.9994 | 834 | 211201.9994 | 837 | 211201.9994 | 839.5 | 211201.9994 | 825.5 | 211201.9994
842.5 | 211201.9994 | 845.5 | 211201.9994 | 848.5 | 211201.9994 | 851 | 211201.9994 | 854 | 211201.9994 | 856.5 | 211201.9994 | 842.5 | 211201.9994
859.5 | 211201.9994 | 862.5 | 211201.9994 | 865 | 211201.9994 | 868 | 211201.9994 | 870.5 | 211201.9994 | 873.5 | 211201.9994 | 859.5 | 211201.9994
876.5 | 211201.9994 | 879 | 211201.9994 | 882 | 211201.9994 | 884.5 | 210902.142 | 887.5 | 211201.9994 | 890 | 211201.9994 | 876.5 | 210902.142
893 | 211201.9994 | 895.5 | 211201.9994 | 898.5 | 211201.9994 | 901.5 | 211201.9994 | 904.5 | 211201.9994 | 907 | 211201.9994 | 893 | 211201.9994
910 | 211201.9994 | 912.5 | 211201.9994 | 915.5 | 211201.9994 | 918 | 211201.9994 | 921 | 211201.9994 | 923.5 | 211201.9994 | 910 | 211201.9994
926.5 | 211201.9994 | 929.5 | 211201.9994 | 932 | 211201.9994 | 935 | 211201.9994 | 938 | 211201.9994 | 940.5 | 211201.9994 | 926.5 | 211201.9994
943.5 | 211201.9994 | 946.5 | 211201.9994 | 949 | 211201.9994 | 952 | 211201.9994 | 954.5 | 211201.9994 | 957.5 | 211201.9994 | 943.5 | 211201.9994
960 | 211201.9994 | 963 | 211201.9994 | 966 | 211201.9994 | 968.5 | 211201.9994 | 971.5 | 211201.9994 | 974 | 211201.9994 | 960 | 211201.9994
977 | 211201.9994 | 980 | 211201.9994 | 982.5 | 211201.9994 | 985.5 | 211201.9994 | 988 | 211201.9994 | 991 | 211201.9994 | 977 | 211201.9994
993.5 | 211201.9994 | 996.5 | 211201.9994 | 999.5 | 211201.9994 | 1002.5 | 211201.9994 | 1005 | 211201.9994 | 1007.5 | 211201.9994 | 993.5 | 211201.9994
1010.5 | 211201.9994 | 1013.5 | 211201.9994 | 1016 | 211201.9994 | 1019 | 211201.9994 | 1021.5 | 211201.9994 | 1024.5 | 211201.9994 | 1010.5 | 211201.9994
1027.5 | 211201.9994 | 1030 | 211201.9994 | 1033 | 211201.9994 | 1036 | 211201.9994 | 1038.5 | 211201.9994 | 1041.5 | 211201.9994 | 1027.5 | 211201.9994
1044 | 211002.0947 | 1047 | 211201.9994 | 1049.5 | 211201.9994 | 1052.5 | 211201.9994 | 1055.5 | 211201.9994 | 1058 | 211201.9994 | 1044 | 211002.0947
1061 | 211201.9994 | 1063.5 | 211201.9994 | 1066.5 | 211201.9994 | 1069.5 | 211201.9994 | 1072 | 211201.9994 | 1075 | 211201.9994 | 1061 | 211201.9994
1077.5 | 211201.9994 | 1080.5 | 211201.9994 | 1083.5 | 211201.9994 | 1086.5 | 211201.9994 | 1089 | 211201.9994 | 1091.5 | 211201.9994 | 1077.5 | 211201.9994
1094 | 211201.9994 | 1097.5 | 211201.9994 | 1100 | 211201.9994 | 1103 | 211201.9994 | 1105.5 | 211201.9994 | 1108.5 | 211201.9994 | 1094 | 211201.9994
1111.5 | 211201.9994 | 1114 | 211201.9994 | 1117 | 211201.9994 | 1119.5 | 211201.9994 | 1122.5 | 211201.9994 | 1125.5 | 211201.9994 | 1111.5 | 211201.9994
1128.5 | 211201.9994 | 1131 | 211201.9994 | 1134 | 211201.9994 | 1136.5 | 211201.9994 | 1139.5 | 211201.9994 | 1142 | 211201.9994 | 1128.5 | 211201.9994
1145 | 211201.9994 | 1147.5 | 211201.9994 | 1150.5 | 211201.9994 | 1153.5 | 211201.9994 | 1156 | 211201.9994 | 1159 | 211201.9994 | 1145 | 211201.9994
1161.5 | 211201.9994 | 1164.5 | 211201.9994 | 1167.5 | 5355.5628 | 1170 | 211201.9994 | 1173 | 19.4242 | 1175.5 | 105401.071 | 1161.5 | 19.4242
1178.5 | 211002.0947 | 1181.5 | 211002.0947 | 1184 | 6.2805 | 1187 | 16092.9503 | 1189.5 | 15.4751 | 1192.5 | 42100.5417 | 1178.5 | 6.2805
1195.5 | 70267.3018 | 1198 | 211002.0947 | 1201 | 26.8109 | 1203.5 | 14936.4716 | 1206.5 | 8.8101 | 1209.5 | 30014.8142 | 1195.5 | 8.8101
1212 | 70267.3018 | 1215 | 210902.142 | 1217.5 | 5.0144 | 1220.5 | 13933.959 | 1223.5 | 16.7333 | 1226 | 30000.6429 | 1212 | 5.0144
1229 | 70267.3018 | 1231.5 | 105401.071 | 1234.5 | 8.0539 | 1237.5 | 12283.1399 | 1240 | 19.2626 | 1243 | 405.4189 | 1229 | 8.0539
1245.5 | 10.8389 | 1248.5 | 17.6155 | 1251.5 | 23.7685 | 1254 | 17.5016 | 1257 | 1.7499 | 1259.5 | 1.0116 | 1245.5 | 1.0116
1262.5 | 8.2194 | 1265.5 | 0.90876 | 1268 | 15.5595 | 1271 | 8.5281 | 1273.5 | 15.1609 | 1276.5 | 5.5642 | 1262.5 | 0.90876
1279.5 | 8.2732 | 1282 | 17.7246 | 1285 | 3.0714 | 1287.5 | 15.1439 | 1290.5 | 8.6026 | 1293.5 | 3.3746 | 1279.5 | 3.0714
1296 | 3.1409 | 1299 | 24.3976 | 1301.5 | 16.0064 | 1304.5 | 6.7728 | 1307.5 | 4.138 | 1310 | 20.5281 | 1296 | 3.1409
1313 | 3.0747 | 1315.5 | 2.9459 | 1318.5 | 25.4539 | 1321.5 | 6.5457 | 1324 | 23.4547 | 1327 | 5.9963 | 1313 | 2.9459
1329.5 | 2.2228 | 1332.5 | 12.3443 | 1335.5 | 15.4329 | 1338 | 18.7632 | 1341 | 5.5072 | 1343.5 | 20.9676 | 1329.5 | 2.2228
1346.5 | 3.8116 | 1349.5 | 14.2463 | 1352 | 12.5285 | 1355 | 0.10712 | 1357.5 | 14.8157 | 1360.5 | 21.4332 | 1346.5 | 0.10712
1363.5 | 9.4355 | 1366 | 18.5656 | 1369 | 17.5315 | 1371.5 | 7.7893 | 1374.5 | 8.4616 | 1377.5 | 12.8555 | 1363.5 | 7.7893
1380 | 9.4421 | 1383 | 15.2886 | 1385.5 | 14.3942 | 1388.5 | 3.5313 | 1391.5 | 19.8136 | 1394 | 14.9041 | 1380 | 3.5313
1397 | 12.573 | 1399.5 | 6.154 | 1402.5 | 14.991 | 1405.5 | 26.2349 | 1408 | 28.7208 | 1411 | 7.2052 | 1397 | 6.154
1413.5 | 7.7855 | 1416.5 | 13.4147 | 1419.5 | 19.7841 | 1422 | 9.0089 | 1425 | 0.27786 | 1427.5 | 11.717 | 1413.5 | 0.27786
1430.5 | 6.3654 | 1433.5 | 12.268 | 1436 | 22.8483 | 1439 | 13.1951 | 1441.5 | 31.3295 | 1444.5 | 10.3283 | 1430.5 | 6.3654
1447.5 | 1.3841 | 1450 | 2.3385 | 1453 | 2.0345 | 1455.5 | 10.5613 | 1458.5 | 16.3587 | 1461.5 | 29.9155 | 1447.5 | 1.3841
1464 | 32.1818 | 1467 | 30.9389 | 1469.5 | 19.997 | 1472.5 | 2.2742 | 1475.5 | 2.2797 | 1478 | 3.4784 | 1464 | 2.2742
1481 | 4.4466 | 1483.5 | 8.8004 | 1486.5 | 36.8493 | 1489.5 | 7.477 | 1492 | 16.0443 | 1495 | 7.9878 | 1481 | 4.4466
1497.5 | 8.192 | 1500.5 | 2.1831 | 1503.5 | 19.1381 | 1506 | 14.5034 | 1509 | 9.3635 | 1511.5 | 20.6929 | 1497.5 | 2.1831
1514.5 | 34.9143 | 1517.5 | 1.102 | 1520 | 20.7044 | 1523 | 18.799 | 1525.5 | 22.5918 | 1528.5 | 15.0038 | 1514.5 | 1.102
1531.5 | 13.6027 | 1534 | 16.4633 | 1537 | 7.3428 | 1539.5 | 17.373 | 1542.5 | 3.3637 | 1545.5 | 16.6495 | 1531.5 | 3.3637
1548 | 20.9755 | 1551 | 25.6428 | 1553.5 | 32.636 | 1556.5 | 39.7787 | 1559.5 | 15.7981 | 1562 | 12.6632 | 1548 | 12.6632
1565 | 23.5556 | 1567.5 | 10.4661 | 1570.5 | 23.2663 | 1573.5 | 2.2497 | 1576 | 19.9574 | 1579 | 6.0805 | 1565 | 2.2497
1581.5 | 25.8393 | 1584.5 | 13.7749 | 1587.5 | 13.2579 | 1590 | 21.6233 | 1593 | 15.1323 | 1595.5 | 2.441 | 1581.5 | 2.441
1598.5 | 2.7836 | 1601.5 | 26.9194 | 1604 | 15.2397 | 1607 | 13.8797 | 1609.5 | 6.031 | 1612.5 | 17.5702 | 1598.5 | 2.7836
1615.5 | 15.0136 | 1618 | 0.93772 | 1620 | 3.3962 | 1623.5 | 15.0781 | 1626.5 | 11.0466 | 1629.5 | 16.4262 | 1615.5 | 0.93772
1632 | 11.5309 | 1635 | 14.9364 | 1637.5 | 31.3771 | 1640.5 | 18.1025 | 1643.5 | 14.7312 | 1646 | 12.7268 | 1632 | 11.5309
1649 | 32.6024 | 1651.5 | 2.7729 | 1654.5 | 0.67334 | 1657.5 | 4.5405 | 1660 | 6.153 | 1663 | 4.1277 | 1649 | 0.67334
1665.5 | 16.4011 | 1668.5 | 0.96351 | 1671.5 | 3.2084 | 1674 | 33.9569 | 1677 | 16.55 | 1679.5 | 26.7297 | 1665.5 | 0.96351
1682.5 | 12.8001 | 1685.5 | 33.8523 | 1688 | 4.6191 | 1691 | 5.9482 | 1693.5 | 14.1282 | 1696.5 | 18.6961 | 1682.5 | 4.6191
1699.5 | 19.7248 | 1702 | 18.9799 | 1705 | 7.7945 | 1707.5 | 32.1844 | 1710.5 | 12.9968 | 1713.5 | 15.1669 | 1699.5 | 7.7945
1716 | 1.9225 | 1719 | 23.2392 | 1721.5 | 35.7519 | 1724.5 | 7.8113 | 1727.5 | 12.9939 | 1730 | 19.1036 | 1716 | 1.9225
1733 | 9.1491 | 1735.5 | 15.7834 | 1738.5 | 21.9403 | 1741.5 | 9.7525 | 1744 | 4.1942 | 1747 | 11.1871 | 1733 | 4.1942
1749.5 | 20.7567 | 1752.5 | 29.3042 | 1755.5 | 17.5311 | 1758 | 5.9111 | 1761 | 2.8303 | 1763.5 | 34.3438 | 1749.5 | 2.8303
1766.5 | 4.2518 | 1769.5 | 9.0817 | 1772 | 4.541 | 1775 | 25.4642 | 1777.5 | 3.7991 | 1780.5 | 12.2238 | 1766.5 | 3.7991
1783.5 | 6.4549 | 1786 | 14.2955 | 1789 | 18.9307 | 1791.5 | 14.6418 | 1794.5 | 6.2108 | 1797.5 | 1.9205 | 1783.5 | 1.9205
1800 | 4.9451 | 1803 | 16.2694 | 1805.5 | 17.0407 | 1808.5 | 6.425 | 1811.5 | 6.8259 | 1814 | 4.7833 | 1800 | 4.7833
1817 | 31.127 | 1819.5 | 2.5699 | 1822.5 | 5.0359 | 1825.5 | 9.299 | 1828 | 8.7547 | 1830.5 | 18.3569 | 1817 | 2.5699
1833.5 | 17.1793 | 1836.5 | 12.9193 | 1839.5 | 29.1239 | 1842 | 21.8386 | 1845 | 12.4032 | 1847.5 | 11.3455 | 1833.5 | 11.3455

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5
0 | -115 | 20.6 | 26.3 | 26.5 | 26.7 | 25.3 | 25.3
1 | -114 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
2 | -113 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
3 | -112 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
4 | -111 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
5 | -110 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
6 | -109 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
7 | -108 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
8 | -107 | 20.6 | 26.3 | 26.5 | 26.7 | 25.3 | 25.3
9 | -106 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
10 | -105 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
11 | -104 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
12 | -103 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
13 | -102 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
14 | -101 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
15 | -100 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
16 | -99 | 20.6 | 26.3 | 26.5 | 26.7 | 25.3 | 25.3
17 | -98 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
18 | -97 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
19 | -96 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
20 | -95 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
21 | -94 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
22 | -93 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
23 | -92 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
24 | -91 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
25 | -90 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
26 | -89 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
27 | -88 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
28 | -87 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
29 | -86 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
30 | -85 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
31 | -84 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
32 | -83 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
33 | -82 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
34 | -81 | 20.6 | 26.3 | 26.5 | 26.7 | 25.3 | 25.3
35 | -80 | 20.6 | 26.3 | 26.5 | 26.7 | 25.3 | 25.3
36 | -79 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
37 | -78 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
38 | -77 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
39 | -76 | 20.6 | 26.3 | 26.5 | 26.8 | 25.3 | 25.3
40 | -75 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
41 | -74 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
42 | -73 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
43 | -72 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
44 | -71 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
45 | -70 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
46 | -69 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
47 | -68 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
48 | -67 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
49 | -66 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
50 | -65 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
51 | -64 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
52 | -63 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
53 | -62 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
54 | -61 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
55 | -60 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
56 | -59 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
57 | -58 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
58 | -57 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
59 | -56 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
60 | -55 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
61 | -54 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
62 | -53 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
63 | -52 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
64 | -51 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
65 | -50 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
66 | -49 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
67 | -48 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
68 | -47 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
69 | -46 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
70 | -45 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
71 | -44 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
72 | -43 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
73 | -42 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
74 | -41 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
75 | -40 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
76 | -39 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
77 | -38 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
78 | -37 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
79 | -36 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
80 | -35 | 20.6 | 26.4 | 26.5 | 26.8 | 25.3 | 25.3
81 | -34 | 20.6 | 27.5 | 24.5 | 27.5 | 25.6 | 25.4
82 | -33 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
83 | -32 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
84 | -31 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
85 | -30 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
86 | -29 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
87 | -28 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
88 | -27 | 20.6 | 27.7 | 24 | 27.6 | 25.7 | 25.4
89 | -26 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
90 | -25 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
91 | -24 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
92 | -23 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
93 | -22 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
94 | -21 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
95 | -20 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
96 | -19 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
97 | -18 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
98 | -17 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
99 | -16 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
100 | -15 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
101 | -14 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
102 | -13 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
103 | -12 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
104 | -11 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
105 | -10 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
106 | -9 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
107 | -8 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
108 | -7 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
109 | -6 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
110 | -5 | 20.5 | 27.7 | 24 | 27.6 | 25.7 | 25.4
111 | -4 | 20.5 | 27.8 | 23.9 | 27.6 | 25.7 | 25.4
112 | -3 | 20.5 | 28.1 | 23.2 | 27.9 | 25.9 | 25.5
113 | -2 | 20.5 | 28.4 | 22.8 | 28 | 25.9 | 25.5
114 | -1 | 20.8 | 28.5 | 22.6 | 28.1 | 25.9 | 25.5
115 | 0 | 21.7 | 28.5 | 22.5 | 28.1 | 25.9 | 25.5
116 | 1 | 23.5 | 28.5 | 22.6 | 28.1 | 25.9 | 25.5
117 | 2 | 25.9 | 28.4 | 22.7 | 28.1 | 25.9 | 25.5
118 | 3 | 28.8 | 28.5 | 22.6 | 28.1 | 26 | 25.6
119 | 4 | 32.2 | 28.5 | 22.6 | 28.1 | 26 | 25.6
120 | 5 | 35.9 | 28.5 | 22.6 | 28.1 | 26.1 | 25.7
121 | 6 | 40 | 28.5 | 22.6 | 28.1 | 26.1 | 25.7
122 | 7 | 44.3 | 28.5 | 22.6 | 28.1 | 26.2 | 25.8
123 | 8 | 48.8 | 28.5 | 22.7 | 28.1 | 26.2 | 25.9
124 | 9 | 53.4 | 28.5 | 22.7 | 28.1 | 26.3 | 26
125 | 10 | 58.2 | 28.5 | 22.6 | 28.2 | 26.4 | 26.1
126 | 11 | 63.1 | 28.5 | 22.7 | 28.2 | 26.5 | 26.3
127 | 12 | 68.1 | 28.6 | 22.7 | 28.2 | 26.7 | 26.4
128 | 13 | 73.2 | 28.6 | 22.7 | 28.2 | 26.8 | 26.6
129 | 14 | 78.4 | 28.7 | 22.6 | 28.3 | 26.9 | 26.8
130 | 15 | 83.7 | 28.7 | 22.6 | 28.3 | 27.1 | 27
131 | 16 | 89 | 28.8 | 22.6 | 28.4 | 27.3 | 27.2
132 | 17 | 94.4 | 28.8 | 22.7 | 28.5 | 27.5 | 27.4
133 | 18 | 99.9 | 28.9 | 22.7 | 28.5 | 27.8 | 27.6
134 | 19 | 105.4 | 29 | 22.7 | 28.6 | 28.1 | 27.9
135 | 20 | 110.9 | 29.1 | 22.7 | 28.7 | 28.3 | 28.2
136 | 21 | 116.5 | 29.1 | 22.7 | 28.7 | 28.6 | 28.5
137 | 22 | 122.2 | 29.3 | 22.7 | 28.8 | 28.9 | 28.9
138 | 23 | 127.8 | 29.4 | 22.7 | 28.9 | 29.2 | 29.2
139 | 24 | 133.6 | 29.5 | 22.7 | 29.1 | 29.5 | 29.6
140 | 25 | 139.3 | 29.7 | 22.7 | 29.2 | 29.8 | 30
141 | 26 | 145 | 29.8 | 22.7 | 29.3 | 30.2 | 30.4
142 | 27 | 150.6 | 30 | 22.7 | 29.5 | 30.5 | 30.8
143 | 28 | 156.2 | 30.2 | 22.8 | 29.7 | 31 | 31.2
144 | 29 | 161.9 | 30.3 | 22.8 | 29.8 | 31.4 | 31.7
145 | 30 | 167.6 | 30.6 | 22.8 | 30 | 31.9 | 32.3
146 | 31 | 173.3 | 30.8 | 22.8 | 30.2 | 32.4 | 32.8
147 | 32 | 179 | 31 | 22.9 | 30.4 | 32.9 | 33.3
148 | 33 | 184.6 | 31.2 | 22.9 | 30.7 | 33.4 | 33.9
149 | 34 | 190.4 | 31.5 | 22.9 | 30.9 | 33.9 | 34.5
150 | 35 | 196.1 | 31.8 | 22.9 | 31.2 | 34.5 | 35.1
151 | 36 | 201.8 | 32.1 | 23 | 31.5 | 35.1 | 35.8
152 | 37 | 207.6 | 32.4 | 23 | 31.7 | 35.8 | 36.5
153 | 38 | 213.3 | 32.8 | 23.1 | 32.1 | 36.5 | 37.2
154 | 39 | 219.1 | 33.1 | 23.1 | 32.4 | 37.1 | 38
155 | 40 | 224.6 | 33.5 | 23.1 | 32.7 | 37.9 | 38.7
156 | 41 | 230.2 | 33.9 | 23.2 | 33.1 | 38.6 | 39.5
157 | 42 | 235.8 | 34.3 | 23.2 | 33.5 | 39.3 | 40.4
158 | 43 | 241.4 | 34.7 | 23.3 | 33.8 | 40.1 | 41.3
159 | 44 | 246.9 | 35.2 | 23.3 | 34.3 | 41 | 42.2
160 | 45 | 252.4 | 35.7 | 23.3 | 34.7 | 41.9 | 43.1
161 | 46 | 258 | 36.2 | 23.4 | 35.1 | 42.8 | 44
162 | 47 | 263.6 | 36.7 | 23.5 | 35.6 | 43.8 | 45
163 | 48 | 269.2 | 37.3 | 23.6 | 36.1 | 44.7 | 46
164 | 49 | 274.7 | 37.7 | 23.9 | 36.5 | 45.7 | 47
165 | 50 | 280.1 | 38.3 | 23.9 | 37 | 46.7 | 48.1
166 | 51 | 285.3 | 39 | 23.9 | 37.6 | 47.7 | 49.2
167 | 52 | 289.9 | 39.7 | 24 | 38.1 | 48.8 | 50.4
168 | 53 | 294.2 | 40.3 | 24.1 | 38.7 | 49.9 | 51.5
169 | 54 | 298.1 | 41 | 24.3 | 39.3 | 50.9 | 52.6
170 | 55 | 301.7 | 41.7 | 24.4 | 39.9 | 52 | 53.8
171 | 56 | 305.4 | 42.5 | 24.5 | 40.6 | 53.1 | 54.9
172 | 57 | 308.8 | 43.2 | 24.6 | 41.2 | 54.2 | 56
173 | 58 | 312 | 44 | 25 | 41.9 | 55.3 | 57.2
174 | 59 | 315 | 44.7 | 25.3 | 42.5 | 56.3 | 58.3
175 | 60 | 317.7 | 45.4 | 25.8 | 43.1 | 57.4 | 59.4
176 | 61 | 320.2 | 46.2 | 26 | 43.8 | 58.6 | 60.5
177 | 62 | 322.2 | 47 | 26.3 | 44.5 | 59.7 | 61.6
178 | 63 | 323.9 | 47.9 | 26.6 | 45.3 | 60.7 | 62.7
179 | 64 | 325.4 | 48.7 | 26.8 | 46 | 61.8 | 63.7
180 | 65 | 326.5 | 49.6 | 27.1 | 46.8 | 62.9 | 64.8
181 | 66 | 327.5 | 50.5 | 27.6 | 47.5 | 63.9 | 65.8
182 | 67 | 328.2 | 51.5 | 27.8 | 48.3 | 64.9 | 66.7
183 | 68 | 328.7 | 52.5 | 28 | 49.1 | 65.9 | 67.8
184 | 69 | 329 | 53.5 | 28.2 | 49.9 | 66.9 | 68.7
185 | 70 | 329.4 | 54.4 | 28.5 | 50.7 | 67.9 | 69.7
186 | 71 | 329.5 | 55.4 | 28.8 | 51.6 | 68.8 | 70.6
187 | 72 | 329.6 | 56.4 | 29 | 52.4 | 69.7 | 71.5
188 | 73 | 329.6 | 57.4 | 29.3 | 53.3 | 70.6 | 72.4
189 | 74 | 329.6 | 58.4 | 29.6 | 54.1 | 71.5 | 73.3
190 | 75 | 329.6 | 59.4 | 30 | 55 | 72.4 | 74.1
191 | 76 | 329.6 | 60.4 | 30.3 | 55.9 | 73.3 | 75
192 | 77 | 329.4 | 61.4 | 30.6 | 56.8 | 74.1 | 75.8
193 | 78 | 329.2 | 62.4 | 31 | 57.6 | 74.9 | 76.6
194 | 79 | 329 | 63.3 | 31.3 | 58.5 | 75.8 | 77.4
195 | 80 | 328.7 | 64.3 | 31.6 | 59.3 | 76.6 | 78.1
196 | 81 | 328.6 | 65.3 | 32 | 60.2 | 77.4 | 78.9
197 | 82 | 328.2 | 66.4 | 32.2 | 61.1 | 78.2 | 79.7
198 | 83 | 327.8 | 67.3 | 32.6 | 61.9 | 78.9 | 80.4
199 | 84 | 327.3 | 68.2 | 33 | 62.6 | 79.7 | 81
200 | 85 | 326.9 | 69.2 | 33.4 | 63.4 | 80.4 | 81.8
201 | 86 | 326.5 | 70.1 | 33.7 | 64.2 | 81.2 | 82.4
202 | 87 | 326 | 71.1 | 34.2 | 65 | 81.9 | 83.1
203 | 88 | 325.7 | 71.9 | 34.6 | 65.7 | 82.6 | 83.8
204 | 89 | 325.3 | 72.8 | 35 | 66.4 | 83.2 | 84.4
205 | 90 | 324.8 | 73.7 | 35.4 | 67.1 | 83.9 | 85.1
206 | 91 | 324.4 | 74.6 | 35.8 | 67.9 | 84.6 | 85.7
207 | 92 | 324 | 75.5 | 36.2 | 68.6 | 85.3 | 86.3
208 | 93 | 323.7 | 76.4 | 36.6 | 69.3 | 85.9 | 86.8
209 | 94 | 323.4 | 77.2 | 37 | 69.9 | 86.5 | 87.4
210 | 95 | 323 | 78.1 | 37.5 | 70.6 | 87.2 | 88
211 | 96 | 322.7 | 78.9 | 37.9 | 71.3 | 87.8 | 88.5
212 | 97 | 322.2 | 79.7 | 38.4 | 71.9 | 88.4 | 89
213 | 98 | 321.6 | 80.5 | 38.8 | 72.6 | 89 | 89.6
214 | 99 | 321.2 | 81.3 | 39.3 | 73.2 | 89.5 | 90.1
215 | 100 | 320.8 | 82.1 | 39.8 | 73.8 | 90.1 | 90.6
216 | 101 | 320.4 | 82.8 | 40.2 | 74.4 | 90.7 | 91.1
217 | 102 | 319.8 | 83.6 | 40.7 | 75 | 91.2 | 91.6
218 | 103 | 319.5 | 84.3 | 41.2 | 75.6 | 91.7 | 92.1
219 | 104 | 319.1 | 85 | 41.6 | 76.2 | 92.2 | 92.6
220 | 105 | 318.8 | 85.7 | 42.1 | 76.8 | 92.8 | 93
221 | 106 | 318.3 | 86.4 | 42.5 | 77.4 | 93.3 | 93.4
222 | 107 | 317.9 | 87.1 | 43 | 78 | 93.8 | 93.9
223 | 108 | 317.3 | 87.8 | 43.5 | 78.5 | 94.3 | 94.3
224 | 109 | 316.8 | 88.5 | 44 | 79.1 | 94.8 | 94.7
225 | 110 | 316.3 | 89.1 | 44.5 | 79.6 | 95.3 | 95.1
226 | 111 | 315.8 | 89.8 | 44.9 | 80.2 | 95.7 | 95.6
227 | 112 | 315.4 | 90.4 | 45.4 | 80.7 | 96.2 | 95.9
228 | 113 | 315 | 91 | 45.9 | 81.2 | 96.7 | 96.3
229 | 114 | 314.4 | 91.7 | 46.4 | 81.7 | 97.1 | 96.7
230 | 115 | 313.9 | 92.3 | 46.9 | 82.1 | 97.6 | 97
231 | 116 | 313.4 | 92.9 | 47.4 | 82.6 | 98 | 97.4
232 | 117 | 312.9 | 93.5 | 47.8 | 83.1 | 98.5 | 97.7
233 | 118 | 312.3 | 94.1 | 48.3 | 83.5 | 98.9 | 98.1
234 | 119 | 311.7 | 94.7 | 48.8 | 84 | 99.3 | 98.4
235 | 120 | 311.2 | 95.3 | 49.2 | 84.5 | 99.8 | 98.8
236 | 121 | 310.8 | 95.9 | 49.8 | 84.9 | 100.2 | 99.1
237 | 122 | 310.2 | 96.4 | 50.3 | 85.3 | 100.6 | 99.5
238 | 123 | 309.7 | 97 | 50.7 | 85.8 | 101 | 99.7
239 | 124 | 309.2 | 97.6 | 51.2 | 86.2 | 101.4 | 100.1
240 | 125 | 308.6 | 98.1 | 51.7 | 86.6 | 101.8 | 100.4
241 | 126 | 308.1 | 98.7 | 52.2 | 87 | 102.1 | 100.7
242 | 127 | 307.5 | 99.2 | 52.7 | 87.4 | 102.5 | 101.1
243 | 128 | 307 | 99.7 | 53.1 | 87.8 | 102.9 | 101.3
244 | 129 | 306.6 | 100.2 | 53.6 | 88.2 | 103.3 | 101.6
245 | 130 | 306.1 | 100.7 | 54.1 | 88.6 | 103.6 | 101.9
246 | 131 | 305.5 | 101.2 | 54.6 | 88.9 | 104 | 102.1
247 | 132 | 305 | 101.7 | 55.1 | 89.3 | 104.3 | 102.4
248 | 133 | 304.6 | 102.1 | 55.6 | 89.7 | 104.6 | 102.6
249 | 134 | 304.1 | 102.6 | 56 | 90 | 105 | 102.9
250 | 135 | 303.7 | 103.1 | 56.5 | 90.4 | 105.3 | 103.2
251 | 136 | 303.2 | 103.5 | 57 | 90.7 | 105.6 | 103.4
252 | 137 | 302.6 | 104 | 57.5 | 91 | 105.9 | 103.7
253 | 138 | 302.1 | 104.4 | 58 | 91.3 | 106.3 | 103.9
254 | 139 | 301.6 | 104.9 | 58.4 | 91.7 | 106.5 | 104.1
255 | 140 | 301.1 | 105.3 | 58.9 | 92 | 106.8 | 104.4
256 | 141 | 300.6 | 105.7 | 59.4 | 92.3 | 107.2 | 104.6
257 | 142 | 300.2 | 106.2 | 59.9 | 92.6 | 107.5 | 104.9
258 | 143 | 299.7 | 106.6 | 60.4 | 92.9 | 107.8 | 105.1
259 | 144 | 299.2 | 107 | 60.8 | 93.2 | 108.1 | 105.3
260 | 145 | 298.8 | 107.4 | 61.3 | 93.6 | 108.4 | 105.4
261 | 146 | 298.2 | 107.8 | 61.7 | 93.9 | 108.7 | 105.6
262 | 147 | 297.6 | 108.3 | 62.2 | 94.2 | 109 | 105.8
263 | 148 | 297.1 | 108.7 | 62.7 | 94.5 | 109.3 | 106
264 | 149 | 296.7 | 109.1 | 63.1 | 94.8 | 109.5 | 106.1
265 | 150 | 296.2 | 109.6 | 63.3 | 95.2 | 109.9 | 106.4
266 | 151 | 295.7 | 110 | 63.7 | 95.6 | 110.1 | 106.6
267 | 152 | 295.2 | 110.3 | 64.2 | 95.8 | 110.4 | 106.7
268 | 153 | 294.7 | 110.7 | 64.7 | 96.1 | 110.7 | 106.9
269 | 154 | 294.2 | 111 | 65.1 | 96.4 | 110.9 | 107.1
270 | 155 | 293.7 | 111.4 | 65.6 | 96.8 | 111.2 | 107.2
271 | 156 | 293.2 | 111.8 | 66 | 97.1 | 111.4 | 107.4
272 | 157 | 292.6 | 112.1 | 66.4 | 97.4 | 111.6 | 107.5
273 | 158 | 292.1 | 112.5 | 66.8 | 97.7 | 111.9 | 107.7
274 | 159 | 291.8 | 112.9 | 67.2 | 98 | 112.1 | 107.8
275 | 160 | 291.4 | 113.2 | 67.6 | 98.3 | 112.4 | 108
276 | 161 | 291 | 113.6 | 68.1 | 98.6 | 112.6 | 108.2
277 | 162 | 290.6 | 113.9 | 68.6 | 98.8 | 112.8 | 108.3
278 | 163 | 290.3 | 114.2 | 69 | 99.1 | 113 | 108.5
279 | 164 | 290 | 114.5 | 69.5 | 99.4 | 113.2 | 108.7
280 | 165 | 289.7 | 114.9 | 69.9 | 99.7 | 113.5 | 108.8
281 | 166 | 289.5 | 115.2 | 70.3 | 99.9 | 113.7 | 109
282 | 167 | 289.3 | 115.5 | 70.7 | 100.2 | 113.9 | 109.1
283 | 168 | 289.2 | 115.8 | 71.2 | 100.4 | 114.2 | 109.2
284 | 169 | 289.2 | 116.2 | 71.6 | 100.7 | 114.4 | 109.4
285 | 170 | 289.2 | 116.5 | 72 | 101 | 114.7 | 109.6
286 | 171 | 289.2 | 116.8 | 72.4 | 101.2 | 114.9 | 109.7
287 | 172 | 289.2 | 117.1 | 72.7 | 101.5 | 115.1 | 109.9
288 | 173 | 289.3 | 117.4 | 73.1 | 101.8 | 115.4 | 110.1
289 | 174 | 289.5 | 117.7 | 73.5 | 102.1 | 115.6 | 110.2
290 | 175 | 289.6 | 118 | 73.9 | 102.3 | 115.9 | 110.5
291 | 176 | 289.9 | 118.3 | 74.4 | 102.6 | 116.1 | 110.7
292 | 177 | 290.3 | 118.5 | 74.8 | 102.9 | 116.3 | 110.9
293 | 178 | 290.6 | 118.8 | 75.2 | 103.1 | 116.6 | 111.1
294 | 179 | 291 | 119.1 | 75.7 | 103.4 | 116.9 | 111.3
295 | 180 | 291.4 | 119.3 | 76.1 | 103.6 | 117.1 | 111.5
296 | 181 | 291.8 | 119.6 | 76.5 | 103.9 | 117.4 | 111.7
297 | 182 | 292.3 | 119.9 | 77 | 104.1 | 117.7 | 111.9
298 | 183 | 292.8 | 120.1 | 77.4 | 104.3 | 118 | 112.2
299 | 184 | 293.3 | 120.4 | 77.8 | 104.6 | 118.3 | 112.4
300 | 185 | 293.7 | 120.7 | 78.2 | 104.9 | 118.6 | 112.6
301 | 186 | 294.1 | 120.9 | 78.7 | 105.1 | 118.8 | 112.8
302 | 187 | 294.5 | 121.1 | 79.1 | 105.4 | 119 | 113
303 | 188 | 294.9 | 121.4 | 79.5 | 105.6 | 119.3 | 113.3
304 | 189 | 295.4 | 121.6 | 80 | 105.9 | 119.5 | 113.5
305 | 190 | 295.9 | 121.9 | 80.4 | 106.1 | 119.7 | 113.7
306 | 191 | 296.2 | 122.2 | 80.9 | 106.4 | 120 | 114
307 | 192 | 296.5 | 122.5 | 81.2 | 106.6 | 120.3 | 114.2
308 | 193 | 296.9 | 122.7 | 81.6 | 106.9 | 120.6 | 114.4
309 | 194 | 297.2 | 123 | 82.1 | 107.1 | 120.9 | 114.7
310 | 195 | 297.6 | 123.3 | 82.4 | 107.4 | 121.2 | 114.9
311 | 196 | 297.9 | 123.5 | 82.9 | 107.6 | 121.5 | 115.2
312 | 197 | 298.2 | 123.8 | 83.3 | 107.9 | 121.8 | 115.5
313 | 198 | 298.4 | 124.2 | 83.6 | 108.2 | 122.1 | 115.7
314 | 199 | 298.7 | 124.5 | 84 | 108.5 | 122.4 | 115.9
315 | 200 | 299 | 124.7 | 84.4 | 108.8 | 122.7 | 116.2
316 | 201 | 299.3 | 125 | 84.8 | 109.1 | 123 | 116.5
317 | 202 | 299.5 | 125.3 | 85.1 | 109.3 | 123.3 | 116.8
318 | 203 | 299.7 | 125.6 | 85.5 | 109.6 | 123.6 | 117
319 | 204 | 299.8 | 125.8 | 85.9 | 109.9 | 123.9 | 117.3
320 | 205 | 299.9 | 126.1 | 86.3 | 110.2 | 124.2 | 117.4
321 | 206 | 300.1 | 126.4 | 86.7 | 110.5 | 124.4 | 117.7
322 | 207 | 300 | 126.7 | 87.1 | 110.8 | 124.7 | 117.9
323 | 208 | 300.1 | 127 | 87.5 | 111 | 124.9 | 118.1
324 | 209 | 300.1 | 127.3 | 87.8 | 111.3 | 125.2 | 118.4
325 | 210 | 300.1 | 127.6 | 88.2 | 111.6 | 125.5 | 118.6
326 | 211 | 300.1 | 127.9 | 88.6 | 111.8 | 125.8 | 118.8
327 | 212 | 300 | 128.2 | 88.9 | 112.1 | 126.1 | 119.1
328 | 213 | 300 | 128.5 | 89.3 | 112.4 | 126.4 | 119.4
329 | 214 | 300.1 | 128.8 | 89.6 | 112.7 | 126.7 | 119.6
330 | 215 | 300.1 | 129.1 | 90 | 113 | 127 | 119.8
331 | 216 | 300.1 | 129.4 | 90.4 | 113.3 | 127.3 | 120
332 | 217 | 300.2 | 129.7 | 90.7 | 113.6 | 127.5 | 120.3
333 | 218 | 300.2 | 130 | 91.1 | 113.9 | 127.8 | 120.6
334 | 219 | 300.1 | 130.3 | 91.4 | 114.2 | 128.1 | 120.8
335 | 220 | 299.9 | 130.6 | 91.8 | 114.5 | 128.4 | 121
336 | 221 | 299.9 | 131 | 92.1 | 114.8 | 128.7 | 121.1
337 | 222 | 299.8 | 131.2 | 92.5 | 115 | 128.9 | 121.3
338 | 223 | 299.8 | 131.5 | 92.9 | 115.3 | 129.2 | 121.5
339 | 224 | 299.8 | 131.9 | 93.2 | 115.6 | 129.5 | 121.8
340 | 225 | 299.8 | 132.1 | 93.5 | 115.9 | 129.8 | 121.9
341 | 226 | 299.8 | 132.4 | 93.9 | 116.2 | 130 | 122.1
342 | 227 | 299.7 | 132.7 | 94.3 | 116.5 | 130.1 | 122.3
343 | 228 | 299.6 | 133 | 94.6 | 116.8 | 130.4 | 122.6
344 | 229 | 299.6 | 133.3 | 95 | 117.1 | 130.6 | 122.8
345 | 230 | 299.5 | 133.6 | 95.3 | 117.4 | 130.9 | 123
346 | 231 | 299.5 | 133.9 | 95.7 | 117.6 | 131.1 | 123.3
347 | 232 | 299.5 | 134.2 | 96 | 117.9 | 131.3 | 123.4
348 | 233 | 299.3 | 134.5 | 96.4 | 118.2 | 131.6 | 123.6
349 | 234 | 299.2 | 134.8 | 96.7 | 118.4 | 131.8 | 123.8
350 | 235 | 299.2 | 135.1 | 97.1 | 118.7 | 132.1 | 123.9
351 | 236 | 299 | 135.4 | 97.4 | 119 | 132.4 | 124.1
352 | 237 | 299 | 135.7 | 97.8 | 119.2 | 132.6 | 124.3
353 | 238 | 299 | 136 | 98.1 | 119.5 | 132.9 | 124.6
354 | 239 | 298.9 | 136.2 | 98.4 | 119.7 | 133.1 | 124.8
355 | 240 | 298.8 | 136.5 | 98.8 | 120 | 133.3 | 125
356 | 241 | 298.7 | 136.8 | 99.1 | 120.3 | 133.5 | 125.1
357 | 242 | 298.6 | 137.1 | 99.5 | 120.5 | 133.7 | 125.3
358 | 243 | 298.4 | 137.4 | 99.8 | 120.8 | 134 | 125.5
359 | 244 | 298.4 | 137.7 | 100.1 | 121 | 134.2 | 125.8
360 | 245 | 298.3 | 137.9 | 100.5 | 121.3 | 134.5 | 125.9
361 | 246 | 298.3 | 138.2 | 100.8 | 121.5 | 134.7 | 126.1
362 | 247 | 298.1 | 138.5 | 101.2 | 121.7 | 135 | 126.3
363 | 248 | 298 | 138.8 | 101.5 | 122 | 135.2 | 126.5
364 | 249 | 297.9 | 139 | 101.9 | 122.2 | 135.4 | 126.6
365 | 250 | 297.9 | 139.3 | 102.2 | 122.5 | 135.7 | 126.8
366 | 251 | 297.9 | 139.6 | 102.5 | 122.7 | 135.9 | 126.9
367 | 252 | 297.8 | 139.9 | 102.8 | 122.9 | 136.1 | 127.1
368 | 253 | 297.7 | 140.2 | 103.2 | 123.2 | 136.3 | 127.3
369 | 254 | 297.8 | 140.4 | 103.5 | 123.4 | 136.4 | 127.5
370 | 255 | 298 | 140.7 | 103.8 | 123.6 | 136.7 | 127.7
371 | 256 | 298.1 | 141 | 104.2 | 123.9 | 137 | 128
372 | 257 | 298.2 | 141.2 | 104.5 | 124.1 | 137.2 | 128.2
373 | 258 | 298.2 | 141.5 | 104.8 | 124.4 | 137.5 | 128.4
374 | 259 | 298.1 | 141.8 | 105.1 | 124.6 | 137.7 | 128.6
375 | 260 | 298.1 | 142 | 105.4 | 124.9 | 137.9 | 128.8
376 | 261 | 298 | 142.3 | 105.8 | 125.1 | 138.1 | 128.9
377 | 262 | 298 | 142.6 | 106.1 | 125.4 | 138.4 | 129.1
378 | 263 | 297.9 | 142.8 | 106.4 | 125.6 | 138.6 | 129.2
379 | 264 | 298 | 143.1 | 106.7 | 125.8 | 138.8 | 129.4
380 | 265 | 298.2 | 143.3 | 107.1 | 126.1 | 139.1 | 129.5
381 | 266 | 298.3 | 143.5 | 107.4 | 126.3 | 139.3 | 129.6
382 | 267 | 298.5 | 143.8 | 107.7 | 126.5 | 139.6 | 129.8
383 | 268 | 298.6 | 144 | 108 | 126.8 | 139.8 | 130
384 | 269 | 298.6 | 144.2 | 108.3 | 127 | 140.1 | 130.2
385 | 270 | 298.7 | 144.4 | 108.7 | 127.2 | 140.3 | 130.4
386 | 271 | 298.7 | 144.7 | 109 | 127.5 | 140.5 | 130.6
387 | 272 | 298.7 | 144.9 | 109.3 | 127.7 | 140.8 | 130.8
388 | 273 | 298.7 | 145.2 | 109.6 | 128 | 141 | 131.1
389 | 274 | 298.8 | 145.4 | 109.9 | 128.2 | 141.1 | 131.2
390 | 275 | 298.8 | 145.6 | 110.2 | 128.4 | 141.4 | 131.4
391 | 276 | 298.7 | 145.8 | 110.5 | 128.6 | 141.6 | 131.6
392 | 277 | 298.8 | 146.1 | 110.8 | 128.8 | 141.8 | 131.8
393 | 278 | 298.8 | 146.3 | 111.2 | 129 | 142.1 | 132
394 | 279 | 298.9 | 146.5 | 111.4 | 129.3 | 142.3 | 132.2
395 | 280 | 299 | 146.8 | 111.7 | 129.5 | 142.5 | 132.3
396 | 281 | 299 | 147 | 112 | 129.7 | 142.8 | 132.5
397 | 282 | 299 | 147.2 | 112.4 | 129.9 | 143 | 132.8
398 | 283 | 299.1 | 147.5 | 112.7 | 130.1 | 143.2 | 132.9
399 | 284 | 299.1 | 147.7 | 113 | 130.4 | 143.4 | 133.1
400 | 285 | 299.1 | 147.9 | 113.3 | 130.6 | 143.6 | 133.3
401 | 286 | 299.1 | 148.1 | 113.5 | 130.8 | 143.9 | 133.5
402 | 287 | 299.2 | 148.3 | 113.8 | 131 | 144.1 | 133.7
403 | 288 | 299.2 | 148.6 | 114.1 | 131.3 | 144.3 | 133.9
404 | 289 | 299.2 | 148.8 | 114.4 | 131.5 | 144.4 | 134
405 | 290 | 299 | 149 | 114.7 | 131.7 | 144.7 | 134
406 | 291 | 299 | 149.2 | 115 | 131.9 | 144.9 | 134.2
407 | 292 | 298.9 | 149.4 | 115.3 | 132.1 | 145.1 | 134.4
408 | 293 | 298.9 | 149.6 | 115.6 | 132.4 | 145.3 | 134.6
409 | 294 | 298.9 | 149.8 | 115.9 | 132.6 | 145.5 | 134.8
410 | 295 | 298.8 | 150.1 | 116.2 | 132.8 | 145.7 | 134.9
411 | 296 | 298.7 | 150.3 | 116.5 | 133 | 145.9 | 135.1
412 | 297 | 298.5 | 150.5 | 116.8 | 133.2 | 146.1 | 135.3
413 | 298 | 298.5 | 150.7 | 117.1 | 133.4 | 146.3 | 135.4
414 | 299 | 298.4 | 150.9 | 117.4 | 133.7 | 146.5 | 135.5
415 | 300 | 298.4 | 151.1 | 117.7 | 133.9 | 146.7 | 135.6
416 | 301 | 298.4 | 151.3 | 117.9 | 134.1 | 146.9 | 135.7
417 | 302 | 298.3 | 151.5 | 118.2 | 134.3 | 147.1 | 135.8
418 | 303 | 298.2 | 151.8 | 118.5 | 134.5 | 147.4 | 136
419 | 304 | 298.1 | 152 | 118.8 | 134.7 | 147.6 | 136.2
420 | 305 | 298.2 | 152.2 | 119.1 | 134.9 | 147.7 | 136.5
421 | 306 | 298.3 | 152.4 | 119.4 | 135.1 | 148 | 136.6
422 | 307 | 298.3 | 152.6 | 119.7 | 135.3 | 148.1 | 136.8
423 | 308 | 298.3 | 152.8 | 119.9 | 135.5 | 148.3 | 137
424 | 309 | 298.4 | 153.1 | 120.2 | 135.7 | 148.5 | 137.1
425 | 310 | 298.5 | 153.3 | 120.5 | 135.9 | 148.6 | 137.3
426 | 311 | 298.5 | 153.5 | 120.8 | 136.1 | 148.7 | 137.4
427 | 312 | 298.6 | 153.7 | 121.1 | 136.3 | 148.9 | 137.6
428 | 313 | 298.7 | 153.9 | 121.3 | 136.5 | 149.1 | 137.7
429 | 314 | 298.7 | 154.2 | 121.6 | 136.7 | 149.4 | 138
430 | 315 | 298.7 | 154.4 | 121.9 | 136.9 | 149.6 | 138.1
431 | 316 | 298.8 | 154.6 | 122.2 | 137.1 | 149.8 | 138.3
432 | 317 | 298.8 | 154.8 | 122.4 | 137.3 | 150 | 138.5
433 | 318 | 298.8 | 155 | 122.7 | 137.5 | 150.2 | 138.5
434 | 319 | 298.8 | 155.2 | 123 | 137.7 | 150.4 | 138.7
435 | 320 | 298.7 | 155.4 | 123.3 | 137.9 | 150.6 | 138.8
436 | 321 | 298.8 | 155.6 | 123.5 | 138.1 | 150.8 | 139
437 | 322 | 298.8 | 155.8 | 123.8 | 138.3 | 151 | 139.2
438 | 323 | 298.9 | 156 | 124.1 | 138.4 | 151.2 | 139.3
439 | 324 | 298.9 | 156.2 | 124.3 | 138.6 | 151.4 | 139.5
440 | 325 | 299 | 156.4 | 124.6 | 138.8 | 151.5 | 139.7
441 | 326 | 299 | 156.6 | 124.8 | 139 | 151.7 | 139.8
442 | 327 | 299.1 | 156.8 | 125.1 | 139.2 | 152 | 140.1
443 | 328 | 299.1 | 157 | 125.4 | 139.4 | 152.2 | 140.2
444 | 329 | 299 | 157.2 | 125.6 | 139.6 | 152.3 | 140.4
445 | 330 | 298.9 | 157.4 | 125.9 | 139.8 | 152.5 | 140.5
446 | 331 | 298.9 | 157.6 | 126.2 | 140 | 152.7 | 140.7
447 | 332 | 298.9 | 157.8 | 126.4 | 140.2 | 152.9 | 140.9
448 | 333 | 298.8 | 158 | 126.7 | 140.4 | 153.1 | 141
449 | 334 | 298.9 | 158.1 | 126.9 | 140.6 | 153.2 | 141.2
450 | 335 | 299 | 158.3 | 127.2 | 140.8 | 153.4 | 141.3
451 | 336 | 299 | 158.5 | 127.5 | 141 | 153.6 | 141.4
452 | 337 | 298.9 | 158.7 | 127.7 | 141.2 | 153.7 | 141.6
453 | 338 | 298.9 | 158.8 | 128 | 141.4 | 153.9 | 141.8
454 | 339 | 298.9 | 159 | 128.2 | 141.6 | 154.1 | 142
455 | 340 | 298.9 | 159.2 | 128.5 | 141.8 | 154.3 | 142.2
456 | 341 | 298.9 | 159.4 | 128.7 | 142.1 | 154.6 | 142.3
457 | 342 | 298.8 | 159.6 | 129 | 142.3 | 154.7 | 142.6
458 | 343 | 298.8 | 159.7 | 129.2 | 142.4 | 154.9 | 142.8
459 | 344 | 298.6 | 159.9 | 129.5 | 142.6 | 155.1 | 142.9
460 | 345 | 298.5 | 160.1 | 129.8 | 142.8 | 155.3 | 143
461 | 346 | 298.6 | 160.2 | 130 | 143 | 155.5 | 143.2
462 | 347 | 298.6 | 160.4 | 130.3 | 143.2 | 155.7 | 143.2
463 | 348 | 298.7 | 160.5 | 130.5 | 143.4 | 155.8 | 143.4
464 | 349 | 298.7 | 160.7 | 130.8 | 143.6 | 156 | 143.4
465 | 350 | 298.8 | 160.9 | 131 | 143.8 | 156.1 | 143.5
466 | 351 | 298.8 | 161 | 131.3 | 144 | 156.2 | 143.7
467 | 352 | 298.7 | 161.2 | 131.5 | 144.2 | 156.4 | 143.8
468 | 353 | 298.6 | 161.4 | 131.8 | 144.4 | 156.6 | 143.9
469 | 354 | 298.6 | 161.6 | 132 | 144.5 | 156.7 | 144.1
470 | 355 | 298.6 | 161.8 | 132.2 | 144.7 | 156.9 | 144.3
471 | 356 | 298.5 | 162 | 132.5 | 144.9 | 157.1 | 144.4
472 | 357 | 298.5 | 162.2 | 132.7 | 145.1 | 157.3 | 144.5
473 | 358 | 298.5 | 162.4 | 133 | 145.3 | 157.5 | 144.6
474 | 359 | 298.5 | 162.5 | 133.2 | 145.4 | 157.6 | 144.7
475 | 360 | 298.5 | 162.8 | 133.5 | 145.6 | 157.8 | 144.8
476 | 361 | 298.5 | 163 | 133.7 | 145.8 | 158 | 144.9
477 | 362 | 298.7 | 163.2 | 133.9 | 146 | 158.1 | 145.1
478 | 363 | 298.7 | 163.4 | 134.1 | 146.2 | 158.3 | 145.2
479 | 364 | 298.6 | 163.6 | 134.4 | 146.3 | 158.4 | 145.3
480 | 365 | 298.7 | 163.8 | 134.6 | 146.5 | 158.6 | 145.4
481 | 366 | 298.7 | 164 | 134.8 | 146.7 | 158.8 | 145.6
482 | 367 | 298.8 | 164.2 | 135.1 | 146.8 | 159 | 145.7
483 | 368 | 298.8 | 164.4 | 135.3 | 147 | 159.1 | 145.8
484 | 369 | 298.7 | 164.6 | 135.6 | 147.2 | 159.3 | 145.9
485 | 370 | 298.6 | 164.8 | 135.8 | 147.3 | 159.4 | 146.2
486 | 371 | 298.7 | 165 | 136 | 147.5 | 159.6 | 146.4
487 | 372 | 298.6 | 165.1 | 136.3 | 147.7 | 159.7 | 146.5
488 | 373 | 298.5 | 165.3 | 136.5 | 147.8 | 159.9 | 146.6
489 | 374 | 298.6 | 165.6 | 136.7 | 148 | 160.1 | 146.8
490 | 375 | 298.7 | 165.8 | 136.8 | 148.2 | 160.2 | 147
491 | 376 | 298.7 | 165.9 | 137.1 | 148.4 | 160.3 | 147.1
492 | 377 | 298.7 | 166.1 | 137.3 | 148.5 | 160.5 | 147.2
493 | 378 | 298.8 | 166.3 | 137.5 | 148.7 | 160.7 | 147.2
494 | 379 | 298.9 | 166.4 | 137.8 | 148.8 | 160.9 | 147.4
495 | 380 | 299 | 166.6 | 138 | 149 | 161 | 147.5
496 | 381 | 299 | 166.8 | 138.2 | 149.1 | 161.2 | 147.6
497 | 382 | 299 | 167 | 138.4 | 149.3 | 161.4 | 147.8
498 | 383 | 299.2 | 167.1 | 138.7 | 149.5 | 161.6 | 148
499 | 384 | 299.2 | 167.3 | 138.9 | 149.6 | 161.8 | 148.2
500 | 385 | 299 | 167.5 | 139.1 | 149.8 | 162 | 148.4
501 | 386 | 299 | 167.7 | 139.4 | 149.9 | 162.2 | 148.5
502 | 387 | 298.9 | 167.9 | 139.6 | 150.1 | 162.3 | 148.7
503 | 388 | 298.8 | 168 | 139.8 | 150.3 | 162.4 | 148.8
504 | 389 | 298.7 | 168.2 | 140 | 150.4 | 162.6 | 149
505 | 390 | 298.8 | 168.4 | 140.2 | 150.6 | 162.8 | 149.2
506 | 391 | 298.8 | 168.6 | 140.4 | 150.8 | 162.9 | 149.2
507 | 392 | 298.9 | 168.7 | 140.7 | 150.9 | 163.1 | 149.3
508 | 393 | 298.9 | 168.9 | 140.9 | 151.1 | 163.3 | 149.4
509 | 394 | 298.8 | 169.1 | 141.1 | 151.2 | 163.4 | 149.5
510 | 395 | 298.9 | 169.2 | 141.3 | 151.4 | 163.5 | 149.6
511 | 396 | 299 | 169.4 | 141.6 | 151.6 | 163.7 | 149.8
512 | 397 | 299 | 169.6 | 141.8 | 151.8 | 163.9 | 150
513 | 398 | 299 | 169.7 | 142 | 151.9 | 164 | 150.1
514 | 399 | 299.1 | 169.9 | 142.2 | 152.1 | 164.1 | 150.2
515 | 400 | 299.2 | 170 | 142.4 | 152.2 | 164.3 | 150.4
516 | 401 | 299.2 | 170.2 | 142.6 | 152.4 | 164.5 | 150.5
517 | 402 | 299.4 | 170.4 | 142.8 | 152.6 | 164.7 | 150.6
518 | 403 | 299.4 | 170.6 | 143 | 152.8 | 164.8 | 150.7
519 | 404 | 299.5 | 170.8 | 143.3 | 152.9 | 165 | 150.9
520 | 405 | 299.5 | 170.9 | 143.5 | 153.1 | 165.1 | 151
521 | 406 | 299.6 | 171.1 | 143.7 | 153.3 | 165.3 | 151.1
522 | 407 | 299.6 | 171.2 | 143.9 | 153.4 | 165.5 | 151.2
523 | 408 | 299.5 | 171.4 | 144.1 | 153.6 | 165.6 | 151.2
524 | 409 | 299.7 | 171.6 | 144.3 | 153.8 | 165.8 | 151.3
525 | 410 | 299.7 | 171.7 | 144.5 | 153.9 | 166 | 151.4
526 | 411 | 299.8 | 171.9 | 144.7 | 154.1 | 166.1 | 151.5
527 | 412 | 299.7 | 172.1 | 144.9 | 154.3 | 166.3 | 151.6
528 | 413 | 299.7 | 172.2 | 145.1 | 154.4 | 166.4 | 151.8
529 | 414 | 299.8 | 172.4 | 145.4 | 154.6 | 166.6 | 151.9
530 | 415 | 299.9 | 172.5 | 145.5 | 154.8 | 166.7 | 152.1
531 | 416 | 300 | 172.7 | 145.8 | 155 | 166.9 | 152.1
532 | 417 | 300.1 | 172.8 | 146 | 155.1 | 167 | 152.2
533 | 418 | 300 | 173 | 146.2 | 155.3 | 167.1 | 152.4
534 | 419 | 300 | 173.2 | 146.4 | 155.5 | 167.2 | 152.6
535 | 420 | 300 | 173.3 | 146.6 | 155.6 | 167.4 | 152.8
536 | 421 | 299.9 | 173.5 | 146.8 | 155.8 | 167.5 | 153
537 | 422 | 300 | 173.7 | 147 | 156 | 167.6 | 153.1
538 | 423 | 300 | 173.8 | 147.2 | 156.1 | 167.8 | 153.2
539 | 424 | 299.8 | 174 | 147.4 | 156.3 | 168 | 153.3
540 | 425 | 299.8 | 174.1 | 147.6 | 156.5 | 168.1 | 153.5
541 | 426 | 299.8 | 174.3 | 147.8 | 156.6 | 168.2 | 153.6
542 | 427 | 299.8 | 174.5 | 148 | 156.8 | 168.4 | 153.8
543 | 428 | 299.8 | 174.6 | 148.2 | 156.9 | 168.5 | 154
544 | 429 | 299.8 | 174.8 | 148.4 | 157.1 | 168.6 | 154.2
545 | 430 | 299.8 | 175 | 148.6 | 157.3 | 168.8 | 154.3
546 | 431 | 299.8 | 175.2 | 148.8 | 157.4 | 168.9 | 154.3
547 | 432 | 299.9 | 175.3 | 149 | 157.6 | 169.1 | 154.6
548 | 433 | 300 | 175.5 | 149.2 | 157.8 | 169.3 | 154.7
549 | 434 | 300.1 | 175.7 | 149.4 | 157.9 | 169.4 | 154.9
550 | 435 | 300.1 | 175.8 | 149.6 | 158.1 | 169.5 | 155.1
551 | 436 | 300.1 | 176 | 149.7 | 158.2 | 169.7 | 155.3
552 | 437 | 300.1 | 176.2 | 149.9 | 158.4 | 169.8 | 155.4
553 | 438 | 300.1 | 176.4 | 150.1 | 158.5 | 170 | 155.4
554 | 439 | 300.2 | 176.6 | 150.3 | 158.7 | 170.1 | 155.5
555 | 440 | 300.3 | 176.8 | 150.5 | 158.8 | 170.2 | 155.6
556 | 441 | 300.2 | 176.9 | 150.7 | 159 | 170.3 | 155.6
557 | 442 | 300.1 | 177.1 | 150.9 | 159.1 | 170.5 | 155.6
558 | 443 | 300 | 177.3 | 151.1 | 159.2 | 170.6 | 155.8
559 | 444 | 300 | 177.5 | 151.3 | 159.4 | 170.7 | 155.9
560 | 445 | 299.9 | 177.7 | 151.4 | 159.6 | 170.8 | 155.9
561 | 446 | 299.8 | 177.8 | 151.7 | 159.7 | 170.9 | 155.9
562 | 447 | 299.5 | 178 | 151.8 | 159.9 | 171 | 156
563 | 448 | 299.4 | 178.2 | 152.1 | 160.1 | 171 | 156.2
564 | 449 | 299.4 | 178.4 | 152.2 | 160.2 | 171.2 | 156.3
565 | 450 | 299.2 | 178.5 | 152.4 | 160.4 | 171.3 | 156.5
566 | 451 | 299.1 | 178.7 | 152.6 | 160.6 | 171.5 | 156.5
567 | 452 | 299 | 178.9 | 152.8 | 160.7 | 171.6 | 156.5
568 | 453 | 299 | 179.1 | 153 | 160.9 | 171.7 | 156.3
569 | 454 | 298.9 | 179.3 | 153.2 | 161.1 | 171.8 | 156.4
570 | 455 | 298.9 | 179.4 | 153.3 | 161.2 | 171.9 | 156.5
571 | 456 | 298.9 | 179.6 | 153.5 | 161.4 | 172 | 156.7
572 | 457 | 298.9 | 179.8 | 153.7 | 161.6 | 172 | 156.8
573 | 458 | 298.9 | 179.9 | 153.9 | 161.7 | 172 | 157
574 | 459 | 298.9 | 180.1 | 154.1 | 161.9 | 172.2 | 157.1
575 | 460 | 298.9 | 180.3 | 154.3 | 162 | 172.3 | 157.3
576 | 461 | 298.8 | 180.5 | 154.5 | 162.2 | 172.4 | 157.4
577 | 462 | 298.8 | 180.7 | 154.7 | 162.4 | 172.5 | 157.4
578 | 463 | 298.7 | 180.8 | 154.9 | 162.5 | 172.6 | 157.5
579 | 464 | 298.6 | 181 | 155 | 162.7 | 172.7 | 157.5
580 | 465 | 298.6 | 181.2 | 155.2 | 162.8 | 172.8 | 157.7
581 | 466 | 298.5 | 181.4 | 155.4 | 163 | 173 | 157.8
582 | 467 | 298.4 | 181.5 | 155.6 | 163.2 | 173.1 | 157.9
583 | 468 | 298.6 | 181.7 | 155.8 | 163.3 | 173.2 | 158
584 | 469 | 298.7 | 181.9 | 156 | 163.5 | 173.3 | 158
585 | 470 | 298.7 | 182 | 156.2 | 163.7 | 173.4 | 158.1
586 | 471 | 298.8 | 182.2 | 156.3 | 163.8 | 173.5 | 158.3
587 | 472 | 298.8 | 182.4 | 156.5 | 164 | 173.6 | 158.4
588 | 473 | 298.7 | 182.6 | 156.7 | 164.2 | 173.7 | 158.5
589 | 474 | 298.7 | 182.7 | 156.9 | 164.3 | 173.9 | 158.7
590 | 475 | 298.6 | 182.9 | 157.1 | 164.5 | 174 | 158.8
591 | 476 | 298.7 | 183.1 | 157.2 | 164.7 | 174.2 | 159
592 | 477 | 298.8 | 183.3 | 157.4 | 164.9 | 174.4 | 159.1
593 | 478 | 298.9 | 183.5 | 157.6 | 165 | 174.5 | 159.2
594 | 479 | 299 | 183.6 | 157.7 | 165.2 | 174.7 | 159.3
595 | 480 | 299.1 | 183.8 | 157.9 | 165.4 | 174.8 | 159.5
596 | 481 | 299.2 | 183.9 | 158.1 | 165.6 | 174.9 | 159.6
597 | 482 | 299.3 | 184.1 | 158.3 | 165.7 | 175 | 159.7
598 | 483 | 299.4 | 184.3 | 158.4 | 165.9 | 175.2 | 159.9
599 | 484 | 299.6 | 184.4 | 158.6 | 166.1 | 175.3 | 159.9
600 | 485 | 299.8 | 184.6 | 158.8 | 166.2 | 175.4 | 160
601 | 486 | 299.9 | 184.7 | 158.9 | 166.4 | 175.5 | 160
602 | 487 | 299.9 | 184.9 | 159.1 | 166.6 | 175.7 | 160.2
603 | 488 | 299.9 | 185 | 159.3 | 166.8 | 175.8 | 160.1
604 | 489 | 300 | 185.2 | 159.4 | 166.9 | 176 | 160.1
605 | 490 | 300.1 | 185.3 | 159.6 | 167.1 | 176.1 | 160
606 | 491 | 300.1 | 185.4 | 159.7 | 167.3 | 176.3 | 160.1
607 | 492 | 300.1 | 185.5 | 160 | 167.4 | 176.4 | 160.2
608 | 493 | 300 | 185.7 | 160.1 | 167.6 | 176.5 | 160.4
609 | 494 | 299.9 | 185.8 | 160.3 | 167.8 | 176.6 | 160.4
610 | 495 | 299.8 | 185.9 | 160.5 | 167.9 | 176.7 | 160.4
611 | 496 | 299.8 | 186 | 160.6 | 168.1 | 176.8 | 160.5
612 | 497 | 299.8 | 186.1 | 160.8 | 168.3 | 177 | 160.6
613 | 498 | 299.7 | 186.2 | 161 | 168.5 | 177.1 | 160.8
614 | 499 | 299.7 | 186.3 | 161.2 | 168.6 | 177.2 | 160.8
615 | 500 | 299.6 | 186.4 | 161.3 | 168.8 | 177.3 | 160.8
616 | 501 | 299.5 | 186.5 | 161.5 | 169 | 177.4 | 160.8
617 | 502 | 299.6 | 186.6 | 161.7 | 169.1 | 177.5 | 160.9
618 | 503 | 299.6 | 186.7 | 161.8 | 169.3 | 177.6 | 160.9
619 | 504 | 299.6 | 186.9 | 162 | 169.5 | 177.7 | 161.1
620 | 505 | 299.7 | 187 | 162.2 | 169.6 | 177.8 | 161.2
621 | 506 | 299.6 | 187.1 | 162.3 | 169.8 | 177.9 | 161.4
622 | 507 | 299.6 | 187.2 | 162.5 | 170 | 178.1 | 161.5
623 | 508 | 299.7 | 187.3 | 162.7 | 170.2 | 178.2 | 161.6
624 | 509 | 299.5 | 187.4 | 162.9 | 170.3 | 178.3 | 161.6
625 | 510 | 299.4 | 187.6 | 163 | 170.5 | 178.4 | 161.6
626 | 511 | 299.4 | 187.7 | 163.2 | 170.7 | 178.5 | 161.8
627 | 512 | 299.3 | 187.8 | 163.3 | 170.9 | 178.5 | 161.8
628 | 513 | 299.1 | 188 | 163.5 | 171 | 178.6 | 161.9
629 | 514 | 299 | 188.1 | 163.6 | 171.2 | 178.8 | 162
630 | 515 | 299 | 188.2 | 163.8 | 171.4 | 178.9 | 162
631 | 516 | 299 | 188.3 | 164 | 171.5 | 179 | 162.1
632 | 517 | 299 | 188.4 | 164.1 | 171.7 | 179.1 | 162.2
633 | 518 | 298.9 | 188.6 | 164.3 | 171.9 | 179.1 | 162.2
634 | 519 | 298.7 | 188.7 | 164.4 | 172 | 179.2 | 162.4
635 | 520 | 298.6 | 188.8 | 164.6 | 172.2 | 179.3 | 162.3
636 | 521 | 298.6 | 189 | 164.7 | 172.4 | 179.3 | 162.5
637 | 522 | 298.7 | 189.2 | 164.8 | 172.6 | 179.4 | 162.7
638 | 523 | 299 | 189.3 | 165 | 172.7 | 179.5 | 162.8
639 | 524 | 299.1 | 189.4 | 165.2 | 172.9 | 179.3 | 163
640 | 525 | 299.2 | 189.6 | 165.4 | 173 | 179.3 | 163.2
641 | 526 | 299.2 | 189.7 | 165.5 | 173.2 | 179.5 | 163.2
642 | 527 | 299.2 | 189.9 | 165.7 | 173.3 | 179.6 | 163.3
643 | 528 | 299 | 190.1 | 165.8 | 173.5 | 179.7 | 163.3
644 | 529 | 298.9 | 190.2 | 166 | 173.6 | 179.8 | 163.5
645 | 530 | 298.9 | 190.4 | 166.1 | 173.8 | 179.9 | 163.6
646 | 531 | 298.8 | 190.5 | 166.3 | 173.9 | 180 | 163.7
647 | 532 | 298.9 | 190.6 | 166.5 | 174.1 | 180.1 | 163.8
648 | 533 | 298.9 | 190.8 | 166.6 | 174.2 | 180.2 | 163.9
649 | 534 | 298.9 | 190.9 | 166.8 | 174.4 | 180.3 | 164.1
650 | 535 | 299 | 191.1 | 166.9 | 174.5 | 180.5 | 164.2
651 | 536 | 299 | 191.2 | 167.1 | 174.7 | 180.6 | 164.3
652 | 537 | 299 | 191.3 | 167.2 | 174.8 | 180.7 | 164.5
653 | 538 | 299 | 191.5 | 167.4 | 174.9 | 180.8 | 164.5
654 | 539 | 298.9 | 191.6 | 167.6 | 175.1 | 180.9 | 164.6
655 | 540 | 298.9 | 191.8 | 167.7 | 175.2 | 181.1 | 164.7
656 | 541 | 298.9 | 192 | 167.9 | 175.3 | 181.1 | 164.9
657 | 542 | 299 | 192.1 | 168 | 175.5 | 181.2 | 165
658 | 543 | 299.1 | 192.3 | 168.1 | 175.6 | 181.3 | 165.1
659 | 544 | 299.1 | 192.4 | 168.3 | 175.7 | 181.4 | 165
660 | 545 | 299.1 | 192.6 | 168.5 | 175.9 | 181.5 | 165.1
661 | 546 | 299.2 | 192.7 | 168.6 | 176 | 181.6 | 165.2
662 | 547 | 299.2 | 192.9 | 168.8 | 176.1 | 181.7 | 165.3
663 | 548 | 299.2 | 193 | 168.9 | 176.2 | 181.8 | 165.4
664 | 549 | 299.3 | 193.2 | 169.1 | 176.3 | 181.9 | 165.5
665 | 550 | 299.2 | 193.3 | 169.2 | 176.4 | 182 | 165.6
666 | 551 | 299.1 | 193.5 | 169.4 | 176.6 | 182.2 | 165.8
667 | 552 | 299.1 | 193.6 | 169.5 | 176.7 | 182.3 | 165.9
668 | 553 | 299.2 | 193.8 | 169.7 | 176.8 | 182.4 | 165.9
669 | 554 | 299.3 | 193.9 | 169.8 | 176.9 | 182.6 | 166
670 | 555 | 299.3 | 194.1 | 170 | 177 | 182.7 | 166.1
671 | 556 | 299.2 | 194.3 | 170.1 | 177.2 | 182.9 | 166.2
672 | 557 | 299.1 | 194.4 | 170.2 | 177.3 | 183 | 166.3
673 | 558 | 299.1 | 194.6 | 170.4 | 177.4 | 183.1 | 166.3
674 | 559 | 299.1 | 194.7 | 170.5 | 177.5 | 183.2 | 166.4
675 | 560 | 299 | 194.9 | 170.7 | 177.7 | 183.3 | 166.4
676 | 561 | 298.9 | 195 | 170.8 | 177.8 | 183.4 | 166.4
677 | 562 | 298.9 | 195.2 | 171 | 177.9 | 183.5 | 166.5
678 | 563 | 298.9 | 195.3 | 171.1 | 178.1 | 183.6 | 166.5
679 | 564 | 298.9 | 195.4 | 171.2 | 178.2 | 183.7 | 166.7
680 | 565 | 298.9 | 195.5 | 171.4 | 178.3 | 183.9 | 166.7
681 | 566 | 298.8 | 195.7 | 171.5 | 178.5 | 183.9 | 166.8
682 | 567 | 298.7 | 195.8 | 171.7 | 178.6 | 184 | 166.8
683 | 568 | 298.8 | 195.9 | 171.8 | 178.7 | 184.1 | 166.9
684 | 569 | 298.8 | 196 | 172 | 178.8 | 184.2 | 167
685 | 570 | 298.8 | 196.2 | 172.1 | 179 | 184.3 | 167
686 | 571 | 298.9 | 196.3 | 172.3 | 179.1 | 184.4 | 166.9
687 | 572 | 298.8 | 196.4 | 172.4 | 179.2 | 184.5 | 166.9
688 | 573 | 298.9 | 196.5 | 172.6 | 179.4 | 184.6 | 166.9
689 | 574 | 299 | 196.7 | 172.7 | 179.5 | 184.7 | 166.9
690 | 575 | 299 | 196.8 | 172.8 | 179.6 | 184.8 | 166.9
691 | 576 | 299 | 196.9 | 173 | 179.7 | 184.9 | 167.1
692 | 577 | 299.1 | 197 | 173.1 | 179.9 | 184.9 | 167.2
693 | 578 | 299.2 | 197.1 | 173.3 | 180 | 185 | 167.3
694 | 579 | 299.2 | 197.2 | 173.4 | 180.1 | 185.1 | 167.3
695 | 580 | 299.1 | 197.4 | 173.6 | 180.2 | 185.2 | 167.4
696 | 581 | 299.2 | 197.5 | 173.7 | 180.3 | 185.3 | 167.3
697 | 582 | 299.2 | 197.6 | 173.8 | 180.5 | 185.5 | 167.4
698 | 583 | 299.2 | 197.7 | 174 | 180.6 | 185.6 | 167.5
699 | 584 | 299.2 | 197.8 | 174.1 | 180.7 | 185.7 | 167.7
700 | 585 | 299.3 | 197.9 | 174.2 | 180.8 | 185.8 | 167.8
701 | 586 | 299.4 | 198.1 | 174.4 | 180.9 | 185.9 | 167.8
702 | 587 | 299.6 | 198.2 | 174.5 | 181.1 | 186 | 167.9
703 | 588 | 299.7 | 198.3 | 174.6 | 181.2 | 186.1 | 167.9
704 | 589 | 299.8 | 198.4 | 174.8 | 181.3 | 186.1 | 167.9
705 | 590 | 299.8 | 198.5 | 174.9 | 181.4 | 186.2 | 168
706 | 591 | 299.9 | 198.6 | 175 | 181.6 | 186.3 | 168.1
707 | 592 | 299.8 | 198.7 | 175.2 | 181.7 | 186.3 | 168.2
708 | 593 | 300 | 198.8 | 175.3 | 181.8 | 186.4 | 168.3
709 | 594 | 300.1 | 198.9 | 175.5 | 181.9 | 186.5 | 168.4
710 | 595 | 300.2 | 199 | 175.6 | 182.1 | 186.6 | 168.5
711 | 596 | 300.2 | 199.1 | 175.8 | 182.2 | 186.7 | 168.6
712 | 597 | 300.2 | 199.3 | 175.9 | 182.3 | 186.8 | 168.5
713 | 598 | 300.3 | 199.4 | 176 | 182.4 | 186.8 | 168.5
714 | 599 | 300.4 | 199.5 | 176.1 | 182.5 | 186.9 | 168.4
715 | 600 | 300.5 | 199.6 | 176.3 | 182.6 | 187 | 168.7
716 | 601 | 300.6 | 199.8 | 176.4 | 182.7 | 187.1 | 168.9
717 | 602 | 300.6 | 199.9 | 176.5 | 182.8 | 187.2 | 169
718 | 603 | 300.5 | 200 | 176.6 | 182.9 | 187.3 | 169.1
719 | 604 | 300.4 | 200.2 | 176.8 | 183 | 187.5 | 169.3
720 | 605 | 300.4 | 200.3 | 176.9 | 183.1 | 187.6 | 169.5
721 | 606 | 300.4 | 200.5 | 177 | 183.2 | 187.7 | 169.6
722 | 607 | 300.2 | 200.6 | 177.2 | 183.3 | 187.7 | 169.6
723 | 608 | 300.2 | 200.7 | 177.3 | 183.4 | 187.9 | 169.5
724 | 609 | 300.2 | 200.9 | 177.4 | 183.5 | 188 | 169.5
725 | 610 | 300.3 | 201 | 177.6 | 183.6 | 188.1 | 169.6
726 | 611 | 300.2 | 201.1 | 177.6 | 183.7 | 188.2 | 169.7
727 | 612 | 300.2 | 201.3 | 177.8 | 183.8 | 188.3 | 169.9
728 | 613 | 300.3 | 201.4 | 177.9 | 183.8 | 188.4 | 170
729 | 614 | 300.3 | 201.5 | 178.1 | 183.9 | 188.5 | 170.1
730 | 615 | 300.3 | 201.6 | 178.2 | 184 | 188.6 | 170.3
731 | 616 | 300.3 | 201.8 | 178.3 | 184.1 | 188.7 | 170.3
732 | 617 | 300.4 | 201.9 | 178.5 | 184.2 | 188.8 | 170.3
733 | 618 | 300.4 | 202 | 178.6 | 184.3 | 188.9 | 170.4
734 | 619 | 300.3 | 202.1 | 178.7 | 184.4 | 189.1 | 170.5
735 | 620 | 300.2 | 202.3 | 178.8 | 184.5 | 189.2 | 170.6
736 | 621 | 300.2 | 202.4 | 179 | 184.6 | 189.3 | 170.8
737 | 622 | 300 | 202.5 | 179.1 | 184.7 | 189.4 | 170.9
738 | 623 | 300 | 202.6 | 179.2 | 184.9 | 189.5 | 171.1
739 | 624 | 300.2 | 202.7 | 179.3 | 185 | 189.5 | 171.1
740 | 625 | 300.2 | 202.8 | 179.5 | 185.1 | 189.6 | 171.2
741 | 626 | 300.2 | 202.9 | 179.6 | 185.2 | 189.7 | 171.3
742 | 627 | 300.2 | 203 | 179.7 | 185.3 | 189.8 | 171.3
743 | 628 | 300.2 | 203.1 | 179.8 | 185.4 | 189.9 | 171.4
744 | 629 | 300 | 203.2 | 179.9 | 185.6 | 189.9 | 171.6
745 | 630 | 300 | 203.3 | 180.1 | 185.7 | 190 | 171.8
746 | 631 | 300 | 203.4 | 180.2 | 185.7 | 190.1 | 171.8
747 | 632 | 300 | 203.5 | 180.3 | 185.8 | 190.1 | 171.9
748 | 633 | 299.9 | 203.6 | 180.4 | 186 | 190.2 | 172
749 | 634 | 299.9 | 203.7 | 180.6 | 186.1 | 190.4 | 172.2
750 | 635 | 300 | 203.9 | 180.7 | 186.2 | 190.5 | 172.3
751 | 636 | 300.1 | 204 | 180.8 | 186.2 | 190.6 | 172.2
752 | 637 | 299.9 | 204.1 | 180.9 | 186.3 | 190.7 | 172.1
753 | 638 | 299.8 | 204.2 | 181.1 | 186.4 | 190.8 | 172.2
754 | 639 | 299.7 | 204.4 | 181.2 | 186.5 | 190.9 | 172.2
755 | 640 | 299.8 | 204.5 | 181.3 | 186.6 | 191 | 172.3
756 | 641 | 299.8 | 204.6 | 181.4 | 186.7 | 191.1 | 172.4
757 | 642 | 299.9 | 204.7 | 181.5 | 186.8 | 191.2 | 172.6
758 | 643 | 299.8 | 204.8 | 181.6 | 186.9 | 191.3 | 172.7
759 | 644 | 299.8 | 205 | 181.7 | 187 | 191.4 | 172.7
760 | 645 | 299.8 | 205.1 | 181.8 | 187.1 | 191.5 | 172.7
761 | 646 | 299.7 | 205.2 | 181.9 | 187.2 | 191.6 | 172.5
762 | 647 | 299.5 | 205.3 | 182.1 | 187.3 | 191.6 | 172.5
763 | 648 | 299.5 | 205.4 | 182.2 | 187.4 | 191.7 | 172.5
764 | 649 | 299.6 | 205.5 | 182.3 | 187.6 | 191.7 | 172.6
765 | 650 | 299.6 | 205.6 | 182.4 | 187.7 | 191.8 | 172.8
766 | 651 | 299.8 | 205.7 | 182.5 | 187.8 | 191.9 | 172.9
767 | 652 | 299.9 | 205.8 | 182.7 | 187.9 | 192 | 172.8
768 | 653 | 300.1 | 205.8 | 182.8 | 188.1 | 192 | 172.8
769 | 654 | 300.2 | 205.9 | 182.9 | 188.2 | 192.1 | 172.7
770 | 655 | 300.2 | 206 | 183 | 188.3 | 192.2 | 172.7
771 | 656 | 300.3 | 206.1 | 183.1 | 188.5 | 192.3 | 172.8
772 | 657 | 300.3 | 206.2 | 183.2 | 188.6 | 192.4 | 172.8
773 | 658 | 300.4 | 206.3 | 183.3 | 188.7 | 192.4 | 172.9
774 | 659 | 300.5 | 206.4 | 183.4 | 188.9 | 192.6 | 173
775 | 660 | 300.5 | 206.5 | 183.6 | 189 | 192.6 | 173
776 | 661 | 300.4 | 206.6 | 183.7 | 189.1 | 192.8 | 173.1
777 | 662 | 300.5 | 206.7 | 183.8 | 189.3 | 192.8 | 173.3
778 | 663 | 300.5 | 206.8 | 183.9 | 189.4 | 193 | 173.2
779 | 664 | 300.5 | 206.9 | 184 | 189.5 | 193 | 173.2
780 | 665 | 300.6 | 207 | 184.1 | 189.6 | 193.1 | 173.1
781 | 666 | 300.7 | 207.1 | 184.2 | 189.8 | 193.2 | 173
782 | 667 | 300.7 | 207.2 | 184.4 | 189.9 | 193.3 | 173.2
783 | 668 | 300.7 | 207.3 | 184.5 | 190 | 193.4 | 173.3
784 | 669 | 300.7 | 207.4 | 184.5 | 190.1 | 193.4 | 173.3
785 | 670 | 300.7 | 207.5 | 184.7 | 190.2 | 193.5 | 173.3
786 | 671 | 300.7 | 207.6 | 184.8 | 190.4 | 193.6 | 173.4
787 | 672 | 300.8 | 207.7 | 184.9 | 190.5 | 193.7 | 173.3
788 | 673 | 300.9 | 207.8 | 185 | 190.6 | 193.8 | 173.4
789 | 674 | 300.9 | 207.9 | 185.1 | 190.8 | 193.9 | 173.4
790 | 675 | 300.7 | 208 | 185.2 | 190.9 | 194 | 173.5
791 | 676 | 300.6 | 208 | 185.3 | 191.1 | 194 | 173.5
792 | 677 | 300.6 | 208.1 | 185.4 | 191.2 | 194.1 | 173.8
793 | 678 | 300.6 | 208.2 | 185.5 | 191.3 | 194.2 | 174
794 | 679 | 300.5 | 208.2 | 185.6 | 191.4 | 194.3 | 174.2
795 | 680 | 300.5 | 208.3 | 185.8 | 191.6 | 194.4 | 174.3
796 | 681 | 300.4 | 208.4 | 185.8 | 191.7 | 194.5 | 174.3
797 | 682 | 300.3 | 208.5 | 186 | 191.8 | 194.5 | 174.4
798 | 683 | 300.3 | 208.6 | 186.1 | 191.9 | 194.6 | 174.5
799 | 684 | 300.3 | 208.6 | 186.2 | 192 | 194.7 | 174.7
800 | 685 | 300.2 | 208.7 | 186.3 | 192.1 | 194.8 | 174.8
801 | 686 | 300.1 | 208.8 | 186.4 | 192.2 | 194.9 | 174.7
802 | 687 | 300.1 | 208.8 | 186.5 | 192.3 | 194.9 | 174.8
803 | 688 | 299.9 | 208.9 | 186.6 | 192.5 | 195 | 174.8
804 | 689 | 299.9 | 208.9 | 186.8 | 192.6 | 195 | 175.1
805 | 690 | 299.8 | 209 | 186.8 | 192.7 | 195 | 175.3
806 | 691 | 299.9 | 209.1 | 187 | 192.8 | 195.1 | 175.4
807 | 692 | 299.9 | 209.1 | 187.1 | 193 | 195.1 | 175.5
808 | 693 | 299.9 | 209.2 | 187.2 | 193.1 | 195.2 | 175.5
809 | 694 | 300 | 209.3 | 187.2 | 193.2 | 195.3 | 175.5
810 | 695 | 300.2 | 209.4 | 187.4 | 193.3 | 195.4 | 175.6
811 | 696 | 300.2 | 209.5 | 187.4 | 193.5 | 195.5 | 175.8
812 | 697 | 300.2 | 209.6 | 187.6 | 193.6 | 195.6 | 175.8
813 | 698 | 300.1 | 209.7 | 187.7 | 193.7 | 195.6 | 175.8
814 | 699 | 300 | 209.8 | 187.8 | 193.8 | 195.7 | 175.9
815 | 700 | 299.9 | 209.9 | 187.9 | 193.9 | 195.8 | 176
816 | 701 | 299.9 | 210 | 188 | 194.1 | 195.9 | 176
817 | 702 | 299.9 | 210 | 188.1 | 194.2 | 196 | 176
818 | 703 | 300 | 210.1 | 188.2 | 194.3 | 196.1 | 176
819 | 704 | 300.1 | 210.2 | 188.3 | 194.4 | 196.2 | 176.1
820 | 705 | 300.1 | 210.2 | 188.4 | 194.5 | 196.2 | 176.2
821 | 706 | 300.2 | 210.3 | 188.5 | 194.6 | 196.3 | 176.1
822 | 707 | 300.2 | 210.4 | 188.6 | 194.7 | 196.3 | 176.2
823 | 708 | 300.3 | 210.5 | 188.7 | 194.8 | 196.4 | 176.2
824 | 709 | 300.4 | 210.6 | 188.7 | 194.9 | 196.5 | 176.2
825 | 710 | 300.3 | 210.7 | 188.8 | 195 | 196.6 | 176.3
826 | 711 | 300.4 | 210.8 | 188.9 | 195.1 | 196.7 | 176.5
827 | 712 | 300.5 | 210.9 | 189 | 195.2 | 196.8 | 176.5
828 | 713 | 300.5 | 211 | 189.1 | 195.3 | 196.9 | 176.7
829 | 714 | 300.5 | 211.1 | 189.2 | 195.4 | 197 | 176.6
830 | 715 | 300.6 | 211.2 | 189.3 | 195.5 | 197.1 | 176.6
831 | 716 | 300.5 | 211.4 | 189.4 | 195.6 | 197.2 | 176.6
832 | 717 | 300.5 | 211.5 | 189.5 | 195.7 | 197.2 | 176.7
833 | 718 | 300.4 | 211.6 | 189.6 | 195.8 | 197.3 | 176.7
834 | 719 | 300.3 | 211.7 | 189.7 | 195.8 | 197.4 | 176.8
835 | 720 | 300.3 | 211.8 | 189.8 | 195.9 | 197.5 | 176.9
836 | 721 | 300.2 | 211.9 | 189.9 | 196 | 197.5 | 176.9
837 | 722 | 300.2 | 212 | 190 | 196.1 | 197.6 | 177
838 | 723 | 300.2 | 212 | 190.1 | 196.2 | 197.6 | 177
839 | 724 | 300.2 | 212.1 | 190.2 | 196.2 | 197.7 | 177.2
840 | 725 | 300.2 | 212.2 | 190.3 | 196.3 | 197.8 | 177.1
841 | 726 | 300.1 | 212.3 | 190.3 | 196.4 | 197.9 | 177.4
842 | 727 | 300.2 | 212.4 | 190.4 | 196.5 | 197.9 | 177.4
843 | 728 | 300.3 | 212.5 | 190.5 | 196.6 | 198 | 177.4
844 | 729 | 300.2 | 212.6 | 190.6 | 196.6 | 198.1 | 177.3
845 | 730 | 300.2 | 212.7 | 190.7 | 196.7 | 198.2 | 177.3
846 | 731 | 300.2 | 212.8 | 190.8 | 196.8 | 198.3 | 177.3
847 | 732 | 300.3 | 212.8 | 190.9 | 196.8 | 198.4 | 177.2
848 | 733 | 300.3 | 212.9 | 191 | 196.9 | 198.5 | 177.3
849 | 734 | 300.4 | 213 | 191.1 | 196.9 | 198.6 | 177.3
850 | 735 | 300.4 | 213.1 | 191.1 | 197 | 198.7 | 177.5
851 | 736 | 300.5 | 213.1 | 191.2 | 197.1 | 198.8 | 177.3
852 | 737 | 300.5 | 213.2 | 191.3 | 197.1 | 198.9 | 177.4
853 | 738 | 300.5 | 213.3 | 191.4 | 197.1 | 199 | 177.5
854 | 739 | 300.4 | 213.3 | 191.5 | 197.2 | 199.1 | 177.5
855 | 740 | 300.4 | 213.4 | 191.6 | 197.2 | 199.2 | 177.7
856 | 741 | 300.4 | 213.5 | 191.6 | 197.3 | 199.3 | 177.7
857 | 742 | 300.4 | 213.5 | 191.8 | 197.3 | 199.4 | 177.8
858 | 743 | 300.4 | 213.6 | 191.8 | 197.3 | 199.5 | 177.9
859 | 744 | 300.4 | 213.7 | 191.9 | 197.4 | 199.5 | 177.9
860 | 745 | 300.4 | 213.8 | 192 | 197.4 | 199.6 | 177.9
861 | 746 | 300.4 | 213.9 | 192.1 | 197.4 | 199.7 | 177.9
862 | 747 | 300.5 | 214 | 192.2 | 197.5 | 199.8 | 178
863 | 748 | 300.5 | 214.2 | 192.2 | 197.5 | 199.9 | 178
864 | 749 | 300.4 | 214.3 | 192.3 | 197.5 | 200 | 178
865 | 750 | 300.4 | 214.4 | 192.4 | 197.5 | 200.1 | 178.2
866 | 751 | 300.4 | 214.6 | 192.5 | 197.6 | 200.1 | 178.3
867 | 752 | 300.4 | 214.7 | 192.6 | 197.6 | 200.2 | 178.3
868 | 753 | 300.4 | 214.8 | 192.7 | 197.6 | 200.3 | 178.2
869 | 754 | 300.4 | 214.9 | 192.8 | 197.7 | 200.4 | 178.1
870 | 755 | 300.3 | 215 | 192.9 | 197.7 | 200.4 | 178.1
871 | 756 | 300.2 | 215.1 | 192.9 | 197.7 | 200.5 | 178.3
872 | 757 | 300.2 | 215.2 | 193 | 197.7 | 200.5 | 178.5
873 | 758 | 300.1 | 215.3 | 193.1 | 197.8 | 200.6 | 178.8
874 | 759 | 300.1 | 215.4 | 193.2 | 197.8 | 200.7 | 178.6
875 | 760 | 300.1 | 215.5 | 193.3 | 197.8 | 200.8 | 178.6
876 | 761 | 300.2 | 215.5 | 193.4 | 197.8 | 200.9 | 178.7
877 | 762 | 300.2 | 215.6 | 193.4 | 197.9 | 201 | 178.7
878 | 763 | 300.3 | 215.6 | 193.5 | 197.9 | 201 | 178.7
879 | 764 | 300.3 | 215.7 | 193.6 | 198 | 201.1 | 178.7
880 | 765 | 300.3 | 215.7 | 193.7 | 198 | 201.2 | 178.8
881 | 766 | 300.3 | 215.7 | 193.8 | 198.1 | 201.3 | 178.9
882 | 767 | 300.2 | 215.7 | 193.9 | 198.1 | 201.4 | 178.9
883 | 768 | 300.1 | 215.8 | 194 | 198.2 | 201.5 | 179.1
884 | 769 | 300 | 215.7 | 194.1 | 198.2 | 201.5 | 179.3
885 | 770 | 300 | 215.7 | 194.2 | 198.3 | 201.5 | 179.4
886 | 771 | 300.1 | 215.7 | 194.2 | 198.4 | 201.6 | 179.4
887 | 772 | 300 | 215.7 | 194.3 | 198.4 | 201.6 | 179.5
888 | 773 | 299.9 | 215.8 | 194.3 | 198.5 | 201.7 | 179.6
889 | 774 | 299.9 | 215.8 | 194.4 | 198.6 | 201.7 | 179.6
890 | 775 | 299.6 | 215.9 | 194.5 | 198.6 | 201.8 | 179.5
891 | 776 | 299.5 | 215.9 | 194.6 | 198.7 | 201.8 | 179.6
892 | 777 | 299.5 | 216 | 194.7 | 198.8 | 201.9 | 179.7
893 | 778 | 299.5 | 216.1 | 194.7 | 198.8 | 202 | 179.6
894 | 779 | 299.5 | 216.1 | 194.9 | 198.8 | 202 | 179.8
895 | 780 | 299.4 | 216.2 | 194.9 | 198.9 | 202.1 | 179.6
896 | 781 | 299.3 | 216.3 | 195 | 199 | 202.2 | 179.6
897 | 782 | 299.3 | 216.4 | 195.1 | 199 | 202.2 | 179.7
898 | 783 | 299.3 | 216.4 | 195.1 | 199.1 | 202.3 | 179.7
899 | 784 | 299.1 | 216.5 | 195.2 | 199.2 | 202.4 | 179.9
900 | 785 | 299.1 | 216.6 | 195.3 | 199.2 | 202.4 | 180.1
901 | 786 | 299.1 | 216.6 | 195.4 | 199.3 | 202.5 | 180.3
902 | 787 | 299.1 | 216.7 | 195.5 | 199.3 | 202.5 | 180.2
903 | 788 | 299 | 216.7 | 195.5 | 199.4 | 202.6 | 180.2
904 | 789 | 299.1 | 216.7 | 195.7 | 199.5 | 202.6 | 180.1
905 | 790 | 299.1 | 216.8 | 195.7 | 199.5 | 202.7 | 180.2
906 | 791 | 299.1 | 216.9 | 195.8 | 199.6 | 202.8 | 180.3
907 | 792 | 299.2 | 217 | 195.9 | 199.6 | 202.8 | 180.3
908 | 793 | 299.3 | 217.1 | 195.9 | 199.7 | 202.9 | 180.4
909 | 794 | 299.3 | 217.3 | 196 | 199.7 | 202.9 | 180.5
910 | 795 | 299.3 | 217.4 | 196.1 | 199.8 | 203 | 180.5
911 | 796 | 299.3 | 217.6 | 196.2 | 199.8 | 203 | 180.5
912 | 797 | 299.3 | 217.7 | 196.3 | 199.8 | 203.1 | 180.7
913 | 798 | 299.5 | 217.9 | 196.3 | 199.9 | 203.1 | 180.7
914 | 799 | 299.6 | 218 | 196.4 | 199.9 | 203.2 | 180.8
915 | 800 | 299.6 | 218.1 | 196.5 | 199.9 | 203.3 | 180.7
916 | 801 | 299.6 | 218.3 | 196.5 | 200 | 203.3 | 180.8
917 | 802 | 299.7 | 218.4 | 196.6 | 200 | 203.4 | 180.7
918 | 803 | 299.8 | 218.5 | 196.7 | 200 | 203.4 | 180.9
919 | 804 | 299.7 | 218.7 | 196.7 | 200 | 203.5 | 181
920 | 805 | 299.6 | 218.8 | 196.8 | 200.1 | 203.5 | 180.9
921 | 806 | 299.8 | 218.9 | 196.9 | 200.1 | 203.6 | 180.9
922 | 807 | 299.9 | 219.1 | 197 | 200.1 | 203.7 | 181
923 | 808 | 300 | 219.3 | 197 | 200.1 | 203.7 | 181.1
924 | 809 | 300.2 | 219.5 | 197.1 | 200.1 | 203.8 | 181.3
925 | 810 | 300.3 | 219.7 | 197.2 | 200.2 | 203.8 | 181.4
926 | 811 | 300.4 | 219.8 | 197.3 | 200.2 | 203.9 | 181.5
927 | 812 | 300.5 | 220 | 197.4 | 200.2 | 203.9 | 181.5
928 | 813 | 300.5 | 220.1 | 197.5 | 200.2 | 204 | 181.4
929 | 814 | 300.5 | 220.2 | 197.5 | 200.2 | 204 | 181.5
930 | 815 | 300.6 | 220.2 | 197.6 | 200.3 | 204 | 181.6
931 | 816 | 300.7 | 220.2 | 197.8 | 200.3 | 204.1 | 181.7
932 | 817 | 300.7 | 220.2 | 197.8 | 200.3 | 204.1 | 181.9
933 | 818 | 300.6 | 220.3 | 197.9 | 200.4 | 204.2 | 181.9
934 | 819 | 300.6 | 220.5 | 197.9 | 200.4 | 204.2 | 182
935 | 820 | 300.7 | 220.6 | 198 | 200.4 | 204.3 | 182
936 | 821 | 300.8 | 220.7 | 198.1 | 200.5 | 204.3 | 182
937 | 822 | 300.7 | 220.8 | 198.2 | 200.5 | 204.4 | 181.9
938 | 823 | 300.9 | 220.9 | 198.2 | 200.5 | 204.5 | 182.1
939 | 824 | 301.1 | 221 | 198.3 | 200.6 | 204.5 | 182
940 | 825 | 301.1 | 221.1 | 198.4 | 200.6 | 204.6 | 182.1
941 | 826 | 301.1 | 221.1 | 198.4 | 200.6 | 204.7 | 182.1
942 | 827 | 301.2 | 221.1 | 198.5 | 200.6 | 204.8 | 182.1
943 | 828 | 301.3 | 221.1 | 198.6 | 200.6 | 204.9 | 182.1
944 | 829 | 301.3 | 221.1 | 198.7 | 200.6 | 204.9 | 182.2
945 | 830 | 301.2 | 221.1 | 198.7 | 200.7 | 205 | 182.5
946 | 831 | 301.2 | 221 | 198.8 | 200.7 | 205.1 | 182.5
947 | 832 | 301.2 | 221 | 198.9 | 200.7 | 205.2 | 182.6
948 | 833 | 301.1 | 220.9 | 199 | 200.7 | 205.2 | 182.6
949 | 834 | 301 | 220.9 | 199 | 200.8 | 205.3 | 182.7
950 | 835 | 300.9 | 220.9 | 199.1 | 200.8 | 205.4 | 182.7
951 | 836 | 300.9 | 220.9 | 199.2 | 200.8 | 205.4 | 182.6
952 | 837 | 300.8 | 220.9 | 199.3 | 200.8 | 205.5 | 182.7
953 | 838 | 300.7 | 220.9 | 199.4 | 200.9 | 205.5 | 182.9
954 | 839 | 300.7 | 221 | 199.4 | 200.9 | 205.6 | 182.9
955 | 840 | 300.7 | 221 | 199.5 | 201 | 205.6 | 182.9
956 | 841 | 300.6 | 221.1 | 199.6 | 201 | 205.7 | 183.2
957 | 842 | 300.5 | 221.2 | 199.7 | 201 | 205.7 | 183.3
958 | 843 | 300.4 | 221.3 | 199.7 | 201.1 | 205.7 | 183.3
959 | 844 | 300.3 | 221.4 | 199.8 | 201.1 | 205.8 | 183.4
960 | 845 | 300.2 | 221.4 | 199.8 | 201.2 | 205.9 | 183.5
961 | 846 | 300.1 | 221.4 | 199.9 | 201.2 | 205.9 | 183.5
962 | 847 | 300 | 221.4 | 200 | 201.3 | 205.9 | 183.4
963 | 848 | 299.9 | 221.4 | 200.1 | 201.3 | 206 | 183.5
964 | 849 | 299.8 | 221.4 | 200.1 | 201.4 | 206 | 183.5
965 | 850 | 299.7 | 221.3 | 200.2 | 201.4 | 206.1 | 183.6
966 | 851 | 299.7 | 221.3 | 200.3 | 201.5 | 206.1 | 183.6
967 | 852 | 299.7 | 221.2 | 200.3 | 201.5 | 206.2 | 183.4
968 | 853 | 299.6 | 221.2 | 200.4 | 201.6 | 206.2 | 183.4
969 | 854 | 299.6 | 221.2 | 200.5 | 201.7 | 206.2 | 183.2
970 | 855 | 299.6 | 221.1 | 200.5 | 201.7 | 206.2 | 183.4
971 | 856 | 299.6 | 221.1 | 200.6 | 201.8 | 206.2 | 183.4
972 | 857 | 299.7 | 221 | 200.7 | 201.9 | 206.3 | 183.5
973 | 858 | 299.8 | 221 | 200.7 | 201.9 | 206.3 | 183.6
974 | 859 | 299.8 | 221 | 200.8 | 202 | 206.4 | 183.6
975 | 860 | 299.8 | 221 | 200.9 | 202.1 | 206.4 | 183.7
976 | 861 | 299.8 | 221 | 200.9 | 202.1 | 206.5 | 183.6
977 | 862 | 299.9 | 221 | 201 | 202.2 | 206.6 | 183.6
978 | 863 | 299.9 | 221 | 201.1 | 202.2 | 206.6 | 183.5
979 | 864 | 300 | 221 | 201.1 | 202.3 | 206.7 | 183.6
980 | 865 | 300 | 221 | 201.2 | 202.4 | 206.7 | 183.7
981 | 866 | 300 | 221 | 201.3 | 202.4 | 206.8 | 183.7
982 | 867 | 299.9 | 221.1 | 201.3 | 202.5 | 206.8 | 183.7
983 | 868 | 300 | 221.1 | 201.4 | 202.6 | 206.8 | 183.8
984 | 869 | 300 | 221.1 | 201.5 | 202.7 | 206.9 | 183.8
985 | 870 | 300 | 221.2 | 201.5 | 202.7 | 206.9 | 183.9
986 | 871 | 300 | 221.2 | 201.6 | 202.8 | 207 | 183.7
987 | 872 | 299.9 | 221.3 | 201.7 | 202.9 | 207 | 183.7
988 | 873 | 299.9 | 221.3 | 201.7 | 202.9 | 207.1 | 183.7
989 | 874 | 299.9 | 221.4 | 201.8 | 203 | 207.1 | 183.8
990 | 875 | 299.9 | 221.4 | 201.9 | 203.1 | 207.1 | 183.9
991 | 876 | 300 | 221.4 | 201.9 | 203.1 | 207.2 | 183.9
992 | 877 | 300 | 221.4 | 202 | 203.2 | 207.2 | 184
993 | 878 | 300 | 221.5 | 202 | 203.3 | 207.3 | 184.1
994 | 879 | 300 | 221.6 | 202.1 | 203.4 | 207.3 | 184.1
995 | 880 | 300 | 221.7 | 202.2 | 203.5 | 207.4 | 184.1
996 | 881 | 300 | 221.8 | 202.2 | 203.5 | 207.4 | 184.2
997 | 882 | 300.1 | 221.9 | 202.3 | 203.6 | 207.5 | 184.2
998 | 883 | 300.1 | 221.9 | 202.4 | 203.7 | 207.5 | 184.2
999 | 884 | 300 | 222 | 202.4 | 203.7 | 207.6 | 184.1
1000 | 885 | 300.1 | 222.1 | 202.4 | 203.8 | 207.6 | 184
1001 | 886 | 300.1 | 222.1 | 202.5 | 203.9 | 207.7 | 184
1002 | 887 | 300.1 | 222.2 | 202.6 | 203.9 | 207.8 | 184.2
1003 | 888 | 300.2 | 222.3 | 202.6 | 204 | 207.8 | 184.1
1004 | 889 | 300.2 | 222.4 | 202.7 | 204.1 | 207.9 | 184.3
1005 | 890 | 300.2 | 222.5 | 202.7 | 204.2 | 207.9 | 184.4
1006 | 891 | 300.2 | 222.5 | 202.8 | 204.2 | 208 | 184.5
1007 | 892 | 300.3 | 222.6 | 202.8 | 204.3 | 208 | 184.6
1008 | 893 | 300.4 | 222.7 | 202.9 | 204.3 | 208.1 | 184.7
1009 | 894 | 300.5 | 222.8 | 203 | 204.4 | 208.1 | 184.7
1010 | 895 | 300.8 | 222.9 | 203.1 | 204.5 | 208.1 | 184.7
1011 | 896 | 300.9 | 223 | 203.1 | 204.5 | 208.1 | 184.6
1012 | 897 | 301.1 | 223.1 | 203.2 | 204.6 | 208.1 | 184.7
1013 | 898 | 301.4 | 223.2 | 203.2 | 204.7 | 208.2 | 184.7
1014 | 899 | 301.5 | 223.4 | 203.3 | 204.8 | 208.2 | 184.6
1015 | 900 | 301.6 | 223.5 | 203.3 | 204.8 | 208.2 | 184.6
1016 | 901 | 301.7 | 223.5 | 203.5 | 204.9 | 208.2 | 184.7
1017 | 902 | 301.7 | 223.4 | 203.8 | 204.9 | 208.2 | 184.6
1018 | 903 | 301.6 | 223.4 | 203.9 | 205 | 208.3 | 184.8
1019 | 904 | 301.6 | 223.4 | 203.9 | 205.1 | 208.4 | 184.9
1020 | 905 | 301.6 | 223.4 | 204 | 205.1 | 208.4 | 185.2
1021 | 906 | 301.6 | 223.5 | 204 | 205.2 | 208.5 | 185.1
1022 | 907 | 301.7 | 223.6 | 204.1 | 205.3 | 208.6 | 185.3
1023 | 908 | 301.7 | 223.7 | 204.1 | 205.4 | 208.6 | 185.4
1024 | 909 | 301.8 | 223.8 | 204.2 | 205.5 | 208.7 | 185.5
1025 | 910 | 301.8 | 223.9 | 204.3 | 205.5 | 208.7 | 185.4
1026 | 911 | 301.8 | 224 | 204.3 | 205.6 | 208.8 | 185.5
1027 | 912 | 301.7 | 224 | 204.4 | 205.7 | 208.9 | 185.4
1028 | 913 | 301.7 | 224 | 204.4 | 205.8 | 208.9 | 185.5
1029 | 914 | 301.7 | 224 | 204.5 | 205.8 | 209 | 185.5
1030 | 915 | 301.7 | 224 | 204.6 | 205.9 | 209 | 185.5
1031 | 916 | 301.7 | 224.1 | 204.6 | 206 | 209 | 185.4
1032 | 917 | 301.6 | 224.1 | 204.7 | 206 | 209 | 185.4
1033 | 918 | 301.5 | 224.2 | 204.7 | 206.1 | 209.1 | 185.4
1034 | 919 | 301.4 | 224.3 | 204.8 | 206.2 | 209.1 | 185.6
1035 | 920 | 301.4 | 224.4 | 204.8 | 206.3 | 209.2 | 185.4
1036 | 921 | 301.4 | 224.6 | 204.9 | 206.3 | 209.2 | 185.5
1037 | 922 | 301.3 | 224.7 | 205 | 206.4 | 209.3 | 185.5
1038 | 923 | 301.2 | 224.7 | 205 | 206.5 | 209.3 | 185.7
1039 | 924 | 301.1 | 224.6 | 205.1 | 206.5 | 209.4 | 185.7
1040 | 925 | 301.1 | 224.6 | 205.1 | 206.6 | 209.4 | 185.7
1041 | 926 | 301 | 224.6 | 205.2 | 206.6 | 209.5 | 186
1042 | 927 | 300.9 | 224.6 | 205.3 | 206.7 | 209.6 | 186
1043 | 928 | 300.8 | 224.7 | 205.3 | 206.7 | 209.6 | 186.1
1044 | 929 | 300.7 | 224.7 | 205.4 | 206.8 | 209.7 | 186.2
1045 | 930 | 300.7 | 224.8 | 205.4 | 206.9 | 209.7 | 186.3
1046 | 931 | 300.7 | 224.8 | 205.5 | 206.9 | 209.8 | 186.2
1047 | 932 | 300.6 | 224.7 | 205.5 | 207 | 209.8 | 186.2
1048 | 933 | 300.6 | 224.7 | 205.6 | 207.1 | 209.9 | 186.2
1049 | 934 | 300.5 | 224.7 | 205.6 | 207.1 | 209.9 | 186.2
1050 | 935 | 300.5 | 224.7 | 205.7 | 207.2 | 210 | 186.3
1051 | 936 | 300.5 | 224.7 | 205.8 | 207.3 | 210.1 | 186.3
1052 | 937 | 300.5 | 224.7 | 205.8 | 207.3 | 210.1 | 186.3
1053 | 938 | 300.5 | 224.8 | 205.9 | 207.4 | 210.2 | 186.4
1054 | 939 | 300.5 | 224.8 | 205.9 | 207.5 | 210.2 | 186.4
1055 | 940 | 300.5 | 224.8 | 206 | 207.5 | 210.3 | 186.4
1056 | 941 | 300.5 | 224.9 | 206 | 207.6 | 210.3 | 186.5
1057 | 942 | 300.4 | 224.9 | 206.1 | 207.7 | 210.4 | 186.5
1058 | 943 | 300.4 | 224.9 | 206.1 | 207.8 | 210.4 | 186.4
1059 | 944 | 300.4 | 224.9 | 206.2 | 207.8 | 210.4 | 186.3
1060 | 945 | 300.5 | 225 | 206.3 | 207.9 | 210.4 | 186.1
1061 | 946 | 300.5 | 225.1 | 206.3 | 208 | 210.4 | 186.3
1062 | 947 | 300.6 | 225.2 | 206.4 | 208.1 | 210.4 | 186.4
1063 | 948 | 300.8 | 225.2 | 206.4 | 208.2 | 210.4 | 186.3
1064 | 949 | 300.8 | 225.3 | 206.5 | 208.3 | 210.4 | 186.4
1065 | 950 | 301 | 225.3 | 206.5 | 208.4 | 210.4 | 186.5
1066 | 951 | 301 | 225.2 | 206.6 | 208.5 | 210.4 | 186.5
1067 | 952 | 301 | 225.2 | 206.6 | 208.6 | 210.4 | 186.4
1068 | 953 | 301.1 | 225.1 | 206.7 | 208.7 | 210.4 | 186.4
1069 | 954 | 301 | 225 | 206.7 | 208.8 | 210.4 | 186.3
1070 | 955 | 301 | 224.9 | 206.8 | 209 | 210.5 | 186.4
1071 | 956 | 301 | 224.7 | 206.8 | 209.1 | 210.5 | 186.2
1072 | 957 | 301.1 | 224.7 | 206.9 | 209.2 | 210.6 | 186.2
1073 | 958 | 301.1 | 224.7 | 207 | 209.3 | 210.7 | 186.3
1074 | 959 | 301 | 224.8 | 207 | 209.4 | 210.8 | 186.4
1075 | 960 | 301.2 | 224.9 | 207.1 | 209.6 | 210.8 | 186.6
1076 | 961 | 301.4 | 225 | 207.1 | 209.7 | 210.9 | 186.8
1077 | 962 | 301.5 | 225.1 | 207.1 | 209.9 | 210.9 | 186.8
1078 | 963 | 301.6 | 225.3 | 207.2 | 210 | 211 | 186.9
1079 | 964 | 301.6 | 225.4 | 207.3 | 210.1 | 211 | 186.8
1080 | 965 | 301.7 | 225.5 | 207.3 | 210.3 | 211 | 186.6
1081 | 966 | 301.7 | 225.6 | 207.3 | 210.4 | 211 | 186.6
1082 | 967 | 301.7 | 225.7 | 207.4 | 210.6 | 211 | 186.7
1083 | 968 | 301.8 | 225.8 | 207.4 | 210.7 | 211 | 187
1084 | 969 | 301.8 | 225.8 | 207.5 | 210.8 | 211.1 | 187
1085 | 970 | 301.7 | 225.8 | 207.6 | 211 | 211.2 | 187
1086 | 971 | 301.6 | 225.8 | 207.6 | 211.1 | 211.2 | 187
1087 | 972 | 301.6 | 225.7 | 207.7 | 211.3 | 211.3 | 186.9
1088 | 973 | 301.5 | 225.6 | 207.7 | 211.4 | 211.3 | 186.7
1089 | 974 | 301.3 | 225.6 | 207.8 | 211.5 | 211.4 | 186.7
1090 | 975 | 301.2 | 225.5 | 207.8 | 211.7 | 211.5 | 186.7
1091 | 976 | 301.3 | 225.5 | 207.9 | 211.8 | 211.6 | 186.7
1092 | 977 | 301.3 | 225.4 | 207.9 | 212 | 211.7 | 186.9
1093 | 978 | 301.1 | 225.4 | 208 | 212.1 | 211.7 | 186.9
1094 | 979 | 300.9 | 225.3 | 208 | 212.3 | 211.8 | 187
1095 | 980 | 300.9 | 225.3 | 208.1 | 212.5 | 211.8 | 187.1
1096 | 981 | 300.7 | 225.2 | 208.1 | 212.6 | 211.8 | 187.1
1097 | 982 | 300.7 | 225.3 | 208.2 | 212.8 | 211.8 | 187
1098 | 983 | 300.6 | 225.3 | 208.3 | 213 | 211.8 | 187
1099 | 984 | 300.5 | 225.3 | 208.3 | 213.2 | 211.8 | 187
1100 | 985 | 300.5 | 225.3 | 208.3 | 213.3 | 211.8 | 187.1
1101 | 986 | 300.5 | 225.4 | 208.4 | 213.5 | 211.8 | 187.1
1102 | 987 | 300.5 | 225.4 | 208.5 | 213.6 | 211.8 | 187
1103 | 988 | 300.5 | 225.5 | 208.5 | 213.7 | 211.8 | 187
1104 | 989 | 300.4 | 225.5 | 208.6 | 213.8 | 211.8 | 187
1105 | 990 | 300.4 | 225.6 | 208.6 | 214 | 211.8 | 187
1106 | 991 | 300.3 | 225.6 | 208.7 | 214.2 | 211.8 | 186.9
1107 | 992 | 300.3 | 225.6 | 208.7 | 214.4 | 211.9 | 186.6
1108 | 993 | 300.2 | 225.6 | 208.8 | 214.6 | 211.9 | 186.7
1109 | 994 | 300.2 | 225.6 | 208.8 | 214.8 | 212 | 186.8
1110 | 995 | 300.1 | 225.5 | 208.9 | 214.9 | 212.1 | 186.7
1111 | 996 | 299.9 | 225.5 | 209 | 215 | 212.1 | 186.9
1112 | 997 | 299.9 | 225.4 | 209 | 215.2 | 212.2 | 186.9
1113 | 998 | 299.9 | 225.3 | 209.1 | 215.3 | 212.2 | 187.1
1114 | 999 | 299.9 | 225.2 | 209.1 | 215.5 | 212.3 | 187.2
1115 | 1000 | 299.8 | 225.2 | 209.2 | 215.7 | 212.4 | 187.2
1116 | 1001 | 299.6 | 225.3 | 209.2 | 215.9 | 212.4 | 187.1
1117 | 1002 | 299.6 | 225.3 | 209.3 | 216.1 | 212.5 | 187.3
1118 | 1003 | 299.5 | 225.4 | 209.3 | 216.3 | 212.5 | 187.5
1119 | 1004 | 299.4 | 225.4 | 209.4 | 216.5 | 212.6 | 187.5
1120 | 1005 | 299.4 | 225.5 | 209.4 | 216.7 | 212.6 | 187.5
1121 | 1006 | 299.2 | 225.6 | 209.5 | 216.9 | 212.6 | 187.5
1122 | 1007 | 299.1 | 225.7 | 209.5 | 217.1 | 212.6 | 187.6
1123 | 1008 | 299 | 225.7 | 209.6 | 217.3 | 212.6 | 187.7
1124 | 1009 | 298.9 | 225.8 | 209.6 | 217.4 | 212.6 | 187.7
1125 | 1010 | 298.9 | 225.7 | 209.7 | 217.6 | 212.6 | 187.7
1126 | 1011 | 298.9 | 225.8 | 209.7 | 217.8 | 212.6 | 187.7
1127 | 1012 | 298.8 | 225.7 | 209.8 | 217.9 | 212.6 | 187.8
1128 | 1013 | 298.9 | 225.6 | 209.9 | 218.1 | 212.7 | 187.7
1129 | 1014 | 298.9 | 225.5 | 209.9 | 218.3 | 212.7 | 187.7
1130 | 1015 | 298.9 | 225.4 | 209.9 | 218.3 | 212.7 | 187.8
1131 | 1016 | 299 | 225.3 | 210 | 218.4 | 212.8 | 187.9
1132 | 1017 | 299 | 225.3 | 210.1 | 218.5 | 212.8 | 187.9
1133 | 1018 | 299 | 225.3 | 210.1 | 218.4 | 212.8 | 187.9
1134 | 1019 | 299 | 225.3 | 210.2 | 217.5 | 212.9 | 188.1
1135 | 1020 | 298.9 | 225.3 | 210.2 | 216.6 | 212.9 | 188.2
1136 | 1021 | 299 | 225.3 | 210.3 | 216.1 | 212.9 | 188.2
1137 | 1022 | 299.1 | 225.3 | 210.3 | 215.2 | 212.9 | 188.3
1138 | 1023 | 299.2 | 225.3 | 210.4 | 214.6 | 213 | 188.5
1139 | 1024 | 299.3 | 225.3 | 210.4 | 214 | 213.1 | 188.5
1140 | 1025 | 299.4 | 225.3 | 210.5 | 213.5 | 213.1 | 188.6
1141 | 1026 | 299.5 | 225.3 | 210.5 | 212.7 | 213.2 | 188.6
1142 | 1027 | 299.6 | 225.4 | 210.6 | 212.1 | 213.2 | 188.6
1143 | 1028 | 299.5 | 225.4 | 210.6 | 211.7 | 213.2 | 188.6
1144 | 1029 | 299.5 | 225.5 | 210.7 | 211.1 | 213.2 | 188.5
1145 | 1030 | 299.5 | 225.5 | 210.7 | 210.2 | 213.3 | 188.5
1146 | 1031 | 299.5 | 225.5 | 210.8 | 209.8 | 213.3 | 188.5
1147 | 1032 | 299.5 | 225.5 | 210.8 | 208.5 | 213.3 | 188.5
1148 | 1033 | 299.5 | 225.6 | 210.9 | 207.6 | 213.3 | 188.4
1149 | 1034 | 299.4 | 225.6 | 210.9 | 207.1 | 213.3 | 188.5
1150 | 1035 | 299.6 | 225.6 | 211 | 207 | 213.4 | 188.5
1151 | 1036 | 299.7 | 225.6 | 211 | 206.9 | 213.4 | 188.5
1152 | 1037 | 299.7 | 225.6 | 211.1 | 206.5 | 213.3 | 188.6
1153 | 1038 | 299.8 | 225.6 | 211.2 | 206.2 | 213.3 | 188.7
1154 | 1039 | 299.8 | 225.7 | 211.2 | 205.8 | 213.3 | 188.6
1155 | 1040 | 299.9 | 225.7 | 211.2 | 205.3 | 213.3 | 188.5
1156 | 1041 | 300 | 225.8 | 211.3 | 204 | 213.2 | 188.6
1157 | 1042 | 300 | 225.9 | 211.3 | 203.5 | 213.2 | 188.5
1158 | 1043 | 300 | 225.9 | 211.4 | 202.3 | 213.2 | 188.4
1159 | 1044 | 300 | 225.8 | 211.4 | 200.8 | 213.3 | 188.4
1160 | 1045 | 299.9 | 225.6 | 211.5 | 200.6 | 213.3 | 188.4
1161 | 1046 | 299.8 | 225.5 | 211.6 | 200.4 | 213.4 | 188.5
1162 | 1047 | 299.9 | 225.4 | 211.6 | 200 | 213.5 | 188.5
1163 | 1048 | 299.9 | 225.4 | 211.7 | 199.5 | 213.5 | 188.5
1164 | 1049 | 299.9 | 225.4 | 211.7 | 197.7 | 213.6 | 188.5
1165 | 1050 | 299.9 | 225.2 | 211.8 | 197.2 | 213.7 | 188.6
1166 | 1051 | 299.9 | 225.1 | 211.8 | 196.2 | 213.7 | 188.6
1167 | 1052 | 299.9 | 225 | 211.9 | 195.1 | 213.7 | 188.7
1168 | 1053 | 299.9 | 224.9 | 211.9 | 194 | 213.7 | 188.8
1169 | 1054 | 299.8 | 225 | 212 | 193 | 213.8 | 188.8
1170 | 1055 | 299.8 | 224.9 | 212 | 191.6 | 213.8 | 188.8
1171 | 1056 | 299.8 | 224.9 | 212 | 190.4 | 213.8 | 188.8
1172 | 1057 | 299.7 | 224.8 | 212.1 | 189.8 | 213.9 | 188.7
1173 | 1058 | 299.7 | 224.8 | 212.2 | 188.6 | 213.9 | 188.7
1174 | 1059 | 299.7 | 224.8 | 212.2 | 187.3 | 213.9 | 188.6
1175 | 1060 | 299.7 | 224.8 | 212.2 | 185.9 | 213.9 | 188.6
1176 | 1061 | 299.8 | 224.8 | 212.3 | 185.8 | 213.9 | 188.6
1177 | 1062 | 299.9 | 224.9 | 212.3 | 185.6 | 214 | 188.7
1178 | 1063 | 300 | 224.9 | 212.4 | 185.7 | 214.1 | 188.8
1179 | 1064 | 300.1 | 224.9 | 212.4 | 186.3 | 214.1 | 188.8
1180 | 1065 | 300.2 | 224.9 | 212.5 | 185.5 | 214.1 | 188.8
1181 | 1066 | 300.1 | 225 | 212.5 | 183.8 | 214.2 | 188.9
1182 | 1067 | 300.1 | 225.1 | 212.6 | 182.6 | 214.2 | 188.8
1183 | 1068 | 300.1 | 225.1 | 212.6 | 181.1 | 214.3 | 188.6
1184 | 1069 | 300 | 225 | 212.7 | 179.8 | 214.3 | 188.6
1185 | 1070 | 299.9 | 224.9 | 212.7 | 178.2 | 214.3 | 188.7
1186 | 1071 | 299.9 | 224.8 | 212.7 | 178.4 | 214.4 | 188.8
1187 | 1072 | 299.8 | 224.9 | 212.8 | 179.1 | 214.4 | 188.7
1188 | 1073 | 299.7 | 225 | 212.8 | 179.6 | 214.5 | 188.6
1189 | 1074 | 299.7 | 225 | 212.8 | 178 | 214.5 | 188.6
1190 | 1075 | 299.6 | 225.1 | 212.9 | 176.9 | 214.4 | 188.7
1191 | 1076 | 299.6 | 225.2 | 213 | 175.5 | 214.5 | 188.8
1192 | 1077 | 299.7 | 225.3 | 213 | 174.4 | 214.4 | 188.9
1193 | 1078 | 299.8 | 225.5 | 213 | 173.8 | 214.4 | 188.9
1194 | 1079 | 299.8 | 225.6 | 213.1 | 172.5 | 214.3 | 188.8
1195 | 1080 | 299.9 | 225.6 | 213.1 | 173.4 | 214.2 | 188.9
1196 | 1081 | 299.9 | 225.7 | 213.1 | 173.8 | 214.1 | 189
1197 | 1082 | 299.9 | 225.8 | 213.2 | 174.1 | 213.9 | 189.1
1198 | 1083 | 300 | 225.8 | 213.2 | 174.3 | 213.8 | 189
1199 | 1084 | 300 | 225.9 | 213.3 | 174.7 | 213.8 | 189
1200 | 1085 | 300.1 | 225.9 | 213.3 | 174.3 | 213.7 | 189.1
1201 | 1086 | 300.1 | 225.9 | 213.3 | 173.5 | 213.8 | 189.1
1202 | 1087 | 300.1 | 225.9 | 213.4 | 173.9 | 213.8 | 189.1
1203 | 1088 | 300.2 | 225.9 | 213.4 | 173.7 | 213.8 | 189
1204 | 1089 | 300.2 | 226 | 213.5 | 172.6 | 213.8 | 189.1
1205 | 1090 | 300.2 | 226.1 | 213.5 | 171.9 | 213.8 | 189.2
1206 | 1091 | 300.1 | 226.2 | 213.5 | 170.4 | 213.8 | 189.2
1207 | 1092 | 300.1 | 226.4 | 213.6 | 170.3 | 213.8 | 189.2
1208 | 1093 | 300.1 | 226.5 | 213.6 | 170 | 213.8 | 189.2
1209 | 1094 | 300.2 | 226.6 | 213.7 | 169.4 | 213.8 | 189.2
1210 | 1095 | 300.2 | 226.6 | 213.7 | 168.4 | 213.8 | 189.2
1211 | 1096 | 300.4 | 226.7 | 213.7 | 167.1 | 213.7 | 189.3
1212 | 1097 | 300.5 | 226.7 | 213.8 | 166.6 | 213.6 | 189.3
1213 | 1098 | 300.6 | 226.8 | 213.8 | 166.8 | 213.6 | 189.4
1214 | 1099 | 300.5 | 226.8 | 213.9 | 166.9 | 213.6 | 189.5
1215 | 1100 | 300.5 | 226.8 | 213.9 | 166 | 213.6 | 189.6
1216 | 1101 | 300.5 | 226.9 | 213.9 | 165 | 213.7 | 189.6
1217 | 1102 | 300.4 | 226.9 | 213.9 | 164.3 | 213.7 | 189.8
1218 | 1103 | 300.5 | 226.9 | 214 | 163.6 | 213.8 | 189.8
1219 | 1104 | 300.6 | 226.9 | 214 | 163.5 | 213.8 | 189.7
1220 | 1105 | 300.6 | 227 | 214.1 | 163 | 213.8 | 189.7
1221 | 1106 | 300.8 | 227 | 214.1 | 162.5 | 213.8 | 189.8
1222 | 1107 | 300.8 | 227.1 | 214.1 | 162.2 | 213.7 | 189.8
1223 | 1108 | 300.8 | 227.1 | 214.2 | 161.5 | 213.8 | 189.9
1224 | 1109 | 300.8 | 227.2 | 214.3 | 161.2 | 213.8 | 189.8
1225 | 1110 | 300.9 | 227.2 | 214.5 | 160.8 | 213.8 | 189.9
1226 | 1111 | 300.9 | 227.3 | 214.7 | 160.5 | 213.7 | 190.1
1227 | 1112 | 300.9 | 227.5 | 214.7 | 159.6 | 213.7 | 190.1
1228 | 1113 | 301.1 | 227.6 | 214.7 | 158.9 | 213.8 | 190.2
1229 | 1114 | 301.2 | 227.6 | 214.8 | 158.2 | 213.8 | 190.2
1230 | 1115 | 301.2 | 227.7 | 214.8 | 157.8 | 213.9 | 190.2
1231 | 1116 | 301.2 | 227.9 | 214.8 | 157.8 | 213.9 | 190.1
1232 | 1117 | 301.3 | 228 | 214.9 | 157.3 | 213.8 | 190.1
1233 | 1118 | 301.3 | 228 | 214.9 | 157.2 | 213.9 | 190.2
1234 | 1119 | 301.4 | 228 | 214.9 | 158 | 213.9 | 190.2
1235 | 1120 | 301.4 | 228.1 | 214.9 | 157.6 | 213.9 | 190.3
1236 | 1121 | 301.5 | 228.1 | 215 | 157.1 | 213.8 | 190.5
1237 | 1122 | 301.5 | 228.1 | 215 | 156.9 | 213.8 | 190.4
1238 | 1123 | 301.6 | 228.1 | 215.1 | 157 | 213.9 | 190.5
1239 | 1124 | 301.7 | 228.1 | 215.1 | 156.9 | 213.8 | 190.5
1240 | 1125 | 301.8 | 228.2 | 215.1 | 158.3 | 213.9 | 190.7
1241 | 1126 | 301.7 | 228.2 | 215.1 | 158.3 | 213.9 | 190.8
1242 | 1127 | 301.7 | 228.2 | 215.2 | 158.3 | 213.8 | 190.8
1243 | 1128 | 301.8 | 228.1 | 215.2 | 157.8 | 213.8 | 190.7
1244 | 1129 | 301.8 | 228 | 215.3 | 157.6 | 213.8 | 190.6
1245 | 1130 | 301.8 | 228 | 215.3 | 157 | 213.7 | 190.6
1246 | 1131 | 301.7 | 228 | 215.3 | 156.7 | 213.6 | 190.5
1247 | 1132 | 301.6 | 228 | 215.4 | 157.7 | 213.7 | 190.7
1248 | 1133 | 301.6 | 228 | 215.4 | 157 | 213.7 | 190.7
1249 | 1134 | 301.6 | 228 | 215.4 | 156.9 | 213.7 | 190.7
1250 | 1135 | 301.7 | 228.1 | 215.5 | 157.2 | 213.7 | 190.7
1251 | 1136 | 301.7 | 228 | 215.5 | 156.6 | 213.8 | 190.7
1252 | 1137 | 301.6 | 228 | 215.6 | 156.4 | 213.8 | 190.4
1253 | 1138 | 301.6 | 227.9 | 215.6 | 156.7 | 213.9 | 190.5
1254 | 1139 | 301.5 | 227.9 | 215.6 | 156.4 | 213.9 | 190.5
1255 | 1140 | 301.5 | 227.9 | 215.7 | 157 | 213.9 | 190.6
1256 | 1141 | 301.4 | 227.8 | 215.7 | 157.1 | 213.9 | 190.7
1257 | 1142 | 301.3 | 227.8 | 215.7 | 156.9 | 214 | 190.8
1258 | 1143 | 301.4 | 227.8 | 215.8 | 156.2 | 213.9 | 190.9
1259 | 1144 | 301.4 | 227.8 | 215.8 | 155.8 | 213.8 | 191
1260 | 1145 | 301.3 | 227.8 | 215.9 | 156.5 | 213.8 | 191.1
1261 | 1146 | 301.2 | 227.9 | 215.9 | 156.6 | 213.8 | 191.2
1262 | 1147 | 301.2 | 227.9 | 215.9 | 156.4 | 213.8 | 191.1
1263 | 1148 | 301.2 | 227.8 | 216 | 158 | 213.9 | 191.2
1264 | 1149 | 301.2 | 227.8 | 216 | 157.7 | 213.9 | 191.1
1265 | 1150 | 301.2 | 227.8 | 216 | 157.6 | 214 | 191.2
1266 | 1151 | 301.2 | 227.7 | 216.1 | 158 | 214.1 | 191.3
1267 | 1152 | 301.1 | 227.7 | 216.1 | 157.3 | 214.1 | 191.3
1268 | 1153 | 301 | 227.7 | 216.1 | 156.6 | 214.2 | 191.4
1269 | 1154 | 301 | 227.6 | 216.1 | 157.3 | 214.3 | 191.4
1270 | 1155 | 301 | 227.6 | 216.2 | 158.2 | 214.4 | 191.5
1271 | 1156 | 301 | 227.6 | 216.2 | 159.7 | 214.5 | 191.4
1272 | 1157 | 301 | 227.6 | 216.2 | 160.8 | 214.6 | 191.5
1273 | 1158 | 301.1 | 227.5 | 216.3 | 161.4 | 214.7 | 191.5
1274 | 1159 | 301.1 | 227.4 | 216.3 | 161.4 | 214.8 | 191.6
1275 | 1160 | 301 | 227.5 | 216.4 | 162.4 | 214.7 | 191.6
1276 | 1161 | 301 | 227.6 | 216.4 | 163.3 | 214.8 | 191.6
1277 | 1162 | 300.9 | 227.7 | 216.4 | 163.1 | 214.8 | 191.7
1278 | 1163 | 300.9 | 227.7 | 216.5 | 163.9 | 214.8 | 191.7
1279 | 1164 | 300.9 | 227.8 | 216.5 | 163.9 | 214.9 | 191.8
1280 | 1165 | 300.8 | 228 | 216.5 | 163.5 | 214.8 | 191.8
1281 | 1166 | 300.8 | 227.9 | 216.6 | 163.9 | 214.7 | 191.8
1282 | 1167 | 300.8 | 227.8 | 216.6 | 163 | 214.7 | 191.8
1283 | 1168 | 300.9 | 227.6 | 216.7 | 162.1 | 214.7 | 191.7
1284 | 1169 | 300.8 | 227.5 | 216.7 | 161.5 | 214.8 | 191.8
1285 | 1170 | 300.8 | 227.5 | 216.7 | 161.1 | 214.7 | 191.9
1286 | 1171 | 300.8 | 227.5 | 216.8 | 159.9 | 214.6 | 191.9
1287 | 1172 | 300.8 | 227.5 | 216.8 | 159.4 | 214.6 | 191.9
1288 | 1173 | 300.8 | 227.6 | 216.8 | 159.1 | 214.6 | 191.9 | Time of first failure
1289 | 1174 | 300.8 | 227.6 | 216.9 | 158.2 | 214.5 | 191.8 | 1173 | 0
1290 | 1175 | 300.8 | 227.5 | 216.9 | 157.7 | 214.5 | 191.8 | 1173 | 900
1291 | 1176 | 300.7 | 227.4 | 216.9 | 156.9 | 214.5 | 191.8
1292 | 1177 | 300.8 | 227.3 | 217 | 156.3 | 214.5 | 191.8
1293 | 1178 | 300.8 | 227.3 | 217 | 156.4 | 214.6 | 191.9
1294 | 1179 | 300.8 | 227.3 | 217 | 156.1 | 214.7 | 191.8
1295 | 1180 | 300.8 | 227.3 | 217.1 | 156 | 214.7 | 191.8
1296 | 1181 | 300.9 | 227.4 | 217.1 | 155.5 | 214.7 | 191.8
1297 | 1182 | 300.9 | 227.4 | 217.1 | 155.3 | 214.8 | 191.8
1298 | 1183 | 301 | 227.4 | 217.2 | 154.8 | 214.7 | 191.9
1299 | 1184 | 301 | 227.3 | 217.2 | 154.6 | 214.7 | 192
1300 | 1185 | 301 | 227.2 | 217.2 | 154.4 | 214.8 | 192.1
1301 | 1186 | 300.8 | 227.1 | 217.3 | 154.8 | 214.8 | 192
1302 | 1187 | 300.8 | 227 | 217.3 | 155.2 | 214.8 | 192.1
1303 | 1188 | 300.9 | 226.9 | 217.3 | 155.6 | 214.8 | 192.1
1304 | 1189 | 300.9 | 226.7 | 217.4 | 155.6 | 214.8 | 192.2
1305 | 1190 | 300.9 | 226.6 | 217.4 | 154.8 | 214.8 | 192.1
1306 | 1191 | 301.1 | 226.8 | 217.4 | 154.4 | 214.7 | 192
1307 | 1192 | 301.1 | 226.8 | 217.5 | 154 | 214.6 | 192
1308 | 1193 | 301.1 | 226.8 | 217.5 | 153.9 | 214.6 | 192
1309 | 1194 | 301.1 | 226.9 | 217.5 | 154.1 | 214.6 | 192
1310 | 1195 | 301.1 | 226.8 | 217.6 | 154.7 | 214.7 | 191.9
1311 | 1196 | 301.1 | 226.9 | 217.6 | 155.1 | 214.5 | 192
1312 | 1197 | 301.2 | 226.9 | 217.7 | 155.4 | 214.5 | 192
1313 | 1198 | 301.3 | 226.9 | 217.7 | 155.4 | 214.5 | 192.1
1314 | 1199 | 301.3 | 226.9 | 217.7 | 156 | 214.5 | 192.1
1315 | 1200 | 301.3 | 226.8 | 217.7 | 155.9 | 214.6 | 192.2
1316 | 1201 | 301.3 | 226.7 | 217.7 | 156.2 | 214.7 | 192.2
1317 | 1202 | 301.2 | 226.6 | 217.8 | 156.7 | 214.7 | 192.1
1318 | 1203 | 301.2 | 226.5 | 217.8 | 156.3 | 214.5 | 192.1
1319 | 1204 | 301.2 | 226.6 | 217.8 | 156 | 214.5 | 192.1
1320 | 1205 | 301.3 | 226.6 | 217.9 | 155.8 | 214.6 | 192.2
1321 | 1206 | 301.2 | 226.5 | 217.9 | 155.6 | 214.7 | 192.2
1322 | 1207 | 301.1 | 226.3 | 217.9 | 154.9 | 214.7 | 192.3
1323 | 1208 | 301 | 226.2 | 218 | 154.9 | 214.7 | 192.3
1324 | 1209 | 301 | 226.1 | 218 | 154.8 | 214.7 | 192.4
1325 | 1210 | 301 | 226 | 218 | 154.1 | 214.6 | 192.4
1326 | 1211 | 301 | 226 | 218.1 | 154.5 | 214.6 | 192.4
1327 | 1212 | 300.9 | 225.9 | 218.1 | 154.5 | 214.7 | 192.4
1328 | 1213 | 300.7 | 225.7 | 218.1 | 154.6 | 214.9 | 192.5
1329 | 1214 | 300.6 | 225.7 | 218.1 | 155 | 215 | 192.5
1330 | 1215 | 300.6 | 225.6 | 218.2 | 156 | 215.1 | 192.6
1331 | 1216 | 300.5 | 225.6 | 218.2 | 156.5 | 215.2 | 192.6
1332 | 1217 | 300.4 | 225.5 | 218.3 | 156.7 | 215.3 | 192.6
1333 | 1218 | 300.3 | 225.4 | 218.3 | 157 | 215.3 | 192.6
1334 | 1219 | 300.2 | 225.4 | 218.3 | 158 | 215.4 | 192.6
1335 | 1220 | 300.2 | 225.3 | 218.3 | 159.3 | 215.4 | 192.7
1336 | 1221 | 300.2 | 225.2 | 218.4 | 159.4 | 215.4 | 192.7
1337 | 1222 | 300.2 | 225.1 | 218.4 | 159.2 | 215.4 | 192.6
1338 | 1223 | 300.2 | 225 | 218.4 | 159.2 | 215.3 | 192.5
1339 | 1224 | 300.2 | 224.9 | 218.5 | 159.1 | 215.4 | 192.6
1340 | 1225 | 300.2 | 224.7 | 218.5 | 158.8 | 215.4 | 192.6
1341 | 1226 | 300.1 | 224.5 | 218.5 | 159.1 | 215.4 | 192.5
1342 | 1227 | 300.1 | 224.3 | 218.6 | 159.2 | 215.4 | 192.4
1343 | 1228 | 300 | 224.1 | 218.6 | 159.6 | 215.5 | 192.5
1344 | 1229 | 300 | 224.1 | 218.6 | 159.4 | 215.4 | 192.5
1345 | 1230 | 300 | 224.3 | 218.6 | 158.7 | 215.4 | 192.6
1346 | 1231 | 299.9 | 224.4 | 218.7 | 159.4 | 215.3 | 192.6
1347 | 1232 | 299.8 | 224.5 | 218.7 | 159.9 | 215.2 | 192.6
1348 | 1233 | 299.8 | 224.5 | 218.7 | 160.1 | 215.2 | 192.5
1349 | 1234 | 299.7 | 224.5 | 218.8 | 159.7 | 215.2 | 192.5
1350 | 1235 | 299.7 | 224.5 | 218.8 | 159.1 | 215.1 | 192.4
1351 | 1236 | 299.7 | 224.5 | 218.8 | 158.4 | 214.8 | 192.5
1352 | 1237 | 299.7 | 224.5 | 218.9 | 158.4 | 214.7 | 192.5
1353 | 1238 | 299.6 | 224.4 | 218.9 | 158.3 | 214.7 | 192.5
1354 | 1239 | 299.5 | 224.2 | 218.9 | 158.1 | 214.7 | 192.5
1355 | 1240 | 299.5 | 224.1 | 219 | 157.8 | 214.8 | 192.5
1356 | 1241 | 299.5 | 224.1 | 219 | 156.8 | 214.8 | 192.5
1357 | 1242 | 299.4 | 224.1 | 219 | 155.9 | 215 | 192.5
1358 | 1243 | 299.4 | 224.2 | 219 | 155.9 | 215.1 | 192.5
1359 | 1244 | 299.4 | 224.1 | 219.1 | 155.2 | 215.3 | 192.4
1360 | 1245 | 299.5 | 224 | 219.1 | 154.9 | 215.4 | 192.4
1361 | 1246 | 299.4 | 223.9 | 219.2 | 154 | 215.4 | 192.4
1362 | 1247 | 299.3 | 223.9 | 219.2 | 153.1 | 215.4 | 192.3
1363 | 1248 | 299.3 | 224.1 | 219.2 | 152.5 | 215.3 | 192.3
1364 | 1249 | 299.3 | 224.2 | 219.2 | 152 | 215.3 | 192.2
1365 | 1250 | 299.3 | 224.2 | 219.3 | 151.1 | 215.4 | 192.3
1366 | 1251 | 299.4 | 224.3 | 219.2 | 150.4 | 215.4 | 192.3
1367 | 1252 | 299.4 | 224.2 | 219.3 | 149.6 | 215.1 | 192.3
1368 | 1253 | 299.3 | 224.1 | 219.3 | 149.5 | 215.1 | 192.3
1369 | 1254 | 299.3 | 224.1 | 219.4 | 150 | 214.9 | 192.3
1370 | 1255 | 299.2 | 224.3 | 219.4 | 150.4 | 214.9 | 192.4
1371 | 1256 | 299.3 | 224.5 | 219.4 | 150.1 | 214.9 | 192.4
1372 | 1257 | 299.3 | 224.6 | 219.6 | 149.5 | 215 | 192.4
1373 | 1258 | 299.3 | 224.7 | 219.7 | 150 | 215.1 | 192.4
1374 | 1259 | 299.3 | 224.8 | 219.7 | 149.7 | 215.2 | 192.3
1375 | 1260 | 299.3 | 224.9 | 219.7 | 150.5 | 215.2 | 192.2
1376 | 1261 | 299.2 | 225.1 | 219.7 | 151 | 215.1 | 192
1377 | 1262 | 299.2 | 225.3 | 219.8 | 150.3 | 214.9 | 192
1378 | 1263 | 299.3 | 225.5 | 219.8 | 150 | 214.8 | 192
1379 | 1264 | 299.4 | 225.7 | 219.8 | 149.9 | 214.7 | 192
1380 | 1265 | 299.4 | 225.7 | 219.8 | 149.6 | 214.7 | 192
1381 | 1266 | 299.4 | 225.6 | 219.8 | 149.9 | 214.5 | 192
1382 | 1267 | 299.4 | 225.5 | 219.9 | 149.9 | 214.5 | 192.1
1383 | 1268 | 299.3 | 225.6 | 219.9 | 150.2 | 214.6 | 192.1
1384 | 1269 | 299.2 | 225.6 | 219.9 | 150 | 214.7 | 192.1
1385 | 1270 | 299.2 | 225.5 | 219.9 | 149.1 | 214.8 | 192.2
1386 | 1271 | 299.2 | 225.6 | 220 | 148.1 | 214.9 | 192.2
1387 | 1272 | 299.2 | 225.5 | 220 | 147.6 | 215 | 192.2
1388 | 1273 | 298.9 | 225.5 | 220 | 147.2 | 215.1 | 192.3
1389 | 1274 | 298.9 | 225.4 | 220 | 147.6 | 215.2 | 192.4
1390 | 1275 | 298.9 | 225.5 | 220.1 | 147.8 | 215.3 | 192.3
1391 | 1276 | 299 | 225.6 | 220.1 | 147.5 | 215.4 | 192.3
1392 | 1277 | 299.3 | 225.7 | 220.1 | 146.6 | 215.5 | 192.3
1393 | 1278 | 299.5 | 225.8 | 220.1 | 146.1 | 215.6 | 192.3
1394 | 1279 | 299.6 | 226 | 220.2 | 145.9 | 215.6 | 192.3
1395 | 1280 | 299.7 | 226.1 | 220.2 | 145.6 | 215.6 | 192.3
1396 | 1281 | 299.8 | 226.2 | 220.2 | 145.3 | 215.7 | 192.4
1397 | 1282 | 299.8 | 226.3 | 220.2 | 145.1 | 215.8 | 192.4
1398 | 1283 | 299.8 | 226.4 | 220.2 | 145 | 215.8 | 192.5
1399 | 1284 | 299.7 | 226.3 | 220.3 | 144.6 | 215.6 | 192.5
1400 | 1285 | 299.7 | 226 | 220.3 | 144.2 | 215.6 | 192.5
1401 | 1286 | 299.8 | 225.6 | 220.3 | 144 | 215.7 | 192.5
1402 | 1287 | 299.8 | 225.2 | 220.3 | 143.7 | 215.7 | 192.5
1403 | 1288 | 299.9 | 224.9 | 220.4 | 144.2 | 215.6 | 192.6
1404 | 1289 | 299.8 | 224.7 | 220.4 | 144.3 | 215.6 | 192.6
1405 | 1290 | 299.7 | 224.6 | 220.4 | 144.5 | 215.6 | 192.6
1406 | 1291 | 299.8 | 224.6 | 220.4 | 145.7 | 215.7 | 192.5
1407 | 1292 | 299.8 | 224.7 | 220.4 | 146.3 | 215.6 | 192.5
1408 | 1293 | 299.7 | 224.7 | 220.4 | 147.6 | 215.4 | 192.6
1409 | 1294 | 299.6 | 224.8 | 220.5 | 149.4 | 215.1 | 192.6
1410 | 1295 | 299.5 | 224.8 | 220.5 | 150.7 | 215.2 | 192.6
1411 | 1296 | 299.7 | 224.7 | 220.5 | 150.7 | 215.3 | 192.6
1412 | 1297 | 299.8 | 224.7 | 220.5 | 150 | 215.5 | 192.6
1413 | 1298 | 299.8 | 224.4 | 220.6 | 149.3 | 215.7 | 192.6
1414 | 1299 | 299.7 | 224.1 | 220.6 | 149 | 215.8 | 192.7
1415 | 1300 | 299.7 | 223.7 | 220.6 | 148.7 | 215.8 | 192.7
1416 | 1301 | 299.7 | 223.5 | 220.6 | 148.3 | 215.6 | 192.7
1417 | 1302 | 299.8 | 223.5 | 220.6 | 148.7 | 215.3 | 192.6
1418 | 1303 | 299.8 | 223.8 | 220.7 | 149.2 | 215 | 192.6
1419 | 1304 | 299.8 | 223.9 | 220.7 | 148.9 | 214.8 | 192.6
1420 | 1305 | 299.7 | 224 | 220.7 | 148.6 | 214.9 | 192.6
1421 | 1306 | 299.7 | 224.1 | 220.7 | 149 | 215 | 192.7
1422 | 1307 | 299.6 | 224.2 | 220.7 | 149.2 | 215 | 192.8
1423 | 1308 | 299.5 | 224.2 | 220.8 | 148.8 | 215.1 | 192.8
1424 | 1309 | 299.5 | 224.3 | 220.8 | 148.6 | 215.1 | 192.8
1425 | 1310 | 299.5 | 224.3 | 220.8 | 148.4 | 215.2 | 192.8
1426 | 1311 | 299.4 | 224.3 | 220.9 | 148 | 215.3 | 192.8
1427 | 1312 | 299.3 | 224.2 | 220.9 | 147.2 | 215.5 | 192.8
1428 | 1313 | 299.3 | 224.2 | 220.9 | 147 | 215.5 | 192.7
1429 | 1314 | 299.3 | 224.1 | 220.9 | 146.9 | 215.5 | 192.7
1430 | 1315 | 299.3 | 224.1 | 220.9 | 146.5 | 215.6 | 192.7
1431 | 1316 | 299.2 | 224.1 | 221 | 146.4 | 215.6 | 192.7
1432 | 1317 | 299.2 | 224 | 221 | 145.9 | 215.7 | 192.7
1433 | 1318 | 299.1 | 224 | 221 | 145.3 | 215.7 | 192.7
1434 | 1319 | 299 | 223.9 | 221 | 145.4 | 215.7 | 192.6
1435 | 1320 | 299.1 | 223.8 | 221 | 145.8 | 215.9 | 192.6
1436 | 1321 | 299 | 223.8 | 221.1 | 146.2 | 215.8 | 192.6
1437 | 1322 | 299 | 223.9 | 221.1 | 146.6 | 215.7 | 192.7
1438 | 1323 | 299.1 | 224.1 | 221.1 | 146.7 | 215.9 | 192.7
1439 | 1324 | 299.2 | 224.2 | 221.1 | 146.6 | 215.6 | 192.7
1440 | 1325 | 299.3 | 224.3 | 221.1 | 147 | 215.6 | 192.7
1441 | 1326 | 299.3 | 224.4 | 221.2 | 146.9 | 215.7 | 192.7
1442 | 1327 | 299.4 | 224.4 | 221.2 | 146.7 | 215.8 | 192.7
1443 | 1328 | 299.5 | 224.4 | 221.2 | 146.4 | 215.9 | 192.7
1444 | 1329 | 299.5 | 224.5 | 221.2 | 146.3 | 215.9 | 192.8
1445 | 1330 | 299.5 | 224.6 | 221.2 | 145.9 | 215.9 | 192.7
1446 | 1331 | 299.4 | 224.5 | 221.3 | 145.1 | 216 | 192.7
1447 | 1332 | 299.4 | 224.3 | 221.3 | 144.8 | 215.9 | 192.8
1448 | 1333 | 299.4 | 224.2 | 221.3 | 145.4 | 215.5 | 192.8
1449 | 1334 | 299.3 | 224.3 | 221.3 | 145.9 | 215.4 | 192.8
1450 | 1335 | 299.2 | 224.3 | 221.3 | 146.3 | 215.3 | 192.9
1451 | 1336 | 299.3 | 224.4 | 221.4 | 146.9 | 215.2 | 192.9
1452 | 1337 | 299.3 | 224.4 | 221.4 | 147.1 | 215.3 | 193
1453 | 1338 | 299.2 | 224.4 | 221.4 | 147.3 | 215.4 | 193
1454 | 1339 | 299.3 | 224.3 | 221.4 | 147.2 | 215.4 | 193.1
1455 | 1340 | 299.4 | 224.2 | 221.4 | 147.6 | 215.5 | 193.1
1456 | 1341 | 299.3 | 224.1 | 221.4 | 148.4 | 215.6 | 193.1
1457 | 1342 | 299.4 | 223.9 | 221.5 | 149 | 215.6 | 193.1
1458 | 1343 | 299.4 | 223.8 | 221.5 | 149.6 | 215.6 | 193
1459 | 1344 | 299.4 | 223.9 | 221.5 | 149.7 | 215.6 | 193.1
1460 | 1345 | 299.4 | 224 | 221.5 | 149.9 | 215.6 | 193.1
1461 | 1346 | 299.5 | 224.2 | 221.5 | 150.2 | 215.6 | 193.1
1462 | 1347 | 299.5 | 224.3 | 221.6 | 150.1 | 215.3 | 193.2
1463 | 1348 | 299.4 | 224.4 | 221.6 | 149.7 | 215.3 | 193.2
1464 | 1349 | 299.4 | 224.4 | 221.6 | 149.1 | 215.4 | 193.2
1465 | 1350 | 299.4 | 224.2 | 221.6 | 148.8 | 215.4 | 193.2
1466 | 1351 | 299.6 | 223.9 | 221.6 | 148 | 215.6 | 193.2
1467 | 1352 | 299.6 | 223.8 | 221.7 | 147.5 | 215.8 | 193.2
1468 | 1353 | 299.6 | 223.9 | 221.7 | 147.7 | 215.9 | 193.2
1469 | 1354 | 299.6 | 224.1 | 221.7 | 147 | 216 | 193.2
1470 | 1355 | 299.8 | 224.3 | 221.7 | 146.8 | 216 | 193.2
1471 | 1356 | 299.9 | 224.5 | 221.7 | 147.5 | 216.1 | 193.2
1472 | 1357 | 299.9 | 224.8 | 221.8 | 147 | 216.2 | 193.3
1473 | 1358 | 299.9 | 225 | 221.8 | 147.1 | 216.3 | 193.2
1474 | 1359 | 299.9 | 225.1 | 221.8 | 146.8 | 216.1 | 193.2
1475 | 1360 | 299.9 | 225.1 | 221.8 | 146.7 | 216.1 | 193.2
1476 | 1361 | 299.8 | 225.1 | 221.8 | 145.4 | 216.2 | 193.3
1477 | 1362 | 299.9 | 225 | 221.8 | 145 | 216.3 | 193.3
1478 | 1363 | 299.9 | 224.9 | 221.9 | 145.4 | 216.4 | 193.3
1479 | 1364 | 299.9 | 224.7 | 221.9 | 145.1 | 216.4 | 193.3
1480 | 1365 | 299.9 | 224.8 | 221.9 | 145.1 | 216.4 | 193.3
1481 | 1366 | 300 | 224.9 | 221.9 | 144.9 | 216.5 | 193.3
1482 | 1367 | 300 | 224.9 | 221.9 | 144.5 | 216.6 | 193.3
1483 | 1368 | 299.9 | 224.8 | 222 | 145.6 | 216.7 | 193.3
1484 | 1369 | 300 | 224.8 | 222 | 147.2 | 216.7 | 193.3
1485 | 1370 | 300 | 225 | 222 | 147.7 | 216.7 | 193.3
1486 | 1371 | 299.9 | 225 | 222 | 147.8 | 216.3 | 193.3
1487 | 1372 | 299.9 | 224.8 | 222 | 148 | 216 | 193.3
1488 | 1373 | 299.9 | 224.7 | 222 | 147.6 | 216.2 | 193.3
1489 | 1374 | 299.9 | 224.7 | 222.1 | 147.8 | 216.3 | 193.3
1490 | 1375 | 299.9 | 224.7 | 222.1 | 148.8 | 216.3 | 193.3
1491 | 1376 | 299.9 | 224.8 | 222.1 | 149 | 216.1 | 193.3
1492 | 1377 | 299.8 | 224.8 | 222.1 | 148.8 | 216.1 | 193.3
1493 | 1378 | 299.7 | 224.8 | 222.1 | 148.9 | 216 | 193.3
1494 | 1379 | 299.7 | 224.8 | 222.1 | 149 | 216.2 | 193.3
1495 | 1380 | 299.7 | 224.8 | 222.1 | 149 | 216.1 | 193.3
1496 | 1381 | 299.7 | 224.7 | 222.2 | 149.4 | 216 | 193.3
1497 | 1382 | 299.7 | 224.8 | 222.2 | 149.5 | 215.9 | 193.4
1498 | 1383 | 299.7 | 224.8 | 222.2 | 149.4 | 215.9 | 193.4
1499 | 1384 | 299.6 | 224.9 | 222.2 | 149.2 | 215.8 | 193.4
1500 | 1385 | 299.6 | 225.1 | 222.2 | 148.6 | 215.7 | 193.4
1501 | 1386 | 299.6 | 225.3 | 222.2 | 148.2 | 215.8 | 193.4
1502 | 1387 | 299.6 | 225.3 | 222.3 | 148.5 | 215.8 | 193.4
1503 | 1388 | 299.5 | 225.5 | 222.3 | 148.7 | 215.8 | 193.4
1504 | 1389 | 299.5 | 225.6 | 222.3 | 148.7 | 215.7 | 193.4
1505 | 1390 | 299.6 | 225.7 | 222.3 | 149.1 | 215.5 | 193.4
1506 | 1391 | 299.6 | 225.8 | 222.3 | 149.9 | 215.5 | 193.5
1507 | 1392 | 299.5 | 225.8 | 222.4 | 150 | 215.4 | 193.5
1508 | 1393 | 299.5 | 225.7 | 222.4 | 150.4 | 215.6 | 193.5
1509 | 1394 | 299.6 | 225.5 | 222.4 | 150.7 | 215.7 | 193.5
1510 | 1395 | 299.6 | 225.2 | 222.4 | 151.1 | 215.5 | 193.5
1511 | 1396 | 299.5 | 225.1 | 222.4 | 151.8 | 215.5 | 193.6
1512 | 1397 | 299.4 | 225 | 222.4 | 153.1 | 215.3 | 193.5
1513 | 1398 | 299.4 | 224.9 | 222.5 | 153.4 | 215.3 | 193.6
1514 | 1399 | 299.4 | 224.7 | 222.5 | 153.1 | 215.3 | 193.6
1515 | 1400 | 299.3 | 224.7 | 222.5 | 152.7 | 215.3 | 193.6
1516 | 1401 | 299.2 | 224.7 | 222.5 | 152.7 | 215.3 | 193.6
1517 | 1402 | 299.2 | 224.7 | 222.5 | 152.5 | 215.4 | 193.7
1518 | 1403 | 299.4 | 224.7 | 222.6 | 151.9 | 215.5 | 193.7
1519 | 1404 | 299.4 | 224.9 | 222.6 | 151.6 | 215.4 | 193.7
1520 | 1405 | 299.4 | 225 | 222.6 | 151 | 215 | 193.7
1521 | 1406 | 299.5 | 225.1 | 222.6 | 150.8 | 214.9 | 193.7
1522 | 1407 | 299.5 | 225.3 | 222.7 | 151.1 | 214.8 | 193.7
1523 | 1408 | 299.4 | 225.6 | 222.7 | 152.2 | 214.9 | 193.7
1524 | 1409 | 299.3 | 225.8 | 222.7 | 153.9 | 214.8 | 193.7
1525 | 1410 | 299.3 | 226 | 222.7 | 153.9 | 214.8 | 193.7
1526 | 1411 | 299.3 | 226.1 | 222.7 | 153.7 | 214.8 | 193.7
1527 | 1412 | 299.3 | 226.2 | 222.7 | 154 | 215 | 193.7
1528 | 1413 | 299.4 | 226.3 | 222.8 | 153.9 | 215.1 | 193.8
1529 | 1414 | 299.6 | 226.4 | 222.8 | 153.5 | 214.9 | 193.8
1530 | 1415 | 299.8 | 226.6 | 222.8 | 153.3 | 214.8 | 193.9
1531 | 1416 | 299.8 | 226.8 | 222.8 | 152.9 | 214.9 | 193.9
1532 | 1417 | 299.9 | 226.9 | 222.8 | 152 | 214.9 | 193.9
1533 | 1418 | 299.8 | 227 | 222.8 | 151.2 | 214.9 | 193.9
1534 | 1419 | 299.8 | 227.1 | 222.8 | 150.8 | 214.8 | 193.8
1535 | 1420 | 299.8 | 227.3 | 222.8 | 150.4 | 214.8 | 193.8
1536 | 1421 | 300 | 227.4 | 222.9 | 150.1 | 214.9 | 193.8
1537 | 1422 | 300 | 227.4 | 222.9 | 150.1 | 215.1 | 193.8
1538 | 1423 | 300 | 227.6 | 222.9 | 150.6 | 214.9 | 193.8
1539 | 1424 | 299.9 | 227.8 | 222.9 | 150.6 | 214.8 | 193.8
1540 | 1425 | 299.9 | 228 | 222.9 | 150.7 | 214.7 | 193.8
1541 | 1426 | 299.7 | 228.1 | 222.9 | 150.6 | 214.5 | 193.9
1542 | 1427 | 299.9 | 228.2 | 222.9 | 150.2 | 214.5 | 193.9
1543 | 1428 | 300.2 | 228.3 | 223 | 150.7 | 214.5 | 193.9
1544 | 1429 | 300.3 | 228.5 | 222.9 | 150.7 | 214.5 | 193.9
1545 | 1430 | 300.3 | 228.7 | 223 | 150.1 | 214.3 | 194
1546 | 1431 | 300.3 | 228.7 | 223 | 149.4 | 214 | 194
1547 | 1432 | 300.3 | 228.8 | 223 | 149.2 | 214.2 | 194
1548 | 1433 | 300.4 | 228.9 | 223 | 149.4 | 214.3 | 194
1549 | 1434 | 300.6 | 229 | 223 | 149.7 | 214.3 | 194
1550 | 1435 | 300.7 | 229.1 | 223.1 | 149.9 | 214.4 | 194
1551 | 1436 | 300.8 | 229.3 | 223.1 | 149.4 | 214.7 | 193.9
1552 | 1437 | 300.7 | 229.5 | 223.1 | 149.5 | 214.8 | 194
1553 | 1438 | 300.7 | 229.4 | 223.1 | 149.5 | 214.9 | 193.9
1554 | 1439 | 300.7 | 229.3 | 223.1 | 149.9 | 214.8 | 193.9
1555 | 1440 | 300.8 | 229.4 | 223.1 | 149.8 | 214.4 | 193.9
1556 | 1441 | 300.8 | 229.5 | 223.1 | 149.6 | 213.9 | 194
1557 | 1442 | 300.7 | 229.7 | 223.1 | 149.3 | 214 | 194
1558 | 1443 | 300.7 | 229.7 | 223.2 | 149.2 | 214.1 | 194
1559 | 1444 | 300.8 | 229.8 | 223.2 | 149 | 214.4 | 194.1
1560 | 1445 | 300.8 | 229.8 | 223.2 | 149.4 | 214.5 | 194.1
1561 | 1446 | 300.8 | 229.7 | 223.2 | 149.3 | 214.4 | 194.1
1562 | 1447 | 300.8 | 229.7 | 223.2 | 149.5 | 214.5 | 194.1
1563 | 1448 | 300.9 | 229.8 | 223.2 | 149.7 | 214.4 | 194.1
1564 | 1449 | 300.9 | 229.8 | 223.2 | 150.3 | 214.6 | 194.1
1565 | 1450 | 300.9 | 229.9 | 223.2 | 150.7 | 214.8 | 194.2
1566 | 1451 | 300.9 | 229.9 | 223.3 | 151.1 | 215 | 194.2
1567 | 1452 | 300.9 | 229.8 | 223.3 | 151.1 | 215.1 | 194.2
1568 | 1453 | 300.9 | 229.6 | 223.3 | 150.7 | 215.3 | 194.2
1569 | 1454 | 300.9 | 229.4 | 223.3 | 150.8 | 215.4 | 194.2
1570 | 1455 | 301.1 | 229.3 | 223.3 | 151 | 215.2 | 194.2
1571 | 1456 | 301.2 | 229.3 | 223.3 | 151 | 215.2 | 194.3
1572 | 1457 | 301.2 | 229.3 | 223.3 | 151.3 | 215.1 | 194.3
1573 | 1458 | 301.1 | 229.3 | 223.3 | 150.9 | 214.9 | 194.3
1574 | 1459 | 300.9 | 229.2 | 223.4 | 150.9 | 215.2 | 194.3
1575 | 1460 | 300.9 | 229.1 | 223.4 | 151.2 | 215 | 194.3
1576 | 1461 | 301 | 229 | 223.4 | 151 | 214.8 | 194.3
1577 | 1462 | 301.1 | 229 | 223.4 | 151.4 | 214.9 | 194.2
1578 | 1463 | 301.3 | 229.2 | 223.4 | 151.6 | 214.7 | 194.2
1579 | 1464 | 301.3 | 229.3 | 223.4 | 151.8 | 214.7 | 194.2
1580 | 1465 | 301.3 | 229.5 | 223.4 | 151.4 | 214.7 | 194.2
1581 | 1466 | 301.2 | 229.5 | 223.5 | 151.5 | 214.6 | 194.2
1582 | 1467 | 301.2 | 229.6 | 223.5 | 152.1 | 214.6 | 194.2
1583 | 1468 | 301.1 | 229.5 | 223.5 | 152.5 | 214.7 | 194.2
1584 | 1469 | 301.1 | 229.5 | 223.5 | 152.7 | 214.9 | 194.3
1585 | 1470 | 301.1 | 229.4 | 223.5 | 152.8 | 214.6 | 194.3
1586 | 1471 | 301 | 229.2 | 223.5 | 152.8 | 214.3 | 194.3
1587 | 1472 | 300.9 | 229.2 | 223.6 | 152.6 | 214.4 | 194.3
1588 | 1473 | 300.8 | 229 | 223.6 | 152.3 | 214.8 | 194.3
1589 | 1474 | 300.7 | 228.9 | 223.6 | 153.2 | 214.6 | 194.4
1590 | 1475 | 300.7 | 228.7 | 223.6 | 154 | 214.4 | 194.4
1591 | 1476 | 300.7 | 228.6 | 223.6 | 153.9 | 214.6 | 194.4
1592 | 1477 | 300.6 | 228.4 | 223.6 | 153.6 | 214.6 | 194.4
1593 | 1478 | 300.5 | 228.2 | 223.6 | 153.3 | 214.6 | 194.4
1594 | 1479 | 300.4 | 228.1 | 223.6 | 153 | 214.7 | 194.4
1595 | 1480 | 300.2 | 228.2 | 223.7 | 153.1 | 214.9 | 194.3
1596 | 1481 | 300.1 | 228.2 | 223.7 | 153.1 | 214.9 | 194.4
1597 | 1482 | 299.9 | 228.3 | 223.7 | 153.2 | 214.8 | 194.4
1598 | 1483 | 299.8 | 228.4 | 223.7 | 152.8 | 214.9 | 194.4
1599 | 1484 | 299.8 | 228.4 | 223.7 | 152.5 | 214.8 | 194.4
1600 | 1485 | 299.8 | 228.4 | 223.7 | 152.9 | 214.6 | 194.4
1601 | 1486 | 299.7 | 228.3 | 223.7 | 153 | 214.7 | 194.4
1602 | 1487 | 299.6 | 228.1 | 223.7 | 152.8 | 214.8 | 194.4
1603 | 1488 | 299.6 | 227.9 | 223.9 | 152.6 | 214.9 | 194.4
1604 | 1489 | 299.6 | 227.7 | 224.1 | 153.5 | 214.8 | 194.3
1605 | 1490 | 299.5 | 227.5 | 224.3 | 153.8 | 214.7 | 194.3
1606 | 1491 | 299.4 | 227.4 | 224.3 | 153 | 214.7 | 194.3
1607 | 1492 | 299.2 | 227.3 | 224.3 | 153.3 | 214.7 | 194.3
1608 | 1493 | 299.1 | 227.3 | 224.3 | 152.9 | 214.9 | 194.3
1609 | 1494 | 298.8 | 227.2 | 224.3 | 152.7 | 215 | 194.3
1610 | 1495 | 298.6 | 227 | 224.4 | 153.1 | 215.1 | 194.3
1611 | 1496 | 298.3 | 226.8 | 224.4 | 152.9 | 215.2 | 194.3
1612 | 1497 | 297.9 | 226.8 | 224.4 | 152.6 | 215.3 | 194.3
1613 | 1498 | 297.6 | 226.7 | 224.4 | 152.3 | 215.4 | 194.2
1614 | 1499 | 297.4 | 226.5 | 224.4 | 151.8 | 215.1 | 194.2
1615 | 1500 | 297.1 | 226.3 | 224.4 | 151.2 | 215.1 | 194.2
1616 | 1501 | 296.7 | 225.9 | 224.5 | 151.4 | 215.3 | 194.2
1617 | 1502 | 296.2 | 225.6 | 224.5 | 151.2 | 215.2 | 194.2
1618 | 1503 | 296 | 225.5 | 224.5 | 151 | 214.9 | 194.2
1619 | 1504 | 295.8 | 225.4 | 224.5 | 150.9 | 215.1 | 194.1
1620 | 1505 | 295.4 | 225.1 | 224.5 | 150.9 | 215.3 | 194.1
1621 | 1506 | 295.1 | 224.8 | 224.5 | 151 | 215.4 | 194.1
1622 | 1507 | 294.9 | 224.5 | 224.5 | 150.8 | 215.3 | 194
1623 | 1508 | 294.5 | 224 | 224.5 | 149.9 | 215.1 | 194
1624 | 1509 | 294.1 | 223.7 | 224.5 | 150.1 | 214.7 | 194
1625 | 1510 | 293.7 | 223.4 | 224.6 | 150.1 | 214.9 | 194
1626 | 1511 | 293.2 | 223.1 | 224.6 | 149.9 | 215 | 194
1627 | 1512 | 292.8 | 223 | 224.6 | 149.9 | 214.9 | 193.9
1628 | 1513 | 292.4 | 223 | 224.6 | 149.7 | 215 | 193.8
1629 | 1514 | 292.2 | 223 | 224.6 | 149.5 | 215.1 | 193.7
1630 | 1515 | 291.7 | 222.9 | 224.6 | 149.5 | 215.1 | 193.6
1631 | 1516 | 291.2 | 222.8 | 224.6 | 149.5 | 214.6 | 193.5
1632 | 1517 | 290.9 | 222.9 | 224.6 | 149.6 | 214.4 | 193.5
1633 | 1518 | 290.5 | 222.9 | 224.6 | 148.8 | 214.4 | 193.4
1634 | 1519 | 290.1 | 223 | 224.6 | 148.7 | 214.6 | 193.3
1635 | 1520 | 289.8 | 223.3 | 224.6 | 149 | 214.7 | 193.3
1636 | 1521 | 289.4 | 223.4 | 224.6 | 149.1 | 214.6 | 193.2
1637 | 1522 | 289 | 223.4 | 224.6 | 149.4 | 214.4 | 193.2
1638 | 1523 | 288.7 | 223.3 | 224.6 | 149.5 | 214.2 | 193.1
1639 | 1524 | 288.3 | 223.2 | 224.6 | 149.2 | 214.1 | 193.1
1640 | 1525 | 288 | 223 | 224.6 | 149.1 | 213.8 | 193.1
1641 | 1526 | 287.7 | 222.5 | 224.6 | 148.9 | 213.4 | 193
1642 | 1527 | 287.4 | 222.2 | 224.5 | 148.1 | 213.6 | 193
1643 | 1528 | 287 | 222 | 224.6 | 147.9 | 213.5 | 192.9
1644 | 1529 | 286.5 | 222 | 224.5 | 147.5 | 213.6 | 192.9
1645 | 1530 | 286 | 222 | 224.5 | 147.1 | 213.6 | 192.9
1646 | 1531 | 285.5 | 221.9 | 224.5 | 146.9 | 213.5 | 192.8
1647 | 1532 | 285.1 | 221.8 | 224.5 | 147.1 | 213.3 | 192.8
1648 | 1533 | 284.7 | 221.8 | 224.5 | 148 | 213.3 | 192.8
1649 | 1534 | 284.4 | 221.7 | 224.5 | 148.1 | 213.2 | 192.7
1650 | 1535 | 284 | 221.5 | 224.5 | 148.3 | 213.1 | 192.7
1651 | 1536 | 283.4 | 221.5 | 224.5 | 148.8 | 212.7 | 192.6
1652 | 1537 | 282.9 | 221.5 | 224.5 | 149.1 | 212.6 | 192.6
1653 | 1538 | 282.4 | 221.5 | 224.5 | 148.5 | 212.7 | 192.5
1654 | 1539 | 282 | 221.6 | 224.5 | 147.2 | 212.7 | 192.5
1655 | 1540 | 281.6 | 221.5 | 224.4 | 146.4 | 212.7 | 192.4
1656 | 1541 | 281.2 | 221.4 | 224.4 | 145.8 | 212.6 | 192.4
1657 | 1542 | 280.7 | 221.3 | 224.4 | 145.3 | 212.4 | 192.3
1658 | 1543 | 280.3 | 221.1 | 224.4 | 144.9 | 212.1 | 192.3
1659 | 1544 | 279.9 | 220.8 | 224.4 | 144.9 | 212.1 | 192.2
1660 | 1545 | 279.5 | 220.6 | 224.4 | 144.3 | 212.1 | 192.1
1661 | 1546 | 279.2 | 220.4 | 224.3 | 143.5 | 212 | 192
1662 | 1547 | 278.9 | 220.2 | 224.3 | 142.8 | 212.1 | 191.9
1663 | 1548 | 278.5 | 220 | 224.3 | 142.7 | 212 | 191.8
1664 | 1549 | 278.1 | 219.8 | 224.3 | 143.5 | 212 | 191.7
1665 | 1550 | 277.7 | 219.6 | 224.2 | 144.4 | 211.6 | 191.6
1666 | 1551 | 277.3 | 219.3 | 224.2 | 144.9 | 211.5 | 191.5
1667 | 1552 | 276.9 | 218.9 | 224.2 | 145.2 | 211.5 | 191.3
1668 | 1553 | 276.5 | 218.6 | 224.2 | 145.3 | 211.4 | 191.2
1669 | 1554 | 276.1 | 218.3 | 224.1 | 144.8 | 211.3 | 191.2
1670 | 1555 | 275.7 | 217.9 | 224.1 | 144.8 | 211.3 | 191.1
1671 | 1556 | 275.3 | 217.5 | 224.1 | 145.1 | 211.1 | 191.1
1672 | 1557 | 274.9 | 217.1 | 224.1 | 145 | 210.9 | 191
1673 | 1558 | 274.4 | 216.7 | 224 | 144.9 | 210.7 | 190.9
1674 | 1559 | 274.1 | 216.4 | 224 | 144.8 | 210.5 | 190.8
1675 | 1560 | 273.7 | 215.9 | 224 | 144.9 | 210.5 | 190.7
1676 | 1561 | 273.3 | 215.6 | 223.9 | 144.6 | 210.4 | 190.6
1677 | 1562 | 273 | 215.6 | 223.9 | 144.3 | 210.3 | 190.5
1678 | 1563 | 272.7 | 215.5 | 223.9 | 144 | 210.2 | 190.4
1679 | 1564 | 272.3 | 215.5 | 223.8 | 143.4 | 210.1 | 190.3
1680 | 1565 | 271.9 | 215.6 | 223.8 | 142.7 | 209.9 | 190.2
1681 | 1566 | 271.4 | 215.6 | 223.8 | 142.3 | 209.7 | 190.2
1682 | 1567 | 270.9 | 215.6 | 223.7 | 141.9 | 209.6 | 190.1
1683 | 1568 | 270.5 | 215.5 | 223.7 | 141.6 | 209.3 | 190
1684 | 1569 | 270.1 | 215.4 | 223.6 | 140.9 | 209.1 | 189.9
1685 | 1570 | 269.8 | 215.2 | 223.6 | 140.4 | 208.8 | 189.8
1686 | 1571 | 269.3 | 214.8 | 223.5 | 140.2 | 208.5 | 189.7
1687 | 1572 | 268.9 | 214.4 | 223.5 | 140.6 | 208.4 | 189.7
1688 | 1573 | 268.6 | 214.1 | 223.5 | 140.2 | 208 | 189.6
1689 | 1574 | 268.3 | 213.9 | 223.4 | 139.4 | 207.8 | 189.5
1690 | 1575 | 267.9 | 213.6 | 223.3 | 138.6 | 207.5 | 189.4
1691 | 1576 | 267.5 | 213.3 | 223.3 | 138 | 207.1 | 189.3
1692 | 1577 | 267.1 | 213.1 | 223.2 | 137.7 | 206.8 | 189.3
1693 | 1578 | 266.8 | 212.8 | 223.2 | 137.6 | 206.5 | 189.2
1694 | 1579 | 266.4 | 212.6 | 223.1 | 137.2 | 206 | 189.1
1695 | 1580 | 266.1 | 212.3 | 223.1 | 137.3 | 205.9 | 189.1
1696 | 1581 | 265.7 | 211.8 | 223 | 137.2 | 205.7 | 189
1697 | 1582 | 265.3 | 211.3 | 223 | 137.3 | 205.4 | 188.9
1698 | 1583 | 264.9 | 211 | 222.9 | 137.1 | 205.4 | 188.8
1699 | 1584 | 264.4 | 210.8 | 222.9 | 136.6 | 205.5 | 188.8
1700 | 1585 | 264 | 210.6 | 222.8 | 136.4 | 204.8 | 188.7
1701 | 1586 | 263.8 | 210.3 | 222.8 | 136.1 | 204.8 | 188.6
1702 | 1587 | 263.4 | 210.2 | 222.7 | 135.9 | 204.9 | 188.5
1703 | 1588 | 263 | 210 | 222.6 | 135.4 | 204.9 | 188.4
1704 | 1589 | 262.5 | 209.8 | 222.6 | 135.3 | 204.6 | 188.3
1705 | 1590 | 262.1 | 209.4 | 222.5 | 135.5 | 204.7 | 188.2
1706 | 1591 | 261.6 | 209.1 | 222.5 | 135.7 | 204.2 | 188.1
1707 | 1592 | 261.2 | 208.9 | 222.4 | 135.8 | 204.2 | 188
1708 | 1593 | 260.8 | 208.8 | 222.3 | 135.6 | 204.2 | 187.9
1709 | 1594 | 260.4 | 208.5 | 222.3 | 135.7 | 204 | 187.8
1710 | 1595 | 260 | 208.2 | 222.2 | 135.6 | 203.7 | 187.7
1711 | 1596 | 259.7 | 207.6 | 222.1 | 135 | 203.6 | 187.5
1712 | 1597 | 259.3 | 207.2 | 222.1 | 134.7 | 203.9 | 187.4
1713 | 1598 | 258.9 | 207 | 222 | 134.2 | 203.7 | 187.2
1714 | 1599 | 258.6 | 206.7 | 221.9 | 134.1 | 203.5 | 187.1
1715 | 1600 | 258.2 | 206.5 | 221.9 | 134.2 | 203.3 | 187
1716 | 1601 | 257.8 | 206.2 | 221.8 | 134.1 | 203.2 | 186.8
1717 | 1602 | 257.4 | 205.8 | 221.8 | 134 | 203.1 | 186.7
1718 | 1603 | 257 | 205.7 | 221.7 | 133.8 | 202.9 | 186.6
1719 | 1604 | 256.6 | 205.7 | 221.6 | 133.5 | 202.9 | 186.5
1720 | 1605 | 256.2 | 205.6 | 221.5 | 133.8 | 202.3 | 186.4
1721 | 1606 | 255.8 | 205.4 | 221.5 | 133.5 | 202.2 | 186.3
1722 | 1607 | 255.4 | 205.3 | 221.4 | 133.1 | 201.9 | 186.1
1723 | 1608 | 255.2 | 205.3 | 221.3 | 132.8 | 201.8 | 185.9
1724 | 1609 | 254.9 | 205.2 | 221.2 | 132.6 | 201.7 | 185.8
1725 | 1610 | 254.5 | 205.2 | 221.1 | 132.4 | 201.7 | 185.7
1726 | 1611 | 254.3 | 205.1 | 221.1 | 132.2 | 201.7 | 185.6
1727 | 1612 | 253.9 | 205 | 221 | 131.7 | 201.6 | 185.4
1728 | 1613 | 253.5 | 205 | 220.9 | 131.2 | 201.2 | 185.3
1729 | 1614 | 253.1 | 204.8 | 220.8 | 131 | 201.1 | 185.2
1730 | 1615 | 252.7 | 204.7 | 220.8 | 131 | 200.8 | 185.1
1731 | 1616 | 252.4 | 204.6 | 220.7 | 130.9 | 200.1 | 184.9
1732 | 1617 | 252 | 204.5 | 220.6 | 130.6 | 199.8 | 184.8
1733 | 1618 | 251.7 | 204.4 | 220.5 | 130.3 | 199.6 | 184.6
1734 | 1619 | 251.3 | 204.1 | 220.4 | 129.6 | 199.4 | 184.5
1735 | 1620 | 250.9 | 204 | 220.3 | 129.2 | 199.1 | 184.3
1736 | 1621 | 250.4 | 203.9 | 220.3 | 129.1 | 199 | 184.2
1737 | 1622 | 249.9 | 203.7 | 220.2 | 128.8 | 199 | 184
1738 | 1623 | 249.6 | 203.5 | 220.1 | 128.8 | 199 | 183.8
1739 | 1624 | 249.4 | 203.4 | 220 | 128.6 | 198.8 | 183.6
1740 | 1625 | 249 | 203.2 | 219.9 | 127.9 | 198.3 | 183.5
1741 | 1626 | 248.6 | 202.9 | 219.8 | 127.3 | 198 | 183.3
1742 | 1627 | 248.2 | 202.8 | 219.7 | 126.6 | 197.9 | 183.2
1743 | 1628 | 247.8 | 202.6 | 219.7 | 126.2 | 197.7 | 183.1
1744 | 1629 | 247.4 | 202.5 | 219.5 | 125.9 | 197.6 | 182.9
1745 | 1630 | 247.1 | 202.3 | 219.5 | 125.8 | 197.3 | 182.8
1746 | 1631 | 246.7 | 202.1 | 219.3 | 125.7 | 196.8 | 182.7
1747 | 1632 | 246.4 | 201.9 | 219.3 | 125.8 | 196.3 | 182.6
1748 | 1633 | 246 | 201.6 | 219.2 | 125.5 | 196 | 182.5
1749 | 1634 | 245.7 | 201.3 | 219.1 | 125.4 | 196.1 | 182.4
1750 | 1635 | 245.3 | 201.1 | 219 | 125.2 | 196 | 182.2
1751 | 1636 | 245 | 200.8 | 218.9 | 125.1 | 196.3 | 182.1
1752 | 1637 | 244.5 | 200.4 | 218.8 | 125 | 196.4 | 182
1753 | 1638 | 244.1 | 200 | 218.7 | 124.5 | 196.6 | 181.9
1754 | 1639 | 243.8 | 199.7 | 218.6 | 124.4 | 196.6 | 181.8
1755 | 1640 | 243.5 | 199.4 | 218.5 | 124 | 196.5 | 181.7
1756 | 1641 | 243.2 | 199.1 | 218.4 | 124 | 196.5 | 181.5
1757 | 1642 | 242.9 | 198.6 | 218.3 | 123.5 | 196.5 | 181.4
1758 | 1643 | 242.6 | 198 | 218.2 | 123.3 | 196.4 | 181.2
1759 | 1644 | 242.2 | 197.7 | 218.1 | 123.9 | 196.4 | 181.1
1760 | 1645 | 241.9 | 197.5 | 218 | 124.7 | 196.2 | 180.9
1761 | 1646 | 241.6 | 197.3 | 217.9 | 124.9 | 196 | 180.8
1762 | 1647 | 241.2 | 197.1 | 217.8 | 124.9 | 195.9 | 180.7
1763 | 1648 | 241 | 197 | 217.7 | 124.7 | 195.8 | 180.6
1764 | 1649 | 240.8 | 196.7 | 217.6 | 124 | 195.3 | 180.5
1765 | 1650 | 240.5 | 196.4 | 217.5 | 123.3 | 195.2 | 180.4
1766 | 1651 | 240.2 | 196.2 | 217.3 | 123.2 | 195 | 180.3
1767 | 1652 | 239.8 | 196.1 | 217.3 | 122.8 | 194.8 | 180.2
1768 | 1653 | 239.5 | 196.1 | 217.2 | 122.1 | 194.6 | 180.1
1769 | 1654 | 239.2 | 196 | 217.1 | 121.7 | 194.2 | 179.9
1770 | 1655 | 238.7 | 195.9 | 216.9 | 122.2 | 194 | 179.8
1771 | 1656 | 238.2 | 195.8 | 216.8 | 121.8 | 193.6 | 179.7
1772 | 1657 | 237.7 | 195.7 | 216.7 | 121.1 | 193.4 | 179.5
1773 | 1658 | 237.4 | 195.5 | 216.6 | 121.2 | 193.2 | 179.3
1774 | 1659 | 237.1 | 195.3 | 216.5 | 120.9 | 192.9 | 179.2
1775 | 1660 | 236.8 | 194.9 | 216.4 | 120.5 | 193 | 179
1776 | 1661 | 236.4 | 194.7 | 216.3 | 120.8 | 192.5 | 178.8
1777 | 1662 | 236.2 | 194.4 | 216.1 | 121 | 192.4 | 178.6
1778 | 1663 | 235.9 | 194.2 | 216 | 121.5 | 192.5 | 178.5
1779 | 1664 | 235.6 | 194.1 | 215.9 | 121.7 | 192.5 | 178.4
1780 | 1665 | 235.2 | 193.8 | 215.8 | 121.5 | 192.1 | 178.3
1781 | 1666 | 234.9 | 193.6 | 215.7 | 121.1 | 191.8 | 178.2
1782 | 1667 | 234.6 | 193.4 | 215.6 | 121 | 191.7 | 178.1
1783 | 1668 | 234.2 | 193.2 | 215.4 | 120.9 | 191.1 | 177.9
1784 | 1669 | 233.9 | 193 | 215.3 | 120.6 | 191.1 | 177.8
1785 | 1670 | 233.6 | 192.8 | 215.2 | 120.6 | 190.9 | 177.6
1786 | 1671 | 233.2 | 192.6 | 215.1 | 120.4 | 190.5 | 177.5
1787 | 1672 | 232.9 | 192.3 | 215 | 120.4 | 190.6 | 177.3
1788 | 1673 | 232.5 | 192.1 | 214.9 | 120.1 | 190.5 | 177.2
1789 | 1674 | 232.2 | 192 | 214.7 | 119.7 | 190.4 | 177
1790 | 1675 | 231.9 | 191.9 | 214.6 | 119.2 | 190.4 | 176.9
1791 | 1676 | 231.5 | 191.8 | 214.5 | 118.7 | 190.3 | 176.7
1792 | 1677 | 231.2 | 191.7 | 214.4 | 118.7 | 189.9 | 176.6
1793 | 1678 | 230.8 | 191.5 | 214.3 | 118.7 | 189.7 | 176.5
1794 | 1679 | 230.6 | 191.3 | 214.1 | 118.6 | 189.7 | 176.4
1795 | 1680 | 230.3 | 191.1 | 214 | 118 | 189.6 | 176.3
1796 | 1681 | 230 | 190.8 | 213.9 | 117.6 | 189.4 | 176.2
1797 | 1682 | 229.7 | 190.5 | 213.8 | 117.1 | 189.1 | 176.1
1798 | 1683 | 229.3 | 190.2 | 213.6 | 116.6 | 188.9 | 176
1799 | 1684 | 228.8 | 189.9 | 213.5 | 116.5 | 188.7 | 175.8
1800 | 1685 | 228.5 | 189.5 | 213.4 | 116.5 | 188.4 | 175.7
1801 | 1686 | 228.2 | 189.1 | 213.3 | 116.4 | 188.5 | 175.6
1802 | 1687 | 227.9 | 188.7 | 213.2 | 116.8 | 188.4 | 175.5
1803 | 1688 | 227.7 | 188.5 | 213 | 117 | 188.4 | 175.4
1804 | 1689 | 227.4 | 188.2 | 212.9 | 117.1 | 188.3 | 175.2
1805 | 1690 | 227.1 | 188 | 212.8 | 117.5 | 188.2 | 175.1
1806 | 1691 | 226.7 | 187.9 | 212.6 | 117.4 | 188.1 | 174.9
1807 | 1692 | 226.3 | 187.8 | 212.5 | 117.2 | 187.6 | 174.8
1808 | 1693 | 226 | 187.5 | 212.4 | 117.2 | 187.5 | 174.7
1809 | 1694 | 225.7 | 187.2 | 212.3 | 116.8 | 187.6 | 174.5
1810 | 1695 | 225.5 | 186.9 | 212.1 | 116.1 | 187.6 | 174.4
1811 | 1696 | 225.2 | 186.7 | 212 | 115.6 | 187.5 | 174.3
1812 | 1697 | 224.8 | 186.4 | 211.9 | 115.2 | 187.4 | 174.1
1813 | 1698 | 224.5 | 186.1 | 211.7 | 114.6 | 187.4 | 174
1814 | 1699 | 224.2 | 185.7 | 211.6 | 115 | 187.1 | 173.8
1815 | 1700 | 224 | 185.5 | 211.5 | 115.7 | 186.6 | 173.7
1816 | 1701 | 223.7 | 185.2 | 211.3 | 116.2 | 186.6 | 173.5
1817 | 1702 | 223.4 | 184.9 | 211.2 | 115.9 | 186.4 | 173.4
1818 | 1703 | 223.2 | 184.6 | 211.1 | 115.4 | 186.2 | 173.3
1819 | 1704 | 222.8 | 184.4 | 210.9 | 115.2 | 186.1 | 173.1
1820 | 1705 | 222.4 | 184.2 | 210.8 | 114.8 | 185.9 | 173
1821 | 1706 | 222.2 | 184.1 | 210.7 | 114.9 | 185.8 | 172.8
1822 | 1707 | 221.9 | 183.9 | 210.5 | 115.2 | 185.8 | 172.7
1823 | 1708 | 221.7 | 183.6 | 210.4 | 115.7 | 185.6 | 172.5
1824 | 1709 | 221.4 | 183.2 | 210.3 | 115.9 | 185.4 | 172.4
1825 | 1710 | 221.1 | 182.7 | 210.1 | 116.1 | 185.2 | 172.3
1826 | 1711 | 220.9 | 182 | 210 | 116.3 | 184.9 | 172.2
1827 | 1712 | 220.6 | 181.7 | 209.9 | 115.5 | 184.6 | 172
1828 | 1713 | 220.4 | 181.6 | 209.7 | 114.9 | 184.6 | 171.9
1829 | 1714 | 220.1 | 181.6 | 209.6 | 114.5 | 184.6 | 171.7
1830 | 1715 | 219.7 | 181.5 | 209.4 | 113.9 | 184.4 | 171.6
1831 | 1716 | 219.5 | 181.3 | 209.3 | 113.3 | 184.3 | 171.5
1832 | 1717 | 219.2 | 181 | 209.2 | 112.9 | 184 | 171.4
1833 | 1718 | 218.9 | 180.7 | 209 | 112.6 | 184.1 | 171.3
1834 | 1719 | 218.6 | 180.3 | 208.9 | 112.1 | 183.8 | 171.2
1835 | 1720 | 218.3 | 180.1 | 208.8 | 111.7 | 183.5 | 171
1836 | 1721 | 218 | 179.8 | 208.6 | 111.4 | 183.2 | 170.8
1837 | 1722 | 217.7 | 179.6 | 208.5 | 111.2 | 183 | 170.7
1838 | 1723 | 217.4 | 179.4 | 208.3 | 110.9 | 182.5 | 170.6
1839 | 1724 | 217 | 179.2 | 208.2 | 110.7 | 181.7 | 170.4
1840 | 1725 | 216.7 | 178.9 | 208 | 110.8 | 181.6 | 170.3
1841 | 1726 | 216.4 | 178.7 | 207.9 | 110.9 | 181.6 | 170.1
1842 | 1727 | 216.1 | 178.5 | 207.8 | 110.7 | 181.5 | 170
1843 | 1728 | 215.8 | 178.3 | 207.6 | 110.6 | 181 | 169.8
1844 | 1729 | 215.6 | 178.1 | 207.5 | 110.3 | 180.8 | 169.7
1845 | 1730 | 215.3 | 178 | 207.3 | 110 | 180.6 | 169.5
1846 | 1731 | 215 | 177.9 | 207.2 | 110 | 180.4 | 169.3
1847 | 1732 | 214.7 | 177.8 | 207.1 | 109.6 | 179.5 | 169.2
1848 | 1733 | 214.4 | 177.7 | 206.9 | 109.5 | 179.2 | 169
1849 | 1734 | 214.1 | 177.5 | 206.8 | 109.6 | 179.4 | 168.9
1850 | 1735 | 213.8 | 177.4 | 206.6 | 109.4 | 179.5 | 168.7
1851 | 1736 | 213.5 | 177.3 | 206.5 | 109.2 | 179.5 | 168.5
1852 | 1737 | 213.2 | 177.1 | 206.3 | 109.1 | 179.6 | 168.4
1853 | 1738 | 212.9 | 177 | 206.2 | 109.4 | 179.5 | 168.2
1854 | 1739 | 212.7 | 176.9 | 206.1 | 109.9 | 179.3 | 168.1
1855 | 1740 | 212.4 | 176.7 | 205.9 | 109.9 | 179.3 | 167.9
1856 | 1741 | 212 | 176.4 | 205.8 | 109.9 | 179.1 | 167.8
1857 | 1742 | 211.7 | 176.2 | 205.6 | 109.3 | 179.2 | 167.7
1858 | 1743 | 211.4 | 175.8 | 205.5 | 108.6 | 179.3 | 167.6
1859 | 1744 | 211 | 175.5 | 205.3 | 108 | 179.3 | 167.4
1860 | 1745 | 210.7 | 175.3 | 205.2 | 107.3 | 179.2 | 167.3
1861 | 1746 | 210.2 | 175.1 | 205 | 106.8 | 179.3 | 167.2
1862 | 1747 | 209.9 | 175 | 204.9 | 106.2 | 179.3 | 167.1
1863 | 1748 | 209.6 | 174.7 | 204.7 | 105.6 | 179.2 | 167
1864 | 1749 | 209.3 | 174.5 | 204.6 | 104.7 | 179.3 | 166.8
1865 | 1750 | 209.1 | 174.3 | 204.5 | 104 | 179.1 | 166.7
1866 | 1751 | 208.8 | 174.2 | 204.3 | 103.8 | 179 | 166.5
1867 | 1752 | 208.5 | 174 | 204.2 | 103.5 | 178.9 | 166.4
1868 | 1753 | 208.3 | 173.8 | 204 | 103.3 | 178.8 | 166.2
1869 | 1754 | 208 | 173.6 | 203.9 | 102.8 | 178.6 | 166.1
1870 | 1755 | 207.7 | 173.4 | 203.7 | 102.7 | 178.4 | 165.9
1871 | 1756 | 207.5 | 173.3 | 203.6 | 103 | 178.2 | 165.8
1872 | 1757 | 207.2 | 173.3 | 203.4 | 103.3 | 178.3 | 165.7
1873 | 1758 | 207 | 173.3 | 203.2 | 103.6 | 178.1 | 165.5
1874 | 1759 | 206.8 | 173 | 203.1 | 103.9 | 178 | 165.4
1875 | 1760 | 206.5 | 172.9 | 202.9 | 103.9 | 177.4 | 165.2
1876 | 1761 | 206.2 | 172.7 | 202.8 | 103.7 | 177.3 | 165.1
1877 | 1762 | 206 | 172.3 | 202.6 | 104.2 | 177.1 | 164.9
1878 | 1763 | 205.7 | 171.8 | 202.5 | 104.6 | 177.1 | 164.8
1879 | 1764 | 205.5 | 171.4 | 202.3 | 105.4 | 177.1 | 164.6
1880 | 1765 | 205.3 | 170.8 | 202.2 | 106 | 177 | 164.4
1881 | 1766 | 205 | 170.4 | 202 | 105.9 | 176.9 | 164.3
1882 | 1767 | 204.8 | 170.3 | 201.9 | 105.6 | 176.7 | 164.1
1883 | 1768 | 204.6 | 170.1 | 201.7 | 105.6 | 176.5 | 164
1884 | 1769 | 204.3 | 169.9 | 201.6 | 105.8 | 176.1 | 163.8
1885 | 1770 | 204 | 169.6 | 201.4 | 106 | 176 | 163.7
1886 | 1771 | 203.7 | 169.4 | 201.3 | 105.8 | 175.8 | 163.5
1887 | 1772 | 203.5 | 169.3 | 201.1 | 105.7 | 175.6 | 163.4
1888 | 1773 | 203.2 | 169.2 | 201 | 106.1 | 175.6 | 163.2
1889 | 1774 | 202.9 | 168.9 | 200.8 | 106.3 | 175.4 | 163.1
1890 | 1775 | 202.6 | 168.5 | 200.7 | 106 | 175.3 | 162.9
1891 | 1776 | 202.4 | 168.1 | 200.6 | 106.1 | 175.1 | 162.8
1892 | 1777 | 202.2 | 167.8 | 200.4 | 106.4 | 175 | 162.6
1893 | 1778 | 202 | 167.7 | 200.3 | 106.4 | 174.9 | 162.5
1894 | 1779 | 201.8 | 167.5 | 200.1 | 106.2 | 174.6 | 162.4
1895 | 1780 | 201.5 | 167.4 | 200 | 106.3 | 174.3 | 162.3
1896 | 1781 | 201.3 | 167.3 | 199.8 | 105.9 | 174 | 162.1
1897 | 1782 | 201.1 | 167.3 | 199.7 | 105.6 | 173.9 | 162
1898 | 1783 | 200.9 | 167.3 | 199.5 | 105.6 | 173.8 | 161.8
1899 | 1784 | 200.6 | 167.3 | 199.4 | 105.6 | 173.5 | 161.6
1900 | 1785 | 200.4 | 167.1 | 199.2 | 105.6 | 173.3 | 161.5
1901 | 1786 | 200.1 | 167.1 | 199.1 | 105.6 | 173.2 | 161.3
1902 | 1787 | 199.8 | 167 | 198.9 | 105.1 | 172.9 | 161.2
1903 | 1788 | 199.5 | 166.8 | 198.8 | 104.9 | 172.7 | 161.1
1904 | 1789 | 199.2 | 166.5 | 198.7 | 104.9 | 172.2 | 160.9
1905 | 1790 | 199 | 166.2 | 198.5 | 104.9 | 172 | 160.8
1906 | 1791 | 198.8 | 166.1 | 198.4 | 105 | 171.7 | 160.7
1907 | 1792 | 198.6 | 165.9 | 198.2 | 105.2 | 171.3 | 160.5
1908 | 1793 | 198.4 | 165.8 | 198.1 | 105.1 | 171.4 | 160.4
1909 | 1794 | 198.2 | 165.6 | 197.9 | 104.9 | 171.3 | 160.3
1910 | 1795 | 197.9 | 165.4 | 197.8 | 104.5 | 171.4 | 160.1
1911 | 1796 | 197.6 | 165.4 | 197.7 | 104.5 | 171.2 | 159.9
1912 | 1797 | 197.4 | 165.3 | 197.5 | 104.3 | 171 | 159.7
1913 | 1798 | 197.1 | 165.2 | 197.4 | 104.1 | 170.9 | 159.5
1914 | 1799 | 196.7 | 165.1 | 197.2 | 103.5 | 170.6 | 159.4
1915 | 1800 | 196.4 | 165 | 197.1 | 103.2 | 170.3 | 159.3
1916 | 1801 | 196.2 | 165 | 196.9 | 102.9 | 170.1 | 159.1
1917 | 1802 | 195.9 | 164.9 | 196.8 | 102.8 | 170 | 159
1918 | 1803 | 195.6 | 164.8 | 196.6 | 102.7 | 169.7 | 158.9
1919 | 1804 | 195.4 | 164.6 | 196.5 | 102.3 | 169.7 | 158.7
1920 | 1805 | 195.3 | 164.5 | 196.4 | 102.3 | 169.4 | 158.6
1921 | 1806 | 195.1 | 164.4 | 196.2 | 101.9 | 168.8 | 158.4
1922 | 1807 | 194.8 | 164.3 | 196.1 | 101.5 | 168.4 | 158.3
1923 | 1808 | 194.6 | 164.2 | 195.9 | 101.2 | 168.5 | 158.1
1924 | 1809 | 194.3 | 164.2 | 195.7 | 101 | 168.3 | 158
1925 | 1810 | 194 | 164.1 | 195.6 | 100.7 | 168.4 | 157.9
1926 | 1811 | 193.7 | 163.8 | 195.5 | 100.3 | 167.9 | 157.8
1927 | 1812 | 193.5 | 163.4 | 195.3 | 100.2 | 167.8 | 157.7
1928 | 1813 | 193.3 | 163.1 | 195.2 | 100.1 | 167.7 | 157.6
1929 | 1814 | 193.1 | 162.3 | 196 | 99.5 | 167.6 | 157.4
1930 | 1815 | 192.8 | 161.5 | 196.7 | 99 | 167.7 | 157.3
1931 | 1816 | 192.6 | 161.1 | 196.5 | 98.9 | 167.5 | 157.2
1932 | 1817 | 192.4 | 160.8 | 196.4 | 98.8 | 167.4 | 157.1
1933 | 1818 | 192.2 | 160.6 | 196.2 | 98.5 | 167.3 | 157
1934 | 1819 | 192 | 160.5 | 196.1 | 98.1 | 166.8 | 156.8
1935 | 1820 | 191.8 | 160.6 | 195.9 | 98 | 166.6 | 156.7
1936 | 1821 | 191.6 | 160.6 | 195.8 | 97.9 | 166.8 | 156.5
1937 | 1822 | 191.4 | 160.6 | 195.6 | 97.7 | 166.7 | 156.4
1938 | 1823 | 191.2 | 160.5 | 195.5 | 97.6 | 166.5 | 156.2
1939 | 1824 | 190.9 | 160.3 | 195.3 | 97.2 | 166.3 | 156.1
1940 | 1825 | 190.6 | 160.1 | 195.2 | 96.6 | 165.8 | 155.9
1941 | 1826 | 190.4 | 160.1 | 195 | 96.1 | 165.8 | 155.8
1942 | 1827 | 190.1 | 160.1 | 194.9 | 95.8 | 165.8 | 155.6
1943 | 1828 | 189.9 | 159.9 | 194.7 | 95.6 | 165.8 | 155.5
1944 | 1829 | 189.8 | 159.7 | 194.6 | 95.4 | 165.6 | 155.4
1945 | 1830 | 189.5 | 159.6 | 194.4 | 95.4 | 165.4 | 155.3
1946 | 1831 | 189.3 | 159.5 | 194.3 | 95.2 | 165.2 | 155.2
1947 | 1832 | 189.1 | 159.3 | 194.1 | 95.1 | 164.9 | 155.1
1948 | 1833 | 188.9 | 159.1 | 194 | 95 | 164.7 | 154.9
1949 | 1834 | 188.7 | 159 | 193.8 | 95.1 | 164.5 | 154.8
1950 | 1835 | 188.4 | 158.8 | 193.7 | 94.9 | 164.3 | 154.7
1951 | 1836 | 188.2 | 158.6 | 193.5 | 94.6 | 164.3 | 154.5
1952 | 1837 | 188.1 | 158.3 | 193.4 | 94.4 | 163.9 | 154.4
1953 | 1838 | 187.9 | 158.1 | 193.2 | 94 | 163.6 | 154.2
1954 | 1839 | 187.7 | 158 | 193 | 93.6 | 163.2 | 154.1
1955 | 1840 | 187.5 | 157.9 | 192.9 | 93.3 | 162.8 | 153.9
1956 | 1841 | 187.3 | 157.8 | 192.7 | 93 | 162.6 | 153.8
1957 | 1842 | 187.1 | 157.7 | 192.6 | 93.1 | 162.7 | 153.7
1958 | 1843 | 186.8 | 157.6 | 192.4 | 93.9 | 162.8 | 153.5
1959 | 1844 | 186.4 | 157.6 | 192.3 | 94.6 | 162.9 | 153.4
1960 | 1845 | 186.1 | 157.6 | 192.1 | 94.3 | 163 | 153.3
1961 | 1846 | 185.9 | 157.6 | 191.9 | 93.8 | 163.1 | 153.1
1962 | 1847 | 185.7 | 157.6 | 191.8 | 93.5 | 162.9 | 153
1963 | 1848 | 185.5 | 157.5 | 191.6 | 93.5 | 162.8 | 152.8
1964 | 1849 | 185.3 | 157.4 | 191.5 | 93.4 | 162.8 | 152.7
1965 | 1850 | 185.1 | 157.2 | 191.3 | 93.5 | 162.6 | 152.6
1966 | 1851 | 184.9 | 157.1 | 191.2 | 93.4 | 162.4 | 152.5
1967 | 1852 | 184.6 | 157.1 | 191 | 92.9 | 162.1 | 152.3
1968 | 1853 | 184.3 | 157.1 | 190.8 | 92.5 | 162.1 | 152.2
1969 | 1854 | 184.1 | 157 | 190.7 | 92.3 | 161.9 | 152.1
1970 | 1855 | 183.8 | 156.9 | 190.5 | 92.2 | 161.8 | 152

## C3-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38929.5859 | 1 | 0 | 38929.5859 | 1 | 0 | -101 | 14 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5861 | 1 | 0 | 38929.5861 | 1 | 0 | -84 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5863 | 1 | 0 | 38929.5863 | 1 | 0 | -67.5 | 47.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5865 | 1 | 0 | 38929.5865 | 1 | 0 | -50.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5867 | 1 | 0 | 38929.5867 | 1 | 0 | -33.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5869 | 1 | 0 | 38929.5869 | 1 | 0 | -17 | 98 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.587 | 1 | 0 | 38929.5871 | 1 | 0 | -1.4901e-07 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5872 | 1 | 0 | 38929.5873 | 1 | 0 | 16.5 | 131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5874 | 1 | 0 | 38929.5875 | 1 | 0 | 33.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5876 | 1 | 0 | 38929.5877 | 1 | 0 | 50.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5878 | 1 | 0 | 38929.5878 | 2 | 0 | 67 | 182 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38929.588 | 1 | 0 | 38929.588 | 1 | 0 | 84 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5882 | 1 | 0 | 38929.5882 | 1 | 0 | 100.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5884 | 1 | 0 | 38929.5884 | 1 | 0 | 117.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5886 | 1 | 0 | 38929.5886 | 1 | 0 | 134.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5888 | 1 | 0 | 38929.5888 | 1 | 0 | 151 | 266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.589 | 1 | 0 | 38929.589 | 1 | 0 | 168 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5892 | 1 | 0 | 38929.5892 | 1 | 0 | 184.5 | 299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5894 | 1 | 0 | 38929.5894 | 1 | 0 | 201.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5896 | 1 | 0 | 38929.5896 | 1 | 0 | 218.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5898 | 1 | 0 | 38929.5898 | 1 | 0 | 235 | 350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.59 | 1 | 0 | 38929.59 | 1 | 0 | 252 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5902 | 1 | 0 | 38929.5902 | 1 | 0 | 268.5 | 383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5904 | 1 | 0 | 38929.5904 | 1 | 0 | 285.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5906 | 1 | 0 | 38929.5906 | 1 | 0 | 302.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5907 | 1 | 0 | 38929.5908 | 1 | 0 | 319 | 434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5909 | 2 | 0 | 38929.591 | 1 | 0 | 336 | 451 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38929.5911 | 1 | 0 | 38929.5911 | 1 | 0 | 352.5 | 467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5913 | 1 | 0 | 38929.5913 | 1 | 0 | 369.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5915 | 1 | 0 | 38929.5915 | 1 | 0 | 386.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5917 | 1 | 0 | 38929.5917 | 1 | 0 | 403 | 518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5919 | 1 | 0 | 38929.5919 | 1 | 0 | 420 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5921 | 1 | 0 | 38929.5921 | 1 | 0 | 436.5 | 551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5923 | 1 | 0 | 38929.5923 | 1 | 0 | 453.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5925 | 1 | 0 | 38929.5925 | 1 | 0 | 470.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5927 | 1 | 0 | 38929.5927 | 1 | 0 | 487 | 602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5929 | 1 | 0 | 38929.5929 | 1 | 0 | 504 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5931 | 1 | 0 | 38929.5931 | 1 | 0 | 520.5 | 635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5933 | 1 | 0 | 38929.5933 | 1 | 0 | 537.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5935 | 1 | 0 | 38929.5935 | 1 | 0 | 554.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5937 | 1 | 0 | 38929.5937 | 1 | 0 | 571 | 686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5939 | 1 | 0 | 38929.5939 | 1 | 0 | 588 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5941 | 1 | 0 | 38929.5941 | 1 | 0 | 604.5 | 719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5942 | 1 | 0 | 38929.5943 | 1 | 0 | 621.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5944 | 1 | 0 | 38929.5945 | 1 | 0 | 638.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5946 | 1 | 0 | 38929.5947 | 1 | 0 | 655 | 770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5948 | 1 | 0 | 38929.5948 | 1 | 0 | 671.5 | 786.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.595 | 1 | 0 | 38929.595 | 1 | 0 | 688.5 | 803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5952 | 1 | 0 | 38929.5952 | 1 | 0 | 705.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5954 | 1 | 0 | 38929.5954 | 1 | 0 | 722 | 837 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5956 | 1 | 0 | 38929.5956 | 1 | 0 | 739 | 854 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5958 | 1 | 0 | 38929.5958 | 1 | 0 | 755.5 | 870.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.596 | 1 | 0 | 38929.596 | 1 | 0 | 772.5 | 887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5962 | 1 | 0 | 38929.5962 | 1 | 0 | 789.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5964 | 1 | 0 | 38929.5964 | 1 | 0 | 806 | 921 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5966 | 1 | 0 | 38929.5966 | 1 | 0 | 823 | 938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5968 | 1 | 0 | 38929.5968 | 1 | 0 | 839.5 | 954.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.597 | 1 | 0 | 38929.597 | 1 | 0 | 856.5 | 971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5972 | 1 | 0 | 38929.5972 | 1 | 0 | 873.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5973 | 1 | 0 | 38929.5974 | 1 | 0 | 890 | 1005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5975 | 1 | 0 | 38929.5976 | 1 | 0 | 907 | 1022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5977 | 1 | 0 | 38929.5978 | 1 | 0 | 923.5 | 1038.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5979 | 1 | 0 | 38929.598 | 1 | 0 | 940.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5981 | 1 | 0 | 38929.5981 | 1 | 0 | 957.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5983 | 1 | 0 | 38929.5983 | 1 | 0 | 974 | 1089 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5985 | 1 | 0 | 38929.5985 | 1 | 0 | 991 | 1106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5987 | 1 | 0 | 38929.5987 | 1 | 0 | 1007.5 | 1122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5989 | 1 | 0 | 38929.5989 | 1 | 0 | 1024.5 | 1139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5991 | 1 | 0 | 38929.5991 | 1 | 0 | 1041.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5993 | 1 | 0 | 38929.5993 | 1 | 0 | 1058 | 1173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5995 | 1 | 0 | 38929.5995 | 1 | 0 | 1075 | 1190 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5997 | 1 | 0 | 38929.5997 | 1 | 0 | 1091.5 | 1206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5999 | 1 | 0 | 38929.5999 | 1 | 0 | 1108.5 | 1223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6001 | 1 | 0 | 38929.6001 | 1 | 0 | 1125.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6003 | 1 | 0 | 38929.6003 | 1 | 0 | 1142 | 1257 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6005 | 1 | 0 | 38929.6005 | 1 | 0 | 1159 | 1274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6007 | 2 | 2 | 38929.6007 | 2 | 1 | 1175.5 | 1290.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 222820172.02 | 211101.9053 | 105401.071
38929.6009 | 2 | 5 | 38929.6009 | 2 | 3 | 1192.5 | 1307.5 | 0.1221 | 0.30525 | 0.1221 | 0.18315 | 0.001221 | 0.0030525 | 0.001221 | 0.0018315 | 0.0018315 | 0.0006105 | 70422.6957 | 212005.1398 | 42100.5417
38929.6011 | 3 | 7 | 38929.6011 | 2 | 4 | 1209.5 | 1324.5 | 0.18315 | 0.42735 | 0.1221 | 0.2442 | 0.0018315 | 0.0042735 | 0.001221 | 0.002442 | 0.002442 | 0.001221 | 52837.7717 | 105952.0466 | 30014.8142
38929.6012 | 3 | 7 | 38929.6013 | 2 | 5 | 1226 | 1341 | 0.18315 | 0.42735 | 0.1221 | 0.30525 | 0.0018315 | 0.0042735 | 0.001221 | 0.0030525 | 0.002442 | 0.0018315 | 52881.5994 | 70589.8109 | 30000.6429
38929.6014 | 351 | 348 | 38929.6015 | 533 | 556 | 1243 | 1358 | 21.4286 | 21.2454 | 32.5397 | 33.9438 | 0.21429 | 0.21245 | 0.3254 | 0.33944 | 0.0018315 | 0.014042 | 79368.4578 | 44618.2846 | 405.4189
38929.6016 | 1066 | 1036 | 38929.6016 | 1189 | 1182 | 1259.5 | 1374.5 | 65.0794 | 63.2479 | 72.5885 | 72.1612 | 0.65079 | 0.63248 | 0.72589 | 0.72161 | 0.018315 | 0.0042735 | 1255.9949 | 1941.4637 | 1.0116
38929.6018 | 1041 | 1012 | 38929.6018 | 1010 | 1052 | 1276.5 | 1391.5 | 63.5531 | 61.7827 | 61.6606 | 64.2247 | 0.63553 | 0.61783 | 0.61661 | 0.64225 | 0.017705 | 0.025641 | 1120.4906 | 1517.8294 | 5.5642
38929.602 | 1089 | 1063 | 38929.602 | 923 | 920 | 1293.5 | 1408.5 | 66.4835 | 64.8962 | 56.3492 | 56.1661 | 0.66484 | 0.64896 | 0.56349 | 0.56166 | 0.015873 | 0.0018315 | 867.1391 | 1154.2833 | 3.3746
38929.6022 | 974 | 944 | 38929.6022 | 1030 | 1002 | 1310 | 1425 | 59.4628 | 57.6313 | 62.8816 | 61.1722 | 0.59463 | 0.57631 | 0.62882 | 0.61172 | 0.018315 | 0.017094 | 4748.5135 | 15698.9916 | 20.5281
38929.6024 | 1102 | 1076 | 38929.6024 | 1186 | 1169 | 1327 | 1442 | 67.2772 | 65.6899 | 72.4054 | 71.3675 | 0.67277 | 0.6569 | 0.72405 | 0.71368 | 0.015873 | 0.010379 | 5517.7203 | 14016.1602 | 5.9963
38929.6026 | 970 | 941 | 38929.6026 | 951 | 918 | 1343.5 | 1458.5 | 59.2186 | 57.4481 | 58.0586 | 56.044 | 0.59219 | 0.57448 | 0.58059 | 0.56044 | 0.017705 | 0.020147 | 17552.8278 | 4184.4326 | 20.9676
38929.6028 | 947 | 918 | 38929.6028 | 991 | 1101 | 1360.5 | 1475.5 | 57.8144 | 56.044 | 60.5006 | 67.2161 | 0.57814 | 0.56044 | 0.60501 | 0.67216 | 0.017705 | 0.067155 | 434.7948 | 383.8161 | 21.4332
38929.603 | 999 | 969 | 38929.603 | 1123 | 1099 | 1377.5 | 1492.5 | 60.989 | 59.1575 | 68.5592 | 67.094 | 0.60989 | 0.59158 | 0.68559 | 0.67094 | 0.018315 | 0.014652 | 589.1922 | 609.1435 | 12.8555
38929.6032 | 1183 | 1165 | 38929.6032 | 989 | 1100 | 1394 | 1509 | 72.2222 | 71.1233 | 60.3785 | 67.1551 | 0.72222 | 0.71123 | 0.60379 | 0.67155 | 0.010989 | 0.067766 | 216.4771 | 283.0308 | 14.9041
38929.6034 | 1033 | 1004 | 38929.6034 | 1185 | 1171 | 1411 | 1526 | 63.0647 | 61.2943 | 72.3443 | 71.4896 | 0.63065 | 0.61294 | 0.72344 | 0.7149 | 0.017705 | 0.008547 | 1348.7556 | 1965.7253 | 7.2052
38929.6036 | 1169 | 1147 | 38929.6036 | 937 | 818 | 1427.5 | 1542.5 | 71.3675 | 70.0244 | 57.2039 | 49.9389 | 0.71368 | 0.70024 | 0.57204 | 0.49939 | 0.013431 | 0.07265 | 155.4326 | 195.9511 | 11.717
38929.6038 | 1125 | 1173 | 38929.6038 | 977 | 876 | 1444.5 | 1559.5 | 68.6813 | 71.6117 | 59.6459 | 53.4799 | 0.68681 | 0.71612 | 0.59646 | 0.5348 | 0.029304 | 0.061661 | 148.3523 | 189.8072 | 10.3283
38929.604 | 946 | 845 | 38929.604 | 1110 | 1168 | 1461.5 | 1576.5 | 57.7534 | 51.5873 | 67.7656 | 71.3065 | 0.57753 | 0.51587 | 0.67766 | 0.71306 | 0.061661 | 0.035409 | 351.0552 | 365.118 | 29.9155
38929.6042 | 1075 | 1003 | 38929.6042 | 960 | 855 | 1478 | 1593 | 65.6288 | 61.2332 | 58.6081 | 52.1978 | 0.65629 | 0.61233 | 0.58608 | 0.52198 | 0.043956 | 0.064103 | 1521.659 | 26508.7003 | 3.4784
38929.6044 | 1034 | 944 | 38929.6044 | 1070 | 1091 | 1495 | 1610 | 63.1258 | 57.6313 | 65.3236 | 66.6056 | 0.63126 | 0.57631 | 0.65324 | 0.66606 | 0.054945 | 0.012821 | 129.0186 | 126.4858 | 7.9878
38929.6045 | 995 | 893 | 38929.6046 | 1073 | 1152 | 1511.5 | 1626.5 | 60.7448 | 54.5177 | 65.5067 | 70.3297 | 0.60745 | 0.54518 | 0.65507 | 0.7033 | 0.062271 | 0.04823 | 377.169 | 459.3051 | 20.6929
38929.6047 | 1164 | 1119 | 38929.6048 | 937 | 896 | 1528.5 | 1643.5 | 71.0623 | 68.315 | 57.2039 | 54.7009 | 0.71062 | 0.68315 | 0.57204 | 0.54701 | 0.027473 | 0.025031 | 1610.9644 | 8044.5404 | 15.0038
38929.6049 | 1023 | 925 | 38929.605 | 1036 | 1129 | 1545.5 | 1660.5 | 62.4542 | 56.4713 | 63.2479 | 68.9255 | 0.62454 | 0.56471 | 0.63248 | 0.68926 | 0.059829 | 0.056777 | 664.0814 | 1398.5586 | 16.6495
38929.6051 | 935 | 1023 | 38929.6052 | 999 | 978 | 1562 | 1677 | 57.0818 | 62.4542 | 60.989 | 59.707 | 0.57082 | 0.62454 | 0.60989 | 0.59707 | 0.053724 | 0.012821 | 407.3687 | 508.5053 | 12.6632
38929.6053 | 1068 | 981 | 38929.6053 | 991 | 1092 | 1579 | 1694 | 65.2015 | 59.8901 | 60.5006 | 66.6667 | 0.65201 | 0.5989 | 0.60501 | 0.66667 | 0.053114 | 0.061661 | 6912.1753 | 1364.7469 | 6.0805
38929.6055 | 1109 | 1039 | 38929.6055 | 1063 | 973 | 1595.5 | 1710.5 | 67.7045 | 63.431 | 64.8962 | 59.4017 | 0.67705 | 0.63431 | 0.64896 | 0.59402 | 0.042735 | 0.054945 | 216.3774 | 263.6966 | 2.441
38929.6057 | 963 | 841 | 38929.6057 | 1189 | 1154 | 1612.5 | 1727.5 | 58.7912 | 51.3431 | 72.5885 | 70.4518 | 0.58791 | 0.51343 | 0.72589 | 0.70452 | 0.074481 | 0.021368 | 110.6033 | 91.6351 | 17.5702
38929.6059 | 1198 | 1180 | 38929.6059 | 1058 | 968 | 1629.5 | 1744.5 | 73.138 | 72.0391 | 64.591 | 59.0965 | 0.73138 | 0.72039 | 0.64591 | 0.59096 | 0.010989 | 0.054945 | 202.8166 | 272.4189 | 16.4262
38929.6061 | 1154 | 1106 | 38929.6061 | 1095 | 1168 | 1646 | 1761 | 70.4518 | 67.5214 | 66.8498 | 71.3065 | 0.70452 | 0.67521 | 0.6685 | 0.71306 | 0.029304 | 0.044567 | 989.8851 | 2262.5936 | 12.7268
38929.6063 | 1054 | 978 | 38929.6063 | 1135 | 1084 | 1663 | 1778 | 64.3468 | 59.707 | 69.2918 | 66.1783 | 0.64347 | 0.59707 | 0.69292 | 0.66178 | 0.046398 | 0.031136 | 99.8272 | 99.3041 | 4.1277
38929.6065 | 936 | 909 | 38929.6065 | 967 | 870 | 1679.5 | 1794.5 | 57.1429 | 55.4945 | 59.0354 | 53.1136 | 0.57143 | 0.55495 | 0.59035 | 0.53114 | 0.016484 | 0.059219 | 975.1074 | 970.048 | 26.7297
38929.6067 | 1181 | 1148 | 38929.6067 | 1101 | 1144 | 1696.5 | 1811.5 | 72.1001 | 70.0855 | 67.2161 | 69.8413 | 0.721 | 0.70085 | 0.67216 | 0.69841 | 0.020147 | 0.026252 | 2317.7882 | 15918.7701 | 18.6961
38929.6069 | 1015 | 928 | 38929.6069 | 979 | 968 | 1713.5 | 1828.5 | 61.9658 | 56.6545 | 59.768 | 59.0965 | 0.61966 | 0.56654 | 0.59768 | 0.59096 | 0.053114 | 0.0067155 | 392.1603 | 480.8474 | 15.1669
38929.6071 | 923 | 969 | 38929.6071 | 1006 | 1108 | 1730 | 1845 | 56.3492 | 59.1575 | 61.4164 | 67.6435 | 0.56349 | 0.59158 | 0.61416 | 0.67643 | 0.028083 | 0.062271 | 508.6581 | 515.5549 | 19.1036
38929.6073 | 1022 | 938 | 38929.6073 | 1054 | 1075 | 1747 | 1862 | 62.3932 | 57.265 | 64.3468 | 65.6288 | 0.62393 | 0.57265 | 0.64347 | 0.65629 | 0.051282 | 0.012821 | 212.3342 | 218.2299 | 11.1871
38929.6075 | 931 | 868 | 38929.6075 | 947 | 852 | 1763.5 | 1878.5 | 56.8376 | 52.9915 | 57.8144 | 52.0147 | 0.56838 | 0.52991 | 0.57814 | 0.52015 | 0.038462 | 0.057998 | 7096.3383 | 1872.9808 | 34.3438
38929.6077 | 1177 | 1190 | 38929.6077 | 936 | 855 | 1780.5 | 1895.5 | 71.8559 | 72.6496 | 57.1429 | 52.1978 | 0.71856 | 0.7265 | 0.57143 | 0.52198 | 0.0079365 | 0.049451 | 103.9161 | 134.0474 | 12.2238
38929.6079 | 1095 | 1038 | 38929.6079 | 1154 | 1192 | 1797.5 | 1912.5 | 66.8498 | 63.37 | 70.4518 | 72.7717 | 0.6685 | 0.6337 | 0.70452 | 0.72772 | 0.034799 | 0.023199 | 1714.7967 | 43856.6104 | 1.9205
38929.608 | 1061 | 996 | 38929.6081 | 1143 | 1096 | 1814 | 1929 | 64.7741 | 60.8059 | 69.7802 | 66.9109 | 0.64774 | 0.60806 | 0.6978 | 0.66911 | 0.039683 | 0.028694 | 438.0457 | 568.616 | 4.7833
38929.6082 | 1178 | 1152 | 38929.6083 | 1183 | 1139 | 1830.5 | 1945.5 | 71.917 | 70.3297 | 72.2222 | 69.536 | 0.71917 | 0.7033 | 0.72222 | 0.69536 | 0.015873 | 0.026862 | 1669.4937 | 3839.2063 | 18.3569
38929.6084 | 1149 | 1104 | 38929.6084 | 938 | 860 | 1847.5 | 1962.5 | 70.1465 | 67.3993 | 57.265 | 52.5031 | 0.70147 | 0.67399 | 0.57265 | 0.52503 | 0.027473 | 0.047619 | 551.5171 | 850.5772 | 11.3455

## C2-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38929.5859 | 1 | 0 | 38929.5859 | 1 | 0 | -103.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.586 | 1 | 0 | 38929.5861 | 1 | 0 | -87 | 28 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5862 | 1 | 0 | 38929.5863 | 1 | 0 | -70 | 45 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5864 | 1 | 0 | 38929.5864 | 1 | 0 | -53.5 | 61.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5866 | 1 | 0 | 38929.5866 | 1 | 0 | -36.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5868 | 1 | 0 | 38929.5868 | 1 | 0 | -19.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.587 | 1 | 0 | 38929.587 | 1 | 0 | -3 | 112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5872 | 1 | 0 | 38929.5872 | 1 | 0 | 14 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5874 | 1 | 0 | 38929.5874 | 1 | 0 | 30.5 | 145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5876 | 1 | 0 | 38929.5876 | 1 | 0 | 47.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5878 | 1 | 0 | 38929.5878 | 1 | 0 | 64.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.588 | 1 | 0 | 38929.588 | 1 | 0 | 81 | 196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5882 | 1 | 0 | 38929.5882 | 1 | 0 | 98 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5884 | 1 | 0 | 38929.5884 | 1 | 0 | 114.5 | 229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5886 | 1 | 0 | 38929.5886 | 1 | 0 | 131.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5888 | 1 | 0 | 38929.5888 | 1 | 0 | 148.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.589 | 1 | 0 | 38929.589 | 1 | 0 | 165 | 280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5892 | 1 | 0 | 38929.5892 | 1 | 0 | 182 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5894 | 1 | 0 | 38929.5894 | 1 | 0 | 198.5 | 313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5895 | 1 | 0 | 38929.5896 | 1 | 0 | 215.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5897 | 1 | 0 | 38929.5898 | 1 | 0 | 232.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5899 | 1 | 0 | 38929.59 | 1 | 0 | 249 | 364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5901 | 1 | 0 | 38929.5902 | 1 | 0 | 266 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5903 | 1 | 0 | 38929.5903 | 1 | 0 | 282.5 | 397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5905 | 1 | 0 | 38929.5905 | 1 | 0 | 299.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5907 | 1 | 0 | 38929.5907 | 1 | 0 | 316.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5909 | 1 | 0 | 38929.5909 | 1 | 0 | 333 | 448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5911 | 1 | 0 | 38929.5911 | 1 | 0 | 350 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5913 | 1 | 0 | 38929.5913 | 1 | 0 | 366.5 | 481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5915 | 1 | 0 | 38929.5915 | 1 | 0 | 383.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5917 | 1 | 0 | 38929.5917 | 1 | 0 | 400.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5919 | 1 | 0 | 38929.5919 | 1 | 0 | 417 | 532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5921 | 1 | 0 | 38929.5921 | 1 | 0 | 434 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5923 | 1 | 0 | 38929.5923 | 1 | 0 | 450.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5925 | 1 | 0 | 38929.5925 | 1 | 0 | 467.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5927 | 1 | 0 | 38929.5927 | 1 | 0 | 484.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5928 | 1 | 0 | 38929.5929 | 1 | 0 | 501 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.593 | 1 | 0 | 38929.5931 | 1 | 0 | 518 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5932 | 1 | 0 | 38929.5933 | 1 | 0 | 534.5 | 649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5934 | 1 | 0 | 38929.5934 | 1 | 0 | 551.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5936 | 1 | 0 | 38929.5936 | 1 | 0 | 568.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5938 | 1 | 0 | 38929.5938 | 1 | 0 | 585 | 700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.594 | 1 | 0 | 38929.594 | 1 | 0 | 602 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5942 | 1 | 0 | 38929.5942 | 1 | 0 | 618.5 | 733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5944 | 1 | 0 | 38929.5944 | 1 | 0 | 635.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5946 | 1 | 0 | 38929.5946 | 1 | 0 | 652.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5948 | 1 | 0 | 38929.5948 | 1 | 0 | 669 | 784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.595 | 1 | 0 | 38929.595 | 1 | 0 | 686 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5952 | 1 | 0 | 38929.5952 | 1 | 0 | 702.5 | 817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5954 | 1 | 0 | 38929.5954 | 1 | 0 | 719.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5956 | 1 | 0 | 38929.5956 | 1 | 0 | 736 | 851 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5958 | 1 | 0 | 38929.5958 | 1 | 0 | 753 | 868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.596 | 1 | 0 | 38929.596 | 1 | 0 | 770 | 885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5962 | 1 | 0 | 38929.5962 | 1 | 0 | 786.5 | 901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5964 | 1 | 0 | 38929.5964 | 1 | 0 | 803.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5965 | 1 | 0 | 38929.5966 | 1 | 0 | 820 | 935 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5967 | 1 | 0 | 38929.5968 | 1 | 0 | 837 | 952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5969 | 1 | 0 | 38929.597 | 1 | 0 | 854 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5971 | 1 | 0 | 38929.5971 | 1 | 0 | 870.5 | 985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5973 | 1 | 0 | 38929.5973 | 1 | 0 | 887.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5975 | 1 | 0 | 38929.5975 | 1 | 0 | 904.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5977 | 1 | 0 | 38929.5977 | 1 | 0 | 921 | 1036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5979 | 1 | 0 | 38929.5979 | 1 | 0 | 938 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5981 | 1 | 0 | 38929.5981 | 1 | 0 | 954.5 | 1069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5983 | 1 | 0 | 38929.5983 | 1 | 0 | 971.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5985 | 1 | 0 | 38929.5985 | 1 | 0 | 988 | 1103 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5987 | 1 | 0 | 38929.5987 | 1 | 0 | 1005 | 1120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5989 | 1 | 0 | 38929.5989 | 1 | 0 | 1021.5 | 1136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5991 | 1 | 0 | 38929.5991 | 1 | 0 | 1038.5 | 1153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5993 | 1 | 0 | 38929.5993 | 1 | 0 | 1055.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5995 | 1 | 0 | 38929.5995 | 1 | 0 | 1072 | 1187 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5997 | 1 | 0 | 38929.5997 | 1 | 0 | 1089 | 1204 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5998 | 1 | 0 | 38929.5999 | 1 | 0 | 1105.5 | 1220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6 | 1 | 0 | 38929.6001 | 1 | 0 | 1122.5 | 1237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6002 | 1 | 0 | 38929.6003 | 1 | 0 | 1139.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6004 | 1 | 0 | 38929.6005 | 1 | 0 | 1156 | 1271 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6006 | 1157 | 1187 | 38929.6006 | 3 | 7 | 1173 | 1288 | 70.6349 | 72.4664 | 0.18315 | 0.42735 | 0.70635 | 0.72466 | 0.0018315 | 0.0042735 | 0.018315 | 0.002442 | 3430.9532 | 55585.7181 | 19.4242
38929.6008 | 1156 | 1133 | 38929.6008 | 3 | 11 | 1189.5 | 1304.5 | 70.5739 | 69.1697 | 0.18315 | 0.67155 | 0.70574 | 0.6917 | 0.0018315 | 0.0067155 | 0.014042 | 0.004884 | 5084.9971 | 27108.2665 | 15.4751
38929.601 | 1030 | 995 | 38929.601 | 3 | 12 | 1206.5 | 1321.5 | 62.8816 | 60.7448 | 0.18315 | 0.7326 | 0.62882 | 0.60745 | 0.0018315 | 0.007326 | 0.021368 | 0.0054945 | 3502.9345 | 24372.3597 | 8.8101
38929.6012 | 1163 | 1142 | 38929.6012 | 3 | 13 | 1223.5 | 1338.5 | 71.0012 | 69.7192 | 0.18315 | 0.79365 | 0.71001 | 0.69719 | 0.0018315 | 0.0079365 | 0.012821 | 0.006105 | 6049.5281 | 21563.5859 | 16.7333
38929.6014 | 1158 | 1188 | 38929.6014 | 208 | 172 | 1240 | 1355 | 70.696 | 72.5275 | 12.6984 | 10.5006 | 0.70696 | 0.72527 | 0.12698 | 0.10501 | 0.018315 | 0.021978 | 11228.8195 | 5526.8871 | 19.2626
38929.6016 | 1042 | 1091 | 38929.6016 | 970 | 936 | 1257 | 1372 | 63.6142 | 66.6056 | 59.2186 | 57.1429 | 0.63614 | 0.66606 | 0.59219 | 0.57143 | 0.029915 | 0.020757 | 1073.3927 | 2148.5279 | 1.7499
38929.6018 | 1162 | 1141 | 38929.6018 | 1034 | 1079 | 1273.5 | 1388.5 | 70.9402 | 69.6581 | 63.1258 | 65.873 | 0.7094 | 0.69658 | 0.63126 | 0.65873 | 0.012821 | 0.027473 | 714.5381 | 1017.8796 | 15.1609
38929.602 | 1085 | 1142 | 38929.602 | 1070 | 1042 | 1290.5 | 1405.5 | 66.2393 | 69.7192 | 65.3236 | 63.6142 | 0.66239 | 0.69719 | 0.65324 | 0.63614 | 0.034799 | 0.017094 | 428.4393 | 624.2303 | 8.6026
38929.6022 | 1004 | 973 | 38929.6022 | 1183 | 1090 | 1307.5 | 1422.5 | 61.2943 | 59.4017 | 72.2222 | 66.5446 | 0.61294 | 0.59402 | 0.72222 | 0.66545 | 0.018926 | 0.056777 | 47.2916 | 42.0472 | 4.138
38929.6024 | 917 | 966 | 38929.6024 | 931 | 901 | 1324 | 1439 | 55.9829 | 58.9744 | 56.8376 | 55.0061 | 0.55983 | 0.58974 | 0.56838 | 0.55006 | 0.029915 | 0.018315 | 1877.5837 | 6571.4474 | 23.4547
38929.6026 | 1046 | 1138 | 38929.6026 | 1187 | 1184 | 1341 | 1456 | 63.8584 | 69.475 | 72.4664 | 72.2833 | 0.63858 | 0.69475 | 0.72466 | 0.72283 | 0.056166 | 0.0018315 | 439.3627 | 754.3604 | 5.5072
38929.6028 | 1163 | 1167 | 38929.6028 | 1008 | 979 | 1357.5 | 1472.5 | 71.0012 | 71.2454 | 61.5385 | 59.768 | 0.71001 | 0.71245 | 0.61538 | 0.59768 | 0.002442 | 0.017705 | 315.067 | 392.2299 | 14.8157
38929.603 | 1188 | 1184 | 38929.603 | 937 | 905 | 1374.5 | 1489.5 | 72.5275 | 72.2833 | 57.2039 | 55.2503 | 0.72527 | 0.72283 | 0.57204 | 0.5525 | 0.002442 | 0.019536 | 49.1865 | 63.0916 | 8.4616
38929.6032 | 1182 | 1186 | 38929.6032 | 1061 | 1034 | 1391.5 | 1506.5 | 72.1612 | 72.4054 | 64.7741 | 63.1258 | 0.72161 | 0.72405 | 0.64774 | 0.63126 | 0.002442 | 0.016484 | 887.5856 | 1175.4964 | 19.8136
38929.6033 | 928 | 912 | 38929.6034 | 977 | 932 | 1408 | 1523 | 56.6545 | 55.6777 | 59.6459 | 56.8987 | 0.56654 | 0.55678 | 0.59646 | 0.56899 | 0.009768 | 0.027473 | 2170.3524 | 2362.6728 | 28.7208
38929.6035 | 1030 | 1077 | 38929.6036 | 1063 | 1037 | 1425 | 1540 | 62.8816 | 65.7509 | 64.8962 | 63.3089 | 0.62882 | 0.65751 | 0.64896 | 0.63309 | 0.028694 | 0.015873 | 95.2912 | 98.8493 | 0.27786
38929.6037 | 918 | 871 | 38929.6038 | 1187 | 1157 | 1441.5 | 1556.5 | 56.044 | 53.1746 | 72.4664 | 70.6349 | 0.56044 | 0.53175 | 0.72466 | 0.70635 | 0.028694 | 0.018315 | 568.4227 | 533.5885 | 31.3295
38929.6039 | 1021 | 936 | 38929.6039 | 928 | 853 | 1458.5 | 1573.5 | 62.3321 | 57.1429 | 56.6545 | 52.0757 | 0.62332 | 0.57143 | 0.56654 | 0.52076 | 0.051893 | 0.045788 | 1623.6853 | 5274.9166 | 16.3587
38929.6041 | 1081 | 1009 | 38929.6041 | 952 | 845 | 1475.5 | 1590.5 | 65.9951 | 61.5995 | 58.1197 | 51.5873 | 0.65995 | 0.616 | 0.5812 | 0.51587 | 0.043956 | 0.065324 | 1418.1252 | 130437.8113 | 2.2797
38929.6043 | 1023 | 929 | 38929.6043 | 956 | 848 | 1492 | 1607 | 62.4542 | 56.7155 | 58.3639 | 51.7705 | 0.62454 | 0.56716 | 0.58364 | 0.5177 | 0.057387 | 0.065934 | 5616.8685 | 1245.4116 | 16.0443
38929.6045 | 1137 | 1080 | 38929.6045 | 1141 | 1184 | 1509 | 1624 | 69.4139 | 65.9341 | 69.6581 | 72.2833 | 0.69414 | 0.65934 | 0.69658 | 0.72283 | 0.034799 | 0.026252 | 3681.0249 | 3542.714 | 9.3635
38929.6047 | 986 | 879 | 38929.6047 | 1131 | 1067 | 1525.5 | 1640.5 | 60.1954 | 53.663 | 69.0476 | 65.1404 | 0.60195 | 0.53663 | 0.69048 | 0.6514 | 0.065324 | 0.039072 | 345.8884 | 401.6753 | 22.5918
38929.6049 | 1136 | 1073 | 38929.6049 | 1062 | 972 | 1542.5 | 1657.5 | 69.3529 | 65.5067 | 64.8352 | 59.3407 | 0.69353 | 0.65507 | 0.64835 | 0.59341 | 0.038462 | 0.054945 | 52.9997 | 60.2658 | 3.3637
38929.6051 | 1171 | 1125 | 38929.6051 | 1154 | 1188 | 1559.5 | 1674.5 | 71.4896 | 68.6813 | 70.4518 | 72.5275 | 0.7149 | 0.68681 | 0.70452 | 0.72527 | 0.028083 | 0.020757 | 7384.3118 | 3384.1757 | 15.7981
38929.6053 | 1193 | 1156 | 38929.6053 | 1155 | 1101 | 1576 | 1691 | 72.8327 | 70.5739 | 70.5128 | 67.2161 | 0.72833 | 0.70574 | 0.70513 | 0.67216 | 0.022589 | 0.032967 | 1450.6975 | 4375.6143 | 19.9574
38929.6055 | 1173 | 1127 | 38929.6055 | 1111 | 1037 | 1593 | 1708 | 71.6117 | 68.8034 | 67.8266 | 63.3089 | 0.71612 | 0.68803 | 0.67827 | 0.63309 | 0.028083 | 0.045177 | 607.9069 | 1037.4454 | 15.1323
38929.6057 | 1158 | 1105 | 38929.6057 | 1198 | 936 | 1609.5 | 1724.5 | 70.696 | 67.4603 | 73.138 | 57.1429 | 0.70696 | 0.6746 | 0.73138 | 0.57143 | 0.032357 | 0.15995 | 66.5595 | 79.966 | 6.031
38929.6059 | 1117 | 1154 | 38929.6059 | 1096 | 1019 | 1626.5 | 1741.5 | 68.1929 | 70.4518 | 66.9109 | 62.21 | 0.68193 | 0.70452 | 0.66911 | 0.6221 | 0.022589 | 0.047009 | 318.0934 | 417.9315 | 11.0466
38929.6061 | 1190 | 1153 | 38929.6061 | 933 | 849 | 1643.5 | 1758.5 | 72.6496 | 70.3907 | 56.9597 | 51.8315 | 0.7265 | 0.70391 | 0.5696 | 0.51832 | 0.022589 | 0.051282 | 207.3368 | 282.4741 | 14.7312
38929.6063 | 1031 | 952 | 38929.6063 | 1159 | 1115 | 1660 | 1775 | 62.9426 | 58.1197 | 70.757 | 68.0708 | 0.62943 | 0.5812 | 0.70757 | 0.68071 | 0.04823 | 0.026862 | 87.251 | 81.9896 | 6.153
38929.6065 | 1171 | 1135 | 38929.6065 | 1124 | 1181 | 1677 | 1792 | 71.4896 | 69.2918 | 68.6203 | 72.1001 | 0.7149 | 0.69292 | 0.6862 | 0.721 | 0.021978 | 0.034799 | 1405.1373 | 3656.4385 | 16.55
38929.6067 | 1196 | 1178 | 38929.6067 | 1020 | 938 | 1693.5 | 1808.5 | 73.0159 | 71.917 | 62.2711 | 57.265 | 0.73016 | 0.71917 | 0.62271 | 0.57265 | 0.010989 | 0.050061 | 133.4381 | 176.0245 | 14.1282
38929.6069 | 992 | 988 | 38929.6069 | 1030 | 1041 | 1710.5 | 1825.5 | 60.5617 | 60.3175 | 62.8816 | 63.5531 | 0.60562 | 0.60317 | 0.62882 | 0.63553 | 0.002442 | 0.0067155 | 2839.372 | 2784.5681 | 12.9968
38929.607 | 1013 | 924 | 38929.6071 | 1064 | 1090 | 1727.5 | 1842.5 | 61.8437 | 56.4103 | 64.9573 | 66.5446 | 0.61844 | 0.5641 | 0.64957 | 0.66545 | 0.054335 | 0.015873 | 211.6896 | 214.5653 | 12.9939
38929.6072 | 1026 | 1038 | 38929.6073 | 1184 | 1150 | 1744 | 1859 | 62.6374 | 63.37 | 72.2833 | 70.2076 | 0.62637 | 0.6337 | 0.72283 | 0.70208 | 0.007326 | 0.020757 | 761.4252 | 793.8133 | 4.1942
38929.6074 | 1031 | 1042 | 38929.6075 | 1019 | 937 | 1761 | 1876 | 62.9426 | 63.6142 | 62.21 | 57.2039 | 0.62943 | 0.63614 | 0.6221 | 0.57204 | 0.0067155 | 0.050061 | 282.5203 | 280.1162 | 2.8303
38929.6076 | 1106 | 1048 | 38929.6076 | 1181 | 1152 | 1777.5 | 1892.5 | 67.5214 | 63.9805 | 72.1001 | 70.3297 | 0.67521 | 0.6398 | 0.721 | 0.7033 | 0.035409 | 0.017705 | 1135.5648 | 3415.8947 | 3.7991
38929.6078 | 1054 | 985 | 38929.6078 | 1168 | 1132 | 1794.5 | 1909.5 | 64.3468 | 60.1343 | 71.3065 | 69.1087 | 0.64347 | 0.60134 | 0.71306 | 0.69109 | 0.042125 | 0.021978 | 383.996 | 476.3302 | 6.2108
38929.608 | 1055 | 1141 | 38929.608 | 950 | 860 | 1811.5 | 1926.5 | 64.4078 | 69.6581 | 57.9976 | 52.5031 | 0.64408 | 0.69658 | 0.57998 | 0.52503 | 0.052503 | 0.054945 | 9333.7935 | 1528.1667 | 6.8259
38929.6082 | 1179 | 1189 | 38929.6082 | 954 | 871 | 1828 | 1943 | 71.978 | 72.5885 | 58.2418 | 53.1746 | 0.71978 | 0.72589 | 0.58242 | 0.53175 | 0.006105 | 0.050672 | 53.8813 | 68.9884 | 8.7547
38929.6084 | 1128 | 1175 | 38929.6084 | 986 | 1091 | 1845 | 1960 | 68.8645 | 71.7338 | 60.1954 | 66.6056 | 0.68864 | 0.71734 | 0.60195 | 0.66606 | 0.028694 | 0.064103 | 243.9992 | 329.4102 | 12.4032

## C2-3
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38929.5858 | 1 | 0 | 38929.5858 | 1 | 0 | -106.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.586 | 1 | 0 | 38929.586 | 1 | 0 | -89.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5862 | 1 | 0 | 38929.5862 | 1 | 0 | -73 | 42 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5864 | 1 | 0 | 38929.5864 | 1 | 0 | -56 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5866 | 1 | 0 | 38929.5866 | 1 | 0 | -39.5 | 75.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5868 | 1 | 0 | 38929.5868 | 1 | 0 | -22.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.587 | 1 | 0 | 38929.587 | 1 | 0 | -5.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5872 | 1 | 0 | 38929.5872 | 1 | 0 | 11 | 126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5874 | 1 | 0 | 38929.5874 | 1 | 0 | 28 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5876 | 1 | 0 | 38929.5876 | 1 | 0 | 44.5 | 159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5878 | 1 | 0 | 38929.5878 | 1 | 0 | 61.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.588 | 1 | 0 | 38929.588 | 1 | 0 | 78.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5881 | 1 | 0 | 38929.5882 | 1 | 0 | 95 | 210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5883 | 1 | 0 | 38929.5884 | 1 | 0 | 112 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5885 | 1 | 0 | 38929.5886 | 1 | 0 | 128.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5887 | 1 | 1 | 38929.5888 | 1 | 0 | 145.5 | 260.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38929.5889 | 1 | 0 | 38929.5889 | 1 | 0 | 162.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5891 | 1 | 0 | 38929.5891 | 1 | 0 | 179 | 294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38929.5893 | 1 | 0 | 197 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5895 | 1 | 0 | 38929.5895 | 1 | 0 | 212.5 | 327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5897 | 1 | 0 | 38929.5897 | 1 | 0 | 229.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5899 | 1 | 0 | 38929.5899 | 1 | 0 | 246.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5901 | 1 | 0 | 38929.5901 | 1 | 0 | 263 | 378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5903 | 1 | 0 | 38929.5903 | 1 | 0 | 280 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5905 | 1 | 0 | 38929.5905 | 1 | 0 | 296.5 | 411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5907 | 1 | 0 | 38929.5907 | 1 | 0 | 313.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5909 | 1 | 0 | 38929.5909 | 1 | 0 | 330.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5911 | 1 | 0 | 38929.5911 | 1 | 0 | 347 | 462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5913 | 1 | 0 | 38929.5913 | 1 | 0 | 364 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5915 | 1 | 0 | 38929.5915 | 1 | 0 | 380.5 | 495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5917 | 1 | 0 | 38929.5917 | 1 | 0 | 397.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5919 | 1 | 0 | 38929.5919 | 1 | 0 | 414.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.592 | 1 | 0 | 38929.5921 | 1 | 0 | 431 | 546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5922 | 1 | 0 | 38929.5923 | 1 | 0 | 448 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5924 | 1 | 0 | 38929.5924 | 1 | 0 | 464.5 | 579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5926 | 1 | 0 | 38929.5926 | 1 | 0 | 481.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5928 | 1 | 0 | 38929.5928 | 1 | 0 | 498.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.593 | 1 | 0 | 38929.593 | 1 | 0 | 515 | 630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5932 | 1 | 0 | 38929.5932 | 1 | 0 | 532 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5934 | 1 | 0 | 38929.5934 | 1 | 0 | 548.5 | 663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5936 | 1 | 0 | 38929.5936 | 1 | 0 | 565.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5938 | 1 | 0 | 38929.5938 | 1 | 0 | 582.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.594 | 1 | 0 | 38929.594 | 1 | 0 | 599 | 714 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5942 | 1 | 0 | 38929.5942 | 1 | 0 | 616 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5944 | 1 | 0 | 38929.5944 | 1 | 0 | 632.5 | 747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5946 | 1 | 0 | 38929.5946 | 1 | 0 | 649.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5948 | 1 | 0 | 38929.5948 | 1 | 0 | 666.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.595 | 1 | 0 | 38929.595 | 1 | 0 | 683 | 798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5952 | 1 | 0 | 38929.5952 | 1 | 0 | 700 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5953 | 1 | 0 | 38929.5954 | 1 | 0 | 716.5 | 831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5955 | 1 | 0 | 38929.5956 | 1 | 0 | 733.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5957 | 1 | 0 | 38929.5958 | 1 | 0 | 750 | 865 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5959 | 1 | 0 | 38929.5959 | 1 | 0 | 767 | 882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5961 | 1 | 0 | 38929.5961 | 1 | 0 | 784 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5963 | 1 | 0 | 38929.5963 | 1 | 0 | 800.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5965 | 1 | 0 | 38929.5965 | 1 | 0 | 817.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5967 | 1 | 0 | 38929.5967 | 1 | 0 | 834 | 949 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5969 | 1 | 0 | 38929.5969 | 1 | 0 | 851 | 966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5971 | 1 | 0 | 38929.5971 | 1 | 0 | 868 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5973 | 2 | 1 | 38929.5973 | 1 | 0 | 884.5 | 999.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38929.5975 | 1 | 0 | 38929.5975 | 1 | 0 | 901.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5977 | 1 | 0 | 38929.5977 | 1 | 0 | 918 | 1033 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5979 | 1 | 0 | 38929.5979 | 1 | 0 | 935 | 1050 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5981 | 1 | 0 | 38929.5981 | 1 | 0 | 952 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5983 | 1 | 0 | 38929.5983 | 2 | 0 | 968.5 | 1083.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38929.5985 | 1 | 0 | 38929.5985 | 1 | 0 | 985.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5987 | 1 | 0 | 38929.5987 | 1 | 0 | 1002.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5988 | 1 | 0 | 38929.5989 | 1 | 0 | 1019 | 1134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.599 | 1 | 0 | 38929.5991 | 1 | 0 | 1036 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5992 | 1 | 0 | 38929.5992 | 1 | 0 | 1052.5 | 1167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5994 | 1 | 0 | 38929.5994 | 1 | 0 | 1069.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5996 | 1 | 0 | 38929.5996 | 1 | 0 | 1086.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5998 | 1 | 0 | 38929.5998 | 1 | 0 | 1103 | 1218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6 | 1 | 0 | 38929.6 | 1 | 0 | 1119.5 | 1234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6002 | 1 | 0 | 38929.6002 | 1 | 0 | 1136.5 | 1251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6004 | 1 | 0 | 38929.6004 | 1 | 0 | 1153.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6006 | 1 | 0 | 38929.6006 | 1 | 0 | 1170 | 1285 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6008 | 4 | 13 | 38929.6008 | 3 | 7 | 1187 | 1302 | 0.2442 | 0.79365 | 0.18315 | 0.42735 | 0.002442 | 0.0079365 | 0.0018315 | 0.0042735 | 0.0054945 | 0.002442 | 23497.4183 | 53146.3139 | 16092.9503
38929.601 | 3 | 14 | 38929.601 | 3 | 8 | 1203.5 | 1318.5 | 0.18315 | 0.8547 | 0.18315 | 0.4884 | 0.0018315 | 0.008547 | 0.0018315 | 0.004884 | 0.0067155 | 0.0030525 | 19239.5422 | 42554.2903 | 14936.4716
38929.6012 | 4 | 15 | 38929.6012 | 3 | 7 | 1220.5 | 1335.5 | 0.2442 | 0.91575 | 0.18315 | 0.42735 | 0.002442 | 0.0091575 | 0.0018315 | 0.0042735 | 0.0067155 | 0.002442 | 19222.1473 | 53235.1572 | 13933.959
38929.6014 | 4 | 17 | 38929.6014 | 10 | 14 | 1237.5 | 1352.5 | 0.2442 | 1.0379 | 0.6105 | 0.8547 | 0.002442 | 0.010379 | 0.006105 | 0.008547 | 0.0079365 | 0.002442 | 16262.8102 | 53731.8907 | 12283.1399
38929.6016 | 1185 | 1167 | 38929.6016 | 998 | 963 | 1254 | 1369 | 72.3443 | 71.2454 | 60.928 | 58.7912 | 0.72344 | 0.71245 | 0.60928 | 0.58791 | 0.010989 | 0.021368 | 428.6964 | 587.9838 | 17.5016
38929.6018 | 1100 | 1157 | 38929.6018 | 979 | 1093 | 1271 | 1386 | 67.1551 | 70.6349 | 59.768 | 66.7277 | 0.67155 | 0.70635 | 0.59768 | 0.66728 | 0.034799 | 0.069597 | 172.1945 | 217.7678 | 8.5281
38929.602 | 957 | 925 | 38929.602 | 1178 | 1118 | 1287.5 | 1402.5 | 58.4249 | 56.4713 | 71.917 | 68.254 | 0.58425 | 0.56471 | 0.71917 | 0.68254 | 0.019536 | 0.03663 | 182.7717 | 154.0398 | 15.1439
38929.6022 | 1018 | 987 | 38929.6022 | 1128 | 1103 | 1304.5 | 1419.5 | 62.149 | 60.2564 | 68.8645 | 67.3382 | 0.62149 | 0.60256 | 0.68864 | 0.67338 | 0.018926 | 0.015263 | 171.388 | 162.3588 | 6.7728
38929.6023 | 1106 | 1078 | 38929.6024 | 1180 | 1162 | 1321.5 | 1436.5 | 67.5214 | 65.812 | 72.0391 | 70.9402 | 0.67521 | 0.65812 | 0.72039 | 0.7094 | 0.017094 | 0.010989 | 4658.335 | 16890.185 | 6.5457
38929.6025 | 928 | 957 | 38929.6026 | 963 | 1081 | 1338 | 1453 | 56.6545 | 58.4249 | 58.7912 | 65.9951 | 0.56654 | 0.58425 | 0.58791 | 0.65995 | 0.017705 | 0.072039 | 412.5391 | 370.5706 | 18.7632
38929.6027 | 1167 | 902 | 38929.6028 | 1097 | 1072 | 1355 | 1470 | 71.2454 | 55.0672 | 66.9719 | 65.4457 | 0.71245 | 0.55067 | 0.66972 | 0.65446 | 0.16178 | 0.015263 | 2.3384 | 2.2443 | 0.10712
38929.6029 | 1089 | 1144 | 38929.6029 | 1041 | 1013 | 1371.5 | 1486.5 | 66.4835 | 69.8413 | 63.5531 | 61.8437 | 0.66484 | 0.69841 | 0.63553 | 0.61844 | 0.033578 | 0.017094 | 226.8998 | 288.6634 | 7.7893
38929.6031 | 961 | 1079 | 38929.6031 | 1144 | 1122 | 1388.5 | 1503.5 | 58.6691 | 65.873 | 69.8413 | 68.4982 | 0.58669 | 0.65873 | 0.69841 | 0.68498 | 0.072039 | 0.013431 | 104.0849 | 109.1213 | 3.5313
38929.6033 | 950 | 919 | 38929.6033 | 989 | 959 | 1405.5 | 1520.5 | 57.9976 | 56.105 | 60.3785 | 58.547 | 0.57998 | 0.56105 | 0.60379 | 0.58547 | 0.018926 | 0.018315 | 5855.1064 | 8252.0292 | 26.2349
38929.6035 | 1184 | 1082 | 38929.6035 | 928 | 904 | 1422 | 1537 | 72.2833 | 66.0562 | 56.6545 | 55.1893 | 0.72283 | 0.66056 | 0.56654 | 0.55189 | 0.062271 | 0.014652 | 129.372 | 175.621 | 9.0089
38929.6037 | 1035 | 940 | 38929.6037 | 947 | 909 | 1439 | 1554 | 63.1868 | 57.3871 | 57.8144 | 55.4945 | 0.63187 | 0.57387 | 0.57814 | 0.55495 | 0.057998 | 0.023199 | 536.3394 | 886.8269 | 13.1951
38929.6039 | 1146 | 1099 | 38929.6039 | 1048 | 1067 | 1455.5 | 1570.5 | 69.9634 | 67.094 | 63.9805 | 65.1404 | 0.69963 | 0.67094 | 0.6398 | 0.6514 | 0.028694 | 0.0116 | 489.2465 | 729.4813 | 10.5613
38929.6041 | 1183 | 859 | 38929.6041 | 1172 | 1132 | 1472.5 | 1587.5 | 72.2222 | 52.442 | 71.5507 | 69.1087 | 0.72222 | 0.52442 | 0.71551 | 0.69109 | 0.1978 | 0.02442 | 35.937 | 37.9431 | 2.2742
38929.6043 | 1044 | 959 | 38929.6043 | 1132 | 1174 | 1489.5 | 1604.5 | 63.7363 | 58.547 | 69.1087 | 71.6728 | 0.63736 | 0.58547 | 0.69109 | 0.71673 | 0.051893 | 0.025641 | 178.9337 | 187.1442 | 7.477
38929.6045 | 1178 | 1149 | 38929.6045 | 1070 | 990 | 1506 | 1621 | 71.917 | 70.1465 | 65.3236 | 60.4396 | 0.71917 | 0.70147 | 0.65324 | 0.6044 | 0.017705 | 0.04884 | 263.1086 | 352.0499 | 14.5034
38929.6047 | 1014 | 915 | 38929.6047 | 980 | 873 | 1523 | 1638 | 61.9048 | 55.8608 | 59.8291 | 53.2967 | 0.61905 | 0.55861 | 0.59829 | 0.53297 | 0.06044 | 0.065324 | 3129.678 | 1432.2851 | 18.799
38929.6049 | 1191 | 1154 | 38929.6049 | 1025 | 1119 | 1539.5 | 1654.5 | 72.7106 | 70.4518 | 62.5763 | 68.315 | 0.72711 | 0.70452 | 0.62576 | 0.68315 | 0.022589 | 0.057387 | 422.3878 | 636.5577 | 17.373
38929.6051 | 951 | 826 | 38929.6051 | 1049 | 955 | 1556.5 | 1671.5 | 58.0586 | 50.4274 | 64.0415 | 58.3028 | 0.58059 | 0.50427 | 0.64042 | 0.58303 | 0.076313 | 0.057387 | 808.5163 | 4411.8011 | 39.7787
38929.6053 | 1194 | 876 | 38929.6053 | 1196 | 1171 | 1573.5 | 1688.5 | 72.8938 | 53.4799 | 73.0159 | 71.4896 | 0.72894 | 0.5348 | 0.73016 | 0.7149 | 0.19414 | 0.015263 | 67.8635 | 84.5382 | 2.2497
38929.6055 | 1182 | 1190 | 38929.6055 | 1176 | 1190 | 1590 | 1705 | 72.1612 | 72.6496 | 71.7949 | 72.6496 | 0.72161 | 0.7265 | 0.71795 | 0.7265 | 0.004884 | 0.008547 | 5933.2729 | 15471.6084 | 21.6233
38929.6056 | 1026 | 925 | 38929.6057 | 999 | 981 | 1607 | 1722 | 62.6374 | 56.4713 | 60.989 | 59.8901 | 0.62637 | 0.56471 | 0.60989 | 0.5989 | 0.061661 | 0.010989 | 316.6263 | 381.7373 | 13.8797
38929.6058 | 1170 | 1123 | 38929.6059 | 1067 | 1085 | 1623.5 | 1738.5 | 71.4286 | 68.5592 | 65.1404 | 66.2393 | 0.71429 | 0.68559 | 0.6514 | 0.66239 | 0.028694 | 0.010989 | 801.5396 | 1589.5015 | 15.0781
38929.606 | 1188 | 1152 | 38929.6061 | 1044 | 1049 | 1640.5 | 1755.5 | 72.5275 | 70.3297 | 63.7363 | 64.0415 | 0.72527 | 0.7033 | 0.63736 | 0.64042 | 0.021978 | 0.0030525 | 671.0008 | 1130.9999 | 18.1025
38929.6062 | 1065 | 993 | 38929.6062 | 1147 | 1099 | 1657.5 | 1772.5 | 65.0183 | 60.6227 | 70.0244 | 67.094 | 0.65018 | 0.60623 | 0.70024 | 0.67094 | 0.043956 | 0.029304 | 360.4419 | 453.9227 | 4.5405
38929.6064 | 952 | 856 | 38929.6064 | 1071 | 1003 | 1674 | 1789 | 58.1197 | 52.2589 | 65.3846 | 61.2332 | 0.5812 | 0.52259 | 0.65385 | 0.61233 | 0.058608 | 0.041514 | 839.7617 | 2025.7532 | 33.9569
38929.6066 | 1058 | 987 | 38929.6066 | 1179 | 1143 | 1691 | 1806 | 64.591 | 60.2564 | 71.978 | 69.7802 | 0.64591 | 0.60256 | 0.71978 | 0.6978 | 0.043346 | 0.021978 | 463.6626 | 630.508 | 5.9482
38929.6068 | 938 | 845 | 38929.6068 | 1030 | 1041 | 1707.5 | 1822.5 | 57.265 | 51.5873 | 62.8816 | 63.5531 | 0.57265 | 0.51587 | 0.62882 | 0.63553 | 0.056777 | 0.0067155 | 429.7746 | 468.3938 | 32.1844
38929.607 | 947 | 1047 | 38929.607 | 1142 | 1184 | 1724.5 | 1839.5 | 57.8144 | 63.9194 | 69.7192 | 72.2833 | 0.57814 | 0.63919 | 0.69719 | 0.72283 | 0.06105 | 0.025641 | 202.1895 | 219.6366 | 7.8113
38929.6072 | 1181 | 1148 | 38929.6072 | 970 | 877 | 1741.5 | 1856.5 | 72.1001 | 70.0855 | 59.2186 | 53.5409 | 0.721 | 0.70085 | 0.59219 | 0.53541 | 0.020147 | 0.056777 | 84.7593 | 107.6309 | 9.7525
38929.6074 | 1056 | 985 | 38929.6074 | 1194 | 1185 | 1758 | 1873 | 64.4689 | 60.1343 | 72.8938 | 72.3443 | 0.64469 | 0.60134 | 0.72894 | 0.72344 | 0.043346 | 0.0054945 | 347.2573 | 422.0385 | 5.9111
38929.6076 | 981 | 895 | 38929.6076 | 978 | 893 | 1775 | 1890 | 59.8901 | 54.6398 | 59.707 | 54.5177 | 0.5989 | 0.5464 | 0.59707 | 0.54518 | 0.052503 | 0.051893 | 2254.8946 | 2500.1948 | 25.4642
38929.6078 | 1025 | 948 | 38929.6078 | 1000 | 1104 | 1791.5 | 1906.5 | 62.5763 | 57.8755 | 61.0501 | 67.3993 | 0.62576 | 0.57875 | 0.6105 | 0.67399 | 0.047009 | 0.063492 | 1275.4299 | 11413.2409 | 14.6418
38929.608 | 1001 | 1004 | 38929.608 | 1122 | 1168 | 1808.5 | 1923.5 | 61.1111 | 61.2943 | 68.4982 | 71.3065 | 0.61111 | 0.61294 | 0.68498 | 0.71306 | 0.0018315 | 0.028083 | 163.4724 | 148.2467 | 6.425
38929.6082 | 1071 | 1153 | 38929.6082 | 1187 | 1159 | 1825.5 | 1940.5 | 65.3846 | 70.3907 | 72.4664 | 70.757 | 0.65385 | 0.70391 | 0.72466 | 0.70757 | 0.050061 | 0.017094 | 850.8561 | 2849.2185 | 9.299
38929.6084 | 979 | 900 | 38929.6084 | 1127 | 1077 | 1842 | 1957 | 59.768 | 54.9451 | 68.8034 | 65.7509 | 0.59768 | 0.54945 | 0.68803 | 0.65751 | 0.04823 | 0.030525 | 452.5423 | 524.5099 | 21.8386

## C1-4
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38929.5858 | 1 | 0 | 38929.5858 | 1 | 0 | -109 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.586 | 1 | 0 | 38929.586 | 1 | 0 | -92.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5862 | 1 | 0 | 38929.5862 | 1 | 0 | -75.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5864 | 1 | 0 | 38929.5864 | 1 | 0 | -59 | 56 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5866 | 1 | 0 | 38929.5866 | 1 | 0 | -42 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5868 | 1 | 0 | 38929.5868 | 2 | 0 | -25.5 | 89.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38929.587 | 1 | 0 | 38929.587 | 1 | 0 | -8.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5872 | 1 | 0 | 38929.5872 | 1 | 0 | 8.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5873 | 1 | 0 | 38929.5874 | 1 | 0 | 25 | 140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5875 | 1 | 0 | 38929.5876 | 1 | 0 | 42 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5877 | 1 | 0 | 38929.5877 | 1 | 0 | 58.5 | 173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5879 | 1 | 0 | 38929.5879 | 1 | 0 | 75.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5881 | 1 | 0 | 38929.5881 | 1 | 0 | 92.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5883 | 1 | 0 | 38929.5883 | 1 | 0 | 109 | 224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5885 | 1 | 0 | 38929.5885 | 1 | 0 | 126 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5887 | 1 | 0 | 38929.5887 | 1 | 0 | 142.5 | 257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5889 | 1 | 0 | 38929.5889 | 1 | 0 | 159.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5891 | 1 | 0 | 38929.5891 | 1 | 0 | 176.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5893 | 1 | 0 | 38929.5893 | 1 | 0 | 193 | 308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5895 | 1 | 0 | 38929.5895 | 1 | 0 | 210 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5897 | 1 | 0 | 38929.5897 | 1 | 0 | 226.5 | 341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5899 | 1 | 0 | 38929.5899 | 1 | 0 | 243.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5901 | 1 | 0 | 38929.5901 | 1 | 0 | 260.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5903 | 1 | 0 | 38929.5903 | 1 | 0 | 277 | 392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5905 | 1 | 0 | 38929.5905 | 1 | 0 | 294 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5906 | 1 | 0 | 38929.5907 | 1 | 0 | 310.5 | 425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5908 | 1 | 0 | 38929.5909 | 1 | 0 | 327.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.591 | 1 | 0 | 38929.5911 | 1 | 0 | 344.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5912 | 1 | 0 | 38929.5912 | 1 | 0 | 361 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5914 | 1 | 0 | 38929.5914 | 1 | 0 | 378 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5916 | 1 | 0 | 38929.5916 | 1 | 0 | 394.5 | 509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5918 | 1 | 0 | 38929.5918 | 1 | 0 | 411.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.592 | 1 | 0 | 38929.592 | 1 | 0 | 428.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5922 | 1 | 0 | 38929.5922 | 1 | 0 | 445 | 560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5924 | 1 | 0 | 38929.5924 | 1 | 0 | 462 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5926 | 1 | 0 | 38929.5926 | 1 | 0 | 478.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5928 | 1 | 0 | 38929.5928 | 1 | 0 | 495.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.593 | 1 | 0 | 38929.593 | 1 | 0 | 512.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5932 | 1 | 0 | 38929.5932 | 1 | 0 | 529 | 644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5934 | 1 | 0 | 38929.5934 | 1 | 0 | 546 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5936 | 1 | 0 | 38929.5936 | 1 | 0 | 562.5 | 677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5938 | 1 | 0 | 38929.5938 | 1 | 0 | 579.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.594 | 1 | 0 | 38929.594 | 1 | 0 | 596.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5941 | 1 | 0 | 38929.5942 | 1 | 0 | 613 | 728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5943 | 1 | 0 | 38929.5944 | 1 | 0 | 630 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5945 | 1 | 0 | 38929.5945 | 1 | 0 | 646.5 | 761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5947 | 1 | 0 | 38929.5947 | 1 | 0 | 663.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5949 | 1 | 0 | 38929.5949 | 1 | 0 | 680.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5951 | 1 | 0 | 38929.5951 | 1 | 0 | 697 | 812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5953 | 1 | 0 | 38929.5953 | 1 | 0 | 714 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5955 | 1 | 0 | 38929.5955 | 1 | 0 | 730.5 | 845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5957 | 1 | 0 | 38929.5957 | 1 | 0 | 747.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5959 | 1 | 0 | 38929.5959 | 1 | 0 | 764 | 879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5961 | 1 | 0 | 38929.5961 | 1 | 0 | 781 | 896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5963 | 1 | 0 | 38929.5963 | 1 | 0 | 797.5 | 912.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5965 | 1 | 0 | 38929.5965 | 1 | 0 | 814.5 | 929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5967 | 1 | 0 | 38929.5967 | 1 | 0 | 831.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5969 | 1 | 0 | 38929.5969 | 1 | 0 | 848.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5971 | 1 | 0 | 38929.5971 | 1 | 0 | 865 | 980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5973 | 1 | 0 | 38929.5973 | 1 | 0 | 882 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5975 | 1 | 0 | 38929.5975 | 1 | 0 | 898.5 | 1013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5977 | 1 | 0 | 38929.5977 | 1 | 0 | 915.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5978 | 1 | 0 | 38929.5979 | 1 | 0 | 932 | 1047 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.598 | 1 | 0 | 38929.5981 | 1 | 0 | 949 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5982 | 1 | 0 | 38929.5983 | 1 | 0 | 966 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5984 | 1 | 0 | 38929.5984 | 1 | 0 | 982.5 | 1097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5986 | 1 | 0 | 38929.5986 | 1 | 0 | 999.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5988 | 1 | 0 | 38929.5988 | 1 | 0 | 1016 | 1131 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.599 | 1 | 0 | 38929.599 | 1 | 0 | 1033 | 1148 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5992 | 1 | 0 | 38929.5992 | 1 | 0 | 1049.5 | 1164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5994 | 1 | 0 | 38929.5994 | 1 | 0 | 1066.5 | 1181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5996 | 1 | 0 | 38929.5996 | 1 | 0 | 1083.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5998 | 1 | 0 | 38929.5998 | 1 | 0 | 1100 | 1215 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6 | 1 | 0 | 38929.6 | 1 | 0 | 1117 | 1232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6002 | 1 | 0 | 38929.6002 | 1 | 0 | 1134 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6004 | 1 | 0 | 38929.6004 | 1 | 0 | 1150.5 | 1265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6006 | 35 | 38 | 38929.6006 | 86 | 81 | 1167.5 | 1282.5 | 2.1368 | 2.3199 | 5.2503 | 4.9451 | 0.021368 | 0.023199 | 0.052503 | 0.049451 | 0.0018315 | 0.0030525 | 71449.1127 | 41480.9167 | 5355.5628
38929.6008 | 1038 | 1003 | 38929.6008 | 1132 | 1107 | 1184 | 1299 | 63.37 | 61.2332 | 69.1087 | 67.5824 | 0.6337 | 0.61233 | 0.69109 | 0.67582 | 0.021368 | 0.015263 | 601.5191 | 697.8968 | 6.2805
38929.6009 | 918 | 937 | 38929.601 | 1070 | 1038 | 1201 | 1316 | 56.044 | 57.2039 | 65.3236 | 63.37 | 0.56044 | 0.57204 | 0.65324 | 0.6337 | 0.0116 | 0.019536 | 2693.3608 | 3693.4694 | 26.8109
38929.6011 | 1046 | 1014 | 38929.6012 | 1178 | 1161 | 1217.5 | 1332.5 | 63.8584 | 61.9048 | 71.917 | 70.8791 | 0.63858 | 0.61905 | 0.71917 | 0.70879 | 0.019536 | 0.010379 | 1415.8642 | 2338.4667 | 5.0144
38929.6013 | 1115 | 1087 | 38929.6014 | 1157 | 1135 | 1234.5 | 1349.5 | 68.0708 | 66.3614 | 70.6349 | 69.2918 | 0.68071 | 0.66361 | 0.70635 | 0.69292 | 0.017094 | 0.013431 | 9795.4823 | 6102.8242 | 8.0539
38929.6015 | 963 | 927 | 38929.6016 | 966 | 932 | 1251.5 | 1366.5 | 58.7912 | 56.5934 | 58.9744 | 56.8987 | 0.58791 | 0.56593 | 0.58974 | 0.56899 | 0.021978 | 0.020757 | 4656.2146 | 8202.5264 | 23.7685
38929.6017 | 1180 | 1116 | 38929.6017 | 1081 | 1139 | 1268 | 1383 | 72.0391 | 68.1319 | 65.9951 | 69.536 | 0.72039 | 0.68132 | 0.65995 | 0.69536 | 0.039072 | 0.035409 | 23328.0379 | 1859.9865 | 15.5595
38929.6019 | 1054 | 1027 | 38929.6019 | 1172 | 1188 | 1285 | 1400 | 64.3468 | 62.6984 | 71.5507 | 72.5275 | 0.64347 | 0.62698 | 0.71551 | 0.72527 | 0.016484 | 0.009768 | 2490.2903 | 6614.7252 | 3.0714
38929.6021 | 1127 | 1178 | 38929.6021 | 1176 | 1187 | 1301.5 | 1416.5 | 68.8034 | 71.917 | 71.7949 | 72.4664 | 0.68803 | 0.71917 | 0.71795 | 0.72466 | 0.031136 | 0.0067155 | 1361.9445 | 5505.1983 | 16.0064
38929.6023 | 934 | 902 | 38929.6023 | 1106 | 1169 | 1318.5 | 1433.5 | 57.0208 | 55.0672 | 67.5214 | 71.3675 | 0.57021 | 0.55067 | 0.67521 | 0.71368 | 0.019536 | 0.038462 | 540.0462 | 484.1177 | 25.4539
38929.6025 | 927 | 905 | 38929.6025 | 1180 | 910 | 1335.5 | 1450.5 | 56.5934 | 55.2503 | 72.0391 | 55.5556 | 0.56593 | 0.5525 | 0.72039 | 0.55556 | 0.013431 | 0.16484 | 126.4525 | 98.808 | 15.4329
38929.6027 | 1146 | 1124 | 38929.6027 | 1054 | 1105 | 1352 | 1467 | 69.9634 | 68.6203 | 64.3468 | 67.4603 | 0.69963 | 0.6862 | 0.64347 | 0.6746 | 0.013431 | 0.031136 | 640.4787 | 871.4264 | 12.5285
38929.6029 | 987 | 958 | 38929.6029 | 1073 | 1046 | 1369 | 1484 | 60.2564 | 58.486 | 65.5067 | 63.8584 | 0.60256 | 0.58486 | 0.65507 | 0.63858 | 0.017705 | 0.016484 | 3935.5495 | 246593.6977 | 17.5315
38929.6031 | 946 | 979 | 38929.6031 | 994 | 1103 | 1385.5 | 1500.5 | 57.7534 | 59.768 | 60.6838 | 67.3382 | 0.57753 | 0.59768 | 0.60684 | 0.67338 | 0.020147 | 0.066545 | 323.9766 | 299.1895 | 14.3942
38929.6033 | 1019 | 927 | 38929.6033 | 1013 | 984 | 1402.5 | 1517.5 | 62.21 | 56.5934 | 61.8437 | 60.0733 | 0.6221 | 0.56593 | 0.61844 | 0.60073 | 0.056166 | 0.017705 | 391.9274 | 495.3552 | 14.991
38929.6035 | 977 | 948 | 38929.6035 | 926 | 904 | 1419.5 | 1534.5 | 59.6459 | 57.8755 | 56.5324 | 55.1893 | 0.59646 | 0.57875 | 0.56532 | 0.55189 | 0.017705 | 0.013431 | 3622.5064 | 40168.5623 | 19.7841
38929.6037 | 918 | 945 | 38929.6037 | 1016 | 915 | 1436 | 1551 | 56.044 | 57.6923 | 62.0269 | 55.8608 | 0.56044 | 0.57692 | 0.62027 | 0.55861 | 0.016484 | 0.061661 | 677.9836 | 633.1196 | 22.8483
38929.6039 | 1028 | 942 | 38929.6039 | 1149 | 1103 | 1453 | 1568 | 62.7595 | 57.5092 | 70.1465 | 67.3382 | 0.62759 | 0.57509 | 0.70147 | 0.67338 | 0.052503 | 0.028083 | 17.5747 | 15.4737 | 2.0345
38929.6041 | 1185 | 1179 | 38929.6041 | 1082 | 1114 | 1469.5 | 1584.5 | 72.3443 | 71.978 | 66.0562 | 68.0098 | 0.72344 | 0.71978 | 0.66056 | 0.6801 | 0.003663 | 0.019536 | 1130.5566 | 1549.5781 | 19.997
38929.6043 | 932 | 853 | 38929.6043 | 935 | 898 | 1486.5 | 1601.5 | 56.8987 | 52.0757 | 57.0818 | 54.823 | 0.56899 | 0.52076 | 0.57082 | 0.54823 | 0.04823 | 0.022589 | 1016.6585 | 2295.0566 | 36.8493
38929.6045 | 1001 | 901 | 38929.6045 | 1117 | 1054 | 1503.5 | 1618.5 | 61.1111 | 55.0061 | 68.1929 | 64.3468 | 0.61111 | 0.55006 | 0.68193 | 0.64347 | 0.06105 | 0.038462 | 368.6831 | 446.8815 | 19.1381
38929.6046 | 1190 | 1183 | 38929.6047 | 1180 | 1139 | 1520 | 1635 | 72.6496 | 72.2222 | 72.0391 | 69.536 | 0.7265 | 0.72222 | 0.72039 | 0.69536 | 0.0042735 | 0.025031 | 1158.4926 | 1627.8123 | 20.7044
38929.6048 | 1039 | 947 | 38929.6049 | 1116 | 1176 | 1537 | 1652 | 63.431 | 57.8144 | 68.1319 | 71.7949 | 0.63431 | 0.57814 | 0.68132 | 0.71795 | 0.056166 | 0.03663 | 122.7662 | 120.9683 | 7.3428
38929.605 | 966 | 849 | 38929.605 | 945 | 819 | 1553.5 | 1668.5 | 58.9744 | 51.8315 | 57.6923 | 50 | 0.58974 | 0.51832 | 0.57692 | 0.5 | 0.071429 | 0.076923 | 2170.8797 | 1323.1852 | 32.636
38929.6052 | 1005 | 891 | 38929.6052 | 941 | 1031 | 1570.5 | 1685.5 | 61.3553 | 54.3956 | 57.4481 | 62.9426 | 0.61355 | 0.54396 | 0.57448 | 0.62943 | 0.069597 | 0.054945 | 711.3415 | 2133.3726 | 23.2663
38929.6054 | 1040 | 943 | 38929.6054 | 932 | 870 | 1587.5 | 1702.5 | 63.4921 | 57.5702 | 56.8987 | 53.1136 | 0.63492 | 0.5757 | 0.56899 | 0.53114 | 0.059219 | 0.037851 | 796.6209 | 2501.5624 | 13.2579
38929.6056 | 1167 | 1120 | 38929.6056 | 1180 | 1190 | 1604 | 1719 | 71.2454 | 68.3761 | 72.0391 | 72.6496 | 0.71245 | 0.68376 | 0.72039 | 0.7265 | 0.028694 | 0.006105 | 1378.6146 | 5180.134 | 15.2397
38929.6058 | 1066 | 981 |  | 1132 | 1097 | 1620 | 1735 | 65.0794 | 59.8901 | 69.1087 | 66.9719 | 0.65079 | 0.5989 | 0.69109 | 0.66972 | 0.051893 | 0.021368 | 99.9138 | 101.8773 | 3.3962
38929.606 | 969 | 856 | 38929.606 | 1083 | 1004 | 1637.5 | 1752.5 | 59.1575 | 52.2589 | 66.1172 | 61.2943 | 0.59158 | 0.52259 | 0.66117 | 0.61294 | 0.068987 | 0.04823 | 653.9899 | 1382.221 | 31.3771
38929.6062 | 1044 | 1060 | 38929.6062 | 962 | 862 | 1654.5 | 1769.5 | 63.7363 | 64.7131 | 58.7302 | 52.6252 | 0.63736 | 0.64713 | 0.5873 | 0.52625 | 0.009768 | 0.06105 | 361.6466 | 379.1158 | 0.67334
38929.6064 | 1000 | 997 | 38929.6064 | 1147 | 1098 | 1671.5 | 1786.5 | 61.0501 | 60.8669 | 70.0244 | 67.033 | 0.6105 | 0.60867 | 0.70024 | 0.67033 | 0.0018315 | 0.029915 | 42.4468 | 38.0658 | 3.2084
38929.6066 | 1137 | 1182 | 38929.6066 | 1007 | 925 | 1688 | 1803 | 69.4139 | 72.1612 | 61.4774 | 56.4713 | 0.69414 | 0.72161 | 0.61477 | 0.56471 | 0.027473 | 0.050061 | 29.3774 | 36.0657 | 4.6191
38929.6068 | 1170 | 1129 | 38929.6068 | 1194 | 933 | 1705 | 1820 | 71.4286 | 68.9255 | 72.8938 | 56.9597 | 0.71429 | 0.68926 | 0.72894 | 0.5696 | 0.025031 | 0.15934 | 72.65 | 89.8148 | 7.7945
38929.607 | 948 | 847 | 38929.607 | 940 | 839 | 1721.5 | 1836.5 | 57.8755 | 51.7094 | 57.3871 | 51.221 | 0.57875 | 0.51709 | 0.57387 | 0.51221 | 0.061661 | 0.061661 | 1992.099 | 1992.099 | 35.7519
38929.6072 | 930 | 860 | 38929.6072 | 1170 | 1178 | 1738.5 | 1853.5 | 56.7766 | 52.5031 | 71.4286 | 71.917 | 0.56777 | 0.52503 | 0.71429 | 0.71917 | 0.042735 | 0.004884 | 173.3961 | 140.4621 | 21.9403
38929.6074 | 930 | 876 | 38929.6074 | 1193 | 1183 | 1755.5 | 1870.5 | 56.7766 | 53.4799 | 72.8327 | 72.2222 | 0.56777 | 0.5348 | 0.72833 | 0.72222 | 0.032967 | 0.006105 | 127.3037 | 100.0812 | 17.5311
38929.6076 | 962 | 1070 | 38929.6076 | 1069 | 1153 | 1772 | 1887 | 58.7302 | 65.3236 | 65.2625 | 70.3907 | 0.5873 | 0.65324 | 0.65263 | 0.70391 | 0.065934 | 0.051282 | 139.9925 | 149.8177 | 4.541
38929.6078 | 1184 | 1153 | 38929.6078 | 925 | 893 | 1789 | 1904 | 72.2833 | 70.3907 | 56.4713 | 54.5177 | 0.72283 | 0.70391 | 0.56471 | 0.54518 | 0.018926 | 0.019536 | 109921.8468 | 3823.599 | 18.9307
38929.608 | 1195 | 1170 | 38929.608 | 1043 | 972 | 1805.5 | 1920.5 | 72.9548 | 71.4286 | 63.6752 | 59.3407 | 0.72955 | 0.71429 | 0.63675 | 0.59341 | 0.015263 | 0.043346 | 275.1094 | 379.0177 | 17.0407
38929.6081 | 1063 | 998 | 38929.6082 | 1013 | 935 | 1822.5 | 1937.5 | 64.8962 | 60.928 | 61.8437 | 57.0818 | 0.64896 | 0.60928 | 0.61844 | 0.57082 | 0.039683 | 0.047619 | 3498.7151 | 2852.3731 | 5.0359
38929.6083 | 962 | 875 | 38929.6084 | 925 | 899 | 1839.5 | 1954.5 | 58.7302 | 53.4188 | 56.4713 | 54.884 | 0.5873 | 0.53419 | 0.56471 | 0.54884 | 0.053114 | 0.015873 | 720.5385 | 1202.8414 | 29.1239

## C1-3
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38929.5858 | 1 | 0 | 38929.5858 | 1 | 0 | -112 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5859 | 1 | 0 | 38929.586 | 1 | 0 | -95.5 | 19.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5861 | 1 | 0 | 38929.5862 | 1 | 0 | -78.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5863 | 1 | 0 | 38929.5864 | 1 | 0 | -61.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5865 | 1 | 0 | 38929.5866 | 1 | 0 | -44.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5867 | 1 | 0 | 38929.5867 | 1 | 0 | -28 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5869 | 1 | 0 | 38929.5869 | 3 | 0 | -11.5 | 103.5 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 211202 | 70334 | 211201.9994
38929.5871 | 1 | 0 | 38929.5871 | 1 | 0 | 5.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5873 | 1 | 0 | 38929.5873 | 1 | 0 | 22.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5875 | 1 | 0 | 38929.5875 | 1 | 0 | 39 | 154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5877 | 1 | 0 | 38929.5877 | 1 | 0 | 56 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5879 | 1 | 0 | 38929.5879 | 2 | 0 | 72.5 | 187.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38929.5881 | 1 | 0 | 38929.5881 | 1 | 0 | 89.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5883 | 1 | 0 | 38929.5883 | 1 | 0 | 106.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5885 | 1 | 0 | 38929.5885 | 1 | 0 | 123 | 238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5887 | 1 | 0 | 38929.5887 | 1 | 0 | 140 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5889 | 1 | 0 | 38929.5889 | 1 | 0 | 156.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5891 | 1 | 0 | 38929.5891 | 1 | 0 | 173.5 | 288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5893 | 1 | 0 | 38929.5893 | 1 | 0 | 190.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5894 | 1 | 0 | 38929.5895 | 1 | 0 | 207 | 322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5896 | 1 | 0 | 38929.5897 | 1 | 0 | 224 | 339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5898 | 1 | 0 | 38929.5898 | 1 | 0 | 240.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.59 | 1 | 0 | 38929.59 | 1 | 0 | 257.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5902 | 1 | 0 | 38929.5902 | 1 | 0 | 274.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5904 | 1 | 0 | 38929.5904 | 1 | 0 | 291 | 406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5906 | 1 | 0 | 38929.5906 | 1 | 0 | 308 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5908 | 1 | 0 | 38929.5908 | 1 | 0 | 324.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.591 | 1 | 0 | 38929.591 | 1 | 0 | 341.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5912 | 1 | 0 | 38929.5912 | 1 | 0 | 358.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5914 | 1 | 0 | 38929.5914 | 1 | 0 | 375 | 490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5916 | 1 | 0 | 38929.5916 | 1 | 0 | 392 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5918 | 1 | 0 | 38929.5918 | 1 | 0 | 408.5 | 523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.592 | 1 | 0 | 38929.592 | 1 | 0 | 425.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5922 | 1 | 0 | 38929.5922 | 1 | 0 | 442.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5924 | 1 | 0 | 38929.5924 | 1 | 0 | 459 | 574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5926 | 1 | 0 | 38929.5926 | 1 | 0 | 476 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5928 | 1 | 0 | 38929.5928 | 1 | 0 | 492.5 | 607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.593 | 1 | 0 | 38929.593 | 1 | 0 | 509.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5931 | 1 | 0 | 38929.5932 | 1 | 0 | 526.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5933 | 1 | 0 | 38929.5934 | 1 | 0 | 543 | 658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5935 | 2 | 0 | 38929.5936 | 1 | 0 | 560 | 675 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38929.5937 | 1 | 0 | 38929.5937 | 1 | 0 | 576.5 | 691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5939 | 1 | 0 | 38929.5939 | 1 | 0 | 593.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5941 | 1 | 0 | 38929.5941 | 1 | 0 | 610.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5943 | 1 | 0 | 38929.5943 | 1 | 0 | 627 | 742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5945 | 1 | 0 | 38929.5945 | 1 | 0 | 643.5 | 758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5947 | 1 | 0 | 38929.5947 | 1 | 0 | 660.5 | 775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5949 | 1 | 0 | 38929.5949 | 1 | 0 | 677.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5951 | 1 | 0 | 38929.5951 | 1 | 0 | 694.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5953 | 1 | 0 | 38929.5953 | 1 | 0 | 711 | 826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5955 | 1 | 0 | 38929.5955 | 1 | 0 | 727.5 | 842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5957 | 1 | 0 | 38929.5957 | 1 | 0 | 744.5 | 859.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5959 | 1 | 0 | 38929.5959 | 1 | 0 | 761.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5961 | 1 | 0 | 38929.5961 | 1 | 0 | 778.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5963 | 1 | 0 | 38929.5963 | 1 | 0 | 795 | 910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5964 | 1 | 0 | 38929.5965 | 1 | 0 | 811.5 | 926.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5966 | 1 | 0 | 38929.5967 | 1 | 0 | 828.5 | 943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5968 | 1 | 0 | 38929.5969 | 1 | 0 | 845.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.597 | 1 | 0 | 38929.597 | 1 | 0 | 862.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5972 | 1 | 0 | 38929.5972 | 1 | 0 | 879 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5974 | 1 | 0 | 38929.5974 | 1 | 0 | 895.5 | 1010.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5976 | 1 | 0 | 38929.5976 | 1 | 0 | 912.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5978 | 1 | 0 | 38929.5978 | 1 | 0 | 929.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.598 | 1 | 0 | 38929.598 | 1 | 0 | 946.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5982 | 1 | 0 | 38929.5982 | 1 | 0 | 963 | 1078 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5984 | 1 | 0 | 38929.5984 | 1 | 0 | 980 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5986 | 1 | 0 | 38929.5986 | 1 | 0 | 996.5 | 1111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5988 | 1 | 0 | 38929.5988 | 1 | 0 | 1013.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.599 | 1 | 0 | 38929.599 | 1 | 0 | 1030 | 1145 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5992 | 1 | 0 | 38929.5992 | 1 | 0 | 1047 | 1162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5994 | 1 | 0 | 38929.5994 | 1 | 0 | 1063.5 | 1178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5996 | 1 | 0 | 38929.5996 | 1 | 0 | 1080.5 | 1195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5998 | 1 | 0 | 38929.5998 | 1 | 0 | 1097.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5999 | 1 | 0 | 38929.6 | 1 | 0 | 1114 | 1229 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6001 | 1 | 0 | 38929.6002 | 1 | 0 | 1131 | 1246 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6003 | 1 | 0 | 38929.6003 | 1 | 0 | 1147.5 | 1262.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6005 | 1 | 0 | 38929.6005 | 1 | 0 | 1164.5 | 1279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6007 | 1 | 1 | 38929.6007 | 1 | 0 | 1181.5 | 1296.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38929.6009 | 1 | 1 | 38929.6009 | 1 | 0 | 1198 | 1313 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38929.6011 | 2 | 1 | 38929.6011 | 2 | 1 | 1215 | 1330 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38929.6013 | 2 | 2 | 38929.6013 | 2 | 1 | 1231.5 | 1346.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 222820172.02 | 211101.9053 | 105401.071
38929.6015 | 1138 | 1186 | 38929.6015 | 1083 | 1054 | 1248.5 | 1363.5 | 69.475 | 72.4054 | 66.1172 | 64.3468 | 0.69475 | 0.72405 | 0.66117 | 0.64347 | 0.029304 | 0.017705 | 1633.2462 | 10138.2361 | 17.6155
38929.6017 | 1064 | 1037 | 38929.6017 | 1081 | 1135 | 1265.5 | 1380.5 | 64.9573 | 63.3089 | 65.9951 | 69.2918 | 0.64957 | 0.63309 | 0.65995 | 0.69292 | 0.016484 | 0.032967 | 335.4915 | 362.9917 | 0.90876
38929.6019 | 919 | 941 | 38929.6019 | 1136 | 1183 | 1282 | 1397 | 56.105 | 57.4481 | 69.3529 | 72.2222 | 0.56105 | 0.57448 | 0.69353 | 0.72222 | 0.013431 | 0.028694 | 234.8104 | 193.4209 | 17.7246
38929.6021 | 959 | 927 | 38929.6021 | 924 | 952 | 1299 | 1414 | 58.547 | 56.5934 | 56.4103 | 58.1197 | 0.58547 | 0.56593 | 0.5641 | 0.5812 | 0.019536 | 0.017094 | 4049.1477 | 26488.1238 | 24.3976
38929.6023 | 975 | 1093 | 38929.6023 | 1171 | 1153 | 1315.5 | 1430.5 | 59.5238 | 66.7277 | 71.4896 | 70.3907 | 0.59524 | 0.66728 | 0.7149 | 0.70391 | 0.072039 | 0.010989 | 205.7088 | 251.138 | 2.9459
38929.6025 | 927 | 957 | 38929.6025 | 1183 | 1186 | 1332.5 | 1447.5 | 56.5934 | 58.4249 | 72.2222 | 72.4054 | 0.56593 | 0.58425 | 0.72222 | 0.72405 | 0.018315 | 0.0018315 | 127.7674 | 106.5388 | 12.3443
38929.6027 | 988 | 957 | 38929.6027 | 1073 | 1128 | 1349.5 | 1464.5 | 60.3175 | 58.4249 | 65.5067 | 68.8645 | 0.60317 | 0.58425 | 0.65507 | 0.68864 | 0.018926 | 0.033578 | 443.9816 | 430.3186 | 14.2463
38929.6029 | 1177 | 1159 | 38929.6029 | 1060 | 1032 | 1366 | 1481 | 71.8559 | 70.757 | 64.7131 | 63.0037 | 0.71856 | 0.70757 | 0.64713 | 0.63004 | 0.010989 | 0.017094 | 1559.089 | 2757.1381 | 18.5656
38929.6031 | 1154 | 1133 | 38929.6031 | 1145 | 1122 | 1383 | 1498 | 70.4518 | 69.1697 | 69.9023 | 68.4982 | 0.70452 | 0.6917 | 0.69902 | 0.68498 | 0.012821 | 0.014042 | 5983.2593 | 22789.3881 | 15.2886
38929.6033 | 1102 | 1078 | 38929.6033 | 933 | 904 | 1399.5 | 1514.5 | 67.2772 | 65.812 | 56.9597 | 55.1893 | 0.67277 | 0.65812 | 0.5696 | 0.55189 | 0.014652 | 0.017705 | 7428.5342 | 10375.3137 | 6.154
38929.6034 | 968 | 1005 | 38929.6035 | 1053 | 1026 | 1416.5 | 1531.5 | 59.0965 | 61.3553 | 64.2857 | 62.6374 | 0.59096 | 0.61355 | 0.64286 | 0.62637 | 0.022589 | 0.016484 | 1510.9882 | 2591.5722 | 13.4147
38929.6036 | 1110 | 1147 | 38929.6037 | 1163 | 1172 | 1433.5 | 1548.5 | 67.7656 | 70.0244 | 71.0012 | 71.5507 | 0.67766 | 0.70024 | 0.71001 | 0.71551 | 0.022589 | 0.0054945 | 1576.4421 | 4307.8916 | 12.268
38929.6038 | 1175 | 843 | 38929.6039 | 1102 | 1037 | 1450 | 1565 | 71.7338 | 51.4652 | 67.2772 | 63.3089 | 0.71734 | 0.51465 | 0.67277 | 0.63309 | 0.20269 | 0.039683 | 26.4064 | 26.1781 | 2.3385
38929.604 | 925 | 891 | 38929.6041 | 960 | 857 | 1467 | 1582 | 56.4713 | 54.3956 | 58.6081 | 52.3199 | 0.56471 | 0.54396 | 0.58608 | 0.5232 | 0.020757 | 0.062882 | 1153.1675 | 1290.8866 | 30.9389
38929.6042 | 1140 | 1083 | 38929.6042 | 945 | 834 | 1483.5 | 1598.5 | 69.5971 | 66.1172 | 57.6923 | 50.9158 | 0.69597 | 0.66117 | 0.57692 | 0.50916 | 0.034799 | 0.067766 | 434.9419 | 649.6208 | 8.8004
38929.6044 | 1186 | 1108 | 38929.6044 | 1014 | 917 | 1500.5 | 1615.5 | 72.4054 | 67.6435 | 61.9048 | 55.9829 | 0.72405 | 0.67643 | 0.61905 | 0.55983 | 0.047619 | 0.059219 | 12.7688 | 15.4273 | 2.1831
38929.6046 | 1088 | 1013 | 38929.6046 | 1141 | 1084 | 1517.5 | 1632.5 | 66.4225 | 61.8437 | 69.6581 | 66.1783 | 0.66422 | 0.61844 | 0.69658 | 0.66178 | 0.045788 | 0.034799 | 671.1656 | 1303.3571 | 1.102
38929.6048 | 1143 | 1185 | 38929.6048 | 1048 | 1055 | 1534 | 1649 | 69.7802 | 72.3443 | 63.9805 | 64.4078 | 0.6978 | 0.72344 | 0.6398 | 0.64408 | 0.025641 | 0.0042735 | 595.7988 | 980.8791 | 16.4633
38929.605 | 991 | 881 | 38929.605 | 938 | 822 | 1551 | 1666 | 60.5006 | 53.7851 | 57.265 | 50.1832 | 0.60501 | 0.53785 | 0.57265 | 0.50183 | 0.067155 | 0.070818 | 2196.221 | 1495.4677 | 25.6428
38929.6052 | 1162 | 815 | 38929.6052 | 928 | 871 | 1567.5 | 1682.5 | 70.9402 | 49.7558 | 56.6545 | 53.1746 | 0.7094 | 0.49756 | 0.56654 | 0.53175 | 0.21184 | 0.034799 | 114.3567 | 168.171 | 10.4661
38929.6054 | 1168 | 1122 | 38929.6054 | 961 | 924 | 1584.5 | 1699.5 | 71.3065 | 68.4982 | 58.6691 | 56.4103 | 0.71306 | 0.68498 | 0.58669 | 0.5641 | 0.028083 | 0.022589 | 452.603 | 689.2033 | 13.7749
38929.6056 | 973 | 851 | 38929.6056 | 1008 | 996 | 1601.5 | 1716.5 | 59.4017 | 51.9536 | 61.5385 | 60.8059 | 0.59402 | 0.51954 | 0.61538 | 0.60806 | 0.074481 | 0.007326 | 330.7764 | 382.2148 | 26.9194
38929.6058 | 1197 | 930 | 38929.6058 | 1195 | 1187 | 1618 | 1733 | 73.0769 | 56.7766 | 72.9548 | 72.4664 | 0.73077 | 0.56777 | 0.72955 | 0.72466 | 0.163 | 0.004884 | 110.6508 | 165.8205 | 0.93772
38929.606 | 1169 | 1123 | 38929.606 | 1117 | 1049 | 1635 | 1750 | 71.3675 | 68.5592 | 68.1929 | 64.0415 | 0.71368 | 0.68559 | 0.68193 | 0.64042 | 0.028083 | 0.041514 | 778.3533 | 1491.6797 | 14.9364
38929.6062 | 1076 | 1005 | 38929.6062 | 1144 | 1096 | 1651.5 | 1766.5 | 65.6899 | 61.3553 | 69.8413 | 66.9109 | 0.6569 | 0.61355 | 0.69841 | 0.66911 | 0.043346 | 0.029304 | 469.7709 | 671.1179 | 2.7729
38929.6064 | 1196 | 960 | 38929.6064 | 1089 | 1024 | 1668.5 | 1783.5 | 73.0159 | 58.6081 | 66.4835 | 62.5153 | 0.73016 | 0.58608 | 0.66484 | 0.62515 | 0.14408 | 0.039683 | 24.5404 | 27.4224 | 0.96351
38929.6066 | 949 | 852 | 38929.6066 | 1191 | 1057 | 1685.5 | 1800.5 | 57.9365 | 52.0147 | 72.7106 | 64.5299 | 0.57937 | 0.52015 | 0.72711 | 0.6453 | 0.059219 | 0.081807 | 698.2262 | 1222.1884 | 33.8523
38929.6067 | 1010 | 924 | 38929.6068 | 1029 | 949 | 1702 | 1817 | 61.6606 | 56.4103 | 62.8205 | 57.9365 | 0.61661 | 0.5641 | 0.62821 | 0.57937 | 0.052503 | 0.04884 | 1651.4263 | 4810.4856 | 18.9799
38929.6069 | 979 | 886 | 38929.607 | 985 | 979 | 1719 | 1834 | 59.768 | 54.0904 | 60.1343 | 59.768 | 0.59768 | 0.5409 | 0.60134 | 0.59768 | 0.056777 | 0.003663 | 413.4992 | 488.8285 | 23.2392
38929.6071 | 971 | 958 | 38929.6072 | 1026 | 943 | 1735.5 | 1850.5 | 59.2796 | 58.486 | 62.6374 | 57.5702 | 0.5928 | 0.58486 | 0.62637 | 0.5757 | 0.0079365 | 0.050672 | 516.963 | 460.7776 | 15.7834
38929.6073 | 935 | 849 | 38929.6073 | 1135 | 1180 | 1752.5 | 1867.5 | 57.0818 | 51.8315 | 69.2918 | 72.0391 | 0.57082 | 0.51832 | 0.69292 | 0.72039 | 0.052503 | 0.027473 | 327.4328 | 310.1092 | 29.3042
38929.6075 | 1045 | 974 | 38929.6075 | 999 | 915 | 1769.5 | 1884.5 | 63.7973 | 59.4628 | 60.989 | 55.8608 | 0.63797 | 0.59463 | 0.60989 | 0.55861 | 0.043346 | 0.051282 | 10975.073 | 1589.7194 | 9.0817
38929.6077 | 1119 | 1165 | 38929.6077 | 1118 | 1162 | 1786 | 1901 | 68.315 | 71.1233 | 68.254 | 70.9402 | 0.68315 | 0.71123 | 0.68254 | 0.7094 | 0.028083 | 0.026862 | 6643.3759 | 3753.5328 | 14.2955
38929.6079 | 1193 | 1167 | 38929.6079 | 1194 | 1043 | 1803 | 1918 | 72.8327 | 71.2454 | 72.8938 | 63.6752 | 0.72833 | 0.71245 | 0.72894 | 0.63675 | 0.015873 | 0.092186 | 243.9983 | 332.4218 | 16.2694
38929.6081 | 1137 | 1092 | 38929.6081 | 1036 | 969 | 1819.5 | 1934.5 | 69.4139 | 66.6667 | 63.2479 | 59.1575 | 0.69414 | 0.66667 | 0.63248 | 0.59158 | 0.027473 | 0.040904 | 28.1598 | 31.9205 | 2.5699
38929.6083 | 1189 | 1158 | 38929.6083 | 927 | 917 | 1836.5 | 1951.5 | 72.5885 | 70.696 | 56.5934 | 55.9829 | 0.72589 | 0.70696 | 0.56593 | 0.55983 | 0.018926 | 0.006105 | 135.0725 | 177.3104 | 12.9193

## C1-2
Penlight Test 3 |  |  | 2006-07-05 | 14:09 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38929.5857 | 1 | 0 | 38929.5857 | 1 | 0 | -114.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5859 | 1 | 0 | 38929.5859 | 1 | 0 | -98 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5861 | 1 | 0 | 38929.5861 | 1 | 0 | -81.5 | 33.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5863 | 1 | 0 | 38929.5863 | 1 | 0 | -64.5 | 50.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5865 | 1 | 0 | 38929.5865 | 1 | 0 | -47.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5867 | 1 | 0 | 38929.5867 | 1 | 0 | -31 | 84 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5869 | 1 | 0 | 38929.5869 | 2 | 0 | -14 | 101 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38929.5871 | 1 | 0 | 38929.5871 | 1 | 0 | 2.5 | 117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5873 | 1 | 0 | 38929.5873 | 1 | 0 | 19.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5875 | 1 | 0 | 38929.5875 | 1 | 0 | 36.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5877 | 1 | 0 | 38929.5877 | 1 | 0 | 53 | 168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5879 | 1 | 0 | 38929.5879 | 1 | 0 | 70 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5881 | 1 | 0 | 38929.5881 | 1 | 0 | 86.5 | 201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5883 | 1 | 0 | 38929.5883 | 1 | 0 | 103.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5884 | 1 | 0 | 38929.5885 | 1 | 0 | 120.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5886 | 1 | 0 | 38929.5887 | 1 | 0 | 137 | 252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5888 | 1 | 0 | 38929.5889 | 1 | 0 | 154 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.589 | 1 | 0 | 38929.589 | 1 | 0 | 170.5 | 285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5892 | 1 | 0 | 38929.5892 | 1 | 0 | 187.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5894 | 1 | 0 | 38929.5894 | 1 | 0 | 204.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5896 | 1 | 0 | 38929.5896 | 1 | 0 | 221 | 336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5898 | 1 | 0 | 38929.5898 | 1 | 0 | 238 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.59 | 1 | 0 | 38929.59 | 1 | 0 | 254.5 | 369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5902 | 1 | 0 | 38929.5902 | 1 | 0 | 271.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5904 | 1 | 0 | 38929.5904 | 1 | 0 | 288.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5906 | 1 | 0 | 38929.5906 | 1 | 0 | 305 | 420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5908 | 1 | 0 | 38929.5908 | 1 | 0 | 322 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.591 | 1 | 0 | 38929.591 | 1 | 0 | 338.5 | 453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5912 | 1 | 0 | 38929.5912 | 1 | 0 | 355.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5914 | 1 | 0 | 38929.5914 | 1 | 0 | 372.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5916 | 1 | 0 | 38929.5916 | 1 | 0 | 389 | 504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5917 | 1 | 0 | 38929.5918 | 1 | 0 | 406 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5919 | 1 | 0 | 38929.592 | 1 | 0 | 422.5 | 537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5921 | 1 | 0 | 38929.5922 | 1 | 0 | 439.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5923 | 1 | 0 | 38929.5923 | 1 | 0 | 456.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5925 | 1 | 0 | 38929.5925 | 1 | 0 | 473 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5927 | 1 | 0 | 38929.5927 | 1 | 0 | 490 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5929 | 1 | 0 | 38929.5929 | 1 | 0 | 506.5 | 621.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5931 | 1 | 0 | 38929.5931 | 1 | 0 | 523.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5933 | 1 | 0 | 38929.5933 | 1 | 0 | 540.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5935 | 1 | 0 | 38929.5935 | 1 | 0 | 557 | 672 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5937 | 1 | 0 | 38929.5937 | 1 | 0 | 573.5 | 688.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5939 | 1 | 0 | 38929.5939 | 1 | 0 | 590.5 | 705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5941 | 1 | 0 | 38929.5941 | 1 | 0 | 607.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5943 | 1 | 0 | 38929.5943 | 1 | 0 | 624.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5945 | 1 | 0 | 38929.5945 | 1 | 0 | 641 | 756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5947 | 1 | 0 | 38929.5947 | 1 | 0 | 658 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5949 | 1 | 0 | 38929.5949 | 1 | 0 | 674.5 | 789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5951 | 1 | 0 | 38929.5951 | 1 | 0 | 691.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5953 | 1 | 0 | 38929.5953 | 1 | 0 | 708.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5954 | 1 | 0 | 38929.5955 | 1 | 0 | 725 | 840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5956 | 1 | 0 | 38929.5957 | 1 | 0 | 742 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5958 | 1 | 0 | 38929.5958 | 1 | 0 | 758.5 | 873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.596 | 1 | 0 | 38929.596 | 1 | 0 | 775.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5962 | 1 | 0 | 38929.5962 | 1 | 0 | 792 | 907 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5964 | 1 | 0 | 38929.5964 | 1 | 0 | 809 | 924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5966 | 1 | 0 | 38929.5966 | 1 | 0 | 825.5 | 940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5968 | 1 | 0 | 38929.5968 | 1 | 0 | 842.5 | 957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.597 | 1 | 0 | 38929.597 | 1 | 0 | 859.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5972 | 1 | 0 | 38929.5972 | 1 | 0 | 876.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5974 | 1 | 0 | 38929.5974 | 1 | 0 | 893 | 1008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5976 | 1 | 0 | 38929.5976 | 1 | 0 | 910 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5978 | 1 | 0 | 38929.5978 | 1 | 0 | 926.5 | 1041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.598 | 1 | 0 | 38929.598 | 1 | 0 | 943.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5982 | 1 | 0 | 38929.5982 | 1 | 0 | 960 | 1075 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5984 | 1 | 0 | 38929.5984 | 1 | 0 | 977 | 1092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5986 | 1 | 0 | 38929.5986 | 1 | 0 | 993.5 | 1108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5987 | 1 | 0 | 38929.5988 | 1 | 0 | 1010.5 | 1125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5989 | 1 | 0 | 38929.599 | 1 | 0 | 1027.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5991 | 1 | 1 | 38929.5992 | 1 | 0 | 1044 | 1159 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38929.5993 | 1 | 0 | 38929.5994 | 1 | 0 | 1061 | 1176 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5995 | 1 | 0 | 38929.5995 | 1 | 0 | 1077.5 | 1192.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5997 | 1 | 0 |  | 1 | 0 | 1094 | 1209 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.5999 | 1 | 0 | 38929.5999 | 1 | 0 | 1111.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6001 | 1 | 0 | 38929.6001 | 1 | 0 | 1128.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6003 | 1 | 0 | 38929.6003 | 1 | 0 | 1145 | 1260 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6005 | 1 | 0 | 38929.6005 | 1 | 0 | 1161.5 | 1276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38929.6007 | 1 | 1 | 38929.6007 | 1 | 0 | 1178.5 | 1293.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38929.6009 | 2 | 3 | 38929.6009 | 2 | 2 | 1195.5 | 1310.5 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211101.7158 | 222819972.0267 | 70267.3018
38929.6011 | 2 | 3 | 38929.6011 | 2 | 2 | 1212 | 1327 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211101.7158 | 222819972.0267 | 70267.3018
38929.6013 | 2 | 3 | 38929.6013 | 2 | 2 | 1229 | 1344 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211101.7158 | 222819972.0267 | 70267.3018
38929.6015 | 1018 | 985 | 38929.6015 | 1092 | 1062 | 1245.5 | 1360.5 | 62.149 | 60.1343 | 66.6667 | 64.8352 | 0.62149 | 0.60134 | 0.66667 | 0.64835 | 0.020147 | 0.018315 | 1736.8056 | 3278.096 | 10.8389
38929.6017 | 1032 | 998 | 38929.6017 | 991 | 958 | 1262.5 | 1377.5 | 63.0037 | 60.928 | 60.5006 | 58.486 | 0.63004 | 0.60928 | 0.60501 | 0.58486 | 0.020757 | 0.020147 | 4925.3657 | 8280.7935 | 8.2194
38929.6019 | 955 | 987 | 38929.6019 | 1151 | 904 | 1279.5 | 1394.5 | 58.3028 | 60.2564 | 70.2686 | 55.1893 | 0.58303 | 0.60256 | 0.70269 | 0.55189 | 0.019536 | 0.15079 | 104.1248 | 91.3765 | 8.2732
38929.602 | 1026 | 1128 | 38929.6021 | 1177 | 1158 | 1296 | 1411 | 62.6374 | 68.8645 | 71.8559 | 70.696 | 0.62637 | 0.68864 | 0.71856 | 0.70696 | 0.062271 | 0.0116 | 389.9832 | 638.2435 | 3.1409
38929.6022 | 1086 | 1060 | 38929.6023 | 1171 | 1151 | 1313 | 1428 | 66.3004 | 64.7131 | 71.4896 | 70.2686 | 0.663 | 0.64713 | 0.7149 | 0.70269 | 0.015873 | 0.01221 | 7671.5288 | 8404.3094 | 3.0747
38929.6024 | 1032 | 1128 | 38929.6025 | 1016 | 987 | 1329.5 | 1444.5 | 63.0037 | 68.8645 | 62.0269 | 60.2564 | 0.63004 | 0.68864 | 0.62027 | 0.60256 | 0.058608 | 0.017705 | 99.9485 | 114.4508 | 2.2228
38929.6026 | 1051 | 1023 | 38929.6027 | 926 | 902 | 1346.5 | 1461.5 | 64.1636 | 62.4542 | 56.5324 | 55.0672 | 0.64164 | 0.62454 | 0.56532 | 0.55067 | 0.017094 | 0.014652 | 3890.7323 | 145342.8168 | 3.8116
38929.6028 | 1010 | 928 | 38929.6028 | 1188 | 1179 | 1363.5 | 1478.5 | 61.6606 | 56.6545 | 72.5275 | 71.978 | 0.61661 | 0.56654 | 0.72527 | 0.71978 | 0.050061 | 0.0054945 | 109.3286 | 100.1183 | 9.4355
38929.603 | 1093 | 1148 | 38929.603 | 1057 | 1030 | 1380 | 1495 | 66.7277 | 70.0855 | 64.5299 | 62.8816 | 0.66728 | 0.70085 | 0.6453 | 0.62882 | 0.033578 | 0.016484 | 388.6952 | 553.4622 | 9.4421
38929.6032 | 1142 | 1120 | 38929.6032 | 1133 | 1182 | 1397 | 1512 | 69.7192 | 68.3761 | 69.1697 | 72.1612 | 0.69719 | 0.68376 | 0.6917 | 0.72161 | 0.013431 | 0.029915 | 1117.1245 | 1725.1637 | 12.573
38929.6034 | 1175 | 1155 | 38929.6034 | 920 | 1006 | 1413.5 | 1528.5 | 71.7338 | 70.5128 | 56.1661 | 61.4164 | 0.71734 | 0.70513 | 0.56166 | 0.61416 | 0.01221 | 0.052503 | 56.7823 | 70.7739 | 7.7855
38929.6036 | 958 | 925 | 38929.6036 | 1179 | 1180 | 1430.5 | 1545.5 | 58.486 | 56.4713 | 71.978 | 72.0391 | 0.58486 | 0.56471 | 0.71978 | 0.72039 | 0.020147 | 0.0006105 | 42.4388 | 34.4044 | 6.3654
38929.6038 | 997 | 1097 | 38929.6038 | 1148 | 1100 | 1447.5 | 1562.5 | 60.8669 | 66.9719 | 70.0855 | 67.1551 | 0.60867 | 0.66972 | 0.70085 | 0.67155 | 0.06105 | 0.029304 | 295.85 | 395.7075 | 1.3841
38929.604 | 926 | 889 | 38929.604 | 979 | 966 | 1464 | 1579 | 56.5324 | 54.2735 | 59.768 | 58.9744 | 0.56532 | 0.54274 | 0.59768 | 0.58974 | 0.022589 | 0.0079365 | 1602.9688 | 2399.373 | 32.1818
38929.6042 | 1189 | 990 | 38929.6042 | 1145 | 1091 | 1481 | 1596 | 72.5885 | 60.4396 | 69.9023 | 66.6056 | 0.72589 | 0.6044 | 0.69902 | 0.66606 | 0.12149 | 0.032967 | 133.3708 | 200.4778 | 4.4466
38929.6044 | 1184 | 1186 | 38929.6044 | 961 | 851 | 1497.5 | 1612.5 | 72.2833 | 72.4054 | 58.6691 | 51.9536 | 0.72283 | 0.72405 | 0.58669 | 0.51954 | 0.001221 | 0.067155 | 47.5699 | 60.7906 | 8.192
38929.6046 | 950 | 837 | 38929.6046 | 953 | 921 | 1514.5 | 1629.5 | 57.9976 | 51.0989 | 58.1807 | 56.2271 | 0.57998 | 0.51099 | 0.58181 | 0.56227 | 0.068987 | 0.019536 | 554.4191 | 864.9132 | 34.9143
38929.6048 | 1162 | 1113 | 38929.6048 | 1068 | 1088 | 1531.5 | 1646.5 | 70.9402 | 67.9487 | 65.2015 | 66.4225 | 0.7094 | 0.67949 | 0.65201 | 0.66422 | 0.029915 | 0.01221 | 750.0492 | 1430.6951 | 13.6027
38929.605 | 1195 | 1165 | 38929.605 | 1191 | 1159 | 1548 | 1663 | 72.9548 | 71.1233 | 72.7106 | 70.757 | 0.72955 | 0.71123 | 0.72711 | 0.70757 | 0.018315 | 0.019536 | 5237.3558 | 9341.1565 | 20.9755
38929.6052 | 1035 | 836 | 38929.6052 | 936 | 885 | 1565 | 1680 | 63.1868 | 51.0379 | 57.1429 | 54.0293 | 0.63187 | 0.51038 | 0.57143 | 0.54029 | 0.12149 | 0.031136 | 276.1044 | 436.692 | 23.5556
38929.6054 | 986 | 870 | 38929.6054 | 1107 | 1031 | 1581.5 | 1696.5 | 60.1954 | 53.1136 | 67.5824 | 62.9426 | 0.60195 | 0.53114 | 0.67582 | 0.62943 | 0.070818 | 0.046398 | 468.2533 | 697.753 | 25.8393
38929.6056 | 1108 | 1039 | 38929.6056 | 1039 | 944 | 1598.5 | 1713.5 | 67.6435 | 63.431 | 63.431 | 57.6313 | 0.67643 | 0.63431 | 0.63431 | 0.57631 | 0.042125 | 0.057998 | 400.8338 | 571.7199 | 2.7836
38929.6058 | 969 | 854 | 38929.6058 | 1189 | 1153 | 1615.5 | 1730.5 | 59.1575 | 52.1368 | 72.5885 | 70.3907 | 0.59158 | 0.52137 | 0.72589 | 0.70391 | 0.070208 | 0.021978 | 95.9176 | 79.242 | 15.0136
38929.6059 | 1176 | 1160 | 38929.606 | 1047 | 954 | 1632 | 1747 | 71.7949 | 70.8181 | 63.9194 | 58.2418 | 0.71795 | 0.70818 | 0.63919 | 0.58242 | 0.009768 | 0.056777 | 118.6452 | 149.916 | 11.5309
38929.6061 | 936 | 886 | 38929.6062 | 990 | 905 | 1649 | 1764 | 57.1429 | 54.0904 | 60.4396 | 55.2503 | 0.57143 | 0.5409 | 0.6044 | 0.5525 | 0.030525 | 0.051893 | 2714.0613 | 13358.4232 | 32.6024
38929.6063 | 1019 | 934 | 38929.6063 | 924 | 985 | 1665.5 | 1780.5 | 62.21 | 57.0208 | 56.4103 | 60.1343 | 0.6221 | 0.57021 | 0.5641 | 0.60134 | 0.051893 | 0.037241 | 863.6841 | 2241.4749 | 16.4011
38929.6065 | 1033 | 949 | 38929.6065 | 942 | 834 | 1682.5 | 1797.5 | 63.0647 | 57.9365 | 57.5092 | 50.9158 | 0.63065 | 0.57937 | 0.57509 | 0.50916 | 0.051282 | 0.065934 | 11469.2758 | 1272.4017 | 12.8001
38929.6067 | 1197 | 1178 | 38929.6067 | 1102 | 1039 | 1699.5 | 1814.5 | 73.0769 | 71.917 | 67.2772 | 63.431 | 0.73077 | 0.71917 | 0.67277 | 0.63431 | 0.0116 | 0.038462 | 541.459 | 784.4117 | 19.7248
38929.6069 | 1100 | 1036 | 38929.6069 | 927 | 909 | 1716 | 1831 | 67.1551 | 63.2479 | 56.5934 | 55.4945 | 0.67155 | 0.63248 | 0.56593 | 0.55495 | 0.039072 | 0.010989 | 453.6331 | 650.2937 | 1.9225
38929.6071 | 1135 | 1179 | 38929.6071 | 932 | 1022 | 1733 | 1848 | 69.2918 | 71.978 | 56.8987 | 62.3932 | 0.69292 | 0.71978 | 0.56899 | 0.62393 | 0.026862 | 0.054945 | 92.1169 | 115.8477 | 9.1491
38929.6073 | 1192 | 1166 | 38929.6073 | 1171 | 1133 | 1749.5 | 1864.5 | 72.7717 | 71.1844 | 71.4896 | 69.1697 | 0.72772 | 0.71184 | 0.7149 | 0.6917 | 0.015873 | 0.023199 | 2288.4065 | 8184.0531 | 20.7567
38929.6075 | 951 | 1054 | 38929.6075 | 1106 | 1150 | 1766.5 | 1881.5 | 58.0586 | 64.3468 | 67.5214 | 70.2076 | 0.58059 | 0.64347 | 0.67521 | 0.70208 | 0.062882 | 0.026862 | 73.1033 | 70.902 | 4.2518
38929.6077 | 998 | 998 | 38929.6077 | 1162 | 1120 | 1783.5 | 1898.5 | 60.928 | 60.928 | 70.9402 | 68.3761 | 0.60928 | 0.60928 | 0.7094 | 0.68376 | 0 | 0.025641 | 136.83 | 122.4699 | 6.4549
38929.6079 | 1117 | 1062 | 38929.6079 | 1034 | 1128 | 1800 | 1915 | 68.1929 | 64.8352 | 63.1258 | 68.8645 | 0.68193 | 0.64835 | 0.63126 | 0.68864 | 0.033578 | 0.057387 | 304.3595 | 390.0809 | 4.9451
38929.6081 | 957 | 869 | 38929.6081 | 1008 | 1109 | 1817 | 1932 | 58.4249 | 53.0525 | 61.5385 | 67.7045 | 0.58425 | 0.53053 | 0.61538 | 0.67705 | 0.053724 | 0.061661 | 3311.6454 | 1636.7729 | 31.127
38929.6083 | 975 | 892 | 38929.6083 | 1195 | 1035 | 1833.5 | 1948.5 | 59.5238 | 54.4567 | 72.9548 | 63.1868 | 0.59524 | 0.54457 | 0.72955 | 0.63187 | 0.050672 | 0.09768 | 182.6476 | 165.1642 | 17.1793

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 10 |  |  | 2006-07-27 | 15:36
PVC | 3-C | Air Drop (Horizontal Run)
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | Minimums
-111.8333 | 211202 |  | -108.1667 | 211202 | -106.5 | 211202 | -104.5 | 211202 | -111.8333 | 211202
-95.3333 | 211202 |  | -91.5 | 211202 | -89.6667 | 211202 | -87.8333 | 211202 | -95.3333 | 211202
-78.5 | 211202 |  | -74.8333 | 211202 | -73 | 211202 | -71 | 211202 | -78.5 | 211202
-61.6667 | 211202 |  | -58 | 211202 | -56 | 211202 | -54.3333 | 211202 | -61.6667 | 211202
-44.6667 | 211202 |  | -41.1667 | 211202 | -39.1667 | 211202 | -37.3333 | 211202 | -44.6667 | 211202
-28.1667 | 211202 |  | -24.3333 | 211202 | -22.5 | 211202 | -20.6667 | 175985 | -28.1667 | 175985
-11.3333 | 211202 |  | -7.5 | 175985 | -5.6667 | 164246 | -3.8333 | 211202 | -11.3333 | 164246
5.5 | 211202 |  | 9.1667 | 211202 | 11 | 211202 | 13 | 211202 | 5.5 | 211202
22.3333 | 211202 |  | 26 | 211202 | 28 | 211202 | 29.6667 | 211202 | 22.3333 | 211202
39.1667 | 211202 |  | 42.8333 | 211202 | 44.6667 | 211202 | 46.6667 | 211202 | 39.1667 | 211202
55.8333 | 211202 |  | 59.6667 | 211202 | 61.5 | 211202 | 63.3333 | 175985 | 55.8333 | 175985
72.6667 | 211202 |  | 76.5 | 211202 | 78.3333 | 175985 | 80.1667 | 211202 | 72.6667 | 175985
89.5 | 211202 |  | 93.1667 | 211202 | 95 | 211202 | 97 | 211202 | 89.5 | 211202
106.3333 | 211202 |  | 110 | 211202 | 112 | 211202 | 113.6667 | 211202 | 106.3333 | 211202
123.1667 | 211202 |  | 126.8333 | 211202 | 128.6667 | 211202 | 130.6667 | 211202 | 123.1667 | 211202
139.8333 | 211202 |  | 143.6667 | 148828417.3467 | 145.5 | 211202 | 147.3333 | 211202 | 139.8333 | 211202
156.6667 | 211202 |  | 160.5 | 211202 | 162.3333 | 211202 | 164.1667 | 211202 | 156.6667 | 211202
173.5 | 211202 |  | 177.1667 | 211202 | 179 | 211202 | 181 | 211202 | 173.5 | 211202
190.3333 | 211202 |  | 194.3333 | 211202 | 196.3333 | 211202 | 197.6667 | 211202 | 190.3333 | 211202
207.1667 | 211202 |  | 210.8333 | 211202 | 212.6667 | 211202 | 214.6667 | 211202 | 207.1667 | 211202
223.8333 | 211202 |  | 227.6667 | 211202 | 229.5 | 211202 | 231.3333 | 211202 | 223.8333 | 211202
240.6667 | 211202 |  | 244.5 | 211202 | 246.3333 | 211202 | 248.1667 | 211202 | 240.6667 | 211202
257.5 | 211202 |  | 261.1667 | 211202 | 263 | 211202 | 265 | 211202 | 257.5 | 211202
274.3333 | 211202 |  | 278 | 211202 | 280 | 211202 | 281.6667 | 211202 | 274.3333 | 211202
291.1667 | 211202 |  | 294.8333 | 211202 | 296.6667 | 211202 | 298.6667 | 211202 | 291.1667 | 211202
307.8333 | 211202 |  | 311.6667 | 211202 | 313.5 | 211202 | 315.3333 | 211202 | 307.8333 | 211202
324.6667 | 211202 |  | 328.5 | 211202 | 330.3333 | 175985 | 332.1667 | 211202 | 324.6667 | 175985
341.5 | 211202 |  | 345.1667 | 211202 | 347 | 211202 | 349 | 211202 | 341.5 | 211202
358.3333 | 211202 |  | 362 | 211202 | 364 | 211202 | 365.6667 | 211202 | 358.3333 | 211202
375.1667 | 211202 |  | 378.8333 | 211202 | 380.6667 | 211202 | 382.6667 | 211202 | 375.1667 | 211202
391.8333 | 211202 |  | 395.6667 | 211202 | 397.5 | 211202 | 399.3333 | 211202 | 391.8333 | 211202
408.6667 | 211202 |  | 412.5 | 211202 | 414.3333 | 211202 | 416.1667 | 211202 | 408.6667 | 211202
425.5 | 211202 |  | 429.1667 | 211202 | 431 | 211202 | 433 | 211202 | 425.5 | 211202
442.3333 | 211202 |  | 446 | 211202 | 448 | 211202 | 449.6667 | 211202 | 442.3333 | 211202
459.1667 | 211202 |  | 462.8333 | 211202 | 464.6667 | 211202 | 466.6667 | 211202 | 459.1667 | 211202
475.8333 | 211202 |  | 479.6667 | 211202 | 481.5 | 211202 | 483.3333 | 211202 | 475.8333 | 211202
492.6667 | 211202 |  | 496.5 | 211202 | 498.3333 | 211202 | 500.1667 | 211202 | 492.6667 | 211202
509.5 | 211202 |  | 513.1667 | 211202 | 515 | 211202 | 517 | 211202 | 509.5 | 211202
526.3333 | 211202 |  | 530 | 211202 | 532 | 211202 | 533.6667 | 211202 | 526.3333 | 211202
543.1667 | 211202 |  | 546.8333 | 211202 | 548.6667 | 211202 | 550.6667 | 211202 | 543.1667 | 211202
559.8333 | 175985 |  | 563.6667 | 211202 | 565.5 | 211202 | 567.3333 | 211202 | 559.8333 | 175985
576.5 | 211202 |  | 580.3333 | 211202 | 582.3333 | 211202 | 584.1667 | 211202 | 576.5 | 211202
593.5 | 211202 |  | 597.1667 | 211202 | 599 | 211202 | 601 | 211202 | 593.5 | 211202
610.3333 | 211202 |  | 614 | 211202 | 616 | 211202 | 617.6667 | 211202 | 610.3333 | 211202
627.1667 | 211202 |  | 630.8333 | 211202 | 632.6667 | 211202 | 634.6667 | 211202 | 627.1667 | 211202
643.6667 | 211202 |  | 647.6667 | 211202 | 649.3333 | 211202 | 651.3333 | 211202 | 643.6667 | 211202
660.6667 | 211202 |  | 664.5 | 211202 | 666.1667 | 211202 | 668 | 211202 | 660.6667 | 211202
677.5 | 211202 |  | 681.1667 | 211202 | 683 | 211202 | 685 | 211202 | 677.5 | 211202
694.3333 | 211202 |  | 698 | 211202 | 700 | 211202 | 701.6667 | 211202 | 694.3333 | 211202
711.1667 | 211202 |  | 714.8333 | 211202 | 716.5 | 211202 | 718.5 | 211202 | 711.1667 | 211202
727.6667 | 211202 |  | 731.5 | 211202 | 733.3333 | 211202 | 735.1667 | 211202 | 727.6667 | 211202
744.6667 | 211202 |  | 748.3333 | 211202 | 750 | 211202 | 752 | 211202 | 744.6667 | 211202
761.3333 | 211202 |  | 765.1667 | 211202 | 767 | 211202 | 768.8333 | 211202 | 761.3333 | 211202
778.3333 | 211202 |  | 782 | 211202 | 784 | 211202 | 785.6667 | 211202 | 778.3333 | 211202
794.8333 | 211202 |  | 798.6667 | 211202 | 800.5 | 211202 | 802.3333 | 211202 | 794.8333 | 211202
811.6667 | 211202 |  | 815.5 | 211202 | 817.3333 | 211202 | 819.1667 | 211202 | 811.6667 | 211202
828.5 | 211202 |  | 832.1667 | 211202 | 834 | 211202 | 836 | 211202 | 828.5 | 211202
845.5 | 211202 |  | 849.1667 | 211202 | 851 | 211202 | 853 | 211202 | 845.5 | 211202
862.3333 | 211202 |  | 866 | 211202 | 868 | 211202 | 869.6667 | 211202 | 862.3333 | 211202
879.1667 | 211202 |  | 882.8333 | 211202 | 884.5 | 211202 | 886.5 | 211202 | 879.1667 | 211202
895.6667 | 211202 |  | 899.6667 | 211202 | 901.3333 | 211202 | 903.3333 | 211202 | 895.6667 | 211202
912.6667 | 211202 |  | 916.3333 | 211202 | 918 | 211202 | 920 | 211202 | 912.6667 | 211202
929.3333 | 211202 |  | 933.1667 | 211202 | 935 | 211202 | 936.8333 | 211202 | 929.3333 | 211202
946.3333 | 211202 |  | 950 | 211202 | 952 | 211202 | 953.6667 | 211202 | 946.3333 | 211202
963 | 211202 |  | 966.6667 | 211202 | 968.5 | 175985 | 970.5 | 211202 | 963 | 175985
979.8333 | 211202 |  | 983.5 | 211202 | 985.5 | 211202 | 987.1667 | 211202 | 979.8333 | 211202
996.5 | 211202 |  | 1000.3333 | 211202 | 1002.1667 | 211202 | 1004 | 211202 | 996.5 | 211202
1013.3333 | 211202 |  | 1017 | 211202 | 1019 | 211202 | 1020.6667 | 211202 | 1013.3333 | 211202
1030.1667 | 211202 |  | 1034 | 211202 | 1035.8333 | 211202 | 1037.6667 | 211202 | 1030.1667 | 211202
1046.8333 | 148828417.3467 |  | 1050.6667 | 211202 | 1052.5 | 211202 | 1054.3333 | 211202 | 1046.8333 | 211202
1063.6667 | 211202 |  | 1067.5 | 211202 | 1069.3333 | 211202 | 1071.1667 | 211202 | 1063.6667 | 211202
1080.5 | 211202 |  | 1084.3333 | 211202 | 1086.1667 | 211202 | 1088 | 211202 | 1080.5 | 211202
1097.1667 | 211202 |  | 1100.8333 | 211202 | 1103 | 211202 | 1104.6667 | 211202 | 1097.1667 | 211202
1114.1667 | 211202 |  | 1117.8333 | 211202 | 1119.6667 | 211202 | 1121.6667 | 211202 | 1114.1667 | 211202
1131.1667 | 211202 |  | 1134.8333 | 211202 | 1136.5 | 211202 | 1138.5 | 211202 | 1131.1667 | 211202
1147.6667 | 211202 |  | 1151.5 | 211202 | 1153.3333 | 211202 | 1155.1667 | 211202 | 1147.6667 | 211202
1164.5 | 164617.7042 |  | 1168.1667 | 141944.9844 | 1170 | 74414192.0067 | 1172 | 102722.8467 | 1164.5 | 102722.8467
1181.3333 | 297375432.533 |  | 1185 | 79928.1385 | 1187 | 111590.3366 | 1188.6667 | 79937.1011 | 1181.3333 | 79928.1385
1198.1667 | 148758881.0389 |  | 1201.8333 | 74280904.8345 | 1203.6667 | 102198.0206 | 1205.6667 | 44672.6252 | 1198.1667 | 44672.6252
1214.8333 | 141239.86 |  | 1218.6667 | 74281747.9007 | 1220.5 | 105772.9189 | 1222.3333 | 31497.2878 | 1214.8333 | 31497.2878
1231.6667 | 74347023.0727 |  | 1235.5 | 74282487.8855 | 1237.3333 | 114734.0846 | 1239.1667 | 18749.332 | 1231.6667 | 18749.332
1248.5 | 2675.4221 |  | 1252.1667 | 1593.3951 | 1254 | 3994.0716 | 1256 | 4097.506 | 1248.5 | 1593.3951
1265.3333 | 9529.6317 |  | 1269 | 3055.842 | 1271 | 567.0834 | 1272.6667 | 1465.2318 | 1265.3333 | 567.0834
1282.1667 | 943.0752 |  | 1285.8333 | 234.1958 | 1287.6667 | 404.8666 | 1289.6667 | 2797.7462 | 1282.1667 | 234.1958
1298.8333 | 1933.6918 |  | 1302.6667 | 285.641 | 1304.5 | 10466.332 | 1306.3333 | 7082.079 | 1298.8333 | 285.641
1315.6667 | 2805.7613 |  | 1319.5 | 4980.076 | 1321.3333 | 7553.0144 | 1323.1667 | 7023.9084 | 1315.6667 | 2805.7613
1332.5 | 118.0561 |  | 1336.1667 | 322.1175 | 1338 | 6009.979 | 1340 | 1679.2003 | 1332.5 | 118.0561
1349.3333 | 1658.3976 |  | 1353 | 48553.4074 | 1355 | 289.1192 | 1356.6667 | 549.1575 | 1349.3333 | 289.1192
1366.1667 | 1867.989 |  | 1369.8333 | 125.4016 | 1371.6667 | 1211.6646 | 1373.6667 | 82421.9776 | 1366.1667 | 125.4016
1382.8333 | 2231.977 |  | 1386.6667 | 515.0442 | 1388.5 | 7704.9955 | 1390.3333 | 585.9056 | 1382.8333 | 515.0442
1399.6667 | 2979.1954 |  | 1403.5 | 3250.2075 | 1405.3333 | 6658.6995 | 1407.1667 | 1607.9178 | 1399.6667 | 1607.9178
1416.5 | 1730.0923 |  | 1420.1667 | 98.479 | 1422 | 974.2086 | 1424 | 13487.7876 | 1416.5 | 98.479
1433.3333 | 765.6215 |  | 1437 | 379.7222 | 1439 | 1781.0236 | 1440.6667 | 452.1718 | 1433.3333 | 379.7222
1450.1667 | 113.277 |  | 1453.8333 | 836.2131 | 1455.6667 | 368.9049 | 1457.6667 | 1885.1694 | 1450.1667 | 113.277
1466.8333 | 1295.5643 |  | 1470.6667 | 1284.4784 | 1472.5 | 950.1629 | 1474.3333 | 52832.0299 | 1466.8333 | 950.1629
1483.6667 | 528.3237 |  | 1487.5 | 1998.76 | 1489.3333 | 321.9279 | 1491.1667 | 1222.318 | 1483.6667 | 321.9279
1500.5 | 143.0073 |  | 1504.1667 | 1334.9747 | 1506 | 248.2154 | 1508 | 1482.9669 | 1500.5 | 143.0073
1517.3333 | 794.6924 |  | 1521 | 1446.8265 | 1523 | 1448.8689 | 1524.6667 | 3358.0094 | 1517.3333 | 794.6924
1534.1667 | 489.5381 |  | 1537.8333 | 635.3608 | 1539.6667 | 760.5061 | 1541.6667 | 526.5976 | 1534.1667 | 489.5381
1550.8333 | 3201.4855 |  | 1554.6667 | 5844.6616 | 1556.5 | 2104.8792 | 1558.3333 | 1738.6221 | 1550.8333 | 1738.6221
1567.6667 | 367.2675 |  | 1571.5 | 651.751 | 1573.3333 | 2388.2949 | 1575.1667 | 2624.5779 | 1567.6667 | 367.2675
1584.5 | 572.4924 |  | 1588.1667 | 2412.9776 | 1590 | 5459.063 | 1592 | 1267.5681 | 1584.5 | 572.4924
1601.3333 | 703.4083 |  | 1605 | 318.3019 | 1607 | 291.5184 | 1608.6667 | 1783.9117 | 1601.3333 | 291.5184
1617.8333 | 102.1608 |  | 1621.8333 | 399.625 | 1623.6667 | 652.7129 | 1625.3333 | 264.0759 | 1617.8333 | 102.1608
1634.8333 | 516.9961 |  | 1638.6667 | 342.7512 | 1640.5 | 1204.1882 | 1642.3333 | 1309.0962 | 1634.8333 | 342.7512
1651.6667 | 1181.8263 |  | 1655.5 | 4602.0387 | 1657.3333 | 408.2892 | 1659.1667 | 186.8032 | 1651.6667 | 186.8032
1668.5 | 310.2238 |  | 1672.1667 | 1495.458 | 1674 | 1009.4277 | 1676 | 1554.8508 | 1668.5 | 310.2238
1685.3333 | 4065.6265 |  | 1689 | 623.1675 | 1691 | 1390.1615 | 1692.6667 | 5376.9535 | 1685.3333 | 623.1675
1702.1667 | 755.1785 |  | 1705.8333 | 1351.1861 | 1707.6667 | 1890.3466 | 1709.6667 | 1118.4101 | 1702.1667 | 755.1785
1718.8333 | 953.0771 |  | 1722.6667 | 354.7243 | 1724.5 | 405.7078 | 1726.3333 | 907.4064 | 1718.8333 | 354.7243
1735.6667 | 260.8253 |  | 1739.5 | 320.6774 | 1741.3333 | 260.2476 | 1743.1667 | 384.1684 | 1735.6667 | 260.2476
1752.5 | 914.381 |  | 1756.1667 | 2937.9436 | 1758 | 2609.4953 | 1760 | 751.0594 | 1752.5 | 751.0594
1769.3333 | 3729.3896 |  | 1773 | 1153.7871 | 1775 | 1397.9434 | 1776.6667 | 1233.2533 | 1769.3333 | 1153.7871
1786.1667 | 38900.6843 |  | 1789.8333 | 593.9653 | 1791.6667 | 5627.1901 | 1793.6667 | 16052.1799 | 1786.1667 | 593.9653
1802.8333 | 274.4891 |  | 1806.6667 | 3295.7823 | 1808.5 | 306.2381 | 1810.3333 | 825.2668 | 1802.8333 | 274.4891
1819.6667 | 2279.5068 |  | 1823.5 | 847.1701 | 1825.1667 | 1516.8775 | 1827 | 2253.5226 | 1819.6667 | 847.1701
1836.5 | 346.0862 |  | 1840.1667 | 287.2352 | 1842 | 417.7792 | 1844 | 794.2763 | 1836.5 | 287.2352

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 10 |  |  | 2006-07-27 | 15:36
38929.5857 | 1 | 0 | 1 | PVC | 3-C | Air Drop (Horizontal Run)
38929.5859 | 1 | 0 | 1 | 300 C | 6.1 kW/m2 |  | Conductors
38929.5861 | 1 | 0 | 1
38929.5863 | 1 | 0 | 1
38929.5865 | 1 | 0 | 1
38929.5867 | 1 | 0 | 1
38929.5869 | 1 | 0 | 1
38929.5871 | 1 | 0 | 1
38929.5873 | 1 | 0 | 1
38929.5875 | 1 | 0 | 1
38929.5877 | 1 | 0 | 1
38929.5879 | 1 | 0 | 1
38929.5881 | 1 | 0 | 1
38929.5883 | 1 | 0 | 1
38929.5884 | 1 | 0 | 1
38929.5886 | 1 | 0 | 1
38929.5888 | 1 | 0 | 1
38929.589 | 1 | 0 | 1
38929.5892 | 1 | 0 | 1
38929.5894 | 1 | 0 | 1
38929.5896 | 1 | 0 | 1
38929.5898 | 1 | 0 | 1
38929.59 | 1 | 0 | 1
38929.5902 | 1 | 0 | 1
38929.5904 | 1 | 0 | 1
38929.5906 | 1 | 0 | 1
38929.5908 | 1 | 0 | 1
38929.591 | 1 | 0 | 1
38929.5912 | 1 | 0 | 1
38929.5914 | 1 | 0 | 1
38929.5916 | 1 | 0 | 1
38929.5917 | 1 | 0 | 1
38929.5919 | 1 | 0 | 1
38929.5921 | 1 | 0 | 1
38929.5923 | 1 | 0 | 1
38929.5925 | 1 | 0 | 1
38929.5927 | 1 | 0 | 1
38929.5929 | 1 | 0 | 1
38929.5931 | 1 | 0 | 1
38929.5933 | 1 | 0 | 1
38929.5935 | 1 | 0 | 1
38929.5937 | 1 | 0 | 1
38929.5939 | 1 | 0 | 1
38929.5941 | 1 | 0 | 1
38929.5943 | 1 | 0 | 1
38929.5945 | 1 | 0 | 1
38929.5947 | 1 | 0 | 1
38929.5949 | 1 | 0 | 1
38929.5951 | 1 | 0 | 1
38929.5953 | 1 | 0 | 1
38929.5954 | 1 | 0 | 1
38929.5956 | 1 | 0 | 1
38929.5958 | 1 | 0 | 1
38929.596 | 1 | 0 | 1
38929.5962 | 1 | 0 | 1
38929.5964 | 1 | 0 | 1
38929.5966 | 1 | 0 | 1
38929.5968 | 1 | 0 | 1
38929.597 | 1 | 0 | 1
38929.5972 | 1 | 0 | 1
38929.5974 | 1 | 0 | 1
38929.5976 | 1 | 0 | 1
38929.5978 | 1 | 0 | 1
38929.598 | 1 | 0 | 1
38929.5982 | 1 | 0 | 1
38929.5984 | 1 | 0 | 1
38929.5986 | 1 | 0 | 1
38929.5987 | 1 | 0 | 1
38929.5989 | 1 | 0 | 1
38929.5991 | 1 | 1 | 1
38929.5993 | 1 | 0 | 1
38929.5995 | 1 | 0 | 1
38929.5997 | 1 | 0 | 1
38929.5999 | 1 | 0 | 1
38929.6001 | 1 | 0 | 1
38929.6003 | 1 | 0 | 1
38929.6005 | 1 | 0 | 1
38929.6007 | 1 | 1 | 1
38929.6009 | 2 | 3 | 1
38929.6011 | 2 | 3 | 1
38929.6013 | 2 | 3 | 1
38929.6015 | 1018 | 985 | 1
38929.6017 | 1032 | 998 | 1
38929.6019 | 955 | 987 | 1
38929.602 | 1026 | 1128 | 1
38929.6022 | 1086 | 1060 | 1
38929.6024 | 1032 | 1128 | 1
38929.6026 | 1051 | 1023 | 1
38929.6028 | 1010 | 928 | 1
38929.603 | 1093 | 1148 | 1
38929.6032 | 1142 | 1120 | 1
38929.6034 | 1175 | 1155 | 1
38929.6036 | 958 | 925 | 1
38929.6038 | 997 | 1097 | 1
38929.604 | 926 | 889 | 1
38929.6042 | 1189 | 990 | 1
38929.6044 | 1184 | 1186 | 1
38929.6046 | 950 | 837 | 1
38929.6048 | 1162 | 1113 | 1
38929.605 | 1195 | 1165 | 1
38929.6052 | 1035 | 836 | 1
38929.6054 | 986 | 870 | 1
38929.6056 | 1108 | 1039 | 1
38929.6058 | 969 | 854 | 1
38929.6059 | 1176 | 1160 | 1
38929.6061 | 936 | 886 | 1
38929.6063 | 1019 | 934 | 1
38929.6065 | 1033 | 949 | 1
38929.6067 | 1197 | 1178 | 1
38929.6069 | 1100 | 1036 | 1
38929.6071 | 1135 | 1179 | 1
38929.6073 | 1192 | 1166 | 1
38929.6075 | 951 | 1054 | 1
38929.6077 | 998 | 998 | 1
38929.6079 | 1117 | 1062 | 1
38929.6081 | 957 | 869 | 1
38929.6083 | 975 | 892 | 1
38929.5857 | 1 | 0 | 2
38929.5859 | 1 | 0 | 2
38929.5861 | 1 | 0 | 2
38929.5863 | 1 | 0 | 2
38929.5865 | 1 | 0 | 2
38929.5867 | 1 | 0 | 2
38929.5869 | 2 | 0 | 2
38929.5871 | 1 | 0 | 2
38929.5873 | 1 | 0 | 2
38929.5875 | 1 | 0 | 2
38929.5877 | 1 | 0 | 2
38929.5879 | 1 | 0 | 2
38929.5881 | 1 | 0 | 2
38929.5883 | 1 | 0 | 2
38929.5885 | 1 | 0 | 2
38929.5887 | 1 | 0 | 2
38929.5889 | 1 | 0 | 2
38929.589 | 1 | 0 | 2
38929.5892 | 1 | 0 | 2
38929.5894 | 1 | 0 | 2
38929.5896 | 1 | 0 | 2
38929.5898 | 1 | 0 | 2
38929.59 | 1 | 0 | 2
38929.5902 | 1 | 0 | 2
38929.5904 | 1 | 0 | 2
38929.5906 | 1 | 0 | 2
38929.5908 | 1 | 0 | 2
38929.591 | 1 | 0 | 2
38929.5912 | 1 | 0 | 2
38929.5914 | 1 | 0 | 2
38929.5916 | 1 | 0 | 2
38929.5918 | 1 | 0 | 2
38929.592 | 1 | 0 | 2
38929.5922 | 1 | 0 | 2
38929.5923 | 1 | 0 | 2
38929.5925 | 1 | 0 | 2
38929.5927 | 1 | 0 | 2
38929.5929 | 1 | 0 | 2
38929.5931 | 1 | 0 | 2
38929.5933 | 1 | 0 | 2
38929.5935 | 1 | 0 | 2
38929.5937 | 1 | 0 | 2
38929.5939 | 1 | 0 | 2
38929.5941 | 1 | 0 | 2
38929.5943 | 1 | 0 | 2
38929.5945 | 1 | 0 | 2
38929.5947 | 1 | 0 | 2
38929.5949 | 1 | 0 | 2
38929.5951 | 1 | 0 | 2
38929.5953 | 1 | 0 | 2
38929.5955 | 1 | 0 | 2
38929.5957 | 1 | 0 | 2
38929.5958 | 1 | 0 | 2
38929.596 | 1 | 0 | 2
38929.5962 | 1 | 0 | 2
38929.5964 | 1 | 0 | 2
38929.5966 | 1 | 0 | 2
38929.5968 | 1 | 0 | 2
38929.597 | 1 | 0 | 2
38929.5972 | 1 | 0 | 2
38929.5974 | 1 | 0 | 2
38929.5976 | 1 | 0 | 2
38929.5978 | 1 | 0 | 2
38929.598 | 1 | 0 | 2
38929.5982 | 1 | 0 | 2
38929.5984 | 1 | 0 | 2
38929.5986 | 1 | 0 | 2
38929.5988 | 1 | 0 | 2
38929.599 | 1 | 0 | 2
38929.5992 | 1 | 0 | 2
38929.5994 | 1 | 0 | 2
38929.5995 | 1 | 0 | 2
38929.5999 | 1 | 0 | 2
38929.6001 | 1 | 1 | 2
38929.6003 | 1 | 0 | 2
38929.6005 | 1 | 0 | 2
38929.6007 | 1 | 1 | 2
38929.6009 | 2 | 2 | 2
38929.6011 | 2 | 2 | 2
38929.6013 | 2 | 2 | 2
38929.6015 | 1092 | 1062 | 2
38929.6017 | 991 | 958 | 2
38929.6019 | 1151 | 904 | 2
38929.6021 | 1177 | 1158 | 2
38929.6023 | 1171 | 1151 | 2
38929.6025 | 1016 | 987 | 2
38929.6027 | 926 | 902 | 2
38929.6028 | 1188 | 1179 | 2
38929.603 | 1057 | 1030 | 2
38929.6032 | 1133 | 1182 | 2
38929.6034 | 920 | 1006 | 2
38929.6036 | 1179 | 1180 | 2
38929.6038 | 1148 | 1100 | 2
38929.604 | 979 | 966 | 2
38929.6042 | 1145 | 1091 | 2
38929.6044 | 961 | 851 | 2
38929.6046 | 953 | 921 | 2
38929.6048 | 1068 | 1088 | 2
38929.605 | 1191 | 1159 | 2
38929.6052 | 936 | 885 | 2
38929.6054 | 1107 | 1031 | 2
38929.6056 | 1039 | 944 | 2
38929.6058 | 1189 | 1153 | 2
38929.606 | 1047 | 954 | 2
38929.6062 | 990 | 905 | 2
38929.6063 | 924 | 985 | 2
38929.6065 | 942 | 834 | 2
38929.6067 | 1102 | 1039 | 2
38929.6069 | 927 | 909 | 2
38929.6071 | 932 | 1022 | 2
38929.6073 | 1171 | 1133 | 2
38929.6075 | 1106 | 1150 | 2
38929.6077 | 1162 | 1120 | 2
38929.6079 | 1034 | 1128 | 2
38929.6081 | 1008 | 1109 | 2
38929.6083 | 1195 | 1035 | 2
38929.5858 | 1 | 0 | 3
38929.5859 | 1 | 0 | 3
38929.5861 | 1 | 0 | 3
38929.5863 | 1 | 0 | 3
38929.5865 | 1 | 0 | 3
38929.5867 | 1 | 0 | 3
38929.5869 | 1 | 0 | 3
38929.5871 | 1 | 0 | 3
38929.5873 | 1 | 0 | 3
38929.5875 | 1 | 0 | 3
38929.5877 | 1 | 0 | 3
38929.5879 | 1 | 0 | 3
38929.5881 | 1 | 0 | 3
38929.5883 | 1 | 0 | 3
38929.5885 | 1 | 0 | 3
38929.5887 | 1 | 0 | 3
38929.5889 | 1 | 0 | 3
38929.5891 | 1 | 0 | 3
38929.5893 | 1 | 0 | 3
38929.5894 | 1 | 0 | 3
38929.5896 | 1 | 0 | 3
38929.5898 | 1 | 0 | 3
38929.59 | 1 | 0 | 3
38929.5902 | 1 | 0 | 3
38929.5904 | 1 | 0 | 3
38929.5906 | 1 | 0 | 3
38929.5908 | 1 | 0 | 3
38929.591 | 1 | 0 | 3
38929.5912 | 1 | 0 | 3
38929.5914 | 1 | 0 | 3
38929.5916 | 1 | 0 | 3
38929.5918 | 1 | 0 | 3
38929.592 | 1 | 0 | 3
38929.5922 | 1 | 0 | 3
38929.5924 | 1 | 0 | 3
38929.5926 | 1 | 0 | 3
38929.5928 | 1 | 0 | 3
38929.593 | 1 | 0 | 3
38929.5931 | 1 | 0 | 3
38929.5933 | 1 | 0 | 3
38929.5935 | 2 | 0 | 3
38929.5937 | 1 | 0 | 3
38929.5939 | 1 | 0 | 3
38929.5941 | 1 | 0 | 3
38929.5943 | 1 | 0 | 3
38929.5945 | 1 | 0 | 3
38929.5947 | 1 | 0 | 3
38929.5949 | 1 | 0 | 3
38929.5951 | 1 | 0 | 3
38929.5953 | 1 | 0 | 3
38929.5955 | 1 | 0 | 3
38929.5957 | 1 | 0 | 3
38929.5959 | 1 | 0 | 3
38929.5961 | 1 | 0 | 3
38929.5963 | 1 | 0 | 3
38929.5964 | 1 | 0 | 3
38929.5966 | 1 | 0 | 3
38929.5968 | 1 | 0 | 3
38929.597 | 1 | 0 | 3
38929.5972 | 1 | 0 | 3
38929.5974 | 1 | 0 | 3
38929.5976 | 1 | 0 | 3
38929.5978 | 1 | 0 | 3
38929.598 | 1 | 0 | 3
38929.5982 | 1 | 0 | 3
38929.5984 | 1 | 0 | 3
38929.5986 | 1 | 0 | 3
38929.5988 | 1 | 0 | 3
38929.599 | 1 | 0 | 3
38929.5992 | 1 | 0 | 3
38929.5994 | 1 | 0 | 3
38929.5996 | 1 | 0 | 3
38929.5998 | 1 | 0 | 3
38929.5999 | 1 | 0 | 3
38929.6001 | 1 | 0 | 3
38929.6003 | 1 | 0 | 3
38929.6005 | 1 | 0 | 3
38929.6007 | 1 | 1 | 3
38929.6009 | 1 | 1 | 3
38929.6011 | 2 | 1 | 3
38929.6013 | 2 | 2 | 3
38929.6015 | 1138 | 1186 | 3
38929.6017 | 1064 | 1037 | 3
38929.6019 | 919 | 941 | 3
38929.6021 | 959 | 927 | 3
38929.6023 | 975 | 1093 | 3
38929.6025 | 927 | 957 | 3
38929.6027 | 988 | 957 | 3
38929.6029 | 1177 | 1159 | 3
38929.6031 | 1154 | 1133 | 3
38929.6033 | 1102 | 1078 | 3
38929.6034 | 968 | 1005 | 3
38929.6036 | 1110 | 1147 | 3
38929.6038 | 1175 | 843 | 3
38929.604 | 925 | 891 | 3
38929.6042 | 1140 | 1083 | 3
38929.6044 | 1186 | 1108 | 3
38929.6046 | 1088 | 1013 | 3
38929.6048 | 1143 | 1185 | 3
38929.605 | 991 | 881 | 3
38929.6052 | 1162 | 815 | 3
38929.6054 | 1168 | 1122 | 3
38929.6056 | 973 | 851 | 3
38929.6058 | 1197 | 930 | 3
38929.606 | 1169 | 1123 | 3
38929.6062 | 1076 | 1005 | 3
38929.6064 | 1196 | 960 | 3
38929.6066 | 949 | 852 | 3
38929.6067 | 1010 | 924 | 3
38929.6069 | 979 | 886 | 3
38929.6071 | 971 | 958 | 3
38929.6073 | 935 | 849 | 3
38929.6075 | 1045 | 974 | 3
38929.6077 | 1119 | 1165 | 3
38929.6079 | 1193 | 1167 | 3
38929.6081 | 1137 | 1092 | 3
38929.6083 | 1189 | 1158 | 3
38929.5858 | 1 | 0 | 4
38929.586 | 1 | 0 | 4
38929.5862 | 1 | 0 | 4
38929.5864 | 1 | 0 | 4
38929.5866 | 1 | 0 | 4
38929.5867 | 1 | 0 | 4
38929.5869 | 3 | 0 | 4
38929.5871 | 1 | 0 | 4
38929.5873 | 1 | 0 | 4
38929.5875 | 1 | 0 | 4
38929.5877 | 1 | 0 | 4
38929.5879 | 2 | 0 | 4
38929.5881 | 1 | 0 | 4
38929.5883 | 1 | 0 | 4
38929.5885 | 1 | 0 | 4
38929.5887 | 1 | 0 | 4
38929.5889 | 1 | 0 | 4
38929.5891 | 1 | 0 | 4
38929.5893 | 1 | 0 | 4
38929.5895 | 1 | 0 | 4
38929.5897 | 1 | 0 | 4
38929.5898 | 1 | 0 | 4
38929.59 | 1 | 0 | 4
38929.5902 | 1 | 0 | 4
38929.5904 | 1 | 0 | 4
38929.5906 | 1 | 0 | 4
38929.5908 | 1 | 0 | 4
38929.591 | 1 | 0 | 4
38929.5912 | 1 | 0 | 4
38929.5914 | 1 | 0 | 4
38929.5916 | 1 | 0 | 4
38929.5918 | 1 | 0 | 4
38929.592 | 1 | 0 | 4
38929.5922 | 1 | 0 | 4
38929.5924 | 1 | 0 | 4
38929.5926 | 1 | 0 | 4
38929.5928 | 1 | 0 | 4
38929.593 | 1 | 0 | 4
38929.5932 | 1 | 0 | 4
38929.5934 | 1 | 0 | 4
38929.5936 | 1 | 0 | 4
38929.5937 | 1 | 0 | 4
38929.5939 | 1 | 0 | 4
38929.5941 | 1 | 0 | 4
38929.5943 | 1 | 0 | 4
38929.5945 | 1 | 0 | 4
38929.5947 | 1 | 0 | 4
38929.5949 | 1 | 0 | 4
38929.5951 | 1 | 0 | 4
38929.5953 | 1 | 0 | 4
38929.5955 | 1 | 0 | 4
38929.5957 | 1 | 0 | 4
38929.5959 | 1 | 0 | 4
38929.5961 | 1 | 0 | 4
38929.5963 | 1 | 0 | 4
38929.5965 | 1 | 0 | 4
38929.5967 | 1 | 0 | 4
38929.5969 | 1 | 0 | 4
38929.597 | 1 | 0 | 4
38929.5972 | 1 | 0 | 4
38929.5974 | 1 | 0 | 4
38929.5976 | 1 | 0 | 4
38929.5978 | 1 | 0 | 4
38929.598 | 1 | 0 | 4
38929.5982 | 1 | 0 | 4
38929.5984 | 1 | 0 | 4
38929.5986 | 1 | 0 | 4
38929.5988 | 1 | 0 | 4
38929.599 | 1 | 0 | 4
38929.5992 | 1 | 0 | 4
38929.5994 | 1 | 0 | 4
38929.5996 | 1 | 0 | 4
38929.5998 | 1 | 0 | 4
38929.6 | 1 | 0 | 4
38929.6002 | 1 | 0 | 4
38929.6003 | 1 | 0 | 4
38929.6005 | 1 | 0 | 4
38929.6007 | 1 | 1 | 4
38929.6009 | 1 | 1 | 4
38929.6011 | 2 | 1 | 4
38929.6013 | 2 | 2 | 4
38929.6015 | 1083 | 1054 | 4
38929.6017 | 1081 | 1135 | 4
38929.6019 | 1136 | 1183 | 4
38929.6021 | 924 | 952 | 4
38929.6023 | 1171 | 1153 | 4
38929.6025 | 1183 | 1186 | 4
38929.6027 | 1073 | 1128 | 4
38929.6029 | 1060 | 1032 | 4
38929.6031 | 1145 | 1122 | 4
38929.6033 | 933 | 904 | 4
38929.6035 | 1053 | 1026 | 4
38929.6037 | 1163 | 1172 | 4
38929.6039 | 1102 | 1037 | 4
38929.6041 | 960 | 857 | 4
38929.6042 | 945 | 834 | 4
38929.6044 | 1014 | 917 | 4
38929.6046 | 1141 | 1084 | 4
38929.6048 | 1048 | 1055 | 4
38929.605 | 938 | 822 | 4
38929.6052 | 928 | 871 | 4
38929.6054 | 961 | 924 | 4
38929.6056 | 1008 | 996 | 4
38929.6058 | 1195 | 1187 | 4
38929.606 | 1117 | 1049 | 4
38929.6062 | 1144 | 1096 | 4
38929.6064 | 1089 | 1024 | 4
38929.6066 | 1191 | 1057 | 4
38929.6068 | 1029 | 949 | 4
38929.607 | 985 | 979 | 4
38929.6072 | 1026 | 943 | 4
38929.6073 | 1135 | 1180 | 4
38929.6075 | 999 | 915 | 4
38929.6077 | 1118 | 1162 | 4
38929.6079 | 1194 | 1043 | 4
38929.6081 | 1036 | 969 | 4
38929.6083 | 927 | 917 | 4
38929.5858 | 1 | 0 | 5
38929.586 | 1 | 0 | 5
38929.5862 | 1 | 0 | 5
38929.5864 | 1 | 0 | 5
38929.5866 | 1 | 0 | 5
38929.5868 | 1 | 0 | 5
38929.587 | 1 | 0 | 5
38929.5872 | 1 | 0 | 5
38929.5873 | 1 | 0 | 5
38929.5875 | 1 | 0 | 5
38929.5877 | 1 | 0 | 5
38929.5879 | 1 | 0 | 5
38929.5881 | 1 | 0 | 5
38929.5883 | 1 | 0 | 5
38929.5885 | 1 | 0 | 5
38929.5887 | 1 | 0 | 5
38929.5889 | 1 | 0 | 5
38929.5891 | 1 | 0 | 5
38929.5893 | 1 | 0 | 5
38929.5895 | 1 | 0 | 5
38929.5897 | 1 | 0 | 5
38929.5899 | 1 | 0 | 5
38929.5901 | 1 | 0 | 5
38929.5903 | 1 | 0 | 5
38929.5905 | 1 | 0 | 5
38929.5906 | 1 | 0 | 5
38929.5908 | 1 | 0 | 5
38929.591 | 1 | 0 | 5
38929.5912 | 1 | 0 | 5
38929.5914 | 1 | 0 | 5
38929.5916 | 1 | 0 | 5
38929.5918 | 1 | 0 | 5
38929.592 | 1 | 0 | 5
38929.5922 | 1 | 0 | 5
38929.5924 | 1 | 0 | 5
38929.5926 | 1 | 0 | 5
38929.5928 | 1 | 0 | 5
38929.593 | 1 | 0 | 5
38929.5932 | 1 | 0 | 5
38929.5934 | 1 | 0 | 5
38929.5936 | 1 | 0 | 5
38929.5938 | 1 | 0 | 5
38929.594 | 1 | 0 | 5
38929.5941 | 1 | 0 | 5
38929.5943 | 1 | 0 | 5
38929.5945 | 1 | 0 | 5
38929.5947 | 1 | 0 | 5
38929.5949 | 1 | 0 | 5
38929.5951 | 1 | 0 | 5
38929.5953 | 1 | 0 | 5
38929.5955 | 1 | 0 | 5
38929.5957 | 1 | 0 | 5
38929.5959 | 1 | 0 | 5
38929.5961 | 1 | 0 | 5
38929.5963 | 1 | 0 | 5
38929.5965 | 1 | 0 | 5
38929.5967 | 1 | 0 | 5
38929.5969 | 1 | 0 | 5
38929.5971 | 1 | 0 | 5
38929.5973 | 1 | 0 | 5
38929.5975 | 1 | 0 | 5
38929.5977 | 1 | 0 | 5
38929.5978 | 1 | 0 | 5
38929.598 | 1 | 0 | 5
38929.5982 | 1 | 0 | 5
38929.5984 | 1 | 0 | 5
38929.5986 | 1 | 0 | 5
38929.5988 | 1 | 0 | 5
38929.599 | 1 | 0 | 5
38929.5992 | 1 | 0 | 5
38929.5994 | 1 | 0 | 5
38929.5996 | 1 | 0 | 5
38929.5998 | 1 | 0 | 5
38929.6 | 1 | 0 | 5
38929.6002 | 1 | 0 | 5
38929.6004 | 1 | 0 | 5
38929.6006 | 35 | 38 | 5
38929.6008 | 1038 | 1003 | 5
38929.6009 | 918 | 937 | 5
38929.6011 | 1046 | 1014 | 5
38929.6013 | 1115 | 1087 | 5
38929.6015 | 963 | 927 | 5
38929.6017 | 1180 | 1116 | 5
38929.6019 | 1054 | 1027 | 5
38929.6021 | 1127 | 1178 | 5
38929.6023 | 934 | 902 | 5
38929.6025 | 927 | 905 | 5
38929.6027 | 1146 | 1124 | 5
38929.6029 | 987 | 958 | 5
38929.6031 | 946 | 979 | 5
38929.6033 | 1019 | 927 | 5
38929.6035 | 977 | 948 | 5
38929.6037 | 918 | 945 | 5
38929.6039 | 1028 | 942 | 5
38929.6041 | 1185 | 1179 | 5
38929.6043 | 932 | 853 | 5
38929.6045 | 1001 | 901 | 5
38929.6046 | 1190 | 1183 | 5
38929.6048 | 1039 | 947 | 5
38929.605 | 966 | 849 | 5
38929.6052 | 1005 | 891 | 5
38929.6054 | 1040 | 943 | 5
38929.6056 | 1167 | 1120 | 5
38929.6058 | 1066 | 981 | 5
38929.606 | 969 | 856 | 5
38929.6062 | 1044 | 1060 | 5
38929.6064 | 1000 | 997 | 5
38929.6066 | 1137 | 1182 | 5
38929.6068 | 1170 | 1129 | 5
38929.607 | 948 | 847 | 5
38929.6072 | 930 | 860 | 5
38929.6074 | 930 | 876 | 5
38929.6076 | 962 | 1070 | 5
38929.6078 | 1184 | 1153 | 5
38929.608 | 1195 | 1170 | 5
38929.6081 | 1063 | 998 | 5
38929.6083 | 962 | 875 | 5
38929.5858 | 1 | 0 | 6
38929.586 | 1 | 0 | 6
38929.5862 | 1 | 0 | 6
38929.5864 | 1 | 0 | 6
38929.5866 | 1 | 0 | 6
38929.5868 | 2 | 0 | 6
38929.587 | 1 | 0 | 6
38929.5872 | 1 | 0 | 6
38929.5874 | 1 | 0 | 6
38929.5876 | 1 | 0 | 6
38929.5877 | 1 | 0 | 6
38929.5879 | 1 | 0 | 6
38929.5881 | 1 | 0 | 6
38929.5883 | 1 | 0 | 6
38929.5885 | 1 | 0 | 6
38929.5887 | 1 | 0 | 6
38929.5889 | 1 | 0 | 6
38929.5891 | 1 | 0 | 6
38929.5893 | 1 | 0 | 6
38929.5895 | 1 | 0 | 6
38929.5897 | 1 | 0 | 6
38929.5899 | 1 | 0 | 6
38929.5901 | 1 | 0 | 6
38929.5903 | 1 | 0 | 6
38929.5905 | 1 | 0 | 6
38929.5907 | 1 | 0 | 6
38929.5909 | 1 | 0 | 6
38929.5911 | 1 | 0 | 6
38929.5912 | 1 | 0 | 6
38929.5914 | 1 | 0 | 6
38929.5916 | 1 | 0 | 6
38929.5918 | 1 | 0 | 6
38929.592 | 1 | 0 | 6
38929.5922 | 1 | 0 | 6
38929.5924 | 1 | 0 | 6
38929.5926 | 1 | 0 | 6
38929.5928 | 1 | 0 | 6
38929.593 | 1 | 0 | 6
38929.5932 | 1 | 0 | 6
38929.5934 | 1 | 0 | 6
38929.5936 | 1 | 0 | 6
38929.5938 | 1 | 0 | 6
38929.594 | 1 | 0 | 6
38929.5942 | 1 | 0 | 6
38929.5944 | 1 | 0 | 6
38929.5945 | 1 | 0 | 6
38929.5947 | 1 | 0 | 6
38929.5949 | 1 | 0 | 6
38929.5951 | 1 | 0 | 6
38929.5953 | 1 | 0 | 6
38929.5955 | 1 | 0 | 6
38929.5957 | 1 | 0 | 6
38929.5959 | 1 | 0 | 6
38929.5961 | 1 | 0 | 6
38929.5963 | 1 | 0 | 6
38929.5965 | 1 | 0 | 6
38929.5967 | 1 | 0 | 6
38929.5969 | 1 | 0 | 6
38929.5971 | 1 | 0 | 6
38929.5973 | 1 | 0 | 6
38929.5975 | 1 | 0 | 6
38929.5977 | 1 | 0 | 6
38929.5979 | 1 | 0 | 6
38929.5981 | 1 | 0 | 6
38929.5983 | 1 | 0 | 6
38929.5984 | 1 | 0 | 6
38929.5986 | 1 | 0 | 6
38929.5988 | 1 | 0 | 6
38929.599 | 1 | 0 | 6
38929.5992 | 1 | 0 | 6
38929.5994 | 1 | 0 | 6
38929.5996 | 1 | 0 | 6
38929.5998 | 1 | 0 | 6
38929.6 | 1 | 1 | 6
38929.6002 | 1 | 0 | 6
38929.6004 | 1 | 0 | 6
38929.6006 | 86 | 81 | 6
38929.6008 | 1132 | 1107 | 6
38929.601 | 1070 | 1038 | 6
38929.6012 | 1178 | 1161 | 6
38929.6014 | 1157 | 1135 | 6
38929.6016 | 966 | 932 | 6
38929.6017 | 1081 | 1139 | 6
38929.6019 | 1172 | 1188 | 6
38929.6021 | 1176 | 1187 | 6
38929.6023 | 1106 | 1169 | 6
38929.6025 | 1180 | 910 | 6
38929.6027 | 1054 | 1105 | 6
38929.6029 | 1073 | 1046 | 6
38929.6031 | 994 | 1103 | 6
38929.6033 | 1013 | 984 | 6
38929.6035 | 926 | 904 | 6
38929.6037 | 1016 | 915 | 6
38929.6039 | 1149 | 1103 | 6
38929.6041 | 1082 | 1114 | 6
38929.6043 | 935 | 898 | 6
38929.6045 | 1117 | 1054 | 6
38929.6047 | 1180 | 1139 | 6
38929.6049 | 1116 | 1176 | 6
38929.605 | 945 | 819 | 6
38929.6052 | 941 | 1031 | 6
38929.6054 | 932 | 870 | 6
38929.6056 | 1180 | 1190 | 6
38929.606 | 1083 | 1004 | 6
38929.6062 | 962 | 862 | 6
38929.6064 | 1147 | 1098 | 6
38929.6066 | 1007 | 925 | 6
38929.6068 | 1194 | 933 | 6
38929.607 | 940 | 839 | 6
38929.6072 | 1170 | 1178 | 6
38929.6074 | 1193 | 1183 | 6
38929.6076 | 1069 | 1153 | 6
38929.6078 | 925 | 893 | 6
38929.608 | 1043 | 972 | 6
38929.6082 | 1013 | 935 | 6
38929.6084 | 925 | 899 | 6
38929.5858 | 1 | 0 | 7
38929.586 | 1 | 0 | 7
38929.5862 | 1 | 0 | 7
38929.5864 | 1 | 0 | 7
38929.5866 | 1 | 0 | 7
38929.5868 | 1 | 0 | 7
38929.587 | 1 | 0 | 7
38929.5872 | 1 | 0 | 7
38929.5874 | 1 | 0 | 7
38929.5876 | 1 | 0 | 7
38929.5878 | 1 | 0 | 7
38929.588 | 1 | 0 | 7
38929.5881 | 1 | 0 | 7
38929.5883 | 1 | 0 | 7
38929.5885 | 1 | 0 | 7
38929.5887 | 1 | 1 | 7
38929.5889 | 1 | 0 | 7
38929.5891 | 1 | 0 | 7
38929.5895 | 1 | 0 | 7
38929.5897 | 1 | 0 | 7
38929.5899 | 1 | 0 | 7
38929.5901 | 1 | 0 | 7
38929.5903 | 1 | 0 | 7
38929.5905 | 1 | 0 | 7
38929.5907 | 1 | 0 | 7
38929.5909 | 1 | 0 | 7
38929.5911 | 1 | 0 | 7
38929.5913 | 1 | 0 | 7
38929.5915 | 1 | 0 | 7
38929.5917 | 1 | 0 | 7
38929.5919 | 1 | 0 | 7
38929.592 | 1 | 0 | 7
38929.5922 | 1 | 0 | 7
38929.5924 | 1 | 0 | 7
38929.5926 | 1 | 0 | 7
38929.5928 | 1 | 0 | 7
38929.593 | 1 | 0 | 7
38929.5932 | 1 | 0 | 7
38929.5934 | 1 | 0 | 7
38929.5936 | 1 | 0 | 7
38929.5938 | 1 | 0 | 7
38929.594 | 1 | 0 | 7
38929.5942 | 1 | 0 | 7
38929.5944 | 1 | 0 | 7
38929.5946 | 1 | 0 | 7
38929.5948 | 1 | 0 | 7
38929.595 | 1 | 0 | 7
38929.5952 | 1 | 0 | 7
38929.5953 | 1 | 0 | 7
38929.5955 | 1 | 0 | 7
38929.5957 | 1 | 0 | 7
38929.5959 | 1 | 0 | 7
38929.5961 | 1 | 0 | 7
38929.5963 | 1 | 0 | 7
38929.5965 | 1 | 0 | 7
38929.5967 | 1 | 0 | 7
38929.5969 | 1 | 0 | 7
38929.5971 | 1 | 0 | 7
38929.5973 | 2 | 1 | 7
38929.5975 | 1 | 0 | 7
38929.5977 | 1 | 0 | 7
38929.5979 | 1 | 0 | 7
38929.5981 | 1 | 0 | 7
38929.5983 | 1 | 0 | 7
38929.5985 | 1 | 0 | 7
38929.5987 | 1 | 0 | 7
38929.5988 | 1 | 0 | 7
38929.599 | 1 | 0 | 7
38929.5992 | 1 | 0 | 7
38929.5994 | 1 | 0 | 7
38929.5996 | 1 | 0 | 7
38929.5998 | 1 | 0 | 7
38929.6 | 1 | 0 | 7
38929.6002 | 1 | 0 | 7
38929.6004 | 1 | 0 | 7
38929.6006 | 1 | 0 | 7
38929.6008 | 4 | 13 | 7
38929.601 | 3 | 14 | 7
38929.6012 | 4 | 15 | 7
38929.6014 | 4 | 17 | 7
38929.6016 | 1185 | 1167 | 7
38929.6018 | 1100 | 1157 | 7
38929.602 | 957 | 925 | 7
38929.6022 | 1018 | 987 | 7
38929.6023 | 1106 | 1078 | 7
38929.6025 | 928 | 957 | 7
38929.6027 | 1167 | 902 | 7
38929.6029 | 1089 | 1144 | 7
38929.6031 | 961 | 1079 | 7
38929.6033 | 950 | 919 | 7
38929.6035 | 1184 | 1082 | 7
38929.6037 | 1035 | 940 | 7
38929.6039 | 1146 | 1099 | 7
38929.6041 | 1183 | 859 | 7
38929.6043 | 1044 | 959 | 7
38929.6045 | 1178 | 1149 | 7
38929.6047 | 1014 | 915 | 7
38929.6049 | 1191 | 1154 | 7
38929.6051 | 951 | 826 | 7
38929.6053 | 1194 | 876 | 7
38929.6055 | 1182 | 1190 | 7
38929.6056 | 1026 | 925 | 7
38929.6058 | 1170 | 1123 | 7
38929.606 | 1188 | 1152 | 7
38929.6062 | 1065 | 993 | 7
38929.6064 | 952 | 856 | 7
38929.6066 | 1058 | 987 | 7
38929.6068 | 938 | 845 | 7
38929.607 | 947 | 1047 | 7
38929.6072 | 1181 | 1148 | 7
38929.6074 | 1056 | 985 | 7
38929.6076 | 981 | 895 | 7
38929.6078 | 1025 | 948 | 7
38929.608 | 1001 | 1004 | 7
38929.6082 | 1071 | 1153 | 7
38929.6084 | 979 | 900 | 7
38929.5858 | 1 | 0 | 8
38929.586 | 1 | 0 | 8
38929.5862 | 1 | 0 | 8
38929.5864 | 1 | 0 | 8
38929.5866 | 1 | 0 | 8
38929.5868 | 1 | 0 | 8
38929.587 | 1 | 0 | 8
38929.5872 | 1 | 0 | 8
38929.5874 | 1 | 0 | 8
38929.5876 | 1 | 0 | 8
38929.5878 | 1 | 0 | 8
38929.588 | 1 | 0 | 8
38929.5882 | 1 | 0 | 8
38929.5884 | 1 | 0 | 8
38929.5886 | 1 | 0 | 8
38929.5888 | 1 | 0 | 8
38929.5889 | 1 | 0 | 8
38929.5891 | 1 | 0 | 8
38929.5893 | 1 | 0 | 8
38929.5895 | 1 | 0 | 8
38929.5897 | 1 | 0 | 8
38929.5899 | 1 | 0 | 8
38929.5901 | 1 | 0 | 8
38929.5903 | 1 | 0 | 8
38929.5905 | 1 | 0 | 8
38929.5907 | 1 | 0 | 8
38929.5909 | 1 | 0 | 8
38929.5911 | 1 | 0 | 8
38929.5913 | 1 | 0 | 8
38929.5915 | 1 | 0 | 8
38929.5917 | 1 | 1 | 8
38929.5919 | 1 | 0 | 8
38929.5921 | 1 | 0 | 8
38929.5923 | 1 | 0 | 8
38929.5924 | 1 | 0 | 8
38929.5926 | 1 | 0 | 8
38929.5928 | 1 | 0 | 8
38929.593 | 1 | 0 | 8
38929.5932 | 1 | 0 | 8
38929.5934 | 1 | 0 | 8
38929.5936 | 1 | 0 | 8
38929.5938 | 1 | 0 | 8
38929.594 | 1 | 0 | 8
38929.5942 | 1 | 0 | 8
38929.5944 | 1 | 0 | 8
38929.5946 | 1 | 0 | 8
38929.5948 | 1 | 0 | 8
38929.595 | 1 | 0 | 8
38929.5952 | 1 | 0 | 8
38929.5954 | 1 | 0 | 8
38929.5956 | 1 | 0 | 8
38929.5958 | 1 | 0 | 8
38929.5959 | 1 | 0 | 8
38929.5961 | 1 | 0 | 8
38929.5963 | 1 | 0 | 8
38929.5965 | 1 | 0 | 8
38929.5967 | 1 | 0 | 8
38929.5969 | 1 | 0 | 8
38929.5971 | 1 | 0 | 8
38929.5973 | 1 | 0 | 8
38929.5975 | 1 | 0 | 8
38929.5977 | 1 | 0 | 8
38929.5979 | 1 | 0 | 8
38929.5981 | 1 | 0 | 8
38929.5983 | 2 | 0 | 8
38929.5985 | 1 | 0 | 8
38929.5987 | 1 | 0 | 8
38929.5989 | 1 | 0 | 8
38929.5991 | 1 | 0 | 8
38929.5992 | 1 | 0 | 8
38929.5994 | 1 | 0 | 8
38929.5996 | 1 | 0 | 8
38929.5998 | 1 | 0 | 8
38929.6 | 1 | 0 | 8
38929.6002 | 1 | 0 | 8
38929.6004 | 1 | 0 | 8
38929.6006 | 1 | 0 | 8
38929.6008 | 3 | 7 | 8
38929.601 | 3 | 8 | 8
38929.6012 | 3 | 7 | 8
38929.6014 | 10 | 14 | 8
38929.6016 | 998 | 963 | 8
38929.6018 | 979 | 1093 | 8
38929.602 | 1178 | 1118 | 8
38929.6022 | 1128 | 1103 | 8
38929.6024 | 1180 | 1162 | 8
38929.6026 | 963 | 1081 | 8
38929.6028 | 1097 | 1072 | 8
38929.6029 | 1041 | 1013 | 8
38929.6031 | 1144 | 1122 | 8
38929.6033 | 989 | 959 | 8
38929.6035 | 928 | 904 | 8
38929.6037 | 947 | 909 | 8
38929.6039 | 1048 | 1067 | 8
38929.6041 | 1172 | 1132 | 8
38929.6043 | 1132 | 1174 | 8
38929.6045 | 1070 | 990 | 8
38929.6047 | 980 | 873 | 8
38929.6049 | 1025 | 1119 | 8
38929.6051 | 1049 | 955 | 8
38929.6053 | 1196 | 1171 | 8
38929.6055 | 1176 | 1190 | 8
38929.6057 | 999 | 981 | 8
38929.6059 | 1067 | 1085 | 8
38929.6061 | 1044 | 1049 | 8
38929.6062 | 1147 | 1099 | 8
38929.6064 | 1071 | 1003 | 8
38929.6066 | 1179 | 1143 | 8
38929.6068 | 1030 | 1041 | 8
38929.607 | 1142 | 1184 | 8
38929.6072 | 970 | 877 | 8
38929.6074 | 1194 | 1185 | 8
38929.6076 | 978 | 893 | 8
38929.6078 | 1000 | 1104 | 8
38929.608 | 1122 | 1168 | 8
38929.6082 | 1187 | 1159 | 8
38929.6084 | 1127 | 1077 | 8
38929.5859 | 1 | 0 | 9
38929.586 | 1 | 0 | 9
38929.5862 | 1 | 0 | 9
38929.5864 | 1 | 0 | 9
38929.5866 | 1 | 0 | 9
38929.5868 | 1 | 0 | 9
38929.587 | 1 | 0 | 9
38929.5872 | 1 | 0 | 9
38929.5874 | 1 | 0 | 9
38929.5876 | 1 | 0 | 9
38929.5878 | 1 | 0 | 9
38929.588 | 1 | 0 | 9
38929.5882 | 1 | 0 | 9
38929.5884 | 1 | 0 | 9
38929.5886 | 1 | 0 | 9
38929.5888 | 1 | 0 | 9
38929.589 | 1 | 0 | 9
38929.5892 | 1 | 0 | 9
38929.5894 | 1 | 0 | 9
38929.5895 | 1 | 0 | 9
38929.5897 | 1 | 0 | 9
38929.5899 | 1 | 0 | 9
38929.5901 | 1 | 0 | 9
38929.5903 | 1 | 0 | 9
38929.5905 | 1 | 0 | 9
38929.5907 | 1 | 0 | 9
38929.5909 | 1 | 0 | 9
38929.5911 | 1 | 0 | 9
38929.5913 | 1 | 0 | 9
38929.5915 | 1 | 0 | 9
38929.5917 | 1 | 0 | 9
38929.5919 | 1 | 0 | 9
38929.5921 | 1 | 0 | 9
38929.5923 | 1 | 0 | 9
38929.5925 | 1 | 0 | 9
38929.5927 | 1 | 0 | 9
38929.5928 | 1 | 0 | 9
38929.593 | 1 | 0 | 9
38929.5932 | 1 | 0 | 9
38929.5934 | 1 | 0 | 9
38929.5936 | 1 | 0 | 9
38929.5938 | 1 | 0 | 9
38929.594 | 1 | 0 | 9
38929.5942 | 1 | 0 | 9
38929.5944 | 1 | 0 | 9
38929.5946 | 1 | 0 | 9
38929.5948 | 1 | 0 | 9
38929.595 | 1 | 0 | 9
38929.5952 | 1 | 0 | 9
38929.5954 | 1 | 0 | 9
38929.5956 | 1 | 0 | 9
38929.5958 | 1 | 0 | 9
38929.596 | 1 | 0 | 9
38929.5962 | 1 | 0 | 9
38929.5964 | 1 | 0 | 9
38929.5965 | 1 | 0 | 9
38929.5967 | 1 | 0 | 9
38929.5969 | 1 | 0 | 9
38929.5971 | 1 | 0 | 9
38929.5973 | 1 | 0 | 9
38929.5975 | 1 | 0 | 9
38929.5977 | 1 | 0 | 9
38929.5979 | 1 | 0 | 9
38929.5981 | 1 | 0 | 9
38929.5983 | 1 | 0 | 9
38929.5985 | 1 | 0 | 9
38929.5987 | 1 | 0 | 9
38929.5989 | 1 | 0 | 9
38929.5991 | 1 | 0 | 9
38929.5993 | 1 | 0 | 9
38929.5995 | 1 | 0 | 9
38929.5997 | 1 | 0 | 9
38929.5998 | 1 | 0 | 9
38929.6 | 1 | 0 | 9
38929.6002 | 1 | 0 | 9
38929.6004 | 1 | 0 | 9
38929.6006 | 1157 | 1187 | 9
38929.6008 | 1156 | 1133 | 9
38929.601 | 1030 | 995 | 9
38929.6012 | 1163 | 1142 | 9
38929.6014 | 1158 | 1188 | 9
38929.6016 | 1042 | 1091 | 9
38929.6018 | 1162 | 1141 | 9
38929.602 | 1085 | 1142 | 9
38929.6022 | 1004 | 973 | 9
38929.6024 | 917 | 966 | 9
38929.6026 | 1046 | 1138 | 9
38929.6028 | 1163 | 1167 | 9
38929.603 | 1188 | 1184 | 9
38929.6032 | 1182 | 1186 | 9
38929.6033 | 928 | 912 | 9
38929.6035 | 1030 | 1077 | 9
38929.6037 | 918 | 871 | 9
38929.6039 | 1021 | 936 | 9
38929.6041 | 1081 | 1009 | 9
38929.6043 | 1023 | 929 | 9
38929.6045 | 1137 | 1080 | 9
38929.6047 | 986 | 879 | 9
38929.6049 | 1136 | 1073 | 9
38929.6051 | 1171 | 1125 | 9
38929.6053 | 1193 | 1156 | 9
38929.6055 | 1173 | 1127 | 9
38929.6057 | 1158 | 1105 | 9
38929.6059 | 1117 | 1154 | 9
38929.6061 | 1190 | 1153 | 9
38929.6063 | 1031 | 952 | 9
38929.6065 | 1171 | 1135 | 9
38929.6067 | 1196 | 1178 | 9
38929.6069 | 992 | 988 | 9
38929.607 | 1013 | 924 | 9
38929.6072 | 1026 | 1038 | 9
38929.6074 | 1031 | 1042 | 9
38929.6076 | 1106 | 1048 | 9
38929.6078 | 1054 | 985 | 9
38929.608 | 1055 | 1141 | 9
38929.6082 | 1179 | 1189 | 9
38929.6084 | 1128 | 1175 | 9
38929.5859 | 1 | 0 | 10
38929.5861 | 1 | 0 | 10
38929.5863 | 1 | 0 | 10
38929.5864 | 1 | 0 | 10
38929.5866 | 1 | 0 | 10
38929.5868 | 1 | 0 | 10
38929.587 | 1 | 0 | 10
38929.5872 | 1 | 0 | 10
38929.5874 | 1 | 0 | 10
38929.5876 | 1 | 0 | 10
38929.5878 | 1 | 0 | 10
38929.588 | 1 | 0 | 10
38929.5882 | 1 | 0 | 10
38929.5884 | 1 | 0 | 10
38929.5886 | 1 | 0 | 10
38929.5888 | 1 | 0 | 10
38929.589 | 1 | 0 | 10
38929.5892 | 1 | 0 | 10
38929.5894 | 1 | 0 | 10
38929.5896 | 1 | 0 | 10
38929.5898 | 1 | 0 | 10
38929.59 | 1 | 0 | 10
38929.5902 | 1 | 0 | 10
38929.5903 | 1 | 0 | 10
38929.5905 | 1 | 0 | 10
38929.5907 | 1 | 0 | 10
38929.5909 | 1 | 0 | 10
38929.5911 | 1 | 0 | 10
38929.5913 | 1 | 0 | 10
38929.5915 | 1 | 0 | 10
38929.5917 | 1 | 0 | 10
38929.5919 | 1 | 0 | 10
38929.5921 | 1 | 0 | 10
38929.5923 | 1 | 0 | 10
38929.5925 | 1 | 0 | 10
38929.5927 | 1 | 0 | 10
38929.5929 | 1 | 0 | 10
38929.5931 | 1 | 0 | 10
38929.5933 | 1 | 0 | 10
38929.5934 | 1 | 0 | 10
38929.5936 | 1 | 0 | 10
38929.5938 | 1 | 0 | 10
38929.594 | 1 | 0 | 10
38929.5942 | 1 | 0 | 10
38929.5944 | 1 | 0 | 10
38929.5946 | 1 | 0 | 10
38929.5948 | 1 | 0 | 10
38929.595 | 1 | 0 | 10
38929.5952 | 1 | 0 | 10
38929.5954 | 1 | 0 | 10
38929.5956 | 1 | 0 | 10
38929.5958 | 1 | 0 | 10
38929.596 | 1 | 0 | 10
38929.5962 | 1 | 0 | 10
38929.5964 | 1 | 0 | 10
38929.5966 | 1 | 0 | 10
38929.5968 | 1 | 0 | 10
38929.597 | 1 | 0 | 10
38929.5971 | 1 | 0 | 10
38929.5973 | 1 | 0 | 10
38929.5975 | 1 | 0 | 10
38929.5977 | 1 | 0 | 10
38929.5979 | 1 | 0 | 10
38929.5981 | 1 | 0 | 10
38929.5983 | 1 | 0 | 10
38929.5985 | 1 | 0 | 10
38929.5987 | 1 | 0 | 10
38929.5989 | 1 | 0 | 10
38929.5991 | 1 | 0 | 10
38929.5993 | 1 | 0 | 10
38929.5995 | 1 | 0 | 10
38929.5997 | 1 | 0 | 10
38929.5999 | 1 | 0 | 10
38929.6001 | 1 | 0 | 10
38929.6003 | 1 | 1 | 10
38929.6005 | 1 | 0 | 10
38929.6006 | 3 | 7 | 10
38929.6008 | 3 | 11 | 10
38929.601 | 3 | 12 | 10
38929.6012 | 3 | 13 | 10
38929.6014 | 208 | 172 | 10
38929.6016 | 970 | 936 | 10
38929.6018 | 1034 | 1079 | 10
38929.602 | 1070 | 1042 | 10
38929.6022 | 1183 | 1090 | 10
38929.6024 | 931 | 901 | 10
38929.6026 | 1187 | 1184 | 10
38929.6028 | 1008 | 979 | 10
38929.603 | 937 | 905 | 10
38929.6032 | 1061 | 1034 | 10
38929.6034 | 977 | 932 | 10
38929.6036 | 1063 | 1037 | 10
38929.6038 | 1187 | 1157 | 10
38929.6039 | 928 | 853 | 10
38929.6041 | 952 | 845 | 10
38929.6043 | 956 | 848 | 10
38929.6045 | 1141 | 1184 | 10
38929.6047 | 1131 | 1067 | 10
38929.6049 | 1062 | 972 | 10
38929.6051 | 1154 | 1188 | 10
38929.6053 | 1155 | 1101 | 10
38929.6055 | 1111 | 1037 | 10
38929.6057 | 1198 | 936 | 10
38929.6059 | 1096 | 1019 | 10
38929.6061 | 933 | 849 | 10
38929.6063 | 1159 | 1115 | 10
38929.6065 | 1124 | 1181 | 10
38929.6067 | 1020 | 938 | 10
38929.6069 | 1030 | 1041 | 10
38929.6071 | 1064 | 1090 | 10
38929.6073 | 1184 | 1150 | 10
38929.6075 | 1019 | 937 | 10
38929.6076 | 1181 | 1152 | 10
38929.6078 | 1168 | 1132 | 10
38929.608 | 950 | 860 | 10
38929.6082 | 954 | 871 | 10
38929.6084 | 986 | 1091 | 10
38929.5859 | 1 | 0 | 11
38929.5861 | 1 | 0 | 11
38929.5863 | 1 | 0 | 11
38929.5865 | 1 | 0 | 11
38929.5867 | 1 | 0 | 11
38929.5869 | 1 | 0 | 11
38929.587 | 1 | 0 | 11
38929.5872 | 1 | 0 | 11
38929.5874 | 1 | 0 | 11
38929.5876 | 1 | 0 | 11
38929.5878 | 1 | 0 | 11
38929.588 | 1 | 0 | 11
38929.5882 | 1 | 0 | 11
38929.5884 | 1 | 0 | 11
38929.5886 | 1 | 0 | 11
38929.5888 | 1 | 0 | 11
38929.589 | 1 | 0 | 11
38929.5892 | 1 | 0 | 11
38929.5894 | 1 | 0 | 11
38929.5896 | 1 | 0 | 11
38929.5898 | 1 | 0 | 11
38929.59 | 1 | 0 | 11
38929.5902 | 1 | 0 | 11
38929.5904 | 1 | 0 | 11
38929.5906 | 1 | 0 | 11
38929.5907 | 1 | 0 | 11
38929.5909 | 2 | 0 | 11
38929.5911 | 1 | 0 | 11
38929.5913 | 1 | 0 | 11
38929.5915 | 1 | 0 | 11
38929.5917 | 1 | 0 | 11
38929.5919 | 1 | 0 | 11
38929.5921 | 1 | 0 | 11
38929.5923 | 1 | 0 | 11
38929.5925 | 1 | 0 | 11
38929.5927 | 1 | 0 | 11
38929.5929 | 1 | 0 | 11
38929.5931 | 1 | 0 | 11
38929.5933 | 1 | 0 | 11
38929.5935 | 1 | 0 | 11
38929.5937 | 1 | 0 | 11
38929.5939 | 1 | 0 | 11
38929.5941 | 1 | 0 | 11
38929.5942 | 1 | 0 | 11
38929.5944 | 1 | 0 | 11
38929.5946 | 1 | 0 | 11
38929.5948 | 1 | 0 | 11
38929.595 | 1 | 0 | 11
38929.5952 | 1 | 0 | 11
38929.5954 | 1 | 0 | 11
38929.5956 | 1 | 0 | 11
38929.5958 | 1 | 0 | 11
38929.596 | 1 | 0 | 11
38929.5962 | 1 | 0 | 11
38929.5964 | 1 | 0 | 11
38929.5966 | 1 | 0 | 11
38929.5968 | 1 | 0 | 11
38929.597 | 1 | 0 | 11
38929.5972 | 1 | 0 | 11
38929.5973 | 1 | 0 | 11
38929.5975 | 1 | 0 | 11
38929.5977 | 1 | 0 | 11
38929.5979 | 1 | 0 | 11
38929.5981 | 1 | 0 | 11
38929.5983 | 1 | 0 | 11
38929.5985 | 1 | 0 | 11
38929.5987 | 1 | 0 | 11
38929.5989 | 1 | 0 | 11
38929.5991 | 1 | 0 | 11
38929.5993 | 1 | 0 | 11
38929.5995 | 1 | 0 | 11
38929.5997 | 1 | 0 | 11
38929.5999 | 1 | 0 | 11
38929.6001 | 1 | 0 | 11
38929.6003 | 1 | 0 | 11
38929.6005 | 1 | 0 | 11
38929.6007 | 2 | 2 | 11
38929.6009 | 2 | 5 | 11
38929.6011 | 3 | 7 | 11
38929.6012 | 3 | 7 | 11
38929.6014 | 351 | 348 | 11
38929.6016 | 1066 | 1036 | 11
38929.6018 | 1041 | 1012 | 11
38929.602 | 1089 | 1063 | 11
38929.6022 | 974 | 944 | 11
38929.6024 | 1102 | 1076 | 11
38929.6026 | 970 | 941 | 11
38929.6028 | 947 | 918 | 11
38929.603 | 999 | 969 | 11
38929.6032 | 1183 | 1165 | 11
38929.6034 | 1033 | 1004 | 11
38929.6036 | 1169 | 1147 | 11
38929.6038 | 1125 | 1173 | 11
38929.604 | 946 | 845 | 11
38929.6042 | 1075 | 1003 | 11
38929.6044 | 1034 | 944 | 11
38929.6045 | 995 | 893 | 11
38929.6047 | 1164 | 1119 | 11
38929.6049 | 1023 | 925 | 11
38929.6051 | 935 | 1023 | 11
38929.6053 | 1068 | 981 | 11
38929.6055 | 1109 | 1039 | 11
38929.6057 | 963 | 841 | 11
38929.6059 | 1198 | 1180 | 11
38929.6061 | 1154 | 1106 | 11
38929.6063 | 1054 | 978 | 11
38929.6065 | 936 | 909 | 11
38929.6067 | 1181 | 1148 | 11
38929.6069 | 1015 | 928 | 11
38929.6071 | 923 | 969 | 11
38929.6073 | 1022 | 938 | 11
38929.6075 | 931 | 868 | 11
38929.6077 | 1177 | 1190 | 11
38929.6079 | 1095 | 1038 | 11
38929.608 | 1061 | 996 | 11
38929.6082 | 1178 | 1152 | 11
38929.6084 | 1149 | 1104 | 11
38929.5859 | 1 | 0 | 12
38929.5861 | 1 | 0 | 12
38929.5863 | 1 | 0 | 12
38929.5865 | 1 | 0 | 12
38929.5867 | 1 | 0 | 12
38929.5869 | 1 | 0 | 12
38929.5871 | 1 | 0 | 12
38929.5873 | 1 | 0 | 12
38929.5875 | 1 | 0 | 12
38929.5877 | 1 | 0 | 12
38929.5878 | 2 | 0 | 12
38929.588 | 1 | 0 | 12
38929.5882 | 1 | 0 | 12
38929.5884 | 1 | 0 | 12
38929.5886 | 1 | 0 | 12
38929.5888 | 1 | 0 | 12
38929.589 | 1 | 0 | 12
38929.5892 | 1 | 0 | 12
38929.5894 | 1 | 0 | 12
38929.5896 | 1 | 0 | 12
38929.5898 | 1 | 0 | 12
38929.59 | 1 | 0 | 12
38929.5902 | 1 | 0 | 12
38929.5904 | 1 | 0 | 12
38929.5906 | 1 | 0 | 12
38929.5908 | 1 | 0 | 12
38929.591 | 1 | 0 | 12
38929.5911 | 1 | 0 | 12
38929.5913 | 1 | 0 | 12
38929.5915 | 1 | 0 | 12
38929.5917 | 1 | 0 | 12
38929.5919 | 1 | 0 | 12
38929.5921 | 1 | 0 | 12
38929.5923 | 1 | 0 | 12
38929.5925 | 1 | 0 | 12
38929.5927 | 1 | 0 | 12
38929.5929 | 1 | 0 | 12
38929.5931 | 1 | 0 | 12
38929.5933 | 1 | 0 | 12
38929.5935 | 1 | 0 | 12
38929.5937 | 1 | 0 | 12
38929.5939 | 1 | 0 | 12
38929.5941 | 1 | 0 | 12
38929.5943 | 1 | 0 | 12
38929.5945 | 1 | 0 | 12
38929.5947 | 1 | 0 | 12
38929.5948 | 1 | 0 | 12
38929.595 | 1 | 0 | 12
38929.5952 | 1 | 0 | 12
38929.5954 | 1 | 0 | 12
38929.5956 | 1 | 0 | 12
38929.5958 | 1 | 0 | 12
38929.596 | 1 | 0 | 12
38929.5962 | 1 | 0 | 12
38929.5964 | 1 | 0 | 12
38929.5966 | 1 | 0 | 12
38929.5968 | 1 | 0 | 12
38929.597 | 1 | 0 | 12
38929.5972 | 1 | 0 | 12
38929.5974 | 1 | 0 | 12
38929.5976 | 1 | 0 | 12
38929.5978 | 1 | 0 | 12
38929.598 | 1 | 0 | 12
38929.5981 | 1 | 0 | 12
38929.5983 | 1 | 0 | 12
38929.5985 | 1 | 0 | 12
38929.5987 | 1 | 0 | 12
38929.5989 | 1 | 0 | 12
38929.5991 | 1 | 0 | 12
38929.5993 | 1 | 0 | 12
38929.5995 | 1 | 0 | 12
38929.5997 | 1 | 0 | 12
38929.5999 | 1 | 0 | 12
38929.6001 | 1 | 0 | 12
38929.6003 | 1 | 0 | 12
38929.6005 | 1 | 0 | 12
38929.6007 | 2 | 2 | 12
38929.6009 | 2 | 3 | 12
38929.6011 | 2 | 4 | 12
38929.6013 | 2 | 5 | 12
38929.6015 | 533 | 556 | 12
38929.6016 | 1189 | 1182 | 12
38929.6018 | 1010 | 1052 | 12
38929.602 | 923 | 920 | 12
38929.6022 | 1030 | 1002 | 12
38929.6024 | 1186 | 1169 | 12
38929.6026 | 951 | 918 | 12
38929.6028 | 991 | 1101 | 12
38929.603 | 1123 | 1099 | 12
38929.6032 | 989 | 1100 | 12
38929.6034 | 1185 | 1171 | 12
38929.6036 | 937 | 818 | 12
38929.6038 | 977 | 876 | 12
38929.604 | 1110 | 1168 | 12
38929.6042 | 960 | 855 | 12
38929.6044 | 1070 | 1091 | 12
38929.6046 | 1073 | 1152 | 12
38929.6048 | 937 | 896 | 12
38929.605 | 1036 | 1129 | 12
38929.6052 | 999 | 978 | 12
38929.6053 | 991 | 1092 | 12
38929.6055 | 1063 | 973 | 12
38929.6057 | 1189 | 1154 | 12
38929.6059 | 1058 | 968 | 12
38929.6061 | 1095 | 1168 | 12
38929.6063 | 1135 | 1084 | 12
38929.6065 | 967 | 870 | 12
38929.6067 | 1101 | 1144 | 12
38929.6069 | 979 | 968 | 12
38929.6071 | 1006 | 1108 | 12
38929.6073 | 1054 | 1075 | 12
38929.6075 | 947 | 852 | 12
38929.6077 | 936 | 855 | 12
38929.6079 | 1154 | 1192 | 12
38929.6081 | 1143 | 1096 | 12
38929.6083 | 1183 | 1139 | 12
38929.6084 | 938 | 860 | 12