## Test Facts
Last row in IRMS data sheets: | 40
Time when Penlight power was initiated: | 97
NOTE: The thermocouple labeled Cable 5 may have separated from the cable surface during a portion of the test (beginning around 400s (Penlight time)). This thermocouple shows an unexpected and atypical deviation from the general behavior observed for other surface thermocouples. The data for this thermocouple may be suspect.

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 11
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III control cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 97 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
97 | 0 | Initated Penlight Heating
1322-1351 | 1225-1254 | Conductor 7 shorts to conductors 2, 5 & 6 (276, 89 & 24 ohms) | Initial failure is by shorting between conductors
1372-1404 | 1275-1407 | Conductor 2 shorts to ground (851), and to conductors 5, 6 & 7 (108, 72 & 56). Conductor 7 shorts to ground (952), and to conductors 3 & 4 (65 & 52), while the short between 7 and 2 degrades to 56 ohms. Conductor 6 shorts to 3, 4 & 5 (367, 99 & 650). | Failures progress to additional conductor-to-conductor shorts and shorts to ground
1412-1429 | 1315-1332 | Conductor 1 shorts to conductors 2, 3, 4, 6 & 7 (at 36, 91, 160, 36 & 29 ohms, respectively)
1438 | 1341 | Conductor 3 shorts to ground at less than 1000 ohms (746)
1443-1451 | 1346-1354 | Conductor 3 shorts to conductors 4 & 5 (342 & 88), while the short between conductors 3 and 6 degrades to 19 ohms
1477-1513 | 1380-1416 | Conductor 4 shorts to conductors 1, 2, 3 & 5 (7, 65, 75 & 43), while conductor 6 shorts to ground (668)
1536-1569 | 1439-1472 | Conductor 1 shorts to conductor 5 (47) and conductors 1, 4 & 5 all short to ground (449, 12, 15). The ground shorts for conductors 6 & 7 degrade to 5 & 18 ohms, respectively.
1596-1615 | 1499-1518 | The ground shorts for conductors 1, 2 & 3 all degrade to less than 100 ohms (8, 7 & 34) | All conductors have shorted to external ground.
Additional Observations
Observation 1 | The progression of failure modes for this cable followed that expected for a typical thermoset-insulated cable: conductor-to-conductor shorting followed by shorts to ground.
Observation 2 | It took 1225 s (20.4 min.) from the start of Penlight heating for the first conductor-to-conductor short to occur, and it took 1275 s (21.25 min.) for the first short to ground.
Observation 3 | NOTE: The thermocouple labeled Cable 5 may have separated from the cable surface during a portion of the test (beginning around 400s (Penlight time)). This thermocouple shows an unexpected and atypical deviation from the general behavior observed for other surface thermocouples. The data for this thermocouple may be suspect.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center
NOTE: The thermocouple labeled Cable 5 may have separated from the cable surface during a portion of the test (beginning around 400s (Penlight time)). This thermocouple shows an unexpected and atypical deviation from the general behavior observed for other surface thermocouples. The data for this thermocouple may be suspect.

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 11 |  |  | 2006-07-10 | 10:57
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-88.9167 | 232738 |  | -77.25 | 228238 | -69.25 | 221038 | -64.25 | 228138 | -60.9167 | 229638 | -58.5 | 221038 | -56.25 | 228138 | -88.9167 | 221038
-30.0833 | 232738 |  | -18.4167 | 228238 | -10.5833 | 221038 | -5.4167 | 228138 | -2 | 229638 | 0.25 | 221038 | 2.5833 | 228138 | -30.0833 | 221038
28.6667 | 232738 |  | 40.3333 | 228238 | 48.3333 | 221038 | 53.5 | 228138 | 56.6667 | 229638 | 59 | 221038 | 61.3333 | 228138 | 28.6667 | 221038
87.5 | 232738 |  | 99.1667 | 228238 | 107.1667 | 221038 | 112.25 | 228138 | 115.5 | 229638 | 117.8333 | 221038 | 120.0833 | 118519 | 87.5 | 118519
146.3333 | 232738 |  | 158 | 228238 | 165.9167 | 221038 | 171.1667 | 228138 | 174.25 | 229638 | 176.5833 | 221038 | 179.0833 | 228138 | 146.3333 | 221038
205.0833 | 232738 |  | 216.75 | 228238 | 224.75 | 221038 | 229.75 | 228138 | 233.0833 | 229638 | 235.5 | 221038 | 237.75 | 228138 | 205.0833 | 221038
263.9167 | 232738 |  | 275.5833 | 228238 | 283.4167 | 221038 | 288.5833 | 114069 | 292 | 229638 | 294.25 | 221038 | 296.5833 | 228138 | 263.9167 | 114069
322.6667 | 232738 |  | 334.1667 | 228238 | 342.3333 | 221038 | 347.4167 | 228138 | 350.6667 | 229638 | 352.9167 | 221038 | 355.3333 | 228138 | 322.6667 | 221038
381.5 | 232738 |  | 393.0833 | 228238 | 401.0833 | 221038 | 406.1667 | 228138 | 409.4167 | 229638 | 411.8333 | 221038 | 414.0833 | 228138 | 381.5 | 221038
440.1667 | 232738 |  | 451.9167 | 228238 | 459.75 | 221038 | 464.8333 | 228138 | 468.1667 | 229638 | 470.5833 | 221038 | 472.9167 | 228138 | 440.1667 | 221038
499 | 232738 |  | 510.75 | 228238 | 518.6667 | 110469 | 523.6667 | 228138 | 527 | 229638 | 529.4167 | 221038 | 531.6667 | 228138 | 499 | 110469
557.9167 | 232738 |  | 569.5 | 228238 | 577.4167 | 221038 | 582.5833 | 228138 | 586 | 229638 | 588.1667 | 221038 | 590.4167 | 228138 | 557.9167 | 221038
616.6667 | 232738 |  | 628.25 | 228238 | 636.25 | 221038 | 641.3333 | 228138 | 644.5833 | 229638 | 647 | 221038 | 649.25 | 228138 | 616.6667 | 221038
675.4167 | 232738 |  | 687.0833 | 228238 | 695.0833 | 221038 | 700.0833 | 228138 | 703.3333 | 229638 | 705.75 | 221038 | 708.0833 | 228138 | 675.4167 | 221038
734.25 | 232738 |  | 745.8333 | 228238 | 753.75 | 221038 | 758.8333 | 228138 | 762.0833 | 229638 | 764.5 | 221038 | 766.9167 | 228138 | 734.25 | 221038
793 | 232738 |  | 804.6667 | 228238 | 812.5 | 221038 | 817.6667 | 228138 | 821.0833 | 229638 | 823.4167 | 221038 | 825.6667 | 228138 | 793 | 221038
851.75 | 232738 |  | 863.4167 | 228238 | 871.3333 | 221038 | 876.5833 | 228138 | 879.75 | 229638 | 882.0833 | 221038 | 884.5833 | 228138 | 851.75 | 221038
910.5833 | 232738 |  | 922.25 | 228238 | 930.1667 | 221038 | 935.4167 | 228138 | 938.5 | 229638 | 940.8333 | 221038 | 943.0833 | 228138 | 910.5833 | 221038
969.4167 | 232738 |  | 981 | 228238 | 988.8333 | 221038 | 994.0833 | 228138 | 997.3333 | 229638 | 999.5833 | 221038 | 1002.0833 | 228138 | 969.4167 | 221038
1028.1667 | 232738 |  | 1039.8333 | 228238 | 1047.75 | 119519 | 1052.75 | 228138 | 1056.0833 | 229638 | 1058.5 | 221038 | 1060.75 | 228138 | 1028.1667 | 119519
1086.9167 | 232738 |  | 1098.5833 | 228238 | 1106.4167 | 119219 | 1111.5833 | 228138 | 1115.0833 | 229638 | 1117.3333 | 221038 | 1119.5833 | 228138 | 1086.9167 | 119219
1145.6667 | 232738 |  | 1157.3333 | 228238 | 1165.3333 | 221038 | 1170.5 | 228138 | 1173.6667 | 229638 | 1176 | 221038 | 1178.3333 | 95734.028 | 1145.6667 | 95734.028
1204.5 | 60546.8838 |  | 1216.1667 | 1038.8526 | 1224.1667 | 47763.4441 | 1229.25 | 79735.2504 | 1232.5 | 18446.0582 | 1234.8333 | 14882.329 | 1237.0833 | 3980.4151 | 1204.5 | 1038.8526
1263.3333 | 26963.1945 |  | 1275 | 850.8921 | 1282.8333 | 3619.6109 | 1288.0833 | 2038.7142 | 1291.25 | 4637.5733 | 1293.5833 | 3823.1486 | 1296.0833 | 952.1793 | 1263.3333 | 850.8921
1322.1667 | 4283.6007 |  | 1333.75 | 1457.5453 | 1341.75 | 745.8977 | 1346.75 | 5605.95 | 1350.1667 | 2634.3356 | 1352.5 | 1722.02 | 1354.75 | 1520.6672 | 1322.1667 | 745.8977
1380.9167 | 2746.3176 |  | 1392.5833 | 1519.3401 | 1400.4167 | 2315.6813 | 1405.5833 | 2474.6643 | 1409 | 3531.7218 | 1411.25 | 668.2864 | 1413.5833 | 2466.3648 | 1380.9167 | 668.2864
1439.6667 | 449.3902 |  | 1451.3333 | 759.038 | 1459.3333 | 230.3956 | 1464.5 | 11.8222 | 1467.6667 | 15.2622 | 1470 | 5.0277 | 1472.3333 | 17.9991 | 1439.6667 | 5.0277
1498.5 | 8.0251 |  | 1510.1667 | 6.7587 | 1518.1667 | 33.8708 | 1523.25 | 10.2639 | 1526.5 | 24.2587 | 1528.8333 | 19.9308 | 1531.0833 | 17.3872 | 1498.5 | 6.7587
1557.3333 | 1.826 |  | 1569 | 16.2976 | 1576.8333 | 4.2915 | 1582.0833 | 2.2867 | 1585.25 | 2.6816 | 1587.5833 | 8.0085 | 1590.0833 | 13.1237 | 1557.3333 | 1.826
1616.0833 | 2.2526 |  | 1627.75 | 2.1697 | 1635.75 | 5.019 | 1640.6667 | 4.6426 | 1644.0833 | 0.70779 | 1646.4167 | 0.97389 | 1648.75 | 1.6418 | 1616.0833 | 0.70779
1674.9167 | 2.3654 |  | 1686.5 | 0.89229 | 1694.4167 | 1.4124 | 1699.5833 | 1.3986 | 1702.9167 | 3.0292 | 1705.25 | 5.9162 | 1707.5833 | 0.69204 | 1674.9167 | 0.69204
1733.6667 | 0.68429 |  | 1745.25 | 0.68054 | 1753.3333 | 0.56798 | 1758.4167 | 0.69694 | 1761.5833 | 3.5193 | 1764 | 0.68599 | 1766.25 | 0.88348 | 1733.6667 | 0.56798
1792.5 | 0.68718 |  | 1804.0833 | 0.66397 | 1812.0833 | 1.1177 | 1817.25 | 1.1596 | 1820.4167 | 3.9395 | 1822.75 | 1.4653 | 1825.0833 | 1.883 | 1792.5 | 0.66397
1851.1667 | 1.1377 |  | 1862.8333 | 0.50332 | 1870.8333 | 0.10226 | 1875.9167 | 13.8756 | 1879.1667 | 0.54294 | 1881.5833 | 1.0781 | 1884 | 6.7578 | 1851.1667 | 0.10226
1910.0833 | 127.7596 |  | 1921.6667 | 306.1502 | 1929.6667 | 177.9846 | 1934.6667 | 390.3408 | 1938.0833 | 218.9934 | 1940.3333 | 230.1659 | 1942.6667 | 688.3577 | 1910.0833 | 127.7596

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 11 |  |  | 2006-07-10 | 10:57
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-96 | 242137.9994 | -93 | 242637.9994 | -90.5 | 234537.9994 | -87.5 | 232737.9994 | -84.5 | 234737.9994 | -82 | 237137.9994 | -79 | 231837.9994 | -76.5 | 228237.9994 | -73.5 | 243937.9994 | -70.5 | 242137.9994 | -68 | 240237.9994 | -65 | 238537.9994 | -62.5 | 237837.9994 | -59.5 | 221037.9994 | -56.5 | 239137.9994 | -54 | 229637.9994 | -51 | 237337.9994 | -48.5 | 228137.9994 | -45.5 | 232237.9994 | -42.5 | 240337.9994 | -40 | 237937.9994 | -96 | 221037.9994
-37 | 242137.9994 | -34.5 | 242637.9994 | -31.5 | 234537.9994 | -28.5 | 232737.9994 | -26 | 234737.9994 | -23 | 237137.9994 | -20.5 | 231837.9994 | -17.5 | 228237.9994 | -14.5 | 243937.9994 | -12 | 242137.9994 | -9 | 240237.9994 | -6.5 | 238537.9994 | -3.5 | 237837.9994 | -0.5 | 221037.9994 | 2 | 239137.9994 | 5 | 229637.9994 | 7.5 | 237337.9994 | 10.5 | 228137.9994 | 13.5 | 232237.9994 | 16 | 240337.9994 | 19 | 237937.9994 | -37 | 221037.9994
21.5 | 242137.9994 | 24.5 | 242637.9994 | 27.5 | 234537.9994 | 30 | 232737.9994 | 33 | 234737.9994 | 35.5 | 237137.9994 | 38.5 | 231837.9994 | 41.5 | 228237.9994 | 44 | 243937.9994 | 47 | 242137.9994 | 49.5 | 240237.9994 | 52.5 | 238537.9994 | 55.5 | 237837.9994 | 58 | 221037.9994 | 61 | 239137.9994 | 63.5 | 229637.9994 | 66.5 | 237337.9994 | 69.5 | 228137.9994 | 72 | 232237.9994 | 75 | 240337.9994 | 77.5 | 237937.9994 | 21.5 | 221037.9994
80.5 | 242137.9994 | 83.5 | 242637.9994 | 86 | 234537.9994 | 89 | 232737.9994 | 91.5 | 234737.9994 | 94.5 | 237137.9994 | 97.5 | 231837.9994 | 100 | 228237.9994 | 103 | 243937.9994 | 105.5 | 242137.9994 | 108.5 | 240237.9994 | 111.5 | 238537.9994 | 114 | 237837.9994 | 117 | 221037.9994 | 119.5 | 239137.9994 | 122.5 | 229637.9994 | 125.5 | 237337.9994 | 128 | 228137.9994 | 131 | 232237.9994 | 133.5 | 240337.9994 | 136.5 | 237937.9994 | 80.5 | 221037.9994
139.5 | 242137.9994 | 142 | 242637.9994 | 145 | 234537.9994 | 147.5 | 232737.9994 | 150.5 | 234737.9994 | 153.5 | 237137.9994 | 156 | 231837.9994 | 159 | 228237.9994 | 161.5 | 243937.9994 | 164.5 | 242137.9994 | 167.5 | 240237.9994 | 170.5 | 238537.9994 | 173 | 237837.9994 | 175.5 | 221037.9994 | 178.5 | 239137.9994 | 181.5 | 229637.9994 | 184 | 237337.9994 | 187 | 228137.9994 | 189.5 | 232237.9994 | 192.5 | 240337.9994 | 195.5 | 237937.9994 | 139.5 | 221037.9994
198 | 242137.9994 | 201 | 242637.9994 | 203.5 | 234537.9994 | 206.5 | 232737.9994 | 209.5 | 234737.9994 | 212 | 237137.9994 | 215 | 231837.9994 | 217.5 | 228237.9994 | 220.5 | 243937.9994 | 223.5 | 242137.9994 | 226 | 240237.9994 | 229 | 238537.9994 | 231.5 | 237837.9994 | 234.5 | 221037.9994 | 237.5 | 239137.9994 | 240 | 229637.9994 | 243 | 237337.9994 | 245.5 | 228137.9994 | 248.5 | 232237.9994 | 251.5 | 240337.9994 | 254 | 237937.9994 | 198 | 221037.9994
257 | 242137.9994 | 259.5 | 242637.9994 | 262.5 | 234537.9994 | 265.5 | 232737.9994 | 268 | 234737.9994 | 271 | 237137.9994 | 273.5 | 231837.9994 | 276.5 | 228237.9994 | 279.5 | 243937.9994 | 282 | 242137.9994 | 285 | 240237.9994 | 287.5 | 238537.9994 | 290.5 | 237837.9994 | 293.5 | 221037.9994 | 296 | 239137.9994 | 299 | 229637.9994 | 301.5 | 237337.9994 | 304.5 | 228137.9994 | 307.5 | 232237.9994 | 310 | 240337.9994 | 313 | 237937.9994 | 257 | 221037.9994
315.5 | 242137.9994 | 318.5 | 242637.9994 | 321.5 | 234537.9994 | 324 | 232737.9994 | 327 | 234737.9994 | 329.5 | 237137.9994 | 332.5 | 231837.9994 | 335 | 228237.9994 | 338 | 243937.9994 | 340.5 | 242137.9994 | 343.5 | 240237.9994 | 346.5 | 238537.9994 | 349.5 | 237837.9994 | 352 | 221037.9994 | 355 | 239137.9994 | 357.5 | 229637.9994 | 360.5 | 237337.9994 | 363.5 | 228137.9994 | 366 | 232237.9994 | 369 | 240337.9994 | 371.5 | 237937.9994 | 315.5 | 221037.9994
374.5 | 242137.9994 | 377.5 | 242637.9994 | 380 | 234537.9994 | 383 | 232737.9994 | 385.5 | 234737.9994 | 388.5 | 237137.9994 | 391.5 | 231837.9994 | 394 | 228237.9994 | 396.5 | 243937.9994 | 399.5 | 242137.9994 | 402.5 | 240237.9994 | 405 | 238537.9994 | 408 | 237837.9994 | 411 | 221037.9994 | 413.5 | 239137.9994 | 416.5 | 229637.9994 | 419.5 | 237337.9994 | 422 | 228137.9994 | 425 | 232237.9994 | 427.5 | 240138.0832 | 430.5 | 237937.9994 | 374.5 | 221037.9994
433.5 | 242137.9994 | 436 | 242637.9994 | 438.5 | 234537.9994 | 441.5 | 232737.9994 | 444.5 | 234737.9994 | 447 | 237137.9994 | 450 | 231837.9994 | 452.5 | 228237.9994 | 455.5 | 243937.9994 | 458.5 | 242137.9994 | 461.5 | 240237.9994 | 464 | 238537.9994 | 466.5 | 237837.9994 | 469.5 | 221037.9994 | 472.5 | 239137.9994 | 475.5 | 229637.9994 | 478 | 237337.9994 | 480.5 | 228137.9994 | 483.5 | 232237.9994 | 486.5 | 240337.9994 | 489.5 | 237937.9994 | 433.5 | 221037.9994
492 | 242137.9994 | 495 | 242637.9994 | 497.5 | 234537.9994 | 500.5 | 232737.9994 | 503 | 234737.9994 | 506 | 237137.9994 | 509 | 231837.9994 | 511.5 | 228237.9994 | 514.5 | 243937.9994 | 517.5 | 242137.9994 | 520 | 240237.9994 | 522.5 | 238537.9994 | 525.5 | 237837.9994 | 528.5 | 110468.9988 | 531.5 | 239137.9994 | 534 | 229637.9994 | 537 | 237337.9994 | 539.5 | 228137.9994 | 542.5 | 232237.9994 | 545 | 240337.9994 | 548 | 237937.9994 | 492 | 110468.9988
551 | 242137.9994 | 553.5 | 242637.9994 | 556.5 | 234537.9994 | 559.5 | 232737.9994 | 562 | 234737.9994 | 565 | 237137.9994 | 567.5 | 231837.9994 | 570.5 | 228237.9994 | 573.5 | 243937.9994 | 576 | 242137.9994 | 578.5 | 240237.9994 | 581.5 | 238537.9994 | 584.5 | 237837.9994 | 587.5 | 221037.9994 | 590 | 239137.9994 | 593 | 229637.9994 | 595.5 | 237337.9994 | 598.5 | 228137.9994 | 601.5 | 232237.9994 | 604 | 240337.9994 | 606.5 | 237937.9994 | 551 | 221037.9994
609.5 | 242137.9994 | 612.5 | 242637.9994 | 615.5 | 234537.9994 | 618 | 232737.9994 | 621 | 234737.9994 | 623.5 | 237137.9994 | 626.5 | 231837.9994 | 629 | 228237.9994 | 632 | 243937.9994 | 635 | 242137.9994 | 637.5 | 240237.9994 | 640.5 | 238537.9994 | 643 | 237837.9994 | 646 | 221037.9994 | 649 | 239137.9994 | 651.5 | 229637.9994 | 654.5 | 237337.9994 | 657 | 228137.9994 | 660 | 232237.9994 | 663 | 240337.9994 | 665.5 | 237937.9994 | 609.5 | 221037.9994
668.5 | 242137.9994 | 671.5 | 242637.9994 | 674 | 234537.9994 | 676.5 | 232737.9994 | 679.5 | 234737.9994 | 682.5 | 237137.9994 | 685.5 | 231837.9994 | 688 | 228237.9994 | 690.5 | 243937.9994 | 693.5 | 242137.9994 | 696.5 | 240237.9994 | 699 | 238537.9994 | 702 | 237837.9994 | 705 | 221037.9994 | 707.5 | 239137.9994 | 710.5 | 229637.9994 | 713 | 237337.9994 | 716 | 228137.9994 | 719 | 232237.9994 | 721.5 | 240337.9994 | 724.5 | 237937.9994 | 668.5 | 221037.9994
727 | 242137.9994 | 730 | 242637.9994 | 733 | 234537.9994 | 735.5 | 232737.9994 | 738.5 | 234737.9994 | 741.5 | 237137.9994 | 744 | 231837.9994 | 746.5 | 228237.9994 | 749.5 | 243937.9994 | 752.5 | 242137.9994 | 755.5 | 240237.9994 | 758 | 238537.9994 | 760.5 | 237837.9994 | 763.5 | 221037.9994 | 766.5 | 239137.9994 | 769 | 229637.9994 | 772 | 237337.9994 | 774.5 | 228137.9994 | 777.5 | 232237.9994 | 780.5 | 240337.9994 | 783 | 237937.9994 | 727 | 221037.9994
786 | 242137.9994 | 788.5 | 242637.9994 | 791.5 | 234537.9994 | 794.5 | 232737.9994 | 797.5 | 234737.9994 | 800 | 237137.9994 | 802.5 | 231837.9994 | 805.5 | 228237.9994 | 808.5 | 243937.9994 | 811.5 | 242137.9994 | 814 | 240237.9994 | 817 | 238537.9994 | 819.5 | 237837.9994 | 822.5 | 221037.9994 | 825 | 239137.9994 | 828 | 229637.9994 | 830.5 | 237337.9994 | 833.5 | 228137.9994 | 836.5 | 232237.9994 | 839.5 | 240337.9994 | 842 | 237937.9994 | 786 | 221037.9994
844.5 | 242137.9994 | 847.5 | 242637.9994 | 850.5 | 234537.9994 | 853 | 232737.9994 | 856 | 234737.9994 | 859 | 237137.9994 | 861.5 | 231837.9994 | 864.5 | 228237.9994 | 867 | 243937.9994 | 870 | 242137.9994 | 873 | 240237.9994 | 875.5 | 238537.9994 | 878.5 | 237837.9994 | 881 | 221037.9994 | 884 | 239137.9994 | 887 | 229637.9994 | 889.5 | 237337.9994 | 892.5 | 228137.9994 | 895 | 232237.9994 | 898 | 240337.9994 | 901 | 237937.9994 | 844.5 | 221037.9994
903.5 | 242137.9994 | 906.5 | 242637.9994 | 909.5 | 234537.9994 | 912 | 232737.9994 | 914.5 | 234737.9994 | 917.5 | 237137.9994 | 920.5 | 231837.9994 | 923.5 | 228237.9994 | 926 | 243937.9994 | 928.5 | 242137.9994 | 931.5 | 240237.9994 | 934.5 | 238537.9994 | 937 | 237837.9994 | 940 | 221037.9994 | 942.5 | 239137.9994 | 945.5 | 229637.9994 | 948.5 | 237337.9994 | 951 | 228137.9994 | 954 | 232237.9994 | 956.5 | 240337.9994 | 959.5 | 237937.9994 | 903.5 | 221037.9994
962.5 | 242137.9994 | 965 | 242637.9994 | 968 | 234537.9994 | 971 | 232737.9994 | 973.5 | 234737.9994 | 976.5 | 237137.9994 | 979 | 231837.9994 | 982 | 228237.9994 | 984.5 | 243937.9994 | 987.5 | 242137.9994 | 990.5 | 240237.9994 | 993 | 238537.9994 | 996 | 237837.9994 | 998.5 | 221037.9994 | 1001.5 | 239137.9994 | 1004.5 | 229637.9994 | 1007 | 237337.9994 | 1010 | 228137.9994 | 1012.5 | 232237.9994 | 1015.5 | 240337.9994 | 1018.5 | 237937.9994 | 962.5 | 221037.9994
1021.5 | 242137.9994 | 1024 | 242637.9994 | 1026.5 | 234537.9994 | 1029.5 | 232737.9994 | 1032.5 | 234737.9994 | 1035 | 237137.9994 | 1038 | 231837.9994 | 1040.5 | 228237.9994 | 1043.5 | 243937.9994 | 1046.5 | 242137.9994 | 1049 | 240237.9994 | 1052 | 238537.9994 | 1054.5 | 237837.9994 | 1057.5 | 221037.9994 | 1060.5 | 119518.9988 | 1063 | 229637.9994 | 1066 | 237337.9994 | 1068.5 | 228137.9994 | 1071.5 | 232237.9994 | 1074.5 | 240337.9994 | 1077 | 237937.9994 | 1021.5 | 119518.9988
1080 | 242137.9994 | 1082.5 | 242637.9994 | 1085.5 | 234537.9994 | 1088.5 | 232737.9994 | 1091 | 234737.9994 | 1094 | 237137.9994 | 1096.5 | 231837.9994 | 1099.5 | 228237.9994 | 1102.5 | 243937.9994 | 1105 | 242137.9994 | 1108 | 240237.9994 | 1110.5 | 119218.9988 | 1113.5 | 237837.9994 | 1116.5 | 221037.9994 | 1119 | 239137.9994 | 1122 | 229637.9994 | 1124.5 | 237337.9994 | 1127.5 | 228137.9994 | 1131 | 232237.9994 | 1133 | 240337.9994 | 1136 | 237937.9994 | 1080 | 119218.9988
1138.5 | 242137.9994 | 1141.5 | 242637.9994 | 1144.5 | 234537.9994 | 1147 | 232737.9994 | 1150 | 234737.9994 | 1152.5 | 237137.9994 | 1155.5 | 231837.9994 | 1158.5 | 228237.9994 | 1161 | 243937.9994 | 1164 | 242137.9994 | 1166.5 | 240237.9994 | 1169.5 | 238537.9994 | 1172.5 | 237837.9994 | 1175 | 221037.9994 | 1178 | 239137.9994 | 1180.5 | 229637.9994 | 1183.5 | 237337.9994 | 1186.5 | 228137.9994 | 1189 | 232237.9994 | 1192 | 240138.0832 | 1194.5 | 13005.1931 | 1138.5 | 13005.1931
1197.5 | 40223.1099 | 1200.5 | 242438.0824 | 1203 | 234537.9994 | 1206 | 232737.9994 | 1208.5 | 234737.9994 | 1211.5 | 237137.9994 | 1214.5 | 231837.9994 | 1217 | 228237.9994 | 1220 | 243937.9994 | 1222.5 | 242137.9994 | 1225.5 | 275.7914 | 1228.5 | 29655.0581 | 1231 | 237637.958 | 1234 | 221037.9994 | 1236.5 | 238938.0836 | 1239.5 | 229438.0871 | 1242.5 | 237337.9994 | 1245 | 228137.9994 | 1248 | 230673.3936 | 1250.5 | 88.8375 | 1253.5 | 24.49 | 1197.5 | 24.49
1256.5 | 17124.7761 | 1259 | 30142.7885 | 1262 | 46747.8212 | 1264.5 | 77445.9714 | 1267.5 | 117019.2555 | 1270.5 | 9634.3501 | 1273 | 231438.2587 | 1276 | 114068.9988 | 1278.5 | 108.1461 | 1281.5 | 72.1364 | 1284.5 | 56.1667 | 1287 | 15729.7447 | 1290 | 19467.1504 | 1292.5 | 367.0363 | 1295.5 | 64.522 | 1298.5 | 1639.1141 | 1301 | 99.2433 | 1304 | 51.5673 | 1306.5 | 650.0843 | 1309.5 | 28.2967 | 1312.5 | 11.2795 | 1256.5 | 11.2795
1315 | 35.8939 | 1318 | 91.1086 | 1320.5 | 160.6248 | 1324 | 7140.2414 | 1326.5 | 36.3873 | 1329 | 28.7924 | 1332 | 28.2125 | 1334.5 | 2793.9916 | 1337.5 | 285.6296 | 1340.5 | 27.7893 | 1343 | 72.6112 | 1346 | 342.322 | 1348.5 | 87.8976 | 1351.5 | 19.1407 | 1354.5 | 59.3378 | 1357 | 2080.1988 | 1360 | 244.0107 | 1362.5 | 6.7414 | 1365.5 | 72.9656 | 1368.5 | 16.7315 | 1371 | 75.6539 | 1315 | 6.7414
1374 | 20.7913 | 1376.5 | 61.1076 | 1379.5 | 6.6668 | 1382.5 | 3768.4291 | 1385 | 880.3551 | 1388 | 98.0883 | 1390.5 | 31.1823 | 1393.5 | 65.1279 | 1396.5 | 579.106 | 1399 | 110.773 | 1402 | 55.1992 | 1404.5 | 75.3522 | 1407.5 | 45.2938 | 1410.5 | 528.5401 | 1413 | 673.9827 | 1416 | 43.5154 | 1418.5 | 1679.6429 | 1421.5 | 56.1967 | 1424.5 | 1367.1327 | 1427 | 47.2805 | 1430 | 423.0583 | 1374 | 6.6668
1432.5 | 15.9957 | 1435.5 | 76.2493 | 1438.5 | 38.0759 | 1441 | 46.6807 | 1444 | 20.2486 | 1446.5 | 54.3178 | 1449.5 | 30.1839 | 1452.5 | 66.9938 | 1455 | 63.3412 | 1458 | 16.9698 | 1460.5 | 44.8144 | 1463.5 | 56.0167 | 1466.5 | 17.8401 | 1469 | 22.4242 | 1472 | 54.0694 | 1474.5 | 28.128 | 1477.5 | 38.9832 | 1480.5 | 179.3094 | 1483 | 11.5845 | 1486 | 144.2179 | 1488.5 | 24.0762 | 1432.5 | 11.5845
1491.5 | 66.376 | 1494.5 | 54.9492 | 1497 | 52.3764 | 1500 | 53.8546 | 1502.5 | 124.6033 | 1505.5 | 65.2108 | 1508.5 | 54.9532 | 1511 | 30.0465 | 1514 | 16.5897 | 1516.5 | 92.1014 | 1519.5 | 10.1585 | 1522.5 | 334.5992 | 1525 | 39.2484 | 1528 | 23.1546 | 1530.5 | 10.1975 | 1533.5 | 6.1669 | 1536.5 | 26.1193 | 1539 | 0.6701 | 1542 | 17.382 | 1544.5 | 26.5504 | 1547.5 | 50.3538 | 1491.5 | 0.6701
1550.5 | 7.9521 | 1553 | 23.5281 | 1556 | 0.38979 | 1558.5 | 1.5617 | 1561.5 | 17.6769 | 1564.5 | 48.3004 | 1567 | 8.3654 | 1570 | 0.91427 | 1572.5 | 37.1293 | 1575.5 | 31.6609 | 1578.5 | 17.3267 | 1581 | 18.2374 | 1584 | 51.5568 | 1586.5 | 1.6382 | 1589.5 | 89.9751 | 1592.5 | 0.42886 | 1595 | 79.8144 | 1598 | 20.2207 | 1600.5 | 31.3235 | 1603.5 | 106.657 | 1606.5 | 41.0732 | 1550.5 | 0.38979
1609 | 158.3605 | 1612 | 69.3762 | 1614.5 | 50.018 | 1617.5 | 40.1634 | 1620.5 | 117.2744 | 1623 | 1.0056 | 1626 | 164.6316 | 1628.5 | 45.4519 | 1631.5 | 92.7602 | 1634.5 | 293.4346 | 1637 | 33.7836 | 1640 | 169.8019 | 1642.5 | 72.9263 | 1645.5 | 17.3236 | 1648.5 | 8.6441 | 1651 | 325.4457 | 1653.5 | 43.1145 | 1656.5 | 379.2281 | 1659.5 | 7.6615 | 1662.5 | 772.0531 | 1665 | 171.2959 | 1609 | 1.0056
1668 | 54.5548 | 1670.5 | 141.2246 | 1673.5 | 50.2082 | 1676.5 | 48.0199 | 1679 | 56.7775 | 1682 | 56.7895 | 1684.5 | 39.0481 | 1687.5 | 3.5356 | 1690 | 54.0258 | 1693 | 139.8794 | 1696 | 4.1381 | 1698.5 | 328.2643 | 1701.5 | 10.3525 | 1704.5 | 274.7665 | 1707 | 28.0502 | 1710 | 7.7765 | 1712.5 | 224.6083 | 1715.5 | 156.2472 | 1718.5 | 449.8332 | 1721 | 21.1673 | 1724 | 582.6661 | 1668 | 3.5356
1726.5 | 15.0628 | 1729.5 | 2.1986 | 1732.5 | 4.858 | 1735 | 426.0689 | 1738 | 244.0866 | 1740.5 | 16.9403 | 1743.5 | 265.9155 | 1746 | 396.3394 | 1749 | 43.2104 | 1752 | 117.7692 | 1754.5 | 39.1079 | 1757.5 | 343.8289 | 1760.5 | 0.46879 | 1763 | 332.2557 | 1766 | 132.5273 | 1768.5 | 6.4985 | 1771.5 | 71.4965 | 1774.5 | 5.2741 | 1777 | 253.3008 | 1779.5 | 74.2199 | 1782.5 | 8.2884 | 1726.5 | 0.46879
1785.5 | 209.8352 | 1788.5 | 95.1623 | 1791 | 298.3546 | 1794 | 214.2497 | 1796.5 | 9.2797 | 1799.5 | 330.9126 | 1802.5 | 18.0577 | 1805 | 65.2704 | 1807.5 | 40.6266 | 1810.5 | 5.3532 | 1813.5 | 440.9364 | 1816.5 | 12.1475 | 1819 | 313.1521 | 1821.5 | 25.6944 | 1824.5 | 5.6402 | 1827.5 | 30.1574 | 1830.5 | 0.79168 | 1833 | 9.6969 | 1836 | 35.3694 | 1838.5 | 13.2217 | 1841.5 | 255.1024 | 1785.5 | 0.79168
1844 | 46.0868 | 1847 | 42.4915 | 1849.5 | 163.7241 | 1852.5 | 2.8365 | 1855.5 | 0.49623 | 1858.5 | 249.4642 | 1861 | 0.41808 | 1864 | 62.4954 | 1866.5 | 137.9983 | 1869.5 | 17.6163 | 1872 | 47.7045 | 1875 | 49.207 | 1878 | 35.2429 | 1880.5 | 15.8369 | 1883.5 | 27.1031 | 1886 | 13.0736 | 1889 | 4.1148 | 1892 | 1.3692 | 1894.5 | 4.7747 | 1897.5 | 2.8644 | 1900.5 | 27.2603 | 1844 | 0.41808
1903 | 39.9607 | 1906 | 6.5536 | 1908.5 | 17.1142 | 1911.5 | 33.4689 | 1914.5 | 17.9922 | 1917 | 18.2476 | 1920 | 45.7115 | 1922.5 | 19.9731 | 1925.5 | 9.6728 | 1928 | 43.0077 | 1931 | 9.8562 | 1934 | 51.3542 | 1936.5 | 14.424 | 1939.5 | 41.2007 | 1942 | 15.3839 | 1945 | 44.8041 | 1947.5 | 4.5875 | 1950.5 | 46.2903 | 1953.5 | 11.2691 | 1956.5 | 13.0969 | 1959 | 46.6972 | 1903 | 4.5875

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -97 | 30.6667 | 28.0083 | 27.98 | 27.9152 | 28.0908 | 25.9457 | 25.8082
0.6309 | -96.3691 | 30.6557 | 28.0052 | 27.9806 | 27.9179 | 28.0937 | 25.9444 | 25.8048
1.5823 | -95.4177 | 30.6568 | 28.0058 | 27.9817 | 27.9132 | 28.0791 | 25.9472 | 25.8028
2.5837 | -94.4163 | 30.6564 | 28.0047 | 27.9763 | 27.9094 | 28.0702 | 25.9418 | 25.797
3.5852 | -93.4148 | 30.65 | 28.0004 | 27.9734 | 27.9091 | 28.0745 | 25.9466 | 25.8018
4.5866 | -92.4134 | 30.6555 | 27.9952 | 27.9804 | 27.9138 | 28.0825 | 25.9525 | 25.8046
5.588 | -91.412 | 30.6514 | 27.9938 | 27.9736 | 27.9164 | 28.079 | 25.9485 | 25.8021
6.6195 | -90.3805 | 30.6436 | 27.9864 | 27.9804 | 27.9053 | 28.0832 | 25.9516 | 25.8013
7.5909 | -89.4091 | 30.6441 | 27.9932 | 27.9724 | 27.9062 | 28.0832 | 25.9546 | 25.8011
8.5823 | -88.4177 | 30.6418 | 27.9976 | 27.9774 | 27.9153 | 28.0821 | 25.9516 | 25.7967
9.5838 | -87.4162 | 30.6345 | 27.9876 | 27.9714 | 27.9072 | 28.0813 | 25.9515 | 25.8048
10.5852 | -86.4148 | 30.6337 | 27.9923 | 27.9729 | 27.9074 | 28.0863 | 25.9518 | 25.7999
11.5867 | -85.4133 | 30.6278 | 27.9905 | 27.9822 | 27.9075 | 28.0873 | 25.9535 | 25.805
12.5881 | -84.4119 | 30.6205 | 27.9942 | 27.976 | 27.9152 | 28.0823 | 25.9551 | 25.7971
13.5895 | -83.4105 | 30.6225 | 27.9901 | 27.9796 | 27.9094 | 28.0803 | 25.9555 | 25.7998
14.581 | -82.419 | 30.6151 | 27.9913 | 27.985 | 27.9101 | 28.0791 | 25.9555 | 25.809
15.5824 | -81.4176 | 30.618 | 27.9923 | 27.9738 | 27.9089 | 28.0785 | 25.9589 | 25.8023
16.5838 | -80.4162 | 30.616 | 27.9876 | 27.9795 | 27.9145 | 28.0806 | 25.9532 | 25.8008
17.5853 | -79.4147 | 30.6064 | 27.9946 | 27.9705 | 27.9175 | 28.0824 | 25.956 | 25.7996
18.5867 | -78.4133 | 30.6014 | 27.9917 | 27.9737 | 27.9094 | 28.0866 | 25.9576 | 25.8038
19.5882 | -77.4118 | 30.6039 | 27.9922 | 27.9685 | 27.9123 | 28.0831 | 25.956 | 25.8022
20.5896 | -76.4104 | 30.5957 | 27.9983 | 27.9791 | 27.9144 | 28.092 | 25.9592 | 25.801
21.581 | -75.419 | 30.5973 | 27.9991 | 27.9698 | 27.9107 | 28.0886 | 25.9605 | 25.798
22.5925 | -74.4075 | 30.5934 | 27.994 | 27.9816 | 27.9138 | 28.092 | 25.9547 | 25.8073
23.5839 | -73.4161 | 30.587 | 27.9966 | 27.9857 | 27.916 | 28.0817 | 25.9576 | 25.8028
24.5854 | -72.4146 | 30.5849 | 27.9964 | 27.9746 | 27.9169 | 28.0805 | 25.9594 | 25.8059
25.5868 | -71.4132 | 30.5772 | 27.9976 | 27.9796 | 27.9087 | 28.0781 | 25.9597 | 25.8047
26.5882 | -70.4118 | 30.5718 | 27.999 | 27.981 | 27.9137 | 28.0833 | 25.959 | 25.8057
27.5897 | -69.4103 | 30.5693 | 27.9892 | 27.9813 | 27.9114 | 28.0801 | 25.9558 | 25.8063
28.5811 | -68.4189 | 30.5608 | 27.9981 | 27.9671 | 27.9099 | 28.0838 | 25.9549 | 25.8061
29.5825 | -67.4175 | 30.5566 | 27.997 | 27.9788 | 27.9091 | 28.0792 | 25.9617 | 25.8124
30.584 | -66.416 | 30.5501 | 27.9937 | 27.9773 | 27.9097 | 28.0733 | 25.9643 | 25.8084
31.5854 | -65.4146 | 30.5507 | 27.9947 | 27.9806 | 27.9159 | 28.0858 | 25.9636 | 25.8091
32.5869 | -64.4131 | 30.5456 | 27.9964 | 27.9756 | 27.9146 | 28.0861 | 25.9672 | 25.8104
33.5883 | -63.4117 | 30.5491 | 27.9878 | 27.9877 | 27.9105 | 28.0829 | 25.96 | 25.8131
34.5897 | -62.4103 | 30.5428 | 27.9899 | 27.973 | 27.9095 | 28.0749 | 25.9675 | 25.8088
35.5912 | -61.4088 | 30.5367 | 27.9955 | 27.9838 | 27.9108 | 28.0741 | 25.9616 | 25.8125
36.5826 | -60.4174 | 30.5312 | 27.9942 | 27.9804 | 27.9148 | 28.0837 | 25.9648 | 25.8117
37.584 | -59.416 | 30.5319 | 27.9966 | 27.9807 | 27.9084 | 28.0783 | 25.9693 | 25.8163
38.5855 | -58.4145 | 30.5358 | 27.9948 | 27.9737 | 27.9063 | 28.0781 | 25.9576 | 25.8142
39.5869 | -57.4131 | 30.529 | 27.995 | 27.9857 | 27.9115 | 28.0786 | 25.9635 | 25.8132
40.5884 | -56.4116 | 30.5271 | 27.9967 | 27.9801 | 27.9104 | 28.0859 | 25.9656 | 25.8133
41.5898 | -55.4102 | 30.5227 | 27.9993 | 27.9757 | 27.9095 | 28.0813 | 25.9652 | 25.8126
42.5812 | -54.4188 | 30.5244 | 28.0031 | 27.9808 | 27.9142 | 28.0747 | 25.9697 | 25.8154
43.5827 | -53.4173 | 30.5269 | 27.9962 | 27.9734 | 27.9113 | 28.0798 | 25.9613 | 25.8128
44.5841 | -52.4159 | 30.524 | 28.0027 | 27.983 | 27.9044 | 28.0726 | 25.9641 | 25.8094
45.5855 | -51.4145 | 30.524 | 27.9975 | 27.9814 | 27.9077 | 28.0752 | 25.9639 | 25.8158
46.587 | -50.413 | 30.5173 | 27.9955 | 27.9807 | 27.9134 | 28.0779 | 25.9658 | 25.816
47.5884 | -49.4116 | 30.5121 | 27.9922 | 27.9735 | 27.9097 | 28.081 | 25.9644 | 25.8165
48.5899 | -48.4101 | 30.5132 | 27.9953 | 27.9753 | 27.913 | 28.0803 | 25.9614 | 25.8137
49.5913 | -47.4087 | 30.5169 | 27.992 | 27.9739 | 27.9099 | 28.0869 | 25.968 | 25.8151
50.5827 | -46.4173 | 30.5096 | 27.9912 | 27.9814 | 27.9098 | 28.0797 | 25.9639 | 25.8174
51.5842 | -45.4158 | 30.508 | 27.9928 | 27.9799 | 27.9107 | 28.0818 | 25.9705 | 25.8167
52.5856 | -44.4144 | 30.507 | 27.9887 | 27.9759 | 27.9107 | 28.0817 | 25.9657 | 25.8112
53.5871 | -43.4129 | 30.5061 | 27.9911 | 27.9771 | 27.9156 | 28.0846 | 25.9706 | 25.8164
54.5885 | -42.4115 | 30.4998 | 27.9897 | 27.9797 | 27.9154 | 28.0827 | 25.9692 | 25.8187
55.5899 | -41.4101 | 30.4929 | 27.9986 | 27.9717 | 27.9168 | 28.0853 | 25.969 | 25.8166
56.5814 | -40.4186 | 30.4909 | 27.9907 | 27.9694 | 27.9122 | 28.0828 | 25.9674 | 25.8169
57.5828 | -39.4172 | 30.488 | 27.9902 | 27.9745 | 27.9173 | 28.083 | 25.9655 | 25.8181
58.5842 | -38.4158 | 30.4949 | 27.9894 | 27.9787 | 27.9184 | 28.0815 | 25.9671 | 25.8211
59.5857 | -37.4143 | 30.474 | 27.9953 | 27.9791 | 27.9125 | 28.0774 | 25.9618 | 25.814
60.5871 | -36.4129 | 30.4779 | 27.9928 | 27.9772 | 27.9171 | 28.0816 | 25.9693 | 25.8179
61.5886 | -35.4114 | 30.4714 | 27.9882 | 27.9716 | 27.9165 | 28.0756 | 25.9654 | 25.8218
62.59 | -34.41 | 30.4659 | 27.9893 | 27.9708 | 27.9145 | 28.0875 | 25.9655 | 25.8221
63.5914 | -33.4086 | 30.46 | 27.991 | 27.9736 | 27.915 | 28.088 | 25.9646 | 25.8162
64.5829 | -32.4171 | 30.4583 | 27.995 | 27.9777 | 27.9158 | 28.081 | 25.9687 | 25.822
65.5843 | -31.4157 | 30.4564 | 27.9837 | 27.9805 | 27.9122 | 28.0873 | 25.9677 | 25.8231
66.5857 | -30.4143 | 30.4533 | 27.9883 | 27.9809 | 27.9131 | 28.0837 | 25.9617 | 25.8193
67.5872 | -29.4128 | 30.443 | 27.9935 | 27.9672 | 27.9117 | 28.0832 | 25.9712 | 25.8252
68.5886 | -28.4114 | 30.4437 | 27.9848 | 27.9799 | 27.9128 | 28.0797 | 25.9728 | 25.8181
69.5901 | -27.4099 | 30.4489 | 27.9903 | 27.9833 | 27.9162 | 28.0833 | 25.9691 | 25.8231
70.5915 | -26.4085 | 30.4408 | 27.9865 | 27.9743 | 27.9131 | 28.084 | 25.9625 | 25.824
71.5829 | -25.4171 | 30.4335 | 27.995 | 27.9787 | 27.9203 | 28.0782 | 25.9692 | 25.8218
72.5844 | -24.4156 | 30.4256 | 27.9924 | 27.9739 | 27.912 | 28.0826 | 25.9694 | 25.8255
73.5858 | -23.4142 | 30.4159 | 27.9922 | 27.9716 | 27.9075 | 28.0831 | 25.9677 | 25.8205
74.5873 | -22.4127 | 30.4145 | 27.9884 | 27.9753 | 27.9118 | 28.0814 | 25.9668 | 25.8269
75.5887 | -21.4113 | 30.4126 | 27.9863 | 27.9742 | 27.9158 | 28.081 | 25.9706 | 25.8281
76.5801 | -20.4199 | 30.4075 | 27.9888 | 27.9771 | 27.9187 | 28.0801 | 25.9666 | 25.8244
77.5816 | -19.4184 | 30.405 | 27.9883 | 27.9773 | 27.9102 | 28.081 | 25.969 | 25.8272
78.583 | -18.417 | 30.4043 | 27.9914 | 27.987 | 27.9124 | 28.0863 | 25.9749 | 25.8252
79.5844 | -17.4156 | 30.4036 | 27.9916 | 27.9745 | 27.9119 | 28.0822 | 25.9725 | 25.828
80.5859 | -16.4141 | 30.4064 | 27.9869 | 27.9804 | 27.9149 | 28.0895 | 25.968 | 25.8247
81.5873 | -15.4127 | 30.4045 | 27.983 | 27.9736 | 27.9171 | 28.0826 | 25.9707 | 25.8351
82.5888 | -14.4112 | 30.3987 | 27.9878 | 27.9754 | 27.9139 | 28.0869 | 25.9727 | 25.823
83.5902 | -13.4098 | 30.3981 | 27.99 | 27.984 | 27.9087 | 28.0828 | 25.9752 | 25.8293
84.5816 | -12.4184 | 30.3942 | 27.9874 | 27.9743 | 27.9108 | 28.0847 | 25.9653 | 25.8295
85.5831 | -11.4169 | 30.3893 | 27.9865 | 27.979 | 27.9089 | 28.0809 | 25.9684 | 25.8299
86.5845 | -10.4155 | 30.398 | 27.9864 | 27.9773 | 27.9086 | 28.0735 | 25.9678 | 25.8235
87.5859 | -9.4141 | 30.3926 | 27.9873 | 27.9771 | 27.9114 | 28.086 | 25.9787 | 25.8305
88.5874 | -8.4126 | 30.395 | 27.9904 | 27.9747 | 27.9154 | 28.083 | 25.9643 | 25.8249
89.5888 | -7.4112 | 30.3862 | 27.9932 | 27.9773 | 27.9137 | 28.0789 | 25.9701 | 25.8258
90.5903 | -6.4097 | 30.383 | 27.9872 | 27.9805 | 27.9153 | 28.0892 | 25.9658 | 25.8269
91.5917 | -5.4083 | 30.3827 | 27.9861 | 27.9702 | 27.9092 | 28.0793 | 25.9626 | 25.8279
92.5831 | -4.4169 | 30.3779 | 27.9835 | 27.9785 | 27.9107 | 28.0829 | 25.9725 | 25.8315
93.5846 | -3.4154 | 30.3749 | 27.9862 | 27.9774 | 27.9091 | 28.0795 | 25.975 | 25.8316
94.586 | -2.414 | 30.369 | 27.8441 | 27.9448 | 27.8456 | 28.2219 | 26.0126 | 25.8244
95.5874 | -1.4126 | 30.3654 | 27.8675 | 27.9786 | 27.8667 | 28.2429 | 25.9979 | 25.8262
96.5889 | -0.4111 | 30.4477 | 27.9032 | 27.9799 | 27.881 | 28.2063 | 25.9838 | 25.8256
97.5803 | 0.5803 | 30.9282 | 27.9338 | 27.9801 | 27.8913 | 28.1901 | 25.9798 | 25.8272
98.5818 | 1.5818 | 31.9776 | 27.9331 | 27.982 | 27.8925 | 28.1754 | 25.98 | 25.8296
99.5832 | 2.5832 | 33.6106 | 27.9404 | 27.9768 | 27.8956 | 28.1717 | 25.9805 | 25.831
100.5846 | 3.5846 | 35.7368 | 27.9461 | 27.9818 | 27.8987 | 28.155 | 25.9794 | 25.8296
101.5861 | 4.5861 | 38.3261 | 27.9483 | 27.9769 | 27.8999 | 28.1562 | 25.979 | 25.8356
102.5875 | 5.5875 | 41.2817 | 27.9439 | 27.9696 | 27.9105 | 28.1542 | 25.9847 | 25.8325
103.589 | 6.589 | 44.5578 | 27.9478 | 27.976 | 27.9079 | 28.153 | 25.992 | 25.8332
104.5904 | 7.5904 | 48.102 | 27.9529 | 27.9758 | 27.9092 | 28.1724 | 25.9902 | 25.8435
105.5818 | 8.5818 | 51.9119 | 27.9617 | 27.9722 | 27.9122 | 28.1709 | 25.9988 | 25.8398
106.5833 | 9.5833 | 55.9366 | 27.9711 | 27.978 | 27.9227 | 28.1755 | 26.0167 | 25.8549
107.5847 | 10.5847 | 60.1468 | 27.9821 | 27.969 | 27.93 | 28.1913 | 26.0318 | 25.8645
108.5861 | 11.5861 | 64.5322 | 27.9922 | 27.9852 | 27.9464 | 28.2023 | 26.0447 | 25.8857
109.5876 | 12.5876 | 69.084 | 28.0053 | 27.9788 | 27.9574 | 28.2177 | 26.0654 | 25.8989
110.589 | 13.589 | 73.7561 | 28.0277 | 27.9797 | 27.9744 | 28.2279 | 26.0932 | 25.9229
111.5905 | 14.5905 | 78.5846 | 28.0457 | 27.9836 | 28.0011 | 28.26 | 26.1303 | 25.9435
112.5919 | 15.5919 | 83.5407 | 28.0768 | 27.9813 | 28.0261 | 28.2807 | 26.1601 | 25.9691
113.5833 | 16.5833 | 88.5855 | 28.108 | 27.9896 | 28.0533 | 28.3133 | 26.1932 | 25.9946
114.5848 | 17.5848 | 93.6957 | 28.1491 | 27.9853 | 28.0853 | 28.3469 | 26.2409 | 26.0333
115.5862 | 18.5862 | 98.931 | 28.1824 | 27.9981 | 28.1324 | 28.3719 | 26.3036 | 26.0744
116.5876 | 19.5876 | 104.3057 | 28.2305 | 28.005 | 28.1726 | 28.4281 | 26.3618 | 26.1196
117.5891 | 20.5891 | 109.7288 | 28.2868 | 28.0126 | 28.2237 | 28.474 | 26.4331 | 26.1722
118.5805 | 21.5805 | 115.2237 | 28.3409 | 28.0207 | 28.2806 | 28.5165 | 26.5025 | 26.2299
119.582 | 22.582 | 120.7666 | 28.4002 | 28.0289 | 28.3402 | 28.586 | 26.5901 | 26.2877
120.5834 | 23.5834 | 126.3348 | 28.4786 | 28.0464 | 28.4076 | 28.6465 | 26.6802 | 26.3616
121.5848 | 24.5848 | 131.8973 | 28.5583 | 28.0542 | 28.4797 | 28.7228 | 26.7824 | 26.4395
122.5863 | 25.5863 | 137.4437 | 28.6393 | 28.0653 | 28.5659 | 28.7934 | 26.8911 | 26.516
123.5877 | 26.5877 | 143.0004 | 28.7298 | 28.089 | 28.652 | 28.8832 | 27.0131 | 26.6107
124.5892 | 27.5892 | 148.5455 | 28.8301 | 28.1088 | 28.7484 | 28.9648 | 27.1452 | 26.711
125.5806 | 28.5806 | 154.1111 | 28.9354 | 28.1348 | 28.8495 | 29.0538 | 27.2917 | 26.8088
126.582 | 29.582 | 159.703 | 29.0606 | 28.1595 | 28.9641 | 29.1563 | 27.4449 | 26.9313
127.5835 | 30.5835 | 165.3036 | 29.1871 | 28.1872 | 29.0814 | 29.2718 | 27.6055 | 27.0534
128.5849 | 31.5849 | 170.8036 | 29.3171 | 28.2093 | 29.2162 | 29.395 | 27.7841 | 27.1792
129.5863 | 32.5863 | 176.2661 | 29.4621 | 28.2555 | 29.3533 | 29.5157 | 27.9691 | 27.3177
130.5878 | 33.5878 | 181.6796 | 29.6223 | 28.2971 | 29.4981 | 29.6565 | 28.1704 | 27.4717
131.5892 | 34.5892 | 187.1328 | 29.7835 | 28.3327 | 29.6562 | 29.7835 | 28.3779 | 27.6353
132.5907 | 35.5907 | 192.6633 | 29.9637 | 28.3731 | 29.8248 | 29.9245 | 28.6078 | 27.8098
133.5821 | 36.5821 | 198.108 | 30.1558 | 28.4289 | 30.0033 | 30.0968 | 28.8385 | 27.9827
134.5835 | 37.5835 | 203.3955 | 30.3497 | 28.4812 | 30.1879 | 30.2534 | 29.0915 | 28.1665
135.585 | 38.585 | 208.8362 | 30.5692 | 28.5448 | 30.3878 | 30.4389 | 29.3471 | 28.3655
136.5864 | 39.5864 | 214.1858 | 30.7979 | 28.6101 | 30.6037 | 30.6185 | 29.6149 | 28.5763
137.5878 | 40.5878 | 219.5541 | 31.0338 | 28.6758 | 30.8217 | 30.8085 | 29.9016 | 28.7955
138.5893 | 41.5893 | 225.0008 | 31.2853 | 28.7401 | 31.0527 | 31.0197 | 30.2026 | 29.0175
139.5807 | 42.5807 | 230.5115 | 31.5485 | 28.8225 | 31.2992 | 31.2328 | 30.5103 | 29.2564
140.5821 | 43.5821 | 235.9873 | 31.8229 | 28.9065 | 31.5681 | 31.4544 | 30.8329 | 29.5095
141.5836 | 44.5836 | 241.554 | 32.1205 | 29.0033 | 31.8334 | 31.6927 | 31.1756 | 29.7732
142.585 | 45.585 | 246.9897 | 32.4225 | 29.091 | 32.1295 | 31.9411 | 31.5148 | 30.0392
143.5865 | 46.5865 | 252.4443 | 32.7421 | 29.1954 | 32.4235 | 32.2131 | 31.8878 | 30.3347
144.5879 | 47.5879 | 257.8989 | 33.0695 | 29.307 | 32.7342 | 32.4855 | 32.2718 | 30.6283
145.5893 | 48.5893 | 263.2787 | 33.4166 | 29.4205 | 33.063 | 32.7653 | 32.6682 | 30.9359
146.5808 | 49.5808 | 268.631 | 33.7928 | 29.5474 | 33.4076 | 33.0522 | 33.078 | 31.2595
147.5822 | 50.5822 | 273.9784 | 34.168 | 29.6666 | 33.7739 | 33.3575 | 33.5001 | 31.603
148.5837 | 51.5837 | 279.4553 | 34.5548 | 29.808 | 34.1408 | 33.6825 | 33.9439 | 31.9607
149.5851 | 52.5851 | 284.888 | 34.9573 | 29.9406 | 34.5216 | 34.0149 | 34.3979 | 32.3234
150.5865 | 53.5865 | 290.2528 | 35.3766 | 30.0951 | 34.9304 | 34.3634 | 34.8699 | 32.7084
151.588 | 54.588 | 295.7356 | 35.814 | 30.2482 | 35.3381 | 34.7225 | 35.3515 | 33.101
152.5894 | 55.5894 | 301.1366 | 36.2663 | 30.4134 | 35.7756 | 35.0911 | 35.8545 | 33.5104
153.5909 | 56.5909 | 306.5164 | 36.7408 | 30.5939 | 36.218 | 35.4808 | 36.3695 | 33.9417
154.5823 | 57.5823 | 311.8024 | 37.2297 | 30.7733 | 36.6816 | 35.877 | 36.9096 | 34.379
155.5837 | 58.5837 | 316.9158 | 37.736 | 30.9558 | 37.1624 | 36.2897 | 37.463 | 34.8352
156.5852 | 59.5852 | 322.0443 | 38.2561 | 31.1544 | 37.6553 | 36.7017 | 38.0407 | 35.3051
157.5866 | 60.5866 | 327.2995 | 38.7932 | 31.3666 | 38.1646 | 37.1346 | 38.6192 | 35.7943
158.588 | 61.588 | 332.4696 | 39.3462 | 31.5778 | 38.6803 | 37.5911 | 39.2257 | 36.2836
159.5895 | 62.5895 | 337.7148 | 39.9126 | 31.7984 | 39.2264 | 38.0588 | 39.8439 | 36.796
160.5909 | 63.5909 | 343.0076 | 40.4874 | 32.0331 | 39.7794 | 38.527 | 40.4787 | 37.3352
161.5823 | 64.5823 | 348.1556 | 41.0966 | 32.2786 | 40.3582 | 39.0228 | 41.1259 | 37.8679
162.5838 | 65.5838 | 353.3382 | 41.7145 | 32.5317 | 40.9522 | 39.522 | 41.8004 | 38.4272
163.5852 | 66.5852 | 358.5681 | 42.355 | 32.7884 | 41.5679 | 40.0326 | 42.4725 | 39.0001
164.5867 | 67.5867 | 363.6065 | 43.0154 | 33.0603 | 42.189 | 40.5669 | 43.1758 | 39.5952
165.5881 | 68.5881 | 368.5642 | 43.7009 | 33.3403 | 42.8345 | 41.1254 | 43.8934 | 40.1973
166.5895 | 69.5895 | 373.6214 | 44.3983 | 33.6328 | 43.49 | 41.682 | 44.6195 | 40.8214
167.591 | 70.591 | 378.6925 | 45.1199 | 33.9357 | 44.167 | 42.2546 | 45.3759 | 41.4629
168.5824 | 71.5824 | 383.5347 | 45.8611 | 34.2459 | 44.857 | 42.8451 | 46.149 | 42.1192
169.5838 | 72.5838 | 388.5665 | 46.627 | 34.5688 | 45.5689 | 43.4479 | 46.9507 | 42.7893
170.5853 | 73.5853 | 393.7639 | 47.3916 | 34.8994 | 46.3093 | 44.074 | 47.7724 | 43.4741
171.5867 | 74.5867 | 398.736 | 48.1797 | 35.2412 | 47.0661 | 44.7052 | 48.6085 | 44.1688
172.5882 | 75.5882 | 403.6214 | 48.9909 | 35.5924 | 47.8552 | 45.3498 | 49.4655 | 44.882
173.5896 | 76.5896 | 408.4576 | 49.8114 | 35.964 | 48.6711 | 46.0277 | 50.3424 | 45.6191
174.591 | 77.591 | 413.2865 | 50.6557 | 36.3366 | 49.5217 | 46.7291 | 51.2378 | 46.3657
175.5825 | 78.5825 | 417.8726 | 51.5251 | 36.733 | 50.404 | 47.4443 | 52.1462 | 47.138
176.5839 | 79.5839 | 422.4814 | 52.4226 | 37.1268 | 51.3147 | 48.1914 | 53.0598 | 47.9152
177.5854 | 80.5854 | 427.0434 | 53.2554 | 37.5294 | 52.2128 | 49.0645 | 54.0181 | 48.715
178.5868 | 81.5868 | 431.6915 | 54.177 | 37.961 | 53.1585 | 49.9641 | 54.9651 | 49.5434
179.5882 | 82.5882 | 436.0681 | 55.2271 | 38.388 | 54.1547 | 50.7187 | 55.9287 | 50.3956
180.5897 | 83.5897 | 439.9908 | 56.2432 | 38.8449 | 55.1528 | 51.5962 | 56.9119 | 51.2748
181.5811 | 84.5811 | 443.7355 | 57.3203 | 39.2933 | 56.1933 | 52.4096 | 57.919 | 52.1695
182.5825 | 85.5825 | 447.1778 | 58.3965 | 39.7557 | 57.2283 | 53.312 | 58.9547 | 53.0864
183.584 | 86.584 | 450.4364 | 59.5452 | 40.2479 | 58.3055 | 54.1363 | 60.0134 | 54.0217
184.5854 | 87.5854 | 453.511 | 60.6457 | 40.7511 | 59.3715 | 55.085 | 61.119 | 54.9787
185.5869 | 88.5869 | 456.4182 | 61.7893 | 41.2569 | 60.4648 | 56.0143 | 62.2449 | 55.9405
186.5883 | 89.5883 | 459.094 | 62.9623 | 41.7776 | 61.5718 | 56.948 | 63.3829 | 56.9273
187.5897 | 90.5897 | 461.687 | 64.0735 | 42.3097 | 62.6534 | 57.9736 | 64.5737 | 57.9195
188.5812 | 91.5812 | 464.172 | 65.3384 | 42.8312 | 63.7938 | 58.8242 | 65.7197 | 58.9075
189.5826 | 92.5826 | 466.2719 | 66.5691 | 43.3912 | 64.9504 | 59.7729 | 66.8704 | 59.9199
190.584 | 93.584 | 468.1806 | 67.8234 | 43.9631 | 66.1206 | 60.6974 | 68.0348 | 60.9356
191.5855 | 94.5855 | 470.0663 | 69.0323 | 44.5404 | 67.2659 | 61.7185 | 69.2203 | 61.9614
192.5869 | 95.5869 | 471.7389 | 70.2892 | 45.1306 | 68.4224 | 62.6953 | 70.4054 | 62.9908
193.5884 | 96.5884 | 473.0533 | 71.5213 | 45.7271 | 69.5816 | 63.7188 | 71.6032 | 64.0347
194.5898 | 97.5898 | 473.9294 | 72.7774 | 46.342 | 70.7524 | 64.7388 | 72.8014 | 65.0788
195.5912 | 98.5912 | 474.5673 | 74.0762 | 46.9676 | 71.9443 | 65.7108 | 73.989 | 66.1327
196.5927 | 99.5927 | 474.977 | 75.3399 | 47.6068 | 73.1046 | 66.7519 | 75.1952 | 67.1917
197.5841 | 100.5841 | 475.1063 | 76.6356 | 48.2448 | 74.2942 | 67.7254 | 76.3804 | 68.251
198.5856 | 101.5856 | 475.4628 | 77.8892 | 48.8988 | 75.4723 | 68.8094 | 77.5876 | 69.3036
199.587 | 102.587 | 475.6712 | 79.2269 | 49.5568 | 76.6736 | 69.7345 | 78.761 | 70.3719
200.5884 | 103.5884 | 475.5432 | 80.4607 | 50.2306 | 77.8344 | 70.8245 | 79.9648 | 71.422
201.5899 | 104.5899 | 475.2834 | 81.7995 | 50.9051 | 79.0361 | 71.7848 | 81.1292 | 72.4835
202.5813 | 105.5813 | 475.0913 | 83.0507 | 51.6008 | 80.2042 | 72.8498 | 82.3166 | 73.532
203.5827 | 106.5827 | 475.0223 | 84.377 | 52.2975 | 81.3734 | 73.7914 | 83.4756 | 74.5782
204.5842 | 107.5842 | 474.7109 | 85.6377 | 53 | 82.5313 | 74.8262 | 84.6477 | 75.636
205.5856 | 108.5856 | 474.4807 | 86.9375 | 53.7058 | 83.6998 | 75.7979 | 85.791 | 76.6763
206.5871 | 109.5871 | 474.105 | 88.2027 | 54.4029 | 84.8656 | 76.8074 | 86.9447 | 77.7082
207.5885 | 110.5885 | 473.9119 | 89.4676 | 55.1401 | 86.0073 | 77.811 | 88.0879 | 78.7401
208.5899 | 111.5899 | 473.8393 | 90.7584 | 55.8572 | 87.1586 | 78.7753 | 89.2316 | 79.7727
209.5814 | 112.5814 | 473.514 | 91.9904 | 56.6046 | 88.2798 | 79.8032 | 90.3597 | 80.7896
210.5828 | 113.5828 | 473.0941 | 93.2784 | 57.318 | 89.4117 | 80.7452 | 91.4647 | 81.8065
211.5842 | 114.5842 | 472.7423 | 94.4842 | 58.0751 | 90.5007 | 81.7954 | 92.5942 | 82.8045
212.5857 | 115.5857 | 472.2082 | 95.7643 | 58.803 | 91.6044 | 82.7037 | 93.6813 | 83.8144
213.5871 | 116.5871 | 471.7746 | 96.9587 | 59.5531 | 92.6843 | 83.7517 | 94.7876 | 84.8155
214.5886 | 117.5886 | 471.4525 | 98.2214 | 60.2909 | 93.7812 | 84.6795 | 95.8605 | 85.8072
215.59 | 118.59 | 471.1599 | 99.4382 | 61.0516 | 94.8514 | 85.6938 | 96.9337 | 86.7927
216.5814 | 119.5814 | 470.8942 | 100.6422 | 61.7984 | 95.8917 | 86.6935 | 97.9973 | 87.7707
217.5929 | 120.5929 | 470.8042 | 101.8588 | 62.5518 | 96.9394 | 87.6755 | 99.0601 | 88.7451
218.5843 | 121.5843 | 470.7059 | 103.0563 | 63.3051 | 97.9681 | 88.6648 | 100.1073 | 89.7164
219.5857 | 122.5857 | 470.6317 | 104.2739 | 64.0658 | 99.0074 | 89.6263 | 101.1443 | 90.6864
220.5872 | 123.5872 | 470.5942 | 105.43 | 64.831 | 100.0095 | 90.6226 | 102.174 | 91.627
221.5886 | 124.5886 | 470.8505 | 106.6409 | 65.5832 | 101.0173 | 91.5724 | 103.21 | 92.5805
222.5901 | 125.5901 | 470.7842 | 107.795 | 66.3574 | 101.9892 | 92.5512 | 104.2412 | 93.5233
223.5815 | 126.5815 | 470.726 | 108.9788 | 67.1137 | 102.9713 | 93.4812 | 105.2547 | 94.4667
224.5829 | 127.5829 | 470.8345 | 110.1092 | 67.8688 | 103.9112 | 94.4546 | 106.2811 | 95.3926
225.5844 | 128.5844 | 470.9305 | 111.2753 | 68.6334 | 104.845 | 95.3638 | 107.2976 | 96.3142
226.5858 | 129.5858 | 471.1963 | 112.4143 | 69.3902 | 105.7633 | 96.3041 | 108.3265 | 97.233
227.5873 | 130.5873 | 471.4217 | 113.538 | 70.1458 | 106.6562 | 97.2306 | 109.3494 | 98.1435
228.5887 | 131.5887 | 471.4773 | 114.6621 | 70.9106 | 107.5508 | 98.1383 | 110.364 | 99.056
229.5901 | 132.5901 | 471.407 | 115.7521 | 71.6634 | 108.409 | 99.0825 | 111.3912 | 99.9625
230.5816 | 133.5816 | 471.4214 | 116.8865 | 72.4194 | 109.2689 | 99.9401 | 112.3971 | 100.8572
231.583 | 134.583 | 471.5008 | 117.9478 | 73.1801 | 110.111 | 100.8778 | 113.4247 | 101.7457
232.5844 | 135.5844 | 471.5736 | 119.0748 | 73.9275 | 110.9719 | 101.711 | 114.4252 | 102.6286
233.5859 | 136.5859 | 471.8119 | 120.1168 | 74.6815 | 111.7944 | 102.6361 | 115.4368 | 103.5196
234.5873 | 137.5873 | 471.9035 | 121.2209 | 75.4259 | 112.6802 | 103.4813 | 116.4311 | 104.3999
235.5888 | 138.5888 | 472.0363 | 122.2722 | 76.178 | 113.53 | 104.3969 | 117.4342 | 105.2723
236.5902 | 139.5902 | 472.3931 | 123.3507 | 76.9137 | 114.387 | 105.2218 | 118.4217 | 106.1305
237.5816 | 140.5816 | 472.8357 | 124.3797 | 77.6573 | 115.2216 | 106.1128 | 119.4236 | 106.9898
238.5831 | 141.5831 | 473.0972 | 125.4264 | 78.4031 | 116.057 | 106.9451 | 120.4048 | 107.852
239.5845 | 142.5845 | 473.3535 | 126.4564 | 79.1209 | 116.8675 | 107.7825 | 121.3918 | 108.7015
240.5859 | 143.5859 | 473.5552 | 127.4665 | 79.8586 | 117.6718 | 108.6637 | 122.4051 | 109.5484
241.5874 | 144.5874 | 473.8377 | 128.495 | 80.5802 | 118.4724 | 109.4746 | 123.3912 | 110.3839
242.5888 | 145.5888 | 474.0551 | 129.4826 | 81.3109 | 119.2331 | 110.3501 | 124.4212 | 111.2182
243.5903 | 146.5903 | 474.1078 | 130.5128 | 82.0292 | 120.0046 | 111.1497 | 125.4098 | 112.0443
244.5817 | 147.5817 | 474.2291 | 131.4897 | 82.7526 | 120.7342 | 112.013 | 126.4186 | 112.8781
245.5831 | 148.5831 | 474.3814 | 132.4871 | 83.4625 | 121.4699 | 112.8163 | 127.4103 | 113.6945
246.5846 | 149.5846 | 474.3352 | 133.4389 | 84.1752 | 122.1549 | 113.6884 | 128.4115 | 114.496
247.586 | 150.586 | 474.3337 | 134.4281 | 84.8934 | 122.8302 | 114.4897 | 129.395 | 115.2946
248.5875 | 151.5875 | 474.4198 | 135.3936 | 85.6092 | 123.492 | 115.3235 | 130.3804 | 116.0858
249.5889 | 152.5889 | 474.2305 | 136.3393 | 86.3193 | 124.1346 | 116.1615 | 131.3718 | 116.8745
250.5803 | 153.5803 | 474.059 | 137.3054 | 87.0196 | 124.7779 | 116.9511 | 132.3651 | 117.647
251.5818 | 154.5818 | 473.9932 | 138.2349 | 87.7392 | 125.4093 | 117.7944 | 133.3504 | 118.4168
252.5832 | 155.5832 | 474.0161 | 139.1984 | 88.4486 | 126.0304 | 118.5547 | 134.3235 | 119.1749
253.5846 | 156.5846 | 474.1728 | 140.0874 | 89.1636 | 126.6217 | 119.3818 | 135.3018 | 119.9257
254.5861 | 157.5861 | 474.288 | 141.0501 | 89.8638 | 127.2434 | 120.0979 | 136.252 | 120.674
255.5875 | 158.5875 | 474.4954 | 141.9601 | 90.5782 | 127.8461 | 120.8498 | 137.2217 | 121.4102
256.589 | 159.589 | 474.7788 | 142.8937 | 91.2926 | 128.4681 | 121.5414 | 138.171 | 122.1448
257.5904 | 160.5904 | 474.7581 | 143.8148 | 91.9941 | 129.0856 | 122.2492 | 139.1101 | 122.8789
258.5818 | 161.5818 | 474.6289 | 144.6991 | 92.7138 | 129.7054 | 122.9601 | 140.0533 | 123.5905
259.5833 | 162.5833 | 474.6834 | 145.6141 | 93.4326 | 130.3315 | 123.6282 | 140.9885 | 124.2945
260.5847 | 163.5847 | 474.7921 | 146.5211 | 94.17 | 130.9629 | 124.294 | 141.9203 | 124.9915
261.5861 | 164.5861 | 474.7805 | 147.4087 | 94.9031 | 131.6184 | 124.9532 | 142.8361 | 125.6875
262.5876 | 165.5876 | 474.8708 | 148.3052 | 95.6365 | 132.2806 | 125.6218 | 143.7429 | 126.3789
263.589 | 166.589 | 474.9385 | 149.1787 | 96.4015 | 132.9456 | 126.2932 | 144.6563 | 127.065
264.5905 | 167.5905 | 474.96 | 150.0724 | 97.1597 | 133.6317 | 126.941 | 145.5426 | 127.741
265.5919 | 168.5919 | 474.94 | 150.9327 | 97.926 | 134.3023 | 127.6457 | 146.4519 | 128.4142
266.5833 | 169.5833 | 474.8896 | 151.8208 | 98.7111 | 135.0108 | 128.2921 | 147.3183 | 129.0872
267.5848 | 170.5848 | 474.7056 | 152.6779 | 99.4793 | 135.7041 | 128.9687 | 148.2005 | 129.745
268.5862 | 171.5862 | 474.6472 | 153.5489 | 100.258 | 136.4247 | 129.6429 | 149.0711 | 130.4033
269.5876 | 172.5876 | 474.7884 | 154.4058 | 101.0116 | 137.1438 | 130.3286 | 149.9446 | 131.0535
270.5891 | 173.5891 | 474.8485 | 155.2458 | 101.7666 | 137.8536 | 131.0334 | 150.8152 | 131.6973
271.5805 | 174.5805 | 474.8439 | 156.1147 | 102.5147 | 138.596 | 131.6927 | 151.6735 | 132.3431
272.582 | 175.582 | 474.9965 | 156.9533 | 103.2491 | 139.3297 | 132.4168 | 152.5421 | 132.9815
273.5834 | 176.5834 | 474.9755 | 157.8094 | 103.9664 | 140.0727 | 133.106 | 153.396 | 133.613
274.5848 | 177.5848 | 475.0287 | 158.6225 | 104.6772 | 140.8019 | 133.8466 | 154.254 | 134.2437
275.5863 | 178.5863 | 475.0875 | 159.4823 | 105.3696 | 141.563 | 134.5233 | 155.0953 | 134.8756
276.5877 | 179.5877 | 475.0182 | 160.2976 | 106.079 | 142.2863 | 135.2767 | 155.946 | 135.4932
277.5892 | 180.5892 | 475.1177 | 161.1301 | 106.7652 | 143.0269 | 136.0103 | 156.7812 | 136.1099
278.5906 | 181.5906 | 475.2351 | 161.954 | 107.4434 | 143.762 | 136.7546 | 157.6167 | 136.7397
279.592 | 182.592 | 475.1981 | 162.7607 | 108.1364 | 144.5015 | 137.4894 | 158.4592 | 137.3575
280.5835 | 183.5835 | 475.2196 | 163.5805 | 108.8277 | 145.2416 | 138.214 | 159.275 | 137.9771
281.5849 | 184.5849 | 475.1815 | 164.3651 | 109.5363 | 145.9876 | 138.9764 | 160.101 | 138.5933
282.5863 | 185.5863 | 475.3003 | 165.1813 | 110.2582 | 146.7096 | 139.6857 | 160.9199 | 139.2205
283.5878 | 186.5878 | 475.3842 | 165.9481 | 110.9972 | 147.4167 | 140.4557 | 161.7401 | 139.8343
284.5892 | 187.5892 | 475.4298 | 166.7623 | 111.7311 | 148.1356 | 141.1677 | 162.5509 | 140.4466
285.5907 | 188.5907 | 475.4506 | 167.5162 | 112.4963 | 148.8543 | 141.9514 | 163.3645 | 141.0743
286.5821 | 189.5821 | 475.358 | 168.3209 | 113.2566 | 149.6026 | 142.6764 | 164.1557 | 141.703
287.5835 | 190.5835 | 475.4689 | 169.0584 | 114.0334 | 150.3418 | 143.479 | 164.9481 | 142.3233
288.585 | 191.585 | 475.4302 | 169.8595 | 114.7915 | 151.1229 | 144.2188 | 165.7377 | 142.9404
289.5864 | 192.5864 | 475.384 | 170.6257 | 115.5677 | 151.885 | 145.0242 | 166.5215 | 143.564
290.5878 | 193.5878 | 475.4467 | 171.4138 | 116.359 | 152.6594 | 145.799 | 167.2987 | 144.1939
291.5893 | 194.5893 | 475.678 | 172.2129 | 117.1781 | 153.4427 | 146.5924 | 168.0699 | 144.8202
292.5807 | 195.5807 | 475.8077 | 172.9834 | 118.0316 | 154.2191 | 147.3889 | 168.8546 | 145.4544
293.5822 | 196.5822 | 475.9572 | 173.819 | 118.9029 | 155.0251 | 148.0968 | 169.6092 | 146.0928
294.5836 | 197.5836 | 476.0387 | 174.5913 | 119.8112 | 155.8216 | 148.9101 | 170.3823 | 146.731
295.585 | 198.585 | 476.0302 | 175.4286 | 120.7065 | 156.6452 | 149.5996 | 171.1278 | 147.3686
296.5865 | 199.5865 | 476.1564 | 176.2188 | 121.5878 | 157.4583 | 150.3525 | 171.8884 | 148.0051
297.5879 | 200.5879 | 476.0423 | 177.0675 | 122.4422 | 158.3038 | 150.9939 | 172.6108 | 148.6483
298.5894 | 201.5894 | 475.9426 | 177.8736 | 123.2618 | 159.1289 | 151.709 | 173.362 | 149.2964
299.5908 | 202.5908 | 475.9994 | 178.7191 | 124.0645 | 159.9771 | 152.3395 | 174.0881 | 149.934
300.5822 | 203.5822 | 476.028 | 179.5588 | 124.8407 | 160.836 | 153.0082 | 174.8177 | 150.5791
301.5837 | 204.5837 | 476.1231 | 180.4169 | 125.5902 | 161.6975 | 153.6755 | 175.5422 | 151.2295
302.5851 | 205.5851 | 476.0425 | 181.2677 | 126.3361 | 162.5558 | 154.3536 | 176.2593 | 151.8693
303.5865 | 206.5865 | 475.9007 | 182.1089 | 127.064 | 163.4109 | 155.0639 | 176.9808 | 152.5183
304.588 | 207.588 | 475.8274 | 182.9656 | 127.7996 | 164.2909 | 155.7488 | 177.6899 | 153.1668
305.5894 | 208.5894 | 475.7637 | 183.8125 | 128.5324 | 165.1662 | 156.4893 | 178.394 | 153.8045
306.5909 | 209.5909 | 475.6193 | 184.6706 | 129.2504 | 166.0365 | 157.194 | 179.0887 | 154.4362
307.5823 | 210.5823 | 475.7094 | 185.5169 | 129.9705 | 166.9121 | 157.9354 | 179.7826 | 155.0829
308.5837 | 211.5837 | 475.727 | 186.3949 | 130.6844 | 167.7839 | 158.6722 | 180.4756 | 155.7298
309.5852 | 212.5852 | 475.6027 | 187.2474 | 131.4043 | 168.6474 | 159.4419 | 181.1648 | 156.3658
310.5866 | 213.5866 | 475.4729 | 188.1216 | 132.1367 | 169.5202 | 160.1926 | 181.838 | 157.0061
311.588 | 214.588 | 475.497 | 188.976 | 132.8622 | 170.3779 | 161.0093 | 182.5333 | 157.6427
312.5895 | 215.5895 | 475.4577 | 189.8785 | 133.5853 | 171.2498 | 161.7494 | 183.2046 | 158.2913
313.5809 | 216.5809 | 475.5508 | 190.7294 | 134.3356 | 172.103 | 162.5235 | 183.8804 | 158.9316
314.5823 | 217.5823 | 475.6638 | 191.6062 | 135.0825 | 172.9634 | 163.2834 | 184.5574 | 159.5733
315.5838 | 218.5838 | 475.7178 | 192.4729 | 135.8494 | 173.8135 | 164.0452 | 185.2255 | 160.2219
316.5852 | 219.5852 | 475.6222 | 193.322 | 136.6186 | 174.654 | 164.8357 | 185.9023 | 160.8678
317.5867 | 220.5867 | 475.6078 | 194.1961 | 137.3997 | 175.4931 | 165.5849 | 186.5568 | 161.5147
318.5881 | 221.5881 | 475.5928 | 195.0079 | 138.2106 | 176.3191 | 166.4004 | 187.2372 | 162.1588
319.5895 | 222.5895 | 475.5343 | 195.8678 | 139.0142 | 177.1633 | 167.1451 | 187.8928 | 162.799
320.581 | 223.581 | 475.6208 | 196.721 | 139.8378 | 177.9834 | 167.9344 | 188.5539 | 163.445
321.5824 | 224.5824 | 475.8095 | 197.5646 | 140.6754 | 178.8139 | 168.7108 | 189.2238 | 164.0919
322.5839 | 225.5839 | 476.0227 | 198.4321 | 141.5212 | 179.6383 | 169.4599 | 189.8807 | 164.7408
323.5853 | 226.5853 | 476.0111 | 199.2563 | 142.4078 | 180.4771 | 170.1272 | 190.5549 | 165.3925
324.5867 | 227.5867 | 475.975 | 200.1062 | 143.3015 | 181.3002 | 170.771 | 191.2155 | 166.048
325.5882 | 228.5882 | 475.9021 | 200.9231 | 144.2192 | 182.1187 | 171.4722 | 191.8922 | 166.6971
326.5896 | 229.5896 | 475.7833 | 201.7575 | 145.1374 | 182.9515 | 172.165 | 192.5691 | 167.3511
327.5911 | 230.5911 | 475.7817 | 202.557 | 146.0763 | 183.7688 | 172.9146 | 193.2391 | 168.0136
328.5925 | 231.5925 | 475.8655 | 203.3853 | 147.0136 | 184.5975 | 173.6345 | 193.9108 | 168.6681
329.5839 | 232.5839 | 476.0164 | 204.1789 | 147.9613 | 185.4244 | 174.4135 | 194.596 | 169.3307
330.5854 | 233.5854 | 475.9354 | 204.9954 | 148.8946 | 186.2539 | 175.1561 | 195.2658 | 169.9959
331.5868 | 234.5868 | 475.9081 | 205.7827 | 149.8261 | 187.0961 | 175.8935 | 195.9504 | 170.6654
332.5882 | 235.5882 | 475.9506 | 206.5925 | 150.7597 | 187.9755 | 176.6603 | 196.6172 | 171.3358
333.5897 | 236.5897 | 475.9964 | 207.3721 | 151.6866 | 188.8409 | 177.4433 | 197.2785 | 171.9965
334.5811 | 237.5811 | 475.8574 | 208.148 | 152.6072 | 189.6636 | 178.2423 | 197.9435 | 172.6658
335.5825 | 238.5825 | 475.7061 | 208.9469 | 153.5195 | 190.5145 | 179.0255 | 198.5956 | 173.3355
336.584 | 239.584 | 475.7081 | 209.7108 | 154.43 | 191.3554 | 179.8596 | 199.2525 | 173.9991
337.5854 | 240.5854 | 475.6464 | 210.4886 | 155.329 | 192.204 | 180.6712 | 199.9025 | 174.6695
338.5869 | 241.5869 | 475.5393 | 211.2318 | 156.2322 | 193.0308 | 181.5521 | 200.5535 | 175.3409
339.5883 | 242.5883 | 475.3195 | 212.0109 | 157.1266 | 193.8849 | 182.4018 | 201.1899 | 175.9979
340.5897 | 243.5897 | 475.2869 | 212.7508 | 158.02 | 194.7473 | 183.2817 | 201.8289 | 176.6644
341.5812 | 244.5812 | 475.1172 | 213.5018 | 158.8891 | 195.5927 | 184.1231 | 202.4506 | 177.3376
342.5826 | 245.5826 | 475.0014 | 214.2109 | 159.7655 | 196.4169 | 185.0113 | 203.0828 | 178.0019
343.584 | 246.584 | 475.0396 | 214.9228 | 160.6148 | 197.2318 | 185.8802 | 203.7107 | 178.6603
344.5855 | 247.5855 | 475.0168 | 215.5516 | 161.4643 | 198.0327 | 186.7678 | 204.3408 | 179.3178
345.5869 | 248.5869 | 475.0336 | 216.165 | 162.3126 | 198.8306 | 187.7834 | 204.9748 | 179.9849
346.5884 | 249.5884 | 474.9781 | 216.8161 | 163.1374 | 199.6566 | 189.099 | 205.5936 | 180.6478
347.5898 | 250.5898 | 474.9545 | 217.4456 | 163.9634 | 200.4491 | 190.2863 | 206.2234 | 181.3108
348.5912 | 251.5912 | 475.0603 | 217.903 | 164.8051 | 201.2108 | 191.3527 | 206.8512 | 181.9692
349.5827 | 252.5827 | 475.0071 | 218.2766 | 165.6695 | 201.9799 | 192.3732 | 207.4762 | 182.625
350.5841 | 253.5841 | 475.0495 | 218.6487 | 166.5614 | 202.7307 | 193.3185 | 208.0968 | 183.2817
351.5856 | 254.5856 | 475.0245 | 218.9491 | 167.4307 | 203.4774 | 194.2654 | 208.7256 | 183.9361
352.587 | 255.587 | 475.0301 | 219.2882 | 168.2882 | 204.2116 | 195.1907 | 209.346 | 184.5879
353.5884 | 256.5884 | 475.15 | 219.7081 | 169.1403 | 204.9268 | 196.0997 | 209.9832 | 185.2475
354.5899 | 257.5899 | 475.3404 | 220.1764 | 169.9699 | 205.633 | 197.0156 | 210.6001 | 185.8983
355.5813 | 258.5813 | 475.3215 | 220.7091 | 170.7875 | 206.3961 | 197.8669 | 211.2098 | 186.552
356.5827 | 259.5827 | 475.3313 | 221.2472 | 171.6177 | 207.0518 | 198.762 | 211.8348 | 187.2071
357.5842 | 260.5842 | 475.4028 | 221.7464 | 172.423 | 207.6848 | 199.5945 | 212.4399 | 187.8576
358.5856 | 261.5856 | 475.7138 | 222.1645 | 173.2165 | 208.3504 | 200.4688 | 213.0608 | 188.5075
359.5871 | 262.5871 | 476.0127 | 222.5749 | 174.0077 | 209.0242 | 201.2624 | 213.6663 | 189.151
360.5885 | 263.5885 | 476.1483 | 222.8799 | 174.7854 | 209.7361 | 202.1078 | 214.2948 | 189.8088
361.5899 | 264.5899 | 476.13 | 223.2019 | 175.5637 | 210.4322 | 202.8505 | 214.8948 | 190.4671
362.5914 | 265.5914 | 476.1384 | 223.4601 | 176.341 | 211.0668 | 203.6656 | 215.5231 | 191.1117
363.5828 | 266.5828 | 476.1023 | 223.7764 | 177.0892 | 211.7013 | 204.4098 | 216.1281 | 191.7581
364.5842 | 267.5842 | 475.9223 | 224.1514 | 177.8578 | 212.3263 | 205.2001 | 216.7556 | 192.4071
365.5857 | 268.5857 | 475.6353 | 224.5389 | 178.6182 | 212.9696 | 205.9064 | 217.3597 | 193.0391
366.5871 | 269.5871 | 475.4538 | 224.9141 | 179.367 | 213.6024 | 206.6559 | 217.9738 | 193.6782
367.5986 | 270.5986 | 475.1282 | 225.3047 | 180.119 | 214.2505 | 207.419 | 218.5908 | 194.324
368.59 | 271.59 | 475.047 | 225.6757 | 180.8518 | 214.9223 | 208.0991 | 219.1737 | 194.951
369.5914 | 272.5914 | 474.9932 | 226.0026 | 181.5838 | 215.5844 | 208.8576 | 219.7947 | 195.581
370.5829 | 273.5829 | 474.9475 | 226.4176 | 182.3037 | 216.3041 | 209.5079 | 220.3734 | 196.2133
371.5843 | 274.5843 | 474.9455 | 226.806 | 183.0398 | 217.041 | 210.2648 | 220.9809 | 196.8418
372.5858 | 275.5858 | 474.8042 | 227.2925 | 183.7523 | 217.8055 | 210.8999 | 221.5593 | 197.469
373.5872 | 276.5872 | 474.4632 | 227.9137 | 184.4816 | 218.554 | 211.6282 | 222.1559 | 198.098
374.5886 | 277.5886 | 474.3567 | 228.6461 | 185.1765 | 219.3467 | 212.2693 | 222.7319 | 198.7232
375.5901 | 278.5901 | 474.0914 | 229.448 | 185.8901 | 220.1735 | 212.9185 | 223.3215 | 199.3425
376.5815 | 279.5815 | 473.883 | 230.2942 | 186.5797 | 221.0409 | 213.5435 | 223.9031 | 199.9712
377.5829 | 280.5829 | 473.6045 | 231.2047 | 187.2622 | 221.9846 | 214.1403 | 224.4838 | 200.5996
378.5844 | 281.5844 | 473.386 | 232.1865 | 187.9461 | 222.9946 | 214.751 | 225.0742 | 201.2232
379.5858 | 282.5858 | 473.3499 | 233.1973 | 188.6225 | 224.0978 | 215.2922 | 225.6332 | 201.845
380.5873 | 283.5873 | 473.3145 | 234.0527 | 189.3145 | 225.1934 | 215.9086 | 226.2145 | 202.4605
381.5887 | 284.5887 | 473.3684 | 235.0752 | 190.0113 | 226.3109 | 216.4151 | 226.7842 | 203.0735
382.5901 | 285.5901 | 473.3514 | 235.8566 | 190.7008 | 227.4327 | 217.004 | 227.37 | 203.6809
383.5816 | 286.5816 | 473.2094 | 236.7022 | 191.3867 | 228.683 | 217.5189 | 227.961 | 204.2976
384.583 | 287.583 | 473.3049 | 237.3495 | 192.0724 | 230.058 | 218.0298 | 228.561 | 204.911
385.5844 | 288.5844 | 473.2809 | 238.1835 | 192.7481 | 231.4651 | 218.455 | 229.169 | 205.5251
386.5859 | 289.5859 | 473.4218 | 238.9475 | 193.4202 | 233.0254 | 218.8322 | 229.7662 | 206.136
387.5873 | 290.5873 | 473.5908 | 239.7108 | 194.0946 | 234.716 | 219.2093 | 230.3576 | 206.7429
388.5888 | 291.5888 | 473.8919 | 241.8821 | 194.7574 | 236.4604 | 219.4367 | 230.93 | 207.3468
389.5902 | 292.5902 | 473.9764 | 244.946 | 195.4361 | 238.3819 | 219.6358 | 231.5197 | 207.9526
390.5916 | 293.5916 | 473.9842 | 247.1373 | 196.1117 | 240.6835 | 219.7671 | 232.0872 | 208.5588
391.5831 | 294.5831 | 473.957 | 248.0672 | 196.7864 | 243.1968 | 219.8641 | 232.665 | 209.16
392.5845 | 295.5845 | 473.9195 | 248 | 197.453 | 245.6556 | 219.9049 | 233.2314 | 209.7695
393.5859 | 296.5859 | 473.7893 | 247.1272 | 198.118 | 247.8736 | 220.0078 | 233.8163 | 210.376
394.5874 | 297.5874 | 473.663 | 246.7629 | 198.782 | 249.5645 | 220.1365 | 234.3725 | 210.9713
395.5888 | 298.5888 | 473.5431 | 246.8062 | 199.4627 | 251.2353 | 220.3414 | 234.9366 | 211.5752
396.5903 | 299.5903 | 473.5476 | 247.2137 | 200.129 | 252.8711 | 220.5694 | 235.4926 | 212.1822
397.5817 | 300.5817 | 473.7034 | 247.8222 | 200.8031 | 254.6629 | 220.8203 | 236.0468 | 212.7779
398.5831 | 301.5831 | 473.947 | 248.508 | 201.481 | 256.6092 | 221.1458 | 236.5967 | 213.3819
399.5846 | 302.5846 | 474.1368 | 248.9616 | 202.1334 | 258.3524 | 221.4935 | 237.1401 | 213.9806
400.586 | 303.586 | 474.3346 | 249.5033 | 202.7932 | 260.0314 | 221.9529 | 237.6923 | 214.5748
401.5875 | 304.5875 | 474.3806 | 250.0557 | 203.444 | 261.4393 | 222.3557 | 238.2246 | 215.1685
402.5889 | 305.5889 | 474.4839 | 250.5613 | 204.0975 | 262.9137 | 222.8235 | 238.7829 | 215.7714
403.5803 | 306.5803 | 474.4289 | 251.1834 | 204.7366 | 264.1637 | 223.2162 | 239.31 | 216.3667
404.5818 | 307.5818 | 474.137 | 251.8415 | 205.3761 | 265.3635 | 223.6772 | 239.8563 | 216.9629
405.5832 | 308.5832 | 474.0458 | 252.45 | 205.9924 | 266.5956 | 224.1049 | 240.3857 | 217.5612
406.5846 | 309.5846 | 474.1532 | 253.4232 | 206.6205 | 267.8038 | 224.5584 | 240.9177 | 218.1456
407.5861 | 310.5861 | 474.287 | 254.2965 | 207.253 | 269.0012 | 224.9827 | 241.455 | 218.7444
408.5875 | 311.5875 | 474.3541 | 254.9884 | 207.8532 | 270.3169 | 225.3455 | 241.9732 | 219.3327
409.589 | 312.589 | 474.3414 | 255.4504 | 208.4843 | 271.3447 | 225.7555 | 242.5055 | 219.9151
410.5904 | 313.5904 | 474.38 | 255.9922 | 209.0942 | 272.3799 | 226.0521 | 243.0139 | 220.4977
411.5918 | 314.5918 | 474.388 | 256.2298 | 209.6979 | 273.5914 | 226.4435 | 243.5556 | 221.0865
412.5833 | 315.5833 | 474.3957 | 256.6087 | 210.3144 | 274.6207 | 226.7577 | 244.0803 | 221.661
413.5847 | 316.5847 | 474.5192 | 256.8683 | 210.9193 | 275.6448 | 227.113 | 244.6156 | 222.239
414.5861 | 317.5861 | 474.6314 | 257.0023 | 211.5095 | 276.8683 | 227.4594 | 245.1366 | 222.8012
415.5876 | 318.5876 | 474.6357 | 257.0555 | 212.093 | 277.9271 | 227.7977 | 245.6573 | 223.3781
416.589 | 319.589 | 474.605 | 257.1287 | 212.7098 | 278.8697 | 228.2265 | 246.1906 | 223.9572
417.5905 | 320.5905 | 474.4949 | 257.1991 | 213.2843 | 279.8184 | 228.5093 | 246.6904 | 224.5402
418.5819 | 321.5819 | 474.3586 | 257.0176 | 213.8675 | 280.6953 | 228.9107 | 247.2775 | 225.1123
419.5833 | 322.5833 | 474.162 | 256.8777 | 214.4476 | 281.6033 | 229.2167 | 247.9842 | 225.6862
420.5848 | 323.5848 | 473.9906 | 256.9653 | 215.0233 | 282.4126 | 229.5688 | 248.6565 | 226.2661
421.5862 | 324.5862 | 473.8068 | 257.1615 | 215.5983 | 283.1861 | 229.9097 | 249.2756 | 226.8397
422.5877 | 325.5877 | 473.6499 | 257.4097 | 216.1809 | 283.9706 | 230.2281 | 249.9071 | 227.4199
423.5891 | 326.5891 | 473.6219 | 257.6779 | 216.747 | 284.8098 | 230.5917 | 250.5244 | 228.0019
424.5905 | 327.5905 | 473.5985 | 257.9995 | 217.3102 | 285.6762 | 230.9137 | 251.1479 | 228.5833
425.582 | 328.582 | 473.3343 | 258.2068 | 217.8829 | 286.438 | 231.2961 | 251.7522 | 229.1577
426.5834 | 329.5834 | 473.2074 | 258.4996 | 218.4436 | 287.1812 | 231.6338 | 252.3312 | 229.741
427.5848 | 330.5848 | 473.4738 | 258.6103 | 219.0153 | 287.8798 | 232.0215 | 252.9122 | 230.3302
428.5863 | 331.5863 | 473.725 | 258.9142 | 219.5755 | 288.5854 | 232.3924 | 253.4701 | 230.9016
429.5877 | 332.5877 | 473.7225 | 259.3201 | 220.1593 | 289.2235 | 232.7797 | 254.0049 | 231.4646
430.5892 | 333.5892 | 473.9013 | 259.9172 | 220.7271 | 289.8631 | 233.1629 | 254.5406 | 232.0174
431.5806 | 334.5806 | 474.1885 | 260.5041 | 221.2791 | 290.4068 | 233.509 | 255.0313 | 232.5721
432.592 | 335.592 | 474.1389 | 260.9872 | 221.8519 | 290.956 | 233.9275 | 255.544 | 233.1283
433.5835 | 336.5835 | 474.2034 | 261.8051 | 222.4097 | 291.449 | 234.2979 | 256.046 | 233.6866
434.5849 | 337.5849 | 474.2841 | 262.6474 | 222.9571 | 291.9386 | 234.7195 | 256.5506 | 234.2325
435.5863 | 338.5863 | 474.2915 | 263.6304 | 223.5053 | 292.3884 | 235.038 | 256.9723 | 234.7822
436.5878 | 339.5878 | 474.1556 | 264.4042 | 224.0529 | 292.6938 | 235.3578 | 257.4021 | 235.3121
437.5892 | 340.5892 | 474.0485 | 265.1512 | 224.5989 | 292.6081 | 235.6417 | 257.8424 | 235.8523
438.5907 | 341.5907 | 474.1566 | 265.8686 | 225.1541 | 292.7658 | 235.9758 | 258.305 | 236.4032
439.5821 | 342.5821 | 474.2861 | 266.6014 | 225.6979 | 293.0242 | 236.3158 | 258.7755 | 236.951
440.5835 | 343.5835 | 474.4013 | 267.3188 | 226.2345 | 293.3789 | 236.6446 | 259.2414 | 237.5191
441.585 | 344.585 | 474.4279 | 268.1064 | 226.7725 | 293.8247 | 237.0061 | 259.6859 | 238.0755
442.5864 | 345.5864 | 474.518 | 268.8029 | 227.315 | 294.2671 | 237.3262 | 260.1285 | 238.6431
443.5878 | 346.5878 | 474.661 | 269.5192 | 227.8443 | 294.7215 | 237.7191 | 260.5749 | 239.2291
444.5893 | 347.5893 | 474.688 | 270.1551 | 228.3567 | 295.2112 | 238.0873 | 261.0108 | 239.9977
445.5807 | 348.5807 | 474.6574 | 270.829 | 228.8811 | 295.6476 | 238.4823 | 261.4645 | 240.9476
446.5822 | 349.5822 | 474.7124 | 271.5301 | 229.3874 | 296.0857 | 238.8385 | 261.8922 | 241.7904
447.5836 | 350.5836 | 474.7694 | 272.3409 | 229.8956 | 296.4364 | 239.2571 | 262.3406 | 242.5434
448.585 | 351.585 | 474.7481 | 273.0798 | 230.3984 | 296.8003 | 239.6329 | 262.7689 | 243.2793
449.5865 | 352.5865 | 474.8688 | 273.6477 | 230.9147 | 297.1129 | 240.0195 | 263.2044 | 244.0118
450.5879 | 353.5879 | 474.938 | 274.0912 | 231.4293 | 297.4116 | 240.4484 | 263.6171 | 244.7083
451.5894 | 354.5894 | 475.0325 | 274.5788 | 231.935 | 297.7129 | 240.8547 | 264.0334 | 245.3847
452.5808 | 355.5808 | 475.0532 | 275.1542 | 232.4473 | 298.0243 | 241.337 | 264.4694 | 246.0599
453.5822 | 356.5822 | 475.0599 | 275.4215 | 232.947 | 298.3942 | 241.7409 | 264.8787 | 246.713
454.5837 | 357.5837 | 475.0881 | 274.9915 | 233.4616 | 298.7487 | 242.1984 | 265.3017 | 247.3213
455.5851 | 358.5851 | 475.0955 | 275.1925 | 233.9642 | 299.1202 | 242.6187 | 265.7148 | 247.9135
456.5865 | 359.5865 | 475.036 | 275.6631 | 234.4743 | 299.4818 | 243.0871 | 266.1453 | 248.5194
457.588 | 360.588 | 475.0868 | 276.4093 | 234.9805 | 299.8635 | 243.5707 | 266.5655 | 249.116
458.5894 | 361.5894 | 475.0349 | 277.3739 | 235.5049 | 300.2318 | 244.0971 | 266.9914 | 249.7215
459.5909 | 362.5909 | 474.9727 | 278.6634 | 236.0329 | 300.6107 | 244.636 | 267.4323 | 250.2821
460.5823 | 363.5823 | 475.0836 | 279.6953 | 236.5662 | 300.9855 | 245.1652 | 267.8596 | 250.874
461.5837 | 364.5837 | 474.9272 | 280.5268 | 237.0949 | 301.3569 | 245.7907 | 268.258 | 251.4229
462.5852 | 365.5852 | 474.7243 | 281.3492 | 237.6565 | 301.732 | 246.3694 | 268.6178 | 251.9568
463.5866 | 366.5866 | 474.6532 | 281.9707 | 238.2332 | 302.079 | 247.0679 | 269.0143 | 252.4893
464.588 | 367.588 | 474.5129 | 282.5805 | 238.8212 | 302.4529 | 247.7228 | 269.3912 | 252.9652
465.5895 | 368.5895 | 474.6246 | 283.2545 | 239.4329 | 302.8287 | 248.4905 | 269.7928 | 253.4726
466.5809 | 369.5809 | 474.6755 | 283.8882 | 240.0099 | 303.2385 | 249.2326 | 270.1934 | 253.9796
467.5824 | 370.5824 | 474.8099 | 284.4379 | 240.5885 | 303.6846 | 250.0429 | 270.5889 | 254.475
468.5838 | 371.5838 | 474.8153 | 284.9624 | 241.1908 | 304.1157 | 251.0047 | 270.9999 | 254.9724
469.5852 | 372.5852 | 474.8193 | 285.5572 | 241.7736 | 304.5983 | 252.3055 | 271.4244 | 255.4494
470.5867 | 373.5867 | 474.7421 | 286.0592 | 242.3533 | 305.0857 | 253.6689 | 271.9058 | 255.9518
471.5881 | 374.5881 | 474.764 | 286.5842 | 242.9195 | 305.5981 | 254.9742 | 272.3526 | 256.4697
472.5896 | 375.5896 | 474.7501 | 287.0316 | 243.4799 | 306.1296 | 256.3282 | 272.7953 | 256.9559
473.581 | 376.581 | 474.6799 | 287.4927 | 244.0541 | 306.7029 | 257.4619 | 273.2234 | 257.418
474.5924 | 377.5924 | 474.6833 | 287.897 | 244.6128 | 307.2941 | 258.4994 | 273.6653 | 257.8631
475.5839 | 378.5839 | 474.7627 | 288.2695 | 245.1813 | 307.8967 | 259.5173 | 274.1055 | 258.3275
476.5853 | 379.5853 | 474.8664 | 288.559 | 245.7466 | 308.5011 | 260.564 | 274.6044 | 258.7858
477.5867 | 380.5867 | 475.0157 | 288.8302 | 246.3059 | 309.131 | 261.6101 | 275.1335 | 259.2523
478.5882 | 381.5882 | 475.1909 | 289.0966 | 246.8804 | 309.749 | 262.6188 | 275.6032 | 259.7481
479.5896 | 382.5896 | 475.249 | 289.324 | 247.4404 | 310.3525 | 263.5555 | 276.0615 | 260.2552
480.5911 | 383.5911 | 475.1278 | 289.5491 | 247.9729 | 310.9719 | 264.3142 | 276.5988 | 260.7267
481.5825 | 384.5825 | 475.069 | 289.7563 | 248.5104 | 311.5794 | 265.097 | 284.524 | 261.1597
482.5839 | 385.5839 | 475.0473 | 289.9862 | 249.057 | 312.1964 | 265.7364 | 295.1007 | 261.5787
483.5854 | 386.5854 | 475.078 | 290.1681 | 249.587 | 312.7711 | 266.3959 | 303.4747 | 262.03
484.5868 | 387.5868 | 475.2264 | 290.3277 | 250.0999 | 313.3874 | 267.011 | 310.9311 | 262.5158
485.5882 | 388.5882 | 475.2365 | 290.5168 | 250.6204 | 314.0047 | 267.6621 | 317.7024 | 263.0139
486.5897 | 389.5897 | 475.2223 | 290.82 | 251.1254 | 314.6443 | 268.2773 | 323.856 | 263.5104
487.5811 | 390.5811 | 475.2362 | 291.0962 | 251.6171 | 315.2654 | 268.8756 | 329.5083 | 263.985
488.5825 | 391.5825 | 475.159 | 291.3686 | 252.0993 | 315.9051 | 269.4941 | 334.5895 | 264.4461
489.584 | 392.584 | 475.0732 | 291.6373 | 252.5887 | 316.5431 | 269.9795 | 339.2452 | 264.9246
490.5854 | 393.5854 | 475.0474 | 291.9125 | 253.0776 | 317.1641 | 270.5518 | 343.5867 | 265.3959
491.5869 | 394.5869 | 475.002 | 292.2179 | 253.5718 | 317.787 | 271.181 | 347.4627 | 265.8777
492.5883 | 395.5883 | 475.1185 | 292.4836 | 254.0461 | 318.3984 | 271.7644 | 351.1161 | 266.307
493.5897 | 396.5897 | 475.1595 | 292.7362 | 254.5233 | 319.027 | 272.2314 | 354.3836 | 266.7229
494.5812 | 397.5812 | 475.114 | 292.9485 | 254.9953 | 319.6538 | 272.7396 | 357.3841 | 267.1337
495.5926 | 398.5926 | 474.984 | 293.1636 | 255.4749 | 320.2704 | 273.2622 | 360.1594 | 267.5462
496.5841 | 399.5841 | 474.8623 | 293.412 | 255.94 | 320.9024 | 273.7237 | 362.5655 | 267.9617
497.5855 | 400.5855 | 474.6701 | 293.643 | 256.3826 | 321.5132 | 274.1958 | 364.8419 | 268.3455
498.5869 | 401.5869 | 474.4525 | 293.9369 | 256.8348 | 322.1372 | 274.7065 | 366.9551 | 268.734
499.5884 | 402.5884 | 474.2867 | 294.1935 | 257.2888 | 322.7605 | 275.2286 | 368.9449 | 269.1222
500.5898 | 403.5898 | 474.2281 | 294.4712 | 257.7185 | 323.3893 | 275.698 | 370.7003 | 269.5365
501.5913 | 404.5913 | 474.3864 | 294.7172 | 258.17 | 324.0269 | 276.0893 | 372.4108 | 269.9575
502.5827 | 405.5827 | 474.4347 | 294.9514 | 258.6148 | 324.6546 | 276.3463 | 373.8423 | 270.3623
503.5841 | 406.5841 | 474.3104 | 295.2871 | 259.0603 | 325.2679 | 276.6873 | 375.2128 | 270.7693
504.5856 | 407.5856 | 474.174 | 295.6004 | 259.4982 | 325.8677 | 277.0488 | 376.402 | 271.1945
505.587 | 408.587 | 474.19 | 295.8714 | 259.9431 | 326.467 | 277.4271 | 377.4815 | 271.6318
506.5884 | 409.5884 | 474.3681 | 296.1079 | 260.3939 | 327.0585 | 277.8683 | 378.5506 | 272.0805
507.5899 | 410.5899 | 474.3169 | 296.531 | 260.8319 | 327.6531 | 278.242 | 379.3823 | 272.5686
508.5813 | 411.5813 | 474.2949 | 296.8923 | 261.28 | 328.2331 | 278.6488 | 380.2118 | 272.987
509.5827 | 412.5827 | 474.1901 | 297.2063 | 261.7229 | 328.7924 | 279.0455 | 380.8786 | 273.38
510.5842 | 413.5842 | 474.1271 | 297.5256 | 262.161 | 329.3188 | 279.4728 | 381.5125 | 273.7506
511.5856 | 414.5856 | 474.1695 | 297.9655 | 262.5893 | 329.8507 | 279.9007 | 382.1792 | 274.1426
512.5871 | 415.5871 | 474.0667 | 298.3464 | 263.0206 | 330.3721 | 280.3098 | 382.7687 | 274.5177
513.5885 | 416.5885 | 474.0606 | 298.6166 | 263.453 | 330.8916 | 280.7724 | 383.405 | 274.7989
514.5899 | 417.5899 | 474.0835 | 299.0259 | 263.8606 | 331.3967 | 281.1719 | 383.89 | 275.1405
515.5814 | 418.5814 | 474.1776 | 299.3102 | 264.27 | 331.8858 | 281.6177 | 384.3283 | 275.5373
516.5828 | 419.5828 | 474.2189 | 299.6943 | 264.6791 | 332.3707 | 282.0078 | 384.7504 | 275.9226
517.5842 | 420.5842 | 474.3128 | 300.0444 | 265.092 | 332.8276 | 282.4543 | 385.1446 | 276.4829
518.5857 | 421.5857 | 474.4449 | 300.4436 | 265.496 | 333.308 | 282.8832 | 385.5076 | 276.9902
519.5871 | 422.5871 | 474.539 | 300.7408 | 265.928 | 333.7604 | 283.3433 | 385.7781 | 277.4938
520.5886 | 423.5886 | 474.6482 | 301.0367 | 266.355 | 334.213 | 283.7692 | 386.0548 | 278.0348
521.59 | 424.59 | 474.813 | 301.3214 | 266.7813 | 334.6645 | 284.2291 | 386.2859 | 278.6654
522.5914 | 425.5914 | 474.7837 | 301.5455 | 267.21 | 335.1042 | 284.6922 | 386.5965 | 279.1705
523.5829 | 426.5829 | 474.6939 | 301.8284 | 267.6321 | 335.5521 | 285.1239 | 386.8074 | 279.4454
524.5843 | 427.5843 | 474.8446 | 302.0787 | 268.0654 | 335.9655 | 285.6248 | 387.0832 | 279.7586
525.5858 | 428.5858 | 475.1053 | 302.3912 | 268.4674 | 336.3782 | 286.0531 | 387.2603 | 280.139
526.5872 | 429.5872 | 475.1169 | 302.6401 | 268.9036 | 336.7649 | 286.5564 | 387.5153 | 280.558
527.5886 | 430.5886 | 475.0638 | 302.8963 | 269.3329 | 337.1532 | 287.0032 | 387.7079 | 280.9954
528.5901 | 431.5901 | 474.962 | 303.1154 | 269.7674 | 337.5192 | 287.5091 | 387.8493 | 281.4616
529.5815 | 432.5815 | 474.9288 | 303.339 | 270.2175 | 337.9006 | 287.9448 | 387.9068 | 281.9714
530.5829 | 433.5829 | 474.7631 | 303.5624 | 270.6494 | 338.2458 | 288.4239 | 388.0859 | 282.4967
531.5844 | 434.5844 | 474.6015 | 303.8903 | 271.0731 | 338.5841 | 288.8816 | 388.1956 | 282.9564
532.5858 | 435.5858 | 474.4553 | 304.0551 | 271.5061 | 338.9165 | 289.3355 | 388.293 | 283.3956
533.5873 | 436.5873 | 474.288 | 304.1523 | 271.9482 | 339.2373 | 289.7821 | 388.4059 | 283.8448
534.5887 | 437.5887 | 474.2491 | 304.2392 | 272.3796 | 339.5498 | 290.2319 | 388.5303 | 284.2868
535.5901 | 438.5901 | 474.3501 | 304.4368 | 272.7947 | 339.8457 | 290.744 | 388.6478 | 284.7575
536.5816 | 439.5816 | 474.5364 | 304.6012 | 273.1954 | 340.1888 | 291.1755 | 388.6147 | 285.2788
537.583 | 440.583 | 474.6701 | 304.8068 | 273.5972 | 340.506 | 291.7289 | 388.6509 | 285.7667
538.5844 | 441.5844 | 474.8127 | 304.9711 | 273.9966 | 340.823 | 292.2183 | 388.5614 | 286.2402
539.5859 | 442.5859 | 474.8716 | 305.072 | 274.3991 | 341.0885 | 292.8073 | 388.6583 | 286.707
540.5873 | 443.5873 | 474.8605 | 305.3441 | 274.813 | 341.3711 | 293.2298 | 388.5664 | 287.1568
541.5888 | 444.5888 | 474.7745 | 305.4584 | 275.2463 | 341.6289 | 293.7767 | 388.5962 | 287.6204
542.5902 | 445.5902 | 474.6927 | 305.6843 | 275.664 | 341.8723 | 294.2535 | 388.5214 | 288.0672
543.5916 | 446.5916 | 474.4747 | 305.8685 | 276.096 | 342.0823 | 295.0696 | 388.5405 | 288.5541
544.5831 | 447.5831 | 474.5526 | 306.0928 | 276.5156 | 342.3021 | 295.5877 | 388.4911 | 288.9422
545.5845 | 448.5845 | 474.474 | 306.2573 | 276.956 | 342.474 | 296.1071 | 388.4421 | 289.3802
546.586 | 449.586 | 474.3746 | 306.498 | 277.3989 | 341.5985 | 296.6136 | 388.4978 | 289.8184
547.5874 | 450.5874 | 474.0495 | 306.7074 | 277.8331 | 339.7998 | 297.0758 | 388.4526 | 290.1783
548.719 | 451.719 | 473.9615 | 306.9507 | 278.3317 | 339.48 | 297.724 | 388.4245 | 290.5705
549.5903 | 452.5903 | 473.9531 | 307.1887 | 278.6926 | 339.5062 | 298.2038 | 388.2988 | 290.8732
550.5817 | 453.5817 | 473.886 | 307.3698 | 279.1393 | 339.6556 | 298.8077 | 388.2997 | 291.2278
551.5831 | 454.5831 | 473.7201 | 307.7643 | 279.5747 | 339.8646 | 299.3042 | 388.2732 | 291.6167
552.5846 | 455.5846 | 473.7663 | 307.9682 | 280.0099 | 340.0358 | 299.8757 | 388.3349 | 292.0308
553.586 | 456.586 | 473.8281 | 308.2633 | 280.4325 | 340.2371 | 300.3801 | 388.3797 | 292.4987
554.5875 | 457.5875 | 474.0614 | 308.4962 | 280.8836 | 340.3899 | 300.8858 | 388.4055 | 292.9705
555.5889 | 458.5889 | 474.1232 | 308.8695 | 281.3511 | 340.592 | 301.415 | 388.397 | 293.4247
556.5803 | 459.5803 | 474.0929 | 309.1896 | 281.8262 | 340.9155 | 301.8916 | 388.3802 | 293.8797
557.5818 | 460.5818 | 474.2266 | 309.4225 | 282.2781 | 341.0633 | 302.4327 | 388.4198 | 294.4158
558.5832 | 461.5832 | 474.6244 | 309.6246 | 282.7186 | 341.2003 | 303.122 | 388.3392 | 294.8916
559.5846 | 462.5846 | 474.9688 | 310.122 | 283.1578 | 341.4474 | 303.7787 | 388.468 | 295.3522
560.5861 | 463.5861 | 475.3334 | 310.398 | 283.598 | 341.6337 | 304.2718 | 388.5129 | 295.8441
561.5875 | 464.5875 | 475.6028 | 310.5509 | 284.0252 | 341.8364 | 304.8047 | 388.5917 | 296.3627
562.589 | 465.589 | 475.7235 | 310.893 | 284.4568 | 342.0606 | 305.283 | 388.6246 | 296.8888
563.5904 | 466.5904 | 475.601 | 311.1715 | 284.9033 | 342.3741 | 305.7645 | 388.6306 | 297.433
564.5818 | 467.5818 | 475.4592 | 311.52 | 285.3268 | 342.633 | 306.2111 | 388.6018 | 297.9726
565.5833 | 468.5833 | 475.471 | 311.9617 | 285.7536 | 342.7394 | 306.6833 | 388.4782 | 298.5132
566.5847 | 469.5847 | 475.3694 | 312.3931 | 286.1749 | 342.9579 | 307.1435 | 388.462 | 299.0279
567.5861 | 470.5861 | 475.3961 | 312.9308 | 286.5922 | 343.1233 | 307.5735 | 388.4111 | 299.5411
568.5876 | 471.5876 | 475.3919 | 313.1775 | 287.0255 | 343.41 | 308.0692 | 388.2475 | 300.056
569.589 | 472.589 | 475.1458 | 313.3806 | 287.4471 | 343.6542 | 308.506 | 388.2283 | 300.5748
570.5905 | 473.5905 | 475.0716 | 313.6978 | 287.8971 | 343.8874 | 308.9553 | 388.1625 | 301.0833
571.5819 | 474.5819 | 475.0453 | 313.9802 | 288.3467 | 344.1978 | 309.3764 | 388.1386 | 301.561
572.5833 | 475.5833 | 474.8017 | 314.3057 | 288.7764 | 344.4447 | 309.8059 | 388.1545 | 302.0306
573.5848 | 476.5848 | 474.7455 | 314.7708 | 289.2221 | 344.7684 | 310.2282 | 388.1806 | 302.5095
574.5862 | 477.5862 | 474.6386 | 315.1721 | 289.6499 | 344.9225 | 310.6577 | 388.2763 | 302.944
575.5877 | 478.5877 | 474.6682 | 315.7437 | 290.087 | 345.1288 | 311.0837 | 388.3676 | 303.3629
576.5891 | 479.5891 | 474.778 | 316.2629 | 290.5209 | 345.4645 | 311.4951 | 388.4207 | 303.7658
577.5805 | 480.5805 | 474.89 | 316.9015 | 290.9482 | 345.631 | 311.929 | 388.5299 | 304.1641
578.582 | 481.582 | 474.9582 | 316.9978 | 291.3633 | 345.8448 | 312.3182 | 388.5615 | 304.5617
579.5834 | 482.5834 | 474.8455 | 317.0696 | 291.8006 | 346.0322 | 312.7699 | 388.5347 | 304.9581
580.5848 | 483.5848 | 474.8397 | 317.411 | 292.2258 | 346.259 | 313.108 | 388.4152 | 305.3615
581.5863 | 484.5863 | 474.9686 | 317.8004 | 292.6681 | 346.4867 | 313.5329 | 388.5076 | 305.7843
582.5877 | 485.5877 | 474.8326 | 318.3243 | 293.0909 | 346.7873 | 313.8714 | 388.4771 | 306.2157
583.5892 | 486.5892 | 474.8663 | 318.6445 | 293.5729 | 346.975 | 314.2484 | 388.5598 | 306.6272
584.5906 | 487.5906 | 474.8213 | 319.0893 | 294.0292 | 347.174 | 314.6157 | 388.5933 | 307.0405
585.592 | 488.592 | 474.7131 | 319.4781 | 294.4544 | 347.4096 | 315.0576 | 388.6102 | 307.4658
586.5835 | 489.5835 | 474.6047 | 319.8464 | 294.8858 | 347.6148 | 315.4621 | 388.5613 | 307.9035
587.5849 | 490.5849 | 474.3019 | 320.2515 | 295.2999 | 347.7604 | 315.7956 | 388.4656 | 308.313
588.5863 | 491.5863 | 474.1152 | 320.5629 | 295.7242 | 348.0098 | 316.2618 | 388.5326 | 308.7275
589.5878 | 492.5878 | 474.0798 | 320.9963 | 296.1345 | 348.2105 | 316.6521 | 388.479 | 309.1484
590.5892 | 493.5892 | 474.3372 | 321.3746 | 296.5445 | 348.4125 | 317.0866 | 388.4518 | 309.5648
591.5907 | 494.5907 | 474.561 | 321.9111 | 296.9491 | 348.6172 | 317.4259 | 388.4239 | 309.9721
592.5821 | 495.5821 | 474.6841 | 322.3253 | 297.3924 | 348.8902 | 317.7505 | 388.4311 | 310.3799
593.5835 | 496.5835 | 474.7077 | 322.6178 | 297.8091 | 349.0623 | 318.0797 | 388.3602 | 310.7877
594.585 | 497.585 | 474.5225 | 322.89 | 298.2236 | 349.3502 | 318.4309 | 388.4053 | 311.1886
595.5864 | 498.5864 | 474.4286 | 323.0867 | 298.6371 | 349.5751 | 318.794 | 388.4222 | 311.5806
596.5879 | 499.5879 | 474.2424 | 323.5628 | 299.0327 | 349.8018 | 319.081 | 388.4403 | 311.9919
597.5893 | 500.5893 | 474.1968 | 323.9951 | 299.4593 | 350.0356 | 319.5025 | 388.4957 | 312.3974
598.5907 | 501.5907 | 474.0707 | 324.5225 | 299.8823 | 350.2752 | 319.8437 | 388.5213 | 312.7984
599.5822 | 502.5822 | 473.9885 | 324.76 | 300.3162 | 350.4266 | 320.2119 | 388.6646 | 313.1727
600.5836 | 503.5836 | 474.0323 | 325.1165 | 300.8435 | 350.6551 | 320.5255 | 388.6596 | 313.5179
601.585 | 504.585 | 474.1668 | 325.4478 | 301.2801 | 350.8887 | 320.917 | 388.7603 | 313.8482
602.5865 | 505.5865 | 474.1782 | 325.7413 | 301.6566 | 351.0777 | 321.2216 | 388.8342 | 314.1633
603.5879 | 506.5879 | 474.2323 | 326.1078 | 302.039 | 351.2033 | 321.5862 | 388.8502 | 314.4783
604.5894 | 507.5894 | 474.2914 | 326.453 | 302.4472 | 351.4652 | 321.9191 | 388.7376 | 314.7735
605.5908 | 508.5908 | 474.3592 | 326.8036 | 302.8435 | 351.68 | 322.2315 | 389.0132 | 315.0587
606.5922 | 509.5922 | 474.402 | 327.1279 | 303.2256 | 351.8667 | 322.5951 | 389.0888 | 315.3291
607.5837 | 510.5837 | 474.4258 | 327.5857 | 303.6158 | 352.0017 | 322.8709 | 389.1312 | 315.5941
608.5851 | 511.5851 | 474.5715 | 327.7611 | 304.0271 | 352.2536 | 323.2353 | 389.2092 | 315.8668
609.5865 | 512.5865 | 474.7641 | 328.1667 | 304.4111 | 352.477 | 323.5112 | 389.172 | 316.1453
610.588 | 513.588 | 475.0279 | 328.5655 | 304.8496 | 352.7068 | 323.8594 | 389.2075 | 316.4185
611.5894 | 514.5894 | 475.1242 | 328.9486 | 305.2334 | 352.9208 | 324.095 | 389.0522 | 316.6931
612.5909 | 515.5909 | 474.9972 | 329.241 | 305.6336 | 353.1457 | 324.368 | 389.1344 | 316.954
613.5823 | 516.5823 | 474.883 | 329.6797 | 306.0309 | 353.3558 | 324.6331 | 389.1077 | 317.1905
614.5837 | 517.5837 | 474.6582 | 330.0498 | 306.4029 | 353.5585 | 324.9373 | 389.1452 | 317.4158
615.5852 | 518.5852 | 474.2916 | 330.3863 | 306.8173 | 353.78 | 325.2595 | 389.2343 | 317.6312
616.5866 | 519.5866 | 474.0753 | 330.7126 | 307.2197 | 354.0302 | 325.5076 | 389.2842 | 317.8724
617.588 | 520.588 | 474.0326 | 331.0469 | 307.6132 | 354.1968 | 325.8223 | 389.3976 | 318.1123
618.5895 | 521.5895 | 473.8292 | 331.3086 | 308.0173 | 354.4414 | 326.0683 | 389.4375 | 318.3612
619.5809 | 522.5809 | 473.691 | 331.6149 | 308.4297 | 354.6578 | 326.4261 | 389.5053 | 318.5937
620.5824 | 523.5824 | 473.7783 | 332.0358 | 308.8297 | 354.8741 | 326.6463 | 389.5055 | 318.8626
621.5838 | 524.5838 | 473.8804 | 332.4382 | 309.2415 | 355.1196 | 326.9175 | 389.443 | 319.1307
622.5852 | 525.5852 | 473.9436 | 332.8177 | 309.6439 | 355.3841 | 327.2049 | 389.3293 | 319.4086
623.5867 | 526.5867 | 473.8746 | 333.2011 | 310.0509 | 355.5361 | 327.5003 | 389.3476 | 319.6776
624.5881 | 527.5881 | 473.7972 | 333.4879 | 310.4514 | 355.7971 | 327.7702 | 389.2588 | 319.9379
625.5896 | 528.5896 | 473.7131 | 333.812 | 310.8509 | 356.0357 | 327.9789 | 389.3653 | 320.2092
626.591 | 529.591 | 473.6567 | 334.226 | 311.2502 | 356.2141 | 328.1734 | 389.2381 | 320.4829
627.5924 | 530.5924 | 473.8431 | 334.5282 | 311.6783 | 356.455 | 328.4768 | 389.1404 | 320.7516
628.5839 | 531.5839 | 474.0273 | 334.9015 | 312.0827 | 356.6617 | 328.8015 | 389.1635 | 321.0244
629.5853 | 532.5853 | 474.0684 | 335.26 | 312.5987 | 356.8594 | 329.0485 | 389.0749 | 321.2908
630.5867 | 533.5867 | 473.944 | 335.5905 | 312.975 | 357.0686 | 329.3114 | 388.979 | 321.5712
631.5882 | 534.5882 | 473.8742 | 335.9886 | 313.2905 | 357.3115 | 329.48 | 388.9603 | 321.8537
632.5896 | 535.5896 | 473.8869 | 336.3997 | 313.6778 | 357.4924 | 329.727 | 388.9633 | 322.1294
633.5911 | 536.5911 | 474.05 | 336.6673 | 314.0356 | 357.7208 | 330.0024 | 388.9151 | 322.4167
634.5825 | 537.5825 | 474.1068 | 337.0325 | 314.4243 | 357.901 | 330.3149 | 388.9158 | 322.7203
635.5839 | 538.5839 | 474.1545 | 337.3971 | 314.8125 | 358.129 | 330.4377 | 388.8386 | 323.0288
636.5854 | 539.5854 | 474.2983 | 337.7259 | 315.2272 | 358.3354 | 330.6182 | 388.8532 | 323.3385
637.5868 | 540.5868 | 474.2632 | 338.0948 | 315.6127 | 358.5287 | 330.8375 | 388.8153 | 323.655
638.5882 | 541.5882 | 474.0601 | 338.4134 | 315.9929 | 358.7441 | 330.945 | 388.8283 | 323.9686
639.5897 | 542.5897 | 474.1469 | 338.7913 | 316.3792 | 358.9341 | 331.0703 | 388.7937 | 324.2585
640.5811 | 543.5811 | 474.166 | 339.1153 | 316.7494 | 359.157 | 331.4017 | 388.7836 | 324.5766
641.5826 | 544.5826 | 474.0401 | 339.4272 | 317.1404 | 359.3798 | 331.6792 | 388.7297 | 324.901
642.584 | 545.584 | 473.7616 | 339.822 | 317.5168 | 359.5775 | 332.1264 | 388.7305 | 325.1903
643.5854 | 546.5854 | 473.3457 | 340.1606 | 317.8966 | 359.8559 | 331.9895 | 388.7881 | 325.4412
644.5869 | 547.5869 | 473.0086 | 340.4363 | 318.2716 | 360.0634 | 332.3286 | 388.8509 | 325.7291
645.5883 | 548.5883 | 473.0032 | 340.7635 | 318.6506 | 360.3179 | 332.1998 | 388.8678 | 326.0345
646.5898 | 549.5898 | 473.1394 | 341.0757 | 319.0347 | 360.5695 | 332.2419 | 388.8392 | 326.3478
647.5812 | 550.5812 | 472.9839 | 341.4475 | 319.4194 | 360.8003 | 332.5255 | 388.8678 | 326.7254
648.5926 | 551.5926 | 472.7939 | 341.7464 | 319.807 | 361.0537 | 332.5429 | 388.874 | 327.1133
649.5841 | 552.5841 | 472.9164 | 342.0531 | 320.1808 | 361.3308 | 332.683 | 388.8735 | 327.493
650.5855 | 553.5855 | 473.1256 | 342.346 | 320.5562 | 361.5925 | 332.7835 | 388.9068 | 327.8619
651.5869 | 554.5869 | 473.2083 | 342.7079 | 320.9342 | 361.858 | 333.0211 | 388.8867 | 328.3394
652.5884 | 555.5884 | 473.3492 | 343.0107 | 321.3285 | 362.0849 | 333.2989 | 388.927 | 328.704
653.5898 | 556.5898 | 473.3861 | 343.3713 | 321.7003 | 362.3571 | 333.3504 | 388.8311 | 328.9305
654.5913 | 557.5913 | 473.438 | 343.74 | 322.0726 | 362.6194 | 333.6318 | 388.8031 | 329.1722
655.5827 | 558.5827 | 473.6139 | 344.2586 | 322.4452 | 362.8937 | 333.8054 | 388.7996 | 329.4545
656.5841 | 559.5841 | 473.5743 | 344.5858 | 322.8142 | 363.1383 | 333.9495 | 388.6913 | 329.7202
657.5856 | 560.5856 | 473.4625 | 344.897 | 323.1859 | 363.3626 | 334.3997 | 388.7272 | 330.0106
658.587 | 561.587 | 473.4371 | 345.2036 | 323.5615 | 363.6449 | 334.6462 | 388.7751 | 330.2793
659.5884 | 562.5884 | 473.3669 | 345.4743 | 323.9458 | 363.8935 | 335.2034 | 388.848 | 330.6877
660.5899 | 563.5899 | 473.2399 | 345.7819 | 324.3054 | 364.18 | 335.3943 | 388.8556 | 331.0773
661.5813 | 564.5813 | 473.1784 | 346.1114 | 324.6926 | 364.439 | 335.5069 | 388.9772 | 331.4055
662.5827 | 565.5827 | 473.3855 | 346.5115 | 325.0549 | 364.7082 | 335.5689 | 388.9719 | 331.8752
663.5842 | 566.5842 | 473.5243 | 346.7946 | 325.4144 | 364.9773 | 335.7205 | 388.9821 | 332.1961
664.5856 | 567.5856 | 473.6972 | 347.1084 | 325.7598 | 365.2594 | 335.8473 | 389.0325 | 332.3433
665.5871 | 568.5871 | 473.9122 | 347.4219 | 326.1354 | 365.5119 | 335.9709 | 389.0489 | 332.6202
666.5885 | 569.5885 | 474.1684 | 347.6265 | 326.4987 | 365.7866 | 336.1603 | 389.0002 | 332.8273
667.5899 | 570.5899 | 474.3635 | 347.7985 | 326.8693 | 366.0882 | 336.3007 | 388.9082 | 333.06
668.5814 | 571.5814 | 474.5802 | 348.0058 | 327.249 | 366.3768 | 336.6607 | 388.801 | 333.3034
669.5828 | 572.5828 | 474.7632 | 348.3084 | 327.62 | 366.651 | 336.8556 | 388.7599 | 333.4863
670.5843 | 573.5843 | 474.913 | 348.5476 | 327.9921 | 366.9123 | 337.0692 | 388.7636 | 333.9412
671.5857 | 574.5857 | 474.795 | 348.8775 | 328.3504 | 367.1879 | 337.4968 | 388.7715 | 334.3379
672.5871 | 575.5871 | 474.5809 | 349.2943 | 328.7151 | 367.4445 | 337.7885 | 388.8473 | 334.7251
673.5886 | 576.5886 | 474.4437 | 349.7424 | 329.0659 | 367.7229 | 338.0043 | 388.8092 | 334.9443
674.59 | 577.59 | 474.2767 | 350.1186 | 329.4222 | 368.0183 | 338.339 | 388.8587 | 334.9714
675.5814 | 578.5814 | 474.1264 | 350.4178 | 329.7872 | 368.2832 | 338.7719 | 388.8765 | 335.102
676.5829 | 579.5829 | 474.0759 | 350.7366 | 330.1563 | 368.5646 | 339.1114 | 388.929 | 335.2622
677.5843 | 580.5843 | 474.0459 | 351.1348 | 330.5153 | 368.8495 | 339.4506 | 388.9277 | 335.3513
678.5858 | 581.5858 | 474.0401 | 351.4571 | 330.8773 | 369.0988 | 339.6464 | 388.9047 | 335.3778
679.5872 | 582.5872 | 473.8531 | 351.7749 | 331.2524 | 369.3124 | 339.8771 | 388.8414 | 335.2869
680.5886 | 583.5886 | 473.9005 | 351.9259 | 331.6147 | 369.5644 | 340.0783 | 388.7764 | 335.4746
681.5901 | 584.5901 | 473.8627 | 352.1365 | 331.9912 | 369.8241 | 340.3684 | 388.7519 | 335.292
682.5815 | 585.5815 | 473.7469 | 352.3974 | 332.3507 | 370.0667 | 340.6126 | 388.7316 | 335.2576
683.5829 | 586.5829 | 473.7637 | 352.6599 | 332.71 | 370.3079 | 341.0205 | 388.7365 | 335.4734
684.5844 | 587.5844 | 473.9714 | 352.9165 | 333.0716 | 370.5585 | 341.2687 | 388.6787 | 335.6449
685.5858 | 588.5858 | 474.0598 | 353.172 | 333.4433 | 370.8265 | 341.5143 | 388.648 | 335.8628
686.5873 | 589.5873 | 474.071 | 353.4578 | 333.7943 | 371.1024 | 341.827 | 388.7254 | 335.4956
687.5887 | 590.5887 | 474.2954 | 353.7173 | 334.1459 | 371.3812 | 342.2266 | 388.7753 | 335.7603
688.5901 | 591.5901 | 474.5304 | 354.0037 | 334.5061 | 371.6271 | 342.3923 | 388.7685 | 336.1098
689.5816 | 592.5816 | 474.682 | 354.2663 | 334.8558 | 371.8596 | 342.6022 | 388.8413 | 335.0392
690.583 | 593.583 | 474.7094 | 354.5796 | 335.1912 | 372.1387 | 342.8065 | 388.8645 | 334.8097
691.5844 | 594.5844 | 474.8135 | 354.9848 | 335.5506 | 372.3938 | 343.0688 | 388.953 | 334.755
692.5859 | 595.5859 | 474.8821 | 355.3655 | 335.8899 | 372.643 | 343.3 | 388.9324 | 334.9208
693.5873 | 596.5873 | 474.8371 | 355.714 | 336.2274 | 372.9043 | 343.5475 | 388.9689 | 335.053
694.5888 | 597.5888 | 474.8409 | 356.0205 | 336.5735 | 373.1852 | 343.789 | 389.0136 | 335.4605
695.5902 | 598.5902 | 474.765 | 356.345 | 336.9109 | 373.4541 | 344.0205 | 388.9523 | 335.6562
696.5916 | 599.5916 | 474.7244 | 356.5686 | 337.2631 | 373.72 | 344.3288 | 388.9574 | 335.9853
697.5831 | 600.5831 | 474.727 | 356.8066 | 337.5935 | 373.9806 | 344.5364 | 388.9461 | 336.188
698.5845 | 601.5845 | 474.6715 | 357.015 | 337.9201 | 374.2287 | 344.7824 | 388.9338 | 336.6063
699.586 | 602.586 | 474.6151 | 357.2844 | 338.2494 | 374.459 | 344.9766 | 388.855 | 337.1452
700.5874 | 603.5874 | 474.5806 | 357.5269 | 338.5945 | 374.6948 | 345.2259 | 388.8516 | 337.3693
701.5888 | 604.5888 | 474.5123 | 357.8309 | 338.9312 | 374.9469 | 345.3902 | 388.7863 | 337.5313
702.5903 | 605.5903 | 474.5883 | 358.0538 | 339.265 | 375.1929 | 345.6989 | 388.8595 | 337.3555
703.5817 | 606.5817 | 474.7076 | 358.3415 | 339.5933 | 375.4542 | 345.8937 | 388.9209 | 337.4957
704.5831 | 607.5831 | 474.8315 | 358.6171 | 339.9388 | 375.6924 | 346.1846 | 388.9965 | 337.8168
705.5846 | 608.5846 | 474.6218 | 358.8593 | 340.267 | 375.919 | 346.4862 | 389.0741 | 338.1768
706.586 | 609.586 | 474.4886 | 359.1441 | 340.5909 | 376.185 | 346.7398 | 389.1376 | 337.9858
707.5875 | 610.5875 | 474.1896 | 359.3777 | 340.9064 | 376.4296 | 347.1173 | 389.1626 | 338.4993
708.5889 | 611.5889 | 474.2043 | 359.6626 | 341.2337 | 376.7038 | 347.352 | 389.1537 | 339.0492
709.5803 | 612.5803 | 474.3548 | 359.9317 | 341.5688 | 376.9249 | 347.6826 | 389.1118 | 339.4765
710.5818 | 613.5818 | 474.3995 | 360.2559 | 341.8933 | 377.17 | 347.9443 | 389.1443 | 339.6417
711.5832 | 614.5832 | 474.2498 | 360.4911 | 342.2085 | 377.3756 | 348.279 | 389.199 | 339.8019
712.5846 | 615.5846 | 474.1927 | 360.7909 | 342.5154 | 377.5957 | 348.4925 | 389.1732 | 340.1473
713.5861 | 616.5861 | 474.1054 | 361.0661 | 342.8363 | 377.795 | 348.7998 | 389.1292 | 340.479
714.5875 | 617.5875 | 474.166 | 361.3872 | 343.1699 | 377.9521 | 349.0432 | 389.1376 | 340.9832
715.589 | 618.589 | 474.3403 | 361.7012 | 343.4839 | 378.1571 | 349.2642 | 389.1887 | 341.4692
716.5904 | 619.5904 | 474.2643 | 361.9489 | 343.8042 | 378.3384 | 349.8534 | 389.2655 | 341.9531
717.5818 | 620.5818 | 474.1565 | 362.2127 | 344.1113 | 378.532 | 349.9658 | 389.2075 | 342.3989
718.5833 | 621.5833 | 474.0623 | 362.4089 | 344.431 | 378.7063 | 350.3345 | 389.2749 | 342.7739
719.5847 | 622.5847 | 474.0609 | 362.7343 | 344.7407 | 378.9281 | 350.621 | 389.2457 | 342.9556
720.5862 | 623.5862 | 474.253 | 362.9126 | 345.0598 | 379.1139 | 350.9833 | 389.2825 | 343.094
721.5876 | 624.5876 | 474.4732 | 363.2018 | 345.3786 | 379.3232 | 351.1353 | 389.3119 | 343.3989
722.589 | 625.589 | 474.5122 | 363.4943 | 345.6913 | 379.5331 | 351.4035 | 389.3406 | 343.4909
723.5905 | 626.5905 | 474.4952 | 363.789 | 346.0107 | 379.7433 | 351.6243 | 389.339 | 343.2101
724.5819 | 627.5819 | 474.6444 | 364.0434 | 346.3171 | 379.9509 | 351.9298 | 389.3624 | 343.5079
725.5833 | 628.5833 | 474.8492 | 364.2932 | 346.6319 | 380.1572 | 352.2832 | 389.4616 | 343.6699
726.5848 | 629.5848 | 474.966 | 364.5849 | 346.948 | 380.3759 | 352.5708 | 389.5476 | 343.7936
727.5862 | 630.5862 | 474.8076 | 364.8241 | 347.2761 | 380.5862 | 352.8155 | 389.5934 | 342.9075
728.5977 | 631.5977 | 474.846 | 365.1673 | 347.5897 | 380.8341 | 353.0093 | 389.6377 | 343.2745
729.5891 | 632.5891 | 474.9464 | 365.4221 | 347.9031 | 381.0558 | 353.2791 | 389.7336 | 343.6794
730.5905 | 633.5905 | 475.0573 | 365.6893 | 348.2041 | 381.2838 | 353.5042 | 389.8433 | 343.6349
731.582 | 634.582 | 475.1337 | 365.9449 | 348.526 | 381.4527 | 353.7748 | 389.9316 | 343.4308
732.5834 | 635.5834 | 475.414 | 366.2182 | 348.8293 | 381.6563 | 353.9669 | 390.0043 | 343.8034
733.5848 | 636.5848 | 475.7855 | 366.4265 | 349.1394 | 381.8307 | 354.2597 | 390.0909 | 344.0129
734.5863 | 637.5863 | 475.8663 | 366.7102 | 349.4469 | 381.9892 | 354.5051 | 390.1688 | 344.4272
735.5877 | 638.5877 | 475.7853 | 366.9678 | 349.7548 | 382.1442 | 354.7042 | 390.2878 | 344.6561
736.5892 | 639.5892 | 475.6 | 367.276 | 350.067 | 382.33 | 355.1044 | 390.4437 | 344.9693
737.5906 | 640.5906 | 475.6203 | 367.5004 | 350.382 | 382.4956 | 355.4045 | 390.6269 | 345.2474
738.592 | 641.592 | 475.5905 | 367.8222 | 350.6823 | 382.6529 | 355.6249 | 390.645 | 345.4791
739.5835 | 642.5835 | 475.756 | 368.0482 | 351.0082 | 382.8157 | 355.9136 | 390.782 | 345.8883
740.5849 | 643.5849 | 476.0172 | 368.303 | 351.3092 | 383.0192 | 356.1899 | 390.9126 | 346.0202
741.5863 | 644.5863 | 476.2606 | 368.6096 | 351.6096 | 383.2351 | 356.5453 | 390.9994 | 346.3125
742.5878 | 645.5878 | 476.2577 | 368.8823 | 351.9158 | 383.4364 | 356.8219 | 391.1413 | 346.5483
743.5892 | 646.5892 | 476.2174 | 369.1784 | 352.2189 | 383.6441 | 356.9639 | 391.2372 | 346.6981
744.5907 | 647.5907 | 476.0553 | 369.4222 | 352.5405 | 383.8369 | 357.25 | 391.3119 | 347.0976
745.5821 | 648.5821 | 476.211 | 369.7298 | 352.8488 | 384.0884 | 357.5132 | 391.3548 | 347.3107
746.5835 | 649.5835 | 476.3815 | 369.9655 | 353.149 | 384.3108 | 357.8376 | 391.2181 | 347.6197
747.585 | 650.585 | 476.5864 | 370.2786 | 353.4337 | 384.5465 | 358.0003 | 391.1021 | 347.5997
748.5864 | 651.5864 | 476.5264 | 370.5532 | 353.7487 | 384.7617 | 358.2501 | 391.0328 | 347.6391
749.5879 | 652.5879 | 476.2537 | 370.8212 | 354.0424 | 384.9773 | 358.5618 | 390.8777 | 347.976
750.5893 | 653.5893 | 476.2516 | 371.0966 | 354.342 | 385.2027 | 359.1055 | 390.8622 | 348.2234
751.5907 | 654.5907 | 476.1779 | 371.322 | 354.6478 | 385.412 | 359.3128 | 390.8582 | 348.468
752.5822 | 655.5822 | 476.2488 | 371.6097 | 354.9415 | 385.6397 | 359.4394 | 390.8914 | 348.7332
753.5836 | 656.5836 | 476.1422 | 371.8605 | 355.2369 | 385.8497 | 359.671 | 390.9301 | 348.588
754.585 | 657.585 | 475.9296 | 372.1428 | 355.5241 | 386.0454 | 359.8657 | 390.9354 | 348.866
755.5865 | 658.5865 | 475.5831 | 372.4078 | 355.8184 | 386.2266 | 360.0891 | 390.8931 | 349.155
756.5879 | 659.5879 | 475.3119 | 372.6982 | 356.105 | 386.4293 | 360.2598 | 390.8806 | 349.4163
757.5894 | 660.5894 | 475.1186 | 372.9344 | 356.4075 | 386.6053 | 360.5397 | 390.9235 | 349.6917
758.5908 | 661.5908 | 474.8803 | 373.2021 | 356.6837 | 386.7985 | 360.7047 | 390.8497 | 349.8704
759.5822 | 662.5822 | 474.511 | 373.4107 | 356.9752 | 386.9571 | 361.0362 | 390.7272 | 350.0854
760.5837 | 663.5837 | 474.2789 | 373.6597 | 357.2631 | 387.1323 | 361.2884 | 390.685 | 350.2861
761.5851 | 664.5851 | 474.1901 | 373.8479 | 357.5535 | 387.2867 | 361.5692 | 390.6218 | 350.4381
762.5865 | 665.5865 | 473.9153 | 374.0361 | 357.8424 | 387.4399 | 361.7804 | 390.5542 | 350.5921
763.588 | 666.588 | 473.7682 | 374.2658 | 358.1285 | 387.5812 | 362.0238 | 390.5465 | 350.7976
764.5894 | 667.5894 | 473.5256 | 374.4701 | 358.413 | 387.6902 | 362.3397 | 390.5337 | 350.9663
765.5909 | 668.5909 | 473.3294 | 374.7417 | 358.7035 | 387.8198 | 362.5088 | 390.4618 | 351.0884
766.5823 | 669.5823 | 473.2219 | 374.9546 | 358.9773 | 387.9228 | 362.7533 | 390.5176 | 350.9841
767.5837 | 670.5837 | 473.3784 | 375.1913 | 359.256 | 388.0687 | 362.9661 | 390.41 | 351.1376
768.5852 | 671.5852 | 473.4932 | 375.3902 | 359.5381 | 388.1946 | 363.181 | 390.424 | 351.2503
769.5866 | 672.5866 | 473.5626 | 375.5777 | 359.8219 | 388.3348 | 363.3766 | 390.3756 | 351.3863
770.5881 | 673.5881 | 473.5529 | 375.8377 | 360.1107 | 388.4671 | 363.6634 | 390.368 | 351.5166
771.5895 | 674.5895 | 473.4744 | 376.1204 | 360.3604 | 388.608 | 363.9483 | 390.4051 | 351.757
772.5809 | 675.5809 | 473.2522 | 376.4027 | 360.6178 | 388.7264 | 364.2191 | 390.4563 | 351.7431
773.5824 | 676.5824 | 473.0224 | 376.616 | 360.9007 | 388.8529 | 364.4498 | 390.5076 | 351.8509
774.5838 | 677.5838 | 473.0324 | 376.8788 | 361.1708 | 388.9831 | 364.6277 | 390.5653 | 351.9458
775.5852 | 678.5852 | 473.2308 | 377.0941 | 361.4567 | 389.0971 | 364.9681 | 390.6179 | 351.902
776.5867 | 679.5867 | 473.2833 | 377.3945 | 361.7255 | 389.2482 | 365.0777 | 390.6877 | 351.9638
777.5881 | 680.5881 | 473.206 | 377.6073 | 362.0162 | 389.3842 | 365.365 | 390.7257 | 352.002
778.5896 | 681.5896 | 473.3185 | 377.8917 | 362.2824 | 389.5373 | 365.5133 | 390.8138 | 352.1424
779.591 | 682.591 | 473.461 | 378.1031 | 362.571 | 389.6738 | 365.8113 | 390.8139 | 352.2061
780.5924 | 683.5924 | 473.5186 | 378.3944 | 362.8364 | 389.851 | 366.0191 | 390.8671 | 352.3822
781.5939 | 684.5939 | 473.6205 | 378.6111 | 363.1388 | 389.9983 | 366.249 | 390.8435 | 352.5542
782.5853 | 685.5853 | 473.6343 | 378.8441 | 363.4081 | 390.1561 | 366.4537 | 390.8788 | 352.7465
783.5867 | 686.5867 | 473.7473 | 379.1259 | 363.6729 | 390.3311 | 366.56 | 390.8466 | 352.8814
784.5882 | 687.5882 | 474.0667 | 379.3244 | 363.9621 | 390.4831 | 366.8028 | 390.8404 | 352.9891
785.5896 | 688.5896 | 474.4524 | 379.5893 | 364.2268 | 390.668 | 366.9847 | 390.7125 | 353.1179
786.5911 | 689.5911 | 474.7879 | 379.7854 | 364.5024 | 390.831 | 367.2597 | 390.6505 | 353.3466
787.5825 | 690.5825 | 475.0338 | 380.0385 | 364.7782 | 391.0254 | 367.3864 | 390.6064 | 353.5432
788.5839 | 691.5839 | 475.3595 | 380.2454 | 365.0587 | 391.2124 | 367.6179 | 390.5608 | 353.6612
789.5854 | 692.5854 | 475.5644 | 380.4593 | 365.3334 | 391.3937 | 367.8354 | 390.5993 | 353.8693
790.5868 | 693.5868 | 475.5216 | 380.6985 | 365.6054 | 391.5868 | 367.9996 | 390.6138 | 354.0694
791.5882 | 694.5882 | 475.5354 | 380.9174 | 365.876 | 391.7539 | 368.2576 | 390.6948 | 354.2396
792.5897 | 695.5897 | 475.5477 | 381.1853 | 366.1508 | 391.9588 | 368.3914 | 390.7214 | 354.4767
793.5811 | 696.5811 | 475.4934 | 381.3643 | 366.4233 | 392.1318 | 368.6376 | 390.8009 | 354.6843
794.5826 | 697.5826 | 475.5014 | 381.6002 | 366.6839 | 392.3479 | 368.7997 | 390.8433 | 354.7446
795.584 | 698.584 | 475.3616 | 381.7712 | 366.9659 | 392.5298 | 369.043 | 390.8833 | 354.8301
796.5854 | 699.5854 | 475.3054 | 382.0009 | 367.2253 | 392.7495 | 369.1958 | 390.8712 | 354.886
797.5869 | 700.5869 | 475.2233 | 382.1696 | 367.4629 | 392.9354 | 369.431 | 390.8389 | 354.9669
798.5883 | 701.5883 | 475.1405 | 382.3839 | 367.7236 | 393.1385 | 369.6087 | 390.8416 | 355.0203
799.5898 | 702.5898 | 475.0298 | 382.5545 | 367.9812 | 393.3365 | 369.8046 | 390.7959 | 355.03
800.5912 | 703.5912 | 474.9397 | 382.747 | 368.2275 | 393.5377 | 370.0025 | 390.7198 | 354.9858
801.5926 | 704.5926 | 474.8618 | 382.9407 | 368.4537 | 393.7518 | 370.1709 | 390.7363 | 354.969
802.5841 | 705.5841 | 474.7616 | 383.089 | 368.6846 | 393.952 | 370.4083 | 390.7865 | 354.9963
803.5855 | 706.5855 | 474.8528 | 383.2938 | 368.9044 | 394.161 | 370.5378 | 390.8129 | 355.076
804.5869 | 707.5869 | 474.7414 | 383.448 | 369.1517 | 394.3636 | 370.7657 | 390.8955 | 355.1988
805.5884 | 708.5884 | 474.5726 | 383.6262 | 369.3827 | 394.5669 | 370.9317 | 391.0031 | 355.307
806.5898 | 709.5898 | 474.4137 | 383.767 | 369.6208 | 394.7636 | 371.1531 | 391.0806 | 355.3808
807.5812 | 710.5812 | 474.2502 | 383.9616 | 369.8531 | 395.0002 | 371.2838 | 391.158 | 355.4486
808.5827 | 711.5827 | 474.1453 | 384.1028 | 370.0812 | 395.2238 | 371.5007 | 391.2817 | 355.568
809.5841 | 712.5841 | 474.1944 | 384.2852 | 370.301 | 395.4582 | 371.6848 | 391.37 | 355.6868
810.5856 | 713.5856 | 474.4171 | 384.4394 | 370.513 | 395.6886 | 371.8794 | 391.4598 | 355.7895
811.587 | 714.587 | 474.416 | 384.6076 | 370.7331 | 395.9095 | 372.0389 | 391.6045 | 355.8133
812.5884 | 715.5884 | 474.5352 | 384.7455 | 370.9256 | 396.1358 | 372.2254 | 391.7085 | 355.8246
813.5899 | 716.5899 | 474.5875 | 384.9183 | 371.1151 | 396.3611 | 372.388 | 391.7979 | 355.8491
814.5813 | 717.5813 | 474.5585 | 385.1183 | 371.2922 | 396.6014 | 372.5335 | 391.8943 | 355.8187
815.5828 | 718.5828 | 474.5375 | 385.2764 | 371.4904 | 396.8118 | 372.7243 | 391.9986 | 355.5962
816.5842 | 719.5842 | 474.4689 | 385.4641 | 371.6593 | 397.0535 | 372.8718 | 392.0644 | 355.4891
817.5856 | 720.5856 | 474.5021 | 385.6219 | 371.8443 | 397.2805 | 373.0589 | 392.1187 | 355.6273
818.5871 | 721.5871 | 474.7372 | 385.818 | 372.0106 | 397.5192 | 373.2059 | 392.1899 | 355.7301
819.5885 | 722.5885 | 474.8341 | 385.9685 | 372.1965 | 397.7417 | 373.413 | 392.2541 | 355.85
820.59 | 723.59 | 474.7585 | 386.1414 | 372.3529 | 397.9796 | 373.5692 | 392.3121 | 355.9706
821.5914 | 724.5914 | 474.792 | 386.296 | 372.5101 | 398.2131 | 373.7504 | 392.3564 | 356.0155
822.5828 | 725.5828 | 474.7333 | 386.4679 | 372.6686 | 398.4462 | 373.9258 | 392.4496 | 356.0506
823.5843 | 726.5843 | 474.6355 | 386.6287 | 372.7999 | 398.685 | 374.0892 | 392.4778 | 356.1146
824.5857 | 727.5857 | 474.6387 | 386.7789 | 372.9601 | 398.9217 | 374.283 | 392.548 | 356.2088
825.5871 | 728.5871 | 474.5873 | 386.947 | 373.0821 | 399.1644 | 374.4553 | 392.5503 | 356.3158
826.5886 | 729.5886 | 474.4517 | 387.1025 | 373.2174 | 399.3997 | 374.6449 | 392.5994 | 356.4607
827.59 | 730.59 | 474.3911 | 387.2708 | 373.3377 | 399.6409 | 374.8121 | 392.4607 | 356.5496
828.5915 | 731.5915 | 474.4985 | 387.4165 | 373.4649 | 399.8664 | 375.015 | 392.3953 | 356.3589
829.5829 | 732.5829 | 474.6595 | 387.5816 | 373.5775 | 400.0968 | 375.1818 | 392.3698 | 356.034
830.5843 | 733.5843 | 474.663 | 387.7344 | 373.6789 | 400.3309 | 375.3614 | 392.391 | 355.7456
831.5858 | 734.5858 | 474.6142 | 387.8923 | 373.7989 | 400.5719 | 375.5257 | 392.4655 | 356.0088
832.5872 | 735.5872 | 474.6253 | 388.0581 | 373.9145 | 400.8096 | 375.6669 | 392.4611 | 356.3356
833.5886 | 736.5886 | 474.5992 | 388.2054 | 374.0209 | 401.0359 | 375.8576 | 392.5199 | 356.4365
834.5901 | 737.5901 | 474.5347 | 388.3661 | 374.1313 | 401.2813 | 375.9888 | 392.5289 | 356.5772
835.5815 | 738.5815 | 474.5225 | 388.5066 | 374.2273 | 401.4961 | 376.1331 | 392.5825 | 356.69
836.5829 | 739.5829 | 474.505 | 388.6742 | 374.32 | 401.7303 | 376.2897 | 392.5315 | 356.7415
837.5844 | 740.5844 | 474.4488 | 388.8175 | 374.4298 | 401.9563 | 376.4947 | 392.572 | 356.84
838.5858 | 741.5858 | 474.5139 | 388.9766 | 374.5205 | 402.1752 | 376.6806 | 392.6174 | 356.8883
839.5873 | 742.5873 | 474.4213 | 389.1258 | 374.6099 | 402.3826 | 376.8534 | 392.6696 | 357.0503
840.5887 | 743.5887 | 474.4873 | 389.2989 | 374.692 | 402.587 | 376.9882 | 392.666 | 357.4393
841.5901 | 744.5901 | 474.5435 | 389.4512 | 374.7846 | 402.8007 | 377.0898 | 392.7451 | 357.7243
842.5816 | 745.5816 | 474.6532 | 389.5973 | 374.8555 | 403.003 | 377.2049 | 392.824 | 357.5611
843.583 | 746.583 | 474.6495 | 389.7363 | 374.9372 | 403.2048 | 377.324 | 392.9143 | 357.5123
844.5845 | 747.5845 | 474.5594 | 389.8706 | 375.0287 | 403.4156 | 377.4565 | 392.8795 | 357.3845
845.5859 | 748.5859 | 474.6003 | 390.0298 | 375.1054 | 403.6356 | 377.5528 | 392.9263 | 357.1348
846.5873 | 749.5873 | 474.8381 | 390.1553 | 375.183 | 403.8476 | 377.7021 | 392.9153 | 356.9614
847.5888 | 750.5888 | 474.9653 | 390.3099 | 375.2593 | 404.0809 | 377.7817 | 392.9515 | 356.9962
848.5902 | 751.5902 | 475.0642 | 390.4109 | 375.3322 | 404.2836 | 377.9567 | 392.9691 | 357.1907
849.5917 | 752.5917 | 475.1617 | 390.557 | 375.4043 | 404.5115 | 378.0631 | 393.0385 | 357.4824
850.5831 | 753.5831 | 475.3694 | 390.6652 | 375.4728 | 404.7233 | 378.2402 | 393.0649 | 357.6659
851.5845 | 754.5845 | 475.3854 | 390.804 | 375.5444 | 404.9519 | 378.3595 | 393.1078 | 357.8227
852.586 | 755.586 | 475.3024 | 390.9175 | 375.63 | 405.1632 | 378.5331 | 393.0629 | 357.8938
853.5874 | 756.5874 | 475.3547 | 391.0513 | 375.7082 | 405.3833 | 378.6865 | 393.1383 | 358.019
854.5888 | 757.5888 | 475.3432 | 391.1785 | 375.7769 | 405.5908 | 378.8558 | 393.1417 | 358.1322
855.5903 | 758.5903 | 475.1988 | 391.3009 | 375.8502 | 405.8005 | 379.0292 | 393.1048 | 358.2283
856.5817 | 759.5817 | 475.1126 | 391.457 | 375.9294 | 406.0246 | 379.1559 | 393.1322 | 358.2891
857.5831 | 760.5831 | 475.1568 | 391.5607 | 376.0045 | 406.215 | 379.3551 | 393.1384 | 358.321
858.5846 | 761.5846 | 475.1313 | 391.6945 | 376.0774 | 406.4236 | 379.511 | 393.1735 | 358.2987
859.586 | 762.586 | 475.1103 | 391.8137 | 376.1425 | 406.6165 | 379.6933 | 392.9611 | 358.2999
860.5875 | 763.5875 | 474.839 | 391.959 | 376.2108 | 406.8206 | 379.8325 | 392.7168 | 358.4702
861.5889 | 764.5889 | 474.8328 | 392.0875 | 376.302 | 407.0129 | 380.0141 | 392.7073 | 358.5994
862.5803 | 765.5803 | 474.782 | 392.2115 | 376.3662 | 407.2012 | 380.19 | 392.6745 | 358.8311
863.5818 | 766.5818 | 474.7503 | 392.3451 | 376.4361 | 407.3967 | 380.3536 | 392.705 | 359.05
864.5832 | 767.5832 | 474.5252 | 392.4552 | 376.5017 | 407.5819 | 380.5534 | 392.7718 | 359.2604
865.5846 | 768.5846 | 474.2302 | 392.6015 | 376.585 | 407.783 | 380.69 | 392.8121 | 359.4411
866.5861 | 769.5861 | 474.06 | 392.7087 | 376.6525 | 407.9816 | 380.8672 | 392.8175 | 359.5559
867.5875 | 770.5875 | 473.9645 | 392.8641 | 376.7255 | 408.1791 | 380.9961 | 392.8647 | 359.7589
868.589 | 771.589 | 474.0918 | 392.9585 | 376.8019 | 408.3471 | 381.2138 | 392.9092 | 359.9913
869.5904 | 772.5904 | 474.0713 | 393.1168 | 376.8662 | 408.5527 | 381.3148 | 392.8838 | 360.211
870.5818 | 773.5818 | 474.0972 | 393.2073 | 376.9422 | 408.7159 | 381.5186 | 392.9766 | 360.4389
871.5833 | 774.5833 | 474.0423 | 393.3624 | 377.0211 | 408.9034 | 381.6359 | 393.0443 | 360.597
872.5847 | 775.5847 | 473.8859 | 393.4672 | 377.0944 | 409.0685 | 381.8247 | 393.1736 | 360.6839
873.5862 | 776.5862 | 473.8579 | 393.5985 | 377.1599 | 409.2396 | 381.9721 | 393.295 | 360.8056
874.5876 | 777.5876 | 473.9059 | 393.7137 | 377.2378 | 409.4009 | 382.1462 | 393.4254 | 360.9357
875.589 | 778.589 | 473.9267 | 393.8449 | 377.3087 | 409.5523 | 382.296 | 393.5025 | 361.1537
876.5905 | 779.5905 | 473.9272 | 393.9763 | 377.3751 | 409.7136 | 382.4051 | 393.5038 | 361.4648
877.5819 | 780.5819 | 473.8926 | 394.0681 | 377.4543 | 409.8438 | 382.6 | 393.5943 | 361.7344
878.5833 | 781.5833 | 474.0848 | 394.2163 | 377.5175 | 410.0048 | 382.7068 | 393.5213 | 361.9531
879.5848 | 782.5848 | 474.2944 | 394.3084 | 377.5909 | 410.1415 | 382.8865 | 393.4383 | 362.1535
880.5862 | 783.5862 | 474.5727 | 394.4538 | 377.6601 | 410.3123 | 382.9757 | 393.3878 | 362.3517
881.5877 | 784.5877 | 474.8013 | 394.5418 | 377.7326 | 410.4541 | 383.1573 | 393.3273 | 362.5136
882.5891 | 785.5891 | 474.9579 | 394.6862 | 377.8014 | 410.6162 | 383.2442 | 393.2068 | 362.6541
883.5905 | 786.5905 | 475.0079 | 394.7778 | 377.893 | 410.7568 | 383.4048 | 393.025 | 362.8168
884.592 | 787.592 | 474.9921 | 394.9156 | 377.9584 | 410.9136 | 383.5082 | 392.9834 | 362.9643
885.5834 | 788.5834 | 474.7996 | 395.0377 | 378.0359 | 411.0668 | 383.6339 | 392.9117 | 363.1025
886.5848 | 789.5848 | 474.6674 | 395.1315 | 378.1187 | 411.1985 | 383.7911 | 392.9148 | 363.2699
887.5863 | 790.5863 | 474.7788 | 395.2673 | 378.1819 | 411.3523 | 383.8759 | 392.8518 | 363.4444
888.5877 | 791.5877 | 474.9524 | 395.3705 | 378.2632 | 411.4867 | 384.0362 | 392.7951 | 363.5824
889.5892 | 792.5892 | 474.9878 | 395.5186 | 378.3362 | 411.6434 | 384.1139 | 392.7467 | 363.7269
890.5906 | 793.5906 | 474.8684 | 395.6017 | 378.4261 | 411.7677 | 384.271 | 392.7102 | 363.8672
891.582 | 794.582 | 474.8304 | 395.7453 | 378.4964 | 411.9159 | 384.3482 | 392.7301 | 364.0051
892.5835 | 795.5835 | 474.7866 | 395.8423 | 378.5853 | 412.0273 | 384.5061 | 392.7998 | 364.1334
893.5849 | 796.5849 | 474.7044 | 395.977 | 378.6394 | 412.1605 | 384.5722 | 392.8529 | 364.2708
894.5864 | 797.5864 | 474.6485 | 396.0805 | 378.733 | 412.2609 | 384.7119 | 392.7443 | 364.4035
895.5878 | 798.5878 | 474.636 | 396.1935 | 378.8319 | 412.3689 | 384.8238 | 392.7413 | 364.5289
896.5892 | 799.5892 | 474.59 | 396.3141 | 378.898 | 412.475 | 384.924 | 392.6884 | 364.6058
897.5907 | 800.5907 | 474.5653 | 396.4218 | 378.9885 | 412.5755 | 385.0323 | 392.6353 | 364.681
898.5821 | 801.5821 | 474.4697 | 396.5726 | 379.0668 | 412.6894 | 385.1054 | 392.6471 | 364.788
899.5835 | 802.5835 | 474.2836 | 396.6609 | 379.1572 | 412.7637 | 385.2582 | 392.4473 | 364.8786
900.585 | 803.585 | 474.0066 | 396.8156 | 379.2302 | 412.8612 | 385.3041 | 392.4453 | 365.004
901.5864 | 804.5864 | 473.8491 | 396.9104 | 379.3274 | 412.9319 | 385.44 | 392.3913 | 365.179
902.5879 | 805.5879 | 473.9178 | 397.0592 | 379.3993 | 413.0199 | 385.4886 | 392.343 | 365.3508
903.5893 | 806.5893 | 474.0193 | 397.1551 | 379.4717 | 413.0748 | 385.6431 | 392.3172 | 365.5349
904.5907 | 807.5907 | 474.1077 | 397.2774 | 379.5635 | 413.1348 | 385.7293 | 392.3421 | 365.7039
905.5922 | 808.5922 | 474.0671 | 397.4228 | 379.645 | 413.2077 | 385.801 | 392.294 | 365.7896
906.5836 | 809.5836 | 473.9044 | 397.5048 | 379.7291 | 413.2462 | 385.9411 | 392.3062 | 365.8402
907.585 | 810.585 | 473.7893 | 397.6418 | 379.7978 | 413.299 | 385.9783 | 392.3048 | 365.9492
908.5865 | 811.5865 | 473.7797 | 397.72 | 379.8919 | 413.3249 | 386.1178 | 392.2983 | 366.0574
909.608 | 812.608 | 473.9987 | 397.8663 | 379.9819 | 413.369 | 386.157 | 392.3094 | 366.1908
910.5894 | 813.5894 | 473.8787 | 397.9445 | 380.0746 | 413.3865 | 386.3003 | 392.3476 | 366.3045
911.5908 | 814.5908 | 473.6452 | 398.0652 | 380.1651 | 413.4111 | 386.3352 | 392.4277 | 366.4367
912.5922 | 815.5922 | 473.5805 | 398.1557 | 380.2624 | 413.4331 | 386.4609 | 392.4825 | 366.5567
913.5837 | 816.5837 | 473.6988 | 398.2855 | 380.3392 | 413.4555 | 386.5006 | 392.5539 | 366.6983
914.5851 | 817.5851 | 473.7802 | 398.3808 | 380.4445 | 413.4769 | 386.5876 | 392.6337 | 366.8536
915.5865 | 818.5865 | 473.9485 | 398.4753 | 380.5488 | 413.4913 | 386.7042 | 392.7559 | 366.998
916.588 | 819.588 | 473.8772 | 398.6157 | 380.6493 | 413.5225 | 386.7296 | 392.8344 | 367.0803
917.5894 | 820.5894 | 473.8153 | 398.6833 | 380.743 | 413.5417 | 386.8404 | 392.8618 | 367.1616
918.5909 | 821.5909 | 473.7202 | 398.8164 | 380.8327 | 413.5775 | 386.8345 | 392.9195 | 367.2409
919.5823 | 822.5823 | 473.6987 | 398.8705 | 380.9355 | 413.5909 | 386.977 | 392.959 | 367.3538
920.5837 | 823.5837 | 473.807 | 398.9957 | 381.0265 | 413.6293 | 386.9806 | 393.0004 | 367.4613
921.5852 | 824.5852 | 473.8696 | 399.0669 | 381.1207 | 413.63 | 387.0848 | 393.0961 | 367.6454
922.5866 | 825.5866 | 473.7714 | 399.1916 | 381.2191 | 413.6451 | 387.082 | 393.2012 | 367.8087
923.5881 | 826.5881 | 473.6532 | 399.2517 | 381.3202 | 413.6549 | 387.1746 | 393.2998 | 367.9565
924.5895 | 827.5895 | 473.6701 | 399.3445 | 381.4093 | 413.6632 | 387.2259 | 393.2821 | 368.0958
925.5809 | 828.5809 | 473.7608 | 399.4761 | 381.5038 | 413.6963 | 387.2222 | 393.2202 | 368.1933
926.5824 | 829.5824 | 473.7863 | 399.5294 | 381.6026 | 413.6987 | 387.3136 | 393.2414 | 368.295
927.5838 | 830.5838 | 473.8417 | 399.6491 | 381.7015 | 413.7283 | 387.2927 | 393.2142 | 368.4107
928.5852 | 831.5852 | 473.7244 | 399.7023 | 381.8089 | 413.7315 | 387.3983 | 393.2279 | 368.5562
929.5867 | 832.5867 | 473.786 | 399.8335 | 381.8916 | 413.7677 | 387.379 | 393.2045 | 368.6971
930.5881 | 833.5881 | 473.7915 | 399.8845 | 382 | 413.7761 | 387.4873 | 393.23 | 368.8194
931.5896 | 834.5896 | 473.8905 | 400.0075 | 382.0969 | 413.8177 | 387.4671 | 393.3199 | 368.8869
932.591 | 835.591 | 474.0205 | 400.0589 | 382.2017 | 413.8185 | 387.5797 | 393.4001 | 369.001
933.5824 | 836.5824 | 474.3279 | 400.1587 | 382.2958 | 413.8661 | 387.6086 | 393.5157 | 369.1202
934.5839 | 837.5839 | 474.4136 | 400.2353 | 382.4025 | 413.8945 | 387.6949 | 393.5708 | 369.2228
935.5853 | 838.5853 | 474.4989 | 400.3053 | 382.4943 | 413.9154 | 387.7626 | 393.5753 | 369.3038
936.5867 | 839.5867 | 474.5851 | 400.4186 | 382.5995 | 413.9601 | 387.7696 | 393.6322 | 369.3681
937.5882 | 840.5882 | 474.5774 | 400.4658 | 382.7062 | 413.9867 | 387.8763 | 393.6331 | 369.4539
938.5896 | 841.5896 | 474.6606 | 400.5895 | 382.8152 | 414.0372 | 387.8957 | 393.6219 | 369.5358
939.5811 | 842.5811 | 474.6986 | 400.6399 | 382.9194 | 414.063 | 388.0063 | 393.6682 | 369.6508
940.5825 | 843.5825 | 474.8816 | 400.7657 | 383.0306 | 414.1083 | 388.0124 | 393.7311 | 369.7437
941.5839 | 844.5839 | 475.0726 | 400.8103 | 383.1397 | 414.1256 | 388.1377 | 393.8348 | 369.8135
942.5854 | 845.5854 | 475.2087 | 400.9381 | 383.2423 | 414.168 | 388.1282 | 393.8854 | 369.8813
943.5868 | 846.5868 | 475.2228 | 400.9932 | 383.3527 | 414.1864 | 388.2443 | 393.9612 | 370.01
944.5883 | 847.5883 | 475.1726 | 401.0888 | 383.4586 | 414.2158 | 388.2969 | 393.994 | 370.1279
945.5897 | 848.5897 | 475.304 | 401.1822 | 383.569 | 414.2427 | 388.3664 | 393.9733 | 370.2467
946.5811 | 849.5811 | 475.3798 | 401.2535 | 383.6806 | 414.2631 | 388.4499 | 393.8993 | 370.3376
947.5826 | 850.5826 | 475.4023 | 401.3963 | 383.7824 | 414.3112 | 388.4399 | 393.8808 | 370.4469
948.584 | 851.584 | 475.2756 | 401.4462 | 383.8988 | 414.3274 | 388.5365 | 393.8411 | 370.5644
949.5854 | 852.5854 | 475.2078 | 401.5399 | 383.9955 | 414.3621 | 388.6245 | 393.818 | 370.6826
950.5869 | 853.5869 | 475.1632 | 401.6177 | 384.1205 | 414.3908 | 388.7109 | 393.8477 | 370.798
951.5883 | 854.5883 | 474.9397 | 401.7359 | 384.2243 | 414.4308 | 388.7273 | 393.7838 | 370.8548
952.5898 | 855.5898 | 474.8713 | 401.7864 | 384.3404 | 414.4568 | 388.855 | 393.7488 | 370.9112
953.5912 | 856.5912 | 474.7319 | 401.8946 | 384.4551 | 414.5024 | 388.9119 | 393.6663 | 370.99
954.5826 | 857.5826 | 474.6277 | 401.9752 | 384.5756 | 414.5324 | 389.0026 | 393.6586 | 371.0469
955.5841 | 858.5841 | 474.5201 | 402.0873 | 384.6898 | 414.5921 | 389.033 | 393.6643 | 371.1244
956.5855 | 859.5855 | 474.5448 | 402.1859 | 384.8028 | 414.6243 | 389.0954 | 393.7257 | 371.2042
957.5869 | 860.5869 | 474.4408 | 402.2294 | 384.9228 | 414.6574 | 389.2316 | 393.8084 | 371.2513
958.5884 | 861.5884 | 474.4381 | 402.3437 | 385.0454 | 414.7093 | 389.276 | 393.7791 | 371.2981
959.5898 | 862.5898 | 474.2809 | 402.4401 | 385.1605 | 414.7505 | 389.3474 | 393.7808 | 371.3371
960.5913 | 863.5913 | 474.1952 | 402.5455 | 385.2698 | 414.7932 | 389.3903 | 393.8585 | 371.3706
961.5827 | 864.5827 | 474.2521 | 402.5903 | 385.3935 | 414.8154 | 389.5085 | 393.8778 | 371.4133
962.5841 | 865.5841 | 474.1951 | 402.6817 | 385.507 | 414.851 | 389.5674 | 393.8889 | 371.4496
963.5856 | 866.5856 | 474.049 | 402.7839 | 385.6219 | 414.9005 | 389.6141 | 393.9075 | 371.4996
964.587 | 867.587 | 474.1137 | 402.8737 | 385.7457 | 414.9267 | 389.7043 | 393.9746 | 371.5242
965.5884 | 868.5884 | 474.3038 | 402.9446 | 385.8586 | 414.9639 | 389.7898 | 394.0252 | 371.5608
966.5899 | 869.5899 | 474.2878 | 403.0139 | 385.9831 | 414.9984 | 389.8693 | 394.096 | 371.5869
967.5813 | 870.5813 | 474.3417 | 403.1465 | 386.0953 | 415.0661 | 389.8792 | 394.0904 | 371.6334
968.5828 | 871.5828 | 474.4295 | 403.1979 | 386.2105 | 415.0899 | 389.9894 | 394.1324 | 371.6556
969.5842 | 872.5842 | 474.5923 | 403.268 | 386.3478 | 415.1328 | 390.0838 | 394.0684 | 371.6924
970.5856 | 873.5856 | 474.8269 | 403.3464 | 386.4603 | 415.1703 | 390.1606 | 394.0018 | 371.7597
971.5871 | 874.5871 | 474.9548 | 403.4373 | 386.5777 | 415.2122 | 390.2058 | 393.864 | 371.8436
972.5885 | 875.5885 | 475.0038 | 403.532 | 386.6937 | 415.2573 | 390.2547 | 393.7445 | 371.9335
973.59 | 876.59 | 474.9742 | 403.5543 | 386.819 | 415.2785 | 390.4061 | 393.7423 | 371.9879
974.5814 | 877.5814 | 474.8942 | 403.6631 | 386.938 | 415.3318 | 390.4187 | 393.6099 | 372.0537
975.5828 | 878.5828 | 474.7689 | 403.6919 | 387.0546 | 415.3561 | 390.5605 | 393.6091 | 372.1337
976.5843 | 879.5843 | 474.9132 | 403.8082 | 387.1775 | 415.4167 | 390.584 | 393.5066 | 372.1976
977.5857 | 880.5857 | 474.8478 | 403.8389 | 387.3085 | 415.4325 | 390.7255 | 393.5386 | 372.2871
978.5871 | 881.5871 | 474.7455 | 403.957 | 387.4233 | 415.4885 | 390.7608 | 393.5144 | 372.3552
979.5886 | 882.5886 | 474.6645 | 404.0105 | 387.5338 | 415.5213 | 390.8603 | 393.465 | 372.4033
980.59 | 883.59 | 474.6112 | 404.064 | 387.6683 | 415.5579 | 390.9581 | 393.525 | 372.4809
981.5814 | 884.5814 | 474.4324 | 404.1438 | 387.7963 | 415.6071 | 391.0441 | 393.5384 | 372.5418
982.5829 | 885.5829 | 474.2252 | 404.1968 | 387.9197 | 415.6497 | 391.1631 | 393.6499 | 372.6048
983.5843 | 886.5843 | 474.3026 | 404.3122 | 388.0388 | 415.7213 | 391.1705 | 393.7188 | 372.6613
984.5858 | 887.5858 | 474.3967 | 404.3471 | 388.1743 | 415.7597 | 391.334 | 393.8062 | 372.7397
985.5872 | 888.5872 | 474.5464 | 404.4655 | 388.2868 | 415.8275 | 391.3597 | 393.8869 | 372.817
986.5886 | 889.5886 | 474.4862 | 404.4894 | 388.4171 | 415.8671 | 391.4979 | 393.9563 | 372.8966
987.5901 | 890.5901 | 474.4902 | 404.6045 | 388.5387 | 415.9379 | 391.5338 | 393.9999 | 372.9889
988.5815 | 891.5815 | 474.716 | 404.6524 | 388.6703 | 415.9927 | 391.6538 | 394.0694 | 373.0647
989.583 | 892.583 | 475.0975 | 404.7393 | 388.7864 | 416.0551 | 391.7146 | 394.0496 | 373.1325
990.5844 | 893.5844 | 475.2456 | 404.8307 | 388.9149 | 416.1292 | 391.7881 | 394.0441 | 373.2085
991.5858 | 894.5858 | 475.3982 | 404.8699 | 389.055 | 416.2049 | 391.9168 | 394.0097 | 373.2747
992.5873 | 895.5873 | 475.6347 | 404.9785 | 389.176 | 416.2839 | 391.9546 | 394.0546 | 373.3542
993.5887 | 896.5887 | 475.6858 | 405.0258 | 389.306 | 416.3556 | 392.0821 | 394.0571 | 373.41
994.5902 | 897.5902 | 475.6303 | 405.1373 | 389.4346 | 416.4593 | 392.1015 | 393.9345 | 373.4895
995.5916 | 898.5916 | 475.3707 | 405.166 | 389.5605 | 416.5272 | 392.245 | 393.9884 | 373.629
996.583 | 899.583 | 475.2861 | 405.2873 | 389.6785 | 416.6199 | 392.2611 | 394.0228 | 373.7505
997.5845 | 900.5845 | 475.4782 | 405.3306 | 389.8172 | 416.687 | 392.4054 | 394.0915 | 373.8593
998.5859 | 901.5859 | 475.5593 | 405.4536 | 389.9574 | 416.7817 | 392.4311 | 393.9845 | 373.946
999.5873 | 902.5873 | 475.4836 | 405.4878 | 390.0964 | 416.8442 | 392.5792 | 394.0599 | 374.0445
1000.5888 | 903.5888 | 475.4537 | 405.5802 | 390.2201 | 416.9299 | 392.6211 | 394.105 | 374.1412
1001.5902 | 904.5902 | 475.536 | 405.6763 | 390.3493 | 417.0071 | 392.6873 | 394.2019 | 374.2326
1002.5917 | 905.5917 | 475.6258 | 405.7271 | 390.4908 | 417.062 | 392.8242 | 394.2776 | 374.3175
1003.5831 | 906.5831 | 475.4717 | 405.8389 | 390.6185 | 417.1565 | 392.8487 | 394.3323 | 374.4169
1004.5845 | 907.5845 | 475.3074 | 405.8865 | 390.7634 | 417.2158 | 392.9953 | 394.4574 | 374.5186
1005.586 | 908.586 | 475.181 | 406.0131 | 390.8867 | 417.3033 | 393.021 | 394.5758 | 374.616
1006.5874 | 909.5874 | 474.9954 | 406.0606 | 391.0301 | 417.3661 | 393.16 | 394.7081 | 374.6783
1007.5888 | 910.5888 | 474.8927 | 406.1689 | 391.165 | 417.4466 | 393.1989 | 394.7892 | 374.7724
1008.5903 | 911.5903 | 474.7967 | 406.2473 | 391.2956 | 417.5104 | 393.3008 | 394.9137 | 374.8714
1009.5817 | 912.5817 | 474.7449 | 406.3207 | 391.4321 | 417.5752 | 393.3845 | 394.9246 | 374.9452
1010.5831 | 913.5831 | 474.7355 | 406.4118 | 391.573 | 417.6307 | 393.4341 | 395.0002 | 375.0521
1011.5846 | 914.5846 | 474.9433 | 406.4741 | 391.7077 | 417.6947 | 393.5425 | 395.0242 | 375.154
1012.586 | 915.586 | 475.0413 | 406.5769 | 391.8484 | 417.7618 | 393.5838 | 395.0343 | 375.2446
1013.5875 | 916.5875 | 475.2204 | 406.6161 | 391.9827 | 417.8054 | 393.7148 | 395.0463 | 375.3271
1014.5889 | 917.5889 | 475.2331 | 406.7331 | 392.1136 | 417.8605 | 393.7484 | 395.0693 | 375.4149
1015.5803 | 918.5803 | 475.3187 | 406.7652 | 392.2628 | 417.8991 | 393.8731 | 395.0651 | 375.5048
1016.5818 | 919.5818 | 475.3562 | 406.8742 | 392.3976 | 417.9604 | 393.8957 | 395.0711 | 375.5894
1017.5832 | 920.5832 | 475.4354 | 406.928 | 392.5364 | 418.0024 | 394.0365 | 394.9835 | 375.6691
1018.5847 | 921.5847 | 475.4125 | 407.0224 | 392.6739 | 418.0525 | 394.0743 | 394.9883 | 375.777
1019.5861 | 922.5861 | 475.5279 | 407.078 | 392.8233 | 418.1014 | 394.1775 | 394.9198 | 375.8482
1020.5875 | 923.5875 | 475.5586 | 407.1397 | 392.9508 | 418.1471 | 394.2654 | 394.7994 | 375.8989
1021.589 | 924.589 | 475.5166 | 407.2167 | 393.085 | 418.2075 | 394.3518 | 394.7563 | 375.9598
1022.5904 | 925.5904 | 475.514 | 407.279 | 393.2203 | 418.2652 | 394.4633 | 394.7011 | 376.0139
1023.5919 | 926.5919 | 475.6477 | 407.383 | 393.363 | 418.3323 | 394.5074 | 394.6753 | 376.0625
1024.5833 | 927.5833 | 475.6844 | 407.4226 | 393.4955 | 418.3748 | 394.6579 | 394.622 | 376.0993
1025.5847 | 928.5847 | 475.5875 | 407.5425 | 393.6166 | 418.46 | 394.6568 | 394.5809 | 376.1531
1026.5862 | 929.5862 | 475.2143 | 407.5619 | 393.7603 | 418.5033 | 394.8461 | 394.5282 | 376.2386
1027.5876 | 930.5876 | 475.181 | 407.6815 | 393.8902 | 418.5788 | 394.8891 | 394.4429 | 376.3096
1028.589 | 931.589 | 475.035 | 407.7268 | 394.0271 | 418.6193 | 395.0382 | 394.3992 | 376.3996
1029.5905 | 932.5905 | 474.914 | 407.821 | 394.1633 | 418.6794 | 395.1062 | 394.3256 | 376.4814
1030.5819 | 933.5819 | 474.8324 | 407.9031 | 394.2836 | 418.7269 | 395.2079 | 394.3443 | 376.5664
1031.5833 | 934.5833 | 474.8304 | 407.9827 | 394.4224 | 418.773 | 395.3137 | 394.4261 | 376.672
1032.5848 | 935.5848 | 474.7105 | 408.0652 | 394.5569 | 418.8214 | 395.4029 | 394.5077 | 376.7406
1033.5862 | 936.5862 | 474.6685 | 408.1403 | 394.6854 | 418.8641 | 395.5058 | 394.3928 | 376.8313
1034.5877 | 937.5877 | 474.8163 | 408.2378 | 394.8172 | 418.9094 | 395.5916 | 394.3299 | 376.9342
1035.5891 | 938.5891 | 474.7735 | 408.3203 | 394.9508 | 418.9452 | 395.7169 | 394.3429 | 377.0188
1036.5905 | 939.5905 | 474.6978 | 408.4117 | 395.0697 | 418.9824 | 395.7999 | 394.3726 | 377.1036
1037.592 | 940.592 | 474.6569 | 408.5007 | 395.2168 | 419.0233 | 395.9076 | 394.4455 | 377.189
1038.5834 | 941.5834 | 474.5153 | 408.604 | 395.335 | 419.0701 | 395.9716 | 394.4335 | 377.254
1039.5848 | 942.5848 | 474.6143 | 408.6739 | 395.4675 | 419.1002 | 396.0915 | 394.48 | 377.3004
1040.5863 | 943.5863 | 474.4522 | 408.7741 | 395.577 | 419.1517 | 396.1744 | 394.4301 | 377.3883
1041.5877 | 944.5877 | 474.5533 | 408.8454 | 395.7161 | 419.1904 | 396.2888 | 394.3632 | 377.4572
1042.5892 | 945.5892 | 474.8101 | 408.967 | 395.8421 | 419.2438 | 396.3306 | 394.3021 | 377.5491
1043.5906 | 946.5906 | 474.9265 | 409.0548 | 395.9692 | 419.2767 | 396.4334 | 394.2276 | 377.6266
1044.592 | 947.592 | 474.9171 | 409.1459 | 396.1019 | 419.317 | 396.551 | 394.1708 | 377.6955
1045.5835 | 948.5835 | 474.8257 | 409.2479 | 396.2282 | 419.3508 | 396.6272 | 394.1143 | 377.7853
1046.5849 | 949.5849 | 474.7235 | 409.3275 | 396.3534 | 419.3718 | 396.7298 | 394.1308 | 377.8556
1047.5864 | 950.5864 | 474.7225 | 409.4247 | 396.4769 | 419.3974 | 396.8125 | 394.0394 | 377.9436
1048.5878 | 951.5878 | 474.5676 | 409.5196 | 396.6104 | 419.4165 | 396.911 | 393.9495 | 378.0144
1049.5892 | 952.5892 | 474.5784 | 409.6284 | 396.7258 | 419.4393 | 396.977 | 393.9253 | 378.0904
1050.5907 | 953.5907 | 474.6399 | 409.7288 | 396.8396 | 419.4551 | 397.0675 | 393.7571 | 378.156
1051.5821 | 954.5821 | 474.7093 | 409.8206 | 396.9762 | 419.4652 | 397.1604 | 393.6784 | 378.2395
1052.5835 | 955.5835 | 474.5448 | 409.9032 | 397.1112 | 419.4765 | 397.2775 | 393.6515 | 378.331
1053.585 | 956.585 | 474.1792 | 410.0073 | 397.2302 | 419.4822 | 397.3474 | 393.6065 | 378.4089
1054.5864 | 957.5864 | 473.9 | 410.0854 | 397.3569 | 419.4771 | 397.4326 | 393.6365 | 378.4881
1055.5879 | 958.5879 | 473.9225 | 410.2104 | 397.477 | 419.487 | 397.4748 | 393.5645 | 378.569
1056.5893 | 959.5893 | 474.0092 | 410.3147 | 397.6053 | 419.493 | 397.5368 | 393.493 | 378.6376
1057.5907 | 960.5907 | 473.9165 | 410.3576 | 397.7285 | 419.4759 | 397.6786 | 393.4919 | 378.7172
1058.5822 | 961.5822 | 473.7927 | 410.459 | 397.8537 | 419.4776 | 397.7418 | 393.456 | 378.8101
1059.5836 | 962.5836 | 473.926 | 410.5353 | 397.9801 | 419.4648 | 397.8418 | 393.4694 | 378.899
1060.585 | 963.585 | 474.1589 | 410.6515 | 398.1048 | 419.4662 | 397.8836 | 393.3967 | 378.9964
1061.5865 | 964.5865 | 474.2948 | 410.7483 | 398.2348 | 419.4628 | 397.9505 | 393.3976 | 379.0689
1062.5879 | 965.5879 | 474.3197 | 410.8055 | 398.3619 | 419.4567 | 398.0747 | 393.3226 | 379.1638
1063.5894 | 966.5894 | 474.4043 | 410.9179 | 398.4701 | 419.4615 | 398.1128 | 393.2654 | 379.2607
1064.5908 | 967.5908 | 474.5501 | 410.9736 | 398.6028 | 419.4586 | 398.2086 | 393.2195 | 379.3602
1065.5822 | 968.5822 | 474.6279 | 411.0514 | 398.7197 | 419.4656 | 398.3038 | 393.2743 | 379.448
1066.5837 | 969.5837 | 474.5246 | 411.134 | 398.8299 | 419.476 | 398.3674 | 393.3449 | 379.5489
1067.5851 | 970.5851 | 474.5533 | 411.2153 | 398.9574 | 419.4898 | 398.4328 | 393.4232 | 379.6526
1068.5866 | 971.5866 | 474.5003 | 411.3044 | 399.0587 | 419.4995 | 398.4904 | 393.4529 | 379.7675
1069.588 | 972.588 | 474.5864 | 411.3418 | 399.185 | 419.4958 | 398.6298 | 393.5418 | 379.886
1070.5894 | 973.5894 | 474.5492 | 411.4202 | 399.2991 | 419.4998 | 398.6768 | 393.603 | 379.971
1071.5909 | 974.5909 | 474.2976 | 411.4929 | 399.4224 | 419.5159 | 398.743 | 393.6693 | 380.0735
1072.5823 | 975.5823 | 474.0988 | 411.5884 | 399.5281 | 419.5332 | 398.776 | 393.7778 | 380.1825
1073.5837 | 976.5837 | 473.9402 | 411.6536 | 399.6458 | 419.5374 | 398.844 | 393.9137 | 380.2851
1074.5852 | 977.5852 | 473.644 | 411.7131 | 399.757 | 419.5453 | 398.9372 | 394.0324 | 380.388
1075.5866 | 978.5866 | 473.5099 | 411.815 | 399.87 | 419.5601 | 398.9671 | 394.1813 | 380.4866
1076.5881 | 979.5881 | 473.5701 | 411.8751 | 399.9876 | 419.5703 | 399.0745 | 394.3476 | 380.5852
1077.5895 | 980.5895 | 473.5243 | 411.9594 | 400.1019 | 419.6019 | 399.1188 | 394.5115 | 380.668
1078.5809 | 981.5809 | 473.5911 | 412.0339 | 400.2047 | 419.6266 | 399.172 | 394.634 | 380.7438
1079.5824 | 982.5824 | 473.6573 | 412.1091 | 400.3207 | 419.6554 | 399.2265 | 394.6779 | 380.8132
1080.5838 | 983.5838 | 473.7215 | 412.1485 | 400.4284 | 419.6827 | 399.332 | 394.7785 | 380.8982
1081.6053 | 984.6053 | 473.7019 | 412.2495 | 400.5373 | 419.738 | 399.3369 | 394.7667 | 380.9894
1082.5867 | 985.5867 | 473.5815 | 412.2785 | 400.639 | 419.774 | 399.4347 | 394.8804 | 381.0798
1083.5881 | 986.5881 | 473.6524 | 412.3611 | 400.7486 | 419.8356 | 399.4614 | 394.9433 | 381.2
1084.5896 | 987.5896 | 473.7534 | 412.3862 | 400.8563 | 419.8664 | 399.5452 | 394.8962 | 381.3264
1085.591 | 988.591 | 473.9032 | 412.4442 | 400.9544 | 419.9028 | 399.6044 | 394.8449 | 381.4299
1086.5824 | 989.5824 | 474.0828 | 412.4826 | 401.0742 | 419.9421 | 399.6786 | 394.7805 | 381.5823
1087.5839 | 990.5839 | 474.1548 | 412.5059 | 401.176 | 419.9846 | 399.7776 | 394.7333 | 381.6964
1088.5853 | 991.5853 | 474.2342 | 412.5916 | 401.2817 | 420.0195 | 399.7925 | 394.6858 | 381.8212
1089.5867 | 992.5867 | 474.2763 | 412.6114 | 401.3807 | 420.046 | 399.9064 | 394.6439 | 381.9256
1090.5882 | 993.5882 | 474.2891 | 412.7024 | 401.4764 | 420.1143 | 399.8973 | 394.6199 | 382.0378
1091.5896 | 994.5896 | 474.3855 | 412.7262 | 401.5764 | 420.1409 | 400.0151 | 394.5422 | 382.145
1092.5911 | 995.5911 | 474.4033 | 412.783 | 401.6884 | 420.1763 | 400.0641 | 394.5274 | 382.2626
1093.5825 | 996.5825 | 474.4091 | 412.8384 | 401.7774 | 420.217 | 400.1122 | 394.3519 | 382.4074
1094.5839 | 997.5839 | 474.2975 | 412.8643 | 401.8813 | 420.2298 | 400.2493 | 394.1985 | 382.5401
1095.5854 | 998.5854 | 474.2611 | 412.9525 | 401.9767 | 420.2767 | 400.2568 | 394.1947 | 382.7
1096.5868 | 999.5868 | 474.3484 | 412.9497 | 402.0867 | 420.2951 | 400.3914 | 394.1928 | 382.8777
1097.5883 | 1000.5883 | 474.3266 | 413.0222 | 402.1807 | 420.3537 | 400.4064 | 394.1508 | 383.0473
1098.5897 | 1001.5897 | 474.3809 | 413.0239 | 402.2764 | 420.3703 | 400.5407 | 394.1978 | 383.2396
1099.5811 | 1002.5811 | 474.7296 | 413.0935 | 402.3693 | 420.4133 | 400.5606 | 394.3018 | 383.4477
1100.5826 | 1003.5826 | 474.9935 | 413.0938 | 402.4861 | 420.4467 | 400.7075 | 394.4 | 383.6633
1101.584 | 1004.584 | 475.0943 | 413.1755 | 402.5863 | 420.4998 | 400.7168 | 394.5085 | 383.8725
1102.5854 | 1005.5854 | 475.0717 | 413.1627 | 402.6979 | 420.5268 | 400.8671 | 394.6738 | 384.0666
1103.5869 | 1006.5869 | 475.0709 | 413.226 | 402.7873 | 420.5772 | 400.9179 | 394.783 | 384.2773
1104.5883 | 1007.5883 | 475.0485 | 413.2693 | 402.8904 | 420.6115 | 401.0098 | 394.9325 | 384.4932
1105.5898 | 1008.5898 | 475.0904 | 413.2943 | 402.985 | 420.6572 | 401.0948 | 395.0618 | 384.6832
1106.5812 | 1009.5812 | 475.1119 | 413.3171 | 403.0905 | 420.7002 | 401.1677 | 395.1466 | 384.8721
1107.5826 | 1010.5826 | 475.1006 | 413.3393 | 403.1882 | 420.7438 | 401.2893 | 395.3082 | 385.07
1108.5841 | 1011.5841 | 475.1544 | 413.4204 | 403.2722 | 420.8039 | 401.3155 | 395.4337 | 385.1567
1109.5855 | 1012.5855 | 475.3196 | 413.4201 | 403.3684 | 420.8476 | 401.4558 | 395.499 | 385.2642
1110.5869 | 1013.5869 | 475.3311 | 413.5169 | 403.447 | 420.9091 | 401.4712 | 395.5141 | 385.3546
1111.5884 | 1014.5884 | 475.2991 | 413.5223 | 403.5629 | 420.9472 | 401.6174 | 395.5461 | 385.4247
1112.5898 | 1015.5898 | 475.2499 | 413.6154 | 403.665 | 421.0107 | 401.6654 | 395.4777 | 385.495
1113.5913 | 1016.5913 | 475.0536 | 413.6549 | 403.7692 | 421.0597 | 401.7513 | 395.4848 | 385.5556
1114.5827 | 1017.5827 | 474.9582 | 413.6914 | 403.8586 | 421.0873 | 401.862 | 395.4906 | 385.614
1115.5841 | 1018.5841 | 474.7193 | 413.7635 | 403.9625 | 421.1265 | 401.9293 | 395.5065 | 385.686
1116.5856 | 1019.5856 | 474.7334 | 413.7837 | 404.0608 | 421.1637 | 402.059 | 395.5979 | 385.7506
1117.587 | 1020.587 | 474.8243 | 413.8896 | 404.1536 | 421.2058 | 402.0836 | 395.6908 | 385.8389
1118.5885 | 1021.5885 | 474.8373 | 413.8971 | 404.2447 | 421.212 | 402.2373 | 395.7696 | 385.9065
1119.5899 | 1022.5899 | 474.7782 | 413.9789 | 404.3273 | 421.2622 | 402.2754 | 395.855 | 385.9884
1120.5813 | 1023.5813 | 474.7116 | 413.9906 | 404.4563 | 421.2836 | 402.4053 | 395.9346 | 386.0797
1121.5828 | 1024.5828 | 474.9232 | 414.0787 | 404.5511 | 421.3301 | 402.426 | 395.9474 | 386.182
1122.5842 | 1025.5842 | 475.0871 | 414.0829 | 404.6604 | 421.3578 | 402.5924 | 396.0132 | 386.2725
1123.5856 | 1026.5856 | 475.2697 | 414.1725 | 404.7611 | 421.4018 | 402.6166 | 395.9675 | 386.3532
1124.5871 | 1027.5871 | 475.288 | 414.1787 | 404.8624 | 421.4172 | 402.782 | 396.0113 | 386.4316
1125.5885 | 1028.5885 | 475.2939 | 414.2764 | 404.9578 | 421.4821 | 402.8038 | 395.9888 | 386.5382
1126.59 | 1029.59 | 475.422 | 414.3002 | 405.0665 | 421.5032 | 402.9516 | 395.8622 | 386.6402
1127.5914 | 1030.5914 | 475.5222 | 414.3726 | 405.1585 | 421.5384 | 403.0213 | 395.7712 | 386.7551
1128.5828 | 1031.5828 | 475.5659 | 414.4483 | 405.2567 | 421.5684 | 403.0944 | 395.778 | 386.8755
1129.5843 | 1032.5843 | 475.5501 | 414.502 | 405.3512 | 421.5882 | 403.2108 | 395.8189 | 387.0004
1130.5857 | 1033.5857 | 475.5022 | 414.5874 | 405.4442 | 421.6267 | 403.2466 | 395.8702 | 387.133
1131.5871 | 1034.5871 | 475.2419 | 414.6275 | 405.5501 | 421.637 | 403.3848 | 395.9165 | 387.2569
1132.5886 | 1035.5886 | 474.9886 | 414.7297 | 405.6353 | 421.6849 | 403.3867 | 395.961 | 387.3795
1133.59 | 1036.59 | 474.8371 | 414.765 | 405.7402 | 421.7033 | 403.5456 | 395.9706 | 387.4928
1134.5915 | 1037.5915 | 474.8154 | 414.8884 | 405.8392 | 421.7542 | 403.5473 | 395.9279 | 387.6058
1135.5829 | 1038.5829 | 474.9165 | 414.9245 | 405.9332 | 421.7633 | 403.6952 | 395.9341 | 387.6793
1136.5843 | 1039.5843 | 474.9339 | 415.0132 | 406.0245 | 421.7878 | 403.7676 | 395.9132 | 387.7433
1137.5858 | 1040.5858 | 474.9985 | 415.1058 | 406.1092 | 421.8258 | 403.8193 | 395.8756 | 387.8139
1138.5872 | 1041.5872 | 474.9776 | 415.145 | 406.2168 | 421.8386 | 403.9428 | 395.8918 | 387.8765
1139.5886 | 1042.5886 | 474.9113 | 415.2491 | 406.3109 | 421.8818 | 403.9355 | 395.9015 | 387.9412
1140.5801 | 1043.5801 | 474.8726 | 415.2592 | 406.4037 | 421.8831 | 404.0773 | 395.906 | 388.0132
1141.5815 | 1044.5815 | 474.8725 | 415.3575 | 406.504 | 421.9298 | 404.0854 | 395.907 | 388.102
1142.583 | 1045.583 | 474.9916 | 415.3843 | 406.613 | 421.942 | 404.2058 | 395.8256 | 388.1871
1143.5844 | 1046.5844 | 475.1993 | 415.4947 | 406.7039 | 421.9869 | 404.2421 | 395.8606 | 388.2794
1144.5858 | 1047.5858 | 475.3088 | 415.528 | 406.7974 | 421.9995 | 404.3498 | 395.8372 | 388.3804
1145.5873 | 1048.5873 | 475.2765 | 415.5987 | 406.8944 | 422.0312 | 404.3782 | 395.7268 | 388.4743
1146.5887 | 1049.5887 | 475.2952 | 415.6726 | 406.9966 | 422.0512 | 404.4411 | 395.6784 | 388.57
1147.5902 | 1050.5902 | 475.2201 | 415.7567 | 407.0646 | 422.0706 | 404.5172 | 395.6526 | 388.6585
1148.5816 | 1051.5816 | 475.1674 | 415.8326 | 407.1634 | 422.0996 | 404.5716 | 395.5868 | 388.7511
1149.583 | 1052.583 | 475.138 | 415.8973 | 407.233 | 422.1043 | 404.6739 | 395.5691 | 388.8215
1150.5845 | 1053.5845 | 475.3206 | 416.0139 | 407.3301 | 422.1377 | 404.6724 | 395.5213 | 388.8836
1151.5859 | 1054.5859 | 475.306 | 416.0622 | 407.4309 | 422.1359 | 404.7775 | 395.5219 | 388.9403
1152.5873 | 1055.5873 | 475.2556 | 416.154 | 407.5172 | 422.1557 | 404.8234 | 395.5323 | 389.004
1153.5888 | 1056.5888 | 475.0069 | 416.2242 | 407.6024 | 422.156 | 404.9092 | 395.5783 | 389.0491
1154.5902 | 1057.5902 | 474.9826 | 416.2983 | 407.6943 | 422.1662 | 404.9632 | 395.5645 | 389.1077
1155.5917 | 1058.5917 | 474.9515 | 416.392 | 407.7818 | 422.1805 | 405.0088 | 395.5335 | 389.1718
1156.5831 | 1059.5831 | 474.8917 | 416.4435 | 407.8788 | 422.1885 | 405.1014 | 395.5969 | 389.228
1157.5845 | 1060.5845 | 474.6884 | 416.5253 | 407.9527 | 422.2004 | 405.1012 | 395.6061 | 389.3056
1158.586 | 1061.586 | 474.3918 | 416.5687 | 408.0558 | 422.1972 | 405.2255 | 395.573 | 389.3781
1159.5874 | 1062.5874 | 474.2737 | 416.6767 | 408.1403 | 422.2202 | 405.2249 | 395.5362 | 389.4538
1160.5888 | 1063.5888 | 474.4036 | 416.7319 | 408.2343 | 422.2151 | 405.3351 | 395.449 | 389.5336
1161.5803 | 1064.5803 | 474.4433 | 416.8273 | 408.3199 | 422.2273 | 405.3521 | 395.4588 | 389.6106
1162.5817 | 1065.5817 | 474.5222 | 416.8984 | 408.4224 | 422.236 | 405.4118 | 395.4903 | 389.6933
1163.5832 | 1066.5832 | 474.4 | 416.9358 | 408.5249 | 422.2211 | 405.5177 | 395.5593 | 389.7755
1164.5846 | 1067.5846 | 474.459 | 417.027 | 408.6154 | 422.2208 | 405.5682 | 395.6678 | 389.8449
1165.586 | 1068.586 | 474.6478 | 417.0774 | 408.7121 | 422.2137 | 405.6482 | 395.669 | 389.9168
1166.5875 | 1069.5875 | 474.736 | 417.1765 | 408.7899 | 422.2247 | 405.6599 | 395.7117 | 389.9801
1167.5889 | 1070.5889 | 474.9674 | 417.2092 | 408.8911 | 422.2102 | 405.7471 | 395.6777 | 390.0381
1168.5904 | 1071.5904 | 475.1042 | 417.2826 | 408.9844 | 422.2073 | 405.8066 | 395.6777 | 390.105
1169.5918 | 1072.5918 | 475.1261 | 417.3941 | 409.0706 | 422.2159 | 405.8346 | 395.6553 | 390.1559
1170.5832 | 1073.5832 | 474.9608 | 417.4717 | 409.1591 | 422.2072 | 405.8816 | 395.6149 | 390.2039
1171.5847 | 1074.5847 | 474.8479 | 417.5199 | 409.253 | 422.2033 | 405.961 | 395.6256 | 390.2399
1172.5861 | 1075.5861 | 474.9407 | 417.569 | 409.3415 | 422.2074 | 406.0364 | 395.5822 | 390.2795
1173.5875 | 1076.5875 | 474.7697 | 417.6477 | 409.4305 | 422.217 | 406.0914 | 395.5735 | 390.3179
1174.589 | 1077.589 | 474.5518 | 417.736 | 409.5167 | 422.2237 | 406.1388 | 395.6062 | 390.3502
1175.5904 | 1078.5904 | 474.3662 | 417.7896 | 409.6179 | 422.2157 | 406.2315 | 395.6864 | 390.3918
1176.5919 | 1079.5919 | 474.1445 | 417.8814 | 409.7004 | 422.2309 | 406.2609 | 395.6741 | 390.4374
1177.5833 | 1080.5833 | 473.9831 | 417.9295 | 409.7863 | 422.2272 | 406.3647 | 395.6713 | 390.4901
1178.5847 | 1081.5847 | 473.8351 | 418.0422 | 409.8612 | 422.2254 | 406.3929 | 395.7025 | 390.5457
1179.5862 | 1082.5862 | 473.8637 | 418.0805 | 409.9565 | 422.2128 | 406.4748 | 395.7509 | 390.5987
1180.5876 | 1083.5876 | 473.9646 | 418.1481 | 410.0369 | 422.205 | 406.5334 | 395.8045 | 390.6461
1181.589 | 1084.589 | 473.8797 | 418.2131 | 410.136 | 422.2051 | 406.5978 | 395.8513 | 390.6933
1182.5905 | 1085.5905 | 473.7611 | 418.2662 | 410.2292 | 422.1934 | 406.6815 | 395.9116 | 390.7538
1183.5819 | 1086.5819 | 473.8501 | 418.365 | 410.3138 | 422.2087 | 406.691 | 395.9216 | 390.7949
1184.5833 | 1087.5833 | 473.8598 | 418.4017 | 410.3953 | 422.1948 | 406.778 | 395.9243 | 390.8592
1185.5848 | 1088.5848 | 474.0789 | 418.4629 | 410.4798 | 422.1899 | 406.8396 | 395.9185 | 390.9176
1186.5862 | 1089.5862 | 474.1966 | 418.5177 | 410.569 | 422.1747 | 406.9199 | 395.8745 | 390.9739
1187.5877 | 1090.5877 | 474.4992 | 418.6058 | 410.6616 | 422.1666 | 406.972 | 395.8255 | 391.0264
1188.5891 | 1091.5891 | 474.6753 | 418.6857 | 410.7695 | 422.1663 | 407.0177 | 395.8353 | 391.0668
1189.5805 | 1092.5805 | 474.6605 | 418.7096 | 410.8871 | 422.1416 | 407.141 | 395.8643 | 391.1119
1190.582 | 1093.582 | 474.6129 | 418.8193 | 410.9826 | 422.1576 | 407.1426 | 395.8985 | 391.1603
1191.5834 | 1094.5834 | 474.6779 | 418.855 | 411.113 | 422.1547 | 407.2607 | 395.9356 | 391.2004
1192.5849 | 1095.5849 | 474.7194 | 418.9457 | 411.2215 | 422.1589 | 407.2672 | 396.0142 | 391.2434
1193.5863 | 1096.5863 | 474.7481 | 418.9684 | 411.3238 | 422.1613 | 407.4016 | 396.0365 | 391.296
1194.5977 | 1097.5977 | 474.7134 | 419.0401 | 411.4268 | 422.1715 | 407.4249 | 396.0291 | 391.3481
1195.5892 | 1098.5892 | 474.6073 | 419.0826 | 411.5143 | 422.1773 | 407.4653 | 396.0752 | 391.4003
1196.5906 | 1099.5906 | 474.6085 | 419.0923 | 411.6079 | 422.187 | 407.6057 | 396.1397 | 391.4603
1197.582 | 1100.582 | 474.7665 | 419.1925 | 411.7075 | 422.2243 | 407.6083 | 396.1651 | 391.5263
1198.5835 | 1101.5835 | 474.7836 | 419.1902 | 411.8048 | 422.2244 | 407.7383 | 396.2932 | 391.592
1199.5849 | 1102.5849 | 474.8038 | 419.2618 | 411.8879 | 422.2619 | 407.7396 | 396.3376 | 391.6602
1200.5864 | 1103.5864 | 474.7992 | 419.2665 | 411.9772 | 422.2731 | 407.8718 | 396.4513 | 391.7181
1201.5878 | 1104.5878 | 474.9476 | 419.3258 | 412.0737 | 422.3115 | 407.8981 | 396.5495 | 391.7822
1202.5892 | 1105.5892 | 475.1302 | 419.3454 | 412.1692 | 422.3252 | 408.0102 | 396.6261 | 391.8431
1203.5907 | 1106.5907 | 475.2035 | 419.3911 | 412.2611 | 422.354 | 408.0824 | 396.7193 | 391.8976
1204.5821 | 1107.5821 | 475.5168 | 419.4198 | 412.3537 | 422.3821 | 408.1577 | 396.7857 | 391.9473
1205.5835 | 1108.5835 | 475.6493 | 419.4548 | 412.4329 | 422.4057 | 408.2461 | 396.8426 | 391.9916
1206.585 | 1109.585 | 475.8185 | 419.5247 | 412.5196 | 422.4412 | 408.277 | 396.8848 | 392.0235
1207.5864 | 1110.5864 | 475.7457 | 419.521 | 412.6142 | 422.4499 | 408.3958 | 396.9853 | 392.0715
1208.5879 | 1111.5879 | 475.8204 | 419.5878 | 412.6917 | 422.4847 | 408.381 | 397.032 | 392.1044
1209.5893 | 1112.5893 | 475.8728 | 419.5903 | 412.7632 | 422.4876 | 408.5308 | 397.0634 | 392.1443
1210.5907 | 1113.5907 | 475.9777 | 419.6633 | 412.8488 | 422.5118 | 408.553 | 397.0712 | 392.1803
1211.5922 | 1114.5922 | 475.9346 | 419.657 | 412.9541 | 422.5113 | 408.6687 | 397.0809 | 392.2081
1212.5836 | 1115.5836 | 475.9974 | 419.7052 | 413.0449 | 422.532 | 408.7177 | 397.0736 | 392.2183
1213.585 | 1116.585 | 476.0388 | 419.7656 | 413.1334 | 422.5555 | 408.7777 | 397.0237 | 392.2263
1214.5865 | 1117.5865 | 475.9285 | 419.7869 | 413.21 | 422.5527 | 408.8916 | 396.9884 | 392.2239
1215.5879 | 1118.5879 | 475.9917 | 419.8444 | 413.2883 | 422.5821 | 408.9178 | 397.0441 | 392.2211
1216.5894 | 1119.5894 | 476.0295 | 419.8595 | 413.372 | 422.5985 | 409.046 | 396.969 | 392.217
1217.5908 | 1120.5908 | 475.8494 | 419.9405 | 413.4436 | 422.6565 | 409.0486 | 396.9766 | 392.2153
1218.5922 | 1121.5922 | 475.6633 | 419.9593 | 413.5363 | 422.6621 | 409.1841 | 397.0213 | 392.208
1219.5837 | 1122.5837 | 475.5847 | 420.0429 | 413.6256 | 422.7 | 409.195 | 396.9415 | 392.2071
1220.5851 | 1123.5851 | 475.5024 | 420.0565 | 413.706 | 422.723 | 409.3124 | 397.0085 | 392.1954
1221.5866 | 1124.5866 | 475.2985 | 420.1173 | 413.7778 | 422.754 | 409.355 | 397.0315 | 392.182
1222.588 | 1125.588 | 475.1501 | 420.1691 | 413.8492 | 422.7973 | 409.423 | 396.9925 | 392.171
1223.5894 | 1126.5894 | 474.9465 | 420.2172 | 413.9295 | 422.817 | 409.5254 | 397.0237 | 392.167
1224.5909 | 1127.5909 | 474.7663 | 420.295 | 414.0137 | 422.8624 | 409.5434 | 397.0955 | 392.1592
1225.5823 | 1128.5823 | 474.4693 | 420.3209 | 414.0996 | 422.8653 | 409.6465 | 397.1299 | 392.1381
1226.5837 | 1129.5837 | 474.4081 | 420.4364 | 414.1732 | 422.8961 | 409.6652 | 397.169 | 392.1336
1227.5852 | 1130.5852 | 474.2572 | 420.4521 | 414.2562 | 422.91 | 409.8072 | 397.2742 | 392.1165
1228.5866 | 1131.5866 | 474.1702 | 420.5318 | 414.3394 | 422.9253 | 409.8458 | 397.3691 | 392.0986
1229.5881 | 1132.5881 | 474.1457 | 420.5842 | 414.4271 | 422.9588 | 409.9506 | 397.4034 | 392.0868
1230.5895 | 1133.5895 | 474.3802 | 420.6569 | 414.4988 | 422.9727 | 409.9891 | 397.3622 | 392.0634
1231.5809 | 1134.5809 | 474.4429 | 420.687 | 414.5819 | 422.9816 | 410.0705 | 397.3196 | 392.0466
1232.5824 | 1135.5824 | 474.633 | 420.7263 | 414.6641 | 422.9998 | 410.1155 | 397.2599 | 392.0402
1233.5838 | 1136.5838 | 474.7129 | 420.7721 | 414.7415 | 423.0124 | 410.1914 | 397.16 | 392.0142
1234.5852 | 1137.5852 | 474.7198 | 420.821 | 414.8403 | 423.0066 | 410.2812 | 397.1639 | 392.0057
1235.5867 | 1138.5867 | 474.8863 | 420.9016 | 414.9102 | 423.0129 | 410.3242 | 397.101 | 391.9853
1236.5881 | 1139.5881 | 474.9072 | 420.9225 | 415.0034 | 423.0016 | 410.4401 | 397.0505 | 391.9712
1237.5896 | 1140.5896 | 474.9034 | 421.0193 | 415.088 | 423.0252 | 410.4602 | 397.074 | 391.9553
1238.591 | 1141.591 | 474.9571 | 421.0463 | 415.1701 | 423.0128 | 410.5881 | 397.0641 | 391.9334
1239.5824 | 1142.5824 | 474.923 | 421.1482 | 415.2378 | 423.0143 | 410.5936 | 397.0603 | 391.9163
1240.5839 | 1143.5839 | 474.8828 | 421.1787 | 415.3331 | 422.9862 | 410.7081 | 397.0478 | 391.9044
1241.5853 | 1144.5853 | 475.0308 | 421.2535 | 415.4023 | 422.9833 | 410.7056 | 397.0408 | 391.8911
1242.5868 | 1145.5868 | 475.1067 | 421.2869 | 415.4799 | 422.9767 | 410.7993 | 397.0574 | 391.867
1243.5882 | 1146.5882 | 475.1372 | 421.3426 | 415.574 | 422.971 | 410.8783 | 397.0945 | 391.8484
1244.5896 | 1147.5896 | 474.9712 | 421.4212 | 415.657 | 422.985 | 410.9101 | 397.1572 | 391.8236
1245.5911 | 1148.5911 | 474.968 | 421.4559 | 415.7467 | 422.9781 | 411.0121 | 397.1683 | 391.8039
1246.5825 | 1149.5825 | 475.0807 | 421.533 | 415.8361 | 423.0002 | 411.0424 | 397.0587 | 391.7854
1247.5839 | 1150.5839 | 475.1271 | 421.5723 | 415.9516 | 423.0301 | 411.11 | 396.9279 | 391.7552
1248.5854 | 1151.5854 | 475.1478 | 421.6374 | 416.0301 | 423.054 | 411.1833 | 396.8294 | 391.7401
1249.5868 | 1152.5868 | 475.019 | 421.6685 | 416.0924 | 423.0626 | 411.2878 | 396.6483 | 391.7137
1250.5883 | 1153.5883 | 474.9098 | 421.7254 | 416.166 | 423.0877 | 411.3461 | 396.4784 | 391.7009
1251.5897 | 1154.5897 | 474.9814 | 421.7795 | 416.2258 | 423.1159 | 411.4052 | 396.3193 | 391.6824
1252.5911 | 1155.5911 | 475.0268 | 421.825 | 416.2869 | 423.1592 | 411.4675 | 396.2563 | 391.6691
1253.5826 | 1156.5826 | 474.8909 | 421.8776 | 416.3578 | 423.1757 | 411.5242 | 396.1063 | 391.6577
1254.594 | 1157.594 | 474.9518 | 421.9243 | 416.4288 | 423.1966 | 411.5835 | 396.0779 | 391.6445
1255.5854 | 1158.5854 | 474.94 | 421.9759 | 416.5041 | 423.2052 | 411.6651 | 396.0789 | 391.6323
1256.5869 | 1159.5869 | 474.5302 | 422.0404 | 416.5733 | 423.2334 | 411.7254 | 396.1381 | 391.6192
1257.5883 | 1160.5883 | 474.2647 | 422.0746 | 416.6444 | 423.2625 | 411.8039 | 396.1961 | 391.5984
1258.5898 | 1161.5898 | 474.1732 | 422.1669 | 416.718 | 423.2863 | 411.8073 | 396.2955 | 391.5742
1259.5912 | 1162.5912 | 474.2347 | 422.2094 | 416.8082 | 423.2854 | 411.8907 | 396.3027 | 391.5535
1260.5826 | 1163.5826 | 474.1404 | 422.2671 | 416.8828 | 423.2782 | 411.9516 | 396.2541 | 391.533
1261.5841 | 1164.5841 | 473.8517 | 422.31 | 416.9573 | 423.2788 | 412.0286 | 396.2212 | 391.5103
1262.5855 | 1165.5855 | 473.8611 | 422.3531 | 417.0347 | 423.3007 | 412.088 | 396.1666 | 391.4923
1263.5869 | 1166.5869 | 473.8604 | 422.4235 | 417.0973 | 423.3313 | 412.1117 | 396.153 | 391.47
1264.5884 | 1167.5884 | 473.8087 | 422.4589 | 417.1804 | 423.3235 | 412.2015 | 396.1314 | 391.4461
1265.5898 | 1168.5898 | 473.5226 | 422.5344 | 417.2491 | 423.3451 | 412.2186 | 396.066 | 391.4176
1266.5913 | 1169.5913 | 473.5647 | 422.5684 | 417.3258 | 423.3611 | 412.3296 | 396.0921 | 391.3887
1267.5827 | 1170.5827 | 473.6096 | 422.6508 | 417.3898 | 423.4055 | 412.3395 | 396.0973 | 391.3604
1268.5841 | 1171.5841 | 473.4984 | 422.6408 | 417.4715 | 423.4194 | 412.4441 | 396.0823 | 391.3216
1269.5856 | 1172.5856 | 473.4798 | 422.6913 | 417.541 | 423.4467 | 412.4843 | 396.0041 | 391.2832
1270.6271 | 1173.6271 | 473.4066 | 422.7161 | 417.6066 | 423.4699 | 412.5384 | 395.9498 | 391.242
1271.5885 | 1174.5885 | 473.3683 | 422.72 | 417.6763 | 423.4853 | 412.6228 | 395.9811 | 391.2
1272.5899 | 1175.5899 | 473.4643 | 422.8124 | 417.756 | 423.5307 | 412.6491 | 395.8935 | 391.1587
1273.5813 | 1176.5813 | 473.6031 | 422.8409 | 417.8325 | 423.5569 | 412.7345 | 395.9309 | 391.1156
1274.5828 | 1177.5828 | 473.8629 | 422.9076 | 417.9141 | 423.5943 | 412.7471 | 395.9271 | 391.0674
1275.5842 | 1178.5842 | 474.0645 | 422.934 | 417.9911 | 423.5906 | 412.8455 | 395.9532 | 391.0252
1276.5856 | 1179.5856 | 474.2522 | 423.0079 | 418.0587 | 423.6199 | 412.8661 | 395.9521 | 390.9918
1277.5871 | 1180.5871 | 474.5227 | 423.0192 | 418.1257 | 423.6289 | 412.9565 | 395.9978 | 390.9581
1278.5885 | 1181.5885 | 474.6401 | 423.0693 | 418.1982 | 423.6485 | 413.0074 | 396.0082 | 390.9252
1279.59 | 1182.59 | 474.5403 | 423.1224 | 418.2509 | 423.707 | 413.036 | 396.052 | 390.8989
1280.5814 | 1183.5814 | 474.3539 | 423.1457 | 418.3253 | 423.7228 | 413.1531 | 396.1251 | 390.8716
1281.5828 | 1184.5828 | 474.0767 | 423.2321 | 418.3787 | 423.7618 | 413.1612 | 396.2216 | 390.8517
1282.5843 | 1185.5843 | 473.9897 | 423.2405 | 418.45 | 423.7809 | 413.2614 | 396.3318 | 390.8395
1283.5857 | 1186.5857 | 473.9286 | 423.3114 | 418.4984 | 423.832 | 413.2683 | 396.4326 | 390.83
1284.5871 | 1187.5871 | 473.8896 | 423.3418 | 418.5751 | 423.8611 | 413.3622 | 396.4216 | 390.8217
1285.5886 | 1188.5886 | 473.7789 | 423.4023 | 418.63 | 423.9072 | 413.3987 | 396.4127 | 390.8164
1286.59 | 1189.59 | 473.8905 | 423.4676 | 418.6855 | 423.9525 | 413.4454 | 396.4665 | 390.8198
1287.5915 | 1190.5915 | 474.179 | 423.519 | 418.7741 | 424.0201 | 413.4927 | 396.446 | 390.8192
1288.5829 | 1191.5829 | 474.4438 | 423.5496 | 418.8374 | 424.0787 | 413.5579 | 396.4684 | 390.8147
1289.5843 | 1192.5843 | 474.5336 | 423.6297 | 418.8998 | 424.1608 | 413.5849 | 396.5319 | 390.8054
1290.5858 | 1193.5858 | 474.5785 | 423.708 | 418.9621 | 424.2404 | 413.6268 | 396.518 | 390.7928
1291.5872 | 1194.5872 | 474.6403 | 423.7528 | 419.0232 | 424.2891 | 413.687 | 396.4753 | 390.7786
1292.5887 | 1195.5887 | 474.378 | 423.8303 | 419.0704 | 424.3497 | 413.6932 | 396.4352 | 390.7631
1293.5901 | 1196.5901 | 474.1497 | 423.859 | 419.1362 | 424.4079 | 413.7834 | 396.3803 | 390.7475
1294.5815 | 1197.5815 | 474.1903 | 423.9478 | 419.1846 | 424.476 | 413.7608 | 396.3616 | 390.7429
1295.583 | 1198.583 | 474.3406 | 423.9987 | 419.2526 | 424.549 | 413.8552 | 396.3955 | 390.7252
1296.5844 | 1199.5844 | 474.3055 | 424.0476 | 419.3023 | 424.6294 | 413.8916 | 396.401 | 390.7271
1297.5858 | 1200.5858 | 474.2529 | 424.106 | 419.3675 | 424.7101 | 413.9426 | 396.3206 | 390.7199
1298.5873 | 1201.5873 | 474.1074 | 424.1884 | 419.4187 | 424.793 | 413.9264 | 396.1728 | 390.7055
1299.5887 | 1202.5887 | 473.9686 | 424.2147 | 419.4828 | 424.8767 | 413.9924 | 396.1632 | 390.7048
1300.5902 | 1203.5902 | 473.7274 | 424.2516 | 419.5423 | 424.9719 | 414.0253 | 396.146 | 390.6941
1301.5916 | 1204.5916 | 473.6123 | 424.3248 | 419.589 | 425.0621 | 414.039 | 395.9858 | 390.6942
1302.583 | 1205.583 | 473.5408 | 424.3711 | 419.6556 | 425.1522 | 414.0781 | 396.0198 | 390.6816
1303.5845 | 1206.5845 | 473.4481 | 424.4262 | 419.7096 | 425.2488 | 414.0868 | 396.0096 | 390.6653
1304.5859 | 1207.5859 | 473.2855 | 424.4437 | 419.7659 | 425.3104 | 414.1729 | 396.0806 | 390.649
1305.5873 | 1208.5873 | 473.2103 | 424.5087 | 419.8371 | 425.3916 | 414.1667 | 396.1547 | 390.6385
1306.5888 | 1209.5888 | 473.1575 | 424.5104 | 419.8903 | 425.4455 | 414.2324 | 396.2267 | 390.6089
1307.5902 | 1210.5902 | 473.1434 | 424.5723 | 419.9641 | 425.5217 | 414.2312 | 396.2327 | 390.5898
1308.5917 | 1211.5917 | 473.2215 | 424.6001 | 420.0324 | 425.5814 | 414.2907 | 396.2255 | 390.5724
1309.5831 | 1212.5831 | 473.4306 | 424.6611 | 420.0946 | 425.658 | 414.3072 | 396.1068 | 390.551
1310.5845 | 1213.5845 | 473.56 | 424.6478 | 420.168 | 425.7329 | 414.3827 | 396.1373 | 390.5242
1311.586 | 1214.586 | 473.7062 | 424.6908 | 420.2219 | 425.8014 | 414.3839 | 396.1576 | 390.5079
1312.5874 | 1215.5874 | 474.1293 | 424.6886 | 420.2821 | 425.8345 | 414.4534 | 396.1112 | 390.4761
1313.5888 | 1216.5888 | 474.3893 | 424.7514 | 420.3312 | 425.884 | 414.4452 | 396.0776 | 390.4566
1314.5903 | 1217.5903 | 474.5001 | 424.7645 | 420.3899 | 425.9287 | 414.5105 | 396.0895 | 390.4316
1315.5817 | 1218.5817 | 474.5871 | 424.8068 | 420.4425 | 425.9757 | 414.5404 | 396.1575 | 390.4234
1316.5832 | 1219.5832 | 474.5729 | 424.8407 | 420.4771 | 426.0053 | 414.5777 | 396.2223 | 390.4085
1317.5846 | 1220.5846 | 474.6687 | 424.8539 | 420.5346 | 426.0388 | 414.6131 | 396.2971 | 390.3999
1318.586 | 1221.586 | 474.7642 | 424.892 | 420.5681 | 426.0638 | 414.6629 | 396.3851 | 390.3914
1319.5875 | 1222.5875 | 474.7498 | 424.9428 | 420.6075 | 426.1162 | 414.6922 | 396.4542 | 390.4001
1320.5889 | 1223.5889 | 474.7338 | 424.9975 | 420.6566 | 426.1761 | 414.719 | 396.5732 | 390.4004
1321.5904 | 1224.5904 | 474.7441 | 425.0321 | 420.7088 | 426.2163 | 414.7888 | 396.669 | 390.3931 | Time of first failure
1322.5818 | 1225.5818 | 474.6387 | 425.0502 | 420.7533 | 426.2574 | 414.8381 | 396.8007 | 390.3918 | 1225 | 0
1323.5832 | 1226.5832 | 474.5632 | 425.0917 | 420.8003 | 426.274 | 414.8808 | 396.9009 | 390.3804 | 1225 | 900
1324.5847 | 1227.5847 | 474.3981 | 425.1322 | 420.8356 | 426.3373 | 414.8953 | 396.8606 | 390.3624
1325.5861 | 1228.5861 | 474.2414 | 425.1315 | 420.8912 | 426.4078 | 414.9774 | 396.9511 | 390.3529
1326.5875 | 1229.5875 | 474.2662 | 425.1986 | 420.9363 | 426.5078 | 414.9856 | 396.9787 | 390.3434
1327.589 | 1230.589 | 474.2893 | 425.1887 | 420.966 | 426.5784 | 415.0527 | 397.0306 | 390.3425
1328.5904 | 1231.5904 | 474.3877 | 425.2569 | 421.0113 | 426.6462 | 415.0536 | 396.9943 | 390.3364
1329.5919 | 1232.5919 | 474.4155 | 425.2511 | 421.0402 | 426.6571 | 415.1608 | 396.8772 | 390.3356
1330.5833 | 1233.5833 | 474.294 | 425.3047 | 421.0955 | 426.7163 | 415.1522 | 396.9048 | 390.3406
1331.5847 | 1234.5847 | 474.2043 | 425.3101 | 421.14 | 426.762 | 415.2148 | 396.8467 | 390.3489
1332.5862 | 1235.5862 | 474.2089 | 425.315 | 421.197 | 426.8279 | 415.2782 | 396.8942 | 390.3616
1333.5876 | 1236.5876 | 474.2639 | 425.3234 | 421.2588 | 426.8753 | 415.3229 | 396.9369 | 390.3721
1334.589 | 1237.589 | 474.4775 | 425.3027 | 421.312 | 426.9773 | 415.4331 | 397.0057 | 390.3764
1335.5805 | 1238.5805 | 474.496 | 425.3318 | 421.364 | 427.0894 | 415.4311 | 397.1371 | 390.3864
1336.5919 | 1239.5919 | 474.6354 | 425.313 | 421.4343 | 427.1316 | 415.5525 | 397.2532 | 390.3854
1337.5834 | 1240.5834 | 474.8741 | 425.3548 | 421.4905 | 427.1957 | 415.5802 | 397.3115 | 390.396
1338.5848 | 1241.5848 | 475.2516 | 425.3087 | 421.554 | 427.2674 | 415.6985 | 397.3752 | 390.4088
1339.5862 | 1242.5862 | 475.5245 | 425.328 | 421.5992 | 427.3624 | 415.7343 | 397.3331 | 390.4083
1340.5877 | 1243.5877 | 475.6576 | 425.3334 | 421.6558 | 427.4464 | 415.8182 | 397.3531 | 390.4136
1341.5891 | 1244.5891 | 475.6218 | 425.3555 | 421.7178 | 427.5387 | 415.9038 | 397.3734 | 390.4089
1342.5906 | 1245.5906 | 475.5372 | 425.3997 | 421.7703 | 427.622 | 415.9264 | 397.2597 | 390.3985
1343.592 | 1246.592 | 475.2396 | 425.4137 | 421.8289 | 427.695 | 416.0252 | 397.2365 | 390.3777
1344.5834 | 1247.5834 | 475.1242 | 425.4415 | 421.8872 | 427.7662 | 416.0513 | 397.2283 | 390.3679
1345.5849 | 1248.5849 | 474.96 | 425.4425 | 421.9562 | 427.8474 | 416.151 | 397.2772 | 390.3533
1346.5863 | 1249.5863 | 474.9423 | 425.5029 | 421.9968 | 427.9305 | 416.1769 | 397.2908 | 390.3507
1347.5877 | 1250.5877 | 474.9426 | 425.5019 | 422.0512 | 427.9941 | 416.3017 | 397.3258 | 390.3318
1348.5892 | 1251.5892 | 474.6823 | 425.5648 | 422.0891 | 428.1359 | 416.3203 | 397.2802 | 390.3271
1349.5906 | 1252.5906 | 474.5029 | 425.5748 | 422.14 | 428.2261 | 416.4282 | 397.3084 | 390.3255
1350.582 | 1253.582 | 474.4173 | 425.6636 | 422.1873 | 428.3047 | 416.4219 | 397.3051 | 390.3219
1351.5835 | 1254.5835 | 474.2184 | 425.672 | 422.2528 | 428.3676 | 416.5498 | 397.3583 | 390.3257
1352.5849 | 1255.5849 | 474.1583 | 425.7296 | 422.2985 | 428.4367 | 416.6111 | 397.4555 | 390.3367
1353.5864 | 1256.5864 | 474.0626 | 425.76 | 422.34 | 428.5047 | 416.6767 | 397.5512 | 390.3515
1354.5878 | 1257.5878 | 474.0063 | 425.7964 | 422.416 | 428.5498 | 416.7685 | 397.6829 | 390.3699
1355.5892 | 1258.5892 | 473.9305 | 425.8559 | 422.4417 | 428.5913 | 416.7875 | 397.7329 | 390.3795
1356.5807 | 1259.5807 | 473.7559 | 425.8558 | 422.4806 | 428.6776 | 416.8781 | 397.6729 | 390.3928
1357.5821 | 1260.5821 | 473.6295 | 425.943 | 422.5246 | 428.7315 | 416.8825 | 397.7354 | 390.406
1358.5835 | 1261.5835 | 473.5714 | 425.9772 | 422.578 | 428.7707 | 416.9852 | 397.6297 | 390.4228
1359.585 | 1262.585 | 473.5917 | 426.0323 | 422.6258 | 428.8058 | 416.9884 | 397.5562 | 390.4475
1360.5864 | 1263.5864 | 473.6327 | 425.9994 | 422.6879 | 428.8015 | 417.1071 | 397.4662 | 390.4655
1361.5879 | 1264.5879 | 473.6666 | 426.0129 | 422.738 | 428.8316 | 417.1609 | 397.3942 | 390.4924
1362.5893 | 1265.5893 | 473.7196 | 426.0078 | 422.7856 | 428.8546 | 417.2092 | 397.3685 | 390.504
1363.5907 | 1266.5907 | 473.8693 | 425.999 | 422.8295 | 428.8836 | 417.2752 | 397.2034 | 390.5356
1364.5822 | 1267.5822 | 473.9478 | 426.0152 | 422.8798 | 428.9415 | 417.3343 | 397.1397 | 390.5547
1365.5836 | 1268.5836 | 473.9352 | 426.0147 | 422.9343 | 428.9741 | 417.4099 | 397.0803 | 390.5782
1366.5851 | 1269.5851 | 473.7687 | 426.0522 | 422.9824 | 429.1041 | 417.3765 | 396.9895 | 390.6089
1367.5865 | 1270.5865 | 473.7367 | 426.066 | 423.0423 | 429.2114 | 417.4545 | 396.9981 | 390.6388
1368.5879 | 1271.5879 | 473.6985 | 426.1093 | 423.0791 | 429.3346 | 417.4257 | 396.9842 | 390.6756
1369.5894 | 1272.5894 | 473.701 | 426.0959 | 423.1182 | 429.3698 | 417.5009 | 397.1046 | 390.7101
1370.5908 | 1273.5908 | 473.7873 | 426.1501 | 423.1602 | 429.4609 | 417.4483 | 397.1588 | 390.7435
1371.5822 | 1274.5822 | 473.8836 | 426.2252 | 423.2205 | 429.5139 | 417.537 | 397.1469 | 390.7844
1372.5837 | 1275.5837 | 474.064 | 426.2951 | 423.2754 | 429.5797 | 417.5764 | 397.1193 | 390.8287
1373.5851 | 1276.5851 | 474.2349 | 426.2795 | 423.3242 | 429.6646 | 417.6347 | 397.1283 | 390.8715
1374.5866 | 1277.5866 | 474.4828 | 426.2171 | 423.369 | 429.7545 | 417.6851 | 397.1093 | 390.9106
1375.588 | 1278.588 | 474.5475 | 426.2374 | 423.394 | 429.8504 | 417.6798 | 397.157 | 390.9438
1376.5894 | 1279.5894 | 474.6281 | 426.2186 | 423.4569 | 429.8709 | 417.7958 | 397.2016 | 390.9753
1377.5909 | 1280.5909 | 474.7992 | 426.2527 | 423.4956 | 430.0227 | 417.8141 | 397.2339 | 390.9968
1378.5823 | 1281.5823 | 475.1393 | 426.2279 | 423.5584 | 430.083 | 417.8999 | 397.2454 | 390.9997
1379.5837 | 1282.5837 | 475.5285 | 426.2388 | 423.6059 | 430.2316 | 417.8817 | 397.2762 | 391.0122
1380.5852 | 1283.5852 | 475.5904 | 426.1855 | 423.6807 | 430.2882 | 417.9655 | 397.2565 | 391.0133
1381.6467 | 1284.6467 | 475.6016 | 426.2107 | 423.7316 | 430.3659 | 417.959 | 397.3388 | 391.0374
1382.5881 | 1285.5881 | 475.6175 | 426.1618 | 423.7985 | 430.5326 | 418.0191 | 397.4206 | 391.0568
1383.5895 | 1286.5895 | 475.596 | 426.1549 | 423.8793 | 430.666 | 418.0482 | 397.5664 | 391.1043
1384.5909 | 1287.5909 | 475.639 | 426.1472 | 423.9527 | 430.6934 | 418.1371 | 397.8908 | 391.1606
1385.5924 | 1288.5924 | 475.6723 | 426.1551 | 424.0302 | 430.8195 | 418.3066 | 398.2577 | 391.2467
1386.5838 | 1289.5838 | 475.775 | 426.3093 | 424.0998 | 431.0143 | 418.3418 | 398.9674 | 391.3754
1387.5852 | 1290.5852 | 475.8414 | 426.4577 | 424.163 | 431.3755 | 418.4169 | 399.5628 | 391.5537
1388.5867 | 1291.5867 | 476.0098 | 426.7301 | 424.1476 | 431.7607 | 418.3276 | 400.1769 | 391.7975
1389.5881 | 1292.5881 | 476.0509 | 427.1513 | 424.2234 | 432.4477 | 418.3468 | 400.846 | 392.1179
1390.5896 | 1293.5896 | 476.1059 | 427.7318 | 424.3239 | 433.9204 | 418.4482 | 401.4698 | 392.5247
1391.591 | 1294.591 | 475.9842 | 428.5235 | 424.3912 | 436.2116 | 418.871 | 402.2485 | 393.0322
1392.5824 | 1295.5824 | 475.7542 | 429.2404 | 424.5175 | 438.6485 | 419.3913 | 403.0297 | 393.613
1393.5839 | 1296.5839 | 475.6124 | 430.2255 | 424.6322 | 440.7086 | 419.8492 | 403.8693 | 394.2536
1394.5853 | 1297.5853 | 475.6198 | 431.3627 | 424.816 | 442.4178 | 420.2621 | 404.6938 | 394.9627
1395.5868 | 1298.5868 | 475.7233 | 432.5271 | 425.0011 | 444.4319 | 420.6488 | 405.4858 | 395.7264
1396.5882 | 1299.5882 | 475.7629 | 433.7306 | 425.1672 | 447.1252 | 421.1562 | 406.375 | 396.5869
1397.5896 | 1300.5896 | 475.7455 | 435.001 | 425.3268 | 449.8998 | 421.5039 | 407.2084 | 397.5874
1398.5811 | 1301.5811 | 475.5829 | 436.2911 | 425.5515 | 452.2404 | 422.0867 | 408.041 | 398.7099
1399.5825 | 1302.5825 | 475.4453 | 437.6705 | 425.8037 | 454.0868 | 422.8246 | 408.8002 | 399.9031
1400.5839 | 1303.5839 | 475.3287 | 439.0467 | 426.0784 | 455.7112 | 423.7353 | 409.7118 | 401.1554
1401.5854 | 1304.5854 | 475.2534 | 440.4307 | 426.3599 | 457.7463 | 424.605 | 410.5163 | 402.4872
1402.5868 | 1305.5868 | 475.144 | 441.7435 | 426.6004 | 460.1865 | 425.4583 | 411.3267 | 403.9612
1403.5883 | 1306.5883 | 475.0749 | 443.1326 | 426.8877 | 462.597 | 426.3361 | 412.1717 | 405.6589
1404.5897 | 1307.5897 | 474.9322 | 444.2861 | 427.2368 | 464.7054 | 427.3067 | 413.0629 | 407.8548
1405.5911 | 1308.5911 | 474.7374 | 445.4445 | 427.4888 | 466.6044 | 428.2786 | 413.8326 | 410.3354
1406.5826 | 1309.5826 | 474.6113 | 446.4729 | 427.8352 | 468.416 | 429.3638 | 414.6036 | 413.1491
1407.584 | 1310.584 | 474.5456 | 447.512 | 428.2243 | 470.4276 | 430.5343 | 415.4868 | 416.1524
1408.5854 | 1311.5854 | 474.4721 | 448.5046 | 428.7653 | 472.773 | 431.8662 | 416.1869 | 419.3427
1409.5869 | 1312.5869 | 474.4269 | 449.3565 | 429.162 | 474.6531 | 433.1382 | 416.9229 | 422.5988
1410.5883 | 1313.5883 | 474.3892 | 450.2305 | 429.6627 | 476.4448 | 434.1941 | 417.6828 | 426.1411
1411.5898 | 1314.5898 | 474.1924 | 451.0539 | 430.1759 | 478.067 | 435.0873 | 418.2144 | 429.8126
1412.5912 | 1315.5912 | 473.9854 | 451.6072 | 430.6594 | 479.4061 | 436.0669 | 418.9502 | 433.5625
1413.5826 | 1316.5826 | 473.6785 | 452.1409 | 431.1157 | 480.6312 | 437.0422 | 419.7545 | 437.5313
1414.5841 | 1317.5841 | 473.229 | 452.5964 | 431.5916 | 482.0126 | 438.14 | 420.5536 | 441.519
1415.5855 | 1318.5855 | 472.9901 | 453.092 | 432.0868 | 483.5096 | 439.1981 | 421.3068 | 445.5665
1416.587 | 1319.587 | 472.6548 | 453.5333 | 432.6025 | 484.8248 | 440.3006 | 422.198 | 449.5622
1417.5884 | 1320.5884 | 472.284 | 453.7127 | 433.0639 | 486.1048 | 441.3666 | 423.004 | 453.5763
1418.5898 | 1321.5898 | 471.8784 | 453.9638 | 433.5241 | 487.2882 | 442.4372 | 423.8729 | 457.5751
1419.5813 | 1322.5813 | 471.6197 | 454.2602 | 434.0193 | 488.372 | 443.6257 | 424.7371 | 461.5485
1420.5827 | 1323.5827 | 471.2296 | 454.5717 | 434.4904 | 489.3386 | 444.8171 | 425.6781 | 465.5477
1421.5841 | 1324.5841 | 470.86 | 455.0384 | 434.9569 | 490.2852 | 445.9876 | 426.5132 | 469.4276
1422.5856 | 1325.5856 | 470.6939 | 455.6934 | 435.4801 | 491.206 | 447.2243 | 427.4526 | 473.272
1423.587 | 1326.587 | 470.5132 | 456.3554 | 436.0695 | 492.0798 | 448.4304 | 428.2504 | 477.0404
1424.5885 | 1327.5885 | 470.3025 | 457.0247 | 436.7479 | 492.9242 | 449.3842 | 429.1187 | 480.6947
1425.5899 | 1328.5899 | 469.9747 | 457.6274 | 437.4495 | 493.8628 | 450.4146 | 429.9791 | 484.2386
1426.5913 | 1329.5913 | 469.5408 | 458.2945 | 438.0984 | 494.7981 | 451.1899 | 430.778 | 487.6708
1427.5828 | 1330.5828 | 469.3009 | 459.1013 | 438.7922 | 495.7262 | 452.3566 | 431.5659 | 490.9539
1428.5842 | 1331.5842 | 468.9332 | 459.8272 | 439.4956 | 496.6383 | 453.6417 | 432.3329 | 494.1393
1429.5856 | 1332.5856 | 468.5077 | 460.4916 | 440.1519 | 497.5337 | 454.8435 | 433.1028 | 497.2341
1430.5871 | 1333.5871 | 468.1008 | 461.2428 | 440.8913 | 498.4613 | 455.9703 | 433.8853 | 500.0693
1431.5885 | 1334.5885 | 467.7831 | 461.9456 | 441.5844 | 499.363 | 457.2008 | 434.6438 | 503.0681
1432.59 | 1335.59 | 467.4727 | 462.5891 | 442.3536 | 500.1838 | 457.9148 | 435.4087 | 506.1436
1433.5914 | 1336.5914 | 467.0786 | 463.4061 | 443.1395 | 501.0781 | 458.9282 | 436.1783 | 509.179
1434.5928 | 1337.5928 | 466.6367 | 464.2532 | 443.947 | 501.9353 | 460.1175 | 436.9517 | 512.1892
1435.5843 | 1338.5843 | 466.0589 | 465.0122 | 444.6652 | 502.7342 | 460.9509 | 437.6887 | 515.1555
1436.5857 | 1339.5857 | 465.5357 | 465.9513 | 445.4392 | 503.5613 | 461.7618 | 438.5366 | 518.134
1437.5871 | 1340.5871 | 465.0825 | 466.9048 | 446.365 | 504.5049 | 461.8336 | 439.372 | 520.961
1438.5886 | 1341.5886 | 464.6096 | 467.9364 | 447.3333 | 505.4696 | 462.515 | 440.1366 | 523.6626
1439.59 | 1342.59 | 463.9641 | 468.8756 | 448.0883 | 506.4217 | 463.9739 | 440.9189 | 526.1541
1440.5915 | 1343.5915 | 463.5302 | 469.9641 | 448.8925 | 507.4813 | 465.1824 | 441.7701 | 528.4959
1441.5829 | 1344.5829 | 463.1881 | 471.0706 | 449.7222 | 508.5095 | 466.6418 | 442.4751 | 530.7756
1442.5843 | 1345.5843 | 462.824 | 472.2967 | 450.5647 | 509.613 | 468.2916 | 443.2643 | 532.8896
1443.5858 | 1346.5858 | 462.5801 | 473.3762 | 451.2902 | 510.6297 | 470.3903 | 443.9822 | 534.6978
1444.5872 | 1347.5872 | 462.359 | 474.5335 | 452.0362 | 511.5584 | 472.1051 | 444.6853 | 536.5994
1445.5887 | 1348.5887 | 462.0413 | 475.6886 | 453.0288 | 512.4961 | 473.0645 | 445.4768 | 538.4813
1446.5901 | 1349.5901 | 461.5165 | 477.0124 | 454.0417 | 513.3923 | 475.47 | 446.169 | 540.2359
1447.5815 | 1350.5815 | 460.849 | 478.1915 | 455.0711 | 514.1746 | 477.0779 | 446.9005 | 541.4671
1448.583 | 1351.583 | 460.2922 | 479.3319 | 456.0313 | 514.9996 | 477.0435 | 447.508 | 542.7431
1449.5844 | 1352.5844 | 459.6727 | 480.5289 | 457.0755 | 515.7194 | 477.3853 | 448.2679 | 543.6988
1450.5858 | 1353.5858 | 459.1344 | 481.7337 | 458.1576 | 516.3391 | 477.8967 | 449.1033 | 544.9567
1451.6674 | 1354.6674 | 458.4893 | 482.7061 | 459.1403 | 517.0179 | 478.3897 | 449.7571 | 545.0731
1452.5887 | 1355.5887 | 457.8884 | 483.6078 | 459.8781 | 517.5541 | 479.1889 | 450.328 | 543.8763
1453.5902 | 1356.5902 | 457.4098 | 484.4754 | 460.741 | 518.2324 | 480.214 | 450.8922 | 542.9947
1454.5916 | 1357.5916 | 457.0201 | 485.3726 | 461.5697 | 519.0196 | 479.8137 | 451.8233 | 540.8246
1455.583 | 1358.583 | 456.4228 | 486.3131 | 462.3378 | 519.8422 | 480.3045 | 452.4257 | 538.8224
1456.5845 | 1359.5845 | 455.7983 | 487.4137 | 463.0955 | 520.536 | 480.7374 | 452.6601 | 537.9349
1457.5859 | 1360.5859 | 455.1151 | 488.3072 | 463.9142 | 521.2489 | 481.0846 | 453.0249 | 536.9809
1458.5873 | 1361.5873 | 454.451 | 489.3064 | 464.6953 | 522.0585 | 481.5182 | 453.5022 | 534.7586
1459.5888 | 1362.5888 | 454.1346 | 490.3007 | 465.4598 | 522.5655 | 482.0853 | 454.0733 | 534.6605
1460.5902 | 1363.5902 | 453.917 | 491.3247 | 466.2315 | 523.1331 | 482.0811 | 454.6862 | 534.1633
1461.5917 | 1364.5917 | 453.4903 | 492.0588 | 466.9872 | 523.8392 | 482.4454 | 455.2487 | 533.0434
1462.5831 | 1365.5831 | 453.0351 | 492.7467 | 467.842 | 524.2452 | 482.8013 | 455.7379 | 532.6152
1463.5845 | 1366.5845 | 452.6756 | 493.4852 | 468.8221 | 524.6941 | 483.1855 | 456.4028 | 532.1348
1464.586 | 1367.586 | 452.3177 | 494.399 | 469.6651 | 525.1621 | 483.6751 | 456.7297 | 531.9287
1465.5874 | 1368.5874 | 452.0147 | 495.0471 | 470.6058 | 525.499 | 484.2455 | 457.3739 | 530.9428
1466.5889 | 1369.5889 | 451.5676 | 495.7903 | 471.5607 | 525.7458 | 484.4608 | 457.6069 | 531.6065
1467.5803 | 1370.5803 | 451.1527 | 496.683 | 472.4718 | 526.1358 | 484.3348 | 457.9906 | 531.7194
1468.5817 | 1371.5817 | 450.8912 | 497.6012 | 473.4579 | 526.398 | 484.3388 | 458.2528 | 530.8652
1469.5832 | 1372.5832 | 450.7195 | 498.3193 | 474.3849 | 526.7818 | 484.4691 | 458.723 | 530.3067
1470.5846 | 1373.5846 | 450.4738 | 498.906 | 475.3923 | 527.1576 | 485.3821 | 458.8155 | 529.7434
1471.586 | 1374.586 | 450.0859 | 499.554 | 476.4676 | 527.5051 | 485.9737 | 459.2027 | 529.8156
1472.5875 | 1375.5875 | 449.7408 | 500.0582 | 477.6083 | 527.8807 | 486.4602 | 459.2274 | 529.3056
1473.5889 | 1376.5889 | 449.1642 | 500.7734 | 478.7026 | 528.4349 | 486.8684 | 459.4745 | 529.3345
1474.5904 | 1377.5904 | 448.6581 | 501.3326 | 479.8211 | 528.9321 | 487.2952 | 459.792 | 529.7218
1475.5918 | 1378.5918 | 448.0812 | 501.7526 | 480.9272 | 528.8009 | 487.9234 | 459.8347 | 529.2492
1476.5832 | 1379.5832 | 447.5914 | 502.3657 | 481.9756 | 528.6866 | 488.6054 | 459.8227 | 529.2043
1477.5847 | 1380.5847 | 447.1756 | 502.902 | 483.0042 | 528.5037 | 489.1814 | 459.9545 | 528.8732
1478.5861 | 1381.5861 | 446.6955 | 503.4506 | 484.0179 | 528.2348 | 490.4048 | 460.1365 | 529.2343
1479.5875 | 1382.5875 | 446.3931 | 504.0807 | 484.9858 | 527.8946 | 491.1688 | 459.8778 | 529.6896
1480.589 | 1383.589 | 445.9491 | 504.6425 | 485.8961 | 527.6919 | 491.0068 | 460.6304 | 529.6527
1481.5904 | 1384.5904 | 445.6583 | 505.2393 | 486.8254 | 527.3214 | 491.3419 | 460.9421 | 528.9375
1482.5919 | 1385.5919 | 445.2108 | 505.79 | 487.7172 | 527.1637 | 491.3943 | 461.0213 | 529.5972
1483.5833 | 1386.5833 | 444.6795 | 506.3355 | 488.5379 | 526.8794 | 491.7402 | 461.4988 | 529.4482
1484.5847 | 1387.5847 | 444.1933 | 506.866 | 489.3481 | 526.7595 | 491.7171 | 461.5724 | 528.6467
1485.5862 | 1388.5862 | 443.8483 | 507.4053 | 490.0978 | 526.3905 | 492.0324 | 461.7703 | 529.4253
1486.5876 | 1389.5876 | 443.4077 | 508.0257 | 490.8473 | 526.2023 | 491.6289 | 461.5498 | 529.0735
1487.589 | 1390.589 | 442.991 | 508.6796 | 491.5979 | 526.123 | 491.5111 | 461.7544 | 528.5408
1488.5805 | 1391.5805 | 442.4388 | 509.3371 | 492.2861 | 526.0985 | 491.7845 | 461.9028 | 527.68
1489.5819 | 1392.5819 | 441.8684 | 510.0403 | 493.0024 | 526.0765 | 492.1796 | 461.9349 | 528.4787
1490.5834 | 1393.5834 | 441.1769 | 510.7008 | 493.7658 | 526.3204 | 492.2656 | 461.7859 | 528.0639
1491.5848 | 1394.5848 | 440.5475 | 511.3553 | 494.5081 | 526.6868 | 492.5847 | 461.5186 | 527.8103
1492.5862 | 1395.5862 | 440.0579 | 511.9949 | 495.1995 | 526.9561 | 492.883 | 461.7633 | 527.8067
1493.5877 | 1396.5877 | 439.4172 | 512.6609 | 496.0327 | 527.3368 | 493.0347 | 461.8385 | 527.6943
1494.5891 | 1397.5891 | 438.923 | 513.3394 | 496.8436 | 527.5276 | 493.0767 | 462.0646 | 528.1367
1495.5805 | 1398.5805 | 438.4989 | 513.9982 | 497.6447 | 527.7993 | 493.3081 | 462.3098 | 528.7314
1496.592 | 1399.592 | 438.1747 | 514.6174 | 498.4078 | 528.0751 | 493.2471 | 462.2722 | 528.5499
1497.5834 | 1400.5834 | 437.6013 | 515.3005 | 499.1519 | 528.4202 | 493.1501 | 462.0607 | 529.0683
1498.5849 | 1401.5849 | 436.9967 | 516.0199 | 499.9537 | 528.768 | 493.1304 | 461.7273 | 529.313
1499.5863 | 1402.5863 | 436.6045 | 516.7701 | 500.6512 | 529.1822 | 493.1207 | 461.4742 | 529.2749
1500.5877 | 1403.5877 | 436.1866 | 517.469 | 501.4286 | 529.694 | 493.2247 | 461.3966 | 529.8047
1501.5892 | 1404.5892 | 435.7141 | 518.2172 | 502.2393 | 530.2185 | 493.3957 | 461.3141 | 529.3783
1502.5906 | 1405.5906 | 435.1453 | 518.9626 | 503.0188 | 530.8603 | 493.6933 | 461.2258 | 530.5123
1503.582 | 1406.582 | 434.5432 | 519.7382 | 503.7447 | 531.4543 | 493.9304 | 461.2559 | 529.6135
1504.5835 | 1407.5835 | 434.0573 | 520.5114 | 504.4771 | 532.0809 | 494.36 | 461.3115 | 530.1821
1505.5849 | 1408.5849 | 433.6162 | 521.2237 | 505.1845 | 532.6783 | 495.1023 | 460.9439 | 530.0988
1506.5864 | 1409.5864 | 433.0816 | 521.9228 | 505.8788 | 533.3403 | 495.4417 | 460.4645 | 529.5049
1507.5878 | 1410.5878 | 432.5277 | 522.6046 | 506.5849 | 533.9985 | 495.7444 | 460.2934 | 529.7622
1508.5892 | 1411.5892 | 431.9446 | 523.2563 | 507.2578 | 534.692 | 496.0816 | 460.065 | 529.6918
1509.5807 | 1412.5807 | 431.3681 | 523.9175 | 507.9488 | 535.261 | 496.5276 | 459.6123 | 529.4291
1510.5821 | 1413.5821 | 430.9995 | 524.5546 | 508.6303 | 535.8446 | 496.8842 | 459.3586 | 530.3029
1511.5836 | 1414.5836 | 430.5962 | 525.157 | 509.2981 | 536.3156 | 497.3357 | 458.8418 | 529.6601
1512.585 | 1415.585 | 430.1601 | 525.6805 | 509.9682 | 536.7828 | 497.8712 | 458.7277 | 529.0467
1513.5864 | 1416.5864 | 429.5719 | 526.2026 | 510.6006 | 537.2611 | 498.4255 | 458.2128 | 529.0253
1514.5879 | 1417.5879 | 429.0957 | 526.7078 | 511.2535 | 537.7274 | 499.1233 | 458.1888 | 529.3753
1515.5893 | 1418.5893 | 428.6801 | 527.2188 | 511.8955 | 538.1844 | 499.7087 | 457.7992 | 529.7007
1516.5908 | 1419.5908 | 428.2071 | 527.6806 | 512.5703 | 538.6358 | 500.1834 | 457.6514 | 530.5541
1517.5922 | 1420.5922 | 427.5504 | 528.1585 | 513.2335 | 539.0241 | 500.8995 | 457.5576 | 531.1394
1518.5836 | 1421.5836 | 426.9807 | 528.6065 | 513.8849 | 539.3937 | 501.5914 | 457.0592 | 531.7519
1519.5851 | 1422.5851 | 426.5486 | 529.0229 | 514.4952 | 539.8037 | 502.2787 | 456.8199 | 531.6147
1520.5865 | 1423.5865 | 425.9847 | 529.4107 | 515.1218 | 540.1832 | 502.8926 | 456.4681 | 531.6477
1521.5879 | 1424.5879 | 425.3779 | 529.6926 | 515.7195 | 540.5958 | 503.4629 | 456.425 | 532.2868
1522.5894 | 1425.5894 | 424.8814 | 530.0249 | 516.335 | 541.0818 | 503.9965 | 456.0035 | 532.7741
1523.5908 | 1426.5908 | 424.3934 | 530.4312 | 516.9486 | 541.5119 | 504.563 | 455.8797 | 533.1203
1524.5822 | 1427.5822 | 423.9757 | 530.8357 | 517.5252 | 541.9489 | 505.0704 | 455.6115 | 533.7084
1525.5837 | 1428.5837 | 423.6816 | 531.0819 | 518.1162 | 542.457 | 505.5842 | 455.2785 | 534.1724
1526.5851 | 1429.5851 | 423.2294 | 531.3431 | 518.7224 | 542.8884 | 506.0162 | 455.0249 | 534.0571
1527.5866 | 1430.5866 | 422.6621 | 531.6327 | 519.294 | 543.3687 | 506.4366 | 454.8325 | 534.278
1528.588 | 1431.588 | 422.1132 | 531.8351 | 519.7673 | 543.77 | 506.8157 | 454.6796 | 534.4774
1529.5894 | 1432.5894 | 421.6554 | 532.0325 | 520.342 | 544.1744 | 507.2979 | 454.711 | 534.6106
1530.5809 | 1433.5809 | 421.2694 | 532.2045 | 520.815 | 544.6155 | 507.6029 | 454.3564 | 534.9993
1531.5823 | 1434.5823 | 420.8004 | 532.3314 | 521.2819 | 545.1061 | 507.9445 | 453.9749 | 535.1159
1532.5837 | 1435.5837 | 420.2721 | 532.515 | 521.7789 | 545.5848 | 508.3317 | 453.0011 | 535.3799
1533.5852 | 1436.5852 | 419.8368 | 532.7707 | 522.2983 | 546.1072 | 508.7478 | 452.7822 | 535.4424
1534.5866 | 1437.5866 | 419.1851 | 533.0125 | 522.798 | 546.4831 | 509.1998 | 452.3182 | 535.6508
1535.5881 | 1438.5881 | 418.676 | 533.1902 | 523.2564 | 546.872 | 509.6009 | 451.9164 | 535.2895
1536.5895 | 1439.5895 | 418.2393 | 533.3938 | 523.7079 | 547.2179 | 509.9906 | 451.5642 | 535.5318
1537.5809 | 1440.5809 | 417.6542 | 533.5561 | 524.1248 | 547.6018 | 510.3741 | 451.3489 | 535.7785
1538.5824 | 1441.5824 | 417.127 | 533.6727 | 524.573 | 547.9216 | 510.7445 | 451.1257 | 535.881
1539.5838 | 1442.5838 | 416.6974 | 533.8629 | 525.0101 | 548.2477 | 511.1638 | 450.6997 | 536.0684
1540.5853 | 1443.5853 | 416.2749 | 534.0408 | 525.4368 | 548.5202 | 511.5011 | 450.4641 | 536.2946
1541.5867 | 1444.5867 | 415.689 | 534.1847 | 525.8626 | 548.8496 | 511.8863 | 450.1533 | 536.3862
1542.5881 | 1445.5881 | 415.1785 | 534.3694 | 526.29 | 549.1648 | 512.3951 | 449.8498 | 536.1935
1543.5896 | 1446.5896 | 414.7679 | 534.5936 | 526.6915 | 549.5183 | 512.9101 | 449.6027 | 536.5379
1544.591 | 1447.591 | 414.2772 | 534.819 | 527.1484 | 549.8791 | 513.4452 | 449.3211 | 536.9081
1545.5824 | 1448.5824 | 413.86 | 535.0396 | 527.6341 | 550.1972 | 513.975 | 448.7986 | 537.064
1546.5839 | 1449.5839 | 413.3824 | 535.2256 | 528.0713 | 550.4992 | 514.4588 | 448.6727 | 537.2621
1547.5853 | 1450.5853 | 412.9275 | 535.3572 | 528.489 | 550.7782 | 514.9269 | 448.3668 | 537.2925
1548.5868 | 1451.5868 | 412.3301 | 535.4984 | 528.9219 | 550.9936 | 515.3932 | 447.7535 | 537.2588
1549.5882 | 1452.5882 | 411.8335 | 535.6313 | 529.2765 | 551.2278 | 515.7931 | 447.5061 | 536.7959
1550.5896 | 1453.5896 | 411.3699 | 535.6555 | 529.6161 | 551.4078 | 516.2226 | 447.1237 | 536.7115
1551.5811 | 1454.5811 | 410.9255 | 535.6707 | 529.9291 | 551.5339 | 516.6362 | 446.6232 | 536.7186
1552.5825 | 1455.5825 | 410.4377 | 535.6835 | 530.3604 | 551.6897 | 517.0694 | 445.7468 | 536.4845
1553.5839 | 1456.5839 | 409.9121 | 535.6653 | 530.7088 | 551.8088 | 517.4489 | 445.3405 | 536.6685
1554.5854 | 1457.5854 | 409.5187 | 535.6262 | 531.0474 | 551.9496 | 517.865 | 444.5384 | 536.4131
1555.5868 | 1458.5868 | 409.0933 | 535.6112 | 531.4673 | 551.957 | 518.3399 | 444.2538 | 536.2326
1556.5883 | 1459.5883 | 408.759 | 535.6509 | 531.7916 | 552.0215 | 518.7058 | 443.3775 | 536.3698
1557.5897 | 1460.5897 | 408.3176 | 535.6284 | 532.1011 | 552.0171 | 519.0997 | 442.3997 | 536.0469
1558.5911 | 1461.5911 | 407.7467 | 535.6118 | 532.5111 | 552.038 | 519.6292 | 441.5491 | 536.1897
1559.5926 | 1462.5926 | 407.3457 | 535.5683 | 532.8334 | 552.0741 | 520.0809 | 440.7352 | 535.9911
1560.584 | 1463.584 | 407.0404 | 535.617 | 533.0585 | 552.1391 | 520.5579 | 440.1016 | 536.1658
1561.5854 | 1464.5854 | 406.7607 | 535.5692 | 533.341 | 552.171 | 521.0961 | 439.1482 | 536.0014
1562.5869 | 1465.5869 | 406.4137 | 535.4239 | 533.6335 | 552.2141 | 521.5824 | 438.3645 | 536.4067
1563.5883 | 1466.5883 | 406.1731 | 535.3447 | 533.9208 | 552.2112 | 522.1188 | 437.305 | 536.6697
1564.5898 | 1467.5898 | 405.9449 | 535.246 | 534.1991 | 552.1652 | 522.6577 | 436.4303 | 536.4421
1565.5912 | 1468.5912 | 405.4637 | 535.1543 | 534.4788 | 552.1491 | 523.1806 | 435.6654 | 536.4529
1566.5826 | 1469.5826 | 404.9886 | 535.0656 | 534.7644 | 552.1484 | 523.6736 | 435.0111 | 536.7026
1567.5841 | 1470.5841 | 404.5377 | 534.9567 | 535.0152 | 552.1547 | 524.1814 | 434.28 | 536.9882
1568.5855 | 1471.5855 | 404.1245 | 534.8623 | 535.2475 | 552.1935 | 524.6039 | 433.3084 | 537.4785
1569.587 | 1472.587 | 403.6285 | 534.7161 | 535.5059 | 552.2941 | 525.141 | 432.769 | 537.1626
1570.5884 | 1473.5884 | 403.2346 | 534.5199 | 535.8055 | 552.4589 | 525.6649 | 431.8466 | 537.2074
1571.5898 | 1474.5898 | 402.924 | 534.4544 | 536.0333 | 552.5752 | 526.0974 | 431.3218 | 537.1046
1572.5813 | 1475.5813 | 402.4526 | 534.3247 | 536.2591 | 552.7458 | 526.5769 | 430.839 | 537.3628
1573.5827 | 1476.5827 | 401.8884 | 534.208 | 536.4969 | 552.8771 | 526.9776 | 430.0993 | 537.3897
1574.5841 | 1477.5841 | 401.4307 | 534.216 | 536.7154 | 553.0077 | 527.3615 | 429.5938 | 537.3344
1575.5856 | 1478.5856 | 401.0008 | 534.0975 | 536.9848 | 553.1433 | 527.8129 | 429.0721 | 537.3818
1576.587 | 1479.587 | 400.615 | 534.0288 | 537.1675 | 553.2647 | 528.193 | 428.3773 | 537.7425
1577.5885 | 1480.5885 | 400.0306 | 534.0043 | 537.4426 | 553.4637 | 528.6812 | 427.4721 | 537.8121
1578.5899 | 1481.5899 | 399.4641 | 533.9897 | 537.7373 | 553.7789 | 529.2388 | 427.2726 | 537.9928
1579.5813 | 1482.5813 | 398.9318 | 533.9162 | 538.0013 | 554.0959 | 529.6892 | 426.7056 | 538.8741
1580.5828 | 1483.5828 | 398.4726 | 533.9266 | 538.2755 | 554.3792 | 530.125 | 426.0426 | 538.9085
1581.5842 | 1484.5842 | 397.9461 | 533.9158 | 538.4477 | 554.6226 | 530.5648 | 425.4134 | 538.8305
1582.5856 | 1485.5856 | 397.3748 | 533.8572 | 538.7567 | 554.8131 | 531.0396 | 424.9291 | 539.1519
1583.5871 | 1486.5871 | 396.8753 | 533.8117 | 538.8797 | 554.9945 | 531.4241 | 424.5468 | 539.1987
1584.5885 | 1487.5885 | 396.4829 | 533.791 | 539.0122 | 555.1332 | 531.872 | 424.065 | 539.8874
1585.59 | 1488.59 | 395.9957 | 533.8043 | 539.1787 | 555.2545 | 532.3002 | 423.9563 | 540.1775
1586.5914 | 1489.5914 | 395.4981 | 533.701 | 539.3168 | 555.3131 | 532.7534 | 423.5674 | 540.7575
1587.5828 | 1490.5828 | 395.0397 | 533.7698 | 539.4196 | 555.3196 | 533.1525 | 423.1687 | 541.1894
1588.5843 | 1491.5843 | 394.6077 | 533.8623 | 539.5481 | 555.2881 | 533.6164 | 422.7011 | 541.5238
1589.5857 | 1492.5857 | 394.2223 | 534.0427 | 539.6679 | 555.1921 | 534.0244 | 422.1697 | 542.1473
1590.5872 | 1493.5872 | 393.7212 | 534.2477 | 539.7675 | 555.115 | 534.416 | 421.812 | 542.6589
1591.5886 | 1494.5886 | 393.159 | 534.3904 | 539.8715 | 555.0667 | 534.8245 | 421.3464 | 542.9784
1592.59 | 1495.59 | 392.7918 | 534.5854 | 539.943 | 555.0196 | 535.1874 | 420.9834 | 543.2024
1593.5815 | 1496.5815 | 392.4558 | 534.8472 | 540.0073 | 554.9689 | 535.5322 | 420.3607 | 543.1327
1594.5829 | 1497.5829 | 392.0347 | 535.1071 | 540.0674 | 554.9019 | 535.8975 | 419.9286 | 543.8073
1595.5843 | 1498.5843 | 391.5696 | 535.2629 | 540.1301 | 554.8593 | 536.2556 | 419.44 | 544.6233
1596.5858 | 1499.5858 | 391.1099 | 535.4166 | 540.1909 | 554.8563 | 536.595 | 418.8965 | 545.5835
1597.5872 | 1500.5872 | 390.6938 | 535.6758 | 540.278 | 554.847 | 536.959 | 418.4485 | 546.648
1598.5887 | 1501.5887 | 390.1536 | 535.8339 | 540.3825 | 554.8742 | 537.3479 | 417.9939 | 547.6891
1599.5901 | 1502.5901 | 389.7255 | 536.1563 | 540.4504 | 554.8336 | 537.6483 | 417.4467 | 548.7245
1600.5915 | 1503.5915 | 389.3797 | 536.5902 | 540.5786 | 554.8203 | 538.0195 | 417.0836 | 549.7653
1601.583 | 1504.583 | 389.0406 | 536.8747 | 540.5619 | 554.7754 | 538.3537 | 416.4746 | 550.8059
1602.5844 | 1505.5844 | 388.6212 | 537.1346 | 540.5936 | 554.6937 | 538.7047 | 416.039 | 551.925
1603.5858 | 1506.5858 | 388.203 | 537.4839 | 540.6635 | 554.6141 | 539.0262 | 415.5789 | 553.0345
1604.5873 | 1507.5873 | 387.7644 | 537.849 | 540.7588 | 554.5538 | 539.3828 | 415.1904 | 554.1771
1605.5887 | 1508.5887 | 387.3461 | 538.1534 | 540.8019 | 554.5286 | 539.6761 | 414.7613 | 555.1195
1606.5902 | 1509.5902 | 386.9469 | 538.4902 | 540.86 | 554.6553 | 540.0383 | 414.3575 | 556.0626
1607.5916 | 1510.5916 | 386.4309 | 538.8354 | 540.9354 | 554.7716 | 540.3701 | 413.8337 | 557.0849
1608.583 | 1511.583 | 385.9981 | 539.2069 | 540.9941 | 554.869 | 540.6906 | 413.4061 | 557.9824
1609.5845 | 1512.5845 | 385.6738 | 539.5941 | 541.1184 | 554.9438 | 541.0344 | 413.0436 | 558.8391
1610.5859 | 1513.5859 | 385.2865 | 540.0379 | 541.238 | 555.051 | 541.3607 | 412.5351 | 559.6953
1611.5873 | 1514.5873 | 384.8066 | 540.5565 | 541.3634 | 555.1384 | 541.7072 | 412.0269 | 560.5293
1612.5888 | 1515.5888 | 384.3157 | 541.0311 | 541.3984 | 555.2466 | 541.9937 | 411.5078 | 561.2171
1613.5902 | 1516.5902 | 383.6668 | 541.5396 | 541.5735 | 555.3485 | 542.3524 | 410.9302 | 561.8164
1614.5917 | 1517.5917 | 383.0872 | 542.024 | 541.6514 | 555.4508 | 542.6567 | 410.4935 | 562.4689
1615.5831 | 1518.5831 | 382.6887 | 542.5227 | 541.6863 | 555.5584 | 542.9483 | 410.0978 | 562.9503
1616.5845 | 1519.5845 | 382.2152 | 543.0327 | 541.804 | 555.6862 | 543.2166 | 409.5315 | 563.4097
1617.586 | 1520.586 | 381.7559 | 543.5718 | 541.9371 | 555.768 | 543.5109 | 408.9292 | 563.8963
1618.5874 | 1521.5874 | 381.3709 | 544.1044 | 542.0003 | 555.8382 | 543.778 | 408.5647 | 564.3521
1619.5889 | 1522.5889 | 380.8462 | 544.6943 | 542.1342 | 555.8937 | 544.0266 | 408.1396 | 564.7492
1620.5803 | 1523.5803 | 380.1802 | 545.2315 | 542.1186 | 555.9553 | 544.3061 | 407.7591 | 565.0948
1621.5817 | 1524.5817 | 379.6471 | 545.7566 | 542.203 | 556.0475 | 544.5191 | 407.3278 | 565.4045
1622.5832 | 1525.5832 | 379.2974 | 546.2892 | 542.3826 | 556.1101 | 544.8629 | 407.13 | 565.7806
1623.5846 | 1526.5846 | 378.8999 | 546.8679 | 542.5591 | 556.1632 | 545.0966 | 406.7504 | 566.1938
1624.586 | 1527.586 | 378.4824 | 547.5158 | 542.6846 | 556.2073 | 545.3009 | 406.1556 | 566.5047
1625.5875 | 1528.5875 | 378.0412 | 548.0935 | 542.844 | 556.2433 | 545.6494 | 405.8657 | 566.7781
1626.5889 | 1529.5889 | 377.4608 | 548.685 | 542.9975 | 556.2887 | 545.9139 | 405.6117 | 567.1915
1627.5904 | 1530.5904 | 376.879 | 549.277 | 543.134 | 556.2918 | 546.1081 | 405.0846 | 567.4865
1628.5918 | 1531.5918 | 376.3486 | 549.9149 | 543.0932 | 556.2953 | 546.351 | 404.7577 | 567.7502
1629.5832 | 1532.5832 | 375.9226 | 550.5678 | 543.135 | 556.2664 | 546.6081 | 404.3813 | 568.0499
1630.5847 | 1533.5847 | 375.4477 | 551.1651 | 543.2962 | 556.1901 | 546.8378 | 403.8096 | 568.3319
1631.5861 | 1534.5861 | 374.9259 | 551.7765 | 543.5371 | 556.0226 | 547.155 | 403.5375 | 568.653
1632.5875 | 1535.5875 | 374.3774 | 552.3779 | 543.6032 | 555.8635 | 547.4157 | 403.0701 | 568.9145
1633.589 | 1536.589 | 373.8368 | 552.9981 | 543.6918 | 555.663 | 547.6605 | 402.8695 | 569.1515
1634.5904 | 1537.5904 | 373.2899 | 553.611 | 543.88 | 555.4682 | 547.8991 | 402.5277 | 569.3882
1635.5819 | 1538.5819 | 372.7463 | 554.2419 | 544.0332 | 555.2672 | 548.2282 | 402.4463 | 569.5894
1636.5833 | 1539.5833 | 372.2601 | 554.804 | 544.0927 | 554.9981 | 548.5461 | 401.9864 | 569.7707
1637.5847 | 1540.5847 | 371.8765 | 555.387 | 544.2652 | 554.7233 | 548.8024 | 401.7227 | 569.8568
1638.5862 | 1541.5862 | 371.4836 | 555.957 | 544.4715 | 554.4103 | 549.1109 | 401.3718 | 569.8762
1639.5876 | 1542.5876 | 371.0612 | 556.5623 | 544.6645 | 554.0908 | 549.4237 | 401.106 | 569.9269
1640.5891 | 1543.5891 | 370.5034 | 557.2205 | 544.9373 | 553.7867 | 549.7378 | 400.8231 | 569.8371
1641.5905 | 1544.5905 | 370.0846 | 557.8713 | 545.0861 | 553.4131 | 550.0137 | 400.4626 | 569.7607
1642.5919 | 1545.5919 | 369.658 | 558.5573 | 545.2505 | 553.0916 | 550.3775 | 400.1 | 569.6218
1643.5834 | 1546.5834 | 369.1747 | 559.2564 | 545.4227 | 552.6981 | 550.7551 | 399.6227 | 569.4751
1644.5848 | 1547.5848 | 368.6744 | 559.9972 | 545.5993 | 552.2753 | 551.1017 | 399.4189 | 569.2233
1645.5862 | 1548.5862 | 368.0685 | 560.7581 | 545.7521 | 551.9098 | 551.4459 | 399.1883 | 568.9557
1646.5877 | 1549.5877 | 367.5465 | 561.4784 | 545.9509 | 551.6099 | 551.8663 | 398.5892 | 568.6214
1647.5891 | 1550.5891 | 367.05 | 562.1651 | 546.1114 | 551.2181 | 552.2789 | 398.0284 | 568.3824
1648.5906 | 1551.5906 | 366.5625 | 562.9223 | 546.3361 | 550.8847 | 552.7097 | 397.7163 | 568.2772
1649.592 | 1552.592 | 366.1416 | 563.6408 | 546.5429 | 550.574 | 553.1696 | 397.2747 | 568.1474
1650.5834 | 1553.5834 | 365.69 | 564.313 | 546.6888 | 550.267 | 553.6563 | 396.871 | 568.0659
1651.5849 | 1554.5849 | 365.31 | 564.9893 | 546.8369 | 549.9683 | 554.0385 | 396.5211 | 567.9156
1652.5863 | 1555.5863 | 364.9576 | 565.6949 | 546.9857 | 549.7168 | 554.3992 | 396.1293 | 567.7062
1653.5877 | 1556.5877 | 364.573 | 566.3395 | 547.154 | 549.4679 | 554.8791 | 395.4887 | 567.4257
1654.5892 | 1557.5892 | 364.0828 | 567.0123 | 547.3031 | 549.2375 | 555.3291 | 394.8212 | 567.1277
1655.5906 | 1558.5906 | 363.71 | 567.7133 | 547.4874 | 549.0341 | 555.7635 | 394.2176 | 566.7229
1656.582 | 1559.582 | 363.2351 | 568.3806 | 547.6577 | 548.8808 | 556.1615 | 393.5592 | 566.3809
1657.5835 | 1560.5835 | 362.7383 | 569.12 | 547.8756 | 548.7331 | 556.6053 | 393.0884 | 565.9843
1658.5849 | 1561.5849 | 362.2714 | 569.8039 | 548.0205 | 548.6163 | 556.9204 | 392.5855 | 565.7086
1659.5864 | 1562.5864 | 361.844 | 570.5245 | 548.2122 | 548.5081 | 557.2468 | 392.0149 | 565.4171
1660.5878 | 1563.5878 | 361.3703 | 571.2048 | 548.4254 | 548.4055 | 557.5648 | 391.6697 | 565.2588
1661.5892 | 1564.5892 | 360.8511 | 571.8737 | 548.6113 | 548.3356 | 557.8758 | 391.2431 | 565.1012
1662.5807 | 1565.5807 | 360.3156 | 572.5171 | 548.7941 | 548.2953 | 558.152 | 390.8022 | 564.9588
1663.5821 | 1566.5821 | 359.8369 | 573.1065 | 548.9062 | 548.2818 | 558.5008 | 390.5236 | 564.9485
1664.5836 | 1567.5836 | 359.4459 | 573.6941 | 549.0363 | 548.2882 | 558.8495 | 390.3524 | 564.9024
1665.585 | 1568.585 | 359.1201 | 574.3038 | 549.2575 | 548.3011 | 559.1398 | 389.7195 | 564.833
1666.5864 | 1569.5864 | 358.6847 | 574.9024 | 549.4122 | 548.2953 | 559.3131 | 389.1713 | 564.6278
1667.5879 | 1570.5879 | 358.1208 | 575.4848 | 549.6147 | 548.3163 | 559.6146 | 388.6984 | 564.5224
1668.5893 | 1571.5893 | 357.5822 | 576.0904 | 549.8144 | 548.3521 | 559.8207 | 388.1965 | 564.2102
1669.5908 | 1572.5908 | 357.0259 | 576.713 | 550.0458 | 548.3924 | 560.0595 | 387.6892 | 563.899
1670.5922 | 1573.5922 | 356.5348 | 577.3336 | 550.2639 | 548.4194 | 560.2871 | 387.2251 | 563.6029
1671.5836 | 1574.5836 | 356.1623 | 577.9434 | 550.4665 | 548.4407 | 560.5407 | 386.7988 | 563.2387
1672.5851 | 1575.5851 | 355.7268 | 578.5514 | 550.6866 | 548.4796 | 560.6789 | 386.3696 | 562.851
1673.5865 | 1576.5865 | 355.2879 | 579.1532 | 550.8701 | 548.5606 | 560.9442 | 385.9882 | 562.5084
1674.5879 | 1577.5879 | 354.8243 | 579.7209 | 551.0846 | 548.6781 | 561.2068 | 385.4669 | 562.1985
1675.5894 | 1578.5894 | 354.4337 | 580.2884 | 551.2501 | 548.7872 | 561.5125 | 385.1778 | 561.8657
1676.5908 | 1579.5908 | 353.9977 | 580.8751 | 551.3995 | 548.897 | 561.8664 | 384.5745 | 561.5033
1677.5923 | 1580.5923 | 353.6062 | 581.4885 | 551.5928 | 549.0089 | 562.0443 | 384.106 | 561.0908
1678.5837 | 1581.5837 | 353.1726 | 582.1124 | 551.7636 | 549.132 | 562.3473 | 383.6657 | 560.7626
1679.5851 | 1582.5851 | 352.7267 | 582.7493 | 551.9304 | 549.2646 | 562.5579 | 383.204 | 560.3352
1680.5866 | 1583.5866 | 352.2965 | 583.3862 | 552.1187 | 549.3932 | 562.7317 | 382.6818 | 560.1159
1681.6581 | 1584.6581 | 351.7983 | 584.0855 | 552.3075 | 549.5681 | 563.0005 | 382.1678 | 559.7152
1682.5894 | 1585.5894 | 351.3585 | 584.7027 | 552.4994 | 549.7284 | 563.2425 | 381.6517 | 559.2127
1683.5909 | 1586.5909 | 350.9537 | 585.3833 | 552.7001 | 549.8947 | 563.4613 | 381.1783 | 558.7565
1684.5823 | 1587.5823 | 350.5524 | 586.1163 | 552.9206 | 550.0612 | 563.6975 | 380.5476 | 558.0823
1685.5838 | 1588.5838 | 350.1525 | 586.8598 | 553.148 | 550.2365 | 564.0135 | 379.9313 | 557.5914
1686.5852 | 1589.5852 | 349.7459 | 587.6476 | 553.4004 | 550.4446 | 564.3544 | 379.3537 | 557.0071
1687.5866 | 1590.5866 | 349.365 | 588.4125 | 553.6142 | 550.6646 | 564.744 | 378.985 | 556.5294
1688.5881 | 1591.5881 | 348.9307 | 589.125 | 553.7902 | 550.8925 | 565.0393 | 378.3814 | 556.188
1689.5895 | 1592.5895 | 348.5185 | 589.8441 | 553.9966 | 551.1097 | 565.388 | 377.8534 | 555.729
1690.591 | 1593.591 | 348.068 | 590.5187 | 554.2127 | 551.3535 | 565.6963 | 377.3549 | 555.332
1691.5924 | 1594.5924 | 347.5933 | 591.1856 | 554.469 | 551.5917 | 565.9995 | 376.866 | 554.9129
1692.5838 | 1595.5838 | 347.0601 | 591.8366 | 554.7144 | 551.8051 | 566.293 | 376.1894 | 554.6816
1693.5853 | 1596.5853 | 346.6678 | 592.4552 | 554.9535 | 552.0166 | 566.5883 | 375.685 | 554.4848
1694.5867 | 1597.5867 | 346.2316 | 593.0711 | 555.1929 | 552.2393 | 566.9374 | 375.2827 | 554.3891
1695.5881 | 1598.5881 | 345.9735 | 593.6735 | 555.4263 | 552.4456 | 567.3025 | 374.6363 | 554.2661
1696.5896 | 1599.5896 | 345.5583 | 594.2434 | 555.6626 | 552.6817 | 567.6845 | 374.1619 | 554.0947
1697.591 | 1600.591 | 344.9771 | 594.804 | 555.8773 | 552.8912 | 568.0887 | 373.3166 | 553.7616
1698.5824 | 1601.5824 | 344.4755 | 595.3629 | 556.1027 | 553.0922 | 568.4941 | 372.5692 | 553.5916
1699.5839 | 1602.5839 | 344.0515 | 595.8961 | 556.2897 | 553.3211 | 568.8821 | 371.9549 | 553.4363
1700.5853 | 1603.5853 | 343.6869 | 596.5114 | 556.5159 | 553.5356 | 569.2777 | 371.1815 | 553.4122
1701.5868 | 1604.5868 | 343.1531 | 597.1444 | 556.7884 | 553.7683 | 569.6644 | 370.4029 | 553.3967
1702.5882 | 1605.5882 | 342.6926 | 597.7299 | 557.0022 | 553.9967 | 570.0716 | 369.6033 | 553.3153
1703.5896 | 1606.5896 | 342.3876 | 598.3212 | 557.2004 | 554.2091 | 570.4738 | 368.8708 | 553.2667
1704.5811 | 1607.5811 | 342.0148 | 598.8809 | 557.43 | 554.434 | 570.878 | 368.2094 | 553.2751
1705.5825 | 1608.5825 | 341.5555 | 599.4434 | 557.6645 | 554.6858 | 571.2744 | 367.5163 | 553.2885
1706.5839 | 1609.5839 | 341.0404 | 600.0147 | 557.8969 | 554.9513 | 571.6879 | 366.884 | 553.3318
1707.5854 | 1610.5854 | 340.5734 | 600.5889 | 558.1521 | 555.2083 | 572.1007 | 366.1096 | 553.4138
1708.5868 | 1611.5868 | 340.0987 | 601.1768 | 558.3832 | 555.4768 | 572.5138 | 365.4787 | 553.4195
1709.5883 | 1612.5883 | 339.6938 | 601.7563 | 558.6125 | 555.7457 | 572.9278 | 364.9166 | 553.4478
1710.5897 | 1613.5897 | 339.2762 | 602.3221 | 558.8096 | 556.0153 | 573.3123 | 364.151 | 553.4411
1711.5911 | 1614.5911 | 338.8075 | 602.8864 | 559.0539 | 556.2768 | 573.7445 | 363.5695 | 553.5643
1712.5926 | 1615.5926 | 338.4171 | 603.4042 | 559.2705 | 556.5524 | 574.1549 | 362.9273 | 553.6501
1713.584 | 1616.584 | 338.0081 | 603.9634 | 559.5321 | 556.7997 | 574.579 | 362.3698 | 553.6959
1714.5855 | 1617.5855 | 337.6642 | 604.4625 | 559.8061 | 557.0952 | 574.9812 | 361.827 | 553.685
1715.5869 | 1618.5869 | 337.3656 | 604.9641 | 560.0756 | 557.3235 | 575.3882 | 361.1714 | 553.6336
1716.5883 | 1619.5883 | 337.131 | 605.4217 | 560.3057 | 557.615 | 575.774 | 360.6298 | 553.5034
1717.5898 | 1620.5898 | 336.8592 | 605.8761 | 560.584 | 557.8708 | 576.1643 | 360.0032 | 553.3869
1718.5912 | 1621.5912 | 336.4451 | 606.3542 | 560.793 | 558.1412 | 576.5459 | 359.4553 | 553.3784
1719.5826 | 1622.5826 | 336.0196 | 606.865 | 561.0807 | 558.4008 | 576.9333 | 358.8274 | 553.333
1720.5841 | 1623.5841 | 335.7311 | 607.3875 | 561.3659 | 558.6943 | 577.3386 | 358.1779 | 553.3664
1721.5855 | 1624.5855 | 335.3309 | 607.9205 | 561.6564 | 558.9586 | 577.7306 | 357.5944 | 553.3046
1722.587 | 1625.587 | 334.8854 | 608.4949 | 561.9504 | 559.2385 | 578.1187 | 357.0954 | 553.1676
1723.5884 | 1626.5884 | 334.4558 | 609.077 | 562.1971 | 559.5592 | 578.5054 | 356.4791 | 553.1254
1724.5898 | 1627.5898 | 333.9999 | 609.706 | 562.4423 | 559.8797 | 578.8882 | 355.9002 | 553.047
1725.5813 | 1628.5813 | 333.4968 | 610.3032 | 562.6978 | 560.1642 | 579.2828 | 355.2993 | 552.8765
1726.5827 | 1629.5827 | 333.0181 | 610.8354 | 562.9338 | 560.434 | 579.6708 | 354.7611 | 552.7735
1727.5841 | 1630.5841 | 332.4919 | 611.2903 | 563.1872 | 560.6991 | 580.0363 | 354.1546 | 552.7604
1728.5856 | 1631.5856 | 332.013 | 611.6639 | 563.4539 | 560.9686 | 580.4029 | 353.6075 | 552.8224
1729.587 | 1632.587 | 331.5941 | 611.9883 | 563.6897 | 561.2324 | 580.7645 | 352.9171 | 552.8275
1730.5885 | 1633.5885 | 331.122 | 612.2951 | 563.9425 | 561.4789 | 581.1177 | 352.1833 | 552.6895
1731.5899 | 1634.5899 | 330.6991 | 612.6346 | 564.1788 | 561.7607 | 581.4997 | 351.5825 | 552.7237
1732.5913 | 1635.5913 | 330.3518 | 612.966 | 564.436 | 562.0476 | 581.8824 | 350.9033 | 552.7242
1733.5828 | 1636.5828 | 329.9479 | 613.2935 | 564.6904 | 562.3618 | 582.2509 | 350.2902 | 552.5874
1734.5942 | 1637.5942 | 329.5689 | 613.604 | 564.9804 | 562.6764 | 582.615 | 349.8207 | 552.4295
1735.5856 | 1638.5856 | 329.1575 | 613.9327 | 565.1946 | 563.0192 | 583.0382 | 349.2416 | 552.2608
1736.5871 | 1639.5871 | 328.7358 | 614.2317 | 565.4276 | 563.3463 | 583.4741 | 348.5793 | 552.1263
1737.5885 | 1640.5885 | 328.2555 | 614.4979 | 565.7012 | 563.6935 | 583.9201 | 348.1171 | 552.0156
1738.59 | 1641.59 | 327.8379 | 614.7857 | 565.9575 | 564.0484 | 584.3711 | 347.512 | 551.9229
1739.5914 | 1642.5914 | 327.4307 | 615.0772 | 566.2367 | 564.3975 | 584.8272 | 346.9572 | 551.8662
1740.5928 | 1643.5928 | 327.1164 | 615.368 | 566.4726 | 564.7166 | 585.2712 | 346.5053 | 551.8192
1741.5843 | 1644.5843 | 326.656 | 615.6347 | 566.6932 | 565.0066 | 585.7017 | 345.9648 | 551.8289
1742.5857 | 1645.5857 | 326.1647 | 615.9053 | 566.893 | 565.3103 | 586.1148 | 345.6213 | 551.8494
1743.5872 | 1646.5872 | 325.8445 | 616.1542 | 567.0788 | 565.6362 | 586.531 | 345.1209 | 551.8767
1744.5886 | 1647.5886 | 325.4868 | 616.3895 | 567.3173 | 565.9655 | 586.9134 | 344.6883 | 552.0314
1745.59 | 1648.59 | 325.084 | 616.5747 | 567.6331 | 566.279 | 587.2933 | 344.1619 | 552.0655
1746.5815 | 1649.5815 | 324.7606 | 616.7404 | 567.8477 | 566.5957 | 587.6884 | 343.7287 | 552.1935
1747.5829 | 1650.5829 | 324.3243 | 616.9 | 568.0855 | 566.9154 | 588.046 | 343.2954 | 552.2577
1748.5843 | 1651.5843 | 323.9395 | 617.0421 | 568.316 | 567.2124 | 588.3932 | 342.791 | 552.4628
1749.5858 | 1652.5858 | 323.5426 | 617.2055 | 568.5867 | 567.5136 | 588.7715 | 342.3871 | 552.6735
1750.5872 | 1653.5872 | 323.1323 | 617.3567 | 568.8224 | 567.8037 | 589.1405 | 341.929 | 552.7769
1751.5887 | 1654.5887 | 322.6471 | 617.455 | 569.0817 | 568.0865 | 589.5181 | 341.4949 | 552.6718
1752.5901 | 1655.5901 | 322.2431 | 617.5224 | 569.3368 | 568.3843 | 589.8659 | 340.9957 | 552.6179
1753.5915 | 1656.5915 | 321.9466 | 617.5914 | 569.5736 | 568.6713 | 590.2226 | 340.5262 | 552.6922
1754.583 | 1657.583 | 321.6346 | 617.6901 | 569.8271 | 568.955 | 590.5564 | 340.0516 | 552.7983
1755.5844 | 1658.5844 | 321.2257 | 617.7782 | 570.0506 | 569.2469 | 590.9212 | 339.5972 | 552.8782
1756.5858 | 1659.5858 | 320.8416 | 617.8833 | 570.2975 | 569.5283 | 591.2454 | 339.0757 | 552.9214
1757.5873 | 1660.5873 | 320.4037 | 617.9819 | 570.5472 | 569.8179 | 591.5913 | 338.6964 | 552.8951
1758.5887 | 1661.5887 | 320.0271 | 618.1207 | 570.8005 | 570.0967 | 591.9322 | 338.2988 | 552.9647
1759.5902 | 1662.5902 | 319.6193 | 618.258 | 571.0232 | 570.3852 | 592.3058 | 337.8351 | 553.0551
1760.5916 | 1663.5916 | 319.2433 | 618.4188 | 571.2817 | 570.6724 | 592.6627 | 337.4487 | 553.1689
1761.583 | 1664.583 | 318.863 | 618.6058 | 571.5285 | 570.9783 | 593.0176 | 336.9983 | 553.2715
1762.5845 | 1665.5845 | 318.5285 | 618.8291 | 571.6991 | 571.3017 | 593.4182 | 336.5573 | 553.3804
1763.5859 | 1666.5859 | 318.2217 | 619.0557 | 571.9385 | 571.5765 | 593.7803 | 336.0952 | 553.5747
1764.5874 | 1667.5874 | 317.7929 | 619.2851 | 572.1772 | 571.8859 | 594.1577 | 335.6389 | 553.7895
1765.5888 | 1668.5888 | 317.3914 | 619.4675 | 572.3629 | 572.1659 | 594.54 | 335.1437 | 554.0315
1766.5902 | 1669.5902 | 317.0462 | 619.6274 | 572.5497 | 572.4622 | 594.9279 | 334.6902 | 554.1855
1767.5817 | 1670.5817 | 316.6716 | 619.7156 | 572.8107 | 572.7538 | 595.3012 | 334.2088 | 554.3933
1768.5831 | 1671.5831 | 316.297 | 619.7637 | 573.0668 | 573.0199 | 595.6436 | 333.6467 | 554.5851
1769.5845 | 1672.5845 | 315.9341 | 619.7911 | 573.3029 | 573.264 | 595.9828 | 333.1558 | 554.8006
1770.586 | 1673.586 | 315.5338 | 619.9068 | 573.5925 | 573.5077 | 596.2733 | 332.5844 | 555.0865
1771.5874 | 1674.5874 | 315.1154 | 620.0501 | 573.881 | 573.7553 | 596.5422 | 332.0876 | 555.3739
1772.5889 | 1675.5889 | 314.7324 | 620.2484 | 574.1624 | 574.0025 | 596.7902 | 331.5635 | 555.5163
1773.5903 | 1676.5903 | 314.4134 | 620.4221 | 574.4348 | 574.2264 | 597.0204 | 331.0945 | 555.5321
1774.5917 | 1677.5917 | 314.1576 | 620.5445 | 574.6919 | 574.4418 | 597.2361 | 330.6172 | 555.5545
1775.5832 | 1678.5832 | 313.7965 | 620.5973 | 574.9027 | 574.6764 | 597.4836 | 330.1116 | 555.7026
1776.5846 | 1679.5846 | 313.3372 | 620.6368 | 575.1107 | 574.9193 | 597.7536 | 329.6709 | 555.7922
1777.586 | 1680.586 | 312.9659 | 620.6784 | 575.271 | 575.1706 | 598.0449 | 329.1543 | 555.9343
1778.5875 | 1681.5875 | 312.5746 | 620.7482 | 575.4638 | 575.4121 | 598.3785 | 328.6869 | 555.9909
1779.5889 | 1682.5889 | 312.298 | 620.8097 | 575.6462 | 575.6745 | 598.6708 | 328.2144 | 555.9449
1780.5904 | 1683.5904 | 311.91 | 620.8249 | 575.9095 | 575.92 | 598.9598 | 327.761 | 555.8556
1781.5918 | 1684.5918 | 311.5671 | 620.8081 | 576.0409 | 576.1637 | 599.2643 | 327.3555 | 555.9274
1782.5832 | 1685.5832 | 311.2627 | 620.854 | 576.223 | 576.4049 | 599.5743 | 326.9794 | 555.9328
1783.5847 | 1686.5847 | 310.9227 | 620.9073 | 576.4306 | 576.6459 | 599.8985 | 326.6074 | 555.9187
1784.5861 | 1687.5861 | 310.546 | 620.9863 | 576.6639 | 576.9017 | 600.242 | 326.1921 | 555.9153
1785.5875 | 1688.5875 | 310.1906 | 621.0605 | 576.8326 | 577.1585 | 600.5736 | 325.7586 | 555.9879
1786.589 | 1689.589 | 309.8723 | 621.1755 | 577.0141 | 577.4195 | 600.9464 | 325.2085 | 556.0587
1787.5904 | 1690.5904 | 309.5317 | 621.2255 | 577.2055 | 577.6727 | 601.3162 | 324.6799 | 556.1532
1788.5819 | 1691.5819 | 309.1637 | 621.2541 | 577.4124 | 577.9162 | 601.667 | 324.1075 | 556.2049
1789.5833 | 1692.5833 | 308.7606 | 621.291 | 577.6412 | 578.157 | 601.9999 | 323.5887 | 556.2542
1790.5847 | 1693.5847 | 308.4399 | 621.3125 | 577.8161 | 578.3956 | 602.3501 | 323.0512 | 556.2948
1791.5862 | 1694.5862 | 308.1298 | 621.3421 | 578.0432 | 578.6361 | 602.7007 | 322.5652 | 556.3494
1792.5876 | 1695.5876 | 307.7804 | 621.3623 | 578.21 | 578.8817 | 603.0183 | 322.0246 | 556.4317
1793.5891 | 1696.5891 | 307.4123 | 621.4254 | 578.3316 | 579.1216 | 603.3267 | 321.5536 | 556.5838
1794.5905 | 1697.5905 | 307.0773 | 621.5553 | 578.5587 | 579.37 | 603.6035 | 320.9609 | 556.7859
1795.5919 | 1698.5919 | 306.7491 | 621.6627 | 578.7038 | 579.6091 | 603.8671 | 320.378 | 556.8984
1796.5834 | 1699.5834 | 306.3445 | 621.7951 | 578.8906 | 579.8271 | 604.1022 | 319.9263 | 557.0318
1797.5848 | 1700.5848 | 305.8954 | 621.9642 | 579.0811 | 580.0436 | 604.3324 | 319.3654 | 557.1416
1798.5862 | 1701.5862 | 305.4404 | 622.1142 | 579.2419 | 580.2586 | 604.5932 | 318.8277 | 557.3098
1799.5877 | 1702.5877 | 305.1185 | 622.2189 | 579.4151 | 580.4981 | 604.8257 | 318.3756 | 557.3983
1800.5891 | 1703.5891 | 304.8316 | 622.2771 | 579.5638 | 580.7315 | 605.1096 | 317.8786 | 557.5023
1801.5906 | 1704.5906 | 304.4754 | 622.3919 | 579.7085 | 580.9559 | 605.4295 | 317.3717 | 557.6562
1802.592 | 1705.592 | 304.1068 | 622.5765 | 579.8735 | 581.1781 | 605.7647 | 316.8109 | 557.7506
1803.5834 | 1706.5834 | 303.6782 | 622.8245 | 580.0513 | 581.3937 | 606.0866 | 316.3085 | 557.8615
1804.5849 | 1707.5849 | 303.2441 | 623.0297 | 580.2042 | 581.6268 | 606.3639 | 315.8469 | 557.9321
1805.5863 | 1708.5863 | 302.8675 | 623.1684 | 580.3878 | 581.8557 | 606.6512 | 315.4916 | 558.1142
1806.5877 | 1709.5877 | 302.5116 | 623.2781 | 580.5676 | 582.1061 | 606.9522 | 315.0252 | 558.1896
1807.5892 | 1710.5892 | 302.0892 | 623.3513 | 580.7289 | 582.3527 | 607.282 | 314.6363 | 558.1855
1808.5906 | 1711.5906 | 301.598 | 623.4377 | 580.8673 | 582.609 | 607.6465 | 314.2126 | 558.2771
1809.5821 | 1712.5821 | 301.1931 | 623.5134 | 581.0366 | 582.8406 | 607.9671 | 313.73 | 558.403
1810.5835 | 1713.5835 | 300.8527 | 623.559 | 581.1273 | 583.0561 | 608.2436 | 313.2558 | 558.4603
1811.5849 | 1714.5849 | 300.4229 | 623.6079 | 581.2753 | 583.2558 | 608.5012 | 312.9997 | 558.4051
1812.7266 | 1715.7266 | 299.9539 | 623.6497 | 581.4674 | 583.4827 | 608.7535 | 312.6473 | 558.2384
1813.5878 | 1716.5878 | 299.6845 | 623.6578 | 581.575 | 583.6333 | 608.9627 | 312.3269 | 558.1205
1814.5893 | 1717.5893 | 299.4336 | 623.6906 | 581.7019 | 583.8279 | 609.2176 | 311.9325 | 558.0815
1815.5907 | 1718.5907 | 299.0343 | 623.7359 | 581.8238 | 584.0197 | 609.4181 | 311.6085 | 558.1901
1816.5921 | 1719.5921 | 298.6436 | 623.8142 | 582.0206 | 584.2018 | 609.6097 | 311.1152 | 558.3585
1817.5836 | 1720.5836 | 298.308 | 623.8633 | 582.1374 | 584.3798 | 609.832 | 310.5637 | 558.6092
1818.585 | 1721.585 | 297.9968 | 623.9388 | 582.2739 | 584.5598 | 610.0499 | 310.112 | 558.7453
1819.5864 | 1722.5864 | 297.6888 | 624.0185 | 582.3969 | 584.7688 | 610.2811 | 309.6172 | 558.857
1820.5879 | 1723.5879 | 297.4167 | 624.1238 | 582.5553 | 584.9789 | 610.4907 | 309.1486 | 558.961
1821.5893 | 1724.5893 | 297.2011 | 624.1939 | 582.7156 | 585.1935 | 610.6974 | 308.7634 | 559.1321
1822.5908 | 1725.5908 | 296.9198 | 624.2368 | 582.8074 | 585.3958 | 610.9345 | 308.2325 | 559.2668
1823.5922 | 1726.5922 | 296.5906 | 624.2871 | 582.9322 | 585.5932 | 611.159 | 307.7487 | 559.3661
1824.5836 | 1727.5836 | 296.1701 | 624.3549 | 583.0358 | 585.7804 | 611.3699 | 307.2604 | 559.5755
1825.5851 | 1728.5851 | 295.7102 | 624.4251 | 583.1141 | 585.9718 | 611.6019 | 306.8077 | 559.5999
1826.5865 | 1729.5865 | 295.2883 | 624.4864 | 583.2362 | 586.1505 | 611.8153 | 306.4166 | 559.589
1827.5879 | 1730.5879 | 294.9723 | 624.5047 | 583.3609 | 586.3146 | 612.012 | 305.9799 | 559.5808
1828.5894 | 1731.5894 | 294.6352 | 624.5601 | 583.4833 | 586.4834 | 612.2066 | 305.5329 | 559.559
1829.5908 | 1732.5908 | 294.386 | 624.586 | 583.6354 | 586.6678 | 612.4076 | 305.2355 | 559.6024
1830.5822 | 1733.5822 | 294.0722 | 624.5852 | 583.7164 | 586.8481 | 612.5857 | 304.7817 | 559.6448
1831.5837 | 1734.5837 | 293.6601 | 624.642 | 583.8196 | 587.0329 | 612.7952 | 304.3768 | 559.7383
1832.5851 | 1735.5851 | 293.2439 | 624.7432 | 583.9079 | 587.2418 | 613.0169 | 303.9558 | 559.822
1833.5866 | 1736.5866 | 292.8474 | 624.9051 | 584.0636 | 587.4255 | 613.2252 | 303.5545 | 559.8325
1834.588 | 1737.588 | 292.4243 | 624.9923 | 584.178 | 587.6141 | 613.4562 | 303.1767 | 559.8456
1835.5894 | 1738.5894 | 291.9904 | 625.0768 | 584.2956 | 587.8238 | 613.6922 | 302.8114 | 559.909
1836.5909 | 1739.5909 | 291.5956 | 625.1727 | 584.4436 | 588.0135 | 613.9382 | 302.3318 | 559.929
1837.5823 | 1740.5823 | 291.3513 | 625.2603 | 584.5778 | 588.2005 | 614.2026 | 301.9399 | 560.0179
1838.5838 | 1741.5838 | 291.1468 | 625.2818 | 584.6484 | 588.401 | 614.4566 | 301.4713 | 560.0807
1839.5852 | 1742.5852 | 290.853 | 625.3352 | 584.7667 | 588.6059 | 614.7276 | 301.02 | 560.1121
1840.5866 | 1743.5866 | 290.551 | 625.4024 | 584.8927 | 588.798 | 614.9584 | 300.506 | 560.1578
1841.5881 | 1744.5881 | 290.2496 | 625.5177 | 585.0385 | 588.9804 | 615.161 | 300.0264 | 560.206
1842.5895 | 1745.5895 | 289.979 | 625.665 | 585.1869 | 589.1701 | 615.397 | 299.5448 | 560.2787
1843.591 | 1746.591 | 289.7692 | 625.7976 | 585.3255 | 589.3693 | 615.6146 | 299.0613 | 560.3119
1844.5924 | 1747.5924 | 289.5353 | 625.9223 | 585.4516 | 589.6021 | 615.8541 | 298.5338 | 560.3434
1845.5838 | 1748.5838 | 289.2357 | 626.0444 | 585.5887 | 589.795 | 616.0309 | 297.9897 | 560.3951
1846.5853 | 1749.5853 | 288.8403 | 626.2066 | 585.7192 | 589.9464 | 616.2035 | 297.4914 | 560.4641
1847.5867 | 1750.5867 | 288.4371 | 626.3518 | 585.8626 | 590.0787 | 616.3819 | 297.0517 | 560.5677
1848.5881 | 1751.5881 | 288.133 | 626.4233 | 585.9552 | 590.2311 | 616.5888 | 296.6126 | 560.6908
1849.5896 | 1752.5896 | 287.8384 | 626.4636 | 586.07 | 590.3558 | 616.7781 | 296.1532 | 560.7392
1850.591 | 1753.591 | 287.5317 | 626.5082 | 586.2246 | 590.4717 | 616.9329 | 295.6824 | 560.8234
1851.5824 | 1754.5824 | 287.1602 | 626.4709 | 586.3237 | 590.5842 | 617.0644 | 295.143 | 560.8763
1852.5839 | 1755.5839 | 286.7533 | 626.4453 | 586.4429 | 590.688 | 617.1798 | 294.6471 | 560.8657
1853.5853 | 1756.5853 | 286.3747 | 626.3871 | 586.5405 | 590.8132 | 617.3008 | 294.0713 | 560.8898
1854.5868 | 1757.5868 | 286.0213 | 626.31 | 586.608 | 590.9278 | 617.3923 | 293.4986 | 560.914
1855.5882 | 1758.5882 | 285.7463 | 626.2075 | 586.6784 | 591.0356 | 617.5006 | 292.9634 | 560.829
1856.5896 | 1759.5896 | 285.5258 | 626.119 | 586.7579 | 591.1335 | 617.5666 | 292.4588 | 560.8352
1857.5911 | 1760.5911 | 285.3245 | 626.1051 | 586.8426 | 591.2035 | 617.6185 | 291.9729 | 560.7504
1858.5825 | 1761.5825 | 285.1149 | 626.1853 | 586.9352 | 591.271 | 617.7125 | 291.5203 | 560.5281
1859.584 | 1762.584 | 284.8787 | 626.3332 | 587.0214 | 591.3622 | 617.7941 | 291.1223 | 560.3517
1860.5854 | 1763.5854 | 284.6652 | 626.4987 | 587.0743 | 591.4765 | 617.8799 | 290.7612 | 560.2141
1861.5868 | 1764.5868 | 284.4392 | 626.7249 | 587.1787 | 591.5827 | 617.962 | 290.3982 | 560.1005
1862.5883 | 1765.5883 | 284.207 | 626.897 | 587.3053 | 591.6975 | 618.0861 | 290.0036 | 560.052
1863.5897 | 1766.5897 | 283.9428 | 626.9998 | 587.4072 | 591.8109 | 618.19 | 289.61 | 560.0061
1864.5912 | 1767.5912 | 283.666 | 627.1011 | 587.5052 | 591.9652 | 618.3492 | 289.1743 | 560.0133
1865.5926 | 1768.5926 | 283.3739 | 627.2409 | 587.6205 | 592.1097 | 618.5313 | 288.7849 | 560.0461
1866.584 | 1769.584 | 282.9726 | 627.3513 | 587.7097 | 592.2356 | 618.7041 | 288.4009 | 560.1069
1867.5855 | 1770.5855 | 282.536 | 627.5403 | 587.8341 | 592.354 | 618.9115 | 287.9816 | 560.1025
1868.5869 | 1771.5869 | 282.181 | 627.7022 | 587.9407 | 592.4713 | 619.1217 | 287.5372 | 560.0991
1869.5883 | 1772.5883 | 281.8314 | 627.8776 | 588.0551 | 592.583 | 619.3379 | 287.0995 | 560.0977
1870.5898 | 1773.5898 | 281.454 | 628.032 | 588.1298 | 592.7398 | 619.5711 | 286.6475 | 560.1696
1871.5812 | 1774.5812 | 280.9991 | 628.1991 | 588.2387 | 592.8956 | 619.8272 | 286.2274 | 560.2107
1872.5826 | 1775.5826 | 280.645 | 628.3272 | 588.3083 | 593.0102 | 620.0837 | 285.8103 | 560.3195
1873.5841 | 1776.5841 | 280.2084 | 628.42 | 588.3888 | 593.1067 | 620.3198 | 285.4126 | 560.3671
1874.5855 | 1777.5855 | 279.8175 | 628.4839 | 588.4494 | 593.1776 | 620.5763 | 285.055 | 560.3752
1875.587 | 1778.587 | 279.4643 | 628.4798 | 588.5132 | 593.2456 | 620.7812 | 284.7238 | 560.38
1876.5884 | 1779.5884 | 279.1264 | 628.3671 | 588.5805 | 593.3121 | 620.9654 | 284.4242 | 560.3758
1877.5898 | 1780.5898 | 278.7153 | 628.2081 | 588.638 | 593.3681 | 621.1499 | 284.1319 | 560.3331
1878.5813 | 1781.5813 | 278.3077 | 628.0412 | 588.7096 | 593.422 | 621.397 | 283.8643 | 560.258
1879.5827 | 1782.5827 | 277.9493 | 627.8522 | 588.7532 | 593.5129 | 621.6763 | 283.5502 | 560.1326
1880.5841 | 1783.5841 | 277.5766 | 627.6882 | 588.8357 | 593.5888 | 621.9113 | 283.2377 | 560.0243
1881.5856 | 1784.5856 | 277.2721 | 627.5468 | 588.8959 | 593.648 | 622.0975 | 282.9226 | 559.9338
1882.587 | 1785.587 | 277.0141 | 627.4319 | 588.9663 | 593.6958 | 622.2594 | 282.6191 | 559.8027
1883.5885 | 1786.5885 | 276.8051 | 627.3181 | 589.0353 | 593.7146 | 622.387 | 282.3386 | 559.6172
1884.5899 | 1787.5899 | 276.4941 | 627.1994 | 589.0966 | 593.7739 | 622.4939 | 282.064 | 559.4009
1885.5913 | 1788.5913 | 276.121 | 627.0659 | 589.1543 | 593.8552 | 622.5773 | 281.7558 | 559.1918
1886.5828 | 1789.5828 | 275.8076 | 626.9051 | 589.2178 | 593.9023 | 622.6013 | 281.4528 | 559.0399
1887.5842 | 1790.5842 | 275.4594 | 626.7536 | 589.2474 | 593.9436 | 622.6598 | 281.1267 | 558.8681
1888.5857 | 1791.5857 | 275.1566 | 626.6438 | 589.3166 | 593.9853 | 622.7765 | 280.7978 | 558.7246
1889.5871 | 1792.5871 | 274.7666 | 626.574 | 589.3706 | 594.0496 | 622.9401 | 280.4856 | 558.5368
1890.5885 | 1793.5885 | 274.3543 | 626.5022 | 589.4098 | 594.1032 | 623.0738 | 280.2019 | 558.3218
1891.59 | 1794.59 | 274.0157 | 626.4811 | 589.4562 | 594.1359 | 623.2402 | 279.9313 | 558.1658
1892.5914 | 1795.5914 | 273.7334 | 626.5151 | 589.4971 | 594.1698 | 623.4431 | 279.6789 | 558.0184
1893.5828 | 1796.5828 | 273.4361 | 626.5975 | 589.5341 | 594.193 | 623.5455 | 279.4443 | 557.8516
1894.5843 | 1797.5843 | 273.13 | 626.686 | 589.5732 | 594.2529 | 623.6569 | 279.2013 | 557.6409
1895.5857 | 1798.5857 | 272.7871 | 626.7262 | 589.63 | 594.3737 | 623.7809 | 278.9842 | 557.2935
1896.5872 | 1799.5872 | 272.5031 | 626.7619 | 589.6699 | 594.4986 | 623.9097 | 278.7607 | 556.995
1897.5886 | 1800.5886 | 272.2022 | 626.8064 | 589.712 | 594.6304 | 624.0432 | 278.5398 | 556.8162
1898.59 | 1801.59 | 271.9049 | 626.8179 | 589.7394 | 594.7485 | 624.1876 | 278.3048 | 556.639
1899.5815 | 1802.5815 | 271.5336 | 626.8038 | 589.7697 | 594.8509 | 624.3262 | 278.0808 | 556.5272
1900.5829 | 1803.5829 | 271.1573 | 626.8044 | 589.7958 | 594.9369 | 624.4878 | 277.8611 | 556.4664
1901.5843 | 1804.5843 | 270.7905 | 626.8157 | 589.8204 | 595.0583 | 624.6406 | 277.6104 | 556.4155
1902.5858 | 1805.5858 | 270.4639 | 626.8153 | 589.8437 | 595.1926 | 624.7467 | 277.3502 | 556.4254
1903.5872 | 1806.5872 | 270.1121 | 626.8221 | 589.8727 | 595.3164 | 624.83 | 277.0818 | 556.61
1904.5887 | 1807.5887 | 269.7787 | 626.8262 | 589.89 | 595.4163 | 624.8562 | 276.8268 | 556.6947
1905.5901 | 1808.5901 | 269.5579 | 626.8176 | 589.9222 | 595.5131 | 624.9154 | 276.5825 | 556.6588
1906.5915 | 1809.5915 | 269.217 | 626.8406 | 589.9431 | 595.5791 | 624.9256 | 276.3271 | 556.739
1907.583 | 1810.583 | 268.8579 | 626.8736 | 589.9699 | 595.5978 | 624.8851 | 276.0241 | 556.8893
1908.5844 | 1811.5844 | 268.5557 | 626.9078 | 589.9906 | 595.6463 | 624.8196 | 275.7221 | 556.8468
1909.5858 | 1812.5858 | 268.2227 | 626.8851 | 590.0201 | 595.7238 | 624.821 | 275.4134 | 556.8866
1910.5873 | 1813.5873 | 267.9454 | 626.7999 | 590.0569 | 595.8082 | 624.8844 | 275.0658 | 556.969
1911.5887 | 1814.5887 | 267.7364 | 626.7277 | 590.0816 | 595.8896 | 624.8986 | 274.7481 | 556.9782
1912.5902 | 1815.5902 | 267.4542 | 626.7431 | 590.119 | 596.027 | 624.9512 | 274.4107 | 556.9662
1913.5816 | 1816.5816 | 267.1828 | 626.8281 | 590.1462 | 596.1415 | 625.0109 | 274.0531 | 556.9494
1914.583 | 1817.583 | 266.9657 | 626.9108 | 590.1668 | 596.2716 | 625.1476 | 273.6981 | 556.9422
1915.5845 | 1818.5845 | 266.8347 | 626.961 | 590.1998 | 596.4588 | 625.3015 | 273.3224 | 556.9532
1916.5859 | 1819.5859 | 266.6268 | 627.0199 | 590.2227 | 596.6021 | 625.4879 | 272.9336 | 557.0141
1917.5874 | 1820.5874 | 266.3402 | 627.0477 | 590.2398 | 596.7126 | 625.6264 | 272.53 | 557.0887
1918.5888 | 1821.5888 | 265.9376 | 627.0388 | 590.2717 | 596.8016 | 625.6531 | 272.1313 | 557.095
1919.5902 | 1822.5902 | 265.6 | 627.0507 | 590.2932 | 596.9001 | 625.7228 | 271.7411 | 557.1086
1920.5817 | 1823.5817 | 265.2991 | 627.0599 | 590.2977 | 597.0069 | 625.7357 | 271.3256 | 557.1498
1921.5831 | 1824.5831 | 264.9342 | 627.0546 | 590.309 | 597.0722 | 625.7978 | 270.9607 | 557.1398
1922.5845 | 1825.5845 | 264.5981 | 627.095 | 590.3156 | 597.14 | 625.838 | 270.5846 | 557.0945
1923.586 | 1826.586 | 264.2246 | 627.1166 | 590.3371 | 597.1791 | 625.8333 | 270.2192 | 556.9646
1924.5874 | 1827.5874 | 263.8614 | 627.1342 | 590.3511 | 597.209 | 625.7376 | 269.8797 | 556.9074
1925.5889 | 1828.5889 | 263.4487 | 627.1505 | 590.368 | 597.2286 | 625.6922 | 269.5337 | 556.8454
1926.5903 | 1829.5903 | 263.0861 | 627.1987 | 590.3707 | 597.2399 | 625.6356 | 269.2118 | 556.8307
1927.5917 | 1830.5917 | 262.7348 | 627.2414 | 590.401 | 597.2378 | 625.5805 | 268.8961 | 556.8271
1928.5832 | 1831.5832 | 262.4371 | 627.2568 | 590.4279 | 597.2726 | 625.5403 | 268.6255 | 556.7862
1929.5846 | 1832.5846 | 262.1204 | 627.2659 | 590.4451 | 597.3279 | 625.5604 | 268.3362 | 556.6725
1930.586 | 1833.586 | 261.7931 | 627.2629 | 590.4721 | 597.3812 | 625.5769 | 268.0658 | 556.675
1931.5875 | 1834.5875 | 261.5877 | 627.2228 | 590.4858 | 597.4105 | 625.5443 | 267.8026 | 556.6285
1932.5889 | 1835.5889 | 261.2902 | 627.2021 | 590.4985 | 597.4684 | 625.4575 | 267.5527 | 556.6038
1933.5904 | 1836.5904 | 260.9391 | 627.2089 | 590.5064 | 597.5241 | 625.442 | 267.2879 | 556.5475
1934.5918 | 1837.5918 | 260.6381 | 627.2077 | 590.5198 | 597.5899 | 625.4111 | 267.0205 | 556.4056
1935.5832 | 1838.5832 | 260.2949 | 627.2224 | 590.5417 | 597.6102 | 625.3737 | 266.7093 | 556.2996
1936.5847 | 1839.5847 | 259.9867 | 627.1828 | 590.5446 | 597.6869 | 625.3469 | 266.4165 | 556.2486
1937.5861 | 1840.5861 | 259.6844 | 627.0771 | 590.5678 | 597.7521 | 625.3127 | 266.0589 | 556.1709
1938.5876 | 1841.5876 | 259.417 | 626.9871 | 590.5876 | 597.8206 | 625.299 | 265.6969 | 556.0336
1939.589 | 1842.589 | 259.027 | 626.9422 | 590.5872 | 597.8812 | 625.3146 | 265.3633 | 555.8029
1940.5904 | 1843.5904 | 258.7542 | 626.9248 | 590.59 | 597.9334 | 625.3368 | 264.972 | 555.5444
1941.5819 | 1844.5819 | 258.522 | 626.8965 | 590.5815 | 597.9904 | 625.3274 | 264.6203 | 555.4516
1942.5833 | 1845.5833 | 258.2575 | 626.8766 | 590.5712 | 598.0643 | 625.3026 | 264.2913 | 555.3748
1943.5847 | 1846.5847 | 257.9726 | 626.8809 | 590.5721 | 598.1229 | 625.3233 | 263.965 | 555.2481
1944.5862 | 1847.5862 | 257.7465 | 626.9208 | 590.5603 | 598.208 | 625.3443 | 263.6633 | 555.1681
1945.5876 | 1848.5876 | 257.4968 | 626.9703 | 590.5605 | 598.2782 | 625.3787 | 263.3525 | 554.9968
1946.5891 | 1849.5891 | 257.2111 | 626.9226 | 590.5634 | 598.3704 | 625.3933 | 263.0593 | 554.9186
1947.5905 | 1850.5905 | 256.9139 | 626.8023 | 590.5498 | 598.529 | 625.3762 | 262.7664 | 554.8959
1948.5919 | 1851.5919 | 256.6547 | 626.7073 | 590.5461 | 598.7307 | 625.2772 | 262.438 | 554.9222
1949.5834 | 1852.5834 | 256.3656 | 626.646 | 590.5359 | 598.8605 | 625.1098 | 262.1328 | 555.042
1950.5848 | 1853.5848 | 256.0321 | 626.5989 | 590.5226 | 598.9983 | 624.9855 | 261.801 | 555.1121
1951.5862 | 1854.5862 | 255.6826 | 626.5357 | 590.5053 | 599.0667 | 624.8987 | 261.4813 | 555.1555
1952.5877 | 1855.5877 | 255.3464 | 626.4747 | 590.4853 | 599.099 | 624.797 | 261.1463 | 555.1774
1953.5891 | 1856.5891 | 255.0186 | 626.465 | 590.4851 | 599.0765 | 624.6535 | 260.8029 | 555.1852
1954.5805 | 1857.5805 | 254.7563 | 626.4636 | 590.4573 | 599.0438 | 624.5874 | 260.4484 | 555.1827
1955.582 | 1858.582 | 254.5638 | 626.4915 | 590.4675 | 599.0482 | 624.5972 | 260.0649 | 555.11
1956.5834 | 1859.5834 | 254.396 | 626.5781 | 590.4611 | 599.1113 | 624.6758 | 259.6646 | 554.9792
1957.5849 | 1860.5849 | 254.163 | 626.6978 | 590.4622 | 599.1647 | 624.7671 | 259.2451 | 554.9113
1958.5863 | 1861.5863 | 253.8986 | 626.826 | 590.4571 | 599.2214 | 624.755 | 258.8047 | 554.9073
1959.5877 | 1862.5877 | 253.6766 | 626.9593 | 590.4565 | 599.3187 | 624.7992 | 258.3349 | 554.9316
1960.5892 | 1863.5892 | 253.3861 | 627.0181 | 590.4465 | 599.3986 | 624.7772 | 257.8188 | 554.9563
1961.5906 | 1864.5906 | 253.0617 | 627.0272 | 590.4323 | 599.468 | 624.6574 | 257.3235 | 554.9676
1962.5821 | 1865.5821 | 252.7149 | 627.0386 | 590.4118 | 599.5853 | 624.5602 | 256.8251 | 555.0268
1963.5835 | 1866.5835 | 252.445 | 627.025 | 590.3933 | 599.6966 | 624.5235 | 256.3205 | 555.0204
1964.5849 | 1867.5849 | 252.1919 | 627.0024 | 590.3731 | 599.7143 | 624.4474 | 255.8364 | 554.9933
1965.5864 | 1868.5864 | 251.8803 | 627.0133 | 590.3662 | 599.698 | 624.3184 | 255.3994 | 554.9032
1966.5878 | 1869.5878 | 251.5485 | 627.0002 | 590.3532 | 599.6684 | 624.1877 | 254.9634 | 554.745
1967.5893 | 1870.5893 | 251.2859 | 626.864 | 590.3351 | 599.6878 | 624.025 | 254.5728 | 554.5236
1968.5907 | 1871.5907 | 251.0705 | 626.7032 | 590.3203 | 599.7476 | 623.929 | 254.2146 | 554.3163
1969.5921 | 1872.5921 | 250.8567 | 626.656 | 590.3165 | 599.7762 | 623.8488 | 253.8756 | 554.1412
1970.5836 | 1873.5836 | 250.629 | 626.7301 | 590.3205 | 599.8797 | 623.902 | 253.5446 | 554.0021
1971.585 | 1874.585 | 250.3846 | 626.8655 | 590.31 | 599.9502 | 623.9789 | 253.1816 | 553.9156
1972.5864 | 1875.5864 | 250.2385 | 626.9888 | 590.3077 | 600.0278 | 624.0526 | 252.8069 | 553.8603
1973.5879 | 1876.5879 | 250.0803 | 627.0743 | 590.294 | 600.0596 | 624.0794 | 252.4485 | 553.8614
1974.5893 | 1877.5893 | 249.8935 | 627.1479 | 590.2898 | 600.0502 | 623.9445 | 252.0731 | 553.851
1975.5908 | 1878.5908 | 249.6703 | 627.1925 | 590.2849 | 600.0647 | 623.7676 | 251.7043 | 553.7888
1976.5922 | 1879.5922 | 249.3809 | 627.2296 | 590.2782 | 600.0893 | 623.6298 | 251.3239 | 553.6857
1977.5836 | 1880.5836 | 249.0667 | 627.2904 | 590.2692 | 600.111 | 623.4676 | 250.9217 | 553.6366
1978.5851 | 1881.5851 | 248.8018 | 627.3319 | 590.2544 | 600.1552 | 623.355 | 250.5566 | 553.5983
1979.5865 | 1882.5865 | 248.5905 | 627.3745 | 590.2558 | 600.2462 | 623.4281 | 250.2495 | 553.5673
1980.5879 | 1883.5879 | 248.3195 | 627.4506 | 590.2425 | 600.2981 | 623.4447 | 249.8992 | 553.5131
1981.6695 | 1884.6695 | 248.0298 | 627.5359 | 590.2355 | 600.3165 | 623.2895 | 249.5128 | 553.5475
1982.5908 | 1885.5908 | 247.7864 | 627.5839 | 590.2457 | 600.3403 | 623.2253 | 249.3269 | 553.5946
1983.5823 | 1886.5823 | 247.5087 | 627.639 | 590.2318 | 600.433 | 623.1516 | 248.9808 | 553.5559
1984.5837 | 1887.5837 | 247.1938 | 627.5818 | 590.24 | 600.4518 | 623.0285 | 248.6575 | 553.5533
1985.5851 | 1888.5851 | 246.8672 | 627.4551 | 590.2219 | 600.4998 | 622.9402 | 248.3473 | 553.5323
1986.5866 | 1889.5866 | 246.5161 | 627.2882 | 590.218 | 600.6393 | 622.937 | 248.0934 | 553.5537
1987.588 | 1890.588 | 246.2488 | 627.1661 | 590.1827 | 600.7044 | 622.8532 | 247.678 | 553.6214
1988.5895 | 1891.5895 | 245.9868 | 627.1173 | 590.1731 | 600.7553 | 622.8264 | 247.2591 | 553.6107
1989.5909 | 1892.5909 | 245.6764 | 627.0879 | 590.1704 | 600.7872 | 622.98 | 246.9848 | 553.3487
1990.5823 | 1893.5823 | 245.3148 | 627.0529 | 590.1602 | 600.8356 | 623.1182 | 246.7616 | 553.0351
1991.5838 | 1894.5838 | 244.939 | 626.9838 | 590.125 | 600.882 | 623.03 | 246.2217 | 552.8542
1992.5952 | 1895.5952 | 244.6026 | 626.7992 | 590.0937 | 600.8241 | 623.0029 | 245.8454 | 552.7872
1993.5866 | 1896.5866 | 244.2686 | 626.6051 | 590.0576 | 600.7974 | 622.9655 | 245.6275 | 552.7171
1994.5881 | 1897.5881 | 243.9264 | 626.4389 | 590.0379 | 600.8832 | 622.9334 | 245.4635 | 552.5809
1995.5895 | 1898.5895 | 243.6114 | 626.3305 | 590.0018 | 600.9245 | 622.7862 | 245.2126 | 552.3561
1996.5809 | 1899.5809 | 243.2528 | 626.1876 | 589.9823 | 600.9783 | 622.8417 | 245.0646 | 552.1676
1997.5824 | 1900.5824 | 242.9513 | 626.0644 | 589.9377 | 601.0555 | 622.8993 | 244.8886 | 551.9383
1998.5838 | 1901.5838 | 242.6212 | 626.0029 | 589.9089 | 601.0639 | 623.001 | 244.6758 | 551.6587
1999.5853 | 1902.5853 | 242.2896 | 625.9861 | 589.8684 | 601.0745 | 623.0885 | 244.4986 | 551.3243
2000.5867 | 1903.5867 | 241.971 | 626.0883 | 589.8198 | 601.1681 | 623.2219 | 244.3757 | 551.0751
2001.5881 | 1904.5881 | 241.671 | 626.1307 | 589.7898 | 601.2601 | 623.3381 | 244.228 | 550.7448
2002.5896 | 1905.5896 | 241.5001 | 626.1307 | 589.7503 | 601.3543 | 623.3174 | 243.9723 | 550.4433
2003.591 | 1906.591 | 241.3486 | 626.1247 | 589.6981 | 601.366 | 623.2691 | 243.8278 | 550.1758
2004.5824 | 1907.5824 | 241.1907 | 626.1876 | 589.6631 | 601.365 | 623.2065 | 243.6318 | 549.9392
2005.5839 | 1908.5839 | 240.8984 | 626.2947 | 589.6076 | 601.3301 | 623.0701 | 243.3522 | 549.8482
2006.5853 | 1909.5853 | 240.6413 | 626.297 | 589.5552 | 601.3384 | 622.927 | 243.093 | 549.75
2007.5868 | 1910.5868 | 240.446 | 626.2382 | 589.5037 | 601.3457 | 622.8529 | 242.8423 | 549.6539
2008.5882 | 1911.5882 | 240.2454 | 626.1363 | 589.4576 | 601.4352 | 622.7879 | 242.5593 | 549.5973
2009.5896 | 1912.5896 | 240.0684 | 626.0429 | 589.3915 | 601.5466 | 622.7653 | 242.2596 | 549.5061
2010.5911 | 1913.5911 | 239.9005 | 625.9965 | 589.3247 | 601.5959 | 622.7803 | 241.9877 | 549.3589
2011.5825 | 1914.5825 | 239.6408 | 626.04 | 589.2784 | 601.5509 | 622.7514 | 241.6736 | 549.2157
2012.584 | 1915.584 | 239.3425 | 626.1384 | 589.2162 | 601.4882 | 622.7416 | 241.2947 | 549.2393
2013.5854 | 1916.5854 | 239.0297 | 626.3177 | 589.1627 | 601.4093 | 622.7471 | 240.9369 | 549.273
2014.5868 | 1917.5868 | 238.7201 | 626.5247 | 589.1249 | 601.4464 | 622.7654 | 240.6429 | 549.3301
2015.5883 | 1918.5883 | 238.4263 | 626.651 | 589.0791 | 601.5057 | 622.7198 | 240.3208 | 549.3456
2016.5897 | 1919.5897 | 238.1158 | 626.696 | 589.0365 | 601.5509 | 622.7161 | 240.0302 | 549.2752
2017.5912 | 1920.5912 | 237.8667 | 626.7363 | 588.9871 | 601.6223 | 622.7984 | 239.8048 | 549.3102
2018.5926 | 1921.5926 | 237.643 | 626.6931 | 588.9429 | 601.6236 | 622.8065 | 239.5381 | 549.3158
2019.584 | 1922.584 | 237.396 | 626.7043 | 588.8904 | 601.5584 | 622.7947 | 239.2939 | 549.2563
2020.5855 | 1923.5855 | 237.1336 | 626.7524 | 588.8339 | 601.5593 | 622.7648 | 239.0249 | 549.1633
2021.5869 | 1924.5869 | 236.8058 | 626.7703 | 588.7731 | 601.5887 | 622.7018 | 238.7922 | 549.0178
2022.5883 | 1925.5883 | 236.5344 | 626.7007 | 588.7095 | 601.6235 | 622.7934 | 238.5321 | 548.9115
2023.5898 | 1926.5898 | 236.2999 | 626.6909 | 588.6243 | 601.6874 | 623.028 | 238.231 | 548.8479
2024.5912 | 1927.5912 | 236.1099 | 626.6752 | 588.5539 | 601.7462 | 623.2056 | 237.9446 | 548.7267
2025.5826 | 1928.5826 | 235.9385 | 626.6967 | 588.4816 | 601.7741 | 623.2806 | 237.6156 | 548.6315
2026.5841 | 1929.5841 | 235.7075 | 626.6813 | 588.4204 | 601.8207 | 623.3522 | 237.3283 | 548.6108
2027.5855 | 1930.5855 | 235.4146 | 626.6528 | 588.3415 | 601.8147 | 623.4748 | 237.048 | 548.5292
2028.587 | 1931.587 | 235.0628 | 626.6106 | 588.2746 | 601.7656 | 623.6237 | 236.8129 | 548.397
2029.5884 | 1932.5884 | 234.8057 | 626.6542 | 588.193 | 601.7555 | 623.7177 | 236.5574 | 548.2103
2030.5898 | 1933.5898 | 234.5341 | 626.7143 | 588.1198 | 601.7792 | 623.8201 | 236.3174 | 548.01
2031.5913 | 1934.5913 | 234.2528 | 626.7432 | 588.0625 | 601.8154 | 623.8946 | 236.0849 | 547.806
2032.5827 | 1935.5827 | 233.9432 | 626.7652 | 587.9885 | 601.8007 | 623.8485 | 235.8472 | 547.6686
2033.5842 | 1936.5842 | 233.6795 | 626.8147 | 587.922 | 601.8005 | 623.8112 | 235.6134 | 547.4967
2034.5856 | 1937.5856 | 233.465 | 626.7696 | 587.8616 | 601.7876 | 623.765 | 235.3939 | 547.3145
2035.587 | 1938.587 | 233.2716 | 626.6949 | 587.7844 | 601.8605 | 623.6767 | 235.1813 | 547.0479
2036.5885 | 1939.5885 | 233.074 | 626.625 | 587.702 | 601.9115 | 623.6521 | 234.9572 | 546.8228
2037.5899 | 1940.5899 | 232.8327 | 626.6136 | 587.621 | 601.8491 | 623.5647 | 234.7396 | 546.7012
2038.5914 | 1941.5914 | 232.5416 | 626.482 | 587.5342 | 601.7895 | 623.4621 | 234.4797 | 546.6575
2039.5828 | 1942.5828 | 232.3561 | 626.3899 | 587.4601 | 601.8218 | 623.3873 | 234.1814 | 546.5442
2040.5842 | 1943.5842 | 232.1893 | 626.3392 | 587.381 | 601.9585 | 623.29 | 233.8954 | 546.3374
2041.5857 | 1944.5857 | 232.0337 | 626.4054 | 587.314 | 602.0264 | 623.2855 | 233.5667 | 546.051
2042.5871 | 1945.5871 | 231.8349 | 626.4114 | 587.2437 | 602.0817 | 623.2185 | 233.2597 | 545.8216
2043.5885 | 1946.5885 | 231.5987 | 626.4309 | 587.1789 | 602.2562 | 623.2175 | 232.9086 | 545.4685
2044.59 | 1947.59 | 231.4035 | 626.444 | 587.1193 | 602.4622 | 623.2648 | 232.5437 | 545.3336
2045.5814 | 1948.5814 | 231.2019 | 626.3957 | 587.0456 | 602.475 | 623.2819 | 232.1662 | 545.2681
2046.5828 | 1949.5828 | 230.9848 | 626.31 | 586.9871 | 602.4234 | 623.3608 | 231.8058 | 545.2132
2047.5843 | 1950.5843 | 230.7384 | 626.2566 | 586.9164 | 602.4298 | 623.4057 | 231.416 | 545.1872
2048.5857 | 1951.5857 | 230.5251 | 626.2032 | 586.8302 | 602.4584 | 623.4285 | 230.9996 | 545.1121
2049.5872 | 1952.5872 | 230.3007 | 626.114 | 586.749 | 602.5543 | 623.4785 | 230.5886 | 545.1066
2050.5886 | 1953.5886 | 230.0371 | 626.0554 | 586.6559 | 602.5245 | 623.4262 | 230.1867 | 545.0747
2051.59 | 1954.59 | 229.8289 | 625.8896 | 586.5546 | 602.4334 | 623.2598 | 229.7671 | 545.0509
2052.5815 | 1955.5815 | 229.6498 | 625.6842 | 586.4658 | 602.4706 | 623.2672 | 229.3653 | 544.9113
2053.5829 | 1956.5829 | 229.4933 | 625.6124 | 586.3709 | 602.5035 | 623.2012 | 228.9921 | 544.7814
2054.5843 | 1957.5843 | 229.3005 | 625.6816 | 586.3052 | 602.4273 | 623.1062 | 228.6005 | 544.6987
2055.5858 | 1958.5858 | 229.1037 | 625.7244 | 586.2327 | 602.3519 | 622.973 | 228.1811 | 544.5297
2056.5872 | 1959.5872 | 228.8477 | 625.791 | 586.1592 | 602.3429 | 622.8425 | 227.7745 | 544.4192
2057.5887 | 1960.5887 | 228.6377 | 625.7693 | 586.0859 | 602.3534 | 622.821 | 227.3531 | 544.0756
2058.5901 | 1961.5901 | 228.4868 | 625.7294 | 586.0336 | 602.5617 | 622.7155 | 226.9345 | 543.6761
2059.5815 | 1962.5815 | 228.2991 | 625.6377 | 585.9783 | 602.6634 | 622.5125 | 226.5131 | 543.2603
2060.583 | 1963.583 | 227.9951 | 625.5198 | 585.9101 | 602.7857 | 622.4619 | 226.1093 | 542.926
2061.5844 | 1964.5844 | 227.6567 | 625.4601 | 585.8327 | 602.7256 | 622.4404 | 225.6871 | 542.7544
2062.5859 | 1965.5859 | 227.3624 | 625.404 | 585.7441 | 602.4621 | 622.383 | 225.2896 | 542.6411
2063.5873 | 1966.5873 | 227.142 | 625.3714 | 585.6475 | 602.2585 | 622.3052 | 224.9078 | 542.5157
2064.5887 | 1967.5887 | 226.965 | 625.3805 | 585.5389 | 602.2506 | 622.2554 | 224.5497 | 542.4212
2065.5902 | 1968.5902 | 226.6657 | 625.3744 | 585.4374 | 601.9986 | 622.0541 | 224.2324 | 542.2614
2066.5916 | 1969.5916 | 226.3468 | 625.2948 | 585.3112 | 601.7872 | 621.8248 | 223.9174 | 542.1116
2067.5931 | 1970.5931 | 225.9883 | 625.1712 | 585.1879 | 601.7532 | 621.7483 | 223.6535 | 542.0486
2068.5845 | 1971.5845 | 225.6199 | 625.0321 | 585.0708 | 601.5963 | 621.7153 | 223.3919 | 541.9747
2069.5859 | 1972.5859 | 225.3367 | 624.8945 | 584.9671 | 601.4976 | 621.7199 | 223.1665 | 541.8608
2070.5874 | 1973.5874 | 225.0831 | 624.7838 | 584.8418 | 601.3986 | 621.5184 | 222.9552 | 541.7591

## C6-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 145.3223 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38908.4557 | 1 | 0 | 38908.4557 | 1 | 0 | -40 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4563 | 1 | 0 | 38908.4564 | 1 | 0 | 19 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.457 | 1 | 0 | 38908.457 | 1 | 0 | 77.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4577 | 1 | 0 | 38908.4577 | 1 | 0 | 136.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4584 | 1 | 0 | 38908.4584 | 1 | 0 | 195.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4591 | 1 | 0 | 38908.4591 | 1 | 0 | 254 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4597 | 1 | 0 | 38908.4598 | 1 | 0 | 313 | 410 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4604 | 1 | 0 | 38908.4604 | 1 | 0 | 371.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4611 | 1 | 0 | 38908.4611 | 1 | 0 | 430.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4618 | 1 | 0 | 38908.4618 | 1 | 0 | 489.5 | 586.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4625 | 1 | 0 | 38908.4625 | 1 | 0 | 548 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4631 | 1 | 0 | 38908.4632 | 1 | 0 | 606.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4638 | 1 | 0 | 38908.4638 | 1 | 0 | 665.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4645 | 1 | 0 | 38908.4645 | 1 | 0 | 724.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4652 | 1 | 0 | 38908.4652 | 1 | 0 | 783 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4659 | 1 | 0 | 38908.4659 | 1 | 0 | 842 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4666 | 1 | 0 | 38908.4666 | 1 | 0 | 901 | 998 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4672 | 1 | 0 | 38908.4672 | 1 | 0 | 959.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4679 | 1 | 0 | 38908.4679 | 1 | 0 | 1018.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4686 | 1 | 0 | 38908.4686 | 1 | 0 | 1077 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.4693 | 1 | 0 | 38908.4693 | 1 | 0 | 1136 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237938 | 237938 | 237937.9994
38908.47 | 19 | 18 | 38908.47 | 772 | 770 | 1194.5 | 1291.5 | 1.16 | 1.0989 | 47.1306 | 47.0085 | 0.0116 | 0.010989 | 0.47131 | 0.47009 | 0.0006105 | 0.001221 | 240662.9672 | 95734.028 | 13005.1931
38908.4706 | 1072 | 1048 | 38908.4706 | 1074 | 1048 | 1253.5 | 1350.5 | 65.4457 | 63.9805 | 65.5678 | 63.9805 | 0.65446 | 0.6398 | 0.65568 | 0.6398 | 0.014652 | 0.015873 | 14882.329 | 6890.8835 | 24.49
38908.4713 | 1140 | 1114 | 38908.4713 | 1170 | 1147 | 1312.5 | 1409.5 | 69.5971 | 68.0098 | 71.4286 | 70.0244 | 0.69597 | 0.6801 | 0.71429 | 0.70024 | 0.015873 | 0.014042 | 3823.1486 | 17287.5636 | 11.2795
38908.472 | 887 | 844 | 38908.472 | 1067 | 1025 | 1371 | 1468 | 54.1514 | 51.5263 | 65.1404 | 62.5763 | 0.54151 | 0.51526 | 0.6514 | 0.62576 | 0.026252 | 0.025641 | 5213.5716 | 5879.1107 | 75.6539
38908.4727 | 387 | 369 | 38908.4727 | 988 | 910 | 1430 | 1527 | 23.6264 | 22.5275 | 60.3175 | 55.5556 | 0.23626 | 0.22527 | 0.60317 | 0.55556 | 0.010989 | 0.047619 | 65599.5559 | 2466.3648 | 423.0583
38908.4734 | 2187 | 75 | 38908.4734 | 2132 | 77 | 1488.5 | 1585.5 | 133.5165 | 4.5788 | 130.1587 | 4.7009 | 1.3352 | 0.045788 | 1.3016 | 0.047009 | 1.2894 | 1.2546 | 11.4068 | 17.9991 | 24.0762
38908.474 | 1454 | 529 | 38908.4741 | 1289 | 801 | 1547.5 | 1644.5 | 88.7668 | 32.2955 | 78.6935 | 48.9011 | 0.88767 | 0.32295 | 0.78694 | 0.48901 | 0.56471 | 0.29792 | 78.1639 | 203.3237 | 50.3538
38908.4747 | 2191 | 87 | 38908.4747 | 1797 | 63 | 1606.5 | 1703.5 | 133.7607 | 5.3114 | 109.707 | 3.8462 | 1.3376 | 0.053114 | 1.0971 | 0.038462 | 1.2845 | 1.0586 | 9.7531 | 53.6169 | 41.0732
38908.4754 | 2029 | 16 | 38908.4754 | 2195 | 18 | 1665 | 1762 | 123.8706 | 0.9768 | 134.0049 | 1.0989 | 1.2387 | 0.009768 | 1.34 | 0.010989 | 1.2289 | 1.3291 | 19.1675 | 8.8993 | 171.2959
38908.4761 | 1816 | 15 | 38908.4761 | 2012 | 16 | 1724 | 1821 | 110.8669 | 0.91575 | 122.8327 | 0.9768 | 1.1087 | 0.0091575 | 1.2283 | 0.009768 | 1.0995 | 1.2186 | 32.7801 | 18.9185 | 582.6661
38908.4768 | 2364 | 22 | 38908.4768 | 2003 | 19 | 1782.5 | 1879.5 | 144.3223 | 1.3431 | 122.2833 | 1.16 | 1.4432 | 0.013431 | 1.2228 | 0.0116 | 1.4298 | 1.2112 | 0.68599 | 48.0287 | 8.2884
38908.4774 | 1858 | 36 | 38908.4775 | 1961 | 38 | 1841.5 | 1938.5 | 113.431 | 2.1978 | 119.7192 | 2.3199 | 1.1343 | 0.021978 | 1.1972 | 0.023199 | 1.1123 | 1.174 | 31.3302 | 23.2768 | 255.1024
38908.4781 | 1449 | 690 | 38908.4781 | 1431 | 724 | 1900.5 | 1997.5 | 88.4615 | 42.1245 | 87.3626 | 44.2002 | 0.88462 | 0.42125 | 0.87363 | 0.442 | 0.46337 | 0.43162 | 165.2737 | 353.0098 | 27.2603
38908.4788 | 1033 | 903 | 38908.4788 | 992 | 865 | 1959 | 2056 | 63.0647 | 55.1282 | 60.5617 | 52.8083 | 0.63065 | 0.55128 | 0.60562 | 0.52808 | 0.079365 | 0.077534 | 1655.686 | 1857.2206 | 46.6972

## C5-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 146.7875 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38908.4556 | 1 | 0 | 38908.4556 | 1 | 0 | -42.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4563 | 1 | 0 | 38908.4563 | 1 | 0 | 16 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.457 | 1 | 0 | 38908.457 | 1 | 0 | 75 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4577 | 1 | 0 | 38908.4577 | 1 | 0 | 133.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4584 | 1 | 0 | 38908.4584 | 1 | 0 | 192.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.459 | 1 | 0 | 38908.4591 | 1 | 0 | 251.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4597 | 1 | 0 | 38908.4597 | 1 | 0 | 310 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4604 | 1 | 0 | 38908.4604 | 1 | 0 | 369 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4611 | 1 | 1 | 38908.4611 | 1 | 0 | 427.5 | 524.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 577623542.44 | 240338 | 240138.0832
38908.4618 | 1 | 0 | 38908.4618 | 1 | 0 | 486.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4624 | 1 | 0 | 38908.4625 | 1 | 0 | 545 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4631 | 1 | 0 | 38908.4631 | 1 | 0 | 604 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4638 | 1 | 0 | 38908.4638 | 1 | 0 | 663 | 760 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4645 | 1 | 0 | 38908.4645 | 1 | 0 | 721.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4652 | 1 | 0 | 38908.4652 | 1 | 0 | 780.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4658 | 1 | 0 | 38908.4659 | 1 | 0 | 839.5 | 936.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4665 | 1 | 0 | 38908.4665 | 1 | 0 | 898 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4672 | 1 | 0 | 38908.4672 | 1 | 0 | 956.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4679 | 1 | 0 | 38908.4679 | 1 | 0 | 1015.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4686 | 1 | 0 | 38908.4686 | 1 | 0 | 1074.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4692 | 1 | 0 | 38908.4693 | 1 | 0 | 1133 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38908.4699 | 1 | 1 | 38908.4699 | 1 | 0 | 1192 | 1289 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 577623542.44 | 240338 | 240138.0832
38908.4706 | 843 | 820 | 38908.4706 | 849 | 817 | 1250.5 | 1347.5 | 51.4652 | 50.0611 | 51.8315 | 49.8779 | 0.51465 | 0.50061 | 0.51832 | 0.49878 | 0.014042 | 0.019536 | 18446.0582 | 5641.389 | 88.8375
38908.4713 | 1053 | 1048 | 38908.4713 | 1013 | 989 | 1309.5 | 1406.5 | 64.2857 | 63.9805 | 61.8437 | 60.3785 | 0.64286 | 0.6398 | 0.61844 | 0.60379 | 0.0030525 | 0.014652 | 4637.5733 | 4341.3766 | 28.2967
38908.472 | 1122 | 1097 | 38908.472 | 1031 | 993 | 1368.5 | 1465.5 | 68.4982 | 66.9719 | 62.9426 | 60.6227 | 0.68498 | 0.66972 | 0.62943 | 0.60623 | 0.015263 | 0.023199 | 9139.2783 | 10001.3892 | 16.7315
38908.4726 | 1009 | 937 | 38908.4727 | 1144 | 1070 | 1427 | 1524 | 61.5995 | 57.2039 | 69.8413 | 65.3236 | 0.616 | 0.57204 | 0.69841 | 0.65324 | 0.043956 | 0.045177 | 3531.7218 | 2883.956 | 47.2805
38908.4733 | 1807 | 81 | 38908.4733 | 1924 | 82 | 1486 | 1583 | 110.3175 | 4.9451 | 117.4603 | 5.0061 | 1.1032 | 0.049451 | 1.1746 | 0.050061 | 1.0537 | 1.1245 | 41.2286 | 29.236 | 144.2179
38908.474 | 1569 | 614 | 38908.474 | 1193 | 676 | 1544.5 | 1641.5 | 95.7875 | 37.4847 | 72.8327 | 41.2698 | 0.95788 | 0.37485 | 0.72833 | 0.4127 | 0.58303 | 0.31563 | 71.1076 | 279.3311 | 26.5504
38908.4747 | 1746 | 93 | 38908.4747 | 2030 | 95 | 1603.5 | 1700.5 | 106.5934 | 5.6777 | 123.9316 | 5.7998 | 1.0659 | 0.056777 | 1.2393 | 0.057998 | 1.0092 | 1.1813 | 54.1472 | 21.277 | 106.657
38908.4754 | 1882 | 11 | 38908.4754 | 2014 | 12 | 1662.5 | 1759.5 | 114.8962 | 0.67155 | 122.9548 | 0.7326 | 1.149 | 0.0067155 | 1.2295 | 0.007326 | 1.1422 | 1.2222 | 28.7692 | 19.9144 | 772.0531
38908.476 | 1991 | 13 | 38908.4761 | 2388 | 17 | 1721 | 1818 | 121.5507 | 0.79365 | 145.7875 | 1.0379 | 1.2155 | 0.0079365 | 1.4579 | 0.010379 | 1.2076 | 1.4475 | 415.4509 | 0.69204 | 21.1673
38908.4767 | 2144 | 17 | 38908.4767 | 2288 | 20 | 1779.5 | 1876.5 | 130.8913 | 1.0379 | 139.6825 | 1.221 | 1.3089 | 0.010379 | 1.3968 | 0.01221 | 1.2985 | 1.3846 | 14.3375 | 5.4677 | 74.2199
38908.4774 | 2119 | 35 | 38908.4774 | 2361 | 32 | 1838.5 | 1935.5 | 129.3651 | 2.1368 | 144.1392 | 1.9536 | 1.2937 | 0.021368 | 1.4414 | 0.019536 | 1.2723 | 1.4219 | 126.6721 | 1.883 | 13.2217
38908.4781 | 1315 | 750 | 38908.4781 | 1732 | 951 | 1897.5 | 1994.5 | 80.2808 | 45.7875 | 105.7387 | 58.0586 | 0.80281 | 0.45788 | 1.0574 | 0.58059 | 0.34493 | 0.4768 | 9.3402 | 6.7578 | 2.8644
38908.4788 | 1146 | 1096 | 38908.4788 | 1050 | 885 | 1956.5 | 2053.5 | 69.9634 | 66.9109 | 64.1026 | 54.0293 | 0.69963 | 0.66911 | 0.64103 | 0.54029 | 0.030525 | 0.10073 | 649.1851 | 761.9581 | 13.0969

## C5-6
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 141.8425 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38908.4556 | 1 | 0 | 38908.4556 | 1 | 0 | -45.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4563 | 1 | 0 | 38908.4563 | 1 | 0 | 13.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.457 | 1 | 0 | 38908.457 | 1 | 0 | 72 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4576 | 1 | 0 | 38908.4577 | 1 | 0 | 131 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4583 | 1 | 0 | 38908.4583 | 1 | 0 | 189.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.459 | 1 | 0 | 38908.459 | 1 | 0 | 248.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4597 | 1 | 0 | 38908.4597 | 1 | 0 | 307.5 | 404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4604 | 1 | 0 | 38908.4604 | 1 | 0 | 366 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.461 | 1 | 0 | 38908.4611 | 1 | 0 | 425 | 522 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4617 | 1 | 0 | 38908.4617 | 1 | 0 | 483.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4624 | 1 | 0 | 38908.4624 | 1 | 0 | 542.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4631 | 1 | 0 | 38908.4631 | 1 | 0 | 601.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4638 | 1 | 0 | 38908.4638 | 1 | 0 | 660 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4644 | 1 | 0 | 38908.4645 | 1 | 0 | 719 | 816 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4651 | 1 | 0 | 38908.4651 | 1 | 0 | 777.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4658 | 1 | 0 | 38908.4658 | 1 | 0 | 836.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4665 | 1 | 0 | 38908.4665 | 1 | 0 | 895 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4672 | 1 | 0 | 38908.4672 | 1 | 0 | 954 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4678 | 1 | 0 | 38908.4679 | 1 | 0 | 1012.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4685 | 1 | 0 | 38908.4685 | 1 | 0 | 1071.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
| 1 | 0 | 38908.4692 | 1 | 0 | 1131 | 1228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4699 | 1 | 0 | 38908.4699 | 1 | 0 | 1189 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232238 | 232238 | 232237.9994
38908.4706 | 2 | 1 | 38908.4706 | 501 | 512 | 1248 | 1345 | 0.1221 | 0.06105 | 30.5861 | 31.2576 | 0.001221 | 0.0006105 | 0.30586 | 0.31258 | 0.0006105 | 0.0067155 | 233519.4429 | 16904.0245 | 230673.3936
38908.4713 | 277 | 268 | 38908.4713 | 853 | 885 | 1306.5 | 1403.5 | 16.9109 | 16.3614 | 52.0757 | 54.0293 | 0.16911 | 0.16361 | 0.52076 | 0.54029 | 0.0054945 | 0.019536 | 59513.1258 | 4818.8747 | 650.0843
38908.4719 | 871 | 839 | 38908.4719 | 881 | 899 | 1365.5 | 1462.5 | 53.1746 | 51.221 | 53.7851 | 54.884 | 0.53175 | 0.51221 | 0.53785 | 0.54884 | 0.019536 | 0.010989 | 4317.0476 | 51068.2345 | 72.9656
38908.4726 | 199 | 144 | 38908.4726 | 185 | 168 | 1424.5 | 1521.5 | 12.149 | 8.7912 | 11.2943 | 10.2564 | 0.12149 | 0.087912 | 0.11294 | 0.10256 | 0.033578 | 0.010379 | 3923.6071 | 16813.5088 | 1367.1327
38908.4733 | 2019 | 89 | 38908.4733 | 2218 | 80 | 1483 | 1580 | 123.2601 | 5.4335 | 135.409 | 4.884 | 1.2326 | 0.054335 | 1.3541 | 0.04884 | 1.1783 | 1.3053 | 190.4801 | 5.0277 | 11.5845
38908.474 | 1459 | 653 | 38908.474 | 1574 | 515 | 1542 | 1639 | 89.072 | 39.8657 | 96.0928 | 31.4408 | 0.89072 | 0.39866 | 0.96093 | 0.31441 | 0.49206 | 0.64652 | 355.8389 | 115.9679 | 17.382
38908.4747 | 2128 | 109 | 38908.4747 | 1753 | 84 | 1600.5 | 1697.5 | 129.9145 | 6.6545 | 107.0208 | 5.1282 | 1.2991 | 0.066545 | 1.0702 | 0.051282 | 1.2326 | 1.0189 | 10.5484 | 65.3606 | 31.3235
38908.4753 | 2307 | 20 | 38908.4753 | 2060 | 17 | 1659.5 | 1756.5 | 140.8425 | 1.221 | 125.7631 | 1.0379 | 1.4084 | 0.01221 | 1.2576 | 0.010379 | 1.3962 | 1.2473 | 0.70779 | 73.3964 | 7.6615
38908.476 | 1825 | 16 | 38908.476 | 1988 | 17 | 1718.5 | 1815.5 | 111.4164 | 0.9768 | 121.3675 | 1.0379 | 1.1142 | 0.009768 | 1.2137 | 0.010379 | 1.1044 | 1.2033 | 29.0133 | 17.5371 | 449.8332
38908.4767 | 1961 | 21 | 38908.4767 | 1983 | 23 | 1777 | 1874 | 119.7192 | 1.2821 | 121.0623 | 1.4042 | 1.1972 | 0.012821 | 1.2106 | 0.014042 | 1.1844 | 1.1966 | 19.8431 | 18.4579 | 253.3008
38908.4774 | 1874 | 37 | 38908.4774 | 2253 | 41 | 1836 | 1933 | 114.4078 | 2.2589 | 137.5458 | 2.5031 | 1.1441 | 0.022589 | 1.3755 | 0.025031 | 1.1215 | 1.3504 | 63.465 | 3.2775 | 35.3694
38908.4781 | 1465 | 914 | 38908.4781 | 1406 | 731 | 1894.5 | 1991.5 | 89.4383 | 55.7998 | 85.8364 | 44.6276 | 0.89438 | 0.558 | 0.85836 | 0.44628 | 0.33639 | 0.41209 | 107.0447 | 364.3045 | 4.7747
38908.4787 | 1153 | 1012 | 38908.4788 | 1206 | 847 | 1953.5 | 2050.5 | 70.3907 | 61.7827 | 73.6264 | 51.7094 | 0.70391 | 0.61783 | 0.73626 | 0.51709 | 0.086081 | 0.21917 | 218.9934 | 257.2209 | 11.2691

## C4-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 139.3394 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38908.4556 | 1 | 0 | 38908.4556 | 1 | 0 | -48.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4563 | 1 | 0 | 38908.4563 | 1 | 0 | 10.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4569 | 1 | 0 | 38908.4569 | 1 | 0 | 69.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4576 | 1 | 0 | 38908.4576 | 1 | 0 | 128 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4583 | 1 | 0 | 38908.4583 | 1 | 0 | 187 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.459 | 1 | 0 | 38908.459 | 1 | 0 | 245.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4597 | 1 | 0 | 38908.4597 | 1 | 0 | 304.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4603 | 1 | 0 | 38908.4603 | 1 | 0 | 363.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.461 | 1 | 0 | 38908.461 | 1 | 0 | 422 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4617 | 1 | 0 | 38908.4617 | 1 | 0 | 480.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4624 | 1 | 0 | 38908.4624 | 1 | 0 | 539.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4631 | 1 | 0 | 38908.4631 | 1 | 0 | 598.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4637 | 1 | 0 | 38908.4638 | 1 | 0 | 657 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4644 | 1 | 0 | 38908.4644 | 1 | 0 | 716 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4651 | 1 | 0 | 38908.4651 | 1 | 0 | 774.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4658 | 1 | 0 | 38908.4658 | 1 | 0 | 833.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4665 | 1 | 0 | 38908.4665 | 1 | 0 | 892.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4671 | 1 | 0 | 38908.4672 | 1 | 0 | 951 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4678 | 1 | 0 | 38908.4678 | 1 | 0 | 1010 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4685 | 1 | 0 | 38908.4685 | 1 | 0 | 1068.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4692 | 1 | 0 | 38908.4692 | 1 | 0 | 1127.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4699 | 1 | 0 | 38908.4699 | 1 | 0 | 1186.5 | 1283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4705 | 1 | 0 | 38908.4706 | 1 | 0 | 1245 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228138 | 228138 | 228137.9994
38908.4712 | 868 | 931 | 38908.4712 | 807 | 838 | 1304 | 1401 | 52.9915 | 56.8376 | 49.2674 | 51.16 | 0.52991 | 0.56838 | 0.49267 | 0.5116 | 0.038462 | 0.018926 | 2038.7142 | 14601.4511 | 51.5673
38908.4719 | 1124 | 1084 | 38908.4719 | 1041 | 1001 | 1362.5 | 1459.5 | 68.6203 | 66.1783 | 63.5531 | 61.1111 | 0.6862 | 0.66178 | 0.63553 | 0.61111 | 0.02442 | 0.02442 | 5605.95 | 5605.95 | 6.7414
38908.4726 | 923 | 859 | 38908.4726 | 1098 | 1030 | 1421.5 | 1518.5 | 56.3492 | 52.442 | 67.033 | 62.8816 | 0.56349 | 0.52442 | 0.67033 | 0.62882 | 0.039072 | 0.041514 | 4170.9175 | 2734.9606 | 56.1967
38908.4733 | 1705 | 99 | 38908.4733 | 2211 | 109 | 1480.5 | 1577.5 | 104.0904 | 6.044 | 134.9817 | 6.6545 | 1.0409 | 0.06044 | 1.3498 | 0.066545 | 0.98046 | 1.2833 | 32.5506 | 59.0022 | 179.3094
38908.4739 | 1653 | 621 | 38908.474 | 1530 | 468 | 1539 | 1636 | 100.9158 | 37.9121 | 93.4066 | 28.5714 | 1.0092 | 0.37912 | 0.93407 | 0.28571 | 0.63004 | 0.64835 | 156.3903 | 98.6406 | 0.6701
38908.4746 | 2094 | 131 | 38908.4746 | 2172 | 117 | 1598 | 1695 | 127.8388 | 7.9976 | 132.6007 | 7.1429 | 1.2784 | 0.079976 | 1.326 | 0.071429 | 1.1984 | 1.2546 | 10.4064 | 85.751 | 20.2207
38908.4753 | 1967 | 15 | 38908.4753 | 1870 | 15 | 1656.5 | 1753.5 | 120.0855 | 0.91575 | 114.1636 | 0.91575 | 1.2009 | 0.0091575 | 1.1416 | 0.0091575 | 1.1917 | 1.1325 | 16.7063 | 23.3615 | 379.2281
38908.476 | 2044 | 13 | 38908.476 | 2088 | 14 | 1715.5 | 1812.5 | 124.7863 | 0.79365 | 127.4725 | 0.8547 | 1.2479 | 0.0079365 | 1.2747 | 0.008547 | 1.2399 | 1.2662 | 12.5479 | 9.9051 | 156.2472
38908.4767 | 2163 | 17 | 38908.4767 | 2266 | 18 | 1774.5 | 1871.5 | 132.0513 | 1.0379 | 138.3394 | 1.0989 | 1.3205 | 0.010379 | 1.3834 | 0.010989 | 1.3101 | 1.3724 | 53.8239 | 0.88348 | 5.2741
38908.4773 | 2256 | 35 | 38908.4774 | 1824 | 29 | 1833 | 1930 | 137.7289 | 2.1368 | 111.3553 | 1.7705 | 1.3773 | 0.021368 | 1.1136 | 0.017705 | 1.3559 | 1.0958 | 1.1596 | 64.9418 | 9.6969
38908.478 | 1692 | 576 | 38908.478 | 1701 | 841 | 1892 | 1989 | 103.2967 | 35.1648 | 103.8462 | 51.3431 | 1.033 | 0.35165 | 1.0385 | 0.51343 | 0.68132 | 0.52503 | 91.9984 | 121.4494 | 1.3692
38908.4787 | 985 | 861 | 38908.4787 | 1123 | 981 | 1950.5 | 2047.5 | 60.1343 | 52.5641 | 68.5592 | 59.8901 | 0.60134 | 0.52564 | 0.68559 | 0.5989 | 0.075702 | 0.086691 | 3067.3538 | 1053.809 | 46.2903

## C4-6
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 144.956 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38908.4555 | 1 | 0 | 38908.4556 | 1 | 0 | -51 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4562 | 1 | 0 | 38908.4562 | 1 | 0 | 7.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4569 | 1 | 0 | 38908.4569 | 1 | 0 | 66.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4576 | 1 | 0 | 38908.4576 | 1 | 0 | 125.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4583 | 1 | 0 | 38908.4583 | 1 | 0 | 184 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4589 | 1 | 0 | 38908.459 | 1 | 0 | 243 | 340 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4596 | 1 | 0 | 38908.4596 | 1 | 0 | 301.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4603 | 1 | 0 | 38908.4603 | 1 | 0 | 360.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.461 | 1 | 0 | 38908.461 | 1 | 0 | 419.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4617 | 1 | 0 | 38908.4617 | 1 | 0 | 478 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4623 | 1 | 0 | 38908.4624 | 1 | 0 | 537 | 634 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.463 | 1 | 0 | 38908.463 | 1 | 0 | 595.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4637 | 1 | 0 | 38908.4637 | 1 | 0 | 654.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4644 | 1 | 0 | 38908.4644 | 1 | 0 | 713 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4651 | 1 | 0 | 38908.4651 | 1 | 0 | 772 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4657 | 1 | 0 | 38908.4658 | 1 | 0 | 830.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4664 | 1 | 0 | 38908.4664 | 1 | 0 | 889.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4671 | 1 | 0 | 38908.4671 | 1 | 0 | 948.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4678 | 1 | 0 | 38908.4678 | 1 | 0 | 1007 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4685 | 1 | 0 | 38908.4685 | 1 | 0 | 1066 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4691 | 1 | 0 | 38908.4692 | 1 | 0 | 1124.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4698 | 1 | 0 | 38908.4698 | 1 | 0 | 1183.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4705 | 1 | 0 | 38908.4705 | 1 | 0 | 1242.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237338 | 237338 | 237337.9994
38908.4712 | 804 | 780 | 38908.4712 | 912 | 877 | 1301 | 1398 | 49.0842 | 47.619 | 55.6777 | 53.5409 | 0.49084 | 0.47619 | 0.55678 | 0.53541 | 0.014652 | 0.021368 | 20679.8447 | 4754.2917 | 99.2433
38908.4719 | 549 | 522 | 38908.4719 | 920 | 879 | 1360 | 1457 | 33.5165 | 31.8681 | 56.1661 | 53.663 | 0.33516 | 0.31868 | 0.56166 | 0.53663 | 0.016484 | 0.025031 | 12291.0904 | 4296.7367 | 244.0107
38908.4725 | 189 | 122 | 38908.4726 | 133 | 114 | 1418.5 | 1515.5 | 11.5385 | 7.4481 | 8.1197 | 6.9597 | 0.11538 | 0.074481 | 0.081197 | 0.069597 | 0.040904 | 0.0116 | 3303.4912 | 14414.8486 | 1679.6429
38908.4732 | 2156 | 98 | 38908.4732 | 1870 | 83 | 1477.5 | 1574.5 | 131.6239 | 5.9829 | 114.1636 | 5.0672 | 1.3162 | 0.059829 | 1.1416 | 0.050672 | 1.2564 | 1.091 | 11.8222 | 46.4895 | 38.9832
38908.4739 | 1490 | 566 | 38908.4739 | 1747 | 609 | 1536.5 | 1633.5 | 90.9646 | 34.5543 | 106.6545 | 37.1795 | 0.90965 | 0.34554 | 1.0665 | 0.37179 | 0.5641 | 0.69475 | 326.2723 | 86.6843 | 26.1193
38908.4746 | 1740 | 137 | 38908.4746 | 1924 | 118 | 1595 | 1692 | 106.2271 | 8.3639 | 117.4603 | 7.2039 | 1.0623 | 0.083639 | 1.1746 | 0.072039 | 0.97863 | 1.1026 | 56.8019 | 28.1794 | 79.8144
38908.4753 | 2277 | 20 | 38908.4753 | 2155 | 18 | 1653.5 | 1750.5 | 139.011 | 1.221 | 131.5629 | 1.0989 | 1.3901 | 0.01221 | 1.3156 | 0.010989 | 1.3779 | 1.3046 | 4.6426 | 12.5411 | 43.1145
38908.4759 | 1920 | 14 | 38908.476 | 2211 | 18 | 1712.5 | 1809.5 | 117.2161 | 0.8547 | 134.9817 | 1.0989 | 1.1722 | 0.008547 | 1.3498 | 0.010989 | 1.1636 | 1.3388 | 26.3572 | 7.6895 | 224.6083
38908.4766 | 2037 | 18 | 38908.4766 | 2284 | 23 | 1771.5 | 1868.5 | 124.359 | 1.0989 | 139.4383 | 1.4042 | 1.2436 | 0.010989 | 1.3944 | 0.014042 | 1.2326 | 1.3803 | 21.215 | 4.1987 | 71.4965
38908.4773 | 2314 | 39 | 38908.4773 | 2358 | 42 | 1830.5 | 1927.5 | 141.2698 | 2.381 | 143.956 | 2.5641 | 1.4127 | 0.02381 | 1.4396 | 0.025641 | 1.3889 | 1.4139 | 1.2231 | 1.4653 | 0.79168
38908.478 | 1741 | 766 | 38908.478 | 1499 | 671 | 1889 | 1986 | 106.2882 | 46.7643 | 91.514 | 40.9646 | 1.0629 | 0.46764 | 0.91514 | 0.40965 | 0.59524 | 0.50549 | 18.455 | 31.176 | 4.1148
38908.4787 | 1236 | 1087 | 38908.4787 | 1118 | 980 | 1947.5 | 2044.5 | 75.4579 | 66.3614 | 68.254 | 59.8291 | 0.75458 | 0.66361 | 0.68254 | 0.59829 | 0.090965 | 0.084249 | 981.2652 | 3295.0828 | 4.5875

## C4-5
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 140.2552 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38908.4555 | 1 | 0 | 38908.4555 | 1 | 0 | -54 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4562 | 1 | 0 | 38908.4562 | 1 | 0 | 5 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4569 | 1 | 0 | 38908.4569 | 1 | 0 | 63.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4575 | 1 | 0 | 38908.4576 | 1 | 0 | 122.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4582 | 1 | 0 | 38908.4582 | 1 | 0 | 181.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4589 | 1 | 0 | 38908.4589 | 1 | 0 | 240 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4596 | 1 | 0 | 38908.4596 | 1 | 0 | 299 | 396 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4603 | 1 | 0 | 38908.4603 | 1 | 0 | 357.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4609 | 1 | 0 | 38908.461 | 1 | 0 | 416.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4616 | 1 | 0 | 38908.4616 | 1 | 0 | 475.5 | 572.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4623 | 1 | 0 | 38908.4623 | 1 | 0 | 534 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.463 | 1 | 0 | 38908.463 | 1 | 0 | 593 | 690 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4637 | 1 | 0 | 38908.4637 | 1 | 0 | 651.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4644 | 1 | 0 | 38908.4644 | 1 | 0 | 710.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.465 | 1 | 0 | 38908.465 | 1 | 0 | 769 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4657 | 1 | 0 | 38908.4657 | 1 | 0 | 828 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4664 | 1 | 0 | 38908.4664 | 1 | 0 | 887 | 984 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4671 | 1 | 0 | 38908.4671 | 1 | 0 | 945.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4678 | 1 | 0 | 38908.4678 | 1 | 0 | 1004.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4684 | 1 | 0 | 38908.4684 | 1 | 0 | 1063 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4691 | 1 | 0 | 38908.4691 | 1 | 0 | 1122 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4698 | 1 | 0 | 38908.4698 | 1 | 0 | 1180.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38908.4705 | 1 | 1 | 38908.4705 | 1 | 0 | 1239.5 | 1336.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 527336110.44 | 229638 | 229438.0871
38908.4712 | 83 | 127 | 38908.4712 | 350 | 338 | 1298.5 | 1395.5 | 5.0672 | 7.7534 | 21.3675 | 20.6349 | 0.050672 | 0.077534 | 0.21368 | 0.20635 | 0.026862 | 0.007326 | 5072.8099 | 36488.111 | 1639.1141
38908.4718 | 109 | 100 | 38908.4719 | 196 | 187 | 1357 | 1454 | 6.6545 | 6.105 | 11.9658 | 11.4164 | 0.066545 | 0.06105 | 0.11966 | 0.11416 | 0.0054945 | 0.0054945 | 25426.4444 | 25426.4444 | 2080.1988
38908.4725 | 978 | 917 | 38908.4725 | 1153 | 1099 | 1416 | 1513 | 59.707 | 55.9829 | 70.3907 | 67.094 | 0.59707 | 0.55983 | 0.70391 | 0.67094 | 0.037241 | 0.032967 | 2474.6643 | 11933.136 | 43.5154
38908.4732 | 1785 | 164 | 38908.4732 | 2135 | 166 | 1474.5 | 1571.5 | 108.9744 | 10.0122 | 130.3419 | 10.1343 | 1.0897 | 0.10012 | 1.3034 | 0.10134 | 0.98962 | 1.2021 | 93.7657 | 15.2622 | 28.128
38908.4739 | 1467 | 931 | 38908.4739 | 1403 | 613 | 1533.5 | 1630.5 | 89.5604 | 56.8376 | 85.6532 | 37.4237 | 0.8956 | 0.56838 | 0.85653 | 0.37424 | 0.32723 | 0.4823 | 67.1498 | 132.8846 | 6.1669
38908.4746 | 2082 | 185 | 38908.4746 | 2156 | 151 | 1592.5 | 1689.5 | 127.1062 | 11.2943 | 131.6239 | 9.2186 | 1.2711 | 0.11294 | 1.3162 | 0.092186 | 1.1581 | 1.2241 | 2.4486 | 2.6816 | 0.42886
38908.4752 | 1864 | 24 | 38908.4753 | 1882 | 24 | 1651 | 1748 | 113.7973 | 1.4652 | 114.8962 | 1.4652 | 1.138 | 0.014652 | 1.149 | 0.014652 | 1.1233 | 1.1343 | 24.9326 | 23.5778 | 325.4457
38908.4759 | 2267 | 23 | 38908.4759 | 2092 | 20 | 1710 | 1807 | 138.4005 | 1.4042 | 127.7167 | 1.221 | 1.384 | 0.014042 | 1.2772 | 0.01221 | 1.37 | 1.265 | 1.3986 | 31.9883 | 7.7765
38908.4766 | 2281 | 24 | 38908.4766 | 1992 | 22 | 1768.5 | 1865.5 | 139.2552 | 1.4652 | 121.6117 | 1.3431 | 1.3926 | 0.014652 | 1.2161 | 0.013431 | 1.3779 | 1.2027 | 0.69694 | 25.735 | 6.4985
38908.4773 | 2199 | 38 | 38908.4773 | 2007 | 36 | 1827.5 | 1924.5 | 134.2491 | 2.3199 | 122.5275 | 2.1978 | 1.3425 | 0.023199 | 1.2253 | 0.021978 | 1.3193 | 1.2033 | 4.922 | 23.4255 | 30.1574
38908.478 | 1844 | 669 | 38908.478 | 1706 | 868 | 1886 | 1983 | 112.5763 | 40.8425 | 104.1514 | 52.9915 | 1.1258 | 0.40842 | 1.0415 | 0.52991 | 0.71734 | 0.5116 | 232.8293 | 68.2463 | 13.0736
38908.4786 | 985 | 880 | 38908.4787 | 1148 | 1000 | 1945 | 2042 | 60.1343 | 53.7241 | 70.0855 | 61.0501 | 0.60134 | 0.53724 | 0.70085 | 0.6105 | 0.064103 | 0.090354 | 6576.8367 | 1034.7412 | 44.8041

## C3-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 146.0549 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38908.4555 | 1 | 0 | 38908.4555 | 1 | 0 | -56.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4561 | 1 | 0 | 38908.4562 | 1 | 0 | 2 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4568 | 1 | 0 | 38908.4569 | 1 | 0 | 61 | 158 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4575 | 1 | 0 | 38908.4575 | 1 | 0 | 119.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4582 | 1 | 0 | 38908.4582 | 1 | 0 | 178.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4589 | 1 | 0 | 38908.4589 | 1 | 0 | 237.5 | 334.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4595 | 1 | 0 | 38908.4596 | 1 | 0 | 296 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4602 | 1 | 0 | 38908.4603 | 1 | 0 | 355 | 452 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4609 | 1 | 0 | 38908.4609 | 1 | 0 | 413.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4616 | 1 | 0 | 38908.4616 | 1 | 0 | 472.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4623 | 1 | 0 | 38908.4623 | 1 | 0 | 531.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.463 | 1 | 0 | 38908.463 | 1 | 0 | 590 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4636 | 1 | 0 | 38908.4637 | 1 | 0 | 649 | 746 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4643 | 1 | 0 | 38908.4643 | 1 | 0 | 707.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.465 | 1 | 0 | 38908.465 | 1 | 0 | 766.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4657 | 1 | 0 | 38908.4657 | 1 | 0 | 825 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4664 | 1 | 0 | 38908.4664 | 1 | 0 | 884 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.467 | 1 | 0 | 38908.467 | 1 | 0 | 942.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4677 | 1 | 0 | 38908.4677 | 1 | 0 | 1001.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4684 | 2 | 0 | 38908.4684 | 1 | 0 | 1060.5 | 1157.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119519 | 239138 | 119518.9988
38908.4691 | 1 | 0 | 38908.4691 | 1 | 0 | 1119 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4698 | 1 | 0 | 38908.4698 | 1 | 0 | 1178 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
38908.4704 | 1 | 1 | 38908.4705 | 1 | 0 | 1236.5 | 1333.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 571869830.44 | 239138 | 238938.0836
38908.4711 | 881 | 916 | 38908.4711 | 840 | 944 | 1295.5 | 1392.5 | 53.7851 | 55.9219 | 51.2821 | 57.6313 | 0.53785 | 0.55922 | 0.51282 | 0.57631 | 0.021368 | 0.063492 | 3619.6109 | 13559.69 | 64.522
38908.4718 | 902 | 913 | 38908.4718 | 1068 | 1133 | 1354.5 | 1451.5 | 55.0672 | 55.7387 | 65.2015 | 69.1697 | 0.55067 | 0.55739 | 0.65201 | 0.6917 | 0.0067155 | 0.039683 | 2097.9615 | 1520.6672 | 59.3378
38908.4725 | 332 | 262 | 38908.4725 | 411 | 363 | 1413 | 1510 | 20.2686 | 15.9951 | 25.0916 | 22.1612 | 0.20269 | 0.15995 | 0.25092 | 0.22161 | 0.042735 | 0.029304 | 3161.4897 | 5425.7521 | 673.9827
38908.4732 | 1371 | 377 | 38908.4732 | 1704 | 184 | 1472 | 1569 | 83.6996 | 23.0159 | 104.0293 | 11.2332 | 0.837 | 0.23016 | 1.0403 | 0.11233 | 0.60684 | 0.92796 | 569.8509 | 46.2711 | 54.0694
38908.4738 | 1816 | 511 | 38908.4739 | 1800 | 559 | 1530.5 | 1627.5 | 110.8669 | 31.1966 | 109.8901 | 34.127 | 1.1087 | 0.31197 | 1.0989 | 0.34127 | 0.7967 | 0.75763 | 40.162 | 392.6609 | 10.1975
38908.4745 | 1748 | 157 | 38908.4745 | 1833 | 161 | 1589.5 | 1686.5 | 106.7155 | 9.5849 | 111.9048 | 9.8291 | 1.0672 | 0.095849 | 1.119 | 0.098291 | 0.97131 | 1.0208 | 53.4171 | 40.8128 | 89.9751
38908.4752 | 2259 | 21 | 38908.4752 | 2376 | 19 | 1648.5 | 1745.5 | 137.9121 | 1.2821 | 145.0549 | 1.16 | 1.3791 | 0.012821 | 1.4505 | 0.0116 | 1.3663 | 1.4389 | 13.9094 | 1.6418 | 8.6441
38908.4759 | 2192 | 13 | 38908.4759 | 2348 | 13 | 1707 | 1804 | 133.8217 | 0.79365 | 143.3455 | 0.79365 | 1.3382 | 0.0079365 | 1.4335 | 0.0079365 | 1.3303 | 1.4255 | 13.1484 | 1.9847 | 28.0502
38908.4766 | 2200 | 15 | 38908.4766 | 2144 | 15 | 1766 | 1863 | 134.3101 | 0.91575 | 130.8913 | 0.91575 | 1.3431 | 0.0091575 | 1.3089 | 0.0091575 | 1.3339 | 1.2998 | 9.311 | 12.6216 | 132.5273
38908.4772 | 2366 | 24 | 38908.4773 | 1852 | 25 | 1824.5 | 1921.5 | 144.4444 | 1.4652 | 113.0647 | 1.5263 | 1.4444 | 0.014652 | 1.1306 | 0.015263 | 1.4298 | 1.1154 | 1.1177 | 131.8869 | 5.6402
38908.4779 | 1457 | 562 | 38908.4779 | 1697 | 634 | 1883.5 | 1980.5 | 88.9499 | 34.3101 | 103.602 | 38.7057 | 0.8895 | 0.3431 | 1.036 | 0.38706 | 0.5464 | 0.64896 | 1178.4742 | 68.904 | 27.1031
38908.4786 | 1184 | 1036 | 38908.4786 | 1139 | 985 | 1942 | 2039 | 72.2833 | 63.2479 | 69.536 | 60.1343 | 0.72283 | 0.63248 | 0.69536 | 0.60134 | 0.090354 | 0.094017 | 1903.5859 | 1225.7329 | 15.3839

## C3-6
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 135.0049 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38908.4554 | 1 | 0 | 38908.4555 | 1 | 0 | -59.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4561 | 1 | 0 | 38908.4561 | 1 | 0 | -0.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4568 | 1 | 0 | 38908.4568 | 1 | 0 | 58 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4575 | 1 | 0 | 38908.4575 | 1 | 0 | 117 | 214 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4582 | 1 | 0 | 38908.4582 | 1 | 0 | 175.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4588 | 1 | 0 | 38908.4589 | 1 | 0 | 234.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4595 | 1 | 0 | 38908.4595 | 1 | 0 | 293.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4602 | 1 | 0 | 38908.4602 | 1 | 0 | 352 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4609 | 1 | 0 | 38908.4609 | 1 | 0 | 411 | 508 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4616 | 1 | 0 | 38908.4616 | 1 | 0 | 469.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4622 | 2 | 0 | 38908.4623 | 1 | 0 | 528.5 | 625.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 110469 | 221038 | 110468.9988
38908.4629 | 1 | 0 | 38908.4629 | 1 | 0 | 587.5 | 684.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4636 | 1 | 0 | 38908.4636 | 1 | 0 | 646 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4643 | 1 | 0 | 38908.4643 | 1 | 0 | 705 | 802 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.465 | 1 | 0 | 38908.465 | 1 | 0 | 763.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4656 | 1 | 0 | 38908.4657 | 1 | 0 | 822.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4663 | 1 | 0 | 38908.4663 | 1 | 0 | 881 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.467 | 1 | 0 | 38908.467 | 1 | 0 | 940 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4677 | 1 | 0 | 38908.4677 | 1 | 0 | 998.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4684 | 1 | 0 | 38908.4684 | 1 | 0 | 1057.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4691 | 1 | 0 | 38908.4691 | 1 | 0 | 1116.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4697 | 1 | 0 | 38908.4697 | 1 | 0 | 1175 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4704 | 1 | 0 | 38908.4704 | 1 | 0 | 1234 | 1331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 221038 | 221038 | 221037.9994
38908.4711 | 356 | 394 | 38908.4711 | 806 | 777 | 1292.5 | 1389.5 | 21.7338 | 24.0537 | 49.2063 | 47.4359 | 0.21734 | 0.24054 | 0.49206 | 0.47436 | 0.023199 | 0.017705 | 5482.2808 | 9478.4763 | 367.0363
38908.4718 | 1026 | 993 | 38908.4718 | 1115 | 1087 | 1351.5 | 1448.5 | 62.6374 | 60.6227 | 68.0708 | 66.3614 | 0.62637 | 0.60623 | 0.68071 | 0.66361 | 0.020147 | 0.017094 | 2629.1992 | 8216.6546 | 19.1407
38908.4725 | 328 | 285 | 38908.4725 | 311 | 433 | 1410.5 | 1507.5 | 20.0244 | 17.3993 | 18.9866 | 26.4347 | 0.20024 | 0.17399 | 0.18987 | 0.26435 | 0.026252 | 0.074481 | 7361.0268 | 1636.5985 | 528.5401
38908.4731 | 1072 | 876 | 38908.4731 | 1265 | 917 | 1469 | 1566 | 65.4457 | 53.4799 | 77.2283 | 55.9829 | 0.65446 | 0.5348 | 0.77228 | 0.55983 | 0.11966 | 0.21245 | 230.3956 | 293.4358 | 22.4242
38908.4738 | 1641 | 398 | 38908.4738 | 1564 | 389 | 1528 | 1625 | 100.1832 | 24.2979 | 95.4823 | 23.7485 | 1.0018 | 0.24298 | 0.95482 | 0.23748 | 0.75885 | 0.71734 | 63.6211 | 114.8718 | 23.1546
38908.4745 | 1980 | 297 | 38908.4745 | 1985 | 198 | 1586.5 | 1683.5 | 120.8791 | 18.1319 | 121.1844 | 12.0879 | 1.2088 | 0.18132 | 1.2118 | 0.12088 | 1.0275 | 1.091 | 4.2915 | 8.0085 | 1.6382
38908.4752 | 1908 | 16 | 38908.4752 | 2195 | 17 | 1645.5 | 1742.5 | 116.4835 | 0.9768 | 134.0049 | 1.0379 | 1.1648 | 0.009768 | 1.34 | 0.010379 | 1.1551 | 1.3297 | 121.7868 | 0.97389 | 17.3236
38908.4759 | 1934 | 13 | 38908.4759 | 1926 | 13 | 1704.5 | 1801.5 | 118.0708 | 0.79365 | 117.5824 | 0.79365 | 1.1807 | 0.0079365 | 1.1758 | 0.0079365 | 1.1728 | 1.1679 | 15.0932 | 15.6213 | 274.7665
38908.4765 | 1905 | 14 | 38908.4766 | 1875 | 14 | 1763 | 1860 | 116.3004 | 0.8547 | 114.4689 | 0.8547 | 1.163 | 0.008547 | 1.1447 | 0.008547 | 1.1545 | 1.1361 | 16.8618 | 18.9193 | 332.2557
38908.4772 | 2133 | 31 | 38908.4772 | 1957 | 27 | 1821.5 | 1918.5 | 130.2198 | 1.8926 | 119.475 | 1.6484 | 1.3022 | 0.018926 | 1.1947 | 0.016484 | 1.2833 | 1.1783 | 4.0224 | 20.2089 | 25.6944
38908.4779 | 1840 | 581 | 38908.4779 | 1822 | 554 | 1880.5 | 1977.5 | 112.3321 | 35.4701 | 111.2332 | 33.8217 | 1.1233 | 0.3547 | 1.1123 | 0.33822 | 0.76862 | 0.77411 | 71.9195 | 78.2369 | 15.8369
38908.4786 | 958 | 879 | 38908.4786 | 961 | 884 | 1939.5 | 2036.5 | 58.486 | 53.663 | 58.6691 | 53.9683 | 0.58486 | 0.53663 | 0.58669 | 0.53968 | 0.04823 | 0.047009 | 2540.9679 | 2962.2763 | 41.2007

## C3-5
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 145.2613 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38908.4554 | 1 | 0 | 38908.4554 | 1 | 0 | -62.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4561 | 1 | 0 | 38908.4561 | 1 | 0 | -3.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4568 | 1 | 0 | 38908.4568 | 1 | 0 | 55.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4574 | 1 | 0 | 38908.4575 | 1 | 0 | 114 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4581 | 1 | 0 | 38908.4581 | 1 | 0 | 173 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4588 | 1 | 0 | 38908.4588 | 1 | 0 | 231.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4595 | 1 | 0 | 38908.4595 | 1 | 0 | 290.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4602 | 1 | 0 | 38908.4602 | 1 | 0 | 349.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4608 | 1 | 0 | 38908.4609 | 1 | 0 | 408 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4615 | 1 | 0 | 38908.4615 | 1 | 0 | 466.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4622 | 1 | 0 | 38908.4622 | 1 | 0 | 525.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4629 | 1 | 0 | 38908.4629 | 1 | 0 | 584.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4636 | 1 | 0 | 38908.4636 | 1 | 0 | 643 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4642 | 1 | 0 | 38908.4643 | 1 | 0 | 702 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4649 | 1 | 0 | 38908.4649 | 1 | 0 | 760.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4656 | 1 | 0 | 38908.4656 | 1 | 0 | 819.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4663 | 1 | 0 | 38908.4663 | 1 | 0 | 878.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.467 | 1 | 0 | 38908.467 | 1 | 0 | 937 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4677 | 1 | 0 | 38908.4677 | 1 | 0 | 996 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4683 | 1 | 0 | 38908.4683 | 1 | 0 | 1054.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.469 | 1 | 0 | 38908.469 | 1 | 0 | 1113.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4697 | 1 | 0 | 38908.4697 | 1 | 0 | 1172.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38908.4704 | 2 | 1 | 38908.4704 | 1 | 1 | 1231 | 1328 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 237737.958 | 565431204.4352 | 237637.958
38908.4711 | 6 | 12 | 38908.4711 | 102 | 127 | 1290 | 1387 | 0.3663 | 0.7326 | 6.2271 | 7.7534 | 0.003663 | 0.007326 | 0.062271 | 0.077534 | 0.003663 | 0.015263 | 40432.8864 | 9225.4286 | 19467.1504
38908.4717 | 926 | 760 | 38908.4717 | 817 | 875 | 1348.5 | 1445.5 | 56.5324 | 46.398 | 49.8779 | 53.4188 | 0.56532 | 0.46398 | 0.49878 | 0.53419 | 0.10134 | 0.035409 | 745.8977 | 2634.3356 | 87.8976
38908.4724 | 1001 | 942 | 38908.4724 | 979 | 922 | 1407.5 | 1504.5 | 61.1111 | 57.5092 | 59.768 | 56.2882 | 0.61111 | 0.57509 | 0.59768 | 0.56288 | 0.03602 | 0.034799 | 3670.2032 | 4392.8288 | 45.2938
38908.4731 | 1184 | 1014 | 38908.4731 | 992 | 870 | 1466.5 | 1563.5 | 72.2833 | 61.9048 | 60.5617 | 53.1136 | 0.72283 | 0.61905 | 0.60562 | 0.53114 | 0.10379 | 0.074481 | 692.1889 | 37616.3626 | 17.8401
38908.4738 | 1828 | 382 | 38908.4738 | 1454 | 424 | 1525 | 1622 | 111.5995 | 23.3211 | 88.7668 | 25.8852 | 1.116 | 0.23321 | 0.88767 | 0.25885 | 0.88278 | 0.62882 | 36.8678 | 770.8012 | 39.2484
38908.4745 | 1860 | 228 | 38908.4745 | 1714 | 209 | 1584 | 1681 | 113.5531 | 13.9194 | 104.6398 | 12.7595 | 1.1355 | 0.13919 | 1.0464 | 0.12759 | 0.99634 | 0.9188 | 40.1116 | 67.6231 | 51.5568
38908.4751 | 2271 | 27 | 38908.4752 | 1910 | 21 | 1642.5 | 1739.5 | 138.6447 | 1.6484 | 116.6056 | 1.2821 | 1.3864 | 0.016484 | 1.1661 | 0.012821 | 1.37 | 1.1532 | 5.019 | 31.9179 | 72.9263
38908.4758 | 2298 | 18 | 38908.4758 | 2319 | 15 | 1701.5 | 1798.5 | 140.293 | 1.0989 | 141.5751 | 0.91575 | 1.4029 | 0.010989 | 1.4158 | 0.0091575 | 1.3919 | 1.4066 | 4.8274 | 3.0292 | 10.3525
38908.4765 | 2363 | 19 | 38908.4765 | 2337 | 20 | 1760.5 | 1857.5 | 144.2613 | 1.16 | 142.674 | 1.221 | 1.4426 | 0.0116 | 1.4267 | 0.01221 | 1.431 | 1.4145 | 0.56798 | 3.5193 | 0.46879
38908.4772 | 1973 | 26 | 38908.4772 | 1901 | 26 | 1819 | 1916 | 120.4518 | 1.5873 | 116.0562 | 1.5873 | 1.2045 | 0.015873 | 1.1606 | 0.015873 | 1.1886 | 1.1447 | 21.9483 | 27.2342 | 313.1521
38908.4779 | 1527 | 442 | 38908.4779 | 1691 | 397 | 1878 | 1975 | 93.2234 | 26.9841 | 103.2357 | 24.2369 | 0.93223 | 0.26984 | 1.0324 | 0.24237 | 0.66239 | 0.78999 | 235.0962 | 61.1821 | 35.2429
38908.4785 | 1179 | 1016 | 38908.4786 | 1171 | 1095 | 1936.5 | 2033.5 | 71.978 | 62.0269 | 71.4896 | 66.8498 | 0.71978 | 0.62027 | 0.7149 | 0.6685 | 0.099512 | 0.046398 | 282.2508 | 387.3599 | 14.424

## C3-4
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 145.6886 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38908.4554 | 1 | 0 | 38908.4554 | 1 | 0 | -65 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4561 | 1 | 0 | 38908.4561 | 1 | 0 | -6.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4567 | 1 | 0 | 38908.4567 | 1 | 0 | 52.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4574 | 1 | 0 | 38908.4574 | 1 | 0 | 111.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4581 | 1 | 0 | 38908.4581 | 1 | 0 | 170.5 | 267.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4588 | 1 | 0 | 38908.4588 | 1 | 0 | 229 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4595 | 1 | 0 | 38908.4595 | 1 | 0 | 287.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4601 | 1 | 0 | 38908.4602 | 1 | 0 | 346.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4608 | 1 | 0 | 38908.4608 | 1 | 0 | 405 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4615 | 1 | 0 | 38908.4615 | 1 | 0 | 464 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4622 | 1 | 0 | 38908.4622 | 1 | 0 | 522.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4629 | 1 | 0 | 38908.4629 | 1 | 0 | 581.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4635 | 1 | 0 | 38908.4636 | 1 | 0 | 640.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4642 | 1 | 0 | 38908.4642 | 1 | 0 | 699 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4649 | 1 | 0 | 38908.4649 | 1 | 0 | 758 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4656 | 1 | 0 | 38908.4656 | 1 | 0 | 817 | 914 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4663 | 1 | 0 | 38908.4663 | 1 | 0 | 875.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4669 | 1 | 0 | 38908.467 | 1 | 0 | 934.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4676 | 1 | 0 | 38908.4676 | 1 | 0 | 993 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4683 | 1 | 0 | 38908.4683 | 1 | 0 | 1052 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.469 | 2 | 0 | 38908.469 | 1 | 0 | 1110.5 | 1207.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119219 | 238538 | 119218.9988
38908.4697 | 1 | 0 | 38908.4697 | 1 | 0 | 1169.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38908.4703 | 3 | 8 | 38908.4704 | 1 | 4 | 1228.5 | 1325.5 | 0.18315 | 0.4884 | 0.06105 | 0.2442 | 0.0018315 | 0.004884 | 0.0006105 | 0.002442 | 0.0030525 | 0.0018315 | 47763.4441 | 79735.2504 | 29655.0581
38908.471 | 7 | 15 | 38908.471 | 7 | 12 | 1287 | 1384 | 0.42735 | 0.91575 | 0.42735 | 0.7326 | 0.0042735 | 0.0091575 | 0.0042735 | 0.007326 | 0.004884 | 0.0030525 | 29858.9517 | 47973.1985 | 15729.7447
38908.4717 | 453 | 437 | 38908.4717 | 80 | 80 | 1346 | 1443 | 27.6557 | 26.6789 | 4.884 | 4.884 | 0.27656 | 0.26679 | 0.04884 | 0.04884 | 0.009768 | 0 | 11988.8878 | 345636.6378 | 342.322
38908.4724 | 843 | 868 | 38908.4724 | 1122 | 1044 | 1404.5 | 1501.5 | 51.4652 | 52.9915 | 68.4982 | 63.7363 | 0.51465 | 0.52991 | 0.68498 | 0.63736 | 0.015263 | 0.047619 | 2895.8063 | 3067.4551 | 75.3522
38908.4731 | 1023 | 859 | 38908.4731 | 1105 | 1014 | 1463.5 | 1560.5 | 62.4542 | 52.442 | 67.4603 | 61.9048 | 0.62454 | 0.52442 | 0.6746 | 0.61905 | 0.10012 | 0.055556 | 663.7367 | 2074.3894 | 56.0167
38908.4737 | 1819 | 86 | 38908.4738 | 1723 | 323 | 1522.5 | 1619.5 | 111.0501 | 5.2503 | 105.1893 | 19.7192 | 1.1105 | 0.052503 | 1.0519 | 0.19719 | 1.058 | 0.8547 | 33.8708 | 148.6149 | 334.5992
38908.4744 | 1869 | 256 | 38908.4744 | 2047 | 264 | 1581 | 1678 | 114.1026 | 15.6288 | 124.9695 | 16.1172 | 1.141 | 0.15629 | 1.2497 | 0.16117 | 0.98474 | 1.0885 | 118.7228 | 21.7463 | 18.2374
38908.4751 | 2010 | 27 | 38908.4751 | 2093 | 26 | 1640 | 1737 | 122.7106 | 1.6484 | 127.7778 | 1.5873 | 1.2271 | 0.016484 | 1.2778 | 0.015873 | 1.2106 | 1.2619 | 20.8608 | 15.1043 | 169.8019
38908.4758 | 2055 | 19 | 38908.4758 | 1932 | 16 | 1698.5 | 1795.5 | 125.4579 | 1.16 | 117.9487 | 0.9768 | 1.2546 | 0.0116 | 1.1795 | 0.009768 | 1.243 | 1.1697 | 16.9085 | 24.9471 | 328.2643
38908.4765 | 1948 | 16 | 38908.4765 | 2087 | 17 | 1757.5 | 1854.5 | 118.9255 | 0.9768 | 127.4115 | 1.0379 | 1.1893 | 0.009768 | 1.2741 | 0.010379 | 1.1795 | 1.2637 | 24.0188 | 14.9748 | 343.8289
38908.4772 | 2220 | 30 | 38908.4772 | 2370 | 33 | 1816.5 | 1913.5 | 135.5311 | 1.8315 | 144.6886 | 2.0147 | 1.3553 | 0.018315 | 1.4469 | 0.020147 | 1.337 | 1.4267 | 5.0684 | 2.7455 | 12.1475
38908.4778 | 1427 | 415 | 38908.4778 | 1787 | 591 | 1875 | 1972 | 87.1184 | 25.3358 | 109.0965 | 36.0806 | 0.87118 | 0.25336 | 1.091 | 0.36081 | 0.61783 | 0.73016 | 299.1568 | 60.0314 | 49.207
38908.4785 | 1025 | 874 | 38908.4785 | 1237 | 994 | 1934 | 2031 | 62.5763 | 53.3578 | 75.5189 | 60.6838 | 0.62576 | 0.53358 | 0.75519 | 0.60684 | 0.092186 | 0.14835 | 1792.5971 | 1164.4726 | 51.3542

## C2-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 146.7265 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38908.4553 | 1 | 0 | 38908.4554 | 1 | 0 | -68 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.456 | 1 | 0 | 38908.456 | 1 | 0 | -9 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4567 | 1 | 0 | 38908.4567 | 1 | 0 | 49.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4574 | 1 | 0 | 38908.4574 | 1 | 0 | 108.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4581 | 1 | 0 | 38908.4581 | 1 | 0 | 167.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4587 | 1 | 0 | 38908.4588 | 1 | 0 | 226 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4594 | 1 | 0 | 38908.4594 | 1 | 0 | 285 | 382 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4601 | 1 | 0 | 38908.4601 | 1 | 0 | 343.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4608 | 1 | 0 | 38908.4608 | 1 | 0 | 402.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4615 | 1 | 0 | 38908.4615 | 1 | 0 | 461.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4621 | 1 | 0 | 38908.4622 | 1 | 0 | 520 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4628 | 1 | 0 | 38908.4628 | 1 | 0 | 578.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4635 | 1 | 0 | 38908.4635 | 1 | 0 | 637.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4642 | 1 | 0 | 38908.4642 | 1 | 0 | 696.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4649 | 1 | 0 | 38908.4649 | 1 | 0 | 755.5 | 852.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4655 | 1 | 0 | 38908.4656 | 1 | 0 | 814 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4662 | 1 | 0 | 38908.4662 | 1 | 0 | 873 | 970 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4669 | 1 | 0 | 38908.4669 | 1 | 0 | 931.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4676 | 1 | 0 | 38908.4676 | 1 | 0 | 990.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4683 | 1 | 0 | 38908.4683 | 1 | 0 | 1049 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4689 | 1 | 0 | 38908.469 | 1 | 0 | 1108 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4696 | 1 | 0 | 38908.4696 | 1 | 0 | 1166.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240238 | 240238 | 240237.9994
38908.4703 | 352 | 536 | 38908.4703 | 660 | 642 | 1225.5 | 1322.5 | 21.4896 | 32.7228 | 40.293 | 39.1941 | 0.2149 | 0.32723 | 0.40293 | 0.39194 | 0.11233 | 0.010989 | 1038.8526 | 3980.4151 | 275.7914
38908.471 | 867 | 948 | 38908.471 | 1109 | 852 | 1284.5 | 1381.5 | 52.9304 | 57.8755 | 67.7045 | 52.0147 | 0.5293 | 0.57875 | 0.67705 | 0.52015 | 0.049451 | 0.1569 | 850.8921 | 952.1793 | 56.1667
38908.4717 | 899 | 866 | 38908.4717 | 1040 | 1006 | 1343 | 1440 | 54.884 | 52.8694 | 63.4921 | 61.4164 | 0.54884 | 0.52869 | 0.63492 | 0.61416 | 0.020147 | 0.020757 | 7588.6321 | 6572.6191 | 72.6112
38908.4723 | 969 | 916 | 38908.4724 | 1022 | 967 | 1402 | 1499 | 59.1575 | 55.9219 | 62.3932 | 59.0354 | 0.59158 | 0.55922 | 0.62393 | 0.59035 | 0.032357 | 0.033578 | 4798.5159 | 3964.0225 | 55.1992
38908.473 | 1028 | 942 | 38908.473 | 1094 | 931 | 1460.5 | 1557.5 | 62.7595 | 57.5092 | 66.7888 | 56.8376 | 0.62759 | 0.57509 | 0.66789 | 0.56838 | 0.052503 | 0.099512 | 2256.7377 | 3759.8032 | 44.8144
38908.4737 | 2282 | 72 | 38908.4737 | 2272 | 96 | 1519.5 | 1616.5 | 139.3162 | 4.3956 | 138.7057 | 5.8608 | 1.3932 | 0.043956 | 1.3871 | 0.058608 | 1.3492 | 1.3284 | 6.7587 | 17.3872 | 10.1585
38908.4744 | 1972 | 173 | 38908.4744 | 2233 | 107 | 1578.5 | 1675.5 | 120.3907 | 10.5617 | 136.3248 | 6.5324 | 1.2039 | 0.10562 | 1.3632 | 0.065324 | 1.0983 | 1.2979 | 89.7252 | 13.1237 | 17.3267
38908.4751 | 2354 | 23 | 38908.4751 | 1959 | 19 | 1637 | 1734 | 143.7118 | 1.4042 | 119.5971 | 1.16 | 1.4371 | 0.014042 | 1.196 | 0.0116 | 1.4231 | 1.1844 | 2.1697 | 41.7535 | 33.7836
38908.4758 | 2370 | 12 | 38908.4758 | 2362 | 11 | 1696 | 1793 | 144.6886 | 0.7326 | 144.2002 | 0.67155 | 1.4469 | 0.007326 | 1.442 | 0.0067155 | 1.4396 | 1.4353 | 1.8011 | 2.3778 | 4.1381
38908.4764 | 2387 | 9 | 38908.4764 | 1882 | 9 | 1754.5 | 1851.5 | 145.7265 | 0.54945 | 114.8962 | 0.54945 | 1.4573 | 0.0054945 | 1.149 | 0.0054945 | 1.4518 | 1.1435 | 0.69169 | 91.1774 | 39.1079
38908.4771 | 2022 | 17 | 38908.4771 | 1934 | 20 | 1813.5 | 1910.5 | 123.4432 | 1.0379 | 118.0708 | 1.221 | 1.2344 | 0.010379 | 1.1807 | 0.01221 | 1.2241 | 1.1685 | 19.6652 | 25.8997 | 440.9364
38908.4778 | 1485 | 518 | 38908.4778 | 1577 | 625 | 1872 | 1969 | 90.6593 | 31.6239 | 96.2759 | 38.1563 | 0.90659 | 0.31624 | 0.96276 | 0.38156 | 0.59035 | 0.5812 | 142.2283 | 161.2242 | 47.7045
38908.4785 | 1256 | 1031 | 38908.4785 | 976 | 892 | 1931 | 2028 | 76.6789 | 62.9426 | 59.5849 | 54.4567 | 0.76679 | 0.62943 | 0.59585 | 0.54457 | 0.13736 | 0.051282 | 306.1502 | 688.3577 | 9.8562

## C2-6
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 147.8864 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38908.4553 | 1 | 0 | 38908.4553 | 1 | 0 | -70.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.456 | 1 | 0 | 38908.456 | 1 | 0 | -12 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4567 | 1 | 0 | 38908.4567 | 1 | 0 | 47 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4573 | 1 | 0 | 38908.4574 | 1 | 0 | 105.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.458 | 1 | 0 | 38908.458 | 1 | 0 | 164.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4587 | 1 | 0 | 38908.4587 | 1 | 0 | 223.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4594 | 1 | 0 | 38908.4594 | 1 | 0 | 282 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4601 | 1 | 0 | 38908.4601 | 1 | 0 | 340.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4608 | 1 | 0 | 38908.4608 | 1 | 0 | 399.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4614 | 1 | 0 | 38908.4614 | 1 | 0 | 458.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4621 | 1 | 0 | 38908.4621 | 1 | 0 | 517.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4628 | 1 | 0 | 38908.4628 | 1 | 0 | 576 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4635 | 1 | 0 | 38908.4635 | 1 | 0 | 635 | 732 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4642 | 1 | 0 | 38908.4642 | 1 | 0 | 693.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4648 | 1 | 0 | 38908.4648 | 1 | 0 | 752.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4655 | 1 | 0 | 38908.4655 | 1 | 0 | 811.5 | 908.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4662 | 1 | 0 | 38908.4662 | 1 | 0 | 870 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4669 | 1 | 0 | 38908.4669 | 1 | 0 | 928.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4676 | 1 | 0 | 38908.4676 | 1 | 0 | 987.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4682 | 1 | 0 | 38908.4683 | 1 | 0 | 1046.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4689 | 1 | 0 | 38908.4689 | 1 | 0 | 1105 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4696 | 1 | 0 | 38908.4696 | 1 | 0 | 1164 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4703 | 1 | 0 | 38908.4703 | 38 | 32 | 1222.5 | 1319.5 | 0.06105 | 0 | 2.3199 | 1.9536 | 0.0006105 | 0 | 0.023199 | 0.019536 | 0.0006105 | 0.003663 | 242138 | 40273 | 242137.9994
38908.471 | 908 | 876 | 38908.471 | 935 | 906 | 1281.5 | 1378.5 | 55.4335 | 53.4799 | 57.0818 | 55.3114 | 0.55433 | 0.5348 | 0.57082 | 0.55311 | 0.019536 | 0.017705 | 6573.504 | 9774.2082 | 72.1364
38908.4716 | 1074 | 1042 | 38908.4717 | 948 | 1052 | 1340.5 | 1437.5 | 65.5678 | 63.6142 | 57.8755 | 64.2247 | 0.65568 | 0.63614 | 0.57875 | 0.64225 | 0.019536 | 0.063492 | 1457.5453 | 1722.02 | 27.7893
38908.4723 | 740 | 740 | 38908.4723 | 1032 | 882 | 1399 | 1496 | 45.177 | 45.177 | 63.0037 | 53.8462 | 0.45177 | 0.45177 | 0.63004 | 0.53846 | 0 | 0.091575 | 1519.3401 | 668.2864 | 110.773
38908.473 | 1159 | 1069 | 38908.473 | 1036 | 1003 | 1458 | 1555 | 70.757 | 65.2625 | 63.2479 | 61.2332 | 0.70757 | 0.65263 | 0.63248 | 0.61233 | 0.054945 | 0.020147 | 759.038 | 1398.393 | 16.9698
38908.4737 | 2024 | 61 | 38908.4737 | 2074 | 64 | 1516.5 | 1613.5 | 123.5653 | 3.7241 | 126.6178 | 3.9072 | 1.2357 | 0.037241 | 1.2662 | 0.039072 | 1.1984 | 1.2271 | 24.0323 | 19.9794 | 92.1014
38908.4744 | 2130 | 186 | 38908.4744 | 1749 | 169 | 1575.5 | 1672.5 | 130.0366 | 11.3553 | 106.7766 | 10.3175 | 1.3004 | 0.11355 | 1.0678 | 0.10317 | 1.1868 | 0.96459 | 16.2976 | 124.0019 | 31.6609
38908.475 | 2131 | 16 | 38908.4751 | 2038 | 21 | 1634.5 | 1731.5 | 130.0977 | 0.9768 | 124.42 | 1.2821 | 1.301 | 0.009768 | 1.2442 | 0.012821 | 1.2912 | 1.2314 | 14.3033 | 20.5531 | 293.4346
38908.4757 | 2188 | 9 | 38908.4757 | 2293 | 11 | 1693 | 1790 | 133.5775 | 0.54945 | 139.9878 | 0.67155 | 1.3358 | 0.0054945 | 1.3999 | 0.0067155 | 1.3303 | 1.3932 | 11.5636 | 5.9162 | 139.8794
38908.4764 | 2016 | 9 | 38908.4764 | 2359 | 9 | 1752 | 1849 | 123.0769 | 0.54945 | 144.0171 | 0.54945 | 1.2308 | 0.0054945 | 1.4402 | 0.0054945 | 1.2253 | 1.4347 | 24.2098 | 2.7404 | 117.7692
38908.4771 | 2406 | 22 | 38908.4771 | 2093 | 22 | 1810.5 | 1907.5 | 146.8864 | 1.3431 | 127.7778 | 1.3431 | 1.4689 | 0.013431 | 1.2778 | 0.013431 | 1.4554 | 1.2643 | 0.66397 | 26.5114 | 5.3532
38908.4778 | 1579 | 583 | 38908.4778 | 1758 | 577 | 1869.5 | 1966.5 | 96.398 | 35.5922 | 107.326 | 35.2259 | 0.96398 | 0.35592 | 1.0733 | 0.35226 | 0.60806 | 0.721 | 835.5577 | 65.135 | 17.6163
38908.4784 | 1126 | 882 | 38908.4785 | 1249 | 1085 | 1928 | 2025 | 68.7424 | 53.8462 | 76.2515 | 66.2393 | 0.68742 | 0.53846 | 0.76252 | 0.66239 | 0.14896 | 0.10012 | 398.2701 | 1082.1725 | 43.0077

## C2-5
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 148.9853 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38908.4553 | 1 | 0 | 38908.4553 | 1 | 0 | -73.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.456 | 1 | 0 | 38908.456 | 1 | 0 | -14.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4566 | 1 | 0 | 38908.4567 | 1 | 0 | 44 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4573 | 1 | 0 | 38908.4573 | 1 | 0 | 103 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.458 | 1 | 0 | 38908.458 | 1 | 0 | 161.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4587 | 1 | 0 | 38908.4587 | 1 | 0 | 220.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4594 | 1 | 0 | 38908.4594 | 1 | 0 | 279.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.46 | 1 | 0 | 38908.4601 | 1 | 0 | 338 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4607 | 1 | 0 | 38908.4607 | 1 | 0 | 396.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4614 | 1 | 0 | 38908.4614 | 1 | 0 | 455.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4621 | 1 | 0 | 38908.4621 | 1 | 0 | 514.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4628 | 1 | 0 | 38908.4628 | 1 | 0 | 573.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4634 | 1 | 0 | 38908.4635 | 1 | 0 | 632 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4641 | 1 | 0 | 38908.4641 | 1 | 0 | 690.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4648 | 1 | 0 | 38908.4648 | 1 | 0 | 749.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4655 | 1 | 0 | 38908.4655 | 1 | 0 | 808.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4662 | 1 | 0 | 38908.4662 | 1 | 0 | 867 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4668 | 1 | 0 | 38908.4669 | 1 | 0 | 926 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4675 | 1 | 0 | 38908.4675 | 1 | 0 | 984.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4682 | 1 | 0 | 38908.4682 | 1 | 0 | 1043.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4689 | 1 | 0 | 38908.4689 | 1 | 0 | 1102.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4696 | 1 | 0 | 38908.4696 | 1 | 0 | 1161 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4702 | 1 | 0 | 38908.4703 | 1 | 0 | 1220 | 1317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38908.4709 | 733 | 818 | 38908.4709 | 792 | 761 | 1278.5 | 1375.5 | 44.7497 | 49.9389 | 48.3516 | 46.4591 | 0.4475 | 0.49939 | 0.48352 | 0.46459 | 0.051893 | 0.018926 | 1910.0923 | 18644.7093 | 108.1461
38908.4716 | 516 | 498 | 38908.4716 | 394 | 385 | 1337.5 | 1434.5 | 31.5018 | 30.4029 | 24.0537 | 23.5043 | 0.31502 | 0.30403 | 0.24054 | 0.23504 | 0.010989 | 0.0054945 | 11579.4556 | 36058.6322 | 285.6296
38908.4723 | 347 | 303 | 38908.4723 | 339 | 291 | 1396.5 | 1493.5 | 21.1844 | 18.4982 | 20.696 | 17.7656 | 0.21184 | 0.18498 | 0.20696 | 0.17766 | 0.026862 | 0.029304 | 5532.5915 | 4916.6291 | 579.106
38908.473 | 962 | 894 | 38908.473 | 1069 | 929 | 1455 | 1552 | 58.7302 | 54.5788 | 65.2625 | 56.7155 | 0.5873 | 0.54579 | 0.65263 | 0.56716 | 0.041514 | 0.08547 | 3751.2968 | 3126.9498 | 63.3412
38908.4736 | 2285 | 84 | 38908.4737 | 2166 | 80 | 1514 | 1611 | 139.4994 | 5.1282 | 132.2344 | 4.884 | 1.395 | 0.051282 | 1.3223 | 0.04884 | 1.3437 | 1.2735 | 8.3775 | 24.2587 | 16.5897
38908.4743 | 1798 | 225 | 38908.4743 | 2036 | 205 | 1572.5 | 1669.5 | 109.768 | 13.7363 | 124.2979 | 12.5153 | 1.0977 | 0.13736 | 1.243 | 0.12515 | 0.96032 | 1.1178 | 95.3264 | 25.0243 | 37.1293
38908.475 | 2326 | 23 | 38908.475 | 1971 | 21 | 1631.5 | 1728.5 | 142.0024 | 1.4042 | 120.3297 | 1.2821 | 1.42 | 0.014042 | 1.2033 | 0.012821 | 1.406 | 1.1905 | 5.1349 | 30.4587 | 92.7602
38908.4757 | 2419 | 9 | 38908.4757 | 1926 | 10 | 1690 | 1787 | 147.6801 | 0.54945 | 117.5824 | 0.6105 | 1.4768 | 0.0054945 | 1.1758 | 0.006105 | 1.4713 | 1.1697 | 0.89229 | 64.6786 | 54.0258
38908.4764 | 2424 | 9 | 38908.4764 | 1934 | 10 | 1749 | 1846 | 147.9853 | 0.54945 | 118.0708 | 0.6105 | 1.4799 | 0.0054945 | 1.1807 | 0.006105 | 1.4744 | 1.1746 | 0.68054 | 111.3968 | 43.2104
38908.477 | 2206 | 20 | 38908.4771 | 2355 | 23 | 1807.5 | 1904.5 | 134.6764 | 1.221 | 143.7729 | 1.4042 | 1.3468 | 0.01221 | 1.4377 | 0.014042 | 1.3346 | 1.4237 | 13.9652 | 3.9395 | 40.6266
38908.4777 | 1912 | 116 | 38908.4777 | 1910 | 265 | 1866.5 | 1963.5 | 116.7277 | 7.0818 | 116.6056 | 16.1783 | 1.1673 | 0.070818 | 1.1661 | 0.16178 | 1.0965 | 1.0043 | 32.7541 | 63.447 | 137.9983
38908.4784 | 1219 | 1105 | 38908.4784 | 1063 | 913 | 1925.5 | 2022.5 | 74.42 | 67.4603 | 64.8962 | 55.7387 | 0.7442 | 0.6746 | 0.64896 | 0.55739 | 0.069597 | 0.091575 | 7715.2489 | 1125.6068 | 9.6728

## C2-4
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 139.4005 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38908.4552 | 1 | 0 | 38908.4553 | 1 | 0 | -76.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4559 | 1 | 0 | 38908.4559 | 1 | 0 | -17.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4566 | 1 | 0 | 38908.4566 | 1 | 0 | 41.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4573 | 1 | 0 | 38908.4573 | 1 | 0 | 100 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.458 | 1 | 0 | 38908.458 | 1 | 0 | 159 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4586 | 1 | 0 | 38908.4587 | 1 | 0 | 217.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4593 | 1 | 0 | 38908.4593 | 2 | 0 | 276.5 | 373.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 228238 | 114069 | 228237.9994
38908.46 | 1 | 0 | 38908.46 | 1 | 0 | 335 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4607 | 1 | 0 | 38908.4607 | 1 | 0 | 394 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4614 | 1 | 0 | 38908.4614 | 1 | 0 | 452.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.462 | 1 | 0 | 38908.4621 | 1 | 0 | 511.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4627 | 1 | 0 | 38908.4627 | 1 | 0 | 570.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4634 | 1 | 0 | 38908.4634 | 1 | 0 | 629 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4641 | 1 | 0 | 38908.4641 | 1 | 0 | 688 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4648 | 1 | 0 | 38908.4648 | 1 | 0 | 746.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4655 | 1 | 0 | 38908.4655 | 1 | 0 | 805.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4661 | 1 | 0 | 38908.4661 | 1 | 0 | 864.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4668 | 1 | 0 | 38908.4668 | 1 | 0 | 923.5 | 1020.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4675 | 1 | 0 | 38908.4675 | 1 | 0 | 982 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4682 | 1 | 0 | 38908.4682 | 1 | 0 | 1040.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4689 | 1 | 0 | 38908.4689 | 1 | 0 | 1099.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4695 | 1 | 0 | 38908.4695 | 1 | 0 | 1158.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4702 | 1 | 0 | 38908.4702 | 1 | 0 | 1217 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228238 | 228238 | 228237.9994
38908.4709 | 2 | 0 | 38908.4709 | 1 | 0 | 1276 | 1373 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 114069 | 228238 | 114068.9988
38908.4716 | 79 | 76 | 38908.4716 | 298 | 293 | 1334.5 | 1431.5 | 4.823 | 4.6398 | 18.1929 | 17.8877 | 0.04823 | 0.046398 | 0.18193 | 0.17888 | 0.0018315 | 0.0030525 | 78087.4218 | 42929.1816 | 2793.9916
38908.4723 | 886 | 838 | 38908.4723 | 893 | 842 | 1393.5 | 1490.5 | 54.0904 | 51.16 | 54.5177 | 51.4042 | 0.5409 | 0.5116 | 0.54518 | 0.51404 | 0.029304 | 0.031136 | 5155.3368 | 4010.6255 | 65.1279
38908.4729 | 892 | 832 | 38908.473 | 1161 | 1046 | 1452.5 | 1549.5 | 54.4567 | 50.7937 | 70.8791 | 63.8584 | 0.54457 | 0.50794 | 0.70879 | 0.63858 | 0.03663 | 0.070208 | 2439.8497 | 27987.8706 | 66.9938
38908.4736 | 2051 | 73 | 38908.4736 | 2047 | 75 | 1511 | 1608 | 125.2137 | 4.4567 | 124.9695 | 4.5788 | 1.2521 | 0.044567 | 1.2497 | 0.045788 | 1.2076 | 1.2039 | 15.2826 | 15.9582 | 30.0465
38908.4743 | 1490 | 807 | 38908.4743 | 1364 | 586 | 1570 | 1667 | 90.9646 | 49.2674 | 83.2723 | 35.7753 | 0.90965 | 0.49267 | 0.83272 | 0.35775 | 0.41697 | 0.47497 | 283317.5441 | 118.2037 | 0.91427
38908.475 | 2026 | 24 | 38908.475 | 2267 | 27 | 1628.5 | 1725.5 | 123.6874 | 1.4652 | 138.4005 | 1.6484 | 1.2369 | 0.014652 | 1.384 | 0.016484 | 1.2222 | 1.3675 | 17.0165 | 4.9033 | 45.4519
38908.4757 | 2255 | 11 | 38908.4757 | 2245 | 9 | 1687.5 | 1784.5 | 137.6679 | 0.67155 | 137.0574 | 0.54945 | 1.3767 | 0.0067155 | 1.3706 | 0.0054945 | 1.37 | 1.3651 | 1.6094 | 2.2889 | 3.5356
38908.4763 | 2055 | 11 | 38908.4764 | 1845 | 10 | 1746 | 1843 | 125.4579 | 0.67155 | 112.6374 | 0.6105 | 1.2546 | 0.0067155 | 1.1264 | 0.006105 | 1.2479 | 1.1203 | 11.4181 | 25.0873 | 396.3394
38908.477 | 1984 | 17 | 38908.477 | 2199 | 22 | 1805 | 1902 | 121.1233 | 1.0379 | 134.2491 | 1.3431 | 1.2112 | 0.010379 | 1.3425 | 0.013431 | 1.2009 | 1.3291 | 19.2978 | 4.0902 | 65.2704
38908.4777 | 1885 | 65 | 38908.4777 | 2056 | 95 | 1864 | 1961 | 115.0794 | 3.9683 | 125.5189 | 5.7998 | 1.1508 | 0.039683 | 1.2552 | 0.057998 | 1.1111 | 1.1972 | 29.4757 | 13.8756 | 62.4954
38908.4784 | 1060 | 978 | 38908.4784 | 1252 | 1119 | 1922.5 | 2019.5 | 64.7131 | 59.707 | 76.4347 | 68.315 | 0.64713 | 0.59707 | 0.76435 | 0.68315 | 0.050061 | 0.081197 | 367.8782 | 390.3408 | 19.9731

## C2-3
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 141.5983 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38908.4552 | 1 | 0 | 38908.4552 | 1 | 0 | -79 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4559 | 1 | 0 | 38908.4559 | 1 | 0 | -20.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4566 | 1 | 0 | 38908.4566 | 1 | 0 | 38.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4573 | 1 | 0 | 38908.4573 | 1 | 0 | 97.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4579 | 1 | 0 | 38908.458 | 1 | 0 | 156 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4586 | 1 | 0 | 38908.4586 | 1 | 0 | 215 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4593 | 1 | 0 | 38908.4593 | 1 | 0 | 273.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.46 | 1 | 0 | 38908.46 | 1 | 0 | 332.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4607 | 1 | 0 | 38908.4607 | 1 | 0 | 391.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4613 | 1 | 0 | 38908.4614 | 1 | 0 | 450 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.462 | 1 | 0 | 38908.462 | 1 | 0 | 509 | 606 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4627 | 1 | 0 | 38908.4627 | 1 | 0 | 567.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4634 | 1 | 0 | 38908.4634 | 1 | 0 | 626.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4641 | 1 | 0 | 38908.4641 | 1 | 0 | 685.5 | 782.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4647 | 1 | 0 | 38908.4648 | 1 | 0 | 744 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4654 | 1 | 0 | 38908.4654 | 1 | 0 | 802.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4661 | 1 | 0 | 38908.4661 | 1 | 0 | 861.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4668 | 1 | 0 | 38908.4668 | 1 | 0 | 920.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4675 | 1 | 0 | 38908.4675 | 1 | 0 | 979 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4681 | 1 | 0 | 38908.4682 | 1 | 0 | 1038 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4688 | 1 | 0 | 38908.4688 | 1 | 0 | 1096.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4695 | 1 | 0 | 38908.4695 | 1 | 0 | 1155.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231838 | 231838 | 231837.9994
38908.4702 | 1 | 0 | 38908.4702 | 2 | 0 | 1214.5 | 1311.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 231838 | 115869 | 231837.9994
38908.4709 | 2 | 1 | 38908.4709 | 2 | 0 | 1273 | 1370 | 0.1221 | 0.06105 | 0.1221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 0.001221 | 231938.1728 | 115869 | 231438.2587
38908.4715 | 1032 | 1002 | 38908.4716 | 1027 | 1075 | 1332 | 1429 | 63.0037 | 61.1722 | 62.6984 | 65.6288 | 0.63004 | 0.61172 | 0.62698 | 0.65629 | 0.018315 | 0.029304 | 6291.2529 | 10506.4648 | 28.2125
38908.4722 | 988 | 1008 | 38908.4722 | 1042 | 991 | 1390.5 | 1487.5 | 60.3175 | 61.5385 | 63.6142 | 60.5006 | 0.60317 | 0.61538 | 0.63614 | 0.60501 | 0.01221 | 0.031136 | 2713.6092 | 3468.3189 | 31.1823
38908.4729 | 1064 | 951 | 38908.4729 | 1109 | 992 | 1449.5 | 1546.5 | 64.9573 | 58.0586 | 67.7045 | 60.5617 | 0.64957 | 0.58059 | 0.67705 | 0.60562 | 0.068987 | 0.071429 | 2258.6693 | 1656.2321 | 30.1839
38908.4736 | 2175 | 62 | 38908.4736 | 1820 | 74 | 1508.5 | 1605.5 | 132.7839 | 3.7851 | 111.1111 | 4.5177 | 1.3278 | 0.037851 | 1.1111 | 0.045177 | 1.29 | 1.0659 | 7.1296 | 70.5272 | 54.9532
38908.4743 | 1519 | 676 | 38908.4743 | 1434 | 814 | 1567 | 1664 | 92.735 | 41.2698 | 87.5458 | 49.6947 | 0.92735 | 0.4127 | 0.87546 | 0.49695 | 0.51465 | 0.37851 | 48.3954 | 83.3708 | 8.3654
38908.4749 | 2041 | 26 | 38908.475 | 1959 | 25 | 1626 | 1723 | 124.6032 | 1.5873 | 119.5971 | 1.5263 | 1.246 | 0.015873 | 1.196 | 0.015263 | 1.2302 | 1.1807 | 14.747 | 20.4242 | 164.6316
38908.4756 | 2029 | 10 | 38908.4756 | 2288 | 12 | 1684.5 | 1781.5 | 123.8706 | 0.6105 | 139.6825 | 0.7326 | 1.2387 | 0.006105 | 1.3968 | 0.007326 | 1.2326 | 1.3895 | 22.1502 | 1.4124 | 39.0481
38908.4763 | 1868 | 9 | 38908.4763 | 2197 | 12 | 1743.5 | 1840.5 | 114.0415 | 0.54945 | 134.127 | 0.7326 | 1.1404 | 0.0054945 | 1.3413 | 0.007326 | 1.1349 | 1.3339 | 26.5262 | 5.7193 | 265.9155
38908.477 | 2199 | 20 | 38908.477 | 2247 | 21 | 1802.5 | 1899.5 | 134.2491 | 1.221 | 137.1795 | 1.2821 | 1.3425 | 0.01221 | 1.3718 | 0.012821 | 1.3303 | 1.359 | 7.3263 | 3.7322 | 18.0577
38908.4777 | 2024 | 58 | 38908.4777 | 2303 | 75 | 1861 | 1958 | 123.5653 | 3.5409 | 140.5983 | 4.5788 | 1.2357 | 0.035409 | 1.406 | 0.045788 | 1.2002 | 1.3602 | 0.50332 | 0.10226 | 0.41808
38908.4783 | 1040 | 866 | 38908.4784 | 1167 | 1009 | 1920 | 2017 | 63.4921 | 52.8694 | 71.2454 | 61.5995 | 0.63492 | 0.52869 | 0.71245 | 0.616 | 0.10623 | 0.096459 | 942.9652 | 2259.6968 | 45.7115

## C1-7
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 144.8339 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38908.4552 | 1 | 0 | 38908.4552 | 1 | 0 | -82 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4559 | 1 | 0 | 38908.4559 | 1 | 0 | -23 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4565 | 1 | 0 | 38908.4566 | 1 | 0 | 35.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4572 | 1 | 0 | 38908.4572 | 2 | 0 | 94.5 | 191.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 237138 | 118519 | 237137.9994
38908.4579 | 1 | 0 | 38908.4579 | 1 | 0 | 153.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4586 | 1 | 0 | 38908.4586 | 1 | 0 | 212 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4593 | 1 | 0 | 38908.4593 | 1 | 0 | 271 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4599 | 1 | 0 | 38908.46 | 1 | 0 | 329.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4606 | 1 | 0 | 38908.4606 | 1 | 0 | 388.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4613 | 1 | 0 | 38908.4613 | 1 | 0 | 447 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.462 | 1 | 0 | 38908.462 | 1 | 0 | 506 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4627 | 1 | 0 | 38908.4627 | 1 | 0 | 565 | 662 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4633 | 1 | 0 | 38908.4634 | 1 | 0 | 623.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.464 | 1 | 0 | 38908.464 | 1 | 0 | 682.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4647 | 1 | 0 | 38908.4647 | 1 | 0 | 741.5 | 838.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4654 | 1 | 0 | 38908.4654 | 1 | 0 | 800 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4661 | 1 | 0 | 38908.4661 | 1 | 0 | 859 | 956 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4667 | 1 | 0 | 38908.4668 | 1 | 0 | 917.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4674 | 1 | 0 | 38908.4674 | 1 | 0 | 976.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4681 | 1 | 0 | 38908.4681 | 1 | 0 | 1035 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4688 | 1 | 0 | 38908.4688 | 1 | 0 | 1094 | 1191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4695 | 1 | 0 | 38908.4695 | 1 | 0 | 1152.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4702 | 1 | 0 | 38908.4702 | 1 | 0 | 1211.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237138 | 237138 | 237137.9994
38908.4708 | 26 | 24 | 38908.4708 | 114 | 124 | 1270.5 | 1367.5 | 1.5873 | 1.4652 | 6.9597 | 7.5702 | 0.015873 | 0.014652 | 0.069597 | 0.075702 | 0.001221 | 0.006105 | 123833.034 | 22812.2299 | 9634.3501
38908.4715 | 1053 | 1020 | 38908.4715 | 1001 | 1038 | 1329 | 1426 | 64.2857 | 62.2711 | 61.1111 | 63.37 | 0.64286 | 0.62271 | 0.61111 | 0.6337 | 0.020147 | 0.022589 | 9987.4572 | 5154.2145 | 28.7924
38908.4722 | 822 | 777 | 38908.4722 | 872 | 882 | 1388 | 1485 | 50.1832 | 47.4359 | 53.2357 | 53.8462 | 0.50183 | 0.47436 | 0.53236 | 0.53846 | 0.027473 | 0.006105 | 2746.3176 | 6784.2205 | 98.0883
38908.4729 | 935 | 925 | 38908.4729 | 966 | 926 | 1446.5 | 1543.5 | 57.0818 | 56.4713 | 58.9744 | 56.5324 | 0.57082 | 0.56471 | 0.58974 | 0.56532 | 0.006105 | 0.02442 | 5079.0998 | 5054.6733 | 54.3178
38908.4736 | 2142 | 78 | 38908.4736 | 1785 | 66 | 1505.5 | 1602.5 | 130.7692 | 4.7619 | 108.9744 | 4.0293 | 1.3077 | 0.047619 | 1.0897 | 0.040293 | 1.2601 | 1.0495 | 12.0724 | 50.1051 | 65.2108
38908.4742 | 1196 | 651 | 38908.4742 | 1486 | 657 | 1564.5 | 1661.5 | 73.0159 | 39.7436 | 90.7204 | 40.1099 | 0.73016 | 0.39744 | 0.9072 | 0.4011 | 0.33272 | 0.50611 | 1086.5584 | 149.0612 | 48.3004
38908.4749 | 2339 | 42 | 38908.4749 | 2354 | 44 | 1623 | 1720 | 142.7961 | 2.5641 | 143.7118 | 2.6862 | 1.428 | 0.025641 | 1.4371 | 0.026862 | 1.4023 | 1.4103 | 2.2526 | 5.1522 | 1.0056
38908.4756 | 2319 | 18 | 38908.4756 | 1887 | 16 | 1682 | 1779 | 141.5751 | 1.0989 | 115.2015 | 0.9768 | 1.4158 | 0.010989 | 1.152 | 0.009768 | 1.4048 | 1.1422 | 2.3654 | 40.6318 | 56.7895
38908.4763 | 2356 | 14 | 38908.4763 | 1870 | 13 | 1740.5 | 1837.5 | 143.8339 | 0.8547 | 114.1636 | 0.79365 | 1.4383 | 0.008547 | 1.1416 | 0.0079365 | 1.4298 | 1.1337 | 0.69939 | 28394.4404 | 16.9403
38908.477 | 1843 | 19 | 38908.477 | 2092 | 23 | 1799.5 | 1896.5 | 112.5153 | 1.16 | 127.7167 | 1.4042 | 1.1252 | 0.0116 | 1.2772 | 0.014042 | 1.1136 | 1.2631 | 31.3472 | 14.0497 | 330.9126
38908.4776 | 1865 | 47 | 38908.4777 | 1822 | 49 | 1858.5 | 1955.5 | 113.8584 | 2.8694 | 111.2332 | 2.9915 | 1.1386 | 0.028694 | 1.1123 | 0.029915 | 1.1099 | 1.0824 | 30.1931 | 34.17 | 249.4642
38908.4783 | 1186 | 998 | 38908.4783 | 989 | 873 | 1917 | 2014 | 72.4054 | 60.928 | 60.3785 | 53.2967 | 0.72405 | 0.60928 | 0.60379 | 0.53297 | 0.11477 | 0.070818 | 533.5556 | 2905.0811 | 18.2476

## C1-6
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 143.3687 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38908.4552 | 1 | 0 | 38908.4552 | 1 | 0 | -84.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4558 | 1 | 0 | 38908.4558 | 1 | 0 | -26 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4565 | 1 | 0 | 38908.4565 | 1 | 0 | 33 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4572 | 1 | 0 | 38908.4572 | 1 | 0 | 91.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4579 | 1 | 0 | 38908.4579 | 1 | 0 | 150.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4586 | 1 | 0 | 38908.4586 | 1 | 0 | 209.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4592 | 1 | 0 | 38908.4592 | 1 | 0 | 268 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4599 | 1 | 0 | 38908.4599 | 1 | 0 | 327 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4606 | 1 | 0 | 38908.4606 | 1 | 0 | 385.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4613 | 1 | 0 | 38908.4613 | 1 | 0 | 444.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4619 | 1 | 0 | 38908.462 | 1 | 0 | 503 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4626 | 1 | 0 | 38908.4627 | 1 | 0 | 562 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4633 | 1 | 0 | 38908.4633 | 1 | 0 | 621 | 718 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.464 | 1 | 0 | 38908.464 | 1 | 0 | 679.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4647 | 1 | 0 | 38908.4647 | 1 | 0 | 738.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4654 | 1 | 0 | 38908.4654 | 1 | 0 | 797.5 | 894.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.466 | 1 | 0 | 38908.4661 | 1 | 0 | 856 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4667 | 1 | 0 | 38908.4667 | 1 | 0 | 914.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4674 | 1 | 0 | 38908.4674 | 1 | 0 | 973.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4681 | 1 | 0 | 38908.4681 | 1 | 0 | 1032.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4688 | 1 | 0 | 38908.4688 | 1 | 0 | 1091 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4694 | 1 | 0 | 38908.4695 | 1 | 0 | 1150 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4701 | 1 | 0 | 38908.4701 | 1 | 0 | 1208.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234738 | 234738 | 234737.9994
38908.4708 | 4 | 2 | 38908.4708 | 11 | 9 | 1267.5 | 1364.5 | 0.2442 | 0.1221 | 0.67155 | 0.54945 | 0.002442 | 0.001221 | 0.0067155 | 0.0054945 | 0.001221 | 0.001221 | 117319 | 117319 | 117019.2555
38908.4715 | 1013 | 978 | 38908.4715 | 1099 | 1069 | 1326.5 | 1423.5 | 61.8437 | 59.707 | 67.094 | 65.2625 | 0.61844 | 0.59707 | 0.67094 | 0.65263 | 0.021368 | 0.018315 | 4329.3166 | 23538.2053 | 36.3873
38908.4722 | 244 | 213 | 38908.4722 | 187 | 166 | 1385 | 1482 | 14.8962 | 13.0037 | 11.4164 | 10.1343 | 0.14896 | 0.13004 | 0.11416 | 0.10134 | 0.018926 | 0.012821 | 7217.372 | 11558.1856 | 880.3551
38908.4728 | 1059 | 1029 | 38908.4729 | 1208 | 1102 | 1444 | 1541 | 64.652 | 62.8205 | 73.7485 | 67.2772 | 0.64652 | 0.62821 | 0.73748 | 0.67277 | 0.018315 | 0.064713 | 449.3902 | 400.5173 | 20.2486
38908.4735 | 1881 | 55 | 38908.4735 | 1999 | 57 | 1502.5 | 1599.5 | 114.8352 | 3.3578 | 122.0391 | 3.4799 | 1.1484 | 0.033578 | 1.2204 | 0.034799 | 1.1148 | 1.1856 | 30.1527 | 19.9308 | 124.6033
38908.4742 | 1520 | 611 | 38908.4742 | 1613 | 643 | 1561.5 | 1658.5 | 92.7961 | 37.3016 | 98.4737 | 39.2552 | 0.92796 | 0.37302 | 0.98474 | 0.39255 | 0.55495 | 0.59219 | 285.3937 | 98.7489 | 17.6769
38908.4749 | 2126 | 37 | 38908.4749 | 1884 | 37 | 1620.5 | 1717.5 | 129.7924 | 2.2589 | 115.0183 | 2.2589 | 1.2979 | 0.022589 | 1.1502 | 0.022589 | 1.2753 | 1.1276 | 11.3002 | 30.5599 | 117.2744
38908.4756 | 2230 | 14 | 38908.4756 | 2196 | 19 | 1679 | 1776 | 136.1416 | 0.8547 | 134.0659 | 1.16 | 1.3614 | 0.008547 | 1.3407 | 0.0116 | 1.3529 | 1.3291 | 5.7855 | 8.243 | 56.7775
38908.4762 | 1999 | 13 | 38908.4763 | 2137 | 17 | 1738 | 1835 | 122.0391 | 0.79365 | 130.464 | 1.0379 | 1.2204 | 0.0079365 | 1.3046 | 0.010379 | 1.2125 | 1.2943 | 18.7719 | 10.4157 | 244.0866
38908.4769 | 2332 | 26 | 38908.4769 | 1908 | 22 | 1796.5 | 1893.5 | 142.3687 | 1.5873 | 116.4835 | 1.3431 | 1.4237 | 0.015873 | 1.1648 | 0.013431 | 1.4078 | 1.1514 | 0.68718 | 33.4761 | 9.2797
38908.4776 | 2259 | 61 | 38908.4776 | 2311 | 65 | 1855.5 | 1952.5 | 137.9121 | 3.7241 | 141.0867 | 3.9683 | 1.3791 | 0.037241 | 1.4109 | 0.039683 | 1.3419 | 1.3712 | 1.1377 | 1.0781 | 0.49623
38908.4783 | 1201 | 912 | 38908.4783 | 1167 | 1052 | 1914.5 | 2011.5 | 73.3211 | 55.6777 | 71.2454 | 64.2247 | 0.73321 | 0.55678 | 0.71245 | 0.64225 | 0.17643 | 0.070208 | 167.443 | 230.1659 | 17.9922

## C1-5
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 142.1477 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38908.4551 | 1 | 0 | 38908.4551 | 1 | 0 | -87.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4558 | 1 | 0 | 38908.4558 | 1 | 0 | -28.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4565 | 1 | 0 | 38908.4565 | 1 | 0 | 30 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4572 | 1 | 0 | 38908.4572 | 1 | 0 | 89 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4578 | 1 | 0 | 38908.4578 | 1 | 0 | 147.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4585 | 1 | 0 | 38908.4585 | 1 | 0 | 206.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4592 | 1 | 0 | 38908.4592 | 1 | 0 | 265.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4599 | 1 | 0 | 38908.4599 | 1 | 0 | 324 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4606 | 1 | 0 | 38908.4606 | 1 | 0 | 383 | 480 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4612 | 1 | 0 | 38908.4613 | 1 | 0 | 441.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4619 | 1 | 0 | 38908.4619 | 1 | 0 | 500.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4626 | 1 | 0 | 38908.4626 | 1 | 0 | 559.5 | 656.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4633 | 1 | 0 | 38908.4633 | 1 | 0 | 618 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.464 | 1 | 0 | 38908.464 | 1 | 0 | 676.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4646 | 1 | 0 | 38908.4647 | 1 | 0 | 735.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4653 | 1 | 0 | 38908.4653 | 1 | 0 | 794.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.466 | 1 | 0 | 38908.466 | 1 | 0 | 853 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4667 | 1 | 0 | 38908.4667 | 1 | 0 | 912 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4674 | 1 | 0 | 38908.4674 | 1 | 0 | 971 | 1068 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.468 | 1 | 0 | 38908.4681 | 1 | 0 | 1029.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4687 | 1 | 0 | 38908.4687 | 1 | 0 | 1088.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4694 | 1 | 0 | 38908.4694 | 1 | 0 | 1147 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4701 | 1 | 0 | 38908.4701 | 1 | 0 | 1206 | 1303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232738 | 232738 | 232737.9994
38908.4708 | 2 | 3 | 38908.4708 | 2 | 2 | 1264.5 | 1361.5 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 232637.7421 | 270601895.2523 | 77445.9714
| 40 | 31 | 38908.4715 | 946 | 977 | 1324 | 1421 | 2.442 | 1.8926 | 57.7534 | 59.6459 | 0.02442 | 0.018926 | 0.57753 | 0.59646 | 0.0054945 | 0.018926 | 27291.0202 | 5041.4901 | 7140.2414
38908.4721 | 78 | 58 | 38908.4721 | 164 | 156 | 1382.5 | 1479.5 | 4.7619 | 3.5409 | 10.0122 | 9.5238 | 0.047619 | 0.035409 | 0.10012 | 0.095238 | 0.01221 | 0.004884 | 11352.6875 | 32665.5674 | 3768.4291
38908.4728 | 993 | 897 | 38908.4728 | 1115 | 1017 | 1441 | 1538 | 60.6227 | 54.7619 | 68.0708 | 62.0879 | 0.60623 | 0.54762 | 0.68071 | 0.62088 | 0.058608 | 0.059829 | 2477.6489 | 2130.4928 | 46.6807
38908.4735 | 2106 | 85 | 38908.4735 | 1770 | 70 | 1500 | 1597 | 128.5714 | 5.1893 | 108.0586 | 4.2735 | 1.2857 | 0.051893 | 1.0806 | 0.042735 | 1.2338 | 1.0379 | 12.0147 | 49.9723 | 53.8546
38908.4742 | 1589 | 715 | 38908.4742 | 1330 | 755 | 1558.5 | 1655.5 | 97.0085 | 43.6508 | 81.1966 | 46.0928 | 0.97009 | 0.43651 | 0.81197 | 0.46093 | 0.53358 | 0.35104 | 42.9848 | 84.5057 | 1.5617
38908.4748 | 1826 | 35 | 38908.4749 | 2261 | 38 | 1617.5 | 1714.5 | 111.4774 | 2.1368 | 138.0342 | 2.3199 | 1.1148 | 0.021368 | 1.3803 | 0.023199 | 1.0934 | 1.3571 | 75.8535 | 3.1009 | 40.1634
38908.4755 | 2198 | 17 | 38908.4755 | 2185 | 21 | 1676.5 | 1773.5 | 134.188 | 1.0379 | 133.3944 | 1.2821 | 1.3419 | 0.010379 | 1.3339 | 0.012821 | 1.3315 | 1.3211 | 6.6456 | 7.7586 | 48.0199
38908.4762 | 1996 | 15 | 38908.4762 | 1880 | 15 | 1735 | 1832 | 121.8559 | 0.91575 | 114.7741 | 0.91575 | 1.2186 | 0.0091575 | 1.1477 | 0.0091575 | 1.2094 | 1.1386 | 17.2979 | 25.2142 | 426.0689
38908.4769 | 1857 | 21 | 38908.4769 | 2107 | 25 | 1794 | 1891 | 113.37 | 1.2821 | 128.6325 | 1.5263 | 1.1337 | 0.012821 | 1.2863 | 0.015263 | 1.1209 | 1.2711 | 28.6242 | 11.0986 | 214.2497
38908.4776 | 2022 | 49 | 38908.4776 | 2312 | 58 | 1852.5 | 1949.5 | 123.4432 | 2.9915 | 141.1477 | 3.5409 | 1.2344 | 0.029915 | 1.4115 | 0.035409 | 1.2045 | 1.3761 | 2.7858 | 0.54294 | 2.8365
38908.4783 | 1181 | 844 | 38908.4783 | 1072 | 790 | 1911.5 | 2008.5 | 72.1001 | 51.5263 | 65.4457 | 48.2295 | 0.721 | 0.51526 | 0.65446 | 0.4823 | 0.20574 | 0.17216 | 417.9172 | 1351.4209 | 33.4689

## C1-4
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 143.2466 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38908.4551 | 1 | 0 | 38908.4551 | 1 | 0 | -90.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4558 | 1 | 0 | 38908.4558 | 1 | 0 | -31.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4564 | 1 | 0 | 38908.4565 | 1 | 0 | 27.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4571 | 1 | 0 | 38908.4571 | 1 | 0 | 86 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4578 | 1 | 0 | 38908.4578 | 1 | 0 | 145 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4585 | 1 | 0 | 38908.4585 | 1 | 0 | 203.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4592 | 1 | 0 | 38908.4592 | 1 | 0 | 262.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4598 | 1 | 0 | 38908.4599 | 1 | 0 | 321.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4605 | 1 | 0 | 38908.4605 | 1 | 0 | 380 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4612 | 1 | 0 | 38908.4612 | 1 | 0 | 438.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4619 | 1 | 0 | 38908.4619 | 1 | 0 | 497.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4626 | 1 | 0 | 38908.4626 | 1 | 0 | 556.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4633 | 1 | 0 | 38908.4633 | 1 | 0 | 615.5 | 712.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4639 | 1 | 0 | 38908.4639 | 1 | 0 | 674 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4646 | 1 | 0 | 38908.4646 | 1 | 0 | 733 | 830 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4653 | 1 | 0 | 38908.4653 | 1 | 0 | 791.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.466 | 1 | 0 | 38908.466 | 1 | 0 | 850.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4667 | 1 | 0 | 38908.4667 | 1 | 0 | 909.5 | 1006.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4673 | 1 | 0 | 38908.4673 | 1 | 0 | 968 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.468 | 1 | 0 | 38908.468 | 1 | 0 | 1026.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4687 | 1 | 0 | 38908.4687 | 1 | 0 | 1085.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4694 | 1 | 0 | 38908.4694 | 1 | 0 | 1144.5 | 1241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.47 | 1 | 0 | 38908.4701 | 1 | 0 | 1203 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
38908.4707 | 2 | 5 | 38908.4708 | 2 | 4 | 1262 | 1359 | 0.1221 | 0.30525 | 0.1221 | 0.2442 | 0.001221 | 0.0030525 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 78256.9845 | 117519.3421 | 46747.8212
38908.4714 | 625 | 658 | 38908.4714 | 463 | 444 | 1320.5 | 1417.5 | 38.1563 | 40.1709 | 28.2662 | 27.1062 | 0.38156 | 0.40171 | 0.28266 | 0.27106 | 0.020147 | 0.0116 | 5941.3655 | 16338.8984 | 160.6248
38908.4721 | 1158 | 1113 | 38908.4721 | 945 | 902 | 1379.5 | 1476.5 | 70.696 | 67.9487 | 57.6923 | 55.0672 | 0.70696 | 0.67949 | 0.57692 | 0.55067 | 0.027473 | 0.026252 | 4350.7309 | 6293.288 | 6.6668
38908.4728 | 1035 | 942 | 38908.4728 | 937 | 986 | 1438.5 | 1535.5 | 63.1868 | 57.5092 | 57.2039 | 60.1954 | 0.63187 | 0.57509 | 0.57204 | 0.60195 | 0.056777 | 0.029915 | 1082.7626 | 3350.6123 | 38.0759
38908.4734 | 1856 | 74 | 38908.4735 | 2153 | 85 | 1497 | 1594 | 113.3089 | 4.5177 | 131.4408 | 5.1893 | 1.1331 | 0.045177 | 1.3144 | 0.051893 | 1.0879 | 1.2625 | 46.2176 | 10.2639 | 52.3764
38908.4741 | 1761 | 709 | 38908.4742 | 1356 | 801 | 1556 | 1653 | 107.5092 | 43.2845 | 82.7839 | 48.9011 | 1.0751 | 0.43284 | 0.82784 | 0.48901 | 0.64225 | 0.33883 | 1.826 | 2.2867 | 0.38979
38908.4748 | 2187 | 49 | 38908.4748 | 1932 | 36 | 1614.5 | 1711.5 | 133.5165 | 2.9915 | 117.9487 | 2.1978 | 1.3352 | 0.029915 | 1.1795 | 0.021978 | 1.3053 | 1.1575 | 8.1055 | 28.5414 | 50.018
38908.4755 | 2254 | 20 | 38908.4755 | 2087 | 20 | 1673.5 | 1770.5 | 137.6068 | 1.221 | 127.4115 | 1.221 | 1.3761 | 0.01221 | 1.2741 | 0.01221 | 1.3639 | 1.2619 | 4.3785 | 16.1083 | 50.2082
38908.4762 | 2239 | 18 | 38908.4762 | 2330 | 20 | 1732.5 | 1829.5 | 136.6911 | 1.0989 | 142.2466 | 1.221 | 1.3669 | 0.010989 | 1.4225 | 0.01221 | 1.3559 | 1.4103 | 26.9015 | 0.98801 | 4.858
38908.4769 | 1885 | 23 | 38908.4769 | 1997 | 24 | 1791 | 1888 | 115.0794 | 1.4042 | 121.917 | 1.4652 | 1.1508 | 0.014042 | 1.2192 | 0.014652 | 1.1368 | 1.2045 | 26.5456 | 18.5585 | 298.3546
38908.4775 | 2016 | 45 | 38908.4775 | 1817 | 45 | 1849.5 | 1946.5 | 123.0769 | 2.7473 | 110.928 | 2.7473 | 1.2308 | 0.027473 | 1.1093 | 0.027473 | 1.2033 | 1.0818 | 17.9389 | 34.8013 | 163.7241
38908.4782 | 1238 | 941 | 38908.4782 | 1138 | 911 | 1908.5 | 2005.5 | 75.58 | 57.4481 | 69.475 | 55.6166 | 0.7558 | 0.57448 | 0.69475 | 0.55617 | 0.18132 | 0.13858 | 331.833 | 2542.0503 | 17.1142

## C1-3
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 148.1917 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38908.455 | 1 | 0 | 38908.4551 | 1 | 0 | -93 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4557 | 1 | 0 | 38908.4557 | 1 | 0 | -34.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4564 | 1 | 0 | 38908.4564 | 1 | 0 | 24.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4571 | 1 | 0 | 38908.4571 | 1 | 0 | 83.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4578 | 1 | 0 | 38908.4578 | 1 | 0 | 142 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4584 | 1 | 0 | 38908.4585 | 1 | 0 | 201 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4591 | 1 | 0 | 38908.4591 | 1 | 0 | 259.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4598 | 1 | 0 | 38908.4598 | 1 | 0 | 318.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4605 | 1 | 0 | 38908.4605 | 1 | 0 | 377.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4612 | 1 | 0 | 38908.4612 | 1 | 0 | 436 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4619 | 1 | 0 | 38908.4619 | 1 | 0 | 495 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4625 | 1 | 0 | 38908.4625 | 1 | 0 | 553.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4632 | 1 | 0 | 38908.4632 | 1 | 0 | 612.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4639 | 1 | 0 | 38908.4639 | 1 | 0 | 671.5 | 768.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4646 | 1 | 0 | 38908.4646 | 1 | 0 | 730 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4653 | 1 | 0 | 38908.4653 | 1 | 0 | 788.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4659 | 1 | 0 | 38908.4659 | 1 | 0 | 847.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4666 | 1 | 0 | 38908.4666 | 1 | 0 | 906.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4673 | 1 | 0 | 38908.4673 | 1 | 0 | 965 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.468 | 1 | 0 | 38908.468 | 1 | 0 | 1024 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4687 | 1 | 0 | 38908.4687 | 1 | 0 | 1082.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.4693 | 1 | 0 | 38908.4694 | 1 | 0 | 1141.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242638 | 242638 | 242637.9994
38908.47 | 1 | 1 | 38908.47 | 1 | 0 | 1200.5 | 1297.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 588731990.44 | 242638 | 242438.0824
38908.4707 | 3 | 8 | 38908.4707 | 2 | 7 | 1259 | 1356 | 0.18315 | 0.4884 | 0.1221 | 0.42735 | 0.0018315 | 0.004884 | 0.001221 | 0.0042735 | 0.0030525 | 0.0030525 | 48647.6 | 48647.6 | 30142.7885
38908.4714 | 810 | 845 | 38908.4714 | 490 | 485 | 1318 | 1415 | 49.4505 | 51.5873 | 29.9145 | 29.6093 | 0.49451 | 0.51587 | 0.29915 | 0.29609 | 0.021368 | 0.0030525 | 4283.6007 | 30643.8346 | 91.1086
38908.4721 | 916 | 923 | 38908.4721 | 1108 | 1064 | 1376.5 | 1473.5 | 55.9219 | 56.3492 | 67.6435 | 64.9573 | 0.55922 | 0.56349 | 0.67643 | 0.64957 | 0.0042735 | 0.026862 | 3225.4002 | 2315.6813 | 61.1076
38908.4727 | 919 | 839 | 38908.4728 | 1104 | 1015 | 1435.5 | 1532.5 | 56.105 | 51.221 | 67.3993 | 61.9658 | 0.56105 | 0.51221 | 0.67399 | 0.61966 | 0.04884 | 0.054335 | 3668.5799 | 2157.7099 | 76.2493
38908.4734 | 2259 | 80 | 38908.4734 | 1682 | 69 | 1494.5 | 1591.5 | 137.9121 | 4.884 | 102.6862 | 4.2125 | 1.3791 | 0.04884 | 1.0269 | 0.042125 | 1.3303 | 0.98474 | 8.0251 | 98.9617 | 54.9492
38908.4741 | 1505 | 688 | 38908.4741 | 1515 | 713 | 1553 | 1650 | 91.8803 | 42.0024 | 92.4908 | 43.5287 | 0.9188 | 0.42002 | 0.92491 | 0.43529 | 0.49878 | 0.48962 | 181.2745 | 223.2539 | 23.5281
38908.4748 | 2281 | 48 | 38908.4748 | 1833 | 43 | 1612 | 1709 | 139.2552 | 2.9304 | 111.9048 | 2.6252 | 1.3926 | 0.029304 | 1.119 | 0.026252 | 1.3632 | 1.0928 | 6.8428 | 51.1691 | 69.3762
38908.4755 | 2356 | 11 | 38908.4755 | 1906 | 12 | 1670.5 | 1767.5 | 143.8339 | 0.67155 | 116.3614 | 0.7326 | 1.4383 | 0.0067155 | 1.1636 | 0.007326 | 1.4316 | 1.1563 | 3.0857 | 34.6406 | 141.2246
38908.4761 | 2411 | 16 | 38908.4762 | 1951 | 13 | 1729.5 | 1826.5 | 147.1917 | 0.9768 | 119.1087 | 0.79365 | 1.4719 | 0.009768 | 1.1911 | 0.0079365 | 1.4621 | 1.1832 | 0.68429 | 1246.2432 | 2.1986
38908.4768 | 2327 | 23 | 38908.4768 | 1873 | 20 | 1788.5 | 1885.5 | 142.0635 | 1.4042 | 114.3468 | 1.221 | 1.4206 | 0.014042 | 1.1435 | 0.01221 | 1.4066 | 1.1313 | 4.4699 | 39.4418 | 95.1623
38908.4775 | 2363 | 39 | 38908.4775 | 1899 | 44 | 1847 | 1944 | 144.2613 | 2.381 | 115.9341 | 2.6862 | 1.4426 | 0.02381 | 1.1593 | 0.026862 | 1.4188 | 1.1325 | 2.7952 | 188.1373 | 42.4915
38908.4782 | 1314 | 1010 | 38908.4782 | 1383 | 771 | 1906 | 2003 | 80.2198 | 61.6606 | 84.4322 | 47.0696 | 0.8022 | 0.61661 | 0.84432 | 0.4707 | 0.18559 | 0.37363 | 127.7596 | 177.9846 | 6.5536

## C1-2
Penlight Test 11 |  |  | 2006-07-10 | 10:57 |  | Vs = |  | 147.8864 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38908.455 | 1 | 0 | 38908.455 | 1 | 0 | -96 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4557 | 1 | 0 | 38908.4557 | 1 | 0 | -37 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4564 | 1 | 0 | 38908.4564 | 1 | 0 | 21.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4571 | 1 | 0 | 38908.4571 | 1 | 0 | 80.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4577 | 1 | 0 | 38908.4578 | 1 | 0 | 139.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4584 | 1 | 0 | 38908.4584 | 1 | 0 | 198 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4591 | 1 | 0 | 38908.4591 | 1 | 0 | 257 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4598 | 1 | 0 | 38908.4598 | 1 | 0 | 315.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4605 | 1 | 0 | 38908.4605 | 1 | 0 | 374.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4611 | 1 | 0 | 38908.4612 | 1 | 0 | 433.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4618 | 1 | 0 | 38908.4618 | 1 | 0 | 492 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4625 | 1 | 0 | 38908.4625 | 1 | 0 | 551 | 648 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4632 | 1 | 0 | 38908.4632 | 1 | 0 | 609.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4639 | 1 | 0 | 38908.4639 | 1 | 0 | 668.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4645 | 1 | 0 | 38908.4646 | 1 | 0 | 727 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4652 | 1 | 0 | 38908.4652 | 1 | 0 | 786 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4659 | 1 | 0 | 38908.4659 | 1 | 0 | 844.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4666 | 1 | 0 | 38908.4666 | 1 | 0 | 903.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4673 | 1 | 0 | 38908.4673 | 1 | 0 | 962.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.468 | 1 | 0 | 38908.468 | 1 | 0 | 1021.5 | 1118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4686 | 1 | 0 | 38908.4686 | 1 | 0 | 1080 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.4693 | 1 | 0 | 38908.4693 | 1 | 0 | 1138.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
38908.47 | 2 | 6 | 38908.47 | 1 | 2 | 1197.5 | 1294.5 | 0.1221 | 0.3663 | 0.06105 | 0.1221 | 0.001221 | 0.003663 | 0.0006105 | 0.001221 | 0.002442 | 0.0006105 | 60546.8838 | 242940.4872 | 40223.1099
38908.4707 | 5 | 14 | 38908.4707 | 4 | 10 | 1256.5 | 1353.5 | 0.30525 | 0.8547 | 0.2442 | 0.6105 | 0.0030525 | 0.008547 | 0.002442 | 0.006105 | 0.0054945 | 0.003663 | 26963.1945 | 40557.0271 | 17124.7761
38908.4713 | 1041 | 1014 | 38908.4714 | 1099 | 1073 | 1315 | 1412 | 63.5531 | 61.9048 | 67.094 | 65.5067 | 0.63553 | 0.61905 | 0.67094 | 0.65507 | 0.016484 | 0.015873 | 7900.5885 | 10656.3204 | 35.8939
38908.472 | 1115 | 1081 | 38908.472 | 891 | 909 | 1374 | 1471 | 68.0708 | 65.9951 | 54.3956 | 55.4945 | 0.68071 | 0.65995 | 0.54396 | 0.55495 | 0.020757 | 0.010989 | 3126.3427 | 13826.7254 | 20.7913
38908.4727 | 1167 | 1080 | 38908.4727 | 932 | 882 | 1432.5 | 1529.5 | 71.2454 | 65.9341 | 56.8987 | 53.8462 | 0.71245 | 0.65934 | 0.56899 | 0.53846 | 0.053114 | 0.030525 | 1213.8463 | 6576.6792 | 15.9957
38908.4734 | 1940 | 76 | 38908.4734 | 2165 | 93 | 1491.5 | 1588.5 | 118.4371 | 4.6398 | 132.1734 | 5.6777 | 1.1844 | 0.046398 | 1.3217 | 0.056777 | 1.138 | 1.265 | 36.3303 | 14.1728 | 66.376
38908.4741 | 1630 | 701 | 38908.4741 | 1339 | 742 | 1550.5 | 1647.5 | 99.5116 | 42.7961 | 81.746 | 45.2991 | 0.99512 | 0.42796 | 0.81746 | 0.45299 | 0.56716 | 0.36447 | 57.5388 | 156.43 | 7.9521
38908.4747 | 1805 | 52 | 38908.4748 | 2091 | 44 | 1609 | 1706 | 110.1954 | 3.1746 | 127.6557 | 2.6862 | 1.102 | 0.031746 | 1.2766 | 0.026862 | 1.0702 | 1.2497 | 42.6374 | 17.048 | 158.3605
38908.4754 | 1917 | 10 | 38908.4755 | 2396 | 9 | 1668 | 1765 | 117.033 | 0.6105 | 146.2759 | 0.54945 | 1.1703 | 0.006105 | 1.4628 | 0.0054945 | 1.1642 | 1.4573 | 50.0892 | 1.1135 | 54.5548
38908.4761 | 2146 | 12 | 38908.4761 | 2406 | 11 | 1726.5 | 1823.5 | 131.0134 | 0.7326 | 146.8864 | 0.67155 | 1.3101 | 0.007326 | 1.4689 | 0.0067155 | 1.3028 | 1.4621 | 70.7186 | 0.6884 | 15.0628
38908.4768 | 1924 | 14 | 38908.4768 | 2280 | 17 | 1785.5 | 1882.5 | 117.4603 | 0.8547 | 139.1941 | 1.0379 | 1.1746 | 0.008547 | 1.3919 | 0.010379 | 1.1661 | 1.3816 | 29.4349 | 6.4564 | 209.8352
38908.4775 | 1983 | 37 | 38908.4775 | 2326 | 42 | 1844 | 1941 | 121.0623 | 2.2589 | 142.0024 | 2.5641 | 1.2106 | 0.022589 | 1.42 | 0.025641 | 1.188 | 1.3944 | 39.587 | 4.4254 | 46.0868
38908.4781 | 1270 | 765 | 38908.4782 | 1306 | 993 | 1903 | 2000 | 77.5336 | 46.7033 | 79.7314 | 60.6227 | 0.77534 | 0.46703 | 0.79731 | 0.60623 | 0.3083 | 0.19109 | 162.4438 | 374.2621 | 39.9607

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 11 |  |  | 2006-07-10 | 10:57
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-88.9167 | 237321.3333 |  | -77.25 | 238088 | -69.25 | 235171.3333 | -64.25 | 232738 | -60.9167 | 236121.3333 | -58.5 | 234238 | -56.25 | 237154.6667 | -88.9167 | 232738
-30.0833 | 237321.3333 |  | -18.4167 | 238088 | -10.5833 | 235171.3333 | -5.4167 | 232738 | -2 | 236121.3333 | 0.25 | 234238 | 2.5833 | 237154.6667 | -30.0833 | 232738
28.6667 | 237321.3333 |  | 40.3333 | 238088 | 48.3333 | 235171.3333 | 53.5 | 232738 | 56.6667 | 236121.3333 | 59 | 234238 | 61.3333 | 237154.6667 | 28.6667 | 232738
87.5 | 237321.3333 |  | 99.1667 | 238088 | 107.1667 | 235171.3333 | 112.25 | 232738 | 115.5 | 236121.3333 | 117.8333 | 234238 | 120.0833 | 217384.8333 | 87.5 | 217384.8333
146.3333 | 237321.3333 |  | 158 | 238088 | 165.9167 | 235171.3333 | 171.1667 | 232738 | 174.25 | 236121.3333 | 176.5833 | 234238 | 179.0833 | 237154.6667 | 146.3333 | 232738
205.0833 | 237321.3333 |  | 216.75 | 238088 | 224.75 | 235171.3333 | 229.75 | 232738 | 233.0833 | 236121.3333 | 235.5 | 234238 | 237.75 | 237154.6667 | 205.0833 | 232738
263.9167 | 237321.3333 |  | 275.5833 | 238088 | 283.4167 | 235171.3333 | 288.5833 | 213709.8333 | 292 | 236121.3333 | 294.25 | 234238 | 296.5833 | 237154.6667 | 263.9167 | 213709.8333
322.6667 | 237321.3333 |  | 334.1667 | 238088 | 342.3333 | 235171.3333 | 347.4167 | 232738 | 350.6667 | 236121.3333 | 352.9167 | 234238 | 355.3333 | 237154.6667 | 322.6667 | 232738
381.5 | 237321.3333 |  | 393.0833 | 238088 | 401.0833 | 235171.3333 | 406.1667 | 232738 | 409.4167 | 96466655.4067 | 411.8333 | 234238 | 414.0833 | 237154.6667 | 381.5 | 232738
440.1667 | 237321.3333 |  | 451.9167 | 238088 | 459.75 | 235171.3333 | 464.8333 | 232738 | 468.1667 | 236121.3333 | 470.5833 | 234238 | 472.9167 | 237154.6667 | 440.1667 | 232738
499 | 237321.3333 |  | 510.75 | 238088 | 518.6667 | 216743.1667 | 523.6667 | 232738 | 527 | 236121.3333 | 529.4167 | 234238 | 531.6667 | 237154.6667 | 499 | 216743.1667
557.9167 | 237321.3333 |  | 569.5 | 238088 | 577.4167 | 235171.3333 | 582.5833 | 232738 | 586 | 236121.3333 | 588.1667 | 234238 | 590.4167 | 237154.6667 | 557.9167 | 232738
616.6667 | 237321.3333 |  | 628.25 | 238088 | 636.25 | 235171.3333 | 641.3333 | 232738 | 644.5833 | 236121.3333 | 647 | 234238 | 649.25 | 237154.6667 | 616.6667 | 232738
675.4167 | 237321.3333 |  | 687.0833 | 238088 | 695.0833 | 235171.3333 | 700.0833 | 232738 | 703.3333 | 236121.3333 | 705.75 | 234238 | 708.0833 | 237154.6667 | 675.4167 | 232738
734.25 | 237321.3333 |  | 745.8333 | 238088 | 753.75 | 235171.3333 | 758.8333 | 232738 | 762.0833 | 236121.3333 | 764.5 | 234238 | 766.9167 | 237154.6667 | 734.25 | 232738
793 | 237321.3333 |  | 804.6667 | 238088 | 812.5 | 235171.3333 | 817.6667 | 232738 | 821.0833 | 236121.3333 | 823.4167 | 234238 | 825.6667 | 237154.6667 | 793 | 232738
851.75 | 237321.3333 |  | 863.4167 | 238088 | 871.3333 | 235171.3333 | 876.5833 | 232738 | 879.75 | 236121.3333 | 882.0833 | 234238 | 884.5833 | 237154.6667 | 851.75 | 232738
910.5833 | 237321.3333 |  | 922.25 | 238088 | 930.1667 | 235171.3333 | 935.4167 | 232738 | 938.5 | 236121.3333 | 940.8333 | 234238 | 943.0833 | 237154.6667 | 910.5833 | 232738
969.4167 | 237321.3333 |  | 981 | 238088 | 988.8333 | 235171.3333 | 994.0833 | 232738 | 997.3333 | 236121.3333 | 999.5833 | 234238 | 1002.0833 | 237154.6667 | 969.4167 | 232738
1028.1667 | 237321.3333 |  | 1039.8333 | 238088 | 1047.75 | 215234.8333 | 1052.75 | 232738 | 1056.0833 | 236121.3333 | 1058.5 | 234238 | 1060.75 | 237154.6667 | 1028.1667 | 215234.8333
1086.9167 | 237321.3333 |  | 1098.5833 | 238088 | 1106.4167 | 215284.8333 | 1111.5833 | 232738 | 1115.0833 | 236121.3333 | 1117.3333 | 234238 | 1119.5833 | 237154.6667 | 1086.9167 | 215284.8333
1145.6667 | 237321.3333 |  | 1157.3333 | 238088 | 1165.3333 | 235171.3333 | 1170.5 | 232738 | 1173.6667 | 96466655.4067 | 1176 | 234692.1612 | 1178.3333 | 213454.0047 | 1145.6667 | 213454.0047
1204.5 | 98288614.8873 |  | 1216.1667 | 198355.2233 | 1224.1667 | 95455812.807 | 1229.25 | 88057349.6151 | 1232.5 | 94398247.3227 | 1234.8333 | 127528.8923 | 1237.0833 | 120154.4479 | 1204.5 | 120154.4479
1263.3333 | 104609.5925 |  | 1275 | 65983.1147 | 1282.8333 | 40651.7216 | 1288.0833 | 70253.6516 | 1291.25 | 45121734.0334 | 1293.5833 | 24994.6666 | 1296.0833 | 12259.0817 | 1263.3333 | 12259.0817
1322.1667 | 9955.5581 |  | 1333.75 | 19276.7713 | 1341.75 | 9768.7076 | 1346.75 | 74704.7005 | 1350.1667 | 13769.538 | 1352.5 | 15675.9038 | 1354.75 | 5788.9918 | 1322.1667 | 5788.9918
1380.9167 | 5336.4751 |  | 1392.5833 | 5591.0198 | 1400.4167 | 3812.0877 | 1405.5833 | 3886.7402 | 1409 | 10227.2484 | 1411.25 | 18448.4973 | 1413.5833 | 4043.2128 | 1380.9167 | 3812.0877
1439.6667 | 2328.5546 |  | 1451.3333 | 3007.0451 | 1459.3333 | 995.019 | 1464.5 | 5591.8351 | 1467.6667 | 7186.796 | 1470 | 359.2117 | 1472.3333 | 1494.4975 | 1439.6667 | 359.2117
1498.5 | 24.1355 |  | 1510.1667 | 12.6256 | 1518.1667 | 57.3351 | 1523.25 | 120.7749 | 1526.5 | 234.1439 | 1528.8333 | 72.5997 | 1531.0833 | 173.5748 | 1498.5 | 12.6256
1557.3333 | 275.9294 |  | 1569 | 47287.2864 | 1576.8333 | 87.1946 | 1582.0833 | 35.3156 | 1585.25 | 40.755 | 1587.5833 | 55.6754 | 1590.0833 | 60.6071 | 1557.3333 | 35.3156
1616.0833 | 24.4987 |  | 1627.75 | 11.7366 | 1635.75 | 38.8615 | 1640.6667 | 15.8051 | 1644.0833 | 19.7554 | 1646.4167 | 26.1986 | 1648.75 | 16.7871 | 1616.0833 | 11.7366
1674.9167 | 12.0583 |  | 1686.5 | 6.5217 | 1694.4167 | 14.3384 | 1699.5833 | 13.9413 | 1702.9167 | 91.9865 | 1705.25 | 14.6312 | 1707.5833 | 12.4183 | 1674.9167 | 6.5217
1733.6667 | 22.5123 |  | 1745.25 | 10.7025 | 1753.3333 | 217.1204 | 1758.4167 | 19.4643 | 1761.5833 | 33.341 | 1764 | 9.2363 | 1766.25 | 4758.7699 | 1733.6667 | 9.2363
1792.5 | 20.1848 |  | 1804.0833 | 11.2292 | 1812.0833 | 12.5551 | 1817.25 | 5.4498 | 1820.4167 | 42.6392 | 1822.75 | 19.3782 | 1825.0833 | 43.6563 | 1792.5 | 5.4498
1851.1667 | 15.7396 |  | 1862.8333 | 174.1574 | 1870.8333 | 328.8144 | 1875.9167 | 75.3318 | 1879.1667 | 51.6339 | 1881.5833 | 117.534 | 1884 | 124.2525 | 1851.1667 | 15.7396
1910.0833 | 290.1587 |  | 1921.6667 | 1684.1291 | 1929.6667 | 1492.8472 | 1934.6667 | 2453.7199 | 1938.0833 | 794.5512 | 1940.3333 | 1580.4341 | 1942.6667 | 1415.3599 | 1910.0833 | 290.1587

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 11 |  |  | 2006-07-10 | 10:57
38908.455 | 1 | 0 | 1 | XLPE | 7-C | Tray
38908.4557 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38908.4564 | 1 | 0 | 1
38908.4571 | 1 | 0 | 1
38908.4577 | 1 | 0 | 1
38908.4584 | 1 | 0 | 1
38908.4591 | 1 | 0 | 1
38908.4598 | 1 | 0 | 1
38908.4605 | 1 | 0 | 1
38908.4611 | 1 | 0 | 1
38908.4618 | 1 | 0 | 1
38908.4625 | 1 | 0 | 1
38908.4632 | 1 | 0 | 1
38908.4639 | 1 | 0 | 1
38908.4645 | 1 | 0 | 1
38908.4652 | 1 | 0 | 1
38908.4659 | 1 | 0 | 1
38908.4666 | 1 | 0 | 1
38908.4673 | 1 | 0 | 1
38908.468 | 1 | 0 | 1
38908.4686 | 1 | 0 | 1
38908.4693 | 1 | 0 | 1
38908.47 | 2 | 6 | 1
38908.4707 | 5 | 14 | 1
38908.4713 | 1041 | 1014 | 1
38908.472 | 1115 | 1081 | 1
38908.4727 | 1167 | 1080 | 1
38908.4734 | 1940 | 76 | 1
38908.4741 | 1630 | 701 | 1
38908.4747 | 1805 | 52 | 1
38908.4754 | 1917 | 10 | 1
38908.4761 | 2146 | 12 | 1
38908.4768 | 1924 | 14 | 1
38908.4775 | 1983 | 37 | 1
38908.4781 | 1270 | 765 | 1
38908.455 | 1 | 0 | 2
38908.4557 | 1 | 0 | 2
38908.4564 | 1 | 0 | 2
38908.4571 | 1 | 0 | 2
38908.4578 | 1 | 0 | 2
38908.4584 | 1 | 0 | 2
38908.4591 | 1 | 0 | 2
38908.4598 | 1 | 0 | 2
38908.4605 | 1 | 0 | 2
38908.4612 | 1 | 0 | 2
38908.4618 | 1 | 0 | 2
38908.4625 | 1 | 0 | 2
38908.4632 | 1 | 0 | 2
38908.4639 | 1 | 0 | 2
38908.4646 | 1 | 0 | 2
38908.4652 | 1 | 0 | 2
38908.4659 | 1 | 0 | 2
38908.4666 | 1 | 0 | 2
38908.4673 | 1 | 0 | 2
38908.468 | 1 | 0 | 2
38908.4686 | 1 | 0 | 2
38908.4693 | 1 | 0 | 2
38908.47 | 1 | 2 | 2
38908.4707 | 4 | 10 | 2
38908.4714 | 1099 | 1073 | 2
38908.472 | 891 | 909 | 2
38908.4727 | 932 | 882 | 2
38908.4734 | 2165 | 93 | 2
38908.4741 | 1339 | 742 | 2
38908.4748 | 2091 | 44 | 2
38908.4755 | 2396 | 9 | 2
38908.4761 | 2406 | 11 | 2
38908.4768 | 2280 | 17 | 2
38908.4775 | 2326 | 42 | 2
38908.4782 | 1306 | 993 | 2
38908.455 | 1 | 0 | 3
38908.4557 | 1 | 0 | 3
38908.4564 | 1 | 0 | 3
38908.4571 | 1 | 0 | 3
38908.4578 | 1 | 0 | 3
38908.4584 | 1 | 0 | 3
38908.4591 | 1 | 0 | 3
38908.4598 | 1 | 0 | 3
38908.4605 | 1 | 0 | 3
38908.4612 | 1 | 0 | 3
38908.4619 | 1 | 0 | 3
38908.4625 | 1 | 0 | 3
38908.4632 | 1 | 0 | 3
38908.4639 | 1 | 0 | 3
38908.4646 | 1 | 0 | 3
38908.4653 | 1 | 0 | 3
38908.4659 | 1 | 0 | 3
38908.4666 | 1 | 0 | 3
38908.4673 | 1 | 0 | 3
38908.468 | 1 | 0 | 3
38908.4687 | 1 | 0 | 3
38908.4693 | 1 | 0 | 3
38908.47 | 1 | 1 | 3
38908.4707 | 3 | 8 | 3
38908.4714 | 810 | 845 | 3
38908.4721 | 916 | 923 | 3
38908.4727 | 919 | 839 | 3
38908.4734 | 2259 | 80 | 3
38908.4741 | 1505 | 688 | 3
38908.4748 | 2281 | 48 | 3
38908.4755 | 2356 | 11 | 3
38908.4761 | 2411 | 16 | 3
38908.4768 | 2327 | 23 | 3
38908.4775 | 2363 | 39 | 3
38908.4782 | 1314 | 1010 | 3
38908.4551 | 1 | 0 | 4
38908.4557 | 1 | 0 | 4
38908.4564 | 1 | 0 | 4
38908.4571 | 1 | 0 | 4
38908.4578 | 1 | 0 | 4
38908.4585 | 1 | 0 | 4
38908.4591 | 1 | 0 | 4
38908.4598 | 1 | 0 | 4
38908.4605 | 1 | 0 | 4
38908.4612 | 1 | 0 | 4
38908.4619 | 1 | 0 | 4
38908.4625 | 1 | 0 | 4
38908.4632 | 1 | 0 | 4
38908.4639 | 1 | 0 | 4
38908.4646 | 1 | 0 | 4
38908.4653 | 1 | 0 | 4
38908.4659 | 1 | 0 | 4
38908.4666 | 1 | 0 | 4
38908.4673 | 1 | 0 | 4
38908.468 | 1 | 0 | 4
38908.4687 | 1 | 0 | 4
38908.4694 | 1 | 0 | 4
38908.47 | 1 | 0 | 4
38908.4707 | 2 | 7 | 4
38908.4714 | 490 | 485 | 4
38908.4721 | 1108 | 1064 | 4
38908.4728 | 1104 | 1015 | 4
38908.4734 | 1682 | 69 | 4
38908.4741 | 1515 | 713 | 4
38908.4748 | 1833 | 43 | 4
38908.4755 | 1906 | 12 | 4
38908.4762 | 1951 | 13 | 4
38908.4768 | 1873 | 20 | 4
38908.4775 | 1899 | 44 | 4
38908.4782 | 1383 | 771 | 4
38908.4551 | 1 | 0 | 5
38908.4558 | 1 | 0 | 5
38908.4564 | 1 | 0 | 5
38908.4571 | 1 | 0 | 5
38908.4578 | 1 | 0 | 5
38908.4585 | 1 | 0 | 5
38908.4592 | 1 | 0 | 5
38908.4598 | 1 | 0 | 5
38908.4605 | 1 | 0 | 5
38908.4612 | 1 | 0 | 5
38908.4619 | 1 | 0 | 5
38908.4626 | 1 | 0 | 5
38908.4633 | 1 | 0 | 5
38908.4639 | 1 | 0 | 5
38908.4646 | 1 | 0 | 5
38908.4653 | 1 | 0 | 5
38908.466 | 1 | 0 | 5
38908.4667 | 1 | 0 | 5
38908.4673 | 1 | 0 | 5
38908.468 | 1 | 0 | 5
38908.4687 | 1 | 0 | 5
38908.4694 | 1 | 0 | 5
38908.47 | 1 | 0 | 5
38908.4707 | 2 | 5 | 5
38908.4714 | 625 | 658 | 5
38908.4721 | 1158 | 1113 | 5
38908.4728 | 1035 | 942 | 5
38908.4734 | 1856 | 74 | 5
38908.4741 | 1761 | 709 | 5
38908.4748 | 2187 | 49 | 5
38908.4755 | 2254 | 20 | 5
38908.4762 | 2239 | 18 | 5
38908.4769 | 1885 | 23 | 5
38908.4775 | 2016 | 45 | 5
38908.4782 | 1238 | 941 | 5
38908.4551 | 1 | 0 | 6
38908.4558 | 1 | 0 | 6
38908.4565 | 1 | 0 | 6
38908.4571 | 1 | 0 | 6
38908.4578 | 1 | 0 | 6
38908.4585 | 1 | 0 | 6
38908.4592 | 1 | 0 | 6
38908.4599 | 1 | 0 | 6
38908.4605 | 1 | 0 | 6
38908.4612 | 1 | 0 | 6
38908.4619 | 1 | 0 | 6
38908.4626 | 1 | 0 | 6
38908.4633 | 1 | 0 | 6
38908.4639 | 1 | 0 | 6
38908.4646 | 1 | 0 | 6
38908.4653 | 1 | 0 | 6
38908.466 | 1 | 0 | 6
38908.4667 | 1 | 0 | 6
38908.4673 | 1 | 0 | 6
38908.468 | 1 | 0 | 6
38908.4687 | 1 | 0 | 6
38908.4694 | 1 | 0 | 6
38908.4701 | 1 | 0 | 6
38908.4708 | 2 | 4 | 6
38908.4714 | 463 | 444 | 6
38908.4721 | 945 | 902 | 6
38908.4728 | 937 | 986 | 6
38908.4735 | 2153 | 85 | 6
38908.4742 | 1356 | 801 | 6
38908.4748 | 1932 | 36 | 6
38908.4755 | 2087 | 20 | 6
38908.4762 | 2330 | 20 | 6
38908.4769 | 1997 | 24 | 6
38908.4775 | 1817 | 45 | 6
38908.4782 | 1138 | 911 | 6
38908.4551 | 1 | 0 | 7
38908.4558 | 1 | 0 | 7
38908.4565 | 1 | 0 | 7
38908.4572 | 1 | 0 | 7
38908.4578 | 1 | 0 | 7
38908.4585 | 1 | 0 | 7
38908.4592 | 1 | 0 | 7
38908.4599 | 1 | 0 | 7
38908.4606 | 1 | 0 | 7
38908.4612 | 1 | 0 | 7
38908.4619 | 1 | 0 | 7
38908.4626 | 1 | 0 | 7
38908.4633 | 1 | 0 | 7
38908.464 | 1 | 0 | 7
38908.4646 | 1 | 0 | 7
38908.4653 | 1 | 0 | 7
38908.466 | 1 | 0 | 7
38908.4667 | 1 | 0 | 7
38908.4674 | 1 | 0 | 7
38908.468 | 1 | 0 | 7
38908.4687 | 1 | 0 | 7
38908.4694 | 1 | 0 | 7
38908.4701 | 1 | 0 | 7
38908.4708 | 2 | 3 | 7
38908.4721 | 78 | 58 | 7
38908.4728 | 993 | 897 | 7
38908.4735 | 2106 | 85 | 7
38908.4742 | 1589 | 715 | 7
38908.4748 | 1826 | 35 | 7
38908.4755 | 2198 | 17 | 7
38908.4762 | 1996 | 15 | 7
38908.4769 | 1857 | 21 | 7
38908.4776 | 2022 | 49 | 7
38908.4783 | 1181 | 844 | 7
38908.4551 | 1 | 0 | 8
38908.4558 | 1 | 0 | 8
38908.4565 | 1 | 0 | 8
38908.4572 | 1 | 0 | 8
38908.4578 | 1 | 0 | 8
38908.4585 | 1 | 0 | 8
38908.4592 | 1 | 0 | 8
38908.4599 | 1 | 0 | 8
38908.4606 | 1 | 0 | 8
38908.4613 | 1 | 0 | 8
38908.4619 | 1 | 0 | 8
38908.4626 | 1 | 0 | 8
38908.4633 | 1 | 0 | 8
38908.464 | 1 | 0 | 8
38908.4647 | 1 | 0 | 8
38908.4653 | 1 | 0 | 8
38908.466 | 1 | 0 | 8
38908.4667 | 1 | 0 | 8
38908.4674 | 1 | 0 | 8
38908.4681 | 1 | 0 | 8
38908.4687 | 1 | 0 | 8
38908.4694 | 1 | 0 | 8
38908.4701 | 1 | 0 | 8
38908.4708 | 2 | 2 | 8
38908.4715 | 946 | 977 | 8
38908.4721 | 164 | 156 | 8
38908.4728 | 1115 | 1017 | 8
38908.4735 | 1770 | 70 | 8
38908.4742 | 1330 | 755 | 8
38908.4749 | 2261 | 38 | 8
38908.4755 | 2185 | 21 | 8
38908.4762 | 1880 | 15 | 8
38908.4769 | 2107 | 25 | 8
38908.4776 | 2312 | 58 | 8
38908.4783 | 1072 | 790 | 8
38908.4552 | 1 | 0 | 9
38908.4558 | 1 | 0 | 9
38908.4565 | 1 | 0 | 9
38908.4572 | 1 | 0 | 9
38908.4579 | 1 | 0 | 9
38908.4586 | 1 | 0 | 9
38908.4592 | 1 | 0 | 9
38908.4599 | 1 | 0 | 9
38908.4606 | 1 | 0 | 9
38908.4613 | 1 | 0 | 9
38908.4619 | 1 | 0 | 9
38908.4626 | 1 | 0 | 9
38908.4633 | 1 | 0 | 9
38908.464 | 1 | 0 | 9
38908.4647 | 1 | 0 | 9
38908.4654 | 1 | 0 | 9
38908.466 | 1 | 0 | 9
38908.4667 | 1 | 0 | 9
38908.4674 | 1 | 0 | 9
38908.4681 | 1 | 0 | 9
38908.4688 | 1 | 0 | 9
38908.4694 | 1 | 0 | 9
38908.4701 | 1 | 0 | 9
38908.4708 | 4 | 2 | 9
38908.4715 | 1013 | 978 | 9
38908.4722 | 244 | 213 | 9
38908.4728 | 1059 | 1029 | 9
38908.4735 | 1881 | 55 | 9
38908.4742 | 1520 | 611 | 9
38908.4749 | 2126 | 37 | 9
38908.4756 | 2230 | 14 | 9
38908.4762 | 1999 | 13 | 9
38908.4769 | 2332 | 26 | 9
38908.4776 | 2259 | 61 | 9
38908.4783 | 1201 | 912 | 9
38908.4552 | 1 | 0 | 10
38908.4558 | 1 | 0 | 10
38908.4565 | 1 | 0 | 10
38908.4572 | 1 | 0 | 10
38908.4579 | 1 | 0 | 10
38908.4586 | 1 | 0 | 10
38908.4592 | 1 | 0 | 10
38908.4599 | 1 | 0 | 10
38908.4606 | 1 | 0 | 10
38908.4613 | 1 | 0 | 10
38908.462 | 1 | 0 | 10
38908.4627 | 1 | 0 | 10
38908.4633 | 1 | 0 | 10
38908.464 | 1 | 0 | 10
38908.4647 | 1 | 0 | 10
38908.4654 | 1 | 0 | 10
38908.4661 | 1 | 0 | 10
38908.4667 | 1 | 0 | 10
38908.4674 | 1 | 0 | 10
38908.4681 | 1 | 0 | 10
38908.4688 | 1 | 0 | 10
38908.4695 | 1 | 0 | 10
38908.4701 | 1 | 0 | 10
38908.4708 | 11 | 9 | 10
38908.4715 | 1099 | 1069 | 10
38908.4722 | 187 | 166 | 10
38908.4729 | 1208 | 1102 | 10
38908.4735 | 1999 | 57 | 10
38908.4742 | 1613 | 643 | 10
38908.4749 | 1884 | 37 | 10
38908.4756 | 2196 | 19 | 10
38908.4763 | 2137 | 17 | 10
38908.4769 | 1908 | 22 | 10
38908.4776 | 2311 | 65 | 10
38908.4783 | 1167 | 1052 | 10
38908.4552 | 1 | 0 | 11
38908.4559 | 1 | 0 | 11
38908.4565 | 1 | 0 | 11
38908.4572 | 1 | 0 | 11
38908.4579 | 1 | 0 | 11
38908.4586 | 1 | 0 | 11
38908.4593 | 1 | 0 | 11
38908.4599 | 1 | 0 | 11
38908.4606 | 1 | 0 | 11
38908.4613 | 1 | 0 | 11
38908.462 | 1 | 0 | 11
38908.4627 | 1 | 0 | 11
38908.4633 | 1 | 0 | 11
38908.464 | 1 | 0 | 11
38908.4647 | 1 | 0 | 11
38908.4654 | 1 | 0 | 11
38908.4661 | 1 | 0 | 11
38908.4667 | 1 | 0 | 11
38908.4674 | 1 | 0 | 11
38908.4681 | 1 | 0 | 11
38908.4688 | 1 | 0 | 11
38908.4695 | 1 | 0 | 11
38908.4702 | 1 | 0 | 11
38908.4708 | 26 | 24 | 11
38908.4715 | 1053 | 1020 | 11
38908.4722 | 822 | 777 | 11
38908.4729 | 935 | 925 | 11
38908.4736 | 2142 | 78 | 11
38908.4742 | 1196 | 651 | 11
38908.4749 | 2339 | 42 | 11
38908.4756 | 2319 | 18 | 11
38908.4763 | 2356 | 14 | 11
38908.477 | 1843 | 19 | 11
38908.4776 | 1865 | 47 | 11
38908.4783 | 1186 | 998 | 11
38908.4552 | 1 | 0 | 12
38908.4559 | 1 | 0 | 12
38908.4566 | 1 | 0 | 12
38908.4572 | 2 | 0 | 12
38908.4579 | 1 | 0 | 12
38908.4586 | 1 | 0 | 12
38908.4593 | 1 | 0 | 12
38908.46 | 1 | 0 | 12
38908.4606 | 1 | 0 | 12
38908.4613 | 1 | 0 | 12
38908.462 | 1 | 0 | 12
38908.4627 | 1 | 0 | 12
38908.4634 | 1 | 0 | 12
38908.464 | 1 | 0 | 12
38908.4647 | 1 | 0 | 12
38908.4654 | 1 | 0 | 12
38908.4661 | 1 | 0 | 12
38908.4668 | 1 | 0 | 12
38908.4674 | 1 | 0 | 12
38908.4681 | 1 | 0 | 12
38908.4688 | 1 | 0 | 12
38908.4695 | 1 | 0 | 12
38908.4702 | 1 | 0 | 12
38908.4708 | 114 | 124 | 12
38908.4715 | 1001 | 1038 | 12
38908.4722 | 872 | 882 | 12
38908.4729 | 966 | 926 | 12
38908.4736 | 1785 | 66 | 12
38908.4742 | 1486 | 657 | 12
38908.4749 | 2354 | 44 | 12
38908.4756 | 1887 | 16 | 12
38908.4763 | 1870 | 13 | 12
38908.477 | 2092 | 23 | 12
38908.4777 | 1822 | 49 | 12
38908.4783 | 989 | 873 | 12
38908.4552 | 1 | 0 | 13
38908.4559 | 1 | 0 | 13
38908.4566 | 1 | 0 | 13
38908.4573 | 1 | 0 | 13
38908.4579 | 1 | 0 | 13
38908.4586 | 1 | 0 | 13
38908.4593 | 1 | 0 | 13
38908.46 | 1 | 0 | 13
38908.4607 | 1 | 0 | 13
38908.4613 | 1 | 0 | 13
38908.462 | 1 | 0 | 13
38908.4627 | 1 | 0 | 13
38908.4634 | 1 | 0 | 13
38908.4641 | 1 | 0 | 13
38908.4647 | 1 | 0 | 13
38908.4654 | 1 | 0 | 13
38908.4661 | 1 | 0 | 13
38908.4668 | 1 | 0 | 13
38908.4675 | 1 | 0 | 13
38908.4681 | 1 | 0 | 13
38908.4688 | 1 | 0 | 13
38908.4695 | 1 | 0 | 13
38908.4702 | 1 | 0 | 13
38908.4709 | 2 | 1 | 13
38908.4715 | 1032 | 1002 | 13
38908.4722 | 988 | 1008 | 13
38908.4729 | 1064 | 951 | 13
38908.4736 | 2175 | 62 | 13
38908.4743 | 1519 | 676 | 13
38908.4749 | 2041 | 26 | 13
38908.4756 | 2029 | 10 | 13
38908.4763 | 1868 | 9 | 13
38908.477 | 2199 | 20 | 13
38908.4777 | 2024 | 58 | 13
38908.4783 | 1040 | 866 | 13
38908.4552 | 1 | 0 | 14
38908.4559 | 1 | 0 | 14
38908.4566 | 1 | 0 | 14
38908.4573 | 1 | 0 | 14
38908.458 | 1 | 0 | 14
38908.4586 | 1 | 0 | 14
38908.4593 | 1 | 0 | 14
38908.46 | 1 | 0 | 14
38908.4607 | 1 | 0 | 14
38908.4614 | 1 | 0 | 14
38908.462 | 1 | 0 | 14
38908.4627 | 1 | 0 | 14
38908.4634 | 1 | 0 | 14
38908.4641 | 1 | 0 | 14
38908.4648 | 1 | 0 | 14
38908.4654 | 1 | 0 | 14
38908.4661 | 1 | 0 | 14
38908.4668 | 1 | 0 | 14
38908.4675 | 1 | 0 | 14
38908.4682 | 1 | 0 | 14
38908.4688 | 1 | 0 | 14
38908.4695 | 1 | 0 | 14
38908.4702 | 2 | 0 | 14
38908.4709 | 2 | 0 | 14
38908.4716 | 1027 | 1075 | 14
38908.4722 | 1042 | 991 | 14
38908.4729 | 1109 | 992 | 14
38908.4736 | 1820 | 74 | 14
38908.4743 | 1434 | 814 | 14
38908.475 | 1959 | 25 | 14
38908.4756 | 2288 | 12 | 14
38908.4763 | 2197 | 12 | 14
38908.477 | 2247 | 21 | 14
38908.4777 | 2303 | 75 | 14
38908.4784 | 1167 | 1009 | 14
38908.4552 | 1 | 0 | 15
38908.4559 | 1 | 0 | 15
38908.4566 | 1 | 0 | 15
38908.4573 | 1 | 0 | 15
38908.458 | 1 | 0 | 15
38908.4586 | 1 | 0 | 15
38908.4593 | 1 | 0 | 15
38908.46 | 1 | 0 | 15
38908.4607 | 1 | 0 | 15
38908.4614 | 1 | 0 | 15
38908.462 | 1 | 0 | 15
38908.4627 | 1 | 0 | 15
38908.4634 | 1 | 0 | 15
38908.4641 | 1 | 0 | 15
38908.4648 | 1 | 0 | 15
38908.4655 | 1 | 0 | 15
38908.4661 | 1 | 0 | 15
38908.4668 | 1 | 0 | 15
38908.4675 | 1 | 0 | 15
38908.4682 | 1 | 0 | 15
38908.4689 | 1 | 0 | 15
38908.4695 | 1 | 0 | 15
38908.4702 | 1 | 0 | 15
38908.4709 | 2 | 0 | 15
38908.4716 | 79 | 76 | 15
38908.4723 | 886 | 838 | 15
38908.4729 | 892 | 832 | 15
38908.4736 | 2051 | 73 | 15
38908.4743 | 1490 | 807 | 15
38908.475 | 2026 | 24 | 15
38908.4757 | 2255 | 11 | 15
38908.4763 | 2055 | 11 | 15
38908.477 | 1984 | 17 | 15
38908.4777 | 1885 | 65 | 15
38908.4784 | 1060 | 978 | 15
38908.4553 | 1 | 0 | 16
38908.4559 | 1 | 0 | 16
38908.4566 | 1 | 0 | 16
38908.4573 | 1 | 0 | 16
38908.458 | 1 | 0 | 16
38908.4587 | 1 | 0 | 16
38908.4593 | 2 | 0 | 16
38908.46 | 1 | 0 | 16
38908.4607 | 1 | 0 | 16
38908.4614 | 1 | 0 | 16
38908.4621 | 1 | 0 | 16
38908.4627 | 1 | 0 | 16
38908.4634 | 1 | 0 | 16
38908.4641 | 1 | 0 | 16
38908.4648 | 1 | 0 | 16
38908.4655 | 1 | 0 | 16
38908.4661 | 1 | 0 | 16
38908.4668 | 1 | 0 | 16
38908.4675 | 1 | 0 | 16
38908.4682 | 1 | 0 | 16
38908.4689 | 1 | 0 | 16
38908.4695 | 1 | 0 | 16
38908.4702 | 1 | 0 | 16
38908.4709 | 1 | 1 | 16
38908.4716 | 298 | 293 | 16
38908.4723 | 893 | 842 | 16
38908.473 | 1161 | 1046 | 16
38908.4736 | 2047 | 75 | 16
38908.4743 | 1364 | 586 | 16
38908.475 | 2267 | 27 | 16
38908.4757 | 2245 | 9 | 16
38908.4764 | 1845 | 10 | 16
38908.477 | 2199 | 22 | 16
38908.4777 | 2056 | 95 | 16
38908.4784 | 1252 | 1119 | 16
38908.4553 | 1 | 0 | 17
38908.456 | 1 | 0 | 17
38908.4566 | 1 | 0 | 17
38908.4573 | 1 | 0 | 17
38908.458 | 1 | 0 | 17
38908.4587 | 1 | 0 | 17
38908.4594 | 1 | 0 | 17
38908.46 | 1 | 0 | 17
38908.4607 | 1 | 0 | 17
38908.4614 | 1 | 0 | 17
38908.4621 | 1 | 0 | 17
38908.4628 | 1 | 0 | 17
38908.4634 | 1 | 0 | 17
38908.4641 | 1 | 0 | 17
38908.4648 | 1 | 0 | 17
38908.4655 | 1 | 0 | 17
38908.4662 | 1 | 0 | 17
38908.4668 | 1 | 0 | 17
38908.4675 | 1 | 0 | 17
38908.4682 | 1 | 0 | 17
38908.4689 | 1 | 0 | 17
38908.4696 | 1 | 0 | 17
38908.4702 | 1 | 0 | 17
38908.4709 | 733 | 818 | 17
38908.4716 | 516 | 498 | 17
38908.4723 | 347 | 303 | 17
38908.473 | 962 | 894 | 17
38908.4736 | 2285 | 84 | 17
38908.4743 | 1798 | 225 | 17
38908.475 | 2326 | 23 | 17
38908.4757 | 2419 | 9 | 17
38908.4764 | 2424 | 9 | 17
38908.477 | 2206 | 20 | 17
38908.4777 | 1912 | 116 | 17
38908.4784 | 1219 | 1105 | 17
38908.4553 | 1 | 0 | 18
38908.456 | 1 | 0 | 18
38908.4567 | 1 | 0 | 18
38908.4573 | 1 | 0 | 18
38908.458 | 1 | 0 | 18
38908.4587 | 1 | 0 | 18
38908.4594 | 1 | 0 | 18
38908.4601 | 1 | 0 | 18
38908.4607 | 1 | 0 | 18
38908.4614 | 1 | 0 | 18
38908.4621 | 1 | 0 | 18
38908.4628 | 1 | 0 | 18
38908.4635 | 1 | 0 | 18
38908.4641 | 1 | 0 | 18
38908.4648 | 1 | 0 | 18
38908.4655 | 1 | 0 | 18
38908.4662 | 1 | 0 | 18
38908.4669 | 1 | 0 | 18
38908.4675 | 1 | 0 | 18
38908.4682 | 1 | 0 | 18
38908.4689 | 1 | 0 | 18
38908.4696 | 1 | 0 | 18
38908.4703 | 1 | 0 | 18
38908.4709 | 792 | 761 | 18
38908.4716 | 394 | 385 | 18
38908.4723 | 339 | 291 | 18
38908.473 | 1069 | 929 | 18
38908.4737 | 2166 | 80 | 18
38908.4743 | 2036 | 205 | 18
38908.475 | 1971 | 21 | 18
38908.4757 | 1926 | 10 | 18
38908.4764 | 1934 | 10 | 18
38908.4771 | 2355 | 23 | 18
38908.4777 | 1910 | 265 | 18
38908.4784 | 1063 | 913 | 18
38908.4553 | 1 | 0 | 19
38908.456 | 1 | 0 | 19
38908.4567 | 1 | 0 | 19
38908.4573 | 1 | 0 | 19
38908.458 | 1 | 0 | 19
38908.4587 | 1 | 0 | 19
38908.4594 | 1 | 0 | 19
38908.4601 | 1 | 0 | 19
38908.4608 | 1 | 0 | 19
38908.4614 | 1 | 0 | 19
38908.4621 | 1 | 0 | 19
38908.4628 | 1 | 0 | 19
38908.4635 | 1 | 0 | 19
38908.4642 | 1 | 0 | 19
38908.4648 | 1 | 0 | 19
38908.4655 | 1 | 0 | 19
38908.4662 | 1 | 0 | 19
38908.4669 | 1 | 0 | 19
38908.4676 | 1 | 0 | 19
38908.4682 | 1 | 0 | 19
38908.4689 | 1 | 0 | 19
38908.4696 | 1 | 0 | 19
38908.4703 | 1 | 0 | 19
38908.471 | 908 | 876 | 19
38908.4716 | 1074 | 1042 | 19
38908.4723 | 740 | 740 | 19
38908.473 | 1159 | 1069 | 19
38908.4737 | 2024 | 61 | 19
38908.4744 | 2130 | 186 | 19
38908.475 | 2131 | 16 | 19
38908.4757 | 2188 | 9 | 19
38908.4764 | 2016 | 9 | 19
38908.4771 | 2406 | 22 | 19
38908.4778 | 1579 | 583 | 19
38908.4784 | 1126 | 882 | 19
38908.4553 | 1 | 0 | 20
38908.456 | 1 | 0 | 20
38908.4567 | 1 | 0 | 20
38908.4574 | 1 | 0 | 20
38908.458 | 1 | 0 | 20
38908.4587 | 1 | 0 | 20
38908.4594 | 1 | 0 | 20
38908.4601 | 1 | 0 | 20
38908.4608 | 1 | 0 | 20
38908.4614 | 1 | 0 | 20
38908.4621 | 1 | 0 | 20
38908.4628 | 1 | 0 | 20
38908.4635 | 1 | 0 | 20
38908.4642 | 1 | 0 | 20
38908.4648 | 1 | 0 | 20
38908.4655 | 1 | 0 | 20
38908.4662 | 1 | 0 | 20
38908.4669 | 1 | 0 | 20
38908.4676 | 1 | 0 | 20
38908.4683 | 1 | 0 | 20
38908.4689 | 1 | 0 | 20
38908.4696 | 1 | 0 | 20
38908.4703 | 38 | 32 | 20
38908.471 | 935 | 906 | 20
38908.4717 | 948 | 1052 | 20
38908.4723 | 1032 | 882 | 20
38908.473 | 1036 | 1003 | 20
38908.4737 | 2074 | 64 | 20
38908.4744 | 1749 | 169 | 20
38908.4751 | 2038 | 21 | 20
38908.4757 | 2293 | 11 | 20
38908.4764 | 2359 | 9 | 20
38908.4771 | 2093 | 22 | 20
38908.4778 | 1758 | 577 | 20
38908.4785 | 1249 | 1085 | 20
38908.4553 | 1 | 0 | 21
38908.456 | 1 | 0 | 21
38908.4567 | 1 | 0 | 21
38908.4574 | 1 | 0 | 21
38908.4581 | 1 | 0 | 21
38908.4587 | 1 | 0 | 21
38908.4594 | 1 | 0 | 21
38908.4601 | 1 | 0 | 21
38908.4608 | 1 | 0 | 21
38908.4615 | 1 | 0 | 21
38908.4621 | 1 | 0 | 21
38908.4628 | 1 | 0 | 21
38908.4635 | 1 | 0 | 21
38908.4642 | 1 | 0 | 21
38908.4649 | 1 | 0 | 21
38908.4655 | 1 | 0 | 21
38908.4662 | 1 | 0 | 21
38908.4669 | 1 | 0 | 21
38908.4676 | 1 | 0 | 21
38908.4683 | 1 | 0 | 21
38908.4689 | 1 | 0 | 21
38908.4696 | 1 | 0 | 21
38908.4703 | 352 | 536 | 21
38908.471 | 867 | 948 | 21
38908.4717 | 899 | 866 | 21
38908.4723 | 969 | 916 | 21
38908.473 | 1028 | 942 | 21
38908.4737 | 2282 | 72 | 21
38908.4744 | 1972 | 173 | 21
38908.4751 | 2354 | 23 | 21
38908.4758 | 2370 | 12 | 21
38908.4764 | 2387 | 9 | 21
38908.4771 | 2022 | 17 | 21
38908.4778 | 1485 | 518 | 21
38908.4785 | 1256 | 1031 | 21
38908.4554 | 1 | 0 | 22
38908.456 | 1 | 0 | 22
38908.4567 | 1 | 0 | 22
38908.4574 | 1 | 0 | 22
38908.4581 | 1 | 0 | 22
38908.4588 | 1 | 0 | 22
38908.4594 | 1 | 0 | 22
38908.4601 | 1 | 0 | 22
38908.4608 | 1 | 0 | 22
38908.4615 | 1 | 0 | 22
38908.4622 | 1 | 0 | 22
38908.4628 | 1 | 0 | 22
38908.4635 | 1 | 0 | 22
38908.4642 | 1 | 0 | 22
38908.4649 | 1 | 0 | 22
38908.4656 | 1 | 0 | 22
38908.4662 | 1 | 0 | 22
38908.4669 | 1 | 0 | 22
38908.4676 | 1 | 0 | 22
38908.4683 | 1 | 0 | 22
38908.469 | 1 | 0 | 22
38908.4696 | 1 | 0 | 22
38908.4703 | 660 | 642 | 22
38908.471 | 1109 | 852 | 22
38908.4717 | 1040 | 1006 | 22
38908.4724 | 1022 | 967 | 22
38908.473 | 1094 | 931 | 22
38908.4737 | 2272 | 96 | 22
38908.4744 | 2233 | 107 | 22
38908.4751 | 1959 | 19 | 22
38908.4758 | 2362 | 11 | 22
38908.4764 | 1882 | 9 | 22
38908.4771 | 1934 | 20 | 22
38908.4778 | 1577 | 625 | 22
38908.4785 | 976 | 892 | 22
38908.4554 | 1 | 0 | 23
38908.4561 | 1 | 0 | 23
38908.4567 | 1 | 0 | 23
38908.4574 | 1 | 0 | 23
38908.4581 | 1 | 0 | 23
38908.4588 | 1 | 0 | 23
38908.4595 | 1 | 0 | 23
38908.4601 | 1 | 0 | 23
38908.4608 | 1 | 0 | 23
38908.4615 | 1 | 0 | 23
38908.4622 | 1 | 0 | 23
38908.4629 | 1 | 0 | 23
38908.4635 | 1 | 0 | 23
38908.4642 | 1 | 0 | 23
38908.4649 | 1 | 0 | 23
38908.4656 | 1 | 0 | 23
38908.4663 | 1 | 0 | 23
38908.4669 | 1 | 0 | 23
38908.4676 | 1 | 0 | 23
38908.4683 | 1 | 0 | 23
38908.469 | 2 | 0 | 23
38908.4697 | 1 | 0 | 23
38908.4703 | 3 | 8 | 23
38908.471 | 7 | 15 | 23
38908.4717 | 453 | 437 | 23
38908.4724 | 843 | 868 | 23
38908.4731 | 1023 | 859 | 23
38908.4737 | 1819 | 86 | 23
38908.4744 | 1869 | 256 | 23
38908.4751 | 2010 | 27 | 23
38908.4758 | 2055 | 19 | 23
38908.4765 | 1948 | 16 | 23
38908.4772 | 2220 | 30 | 23
38908.4778 | 1427 | 415 | 23
38908.4785 | 1025 | 874 | 23
38908.4554 | 1 | 0 | 24
38908.4561 | 1 | 0 | 24
38908.4567 | 1 | 0 | 24
38908.4574 | 1 | 0 | 24
38908.4581 | 1 | 0 | 24
38908.4588 | 1 | 0 | 24
38908.4595 | 1 | 0 | 24
38908.4602 | 1 | 0 | 24
38908.4608 | 1 | 0 | 24
38908.4615 | 1 | 0 | 24
38908.4622 | 1 | 0 | 24
38908.4629 | 1 | 0 | 24
38908.4636 | 1 | 0 | 24
38908.4642 | 1 | 0 | 24
38908.4649 | 1 | 0 | 24
38908.4656 | 1 | 0 | 24
38908.4663 | 1 | 0 | 24
38908.467 | 1 | 0 | 24
38908.4676 | 1 | 0 | 24
38908.4683 | 1 | 0 | 24
38908.469 | 1 | 0 | 24
38908.4697 | 1 | 0 | 24
38908.4704 | 1 | 4 | 24
38908.471 | 7 | 12 | 24
38908.4717 | 80 | 80 | 24
38908.4724 | 1122 | 1044 | 24
38908.4731 | 1105 | 1014 | 24
38908.4738 | 1723 | 323 | 24
38908.4744 | 2047 | 264 | 24
38908.4751 | 2093 | 26 | 24
38908.4758 | 1932 | 16 | 24
38908.4765 | 2087 | 17 | 24
38908.4772 | 2370 | 33 | 24
38908.4778 | 1787 | 591 | 24
38908.4785 | 1237 | 994 | 24
38908.4554 | 1 | 0 | 25
38908.4561 | 1 | 0 | 25
38908.4568 | 1 | 0 | 25
38908.4574 | 1 | 0 | 25
38908.4581 | 1 | 0 | 25
38908.4588 | 1 | 0 | 25
38908.4595 | 1 | 0 | 25
38908.4602 | 1 | 0 | 25
38908.4608 | 1 | 0 | 25
38908.4615 | 1 | 0 | 25
38908.4622 | 1 | 0 | 25
38908.4629 | 1 | 0 | 25
38908.4636 | 1 | 0 | 25
38908.4642 | 1 | 0 | 25
38908.4649 | 1 | 0 | 25
38908.4656 | 1 | 0 | 25
38908.4663 | 1 | 0 | 25
38908.467 | 1 | 0 | 25
38908.4677 | 1 | 0 | 25
38908.4683 | 1 | 0 | 25
38908.469 | 1 | 0 | 25
38908.4697 | 1 | 0 | 25
38908.4704 | 2 | 1 | 25
38908.4711 | 6 | 12 | 25
38908.4717 | 926 | 760 | 25
38908.4724 | 1001 | 942 | 25
38908.4731 | 1184 | 1014 | 25
38908.4738 | 1828 | 382 | 25
38908.4745 | 1860 | 228 | 25
38908.4751 | 2271 | 27 | 25
38908.4758 | 2298 | 18 | 25
38908.4765 | 2363 | 19 | 25
38908.4772 | 1973 | 26 | 25
38908.4779 | 1527 | 442 | 25
38908.4785 | 1179 | 1016 | 25
38908.4554 | 1 | 0 | 26
38908.4561 | 1 | 0 | 26
38908.4568 | 1 | 0 | 26
38908.4575 | 1 | 0 | 26
38908.4581 | 1 | 0 | 26
38908.4588 | 1 | 0 | 26
38908.4595 | 1 | 0 | 26
38908.4602 | 1 | 0 | 26
38908.4609 | 1 | 0 | 26
38908.4615 | 1 | 0 | 26
38908.4622 | 1 | 0 | 26
38908.4629 | 1 | 0 | 26
38908.4636 | 1 | 0 | 26
38908.4643 | 1 | 0 | 26
38908.4649 | 1 | 0 | 26
38908.4656 | 1 | 0 | 26
38908.4663 | 1 | 0 | 26
38908.467 | 1 | 0 | 26
38908.4677 | 1 | 0 | 26
38908.4683 | 1 | 0 | 26
38908.469 | 1 | 0 | 26
38908.4697 | 1 | 0 | 26
38908.4704 | 1 | 1 | 26
38908.4711 | 102 | 127 | 26
38908.4717 | 817 | 875 | 26
38908.4724 | 979 | 922 | 26
38908.4731 | 992 | 870 | 26
38908.4738 | 1454 | 424 | 26
38908.4745 | 1714 | 209 | 26
38908.4752 | 1910 | 21 | 26
38908.4758 | 2319 | 15 | 26
38908.4765 | 2337 | 20 | 26
38908.4772 | 1901 | 26 | 26
38908.4779 | 1691 | 397 | 26
38908.4786 | 1171 | 1095 | 26
38908.4554 | 1 | 0 | 27
38908.4561 | 1 | 0 | 27
38908.4568 | 1 | 0 | 27
38908.4575 | 1 | 0 | 27
38908.4582 | 1 | 0 | 27
38908.4588 | 1 | 0 | 27
38908.4595 | 1 | 0 | 27
38908.4602 | 1 | 0 | 27
38908.4609 | 1 | 0 | 27
38908.4616 | 1 | 0 | 27
38908.4622 | 2 | 0 | 27
38908.4629 | 1 | 0 | 27
38908.4636 | 1 | 0 | 27
38908.4643 | 1 | 0 | 27
38908.465 | 1 | 0 | 27
38908.4656 | 1 | 0 | 27
38908.4663 | 1 | 0 | 27
38908.467 | 1 | 0 | 27
38908.4677 | 1 | 0 | 27
38908.4684 | 1 | 0 | 27
38908.4691 | 1 | 0 | 27
38908.4697 | 1 | 0 | 27
38908.4704 | 1 | 1 | 27
38908.4711 | 356 | 394 | 27
38908.4718 | 1026 | 993 | 27
38908.4725 | 328 | 285 | 27
38908.4731 | 1072 | 876 | 27
38908.4738 | 1641 | 398 | 27
38908.4745 | 1980 | 297 | 27
38908.4752 | 1908 | 16 | 27
38908.4759 | 1934 | 13 | 27
38908.4765 | 1905 | 14 | 27
38908.4772 | 2133 | 31 | 27
38908.4779 | 1840 | 581 | 27
38908.4786 | 958 | 879 | 27
38908.4555 | 1 | 0 | 28
38908.4561 | 1 | 0 | 28
38908.4568 | 1 | 0 | 28
38908.4575 | 1 | 0 | 28
38908.4582 | 1 | 0 | 28
38908.4589 | 1 | 0 | 28
38908.4595 | 1 | 0 | 28
38908.4602 | 1 | 0 | 28
38908.4609 | 1 | 0 | 28
38908.4616 | 1 | 0 | 28
38908.4623 | 1 | 0 | 28
38908.4629 | 1 | 0 | 28
38908.4636 | 1 | 0 | 28
38908.4643 | 1 | 0 | 28
38908.465 | 1 | 0 | 28
38908.4657 | 1 | 0 | 28
38908.4663 | 1 | 0 | 28
38908.467 | 1 | 0 | 28
38908.4677 | 1 | 0 | 28
38908.4684 | 1 | 0 | 28
38908.4691 | 1 | 0 | 28
38908.4697 | 1 | 0 | 28
38908.4704 | 1 | 1 | 28
38908.4711 | 806 | 777 | 28
38908.4718 | 1115 | 1087 | 28
38908.4725 | 311 | 433 | 28
38908.4731 | 1265 | 917 | 28
38908.4738 | 1564 | 389 | 28
38908.4745 | 1985 | 198 | 28
38908.4752 | 2195 | 17 | 28
38908.4759 | 1926 | 13 | 28
38908.4766 | 1875 | 14 | 28
38908.4772 | 1957 | 27 | 28
38908.4779 | 1822 | 554 | 28
38908.4786 | 961 | 884 | 28
38908.4555 | 1 | 0 | 29
38908.4561 | 1 | 0 | 29
38908.4568 | 1 | 0 | 29
38908.4575 | 1 | 0 | 29
38908.4582 | 1 | 0 | 29
38908.4589 | 1 | 0 | 29
38908.4595 | 1 | 0 | 29
38908.4602 | 1 | 0 | 29
38908.4609 | 1 | 0 | 29
38908.4616 | 1 | 0 | 29
38908.4623 | 1 | 0 | 29
38908.463 | 1 | 0 | 29
38908.4636 | 1 | 0 | 29
38908.4643 | 1 | 0 | 29
38908.465 | 1 | 0 | 29
38908.4657 | 1 | 0 | 29
38908.4664 | 1 | 0 | 29
38908.467 | 1 | 0 | 29
38908.4677 | 1 | 0 | 29
38908.4684 | 2 | 0 | 29
38908.4691 | 1 | 0 | 29
38908.4698 | 1 | 0 | 29
38908.4704 | 1 | 1 | 29
38908.4711 | 881 | 916 | 29
38908.4718 | 902 | 913 | 29
38908.4725 | 332 | 262 | 29
38908.4732 | 1371 | 377 | 29
38908.4738 | 1816 | 511 | 29
38908.4745 | 1748 | 157 | 29
38908.4752 | 2259 | 21 | 29
38908.4759 | 2192 | 13 | 29
38908.4766 | 2200 | 15 | 29
38908.4772 | 2366 | 24 | 29
38908.4779 | 1457 | 562 | 29
38908.4786 | 1184 | 1036 | 29
38908.4555 | 1 | 0 | 30
38908.4562 | 1 | 0 | 30
38908.4569 | 1 | 0 | 30
38908.4575 | 1 | 0 | 30
38908.4582 | 1 | 0 | 30
38908.4589 | 1 | 0 | 30
38908.4596 | 1 | 0 | 30
38908.4603 | 1 | 0 | 30
38908.4609 | 1 | 0 | 30
38908.4616 | 1 | 0 | 30
38908.4623 | 1 | 0 | 30
38908.463 | 1 | 0 | 30
38908.4637 | 1 | 0 | 30
38908.4643 | 1 | 0 | 30
38908.465 | 1 | 0 | 30
38908.4657 | 1 | 0 | 30
38908.4664 | 1 | 0 | 30
38908.467 | 1 | 0 | 30
38908.4677 | 1 | 0 | 30
38908.4684 | 1 | 0 | 30
38908.4691 | 1 | 0 | 30
38908.4698 | 1 | 0 | 30
38908.4705 | 1 | 0 | 30
38908.4711 | 840 | 944 | 30
38908.4718 | 1068 | 1133 | 30
38908.4725 | 411 | 363 | 30
38908.4732 | 1704 | 184 | 30
38908.4739 | 1800 | 559 | 30
38908.4745 | 1833 | 161 | 30
38908.4752 | 2376 | 19 | 30
38908.4759 | 2348 | 13 | 30
38908.4766 | 2144 | 15 | 30
38908.4773 | 1852 | 25 | 30
38908.4779 | 1697 | 634 | 30
38908.4786 | 1139 | 985 | 30
38908.4555 | 1 | 0 | 31
38908.4562 | 1 | 0 | 31
38908.4569 | 1 | 0 | 31
38908.4575 | 1 | 0 | 31
38908.4582 | 1 | 0 | 31
38908.4589 | 1 | 0 | 31
38908.4596 | 1 | 0 | 31
38908.4603 | 1 | 0 | 31
38908.4609 | 1 | 0 | 31
38908.4616 | 1 | 0 | 31
38908.4623 | 1 | 0 | 31
38908.463 | 1 | 0 | 31
38908.4637 | 1 | 0 | 31
38908.4644 | 1 | 0 | 31
38908.465 | 1 | 0 | 31
38908.4657 | 1 | 0 | 31
38908.4664 | 1 | 0 | 31
38908.4671 | 1 | 0 | 31
38908.4678 | 1 | 0 | 31
38908.4684 | 1 | 0 | 31
38908.4691 | 1 | 0 | 31
38908.4698 | 1 | 0 | 31
38908.4705 | 1 | 1 | 31
38908.4712 | 83 | 127 | 31
38908.4718 | 109 | 100 | 31
38908.4725 | 978 | 917 | 31
38908.4732 | 1785 | 164 | 31
38908.4739 | 1467 | 931 | 31
38908.4746 | 2082 | 185 | 31
38908.4752 | 1864 | 24 | 31
38908.4759 | 2267 | 23 | 31
38908.4766 | 2281 | 24 | 31
38908.4773 | 2199 | 38 | 31
38908.478 | 1844 | 669 | 31
38908.4786 | 985 | 880 | 31
38908.4555 | 1 | 0 | 32
38908.4562 | 1 | 0 | 32
38908.4569 | 1 | 0 | 32
38908.4576 | 1 | 0 | 32
38908.4582 | 1 | 0 | 32
38908.4589 | 1 | 0 | 32
38908.4596 | 1 | 0 | 32
38908.4603 | 1 | 0 | 32
38908.461 | 1 | 0 | 32
38908.4616 | 1 | 0 | 32
38908.4623 | 1 | 0 | 32
38908.463 | 1 | 0 | 32
38908.4637 | 1 | 0 | 32
38908.4644 | 1 | 0 | 32
38908.465 | 1 | 0 | 32
38908.4657 | 1 | 0 | 32
38908.4664 | 1 | 0 | 32
38908.4671 | 1 | 0 | 32
38908.4678 | 1 | 0 | 32
38908.4684 | 1 | 0 | 32
38908.4691 | 1 | 0 | 32
38908.4698 | 1 | 0 | 32
38908.4705 | 1 | 0 | 32
38908.4712 | 350 | 338 | 32
38908.4719 | 196 | 187 | 32
38908.4725 | 1153 | 1099 | 32
38908.4732 | 2135 | 166 | 32
38908.4739 | 1403 | 613 | 32
38908.4746 | 2156 | 151 | 32
38908.4753 | 1882 | 24 | 32
38908.4759 | 2092 | 20 | 32
38908.4766 | 1992 | 22 | 32
38908.4773 | 2007 | 36 | 32
38908.478 | 1706 | 868 | 32
38908.4787 | 1148 | 1000 | 32
38908.4555 | 1 | 0 | 33
38908.4562 | 1 | 0 | 33
38908.4569 | 1 | 0 | 33
38908.4576 | 1 | 0 | 33
38908.4583 | 1 | 0 | 33
38908.4589 | 1 | 0 | 33
38908.4596 | 1 | 0 | 33
38908.4603 | 1 | 0 | 33
38908.461 | 1 | 0 | 33
38908.4617 | 1 | 0 | 33
38908.4623 | 1 | 0 | 33
38908.463 | 1 | 0 | 33
38908.4637 | 1 | 0 | 33
38908.4644 | 1 | 0 | 33
38908.4651 | 1 | 0 | 33
38908.4657 | 1 | 0 | 33
38908.4664 | 1 | 0 | 33
38908.4671 | 1 | 0 | 33
38908.4678 | 1 | 0 | 33
38908.4685 | 1 | 0 | 33
38908.4691 | 1 | 0 | 33
38908.4698 | 1 | 0 | 33
38908.4705 | 1 | 0 | 33
38908.4712 | 804 | 780 | 33
38908.4719 | 549 | 522 | 33
38908.4725 | 189 | 122 | 33
38908.4732 | 2156 | 98 | 33
38908.4739 | 1490 | 566 | 33
38908.4746 | 1740 | 137 | 33
38908.4753 | 2277 | 20 | 33
38908.4759 | 1920 | 14 | 33
38908.4766 | 2037 | 18 | 33
38908.4773 | 2314 | 39 | 33
38908.478 | 1741 | 766 | 33
38908.4787 | 1236 | 1087 | 33
38908.4556 | 1 | 0 | 34
38908.4562 | 1 | 0 | 34
38908.4569 | 1 | 0 | 34
38908.4576 | 1 | 0 | 34
38908.4583 | 1 | 0 | 34
38908.459 | 1 | 0 | 34
38908.4596 | 1 | 0 | 34
38908.4603 | 1 | 0 | 34
38908.461 | 1 | 0 | 34
38908.4617 | 1 | 0 | 34
38908.4624 | 1 | 0 | 34
38908.463 | 1 | 0 | 34
38908.4637 | 1 | 0 | 34
38908.4644 | 1 | 0 | 34
38908.4651 | 1 | 0 | 34
38908.4658 | 1 | 0 | 34
38908.4664 | 1 | 0 | 34
38908.4671 | 1 | 0 | 34
38908.4678 | 1 | 0 | 34
38908.4685 | 1 | 0 | 34
38908.4692 | 1 | 0 | 34
38908.4698 | 1 | 0 | 34
38908.4705 | 1 | 0 | 34
38908.4712 | 912 | 877 | 34
38908.4719 | 920 | 879 | 34
38908.4726 | 133 | 114 | 34
38908.4732 | 1870 | 83 | 34
38908.4739 | 1747 | 609 | 34
38908.4746 | 1924 | 118 | 34
38908.4753 | 2155 | 18 | 34
38908.476 | 2211 | 18 | 34
38908.4766 | 2284 | 23 | 34
38908.4773 | 2358 | 42 | 34
38908.478 | 1499 | 671 | 34
38908.4787 | 1118 | 980 | 34
38908.4556 | 1 | 0 | 35
38908.4563 | 1 | 0 | 35
38908.4569 | 1 | 0 | 35
38908.4576 | 1 | 0 | 35
38908.4583 | 1 | 0 | 35
38908.459 | 1 | 0 | 35
38908.4597 | 1 | 0 | 35
38908.4603 | 1 | 0 | 35
38908.461 | 1 | 0 | 35
38908.4617 | 1 | 0 | 35
38908.4624 | 1 | 0 | 35
38908.4631 | 1 | 0 | 35
38908.4637 | 1 | 0 | 35
38908.4644 | 1 | 0 | 35
38908.4651 | 1 | 0 | 35
38908.4658 | 1 | 0 | 35
38908.4665 | 1 | 0 | 35
38908.4671 | 1 | 0 | 35
38908.4678 | 1 | 0 | 35
38908.4685 | 1 | 0 | 35
38908.4692 | 1 | 0 | 35
38908.4699 | 1 | 0 | 35
38908.4705 | 1 | 0 | 35
38908.4712 | 868 | 931 | 35
38908.4719 | 1124 | 1084 | 35
38908.4726 | 923 | 859 | 35
38908.4733 | 1705 | 99 | 35
38908.4739 | 1653 | 621 | 35
38908.4746 | 2094 | 131 | 35
38908.4753 | 1967 | 15 | 35
38908.476 | 2044 | 13 | 35
38908.4767 | 2163 | 17 | 35
38908.4773 | 2256 | 35 | 35
38908.478 | 1692 | 576 | 35
38908.4787 | 985 | 861 | 35
38908.4556 | 1 | 0 | 36
38908.4563 | 1 | 0 | 36
38908.4569 | 1 | 0 | 36
38908.4576 | 1 | 0 | 36
38908.4583 | 1 | 0 | 36
38908.459 | 1 | 0 | 36
38908.4597 | 1 | 0 | 36
38908.4603 | 1 | 0 | 36
38908.461 | 1 | 0 | 36
38908.4617 | 1 | 0 | 36
38908.4624 | 1 | 0 | 36
38908.4631 | 1 | 0 | 36
38908.4638 | 1 | 0 | 36
38908.4644 | 1 | 0 | 36
38908.4651 | 1 | 0 | 36
38908.4658 | 1 | 0 | 36
38908.4665 | 1 | 0 | 36
38908.4672 | 1 | 0 | 36
38908.4678 | 1 | 0 | 36
38908.4685 | 1 | 0 | 36
38908.4692 | 1 | 0 | 36
38908.4699 | 1 | 0 | 36
38908.4706 | 1 | 0 | 36
38908.4712 | 807 | 838 | 36
38908.4719 | 1041 | 1001 | 36
38908.4726 | 1098 | 1030 | 36
38908.4733 | 2211 | 109 | 36
38908.474 | 1530 | 468 | 36
38908.4746 | 2172 | 117 | 36
38908.4753 | 1870 | 15 | 36
38908.476 | 2088 | 14 | 36
38908.4767 | 2266 | 18 | 36
38908.4774 | 1824 | 29 | 36
38908.478 | 1701 | 841 | 36
38908.4787 | 1123 | 981 | 36
38908.4556 | 1 | 0 | 37
38908.4563 | 1 | 0 | 37
38908.457 | 1 | 0 | 37
38908.4576 | 1 | 0 | 37
38908.4583 | 1 | 0 | 37
38908.459 | 1 | 0 | 37
38908.4597 | 1 | 0 | 37
38908.4604 | 1 | 0 | 37
38908.461 | 1 | 0 | 37
38908.4617 | 1 | 0 | 37
38908.4624 | 1 | 0 | 37
38908.4631 | 1 | 0 | 37
38908.4638 | 1 | 0 | 37
38908.4644 | 1 | 0 | 37
38908.4651 | 1 | 0 | 37
38908.4658 | 1 | 0 | 37
38908.4665 | 1 | 0 | 37
38908.4672 | 1 | 0 | 37
38908.4678 | 1 | 0 | 37
38908.4685 | 1 | 0 | 37
38908.4699 | 1 | 0 | 37
38908.4706 | 2 | 1 | 37
38908.4713 | 277 | 268 | 37
38908.4719 | 871 | 839 | 37
38908.4726 | 199 | 144 | 37
38908.4733 | 2019 | 89 | 37
38908.474 | 1459 | 653 | 37
38908.4747 | 2128 | 109 | 37
38908.4753 | 2307 | 20 | 37
38908.476 | 1825 | 16 | 37
38908.4767 | 1961 | 21 | 37
38908.4774 | 1874 | 37 | 37
38908.4781 | 1465 | 914 | 37
38908.4787 | 1153 | 1012 | 37
38908.4556 | 1 | 0 | 38
38908.4563 | 1 | 0 | 38
38908.457 | 1 | 0 | 38
38908.4577 | 1 | 0 | 38
38908.4583 | 1 | 0 | 38
38908.459 | 1 | 0 | 38
38908.4597 | 1 | 0 | 38
38908.4604 | 1 | 0 | 38
38908.4611 | 1 | 0 | 38
38908.4617 | 1 | 0 | 38
38908.4624 | 1 | 0 | 38
38908.4631 | 1 | 0 | 38
38908.4638 | 1 | 0 | 38
38908.4645 | 1 | 0 | 38
38908.4651 | 1 | 0 | 38
38908.4658 | 1 | 0 | 38
38908.4665 | 1 | 0 | 38
38908.4672 | 1 | 0 | 38
38908.4679 | 1 | 0 | 38
38908.4685 | 1 | 0 | 38
38908.4692 | 1 | 0 | 38
38908.4699 | 1 | 0 | 38
38908.4706 | 501 | 512 | 38
38908.4713 | 853 | 885 | 38
38908.4719 | 881 | 899 | 38
38908.4726 | 185 | 168 | 38
38908.4733 | 2218 | 80 | 38
38908.474 | 1574 | 515 | 38
38908.4747 | 1753 | 84 | 38
38908.4753 | 2060 | 17 | 38
38908.476 | 1988 | 17 | 38
38908.4767 | 1983 | 23 | 38
38908.4774 | 2253 | 41 | 38
38908.4781 | 1406 | 731 | 38
38908.4788 | 1206 | 847 | 38
38908.4556 | 1 | 0 | 39
38908.4563 | 1 | 0 | 39
38908.457 | 1 | 0 | 39
38908.4577 | 1 | 0 | 39
38908.4584 | 1 | 0 | 39
38908.459 | 1 | 0 | 39
38908.4597 | 1 | 0 | 39
38908.4604 | 1 | 0 | 39
38908.4611 | 1 | 1 | 39
38908.4618 | 1 | 0 | 39
38908.4624 | 1 | 0 | 39
38908.4631 | 1 | 0 | 39
38908.4638 | 1 | 0 | 39
38908.4645 | 1 | 0 | 39
38908.4652 | 1 | 0 | 39
38908.4658 | 1 | 0 | 39
38908.4665 | 1 | 0 | 39
38908.4672 | 1 | 0 | 39
38908.4679 | 1 | 0 | 39
38908.4686 | 1 | 0 | 39
38908.4692 | 1 | 0 | 39
38908.4699 | 1 | 1 | 39
38908.4706 | 843 | 820 | 39
38908.4713 | 1053 | 1048 | 39
38908.472 | 1122 | 1097 | 39
38908.4726 | 1009 | 937 | 39
38908.4733 | 1807 | 81 | 39
38908.474 | 1569 | 614 | 39
38908.4747 | 1746 | 93 | 39
38908.4754 | 1882 | 11 | 39
38908.476 | 1991 | 13 | 39
38908.4767 | 2144 | 17 | 39
38908.4774 | 2119 | 35 | 39
38908.4781 | 1315 | 750 | 39
38908.4788 | 1146 | 1096 | 39
38908.4556 | 1 | 0 | 40
38908.4563 | 1 | 0 | 40
38908.457 | 1 | 0 | 40
38908.4577 | 1 | 0 | 40
38908.4584 | 1 | 0 | 40
38908.4591 | 1 | 0 | 40
38908.4597 | 1 | 0 | 40
38908.4604 | 1 | 0 | 40
38908.4611 | 1 | 0 | 40
38908.4618 | 1 | 0 | 40
38908.4625 | 1 | 0 | 40
38908.4631 | 1 | 0 | 40
38908.4638 | 1 | 0 | 40
38908.4645 | 1 | 0 | 40
38908.4652 | 1 | 0 | 40
38908.4659 | 1 | 0 | 40
38908.4665 | 1 | 0 | 40
38908.4672 | 1 | 0 | 40
38908.4679 | 1 | 0 | 40
38908.4686 | 1 | 0 | 40
38908.4693 | 1 | 0 | 40
38908.4699 | 1 | 0 | 40
38908.4706 | 849 | 817 | 40
38908.4713 | 1013 | 989 | 40
38908.472 | 1031 | 993 | 40
38908.4727 | 1144 | 1070 | 40
38908.4733 | 1924 | 82 | 40
38908.474 | 1193 | 676 | 40
38908.4747 | 2030 | 95 | 40
38908.4754 | 2014 | 12 | 40
38908.4761 | 2388 | 17 | 40
38908.4767 | 2288 | 20 | 40
38908.4774 | 2361 | 32 | 40
38908.4781 | 1732 | 951 | 40
38908.4788 | 1050 | 885 | 40
38908.4557 | 1 | 0 | 41
38908.4563 | 1 | 0 | 41
38908.457 | 1 | 0 | 41
38908.4577 | 1 | 0 | 41
38908.4584 | 1 | 0 | 41
38908.4591 | 1 | 0 | 41
38908.4597 | 1 | 0 | 41
38908.4604 | 1 | 0 | 41
38908.4611 | 1 | 0 | 41
38908.4618 | 1 | 0 | 41
38908.4625 | 1 | 0 | 41
38908.4631 | 1 | 0 | 41
38908.4638 | 1 | 0 | 41
38908.4645 | 1 | 0 | 41
38908.4652 | 1 | 0 | 41
38908.4659 | 1 | 0 | 41
38908.4666 | 1 | 0 | 41
38908.4672 | 1 | 0 | 41
38908.4679 | 1 | 0 | 41
38908.4686 | 0 | 0 | 41
38908.4693 | 1 | 0 | 41
38908.47 | 19 | 18 | 41
38908.4706 | 1072 | 1048 | 41
38908.4713 | 1140 | 1114 | 41
38908.472 | 887 | 844 | 41
38908.4727 | 387 | 369 | 41
38908.4734 | 2187 | 75 | 41
38908.474 | 1454 | 529 | 41
38908.4747 | 2191 | 87 | 41
38908.4754 | 2029 | 16 | 41
38908.4761 | 1816 | 15 | 41
38908.4768 | 2364 | 22 | 41
38908.4774 | 1858 | 36 | 41
38908.4781 | 1449 | 690 | 41
38908.4788 | 1033 | 903 | 41
38908.4557 | 1 | 0 | 42
38908.4564 | 1 | 0 | 42
38908.457 | 1 | 0 | 42
38908.4577 | 1 | 0 | 42
38908.4584 | 1 | 0 | 42
38908.4591 | 1 | 0 | 42
38908.4598 | 1 | 0 | 42
38908.4604 | 1 | 0 | 42
38908.4611 | 1 | 0 | 42
38908.4618 | 1 | 0 | 42
38908.4625 | 1 | 0 | 42
38908.4632 | 1 | 0 | 42
38908.4638 | 1 | 0 | 42
38908.4645 | 1 | 0 | 42
38908.4652 | 1 | 0 | 42
38908.4659 | 1 | 0 | 42
38908.4666 | 1 | 0 | 42
38908.4672 | 1 | 0 | 42
38908.4679 | 1 | 0 | 42
38908.4686 | 1 | 0 | 42
38908.4693 | 1 | 0 | 42
38908.47 | 772 | 770 | 42
38908.4706 | 1074 | 1048 | 42
38908.4713 | 1170 | 1147 | 42
38908.472 | 1067 | 1025 | 42
38908.4727 | 988 | 910 | 42
38908.4734 | 2132 | 77 | 42
38908.4741 | 1289 | 801 | 42
38908.4747 | 1797 | 63 | 42
38908.4754 | 2195 | 18 | 42
38908.4761 | 2012 | 16 | 42
38908.4768 | 2003 | 19 | 42
38908.4775 | 1961 | 38 | 42
38908.4781 | 1431 | 724 | 42
38908.4788 | 992 | 865 | 42