## Test Facts
Last row in IRMS data sheets: | 41
Time when Penlight power was initiated: | 72

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 12
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III control cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 470C, nominal 17.3 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 72 seconds of baseline data monitoring. Special Note: Test setup and exposure conditions were identical to Penlight Test 11.
DAQ Time | Penlight Time | Event | Interpretation
72 | 0 | Initated Penlight Heating
1345 | 1273 | Conductor 5 shorts to conductor 6 at less than 100 ohms (7) | Initial failure is by shorting between conductors
1361-1365 | 1289-1293 | Conductor 1 shorts to conductors 5 & 6 at less than 100 ohms (49 & 52) | Failures progress to additional conductor-to-conductor shorts and shorts to ground
1379 | 1307 | Conductor 3 shorts to ground at less than 1000 ohms (687) | Initial ground fault failure
1384-1392 | 1312-1320 | Conductor 3 shorts to conductors 4, 5, 6 & 7 (111, 63, 9 & 56)
1396-1401 | 1324-1329 | Conductor 4 shorts to conductors 5, 6 & 7 at less than 100 ohms (55, 90 & 32)
1407-1410 | 1335-1338 | Conductor 7 shorts to conductors 5 & 6 (16 & 250)
1412-1419 | 1340-1347 | Conductor 1 shorts to conductors 2, 3 & 4 at less than 100 ohms (47, 38 & 60) and to ground (274)
1429-1435 | 1357-1363 | Conductor 2 shorts to conductors 3, 4 & 5 (25, 929 & 887)
1447-1451 | 1375-1379 | Conductors 5, 6 & 7 all short to ground at less than 1000 ohms (830, 727 & 866)
1468 | 1396 | The short between conductors 6 & 7 degrades to less than 100 ohms (28)
1485 | 1413 | Conductor 1 shorts to conductor 7 at less than 100 ohms (46)
1490 | 1418 | Conductor 2 shorts to ground at less than 1000 ohms (883)
1496-1499 | 1424-1427 | Conductor 2 shorts to conductors 6 & 7 at less than 100 ohms (5 & 40)
1501 | 1429 | The short between conductors 3 & 4 degrades to less than 100 ohms (23)
1503 | 1431 | Conductor 4 shorts to ground at less than 1000 ohms (461)
1536-1569 | 1464-1497 | The ground shorts for conductors 1 through 7 all degrade to less than 100 ohms (34, 15, 4, 10, 2, 7 & 1) | All conductors have shorted to external ground.
Additional Observations
Observation 1 | The progression of failure modes for this cable followed that expected for a typical thermoset-insulated cable: conductor-to-conductor shorting followed by shorts to ground.
Observation 2 | It took 1273 s (21.2 min.) from the start of Penlight heating for the first conductor-to-conductor short to occur, and it took 1307 s (21.8 min.) for the first short to ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 12 |  |  | 2006-07-10 | 12:56
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-63.9167 | 242438 |  | -52.25 | 241838 | -44.25 | 243438 | -39.25 | 243738 | -35.9167 | 243738 | -33.5 | 241838 | -31.25 | 243238 | -63.9167 | 241838
-5.0833 | 242438 |  | 6.5833 | 241838 | 14.4167 | 243438 | 19.5833 | 243738 | 23 | 243738 | 25.25 | 241838 | 27.5833 | 243238 | -5.0833 | 241838
53.6667 | 242438 |  | 65.3333 | 241838 | 73.3333 | 121669 | 78.5 | 123769 | 81.6667 | 243738 | 84 | 121669 | 86.3333 | 123569 | 53.6667 | 121669
112.5 | 242438 |  | 124.1667 | 241838 | 132.1667 | 121669 | 137.25 | 243738 | 140.5 | 243738 | 142.8333 | 241838 | 145.0833 | 243238 | 112.5 | 121669
171.3333 | 242438 |  | 183 | 241838 | 190.8333 | 243438 | 196.0833 | 243738 | 199.25 | 123669 | 201.5833 | 123219 | 204.0833 | 243238 | 171.3333 | 123219
230.0833 | 242438 |  | 241.75 | 241838 | 249.75 | 243438 | 254.8333 | 243738 | 258.0833 | 243738 | 260.5 | 241838 | 262.8333 | 243238 | 230.0833 | 241838
288.9167 | 242438 |  | 300.5833 | 241838 | 308.4167 | 243438 | 313.5833 | 243738 | 317 | 243738 | 319.25 | 241838 | 321.5833 | 124919 | 288.9167 | 124919
347.6667 | 242438 |  | 359.3333 | 241838 | 367.3333 | 243438 | 372.5 | 243738 | 375.6667 | 243738 | 378 | 241838 | 380.3333 | 243238 | 347.6667 | 241838
406.5 | 242438 |  | 418.1667 | 241838 | 426.1667 | 243438 | 431.25 | 243738 | 434.5 | 123669 | 436.8333 | 241838 | 439.0833 | 243238 | 406.5 | 123669
465.3333 | 242438 |  | 477 | 241838 | 484.8333 | 243438 | 490.0833 | 243738 | 493.25 | 123869 | 495.5833 | 241838 | 498.0833 | 243238 | 465.3333 | 123869
524.0833 | 242438 |  | 535.75 | 241838 | 543.6667 | 243438 | 548.6667 | 243738 | 552.0833 | 243738 | 554.5 | 241838 | 556.75 | 243238 | 524.0833 | 241838
582.8333 | 242438 |  | 594.5 | 241838 | 602.3333 | 243438 | 607.5833 | 243738 | 611 | 243738 | 613.1667 | 241838 | 615.5833 | 243238 | 582.8333 | 241838
641.6667 | 242438 |  | 653.25 | 241838 | 661.25 | 243438 | 666.4167 | 243738 | 669.5833 | 243738 | 672 | 241838 | 674.3333 | 243238 | 641.6667 | 241838
700.4167 | 242438 |  | 712.1667 | 241838 | 720 | 121669 | 725.25 | 243738 | 728.4167 | 122819 | 730.5833 | 241838 | 733 | 243238 | 700.4167 | 121669
759.25 | 242438 |  | 770.9167 | 241838 | 778.8333 | 243438 | 783.9167 | 243738 | 787.1667 | 243738 | 789.5833 | 241838 | 792 | 243238 | 759.25 | 241838
817.9167 | 242438 |  | 829.6667 | 241838 | 837.5833 | 243438 | 842.75 | 243738 | 846.0833 | 243738 | 848.3333 | 241838 | 850.6667 | 243238 | 817.9167 | 241838
876.75 | 242438 |  | 888.5 | 241838 | 896.4167 | 243438 | 901.5 | 243738 | 904.8333 | 243738 | 907.1667 | 241838 | 909.3333 | 243238 | 876.75 | 241838
935.5833 | 242438 |  | 947.25 | 123869 | 955.1667 | 243438 | 960.4167 | 243738 | 963.5833 | 243738 | 965.8333 | 241838 | 968.1667 | 243238 | 935.5833 | 123869
994.3333 | 242438 |  | 1006 | 123869 | 1013.9167 | 243438 | 1019.0833 | 243738 | 1022.3333 | 243738 | 1024.75 | 241838 | 1027.0833 | 243238 | 994.3333 | 123869
1053.1667 | 242438 |  | 1064.75 | 241838 | 1072.75 | 243438 | 1077.8333 | 122619 | 1081.0833 | 243738 | 1083.5 | 241838 | 1085.75 | 122619 | 1053.1667 | 122619
1111.9167 | 242438 |  | 1123.5833 | 241838 | 1131.5 | 123669 | 1136.6667 | 243738 | 1140 | 243738 | 1142.25 | 241838 | 1144.5833 | 243238 | 1111.9167 | 123669
1170.5833 | 242438 |  | 1182.4167 | 122619 | 1190.3333 | 243438 | 1195.4167 | 243738 | 1198.6667 | 243738 | 1201 | 241838 | 1203.4167 | 243238 | 1170.5833 | 122619
1229.5 | 121169 |  | 1241.1667 | 241838 | 1249.1667 | 243438 | 1254.25 | 243738 | 1257.5 | 1709.3152 | 1259.8333 | 1962.5869 | 1262.0833 | 81168.1368 | 1229.5 | 1709.3152
1288.3333 | 1720.6793 |  | 1300 | 122944.4857 | 1307.8333 | 687.2707 | 1313.0833 | 1421.2641 | 1316.25 | 1507.8648 | 1318.5833 | 1568.2108 | 1321.0833 | 1970.2996 | 1288.3333 | 687.2707
1347.0833 | 274.206 |  | 1358.75 | 1332.3832 | 1366.75 | 465.0326 | 1371.75 | 2871.6759 | 1375.0833 | 830.6572 | 1377.5 | 727.3391 | 1379.75 | 866.3864 | 1347.0833 | 274.206
1405.9167 | 242.3996 |  | 1417.5833 | 882.9061 | 1425.4167 | 582.1193 | 1430.5833 | 461.231 | 1434 | 493.1145 | 1436.25 | 140.0515 | 1438.5833 | 401.9645 | 1405.9167 | 140.0515
1464.6667 | 33.8334 |  | 1476.3333 | 14.5662 | 1484.3333 | 4.076 | 1489.5 | 9.9192 | 1492.6667 | 1.7348 | 1495 | 6.5881 | 1497.3333 | 1.2428 | 1464.6667 | 1.2428
1523.5 | 0.68502 |  | 1535.1667 | 3.6954 | 1543.1667 | 4.3467 | 1548.25 | 2.6501 | 1551.5 | 5.2897 | 1553.8333 | 2.6254 | 1556.0833 | 3.6344 | 1523.5 | 0.68502
1582.3333 | 8.0633 |  | 1594 | 1.5602 | 1601.8333 | 6.2688 | 1607.0833 | 14.0108 | 1610.25 | 7.7961 | 1612.5833 | 11.9788 | 1615.0833 | 10.0096 | 1582.3333 | 1.5602
1641.0833 | 48.5752 |  | 1652.9167 | 5.7074 | 1660.9167 | 11.5669 | 1665.75 | 2.5869 | 1669.0833 | 0.68018 | 1671.5 | 21.1494 | 1673.75 | 0.67489 | 1641.0833 | 0.67489
1699.9167 | 0.67387 |  | 1711.5833 | 0.72288 | 1719.4167 | 0.66919 | 1724.5833 | 0.6695 | 1728 | 0.67887 | 1730.25 | 0.68087 | 1732.5833 | 3.9615 | 1699.9167 | 0.66919
1758.6667 | 3.6126 |  | 1770.3333 | 0.68249 | 1778.25 | 0.66519 | 1783.5 | 0.67864 | 1786.5 | 0.67316 | 1789 | 0.67968 | 1791.25 | 0.67509 | 1758.6667 | 0.66519
1817.5 | 0.66441 |  | 1829.1667 | 0.67566 | 1837.1667 | 1.3336 | 1842.25 | 3.8339 | 1845.5 | 0.7979 | 1847.8333 | 7.651 | 1850.0833 | 0.67323 | 1817.5 | 0.66441
1876.3333 | 2.4007 |  | 1888 | 0.68741 | 1895.8333 | 0.72244 | 1901.0833 | 1.897 | 1904.25 | 2.031 | 1906.5833 | 0.68351 | 1909.0833 | 1.4429 | 1876.3333 | 0.68351
1935.0833 | 2.9778 |  | 1946.75 | 1.443 | 1954.75 | 10.8555 | 1959.6667 | 4.5711 | 1963.0833 | 8.2771 | 1965.4167 | 5.7001 | 1967.75 | 9.416 | 1935.0833 | 1.443
1993.8333 | 9.5028 |  | 2005.5833 | 6.6771 | 2013.4167 | 5.5521 | 2018.5833 | 3.9769 | 2022 | 19.1886 | 2024.25 | 4.5524 | 2026.5 | 5.2176 | 1993.8333 | 3.9769

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 12 |  |  | 2006-07-10 | 12:56
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-63.9167 | 246454.6667 |  | -52.25 | 246004.6667 | -44.25 | 246688 | -39.25 | 246204.6667 | -35.9167 | 246688 | -33.5 | 244138 | -31.25 | 247021.3333 | -63.9167 | 244138
-5.0833 | 246454.6667 |  | 6.5833 | 246004.6667 | 14.4167 | 246688 | 19.5833 | 246204.6667 | 23 | 246688 | 25.25 | 244138 | 27.5833 | 247021.3333 | -5.0833 | 244138
53.6667 | 246454.6667 |  | 65.3333 | 246004.6667 | 73.3333 | 226393.1667 | 78.5 | 225559.8333 | 81.6667 | 246688 | 84 | 223843.1667 | 86.3333 | 226409.8333 | 53.6667 | 223843.1667
112.5 | 246454.6667 |  | 124.1667 | 246004.6667 | 132.1667 | 226393.1667 | 137.25 | 246204.6667 | 140.5 | 246688 | 142.8333 | 244138 | 145.0833 | 247021.3333 | 112.5 | 226393.1667
171.3333 | 246454.6667 |  | 183 | 246004.6667 | 190.8333 | 246688 | 196.0833 | 246204.6667 | 199.25 | 226059.8333 | 201.5833 | 223584.8333 | 204.0833 | 247021.3333 | 171.3333 | 223584.8333
230.0833 | 246454.6667 |  | 241.75 | 246004.6667 | 249.75 | 246688 | 254.8333 | 246204.6667 | 258.0833 | 246688 | 260.5 | 244138 | 262.8333 | 247021.3333 | 230.0833 | 244138
288.9167 | 246454.6667 |  | 300.5833 | 246004.6667 | 308.4167 | 246688 | 313.5833 | 246204.6667 | 317 | 246688 | 319.25 | 244138 | 321.5833 | 226184.8333 | 288.9167 | 226184.8333
347.6667 | 246454.6667 |  | 359.3333 | 246004.6667 | 367.3333 | 246688 | 372.5 | 246204.6667 | 375.6667 | 246688 | 378 | 244138 | 380.3333 | 247021.3333 | 347.6667 | 244138
406.5 | 246454.6667 |  | 418.1667 | 246004.6667 | 426.1667 | 246688 | 431.25 | 246204.6667 | 434.5 | 226059.8333 | 436.8333 | 244138 | 439.0833 | 247021.3333 | 406.5 | 226059.8333
465.3333 | 246454.6667 |  | 477 | 246004.6667 | 484.8333 | 246688 | 490.0833 | 246204.6667 | 493.25 | 226026.5 | 495.5833 | 244138 | 498.0833 | 247021.3333 | 465.3333 | 226026.5
524.0833 | 246454.6667 |  | 535.75 | 246004.6667 | 543.6667 | 246688 | 548.6667 | 246204.6667 | 552.0833 | 246688 | 554.5 | 244138 | 556.75 | 247021.3333 | 524.0833 | 244138
582.8333 | 246454.6667 |  | 594.5 | 246004.6667 | 602.3333 | 246688 | 607.5833 | 246204.6667 | 611 | 246688 | 613.1667 | 244138 | 615.5833 | 247021.3333 | 582.8333 | 244138
641.6667 | 246454.6667 |  | 653.25 | 246004.6667 | 661.25 | 246688 | 666.4167 | 246204.6667 | 669.5833 | 246688 | 672 | 244138 | 674.3333 | 247021.3333 | 641.6667 | 244138
700.4167 | 246454.6667 |  | 712.1667 | 246004.6667 | 720 | 226393.1667 | 725.25 | 246204.6667 | 728.4167 | 226201.5 | 730.5833 | 244138 | 733 | 247021.3333 | 700.4167 | 226201.5
759.25 | 246454.6667 |  | 770.9167 | 246004.6667 | 778.8333 | 246688 | 783.9167 | 246204.6667 | 787.1667 | 246688 | 789.5833 | 244138 | 792 | 247021.3333 | 759.25 | 244138
817.9167 | 246454.6667 |  | 829.6667 | 246004.6667 | 837.5833 | 246688 | 842.75 | 246204.6667 | 846.0833 | 246688 | 848.3333 | 244138 | 850.6667 | 247021.3333 | 817.9167 | 244138
876.75 | 246454.6667 |  | 888.5 | 246004.6667 | 896.4167 | 246688 | 901.5 | 246204.6667 | 904.8333 | 246688 | 907.1667 | 244138 | 909.3333 | 247021.3333 | 876.75 | 244138
935.5833 | 246454.6667 |  | 947.25 | 225343.1667 | 955.1667 | 246688 | 960.4167 | 246204.6667 | 963.5833 | 246688 | 965.8333 | 244138 | 968.1667 | 247021.3333 | 935.5833 | 225343.1667
994.3333 | 246454.6667 |  | 1006 | 225343.1667 | 1013.9167 | 246688 | 1019.0833 | 246204.6667 | 1022.3333 | 246688 | 1024.75 | 244138 | 1027.0833 | 247021.3333 | 994.3333 | 225343.1667
1053.1667 | 246454.6667 |  | 1064.75 | 246004.6667 | 1072.75 | 246688 | 1077.8333 | 225751.5 | 1081.0833 | 246688 | 1083.5 | 244138 | 1085.75 | 226568.1667 | 1053.1667 | 225751.5
1111.9167 | 246454.6667 |  | 1123.5833 | 246004.6667 | 1131.5 | 226059.8333 | 1136.6667 | 246204.6667 | 1140 | 246688 | 1142.25 | 244138 | 1144.5833 | 247021.3333 | 1111.9167 | 226059.8333
1170.5833 | 246454.6667 |  | 1182.4167 | 225551.5 | 1190.3333 | 246688 | 1195.4167 | 246204.6667 | 1198.6667 | 246688 | 1201 | 244138 | 1203.4167 | 247021.3333 | 1170.5833 | 225551.5
1229.5 | 102227609.9067 |  | 1241.1667 | 246004.6667 | 1249.1667 | 246688 | 1254.25 | 246204.6667 | 1257.5 | 154181.5141 | 1259.8333 | 183080.6459 | 1262.0833 | 178703.5761 | 1229.5 | 154181.5141
1288.3333 | 102091806.7897 |  | 1300 | 49104169.1533 | 1307.8333 | 99868.7159 | 1313.0833 | 25990.5639 | 1316.25 | 24883.7012 | 1318.5833 | 53729.6104 | 1321.0833 | 16586.5803 | 1288.3333 | 16586.5803
1347.0833 | 15312.1644 |  | 1358.75 | 8604.9624 | 1366.75 | 3901.6759 | 1371.75 | 8845.0945 | 1375.0833 | 12501.7042 | 1377.5 | 17143.92 | 1379.75 | 8980.1111 | 1347.0833 | 3901.6759
1405.9167 | 1727.3878 |  | 1417.5833 | 2323.8293 | 1425.4167 | 2841.712 | 1430.5833 | 1853.2109 | 1434 | 4911.5564 | 1436.25 | 2292.9378 | 1438.5833 | 930.0059 | 1405.9167 | 930.0059
1464.6667 | 216.3808 |  | 1476.3333 | 2878.1829 | 1484.3333 | 236.063 | 1489.5 | 236.9627 | 1492.6667 | 30.1844 | 1495 | 23.564 | 1497.3333 | 139.1366 | 1464.6667 | 23.564
1523.5 | 11.9539 |  | 1535.1667 | 16.4031 | 1543.1667 | 15.5196 | 1548.25 | 21.4767 | 1551.5 | 15.282 | 1553.8333 | 27.6163 | 1556.0833 | 18.4612 | 1523.5 | 11.9539
1582.3333 | 67.7982 |  | 1594 | 14.7062 | 1601.8333 | 21.1509 | 1607.0833 | 95.6423 | 1610.25 | 59.1965 | 1612.5833 | 63.4498 | 1615.0833 | 55.9147 | 1582.3333 | 14.7062
1641.0833 | 331.5705 |  | 1652.9167 | 105.8988 | 1660.9167 | 84.3146 | 1665.75 | 1917.1309 | 1669.0833 | 236.4837 | 1671.5 | 98.6405 | 1673.75 | 47.7608 | 1641.0833 | 47.7608
1699.9167 | 11.1103 |  | 1711.5833 | 15.8171 | 1719.4167 | 18.4117 | 1724.5833 | 17.4926 | 1728 | 12.336 | 1730.25 | 14.5818 | 1732.5833 | 20.0021 | 1699.9167 | 11.1103
1758.6667 | 14.8238 |  | 1770.3333 | 16.9871 | 1778.25 | 10.5695 | 1783.5 | 7.8534 | 1786.5 | 14.2802 | 1789 | 8.1361 | 1791.25 | 12.0392 | 1758.6667 | 7.8534
1817.5 | 9.4372 |  | 1829.1667 | 10.588 | 1837.1667 | 10.7022 | 1842.25 | 14.3319 | 1845.5 | 13.6734 | 1847.8333 | 12.3722 | 1850.0833 | 11.2324 | 1817.5 | 9.4372
1876.3333 | 13.1408 |  | 1888 | 20.5221 | 1895.8333 | 11.8963 | 1901.0833 | 13.2538 | 1904.25 | 17.6598 | 1906.5833 | 17.094 | 1909.0833 | 30.1899 | 1876.3333 | 11.8963
1935.0833 | 12.6869 |  | 1946.75 | 20.812 | 1954.75 | 24.0104 | 1959.6667 | 19.5241 | 1963.0833 | 28.0197 | 1965.4167 | 19.956 | 1967.75 | 32.1505 | 1935.0833 | 12.6869
1993.8333 | 33.2312 |  | 2005.5833 | 78.5271 | 2013.4167 | 18.6731 | 2018.5833 | 25.0033 | 2022 | 40.2565 | 2024.25 | 10.7693 | 2026.5 | 36.0883 | 1993.8333 | 10.7693

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 12 |  |  | 2006-07-10 | 12:56
XLPE | 7-C | Tray
470 C | 17.3 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-71 | 242437.9994 | -68 | 247437.9994 | -65.5 | 248637.9994 | -62.5 | 248437.9994 | -59.5 | 242837.9994 | -57 | 248937.9994 | -54 | 248637.9994 | -51.5 | 245337.9994 | -48.5 | 247837.9994 | -45.5 | 241837.9994 | -43 | 249937.9994 | -40 | 247637.9994 | -37.5 | 245737.9994 | -34.5 | 243437.9994 | -31.5 | 247237.9994 | -29 | 243737.9994 | -26 | 246537.9994 | -23.5 | 245337.9994 | -20.5 | 246937.9994 | -17.5 | 247437.9994 | -15 | 243237.9994 | -71 | 241837.9994
-12 | 242437.9994 | -9.5 | 247437.9994 | -6.5 | 248637.9994 | -3.5 | 248437.9994 | -1 | 242837.9994 | 2 | 248937.9994 | 4.5 | 248637.9994 | 7.5 | 245337.9994 | 10.5 | 247837.9994 | 13 | 241837.9994 | 16 | 249937.9994 | 18.5 | 247637.9994 | 21.5 | 245737.9994 | 24.5 | 243437.9994 | 27 | 247237.9994 | 30 | 243737.9994 | 32.5 | 246537.9994 | 35.5 | 245337.9994 | 38.5 | 246937.9994 | 41 | 247437.9994 | 44 | 243237.9994 | -12 | 241837.9994
46.5 | 242437.9994 | 49.5 | 247437.9994 | 52.5 | 248637.9994 | 55 | 248437.9994 | 58 | 242837.9994 | 60.5 | 248937.9994 | 63.5 | 248637.9994 | 66.5 | 245337.9994 | 69 | 247837.9994 | 72 | 241837.9994 | 74.5 | 249937.9994 | 77.5 | 247637.9994 | 80.5 | 245737.9994 | 83 | 121668.9988 | 86 | 247237.9994 | 88.5 | 243737.9994 | 91.5 | 246537.9994 | 94.5 | 245337.9994 | 97 | 246937.9994 | 100 | 247437.9994 | 102.5 | 243237.9994 | 46.5 | 121668.9988
105.5 | 242437.9994 | 108.5 | 247437.9994 | 111 | 248637.9994 | 114 | 248437.9994 | 116.5 | 242837.9994 | 119.5 | 248937.9994 | 122.5 | 248637.9994 | 125 | 245337.9994 | 128 | 247837.9994 | 130.5 | 241837.9994 | 133.5 | 249937.9994 | 136.5 | 247637.9994 | 139 | 245737.9994 | 142 | 121668.9988 | 144.5 | 247237.9994 | 147.5 | 243737.9994 | 150.5 | 246537.9994 | 153 | 245337.9994 | 156 | 246937.9994 | 158.5 | 247437.9994 | 161.5 | 243237.9994 | 105.5 | 121668.9988
164.5 | 242437.9994 | 167 | 247437.9994 | 170 | 248637.9994 | 172.5 | 248437.9994 | 175.5 | 242837.9994 | 178.5 | 248937.9994 | 181 | 248637.9994 | 184 | 245337.9994 | 186.5 | 247837.9994 | 189.5 | 241837.9994 | 192.5 | 249937.9994 | 195 | 247637.9994 | 198 | 245737.9994 | 200.5 | 243437.9994 | 203.5 | 247237.9994 | 206.5 | 243737.9994 | 209 | 246537.9994 | 212 | 245337.9994 | 214.5 | 246937.9994 | 217.5 | 123668.9988 | 220.5 | 243237.9994 | 164.5 | 123668.9988
223 | 242437.9994 | 226 | 247437.9994 | 228.5 | 248637.9994 | 231.5 | 248437.9994 | 234.5 | 242837.9994 | 237 | 248937.9994 | 240 | 248637.9994 | 242.5 | 245337.9994 | 245.5 | 247837.9994 | 248.5 | 241837.9994 | 251 | 249937.9994 | 254 | 247637.9994 | 256.5 | 245737.9994 | 259.5 | 243437.9994 | 262.5 | 247237.9994 | 265 | 243737.9994 | 268 | 246537.9994 | 271 | 245337.9994 | 273.5 | 246937.9994 | 276.5 | 247437.9994 | 279 | 243237.9994 | 223 | 241837.9994
282 | 242437.9994 | 284.5 | 247437.9994 | 287.5 | 248637.9994 | 290.5 | 248437.9994 | 293 | 242837.9994 | 296 | 248937.9994 | 298.5 | 248637.9994 | 301.5 | 245337.9994 | 304.5 | 247837.9994 | 307 | 241837.9994 | 310 | 249937.9994 | 312.5 | 247637.9994 | 315.5 | 245737.9994 | 318.5 | 243437.9994 | 321 | 247237.9994 | 324 | 243737.9994 | 326.5 | 246537.9994 | 329.5 | 245337.9994 | 332.5 | 246937.9994 | 335 | 247437.9994 | 338 | 243237.9994 | 282 | 241837.9994
340.5 | 242437.9994 | 343.5 | 247437.9994 | 346.5 | 248637.9994 | 349 | 248437.9994 | 352 | 242837.9994 | 354.5 | 248937.9994 | 357.5 | 248637.9994 | 360.5 | 245337.9994 | 363 | 247837.9994 | 366 | 241837.9994 | 368.5 | 249937.9994 | 371.5 | 247637.9994 | 374.5 | 245737.9994 | 377 | 243437.9994 | 380 | 247237.9994 | 382.5 | 243737.9994 | 385.5 | 246537.9994 | 388.5 | 245337.9994 | 391 | 246937.9994 | 394 | 247437.9994 | 396.5 | 243237.9994 | 340.5 | 241837.9994
399.5 | 242437.9994 | 402.5 | 247437.9994 | 405 | 248637.9994 | 408 | 248437.9994 | 410.5 | 242837.9994 | 413.5 | 248937.9994 | 416.5 | 248637.9994 | 419 | 245337.9994 | 422 | 247837.9994 | 424.5 | 241837.9994 | 427.5 | 249937.9994 | 430.5 | 247637.9994 | 433 | 245737.9994 | 436 | 243437.9994 | 438.5 | 247237.9994 | 441.5 | 243737.9994 | 444.5 | 246537.9994 | 447 | 245337.9994 | 450 | 246937.9994 | 452.5 | 123668.9988 | 455.5 | 243237.9994 | 399.5 | 123668.9988
458.5 | 242437.9994 | 461 | 247437.9994 | 464 | 248637.9994 | 466.5 | 248437.9994 | 469.5 | 242837.9994 | 472.5 | 248937.9994 | 475 | 248637.9994 | 478 | 245337.9994 | 480.5 | 247837.9994 | 483.5 | 241837.9994 | 486.5 | 249937.9994 | 489 | 247637.9994 | 492 | 245737.9994 | 494.5 | 243437.9994 | 497.5 | 247237.9994 | 500.5 | 243737.9994 | 503 | 246537.9994 | 506 | 245337.9994 | 508.5 | 246937.9994 | 511.5 | 247437.9994 | 514.5 | 243237.9994 | 458.5 | 241837.9994
517 | 242437.9994 | 520 | 247437.9994 | 522.5 | 248637.9994 | 525.5 | 248437.9994 | 528.5 | 242837.9994 | 531 | 248937.9994 | 534 | 248637.9994 | 536.5 | 245337.9994 | 539.5 | 247837.9994 | 542.5 | 241837.9994 | 545 | 249937.9994 | 547.5 | 247637.9994 | 550.5 | 245737.9994 | 553.5 | 243437.9994 | 556.5 | 247237.9994 | 559 | 243737.9994 | 562 | 246537.9994 | 564.5 | 245337.9994 | 567.5 | 246937.9994 | 570.5 | 247437.9994 | 573 | 243237.9994 | 517 | 241837.9994
575.5 | 242437.9994 | 578.5 | 247437.9994 | 581.5 | 248637.9994 | 584.5 | 248437.9994 | 587 | 242837.9994 | 590 | 248937.9994 | 592.5 | 248637.9994 | 595.5 | 245337.9994 | 598.5 | 247837.9994 | 601 | 241837.9994 | 604 | 249937.9994 | 606.5 | 247637.9994 | 609.5 | 245737.9994 | 612 | 243437.9994 | 615 | 247237.9994 | 618 | 243737.9994 | 620.5 | 246537.9994 | 623.5 | 245337.9994 | 626.5 | 246937.9994 | 629 | 247437.9994 | 632 | 243237.9994 | 575.5 | 241837.9994
634.5 | 242437.9994 | 637.5 | 247437.9994 | 640.5 | 248637.9994 | 643 | 248437.9994 | 646 | 242837.9994 | 648.5 | 248937.9994 | 651.5 | 248637.9994 | 654 | 245337.9994 | 657 | 247837.9994 | 660 | 241837.9994 | 662.5 | 249937.9994 | 665.5 | 247637.9994 | 668 | 245737.9994 | 671 | 243437.9994 | 674 | 247237.9994 | 676.5 | 243737.9994 | 679.5 | 246537.9994 | 682.5 | 245337.9994 | 685 | 246937.9994 | 688 | 247437.9994 | 690.5 | 243237.9994 | 634.5 | 241837.9994
693.5 | 242437.9994 | 696 | 247437.9994 | 699 | 248637.9994 | 702 | 248437.9994 | 704.5 | 242837.9994 | 707.5 | 248937.9994 | 710.5 | 248637.9994 | 713 | 245337.9994 | 716 | 247837.9994 | 718.5 | 241837.9994 | 721.5 | 249937.9994 | 724.5 | 247637.9994 | 727 | 245737.9994 | 729.5 | 121668.9988 | 732.5 | 247237.9994 | 735.5 | 243737.9994 | 738.5 | 246537.9994 | 741 | 245337.9994 | 743.5 | 246937.9994 | 746.5 | 247437.9994 | 749 | 243237.9994 | 693.5 | 121668.9988
752.5 | 242437.9994 | 755 | 247437.9994 | 757.5 | 248637.9994 | 760.5 | 248437.9994 | 763.5 | 242837.9994 | 766.5 | 248937.9994 | 769 | 248637.9994 | 772 | 245337.9994 | 774.5 | 247837.9994 | 777.5 | 241837.9994 | 780 | 249937.9994 | 783 | 247637.9994 | 786 | 245737.9994 | 788.5 | 243437.9994 | 791.5 | 247237.9994 | 794 | 243737.9994 | 797 | 246537.9994 | 800 | 245337.9994 | 802.5 | 246937.9994 | 805.5 | 247437.9994 | 808.5 | 243237.9994 | 752.5 | 241837.9994
811 | 242437.9994 | 813.5 | 247437.9994 | 816.5 | 248637.9994 | 819.5 | 248437.9994 | 822 | 242837.9994 | 825 | 248937.9994 | 828 | 248637.9994 | 830.5 | 245337.9994 | 833.5 | 247837.9994 | 836 | 241837.9994 | 839 | 249937.9994 | 842 | 247637.9994 | 844.5 | 245737.9994 | 847.5 | 243437.9994 | 850 | 247237.9994 | 853 | 243737.9994 | 856 | 246537.9994 | 858.5 | 245337.9994 | 861.5 | 246937.9994 | 864.5 | 247437.9994 | 867 | 243237.9994 | 811 | 241837.9994
870 | 242437.9994 | 872.5 | 247437.9994 | 875.5 | 248637.9994 | 878 | 248437.9994 | 881 | 242837.9994 | 883.5 | 248937.9994 | 886.5 | 248637.9994 | 889.5 | 245337.9994 | 892.5 | 247837.9994 | 895 | 241837.9994 | 897.5 | 249937.9994 | 900.5 | 247637.9994 | 903.5 | 245737.9994 | 906.5 | 243437.9994 | 909 | 247237.9994 | 911.5 | 243737.9994 | 914.5 | 246537.9994 | 917.5 | 245337.9994 | 920.5 | 246937.9994 | 923 | 247437.9994 | 925.5 | 243237.9994 | 870 | 241837.9994
928.5 | 242437.9994 | 931.5 | 247437.9994 | 934.5 | 248637.9994 | 937 | 248437.9994 | 939.5 | 242837.9994 | 942.5 | 248937.9994 | 945.5 | 248637.9994 | 948.5 | 245337.9994 | 951 | 123868.9988 | 953.5 | 241837.9994 | 956.5 | 249937.9994 | 959.5 | 247637.9994 | 962 | 245737.9994 | 965 | 243437.9994 | 967.5 | 247237.9994 | 970.5 | 243737.9994 | 973.5 | 246537.9994 | 976 | 245337.9994 | 979 | 246937.9994 | 982 | 247437.9994 | 984.5 | 243237.9994 | 928.5 | 123868.9988
987.5 | 242437.9994 | 990 | 247437.9994 | 993 | 248637.9994 | 995.5 | 248437.9994 | 998.5 | 242837.9994 | 1001.5 | 248937.9994 | 1004 | 248637.9994 | 1007 | 245337.9994 | 1009.5 | 123868.9988 | 1012.5 | 241837.9994 | 1015.5 | 249937.9994 | 1018 | 247637.9994 | 1021 | 245737.9994 | 1024 | 243437.9994 | 1026.5 | 247237.9994 | 1029.5 | 243737.9994 | 1032 | 246537.9994 | 1035 | 245337.9994 | 1038 | 246937.9994 | 1040.5 | 247437.9994 | 1043.5 | 243237.9994 | 987.5 | 123868.9988
1046 | 242437.9994 | 1049 | 247437.9994 | 1052 | 248637.9994 | 1054.5 | 248437.9994 | 1057.5 | 242837.9994 | 1060 | 248937.9994 | 1063 | 248637.9994 | 1065.5 | 245337.9994 | 1068.5 | 247837.9994 | 1071.5 | 241837.9994 | 1074 | 249937.9994 | 1077 | 247637.9994 | 1079.5 | 245737.9994 | 1082.5 | 243437.9994 | 1085.5 | 247237.9994 | 1088 | 243737.9994 | 1091 | 246537.9994 | 1093.5 | 245337.9994 | 1096.5 | 246937.9994 | 1099.5 | 247437.9994 | 1102 | 243237.9994 | 1046 | 241837.9994
1105 | 242437.9994 | 1107.5 | 247437.9994 | 1110.5 | 248637.9994 | 1113.5 | 248437.9994 | 1116 | 242837.9994 | 1119 | 248937.9994 | 1121.5 | 248637.9994 | 1124.5 | 245337.9994 | 1127.5 | 247837.9994 | 1130 | 241837.9994 | 1133 | 249937.9994 | 1136 | 247637.9994 | 1138.5 | 245737.9994 | 1141.5 | 243437.9994 | 1144 | 247237.9994 | 1147 | 243737.9994 | 1149.5 | 246537.9994 | 1152.5 | 245337.9994 | 1155.5 | 246937.9994 | 1158 | 247437.9994 | 1161 | 243237.9994 | 1105 | 241837.9994
1163.5 | 242437.9994 | 1166.5 | 247437.9994 | 1169 | 248637.9994 | 1172 | 248437.9994 | 1175 | 242837.9994 | 1177.5 | 248937.9994 | 1180.5 | 248637.9994 | 1183.5 | 122618.9988 | 1186 | 247837.9994 | 1189 | 241837.9994 | 1192 | 249937.9994 | 1194.5 | 247637.9994 | 1197.5 | 245737.9994 | 1200 | 243437.9994 | 1203 | 247237.9994 | 1205.5 | 243737.9994 | 1208.5 | 246537.9994 | 1211.5 | 245337.9994 | 1214 | 12141.983 | 1217 | 247437.9994 | 1219.5 | 243237.9994 | 1163.5 | 12141.983
1222.5 | 121168.9988 | 1225.5 | 247238.0808 | 1228 | 248637.9994 | 1231 | 248437.9994 | 1233.5 | 242837.9994 | 1236.5 | 248937.9994 | 1239.5 | 248338.1206 | 1242 | 245337.9994 | 1245 | 247837.9994 | 1247.5 | 241837.9994 | 1250.5 | 249937.9994 | 1253.5 | 247637.9994 | 1256 | 245737.9994 | 1259 | 243437.9994 | 1261.5 | 247237.9994 | 1264.5 | 243737.9994 | 1267.5 | 246537.9994 | 1270 | 245337.9994 | 1273 | 6.936 | 1275.5 | 35191.3617 | 1278.5 | 60609.8281 | 1222.5 | 6.936
1281.5 | 121118.9588 | 1284 | 247238.0404 | 1287 | 13595.5814 | 1289.5 | 48.7452 | 1292.5 | 52.1728 | 1295.5 | 1968.3056 | 1298 | 35319.9894 | 1301 | 48867.9009 | 1303.5 | 49387.7933 | 1306.5 | 80446.0688 | 1309.5 | 41388.3975 | 1312 | 111.3826 | 1315 | 62.5357 | 1317.5 | 8.7397 | 1320.5 | 55.6836 | 1323.5 | 55.4344 | 1326 | 89.7091 | 1329 | 32.1657 | 1331.5 | 28.8344 | 1334.5 | 15.7953 | 1337.5 | 250.8414 | 1281.5 | 8.7397
1340 | 47.0184 | 1343 | 37.9069 | 1345.5 | 59.8248 | 1348.5 | 879.4126 | 1351.5 | 6156.9199 | 1354 | 11574.0517 | 1357 | 25.4747 | 1359.5 | 929.0514 | 1362.5 | 887.3121 | 1365.5 | 2114.6473 | 1368 | 2313.3258 | 1371 | 749.6813 | 1373.5 | 22.5536 | 1376.5 | 12.707 | 1379.5 | 60.0351 | 1382 | 37.0291 | 1385 | 67.2737 | 1387.5 | 38.2819 | 1390.5 | 19.9909 | 1393.5 | 56.0818 | 1396 | 27.558 | 1340 | 12.707
1399 | 8.3466 | 1401.5 | 1494.7007 | 1404.5 | 36.2851 | 1407.5 | 36.0099 | 1410 | 40.1848 | 1413 | 45.816 | 1415.5 | 770.6311 | 1418.5 | 65.2481 | 1421.5 | 34.3718 | 1424 | 5.1749 | 1427 | 40.4295 | 1429.5 | 22.5654 | 1432.5 | 62.7834 | 1435.5 | 40.2398 | 1438 | 50.4858 | 1441 | 40.8912 | 1443.5 | 21.1986 | 1446.5 | 57.747 | 1449.5 | 33.7856 | 1452 | 37.8041 | 1455 | 27.4678 | 1399 | 5.1749
1457.5 | 23.5753 | 1460.5 | 12.1983 | 1463.5 | 87.2557 | 1466 | 46.0077 | 1469 | 66.3723 | 1471.5 | 90.7773 | 1474.5 | 20.1711 | 1477.5 | 10.237 | 1480 | 28.1231 | 1483 | 7.0253 | 1485.5 | 99.1569 | 1488.5 | 33.1044 | 1491.5 | 834.6305 | 1494 | 44.643 | 1497 | 742.0558 | 1499.5 | 306.985 | 1502.5 | 598.4475 | 1505.5 | 29.0247 | 1508 | 71.7838 | 1511 | 386.7147 | 1513.5 | 27.757 | 1457.5 | 7.0253
1516.5 | 759.1131 | 1519.5 | 75.1034 | 1522 | 190.735 | 1525 | 163.5161 | 1527.5 | 29.2134 | 1530.5 | 108.5163 | 1533.5 | 547.3372 | 1536 | 124.0319 | 1539 | 296.6071 | 1541.5 | 459.3064 | 1544.5 | 134.0786 | 1547.5 | 300.0674 | 1550 | 167.887 | 1553 | 811.5138 | 1555.5 | 936.6832 | 1558.5 | 743.1441 | 1561.5 | 103.3484 | 1564 | 603.141 | 1567 | 367.7557 | 1569.5 | 173.6108 | 1572.5 | 370.2039 | 1516.5 | 29.2134
1575.5 | 19.9385 | 1578 | 298.3733 | 1581 | 108.6281 | 1583.5 | 656.262 | 1586.5 | 58.5571 | 1589.5 | 23.696 | 1592 | 47.0818 | 1595 | 39.6586 | 1597.5 | 3.3038 | 1600.5 | 176.3364 | 1603.5 | 95.0399 | 1606 | 42.6768 | 1609 | 64.17 | 1611.5 | 77.0986 | 1614.5 | 75.7621 | 1617.5 | 25.2108 | 1620 | 47.0183 | 1623 | 14.8589 | 1625.5 | 0.37525 | 1628.5 | 4.2358 | 1631.5 | 11.267 | 1575.5 | 0.37525
1634 | 50.3793 | 1637 | 4.9489 | 1639.5 | 47.3574 | 1642.5 | 56.7243 | 1645.5 | 8.3704 | 1648 | 22.393 | 1652 | 57.2015 | 1653.5 | 33.7027 | 1656.5 | 12.241 | 1659.5 | 41.1451 | 1662 | 24.0423 | 1665 | 34.2903 | 1667.5 | 234.4042 | 1670.5 | 57.0832 | 1673.5 | 82.3976 | 1676 | 24.7998 | 1679 | 19.8228 | 1681.5 | 2.0645 | 1684.5 | 18.2865 | 1687.5 | 152.3066 | 1690 | 1317.3042 | 1634 | 2.0645
1693 | 633.7208 | 1695.5 | 36.7454 | 1698.5 | 881.4113 | 1701.5 | 594.1807 | 1704 | 154.2265 | 1707 | 1951.8465 | 1709.5 | 190.746 | 1712.5 | 3432.4203 | 1715.5 | 6.7894 | 1718 | 4660.0113 | 1721 | 1308.2264 | 1723.5 | 99.8834 | 1726.5 | 4575.6865 | 1729.5 | 232.8915 | 1732 | 155.343 | 1735 | 336.7263 | 1737.5 | 3000.3181 | 1740.5 | 10512.9444 | 1743.5 | 1863.83 | 1746 | 5778.5346 | 1749 | 497.997 | 1693 | 6.7894
1751.5 | 160.4434 | 1754.5 | 3571.114 | 1757.5 | 25.0686 | 1760 | 7406.94 | 1763 | 1117.1364 | 1765.5 | 2137.4985 | 1768.5 | 361.0434 | 1771.5 | 2037.4405 | 1774 | 10794.577 | 1777 | 2300.9947 | 1779.5 | 24.9383 | 1782.5 | 3816.1626 | 1785 | 176.78 | 1788 | 732.2308 | 1791 | 240.7836 | 1793.5 | 140.4079 | 1796.5 | 35.9082 | 1799.5 | 7013.5202 | 1802 | 2513.9178 | 1804.5 | 547.5221 | 1807.5 | 2210.3737 | 1751.5 | 24.9383
1810.5 | 69.2317 | 1813.5 | 2090.1846 | 1816 | 623.2679 | 1819 | 86.3478 | 1821.5 | 4455.9809 | 1824.5 | 166.12 | 1827.5 | 7169.7877 | 1830 | 104.8237 | 1833 | 3311.6159 | 1835.5 | 937.4719 | 1838.5 | 231.7715 | 1841.5 | 492.2588 | 1844 | 363.6388 | 1847 | 441.9972 | 1849.5 | 232.5402 | 1852.5 | 10682.4502 | 1855.5 | 2075.9953 | 1858 | 40.4571 | 1861 | 865.2486 | 1863.5 | 51.5765 | 1866.5 | 795.3952 | 1810.5 | 40.4571
1869.5 | 1039.5452 | 1872 | 1415.4617 | 1875 | 682.0479 | 1877.5 | 18.8631 | 1880.5 | 1369.7187 | 1883.5 | 274.878 | 1886 | 4872.3013 | 1889 | 658.9015 | 1891.5 | 1512.3362 | 1894.5 | 51.5181 | 1897.5 | 2004.1537 | 1900 | 55.3476 | 1903 | 23.7658 | 1905.5 | 721.0638 | 1908.5 | 16.97 | 1911.5 | 1232.0042 | 1914 | 104.9372 | 1917 | 1362.2283 | 1919.5 | 653.319 | 1922.5 | 74.9033 | 1925.5 | 26.1818 | 1869.5 | 16.97
1928 | 19.0384 | 1931 | 68.8466 | 1933.5 | 141.7436 | 1936.5 | 208.738 | 1939.5 | 114.4903 | 1942 | 91.0032 | 1945 | 610.3264 | 1947.5 | 35.0314 | 1950.5 | 698.3012 | 1953.5 | 114.658 | 1956 | 28.8493 | 1959 | 82.7951 | 1961.5 | 6.7773 | 1964.5 | 188.9792 | 1967.5 | 35.8558 | 1970 | 39.8686 | 1972.5 | 48.2515 | 1975.5 | 93.3113 | 1978.5 | 68.4598 | 1981.5 | 60.6984 | 1984 | 45.3115 | 1928 | 6.7773
1987 | 18.511 | 1989.5 | 7.5717 | 1992.5 | 43.3845 | 1995.5 | 298.2857 | 1998 | 85.2756 | 2000.5 | 88.0563 | 2003.5 | 218.2122 | 2006.5 | 58.0009 | 2009.5 | 88.9195 | 2012 | 23.2766 | 2015 | 70.1029 | 2017.5 | 81.2901 | 2020.5 | 66.311 | 2023.5 | 45.9669 | 2026 | 65.4805 | 2029 | 308.7004 | 2031.5 | 17.9118 | 2034.5 | 59.4948 | 2037.5 | 95.115 | 2040 | 69.5876 | 2043 | 76.749 | 1987 | 7.5717

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -72 | 31.2502 | 29.808 | 29.8499 | 29.7363 | 29.8863 | 27.8978 | 27.2851
0.691 | -71.309 | 31.2455 | 29.8029 | 29.8441 | 29.7275 | 29.8762 | 27.8912 | 27.277
1.6924 | -70.3076 | 31.2446 | 29.802 | 29.8404 | 29.7264 | 29.8862 | 27.8878 | 27.2794
2.6939 | -69.3061 | 31.2382 | 29.7967 | 29.8353 | 29.7213 | 29.8769 | 27.8905 | 27.2734
3.6953 | -68.3047 | 31.2441 | 29.7965 | 29.8386 | 29.7203 | 29.8726 | 27.8865 | 27.2715
4.6968 | -67.3032 | 31.2393 | 29.7949 | 29.8325 | 29.7185 | 29.8663 | 27.887 | 27.2673
5.6982 | -66.3018 | 31.2375 | 29.7931 | 29.8336 | 29.7223 | 29.869 | 27.8845 | 27.2693
6.6896 | -65.3104 | 31.243 | 29.7921 | 29.8277 | 29.7155 | 29.8693 | 27.8857 | 27.2641
7.6911 | -64.3089 | 31.2483 | 29.7893 | 29.8204 | 29.717 | 29.8632 | 27.8807 | 27.2627
8.6925 | -63.3075 | 31.2376 | 29.7861 | 29.8304 | 29.7107 | 29.8611 | 27.8836 | 27.2609
9.6939 | -62.3061 | 31.2488 | 29.7855 | 29.8255 | 29.7124 | 29.8642 | 27.8762 | 27.2652
10.6954 | -61.3046 | 31.2473 | 29.7851 | 29.8207 | 29.713 | 29.8655 | 27.8807 | 27.266
11.6968 | -60.3032 | 31.2439 | 29.785 | 29.8227 | 29.7148 | 29.8638 | 27.8748 | 27.2621
12.6983 | -59.3017 | 31.2421 | 29.7847 | 29.8208 | 29.7091 | 29.8654 | 27.8782 | 27.2618
13.6997 | -58.3003 | 31.2355 | 29.7858 | 29.8234 | 29.7063 | 29.868 | 27.8727 | 27.2633
14.6911 | -57.3089 | 31.2342 | 29.7811 | 29.8187 | 29.704 | 29.8704 | 27.8809 | 27.2702
15.6926 | -56.3074 | 31.2377 | 29.778 | 29.819 | 29.7037 | 29.8495 | 27.8729 | 27.2659
16.694 | -55.306 | 31.2224 | 29.7781 | 29.8066 | 29.6977 | 29.855 | 27.8749 | 27.2665
17.6954 | -54.3046 | 31.2203 | 29.7706 | 29.8061 | 29.7006 | 29.8588 | 27.8768 | 27.2658
18.6969 | -53.3031 | 31.2219 | 29.7744 | 29.8149 | 29.6992 | 29.857 | 27.8707 | 27.2626
19.6983 | -52.3017 | 31.2172 | 29.7704 | 29.8111 | 29.6944 | 29.8541 | 27.8669 | 27.2587
20.6998 | -51.3002 | 31.2201 | 29.7692 | 29.809 | 29.6969 | 29.8454 | 27.8712 | 27.2588
21.6912 | -50.3088 | 31.2177 | 29.7704 | 29.805 | 29.6966 | 29.8642 | 27.866 | 27.2651
22.6926 | -49.3074 | 31.2138 | 29.7671 | 29.8088 | 29.6924 | 29.8539 | 27.8667 | 27.2609
23.6941 | -48.3059 | 31.2189 | 29.7722 | 29.8061 | 29.6939 | 29.8521 | 27.8624 | 27.2611
24.6955 | -47.3045 | 31.2175 | 29.7608 | 29.8039 | 29.6901 | 29.849 | 27.8635 | 27.2577
25.697 | -46.303 | 31.2095 | 29.7644 | 29.7997 | 29.6901 | 29.8533 | 27.8588 | 27.2509
26.6984 | -45.3016 | 31.2054 | 29.7654 | 29.792 | 29.6864 | 29.8556 | 27.8584 | 27.2518
27.6898 | -44.3102 | 31.2077 | 29.7596 | 29.7921 | 29.6907 | 29.8395 | 27.861 | 27.2524
28.6913 | -43.3087 | 31.2031 | 29.7536 | 29.7992 | 29.6842 | 29.8462 | 27.8585 | 27.2523
29.6927 | -42.3073 | 31.1981 | 29.7564 | 29.7973 | 29.6814 | 29.8352 | 27.8553 | 27.2504
30.6941 | -41.3059 | 31.1921 | 29.751 | 29.7936 | 29.6847 | 29.8283 | 27.8567 | 27.2431
31.6956 | -40.3044 | 31.192 | 29.752 | 29.7934 | 29.6812 | 29.83 | 27.8593 | 27.2462
32.697 | -39.303 | 31.1873 | 29.748 | 29.78 | 29.6801 | 29.835 | 27.8572 | 27.2477
33.6985 | -38.3015 | 31.175 | 29.749 | 29.7951 | 29.6775 | 29.8247 | 27.8586 | 27.2411
34.6999 | -37.3001 | 31.1848 | 29.7547 | 29.7801 | 29.6837 | 29.833 | 27.8566 | 27.2439
35.6913 | -36.3087 | 31.188 | 29.7562 | 29.7915 | 29.6796 | 29.8373 | 27.8494 | 27.2424
36.6928 | -35.3072 | 31.1799 | 29.7437 | 29.787 | 29.6765 | 29.8316 | 27.8529 | 27.2376
37.6942 | -34.3058 | 31.1786 | 29.7457 | 29.7819 | 29.6698 | 29.8261 | 27.8504 | 27.2387
38.6956 | -33.3044 | 31.1755 | 29.7368 | 29.7737 | 29.6729 | 29.8264 | 27.8519 | 27.2366
39.6971 | -32.3029 | 31.1825 | 29.7394 | 29.7834 | 29.6743 | 29.8167 | 27.8404 | 27.2289
40.6985 | -31.3015 | 31.1833 | 29.7433 | 29.7758 | 29.6733 | 29.8167 | 27.8462 | 27.2297
41.6899 | -30.3101 | 31.1805 | 29.7366 | 29.7824 | 29.6642 | 29.8165 | 27.8396 | 27.2298
42.6914 | -29.3086 | 31.1765 | 29.7334 | 29.7715 | 29.6688 | 29.8204 | 27.837 | 27.2283
43.6928 | -28.3072 | 31.177 | 29.7327 | 29.776 | 29.6612 | 29.8124 | 27.8391 | 27.2186
44.6943 | -27.3057 | 31.1771 | 29.7322 | 29.7755 | 29.6634 | 29.8105 | 27.8341 | 27.2278
45.6957 | -26.3043 | 31.1753 | 29.7342 | 29.7655 | 29.6578 | 29.8097 | 27.8368 | 27.2124
46.6971 | -25.3029 | 31.1808 | 29.7297 | 29.7687 | 29.6573 | 29.799 | 27.8344 | 27.2189
47.6986 | -24.3014 | 31.1788 | 29.7346 | 29.7644 | 29.6638 | 29.8018 | 27.8223 | 27.2167
48.69 | -23.31 | 31.1742 | 29.7341 | 29.7597 | 29.6574 | 29.7959 | 27.8202 | 27.2169
49.6915 | -22.3085 | 31.1821 | 29.7259 | 29.7647 | 29.6573 | 29.7953 | 27.8207 | 27.2128
50.6929 | -21.3071 | 31.1785 | 29.7234 | 29.7674 | 29.6568 | 29.8 | 27.8156 | 27.2107
51.6943 | -20.3057 | 31.1779 | 29.727 | 29.766 | 29.6548 | 29.798 | 27.8168 | 27.21
52.6958 | -19.3042 | 31.1835 | 29.7199 | 29.7622 | 29.6534 | 29.797 | 27.8083 | 27.2202
53.6972 | -18.3028 | 31.181 | 29.7216 | 29.7677 | 29.6482 | 29.7853 | 27.8058 | 27.2145
54.6987 | -17.3013 | 31.1836 | 29.7239 | 29.7648 | 29.6499 | 29.7853 | 27.8076 | 27.2164
55.7001 | -16.2999 | 31.1949 | 29.7183 | 29.7599 | 29.653 | 29.7888 | 27.8044 | 27.2162
56.6915 | -15.3085 | 31.1812 | 29.7191 | 29.7487 | 29.6462 | 29.7819 | 27.803 | 27.2139
57.693 | -14.307 | 31.1802 | 29.7166 | 29.7467 | 29.6463 | 29.7853 | 27.8029 | 27.2169
58.6944 | -13.3056 | 31.1844 | 29.7165 | 29.7442 | 29.6452 | 29.787 | 27.7907 | 27.2137
59.6958 | -12.3042 | 31.1816 | 29.7125 | 29.7494 | 29.6354 | 29.7849 | 27.7919 | 27.2163
60.6973 | -11.3027 | 31.1781 | 29.7095 | 29.7443 | 29.6425 | 29.7894 | 27.7892 | 27.2128
61.6987 | -10.3013 | 31.1838 | 29.7148 | 29.7491 | 29.6381 | 29.7808 | 27.794 | 27.2103
62.6901 | -9.3099 | 31.1733 | 29.7089 | 29.7451 | 29.6417 | 29.774 | 27.7916 | 27.2098
63.6916 | -8.3084 | 31.1731 | 29.7065 | 29.7401 | 29.6392 | 29.78 | 27.7906 | 27.2074
64.693 | -7.307 | 31.1766 | 29.703 | 29.7477 | 29.6374 | 29.7857 | 27.785 | 27.2053
65.6945 | -6.3055 | 31.1755 | 29.7073 | 29.7445 | 29.6311 | 29.7764 | 27.7856 | 27.2
66.6959 | -5.3041 | 31.1679 | 29.7022 | 29.7462 | 29.6324 | 29.7749 | 27.7798 | 27.198
67.6973 | -4.3027 | 31.1737 | 29.7087 | 29.7447 | 29.6323 | 29.7762 | 27.782 | 27.1948
68.6988 | -3.3012 | 31.1692 | 29.6942 | 29.7474 | 29.631 | 29.7902 | 27.7826 | 27.193
69.6902 | -2.3098 | 31.1788 | 29.5113 | 29.7192 | 29.548 | 30.0178 | 27.8281 | 27.1879
70.6916 | -1.3084 | 31.1709 | 29.5391 | 29.7327 | 29.5593 | 29.9995 | 27.8063 | 27.1858
71.6931 | -0.3069 | 31.21 | 29.6151 | 29.7351 | 29.5926 | 29.9046 | 27.7851 | 27.1885
72.6945 | 0.6945 | 31.5424 | 29.6414 | 29.7355 | 29.6059 | 29.8676 | 27.7782 | 27.1882
73.696 | 1.696 | 32.406 | 29.6628 | 29.742 | 29.6136 | 29.8445 | 27.7784 | 27.1914
74.6974 | 2.6974 | 33.8405 | 29.6736 | 29.7295 | 29.6164 | 29.8259 | 27.7735 | 27.1876
75.6988 | 3.6988 | 35.7862 | 29.6739 | 29.7235 | 29.6172 | 29.8152 | 27.7742 | 27.19
76.7003 | 4.7003 | 38.1753 | 29.6739 | 29.727 | 29.612 | 29.8187 | 27.7693 | 27.1934
77.6917 | 5.6917 | 40.9642 | 29.6739 | 29.7306 | 29.6184 | 29.8192 | 27.7667 | 27.1997
78.6932 | 6.6932 | 44.0656 | 29.6794 | 29.721 | 29.6143 | 29.8216 | 27.776 | 27.2121
79.6946 | 7.6946 | 47.4645 | 29.6809 | 29.7211 | 29.6099 | 29.8427 | 27.7759 | 27.2313
80.696 | 8.696 | 51.1125 | 29.683 | 29.7162 | 29.6111 | 29.8558 | 27.7872 | 27.2521
81.6975 | 9.6975 | 54.9875 | 29.6908 | 29.7183 | 29.6127 | 29.8822 | 27.7893 | 27.2747
82.6989 | 10.6989 | 59.0818 | 29.6929 | 29.7187 | 29.6082 | 29.905 | 27.8032 | 27.3124
83.6903 | 11.6903 | 63.3022 | 29.7038 | 29.7224 | 29.6105 | 29.9557 | 27.8146 | 27.3542
84.6918 | 12.6918 | 67.7066 | 29.7162 | 29.7199 | 29.6082 | 29.9995 | 27.8338 | 27.3982
85.6932 | 13.6932 | 72.2823 | 29.7321 | 29.7246 | 29.6183 | 30.0451 | 27.8599 | 27.4561
86.6947 | 14.6947 | 76.9206 | 29.7404 | 29.7305 | 29.6151 | 30.0971 | 27.8899 | 27.518
87.6961 | 15.6961 | 81.6738 | 29.7515 | 29.7221 | 29.6193 | 30.1653 | 27.9257 | 27.5837
88.6975 | 16.6975 | 86.5022 | 29.7813 | 29.7366 | 29.6245 | 30.2374 | 27.9655 | 27.6709
89.689 | 17.689 | 91.532 | 29.8046 | 29.7519 | 29.6379 | 30.3319 | 28.0096 | 27.7545
90.6904 | 18.6904 | 96.6136 | 29.8357 | 29.7541 | 29.6473 | 30.433 | 28.061 | 27.8602
91.6918 | 19.6918 | 101.8283 | 29.8682 | 29.7674 | 29.6703 | 30.5337 | 28.1266 | 27.9628
92.6933 | 20.6933 | 107.1444 | 29.9075 | 29.7775 | 29.6693 | 30.6376 | 28.1873 | 28.0768
93.6947 | 21.6947 | 112.5099 | 29.9499 | 29.7907 | 29.6946 | 30.7671 | 28.2658 | 28.1984
94.6962 | 22.6962 | 117.9293 | 29.9996 | 29.8134 | 29.7123 | 30.8993 | 28.3467 | 28.3481
95.6976 | 23.6976 | 123.3342 | 30.0467 | 29.8274 | 29.7369 | 31.0497 | 28.4302 | 28.4876
96.699 | 24.699 | 128.7291 | 30.104 | 29.8506 | 29.7603 | 31.2077 | 28.5389 | 28.6499
97.6905 | 25.6905 | 134.145 | 30.1672 | 29.8776 | 29.792 | 31.3809 | 28.6459 | 28.8377
98.6919 | 26.6919 | 139.6728 | 30.2422 | 29.8939 | 29.8269 | 31.5552 | 28.7713 | 29.0254
99.6934 | 27.6934 | 145.2201 | 30.3129 | 29.943 | 29.8645 | 31.7523 | 28.8955 | 29.2277
100.6948 | 28.6948 | 150.8109 | 30.4035 | 29.9793 | 29.9076 | 31.9543 | 29.0305 | 29.4502
101.6962 | 29.6962 | 156.4066 | 30.4919 | 30.0181 | 29.9542 | 32.177 | 29.1648 | 29.6814
102.6977 | 30.6977 | 161.9453 | 30.5888 | 30.0575 | 30.0015 | 32.4218 | 29.3268 | 29.9261
103.6991 | 31.6991 | 167.5609 | 30.6956 | 30.1 | 30.0563 | 32.6692 | 29.4884 | 30.1821
104.6905 | 32.6905 | 173.1419 | 30.8104 | 30.1629 | 30.1225 | 32.9424 | 29.6687 | 30.4556
105.692 | 33.692 | 178.7104 | 30.9346 | 30.2167 | 30.1843 | 33.2228 | 29.8558 | 30.7533
106.6934 | 34.6934 | 184.2895 | 31.0678 | 30.2768 | 30.2555 | 33.5375 | 30.0517 | 31.053
107.6949 | 35.6949 | 189.7911 | 31.2093 | 30.3426 | 30.3309 | 33.86 | 30.265 | 31.3656
108.6963 | 36.6963 | 195.4237 | 31.3478 | 30.4121 | 30.4197 | 34.1924 | 30.4879 | 31.6981
109.6977 | 37.6977 | 201.0711 | 31.5116 | 30.4968 | 30.5042 | 34.539 | 30.7182 | 32.0373
110.6892 | 38.6892 | 206.6333 | 31.677 | 30.5739 | 30.6043 | 34.9034 | 30.9618 | 32.3953
111.6906 | 39.6906 | 212.2041 | 31.8536 | 30.6635 | 30.6965 | 35.2858 | 31.2118 | 32.7735
112.692 | 40.692 | 217.804 | 32.0347 | 30.7605 | 30.8036 | 35.676 | 31.4853 | 33.1653
113.6935 | 41.6935 | 223.2358 | 32.2323 | 30.8503 | 30.9269 | 36.0975 | 31.768 | 33.5755
114.6949 | 42.6949 | 228.6495 | 32.4379 | 30.9601 | 31.0438 | 36.5139 | 32.073 | 34.0034
115.6964 | 43.6964 | 234.1012 | 32.6564 | 31.0662 | 31.1866 | 36.9554 | 32.3817 | 34.4467
116.6978 | 44.6978 | 239.6178 | 32.8848 | 31.1931 | 31.3137 | 37.4194 | 32.6953 | 34.9046
117.6892 | 45.6892 | 245.0697 | 33.1209 | 31.3198 | 31.4666 | 37.9067 | 33.0417 | 35.3825
118.6907 | 46.6907 | 250.4858 | 33.382 | 31.4449 | 31.6183 | 38.4011 | 33.3785 | 35.8757
119.6921 | 47.6921 | 255.9247 | 33.6436 | 31.5937 | 31.7863 | 38.9269 | 33.7576 | 36.3976
120.6935 | 48.6935 | 261.413 | 33.9191 | 31.7465 | 31.9609 | 39.4631 | 34.1342 | 36.9278
121.695 | 49.695 | 266.8242 | 34.2107 | 31.8949 | 32.1355 | 40.0202 | 34.5326 | 37.4809
122.6964 | 50.6964 | 272.2175 | 34.5124 | 32.0633 | 32.3206 | 40.5807 | 34.9419 | 38.0674
123.6979 | 51.6979 | 277.7162 | 34.8272 | 32.2363 | 32.5201 | 41.1585 | 35.3771 | 38.6601
124.6993 | 52.6993 | 283.0479 | 35.1541 | 32.4174 | 32.7328 | 41.7687 | 35.8245 | 39.2761
125.6907 | 53.6907 | 288.4094 | 35.495 | 32.6083 | 32.9511 | 42.3846 | 36.2719 | 39.9148
126.6922 | 54.6922 | 293.7668 | 35.8492 | 32.8026 | 33.1744 | 43.0139 | 36.7347 | 40.5639
127.6936 | 55.6936 | 299.1543 | 36.2154 | 33.012 | 33.4228 | 43.677 | 37.2196 | 41.2301
128.6951 | 56.6951 | 304.5229 | 36.5963 | 33.2225 | 33.6609 | 44.3602 | 37.7194 | 41.9101
129.6965 | 57.6965 | 309.7603 | 36.9908 | 33.4589 | 33.9177 | 45.0523 | 38.2337 | 42.629
130.6979 | 58.6979 | 314.8646 | 37.4059 | 33.6911 | 34.1933 | 45.7712 | 38.7858 | 43.353
131.6894 | 59.6894 | 320.0446 | 37.8234 | 33.9384 | 34.4712 | 46.5206 | 39.3229 | 44.0914
132.7008 | 60.7008 | 325.3176 | 38.283 | 34.1854 | 34.7586 | 47.3011 | 39.8953 | 44.8521
133.6922 | 61.6922 | 330.4924 | 38.7431 | 34.4547 | 35.0551 | 48.1056 | 40.4762 | 45.6356
134.6937 | 62.6937 | 335.6883 | 39.2132 | 34.7356 | 35.3653 | 48.9319 | 41.0767 | 46.4476
135.6951 | 63.6951 | 340.7835 | 39.7079 | 35.0232 | 35.6853 | 49.778 | 41.6914 | 47.2804
136.6966 | 64.6966 | 345.8647 | 40.2227 | 35.3147 | 36.0173 | 50.6344 | 42.3272 | 48.1488
137.698 | 65.698 | 351.0792 | 40.7557 | 35.6248 | 36.3667 | 51.5145 | 42.9739 | 49.03
138.6894 | 66.6894 | 356.1076 | 41.3016 | 35.9546 | 36.7171 | 52.4102 | 43.6453 | 49.9321
139.7009 | 67.7009 | 361.1449 | 41.8638 | 36.2757 | 37.0844 | 53.3337 | 44.3247 | 50.8556
140.6923 | 68.6923 | 366.1478 | 42.4503 | 36.626 | 37.4641 | 54.2703 | 45.0159 | 51.7814
141.6937 | 69.6937 | 371.1553 | 43.0406 | 36.9832 | 37.8568 | 55.2476 | 45.7483 | 52.7547
142.6952 | 70.6952 | 375.995 | 43.651 | 37.348 | 38.2685 | 56.2419 | 46.4858 | 53.7215
143.6966 | 71.6966 | 380.9096 | 44.266 | 37.75 | 38.6843 | 57.2786 | 47.2499 | 54.7131
144.6981 | 72.6981 | 385.8306 | 44.899 | 38.1199 | 39.1178 | 58.348 | 48.0308 | 55.7257
145.6995 | 73.6995 | 390.6028 | 45.5423 | 38.5249 | 39.5539 | 59.4638 | 48.8325 | 56.756
146.6909 | 74.6909 | 395.3203 | 46.2058 | 38.9618 | 40.0054 | 60.581 | 49.6471 | 57.8314
147.6924 | 75.6924 | 399.9196 | 46.8849 | 39.3769 | 40.4725 | 61.7339 | 50.4827 | 58.9361
148.6938 | 76.6938 | 404.5038 | 47.5911 | 39.8218 | 40.9498 | 62.923 | 51.3221 | 60.0851
149.6953 | 77.6953 | 409.2894 | 48.3043 | 40.2706 | 41.447 | 64.1378 | 52.2009 | 61.2747
150.6967 | 78.6967 | 414.0286 | 49.0484 | 40.7265 | 41.9545 | 65.3691 | 53.0857 | 62.5054
151.6981 | 79.6981 | 418.623 | 49.8087 | 41.2103 | 42.4792 | 66.6132 | 53.982 | 63.7452
152.6896 | 80.6896 | 423.252 | 50.5975 | 41.6789 | 43.015 | 67.9132 | 54.9009 | 65.0153
153.691 | 81.691 | 427.7083 | 51.3381 | 42.1865 | 43.5353 | 69.3128 | 55.8704 | 66.3005
154.6924 | 82.6924 | 432.1324 | 52.0831 | 42.6687 | 44.0504 | 70.7765 | 56.8682 | 67.6123
155.6939 | 83.6939 | 436.5163 | 52.9268 | 43.2069 | 44.621 | 72.1772 | 57.8824 | 68.9508
156.6953 | 84.6953 | 440.4975 | 53.8169 | 43.7425 | 45.2095 | 73.5559 | 58.907 | 70.3138
157.6968 | 85.6968 | 444.0356 | 54.7518 | 44.2815 | 45.8302 | 74.9088 | 59.9723 | 71.6951
158.6982 | 86.6982 | 447.4458 | 55.6949 | 44.857 | 46.4458 | 76.3188 | 61.0628 | 73.0919
159.6896 | 87.6896 | 450.6115 | 56.6363 | 45.4357 | 47.0843 | 77.7765 | 62.1738 | 74.517
160.7011 | 88.7011 | 453.6108 | 57.6215 | 46.0256 | 47.7471 | 79.1841 | 63.2995 | 75.9405
161.6925 | 89.6925 | 456.3418 | 58.5999 | 46.6359 | 48.4201 | 80.6556 | 64.444 | 77.3804
162.6939 | 90.6939 | 459.0427 | 59.59 | 47.2635 | 49.0887 | 82.1438 | 65.6095 | 78.8155
163.6954 | 91.6954 | 461.7636 | 60.558 | 47.9134 | 49.7732 | 83.6466 | 66.7823 | 80.2691
164.6968 | 92.6968 | 464.1602 | 61.552 | 48.5443 | 50.4592 | 85.1254 | 67.9867 | 81.727
165.6983 | 93.6983 | 466.4432 | 62.6522 | 49.1979 | 51.1926 | 86.5494 | 69.1811 | 83.196
166.6997 | 94.6997 | 468.6577 | 63.6723 | 49.8758 | 51.9192 | 88.047 | 70.4123 | 84.6544
167.6911 | 95.6911 | 470.7233 | 64.7727 | 50.5616 | 52.6946 | 89.4975 | 71.6176 | 86.1315
168.6926 | 96.6926 | 472.46 | 65.8292 | 51.2588 | 53.452 | 90.9882 | 72.8746 | 87.6037
169.694 | 97.694 | 473.8187 | 66.886 | 51.9694 | 54.2196 | 92.4745 | 74.1319 | 89.0855
170.6954 | 98.6954 | 475.1339 | 67.9519 | 52.6966 | 54.9995 | 93.9425 | 75.3824 | 90.5613
171.6969 | 99.6969 | 476.3997 | 69.0214 | 53.4232 | 55.7924 | 95.4363 | 76.6441 | 92.035
172.6983 | 100.6983 | 477.4981 | 70.1049 | 54.1698 | 56.5892 | 96.8909 | 77.9097 | 93.5002
173.6898 | 101.6898 | 478.1553 | 71.1985 | 54.9188 | 57.4083 | 98.3352 | 79.1587 | 94.9649
174.6912 | 102.6912 | 478.597 | 72.302 | 55.6779 | 58.2237 | 99.7803 | 80.4137 | 96.4146
175.6926 | 103.6926 | 478.8303 | 73.4091 | 56.4508 | 59.0548 | 101.1934 | 81.6769 | 97.8594
176.6941 | 104.6941 | 478.9963 | 74.5299 | 57.2266 | 59.8885 | 102.6063 | 82.926 | 99.2831
177.6955 | 105.6955 | 479.2911 | 75.704 | 58.0168 | 60.7362 | 103.9982 | 84.1734 | 100.7098
178.697 | 106.697 | 479.2799 | 76.8861 | 58.7974 | 61.5795 | 105.3705 | 85.4108 | 102.1086
179.6984 | 107.6984 | 479.2582 | 78.052 | 59.6056 | 62.4328 | 106.7403 | 86.6541 | 103.4843
180.6898 | 108.6898 | 479.0636 | 79.2263 | 60.3959 | 63.2886 | 108.0901 | 87.8852 | 104.8545
181.7013 | 109.7013 | 478.7459 | 80.3825 | 61.2069 | 64.1493 | 109.4284 | 89.1057 | 106.2067
182.6927 | 110.6927 | 478.4037 | 81.5499 | 62.0344 | 65.0214 | 110.7349 | 90.3193 | 107.5346
183.6941 | 111.6941 | 477.9362 | 82.7013 | 62.8467 | 65.8835 | 112.0462 | 91.515 | 108.8466
184.6956 | 112.6956 | 477.5219 | 83.8478 | 63.6568 | 66.7544 | 113.326 | 92.7173 | 110.1512
185.697 | 113.697 | 477.1529 | 84.996 | 64.486 | 67.63 | 114.5893 | 93.908 | 111.4342
186.6985 | 114.6985 | 476.7005 | 86.1526 | 65.3214 | 68.5014 | 115.8386 | 95.0887 | 112.7156
187.6899 | 115.6899 | 476.4501 | 87.304 | 66.1495 | 69.3691 | 117.0646 | 96.2571 | 113.9743
188.6913 | 116.6913 | 476.0866 | 88.4464 | 66.9821 | 70.236 | 118.2652 | 97.4096 | 115.2179
189.6928 | 117.6928 | 475.8654 | 89.5987 | 67.8159 | 71.104 | 119.4485 | 98.5525 | 116.4411
190.6942 | 118.6942 | 475.5728 | 90.7405 | 68.645 | 71.9774 | 120.6142 | 99.6925 | 117.6582
191.6956 | 119.6956 | 475.334 | 91.8685 | 69.4787 | 72.836 | 121.7708 | 100.8197 | 118.8707
192.6971 | 120.6971 | 474.897 | 92.9929 | 70.3131 | 73.7001 | 122.9165 | 101.9366 | 120.0491
193.6985 | 121.6985 | 474.6855 | 94.1097 | 71.1328 | 74.5619 | 124.0345 | 103.0554 | 121.2223
194.69 | 122.69 | 474.3308 | 95.2215 | 71.969 | 75.427 | 125.134 | 104.1598 | 122.3827
195.6914 | 123.6914 | 474.1262 | 96.3086 | 72.8035 | 76.2942 | 126.2213 | 105.268 | 123.5291
196.7028 | 124.7028 | 473.9261 | 97.378 | 73.6327 | 77.1403 | 127.2938 | 106.3601 | 124.6664
197.6943 | 125.6943 | 473.6921 | 98.4424 | 74.4513 | 77.9938 | 128.3541 | 107.4393 | 125.7893
198.6957 | 126.6957 | 473.3647 | 99.4929 | 75.2764 | 78.8442 | 129.4017 | 108.512 | 126.9007
199.6972 | 127.6972 | 473.1636 | 100.5301 | 76.1176 | 79.6803 | 130.416 | 109.5859 | 128.0015
200.6986 | 128.6986 | 472.9802 | 101.542 | 76.9426 | 80.5289 | 131.422 | 110.6445 | 129.0932
201.69 | 129.69 | 473.0063 | 102.5455 | 77.7592 | 81.3492 | 132.4245 | 111.6901 | 130.1758
202.6915 | 130.6915 | 473.0036 | 103.5325 | 78.5886 | 82.1852 | 133.3999 | 112.7323 | 131.2428
203.6929 | 131.6929 | 472.9688 | 104.5188 | 79.3976 | 83.0097 | 134.3609 | 113.7768 | 132.2979
204.6943 | 132.6943 | 472.9467 | 105.473 | 80.2103 | 83.8346 | 135.315 | 114.8023 | 133.3534
205.6958 | 133.6958 | 472.7733 | 106.4252 | 81.0218 | 84.6396 | 136.2497 | 115.8239 | 134.4055
206.6972 | 134.6972 | 472.8594 | 107.364 | 81.8317 | 85.4637 | 137.1711 | 116.8383 | 135.4383
207.6987 | 135.6987 | 472.9784 | 108.2882 | 82.6302 | 86.2611 | 138.0661 | 117.8431 | 136.487
208.7001 | 136.7001 | 472.8919 | 109.2234 | 83.4271 | 87.0677 | 138.9528 | 118.8368 | 137.513
209.6915 | 137.6915 | 472.8456 | 110.1404 | 84.22 | 87.8623 | 139.8292 | 119.8276 | 138.5194
210.693 | 138.693 | 472.9363 | 111.0397 | 85.0016 | 88.6427 | 140.6929 | 120.8132 | 139.5238
211.6944 | 139.6944 | 473.0598 | 111.9386 | 85.7899 | 89.431 | 141.5462 | 121.7921 | 140.525
212.6958 | 140.6958 | 472.9982 | 112.8228 | 86.5712 | 90.2152 | 142.3909 | 122.7726 | 141.5171
213.6973 | 141.6973 | 473.0086 | 113.7118 | 87.3447 | 90.9873 | 143.2509 | 123.7536 | 142.5056
214.6987 | 142.6987 | 473.1609 | 114.5695 | 88.1142 | 91.7567 | 144.0708 | 124.719 | 143.513
215.6901 | 143.6901 | 473.2419 | 115.4062 | 88.8628 | 92.5184 | 144.9143 | 125.6772 | 144.4951
216.6916 | 144.6916 | 473.2902 | 116.2412 | 89.6262 | 93.2887 | 145.7376 | 126.6264 | 145.4722
217.693 | 145.693 | 473.6953 | 117.0608 | 90.3762 | 94.0353 | 146.5671 | 127.5783 | 146.4524
218.6945 | 146.6945 | 474.0616 | 117.8603 | 91.1279 | 94.8007 | 147.4 | 128.5316 | 147.4396
219.6959 | 147.6959 | 474.1452 | 118.6445 | 91.8675 | 95.5585 | 148.2273 | 129.4617 | 148.4275
220.6973 | 148.6973 | 474.3429 | 119.4063 | 92.6134 | 96.3028 | 149.0341 | 130.3866 | 149.4331
221.6988 | 149.6988 | 474.4522 | 120.1604 | 93.3491 | 97.055 | 149.8652 | 131.3129 | 150.4047
222.6902 | 150.6902 | 474.652 | 120.9058 | 94.0674 | 97.801 | 150.6929 | 132.2255 | 151.3825
223.6917 | 151.6917 | 474.738 | 121.6287 | 94.7955 | 98.5524 | 151.5348 | 133.1493 | 152.3592
224.6931 | 152.6931 | 474.7795 | 122.3396 | 95.5227 | 99.3017 | 152.3689 | 134.0531 | 153.3186
225.7546 | 153.7546 | 474.9824 | 123.0932 | 96.2911 | 100.0968 | 153.2904 | 135.0218 | 154.3483
226.696 | 154.696 | 475.1939 | 123.7581 | 96.978 | 100.8026 | 154.0961 | 135.8632 | 155.2399
227.6974 | 155.6974 | 475.2839 | 124.4532 | 97.6934 | 101.5408 | 154.9715 | 136.7587 | 156.2104
228.6989 | 156.6989 | 475.1687 | 125.1429 | 98.4072 | 102.2942 | 155.8465 | 137.6508 | 157.1729
229.7003 | 157.7003 | 475.0896 | 125.8345 | 99.1321 | 103.0444 | 156.7352 | 138.5414 | 158.1281
230.6917 | 158.6917 | 475.1341 | 126.5209 | 99.8599 | 103.7937 | 157.6165 | 139.4265 | 159.0685
231.6932 | 159.6932 | 475.1764 | 127.2216 | 100.5885 | 104.5585 | 158.5142 | 140.3142 | 160.011
232.6946 | 160.6946 | 475.0789 | 127.9229 | 101.3187 | 105.3117 | 159.4165 | 141.1916 | 160.944
233.696 | 161.696 | 475.0802 | 128.6331 | 102.0502 | 106.0629 | 160.3177 | 142.0615 | 161.8755
234.6975 | 162.6975 | 475.0996 | 129.3468 | 102.7731 | 106.8105 | 161.222 | 142.9494 | 162.8154
235.6989 | 163.6989 | 475.2168 | 130.0706 | 103.5137 | 107.5619 | 162.1292 | 143.8104 | 163.7561
236.6903 | 164.6903 | 475.1388 | 130.8054 | 104.2669 | 108.2984 | 163.0397 | 144.6819 | 164.6895
237.6918 | 165.6918 | 475.082 | 131.559 | 105.0357 | 109.0379 | 163.9463 | 145.5582 | 165.6283
238.6932 | 166.6932 | 475.0041 | 132.3133 | 105.7688 | 109.7482 | 164.8439 | 146.4078 | 166.573
239.6947 | 167.6947 | 474.9063 | 133.0896 | 106.5163 | 110.4676 | 165.7402 | 147.2684 | 167.5067
240.6961 | 168.6961 | 474.9197 | 133.8688 | 107.2663 | 111.1616 | 166.6244 | 148.128 | 168.44
241.6975 | 169.6975 | 474.9633 | 134.6492 | 107.9992 | 111.8574 | 167.5061 | 148.9805 | 169.373
242.699 | 170.699 | 475.1049 | 135.4469 | 108.7236 | 112.5482 | 168.3847 | 149.8262 | 170.2995
243.6904 | 171.6904 | 475.3301 | 136.2419 | 109.4489 | 113.2537 | 169.2581 | 150.6637 | 171.2227
244.6918 | 172.6918 | 475.4508 | 137.0263 | 110.1476 | 113.9663 | 170.1363 | 151.5006 | 172.1871
245.6933 | 173.6933 | 475.4747 | 137.8212 | 110.8221 | 114.699 | 171.0077 | 152.3576 | 173.1595
246.6947 | 174.6947 | 475.5907 | 138.6228 | 111.5004 | 115.4276 | 171.876 | 153.1987 | 174.1076
247.6962 | 175.6962 | 475.799 | 139.4275 | 112.1703 | 116.167 | 172.7595 | 154.0223 | 175.0318
248.6976 | 176.6976 | 475.7691 | 140.2244 | 112.8329 | 116.9068 | 173.627 | 154.846 | 175.9454
249.699 | 177.699 | 475.77 | 141.0337 | 113.5109 | 117.6465 | 174.4748 | 155.6593 | 176.8513
250.7005 | 178.7005 | 475.8819 | 141.846 | 114.206 | 118.3985 | 175.3455 | 156.4824 | 177.7388
251.6919 | 179.6919 | 476.0888 | 142.6712 | 114.9027 | 119.1559 | 176.192 | 157.2913 | 178.6316
252.6934 | 180.6934 | 476.2076 | 143.4818 | 115.6004 | 119.9087 | 177.0255 | 158.0967 | 179.5148
253.6948 | 181.6948 | 476.2559 | 144.3012 | 116.3151 | 120.6847 | 177.8786 | 158.8969 | 180.3739
254.6962 | 182.6962 | 476.2682 | 145.1111 | 117.0219 | 121.4683 | 178.723 | 159.6837 | 181.2257
255.6977 | 183.6977 | 476.3147 | 145.9383 | 117.7392 | 122.2774 | 179.5731 | 160.4827 | 182.0947
256.6991 | 184.6991 | 476.5381 | 146.7523 | 118.4599 | 123.0929 | 180.4105 | 161.2661 | 182.9298
257.6905 | 185.6905 | 476.7334 | 147.5884 | 119.1845 | 123.9324 | 181.2437 | 162.0655 | 183.7609
258.692 | 186.692 | 476.8978 | 148.4132 | 119.9203 | 124.7723 | 182.0884 | 162.8533 | 184.5806
259.6934 | 187.6934 | 476.8363 | 149.2346 | 120.672 | 125.6164 | 182.9159 | 163.6324 | 185.4115
260.6949 | 188.6949 | 476.7969 | 150.0742 | 121.4535 | 126.4624 | 183.7372 | 164.4261 | 186.2225
261.6963 | 189.6963 | 476.6649 | 150.9144 | 122.2442 | 127.3107 | 184.5647 | 165.21 | 187.0338
262.6977 | 190.6977 | 476.6491 | 151.7501 | 123.0396 | 128.1558 | 185.3781 | 165.987 | 187.8244
263.6892 | 191.6892 | 476.7855 | 152.6116 | 123.8951 | 128.9936 | 186.1853 | 166.7767 | 188.6064
264.6906 | 192.6906 | 476.807 | 153.4463 | 124.7331 | 129.8266 | 187.0172 | 167.5584 | 189.3928
265.692 | 193.692 | 476.848 | 154.3034 | 125.5973 | 130.6621 | 187.8338 | 168.3241 | 190.1644
266.6935 | 194.6935 | 476.8611 | 155.1579 | 126.4558 | 131.4832 | 188.6433 | 169.0944 | 190.9398
267.6949 | 195.6949 | 476.9467 | 156.0135 | 127.3355 | 132.3198 | 189.4619 | 169.8551 | 191.7162
268.6964 | 196.6964 | 476.8569 | 156.8647 | 128.2127 | 133.1548 | 190.2743 | 170.6142 | 192.4662
269.6978 | 197.6978 | 476.8029 | 157.7258 | 129.1053 | 133.9788 | 191.0875 | 171.379 | 193.2092
270.6892 | 198.6892 | 476.8473 | 158.5956 | 129.9796 | 134.8101 | 191.9007 | 172.1524 | 193.9566
271.7007 | 199.7007 | 476.8329 | 159.462 | 130.8586 | 135.6472 | 192.7132 | 172.8927 | 194.6867
272.6921 | 200.6921 | 476.8478 | 160.3302 | 131.741 | 136.4695 | 193.5229 | 173.6385 | 195.4089
273.6936 | 201.6936 | 476.7434 | 161.2051 | 132.6179 | 137.3093 | 194.3285 | 174.3882 | 196.1269
274.695 | 202.695 | 476.5598 | 162.0995 | 133.4927 | 138.1408 | 195.1418 | 175.1238 | 196.8329
275.6964 | 203.6964 | 476.4095 | 162.9836 | 134.3617 | 138.9804 | 195.9499 | 175.8586 | 197.5264
276.6979 | 204.6979 | 476.375 | 163.8644 | 135.2254 | 139.8228 | 196.7606 | 176.5966 | 198.2218
277.6993 | 205.6993 | 476.2619 | 164.7608 | 136.1086 | 140.6686 | 197.586 | 177.3271 | 198.8995
278.6907 | 206.6907 | 476.0664 | 165.6514 | 136.9831 | 141.5282 | 198.3865 | 178.0668 | 199.557
279.6922 | 207.6922 | 475.9733 | 166.5578 | 137.8721 | 142.3877 | 199.1942 | 178.8068 | 200.2274
280.6936 | 208.6936 | 475.8408 | 167.4648 | 138.7687 | 143.2456 | 200.0014 | 179.5395 | 200.8872
281.6951 | 209.6951 | 475.8927 | 168.3713 | 139.6585 | 144.1099 | 200.7996 | 180.2819 | 201.5402
282.6965 | 210.6965 | 475.7667 | 169.2743 | 140.5565 | 144.9715 | 201.6225 | 181.0191 | 202.1891
283.6979 | 211.6979 | 475.6318 | 170.1843 | 141.448 | 145.8304 | 202.4202 | 181.7616 | 202.8402
284.6994 | 212.6994 | 475.5297 | 171.0887 | 142.351 | 146.6913 | 203.2248 | 182.502 | 203.472
285.6908 | 213.6908 | 475.5029 | 171.997 | 143.2454 | 147.5562 | 204.0315 | 183.2461 | 204.1053
286.6922 | 214.6922 | 475.4943 | 172.9086 | 144.1391 | 148.404 | 204.84 | 183.989 | 204.7385
287.6937 | 215.6937 | 475.5966 | 173.811 | 145.0298 | 149.2694 | 205.6338 | 184.7236 | 205.3685
288.6951 | 216.6951 | 475.9629 | 174.7109 | 145.9135 | 150.1228 | 206.4729 | 185.4703 | 205.9979
289.6966 | 217.6966 | 476.1661 | 175.6134 | 146.8125 | 150.9862 | 207.3259 | 186.2377 | 206.6236
290.698 | 218.698 | 476.2094 | 176.5126 | 147.7113 | 151.8453 | 208.1688 | 187.0157 | 207.2553
291.6894 | 219.6894 | 476.2375 | 177.4095 | 148.6142 | 152.7073 | 209.0045 | 187.7728 | 207.8628
292.7009 | 220.7009 | 476.2554 | 178.3059 | 149.5035 | 153.5579 | 209.8522 | 188.5405 | 208.4895
293.6923 | 221.6923 | 476.4292 | 179.2022 | 150.4061 | 154.4173 | 210.7144 | 189.2991 | 209.1064
294.6937 | 222.6937 | 476.5699 | 180.101 | 151.2999 | 155.2559 | 211.569 | 190.0635 | 209.7118
295.6952 | 223.6952 | 476.5841 | 180.9927 | 152.1883 | 156.1129 | 212.4088 | 190.8261 | 210.327
296.6966 | 224.6966 | 476.5228 | 181.8833 | 153.1048 | 156.9719 | 213.2613 | 191.5969 | 210.9413
297.6981 | 225.6981 | 476.5082 | 182.7793 | 154.0066 | 157.8261 | 214.11 | 192.3513 | 211.5595
298.6995 | 226.6995 | 476.263 | 183.662 | 154.9108 | 158.6859 | 214.9848 | 193.1154 | 212.1602
299.6909 | 227.6909 | 476.2328 | 184.5443 | 155.8213 | 159.5448 | 215.8627 | 193.8597 | 212.768
300.6924 | 228.6924 | 476.3478 | 185.4273 | 156.7295 | 160.4032 | 216.7416 | 194.6213 | 213.3674
301.6938 | 229.6938 | 476.3251 | 186.3221 | 157.6604 | 161.2667 | 217.6125 | 195.3603 | 213.9759
302.6953 | 230.6953 | 476.4974 | 187.2042 | 158.5725 | 162.1314 | 218.4753 | 196.1057 | 214.5739
303.6967 | 231.6967 | 476.6675 | 188.0872 | 159.4979 | 162.9912 | 219.3637 | 196.8416 | 215.1804
304.6981 | 232.6981 | 476.657 | 188.9669 | 160.4149 | 163.8419 | 220.2175 | 197.5715 | 215.7789
305.6896 | 233.6896 | 476.6734 | 189.8463 | 161.3311 | 164.689 | 221.0969 | 198.2989 | 216.3712
306.691 | 234.691 | 476.5312 | 190.7322 | 162.2506 | 165.5248 | 221.9727 | 199.0243 | 216.9662
307.6924 | 235.6924 | 476.5317 | 191.6158 | 163.1747 | 166.3751 | 222.845 | 199.7561 | 217.5695
308.6939 | 236.6939 | 476.395 | 192.4889 | 164.0983 | 167.2208 | 223.7021 | 200.485 | 218.1612
309.6953 | 237.6953 | 476.2412 | 193.3569 | 165.0031 | 168.0516 | 224.57 | 201.2197 | 218.7604
310.6968 | 238.6968 | 476.0944 | 194.2186 | 165.904 | 168.8945 | 225.4443 | 201.9412 | 219.355
311.6982 | 239.6982 | 476.0468 | 195.073 | 166.8125 | 169.7304 | 226.3104 | 202.6567 | 219.9491
312.6896 | 240.6896 | 476.1101 | 195.9198 | 167.7249 | 170.5674 | 227.1699 | 203.3633 | 220.5401
313.7011 | 241.7011 | 476.2633 | 196.7291 | 168.6205 | 171.4131 | 228.0452 | 204.077 | 221.1339
314.6925 | 242.6925 | 476.3531 | 197.4887 | 169.5222 | 172.2611 | 228.9045 | 204.7865 | 221.725
315.6939 | 243.6939 | 476.2927 | 198.176 | 170.4168 | 173.0908 | 229.7897 | 205.4892 | 222.3069
316.6954 | 244.6954 | 476.3135 | 198.5467 | 171.3192 | 173.9222 | 230.6683 | 206.2006 | 222.8854
317.6968 | 245.6968 | 476.2022 | 198.7126 | 172.2105 | 174.7468 | 231.5548 | 206.8864 | 223.4557
318.6983 | 246.6983 | 476.0739 | 199.0439 | 173.0978 | 175.5719 | 232.445 | 207.5775 | 224.0241
319.6997 | 247.6997 | 476.0794 | 199.4257 | 173.9775 | 176.3888 | 233.3223 | 208.2766 | 224.5919
320.6911 | 248.6911 | 476.1482 | 199.8708 | 174.8477 | 177.2046 | 234.232 | 208.9654 | 225.1612
321.6926 | 249.6926 | 476.0842 | 200.3492 | 175.714 | 178.0187 | 235.1164 | 209.6532 | 225.7372
322.694 | 250.694 | 476.0687 | 200.8913 | 176.5865 | 178.828 | 236.1147 | 210.3406 | 226.3018
323.6955 | 251.6955 | 476.0699 | 201.4551 | 177.4297 | 179.638 | 237.1183 | 211.0317 | 226.8675
324.6969 | 252.6969 | 476.1465 | 201.9751 | 178.2938 | 180.4418 | 238.0266 | 211.7155 | 227.4077
325.6983 | 253.6983 | 476.0842 | 202.515 | 179.1388 | 181.2416 | 238.8998 | 212.3844 | 227.9517
326.6898 | 254.6898 | 476.0053 | 203.2262 | 179.9898 | 182.0554 | 239.7578 | 213.0684 | 228.4986
327.6912 | 255.6912 | 475.836 | 203.9907 | 180.8204 | 182.8634 | 240.5863 | 213.7359 | 229.0455
328.6926 | 256.6926 | 475.8677 | 204.6761 | 181.6537 | 183.6603 | 241.3818 | 214.4036 | 229.594
329.6941 | 257.6941 | 475.9025 | 205.3093 | 182.4913 | 184.4468 | 242.1965 | 215.0595 | 230.1419
330.6955 | 258.6955 | 475.8342 | 205.9666 | 183.32 | 185.2329 | 243.0029 | 215.7188 | 230.6962
331.697 | 259.697 | 475.7032 | 206.6285 | 184.1507 | 186.0092 | 243.833 | 216.3606 | 231.2447
332.6984 | 260.6984 | 475.7624 | 207.1966 | 184.957 | 186.7792 | 244.6891 | 217.0049 | 231.7822
333.6898 | 261.6898 | 475.7133 | 207.5878 | 185.7709 | 187.5525 | 245.5958 | 217.6473 | 232.3135
334.7013 | 262.7013 | 475.6828 | 207.6896 | 186.5687 | 188.3195 | 246.5181 | 218.2898 | 232.8471
335.6927 | 263.6927 | 475.6087 | 207.9347 | 187.3662 | 189.0895 | 247.4792 | 218.9322 | 233.3793
336.6941 | 264.6941 | 475.6031 | 208.2376 | 188.158 | 189.8736 | 248.4139 | 219.5628 | 233.9063
337.6956 | 265.6956 | 475.6409 | 208.563 | 188.9368 | 190.6457 | 249.3581 | 220.1939 | 234.4385
338.697 | 266.697 | 475.5955 | 208.9319 | 189.7183 | 191.425 | 250.3033 | 220.827 | 234.9741
339.6985 | 267.6985 | 475.7786 | 209.3384 | 190.4889 | 192.2022 | 251.236 | 221.4613 | 235.5037
340.6999 | 268.6999 | 475.9626 | 209.7969 | 191.2432 | 192.9865 | 252.1709 | 222.0715 | 236.0244
341.6913 | 269.6913 | 476.364 | 210.2584 | 192.0157 | 193.7689 | 253.0971 | 222.6898 | 236.5602
342.6928 | 270.6928 | 476.3885 | 210.7078 | 192.7715 | 194.5513 | 253.9931 | 223.3055 | 237.0761
343.6942 | 271.6942 | 476.5058 | 211.1624 | 193.5438 | 195.3218 | 254.8276 | 223.9214 | 237.5988
344.6956 | 272.6956 | 476.5838 | 211.6124 | 194.3755 | 196.0811 | 255.6361 | 224.5414 | 238.1237
345.6971 | 273.6971 | 476.6006 | 212.0641 | 195.2204 | 196.8173 | 256.4131 | 225.1517 | 238.6484
346.6985 | 274.6985 | 476.6577 | 212.5062 | 196.0439 | 197.5478 | 257.2009 | 225.774 | 239.1659
347.69 | 275.69 | 476.5749 | 212.969 | 196.8476 | 198.2633 | 258.0201 | 226.3869 | 239.6815
348.6914 | 276.6914 | 476.6089 | 213.4793 | 197.6238 | 198.974 | 258.8683 | 226.9922 | 240.2013
349.6928 | 277.6928 | 476.6313 | 214.0234 | 198.3835 | 199.6921 | 259.7692 | 227.6128 | 240.7068
350.6943 | 278.6943 | 476.4664 | 214.6207 | 199.1218 | 200.4062 | 260.655 | 228.2246 | 241.2113
351.6957 | 279.6957 | 476.3362 | 215.2317 | 199.8421 | 201.1476 | 261.7947 | 228.8367 | 241.7254
352.6972 | 280.6972 | 476.286 | 215.8688 | 200.5579 | 201.8844 | 262.3679 | 229.4445 | 242.2303
353.6986 | 281.6986 | 476.1586 | 216.5389 | 201.2563 | 202.6194 | 262.9925 | 230.0634 | 242.7531
354.69 | 282.69 | 476.0276 | 217.2513 | 201.9515 | 203.3463 | 263.5957 | 230.6828 | 243.2581
355.6915 | 283.6915 | 475.9077 | 217.9927 | 202.6383 | 204.0833 | 264.2322 | 231.2953 | 243.7799
356.6929 | 284.6929 | 476.0182 | 218.7701 | 203.3153 | 204.8266 | 264.8398 | 231.9041 | 244.2909
357.6943 | 285.6943 | 476.0374 | 219.6283 | 203.9891 | 205.5783 | 265.4347 | 232.5083 | 244.797
358.6958 | 286.6958 | 476.0914 | 220.434 | 204.6552 | 206.3515 | 266.0316 | 233.1072 | 245.2973
359.6972 | 287.6972 | 475.9111 | 221.1968 | 205.3147 | 207.1067 | 266.6015 | 233.693 | 245.8103
360.6987 | 288.6987 | 476.0089 | 221.8679 | 205.9811 | 207.8598 | 267.1615 | 234.2817 | 246.325
361.7001 | 289.7001 | 475.9672 | 222.4957 | 206.644 | 208.5852 | 267.728 | 234.8698 | 246.8408
362.6915 | 290.6915 | 475.8814 | 223.1518 | 207.3035 | 209.2851 | 268.2749 | 235.453 | 247.3546
363.693 | 291.693 | 475.9309 | 223.8274 | 207.9539 | 209.9717 | 268.8017 | 236.0363 | 247.8518
364.6944 | 292.6944 | 475.9724 | 224.4979 | 208.5977 | 210.6576 | 269.3595 | 236.6378 | 248.3632
365.6958 | 293.6958 | 475.9663 | 225.1478 | 209.2418 | 211.3275 | 269.8876 | 237.2114 | 248.8801
366.6973 | 294.6973 | 476.1333 | 225.826 | 209.8849 | 211.9765 | 270.0945 | 237.8015 | 249.4049
367.6887 | 295.6887 | 476.115 | 226.5322 | 210.519 | 212.6174 | 270.0084 | 238.3699 | 249.9365
368.6902 | 296.6902 | 476.1328 | 227.2686 | 211.1498 | 213.2412 | 269.9923 | 238.9595 | 250.4579
369.6916 | 297.6916 | 476.0922 | 228.0291 | 211.7976 | 213.8503 | 270.0433 | 239.522 | 250.9757
370.693 | 298.693 | 476.0464 | 228.8077 | 212.429 | 214.4571 | 270.0538 | 239.9963 | 251.4918
371.6945 | 299.6945 | 475.9619 | 229.5682 | 213.066 | 215.0698 | 270.0606 | 240.477 | 251.9955
372.6959 | 300.6959 | 475.872 | 230.2674 | 213.6846 | 215.6894 | 270.1036 | 240.9583 | 252.5061
373.6974 | 301.6974 | 475.8238 | 231.0003 | 214.3028 | 216.298 | 270.1422 | 241.4702 | 253.0091
374.6988 | 302.6988 | 475.8416 | 231.8743 | 214.9193 | 216.8997 | 270.1832 | 241.9786 | 253.5118
375.6902 | 303.6902 | 475.912 | 232.7555 | 215.5485 | 217.5057 | 270.1874 | 242.4886 | 254.0074
376.6917 | 304.6917 | 475.8834 | 233.6539 | 216.1553 | 218.1041 | 270.2639 | 243.0058 | 254.5033
377.6931 | 305.6931 | 475.8087 | 234.5126 | 216.7609 | 218.6961 | 270.3718 | 243.5226 | 254.9989
378.6945 | 306.6945 | 475.8384 | 235.3397 | 217.3846 | 219.2912 | 270.3726 | 244.0446 | 255.4996
379.696 | 307.696 | 475.7566 | 236.0969 | 217.9755 | 219.8755 | 270.2481 | 244.5521 | 255.9979
380.6974 | 308.6974 | 475.8025 | 236.7863 | 218.5796 | 220.4862 | 269.9969 | 245.0605 | 256.4945
381.6989 | 309.6989 | 475.8313 | 237.5324 | 219.1673 | 221.0775 | 268.5232 | 245.5578 | 256.991
382.7003 | 310.7003 | 475.854 | 238.2953 | 219.7554 | 221.6664 | 267.2537 | 246.0272 | 257.4798
383.6917 | 311.6917 | 475.9033 | 239.1134 | 220.342 | 222.2577 | 266.378 | 246.5089 | 257.9622
384.6932 | 312.6932 | 475.7223 | 239.9111 | 220.922 | 222.8451 | 265.791 | 246.9949 | 258.4517
385.6946 | 313.6946 | 475.6709 | 240.544 | 221.5131 | 223.447 | 265.6229 | 247.4844 | 258.94
386.696 | 314.696 | 475.6125 | 241.1533 | 222.0789 | 224.0416 | 265.9484 | 247.9902 | 259.4355
387.6975 | 315.6975 | 475.6797 | 241.8034 | 222.6452 | 224.6392 | 266.2166 | 248.4898 | 259.9126
388.6989 | 316.6989 | 475.7576 | 242.4599 | 223.2096 | 225.239 | 266.5756 | 248.8931 | 260.4017
389.6903 | 317.6903 | 475.789 | 243.0854 | 223.7799 | 225.849 | 266.9397 | 249.2612 | 260.8805
390.6918 | 318.6918 | 475.8881 | 243.8243 | 224.3291 | 226.4586 | 267.3075 | 249.7249 | 261.3632
391.6932 | 319.6932 | 475.9898 | 244.6702 | 224.8933 | 227.062 | 267.7299 | 250.1974 | 261.836
392.6947 | 320.6947 | 476.0322 | 245.4979 | 225.4375 | 227.6416 | 268.1128 | 250.6784 | 262.3027
393.6961 | 321.6961 | 476.1483 | 246.5527 | 225.9977 | 228.2126 | 268.3579 | 251.1428 | 262.7687
394.6975 | 322.6975 | 476.2086 | 250.5868 | 226.5559 | 228.7735 | 268.6125 | 251.6081 | 263.231
395.689 | 323.689 | 476.1304 | 253.8414 | 227.1103 | 229.3222 | 268.8603 | 252.0033 | 263.696
396.6904 | 324.6904 | 476.0935 | 256.2571 | 227.6755 | 229.8524 | 269.0653 | 252.4117 | 264.1668
397.6919 | 325.6919 | 476.1059 | 258.1921 | 228.2086 | 230.401 | 269.2484 | 252.8769 | 264.6191
398.6933 | 326.6933 | 475.9703 | 259.4152 | 228.7633 | 230.9202 | 269.4112 | 253.3889 | 265.0761
399.6947 | 327.6947 | 475.8765 | 259.8731 | 229.3022 | 231.4445 | 269.3331 | 253.9791 | 265.5269
400.6962 | 328.6962 | 475.9534 | 260.8627 | 229.8471 | 231.9667 | 269.1683 | 254.5114 | 265.9844
401.6976 | 329.6976 | 476.0207 | 262.0405 | 230.3867 | 232.4804 | 269.1235 | 254.9841 | 266.4366
402.6991 | 330.6991 | 475.9912 | 262.8258 | 230.9215 | 233.0006 | 269.2446 | 255.4251 | 266.8783
403.6905 | 331.6905 | 476.0846 | 263.6169 | 231.4459 | 233.5182 | 269.5421 | 255.8926 | 267.3172
404.6919 | 332.6919 | 476.1152 | 264.7685 | 231.9734 | 234.0325 | 269.8687 | 256.3447 | 267.7571
405.6934 | 333.6934 | 476.2987 | 266.2233 | 232.5075 | 234.5468 | 270.1676 | 256.8135 | 268.1989
406.7549 | 334.7549 | 476.3168 | 267.4368 | 233.0937 | 235.0817 | 270.5693 | 257.3098 | 268.6394
407.6962 | 335.6962 | 476.3959 | 268.4364 | 233.6084 | 235.5645 | 271.0161 | 257.8169 | 269.0377
408.6977 | 336.6977 | 476.4845 | 269.2533 | 234.1455 | 236.0749 | 271.5762 | 258.3669 | 269.4278
409.6991 | 337.6991 | 476.4458 | 270.1607 | 234.6954 | 236.5876 | 272.1738 | 258.9193 | 269.816
410.6905 | 338.6905 | 476.3958 | 271.328 | 235.2337 | 237.0908 | 272.734 | 259.5071 | 270.204
411.692 | 339.692 | 476.3237 | 272.345 | 235.7711 | 237.5953 | 273.1487 | 260.0847 | 270.5811
412.6934 | 340.6934 | 476.3828 | 273.4095 | 236.3068 | 238.0969 | 273.6207 | 260.6821 | 270.9552
413.6949 | 341.6949 | 476.4108 | 274.4591 | 236.8362 | 238.604 | 273.9947 | 261.2545 | 271.3162
414.6963 | 342.6963 | 476.4205 | 275.4907 | 237.3715 | 239.095 | 274.04 | 261.7209 | 271.674
415.6977 | 343.6977 | 476.3181 | 276.4687 | 237.8917 | 239.5783 | 273.5645 | 262.188 | 272.0286
416.6892 | 344.6892 | 476.2597 | 277.4174 | 238.406 | 240.0638 | 273.1798 | 262.6974 | 272.376
417.6906 | 345.6906 | 476.3046 | 278.2999 | 238.9322 | 240.5121 | 272.4588 | 263.1868 | 272.7162
418.692 | 346.692 | 476.402 | 278.9243 | 239.4333 | 240.9309 | 271.699 | 263.6651 | 273.051
419.6935 | 347.6935 | 476.442 | 279.6444 | 239.931 | 241.3017 | 269.3062 | 264.2327 | 273.3792
420.6949 | 348.6949 | 476.3377 | 280.4226 | 240.4589 | 241.6968 | 267.4855 | 264.8157 | 273.6809
421.6964 | 349.6964 | 476.3253 | 281.1506 | 240.966 | 242.1022 | 266.103 | 265.3955 | 273.9941
422.6978 | 350.6978 | 476.3318 | 281.8436 | 241.4888 | 242.5124 | 264.9677 | 265.9036 | 274.3143
423.6992 | 351.6992 | 476.1971 | 282.4998 | 241.9963 | 242.9268 | 264.0724 | 266.42 | 274.6246
424.7007 | 352.7007 | 476.0369 | 282.7434 | 242.5016 | 243.3552 | 263.356 | 266.922 | 274.9274
425.6921 | 353.6921 | 475.9481 | 282.9275 | 243.0042 | 243.7847 | 262.8118 | 267.4444 | 275.2054
426.6936 | 354.6936 | 475.9035 | 283.1722 | 243.5203 | 244.2077 | 262.4063 | 267.8005 | 275.4838
427.695 | 355.695 | 475.7873 | 283.5226 | 244.0527 | 244.6216 | 262.1301 | 268.104 | 275.7711
428.6964 | 356.6964 | 475.7851 | 283.8656 | 244.5484 | 245.0289 | 261.9198 | 268.4329 | 276.0636
429.6979 | 357.6979 | 475.6687 | 284.2483 | 245.0438 | 245.4205 | 261.7453 | 268.494 | 276.3485
430.6993 | 358.6993 | 475.6146 | 284.7923 | 245.5344 | 245.8212 | 261.5676 | 268.4623 | 276.6402
431.6907 | 359.6907 | 475.5589 | 285.1076 | 246.023 | 246.2209 | 261.5097 | 268.5696 | 276.9231
432.6922 | 360.6922 | 475.519 | 285.26 | 246.49 | 246.627 | 261.5156 | 268.6674 | 277.1999
433.6936 | 361.6936 | 475.6158 | 285.4189 | 246.9707 | 247.0288 | 261.56 | 268.7705 | 277.4768
434.6951 | 362.6951 | 475.6876 | 285.5566 | 247.4203 | 247.446 | 261.6578 | 268.8855 | 277.7446
435.6965 | 363.6965 | 475.7229 | 285.8456 | 247.8729 | 247.8715 | 261.8475 | 269 | 278.002
436.6979 | 364.6979 | 475.8353 | 286.0219 | 248.3274 | 248.2967 | 262.1361 | 269.1095 | 278.2546
437.6894 | 365.6894 | 475.9033 | 286.1233 | 248.7748 | 248.7352 | 262.3937 | 269.1909 | 278.5257
438.6908 | 366.6908 | 475.9323 | 286.0951 | 249.2168 | 249.173 | 263.0133 | 269.2445 | 278.7766
439.6922 | 367.6922 | 476.0177 | 285.9769 | 249.6537 | 249.6392 | 263.6813 | 269.3339 | 278.9989
440.6937 | 368.6937 | 476.0455 | 285.9169 | 250.1193 | 250.0717 | 264.274 | 269.4222 | 279.2008
441.6951 | 369.6951 | 476.0137 | 285.9032 | 250.5639 | 250.4945 | 264.8654 | 269.4572 | 279.4341
442.6966 | 370.6966 | 476.0225 | 285.894 | 251.0098 | 250.9205 | 265.5699 | 269.491 | 279.6704
443.698 | 371.698 | 475.975 | 285.9088 | 251.4661 | 251.3335 | 266.4765 | 269.5405 | 279.8894
444.6894 | 372.6894 | 475.8044 | 285.9881 | 251.9156 | 251.7476 | 267.3977 | 269.6408 | 280.1169
445.6909 | 373.6909 | 475.7382 | 286.105 | 252.3417 | 252.1544 | 268.1802 | 269.858 | 280.3417
446.6923 | 374.6923 | 475.5447 | 286.2141 | 252.7921 | 252.5625 | 268.9851 | 269.9441 | 280.5669
447.6938 | 375.6938 | 475.3777 | 286.3502 | 253.2301 | 252.9562 | 269.8462 | 270.0616 | 280.7869
448.6952 | 376.6952 | 475.4406 | 285.8383 | 253.6599 | 253.3734 | 270.7864 | 270.1557 | 281.0059
449.6966 | 377.6966 | 475.4096 | 282.8641 | 254.0952 | 253.7697 | 271.9477 | 270.2586 | 281.2206
450.6981 | 378.6981 | 475.4361 | 281.3692 | 254.5265 | 254.1715 | 273.448 | 270.3613 | 281.4482
451.6995 | 379.6995 | 475.5876 | 280.4094 | 254.9496 | 254.572 | 275.6351 | 270.5043 | 281.6584
452.6909 | 380.6909 | 475.7616 | 279.7743 | 255.3651 | 254.9792 | 277.4709 | 270.6367 | 281.8689
453.6924 | 381.6924 | 475.6814 | 279.3608 | 255.7679 | 255.3759 | 278.865 | 270.8117 | 282.0851
454.6938 | 382.6938 | 475.6498 | 279.0924 | 256.1768 | 255.7814 | 280.0237 | 271.0233 | 282.2867
455.6953 | 383.6953 | 475.4706 | 278.9455 | 256.5855 | 256.1698 | 281.0449 | 271.2086 | 282.5077
456.6967 | 384.6967 | 475.3735 | 278.8699 | 257.0023 | 256.563 | 281.9698 | 271.385 | 282.7252
457.6981 | 385.6981 | 475.16 | 278.8437 | 257.4016 | 256.9664 | 282.79 | 271.5324 | 282.9437
458.6996 | 386.6996 | 475.126 | 278.8945 | 257.8111 | 257.3692 | 283.5477 | 271.6619 | 283.1339
459.691 | 387.691 | 475.0824 | 278.9901 | 258.2208 | 257.7766 | 284.1618 | 271.8374 | 283.3478
460.6924 | 388.6924 | 474.8833 | 279.162 | 258.6133 | 258.1894 | 284.7393 | 272.0889 | 283.5257
461.6939 | 389.6939 | 474.7825 | 279.3616 | 259.0126 | 258.6004 | 285.3564 | 272.3518 | 283.7301
462.6953 | 390.6953 | 474.8327 | 279.6018 | 259.3935 | 259.0167 | 285.8471 | 272.6122 | 283.9216
463.6968 | 391.6968 | 474.904 | 279.8808 | 259.8022 | 259.4326 | 286.3183 | 272.9033 | 284.1291
464.6982 | 392.6982 | 474.9951 | 280.1742 | 260.1825 | 259.83 | 286.7864 | 273.198 | 284.3305
465.6996 | 393.6996 | 475.164 | 280.5045 | 260.6004 | 260.2417 | 287.2224 | 273.4798 | 284.5535
466.7011 | 394.7011 | 475.3064 | 280.8756 | 260.9999 | 260.6494 | 287.5974 | 273.7401 | 284.7923
467.6925 | 395.6925 | 475.3758 | 281.2814 | 261.4049 | 261.0571 | 288.0134 | 274.0185 | 285.0462
468.6939 | 396.6939 | 475.3836 | 281.6923 | 261.8198 | 261.4664 | 288.444 | 274.2936 | 285.287
469.6954 | 397.6954 | 475.3659 | 282.1409 | 262.2289 | 261.8815 | 288.8356 | 274.5812 | 285.5226
470.6968 | 398.6968 | 475.3293 | 282.6286 | 262.6384 | 262.2945 | 289.1899 | 274.8817 | 285.7676
471.6983 | 399.6983 | 475.324 | 283.1366 | 263.0516 | 262.7084 | 289.4733 | 275.1846 | 286.0056
472.6997 | 400.6997 | 475.3863 | 283.6787 | 263.4596 | 263.1313 | 289.7448 | 275.487 | 286.2447
473.6911 | 401.6911 | 475.4846 | 284.2438 | 263.8759 | 263.5602 | 290.0289 | 275.8225 | 286.4471
474.6926 | 402.6926 | 475.7546 | 284.832 | 264.2856 | 263.986 | 290.2732 | 276.1695 | 286.6705
475.694 | 403.694 | 475.8498 | 285.4389 | 264.6658 | 264.4087 | 290.5057 | 276.5074 | 286.9118
476.6955 | 404.6955 | 476.0127 | 286.0641 | 265.0443 | 264.8323 | 290.7272 | 276.8739 | 287.1738
477.6969 | 405.6969 | 476.031 | 286.722 | 265.4351 | 265.258 | 290.9972 | 277.2056 | 287.4294
478.6983 | 406.6983 | 476.2084 | 287.4265 | 265.8088 | 265.6921 | 291.2407 | 277.5442 | 287.6769
479.6998 | 407.6998 | 476.3974 | 288.1881 | 266.1943 | 266.1341 | 291.463 | 277.9024 | 287.933
480.6912 | 408.6912 | 476.6448 | 288.927 | 266.5194 | 266.5694 | 291.6705 | 278.2428 | 288.1802
481.6926 | 409.6926 | 476.786 | 289.6424 | 266.881 | 267.0076 | 291.9266 | 278.6255 | 288.3678
482.6941 | 410.6941 | 476.8692 | 290.3599 | 267.2347 | 267.4529 | 292.2025 | 278.97 | 288.5709
483.6955 | 411.6955 | 476.9483 | 291.0943 | 267.5789 | 267.8944 | 292.4642 | 279.2805 | 288.7764
484.697 | 412.697 | 476.908 | 291.8158 | 267.9293 | 268.3374 | 292.704 | 279.5692 | 288.9736
485.6984 | 413.6984 | 476.9218 | 292.5496 | 268.2909 | 268.7844 | 292.9731 | 279.8368 | 289.2027
486.6898 | 414.6898 | 476.7626 | 293.3118 | 268.6404 | 269.2322 | 293.2819 | 280.1065 | 289.3963
487.6913 | 415.6913 | 476.6887 | 294.214 | 269.0287 | 269.6758 | 293.5729 | 280.3686 | 289.6057
488.6927 | 416.6927 | 476.8842 | 295.3791 | 269.4187 | 270.1229 | 293.8522 | 280.5967 | 289.8419
489.6941 | 417.6941 | 476.8909 | 296.6882 | 269.8006 | 270.5638 | 294.1312 | 280.7851 | 290.0467
490.6956 | 418.6956 | 476.7959 | 297.6317 | 270.1839 | 271.0152 | 294.402 | 281.0091 | 290.2491
491.697 | 419.697 | 476.6371 | 298.5347 | 270.5741 | 271.4689 | 294.6985 | 281.2183 | 290.4865
492.6985 | 420.6985 | 476.5064 | 299.282 | 270.9568 | 271.9605 | 294.9926 | 281.4484 | 290.7269
493.6999 | 421.6999 | 476.2883 | 299.9977 | 271.3903 | 272.4642 | 295.2865 | 281.7209 | 290.9314
494.6913 | 422.6913 | 476.0375 | 300.6743 | 271.7912 | 272.9883 | 295.5384 | 281.9046 | 291.1166
495.6928 | 423.6928 | 475.8928 | 301.362 | 272.1726 | 273.4603 | 295.867 | 282.1103 | 291.3218
496.6942 | 424.6942 | 475.7424 | 302.1632 | 272.5881 | 273.9271 | 296.1814 | 282.2989 | 291.5301
497.6957 | 425.6957 | 475.599 | 302.8749 | 272.9844 | 274.3852 | 296.5007 | 282.4865 | 291.7662
498.6971 | 426.6971 | 475.6381 | 303.5296 | 273.4214 | 274.8436 | 296.8717 | 282.6613 | 292.0159
499.6985 | 427.6985 | 475.7123 | 304.2413 | 273.8359 | 275.3189 | 297.1911 | 282.8773 | 292.2129
500.69 | 428.69 | 475.7369 | 305.1612 | 274.2437 | 275.7768 | 297.4968 | 283.074 | 292.4327
501.6914 | 429.6914 | 475.7389 | 305.81 | 274.6747 | 276.2421 | 297.8153 | 283.2665 | 292.6532
502.6928 | 430.6928 | 475.6504 | 306.453 | 275.0892 | 276.7644 | 298.1977 | 283.5158 | 292.8728
503.6943 | 431.6943 | 475.5703 | 307.0938 | 275.485 | 277.2686 | 298.5252 | 283.7294 | 293.1378
504.6957 | 432.6957 | 475.6225 | 307.7367 | 275.9007 | 277.728 | 298.8628 | 284.0071 | 293.3983
505.6972 | 433.6972 | 475.78 | 308.485 | 276.2876 | 278.1956 | 299.2244 | 284.2971 | 293.67
506.6986 | 434.6986 | 475.7394 | 309.0761 | 276.7122 | 278.6688 | 299.5767 | 284.6394 | 293.9321
507.7 | 435.7 | 475.8388 | 309.7061 | 277.1679 | 279.0937 | 299.88 | 285.0001 | 294.1486
508.6915 | 436.6915 | 475.8918 | 310.3366 | 277.5805 | 279.5021 | 300.1875 | 285.3463 | 294.3294
509.6929 | 437.6929 | 475.7947 | 311.0218 | 277.9759 | 279.9412 | 300.5281 | 285.6944 | 294.5365
510.6943 | 438.6943 | 475.6427 | 311.6404 | 278.4052 | 280.3669 | 300.8829 | 286.0701 | 294.7385
511.6958 | 439.6958 | 475.4525 | 312.2328 | 278.8519 | 280.8047 | 301.2246 | 286.4045 | 294.9498
512.6972 | 440.6972 | 475.2559 | 312.8025 | 279.3011 | 281.2404 | 301.5942 | 286.7549 | 295.1697
513.6987 | 441.6987 | 475.1567 | 313.368 | 279.7124 | 281.6787 | 301.9466 | 287.0961 | 295.4053
514.7001 | 442.7001 | 475.1554 | 313.9634 | 280.1336 | 282.1007 | 302.2771 | 287.4389 | 295.6481
515.6915 | 443.6915 | 475.287 | 314.6688 | 280.5683 | 282.5264 | 302.6384 | 287.8317 | 295.8747
516.693 | 444.693 | 475.3125 | 315.3374 | 280.9963 | 282.9487 | 303.0109 | 288.2406 | 296.1204
517.6944 | 445.6944 | 475.2343 | 315.876 | 281.4378 | 283.3609 | 303.4042 | 288.6187 | 296.3554
518.6958 | 446.6958 | 475.115 | 316.4312 | 281.8375 | 283.8624 | 303.7409 | 288.9954 | 296.6058
519.6973 | 447.6973 | 475.1212 | 316.951 | 282.2757 | 284.3928 | 304.1142 | 289.3389 | 296.8764
520.6887 | 448.6887 | 475.1175 | 317.5755 | 282.7018 | 284.8502 | 304.4923 | 289.7077 | 297.1532
521.6902 | 449.6902 | 475.1335 | 318.1786 | 283.1284 | 285.285 | 304.8401 | 290.0722 | 297.4297
522.6916 | 450.6916 | 475.2462 | 318.6877 | 283.2714 | 285.7174 | 305.2114 | 290.4389 | 297.6772
523.693 | 451.693 | 475.3653 | 319.2293 | 283.4777 | 286.145 | 305.5904 | 290.7838 | 297.9039
524.6945 | 452.6945 | 475.3612 | 319.7448 | 283.7729 | 286.6534 | 305.9685 | 291.1697 | 298.2585
525.6959 | 453.6959 | 475.3592 | 320.1937 | 284.1221 | 287.1615 | 306.3489 | 291.532 | 298.6465
526.6974 | 454.6974 | 475.3388 | 320.7153 | 284.516 | 287.6365 | 306.7142 | 291.8666 | 299.0326
527.6988 | 455.6988 | 475.2853 | 321.2407 | 284.9125 | 288.0884 | 307.1233 | 292.2057 | 299.4257
528.7002 | 456.7002 | 475.1775 | 321.7137 | 285.3158 | 288.4933 | 307.4844 | 292.5565 | 299.8258
529.6917 | 457.6917 | 475.0479 | 322.2412 | 285.7242 | 288.9154 | 307.8623 | 292.8868 | 300.2144
530.6931 | 458.6931 | 474.9577 | 322.778 | 286.1209 | 289.3506 | 308.2843 | 293.2158 | 300.6123
531.6945 | 459.6945 | 474.9317 | 323.1636 | 286.5613 | 289.7709 | 308.6566 | 293.5812 | 301.0216
532.696 | 460.696 | 475.019 | 323.6779 | 286.9978 | 290.1762 | 309.034 | 293.9705 | 301.421
533.6974 | 461.6974 | 475.0809 | 324.1371 | 287.4437 | 290.6234 | 309.4171 | 294.2712 | 301.8375
534.6989 | 462.6989 | 475.3528 | 324.5714 | 287.9016 | 291.0347 | 309.7967 | 294.5602 | 302.2394
535.7003 | 463.7003 | 475.5186 | 325.0403 | 288.3569 | 291.4574 | 310.1633 | 294.8579 | 302.6413
536.6917 | 464.6917 | 475.51 | 325.485 | 288.8079 | 291.883 | 310.5655 | 295.1184 | 303.0356
537.6932 | 465.6932 | 475.4499 | 325.9072 | 289.267 | 292.3117 | 310.95 | 295.436 | 303.4593
538.6946 | 466.6946 | 475.4279 | 326.3391 | 289.7295 | 292.7783 | 311.3276 | 295.7681 | 303.8759
539.696 | 467.696 | 475.4547 | 326.8016 | 290.1794 | 293.2187 | 311.7465 | 296.0871 | 304.2867
540.6975 | 468.6975 | 475.5792 | 327.2228 | 290.6419 | 293.6411 | 312.1177 | 296.2546 | 304.6863
541.6989 | 469.6989 | 475.7262 | 327.6571 | 291.0913 | 294.0622 | 312.5272 | 296.4686 | 305.1134
542.6904 | 470.6904 | 475.9375 | 328.1215 | 291.5419 | 294.5211 | 312.8948 | 296.668 | 305.5474
543.6918 | 471.6918 | 475.9113 | 328.5203 | 291.9981 | 294.9577 | 313.3195 | 296.8614 | 305.9366
544.6932 | 472.6932 | 475.8987 | 328.9274 | 292.4529 | 295.4078 | 313.7032 | 297.0735 | 306.3172
545.6947 | 473.6947 | 475.8376 | 329.3769 | 292.9076 | 295.8394 | 314.1001 | 297.3113 | 306.7078
546.6961 | 474.6961 | 475.9833 | 329.705 | 293.3952 | 296.2742 | 314.5147 | 297.5504 | 307.0849
547.6976 | 475.6976 | 476.0951 | 330.0993 | 293.8831 | 296.7229 | 314.8966 | 297.7659 | 307.4689
548.699 | 476.699 | 476.1204 | 330.4504 | 294.335 | 297.196 | 315.2907 | 298.0014 | 307.8673
549.7004 | 477.7004 | 476.1396 | 330.8686 | 294.788 | 297.6353 | 315.6887 | 298.1846 | 308.2633
550.6919 | 478.6919 | 476.1786 | 331.2516 | 295.2361 | 298.0706 | 316.0952 | 298.384 | 308.6632
551.6933 | 479.6933 | 476.1274 | 331.6646 | 295.6806 | 298.5126 | 316.506 | 298.5704 | 309.0274
552.6947 | 480.6947 | 475.958 | 332.0377 | 296.1456 | 298.9456 | 316.9002 | 298.7678 | 309.415
553.6962 | 481.6962 | 475.815 | 332.4081 | 296.6072 | 299.3728 | 317.31 | 299.0004 | 309.8004
554.6976 | 482.6976 | 475.7452 | 332.7981 | 297.0793 | 299.7947 | 317.7058 | 299.2401 | 310.1885
555.6991 | 483.6991 | 475.7904 | 333.1363 | 297.5549 | 300.2575 | 318.1116 | 299.5105 | 310.5647
556.7005 | 484.7005 | 475.7554 | 333.4881 | 298.01 | 300.7191 | 318.5185 | 299.7731 | 310.9788
557.6919 | 485.6919 | 475.7052 | 333.7865 | 298.4592 | 301.1434 | 318.937 | 300.0774 | 311.3837
558.6934 | 486.6934 | 475.65 | 334.1378 | 298.9297 | 301.5856 | 319.3284 | 300.34 | 311.7765
559.6948 | 487.6948 | 475.7021 | 334.4892 | 299.3885 | 302.0161 | 319.7201 | 300.6194 | 312.1485
560.6962 | 488.6962 | 475.5609 | 334.8396 | 299.8216 | 302.435 | 320.1045 | 300.8374 | 312.5034
561.6977 | 489.6977 | 475.3799 | 335.1948 | 300.2741 | 302.89 | 320.4958 | 301.097 | 312.8677
562.6991 | 490.6991 | 475.3281 | 335.5027 | 300.7447 | 303.3188 | 320.9093 | 301.3689 | 313.2313
563.6905 | 491.6905 | 475.4041 | 335.8609 | 301.2004 | 303.7303 | 321.3342 | 301.6334 | 313.626
564.692 | 492.692 | 475.4102 | 336.2137 | 301.6559 | 304.1523 | 321.725 | 301.9216 | 314.0568
565.6934 | 493.6934 | 475.3737 | 336.5324 | 302.0833 | 304.5817 | 322.1055 | 302.2128 | 314.4778
566.6949 | 494.6949 | 475.2099 | 336.8538 | 302.5451 | 305.011 | 322.5006 | 302.4375 | 314.8567
567.6963 | 495.6963 | 475.2324 | 337.1892 | 303.0525 | 305.4472 | 322.8559 | 302.671 | 315.2255
568.6977 | 496.6977 | 475.2303 | 337.5209 | 303.5008 | 305.8729 | 323.2386 | 302.8552 | 315.5843
569.6892 | 497.6892 | 475.1667 | 337.803 | 303.9296 | 306.2751 | 323.6341 | 303.0719 | 315.9355
570.6906 | 498.6906 | 474.9766 | 338.1132 | 304.3694 | 306.6854 | 323.9916 | 303.3002 | 316.2659
571.6921 | 499.6921 | 474.8821 | 338.445 | 304.7983 | 307.0957 | 324.4052 | 303.5523 | 316.6028
572.6935 | 500.6935 | 474.8362 | 338.7686 | 305.2336 | 307.5162 | 324.7763 | 303.8199 | 316.9205
573.6949 | 501.6949 | 474.8104 | 339.1064 | 305.7251 | 307.9204 | 325.1696 | 304.0868 | 317.2646
574.6964 | 502.6964 | 474.85 | 339.4502 | 306.2002 | 308.3246 | 325.5362 | 304.3732 | 317.6078
575.6978 | 503.6978 | 474.9052 | 339.7698 | 306.6162 | 308.7221 | 325.9423 | 304.6459 | 317.9258
576.6993 | 504.6993 | 474.8928 | 340.1098 | 307.0546 | 309.1195 | 326.314 | 304.9354 | 318.2283
577.6907 | 505.6907 | 474.8881 | 340.4384 | 307.502 | 309.54 | 326.6987 | 305.2018 | 318.5343
578.6921 | 506.6921 | 474.9366 | 340.7543 | 307.9349 | 309.9351 | 327.0889 | 305.5123 | 318.7895
579.6936 | 507.6936 | 474.9219 | 341.0829 | 308.3924 | 310.3405 | 327.4791 | 305.7816 | 318.9792
580.695 | 508.695 | 475.0011 | 341.3973 | 308.8037 | 310.7583 | 327.8582 | 306.079 | 319.2032
581.6964 | 509.6964 | 475.1034 | 341.717 | 309.2219 | 311.1328 | 328.2509 | 306.3757 | 319.4238
582.6979 | 510.6979 | 475.1825 | 342.0441 | 309.6582 | 311.5448 | 328.6361 | 306.702 | 319.5658
583.6993 | 511.6993 | 475.327 | 342.3833 | 310.0763 | 311.9382 | 329.0073 | 307.029 | 319.7796
584.6907 | 512.6907 | 475.4018 | 342.6976 | 310.5024 | 312.3398 | 329.3968 | 307.3693 | 319.9547
585.6922 | 513.6922 | 475.2734 | 343.0138 | 310.9616 | 312.725 | 329.7798 | 307.6658 | 320.1339
586.6936 | 514.6936 | 475.1355 | 343.3504 | 311.3954 | 313.1212 | 330.164 | 307.9555 | 320.3152
587.6951 | 515.6951 | 475.0855 | 343.6519 | 311.8177 | 313.5174 | 330.5593 | 308.2521 | 320.4914
588.6965 | 516.6965 | 475.0757 | 343.9645 | 312.2458 | 313.9344 | 330.9698 | 308.5204 | 320.6953
589.6979 | 517.6979 | 475.2552 | 344.3011 | 312.6468 | 314.306 | 331.3513 | 308.8324 | 320.7359
590.6894 | 518.6894 | 475.336 | 344.5965 | 313.0679 | 314.6931 | 331.7665 | 309.1444 | 320.7844
591.7008 | 519.7008 | 475.5179 | 344.9128 | 313.5249 | 315.0921 | 332.1444 | 309.4675 | 320.9316
592.6922 | 520.6922 | 475.6245 | 345.2018 | 313.9404 | 315.4805 | 332.5121 | 309.7668 | 321.2192
593.6937 | 521.6937 | 475.6761 | 345.5132 | 314.337 | 315.873 | 332.9074 | 310.08 | 321.3832
594.6951 | 522.6951 | 475.6159 | 345.8238 | 314.7528 | 316.2841 | 333.2805 | 310.376 | 321.5232
595.6966 | 523.6966 | 475.6438 | 346.1257 | 315.1531 | 316.6684 | 333.6664 | 310.6477 | 321.6862
596.698 | 524.698 | 475.7661 | 346.4302 | 315.5756 | 317.0536 | 334.0607 | 310.9117 | 321.8518
597.6994 | 525.6994 | 475.8359 | 346.7169 | 315.9962 | 317.454 | 334.4276 | 311.1699 | 322.0563
598.6909 | 526.6909 | 475.6783 | 347.0117 | 316.4391 | 317.8182 | 334.7782 | 311.4594 | 322.2938
599.6923 | 527.6923 | 475.5529 | 347.3243 | 316.8473 | 318.2283 | 335.153 | 311.7409 | 322.4955
600.6938 | 528.6938 | 475.7196 | 347.6161 | 317.2588 | 318.5925 | 335.5299 | 311.949 | 322.9266
601.6952 | 529.6952 | 475.7013 | 347.9123 | 317.7014 | 318.97 | 335.9128 | 312.1714 | 323.4232
602.6966 | 530.6966 | 475.5499 | 348.2086 | 318.0929 | 319.3751 | 336.2674 | 312.3764 | 323.8935
603.6981 | 531.6981 | 475.4351 | 348.5038 | 318.4933 | 319.7463 | 336.6339 | 312.5763 | 324.3495
604.6995 | 532.6995 | 475.2186 | 348.7817 | 318.901 | 320.1298 | 337.066 | 312.7543 | 324.779
605.6909 | 533.6909 | 475.2172 | 349.0774 | 319.3417 | 320.5288 | 337.3792 | 312.9317 | 325.2045
606.6924 | 534.6924 | 475.2087 | 349.3705 | 319.7353 | 320.919 | 337.7772 | 313.0791 | 325.6297
607.6938 | 535.6938 | 475.0781 | 349.6712 | 320.1255 | 321.3236 | 338.091 | 313.2259 | 326.0498
608.6953 | 536.6953 | 474.8206 | 349.9502 | 320.5089 | 321.7126 | 338.4351 | 313.4012 | 326.455
609.6967 | 537.6967 | 474.8348 | 350.2508 | 320.9143 | 322.1085 | 338.7839 | 313.5816 | 326.8558
610.6981 | 538.6981 | 474.8958 | 350.5469 | 321.2887 | 322.5043 | 339.1179 | 313.7726 | 327.1981
611.6896 | 539.6896 | 474.9004 | 350.8392 | 321.6859 | 322.9086 | 339.4565 | 313.9745 | 327.4723
612.691 | 540.691 | 474.9033 | 351.1312 | 322.0772 | 323.3219 | 339.7787 | 314.1895 | 327.8327
613.6924 | 541.6924 | 474.9429 | 351.4177 | 322.4451 | 323.7215 | 340.1104 | 314.3966 | 328.2275
614.6939 | 542.6939 | 474.8413 | 351.6986 | 322.8273 | 324.0972 | 340.4375 | 314.6198 | 328.6547
615.6953 | 543.6953 | 474.8999 | 351.9928 | 323.1902 | 324.5027 | 340.7571 | 314.8533 | 328.8548
616.6968 | 544.6968 | 475.0066 | 352.2776 | 323.5619 | 324.8981 | 341.0861 | 315.0886 | 328.8211
617.6982 | 545.6982 | 474.9844 | 352.5597 | 323.9551 | 325.299 | 341.4317 | 315.323 | 328.9851
618.6996 | 546.6996 | 475.2079 | 352.8475 | 324.3387 | 325.6777 | 341.7498 | 315.5632 | 329.3194
619.6911 | 547.6911 | 475.5188 | 353.1311 | 324.7191 | 326.0566 | 342.0792 | 315.8087 | 329.9979
620.6925 | 548.6925 | 475.7701 | 353.4256 | 325.1123 | 326.4394 | 342.3865 | 316.0875 | 330.618
621.694 | 549.694 | 475.9315 | 353.7181 | 325.5069 | 326.8058 | 342.7294 | 316.3681 | 331.1745
622.6954 | 550.6954 | 476.0767 | 354.024 | 325.9164 | 327.1695 | 343.0495 | 316.6391 | 331.4847
623.6968 | 551.6968 | 476.1276 | 354.3125 | 326.3124 | 327.5419 | 343.3341 | 316.9117 | 331.8971
624.6983 | 552.6983 | 476.1887 | 354.5985 | 326.691 | 327.9051 | 343.67 | 317.1652 | 332.272
625.6897 | 553.6897 | 476.1619 | 354.8819 | 327.0706 | 328.2937 | 344.0167 | 317.4455 | 332.6361
626.6911 | 554.6911 | 476.2057 | 355.1701 | 327.439 | 328.6769 | 344.3275 | 317.6811 | 333.0511
627.6926 | 555.6926 | 476.2834 | 355.4522 | 327.8255 | 329.0485 | 344.6921 | 317.8733 | 333.428
628.694 | 556.694 | 476.4645 | 355.7374 | 328.206 | 329.4262 | 345.0274 | 318.0791 | 333.8249
629.6955 | 557.6955 | 476.5898 | 356.0284 | 328.5873 | 329.8071 | 345.3417 | 318.2901 | 334.2502
630.6969 | 558.6969 | 476.7286 | 356.3138 | 328.954 | 330.1838 | 345.6555 | 318.5172 | 334.619
631.6983 | 559.6983 | 476.5986 | 356.594 | 329.3342 | 330.5666 | 345.9726 | 318.7591 | 334.9952
632.6998 | 560.6998 | 476.5953 | 356.8846 | 329.6865 | 330.9467 | 346.3037 | 319.0034 | 335.3622
633.6912 | 561.6912 | 476.8768 | 357.1724 | 330.0494 | 331.3308 | 346.6023 | 319.2489 | 335.7746
634.6926 | 562.6926 | 477.0848 | 357.4678 | 330.4171 | 331.7251 | 346.9161 | 319.5082 | 336.1814
635.6941 | 563.6941 | 477.0685 | 357.7587 | 330.7932 | 332.0997 | 347.2026 | 319.7596 | 336.5654
636.6955 | 564.6955 | 477.0371 | 358.0456 | 331.1716 | 332.4719 | 347.508 | 319.963 | 336.8344
637.697 | 565.697 | 477.0017 | 358.3333 | 331.5446 | 332.8384 | 347.8068 | 320.229 | 336.6711
638.6984 | 566.6984 | 477.0237 | 358.6099 | 331.914 | 333.1961 | 348.1212 | 320.4806 | 336.533
639.6998 | 567.6998 | 476.9606 | 358.8953 | 332.2897 | 333.5489 | 348.4082 | 320.7366 | 336.3691
640.6913 | 568.6913 | 476.8044 | 359.1891 | 332.6645 | 333.8941 | 348.7211 | 320.9851 | 336.4958
641.6927 | 569.6927 | 476.6251 | 359.4651 | 333.0469 | 334.2552 | 349.0405 | 321.1999 | 336.6491
642.6941 | 570.6941 | 476.5752 | 359.7383 | 333.4178 | 334.6014 | 349.3503 | 321.4685 | 336.8375
643.6956 | 571.6956 | 476.5179 | 360.0081 | 333.7738 | 334.9667 | 349.6392 | 321.6959 | 337.5376
644.697 | 572.697 | 476.4692 | 360.2798 | 334.1575 | 335.3273 | 349.9274 | 321.9421 | 337.6724
645.6985 | 573.6985 | 476.6076 | 360.5561 | 334.5247 | 335.6933 | 350.2178 | 322.1884 | 338.367
646.6999 | 574.6999 | 476.5953 | 360.838 | 334.8818 | 336.0366 | 350.5225 | 322.4245 | 339.2597
647.6913 | 575.6913 | 476.6124 | 361.1156 | 335.2635 | 336.3869 | 350.8312 | 322.6631 | 339.9729
648.6928 | 576.6928 | 476.6361 | 361.3933 | 335.5998 | 336.738 | 351.1204 | 322.887 | 340.6566
649.6942 | 577.6942 | 476.7207 | 361.6618 | 335.9436 | 337.0813 | 351.4116 | 323.1186 | 340.8289
650.6957 | 578.6957 | 476.6071 | 361.9387 | 336.289 | 337.4344 | 351.6644 | 323.325 | 341.4493
651.6971 | 579.6971 | 476.4129 | 362.1968 | 336.6236 | 337.8013 | 351.9802 | 323.5301 | 342.1622
652.6985 | 580.6985 | 476.3495 | 362.4599 | 336.959 | 338.1549 | 352.2685 | 323.7493 | 342.8894
653.69 | 581.69 | 476.3391 | 362.729 | 337.2869 | 338.5167 | 352.5753 | 323.9371 | 343.3623
654.6914 | 582.6914 | 476.315 | 362.9849 | 337.6212 | 338.8781 | 352.8773 | 324.1309 | 344.0271
655.6928 | 583.6928 | 476.3019 | 363.2486 | 337.945 | 339.2383 | 353.1486 | 324.3402 | 343.6621
656.6943 | 584.6943 | 476.4208 | 363.4996 | 338.2807 | 339.6038 | 353.4296 | 324.5411 | 343.3355
657.6957 | 585.6957 | 476.5076 | 363.7629 | 338.6266 | 339.9564 | 353.7295 | 324.7702 | 343.8157
658.6972 | 586.6972 | 476.5342 | 364.015 | 338.9713 | 340.305 | 354.0274 | 325.0197 | 344.7789
659.6986 | 587.6986 | 476.4734 | 364.2819 | 339.3146 | 340.6557 | 354.3218 | 325.258 | 345.2959
660.69 | 588.69 | 476.3707 | 364.5413 | 339.6569 | 341.0118 | 354.5874 | 325.4874 | 344.6834
661.6915 | 589.6915 | 476.3899 | 364.8059 | 340.0187 | 341.3839 | 354.8749 | 325.7166 | 344.047
662.6929 | 590.6929 | 476.3759 | 365.0639 | 340.3756 | 341.7575 | 355.1781 | 325.958 | 343.7567
663.6943 | 591.6943 | 476.2911 | 365.3344 | 340.7292 | 342.0903 | 355.4749 | 326.1287 | 343.8274
664.6958 | 592.6958 | 476.2375 | 365.5942 | 341.0727 | 342.4283 | 355.743 | 326.3688 | 344.1864
665.6972 | 593.6972 | 476.1801 | 365.8548 | 341.4367 | 342.7669 | 356.0324 | 326.6198 | 344.4736
666.6987 | 594.6987 | 476.1676 | 366.1202 | 341.7859 | 343.1003 | 356.3073 | 326.8353 | 344.3719
667.7001 | 595.7001 | 476.1147 | 366.3836 | 342.1374 | 343.4187 | 356.5847 | 327.0871 | 344.5526
668.6915 | 596.6915 | 476.0886 | 366.6603 | 342.4895 | 343.7531 | 356.8823 | 327.3376 | 344.5599
669.693 | 597.693 | 476.0635 | 366.9423 | 342.829 | 344.0944 | 357.1806 | 327.5601 | 344.5291
670.6944 | 598.6944 | 475.9339 | 367.2354 | 343.1779 | 344.4538 | 357.4734 | 327.8025 | 344.4988
671.6959 | 599.6959 | 475.8702 | 367.5189 | 343.5191 | 344.8083 | 357.7596 | 327.9013 | 344.3397
672.6973 | 600.6973 | 475.8072 | 367.8111 | 343.8478 | 345.1611 | 358.0283 | 328.0865 | 344.2307
673.6887 | 601.6887 | 475.7856 | 368.0913 | 344.187 | 345.5176 | 358.2864 | 328.2524 | 344.2902
674.6902 | 602.6902 | 475.7989 | 368.3853 | 344.5233 | 345.8782 | 358.5649 | 328.3682 | 344.3
675.6916 | 603.6916 | 475.8486 | 368.6874 | 344.8618 | 346.21 | 358.8267 | 328.6085 | 344.499
676.693 | 604.693 | 475.8219 | 369.0013 | 345.1906 | 346.5611 | 359.0788 | 328.8095 | 344.632
677.6945 | 605.6945 | 475.8176 | 369.296 | 345.5183 | 346.9021 | 359.3255 | 329.0233 | 344.7367
678.6959 | 606.6959 | 475.7817 | 369.6103 | 345.8435 | 347.2507 | 359.5758 | 329.123 | 344.6518
679.6974 | 607.6974 | 475.7409 | 369.9163 | 346.1748 | 347.589 | 359.8279 | 329.3439 | 344.8678
680.6988 | 608.6988 | 475.6452 | 370.2359 | 346.4926 | 347.9095 | 360.0858 | 329.5849 | 345.1097
681.7002 | 609.7002 | 475.8066 | 370.5459 | 346.8261 | 348.2507 | 360.3324 | 329.7991 | 345.1191
682.6917 | 610.6917 | 475.8527 | 370.8722 | 347.1504 | 348.5865 | 360.5905 | 329.9803 | 345.1196
683.6931 | 611.6931 | 475.6866 | 371.1858 | 347.4651 | 348.9178 | 360.8368 | 330.1758 | 345.226
684.6945 | 612.6945 | 475.671 | 371.5055 | 347.8038 | 349.237 | 361.1109 | 330.2856 | 345.2182
685.696 | 613.696 | 475.6653 | 371.82 | 348.1371 | 349.5678 | 361.3685 | 330.4634 | 344.6185
686.6974 | 614.6974 | 475.5202 | 372.1377 | 348.4533 | 349.8951 | 361.6363 | 330.6667 | 344.1987
687.6989 | 615.6989 | 475.541 | 372.4595 | 348.7654 | 350.2355 | 361.8865 | 330.8535 | 344.1368
688.7003 | 616.7003 | 475.5389 | 372.7763 | 349.1008 | 350.5445 | 362.1385 | 331.0659 | 344.0208
689.6917 | 617.6917 | 475.5442 | 373.0893 | 349.4234 | 350.8681 | 362.3852 | 331.2572 | 343.9423
690.6932 | 618.6932 | 475.5305 | 373.4227 | 349.7455 | 351.1924 | 362.6187 | 331.4587 | 343.5806
691.6946 | 619.6946 | 475.5939 | 373.7359 | 350.0496 | 351.5103 | 362.8974 | 331.6307 | 343.2736
692.696 | 620.696 | 475.6625 | 374.0565 | 350.3693 | 351.8287 | 363.152 | 331.8614 | 342.4713
693.6975 | 621.6975 | 475.6346 | 374.3633 | 350.6769 | 352.1294 | 363.3749 | 332.0628 | 341.3073
694.6889 | 622.6889 | 475.6943 | 374.6184 | 351.0047 | 352.435 | 363.6311 | 332.248 | 340.451
695.6904 | 623.6904 | 475.7342 | 374.9391 | 351.3125 | 352.7347 | 363.8578 | 332.4905 | 340.425
696.6918 | 624.6918 | 475.8024 | 375.2632 | 351.6216 | 353.0435 | 364.1036 | 332.7244 | 341.2848
697.6932 | 625.6932 | 475.7247 | 375.507 | 351.9439 | 353.3635 | 364.3108 | 332.8974 | 341.8335
698.6947 | 626.6947 | 475.6849 | 375.7471 | 352.2532 | 353.6673 | 364.5469 | 333.1494 | 340.8585
699.6961 | 627.6961 | 475.6098 | 375.9718 | 352.5645 | 353.9601 | 364.8031 | 333.3928 | 341.2161
700.6976 | 628.6976 | 475.6228 | 376.1894 | 352.8941 | 354.2621 | 365.0426 | 333.5833 | 340.3139
701.699 | 629.699 | 475.5922 | 376.3975 | 353.2093 | 354.5574 | 365.3008 | 333.7836 | 341.3321
702.6904 | 630.6904 | 475.6009 | 376.6156 | 353.5142 | 354.8545 | 365.5733 | 333.9262 | 340.4627
703.6919 | 631.6919 | 475.4996 | 376.8542 | 353.8372 | 355.1249 | 365.8414 | 334.1435 | 340.1497
704.6933 | 632.6933 | 475.3831 | 377.0953 | 354.144 | 355.4037 | 366.0945 | 334.4008 | 340.6219
705.6947 | 633.6947 | 475.4392 | 377.3335 | 354.4538 | 355.6659 | 366.3483 | 334.5718 | 339.4698
706.6962 | 634.6962 | 475.3274 | 377.5679 | 354.7659 | 355.9261 | 366.5712 | 334.741 | 340.1261
707.6976 | 635.6976 | 475.2326 | 377.8052 | 355.0707 | 356.1844 | 366.8361 | 334.9477 | 340.2498
708.6991 | 636.6991 | 475.1504 | 378.0454 | 355.3839 | 356.4459 | 367.0734 | 335.0925 | 339.5327
709.7005 | 637.7005 | 475.2028 | 378.2866 | 355.6887 | 356.7134 | 367.321 | 335.2934 | 339.8513
710.6919 | 638.6919 | 475.4736 | 378.5222 | 355.9902 | 356.9809 | 367.5774 | 335.476 | 340.2711
711.6934 | 639.6934 | 475.4696 | 378.7463 | 356.2772 | 357.2528 | 367.8629 | 335.6488 | 340.7595
712.6948 | 640.6948 | 475.5732 | 378.9592 | 356.5821 | 357.5297 | 368.1298 | 335.9103 | 341.8692
713.6962 | 641.6962 | 475.7146 | 379.1823 | 356.8828 | 357.8168 | 368.4177 | 336.1051 | 341.67
714.6977 | 642.6977 | 475.7556 | 379.3973 | 357.1859 | 358.1012 | 368.6996 | 336.3279 | 341.6326
715.6891 | 643.6891 | 475.6471 | 379.6164 | 357.4765 | 358.3795 | 368.9746 | 336.5749 | 342.4578
716.6906 | 644.6906 | 475.5093 | 379.8448 | 357.7765 | 358.6657 | 369.242 | 336.6816 | 342.437
717.692 | 645.692 | 475.4393 | 380.0644 | 358.0778 | 358.9545 | 369.4856 | 336.8711 | 343.1698
718.6934 | 646.6934 | 475.5506 | 380.2844 | 358.3704 | 359.253 | 369.7672 | 337.0807 | 342.8077
719.6949 | 647.6949 | 475.6155 | 380.516 | 358.6623 | 359.5506 | 370.0227 | 337.2252 | 343.6282
720.6963 | 648.6963 | 475.6782 | 380.7244 | 358.9881 | 359.8427 | 370.2758 | 337.3356 | 344.4511
721.6978 | 649.6978 | 475.6973 | 380.9357 | 359.2768 | 360.145 | 370.5391 | 337.5503 | 345.2493
722.6892 | 650.6892 | 475.6327 | 381.1711 | 359.5753 | 360.4468 | 370.7504 | 337.8179 | 345.3095
723.7006 | 651.7006 | 475.6363 | 381.3913 | 359.8617 | 360.7389 | 370.9922 | 338.193 | 345.2676
724.6921 | 652.6921 | 475.689 | 381.6046 | 360.1378 | 361.0406 | 371.2226 | 338.3495 | 345.7544
725.6935 | 653.6935 | 475.8595 | 381.8116 | 360.4237 | 361.3391 | 371.4523 | 338.5178 | 345.7664
726.6949 | 654.6949 | 475.9463 | 382.0048 | 360.701 | 361.6413 | 371.7023 | 338.8091 | 345.9452
727.6964 | 655.6964 | 475.8537 | 382.2138 | 360.9564 | 361.9253 | 371.927 | 339.1088 | 346.7654
728.6978 | 656.6978 | 475.7415 | 382.4224 | 361.2363 | 362.2275 | 372.1443 | 339.2968 | 347.0468
729.6993 | 657.6993 | 475.7349 | 382.6093 | 361.5076 | 362.5183 | 372.374 | 339.4578 | 347.4361
730.6907 | 658.6907 | 475.7744 | 382.815 | 361.7466 | 362.8179 | 372.5874 | 339.6634 | 348.0094
731.6921 | 659.6921 | 475.7641 | 383.0223 | 361.996 | 363.1118 | 372.8059 | 339.8307 | 348.437
732.6936 | 660.6936 | 475.7957 | 383.2248 | 362.2454 | 363.4014 | 372.9734 | 340.0765 | 348.9277
733.695 | 661.695 | 475.9675 | 383.4316 | 362.5127 | 363.6832 | 373.1521 | 340.3503 | 348.8396
734.6964 | 662.6964 | 476.0141 | 383.6411 | 362.7767 | 363.9737 | 373.3315 | 340.593 | 348.6872
735.6979 | 663.6979 | 475.9523 | 383.8522 | 363.0506 | 364.2612 | 373.5158 | 340.8839 | 349.2247
736.6893 | 664.6893 | 476.0034 | 384.0388 | 363.3341 | 364.5372 | 373.6602 | 341.1163 | 349.8206
737.6907 | 665.6907 | 475.9632 | 384.211 | 363.6082 | 364.8138 | 373.8138 | 341.3477 | 350.2205
738.6922 | 666.6922 | 475.7841 | 384.4112 | 363.8891 | 365.1027 | 373.9758 | 341.527 | 350.3253
739.6936 | 667.6936 | 475.6973 | 384.607 | 364.1814 | 365.3775 | 374.1687 | 341.7252 | 350.8137
740.6951 | 668.6951 | 475.6383 | 384.78 | 364.4651 | 365.6399 | 374.3553 | 341.8975 | 351.4273
741.6965 | 669.6965 | 475.4788 | 384.9428 | 364.7517 | 365.9125 | 374.5674 | 342.1133 | 352.0133
742.6979 | 670.6979 | 475.3922 | 385.1105 | 365.0404 | 366.1909 | 374.7715 | 342.2568 | 352.4488
743.6894 | 671.6894 | 475.3949 | 385.2779 | 365.3219 | 366.4665 | 374.9704 | 342.3803 | 352.8826
744.6908 | 672.6908 | 475.4072 | 385.4562 | 365.608 | 366.7376 | 375.1558 | 342.5126 | 353.2872
745.6923 | 673.6923 | 475.3695 | 385.6261 | 365.8981 | 367.0236 | 375.3341 | 342.6594 | 353.8276
746.6937 | 674.6937 | 475.2484 | 385.7967 | 366.1887 | 367.291 | 375.5279 | 342.8176 | 353.3332
747.6951 | 675.6951 | 475.0609 | 385.9571 | 366.4626 | 367.5568 | 375.6963 | 343.0057 | 353.4141
748.6966 | 676.6966 | 475.0688 | 386.1251 | 366.7456 | 367.827 | 375.8769 | 343.192 | 354.0245
749.698 | 677.698 | 475.0268 | 386.2925 | 367.0298 | 368.1053 | 376.039 | 343.329 | 353.9288
750.6894 | 678.6894 | 474.9177 | 386.4606 | 367.3059 | 368.3798 | 376.1928 | 343.5141 | 354.3361
751.6909 | 679.6909 | 475.0426 | 386.6303 | 367.5819 | 368.6371 | 376.3634 | 343.6721 | 354.2916
752.6923 | 680.6923 | 475.2468 | 386.7976 | 367.8579 | 368.9076 | 376.5181 | 343.8054 | 354.8132
753.6938 | 681.6938 | 475.2039 | 386.9699 | 368.1399 | 369.1655 | 376.6491 | 343.9624 | 355.379
754.6952 | 682.6952 | 475.1289 | 387.1472 | 368.4146 | 369.432 | 376.8107 | 344.1725 | 355.0349
755.6966 | 683.6966 | 475.0466 | 387.3197 | 368.6907 | 369.6926 | 376.9537 | 344.3176 | 355.4079
756.6981 | 684.6981 | 475.2029 | 387.4933 | 368.9561 | 369.9573 | 377.0929 | 344.4848 | 355.6335
757.6995 | 685.6995 | 475.3065 | 387.6734 | 369.2371 | 370.2137 | 377.2277 | 344.6728 | 355.7997
758.6909 | 686.6909 | 475.4046 | 387.8485 | 369.507 | 370.4824 | 377.3684 | 344.8531 | 356.1364
759.6924 | 687.6924 | 475.5271 | 388.0191 | 369.7682 | 370.7405 | 377.5309 | 345.0328 | 356.1081
760.6938 | 688.6938 | 475.465 | 388.2043 | 370.0464 | 370.9862 | 377.6838 | 345.2128 | 356.2776
761.6953 | 689.6953 | 475.4022 | 388.4213 | 370.3084 | 371.1875 | 377.8406 | 345.3749 | 356.175
762.6967 | 690.6967 | 475.3233 | 388.6193 | 370.5644 | 371.4215 | 378.0221 | 345.5068 | 356.7526
763.6981 | 691.6981 | 475.3929 | 388.8477 | 370.7812 | 371.6503 | 378.1806 | 345.6537 | 356.5697
764.6996 | 692.6996 | 475.3874 | 389.083 | 371.0161 | 371.8962 | 378.3639 | 345.813 | 356.8607
765.701 | 693.701 | 475.4791 | 389.3318 | 371.2373 | 372.1392 | 378.5352 | 346.027 | 357.3695
766.6924 | 694.6924 | 475.4554 | 389.5833 | 371.4732 | 372.3814 | 378.7225 | 346.2306 | 357.7455
767.8241 | 695.8241 | 475.5103 | 389.8469 | 371.7407 | 372.645 | 378.9153 | 346.4458 | 357.978
768.6953 | 696.6953 | 475.5474 | 390.0503 | 371.9507 | 372.8543 | 379.0697 | 346.5856 | 358.1512
769.6968 | 697.6968 | 475.508 | 390.2836 | 372.1971 | 373.0959 | 379.2434 | 346.7639 | 358.2662
770.6982 | 698.6982 | 475.4068 | 390.5194 | 372.4238 | 373.341 | 379.4162 | 346.9069 | 358.4399
771.6996 | 699.6996 | 475.4615 | 390.7348 | 372.6626 | 373.592 | 379.5982 | 347.0811 | 358.5791
772.6911 | 700.6911 | 475.5642 | 390.9728 | 372.9059 | 373.8496 | 379.7734 | 347.2414 | 358.9626
773.6925 | 701.6925 | 475.6416 | 391.205 | 373.1177 | 374.1031 | 379.9315 | 347.4121 | 359.3892
774.694 | 702.694 | 475.6407 | 391.4363 | 373.3277 | 374.3564 | 380.1108 | 347.6311 | 359.4227
775.6954 | 703.6954 | 475.6466 | 391.6706 | 373.5565 | 374.5991 | 380.2768 | 347.8321 | 359.2923
776.6968 | 704.6968 | 475.6319 | 391.8983 | 373.7652 | 374.8483 | 380.4272 | 348.0018 | 359.5543
777.6983 | 705.6983 | 475.6098 | 392.1317 | 373.9714 | 375.0953 | 380.5916 | 348.1885 | 359.8663
778.6897 | 706.6897 | 475.7102 | 392.3696 | 374.1653 | 375.3203 | 380.7423 | 348.3642 | 360.1427
779.6911 | 707.6911 | 475.9531 | 392.6236 | 374.3429 | 375.5505 | 380.8981 | 348.5319 | 360.4113
780.6926 | 708.6926 | 476.0403 | 392.8579 | 374.5466 | 375.7716 | 381.0556 | 348.7227 | 360.7263
781.694 | 709.694 | 476.0784 | 393.1155 | 374.7377 | 375.9872 | 381.1938 | 348.8921 | 360.8995
782.6955 | 710.6955 | 476.147 | 393.3746 | 374.9254 | 376.2073 | 381.3548 | 348.9736 | 361.2291
783.6969 | 711.6969 | 476.3259 | 393.6137 | 375.1088 | 376.4194 | 381.4949 | 349.207 | 361.4903
784.6983 | 712.6983 | 476.521 | 393.8606 | 375.2796 | 376.6331 | 381.6496 | 349.3707 | 361.7341
785.6898 | 713.6898 | 476.6112 | 394.1039 | 375.4481 | 376.8306 | 381.7936 | 349.5361 | 361.9882
786.6912 | 714.6912 | 476.6731 | 394.3422 | 375.6093 | 377.0383 | 381.9458 | 349.7104 | 362.1928
787.6926 | 715.6926 | 476.6349 | 394.584 | 375.7863 | 377.2356 | 382.0855 | 349.8725 | 362.3361
788.6941 | 716.6941 | 476.6518 | 394.8348 | 375.9403 | 377.4359 | 382.2169 | 350.0624 | 362.4472
789.6955 | 717.6955 | 476.4631 | 395.0895 | 376.091 | 377.6124 | 382.3577 | 350.2227 | 362.5056
790.697 | 718.697 | 476.24 | 395.3537 | 376.2379 | 377.7837 | 382.4998 | 350.3011 | 362.4657
791.6984 | 719.6984 | 476.1194 | 395.6004 | 376.3845 | 377.9607 | 382.6487 | 350.4962 | 362.5624
792.6898 | 720.6898 | 475.9908 | 395.8582 | 376.5304 | 378.1233 | 382.7847 | 350.7198 | 362.6644
793.6913 | 721.6913 | 475.9617 | 396.1015 | 376.6801 | 378.2869 | 382.9558 | 350.9064 | 362.7469
794.6927 | 722.6927 | 475.9567 | 396.3366 | 376.8183 | 378.4513 | 383.1037 | 351.0533 | 362.8597
795.6942 | 723.6942 | 475.9919 | 396.5823 | 376.952 | 378.6184 | 383.2575 | 351.2039 | 362.968
796.6956 | 724.6956 | 475.9654 | 396.8194 | 377.091 | 378.7684 | 383.4029 | 351.3431 | 363.0847
797.697 | 725.697 | 475.932 | 397.0599 | 377.2316 | 378.9179 | 383.5499 | 351.4903 | 363.1638
798.6985 | 726.6985 | 475.9283 | 397.3116 | 377.3599 | 379.0663 | 383.6868 | 351.6598 | 363.2539
799.6999 | 727.6999 | 475.9175 | 397.5561 | 377.4976 | 379.2105 | 383.8226 | 351.7989 | 363.3223
800.6913 | 728.6913 | 475.9953 | 397.798 | 377.6268 | 379.3526 | 383.9674 | 351.9576 | 363.4135
801.6928 | 729.6928 | 475.9927 | 398.0358 | 377.7527 | 379.4925 | 384.0986 | 352.1367 | 363.606
802.6942 | 730.6942 | 475.9182 | 398.2809 | 377.8601 | 379.6287 | 384.2358 | 352.321 | 363.7431
803.6957 | 731.6957 | 475.8103 | 398.5274 | 377.9913 | 379.7746 | 384.3598 | 352.5159 | 363.898
804.6971 | 732.6971 | 475.9127 | 398.7792 | 378.1022 | 379.9068 | 384.5044 | 352.6705 | 364.0614
805.6985 | 733.6985 | 475.9766 | 399.0214 | 378.2103 | 380.0433 | 384.6567 | 352.8481 | 364.224
806.69 | 734.69 | 475.9346 | 399.264 | 378.3302 | 380.1855 | 384.7989 | 353.0022 | 364.3793
807.6914 | 735.6914 | 475.9461 | 399.4973 | 378.4469 | 380.3142 | 384.9532 | 353.1596 | 364.5721
808.6928 | 736.6928 | 475.9131 | 399.7517 | 378.56 | 380.4415 | 385.1049 | 353.3354 | 364.7122
809.6943 | 737.6943 | 475.834 | 399.9894 | 378.653 | 380.5757 | 385.2515 | 353.5004 | 364.8174
810.6957 | 738.6957 | 475.7382 | 400.2273 | 378.7564 | 380.705 | 385.4098 | 353.649 | 364.9387
811.6972 | 739.6972 | 475.6826 | 400.4626 | 378.8623 | 380.8257 | 385.5661 | 353.7787 | 365.1162
812.6986 | 740.6986 | 475.5688 | 400.6963 | 378.9632 | 380.9582 | 385.7209 | 353.9192 | 365.3498
813.7 | 741.7 | 475.4592 | 400.9317 | 379.0606 | 381.0876 | 385.8776 | 354.0482 | 365.6094
814.6915 | 742.6915 | 475.3966 | 401.1551 | 379.1531 | 381.2174 | 386.0302 | 354.1824 | 365.6832
815.6929 | 743.6929 | 475.3353 | 401.3788 | 379.2476 | 381.3511 | 386.1907 | 354.3224 | 365.8006
816.6943 | 744.6943 | 475.155 | 401.6124 | 379.3382 | 381.4789 | 386.3383 | 354.4757 | 365.9825
817.6958 | 745.6958 | 475.0181 | 401.8489 | 379.4289 | 381.6079 | 386.4834 | 354.6393 | 366.141
818.6972 | 746.6972 | 474.9755 | 402.0784 | 379.5267 | 381.7296 | 386.6383 | 354.7913 | 366.3034
819.6987 | 747.6987 | 474.9547 | 402.3151 | 379.6221 | 381.8576 | 386.776 | 354.9641 | 366.4517
820.7001 | 748.7001 | 475.0159 | 402.5383 | 379.7056 | 381.9874 | 386.9338 | 355.0866 | 366.5778
821.6915 | 749.6915 | 475.0781 | 402.7619 | 379.7859 | 382.1078 | 387.0781 | 355.2866 | 366.7216
822.693 | 750.693 | 475.0969 | 402.9708 | 379.8754 | 382.2326 | 387.2196 | 355.4769 | 366.8365
823.6944 | 751.6944 | 475.0999 | 403.1932 | 379.9495 | 382.3631 | 387.3595 | 355.6677 | 366.955
824.6959 | 752.6959 | 475.0894 | 403.4081 | 380.0304 | 382.4904 | 387.4923 | 355.8382 | 367.1448
825.6973 | 753.6973 | 475.1178 | 403.6017 | 380.0991 | 382.6117 | 387.6182 | 355.9811 | 367.3383
826.6987 | 754.6987 | 475.0396 | 403.8088 | 380.1812 | 382.7395 | 387.757 | 356.134 | 367.4785
827.6902 | 755.6902 | 474.9555 | 404.0034 | 380.2606 | 382.8631 | 387.8788 | 356.2736 | 367.6295
828.6916 | 756.6916 | 474.8316 | 404.1936 | 380.331 | 382.9889 | 388.0044 | 356.4177 | 367.7695
829.693 | 757.693 | 474.7465 | 404.3945 | 380.415 | 383.114 | 388.136 | 356.5855 | 367.9324
830.6945 | 758.6945 | 474.8047 | 404.5888 | 380.4859 | 383.2342 | 388.2561 | 356.7498 | 368.0765
831.6959 | 759.6959 | 474.9349 | 404.7751 | 380.565 | 383.3584 | 388.3694 | 356.9202 | 368.2105
832.6974 | 760.6974 | 474.8821 | 404.9534 | 380.6427 | 383.4766 | 388.4938 | 357.0791 | 368.3624
833.6988 | 761.6988 | 474.8563 | 405.1452 | 380.7123 | 383.5987 | 388.6155 | 357.2493 | 368.4822
834.6902 | 762.6902 | 474.8048 | 405.3183 | 380.7958 | 383.7155 | 388.7374 | 357.3915 | 368.6101
835.6917 | 763.6917 | 474.8462 | 405.4927 | 380.8676 | 383.8438 | 388.846 | 357.548 | 368.725
836.6931 | 764.6931 | 474.8077 | 405.6742 | 380.9506 | 383.9611 | 388.959 | 357.7064 | 368.9227
837.6945 | 765.6945 | 474.7582 | 405.8524 | 381.0402 | 384.086 | 389.0751 | 357.867 | 369.0949
838.696 | 766.696 | 474.8217 | 406.0255 | 381.1247 | 384.2064 | 389.1972 | 358.0285 | 369.2389
839.6974 | 767.6974 | 474.757 | 406.1957 | 381.2061 | 384.335 | 389.3087 | 358.1747 | 369.3973
840.6989 | 768.6989 | 474.734 | 406.3551 | 381.292 | 384.4538 | 389.4196 | 358.3389 | 369.5555
841.7003 | 769.7003 | 474.7261 | 406.5169 | 381.3761 | 384.5748 | 389.5193 | 358.4908 | 369.6904
842.6917 | 770.6917 | 474.885 | 406.68 | 381.4476 | 384.6967 | 389.6434 | 358.6409 | 369.8394
843.6932 | 771.6932 | 474.9688 | 406.8421 | 381.5343 | 384.8171 | 389.738 | 358.7624 | 369.9982
844.6946 | 772.6946 | 475.0634 | 407.015 | 381.617 | 384.9368 | 389.8503 | 358.8925 | 370.1755
845.6961 | 773.6961 | 475.1315 | 407.1721 | 381.7039 | 385.0637 | 389.9438 | 359.0196 | 370.3433
846.6975 | 774.6975 | 475.1914 | 407.3332 | 381.7868 | 385.1866 | 390.0411 | 359.1375 | 370.5307
847.6889 | 775.6889 | 475.2765 | 407.4992 | 381.8887 | 385.3057 | 390.1526 | 359.2611 | 370.7333
848.6904 | 776.6904 | 475.2894 | 407.6689 | 381.9687 | 385.4271 | 390.2474 | 359.438 | 370.9365
849.6918 | 777.6918 | 475.1997 | 407.8338 | 382.0623 | 385.5487 | 390.3444 | 359.6027 | 371.1246
850.6932 | 778.6932 | 475.1177 | 407.9967 | 382.1486 | 385.6776 | 390.4576 | 359.8173 | 371.2919
851.6947 | 779.6947 | 475.0665 | 408.1705 | 382.2293 | 385.8022 | 390.5483 | 360.0008 | 371.4108
852.6961 | 780.6961 | 475.1401 | 408.3399 | 382.3215 | 385.9259 | 390.6589 | 360.1781 | 371.435
853.6976 | 781.6976 | 475.0815 | 408.493 | 382.42 | 386.0535 | 390.7538 | 360.3456 | 371.4002
854.699 | 782.699 | 475.0187 | 408.6616 | 382.5041 | 386.1729 | 390.853 | 360.5171 | 371.3644
855.7004 | 783.7004 | 475.1064 | 408.8191 | 382.5941 | 386.2948 | 390.9504 | 360.682 | 371.3769
856.6919 | 784.6919 | 475.2847 | 408.9786 | 382.6908 | 386.4087 | 391.0528 | 360.8446 | 371.4036
857.6933 | 785.6933 | 475.3344 | 409.1274 | 382.7862 | 386.5345 | 391.1493 | 361.0202 | 371.4403
858.6947 | 786.6947 | 475.2507 | 409.2875 | 382.8697 | 386.6565 | 391.2434 | 361.1861 | 371.4906
859.6962 | 787.6962 | 475.1617 | 409.4456 | 382.9649 | 386.787 | 391.3242 | 361.3454 | 371.5641
860.6976 | 788.6976 | 475.2255 | 409.5979 | 383.0567 | 386.9057 | 391.4067 | 361.4861 | 371.6331
861.6991 | 789.6991 | 475.2694 | 409.7385 | 383.1408 | 387.0281 | 391.4928 | 361.6166 | 371.7356
862.7005 | 790.7005 | 475.2907 | 409.8773 | 383.2254 | 387.1542 | 391.5675 | 361.7178 | 371.8232
863.6919 | 791.6919 | 475.3081 | 410.0149 | 383.3079 | 387.2759 | 391.6458 | 361.9171 | 371.9217
864.6934 | 792.6934 | 475.2927 | 410.1476 | 383.3997 | 387.4029 | 391.7157 | 362.1044 | 371.9921
865.6948 | 793.6948 | 475.3474 | 410.273 | 383.4924 | 387.5182 | 391.7995 | 362.2698 | 372.0384
866.6962 | 794.6962 | 475.4636 | 410.4024 | 383.5737 | 387.6389 | 391.8797 | 362.4293 | 372.0889
867.6977 | 795.6977 | 475.6447 | 410.5239 | 383.6738 | 387.7613 | 391.96 | 362.5976 | 372.1722
868.6891 | 796.6891 | 475.6385 | 410.6654 | 383.7721 | 387.8875 | 392.043 | 362.7728 | 372.2634
869.6906 | 797.6906 | 475.6941 | 410.7996 | 383.8558 | 388.0114 | 392.1309 | 362.9151 | 372.3683
870.692 | 798.692 | 475.6701 | 410.9249 | 383.953 | 388.1337 | 392.211 | 363.051 | 372.4834
871.6934 | 799.6934 | 475.6095 | 411.0509 | 384.0446 | 388.2598 | 392.2913 | 363.1898 | 372.5832
872.6949 | 800.6949 | 475.5918 | 411.1805 | 384.143 | 388.3847 | 392.3778 | 363.3508 | 372.702
873.6963 | 801.6963 | 475.4682 | 411.3041 | 384.2391 | 388.5081 | 392.4697 | 363.5099 | 372.818
874.6978 | 802.6978 | 475.441 | 411.4299 | 384.336 | 388.6344 | 392.5526 | 363.6675 | 372.9398
875.6892 | 803.6892 | 475.4541 | 411.5578 | 384.4359 | 388.7642 | 392.6357 | 363.7709 | 373.0421
876.6906 | 804.6906 | 475.4523 | 411.6856 | 384.5322 | 388.8839 | 392.7268 | 363.8933 | 373.1635
877.6921 | 805.6921 | 475.4526 | 411.8171 | 384.6253 | 389.0064 | 392.8247 | 364.0182 | 373.3082
878.6935 | 806.6935 | 475.4933 | 411.9229 | 384.7269 | 389.1321 | 392.9033 | 364.1513 | 373.4551
879.6949 | 807.6949 | 475.6114 | 412.0434 | 384.8242 | 389.2552 | 392.9873 | 364.3085 | 373.6063
880.6964 | 808.6964 | 475.6781 | 412.1517 | 384.9094 | 389.3765 | 393.0731 | 364.4803 | 373.7563
881.6978 | 809.6978 | 475.7211 | 412.2611 | 385.0087 | 389.4941 | 393.1632 | 364.6419 | 373.9113
882.6993 | 810.6993 | 475.8529 | 412.3725 | 385.0977 | 389.6162 | 393.2539 | 364.7673 | 374.0707
883.6907 | 811.6907 | 475.9381 | 412.4868 | 385.1862 | 389.7397 | 393.3529 | 364.9147 | 374.2012
884.6921 | 812.6921 | 475.9643 | 412.589 | 385.2788 | 389.8614 | 393.446 | 365.0502 | 374.3724
885.6936 | 813.6936 | 476.0414 | 412.6768 | 385.3617 | 389.9898 | 393.5537 | 365.1668 | 374.5093
886.695 | 814.695 | 476.1363 | 412.7834 | 385.4629 | 390.1076 | 393.6344 | 365.3162 | 374.4421
887.6964 | 815.6964 | 476.1707 | 412.8911 | 385.5392 | 390.2332 | 393.7212 | 365.4094 | 374.4504
888.6979 | 816.6979 | 476.1388 | 413.0097 | 385.6582 | 390.3543 | 393.8046 | 365.5099 | 374.7868
889.6893 | 817.6893 | 476.1253 | 413.1173 | 385.7479 | 390.48 | 393.8886 | 365.6278 | 374.9954
890.6908 | 818.6908 | 476.2888 | 413.2259 | 385.8382 | 390.6078 | 393.9713 | 365.7679 | 375.16
891.6922 | 819.6922 | 476.4147 | 413.3367 | 385.9524 | 390.7312 | 394.0523 | 365.9185 | 375.3229
892.6936 | 820.6936 | 476.4744 | 413.4519 | 386.0463 | 390.8517 | 394.1155 | 366.0723 | 375.4652
893.6951 | 821.6951 | 476.503 | 413.5628 | 386.1488 | 390.9705 | 394.1941 | 366.2333 | 375.6137
894.6965 | 822.6965 | 476.4972 | 413.6687 | 386.2494 | 391.1011 | 394.2658 | 366.3634 | 375.7765
895.698 | 823.698 | 476.5844 | 413.7985 | 386.3596 | 391.2182 | 394.3227 | 366.5169 | 375.9307
896.6994 | 824.6994 | 476.5445 | 413.9064 | 386.4442 | 391.3388 | 394.3984 | 366.6328 | 376.0912
897.7008 | 825.7008 | 476.4977 | 414.0263 | 386.5448 | 391.4605 | 394.4633 | 366.7191 | 376.2395
898.6923 | 826.6923 | 476.512 | 414.1338 | 386.6458 | 391.5847 | 394.5514 | 366.774 | 376.3966
899.6937 | 827.6937 | 476.5709 | 414.2382 | 386.7354 | 391.7124 | 394.6269 | 366.8035 | 376.5279
900.6951 | 828.6951 | 476.6199 | 414.358 | 386.8338 | 391.841 | 394.7096 | 366.9011 | 376.6571
901.6966 | 829.6966 | 476.7763 | 414.4623 | 386.9377 | 391.9491 | 394.7842 | 366.8849 | 376.8185
902.698 | 830.698 | 476.6572 | 414.5622 | 387.037 | 392.0807 | 394.8654 | 366.9219 | 376.9671
903.6995 | 831.6995 | 476.6103 | 414.6749 | 387.1348 | 392.1999 | 394.9409 | 367.0752 | 377.1179
904.7009 | 832.7009 | 476.5339 | 414.7886 | 387.243 | 392.3195 | 395.0281 | 367.2184 | 377.2647
905.6923 | 833.6923 | 476.4821 | 414.8675 | 387.3472 | 392.4449 | 395.124 | 367.4142 | 377.4008
906.6938 | 834.6938 | 476.6497 | 414.9682 | 387.4508 | 392.5722 | 395.2198 | 367.574 | 377.5359
907.6952 | 835.6952 | 476.65 | 415.0507 | 387.5599 | 392.6858 | 395.3089 | 367.7279 | 377.6578
908.6966 | 836.6966 | 476.526 | 415.1351 | 387.6631 | 392.8134 | 395.4142 | 367.8611 | 377.7816
909.6981 | 837.6981 | 476.3311 | 415.212 | 387.7608 | 392.9351 | 395.5094 | 368.0172 | 377.9016
910.6895 | 838.6895 | 476.2863 | 415.2904 | 387.8796 | 393.0587 | 395.6118 | 368.1566 | 378.0158
911.6909 | 839.6909 | 476.1782 | 415.3705 | 387.9841 | 393.1729 | 395.7005 | 368.2385 | 378.1322
912.6924 | 840.6924 | 476.1517 | 415.4558 | 388.0852 | 393.3032 | 395.7956 | 368.3468 | 378.24
913.6938 | 841.6938 | 476.0924 | 415.5381 | 388.1939 | 393.4209 | 395.8946 | 368.4022 | 378.3484
914.6953 | 842.6953 | 475.9904 | 415.6177 | 388.2997 | 393.5442 | 395.9935 | 368.5057 | 378.4369
915.6967 | 843.6967 | 475.8809 | 415.6908 | 388.4026 | 393.6699 | 396.0834 | 368.6237 | 378.5433
916.6981 | 844.6981 | 475.9729 | 415.7697 | 388.5118 | 393.7932 | 396.1776 | 368.7288 | 378.6322
917.6996 | 845.6996 | 476.0563 | 415.8532 | 388.6255 | 393.9168 | 396.279 | 368.8345 | 378.7532
918.691 | 846.691 | 476.2046 | 415.9141 | 388.7242 | 394.0383 | 396.3794 | 368.9458 | 378.7697
919.6925 | 847.6925 | 476.3255 | 415.9961 | 388.8513 | 394.1535 | 396.474 | 369.0661 | 378.7977
920.6939 | 848.6939 | 476.2047 | 416.0867 | 388.9595 | 394.2793 | 396.5637 | 369.1467 | 378.8809
921.6953 | 849.6953 | 475.9995 | 416.1747 | 389.0789 | 394.4042 | 396.6533 | 369.202 | 379.0077
922.6968 | 850.6968 | 475.9222 | 416.2726 | 389.1974 | 394.5321 | 396.7488 | 369.3122 | 379.1896
923.6982 | 851.6982 | 475.8431 | 416.3582 | 389.307 | 394.65 | 396.8532 | 369.4177 | 379.3251
924.6896 | 852.6896 | 475.8721 | 416.4342 | 389.4212 | 394.7763 | 396.9446 | 369.5018 | 379.4413
925.6911 | 853.6911 | 475.9856 | 416.5364 | 389.5159 | 394.9042 | 397.039 | 369.637 | 379.6005
926.6925 | 854.6925 | 475.9624 | 416.6172 | 389.6442 | 395.0276 | 397.1359 | 369.7544 | 379.7543
927.694 | 855.694 | 475.9786 | 416.7025 | 389.7521 | 395.1524 | 397.2135 | 369.8626 | 379.9064
928.6954 | 856.6954 | 476.0671 | 416.7944 | 389.8829 | 395.2824 | 397.3161 | 369.965 | 380.0632
929.6968 | 857.6968 | 476.1071 | 416.8663 | 389.9982 | 395.3957 | 397.4098 | 370.0143 | 380.2149
930.6983 | 858.6983 | 476.1034 | 416.9405 | 390.1213 | 395.5253 | 397.4995 | 370.1069 | 380.3681
931.6897 | 859.6897 | 476.1798 | 417.0287 | 390.2344 | 395.6442 | 397.5896 | 370.1751 | 380.5158
932.6911 | 860.6911 | 476.1382 | 417.1064 | 390.3511 | 395.7663 | 397.6804 | 370.245 | 380.656
933.6926 | 861.6926 | 476.1803 | 417.1835 | 390.4655 | 395.8896 | 397.7727 | 370.2932 | 380.8009
934.694 | 862.694 | 476.2483 | 417.2486 | 390.5802 | 396.0166 | 397.8664 | 370.3605 | 380.9523
935.6955 | 863.6955 | 476.3784 | 417.327 | 390.6984 | 396.1381 | 397.9718 | 370.4479 | 381.1021
936.6969 | 864.6969 | 476.4137 | 417.4082 | 390.8309 | 396.263 | 398.0722 | 370.5279 | 381.2468
937.6983 | 865.6983 | 476.2938 | 417.4599 | 390.9541 | 396.3902 | 398.1602 | 370.5999 | 381.3788
938.6898 | 866.6898 | 476.3095 | 417.541 | 391.0668 | 396.5153 | 398.2543 | 370.6674 | 381.4894
939.6912 | 867.6912 | 476.2351 | 417.6134 | 391.1987 | 396.6445 | 398.3488 | 370.7033 | 381.5892
940.6926 | 868.6926 | 476.2634 | 417.6726 | 391.3138 | 396.7672 | 398.4491 | 370.7518 | 381.6739
941.6941 | 869.6941 | 476.3825 | 417.7477 | 391.4495 | 396.8949 | 398.5473 | 370.8048 | 381.7689
942.6955 | 870.6955 | 476.3428 | 417.8389 | 391.5654 | 397.0259 | 398.6299 | 370.8676 | 381.8676
943.697 | 871.697 | 476.2476 | 417.9163 | 391.6905 | 397.1522 | 398.7302 | 370.9285 | 381.9697
944.6984 | 872.6984 | 475.9417 | 417.9921 | 391.8138 | 397.2853 | 398.8117 | 370.9718 | 382.09
945.6998 | 873.6998 | 475.692 | 418.0676 | 391.9353 | 397.4056 | 398.8923 | 371.0492 | 382.1994
946.6913 | 874.6913 | 475.4566 | 418.1356 | 392.0613 | 397.541 | 398.9779 | 371.1204 | 382.3301
947.7027 | 875.7027 | 475.4172 | 418.1859 | 392.1954 | 397.665 | 399.0621 | 371.2126 | 382.4537
948.6942 | 876.6942 | 475.4403 | 418.2477 | 392.3104 | 397.7953 | 399.1442 | 371.3012 | 382.5689
949.6956 | 877.6956 | 475.4572 | 418.3013 | 392.4426 | 397.9255 | 399.2348 | 371.3916 | 382.7003
950.697 | 878.697 | 475.3929 | 418.3486 | 392.571 | 398.0597 | 399.3048 | 371.4804 | 382.828
951.6985 | 879.6985 | 475.3636 | 418.3959 | 392.6891 | 398.18 | 399.3961 | 371.5821 | 382.947
952.6899 | 880.6899 | 475.2875 | 418.4481 | 392.8147 | 398.3193 | 399.4919 | 371.7053 | 383.0713
953.6913 | 881.6913 | 475.6041 | 418.4927 | 392.9459 | 398.4513 | 399.5818 | 371.8272 | 383.2025
954.6928 | 882.6928 | 475.9047 | 418.5517 | 393.0857 | 398.5876 | 399.6717 | 371.9005 | 383.3215
955.6942 | 883.6942 | 475.9096 | 418.6041 | 393.2216 | 398.7147 | 399.7726 | 371.9346 | 383.443
956.6957 | 884.6957 | 475.886 | 418.6511 | 393.357 | 398.8478 | 399.8538 | 371.9808 | 383.5621
957.6971 | 885.6971 | 475.8236 | 418.6976 | 393.4916 | 398.9906 | 399.9369 | 372.0271 | 383.6962
958.6985 | 886.6985 | 475.7298 | 418.7391 | 393.6284 | 399.123 | 400.0289 | 372.0815 | 383.8237
959.69 | 887.69 | 475.7665 | 418.8012 | 393.7519 | 399.2661 | 400.1022 | 372.1558 | 383.9579
960.6914 | 888.6914 | 475.8899 | 418.8572 | 393.8933 | 399.4039 | 400.1926 | 372.1989 | 384.0807
961.6928 | 889.6928 | 475.9221 | 418.905 | 394.0162 | 399.5452 | 400.271 | 372.2768 | 384.2051
962.6943 | 890.6943 | 475.8084 | 418.9713 | 394.1483 | 399.6743 | 400.3458 | 372.3199 | 384.342
963.6957 | 891.6957 | 475.5599 | 419.0475 | 394.2861 | 399.8145 | 400.4184 | 372.4142 | 384.4641
964.6972 | 892.6972 | 475.5289 | 419.1405 | 394.4372 | 399.9582 | 400.4805 | 372.485 | 384.5898
965.6986 | 893.6986 | 475.4499 | 419.2267 | 394.5652 | 400.0956 | 400.5453 | 372.5632 | 384.7139
966.69 | 894.69 | 475.4012 | 419.3053 | 394.7023 | 400.2319 | 400.6192 | 372.6163 | 384.8272
967.6915 | 895.6915 | 475.3025 | 419.3945 | 394.8434 | 400.3677 | 400.6951 | 372.6696 | 384.9399
968.6929 | 896.6929 | 475.4581 | 419.4752 | 394.9817 | 400.502 | 400.772 | 372.752 | 385.0404
969.6944 | 897.6944 | 475.5208 | 419.5856 | 395.1175 | 400.6372 | 400.8391 | 372.7957 | 385.1399
970.6958 | 898.6958 | 475.5676 | 419.6747 | 395.2564 | 400.7645 | 400.9097 | 372.8808 | 385.2532
971.6972 | 899.6972 | 475.5636 | 419.7586 | 395.3864 | 400.9034 | 400.9902 | 372.9563 | 385.3733
972.6987 | 900.6987 | 475.6472 | 419.8482 | 395.5307 | 401.0392 | 401.0586 | 373.0121 | 385.4884
973.6901 | 901.6901 | 475.5689 | 419.9296 | 395.6595 | 401.1702 | 401.13 | 373.0583 | 385.6179
974.6915 | 902.6915 | 475.6022 | 420.0174 | 395.7845 | 401.3061 | 401.218 | 373.1108 | 385.7486
975.693 | 903.693 | 475.6607 | 420.0866 | 395.9159 | 401.4451 | 401.2962 | 373.1551 | 385.8751
976.7044 | 904.7044 | 475.4601 | 420.1721 | 396.0355 | 401.5811 | 401.3822 | 373.1691 | 385.9951
977.6959 | 905.6959 | 475.3685 | 420.2688 | 396.1639 | 401.71 | 401.4496 | 373.2207 | 386.105
978.6973 | 906.6973 | 475.3867 | 420.3618 | 396.2979 | 401.8434 | 401.5376 | 373.2513 | 386.2284
979.6987 | 907.6987 | 475.4459 | 420.4586 | 396.4265 | 401.9792 | 401.6058 | 373.2932 | 386.3425
980.6902 | 908.6902 | 475.3707 | 420.5383 | 396.5627 | 402.1082 | 401.6777 | 373.3559 | 386.4596
981.6916 | 909.6916 | 475.3927 | 420.6234 | 396.7013 | 402.234 | 401.7553 | 373.4189 | 386.5666
982.693 | 910.693 | 475.2831 | 420.7245 | 396.8274 | 402.3644 | 401.8265 | 373.4781 | 386.6681
983.6945 | 911.6945 | 475.4336 | 420.8361 | 396.9573 | 402.4966 | 401.8961 | 373.5417 | 386.7726
984.6959 | 912.6959 | 475.4382 | 420.9384 | 397.1032 | 402.6201 | 401.9484 | 373.6428 | 386.8806
985.6974 | 913.6974 | 475.451 | 421.0223 | 397.2253 | 402.7555 | 402.0305 | 373.6846 | 386.9664
986.6988 | 914.6988 | 475.6143 | 421.1198 | 397.3476 | 402.8854 | 402.1046 | 373.7472 | 387.025
987.7002 | 915.7002 | 475.7977 | 421.2138 | 397.4775 | 403.0276 | 402.1684 | 373.8207 | 387.094
988.6917 | 916.6917 | 475.9102 | 421.3088 | 397.6004 | 403.1543 | 402.2415 | 373.9079 | 387.1757
989.6931 | 917.6931 | 475.9568 | 421.3813 | 397.7228 | 403.2881 | 402.3193 | 373.9602 | 387.2525
990.6945 | 918.6945 | 475.9627 | 421.456 | 397.859 | 403.4176 | 402.3878 | 374.0278 | 387.3268
991.696 | 919.696 | 476.0495 | 421.5316 | 397.9802 | 403.5545 | 402.4596 | 374.0875 | 387.4049
992.6974 | 920.6974 | 476.1378 | 421.6224 | 398.1154 | 403.6871 | 402.5247 | 374.1624 | 387.4842
993.6989 | 921.6989 | 476.0395 | 421.7176 | 398.2513 | 403.8233 | 402.6064 | 374.23 | 387.5587
994.6903 | 922.6903 | 475.9064 | 421.8226 | 398.3833 | 403.9539 | 402.6771 | 374.2844 | 387.6538
995.6917 | 923.6917 | 475.7113 | 421.9031 | 398.5105 | 404.0715 | 402.7441 | 374.3579 | 387.7508
996.6932 | 924.6932 | 475.5301 | 421.9847 | 398.6318 | 404.2082 | 402.8084 | 374.4149 | 387.8458
997.6946 | 925.6946 | 475.4408 | 422.0733 | 398.7632 | 404.3323 | 402.8694 | 374.4876 | 387.9179
998.6961 | 926.6961 | 475.3297 | 422.1485 | 398.8866 | 404.4612 | 402.9268 | 374.581 | 387.9849
999.6975 | 927.6975 | 475.2724 | 422.2067 | 399.0023 | 404.5897 | 402.9922 | 374.662 | 388.0498
1000.6989 | 928.6989 | 475.3405 | 422.2817 | 399.1372 | 404.7069 | 403.0602 | 374.7382 | 388.1286
1001.6904 | 929.6904 | 475.2269 | 422.3433 | 399.2531 | 404.8353 | 403.115 | 374.8214 | 388.2057
1002.6918 | 930.6918 | 475.2408 | 422.4316 | 399.3766 | 404.9555 | 403.1774 | 374.8967 | 388.2814
1003.6932 | 931.6932 | 475.1751 | 422.5038 | 399.4925 | 405.0756 | 403.2306 | 374.9625 | 388.3551
1004.6947 | 932.6947 | 475.1542 | 422.5791 | 399.6214 | 405.1972 | 403.2994 | 375.0091 | 388.4286
1005.6961 | 933.6961 | 475.1472 | 422.6786 | 399.7401 | 405.3189 | 403.368 | 375.0603 | 388.5024
1006.6976 | 934.6976 | 475.1145 | 422.7545 | 399.8483 | 405.4354 | 403.4321 | 375.1127 | 388.6006
1007.699 | 935.699 | 475.1956 | 422.8325 | 399.9931 | 405.5543 | 403.5158 | 375.1881 | 388.682
1008.7105 | 936.7105 | 475.247 | 422.9265 | 400.1119 | 405.6843 | 403.5889 | 375.2466 | 388.7535
1009.6919 | 937.6919 | 475.2656 | 423.0192 | 400.2228 | 405.8014 | 403.6591 | 375.3127 | 388.8358
1010.6933 | 938.6933 | 475.3133 | 423.0988 | 400.3452 | 405.9219 | 403.7405 | 375.3752 | 388.9099
1011.6947 | 939.6947 | 475.3828 | 423.1621 | 400.47 | 406.0325 | 403.806 | 375.4231 | 388.9699
1012.6962 | 940.6962 | 475.43 | 423.238 | 400.5962 | 406.1573 | 403.8896 | 375.4649 | 389.0348
1013.6976 | 941.6976 | 475.4367 | 423.3183 | 400.722 | 406.2714 | 403.979 | 375.503 | 389.1069
1014.6991 | 942.6991 | 475.428 | 423.4027 | 400.8417 | 406.3944 | 404.0695 | 375.5503 | 389.1766
1015.7005 | 943.7005 | 475.5179 | 423.4795 | 400.9593 | 406.5076 | 404.1359 | 375.6155 | 389.245
1016.6919 | 944.6919 | 475.6796 | 423.5647 | 401.0809 | 406.6154 | 404.2193 | 375.6888 | 389.3109
1017.6934 | 945.6934 | 475.6764 | 423.6333 | 401.2084 | 406.735 | 404.2929 | 375.745 | 389.3741
1018.6948 | 946.6948 | 475.5333 | 423.6959 | 401.3213 | 406.8465 | 404.387 | 375.8103 | 389.4354
1019.6963 | 947.6963 | 475.4663 | 423.762 | 401.4268 | 406.9632 | 404.4506 | 375.8665 | 389.4917
1020.6977 | 948.6977 | 475.5321 | 423.832 | 401.5511 | 407.0745 | 404.5461 | 375.9287 | 389.546
1021.6991 | 949.6991 | 475.6037 | 423.8982 | 401.6702 | 407.1883 | 404.6207 | 376.0004 | 389.6212
1022.6906 | 950.6906 | 475.6743 | 423.9624 | 401.7836 | 407.2965 | 404.6986 | 376.0861 | 389.7025
1023.692 | 951.692 | 475.5358 | 424.0355 | 401.9044 | 407.4095 | 404.7554 | 376.1548 | 389.7977
1024.6934 | 952.6934 | 475.3497 | 424.0948 | 402.0232 | 407.513 | 404.8391 | 376.2332 | 389.8741
1025.6949 | 953.6949 | 475.4255 | 424.1548 | 402.1403 | 407.6391 | 404.9187 | 376.3197 | 389.9419
1026.6963 | 954.6963 | 475.5215 | 424.2133 | 402.2668 | 407.7487 | 404.9789 | 376.4203 | 389.9898
1027.6978 | 955.6978 | 475.479 | 424.2662 | 402.3927 | 407.8573 | 405.0591 | 376.5122 | 390.0399
1028.6992 | 956.6992 | 475.4064 | 424.3432 | 402.5113 | 407.9731 | 405.1317 | 376.609 | 390.0801
1029.7006 | 957.7006 | 475.2897 | 424.4136 | 402.6276 | 408.081 | 405.1881 | 376.6967 | 390.1265
1030.6921 | 958.6921 | 475.2 | 424.4682 | 402.7368 | 408.1963 | 405.2466 | 376.7924 | 390.1613
1031.6935 | 959.6935 | 475.1591 | 424.5204 | 402.8611 | 408.3039 | 405.3082 | 376.8738 | 390.1943
1032.6949 | 960.6949 | 475.0664 | 424.5599 | 402.9784 | 408.4094 | 405.3663 | 376.956 | 390.2243
1033.6964 | 961.6964 | 474.9999 | 424.5992 | 403.09 | 408.5116 | 405.4276 | 377.0316 | 390.2659
1034.6978 | 962.6978 | 474.9692 | 424.6542 | 403.2011 | 408.6184 | 405.4877 | 377.1231 | 390.3157
1035.6993 | 963.6993 | 475.0616 | 424.711 | 403.3243 | 408.7268 | 405.5492 | 377.2061 | 390.3805
1036.6907 | 964.6907 | 475.2734 | 424.7752 | 403.4387 | 408.8336 | 405.6043 | 377.272 | 390.4507
1037.6921 | 965.6921 | 475.2703 | 424.8146 | 403.5506 | 408.9404 | 405.6737 | 377.343 | 390.5201
1038.6936 | 966.6936 | 475.124 | 424.8671 | 403.6622 | 409.0454 | 405.7338 | 377.4134 | 390.5961
1039.695 | 967.695 | 475.0825 | 424.9078 | 403.7818 | 409.1534 | 405.803 | 377.4795 | 390.6682
1040.6964 | 968.6964 | 475.0823 | 424.9556 | 403.901 | 409.2632 | 405.8525 | 377.5501 | 390.7471
1041.6979 | 969.6979 | 475.0794 | 424.9942 | 404.0149 | 409.3701 | 405.9242 | 377.6157 | 390.8269
1042.6893 | 970.6893 | 475.0492 | 425.0488 | 404.1346 | 409.4668 | 405.9824 | 377.7048 | 390.9178
1043.6908 | 971.6908 | 475.0982 | 425.1107 | 404.2364 | 409.5794 | 406.0537 | 377.7803 | 390.9766
1044.6922 | 972.6922 | 475.0916 | 425.1607 | 404.3527 | 409.683 | 406.1169 | 377.8606 | 391.0404
1045.6936 | 973.6936 | 475.0874 | 425.2117 | 404.4634 | 409.7888 | 406.1916 | 377.9351 | 391.0827
1046.6951 | 974.6951 | 474.9805 | 425.2571 | 404.5641 | 409.8905 | 406.2545 | 378.0054 | 391.1173
1047.6965 | 975.6965 | 475.0001 | 425.301 | 404.6873 | 409.9821 | 406.319 | 378.0858 | 391.1475
1048.698 | 976.698 | 475.0781 | 425.3351 | 404.7846 | 410.0867 | 406.3777 | 378.1626 | 391.1844
1049.6894 | 977.6894 | 475.1007 | 425.3704 | 404.8864 | 410.1835 | 406.4647 | 378.2283 | 391.2171
1050.6908 | 978.6908 | 475.1091 | 425.4164 | 405.003 | 410.2892 | 406.5269 | 378.2899 | 391.2559
1051.6923 | 979.6923 | 474.9501 | 425.4645 | 405.1296 | 410.3863 | 406.6099 | 378.3641 | 391.2934
1052.6937 | 980.6937 | 474.8481 | 425.5155 | 405.2255 | 410.4833 | 406.6911 | 378.4284 | 391.3393
1053.6951 | 981.6951 | 474.9856 | 425.5564 | 405.3352 | 410.5782 | 406.7666 | 378.4919 | 391.3775
1054.6966 | 982.6966 | 475.0574 | 425.6061 | 405.4377 | 410.6772 | 406.8388 | 378.5401 | 391.4186
1055.698 | 983.698 | 475.0724 | 425.6285 | 405.5437 | 410.7859 | 406.9096 | 378.5849 | 391.473
1056.6995 | 984.6995 | 475.119 | 425.6484 | 405.6491 | 410.8753 | 406.9851 | 378.6419 | 391.5096
1057.7009 | 985.7009 | 475.2986 | 425.671 | 405.7616 | 410.981 | 407.0519 | 378.7059 | 391.578
1058.6923 | 986.6923 | 475.3596 | 425.7211 | 405.8654 | 411.0872 | 407.1239 | 378.7691 | 391.6397
1059.6938 | 987.6938 | 475.492 | 425.7573 | 405.9711 | 411.1851 | 407.1952 | 378.8308 | 391.7083
1060.6952 | 988.6952 | 475.6991 | 425.7809 | 406.0604 | 411.2809 | 407.2633 | 378.8908 | 391.7677
1061.6966 | 989.6966 | 475.8867 | 425.817 | 406.1677 | 411.3775 | 407.3324 | 378.9503 | 391.8114
1062.6981 | 990.6981 | 475.9884 | 425.8455 | 406.267 | 411.4817 | 407.4066 | 379.0132 | 391.8698
1063.6895 | 991.6895 | 476.0337 | 425.8918 | 406.365 | 411.5742 | 407.4757 | 379.0787 | 391.9236
1064.691 | 992.691 | 476.0577 | 425.9403 | 406.457 | 411.6688 | 407.5511 | 379.1514 | 391.9834
1065.6924 | 993.6924 | 476.1536 | 425.9748 | 406.5537 | 411.7686 | 407.6259 | 379.2215 | 392.0374
1066.6938 | 994.6938 | 476.0401 | 426.0095 | 406.6492 | 411.8663 | 407.7099 | 379.2807 | 392.0831
1067.6953 | 995.6953 | 475.9572 | 426.0301 | 406.7607 | 411.9648 | 407.7782 | 379.362 | 392.128
1068.6967 | 996.6967 | 475.8717 | 426.0519 | 406.841 | 412.0681 | 407.8576 | 379.4422 | 392.1721
1069.6982 | 997.6982 | 475.7308 | 426.1073 | 406.9562 | 412.159 | 407.9395 | 379.5214 | 392.235
1070.6996 | 998.6996 | 475.6423 | 426.1537 | 407.0497 | 412.2551 | 408.009 | 379.6073 | 392.3109
1071.701 | 999.701 | 475.5583 | 426.1946 | 407.1416 | 412.3505 | 408.0948 | 379.6962 | 392.3853
1072.6925 | 1000.6925 | 475.3643 | 426.232 | 407.2386 | 412.4428 | 408.1654 | 379.7741 | 392.4484
1073.6939 | 1001.6939 | 475.1331 | 426.266 | 407.3434 | 412.5488 | 408.2511 | 379.8596 | 392.5086
1074.6953 | 1002.6953 | 474.9403 | 426.358 | 407.4305 | 412.6494 | 408.3198 | 379.9226 | 392.5638
1075.6968 | 1003.6968 | 474.9418 | 426.4208 | 407.5271 | 412.7428 | 408.3906 | 379.9843 | 392.6047
1076.6982 | 1004.6982 | 474.992 | 426.423 | 407.6228 | 412.8424 | 408.4587 | 380.0431 | 392.6662
1077.6997 | 1005.6997 | 474.982 | 426.4148 | 407.7157 | 412.9382 | 408.5162 | 380.1285 | 392.7127
1078.6911 | 1006.6911 | 474.9297 | 426.415 | 407.8098 | 413.0365 | 408.5944 | 380.2073 | 392.7699
1079.6925 | 1007.6925 | 474.9037 | 426.4362 | 407.8993 | 413.1239 | 408.6726 | 380.28 | 392.8171
1080.694 | 1008.694 | 474.9256 | 426.4298 | 407.991 | 413.2227 | 408.7417 | 380.346 | 392.8776
1081.6954 | 1009.6954 | 475.0028 | 426.4066 | 408.0808 | 413.3141 | 408.8338 | 380.4097 | 392.9373
1082.6968 | 1010.6968 | 475.0155 | 426.3941 | 408.1674 | 413.4082 | 408.9191 | 380.4665 | 392.9817
1083.6983 | 1011.6983 | 475.1495 | 426.4043 | 408.2505 | 413.5174 | 408.9941 | 380.5282 | 393.0307
1084.6897 | 1012.6897 | 475.1025 | 426.4284 | 408.3498 | 413.6155 | 409.0891 | 380.5894 | 393.0784
1085.6911 | 1013.6911 | 475.0176 | 426.4361 | 408.4219 | 413.7173 | 409.1679 | 380.6463 | 393.1178
1086.6926 | 1014.6926 | 474.9828 | 426.4183 | 408.5201 | 413.8217 | 409.2419 | 380.7039 | 393.1602
1087.694 | 1015.694 | 475.133 | 426.4113 | 408.595 | 413.9169 | 409.3277 | 380.7542 | 393.2034
1088.6955 | 1016.6955 | 475.2551 | 426.4069 | 408.7016 | 414.0049 | 409.406 | 380.8019 | 393.2448
1089.6969 | 1017.6969 | 475.2508 | 426.4159 | 408.7896 | 414.0917 | 409.4825 | 380.8527 | 393.2907
1090.6983 | 1018.6983 | 475.2931 | 426.4373 | 408.8852 | 414.1933 | 409.555 | 380.9139 | 393.3231
1091.6898 | 1019.6898 | 475.2379 | 426.4304 | 408.984 | 414.2878 | 409.6281 | 380.9869 | 393.3609
1092.6912 | 1020.6912 | 475.1966 | 426.4621 | 409.0775 | 414.3944 | 409.6901 | 381.0794 | 393.3989
1093.6927 | 1021.6927 | 475.156 | 426.4881 | 409.1656 | 414.494 | 409.7616 | 381.1623 | 393.4324
1094.6941 | 1022.6941 | 475.1957 | 426.4748 | 409.2543 | 414.5859 | 409.8321 | 381.237 | 393.468
1095.6955 | 1023.6955 | 475.2411 | 426.439 | 409.3364 | 414.6827 | 409.8966 | 381.3219 | 393.5101
1096.697 | 1024.697 | 475.1835 | 426.4259 | 409.4268 | 414.7812 | 409.9674 | 381.3876 | 393.5616
1097.6984 | 1025.6984 | 475.0814 | 426.4049 | 409.4981 | 414.8618 | 410.0352 | 381.4587 | 393.597
1098.6999 | 1026.6999 | 475.2 | 426.4015 | 409.5881 | 414.9463 | 410.1015 | 381.5097 | 393.647
1099.6913 | 1027.6913 | 475.2247 | 426.3857 | 409.6839 | 415.0414 | 410.1718 | 381.5597 | 393.6797
1100.6927 | 1028.6927 | 475.3678 | 426.3756 | 409.77 | 415.1298 | 410.2289 | 381.6048 | 393.7343
1101.6942 | 1029.6942 | 475.4629 | 426.4052 | 409.8542 | 415.2233 | 410.2972 | 381.6582 | 393.776
1102.6956 | 1030.6956 | 475.5377 | 426.3822 | 409.9322 | 415.3296 | 410.358 | 381.7202 | 393.8466
1103.697 | 1031.697 | 475.5062 | 426.3907 | 410.0191 | 415.4156 | 410.4124 | 381.7939 | 393.9124
1104.6985 | 1032.6985 | 475.509 | 426.4004 | 410.1098 | 415.5007 | 410.4854 | 381.851 | 393.9734
1105.6899 | 1033.6899 | 475.5967 | 426.3727 | 410.1771 | 415.5995 | 410.5502 | 381.9396 | 394.0085
1106.6913 | 1034.6913 | 475.5132 | 426.359 | 410.2725 | 415.692 | 410.6073 | 382.0502 | 394.0268
1107.6928 | 1035.6928 | 475.2886 | 426.353 | 410.352 | 415.7786 | 410.6705 | 382.1246 | 394.0407
1108.6942 | 1036.6942 | 475.1398 | 426.3339 | 410.4261 | 415.8666 | 410.7243 | 382.1804 | 394.0589
1109.6957 | 1037.6957 | 475.0905 | 426.3092 | 410.5033 | 415.9552 | 410.7865 | 382.2085 | 394.084
1110.6971 | 1038.6971 | 475.1678 | 426.294 | 410.5946 | 416.0507 | 410.8464 | 382.242 | 394.1086
1111.6985 | 1039.6985 | 475.2425 | 426.2983 | 410.6718 | 416.1362 | 410.9105 | 382.2705 | 394.1369
1112.7 | 1040.7 | 475.1945 | 426.2806 | 410.7599 | 416.2231 | 410.9609 | 382.3019 | 394.148
1113.6914 | 1041.6914 | 475.2302 | 426.2652 | 410.842 | 416.327 | 411.0232 | 382.3226 | 394.1635
1114.6928 | 1042.6928 | 475.2019 | 426.2354 | 410.9261 | 416.4144 | 411.0678 | 382.3188 | 394.1774
1115.6943 | 1043.6943 | 475.1172 | 426.2014 | 410.9969 | 416.5023 | 411.1178 | 382.3184 | 394.1907
1116.6957 | 1044.6957 | 475.0187 | 426.1602 | 411.079 | 416.5918 | 411.1717 | 382.329 | 394.2086
1117.6972 | 1045.6972 | 475.0735 | 426.1561 | 411.1645 | 416.6789 | 411.2211 | 382.3416 | 394.2237
1118.6986 | 1046.6986 | 475.1909 | 426.13 | 411.2477 | 416.7747 | 411.2589 | 382.3584 | 394.2341
1119.7 | 1047.7 | 475.3277 | 426.081 | 411.3288 | 416.863 | 411.292 | 382.3766 | 394.2624
1120.6915 | 1048.6915 | 475.5551 | 426.0441 | 411.4137 | 416.9514 | 411.3357 | 382.41 | 394.2921
1121.6929 | 1049.6929 | 475.5932 | 426.0228 | 411.4864 | 417.0297 | 411.3733 | 382.4536 | 394.3311
1122.6944 | 1050.6944 | 475.532 | 426.0015 | 411.565 | 417.1276 | 411.4149 | 382.4863 | 394.3647
1123.6958 | 1051.6958 | 475.517 | 425.9627 | 411.6427 | 417.2055 | 411.4678 | 382.5113 | 394.4254
1124.6972 | 1052.6972 | 475.4457 | 425.9211 | 411.7168 | 417.2936 | 411.515 | 382.5395 | 394.4659
1125.6987 | 1053.6987 | 475.3092 | 425.9071 | 411.7908 | 417.3765 | 411.5534 | 382.5545 | 394.502
1126.6901 | 1054.6901 | 475.2518 | 425.8802 | 411.8692 | 417.4554 | 411.6078 | 382.5911 | 394.5421
1127.6915 | 1055.6915 | 475.2021 | 425.85 | 411.9588 | 417.5362 | 411.6528 | 382.634 | 394.5758
1128.7431 | 1056.7431 | 475.0882 | 425.8102 | 412.0234 | 417.6101 | 411.7098 | 382.6838 | 394.6112
1129.6944 | 1057.6944 | 475.0042 | 425.7739 | 412.1036 | 417.7008 | 411.7528 | 382.7463 | 394.6439
1130.6959 | 1058.6959 | 474.9459 | 425.7498 | 412.1783 | 417.7752 | 411.8072 | 382.8168 | 394.6805
1131.6973 | 1059.6973 | 474.9188 | 425.7184 | 412.2509 | 417.8542 | 411.8544 | 382.8705 | 394.7192
1132.6987 | 1060.6987 | 474.822 | 425.6452 | 412.3314 | 417.9339 | 411.9141 | 382.9156 | 394.7389
1133.6902 | 1061.6902 | 474.8798 | 425.5761 | 412.4066 | 418.0221 | 411.9755 | 382.9596 | 394.7599
1134.6916 | 1062.6916 | 474.8401 | 425.5384 | 412.4905 | 418.0906 | 412.035 | 382.9995 | 394.7749
1135.693 | 1063.693 | 474.8744 | 425.4889 | 412.5609 | 418.1783 | 412.0888 | 383.0301 | 394.7867
1136.6945 | 1064.6945 | 475.0531 | 425.4198 | 412.639 | 418.2687 | 412.1551 | 383.063 | 394.7816
1137.6959 | 1065.6959 | 475.1569 | 425.3721 | 412.7193 | 418.3526 | 412.2196 | 383.1147 | 394.773
1138.6974 | 1066.6974 | 475.2632 | 425.3174 | 412.7987 | 418.4332 | 412.2744 | 383.1672 | 394.7429
1139.6988 | 1067.6988 | 475.2331 | 425.231 | 412.8578 | 418.5171 | 412.3396 | 383.2254 | 394.7162
1140.7002 | 1068.7002 | 475.274 | 425.1374 | 412.941 | 418.593 | 412.4117 | 383.2617 | 394.694
1141.6917 | 1069.6917 | 475.2614 | 425.0808 | 413.0187 | 418.6788 | 412.4682 | 383.2983 | 394.6706
1142.6931 | 1070.6931 | 475.2557 | 425.0275 | 413.0964 | 418.7557 | 412.5244 | 383.3335 | 394.6496
1143.6946 | 1071.6946 | 475.202 | 424.9635 | 413.1527 | 418.8374 | 412.5893 | 383.3685 | 394.6364
1144.696 | 1072.696 | 475.068 | 424.9025 | 413.2325 | 418.9084 | 412.6561 | 383.4109 | 394.6229
1145.6974 | 1073.6974 | 474.9862 | 424.8388 | 413.3038 | 418.9841 | 412.7194 | 383.4618 | 394.6181
1146.6989 | 1074.6989 | 475.0044 | 424.7782 | 413.3858 | 419.0568 | 412.7829 | 383.5094 | 394.6142
1147.6903 | 1075.6903 | 475.1252 | 424.6803 | 413.451 | 419.1316 | 412.8413 | 383.5673 | 394.6257
1148.6917 | 1076.6917 | 475.2847 | 424.5889 | 413.5231 | 419.2017 | 412.9119 | 383.6308 | 394.611
1149.6932 | 1077.6932 | 475.3391 | 424.571 | 413.595 | 419.2685 | 412.9535 | 383.6846 | 394.6306
1150.6946 | 1078.6946 | 475.3738 | 424.5004 | 413.6607 | 419.3344 | 412.998 | 383.7513 | 394.6368
1151.6961 | 1079.6961 | 475.5343 | 424.4256 | 413.7481 | 419.4062 | 413.0505 | 383.8122 | 394.6582
1152.6975 | 1080.6975 | 475.4894 | 424.3775 | 413.8141 | 419.4732 | 413.0995 | 383.8666 | 394.7013
1153.6989 | 1081.6989 | 475.3707 | 424.335 | 413.8932 | 419.548 | 413.1495 | 383.9328 | 394.7207
1154.7004 | 1082.7004 | 475.2345 | 424.2855 | 413.972 | 419.6186 | 413.1996 | 383.9926 | 394.7658
1155.7218 | 1083.7218 | 475.0569 | 424.2429 | 414.0416 | 419.7014 | 413.2647 | 384.0514 | 394.7924
1156.6932 | 1084.6932 | 474.9456 | 424.174 | 414.1164 | 419.7778 | 413.3125 | 384.0879 | 394.8265
1157.6947 | 1085.6947 | 474.9497 | 424.1284 | 414.1949 | 419.8456 | 413.3628 | 384.1083 | 394.8381
1158.6961 | 1086.6961 | 474.8706 | 424.0885 | 414.2739 | 419.9202 | 413.401 | 384.1312 | 394.8517
1159.6976 | 1087.6976 | 474.874 | 424.0435 | 414.3419 | 419.9914 | 413.4634 | 384.1371 | 394.867
1160.699 | 1088.699 | 474.8827 | 423.9933 | 414.3961 | 420.0549 | 413.5098 | 384.1545 | 394.8442
1161.7004 | 1089.7004 | 474.8611 | 423.9298 | 414.4637 | 420.1146 | 413.5684 | 384.144 | 394.8208
1162.6919 | 1090.6919 | 474.931 | 423.9487 | 414.5394 | 420.1777 | 413.6182 | 384.13 | 394.7851
1163.6933 | 1091.6933 | 474.9199 | 423.9118 | 414.599 | 420.2342 | 413.667 | 384.1427 | 394.7442
1164.6947 | 1092.6947 | 474.7131 | 423.887 | 414.6592 | 420.3054 | 413.7186 | 384.1715 | 394.7356
1165.6962 | 1093.6962 | 474.7236 | 423.8589 | 414.7082 | 420.3699 | 413.7545 | 384.2037 | 394.7551
1166.6976 | 1094.6976 | 474.868 | 423.8148 | 414.7758 | 420.4222 | 413.8034 | 384.2388 | 394.7886
1167.6991 | 1095.6991 | 475.0247 | 423.771 | 414.833 | 420.473 | 413.8414 | 384.2768 | 394.8371
1168.6905 | 1096.6905 | 475.271 | 423.7358 | 414.889 | 420.5193 | 413.8961 | 384.319 | 394.8836
1169.6919 | 1097.6919 | 475.4135 | 423.7172 | 414.9408 | 420.5746 | 413.9313 | 384.3492 | 394.9156
1170.6934 | 1098.6934 | 475.5197 | 423.7149 | 414.9995 | 420.6328 | 413.9928 | 384.3836 | 394.9324
1171.6948 | 1099.6948 | 475.5331 | 423.659 | 415.0533 | 420.6789 | 414.0475 | 384.4245 | 394.9452
1172.6963 | 1100.6963 | 475.662 | 423.6079 | 415.0968 | 420.7499 | 414.1023 | 384.461 | 394.94
1173.6977 | 1101.6977 | 475.8167 | 423.5759 | 415.1516 | 420.8107 | 414.1455 | 384.4886 | 394.9235
1174.6891 | 1102.6891 | 475.8554 | 423.5733 | 415.209 | 420.859 | 414.197 | 384.5193 | 394.9015
1175.6906 | 1103.6906 | 475.794 | 423.601 | 415.2683 | 420.9077 | 414.2557 | 384.5461 | 394.8855
1176.692 | 1104.692 | 475.934 | 423.5706 | 415.3143 | 420.9672 | 414.3021 | 384.5701 | 394.873
1177.6934 | 1105.6934 | 476.0497 | 423.5032 | 415.3856 | 421.0202 | 414.3435 | 384.6016 | 394.8781
1178.6949 | 1106.6949 | 476.0259 | 423.4446 | 415.4329 | 421.1087 | 414.404 | 384.6231 | 394.9015
1179.6963 | 1107.6963 | 475.9479 | 423.4012 | 415.4884 | 421.149 | 414.4548 | 384.6456 | 394.9412
1180.6978 | 1108.6978 | 475.8496 | 423.3878 | 415.5499 | 421.1963 | 414.5077 | 384.6575 | 394.9918
1181.6992 | 1109.6992 | 475.9979 | 423.3548 | 415.6064 | 421.2302 | 414.5664 | 384.6581 | 395.0269
1182.6906 | 1110.6906 | 476.0768 | 423.3469 | 415.6611 | 421.2745 | 414.627 | 384.6485 | 395.0467
1183.6921 | 1111.6921 | 476.1374 | 423.3326 | 415.7151 | 421.3244 | 414.6887 | 384.6461 | 395.0417
1184.6935 | 1112.6935 | 476.0055 | 423.3481 | 415.7633 | 421.3685 | 414.7459 | 384.6422 | 395.0034
1185.6949 | 1113.6949 | 476.0146 | 423.336 | 415.8244 | 421.4032 | 414.7937 | 384.6585 | 394.9616
1186.6964 | 1114.6964 | 475.8645 | 423.3372 | 415.894 | 421.4411 | 414.8488 | 384.7083 | 394.9103
1187.6978 | 1115.6978 | 475.9174 | 423.3283 | 415.9362 | 421.4734 | 414.9086 | 384.753 | 394.846
1188.6993 | 1116.6993 | 475.8773 | 423.3176 | 415.9976 | 421.5075 | 414.9574 | 384.8088 | 394.8054
1189.6907 | 1117.6907 | 475.84 | 423.2774 | 416.0561 | 421.5248 | 415.0044 | 384.8571 | 394.7559
1190.6921 | 1118.6921 | 475.9765 | 423.2828 | 416.1062 | 421.5566 | 415.0473 | 384.9009 | 394.7184
1191.6936 | 1119.6936 | 475.9209 | 423.275 | 416.1606 | 421.5796 | 415.1034 | 384.9483 | 394.6907
1192.695 | 1120.695 | 475.8239 | 423.2831 | 416.2343 | 421.6109 | 415.1436 | 384.9741 | 394.6893
1193.6965 | 1121.6965 | 475.8184 | 423.2894 | 416.2966 | 421.6197 | 415.1736 | 385.0147 | 394.6923
1194.6979 | 1122.6979 | 475.718 | 423.3106 | 416.3389 | 421.6357 | 415.213 | 385.0645 | 394.7154
1195.6893 | 1123.6893 | 475.6584 | 423.3178 | 416.387 | 421.6666 | 415.273 | 385.0933 | 394.7645
1196.7008 | 1124.7008 | 475.7079 | 423.3141 | 416.4389 | 421.7056 | 415.3127 | 385.1278 | 394.7781
1197.6922 | 1125.6922 | 475.8404 | 423.3295 | 416.4996 | 421.7416 | 415.353 | 385.1635 | 394.8187
1198.6936 | 1126.6936 | 475.9321 | 423.3407 | 416.5521 | 421.7753 | 415.4041 | 385.1953 | 394.8345
1199.6951 | 1127.6951 | 476.1597 | 423.3342 | 416.6134 | 421.8116 | 415.4512 | 385.2298 | 394.8659
1200.6965 | 1128.6965 | 476.2402 | 423.3355 | 416.6558 | 421.8393 | 415.4979 | 385.2547 | 394.8888
1201.698 | 1129.698 | 476.2397 | 423.3495 | 416.7094 | 421.8665 | 415.545 | 385.2932 | 394.9021
1202.6994 | 1130.6994 | 476.2853 | 423.3629 | 416.7479 | 421.8822 | 415.6012 | 385.3185 | 394.9196
1203.7008 | 1131.7008 | 476.3585 | 423.3638 | 416.8131 | 421.9099 | 415.6434 | 385.3412 | 394.9269
1204.6923 | 1132.6923 | 476.2886 | 423.3596 | 416.8636 | 421.9469 | 415.6698 | 385.3675 | 394.9254
1205.6937 | 1133.6937 | 476.2928 | 423.3625 | 416.904 | 421.9697 | 415.7196 | 385.4017 | 394.9335
1206.6951 | 1134.6951 | 476.4154 | 423.3638 | 416.9639 | 422.0009 | 415.7676 | 385.4363 | 394.929
1207.6966 | 1135.6966 | 476.5786 | 423.3759 | 417.0156 | 422.0238 | 415.8004 | 385.4724 | 394.9108
1208.698 | 1136.698 | 476.7201 | 423.4074 | 417.0596 | 422.0429 | 415.8626 | 385.5166 | 394.8999
1209.6995 | 1137.6995 | 476.8415 | 423.4366 | 417.1165 | 422.0589 | 415.9026 | 385.5573 | 394.8636
1210.6909 | 1138.6909 | 476.8504 | 423.4365 | 417.1616 | 422.0982 | 415.9596 | 385.6112 | 394.8394
1211.6923 | 1139.6923 | 476.8193 | 423.4716 | 417.211 | 422.1294 | 416.0014 | 385.6591 | 394.8203
1212.6938 | 1140.6938 | 476.9781 | 423.4859 | 417.2531 | 422.1614 | 416.0435 | 385.7048 | 394.7798
1213.6952 | 1141.6952 | 476.9 | 423.4911 | 417.3102 | 422.1869 | 416.1026 | 385.744 | 394.7658
1214.6966 | 1142.6966 | 476.9166 | 423.5094 | 417.3736 | 422.2216 | 416.1428 | 385.7848 | 394.7618
1215.6981 | 1143.6981 | 476.8551 | 423.52 | 417.4187 | 422.2763 | 416.1958 | 385.8072 | 394.7661
1216.6895 | 1144.6895 | 476.9719 | 423.534 | 417.4539 | 422.3041 | 416.2429 | 385.8344 | 394.7885
1217.691 | 1145.691 | 477.0186 | 423.5457 | 417.4967 | 422.3116 | 416.2887 | 385.8653 | 394.8265
1218.6924 | 1146.6924 | 476.8971 | 423.5884 | 417.5358 | 422.3315 | 416.3408 | 385.8982 | 394.8814
1219.6938 | 1147.6938 | 476.7452 | 423.6232 | 417.5925 | 422.36 | 416.3897 | 385.9332 | 394.9281
1220.6953 | 1148.6953 | 476.7368 | 423.646 | 417.6356 | 422.4044 | 416.4361 | 385.967 | 394.9602
1221.6967 | 1149.6967 | 476.579 | 423.6476 | 417.6824 | 422.416 | 416.4948 | 386.0208 | 394.9787
1222.6982 | 1150.6982 | 476.6203 | 423.6555 | 417.7256 | 422.4542 | 416.5488 | 386.062 | 394.9944
1223.6996 | 1151.6996 | 476.8276 | 423.6749 | 417.7737 | 422.4682 | 416.5924 | 386.11 | 395.0069
1224.701 | 1152.701 | 476.9569 | 423.6891 | 417.8154 | 422.4831 | 416.6519 | 386.1576 | 394.9913
1225.6925 | 1153.6925 | 477.1173 | 423.6989 | 417.8565 | 422.522 | 416.6955 | 386.2071 | 394.972
1226.6939 | 1154.6939 | 477.1201 | 423.7384 | 417.9148 | 422.566 | 416.7495 | 386.2604 | 394.9405
1227.6953 | 1155.6953 | 477.0265 | 423.7726 | 417.9524 | 422.5728 | 416.8047 | 386.3025 | 394.8959
1228.6968 | 1156.6968 | 477.04 | 423.8103 | 417.9946 | 422.5899 | 416.8496 | 386.3574 | 394.8612
1229.6982 | 1157.6982 | 477.0372 | 423.858 | 418.0438 | 422.5956 | 416.8988 | 386.4086 | 394.8078
1230.6997 | 1158.6997 | 476.9732 | 423.9021 | 418.087 | 422.6028 | 416.9452 | 386.4627 | 394.7838
1231.6911 | 1159.6911 | 476.8066 | 423.9526 | 418.1235 | 422.6066 | 416.9938 | 386.5112 | 394.7445
1232.6925 | 1160.6925 | 476.8528 | 423.9841 | 418.1643 | 422.6132 | 417.0157 | 386.5696 | 394.7357
1233.694 | 1161.694 | 476.6876 | 424.054 | 418.2003 | 422.6248 | 417.0681 | 386.6209 | 394.7469
1234.6954 | 1162.6954 | 476.619 | 424.0865 | 418.2442 | 422.6416 | 417.1036 | 386.6791 | 394.7531
1235.6968 | 1163.6968 | 476.543 | 424.1153 | 418.2799 | 422.6487 | 417.1349 | 386.7315 | 394.7804
1236.6983 | 1164.6983 | 476.4432 | 424.1363 | 418.321 | 422.6547 | 417.1699 | 386.8011 | 394.7859
1237.6897 | 1165.6897 | 476.2821 | 424.1629 | 418.3569 | 422.7018 | 417.2179 | 386.8487 | 394.7821
1238.6912 | 1166.6912 | 476.3714 | 424.2048 | 418.399 | 422.7004 | 417.2551 | 386.9119 | 394.7609
1239.6926 | 1167.6926 | 476.274 | 424.216 | 418.4348 | 422.7028 | 417.299 | 386.9612 | 394.7194
1240.694 | 1168.694 | 476.1116 | 424.1806 | 418.4688 | 422.7316 | 417.3282 | 387.0076 | 394.6861
1241.6955 | 1169.6955 | 475.9686 | 424.1452 | 418.5037 | 422.7498 | 417.3631 | 387.0535 | 394.672
1242.6969 | 1170.6969 | 475.8519 | 424.1447 | 418.5279 | 422.7801 | 417.3898 | 387.0987 | 394.664
1243.6984 | 1171.6984 | 475.781 | 424.1367 | 418.5684 | 422.7733 | 417.4161 | 387.1624 | 394.6696
1244.6998 | 1172.6998 | 475.6208 | 424.1144 | 418.6076 | 422.7679 | 417.4581 | 387.2245 | 394.664
1245.7012 | 1173.7012 | 475.4098 | 424.0797 | 418.6341 | 422.7471 | 417.4787 | 387.2745 | 394.658
1246.6927 | 1174.6927 | 475.2032 | 424.0631 | 418.6488 | 422.7442 | 417.5085 | 387.3318 | 394.6273
1247.6941 | 1175.6941 | 475.0592 | 424.0553 | 418.6969 | 422.7488 | 417.5372 | 387.3735 | 394.6278
1248.6955 | 1176.6955 | 475.0149 | 424.0589 | 418.7219 | 422.7475 | 417.5541 | 387.3953 | 394.6265
1249.697 | 1177.697 | 475.0226 | 424.0746 | 418.753 | 422.7485 | 417.5777 | 387.3916 | 394.6144
1250.6984 | 1178.6984 | 474.9367 | 424.0916 | 418.8038 | 422.7502 | 417.6028 | 387.3858 | 394.6333
1251.6999 | 1179.6999 | 474.8291 | 424.1072 | 418.8397 | 422.7305 | 417.6149 | 387.3812 | 394.6389
1252.7013 | 1180.7013 | 474.8357 | 424.1045 | 418.8757 | 422.766 | 417.6482 | 387.3816 | 394.6782
1253.6927 | 1181.6927 | 474.928 | 424.1087 | 418.9304 | 422.7705 | 417.6684 | 387.3817 | 394.6957
1254.6942 | 1182.6942 | 475.0873 | 424.1222 | 418.9683 | 422.773 | 417.6862 | 387.3825 | 394.7417
1255.6956 | 1183.6956 | 475.3423 | 424.1315 | 419.0062 | 422.7832 | 417.7079 | 387.3864 | 394.7655
1256.697 | 1184.697 | 475.5449 | 424.1536 | 419.0455 | 422.7742 | 417.7172 | 387.3959 | 394.7927
1257.6985 | 1185.6985 | 475.5473 | 424.1903 | 419.0946 | 422.7345 | 417.7534 | 387.4115 | 394.8442
1258.6999 | 1186.6999 | 475.5042 | 424.2038 | 419.1304 | 422.717 | 417.7741 | 387.4323 | 394.8786
1259.6913 | 1187.6913 | 475.8061 | 424.2085 | 419.1791 | 422.7017 | 417.8046 | 387.4489 | 394.8922
1260.6928 | 1188.6928 | 476.0523 | 424.2086 | 419.2148 | 422.7133 | 417.8326 | 387.4592 | 394.9016
1261.6942 | 1189.6942 | 476.0928 | 424.2338 | 419.2635 | 422.6964 | 417.861 | 387.4649 | 394.916
1262.6957 | 1190.6957 | 476.1576 | 424.2293 | 419.3058 | 422.6865 | 417.8998 | 387.4741 | 394.9025
1263.6971 | 1191.6971 | 476.0846 | 424.2657 | 419.351 | 422.6658 | 417.9375 | 387.4787 | 394.9089
1264.6985 | 1192.6985 | 476.1325 | 424.2563 | 419.381 | 422.6531 | 417.9648 | 387.4752 | 394.9194
1265.69 | 1193.69 | 476.3068 | 424.2408 | 419.4297 | 422.6522 | 418.0029 | 387.4809 | 394.9389
1266.6914 | 1194.6914 | 476.3445 | 424.2451 | 419.471 | 422.6513 | 418.0376 | 387.4782 | 394.9746
1267.6929 | 1195.6929 | 476.2337 | 424.2693 | 419.5097 | 422.6635 | 418.0788 | 387.482 | 395.0214
1268.6943 | 1196.6943 | 475.9782 | 424.2625 | 419.5652 | 422.6802 | 418.128 | 387.4882 | 395.0346
1269.6957 | 1197.6957 | 476.0396 | 424.2783 | 419.6036 | 422.6801 | 418.1696 | 387.4985 | 395.0512
1270.6972 | 1198.6972 | 476.1667 | 424.2919 | 419.645 | 422.6694 | 418.2035 | 387.5154 | 395.045
1271.6986 | 1199.6986 | 476.0183 | 424.3156 | 419.6887 | 422.6811 | 418.2549 | 387.5292 | 394.9841
1272.7001 | 1200.7001 | 475.888 | 424.3239 | 419.7355 | 422.6869 | 418.286 | 387.56 | 394.954
1273.7015 | 1201.7015 | 475.9436 | 424.3593 | 419.7781 | 422.7115 | 418.338 | 387.5627 | 394.8887
1274.6929 | 1202.6929 | 475.8717 | 424.3954 | 419.8375 | 422.7252 | 418.3695 | 387.5714 | 394.823
1275.6944 | 1203.6944 | 475.7311 | 424.407 | 419.8816 | 422.7537 | 418.4183 | 387.585 | 394.7775
1276.6958 | 1204.6958 | 475.6395 | 424.3921 | 419.9189 | 422.7575 | 418.4466 | 387.5996 | 394.7193
1277.6972 | 1205.6972 | 475.6521 | 424.3996 | 419.9676 | 422.7753 | 418.4894 | 387.6205 | 394.6804
1278.6987 | 1206.6987 | 475.8053 | 424.4062 | 420.0275 | 422.7991 | 418.511 | 387.6324 | 394.6356
1279.6901 | 1207.6901 | 475.8336 | 424.4321 | 420.0811 | 422.8243 | 418.5405 | 387.6514 | 394.6093
1280.6915 | 1208.6915 | 475.7479 | 424.4229 | 420.1196 | 422.8414 | 418.5795 | 387.6717 | 394.5638
1281.693 | 1209.693 | 475.7122 | 424.4174 | 420.1774 | 422.8526 | 418.6033 | 387.6882 | 394.5364
1282.6944 | 1210.6944 | 475.6379 | 424.4278 | 420.2202 | 422.8638 | 418.6281 | 387.7032 | 394.507
1283.6959 | 1211.6959 | 475.6263 | 424.4267 | 420.2626 | 422.8882 | 418.6562 | 387.7222 | 394.4869
1284.6973 | 1212.6973 | 475.6773 | 424.4406 | 420.3149 | 422.9283 | 418.6867 | 387.7256 | 394.4912
1285.6987 | 1213.6987 | 475.6681 | 424.4702 | 420.3629 | 422.9551 | 418.7002 | 387.7503 | 394.5109
1286.6902 | 1214.6902 | 475.5917 | 424.4784 | 420.4063 | 422.9721 | 418.7298 | 387.7622 | 394.4948
1287.6916 | 1215.6916 | 475.5445 | 424.4841 | 420.4668 | 422.99 | 418.7396 | 387.7655 | 394.5059
1288.693 | 1216.693 | 475.3524 | 424.5008 | 420.5026 | 423.0281 | 418.7503 | 387.778 | 394.485
1289.6945 | 1217.6945 | 475.2068 | 424.5007 | 420.5404 | 423.0656 | 418.7668 | 387.7838 | 394.4446
1290.6959 | 1218.6959 | 474.9674 | 424.5023 | 420.5893 | 423.0958 | 418.7664 | 387.7844 | 394.4204
1291.6974 | 1219.6974 | 474.8357 | 424.5164 | 420.6314 | 423.1199 | 418.79 | 387.7844 | 394.4003
1292.6988 | 1220.6988 | 474.7234 | 424.5157 | 420.6732 | 423.1714 | 418.7988 | 387.7783 | 394.3921
1293.7002 | 1221.7002 | 474.6327 | 424.5213 | 420.7215 | 423.2185 | 418.8148 | 387.7842 | 394.3984
1294.6917 | 1222.6917 | 474.7605 | 424.5265 | 420.7694 | 423.268 | 418.8111 | 387.7819 | 394.4124
1295.6931 | 1223.6931 | 474.7745 | 424.5544 | 420.8301 | 423.321 | 418.8429 | 387.7898 | 394.4161
1296.6946 | 1224.6946 | 474.7684 | 424.5872 | 420.8673 | 423.3681 | 418.8536 | 387.801 | 394.4257
1297.696 | 1225.696 | 474.8388 | 424.5957 | 420.9041 | 423.41 | 418.8527 | 387.8083 | 394.4164
1298.6974 | 1226.6974 | 475.0122 | 424.6157 | 420.9436 | 423.4475 | 418.8655 | 387.8216 | 394.4086
1299.6989 | 1227.6989 | 475.0207 | 424.6194 | 420.9836 | 423.4947 | 418.8976 | 387.8405 | 394.4146
1300.6903 | 1228.6903 | 474.9671 | 424.6212 | 421.0259 | 423.5352 | 418.9104 | 387.8574 | 394.413
1301.6917 | 1229.6917 | 475.0399 | 424.6328 | 421.0626 | 423.5863 | 418.9302 | 387.8839 | 394.4166
1302.6932 | 1230.6932 | 475.1854 | 424.6355 | 421.1018 | 423.6435 | 418.9502 | 387.9063 | 394.4231
1303.6946 | 1231.6946 | 475.2185 | 424.6475 | 421.144 | 423.6962 | 418.9676 | 387.9312 | 394.4259
1304.6961 | 1232.6961 | 475.1596 | 424.6435 | 421.1802 | 423.7446 | 418.9926 | 387.9539 | 394.422
1305.6975 | 1233.6975 | 475.089 | 424.6401 | 421.2294 | 423.8039 | 419.008 | 387.9851 | 394.4101
1306.6989 | 1234.6989 | 475.1234 | 424.6239 | 421.269 | 423.8714 | 419.035 | 388.0175 | 394.3838
1307.6904 | 1235.6904 | 475.3175 | 424.6174 | 421.3067 | 423.9278 | 419.0654 | 388.0445 | 394.3395
1308.6918 | 1236.6918 | 475.3453 | 424.5959 | 421.3448 | 423.9972 | 419.0919 | 388.0727 | 394.3016
1309.7633 | 1237.7633 | 475.4206 | 424.5942 | 421.3956 | 424.0689 | 419.1132 | 388.0979 | 394.2737
1310.6947 | 1238.6947 | 475.4791 | 424.6249 | 421.4426 | 424.1276 | 419.1437 | 388.1222 | 394.2761
1311.6961 | 1239.6961 | 475.5806 | 424.6049 | 421.4951 | 424.2005 | 419.1545 | 388.148 | 394.2878
1312.6976 | 1240.6976 | 475.6736 | 424.6237 | 421.5547 | 424.2327 | 419.1752 | 388.1695 | 394.2916
1313.699 | 1241.699 | 475.8933 | 424.651 | 421.6052 | 424.2798 | 419.1847 | 388.1913 | 394.2958
1314.7004 | 1242.7004 | 475.7554 | 424.6393 | 421.6572 | 424.3444 | 419.1984 | 388.1999 | 394.2729
1315.6919 | 1243.6919 | 475.6218 | 424.6267 | 421.6973 | 424.3916 | 419.2191 | 388.2098 | 394.2536
1316.6933 | 1244.6933 | 475.7116 | 424.6084 | 421.7272 | 424.435 | 419.2377 | 388.221 | 394.2051
1317.6948 | 1245.6948 | 475.8677 | 424.6 | 421.7767 | 424.4969 | 419.2584 | 388.2239 | 394.1519
1318.6962 | 1246.6962 | 475.8953 | 424.6291 | 421.8188 | 424.5523 | 419.2616 | 388.24 | 394.0855
1319.6976 | 1247.6976 | 475.8253 | 424.6456 | 421.8714 | 424.6157 | 419.2739 | 388.2596 | 394.0202
1320.6991 | 1248.6991 | 475.7365 | 424.7046 | 421.9189 | 424.6812 | 419.277 | 388.2734 | 393.9811
1321.6905 | 1249.6905 | 475.8146 | 424.7574 | 421.9725 | 424.7469 | 419.2945 | 388.3003 | 393.9324
1322.6919 | 1250.6919 | 475.7506 | 424.7717 | 422.0309 | 424.8008 | 419.3043 | 388.3214 | 393.9241
1323.6934 | 1251.6934 | 475.7444 | 424.787 | 422.0699 | 424.8425 | 419.3105 | 388.3417 | 393.9093
1324.6948 | 1252.6948 | 475.6691 | 424.7849 | 422.1092 | 424.9023 | 419.3137 | 388.3594 | 393.9318
1325.6963 | 1253.6963 | 475.655 | 424.7921 | 422.1766 | 424.9701 | 419.3061 | 388.3742 | 393.9384
1326.6977 | 1254.6977 | 475.5095 | 424.803 | 422.2215 | 425.0141 | 419.2897 | 388.3996 | 393.9547
1327.6891 | 1255.6891 | 475.6331 | 424.8074 | 422.2579 | 425.0432 | 419.2781 | 388.4226 | 394.0059
1328.7006 | 1256.7006 | 475.6336 | 424.8001 | 422.2988 | 425.094 | 419.2726 | 388.439 | 394.0545
1329.692 | 1257.692 | 475.6571 | 424.7707 | 422.3399 | 425.165 | 419.2849 | 388.455 | 394.0949
1330.6934 | 1258.6934 | 475.7062 | 424.7433 | 422.3825 | 425.222 | 419.2789 | 388.4749 | 394.1537
1331.6949 | 1259.6949 | 475.7537 | 424.7063 | 422.4191 | 425.2791 | 419.2959 | 388.4982 | 394.2056
1332.6963 | 1260.6963 | 475.7093 | 424.6902 | 422.4426 | 425.338 | 419.2962 | 388.5218 | 394.2526
1333.6978 | 1261.6978 | 475.5868 | 424.6869 | 422.4927 | 425.3615 | 419.2931 | 388.54 | 394.2913
1334.6992 | 1262.6992 | 475.5947 | 424.7172 | 422.5484 | 425.3742 | 419.2982 | 388.567 | 394.2984
1335.7006 | 1263.7006 | 475.6632 | 424.709 | 422.5946 | 425.4563 | 419.2982 | 388.5969 | 394.3158
1336.6921 | 1264.6921 | 475.8013 | 424.6741 | 422.6216 | 425.5119 | 419.3069 | 388.6263 | 394.3056
1337.6935 | 1265.6935 | 475.8673 | 424.653 | 422.6622 | 425.5469 | 419.3194 | 388.6381 | 394.3269
1338.6949 | 1266.6949 | 475.8554 | 424.606 | 422.7014 | 425.6043 | 419.3289 | 388.6629 | 394.3358
1339.6964 | 1267.6964 | 475.8402 | 424.5825 | 422.7409 | 425.6691 | 419.3189 | 388.6845 | 394.371
1340.6978 | 1268.6978 | 475.7452 | 424.549 | 422.7826 | 425.7321 | 419.323 | 388.7096 | 394.4099
1341.6993 | 1269.6993 | 475.6583 | 424.5441 | 422.8221 | 425.7803 | 419.3356 | 388.721 | 394.4592
1342.6907 | 1270.6907 | 475.5269 | 424.5535 | 422.8603 | 425.8217 | 419.368 | 388.7322 | 394.463
1343.6921 | 1271.6921 | 475.4278 | 424.5333 | 422.8898 | 425.8733 | 419.3896 | 388.7465 | 394.4898
1344.6936 | 1272.6936 | 475.5563 | 424.5035 | 422.9216 | 425.9043 | 419.4232 | 388.7535 | 394.5304 | Time of first failure
1345.695 | 1273.695 | 475.4645 | 424.4896 | 422.975 | 425.9733 | 419.4377 | 388.7649 | 394.5615 | 1273 | 0
1346.6965 | 1274.6965 | 475.306 | 424.4937 | 423.0223 | 426.03 | 419.4608 | 388.783 | 394.59 | 1273 | 900
1347.6979 | 1275.6979 | 475.2737 | 424.4702 | 423.065 | 426.1096 | 419.4939 | 388.8015 | 394.6256
1348.6993 | 1276.6993 | 475.4427 | 424.4768 | 423.0854 | 426.2062 | 419.5172 | 388.8183 | 394.6576
1349.6908 | 1277.6908 | 475.5295 | 424.4111 | 423.0829 | 426.2349 | 419.54 | 388.8381 | 394.7791
1350.6922 | 1278.6922 | 475.7355 | 424.3321 | 423.0701 | 426.2303 | 419.5721 | 388.831 | 394.9831
1351.6936 | 1279.6936 | 475.8584 | 424.1925 | 422.941 | 426.1936 | 419.6039 | 388.7665 | 395.3101
1352.6951 | 1280.6951 | 476.1104 | 423.7862 | 422.8854 | 426.2447 | 419.6564 | 388.7355 | 395.7666
1353.6965 | 1281.6965 | 476.4949 | 423.6172 | 423.037 | 426.3963 | 419.7796 | 388.7303 | 396.3883
1354.698 | 1282.698 | 476.881 | 423.5637 | 423.142 | 426.6305 | 419.9435 | 388.7617 | 397.2491
1355.6994 | 1283.6994 | 477.3821 | 423.7098 | 423.301 | 426.9064 | 420.2951 | 388.7884 | 398.2608
1356.7008 | 1284.7008 | 477.9518 | 423.8317 | 423.4259 | 427.1426 | 420.7618 | 388.8469 | 399.388
1357.6923 | 1285.6923 | 478.5103 | 423.9269 | 423.6218 | 427.4305 | 421.4264 | 388.9433 | 400.7483
1358.6937 | 1286.6937 | 479.1693 | 424.1142 | 423.7717 | 427.7579 | 422.2931 | 389.0732 | 401.9979
1359.6951 | 1287.6951 | 479.7039 | 424.3486 | 423.9756 | 428.2041 | 423.515 | 389.2146 | 403.4061
1360.6966 | 1288.6966 | 479.9794 | 424.7195 | 424.1629 | 428.6742 | 424.9336 | 389.4042 | 404.8546
1361.698 | 1289.698 | 480.1014 | 424.8596 | 424.2826 | 429.2141 | 426.5748 | 389.6531 | 406.5458
1362.6995 | 1290.6995 | 480.3119 | 425.3462 | 424.5438 | 429.7069 | 428.3087 | 389.9295 | 408.5851
1363.6909 | 1291.6909 | 480.4115 | 425.5568 | 424.6885 | 430.5528 | 430.205 | 390.2624 | 410.5407
1364.6923 | 1292.6923 | 480.5613 | 425.981 | 424.9627 | 431.4792 | 432.1987 | 390.5726 | 412.7482
1365.6938 | 1293.6938 | 480.4156 | 426.32 | 425.2802 | 432.3275 | 434.2723 | 390.8897 | 415.7448
1366.6952 | 1294.6952 | 480.2775 | 426.7607 | 425.4255 | 433.2576 | 436.5165 | 391.3114 | 418.881
1367.6967 | 1295.6967 | 480.1256 | 427.2506 | 425.8268 | 434.1117 | 438.7353 | 391.693 | 423.5225
1368.6981 | 1296.6981 | 479.9104 | 427.7932 | 426.168 | 435.1099 | 440.9568 | 392.1321 | 429.103
1369.6995 | 1297.6995 | 479.6535 | 428.3595 | 426.5455 | 435.8897 | 443.2135 | 392.5457 | 434.1241
1370.701 | 1298.701 | 479.2983 | 428.949 | 427.0153 | 436.5651 | 445.4777 | 393.024 | 439.418
1371.6924 | 1299.6924 | 478.8603 | 429.501 | 427.4369 | 437.4446 | 447.8038 | 393.566 | 444.9651
1372.6938 | 1300.6938 | 478.4102 | 430.2001 | 427.9888 | 438.3075 | 450.0198 | 394.1895 | 450.5141
1373.6953 | 1301.6953 | 477.9845 | 430.6625 | 428.5163 | 439.2041 | 452.3144 | 394.8657 | 455.8358
1374.6967 | 1302.6967 | 477.572 | 431.2774 | 429.0298 | 439.9982 | 454.6923 | 395.6766 | 461.2663
1375.6982 | 1303.6982 | 477.1165 | 431.9638 | 429.4772 | 441.0694 | 456.9801 | 396.5614 | 466.8724
1376.6996 | 1304.6996 | 476.709 | 432.4982 | 429.989 | 442.1858 | 458.9747 | 397.4406 | 472.6692
1377.701 | 1305.701 | 476.2904 | 433.297 | 430.5372 | 443.2879 | 460.8572 | 398.323 | 477.9304
1378.6925 | 1306.6925 | 475.7646 | 433.9365 | 431.1211 | 444.2776 | 462.8822 | 399.3437 | 483.3543
1379.6939 | 1307.6939 | 475.1951 | 434.3353 | 431.894 | 445.4497 | 464.768 | 400.4232 | 488.1933
1380.6953 | 1308.6953 | 474.6782 | 434.9605 | 432.4741 | 446.4703 | 466.8095 | 401.5657 | 492.1491
1381.6968 | 1309.6968 | 474.2294 | 435.5261 | 432.926 | 447.1991 | 468.7049 | 402.8707 | 495.6709
1382.6982 | 1310.6982 | 473.7395 | 436.2464 | 433.4828 | 447.9875 | 470.9099 | 404.334 | 498.505
1383.6997 | 1311.6997 | 473.1848 | 436.7834 | 434.0388 | 448.7522 | 472.7771 | 405.931 | 500.7466
1384.6911 | 1312.6911 | 472.7301 | 437.2264 | 434.6556 | 449.3586 | 474.5671 | 407.618 | 502.7522
1385.6925 | 1313.6925 | 472.3546 | 437.7205 | 435.3551 | 449.6746 | 476.4053 | 409.4548 | 504.3632
1386.694 | 1314.694 | 471.9734 | 438.3112 | 435.905 | 450.124 | 477.8458 | 411.3027 | 505.8266
1387.6954 | 1315.6954 | 471.4934 | 439.0114 | 436.454 | 451.344 | 479.1624 | 413.2845 | 506.991
1388.6968 | 1316.6968 | 470.9902 | 439.6646 | 437.0646 | 452.2284 | 480.5929 | 415.2504 | 508.0284
1389.6983 | 1317.6983 | 470.4868 | 440.3848 | 437.6267 | 452.8647 | 481.9395 | 417.2327 | 509.0147
1390.6897 | 1318.6897 | 469.9366 | 441.0928 | 438.162 | 453.5172 | 482.933 | 419.2346 | 509.7334
1391.6912 | 1319.6912 | 469.4177 | 441.7872 | 438.8139 | 454.1402 | 484.2606 | 421.1601 | 510.7233
1392.6926 | 1320.6926 | 468.899 | 442.5473 | 439.5425 | 454.7215 | 485.052 | 423.0706 | 511.4915
1393.694 | 1321.694 | 468.3514 | 443.2409 | 440.2507 | 454.7718 | 486.2279 | 424.999 | 512.2516
1394.6955 | 1322.6955 | 468.0224 | 443.961 | 440.8989 | 455.8496 | 487.4286 | 426.8209 | 512.7909
1395.6969 | 1323.6969 | 467.546 | 444.6818 | 441.5163 | 457.5739 | 488.1303 | 428.4562 | 513.1461
1396.6984 | 1324.6984 | 466.9922 | 445.2535 | 442.4106 | 458.2939 | 488.5914 | 430.2015 | 514.1487
1397.6898 | 1325.6898 | 466.3859 | 445.9212 | 443.0773 | 458.9591 | 489.1371 | 431.9039 | 514.6277
1398.6912 | 1326.6912 | 465.7765 | 446.5232 | 443.6657 | 459.0293 | 489.717 | 433.5182 | 515.4565
1399.6927 | 1327.6927 | 465.2259 | 447.1992 | 444.5766 | 459.4059 | 490.4336 | 435.1747 | 516.0108
1400.6941 | 1328.6941 | 464.7165 | 447.8692 | 445.2579 | 460.1966 | 490.979 | 436.7021 | 516.9815
1401.6955 | 1329.6955 | 464.2764 | 448.6226 | 445.8235 | 459.9464 | 491.5636 | 438.2367 | 517.5623
1402.697 | 1330.697 | 463.947 | 449.6402 | 446.4063 | 460.2565 | 492.1488 | 439.8392 | 518.1758
1403.6984 | 1331.6984 | 463.5617 | 450.3993 | 447.2096 | 461.6622 | 491.9314 | 441.2062 | 518.7846
1404.6999 | 1332.6999 | 463.1122 | 450.926 | 448.1109 | 461.8469 | 491.4843 | 442.6137 | 519.1517
1405.6913 | 1333.6913 | 462.7936 | 451.944 | 448.8846 | 462.541 | 492.1041 | 444.1326 | 519.4237
1406.6927 | 1334.6927 | 462.3252 | 452.8554 | 449.7081 | 462.7353 | 492.6081 | 445.6767 | 519.6765
1407.6942 | 1335.6942 | 461.8209 | 454.1024 | 450.57 | 463.0205 | 493.3577 | 447.0985 | 519.6327
1408.6956 | 1336.6956 | 461.25 | 454.9793 | 451.3379 | 463.5583 | 494.1186 | 448.9163 | 519.7765
1409.697 | 1337.697 | 460.7901 | 455.358 | 452.1487 | 464.0811 | 494.2735 | 450.6158 | 519.936
1410.6985 | 1338.6985 | 460.3619 | 456.6024 | 452.6055 | 464.0125 | 494.8991 | 451.7614 | 520.1981
1411.6899 | 1339.6899 | 459.9865 | 457.3988 | 453.2388 | 464.3699 | 495.6955 | 452.9352 | 520.2373
1412.6914 | 1340.6914 | 459.5554 | 458.4944 | 453.9646 | 464.8765 | 496.5396 | 453.9816 | 518.9068
1413.6928 | 1341.6928 | 459.1926 | 459.2419 | 454.8772 | 464.9221 | 497.3664 | 454.8783 | 518.3609
1414.6942 | 1342.6942 | 458.8593 | 460.2302 | 456.0199 | 465.4587 | 498.2552 | 456.363 | 518.0249
1415.6957 | 1343.6957 | 458.5514 | 460.7444 | 457.0088 | 466.0518 | 499.2083 | 458.0158 | 517.6176
1416.6971 | 1344.6971 | 458.1599 | 461.6817 | 458.5 | 466.2993 | 499.9484 | 459.1804 | 517.3933
1417.6986 | 1345.6986 | 457.726 | 462.7663 | 459.3176 | 466.7769 | 500.5493 | 460.1408 | 517.2304
1418.7 | 1346.7 | 457.1967 | 463.0809 | 459.6882 | 467.2925 | 501.4945 | 462.0763 | 517.2329
1419.6914 | 1347.6914 | 456.6207 | 463.4543 | 460.8133 | 467.5805 | 502.0708 | 463.465 | 517.2191
1420.6929 | 1348.6929 | 456.2585 | 463.9028 | 461.7149 | 467.8278 | 502.6957 | 464.9234 | 516.9051
1421.6943 | 1349.6943 | 455.9199 | 465.1309 | 462.3817 | 467.9696 | 503.4984 | 466.0101 | 516.8833
1422.6957 | 1350.6957 | 455.5937 | 465.8105 | 463.6207 | 467.813 | 504.029 | 466.7262 | 516.9184
1423.6972 | 1351.6972 | 455.2837 | 466.144 | 464.2943 | 467.2921 | 504.6628 | 467.1807 | 517.0218
1424.6986 | 1352.6986 | 454.8688 | 466.366 | 464.5729 | 467.7088 | 505.3794 | 468.1757 | 517.2542
1425.69 | 1353.69 | 454.3666 | 467.5895 | 465.3748 | 467.732 | 505.7544 | 468.5603 | 517.7293
1426.6915 | 1354.6915 | 454.1289 | 468.448 | 466.1616 | 468.2897 | 506.502 | 469.3682 | 517.8713
1427.6929 | 1355.6929 | 453.6418 | 469.0974 | 466.6183 | 469.0631 | 507.3963 | 470.2655 | 517.9022
1428.6944 | 1356.6944 | 453.1526 | 469.5066 | 466.9748 | 469.7418 | 507.7769 | 470.5261 | 517.6711
1429.6958 | 1357.6958 | 452.6111 | 469.9381 | 467.9892 | 469.6938 | 508.4667 | 471.2816 | 517.339
1430.6972 | 1358.6972 | 452.0303 | 470.2336 | 468.179 | 470.2707 | 509.2461 | 471.8759 | 517.2886
1431.6987 | 1359.6987 | 451.5213 | 471.0501 | 468.7124 | 470.3029 | 509.7182 | 472.457 | 516.0469
1432.6901 | 1360.6901 | 451.0543 | 472.0563 | 469.3111 | 470.6082 | 510.1486 | 472.5199 | 514.0743
1433.6915 | 1361.6915 | 450.5527 | 473.6867 | 469.4245 | 471.5677 | 510.6094 | 473.2693 | 511.8055
1434.693 | 1362.693 | 450.0942 | 474.0033 | 470.1003 | 472.109 | 510.8974 | 473.9661 | 510.3773
1435.6944 | 1363.6944 | 449.549 | 474.348 | 470.6746 | 472.3967 | 511.3717 | 473.9545 | 508.5677
1436.6959 | 1364.6959 | 449.0525 | 474.5485 | 470.7375 | 472.5542 | 511.9079 | 474.7214 | 507.2654
1437.6973 | 1365.6973 | 448.5374 | 474.8086 | 471.09 | 472.9693 | 511.3569 | 474.8376 | 505.9252
1438.6987 | 1366.6987 | 447.968 | 475.1873 | 471.6683 | 473.2815 | 511.7365 | 474.9248 | 504.984
1439.7002 | 1367.7002 | 447.4556 | 475.4699 | 471.9117 | 473.6733 | 512.6115 | 474.9596 | 504.1947
1440.6916 | 1368.6916 | 446.9688 | 476.0506 | 472.3744 | 474.5102 | 513.1887 | 475.6609 | 502.9516
1441.6931 | 1369.6931 | 446.4957 | 476.6698 | 473.1421 | 475.0393 | 513.7374 | 476.3077 | 502.0585
1442.6945 | 1370.6945 | 446.1197 | 476.9657 | 474.2357 | 475.5123 | 513.4476 | 475.996 | 501.1842
1443.6959 | 1371.6959 | 445.7205 | 477.8234 | 474.4695 | 476.0036 | 513.642 | 476.2818 | 500.7367
1444.6974 | 1372.6974 | 445.2286 | 478.2266 | 474.5951 | 476.4364 | 513.7302 | 476.2051 | 500.3594
1445.6988 | 1373.6988 | 444.7986 | 478.8059 | 475.1048 | 477.162 | 514.4445 | 476.7833 | 499.7837
1446.7003 | 1374.7003 | 444.3463 | 479.2074 | 475.5723 | 477.6664 | 514.042 | 476.8824 | 499.1476
1447.6917 | 1375.6917 | 443.9143 | 479.5604 | 475.495 | 478.1369 | 514.1145 | 477.5064 | 498.9771
1448.6931 | 1376.6931 | 443.5626 | 479.8653 | 476.0102 | 478.7883 | 514.7928 | 477.5123 | 498.5047
1449.6946 | 1377.6946 | 443.3101 | 480.2543 | 476.4268 | 479.5783 | 515.2977 | 477.4042 | 498.4451
1450.696 | 1378.696 | 443.0169 | 480.7771 | 476.8434 | 480.2889 | 516.0681 | 477.2889 | 498.6929
1451.6974 | 1379.6974 | 442.5681 | 481.2501 | 477.3588 | 480.9021 | 515.8253 | 477.3313 | 498.7053
1452.6989 | 1380.6989 | 442.0336 | 481.6608 | 477.8562 | 481.4093 | 516.3344 | 477.6355 | 498.2938
1453.7003 | 1381.7003 | 441.5474 | 482.2722 | 478.6197 | 481.8343 | 516.7693 | 477.7209 | 498.0127
1454.6917 | 1382.6917 | 441.0977 | 482.7354 | 479.2605 | 482.3825 | 516.5954 | 477.2354 | 497.6637
1455.6932 | 1383.6932 | 440.6986 | 483.2678 | 479.7427 | 482.7616 | 516.9316 | 476.6683 | 497.1732
1456.6946 | 1384.6946 | 440.2688 | 483.6946 | 480.2366 | 483.2446 | 516.7036 | 476.6081 | 497.0281
1457.6961 | 1385.6961 | 439.7484 | 484.2016 | 480.8526 | 483.9011 | 516.5855 | 476.6793 | 496.6061
1458.6975 | 1386.6975 | 439.2046 | 485.0203 | 481.3681 | 484.4732 | 516.7924 | 476.8156 | 496.4601
1459.6989 | 1387.6989 | 438.6907 | 485.9228 | 481.8952 | 484.9486 | 516.9906 | 477.1692 | 496.5669
1460.6904 | 1388.6904 | 438.1978 | 486.8757 | 482.1513 | 485.7996 | 517.2984 | 477.0841 | 496.325
1461.6918 | 1389.6918 | 437.8798 | 487.8025 | 482.4072 | 486.4356 | 517.4175 | 476.7623 | 495.9111
1462.6932 | 1390.6932 | 437.6573 | 488.5601 | 482.7462 | 487.1044 | 517.5667 | 476.4875 | 495.9032
1463.6947 | 1391.6947 | 437.3065 | 489.2352 | 483.0667 | 487.6026 | 517.8022 | 476.7309 | 495.5474
1464.6961 | 1392.6961 | 436.8419 | 489.7552 | 483.412 | 488.231 | 517.7785 | 477.0511 | 495.5131
1465.6976 | 1393.6976 | 436.3818 | 490.5113 | 483.8271 | 488.8459 | 518.011 | 476.9212 | 495.2132
1466.699 | 1394.699 | 435.8467 | 491.0431 | 484.247 | 489.6023 | 518.281 | 477.2759 | 495.4678
1467.6904 | 1395.6904 | 435.4163 | 491.5518 | 484.5342 | 490.2909 | 519.2679 | 477.099 | 495.4505
1468.6919 | 1396.6919 | 435.058 | 491.6753 | 485.1046 | 490.8281 | 519.063 | 477.0993 | 495.0672
1469.6933 | 1397.6933 | 434.642 | 491.8351 | 485.8218 | 491.3473 | 519.5669 | 477.1849 | 494.9248
1470.6948 | 1398.6948 | 434.1875 | 492.1354 | 486.586 | 491.9489 | 519.4388 | 477.3409 | 494.9101
1471.6962 | 1399.6962 | 433.7345 | 492.6611 | 487.1637 | 492.4422 | 519.4968 | 477.9459 | 495.1642
1472.6976 | 1400.6976 | 433.4476 | 493.1204 | 487.7349 | 493.0692 | 519.6502 | 478.39 | 495.3474
1473.6991 | 1401.6991 | 433.2002 | 493.5151 | 488.264 | 493.6863 | 519.778 | 479.2285 | 495.6494
1474.6905 | 1402.6905 | 432.8975 | 494.1874 | 488.822 | 494.2539 | 520.1647 | 479.7437 | 495.8334
1475.6919 | 1403.6919 | 432.5449 | 494.5585 | 489.1857 | 494.8752 | 520.8895 | 479.3196 | 495.8429
1476.6934 | 1404.6934 | 432.1523 | 494.8792 | 489.638 | 495.5943 | 521.3328 | 479.7842 | 496.252
1477.6948 | 1405.6948 | 431.7008 | 495.1533 | 490.067 | 496.3336 | 521.8026 | 480.3548 | 496.0605
1478.6963 | 1406.6963 | 431.2804 | 495.42 | 490.3634 | 497.1122 | 521.4605 | 480.8472 | 496.6026
1479.6977 | 1407.6977 | 430.7571 | 495.6999 | 490.6207 | 497.885 | 521.3426 | 480.8272 | 496.6014
1480.6991 | 1408.6991 | 430.3933 | 496.2406 | 491.012 | 498.6467 | 521.4315 | 481.3527 | 496.8841
1481.7006 | 1409.7006 | 430.0702 | 497.1266 | 491.415 | 499.3925 | 522.0055 | 481.2874 | 496.8702
1482.692 | 1410.692 | 429.665 | 498.3499 | 491.8757 | 500.0176 | 522.4177 | 481.4964 | 496.7421
1483.6934 | 1411.6934 | 429.2407 | 499.1906 | 492.2254 | 500.7359 | 522.8068 | 481.7204 | 496.9426
1484.6949 | 1412.6949 | 428.8155 | 499.9506 | 492.6342 | 501.3892 | 523.4351 | 481.3825 | 496.6152
1485.6963 | 1413.6963 | 428.3353 | 500.5266 | 492.9854 | 501.9925 | 524.0635 | 480.5613 | 497.3356
1486.6978 | 1414.6978 | 427.8534 | 501.0473 | 493.3194 | 502.5667 | 524.682 | 480.1545 | 498.1832
1487.6992 | 1415.6992 | 427.3995 | 501.783 | 493.7896 | 503.1574 | 525.4391 | 480.6764 | 498.2749
1488.7006 | 1416.7006 | 426.9126 | 502.5612 | 494.1836 | 503.6479 | 526.1647 | 479.968 | 498.5613
1489.7021 | 1417.7021 | 426.4843 | 503.0291 | 494.4595 | 504.2263 | 527.0001 | 479.8102 | 498.1732
1490.6935 | 1418.6935 | 425.9881 | 503.6924 | 494.8972 | 504.749 | 527.6892 | 479.431 | 498.9901
1491.695 | 1419.695 | 425.5247 | 504.3022 | 495.3691 | 505.2539 | 528.5645 | 479.0379 | 499.4085
1492.6964 | 1420.6964 | 425.158 | 504.7648 | 495.7934 | 505.7655 | 529.7084 | 478.8701 | 499.3758
1493.6978 | 1421.6978 | 424.8336 | 505.5489 | 496.1832 | 506.2564 | 531.0048 | 478.4243 | 499.4215
1494.6993 | 1422.6993 | 424.5305 | 506.0517 | 496.4785 | 506.6448 | 532.0534 | 477.6342 | 499.9934
1495.6907 | 1423.6907 | 424.2827 | 506.6138 | 496.9052 | 507.0709 | 533.3571 | 476.3756 | 500.8393
1496.6921 | 1424.6921 | 423.8528 | 507.0735 | 497.3709 | 507.6201 | 534.8622 | 476.4222 | 501.3305
1497.6936 | 1425.6936 | 423.3773 | 507.6733 | 497.8077 | 508.0502 | 536.2298 | 475.8978 | 501.5621
1498.695 | 1426.695 | 422.9024 | 508.3054 | 498.2141 | 508.4108 | 537.487 | 475.754 | 502.0629
1499.6965 | 1427.6965 | 422.4963 | 508.7538 | 498.6416 | 508.8467 | 538.6084 | 475.9509 | 501.8784
1500.6979 | 1428.6979 | 422.0177 | 509.2058 | 499.0234 | 509.2119 | 539.3005 | 476.5437 | 502.3398
1501.6993 | 1429.6993 | 421.5817 | 509.8267 | 499.437 | 509.6975 | 540.0376 | 476.4583 | 502.5065
1502.7008 | 1430.7008 | 421.2676 | 510.2678 | 499.7831 | 510.1053 | 540.7485 | 476.7073 | 502.5768
1503.6922 | 1431.6922 | 420.9539 | 510.8141 | 500.0402 | 510.5928 | 541.8185 | 476.7872 | 502.865
1504.6936 | 1432.6936 | 420.4987 | 511.306 | 500.5136 | 511.0923 | 542.7576 | 477.2926 | 502.6952
1505.6951 | 1433.6951 | 420.1011 | 511.7632 | 500.929 | 511.5323 | 543.6448 | 477.6471 | 502.8095
1506.6965 | 1434.6965 | 419.6682 | 512.37 | 501.2036 | 511.9025 | 544.0701 | 478.3113 | 503.1217
1507.698 | 1435.698 | 419.1283 | 512.7086 | 501.4934 | 512.265 | 544.7325 | 478.8438 | 503.3197
1508.6994 | 1436.6994 | 418.7139 | 513.1053 | 501.9417 | 512.6863 | 545.3896 | 478.8528 | 503.328
1509.7008 | 1437.7008 | 418.2756 | 513.4873 | 502.2795 | 512.984 | 545.8289 | 479.2371 | 503.3604
1510.6923 | 1438.6923 | 417.7951 | 513.7862 | 502.6298 | 513.4101 | 546.4396 | 479.4466 | 503.7106
1511.6937 | 1439.6937 | 417.2825 | 514.135 | 503.0335 | 513.6659 | 547.0296 | 479.7966 | 503.8926
1512.6951 | 1440.6951 | 416.8635 | 514.6196 | 503.3267 | 513.8547 | 547.4923 | 480.2415 | 503.6554
1513.7066 | 1441.7066 | 416.2656 | 514.9351 | 503.5801 | 514.0031 | 547.954 | 480.8209 | 503.9882
1514.698 | 1442.698 | 415.7342 | 515.4881 | 503.7102 | 514.197 | 548.5261 | 481.4091 | 504.2469
1515.6995 | 1443.6995 | 415.2831 | 515.8511 | 503.929 | 514.3617 | 548.9585 | 481.9961 | 504.5718
1516.6909 | 1444.6909 | 414.9549 | 516.1052 | 504.213 | 514.4482 | 549.274 | 482.5141 | 504.7293
1517.6923 | 1445.6923 | 414.5625 | 516.4754 | 504.6158 | 514.6901 | 549.1582 | 482.9967 | 504.7003
1518.6938 | 1446.6938 | 414.0596 | 516.9104 | 504.8307 | 514.8621 | 549.4465 | 483.4607 | 504.8144
1519.6952 | 1447.6952 | 413.5322 | 517.3447 | 505.1184 | 515.0718 | 549.679 | 484.0762 | 504.9244
1520.6967 | 1448.6967 | 412.9776 | 517.6564 | 505.4098 | 515.3922 | 549.8616 | 484.5681 | 505.0331
1521.6981 | 1449.6981 | 412.525 | 518.1464 | 505.6988 | 515.6719 | 550.1473 | 485.1298 | 505.2637
1522.6995 | 1450.6995 | 412.0217 | 518.5553 | 505.9852 | 515.9065 | 550.6765 | 485.5272 | 505.4536
1523.701 | 1451.701 | 411.6464 | 519.0618 | 506.339 | 516.1679 | 551.1043 | 486.0626 | 505.2026
1524.6924 | 1452.6924 | 411.258 | 519.4893 | 506.6876 | 516.4549 | 551.4879 | 486.4155 | 505.6939
1525.6938 | 1453.6938 | 410.7957 | 519.9042 | 507.0167 | 516.782 | 551.9242 | 487.0357 | 505.6324
1526.6953 | 1454.6953 | 410.3986 | 520.2792 | 507.323 | 517.044 | 552.4274 | 487.6 | 505.846
1527.6967 | 1455.6967 | 409.9381 | 520.7392 | 507.6285 | 517.3046 | 552.8184 | 487.9372 | 505.8867
1528.6982 | 1456.6982 | 409.4112 | 521.0972 | 507.9735 | 517.5723 | 553.088 | 488.3627 | 505.9882
1529.6996 | 1457.6996 | 408.9126 | 521.3644 | 508.301 | 517.8811 | 553.2308 | 488.8842 | 506.2433
1530.701 | 1458.701 | 408.4804 | 521.7142 | 508.6098 | 518.2002 | 553.3661 | 489.3429 | 506.0043
1531.6925 | 1459.6925 | 408.0391 | 522.206 | 508.9914 | 518.5482 | 553.5817 | 489.7087 | 506.3228
1532.6939 | 1460.6939 | 407.5361 | 522.5492 | 509.2805 | 518.8821 | 553.8287 | 490.1979 | 506.2858
1533.6953 | 1461.6953 | 407.0751 | 522.9115 | 509.5669 | 519.2384 | 554.1676 | 490.4356 | 506.4376
1534.6968 | 1462.6968 | 406.7264 | 523.4881 | 509.941 | 519.5686 | 554.5326 | 491.1572 | 506.8225
1535.6982 | 1463.6982 | 406.2451 | 523.9811 | 510.2403 | 519.8369 | 554.9502 | 491.7043 | 506.8659
1536.6997 | 1464.6997 | 405.7964 | 524.3971 | 510.6006 | 520.1102 | 555.3627 | 491.7051 | 506.8066
1537.6911 | 1465.6911 | 405.3113 | 524.8544 | 510.9869 | 520.4219 | 555.8399 | 492.0538 | 506.6803
1538.6925 | 1466.6925 | 404.9042 | 525.3381 | 511.3991 | 520.6925 | 556.3904 | 492.4878 | 506.8623
1539.694 | 1467.694 | 404.4261 | 525.8002 | 511.7978 | 520.9665 | 556.9103 | 492.6755 | 506.9621
1540.6954 | 1468.6954 | 403.9439 | 526.211 | 512.2321 | 521.2549 | 557.3896 | 493.372 | 506.7701
1541.6969 | 1469.6969 | 403.4881 | 526.6827 | 512.657 | 521.5137 | 557.8798 | 493.718 | 506.5473
1542.6983 | 1470.6983 | 403.1021 | 527.0651 | 513.0014 | 521.8358 | 558.3123 | 494.1338 | 506.7241
1543.6997 | 1471.6997 | 402.6107 | 527.5516 | 513.5067 | 522.1075 | 558.7521 | 494.189 | 506.4748
1544.6912 | 1472.6912 | 402.1292 | 527.9345 | 513.9171 | 522.3612 | 559.0014 | 494.854 | 506.6669
1545.6926 | 1473.6926 | 401.6555 | 528.3322 | 514.3048 | 522.6617 | 559.1847 | 495.161 | 506.3775
1546.694 | 1474.694 | 401.157 | 528.8438 | 514.7004 | 522.908 | 559.3304 | 495.8318 | 506.2885
1547.6955 | 1475.6955 | 400.5649 | 529.2477 | 515.0661 | 523.1749 | 559.4495 | 496.34 | 506.285
1548.6969 | 1476.6969 | 400.2415 | 529.6808 | 515.4141 | 523.4303 | 559.6109 | 496.7949 | 506.2619
1549.6984 | 1477.6984 | 399.8727 | 530.0348 | 515.8461 | 523.65 | 559.8869 | 496.8648 | 506.2367
1550.6998 | 1478.6998 | 399.3841 | 530.459 | 516.2318 | 523.9229 | 560.2261 | 497.1932 | 506.1901
1551.7012 | 1479.7012 | 398.9513 | 530.8653 | 516.6314 | 524.2089 | 560.5738 | 497.7363 | 505.7747
1552.6927 | 1480.6927 | 398.4282 | 531.2203 | 516.968 | 524.5319 | 560.9725 | 498.0381 | 505.728
1553.6941 | 1481.6941 | 397.8913 | 531.5953 | 517.325 | 524.7941 | 561.3402 | 498.3982 | 505.9267
1554.6955 | 1482.6955 | 397.5598 | 532.0006 | 517.7186 | 525.0229 | 561.7059 | 498.439 | 506.0567
1555.697 | 1483.697 | 397.2159 | 532.4599 | 518.0806 | 525.2818 | 562.0622 | 498.6667 | 505.9889
1556.6984 | 1484.6984 | 396.7698 | 532.8285 | 518.4508 | 525.4849 | 562.3787 | 499.0783 | 505.7694
1557.6999 | 1485.6999 | 396.3234 | 533.2139 | 518.7845 | 525.7318 | 562.6227 | 499.4066 | 505.8247
1558.6913 | 1486.6913 | 395.8804 | 533.5183 | 519.1348 | 526.0048 | 562.7249 | 499.56 | 505.9072
1559.6927 | 1487.6927 | 395.453 | 533.9319 | 519.4353 | 526.2787 | 562.9106 | 499.8933 | 505.9734
1560.6942 | 1488.6942 | 394.9363 | 534.319 | 519.7505 | 526.5248 | 563.1291 | 500.0507 | 505.8138
1561.6956 | 1489.6956 | 394.4369 | 534.7476 | 520.0604 | 526.768 | 563.2824 | 500.2177 | 505.8867
1562.697 | 1490.697 | 394.0464 | 534.9614 | 520.2937 | 527.0357 | 563.5431 | 500.4901 | 506.2325
1563.6985 | 1491.6985 | 393.6461 | 535.3655 | 520.5538 | 527.2547 | 563.9583 | 500.8143 | 506.2537
1564.6899 | 1492.6899 | 393.2725 | 535.8206 | 520.8537 | 527.5375 | 564.3698 | 500.8463 | 506.3757
1565.6914 | 1493.6914 | 392.7616 | 536.1855 | 521.1429 | 527.8484 | 564.7391 | 501.2435 | 506.4099
1566.6928 | 1494.6928 | 392.3428 | 536.5502 | 521.4289 | 528.1256 | 565.1337 | 501.3469 | 506.552
1567.6942 | 1495.6942 | 391.8238 | 537.0548 | 521.6766 | 528.4115 | 565.4774 | 501.3321 | 506.5015
1568.6957 | 1496.6957 | 391.2288 | 537.4634 | 521.9948 | 528.7279 | 565.8133 | 501.8688 | 506.8216
1569.6971 | 1497.6971 | 390.748 | 538.1236 | 522.2415 | 529.0851 | 566.1657 | 501.6016 | 507.0089
1570.6986 | 1498.6986 | 390.3869 | 538.4791 | 522.4984 | 529.4253 | 566.4951 | 501.8165 | 507.2212
1571.7 | 1499.7 | 390.0208 | 538.8456 | 522.7475 | 529.7741 | 566.9254 | 502.1989 | 506.7147
1572.6914 | 1500.6914 | 389.5798 | 539.379 | 523.0677 | 530.1329 | 567.3424 | 502.4953 | 506.7691
1573.7029 | 1501.7029 | 389.0956 | 539.7149 | 523.2952 | 530.5237 | 567.686 | 502.6502 | 506.9632
1574.6943 | 1502.6943 | 388.6432 | 540.1689 | 523.5676 | 530.9131 | 568.0434 | 502.8906 | 507.363
1575.6957 | 1503.6957 | 388.1087 | 540.5627 | 523.8117 | 531.2673 | 568.4931 | 503.1175 | 507.4309
1576.6972 | 1504.6972 | 387.6058 | 540.8882 | 524.0419 | 531.66 | 568.8748 | 503.1158 | 507.6031
1577.6986 | 1505.6986 | 387.123 | 541.0626 | 524.29 | 532.011 | 569.0679 | 503.2024 | 507.9359
1578.7001 | 1506.7001 | 386.6351 | 541.7021 | 524.6238 | 532.3786 | 569.3438 | 503.4726 | 508.3141
1579.6915 | 1507.6915 | 386.2577 | 541.9538 | 524.9022 | 532.8484 | 569.6563 | 503.7861 | 508.3921
1580.6929 | 1508.6929 | 385.7786 | 542.4486 | 525.1701 | 533.2198 | 569.9434 | 504.1881 | 508.5321
1581.6944 | 1509.6944 | 385.304 | 542.9946 | 525.4238 | 533.5799 | 570.1421 | 504.4994 | 508.7736
1582.6958 | 1510.6958 | 384.7861 | 543.3031 | 525.6804 | 533.9388 | 570.4368 | 504.7599 | 508.8359
1583.6972 | 1511.6972 | 384.3718 | 543.8703 | 525.9851 | 534.2717 | 570.7705 | 505.0561 | 509.0577
1584.6987 | 1512.6987 | 383.88 | 544.211 | 526.2408 | 534.6489 | 571.2223 | 505.4133 | 509.3869
1585.7001 | 1513.7001 | 383.4946 | 544.4273 | 526.4724 | 534.9204 | 571.5898 | 505.8413 | 509.5761
1586.6916 | 1514.6916 | 383.039 | 544.9904 | 526.7919 | 535.2438 | 571.9259 | 506.3447 | 509.6608
1587.693 | 1515.693 | 382.5425 | 545.6481 | 527.094 | 535.4856 | 572.1889 | 506.5952 | 509.6226
1588.6944 | 1516.6944 | 382.1457 | 545.9101 | 527.3209 | 535.7347 | 572.4977 | 506.8164 | 509.6657
1589.6959 | 1517.6959 | 381.8122 | 546.4653 | 527.5908 | 535.9491 | 572.841 | 507.28 | 509.6813
1590.6973 | 1518.6973 | 381.4281 | 547.0712 | 527.8663 | 536.1083 | 573.1618 | 507.8644 | 509.6878
1591.6988 | 1519.6988 | 381.0706 | 547.2619 | 528.111 | 536.2386 | 573.5034 | 508.0029 | 509.8202
1592.7002 | 1520.7002 | 380.5656 | 547.7638 | 528.3773 | 536.386 | 573.9514 | 508.1806 | 510.0419
1593.6916 | 1521.6916 | 380.0896 | 548.0267 | 528.5979 | 536.478 | 574.3404 | 508.6646 | 510.4574
1594.6931 | 1522.6931 | 379.6179 | 548.626 | 528.8812 | 536.5158 | 574.8656 | 509.3244 | 510.7464
1595.6945 | 1523.6945 | 379.1136 | 548.8764 | 529.1111 | 536.486 | 575.4478 | 509.5619 | 511.0309
1596.6959 | 1524.6959 | 378.5811 | 549.4046 | 529.3698 | 536.4401 | 576.1046 | 509.9785 | 511.3094
1597.6974 | 1525.6974 | 378.0812 | 549.778 | 529.6336 | 536.3658 | 576.7644 | 510.0999 | 511.5177
1598.6988 | 1526.6988 | 377.4953 | 550.4463 | 529.9413 | 536.365 | 577.4444 | 510.343 | 511.7801
1599.7003 | 1527.7003 | 377.0348 | 550.7664 | 530.2048 | 536.3709 | 578.0959 | 510.6143 | 512.0684
1600.6917 | 1528.6917 | 376.5697 | 551.4609 | 530.5425 | 536.3022 | 578.6465 | 510.9208 | 512.3299
1601.6931 | 1529.6931 | 376.1494 | 551.9536 | 530.7842 | 536.2526 | 579.0984 | 511.3813 | 512.6499
1602.6946 | 1530.6946 | 375.6749 | 552.2515 | 530.9847 | 536.2471 | 579.3692 | 511.6749 | 513.0396
1603.696 | 1531.696 | 375.088 | 552.7773 | 531.3164 | 536.2158 | 579.7272 | 512.1246 | 513.3533
1604.6974 | 1532.6974 | 374.6386 | 553.1133 | 531.5177 | 536.2158 | 580.062 | 512.4004 | 513.8714
1605.6989 | 1533.6989 | 374.1374 | 553.6814 | 531.799 | 536.2812 | 580.4873 | 512.7157 | 514.502
1606.6903 | 1534.6903 | 373.6646 | 554.1039 | 532.0391 | 536.2618 | 580.9554 | 513.1771 | 515.162
1607.6917 | 1535.6917 | 373.2646 | 554.4077 | 532.3136 | 536.3202 | 581.3813 | 513.5421 | 515.8003
1608.6932 | 1536.6932 | 372.8387 | 554.651 | 532.558 | 536.4068 | 581.8185 | 513.8679 | 516.7661
1609.6946 | 1537.6946 | 372.3802 | 555.0556 | 532.7764 | 536.4315 | 582.3106 | 514.3587 | 517.6561
1610.6961 | 1538.6961 | 371.9063 | 555.6366 | 533.0592 | 536.5101 | 582.6397 | 514.6712 | 518.584
1611.6975 | 1539.6975 | 371.4465 | 556.1631 | 533.3283 | 536.6312 | 582.9369 | 515.0422 | 519.4996
1612.6989 | 1540.6989 | 371.0372 | 556.4864 | 533.5224 | 536.7153 | 583.3234 | 515.3258 | 520.3475
1613.7004 | 1541.7004 | 370.558 | 556.9604 | 533.8061 | 536.7928 | 583.6661 | 515.5984 | 521.2311
1614.6918 | 1542.6918 | 370.0834 | 557.0838 | 534.0249 | 536.91 | 584.0342 | 516.1174 | 522.0402
1615.6933 | 1543.6933 | 369.5918 | 557.375 | 534.2133 | 536.9972 | 584.4988 | 516.5545 | 522.8368
1616.6947 | 1544.6947 | 369.245 | 557.6604 | 534.38 | 537.0741 | 584.856 | 516.9459 | 523.4753
1617.6961 | 1545.6961 | 368.8764 | 558.1414 | 534.6777 | 537.2021 | 585.344 | 517.4099 | 524.1097
1618.6976 | 1546.6976 | 368.3717 | 558.5818 | 534.9138 | 537.3791 | 585.8208 | 518.0043 | 524.6954
1619.699 | 1547.699 | 367.8566 | 559.0949 | 535.2049 | 537.5426 | 586.4779 | 518.5038 | 525.2462
1620.7005 | 1548.7005 | 367.2722 | 559.4072 | 535.4189 | 537.7079 | 587.1187 | 519.0231 | 525.864
1621.6919 | 1549.6919 | 366.763 | 559.6672 | 535.6506 | 537.8339 | 587.6483 | 519.3843 | 526.5223
1622.6933 | 1550.6933 | 366.3477 | 559.9518 | 535.8642 | 537.9703 | 588.1677 | 519.7177 | 526.9105
1623.6948 | 1551.6948 | 365.8178 | 560.2804 | 536.1144 | 538.1054 | 588.6589 | 520.2282 | 527.4169
1624.6962 | 1552.6962 | 365.3501 | 560.5342 | 536.3593 | 538.2749 | 589.2146 | 520.6864 | 527.8777
1625.6976 | 1553.6976 | 364.9308 | 560.878 | 536.608 | 538.4645 | 589.7353 | 521.3904 | 528.3139
1626.6991 | 1554.6991 | 364.4246 | 561.2696 | 536.8453 | 538.6082 | 590.3358 | 521.7912 | 528.7279
1627.6905 | 1555.6905 | 363.9085 | 561.6446 | 537.0497 | 538.772 | 590.7711 | 522.1126 | 529.2926
1628.6919 | 1556.6919 | 363.3831 | 562.0016 | 537.2922 | 538.9355 | 591.0863 | 522.4693 | 529.9908
1629.6934 | 1557.6934 | 362.9075 | 562.3511 | 537.5069 | 539.0799 | 591.5439 | 522.8996 | 530.8814
1630.6948 | 1558.6948 | 362.4632 | 562.8315 | 537.7583 | 539.2535 | 592.1542 | 523.4059 | 531.4532
1631.6963 | 1559.6963 | 362.0512 | 563.1758 | 537.9765 | 539.4389 | 592.6274 | 523.9816 | 532.0802
1632.6977 | 1560.6977 | 361.5953 | 563.616 | 538.2206 | 539.6181 | 593.0702 | 524.4482 | 532.8334
1633.6991 | 1561.6991 | 361.0806 | 564.0561 | 538.4753 | 539.7991 | 593.6508 | 524.9895 | 533.4019
1634.7006 | 1562.7006 | 360.6234 | 564.4915 | 538.6729 | 540.0063 | 593.9952 | 525.4577 | 533.7913
1635.692 | 1563.692 | 360.1007 | 564.712 | 538.8996 | 540.1988 | 594.4955 | 525.9454 | 534.2143
1636.6934 | 1564.6934 | 359.5786 | 565.1074 | 539.0936 | 540.378 | 594.8722 | 526.29 | 534.6349
1637.6949 | 1565.6949 | 359.1674 | 565.4475 | 539.3651 | 540.5727 | 595.4826 | 526.6894 | 535.0782
1638.6963 | 1566.6963 | 358.7184 | 565.7237 | 539.6201 | 540.7497 | 595.9978 | 526.9412 | 535.4922
1639.6978 | 1567.6978 | 358.2688 | 566.0773 | 539.8404 | 540.9431 | 596.6027 | 527.2719 | 535.8924
1640.6992 | 1568.6992 | 357.8581 | 566.4162 | 540.0861 | 541.1408 | 597.1618 | 527.7116 | 536.3715
1641.6906 | 1569.6906 | 357.4192 | 566.8586 | 540.3607 | 541.317 | 597.8301 | 528.0708 | 536.7928
1642.6921 | 1570.6921 | 356.9679 | 567.1906 | 540.6111 | 541.5018 | 598.2937 | 528.2513 | 537.142
1643.6935 | 1571.6935 | 356.5332 | 567.5241 | 540.8826 | 541.697 | 598.9135 | 528.4775 | 537.6625
1644.695 | 1572.695 | 356.0923 | 567.7383 | 541.0899 | 541.8857 | 599.4916 | 528.6838 | 538.0239
1645.6964 | 1573.6964 | 355.6306 | 568.2369 | 541.3281 | 542.0827 | 600.1566 | 528.9981 | 538.2585
1646.6978 | 1574.6978 | 355.1805 | 568.787 | 541.5609 | 542.2803 | 600.7354 | 529.4368 | 538.5555
1647.6993 | 1575.6993 | 354.583 | 569.213 | 541.8095 | 542.4843 | 601.2812 | 529.7846 | 538.9175
1648.7007 | 1576.7007 | 354.1171 | 569.6259 | 542.0465 | 542.6871 | 601.8758 | 530.0922 | 539.1612
1649.6921 | 1577.6921 | 353.6479 | 570.041 | 542.2584 | 542.8889 | 602.3965 | 530.4492 | 539.4315
1650.6936 | 1578.6936 | 353.1888 | 570.5936 | 542.5416 | 543.1039 | 603.0637 | 530.9308 | 540.0137
1651.695 | 1579.695 | 352.7368 | 571.0934 | 542.7936 | 543.3194 | 603.636 | 531.3745 | 540.5089
1652.6965 | 1580.6965 | 352.305 | 571.2051 | 543.0311 | 543.5184 | 604.0791 | 531.814 | 540.8742
1653.6979 | 1581.6979 | 351.9241 | 571.3469 | 543.2541 | 543.7226 | 604.6201 | 532.2692 | 541.1858
1654.6993 | 1582.6993 | 351.5882 | 571.6978 | 543.5285 | 543.9232 | 605.0377 | 532.74 | 541.5597
1655.7008 | 1583.7008 | 351.1867 | 572.1937 | 543.7882 | 544.1097 | 605.4908 | 533.2354 | 542.1285
1656.6922 | 1584.6922 | 350.7905 | 572.7461 | 544.0331 | 544.3194 | 606.001 | 533.8448 | 542.5767
1657.6936 | 1585.6936 | 350.4163 | 572.9781 | 544.2215 | 544.5141 | 606.2568 | 534.3888 | 542.9418
1658.6951 | 1586.6951 | 350.0104 | 573.2912 | 544.462 | 544.723 | 606.6941 | 534.9246 | 543.2974
1659.6965 | 1587.6965 | 349.5627 | 573.6933 | 544.7278 | 544.9178 | 607.0648 | 535.358 | 543.337
1660.698 | 1588.698 | 349.075 | 573.8918 | 544.9652 | 545.1167 | 607.4376 | 535.789 | 543.2696
1661.6994 | 1589.6994 | 348.6752 | 574.2949 | 545.2169 | 545.3197 | 608.024 | 536.3195 | 543.3354
1662.7008 | 1590.7008 | 348.2602 | 574.6566 | 545.4443 | 545.5151 | 608.5143 | 536.8402 | 543.5574
1663.6923 | 1591.6923 | 347.8286 | 575.0818 | 545.7328 | 545.713 | 609.0046 | 537.2821 | 543.6478
1664.6937 | 1592.6937 | 347.4804 | 575.2686 | 545.9219 | 545.9195 | 609.4948 | 537.8993 | 543.9628
1665.6952 | 1593.6952 | 347.1704 | 575.7377 | 546.1814 | 546.1217 | 609.9633 | 538.5068 | 544.2014
1666.6966 | 1594.6966 | 346.8211 | 576.1222 | 546.4482 | 546.327 | 610.511 | 539.0272 | 544.4255
1667.698 | 1595.698 | 346.4741 | 576.4802 | 546.6837 | 546.5244 | 610.8534 | 539.5118 | 544.461
1668.6995 | 1596.6995 | 346.1895 | 576.7578 | 546.9331 | 546.7398 | 611.2578 | 539.9605 | 544.623
1669.6909 | 1597.6909 | 345.8311 | 577.1044 | 547.2102 | 546.9511 | 611.6206 | 540.4188 | 544.6886
1670.8426 | 1598.8426 | 345.3211 | 577.3617 | 547.4338 | 547.2014 | 612.1784 | 540.9647 | 544.6405
1671.6938 | 1599.6938 | 344.9235 | 577.7907 | 547.6376 | 547.3903 | 612.5607 | 541.3732 | 544.631
1672.6952 | 1600.6952 | 344.3876 | 578.16 | 547.906 | 547.6088 | 612.9553 | 541.8604 | 545.0723
1673.6967 | 1601.6967 | 343.9616 | 578.5494 | 548.0958 | 547.8347 | 613.0923 | 542.2494 | 545.2284
1674.6981 | 1602.6981 | 343.5146 | 578.612 | 548.2526 | 548.0559 | 613.1802 | 542.6456 | 545.2757
1675.6995 | 1603.6995 | 343.0188 | 578.988 | 548.5361 | 548.2816 | 613.5096 | 542.989 | 545.3629
1676.701 | 1604.701 | 342.5082 | 579.501 | 548.8097 | 548.5016 | 613.8709 | 543.3926 | 545.4604
1677.6924 | 1605.6924 | 342.0692 | 579.9173 | 549.0238 | 548.711 | 614.394 | 543.8141 | 545.8778
1678.6938 | 1606.6938 | 341.68 | 580.3404 | 549.3141 | 548.9239 | 614.9516 | 544.195 | 545.8754
1679.6953 | 1607.6953 | 341.3018 | 580.5627 | 549.5658 | 549.1384 | 615.3379 | 544.6006 | 545.8949
1680.6967 | 1608.6967 | 340.8952 | 580.8586 | 549.8028 | 549.3456 | 615.8387 | 545.0139 | 545.5522
1681.6982 | 1609.6982 | 340.4162 | 580.9796 | 549.9937 | 549.5616 | 616.4695 | 545.4035 | 546.2687
1682.6896 | 1610.6896 | 340.0099 | 581.3038 | 550.2584 | 549.782 | 617.0653 | 545.7816 | 546.6193
1683.691 | 1611.691 | 339.5404 | 581.7562 | 550.4953 | 549.9985 | 617.4592 | 546.1531 | 546.3062
1684.6925 | 1612.6925 | 339.0257 | 582.0759 | 550.7488 | 550.2097 | 617.7917 | 546.5495 | 546.2954
1685.6939 | 1613.6939 | 338.5961 | 582.4082 | 550.9831 | 550.4286 | 618.1561 | 546.8995 | 546.5075
1686.6953 | 1614.6953 | 338.2425 | 582.5983 | 551.1927 | 550.6398 | 618.6643 | 547.2908 | 546.8833
1687.6968 | 1615.6968 | 337.7698 | 582.8336 | 551.4052 | 550.8565 | 619.1345 | 547.7231 | 546.9405
1688.6982 | 1616.6982 | 337.3672 | 583.1661 | 551.6433 | 551.0783 | 619.6093 | 548.2156 | 546.7326
1689.6997 | 1617.6997 | 336.9725 | 583.5183 | 551.8997 | 551.3071 | 620.0733 | 548.6565 | 546.6103
1690.6911 | 1618.6911 | 336.5531 | 583.8657 | 552.1475 | 551.5323 | 620.7318 | 549.0477 | 546.6175
1691.6925 | 1619.6925 | 336.141 | 584.1877 | 552.3548 | 551.7701 | 621.4957 | 549.3333 | 546.902
1692.694 | 1620.694 | 335.6897 | 584.4171 | 552.6071 | 551.9921 | 622.0459 | 549.5768 | 547.4769
1693.6954 | 1621.6954 | 335.3566 | 584.7416 | 552.8325 | 552.2151 | 622.6295 | 549.8939 | 547.1876
1694.6969 | 1622.6969 | 335.038 | 585.0585 | 553.045 | 552.4361 | 623.0793 | 550.2885 | 547.0755
1695.6983 | 1623.6983 | 334.6215 | 585.4001 | 553.2514 | 552.6546 | 623.5479 | 550.6114 | 546.9168
1696.6997 | 1624.6997 | 334.3433 | 585.6804 | 553.4751 | 552.8825 | 623.8972 | 550.8905 | 546.8066
1697.6912 | 1625.6912 | 334.004 | 585.9855 | 553.7081 | 553.0985 | 624.3914 | 551.1839 | 547.2777
1698.6926 | 1626.6926 | 333.634 | 586.3025 | 553.9451 | 553.2612 | 624.6375 | 551.4891 | 546.7494
1699.694 | 1627.694 | 333.1697 | 586.6148 | 554.1935 | 553.3675 | 624.8056 | 551.8359 | 546.3202
1700.6955 | 1628.6955 | 332.7537 | 586.9474 | 554.4025 | 553.5154 | 625.259 | 552.1511 | 546.1434
1701.6969 | 1629.6969 | 332.2866 | 587.244 | 554.6359 | 553.696 | 625.9728 | 552.4912 | 546.3806
1702.6984 | 1630.6984 | 331.8637 | 587.5221 | 554.8593 | 553.8814 | 626.6884 | 552.8184 | 546.7409
1703.6998 | 1631.6998 | 331.5259 | 587.786 | 555.074 | 554.0833 | 627.2926 | 553.0939 | 546.9891
1704.7012 | 1632.7012 | 331.1255 | 588.0339 | 555.302 | 554.2911 | 627.6799 | 553.3495 | 547.192
1705.6927 | 1633.6927 | 330.7584 | 588.3397 | 555.5378 | 554.4948 | 628.0767 | 553.6507 | 546.8921
1706.6941 | 1634.6941 | 330.3835 | 588.5384 | 555.737 | 554.6995 | 628.5327 | 553.8988 | 546.5564
1707.6955 | 1635.6955 | 329.9547 | 588.8563 | 555.9619 | 554.9061 | 629.1316 | 554.1337 | 546.5457
1708.697 | 1636.697 | 329.6018 | 589.1181 | 556.1612 | 555.1123 | 629.6223 | 554.4234 | 546.8853
1709.6984 | 1637.6984 | 329.1524 | 589.4371 | 556.3717 | 555.3161 | 630.1702 | 554.7272 | 546.7163
1710.6999 | 1638.6999 | 328.7498 | 589.7787 | 556.6156 | 555.5215 | 630.5756 | 555.0361 | 546.7408
1711.6913 | 1639.6913 | 328.4793 | 590.1201 | 556.8462 | 555.73 | 630.857 | 555.2913 | 546.7441
1712.6927 | 1640.6927 | 328.2523 | 590.4503 | 557.089 | 555.9387 | 631.2448 | 555.6477 | 546.599
1713.6942 | 1641.6942 | 327.9037 | 590.7631 | 557.3007 | 556.137 | 631.7089 | 555.9703 | 546.4567
1714.6956 | 1642.6956 | 327.4925 | 591.0021 | 557.4902 | 556.3569 | 631.9042 | 556.2251 | 546.5868
1715.6971 | 1643.6971 | 327.0307 | 591.2638 | 557.6978 | 556.5502 | 632.0461 | 556.5201 | 546.7472
1716.6985 | 1644.6985 | 326.6232 | 591.5282 | 557.8894 | 556.7478 | 632.2696 | 556.8528 | 546.4626
1717.6999 | 1645.6999 | 326.2257 | 591.7638 | 558.0737 | 556.9516 | 632.7328 | 557.14 | 546.0076
1718.6914 | 1646.6914 | 325.8314 | 592.0752 | 558.2965 | 557.1531 | 633.3313 | 557.4227 | 545.6828
1719.6928 | 1647.6928 | 325.4287 | 592.3636 | 558.5015 | 557.3438 | 633.7336 | 557.7322 | 545.4144
1720.6942 | 1648.6942 | 325.0049 | 592.6551 | 558.6879 | 557.5358 | 634.0283 | 558.0313 | 545.6308
1721.6957 | 1649.6957 | 324.5728 | 592.915 | 558.8702 | 557.7132 | 634.265 | 558.3854 | 545.5128
1722.6971 | 1650.6971 | 324.1645 | 593.1898 | 559.0932 | 557.9113 | 634.6297 | 558.7328 | 545.3578
1723.6986 | 1651.6986 | 323.7648 | 593.4911 | 559.2944 | 558.0969 | 634.8067 | 559.0098 | 545.482
1724.69 | 1652.69 | 323.2717 | 593.7575 | 559.4783 | 558.2842 | 635.2136 | 559.2427 | 544.976
1725.6914 | 1653.6914 | 322.7957 | 594.1012 | 559.7166 | 558.4734 | 635.5616 | 559.6104 | 544.442
1726.6929 | 1654.6929 | 322.4473 | 594.3164 | 559.9111 | 558.6715 | 635.8749 | 559.9412 | 544.112
1727.6943 | 1655.6943 | 322.1427 | 594.5438 | 560.0959 | 558.8647 | 636.3421 | 560.2675 | 544.4735
1728.6957 | 1656.6957 | 321.7834 | 594.8334 | 560.2962 | 559.0684 | 636.7142 | 560.5425 | 544.2696
1729.6972 | 1657.6972 | 321.4181 | 595.0571 | 560.4996 | 559.2689 | 636.8343 | 560.8458 | 543.9422
1730.6986 | 1658.6986 | 321.0138 | 595.2779 | 560.7053 | 559.4672 | 637.0293 | 561.1957 | 543.5307
1731.7001 | 1659.7001 | 320.5364 | 595.4783 | 560.8859 | 559.6729 | 637.1649 | 561.5585 | 543.1693
1732.6915 | 1660.6915 | 320.1119 | 595.7407 | 561.0792 | 559.8657 | 637.2452 | 561.823 | 543.0291
1733.6929 | 1661.6929 | 319.6945 | 595.9554 | 561.2593 | 560.0574 | 637.4265 | 562.2213 | 543.076
1734.6944 | 1662.6944 | 319.318 | 596.1443 | 561.4513 | 560.2604 | 637.5983 | 562.4871 | 542.8551
1735.6958 | 1663.6958 | 318.8841 | 596.3656 | 561.6382 | 560.4549 | 637.5632 | 562.6953 | 542.5802
1736.6972 | 1664.6972 | 318.4775 | 596.6344 | 561.8553 | 560.6536 | 637.4886 | 562.9599 | 542.3507
1737.6987 | 1665.6987 | 318.1594 | 596.8385 | 562.0483 | 560.853 | 637.3052 | 563.3139 | 542.5001
1738.7001 | 1666.7001 | 317.7788 | 597.1045 | 562.2326 | 561.0484 | 637.1813 | 563.5272 | 542.3243
1739.6916 | 1667.6916 | 317.419 | 597.3848 | 562.4256 | 561.2354 | 637.2499 | 563.8878 | 542.3734
1740.693 | 1668.693 | 317.0312 | 597.6005 | 562.6012 | 561.4201 | 637.6196 | 564.2562 | 542.0805
1741.6944 | 1669.6944 | 316.622 | 597.7997 | 562.787 | 561.6117 | 637.9465 | 564.6026 | 541.8805
1742.6959 | 1670.6959 | 316.2889 | 598.0059 | 562.9577 | 561.7979 | 638.1276 | 564.9429 | 541.899
1743.6973 | 1671.6973 | 315.902 | 598.1979 | 563.1178 | 561.997 | 638.4176 | 565.2393 | 541.7022
1744.6988 | 1672.6988 | 315.5507 | 598.3858 | 563.3 | 562.1708 | 638.8245 | 565.5506 | 541.4282
1745.7002 | 1673.7002 | 315.1872 | 598.6337 | 563.4929 | 562.3561 | 639.1821 | 565.7986 | 541.4208
1746.6916 | 1674.6916 | 314.778 | 598.8991 | 563.6875 | 562.5443 | 639.4659 | 566.0393 | 541.2563
1747.6931 | 1675.6931 | 314.4305 | 599.1371 | 563.8628 | 562.7189 | 639.5401 | 566.2674 | 541.3789
1748.6945 | 1676.6945 | 314.0221 | 599.3395 | 564.0461 | 562.9053 | 639.5697 | 566.5097 | 541.4008
1749.6959 | 1677.6959 | 313.5712 | 599.4955 | 564.2054 | 563.0941 | 639.6075 | 566.7041 | 541.1192
1750.6974 | 1678.6974 | 313.1687 | 599.6005 | 564.3787 | 563.2667 | 639.98 | 566.8988 | 541.1441
1751.6988 | 1679.6988 | 312.757 | 599.7629 | 564.552 | 563.4365 | 640.5791 | 567.0417 | 541.0314
1752.7003 | 1680.7003 | 312.4341 | 599.9052 | 564.7213 | 563.6163 | 641.0518 | 567.1731 | 541.1622
1753.7017 | 1681.7017 | 312.0987 | 600.0405 | 564.8664 | 563.7814 | 641.3458 | 567.31 | 541.4594
1754.6931 | 1682.6931 | 311.732 | 600.2259 | 565.0365 | 563.9441 | 641.7078 | 567.6157 | 541.45
1755.6946 | 1683.6946 | 311.3557 | 600.4597 | 565.2038 | 564.0995 | 641.9725 | 567.9828 | 541.1285
1756.696 | 1684.696 | 310.9837 | 600.6769 | 565.3774 | 564.2451 | 642.2534 | 568.2618 | 541.2313
1757.6974 | 1685.6974 | 310.5374 | 600.8712 | 565.551 | 564.3936 | 642.7527 | 568.5065 | 541.3118
1758.6989 | 1686.6989 | 310.164 | 601.0999 | 565.7172 | 564.539 | 643.2141 | 568.6736 | 541.4493
1759.7003 | 1687.7003 | 309.8084 | 601.2559 | 565.8649 | 564.6902 | 643.3919 | 568.8087 | 541.462
1760.6918 | 1688.6918 | 309.4756 | 601.4138 | 566.0281 | 564.832 | 643.1595 | 569.0364 | 541.4189
1761.6932 | 1689.6932 | 309.1432 | 601.6204 | 566.1964 | 564.9696 | 642.9642 | 569.2844 | 541.3426
1762.6946 | 1690.6946 | 308.7831 | 601.828 | 566.3555 | 565.1258 | 642.9053 | 569.531 | 541.3528
1763.6961 | 1691.6961 | 308.4451 | 601.9731 | 566.4913 | 565.2683 | 643.1372 | 569.8621 | 541.5167
1764.6975 | 1692.6975 | 308.0531 | 602.1442 | 566.651 | 565.4167 | 643.1407 | 570.1187 | 541.5266
1765.699 | 1693.699 | 307.7026 | 602.3476 | 566.7881 | 565.5664 | 643.1237 | 570.3364 | 541.4066
1766.6904 | 1694.6904 | 307.4017 | 602.5277 | 566.9296 | 565.7157 | 643.1232 | 570.5334 | 541.2884
1767.6918 | 1695.6918 | 307.1176 | 602.7552 | 567.0908 | 565.8682 | 643.5685 | 570.6968 | 541.0788
1768.6933 | 1696.6933 | 306.7381 | 602.9266 | 567.2551 | 566.0155 | 644.017 | 570.8593 | 540.7984
1769.6947 | 1697.6947 | 306.3598 | 603.0888 | 567.4011 | 566.1649 | 644.4809 | 571.0552 | 540.7636
1770.6961 | 1698.6961 | 306.034 | 603.225 | 567.5332 | 566.3258 | 644.7019 | 571.2376 | 540.9784
1771.6976 | 1699.6976 | 305.6855 | 603.3829 | 567.6778 | 566.47 | 644.7642 | 571.4785 | 541.5448
1772.699 | 1700.699 | 305.2653 | 603.5606 | 567.8282 | 566.6284 | 644.982 | 571.8326 | 541.583
1773.7005 | 1701.7005 | 304.8704 | 603.7124 | 567.9522 | 566.7786 | 645.3658 | 571.9774 | 541.4439
1774.6919 | 1702.6919 | 304.4528 | 603.8636 | 568.0878 | 566.9207 | 645.6382 | 572.1533 | 541.5751
1775.6933 | 1703.6933 | 304.0482 | 604.0404 | 568.2231 | 567.0616 | 645.7876 | 572.3161 | 541.4248
1776.6948 | 1704.6948 | 303.6914 | 604.159 | 568.3674 | 567.1931 | 646.0099 | 572.6402 | 541.4277
1777.6962 | 1705.6962 | 303.3231 | 604.2967 | 568.4936 | 567.3159 | 646.1596 | 572.8503 | 541.4618
1778.6976 | 1706.6976 | 302.9463 | 604.4631 | 568.6361 | 567.4392 | 646.0325 | 573.0304 | 541.1666
1779.6991 | 1707.6991 | 302.6268 | 604.6271 | 568.7803 | 567.5747 | 646.1176 | 573.3588 | 541.2069
1780.7005 | 1708.7005 | 302.2621 | 604.74 | 568.9291 | 567.6869 | 646.1059 | 573.6455 | 541.256
1781.6919 | 1709.6919 | 301.8738 | 604.8893 | 569.0632 | 567.8041 | 645.915 | 573.9007 | 541.3124
1782.6934 | 1710.6934 | 301.5095 | 604.9615 | 569.1668 | 567.9204 | 645.8032 | 574.0146 | 541.0658
1783.6948 | 1711.6948 | 301.1723 | 605.1078 | 569.3159 | 568.0404 | 645.7807 | 574.1975 | 540.8507
1784.6963 | 1712.6963 | 300.8569 | 605.2422 | 569.4653 | 568.1606 | 645.903 | 574.5698 | 540.4439
1785.6977 | 1713.6977 | 300.4786 | 605.379 | 569.5897 | 568.2757 | 646.2194 | 574.9213 | 540.2955
1786.6991 | 1714.6991 | 300.1167 | 605.5216 | 569.7113 | 568.393 | 646.3602 | 575.2789 | 540.409
1787.7006 | 1715.7006 | 299.8152 | 605.628 | 569.8341 | 568.5136 | 646.5194 | 575.5385 | 540.3534
1788.692 | 1716.692 | 299.5327 | 605.7329 | 569.9477 | 568.626 | 646.6823 | 575.7154 | 540.2675
1789.6935 | 1717.6935 | 299.1713 | 605.8624 | 570.0814 | 568.7376 | 646.8766 | 575.9248 | 540.2056
1790.6949 | 1718.6949 | 298.7887 | 606.0308 | 570.2045 | 568.8555 | 646.9697 | 576.2818 | 540.0936
1791.6963 | 1719.6963 | 298.43 | 606.1941 | 570.3374 | 568.9721 | 647.1787 | 576.5522 | 539.9141
1792.6978 | 1720.6978 | 298.0115 | 606.3529 | 570.4528 | 569.0843 | 647.4148 | 576.7617 | 539.8493
1793.6992 | 1721.6992 | 297.5586 | 606.5228 | 570.571 | 569.2088 | 647.6416 | 576.9972 | 539.9351
1794.6906 | 1722.6906 | 297.1839 | 606.6599 | 570.6998 | 569.321 | 647.7478 | 577.2263 | 539.9968
1795.6921 | 1723.6921 | 296.8476 | 606.7616 | 570.822 | 569.4305 | 647.7221 | 577.4672 | 539.9975
1796.6935 | 1724.6935 | 296.4815 | 606.8563 | 570.9443 | 569.5472 | 648.078 | 577.5922 | 540.0038
1797.695 | 1725.695 | 296.2322 | 606.9764 | 571.0491 | 569.66 | 648.2835 | 577.712 | 539.8745
1798.6964 | 1726.6964 | 296.0068 | 607.0602 | 571.1685 | 569.7613 | 648.3872 | 577.9038 | 539.6985
1799.6978 | 1727.6978 | 295.6825 | 607.16 | 571.2455 | 569.8799 | 648.3037 | 577.9353 | 539.6821
1800.6993 | 1728.6993 | 295.4292 | 607.271 | 571.3729 | 569.988 | 648.7894 | 578.096 | 539.7722
1801.7007 | 1729.7007 | 295.1359 | 607.3699 | 571.4609 | 570.0913 | 648.8843 | 578.2414 | 539.634
1802.6921 | 1730.6921 | 294.7978 | 607.5313 | 571.558 | 570.1984 | 648.7873 | 578.4061 | 539.5061
1803.6936 | 1731.6936 | 294.3729 | 607.6829 | 571.6684 | 570.2885 | 648.6771 | 578.5846 | 539.4124
1804.695 | 1732.695 | 294.0134 | 607.8301 | 571.7875 | 570.3827 | 649.2001 | 578.8078 | 539.5113
1805.6965 | 1733.6965 | 293.6237 | 607.9566 | 571.8974 | 570.4728 | 649.5733 | 579.0543 | 539.5667
1806.6979 | 1734.6979 | 293.309 | 608.0766 | 571.9936 | 570.5476 | 649.7856 | 579.2549 | 539.3798
1807.6993 | 1735.6993 | 292.9836 | 608.1615 | 572.0855 | 570.6291 | 649.7717 | 579.4511 | 539.0746
1808.7008 | 1736.7008 | 292.6426 | 608.2523 | 572.1888 | 570.7114 | 649.5567 | 579.6861 | 538.7401
1809.6922 | 1737.6922 | 292.2804 | 608.3498 | 572.2789 | 570.7865 | 649.3431 | 579.8533 | 538.9175
1810.6936 | 1738.6936 | 291.9201 | 608.4711 | 572.3703 | 570.8696 | 649.0771 | 580.0157 | 538.7358
1811.6951 | 1739.6951 | 291.6532 | 608.556 | 572.4575 | 570.9456 | 648.9477 | 580.1856 | 538.7755
1812.6965 | 1740.6965 | 291.3658 | 608.6487 | 572.5551 | 571.028 | 648.868 | 580.3537 | 538.7538
1813.698 | 1741.698 | 291.0312 | 608.7332 | 572.6334 | 571.1269 | 648.9235 | 580.5007 | 538.6781
1814.6994 | 1742.6994 | 290.66 | 608.8106 | 572.7063 | 571.2013 | 649.242 | 580.6498 | 538.7487
1815.6908 | 1743.6908 | 290.2254 | 608.8996 | 572.8124 | 571.3036 | 649.6389 | 580.7924 | 538.6708
1816.6923 | 1744.6923 | 289.7255 | 608.9802 | 572.9002 | 571.393 | 649.4412 | 580.9118 | 538.5719
1817.6937 | 1745.6937 | 289.3731 | 609.0828 | 572.9776 | 571.4821 | 649.2639 | 581.0404 | 538.6518
1818.6952 | 1746.6952 | 289.028 | 609.171 | 573.0627 | 571.5627 | 649.3169 | 581.1615 | 538.7178
1819.6966 | 1747.6966 | 288.6466 | 609.2608 | 573.1419 | 571.6385 | 649.4561 | 581.4159 | 538.8154
1820.698 | 1748.698 | 288.3364 | 609.33 | 573.2294 | 571.717 | 649.5898 | 581.5259 | 538.909
1821.6995 | 1749.6995 | 287.9927 | 609.3852 | 573.3147 | 571.7974 | 649.7616 | 581.7195 | 538.719
1822.6909 | 1750.6909 | 287.6981 | 609.4345 | 573.394 | 571.874 | 650.0079 | 581.9818 | 538.8972
1823.6923 | 1751.6923 | 287.3445 | 609.4638 | 573.4694 | 571.9561 | 650.5867 | 582.1777 | 538.9339
1824.6938 | 1752.6938 | 286.9397 | 609.5162 | 573.5508 | 572.0308 | 650.7153 | 582.3821 | 539.0099
1825.6952 | 1753.6952 | 286.576 | 609.5517 | 573.6278 | 572.1033 | 650.8355 | 582.5514 | 539.1426
1826.6967 | 1754.6967 | 286.2367 | 609.5957 | 573.6969 | 572.1681 | 650.7672 | 582.6921 | 539.1522
1827.6981 | 1755.6981 | 285.9081 | 609.6344 | 573.759 | 572.2347 | 650.5271 | 582.8547 | 539.1658
1828.6995 | 1756.6995 | 285.5964 | 609.6912 | 573.8423 | 572.2925 | 650.6586 | 583.0429 | 539.1935
1829.701 | 1757.701 | 285.1863 | 609.7304 | 573.9003 | 572.3537 | 650.46 | 583.307 | 539.1343
1830.6924 | 1758.6924 | 284.8382 | 609.8054 | 573.9584 | 572.4225 | 650.3336 | 583.4193 | 539.2315
1831.6938 | 1759.6938 | 284.472 | 609.8677 | 574.0289 | 572.4788 | 650.4219 | 583.6186 | 539.3639
1832.6953 | 1760.6953 | 284.0869 | 609.9491 | 574.0933 | 572.528 | 650.3294 | 583.797 | 539.2492
1833.6967 | 1761.6967 | 283.7024 | 610.051 | 574.1523 | 572.5882 | 650.5698 | 583.969 | 539.208
1834.6982 | 1762.6982 | 283.3821 | 610.1354 | 574.2009 | 572.6453 | 650.707 | 584.1038 | 539.0422
1835.6996 | 1763.6996 | 283.1132 | 610.2479 | 574.2643 | 572.6948 | 650.8499 | 584.2188 | 539.1568
1836.701 | 1764.701 | 282.8122 | 610.3758 | 574.3158 | 572.7393 | 651.198 | 584.2513 | 539.0252
1837.6925 | 1765.6925 | 282.5065 | 610.5011 | 574.3768 | 572.7875 | 651.0206 | 584.3393 | 538.7399
1838.6939 | 1766.6939 | 282.2105 | 610.6011 | 574.4295 | 572.8335 | 650.444 | 584.4465 | 538.6164
1839.6954 | 1767.6954 | 281.926 | 610.6973 | 574.4811 | 572.8802 | 650.1141 | 584.5772 | 538.5476
1840.6968 | 1768.6968 | 281.6526 | 610.7763 | 574.5401 | 572.9283 | 650.2639 | 584.7102 | 538.5319
1841.6982 | 1769.6982 | 281.3375 | 610.8512 | 574.5998 | 572.9738 | 650.2749 | 584.8187 | 538.4402
1842.6997 | 1770.6997 | 281.101 | 610.9071 | 574.6617 | 573.0292 | 650.5417 | 584.9361 | 538.3485
1843.6911 | 1771.6911 | 280.7993 | 610.9494 | 574.7233 | 573.0803 | 650.6043 | 585.1074 | 538.4955
1844.6925 | 1772.6925 | 280.3986 | 610.9481 | 574.774 | 573.1297 | 650.8574 | 585.2109 | 538.4758
1845.694 | 1773.694 | 280.0889 | 610.9622 | 574.8279 | 573.1878 | 650.818 | 585.3484 | 538.4437
1846.6954 | 1774.6954 | 279.8024 | 611.0092 | 574.873 | 573.2387 | 650.5627 | 585.517 | 538.2579
1847.6969 | 1775.6969 | 279.5183 | 611.057 | 574.9148 | 573.2906 | 650.3965 | 585.6515 | 538.262
1848.6983 | 1776.6983 | 279.2073 | 611.1075 | 574.9605 | 573.3432 | 650.1475 | 585.7751 | 537.9881
1849.6997 | 1777.6997 | 278.8383 | 611.1463 | 575.003 | 573.388 | 649.9279 | 585.8612 | 537.6409
1850.6912 | 1778.6912 | 278.459 | 611.1937 | 575.0543 | 573.4319 | 649.656 | 585.9074 | 537.1526
1851.6926 | 1779.6926 | 278.0952 | 611.2732 | 575.1003 | 573.4803 | 649.7991 | 585.999 | 536.9729
1852.694 | 1780.694 | 277.752 | 611.337 | 575.1538 | 573.5278 | 649.6964 | 586.0801 | 536.9503
1853.6955 | 1781.6955 | 277.4676 | 611.3719 | 575.1931 | 573.5608 | 649.5541 | 586.1333 | 536.8497
1854.6969 | 1782.6969 | 277.166 | 611.3987 | 575.2353 | 573.584 | 649.3609 | 586.243 | 536.78
1855.6984 | 1783.6984 | 276.8162 | 611.4432 | 575.2756 | 573.6084 | 649.6562 | 586.3332 | 536.6146
1856.6898 | 1784.6898 | 276.4671 | 611.4856 | 575.3228 | 573.6368 | 649.5432 | 586.3986 | 536.4386
1857.6912 | 1785.6912 | 276.0947 | 611.5048 | 575.3514 | 573.6597 | 649.1711 | 586.4825 | 536.4609
1858.6927 | 1786.6927 | 275.7845 | 611.4941 | 575.3848 | 573.686 | 648.9659 | 586.5231 | 536.6347
1859.6941 | 1787.6941 | 275.4481 | 611.5082 | 575.4166 | 573.7108 | 648.6768 | 586.6336 | 536.5433
1860.6955 | 1788.6955 | 275.0926 | 611.51 | 575.4638 | 573.7467 | 648.4329 | 586.7095 | 536.3896
1861.697 | 1789.697 | 274.8564 | 611.4896 | 575.4796 | 573.7807 | 648.2989 | 586.8431 | 536.3612
1862.6984 | 1790.6984 | 274.5437 | 611.4815 | 575.5052 | 573.8136 | 648.0816 | 586.9689 | 536.217
1863.6999 | 1791.6999 | 274.3007 | 611.4796 | 575.5213 | 573.8563 | 647.938 | 587.1138 | 536.1742
1864.6913 | 1792.6913 | 273.9926 | 611.5071 | 575.5563 | 573.8799 | 647.8479 | 587.167 | 535.9129
1865.6927 | 1793.6927 | 273.65 | 611.5263 | 575.5786 | 573.9232 | 647.6801 | 587.2543 | 535.6759
1866.6942 | 1794.6942 | 273.3525 | 611.5475 | 575.6 | 573.9565 | 647.2187 | 587.3492 | 535.8083
1867.6956 | 1795.6956 | 273.0574 | 611.5601 | 575.6336 | 573.9906 | 647.1643 | 587.407 | 535.7336
1868.6971 | 1796.6971 | 272.6784 | 611.554 | 575.6596 | 574.0335 | 647.0926 | 587.443 | 535.6572
1869.6985 | 1797.6985 | 272.3213 | 611.536 | 575.6736 | 574.065 | 647.2035 | 587.4793 | 535.4998
1870.6899 | 1798.6899 | 271.9544 | 611.5533 | 575.6911 | 574.0883 | 647.1273 | 587.5671 | 535.503
1871.6914 | 1799.6914 | 271.6337 | 611.5548 | 575.7035 | 574.1133 | 647.0653 | 587.6246 | 535.4395
1872.6928 | 1800.6928 | 271.3297 | 611.5575 | 575.7264 | 574.1266 | 646.8694 | 587.6849 | 535.507
1873.6942 | 1801.6942 | 271.0258 | 611.5876 | 575.7419 | 574.1438 | 646.9402 | 587.7394 | 535.4852
1874.6957 | 1802.6957 | 270.7325 | 611.5865 | 575.7601 | 574.1644 | 646.7079 | 587.773 | 535.2664
1875.6971 | 1803.6971 | 270.4933 | 611.6033 | 575.7712 | 574.179 | 646.3921 | 587.8207 | 535.0725
1876.6986 | 1804.6986 | 270.2114 | 611.6119 | 575.7742 | 574.1922 | 646.148 | 587.8669 | 534.9579
1877.7 | 1805.7 | 269.8958 | 611.6087 | 575.7795 | 574.2027 | 645.9671 | 587.8899 | 534.8668
1878.6914 | 1806.6914 | 269.5589 | 611.5978 | 575.7917 | 574.2185 | 646.3511 | 587.927 | 534.7409
1879.6929 | 1807.6929 | 269.1601 | 611.5995 | 575.7922 | 574.2324 | 646.3753 | 587.9423 | 534.6024
1880.6943 | 1808.6943 | 268.8918 | 611.5885 | 575.8075 | 574.2403 | 646.3916 | 587.9647 | 534.5263
1881.6957 | 1809.6957 | 268.607 | 611.6176 | 575.8059 | 574.2465 | 646.2878 | 588.0171 | 534.2617
1882.6972 | 1810.6972 | 268.3446 | 611.628 | 575.8106 | 574.2564 | 646.1674 | 588.0528 | 533.9063
1883.6986 | 1811.6986 | 268.1427 | 611.6335 | 575.8116 | 574.2592 | 646.3969 | 588.1145 | 533.8802
1884.7001 | 1812.7001 | 267.8249 | 611.6545 | 575.8129 | 574.258 | 646.3118 | 588.1259 | 533.5949
1885.6915 | 1813.6915 | 267.5108 | 611.6625 | 575.8152 | 574.2588 | 646.1359 | 588.1732 | 533.6033
1886.6929 | 1814.6929 | 267.2241 | 611.6694 | 575.8158 | 574.2431 | 645.7872 | 588.2556 | 533.4723
1887.6944 | 1815.6944 | 266.9351 | 611.6555 | 575.8125 | 574.2418 | 645.5416 | 588.4318 | 533.3083
1888.6958 | 1816.6958 | 266.6451 | 611.6228 | 575.8231 | 574.2385 | 645.0471 | 588.4847 | 533.1649
1889.6973 | 1817.6973 | 266.4051 | 611.5855 | 575.8251 | 574.238 | 644.8171 | 588.491 | 533.0574
1890.6987 | 1818.6987 | 266.0768 | 611.5997 | 575.8213 | 574.2364 | 644.7095 | 588.5163 | 532.8926
1891.6901 | 1819.6901 | 265.7719 | 611.6173 | 575.8116 | 574.2332 | 644.4054 | 588.5393 | 532.7947
1892.6916 | 1820.6916 | 265.4278 | 611.5891 | 575.8186 | 574.2295 | 644.2253 | 588.549 | 532.6685
1893.693 | 1821.693 | 265.1118 | 611.5786 | 575.8094 | 574.2243 | 644.0193 | 588.5519 | 532.4998
1894.6944 | 1822.6944 | 264.8505 | 611.5362 | 575.8057 | 574.2262 | 644.05 | 588.5493 | 532.4627
1895.6959 | 1823.6959 | 264.5576 | 611.5142 | 575.8143 | 574.233 | 644.2422 | 588.533 | 532.4211
1896.6973 | 1824.6973 | 264.2269 | 611.4818 | 575.7993 | 574.2266 | 644.286 | 588.5479 | 532.1613
1897.6988 | 1825.6988 | 263.9425 | 611.4603 | 575.7894 | 574.226 | 644.1531 | 588.5776 | 531.9944
1898.6902 | 1826.6902 | 263.6159 | 611.4274 | 575.7769 | 574.2196 | 644.0758 | 588.6686 | 531.8367
1899.6916 | 1827.6916 | 263.3286 | 611.3874 | 575.7735 | 574.2112 | 643.9714 | 588.7781 | 531.8957
1900.6931 | 1828.6931 | 263.0411 | 611.3405 | 575.7617 | 574.1995 | 643.9214 | 588.8268 | 531.9349
1901.6945 | 1829.6945 | 262.7332 | 611.3071 | 575.7579 | 574.1928 | 643.6669 | 588.9198 | 531.6493
1902.6959 | 1830.6959 | 262.3068 | 611.2875 | 575.7431 | 574.1847 | 643.5112 | 588.935 | 531.4218
1903.6974 | 1831.6974 | 261.8942 | 611.2812 | 575.7306 | 574.1723 | 643.2301 | 588.9906 | 531.1811
1904.6988 | 1832.6988 | 261.584 | 611.2827 | 575.7226 | 574.1718 | 642.9092 | 589.018 | 530.931
1905.7003 | 1833.7003 | 261.3228 | 611.2549 | 575.7059 | 574.1552 | 642.5408 | 588.9735 | 530.907
1906.6917 | 1834.6917 | 260.9885 | 611.2476 | 575.7026 | 574.1426 | 642.3381 | 588.9308 | 530.6831
1907.6931 | 1835.6931 | 260.651 | 611.2164 | 575.7021 | 574.1255 | 642.0754 | 588.9393 | 530.5227
1908.6946 | 1836.6946 | 260.3469 | 611.1827 | 575.6743 | 574.1208 | 641.7992 | 589.0842 | 530.2303
1909.696 | 1837.696 | 260.0519 | 611.1425 | 575.6638 | 574.0949 | 641.8662 | 589.19 | 530.2878
1910.6974 | 1838.6974 | 259.7586 | 611.1112 | 575.6555 | 574.0789 | 641.7262 | 589.1799 | 530.1933
1911.6989 | 1839.6989 | 259.4787 | 611.054 | 575.649 | 574.064 | 641.4799 | 589.166 | 529.6965
1912.7003 | 1840.7003 | 259.2002 | 610.9941 | 575.6426 | 574.0452 | 641.1497 | 589.1179 | 529.4774
1913.6918 | 1841.6918 | 258.9217 | 610.9518 | 575.6211 | 574.0345 | 640.8689 | 589.1054 | 529.2827
1914.6932 | 1842.6932 | 258.6539 | 610.9164 | 575.6061 | 574.0069 | 640.6739 | 589.0988 | 529.1252
1915.6946 | 1843.6946 | 258.401 | 610.8985 | 575.5905 | 573.9754 | 640.482 | 589.0899 | 529.0746
1916.6961 | 1844.6961 | 258.1749 | 610.8881 | 575.5671 | 573.9547 | 640.3302 | 589.0112 | 528.9362
1917.6975 | 1845.6975 | 257.8478 | 610.8386 | 575.549 | 573.9187 | 640.3366 | 588.9389 | 528.7755
1918.699 | 1846.699 | 257.5661 | 610.7735 | 575.5355 | 573.8974 | 640.0797 | 588.8521 | 528.6855
1919.6904 | 1847.6904 | 257.3168 | 610.7582 | 575.5176 | 573.8802 | 639.914 | 588.8515 | 528.7011
1920.6918 | 1848.6918 | 257.0247 | 610.7195 | 575.4947 | 573.8682 | 639.9572 | 588.8178 | 528.4816
1921.6933 | 1849.6933 | 256.7348 | 610.68 | 575.4792 | 573.8563 | 639.7659 | 588.7476 | 528.4017
1922.6947 | 1850.6947 | 256.5484 | 610.6699 | 575.4576 | 573.8374 | 639.4246 | 588.8299 | 528.2855
1923.6961 | 1851.6961 | 256.3221 | 610.6584 | 575.4239 | 573.829 | 639.0119 | 588.8979 | 528.1217
1924.6976 | 1852.6976 | 256.0311 | 610.6213 | 575.4043 | 573.8103 | 638.7867 | 588.9346 | 528.1631
1925.699 | 1853.699 | 255.7096 | 610.5771 | 575.382 | 573.7859 | 638.7386 | 588.897 | 528.1132
1926.7005 | 1854.7005 | 255.4025 | 610.4935 | 575.3526 | 573.7568 | 638.4547 | 588.9171 | 527.9716
1927.6919 | 1855.6919 | 255.1211 | 610.4586 | 575.3236 | 573.7159 | 637.9981 | 588.8747 | 527.7382
1928.6933 | 1856.6933 | 254.8114 | 610.4396 | 575.304 | 573.6833 | 637.5961 | 588.9272 | 527.3966
1929.6948 | 1857.6948 | 254.5208 | 610.4526 | 575.2723 | 573.6456 | 637.3746 | 589.019 | 527.1536
1930.6962 | 1858.6962 | 254.2395 | 610.4256 | 575.2396 | 573.6149 | 637.1526 | 589.1213 | 527.0888
1931.6976 | 1859.6976 | 254.0528 | 610.385 | 575.2213 | 573.5899 | 636.8463 | 589.0378 | 527.0324
1932.6991 | 1860.6991 | 253.8898 | 610.3373 | 575.1864 | 573.5602 | 636.3306 | 588.9245 | 526.9667
1933.7005 | 1861.7005 | 253.6259 | 610.3005 | 575.1487 | 573.5405 | 636.1408 | 588.971 | 526.7343
1934.692 | 1862.692 | 253.365 | 610.2491 | 575.1233 | 573.5094 | 635.8917 | 589.119 | 526.3737
1935.6934 | 1863.6934 | 253.1935 | 610.2078 | 575.092 | 573.4792 | 635.6683 | 589.3366 | 526.251
1936.6948 | 1864.6948 | 252.9114 | 610.2185 | 575.0652 | 573.4504 | 635.2147 | 589.4759 | 526.0713
1937.6963 | 1865.6963 | 252.6609 | 610.1989 | 575.0337 | 573.4251 | 634.9751 | 589.408 | 525.7385
1938.6977 | 1866.6977 | 252.4862 | 610.1321 | 575.0102 | 573.3956 | 634.7821 | 589.1752 | 525.5372
1939.6891 | 1867.6891 | 252.2152 | 610.0712 | 574.971 | 573.3602 | 634.5099 | 589.1176 | 525.4373
1940.6906 | 1868.6906 | 251.9162 | 609.9885 | 574.9387 | 573.3409 | 634.4443 | 589.0925 | 525.261
1941.692 | 1869.692 | 251.7172 | 609.9207 | 574.9133 | 573.314 | 634.1714 | 588.9107 | 525.1076
1942.6935 | 1870.6935 | 251.4496 | 609.832 | 574.8786 | 573.2981 | 633.8057 | 588.6546 | 524.9871
1943.6949 | 1871.6949 | 251.1828 | 609.7533 | 574.835 | 573.2775 | 633.3775 | 588.4691 | 524.7408
1944.6963 | 1872.6963 | 250.8503 | 609.6947 | 574.7879 | 573.2484 | 633.4176 | 588.2831 | 524.5027
1945.6978 | 1873.6978 | 250.5286 | 609.6184 | 574.7481 | 573.2321 | 633.1303 | 588.2009 | 524.2256
1946.6992 | 1874.6992 | 250.225 | 609.5816 | 574.6908 | 573.2117 | 632.8742 | 588.1907 | 524.038
1947.6906 | 1875.6906 | 249.9942 | 609.544 | 574.6652 | 573.1834 | 632.7181 | 588.2141 | 523.9633
1948.6921 | 1876.6921 | 249.7272 | 609.4923 | 574.6228 | 573.1618 | 632.4148 | 588.2651 | 523.9366
1949.6935 | 1877.6935 | 249.446 | 609.3924 | 574.5874 | 573.1439 | 631.9691 | 588.3226 | 523.8385
1950.695 | 1878.695 | 249.1702 | 609.3186 | 574.5442 | 573.1222 | 631.171 | 588.4446 | 523.6528
1951.6964 | 1879.6964 | 248.9024 | 609.2727 | 574.4955 | 573.1055 | 630.7313 | 588.3185 | 523.5201
1952.6978 | 1880.6978 | 248.694 | 609.2442 | 574.4574 | 573.0802 | 630.4671 | 588.2452 | 523.385
1953.6993 | 1881.6993 | 248.4669 | 609.2202 | 574.4223 | 573.0619 | 630.304 | 588.0882 | 523.3214
1954.7007 | 1882.7007 | 248.229 | 609.1847 | 574.378 | 573.039 | 630.0904 | 588.116 | 523.228
1955.6921 | 1883.6921 | 247.9239 | 609.1472 | 574.3471 | 573.0245 | 629.704 | 588.0438 | 523.129
1956.6936 | 1884.6936 | 247.6475 | 609.1327 | 574.3068 | 573.0001 | 629.3332 | 587.8615 | 523.0305
1957.695 | 1885.695 | 247.376 | 609.1023 | 574.2662 | 572.9803 | 628.9277 | 587.7281 | 522.7486
1958.6965 | 1886.6965 | 247.1458 | 609.0625 | 574.2328 | 572.9682 | 628.4266 | 587.6559 | 522.6577
1959.6979 | 1887.6979 | 246.8966 | 609.0491 | 574.1856 | 572.9452 | 628.1094 | 587.6089 | 522.5919
1960.6993 | 1888.6993 | 246.6136 | 608.993 | 574.1659 | 572.9195 | 627.6467 | 587.5808 | 522.4734
1961.7008 | 1889.7008 | 246.3275 | 608.9411 | 574.1242 | 572.8971 | 627.2132 | 587.4505 | 522.2507
1962.6922 | 1890.6922 | 246.077 | 608.9198 | 574.0969 | 572.8581 | 626.7914 | 587.3226 | 522.0386
1963.6937 | 1891.6937 | 245.8617 | 608.8604 | 574.0566 | 572.808 | 626.3506 | 587.1907 | 521.9649
1964.6951 | 1892.6951 | 245.5748 | 608.7719 | 574.0206 | 572.7654 | 625.8886 | 587.0686 | 521.6316
1965.6965 | 1893.6965 | 245.2588 | 608.7385 | 573.9796 | 572.7168 | 625.4844 | 586.9176 | 521.4149
1966.698 | 1894.698 | 244.9363 | 608.7284 | 573.9517 | 572.6683 | 624.9679 | 586.8432 | 521.4105
1967.6994 | 1895.6994 | 244.6401 | 608.7245 | 573.9124 | 572.6178 | 624.6157 | 586.7423 | 521.338
1968.7009 | 1896.7009 | 244.4341 | 608.6998 | 573.8573 | 572.5717 | 624.0789 | 586.6263 | 521.112
1969.6923 | 1897.6923 | 244.1968 | 608.6874 | 573.8178 | 572.5212 | 623.4515 | 586.4141 | 520.8402
1970.6937 | 1898.6937 | 243.9412 | 608.6369 | 573.7742 | 572.4769 | 623.092 | 586.2176 | 520.6652
1971.6952 | 1899.6952 | 243.6073 | 608.5904 | 573.7418 | 572.4226 | 622.781 | 586.0374 | 520.5173
1972.6966 | 1900.6966 | 243.298 | 608.5466 | 573.689 | 572.3812 | 622.3478 | 585.8891 | 520.375
1973.698 | 1901.698 | 243.0851 | 608.4949 | 573.6358 | 572.3384 | 621.8588 | 585.79 | 520.1948
1974.6995 | 1902.6995 | 242.8609 | 608.4673 | 573.5904 | 572.2913 | 621.4191 | 585.7237 | 519.9683
1975.6909 | 1903.6909 | 242.5883 | 608.4194 | 573.5484 | 572.2543 | 621.0975 | 585.6622 | 519.6097
1976.6923 | 1904.6923 | 242.246 | 608.3717 | 573.5075 | 572.2085 | 620.6762 | 585.587 | 519.3042
1977.6938 | 1905.6938 | 241.9593 | 608.3322 | 573.4536 | 572.1656 | 620.1508 | 585.5506 | 519.1306
1978.6952 | 1906.6952 | 241.6593 | 608.2922 | 573.3888 | 572.1227 | 619.7954 | 585.4535 | 518.8146
1979.6967 | 1907.6967 | 241.362 | 608.2267 | 573.3452 | 572.0867 | 619.3311 | 585.4567 | 518.6499
1980.6981 | 1908.6981 | 241.1098 | 608.2366 | 573.2984 | 572.0466 | 618.8347 | 585.3823 | 518.6275
1981.6895 | 1909.6895 | 240.8242 | 608.1913 | 573.2372 | 571.995 | 618.3421 | 585.3293 | 518.4686
1982.691 | 1910.691 | 240.587 | 608.1447 | 573.1761 | 571.9506 | 617.5382 | 585.3919 | 518.2598
1983.6924 | 1911.6924 | 240.3655 | 608.0926 | 573.1234 | 571.8886 | 617.1112 | 585.3129 | 518.0425
1984.6938 | 1912.6938 | 240.1619 | 608.0548 | 573.064 | 571.8353 | 616.5961 | 585.2099 | 517.7839
1985.6953 | 1913.6953 | 239.9758 | 608.0099 | 573.0113 | 571.7735 | 616.1979 | 585.0523 | 517.5212
1986.6967 | 1914.6967 | 239.7248 | 607.9684 | 572.948 | 571.7162 | 615.9529 | 584.9341 | 517.3492
1987.6982 | 1915.6982 | 239.4932 | 607.9572 | 572.8922 | 571.6613 | 615.6535 | 584.8763 | 517.2375
1988.6896 | 1916.6896 | 239.2099 | 607.9466 | 572.8305 | 571.6152 | 615.2561 | 584.81 | 517.1908
1989.691 | 1917.691 | 238.9252 | 607.9076 | 572.7763 | 571.5658 | 614.7384 | 584.7464 | 517.1208
1990.6925 | 1918.6925 | 238.6957 | 607.8699 | 572.7067 | 571.517 | 614.2048 | 584.6595 | 517.0027
1991.6939 | 1919.6939 | 238.4836 | 607.8551 | 572.6346 | 571.4651 | 613.4956 | 584.5527 | 516.7135
1992.6954 | 1920.6954 | 238.2505 | 607.8239 | 572.6033 | 571.4093 | 612.845 | 584.4328 | 516.449
1993.6968 | 1921.6968 | 238.037 | 607.8199 | 572.5362 | 571.3494 | 612.1558 | 584.3399 | 516.1871
1994.6982 | 1922.6982 | 237.8784 | 607.8271 | 572.4795 | 571.296 | 611.7217 | 584.2046 | 516.021
1995.6997 | 1923.6997 | 237.5891 | 607.8863 | 572.4107 | 571.2348 | 611.3105 | 584.0782 | 515.7264
1996.6911 | 1924.6911 | 237.2546 | 607.8067 | 572.3519 | 571.1781 | 610.92 | 584.0918 | 515.471
1997.6925 | 1925.6925 | 237.0299 | 607.7751 | 572.2702 | 571.1228 | 610.5112 | 583.9914 | 515.3141
1998.694 | 1926.694 | 236.8023 | 607.6884 | 572.2238 | 571.0679 | 610.2723 | 583.8877 | 515.0767
1999.6954 | 1927.6954 | 236.5497 | 607.6251 | 572.1552 | 571.0123 | 609.7766 | 583.7752 | 514.8045
2000.6969 | 1928.6969 | 236.3243 | 607.5811 | 572.0928 | 570.9582 | 609.2233 | 583.6876 | 514.5096
2001.6983 | 1929.6983 | 236.1183 | 607.4932 | 572.0244 | 570.896 | 608.6712 | 583.6158 | 514.2785
2002.6997 | 1930.6997 | 235.8529 | 607.4387 | 571.9714 | 570.8334 | 608.1501 | 583.5574 | 514.0863
2003.6912 | 1931.6912 | 235.6033 | 607.3452 | 571.9121 | 570.7672 | 607.6214 | 583.4972 | 513.8637
2004.6926 | 1932.6926 | 235.3468 | 607.2684 | 571.8421 | 570.6932 | 607.1987 | 583.3855 | 513.7722
2005.694 | 1933.694 | 235.064 | 607.1994 | 571.7816 | 570.6383 | 606.7216 | 583.267 | 513.6255
2006.6955 | 1934.6955 | 234.8537 | 607.0856 | 571.7099 | 570.5574 | 606.3481 | 583.1971 | 513.4226
2007.6969 | 1935.6969 | 234.6156 | 606.9999 | 571.6475 | 570.4771 | 606.6432 | 583.0298 | 513.2042
2008.6984 | 1936.6984 | 234.3648 | 606.9163 | 571.5636 | 570.4053 | 606.3421 | 583.014 | 512.9355
2009.6998 | 1937.6998 | 234.0426 | 606.8452 | 571.4947 | 570.3322 | 605.9677 | 583.1256 | 512.7051
2010.6912 | 1938.6912 | 233.7607 | 606.7708 | 571.4205 | 570.2684 | 605.519 | 583.0916 | 512.5415
2011.6927 | 1939.6927 | 233.5286 | 606.6985 | 571.3374 | 570.1988 | 605.1946 | 583.0092 | 512.394
2012.6941 | 1940.6941 | 233.2678 | 606.5569 | 571.2613 | 570.1337 | 604.7629 | 582.8793 | 512.1933
2013.6956 | 1941.6956 | 233.0355 | 606.4473 | 571.1678 | 570.0675 | 604.3524 | 582.7712 | 511.9098
2014.697 | 1942.697 | 232.8074 | 606.3536 | 571.0964 | 570.004 | 603.8033 | 582.7054 | 511.6978
2015.6984 | 1943.6984 | 232.5519 | 606.249 | 570.9995 | 569.9406 | 603.065 | 582.6362 | 511.3948
2016.6999 | 1944.6999 | 232.3223 | 606.1833 | 570.9203 | 569.8634 | 602.4376 | 582.566 | 511.1234
2017.6913 | 1945.6913 | 232.1007 | 606.069 | 570.8364 | 569.7847 | 601.9452 | 582.498 | 510.8519
2018.6927 | 1946.6927 | 231.8587 | 605.9941 | 570.747 | 569.71 | 601.3771 | 582.3775 | 510.5156
2019.6942 | 1947.6942 | 231.6363 | 605.9068 | 570.6513 | 569.62 | 600.883 | 582.1659 | 510.1662
2020.6956 | 1948.6956 | 231.441 | 605.8306 | 570.5661 | 569.5482 | 600.4509 | 582.0074 | 509.9227
2021.6971 | 1949.6971 | 231.197 | 605.7813 | 570.465 | 569.4599 | 599.9576 | 581.8516 | 509.6218
2022.6985 | 1950.6985 | 230.975 | 605.7273 | 570.3697 | 569.3818 | 599.5374 | 581.7321 | 509.3812
2023.6999 | 1951.6999 | 230.7553 | 605.6236 | 570.2768 | 569.2943 | 598.9766 | 581.6022 | 509.1043
2024.6914 | 1952.6914 | 230.561 | 605.5208 | 570.1821 | 569.2094 | 598.3469 | 581.4608 | 508.7918
2025.6928 | 1953.6928 | 230.3035 | 605.4039 | 570.0947 | 569.1167 | 597.7836 | 581.3255 | 508.5119
2026.6942 | 1954.6942 | 230.0571 | 605.223 | 569.993 | 569.0306 | 597.178 | 581.1974 | 508.1825
2027.6957 | 1955.6957 | 229.8853 | 605.0674 | 569.8989 | 568.9475 | 596.6526 | 581.0766 | 507.8787
2028.6971 | 1956.6971 | 229.6947 | 604.8933 | 569.8013 | 568.8593 | 596.1289 | 580.9469 | 507.4818
2029.6986 | 1957.6986 | 229.49 | 604.783 | 569.7109 | 568.7638 | 595.6893 | 580.8343 | 507.2073
2030.7 | 1958.7 | 229.329 | 604.6283 | 569.6206 | 568.6654 | 595.1418 | 580.6994 | 506.9432
2031.7415 | 1959.7415 | 229.1432 | 604.4543 | 569.5197 | 568.5538 | 594.5331 | 580.5329 | 506.6595
2032.6929 | 1960.6929 | 228.8855 | 604.2883 | 569.4315 | 568.4425 | 593.9194 | 580.4372 | 506.3593
2033.6943 | 1961.6943 | 228.6025 | 604.0435 | 569.3309 | 568.3341 | 593.4624 | 580.3076 | 506.1454
2034.6957 | 1962.6957 | 228.3354 | 603.7998 | 569.2503 | 568.2286 | 592.9253 | 580.1245 | 505.9371
2035.6972 | 1963.6972 | 228.0579 | 603.5947 | 569.1576 | 568.1185 | 592.1926 | 580.0076 | 505.7036
2036.6986 | 1964.6986 | 227.8084 | 603.4316 | 569.0517 | 568.0152 | 591.4838 | 579.8399 | 505.3798
2037.7001 | 1965.7001 | 227.5753 | 603.2275 | 568.9635 | 567.9132 | 590.9012 | 579.7008 | 504.99
2038.6915 | 1966.6915 | 227.3072 | 603.0431 | 568.873 | 567.818 | 590.2634 | 579.5427 | 504.6792
2039.6929 | 1967.6929 | 226.9979 | 602.8744 | 568.7629 | 567.7146 | 589.5081 | 579.3719 | 504.3742
2040.6944 | 1968.6944 | 226.6979 | 602.7737 | 568.6682 | 567.6056 | 588.8241 | 579.2223 | 504.1287
2041.6958 | 1969.6958 | 226.4517 | 602.5759 | 568.5612 | 567.4984 | 588.0825 | 579.0615 | 503.8888
2042.6973 | 1970.6973 | 226.2192 | 602.288 | 568.4581 | 567.3944 | 587.3827 | 578.9387 | 503.6266
2043.6987 | 1971.6987 | 225.9495 | 601.9836 | 568.3656 | 567.2916 | 586.6615 | 578.7862 | 503.2726
2044.7001 | 1972.7001 | 225.7031 | 601.6601 | 568.2572 | 567.181 | 585.923 | 578.6357 | 502.8843
2045.6916 | 1973.6916 | 225.4552 | 601.4093 | 568.1537 | 567.0862 | 585.3102 | 578.4867 | 502.5127
2046.693 | 1974.693 | 225.2856 | 601.1256 | 568.0333 | 566.973 | 584.5241 | 578.3439 | 502.1753
2047.6944 | 1975.6944 | 225.0944 | 600.8586 | 567.9215 | 566.8706 | 583.6585 | 578.1827 | 501.7878
2048.6959 | 1976.6959 | 224.8853 | 600.6377 | 567.8174 | 566.7723 | 582.7992 | 578.0027 | 501.4265
2049.6973 | 1977.6973 | 224.7386 | 600.3222 | 567.7023 | 566.6798 | 581.9475 | 577.8386 | 501.0696
2050.6988 | 1978.6988 | 224.5028 | 600.0535 | 567.5933 | 566.5784 | 581.1731 | 577.6756 | 500.7395
2051.7002 | 1979.7002 | 224.2944 | 599.7847 | 567.4713 | 566.4811 | 580.4588 | 577.4833 | 500.403
2052.6916 | 1980.6916 | 224.0206 | 599.4708 | 567.362 | 566.3921 | 579.7506 | 577.3443 | 500.0016
2053.7031 | 1981.7031 | 223.7052 | 599.1737 | 567.2463 | 566.3037 | 579.0628 | 577.2855 | 499.8991
2054.6945 | 1982.6945 | 223.4109 | 598.8972 | 567.1227 | 566.1907 | 578.4063 | 577.1778 | 499.7845
2055.716 | 1983.716 | 223.121 | 598.6022 | 567.0067 | 566.0747 | 577.7577 | 577.0526 | 499.5558
2056.6974 | 1984.6974 | 222.829 | 598.3069 | 566.8841 | 565.9572 | 577.1317 | 576.8889 | 499.2275
2057.6988 | 1985.6988 | 222.5999 | 598.0373 | 566.7571 | 565.8239 | 576.531 | 576.7225 | 498.8197
2058.7003 | 1986.7003 | 222.412 | 597.7871 | 566.6425 | 565.6993 | 576.0475 | 576.526 | 498.4967
2059.6917 | 1987.6917 | 222.1552 | 597.4897 | 566.521 | 565.5783 | 575.5078 | 576.3579 | 498.1246
2060.6931 | 1988.6931 | 221.8684 | 597.1861 | 566.369 | 565.45 | 574.9821 | 576.181 | 497.6454
2061.6946 | 1989.6946 | 221.6233 | 596.9126 | 566.2602 | 565.3271 | 574.5319 | 576.0055 | 497.2972
2062.696 | 1990.696 | 221.324 | 596.6267 | 566.129 | 565.2048 | 574.0783 | 575.8402 | 497.0337
2063.6975 | 1991.6975 | 221.0678 | 596.3168 | 565.9863 | 565.0695 | 573.6265 | 575.6657 | 496.7177
2064.6989 | 1992.6989 | 220.8386 | 595.9887 | 565.8459 | 564.9354 | 573.1575 | 575.6574 | 496.3297
2065.6903 | 1993.6903 | 220.623 | 595.6753 | 565.7096 | 564.7829 | 572.6677 | 575.495 | 495.9301
2066.6918 | 1994.6918 | 220.3795 | 595.3621 | 565.5741 | 564.6432 | 572.2196 | 575.3891 | 495.584
2067.6932 | 1995.6932 | 220.1622 | 595.0356 | 565.4423 | 564.5081 | 571.7131 | 575.3701 | 495.2571
2068.6946 | 1996.6946 | 219.9122 | 594.7492 | 565.313 | 564.3624 | 571.2299 | 575.2788 | 494.9294
2069.6961 | 1997.6961 | 219.666 | 594.4711 | 565.1678 | 564.2235 | 570.7425 | 575.214 | 494.6378
2070.6975 | 1998.6975 | 219.4732 | 594.2229 | 565.0207 | 564.084 | 570.2809 | 575.2249 | 494.3395
2071.699 | 1999.699 | 219.267 | 593.9559 | 564.8885 | 563.9312 | 569.8831 | 575.1603 | 494.0272
2072.6904 | 2000.6904 | 219.0137 | 593.6548 | 564.7535 | 563.7844 | 569.4731 | 574.9501 | 493.6373
2073.6918 | 2001.6918 | 218.7117 | 593.3298 | 564.6241 | 563.6455 | 569.0523 | 574.7253 | 493.2312
2074.6933 | 2002.6933 | 218.4203 | 593.0359 | 564.4711 | 563.5022 | 568.6794 | 574.4543 | 492.8185
2075.6947 | 2003.6947 | 218.1946 | 592.7499 | 564.3321 | 563.3636 | 568.2756 | 574.1722 | 492.4453
2076.6961 | 2004.6961 | 217.9355 | 592.4487 | 564.1855 | 563.219 | 567.8258 | 573.8888 | 492.0251
2077.6976 | 2005.6976 | 217.73 | 592.1357 | 564.0387 | 563.0808 | 567.3444 | 573.6363 | 491.6586
2078.699 | 2006.699 | 217.4673 | 591.8079 | 563.9018 | 562.9365 | 566.8609 | 573.2919 | 491.2869
2079.7005 | 2007.7005 | 217.2186 | 591.4975 | 563.7457 | 562.7907 | 566.4131 | 573.0093 | 490.9021
2080.6919 | 2008.6919 | 216.9932 | 591.1903 | 563.5928 | 562.6459 | 565.9709 | 572.7217 | 490.515
2081.6933 | 2009.6933 | 216.8318 | 590.8694 | 563.4506 | 562.5072 | 565.5413 | 572.4426 | 490.1647
2082.6948 | 2010.6948 | 216.6286 | 590.5379 | 563.2978 | 562.3607 | 565.0876 | 572.2249 | 489.7433
2083.6962 | 2011.6962 | 216.4436 | 590.1963 | 563.1331 | 562.2198 | 564.6397 | 572.0014 | 489.3802
2084.6976 | 2012.6976 | 216.239 | 589.8763 | 562.9778 | 562.0664 | 564.1764 | 571.7784 | 489.0066
2085.6991 | 2013.6991 | 216.0217 | 589.5572 | 562.8171 | 561.9088 | 563.7584 | 571.5129 | 488.6476
2086.7005 | 2014.7005 | 215.8399 | 589.212 | 562.6649 | 561.7587 | 563.336 | 571.2692 | 488.3429
2087.692 | 2015.692 | 215.6813 | 588.8762 | 562.4993 | 561.6125 | 562.9238 | 570.9892 | 488.0382
2088.6934 | 2016.6934 | 215.504 | 588.5423 | 562.3345 | 561.4621 | 562.4988 | 570.7212 | 487.6288
2089.6948 | 2017.6948 | 215.3214 | 588.21 | 562.1751 | 561.304 | 562.0757 | 570.4673 | 487.2345
2090.6963 | 2018.6963 | 215.1197 | 587.8725 | 562.0044 | 561.1543 | 561.6419 | 570.1831 | 486.8662
2091.6977 | 2019.6977 | 214.8741 | 587.5446 | 561.8362 | 561.0066 | 561.2216 | 569.9413 | 486.4642
2092.6992 | 2020.6992 | 214.6385 | 587.2046 | 561.6681 | 560.8378 | 560.8016 | 569.7878 | 486.0759
2093.7006 | 2021.7006 | 214.4141 | 586.915 | 561.4995 | 560.6768 | 560.4155 | 569.6294 | 485.7004
2094.692 | 2022.692 | 214.1526 | 586.6374 | 561.3234 | 560.5106 | 560.0225 | 569.4024 | 485.2846
2095.6935 | 2023.6935 | 213.899 | 586.3361 | 561.1596 | 560.362 | 559.6372 | 569.2065 | 484.8754
2096.6949 | 2024.6949 | 213.6826 | 586.0419 | 560.9807 | 560.1938 | 559.2402 | 569.0511 | 484.4809
2097.6963 | 2025.6963 | 213.4389 | 585.762 | 560.8196 | 560.0372 | 558.8355 | 568.8444 | 484.1733
2098.6978 | 2026.6978 | 213.2275 | 585.4625 | 560.6392 | 559.8732 | 558.4055 | 568.5756 | 483.8498
2099.6992 | 2027.6992 | 213.0144 | 585.1576 | 560.4576 | 559.7124 | 557.9825 | 568.266 | 483.5075
2100.6906 | 2028.6906 | 212.8052 | 584.8665 | 560.2912 | 559.5536 | 557.5428 | 568.0031 | 483.1061
2101.6921 | 2029.6921 | 212.6247 | 584.5471 | 560.1048 | 559.3967 | 557.0848 | 567.7372 | 482.734
2102.6935 | 2030.6935 | 212.4484 | 584.2298 | 559.917 | 559.2224 | 556.6547 | 567.4825 | 482.3451
2103.695 | 2031.695 | 212.2435 | 583.8994 | 559.7555 | 559.0451 | 556.2675 | 567.2699 | 481.9264
2104.6964 | 2032.6964 | 211.9812 | 583.5555 | 559.5648 | 558.8679 | 555.8821 | 567.0164 | 481.5225
2105.6978 | 2033.6978 | 211.6994 | 583.2155 | 559.3743 | 558.6882 | 555.5104 | 566.7545 | 481.091
2106.6993 | 2034.6993 | 211.4712 | 582.8681 | 559.191 | 558.5151 | 555.1387 | 566.4107 | 480.6843
2107.6907 | 2035.6907 | 211.2736 | 582.4965 | 558.9976 | 558.3407 | 554.7335 | 566.1412 | 480.2607
2108.6922 | 2036.6922 | 211.052 | 582.1362 | 558.8065 | 558.1662 | 554.3033 | 565.9108 | 479.8785
2109.6936 | 2037.6936 | 210.834 | 581.8014 | 558.6174 | 557.9818 | 553.8735 | 565.6715 | 479.5187
2110.695 | 2038.695 | 210.64 | 581.4595 | 558.4232 | 557.7974 | 553.4534 | 565.4404 | 479.1737
2111.6965 | 2039.6965 | 210.4323 | 581.1049 | 558.2251 | 557.608 | 553.0326 | 565.2218 | 478.8129
2112.6979 | 2040.6979 | 210.1861 | 580.781 | 558.0238 | 557.4084 | 552.6192 | 565.0261 | 478.4437
2113.6893 | 2041.6893 | 209.9374 | 580.4434 | 557.8187 | 557.2062 | 552.2386 | 564.8268 | 478.0718

## C6-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 148.558 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38908.5388 | 1 | 0 | 38908.5388 | 1 | 0 | -15 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5395 | 1 | 0 | 38908.5395 | 1 | 0 | 44 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5402 | 1 | 0 | 38908.5402 | 1 | 0 | 102.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5409 | 1 | 0 | 38908.5409 | 1 | 0 | 161.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5416 | 1 | 0 | 38908.5416 | 1 | 0 | 220.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5422 | 1 | 0 | 38908.5422 | 1 | 0 | 279 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5429 | 1 | 0 | 38908.5429 | 1 | 0 | 338 | 410 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5436 | 1 | 0 | 38908.5436 | 1 | 0 | 396.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5443 | 1 | 0 | 38908.5443 | 1 | 0 | 455.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.545 | 1 | 0 | 38908.545 | 1 | 0 | 514.5 | 586.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5456 | 1 | 0 | 38908.5456 | 1 | 0 | 573 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5463 | 1 | 0 | 38908.5463 | 1 | 0 | 632 | 704 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.547 | 1 | 0 | 38908.547 | 1 | 0 | 690.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5477 | 1 | 0 |  | 1 | 0 | 749 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5484 | 1 | 0 | 38908.5484 | 1 | 0 | 808.5 | 880.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.549 | 1 | 0 | 38908.5491 | 1 | 0 | 867 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5497 | 1 | 0 | 38908.5497 | 1 | 0 | 925.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5504 | 1 | 0 | 38908.5504 | 1 | 0 | 984.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5511 | 1 | 0 | 38908.5511 | 1 | 0 | 1043.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5517 | 1 | 0 | 38908.5518 | 1 | 0 | 1102 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5524 | 1 | 0 | 38908.5525 | 1 | 0 | 1161 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5531 | 1 | 0 | 38908.5531 | 1 | 0 | 1219.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243238 | 243238 | 243237.9994
38908.5538 | 2 | 4 | 38908.5538 | 1 | 4 | 1278.5 | 1350.5 | 0.1221 | 0.2442 | 0.06105 | 0.2442 | 0.001221 | 0.002442 | 0.0006105 | 0.002442 | 0.001221 | 0.0018315 | 121869.2885 | 81168.1368 | 60609.8281
38908.5545 | 548 | 529 | 38908.5545 | 973 | 937 | 1337.5 | 1409.5 | 33.4554 | 32.2955 | 59.4017 | 57.2039 | 0.33455 | 0.32295 | 0.59402 | 0.57204 | 0.0116 | 0.021978 | 25940.9534 | 4509.0225 | 250.8414
38908.5552 | 1092 | 1026 | 38908.5552 | 1131 | 1137 | 1396 | 1468 | 66.6667 | 62.6374 | 69.0476 | 69.4139 | 0.66667 | 0.62637 | 0.69048 | 0.69414 | 0.040293 | 0.003663 | 727.3391 | 866.3864 | 27.558
38908.5558 | 1363 | 797 | 38908.5559 | 1202 | 880 | 1455 | 1527 | 83.2112 | 48.6569 | 73.3822 | 53.7241 | 0.83211 | 0.48657 | 0.73382 | 0.53724 | 0.34554 | 0.19658 | 140.0515 | 401.9645 | 27.4678
38908.5565 | 2308 | 13 | 38908.5565 | 2362 | 13 | 1513.5 | 1585.5 | 140.9035 | 0.79365 | 144.2002 | 0.79365 | 1.409 | 0.0079365 | 1.442 | 0.0079365 | 1.4011 | 1.4341 | 6.5881 | 3.3174 | 27.757
38908.5572 | 1989 | 28 | 38908.5572 | 1864 | 28 | 1572.5 | 1644.5 | 121.4286 | 1.7094 | 113.7973 | 1.7094 | 1.2143 | 0.017094 | 1.138 | 0.017094 | 1.1972 | 1.1209 | 23.681 | 33.1466 | 370.2039
38908.5579 | 1705 | 623 | 38908.5579 | 1703 | 650 | 1631.5 | 1703.5 | 104.0904 | 38.0342 | 103.9683 | 39.6825 | 1.0409 | 0.38034 | 1.0397 | 0.39683 | 0.66056 | 0.64286 | 94.631 | 199.4911 | 11.267
38908.5586 | 1904 | 6 | 38908.5586 | 2070 | 6 | 1690 | 1762 | 116.2393 | 0.3663 | 126.3736 | 0.3663 | 1.1624 | 0.003663 | 1.2637 | 0.003663 | 1.1587 | 1.2601 | 28.3961 | 17.7877 | 1317.3042
38908.5592 | 2170 | 2 | 38908.5593 | 2341 | 1 | 1749 | 1821 | 132.4786 | 0.1221 | 142.9182 | 0.06105 | 1.3248 | 0.001221 | 1.4292 | 0.0006105 | 1.3236 | 1.4286 | 12.4382 | 3.9615 | 497.997
38908.5599 | 1909 | 1 | 38908.5599 | 2331 | 2 | 1807.5 | 1879.5 | 116.5446 | 0.06105 | 142.3077 | 0.1221 | 1.1654 | 0.0006105 | 1.4231 | 0.001221 | 1.1648 | 1.4219 | 27.8138 | 4.4095 | 2210.3737
38908.5606 | 2232 | 3 | 38908.5606 | 2145 | 3 | 1866.5 | 1938.5 | 136.2637 | 0.18315 | 130.9524 | 0.18315 | 1.3626 | 0.0018315 | 1.3095 | 0.0018315 | 1.3608 | 1.3077 | 9.1244 | 13.673 | 795.3952
38908.5613 | 2417 | 11 | 38908.5613 | 2077 | 12 | 1925.5 | 1997.5 | 147.558 | 0.67155 | 126.801 | 0.7326 | 1.4756 | 0.0067155 | 1.268 | 0.007326 | 1.4689 | 1.2607 | 0.68351 | 115.1999 | 26.1818
38908.562 | 1930 | 176 | 38908.562 | 2012 | 207 | 1984 | 2056 | 117.8266 | 10.7448 | 122.8327 | 12.6374 | 1.1783 | 0.10745 | 1.2283 | 0.12637 | 1.0708 | 1.102 | 41.6881 | 32.2044 | 45.3115
38908.5626 | 2239 | 56 | 38908.5627 | 1836 | 44 | 2043 | 2115 | 136.6911 | 3.4188 | 112.0879 | 2.6862 | 1.3669 | 0.034188 | 1.1209 | 0.026862 | 1.3327 | 1.094 | 9.4419 | 45.0516 | 76.749

## C5-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.1221 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38908.5388 | 1 | 0 | 38908.5388 | 1 | 0 | -17.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5395 | 1 | 0 | 38908.5395 | 1 | 0 | 41 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5402 | 1 | 0 | 38908.5402 | 1 | 0 | 100 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5408 | 1 | 0 | 38908.5408 | 1 | 0 | 158.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5415 | 2 | 0 | 38908.5415 | 1 | 0 | 217.5 | 289.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123669 | 247438 | 123668.9988
38908.5422 | 1 | 0 | 38908.5422 | 1 | 0 | 276.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5429 | 1 | 0 | 38908.5429 | 1 | 0 | 335 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5436 | 1 | 0 | 38908.5436 | 1 | 0 | 394 | 466 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5442 | 2 | 0 | 38908.5442 | 1 | 0 | 452.5 | 524.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123669 | 247438 | 123668.9988
38908.5449 | 1 | 0 | 38908.5449 | 1 | 0 | 511.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5456 | 1 | 0 | 38908.5456 | 1 | 0 | 570.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5463 | 1 | 0 | 38908.5463 | 1 | 0 | 629 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.547 | 1 | 0 | 38908.547 | 1 | 0 | 688 | 760 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5476 | 1 | 0 | 38908.5477 | 1 | 0 | 746.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5483 | 1 | 0 | 38908.5483 | 1 | 0 | 805.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.549 | 1 | 0 | 38908.549 | 1 | 0 | 864.5 | 936.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5497 | 1 | 0 | 38908.5497 | 1 | 0 | 923 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5504 | 1 | 0 | 38908.5504 | 1 | 0 | 982 | 1054 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.551 | 1 | 0 | 38908.5511 | 1 | 0 | 1040.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5517 | 1 | 0 | 38908.5517 | 1 | 0 | 1099.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5524 | 1 | 0 | 38908.5524 | 1 | 0 | 1158 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5531 | 1 | 0 | 38908.5531 | 1 | 0 | 1217 | 1289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5538 | 3 | 7 | 38908.5538 | 3 | 5 | 1275.5 | 1347.5 | 0.18315 | 0.42735 | 0.18315 | 0.30525 | 0.0018315 | 0.0042735 | 0.0018315 | 0.0030525 | 0.002442 | 0.001221 | 61896.7696 | 124120.3199 | 35191.3617
38908.5544 | 1159 | 1129 | 38908.5545 | 1146 | 1138 | 1334.5 | 1406.5 | 70.757 | 68.9255 | 69.9634 | 69.475 | 0.70757 | 0.68926 | 0.69963 | 0.69475 | 0.018315 | 0.004884 | 1507.8648 | 1970.2996 | 15.7953
38908.5551 | 995 | 938 | 38908.5551 | 1037 | 974 | 1393.5 | 1465.5 | 60.7448 | 57.265 | 63.3089 | 59.4628 | 0.60745 | 0.57265 | 0.63309 | 0.59463 | 0.034799 | 0.038462 | 5310.3653 | 3220.8417 | 56.0818
38908.5558 | 1116 | 955 | 38908.5558 | 1338 | 1026 | 1452 | 1524 | 68.1319 | 58.3028 | 81.685 | 62.6374 | 0.68132 | 0.58303 | 0.81685 | 0.62637 | 0.098291 | 0.19048 | 493.1145 | 832.8079 | 37.8041
38908.5565 | 2021 | 9 | 38908.5565 | 2286 | 10 | 1511 | 1583 | 123.3822 | 0.54945 | 139.5604 | 0.6105 | 1.2338 | 0.0054945 | 1.3956 | 0.006105 | 1.2283 | 1.3895 | 23.8416 | 8.477 | 386.7147
38908.5572 | 2187 | 21 | 38908.5572 | 2162 | 22 | 1569.5 | 1641.5 | 133.5165 | 1.2821 | 131.9902 | 1.3431 | 1.3352 | 0.012821 | 1.3199 | 0.013431 | 1.3223 | 1.3065 | 14.185 | 15.7881 | 173.6108
38908.5578 | 1936 | 653 | 38908.5579 | 1617 | 600 | 1628.5 | 1700.5 | 118.1929 | 39.8657 | 98.7179 | 36.63 | 1.1819 | 0.39866 | 0.98718 | 0.3663 | 0.78327 | 0.62088 | 16.2838 | 32.1776 | 4.2358
38908.5585 | 2345 | 7 | 38908.5585 | 2271 | 6 | 1687.5 | 1759.5 | 143.1624 | 0.42735 | 138.6447 | 0.3663 | 1.4316 | 0.0042735 | 1.3864 | 0.003663 | 1.4274 | 1.3828 | 5.7589 | 9.4585 | 152.3066
38908.5592 | 1936 | 2 | 38908.5592 | 1944 | 1 | 1746 | 1818 | 118.1929 | 0.1221 | 118.6813 | 0.06105 | 1.1819 | 0.001221 | 1.1868 | 0.0006105 | 1.1807 | 1.1862 | 27.995 | 27.3988 | 5778.5346
38908.5599 | 2417 | 2 | 38908.5599 | 2011 | 2 | 1804.5 | 1876.5 | 147.558 | 0.1221 | 122.7717 | 0.1221 | 1.4756 | 0.001221 | 1.2277 | 0.001221 | 1.4744 | 1.2265 | 2.4257 | 24.1042 | 547.5221
38908.5606 | 2241 | 3 | 38908.5606 | 2459 | 3 | 1863.5 | 1935.5 | 136.8132 | 0.18315 | 150.1221 | 0.18315 | 1.3681 | 0.0018315 | 1.5012 | 0.0018315 | 1.3663 | 1.4994 | 13.0764 | 0.67323 | 51.5765
38908.5612 | 2268 | 11 | 38908.5613 | 2376 | 10 | 1922.5 | 1994.5 | 138.4615 | 0.67155 | 145.0549 | 0.6105 | 1.3846 | 0.0067155 | 1.4505 | 0.006105 | 1.3779 | 1.4444 | 10.3389 | 4.3794 | 74.9033
38908.5619 | 2159 | 128 | 38908.5619 | 1827 | 132 | 1981.5 | 2053.5 | 131.8071 | 7.8144 | 111.5385 | 8.0586 | 1.3181 | 0.078144 | 1.1154 | 0.080586 | 1.2399 | 1.0348 | 17.1141 | 70.1932 | 60.6984
38908.5626 | 1844 | 42 | 38908.5626 | 2358 | 42 | 2040 | 2112 | 112.5763 | 2.5641 | 143.956 | 2.5641 | 1.1258 | 0.025641 | 1.4396 | 0.025641 | 1.1001 | 1.4139 | 63.3255 | 5.2176 | 69.5876

## C5-6
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 150.8168 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38908.5388 | 1 | 0 | 38908.5388 | 1 | 0 | -20.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5394 | 1 | 0 | 38908.5395 | 1 | 0 | 38.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5401 | 1 | 0 | 38908.5401 | 1 | 0 | 97 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5408 | 1 | 0 | 38908.5408 | 1 | 0 | 156 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5415 | 1 | 0 | 38908.5415 | 1 | 0 | 214.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5422 | 1 | 0 | 38908.5422 | 1 | 0 | 273.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5428 | 1 | 0 | 38908.5429 | 1 | 0 | 332.5 | 404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5435 | 1 | 0 | 38908.5435 | 1 | 0 | 391 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5442 | 1 | 0 | 38908.5442 | 1 | 0 | 450 | 522 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5449 | 1 | 0 | 38908.5449 | 1 | 0 | 508.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5456 | 1 | 0 | 38908.5456 | 1 | 0 | 567.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5462 | 1 | 0 | 38908.5463 | 1 | 0 | 626.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5469 | 1 | 0 | 38908.5469 | 1 | 0 | 685 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5476 | 1 | 0 | 38908.5476 | 1 | 0 | 743.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5483 | 1 | 0 | 38908.5483 | 1 | 0 | 802.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.549 | 1 | 0 | 38908.549 | 1 | 0 | 861.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5497 | 1 | 0 | 38908.5497 | 1 | 0 | 920.5 | 992.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5503 | 1 | 0 | 38908.5503 | 1 | 0 | 979 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.551 | 1 | 0 | 38908.551 | 1 | 0 | 1038 | 1110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5517 | 1 | 0 | 38908.5517 | 1 | 0 | 1096.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.5524 | 1 | 0 | 38908.5524 | 2 | 1 | 1155.5 | 1227.5 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38908.553 | 21 | 20 | 38908.5531 | 2 | 1 | 1214 | 1286 | 1.2821 | 1.221 | 0.1221 | 0.06105 | 0.012821 | 0.01221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 246938 | 246938 | 12141.983
38908.5537 | 1199 | 1185 | 38908.5537 | 1193 | 1198 | 1273 | 1345 | 73.199 | 72.3443 | 72.8327 | 73.138 | 0.73199 | 0.72344 | 0.72833 | 0.73138 | 0.008547 | 0.0030525 | 1709.3152 | 1962.5869 | 6.936
38908.5544 | 1088 | 1060 | 38908.5544 | 927 | 1029 | 1331.5 | 1403.5 | 66.4225 | 64.7131 | 56.5934 | 62.8205 | 0.66422 | 0.64713 | 0.56593 | 0.62821 | 0.017094 | 0.062271 | 1606.6433 | 1826.2795 | 28.8344
38908.5551 | 1146 | 1087 | 38908.5551 | 1143 | 1160 | 1390.5 | 1462.5 | 69.9634 | 66.3614 | 69.7802 | 70.8181 | 0.69963 | 0.66361 | 0.6978 | 0.70818 | 0.03602 | 0.010379 | 830.6572 | 1082.2639 | 19.9909
38908.5558 | 1192 | 917 | 38908.5558 | 1228 | 932 | 1449.5 | 1521.5 | 72.7717 | 55.9829 | 74.9695 | 56.8987 | 0.72772 | 0.55983 | 0.74969 | 0.56899 | 0.16789 | 0.18071 | 1044.6648 | 600.8082 | 33.7856
38908.5564 | 2429 | 10 | 38908.5565 | 2026 | 9 | 1508 | 1580 | 148.2906 | 0.6105 | 123.6874 | 0.54945 | 1.4829 | 0.006105 | 1.2369 | 0.0054945 | 1.4768 | 1.2314 | 1.7348 | 29.6607 | 71.7838
38908.5571 | 2037 | 15 | 38908.5572 | 2159 | 20 | 1567 | 1639 | 124.359 | 0.91575 | 131.8071 | 1.221 | 1.2436 | 0.0091575 | 1.3181 | 0.01221 | 1.2344 | 1.3059 | 22.5339 | 15.1875 | 367.7557
38908.5578 | 1891 | 589 | 38908.5578 | 1741 | 629 | 1625.5 | 1697.5 | 115.4457 | 35.9585 | 106.2882 | 38.4005 | 1.1545 | 0.35958 | 1.0629 | 0.384 | 0.79487 | 0.67888 | 17.6823 | 29.8288 | 0.37525
38908.5585 | 2454 | 8 | 38908.5585 | 2220 | 7 | 1684.5 | 1756.5 | 149.8168 | 0.4884 | 135.5311 | 0.42735 | 1.4982 | 0.004884 | 1.3553 | 0.0042735 | 1.4933 | 1.351 | 0.68018 | 21.1494 | 18.2865
38908.5592 | 2285 | 1 | 38908.5592 | 2222 | 1 | 1743.5 | 1815.5 | 139.4994 | 0.06105 | 135.6532 | 0.06105 | 1.395 | 0.0006105 | 1.3565 | 0.0006105 | 1.3944 | 1.3559 | 8.1482 | 11.2454 | 1863.83
38908.5598 | 2016 | 1 | 38908.5599 | 2334 | 2 | 1802 | 1874 | 123.0769 | 0.06105 | 142.4908 | 0.1221 | 1.2308 | 0.0006105 | 1.4249 | 0.001221 | 1.2302 | 1.4237 | 22.7421 | 5.8703 | 2513.9178
38908.5605 | 2239 | 3 | 38908.5606 | 2192 | 2 | 1861 | 1933 | 136.6911 | 0.18315 | 133.8217 | 0.1221 | 1.3669 | 0.0018315 | 1.3382 | 0.001221 | 1.3651 | 1.337 | 10.4574 | 12.8234 | 865.2486
38908.5612 | 2053 | 9 | 38908.5612 | 2123 | 10 | 1919.5 | 1991.5 | 125.3358 | 0.54945 | 129.6093 | 0.6105 | 1.2534 | 0.0054945 | 1.2961 | 0.006105 | 1.2479 | 1.29 | 20.9687 | 16.8198 | 653.319
38908.5619 | 2075 | 73 | 38908.5619 | 2147 | 76 | 1978.5 | 2050.5 | 126.6789 | 4.4567 | 131.0745 | 4.6398 | 1.2668 | 0.044567 | 1.3107 | 0.046398 | 1.2222 | 1.2643 | 24.6482 | 18.3461 | 68.4598
38908.5626 | 2123 | 50 | 38908.5626 | 2122 | 47 | 2037.5 | 2109.5 | 129.6093 | 3.0525 | 129.5482 | 2.8694 | 1.2961 | 0.030525 | 1.2955 | 0.028694 | 1.2656 | 1.2668 | 19.1886 | 19.0365 | 95.115

## C4-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 149.84 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38908.5387 | 1 | 0 | 38908.5387 | 1 | 0 | -23.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5394 | 1 | 0 | 38908.5394 | 1 | 0 | 35.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5401 | 1 | 0 | 38908.5401 | 1 | 0 | 94.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5408 | 1 | 0 | 38908.5408 | 1 | 0 | 153 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5414 | 1 | 0 | 38908.5415 | 1 | 0 | 212 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
| 1 | 0 | 38908.5421 | 1 | 0 | 271 | 343 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5428 | 1 | 0 | 38908.5428 | 1 | 0 | 329.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5435 | 1 | 0 | 38908.5435 | 1 | 0 | 388.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5442 | 1 | 0 | 38908.5442 | 1 | 0 | 447 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5448 | 1 | 0 | 38908.5449 | 1 | 0 | 506 | 578 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5455 | 1 | 0 | 38908.5455 | 1 | 0 | 564.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5462 | 1 | 0 | 38908.5462 | 1 | 0 | 623.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5469 | 1 | 0 | 38908.5469 | 1 | 0 | 682.5 | 754.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5476 | 1 | 0 | 38908.5476 | 1 | 0 | 741 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5483 | 1 | 0 | 38908.5483 | 1 | 0 | 800 | 872 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5489 | 1 | 0 | 38908.5489 | 1 | 0 | 858.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5496 | 1 | 0 | 38908.5496 | 1 | 0 | 917.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5503 | 1 | 0 | 38908.5503 | 1 | 0 | 976 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.551 | 1 | 0 | 38908.551 | 1 | 0 | 1035 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5517 | 1 | 0 | 38908.5517 | 2 | 0 | 1093.5 | 1165.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245338 | 122619 | 245337.9994
38908.5523 | 1 | 0 | 38908.5523 | 1 | 0 | 1152.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.553 | 1 | 0 | 38908.553 | 1 | 0 | 1211.5 | 1283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5537 | 1 | 0 | 38908.5537 | 1 | 0 | 1270 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5544 | 1030 | 1075 | 38908.5544 | 1117 | 1088 | 1329 | 1401 | 62.8816 | 65.6288 | 68.1929 | 66.4225 | 0.62882 | 0.65629 | 0.68193 | 0.66422 | 0.027473 | 0.017705 | 2535.0253 | 9608.5097 | 32.1657
38908.5551 | 1014 | 1033 | 38908.5551 | 1074 | 1017 | 1387.5 | 1459.5 | 61.9048 | 63.0647 | 65.5678 | 62.0879 | 0.61905 | 0.63065 | 0.65568 | 0.62088 | 0.0116 | 0.034799 | 2871.6759 | 3315.3427 | 38.2819
38908.5557 | 1037 | 867 | 38908.5558 | 1059 | 869 | 1446.5 | 1518.5 | 63.3089 | 52.9304 | 64.652 | 53.0525 | 0.63309 | 0.5293 | 0.64652 | 0.53053 | 0.10379 | 0.116 | 1689.1322 | 1007.1058 | 57.747
38908.5564 | 2134 | 13 | 38908.5564 | 2425 | 14 | 1505.5 | 1577.5 | 130.2808 | 0.79365 | 148.0464 | 0.8547 | 1.3028 | 0.0079365 | 1.4805 | 0.008547 | 1.2949 | 1.4719 | 29.8036 | 1.2428 | 29.0247
38908.5571 | 1918 | 18 | 38908.5571 | 1957 | 18 | 1564 | 1636 | 117.094 | 1.0989 | 119.475 | 1.0989 | 1.1709 | 0.010989 | 1.1947 | 0.010989 | 1.16 | 1.1838 | 29.2775 | 26.4913 | 603.141
38908.5578 | 1704 | 533 | 38908.5578 | 1823 | 546 | 1623 | 1695 | 104.0293 | 32.5397 | 111.2943 | 33.3333 | 1.0403 | 0.3254 | 1.1129 | 0.33333 | 0.7149 | 0.77961 | 311.3142 | 57.3141 | 14.8589
38908.5585 | 1769 | 168 | 38908.5585 | 2438 | 8 | 1681.5 | 1753.5 | 107.9976 | 10.2564 | 148.84 | 0.4884 | 1.08 | 0.10256 | 1.4884 | 0.004884 | 0.97741 | 1.4835 | 2.5869 | 0.67489 | 2.0645
38908.5591 | 1976 | 1 | 38908.5592 | 1915 | 1 | 1740.5 | 1812.5 | 120.6349 | 0.06105 | 116.9109 | 0.06105 | 1.2063 | 0.0006105 | 1.1691 | 0.0006105 | 1.2057 | 1.1685 | 24.2653 | 28.2416 | 10512.9444
38908.5598 | 1971 | 1 | 38908.5598 | 2099 | 2 | 1799.5 | 1871.5 | 120.3297 | 0.06105 | 128.1441 | 0.1221 | 1.2033 | 0.0006105 | 1.2814 | 0.001221 | 1.2027 | 1.2802 | 24.6105 | 17.013 | 7013.5202
38908.5605 | 2371 | 4 | 38908.5605 | 2406 | 3 | 1858 | 1930 | 144.7497 | 0.2442 | 146.8864 | 0.18315 | 1.4475 | 0.002442 | 1.4689 | 0.0018315 | 1.4451 | 1.467 | 3.8339 | 2.0811 | 40.4571
38908.5612 | 1925 | 8 | 38908.5612 | 1949 | 8 | 1917 | 1989 | 117.5214 | 0.4884 | 118.9866 | 0.4884 | 1.1752 | 0.004884 | 1.1899 | 0.004884 | 1.1703 | 1.185 | 28.0581 | 26.4253 | 1362.2283
38908.5619 | 2090 | 77 | 38908.5619 | 1935 | 64 | 1975.5 | 2047.5 | 127.5946 | 4.7009 | 118.1319 | 3.9072 | 1.2759 | 0.047009 | 1.1813 | 0.039072 | 1.2289 | 1.1422 | 20.4476 | 33.3362 | 93.3113
38908.5625 | 2364 | 36 | 38908.5626 | 1879 | 38 | 2034.5 | 2106.5 | 144.3223 | 2.1978 | 114.7131 | 2.3199 | 1.4432 | 0.021978 | 1.1471 | 0.023199 | 1.4212 | 1.1239 | 3.9769 | 64.9785 | 59.4948

## C4-6
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 150.5726 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38908.5387 | 1 | 0 | 38908.5387 | 1 | 0 | -26 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5394 | 1 | 0 | 38908.5394 | 1 | 0 | 32.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5401 | 1 | 0 | 38908.5401 | 1 | 0 | 91.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5407 | 1 | 0 | 38908.5408 | 1 | 0 | 150.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5414 | 1 | 0 | 38908.5414 | 2 | 0 | 209 | 281 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 246538 | 123219 | 246537.9994
38908.5421 | 1 | 0 | 38908.5421 | 1 | 0 | 268 | 340 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5428 | 1 | 0 | 38908.5428 | 1 | 0 | 326.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5435 | 1 | 0 | 38908.5435 | 1 | 0 | 385.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5441 | 1 | 0 | 38908.5442 | 1 | 0 | 444.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5448 | 1 | 0 | 38908.5448 | 1 | 0 | 503 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5455 | 1 | 0 | 38908.5455 | 1 | 0 | 562 | 634 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5462 | 1 | 0 | 38908.5462 | 1 | 0 | 620.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5469 | 1 | 0 | 38908.5469 | 1 | 0 | 679.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5475 | 1 | 0 | 38908.5476 | 1 | 0 | 738.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5482 | 1 | 0 | 38908.5482 | 1 | 0 | 797 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5489 | 1 | 0 | 38908.5489 | 1 | 0 | 856 | 928 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5496 | 1 | 0 | 38908.5496 | 1 | 0 | 914.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5503 | 1 | 0 | 38908.5503 | 1 | 0 | 973.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5509 | 1 | 0 | 38908.551 | 1 | 0 | 1032 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5516 | 1 | 0 | 38908.5516 | 1 | 0 | 1091 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5523 | 1 | 0 | 38908.5523 | 1 | 0 | 1149.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.553 | 1 | 0 | 38908.553 | 1 | 0 | 1208.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5537 | 1 | 0 | 38908.5537 | 1 | 0 | 1267.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
38908.5543 | 867 | 838 | 38908.5544 | 887 | 857 | 1326 | 1398 | 52.9304 | 51.16 | 54.1514 | 52.3199 | 0.5293 | 0.5116 | 0.54151 | 0.5232 | 0.017705 | 0.018315 | 8749.6904 | 7816.6358 | 89.7091
38908.555 | 953 | 904 | 38908.555 | 1117 | 1153 | 1385 | 1457 | 58.1807 | 55.1893 | 68.1929 | 70.3907 | 0.58181 | 0.55189 | 0.68193 | 0.70391 | 0.029915 | 0.021978 | 2977.7937 | 49610.6179 | 67.2737
38908.5557 | 1252 | 1000 | 38908.5557 | 1253 | 1041 | 1443.5 | 1515.5 | 76.4347 | 61.0501 | 76.4957 | 63.5531 | 0.76435 | 0.6105 | 0.76496 | 0.63553 | 0.15385 | 0.12943 | 461.231 | 8856.552 | 21.1986
38908.5564 | 1929 | 13 | 38908.5564 | 2109 | 13 | 1502.5 | 1574.5 | 117.7656 | 0.79365 | 128.7546 | 0.79365 | 1.1777 | 0.0079365 | 1.2875 | 0.0079365 | 1.1697 | 1.2796 | 29.1836 | 17.4208 | 598.4475
38908.5571 | 2011 | 11 | 38908.5571 | 2405 | 15 | 1561.5 | 1633.5 | 122.7717 | 0.67155 | 146.8254 | 0.91575 | 1.2277 | 0.0067155 | 1.4683 | 0.0091575 | 1.221 | 1.4591 | 28.803 | 2.6254 | 103.3484
38908.5577 | 1644 | 475 | 38908.5578 | 1714 | 617 | 1620 | 1692 | 100.3663 | 28.9988 | 104.6398 | 37.6679 | 1.0037 | 0.28999 | 1.0464 | 0.37668 | 0.71368 | 0.66972 | 90.8525 | 180.0482 | 47.0183
38908.5584 | 2151 | 227 | 38908.5584 | 1788 | 177 | 1679 | 1751 | 131.3187 | 13.8584 | 109.1575 | 10.8059 | 1.3132 | 0.13858 | 1.0916 | 0.10806 | 1.1746 | 0.98352 | 18.4957 | 103.7243 | 19.8228
38908.5591 | 2192 | 2 | 38908.5591 | 1925 | 1 | 1737.5 | 1809.5 | 133.8217 | 0.1221 | 117.5214 | 0.06105 | 1.3382 | 0.001221 | 1.1752 | 0.0006105 | 1.337 | 1.1746 | 12.5694 | 28.2551 | 3000.3181
38908.5598 | 2358 | 2 | 38908.5598 | 2450 | 2 | 1796.5 | 1868.5 | 143.956 | 0.1221 | 149.5726 | 0.1221 | 1.4396 | 0.001221 | 1.4957 | 0.001221 | 1.4383 | 1.4945 | 5.2567 | 0.67968 | 35.9082
38908.5605 | 2105 | 2 | 38908.5605 | 2183 | 2 | 1855.5 | 1927.5 | 128.5104 | 0.1221 | 133.2723 | 0.1221 | 1.2851 | 0.001221 | 1.3327 | 0.001221 | 1.2839 | 1.3315 | 17.3101 | 13.0623 | 2075.9953
38908.5611 | 2296 | 10 | 38908.5612 | 2313 | 9 | 1914 | 1986 | 140.1709 | 0.6105 | 141.2088 | 0.54945 | 1.4017 | 0.006105 | 1.4121 | 0.0054945 | 1.3956 | 1.4066 | 7.9499 | 7.0011 | 104.9372
38908.5618 | 1937 | 62 | 38908.5618 | 2323 | 80 | 1972.5 | 2044.5 | 118.254 | 3.7851 | 141.8193 | 4.884 | 1.1825 | 0.037851 | 1.4182 | 0.04884 | 1.1447 | 1.3694 | 54.6672 | 6.8385 | 48.2515
38908.5625 | 2286 | 47 | 38908.5625 | 2333 | 37 | 2031.5 | 2103.5 | 139.5604 | 2.8694 | 142.4298 | 2.2589 | 1.3956 | 0.028694 | 1.4243 | 0.022589 | 1.3669 | 1.4017 | 11.7027 | 6.7369 | 17.9118

## C4-5
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 148.8632 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38908.5387 | 1 | 0 | 38908.5387 | 1 | 0 | -29 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5393 | 1 | 0 | 38908.5394 | 1 | 0 | 30 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.54 | 1 | 0 | 38908.54 | 1 | 0 | 88.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5407 | 1 | 0 | 38908.5407 | 1 | 0 | 147.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5414 | 1 | 0 | 38908.5414 | 1 | 0 | 206.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5421 | 1 | 0 | 38908.5421 | 1 | 0 | 265 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5427 | 1 | 0 | 38908.5428 | 1 | 0 | 324 | 396 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5434 | 1 | 0 | 38908.5434 | 1 | 0 | 382.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5441 | 1 | 0 | 38908.5441 | 1 | 0 | 441.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5448 | 1 | 0 | 38908.5448 | 1 | 0 | 500.5 | 572.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5455 | 1 | 0 | 38908.5455 | 1 | 0 | 559 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5461 | 1 | 0 | 38908.5462 | 1 | 0 | 618 | 690 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5468 | 1 | 0 | 38908.5468 | 1 | 0 | 676.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5475 | 1 | 0 | 38908.5475 | 1 | 0 | 735.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5482 | 1 | 0 | 38908.5482 | 1 | 0 | 794 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5489 | 1 | 0 | 38908.5489 | 1 | 0 | 853 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5495 | 1 | 0 | 38908.5496 | 1 | 0 | 911.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5502 | 1 | 0 | 38908.5502 | 1 | 0 | 970.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5509 | 1 | 0 | 38908.5509 | 1 | 0 | 1029.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5516 | 1 | 0 | 38908.5516 | 1 | 0 | 1088 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5523 | 1 | 0 | 38908.5523 | 1 | 0 | 1147 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.553 | 1 | 0 | 38908.553 | 1 | 0 | 1205.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5536 | 1 | 0 | 38908.5536 | 1 | 0 | 1264.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38908.5543 | 969 | 938 | 38908.5543 | 958 | 899 | 1323.5 | 1395.5 | 59.1575 | 57.265 | 58.486 | 54.884 | 0.59158 | 0.57265 | 0.58486 | 0.54884 | 0.018926 | 0.03602 | 14094.6852 | 4558.945 | 55.4344
38908.555 | 1053 | 1004 | 38908.555 | 1103 | 1051 | 1382 | 1454 | 64.2857 | 61.2943 | 67.3382 | 64.1636 | 0.64286 | 0.61294 | 0.67338 | 0.64164 | 0.029915 | 0.031746 | 6009.584 | 3869.4028 | 37.0291
38908.5557 | 1143 | 918 | 38908.5557 | 1121 | 958 | 1441 | 1513 | 69.7802 | 56.044 | 68.4371 | 58.486 | 0.6978 | 0.56044 | 0.68437 | 0.58486 | 0.13736 | 0.099512 | 563.4851 | 18783.8391 | 40.8912
38908.5564 | 2091 | 11 | 38908.5564 | 2201 | 11 | 1499.5 | 1571.5 | 127.6557 | 0.67155 | 134.3712 | 0.67155 | 1.2766 | 0.0067155 | 1.3437 | 0.0067155 | 1.2698 | 1.337 | 17.5318 | 11.159 | 306.985
38908.557 | 2004 | 6 | 38908.557 | 2188 | 6 | 1558.5 | 1630.5 | 122.3443 | 0.3663 | 133.5775 | 0.3663 | 1.2234 | 0.003663 | 1.3358 | 0.003663 | 1.2198 | 1.3321 | 22.3176 | 11.6179 | 743.1441
38908.5577 | 1877 | 417 | 38908.5577 | 1551 | 367 | 1617.5 | 1689.5 | 114.591 | 25.4579 | 94.6886 | 22.4054 | 1.1459 | 0.25458 | 0.94689 | 0.22405 | 0.89133 | 0.72283 | 43.0404 | 267.8369 | 25.2108
38908.5584 | 1703 | 315 | 38908.5584 | 2049 | 327 | 1676 | 1748 | 103.9683 | 19.2308 | 125.0916 | 19.9634 | 1.0397 | 0.19231 | 1.2509 | 0.19963 | 0.84737 | 1.0513 | 9303.8154 | 22.8245 | 24.7998
38908.5591 | 1938 | 1 | 38908.5591 | 2422 | 2 | 1735 | 1807 | 118.315 | 0.06105 | 147.8632 | 0.1221 | 1.1832 | 0.0006105 | 1.4786 | 0.001221 | 1.1825 | 1.4774 | 27.9589 | 0.67887 | 336.7263
38908.5598 | 2378 | 2 | 38908.5598 | 2323 | 1 | 1793.5 | 1865.5 | 145.177 | 0.1221 | 141.8193 | 0.06105 | 1.4518 | 0.001221 | 1.4182 | 0.0006105 | 1.4505 | 1.4176 | 2.5843 | 5.0532 | 140.4079
38908.5604 | 1926 | 1 | 38908.5605 | 1931 | 2 | 1852.5 | 1924.5 | 117.5824 | 0.06105 | 117.8877 | 0.1221 | 1.1758 | 0.0006105 | 1.1789 | 0.001221 | 1.1752 | 1.1777 | 26.6696 | 26.4054 | 10682.4502
38908.5611 | 1957 | 8 | 38908.5611 | 1939 | 8 | 1911.5 | 1983.5 | 119.475 | 0.4884 | 118.3761 | 0.4884 | 1.1947 | 0.004884 | 1.1838 | 0.004884 | 1.1899 | 1.1789 | 25.0905 | 26.2954 | 1232.0042
38908.5618 | 2291 | 73 | 38908.5618 | 1837 | 59 | 1970 | 2042 | 139.8657 | 4.4567 | 112.149 | 3.602 | 1.3987 | 0.044567 | 1.1215 | 0.03602 | 1.3541 | 1.0855 | 7.0033 | 64.2816 | 39.8686
38908.5625 | 1875 | 38 | 38908.5625 | 1929 | 39 | 2029 | 2101 | 114.4689 | 2.3199 | 117.7656 | 2.381 | 1.1447 | 0.023199 | 1.1777 | 0.02381 | 1.1215 | 1.1538 | 33.0465 | 28.7463 | 308.7004

## C3-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38908.5386 | 1 | 0 | 38908.5386 | 1 | 0 | -31.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5393 | 1 | 0 | 38908.5393 | 1 | 0 | 27 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.54 | 1 | 0 | 38908.54 | 2 | 0 | 86 | 158 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 247238 | 123569 | 247237.9994
38908.5407 | 1 | 0 | 38908.5407 | 1 | 0 | 144.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5414 | 1 | 0 | 38908.5414 | 1 | 0 | 203.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.542 | 1 | 0 | 38908.542 | 1 | 0 | 262.5 | 334.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5427 | 1 | 0 | 38908.5427 | 1 | 0 | 321 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5434 | 1 | 0 | 38908.5434 | 1 | 0 | 380 | 452 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5441 | 1 | 0 | 38908.5441 | 1 | 0 | 438.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5448 | 1 | 0 | 38908.5448 | 1 | 0 | 497.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5454 | 1 | 0 | 38908.5455 | 1 | 0 | 556.5 | 628.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5461 | 1 | 0 | 38908.5461 | 1 | 0 | 615 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5468 | 1 | 0 | 38908.5468 | 1 | 0 | 674 | 746 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5475 | 1 | 0 | 38908.5475 | 1 | 0 | 732.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5482 | 1 | 0 | 38908.5482 | 1 | 0 | 791.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5488 | 1 | 0 | 38908.5489 | 1 | 0 | 850 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5495 | 1 | 0 | 38908.5495 | 1 | 0 | 909 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5502 | 1 | 0 | 38908.5502 | 1 | 0 | 967.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5509 | 1 | 0 | 38908.5509 | 1 | 0 | 1026.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5516 | 1 | 0 | 38908.5516 | 1 | 0 | 1085.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5522 | 1 | 0 | 38908.5523 | 1 | 0 | 1144 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5529 | 1 | 0 | 38908.5529 | 1 | 0 | 1203 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5536 | 1 | 0 | 38908.5536 | 1 | 0 | 1261.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
38908.5543 | 980 | 948 | 38908.5543 | 1064 | 1112 | 1320.5 | 1392.5 | 59.8291 | 57.8755 | 64.9573 | 67.8877 | 0.59829 | 0.57875 | 0.64957 | 0.67888 | 0.019536 | 0.029304 | 260143.5976 | 3016.6162 | 55.6836
38908.555 | 977 | 931 | 38908.555 | 1044 | 1068 | 1379.5 | 1451.5 | 59.6459 | 56.8376 | 63.7363 | 65.2015 | 0.59646 | 0.56838 | 0.63736 | 0.65201 | 0.028083 | 0.014652 | 2636.8443 | 8661.3548 | 60.0351
38908.5556 | 1048 | 911 | 38908.5557 | 1205 | 813 | 1438 | 1510 | 63.9805 | 55.6166 | 73.5653 | 49.6337 | 0.6398 | 0.55617 | 0.73565 | 0.49634 | 0.083639 | 0.23932 | 582.1193 | 844.6098 | 50.4858
38908.5563 | 1908 | 17 | 38908.5563 | 1921 | 17 | 1497 | 1569 | 116.4835 | 1.0379 | 117.2772 | 1.0379 | 1.1648 | 0.010379 | 1.1728 | 0.010379 | 1.1545 | 1.1624 | 30.826 | 29.8769 | 742.0558
38908.557 | 2059 | 9 | 38908.557 | 1970 | 9 | 1555.5 | 1627.5 | 125.7021 | 0.54945 | 120.2686 | 0.54945 | 1.257 | 0.0054945 | 1.2027 | 0.0054945 | 1.2515 | 1.1972 | 20.5574 | 26.2557 | 936.6832
38908.5577 | 2030 | 85 | 38908.5577 | 2140 | 137 | 1614.5 | 1686.5 | 123.9316 | 5.1893 | 130.6471 | 8.3639 | 1.2393 | 0.051893 | 1.3065 | 0.083639 | 1.1874 | 1.2228 | 28.4772 | 21.9053 | 75.7621
38908.5584 | 1698 | 300 | 38908.5584 | 1654 | 367 | 1673.5 | 1745.5 | 103.663 | 18.315 | 100.9768 | 22.4054 | 1.0366 | 0.18315 | 1.0098 | 0.22405 | 0.85348 | 0.78571 | 69.1645 | 108.329 | 82.3976
38908.559 | 2457 | 2 | 38908.5591 | 2004 | 2 | 1732 | 1804 | 150 | 0.1221 | 122.3443 | 0.1221 | 1.5 | 0.001221 | 1.2234 | 0.001221 | 1.4988 | 1.2222 | 0.66919 | 27.5598 | 155.343
38908.5597 | 2371 | 2 | 38908.5597 | 2357 | 2 | 1791 | 1863 | 144.7497 | 0.1221 | 143.895 | 0.1221 | 1.4475 | 0.001221 | 1.4389 | 0.001221 | 1.4463 | 1.4377 | 4.3953 | 5.0392 | 240.7836
38908.5604 | 2441 | 2 | 38908.5604 | 2118 | 2 | 1849.5 | 1921.5 | 149.0232 | 0.1221 | 129.304 | 0.1221 | 1.4902 | 0.001221 | 1.293 | 0.001221 | 1.489 | 1.2918 | 1.3336 | 18.076 | 232.5402
38908.5611 | 2357 | 9 | 38908.5611 | 2440 | 8 | 1908.5 | 1980.5 | 143.895 | 0.54945 | 148.9621 | 0.4884 | 1.4389 | 0.0054945 | 1.4896 | 0.004884 | 1.4335 | 1.4847 | 6.7497 | 1.4429 | 16.97
38908.5618 | 2128 | 70 | 38908.5618 | 2279 | 69 | 1967.5 | 2039.5 | 129.9145 | 4.2735 | 139.1331 | 4.2125 | 1.2991 | 0.042735 | 1.3913 | 0.042125 | 1.2564 | 1.3492 | 25.396 | 10.0284 | 35.8558
38908.5624 | 2338 | 41 | 38908.5625 | 1946 | 36 | 2026 | 2098 | 142.735 | 2.5031 | 118.8034 | 2.1978 | 1.4274 | 0.025031 | 1.188 | 0.021978 | 1.4023 | 1.1661 | 6.1708 | 39.7539 | 65.4805

## C3-6
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 148.6801 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38908.5386 | 1 | 0 | 38908.5386 | 1 | 0 | -34.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5393 | 1 | 0 | 38908.5393 | 1 | 0 | 24.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.54 | 2 | 0 | 38908.54 | 2 | 0 | 83 | 155 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121669 | 121669 | 121668.9988
38908.5406 | 2 | 0 | 38908.5407 | 1 | 0 | 142 | 214 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121669 | 243438 | 121668.9988
38908.5413 | 1 | 0 | 38908.5413 | 1 | 0 | 200.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.542 | 1 | 0 | 38908.542 | 1 | 0 | 259.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5427 | 1 | 0 | 38908.5427 | 1 | 0 | 318.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5434 | 1 | 0 | 38908.5434 | 1 | 0 | 377 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.544 | 1 | 0 | 38908.5441 | 1 | 0 | 436 | 508 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5447 | 1 | 0 | 38908.5447 | 1 | 0 | 494.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5454 | 1 | 0 | 38908.5454 | 1 | 0 | 553.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5461 | 1 | 0 | 38908.5461 | 1 | 0 | 612 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5468 | 1 | 0 | 38908.5468 | 1 | 0 | 671 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5474 | 2 | 0 | 38908.5475 | 1 | 0 | 729.5 | 801.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121669 | 243438 | 121668.9988
38908.5481 | 1 | 0 | 38908.5481 | 1 | 0 | 788.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5488 | 1 | 0 | 38908.5488 | 1 | 0 | 847.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5495 | 1 | 0 | 38908.5495 | 1 | 0 | 906.5 | 978.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5502 | 1 | 0 | 38908.5502 | 1 | 0 | 965 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5508 | 1 | 0 | 38908.5509 | 1 | 0 | 1024 | 1096 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5515 | 1 | 0 | 38908.5515 | 1 | 0 | 1082.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5522 | 1 | 0 | 38908.5522 | 1 | 0 | 1141.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5529 | 1 | 0 | 38908.5529 | 1 | 0 | 1200 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5536 | 1 | 0 | 38908.5536 | 1 | 0 | 1259 | 1331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243438 | 243438 | 243437.9994
38908.5542 | 1173 | 1155 | 38908.5543 | 987 | 916 | 1317.5 | 1389.5 | 71.6117 | 70.5128 | 60.2564 | 55.9219 | 0.71612 | 0.70513 | 0.60256 | 0.55922 | 0.010989 | 0.043346 | 1377.38 | 1568.2108 | 8.7397
38908.5549 | 1169 | 1122 | 38908.5549 | 1158 | 1113 | 1376.5 | 1448.5 | 71.3675 | 68.4982 | 70.696 | 67.9487 | 0.71368 | 0.68498 | 0.70696 | 0.67949 | 0.028694 | 0.027473 | 3863.7048 | 7888.2506 | 12.707
38908.5556 | 1109 | 911 | 38908.5556 | 1187 | 965 | 1435.5 | 1507.5 | 67.7045 | 55.6166 | 72.4664 | 58.9133 | 0.67705 | 0.55617 | 0.72466 | 0.58913 | 0.12088 | 0.13553 | 1728.4356 | 751.2705 | 40.2398
38908.5563 | 2346 | 21 | 38908.5563 | 2175 | 21 | 1494 | 1566 | 143.2234 | 1.2821 | 132.7839 | 1.2821 | 1.4322 | 0.012821 | 1.3278 | 0.012821 | 1.4194 | 1.315 | 4.076 | 15.8885 | 44.643
38908.557 | 2053 | 9 | 38908.557 | 1970 | 9 | 1553 | 1625 | 125.3358 | 0.54945 | 120.2686 | 0.54945 | 1.2534 | 0.0054945 | 1.2027 | 0.0054945 | 1.2479 | 1.1972 | 19.0524 | 24.3175 | 811.5138
38908.5577 | 2157 | 74 | 38908.5577 | 1897 | 65 | 1611.5 | 1683.5 | 131.685 | 4.5177 | 115.812 | 3.9683 | 1.3168 | 0.045177 | 1.1581 | 0.039683 | 1.2717 | 1.1184 | 14.7142 | 38.7254 | 77.0986
38908.5583 | 1879 | 196 | 38908.5583 | 1937 | 256 | 1670.5 | 1742.5 | 114.7131 | 11.9658 | 118.254 | 15.6288 | 1.1471 | 0.11966 | 1.1825 | 0.15629 | 1.0275 | 1.0263 | 44.5933 | 45.0239 | 57.0832
38908.559 | 2090 | 1 | 38908.559 | 2419 | 2 | 1729.5 | 1801.5 | 127.5946 | 0.06105 | 147.6801 | 0.1221 | 1.2759 | 0.0006105 | 1.4768 | 0.001221 | 1.2753 | 1.4756 | 17.7836 | 0.68087 | 232.8915
38908.5597 | 2287 | 1 | 38908.5597 | 2316 | 2 | 1788 | 1860 | 139.6215 | 0.06105 | 141.3919 | 0.1221 | 1.3962 | 0.0006105 | 1.4139 | 0.001221 | 1.3956 | 1.4127 | 6.5456 | 5.2281 | 732.2308
38908.5604 | 2309 | 2 | 38908.5604 | 2265 | 2 | 1847 | 1919 | 140.9646 | 0.1221 | 138.2784 | 0.1221 | 1.4096 | 0.001221 | 1.3828 | 0.001221 | 1.4084 | 1.3816 | 5.5409 | 7.651 | 441.9972
38908.5611 | 2079 | 8 | 38908.5611 | 2041 | 8 | 1905.5 | 1977.5 | 126.9231 | 0.4884 | 124.6032 | 0.4884 | 1.2692 | 0.004884 | 1.246 | 0.004884 | 1.2643 | 1.2411 | 17.5497 | 19.8439 | 721.0638
38908.5617 | 1910 | 60 | 38908.5617 | 1908 | 65 | 1964.5 | 2036.5 | 116.6056 | 3.663 | 116.4835 | 3.9683 | 1.1661 | 0.03663 | 1.1648 | 0.039683 | 1.1294 | 1.1252 | 31.5782 | 32.2131 | 188.9792
38908.5624 | 2054 | 33 | 38908.5624 | 2337 | 40 | 2023.5 | 2095.5 | 125.3968 | 2.0147 | 142.674 | 2.442 | 1.254 | 0.020147 | 1.4267 | 0.02442 | 1.2338 | 1.4023 | 29.4251 | 4.5524 | 45.9669

## C3-5
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 150.0842 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38908.5386 | 1 | 0 | 38908.5386 | 1 | 0 | -37.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5392 | 1 | 0 | 38908.5393 | 1 | 0 | 21.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5399 | 1 | 0 | 38908.5399 | 1 | 0 | 80.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5406 | 1 | 0 | 38908.5406 | 1 | 0 | 139 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5413 | 1 | 0 | 38908.5413 | 1 | 0 | 198 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.542 | 1 | 0 | 38908.542 | 1 | 0 | 256.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5427 | 1 | 0 | 38908.5427 | 1 | 0 | 315.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5433 | 1 | 0 | 38908.5433 | 1 | 0 | 374.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.544 | 1 | 0 | 38908.544 | 1 | 0 | 433 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5447 | 1 | 0 | 38908.5447 | 1 | 0 | 492 | 564 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5454 | 1 | 0 | 38908.5454 | 1 | 0 | 550.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5461 | 1 | 0 | 38908.5461 | 1 | 0 | 609.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5467 | 1 | 0 | 38908.5467 | 1 | 0 | 668 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5474 | 1 | 0 | 38908.5474 | 2 | 0 | 727 | 799 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245738 | 122819 | 245737.9994
38908.5481 | 1 | 0 | 38908.5481 | 1 | 0 | 786 | 858 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5488 | 1 | 0 | 38908.5488 | 1 | 0 | 844.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5495 | 1 | 0 | 38908.5495 | 1 | 0 | 903.5 | 975.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5501 | 1 | 0 | 38908.5502 | 1 | 0 | 962 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5508 | 1 | 0 | 38908.5508 | 1 | 0 | 1021 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5515 | 1 | 0 | 38908.5515 | 1 | 0 | 1079.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5522 | 1 | 0 | 38908.5522 | 1 | 0 | 1138.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5529 | 1 | 0 | 38908.5529 | 1 | 0 | 1197.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5535 | 1 | 0 | 38908.5536 | 1 | 0 | 1256 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245738 | 245738 | 245737.9994
38908.5542 | 917 | 946 | 38908.5542 | 1135 | 1110 | 1315 | 1387 | 55.9829 | 57.7534 | 69.2918 | 67.7656 | 0.55983 | 0.57753 | 0.69292 | 0.67766 | 0.017705 | 0.015263 | 6720.3294 | 15600.4644 | 62.5357
38908.5549 | 1128 | 1084 | 38908.5549 | 1158 | 1118 | 1373.5 | 1445.5 | 68.8645 | 66.1783 | 70.696 | 68.254 | 0.68864 | 0.66178 | 0.70696 | 0.68254 | 0.026862 | 0.02442 | 3738.8902 | 12877.4991 | 22.5536
38908.5556 | 1044 | 863 | 38908.5556 | 967 | 842 | 1432.5 | 1504.5 | 63.7363 | 52.6862 | 59.0354 | 51.4042 | 0.63736 | 0.52686 | 0.59035 | 0.51404 | 0.1105 | 0.076313 | 853.1971 | 5667.9799 | 62.7834
38908.5563 | 1859 | 14 | 38908.5563 | 1978 | 13 | 1491.5 | 1563.5 | 113.4921 | 0.8547 | 120.757 | 0.79365 | 1.1349 | 0.008547 | 1.2076 | 0.0079365 | 1.1264 | 1.1996 | 33.5062 | 24.9392 | 834.6305
38908.5569 | 2323 | 7 | 38908.557 | 2243 | 6 | 1550 | 1622 | 141.8193 | 0.42735 | 136.9353 | 0.3663 | 1.4182 | 0.0042735 | 1.3694 | 0.003663 | 1.4139 | 1.3657 | 6.0262 | 10.0766 | 167.887
38908.5576 | 1945 | 52 | 38908.5576 | 2297 | 67 | 1609 | 1681 | 118.7424 | 3.1746 | 140.232 | 4.0904 | 1.1874 | 0.031746 | 1.4023 | 0.040904 | 1.1557 | 1.3614 | 41.8743 | 7.7961 | 64.17
38908.5583 | 1813 | 58 | 38908.5583 | 1944 | 69 | 1667.5 | 1739.5 | 110.6838 | 3.5409 | 118.6813 | 4.2125 | 1.1068 | 0.035409 | 1.1868 | 0.042125 | 1.0714 | 1.1447 | 41.3065 | 30.1167 | 234.4042
38908.559 | 1944 | 2 | 38908.559 | 2021 | 2 | 1726.5 | 1798.5 | 118.6813 | 0.1221 | 123.3822 | 0.1221 | 1.1868 | 0.001221 | 1.2338 | 0.001221 | 1.1856 | 1.2326 | 26.6132 | 21.7441 | 4575.6865
38908.5597 | 2193 | 1 | 38908.5597 | 2442 | 1 | 1785 | 1857 | 133.8828 | 0.06105 | 149.0842 | 0.06105 | 1.3388 | 0.0006105 | 1.4908 | 0.0006105 | 1.3382 | 1.4902 | 12.9869 | 0.67316 | 176.78
38908.5603 | 1998 | 1 | 38908.5604 | 2439 | 2 | 1844 | 1916 | 121.978 | 0.06105 | 148.9011 | 0.1221 | 1.2198 | 0.0006105 | 1.489 | 0.001221 | 1.2192 | 1.4878 | 24.5973 | 0.7979 | 363.6388
38908.561 | 2441 | 9 | 38908.561 | 2080 | 7 | 1903 | 1975 | 149.0232 | 0.54945 | 126.9841 | 0.42735 | 1.4902 | 0.0054945 | 1.2698 | 0.0042735 | 1.4847 | 1.2656 | 0.72244 | 34.2717 | 23.7658
38908.5617 | 2315 | 76 | 38908.5617 | 2329 | 75 | 1961.5 | 2033.5 | 141.3309 | 4.6398 | 142.1856 | 4.5788 | 1.4133 | 0.046398 | 1.4219 | 0.045788 | 1.3669 | 1.3761 | 10.8555 | 8.2771 | 6.7773
38908.5624 | 2336 | 35 | 38908.5624 | 1967 | 32 | 2020.5 | 2092.5 | 142.6129 | 2.1368 | 120.0855 | 1.9536 | 1.4261 | 0.021368 | 1.2009 | 0.019536 | 1.4048 | 1.1813 | 5.5521 | 36.1671 | 66.311

## C3-4
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.2442 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38908.5385 | 1 | 0 | 38908.5386 | 1 | 0 | -40 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5392 | 1 | 0 | 38908.5392 | 1 | 0 | 18.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5399 | 1 | 0 | 38908.5399 | 2 | 0 | 77.5 | 149.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 247638 | 123769 | 247637.9994
38908.5406 | 1 | 0 | 38908.5406 | 1 | 0 | 136.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5413 | 1 | 0 | 38908.5413 | 1 | 0 | 195 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5419 | 1 | 0 | 38908.542 | 1 | 0 | 254 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5426 | 1 | 0 | 38908.5426 | 1 | 0 | 312.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5433 | 1 | 0 | 38908.5433 | 1 | 0 | 371.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.544 | 1 | 0 | 38908.544 | 1 | 0 | 430.5 | 502.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5447 | 1 | 0 | 38908.5447 | 1 | 0 | 489 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5453 | 1 | 0 | 38908.5453 | 1 | 0 | 547.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.546 | 1 | 0 | 38908.546 | 1 | 0 | 606.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5467 | 1 | 0 | 38908.5467 | 1 | 0 | 665.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5474 | 1 | 0 | 38908.5474 | 1 | 0 | 724.5 | 796.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5481 | 1 | 0 | 38908.5481 | 1 | 0 | 783 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5487 | 1 | 0 | 38908.5488 | 1 | 0 | 842 | 914 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5494 | 1 | 0 | 38908.5494 | 1 | 0 | 900.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5501 | 1 | 0 | 38908.5501 | 1 | 0 | 959.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5508 | 1 | 0 | 38908.5508 | 1 | 0 | 1018 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5515 | 1 | 0 | 38908.5515 | 1 | 0 | 1077 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5521 | 1 | 0 | 38908.5522 | 1 | 0 | 1136 | 1208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5528 | 1 | 0 | 38908.5528 | 1 | 0 | 1194.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5535 | 1 | 0 | 38908.5535 | 1 | 0 | 1253.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247638 | 247638 | 247637.9994
38908.5542 | 899 | 720 | 38908.5542 | 972 | 941 | 1312 | 1384 | 54.884 | 43.956 | 59.3407 | 57.4481 | 0.54884 | 0.43956 | 0.59341 | 0.57448 | 0.10928 | 0.018926 | 687.2707 | 1421.2641 | 111.3826
38908.5549 | 284 | 253 | 38908.5549 | 999 | 954 | 1371 | 1443 | 17.3382 | 15.4457 | 60.989 | 58.2418 | 0.17338 | 0.15446 | 0.60989 | 0.58242 | 0.018926 | 0.027473 | 8713.3293 | 4341.6312 | 749.6813
38908.5555 | 1211 | 1020 | 38908.5556 | 1041 | 859 | 1429.5 | 1501.5 | 73.9316 | 62.2711 | 63.5531 | 52.442 | 0.73932 | 0.62271 | 0.63553 | 0.52442 | 0.11661 | 0.11111 | 1062.8317 | 1419.654 | 22.5654
38908.5562 | 2356 | 26 | 38908.5562 | 2288 | 21 | 1488.5 | 1560.5 | 143.8339 | 1.5873 | 139.6825 | 1.2821 | 1.4383 | 0.015873 | 1.3968 | 0.012821 | 1.4225 | 1.384 | 5.8698 | 9.9192 | 33.1044
38908.5569 | 2066 | 8 | 38908.5569 | 2333 | 9 | 1547.5 | 1619.5 | 126.1294 | 0.4884 | 142.4298 | 0.54945 | 1.2613 | 0.004884 | 1.4243 | 0.0054945 | 1.2564 | 1.4188 | 21.2977 | 6.3276 | 300.0674
38908.5576 | 2340 | 74 | 38908.5576 | 1792 | 65 | 1606 | 1678 | 142.8571 | 4.5177 | 109.4017 | 3.9683 | 1.4286 | 0.045177 | 1.094 | 0.039683 | 1.3834 | 1.0543 | 6.2688 | 99.3133 | 42.6768
38908.5583 | 1620 | 448 | 38908.5583 | 1682 | 239 | 1665 | 1737 | 98.9011 | 27.3504 | 102.6862 | 14.591 | 0.98901 | 0.2735 | 1.0269 | 0.14591 | 0.71551 | 0.88095 | 201.1998 | 60.0644 | 34.2903
38908.5589 | 2175 | 2 | 38908.559 | 2461 | 2 | 1723.5 | 1795.5 | 132.7839 | 0.1221 | 150.2442 | 0.1221 | 1.3278 | 0.001221 | 1.5024 | 0.001221 | 1.3266 | 1.5012 | 16.1332 | 0.6695 | 99.8834
38908.5596 | 1960 | 1 | 38908.5596 | 2295 | 2 | 1782.5 | 1854.5 | 119.6581 | 0.06105 | 140.1099 | 0.1221 | 1.1966 | 0.0006105 | 1.4011 | 0.001221 | 1.196 | 1.3999 | 26.5804 | 7.98 | 3816.1626
38908.5603 | 2401 | 2 | 38908.5603 | 2158 | 2 | 1841.5 | 1913.5 | 146.5812 | 0.1221 | 131.746 | 0.1221 | 1.4658 | 0.001221 | 1.3175 | 0.001221 | 1.4646 | 1.3162 | 3.2013 | 15.2556 | 492.2588
38908.561 | 2293 | 6 | 38908.561 | 2433 | 8 | 1900 | 1972 | 139.9878 | 0.3663 | 148.5348 | 0.4884 | 1.3999 | 0.003663 | 1.4853 | 0.004884 | 1.3962 | 1.4805 | 9.356 | 1.897 | 55.3476
38908.5617 | 2178 | 53 | 38908.5617 | 2136 | 77 | 1959 | 2031 | 132.967 | 3.2357 | 130.4029 | 4.7009 | 1.3297 | 0.032357 | 1.304 | 0.047009 | 1.2973 | 1.257 | 15.9209 | 21.67 | 82.7951
38908.5623 | 2113 | 30 | 38908.5624 | 2312 | 37 | 2017.5 | 2089.5 | 128.9988 | 1.8315 | 141.1477 | 2.2589 | 1.29 | 0.018315 | 1.4115 | 0.022589 | 1.2717 | 1.3889 | 21.4132 | 7.867 | 81.2901

## C2-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 152.6484 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38908.5385 | 1 | 0 | 38908.5385 | 1 | 0 | -43 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5392 | 1 | 0 | 38908.5392 | 1 | 0 | 16 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5399 | 1 | 0 | 38908.5399 | 1 | 0 | 74.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5405 | 1 | 0 | 38908.5406 | 1 | 0 | 133.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5412 | 1 | 0 | 38908.5412 | 1 | 0 | 192.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5419 | 1 | 0 | 38908.5419 | 1 | 0 | 251 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5426 | 1 | 0 | 38908.5426 | 2 | 0 | 310 | 382 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249938 | 124919 | 249937.9994
38908.5433 | 1 | 0 | 38908.5433 | 1 | 0 | 368.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5439 | 1 | 0 | 38908.544 | 1 | 0 | 427.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5446 | 1 | 0 | 38908.5446 | 1 | 0 | 486.5 | 558.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5453 | 1 | 0 | 38908.5453 | 1 | 0 | 545 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.546 | 1 | 0 | 38908.546 | 1 | 0 | 604 | 676 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5467 | 1 | 0 | 38908.5467 | 1 | 0 | 662.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5473 | 1 | 0 | 38908.5474 | 1 | 0 | 721.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.548 | 1 | 0 | 38908.548 | 1 | 0 | 780 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5487 | 1 | 0 | 38908.5487 | 1 | 0 | 839 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5494 | 1 | 0 | 38908.5494 | 1 | 0 | 897.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5501 | 1 | 0 | 38908.5501 | 1 | 0 | 956.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5508 | 1 | 0 | 38908.5508 | 1 | 0 | 1015.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5514 | 1 | 0 | 38908.5514 | 1 | 0 | 1074 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5521 | 1 | 0 | 38908.5521 | 1 | 0 | 1133 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5528 | 1 | 0 | 38908.5528 | 1 | 0 | 1192 | 1264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5535 | 1 | 0 | 38908.5535 | 1 | 0 | 1250.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249938 | 249938 | 249937.9994
38908.5542 | 7 | 6 | 38908.5542 | 85 | 89 | 1309.5 | 1381.5 | 0.42735 | 0.3663 | 5.1893 | 5.4335 | 0.0042735 | 0.003663 | 0.051893 | 0.054335 | 0.0006105 | 0.002442 | 251818.0375 | 60922.7983 | 41388.3975
38908.5548 | 118 | 98 | 38908.5548 | 114 | 95 | 1368 | 1440 | 7.2039 | 5.9829 | 6.9597 | 5.7998 | 0.072039 | 0.059829 | 0.069597 | 0.057998 | 0.01221 | 0.0116 | 12375.1875 | 13088.7241 | 2313.3258
38908.5555 | 1126 | 948 | 38908.5555 | 1257 | 1062 | 1427 | 1499 | 68.7424 | 57.8755 | 76.7399 | 64.8352 | 0.68742 | 0.57875 | 0.7674 | 0.64835 | 0.10867 | 0.11905 | 1925.587 | 889.094 | 40.4295
38908.5562 | 2023 | 69 | 38908.5562 | 2102 | 28 | 1485.5 | 1557.5 | 123.5043 | 4.2125 | 128.3272 | 1.7094 | 1.235 | 0.042125 | 1.2833 | 0.017094 | 1.1929 | 1.2662 | 29.6298 | 20.1253 | 99.1569
38908.5569 | 2231 | 10 | 38908.5569 | 2376 | 11 | 1544.5 | 1616.5 | 136.2027 | 0.6105 | 145.0549 | 0.67155 | 1.362 | 0.006105 | 1.4505 | 0.0067155 | 1.3559 | 1.4438 | 13.2208 | 5.451 | 134.0786
38908.5576 | 2001 | 59 | 38908.5576 | 2222 | 77 | 1603.5 | 1675.5 | 122.1612 | 3.602 | 135.6532 | 4.7009 | 1.2216 | 0.03602 | 1.3565 | 0.047009 | 1.1856 | 1.3095 | 32.4771 | 14.5908 | 95.0399
38908.5582 | 1819 | 409 | 38908.5583 | 2023 | 587 | 1662 | 1734 | 111.0501 | 24.9695 | 123.5043 | 35.8364 | 1.1105 | 0.24969 | 1.235 | 0.35836 | 0.86081 | 0.87668 | 99.315 | 56.4979 | 24.0423
38908.5589 | 1943 | 2 | 38908.5589 | 2383 | 2 | 1721 | 1793 | 118.6203 | 0.1221 | 145.4823 | 0.1221 | 1.1862 | 0.001221 | 1.4548 | 0.001221 | 1.185 | 1.4536 | 29.3273 | 4.944 | 1308.2264
38908.5596 | 2424 | 2 | 38908.5596 | 2484 | 2 | 1779.5 | 1851.5 | 147.9853 | 0.1221 | 151.6484 | 0.1221 | 1.4799 | 0.001221 | 1.5165 | 0.001221 | 1.4786 | 1.5153 | 3.5931 | 0.67509 | 24.9383
38908.5603 | 2246 | 3 | 38908.5603 | 2432 | 3 | 1838.5 | 1910.5 | 137.1184 | 0.18315 | 148.4737 | 0.18315 | 1.3712 | 0.0018315 | 1.4847 | 0.0018315 | 1.3694 | 1.4829 | 11.9006 | 2.8447 | 231.7715
38908.561 | 1945 | 5 | 38908.561 | 2050 | 6 | 1897.5 | 1969.5 | 118.7424 | 0.30525 | 125.1526 | 0.3663 | 1.1874 | 0.0030525 | 1.2515 | 0.003663 | 1.1844 | 1.2479 | 28.9632 | 22.2599 | 2004.1537
38908.5616 | 2261 | 55 | 38908.5617 | 2320 | 52 | 1956 | 2028 | 138.0342 | 3.3578 | 141.6361 | 3.1746 | 1.3803 | 0.033578 | 1.4164 | 0.031746 | 1.3468 | 1.3846 | 14.7594 | 9.416 | 28.8493
38908.5623 | 2354 | 33 | 38908.5623 | 2088 | 30 | 2015 | 2087 | 143.7118 | 2.0147 | 127.4725 | 1.8315 | 1.4371 | 0.020147 | 1.2747 | 0.018315 | 1.417 | 1.2564 | 6.6771 | 25.6343 | 70.1029

## C2-6
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 147.7033 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38908.5385 | 1 | 0 | 38908.5385 | 1 | 0 | -45.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5391 | 1 | 0 | 38908.5392 | 1 | 0 | 13 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5398 | 1 | 0 | 38908.5398 | 1 | 0 | 72 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5405 | 1 | 0 | 38908.5405 | 1 | 0 | 130.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5412 | 1 | 0 | 38908.5412 | 1 | 0 | 189.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5419 | 1 | 0 | 38908.5419 | 1 | 0 | 248.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5425 | 1 | 0 | 38908.5426 | 1 | 0 | 307 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5432 | 1 | 0 | 38908.5433 | 1 | 0 | 366 | 438 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5439 | 1 | 0 | 38908.5439 | 1 | 0 | 424.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5446 | 1 | 0 | 38908.5446 | 1 | 0 | 483.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5453 | 1 | 0 | 38908.5453 | 1 | 0 | 542.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5459 | 1 | 0 | 38908.546 | 1 | 0 | 601 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5466 | 1 | 0 | 38908.5467 | 1 | 0 | 660 | 732 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5473 | 1 | 0 | 38908.5473 | 1 | 0 | 718.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.548 | 1 | 0 | 38908.548 | 1 | 0 | 777.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5487 | 1 | 0 | 38908.5487 | 1 | 0 | 836 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5494 | 1 | 0 | 38908.5494 | 1 | 0 | 895 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.55 | 1 | 0 | 38908.55 | 1 | 0 | 953.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5507 | 1 | 0 | 38908.5507 | 1 | 0 | 1012.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5514 | 1 | 0 | 38908.5514 | 1 | 0 | 1071.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5521 | 1 | 0 | 38908.5521 | 1 | 0 | 1130 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5528 | 1 | 0 | 38908.5528 | 1 | 0 | 1189 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5534 | 1 | 0 | 38908.5534 | 1 | 0 | 1247.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241838 | 241838 | 241837.9994
38908.5541 | 2 | 3 | 38908.5541 | 13 | 12 | 1306.5 | 1378.5 | 0.1221 | 0.18315 | 0.79365 | 0.7326 | 0.001221 | 0.0018315 | 0.0079365 | 0.007326 | 0.0006105 | 0.0006105 | 242038.2496 | 241837.0022 | 80446.0688
38908.5548 | 122 | 103 | 38908.5548 | 98 | 80 | 1365.5 | 1437.5 | 7.4481 | 6.2882 | 5.9829 | 4.884 | 0.074481 | 0.062882 | 0.059829 | 0.04884 | 0.0116 | 0.010989 | 12602.5378 | 13367.9948 | 2114.6473
38908.5555 | 1245 | 1111 | 38908.5555 | 1088 | 919 | 1424 | 1496 | 76.0073 | 67.8266 | 66.4225 | 56.105 | 0.76007 | 0.67827 | 0.66422 | 0.56105 | 0.081807 | 0.10317 | 5800.0043 | 976.6854 | 5.1749
38908.5562 | 2212 | 152 | 38908.5562 | 2056 | 68 | 1483 | 1555 | 135.0427 | 9.2796 | 125.5189 | 4.1514 | 1.3504 | 0.092796 | 1.2552 | 0.041514 | 1.2576 | 1.2137 | 14.5662 | 23.8882 | 7.0253
38908.5568 | 2101 | 9 | 38908.5569 | 2105 | 9 | 1541.5 | 1613.5 | 128.2662 | 0.54945 | 128.5104 | 0.54945 | 1.2827 | 0.0054945 | 1.2851 | 0.0054945 | 1.2772 | 1.2796 | 15.6557 | 15.422 | 459.3064
38908.5575 | 1974 | 46 | 38908.5575 | 1979 | 51 | 1600.5 | 1672.5 | 120.5128 | 2.8083 | 120.8181 | 3.1136 | 1.2051 | 0.028083 | 1.2082 | 0.031136 | 1.177 | 1.177 | 25.4865 | 25.4865 | 176.3364
38908.5582 | 1597 | 443 | 38908.5582 | 1690 | 495 | 1659.5 | 1731.5 | 97.4969 | 27.0452 | 103.1746 | 30.2198 | 0.97497 | 0.27045 | 1.0317 | 0.3022 | 0.70452 | 0.72955 | 121.844 | 92.4738 | 41.1451
38908.5589 | 1940 | 2 | 38908.5589 | 1949 | 2 | 1718 | 1790 | 118.4371 | 0.1221 | 118.9866 | 0.1221 | 1.1844 | 0.001221 | 1.1899 | 0.001221 | 1.1832 | 1.1886 | 24.8415 | 24.2595 | 4660.0113
38908.5596 | 1924 | 1 | 38908.5596 | 2307 | 1 | 1777 | 1849 | 117.4603 | 0.06105 | 140.8425 | 0.06105 | 1.1746 | 0.0006105 | 1.4084 | 0.0006105 | 1.174 | 1.4078 | 26.0382 | 4.8815 | 2300.9947
38908.5602 | 2256 | 2 | 38908.5603 | 2140 | 1 | 1835.5 | 1907.5 | 137.7289 | 0.1221 | 130.6471 | 0.06105 | 1.3773 | 0.001221 | 1.3065 | 0.0006105 | 1.3761 | 1.3059 | 7.2977 | 13.1455 | 937.4719
38908.5609 | 2403 | 6 | 38908.5609 | 1917 | 5 | 1894.5 | 1966.5 | 146.7033 | 0.3663 | 117.033 | 0.30525 | 1.467 | 0.003663 | 1.1703 | 0.0030525 | 1.4634 | 1.1673 | 0.68741 | 42.408 | 51.5181
38908.5616 | 2066 | 36 | 38908.5616 | 2141 | 46 | 1953.5 | 2025.5 | 126.1294 | 2.1978 | 130.7082 | 2.8083 | 1.2613 | 0.021978 | 1.3071 | 0.028083 | 1.2393 | 1.279 | 19.7508 | 14.9498 | 114.658
38908.5623 | 2090 | 90 | 38908.5623 | 2218 | 28 | 2012 | 2084 | 127.5946 | 5.4945 | 135.409 | 1.7094 | 1.2759 | 0.054945 | 1.3541 | 0.017094 | 1.221 | 1.337 | 31.0272 | 9.5906 | 23.2766

## C2-5
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.3663 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38908.5384 | 1 | 0 | 38908.5384 | 1 | 0 | -48.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5391 | 1 | 0 | 38908.5391 | 1 | 0 | 10.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5398 | 1 | 0 | 38908.5398 | 1 | 0 | 69 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5405 | 1 | 0 | 38908.5405 | 1 | 0 | 128 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5412 | 1 | 0 | 38908.5412 | 1 | 0 | 186.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5418 | 1 | 0 | 38908.5419 | 1 | 0 | 245.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5425 | 1 | 0 | 38908.5425 | 1 | 0 | 304.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5432 | 1 | 0 | 38908.5432 | 1 | 0 | 363 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5439 | 1 | 0 | 38908.5439 | 1 | 0 | 422 | 494 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5446 | 1 | 0 | 38908.5446 | 2 | 0 | 480.5 | 552.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 247838 | 123869 | 247837.9994
38908.5452 | 1 | 0 | 38908.5453 | 1 | 0 | 539.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5459 | 1 | 0 | 38908.5459 | 1 | 0 | 598.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5466 | 1 | 0 | 38908.5466 | 1 | 0 | 657 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5473 | 1 | 0 | 38908.5473 | 1 | 0 | 716 | 788 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.548 | 1 | 0 | 38908.548 | 1 | 0 | 774.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5486 | 1 | 0 | 38908.5487 | 1 | 0 | 833.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5493 | 1 | 0 | 38908.5493 | 1 | 0 | 892.5 | 964.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.55 | 2 | 0 | 38908.55 | 1 | 0 | 951 | 1023 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123869 | 247838 | 123868.9988
38908.5507 | 2 | 0 | 38908.5507 | 1 | 0 | 1009.5 | 1081.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123869 | 247838 | 123868.9988
38908.5514 | 1 | 0 | 38908.5514 | 1 | 0 | 1068.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.552 | 1 | 0 | 38908.5521 | 1 | 0 | 1127.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5527 | 1 | 0 | 38908.5527 | 1 | 0 | 1186 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5534 | 1 | 0 | 38908.5534 | 1 | 0 | 1245 | 1317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38908.5541 | 3 | 5 | 38908.5541 | 3 | 5 | 1303.5 | 1375.5 | 0.18315 | 0.30525 | 0.18315 | 0.30525 | 0.0018315 | 0.0030525 | 0.0018315 | 0.0030525 | 0.001221 | 0.001221 | 124069 | 124069 | 49387.7933
38908.5548 | 253 | 222 | 38908.5548 | 372 | 414 | 1362.5 | 1434.5 | 15.4457 | 13.5531 | 22.7106 | 25.2747 | 0.15446 | 0.13553 | 0.22711 | 0.25275 | 0.018926 | 0.025641 | 8213.443 | 5701.8655 | 887.3121
38908.5555 | 1147 | 983 | 38908.5555 | 981 | 847 | 1421.5 | 1493.5 | 70.0244 | 60.0122 | 59.8901 | 51.7094 | 0.70024 | 0.60012 | 0.5989 | 0.51709 | 0.10012 | 0.081807 | 1020.7761 | 2936.6226 | 34.3718
38908.5561 | 1712 | 371 | 38908.5561 | 2051 | 253 | 1480 | 1552 | 104.5177 | 22.6496 | 125.2137 | 15.4457 | 1.0452 | 0.2265 | 1.2521 | 0.15446 | 0.81868 | 1.0977 | 253.6352 | 35.7264 | 28.1231
38908.5568 | 2392 | 6 | 38908.5568 | 1974 | 6 | 1539 | 1611 | 146.0317 | 0.3663 | 120.5128 | 0.3663 | 1.4603 | 0.003663 | 1.2051 | 0.003663 | 1.4567 | 1.2015 | 3.6954 | 27.989 | 296.6071
38908.5575 | 2383 | 68 | 38908.5575 | 2343 | 45 | 1597.5 | 1669.5 | 145.4823 | 4.1514 | 143.0403 | 2.7473 | 1.4548 | 0.041514 | 1.4304 | 0.027473 | 1.4133 | 1.4029 | 6.3242 | 8.5966 | 3.3038
38908.5582 | 1893 | 482 | 38908.5582 | 1829 | 479 | 1656.5 | 1728.5 | 115.5678 | 29.4261 | 111.6606 | 29.243 | 1.1557 | 0.29426 | 1.1166 | 0.29243 | 0.86142 | 0.82418 | 56.3669 | 130.0213 | 12.241
38908.5589 | 2463 | 3 | 38908.5589 | 2448 | 3 | 1715.5 | 1787.5 | 150.3663 | 0.18315 | 149.4505 | 0.18315 | 1.5037 | 0.0018315 | 1.4945 | 0.0018315 | 1.5018 | 1.4927 | 0.72288 | 1.5458 | 6.7894
38908.5595 | 2006 | 1 | 38908.5595 | 1914 | 1 | 1774 | 1846 | 122.4664 | 0.06105 | 116.8498 | 0.06105 | 1.2247 | 0.0006105 | 1.1685 | 0.0006105 | 1.2241 | 1.1679 | 23.6498 | 29.6201 | 10794.577
38908.5602 | 2036 | 2 | 38908.5602 | 2109 | 2 | 1833 | 1905 | 124.2979 | 0.1221 | 128.7546 | 0.1221 | 1.243 | 0.001221 | 1.2875 | 0.001221 | 1.2418 | 1.2863 | 21.9205 | 17.655 | 3311.6159
38908.5609 | 1913 | 4 | 38908.5609 | 2215 | 5 | 1891.5 | 1963.5 | 116.7888 | 0.2442 | 135.2259 | 0.30525 | 1.1679 | 0.002442 | 1.3523 | 0.0030525 | 1.1654 | 1.3492 | 30.1938 | 12.0532 | 1512.3362
38908.5616 | 1856 | 19 | 38908.5616 | 1957 | 26 | 1950.5 | 2022.5 | 113.3089 | 1.16 | 119.475 | 1.5873 | 1.1331 | 0.0116 | 1.1947 | 0.015873 | 1.1215 | 1.1789 | 35.2302 | 28.1273 | 698.3012
38908.5623 | 2164 | 90 | 38908.5623 | 1802 | 81 | 2009.5 | 2081.5 | 132.1123 | 5.4945 | 110.0122 | 4.9451 | 1.3211 | 0.054945 | 1.1001 | 0.049451 | 1.2662 | 1.0507 | 16.5074 | 55.0576 | 88.9195

## C2-4
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 149.84 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38908.5384 | 1 | 0 | 38908.5384 | 1 | 0 | -51.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5391 | 1 | 0 | 38908.5391 | 1 | 0 | 7.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5398 | 1 | 0 | 38908.5398 | 1 | 0 | 66.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5404 | 1 | 0 | 38908.5405 | 1 | 0 | 125 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5411 | 1 | 0 | 38908.5411 | 1 | 0 | 184 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5418 | 1 | 0 | 38908.5418 | 1 | 0 | 242.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5425 | 1 | 0 | 38908.5425 | 1 | 0 | 301.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5432 | 1 | 0 | 38908.5432 | 1 | 0 | 360.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5438 | 1 | 0 | 38908.5439 | 1 | 0 | 419 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5445 | 1 | 0 | 38908.5445 | 1 | 0 | 478 | 550 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5452 | 1 | 0 | 38908.5452 | 1 | 0 | 536.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5459 | 1 | 0 | 38908.5459 | 1 | 0 | 595.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5466 | 1 | 0 | 38908.5466 | 1 | 0 | 654 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5472 | 1 | 0 | 38908.5473 | 1 | 0 | 713 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5479 | 1 | 0 | 38908.548 | 1 | 0 | 772 | 844 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5486 | 1 | 0 | 38908.5486 | 1 | 0 | 830.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5493 | 1 | 0 | 38908.5493 | 1 | 0 | 889.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.55 | 1 | 0 | 38908.55 | 1 | 0 | 948.5 | 1020.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5506 | 1 | 0 | 38908.5507 | 1 | 0 | 1007 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5513 | 1 | 0 | 38908.5513 | 2 | 0 | 1065.5 | 1137.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 245338 | 122619 | 245337.9994
38908.552 | 1 | 0 | 38908.552 | 1 | 0 | 1124.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5527 | 2 | 0 | 38908.5527 | 1 | 0 | 1183.5 | 1255.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122619 | 245338 | 122618.9988
38908.5534 | 1 | 0 | 38908.5534 | 1 | 0 | 1242 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
38908.5541 | 3 | 5 | 38908.5541 | 2 | 5 | 1301 | 1373 | 0.18315 | 0.30525 | 0.1221 | 0.30525 | 0.0018315 | 0.0030525 | 0.001221 | 0.0030525 | 0.001221 | 0.0018315 | 122944.4857 | 81856.9674 | 48867.9009
38908.5547 | 235 | 215 | 38908.5547 | 304 | 294 | 1359.5 | 1431.5 | 14.3468 | 13.1258 | 18.5592 | 17.9487 | 0.14347 | 0.13126 | 0.18559 | 0.17949 | 0.01221 | 0.006105 | 11526.1307 | 28866.9738 | 929.0514
38908.5554 | 1012 | 866 | 38908.5554 | 1079 | 994 | 1418.5 | 1490.5 | 61.7827 | 52.8694 | 65.873 | 60.6838 | 0.61783 | 0.52869 | 0.65873 | 0.60684 | 0.089133 | 0.051893 | 882.9061 | 4986.3758 | 65.2481
38908.5561 | 1831 | 541 | 38908.5561 | 1548 | 418 | 1477.5 | 1549.5 | 111.7827 | 33.0281 | 94.5055 | 25.5189 | 1.1178 | 0.33028 | 0.94505 | 0.25519 | 0.78755 | 0.68987 | 60.7423 | 205.1346 | 10.237
38908.5568 | 2013 | 9 | 38908.5568 | 2392 | 8 | 1536 | 1608 | 122.8938 | 0.54945 | 146.0317 | 0.4884 | 1.2289 | 0.0054945 | 1.4603 | 0.004884 | 1.2234 | 1.4554 | 26.5189 | 2.6501 | 124.0319
38908.5575 | 2291 | 41 | 38908.5575 | 2226 | 56 | 1595 | 1667 | 139.8657 | 2.5031 | 135.8974 | 3.4188 | 1.3987 | 0.025031 | 1.359 | 0.034188 | 1.3736 | 1.3248 | 8.2415 | 15.3223 | 39.6586
38908.5581 | 1971 | 351 | 38908.5581 | 1905 | 444 | 1653.5 | 1725.5 | 120.3297 | 21.4286 | 116.3004 | 27.1062 | 1.2033 | 0.21429 | 1.163 | 0.27106 | 0.98901 | 0.89194 | 29.088 | 839.9695 | 33.7027
38908.5588 | 1902 | 3 | 38908.5588 | 1996 | 2 | 1712.5 | 1784.5 | 116.1172 | 0.18315 | 121.8559 | 0.1221 | 1.1612 | 0.0018315 | 1.2186 | 0.001221 | 1.1593 | 1.2173 | 29.2885 | 23.067 | 3432.4203
38908.5595 | 2094 | 1 | 38908.5595 | 2316 | 2 | 1771.5 | 1843.5 | 127.8388 | 0.06105 | 141.3919 | 0.1221 | 1.2784 | 0.0006105 | 1.4139 | 0.001221 | 1.2778 | 1.4127 | 17.3563 | 6.01 | 2037.4405
38908.5602 | 2438 | 2 | 38908.5602 | 2140 | 2 | 1830 | 1902 | 148.84 | 0.1221 | 130.6471 | 0.1221 | 1.4884 | 0.001221 | 1.3065 | 0.001221 | 1.4872 | 1.3053 | 0.67566 | 17.0674 | 104.8237
38908.5609 | 2154 | 5 | 38908.5609 | 2186 | 6 | 1889 | 1961 | 131.5018 | 0.30525 | 133.4554 | 0.3663 | 1.315 | 0.0030525 | 1.3346 | 0.003663 | 1.312 | 1.3309 | 14.2416 | 12.5536 | 658.9015
38908.5615 | 2211 | 27 | 38908.5616 | 2356 | 27 | 1947.5 | 2019.5 | 134.9817 | 1.6484 | 143.8339 | 1.6484 | 1.3498 | 0.016484 | 1.4383 | 0.016484 | 1.3333 | 1.4219 | 15.275 | 4.5711 | 35.0314
38908.5622 | 2179 | 76 | 38908.5622 | 2049 | 81 | 2006.5 | 2078.5 | 133.0281 | 4.6398 | 125.0916 | 4.9451 | 1.3303 | 0.046398 | 1.2509 | 0.049451 | 1.2839 | 1.2015 | 15.0051 | 28.3843 | 58.0009

## C2-3
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.8547 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38908.5384 | 1 | 0 | 38908.5384 | 1 | 0 | -54 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5391 | 1 | 0 | 38908.5391 | 1 | 0 | 4.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5397 | 1 | 0 | 38908.5397 | 1 | 0 | 63.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5404 | 1 | 0 | 38908.5404 | 1 | 0 | 122.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5411 | 1 | 0 | 38908.5411 | 1 | 0 | 181 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5418 | 1 | 0 | 38908.5418 | 1 | 0 | 240 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5425 | 1 | 0 | 38908.5425 | 1 | 0 | 298.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5431 | 1 | 0 | 38908.5431 | 1 | 0 | 357.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5438 | 1 | 0 | 38908.5438 | 1 | 0 | 416.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5445 | 1 | 0 | 38908.5445 | 1 | 0 | 475 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5452 | 1 | 0 | 38908.5452 | 1 | 0 | 534 | 606 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5459 | 1 | 0 | 38908.5459 | 1 | 0 | 592.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5465 | 1 | 0 | 38908.5466 | 1 | 0 | 651.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5472 | 1 | 0 | 38908.5472 | 1 | 0 | 710.5 | 782.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5479 | 1 | 0 | 38908.5479 | 1 | 0 | 769 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5486 | 1 | 0 | 38908.5486 | 1 | 0 | 828 | 900 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5493 | 1 | 0 | 38908.5493 | 1 | 0 | 886.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5499 | 1 | 0 | 38908.55 | 1 | 0 | 945.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5506 | 1 | 0 | 38908.5506 | 1 | 0 | 1004 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5513 | 1 | 0 | 38908.5513 | 1 | 0 | 1063 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.552 | 1 | 0 | 38908.552 | 1 | 0 | 1121.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5527 | 1 | 0 | 38908.5527 | 1 | 0 | 1180.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5533 | 2 | 1 | 38908.5534 | 1 | 0 | 1239.5 | 1311.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248338.1206
38908.554 | 5 | 7 | 38908.554 | 3 | 6 | 1298 | 1370 | 0.30525 | 0.42735 | 0.18315 | 0.3663 | 0.0030525 | 0.0042735 | 0.0018315 | 0.003663 | 0.001221 | 0.0018315 | 124644.955 | 82945.7579 | 35319.9894
38908.5547 | 1056 | 1135 | 38908.5547 | 1052 | 1012 | 1357 | 1429 | 64.4689 | 69.2918 | 64.2247 | 61.7827 | 0.64469 | 0.69292 | 0.64225 | 0.61783 | 0.04823 | 0.02442 | 1332.3832 | 3992.254 | 25.4747
38908.5554 | 379 | 238 | 38908.5554 | 256 | 199 | 1415.5 | 1487.5 | 23.138 | 14.5299 | 15.6288 | 12.149 | 0.23138 | 0.1453 | 0.15629 | 0.12149 | 0.086081 | 0.034799 | 1546.9531 | 5055.6912 | 770.6311
38908.5561 | 1614 | 619 | 38908.5561 | 1507 | 349 | 1474.5 | 1546.5 | 98.5348 | 37.79 | 92.0024 | 21.3065 | 0.98535 | 0.3779 | 0.92002 | 0.21306 | 0.60745 | 0.70696 | 247.4961 | 96.4004 | 20.1711
38908.5567 | 2172 | 10 | 38908.5568 | 2054 | 9 | 1533.5 | 1605.5 | 132.6007 | 0.6105 | 125.3968 | 0.54945 | 1.326 | 0.006105 | 1.254 | 0.0054945 | 1.3199 | 1.2485 | 14.9031 | 21.837 | 547.3372
38908.5574 | 2235 | 40 | 38908.5574 | 2294 | 38 | 1592 | 1664 | 136.4469 | 2.442 | 140.0488 | 2.3199 | 1.3645 | 0.02442 | 1.4005 | 0.023199 | 1.34 | 1.3773 | 14.1476 | 9.7303 | 47.0818
| 2344 | 22 | 38908.5581 | 1897 | 378 | 1652 | 1724 | 143.1013 | 1.3431 | 115.812 | 23.0769 | 1.431 | 0.013431 | 1.1581 | 0.23077 | 1.4176 | 0.92735 | 5.7074 | 11.5669 | 57.2015
38908.5588 | 2453 | 3 | 38908.5588 | 2060 | 2 | 1709.5 | 1781.5 | 149.7558 | 0.18315 | 125.7631 | 0.1221 | 1.4976 | 0.0018315 | 1.2576 | 0.001221 | 1.4957 | 1.2564 | 1.411 | 22.3028 | 190.746
38908.5595 | 1940 | 1 | 38908.5595 | 2471 | 2 | 1768.5 | 1840.5 | 118.4371 | 0.06105 | 150.8547 | 0.1221 | 1.1844 | 0.0006105 | 1.5085 | 0.001221 | 1.1838 | 1.5073 | 30.6027 | 0.66519 | 361.0434
38908.5602 | 2073 | 1 | 38908.5602 | 2057 | 1 | 1827.5 | 1899.5 | 126.5568 | 0.06105 | 125.58 | 0.06105 | 1.2656 | 0.0006105 | 1.2558 | 0.0006105 | 1.265 | 1.2552 | 20.0451 | 20.9838 | 7169.7877
38908.5608 | 1950 | 2 | 38908.5608 | 2038 | 4 | 1886 | 1958 | 119.0476 | 0.1221 | 124.42 | 0.2442 | 1.1905 | 0.001221 | 1.2442 | 0.002442 | 1.1893 | 1.2418 | 27.7141 | 22.2513 | 4872.3013
38908.5615 | 1826 | 25 | 38908.5615 | 1910 | 22 | 1945 | 2017 | 111.4774 | 1.5263 | 116.6056 | 1.3431 | 1.1148 | 0.015263 | 1.1661 | 0.013431 | 1.0995 | 1.1526 | 38.4137 | 31.5383 | 610.3264
38908.5622 | 1917 | 66 | 38908.5622 | 1837 | 53 | 2003.5 | 2075.5 | 117.033 | 4.0293 | 112.149 | 3.2357 | 1.1703 | 0.040293 | 1.1215 | 0.032357 | 1.13 | 1.0891 | 33.8332 | 39.9656 | 218.2122

## C1-7
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 152.0379 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38908.5383 | 1 | 0 | 38908.5384 | 1 | 0 | -57 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.539 | 1 | 0 | 38908.539 | 1 | 0 | 2 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5397 | 1 | 0 | 38908.5397 | 1 | 0 | 60.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5404 | 1 | 0 | 38908.5404 | 1 | 0 | 119.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5411 | 1 | 0 | 38908.5411 | 1 | 0 | 178.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5417 | 1 | 0 | 38908.5418 | 1 | 0 | 237 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5424 | 1 | 0 | 38908.5424 | 1 | 0 | 296 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5431 | 1 | 0 | 38908.5431 | 1 | 0 | 354.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5438 | 1 | 0 | 38908.5438 | 1 | 0 | 413.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5445 | 1 | 0 | 38908.5445 | 1 | 0 | 472.5 | 544.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5451 | 1 | 0 | 38908.5452 | 1 | 0 | 531 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5458 | 1 | 0 | 38908.5458 | 1 | 0 | 590 | 662 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5465 | 1 | 0 | 38908.5465 | 1 | 0 | 648.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5472 | 1 | 0 | 38908.5472 | 1 | 0 | 707.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5479 | 1 | 0 | 38908.5479 | 1 | 0 | 766.5 | 838.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5485 | 1 | 0 | 38908.5486 | 1 | 0 | 825 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5492 | 1 | 0 | 38908.5492 | 1 | 0 | 883.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5499 | 1 | 0 | 38908.5499 | 1 | 0 | 942.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5506 | 1 | 0 | 38908.5506 | 1 | 0 | 1001.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5513 | 1 | 0 | 38908.5513 | 1 | 0 | 1060 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5519 | 1 | 0 | 38908.552 | 1 | 0 | 1119 | 1191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5526 | 1 | 0 | 38908.5526 | 1 | 0 | 1177.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38908.5533 | 1 | 0 | 38908.5533 | 2 | 0 | 1236.5 | 1308.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248938 | 124419 | 248937.9994
38908.554 | 121 | 114 | 38908.554 | 307 | 295 | 1295.5 | 1367.5 | 7.3871 | 6.9597 | 18.7424 | 18.0098 | 0.073871 | 0.069597 | 0.18742 | 0.1801 | 0.0042735 | 0.007326 | 36934.1225 | 19492.2356 | 1968.3056
38908.5547 | 29 | 21 | 38908.5547 | 47 | 37 | 1354 | 1426 | 1.7705 | 1.2821 | 2.8694 | 2.2589 | 0.017705 | 0.012821 | 0.028694 | 0.022589 | 0.004884 | 0.006105 | 31097.3637 | 24728.0168 | 11574.0517
38908.5553 | 1078 | 950 | 38908.5554 | 1151 | 1090 | 1413 | 1485 | 65.812 | 57.9976 | 70.2686 | 66.5446 | 0.65812 | 0.57998 | 0.70269 | 0.66545 | 0.078144 | 0.037241 | 754.4354 | 1604.4531 | 45.816
38908.556 | 1822 | 330 | 38908.556 | 1632 | 480 | 1471.5 | 1543.5 | 111.2332 | 20.1465 | 99.6337 | 29.304 | 1.1123 | 0.20147 | 0.99634 | 0.29304 | 0.91087 | 0.7033 | 46.1193 | 771.7803 | 90.7773
38908.5567 | 2139 | 11 | 38908.5567 | 2405 | 9 | 1530.5 | 1602.5 | 130.5861 | 0.67155 | 146.8254 | 0.54945 | 1.3059 | 0.0067155 | 1.4683 | 0.0054945 | 1.2991 | 1.4628 | 19.2502 | 3.6344 | 108.5163
38908.5574 | 2339 | 42 | 38908.5574 | 2315 | 42 | 1589.5 | 1661.5 | 142.7961 | 2.5641 | 141.3309 | 2.5641 | 1.428 | 0.025641 | 1.4133 | 0.025641 | 1.4023 | 1.3877 | 8.0633 | 10.0096 | 23.696
38908.5581 | 1664 | 565 | 38908.5581 | 2052 | 114 | 1648 | 1720 | 101.5873 | 34.4933 | 125.2747 | 6.9597 | 1.0159 | 0.34493 | 1.2527 | 0.069597 | 0.67094 | 1.1832 | 48.5752 | 93.8167 | 22.393
38908.5587 | 2219 | 3 | 38908.5588 | 1953 | 3 | 1707 | 1779 | 135.4701 | 0.18315 | 119.2308 | 0.18315 | 1.3547 | 0.0018315 | 1.1923 | 0.0018315 | 1.3529 | 1.1905 | 12.3061 | 27.9068 | 1951.8465
38908.5594 | 2242 | 2 | 38908.5594 | 2060 | 1 | 1765.5 | 1837.5 | 136.8742 | 0.1221 | 125.7631 | 0.06105 | 1.3687 | 0.001221 | 1.2576 | 0.0006105 | 1.3675 | 1.257 | 11.1358 | 20.9939 | 2137.4985
38908.5601 | 2474 | 2 | 38908.5601 | 1950 | 1 | 1824.5 | 1896.5 | 151.0379 | 0.1221 | 119.0476 | 0.06105 | 1.5104 | 0.001221 | 1.1905 | 0.0006105 | 1.5092 | 1.1899 | 0.66441 | 30.0463 | 166.12
38908.5608 | 2407 | 3 | 38908.5608 | 2247 | 4 | 1883.5 | 1955.5 | 146.9475 | 0.18315 | 137.1795 | 0.2442 | 1.4695 | 0.0018315 | 1.3718 | 0.002442 | 1.4676 | 1.3694 | 3.5067 | 11.432 | 274.878
38908.5615 | 2378 | 26 | 38908.5615 | 1925 | 20 | 1942 | 2014 | 145.177 | 1.5873 | 117.5214 | 1.221 | 1.4518 | 0.015873 | 1.1752 | 0.01221 | 1.4359 | 1.163 | 4.9223 | 37.7251 | 91.0032
38908.5622 | 2070 | 97 | 38908.5622 | 1978 | 109 | 2000.5 | 2072.5 | 126.3736 | 5.9219 | 120.757 | 6.6545 | 1.2637 | 0.059219 | 1.2076 | 0.066545 | 1.2045 | 1.141 | 24.6882 | 35.8937 | 88.0563

## C1-6
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 148.3138 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38908.5383 | 1 | 0 | 38908.5383 | 1 | 0 | -59.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.539 | 1 | 0 | 38908.539 | 1 | 0 | -1 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5397 | 1 | 0 | 38908.5397 | 1 | 0 | 58 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5403 | 1 | 0 | 38908.5404 | 1 | 0 | 116.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.541 | 1 | 0 | 38908.541 | 1 | 0 | 175.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5417 | 1 | 0 | 38908.5417 | 1 | 0 | 234.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5424 | 1 | 0 | 38908.5424 | 1 | 0 | 293 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5431 | 1 | 0 | 38908.5431 | 1 | 0 | 352 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5437 | 1 | 0 | 38908.5438 | 1 | 0 | 410.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5444 | 1 | 0 | 38908.5444 | 1 | 0 | 469.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5451 | 1 | 0 | 38908.5451 | 1 | 0 | 528.5 | 600.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5458 | 1 | 0 | 38908.5458 | 1 | 0 | 587 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5465 | 1 | 0 | 38908.5465 | 1 | 0 | 646 | 718 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5472 | 1 | 0 | 38908.5472 | 1 | 0 | 704.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5478 | 1 | 0 | 38908.5478 | 1 | 0 | 763.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5485 | 1 | 0 | 38908.5485 | 1 | 0 | 822 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5492 | 1 | 0 | 38908.5492 | 1 | 0 | 881 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5499 | 1 | 0 | 38908.5499 | 1 | 0 | 939.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5506 | 1 | 0 | 38908.5506 | 1 | 0 | 998.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5512 | 1 | 0 | 38908.5512 | 1 | 0 | 1057.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5519 | 1 | 0 | 38908.5519 | 1 | 0 | 1116 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5526 | 1 | 0 | 38908.5526 | 1 | 0 | 1175 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.5533 | 1 | 0 | 38908.5533 | 1 | 0 | 1233.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242838 | 242838 | 242837.9994
38908.554 | 943 | 976 | 38908.554 | 1139 | 1113 | 1292.5 | 1364.5 | 57.5702 | 59.5849 | 69.536 | 67.9487 | 0.5757 | 0.59585 | 0.69536 | 0.67949 | 0.020147 | 0.015873 | 4833.668 | 43388.5806 | 52.1728
38908.5546 | 44 | 38 | 38908.5547 | 33 | 25 | 1351.5 | 1423.5 | 2.6862 | 2.3199 | 2.0147 | 1.5263 | 0.026862 | 0.023199 | 0.020147 | 0.015263 | 0.003663 | 0.004884 | 40608.3077 | 30187.0536 | 6156.9199
38908.5553 | 1072 | 957 | 38908.5553 | 1012 | 961 | 1410 | 1482 | 65.4457 | 58.4249 | 61.7827 | 58.6691 | 0.65446 | 0.58425 | 0.61783 | 0.58669 | 0.070208 | 0.031136 | 879.4389 | 2432.2592 | 40.1848
38908.556 | 1774 | 215 | 38908.556 | 1891 | 285 | 1469 | 1541 | 108.3028 | 13.1258 | 115.4457 | 17.3993 | 1.083 | 0.13126 | 1.1545 | 0.17399 | 0.95177 | 0.98046 | 59.0167 | 47.9376 | 66.3723
38908.5567 | 2413 | 10 | 38908.5567 | 1990 | 10 | 1527.5 | 1599.5 | 147.3138 | 0.6105 | 121.4896 | 0.6105 | 1.4731 | 0.006105 | 1.2149 | 0.006105 | 1.467 | 1.2088 | 0.68502 | 84.4645 | 29.2134
38908.5574 | 2151 | 43 | 38908.5574 | 2203 | 43 | 1586.5 | 1658.5 | 131.3187 | 2.6252 | 134.4933 | 2.6252 | 1.3132 | 0.026252 | 1.3449 | 0.026252 | 1.2869 | 1.3187 | 15.9162 | 11.9788 | 58.5571
38908.558 | 1359 | 963 | 38908.5581 | 1175 | 708 | 1645.5 | 1717.5 | 82.967 | 58.7912 | 71.7338 | 43.2234 | 0.82967 | 0.58791 | 0.71734 | 0.43223 | 0.24176 | 0.2851 | 1405.6804 | 301.0756 | 8.3704
38908.5587 | 2344 | 5 | 38908.5587 | 2207 | 4 | 1704 | 1776 | 143.1013 | 0.30525 | 134.7375 | 0.2442 | 1.431 | 0.0030525 | 1.3474 | 0.002442 | 1.428 | 1.3449 | 3.7253 | 10.6116 | 154.2265
38908.5594 | 2160 | 1 | 38908.5594 | 2329 | 2 | 1763 | 1835 | 131.8681 | 0.06105 | 142.1856 | 0.1221 | 1.3187 | 0.0006105 | 1.4219 | 0.001221 | 1.3181 | 1.4206 | 12.6116 | 4.3433 | 1117.1364
38908.5601 | 2142 | 1 | 38908.5601 | 2054 | 2 | 1821.5 | 1893.5 | 130.7692 | 0.06105 | 125.3968 | 0.1221 | 1.3077 | 0.0006105 | 1.254 | 0.001221 | 1.3071 | 1.2527 | 13.4568 | 18.4268 | 4455.9809
38908.5608 | 2024 | 4 | 38908.5608 | 2101 | 4 | 1880.5 | 1952.5 | 123.5653 | 0.2442 | 128.2662 | 0.2442 | 1.2357 | 0.002442 | 1.2827 | 0.002442 | 1.2332 | 1.2802 | 20.3229 | 15.8079 | 1369.7187
38908.5614 | 2007 | 19 | 38908.5615 | 2305 | 25 | 1939.5 | 2011.5 | 122.5275 | 1.16 | 140.7204 | 1.5263 | 1.2253 | 0.0116 | 1.4072 | 0.015263 | 1.2137 | 1.3919 | 25.5265 | 5.7001 | 114.4903
38908.5621 | 1901 | 71 | 38908.5621 | 2150 | 89 | 1998 | 2070 | 116.0562 | 4.3346 | 131.2576 | 5.4335 | 1.1606 | 0.043346 | 1.3126 | 0.054335 | 1.1172 | 1.2582 | 38.7192 | 15.2572 | 85.2756

## C1-5
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.7326 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38908.5383 | 1 | 0 | 38908.5383 | 1 | 0 | -62.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.539 | 1 | 0 | 38908.539 | 1 | 0 | -3.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5396 | 1 | 0 | 38908.5397 | 1 | 0 | 55 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5403 | 1 | 0 | 38908.5403 | 1 | 0 | 114 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.541 | 1 | 0 | 38908.541 | 1 | 0 | 172.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5417 | 1 | 0 | 38908.5417 | 1 | 0 | 231.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5424 | 1 | 0 | 38908.5424 | 1 | 0 | 290.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.543 | 1 | 0 | 38908.5431 | 1 | 0 | 349 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5437 | 1 | 0 | 38908.5437 | 1 | 0 | 408 | 480 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5444 | 1 | 0 | 38908.5444 | 1 | 0 | 466.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5451 | 1 | 0 | 38908.5451 | 1 | 0 | 525.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5458 | 1 | 0 | 38908.5458 | 1 | 0 | 584.5 | 656.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5464 | 1 | 0 | 38908.5465 | 1 | 0 | 643 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5471 | 1 | 0 | 38908.5471 | 1 | 0 | 702 | 774 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5478 | 1 | 0 | 38908.5478 | 1 | 0 | 760.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5485 | 1 | 0 | 38908.5485 | 1 | 0 | 819.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5492 | 1 | 0 | 38908.5492 | 1 | 0 | 878 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5498 | 1 | 0 | 38908.5499 | 1 | 0 | 937 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5505 | 1 | 0 | 38908.5505 | 1 | 0 | 995.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5512 | 1 | 0 | 38908.5512 | 1 | 0 | 1054.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5519 | 1 | 0 | 38908.5519 | 1 | 0 | 1113.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5526 | 1 | 0 | 38908.5526 | 1 | 0 | 1172 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38908.5532 | 1 | 0 | 38908.5533 | 2 | 0 | 1231 | 1303 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248438 | 124169 | 248437.9994
38908.5539 | 967 | 1004 | 38908.5539 | 1188 | 1191 | 1289.5 | 1361.5 | 59.0354 | 61.2943 | 72.5275 | 72.7106 | 0.59035 | 0.61294 | 0.72527 | 0.72711 | 0.022589 | 0.0018315 | 1720.6793 | 1959.2898 | 48.7452
38908.5546 | 248 | 228 | 38908.5546 | 260 | 253 | 1348.5 | 1420.5 | 15.1404 | 13.9194 | 15.873 | 15.4457 | 0.1514 | 0.13919 | 0.15873 | 0.15446 | 0.01221 | 0.0042735 | 11468.5463 | 46420.4351 | 879.4126
38908.5553 | 1233 | 878 | 38908.5553 | 1025 | 916 | 1407.5 | 1479.5 | 75.2747 | 53.602 | 62.5763 | 55.9219 | 0.75275 | 0.53602 | 0.62576 | 0.55922 | 0.21673 | 0.066545 | 242.3996 | 543.1174 | 36.0099
38908.556 | 1993 | 245 | 38908.556 | 1717 | 202 | 1466 | 1538 | 121.6728 | 14.9573 | 104.823 | 12.3321 | 1.2167 | 0.14957 | 1.0482 | 0.12332 | 1.0672 | 0.92491 | 33.8334 | 83.7054 | 46.0077
38908.5566 | 2217 | 8 | 38908.5567 | 2364 | 8 | 1525 | 1597 | 135.348 | 0.4884 | 144.3223 | 0.4884 | 1.3535 | 0.004884 | 1.4432 | 0.004884 | 1.3486 | 1.4383 | 13.0423 | 5.2897 | 163.5161
38908.5573 | 1878 | 24 | 38908.5573 | 1841 | 25 | 1583.5 | 1655.5 | 114.652 | 1.4652 | 112.3932 | 1.5263 | 1.1465 | 0.014652 | 1.1239 | 0.015263 | 1.1319 | 1.1087 | 33.9488 | 36.9832 | 656.262
38908.558 | 1306 | 731 | 38908.558 | 1362 | 945 | 1642.5 | 1714.5 | 79.7314 | 44.6276 | 83.1502 | 57.6923 | 0.79731 | 0.44628 | 0.8315 | 0.57692 | 0.35104 | 0.25458 | 185.8887 | 1229.5004 | 56.7243
38908.5587 | 2237 | 5 | 38908.5587 | 2188 | 5 | 1701.5 | 1773.5 | 136.569 | 0.30525 | 133.5775 | 0.30525 | 1.3657 | 0.0030525 | 1.3358 | 0.0030525 | 1.3626 | 1.3327 | 11.3104 | 13.9041 | 594.1807
38908.5594 | 2116 | 1 | 38908.5594 | 1987 | 1 | 1760 | 1832 | 129.1819 | 0.06105 | 121.3065 | 0.06105 | 1.2918 | 0.0006105 | 1.2131 | 0.0006105 | 1.2912 | 1.2125 | 17.4976 | 25.1671 | 7406.94
38908.56 | 2469 | 2 | 38908.5601 | 2205 | 1 | 1819 | 1891 | 150.7326 | 0.1221 | 134.6154 | 0.06105 | 1.5073 | 0.001221 | 1.3462 | 0.0006105 | 1.5061 | 1.3455 | 0.66793 | 13.6486 | 86.3478
38908.5607 | 2433 | 5 | 38908.5607 | 2441 | 6 | 1877.5 | 1949.5 | 148.5348 | 0.30525 | 149.0232 | 0.3663 | 1.4853 | 0.0030525 | 1.4902 | 0.003663 | 1.4823 | 1.4866 | 2.4007 | 2.031 | 18.8631
38908.5614 | 2261 | 20 | 38908.5614 | 2019 | 19 | 1936.5 | 2008.5 | 138.0342 | 1.221 | 123.2601 | 1.16 | 1.3803 | 0.01221 | 1.2326 | 0.0116 | 1.3681 | 1.221 | 10.3731 | 25.6699 | 208.738
38908.5621 | 1823 | 57 | 38908.5621 | 1858 | 73 | 1995.5 | 2067.5 | 111.2943 | 3.4799 | 113.431 | 4.4567 | 1.1129 | 0.034799 | 1.1343 | 0.044567 | 1.0781 | 1.0897 | 40.8865 | 39.0536 | 298.2857

## C1-4
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.8547 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38908.5382 | 1 | 0 | 38908.5383 | 1 | 0 | -65.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5389 | 1 | 0 | 38908.5389 | 1 | 0 | -6.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5396 | 1 | 0 | 38908.5396 | 1 | 0 | 52.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5403 | 1 | 0 | 38908.5403 | 1 | 0 | 111 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.541 | 1 | 0 | 38908.541 | 1 | 0 | 170 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5416 | 1 | 0 | 38908.5417 | 1 | 0 | 228.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5423 | 1 | 0 | 38908.5423 | 1 | 0 | 287.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.543 | 1 | 0 | 38908.543 | 1 | 0 | 346.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5437 | 1 | 0 | 38908.5437 | 1 | 0 | 405 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5444 | 1 | 0 | 38908.5444 | 1 | 0 | 464 | 536 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.545 | 1 | 0 | 38908.5451 | 1 | 0 | 522.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5457 | 1 | 0 | 38908.5457 | 1 | 0 | 581.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5464 | 1 | 0 | 38908.5464 | 1 | 0 | 640.5 | 712.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5471 | 1 | 0 | 38908.5471 | 1 | 0 | 699 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5478 | 1 | 0 | 38908.5478 | 1 | 0 | 757.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5484 | 1 | 0 | 38908.5485 | 1 | 0 | 816.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5491 | 1 | 0 | 38908.5491 | 1 | 0 | 875.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5498 | 1 | 0 | 38908.5498 | 1 | 0 | 934.5 | 1006.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5505 | 1 | 0 | 38908.5505 | 1 | 0 | 993 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5512 | 1 | 0 | 38908.5512 | 1 | 0 | 1052 | 1124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5519 | 1 | 0 | 38908.5519 | 1 | 0 | 1110.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5525 | 1 | 0 |  | 1 | 0 | 1169 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5532 | 1 | 0 | 38908.5532 | 1 | 0 | 1228 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
38908.5539 | 17 | 18 | 38908.5539 | 152 | 157 | 1287 | 1359 | 1.0379 | 1.0989 | 9.2796 | 9.5849 | 0.010379 | 0.010989 | 0.092796 | 0.095849 | 0.0006105 | 0.0030525 | 256813.9934 | 47285.751 | 13595.5814
38908.5546 | 978 | 940 | 38908.5546 | 1132 | 1096 | 1345.5 | 1417.5 | 59.707 | 57.3871 | 69.1087 | 66.9109 | 0.59707 | 0.57387 | 0.69109 | 0.66911 | 0.023199 | 0.021978 | 5749.0838 | 8002.9084 | 59.8248
38908.5553 | 1105 | 1001 | 38908.5553 | 1203 | 1096 | 1404.5 | 1476.5 | 67.4603 | 61.1111 | 73.4432 | 66.9109 | 0.6746 | 0.61111 | 0.73443 | 0.66911 | 0.063492 | 0.065324 | 2563.0644 | 1999.3871 | 36.2851
38908.5559 | 1105 | 709 | 38908.5559 | 1510 | 665 | 1463.5 | 1535.5 | 67.4603 | 43.2845 | 92.1856 | 40.5983 | 0.6746 | 0.43284 | 0.92186 | 0.40598 | 0.24176 | 0.51587 | 414.7954 | 1130.2033 | 87.2557
38908.5566 | 2410 | 10 | 38908.5566 | 1864 | 9 | 1522 | 1594 | 147.1306 | 0.6105 | 113.7973 | 0.54945 | 1.4713 | 0.006105 | 1.138 | 0.0054945 | 1.4652 | 1.1325 | 3.2586 | 39.4843 | 190.735
38908.5573 | 2143 | 35 | 38908.5573 | 2210 | 36 | 1581 | 1653 | 130.8303 | 2.1368 | 134.9206 | 2.1978 | 1.3083 | 0.021368 | 1.3492 | 0.021978 | 1.2869 | 1.3272 | 18.5331 | 14.0108 | 108.6281
38908.558 | 1368 | 741 | 38908.558 | 1315 | 811 | 1639.5 | 1711.5 | 83.5165 | 45.2381 | 80.2808 | 49.5116 | 0.83516 | 0.45238 | 0.80281 | 0.49512 | 0.38278 | 0.30769 | 196.7234 | 1277.8536 | 47.3574
38908.5587 | 2170 | 5 | 38908.5587 | 2143 | 6 | 1698.5 | 1770.5 | 132.4786 | 0.30525 | 130.8303 | 0.3663 | 1.3248 | 0.0030525 | 1.3083 | 0.003663 | 1.3217 | 1.3046 | 14.8686 | 16.4253 | 881.4113
38908.5593 | 2411 | 2 | 38908.5594 | 2471 | 2 | 1757.5 | 1829.5 | 147.1917 | 0.1221 | 150.8547 | 0.1221 | 1.4719 | 0.001221 | 1.5085 | 0.001221 | 1.4707 | 1.5073 | 3.6126 | 0.67864 | 25.0686
38908.56 | 2260 | 2 | 38908.56 | 2351 | 2 | 1816 | 1888 | 137.9731 | 0.1221 | 143.5287 | 0.1221 | 1.3797 | 0.001221 | 1.4353 | 0.001221 | 1.3785 | 1.4341 | 10.2247 | 5.8546 | 623.2679
38908.5607 | 1949 | 3 | 38908.5607 | 2393 | 4 | 1875 | 1947 | 118.9866 | 0.18315 | 146.0928 | 0.2442 | 1.1899 | 0.0018315 | 1.4609 | 0.002442 | 1.188 | 1.4585 | 28.7826 | 3.9737 | 682.0479
38908.5614 | 2172 | 17 | 38908.5614 | 2297 | 18 | 1933.5 | 2005.5 | 132.6007 | 1.0379 | 140.232 | 1.0989 | 1.326 | 0.010379 | 1.4023 | 0.010989 | 1.3156 | 1.3913 | 16.0786 | 8.7852 | 141.7436
38908.5621 | 2292 | 93 | 38908.5621 | 1825 | 70 | 1992.5 | 2064.5 | 139.9267 | 5.6777 | 111.4164 | 4.2735 | 1.3993 | 0.056777 | 1.1142 | 0.042735 | 1.3425 | 1.0714 | 9.5028 | 65.0426 | 43.3845

## C1-3
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 151.1221 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38908.5382 | 1 | 0 | 38908.5382 | 1 | 0 | -68 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5389 | 1 | 0 | 38908.5389 | 1 | 0 | -9.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5396 | 1 | 0 | 38908.5396 | 1 | 0 | 49.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5403 | 1 | 0 | 38908.5403 | 1 | 0 | 108.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5409 | 1 | 0 | 38908.5409 | 1 | 0 | 167 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5416 | 1 | 0 | 38908.5416 | 1 | 0 | 226 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5423 | 1 | 0 | 38908.5423 | 1 | 0 | 284.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.543 | 1 | 0 | 38908.543 | 1 | 0 | 343.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5437 | 1 | 0 | 38908.5437 | 1 | 0 | 402.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5443 | 1 | 0 | 38908.5444 | 1 | 0 | 461 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.545 | 1 | 0 | 38908.545 | 1 | 0 | 520 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5457 | 1 | 0 | 38908.5457 | 1 | 0 | 578.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5464 | 1 | 0 | 38908.5464 | 1 | 0 | 637.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.547 | 1 | 0 | 38908.5471 | 1 | 0 | 696 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5477 | 1 | 0 | 38908.5478 | 1 | 0 | 755 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5484 | 1 | 0 | 38908.5484 | 1 | 0 | 813.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5491 | 1 | 0 | 38908.5491 | 1 | 0 | 872.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5498 | 1 | 0 | 38908.5498 | 1 | 0 | 931.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5505 | 1 | 0 | 38908.5505 | 1 | 0 | 990 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5511 | 1 | 0 | 38908.5512 | 1 | 0 | 1049 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5518 | 1 | 0 | 38908.5518 | 2 | 0 | 1107.5 | 1179.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 247438 | 123669 | 247437.9994
38908.5525 | 1 | 0 | 38908.5525 | 1 | 0 | 1166.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38908.5532 | 1 | 1 | 38908.5532 | 1 | 0 | 1225.5 | 1297.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 612255638.44 | 247438 | 247238.0808
38908.5539 | 1 | 1 | 38908.5539 | 2 | 1 | 1284 | 1356 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 612008100.44 | 247337.9596 | 247238.0404
38908.5545 | 1174 | 891 | 38908.5546 | 1010 | 971 | 1343 | 1415 | 71.6728 | 54.3956 | 61.6606 | 59.2796 | 0.71673 | 0.54396 | 0.61661 | 0.5928 | 0.17277 | 0.02381 | 274.206 | 465.0326 | 37.9069
38908.5552 | 232 | 139 | 38908.5552 | 164 | 129 | 1401.5 | 1473.5 | 14.1636 | 8.486 | 10.0122 | 7.8755 | 0.14164 | 0.08486 | 0.10012 | 0.078755 | 0.056777 | 0.021368 | 2459.5604 | 7767.9971 | 1494.7007
38908.5559 | 1347 | 997 | 38908.5559 | 1112 | 809 | 1460.5 | 1532.5 | 82.2344 | 60.8669 | 67.8877 | 49.3895 | 0.82234 | 0.60867 | 0.67888 | 0.49389 | 0.21368 | 0.18498 | 417.9733 | 1245.6995 | 12.1983
38908.5566 | 2228 | 13 | 38908.5566 | 2377 | 13 | 1519.5 | 1591.5 | 136.0195 | 0.79365 | 145.116 | 0.79365 | 1.3602 | 0.0079365 | 1.4512 | 0.0079365 | 1.3523 | 1.4432 | 12.9118 | 4.3467 | 75.1034
38908.5573 | 2025 | 29 | 38908.5573 | 1999 | 30 | 1578 | 1650 | 123.6264 | 1.7705 | 122.0391 | 1.8315 | 1.2363 | 0.017705 | 1.2204 | 0.018315 | 1.2186 | 1.2021 | 23.9084 | 25.8408 | 298.3733
38908.5579 | 1682 | 731 | 38908.558 | 1127 | 734 | 1637 | 1709 | 102.6862 | 44.6276 | 68.8034 | 44.8107 | 1.0269 | 0.44628 | 0.68803 | 0.44811 | 0.58059 | 0.23993 | 53.5889 | 138.0566 | 4.9489
38908.5586 | 2459 | 6 | 38908.5586 | 2140 | 6 | 1695.5 | 1767.5 | 150.1221 | 0.3663 | 130.6471 | 0.3663 | 1.5012 | 0.003663 | 1.3065 | 0.003663 | 1.4976 | 1.3028 | 0.67387 | 26.9682 | 36.7454
38908.5593 | 2147 | 1 | 38908.5593 | 2207 | 2 | 1754.5 | 1826.5 | 131.0745 | 0.06105 | 134.7375 | 0.1221 | 1.3107 | 0.0006105 | 1.3474 | 0.001221 | 1.3101 | 1.3462 | 15.3604 | 12.2437 | 3571.114
38908.56 | 1943 | 2 | 38908.56 | 2281 | 2 | 1813.5 | 1885.5 | 118.6203 | 0.1221 | 139.2552 | 0.1221 | 1.1862 | 0.001221 | 1.3926 | 0.001221 | 1.185 | 1.3913 | 27.7625 | 8.5562 | 2090.1846
38908.5607 | 2142 | 3 | 38908.5607 | 2161 | 4 | 1872 | 1944 | 130.7692 | 0.18315 | 131.9292 | 0.2442 | 1.3077 | 0.0018315 | 1.3193 | 0.002442 | 1.3059 | 1.3168 | 15.7354 | 14.7487 | 1415.4617
38908.5613 | 2406 | 17 | 38908.5614 | 2015 | 12 | 1931 | 2003 | 146.8864 | 1.0379 | 123.0159 | 0.7326 | 1.4689 | 0.010379 | 1.2302 | 0.007326 | 1.4585 | 1.2228 | 2.9778 | 28.7735 | 68.8466
38908.562 | 2189 | 153 | 38908.562 | 2279 | 86 | 1989.5 | 2061.5 | 133.6386 | 9.3407 | 139.1331 | 5.2503 | 1.3364 | 0.093407 | 1.3913 | 0.052503 | 1.243 | 1.3388 | 66.9998 | 9.5116 | 7.5717

## C1-2
Penlight Test 12 |  |  | 2006-07-10 | 12:56 |  | Vs = |  | 148.0696 |  | R = | 100
XLPE | 7-C | Tray
470 C | 17.3 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38908.5382 | 1 | 0 | 38908.5382 | 1 | 0 | -71 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5389 | 1 | 0 | 38908.5389 | 1 | 0 | -12 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5395 | 1 | 0 | 38908.5395 | 1 | 0 | 46.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5402 | 1 | 0 | 38908.5402 | 1 | 0 | 105.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5409 | 1 | 0 | 38908.5409 | 1 | 0 | 164.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5416 | 1 | 0 | 38908.5416 | 1 | 0 | 223 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5423 | 1 | 0 | 38908.5423 | 1 | 0 | 282 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5429 | 1 | 0 | 38908.543 | 1 | 0 | 340.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5436 | 1 | 0 | 38908.5436 | 1 | 0 | 399.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5443 | 1 | 0 | 38908.5443 | 1 | 0 | 458.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.545 | 1 | 0 | 38908.545 | 1 | 0 | 517 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5457 | 1 | 0 | 38908.5457 | 1 | 0 | 575.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5463 | 1 | 0 | 38908.5464 | 1 | 0 | 634.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.547 | 1 | 0 | 38908.547 | 1 | 0 | 693.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5477 | 1 | 0 | 38908.5477 | 1 | 0 | 752.5 | 824.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5484 | 1 | 0 | 38908.5484 | 1 | 0 | 811 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5491 | 1 | 0 | 38908.5491 | 1 | 0 | 870 | 942 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5497 | 1 | 0 | 38908.5498 | 1 | 0 | 928.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5504 | 1 | 0 | 38908.5504 | 1 | 0 | 987.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5511 | 1 | 0 | 38908.5511 | 1 | 0 | 1046 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5518 | 1 | 0 | 38908.5518 | 1 | 0 | 1105 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5525 | 1 | 0 | 38908.5525 | 1 | 0 | 1163.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242438 | 242438 | 242437.9994
38908.5531 | 2 | 0 | 38908.5532 | 1 | 0 | 1222.5 | 1294.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121169 | 242438 | 121168.9988
38908.5538 | 1 | 2 | 38908.5538 | 2 | 2 | 1281.5 | 1353.5 | 0.06105 | 0.1221 | 0.1221 | 0.1221 | 0.0006105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 242437.8349 | 293759500.1917 | 121118.9588
38908.5545 | 1000 | 964 | 38908.5545 | 1169 | 1191 | 1340 | 1412 | 61.0501 | 58.8523 | 71.3675 | 72.7106 | 0.6105 | 0.58852 | 0.71368 | 0.72711 | 0.021978 | 0.013431 | 2675.4787 | 5580.0921 | 47.0184
38908.5552 | 1202 | 1126 | 38908.5552 | 1017 | 939 | 1399 | 1471 | 73.3822 | 68.7424 | 62.0879 | 57.326 | 0.73382 | 0.68742 | 0.62088 | 0.57326 | 0.046398 | 0.047619 | 3465.4281 | 2766.7493 | 8.3466
38908.5559 | 1281 | 925 | 38908.5559 | 1322 | 1007 | 1457.5 | 1529.5 | 78.2051 | 56.4713 | 80.7082 | 61.4774 | 0.78205 | 0.56471 | 0.80708 | 0.61477 | 0.21734 | 0.19231 | 326.547 | 16663.0278 | 23.5753
38908.5566 | 1989 | 11 | 38908.5566 | 1961 | 11 | 1516.5 | 1588.5 | 121.4286 | 0.67155 | 119.7192 | 0.67155 | 1.2143 | 0.0067155 | 1.1972 | 0.0067155 | 1.2076 | 1.1905 | 22.5757 | 24.4247 | 759.1131
38908.5572 | 2020 | 29 | 38908.5572 | 2393 | 33 | 1575.5 | 1647.5 | 123.3211 | 1.7705 | 146.0928 | 2.0147 | 1.2332 | 0.017705 | 1.4609 | 0.020147 | 1.2155 | 1.4408 | 306.4195 | 1.5602 | 19.9385
38908.5579 | 1559 | 522 | 38908.5579 | 1476 | 588 | 1634 | 1706 | 95.177 | 31.8681 | 90.1099 | 35.8974 | 0.95177 | 0.31868 | 0.9011 | 0.35897 | 0.63309 | 0.54212 | 98.9667 | 323.0714 | 50.3793
38908.5586 | 1973 | 6 | 38908.5586 | 2221 | 5 | 1693 | 1765 | 120.4518 | 0.3663 | 135.5922 | 0.30525 | 1.2045 | 0.003663 | 1.3559 | 0.0030525 | 1.2009 | 1.3529 | 23.7774 | 9.3113 | 633.7208
38908.5593 | 1950 | 2 | 38908.5593 | 2409 | 2 | 1751.5 | 1823.5 | 119.0476 | 0.1221 | 147.0696 | 0.1221 | 1.1905 | 0.001221 | 1.4707 | 0.001221 | 1.1893 | 1.4695 | 28.7246 | 0.68249 | 160.4434
38908.56 | 2340 | 2 | 38908.56 | 2386 | 2 | 1810.5 | 1882.5 | 142.8571 | 0.1221 | 145.6654 | 0.1221 | 1.4286 | 0.001221 | 1.4567 | 0.001221 | 1.4274 | 1.4554 | 3.8467 | 1.6887 | 69.2317
38908.5606 | 2245 | 3 | 38908.5606 | 2006 | 3 | 1869.5 | 1941.5 | 137.0574 | 0.18315 | 122.4664 | 0.18315 | 1.3706 | 0.0018315 | 1.2247 | 0.0018315 | 1.3687 | 1.2228 | 8.0963 | 21.3322 | 1039.5452
38908.5613 | 2224 | 14 | 38908.5613 | 2392 | 11 | 1928 | 2000 | 135.7753 | 0.8547 | 146.0317 | 0.67155 | 1.3578 | 0.008547 | 1.4603 | 0.0067155 | 1.3492 | 1.4536 | 16.2432 | 1.443 | 19.0384
38908.562 | 2098 | 265 | 38908.562 | 1707 | 237 | 1987 | 2059 | 128.083 | 16.1783 | 104.2125 | 14.4689 | 1.2808 | 0.16178 | 1.0421 | 0.14469 | 1.119 | 0.89744 | 18.5905 | 368.1125 | 18.511

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 12 |  |  | 2006-07-10 | 12:56
38908.5382 | 1 | 0 | 1 | XLPE | 7-C | Tray
38908.5389 | 1 | 0 | 1 | 470 C | 17.3 kW/m2 |  | Conductors
38908.5395 | 1 | 0 | 1
38908.5402 | 1 | 0 | 1
38908.5409 | 1 | 0 | 1
38908.5416 | 1 | 0 | 1
38908.5423 | 1 | 0 | 1
38908.5429 | 1 | 0 | 1
38908.5436 | 1 | 0 | 1
38908.5443 | 1 | 0 | 1
38908.545 | 1 | 0 | 1
38908.5457 | 1 | 0 | 1
38908.5463 | 1 | 0 | 1
38908.547 | 1 | 0 | 1
38908.5477 | 1 | 0 | 1
38908.5484 | 1 | 0 | 1
38908.5491 | 1 | 0 | 1
38908.5497 | 1 | 0 | 1
38908.5504 | 1 | 0 | 1
38908.5511 | 1 | 0 | 1
38908.5518 | 1 | 0 | 1
38908.5525 | 1 | 0 | 1
38908.5531 | 2 | 0 | 1
38908.5538 | 1 | 2 | 1
38908.5545 | 1000 | 964 | 1
38908.5552 | 1202 | 1126 | 1
38908.5559 | 1281 | 925 | 1
38908.5566 | 1989 | 11 | 1
38908.5572 | 2020 | 29 | 1
38908.5579 | 1559 | 522 | 1
38908.5586 | 1973 | 6 | 1
38908.5593 | 1950 | 2 | 1
38908.56 | 2340 | 2 | 1
38908.5606 | 2245 | 3 | 1
38908.5613 | 2224 | 14 | 1
38908.562 | 2098 | 265 | 1
38908.5382 | 1 | 0 | 2
38908.5389 | 1 | 0 | 2
38908.5395 | 1 | 0 | 2
38908.5402 | 1 | 0 | 2
38908.5409 | 1 | 0 | 2
38908.5416 | 1 | 0 | 2
38908.5423 | 1 | 0 | 2
38908.543 | 1 | 0 | 2
38908.5436 | 1 | 0 | 2
38908.5443 | 1 | 0 | 2
38908.545 | 1 | 0 | 2
38908.5457 | 1 | 0 | 2
38908.5464 | 1 | 0 | 2
38908.547 | 1 | 0 | 2
38908.5477 | 1 | 0 | 2
38908.5484 | 1 | 0 | 2
38908.5491 | 1 | 0 | 2
38908.5498 | 1 | 0 | 2
38908.5504 | 1 | 0 | 2
38908.5511 | 1 | 0 | 2
38908.5518 | 1 | 0 | 2
38908.5525 | 1 | 0 | 2
38908.5532 | 1 | 0 | 2
38908.5538 | 2 | 2 | 2
38908.5545 | 1169 | 1191 | 2
38908.5552 | 1017 | 939 | 2
38908.5559 | 1322 | 1007 | 2
38908.5566 | 1961 | 11 | 2
38908.5572 | 2393 | 33 | 2
38908.5579 | 1476 | 588 | 2
38908.5586 | 2221 | 5 | 2
38908.5593 | 2409 | 2 | 2
38908.56 | 2386 | 2 | 2
38908.5606 | 2006 | 3 | 2
38908.5613 | 2392 | 11 | 2
38908.562 | 1707 | 237 | 2
38908.5382 | 1 | 0 | 3
38908.5389 | 1 | 0 | 3
38908.5396 | 1 | 0 | 3
38908.5403 | 1 | 0 | 3
38908.5409 | 1 | 0 | 3
38908.5416 | 1 | 0 | 3
38908.5423 | 1 | 0 | 3
38908.543 | 1 | 0 | 3
38908.5437 | 1 | 0 | 3
38908.5443 | 1 | 0 | 3
38908.545 | 1 | 0 | 3
38908.5457 | 1 | 0 | 3
38908.5464 | 1 | 0 | 3
38908.547 | 1 | 0 | 3
38908.5477 | 1 | 0 | 3
38908.5484 | 1 | 0 | 3
38908.5491 | 1 | 0 | 3
38908.5498 | 1 | 0 | 3
38908.5505 | 1 | 0 | 3
38908.5511 | 1 | 0 | 3
38908.5518 | 1 | 0 | 3
38908.5525 | 1 | 0 | 3
38908.5532 | 1 | 1 | 3
38908.5539 | 1 | 1 | 3
38908.5545 | 1174 | 891 | 3
38908.5552 | 232 | 139 | 3
38908.5559 | 1347 | 997 | 3
38908.5566 | 2228 | 13 | 3
38908.5573 | 2025 | 29 | 3
38908.5579 | 1682 | 731 | 3
38908.5586 | 2459 | 6 | 3
38908.5593 | 2147 | 1 | 3
38908.56 | 1943 | 2 | 3
38908.5607 | 2142 | 3 | 3
38908.5613 | 2406 | 17 | 3
38908.562 | 2189 | 153 | 3
38908.5382 | 1 | 0 | 4
38908.5389 | 1 | 0 | 4
38908.5396 | 1 | 0 | 4
38908.5403 | 1 | 0 | 4
38908.5409 | 1 | 0 | 4
38908.5416 | 1 | 0 | 4
38908.5423 | 1 | 0 | 4
38908.543 | 1 | 0 | 4
38908.5437 | 1 | 0 | 4
38908.5444 | 1 | 0 | 4
38908.545 | 1 | 1 | 4
38908.5457 | 1 | 0 | 4
38908.5464 | 1 | 0 | 4
38908.5471 | 1 | 0 | 4
38908.5478 | 1 | 0 | 4
38908.5484 | 1 | 0 | 4
38908.5491 | 1 | 0 | 4
38908.5498 | 1 | 0 | 4
38908.5505 | 1 | 0 | 4
38908.5512 | 1 | 0 | 4
38908.5518 | 2 | 0 | 4
38908.5525 | 1 | 0 | 4
38908.5532 | 1 | 0 | 4
38908.5539 | 2 | 1 | 4
38908.5546 | 1010 | 971 | 4
38908.5552 | 164 | 129 | 4
38908.5559 | 1112 | 809 | 4
38908.5566 | 2377 | 13 | 4
38908.5573 | 1999 | 30 | 4
38908.558 | 1127 | 734 | 4
38908.5586 | 2140 | 6 | 4
38908.5593 | 2207 | 2 | 4
38908.56 | 2281 | 2 | 4
38908.5607 | 2161 | 4 | 4
38908.5614 | 2015 | 12 | 4
38908.562 | 2279 | 86 | 4
38908.5382 | 1 | 0 | 5
38908.5389 | 1 | 0 | 5
38908.5396 | 1 | 0 | 5
38908.5403 | 1 | 0 | 5
38908.541 | 1 | 0 | 5
38908.5416 | 1 | 0 | 5
38908.5423 | 1 | 0 | 5
38908.543 | 1 | 0 | 5
38908.5437 | 1 | 0 | 5
38908.5444 | 1 | 0 | 5
38908.545 | 1 | 0 | 5
38908.5457 | 1 | 0 | 5
38908.5464 | 1 | 0 | 5
38908.5471 | 1 | 0 | 5
38908.5478 | 1 | 0 | 5
38908.5484 | 1 | 0 | 5
38908.5491 | 1 | 0 | 5
38908.5498 | 1 | 0 | 5
38908.5505 | 1 | 0 | 5
38908.5512 | 1 | 0 | 5
38908.5519 | 1 | 0 | 5
38908.5525 | 1 | 0 | 5
38908.5532 | 1 | 0 | 5
38908.5539 | 17 | 18 | 5
38908.5546 | 978 | 940 | 5
38908.5553 | 1105 | 1001 | 5
38908.5559 | 1105 | 709 | 5
38908.5566 | 2410 | 10 | 5
38908.5573 | 2143 | 35 | 5
38908.558 | 1368 | 741 | 5
38908.5587 | 2170 | 5 | 5
38908.5593 | 2411 | 2 | 5
38908.56 | 2260 | 2 | 5
38908.5607 | 1949 | 3 | 5
38908.5614 | 2172 | 17 | 5
38908.5621 | 2292 | 93 | 5
38908.5383 | 1 | 0 | 6
38908.5389 | 1 | 0 | 6
38908.5396 | 1 | 0 | 6
38908.5403 | 1 | 0 | 6
38908.541 | 1 | 0 | 6
38908.5417 | 1 | 0 | 6
38908.5423 | 1 | 0 | 6
38908.543 | 1 | 0 | 6
38908.5437 | 1 | 0 | 6
38908.5444 | 1 | 0 | 6
38908.5451 | 1 | 0 | 6
38908.5457 | 1 | 0 | 6
38908.5464 | 1 | 0 | 6
38908.5471 | 1 | 0 | 6
38908.5478 | 1 | 0 | 6
38908.5485 | 1 | 0 | 6
38908.5491 | 1 | 0 | 6
38908.5498 | 1 | 0 | 6
38908.5505 | 1 | 0 | 6
38908.5512 | 1 | 0 | 6
38908.5519 | 1 | 0 | 6
38908.5532 | 1 | 0 | 6
38908.5539 | 152 | 157 | 6
38908.5546 | 1132 | 1096 | 6
38908.5553 | 1203 | 1096 | 6
38908.5559 | 1510 | 665 | 6
38908.5566 | 1864 | 9 | 6
38908.5573 | 2210 | 36 | 6
38908.558 | 1315 | 811 | 6
38908.5587 | 2143 | 6 | 6
38908.5594 | 2471 | 2 | 6
38908.56 | 2351 | 2 | 6
38908.5607 | 2393 | 4 | 6
38908.5614 | 2297 | 18 | 6
38908.5621 | 1825 | 70 | 6
38908.5383 | 1 | 0 | 7
38908.539 | 1 | 0 | 7
38908.5396 | 1 | 0 | 7
38908.5403 | 1 | 0 | 7
38908.541 | 1 | 0 | 7
38908.5417 | 1 | 0 | 7
38908.5424 | 1 | 0 | 7
38908.543 | 1 | 0 | 7
38908.5437 | 1 | 0 | 7
38908.5444 | 1 | 0 | 7
38908.5451 | 1 | 0 | 7
38908.5458 | 1 | 0 | 7
38908.5464 | 1 | 0 | 7
38908.5471 | 1 | 0 | 7
38908.5478 | 1 | 0 | 7
38908.5485 | 1 | 0 | 7
38908.5492 | 1 | 0 | 7
38908.5498 | 1 | 0 | 7
38908.5505 | 1 | 0 | 7
38908.5512 | 1 | 0 | 7
38908.5519 | 1 | 0 | 7
38908.5526 | 1 | 0 | 7
38908.5532 | 1 | 0 | 7
38908.5539 | 967 | 1004 | 7
38908.5546 | 248 | 228 | 7
38908.5553 | 1233 | 878 | 7
38908.556 | 1993 | 245 | 7
38908.5566 | 2217 | 8 | 7
38908.5573 | 1878 | 24 | 7
38908.558 | 1306 | 731 | 7
38908.5587 | 2237 | 5 | 7
38908.5594 | 2116 | 1 | 7
38908.56 | 2469 | 2 | 7
38908.5607 | 2433 | 5 | 7
38908.5614 | 2261 | 20 | 7
38908.5621 | 1823 | 57 | 7
38908.5383 | 1 | 0 | 8
38908.539 | 1 | 0 | 8
38908.5397 | 1 | 0 | 8
38908.5403 | 1 | 0 | 8
38908.541 | 1 | 0 | 8
38908.5417 | 1 | 0 | 8
38908.5424 | 1 | 0 | 8
38908.5431 | 1 | 0 | 8
38908.5437 | 1 | 0 | 8
38908.5444 | 1 | 0 | 8
38908.5451 | 1 | 0 | 8
38908.5458 | 1 | 0 | 8
38908.5465 | 1 | 0 | 8
38908.5471 | 1 | 0 | 8
38908.5478 | 1 | 0 | 8
38908.5485 | 1 | 0 | 8
38908.5492 | 1 | 0 | 8
38908.5499 | 1 | 0 | 8
38908.5505 | 1 | 0 | 8
38908.5512 | 1 | 0 | 8
38908.5519 | 1 | 0 | 8
38908.5526 | 1 | 0 | 8
38908.5533 | 2 | 0 | 8
38908.5539 | 1188 | 1191 | 8
38908.5546 | 260 | 253 | 8
38908.5553 | 1025 | 916 | 8
38908.556 | 1717 | 202 | 8
38908.5567 | 2364 | 8 | 8
38908.5573 | 1841 | 25 | 8
38908.558 | 1362 | 945 | 8
38908.5587 | 2188 | 5 | 8
38908.5594 | 1987 | 1 | 8
38908.5601 | 2205 | 1 | 8
38908.5607 | 2441 | 6 | 8
38908.5614 | 2019 | 19 | 8
38908.5621 | 1858 | 73 | 8
38908.5383 | 1 | 0 | 9
38908.539 | 1 | 0 | 9
38908.5397 | 1 | 0 | 9
38908.5403 | 1 | 0 | 9
38908.541 | 1 | 0 | 9
38908.5417 | 1 | 0 | 9
38908.5424 | 1 | 0 | 9
38908.5431 | 1 | 0 | 9
38908.5437 | 1 | 0 | 9
38908.5444 | 1 | 0 | 9
38908.5451 | 1 | 0 | 9
38908.5458 | 1 | 0 | 9
38908.5465 | 1 | 0 | 9
38908.5472 | 1 | 0 | 9
38908.5478 | 1 | 0 | 9
38908.5485 | 1 | 0 | 9
38908.5492 | 1 | 0 | 9
38908.5499 | 1 | 0 | 9
38908.5506 | 1 | 0 | 9
38908.5512 | 1 | 0 | 9
38908.5519 | 1 | 0 | 9
38908.5526 | 1 | 0 | 9
38908.5533 | 1 | 0 | 9
38908.554 | 943 | 976 | 9
38908.5546 | 44 | 38 | 9
38908.5553 | 1072 | 957 | 9
38908.556 | 1774 | 215 | 9
38908.5567 | 2413 | 10 | 9
38908.5574 | 2151 | 43 | 9
38908.558 | 1359 | 963 | 9
38908.5587 | 2344 | 5 | 9
38908.5594 | 2160 | 1 | 9
38908.5601 | 2142 | 1 | 9
38908.5608 | 2024 | 4 | 9
38908.5614 | 2007 | 19 | 9
38908.5621 | 1901 | 71 | 9
38908.5383 | 1 | 0 | 10
38908.539 | 1 | 0 | 10
38908.5397 | 1 | 0 | 10
38908.5404 | 1 | 0 | 10
38908.541 | 1 | 0 | 10
38908.5417 | 1 | 0 | 10
38908.5424 | 1 | 0 | 10
38908.5431 | 1 | 0 | 10
38908.5438 | 1 | 0 | 10
38908.5444 | 1 | 0 | 10
38908.5451 | 1 | 0 | 10
38908.5458 | 1 | 0 | 10
38908.5465 | 1 | 0 | 10
38908.5472 | 1 | 1 | 10
38908.5478 | 1 | 0 | 10
38908.5485 | 1 | 0 | 10
38908.5492 | 1 | 0 | 10
38908.5499 | 1 | 0 | 10
38908.5506 | 1 | 0 | 10
38908.5512 | 1 | 0 | 10
38908.5519 | 1 | 0 | 10
38908.5526 | 1 | 0 | 10
38908.5533 | 1 | 0 | 10
38908.554 | 1139 | 1113 | 10
38908.5547 | 33 | 25 | 10
38908.5553 | 1012 | 961 | 10
38908.556 | 1891 | 285 | 10
38908.5567 | 1990 | 10 | 10
38908.5574 | 2203 | 43 | 10
38908.5581 | 1175 | 708 | 10
38908.5587 | 2207 | 4 | 10
38908.5594 | 2329 | 2 | 10
38908.5601 | 2054 | 2 | 10
38908.5608 | 2101 | 4 | 10
38908.5615 | 2305 | 25 | 10
38908.5621 | 2150 | 89 | 10
38908.5383 | 1 | 0 | 11
38908.539 | 1 | 0 | 11
38908.5397 | 1 | 0 | 11
38908.5404 | 1 | 0 | 11
38908.5411 | 1 | 0 | 11
38908.5417 | 1 | 0 | 11
38908.5424 | 1 | 0 | 11
38908.5431 | 1 | 0 | 11
38908.5438 | 1 | 0 | 11
38908.5445 | 1 | 0 | 11
38908.5451 | 1 | 0 | 11
38908.5458 | 1 | 0 | 11
38908.5465 | 1 | 0 | 11
38908.5472 | 1 | 0 | 11
38908.5479 | 1 | 0 | 11
38908.5485 | 1 | 0 | 11
38908.5492 | 1 | 0 | 11
38908.5499 | 1 | 0 | 11
38908.5506 | 1 | 0 | 11
38908.5513 | 1 | 0 | 11
38908.5519 | 1 | 0 | 11
38908.5526 | 1 | 0 | 11
38908.5533 | 1 | 0 | 11
38908.554 | 121 | 114 | 11
38908.5547 | 29 | 21 | 11
38908.5553 | 1078 | 950 | 11
38908.556 | 1822 | 330 | 11
38908.5567 | 2139 | 11 | 11
38908.5574 | 2339 | 42 | 11
38908.5581 | 1664 | 565 | 11
38908.5587 | 2219 | 3 | 11
38908.5594 | 2242 | 2 | 11
38908.5601 | 2474 | 2 | 11
38908.5608 | 2407 | 3 | 11
38908.5615 | 2378 | 26 | 11
38908.5622 | 2070 | 97 | 11
38908.5384 | 1 | 0 | 12
38908.539 | 1 | 0 | 12
38908.5397 | 1 | 0 | 12
38908.5404 | 1 | 0 | 12
38908.5411 | 1 | 0 | 12
38908.5418 | 1 | 0 | 12
38908.5424 | 1 | 0 | 12
38908.5431 | 1 | 0 | 12
38908.5438 | 1 | 0 | 12
38908.5445 | 1 | 0 | 12
38908.5452 | 1 | 0 | 12
38908.5458 | 1 | 0 | 12
38908.5465 | 1 | 0 | 12
38908.5472 | 1 | 0 | 12
38908.5479 | 1 | 0 | 12
38908.5486 | 1 | 0 | 12
38908.5492 | 1 | 0 | 12
38908.5499 | 1 | 0 | 12
38908.5506 | 1 | 0 | 12
38908.5513 | 1 | 0 | 12
38908.552 | 1 | 0 | 12
38908.5526 | 1 | 0 | 12
38908.5533 | 2 | 0 | 12
38908.554 | 307 | 295 | 12
38908.5547 | 47 | 37 | 12
38908.5554 | 1151 | 1090 | 12
38908.556 | 1632 | 480 | 12
38908.5567 | 2405 | 9 | 12
38908.5574 | 2315 | 42 | 12
38908.5581 | 2052 | 114 | 12
38908.5588 | 1953 | 3 | 12
38908.5594 | 2060 | 1 | 12
38908.5601 | 1950 | 1 | 12
38908.5608 | 2247 | 4 | 12
38908.5615 | 1925 | 20 | 12
38908.5622 | 1978 | 109 | 12
38908.5384 | 1 | 0 | 13
38908.5391 | 1 | 0 | 13
38908.5397 | 1 | 0 | 13
38908.5404 | 1 | 0 | 13
38908.5411 | 1 | 0 | 13
38908.5418 | 1 | 0 | 13
38908.5425 | 1 | 0 | 13
38908.5431 | 1 | 0 | 13
38908.5438 | 1 | 0 | 13
38908.5445 | 1 | 0 | 13
38908.5452 | 1 | 0 | 13
38908.5459 | 1 | 0 | 13
38908.5465 | 1 | 0 | 13
38908.5472 | 1 | 0 | 13
38908.5479 | 1 | 0 | 13
38908.5486 | 1 | 0 | 13
38908.5493 | 1 | 0 | 13
38908.5499 | 1 | 0 | 13
38908.5506 | 1 | 0 | 13
38908.5513 | 1 | 0 | 13
38908.552 | 1 | 0 | 13
38908.5527 | 1 | 0 | 13
38908.5533 | 2 | 1 | 13
38908.554 | 5 | 7 | 13
38908.5547 | 1056 | 1135 | 13
38908.5554 | 379 | 238 | 13
38908.5561 | 1614 | 619 | 13
38908.5567 | 2172 | 10 | 13
38908.5574 | 2235 | 40 | 13
38908.5588 | 2453 | 3 | 13
38908.5595 | 1940 | 1 | 13
38908.5602 | 2073 | 1 | 13
38908.5608 | 1950 | 2 | 13
38908.5615 | 1826 | 25 | 13
38908.5622 | 1917 | 66 | 13
38908.5384 | 1 | 0 | 14
38908.5391 | 1 | 0 | 14
38908.5397 | 1 | 0 | 14
38908.5404 | 1 | 0 | 14
38908.5411 | 1 | 0 | 14
38908.5418 | 1 | 0 | 14
38908.5425 | 1 | 0 | 14
38908.5431 | 1 | 0 | 14
38908.5438 | 1 | 0 | 14
38908.5445 | 1 | 0 | 14
38908.5452 | 1 | 0 | 14
38908.5459 | 1 | 0 | 14
38908.5466 | 1 | 0 | 14
38908.5472 | 1 | 0 | 14
38908.5479 | 1 | 0 | 14
38908.5486 | 1 | 0 | 14
38908.5493 | 1 | 0 | 14
38908.55 | 1 | 0 | 14
38908.5506 | 1 | 0 | 14
38908.5513 | 1 | 0 | 14
38908.552 | 1 | 0 | 14
38908.5527 | 1 | 0 | 14
38908.5534 | 1 | 0 | 14
38908.554 | 3 | 6 | 14
38908.5547 | 1052 | 1012 | 14
38908.5554 | 256 | 199 | 14
38908.5561 | 1507 | 349 | 14
38908.5568 | 2054 | 9 | 14
38908.5574 | 2294 | 38 | 14
38908.5581 | 1897 | 378 | 14
38908.5588 | 2060 | 2 | 14
38908.5595 | 2471 | 2 | 14
38908.5602 | 2057 | 1 | 14
38908.5608 | 2038 | 4 | 14
38908.5615 | 1910 | 22 | 14
38908.5622 | 1837 | 53 | 14
38908.5384 | 1 | 0 | 15
38908.5391 | 1 | 0 | 15
38908.5398 | 1 | 0 | 15
38908.5404 | 1 | 0 | 15
38908.5411 | 1 | 0 | 15
38908.5418 | 1 | 0 | 15
38908.5425 | 1 | 0 | 15
38908.5432 | 1 | 0 | 15
38908.5438 | 1 | 0 | 15
38908.5445 | 1 | 0 | 15
38908.5452 | 1 | 0 | 15
38908.5459 | 1 | 0 | 15
38908.5466 | 1 | 0 | 15
38908.5472 | 1 | 0 | 15
38908.5479 | 1 | 0 | 15
38908.5486 | 1 | 0 | 15
38908.5493 | 1 | 0 | 15
38908.55 | 1 | 0 | 15
38908.5506 | 1 | 0 | 15
38908.5513 | 1 | 0 | 15
38908.552 | 1 | 0 | 15
38908.5527 | 2 | 0 | 15
38908.5534 | 1 | 0 | 15
38908.5541 | 3 | 5 | 15
38908.5547 | 235 | 215 | 15
38908.5554 | 1012 | 866 | 15
38908.5561 | 1831 | 541 | 15
38908.5568 | 2013 | 9 | 15
38908.5575 | 2291 | 41 | 15
38908.5581 | 1971 | 351 | 15
38908.5588 | 1902 | 3 | 15
38908.5595 | 2094 | 1 | 15
38908.5602 | 2438 | 2 | 15
38908.5609 | 2154 | 5 | 15
38908.5615 | 2211 | 27 | 15
38908.5622 | 2179 | 76 | 15
38908.5384 | 1 | 0 | 16
38908.5391 | 1 | 0 | 16
38908.5398 | 1 | 0 | 16
38908.5405 | 1 | 0 | 16
38908.5411 | 1 | 0 | 16
38908.5418 | 1 | 0 | 16
38908.5425 | 1 | 0 | 16
38908.5432 | 1 | 0 | 16
38908.5439 | 1 | 0 | 16
38908.5445 | 1 | 0 | 16
38908.5452 | 1 | 0 | 16
38908.5459 | 1 | 0 | 16
38908.5466 | 1 | 0 | 16
38908.5473 | 1 | 0 | 16
38908.548 | 1 | 0 | 16
38908.5486 | 1 | 0 | 16
38908.5493 | 1 | 0 | 16
38908.55 | 1 | 1 | 16
38908.5507 | 1 | 0 | 16
38908.5513 | 2 | 0 | 16
38908.552 | 1 | 0 | 16
38908.5527 | 1 | 0 | 16
38908.5534 | 1 | 0 | 16
38908.5541 | 2 | 5 | 16
38908.5547 | 304 | 294 | 16
38908.5554 | 1079 | 994 | 16
38908.5561 | 1548 | 418 | 16
38908.5568 | 2392 | 8 | 16
38908.5575 | 2226 | 56 | 16
38908.5581 | 1905 | 444 | 16
38908.5588 | 1996 | 2 | 16
38908.5595 | 2316 | 2 | 16
38908.5602 | 2140 | 2 | 16
38908.5609 | 2186 | 6 | 16
38908.5616 | 2356 | 27 | 16
38908.5622 | 2049 | 81 | 16
38908.5384 | 1 | 0 | 17
38908.5391 | 1 | 0 | 17
38908.5398 | 1 | 0 | 17
38908.5405 | 1 | 0 | 17
38908.5412 | 1 | 0 | 17
38908.5418 | 1 | 0 | 17
38908.5425 | 1 | 0 | 17
38908.5432 | 1 | 0 | 17
38908.5439 | 1 | 0 | 17
38908.5446 | 1 | 0 | 17
38908.5452 | 1 | 0 | 17
38908.5459 | 1 | 0 | 17
38908.5466 | 1 | 0 | 17
38908.5473 | 1 | 0 | 17
38908.548 | 1 | 0 | 17
38908.5486 | 1 | 0 | 17
38908.5493 | 1 | 0 | 17
38908.55 | 2 | 0 | 17
38908.5507 | 2 | 0 | 17
38908.5514 | 1 | 0 | 17
38908.552 | 1 | 0 | 17
38908.5527 | 1 | 0 | 17
38908.5534 | 1 | 0 | 17
38908.5541 | 3 | 5 | 17
38908.5548 | 253 | 222 | 17
38908.5555 | 1147 | 983 | 17
38908.5561 | 1712 | 371 | 17
38908.5568 | 2392 | 6 | 17
38908.5575 | 2383 | 68 | 17
38908.5582 | 1893 | 482 | 17
38908.5589 | 2463 | 3 | 17
38908.5595 | 2006 | 1 | 17
38908.5602 | 2036 | 2 | 17
38908.5609 | 1913 | 4 | 17
38908.5616 | 1856 | 19 | 17
38908.5623 | 2164 | 90 | 17
38908.5384 | 1 | 0 | 18
38908.5391 | 1 | 0 | 18
38908.5398 | 1 | 0 | 18
38908.5405 | 1 | 0 | 18
38908.5412 | 1 | 0 | 18
38908.5419 | 1 | 0 | 18
38908.5425 | 1 | 0 | 18
38908.5432 | 1 | 0 | 18
38908.5439 | 1 | 0 | 18
38908.5446 | 2 | 0 | 18
38908.5453 | 1 | 0 | 18
38908.5459 | 1 | 0 | 18
38908.5466 | 1 | 0 | 18
38908.5473 | 1 | 0 | 18
38908.548 | 1 | 0 | 18
38908.5487 | 1 | 0 | 18
38908.5493 | 1 | 0 | 18
38908.55 | 1 | 0 | 18
38908.5507 | 1 | 0 | 18
38908.5514 | 1 | 0 | 18
38908.5521 | 1 | 0 | 18
38908.5527 | 1 | 0 | 18
38908.5534 | 1 | 0 | 18
38908.5541 | 3 | 5 | 18
38908.5548 | 372 | 414 | 18
38908.5555 | 981 | 847 | 18
38908.5561 | 2051 | 253 | 18
38908.5568 | 1974 | 6 | 18
38908.5575 | 2343 | 45 | 18
38908.5582 | 1829 | 479 | 18
38908.5589 | 2448 | 3 | 18
38908.5595 | 1914 | 1 | 18
38908.5602 | 2109 | 2 | 18
38908.5609 | 2215 | 5 | 18
38908.5616 | 1957 | 26 | 18
38908.5623 | 1802 | 81 | 18
38908.5385 | 1 | 0 | 19
38908.5391 | 1 | 0 | 19
38908.5398 | 1 | 0 | 19
38908.5405 | 1 | 0 | 19
38908.5412 | 1 | 0 | 19
38908.5419 | 1 | 0 | 19
38908.5425 | 1 | 0 | 19
38908.5432 | 1 | 0 | 19
38908.5439 | 1 | 0 | 19
38908.5446 | 1 | 0 | 19
38908.5453 | 1 | 0 | 19
38908.5459 | 1 | 0 | 19
38908.5466 | 1 | 0 | 19
38908.5473 | 1 | 0 | 19
38908.548 | 1 | 0 | 19
38908.5487 | 1 | 0 | 19
38908.5494 | 1 | 0 | 19
38908.55 | 1 | 0 | 19
38908.5507 | 1 | 0 | 19
38908.5514 | 1 | 0 | 19
38908.5521 | 1 | 0 | 19
38908.5528 | 1 | 0 | 19
38908.5534 | 1 | 0 | 19
38908.5541 | 2 | 3 | 19
38908.5548 | 122 | 103 | 19
38908.5555 | 1245 | 1111 | 19
38908.5562 | 2212 | 152 | 19
38908.5568 | 2101 | 9 | 19
38908.5575 | 1974 | 46 | 19
38908.5582 | 1597 | 443 | 19
38908.5589 | 1940 | 2 | 19
38908.5596 | 1924 | 1 | 19
38908.5602 | 2256 | 2 | 19
38908.5609 | 2403 | 6 | 19
38908.5616 | 2066 | 36 | 19
38908.5623 | 2090 | 90 | 19
38908.5385 | 1 | 0 | 20
38908.5392 | 1 | 0 | 20
38908.5398 | 1 | 0 | 20
38908.5405 | 1 | 0 | 20
38908.5412 | 1 | 0 | 20
38908.5419 | 1 | 0 | 20
38908.5426 | 1 | 0 | 20
38908.5433 | 1 | 0 | 20
38908.5439 | 1 | 0 | 20
38908.5446 | 1 | 0 | 20
38908.5453 | 1 | 0 | 20
38908.546 | 1 | 0 | 20
38908.5467 | 1 | 0 | 20
38908.5473 | 1 | 0 | 20
38908.548 | 1 | 0 | 20
38908.5487 | 1 | 0 | 20
38908.5494 | 1 | 0 | 20
38908.55 | 1 | 0 | 20
38908.5507 | 1 | 0 | 20
38908.5514 | 1 | 0 | 20
38908.5521 | 1 | 0 | 20
38908.5528 | 1 | 0 | 20
38908.5534 | 1 | 0 | 20
38908.5541 | 13 | 12 | 20
38908.5548 | 98 | 80 | 20
38908.5555 | 1088 | 919 | 20
38908.5562 | 2056 | 68 | 20
38908.5569 | 2105 | 9 | 20
38908.5575 | 1979 | 51 | 20
38908.5582 | 1690 | 495 | 20
38908.5589 | 1949 | 2 | 20
38908.5596 | 2307 | 1 | 20
38908.5603 | 2140 | 1 | 20
38908.5609 | 1917 | 5 | 20
38908.5616 | 2141 | 46 | 20
38908.5623 | 2218 | 28 | 20
38908.5385 | 1 | 0 | 21
38908.5392 | 1 | 0 | 21
38908.5399 | 1 | 0 | 21
38908.5405 | 1 | 0 | 21
38908.5412 | 1 | 0 | 21
38908.5419 | 1 | 0 | 21
38908.5426 | 1 | 0 | 21
38908.5433 | 1 | 0 | 21
38908.5439 | 1 | 0 | 21
38908.5446 | 1 | 0 | 21
38908.5453 | 1 | 0 | 21
38908.546 | 1 | 0 | 21
38908.5467 | 1 | 0 | 21
38908.5473 | 1 | 0 | 21
38908.548 | 1 | 0 | 21
38908.5487 | 1 | 0 | 21
38908.5494 | 1 | 0 | 21
38908.5501 | 1 | 0 | 21
38908.5508 | 1 | 0 | 21
38908.5514 | 1 | 0 | 21
38908.5521 | 1 | 0 | 21
38908.5528 | 1 | 0 | 21
38908.5535 | 1 | 0 | 21
38908.5542 | 7 | 6 | 21
38908.5548 | 118 | 98 | 21
38908.5555 | 1126 | 948 | 21
38908.5562 | 2023 | 69 | 21
38908.5569 | 2231 | 10 | 21
38908.5576 | 2001 | 59 | 21
38908.5582 | 1819 | 409 | 21
38908.5589 | 1943 | 2 | 21
38908.5596 | 2424 | 2 | 21
38908.5603 | 2246 | 3 | 21
38908.561 | 1945 | 5 | 21
38908.5616 | 2261 | 55 | 21
38908.5623 | 2354 | 33 | 21
38908.5385 | 1 | 0 | 22
38908.5392 | 1 | 0 | 22
38908.5399 | 1 | 0 | 22
38908.5406 | 1 | 0 | 22
38908.5412 | 1 | 0 | 22
38908.5419 | 1 | 0 | 22
38908.5426 | 2 | 0 | 22
38908.5433 | 1 | 0 | 22
38908.544 | 1 | 0 | 22
38908.5446 | 1 | 0 | 22
38908.5453 | 1 | 0 | 22
38908.546 | 1 | 0 | 22
38908.5467 | 1 | 0 | 22
38908.5474 | 1 | 0 | 22
38908.548 | 1 | 0 | 22
38908.5487 | 1 | 0 | 22
38908.5494 | 1 | 0 | 22
38908.5501 | 1 | 0 | 22
38908.5508 | 1 | 0 | 22
38908.5514 | 1 | 0 | 22
38908.5521 | 1 | 0 | 22
38908.5528 | 1 | 0 | 22
38908.5535 | 1 | 0 | 22
38908.5542 | 85 | 89 | 22
38908.5548 | 114 | 95 | 22
38908.5555 | 1257 | 1062 | 22
38908.5562 | 2102 | 28 | 22
38908.5569 | 2376 | 11 | 22
38908.5576 | 2222 | 77 | 22
38908.5583 | 2023 | 587 | 22
38908.5589 | 2383 | 2 | 22
38908.5596 | 2484 | 2 | 22
38908.5603 | 2432 | 3 | 22
38908.561 | 2050 | 6 | 22
38908.5617 | 2320 | 52 | 22
38908.5623 | 2088 | 30 | 22
38908.5385 | 1 | 0 | 23
38908.5392 | 1 | 0 | 23
38908.5399 | 1 | 0 | 23
38908.5406 | 1 | 0 | 23
38908.5413 | 1 | 0 | 23
38908.5419 | 1 | 0 | 23
38908.5426 | 1 | 0 | 23
38908.5433 | 1 | 0 | 23
38908.544 | 1 | 0 | 23
38908.5447 | 1 | 0 | 23
38908.5453 | 1 | 0 | 23
38908.546 | 1 | 0 | 23
38908.5467 | 1 | 0 | 23
38908.5474 | 1 | 0 | 23
38908.5481 | 1 | 0 | 23
38908.5487 | 1 | 0 | 23
38908.5494 | 1 | 0 | 23
38908.5501 | 1 | 0 | 23
38908.5508 | 1 | 0 | 23
38908.5515 | 1 | 0 | 23
38908.5521 | 1 | 0 | 23
38908.5528 | 1 | 0 | 23
38908.5535 | 1 | 0 | 23
38908.5542 | 899 | 720 | 23
38908.5549 | 284 | 253 | 23
38908.5555 | 1211 | 1020 | 23
38908.5562 | 2356 | 26 | 23
38908.5569 | 2066 | 8 | 23
38908.5576 | 2340 | 74 | 23
38908.5583 | 1620 | 448 | 23
38908.5589 | 2175 | 2 | 23
38908.5596 | 1960 | 1 | 23
38908.5603 | 2401 | 2 | 23
38908.561 | 2293 | 6 | 23
38908.5617 | 2178 | 53 | 23
38908.5623 | 2113 | 30 | 23
38908.5386 | 1 | 0 | 24
38908.5392 | 1 | 0 | 24
38908.5399 | 2 | 0 | 24
38908.5406 | 1 | 0 | 24
38908.5413 | 1 | 0 | 24
38908.542 | 1 | 0 | 24
38908.5426 | 1 | 0 | 24
38908.5433 | 1 | 0 | 24
38908.544 | 1 | 0 | 24
38908.5447 | 1 | 0 | 24
38908.5453 | 1 | 0 | 24
38908.546 | 1 | 0 | 24
38908.5467 | 1 | 0 | 24
38908.5474 | 1 | 0 | 24
38908.5481 | 1 | 0 | 24
38908.5488 | 1 | 0 | 24
38908.5494 | 1 | 0 | 24
38908.5501 | 1 | 0 | 24
38908.5508 | 1 | 0 | 24
38908.5515 | 1 | 0 | 24
38908.5522 | 1 | 0 | 24
38908.5528 | 1 | 0 | 24
38908.5535 | 1 | 0 | 24
38908.5542 | 972 | 941 | 24
38908.5549 | 999 | 954 | 24
38908.5556 | 1041 | 859 | 24
38908.5562 | 2288 | 21 | 24
38908.5569 | 2333 | 9 | 24
38908.5576 | 1792 | 65 | 24
38908.5583 | 1682 | 239 | 24
38908.559 | 2461 | 2 | 24
38908.5596 | 2295 | 2 | 24
38908.5603 | 2158 | 2 | 24
38908.561 | 2433 | 8 | 24
38908.5617 | 2136 | 77 | 24
38908.5624 | 2312 | 37 | 24
38908.5386 | 1 | 0 | 25
38908.5392 | 1 | 0 | 25
38908.5399 | 1 | 0 | 25
38908.5406 | 1 | 0 | 25
38908.5413 | 1 | 0 | 25
38908.542 | 1 | 0 | 25
38908.5427 | 1 | 0 | 25
38908.5433 | 1 | 0 | 25
38908.544 | 1 | 0 | 25
38908.5447 | 1 | 0 | 25
38908.5454 | 1 | 0 | 25
38908.5461 | 1 | 0 | 25
38908.5467 | 1 | 0 | 25
38908.5474 | 1 | 0 | 25
38908.5481 | 1 | 0 | 25
38908.5488 | 1 | 0 | 25
38908.5495 | 1 | 0 | 25
38908.5501 | 1 | 0 | 25
38908.5508 | 1 | 0 | 25
38908.5515 | 1 | 0 | 25
38908.5522 | 1 | 0 | 25
38908.5529 | 1 | 0 | 25
38908.5535 | 1 | 0 | 25
38908.5542 | 917 | 946 | 25
38908.5549 | 1128 | 1084 | 25
38908.5556 | 1044 | 863 | 25
38908.5563 | 1859 | 14 | 25
38908.5569 | 2323 | 7 | 25
38908.5576 | 1945 | 52 | 25
38908.5583 | 1813 | 58 | 25
38908.559 | 1944 | 2 | 25
38908.5597 | 2193 | 1 | 25
38908.5603 | 1998 | 1 | 25
38908.561 | 2441 | 9 | 25
38908.5617 | 2315 | 76 | 25
38908.5624 | 2336 | 35 | 25
38908.5386 | 1 | 0 | 26
38908.5393 | 1 | 0 | 26
38908.5399 | 1 | 0 | 26
38908.5406 | 1 | 0 | 26
38908.5413 | 1 | 0 | 26
38908.542 | 1 | 0 | 26
38908.5427 | 1 | 0 | 26
38908.5433 | 1 | 0 | 26
38908.544 | 1 | 0 | 26
38908.5447 | 1 | 0 | 26
38908.5454 | 1 | 1 | 26
38908.5461 | 1 | 0 | 26
38908.5467 | 1 | 0 | 26
38908.5474 | 2 | 0 | 26
38908.5481 | 1 | 0 | 26
38908.5488 | 1 | 0 | 26
38908.5495 | 1 | 0 | 26
38908.5502 | 1 | 0 | 26
38908.5508 | 1 | 0 | 26
38908.5515 | 1 | 0 | 26
38908.5522 | 1 | 0 | 26
38908.5529 | 1 | 0 | 26
38908.5536 | 1 | 0 | 26
38908.5542 | 1135 | 1110 | 26
38908.5549 | 1158 | 1118 | 26
38908.5556 | 967 | 842 | 26
38908.5563 | 1978 | 13 | 26
38908.557 | 2243 | 6 | 26
38908.5576 | 2297 | 67 | 26
38908.5583 | 1944 | 69 | 26
38908.559 | 2021 | 2 | 26
38908.5597 | 2442 | 1 | 26
38908.5604 | 2439 | 2 | 26
38908.561 | 2080 | 7 | 26
38908.5617 | 2329 | 75 | 26
38908.5624 | 1967 | 32 | 26
38908.5386 | 1 | 0 | 27
38908.5393 | 1 | 0 | 27
38908.54 | 2 | 0 | 27
38908.5406 | 2 | 0 | 27
38908.5413 | 1 | 0 | 27
38908.542 | 1 | 0 | 27
38908.5427 | 1 | 0 | 27
38908.5434 | 1 | 0 | 27
38908.544 | 1 | 0 | 27
38908.5447 | 1 | 0 | 27
38908.5454 | 1 | 0 | 27
38908.5461 | 1 | 0 | 27
38908.5468 | 1 | 0 | 27
38908.5474 | 2 | 0 | 27
38908.5481 | 1 | 0 | 27
38908.5488 | 1 | 0 | 27
38908.5495 | 1 | 0 | 27
38908.5502 | 1 | 0 | 27
38908.5508 | 1 | 0 | 27
38908.5515 | 1 | 0 | 27
38908.5522 | 1 | 0 | 27
38908.5529 | 1 | 0 | 27
38908.5536 | 1 | 0 | 27
38908.5542 | 1173 | 1155 | 27
38908.5549 | 1169 | 1122 | 27
38908.5556 | 1109 | 911 | 27
38908.5563 | 2346 | 21 | 27
38908.557 | 2053 | 9 | 27
38908.5577 | 2157 | 74 | 27
38908.5583 | 1879 | 196 | 27
38908.559 | 2090 | 1 | 27
38908.5597 | 2287 | 1 | 27
38908.5604 | 2309 | 2 | 27
38908.5611 | 2079 | 8 | 27
38908.5617 | 1910 | 60 | 27
38908.5624 | 2054 | 33 | 27
38908.5386 | 1 | 0 | 28
38908.5393 | 1 | 0 | 28
38908.54 | 2 | 0 | 28
38908.5407 | 1 | 0 | 28
38908.5413 | 1 | 0 | 28
38908.542 | 1 | 0 | 28
38908.5427 | 1 | 0 | 28
38908.5434 | 1 | 0 | 28
38908.5441 | 1 | 0 | 28
38908.5447 | 1 | 0 | 28
38908.5454 | 1 | 0 | 28
38908.5461 | 1 | 0 | 28
38908.5468 | 1 | 0 | 28
38908.5475 | 1 | 0 | 28
38908.5481 | 1 | 0 | 28
38908.5488 | 1 | 0 | 28
38908.5495 | 1 | 0 | 28
38908.5502 | 1 | 0 | 28
38908.5509 | 1 | 0 | 28
38908.5515 | 1 | 0 | 28
38908.5522 | 1 | 0 | 28
38908.5529 | 1 | 0 | 28
38908.5536 | 1 | 0 | 28
38908.5543 | 987 | 916 | 28
38908.5549 | 1158 | 1113 | 28
38908.5556 | 1187 | 965 | 28
38908.5563 | 2175 | 21 | 28
38908.557 | 1970 | 9 | 28
38908.5577 | 1897 | 65 | 28
38908.5583 | 1937 | 256 | 28
38908.559 | 2419 | 2 | 28
38908.5597 | 2316 | 2 | 28
38908.5604 | 2265 | 2 | 28
38908.5611 | 2041 | 8 | 28
38908.5617 | 1908 | 65 | 28
38908.5624 | 2337 | 40 | 28
38908.5386 | 1 | 0 | 29
38908.5393 | 1 | 0 | 29
38908.54 | 1 | 0 | 29
38908.5407 | 1 | 0 | 29
38908.5414 | 1 | 0 | 29
38908.542 | 1 | 0 | 29
38908.5427 | 1 | 0 | 29
38908.5434 | 1 | 0 | 29
38908.5441 | 1 | 0 | 29
38908.5448 | 1 | 0 | 29
38908.5454 | 1 | 0 | 29
38908.5461 | 1 | 0 | 29
38908.5468 | 1 | 0 | 29
38908.5475 | 1 | 0 | 29
38908.5482 | 1 | 0 | 29
38908.5488 | 1 | 0 | 29
38908.5495 | 1 | 0 | 29
38908.5502 | 1 | 0 | 29
38908.5509 | 1 | 0 | 29
38908.5516 | 1 | 0 | 29
38908.5522 | 1 | 0 | 29
38908.5529 | 1 | 0 | 29
38908.5536 | 1 | 0 | 29
38908.5543 | 980 | 948 | 29
38908.555 | 977 | 931 | 29
38908.5556 | 1048 | 911 | 29
38908.5563 | 1908 | 17 | 29
38908.557 | 2059 | 9 | 29
38908.5577 | 2030 | 85 | 29
38908.5584 | 1698 | 300 | 29
38908.559 | 2457 | 2 | 29
38908.5597 | 2371 | 2 | 29
38908.5604 | 2441 | 2 | 29
38908.5611 | 2357 | 9 | 29
38908.5618 | 2128 | 70 | 29
38908.5624 | 2338 | 41 | 29
38908.5386 | 1 | 0 | 30
38908.5393 | 1 | 0 | 30
38908.54 | 2 | 0 | 30
38908.5407 | 1 | 0 | 30
38908.5414 | 1 | 0 | 30
38908.542 | 1 | 0 | 30
38908.5427 | 1 | 0 | 30
38908.5434 | 1 | 0 | 30
38908.5441 | 1 | 0 | 30
38908.5448 | 1 | 0 | 30
38908.5455 | 1 | 0 | 30
38908.5461 | 1 | 0 | 30
38908.5468 | 1 | 0 | 30
38908.5475 | 1 | 0 | 30
38908.5482 | 1 | 0 | 30
38908.5489 | 1 | 0 | 30
38908.5495 | 1 | 0 | 30
38908.5502 | 1 | 0 | 30
38908.5509 | 1 | 0 | 30
38908.5516 | 1 | 0 | 30
38908.5523 | 1 | 0 | 30
38908.5529 | 1 | 0 | 30
38908.5536 | 1 | 0 | 30
38908.5543 | 1064 | 1112 | 30
38908.555 | 1044 | 1068 | 30
38908.5557 | 1205 | 813 | 30
38908.5563 | 1921 | 17 | 30
38908.557 | 1970 | 9 | 30
38908.5577 | 2140 | 137 | 30
38908.5584 | 1654 | 367 | 30
38908.5591 | 2004 | 2 | 30
38908.5597 | 2357 | 2 | 30
38908.5604 | 2118 | 2 | 30
38908.5611 | 2440 | 8 | 30
38908.5618 | 2279 | 69 | 30
38908.5625 | 1946 | 36 | 30
38908.5387 | 1 | 0 | 31
38908.5393 | 1 | 0 | 31
38908.54 | 1 | 0 | 31
38908.5407 | 1 | 0 | 31
38908.5414 | 1 | 0 | 31
38908.5421 | 1 | 0 | 31
38908.5427 | 1 | 0 | 31
38908.5434 | 1 | 0 | 31
38908.5441 | 1 | 0 | 31
38908.5448 | 1 | 0 | 31
38908.5455 | 1 | 0 | 31
38908.5461 | 1 | 0 | 31
38908.5468 | 1 | 0 | 31
38908.5475 | 1 | 0 | 31
38908.5482 | 1 | 0 | 31
38908.5489 | 1 | 0 | 31
38908.5495 | 1 | 0 | 31
38908.5502 | 1 | 0 | 31
38908.5509 | 1 | 0 | 31
38908.5516 | 1 | 0 | 31
38908.5523 | 1 | 0 | 31
38908.553 | 1 | 0 | 31
38908.5536 | 1 | 0 | 31
38908.5543 | 969 | 938 | 31
38908.555 | 1053 | 1004 | 31
38908.5557 | 1143 | 918 | 31
38908.5564 | 2091 | 11 | 31
38908.557 | 2004 | 6 | 31
38908.5577 | 1877 | 417 | 31
38908.5584 | 1703 | 315 | 31
38908.5591 | 1938 | 1 | 31
38908.5598 | 2378 | 2 | 31
38908.5604 | 1926 | 1 | 31
38908.5611 | 1957 | 8 | 31
38908.5618 | 2291 | 73 | 31
38908.5625 | 1875 | 38 | 31
38908.5387 | 1 | 0 | 32
38908.5394 | 1 | 0 | 32
38908.54 | 1 | 0 | 32
38908.5407 | 1 | 1 | 32
38908.5414 | 1 | 0 | 32
38908.5421 | 1 | 0 | 32
38908.5428 | 1 | 0 | 32
38908.5434 | 1 | 0 | 32
38908.5441 | 1 | 0 | 32
38908.5448 | 1 | 0 | 32
38908.5455 | 1 | 0 | 32
38908.5462 | 1 | 0 | 32
38908.5468 | 1 | 0 | 32
38908.5475 | 1 | 0 | 32
38908.5482 | 1 | 0 | 32
38908.5489 | 1 | 0 | 32
38908.5496 | 1 | 0 | 32
38908.5502 | 1 | 0 | 32
38908.5509 | 1 | 0 | 32
38908.5516 | 1 | 0 | 32
38908.5523 | 1 | 0 | 32
38908.553 | 1 | 0 | 32
38908.5536 | 1 | 0 | 32
38908.5543 | 958 | 899 | 32
38908.555 | 1103 | 1051 | 32
38908.5557 | 1121 | 958 | 32
38908.5564 | 2201 | 11 | 32
38908.557 | 2188 | 6 | 32
38908.5577 | 1551 | 367 | 32
38908.5584 | 2049 | 327 | 32
38908.5591 | 2422 | 2 | 32
38908.5598 | 2323 | 1 | 32
38908.5605 | 1931 | 2 | 32
38908.5611 | 1939 | 8 | 32
38908.5618 | 1837 | 59 | 32
38908.5625 | 1929 | 39 | 32
38908.5387 | 1 | 0 | 33
38908.5394 | 1 | 0 | 33
38908.5401 | 1 | 0 | 33
38908.5407 | 1 | 0 | 33
38908.5414 | 1 | 0 | 33
38908.5421 | 1 | 0 | 33
38908.5428 | 1 | 0 | 33
38908.5435 | 1 | 0 | 33
38908.5441 | 1 | 0 | 33
38908.5448 | 1 | 0 | 33
38908.5455 | 1 | 0 | 33
38908.5462 | 1 | 0 | 33
38908.5469 | 1 | 0 | 33
38908.5475 | 1 | 0 | 33
38908.5482 | 1 | 0 | 33
38908.5489 | 1 | 0 | 33
38908.5496 | 1 | 0 | 33
38908.5503 | 1 | 0 | 33
38908.5509 | 1 | 0 | 33
38908.5516 | 1 | 0 | 33
38908.5523 | 1 | 0 | 33
38908.553 | 1 | 0 | 33
38908.5537 | 1 | 0 | 33
38908.5543 | 867 | 838 | 33
38908.555 | 953 | 904 | 33
38908.5557 | 1252 | 1000 | 33
38908.5564 | 1929 | 13 | 33
38908.5571 | 2011 | 11 | 33
38908.5577 | 1644 | 475 | 33
38908.5584 | 2151 | 227 | 33
38908.5591 | 2192 | 2 | 33
38908.5598 | 2358 | 2 | 33
38908.5605 | 2105 | 2 | 33
38908.5611 | 2296 | 10 | 33
38908.5618 | 1937 | 62 | 33
38908.5625 | 2286 | 47 | 33
38908.5387 | 1 | 0 | 34
38908.5394 | 1 | 0 | 34
38908.5401 | 1 | 0 | 34
38908.5408 | 1 | 0 | 34
38908.5414 | 2 | 0 | 34
38908.5421 | 1 | 0 | 34
38908.5428 | 1 | 0 | 34
38908.5435 | 1 | 0 | 34
38908.5442 | 1 | 0 | 34
38908.5448 | 1 | 0 | 34
38908.5455 | 1 | 0 | 34
38908.5462 | 1 | 0 | 34
38908.5469 | 1 | 0 | 34
38908.5476 | 1 | 0 | 34
38908.5482 | 1 | 0 | 34
38908.5489 | 1 | 0 | 34
38908.5496 | 1 | 0 | 34
38908.5503 | 1 | 0 | 34
38908.551 | 1 | 0 | 34
38908.5516 | 1 | 0 | 34
38908.5523 | 1 | 0 | 34
38908.553 | 1 | 0 | 34
38908.5537 | 1 | 0 | 34
38908.5544 | 887 | 857 | 34
38908.555 | 1117 | 1153 | 34
38908.5557 | 1253 | 1041 | 34
38908.5564 | 2109 | 13 | 34
38908.5571 | 2405 | 15 | 34
38908.5578 | 1714 | 617 | 34
38908.5584 | 1788 | 177 | 34
38908.5591 | 1925 | 1 | 34
38908.5598 | 2450 | 2 | 34
38908.5605 | 2183 | 2 | 34
38908.5612 | 2313 | 9 | 34
38908.5618 | 2323 | 80 | 34
38908.5625 | 2333 | 37 | 34
38908.5387 | 1 | 0 | 35
38908.5394 | 1 | 0 | 35
38908.5401 | 1 | 0 | 35
38908.5408 | 1 | 0 | 35
38908.5414 | 1 | 0 | 35
38908.5428 | 1 | 0 | 35
38908.5435 | 1 | 0 | 35
38908.5442 | 1 | 0 | 35
38908.5448 | 1 | 0 | 35
38908.5455 | 1 | 0 | 35
38908.5462 | 1 | 0 | 35
38908.5469 | 1 | 0 | 35
38908.5476 | 1 | 0 | 35
38908.5483 | 1 | 0 | 35
38908.5489 | 1 | 0 | 35
38908.5496 | 1 | 0 | 35
38908.5503 | 1 | 0 | 35
38908.551 | 1 | 0 | 35
38908.5517 | 1 | 0 | 35
38908.5523 | 1 | 0 | 35
38908.553 | 1 | 0 | 35
38908.5537 | 1 | 0 | 35
38908.5544 | 1030 | 1075 | 35
38908.5551 | 1014 | 1033 | 35
38908.5557 | 1037 | 867 | 35
38908.5564 | 2134 | 13 | 35
38908.5571 | 1918 | 18 | 35
38908.5578 | 1704 | 533 | 35
38908.5585 | 1769 | 168 | 35
38908.5591 | 1976 | 1 | 35
38908.5598 | 1971 | 1 | 35
38908.5605 | 2371 | 4 | 35
38908.5612 | 1925 | 8 | 35
38908.5619 | 2090 | 77 | 35
38908.5625 | 2364 | 36 | 35
38908.5387 | 1 | 0 | 36
38908.5394 | 1 | 0 | 36
38908.5401 | 1 | 0 | 36
38908.5408 | 1 | 0 | 36
38908.5415 | 1 | 0 | 36
38908.5421 | 1 | 0 | 36
38908.5428 | 1 | 0 | 36
38908.5435 | 1 | 0 | 36
38908.5442 | 1 | 0 | 36
38908.5449 | 1 | 0 | 36
38908.5455 | 1 | 0 | 36
38908.5462 | 1 | 0 | 36
38908.5469 | 1 | 0 | 36
38908.5476 | 1 | 0 | 36
38908.5483 | 1 | 0 | 36
38908.5489 | 1 | 0 | 36
38908.5496 | 1 | 0 | 36
38908.5503 | 1 | 0 | 36
38908.551 | 1 | 0 | 36
38908.5517 | 2 | 0 | 36
38908.5523 | 1 | 0 | 36
38908.553 | 1 | 0 | 36
38908.5537 | 1 | 0 | 36
38908.5544 | 1117 | 1088 | 36
38908.5551 | 1074 | 1017 | 36
38908.5558 | 1059 | 869 | 36
38908.5564 | 2425 | 14 | 36
38908.5571 | 1957 | 18 | 36
38908.5578 | 1823 | 546 | 36
38908.5585 | 2438 | 8 | 36
38908.5592 | 1915 | 1 | 36
38908.5598 | 2099 | 2 | 36
38908.5605 | 2406 | 3 | 36
38908.5612 | 1949 | 8 | 36
38908.5619 | 1935 | 64 | 36
38908.5626 | 1879 | 38 | 36
38908.5388 | 1 | 0 | 37
38908.5394 | 1 | 0 | 37
38908.5401 | 1 | 0 | 37
38908.5408 | 1 | 0 | 37
38908.5415 | 1 | 0 | 37
38908.5422 | 1 | 0 | 37
38908.5428 | 1 | 0 | 37
38908.5435 | 1 | 0 | 37
38908.5442 | 1 | 0 | 37
38908.5449 | 1 | 0 | 37
38908.5456 | 1 | 0 | 37
38908.5462 | 1 | 0 | 37
38908.5469 | 1 | 0 | 37
38908.5476 | 1 | 0 | 37
38908.5483 | 1 | 0 | 37
38908.549 | 1 | 0 | 37
38908.5497 | 1 | 0 | 37
38908.5503 | 1 | 0 | 37
38908.551 | 1 | 0 | 37
38908.5517 | 1 | 0 | 37
38908.5524 | 1 | 0 | 37
38908.553 | 21 | 20 | 37
38908.5537 | 1199 | 1185 | 37
38908.5544 | 1088 | 1060 | 37
38908.5551 | 1146 | 1087 | 37
38908.5558 | 1192 | 917 | 37
38908.5564 | 2429 | 10 | 37
38908.5571 | 2037 | 15 | 37
38908.5578 | 1891 | 589 | 37
38908.5585 | 2454 | 8 | 37
38908.5592 | 2285 | 1 | 37
38908.5598 | 2016 | 1 | 37
38908.5605 | 2239 | 3 | 37
38908.5612 | 2053 | 9 | 37
38908.5619 | 2075 | 73 | 37
38908.5626 | 2123 | 50 | 37
38908.5388 | 1 | 0 | 38
38908.5395 | 1 | 0 | 38
38908.5401 | 1 | 0 | 38
38908.5408 | 1 | 0 | 38
38908.5415 | 1 | 0 | 38
38908.5422 | 1 | 0 | 38
38908.5429 | 1 | 0 | 38
38908.5435 | 1 | 0 | 38
38908.5442 | 1 | 0 | 38
38908.5449 | 1 | 0 | 38
38908.5456 | 1 | 0 | 38
38908.5463 | 1 | 0 | 38
38908.5469 | 1 | 0 | 38
38908.5476 | 1 | 0 | 38
38908.5483 | 1 | 0 | 38
38908.549 | 1 | 0 | 38
38908.5497 | 1 | 0 | 38
38908.5503 | 1 | 0 | 38
38908.551 | 1 | 1 | 38
38908.5517 | 1 | 0 | 38
38908.5524 | 2 | 1 | 38
38908.5531 | 2 | 1 | 38
38908.5537 | 1193 | 1198 | 38
38908.5544 | 927 | 1029 | 38
38908.5551 | 1143 | 1160 | 38
38908.5558 | 1228 | 932 | 38
38908.5565 | 2026 | 9 | 38
38908.5572 | 2159 | 20 | 38
38908.5578 | 1741 | 629 | 38
38908.5585 | 2220 | 7 | 38
38908.5592 | 2222 | 1 | 38
38908.5599 | 2334 | 2 | 38
38908.5606 | 2192 | 2 | 38
38908.5612 | 2123 | 10 | 38
38908.5619 | 2147 | 76 | 38
38908.5626 | 2122 | 47 | 38
38908.5388 | 1 | 0 | 39
38908.5395 | 1 | 0 | 39
38908.5402 | 1 | 0 | 39
38908.5408 | 1 | 0 | 39
38908.5415 | 2 | 0 | 39
38908.5422 | 1 | 0 | 39
38908.5429 | 1 | 0 | 39
38908.5436 | 1 | 0 | 39
38908.5442 | 2 | 0 | 39
38908.5449 | 1 | 0 | 39
38908.5456 | 1 | 0 | 39
38908.5463 | 1 | 0 | 39
38908.547 | 1 | 0 | 39
38908.5476 | 1 | 0 | 39
38908.5483 | 1 | 0 | 39
38908.549 | 1 | 0 | 39
38908.5497 | 1 | 0 | 39
38908.5504 | 1 | 0 | 39
38908.551 | 1 | 0 | 39
38908.5517 | 1 | 0 | 39
38908.5524 | 1 | 0 | 39
38908.5531 | 1 | 0 | 39
38908.5538 | 3 | 7 | 39
38908.5544 | 1159 | 1129 | 39
38908.5551 | 995 | 938 | 39
38908.5558 | 1116 | 955 | 39
38908.5565 | 2021 | 9 | 39
38908.5572 | 2187 | 21 | 39
38908.5578 | 1936 | 653 | 39
38908.5585 | 2345 | 7 | 39
38908.5592 | 1936 | 2 | 39
38908.5599 | 2417 | 2 | 39
38908.5606 | 2241 | 3 | 39
38908.5612 | 2268 | 11 | 39
38908.5619 | 2159 | 128 | 39
38908.5626 | 1844 | 42 | 39
38908.5388 | 1 | 0 | 40
38908.5395 | 1 | 0 | 40
38908.5402 | 1 | 0 | 40
38908.5408 | 1 | 0 | 40
38908.5415 | 1 | 0 | 40
38908.5422 | 1 | 0 | 40
38908.5429 | 1 | 0 | 40
38908.5436 | 1 | 0 | 40
38908.5442 | 1 | 0 | 40
38908.5449 | 1 | 0 | 40
38908.5456 | 1 | 0 | 40
38908.5463 | 1 | 0 | 40
38908.547 | 1 | 0 | 40
38908.5477 | 1 | 0 | 40
38908.5483 | 1 | 0 | 40
38908.549 | 1 | 0 | 40
38908.5497 | 1 | 0 | 40
38908.5504 | 1 | 0 | 40
38908.5511 | 1 | 0 | 40
38908.5517 | 1 | 0 | 40
38908.5524 | 1 | 0 | 40
38908.5531 | 1 | 0 | 40
38908.5538 | 3 | 5 | 40
38908.5545 | 1146 | 1138 | 40
38908.5551 | 1037 | 974 | 40
38908.5558 | 1338 | 1026 | 40
38908.5565 | 2286 | 10 | 40
38908.5572 | 2162 | 22 | 40
38908.5579 | 1617 | 600 | 40
38908.5585 | 2271 | 6 | 40
38908.5592 | 1944 | 1 | 40
38908.5599 | 2011 | 2 | 40
38908.5606 | 2459 | 3 | 40
38908.5613 | 2376 | 10 | 40
38908.5619 | 1827 | 132 | 40
38908.5626 | 2358 | 42 | 40
38908.5388 | 1 | 0 | 41
38908.5395 | 1 | 0 | 41
38908.5402 | 1 | 0 | 41
38908.5409 | 1 | 0 | 41
38908.5416 | 1 | 0 | 41
38908.5422 | 1 | 0 | 41
38908.5429 | 1 | 0 | 41
38908.5436 | 1 | 0 | 41
38908.5443 | 1 | 0 | 41
38908.545 | 1 | 0 | 41
38908.5456 | 1 | 0 | 41
38908.5463 | 1 | 0 | 41
38908.547 | 1 | 0 | 41
38908.5477 | 1 | 0 | 41
38908.5484 | 1 | 0 | 41
38908.549 | 1 | 0 | 41
38908.5497 | 1 | 0 | 41
38908.5504 | 1 | 0 | 41
38908.5511 | 1 | 0 | 41
38908.5517 | 1 | 0 | 41
38908.5524 | 1 | 0 | 41
38908.5531 | 1 | 0 | 41
38908.5538 | 2 | 4 | 41
38908.5545 | 548 | 529 | 41
38908.5552 | 1092 | 1026 | 41
38908.5558 | 1363 | 797 | 41
38908.5565 | 2308 | 13 | 41
38908.5572 | 1989 | 28 | 41
38908.5579 | 1705 | 623 | 41
38908.5586 | 1904 | 6 | 41
38908.5592 | 2170 | 2 | 41
38908.5599 | 1909 | 1 | 41
38908.5606 | 2232 | 3 | 41
38908.5613 | 2417 | 11 | 41
38908.562 | 1930 | 176 | 41
38908.5626 | 2239 | 56 | 41
38908.5388 | 1 | 0 | 42
38908.5395 | 1 | 0 | 42
38908.5402 | 1 | 0 | 42
38908.5409 | 1 | 1 | 42
38908.5416 | 1 | 0 | 42
38908.5422 | 1 | 1 | 42
38908.5429 | 1 | 0 | 42
38908.5436 | 1 | 0 | 42
38908.5443 | 1 | 0 | 42
38908.545 | 1 | 0 | 42
38908.5456 | 1 | 0 | 42
38908.5463 | 1 | 0 | 42
38908.547 | 1 | 0 | 42
38908.5484 | 1 | 0 | 42
38908.5491 | 1 | 0 | 42
38908.5497 | 1 | 0 | 42
38908.5504 | 1 | 0 | 42
38908.5511 | 1 | 0 | 42
38908.5518 | 1 | 0 | 42
38908.5525 | 1 | 0 | 42
38908.5531 | 1 | 0 | 42
38908.5538 | 1 | 4 | 42
38908.5545 | 973 | 937 | 42
38908.5552 | 1131 | 1137 | 42
38908.5559 | 1202 | 880 | 42
38908.5565 | 2362 | 13 | 42
38908.5572 | 1864 | 28 | 42
38908.5579 | 1703 | 650 | 42
38908.5586 | 2070 | 6 | 42
38908.5593 | 2341 | 1 | 42
38908.5599 | 2331 | 2 | 42
38908.5606 | 2145 | 3 | 42
38908.5613 | 2077 | 12 | 42
38908.562 | 2012 | 207 | 42
38908.5627 | 1836 | 44 | 42