## Test Facts
Last row in IRMS data sheets: | 47
Time when Penlight power was initiated: | 73

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 14
Test conditions: Cable: 7-conductor, 12 AWG, PE insulated, PVC jacketed, industrial grade control cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 300C, nominal 6.1 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 73 seconds of baseline data monitoring. Special Note: Test setup included a thermocouple on the inner surface of one center tray rung during Penlight Test 14.
DAQ Time | Penlight Time | Event | Interpretation
73 | 0 | Initated Penlight Heating
1537 | 1464 | Conductor 1 shorts to ground at less than 1000 ohms (836) | Initial failure is by shorting to ground
1544 | 1471 | Conductor 1 shorts to conductor 7 at less than 100 ohms (16) | Initial conductor-to-conductor short
1687 | 1614 | Conductor 7 shorts to ground at less than 1000 ohms (764)
1779 | 1706 | The short between conductors 1 & 7 begin to "heal" and IR increases (166)
2438 | 2365 | Conductor 3 shorts to ground at less than 100 ohms (66)
2450 | 2377 | Conductor 3 shorts to conductor 7 at less than 100 ohms (65)
Additional Observations
Observation 1 | The progression of failure modes for this cable followed that expected for a typical thermoplastic-insulated cable: shorting to ground followed by conductor-to-conductor shorts.
Observation 2 | It took 1464 s (24.4 min.) from the start of Penlight heating for the first short to ground to occur, and it took 1471 s (24.5 min.) for the first conductor-to-conductor short.
Observation 3 | There was very little evidence of failure at this low heat flux.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 14 |  |  | 2006-07-11 | 10:23
PE | 7-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-64.9167 | 211202 |  | -53.25 | 211202 | -45.25 | 211202 | -40.25 | 211202 | -36.9167 | 211202 | -34.5 | 211202 | -32.25 | 211202 | -64.9167 | 211202
-6.0833 | 211202 |  | 5.5833 | 211202 | 13.4167 | 211202 | 18.5833 | 211202 | 22 | 211202 | 24.25 | 211202 | 26.5833 | 211202 | -6.0833 | 211202
52.6667 | 211202 |  | 64.3333 | 211202 | 72.3333 | 211202 | 77.5 | 211202 | 80.6667 | 211202 | 83 | 211202 | 85.3333 | 211202 | 52.6667 | 211202
111.5 | 211202 |  | 123.1667 | 211202 | 131.1667 | 211202 | 136.25 | 211202 | 139.5 | 211202 | 141.8333 | 211202 | 144.0833 | 211202 | 111.5 | 211202
170.3333 | 211202 |  | 182 | 211202 | 189.8333 | 211202 | 195.0833 | 211202 | 198.25 | 211202 | 200.5833 | 211202 | 203.0833 | 211202 | 170.3333 | 211202
229.0833 | 211202 |  | 240.75 | 211202 | 248.75 | 211202 | 253.75 | 211202 | 257 | 211202 | 259.5 | 211202 | 261.6667 | 211202 | 229.0833 | 211202
287.9167 | 211202 |  | 299.5 | 211202 | 307.4167 | 105551 | 312.5833 | 211202 | 316 | 211202 | 318.25 | 211202 | 320.5 | 211202 | 287.9167 | 105551
346.6667 | 211202 |  | 358.25 | 211202 | 366.3333 | 211202 | 371.5 | 211202 | 374.5833 | 211202 | 376.9167 | 211202 | 379.25 | 211202 | 346.6667 | 211202
405.5 | 211202 |  | 417.1667 | 211202 | 425.0833 | 211202 | 430.1667 | 211202 | 433.4167 | 211202 | 435.75 | 211202 | 438.0833 | 211202 | 405.5 | 211202
464.25 | 211202 |  | 475.9167 | 211202 | 483.8333 | 211202 | 489 | 211202 | 492.1667 | 211202 | 494.5 | 211202 | 496.8333 | 211202 | 464.25 | 211202
523 | 211202 |  | 534.6667 | 211202 | 542.5 | 211202 | 547.5833 | 211202 | 551.0833 | 211202 | 553.3333 | 211202 | 555.6667 | 211202 | 523 | 211202
581.75 | 211202 |  | 593.5 | 211202 | 601.3333 | 211202 | 606.5 | 211202 | 609.9167 | 211202 | 612.1667 | 211202 | 614.5 | 211202 | 581.75 | 211202
640.5833 | 211202 |  | 652.25 | 211202 | 660.1667 | 211202 | 665.25 | 211202 | 668.5833 | 211202 | 671 | 211202 | 673.1667 | 211202 | 640.5833 | 211202
699.3333 | 211202 |  | 711.0833 | 211202 | 718.8333 | 211202 | 724.1667 | 211202 | 727.3333 | 211202 | 729.6667 | 211202 | 732.0833 | 211202 | 699.3333 | 211202
758.1667 | 211202 |  | 769.8333 | 211202 | 777.8333 | 211202 | 782.75 | 211202 | 786.1667 | 211202 | 788.5833 | 211202 | 790.8333 | 211202 | 758.1667 | 211202
816.9167 | 211202 |  | 828.6667 | 211202 | 836.5 | 211202 | 841.5833 | 211202 | 845.0833 | 211202 | 847.25 | 211202 | 849.6667 | 105551 | 816.9167 | 105551
875.6667 | 211202 |  | 887.4167 | 211202 | 895.3333 | 105551 | 900.5 | 211202 | 903.75 | 211202 | 906.0833 | 211202 | 908.4167 | 211202 | 875.6667 | 105551
934.5 | 211202 |  | 946.25 | 211202 | 954.1667 | 211202 | 959.25 | 211202 | 962.5833 | 211202 | 964.9167 | 105551 | 967.1667 | 211202 | 934.5 | 105551
993.3333 | 211202 |  | 1005.0833 | 211202 | 1012.8333 | 211202 | 1018.0833 | 211202 | 1021.3333 | 211202 | 1023.5833 | 211202 | 1026.0833 | 211202 | 993.3333 | 211202
1052.0833 | 211202 |  | 1063.75 | 211202 | 1071.75 | 211202 | 1076.75 | 211202 | 1080.0833 | 211202 | 1082.5 | 211202 | 1084.75 | 211202 | 1052.0833 | 211202
1110.9167 | 211202 |  | 1122.5833 | 105551 | 1130.4167 | 105551 | 1135.5833 | 211202 | 1139 | 211202 | 1141.25 | 211202 | 1143.5833 | 211202 | 1110.9167 | 105551
1169.6667 | 211202 |  | 1181.3333 | 211202 | 1189.3333 | 211202 | 1194.5 | 211202 | 1197.6667 | 211202 | 1200 | 211202 | 1202.3333 | 211202 | 1169.6667 | 211202
1228.5 | 211202 |  | 1240.1667 | 105551 | 1248.1667 | 211202 | 1253.25 | 211202 | 1256.5 | 211202 | 1258.8333 | 211202 | 1261.0833 | 211202 | 1228.5 | 105551
1287.3333 | 211202 |  | 1299 | 211202 | 1306.8333 | 211202 | 1312.0833 | 211202 | 1315.25 | 211202 | 1317.5833 | 211202 | 1320.0833 | 211202 | 1287.3333 | 211202
1346.0833 | 211202 |  | 1357.75 | 211202 | 1365.75 | 211202 | 1370.75 | 211202 | 1374.0833 | 211202 | 1376.5 | 211202 | 1378.75 | 211202 | 1346.0833 | 211202
1404.9167 | 211202 |  | 1416.5833 | 211202 | 1424.4167 | 211202 | 1429.5833 | 211202 | 1433 | 211202 | 1435.25 | 211202 | 1437.5833 | 211202 | 1404.9167 | 211202
1463.6667 | 835.8659 |  | 1475.3333 | 23529.5845 | 1483.3333 | 35392.6263 | 1488.5 | 70645.6571 | 1491.6667 | 211202 | 1494 | 211202 | 1496.3333 | 1260.2533 | 1463.6667 | 835.8659
1522.5 | 2260.2646 |  | 1534.1667 | 23545.7162 | 1542.1667 | 30323.0074 | 1547.25 | 105851.38 | 1550.5 | 211202 | 1552.8333 | 211202 | 1555.0833 | 7278.731 | 1522.5 | 2260.2646
1581.3333 | 614.7555 |  | 1592.9167 | 35255.5886 | 1600.8333 | 53013.6466 | 1606.0833 | 105851.38 | 1609.25 | 105751 | 1611.5833 | 211202 | 1614 | 764.1215 | 1581.3333 | 614.7555
1640.0833 | 142.6185 |  | 1651.75 | 23529.6076 | 1659.6667 | 35384.1753 | 1664.6667 | 70645.6571 | 1668 | 211201.9053 | 1670.5 | 211101.9527 | 1672.6667 | 123.1137 | 1640.0833 | 123.1137
1698.8333 | 7878.2186 |  | 1710.5 | 211202 | 1718.4167 | 211201.9052 | 1723.5833 | 211202 | 1726.8333 | 211202 | 1729.1667 | 211202 | 1731.5 | 86253.8695 | 1698.8333 | 7878.2186
1757.5833 | 211202 |  | 1769.25 | 211202 | 1777.25 | 211202 | 1782.4167 | 211202 | 1785.5833 | 105551 | 1788 | 211202 | 1790.25 | 211202 | 1757.5833 | 105551
1816.5 | 5393.2281 |  | 1828.0833 | 211101.9527 | 1836.0833 | 211201.9052 | 1841.25 | 211202 | 1844.4167 | 211202 | 1846.75 | 211202 | 1849.0833 | 3059.6164 | 1816.5 | 3059.6164
1875.1667 | 211202 |  | 1886.8333 | 211202 | 1894.75 | 211202 | 1899.9167 | 211202 | 1903.1667 | 211202 | 1905.5833 | 211202 | 1907.9167 | 211202 | 1875.1667 | 211202
1933.9167 | 211202 |  | 1945.75 | 211202 | 1953.5833 | 211202 | 1958.5833 | 211202 | 1962.0833 | 211202 | 1964.3333 | 211202 | 1966.75 | 211202 | 1933.9167 | 211202
1992.6667 | 55481.0209 |  | 2004.4167 | 35191.7926 | 2012.4167 | 211202 | 2017.5 | 211101.9527 | 2020.75 | 211202 | 2023.1667 | 211202 | 2025.4167 | 19903.1445 | 1992.6667 | 19903.1445
2051.5 | 211202 |  | 2063.25 | 105551 | 2071.25 | 211202 | 2076.3333 | 211202 | 2079.5833 | 211202 | 2081.8333 | 211202 | 2084.25 | 211202 | 2051.5 | 105551
2110.3333 | 211202 |  | 2122.0833 | 211202 | 2129.9167 | 211202 | 2135.0833 | 211202 | 2138.3333 | 211202 | 2140.6667 | 211202 | 2143.0833 | 211202 | 2110.3333 | 211202
2169.1667 | 211202 |  | 2180.8333 | 211202 | 2188.75 | 211202 | 2193.75 | 211202 | 2197.0833 | 211202 | 2199.5 | 211202 | 2201.9167 | 211202 | 2169.1667 | 211202
2228 | 211202 |  | 2239.5833 | 211202 | 2247.5833 | 211202 | 2252.6667 | 211202 | 2256 | 211202 | 2258.25 | 211202 | 2260.5833 | 211202 | 2228 | 211202
2286.8333 | 211202 |  | 2298.3333 | 211202 | 2306.4167 | 211202 | 2311.5 | 211202 | 2314.75 | 211202 | 2317.0833 | 211202 | 2319.4167 | 211202 | 2286.8333 | 211202
2345.5 | 211202 |  | 2357.1667 | 211202 | 2365.1667 | 66.2486 | 2370.25 | 211202 | 2373.5 | 211202 | 2375.8333 | 211202 | 2378.0833 | 105551 | 2345.5 | 66.2486

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 14 |  |  | 2006-07-11 | 10:23
PE | 7-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-64.9167 | 211202 |  | -53.25 | 211202 | -45.25 | 211202 | -40.25 | 211202 | -36.9167 | 211202 | -34.5 | 211202 | -32.25 | 211202 | -64.9167 | 211202
-6.0833 | 211202 |  | 5.5833 | 211202 | 13.4167 | 211202 | 18.5833 | 211202 | 22 | 211202 | 24.25 | 211202 | 26.5833 | 211202 | -6.0833 | 211202
52.6667 | 211202 |  | 64.3333 | 211202 | 72.3333 | 211202 | 77.5 | 211202 | 80.6667 | 211202 | 83 | 211202 | 85.3333 | 211202 | 52.6667 | 211202
111.5 | 211202 |  | 123.1667 | 211202 | 131.1667 | 211202 | 136.25 | 211202 | 139.5 | 211202 | 141.8333 | 211202 | 144.0833 | 211202 | 111.5 | 211202
170.3333 | 211202 |  | 182 | 211202 | 189.8333 | 211202 | 195.0833 | 211202 | 198.25 | 211202 | 200.5833 | 211202 | 203.0833 | 211202 | 170.3333 | 211202
229.0833 | 211202 |  | 240.75 | 211202 | 248.75 | 211202 | 253.75 | 211202 | 257 | 211202 | 259.5 | 211202 | 261.6667 | 211202 | 229.0833 | 211202
287.9167 | 211202 |  | 299.5 | 211202 | 307.4167 | 193593.5 | 312.5833 | 211202 | 316 | 211202 | 318.25 | 211202 | 320.5 | 211202 | 287.9167 | 193593.5
346.6667 | 211202 |  | 358.25 | 211202 | 366.3333 | 211202 | 371.5 | 211202 | 374.5833 | 211202 | 376.9167 | 211202 | 379.25 | 211202 | 346.6667 | 211202
405.5 | 211202 |  | 417.1667 | 211202 | 425.0833 | 211202 | 430.1667 | 211202 | 433.4167 | 211202 | 435.75 | 211202 | 438.0833 | 211202 | 405.5 | 211202
464.25 | 211202 |  | 475.9167 | 211202 | 483.8333 | 211202 | 489 | 211202 | 492.1667 | 211202 | 494.5 | 211202 | 496.8333 | 211202 | 464.25 | 211202
523 | 211202 |  | 534.6667 | 211202 | 542.5 | 211202 | 547.5833 | 211202 | 551.0833 | 211202 | 553.3333 | 211202 | 555.6667 | 211202 | 523 | 211202
581.75 | 211202 |  | 593.5 | 211202 | 601.3333 | 211202 | 606.5 | 211202 | 609.9167 | 211202 | 612.1667 | 211202 | 614.5 | 211202 | 581.75 | 211202
640.5833 | 211202 |  | 652.25 | 211202 | 660.1667 | 211202 | 665.25 | 211202 | 668.5833 | 211202 | 671 | 211202 | 673.1667 | 211202 | 640.5833 | 211202
699.3333 | 211202 |  | 711.0833 | 211202 | 718.8333 | 211202 | 724.1667 | 211202 | 727.3333 | 211202 | 729.6667 | 211202 | 732.0833 | 211202 | 699.3333 | 211202
758.1667 | 211202 |  | 769.8333 | 74519809.6733 | 777.8333 | 211202 | 782.75 | 211202 | 786.1667 | 211202 | 788.5833 | 211202 | 790.8333 | 211202 | 758.1667 | 211202
816.9167 | 211202 |  | 828.6667 | 74519809.6733 | 836.5 | 211202 | 841.5833 | 211202 | 845.0833 | 211202 | 847.25 | 211202 | 849.6667 | 193593.5 | 816.9167 | 193593.5
875.6667 | 211202 |  | 887.4167 | 211202 | 895.3333 | 193593.5 | 900.5 | 211202 | 903.75 | 211202 | 906.0833 | 211202 | 908.4167 | 211202 | 875.6667 | 193593.5
934.5 | 74519809.6733 |  | 946.25 | 74519809.6733 | 954.1667 | 211202 | 959.25 | 211202 | 962.5833 | 211202 | 964.9167 | 193593.5 | 967.1667 | 211202 | 934.5 | 193593.5
993.3333 | 211202 |  | 1005.0833 | 211202 | 1012.8333 | 211202 | 1018.0833 | 211202 | 1021.3333 | 211202 | 1023.5833 | 211202 | 1026.0833 | 211202 | 993.3333 | 211202
1052.0833 | 211202 |  | 1063.75 | 211202 | 1071.75 | 211202 | 1076.75 | 211202 | 1080.0833 | 211202 | 1082.5 | 211202 | 1084.75 | 211202 | 1052.0833 | 211202
1110.9167 | 211202 |  | 1122.5833 | 193593.5 | 1130.4167 | 193593.5 | 1135.5833 | 211202 | 1139 | 211202 | 1141.25 | 211202 | 1143.5833 | 211202 | 1110.9167 | 193593.5
1169.6667 | 211202 |  | 1181.3333 | 211202 | 1189.3333 | 211202 | 1194.5 | 211202 | 1197.6667 | 211202 | 1200 | 211202 | 1202.3333 | 211202 | 1169.6667 | 211202
1228.5 | 211202 |  | 1240.1667 | 193593.5 | 1248.1667 | 211202 | 1253.25 | 211202 | 1256.5 | 211202 | 1258.8333 | 211202 | 1261.0833 | 211202 | 1228.5 | 193593.5
1287.3333 | 211202 |  | 1299 | 211202 | 1306.8333 | 211202 | 1312.0833 | 211202 | 1315.25 | 211202 | 1317.5833 | 211202 | 1320.0833 | 211202 | 1287.3333 | 211202
1346.0833 | 211202 |  | 1357.75 | 211202 | 1365.75 | 211202 | 1370.75 | 211202 | 1374.0833 | 211202 | 1376.5 | 211202 | 1378.75 | 211202 | 1346.0833 | 211202
1404.9167 | 211202 |  | 1416.5833 | 211202 | 1424.4167 | 211202 | 1429.5833 | 211202 | 1433 | 211202 | 1435.25 | 211202 | 1437.5833 | 211202 | 1404.9167 | 211202
1463.6667 | 176140.9776 |  | 1475.3333 | 74442772.7784 | 1483.3333 | 74490508.1111 | 1488.5 | 187775.9429 | 1491.6667 | 211268.7616 | 1494 | 74484592.7479 | 1496.3333 | 176211.7089 | 1463.6667 | 176140.9776
1522.5 | 176378.3774 |  | 1534.1667 | 74465046.2881 | 1542.1667 | 223106878.5212 | 1547.25 | 193643.5633 | 1550.5 | 37312663.6711 | 1552.8333 | 211202 | 1555.0833 | 74450605.5364 | 1522.5 | 176378.3774
1581.3333 | 176104.1259 |  | 1592.9167 | 140848.4821 | 1600.8333 | 148802052.6211 | 1606.0833 | 193643.5633 | 1609.25 | 193626.8333 | 1611.5833 | 211202 | 1614 | 176129.0202 | 1581.3333 | 140848.4821
1640.0833 | 176025.4364 |  | 1651.75 | 74425197.6787 | 1659.6667 | 148799114.3759 | 1664.6667 | 148804991.2895 | 1668 | 211201.9842 | 1670.5 | 211185.3254 | 1672.6667 | 176022.1856 | 1640.0833 | 176022.1856
1698.8333 | 177314.7031 |  | 1710.5 | 211235.3808 | 1718.4167 | 211201.9842 | 1723.5833 | 211202 | 1726.8333 | 211202 | 1729.1667 | 211202 | 1731.5 | 190377.3116 | 1698.8333 | 177314.7031
1757.5833 | 211202 |  | 1769.25 | 211202 | 1777.25 | 74519809.6733 | 1782.4167 | 211202 | 1785.5833 | 193593.5 | 1788 | 211202 | 1790.25 | 211202 | 1757.5833 | 193593.5
1816.5 | 176900.538 |  | 1828.0833 | 148828434.0529 | 1836.0833 | 211201.9842 | 1841.25 | 74484592.7479 | 1844.4167 | 211202 | 1846.75 | 211202 | 1849.0833 | 176511.6027 | 1816.5 | 176511.6027
1875.1667 | 74519809.6733 |  | 1886.8333 | 211202 | 1894.75 | 211202 | 1899.9167 | 211202 | 1903.1667 | 211202 | 1905.5833 | 211202 | 1907.9167 | 211202 | 1875.1667 | 211202
1933.9167 | 211202 |  | 1945.75 | 211202 | 1953.5833 | 211202 | 1958.5833 | 211202 | 1962.0833 | 211202 | 1964.3333 | 211202 | 1966.75 | 211202 | 1933.9167 | 211202
1992.6667 | 185248.5035 |  | 2004.4167 | 223072472.9854 | 2012.4167 | 74520095.5162 | 2017.5 | 211185.3254 | 2020.75 | 211202 | 2023.1667 | 211202 | 2025.4167 | 179318.8574 | 1992.6667 | 179318.8574
2051.5 | 211202 |  | 2063.25 | 74502201.1733 | 2071.25 | 211202 | 2076.3333 | 211202 | 2079.5833 | 211202 | 2081.8333 | 211202 | 2084.25 | 211202 | 2051.5 | 211202
2110.3333 | 211202 |  | 2122.0833 | 211202 | 2129.9167 | 211202 | 2135.0833 | 211202 | 2138.3333 | 211202 | 2140.6667 | 211202 | 2143.0833 | 211202 | 2110.3333 | 211202
2169.1667 | 211202 |  | 2180.8333 | 211202 | 2188.75 | 211202 | 2193.75 | 211202 | 2197.0833 | 211202 | 2199.5 | 211202 | 2201.9167 | 211202 | 2169.1667 | 211202
2228 | 74519809.6733 |  | 2239.5833 | 211202 | 2247.5833 | 211202 | 2252.6667 | 211202 | 2256 | 211202 | 2258.25 | 211202 | 2260.5833 | 211202 | 2228 | 211202
2286.8333 | 211202 |  | 2298.3333 | 211202 | 2306.4167 | 211202 | 2311.5 | 211202 | 2314.75 | 211202 | 2317.0833 | 211202 | 2319.4167 | 211202 | 2286.8333 | 211202
2345.5 | 211202 |  | 2357.1667 | 211202 | 2365.1667 | 142996.7706 | 2370.25 | 211202 | 2373.5 | 211202 | 2375.8333 | 211202 | 2378.0833 | 193593.5 | 2345.5 | 142996.7706

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 14 |  |  | 2006-07-11 | 10:23
PE | 7-C | Tray
300 C | 6.1 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-72 | 211201.9994 | -69 | 211201.9994 | -66.5 | 211201.9994 | -63.5 | 211201.9994 | -60.5 | 211201.9994 | -58 | 211201.9994 | -55 | 211201.9994 | -52.5 | 211201.9994 | -49.5 | 211201.9994 | -46.5 | 211201.9994 | -44 | 211201.9994 | -41 | 211201.9994 | -38.5 | 211201.9994 | -35.5 | 211201.9994 | -32.5 | 211201.9994 | -30 | 211201.9994 | -27 | 211201.9994 | -24.5 | 211201.9994 | -21.5 | 211201.9994 | -18.5 | 211201.9994 | -16 | 211201.9994 | -72 | 211201.9994
-13 | 211201.9994 | -10.5 | 211201.9994 | -7.5 | 211201.9994 | -4.5 | 211201.9994 | -2 | 211201.9994 | 1 | 211201.9994 | 3.5 | 211201.9994 | 6.5 | 211201.9994 | 9.5 | 211201.9994 | 12 | 211201.9994 | 15 | 211201.9994 | 17.5 | 211201.9994 | 20.5 | 211201.9994 | 23.5 | 211201.9994 | 26 | 211201.9994 | 29 | 211201.9994 | 31.5 | 211201.9994 | 34.5 | 211201.9994 | 37.5 | 211201.9994 | 40 | 211201.9994 | 43 | 211201.9994 | -13 | 211201.9994
45.5 | 211201.9994 | 48.5 | 211201.9994 | 51.5 | 211201.9994 | 54 | 211201.9994 | 57 | 211201.9994 | 59.5 | 211201.9994 | 62.5 | 211201.9994 | 65.5 | 211201.9994 | 68 | 211201.9994 | 71 | 211201.9994 | 73.5 | 211201.9994 | 76.5 | 211201.9994 | 79.5 | 211201.9994 | 82 | 211201.9994 | 85 | 211201.9994 | 87.5 | 211201.9994 | 90.5 | 211201.9994 | 93.5 | 211201.9994 | 96 | 211201.9994 | 99 | 211201.9994 | 101.5 | 211201.9994 | 45.5 | 211201.9994
104.5 | 211201.9994 | 107.5 | 211201.9994 | 110 | 211201.9994 | 113 | 211201.9994 | 115.5 | 211201.9994 | 118.5 | 211201.9994 | 121.5 | 211201.9994 | 124 | 211201.9994 | 127 | 211201.9994 | 129.5 | 211201.9994 | 132.5 | 211201.9994 | 135.5 | 211201.9994 | 138 | 211201.9994 | 141 | 211201.9994 | 143.5 | 211201.9994 | 146.5 | 211201.9994 | 149.5 | 211201.9994 | 152 | 211201.9994 | 155 | 211201.9994 | 157.5 | 211201.9994 | 160.5 | 211201.9994 | 104.5 | 211201.9994
163.5 | 211201.9994 | 166 | 211201.9994 | 169 | 211201.9994 | 171.5 | 211201.9994 | 174.5 | 211201.9994 | 177.5 | 211201.9994 | 180 | 211201.9994 | 183 | 211201.9994 | 185.5 | 211201.9994 | 188.5 | 211201.9994 | 191.5 | 211201.9994 | 194 | 211201.9994 | 197 | 211201.9994 | 199.5 | 211201.9994 | 202.5 | 211201.9994 | 205.5 | 211201.9994 | 208 | 211201.9994 | 211 | 211201.9994 | 213.5 | 211201.9994 | 216.5 | 211201.9994 | 219.5 | 211201.9994 | 163.5 | 211201.9994
222 | 211201.9994 | 225 | 211201.9994 | 227.5 | 211201.9994 | 230.5 | 211201.9994 | 233.5 | 211201.9994 | 236 | 211201.9994 | 239 | 211201.9994 | 241.5 | 211201.9994 | 244.5 | 211201.9994 | 247.5 | 211201.9994 | 250 | 211201.9994 | 253 | 211201.9994 | 255.5 | 211201.9994 | 258.5 | 211201.9994 | 261.5 | 211201.9994 | 264 | 211201.9994 | 267 | 211201.9994 | 269.5 | 211201.9994 | 272.5 | 211201.9994 | 275 | 211201.9994 | 278 | 211201.9994 | 222 | 211201.9994
281 | 211201.9994 | 283.5 | 211201.9994 | 286.5 | 211201.9994 | 289.5 | 211201.9994 | 292 | 211201.9994 | 295 | 211201.9994 | 297.5 | 211201.9994 | 300.5 | 211201.9994 | 303.5 | 211201.9994 | 306 | 211201.9994 | 308.5 | 211201.9994 | 311.5 | 211201.9994 | 314.5 | 211201.9994 | 317.5 | 211201.9994 | 320 | 105550.9988 | 323 | 211201.9994 | 325.5 | 211201.9994 | 328.5 | 211201.9994 | 331.5 | 211201.9994 | 334 | 211201.9994 | 337 | 211201.9994 | 281 | 105550.9988
339.5 | 211201.9994 | 342.5 | 211201.9994 | 345.5 | 211201.9994 | 348 | 211201.9994 | 351 | 211201.9994 | 353.5 | 211201.9994 | 356.5 | 211201.9994 | 359.5 | 211201.9994 | 362 | 211201.9994 | 364.5 | 211201.9994 | 367.5 | 211201.9994 | 370.5 | 211201.9994 | 373.5 | 211201.9994 | 376 | 211201.9994 | 379 | 211201.9994 | 381.5 | 211201.9994 | 384.5 | 211201.9994 | 387.5 | 211201.9994 | 390 | 211201.9994 | 392.5 | 211201.9994 | 395.5 | 211201.9994 | 339.5 | 211201.9994
398.5 | 211201.9994 | 401.5 | 211201.9994 | 404 | 211201.9994 | 407 | 211201.9994 | 409.5 | 211201.9994 | 412.5 | 211201.9994 | 415.5 | 211201.9994 | 418 | 211201.9994 | 421 | 211201.9994 | 423.5 | 211201.9994 | 426.5 | 211201.9994 | 429 | 211201.9994 | 432 | 211201.9994 | 435 | 211201.9994 | 437.5 | 211201.9994 | 440.5 | 211201.9994 | 443.5 | 211201.9994 | 446 | 211201.9994 | 448.5 | 211201.9994 | 451.5 | 211201.9994 | 454.5 | 211201.9994 | 398.5 | 211201.9994
457.5 | 211201.9994 | 460 | 211201.9994 | 463 | 211201.9994 | 465.5 | 211201.9994 | 468.5 | 211201.9994 | 471 | 211201.9994 | 474 | 211201.9994 | 477 | 211201.9994 | 479.5 | 211201.9994 | 482.5 | 211201.9994 | 485 | 211201.9994 | 488 | 211201.9994 | 491 | 211201.9994 | 493.5 | 211201.9994 | 496.5 | 211201.9994 | 499 | 211201.9994 | 502 | 211201.9994 | 505 | 211201.9994 | 507.5 | 211201.9994 | 510.5 | 211201.9994 | 513 | 211201.9994 | 457.5 | 211201.9994
516 | 211201.9994 | 519 | 211201.9994 | 521.5 | 211201.9994 | 524.5 | 211201.9994 | 527 | 211201.9994 | 530 | 211201.9994 | 532.5 | 211201.9994 | 535.5 | 211201.9994 | 538.5 | 211201.9994 | 541.5 | 211201.9994 | 544 | 211201.9994 | 546.5 | 211201.9994 | 549.5 | 211201.9994 | 552.5 | 211201.9994 | 555 | 211201.9994 | 558 | 211201.9994 | 560.5 | 211201.9994 | 563.5 | 211201.9994 | 566.5 | 211201.9994 | 569.5 | 211201.9994 | 572 | 211201.9994 | 516 | 211201.9994
574.5 | 211201.9994 | 577.5 | 211201.9994 | 580.5 | 211201.9994 | 583.5 | 211201.9994 | 586 | 211201.9994 | 588.5 | 211201.9994 | 591.5 | 211201.9994 | 594.5 | 211201.9994 | 597.5 | 211201.9994 | 600 | 211201.9994 | 603 | 211201.9994 | 605.5 | 211201.9994 | 608.5 | 211201.9994 | 611 | 211201.9994 | 614 | 211201.9994 | 616.5 | 211201.9994 | 619.5 | 211201.9994 | 622.5 | 211201.9994 | 625.5 | 211201.9994 | 628 | 211201.9994 | 631 | 211201.9994 | 574.5 | 211201.9994
633.5 | 211201.9994 | 636.5 | 211201.9994 | 639 | 211201.9994 | 642 | 211201.9994 | 645 | 211201.9994 | 647.5 | 211201.9994 | 650.5 | 211201.9994 | 653 | 211201.9994 | 656 | 211201.9994 | 659 | 211201.9994 | 661.5 | 211201.9994 | 664.5 | 211201.9994 | 667 | 211201.9994 | 670 | 211201.9994 | 672.5 | 211201.9994 | 675.5 | 211201.9994 | 678.5 | 211201.9994 | 681 | 211201.9994 | 684 | 211201.9994 | 687 | 211201.9994 | 689.5 | 211201.9994 | 633.5 | 211201.9994
692.5 | 211201.9994 | 695 | 211201.9994 | 698 | 211201.9994 | 700.5 | 211201.9994 | 703.5 | 211201.9994 | 706.5 | 211201.9994 | 709 | 211201.9994 | 712 | 211201.9994 | 715 | 211201.9994 | 717.5 | 211201.9994 | 720.5 | 211201.9994 | 723 | 211201.9994 | 726 | 211201.9994 | 728.5 | 211201.9994 | 731.5 | 211201.9994 | 734.5 | 211201.9994 | 737.5 | 211201.9994 | 740 | 211201.9994 | 742.5 | 211201.9994 | 745.5 | 211201.9994 | 748.5 | 211201.9994 | 692.5 | 211201.9994
751.5 | 211201.9994 | 754 | 211201.9994 | 756.5 | 211201.9994 | 759.5 | 211201.9994 | 762.5 | 211201.9994 | 765 | 211201.9994 | 768 | 211201.9994 | 770.5 | 211201.9994 | 773.5 | 211201.9994 | 776.5 | 211201.9994 | 779 | 211002.0947 | 782 | 211201.9994 | 785 | 211201.9994 | 787.5 | 211201.9994 | 790.5 | 211201.9994 | 793 | 211201.9994 | 796 | 211201.9994 | 798.5 | 211201.9994 | 801.5 | 211201.9994 | 804.5 | 211201.9994 | 807.5 | 211201.9994 | 751.5 | 211002.0947
810 | 211201.9994 | 812.5 | 211201.9994 | 815.5 | 211201.9994 | 818.5 | 211201.9994 | 821 | 211201.9994 | 824 | 211201.9994 | 827 | 211201.9994 | 829.5 | 211201.9994 | 832.5 | 211201.9994 | 835 | 211002.0947 | 838 | 211201.9994 | 840.5 | 211201.9994 | 843.5 | 211201.9994 | 846.5 | 211201.9994 | 849 | 211201.9994 | 852 | 211201.9994 | 854.5 | 211201.9994 | 857.5 | 211201.9994 | 860.5 | 211201.9994 | 863.5 | 211201.9994 | 866 | 211201.9994 | 810 | 211002.0947
868.5 | 211201.9994 | 871.5 | 211201.9994 | 874.5 | 211201.9994 | 877 | 211201.9994 | 880 | 211201.9994 | 882.5 | 211201.9994 | 885.5 | 211201.9994 | 888.5 | 211201.9994 | 891 | 211201.9994 | 894 | 211201.9994 | 897 | 211201.9994 | 899.5 | 211201.9994 | 902.5 | 105550.9988 | 905 | 211201.9994 | 908 | 211201.9994 | 910.5 | 211201.9994 | 913.5 | 211201.9994 | 916.5 | 211201.9994 | 919.5 | 211201.9994 | 922 | 211201.9994 | 924.5 | 211201.9994 | 868.5 | 105550.9988
927.5 | 211002.0947 | 930.5 | 211201.9994 | 933 | 211201.9994 | 936 | 211201.9994 | 938.5 | 211201.9994 | 941.5 | 211201.9994 | 944.5 | 211201.9994 | 947 | 211201.9994 | 950 | 211002.0947 | 953 | 211201.9994 | 955.5 | 211201.9994 | 958.5 | 211201.9994 | 961 | 211201.9994 | 964 | 211201.9994 | 966.5 | 211201.9994 | 969.5 | 211201.9994 | 972.5 | 211201.9994 | 975 | 211201.9994 | 978 | 211201.9994 | 981 | 211201.9994 | 983.5 | 211201.9994 | 927.5 | 211002.0947
986.5 | 211201.9994 | 989 | 211201.9994 | 992 | 211201.9994 | 994.5 | 211201.9994 | 997.5 | 211201.9994 | 1000.5 | 211201.9994 | 1003 | 211201.9994 | 1006 | 211201.9994 | 1009 | 211201.9994 | 1011.5 | 211201.9994 | 1014.5 | 211201.9994 | 1017 | 211201.9994 | 1020 | 211201.9994 | 1022.5 | 211201.9994 | 1025.5 | 211201.9994 | 1028.5 | 211201.9994 | 1031 | 211201.9994 | 1034 | 211201.9994 | 1036.5 | 211201.9994 | 1039.5 | 211201.9994 | 1042.5 | 211201.9994 | 986.5 | 211201.9994
1045 | 211201.9994 | 1048 | 211201.9994 | 1050.5 | 211201.9994 | 1053.5 | 211201.9994 | 1056.5 | 211201.9994 | 1059 | 211201.9994 | 1062 | 211201.9994 | 1064.5 | 211201.9994 | 1067.5 | 211201.9994 | 1070.5 | 211201.9994 | 1073 | 211201.9994 | 1076 | 211201.9994 | 1078.5 | 211201.9994 | 1081.5 | 211201.9994 | 1084.5 | 211201.9994 | 1087 | 211201.9994 | 1090 | 211201.9994 | 1092.5 | 211201.9994 | 1095.5 | 211201.9994 | 1098.5 | 211201.9994 | 1101 | 211201.9994 | 1045 | 211201.9994
1104 | 211201.9994 | 1106.5 | 211201.9994 | 1109.5 | 211201.9994 | 1112.5 | 211201.9994 | 1115 | 211201.9994 | 1118 | 211201.9994 | 1120.5 | 211201.9994 | 1123.5 | 211201.9994 | 1126.5 | 211201.9994 | 1129 | 105550.9988 | 1132 | 211201.9994 | 1134.5 | 211201.9994 | 1137.5 | 211201.9994 | 1140.5 | 211201.9994 | 1143 | 211201.9994 | 1146 | 211201.9994 | 1148.5 | 211201.9994 | 1151.5 | 211201.9994 | 1154.5 | 211201.9994 | 1157 | 211201.9994 | 1160 | 211201.9994 | 1104 | 105550.9988
1162.5 | 211201.9994 | 1165.5 | 211201.9994 | 1168.5 | 211201.9994 | 1171 | 211201.9994 | 1174 | 211201.9994 | 1176.5 | 211201.9994 | 1179.5 | 211201.9994 | 1182.5 | 211201.9994 | 1185 | 211201.9994 | 1188 | 211201.9994 | 1190.5 | 211201.9994 | 1193.5 | 211201.9994 | 1196.5 | 211201.9994 | 1199 | 211201.9994 | 1202 | 211201.9994 | 1204.5 | 211201.9994 | 1207.5 | 211201.9994 | 1210.5 | 211201.9994 | 1213 | 211201.9994 | 1216 | 211201.9994 | 1218.5 | 211201.9994 | 1162.5 | 211201.9994
1221.5 | 211201.9994 | 1224.5 | 211201.9994 | 1227 | 211201.9994 | 1230 | 211201.9994 | 1232.5 | 211201.9994 | 1235.5 | 211201.9994 | 1238.5 | 211201.9994 | 1241 | 105550.9988 | 1244 | 211201.9994 | 1246.5 | 211201.9994 | 1249.5 | 211201.9994 | 1252.5 | 211201.9994 | 1255 | 211201.9994 | 1258 | 211201.9994 | 1260.5 | 211201.9994 | 1263.5 | 211201.9994 | 1266.5 | 211201.9994 | 1269 | 211201.9994 | 1272 | 211201.9994 | 1274.5 | 211201.9994 | 1277.5 | 211201.9994 | 1221.5 | 105550.9988
1280.5 | 211201.9994 | 1283 | 211201.9994 | 1286 | 211201.9994 | 1288.5 | 211201.9994 | 1291.5 | 211201.9994 | 1294.5 | 211201.9994 | 1297 | 211201.9994 | 1300 | 211201.9994 | 1302.5 | 211201.9994 | 1305.5 | 211201.9994 | 1308.5 | 211201.9994 | 1311 | 211201.9994 | 1314 | 211201.9994 | 1316.5 | 211201.9994 | 1319.5 | 211201.9994 | 1322.5 | 211201.9994 | 1325 | 211201.9994 | 1328 | 211201.9994 | 1330.5 | 211201.9994 | 1333.5 | 211201.9994 | 1336.5 | 211201.9994 | 1280.5 | 211201.9994
1339 | 211201.9994 | 1342 | 211201.9994 | 1344.5 | 211201.9994 | 1347.5 | 211201.9994 | 1350.5 | 211201.9994 | 1353 | 211201.9994 | 1356 | 211201.9994 | 1358.5 | 211201.9994 | 1361.5 | 211201.9994 | 1364.5 | 211201.9994 | 1367 | 211201.9994 | 1370 | 211201.9994 | 1372.5 | 211201.9994 | 1375.5 | 211201.9994 | 1378.5 | 211201.9994 | 1381 | 211201.9994 | 1384 | 211201.9994 | 1386.5 | 211201.9994 | 1389.5 | 211201.9994 | 1392.5 | 211201.9994 | 1395 | 211201.9994 | 1339 | 211201.9994
1398 | 211201.9994 | 1400.5 | 211201.9994 | 1403.5 | 211201.9994 | 1406.5 | 211201.9994 | 1409 | 211201.9994 | 1412 | 211201.9994 | 1414.5 | 211201.9994 | 1417.5 | 211201.9994 | 1420.5 | 211201.9994 | 1423 | 211201.9994 | 1426 | 211201.9994 | 1428.5 | 211201.9994 | 1431.5 | 211201.9994 | 1434.5 | 211201.9994 | 1437 | 211201.9994 | 1440 | 211201.9994 | 1442.5 | 211201.9994 | 1445.5 | 211201.9994 | 1448.5 | 211201.9994 | 1451 | 211201.9994 | 1454 | 211201.9994 | 1398 | 211201.9994
1456.5 | 211201.9994 | 1459.5 | 211201.9994 | 1462.5 | 211201.9994 | 1465 | 211201.9994 | 1468 | 211201.9994 | 1470.5 | 15.5886 | 1473.5 | 16077.8038 | 1476.5 | 30014.942 | 1479 | 52650.6182 | 1482 | 211001.9527 | 1484.5 | 211002.0947 | 1487.5 | 211002.0947 | 1490.5 | 211201.9994 | 1493 | 211201.9994 | 1496 | 211201.9994 | 1498.5 | 211201.9994 | 1501.5 | 211201.9994 | 1504.5 | 211201.9994 | 1507 | 211201.9994 | 1510 | 211201.9994 | 1512.5 | 211201.9994 | 1456.5 | 15.5886
1515.5 | 211201.9994 | 1518.5 | 211201.9994 | 1521 | 211201.9994 | 1524 | 211201.9994 | 1526.5 | 211201.9994 | 1529.5 | 7.7949 | 1532.5 | 16070.2339 | 1535 | 42080.6455 | 1538 | 70267.3018 | 1540.5 | 211002.0947 | 1543.5 | 211001.9527 | 1546.5 | 211002.0947 | 1549 | 211002.0947 | 1552 | 211201.9994 | 1554.5 | 211002.0947 | 1557.5 | 211201.9994 | 1560.5 | 211201.9994 | 1563 | 211201.9994 | 1566 | 211201.9994 | 1568.5 | 211201.9994 | 1571.5 | 211201.9994 | 1515.5 | 7.7949
1574.5 | 211201.9994 | 1577 | 211201.9994 | 1580 | 211201.9994 | 1582.5 | 211201.9994 | 1585.5 | 211201.9994 | 1588.5 | 3.8609 | 1591 | 19027.9257 | 1594 | 42080.6455 | 1596.5 | 70234.2519 | 1599.5 | 210902.142 | 1602 | 210902.142 | 1605 | 211002.0947 | 1608 | 211201.9994 | 1610.5 | 211002.0947 | 1613.5 | 211201.9994 | 1616.5 | 211201.9994 | 1619 | 211201.9994 | 1622 | 211201.9994 | 1624.5 | 211201.9994 | 1627.5 | 211201.9994 | 1630.5 | 211201.9994 | 1574.5 | 3.8609
1633 | 211201.9994 | 1636 | 211201.9994 | 1638.5 | 211201.9994 | 1641.5 | 211201.9994 | 1644.5 | 211201.9994 | 1647 | 12.1124 | 1650 | 16077.793 | 1652.5 | 30014.942 | 1655.5 | 105451.071 | 1658.5 | 211002.0473 | 1661 | 211201.9994 | 1663.5 | 211002.0947 | 1666.5 | 211201.9994 | 1669.5 | 211002.0947 | 1672.5 | 211201.9994 | 1675 | 211201.9994 | 1678 | 211002.0947 | 1680.5 | 211002.0947 | 1683.5 | 211201.9994 | 1686 | 211201.9994 | 1689 | 211201.9994 | 1633 | 12.1124
1692 | 211201.9994 | 1694.5 | 211201.9994 | 1697.5 | 211201.9994 | 1700 | 211201.9994 | 1703 | 211201.9994 | 1706 | 166.1339 | 1708.5 | 70234.0789 | 1711.5 | 211201.9994 | 1714 | 211201.9994 | 1717 | 211201.9994 | 1720 | 211201.9994 | 1722.5 | 211201.9994 | 1725.5 | 211201.9994 | 1728.5 | 211201.9994 | 1731 | 211201.9994 | 1734 | 211201.9994 | 1736.5 | 211201.9994 | 1739.5 | 211201.9994 | 1742.5 | 211201.9994 | 1745 | 211201.9994 | 1747.5 | 211201.9994 | 1692 | 166.1339
1750.5 | 211201.9994 | 1753 | 211201.9994 | 1756.5 | 211201.9994 | 1759 | 211201.9994 | 1762 | 211201.9994 | 1764.5 | 211201.9994 | 1767.5 | 211201.9994 | 1770 | 211201.9994 | 1773 | 211201.9994 | 1776 | 211201.9994 | 1778.5 | 211201.9994 | 1781.5 | 211201.9994 | 1784.5 | 211201.9994 | 1787 | 211201.9994 | 1790 | 211002.0947 | 1792.5 | 211201.9994 | 1795.5 | 211201.9994 | 1798.5 | 211201.9994 | 1801 | 211201.9994 | 1803.5 | 211201.9994 | 1806.5 | 211201.9994 | 1750.5 | 211002.0947
1809.5 | 211201.9994 | 1812.5 | 211201.9994 | 1815 | 211201.9994 | 1818 | 211201.9994 | 1820.5 | 211201.9994 | 1823.5 | 2587.4586 | 1826.5 | 70234.0789 | 1829 | 211001.9527 | 1831.5 | 211002.0947 | 1834.5 | 211201.9994 | 1837.5 | 211002.0947 | 1840.5 | 211201.9994 | 1843 | 211201.9994 | 1845.5 | 211201.9994 | 1848.5 | 211201.9994 | 1851.5 | 211201.9994 | 1854.5 | 211201.9994 | 1857 | 211201.9994 | 1860 | 211201.9994 | 1862.5 | 211201.9994 | 1865.5 | 211201.9994 | 1809.5 | 2587.4586
1868 | 211201.9994 | 1871 | 211201.9994 | 1873.5 | 211002.0947 | 1876.5 | 211201.9994 | 1879.5 | 211201.9994 | 1882.5 | 211201.9994 | 1885 | 211201.9994 | 1888 | 211201.9994 | 1890.5 | 211201.9994 | 1893.5 | 211201.9994 | 1896 | 211201.9994 | 1899 | 211201.9994 | 1901.5 | 211201.9994 | 1904.5 | 211201.9994 | 1907.5 | 211201.9994 | 1910.5 | 211201.9994 | 1913 | 211201.9994 | 1915.5 | 211201.9994 | 1918.5 | 211201.9994 | 1921.5 | 211201.9994 | 1924.5 | 211201.9994 | 1868 | 211002.0947
1927 | 211201.9994 | 1929.5 | 211201.9994 | 1932.5 | 211201.9994 | 1935.5 | 211201.9994 | 1938 | 211201.9994 | 1941 | 211201.9994 | 1944 | 211201.9994 | 1946.5 | 211201.9994 | 1949.5 | 211201.9994 | 1952.5 | 211201.9994 | 1955 | 211201.9994 | 1957.5 | 211201.9994 | 1960.5 | 211201.9994 | 1963.5 | 211201.9994 | 1966.5 | 211201.9994 | 1969 | 211201.9994 | 1971.5 | 211201.9994 | 1974.5 | 211201.9994 | 1977.5 | 211201.9994 | 1980.5 | 211201.9994 | 1983 | 211201.9994 | 1927 | 211201.9994
1985.5 | 211201.9994 | 1988.5 | 211201.9994 | 1991.5 | 211201.9994 | 1994 | 211201.9994 | 1997 | 211201.9994 | 1999.5 | 375.2319 | 2002.5 | 23333.7076 | 2005.5 | 211002.0473 | 2008.5 | 211002.0947 | 2011 | 211002.0947 | 2013.5 | 211201.9994 | 2016.5 | 211201.9994 | 2019.5 | 211002.0947 | 2022.5 | 211201.9994 | 2025 | 211201.9994 | 2027.5 | 211201.9994 | 2030.5 | 211201.9994 | 2033.5 | 211201.9994 | 2036 | 211201.9994 | 2039 | 211201.9994 | 2042 | 211201.9994 | 1985.5 | 375.2319
2044.5 | 211201.9994 | 2047.5 | 211201.9994 | 2050 | 211201.9994 | 2053 | 211201.9994 | 2055.5 | 211201.9994 | 2058.5 | 211201.9994 | 2061.5 | 211201.9994 | 2064.5 | 105550.9988 | 2067 | 211002.0947 | 2069.5 | 211201.9994 | 2072.5 | 211201.9994 | 2075.5 | 211201.9994 | 2078 | 211201.9994 | 2081 | 211201.9994 | 2084 | 211201.9994 | 2086.5 | 211201.9994 | 2089.5 | 211201.9994 | 2092 | 211201.9994 | 2095 | 211201.9994 | 2098 | 211201.9994 | 2100.5 | 211201.9994 | 2044.5 | 105550.9988
2103.5 | 211201.9994 | 2106 | 211201.9994 | 2109 | 211201.9994 | 2111.5 | 211201.9994 | 2114.5 | 211201.9994 | 2117.5 | 211201.9994 | 2120.5 | 211201.9994 | 2123 | 211201.9994 | 2125.5 | 211201.9994 | 2128.5 | 211201.9994 | 2131.5 | 211201.9994 | 2134 | 211201.9994 | 2137 | 211201.9994 | 2139.5 | 211201.9994 | 2142.5 | 211201.9994 | 2145.5 | 211201.9994 | 2148 | 211201.9994 | 2151 | 211201.9994 | 2154 | 211201.9994 | 2156.5 | 211201.9994 | 2159.5 | 211201.9994 | 2103.5 | 211201.9994
2162 | 211201.9994 | 2165 | 211201.9994 | 2167.5 | 211201.9994 | 2170.5 | 211201.9994 | 2173.5 | 211201.9994 | 2176.5 | 211201.9994 | 2179 | 211201.9994 | 2181.5 | 211201.9994 | 2184.5 | 211201.9994 | 2187.5 | 211201.9994 | 2190.5 | 211201.9994 | 2193 | 211201.9994 | 2195.5 | 211201.9994 | 2198.5 | 211201.9994 | 2201.5 | 211201.9994 | 2204 | 211201.9994 | 2207 | 211201.9994 | 2209.5 | 211201.9994 | 2212.5 | 211201.9994 | 2215.5 | 211201.9994 | 2218 | 211201.9994 | 2162 | 211201.9994
2221 | 211201.9994 | 2224 | 211201.9994 | 2226.5 | 211201.9994 | 2229.5 | 211201.9994 | 2232 | 211201.9994 | 2235 | 211002.0947 | 2237.5 | 211201.9994 | 2240.5 | 211201.9994 | 2243.5 | 211201.9994 | 2246 | 211201.9994 | 2249 | 211201.9994 | 2252 | 211201.9994 | 2254.5 | 211201.9994 | 2257.5 | 211201.9994 | 2260 | 211201.9994 | 2263 | 211201.9994 | 2265.5 | 211201.9994 | 2268.5 | 211201.9994 | 2271.5 | 211201.9994 | 2274 | 211201.9994 | 2277 | 211201.9994 | 2221 | 211002.0947
2279.5 | 211201.9994 | 2282.5 | 211201.9994 | 2285.5 | 211201.9994 | 2288.5 | 211201.9994 | 2291 | 211201.9994 | 2294 | 211201.9994 | 2296.5 | 211201.9994 | 2299.5 | 211201.9994 | 2302 | 211201.9994 | 2305 | 211201.9994 | 2307.5 | 211201.9994 | 2310.5 | 211201.9994 | 2313.5 | 211201.9994 | 2316.5 | 211201.9994 | 2319 | 211201.9994 | 2321.5 | 211201.9994 | 2324.5 | 211201.9994 | 2327.5 | 211201.9994 | 2330 | 211201.9994 | 2333 | 211201.9994 | 2335.5 | 211201.9994 | 2279.5 | 211201.9994
2338.5 | 211201.9994 | 2341.5 | 211201.9994 | 2344 | 211201.9994 | 2347 | 211201.9994 | 2349.5 | 211201.9994 | 2352.5 | 211201.9994 | 2355.5 | 211201.9994 | 2358 | 211201.9994 | 2361 | 211201.9994 | 2363.5 | 211201.9994 | 2366.5 | 211201.9994 | 2369.5 | 211201.9994 | 2372 | 211201.9994 | 2375 | 211201.9994 | 2377.5 | 65.4727 | 2380.5 | 211201.9994 | 2383.5 | 211201.9994 | 2386 | 211201.9994 | 2389 | 211201.9994 | 2391.5 | 211201.9994 | 2394.5 | 211201.9994 | 2338.5 | 65.4727

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -73 | 22.2618 | 20.2959 | 20.2914 | 20.254 | 20.5006 | 20.4179 | 20.3633 | 21.7932
0.6209 | -72.3791 | 22.2514 | 20.2948 | 20.2862 | 20.2464 | 20.5059 | 20.4184 | 20.3676 | 21.7847
1.2318 | -71.7682 | 22.254 | 20.2903 | 20.2878 | 20.2487 | 20.5105 | 20.4118 | 20.3649 | 21.7803
2.1831 | -70.8169 | 22.2501 | 20.2882 | 20.2908 | 20.2472 | 20.5002 | 20.4158 | 20.3672 | 21.7962
3.1846 | -69.8154 | 22.25 | 20.2838 | 20.2891 | 20.2452 | 20.5035 | 20.4212 | 20.365 | 21.7776
4.176 | -68.824 | 22.2514 | 20.2865 | 20.2929 | 20.2419 | 20.4983 | 20.4146 | 20.3574 | 21.7826
5.1774 | -67.8226 | 22.25 | 20.2921 | 20.2831 | 20.2424 | 20.507 | 20.4176 | 20.3631 | 21.7963
6.1789 | -66.8211 | 22.2527 | 20.2842 | 20.2904 | 20.2442 | 20.4906 | 20.4095 | 20.3618 | 21.7893
7.1803 | -65.8197 | 22.2515 | 20.2889 | 20.282 | 20.2406 | 20.5029 | 20.4144 | 20.3613 | 21.7907
8.1818 | -64.8182 | 22.2485 | 20.2898 | 20.2927 | 20.2419 | 20.4924 | 20.4201 | 20.3624 | 21.7864
9.1832 | -63.8168 | 22.2505 | 20.2862 | 20.2841 | 20.2405 | 20.5087 | 20.4188 | 20.3595 | 21.7837
10.1846 | -62.8154 | 22.2483 | 20.2883 | 20.2778 | 20.243 | 20.4927 | 20.4126 | 20.3595 | 21.7962
11.1761 | -61.8239 | 22.2469 | 20.2809 | 20.2932 | 20.2439 | 20.4918 | 20.4185 | 20.3592 | 21.7879
12.1775 | -60.8225 | 22.2524 | 20.2872 | 20.2926 | 20.2467 | 20.4933 | 20.4191 | 20.3626 | 21.788
13.179 | -59.821 | 22.2562 | 20.2865 | 20.2886 | 20.2405 | 20.4943 | 20.4184 | 20.3622 | 21.7805
14.1804 | -58.8196 | 22.2518 | 20.2868 | 20.2844 | 20.2458 | 20.4939 | 20.4182 | 20.3549 | 21.791
15.1818 | -57.8182 | 22.2608 | 20.2938 | 20.2862 | 20.2452 | 20.5044 | 20.4148 | 20.3636 | 21.7942
16.1833 | -56.8167 | 22.2517 | 20.2855 | 20.2881 | 20.2445 | 20.5033 | 20.4196 | 20.3589 | 21.7807
17.1847 | -55.8153 | 22.2525 | 20.2937 | 20.2906 | 20.2451 | 20.5022 | 20.4208 | 20.3658 | 21.7848
18.1862 | -54.8138 | 22.2513 | 20.2883 | 20.2921 | 20.2464 | 20.4921 | 20.4164 | 20.3602 | 21.7877
19.1776 | -53.8224 | 22.246 | 20.2947 | 20.2954 | 20.2447 | 20.4987 | 20.4169 | 20.3576 | 21.7891
20.179 | -52.821 | 22.2474 | 20.2918 | 20.3006 | 20.2458 | 20.4998 | 20.4159 | 20.3656 | 21.7839
21.1805 | -51.8195 | 22.2485 | 20.2875 | 20.2882 | 20.2477 | 20.5024 | 20.4196 | 20.367 | 21.7836
22.1819 | -50.8181 | 22.2473 | 20.2896 | 20.286 | 20.2462 | 20.4964 | 20.4258 | 20.3638 | 21.7895
23.1833 | -49.8167 | 22.2503 | 20.2895 | 20.2909 | 20.249 | 20.489 | 20.4217 | 20.3621 | 21.7844
24.1848 | -48.8152 | 22.2495 | 20.2872 | 20.2932 | 20.246 | 20.5071 | 20.4187 | 20.3665 | 21.7938
25.1862 | -47.8138 | 22.2513 | 20.291 | 20.2969 | 20.2429 | 20.4964 | 20.4177 | 20.3664 | 21.7947
26.1877 | -46.8123 | 22.2548 | 20.2938 | 20.2874 | 20.2483 | 20.499 | 20.4217 | 20.3593 | 21.7937
27.1791 | -45.8209 | 22.2533 | 20.2886 | 20.2846 | 20.2507 | 20.4874 | 20.4201 | 20.3691 | 21.7807
28.1805 | -44.8195 | 22.2452 | 20.2877 | 20.2922 | 20.2479 | 20.4995 | 20.4185 | 20.3651 | 21.7973
29.182 | -43.818 | 22.2449 | 20.2895 | 20.2857 | 20.254 | 20.5082 | 20.4165 | 20.3685 | 21.7842
30.1834 | -42.8166 | 22.2459 | 20.2897 | 20.2883 | 20.2456 | 20.4991 | 20.419 | 20.3649 | 21.7875
31.1848 | -41.8152 | 22.2514 | 20.2908 | 20.2977 | 20.2536 | 20.5076 | 20.4189 | 20.371 | 21.7987
32.1763 | -40.8237 | 22.2484 | 20.2934 | 20.2889 | 20.2474 | 20.5133 | 20.4215 | 20.3658 | 21.7997
33.1777 | -39.8223 | 22.2481 | 20.2907 | 20.2931 | 20.2469 | 20.503 | 20.4158 | 20.366 | 21.7878
34.1791 | -38.8209 | 22.2474 | 20.2844 | 20.2968 | 20.2492 | 20.5086 | 20.4192 | 20.3689 | 21.7874
35.1806 | -37.8194 | 22.2465 | 20.2936 | 20.2893 | 20.2459 | 20.5061 | 20.4222 | 20.3686 | 21.7921
36.182 | -36.818 | 22.2557 | 20.2882 | 20.2908 | 20.2517 | 20.501 | 20.4211 | 20.3732 | 21.7791
37.1835 | -35.8165 | 22.246 | 20.293 | 20.3056 | 20.257 | 20.4994 | 20.4211 | 20.3737 | 21.7929
38.1849 | -34.8151 | 22.2542 | 20.293 | 20.2968 | 20.2561 | 20.5013 | 20.4212 | 20.3747 | 21.7891
39.1863 | -33.8137 | 22.256 | 20.2882 | 20.2943 | 20.2526 | 20.5087 | 20.4236 | 20.3722 | 21.8001
40.1778 | -32.8222 | 22.2556 | 20.2933 | 20.2802 | 20.2559 | 20.5169 | 20.4231 | 20.3695 | 21.7956
41.1792 | -31.8208 | 22.2541 | 20.2919 | 20.2888 | 20.244 | 20.5006 | 20.4207 | 20.3685 | 21.8048
42.1807 | -30.8193 | 22.2532 | 20.2925 | 20.2996 | 20.2536 | 20.5017 | 20.4227 | 20.3705 | 21.7971
43.1821 | -29.8179 | 22.2549 | 20.2875 | 20.2842 | 20.2579 | 20.5073 | 20.4279 | 20.3743 | 21.7933
44.1835 | -28.8165 | 22.2577 | 20.2899 | 20.2966 | 20.2518 | 20.5003 | 20.4197 | 20.3713 | 21.7931
45.185 | -27.815 | 22.2591 | 20.2916 | 20.2928 | 20.2499 | 20.5067 | 20.4214 | 20.3753 | 21.7943
46.1864 | -26.8136 | 22.2635 | 20.2938 | 20.29 | 20.2547 | 20.5068 | 20.42 | 20.3764 | 21.8041
47.1778 | -25.8222 | 22.2605 | 20.2947 | 20.2892 | 20.2549 | 20.5089 | 20.4257 | 20.3723 | 21.8079
48.1793 | -24.8207 | 22.2644 | 20.2949 | 20.2937 | 20.2568 | 20.505 | 20.4316 | 20.3753 | 21.7851
49.1807 | -23.8193 | 22.2642 | 20.2943 | 20.3016 | 20.2585 | 20.5096 | 20.424 | 20.3738 | 21.7859
50.1822 | -22.8178 | 22.2634 | 20.2984 | 20.2951 | 20.2569 | 20.509 | 20.4279 | 20.3736 | 21.7985
51.1836 | -21.8164 | 22.2614 | 20.2912 | 20.2969 | 20.254 | 20.5146 | 20.4272 | 20.3759 | 21.7904
52.185 | -20.815 | 22.2655 | 20.2912 | 20.2898 | 20.2555 | 20.5087 | 20.4334 | 20.3726 | 21.7975
53.1765 | -19.8235 | 22.2705 | 20.2884 | 20.2903 | 20.2531 | 20.5023 | 20.4212 | 20.3755 | 21.7992
54.1779 | -18.8221 | 22.2704 | 20.2937 | 20.2961 | 20.2544 | 20.5088 | 20.4268 | 20.3756 | 21.7808
55.1793 | -17.8207 | 22.2646 | 20.2907 | 20.2874 | 20.2519 | 20.5123 | 20.425 | 20.3761 | 21.7802
56.1808 | -16.8192 | 22.2607 | 20.2936 | 20.2927 | 20.2522 | 20.5164 | 20.4256 | 20.3757 | 21.7838
57.1822 | -15.8178 | 22.2712 | 20.2928 | 20.2917 | 20.2528 | 20.5023 | 20.4252 | 20.3754 | 21.8039
58.1837 | -14.8163 | 22.2741 | 20.2917 | 20.291 | 20.2547 | 20.5154 | 20.4241 | 20.3797 | 21.7973
59.1851 | -13.8149 | 22.2675 | 20.2975 | 20.2942 | 20.258 | 20.512 | 20.4299 | 20.3844 | 21.7922
60.1865 | -12.8135 | 22.2716 | 20.2942 | 20.298 | 20.2515 | 20.5131 | 20.4247 | 20.3763 | 21.8045
61.178 | -11.822 | 22.2765 | 20.2925 | 20.2982 | 20.2546 | 20.5093 | 20.429 | 20.3806 | 21.7958
62.1794 | -10.8206 | 22.2704 | 20.2921 | 20.285 | 20.2554 | 20.5085 | 20.4246 | 20.379 | 21.797
63.1809 | -9.8191 | 22.2718 | 20.2922 | 20.2977 | 20.256 | 20.5086 | 20.4339 | 20.377 | 21.7827
64.1823 | -8.8177 | 22.2673 | 20.293 | 20.3021 | 20.2537 | 20.5132 | 20.4288 | 20.382 | 21.8022
65.1837 | -7.8163 | 22.267 | 20.2943 | 20.2943 | 20.2581 | 20.5113 | 20.4331 | 20.3797 | 21.8035
66.1852 | -6.8148 | 22.2643 | 20.2995 | 20.2964 | 20.2566 | 20.5136 | 20.4307 | 20.3835 | 21.7998
67.1766 | -5.8234 | 22.2604 | 20.2968 | 20.3032 | 20.2556 | 20.5133 | 20.4301 | 20.3813 | 21.8009
68.178 | -4.822 | 22.2657 | 20.2951 | 20.297 | 20.2614 | 20.5164 | 20.4341 | 20.3784 | 21.7976
69.1795 | -3.8205 | 22.2657 | 20.2929 | 20.3038 | 20.2574 | 20.5125 | 20.4243 | 20.3845 | 21.7985
70.1809 | -2.8191 | 22.2687 | 20.2986 | 20.2965 | 20.2578 | 20.5223 | 20.4528 | 20.3741 | 21.709
71.1824 | -1.8176 | 22.2678 | 20.294 | 20.2947 | 20.2564 | 20.5113 | 20.4463 | 20.3802 | 21.7608
72.1838 | -0.8162 | 22.3956 | 20.2993 | 20.3 | 20.2597 | 20.5227 | 20.4324 | 20.379 | 21.7762
73.1852 | 0.1852 | 22.9701 | 20.2923 | 20.2968 | 20.2574 | 20.5109 | 20.4346 | 20.3817 | 21.7867
74.1867 | 1.1867 | 24.1441 | 20.2939 | 20.3006 | 20.2577 | 20.5183 | 20.436 | 20.3791 | 21.7834
75.1781 | 2.1781 | 25.8957 | 20.2947 | 20.2983 | 20.2623 | 20.5177 | 20.4328 | 20.3828 | 21.807
76.1795 | 3.1795 | 28.1711 | 20.2977 | 20.3075 | 20.2617 | 20.5036 | 20.4339 | 20.3856 | 21.8419
77.181 | 4.181 | 30.8731 | 20.3007 | 20.3066 | 20.2718 | 20.5213 | 20.4357 | 20.3897 | 21.8553
78.1824 | 5.1824 | 33.9221 | 20.3126 | 20.3036 | 20.2736 | 20.5316 | 20.4443 | 20.4002 | 21.8876
79.1839 | 6.1839 | 37.2912 | 20.3266 | 20.3133 | 20.2849 | 20.5362 | 20.4495 | 20.4084 | 21.919
80.1853 | 7.1853 | 40.9353 | 20.3282 | 20.3097 | 20.2951 | 20.5391 | 20.4573 | 20.4271 | 21.9458
81.1867 | 8.1867 | 44.8177 | 20.3493 | 20.3368 | 20.3112 | 20.5526 | 20.4696 | 20.4466 | 21.9986
82.1782 | 9.1782 | 48.8867 | 20.3744 | 20.3407 | 20.3403 | 20.5627 | 20.4835 | 20.4705 | 22.0411
83.1796 | 10.1796 | 53.1278 | 20.4004 | 20.3639 | 20.368 | 20.5868 | 20.5022 | 20.501 | 22.0934
84.181 | 11.181 | 57.528 | 20.4322 | 20.3765 | 20.4036 | 20.6106 | 20.512 | 20.5331 | 22.1635
85.1825 | 12.1825 | 62.0631 | 20.4682 | 20.4061 | 20.4434 | 20.642 | 20.5387 | 20.5764 | 22.2473
86.1839 | 13.1839 | 66.7218 | 20.5141 | 20.4281 | 20.4858 | 20.6761 | 20.5706 | 20.619 | 22.3185
87.1854 | 14.1854 | 71.4963 | 20.5672 | 20.4643 | 20.5448 | 20.723 | 20.6004 | 20.6664 | 22.4216
88.1768 | 15.1768 | 76.4047 | 20.6269 | 20.5003 | 20.6116 | 20.7507 | 20.6421 | 20.7256 | 22.5096
89.1782 | 16.1782 | 81.4605 | 20.7012 | 20.5379 | 20.6812 | 20.8124 | 20.6844 | 20.7899 | 22.6323
90.1797 | 17.1797 | 86.5921 | 20.7725 | 20.5969 | 20.7611 | 20.8711 | 20.7346 | 20.8591 | 22.7564
91.1811 | 18.1811 | 91.8063 | 20.8555 | 20.6389 | 20.8687 | 20.9404 | 20.7849 | 20.9404 | 22.8793
92.1826 | 19.1826 | 97.1661 | 20.9458 | 20.7166 | 20.9624 | 21.0221 | 20.8491 | 21.0291 | 23.0378
93.184 | 20.184 | 102.5762 | 21.0472 | 20.7659 | 21.0778 | 21.0958 | 20.9171 | 21.121 | 23.1825
94.1854 | 21.1854 | 108.1051 | 21.1594 | 20.8483 | 21.2071 | 21.1888 | 21.0002 | 21.2252 | 23.3657
95.1769 | 22.1769 | 113.6502 | 21.2896 | 20.9333 | 21.3462 | 21.2828 | 21.0717 | 21.3398 | 23.5418
96.1783 | 23.1783 | 119.1917 | 21.4298 | 21.0084 | 21.4916 | 21.3829 | 21.1695 | 21.4582 | 23.7835
97.1797 | 24.1797 | 124.7524 | 21.5712 | 21.1124 | 21.6568 | 21.4891 | 21.2723 | 21.5925 | 23.9934
98.1812 | 25.1812 | 130.3564 | 21.7347 | 21.2206 | 21.8324 | 21.604 | 21.3818 | 21.733 | 24.2178
99.1826 | 26.1826 | 135.9956 | 21.916 | 21.3339 | 22.017 | 21.7502 | 21.5039 | 21.8961 | 24.4508
100.1841 | 27.1841 | 141.5489 | 22.1106 | 21.4469 | 22.2389 | 21.8759 | 21.6296 | 22.054 | 24.7113
101.1855 | 28.1855 | 147.1495 | 22.3144 | 21.5805 | 22.4475 | 22.0127 | 21.7672 | 22.2332 | 24.9718
102.1869 | 29.1869 | 152.6677 | 22.5385 | 21.7312 | 22.6866 | 22.1877 | 21.9142 | 22.4254 | 25.2463
103.1784 | 30.1784 | 158.162 | 22.7732 | 21.8879 | 22.9325 | 22.368 | 22.0612 | 22.6259 | 25.5789
104.1798 | 31.1798 | 163.6795 | 23.03 | 22.0533 | 23.1961 | 22.5486 | 22.2199 | 22.8379 | 25.9392
105.1812 | 32.1812 | 169.2551 | 23.3031 | 22.2262 | 23.4884 | 22.7537 | 22.3897 | 23.0699 | 26.2608
106.1827 | 33.1827 | 174.8126 | 23.5988 | 22.4217 | 23.7752 | 22.9463 | 22.577 | 23.3139 | 26.6413
107.1841 | 34.1841 | 180.5101 | 23.9037 | 22.6245 | 24.091 | 23.1668 | 22.7566 | 23.5634 | 27.0004
108.1755 | 35.1755 | 186.2245 | 24.2346 | 22.8377 | 24.43 | 23.4028 | 22.9584 | 23.8343 | 27.4166
109.177 | 36.177 | 191.8306 | 24.5726 | 23.07 | 24.7813 | 23.6502 | 23.174 | 24.1155 | 27.823
110.1784 | 37.1784 | 197.3714 | 24.9314 | 23.3059 | 25.1475 | 23.9075 | 23.4011 | 24.406 | 28.2527
111.1799 | 38.1799 | 202.9752 | 25.3163 | 23.5611 | 25.5433 | 24.1748 | 23.6335 | 24.7122 | 28.6903
112.1813 | 39.1813 | 208.5498 | 25.7093 | 23.8174 | 25.9538 | 24.4722 | 23.8751 | 25.035 | 29.2419
113.1827 | 40.1827 | 214.1898 | 26.1316 | 24.1077 | 26.3863 | 24.7615 | 24.1371 | 25.3741 | 29.7403
114.1842 | 41.1842 | 219.7928 | 26.5532 | 24.3886 | 26.8308 | 25.0793 | 24.4099 | 25.7263 | 30.2675
115.1856 | 42.1856 | 225.4145 | 26.9939 | 24.7067 | 27.3002 | 25.402 | 24.6911 | 26.0947 | 30.8835
116.1971 | 43.1971 | 231.1424 | 27.4605 | 25.0183 | 27.7985 | 25.754 | 25.0005 | 26.4993 | 31.4547
117.1785 | 44.1785 | 236.416 | 27.9333 | 25.3569 | 28.2983 | 26.1027 | 25.3022 | 26.9004 | 32.0302
118.1799 | 45.1799 | 241.951 | 28.4351 | 25.7076 | 28.8287 | 26.4827 | 25.6364 | 27.3201 | 32.6606
119.1814 | 46.1814 | 247.5514 | 28.9594 | 26.0743 | 29.3858 | 26.8776 | 25.9836 | 27.7625 | 33.3671
120.1828 | 47.1828 | 253.2091 | 29.5097 | 26.4642 | 29.9568 | 27.2831 | 26.3315 | 28.2212 | 34.0383
121.1843 | 48.1843 | 258.6319 | 30.0649 | 26.8697 | 30.5589 | 27.7044 | 26.7086 | 28.6921 | 34.7957
122.1857 | 49.1857 | 263.9989 | 30.6568 | 27.2728 | 31.1843 | 28.1528 | 27.0917 | 29.1872 | 35.5102
123.1871 | 50.1871 | 269.2971 | 31.236 | 27.6974 | 31.8259 | 28.62 | 27.5066 | 29.6871 | 36.183
124.1786 | 51.1786 | 274.6727 | 31.8464 | 28.1402 | 32.5018 | 29.0929 | 27.9201 | 30.2133 | 37.0245
125.18 | 52.18 | 279.8224 | 32.4695 | 28.6048 | 33.1951 | 29.5798 | 28.3478 | 30.7715 | 37.7908
126.1814 | 53.1814 | 284.4668 | 33.1227 | 29.0712 | 33.9191 | 30.0886 | 28.788 | 31.3474 | 38.6516
127.1829 | 54.1829 | 288.6594 | 33.787 | 29.5643 | 34.6579 | 30.621 | 29.2494 | 31.9264 | 39.4393
128.1843 | 55.1843 | 292.7377 | 34.4849 | 30.0832 | 35.4264 | 31.1727 | 29.73 | 32.5335 | 40.2732
129.1757 | 56.1757 | 296.5975 | 35.1812 | 30.5939 | 36.2107 | 31.7259 | 30.2142 | 33.1543 | 41.166
130.1772 | 57.1772 | 300.4379 | 35.9081 | 31.1494 | 37.0211 | 32.3057 | 30.7181 | 33.7852 | 42.1044
131.1786 | 58.1786 | 304.1734 | 36.6532 | 31.6905 | 37.8431 | 32.8909 | 31.2417 | 34.4337 | 42.9931
132.1801 | 59.1801 | 307.6421 | 37.4022 | 32.2717 | 38.6805 | 33.4865 | 31.7737 | 35.095 | 43.9301
133.1815 | 60.1815 | 310.8908 | 38.1697 | 32.8569 | 39.5434 | 34.09 | 32.3116 | 35.769 | 44.8599
134.1829 | 61.1829 | 313.8913 | 38.9421 | 33.4579 | 40.4117 | 34.7211 | 32.8547 | 36.466 | 45.8712
135.1844 | 62.1844 | 316.52 | 39.7389 | 34.0709 | 41.2983 | 35.3542 | 33.4013 | 37.1435 | 46.844
136.1758 | 63.1758 | 318.8089 | 40.5371 | 34.6946 | 42.2158 | 36.0126 | 33.9555 | 37.8547 | 47.8218
137.1773 | 64.1773 | 320.7475 | 41.3397 | 35.3226 | 43.1295 | 36.6595 | 34.5234 | 38.5614 | 48.7438
138.1787 | 65.1787 | 322.4445 | 42.1589 | 35.9648 | 44.0674 | 37.3222 | 35.0906 | 39.2661 | 49.6724
139.1801 | 66.1801 | 324.016 | 42.975 | 36.6113 | 45.0173 | 37.9899 | 35.6815 | 39.9897 | 50.6401
140.1816 | 67.1816 | 325.2229 | 43.8047 | 37.2725 | 45.9547 | 38.6564 | 36.2508 | 40.712 | 51.5656
141.183 | 68.183 | 326.2602 | 44.6472 | 37.925 | 46.9142 | 39.3273 | 36.8228 | 41.4283 | 52.5382
142.1845 | 69.1845 | 327.1407 | 45.4927 | 38.5882 | 47.8735 | 40.0016 | 37.4008 | 42.1488 | 53.484
143.1859 | 70.1859 | 328.0462 | 46.3206 | 39.2641 | 48.8386 | 40.6706 | 37.9803 | 42.8664 | 54.4705
144.1773 | 71.1773 | 328.7131 | 47.1527 | 39.9238 | 49.8017 | 41.3391 | 38.5644 | 43.5816 | 55.3935
145.1788 | 72.1788 | 329.1552 | 47.9729 | 40.5954 | 50.7732 | 42.0113 | 39.1415 | 44.2989 | 56.3185
146.1802 | 73.1802 | 329.5661 | 48.7904 | 41.2685 | 51.7261 | 42.682 | 39.7175 | 44.9969 | 57.29
147.1816 | 74.1816 | 330.0536 | 49.608 | 41.9374 | 52.6922 | 43.3504 | 40.2902 | 45.707 | 58.2499
148.1831 | 75.1831 | 330.3999 | 50.4293 | 42.6117 | 53.6549 | 44.011 | 40.8664 | 46.4084 | 59.1592
149.1845 | 76.1845 | 330.528 | 51.2419 | 43.2864 | 54.6225 | 44.6759 | 41.4475 | 47.1011 | 60.0797
150.1759 | 77.1759 | 330.5528 | 52.0472 | 43.952 | 55.5808 | 45.3354 | 42.0183 | 47.7932 | 60.9923
151.1774 | 78.1774 | 330.513 | 52.8592 | 44.6173 | 56.5416 | 45.9964 | 42.5978 | 48.481 | 61.9188
152.1788 | 79.1788 | 330.4962 | 53.6638 | 45.2941 | 57.4848 | 46.6491 | 43.1739 | 49.166 | 62.8257
153.1803 | 80.1803 | 330.5951 | 54.4658 | 45.9629 | 58.4315 | 47.2987 | 43.7387 | 49.8385 | 63.7538
154.1817 | 81.1817 | 330.6534 | 55.2507 | 46.6364 | 59.3706 | 47.9512 | 44.3031 | 50.5102 | 64.6566
155.1831 | 82.1831 | 330.5928 | 56.0163 | 47.289 | 60.3055 | 48.582 | 44.8684 | 51.172 | 65.54
156.1846 | 83.1846 | 330.4449 | 56.7836 | 47.9383 | 61.2365 | 49.2175 | 45.4261 | 51.8453 | 66.4211
157.176 | 84.176 | 330.2285 | 57.5286 | 48.5968 | 62.1426 | 49.8507 | 45.9829 | 52.493 | 67.3276
158.1774 | 85.1774 | 329.9393 | 58.2658 | 49.248 | 63.0553 | 50.4732 | 46.535 | 53.1311 | 68.2037
159.1789 | 86.1789 | 329.7919 | 59.0012 | 49.8828 | 63.961 | 51.0875 | 47.0881 | 53.7783 | 69.0915
160.1803 | 87.1803 | 329.6836 | 59.7117 | 50.536 | 64.8397 | 51.698 | 47.6275 | 54.4028 | 69.994
161.1818 | 88.1818 | 329.4735 | 60.4243 | 51.1573 | 65.7213 | 52.3067 | 48.1646 | 55.0332 | 70.8642
162.1832 | 89.1832 | 329.0852 | 61.1161 | 51.7994 | 66.5905 | 52.9096 | 48.6926 | 55.6545 | 71.75
163.1846 | 90.1846 | 328.7138 | 61.8046 | 52.4283 | 67.4427 | 53.5048 | 49.2215 | 56.2565 | 72.6025
164.1761 | 91.1761 | 328.4998 | 62.4838 | 53.0428 | 68.2975 | 54.1042 | 49.7452 | 56.8535 | 73.4533
165.1775 | 92.1775 | 328.2048 | 63.1599 | 53.6597 | 69.145 | 54.6918 | 50.2757 | 57.4536 | 74.3013
166.179 | 93.179 | 327.9459 | 63.8351 | 54.268 | 69.9908 | 55.2878 | 50.7939 | 58.0479 | 75.1525
167.1804 | 94.1804 | 327.5426 | 64.4994 | 54.8792 | 70.8149 | 55.8635 | 51.3127 | 58.6303 | 75.9954
168.1818 | 95.1818 | 327.0295 | 65.14 | 55.4827 | 71.6316 | 56.4288 | 51.8199 | 59.2014 | 76.8084
169.1833 | 96.1833 | 326.5834 | 65.7854 | 56.0813 | 72.4367 | 56.987 | 52.3162 | 59.771 | 77.6467
170.1847 | 97.1847 | 326.1565 | 66.41 | 56.6752 | 73.2335 | 57.5481 | 52.818 | 60.3332 | 78.4822
171.1862 | 98.1862 | 325.7371 | 67.0352 | 57.2543 | 74.0243 | 58.0922 | 53.3136 | 60.8839 | 79.2959
172.1776 | 99.1776 | 325.2568 | 67.6551 | 57.8344 | 74.7974 | 58.6397 | 53.7993 | 61.4317 | 80.1055
173.179 | 100.179 | 324.8088 | 68.2734 | 58.4096 | 75.5746 | 59.1778 | 54.2797 | 61.9674 | 80.9158
174.1805 | 101.1805 | 324.3024 | 68.8807 | 58.9854 | 76.3374 | 59.7054 | 54.7694 | 62.4967 | 81.7129
175.1819 | 102.1819 | 323.8315 | 69.4802 | 59.5587 | 77.0924 | 60.2384 | 55.239 | 63.0178 | 82.5344
176.1833 | 103.1833 | 323.2723 | 70.0625 | 60.1243 | 77.8482 | 60.7728 | 55.7056 | 63.5363 | 83.3335
177.1848 | 104.1848 | 322.8318 | 70.6464 | 60.6772 | 78.585 | 61.2982 | 56.1693 | 64.0577 | 84.1321
178.1762 | 105.1762 | 322.3729 | 71.2285 | 61.2469 | 79.3234 | 61.7966 | 56.6374 | 64.57 | 84.9343
179.1776 | 106.1776 | 321.9199 | 71.7924 | 61.7981 | 80.0505 | 62.3195 | 57.091 | 65.0704 | 85.7136
180.1791 | 107.1791 | 321.4909 | 72.3595 | 62.3441 | 80.7628 | 62.8228 | 57.5542 | 65.5584 | 86.5025
181.1805 | 108.1805 | 320.9137 | 72.9217 | 62.9105 | 81.4733 | 63.3227 | 58.0066 | 66.0454 | 87.2848
182.182 | 109.182 | 320.2875 | 73.4773 | 63.4446 | 82.1711 | 63.8075 | 58.4585 | 66.5269 | 88.0456
183.1834 | 110.1834 | 319.8292 | 74.0231 | 63.9952 | 82.8791 | 64.3083 | 58.9045 | 67.0049 | 88.8068
184.1848 | 111.1848 | 319.4382 | 74.5563 | 64.5399 | 83.572 | 64.8019 | 59.3428 | 67.4778 | 89.5672
185.1863 | 112.1863 | 318.836 | 75.1008 | 65.0803 | 84.2564 | 65.2822 | 59.77 | 67.9333 | 90.3371
186.1777 | 113.1777 | 318.2473 | 75.6303 | 65.6157 | 84.9392 | 65.7537 | 60.2072 | 68.3852 | 91.0816
187.1792 | 114.1792 | 317.6712 | 76.1589 | 66.1463 | 85.6073 | 66.2157 | 60.6308 | 68.8317 | 91.8167
188.1806 | 115.1806 | 317.0812 | 76.683 | 66.6665 | 86.2807 | 66.691 | 61.0477 | 69.2687 | 92.5571
189.182 | 116.182 | 316.45 | 77.1893 | 67.1881 | 86.9439 | 67.155 | 61.4617 | 69.71 | 93.2808
190.1835 | 117.1835 | 315.9919 | 77.6975 | 67.7049 | 87.5974 | 67.6105 | 61.8845 | 70.1363 | 94.0258
191.1849 | 118.1849 | 315.4284 | 78.1927 | 68.2159 | 88.248 | 68.0627 | 62.286 | 70.5577 | 94.7226
192.1763 | 119.1763 | 314.95 | 78.6898 | 68.7269 | 88.8893 | 68.5025 | 62.6934 | 70.9806 | 95.4336
193.1778 | 120.1778 | 314.5663 | 79.1722 | 69.2438 | 89.519 | 68.9466 | 63.0934 | 71.3806 | 96.1561
194.1792 | 121.1792 | 314.1025 | 79.656 | 69.7366 | 90.1465 | 69.3877 | 63.4973 | 71.7871 | 96.8488
195.1807 | 122.1807 | 313.5663 | 80.1298 | 70.2292 | 90.7563 | 69.821 | 63.9012 | 72.1769 | 97.5428
196.1821 | 123.1821 | 313.0661 | 80.6077 | 70.718 | 91.3567 | 70.2432 | 64.3028 | 72.5692 | 98.2033
197.1835 | 124.1835 | 312.4952 | 81.0648 | 71.199 | 91.9451 | 70.6639 | 64.6921 | 72.9518 | 98.8792
198.185 | 125.185 | 311.984 | 81.5253 | 71.6722 | 92.5245 | 71.0808 | 65.0827 | 73.3258 | 99.5546
199.1764 | 126.1764 | 311.4659 | 81.9739 | 72.1467 | 93.0881 | 71.477 | 65.4624 | 73.7071 | 100.2304
200.1778 | 127.1778 | 311.1179 | 82.4096 | 72.6114 | 93.6327 | 71.8759 | 65.8473 | 74.0784 | 100.8943
201.1793 | 128.1793 | 310.7757 | 82.8511 | 73.0771 | 94.1669 | 72.2823 | 66.2273 | 74.439 | 101.5581
202.1807 | 129.1807 | 310.3873 | 83.2718 | 73.5279 | 94.6808 | 72.6682 | 66.5982 | 74.8013 | 102.2313
203.1822 | 130.1822 | 309.8487 | 83.6803 | 73.9786 | 95.2114 | 73.0537 | 66.9671 | 75.1485 | 102.8566
204.1836 | 131.1836 | 309.2938 | 84.0749 | 74.4301 | 95.7133 | 73.4319 | 67.339 | 75.497 | 103.5099
205.185 | 132.185 | 308.841 | 84.476 | 74.8584 | 96.2243 | 73.8251 | 67.6995 | 75.8366 | 104.1447
206.1765 | 133.1765 | 308.3484 | 84.8703 | 75.3065 | 96.7338 | 74.2089 | 68.0597 | 76.1821 | 104.7675
207.1779 | 134.1779 | 307.8969 | 85.252 | 75.7395 | 97.2416 | 74.5794 | 68.4129 | 76.5096 | 105.4056
208.1793 | 135.1793 | 307.4241 | 85.6355 | 76.1749 | 97.7397 | 74.9522 | 68.7641 | 76.8452 | 106.0144
209.1808 | 136.1808 | 306.901 | 86.0136 | 76.6081 | 98.2332 | 75.3213 | 69.1086 | 77.1674 | 106.6464
210.1822 | 137.1822 | 306.399 | 86.3934 | 77.028 | 98.7098 | 75.6839 | 69.4471 | 77.4768 | 107.25
211.1837 | 138.1837 | 305.8014 | 86.7704 | 77.4466 | 99.1846 | 76.0454 | 69.7792 | 77.7906 | 107.8411
212.1851 | 139.1851 | 305.2583 | 87.1386 | 77.8634 | 99.6591 | 76.4014 | 70.1209 | 78.095 | 108.4431
213.1865 | 140.1865 | 304.7549 | 87.5104 | 78.2856 | 100.1285 | 76.7549 | 70.4557 | 78.4016 | 109.0422
214.178 | 141.178 | 304.348 | 87.8746 | 78.6937 | 100.5899 | 77.1028 | 70.7786 | 78.7061 | 109.6124
215.1794 | 142.1794 | 303.9319 | 88.2258 | 79.0895 | 101.0371 | 77.454 | 71.109 | 78.9975 | 110.1964
216.1809 | 143.1809 | 303.4745 | 88.575 | 79.4954 | 101.4928 | 77.8168 | 71.4286 | 79.2916 | 110.7483
217.1823 | 144.1823 | 303.068 | 88.9195 | 79.8827 | 101.9342 | 78.154 | 71.755 | 79.5858 | 111.3089
218.1837 | 145.1837 | 302.5496 | 89.2548 | 80.2875 | 102.3727 | 78.4858 | 72.0724 | 79.8684 | 111.8755
219.1852 | 146.1852 | 302.0953 | 89.5996 | 80.6613 | 102.7953 | 78.8344 | 72.381 | 80.154 | 112.4176
220.1766 | 147.1766 | 301.46 | 89.936 | 81.0606 | 103.2261 | 79.1584 | 72.6909 | 80.4272 | 112.973
221.178 | 148.178 | 300.8886 | 90.2666 | 81.4377 | 103.6416 | 79.4924 | 72.9914 | 80.6954 | 113.5156
222.1795 | 149.1795 | 300.4367 | 90.6003 | 81.8162 | 104.0449 | 79.8226 | 73.2909 | 80.9712 | 114.0716
223.1809 | 150.1809 | 299.9865 | 90.9314 | 82.196 | 104.4423 | 80.1499 | 73.5853 | 81.2332 | 114.6179
224.1824 | 151.1824 | 299.4331 | 91.2624 | 82.5696 | 104.8364 | 80.4605 | 73.8787 | 81.4891 | 115.1426
225.1838 | 152.1838 | 298.875 | 91.5845 | 82.934 | 105.2367 | 80.7827 | 74.1663 | 81.744 | 115.6813
226.1852 | 153.1852 | 298.3639 | 91.903 | 83.3188 | 105.6281 | 81.1045 | 74.4423 | 81.9961 | 116.2189
227.1767 | 154.1767 | 297.9892 | 92.2359 | 83.6889 | 106.0083 | 81.4168 | 74.7284 | 82.2438 | 116.7325
228.1881 | 155.1881 | 297.6378 | 92.5516 | 84.0514 | 106.3941 | 81.7229 | 75.005 | 82.4929 | 117.2696
229.1795 | 156.1795 | 297.0772 | 92.8576 | 84.3962 | 106.7786 | 82.0385 | 75.2882 | 82.7398 | 117.7697
230.181 | 157.181 | 296.6481 | 93.161 | 84.7554 | 107.139 | 82.3477 | 75.5592 | 82.9734 | 118.2632
231.1824 | 158.1824 | 296.342 | 93.4628 | 85.0988 | 107.4973 | 82.6489 | 75.8354 | 83.2356 | 118.7727
232.1839 | 159.1839 | 295.9606 | 93.7563 | 85.4506 | 107.8424 | 82.9527 | 76.109 | 83.4674 | 119.2604
233.1853 | 160.1853 | 295.591 | 94.0523 | 85.7941 | 108.1747 | 83.2557 | 76.3844 | 83.7045 | 119.7705
234.1867 | 161.1867 | 295.4017 | 94.337 | 86.1281 | 108.5015 | 83.5508 | 76.6462 | 83.9367 | 120.27
235.1782 | 162.1782 | 295.3458 | 94.6221 | 86.4709 | 108.8265 | 83.857 | 76.9162 | 84.163 | 120.7666
236.1796 | 163.1796 | 295.3926 | 94.9082 | 86.7976 | 109.1554 | 84.1513 | 77.1722 | 84.3901 | 121.2681
237.181 | 164.181 | 295.4928 | 95.2029 | 87.1354 | 109.4885 | 84.4439 | 77.4338 | 84.618 | 121.7595
238.1825 | 165.1825 | 295.55 | 95.4909 | 87.473 | 109.8145 | 84.7334 | 77.6963 | 84.8435 | 122.2375
239.1839 | 166.1839 | 295.6196 | 95.7777 | 87.8062 | 110.145 | 85.0383 | 77.9555 | 85.0677 | 122.7339
240.1854 | 167.1854 | 295.7167 | 96.0637 | 88.1314 | 110.4863 | 85.3173 | 78.2088 | 85.2972 | 123.2305
241.1768 | 168.1768 | 295.8506 | 96.3546 | 88.4647 | 110.8162 | 85.6096 | 78.4706 | 85.5159 | 123.7013
242.1782 | 169.1782 | 296.0828 | 96.6489 | 88.8029 | 111.172 | 85.8933 | 78.7287 | 85.7432 | 124.1981
243.1797 | 170.1797 | 296.4198 | 96.9429 | 89.1303 | 111.5121 | 86.1848 | 78.9823 | 85.9628 | 124.7014
244.1811 | 171.1811 | 296.6923 | 97.2368 | 89.4579 | 111.8545 | 86.4856 | 79.2401 | 86.1845 | 125.1763
245.1826 | 172.1826 | 297.0293 | 97.5266 | 89.7858 | 112.1904 | 86.7766 | 79.4966 | 86.402 | 125.6609
246.184 | 173.184 | 297.4204 | 97.8121 | 90.1085 | 112.5428 | 87.065 | 79.7545 | 86.627 | 126.1534
247.1854 | 174.1854 | 297.905 | 98.1046 | 90.4333 | 112.889 | 87.3472 | 80.0067 | 86.8461 | 126.6346
248.1769 | 175.1769 | 298.3497 | 98.3926 | 90.7662 | 113.2227 | 87.6514 | 80.2565 | 87.0748 | 127.1188
249.1783 | 176.1783 | 298.8141 | 98.6732 | 91.0915 | 113.5563 | 87.95 | 80.5163 | 87.3111 | 127.6036
250.1797 | 177.1797 | 299.2518 | 98.9658 | 91.4154 | 113.9071 | 88.241 | 80.7647 | 87.5317 | 128.0801
251.1812 | 178.1812 | 299.6869 | 99.258 | 91.7472 | 114.2558 | 88.5425 | 81.0195 | 87.7652 | 128.5997
252.1826 | 179.1826 | 300.2325 | 99.5474 | 92.0654 | 114.6043 | 88.83 | 81.2723 | 88.0017 | 129.0759
253.1841 | 180.1841 | 300.7628 | 99.847 | 92.4017 | 114.9621 | 89.1174 | 81.5302 | 88.2337 | 129.569
254.1855 | 181.1855 | 301.3369 | 100.1391 | 92.7394 | 115.3255 | 89.4142 | 81.7886 | 88.4689 | 130.0783
255.1869 | 182.1869 | 301.7958 | 100.4439 | 93.062 | 115.6971 | 89.7083 | 82.0496 | 88.7081 | 130.5524
256.1784 | 183.1784 | 302.2508 | 100.7476 | 93.4104 | 116.0684 | 90.013 | 82.3104 | 88.9422 | 131.0613
257.1798 | 184.1798 | 302.6756 | 101.0565 | 93.735 | 116.4426 | 90.3231 | 82.5651 | 89.1782 | 131.5418
258.1812 | 185.1812 | 303.0388 | 101.3754 | 94.0757 | 116.8276 | 90.6167 | 82.8283 | 89.4244 | 132.0297
259.1827 | 186.1827 | 303.3397 | 101.6945 | 94.4084 | 117.2026 | 90.9162 | 83.0901 | 89.66 | 132.5236
260.1841 | 187.1841 | 303.6426 | 102.0133 | 94.7502 | 117.5873 | 91.2251 | 83.3479 | 89.9023 | 133.002
261.1756 | 188.1756 | 303.988 | 102.3315 | 95.0831 | 117.9752 | 91.5246 | 83.6142 | 90.1484 | 133.5031
262.177 | 189.177 | 304.2763 | 102.6527 | 95.4294 | 118.3606 | 91.8271 | 83.8752 | 90.3809 | 133.9895
263.1784 | 190.1784 | 304.6272 | 102.9708 | 95.7511 | 118.7564 | 92.1281 | 84.1427 | 90.6278 | 134.4813
264.1799 | 191.1799 | 304.9585 | 103.2939 | 96.1046 | 119.154 | 92.4374 | 84.409 | 90.8653 | 134.9697
265.1813 | 192.1813 | 305.1409 | 103.6112 | 96.4388 | 119.5432 | 92.7585 | 84.6696 | 91.1157 | 135.458
266.1828 | 193.1828 | 305.4018 | 103.9312 | 96.7846 | 119.9386 | 93.0627 | 84.9392 | 91.3563 | 135.9503
267.1842 | 194.1842 | 305.7053 | 104.2476 | 97.117 | 120.3337 | 93.3775 | 85.2048 | 91.6105 | 136.418
268.1856 | 195.1856 | 305.9701 | 104.568 | 97.466 | 120.7383 | 93.6849 | 85.4724 | 91.8522 | 136.9245
269.1771 | 196.1771 | 306.2876 | 104.8918 | 97.803 | 121.1364 | 93.9884 | 85.738 | 92.1045 | 137.4009
270.1785 | 197.1785 | 306.6129 | 105.2134 | 98.14 | 121.5313 | 94.3017 | 86.0057 | 92.3475 | 137.8842
271.1799 | 198.1799 | 306.7289 | 105.533 | 98.4826 | 121.9271 | 94.608 | 86.2789 | 92.5959 | 138.3761
272.1814 | 199.1814 | 306.8092 | 105.8481 | 98.8273 | 122.3319 | 94.9194 | 86.5442 | 92.8497 | 138.855
273.1828 | 200.1828 | 306.9035 | 106.1758 | 99.158 | 122.7367 | 95.2275 | 86.8118 | 93.0958 | 139.3406
274.1843 | 201.1843 | 307.0729 | 106.5028 | 99.4952 | 123.1325 | 95.5307 | 87.0728 | 93.339 | 139.8189
275.1857 | 202.1857 | 307.258 | 106.8252 | 99.8364 | 123.5331 | 95.8489 | 87.3451 | 93.5842 | 140.2963
276.1871 | 203.1871 | 307.3995 | 107.1413 | 100.1754 | 123.9339 | 96.1612 | 87.6183 | 93.8357 | 140.7715
277.1786 | 204.1786 | 307.4299 | 107.4501 | 100.5151 | 124.3492 | 96.4783 | 87.8805 | 94.0847 | 141.2348
278.18 | 205.18 | 307.5139 | 107.7695 | 100.8515 | 124.7618 | 96.7863 | 88.1412 | 94.3263 | 141.7135
279.1814 | 206.1814 | 307.6274 | 108.088 | 101.1918 | 125.1717 | 97.1033 | 88.4092 | 94.5743 | 142.1832
280.1829 | 207.1829 | 307.6532 | 108.4043 | 101.523 | 125.5886 | 97.4202 | 88.673 | 94.8243 | 142.645
281.1843 | 208.1843 | 307.7483 | 108.7181 | 101.8688 | 125.9819 | 97.733 | 88.9473 | 95.0592 | 143.1057
282.1757 | 209.1757 | 307.8864 | 109.0408 | 102.2066 | 126.3862 | 98.0445 | 89.2123 | 95.3064 | 143.5562
283.1772 | 210.1772 | 308.0238 | 109.3521 | 102.5363 | 126.7843 | 98.3347 | 89.4796 | 95.5457 | 144.0268
284.1786 | 211.1786 | 308.088 | 109.6718 | 102.8702 | 127.1818 | 98.6533 | 89.7453 | 95.7899 | 144.4797
285.1801 | 212.1801 | 308.1384 | 109.9915 | 103.2058 | 127.5803 | 98.9521 | 90.0124 | 96.0353 | 144.9318
286.1815 | 213.1815 | 308.1833 | 110.3072 | 103.528 | 127.9761 | 99.2627 | 90.278 | 96.2766 | 145.3844
287.1829 | 214.1829 | 308.2554 | 110.6303 | 103.8667 | 128.3658 | 99.564 | 90.5415 | 96.5174 | 145.828
288.1844 | 215.1844 | 308.2666 | 110.9463 | 104.193 | 128.7522 | 99.8729 | 90.7999 | 96.7541 | 146.2851
289.1858 | 216.1858 | 308.2189 | 111.2692 | 104.5304 | 129.1401 | 100.1671 | 91.0675 | 96.9924 | 146.7139
290.1773 | 217.1773 | 308.1393 | 111.5726 | 104.8528 | 129.5231 | 100.479 | 91.3269 | 97.2402 | 147.1697
291.1787 | 218.1787 | 308.1354 | 111.8776 | 105.1792 | 129.8972 | 100.7842 | 91.5793 | 97.4692 | 147.5972
292.1801 | 219.1801 | 308.1185 | 112.1837 | 105.4903 | 130.2871 | 101.0736 | 91.8388 | 97.701 | 148.0273
293.1816 | 220.1816 | 307.979 | 112.4865 | 105.8106 | 130.6646 | 101.3681 | 92.0975 | 97.9396 | 148.4562
294.183 | 221.183 | 307.9433 | 112.7957 | 106.1199 | 131.0389 | 101.67 | 92.3644 | 98.1783 | 148.8836
295.1845 | 222.1845 | 307.9008 | 113.0955 | 106.4423 | 131.4109 | 101.9758 | 92.6159 | 98.4141 | 149.3175
296.1859 | 223.1859 | 307.9353 | 113.3979 | 106.7496 | 131.7769 | 102.2741 | 92.8748 | 98.6436 | 149.738
297.2174 | 224.2174 | 307.9101 | 113.6975 | 107.0772 | 132.1473 | 102.5666 | 93.1333 | 98.885 | 150.1811
298.1788 | 225.1788 | 307.7289 | 113.9774 | 107.3738 | 132.4815 | 102.8404 | 93.3751 | 99.1076 | 150.5808
299.1802 | 226.1802 | 307.6168 | 114.2572 | 107.6799 | 132.8313 | 103.1333 | 93.6327 | 99.355 | 150.997
300.1816 | 227.1816 | 307.5586 | 114.5254 | 107.9711 | 133.1777 | 103.4286 | 93.8805 | 99.584 | 151.4122
301.1831 | 228.1831 | 307.4138 | 114.8066 | 108.275 | 133.5168 | 103.7148 | 94.1367 | 99.8231 | 151.8294
302.1845 | 229.1845 | 307.2076 | 115.0807 | 108.5711 | 133.865 | 103.9919 | 94.3843 | 100.0513 | 152.2151
303.1759 | 230.1759 | 307.0176 | 115.3559 | 108.8618 | 134.2111 | 104.2829 | 94.6297 | 100.2866 | 152.6489
304.1774 | 231.1774 | 306.7913 | 115.6385 | 109.1523 | 134.5522 | 104.5624 | 94.8838 | 100.5141 | 153.0437
305.1788 | 232.1788 | 306.7092 | 115.9084 | 109.4556 | 134.8962 | 104.8513 | 95.1316 | 100.7367 | 153.4477
306.1803 | 233.1803 | 306.5647 | 116.1945 | 109.7352 | 135.2307 | 105.1218 | 95.367 | 100.9589 | 153.8433
307.1817 | 234.1817 | 306.4739 | 116.4789 | 110.0289 | 135.5674 | 105.4105 | 95.6138 | 101.1784 | 154.2266
308.1831 | 235.1831 | 306.3436 | 116.7519 | 110.3211 | 135.8903 | 105.6792 | 95.8604 | 101.3976 | 154.6351
309.1846 | 236.1846 | 306.1692 | 117.0417 | 110.6109 | 136.2211 | 105.9608 | 96.1063 | 101.6235 | 155.0345
310.176 | 237.176 | 306.0666 | 117.3225 | 110.8944 | 136.5398 | 106.2421 | 96.3444 | 101.8347 | 155.4156
311.1875 | 238.1875 | 306.0397 | 117.6094 | 111.1885 | 136.8627 | 106.5196 | 96.5932 | 102.0675 | 155.8016
312.1789 | 239.1789 | 306.0682 | 117.8937 | 111.4683 | 137.187 | 106.795 | 96.8318 | 102.2822 | 156.1994
313.1803 | 240.1803 | 306.1378 | 118.1802 | 111.7599 | 137.5052 | 107.0704 | 97.081 | 102.503 | 156.5662
314.1818 | 241.1818 | 306.1079 | 118.4569 | 112.04 | 137.8109 | 107.3393 | 97.3236 | 102.7145 | 156.9349
315.1832 | 242.1832 | 306.0926 | 118.7343 | 112.3024 | 138.1301 | 107.6053 | 97.5606 | 102.9355 | 157.3181
316.1847 | 243.1847 | 306.0096 | 119.0135 | 112.5868 | 138.4275 | 107.8723 | 97.7967 | 103.1593 | 157.6983
317.1861 | 244.1861 | 305.8893 | 119.2919 | 112.8557 | 138.7378 | 108.1436 | 98.0416 | 103.3667 | 158.0706
318.1875 | 245.1875 | 305.7298 | 119.568 | 113.1204 | 139.0434 | 108.4057 | 98.2715 | 103.5826 | 158.4418
319.179 | 246.179 | 305.6504 | 119.8361 | 113.3823 | 139.3457 | 108.6772 | 98.5066 | 103.7946 | 158.815
320.1804 | 247.1804 | 305.6067 | 120.1101 | 113.6493 | 139.6465 | 108.9316 | 98.7355 | 104.0025 | 159.1833
321.1818 | 248.1818 | 305.5409 | 120.3763 | 113.9057 | 139.9537 | 109.2045 | 98.9765 | 104.2123 | 159.5527
322.1833 | 249.1833 | 305.4487 | 120.6447 | 114.1725 | 140.2541 | 109.4577 | 99.2006 | 104.4179 | 159.916
323.1847 | 250.1847 | 305.3433 | 120.9028 | 114.4218 | 140.5479 | 109.7123 | 99.4333 | 104.6233 | 160.265
324.1761 | 251.1761 | 305.214 | 121.1526 | 114.6756 | 140.8512 | 109.9658 | 99.6675 | 104.8336 | 160.6072
325.1776 | 252.1776 | 305.0612 | 121.4079 | 114.9424 | 141.1394 | 110.2232 | 99.8993 | 105.0371 | 160.9719
326.179 | 253.179 | 304.9831 | 121.6578 | 115.183 | 141.4393 | 110.4757 | 100.1309 | 105.2485 | 161.3302
327.1805 | 254.1805 | 304.891 | 121.916 | 115.4358 | 141.733 | 110.7395 | 100.3552 | 105.4558 | 161.6881
328.1819 | 255.1819 | 304.8108 | 122.1679 | 115.6684 | 142.0217 | 110.9905 | 100.5893 | 105.6589 | 162.033
329.1833 | 256.1833 | 304.787 | 122.4208 | 115.9094 | 142.2954 | 111.2496 | 100.8166 | 105.861 | 162.3714
330.1848 | 257.1848 | 304.7974 | 122.6835 | 116.158 | 142.5712 | 111.4807 | 101.0478 | 106.066 | 162.7141
331.1762 | 258.1762 | 304.8502 | 122.9314 | 116.3922 | 142.8519 | 111.7463 | 101.2859 | 106.2647 | 163.068
332.1776 | 259.1776 | 304.9389 | 123.1903 | 116.6262 | 143.1307 | 111.9975 | 101.5124 | 106.466 | 163.3925
333.1791 | 260.1791 | 304.9868 | 123.4323 | 116.8515 | 143.407 | 112.2525 | 101.7475 | 106.6735 | 163.7526
334.1805 | 261.1805 | 305.043 | 123.6843 | 117.0884 | 143.6745 | 112.5033 | 101.9794 | 106.8688 | 164.0978
335.182 | 262.182 | 305.0479 | 123.9238 | 117.3297 | 143.9463 | 112.7381 | 102.2087 | 107.0725 | 164.4271
336.1834 | 263.1834 | 305.1119 | 124.1832 | 117.5532 | 144.2249 | 113.0011 | 102.4308 | 107.2697 | 164.7715
337.1848 | 264.1848 | 305.1743 | 124.425 | 117.7781 | 144.4961 | 113.2488 | 102.6591 | 107.4747 | 165.1069
338.1863 | 265.1863 | 305.223 | 124.6629 | 118.0032 | 144.777 | 113.4956 | 102.8703 | 107.6726 | 165.435
339.1877 | 266.1877 | 305.2504 | 124.9046 | 118.2315 | 145.0531 | 113.7441 | 103.1019 | 107.8853 | 165.7603
340.1792 | 267.1792 | 305.3045 | 125.151 | 118.4416 | 145.3209 | 113.9862 | 103.3211 | 108.0812 | 166.103
341.1806 | 268.1806 | 305.4549 | 125.392 | 118.6668 | 145.5837 | 114.2375 | 103.5369 | 108.2837 | 166.4048
342.182 | 269.182 | 305.5312 | 125.6319 | 118.8811 | 145.8529 | 114.4784 | 103.7575 | 108.4807 | 166.7289
343.1835 | 270.1835 | 305.5977 | 125.8717 | 119.0966 | 146.1241 | 114.7171 | 103.9662 | 108.6867 | 167.0538
344.1849 | 271.1849 | 305.5114 | 126.1044 | 119.3225 | 146.3869 | 114.9518 | 104.1873 | 108.8942 | 167.381
345.1763 | 272.1763 | 305.4491 | 126.334 | 119.5308 | 146.6686 | 115.2086 | 104.4056 | 109.0968 | 167.7012
346.1778 | 273.1778 | 305.324 | 126.5604 | 119.7421 | 146.9511 | 115.4376 | 104.6229 | 109.2994 | 168.0108
347.1792 | 274.1792 | 305.2536 | 126.7864 | 119.9626 | 147.2314 | 115.6889 | 104.8459 | 109.506 | 168.3415
348.1807 | 275.1807 | 305.3464 | 127.0036 | 120.1863 | 147.5253 | 115.9367 | 105.0583 | 109.7088 | 168.6869
349.1821 | 276.1821 | 305.4485 | 127.2192 | 120.396 | 147.8152 | 116.1681 | 105.2805 | 109.91 | 169.0094
350.1835 | 277.1835 | 305.5697 | 127.4404 | 120.6155 | 148.0988 | 116.4128 | 105.4921 | 110.1091 | 169.3088
351.185 | 278.185 | 305.6854 | 127.6453 | 120.814 | 148.3814 | 116.6485 | 105.7069 | 110.309 | 169.6439
352.1764 | 279.1764 | 305.7407 | 127.8573 | 121.0294 | 148.6606 | 116.8791 | 105.9179 | 110.5087 | 169.9618
353.1778 | 280.1778 | 305.7834 | 128.0711 | 121.2427 | 148.9275 | 117.12 | 106.1293 | 110.7055 | 170.2715
354.1793 | 281.1793 | 305.7301 | 128.2726 | 121.454 | 149.2084 | 117.3331 | 106.3434 | 110.902 | 170.5612
355.1807 | 282.1807 | 305.8043 | 128.4805 | 121.674 | 149.5001 | 117.5783 | 106.5563 | 111.1044 | 170.8909
356.1822 | 283.1822 | 305.8154 | 128.687 | 121.8767 | 149.7795 | 117.7989 | 106.7719 | 111.3036 | 171.1838
357.1836 | 284.1836 | 305.9368 | 128.8911 | 122.0865 | 150.0646 | 118.0478 | 106.9766 | 111.5102 | 171.4933
358.185 | 285.185 | 306.057 | 129.0928 | 122.2945 | 150.3416 | 118.2776 | 107.1846 | 111.7151 | 171.82
359.1865 | 286.1865 | 306.1105 | 129.2799 | 122.4997 | 150.6372 | 118.5116 | 107.3933 | 111.9141 | 172.1092
360.1779 | 287.1779 | 306.2369 | 129.4695 | 122.7068 | 150.9167 | 118.7247 | 107.6065 | 112.1147 | 172.4294
361.1794 | 288.1794 | 306.3002 | 129.6475 | 122.9173 | 151.192 | 118.9468 | 107.8172 | 112.3061 | 172.7308
362.1808 | 289.1808 | 306.2955 | 129.844 | 123.1195 | 151.471 | 119.1766 | 108.0313 | 112.5023 | 173.008
363.1822 | 290.1822 | 306.2754 | 130.0349 | 123.3221 | 151.7561 | 119.3936 | 108.2388 | 112.709 | 173.3289
364.1837 | 291.1837 | 306.3335 | 130.2336 | 123.5448 | 152.0368 | 119.6025 | 108.4487 | 112.9003 | 173.6386
365.1851 | 292.1851 | 306.3198 | 130.432 | 123.758 | 152.314 | 119.8307 | 108.6535 | 113.0963 | 173.919
366.1765 | 293.1765 | 306.2211 | 130.628 | 123.9608 | 152.59 | 120.0568 | 108.8684 | 113.2962 | 174.2178
367.178 | 294.178 | 306.1222 | 130.8297 | 124.1838 | 152.8643 | 120.2773 | 109.069 | 113.4957 | 174.5079
368.1794 | 295.1794 | 305.8377 | 131.0327 | 124.3923 | 153.1419 | 120.4905 | 109.2708 | 113.6878 | 174.8043
369.1809 | 296.1809 | 305.6847 | 131.2331 | 124.6099 | 153.4116 | 120.7105 | 109.482 | 113.893 | 175.0907
370.1823 | 297.1823 | 305.625 | 131.437 | 124.8215 | 153.6785 | 120.9204 | 109.682 | 114.0815 | 175.3845
371.1837 | 298.1837 | 305.6191 | 131.6372 | 125.0216 | 153.9416 | 121.1548 | 109.8852 | 114.282 | 175.6734
372.1852 | 299.1852 | 305.6371 | 131.8309 | 125.2505 | 154.2063 | 121.3642 | 110.087 | 114.4801 | 175.9582
373.1866 | 300.1866 | 305.7196 | 132.0252 | 125.4706 | 154.4694 | 121.5692 | 110.29 | 114.6759 | 176.2519
374.178 | 301.178 | 305.8656 | 132.2172 | 125.6947 | 154.733 | 121.7818 | 110.4794 | 114.8639 | 176.5163
375.1795 | 302.1795 | 305.9967 | 132.3994 | 125.9196 | 155.0027 | 122.0003 | 110.678 | 115.0595 | 176.8236
376.1809 | 303.1809 | 306.0515 | 132.5854 | 126.1368 | 155.2668 | 122.2102 | 110.8736 | 115.2486 | 177.0964
377.1824 | 304.1824 | 306.0407 | 132.7733 | 126.3599 | 155.5293 | 122.4243 | 111.0679 | 115.4412 | 177.3624
378.1838 | 305.1838 | 306.0222 | 132.9665 | 126.5869 | 155.7821 | 122.6325 | 111.2662 | 115.6313 | 177.6432
379.1852 | 306.1852 | 306.0232 | 133.1554 | 126.8183 | 156.0281 | 122.8406 | 111.4627 | 115.8158 | 177.9197
380.1867 | 307.1867 | 306.0468 | 133.3486 | 127.0525 | 156.2809 | 123.0439 | 111.657 | 116.0085 | 178.2012
381.1781 | 308.1781 | 306.143 | 133.5488 | 127.2811 | 156.5241 | 123.2501 | 111.8508 | 116.1913 | 178.47
382.1795 | 309.1795 | 306.1362 | 133.742 | 127.5074 | 156.7517 | 123.4593 | 112.0526 | 116.3734 | 178.7618
383.181 | 310.181 | 306.0296 | 133.9512 | 127.7237 | 156.9834 | 123.6624 | 112.2439 | 116.5596 | 179.0269
384.1824 | 311.1824 | 305.9409 | 134.143 | 127.9478 | 157.2198 | 123.8669 | 112.4461 | 116.7386 | 179.2939
385.1839 | 312.1839 | 305.9049 | 134.3442 | 128.1862 | 157.4672 | 124.0706 | 112.6329 | 116.9212 | 179.5598
386.1853 | 313.1853 | 305.8748 | 134.5404 | 128.4144 | 157.7134 | 124.2697 | 112.8291 | 117.1053 | 179.8162
387.1767 | 314.1767 | 305.9835 | 134.7356 | 128.6505 | 157.9626 | 124.4745 | 113.0182 | 117.2916 | 180.0912
388.1882 | 315.1882 | 306.0844 | 134.937 | 128.8731 | 158.2054 | 124.675 | 113.2085 | 117.4649 | 180.35
389.1796 | 316.1796 | 306.0355 | 135.1299 | 129.1217 | 158.4574 | 124.876 | 113.4014 | 117.652 | 180.5927
390.1811 | 317.1811 | 306.0672 | 135.323 | 129.367 | 158.7077 | 125.0764 | 113.5824 | 117.8311 | 180.8687
391.1825 | 318.1825 | 306.0834 | 135.5193 | 129.5981 | 158.9612 | 125.29 | 113.7686 | 118.0138 | 181.1291
392.1839 | 319.1839 | 305.9236 | 135.7209 | 129.809 | 159.2363 | 125.487 | 113.9517 | 118.202 | 181.3747
393.1854 | 320.1854 | 305.8145 | 135.926 | 130.067 | 159.4942 | 125.694 | 114.1382 | 118.382 | 181.6332
394.1768 | 321.1768 | 305.7371 | 136.1271 | 130.3085 | 159.7556 | 125.9035 | 114.3304 | 118.56 | 181.8951
395.1782 | 322.1782 | 305.6786 | 136.3328 | 130.5531 | 160.0148 | 126.1013 | 114.5175 | 118.745 | 182.1416
396.1797 | 323.1797 | 305.637 | 136.5438 | 130.8118 | 160.2846 | 126.3019 | 114.7031 | 118.926 | 182.3958
397.1811 | 324.1811 | 305.6062 | 136.7502 | 131.059 | 160.547 | 126.5164 | 114.8836 | 119.0948 | 182.6521
398.1826 | 325.1826 | 305.7339 | 136.9704 | 131.3081 | 160.8124 | 126.7205 | 115.0615 | 119.2787 | 182.8905
399.184 | 326.184 | 305.7567 | 137.1745 | 131.5617 | 161.0751 | 126.917 | 115.2434 | 119.4475 | 183.16
400.1854 | 327.1854 | 305.7225 | 137.4067 | 131.8134 | 161.341 | 127.1399 | 115.4238 | 119.6261 | 183.3816
401.1869 | 328.1869 | 305.681 | 137.6154 | 132.0634 | 161.5995 | 127.3551 | 115.6097 | 119.8001 | 183.6456
402.1783 | 329.1783 | 305.7022 | 137.8341 | 132.3306 | 161.8366 | 127.559 | 115.7888 | 119.9814 | 183.8934
403.1797 | 330.1797 | 305.7223 | 138.053 | 132.5821 | 162.0873 | 127.7723 | 115.9703 | 120.1604 | 184.1408
404.1812 | 331.1812 | 305.7847 | 138.282 | 132.8343 | 162.3226 | 127.9663 | 116.15 | 120.3396 | 184.3833
405.1826 | 332.1826 | 305.7626 | 138.51 | 133.0856 | 162.5695 | 128.1714 | 116.3209 | 120.5273 | 184.6125
406.1841 | 333.1841 | 305.7733 | 138.7387 | 133.3389 | 162.8208 | 128.3745 | 116.4961 | 120.7034 | 184.8482
407.1855 | 334.1855 | 305.7441 | 138.9603 | 133.601 | 163.0536 | 128.5986 | 116.6749 | 120.8777 | 185.0961
408.1769 | 335.1769 | 305.8222 | 139.1981 | 133.8552 | 163.2959 | 128.8053 | 116.8551 | 121.07 | 185.3197
409.1784 | 336.1784 | 305.9313 | 139.4244 | 134.1085 | 163.5328 | 129.0187 | 117.03 | 121.2509 | 185.5363
410.1798 | 337.1798 | 305.9504 | 139.655 | 134.3695 | 163.7737 | 129.2318 | 117.2116 | 121.4283 | 185.7976
411.1812 | 338.1812 | 306.0002 | 139.8992 | 134.6333 | 164.0053 | 129.4559 | 117.3812 | 121.6071 | 186.0175
412.1827 | 339.1827 | 306.0128 | 140.1348 | 134.8896 | 164.2637 | 129.6756 | 117.5543 | 121.7768 | 186.2658
413.1841 | 340.1841 | 305.9334 | 140.3794 | 135.1408 | 164.5149 | 129.8902 | 117.7281 | 121.9589 | 186.465
414.1756 | 341.1756 | 305.927 | 140.6156 | 135.4088 | 164.7587 | 130.1175 | 117.8929 | 122.1293 | 186.6948
415.177 | 342.177 | 305.9256 | 140.8695 | 135.6653 | 164.9995 | 130.3376 | 118.0703 | 122.2997 | 186.9342
416.1784 | 343.1784 | 305.8948 | 141.1173 | 135.9179 | 165.2312 | 130.5515 | 118.2343 | 122.4622 | 187.1717
417.1799 | 344.1799 | 305.9384 | 141.3686 | 136.1875 | 165.4728 | 130.7773 | 118.4077 | 122.636 | 187.4158
418.1813 | 345.1813 | 305.9418 | 141.6266 | 136.4399 | 165.7124 | 130.9912 | 118.5739 | 122.8036 | 187.6486
419.1828 | 346.1828 | 305.9455 | 141.8752 | 136.712 | 165.9491 | 131.2082 | 118.7448 | 122.9726 | 187.8668
420.1842 | 347.1842 | 306.0703 | 142.1342 | 136.9678 | 166.206 | 131.4359 | 118.902 | 123.1449 | 188.1003
421.1856 | 348.1856 | 306.2366 | 142.3895 | 137.2405 | 166.4558 | 131.6422 | 119.0774 | 123.3093 | 188.3095
422.1871 | 349.1871 | 306.3385 | 142.645 | 137.5028 | 166.7056 | 131.8783 | 119.2429 | 123.4773 | 188.5488
423.1785 | 350.1785 | 306.3998 | 142.8976 | 137.7738 | 166.9344 | 132.0869 | 119.4079 | 123.6456 | 188.7645
424.1799 | 351.1799 | 306.3518 | 143.152 | 138.0191 | 167.1641 | 132.2971 | 119.5735 | 123.8209 | 188.9896
425.1814 | 352.1814 | 306.3779 | 143.4051 | 138.3023 | 167.392 | 132.5154 | 119.7367 | 123.992 | 189.2043
426.1828 | 353.1828 | 306.4685 | 143.6568 | 138.5619 | 167.6202 | 132.7276 | 119.9021 | 124.1602 | 189.4404
427.1843 | 354.1843 | 306.5192 | 143.9151 | 138.8272 | 167.8207 | 132.9545 | 120.0622 | 124.3303 | 189.6541
428.1857 | 355.1857 | 306.5352 | 144.1647 | 139.081 | 168.0246 | 133.1677 | 120.2247 | 124.495 | 189.8737
429.1871 | 356.1871 | 306.5864 | 144.4223 | 139.3467 | 168.2272 | 133.4034 | 120.3929 | 124.6634 | 190.0921
430.1786 | 357.1786 | 306.5733 | 144.6752 | 139.6144 | 168.4362 | 133.6337 | 120.5522 | 124.825 | 190.3009
431.18 | 358.18 | 306.5508 | 144.9213 | 139.8725 | 168.6498 | 133.8571 | 120.7126 | 124.9811 | 190.531
432.1814 | 359.1814 | 306.5726 | 145.157 | 140.1397 | 168.8441 | 134.0766 | 120.8796 | 125.146 | 190.7304
433.1829 | 360.1829 | 306.5516 | 145.4046 | 140.4018 | 169.0533 | 134.3157 | 121.0415 | 125.3062 | 190.9365
434.1843 | 361.1843 | 306.4536 | 145.6381 | 140.6584 | 169.2574 | 134.5399 | 121.1908 | 125.4645 | 191.14
435.1858 | 362.1858 | 306.3958 | 145.8699 | 140.9192 | 169.4652 | 134.7643 | 121.3405 | 125.6176 | 191.351
436.1772 | 363.1772 | 306.2838 | 146.1022 | 141.1606 | 169.6706 | 135.0084 | 121.498 | 125.7777 | 191.5435
437.1786 | 364.1786 | 306.2183 | 146.3292 | 141.4181 | 169.8802 | 135.2265 | 121.6537 | 125.9387 | 191.7485
438.1801 | 365.1801 | 306.1971 | 146.5515 | 141.6738 | 170.0945 | 135.4466 | 121.8036 | 126.0969 | 191.9341
439.1815 | 366.1815 | 306.0977 | 146.7815 | 141.9212 | 170.3069 | 135.6951 | 121.9549 | 126.2554 | 192.1479
440.183 | 367.183 | 305.9402 | 147.0129 | 142.1812 | 170.5046 | 135.9121 | 122.1116 | 126.4118 | 192.3507
441.1844 | 368.1844 | 305.8237 | 147.2427 | 142.4257 | 170.7114 | 136.1447 | 122.2579 | 126.565 | 192.5357
442.1858 | 369.1858 | 305.7311 | 147.4688 | 142.6728 | 170.9092 | 136.3799 | 122.4063 | 126.7163 | 192.7291
443.1873 | 370.1873 | 305.6697 | 147.6962 | 142.9241 | 171.1159 | 136.6056 | 122.5544 | 126.8716 | 192.908
444.1787 | 371.1787 | 305.5531 | 147.9243 | 143.1604 | 171.3203 | 136.8314 | 122.7064 | 127.0209 | 193.1075
445.1801 | 372.1801 | 305.4609 | 148.1419 | 143.3983 | 171.5228 | 137.0648 | 122.8455 | 127.166 | 193.3094
446.1816 | 373.1816 | 305.343 | 148.3581 | 143.638 | 171.722 | 137.2923 | 122.9925 | 127.3101 | 193.4977
447.183 | 374.183 | 305.3122 | 148.5846 | 143.8792 | 171.9283 | 137.5322 | 123.1378 | 127.4651 | 193.6811
448.1845 | 375.1845 | 305.2446 | 148.8029 | 144.1182 | 172.1229 | 137.7586 | 123.2761 | 127.6104 | 193.8636
449.1859 | 376.1859 | 305.0835 | 149.0267 | 144.3612 | 172.3204 | 137.9862 | 123.4213 | 127.7543 | 194.0342
450.1773 | 377.1773 | 305.0643 | 149.2489 | 144.592 | 172.5204 | 138.2216 | 123.5672 | 127.9118 | 194.2094
451.1788 | 378.1788 | 305.0812 | 149.4646 | 144.8333 | 172.707 | 138.4557 | 123.7008 | 128.0666 | 194.3861
452.1802 | 379.1802 | 305.0037 | 149.6881 | 145.0753 | 172.9078 | 138.6793 | 123.8534 | 128.22 | 194.573
453.1816 | 380.1816 | 304.8952 | 149.9155 | 145.308 | 173.1136 | 138.9196 | 123.992 | 128.37 | 194.771
454.1831 | 381.1831 | 304.8392 | 150.13 | 145.5387 | 173.2996 | 139.1468 | 124.1319 | 128.5196 | 194.9441
455.1845 | 382.1845 | 304.7862 | 150.3475 | 145.7743 | 173.4683 | 139.3672 | 124.2748 | 128.6697 | 195.0999
456.186 | 383.186 | 304.8126 | 150.5677 | 146.0086 | 173.6215 | 139.6058 | 124.4252 | 128.8202 | 195.3032
457.1774 | 384.1774 | 304.9598 | 150.778 | 146.2405 | 173.7983 | 139.8294 | 124.563 | 128.9654 | 195.475
458.1788 | 385.1788 | 304.9675 | 150.9976 | 146.478 | 173.9858 | 140.0603 | 124.7138 | 129.1209 | 195.6539
459.1803 | 386.1803 | 305.035 | 151.2021 | 146.6978 | 174.1773 | 140.2986 | 124.8522 | 129.2671 | 195.811
460.1817 | 387.1817 | 305.0855 | 151.4178 | 146.9368 | 174.3899 | 140.5154 | 124.9968 | 129.413 | 195.9875
461.1831 | 388.1831 | 305.1606 | 151.6308 | 147.1686 | 174.6036 | 140.751 | 125.1476 | 129.5602 | 196.1651
462.1846 | 389.1846 | 305.1801 | 151.8551 | 147.398 | 174.8152 | 140.9751 | 125.2997 | 129.7073 | 196.3498
463.176 | 390.176 | 305.3227 | 152.0559 | 147.629 | 175.0288 | 141.2023 | 125.4408 | 129.8431 | 196.5279
464.1775 | 391.1775 | 305.419 | 152.2697 | 147.8548 | 175.239 | 141.4321 | 125.5893 | 129.9988 | 196.6841
465.1789 | 392.1789 | 305.4474 | 152.4753 | 148.08 | 175.4234 | 141.6584 | 125.7344 | 130.1503 | 196.8589
466.1803 | 393.1803 | 305.5209 | 152.6851 | 148.3129 | 175.6302 | 141.8878 | 125.8782 | 130.2927 | 197.0325
467.1818 | 394.1818 | 305.7268 | 152.8838 | 148.5471 | 175.8417 | 142.0981 | 126.0245 | 130.4295 | 197.2054
468.1832 | 395.1832 | 305.7754 | 153.093 | 148.7719 | 176.0452 | 142.3273 | 126.1678 | 130.5827 | 197.3712
469.1847 | 396.1847 | 305.8568 | 153.2967 | 149.0056 | 176.2423 | 142.541 | 126.3117 | 130.7376 | 197.5512
470.1861 | 397.1861 | 305.9903 | 153.5017 | 149.2243 | 176.4365 | 142.7674 | 126.4517 | 130.8885 | 197.7376
471.1875 | 398.1875 | 306.1273 | 153.7065 | 149.4518 | 176.6242 | 142.999 | 126.5867 | 131.033 | 197.8971
472.179 | 399.179 | 306.3192 | 153.9139 | 149.6833 | 176.819 | 143.2214 | 126.7309 | 131.1787 | 198.0561
473.1804 | 400.1804 | 306.3932 | 154.1306 | 149.9013 | 177.0133 | 143.4355 | 126.8845 | 131.3295 | 198.245
474.1818 | 401.1818 | 306.3306 | 154.3336 | 150.1532 | 177.207 | 143.6554 | 127.0299 | 131.4757 | 198.4117
475.1833 | 402.1833 | 306.3393 | 154.5435 | 150.3763 | 177.4078 | 143.8835 | 127.1846 | 131.6183 | 198.5722
476.1847 | 403.1847 | 306.4177 | 154.7475 | 150.6127 | 177.6221 | 144.1116 | 127.3316 | 131.764 | 198.7238
477.1862 | 404.1862 | 306.5008 | 154.9623 | 150.8346 | 177.8361 | 144.3235 | 127.4833 | 131.9103 | 198.9007
478.1776 | 405.1776 | 306.4804 | 155.1659 | 151.0721 | 178.0454 | 144.5416 | 127.6407 | 132.0587 | 199.0654
479.179 | 406.179 | 306.3614 | 155.38 | 151.2999 | 178.2266 | 144.7657 | 127.7975 | 132.2112 | 199.202
480.1805 | 407.1805 | 306.3194 | 155.5874 | 151.5222 | 178.3878 | 144.9863 | 127.9466 | 132.3613 | 199.3667
481.1819 | 408.1819 | 306.2535 | 155.7853 | 151.7459 | 178.5364 | 145.2151 | 128.11 | 132.5217 | 199.5058
482.1833 | 409.1833 | 306.1831 | 155.98 | 151.9674 | 178.7004 | 145.4304 | 128.263 | 132.6676 | 199.6495
483.1848 | 410.1848 | 306.1368 | 156.1728 | 152.2023 | 178.8876 | 145.6501 | 128.4131 | 132.8185 | 199.8096
484.1762 | 411.1762 | 306.0649 | 156.3724 | 152.4118 | 179.0634 | 145.8704 | 128.5623 | 132.9755 | 199.9398
485.1877 | 412.1877 | 306.0779 | 156.5668 | 152.6427 | 179.2363 | 146.0833 | 128.7248 | 133.134 | 200.1135
486.1791 | 413.1791 | 306.0747 | 156.771 | 152.8729 | 179.4237 | 146.3107 | 128.881 | 133.2908 | 200.2449
487.1805 | 414.1805 | 305.9695 | 156.9662 | 153.0911 | 179.6082 | 146.5242 | 129.0401 | 133.4508 | 200.4029
488.182 | 415.182 | 305.8946 | 157.1663 | 153.3147 | 179.7887 | 146.7492 | 129.2059 | 133.6055 | 200.5536
489.1834 | 416.1834 | 305.8903 | 157.371 | 153.5384 | 179.9735 | 146.9584 | 129.3604 | 133.763 | 200.6992
490.1849 | 417.1849 | 305.8604 | 157.5818 | 153.7568 | 180.1767 | 147.1783 | 129.5235 | 133.9145 | 200.8314
491.1863 | 418.1863 | 305.6485 | 157.7867 | 153.9866 | 180.3661 | 147.4017 | 129.6833 | 134.0709 | 200.9876
492.1877 | 419.1877 | 305.5114 | 157.9938 | 154.2083 | 180.5781 | 147.6111 | 129.8491 | 134.2333 | 201.1313
493.1792 | 420.1792 | 305.6274 | 158.195 | 154.4358 | 180.7732 | 147.8349 | 130.008 | 134.3849 | 201.2737
494.1806 | 421.1806 | 305.696 | 158.4064 | 154.6553 | 180.9761 | 148.0377 | 130.1727 | 134.5391 | 201.4114
495.182 | 422.182 | 305.7792 | 158.6123 | 154.8909 | 181.1722 | 148.261 | 130.336 | 134.7012 | 201.5409
496.1835 | 423.1835 | 305.8753 | 158.8123 | 155.105 | 181.3654 | 148.4822 | 130.5006 | 134.8578 | 201.691
497.1849 | 424.1849 | 306.0574 | 159.0191 | 155.3239 | 181.5581 | 148.6956 | 130.6616 | 135.0149 | 201.7992
498.1763 | 425.1763 | 306.1926 | 159.2302 | 155.5576 | 181.7396 | 148.9045 | 130.8288 | 135.17 | 201.9651
499.1778 | 426.1778 | 306.1614 | 159.4327 | 155.768 | 181.9024 | 149.1166 | 130.9949 | 135.3156 | 202.0754
500.1792 | 427.1792 | 306.1629 | 159.6352 | 155.9969 | 182.0791 | 149.3158 | 131.1604 | 135.4709 | 202.2318
501.1807 | 428.1807 | 306.2569 | 159.8398 | 156.2133 | 182.2022 | 149.5313 | 131.3326 | 135.6115 | 202.37
502.1821 | 429.1821 | 306.3427 | 160.0318 | 156.4272 | 182.2988 | 149.7476 | 131.4968 | 135.7571 | 202.5099
503.1835 | 430.1835 | 306.3666 | 160.2345 | 156.657 | 182.4312 | 149.9657 | 131.677 | 135.9033 | 202.6266
504.185 | 431.185 | 306.3554 | 160.4228 | 156.8625 | 182.5855 | 150.169 | 131.8379 | 136.046 | 202.7761
505.1864 | 432.1864 | 306.3017 | 160.6258 | 157.0829 | 182.7473 | 150.3836 | 132.0081 | 136.1947 | 202.8953
506.1778 | 433.1778 | 306.3327 | 160.8078 | 157.2989 | 182.908 | 150.5997 | 132.1819 | 136.3449 | 203.0221
507.1793 | 434.1793 | 306.4157 | 161.0078 | 157.5235 | 183.0933 | 150.789 | 132.3564 | 136.5029 | 203.168
508.1807 | 435.1807 | 306.4347 | 161.2008 | 157.7323 | 183.2727 | 150.9951 | 132.525 | 136.6508 | 203.303
509.1822 | 436.1822 | 306.4704 | 161.3919 | 157.9411 | 183.4524 | 151.2133 | 132.7001 | 136.8002 | 203.4287
510.1836 | 437.1836 | 306.4232 | 161.5869 | 158.1671 | 183.646 | 151.4128 | 132.8695 | 136.9545 | 203.5633
511.185 | 438.185 | 306.4859 | 161.7772 | 158.3729 | 183.8257 | 151.6228 | 133.0475 | 137.0959 | 203.6807
512.1865 | 439.1865 | 306.5341 | 161.9734 | 158.5961 | 184.018 | 151.8125 | 133.2144 | 137.2441 | 203.8167
513.1779 | 440.1779 | 306.6217 | 162.1657 | 158.798 | 184.2057 | 152.0212 | 133.3816 | 137.389 | 203.9274
514.1794 | 441.1794 | 306.5797 | 162.3557 | 159.0041 | 184.4002 | 152.2124 | 133.561 | 137.5397 | 204.0371
515.1808 | 442.1808 | 306.4947 | 162.5497 | 159.2155 | 184.5958 | 152.4226 | 133.7381 | 137.6858 | 204.1472
516.1822 | 443.1822 | 306.3515 | 162.744 | 159.4349 | 184.7844 | 152.6151 | 133.9092 | 137.8306 | 204.2816
517.1837 | 444.1837 | 306.412 | 162.9451 | 159.6508 | 184.9699 | 152.811 | 134.0899 | 137.9672 | 204.4028
518.1851 | 445.1851 | 306.4605 | 163.131 | 159.8545 | 185.1321 | 153.0151 | 134.2598 | 138.1087 | 204.4965
519.1765 | 446.1765 | 306.5467 | 163.3396 | 160.0669 | 185.3099 | 153.2225 | 134.433 | 138.253 | 204.6193
520.178 | 447.178 | 306.5399 | 163.5348 | 160.2727 | 185.4754 | 153.4087 | 134.6042 | 138.3911 | 204.7666
521.1794 | 448.1794 | 306.5135 | 163.7367 | 160.4914 | 185.6314 | 153.6183 | 134.7802 | 138.5362 | 204.8915
522.1809 | 449.1809 | 306.447 | 163.9361 | 160.6883 | 185.7933 | 153.8161 | 134.9427 | 138.679 | 205.006
523.1823 | 450.1823 | 306.4064 | 164.1298 | 160.8992 | 185.9641 | 154.008 | 135.1113 | 138.8318 | 205.1367
524.1837 | 451.1837 | 306.3231 | 164.3328 | 161.0903 | 186.143 | 154.2092 | 135.284 | 138.9757 | 205.2465
525.1852 | 452.1852 | 306.2657 | 164.5295 | 161.3056 | 186.3216 | 154.4183 | 135.4579 | 139.1213 | 205.3573
526.1766 | 453.1766 | 306.2456 | 164.7189 | 161.5115 | 186.4813 | 154.6197 | 135.63 | 139.266 | 205.4658
527.178 | 454.178 | 306.1894 | 164.9153 | 161.7224 | 186.6506 | 154.8115 | 135.8058 | 139.403 | 205.5902
528.1795 | 455.1795 | 306.2194 | 165.1105 | 161.9258 | 186.8289 | 155.0241 | 135.9795 | 139.5508 | 205.7135
529.1809 | 456.1809 | 306.0598 | 165.2884 | 162.1298 | 187.0121 | 155.215 | 136.1501 | 139.6947 | 205.834
530.1824 | 457.1824 | 305.8773 | 165.489 | 162.3295 | 187.2065 | 155.4169 | 136.3197 | 139.8375 | 205.9504
531.1838 | 458.1838 | 305.7472 | 165.6678 | 162.5371 | 187.3911 | 155.613 | 136.4958 | 139.979 | 206.0588
532.1852 | 459.1852 | 305.5785 | 165.8583 | 162.7363 | 187.5931 | 155.8257 | 136.6615 | 140.1193 | 206.1549
533.1867 | 460.1867 | 305.4389 | 166.0434 | 162.9396 | 187.7694 | 156.0221 | 136.8384 | 140.2694 | 206.2772
534.1881 | 461.1881 | 305.2324 | 166.2255 | 163.1362 | 187.9493 | 156.2185 | 137.0051 | 140.4132 | 206.385
535.1796 | 462.1796 | 305.0003 | 166.4059 | 163.3188 | 188.1411 | 156.4159 | 137.1777 | 140.5534 | 206.4912
536.181 | 463.181 | 304.914 | 166.586 | 163.5174 | 188.3339 | 156.6104 | 137.3391 | 140.6934 | 206.5863
537.1824 | 464.1824 | 304.8865 | 166.7687 | 163.7098 | 188.5385 | 156.8123 | 137.5087 | 140.8316 | 206.7182
538.1839 | 465.1839 | 304.8323 | 166.9493 | 163.9027 | 188.7365 | 157.0108 | 137.6763 | 140.9632 | 206.826
539.1853 | 466.1853 | 304.8735 | 167.1348 | 164.0905 | 188.9313 | 157.1979 | 137.8433 | 141.1 | 206.9336
540.1767 | 467.1767 | 305.1123 | 167.3073 | 164.2708 | 189.1118 | 157.4079 | 138.011 | 141.235 | 207.0557
541.1782 | 468.1782 | 305.3804 | 167.4877 | 164.4742 | 189.2943 | 157.612 | 138.1809 | 141.3686 | 207.1563
542.1796 | 469.1796 | 305.5195 | 167.6676 | 164.6507 | 189.4825 | 157.7984 | 138.3455 | 141.5056 | 207.2535
543.1811 | 470.1811 | 305.6172 | 167.8426 | 164.8373 | 189.6612 | 158.0014 | 138.5199 | 141.6393 | 207.3609
544.1825 | 471.1825 | 305.7285 | 168.0205 | 165.0163 | 189.8261 | 158.2045 | 138.6825 | 141.761 | 207.4718
545.1839 | 472.1839 | 305.8839 | 168.1904 | 165.2036 | 189.9923 | 158.3832 | 138.8492 | 141.9001 | 207.5798
546.1854 | 473.1854 | 305.9968 | 168.3684 | 165.3738 | 190.1637 | 158.5864 | 139.0125 | 142.0344 | 207.6804
547.1768 | 474.1768 | 306.1569 | 168.54 | 165.5512 | 190.3219 | 158.7819 | 139.1902 | 142.1774 | 207.7891
548.1782 | 475.1782 | 306.1325 | 168.7065 | 165.7288 | 190.4876 | 158.9722 | 139.3577 | 142.3204 | 207.8871
549.1797 | 476.1797 | 306.1217 | 168.879 | 165.8943 | 190.6372 | 159.164 | 139.5258 | 142.4701 | 207.9769
550.1811 | 477.1811 | 306.2767 | 169.0514 | 166.0655 | 190.8154 | 159.3676 | 139.6959 | 142.6178 | 208.0896
551.1826 | 478.1826 | 306.4636 | 169.2237 | 166.236 | 190.9852 | 159.5513 | 139.8706 | 142.7644 | 208.1981
552.184 | 479.184 | 306.5642 | 169.3918 | 166.4 | 191.1529 | 159.7556 | 140.0479 | 142.9119 | 208.2939
553.1854 | 480.1854 | 306.5682 | 169.5556 | 166.569 | 191.3436 | 159.9487 | 140.2231 | 143.0574 | 208.3991
554.1869 | 481.1869 | 306.5147 | 169.7137 | 166.7361 | 191.5254 | 160.1314 | 140.3876 | 143.2044 | 208.4878
555.1783 | 482.1783 | 306.4135 | 169.8842 | 166.8963 | 191.6714 | 160.3315 | 140.5564 | 143.3458 | 208.5564
556.1797 | 483.1797 | 306.3242 | 170.0498 | 167.064 | 191.842 | 160.5226 | 140.7259 | 143.4974 | 208.6887
557.1812 | 484.1812 | 306.2677 | 170.2219 | 167.2191 | 191.9815 | 160.702 | 140.8945 | 143.6404 | 208.7823
558.1826 | 485.1826 | 306.1642 | 170.3867 | 167.3683 | 192.1267 | 160.9039 | 141.0634 | 143.7824 | 208.8718
559.1841 | 486.1841 | 306.0301 | 170.5548 | 167.5071 | 192.2969 | 161.0907 | 141.2327 | 143.9255 | 208.9866
560.1855 | 487.1855 | 305.9759 | 170.7261 | 167.666 | 192.4678 | 161.2875 | 141.4051 | 144.0773 | 209.1139
561.1769 | 488.1769 | 305.9451 | 170.8943 | 167.802 | 192.6534 | 161.4659 | 141.5748 | 144.2129 | 209.2145
562.1784 | 489.1784 | 306.0101 | 171.0651 | 167.9393 | 192.8461 | 161.6617 | 141.7433 | 144.3607 | 209.3154
563.1798 | 490.1798 | 306.0516 | 171.2392 | 168.0695 | 193.0439 | 161.8511 | 141.916 | 144.5153 | 209.4159
564.1813 | 491.1813 | 306.0328 | 171.4058 | 168.197 | 193.2217 | 162.0409 | 142.077 | 144.655 | 209.5161
565.1827 | 492.1827 | 305.9693 | 171.5757 | 168.2963 | 193.4004 | 162.2274 | 142.2431 | 144.8039 | 209.6305
566.1841 | 493.1841 | 305.9443 | 171.7406 | 168.4042 | 193.5375 | 162.4252 | 142.3998 | 144.9414 | 209.7149
567.1856 | 494.1856 | 305.9469 | 171.909 | 168.4892 | 193.6909 | 162.6116 | 142.5687 | 145.0899 | 209.8099
568.197 | 495.197 | 306.0382 | 172.0739 | 168.543 | 193.8527 | 162.796 | 142.729 | 145.2346 | 209.9169
569.1784 | 496.1784 | 306.1115 | 172.2346 | 168.5368 | 194.0006 | 162.9789 | 142.8912 | 145.3823 | 210.0157
570.1799 | 497.1799 | 306.2128 | 172.3928 | 168.4194 | 194.1416 | 163.1702 | 143.0541 | 145.5227 | 210.1069
571.1813 | 498.1813 | 306.2993 | 172.5468 | 168.3982 | 194.263 | 163.3624 | 143.212 | 145.664 | 210.212
572.1828 | 499.1828 | 306.3614 | 172.7081 | 168.451 | 194.4156 | 163.5381 | 143.3791 | 145.8096 | 210.3061
573.1842 | 500.1842 | 306.5212 | 172.8675 | 168.5609 | 194.5732 | 163.7303 | 143.5358 | 145.9419 | 210.4092
574.1856 | 501.1856 | 306.7767 | 173.0275 | 168.6792 | 194.7478 | 163.9103 | 143.6939 | 146.0907 | 210.4899
575.1871 | 502.1871 | 306.9614 | 173.1918 | 168.8174 | 194.9138 | 164.0963 | 143.8529 | 146.2316 | 210.5948
576.1785 | 503.1785 | 307.1622 | 173.3483 | 168.9755 | 194.9886 | 164.2823 | 144.0158 | 146.3675 | 210.667
577.1799 | 504.1799 | 307.3749 | 173.5014 | 169.1383 | 195.09 | 164.4785 | 144.18 | 146.5063 | 210.7728
578.1814 | 505.1814 | 307.4557 | 173.6481 | 169.3049 | 195.2173 | 164.6561 | 144.3457 | 146.6478 | 210.8492
579.1828 | 506.1828 | 307.6478 | 173.7954 | 169.4749 | 195.3807 | 164.8387 | 144.5078 | 146.7839 | 210.9439
580.1843 | 507.1843 | 307.7522 | 173.9382 | 169.6548 | 195.5711 | 165.0255 | 144.6696 | 146.9341 | 211.0368
581.1857 | 508.1857 | 307.7828 | 174.0863 | 169.8405 | 195.7286 | 165.2074 | 144.8389 | 147.0883 | 211.1179
582.1771 | 509.1771 | 307.8157 | 174.2328 | 170.0163 | 195.8067 | 165.3917 | 145.0053 | 147.2368 | 211.2086
583.1786 | 510.1786 | 307.7614 | 174.3786 | 170.1906 | 195.9027 | 165.5777 | 145.1789 | 147.3799 | 211.2771
584.18 | 511.18 | 307.5979 | 174.5297 | 170.3681 | 196.0169 | 165.7422 | 145.3424 | 147.5261 | 211.3643
585.1814 | 512.1814 | 307.4317 | 174.6828 | 170.5515 | 196.1381 | 165.9327 | 145.5094 | 147.6724 | 211.4624
586.1829 | 513.1829 | 307.3564 | 174.8408 | 170.7439 | 196.2508 | 166.1142 | 145.6737 | 147.8258 | 211.5354
587.1843 | 514.1843 | 307.4403 | 174.9933 | 170.916 | 196.3628 | 166.2841 | 145.833 | 147.9715 | 211.6057
588.1758 | 515.1758 | 307.5176 | 175.1503 | 171.1029 | 196.4709 | 166.4672 | 145.9933 | 148.1067 | 211.6885
589.1772 | 516.1772 | 307.5945 | 175.3089 | 171.2894 | 196.5898 | 166.6416 | 146.1584 | 148.2544 | 211.7672
590.1786 | 517.1786 | 307.5896 | 175.4553 | 171.4787 | 196.725 | 166.8104 | 146.3252 | 148.3953 | 211.8383
591.1801 | 518.1801 | 307.5653 | 175.6045 | 171.6622 | 196.8991 | 166.9911 | 146.4821 | 148.5367 | 211.9166
592.1815 | 519.1815 | 307.5662 | 175.7485 | 171.8517 | 197.0846 | 167.166 | 146.6393 | 148.6737 | 211.9893
593.183 | 520.183 | 307.5532 | 175.9037 | 172.0333 | 197.2665 | 167.3417 | 146.7984 | 148.8124 | 212.0653
594.1844 | 521.1844 | 307.4256 | 176.0504 | 172.2179 | 197.4195 | 167.5119 | 146.9636 | 148.9507 | 212.1371
595.1858 | 522.1858 | 307.233 | 176.1828 | 172.4025 | 197.5629 | 167.6848 | 147.1153 | 149.0895 | 212.2308
596.1873 | 523.1873 | 307.0012 | 176.3289 | 172.5908 | 197.7097 | 167.8621 | 147.2705 | 149.229 | 212.3053
597.1787 | 524.1787 | 306.7756 | 176.4634 | 172.7742 | 197.8679 | 168.032 | 147.4317 | 149.3742 | 212.3712
598.1801 | 525.1801 | 306.5093 | 176.6124 | 172.9623 | 198.0016 | 168.2001 | 147.5824 | 149.5196 | 212.4424
599.1816 | 526.1816 | 306.2713 | 176.7514 | 173.1401 | 198.1573 | 168.3693 | 147.742 | 149.6684 | 212.5188
600.183 | 527.183 | 306.1854 | 176.8908 | 173.3284 | 198.2743 | 168.5455 | 147.8981 | 149.7998 | 212.5651
601.1845 | 528.1845 | 306.0375 | 177.0279 | 173.5149 | 198.3527 | 168.7187 | 148.0488 | 149.9352 | 212.6566
602.1859 | 529.1859 | 305.9129 | 177.1799 | 173.7021 | 198.465 | 168.8835 | 148.2033 | 150.0764 | 212.7086
603.1773 | 530.1773 | 305.83 | 177.3288 | 173.8873 | 198.5288 | 169.0599 | 148.3573 | 150.212 | 212.7714
604.1788 | 531.1788 | 305.6774 | 177.471 | 174.0639 | 198.6278 | 169.2275 | 148.5043 | 150.3435 | 212.8499
605.1802 | 532.1802 | 305.5948 | 177.6214 | 174.2638 | 198.74 | 169.4003 | 148.6578 | 150.4675 | 212.9285
606.1816 | 533.1816 | 305.4104 | 177.7593 | 174.4456 | 198.8722 | 169.5774 | 148.8091 | 150.5935 | 213.0204
607.1831 | 534.1831 | 305.3388 | 177.9037 | 174.6339 | 199.0223 | 169.7302 | 148.9626 | 150.7252 | 213.0564
608.1845 | 535.1845 | 305.213 | 178.0454 | 174.8097 | 199.1678 | 169.9023 | 149.1026 | 150.8617 | 213.1353
609.176 | 536.176 | 305.1362 | 178.1892 | 174.9807 | 199.3034 | 170.0626 | 149.2607 | 150.9962 | 213.1602
610.1774 | 537.1774 | 305.0313 | 178.3258 | 175.1719 | 199.4648 | 170.221 | 149.4119 | 151.1323 | 213.2839
611.1788 | 538.1788 | 304.9486 | 178.4719 | 175.3357 | 199.6089 | 170.385 | 149.5588 | 151.2704 | 213.298
612.1803 | 539.1803 | 304.8443 | 178.6121 | 175.5368 | 199.7457 | 170.5401 | 149.6985 | 151.4026 | 213.3966
613.1817 | 540.1817 | 304.7157 | 178.7626 | 175.7034 | 199.8646 | 170.7092 | 149.8637 | 151.5352 | 213.4443
614.1832 | 541.1832 | 304.7774 | 178.9081 | 175.8996 | 199.998 | 170.8692 | 150.0135 | 151.6616 | 213.5113
615.1846 | 542.1846 | 304.734 | 179.0558 | 176.0811 | 200.1327 | 171.0293 | 150.1584 | 151.7787 | 213.5883
616.176 | 543.176 | 304.6786 | 179.2003 | 176.2619 | 200.2762 | 171.1894 | 150.3021 | 151.9054 | 213.6467
617.1875 | 544.1875 | 304.602 | 179.3399 | 176.4481 | 200.4233 | 171.3618 | 150.4507 | 152.0337 | 213.7228
618.1789 | 545.1789 | 304.6836 | 179.4863 | 176.6292 | 200.5729 | 171.5235 | 150.5956 | 152.1509 | 213.7625
619.1803 | 546.1803 | 304.6596 | 179.6274 | 176.8095 | 200.7404 | 171.6769 | 150.7298 | 152.2769 | 213.8581
620.1818 | 547.1818 | 304.674 | 179.7655 | 176.9918 | 200.889 | 171.8457 | 150.8876 | 152.4007 | 213.8857
621.1832 | 548.1832 | 304.732 | 179.8975 | 177.1744 | 201.0437 | 172.0071 | 151.0239 | 152.5361 | 213.9558
622.1847 | 549.1847 | 304.8435 | 180.0466 | 177.3667 | 201.1896 | 172.1742 | 151.1623 | 152.6689 | 214.0071
623.1861 | 550.1861 | 304.8778 | 180.1851 | 177.5359 | 201.3375 | 172.339 | 151.3067 | 152.8041 | 214.0554
624.1775 | 551.1775 | 304.9004 | 180.3263 | 177.7197 | 201.4655 | 172.4918 | 151.4448 | 152.9307 | 214.1286
625.179 | 552.179 | 304.8485 | 180.4712 | 177.912 | 201.6045 | 172.6663 | 151.5901 | 153.0614 | 214.1885
626.1804 | 553.1804 | 304.9088 | 180.6128 | 178.0907 | 201.7251 | 172.8195 | 151.7235 | 153.1922 | 214.2656
627.1818 | 554.1818 | 305.0017 | 180.7558 | 178.2664 | 201.8699 | 172.9731 | 151.8608 | 153.3232 | 214.298
628.1833 | 555.1833 | 305.1531 | 180.8965 | 178.4503 | 201.9987 | 173.1321 | 151.9906 | 153.4567 | 214.3958
629.1847 | 556.1847 | 305.1238 | 181.038 | 178.6486 | 202.1389 | 173.3075 | 152.1362 | 153.5824 | 214.4495
630.1862 | 557.1862 | 305.1131 | 181.1778 | 178.804 | 202.2726 | 173.4716 | 152.2746 | 153.7107 | 214.5386
631.1776 | 558.1776 | 305.0909 | 181.3172 | 179 | 202.3943 | 173.63 | 152.4264 | 153.8403 | 214.5721
632.179 | 559.179 | 305.1033 | 181.4614 | 179.17 | 202.5157 | 173.781 | 152.5617 | 153.9728 | 214.6535
633.1805 | 560.1805 | 305.2647 | 181.5951 | 179.3655 | 202.6327 | 173.9408 | 152.6987 | 154.1021 | 214.7091
634.1819 | 561.1819 | 305.4462 | 181.7281 | 179.5491 | 202.7606 | 174.1066 | 152.8425 | 154.2336 | 214.7659
635.1833 | 562.1833 | 305.6045 | 181.8618 | 179.7227 | 202.8718 | 174.265 | 152.9828 | 154.3638 | 214.8573
636.1848 | 563.1848 | 305.8416 | 181.9936 | 179.8989 | 202.9995 | 174.426 | 153.1268 | 154.4986 | 214.9034
637.1762 | 564.1762 | 306.0046 | 182.1225 | 180.0678 | 203.1522 | 174.5645 | 153.2685 | 154.6344 | 215.0014
638.1877 | 565.1877 | 305.9995 | 182.2533 | 180.2494 | 203.3159 | 174.7398 | 153.4096 | 154.7723 | 215.0465
639.1791 | 566.1791 | 305.9529 | 182.3798 | 180.4222 | 203.4687 | 174.8955 | 153.5406 | 154.9066 | 215.1346
640.1805 | 567.1805 | 305.9267 | 182.5065 | 180.6003 | 203.6354 | 175.0575 | 153.6853 | 155.0484 | 215.1895
641.182 | 568.182 | 305.8811 | 182.6339 | 180.7755 | 203.7685 | 175.2036 | 153.8105 | 155.1827 | 215.2671
642.1834 | 569.1834 | 305.8943 | 182.7551 | 180.938 | 203.8836 | 175.3687 | 153.9267 | 155.3215 | 215.3116
643.1849 | 570.1849 | 305.8919 | 182.8807 | 181.1128 | 203.9952 | 175.5173 | 154.0288 | 155.4687 | 215.3838
644.1863 | 571.1863 | 305.9435 | 182.9991 | 181.2892 | 204.0896 | 175.6714 | 154.1389 | 155.6116 | 215.4508
645.1777 | 572.1777 | 306.0355 | 183.1213 | 181.4447 | 204.2062 | 175.8303 | 154.2635 | 155.7458 | 215.4867
646.1792 | 573.1792 | 306.1448 | 183.2517 | 181.6195 | 204.3202 | 175.9773 | 154.3758 | 155.8801 | 215.578
647.1806 | 574.1806 | 306.2559 | 183.377 | 181.7913 | 204.43 | 176.1343 | 154.4897 | 156.0075 | 215.6224
648.182 | 575.182 | 306.2876 | 183.4974 | 181.9702 | 204.5645 | 176.2971 | 154.5995 | 156.1406 | 215.7014
649.1835 | 576.1835 | 306.2895 | 183.6254 | 182.146 | 204.6799 | 176.4336 | 154.7127 | 156.2615 | 215.7371
650.1849 | 577.1849 | 306.231 | 183.7726 | 182.3201 | 204.8108 | 176.6158 | 154.8198 | 156.3839 | 215.8022
651.1763 | 578.1763 | 306.1786 | 183.9051 | 182.4862 | 204.9532 | 176.7539 | 154.927 | 156.5126 | 215.8461
652.1778 | 579.1778 | 306.2405 | 184.0313 | 182.664 | 205.1006 | 176.9092 | 155.0452 | 156.6384 | 215.9057
653.1792 | 580.1792 | 306.4005 | 184.1573 | 182.8355 | 205.2318 | 177.0622 | 155.157 | 156.77 | 215.9544
654.1807 | 581.1807 | 306.5087 | 184.2808 | 183.0066 | 205.3707 | 177.2184 | 155.2757 | 156.9023 | 216.0145
655.1821 | 582.1821 | 306.4981 | 184.4102 | 183.1774 | 205.5054 | 177.386 | 155.3992 | 157.0304 | 216.1015
656.1835 | 583.1835 | 306.4989 | 184.5314 | 183.3516 | 205.5935 | 177.5322 | 155.534 | 157.1501 | 216.1414
657.185 | 584.185 | 306.5623 | 184.6631 | 183.5152 | 205.5961 | 177.6823 | 155.6499 | 157.2739 | 216.1996
658.3066 | 585.3066 | 306.6227 | 184.8073 | 183.7169 | 205.6078 | 177.8462 | 155.8116 | 157.4097 | 216.2625
659.1879 | 586.1879 | 306.5911 | 184.9284 | 183.8553 | 205.6396 | 177.9938 | 155.9406 | 157.5125 | 216.293
660.1793 | 587.1793 | 306.5269 | 185.0553 | 184.0316 | 205.7005 | 178.1452 | 156.0832 | 157.6307 | 216.3333
661.1807 | 588.1807 | 306.3796 | 185.1882 | 184.1906 | 205.7786 | 178.2959 | 156.2307 | 157.7604 | 216.3969
662.1822 | 589.1822 | 306.1499 | 185.3194 | 184.3662 | 205.8657 | 178.4557 | 156.3849 | 157.8734 | 216.4436
663.1836 | 590.1836 | 306.0768 | 185.4455 | 184.537 | 205.964 | 178.6057 | 156.5415 | 157.9999 | 216.4829
664.1851 | 591.1851 | 306.1014 | 185.5783 | 184.6951 | 206.0474 | 178.7515 | 156.6922 | 158.12 | 216.5383
665.1865 | 592.1865 | 306.1291 | 185.7097 | 184.8609 | 206.145 | 178.8946 | 156.841 | 158.2408 | 216.5631
666.1779 | 593.1779 | 306.1444 | 185.8329 | 185.0314 | 206.2506 | 179.0459 | 156.9821 | 158.3706 | 216.6169
667.1794 | 594.1794 | 306.1374 | 185.9556 | 185.1938 | 206.3745 | 179.1927 | 157.1237 | 158.4971 | 216.662
668.1808 | 595.1808 | 306.1281 | 186.0904 | 185.3523 | 206.4769 | 179.3423 | 157.2657 | 158.6211 | 216.7133
669.1822 | 596.1822 | 306.0594 | 186.221 | 185.5121 | 206.5827 | 179.4969 | 157.4023 | 158.7338 | 216.7496
670.1837 | 597.1837 | 305.8945 | 186.3379 | 185.6818 | 206.6946 | 179.6343 | 157.5455 | 158.8571 | 216.7995
671.1851 | 598.1851 | 305.8287 | 186.468 | 185.8363 | 206.8023 | 179.7819 | 157.6874 | 158.9603 | 216.8313
672.1765 | 599.1765 | 305.7653 | 186.603 | 186.0026 | 206.8755 | 179.923 | 157.8324 | 159.0714 | 216.8697
673.178 | 600.178 | 305.7558 | 186.724 | 186.1556 | 206.962 | 180.081 | 157.9717 | 159.1874 | 216.9169
674.1794 | 601.1794 | 305.877 | 186.8572 | 186.3309 | 207.0445 | 180.2244 | 158.1164 | 159.2949 | 216.9538
675.1809 | 602.1809 | 305.9162 | 186.9843 | 186.4884 | 207.1087 | 180.3763 | 158.2553 | 159.4186 | 217
676.1823 | 603.1823 | 305.9299 | 187.1078 | 186.6513 | 207.1723 | 180.5083 | 158.406 | 159.538 | 217.0366
677.1837 | 604.1837 | 305.9334 | 187.2292 | 186.7969 | 207.2675 | 180.662 | 158.5581 | 159.6516 | 217.0867
678.1852 | 605.1852 | 305.9964 | 187.3541 | 186.9643 | 207.3728 | 180.8038 | 158.6952 | 159.7803 | 217.1059
679.1766 | 606.1766 | 306.0068 | 187.4702 | 187.1299 | 207.4597 | 180.9524 | 158.838 | 159.8979 | 217.1626
680.178 | 607.178 | 305.9339 | 187.6001 | 187.2777 | 207.549 | 181.0827 | 158.9782 | 160.0132 | 217.1866
681.1795 | 608.1795 | 305.8187 | 187.7143 | 187.4409 | 207.6563 | 181.2387 | 159.1191 | 160.1334 | 217.2333
682.1809 | 609.1809 | 305.6866 | 187.833 | 187.5981 | 207.7593 | 181.3841 | 159.2442 | 160.2519 | 217.2704
683.1824 | 610.1824 | 305.5966 | 187.95 | 187.748 | 207.8803 | 181.5318 | 159.3868 | 160.3746 | 217.3214
684.1838 | 611.1838 | 305.597 | 188.0588 | 187.9029 | 207.9879 | 181.6724 | 159.524 | 160.4949 | 217.358
685.1852 | 612.1852 | 305.618 | 188.1744 | 188.0513 | 208.1116 | 181.8135 | 159.6498 | 160.6079 | 217.4004
686.1867 | 613.1867 | 305.7935 | 188.2863 | 188.2024 | 208.2514 | 181.9696 | 159.7701 | 160.7235 | 217.4405
687.1881 | 614.1881 | 305.8447 | 188.3965 | 188.3675 | 208.3818 | 182.1135 | 159.9029 | 160.839 | 217.458
688.1896 | 615.1896 | 305.9586 | 188.5097 | 188.5182 | 208.4992 | 182.2636 | 160.0269 | 160.9482 | 217.5191
689.181 | 616.181 | 306.0807 | 188.6349 | 188.674 | 208.5937 | 182.4148 | 160.1561 | 161.0666 | 217.5627
690.1824 | 617.1824 | 306.1159 | 188.7473 | 188.8296 | 208.6743 | 182.5628 | 160.273 | 161.1836 | 217.606
691.1839 | 618.1839 | 306.1077 | 188.8672 | 188.9745 | 208.7604 | 182.6997 | 160.3944 | 161.2864 | 217.6484
692.1853 | 619.1853 | 306.0928 | 188.9747 | 189.1207 | 208.8579 | 182.8533 | 160.5175 | 161.4038 | 217.6984
693.1767 | 620.1767 | 306.0988 | 189.0915 | 189.2819 | 208.9499 | 183.0001 | 160.6401 | 161.5236 | 217.7391
694.1782 | 621.1782 | 306.0555 | 189.1952 | 189.4418 | 209.0157 | 183.1434 | 160.7612 | 161.6495 | 217.7791
695.1796 | 622.1796 | 306.0386 | 189.3164 | 189.5974 | 209.1028 | 183.2866 | 160.8848 | 161.762 | 217.8299
696.1811 | 623.1811 | 306.0561 | 189.4333 | 189.7418 | 209.2073 | 183.4412 | 161.008 | 161.8788 | 217.8799
697.1825 | 624.1825 | 306.0708 | 189.5347 | 189.8926 | 209.3242 | 183.5813 | 161.1364 | 162.0041 | 217.9155
698.1839 | 625.1839 | 306.0689 | 189.6474 | 190.0349 | 209.446 | 183.7226 | 161.2765 | 162.1104 | 217.973
699.1854 | 626.1854 | 306.0806 | 189.7644 | 190.184 | 209.5597 | 183.8685 | 161.4086 | 162.2229 | 218.0175
700.1768 | 627.1768 | 306.0582 | 189.865 | 190.3197 | 209.6895 | 184.0085 | 161.5352 | 162.3326 | 218.0342
701.1782 | 628.1782 | 306.0856 | 189.9807 | 190.4877 | 209.827 | 184.1414 | 161.6781 | 162.4425 | 218.0839
702.1797 | 629.1797 | 306.1865 | 190.0904 | 190.6298 | 209.9426 | 184.2924 | 161.8264 | 162.5468 | 218.1273
703.1811 | 630.1811 | 306.339 | 190.2067 | 190.7665 | 210.0881 | 184.4332 | 161.9752 | 162.6635 | 218.1741
704.1826 | 631.1826 | 306.3606 | 190.3311 | 190.9163 | 210.2163 | 184.5713 | 162.114 | 162.7666 | 218.2041
705.184 | 632.184 | 306.3752 | 190.4503 | 191.0703 | 210.3578 | 184.7156 | 162.2507 | 162.8669 | 218.266
706.1854 | 633.1854 | 306.3229 | 190.572 | 191.2216 | 210.4879 | 184.8547 | 162.4024 | 162.9637 | 218.3032
707.1869 | 634.1869 | 306.2688 | 190.6902 | 191.3564 | 210.6113 | 185.0028 | 162.5529 | 163.0685 | 218.3463
708.1783 | 635.1783 | 306.2264 | 190.8126 | 191.5142 | 210.7355 | 185.1362 | 162.7018 | 163.1678 | 218.3771
709.1798 | 636.1798 | 306.2198 | 190.9377 | 191.6689 | 210.8546 | 185.2775 | 162.8451 | 163.2782 | 218.4054
710.1812 | 637.1812 | 306.2427 | 191.0533 | 191.8103 | 210.971 | 185.4175 | 162.9789 | 163.3835 | 218.442
711.1826 | 638.1826 | 306.1417 | 191.1746 | 191.9683 | 211.0867 | 185.5512 | 163.1079 | 163.4923 | 218.4959
712.1841 | 639.1841 | 306.1289 | 191.2818 | 192.1032 | 211.2157 | 185.7033 | 163.2401 | 163.5971 | 218.5245
713.1855 | 640.1855 | 306.2528 | 191.4076 | 192.2539 | 211.3526 | 185.8244 | 163.366 | 163.7147 | 218.5718
714.1769 | 641.1769 | 306.3528 | 191.5176 | 192.3995 | 211.4692 | 185.9621 | 163.5117 | 163.8244 | 218.6247
715.1784 | 642.1784 | 306.3621 | 191.6343 | 192.5513 | 211.5444 | 186.1058 | 163.6518 | 163.9311 | 218.666
716.1798 | 643.1798 | 306.3721 | 191.7444 | 192.678 | 211.6137 | 186.2469 | 163.7907 | 164.0321 | 218.6962
717.1813 | 644.1813 | 306.4908 | 191.8617 | 192.8363 | 211.6928 | 186.3805 | 163.9317 | 164.1422 | 218.7291
718.1827 | 645.1827 | 306.5687 | 191.9681 | 192.9826 | 211.7658 | 186.5139 | 164.069 | 164.2574 | 218.7946
719.1841 | 646.1841 | 306.6657 | 192.0828 | 193.1182 | 211.8684 | 186.6587 | 164.1604 | 164.3711 | 218.8351
720.1856 | 647.1856 | 306.7887 | 192.1929 | 193.2659 | 211.9793 | 186.7977 | 164.2528 | 164.4812 | 218.8755
721.177 | 648.177 | 306.8107 | 192.3201 | 193.4175 | 212.0849 | 186.9419 | 164.359 | 164.594 | 218.9328
722.1784 | 649.1784 | 306.8211 | 192.432 | 193.561 | 212.1382 | 187.0779 | 164.479 | 164.7114 | 218.9864
723.1799 | 650.1799 | 306.8582 | 192.5518 | 193.7042 | 212.2422 | 187.2254 | 164.5939 | 164.8164 | 219.0327
724.1813 | 651.1813 | 306.8719 | 192.6782 | 193.8485 | 212.3575 | 187.3573 | 164.7141 | 164.9296 | 219.0732
725.1828 | 652.1828 | 306.8978 | 192.8054 | 193.9979 | 212.4828 | 187.5043 | 164.841 | 165.0387 | 219.1185
726.1842 | 653.1842 | 306.911 | 192.9206 | 194.136 | 212.6286 | 187.6332 | 164.9662 | 165.1489 | 219.1847
727.1856 | 654.1856 | 306.8336 | 193.0404 | 194.2704 | 212.7411 | 187.7719 | 165.0843 | 165.2584 | 219.2157
728.1771 | 655.1771 | 306.6409 | 193.1571 | 194.4127 | 212.8401 | 187.9127 | 165.2095 | 165.3718 | 219.2822
729.1785 | 656.1785 | 306.4136 | 193.2615 | 194.5474 | 212.9097 | 188.048 | 165.3345 | 165.4831 | 219.3453
730.1799 | 657.1799 | 306.3576 | 193.3657 | 194.6846 | 213.0202 | 188.1832 | 165.4548 | 165.5969 | 219.3779
731.1814 | 658.1814 | 306.3403 | 193.478 | 194.8293 | 213.1138 | 188.3158 | 165.5633 | 165.7206 | 219.4336
732.1828 | 659.1828 | 306.3126 | 193.5758 | 194.9754 | 213.2069 | 188.4584 | 165.7029 | 165.8235 | 219.4749
733.1843 | 660.1843 | 306.3683 | 193.6721 | 195.1128 | 213.2643 | 188.5902 | 165.81 | 165.9399 | 219.5272
734.1857 | 661.1857 | 306.258 | 193.7728 | 195.2373 | 213.3527 | 188.7363 | 165.9304 | 166.0501 | 219.5711
735.1771 | 662.1771 | 306.1456 | 193.8777 | 195.3833 | 213.4209 | 188.8605 | 166.0539 | 166.1555 | 219.6251
736.1786 | 663.1786 | 306.0334 | 193.9845 | 195.5164 | 213.4756 | 189.0015 | 166.1765 | 166.2571 | 219.6637
737.18 | 664.18 | 306.0977 | 194.0994 | 195.653 | 213.5111 | 189.1475 | 166.3086 | 166.3559 | 219.7322
738.1815 | 665.1815 | 306.2989 | 194.2174 | 195.7965 | 213.5424 | 189.2831 | 166.4289 | 166.4624 | 219.7847
739.1829 | 666.1829 | 306.4923 | 194.331 | 195.9481 | 213.6109 | 189.4095 | 166.5667 | 166.5609 | 219.8277
740.1843 | 667.1843 | 306.6119 | 194.4444 | 196.0804 | 213.7038 | 189.5435 | 166.699 | 166.6755 | 219.8608
741.1858 | 668.1858 | 306.6385 | 194.5582 | 196.2168 | 213.8257 | 189.6881 | 166.8349 | 166.7755 | 219.9315
742.1772 | 669.1772 | 306.6696 | 194.6845 | 196.3647 | 213.945 | 189.8164 | 166.9713 | 166.8874 | 219.9579
743.1786 | 670.1786 | 306.6501 | 194.8021 | 196.4972 | 214.069 | 189.947 | 167.0984 | 166.9868 | 220.0041
744.1801 | 671.1801 | 306.5339 | 194.9227 | 196.636 | 214.1664 | 190.0887 | 167.2212 | 167.0909 | 220.0534
745.1815 | 672.1815 | 306.3873 | 195.0488 | 196.7609 | 214.2077 | 190.2089 | 167.3469 | 167.1951 | 220.0986
746.183 | 673.183 | 306.2954 | 195.1631 | 196.9084 | 214.1523 | 190.3495 | 167.4818 | 167.2954 | 220.1425
747.1844 | 674.1844 | 306.2158 | 195.2838 | 197.043 | 214.1903 | 190.4652 | 167.6025 | 167.4066 | 220.1676
748.1858 | 675.1858 | 306.1795 | 195.4052 | 197.1737 | 214.2519 | 190.597 | 167.724 | 167.5053 | 220.2283
749.1773 | 676.1773 | 306.0754 | 195.527 | 197.3186 | 214.3452 | 190.7379 | 167.837 | 167.6118 | 220.2726
750.1787 | 677.1787 | 305.9898 | 195.6435 | 197.4533 | 214.4607 | 190.8585 | 167.9613 | 167.7197 | 220.3083
751.1801 | 678.1801 | 305.8324 | 195.7717 | 197.5885 | 214.548 | 190.9916 | 168.0798 | 167.8289 | 220.3589
752.1816 | 679.1816 | 305.8625 | 195.8942 | 197.7207 | 214.6061 | 191.1298 | 168.2062 | 167.9309 | 220.4112
753.183 | 680.183 | 305.8411 | 196.0102 | 197.868 | 214.7168 | 191.25 | 168.3521 | 168.0273 | 220.4528
754.1845 | 681.1845 | 305.8455 | 196.1211 | 197.9942 | 214.823 | 191.392 | 168.4626 | 168.1276 | 220.5024
755.1859 | 682.1859 | 305.8074 | 196.231 | 198.1311 | 214.885 | 191.5226 | 168.6422 | 168.2266 | 220.5279
756.1773 | 683.1773 | 305.7924 | 196.3488 | 198.2634 | 214.9769 | 191.6638 | 168.8811 | 168.3328 | 220.5923
757.1788 | 684.1788 | 305.838 | 196.4518 | 198.3819 | 214.9631 | 191.8001 | 169.0925 | 168.4314 | 220.6457
758.1802 | 685.1802 | 305.7998 | 196.5604 | 198.5251 | 214.9884 | 191.9283 | 169.2741 | 168.5256 | 220.6785
759.1816 | 686.1816 | 305.756 | 196.6662 | 198.6552 | 214.944 | 192.0594 | 169.4589 | 168.6306 | 220.7165
760.1831 | 687.1831 | 305.809 | 196.7883 | 198.7814 | 215.0552 | 192.1775 | 169.6312 | 168.7299 | 220.7561
761.1845 | 688.1845 | 305.8637 | 196.8987 | 198.9078 | 215.1025 | 192.3376 | 169.7871 | 168.8283 | 220.8002
762.176 | 689.176 | 305.8853 | 197.0184 | 199.0433 | 215.2183 | 192.4677 | 169.9386 | 168.9208 | 220.8353
763.1774 | 690.1774 | 305.9266 | 197.1408 | 199.1743 | 215.2967 | 192.593 | 170.0867 | 169.0199 | 220.8785
764.1788 | 691.1788 | 305.8685 | 197.2678 | 199.3077 | 215.3657 | 192.7408 | 170.2283 | 169.1099 | 220.9203
765.1803 | 692.1803 | 305.7421 | 197.3812 | 199.4392 | 215.4229 | 192.8693 | 170.3553 | 169.2198 | 220.9771
766.1817 | 693.1817 | 305.7963 | 197.5107 | 199.5654 | 215.4446 | 193.0051 | 170.4895 | 169.3162 | 221.017
767.1832 | 694.1832 | 305.876 | 197.6251 | 199.6948 | 215.5353 | 193.1374 | 170.6108 | 169.4155 | 221.0717
768.1846 | 695.1846 | 305.8222 | 197.7448 | 199.8224 | 215.6122 | 193.2824 | 170.738 | 169.529 | 221.1108
769.186 | 696.186 | 305.8664 | 197.8704 | 199.9575 | 215.5689 | 193.4162 | 170.858 | 169.6369 | 221.1484
770.1875 | 697.1875 | 305.8298 | 197.9923 | 200.0735 | 215.4128 | 193.5363 | 170.9773 | 169.7535 | 221.1802
771.1789 | 698.1789 | 305.839 | 198.1108 | 200.1962 | 215.432 | 193.6808 | 171.099 | 169.8629 | 221.2392
772.1803 | 699.1803 | 305.8645 | 198.2183 | 200.3255 | 215.546 | 193.8123 | 171.2151 | 169.973 | 221.2805
773.1818 | 700.1818 | 305.9341 | 198.3355 | 200.4441 | 215.5357 | 193.957 | 171.3404 | 170.0782 | 221.314
774.1832 | 701.1832 | 306.0313 | 198.4466 | 200.5747 | 215.6314 | 194.0855 | 171.4643 | 170.1916 | 221.3557
775.1847 | 702.1847 | 306.1217 | 198.5567 | 200.6946 | 215.6404 | 194.2212 | 171.5851 | 170.3 | 221.4087
776.1861 | 703.1861 | 306.0681 | 198.6666 | 200.8222 | 215.7713 | 194.3536 | 171.7074 | 170.4146 | 221.4578
777.1775 | 704.1775 | 306.0729 | 198.7587 | 200.9469 | 215.8353 | 194.4763 | 171.8271 | 170.5215 | 221.4804
778.179 | 705.179 | 306.1576 | 198.8652 | 201.0623 | 215.8181 | 194.6127 | 171.9529 | 170.6329 | 221.5318
779.1804 | 706.1804 | 306.2862 | 198.9583 | 201.1769 | 215.8662 | 194.7519 | 172.0787 | 170.7461 | 221.5689
780.1818 | 707.1818 | 306.3347 | 199.0661 | 201.3027 | 216.0273 | 194.8891 | 172.2046 | 170.8574 | 221.6165
781.1833 | 708.1833 | 306.3562 | 199.1643 | 201.4229 | 216.0256 | 195.0121 | 172.3244 | 170.972 | 221.6399
782.1847 | 709.1847 | 306.3924 | 199.2663 | 201.5504 | 216.1478 | 195.1517 | 172.453 | 171.0928 | 221.6945
783.1862 | 710.1862 | 306.4565 | 199.3697 | 201.67 | 216.2788 | 195.2858 | 172.5797 | 171.2038 | 221.7434
784.1776 | 711.1776 | 306.5059 | 199.4734 | 201.7907 | 216.4556 | 195.4178 | 172.6944 | 171.3178 | 221.7703
785.179 | 712.179 | 306.485 | 199.5821 | 201.9186 | 216.5007 | 195.5487 | 172.8214 | 171.43 | 221.8247
786.1805 | 713.1805 | 306.4081 | 199.6884 | 202.0361 | 216.5066 | 195.6785 | 172.937 | 171.5306 | 221.8818
787.1819 | 714.1819 | 306.2945 | 199.8067 | 202.162 | 216.6326 | 195.8145 | 173.0625 | 171.6302 | 221.9188
788.1834 | 715.1834 | 306.2173 | 199.9226 | 202.278 | 216.7208 | 195.9321 | 173.1813 | 171.7333 | 221.9687
789.1848 | 716.1848 | 306.1789 | 200.0386 | 202.4049 | 216.7434 | 196.0641 | 173.2954 | 171.8271 | 221.9858
790.1862 | 717.1862 | 306.0136 | 200.1515 | 202.5106 | 216.6347 | 196.1864 | 173.4088 | 171.9252 | 222.0391
791.1877 | 718.1877 | 306.0185 | 200.2628 | 202.6405 | 216.6715 | 196.2989 | 173.5199 | 172.0232 | 222.0779
792.1791 | 719.1791 | 306.0721 | 200.3768 | 202.7517 | 216.6403 | 196.4274 | 173.6302 | 172.1198 | 222.1219
793.1805 | 720.1805 | 306.0828 | 200.483 | 202.855 | 216.6969 | 196.548 | 173.7436 | 172.2151 | 222.1746
794.182 | 721.182 | 305.9087 | 200.6031 | 202.9842 | 216.6833 | 196.6688 | 173.8651 | 172.3099 | 222.1862
795.1834 | 722.1834 | 305.8014 | 200.7123 | 203.0881 | 216.7287 | 196.8019 | 173.9806 | 172.4025 | 222.2315
796.1849 | 723.1849 | 305.6921 | 200.8224 | 203.195 | 216.7928 | 196.9214 | 174.0916 | 172.4813 | 222.2674
797.1863 | 724.1863 | 305.5693 | 200.9317 | 203.3153 | 216.7725 | 197.0544 | 174.1982 | 172.5668 | 222.3193
798.1777 | 725.1777 | 305.5269 | 201.0409 | 203.4286 | 216.7875 | 197.1863 | 174.3015 | 172.6458 | 222.356
799.1792 | 726.1792 | 305.416 | 201.1434 | 203.5449 | 216.8913 | 197.3172 | 174.419 | 172.7445 | 222.4143
800.1806 | 727.1806 | 305.3752 | 201.2517 | 203.6538 | 216.8303 | 197.4418 | 174.5335 | 172.8242 | 222.4499
801.182 | 728.182 | 305.3683 | 201.3658 | 203.7737 | 216.9897 | 197.5608 | 174.6456 | 172.9121 | 222.4788
802.1835 | 729.1835 | 305.282 | 201.4773 | 203.8788 | 216.9528 | 197.7012 | 174.7555 | 172.9984 | 222.5243
803.1849 | 730.1849 | 305.1699 | 201.5978 | 203.9971 | 216.7952 | 197.8308 | 174.8962 | 173.0837 | 222.5818
804.1763 | 731.1763 | 305.1407 | 201.7061 | 204.1175 | 216.247 | 197.9639 | 175.0245 | 173.1669 | 222.6209
805.1778 | 732.1778 | 305.1213 | 201.8212 | 204.2284 | 216.2404 | 198.0775 | 175.151 | 173.2543 | 222.6705
806.1792 | 733.1792 | 305.2532 | 201.942 | 204.3286 | 216.242 | 198.2127 | 175.2855 | 173.3465 | 222.706
807.1807 | 734.1807 | 305.3379 | 202.0609 | 204.4463 | 216.2798 | 198.3441 | 175.4162 | 173.4261 | 222.7271
808.1821 | 735.1821 | 305.2666 | 202.1724 | 204.5563 | 216.3061 | 198.463 | 175.5437 | 173.5107 | 222.7703
809.1835 | 736.1835 | 305.2109 | 202.28 | 204.662 | 216.4526 | 198.5799 | 175.6702 | 173.5914 | 222.8141
810.185 | 737.185 | 305.2132 | 202.3928 | 204.7861 | 216.5736 | 198.7184 | 175.787 | 173.676 | 222.8606
811.1864 | 738.1864 | 305.205 | 202.507 | 204.8919 | 216.7209 | 198.8445 | 175.9161 | 173.7561 | 222.8763
812.1879 | 739.1879 | 305.3477 | 202.6071 | 204.9982 | 216.8046 | 198.9762 | 176.0487 | 173.8277 | 222.9273
813.1793 | 740.1793 | 305.5659 | 202.7194 | 205.1111 | 216.8555 | 199.1145 | 176.1723 | 173.909 | 222.969
814.1807 | 741.1807 | 305.6806 | 202.8228 | 205.2362 | 216.8773 | 199.2363 | 176.2949 | 173.992 | 222.9858
815.1822 | 742.1822 | 305.7295 | 202.9401 | 205.3373 | 217.0332 | 199.3625 | 176.4111 | 174.0736 | 223.0484
816.1836 | 743.1836 | 305.7855 | 203.0533 | 205.4427 | 217.1093 | 199.4906 | 176.5393 | 174.1507 | 223.0748
817.1851 | 744.1851 | 305.8311 | 203.1764 | 205.566 | 217.1344 | 199.6303 | 176.6705 | 174.2406 | 223.1415
818.1865 | 745.1865 | 305.9086 | 203.3005 | 205.6743 | 217.2212 | 199.751 | 176.7989 | 174.3156 | 223.1609
819.1779 | 746.1779 | 305.9631 | 203.4211 | 205.8056 | 217.28 | 199.8801 | 176.9322 | 174.4018 | 223.2107
820.1794 | 747.1794 | 306.0002 | 203.535 | 205.9159 | 217.3623 | 200.0057 | 177.0514 | 174.4835 | 223.2341
821.1808 | 748.1808 | 306.0287 | 203.6608 | 206.0291 | 217.4044 | 200.1314 | 177.1743 | 174.5723 | 223.2993
822.1822 | 749.1822 | 305.9943 | 203.7739 | 206.1466 | 217.4249 | 200.2717 | 177.3025 | 174.6659 | 223.3146
823.1837 | 750.1837 | 306.0321 | 203.8919 | 206.2663 | 217.6103 | 200.4008 | 177.4195 | 174.7523 | 223.3649
824.1851 | 751.1851 | 306.1319 | 204.0116 | 206.3829 | 217.6888 | 200.5156 | 177.5394 | 174.8488 | 223.4174
825.1765 | 752.1765 | 306.2589 | 204.1335 | 206.4874 | 217.7545 | 200.6533 | 177.6491 | 174.9358 | 223.4313
826.178 | 753.178 | 306.2771 | 204.2546 | 206.6178 | 217.7947 | 200.7723 | 177.7713 | 175.0367 | 223.4925
827.1794 | 754.1794 | 306.162 | 204.3735 | 206.7314 | 217.8453 | 200.9058 | 177.8899 | 175.1357 | 223.5399
828.1809 | 755.1809 | 306.1569 | 204.4888 | 206.8483 | 217.841 | 201.044 | 178.0039 | 175.239 | 223.5998
829.1823 | 756.1823 | 306.0295 | 204.5998 | 206.9662 | 217.8842 | 201.1616 | 178.1173 | 175.3306 | 223.6297
830.1837 | 757.1837 | 305.8658 | 204.7147 | 207.0987 | 217.9209 | 201.2906 | 178.2297 | 175.4244 | 223.6667
831.1852 | 758.1852 | 305.8212 | 204.8407 | 207.2124 | 217.8836 | 201.4158 | 178.3469 | 175.5194 | 223.7141
832.1866 | 759.1866 | 305.6983 | 204.9566 | 207.3356 | 217.9773 | 201.5541 | 178.4587 | 175.6073 | 223.7353
833.1781 | 760.1781 | 305.6077 | 205.0735 | 207.4425 | 217.9744 | 201.6639 | 178.5772 | 175.6852 | 223.789
834.1795 | 761.1795 | 305.5927 | 205.1868 | 207.5565 | 218.1358 | 201.7969 | 178.6893 | 175.7758 | 223.8302
835.1809 | 762.1809 | 305.598 | 205.302 | 207.6669 | 218.2331 | 201.9169 | 178.8082 | 175.8494 | 223.868
836.1824 | 763.1824 | 305.6693 | 205.4205 | 207.788 | 218.1534 | 202.04 | 178.9191 | 175.9361 | 223.9065
837.1838 | 764.1838 | 305.7956 | 205.5343 | 207.8989 | 217.7902 | 202.1644 | 179.019 | 176.015 | 223.9529
838.1853 | 765.1853 | 305.8155 | 205.6438 | 208.0051 | 218.0944 | 202.2818 | 179.144 | 176.0995 | 223.9751
839.1767 | 766.1767 | 305.7076 | 205.7675 | 208.1161 | 218.2184 | 202.4072 | 179.2372 | 176.1956 | 224.0384
840.1781 | 767.1781 | 305.648 | 205.8752 | 208.2288 | 218.1734 | 202.5326 | 179.3479 | 176.2883 | 224.0593
841.1796 | 768.1796 | 305.6854 | 205.998 | 208.342 | 217.9161 | 202.6522 | 179.4476 | 176.3738 | 224.0803
842.181 | 769.181 | 305.6794 | 206.1185 | 208.4383 | 218.1299 | 202.7588 | 179.5426 | 176.4557 | 224.1116
843.1824 | 770.1824 | 305.6055 | 206.2348 | 208.5426 | 218.1588 | 202.8868 | 179.644 | 176.5373 | 224.1268
844.1839 | 771.1839 | 305.5367 | 206.3461 | 208.6385 | 218.3492 | 203.008 | 179.7463 | 176.6205 | 224.1876
845.1853 | 772.1853 | 305.456 | 206.4628 | 208.7453 | 218.5261 | 203.1271 | 179.8489 | 176.7075 | 224.2425
846.1767 | 773.1767 | 305.3427 | 206.5867 | 208.8573 | 218.7204 | 203.2472 | 179.9544 | 176.7892 | 224.2746
847.1782 | 774.1782 | 305.3062 | 206.6906 | 208.9795 | 218.6571 | 203.3665 | 180.0674 | 176.8771 | 224.3102
848.1796 | 775.1796 | 305.2729 | 206.8096 | 209.0882 | 218.6845 | 203.492 | 180.1668 | 176.9557 | 224.3752
849.1811 | 776.1811 | 305.368 | 206.9246 | 209.2135 | 218.7062 | 203.6131 | 180.2721 | 177.045 | 224.363
850.1825 | 777.1825 | 305.4035 | 207.042 | 209.3271 | 218.8561 | 203.732 | 180.3743 | 177.1376 | 224.4303
851.1839 | 778.1839 | 305.5059 | 207.1663 | 209.4387 | 218.8788 | 203.8644 | 180.4871 | 177.2153 | 224.4447
852.1854 | 779.1854 | 305.5708 | 207.2825 | 209.5453 | 218.9605 | 203.9755 | 180.5776 | 177.2965 | 224.5075
853.1868 | 780.1868 | 305.6035 | 207.4006 | 209.6596 | 218.9301 | 204.0972 | 180.6681 | 177.3778 | 224.547
854.1782 | 781.1782 | 305.6076 | 207.5149 | 209.7625 | 218.9667 | 204.2219 | 180.7633 | 177.4566 | 224.602
855.1797 | 782.1797 | 305.6296 | 207.6365 | 209.8757 | 219.1226 | 204.3273 | 180.8482 | 177.5376 | 224.6325
856.1811 | 783.1811 | 305.545 | 207.761 | 209.9851 | 219.1738 | 204.4593 | 180.9453 | 177.6288 | 224.6604
857.1826 | 784.1826 | 305.4598 | 207.8726 | 210.0913 | 219.2184 | 204.5619 | 181.036 | 177.7065 | 224.7359
858.184 | 785.184 | 305.4 | 207.9972 | 210.1999 | 219.2651 | 204.7007 | 181.1287 | 177.7775 | 224.7432
859.1854 | 786.1854 | 305.3504 | 208.1132 | 210.3109 | 219.2841 | 204.8137 | 181.2158 | 177.8451 | 224.8344
860.1869 | 787.1869 | 305.2824 | 208.2318 | 210.4204 | 219.4333 | 204.9254 | 181.3073 | 177.9258 | 224.8463
861.1783 | 788.1783 | 305.2721 | 208.353 | 210.52 | 219.4616 | 205.0439 | 181.4026 | 177.9996 | 224.8829
862.1798 | 789.1798 | 305.3615 | 208.4674 | 210.6336 | 219.5992 | 205.1605 | 181.4937 | 178.0725 | 224.9337
863.1812 | 790.1812 | 305.3984 | 208.5843 | 210.7438 | 219.7335 | 205.283 | 181.5922 | 178.1574 | 224.9732
864.1826 | 791.1826 | 305.5073 | 208.7009 | 210.8449 | 219.8833 | 205.3865 | 181.6955 | 178.2256 | 225.0151
865.1841 | 792.1841 | 305.6099 | 208.8162 | 210.9554 | 219.9595 | 205.5174 | 181.7975 | 178.2952 | 225.0453
866.1855 | 793.1855 | 305.7437 | 208.9307 | 211.0449 | 219.5276 | 205.6444 | 181.9055 | 178.3682 | 225.0704
867.1769 | 794.1769 | 305.8364 | 209.0523 | 211.1682 | 219.806 | 205.7495 | 182.0067 | 178.4479 | 225.1192
868.1984 | 795.1984 | 305.9454 | 209.1635 | 211.2765 | 219.2306 | 205.875 | 182.112 | 178.5341 | 225.1763
869.1798 | 796.1798 | 305.9483 | 209.2656 | 211.3862 | 219.0616 | 205.9936 | 182.211 | 178.6145 | 225.1984
870.1813 | 797.1813 | 305.9803 | 209.3703 | 211.5045 | 219.1243 | 206.1151 | 182.3232 | 178.6969 | 225.2344
871.1827 | 798.1827 | 306.011 | 209.4795 | 211.6159 | 218.6194 | 206.21 | 182.4255 | 178.7934 | 225.2669
872.1841 | 799.1841 | 306.056 | 209.5882 | 211.7051 | 218.597 | 206.3426 | 182.5245 | 178.88 | 225.3043
873.1856 | 800.1856 | 306.1509 | 209.6966 | 211.7888 | 218.6197 | 206.4568 | 182.6237 | 178.9689 | 225.3317
874.187 | 801.187 | 306.3116 | 209.8147 | 211.8871 | 218.8091 | 206.5646 | 182.7128 | 179.0609 | 225.3815
875.1784 | 802.1784 | 306.3027 | 209.9127 | 212.0079 | 219.3114 | 206.6796 | 182.8083 | 179.157 | 225.4184
876.1799 | 803.1799 | 306.2411 | 210.0172 | 212.1112 | 219.4104 | 206.8051 | 182.9083 | 179.2477 | 225.4206
877.1813 | 804.1813 | 306.2876 | 210.115 | 212.2166 | 219.6507 | 206.9084 | 183.0045 | 179.3439 | 225.485
878.1828 | 805.1828 | 306.3866 | 210.2285 | 212.3125 | 219.6096 | 207.0366 | 183.1126 | 179.4391 | 225.4968
879.1842 | 806.1842 | 306.4734 | 210.3232 | 212.4131 | 219.2575 | 207.1563 | 183.21 | 179.5322 | 225.5631
880.1856 | 807.1856 | 306.4571 | 210.4211 | 212.5174 | 219.641 | 207.2669 | 183.3165 | 179.6249 | 225.6061
881.1771 | 808.1771 | 306.5331 | 210.5207 | 212.6153 | 219.296 | 207.3935 | 183.4286 | 179.7231 | 225.6339
882.1785 | 809.1785 | 306.5006 | 210.6127 | 212.7035 | 218.8171 | 207.5018 | 183.5384 | 179.814 | 225.6628
883.18 | 810.18 | 306.5564 | 210.717 | 212.8156 | 219.2953 | 207.6159 | 183.6464 | 179.8912 | 225.7052
884.1814 | 811.1814 | 306.536 | 210.8205 | 212.9286 | 219.636 | 207.7373 | 183.7485 | 179.9711 | 225.7417
885.1828 | 812.1828 | 306.5405 | 210.9306 | 213.0435 | 219.485 | 207.8392 | 183.8631 | 180.0508 | 225.768
886.1843 | 813.1843 | 306.4503 | 211.0303 | 213.1426 | 219.8828 | 207.9553 | 183.9669 | 180.1255 | 225.8122
887.1857 | 814.1857 | 306.3429 | 211.126 | 213.2383 | 219.8245 | 208.0721 | 184.0773 | 180.2029 | 225.8185
888.1771 | 815.1771 | 306.2873 | 211.2372 | 213.3258 | 220.0825 | 208.1846 | 184.1772 | 180.2825 | 225.8828
889.1786 | 816.1786 | 306.2178 | 211.3263 | 213.4347 | 220.2757 | 208.2992 | 184.2756 | 180.3532 | 225.8888
890.18 | 817.18 | 306.1054 | 211.4407 | 213.5427 | 220.4898 | 208.4123 | 184.3768 | 180.4282 | 225.9553
891.1815 | 818.1815 | 305.942 | 211.5393 | 213.6347 | 220.3568 | 208.5324 | 184.4741 | 180.5043 | 225.9945
892.1829 | 819.1829 | 305.8393 | 211.6592 | 213.7428 | 220.0008 | 208.634 | 184.5674 | 180.578 | 226.0042
893.1843 | 820.1843 | 305.8159 | 211.7674 | 213.8396 | 220.3146 | 208.7526 | 184.6651 | 180.6522 | 226.0611
894.1758 | 821.1758 | 305.812 | 211.873 | 213.9483 | 220.4887 | 208.8787 | 184.7646 | 180.7333 | 226.0674
895.1872 | 822.1872 | 305.8365 | 211.9899 | 214.0602 | 220.6939 | 208.9908 | 184.8528 | 180.8132 | 226.1377
896.1786 | 823.1786 | 305.8468 | 212.0962 | 214.166 | 220.7888 | 209.0959 | 184.9351 | 180.8981 | 226.1556
897.1801 | 824.1801 | 305.8509 | 212.2164 | 214.269 | 220.6686 | 209.219 | 185.0268 | 180.9734 | 226.2125
898.1815 | 825.1815 | 305.7639 | 212.3245 | 214.3623 | 220.7731 | 209.3272 | 185.1055 | 181.0451 | 226.2261
899.183 | 826.183 | 305.7223 | 212.4408 | 214.477 | 220.651 | 209.4518 | 185.1865 | 181.114 | 226.2646
900.1844 | 827.1844 | 305.6067 | 212.5506 | 214.5824 | 220.0594 | 209.5551 | 185.2735 | 181.1909 | 226.2952
901.1858 | 828.1858 | 305.5268 | 212.6703 | 214.6974 | 219.8336 | 209.6674 | 185.3631 | 181.2605 | 226.3294
902.1873 | 829.1873 | 305.3521 | 212.7851 | 214.8003 | 219.3407 | 209.7782 | 185.4397 | 181.3244 | 226.3891
903.1787 | 830.1787 | 305.1455 | 212.9025 | 214.8969 | 218.5538 | 209.8935 | 185.5191 | 181.3935 | 226.4207
904.1801 | 831.1801 | 305.1475 | 213.0154 | 214.9829 | 219.3 | 209.9922 | 185.6059 | 181.4519 | 226.4514
905.1816 | 832.1816 | 305.2071 | 213.125 | 215.0913 | 219.4313 | 210.096 | 185.6802 | 181.5145 | 226.48
906.183 | 833.183 | 305.2981 | 213.2313 | 215.1798 | 219.4757 | 210.1996 | 185.7499 | 181.5823 | 226.5402
907.1845 | 834.1845 | 305.4221 | 213.3317 | 215.26 | 219.5178 | 210.306 | 185.8243 | 181.6483 | 226.5337
908.1859 | 835.1859 | 305.4661 | 213.4387 | 215.3406 | 219.5921 | 210.4159 | 185.8937 | 181.7235 | 226.5706
909.1773 | 836.1773 | 305.377 | 213.5361 | 215.433 | 219.6972 | 210.5218 | 185.9665 | 181.8029 | 226.6051
910.1788 | 837.1788 | 305.3376 | 213.6296 | 215.5226 | 219.4539 | 210.6243 | 186.035 | 181.8757 | 226.6198
911.1802 | 838.1802 | 305.3724 | 213.7212 | 215.623 | 218.8149 | 210.7319 | 186.1079 | 181.9512 | 226.6627
912.1817 | 839.1817 | 305.4615 | 213.8371 | 215.7234 | 219.3649 | 210.8385 | 186.1816 | 182.0359 | 226.6861
913.1831 | 840.1831 | 305.3647 | 213.9322 | 215.7964 | 219.6965 | 210.9272 | 186.2663 | 182.1137 | 226.7306
914.1845 | 841.1845 | 305.3111 | 214.0338 | 215.8861 | 219.3615 | 211.041 | 186.3516 | 182.194 | 226.7572
915.176 | 842.176 | 305.3511 | 214.1427 | 215.9594 | 219.7736 | 211.1327 | 186.4357 | 182.2704 | 226.7814
916.1874 | 843.1874 | 305.3365 | 214.2488 | 216.0497 | 219.9994 | 211.2452 | 186.5246 | 182.3409 | 226.8428
917.1788 | 844.1788 | 305.3258 | 214.3505 | 216.1571 | 220.1311 | 211.3415 | 186.6016 | 182.4141 | 226.8721
918.1803 | 845.1803 | 305.2188 | 214.4431 | 216.2658 | 220.3389 | 211.4453 | 186.6917 | 182.4923 | 226.894
919.1817 | 846.1817 | 305.1781 | 214.5375 | 216.3704 | 220.2575 | 211.5499 | 186.7799 | 182.5714 | 226.9111
920.1832 | 847.1832 | 305.2115 | 214.6374 | 216.4589 | 220.1551 | 211.6403 | 186.858 | 182.6431 | 226.9289
921.1846 | 848.1846 | 305.2068 | 214.737 | 216.5704 | 220.5021 | 211.741 | 186.949 | 182.7221 | 226.9751
922.176 | 849.176 | 305.1588 | 214.83 | 216.6696 | 220.8245 | 211.8429 | 187.0314 | 182.7862 | 226.9889
923.1775 | 850.1775 | 305.2042 | 214.9418 | 216.7916 | 220.9176 | 211.9412 | 187.1184 | 182.8505 | 227.0283
924.1789 | 851.1789 | 305.2765 | 215.0457 | 216.9118 | 221.1274 | 212.0281 | 187.1901 | 182.9176 | 227.075
925.1803 | 852.1803 | 305.3356 | 215.147 | 217.029 | 221.1735 | 212.1368 | 187.2606 | 182.9781 | 227.1106
926.1818 | 853.1818 | 305.326 | 215.2489 | 217.1354 | 220.5237 | 212.2312 | 187.3369 | 183.0489 | 227.1479
927.1832 | 854.1832 | 305.3432 | 215.3458 | 217.2432 | 220.0721 | 212.3273 | 187.4049 | 183.1219 | 227.1936
928.1847 | 855.1847 | 305.384 | 215.4407 | 217.3385 | 219.4649 | 212.4224 | 187.4801 | 183.1995 | 227.2251
929.1861 | 856.1861 | 305.4737 | 215.5428 | 217.4316 | 219.6092 | 212.5275 | 187.5515 | 183.2771 | 227.257
930.1775 | 857.1775 | 305.5627 | 215.6362 | 217.5231 | 220.1516 | 212.6226 | 187.6221 | 183.3552 | 227.298
931.179 | 858.179 | 305.6235 | 215.7174 | 217.6047 | 220.522 | 212.7115 | 187.6903 | 183.4288 | 227.3255
932.1804 | 859.1804 | 305.6729 | 215.8028 | 217.683 | 220.7414 | 212.8191 | 187.768 | 183.5073 | 227.3534
933.1818 | 860.1818 | 305.6875 | 215.8943 | 217.7727 | 220.8838 | 212.9199 | 187.8451 | 183.5817 | 227.3801
934.1833 | 861.1833 | 305.7422 | 215.9812 | 217.8637 | 221.0402 | 213.0134 | 187.9258 | 183.651 | 227.3955
935.1847 | 862.1847 | 305.7526 | 216.0638 | 217.9684 | 221.1153 | 213.1001 | 188.0054 | 183.7206 | 227.4368
936.1762 | 863.1762 | 305.7923 | 216.141 | 218.0743 | 221.2546 | 213.2033 | 188.088 | 183.8074 | 227.4737
937.1776 | 864.1776 | 305.8862 | 216.2203 | 218.1583 | 221.2068 | 213.3004 | 188.1774 | 183.8876 | 227.5028
938.179 | 865.179 | 305.9824 | 216.3014 | 218.2389 | 221.484 | 213.3994 | 188.2611 | 183.9686 | 227.5414
939.1805 | 866.1805 | 305.9515 | 216.3816 | 218.3271 | 221.1811 | 213.4811 | 188.3474 | 184.041 | 227.5673
940.1819 | 867.1819 | 306.0157 | 216.4658 | 218.4441 | 221.6159 | 213.5725 | 188.4342 | 184.1214 | 227.6148
941.1834 | 868.1834 | 306.1573 | 216.5483 | 218.5581 | 221.4008 | 213.66 | 188.5325 | 184.183 | 227.6463
942.1848 | 869.1848 | 306.2991 | 216.6378 | 218.6795 | 221.6373 | 213.7473 | 188.6178 | 184.2644 | 227.7074
943.1862 | 870.1862 | 306.3724 | 216.7395 | 218.7966 | 221.4521 | 213.8405 | 188.6994 | 184.3435 | 227.7242
944.1877 | 871.1877 | 306.3345 | 216.8355 | 218.9113 | 221.81 | 213.9237 | 188.788 | 184.4182 | 227.7964
945.1791 | 872.1791 | 306.2968 | 216.9325 | 219.0094 | 221.6659 | 214.0218 | 188.8769 | 184.5011 | 227.8277
946.1805 | 873.1805 | 306.2362 | 217.0362 | 219.1183 | 221.7579 | 214.1127 | 188.9782 | 184.5912 | 227.87
947.182 | 874.182 | 306.2249 | 217.1373 | 219.2147 | 221.9225 | 214.1995 | 189.0718 | 184.6805 | 227.9135
948.1834 | 875.1834 | 306.2253 | 217.2458 | 219.3314 | 221.8014 | 214.2968 | 189.1616 | 184.7661 | 227.9415
949.1849 | 876.1849 | 306.2688 | 217.3418 | 219.454 | 222.1476 | 214.3721 | 189.2491 | 184.8474 | 227.976
950.1863 | 877.1863 | 306.3717 | 217.4569 | 219.5705 | 222.1395 | 214.4664 | 189.3288 | 184.917 | 228.019
951.1777 | 878.1777 | 306.4751 | 217.5605 | 219.6785 | 222.2147 | 214.5567 | 189.405 | 184.9982 | 228.062
952.1792 | 879.1792 | 306.3681 | 217.6699 | 219.7832 | 222.4091 | 214.6403 | 189.4922 | 185.065 | 228.1013
953.1806 | 880.1806 | 306.3396 | 217.7672 | 219.8847 | 222.498 | 214.7301 | 189.5633 | 185.1399 | 228.1327
954.182 | 881.182 | 306.3098 | 217.866 | 219.9709 | 222.5787 | 214.8219 | 189.6441 | 185.1998 | 228.177
955.1835 | 882.1835 | 306.224 | 217.9785 | 220.0579 | 222.9006 | 214.9061 | 189.7237 | 185.2795 | 228.2086
956.1849 | 883.1849 | 306.061 | 218.0905 | 220.1645 | 222.7744 | 214.9964 | 189.8045 | 185.3494 | 228.2443
957.1764 | 884.1764 | 305.9444 | 218.19 | 220.2625 | 222.6985 | 215.0798 | 189.8683 | 185.4093 | 228.2686
958.1778 | 885.1778 | 305.8148 | 218.289 | 220.384 | 222.9841 | 215.1661 | 189.9402 | 185.4759 | 228.3042
959.1792 | 886.1792 | 305.6794 | 218.395 | 220.4707 | 222.7765 | 215.262 | 190.0018 | 185.5393 | 228.344
960.1807 | 887.1807 | 305.7195 | 218.4947 | 220.5735 | 222.8391 | 215.3435 | 190.0746 | 185.6006 | 228.3807
961.1821 | 888.1821 | 305.8734 | 218.5892 | 220.667 | 223.1257 | 215.4411 | 190.1433 | 185.6741 | 228.4126
962.1836 | 889.1836 | 305.9436 | 218.6816 | 220.7639 | 223.1254 | 215.5204 | 190.2036 | 185.7409 | 228.4404
963.185 | 890.185 | 306.0019 | 218.7768 | 220.8588 | 223.1405 | 215.617 | 190.2575 | 185.8229 | 228.486
964.1864 | 891.1864 | 305.8781 | 218.8827 | 220.9561 | 223.4051 | 215.6931 | 190.3303 | 185.8855 | 228.516
965.1779 | 892.1779 | 305.8271 | 218.9743 | 221.0541 | 223.4884 | 215.7884 | 190.3907 | 185.9507 | 228.5724
966.1793 | 893.1793 | 305.8061 | 219.0797 | 221.1329 | 223.4243 | 215.8765 | 190.4494 | 186.0115 | 228.5879
967.1807 | 894.1807 | 305.8013 | 219.1776 | 221.2235 | 223.4134 | 215.9727 | 190.515 | 186.0735 | 228.5936
968.1822 | 895.1822 | 305.7686 | 219.2901 | 221.2941 | 223.6739 | 216.0546 | 190.5832 | 186.1369 | 228.6292
969.1836 | 896.1836 | 305.6502 | 219.389 | 221.3816 | 223.7338 | 216.1341 | 190.637 | 186.2015 | 228.6701
970.1851 | 897.1851 | 305.7328 | 219.4861 | 221.4564 | 223.887 | 216.2176 | 190.7042 | 186.2745 | 228.7012
971.1765 | 898.1765 | 305.8022 | 219.5834 | 221.5557 | 224.1346 | 216.313 | 190.7569 | 186.3429 | 228.7283
972.1779 | 899.1779 | 305.9284 | 219.6846 | 221.6555 | 224.2293 | 216.4034 | 190.8133 | 186.4091 | 228.7606
973.1794 | 900.1794 | 305.9133 | 219.7842 | 221.7577 | 224.2428 | 216.4817 | 190.8627 | 186.464 | 228.8116
974.1808 | 901.1808 | 305.8348 | 219.8769 | 221.8565 | 224.4591 | 216.579 | 190.9196 | 186.5228 | 228.8463
975.1822 | 902.1822 | 305.8281 | 219.9723 | 221.9429 | 224.3224 | 216.6639 | 190.9724 | 186.5802 | 228.8759
976.1837 | 903.1837 | 305.9051 | 220.0762 | 222.0318 | 224.5849 | 216.7495 | 191.0299 | 186.636 | 228.9167
977.1851 | 904.1851 | 305.9107 | 220.1772 | 222.1323 | 224.6915 | 216.8381 | 191.1021 | 186.691 | 228.9396
978.1765 | 905.1765 | 305.8674 | 220.2766 | 222.2333 | 224.6396 | 216.9231 | 191.1639 | 186.7493 | 228.9869
979.178 | 906.178 | 305.8142 | 220.3668 | 222.3211 | 224.2756 | 217.0046 | 191.2177 | 186.8078 | 229.0184
980.1794 | 907.1794 | 305.8386 | 220.4613 | 222.4109 | 224.7767 | 217.0931 | 191.2696 | 186.8681 | 229.0535
981.1809 | 908.1809 | 305.7351 | 220.5539 | 222.4934 | 224.3608 | 217.1878 | 191.3202 | 186.9294 | 229.0554
982.1823 | 909.1823 | 305.6859 | 220.6329 | 222.5753 | 224.7408 | 217.2731 | 191.3582 | 186.9966 | 229.0869
983.1837 | 910.1837 | 305.6752 | 220.7194 | 222.6542 | 224.7347 | 217.3564 | 191.4111 | 187.0552 | 229.1275
984.1852 | 911.1852 | 305.64 | 220.7962 | 222.7437 | 224.8297 | 217.4539 | 191.4685 | 187.1126 | 229.1662
985.1866 | 912.1866 | 305.63 | 220.8779 | 222.8002 | 224.8255 | 217.5416 | 191.5263 | 187.1755 | 229.1854
986.1781 | 913.1781 | 305.651 | 220.9542 | 222.8566 | 224.7766 | 217.6299 | 191.5811 | 187.2401 | 229.2083
987.1795 | 914.1795 | 305.6777 | 221.0341 | 222.9202 | 224.8496 | 217.7173 | 191.6451 | 187.3136 | 229.2424
988.1809 | 915.1809 | 305.674 | 221.1131 | 223.0031 | 224.8448 | 217.8034 | 191.6969 | 187.3807 | 229.27
989.1824 | 916.1824 | 305.7719 | 221.1804 | 223.0724 | 225.0095 | 217.893 | 191.7513 | 187.4537 | 229.2887
990.1838 | 917.1838 | 305.984 | 221.2549 | 223.1532 | 224.9697 | 217.9825 | 191.8095 | 187.5282 | 229.3255
991.1853 | 918.1853 | 306.2022 | 221.3215 | 223.2352 | 224.8483 | 218.072 | 191.8603 | 187.5976 | 229.3388
992.1867 | 919.1867 | 306.3854 | 221.3899 | 223.3119 | 225.0226 | 218.157 | 191.9103 | 187.676 | 229.3975
993.1781 | 920.1781 | 306.4377 | 221.4608 | 223.3998 | 225.1384 | 218.2451 | 191.9582 | 187.7389 | 229.418
994.1796 | 921.1796 | 306.5077 | 221.5255 | 223.4819 | 225.1283 | 218.3272 | 192.009 | 187.8077 | 229.4526
995.181 | 922.181 | 306.529 | 221.5957 | 223.578 | 225.0261 | 218.4048 | 192.0457 | 187.8771 | 229.4865
996.1824 | 923.1824 | 306.458 | 221.672 | 223.6778 | 225.062 | 218.4881 | 192.0851 | 187.9566 | 229.5128
997.1839 | 924.1839 | 306.4226 | 221.7545 | 223.7776 | 225.1201 | 218.5842 | 192.1191 | 188.0494 | 229.5565
998.1853 | 925.1853 | 306.4985 | 221.8275 | 223.8582 | 225.1729 | 218.6573 | 192.1456 | 188.141 | 229.5754
999.1767 | 926.1767 | 306.5292 | 221.9095 | 223.9385 | 225.3818 | 218.7349 | 192.1919 | 188.2193 | 229.594
1000.1782 | 927.1782 | 306.6119 | 221.986 | 224.0012 | 225.3113 | 218.82 | 192.2261 | 188.2986 | 229.6402
1001.1796 | 928.1796 | 306.5661 | 222.0653 | 224.0907 | 225.55 | 218.9006 | 192.2599 | 188.3747 | 229.6732
1002.1811 | 929.1811 | 306.6371 | 222.1393 | 224.1786 | 225.2473 | 218.9789 | 192.3055 | 188.4434 | 229.7179
1003.1825 | 930.1825 | 306.7322 | 222.2157 | 224.25 | 225.4323 | 219.0563 | 192.3549 | 188.5203 | 229.7345
1004.1839 | 931.1839 | 306.7452 | 222.2885 | 224.3411 | 225.6122 | 219.1349 | 192.4161 | 188.6029 | 229.762
1005.1854 | 932.1854 | 306.7864 | 222.3616 | 224.434 | 225.6304 | 219.2097 | 192.4864 | 188.6788 | 229.784
1006.1868 | 933.1868 | 306.7874 | 222.4387 | 224.5205 | 225.7234 | 219.2862 | 192.5519 | 188.7439 | 229.8155
1007.1783 | 934.1783 | 306.8334 | 222.5213 | 224.5965 | 225.728 | 219.3815 | 192.6155 | 188.8237 | 229.8527
1008.1797 | 935.1797 | 306.888 | 222.5965 | 224.6916 | 225.6048 | 219.4508 | 192.6781 | 188.8848 | 229.8766
1009.1811 | 936.1811 | 306.8972 | 222.6812 | 224.7736 | 225.8224 | 219.5325 | 192.7402 | 188.9498 | 229.9131
1010.1826 | 937.1826 | 306.9131 | 222.7661 | 224.8552 | 225.9297 | 219.6125 | 192.8025 | 189.014 | 229.9474
1011.184 | 938.184 | 306.8971 | 222.8449 | 224.9313 | 225.8196 | 219.6933 | 192.8672 | 189.0862 | 230.0037
1012.1855 | 939.1855 | 306.754 | 222.9275 | 224.999 | 226.0787 | 219.7793 | 192.9234 | 189.1668 | 230.037
1013.1869 | 940.1869 | 306.6465 | 223.0064 | 225.0676 | 226.2802 | 219.8559 | 192.9718 | 189.2488 | 230.0603
1014.1783 | 941.1783 | 306.5758 | 223.0719 | 225.1272 | 226.3573 | 219.9438 | 193.0256 | 189.3341 | 230.0819
1015.1798 | 942.1798 | 306.5591 | 223.1338 | 225.1842 | 226.4528 | 220.0191 | 193.0744 | 189.4123 | 230.1007
1016.1812 | 943.1812 | 306.6211 | 223.1853 | 225.2468 | 226.4135 | 220.0958 | 193.1267 | 189.4832 | 230.118
1017.1826 | 944.1826 | 306.6309 | 223.239 | 225.3165 | 226.4081 | 220.1737 | 193.1855 | 189.5601 | 230.136
1018.1841 | 945.1841 | 306.614 | 223.2827 | 225.3741 | 226.4608 | 220.2424 | 193.2421 | 189.6254 | 230.1723
1019.2156 | 946.2156 | 306.5513 | 223.3463 | 225.4345 | 226.4567 | 220.335 | 193.3102 | 189.6935 | 230.2027
1020.1769 | 947.1769 | 306.5559 | 223.3957 | 225.49 | 226.6429 | 220.3961 | 193.38 | 189.755 | 230.2127
1021.1784 | 948.1784 | 306.5278 | 223.4699 | 225.5688 | 226.4998 | 220.4582 | 193.4523 | 189.8222 | 230.2526
1022.1798 | 949.1798 | 306.5201 | 223.5309 | 225.6517 | 226.5094 | 220.5492 | 193.5247 | 189.8888 | 230.2698
1023.1813 | 950.1813 | 306.5129 | 223.6046 | 225.7333 | 226.4509 | 220.6362 | 193.5857 | 189.96 | 230.2945
1024.1827 | 951.1827 | 306.492 | 223.6817 | 225.8119 | 226.5121 | 220.7054 | 193.6553 | 190.0244 | 230.3188
1025.1841 | 952.1841 | 306.4636 | 223.7638 | 225.8887 | 226.3668 | 220.7878 | 193.7093 | 190.0899 | 230.343
1026.1856 | 953.1856 | 306.4459 | 223.8382 | 225.969 | 226.5242 | 220.8658 | 193.7799 | 190.1416 | 230.3441
1027.187 | 954.187 | 306.448 | 223.9165 | 226.0468 | 226.7174 | 220.9385 | 193.849 | 190.2079 | 230.3922
1028.1784 | 955.1784 | 306.3416 | 223.992 | 226.1298 | 226.6282 | 221.0231 | 193.914 | 190.2636 | 230.4174
1029.1799 | 956.1799 | 306.3163 | 224.0572 | 226.2137 | 226.6808 | 221.1026 | 193.9854 | 190.3291 | 230.4465
1030.1813 | 957.1813 | 306.3618 | 224.1214 | 226.2846 | 226.7259 | 221.1724 | 194.0391 | 190.3919 | 230.4702
1031.1828 | 958.1828 | 306.3457 | 224.2015 | 226.3589 | 226.8698 | 221.2483 | 194.1007 | 190.4723 | 230.4751
1032.1842 | 959.1842 | 306.3166 | 224.2614 | 226.4247 | 226.7819 | 221.3161 | 194.1548 | 190.5484 | 230.5096
1033.1856 | 960.1856 | 306.3333 | 224.3281 | 226.4994 | 226.6899 | 221.3985 | 194.2167 | 190.6332 | 230.5319
1034.1871 | 961.1871 | 306.3651 | 224.403 | 226.5612 | 226.7344 | 221.4649 | 194.278 | 190.7041 | 230.5288
1035.1785 | 962.1785 | 306.3 | 224.4587 | 226.6188 | 226.6771 | 221.5396 | 194.3389 | 190.7838 | 230.5435
1036.18 | 963.18 | 306.1777 | 224.5155 | 226.6863 | 226.8396 | 221.6091 | 194.4073 | 190.858 | 230.5681
1037.1814 | 964.1814 | 306.1691 | 224.5839 | 226.749 | 227.0327 | 221.6742 | 194.4674 | 190.9145 | 230.5817
1038.1828 | 965.1828 | 306.0792 | 224.6433 | 226.814 | 227.1105 | 221.75 | 194.5267 | 190.9748 | 230.61
1039.1843 | 966.1843 | 305.9271 | 224.7013 | 226.8736 | 226.913 | 221.8161 | 194.5782 | 191.0215 | 230.6234
1040.1857 | 967.1857 | 305.7677 | 224.7722 | 226.9336 | 226.6192 | 221.8757 | 194.6305 | 191.0753 | 230.6455
1041.1771 | 968.1771 | 305.656 | 224.8482 | 227.0107 | 226.8789 | 221.9454 | 194.6772 | 191.1335 | 230.6629
1042.1786 | 969.1786 | 305.58 | 224.9248 | 227.0734 | 227.1996 | 222.0131 | 194.7255 | 191.1968 | 230.6803
1043.18 | 970.18 | 305.5201 | 224.9943 | 227.1321 | 227.1211 | 222.0916 | 194.7714 | 191.2632 | 230.6928
1044.1815 | 971.1815 | 305.473 | 225.0744 | 227.2054 | 227.3503 | 222.1557 | 194.8328 | 191.3168 | 230.7094
1045.1829 | 972.1829 | 305.4304 | 225.1414 | 227.2726 | 227.4815 | 222.2259 | 194.8898 | 191.3724 | 230.7383
1046.1843 | 973.1843 | 305.4775 | 225.2172 | 227.3381 | 227.6374 | 222.2932 | 194.9372 | 191.432 | 230.7758
1047.1858 | 974.1858 | 305.5222 | 225.2936 | 227.3947 | 227.7482 | 222.3614 | 195.0037 | 191.4858 | 230.7882
1048.1872 | 975.1872 | 305.5046 | 225.3599 | 227.4569 | 227.8062 | 222.4342 | 195.0583 | 191.5352 | 230.8275
1049.1786 | 976.1786 | 305.6105 | 225.4264 | 227.5314 | 227.831 | 222.4946 | 195.1172 | 191.5865 | 230.844
1050.1801 | 977.1801 | 305.7502 | 225.4944 | 227.5956 | 227.9477 | 222.5648 | 195.1769 | 191.6374 | 230.8664
1051.1815 | 978.1815 | 305.9393 | 225.5666 | 227.66 | 227.9725 | 222.6264 | 195.2291 | 191.6903 | 230.8924
1052.183 | 979.183 | 305.9429 | 225.6374 | 227.7274 | 227.9727 | 222.6959 | 195.2804 | 191.7414 | 230.9082
1053.1844 | 980.1844 | 305.8918 | 225.7022 | 227.7874 | 228.1179 | 222.7619 | 195.3306 | 191.7935 | 230.9405
1054.1858 | 981.1858 | 305.9302 | 225.7659 | 227.8542 | 228.2339 | 222.8353 | 195.3898 | 191.8517 | 230.9525
1055.1773 | 982.1773 | 305.9459 | 225.8373 | 227.9128 | 228.2511 | 222.9023 | 195.4447 | 191.9046 | 230.9741
1056.1787 | 983.1787 | 305.9456 | 225.8979 | 227.9755 | 228.2409 | 222.9684 | 195.5015 | 191.9552 | 231.0032
1057.1802 | 984.1802 | 306.0268 | 225.9659 | 228.0266 | 228.4395 | 223.0422 | 195.5538 | 192.0144 | 231.0292
1058.1816 | 985.1816 | 306.0986 | 226.0341 | 228.0941 | 228.4153 | 223.1062 | 195.6108 | 192.0719 | 231.067
1059.183 | 986.183 | 306.1986 | 226.0922 | 228.1476 | 228.3434 | 223.1655 | 195.6719 | 192.1302 | 231.0801
1060.1845 | 987.1845 | 306.1554 | 226.1549 | 228.211 | 228.4752 | 223.238 | 195.7225 | 192.1884 | 231.1039
1061.1859 | 988.1859 | 306.1104 | 226.215 | 228.2517 | 228.6333 | 223.3046 | 195.785 | 192.2471 | 231.1424
1062.1773 | 989.1773 | 306.0406 | 226.2635 | 228.3005 | 228.7353 | 223.3738 | 195.8429 | 192.3024 | 231.1575
1063.1788 | 990.1788 | 306.0332 | 226.3105 | 228.3562 | 228.8457 | 223.445 | 195.9106 | 192.356 | 231.1938
1064.1802 | 991.1802 | 306.1153 | 226.3623 | 228.4015 | 228.8621 | 223.4992 | 195.9756 | 192.4048 | 231.2275
1065.1817 | 992.1817 | 306.189 | 226.4243 | 228.4434 | 228.7795 | 223.5719 | 196.038 | 192.4506 | 231.2487
1066.1831 | 993.1831 | 306.2496 | 226.4894 | 228.5009 | 228.8903 | 223.6376 | 196.0972 | 192.501 | 231.2579
1067.1845 | 994.1845 | 306.2472 | 226.5644 | 228.5534 | 229.0277 | 223.7053 | 196.1535 | 192.5465 | 231.2893
1068.186 | 995.186 | 306.2531 | 226.6382 | 228.6141 | 229.1386 | 223.7718 | 196.2116 | 192.6008 | 231.323
1069.1874 | 996.1874 | 306.2853 | 226.7249 | 228.6625 | 229.0708 | 223.8323 | 196.2589 | 192.6565 | 231.3491
1070.1788 | 997.1788 | 306.3376 | 226.8101 | 228.7209 | 229.224 | 223.9034 | 196.3185 | 192.7094 | 231.3727
1071.1803 | 998.1803 | 306.3632 | 226.8854 | 228.7732 | 229.1947 | 223.9579 | 196.3548 | 192.7588 | 231.4124
1072.1817 | 999.1817 | 306.3506 | 226.9558 | 228.8169 | 229.223 | 224.0364 | 196.4105 | 192.825 | 231.4312
1073.1832 | 1000.1832 | 306.4267 | 227.0278 | 228.8751 | 229.3344 | 224.1043 | 196.4532 | 192.8855 | 231.4874
1074.1846 | 1001.1846 | 306.392 | 227.0967 | 228.9153 | 229.5807 | 224.1668 | 196.5016 | 192.9458 | 231.4995
1075.186 | 1002.186 | 306.4614 | 227.1626 | 228.9568 | 229.5136 | 224.2205 | 196.542 | 192.9994 | 231.5206
1076.1775 | 1003.1775 | 306.5233 | 227.2295 | 229.0164 | 229.5218 | 224.3036 | 196.5942 | 193.0509 | 231.5458
1077.1789 | 1004.1789 | 306.5433 | 227.2974 | 229.0836 | 229.5713 | 224.3642 | 196.6376 | 193.1 | 231.5935
1078.1803 | 1005.1803 | 306.5077 | 227.3651 | 229.1475 | 229.4414 | 224.417 | 196.6813 | 193.152 | 231.6086
1079.1818 | 1006.1818 | 306.5245 | 227.4476 | 229.2134 | 229.5658 | 224.5023 | 196.7399 | 193.2042 | 231.6171
1080.1832 | 1007.1832 | 306.4609 | 227.5143 | 229.2841 | 229.2276 | 224.5653 | 196.7964 | 193.26 | 231.6563
1081.1847 | 1008.1847 | 306.4381 | 227.5765 | 229.3316 | 229.2193 | 224.6216 | 196.8521 | 193.3113 | 231.6479
1082.1861 | 1009.1861 | 306.3414 | 227.63 | 229.377 | 229.4223 | 224.6965 | 196.9077 | 193.3621 | 231.6912
1083.1775 | 1010.1775 | 306.3782 | 227.6883 | 229.4301 | 229.5719 | 224.7574 | 196.9712 | 193.4261 | 231.7206
1084.179 | 1011.179 | 306.401 | 227.7466 | 229.4666 | 229.672 | 224.8139 | 197.025 | 193.4894 | 231.7459
1085.1804 | 1012.1804 | 306.4021 | 227.8087 | 229.5143 | 229.5552 | 224.8834 | 197.0847 | 193.5454 | 231.7786
1086.1819 | 1013.1819 | 306.4361 | 227.8752 | 229.563 | 229.7294 | 224.9471 | 197.1332 | 193.5953 | 231.8098
1087.1833 | 1014.1833 | 306.4092 | 227.9277 | 229.6198 | 229.7187 | 225.0066 | 197.1839 | 193.6554 | 231.8275
1088.1847 | 1015.1847 | 306.3431 | 227.9815 | 229.6624 | 229.9063 | 225.0763 | 197.2365 | 193.7285 | 231.8436
1089.1862 | 1016.1862 | 306.3309 | 228.018 | 229.7122 | 230.0275 | 225.1446 | 197.2907 | 193.7992 | 231.8616
1090.1776 | 1017.1776 | 306.376 | 228.0499 | 229.7388 | 229.8489 | 225.2078 | 197.3422 | 193.8728 | 231.8666
1091.179 | 1018.179 | 306.4161 | 228.0801 | 229.7806 | 230.0633 | 225.2725 | 197.4 | 193.9369 | 231.9165
1092.1805 | 1019.1805 | 306.3178 | 228.1111 | 229.8137 | 230.0742 | 225.3386 | 197.457 | 194.0109 | 231.9319
1093.1819 | 1020.1819 | 306.4001 | 228.1331 | 229.8526 | 229.9768 | 225.387 | 197.5193 | 194.0692 | 231.9693
1094.1834 | 1021.1834 | 306.448 | 228.1715 | 229.9075 | 229.9366 | 225.4685 | 197.5847 | 194.136 | 231.9733
1095.1848 | 1022.1848 | 306.4426 | 228.2065 | 229.9689 | 230.038 | 225.5128 | 197.639 | 194.1875 | 231.9848
1096.1762 | 1023.1762 | 306.3757 | 228.2447 | 230.0324 | 230.1633 | 225.5809 | 197.699 | 194.2566 | 232.0053
1097.1777 | 1024.1777 | 306.2249 | 228.2879 | 230.1023 | 230.2105 | 225.6355 | 197.7617 | 194.3109 | 232.0538
1098.1791 | 1025.1791 | 306.093 | 228.3417 | 230.1538 | 230.1661 | 225.704 | 197.8221 | 194.3749 | 232.0584
1099.1805 | 1026.1805 | 306.0808 | 228.3982 | 230.2301 | 230.2382 | 225.7578 | 197.8784 | 194.4238 | 232.0714
1100.182 | 1027.182 | 306.0834 | 228.4552 | 230.2838 | 230.2621 | 225.8156 | 197.9411 | 194.478 | 232.1106
1101.1834 | 1028.1834 | 306.1012 | 228.5164 | 230.348 | 229.8902 | 225.8851 | 198.0032 | 194.534 | 232.1074
1102.1849 | 1029.1849 | 306.1647 | 228.582 | 230.4212 | 229.9877 | 225.9448 | 198.0503 | 194.5787 | 232.163
1103.1863 | 1030.1863 | 306.1936 | 228.6397 | 230.4784 | 229.8517 | 226.0028 | 198.1099 | 194.6221 | 232.1748
1104.1777 | 1031.1777 | 306.2417 | 228.7092 | 230.5412 | 229.8686 | 226.0555 | 198.1582 | 194.6728 | 232.199
1105.1792 | 1032.1792 | 306.1968 | 228.7776 | 230.598 | 230.079 | 226.1238 | 198.2141 | 194.7208 | 232.226
1106.1806 | 1033.1806 | 306.1879 | 228.8255 | 230.6534 | 229.9639 | 226.1729 | 198.2552 | 194.7708 | 232.2523
1107.182 | 1034.182 | 306.1524 | 228.889 | 230.7217 | 229.7689 | 226.2349 | 198.3081 | 194.8167 | 232.2712
1108.1835 | 1035.1835 | 306.158 | 228.9376 | 230.7819 | 230.0095 | 226.2906 | 198.3628 | 194.8641 | 232.3015
1109.1849 | 1036.1849 | 306.164 | 228.9766 | 230.8166 | 230.1627 | 226.345 | 198.4102 | 194.9172 | 232.3005
1110.1864 | 1037.1864 | 306.1196 | 229.0047 | 230.8494 | 230.2826 | 226.4054 | 198.4698 | 194.969 | 232.3309
1111.1778 | 1038.1778 | 306.0666 | 229.0386 | 230.8939 | 230.303 | 226.4684 | 198.5223 | 195.0203 | 232.3423
1112.1792 | 1039.1792 | 306.1362 | 229.0716 | 230.9196 | 230.453 | 226.5163 | 198.5806 | 195.0841 | 232.3601
1113.1807 | 1040.1807 | 306.2304 | 229.1088 | 230.9592 | 230.1181 | 226.5787 | 198.6406 | 195.1444 | 232.3976
1114.1821 | 1041.1821 | 306.2383 | 229.1523 | 231.0071 | 230.2216 | 226.6258 | 198.7076 | 195.2085 | 232.4051
1115.1836 | 1042.1836 | 306.232 | 229.19 | 231.0459 | 230.4323 | 226.6945 | 198.767 | 195.2679 | 232.4328
1116.185 | 1043.185 | 306.2509 | 229.2252 | 231.0821 | 230.508 | 226.7477 | 198.8325 | 195.3295 | 232.4342
1117.1864 | 1044.1864 | 306.3036 | 229.2629 | 231.1255 | 230.7007 | 226.8045 | 198.8992 | 195.3797 | 232.4407
1118.1879 | 1045.1879 | 306.4274 | 229.3029 | 231.1671 | 230.7186 | 226.8591 | 198.9595 | 195.4313 | 232.4459
1119.1793 | 1046.1793 | 306.4305 | 229.3414 | 231.2011 | 230.816 | 226.9232 | 199.0162 | 195.483 | 232.4437
1120.1807 | 1047.1807 | 306.372 | 229.3824 | 231.2648 | 230.9123 | 226.9679 | 199.0734 | 195.5318 | 232.4712
1121.1822 | 1048.1822 | 306.3956 | 229.4324 | 231.2994 | 230.6917 | 227.0235 | 199.1332 | 195.5898 | 232.4835
1122.1836 | 1049.1836 | 306.4345 | 229.4858 | 231.3381 | 230.2696 | 227.0938 | 199.1838 | 195.6454 | 232.4989
1123.1851 | 1050.1851 | 306.3831 | 229.541 | 231.3855 | 230.5672 | 227.1358 | 199.2383 | 195.7049 | 232.5065
1124.1865 | 1051.1865 | 306.2925 | 229.6028 | 231.4203 | 230.6247 | 227.2047 | 199.3003 | 195.7536 | 232.5224
1125.1779 | 1052.1779 | 306.3214 | 229.6629 | 231.4596 | 230.5236 | 227.2566 | 199.3504 | 195.8126 | 232.525
1126.1794 | 1053.1794 | 306.3861 | 229.7242 | 231.4828 | 230.7596 | 227.3061 | 199.4034 | 195.8751 | 232.5442
1127.1808 | 1054.1808 | 306.3177 | 229.7852 | 231.5286 | 230.8991 | 227.3622 | 199.4492 | 195.9221 | 232.5605
1128.1822 | 1055.1822 | 306.3193 | 229.8422 | 231.5769 | 231.0013 | 227.4181 | 199.516 | 195.9703 | 232.5901
1129.1837 | 1056.1837 | 306.3838 | 229.9084 | 231.6168 | 231.0416 | 227.4711 | 199.566 | 196.0115 | 232.5845
1130.1851 | 1057.1851 | 306.4365 | 229.9714 | 231.6519 | 231.1818 | 227.5309 | 199.6208 | 196.0611 | 232.6012
1131.1766 | 1058.1766 | 306.4344 | 230.0301 | 231.6922 | 231.1475 | 227.5849 | 199.6838 | 196.0948 | 232.6162
1132.178 | 1059.178 | 306.396 | 230.087 | 231.7211 | 231.1413 | 227.6427 | 199.7437 | 196.1376 | 232.6231
1133.1794 | 1060.1794 | 306.3069 | 230.1542 | 231.7486 | 231.2855 | 227.6975 | 199.807 | 196.1791 | 232.6357
1134.1809 | 1061.1809 | 306.3093 | 230.2161 | 231.7693 | 231.3472 | 227.7471 | 199.873 | 196.2175 | 232.6427
1135.1823 | 1062.1823 | 306.333 | 230.2803 | 231.7929 | 231.3587 | 227.8036 | 199.9263 | 196.2584 | 232.6611
1136.1838 | 1063.1838 | 306.2512 | 230.3408 | 231.8132 | 231.4284 | 227.8639 | 199.9869 | 196.3012 | 232.6887
1137.1852 | 1064.1852 | 306.1131 | 230.4062 | 231.8388 | 231.5271 | 227.9061 | 200.0394 | 196.3401 | 232.7077
1138.1766 | 1065.1766 | 305.936 | 230.4626 | 231.8896 | 231.3585 | 227.9558 | 200.099 | 196.3852 | 232.6965
1139.1781 | 1066.1781 | 305.7742 | 230.5245 | 231.9302 | 231.3669 | 228.0057 | 200.1571 | 196.4276 | 232.7232
1140.1795 | 1067.1795 | 305.458 | 230.5906 | 231.9573 | 231.4905 | 228.0655 | 200.2173 | 196.4673 | 232.7429
1141.1809 | 1068.1809 | 305.2431 | 230.6465 | 231.9926 | 231.6034 | 228.1141 | 200.2591 | 196.518 | 232.7494
1142.1824 | 1069.1824 | 305.177 | 230.7 | 232.017 | 231.675 | 228.1628 | 200.3073 | 196.5643 | 232.7487
1143.1838 | 1070.1838 | 305.1184 | 230.7487 | 232.0608 | 231.8349 | 228.2029 | 200.3549 | 196.6088 | 232.7729
1144.1853 | 1071.1853 | 304.9721 | 230.7966 | 232.0763 | 231.8303 | 228.2537 | 200.3843 | 196.6683 | 232.7841
1145.1867 | 1072.1867 | 304.9797 | 230.8366 | 232.0777 | 231.8506 | 228.3123 | 200.4399 | 196.7138 | 232.7697
1146.1781 | 1073.1781 | 304.903 | 230.8661 | 232.0982 | 231.9245 | 228.3655 | 200.4851 | 196.7672 | 232.8039
1147.1796 | 1074.1796 | 304.7609 | 230.9088 | 232.1381 | 231.9947 | 228.4178 | 200.5321 | 196.8168 | 232.7911
1148.181 | 1075.181 | 304.6678 | 230.9314 | 232.1796 | 232.0431 | 228.4522 | 200.5773 | 196.8616 | 232.8031
1149.1824 | 1076.1824 | 304.6622 | 230.9596 | 232.2126 | 232.0268 | 228.4952 | 200.6343 | 196.9017 | 232.8166
1150.1839 | 1077.1839 | 304.7398 | 230.9884 | 232.2219 | 232.0532 | 228.5492 | 200.6803 | 196.9291 | 232.8108
1151.1853 | 1078.1853 | 304.8552 | 231.022 | 232.2352 | 232.1069 | 228.5921 | 200.7287 | 196.9577 | 232.8222
1152.1767 | 1079.1767 | 304.937 | 231.0345 | 232.2567 | 232.0847 | 228.6248 | 200.7759 | 196.9854 | 232.8269
1153.1782 | 1080.1782 | 304.8846 | 231.0736 | 232.2825 | 232.2301 | 228.6759 | 200.8158 | 197.0263 | 232.8178
1154.1796 | 1081.1796 | 304.9255 | 231.0951 | 232.3111 | 232.2639 | 228.7265 | 200.858 | 197.0558 | 232.8513
1155.1811 | 1082.1811 | 305.0488 | 231.1268 | 232.3485 | 232.3263 | 228.7694 | 200.9019 | 197.1029 | 232.8592
1156.1825 | 1083.1825 | 305.0253 | 231.1574 | 232.3983 | 232.4199 | 228.8063 | 200.9576 | 197.1386 | 232.87
1157.1839 | 1084.1839 | 305.039 | 231.1919 | 232.4261 | 232.2563 | 228.8571 | 201.0005 | 197.1851 | 232.8848
1158.1854 | 1085.1854 | 305.0995 | 231.2276 | 232.4465 | 232.2482 | 228.9086 | 201.0551 | 197.2237 | 232.894
1159.1868 | 1086.1868 | 305.1319 | 231.2808 | 232.4916 | 232.2717 | 228.9496 | 201.1068 | 197.2614 | 232.8983
1160.1783 | 1087.1783 | 305.2616 | 231.3354 | 232.5318 | 232.352 | 228.986 | 201.1571 | 197.3142 | 232.904
1161.1797 | 1088.1797 | 305.4286 | 231.3929 | 232.5652 | 232.3238 | 229.0382 | 201.1961 | 197.3577 | 232.9253
1162.1811 | 1089.1811 | 305.4203 | 231.4435 | 232.6063 | 232.3909 | 229.0713 | 201.2464 | 197.4049 | 232.9347
1163.1826 | 1090.1826 | 305.4704 | 231.4885 | 232.6509 | 232.438 | 229.1223 | 201.2897 | 197.4503 | 232.933
1164.184 | 1091.184 | 305.49 | 231.5356 | 232.6915 | 232.5174 | 229.1611 | 201.3297 | 197.4892 | 232.9483
1165.1855 | 1092.1855 | 305.4804 | 231.586 | 232.7429 | 232.5596 | 229.2111 | 201.3813 | 197.5256 | 232.9622
1166.1869 | 1093.1869 | 305.4557 | 231.6352 | 232.7881 | 232.4185 | 229.257 | 201.4424 | 197.5592 | 232.9586
1167.1783 | 1094.1783 | 305.5056 | 231.6858 | 232.8323 | 232.5932 | 229.3001 | 201.4932 | 197.5934 | 232.999
1168.1798 | 1095.1798 | 305.609 | 231.743 | 232.8692 | 232.6542 | 229.3316 | 201.5297 | 197.628 | 233.001
1169.1812 | 1096.1812 | 305.7148 | 231.7966 | 232.922 | 232.7104 | 229.3826 | 201.5773 | 197.6778 | 233.0243
1170.1826 | 1097.1826 | 305.841 | 231.8398 | 232.9482 | 232.7751 | 229.4268 | 201.6237 | 197.7178 | 233.0462
1171.1841 | 1098.1841 | 305.9644 | 231.8796 | 232.9695 | 232.9136 | 229.4756 | 201.6717 | 197.7677 | 233.0626
1172.1855 | 1099.1855 | 306.1227 | 231.9143 | 232.9873 | 232.7924 | 229.5144 | 201.7106 | 197.8114 | 233.0702
1173.1769 | 1100.1769 | 306.2902 | 231.9459 | 233.0007 | 232.9566 | 229.5538 | 201.7618 | 197.8507 | 233.0901
1174.1784 | 1101.1784 | 306.4064 | 231.9833 | 233.0376 | 232.8999 | 229.6024 | 201.8093 | 197.8849 | 233.1063
1175.1798 | 1102.1798 | 306.4954 | 232.0438 | 233.0622 | 232.9644 | 229.6414 | 201.8613 | 197.9226 | 233.136
1176.1813 | 1103.1813 | 306.4447 | 232.1026 | 233.0893 | 232.9896 | 229.6917 | 201.9117 | 197.9535 | 233.1551
1177.1827 | 1104.1827 | 306.344 | 232.1728 | 233.1293 | 233.1137 | 229.7232 | 201.9673 | 197.9777 | 233.1811
1178.1841 | 1105.1841 | 306.175 | 232.2375 | 233.167 | 233.1128 | 229.7726 | 202.0114 | 198.0115 | 233.2028
1179.1856 | 1106.1856 | 306.0442 | 232.3034 | 233.1966 | 233.1985 | 229.8168 | 202.0581 | 198.048 | 233.2149
1180.177 | 1107.177 | 306.0301 | 232.3669 | 233.222 | 233.2343 | 229.8595 | 202.1076 | 198.0877 | 233.2303
1181.1785 | 1108.1785 | 306.1477 | 232.4253 | 233.2497 | 233.3181 | 229.8908 | 202.1515 | 198.1167 | 233.2302
1182.1799 | 1109.1799 | 306.2434 | 232.4862 | 233.2808 | 233.3647 | 229.9399 | 202.1953 | 198.1554 | 233.2485
1183.1813 | 1110.1813 | 306.3155 | 232.5346 | 233.3212 | 233.4212 | 229.9792 | 202.2349 | 198.1934 | 233.2643
1184.1828 | 1111.1828 | 306.2636 | 232.5843 | 233.348 | 233.5271 | 230.0242 | 202.2793 | 198.2278 | 233.2652
1185.1842 | 1112.1842 | 306.1516 | 232.6352 | 233.3781 | 233.5225 | 230.0662 | 202.3206 | 198.2632 | 233.2768
1186.1857 | 1113.1857 | 306.0712 | 232.6774 | 233.4137 | 233.4478 | 230.1016 | 202.3649 | 198.3001 | 233.2869
1187.1771 | 1114.1771 | 306.1218 | 232.7232 | 233.4579 | 233.3942 | 230.1545 | 202.4123 | 198.3423 | 233.3108
1188.1785 | 1115.1785 | 306.1335 | 232.76 | 233.4982 | 233.468 | 230.1977 | 202.4602 | 198.3761 | 233.3154
1189.18 | 1116.18 | 305.9908 | 232.8132 | 233.5455 | 233.4837 | 230.2342 | 202.5036 | 198.4241 | 233.3358
1190.1814 | 1117.1814 | 305.906 | 232.8466 | 233.5803 | 233.4445 | 230.2763 | 202.5489 | 198.4528 | 233.3665
1191.1828 | 1118.1828 | 305.8108 | 232.9047 | 233.6262 | 233.4292 | 230.3194 | 202.6005 | 198.4922 | 233.3715
1192.1843 | 1119.1843 | 305.6944 | 232.9367 | 233.6539 | 233.5446 | 230.3573 | 202.6504 | 198.5188 | 233.3955
1193.1857 | 1120.1857 | 305.5932 | 232.9872 | 233.6779 | 233.625 | 230.406 | 202.6908 | 198.5604 | 233.381
1194.1771 | 1121.1771 | 305.6051 | 233.0301 | 233.704 | 233.688 | 230.4456 | 202.7351 | 198.5916 | 233.4177
1195.1786 | 1122.1786 | 305.6133 | 233.0831 | 233.7422 | 233.6973 | 230.4736 | 202.7859 | 198.6344 | 233.4327
1196.18 | 1123.18 | 305.6187 | 233.1182 | 233.7832 | 233.77 | 230.5184 | 202.823 | 198.6708 | 233.4506
1197.1815 | 1124.1815 | 305.6802 | 233.1614 | 233.8226 | 233.8241 | 230.562 | 202.8741 | 198.7054 | 233.4756
1198.1829 | 1125.1829 | 305.6045 | 233.1977 | 233.8593 | 233.8351 | 230.5935 | 202.9013 | 198.7424 | 233.4854
1199.1843 | 1126.1843 | 305.4637 | 233.2471 | 233.893 | 233.9171 | 230.6367 | 202.9501 | 198.7805 | 233.494
1200.1858 | 1127.1858 | 305.4734 | 233.2908 | 233.9312 | 233.9707 | 230.6687 | 202.9724 | 198.8157 | 233.5164
1201.1772 | 1128.1772 | 305.3774 | 233.3292 | 233.9693 | 233.9902 | 230.7109 | 203.0183 | 198.8552 | 233.5344
1202.1786 | 1129.1786 | 305.4153 | 233.3656 | 233.9963 | 234.1242 | 230.7552 | 203.061 | 198.903 | 233.5494
1203.1801 | 1130.1801 | 305.415 | 233.3906 | 234.0367 | 234.063 | 230.7954 | 203.096 | 198.9525 | 233.5704
1204.1815 | 1131.1815 | 305.4109 | 233.4305 | 234.0561 | 233.9279 | 230.8294 | 203.1416 | 198.9941 | 233.5687
1205.183 | 1132.183 | 305.5487 | 233.4649 | 234.1002 | 234.0395 | 230.8625 | 203.1803 | 199.0274 | 233.5939
1206.1844 | 1133.1844 | 305.6471 | 233.5005 | 234.1353 | 234.0839 | 230.9184 | 203.2256 | 199.0509 | 233.6031
1207.1858 | 1134.1858 | 305.6962 | 233.5408 | 234.1746 | 234.1756 | 230.9592 | 203.2676 | 199.084 | 233.6238
1208.1873 | 1135.1873 | 305.7551 | 233.5647 | 234.2023 | 234.2862 | 230.9933 | 203.3213 | 199.1251 | 233.638
1209.1787 | 1136.1787 | 305.7073 | 233.5913 | 234.2391 | 234.3768 | 231.0407 | 203.3617 | 199.1626 | 233.6468
1210.1802 | 1137.1802 | 305.6473 | 233.6151 | 234.2666 | 234.3635 | 231.0733 | 203.406 | 199.2009 | 233.6444
1211.1816 | 1138.1816 | 305.5066 | 233.6438 | 234.2734 | 234.4956 | 231.1098 | 203.4395 | 199.2526 | 233.6622
1212.183 | 1139.183 | 305.4722 | 233.6725 | 234.3033 | 234.459 | 231.1561 | 203.4723 | 199.3059 | 233.683
1213.1845 | 1140.1845 | 305.5118 | 233.7074 | 234.3328 | 234.4325 | 231.2002 | 203.5094 | 199.3505 | 233.6768
1214.1859 | 1141.1859 | 305.5907 | 233.7446 | 234.3525 | 234.5114 | 231.2327 | 203.541 | 199.3945 | 233.6882
1215.1773 | 1142.1773 | 305.7297 | 233.7754 | 234.3773 | 234.5736 | 231.2737 | 203.5856 | 199.4415 | 233.7029
1216.1788 | 1143.1788 | 305.8183 | 233.8045 | 234.3947 | 234.6268 | 231.3232 | 203.625 | 199.4855 | 233.7158
1217.1802 | 1144.1802 | 305.9284 | 233.8353 | 234.4129 | 234.592 | 231.3582 | 203.673 | 199.5254 | 233.71
1218.1817 | 1145.1817 | 306.0059 | 233.8637 | 234.4132 | 234.6933 | 231.4034 | 203.7057 | 199.5598 | 233.7211
1219.1831 | 1146.1831 | 306.0963 | 233.8922 | 234.4413 | 234.7575 | 231.4376 | 203.7473 | 199.6036 | 233.7465
1220.1845 | 1147.1845 | 306.1467 | 233.9359 | 234.472 | 234.7616 | 231.481 | 203.786 | 199.6323 | 233.7624
1221.176 | 1148.176 | 306.1523 | 233.968 | 234.5019 | 234.8578 | 231.5232 | 203.8336 | 199.6709 | 233.7749
1222.1774 | 1149.1774 | 306.1503 | 234.0095 | 234.5225 | 234.9225 | 231.5667 | 203.8879 | 199.705 | 233.769
1223.1788 | 1150.1788 | 306.1532 | 234.0583 | 234.5564 | 234.9731 | 231.6006 | 203.9338 | 199.737 | 233.7781
1224.1803 | 1151.1803 | 306.1297 | 234.1008 | 234.5948 | 234.9471 | 231.6469 | 203.9805 | 199.7632 | 233.7891
1225.1817 | 1152.1817 | 306.1408 | 234.1431 | 234.632 | 235.016 | 231.6784 | 204.0371 | 199.7813 | 233.8218
1226.1832 | 1153.1832 | 306.1349 | 234.1801 | 234.6683 | 235.0216 | 231.7249 | 204.0904 | 199.7945 | 233.8293
1227.1846 | 1154.1846 | 306.1801 | 234.2248 | 234.7078 | 235.0625 | 231.768 | 204.1336 | 199.8304 | 233.8466
1228.176 | 1155.176 | 306.1207 | 234.266 | 234.7596 | 235.153 | 231.7988 | 204.1742 | 199.8577 | 233.8599
1229.1775 | 1156.1775 | 306.0929 | 234.3062 | 234.8029 | 235.1877 | 231.8388 | 204.2286 | 199.8959 | 233.8711
1230.1789 | 1157.1789 | 306.107 | 234.3501 | 234.8513 | 235.2878 | 231.8809 | 204.2693 | 199.9409 | 233.8952
1231.1804 | 1158.1804 | 306.1156 | 234.3824 | 234.8853 | 235.2121 | 231.9116 | 204.3194 | 199.9841 | 233.9261
1232.1818 | 1159.1818 | 306.1151 | 234.4122 | 234.9211 | 235.2635 | 231.9626 | 204.3587 | 200.0225 | 233.9424
1233.1832 | 1160.1832 | 306.0609 | 234.4492 | 234.9525 | 235.3215 | 231.9987 | 204.4032 | 200.0687 | 233.9633
1234.1847 | 1161.1847 | 305.8886 | 234.4813 | 234.9952 | 235.3411 | 232.0398 | 204.441 | 200.1156 | 233.9654
1235.1861 | 1162.1861 | 305.8622 | 234.5189 | 235.0376 | 235.3806 | 232.0803 | 204.4714 | 200.1636 | 233.9681
1236.1775 | 1163.1775 | 305.9472 | 234.5561 | 235.0654 | 235.4913 | 232.1138 | 204.5092 | 200.222 | 233.9834
1237.179 | 1164.179 | 305.9636 | 234.5864 | 235.0749 | 235.4121 | 232.1465 | 204.552 | 200.2717 | 233.996
1238.1804 | 1165.1804 | 305.8498 | 234.6166 | 235.1015 | 235.4884 | 232.1826 | 204.5781 | 200.3114 | 234.0115
1239.1819 | 1166.1819 | 305.7609 | 234.6435 | 235.124 | 235.5961 | 232.228 | 204.6117 | 200.3597 | 234.0104
1240.1833 | 1167.1833 | 305.8448 | 234.6718 | 235.1494 | 235.6303 | 232.2565 | 204.6455 | 200.3994 | 234.0176
1241.1847 | 1168.1847 | 305.877 | 234.6936 | 235.1698 | 235.6261 | 232.2947 | 204.6801 | 200.4427 | 234.025
1242.1862 | 1169.1862 | 305.7546 | 234.7234 | 235.1998 | 235.6785 | 232.3353 | 204.7166 | 200.4904 | 234.044
1243.1876 | 1170.1876 | 305.6862 | 234.7437 | 235.2315 | 235.6427 | 232.3772 | 204.7467 | 200.5393 | 234.0565
1244.179 | 1171.179 | 305.6079 | 234.7639 | 235.2509 | 235.6841 | 232.4203 | 204.7777 | 200.5842 | 234.0703
1245.1805 | 1172.1805 | 305.5635 | 234.7967 | 235.2783 | 235.7115 | 232.455 | 204.8092 | 200.625 | 234.0868
1246.1819 | 1173.1819 | 305.5822 | 234.8076 | 235.2985 | 235.7291 | 232.4906 | 204.851 | 200.6609 | 234.0961
1247.1834 | 1174.1834 | 305.7066 | 234.8271 | 235.3255 | 235.6801 | 232.5374 | 204.8918 | 200.7039 | 234.1255
1248.1848 | 1175.1848 | 305.6487 | 234.8466 | 235.3277 | 235.7578 | 232.5701 | 204.9329 | 200.7395 | 234.1235
1249.1862 | 1176.1862 | 305.6184 | 234.8578 | 235.338 | 235.8826 | 232.5958 | 204.974 | 200.7699 | 234.147
1250.1877 | 1177.1877 | 305.6627 | 234.8713 | 235.3418 | 235.9338 | 232.6301 | 205.0155 | 200.7988 | 234.1537
1251.1791 | 1178.1791 | 305.788 | 234.8868 | 235.3564 | 235.913 | 232.6617 | 205.0521 | 200.8388 | 234.1602
1252.1805 | 1179.1805 | 305.7785 | 234.8949 | 235.3524 | 235.9527 | 232.7085 | 205.0972 | 200.8734 | 234.1841
1253.182 | 1180.182 | 305.7217 | 234.9119 | 235.3754 | 235.9929 | 232.7322 | 205.1447 | 200.9193 | 234.195
1254.1834 | 1181.1834 | 305.6103 | 234.9139 | 235.387 | 235.967 | 232.7726 | 205.1903 | 200.9563 | 234.2085
1255.1849 | 1182.1849 | 305.6755 | 234.9144 | 235.4079 | 235.9772 | 232.7975 | 205.2272 | 200.999 | 234.2312
1256.1863 | 1183.1863 | 305.7694 | 234.9185 | 235.436 | 236.0577 | 232.842 | 205.2699 | 201.0332 | 234.2681
1257.1777 | 1184.1777 | 305.8266 | 234.9217 | 235.4553 | 236.0746 | 232.8586 | 205.3118 | 201.0581 | 234.2775
1258.1792 | 1185.1792 | 305.8446 | 234.9288 | 235.4735 | 236.1334 | 232.8996 | 205.3502 | 201.1063 | 234.2884
1259.1806 | 1186.1806 | 305.9288 | 234.9367 | 235.4903 | 236.1488 | 232.9313 | 205.3943 | 201.1371 | 234.322
1260.1821 | 1187.1821 | 305.9403 | 234.9398 | 235.5109 | 236.0941 | 232.9561 | 205.4318 | 201.183 | 234.327
1261.1835 | 1188.1835 | 305.9876 | 234.9512 | 235.5299 | 236.174 | 232.9846 | 205.4781 | 201.2138 | 234.3552
1262.1849 | 1189.1849 | 306.1457 | 234.9606 | 235.5452 | 236.1442 | 233.0117 | 205.5074 | 201.2589 | 234.3658
1263.1864 | 1190.1864 | 306.2526 | 234.979 | 235.5634 | 236.1588 | 233.0483 | 205.5497 | 201.2824 | 234.387
1264.1778 | 1191.1778 | 306.3338 | 234.9814 | 235.5704 | 236.1688 | 233.0745 | 205.589 | 201.3099 | 234.3993
1265.1792 | 1192.1792 | 306.3387 | 234.9956 | 235.5849 | 236.1665 | 233.1008 | 205.6308 | 201.3378 | 234.414
1266.1807 | 1193.1807 | 306.3737 | 235 | 235.5988 | 236.2367 | 233.138 | 205.6669 | 201.3697 | 234.445
1267.1821 | 1194.1821 | 306.3976 | 234.9913 | 235.6077 | 236.2976 | 233.1555 | 205.6953 | 201.3978 | 234.4523
1268.1836 | 1195.1836 | 306.408 | 234.9932 | 235.6165 | 236.3625 | 233.1924 | 205.7463 | 201.4322 | 234.455
1269.185 | 1196.185 | 306.4963 | 234.9902 | 235.6362 | 236.3496 | 233.2241 | 205.7866 | 201.4783 | 234.4579
1270.1764 | 1197.1764 | 306.4654 | 235 | 235.6417 | 236.3669 | 233.2351 | 205.8291 | 201.5184 | 234.4573
1271.1779 | 1198.1779 | 306.4271 | 235 | 235.6585 | 236.4023 | 233.2788 | 205.8649 | 201.5642 | 234.4644
1272.1793 | 1199.1793 | 306.4651 | 235.0063 | 235.6683 | 236.4585 | 233.3021 | 205.9082 | 201.603 | 234.4728
1273.1807 | 1200.1807 | 306.593 | 235.0219 | 235.6898 | 236.4863 | 233.3399 | 205.9458 | 201.6455 | 234.4733
1274.1822 | 1201.1822 | 306.567 | 235.0199 | 235.7062 | 236.527 | 233.3512 | 205.9814 | 201.6885 | 234.4921
1275.1836 | 1202.1836 | 306.5204 | 235.0247 | 235.7032 | 236.4997 | 233.3767 | 206.0158 | 201.7239 | 234.5108
1276.1851 | 1203.1851 | 306.5719 | 235.0286 | 235.704 | 236.5281 | 233.4116 | 206.0523 | 201.7752 | 234.51
1277.1865 | 1204.1865 | 306.6079 | 235.046 | 235.6688 | 236.5609 | 233.4311 | 206.0942 | 201.8195 | 234.5267
1278.1779 | 1205.1779 | 306.4587 | 235.0527 | 235.6724 | 236.5529 | 233.456 | 206.1345 | 201.8537 | 234.5326
1279.1794 | 1206.1794 | 306.2797 | 235.0636 | 235.6751 | 236.5999 | 233.4912 | 206.1779 | 201.8959 | 234.557
1280.1808 | 1207.1808 | 306.1862 | 235.083 | 235.7048 | 236.6391 | 233.5056 | 206.213 | 201.9434 | 234.5643
1281.1823 | 1208.1823 | 306.1476 | 235.099 | 235.7117 | 236.7075 | 233.5436 | 206.2356 | 201.9884 | 234.5761
1282.1837 | 1209.1837 | 306.1141 | 235.1163 | 235.7386 | 236.7026 | 233.5555 | 206.2787 | 202.0342 | 234.5783
1283.1851 | 1210.1851 | 306.1349 | 235.1413 | 235.7667 | 236.7981 | 233.5765 | 206.3066 | 202.0793 | 234.5799
1284.1866 | 1211.1866 | 306.1722 | 235.159 | 235.7846 | 236.8151 | 233.6037 | 206.3416 | 202.1131 | 234.5896
1285.178 | 1212.178 | 306.0337 | 235.1747 | 235.8136 | 236.8936 | 233.6284 | 206.3763 | 202.1576 | 234.5841
1286.1794 | 1213.1794 | 305.8502 | 235.1912 | 235.8433 | 236.9179 | 233.663 | 206.4063 | 202.204 | 234.6119
1287.1809 | 1214.1809 | 305.6912 | 235.2045 | 235.8653 | 236.9052 | 233.6816 | 206.4354 | 202.2495 | 234.6245
1288.1823 | 1215.1823 | 305.5471 | 235.2165 | 235.8886 | 236.9434 | 233.7065 | 206.4501 | 202.2878 | 234.6226
1289.1838 | 1216.1838 | 305.4564 | 235.2368 | 235.9005 | 236.896 | 233.7349 | 206.4961 | 202.3307 | 234.6195
1290.1852 | 1217.1852 | 305.3594 | 235.2436 | 235.9118 | 236.9622 | 233.7575 | 206.5185 | 202.3674 | 234.6207
1291.1866 | 1218.1866 | 305.276 | 235.2489 | 235.9305 | 236.9126 | 233.7817 | 206.5539 | 202.4082 | 234.6182
1292.1881 | 1219.1881 | 305.3046 | 235.2325 | 235.9481 | 236.9027 | 233.7993 | 206.5865 | 202.4484 | 234.6367
1293.1795 | 1220.1795 | 305.3188 | 235.2117 | 235.9757 | 236.8862 | 233.8278 | 206.6218 | 202.4798 | 234.6428
1294.1809 | 1221.1809 | 305.3314 | 235.2011 | 235.9939 | 236.9049 | 233.8555 | 206.6544 | 202.5084 | 234.6315
1295.1824 | 1222.1824 | 305.3877 | 235.1896 | 236.0203 | 236.9571 | 233.8874 | 206.6869 | 202.5383 | 234.654
1296.1838 | 1223.1838 | 305.4212 | 235.1787 | 236.0441 | 236.954 | 233.9075 | 206.7168 | 202.5804 | 234.6615
1297.1853 | 1224.1853 | 305.3894 | 235.177 | 236.0613 | 237.0162 | 233.9225 | 206.7558 | 202.6123 | 234.6569
1298.1867 | 1225.1867 | 305.3978 | 235.1779 | 236.0843 | 237.0123 | 233.9444 | 206.7917 | 202.6496 | 234.675
1299.1781 | 1226.1781 | 305.4255 | 235.1842 | 236.0996 | 237.0592 | 233.9661 | 206.8245 | 202.682 | 234.6637
1300.1796 | 1227.1796 | 305.4155 | 235.1918 | 236.1179 | 237.0586 | 233.9876 | 206.8548 | 202.7219 | 234.6849
1301.181 | 1228.181 | 305.3217 | 235.2008 | 236.1332 | 237.1308 | 234.0096 | 206.8937 | 202.7541 | 234.6852
1302.1824 | 1229.1824 | 305.306 | 235.2063 | 236.1616 | 237.1549 | 234.0372 | 206.9216 | 202.7839 | 234.6824
1303.1839 | 1230.1839 | 305.1953 | 235.2223 | 236.1824 | 237.136 | 234.0503 | 206.9576 | 202.804 | 234.6971
1304.1853 | 1231.1853 | 305.0838 | 235.2335 | 236.1999 | 237.1389 | 234.0732 | 206.9805 | 202.8393 | 234.6839
1305.1768 | 1232.1768 | 304.9206 | 235.2427 | 236.2176 | 237.1477 | 234.0881 | 207.0074 | 202.8712 | 234.6882
1306.1782 | 1233.1782 | 304.8613 | 235.2518 | 236.2477 | 237.219 | 234.1017 | 207.0358 | 202.9045 | 234.7062
1307.1796 | 1234.1796 | 304.8359 | 235.2615 | 236.2652 | 237.2483 | 234.123 | 207.0757 | 202.9425 | 234.7106
1308.1811 | 1235.1811 | 304.8722 | 235.2806 | 236.2801 | 237.2568 | 234.1391 | 207.1083 | 202.9803 | 234.7207
1309.1825 | 1236.1825 | 304.933 | 235.2928 | 236.2991 | 237.3011 | 234.159 | 207.1423 | 203.0108 | 234.7331
1310.184 | 1237.184 | 304.9773 | 235.318 | 236.3188 | 237.3198 | 234.1771 | 207.1727 | 203.0521 | 234.7455
1311.1854 | 1238.1854 | 304.9583 | 235.3399 | 236.3409 | 237.3495 | 234.2002 | 207.2 | 203.0795 | 234.7507
1312.1768 | 1239.1768 | 305.0515 | 235.3622 | 236.3552 | 237.3404 | 234.2117 | 207.2209 | 203.1089 | 234.7418
1313.1783 | 1240.1783 | 305.1809 | 235.3874 | 236.3776 | 237.3883 | 234.2334 | 207.2563 | 203.154 | 234.7446
1314.1797 | 1241.1797 | 305.1823 | 235.4089 | 236.3998 | 237.4387 | 234.2447 | 207.2837 | 203.1904 | 234.7845
1315.1811 | 1242.1811 | 305.131 | 235.4337 | 236.423 | 237.4949 | 234.2676 | 207.2985 | 203.2302 | 234.7841
1316.1826 | 1243.1826 | 305.1905 | 235.4608 | 236.4361 | 237.518 | 234.2862 | 207.328 | 203.2574 | 234.8067
1317.184 | 1244.184 | 305.1865 | 235.4733 | 236.438 | 237.5152 | 234.3056 | 207.3604 | 203.2984 | 234.8008
1318.1855 | 1245.1855 | 305.212 | 235.4842 | 236.4517 | 237.5373 | 234.3231 | 207.3939 | 203.3334 | 234.8192
1319.1869 | 1246.1869 | 305.2318 | 235.4773 | 236.4661 | 237.4949 | 234.3443 | 207.4278 | 203.374 | 234.8249
1320.1783 | 1247.1783 | 305.1679 | 235.476 | 236.4726 | 237.5405 | 234.3614 | 207.4584 | 203.4177 | 234.8373
1321.1798 | 1248.1798 | 305.0923 | 235.4725 | 236.5024 | 237.5217 | 234.3799 | 207.497 | 203.4585 | 234.868
1322.1812 | 1249.1812 | 305.1276 | 235.4687 | 236.5169 | 237.5476 | 234.3985 | 207.526 | 203.4865 | 234.8649
1323.1826 | 1250.1826 | 305.1944 | 235.4738 | 236.5235 | 237.5871 | 234.4041 | 207.5521 | 203.5205 | 234.8889
1324.1841 | 1251.1841 | 305.2357 | 235.4697 | 236.5378 | 237.5594 | 234.4262 | 207.5777 | 203.5552 | 234.8942
1325.1755 | 1252.1755 | 305.231 | 235.482 | 236.5393 | 237.5506 | 234.4444 | 207.6028 | 203.5894 | 234.8813
1326.187 | 1253.187 | 305.1917 | 235.4866 | 236.549 | 237.6162 | 234.4703 | 207.6272 | 203.6278 | 234.9163
1327.1784 | 1254.1784 | 305.2222 | 235.5042 | 236.5593 | 237.5423 | 234.4812 | 207.6468 | 203.6492 | 234.9124
1328.1798 | 1255.1798 | 305.2511 | 235.516 | 236.572 | 237.5923 | 234.5124 | 207.6723 | 203.6823 | 234.9285
1329.1813 | 1256.1813 | 305.2735 | 235.5353 | 236.5798 | 237.5876 | 234.5228 | 207.692 | 203.7025 | 234.9117
1330.1827 | 1257.1827 | 305.2923 | 235.5535 | 236.5982 | 237.6411 | 234.5391 | 207.7223 | 203.7352 | 234.9251
1331.1841 | 1258.1841 | 305.3358 | 235.554 | 236.6122 | 237.7265 | 234.5575 | 207.76 | 203.7686 | 234.9174
1332.1856 | 1259.1856 | 305.454 | 235.5594 | 236.627 | 237.7064 | 234.586 | 207.7932 | 203.7998 | 234.8999
1333.187 | 1260.187 | 305.5049 | 235.5548 | 236.6516 | 237.5351 | 234.593 | 207.8228 | 203.8284 | 234.904
1334.1785 | 1261.1785 | 305.5526 | 235.5492 | 236.651 | 237.5363 | 234.6084 | 207.8679 | 203.8483 | 234.9041
1335.1799 | 1262.1799 | 305.5509 | 235.5637 | 236.6683 | 237.6003 | 234.6266 | 207.9047 | 203.8732 | 234.9169
1336.1813 | 1263.1813 | 305.5633 | 235.5717 | 236.6943 | 237.6737 | 234.6486 | 207.9418 | 203.8973 | 234.9113
1337.1828 | 1264.1828 | 305.6349 | 235.5767 | 236.7182 | 237.7039 | 234.6638 | 207.9719 | 203.9154 | 234.921
1338.1842 | 1265.1842 | 305.6993 | 235.5935 | 236.7269 | 237.6737 | 234.6739 | 208.0155 | 203.9383 | 234.9278
1339.1857 | 1266.1857 | 305.713 | 235.6147 | 236.7453 | 237.7315 | 234.6907 | 208.039 | 203.9626 | 234.9259
1340.1871 | 1267.1871 | 305.6116 | 235.6279 | 236.7715 | 237.769 | 234.71 | 208.0673 | 203.9914 | 234.9389
1341.1785 | 1268.1785 | 305.6692 | 235.6493 | 236.7995 | 237.7946 | 234.7393 | 208.0997 | 204.0123 | 234.9429
1342.18 | 1269.18 | 305.7809 | 235.6685 | 236.8229 | 237.8282 | 234.7528 | 208.1235 | 204.0384 | 234.9569
1343.1814 | 1270.1814 | 305.9054 | 235.6864 | 236.8458 | 237.8878 | 234.77 | 208.1521 | 204.0689 | 234.9852
1344.1828 | 1271.1828 | 306.0481 | 235.7142 | 236.8891 | 237.8899 | 234.7787 | 208.1887 | 204.0931 | 234.9861
1345.1843 | 1272.1843 | 306.1341 | 235.7356 | 236.9108 | 237.9861 | 234.7994 | 208.2255 | 204.1183 | 234.995
1346.1857 | 1273.1857 | 306.1809 | 235.7606 | 236.9473 | 237.9556 | 234.8232 | 208.2686 | 204.1387 | 235.014
1347.1872 | 1274.1872 | 306.3979 | 235.7807 | 236.9636 | 238.0658 | 234.8445 | 208.306 | 204.1641 | 235.0106
1348.1786 | 1275.1786 | 306.5196 | 235.802 | 236.9899 | 238.1173 | 234.8526 | 208.3407 | 204.1887 | 235.0298
1349.18 | 1276.18 | 306.5336 | 235.8168 | 236.9978 | 238.1745 | 234.8721 | 208.3772 | 204.2129 | 235.0261
1350.1815 | 1277.1815 | 306.6472 | 235.8457 | 237.0251 | 238.167 | 234.892 | 208.4097 | 204.2407 | 235.0446
1351.1829 | 1278.1829 | 306.7992 | 235.8592 | 237.0466 | 238.1992 | 234.9157 | 208.4414 | 204.2641 | 235.0537
1352.1843 | 1279.1843 | 306.9916 | 235.8791 | 237.0615 | 238.2499 | 234.925 | 208.4827 | 204.2844 | 235.0816
1353.1858 | 1280.1858 | 307.0631 | 235.8931 | 237.0776 | 238.2394 | 234.9439 | 208.5113 | 204.3157 | 235.0925
1354.1772 | 1281.1772 | 306.9581 | 235.9133 | 237.088 | 238.3193 | 234.9542 | 208.547 | 204.3514 | 235.1109
1355.1787 | 1282.1787 | 306.9125 | 235.9235 | 237.0968 | 238.3736 | 234.9701 | 208.5761 | 204.3834 | 235.1253
1356.1801 | 1283.1801 | 307.0037 | 235.9346 | 237.1128 | 238.4195 | 234.9904 | 208.6237 | 204.4282 | 235.1406
1357.1815 | 1284.1815 | 307.0258 | 235.9331 | 237.1229 | 238.3992 | 235.0099 | 208.6619 | 204.4703 | 235.1304
1358.183 | 1285.183 | 306.9893 | 235.938 | 237.14 | 238.4297 | 235.0191 | 208.6966 | 204.5052 | 235.1596
1359.1844 | 1286.1844 | 306.92 | 235.9404 | 237.1615 | 238.4743 | 235.0335 | 208.7352 | 204.5388 | 235.1726
1360.1859 | 1287.1859 | 306.8918 | 235.944 | 237.1701 | 238.4667 | 235.0617 | 208.7894 | 204.5714 | 235.1999
1361.1773 | 1288.1773 | 306.9673 | 235.9467 | 237.2003 | 238.4634 | 235.0648 | 208.8241 | 204.6033 | 235.2131
1362.1787 | 1289.1787 | 306.9484 | 235.9439 | 237.2206 | 238.504 | 235.0853 | 208.8656 | 204.6348 | 235.2235
1363.1802 | 1290.1802 | 306.9021 | 235.9466 | 237.2434 | 238.5206 | 235.0938 | 208.9088 | 204.6604 | 235.2501
1364.1816 | 1291.1816 | 306.8346 | 235.9415 | 237.2623 | 238.5315 | 235.1169 | 208.9448 | 204.6922 | 235.2379
1365.183 | 1292.183 | 306.8325 | 235.9386 | 237.2911 | 238.5397 | 235.1174 | 208.9836 | 204.7296 | 235.2685
1366.1845 | 1293.1845 | 306.8203 | 235.9379 | 237.3147 | 238.5619 | 235.1452 | 209.0105 | 204.767 | 235.2822
1367.1859 | 1294.1859 | 306.7893 | 235.9532 | 237.3346 | 238.5191 | 235.1602 | 209.0535 | 204.7905 | 235.288
1368.1874 | 1295.1874 | 306.664 | 235.9663 | 237.3593 | 238.5839 | 235.172 | 209.0803 | 204.8223 | 235.287
1369.1788 | 1296.1788 | 306.5894 | 235.985 | 237.3733 | 238.5243 | 235.1878 | 209.1223 | 204.8419 | 235.2745
1370.1802 | 1297.1802 | 306.5973 | 235.9987 | 237.3931 | 238.4757 | 235.2013 | 209.1553 | 204.8641 | 235.3012
1371.1817 | 1298.1817 | 306.6095 | 236.0137 | 237.4147 | 238.5424 | 235.2279 | 209.1871 | 204.8959 | 235.2959
1372.1831 | 1299.1831 | 306.6073 | 236.0281 | 237.4344 | 238.4467 | 235.2338 | 209.2282 | 204.925 | 235.3146
1373.1845 | 1300.1845 | 306.5052 | 236.0363 | 237.4631 | 238.5122 | 235.2578 | 209.2614 | 204.9435 | 235.3127
1374.186 | 1301.186 | 306.4509 | 236.043 | 237.4806 | 238.5234 | 235.2702 | 209.2939 | 204.9708 | 235.3102
1375.1874 | 1302.1874 | 306.4472 | 236.0478 | 237.5057 | 238.5196 | 235.2811 | 209.3284 | 204.9982 | 235.3201
1376.1788 | 1303.1788 | 306.3892 | 236.0542 | 237.526 | 238.5058 | 235.2894 | 209.3756 | 205.0254 | 235.3341
1377.1803 | 1304.1803 | 306.2304 | 236.0592 | 237.5498 | 238.5183 | 235.3071 | 209.4153 | 205.0457 | 235.3284
1378.1817 | 1305.1817 | 306.015 | 236.0589 | 237.5597 | 238.4836 | 235.3442 | 209.4458 | 205.0729 | 235.349
1379.1832 | 1306.1832 | 305.8162 | 236.0673 | 237.5752 | 238.5302 | 235.3391 | 209.494 | 205.0995 | 235.3661
1380.1946 | 1307.1946 | 305.5816 | 236.0781 | 237.5878 | 238.5195 | 235.3671 | 209.5606 | 205.1265 | 235.3549
1381.176 | 1308.176 | 305.4367 | 236.0839 | 237.5995 | 238.5691 | 235.3783 | 209.6092 | 205.1645 | 235.3715
1382.1775 | 1309.1775 | 305.4159 | 236.089 | 237.607 | 238.6018 | 235.3896 | 209.6608 | 205.1925 | 235.384
1383.1789 | 1310.1789 | 305.3472 | 236.0837 | 237.6158 | 238.593 | 235.4027 | 209.7083 | 205.2275 | 235.3843
1384.1804 | 1311.1804 | 305.2976 | 236.0738 | 237.6329 | 238.6239 | 235.4245 | 209.7469 | 205.2499 | 235.3851
1385.1818 | 1312.1818 | 305.2389 | 236.0727 | 237.6322 | 238.6596 | 235.4363 | 209.7957 | 205.285 | 235.383
1386.1832 | 1313.1832 | 305.1154 | 236.0665 | 237.6378 | 238.6454 | 235.4527 | 209.8235 | 205.3118 | 235.3941
1387.1847 | 1314.1847 | 305.098 | 236.0573 | 237.6298 | 238.6779 | 235.4803 | 209.8618 | 205.3306 | 235.4278
1388.1861 | 1315.1861 | 304.9646 | 236.0574 | 237.6339 | 238.7273 | 235.4854 | 209.9107 | 205.3565 | 235.4352
1389.1775 | 1316.1775 | 304.7479 | 236.0569 | 237.6407 | 238.7121 | 235.5054 | 209.9505 | 205.3753 | 235.4324
1390.179 | 1317.179 | 304.6385 | 236.0632 | 237.6385 | 238.6923 | 235.5273 | 209.9892 | 205.3874 | 235.4443
1391.1804 | 1318.1804 | 304.7271 | 236.0637 | 237.6336 | 238.7357 | 235.5439 | 210.0325 | 205.4017 | 235.4439
1392.1819 | 1319.1819 | 304.6978 | 236.0692 | 237.6231 | 238.7403 | 235.5525 | 210.0617 | 205.4154 | 235.4558
1393.1833 | 1320.1833 | 304.6195 | 236.0787 | 237.6559 | 238.7586 | 235.556 | 210.1011 | 205.4375 | 235.4508
1394.1847 | 1321.1847 | 304.4989 | 236.0808 | 237.6596 | 238.7683 | 235.5704 | 210.1283 | 205.462 | 235.4723
1395.1762 | 1322.1762 | 304.4657 | 236.0963 | 237.6732 | 238.7699 | 235.5842 | 210.158 | 205.4899 | 235.4616
1396.1776 | 1323.1776 | 304.4236 | 236.1104 | 237.6784 | 238.7677 | 235.6026 | 210.1943 | 205.5103 | 235.4783
1397.179 | 1324.179 | 304.4743 | 236.1132 | 237.6986 | 238.7184 | 235.6252 | 210.234 | 205.5339 | 235.4684
1398.1805 | 1325.1805 | 304.5101 | 236.127 | 237.7052 | 238.7582 | 235.6282 | 210.2765 | 205.56 | 235.4789
1399.1819 | 1326.1819 | 304.5761 | 236.1375 | 237.7083 | 238.7639 | 235.6415 | 210.3145 | 205.5825 | 235.4842
1400.1834 | 1327.1834 | 304.6311 | 236.1483 | 237.7083 | 238.775 | 235.6405 | 210.3653 | 205.6015 | 235.499
1401.1848 | 1328.1848 | 304.6739 | 236.151 | 237.7343 | 238.7739 | 235.6614 | 210.3947 | 205.6218 | 235.4989
1402.1762 | 1329.1762 | 304.7979 | 236.1522 | 237.7372 | 238.7534 | 235.6772 | 210.4342 | 205.6369 | 235.505
1403.1777 | 1330.1777 | 304.9832 | 236.1601 | 237.749 | 238.7353 | 235.6773 | 210.4612 | 205.6591 | 235.4952
1404.1791 | 1331.1791 | 305.1644 | 236.1552 | 237.759 | 238.7479 | 235.692 | 210.4987 | 205.6697 | 235.4903
1405.1806 | 1332.1806 | 305.2652 | 236.1523 | 237.7518 | 238.7791 | 235.7061 | 210.5247 | 205.6834 | 235.5086
1406.182 | 1333.182 | 305.3882 | 236.1623 | 237.7824 | 238.8523 | 235.7135 | 210.556 | 205.7025 | 235.5031
1407.1834 | 1334.1834 | 305.4921 | 236.1704 | 237.7948 | 238.8654 | 235.729 | 210.5816 | 205.7267 | 235.5155
1408.1849 | 1335.1849 | 305.5856 | 236.1771 | 237.8014 | 238.8641 | 235.7436 | 210.608 | 205.7384 | 235.5264
1409.1863 | 1336.1863 | 305.6497 | 236.1883 | 237.8193 | 238.9279 | 235.7459 | 210.6377 | 205.7677 | 235.519
1410.1777 | 1337.1777 | 305.6755 | 236.1927 | 237.8151 | 238.9042 | 235.7633 | 210.6652 | 205.7826 | 235.5552
1411.1792 | 1338.1792 | 305.7521 | 236.1971 | 237.8122 | 238.9552 | 235.7723 | 210.6938 | 205.7979 | 235.5581
1412.1806 | 1339.1806 | 305.9083 | 236.196 | 237.8062 | 238.9381 | 235.7885 | 210.7242 | 205.8149 | 235.5802
1413.1821 | 1340.1821 | 306.0533 | 236.1892 | 237.8074 | 238.9995 | 235.7959 | 210.7495 | 205.8353 | 235.5862
1414.1835 | 1341.1835 | 306.2398 | 236.1936 | 237.8085 | 238.9758 | 235.8092 | 210.7907 | 205.8582 | 235.5907
1415.1849 | 1342.1849 | 306.4044 | 236.1941 | 237.8054 | 238.9838 | 235.8255 | 210.8279 | 205.8764 | 235.6096
1416.1864 | 1343.1864 | 306.5221 | 236.2162 | 237.8164 | 238.9906 | 235.8349 | 210.8649 | 205.8992 | 235.5968
1417.1878 | 1344.1878 | 306.6337 | 236.2244 | 237.8282 | 238.9813 | 235.8409 | 210.8865 | 205.9224 | 235.6105
1418.1792 | 1345.1792 | 306.8296 | 236.2426 | 237.8438 | 239.0021 | 235.8644 | 210.9201 | 205.9418 | 235.628
1419.1807 | 1346.1807 | 306.8603 | 236.2581 | 237.8579 | 239.0575 | 235.8735 | 210.9577 | 205.9634 | 235.6343
1420.1821 | 1347.1821 | 306.7678 | 236.2739 | 237.8838 | 239.0633 | 235.8912 | 210.979 | 205.9803 | 235.6567
1421.1836 | 1348.1836 | 306.7916 | 236.3027 | 237.8886 | 239.1256 | 235.903 | 211.0029 | 206.0151 | 235.6624
1422.185 | 1349.185 | 306.9208 | 236.3162 | 237.8959 | 239.1136 | 235.9198 | 211.0415 | 206.0397 | 235.6742
1423.1864 | 1350.1864 | 306.8829 | 236.325 | 237.9243 | 239.1373 | 235.9235 | 211.0632 | 206.0665 | 235.6946
1424.1879 | 1351.1879 | 306.8755 | 236.3467 | 237.9543 | 239.1547 | 235.9395 | 211.0877 | 206.1017 | 235.7026
1425.1793 | 1352.1793 | 306.9938 | 236.3693 | 237.967 | 239.2087 | 235.9557 | 211.1186 | 206.1303 | 235.7203
1426.1807 | 1353.1807 | 307.1544 | 236.3931 | 238.0018 | 239.251 | 235.9757 | 211.154 | 206.1428 | 235.7398
1427.1822 | 1354.1822 | 307.2279 | 236.4128 | 238.0187 | 239.2575 | 235.9877 | 211.1877 | 206.1656 | 235.7525
1428.1836 | 1355.1836 | 307.1629 | 236.4351 | 238.0563 | 239.2831 | 236.0003 | 211.2057 | 206.1781 | 235.7724
1429.1851 | 1356.1851 | 307.2068 | 236.4601 | 238.0864 | 239.316 | 236.0146 | 211.2325 | 206.1978 | 235.7865
1430.1865 | 1357.1865 | 307.3089 | 236.4934 | 238.1315 | 239.2939 | 236.0378 | 211.2508 | 206.2041 | 235.8203
1431.1779 | 1358.1779 | 307.3304 | 236.5196 | 238.1768 | 239.4045 | 236.048 | 211.2613 | 206.2148 | 235.8358
1432.1794 | 1359.1794 | 307.2201 | 236.5549 | 238.2024 | 239.4862 | 236.0647 | 211.2798 | 206.2198 | 235.8651
1433.1808 | 1360.1808 | 307.2 | 236.5913 | 238.2367 | 239.4835 | 236.0796 | 211.3038 | 206.2194 | 235.8697
1434.1823 | 1361.1823 | 307.1326 | 236.6311 | 238.2718 | 239.5409 | 236.1055 | 211.3265 | 206.2308 | 235.8668
1435.1837 | 1362.1837 | 307.0072 | 236.6644 | 238.3305 | 239.5619 | 236.1263 | 211.3418 | 206.237 | 235.8913
1436.1851 | 1363.1851 | 306.8718 | 236.6989 | 238.361 | 239.573 | 236.135 | 211.3572 | 206.2477 | 235.8996
1437.1866 | 1364.1866 | 306.7661 | 236.7338 | 238.3945 | 239.6084 | 236.1507 | 211.3818 | 206.269 | 235.9253
1438.178 | 1365.178 | 306.6346 | 236.7781 | 238.4258 | 239.6188 | 236.1622 | 211.3934 | 206.2811 | 235.9216
1439.1794 | 1366.1794 | 306.4598 | 236.8002 | 238.4601 | 239.6622 | 236.1904 | 211.4216 | 206.295 | 235.9148
1440.1809 | 1367.1809 | 306.3092 | 236.8334 | 238.4688 | 239.7303 | 236.1977 | 211.4411 | 206.3238 | 235.9231
1441.1823 | 1368.1823 | 306.1165 | 236.8614 | 238.5017 | 239.7252 | 236.2127 | 211.4655 | 206.3518 | 235.9463
1442.1838 | 1369.1838 | 306.0013 | 236.8809 | 238.5177 | 239.7596 | 236.2258 | 211.4783 | 206.373 | 235.9366
1443.1852 | 1370.1852 | 305.9158 | 236.9037 | 238.5327 | 239.8448 | 236.246 | 211.517 | 206.4008 | 235.9558
1444.1766 | 1371.1766 | 305.7779 | 236.927 | 238.5504 | 239.8344 | 236.255 | 211.5279 | 206.4243 | 235.9632
1445.1781 | 1372.1781 | 305.6489 | 236.9443 | 238.5636 | 239.8517 | 236.2687 | 211.5415 | 206.4424 | 235.9672
1446.1795 | 1373.1795 | 305.6297 | 236.9588 | 238.5699 | 239.9039 | 236.2781 | 211.5645 | 206.4614 | 235.9765
1447.1809 | 1374.1809 | 305.5775 | 236.9686 | 238.5806 | 239.917 | 236.2997 | 211.5756 | 206.4697 | 235.9665
1448.1824 | 1375.1824 | 305.4583 | 236.9733 | 238.5915 | 239.9662 | 236.3195 | 211.5963 | 206.4854 | 235.9861
1449.1838 | 1376.1838 | 305.3513 | 236.9806 | 238.6021 | 240.0188 | 236.3157 | 211.6236 | 206.5032 | 235.9925
1450.1853 | 1377.1853 | 305.2704 | 236.984 | 238.5989 | 240.0662 | 236.3394 | 211.6604 | 206.5207 | 235.9921
1451.1867 | 1378.1867 | 305.2455 | 236.9917 | 238.5967 | 240.0412 | 236.3367 | 211.6872 | 206.5399 | 235.9894
1452.1781 | 1379.1781 | 305.2394 | 236.991 | 238.5728 | 240.0298 | 236.3529 | 211.7042 | 206.5587 | 235.9962
1453.1796 | 1380.1796 | 305.1747 | 236.9905 | 238.5754 | 240.0338 | 236.377 | 211.7239 | 206.5848 | 236.0023
1454.181 | 1381.181 | 305.1869 | 236.9878 | 238.5713 | 240.0827 | 236.3795 | 211.736 | 206.5978 | 236.0027
1455.1824 | 1382.1824 | 305.1578 | 236.9793 | 238.5736 | 240.1055 | 236.3936 | 211.7364 | 206.6207 | 236.0234
1456.1839 | 1383.1839 | 305.2414 | 236.9674 | 238.5818 | 239.9902 | 236.3975 | 211.7178 | 206.6285 | 236.0208
1457.1853 | 1384.1853 | 305.3487 | 236.9627 | 238.5865 | 240.0249 | 236.423 | 211.7276 | 206.6475 | 236.0269
1458.1768 | 1385.1768 | 305.4657 | 236.959 | 238.5961 | 239.9951 | 236.4335 | 211.7365 | 206.6743 | 236.0145
1459.1782 | 1386.1782 | 305.6109 | 236.9449 | 238.6189 | 239.98 | 236.4371 | 211.7531 | 206.701 | 236.0273
1460.1796 | 1387.1796 | 305.8076 | 236.9395 | 238.6157 | 239.9682 | 236.4534 | 211.7655 | 206.7268 | 236.0285
1461.1811 | 1388.1811 | 305.9239 | 236.9358 | 238.6259 | 240.0006 | 236.4475 | 211.7923 | 206.7435 | 236.0403
1462.1825 | 1389.1825 | 306.0344 | 236.9406 | 238.6262 | 240.0096 | 236.4667 | 211.8188 | 206.7662 | 236.0383
1463.184 | 1390.184 | 306.2694 | 236.9443 | 238.6367 | 239.9895 | 236.4811 | 211.8384 | 206.774 | 236.0279
1464.1854 | 1391.1854 | 306.4554 | 236.9561 | 238.6365 | 240.0263 | 236.4936 | 211.8601 | 206.7922 | 236.0383
1465.1868 | 1392.1868 | 306.5022 | 236.9695 | 238.6593 | 240.0526 | 236.5005 | 211.8888 | 206.7958 | 236.0403
1466.1783 | 1393.1783 | 306.581 | 236.9949 | 238.6842 | 240.004 | 236.5132 | 211.9165 | 206.8075 | 236.0544
1467.1797 | 1394.1797 | 306.586 | 237.0125 | 238.6933 | 240.015 | 236.5294 | 211.9479 | 206.8202 | 236.0366
1468.1811 | 1395.1811 | 306.6022 | 237.0367 | 238.7225 | 240.0701 | 236.5374 | 211.9664 | 206.8395 | 236.0554
1469.1826 | 1396.1826 | 306.5836 | 237.0608 | 238.7364 | 240.1162 | 236.5539 | 211.9661 | 206.8621 | 236.0662
1470.184 | 1397.184 | 306.5169 | 237.0843 | 238.7719 | 240.0693 | 236.5614 | 211.9808 | 206.8846 | 236.0621
1471.1855 | 1398.1855 | 306.3995 | 237.1111 | 238.782 | 240.1173 | 236.5797 | 211.9833 | 206.9131 | 236.0666
1472.1869 | 1399.1869 | 306.3809 | 237.1314 | 238.8106 | 240.103 | 236.5807 | 211.9996 | 206.9397 | 236.0827
1473.1783 | 1400.1783 | 306.4532 | 237.1453 | 238.8195 | 240.065 | 236.5945 | 212.0128 | 206.9643 | 236.0821
1474.1798 | 1401.1798 | 306.5829 | 237.155 | 238.844 | 240.0834 | 236.609 | 212.0362 | 206.9794 | 236.0739
1475.1812 | 1402.1812 | 306.5525 | 237.1686 | 238.8522 | 240.1512 | 236.6226 | 212.0514 | 206.9936 | 236.089
1476.1826 | 1403.1826 | 306.5089 | 237.1877 | 238.8729 | 240.1387 | 236.6259 | 212.0739 | 207.0098 | 236.0953
1477.1841 | 1404.1841 | 306.4833 | 237.196 | 238.8982 | 240.2024 | 236.638 | 212.0952 | 207.0308 | 236.0871
1478.1755 | 1405.1755 | 306.4073 | 237.19 | 238.9099 | 240.2444 | 236.653 | 212.1139 | 207.045 | 236.1229
1479.177 | 1406.177 | 306.3267 | 237.1936 | 238.9274 | 240.2482 | 236.6686 | 212.1272 | 207.0598 | 236.1128
1480.1784 | 1407.1784 | 306.4011 | 237.2058 | 238.9344 | 240.325 | 236.6719 | 212.1443 | 207.0784 | 236.1352
1481.1798 | 1408.1798 | 306.4983 | 237.2093 | 238.9388 | 240.2835 | 236.6812 | 212.1632 | 207.0942 | 236.1202
1482.1813 | 1409.1813 | 306.6464 | 237.2168 | 238.9292 | 240.3383 | 236.6939 | 212.1932 | 207.1066 | 236.1495
1483.1827 | 1410.1827 | 306.6963 | 237.2261 | 238.9521 | 240.2411 | 236.7129 | 212.2142 | 207.1264 | 236.1611
1484.1842 | 1411.1842 | 306.7933 | 237.2387 | 238.9525 | 240.2931 | 236.722 | 212.2298 | 207.149 | 236.1653
1485.1856 | 1412.1856 | 306.7253 | 237.2467 | 238.9556 | 240.3082 | 236.7295 | 212.2429 | 207.1704 | 236.1676
1486.177 | 1413.177 | 306.6374 | 237.2547 | 238.9687 | 240.3399 | 236.7493 | 212.2659 | 207.1879 | 236.1654
1487.1785 | 1414.1785 | 306.6231 | 237.262 | 238.9722 | 240.4004 | 236.7627 | 212.2877 | 207.2089 | 236.1699
1488.1799 | 1415.1799 | 306.5857 | 237.2654 | 238.976 | 240.3963 | 236.776 | 212.3066 | 207.2164 | 236.2037
1489.1813 | 1416.1813 | 306.5019 | 237.2795 | 238.9642 | 240.3962 | 236.7752 | 212.3368 | 207.232 | 236.1973
1490.1828 | 1417.1828 | 306.3344 | 237.2787 | 238.954 | 240.4687 | 236.8205 | 212.3605 | 207.2479 | 236.2158
1491.1842 | 1418.1842 | 306.1789 | 237.2856 | 238.9312 | 240.4452 | 236.8205 | 212.3782 | 207.2644 | 236.2152
1492.1857 | 1419.1857 | 306.0378 | 237.2875 | 238.9163 | 240.4673 | 236.8365 | 212.3898 | 207.2813 | 236.2255
1493.1871 | 1420.1871 | 305.9034 | 237.2987 | 238.8983 | 240.4557 | 236.8595 | 212.3904 | 207.2931 | 236.2101
1494.1785 | 1421.1785 | 305.8518 | 237.3064 | 238.8632 | 240.4413 | 236.8713 | 212.3894 | 207.3064 | 236.2259
1495.18 | 1422.18 | 305.8751 | 237.3175 | 238.8596 | 240.5197 | 236.8838 | 212.3878 | 207.3238 | 236.2132
1496.1814 | 1423.1814 | 306.06 | 237.3228 | 238.8432 | 240.5625 | 236.8971 | 212.3936 | 207.3367 | 236.2118
1497.1828 | 1424.1828 | 306.1579 | 237.3194 | 238.8245 | 240.5392 | 236.9095 | 212.4094 | 207.3445 | 236.2145
1498.1843 | 1425.1843 | 306.2467 | 237.3149 | 238.8016 | 240.6104 | 236.9248 | 212.4198 | 207.3609 | 236.2037
1499.1757 | 1426.1757 | 306.2818 | 237.3118 | 238.7889 | 240.612 | 236.9328 | 212.4403 | 207.378 | 236.222
1500.1771 | 1427.1771 | 306.2974 | 237.3053 | 238.7994 | 240.6336 | 236.9426 | 212.4601 | 207.3891 | 236.2142
1501.1786 | 1428.1786 | 306.2611 | 237.3001 | 238.7814 | 240.691 | 236.9699 | 212.4742 | 207.4048 | 236.22
1502.18 | 1429.18 | 306.2778 | 237.2937 | 238.7729 | 240.7139 | 236.973 | 212.4936 | 207.4117 | 236.2186
1503.1815 | 1430.1815 | 306.1797 | 237.2974 | 238.7844 | 240.759 | 236.9854 | 212.5135 | 207.4209 | 236.2226
1504.1829 | 1431.1829 | 306.132 | 237.2846 | 238.7874 | 240.7824 | 237.0077 | 212.5322 | 207.436 | 236.2319
1505.1843 | 1432.1843 | 306.0714 | 237.277 | 238.7694 | 240.7803 | 237.0121 | 212.564 | 207.4588 | 236.2205
1506.1858 | 1433.1858 | 306.1173 | 237.2704 | 238.7979 | 240.818 | 237.0187 | 212.5849 | 207.4648 | 236.2285
1507.1872 | 1434.1872 | 306.2061 | 237.2654 | 238.7939 | 240.8551 | 237.0385 | 212.6146 | 207.4781 | 236.2528
1508.1787 | 1435.1787 | 306.3055 | 237.2667 | 238.7999 | 240.8793 | 237.0438 | 212.6383 | 207.493 | 236.259
1509.1801 | 1436.1801 | 306.327 | 237.2686 | 238.8025 | 240.8962 | 237.0643 | 212.6699 | 207.5132 | 236.2467
1510.1815 | 1437.1815 | 306.3479 | 237.272 | 238.8047 | 240.9091 | 237.0727 | 212.6831 | 207.5264 | 236.2641
1511.183 | 1438.183 | 306.2661 | 237.2845 | 238.8099 | 240.9433 | 237.0768 | 212.6982 | 207.5543 | 236.233
1512.1844 | 1439.1844 | 306.1969 | 237.2938 | 238.8157 | 240.8932 | 237.0952 | 212.7116 | 207.563 | 236.2435
1513.1859 | 1440.1859 | 306.1732 | 237.3063 | 238.8303 | 240.92 | 237.1021 | 212.7118 | 207.5773 | 236.2265
1514.1773 | 1441.1773 | 306.1936 | 237.3164 | 238.8348 | 240.9713 | 237.1164 | 212.7158 | 207.5942 | 236.2267
1515.1787 | 1442.1787 | 306.2021 | 237.3313 | 238.8482 | 240.949 | 237.1202 | 212.7258 | 207.6111 | 236.2373
1516.1802 | 1443.1802 | 306.2105 | 237.3498 | 238.8759 | 240.9668 | 237.1345 | 212.7573 | 207.6288 | 236.2655
1517.1816 | 1444.1816 | 306.2477 | 237.3675 | 238.89 | 240.9766 | 237.1399 | 212.7675 | 207.649 | 236.2714
1518.183 | 1445.183 | 306.2055 | 237.3853 | 238.9083 | 241.0204 | 237.154 | 212.7941 | 207.658 | 236.2829
1519.1845 | 1446.1845 | 306.2345 | 237.4055 | 238.9287 | 240.9595 | 237.1604 | 212.813 | 207.6781 | 236.2827
1520.1759 | 1447.1759 | 306.2894 | 237.4395 | 238.9526 | 240.981 | 237.1801 | 212.8418 | 207.7013 | 236.2903
1521.1773 | 1448.1773 | 306.2608 | 237.4717 | 238.965 | 240.9828 | 237.1904 | 212.8646 | 207.7164 | 236.2818
1522.1788 | 1449.1788 | 306.2194 | 237.5015 | 238.9905 | 241.013 | 237.1928 | 212.8946 | 207.7322 | 236.2885
1523.1802 | 1450.1802 | 306.2607 | 237.5283 | 239.0074 | 241.0482 | 237.2095 | 212.9212 | 207.7479 | 236.2792
1524.1817 | 1451.1817 | 306.2479 | 237.5684 | 239.0301 | 241.0518 | 237.2168 | 212.9428 | 207.7708 | 236.2926
1525.1831 | 1452.1831 | 306.177 | 237.5975 | 239.0448 | 241.1085 | 237.2186 | 212.9661 | 207.7942 | 236.302
1526.1845 | 1453.1845 | 305.998 | 237.6254 | 239.0625 | 241.1308 | 237.242 | 212.9789 | 207.8171 | 236.31
1527.176 | 1454.176 | 306.0548 | 237.6528 | 239.0696 | 241.1462 | 237.2568 | 213.0108 | 207.8371 | 236.3103
1528.1774 | 1455.1774 | 306.1154 | 237.678 | 239.0833 | 241.2058 | 237.2595 | 213.0289 | 207.8583 | 236.3049
1529.1789 | 1456.1789 | 306.0692 | 237.6953 | 239.1131 | 241.22 | 237.2733 | 213.0502 | 207.8842 | 236.3149
1530.1803 | 1457.1803 | 306.0823 | 237.7302 | 239.136 | 241.2282 | 237.2793 | 213.0753 | 207.9158 | 236.3102
1531.1817 | 1458.1817 | 306.1126 | 237.7554 | 239.1628 | 241.2499 | 237.2919 | 213.087 | 207.9327 | 236.3059
1532.1832 | 1459.1832 | 306.0648 | 237.7876 | 239.1792 | 241.2062 | 237.2969 | 213.1133 | 207.9676 | 236.3258
1533.1846 | 1460.1846 | 306.0142 | 237.8117 | 239.192 | 241.2765 | 237.3085 | 213.1245 | 207.9951 | 236.3278
1534.1861 | 1461.1861 | 306.0691 | 237.8325 | 239.1982 | 241.3088 | 237.3169 | 213.1446 | 208.0278 | 236.3236
1535.1775 | 1462.1775 | 306.1253 | 237.8535 | 239.2133 | 241.3229 | 237.3258 | 213.1531 | 208.0628 | 236.3288
1536.1789 | 1463.1789 | 306.1255 | 237.8681 | 239.2315 | 241.2919 | 237.336 | 213.1717 | 208.0892 | 236.3336
1537.1804 | 1464.1804 | 306.1331 | 237.8751 | 239.2307 | 241.3405 | 237.36 | 213.193 | 208.1203 | 236.3469 | Time of first failure
1538.1818 | 1465.1818 | 306.1863 | 237.8861 | 239.2504 | 241.3482 | 237.3639 | 213.2179 | 208.1545 | 236.3518 | 1464 | 0
1539.1832 | 1466.1832 | 306.2287 | 237.8917 | 239.2753 | 241.3753 | 237.3766 | 213.2314 | 208.1745 | 236.3584 | 1464 | 900
1540.1847 | 1467.1847 | 306.2458 | 237.8947 | 239.2925 | 241.3552 | 237.3782 | 213.2604 | 208.2023 | 236.3581
1541.1761 | 1468.1761 | 306.2396 | 237.9038 | 239.3125 | 241.3234 | 237.3905 | 213.2842 | 208.2409 | 236.3682
1542.1775 | 1469.1775 | 306.2092 | 237.9049 | 239.3294 | 241.2638 | 237.4036 | 213.2972 | 208.2656 | 236.3712
1543.179 | 1470.179 | 306.1925 | 237.9152 | 239.3357 | 241.3158 | 237.4038 | 213.3318 | 208.2952 | 236.3707
1544.1804 | 1471.1804 | 306.1044 | 237.9239 | 239.3457 | 241.3422 | 237.4102 | 213.358 | 208.3184 | 236.3771
1545.1819 | 1472.1819 | 306.1102 | 237.9304 | 239.3399 | 241.4023 | 237.423 | 213.3724 | 208.338 | 236.3624
1546.1833 | 1473.1833 | 306.2051 | 237.9448 | 239.3467 | 241.3913 | 237.4341 | 213.3895 | 208.3628 | 236.3713
1547.1847 | 1474.1847 | 306.241 | 237.9637 | 239.3477 | 241.4313 | 237.4419 | 213.4095 | 208.3857 | 236.3758
1548.1862 | 1475.1862 | 306.2866 | 237.9751 | 239.3532 | 241.4317 | 237.4559 | 213.4401 | 208.4048 | 236.3807
1549.1876 | 1476.1876 | 306.2624 | 237.9941 | 239.3526 | 241.3529 | 237.453 | 213.464 | 208.4268 | 236.3756
1550.179 | 1477.179 | 306.1742 | 237.9951 | 239.355 | 241.1888 | 237.4641 | 213.4662 | 208.4419 | 236.3719
1551.1805 | 1478.1805 | 306.1144 | 238.0076 | 239.3423 | 241.2414 | 237.4688 | 213.4683 | 208.4595 | 236.3665
1552.1819 | 1479.1819 | 306.0866 | 238.0071 | 239.3452 | 241.2404 | 237.4773 | 213.4807 | 208.4738 | 236.3653
1553.1834 | 1480.1834 | 306.0338 | 238.0171 | 239.3325 | 241.2441 | 237.4883 | 213.4889 | 208.4953 | 236.3555
1554.1848 | 1481.1848 | 305.9107 | 238.0346 | 239.3305 | 241.2507 | 237.4839 | 213.5049 | 208.5059 | 236.3775
1555.1862 | 1482.1862 | 305.7982 | 238.0357 | 239.3278 | 241.308 | 237.4986 | 213.5171 | 208.5272 | 236.3738
1556.1777 | 1483.1777 | 305.6845 | 238.0447 | 239.325 | 241.3302 | 237.509 | 213.5157 | 208.5453 | 236.3847
1557.1791 | 1484.1791 | 305.6809 | 238.0562 | 239.324 | 241.3504 | 237.5154 | 213.5292 | 208.5598 | 236.3913
1558.1806 | 1485.1806 | 305.7935 | 238.0691 | 239.3226 | 241.3914 | 237.533 | 213.5382 | 208.5824 | 236.4066
1559.182 | 1486.182 | 305.9103 | 238.0771 | 239.3312 | 241.4224 | 237.5264 | 213.5489 | 208.6033 | 236.4016
1560.1834 | 1487.1834 | 305.8478 | 238.0821 | 239.3233 | 241.4623 | 237.5427 | 213.5685 | 208.6215 | 236.4191
1561.245 | 1488.245 | 305.8244 | 238.0877 | 239.3181 | 241.4837 | 237.5622 | 213.582 | 208.6504 | 236.416
1562.1763 | 1489.1763 | 305.8737 | 238.0952 | 239.3305 | 241.5458 | 237.5612 | 213.6043 | 208.6716 | 236.4178
1563.1777 | 1490.1777 | 305.9165 | 238.1024 | 239.3155 | 241.5497 | 237.579 | 213.6239 | 208.6941 | 236.4406
1564.1792 | 1491.1792 | 305.9561 | 238.1147 | 239.3151 | 241.5471 | 237.5918 | 213.6372 | 208.7215 | 236.4472
1565.1806 | 1492.1806 | 305.9129 | 238.1198 | 239.3162 | 241.5663 | 237.6061 | 213.6516 | 208.7507 | 236.4573
1566.1821 | 1493.1821 | 305.8829 | 238.1361 | 239.3186 | 241.6221 | 237.6038 | 213.6593 | 208.7629 | 236.4592
1567.1835 | 1494.1835 | 305.843 | 238.1494 | 239.3128 | 241.6863 | 237.626 | 213.657 | 208.7855 | 236.4779
1568.1849 | 1495.1849 | 305.8273 | 238.1598 | 239.3126 | 241.711 | 237.6369 | 213.6523 | 208.8051 | 236.4695
1569.1764 | 1496.1764 | 305.7823 | 238.1772 | 239.3029 | 241.6658 | 237.6433 | 213.6461 | 208.8242 | 236.4999
1570.1778 | 1497.1778 | 305.7973 | 238.1865 | 239.3013 | 241.668 | 237.6558 | 213.6504 | 208.8433 | 236.4912
1571.1792 | 1498.1792 | 305.7908 | 238.1998 | 239.3003 | 241.6742 | 237.6786 | 213.6455 | 208.8512 | 236.4977
1572.1807 | 1499.1807 | 305.8607 | 238.2049 | 239.2976 | 241.6951 | 237.6872 | 213.6493 | 208.8676 | 236.5134
1573.1821 | 1500.1821 | 305.936 | 238.2147 | 239.2892 | 241.7185 | 237.7123 | 213.6541 | 208.8831 | 236.5189
1574.1836 | 1501.1836 | 306.0679 | 238.2236 | 239.2979 | 241.7498 | 237.7293 | 213.6596 | 208.8998 | 236.5204
1575.185 | 1502.185 | 306.1724 | 238.2348 | 239.294 | 241.7831 | 237.7312 | 213.672 | 208.918 | 236.5428
1576.2065 | 1503.2065 | 306.212 | 238.2454 | 239.3055 | 241.7836 | 237.743 | 213.6825 | 208.943 | 236.552
1577.1779 | 1504.1779 | 306.3238 | 238.2524 | 239.3338 | 241.7979 | 237.7541 | 213.6841 | 208.9536 | 236.5621
1578.1793 | 1505.1793 | 306.3375 | 238.2698 | 239.3365 | 241.799 | 237.7785 | 213.7007 | 208.9686 | 236.5698
1579.1808 | 1506.1808 | 306.3184 | 238.2831 | 239.3628 | 241.8166 | 237.7864 | 213.7082 | 208.9918 | 236.5886
1580.1822 | 1507.1822 | 306.3126 | 238.2978 | 239.3834 | 241.855 | 237.791 | 213.7078 | 209.0147 | 236.6243
1581.1836 | 1508.1836 | 306.311 | 238.3167 | 239.3943 | 241.6606 | 237.8004 | 213.7076 | 209.0309 | 236.6326
1582.1851 | 1509.1851 | 306.2821 | 238.3356 | 239.4137 | 241.6988 | 237.8081 | 213.7089 | 209.0427 | 236.6388
1583.1765 | 1510.1765 | 306.3056 | 238.3565 | 239.4336 | 241.7686 | 237.8226 | 213.7064 | 209.0664 | 236.6566
1584.1779 | 1511.1779 | 306.3153 | 238.3875 | 239.4526 | 241.7965 | 237.8338 | 213.7163 | 209.0803 | 236.6674
1585.1794 | 1512.1794 | 306.2144 | 238.4125 | 239.4654 | 241.8613 | 237.8553 | 213.7287 | 209.1018 | 236.6764
1586.1808 | 1513.1808 | 306.2346 | 238.4406 | 239.4835 | 241.8816 | 237.8756 | 213.7353 | 209.1025 | 236.6863
1587.1823 | 1514.1823 | 306.3281 | 238.4676 | 239.487 | 241.8817 | 237.8826 | 213.7555 | 209.1151 | 236.693
1588.1837 | 1515.1837 | 306.3495 | 238.4934 | 239.5012 | 241.8474 | 237.9043 | 213.7674 | 209.1163 | 236.7006
1589.1851 | 1516.1851 | 306.3809 | 238.5101 | 239.5158 | 241.8535 | 237.9276 | 213.7871 | 209.1241 | 236.7223
1590.1866 | 1517.1866 | 306.4518 | 238.5222 | 239.5178 | 241.7663 | 237.9367 | 213.8065 | 209.1283 | 236.743
1591.178 | 1518.178 | 306.4706 | 238.5421 | 239.5252 | 241.8583 | 237.9524 | 213.8264 | 209.1349 | 236.7268
1592.1794 | 1519.1794 | 306.4695 | 238.5483 | 239.5314 | 241.6612 | 237.9635 | 213.84 | 209.1444 | 236.7471
1593.1809 | 1520.1809 | 306.4954 | 238.5575 | 239.5394 | 241.7168 | 237.9777 | 213.8369 | 209.1494 | 236.7585
1594.1823 | 1521.1823 | 306.5606 | 238.5659 | 239.5377 | 241.6435 | 237.9896 | 213.8385 | 209.1568 | 236.7563
1595.1838 | 1522.1838 | 306.6156 | 238.57 | 239.5439 | 241.6907 | 237.9996 | 213.8343 | 209.1635 | 236.7724
1596.1852 | 1523.1852 | 306.6117 | 238.574 | 239.5427 | 241.7804 | 238.019 | 213.8512 | 209.1704 | 236.7575
1597.1866 | 1524.1866 | 306.5292 | 238.5747 | 239.542 | 241.7806 | 238.043 | 213.8621 | 209.1668 | 236.7657
1598.1881 | 1525.1881 | 306.4533 | 238.5703 | 239.5389 | 241.839 | 238.0505 | 213.8738 | 209.1642 | 236.7589
1599.1795 | 1526.1795 | 306.3467 | 238.5689 | 239.5485 | 241.8379 | 238.0631 | 213.8788 | 209.166 | 236.7576
1600.1809 | 1527.1809 | 306.3132 | 238.5665 | 239.5524 | 241.8581 | 238.0687 | 213.8876 | 209.1659 | 236.7663
1601.1824 | 1528.1824 | 306.2469 | 238.5604 | 239.5637 | 241.8254 | 238.0991 | 213.8854 | 209.1726 | 236.7788
1602.1838 | 1529.1838 | 306.2892 | 238.5587 | 239.5698 | 241.9131 | 238.1012 | 213.8968 | 209.163 | 236.7912
1603.1853 | 1530.1853 | 306.3451 | 238.5565 | 239.5728 | 241.9065 | 238.1229 | 213.8996 | 209.1699 | 236.786
1604.1767 | 1531.1767 | 306.4639 | 238.5555 | 239.5881 | 241.9594 | 238.1325 | 213.9183 | 209.1686 | 236.7874
1605.1781 | 1532.1781 | 306.5348 | 238.5724 | 239.6092 | 241.9547 | 238.13 | 213.9321 | 209.1695 | 236.7864
1606.1796 | 1533.1796 | 306.5664 | 238.5842 | 239.6158 | 241.9403 | 238.1427 | 213.9434 | 209.173 | 236.7835
1607.181 | 1534.181 | 306.5662 | 238.5864 | 239.6456 | 241.8457 | 238.1671 | 213.9452 | 209.1665 | 236.7949
1608.1825 | 1535.1825 | 306.6153 | 238.6006 | 239.6739 | 241.9133 | 238.1919 | 213.926 | 209.171 | 236.7787
1609.1839 | 1536.1839 | 306.5772 | 238.6129 | 239.6973 | 241.9687 | 238.2031 | 213.9206 | 209.1706 | 236.7941
1610.1853 | 1537.1853 | 306.5643 | 238.633 | 239.7011 | 242.0105 | 238.2213 | 213.9192 | 209.1767 | 236.7887
1611.1768 | 1538.1768 | 306.645 | 238.6506 | 239.7208 | 242.0014 | 238.2417 | 213.9132 | 209.1725 | 236.7976
1612.1782 | 1539.1782 | 306.6664 | 238.6705 | 239.7429 | 242.0672 | 238.255 | 213.904 | 209.1834 | 236.8005
1613.1796 | 1540.1796 | 306.6705 | 238.6929 | 239.7591 | 242.0738 | 238.2585 | 213.9031 | 209.1883 | 236.7883
1614.1811 | 1541.1811 | 306.7353 | 238.7134 | 239.7594 | 242.0736 | 238.2866 | 213.9107 | 209.1886 | 236.7994
1615.1825 | 1542.1825 | 306.8311 | 238.7315 | 239.7897 | 242.1296 | 238.2979 | 213.9138 | 209.1833 | 236.8057
1616.184 | 1543.184 | 306.9772 | 238.7613 | 239.8294 | 242.1254 | 238.3191 | 213.9183 | 209.1886 | 236.7954
1617.1854 | 1544.1854 | 306.9407 | 238.7816 | 239.8552 | 242.1434 | 238.3101 | 213.9156 | 209.1892 | 236.8075
1618.1868 | 1545.1868 | 306.8185 | 238.807 | 239.8841 | 242.1654 | 238.3343 | 213.9305 | 209.1946 | 236.8041
1619.1783 | 1546.1783 | 306.7478 | 238.839 | 239.9029 | 242.1844 | 238.3399 | 213.9311 | 209.2034 | 236.7911
1620.1797 | 1547.1797 | 306.6979 | 238.8754 | 239.9121 | 242.1751 | 238.3453 | 213.9403 | 209.2027 | 236.8214
1621.1811 | 1548.1811 | 306.6177 | 238.9027 | 239.9187 | 242.2229 | 238.3574 | 213.9357 | 209.2091 | 236.8162
1622.1826 | 1549.1826 | 306.6176 | 238.932 | 239.9223 | 242.1919 | 238.3527 | 213.9149 | 209.212 | 236.824
1623.184 | 1550.184 | 306.6862 | 238.956 | 239.9442 | 242.23 | 238.3638 | 213.9208 | 209.2161 | 236.8256
1624.1855 | 1551.1855 | 306.6696 | 238.9897 | 239.959 | 242.3048 | 238.3657 | 213.9305 | 209.2211 | 236.841
1625.1869 | 1552.1869 | 306.7034 | 239.002 | 239.9723 | 242.3251 | 238.3817 | 213.942 | 209.2214 | 236.8519
1626.1783 | 1553.1783 | 306.7339 | 239.0341 | 239.9912 | 242.3137 | 238.3917 | 213.9678 | 209.2215 | 236.8487
1627.1798 | 1554.1798 | 306.7375 | 239.0627 | 240.0041 | 242.3129 | 238.3987 | 213.9791 | 209.2218 | 236.828
1628.1812 | 1555.1812 | 306.7515 | 239.0947 | 240.0353 | 242.3728 | 238.4016 | 213.9991 | 209.2276 | 236.8595
1629.1826 | 1556.1826 | 306.7834 | 239.1247 | 240.0549 | 242.3898 | 238.4062 | 213.9978 | 209.2182 | 236.8405
1630.1841 | 1557.1841 | 306.8218 | 239.155 | 240.0834 | 242.3876 | 238.425 | 214.0116 | 209.2305 | 236.8407
1631.1855 | 1558.1855 | 306.786 | 239.1839 | 240.1087 | 242.396 | 238.4284 | 214.0226 | 209.2326 | 236.8505
1632.177 | 1559.177 | 306.6654 | 239.2133 | 240.1195 | 242.4107 | 238.4437 | 214.0382 | 209.2418 | 236.8711
1633.1784 | 1560.1784 | 306.5778 | 239.2407 | 240.1549 | 242.4191 | 238.4532 | 214.0599 | 209.2561 | 236.8717
1634.1798 | 1561.1798 | 306.4738 | 239.2579 | 240.1884 | 242.4186 | 238.4544 | 214.0719 | 209.2681 | 236.8715
1635.1813 | 1562.1813 | 306.3563 | 239.2732 | 240.226 | 242.4388 | 238.4668 | 214.0887 | 209.2923 | 236.8667
1636.1827 | 1563.1827 | 306.2464 | 239.2817 | 240.2489 | 242.4318 | 238.4791 | 214.0987 | 209.295 | 236.8755
1637.1842 | 1564.1842 | 306.112 | 239.29 | 240.2612 | 242.4566 | 238.4931 | 214.1011 | 209.3029 | 236.8873
1638.1856 | 1565.1856 | 306.117 | 239.3041 | 240.267 | 242.4746 | 238.4928 | 214.1215 | 209.3104 | 236.867
1639.187 | 1566.187 | 306.1784 | 239.3118 | 240.2684 | 242.4734 | 238.508 | 214.14 | 209.3175 | 236.865
1640.1785 | 1567.1785 | 306.2812 | 239.3137 | 240.2799 | 242.5016 | 238.5163 | 214.1495 | 209.3266 | 236.8743
1641.1799 | 1568.1799 | 306.3665 | 239.3203 | 240.2814 | 242.4339 | 238.5302 | 214.1647 | 209.3261 | 236.8686
1642.1813 | 1569.1813 | 306.3362 | 239.3284 | 240.2829 | 242.4803 | 238.5242 | 214.1777 | 209.3269 | 236.8548
1643.1828 | 1570.1828 | 306.3941 | 239.3313 | 240.2763 | 242.4978 | 238.5438 | 214.1822 | 209.3331 | 236.8659
1644.1842 | 1571.1842 | 306.3631 | 239.34 | 240.2706 | 242.4989 | 238.5525 | 214.1986 | 209.3445 | 236.8496
1645.1857 | 1572.1857 | 306.2463 | 239.3482 | 240.2671 | 242.4954 | 238.5631 | 214.2045 | 209.354 | 236.8449
1646.1871 | 1573.1871 | 306.1768 | 239.3706 | 240.2549 | 242.5063 | 238.5745 | 214.2184 | 209.3636 | 236.8509
1647.1785 | 1574.1785 | 306.1625 | 239.383 | 240.2431 | 242.409 | 238.5918 | 214.2312 | 209.3693 | 236.8494
1648.18 | 1575.18 | 306.191 | 239.4056 | 240.235 | 242.4405 | 238.5897 | 214.2357 | 209.3735 | 236.847
1649.1814 | 1576.1814 | 306.1093 | 239.4112 | 240.2372 | 242.4522 | 238.6006 | 214.245 | 209.3729 | 236.8348
1650.1828 | 1577.1828 | 305.9789 | 239.4315 | 240.2303 | 242.3569 | 238.6304 | 214.2587 | 209.3828 | 236.8451
1651.1843 | 1578.1843 | 305.8367 | 239.449 | 240.2244 | 242.3706 | 238.6215 | 214.2756 | 209.3902 | 236.8526
1652.1857 | 1579.1857 | 305.7272 | 239.4653 | 240.2226 | 242.3636 | 238.6402 | 214.2844 | 209.3983 | 236.8527
1653.1772 | 1580.1772 | 305.6385 | 239.4746 | 240.2197 | 242.3541 | 238.6469 | 214.3029 | 209.4047 | 236.8248
1654.1786 | 1581.1786 | 305.621 | 239.4916 | 240.2277 | 242.3569 | 238.6674 | 214.3138 | 209.4184 | 236.8469
1655.18 | 1582.18 | 305.587 | 239.5042 | 240.2271 | 242.4098 | 238.6695 | 214.3304 | 209.4289 | 236.8537
1656.1815 | 1583.1815 | 305.5411 | 239.5134 | 240.2236 | 242.4418 | 238.684 | 214.3301 | 209.4414 | 236.8395
1657.1829 | 1584.1829 | 305.5239 | 239.5323 | 240.2175 | 242.451 | 238.6883 | 214.3342 | 209.4422 | 236.8368
1658.1844 | 1585.1844 | 305.5503 | 239.5354 | 240.2077 | 242.4549 | 238.6905 | 214.3378 | 209.4589 | 236.8423
1659.1858 | 1586.1858 | 305.5593 | 239.549 | 240.2043 | 242.4712 | 238.7001 | 214.3363 | 209.4689 | 236.8297
1660.1772 | 1587.1772 | 305.6636 | 239.5518 | 240.2019 | 242.4719 | 238.7069 | 214.3455 | 209.4759 | 236.8341
1661.1787 | 1588.1787 | 305.6964 | 239.5678 | 240.1866 | 242.4559 | 238.7278 | 214.3503 | 209.4931 | 236.857
1662.1801 | 1589.1801 | 305.7866 | 239.5873 | 240.1889 | 242.4872 | 238.73 | 214.3501 | 209.5047 | 236.8539
1663.1815 | 1590.1815 | 305.9165 | 239.6051 | 240.1874 | 242.4927 | 238.7409 | 214.3599 | 209.5056 | 236.8495
1664.183 | 1591.183 | 306.0243 | 239.6223 | 240.1843 | 242.4974 | 238.7534 | 214.366 | 209.5122 | 236.8502
1665.1844 | 1592.1844 | 306.1723 | 239.6516 | 240.1837 | 242.5571 | 238.7615 | 214.3795 | 209.5221 | 236.8579
1666.1859 | 1593.1859 | 306.2698 | 239.6758 | 240.1916 | 242.585 | 238.7675 | 214.3984 | 209.5251 | 236.8519
1667.1773 | 1594.1773 | 306.3995 | 239.6888 | 240.1803 | 242.5829 | 238.7812 | 214.4186 | 209.5284 | 236.8616
1668.1787 | 1595.1787 | 306.4405 | 239.696 | 240.1826 | 242.5884 | 238.8033 | 214.4342 | 209.5381 | 236.8495
1669.1802 | 1596.1802 | 306.5064 | 239.7012 | 240.1779 | 242.6169 | 238.812 | 214.4595 | 209.545 | 236.8542
1670.1816 | 1597.1816 | 306.6282 | 239.6867 | 240.1877 | 242.6272 | 238.8223 | 214.4798 | 209.5585 | 236.8663
1671.183 | 1598.183 | 306.7152 | 239.6704 | 240.1815 | 242.6417 | 238.826 | 214.4926 | 209.5634 | 236.8753
1672.1845 | 1599.1845 | 306.8449 | 239.6537 | 240.175 | 242.6356 | 238.8416 | 214.5135 | 209.5704 | 236.8619
1673.1859 | 1600.1859 | 306.9634 | 239.6417 | 240.171 | 242.61 | 238.8501 | 214.5302 | 209.5739 | 236.877
1674.1773 | 1601.1773 | 306.9485 | 239.6447 | 240.1749 | 242.6177 | 238.8764 | 214.5534 | 209.5844 | 236.8939
1675.1788 | 1602.1788 | 306.948 | 239.6384 | 240.1749 | 242.618 | 238.8666 | 214.5756 | 209.6001 | 236.9026
1676.1802 | 1603.1802 | 306.8982 | 239.6404 | 240.1645 | 242.5873 | 238.8799 | 214.6097 | 209.6304 | 236.8935
1677.1817 | 1604.1817 | 306.8284 | 239.6361 | 240.1573 | 242.6216 | 238.8794 | 214.6377 | 209.6487 | 236.8999
1678.1831 | 1605.1831 | 306.7553 | 239.643 | 240.144 | 242.6294 | 238.8813 | 214.6575 | 209.679 | 236.8997
1679.1845 | 1606.1845 | 306.7086 | 239.6436 | 240.1354 | 242.6249 | 238.8857 | 214.6852 | 209.7047 | 236.9013
1680.186 | 1607.186 | 306.6095 | 239.6507 | 240.1256 | 242.6223 | 238.8789 | 214.7099 | 209.7339 | 236.8923
1681.1874 | 1608.1874 | 306.5654 | 239.6463 | 240.1039 | 242.6209 | 238.9025 | 214.7368 | 209.7523 | 236.8724
1682.1789 | 1609.1789 | 306.605 | 239.648 | 240.1028 | 242.6278 | 238.8976 | 214.7599 | 209.7688 | 236.9014
1683.1803 | 1610.1803 | 306.6191 | 239.649 | 240.0988 | 242.6342 | 238.9097 | 214.7856 | 209.7807 | 236.9127
1684.1817 | 1611.1817 | 306.6336 | 239.6567 | 240.0904 | 242.6184 | 238.9007 | 214.8075 | 209.7879 | 236.9083
1685.1832 | 1612.1832 | 306.6546 | 239.66 | 240.0854 | 242.6619 | 238.9141 | 214.8294 | 209.8026 | 236.9151
1686.1846 | 1613.1846 | 306.6674 | 239.6681 | 240.0887 | 242.7062 | 238.9052 | 214.8525 | 209.8148 | 236.9323
1687.1861 | 1614.1861 | 306.7339 | 239.6782 | 240.1005 | 242.7345 | 238.9139 | 214.8743 | 209.8329 | 236.9231
1688.1775 | 1615.1775 | 306.7446 | 239.6899 | 240.0924 | 242.7942 | 238.9266 | 214.9021 | 209.8454 | 236.9306
1689.1789 | 1616.1789 | 306.6966 | 239.6858 | 240.081 | 242.7835 | 238.9246 | 214.9255 | 209.8627 | 236.9317
1690.1804 | 1617.1804 | 306.6574 | 239.7024 | 240.0769 | 242.813 | 238.9365 | 214.9403 | 209.8875 | 236.9325
1691.1818 | 1618.1818 | 306.604 | 239.697 | 240.0764 | 242.8184 | 238.949 | 214.9572 | 209.9059 | 236.9226
1692.1832 | 1619.1832 | 306.5282 | 239.7015 | 240.0809 | 242.7808 | 238.9516 | 214.9765 | 209.9231 | 236.9043
1693.1847 | 1620.1847 | 306.4894 | 239.6964 | 240.0744 | 242.7668 | 238.963 | 215.0016 | 209.9396 | 236.9138
1694.1761 | 1621.1761 | 306.428 | 239.685 | 240.0651 | 242.6807 | 238.9645 | 215.0185 | 209.9549 | 236.9085
1695.1775 | 1622.1775 | 306.4291 | 239.687 | 240.0655 | 242.6647 | 238.9793 | 215.0465 | 209.9675 | 236.8999
1696.179 | 1623.179 | 306.3631 | 239.6768 | 240.0649 | 242.6505 | 239.0054 | 215.0633 | 209.9833 | 236.8998
1697.1804 | 1624.1804 | 306.3578 | 239.6714 | 240.0601 | 242.6411 | 239.0083 | 215.089 | 209.9922 | 236.8843
1698.1819 | 1625.1819 | 306.3352 | 239.6642 | 240.0768 | 242.6011 | 239.0034 | 215.1138 | 209.9998 | 236.8877
1699.1833 | 1626.1833 | 306.351 | 239.6651 | 240.0878 | 242.6246 | 239.0226 | 215.1287 | 210.0095 | 236.872
1700.1847 | 1627.1847 | 306.3576 | 239.6648 | 240.0996 | 242.6465 | 239.0363 | 215.1434 | 210.0192 | 236.8744
1701.1762 | 1628.1762 | 306.4288 | 239.6697 | 240.1012 | 242.6758 | 239.0473 | 215.1578 | 210.0266 | 236.879
1702.1876 | 1629.1876 | 306.4402 | 239.6836 | 240.1207 | 242.6897 | 239.0727 | 215.1758 | 210.0325 | 236.859
1703.1791 | 1630.1791 | 306.3449 | 239.695 | 240.1305 | 242.667 | 239.0778 | 215.1855 | 210.0393 | 236.8822
1704.1805 | 1631.1805 | 306.3425 | 239.7167 | 240.1515 | 242.6651 | 239.0898 | 215.2024 | 210.0464 | 236.8787
1705.1819 | 1632.1819 | 306.2853 | 239.7208 | 240.1629 | 242.665 | 239.1074 | 215.2175 | 210.048 | 236.8932
1706.1834 | 1633.1834 | 306.2798 | 239.7278 | 240.1808 | 242.7111 | 239.1231 | 215.2383 | 210.0429 | 236.8858
1707.1848 | 1634.1848 | 306.176 | 239.7292 | 240.213 | 242.6746 | 239.1252 | 215.2573 | 210.0331 | 236.8749
1708.1863 | 1635.1863 | 306.1225 | 239.7241 | 240.2185 | 242.6895 | 239.1298 | 215.2722 | 210.0342 | 236.8725
1709.1777 | 1636.1777 | 306.0969 | 239.7149 | 240.2361 | 242.6683 | 239.141 | 215.2849 | 210.0329 | 236.8731
1710.1791 | 1637.1791 | 306.0873 | 239.7026 | 240.2377 | 242.6887 | 239.1473 | 215.2804 | 210.0386 | 236.8841
1711.1806 | 1638.1806 | 306.0202 | 239.6838 | 240.2466 | 242.7241 | 239.1503 | 215.2895 | 210.0573 | 236.8583
1712.182 | 1639.182 | 305.9527 | 239.6714 | 240.2525 | 242.7312 | 239.1498 | 215.296 | 210.0726 | 236.8744
1713.1834 | 1640.1834 | 305.9074 | 239.6689 | 240.2498 | 242.6854 | 239.1476 | 215.3048 | 210.0883 | 236.8731
1714.1849 | 1641.1849 | 305.8499 | 239.665 | 240.2532 | 242.7328 | 239.1555 | 215.3052 | 210.1039 | 236.871
1715.1763 | 1642.1763 | 305.8168 | 239.6601 | 240.2492 | 242.7213 | 239.1496 | 215.3176 | 210.1208 | 236.8381
1716.1777 | 1643.1777 | 305.713 | 239.6505 | 240.2556 | 242.7541 | 239.1586 | 215.3307 | 210.1304 | 236.8544
1717.1792 | 1644.1792 | 305.6004 | 239.6437 | 240.2556 | 242.7835 | 239.1676 | 215.3338 | 210.1464 | 236.8674
1718.1806 | 1645.1806 | 305.4466 | 239.6454 | 240.2557 | 242.7815 | 239.1844 | 215.3363 | 210.1486 | 236.8434
1719.1821 | 1646.1821 | 305.2894 | 239.6496 | 240.2578 | 242.7878 | 239.1763 | 215.3367 | 210.154 | 236.8526
1720.1835 | 1647.1835 | 305.1345 | 239.6502 | 240.2619 | 242.7982 | 239.1825 | 215.3425 | 210.1479 | 236.8404
1721.1849 | 1648.1849 | 304.9977 | 239.6431 | 240.2586 | 242.8119 | 239.1901 | 215.3537 | 210.1485 | 236.8171
1722.1864 | 1649.1864 | 304.9024 | 239.655 | 240.2587 | 242.8275 | 239.1827 | 215.3645 | 210.144 | 236.8363
1723.1878 | 1650.1878 | 304.8912 | 239.6589 | 240.2596 | 242.7811 | 239.177 | 215.3635 | 210.1373 | 236.836
1724.1792 | 1651.1792 | 304.9382 | 239.6673 | 240.2578 | 242.8034 | 239.1759 | 215.3693 | 210.126 | 236.8415
1725.1807 | 1652.1807 | 304.9699 | 239.6793 | 240.2444 | 242.7963 | 239.1686 | 215.3769 | 210.1191 | 236.8417
1726.1821 | 1653.1821 | 305.0301 | 239.6923 | 240.255 | 242.7909 | 239.1774 | 215.3945 | 210.1065 | 236.8515
1727.1836 | 1654.1836 | 305.0999 | 239.712 | 240.2434 | 242.7508 | 239.1845 | 215.4084 | 210.1062 | 236.8313
1728.185 | 1655.185 | 305.2149 | 239.725 | 240.2373 | 242.7781 | 239.1761 | 215.4042 | 210.1034 | 236.8193
1729.1864 | 1656.1864 | 305.3251 | 239.7395 | 240.2521 | 242.7993 | 239.1749 | 215.4172 | 210.1078 | 236.8553
1730.1779 | 1657.1779 | 305.347 | 239.7434 | 240.2538 | 242.8015 | 239.191 | 215.4178 | 210.1206 | 236.8597
1731.1793 | 1658.1793 | 305.4359 | 239.7601 | 240.2665 | 242.8401 | 239.1917 | 215.4228 | 210.1205 | 236.8722
1732.1808 | 1659.1808 | 305.5426 | 239.774 | 240.2774 | 242.8452 | 239.1844 | 215.4251 | 210.1319 | 236.8717
1733.1822 | 1660.1822 | 305.4821 | 239.7931 | 240.2816 | 242.8794 | 239.2101 | 215.4275 | 210.1493 | 236.8677
1734.1836 | 1661.1836 | 305.6203 | 239.8061 | 240.2916 | 242.8879 | 239.2071 | 215.4404 | 210.1627 | 236.8739
1735.1851 | 1662.1851 | 305.7505 | 239.8244 | 240.3092 | 242.8923 | 239.2162 | 215.4429 | 210.1833 | 236.8809
1736.1765 | 1663.1765 | 305.8682 | 239.8381 | 240.3254 | 242.8808 | 239.223 | 215.4484 | 210.1976 | 236.8882
1737.1779 | 1664.1779 | 306.0394 | 239.8578 | 240.3393 | 242.928 | 239.2371 | 215.4555 | 210.2078 | 236.8837
1738.1794 | 1665.1794 | 306.0067 | 239.8731 | 240.3442 | 242.9414 | 239.2434 | 215.4683 | 210.2204 | 236.8947
1739.1808 | 1666.1808 | 306.0233 | 239.889 | 240.3526 | 242.8834 | 239.2579 | 215.481 | 210.2286 | 236.9187
1740.1823 | 1667.1823 | 306.1303 | 239.9079 | 240.3561 | 242.8834 | 239.2636 | 215.4958 | 210.2448 | 236.9163
1741.1837 | 1668.1837 | 306.2089 | 239.9264 | 240.3513 | 242.8781 | 239.2562 | 215.5137 | 210.254 | 236.9264
1742.1851 | 1669.1851 | 306.1871 | 239.9334 | 240.3503 | 242.8786 | 239.2842 | 215.5306 | 210.2611 | 236.9122
1743.1866 | 1670.1866 | 306.1933 | 239.939 | 240.3493 | 242.8392 | 239.2975 | 215.5359 | 210.2622 | 236.946
1744.178 | 1671.178 | 306.3592 | 239.9654 | 240.3557 | 242.8505 | 239.3051 | 215.5448 | 210.2644 | 236.9423
1745.1794 | 1672.1794 | 306.4767 | 239.9823 | 240.3546 | 242.8358 | 239.3173 | 215.552 | 210.2545 | 236.9509
1746.1809 | 1673.1809 | 306.5912 | 239.998 | 240.3601 | 242.8594 | 239.3319 | 215.5644 | 210.2605 | 236.9425
1747.1823 | 1674.1823 | 306.6197 | 240.0161 | 240.3409 | 242.8315 | 239.3386 | 215.5707 | 210.2627 | 236.9447
1748.1838 | 1675.1838 | 306.4918 | 240.0351 | 240.3658 | 242.8486 | 239.3513 | 215.5794 | 210.2712 | 236.9451
1749.1852 | 1676.1852 | 306.4445 | 240.0575 | 240.3644 | 242.8174 | 239.3614 | 215.5928 | 210.2689 | 236.9343
1750.1866 | 1677.1866 | 306.5003 | 240.0729 | 240.3709 | 242.7728 | 239.3665 | 215.5977 | 210.2742 | 236.933
1751.1781 | 1678.1781 | 306.4947 | 240.0867 | 240.3809 | 242.7907 | 239.3609 | 215.6186 | 210.2786 | 236.9324
1752.1795 | 1679.1795 | 306.5626 | 240.1033 | 240.3833 | 242.6508 | 239.3608 | 215.6371 | 210.2723 | 236.9384
1753.181 | 1680.181 | 306.5545 | 240.1198 | 240.3947 | 242.6516 | 239.3729 | 215.6549 | 210.2671 | 236.9217
1754.1824 | 1681.1824 | 306.5758 | 240.1425 | 240.4002 | 242.6661 | 239.3857 | 215.6684 | 210.2791 | 236.9324
1755.1838 | 1682.1838 | 306.6177 | 240.1696 | 240.4162 | 242.6176 | 239.381 | 215.6897 | 210.2796 | 236.9402
1756.1853 | 1683.1853 | 306.6634 | 240.1976 | 240.4299 | 242.59 | 239.389 | 215.7109 | 210.2834 | 236.9277
1757.1767 | 1684.1767 | 306.7066 | 240.2216 | 240.4496 | 242.5961 | 239.4099 | 215.7353 | 210.285 | 236.9262
1758.1781 | 1685.1781 | 306.6649 | 240.2468 | 240.4654 | 242.6107 | 239.4144 | 215.7496 | 210.2886 | 236.9307
1759.1796 | 1686.1796 | 306.6865 | 240.2791 | 240.4706 | 242.6104 | 239.4203 | 215.7688 | 210.3026 | 236.9048
1760.181 | 1687.181 | 306.7414 | 240.3172 | 240.4908 | 242.5551 | 239.4207 | 215.7671 | 210.3102 | 236.9182
1761.1825 | 1688.1825 | 306.7305 | 240.3457 | 240.5111 | 242.5258 | 239.4389 | 215.7734 | 210.3355 | 236.9192
1762.1839 | 1689.1839 | 306.675 | 240.3718 | 240.5211 | 242.5117 | 239.4421 | 215.7732 | 210.3537 | 236.9181
1763.1853 | 1690.1853 | 306.584 | 240.3929 | 240.5399 | 242.5317 | 239.4423 | 215.7687 | 210.3672 | 236.9204
1764.1868 | 1691.1868 | 306.5049 | 240.423 | 240.5496 | 242.5787 | 239.45 | 215.7591 | 210.38 | 236.9176
1765.1782 | 1692.1782 | 306.4475 | 240.4407 | 240.5597 | 242.611 | 239.4539 | 215.7532 | 210.3946 | 236.9252
1766.1796 | 1693.1796 | 306.4223 | 240.4497 | 240.5546 | 242.6495 | 239.4648 | 215.7547 | 210.3949 | 236.9003
1767.1811 | 1694.1811 | 306.4475 | 240.4514 | 240.5716 | 242.6476 | 239.4643 | 215.7614 | 210.4118 | 236.9222
1768.1825 | 1695.1825 | 306.4404 | 240.4517 | 240.6275 | 242.694 | 239.4787 | 215.7643 | 210.4226 | 236.9109
1769.184 | 1696.184 | 306.5233 | 240.4561 | 240.6515 | 242.67 | 239.4869 | 215.7569 | 210.4316 | 236.9184
1770.1854 | 1697.1854 | 306.6246 | 240.4578 | 240.6501 | 242.7112 | 239.4879 | 215.7595 | 210.4388 | 236.9319
1771.1868 | 1698.1868 | 306.7346 | 240.4686 | 240.6465 | 242.7227 | 239.4897 | 215.7531 | 210.443 | 236.9208
1772.1783 | 1699.1783 | 306.8141 | 240.4696 | 240.6673 | 242.7084 | 239.5077 | 215.7565 | 210.4512 | 236.9282
1773.1797 | 1700.1797 | 306.7906 | 240.4642 | 240.6593 | 242.71 | 239.5028 | 215.7536 | 210.4497 | 236.9222
1774.1811 | 1701.1811 | 306.8368 | 240.4642 | 240.6656 | 242.6999 | 239.5087 | 215.7529 | 210.4564 | 236.9404
1775.1826 | 1702.1826 | 306.8414 | 240.4568 | 240.6527 | 242.689 | 239.518 | 215.7541 | 210.4744 | 236.9463
1776.184 | 1703.184 | 306.7943 | 240.464 | 240.6525 | 242.6943 | 239.5271 | 215.7592 | 210.4921 | 236.949
1777.1855 | 1704.1855 | 306.8899 | 240.464 | 240.664 | 242.6571 | 239.5318 | 215.7622 | 210.5173 | 236.9402
1778.1769 | 1705.1769 | 306.8801 | 240.4621 | 240.6674 | 242.6854 | 239.5466 | 215.7667 | 210.5507 | 236.9579
1779.1783 | 1706.1783 | 306.8072 | 240.4601 | 240.6644 | 242.7391 | 239.5548 | 215.7752 | 210.5727 | 236.9675
1780.1798 | 1707.1798 | 306.7873 | 240.459 | 240.652 | 242.7705 | 239.5636 | 215.7758 | 210.5982 | 236.952
1781.1812 | 1708.1812 | 306.8552 | 240.4532 | 240.6632 | 242.7365 | 239.5519 | 215.7844 | 210.6302 | 236.9502
1782.1827 | 1709.1827 | 306.8126 | 240.4454 | 240.6638 | 242.803 | 239.5589 | 215.7874 | 210.6511 | 236.9501
1783.1841 | 1710.1841 | 306.8589 | 240.4161 | 240.67 | 242.7975 | 239.6242 | 215.8488 | 210.6674 | 236.8679
1784.1755 | 1711.1755 | 306.8503 | 240.4298 | 240.6485 | 242.8225 | 239.5767 | 215.7983 | 210.6869 | 236.943
1785.177 | 1712.177 | 306.8529 | 240.4362 | 240.6631 | 242.8353 | 239.586 | 215.815 | 210.7003 | 236.9497
1786.1784 | 1713.1784 | 306.8922 | 240.4409 | 240.6671 | 242.8849 | 239.5786 | 215.819 | 210.7105 | 236.9425
1787.1798 | 1714.1798 | 306.9228 | 240.4523 | 240.6613 | 242.8965 | 239.5858 | 215.8283 | 210.707 | 236.9516
1788.1813 | 1715.1813 | 306.9281 | 240.4655 | 240.6809 | 242.9365 | 239.5898 | 215.8386 | 210.7147 | 236.9526
1789.1827 | 1716.1827 | 306.8694 | 240.4889 | 240.6866 | 242.9437 | 239.5928 | 215.8506 | 210.7269 | 236.9333
1790.1842 | 1717.1842 | 306.8504 | 240.5006 | 240.6976 | 242.9947 | 239.5943 | 215.8659 | 210.7302 | 236.9479
1791.1856 | 1718.1856 | 306.8271 | 240.503 | 240.7139 | 243.0077 | 239.6057 | 215.8833 | 210.7276 | 236.9298
1792.187 | 1719.187 | 306.8319 | 240.5093 | 240.7348 | 243.0008 | 239.6031 | 215.8961 | 210.7319 | 236.9392
1793.1785 | 1720.1785 | 306.8268 | 240.5326 | 240.7574 | 243.0222 | 239.5955 | 215.9132 | 210.737 | 236.9448
1794.1799 | 1721.1799 | 306.7281 | 240.5338 | 240.7805 | 243.0556 | 239.6063 | 215.9267 | 210.7428 | 236.9627
1795.1813 | 1722.1813 | 306.6738 | 240.5494 | 240.7877 | 243.044 | 239.5987 | 215.9347 | 210.7493 | 236.9664
1796.1828 | 1723.1828 | 306.6047 | 240.5667 | 240.8103 | 243.0511 | 239.607 | 215.9621 | 210.7653 | 236.9596
1797.1842 | 1724.1842 | 306.5528 | 240.5902 | 240.8348 | 243.0541 | 239.6142 | 215.9801 | 210.7857 | 236.9633
1798.1857 | 1725.1857 | 306.3721 | 240.5994 | 240.8593 | 243.0985 | 239.6086 | 215.9986 | 210.7909 | 236.969
1799.1771 | 1726.1771 | 306.2102 | 240.6124 | 240.8904 | 243.1242 | 239.6211 | 216.0212 | 210.8079 | 236.9605
1800.1785 | 1727.1785 | 306.0524 | 240.6071 | 240.9014 | 243.1148 | 239.626 | 216.0333 | 210.8264 | 236.9527
1801.18 | 1728.18 | 305.959 | 240.6067 | 240.9257 | 243.156 | 239.6324 | 216.05 | 210.8412 | 236.9471
1802.1814 | 1729.1814 | 305.794 | 240.6066 | 240.9383 | 243.1797 | 239.6184 | 216.0617 | 210.8501 | 236.9427
1803.1828 | 1730.1828 | 305.7511 | 240.6103 | 240.9428 | 243.174 | 239.6231 | 216.0719 | 210.8553 | 236.9387
1804.1843 | 1731.1843 | 305.6298 | 240.6125 | 240.9457 | 243.1543 | 239.6257 | 216.0901 | 210.8644 | 236.9409
1805.1857 | 1732.1857 | 305.414 | 240.6093 | 240.9604 | 243.1555 | 239.6301 | 216.102 | 210.8712 | 236.9235
1806.1872 | 1733.1872 | 305.2482 | 240.5999 | 240.9761 | 243.1572 | 239.6173 | 216.1246 | 210.8843 | 236.9306
1807.1786 | 1734.1786 | 305.1153 | 240.5911 | 240.9687 | 243.1394 | 239.6278 | 216.1368 | 210.8849 | 236.9265
1808.18 | 1735.18 | 305.0873 | 240.5922 | 240.9887 | 243.0509 | 239.6389 | 216.1568 | 210.9032 | 236.9003
1809.1815 | 1736.1815 | 305.0526 | 240.5989 | 241.0017 | 243.0611 | 239.6415 | 216.1756 | 210.9094 | 236.926
1810.1829 | 1737.1829 | 304.9954 | 240.6136 | 241.0072 | 243.0869 | 239.6461 | 216.1859 | 210.9181 | 236.9195
1811.1844 | 1738.1844 | 304.8872 | 240.6136 | 241.0094 | 242.9907 | 239.6393 | 216.1971 | 210.9227 | 236.9116
1812.1858 | 1739.1858 | 304.6512 | 240.622 | 241.0142 | 243.0007 | 239.6418 | 216.2096 | 210.9192 | 236.8947
1813.1872 | 1740.1872 | 304.5813 | 240.6283 | 241.0099 | 242.9961 | 239.6394 | 216.2247 | 210.9184 | 236.9036
1814.1787 | 1741.1787 | 304.5812 | 240.6368 | 241.022 | 243.0004 | 239.6411 | 216.2319 | 210.9135 | 236.906
1815.1801 | 1742.1801 | 304.6582 | 240.6505 | 241.0326 | 242.9343 | 239.6399 | 216.2524 | 210.9156 | 236.9143
1816.1815 | 1743.1815 | 304.6437 | 240.6743 | 241.0348 | 242.8906 | 239.6411 | 216.2628 | 210.9109 | 236.8959
1817.183 | 1744.183 | 304.7092 | 240.69 | 241.0497 | 242.882 | 239.6295 | 216.2791 | 210.9132 | 236.8859
1818.1844 | 1745.1844 | 304.7236 | 240.7154 | 241.0728 | 242.901 | 239.6325 | 216.2839 | 210.9179 | 236.8854
1819.1859 | 1746.1859 | 304.7256 | 240.7378 | 241.0693 | 242.9049 | 239.6267 | 216.2975 | 210.9104 | 236.8735
1820.1873 | 1747.1873 | 304.7135 | 240.7655 | 241.0789 | 242.8975 | 239.6219 | 216.3097 | 210.9005 | 236.8724
1821.1787 | 1748.1787 | 304.8421 | 240.7788 | 241.111 | 242.9002 | 239.6088 | 216.3239 | 210.8916 | 236.8725
1822.1802 | 1749.1802 | 305.0247 | 240.7985 | 241.1279 | 242.8909 | 239.6007 | 216.3347 | 210.8896 | 236.8498
1823.1816 | 1750.1816 | 305.1992 | 240.8199 | 241.1435 | 242.9126 | 239.6095 | 216.3416 | 210.8885 | 236.855
1824.183 | 1751.183 | 305.2712 | 240.8349 | 241.1304 | 242.9179 | 239.5926 | 216.351 | 210.8957 | 236.8611
1825.1845 | 1752.1845 | 305.3597 | 240.8568 | 241.1323 | 242.9207 | 239.5968 | 216.3659 | 210.8988 | 236.8688
1826.1859 | 1753.1859 | 305.3684 | 240.8551 | 241.1252 | 242.8894 | 239.586 | 216.3683 | 210.9018 | 236.8671
1827.1774 | 1754.1774 | 305.4197 | 240.852 | 241.1247 | 242.8506 | 239.5834 | 216.3776 | 210.8997 | 236.8681
1828.1788 | 1755.1788 | 305.4315 | 240.8525 | 241.1287 | 242.8293 | 239.5928 | 216.3818 | 210.9101 | 236.8555
1829.1802 | 1756.1802 | 305.4609 | 240.857 | 241.1311 | 242.8447 | 239.5891 | 216.3954 | 210.9216 | 236.8554
1830.1817 | 1757.1817 | 305.6161 | 240.867 | 241.1366 | 242.8274 | 239.5899 | 216.4145 | 210.9253 | 236.8463
1831.1831 | 1758.1831 | 305.7113 | 240.8849 | 241.1369 | 242.8592 | 239.6003 | 216.4319 | 210.9234 | 236.8492
1832.1846 | 1759.1846 | 305.7507 | 240.911 | 241.1526 | 242.8594 | 239.5981 | 216.4425 | 210.925 | 236.855
1833.186 | 1760.186 | 305.7586 | 240.9394 | 241.1713 | 242.8903 | 239.6088 | 216.4593 | 210.928 | 236.8527
1834.1874 | 1761.1874 | 305.8255 | 240.9656 | 241.1742 | 242.9 | 239.6051 | 216.4667 | 210.9254 | 236.8511
1835.1789 | 1762.1789 | 305.8935 | 240.9858 | 241.1834 | 242.9419 | 239.6141 | 216.4805 | 210.9259 | 236.8681
1836.1803 | 1763.1803 | 305.9833 | 241.0053 | 241.1699 | 242.9889 | 239.6154 | 216.499 | 210.9261 | 236.861
1837.1817 | 1764.1817 | 306.1511 | 241.0399 | 241.1874 | 243.0402 | 239.615 | 216.5178 | 210.9321 | 236.8624
1838.1832 | 1765.1832 | 306.2752 | 241.0666 | 241.1794 | 243.0883 | 239.6299 | 216.533 | 210.9372 | 236.8731
1839.1846 | 1766.1846 | 306.3198 | 241.1056 | 241.1801 | 243.0901 | 239.6355 | 216.551 | 210.9535 | 236.8669
1840.1861 | 1767.1861 | 306.4962 | 241.1285 | 241.1763 | 243.1518 | 239.6425 | 216.5643 | 210.9628 | 236.8782
1841.1775 | 1768.1775 | 306.6546 | 241.1656 | 241.1697 | 243.1332 | 239.6416 | 216.579 | 210.9699 | 236.877
1842.1789 | 1769.1789 | 306.6592 | 241.1903 | 241.1772 | 243.1294 | 239.6524 | 216.5852 | 210.9744 | 236.8754
1843.1804 | 1770.1804 | 306.6365 | 241.2141 | 241.1913 | 243.1948 | 239.6576 | 216.602 | 210.9677 | 236.8872
1844.1818 | 1771.1818 | 306.6034 | 241.237 | 241.1951 | 243.2103 | 239.6559 | 216.6116 | 210.9785 | 236.9018
1845.1832 | 1772.1832 | 306.6066 | 241.2541 | 241.204 | 243.1971 | 239.6686 | 216.6422 | 210.9765 | 236.8905
1846.1847 | 1773.1847 | 306.7903 | 241.2711 | 241.2094 | 243.2437 | 239.6648 | 216.6557 | 210.9782 | 236.8982
1847.1861 | 1774.1861 | 306.8963 | 241.2767 | 241.2191 | 243.2616 | 239.6833 | 216.6759 | 210.9904 | 236.9195
1848.1876 | 1775.1876 | 306.8592 | 241.2964 | 241.2268 | 243.2538 | 239.6962 | 216.6961 | 211.0015 | 236.9314
1849.179 | 1776.179 | 306.8646 | 241.3152 | 241.2319 | 243.3052 | 239.709 | 216.7097 | 211.0061 | 236.9301
1850.1804 | 1777.1804 | 306.8329 | 241.3339 | 241.2292 | 243.331 | 239.7263 | 216.7191 | 211.0165 | 236.9404
1851.1819 | 1778.1819 | 306.7867 | 241.342 | 241.2413 | 243.3402 | 239.725 | 216.736 | 211.0196 | 236.9449
1852.1833 | 1779.1833 | 306.7255 | 241.3503 | 241.2287 | 243.2693 | 239.7468 | 216.7575 | 211.0181 | 236.9554
1853.1847 | 1780.1847 | 306.7245 | 241.351 | 241.24 | 243.3293 | 239.7588 | 216.7642 | 211.0245 | 236.9602
1854.1862 | 1781.1862 | 306.7542 | 241.3371 | 241.2614 | 243.3737 | 239.7629 | 216.791 | 211.0337 | 236.9634
1855.1876 | 1782.1876 | 306.8127 | 241.3192 | 241.2574 | 243.3687 | 239.7684 | 216.8074 | 211.0321 | 236.9764
1856.1791 | 1783.1791 | 306.8625 | 241.3028 | 241.2675 | 243.4034 | 239.7797 | 216.8276 | 211.0459 | 236.9774
1857.1805 | 1784.1805 | 306.93 | 241.2974 | 241.2685 | 243.4121 | 239.7925 | 216.8438 | 211.0626 | 236.9953
1858.1819 | 1785.1819 | 307.019 | 241.2803 | 241.2582 | 243.4484 | 239.797 | 216.8598 | 211.0774 | 236.9973
1859.1834 | 1786.1834 | 307.1303 | 241.2813 | 241.2567 | 243.4443 | 239.8016 | 216.8805 | 211.0904 | 237.012
1860.1848 | 1787.1848 | 307.0796 | 241.2853 | 241.2616 | 243.381 | 239.8115 | 216.9017 | 211.104 | 237.0146
1861.1762 | 1788.1762 | 307.0387 | 241.2846 | 241.2552 | 243.4259 | 239.8131 | 216.9119 | 211.1208 | 237.0282
1862.1877 | 1789.1877 | 307.0354 | 241.2841 | 241.255 | 243.4393 | 239.8206 | 216.9252 | 211.1381 | 237.0341
1863.1791 | 1790.1791 | 306.9284 | 241.2752 | 241.2414 | 243.4542 | 239.8316 | 216.9421 | 211.1511 | 237.0406
1864.1806 | 1791.1806 | 306.8544 | 241.275 | 241.2332 | 243.4717 | 239.846 | 216.9597 | 211.1633 | 237.0578
1865.182 | 1792.182 | 306.7574 | 241.2749 | 241.2383 | 243.5061 | 239.8525 | 216.981 | 211.175 | 237.0634
1866.1834 | 1793.1834 | 306.5728 | 241.2835 | 241.2386 | 243.4001 | 239.8563 | 216.9932 | 211.1778 | 237.067
1867.1849 | 1794.1849 | 306.3689 | 241.2808 | 241.2406 | 243.4174 | 239.8682 | 217.0149 | 211.1852 | 237.0763
1868.1763 | 1795.1763 | 306.2554 | 241.2885 | 241.2361 | 243.4141 | 239.8785 | 217.0289 | 211.1933 | 237.0718
1869.1777 | 1796.1777 | 306.1528 | 241.2928 | 241.2277 | 243.4327 | 239.8871 | 217.0468 | 211.1945 | 237.0737
1870.1792 | 1797.1792 | 305.9918 | 241.3101 | 241.2266 | 243.4679 | 239.8898 | 217.0654 | 211.1959 | 237.0642
1871.1806 | 1798.1806 | 305.8427 | 241.3157 | 241.2197 | 243.4363 | 239.8982 | 217.0811 | 211.201 | 237.0773
1872.1821 | 1799.1821 | 305.723 | 241.3222 | 241.2031 | 243.4772 | 239.9057 | 217.1028 | 211.2031 | 237.069
1873.1835 | 1800.1835 | 305.6668 | 241.3171 | 241.2048 | 243.5351 | 239.9078 | 217.1143 | 211.2007 | 237.073
1874.1849 | 1801.1849 | 305.5734 | 241.3022 | 241.194 | 243.5833 | 239.9233 | 217.1259 | 211.2048 | 237.0648
1875.1864 | 1802.1864 | 305.4563 | 241.2828 | 241.1871 | 243.6105 | 239.9296 | 217.1438 | 211.2147 | 237.0864
1876.1878 | 1803.1878 | 305.3849 | 241.266 | 241.1717 | 243.6048 | 239.9246 | 217.1687 | 211.2198 | 237.0922
1877.1793 | 1804.1793 | 305.3052 | 241.2513 | 241.1769 | 243.5705 | 239.9416 | 217.1756 | 211.2287 | 237.1007
1878.1807 | 1805.1807 | 305.2013 | 241.262 | 241.1671 | 243.5915 | 239.9511 | 217.1845 | 211.2371 | 237.1143
1879.1821 | 1806.1821 | 305.2106 | 241.2796 | 241.1635 | 243.5936 | 239.949 | 217.1994 | 211.2478 | 237.11
1880.1836 | 1807.1836 | 305.2497 | 241.2883 | 241.1563 | 243.6171 | 239.9556 | 217.2069 | 211.2547 | 237.1228
1881.185 | 1808.185 | 305.2577 | 241.301 | 241.1637 | 243.63 | 239.9593 | 217.2158 | 211.2603 | 237.118
1882.1865 | 1809.1865 | 305.3106 | 241.3121 | 241.154 | 243.6012 | 239.9632 | 217.2235 | 211.2754 | 237.1379
1883.1879 | 1810.1879 | 305.4347 | 241.3086 | 241.1476 | 243.6118 | 239.9601 | 217.2311 | 211.285 | 237.1205
1884.1793 | 1811.1793 | 305.5451 | 241.2962 | 241.1465 | 243.6293 | 239.9696 | 217.2312 | 211.2822 | 237.1118
1885.1808 | 1812.1808 | 305.6325 | 241.2921 | 241.1417 | 243.6473 | 239.9719 | 217.2294 | 211.2961 | 237.1393
1886.1822 | 1813.1822 | 305.7397 | 241.2743 | 241.1418 | 243.68 | 239.9809 | 217.2219 | 211.3131 | 237.1368
1887.1836 | 1814.1836 | 305.7593 | 241.2563 | 241.1301 | 243.6315 | 239.9671 | 217.222 | 211.3189 | 237.1468
1888.1851 | 1815.1851 | 305.7971 | 241.2326 | 241.1274 | 243.6441 | 239.9861 | 217.2148 | 211.3286 | 237.1441
1889.1765 | 1816.1765 | 305.9178 | 241.196 | 241.127 | 243.6481 | 239.993 | 217.2015 | 211.3424 | 237.1526
1890.1779 | 1817.1779 | 305.9312 | 241.1763 | 241.1078 | 243.6176 | 239.9959 | 217.1936 | 211.3542 | 237.1586
1891.1794 | 1818.1794 | 305.8891 | 241.1612 | 241.1078 | 243.6293 | 240.0034 | 217.193 | 211.3615 | 237.1531
1892.1808 | 1819.1808 | 305.8261 | 241.1428 | 241.0958 | 243.6221 | 239.9973 | 217.1886 | 211.3706 | 237.1501
1893.1823 | 1820.1823 | 305.6845 | 241.1356 | 241.0779 | 243.6348 | 240.0084 | 217.1779 | 211.3758 | 237.1711
1894.1837 | 1821.1837 | 305.6649 | 241.1391 | 241.0793 | 243.6216 | 240.0105 | 217.171 | 211.3856 | 237.1758
1895.1851 | 1822.1851 | 305.6931 | 241.1201 | 241.0712 | 243.6848 | 240.0142 | 217.1574 | 211.4033 | 237.1602
1896.1866 | 1823.1866 | 305.7294 | 241.1183 | 241.0695 | 243.7196 | 239.993 | 217.1417 | 211.4216 | 237.1934
1897.178 | 1824.178 | 305.7185 | 241.1161 | 241.0697 | 243.6711 | 239.996 | 217.1312 | 211.4428 | 237.1759
1898.1794 | 1825.1794 | 305.7156 | 241.1028 | 241.0675 | 243.5948 | 240.0074 | 217.1202 | 211.4629 | 237.1864
1899.1809 | 1826.1809 | 305.7983 | 241.0562 | 241.096 | 243.5701 | 240.1346 | 217.2467 | 211.4595 | 237.0013
1900.1823 | 1827.1823 | 305.9612 | 241.0916 | 241.0768 | 243.5229 | 240.0273 | 217.1378 | 211.4889 | 237.1733
1901.1838 | 1828.1838 | 306.066 | 241.1196 | 241.0638 | 243.4739 | 240.011 | 217.1133 | 211.4991 | 237.1638
1902.1852 | 1829.1852 | 305.9912 | 241.1406 | 241.0479 | 243.3719 | 239.9883 | 217.0833 | 211.5009 | 237.2031
1903.1866 | 1830.1866 | 306.0393 | 241.1611 | 241.0469 | 243.3378 | 239.985 | 217.0816 | 211.5049 | 237.208
1904.1781 | 1831.1781 | 306.1428 | 241.1699 | 241.0638 | 243.3137 | 239.986 | 217.0717 | 211.5157 | 237.1952
1905.1795 | 1832.1795 | 306.2086 | 241.1834 | 241.0553 | 243.3412 | 239.9754 | 217.0732 | 211.519 | 237.2011
1906.181 | 1833.181 | 306.3268 | 241.1958 | 241.0637 | 243.3165 | 239.9662 | 217.0715 | 211.5328 | 237.1878
1907.1824 | 1834.1824 | 306.3445 | 241.2036 | 241.0541 | 243.2843 | 239.9547 | 217.0744 | 211.5305 | 237.1919
1908.1838 | 1835.1838 | 306.3162 | 241.2145 | 241.0699 | 243.1843 | 239.9618 | 217.0784 | 211.5407 | 237.1742
1909.1853 | 1836.1853 | 306.3274 | 241.2237 | 241.0744 | 243.1481 | 239.9366 | 217.092 | 211.5522 | 237.1568
1910.1767 | 1837.1767 | 306.4124 | 241.2339 | 241.0853 | 243.1453 | 239.947 | 217.1006 | 211.5601 | 237.166
1911.1781 | 1838.1781 | 306.4428 | 241.2512 | 241.0869 | 243.1066 | 239.9385 | 217.1014 | 211.564 | 237.1516
1912.1796 | 1839.1796 | 306.4618 | 241.2764 | 241.0963 | 243.0255 | 239.923 | 217.1162 | 211.5833 | 237.1549
1913.181 | 1840.181 | 306.4617 | 241.3065 | 241.1057 | 242.9989 | 239.9222 | 217.1226 | 211.5892 | 237.1473
1914.1825 | 1841.1825 | 306.4317 | 241.3358 | 241.1193 | 243.0388 | 239.9219 | 217.1379 | 211.6025 | 237.1352
1915.1839 | 1842.1839 | 306.3771 | 241.3766 | 241.1266 | 242.988 | 239.9104 | 217.1404 | 211.6137 | 237.1185
1916.1853 | 1843.1853 | 306.3381 | 241.4187 | 241.1395 | 242.9851 | 239.9021 | 217.1593 | 211.6258 | 237.1126
1917.1868 | 1844.1868 | 306.3169 | 241.4535 | 241.1649 | 243.0319 | 239.8785 | 217.1707 | 211.6312 | 237.1104
1918.1782 | 1845.1782 | 306.3019 | 241.487 | 241.1693 | 243.0629 | 239.8862 | 217.1813 | 211.6449 | 237.1115
1919.1796 | 1846.1796 | 306.3496 | 241.5139 | 241.1964 | 243.1276 | 239.8772 | 217.1934 | 211.6563 | 237.1035
1920.1811 | 1847.1811 | 306.4037 | 241.5425 | 241.197 | 243.0901 | 239.871 | 217.2092 | 211.6641 | 237.1128
1921.1825 | 1848.1825 | 306.3843 | 241.5625 | 241.2087 | 243.1439 | 239.87 | 217.2212 | 211.6638 | 237.1014
1922.3142 | 1849.3142 | 306.5314 | 241.5814 | 241.2055 | 243.1537 | 239.861 | 217.2404 | 211.6701 | 237.107
1923.1854 | 1850.1854 | 306.6824 | 241.5931 | 241.2092 | 243.1952 | 239.8634 | 217.2472 | 211.6722 | 237.0892
1924.1868 | 1851.1868 | 306.8562 | 241.601 | 241.2164 | 243.2276 | 239.8641 | 217.2578 | 211.6735 | 237.1014
1925.1783 | 1852.1783 | 306.9585 | 241.6087 | 241.2288 | 243.2863 | 239.8691 | 217.2607 | 211.68 | 237.1175
1926.1797 | 1853.1797 | 307.0862 | 241.6148 | 241.2244 | 243.325 | 239.8715 | 217.2741 | 211.6884 | 237.1131
1927.1812 | 1854.1812 | 307.1955 | 241.6131 | 241.2299 | 243.3853 | 239.8778 | 217.2721 | 211.7085 | 237.1189
1928.1826 | 1855.1826 | 307.2878 | 241.613 | 241.236 | 243.4568 | 239.8742 | 217.2796 | 211.7265 | 237.1287
1929.184 | 1856.184 | 307.3467 | 241.611 | 241.2474 | 243.4703 | 239.8833 | 217.2959 | 211.7612 | 237.1428
1930.1855 | 1857.1855 | 307.2571 | 241.6176 | 241.231 | 243.4468 | 239.8847 | 217.3123 | 211.78 | 237.1379
1931.1769 | 1858.1769 | 307.2724 | 241.6218 | 241.24 | 243.4241 | 239.887 | 217.3305 | 211.801 | 237.1382
1932.1783 | 1859.1783 | 307.2228 | 241.6286 | 241.2438 | 243.4251 | 239.8851 | 217.3412 | 211.8079 | 237.1479
1933.1798 | 1860.1798 | 307.1766 | 241.6535 | 241.2414 | 243.3923 | 239.8912 | 217.3594 | 211.816 | 237.1295
1934.1812 | 1861.1812 | 307.1701 | 241.6819 | 241.2524 | 243.4026 | 239.8862 | 217.3708 | 211.8198 | 237.1426
1935.1827 | 1862.1827 | 307.214 | 241.7193 | 241.2484 | 243.4404 | 239.8932 | 217.3916 | 211.8268 | 237.1352
1936.1841 | 1863.1841 | 307.2092 | 241.764 | 241.2569 | 243.464 | 239.8993 | 217.4095 | 211.8368 | 237.1376
1937.1855 | 1864.1855 | 307.2164 | 241.7708 | 241.2406 | 243.4256 | 239.8955 | 217.4396 | 211.8511 | 237.1505
1938.187 | 1865.187 | 307.2862 | 241.7668 | 241.2194 | 243.4258 | 239.8854 | 217.4567 | 211.861 | 237.1515
1939.1784 | 1866.1784 | 307.2555 | 241.7541 | 241.2243 | 243.3927 | 239.896 | 217.479 | 211.8718 | 237.1579
1940.1798 | 1867.1798 | 307.1363 | 241.7276 | 241.2181 | 243.4391 | 239.8921 | 217.5017 | 211.894 | 237.1613
1941.1813 | 1868.1813 | 307.0498 | 241.7144 | 241.2135 | 243.4083 | 239.9022 | 217.5323 | 211.9037 | 237.1732
1942.1827 | 1869.1827 | 307.0052 | 241.7042 | 241.1918 | 243.4529 | 239.9045 | 217.5507 | 211.9096 | 237.1619
1943.1842 | 1870.1842 | 306.9338 | 241.6886 | 241.1993 | 243.4926 | 239.9047 | 217.5749 | 211.9271 | 237.1687
1944.1856 | 1871.1856 | 306.8749 | 241.6754 | 241.2118 | 243.5187 | 239.9074 | 217.5988 | 211.9407 | 237.1559
1945.187 | 1872.187 | 306.8988 | 241.672 | 241.2117 | 243.5539 | 239.9083 | 217.6104 | 211.9522 | 237.1589
1946.1785 | 1873.1785 | 306.9074 | 241.6778 | 241.2149 | 243.5761 | 239.9077 | 217.6243 | 211.96 | 237.1727
1947.1799 | 1874.1799 | 306.8571 | 241.6996 | 241.2235 | 243.5847 | 239.9109 | 217.6403 | 211.9596 | 237.1839
1948.1813 | 1875.1813 | 306.8165 | 241.7257 | 241.2272 | 243.5398 | 239.9229 | 217.6615 | 211.9575 | 237.1829
1949.1828 | 1876.1828 | 306.7374 | 241.752 | 241.2371 | 243.5924 | 239.9276 | 217.6716 | 211.9515 | 237.1862
1950.1842 | 1877.1842 | 306.6012 | 241.7771 | 241.2445 | 243.5742 | 239.927 | 217.6905 | 211.945 | 237.1816
1951.1857 | 1878.1857 | 306.6401 | 241.793 | 241.2428 | 243.5287 | 239.9403 | 217.7047 | 211.937 | 237.1766
1952.1771 | 1879.1771 | 306.6399 | 241.79 | 241.2565 | 243.5667 | 239.9444 | 217.7199 | 211.9337 | 237.1872
1953.1785 | 1880.1785 | 306.6764 | 241.8026 | 241.2507 | 243.528 | 239.9379 | 217.7303 | 211.9315 | 237.1947
1954.18 | 1881.18 | 306.7238 | 241.7954 | 241.2489 | 243.5328 | 239.955 | 217.7539 | 211.9335 | 237.1752
1955.1814 | 1882.1814 | 306.6992 | 241.7973 | 241.2722 | 243.5346 | 239.9618 | 217.7752 | 211.9332 | 237.1697
1956.1829 | 1883.1829 | 306.652 | 241.8026 | 241.2698 | 243.5908 | 239.9662 | 217.792 | 212.0511 | 237.1878
1957.1843 | 1884.1843 | 306.6339 | 241.8005 | 241.2651 | 243.5809 | 239.9738 | 217.8068 | 211.9318 | 237.1718
1958.1857 | 1885.1857 | 306.5109 | 241.8064 | 241.2663 | 243.5889 | 239.9843 | 217.8227 | 211.9343 | 237.1902
1959.1772 | 1886.1772 | 306.3553 | 241.8081 | 241.2727 | 243.6212 | 239.9915 | 217.8453 | 211.9365 | 237.1761
1960.1786 | 1887.1786 | 306.2364 | 241.8126 | 241.2605 | 243.5702 | 239.9977 | 217.8608 | 211.9354 | 237.1943
1961.18 | 1888.18 | 306.2372 | 241.7884 | 241.2457 | 243.5545 | 239.9998 | 217.8812 | 211.944 | 237.1809
1962.1815 | 1889.1815 | 306.3157 | 241.7843 | 241.2524 | 243.5398 | 240.0065 | 217.8906 | 211.9499 | 237.1919
1963.1829 | 1890.1829 | 306.3274 | 241.7825 | 241.2477 | 243.5542 | 240.011 | 217.9135 | 211.9577 | 237.1721
1964.1844 | 1891.1844 | 306.2677 | 241.7847 | 241.2497 | 243.5547 | 240.0175 | 217.9249 | 211.9595 | 237.156
1965.1858 | 1892.1858 | 306.2493 | 241.7838 | 241.2514 | 243.5809 | 240.0199 | 217.9457 | 211.9551 | 237.1626
1966.1872 | 1893.1872 | 306.2298 | 241.8002 | 241.2549 | 243.5566 | 240.0081 | 217.9686 | 211.9516 | 237.1512
1967.1887 | 1894.1887 | 306.1616 | 241.8073 | 241.2516 | 243.4957 | 240.009 | 217.9788 | 211.9602 | 237.1557
1968.1801 | 1895.1801 | 306.075 | 241.8056 | 241.2499 | 243.5036 | 240.0026 | 218.0004 | 211.9685 | 237.1545
1969.1815 | 1896.1815 | 306.0119 | 241.808 | 241.2556 | 243.5343 | 239.9996 | 218.0107 | 211.976 | 237.1548
1970.183 | 1897.183 | 306.0816 | 241.8138 | 241.2619 | 243.541 | 240.0038 | 218.0298 | 211.988 | 237.1429
1971.1844 | 1898.1844 | 306.0449 | 241.8275 | 241.2671 | 243.5691 | 240.0132 | 218.0448 | 212.0004 | 237.1437
1972.1859 | 1899.1859 | 305.9911 | 241.8293 | 241.2826 | 243.5725 | 240.0049 | 218.0543 | 212.007 | 237.1259
1973.1873 | 1900.1873 | 305.911 | 241.8464 | 241.2999 | 243.5934 | 239.9978 | 218.0641 | 212.0145 | 237.1188
1974.1787 | 1901.1787 | 305.8542 | 241.8551 | 241.3039 | 243.623 | 239.9942 | 218.0736 | 212.0111 | 237.1334
1975.1802 | 1902.1802 | 305.8591 | 241.8654 | 241.3213 | 243.6702 | 239.9833 | 218.0819 | 212.0109 | 237.1237
1976.1816 | 1903.1816 | 305.8327 | 241.8792 | 241.3021 | 243.561 | 239.9957 | 218.087 | 212.0029 | 237.1123
1977.183 | 1904.183 | 305.884 | 241.8956 | 241.3367 | 243.5028 | 239.9896 | 218.0941 | 211.9965 | 237.1153
1978.1845 | 1905.1845 | 305.9784 | 241.9125 | 241.3461 | 243.5126 | 239.9923 | 218.1014 | 211.9897 | 237.1055
1979.1859 | 1906.1859 | 306.0607 | 241.9293 | 241.3529 | 243.5266 | 239.9957 | 218.1121 | 211.9793 | 237.0785
1980.1874 | 1907.1874 | 306.1533 | 241.9387 | 241.3871 | 243.5605 | 239.9983 | 218.1136 | 211.9789 | 237.0742
1981.1788 | 1908.1788 | 306.2609 | 241.9367 | 241.3969 | 243.5731 | 239.9998 | 218.1263 | 211.9735 | 237.0788
1982.1802 | 1909.1802 | 306.4164 | 241.9321 | 241.42 | 243.6098 | 239.985 | 218.1268 | 211.9757 | 237.0761
1983.1817 | 1910.1817 | 306.3602 | 241.9426 | 241.4457 | 243.6268 | 239.985 | 218.1287 | 211.9695 | 237.0855
1984.1831 | 1911.1831 | 306.3748 | 241.956 | 241.4616 | 243.6431 | 239.985 | 218.1412 | 211.9806 | 237.0767
1985.1846 | 1912.1846 | 306.2964 | 241.9828 | 241.4698 | 243.6403 | 239.9892 | 218.1353 | 211.9808 | 237.0731
1986.186 | 1913.186 | 306.2108 | 242.0277 | 241.4896 | 243.6619 | 239.9877 | 218.1459 | 211.9827 | 237.0693
1987.1874 | 1914.1874 | 306.0517 | 242.0385 | 241.5065 | 243.6845 | 239.9788 | 218.1495 | 211.9789 | 237.0724
1988.1789 | 1915.1789 | 305.9625 | 242.0423 | 241.5284 | 243.6746 | 239.986 | 218.1535 | 211.9815 | 237.0717
1989.1803 | 1916.1803 | 305.829 | 242.0253 | 241.5291 | 243.6849 | 239.987 | 218.1594 | 211.9851 | 237.0641
1990.1817 | 1917.1817 | 305.7673 | 241.9953 | 241.5372 | 243.7024 | 239.9871 | 218.1554 | 211.9892 | 237.0639
1991.1832 | 1918.1832 | 305.7221 | 241.9795 | 241.5457 | 243.7335 | 239.9894 | 218.1647 | 211.9944 | 237.0642
1992.1846 | 1919.1846 | 305.6972 | 241.9637 | 241.5553 | 243.7264 | 239.9922 | 218.1716 | 211.9985 | 237.0727
1993.1861 | 1920.1861 | 305.6811 | 241.9475 | 241.565 | 243.7871 | 239.9934 | 218.174 | 211.9956 | 237.0562
1994.1875 | 1921.1875 | 305.6778 | 241.9482 | 241.5769 | 243.8118 | 239.9856 | 218.1828 | 212.0037 | 237.0559
1995.1789 | 1922.1789 | 305.7211 | 241.9528 | 241.5903 | 243.8491 | 239.9893 | 218.1903 | 212.0093 | 237.0502
1996.1804 | 1923.1804 | 305.8439 | 241.9674 | 241.606 | 243.8241 | 239.9947 | 218.19 | 212.0033 | 237.0403
1997.1818 | 1924.1818 | 305.9193 | 241.9731 | 241.6269 | 243.8699 | 239.9934 | 218.1939 | 211.9925 | 237.0446
1998.1832 | 1925.1832 | 306.0389 | 241.9841 | 241.6411 | 243.8963 | 239.9992 | 218.1962 | 211.9957 | 237.0228
1999.1847 | 1926.1847 | 306.1141 | 241.9979 | 241.6634 | 243.9125 | 240.0021 | 218.2089 | 211.9899 | 237.018
2000.1861 | 1927.1861 | 306.2372 | 242.0024 | 241.6818 | 243.9219 | 239.9991 | 218.208 | 211.9902 | 237.0289
2001.1876 | 1928.1876 | 306.4823 | 242.0244 | 241.7083 | 243.9592 | 240.0098 | 218.2105 | 211.9827 | 237.0302
2002.179 | 1929.179 | 306.6112 | 242.0574 | 241.7281 | 243.9563 | 240.005 | 218.2139 | 211.9838 | 237.0364
2003.1804 | 1930.1804 | 306.7371 | 242.1017 | 241.7696 | 243.9895 | 240.0025 | 218.2132 | 211.9829 | 237.0327
2004.1819 | 1931.1819 | 306.8016 | 242.1124 | 241.7902 | 244.0143 | 240.0011 | 218.2219 | 211.986 | 237.0342
2005.1833 | 1932.1833 | 306.8089 | 242.1158 | 241.8214 | 244.0402 | 240.01 | 218.2334 | 211.9776 | 237.0447
2006.1848 | 1933.1848 | 306.8308 | 242.1253 | 241.84 | 244.0687 | 240.0147 | 218.2325 | 211.9833 | 237.0539
2007.1862 | 1934.1862 | 306.8534 | 242.1415 | 241.877 | 244.0574 | 240.0184 | 218.2405 | 211.97 | 237.081
2008.1876 | 1935.1876 | 306.8616 | 242.1517 | 241.9098 | 244.0954 | 240.0166 | 218.2477 | 211.9662 | 237.0681
2009.1791 | 1936.1791 | 306.8627 | 242.1706 | 241.9245 | 244.1696 | 240.0236 | 218.2505 | 211.9735 | 237.0661
2010.1805 | 1937.1805 | 306.7035 | 242.1916 | 241.9661 | 244.2145 | 240.0191 | 218.2599 | 212.072 | 237.0826
2011.1819 | 1938.1819 | 306.5245 | 242.2025 | 241.986 | 244.2734 | 240.0251 | 218.2665 | 211.9741 | 237.0775
2012.1834 | 1939.1834 | 306.496 | 242.2178 | 241.9794 | 244.2755 | 240.0277 | 218.2748 | 211.9757 | 237.0912
2013.1848 | 1940.1848 | 306.4151 | 242.2333 | 242.0049 | 244.3183 | 240.0244 | 218.29 | 212.0847 | 237.0903
2014.1863 | 1941.1863 | 306.2538 | 242.2428 | 242.0099 | 244.3358 | 240.0302 | 218.3015 | 212.0953 | 237.0953
2015.1777 | 1942.1777 | 306.1611 | 242.2651 | 242.0199 | 244.3599 | 240.0414 | 218.3201 | 212.1009 | 237.0806
2016.1791 | 1943.1791 | 306.0971 | 242.2757 | 242.0289 | 244.3727 | 240.0452 | 218.3354 | 212.0988 | 237.0847
2017.1806 | 1944.1806 | 305.969 | 242.2854 | 242.04 | 244.356 | 240.0412 | 218.3477 | 212.1 | 237.0941
2018.182 | 1945.182 | 305.8401 | 242.2988 | 242.0266 | 244.3415 | 240.0434 | 218.3675 | 212.0035 | 237.0699
2019.1834 | 1946.1834 | 305.8725 | 242.3078 | 242.0408 | 244.3617 | 240.0556 | 218.3792 | 212.0603 | 237.1008
2020.1849 | 1947.1849 | 305.8043 | 242.3498 | 242.0446 | 244.4037 | 240.0605 | 218.3949 | 212.1059 | 237.0811
2021.1863 | 1948.1863 | 305.6829 | 242.3955 | 242.0509 | 244.3956 | 240.0721 | 218.4159 | 212.1102 | 237.0955
2022.1777 | 1949.1777 | 305.5891 | 242.4584 | 242.0552 | 244.449 | 240.075 | 218.4352 | 212.1006 | 237.0895
2023.1792 | 1950.1792 | 305.5582 | 242.5035 | 242.068 | 244.4919 | 240.0899 | 218.4519 | 212.0733 | 237.096
2024.1806 | 1951.1806 | 305.6592 | 242.5325 | 242.0787 | 244.5308 | 240.0898 | 218.4703 | 212.1044 | 237.0852
2025.1821 | 1952.1821 | 305.6965 | 242.5508 | 242.0819 | 244.5794 | 240.0869 | 218.4885 | 212.119 | 237.0877
2026.1835 | 1953.1835 | 305.6349 | 242.5672 | 242.0962 | 244.5852 | 240.0913 | 218.5094 | 212.1168 | 237.0957
2027.1849 | 1954.1849 | 305.5247 | 242.5864 | 242.1017 | 244.5976 | 240.1152 | 218.5213 | 212.1264 | 237.0944
2028.1864 | 1955.1864 | 305.5597 | 242.6037 | 242.1057 | 244.618 | 240.1163 | 218.5396 | 212.1261 | 237.1033
2029.1878 | 1956.1878 | 305.514 | 242.6324 | 242.1115 | 244.605 | 240.1285 | 218.5547 | 212.1045 | 237.1052
2030.1793 | 1957.1793 | 305.4601 | 242.6718 | 242.1274 | 244.6216 | 240.1367 | 218.5784 | 212.1319 | 237.1083
2031.1807 | 1958.1807 | 305.4119 | 242.7039 | 242.1367 | 244.6196 | 240.1385 | 218.5949 | 212.1299 | 237.1212
2032.1821 | 1959.1821 | 305.4527 | 242.7294 | 242.1378 | 244.6246 | 240.1498 | 218.6168 | 212.1319 | 237.1057
2033.1836 | 1960.1836 | 305.4825 | 242.7588 | 242.1453 | 244.6427 | 240.1533 | 218.6263 | 212.1326 | 237.1281
2034.185 | 1961.185 | 305.4727 | 242.7668 | 242.1396 | 244.6566 | 240.159 | 218.64 | 212.1319 | 237.1258
2035.1764 | 1962.1764 | 305.5082 | 242.7816 | 242.1401 | 244.6535 | 240.1625 | 218.6497 | 212.1362 | 237.1245
2036.1879 | 1963.1879 | 305.5805 | 242.7838 | 242.1359 | 244.6496 | 240.1728 | 218.6556 | 212.1384 | 237.152
2037.1793 | 1964.1793 | 305.6259 | 242.8022 | 242.1117 | 244.6762 | 240.1843 | 218.6632 | 212.1486 | 237.1494
2038.1808 | 1965.1808 | 305.7411 | 242.8099 | 242.1208 | 244.6392 | 240.1833 | 218.6767 | 212.0397 | 237.1739
2039.1822 | 1966.1822 | 305.8208 | 242.8158 | 242.1109 | 244.6298 | 240.1972 | 218.6823 | 212.0491 | 237.1642
2040.1836 | 1967.1836 | 305.7804 | 242.7918 | 242.0994 | 244.6273 | 240.2015 | 218.6964 | 212.1715 | 237.1675
2041.1851 | 1968.1851 | 305.7207 | 242.7572 | 242.0935 | 244.6385 | 240.2162 | 218.7015 | 212.1759 | 237.1738
2042.1765 | 1969.1765 | 305.7366 | 242.7673 | 242.0763 | 244.6284 | 240.2256 | 218.7134 | 212.0641 | 237.1634
2043.1779 | 1970.1779 | 305.8058 | 242.7773 | 242.0804 | 244.6487 | 240.2395 | 218.7197 | 212.0617 | 237.1705
2044.1794 | 1971.1794 | 305.8547 | 242.7895 | 242.0861 | 244.6532 | 240.247 | 218.7332 | 212.0624 | 237.1695
2045.1808 | 1972.1808 | 305.9338 | 242.81 | 242.0832 | 244.6341 | 240.247 | 218.7396 | 212.0666 | 237.185
2046.1823 | 1973.1823 | 305.9326 | 242.8187 | 242.0837 | 244.6372 | 240.2637 | 218.7437 | 212.0695 | 237.1938
2047.1837 | 1974.1837 | 305.8745 | 242.8292 | 242.0811 | 244.6416 | 240.2834 | 218.7591 | 212.0778 | 237.2017
2048.1851 | 1975.1851 | 305.847 | 242.8476 | 242.0686 | 244.6555 | 240.2752 | 218.7624 | 212.0773 | 237.2159
2049.1866 | 1976.1866 | 305.9389 | 242.8635 | 242.0726 | 244.6865 | 240.2867 | 218.7849 | 212.0849 | 237.2241
2050.178 | 1977.178 | 306.0279 | 242.8725 | 242.0792 | 244.684 | 240.2938 | 218.7914 | 212.0973 | 237.2275
2051.1795 | 1978.1795 | 306.0381 | 242.8849 | 242.0723 | 244.666 | 240.3036 | 218.8038 | 212.1015 | 237.2337
2052.1809 | 1979.1809 | 306.0558 | 242.8914 | 242.063 | 244.6974 | 240.3082 | 218.8163 | 212.1128 | 237.2445
2053.1823 | 1980.1823 | 306.1011 | 242.8951 | 242.0561 | 244.6477 | 240.318 | 218.8279 | 212.1256 | 237.2479
2054.1838 | 1981.1838 | 306.1446 | 242.9081 | 242.0653 | 244.6623 | 240.3228 | 218.8396 | 212.2312 | 237.251
2055.1852 | 1982.1852 | 306.1348 | 242.9105 | 242.0588 | 244.6405 | 240.3306 | 218.86 | 212.2467 | 237.244
2056.1867 | 1983.1867 | 306.2165 | 242.9112 | 242.0508 | 244.6817 | 240.3367 | 218.8705 | 212.2505 | 237.2591
2057.1881 | 1984.1881 | 306.2139 | 242.9069 | 242.0477 | 244.6765 | 240.3485 | 218.8821 | 212.2614 | 237.2718
2058.1795 | 1985.1795 | 306.1636 | 242.894 | 242.0364 | 244.7004 | 240.3584 | 218.8984 | 212.2738 | 237.2749
2059.181 | 1986.181 | 306.1438 | 242.8628 | 242.0318 | 244.7464 | 240.3566 | 218.9104 | 212.2815 | 237.2867
2060.1824 | 1987.1824 | 306.1664 | 242.8267 | 242.0119 | 244.784 | 240.3718 | 218.9272 | 212.2933 | 237.2846
2061.1838 | 1988.1838 | 306.2606 | 242.8041 | 241.9966 | 244.7863 | 240.3763 | 218.9379 | 212.2952 | 237.2876
2062.1853 | 1989.1853 | 306.2576 | 242.7916 | 241.9749 | 244.7961 | 240.3805 | 218.9585 | 212.3037 | 237.3088
2063.1767 | 1990.1767 | 306.2884 | 242.7916 | 241.9606 | 244.8272 | 240.3937 | 218.9761 | 212.2276 | 237.3185
2064.1781 | 1991.1781 | 306.3153 | 242.7995 | 241.9353 | 244.8256 | 240.4006 | 218.9897 | 212.1935 | 237.3184
2065.1796 | 1992.1796 | 306.3208 | 242.807 | 241.9284 | 244.8717 | 240.4123 | 219.0029 | 212.3178 | 237.3409
2066.181 | 1993.181 | 306.2711 | 242.8144 | 241.9177 | 244.8746 | 240.416 | 219.0166 | 212.3227 | 237.3323
2067.1825 | 1994.1825 | 306.2672 | 242.8136 | 241.9002 | 244.8604 | 240.4136 | 219.0355 | 212.3321 | 237.3499
2068.1839 | 1995.1839 | 306.4262 | 242.8178 | 241.8827 | 244.8006 | 240.4279 | 219.049 | 212.3314 | 237.3432
2069.1853 | 1996.1853 | 306.5608 | 242.8335 | 241.8629 | 244.8044 | 240.4368 | 219.0656 | 212.3373 | 237.3694
2070.1768 | 1997.1768 | 306.5843 | 242.8513 | 241.8522 | 244.7335 | 240.4445 | 219.075 | 212.2218 | 237.3742
2071.1782 | 1998.1782 | 306.5521 | 242.8594 | 241.8467 | 244.6986 | 240.446 | 219.095 | 212.3359 | 237.3918
2072.1796 | 1999.1796 | 306.568 | 242.8649 | 241.8343 | 244.6961 | 240.4494 | 219.1108 | 212.2254 | 237.391
2073.1811 | 2000.1811 | 306.5452 | 242.8703 | 241.818 | 244.6775 | 240.4555 | 219.1248 | 212.2342 | 237.4143
2074.1825 | 2001.1825 | 306.5151 | 242.8742 | 241.8089 | 244.6875 | 240.4551 | 219.1446 | 212.244 | 237.4234
2075.184 | 2002.184 | 306.4887 | 242.8623 | 241.7968 | 244.7123 | 240.4861 | 219.1725 | 212.2577 | 237.3985
2076.1854 | 2003.1854 | 306.4466 | 242.867 | 241.7848 | 244.6909 | 240.4769 | 219.1796 | 212.2584 | 237.4034
2077.1768 | 2004.1768 | 306.4637 | 242.8257 | 241.832 | 244.6395 | 240.6058 | 219.3109 | 212.2433 | 237.2802
2078.1883 | 2005.1883 | 306.5167 | 242.8941 | 241.7797 | 244.6086 | 240.4748 | 219.1768 | 212.2772 | 237.4459
2079.1797 | 2006.1797 | 306.5426 | 242.9072 | 241.7633 | 244.609 | 240.4794 | 219.1845 | 212.2888 | 237.4468
2080.1812 | 2007.1812 | 306.5729 | 242.916 | 241.7759 | 244.6277 | 240.4779 | 219.1884 | 212.2858 | 237.4598
2081.1826 | 2008.1826 | 306.6508 | 242.9388 | 241.7757 | 244.6366 | 240.4906 | 219.1996 | 212.3018 | 237.469
2082.184 | 2009.184 | 306.6716 | 242.9643 | 241.7612 | 244.5516 | 240.4942 | 219.212 | 212.3128 | 237.4444
2083.1855 | 2010.1855 | 306.5912 | 242.991 | 241.7587 | 244.4515 | 240.4887 | 219.2147 | 212.3124 | 237.4501
2084.1769 | 2011.1769 | 306.4198 | 243.0082 | 241.775 | 244.4118 | 240.4869 | 219.2247 | 212.3227 | 237.47
2085.1783 | 2012.1783 | 306.2888 | 243.0196 | 241.7687 | 244.3058 | 240.4728 | 219.2293 | 212.3216 | 237.4672
2086.1798 | 2013.1798 | 306.182 | 243.0354 | 241.7869 | 244.2514 | 240.4696 | 219.2373 | 212.3164 | 237.4569
2087.1812 | 2014.1812 | 306.0763 | 243.0388 | 241.7891 | 244.2425 | 240.4723 | 219.2435 | 212.3168 | 237.454
2088.1827 | 2015.1827 | 306.1387 | 243.0496 | 241.8035 | 244.1374 | 240.4683 | 219.2561 | 212.3137 | 237.4587
2089.1841 | 2016.1841 | 306.1092 | 243.0648 | 241.8187 | 244.1335 | 240.462 | 219.2593 | 212.309 | 237.4503
2090.1855 | 2017.1855 | 306.0333 | 243.0924 | 241.816 | 243.9737 | 240.456 | 219.2687 | 212.3041 | 237.4351
2091.187 | 2018.187 | 306.0505 | 243.1086 | 241.8392 | 243.9353 | 240.4614 | 219.2736 | 212.3184 | 237.4162
2092.1784 | 2019.1784 | 306.1062 | 243.1335 | 241.8498 | 243.9272 | 240.4486 | 219.2814 | 212.3122 | 237.4371
2093.1798 | 2020.1798 | 306.1326 | 243.1548 | 241.8685 | 243.8836 | 240.4485 | 219.2865 | 212.316 | 237.4075
2094.1813 | 2021.1813 | 306.0203 | 243.167 | 241.8727 | 243.878 | 240.4422 | 219.301 | 212.3156 | 237.3953
2095.1827 | 2022.1827 | 305.8111 | 243.1749 | 241.9105 | 243.7689 | 240.434 | 219.3044 | 212.3176 | 237.3984
2096.1842 | 2023.1842 | 305.7268 | 243.1949 | 241.9188 | 243.6779 | 240.4307 | 219.3135 | 212.3214 | 237.3839
2097.1856 | 2024.1856 | 305.5425 | 243.225 | 241.9557 | 243.5541 | 240.4215 | 219.3236 | 212.3168 | 237.3793
2098.187 | 2025.187 | 305.4253 | 243.261 | 241.9606 | 243.4956 | 240.4093 | 219.3229 | 212.3176 | 237.3829
2099.1885 | 2026.1885 | 305.4526 | 243.2819 | 241.9832 | 243.5056 | 240.4 | 219.339 | 212.3202 | 237.36
2100.1799 | 2027.1799 | 305.456 | 243.2967 | 241.9851 | 243.4697 | 240.3775 | 219.3433 | 212.3333 | 237.3513
2101.1814 | 2028.1814 | 305.4414 | 243.3018 | 241.9937 | 243.4533 | 240.3604 | 219.3529 | 212.3458 | 237.3443
2102.1828 | 2029.1828 | 305.3962 | 243.3099 | 242.0061 | 243.4132 | 240.3462 | 219.3711 | 212.354 | 237.335
2103.1842 | 2030.1842 | 305.3375 | 243.3053 | 242.0174 | 243.4093 | 240.3422 | 219.3766 | 212.3614 | 237.3316
2104.1857 | 2031.1857 | 305.3014 | 243.3042 | 242.0161 | 243.3938 | 240.3178 | 219.3824 | 212.3634 | 237.3286
2105.1771 | 2032.1771 | 305.3067 | 243.3124 | 242.0271 | 243.3592 | 240.3095 | 219.3916 | 212.4939 | 237.3175
2106.1785 | 2033.1785 | 305.3516 | 243.3247 | 242.0291 | 243.3377 | 240.3028 | 219.3974 | 212.4895 | 237.3046
2107.18 | 2034.18 | 305.3608 | 243.3374 | 242.0265 | 243.3125 | 240.2894 | 219.3953 | 212.4779 | 237.2839
2108.1814 | 2035.1814 | 305.399 | 243.3491 | 242.0317 | 243.3256 | 240.283 | 219.4071 | 212.5071 | 237.2873
2109.1829 | 2036.1829 | 305.4015 | 243.3554 | 242.038 | 243.3345 | 240.2632 | 219.4064 | 212.4405 | 237.2666
2110.1843 | 2037.1843 | 305.4366 | 243.3677 | 242.0375 | 243.3498 | 240.2564 | 219.3985 | 212.5023 | 237.2675
2111.1857 | 2038.1857 | 305.5535 | 243.3842 | 242.0357 | 243.3525 | 240.2541 | 219.4029 | 212.5053 | 237.2511
2112.1872 | 2039.1872 | 305.6073 | 243.4057 | 242.0363 | 243.3451 | 240.2563 | 219.4108 | 212.5032 | 237.242
2113.1786 | 2040.1786 | 305.6408 | 243.4169 | 242.039 | 243.3271 | 240.2373 | 219.4067 | 212.5064 | 237.2393
2114.18 | 2041.18 | 305.6503 | 243.4195 | 242.0438 | 243.2648 | 240.239 | 219.4134 | 212.5003 | 237.2474
2115.1815 | 2042.1815 | 305.7199 | 243.4236 | 242.0514 | 243.2289 | 240.246 | 219.4182 | 212.4949 | 237.2286
2116.1829 | 2043.1829 | 305.8177 | 243.4335 | 242.0382 | 243.2145 | 240.2299 | 219.4222 | 212.5013 | 237.2359
2117.1844 | 2044.1844 | 305.8617 | 243.445 | 242.0469 | 243.2444 | 240.2349 | 219.423 | 212.4985 | 237.2218
2118.1858 | 2045.1858 | 305.8319 | 243.4506 | 242.0544 | 243.2728 | 240.2242 | 219.4271 | 212.5022 | 237.2311
2119.1772 | 2046.1772 | 305.7796 | 243.4598 | 242.0594 | 243.2625 | 240.2278 | 219.4334 | 212.5063 | 237.2352
2120.1887 | 2047.1887 | 305.7921 | 243.4617 | 242.0706 | 243.2937 | 240.22 | 219.4276 | 212.5131 | 237.2361
2121.1801 | 2048.1801 | 305.7692 | 243.4641 | 242.07 | 243.3152 | 240.2194 | 219.436 | 212.5215 | 237.2288
2122.1815 | 2049.1815 | 305.8374 | 243.4748 | 242.0586 | 243.261 | 240.2249 | 219.4428 | 212.5304 | 237.2294
2123.183 | 2050.183 | 305.8333 | 243.4853 | 242.0639 | 243.2736 | 240.2269 | 219.4392 | 212.5344 | 237.227
2124.1844 | 2051.1844 | 305.841 | 243.4719 | 242.0587 | 243.3117 | 240.2281 | 219.4446 | 212.5413 | 237.2298
2125.1859 | 2052.1859 | 305.9264 | 243.4349 | 242.0685 | 243.334 | 240.2139 | 219.449 | 212.556 | 237.2165
2126.1773 | 2053.1773 | 306.0227 | 243.3753 | 242.052 | 243.3274 | 240.2334 | 219.4504 | 212.5628 | 237.2184
2127.1787 | 2054.1787 | 305.97 | 243.3289 | 242.0436 | 243.3527 | 240.23 | 219.4603 | 212.4966 | 237.219
2128.1802 | 2055.1802 | 305.88 | 243.3069 | 242.0555 | 243.3897 | 240.2317 | 219.4592 | 212.5868 | 237.2483
2129.1816 | 2056.1816 | 305.9272 | 243.3021 | 242.0512 | 243.4195 | 240.2356 | 219.4631 | 212.6041 | 237.2307
2130.1831 | 2057.1831 | 305.9953 | 243.3066 | 242.0473 | 243.4459 | 240.2442 | 219.4658 | 212.6028 | 237.2707
2131.1845 | 2058.1845 | 305.9583 | 243.2953 | 242.0404 | 243.4633 | 240.2508 | 219.4686 | 212.6196 | 237.2574
2132.1859 | 2059.1859 | 305.9401 | 243.2843 | 242.0461 | 243.4841 | 240.257 | 219.4751 | 212.6211 | 237.2606
2133.1874 | 2060.1874 | 305.8994 | 243.2706 | 242.0359 | 243.4854 | 240.247 | 219.4731 | 212.6253 | 237.2584
2134.1788 | 2061.1788 | 306.0684 | 243.2735 | 242.0257 | 243.4841 | 240.2568 | 219.4735 | 212.6316 | 237.2503
2135.1802 | 2062.1802 | 306.1839 | 243.2777 | 242.0225 | 243.4683 | 240.2637 | 219.4857 | 212.6422 | 237.2561
2136.1817 | 2063.1817 | 306.24 | 243.2759 | 242.0135 | 243.4801 | 240.2669 | 219.4821 | 212.6595 | 237.2609
2137.1831 | 2064.1831 | 306.2841 | 243.2749 | 242.0026 | 243.4029 | 240.2518 | 219.4841 | 212.6599 | 237.2526
2138.1846 | 2065.1846 | 306.2147 | 243.2694 | 241.9829 | 243.4181 | 240.2642 | 219.4869 | 212.664 | 237.2475
2139.186 | 2066.186 | 306.2423 | 243.2696 | 241.9572 | 243.4298 | 240.2721 | 219.4835 | 212.668 | 237.2345
2140.1774 | 2067.1774 | 306.2058 | 243.2541 | 241.9457 | 243.423 | 240.2618 | 219.4918 | 212.6702 | 237.2341
2141.1889 | 2068.1889 | 306.0699 | 243.2358 | 241.9227 | 243.4301 | 240.2555 | 219.4957 | 212.6741 | 237.2384
2142.1803 | 2069.1803 | 305.9017 | 243.2271 | 241.9067 | 243.4362 | 240.2597 | 219.4997 | 212.6722 | 237.2452
2143.1817 | 2070.1817 | 305.7159 | 243.2249 | 241.9083 | 243.4251 | 240.2502 | 219.5056 | 212.5729 | 237.2435
2144.1832 | 2071.1832 | 305.576 | 243.2373 | 241.9084 | 243.37 | 240.2565 | 219.5067 | 212.5638 | 237.2451
2145.1846 | 2072.1846 | 305.4934 | 243.243 | 241.8956 | 243.3658 | 240.2512 | 219.507 | 212.5734 | 237.218
2146.1861 | 2073.1861 | 305.4652 | 243.2372 | 241.8662 | 243.3748 | 240.235 | 219.5038 | 212.5794 | 237.2219
2147.1775 | 2074.1775 | 305.369 | 243.2422 | 241.8613 | 243.3276 | 240.2318 | 219.5057 | 212.5847 | 237.2222
2148.1789 | 2075.1789 | 305.2925 | 243.2256 | 241.8421 | 243.3388 | 240.2326 | 219.5104 | 212.5822 | 237.2147
2149.1804 | 2076.1804 | 305.2641 | 243.2114 | 241.8253 | 243.2462 | 240.2268 | 219.4981 | 212.5821 | 237.2143
2150.1818 | 2077.1818 | 305.1993 | 243.182 | 241.8089 | 243.2667 | 240.2226 | 219.4979 | 212.5833 | 237.2118
2151.1832 | 2078.1832 | 305.1387 | 243.1534 | 241.7859 | 243.2378 | 240.221 | 219.4954 | 212.5848 | 237.2072
2152.1847 | 2079.1847 | 305.1013 | 243.1292 | 241.772 | 243.2522 | 240.1971 | 219.4886 | 212.5827 | 237.2011
2153.1861 | 2080.1861 | 305.0676 | 243.0968 | 241.7603 | 243.2236 | 240.2059 | 219.4938 | 212.5816 | 237.2035
2154.1876 | 2081.1876 | 305.0444 | 243.0811 | 241.7462 | 243.2561 | 240.1925 | 219.4937 | 212.5822 | 237.1986
2155.179 | 2082.179 | 305.0321 | 243.0597 | 241.7246 | 243.286 | 240.1925 | 219.4925 | 212.5817 | 237.192
2156.1804 | 2083.1804 | 305.074 | 243.0447 | 241.7251 | 243.3171 | 240.1859 | 219.4832 | 212.5845 | 237.1892
2157.1819 | 2084.1819 | 305.1301 | 243.0424 | 241.704 | 243.3504 | 240.1933 | 219.4855 | 212.5939 | 237.194
2158.1833 | 2085.1833 | 305.2101 | 243.0255 | 241.6908 | 243.369 | 240.1903 | 219.4739 | 212.5959 | 237.1832
2159.1848 | 2086.1848 | 305.2326 | 243.015 | 241.6739 | 243.4043 | 240.1938 | 219.4722 | 212.6154 | 237.196
2160.1762 | 2087.1762 | 305.2824 | 243.0108 | 241.666 | 243.4074 | 240.1904 | 219.465 | 212.6207 | 237.201
2161.1776 | 2088.1776 | 305.3103 | 242.9713 | 241.6594 | 243.4634 | 240.1847 | 219.4624 | 212.6288 | 237.1951
2162.1891 | 2089.1891 | 305.3782 | 242.9204 | 241.651 | 243.4043 | 240.1877 | 219.4542 | 212.6441 | 237.2146
2163.1805 | 2090.1805 | 305.4301 | 242.8848 | 241.6387 | 243.4449 | 240.1928 | 219.4513 | 212.6488 | 237.2152
2164.1819 | 2091.1819 | 305.5643 | 242.8322 | 241.625 | 243.441 | 240.1971 | 219.439 | 212.6513 | 237.2168
2165.1834 | 2092.1834 | 305.7246 | 242.8046 | 241.6119 | 243.4776 | 240.1916 | 219.4429 | 212.6574 | 237.2119
2166.1848 | 2093.1848 | 305.9358 | 242.7793 | 241.6012 | 243.5335 | 240.1917 | 219.4376 | 212.6734 | 237.2139
2167.1863 | 2094.1863 | 306.0793 | 242.7802 | 241.5997 | 243.5509 | 240.199 | 219.4321 | 212.6903 | 237.2328
2168.1777 | 2095.1777 | 306.1148 | 242.8327 | 241.5962 | 243.5989 | 240.2028 | 219.4385 | 212.7096 | 237.232
2169.1791 | 2096.1791 | 306.2201 | 242.8532 | 241.592 | 243.6577 | 240.2064 | 219.4353 | 212.8145 | 237.2448
2170.1806 | 2097.1806 | 306.3849 | 242.8448 | 241.5924 | 243.6807 | 240.2074 | 219.4257 | 212.7273 | 237.2435
2171.182 | 2098.182 | 306.4296 | 242.8357 | 241.5927 | 243.7132 | 240.2106 | 219.4298 | 212.8482 | 237.2347
2172.1834 | 2099.1834 | 306.4474 | 242.8345 | 241.6037 | 243.7524 | 240.215 | 219.4254 | 212.8674 | 237.2419
2173.1849 | 2100.1849 | 306.5707 | 242.8026 | 241.6041 | 243.8234 | 240.2095 | 219.4227 | 212.8868 | 237.2581
2174.1863 | 2101.1863 | 306.6331 | 242.7671 | 241.5996 | 243.8617 | 240.2161 | 219.4189 | 212.8935 | 237.238
2175.1778 | 2102.1778 | 306.6755 | 242.7175 | 241.6041 | 243.8883 | 240.2203 | 219.4192 | 212.9042 | 237.2661
2176.1792 | 2103.1792 | 306.689 | 242.6876 | 241.6135 | 243.9261 | 240.209 | 219.4139 | 212.9218 | 237.2649
2177.1806 | 2104.1806 | 306.7526 | 242.658 | 241.6286 | 243.9653 | 240.2126 | 219.4138 | 212.9361 | 237.2674
2178.1821 | 2105.1821 | 306.7735 | 242.6454 | 241.6212 | 244.0035 | 240.2198 | 219.4158 | 212.9515 | 237.287
2179.1835 | 2106.1835 | 306.7945 | 242.6395 | 241.6473 | 244.0672 | 240.2157 | 219.4063 | 212.955 | 237.2872
2180.185 | 2107.185 | 306.8627 | 242.6387 | 241.65 | 244.0967 | 240.2114 | 219.414 | 212.9765 | 237.3024
2181.1864 | 2108.1864 | 306.9422 | 242.6321 | 241.6781 | 244.145 | 240.2244 | 219.4126 | 212.987 | 237.3055
2182.1878 | 2109.1878 | 307.0019 | 242.6365 | 241.6829 | 244.17 | 240.2235 | 219.3973 | 213.0042 | 237.3271
2183.1793 | 2110.1793 | 306.9504 | 242.6567 | 241.7066 | 244.1933 | 240.211 | 219.401 | 213.0182 | 237.37
2184.1807 | 2111.1807 | 306.8914 | 242.6621 | 241.7205 | 244.2327 | 240.2018 | 219.3834 | 213.0351 | 237.4006
2185.1821 | 2112.1821 | 306.8845 | 242.6757 | 241.7306 | 244.2859 | 240.2185 | 219.3865 | 213.0484 | 237.4105
2186.1836 | 2113.1836 | 306.7886 | 242.6739 | 241.7349 | 244.3379 | 240.2179 | 219.3845 | 213.0647 | 237.4207
2187.185 | 2114.185 | 306.6068 | 242.6732 | 241.7594 | 244.332 | 240.232 | 219.3759 | 213.0765 | 237.4242
2188.1865 | 2115.1865 | 306.34 | 242.6949 | 241.7767 | 244.3168 | 240.2349 | 219.3779 | 213.0899 | 237.4399
2189.1779 | 2116.1779 | 306.1117 | 242.7017 | 241.767 | 244.361 | 240.2332 | 219.3677 | 213.1004 | 237.4198
2190.1793 | 2117.1793 | 305.847 | 242.7242 | 241.7945 | 244.3913 | 240.2436 | 219.3619 | 213.1093 | 237.4244
2191.1808 | 2118.1808 | 305.4842 | 242.7272 | 241.7954 | 244.4129 | 240.2392 | 219.3552 | 213.1183 | 237.4145
2192.1822 | 2119.1822 | 305.2276 | 242.7334 | 241.8246 | 244.4519 | 240.2412 | 219.3388 | 213.1333 | 237.4136
2193.1836 | 2120.1836 | 304.9132 | 242.7432 | 241.8466 | 244.445 | 240.2342 | 219.3264 | 213.142 | 237.3939
2194.1851 | 2121.1851 | 304.5403 | 242.753 | 241.8556 | 244.4594 | 240.2335 | 219.3077 | 213.1601 | 237.3807
2195.1765 | 2122.1765 | 304.2971 | 242.7472 | 241.8647 | 244.3637 | 240.2309 | 219.2884 | 213.1651 | 237.3703
2196.1779 | 2123.1779 | 304.0837 | 242.7435 | 241.875 | 244.2944 | 240.2301 | 219.2689 | 213.1738 | 237.3757
2197.1794 | 2124.1794 | 303.7985 | 242.7277 | 241.9005 | 244.3188 | 240.2399 | 219.2505 | 213.1877 | 237.364
2198.1808 | 2125.1808 | 303.4785 | 242.7244 | 241.9008 | 244.2431 | 240.2286 | 219.2334 | 213.1965 | 237.3421
2199.1823 | 2126.1823 | 303.1525 | 242.7164 | 241.8888 | 244.1956 | 240.2301 | 219.2161 | 213.1984 | 237.3426
2200.1837 | 2127.1837 | 302.8165 | 242.7109 | 241.8889 | 244.1526 | 240.2347 | 219.2086 | 213.2002 | 237.308
2201.1851 | 2128.1851 | 302.5187 | 242.7027 | 241.8718 | 244.152 | 240.2352 | 219.1881 | 213.1953 | 237.2756
2202.1766 | 2129.1766 | 302.1651 | 242.6912 | 241.8556 | 244.1478 | 240.2159 | 219.1721 | 213.1929 | 237.2548
2203.178 | 2130.178 | 301.733 | 242.6784 | 241.8425 | 244.1197 | 240.2153 | 219.1488 | 213.1883 | 237.2203
2204.1795 | 2131.1795 | 301.32 | 242.6746 | 241.8267 | 244.1213 | 240.1922 | 219.1383 | 213.1932 | 237.2064
2205.1809 | 2132.1809 | 300.8872 | 242.6613 | 241.8179 | 244.104 | 240.1965 | 219.1213 | 213.1777 | 237.1918
2206.1823 | 2133.1823 | 300.4819 | 242.6481 | 241.8087 | 244.0678 | 240.1727 | 219.1004 | 213.1762 | 237.1654
2207.1838 | 2134.1838 | 300.0669 | 242.6365 | 241.7928 | 244.0451 | 240.1771 | 219.0801 | 213.1614 | 237.1387
2208.1852 | 2135.1852 | 299.6286 | 242.6179 | 241.7715 | 243.9857 | 240.1569 | 219.0586 | 213.1558 | 237.1114
2209.1766 | 2136.1766 | 299.2508 | 242.6122 | 241.7539 | 243.9726 | 240.138 | 219.0331 | 213.1537 | 237.0844
2210.1881 | 2137.1881 | 298.8199 | 242.5932 | 241.7368 | 243.9479 | 240.1215 | 219.0082 | 213.1481 | 237.0498
2211.1795 | 2138.1795 | 298.39 | 242.5675 | 241.7104 | 243.8964 | 240.119 | 218.9866 | 213.1324 | 237.0234
2212.181 | 2139.181 | 297.9776 | 242.5299 | 241.6959 | 243.8433 | 240.0952 | 218.9544 | 213.1282 | 237.0044
2213.1824 | 2140.1824 | 297.6447 | 242.4889 | 241.6722 | 243.8074 | 240.0993 | 218.9258 | 213.1085 | 236.9696
2214.1838 | 2141.1838 | 297.2942 | 242.4503 | 241.6411 | 243.7524 | 240.0739 | 218.8966 | 213.0936 | 236.9323
2215.1853 | 2142.1853 | 296.8743 | 242.4092 | 241.6092 | 243.7304 | 240.0511 | 218.8625 | 213.0806 | 236.9018
2216.1867 | 2143.1867 | 296.5221 | 242.3601 | 241.561 | 243.6999 | 240.0557 | 218.8362 | 213.0656 | 236.8504
2217.1781 | 2144.1781 | 296.1659 | 242.3117 | 241.5292 | 243.6559 | 240.0461 | 218.7949 | 213.0429 | 236.8314
2218.1796 | 2145.1796 | 295.8437 | 242.262 | 241.4932 | 243.6008 | 240.0312 | 218.7733 | 213.0367 | 236.7974
2219.181 | 2146.181 | 295.5114 | 242.2058 | 241.454 | 243.5619 | 240.0143 | 218.7404 | 213.0239 | 236.7539
2220.1825 | 2147.1825 | 295.0826 | 242.1524 | 241.4151 | 243.5162 | 239.9962 | 218.7116 | 213.0139 | 236.7095
2221.1839 | 2148.1839 | 294.6595 | 242.0957 | 241.3732 | 243.4669 | 239.9776 | 218.678 | 212.9947 | 236.6697
2222.1853 | 2149.1853 | 294.2395 | 242.0366 | 241.327 | 243.4268 | 239.9575 | 218.6409 | 212.9841 | 236.6333
2223.1868 | 2150.1868 | 293.7992 | 241.9846 | 241.2849 | 243.3369 | 239.9264 | 218.6036 | 212.9742 | 236.5487
2224.1782 | 2151.1782 | 293.3997 | 241.9381 | 241.2438 | 243.2594 | 239.8983 | 218.575 | 212.9534 | 236.5132
2225.1797 | 2152.1797 | 293.1246 | 241.9024 | 241.196 | 243.203 | 239.8779 | 218.5361 | 212.9384 | 236.4571
2226.1811 | 2153.1811 | 292.8531 | 241.8799 | 241.1641 | 242.9984 | 239.8547 | 218.4954 | 212.9145 | 236.4139
2227.1825 | 2154.1825 | 292.4882 | 241.848 | 241.1044 | 242.9407 | 239.8206 | 218.4671 | 212.9002 | 236.3555
2228.184 | 2155.184 | 292.2311 | 241.8242 | 241.0884 | 242.8604 | 239.7869 | 218.4304 | 212.8735 | 236.2769
2229.1854 | 2156.1854 | 291.9709 | 241.7874 | 241.0529 | 242.795 | 239.775 | 218.3966 | 212.8595 | 236.2284
2230.1869 | 2157.1869 | 291.5758 | 241.7494 | 241.0024 | 242.7211 | 239.7318 | 218.3616 | 212.8288 | 236.1739
2231.1783 | 2158.1783 | 291.128 | 241.7096 | 240.9541 | 242.6424 | 239.7004 | 218.3283 | 212.809 | 236.1276
2232.1797 | 2159.1797 | 290.6991 | 241.6755 | 240.9192 | 242.5527 | 239.6613 | 218.2875 | 212.7795 | 236.0793
2233.1812 | 2160.1812 | 290.3747 | 241.6419 | 240.8709 | 242.4663 | 239.6325 | 218.2475 | 212.7571 | 236.0098
2234.1826 | 2161.1826 | 290.0804 | 241.6048 | 240.8342 | 242.3809 | 239.5937 | 218.2031 | 212.7293 | 235.9566
2235.184 | 2162.184 | 289.7746 | 241.5634 | 240.7737 | 242.3113 | 239.5626 | 218.165 | 212.7011 | 235.8972
2236.1855 | 2163.1855 | 289.4915 | 241.5257 | 240.7265 | 242.2377 | 239.5239 | 218.125 | 212.6717 | 235.8395
2237.1869 | 2164.1869 | 289.1518 | 241.49 | 240.6715 | 242.1626 | 239.5057 | 218.0921 | 212.6355 | 235.771
2238.1783 | 2165.1783 | 288.7634 | 241.4461 | 240.6361 | 242.105 | 239.4652 | 218.0557 | 212.6094 | 235.7008
2239.1798 | 2166.1798 | 288.3279 | 241.4018 | 240.5622 | 242.0253 | 239.4446 | 218.0178 | 212.5682 | 235.6323
2240.1812 | 2167.1812 | 287.8355 | 241.362 | 240.5224 | 241.9594 | 239.3933 | 217.9796 | 212.5341 | 235.5764
2241.1827 | 2168.1827 | 287.3365 | 241.3126 | 240.4603 | 241.8545 | 239.3703 | 217.9448 | 212.4952 | 235.4852
2242.1941 | 2169.1941 | 286.8097 | 241.263 | 240.4172 | 241.725 | 239.3385 | 217.9016 | 212.4572 | 235.4187
2243.1855 | 2170.1855 | 286.3145 | 241.2065 | 240.3631 | 241.6561 | 239.29 | 217.8653 | 212.4218 | 235.3567
2244.187 | 2171.187 | 285.8426 | 241.16 | 240.3106 | 241.5059 | 239.2474 | 217.8174 | 212.3779 | 235.2485
2245.1784 | 2172.1784 | 285.3942 | 241.1147 | 240.2489 | 241.3994 | 239.2113 | 217.7693 | 212.335 | 235.1882
2246.1798 | 2173.1798 | 284.9034 | 241.0763 | 240.2161 | 241.2821 | 239.1564 | 217.7259 | 212.2879 | 235.1042
2247.1813 | 2174.1813 | 284.4401 | 241.0341 | 240.1541 | 241.0925 | 239.1238 | 217.6819 | 212.2317 | 235.0275
2248.1827 | 2175.1827 | 283.9913 | 241.0015 | 240.1078 | 240.9944 | 239.0674 | 217.6255 | 212.1795 | 234.9426
2249.1842 | 2176.1842 | 283.5842 | 240.9608 | 240.0576 | 240.8581 | 239.0158 | 217.5811 | 212.1315 | 234.8568
2250.1856 | 2177.1856 | 283.2229 | 240.9241 | 240.0077 | 240.7441 | 238.9609 | 217.5291 | 212.0789 | 234.7838
2251.177 | 2178.177 | 282.7908 | 240.8761 | 239.95 | 240.6424 | 238.9117 | 217.4707 | 212.0204 | 234.6919
2252.1785 | 2179.1785 | 282.3442 | 240.8476 | 239.8885 | 240.5338 | 238.853 | 217.4161 | 211.9738 | 234.597
2253.1799 | 2180.1799 | 281.9257 | 240.8041 | 239.8462 | 240.4251 | 238.8055 | 217.3646 | 211.9247 | 234.5003
2254.1814 | 2181.1814 | 281.5086 | 240.7555 | 239.7765 | 240.2838 | 238.746 | 217.298 | 211.8736 | 234.4164
2255.1828 | 2182.1828 | 281.0942 | 240.7145 | 239.7239 | 240.161 | 238.6939 | 217.2364 | 211.831 | 234.3243
2256.1842 | 2183.1842 | 280.671 | 240.6681 | 239.6495 | 240.063 | 238.6444 | 217.1816 | 211.7877 | 234.2233
2257.1857 | 2184.1857 | 280.2119 | 240.6246 | 239.5928 | 239.9571 | 238.5832 | 217.1147 | 211.745 | 234.1204
2258.1871 | 2185.1871 | 279.7718 | 240.5768 | 239.5209 | 239.8676 | 238.5099 | 217.0394 | 211.7098 | 234.0112
2259.1785 | 2186.1785 | 279.3377 | 240.5245 | 239.4492 | 239.7725 | 238.4719 | 216.9809 | 211.6647 | 233.916
2260.18 | 2187.18 | 278.8833 | 240.4685 | 239.3692 | 239.6892 | 238.4149 | 216.9123 | 211.6284 | 233.8103
2261.1814 | 2188.1814 | 278.4851 | 240.4095 | 239.2856 | 239.5703 | 238.3662 | 216.8531 | 211.5914 | 233.7098
2262.1829 | 2189.1829 | 278.0951 | 240.3576 | 239.2226 | 239.4633 | 238.299 | 216.7782 | 211.5485 | 233.609
2263.1843 | 2190.1843 | 277.622 | 240.3098 | 239.1512 | 239.3414 | 238.2335 | 216.7002 | 211.4988 | 233.5152
2264.1857 | 2191.1857 | 277.2304 | 240.26 | 239.065 | 239.2251 | 238.173 | 216.6395 | 211.4463 | 233.4388
2265.1872 | 2192.1872 | 276.8419 | 240.21 | 238.9968 | 239.1251 | 238.1156 | 216.5603 | 211.3975 | 233.3348
2266.1786 | 2193.1786 | 276.3992 | 240.1549 | 238.9129 | 239.0304 | 238.0555 | 216.4877 | 211.3449 | 233.2138
2267.18 | 2194.18 | 276.0318 | 240.1003 | 238.8276 | 238.914 | 237.9952 | 216.4131 | 211.2974 | 233.1295
2268.1815 | 2195.1815 | 275.6432 | 240.045 | 238.7471 | 238.7594 | 237.9213 | 216.3353 | 211.2489 | 233.0065
2269.1829 | 2196.1829 | 275.2371 | 239.9912 | 238.6589 | 238.6311 | 237.8594 | 216.2653 | 211.1991 | 232.9191
2270.1844 | 2197.1844 | 274.8277 | 239.9289 | 238.579 | 238.4876 | 237.797 | 216.1842 | 211.1495 | 232.8041
2271.1858 | 2198.1858 | 274.3901 | 239.8704 | 238.498 | 238.355 | 237.7417 | 216.0987 | 211.103 | 232.6753
2272.1872 | 2199.1872 | 273.9676 | 239.8085 | 238.4142 | 238.2009 | 237.685 | 216.0145 | 211.0498 | 232.58
2273.1787 | 2200.1787 | 273.5326 | 239.7387 | 238.3344 | 238.0754 | 237.6163 | 215.9222 | 211.0007 | 232.467
2274.1801 | 2201.1801 | 273.2535 | 239.6809 | 238.2575 | 237.9352 | 237.5566 | 215.8411 | 210.9497 | 232.3568
2275.1816 | 2202.1816 | 272.9405 | 239.6045 | 238.173 | 237.8172 | 237.4789 | 215.7495 | 210.8948 | 232.2287
2276.183 | 2203.183 | 272.5784 | 239.5329 | 238.0812 | 237.6755 | 237.4129 | 215.6616 | 210.8499 | 232.1071
2277.1844 | 2204.1844 | 272.1949 | 239.4563 | 237.9857 | 237.5443 | 237.3369 | 215.5649 | 210.7872 | 232.0043
2278.1859 | 2205.1859 | 271.8248 | 239.3767 | 237.8955 | 237.3319 | 237.2625 | 215.481 | 210.724 | 231.8791
2279.1773 | 2206.1773 | 271.3961 | 239.2975 | 237.8046 | 237.171 | 237.1856 | 215.3841 | 210.659 | 231.7638
2280.1787 | 2207.1787 | 270.9719 | 239.2106 | 237.7155 | 236.9488 | 237.1142 | 215.2938 | 210.5967 | 231.6473
2281.1802 | 2208.1802 | 270.575 | 239.1311 | 237.6188 | 236.7921 | 237.0434 | 215.197 | 210.5291 | 231.5237
2282.1816 | 2209.1816 | 270.2432 | 239.0513 | 237.5212 | 236.6211 | 236.9654 | 215.1025 | 210.4628 | 231.3907
2283.2331 | 2210.2331 | 269.8793 | 238.9628 | 237.4236 | 236.431 | 236.8789 | 215.003 | 210.4024 | 231.2783
2284.1845 | 2211.1845 | 269.5525 | 238.8841 | 237.3281 | 236.2557 | 236.8126 | 214.9117 | 210.3336 | 231.1429
2285.1859 | 2212.1859 | 269.1688 | 238.8094 | 237.2403 | 236.1271 | 236.7326 | 214.8152 | 210.2705 | 231.0257
2286.1874 | 2213.1874 | 268.8612 | 238.7341 | 237.1485 | 235.9596 | 236.6606 | 214.7143 | 210.199 | 230.8982
2287.1788 | 2214.1788 | 268.5474 | 238.6638 | 237.0604 | 235.8114 | 236.582 | 214.6267 | 210.1173 | 230.7726
2288.1802 | 2215.1802 | 268.2019 | 238.5996 | 236.9693 | 235.6607 | 236.4911 | 214.5337 | 210.0385 | 230.652
2289.1817 | 2216.1817 | 267.8302 | 238.5347 | 236.8701 | 235.5065 | 236.4125 | 214.4326 | 209.9658 | 230.526
2290.1831 | 2217.1831 | 267.4591 | 238.4616 | 236.7915 | 235.3181 | 236.3475 | 214.3396 | 209.8927 | 230.4117
2291.1846 | 2218.1846 | 267.0724 | 238.3898 | 236.6999 | 235.1702 | 236.2604 | 214.2461 | 209.8312 | 230.2842
2292.176 | 2219.176 | 266.6956 | 238.3156 | 236.618 | 235.0281 | 236.175 | 214.146 | 209.7617 | 230.1378
2293.1774 | 2220.1774 | 266.3107 | 238.239 | 236.5198 | 234.886 | 236.086 | 214.0476 | 209.6867 | 230.0274
2294.1889 | 2221.1889 | 266.0488 | 238.1481 | 236.4178 | 234.6868 | 236.0191 | 213.9478 | 209.6097 | 229.8921
2295.1803 | 2222.1803 | 265.7555 | 238.0653 | 236.3148 | 234.5472 | 235.9136 | 213.8548 | 209.5332 | 229.7565
2296.1817 | 2223.1817 | 265.4201 | 237.9699 | 236.2144 | 234.3871 | 235.8355 | 213.7583 | 209.454 | 229.6289
2297.1832 | 2224.1832 | 265.1008 | 237.8834 | 236.1037 | 234.2386 | 235.7407 | 213.6635 | 209.3707 | 229.5017
2298.1846 | 2225.1846 | 264.7528 | 237.787 | 236.0008 | 234.0993 | 235.6579 | 213.5682 | 209.2917 | 229.3634
2299.1861 | 2226.1861 | 264.3912 | 237.6966 | 235.8851 | 233.9634 | 235.5689 | 213.4725 | 209.2119 | 229.2304
2300.1775 | 2227.1775 | 263.9882 | 237.5985 | 235.7709 | 233.8125 | 235.4856 | 213.3724 | 209.1312 | 229.1062
2301.1789 | 2228.1789 | 263.5964 | 237.5092 | 235.6699 | 233.6824 | 235.3936 | 213.2835 | 209.0536 | 228.9483
2302.1804 | 2229.1804 | 263.1655 | 237.4194 | 235.5585 | 233.5428 | 235.3051 | 213.1904 | 208.9761 | 228.8213
2303.1818 | 2230.1818 | 262.732 | 237.3161 | 235.4521 | 233.4197 | 235.2123 | 213.0885 | 208.8989 | 228.6876
2304.1833 | 2231.1833 | 262.335 | 237.2188 | 235.3497 | 233.2759 | 235.1182 | 212.9949 | 208.8302 | 228.5406
2305.1847 | 2232.1847 | 261.9788 | 237.1117 | 235.229 | 233.1351 | 235.0332 | 212.8988 | 208.7504 | 228.3915
2306.1861 | 2233.1861 | 261.5546 | 237.0229 | 235.129 | 233.0019 | 234.9309 | 212.7993 | 208.6762 | 228.271
2307.1876 | 2234.1876 | 261.1547 | 236.9187 | 235.0084 | 232.8146 | 234.8427 | 212.7018 | 208.6046 | 228.126
2308.179 | 2235.179 | 260.7977 | 236.8266 | 234.8971 | 232.5962 | 234.7439 | 212.6113 | 208.5278 | 227.9787
2309.1804 | 2236.1804 | 260.4896 | 236.736 | 234.7894 | 232.4454 | 234.6551 | 212.5074 | 208.4633 | 227.828
2310.1819 | 2237.1819 | 260.0768 | 236.6368 | 234.6754 | 232.3024 | 234.5555 | 212.408 | 208.3881 | 227.6773
2311.1833 | 2238.1833 | 259.6365 | 236.5427 | 234.5588 | 232.1382 | 234.4713 | 212.3077 | 208.3086 | 227.5297
2312.1848 | 2239.1848 | 259.2444 | 236.4551 | 234.4461 | 231.9693 | 234.386 | 212.206 | 208.2311 | 227.3871
2313.1862 | 2240.1862 | 258.8931 | 236.3596 | 234.3234 | 231.8219 | 234.2801 | 212.1041 | 208.1515 | 227.236
2314.1876 | 2241.1876 | 258.576 | 236.2572 | 234.2182 | 231.6481 | 234.1787 | 212.0053 | 208.0659 | 227.1029
2315.1791 | 2242.1791 | 258.2156 | 236.1643 | 234.1031 | 231.4773 | 234.0879 | 211.9021 | 207.9843 | 226.9456
2316.1805 | 2243.1805 | 257.8778 | 236.0778 | 233.9749 | 231.3138 | 233.9895 | 211.8054 | 207.9127 | 226.7923
2317.1819 | 2244.1819 | 257.5493 | 235.9792 | 233.8482 | 231.1678 | 233.8896 | 211.6992 | 207.8286 | 226.6389
2318.1834 | 2245.1834 | 257.1819 | 235.8815 | 233.7308 | 231.0118 | 233.7932 | 211.6022 | 207.7565 | 226.4923
2319.1848 | 2246.1848 | 256.7962 | 235.7845 | 233.6331 | 230.8501 | 233.7078 | 211.4951 | 207.6867 | 226.3503
2320.1863 | 2247.1863 | 256.4566 | 235.685 | 233.5148 | 230.7038 | 233.6203 | 211.3856 | 207.6016 | 226.1806
2321.1777 | 2248.1777 | 256.0706 | 235.5873 | 233.3957 | 230.5514 | 233.5201 | 211.2839 | 207.5122 | 226.0307
2322.1791 | 2249.1791 | 255.7068 | 235.4815 | 233.2805 | 230.391 | 233.4262 | 211.1744 | 207.4304 | 225.8833
2323.1806 | 2250.1806 | 255.3443 | 235.3795 | 233.1595 | 230.2476 | 233.3144 | 211.0565 | 207.3475 | 225.74
2324.182 | 2251.182 | 254.9733 | 235.2601 | 233.0301 | 230.0861 | 233.2181 | 210.9445 | 207.2566 | 225.5772
2325.1834 | 2252.1834 | 254.5622 | 235.1535 | 232.9144 | 229.9281 | 233.1178 | 210.838 | 207.1661 | 225.4432
2326.1849 | 2253.1849 | 254.2537 | 235.0279 | 232.7828 | 229.7614 | 233.0129 | 210.7333 | 207.0906 | 225.2812
2327.1863 | 2254.1863 | 253.9882 | 234.9036 | 232.6642 | 229.6019 | 232.9107 | 210.6263 | 207.0164 | 225.1351
2328.1778 | 2255.1778 | 253.673 | 234.7794 | 232.5285 | 229.4344 | 232.823 | 210.513 | 206.9478 | 224.9667
2329.1792 | 2256.1792 | 253.3703 | 234.6623 | 232.4046 | 229.2827 | 232.711 | 210.4021 | 206.8679 | 224.8226
2330.1806 | 2257.1806 | 253.0407 | 234.5342 | 232.2659 | 229.1398 | 232.5981 | 210.2833 | 206.7906 | 224.6841
2331.1821 | 2258.1821 | 252.7448 | 234.4115 | 232.14 | 228.9811 | 232.4817 | 210.1658 | 206.7184 | 224.5501
2332.1835 | 2259.1835 | 252.4298 | 234.2958 | 232.0202 | 228.8193 | 232.3764 | 210.0605 | 206.6373 | 224.3897
2333.185 | 2260.185 | 252.05 | 234.1769 | 231.8872 | 228.6693 | 232.2632 | 209.9444 | 206.563 | 224.2299
2334.1764 | 2261.1764 | 251.6951 | 234.0449 | 231.7567 | 228.5176 | 232.1481 | 209.8258 | 206.4744 | 224.0811
2335.1878 | 2262.1878 | 251.4381 | 233.918 | 231.6278 | 228.3712 | 232.0294 | 209.7143 | 206.385 | 223.9288
2336.1793 | 2263.1793 | 251.2061 | 233.7962 | 231.4985 | 228.197 | 231.9219 | 209.6042 | 206.2978 | 223.7917
2337.1807 | 2264.1807 | 250.9156 | 233.6685 | 231.3569 | 228.0385 | 231.7939 | 209.5002 | 206.2133 | 223.6157
2338.1821 | 2265.1821 | 250.5759 | 233.533 | 231.2338 | 227.8684 | 231.6886 | 209.3832 | 206.1322 | 223.475
2339.1836 | 2266.1836 | 250.177 | 233.4091 | 231.1095 | 227.7096 | 231.5672 | 209.2771 | 206.0358 | 223.2959
2340.185 | 2267.185 | 249.8326 | 233.2742 | 230.9785 | 227.5377 | 231.4551 | 209.1609 | 205.9461 | 223.1262
2341.1865 | 2268.1865 | 249.49 | 233.1417 | 230.8597 | 227.3821 | 231.3348 | 209.0509 | 205.8628 | 222.9839
2342.1779 | 2269.1779 | 249.1251 | 233.0107 | 230.7366 | 227.2216 | 231.2188 | 208.9408 | 205.7752 | 222.8406
2343.1793 | 2270.1793 | 248.7786 | 232.8753 | 230.6219 | 227.0565 | 231.0965 | 208.8355 | 205.6939 | 222.6955
2344.1808 | 2271.1808 | 248.5339 | 232.739 | 230.4958 | 226.9112 | 230.9791 | 208.7213 | 205.6074 | 222.5462
2345.1822 | 2272.1822 | 248.2762 | 232.6025 | 230.3667 | 226.7781 | 230.8647 | 208.6115 | 205.5181 | 222.3855
2346.1836 | 2273.1836 | 247.894 | 232.4623 | 230.2427 | 226.5866 | 230.7582 | 208.5024 | 205.4237 | 222.2353
2347.1851 | 2274.1851 | 247.5753 | 232.3246 | 230.1176 | 226.427 | 230.6339 | 208.3922 | 205.3458 | 222.0749
2348.1765 | 2275.1765 | 247.2199 | 232.1803 | 229.9956 | 226.2653 | 230.5188 | 208.2782 | 205.2548 | 221.9167
2349.178 | 2276.178 | 246.8329 | 232.0402 | 229.858 | 226.0785 | 230.4025 | 208.1697 | 205.1679 | 221.7665
2350.1794 | 2277.1794 | 246.5223 | 231.9101 | 229.722 | 225.9267 | 230.2846 | 208.0524 | 205.066 | 221.6034
2351.1808 | 2278.1808 | 246.197 | 231.7703 | 229.5618 | 225.7537 | 230.179 | 207.9411 | 204.9771 | 221.439
2352.1823 | 2279.1823 | 245.8845 | 231.6347 | 229.3993 | 225.6113 | 230.0538 | 207.8252 | 204.8904 | 221.2892
2353.1837 | 2280.1837 | 245.5007 | 231.5052 | 229.2658 | 225.427 | 229.9265 | 207.7102 | 204.7989 | 221.1213
2354.1852 | 2281.1852 | 245.1354 | 231.3775 | 229.1126 | 225.2411 | 229.8181 | 207.5958 | 204.7116 | 220.9544
2355.1866 | 2282.1866 | 244.7746 | 231.2499 | 228.9676 | 225.0959 | 229.711 | 207.4801 | 204.6208 | 220.8223
2356.188 | 2283.188 | 244.4485 | 231.1171 | 228.8311 | 224.9272 | 229.5871 | 207.3565 | 204.532 | 220.6343
2357.1795 | 2284.1795 | 244.1034 | 230.995 | 228.7015 | 224.7591 | 229.4638 | 207.2376 | 204.4354 | 220.4788
2358.1809 | 2285.1809 | 243.7191 | 230.8735 | 228.6 | 224.5591 | 229.3434 | 207.1204 | 204.351 | 220.3106
2359.1823 | 2286.1823 | 243.3811 | 230.7427 | 228.5168 | 224.3907 | 229.2389 | 206.9946 | 204.2553 | 220.1554
2360.1838 | 2287.1838 | 243.0556 | 230.6188 | 228.3994 | 224.1342 | 229.1233 | 206.8731 | 204.161 | 219.9886
2361.1852 | 2288.1852 | 242.6933 | 230.4918 | 228.2986 | 223.9896 | 229.0076 | 206.7457 | 204.0611 | 219.8196
2362.1867 | 2289.1867 | 242.3567 | 230.3639 | 228.1712 | 223.8194 | 228.8817 | 206.6202 | 203.9591 | 219.6351
2363.1781 | 2290.1781 | 242.0867 | 230.2268 | 228.038 | 223.658 | 228.7557 | 206.4859 | 203.8693 | 219.4858
2364.1795 | 2291.1795 | 241.8915 | 230.0886 | 227.8997 | 223.4943 | 228.6512 | 206.3565 | 203.7613 | 219.3199
2365.181 | 2292.181 | 241.5976 | 229.9512 | 227.7562 | 223.3428 | 228.5433 | 206.2231 | 203.6671 | 219.1578
2366.1824 | 2293.1824 | 241.2291 | 229.8108 | 227.6107 | 223.1781 | 228.4223 | 206.0922 | 203.5667 | 218.9842
2367.1838 | 2294.1838 | 240.8666 | 229.6662 | 227.4652 | 223.0228 | 228.3104 | 205.9562 | 203.4652 | 218.8207
2368.1853 | 2295.1853 | 240.5125 | 229.5336 | 227.3191 | 222.8607 | 228.1898 | 205.8253 | 203.3594 | 218.6335
2369.1767 | 2296.1767 | 240.1693 | 229.3986 | 227.1622 | 222.671 | 228.0651 | 205.6953 | 203.2625 | 218.465
2370.1781 | 2297.1781 | 239.8705 | 229.2495 | 227.0023 | 222.4636 | 227.9443 | 205.5639 | 203.1613 | 218.2931
2371.1796 | 2298.1796 | 239.5658 | 229.1229 | 226.8564 | 222.2722 | 227.832 | 205.432 | 203.0603 | 218.1319
2372.191 | 2299.191 | 239.2577 | 228.9848 | 226.6961 | 222.0906 | 227.7037 | 205.301 | 202.9543 | 217.9682
2373.1825 | 2300.1825 | 238.9037 | 228.8442 | 226.535 | 221.9254 | 227.5775 | 205.1651 | 202.8553 | 217.8033
2374.1839 | 2301.1839 | 238.6323 | 228.7005 | 226.3864 | 221.7362 | 227.4607 | 205.0342 | 202.747 | 217.6266
2375.1853 | 2302.1853 | 238.3607 | 228.5517 | 226.2405 | 221.5839 | 227.3303 | 204.9053 | 202.6423 | 217.4744
2376.1768 | 2303.1768 | 238.1259 | 228.4056 | 226.0918 | 221.4234 | 227.2085 | 204.7749 | 202.5352 | 217.3069
2377.1782 | 2304.1782 | 237.904 | 228.2643 | 225.9447 | 221.2791 | 227.0766 | 204.6378 | 202.4212 | 217.1129
2378.1797 | 2305.1797 | 237.7056 | 228.1328 | 225.8083 | 221.1264 | 226.9446 | 204.4985 | 202.3183 | 216.9543
2379.1811 | 2306.1811 | 237.5145 | 227.9898 | 225.6436 | 220.9481 | 226.8354 | 204.365 | 202.2134 | 216.7728
2380.1825 | 2307.1825 | 237.3043 | 227.8493 | 225.4982 | 220.7773 | 226.7042 | 204.2257 | 202.1121 | 216.6147
2381.184 | 2308.184 | 237.0513 | 227.7166 | 225.3646 | 220.5975 | 226.5738 | 204.1035 | 202.0039 | 216.445
2382.1854 | 2309.1854 | 236.7893 | 227.571 | 225.2044 | 220.4321 | 226.4476 | 203.9584 | 201.9054 | 216.2666
2383.1869 | 2310.1869 | 236.5086 | 227.4301 | 225.0688 | 220.2752 | 226.3292 | 203.833 | 201.8051 | 216.1088
2384.1883 | 2311.1883 | 236.2142 | 227.2902 | 224.9185 | 220.0985 | 226.2008 | 203.6971 | 201.712 | 215.9256
2385.1797 | 2312.1797 | 235.8551 | 227.1411 | 224.7707 | 219.9232 | 226.0678 | 203.5625 | 201.6046 | 215.7694
2386.1812 | 2313.1812 | 235.5525 | 227.0101 | 224.636 | 219.7284 | 225.9428 | 203.439 | 201.5098 | 215.5932
2387.1826 | 2314.1826 | 235.2328 | 226.872 | 224.4837 | 219.5303 | 225.8186 | 203.3199 | 201.4115 | 215.4254
2388.184 | 2315.184 | 234.8988 | 226.7353 | 224.3519 | 219.3479 | 225.6793 | 203.1812 | 201.3134 | 215.2502
2389.1855 | 2316.1855 | 234.6074 | 226.6079 | 224.2205 | 219.1729 | 225.5495 | 203.0505 | 201.2109 | 215.0777
2390.1769 | 2317.1769 | 234.3095 | 226.4715 | 224.0982 | 219.006 | 225.4228 | 202.9214 | 201.1169 | 214.9221
2391.1783 | 2318.1783 | 234.0364 | 226.349 | 223.9571 | 218.8236 | 225.2815 | 202.7904 | 201.0146 | 214.7452
2392.1798 | 2319.1798 | 233.7589 | 226.215 | 223.8165 | 218.6564 | 225.1507 | 202.6593 | 200.9177 | 214.5755
2393.1812 | 2320.1812 | 233.4756 | 226.0837 | 223.6656 | 218.4824 | 225.0224 | 202.536 | 200.8187 | 214.3996
2394.1827 | 2321.1827 | 233.1448 | 225.9494 | 223.5292 | 218.2936 | 224.8855 | 202.4065 | 200.7273 | 214.246
2395.1841 | 2322.1841 | 232.801 | 225.8081 | 223.3918 | 218.1086 | 224.7476 | 202.2805 | 200.6246 | 214.0517
2396.1855 | 2323.1855 | 232.4873 | 225.6746 | 223.2774 | 217.947 | 224.6091 | 202.1421 | 200.5191 | 213.8968
2397.187 | 2324.187 | 232.1941 | 225.5411 | 223.153 | 217.7894 | 224.473 | 202.0104 | 200.41 | 213.7151
2398.1784 | 2325.1784 | 231.8911 | 225.3966 | 223.0128 | 217.6397 | 224.3301 | 201.8766 | 200.3003 | 213.5559
2399.1799 | 2326.1799 | 231.5685 | 225.2672 | 222.8743 | 217.4812 | 224.195 | 201.7366 | 200.1855 | 213.3754
2400.1813 | 2327.1813 | 231.2096 | 225.1292 | 222.7387 | 217.2989 | 224.0642 | 201.6015 | 200.0757 | 213.2033
2401.1827 | 2328.1827 | 230.8588 | 224.9873 | 222.5943 | 217.1328 | 223.9332 | 201.454 | 199.9545 | 213.0103
2402.1842 | 2329.1842 | 230.4892 | 224.8444 | 222.4458 | 216.9534 | 223.7926 | 201.3252 | 199.8396 | 212.8617
2403.1856 | 2330.1856 | 230.1533 | 224.7072 | 222.2932 | 216.7267 | 223.6565 | 201.1771 | 199.7139 | 212.675
2404.1871 | 2331.1871 | 229.881 | 224.5639 | 222.1332 | 216.5586 | 223.5104 | 201.037 | 199.5959 | 212.5075
2405.1785 | 2332.1785 | 229.6113 | 224.4297 | 221.9637 | 216.3795 | 223.3605 | 200.8967 | 199.4885 | 212.3245
2406.1799 | 2333.1799 | 229.2834 | 224.2839 | 221.789 | 216.196 | 223.2352 | 200.7517 | 199.377 | 212.1383
2407.1814 | 2334.1814 | 228.9514 | 224.1436 | 221.6272 | 215.9966 | 223.0916 | 200.6043 | 199.2642 | 211.968
2408.1828 | 2335.1828 | 228.6932 | 224.014 | 221.4567 | 215.8105 | 222.9565 | 200.4613 | 199.1531 | 211.7949
2409.1842 | 2336.1842 | 228.2708 | 223.8658 | 221.3123 | 215.5917 | 222.82 | 200.315 | 199.048 | 211.6155
2410.1857 | 2337.1857 | 227.9163 | 223.7257 | 221.1856 | 215.3909 | 222.6718 | 200.1722 | 198.9379 | 211.4264
2411.1771 | 2338.1771 | 227.6164 | 223.582 | 221.0349 | 215.1439 | 222.5153 | 200.015 | 198.8205 | 211.2563
2412.1785 | 2339.1785 | 227.3672 | 223.438 | 220.8914 | 214.9483 | 222.3897 | 199.877 | 198.6958 | 211.088
2413.18 | 2340.18 | 227.1075 | 223.3109 | 220.7442 | 214.7224 | 222.2322 | 199.7334 | 198.5846 | 210.8874
2414.1814 | 2341.1814 | 226.8382 | 223.1636 | 220.587 | 214.5257 | 222.092 | 199.5891 | 198.4679 | 210.7289
2415.1829 | 2342.1829 | 226.5222 | 223.0237 | 220.4308 | 214.3272 | 221.9452 | 199.4233 | 198.3348 | 210.5362
2416.1843 | 2343.1843 | 226.1725 | 222.8851 | 220.3001 | 214.1046 | 221.809 | 199.2836 | 198.2277 | 210.3559
2417.1757 | 2344.1757 | 225.8429 | 222.7504 | 220.1418 | 213.917 | 221.6435 | 199.1345 | 198.1034 | 210.1673
2418.1772 | 2345.1772 | 225.5767 | 222.6146 | 220.0004 | 213.7123 | 221.5027 | 198.9865 | 197.9823 | 209.9753
2419.1786 | 2346.1786 | 225.2615 | 222.4759 | 219.8553 | 213.5365 | 221.3553 | 198.839 | 197.8563 | 209.7819
2420.18 | 2347.18 | 224.9122 | 222.343 | 219.7049 | 213.3747 | 221.198 | 198.6928 | 197.7379 | 209.6178
2421.1815 | 2348.1815 | 224.5781 | 222.1982 | 219.5576 | 213.1964 | 221.0514 | 198.5402 | 197.6182 | 209.4361
2422.1829 | 2349.1829 | 224.2595 | 222.0556 | 219.4001 | 212.9754 | 220.901 | 198.392 | 197.5032 | 209.2497
2423.1844 | 2350.1844 | 223.9668 | 221.9184 | 219.2667 | 212.7737 | 220.7556 | 198.2442 | 197.3794 | 209.0746
2424.1858 | 2351.1858 | 223.6743 | 221.7677 | 219.1178 | 212.5969 | 220.6127 | 198.0969 | 197.2625 | 208.8649
2425.1872 | 2352.1872 | 223.3677 | 221.6269 | 218.9633 | 212.3508 | 220.4474 | 197.9458 | 197.1521 | 208.6908
2426.1787 | 2353.1787 | 223.0438 | 221.4903 | 218.8038 | 212.1812 | 220.3029 | 197.796 | 197.0424 | 208.4978
2427.1801 | 2354.1801 | 222.7684 | 221.3393 | 218.6727 | 211.974 | 220.1615 | 197.6472 | 196.9344 | 208.3331
2428.1816 | 2355.1816 | 222.4588 | 221.1964 | 218.5091 | 211.7178 | 220.0222 | 197.5029 | 196.8392 | 208.1565
2429.183 | 2356.183 | 222.2004 | 221.0531 | 218.3541 | 211.539 | 219.8667 | 197.3535 | 196.7279 | 207.9689
2430.1844 | 2357.1844 | 221.9456 | 220.9037 | 218.1785 | 211.3487 | 219.7175 | 197.2028 | 196.6196 | 207.7725
2431.1859 | 2358.1859 | 221.6816 | 220.7623 | 218.0353 | 211.161 | 219.5718 | 197.0497 | 196.5063 | 207.6005
2432.1773 | 2359.1773 | 221.4397 | 220.6069 | 217.8754 | 210.9694 | 219.4273 | 196.8934 | 196.387 | 207.4198
2433.1787 | 2360.1787 | 221.1892 | 220.4597 | 217.7145 | 210.772 | 219.2686 | 196.7382 | 196.2784 | 207.2328
2434.1802 | 2361.1802 | 220.9419 | 220.3062 | 217.5548 | 210.5961 | 219.1143 | 196.5927 | 196.1627 | 207.0614
2435.1816 | 2362.1816 | 220.6098 | 220.1573 | 217.3979 | 210.4008 | 218.9606 | 196.4437 | 196.054 | 206.8691
2436.1831 | 2363.1831 | 220.2966 | 220.0044 | 217.2413 | 210.2032 | 218.8029 | 196.2872 | 195.9397 | 206.7141
2437.1845 | 2364.1845 | 220.0389 | 219.8406 | 217.0723 | 210.0343 | 218.6523 | 196.1434 | 195.8408 | 206.537
2438.1859 | 2365.1859 | 219.7451 | 219.6944 | 216.9159 | 209.8558 | 218.5138 | 195.9981 | 195.7281 | 206.357
2439.1874 | 2366.1874 | 219.4132 | 219.5281 | 216.7581 | 209.6521 | 218.3528 | 195.851 | 195.6149 | 206.1712
2440.1788 | 2367.1788 | 219.0927 | 219.3828 | 216.5874 | 209.4576 | 218.2148 | 195.7033 | 195.5092 | 205.983
2441.1802 | 2368.1802 | 218.8291 | 219.2283 | 216.4263 | 209.2814 | 218.0636 | 195.5621 | 195.4006 | 205.8087
2442.1817 | 2369.1817 | 218.5275 | 219.0697 | 216.2544 | 209.0863 | 217.9074 | 195.4174 | 195.2848 | 205.6207
2443.1831 | 2370.1831 | 218.2105 | 218.9017 | 216.0836 | 208.9107 | 217.765 | 195.274 | 195.1813 | 205.4426
2444.1846 | 2371.1846 | 217.8934 | 218.738 | 215.9199 | 208.7355 | 217.6089 | 195.1319 | 195.0661 | 205.2557
2445.186 | 2372.186 | 217.6144 | 218.5797 | 215.7629 | 208.5377 | 217.4705 | 194.9838 | 194.9526 | 205.0734
2446.1874 | 2373.1874 | 217.3055 | 218.4237 | 215.5987 | 208.3537 | 217.3265 | 194.8461 | 194.8502 | 204.899
2447.1789 | 2374.1789 | 217.0287 | 218.2731 | 215.4417 | 208.1692 | 217.1877 | 194.7024 | 194.7499 | 204.7124
2448.1803 | 2375.1803 | 216.7899 | 218.12 | 215.2827 | 207.9824 | 217.0275 | 194.5586 | 194.6314 | 204.546
2449.1818 | 2376.1818 | 216.5553 | 217.966 | 215.1171 | 207.8186 | 216.886 | 194.4167 | 194.5277 | 204.367
2450.1832 | 2377.1832 | 216.279 | 217.8145 | 214.9702 | 207.6464 | 216.7396 | 194.274 | 194.4183 | 204.1942
2451.1846 | 2378.1846 | 215.9873 | 217.6676 | 214.8108 | 207.4041 | 216.5966 | 194.1345 | 194.3037 | 204.004
2452.1861 | 2379.1861 | 215.6756 | 217.5187 | 214.6522 | 207.1951 | 216.4454 | 193.992 | 194.1805 | 203.8008
2453.1775 | 2380.1775 | 215.4092 | 217.3702 | 214.4974 | 206.9745 | 216.3123 | 193.8407 | 194.0664 | 203.619
2454.1789 | 2381.1789 | 215.1207 | 217.2179 | 214.3384 | 206.7469 | 216.1504 | 193.6964 | 193.9443 | 203.4513
2455.1804 | 2382.1804 | 214.9186 | 217.0718 | 214.1768 | 206.5561 | 216.0098 | 193.5671 | 193.8238 | 203.2443
2456.1818 | 2383.1818 | 214.7334 | 216.9153 | 214.0155 | 206.3772 | 215.856 | 193.4212 | 193.6959 | 203.0699
2457.1833 | 2384.1833 | 214.5566 | 216.7656 | 213.8495 | 206.1754 | 215.7013 | 193.2802 | 193.5775 | 202.885
2458.1847 | 2385.1847 | 214.358 | 216.6068 | 213.6848 | 206.0099 | 215.546 | 193.1469 | 193.4404 | 202.7002
2459.1861 | 2386.1861 | 214.1762 | 216.4524 | 213.5298 | 205.8448 | 215.3978 | 193.0011 | 193.3175 | 202.5186
2460.1776 | 2387.1776 | 213.969 | 216.2983 | 213.3664 | 205.6855 | 215.2377 | 192.8649 | 193.1932 | 202.3416
2461.179 | 2388.179 | 213.7092 | 216.1369 | 213.1961 | 205.5256 | 215.0872 | 192.7267 | 193.0691 | 202.1528
2462.1804 | 2389.1804 | 213.4181 | 215.9909 | 213.0413 | 205.3447 | 214.9318 | 192.5921 | 192.9417 | 201.9744
2463.1819 | 2390.1819 | 213.1046 | 215.8359 | 212.8888 | 205.1705 | 214.782 | 192.4579 | 192.8142 | 201.7822
2464.1833 | 2391.1833 | 212.7962 | 215.6883 | 212.7236 | 205.0076 | 214.6369 | 192.3185 | 192.6957 | 201.5936
2465.1848 | 2392.1848 | 212.4991 | 215.5328 | 212.5623 | 204.8596 | 214.4888 | 192.19 | 192.5646 | 201.4382
2466.1762 | 2393.1762 | 212.2371 | 215.3848 | 212.4034 | 204.704 | 214.3479 | 192.048 | 192.4334 | 201.2521
2467.1876 | 2394.1876 | 211.969 | 215.2341 | 212.2347 | 204.545 | 214.1898 | 191.9027 | 192.3045 | 201.0719
2468.1891 | 2395.1891 | 211.707 | 215.0968 | 212.0936 | 204.3852 | 214.0365 | 191.7686 | 192.1795 | 200.8912
2469.1805 | 2396.1805 | 211.3987 | 214.9431 | 211.9291 | 204.2193 | 213.8972 | 191.6326 | 192.0492 | 200.7173
2470.1819 | 2397.1819 | 211.1163 | 214.7947 | 211.7658 | 204.0315 | 213.7369 | 191.4905 | 191.9234 | 200.5087
2471.1834 | 2398.1834 | 210.9004 | 214.6429 | 211.6153 | 203.8573 | 213.583 | 191.3598 | 191.8039 | 200.3502
2472.1848 | 2399.1848 | 210.7279 | 214.4815 | 211.4386 | 203.6744 | 213.4321 | 191.2232 | 191.6689 | 200.173
2473.1863 | 2400.1863 | 210.5387 | 214.3326 | 211.2765 | 203.4853 | 213.2832 | 191.0827 | 191.5397 | 199.9725
2474.1777 | 2401.1777 | 210.3745 | 214.1685 | 211.1346 | 203.3007 | 213.1253 | 190.9435 | 191.4048 | 199.8043
2475.1791 | 2402.1791 | 210.1795 | 214.0193 | 210.9738 | 203.1403 | 212.9755 | 190.8142 | 191.2757 | 199.6351
2476.1806 | 2403.1806 | 209.8931 | 213.8579 | 210.8039 | 202.9595 | 212.821 | 190.6837 | 191.1452 | 199.4593
2477.182 | 2404.182 | 209.5565 | 213.7073 | 210.6462 | 202.7972 | 212.6717 | 190.5465 | 191.0214 | 199.2507

## C6-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38909.4325 | 1 | 0 | 38909.4326 | 1 | 0 | -16 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4332 | 1 | 0 | 38909.4333 | 1 | 0 | 43 | 116 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4339 | 1 | 0 | 38909.4339 | 1 | 0 | 101.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4346 | 1 | 0 | 38909.4346 | 1 | 0 | 160.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4353 | 1 | 0 | 38909.4353 | 1 | 0 | 219.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4359 | 1 | 0 | 38909.436 | 1 | 0 | 278 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4366 | 1 | 0 | 38909.4367 | 1 | 0 | 337 | 410 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4373 | 1 | 0 | 38909.4373 | 1 | 0 | 395.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.438 | 1 | 0 | 38909.438 | 1 | 0 | 454.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4387 | 1 | 0 | 38909.4387 | 1 | 0 | 513 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4394 | 1 | 0 | 38909.4394 | 1 | 0 | 572 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.44 | 1 | 0 | 38909.4401 | 1 | 0 | 631 | 704 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4407 | 1 | 0 | 38909.4407 | 1 | 0 | 689.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4414 | 1 | 0 | 38909.4414 | 1 | 0 | 748.5 | 821.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4421 | 1 | 0 | 38909.4421 | 1 | 0 | 807.5 | 880.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4428 | 1 | 0 | 38909.4428 | 1 | 0 | 866 | 939 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4434 | 1 | 0 | 38909.4434 | 1 | 0 | 924.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4441 | 1 | 0 | 38909.4441 | 1 | 0 | 983.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4448 | 1 | 0 | 38909.4448 | 1 | 0 | 1042.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4455 | 1 | 0 | 38909.4455 | 1 | 0 | 1101 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4462 | 1 | 0 | 38909.4462 | 1 | 0 | 1160 | 1233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4468 | 1 | 0 | 38909.4469 | 1 | 0 | 1218.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4475 | 1 | 0 | 38909.4475 | 1 | 0 | 1277.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4482 | 1 | 0 | 38909.4482 | 1 | 0 | 1336.5 | 1409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4489 | 1 | 0 | 38909.4489 | 1 | 0 | 1395 | 1468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4496 | 1 | 0 | 38909.4496 | 1 | 0 | 1454 | 1527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4502 | 1 | 0 | 38909.4503 | 1 | 0 | 1512.5 | 1585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4509 | 1 | 0 | 38909.4509 | 1 | 0 | 1571.5 | 1644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4516 | 1 | 0 | 38909.4516 | 1 | 0 | 1630.5 | 1703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4523 | 1 | 0 | 38909.4523 | 1 | 0 | 1689 | 1762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.453 | 1 | 0 | 38909.453 | 1 | 0 | 1747.5 | 1820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4536 | 1 | 0 | 38909.4537 | 1 | 0 | 1806.5 | 1879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4543 | 1 | 0 | 38909.4543 | 1 | 0 | 1865.5 | 1938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.455 | 1 | 0 | 38909.455 | 1 | 0 | 1924.5 | 1997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4557 | 1 | 0 | 38909.4557 | 1 | 0 | 1983 | 2056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4564 | 1 | 0 | 38909.4564 | 1 | 0 | 2042 | 2115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.457 | 1 | 0 | 38909.4571 | 1 | 0 | 2100.5 | 2173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4577 | 1 | 0 | 38909.4577 | 1 | 0 | 2159.5 | 2232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4584 | 1 | 0 | 38909.4584 | 1 | 0 | 2218 | 2291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4591 | 1 | 0 | 38909.4591 | 1 | 0 | 2277 | 2350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4598 | 1 | 0 | 38909.4598 | 1 | 0 | 2335.5 | 2408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4605 | 1 | 0 | 38909.4605 | 1 | 0 | 2394.5 | 2467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C5-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38909.4325 | 1 | 0 | 38909.4325 | 1 | 0 | -18.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4332 | 1 | 0 | 38909.4332 | 1 | 0 | 40 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4339 | 1 | 0 | 38909.4339 | 1 | 0 | 99 | 172 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4346 | 1 | 0 | 38909.4346 | 1 | 0 | 157.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4352 | 1 | 0 | 38909.4353 | 1 | 0 | 216.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4359 | 1 | 0 | 38909.4359 | 1 | 0 | 275 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4366 | 1 | 0 | 38909.4366 | 2 | 1 | 334 | 407 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4373 | 1 | 0 | 38909.4373 | 1 | 0 | 392.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.438 | 1 | 0 | 38909.438 | 1 | 0 | 451.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4386 | 1 | 0 | 38909.4387 | 1 | 0 | 510.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4393 | 1 | 0 | 38909.4393 | 1 | 0 | 569.5 | 642.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.44 | 1 | 0 | 38909.44 | 1 | 0 | 628 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4407 | 1 | 0 | 38909.4407 | 1 | 0 | 687 | 760 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4414 | 1 | 0 | 38909.4414 | 1 | 0 | 745.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.442 | 1 | 0 | 38909.4421 | 1 | 0 | 804.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4427 | 1 | 0 | 38909.4427 | 1 | 0 | 863.5 | 936.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4434 | 1 | 0 | 38909.4434 | 1 | 0 | 922 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4441 | 1 | 0 | 38909.4441 | 1 | 0 | 981 | 1054 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4448 | 1 | 0 | 38909.4448 | 1 | 0 | 1039.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4455 | 1 | 0 | 38909.4455 | 1 | 0 | 1098.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4461 | 1 | 0 | 38909.4461 | 1 | 0 | 1157 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4468 | 1 | 0 | 38909.4468 | 1 | 0 | 1216 | 1289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4475 | 1 | 0 | 38909.4475 | 1 | 0 | 1274.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4482 | 1 | 0 | 38909.4482 | 1 | 0 | 1333.5 | 1406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4489 | 1 | 0 | 38909.4489 | 1 | 0 | 1392.5 | 1465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4495 | 1 | 0 | 38909.4495 | 1 | 0 | 1451 | 1524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4502 | 1 | 0 | 38909.4502 | 1 | 0 | 1510 | 1583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4509 | 1 | 0 | 38909.4509 | 1 | 0 | 1568.5 | 1641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4516 | 1 | 0 | 38909.4516 | 1 | 0 | 1627.5 | 1700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4522 | 1 | 0 | 38909.4523 | 1 | 0 | 1686 | 1759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4529 | 1 | 0 | 38909.453 | 1 | 0 | 1745 | 1818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4536 | 1 | 0 | 38909.4536 | 1 | 0 | 1803.5 | 1876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4543 | 1 | 0 | 38909.4543 | 1 | 0 | 1862.5 | 1935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.455 | 1 | 0 | 38909.455 | 1 | 0 | 1921.5 | 1994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4557 | 1 | 0 | 38909.4557 | 1 | 0 | 1980.5 | 2053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4563 | 1 | 0 | 38909.4564 | 1 | 0 | 2039 | 2112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.457 | 1 | 0 | 38909.457 | 1 | 0 | 2098 | 2171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4577 | 1 | 0 | 38909.4577 | 1 | 0 | 2156.5 | 2229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4584 | 1 | 0 | 38909.4584 | 1 | 0 | 2215.5 | 2288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4591 | 1 | 0 | 38909.4591 | 1 | 0 | 2274 | 2347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4597 | 1 | 0 | 38909.4598 | 1 | 0 | 2333 | 2406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4604 | 1 | 0 | 38909.4604 | 1 | 0 | 2391.5 | 2464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C5-6
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38909.4325 | 1 | 0 | 38909.4325 | 1 | 0 | -21.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4332 | 1 | 0 | 38909.4332 | 1 | 0 | 37.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4338 | 1 | 0 | 38909.4339 | 1 | 0 | 96 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4345 | 1 | 0 | 38909.4345 | 1 | 0 | 155 | 228 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4352 | 1 | 0 | 38909.4352 | 1 | 0 | 213.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4359 | 1 | 0 | 38909.4359 | 1 | 0 | 272.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4366 | 1 | 0 | 38909.4366 | 1 | 0 | 331.5 | 404.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4372 | 1 | 0 | 38909.4373 | 1 | 0 | 390 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4379 | 1 | 0 | 38909.4379 | 1 | 0 | 448.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4386 | 1 | 0 | 38909.4386 | 1 | 0 | 507.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4393 | 1 | 0 | 38909.4393 | 1 | 0 | 566.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.44 | 1 | 0 | 38909.44 | 1 | 0 | 625.5 | 698.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4406 | 1 | 0 | 38909.4407 | 1 | 0 | 684 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4413 | 1 | 0 | 38909.4413 | 1 | 0 | 742.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.442 | 1 | 0 | 38909.442 | 1 | 0 | 801.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4427 | 1 | 0 | 38909.4427 | 1 | 0 | 860.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4434 | 1 | 0 | 38909.4434 | 1 | 0 | 919.5 | 992.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4441 | 1 | 0 | 38909.4441 | 1 | 0 | 978 | 1051 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4447 | 1 | 0 | 38909.4447 | 1 | 0 | 1036.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4454 | 1 | 0 | 38909.4454 | 1 | 0 | 1095.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4461 | 1 | 0 | 38909.4461 | 1 | 0 | 1154.5 | 1227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4468 | 1 | 0 | 38909.4468 | 1 | 0 | 1213 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4475 | 1 | 0 | 38909.4475 | 1 | 0 | 1272 | 1345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4481 | 1 | 0 | 38909.4481 | 1 | 0 | 1330.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4488 | 1 | 0 | 38909.4488 | 1 | 0 | 1389.5 | 1462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4495 | 1 | 0 | 38909.4495 | 1 | 0 | 1448.5 | 1521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4502 | 1 | 0 | 38909.4502 | 1 | 0 | 1507 | 1580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4509 | 1 | 0 | 38909.4509 | 1 | 0 | 1566 | 1639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4515 | 1 | 0 | 38909.4516 | 1 | 0 | 1624.5 | 1697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4522 | 1 | 0 | 38909.4522 | 1 | 0 | 1683.5 | 1756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4529 | 1 | 0 | 38909.4529 | 1 | 0 | 1742.5 | 1815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4536 | 1 | 0 | 38909.4536 | 1 | 0 | 1801 | 1874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4543 | 1 | 0 | 38909.4543 | 1 | 0 | 1860 | 1933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4549 | 1 | 0 | 38909.455 | 1 | 0 | 1918.5 | 1991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4556 | 1 | 0 | 38909.4556 | 1 | 0 | 1977.5 | 2050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4563 | 1 | 0 | 38909.4563 | 1 | 0 | 2036 | 2109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.457 | 1 | 0 | 38909.457 | 1 | 0 | 2095 | 2168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4577 | 1 | 0 | 38909.4577 | 1 | 0 | 2154 | 2227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4583 | 1 | 0 | 38909.4584 | 1 | 0 | 2212.5 | 2285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.459 | 1 | 0 | 38909.459 | 1 | 0 | 2271.5 | 2344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4597 | 1 | 0 | 38909.4597 | 1 | 0 | 2330 | 2403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4604 | 1 | 0 | 38909.4604 | 1 | 0 | 2389 | 2462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38909.4325 | 1 | 0 | 38909.4325 | 1 | 0 | -24.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4331 | 1 | 0 | 38909.4331 | 1 | 0 | 34.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4338 | 1 | 0 | 38909.4338 | 1 | 0 | 93.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4345 | 1 | 0 | 38909.4345 | 1 | 0 | 152 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4352 | 1 | 0 | 38909.4352 | 1 | 0 | 211 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4359 | 1 | 0 | 38909.4359 | 1 | 0 | 269.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4365 | 1 | 0 | 38909.4366 | 1 | 0 | 328.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4372 | 1 | 0 | 38909.4372 | 1 | 0 | 387.5 | 460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4379 | 1 | 0 | 38909.4379 | 1 | 0 | 446 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4386 | 1 | 0 | 38909.4386 | 1 | 0 | 505 | 578 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4393 | 1 | 0 | 38909.4393 | 1 | 0 | 563.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4399 | 1 | 0 | 38909.44 | 1 | 0 | 622.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4406 | 1 | 0 | 38909.4406 | 1 | 0 | 681 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4413 | 1 | 0 | 38909.4413 | 1 | 0 | 740 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.442 | 1 | 0 | 38909.442 | 1 | 0 | 798.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4427 | 1 | 0 | 38909.4427 | 1 | 0 | 857.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4433 | 1 | 0 | 38909.4434 | 1 | 0 | 916.5 | 989.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.444 | 1 | 0 | 38909.444 | 1 | 0 | 975 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4447 | 1 | 0 | 38909.4447 | 1 | 0 | 1034 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4454 | 1 | 0 | 38909.4454 | 1 | 0 | 1092.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4461 | 1 | 0 | 38909.4461 | 1 | 0 | 1151.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4467 | 1 | 0 | 38909.4468 | 1 | 0 | 1210.5 | 1283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4474 | 1 | 0 | 38909.4474 | 1 | 0 | 1269 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4481 | 1 | 0 | 38909.4481 | 1 | 0 | 1328 | 1401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4488 | 1 | 0 | 38909.4488 | 1 | 0 | 1386.5 | 1459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4495 | 1 | 0 | 38909.4495 | 1 | 0 | 1445.5 | 1518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4502 | 1 | 0 | 38909.4502 | 1 | 0 | 1504.5 | 1577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4508 | 1 | 0 | 38909.4508 | 1 | 0 | 1563 | 1636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4515 | 1 | 0 | 38909.4515 | 1 | 0 | 1622 | 1695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4522 | 1 | 1 | 38909.4522 | 1 | 0 | 1680.5 | 1753.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4529 | 1 | 0 | 38909.4529 | 1 | 0 | 1739.5 | 1812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4536 | 1 | 0 | 38909.4536 | 1 | 0 | 1798.5 | 1871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4542 | 1 | 0 | 38909.4542 | 1 | 0 | 1857 | 1930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4549 | 1 | 0 | 38909.4549 | 1 | 0 | 1915.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4556 | 1 | 0 | 38909.4556 | 1 | 0 | 1974.5 | 2047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4563 | 1 | 0 | 38909.4563 | 1 | 0 | 2033.5 | 2106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4569 | 1 | 0 | 38909.457 | 1 | 0 | 2092 | 2165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4576 | 1 | 0 | 38909.4577 | 1 | 0 | 2151 | 2224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4583 | 1 | 0 | 38909.4583 | 1 | 0 | 2209.5 | 2282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.459 | 1 | 0 | 38909.459 | 1 | 0 | 2268.5 | 2341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4597 | 1 | 0 | 38909.4597 | 1 | 0 | 2327.5 | 2400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4603 | 1 | 0 | 38909.4604 | 1 | 0 | 2386 | 2459 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-6
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38909.4324 | 1 | 0 | 38909.4324 | 1 | 0 | -27 | 46 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4331 | 1 | 0 | 38909.4331 | 1 | 0 | 31.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4338 | 1 | 0 | 38909.4338 | 1 | 0 | 90.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4345 | 1 | 0 | 38909.4345 | 1 | 0 | 149.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4351 | 1 | 0 | 38909.4352 | 1 | 0 | 208 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4358 | 1 | 0 | 38909.4358 | 1 | 0 | 267 | 340 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4365 | 1 | 0 | 38909.4365 | 1 | 0 | 325.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4372 | 1 | 0 | 38909.4372 | 1 | 0 | 384.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4379 | 1 | 0 | 38909.4379 | 1 | 0 | 443.5 | 516.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4385 | 1 | 0 | 38909.4386 | 1 | 0 | 502 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4392 | 1 | 0 | 38909.4392 | 1 | 0 | 560.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4399 | 1 | 0 | 38909.4399 | 1 | 0 | 619.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4406 | 1 | 0 | 38909.4406 | 1 | 0 | 678.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4413 | 1 | 0 | 38909.4413 | 1 | 0 | 737.5 | 810.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4419 | 1 | 0 | 38909.442 | 1 | 0 | 796 | 869 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4426 | 1 | 0 | 38909.4426 | 1 | 0 | 854.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4433 | 1 | 0 | 38909.4433 | 1 | 0 | 913.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.444 | 1 | 0 | 38909.444 | 1 | 0 | 972.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4447 | 1 | 0 | 38909.4447 | 1 | 0 | 1031 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4453 | 1 | 0 | 38909.4454 | 1 | 0 | 1090 | 1163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.446 | 1 | 0 | 38909.446 | 1 | 0 | 1148.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4467 | 1 | 0 | 38909.4467 | 1 | 0 | 1207.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4474 | 1 | 0 | 38909.4474 | 1 | 0 | 1266.5 | 1339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4481 | 1 | 0 | 38909.4481 | 1 | 0 | 1325 | 1398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4488 | 1 | 0 | 38909.4488 | 1 | 0 | 1384 | 1457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4494 | 1 | 0 | 38909.4494 | 1 | 0 | 1442.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4501 | 1 | 0 | 38909.4501 | 1 | 0 | 1501.5 | 1574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4508 | 1 | 0 | 38909.4508 | 1 | 0 | 1560.5 | 1633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4515 | 1 | 0 | 38909.4515 | 1 | 0 | 1619 | 1692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4522 | 1 | 1 | 38909.4522 | 1 | 0 | 1678 | 1751 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4528 | 1 | 0 | 38909.4528 | 1 | 0 | 1736.5 | 1809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4535 | 1 | 0 | 38909.4535 | 1 | 0 | 1795.5 | 1868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4542 | 1 | 0 | 38909.4542 | 1 | 0 | 1854.5 | 1927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4549 | 1 | 0 | 38909.4549 | 1 | 0 | 1913 | 1986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4556 | 1 | 0 | 38909.4556 | 1 | 0 | 1971.5 | 2044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4562 | 1 | 0 | 38909.4563 | 1 | 0 | 2030.5 | 2103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4569 | 1 | 0 | 38909.4569 | 1 | 0 | 2089.5 | 2162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4576 | 1 | 0 | 38909.4576 | 1 | 0 | 2148 | 2221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4583 | 1 | 0 | 38909.4583 | 1 | 0 | 2207 | 2280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.459 | 1 | 0 | 38909.459 | 1 | 0 | 2265.5 | 2338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4596 | 1 | 0 | 38909.4597 | 1 | 0 | 2324.5 | 2397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4603 | 1 | 0 | 38909.4603 | 1 | 0 | 2383.5 | 2456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-5
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38909.4324 | 1 | 0 | 38909.4324 | 1 | 0 | -30 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4331 | 1 | 0 | 38909.4331 | 1 | 0 | 29 | 102 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4337 | 1 | 0 | 38909.4338 | 1 | 0 | 87.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4344 | 1 | 0 | 38909.4344 | 1 | 0 | 146.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4351 | 1 | 0 | 38909.4351 | 1 | 0 | 205.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4358 | 1 | 0 | 38909.4358 | 1 | 0 | 264 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4365 | 1 | 0 | 38909.4365 | 1 | 0 | 323 | 396 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4372 | 1 | 0 | 38909.4372 | 1 | 0 | 381.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4378 | 1 | 0 | 38909.4378 | 1 | 0 | 440.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4385 | 1 | 0 | 38909.4385 | 1 | 0 | 499 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4392 | 1 | 0 | 38909.4392 | 1 | 0 | 558 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4399 | 1 | 0 | 38909.4399 | 1 | 0 | 616.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4406 | 1 | 0 | 38909.4406 | 1 | 0 | 675.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4412 | 1 | 0 | 38909.4413 | 1 | 0 | 734.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4419 | 1 | 0 | 38909.4419 | 1 | 0 | 793 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4426 | 1 | 0 | 38909.4426 | 1 | 0 | 852 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4433 | 1 | 0 | 38909.4433 | 1 | 0 | 910.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.444 | 1 | 0 | 38909.444 | 1 | 0 | 969.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4446 | 1 | 0 | 38909.4447 | 1 | 0 | 1028.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4453 | 1 | 0 | 38909.4453 | 1 | 0 | 1087 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.446 | 1 | 0 | 38909.446 | 1 | 0 | 1146 | 1219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4467 | 1 | 0 | 38909.4467 | 1 | 0 | 1204.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4474 | 1 | 0 | 38909.4474 | 1 | 0 | 1263.5 | 1336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.448 | 1 | 0 | 38909.4481 | 1 | 0 | 1322.5 | 1395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4487 | 1 | 0 | 38909.4487 | 1 | 0 | 1381 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4494 | 1 | 0 | 38909.4494 | 1 | 0 | 1440 | 1513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4501 | 1 | 0 | 38909.4501 | 1 | 0 | 1498.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4508 | 1 | 0 | 38909.4508 | 1 | 0 | 1557.5 | 1630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4514 | 1 | 0 | 38909.4515 | 1 | 0 | 1616.5 | 1689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4521 | 1 | 0 | 38909.4521 | 1 | 0 | 1675 | 1748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4528 | 1 | 0 | 38909.4528 | 1 | 0 | 1734 | 1807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4535 | 1 | 0 | 38909.4535 | 1 | 0 | 1792.5 | 1865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4542 | 1 | 0 | 38909.4542 | 1 | 0 | 1851.5 | 1924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4548 | 1 | 0 | 38909.4549 | 1 | 0 | 1910.5 | 1983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4555 | 1 | 0 | 38909.4555 | 1 | 0 | 1969 | 2042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4562 | 1 | 0 | 38909.4562 | 1 | 0 | 2027.5 | 2100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4569 | 1 | 0 | 38909.4569 | 1 | 0 | 2086.5 | 2159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4576 | 1 | 0 | 38909.4576 | 1 | 0 | 2145.5 | 2218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4582 | 1 | 0 | 38909.4583 | 1 | 0 | 2204 | 2277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4589 | 1 | 0 | 38909.4589 | 1 | 0 | 2263 | 2336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4596 | 1 | 0 | 38909.4596 | 1 | 0 | 2321.5 | 2394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4603 | 1 | 0 | 38909.4603 | 1 | 0 | 2380.5 | 2453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38909.4324 | 1 | 0 | 38909.4324 | 1 | 0 | -32.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.433 | 1 | 0 | 38909.4331 | 1 | 0 | 26 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4337 | 1 | 0 | 38909.4337 | 1 | 0 | 85 | 158 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4344 | 1 | 0 | 38909.4344 | 1 | 0 | 143.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4351 | 1 | 0 | 38909.4351 | 1 | 0 | 202.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4358 | 1 | 0 | 38909.4358 | 1 | 0 | 261.5 | 334.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4364 | 2 | 0 | 38909.4365 | 1 | 0 | 320 | 393 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38909.4371 | 1 | 0 | 38909.4371 | 1 | 0 | 379 | 452 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4378 | 1 | 0 | 38909.4378 | 1 | 0 | 437.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4385 | 1 | 0 | 38909.4385 | 1 | 0 | 496.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4392 | 1 | 0 | 38909.4392 | 1 | 0 | 555 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4398 | 1 | 0 | 38909.4399 | 1 | 0 | 614 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4405 | 1 | 0 | 38909.4405 | 1 | 0 | 672.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4412 | 1 | 0 | 38909.4412 | 1 | 0 | 731.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4419 | 1 | 0 | 38909.4419 | 1 | 0 | 790.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4426 | 1 | 0 | 38909.4426 | 1 | 0 | 849 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4432 | 1 | 0 | 38909.4433 | 1 | 0 | 908 | 981 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4439 | 1 | 0 | 38909.4439 | 1 | 0 | 966.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4446 | 1 | 0 | 38909.4446 | 1 | 0 | 1025.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4453 | 1 | 0 | 38909.4453 | 1 | 0 | 1084.5 | 1157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.446 | 1 | 0 | 38909.446 | 1 | 0 | 1143 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4466 | 1 | 0 | 38909.4467 | 1 | 0 | 1202 | 1275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4473 | 1 | 0 | 38909.4473 | 1 | 0 | 1260.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.448 | 1 | 0 | 38909.448 | 1 | 0 | 1319.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4487 | 1 | 0 | 38909.4487 | 1 | 0 | 1378.5 | 1451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4494 | 1 | 0 | 38909.4494 | 1 | 0 | 1437 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.45 | 1 | 0 | 38909.4501 | 1 | 0 | 1496 | 1569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4507 | 1 | 1 | 38909.4507 | 1 | 0 | 1554.5 | 1627.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4514 | 1 | 0 | 38909.4514 | 1 | 0 | 1613.5 | 1686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4521 | 1 | 0 | 38909.4521 | 1 | 0 | 1672.5 | 1745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4528 | 1 | 0 | 38909.4528 | 1 | 0 | 1731 | 1804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4534 | 1 | 1 | 38909.4535 | 1 | 0 | 1790 | 1863 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4541 | 1 | 0 | 38909.4541 | 1 | 0 | 1848.5 | 1921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4548 | 1 | 0 | 38909.4548 | 1 | 0 | 1907.5 | 1980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4555 | 1 | 0 | 38909.4555 | 1 | 0 | 1966.5 | 2039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4562 | 1 | 0 | 38909.4562 | 1 | 0 | 2025 | 2098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4569 | 1 | 0 | 38909.4569 | 1 | 0 | 2084 | 2157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4575 | 1 | 0 | 38909.4575 | 1 | 0 | 2142.5 | 2215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4582 | 1 | 0 | 38909.4582 | 1 | 0 | 2201.5 | 2274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4589 | 1 | 0 | 38909.4589 | 1 | 0 | 2260 | 2333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4596 | 1 | 0 | 38909.4596 | 1 | 0 | 2319 | 2392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4603 | 1271 | 0 | 38909.4603 | 2 | 0 | 2377.5 | 2450.5 | 77.5946 | 0 | 0.1221 | 0 | 0.77595 | 0 | 0.001221 | 0 | 0.77595 | 0.001221 | 66.2486 | 105551 | 65.4727

## C3-6
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38909.4323 | 1 | 0 | 38909.4323 | 1 | 0 | -35.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.433 | 1 | 0 | 38909.433 | 1 | 0 | 23.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4337 | 1 | 0 | 38909.4337 | 1 | 0 | 82 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4344 | 1 | 0 | 38909.4344 | 1 | 0 | 141 | 214 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.435 | 1 | 0 | 38909.4351 | 1 | 0 | 199.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4357 | 1 | 0 | 38909.4357 | 1 | 0 | 258.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4364 | 1 | 0 | 38909.4364 | 1 | 0 | 317.5 | 390.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4371 | 1 | 0 | 38909.4371 | 1 | 0 | 376 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38909.4378 | 1 | 0 | 435 | 508 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4384 | 1 | 0 | 38909.4385 | 1 | 0 | 493.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4391 | 1 | 0 | 38909.4391 | 1 | 0 | 552.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4398 | 1 | 0 | 38909.4398 | 1 | 0 | 611 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4405 | 1 | 0 | 38909.4405 | 1 | 0 | 670 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4412 | 1 | 0 | 38909.4412 | 1 | 0 | 728.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4419 | 1 | 0 | 38909.4419 | 1 | 0 | 787.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4425 | 1 | 0 | 38909.4425 | 1 | 0 | 846.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4432 | 1 | 0 | 38909.4432 | 1 | 0 | 905 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4439 | 1 | 0 | 38909.4439 | 1 | 0 | 964 | 1037 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4446 | 1 | 0 | 38909.4446 | 1 | 0 | 1022.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4453 | 1 | 0 | 38909.4453 | 1 | 0 | 1081.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4459 | 1 | 0 | 38909.4459 | 1 | 0 | 1140.5 | 1213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4466 | 1 | 0 | 38909.4466 | 1 | 0 | 1199 | 1272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4473 | 1 | 0 | 38909.4473 | 1 | 0 | 1258 | 1331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.448 | 1 | 0 | 38909.448 | 1 | 0 | 1316.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4487 | 1 | 0 | 38909.4487 | 1 | 0 | 1375.5 | 1448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4493 | 1 | 0 | 38909.4494 | 1 | 0 | 1434.5 | 1507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.45 | 1 | 0 | 38909.45 | 1 | 0 | 1493 | 1566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4507 | 1 | 0 | 38909.4507 | 1 | 0 | 1552 | 1625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4514 | 1 | 1 | 38909.4514 | 1 | 0 | 1610.5 | 1683.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4521 | 1 | 1 | 38909.4521 | 1 | 0 | 1669.5 | 1742.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4527 | 1 | 0 | 38909.4528 | 1 | 0 | 1728.5 | 1801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4534 | 1 | 0 | 38909.4534 | 1 | 0 | 1787 | 1860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4541 | 1 | 0 | 38909.4541 | 1 | 0 | 1845.5 | 1918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4548 | 1 | 0 | 38909.4548 | 1 | 0 | 1904.5 | 1977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4555 | 1 | 0 | 38909.4555 | 1 | 0 | 1963.5 | 2036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4561 | 1 | 0 | 38909.4562 | 1 | 0 | 2022.5 | 2095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4568 | 1 | 0 | 38909.4568 | 1 | 0 | 2081 | 2154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4575 | 1 | 0 | 38909.4575 | 1 | 0 | 2139.5 | 2212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4582 | 1 | 0 | 38909.4582 | 1 | 0 | 2198.5 | 2271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4589 | 1 | 0 | 38909.4589 | 1 | 0 | 2257.5 | 2330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4595 | 1 | 0 | 38909.4596 | 1 | 0 | 2316.5 | 2389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4602 | 1 | 0 | 38909.4602 | 1 | 0 | 2375 | 2448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-5
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38909.4323 | 1 | 0 | 38909.4323 | 1 | 0 | -38.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.433 | 1 | 0 | 38909.433 | 1 | 0 | 20.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4337 | 1 | 0 | 38909.4337 | 1 | 0 | 79.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4343 | 1 | 0 | 38909.4344 | 1 | 0 | 138 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.435 | 1 | 0 | 38909.435 | 1 | 0 | 197 | 270 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4357 | 1 | 0 | 38909.4357 | 1 | 0 | 255.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4364 | 1 | 0 | 38909.4364 | 1 | 0 | 314.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4371 | 1 | 0 | 38909.4371 | 1 | 0 | 373.5 | 446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4377 | 1 | 0 | 38909.4378 | 1 | 0 | 432 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4384 | 1 | 0 | 38909.4384 | 1 | 0 | 491 | 564 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4391 | 1 | 0 | 38909.4391 | 1 | 0 | 549.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4398 | 1 | 0 | 38909.4398 | 1 | 0 | 608.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4405 | 1 | 0 | 38909.4405 | 1 | 0 | 667 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4411 | 1 | 0 | 38909.4412 | 1 | 0 | 726 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4418 | 1 | 0 | 38909.4418 | 1 | 0 | 785 | 858 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4425 | 1 | 0 | 38909.4425 | 1 | 0 | 843.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4432 | 2 | 0 | 38909.4432 | 1 | 0 | 902.5 | 975.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38909.4439 | 1 | 0 | 38909.4439 | 1 | 0 | 961 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4445 | 1 | 0 | 38909.4446 | 1 | 0 | 1020 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4452 | 1 | 0 | 38909.4452 | 1 | 0 | 1078.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4459 | 1 | 0 | 38909.4459 | 1 | 0 | 1137.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4466 | 1 | 0 | 38909.4466 | 1 | 0 | 1196.5 | 1269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4473 | 1 | 0 | 38909.4473 | 1 | 0 | 1255 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4479 | 1 | 0 | 38909.448 | 1 | 0 | 1314 | 1387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4486 | 1 | 0 | 38909.4486 | 1 | 0 | 1372.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4493 | 1 | 0 | 38909.4493 | 1 | 0 | 1431.5 | 1504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.45 | 1 | 0 | 38909.45 | 1 | 0 | 1490.5 | 1563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4507 | 1 | 1 | 38909.4507 | 1 | 0 | 1549 | 1622 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4513 | 1 | 0 | 38909.4514 | 1 | 0 | 1608 | 1681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.452 | 1 | 0 | 38909.452 | 1 | 0 | 1666.5 | 1739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4527 | 1 | 0 | 38909.4527 | 1 | 0 | 1725.5 | 1798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4534 | 1 | 0 | 38909.4534 | 2 | 0 | 1784.5 | 1857.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38909.4541 | 1 | 0 | 38909.4541 | 1 | 0 | 1843 | 1916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4547 | 1 | 0 | 38909.4548 | 1 | 0 | 1901.5 | 1974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4554 | 1 | 0 | 38909.4554 | 1 | 0 | 1960.5 | 2033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4561 | 1 | 1 | 38909.4561 | 1 | 0 | 2019.5 | 2092.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4568 | 1 | 0 | 38909.4568 | 1 | 0 | 2078 | 2151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4575 | 1 | 0 | 38909.4575 | 1 | 0 | 2137 | 2210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4581 | 1 | 0 | 38909.4582 | 1 | 0 | 2195.5 | 2268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4588 | 1 | 0 | 38909.4588 | 1 | 0 | 2254.5 | 2327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4595 | 1 | 0 | 38909.4595 | 1 | 0 | 2313.5 | 2386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4602 | 1 | 0 | 38909.4602 | 1 | 0 | 2372 | 2445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-4
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38909.4323 | 1 | 0 | 38909.4323 | 1 | 0 | -41 | 32 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4329 | 1 | 0 | 38909.433 | 1 | 0 | 17.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4336 | 1 | 0 | 38909.4336 | 1 | 0 | 76.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4343 | 1 | 0 | 38909.4343 | 1 | 0 | 135.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.435 | 1 | 0 | 38909.435 | 1 | 0 | 194 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4357 | 1 | 0 | 38909.4357 | 1 | 0 | 253 | 326 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4363 | 1 | 0 | 38909.4364 | 1 | 0 | 311.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.437 | 1 | 0 | 38909.437 | 1 | 0 | 370.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4377 | 1 | 0 | 38909.4377 | 1 | 0 | 429 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4384 | 1 | 0 | 38909.4384 | 1 | 0 | 488 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4391 | 1 | 0 | 38909.4391 | 1 | 0 | 546.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4397 | 1 | 0 | 38909.4398 | 1 | 0 | 605.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4404 | 1 | 0 | 38909.4404 | 1 | 0 | 664.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4411 | 1 | 0 | 38909.4411 | 1 | 0 | 723 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4418 | 1 | 0 | 38909.4418 | 1 | 0 | 782 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4425 | 1 | 0 | 38909.4425 | 1 | 0 | 840.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4431 | 1 | 0 | 38909.4432 | 1 | 0 | 899.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4438 | 1 | 0 | 38909.4438 | 1 | 0 | 958.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4445 | 1 | 0 | 38909.4445 | 1 | 0 | 1017 | 1090 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4452 | 1 | 0 | 38909.4452 | 1 | 0 | 1076 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4459 | 1 | 0 | 38909.4459 | 1 | 0 | 1134.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4466 | 1 | 0 | 38909.4466 | 1 | 0 | 1193.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4472 | 1 | 0 | 38909.4472 | 1 | 0 | 1252.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4479 | 1 | 0 | 38909.4479 | 1 | 0 | 1311 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4486 | 1 | 0 | 38909.4486 | 1 | 0 | 1370 | 1443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4493 | 1 | 0 | 38909.4493 | 1 | 0 | 1428.5 | 1501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.45 | 1 | 1 | 38909.45 | 1 | 0 | 1487.5 | 1560.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4506 | 1 | 1 | 38909.4506 | 1 | 0 | 1546.5 | 1619.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4513 | 1 | 1 | 38909.4513 | 1 | 0 | 1605 | 1678 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.452 | 1 | 1 | 38909.452 | 1 | 0 | 1663.5 | 1736.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4527 | 1 | 0 | 38909.4527 | 1 | 0 | 1722.5 | 1795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4534 | 1 | 0 | 38909.4534 | 1 | 0 | 1781.5 | 1854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.454 | 1 | 0 | 38909.4541 | 1 | 0 | 1840.5 | 1913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4547 | 1 | 0 | 38909.4547 | 1 | 0 | 1899 | 1972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4554 | 1 | 0 | 38909.4554 | 1 | 0 | 1957.5 | 2030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4561 | 1 | 0 | 38909.4561 | 1 | 0 | 2016.5 | 2089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4568 | 1 | 0 | 38909.4568 | 1 | 0 | 2075.5 | 2148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4574 | 1 | 0 | 38909.4575 | 1 | 0 | 2134 | 2207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4581 | 1 | 0 | 38909.4581 | 1 | 0 | 2193 | 2266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4588 | 1 | 0 | 38909.4588 | 1 | 0 | 2252 | 2325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4595 | 1 | 0 | 38909.4595 | 1 | 0 | 2310.5 | 2383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4602 | 1 | 0 | 38909.4602 | 1 | 0 | 2369.5 | 2442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38909.4322 | 1 | 0 | 38909.4322 | 1 | 0 | -44 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4329 | 1 | 0 | 38909.4329 | 1 | 0 | 15 | 88 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4336 | 1 | 0 | 38909.4336 | 1 | 0 | 73.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4343 | 1 | 0 | 38909.4343 | 1 | 0 | 132.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.435 | 1 | 0 | 38909.435 | 1 | 0 | 191.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4356 | 1 | 0 | 38909.4356 | 1 | 0 | 250 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4363 | 1 | 0 | 38909.4363 | 1 | 0 | 308.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.437 | 1 | 0 | 38909.437 | 1 | 0 | 367.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4377 | 1 | 0 | 38909.4377 | 1 | 0 | 426.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4383 | 1 | 0 | 38909.4384 | 1 | 0 | 485 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.439 | 1 | 0 | 38909.4391 | 1 | 0 | 544 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4397 | 1 | 0 | 38909.4397 | 1 | 0 | 603 | 676 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4404 | 1 | 0 | 38909.4404 | 1 | 0 | 661.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4411 | 1 | 0 | 38909.4411 | 1 | 0 | 720.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4417 | 1 | 1 | 38909.4418 | 1 | 0 | 779 | 852 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4424 | 1 | 0 | 38909.4425 | 1 | 0 | 838 | 911 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4431 | 1 | 0 | 38909.4431 | 1 | 0 | 897 | 970 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4438 | 1 | 0 | 38909.4438 | 1 | 0 | 955.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4445 | 1 | 0 | 38909.4445 | 1 | 0 | 1014.5 | 1087.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4452 | 1 | 0 | 38909.4452 | 1 | 0 | 1073 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4458 | 1 | 0 | 38909.4459 | 1 | 0 | 1132 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4465 | 1 | 0 | 38909.4465 | 1 | 0 | 1190.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4472 | 1 | 0 | 38909.4472 | 1 | 0 | 1249.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4479 | 1 | 0 | 38909.4479 | 1 | 0 | 1308.5 | 1381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4486 | 1 | 0 | 38909.4486 | 1 | 0 | 1367 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4492 | 1 | 0 | 38909.4493 | 1 | 0 | 1426 | 1499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4499 | 1 | 1 | 38909.4499 | 1 | 0 | 1484.5 | 1557.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4506 | 2 | 1 | 38909.4506 | 1 | 1 | 1543.5 | 1616.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38909.4513 | 2 | 1 | 38909.4513 | 2 | 1 | 1602 | 1675 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38909.452 | 1 | 0 | 38909.452 | 2 | 1 | 1661 | 1734 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4526 | 1 | 0 | 38909.4527 | 1 | 0 | 1720 | 1793 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4533 | 1 | 0 | 38909.4533 | 1 | 0 | 1778.5 | 1851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.454 | 1 | 1 | 38909.454 | 1 | 0 | 1837.5 | 1910.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4547 | 1 | 0 | 38909.4547 | 1 | 0 | 1896 | 1969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4554 | 1 | 0 | 38909.4554 | 1 | 0 | 1955 | 2028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.456 | 1 | 0 | 38909.4561 | 1 | 0 | 2013.5 | 2086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4567 | 1 | 0 | 38909.4567 | 1 | 0 | 2072.5 | 2145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4574 | 1 | 0 | 38909.4574 | 1 | 0 | 2131.5 | 2204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4581 | 1 | 0 | 38909.4581 | 1 | 0 | 2190.5 | 2263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4588 | 1 | 0 | 38909.4588 | 1 | 0 | 2249 | 2322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4594 | 1 | 0 | 38909.4595 | 1 | 0 | 2307.5 | 2380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4601 | 1 | 0 | 38909.4601 | 1 | 0 | 2366.5 | 2439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-6
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38909.4322 | 1 | 0 | 38909.4322 | 1 | 0 | -46.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4329 | 1 | 0 | 38909.4329 | 1 | 0 | 12 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4336 | 1 | 0 | 38909.4336 | 1 | 0 | 71 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4342 | 1 | 0 | 38909.4342 | 1 | 0 | 129.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4349 | 1 | 0 | 38909.4349 | 1 | 0 | 188.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4356 | 1 | 0 | 38909.4356 | 1 | 0 | 247.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4363 | 1 | 0 | 38909.4363 | 1 | 0 | 306 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.437 | 1 | 0 | 38909.437 | 1 | 0 | 364.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4376 | 1 | 0 | 38909.4377 | 1 | 0 | 423.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4383 | 1 | 0 | 38909.4383 | 1 | 0 | 482.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.439 | 1 | 0 | 38909.439 | 1 | 0 | 541.5 | 614.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4397 | 1 | 0 | 38909.4397 | 1 | 0 | 600 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4404 | 1 | 0 | 38909.4404 | 1 | 0 | 659 | 732 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.441 | 1 | 0 | 38909.4411 | 1 | 0 | 717.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4417 | 1 | 0 | 38909.4417 | 1 | 0 | 776.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4424 | 1 | 1 | 38909.4424 | 1 | 0 | 835 | 908 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4431 | 1 | 0 | 38909.4431 | 1 | 0 | 894 | 967 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4438 | 1 | 0 | 38909.4438 | 1 | 0 | 953 | 1026 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4444 | 1 | 0 | 38909.4445 | 1 | 0 | 1011.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4451 | 1 | 0 | 38909.4451 | 1 | 0 | 1070.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4458 | 2 | 0 | 38909.4458 | 1 | 0 | 1129 | 1202 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38909.4465 | 1 | 0 | 38909.4465 | 1 | 0 | 1188 | 1261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4472 | 1 | 0 | 38909.4472 | 1 | 0 | 1246.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4478 | 1 | 0 | 38909.4479 | 1 | 0 | 1305.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4485 | 1 | 0 | 38909.4485 | 1 | 0 | 1364.5 | 1437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4492 | 1 | 0 | 38909.4492 | 1 | 0 | 1423 | 1496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4499 | 2 | 1 | 38909.4499 | 1 | 1 | 1482 | 1555 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38909.4506 | 1 | 1 | 38909.4506 | 1 | 0 | 1540.5 | 1613.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4512 | 2 | 1 | 38909.4513 | 2 | 1 | 1599.5 | 1672.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 210902.142
38909.4519 | 1 | 1 | 38909.4519 | 2 | 1 | 1658.5 | 1731.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 445851546.04 | 211101.9527 | 211002.0473
38909.4526 | 1 | 0 | 38909.4526 | 1 | 0 | 1717 | 1790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4533 | 1 | 0 | 38909.4533 | 1 | 0 | 1776 | 1849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.454 | 1 | 0 | 38909.454 | 1 | 0 | 1834.5 | 1907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4547 | 1 | 0 | 38909.4547 | 1 | 0 | 1893.5 | 1966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4553 | 1 | 0 | 38909.4553 | 1 | 0 | 1952.5 | 2025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.456 | 1 | 1 | 38909.456 | 1 | 0 | 2011 | 2084 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4567 | 1 | 0 | 38909.4567 | 1 | 0 | 2069.5 | 2142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4574 | 1 | 0 | 38909.4574 | 1 | 0 | 2128.5 | 2201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4581 | 1 | 0 | 38909.4581 | 1 | 0 | 2187.5 | 2260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4587 | 1 | 0 | 38909.4587 | 1 | 0 | 2246 | 2319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4594 | 1 | 0 | 38909.4594 | 1 | 0 | 2305 | 2378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4601 | 1 | 0 | 38909.4601 | 1 | 0 | 2363.5 | 2436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-5
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38909.4322 | 1 | 0 | 38909.4322 | 1 | 0 | -49.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4328 | 1 | 0 | 38909.4329 | 1 | 0 | 9.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4335 | 1 | 0 | 38909.4335 | 1 | 0 | 68 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4342 | 1 | 0 | 38909.4342 | 1 | 0 | 127 | 200 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4349 | 1 | 0 | 38909.4349 | 1 | 0 | 185.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4356 | 1 | 0 | 38909.4356 | 1 | 0 | 244.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4362 | 1 | 0 | 38909.4363 | 1 | 0 | 303.5 | 376.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4369 | 1 | 0 | 38909.4369 | 1 | 0 | 362 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4376 | 1 | 0 | 38909.4376 | 1 | 0 | 421 | 494 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4383 | 1 | 0 | 38909.4383 | 1 | 0 | 479.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.439 | 1 | 0 | 38909.439 | 1 | 0 | 538.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4397 | 1 | 0 | 38909.4397 | 1 | 0 | 597.5 | 670.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4403 | 1 | 0 | 38909.4403 | 1 | 0 | 656 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.441 | 1 | 0 | 38909.441 | 1 | 0 | 715 | 788 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4417 | 1 | 0 | 38909.4417 | 1 | 0 | 773.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4424 | 1 | 0 | 38909.4424 | 1 | 0 | 832.5 | 905.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.443 | 1 | 0 | 38909.4431 | 1 | 0 | 891 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4437 | 1 | 1 | 38909.4437 | 1 | 0 | 950 | 1023 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4444 | 1 | 0 | 38909.4444 | 1 | 0 | 1009 | 1082 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4451 | 1 | 0 | 38909.4451 | 1 | 0 | 1067.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4458 | 1 | 0 | 38909.4458 | 1 | 0 | 1126.5 | 1199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4464 | 1 | 0 | 38909.4465 | 1 | 0 | 1185 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4471 | 1 | 0 | 38909.4472 | 1 | 0 | 1244 | 1317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4478 | 1 | 0 | 38909.4478 | 1 | 0 | 1302.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4485 | 1 | 0 | 38909.4485 | 1 | 0 | 1361.5 | 1434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4492 | 1 | 0 | 38909.4492 | 1 | 0 | 1420.5 | 1493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4498 | 2 | 4 | 38909.4499 | 1 | 2 | 1479 | 1552 | 0.1221 | 0.2442 | 0.06105 | 0.1221 | 0.001221 | 0.002442 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 105650.8578 | 211602.5695 | 52650.6182
38909.4505 | 2 | 3 | 38909.4506 | 2 | 2 | 1538 | 1611 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 211101.7158 | 222819972.0267 | 70267.3018
38909.4512 | 1 | 3 | 38909.4512 | 1 | 3 | 1596.5 | 1669.5 | 0.06105 | 0.18315 | 0.06105 | 0.18315 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.001221 | 0.001221 | 105751 | 105751 | 70234.2519
38909.4519 | 1 | 2 | 38909.4519 | 2 | 1 | 1655.5 | 1728.5 | 0.06105 | 0.1221 | 0.1221 | 0.06105 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211402.1897 | 211201.9053 | 105451.071
38909.4526 | 1 | 0 | 38909.4526 | 1 | 0 | 1714 | 1787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4533 | 1 | 0 | 38909.4533 | 1 | 0 | 1773 | 1846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4539 | 1 | 1 | 38909.4539 | 1 | 0 | 1831.5 | 1904.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4546 | 1 | 0 | 38909.4546 | 1 | 0 | 1890.5 | 1963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4553 | 1 | 0 | 38909.4553 | 1 | 0 | 1949.5 | 2022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.456 | 1 | 1 | 38909.456 | 1 | 0 | 2008.5 | 2081.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4567 | 1 | 1 | 38909.4567 | 1 | 0 | 2067 | 2140 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4573 | 1 | 0 | 38909.4573 | 1 | 0 | 2125.5 | 2198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.458 | 1 | 0 | 38909.458 | 1 | 0 | 2184.5 | 2257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4587 | 1 | 0 | 38909.4587 | 1 | 0 | 2243.5 | 2316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4594 | 1 | 0 | 38909.4594 | 1 | 0 | 2302 | 2375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4601 | 1 | 0 | 38909.4601 | 1 | 0 | 2361 | 2434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-4
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38909.4321 | 1 | 0 | 38909.4321 | 1 | 0 | -52.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4328 | 1 | 0 | 38909.4328 | 1 | 0 | 6.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4335 | 1 | 0 | 38909.4335 | 1 | 0 | 65.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4342 | 1 | 0 | 38909.4342 | 1 | 0 | 124 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4348 | 1 | 0 | 38909.4349 | 1 | 0 | 183 | 256 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4355 | 1 | 0 | 38909.4355 | 1 | 0 | 241.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4362 | 1 | 0 | 38909.4362 | 1 | 0 | 300.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4369 | 1 | 0 | 38909.4369 | 1 | 0 | 359.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4376 | 1 | 0 | 38909.4376 | 1 | 0 | 418 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4383 | 1 | 0 | 38909.4383 | 1 | 0 | 477 | 550 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4389 | 1 | 0 | 38909.4389 | 1 | 0 | 535.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4396 | 1 | 0 | 38909.4396 | 1 | 0 | 594.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4403 | 1 | 0 | 38909.4403 | 1 | 0 | 653 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.441 | 1 | 0 | 38909.441 | 1 | 0 | 712 | 785 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4417 | 1 | 0 | 38909.4417 | 1 | 0 | 770.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4423 | 1 | 0 | 38909.4423 | 1 | 0 | 829.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.443 | 1 | 0 | 38909.443 | 1 | 0 | 888.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4437 | 1 | 0 | 38909.4437 | 1 | 0 | 947 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4444 | 1 | 0 | 38909.4444 | 1 | 0 | 1006 | 1079 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4451 | 1 | 0 | 38909.4451 | 1 | 0 | 1064.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4457 | 1 | 0 | 38909.4458 | 1 | 0 | 1123.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4464 | 1 | 0 | 38909.4464 | 1 | 0 | 1182.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4471 | 2 | 0 | 38909.4471 | 1 | 0 | 1241 | 1314 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38909.4478 | 1 | 0 | 38909.4478 | 1 | 0 | 1300 | 1373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4485 | 1 | 0 | 38909.4485 | 1 | 0 | 1358.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4491 | 1 | 0 | 38909.4492 | 1 | 0 | 1417.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4498 | 2 | 7 | 38909.4498 | 2 | 5 | 1476.5 | 1549.5 | 0.1221 | 0.42735 | 0.1221 | 0.30525 | 0.001221 | 0.0042735 | 0.001221 | 0.0030525 | 0.0030525 | 0.0018315 | 42304.2352 | 70645.6571 | 30014.942
38909.4505 | 2 | 5 | 38909.4505 | 2 | 4 | 1535 | 1608 | 0.1221 | 0.30525 | 0.1221 | 0.2442 | 0.001221 | 0.0030525 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 70478.3039 | 105851.38 | 42080.6455
38909.4512 | 2 | 5 | 38909.4512 | 2 | 4 | 1594 | 1667 | 0.1221 | 0.30525 | 0.1221 | 0.2442 | 0.001221 | 0.0030525 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 70478.3039 | 105851.38 | 42080.6455
38909.4519 | 2 | 7 | 38909.4519 | 2 | 5 | 1652.5 | 1725.5 | 0.1221 | 0.42735 | 0.1221 | 0.30525 | 0.001221 | 0.0042735 | 0.001221 | 0.0030525 | 0.0030525 | 0.0018315 | 42304.2352 | 70645.6571 | 30014.942
38909.4525 | 1 | 0 | 38909.4526 | 1 | 0 | 1711.5 | 1784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4532 | 1 | 0 | 38909.4532 | 1 | 0 | 1770 | 1843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4539 | 2 | 1 | 38909.4539 | 1 | 1 | 1829 | 1902 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 211101.9527 | 445851546.4873 | 211001.9527
38909.4546 | 1 | 0 | 38909.4546 | 1 | 0 | 1888 | 1961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4553 | 1 | 0 | 38909.4553 | 1 | 0 | 1946.5 | 2019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4559 | 1 | 1 | 38909.456 | 2 | 1 | 2005.5 | 2078.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 445851546.04 | 211101.9527 | 211002.0473
38909.4566 | 2 | 0 | 38909.4566 | 1 | 0 | 2064.5 | 2137.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38909.4573 | 1 | 0 | 38909.4573 | 1 | 0 | 2123 | 2196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.458 | 1 | 0 | 38909.458 | 1 | 0 | 2181.5 | 2254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4587 | 1 | 0 | 38909.4587 | 1 | 0 | 2240.5 | 2313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4594 | 1 | 0 | 38909.4594 | 1 | 0 | 2299.5 | 2372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.46 | 1 | 0 | 38909.46 | 1 | 0 | 2358 | 2431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-3
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38909.4321 | 1 | 0 | 38909.4321 | 1 | 0 | -55 | 18 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4328 | 1 | 0 | 38909.4328 | 1 | 0 | 3.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4335 | 1 | 0 | 38909.4335 | 1 | 0 | 62.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4341 | 1 | 0 | 38909.4342 | 1 | 0 | 121.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4348 | 1 | 0 | 38909.4348 | 1 | 0 | 180 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4355 | 1 | 0 | 38909.4355 | 1 | 0 | 239 | 312 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4362 | 1 | 0 | 38909.4362 | 1 | 0 | 297.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4369 | 1 | 0 | 38909.4369 | 1 | 0 | 356.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4375 | 1 | 0 | 38909.4376 | 1 | 0 | 415.5 | 488.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4382 | 1 | 0 | 38909.4382 | 1 | 0 | 474 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4389 | 1 | 0 | 38909.4389 | 1 | 0 | 532.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4396 | 1 | 0 | 38909.4396 | 1 | 0 | 591.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4403 | 1 | 0 | 38909.4403 | 1 | 0 | 650.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4409 | 1 | 0 | 38909.441 | 1 | 0 | 709 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4416 | 1 | 0 | 38909.4416 | 1 | 0 | 768 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4423 | 1 | 0 | 38909.4423 | 1 | 0 | 827 | 900 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.443 | 1 | 0 | 38909.443 | 1 | 0 | 885.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4437 | 1 | 0 | 38909.4437 | 1 | 0 | 944.5 | 1017.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4443 | 1 | 0 | 38909.4444 | 1 | 0 | 1003 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.445 | 1 | 0 | 38909.445 | 1 | 0 | 1062 | 1135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4457 | 1 | 0 | 38909.4457 | 2 | 0 | 1120.5 | 1193.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38909.4464 | 1 | 0 | 38909.4464 | 1 | 0 | 1179.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4471 | 1 | 0 | 38909.4471 | 1 | 0 | 1238.5 | 1311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4477 | 1 | 0 | 38909.4478 | 1 | 0 | 1297 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4484 | 1 | 0 | 38909.4484 | 1 | 0 | 1356 | 1429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4491 | 1 | 0 | 38909.4491 | 1 | 0 | 1414.5 | 1487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4498 | 4 | 13 | 38909.4498 | 3 | 9 | 1473.5 | 1546.5 | 0.2442 | 0.79365 | 0.18315 | 0.54945 | 0.002442 | 0.0079365 | 0.0018315 | 0.0054945 | 0.0054945 | 0.003663 | 23529.5845 | 35392.6263 | 16077.8038
38909.4505 | 4 | 13 | 38909.4505 | 2 | 9 | 1532.5 | 1605.5 | 0.2442 | 0.79365 | 0.1221 | 0.54945 | 0.002442 | 0.0079365 | 0.001221 | 0.0054945 | 0.0054945 | 0.0042735 | 23545.7162 | 30323.0074 | 16070.2339
38909.4511 | 5 | 11 | 38909.4512 | 3 | 7 | 1591 | 1664 | 0.30525 | 0.67155 | 0.18315 | 0.42735 | 0.0030525 | 0.0067155 | 0.0018315 | 0.0042735 | 0.003663 | 0.002442 | 35255.5886 | 53013.6466 | 19027.9257
38909.4518 | 4 | 13 | 38909.4519 | 2 | 8 | 1650 | 1723 | 0.2442 | 0.79365 | 0.1221 | 0.4884 | 0.002442 | 0.0079365 | 0.001221 | 0.004884 | 0.0054945 | 0.003663 | 23529.6076 | 35384.1753 | 16077.793
38909.4525 | 2 | 3 | 38909.4525 | 2 | 1 | 1708.5 | 1781.5 | 0.1221 | 0.18315 | 0.1221 | 0.06105 | 0.001221 | 0.0018315 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211402.2846 | 211201.9052 | 70234.0789
38909.4532 | 1 | 0 | 38909.4532 | 1 | 0 | 1767.5 | 1840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4539 | 2 | 3 | 38909.4539 | 2 | 1 | 1826.5 | 1899.5 | 0.1221 | 0.18315 | 0.1221 | 0.06105 | 0.001221 | 0.0018315 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211402.2846 | 211201.9052 | 70234.0789
38909.4545 | 1 | 0 | 38909.4546 | 1 | 0 | 1885 | 1958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4552 | 1 | 0 | 38909.4553 | 1 | 0 | 1944 | 2017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4559 | 3 | 9 | 38909.4559 | 2 | 3 | 2002.5 | 2075.5 | 0.18315 | 0.54945 | 0.1221 | 0.18315 | 0.0018315 | 0.0054945 | 0.001221 | 0.0018315 | 0.003663 | 0.0006105 | 35191.7926 | 212917.0572 | 23333.7076
38909.4566 | 1 | 0 | 38909.4566 | 1 | 0 | 2061.5 | 2134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4573 | 1 | 0 | 38909.4573 | 1 | 0 | 2120.5 | 2193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.458 | 1 | 0 | 38909.458 | 1 | 0 | 2179 | 2252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4586 | 1 | 0 | 38909.4586 | 1 | 0 | 2237.5 | 2310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4593 | 1 | 0 | 38909.4593 | 1 | 0 | 2296.5 | 2369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.46 | 1 | 0 | 38909.46 | 1 | 0 | 2355.5 | 2428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-7
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38909.4321 | 1 | 0 | 38909.4321 | 1 | 0 | -58 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4327 | 1 | 0 | 38909.4328 | 1 | 0 | 1 | 74 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4334 | 1 | 0 | 38909.4334 | 1 | 0 | 59.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4341 | 1 | 0 | 38909.4341 | 1 | 0 | 118.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4348 | 1 | 0 | 38909.4348 | 1 | 0 | 177.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4355 | 1 | 0 | 38909.4355 | 1 | 0 | 236 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4361 | 1 | 0 | 38909.4362 | 1 | 0 | 295 | 368 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4368 | 1 | 0 | 38909.4368 | 1 | 0 | 353.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4375 | 1 | 0 | 38909.4375 | 1 | 0 | 412.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4382 | 1 | 0 | 38909.4382 | 1 | 0 | 471 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4389 | 1 | 0 | 38909.4389 | 1 | 0 | 530 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4395 | 1 | 0 | 38909.4396 | 1 | 0 | 588.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4402 | 1 | 0 | 38909.4402 | 1 | 0 | 647.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4409 | 1 | 0 | 38909.4409 | 1 | 0 | 706.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4416 | 1 | 0 | 38909.4416 | 1 | 0 | 765 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4423 | 1 | 0 | 38909.4423 | 2 | 0 | 824 | 897 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38909.443 | 1 | 0 | 38909.443 | 1 | 0 | 882.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4436 | 1 | 0 | 38909.4436 | 1 | 0 | 941.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4443 | 1 | 0 | 38909.4443 | 1 | 0 | 1000.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.445 | 1 | 0 | 38909.445 | 1 | 0 | 1059 | 1132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4457 | 1 | 0 | 38909.4457 | 1 | 0 | 1118 | 1191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4464 | 1 | 0 | 38909.4464 | 1 | 0 | 1176.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.447 | 1 | 0 | 38909.447 | 1 | 0 | 1235.5 | 1308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4477 | 1 | 0 | 38909.4477 | 1 | 0 | 1294.5 | 1367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4484 | 1 | 0 | 38909.4484 | 1 | 0 | 1353 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4491 | 1 | 0 | 38909.4491 | 1 | 0 | 1412 | 1485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4498 | 1164 | 1141 | 38909.4498 | 1024 | 1065 | 1470.5 | 1543.5 | 71.0623 | 69.6581 | 62.5153 | 65.0183 | 0.71062 | 0.69658 | 0.62515 | 0.65018 | 0.014042 | 0.025031 | 835.8659 | 1260.2533 | 15.5886
38909.4504 | 1034 | 1000 | 38909.4505 | 1077 | 1045 | 1529.5 | 1602.5 | 63.1258 | 61.0501 | 65.7509 | 63.7973 | 0.63126 | 0.6105 | 0.65751 | 0.63797 | 0.020757 | 0.019536 | 2260.2646 | 7278.731 | 7.7949
38909.4511 | 1013 | 1054 | 38909.4511 | 1122 | 1093 | 1588.5 | 1661.5 | 61.8437 | 64.3468 | 68.4982 | 66.7277 | 0.61844 | 0.64347 | 0.68498 | 0.66728 | 0.025031 | 0.017705 | 614.7555 | 764.1215 | 3.8609
38909.4518 | 974 | 934 | 38909.4518 | 1185 | 1177 | 1647 | 1720 | 59.4628 | 57.0208 | 72.3443 | 71.8559 | 0.59463 | 0.57021 | 0.72344 | 0.71856 | 0.02442 | 0.004884 | 142.6185 | 123.1137 | 12.1124
38909.4525 | 563 | 582 | 38909.4525 | 981 | 970 | 1706 | 1779 | 34.3712 | 35.5311 | 59.8901 | 59.2186 | 0.34371 | 0.35531 | 0.5989 | 0.59219 | 0.0116 | 0.0067155 | 7878.2186 | 86253.8695 | 166.1339
38909.4532 | 1 | 0 | 38909.4532 | 1 | 0 | 1764.5 | 1837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4538 | 34 | 75 | 38909.4539 | 274 | 210 | 1823.5 | 1896.5 | 2.0757 | 4.5788 | 16.7277 | 12.8205 | 0.020757 | 0.045788 | 0.16728 | 0.12821 | 0.025031 | 0.039072 | 5393.2281 | 3059.6164 | 2587.4586
38909.4545 | 1 | 0 | 38909.4545 | 1 | 0 | 1882.5 | 1955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4552 | 1 | 0 | 38909.4552 | 1 | 0 | 1941 | 2014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4559 | 362 | 367 | 38909.4559 | 787 | 815 | 1999.5 | 2072.5 | 22.1001 | 22.4054 | 48.0464 | 49.7558 | 0.221 | 0.22405 | 0.48046 | 0.49756 | 0.0030525 | 0.017094 | 55481.0209 | 19903.1445 | 375.2319
38909.4566 | 1 | 0 | 38909.4566 | 1 | 0 | 2058.5 | 2131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4572 | 1 | 0 | 38909.4573 | 1 | 0 | 2117.5 | 2190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4579 | 1 | 0 | 38909.4579 | 1 | 0 | 2176.5 | 2249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4586 | 1 | 1 | 38909.4586 | 1 | 0 | 2235 | 2308 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4593 | 1 | 0 | 38909.4593 | 1 | 0 | 2294 | 2367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.46 | 1 | 0 | 38909.46 | 1 | 0 | 2352.5 | 2425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-6
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38909.432 | 1 | 0 | 38909.432 | 1 | 0 | -60.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4327 | 1 | 0 | 38909.4327 | 1 | 0 | -2 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4334 | 1 | 0 | 38909.4334 | 1 | 0 | 57 | 130 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4341 | 1 | 0 | 38909.4341 | 1 | 0 | 115.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4348 | 1 | 0 | 38909.4348 | 1 | 0 | 174.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4354 | 1 | 0 | 38909.4355 | 1 | 0 | 233.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4361 | 1 | 0 | 38909.4361 | 1 | 0 | 292 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4368 | 1 | 0 | 38909.4368 | 1 | 0 | 351 | 424 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4375 | 1 | 0 | 38909.4375 | 1 | 0 | 409.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4382 | 1 | 0 | 38909.4382 | 1 | 0 | 468.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4388 | 1 | 0 | 38909.4389 | 1 | 0 | 527 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4395 | 1 | 0 | 38909.4395 | 1 | 0 | 586 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4402 | 1 | 0 | 38909.4402 | 1 | 0 | 645 | 718 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4409 | 1 | 0 | 38909.4409 | 1 | 0 | 703.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4416 | 1 | 0 | 38909.4416 | 1 | 0 | 762.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4422 | 1 | 0 | 38909.4423 | 1 | 0 | 821 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4429 | 1 | 0 | 38909.4429 | 1 | 0 | 880 | 953 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4436 | 1 | 0 | 38909.4436 | 2 | 0 | 938.5 | 1011.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38909.4443 | 1 | 0 | 38909.4443 | 1 | 0 | 997.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.445 | 1 | 0 | 38909.445 | 1 | 0 | 1056.5 | 1129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4456 | 1 | 0 | 38909.4457 | 1 | 0 | 1115 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4463 | 1 | 0 | 38909.4463 | 1 | 0 | 1174 | 1247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.447 | 1 | 0 | 38909.447 | 1 | 0 | 1232.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4477 | 1 | 0 | 38909.4477 | 1 | 0 | 1291.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4484 | 1 | 0 | 38909.4484 | 1 | 0 | 1350.5 | 1423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.449 | 1 | 0 | 38909.4491 | 1 | 0 | 1409 | 1482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4497 | 1 | 0 | 38909.4497 | 1 | 0 | 1468 | 1541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4504 | 1 | 0 | 38909.4504 | 1 | 0 | 1526.5 | 1599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4511 | 1 | 0 | 38909.4511 | 1 | 0 | 1585.5 | 1658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4518 | 1 | 0 | 38909.4518 | 1 | 0 | 1644.5 | 1717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4524 | 1 | 0 | 38909.4525 | 1 | 0 | 1703 | 1776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4531 | 1 | 0 | 38909.4531 | 1 | 0 | 1762 | 1835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4538 | 1 | 0 | 38909.4538 | 1 | 0 | 1820.5 | 1893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4545 | 1 | 0 | 38909.4545 | 1 | 0 | 1879.5 | 1952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4552 | 1 | 0 | 38909.4552 | 1 | 0 | 1938 | 2011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4558 | 1 | 0 | 38909.4559 | 1 | 0 | 1997 | 2070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4565 | 1 | 0 | 38909.4565 | 1 | 0 | 2055.5 | 2128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4572 | 1 | 0 | 38909.4572 | 1 | 0 | 2114.5 | 2187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4579 | 1 | 0 | 38909.4579 | 1 | 0 | 2173.5 | 2246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4586 | 1 | 0 | 38909.4586 | 1 | 0 | 2232 | 2305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4592 | 1 | 0 | 38909.4593 | 1 | 0 | 2291 | 2364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4599 | 1 | 0 | 38909.4599 | 1 | 0 | 2349.5 | 2422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-5
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38909.432 | 1 | 0 | 38909.432 | 1 | 0 | -63.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4327 | 1 | 0 | 38909.4327 | 1 | 0 | -4.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4334 | 1 | 0 | 38909.4334 | 1 | 0 | 54 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.434 | 1 | 0 | 38909.4341 | 1 | 0 | 113 | 186 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4347 | 1 | 0 | 38909.4347 | 1 | 0 | 171.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4354 | 1 | 0 | 38909.4354 | 1 | 0 | 230.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4361 | 1 | 0 | 38909.4361 | 1 | 0 | 289.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4368 | 1 | 0 | 38909.4368 | 1 | 0 | 348 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4374 | 1 | 0 | 38909.4375 | 1 | 0 | 407 | 480 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4381 | 1 | 0 | 38909.4381 | 1 | 0 | 465.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4388 | 1 | 0 | 38909.4388 | 1 | 0 | 524.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4395 | 1 | 0 | 38909.4395 | 1 | 0 | 583.5 | 656.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4402 | 1 | 0 | 38909.4402 | 1 | 0 | 642 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4408 | 1 | 0 | 38909.4409 | 1 | 0 | 700.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4415 | 1 | 0 | 38909.4415 | 1 | 0 | 759.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4422 | 1 | 0 | 38909.4422 | 1 | 0 | 818.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4429 | 1 | 0 | 38909.4429 | 1 | 0 | 877 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4436 | 1 | 0 | 38909.4436 | 1 | 0 | 936 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4442 | 1 | 0 | 38909.4443 | 1 | 0 | 994.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4449 | 1 | 0 | 38909.4449 | 1 | 0 | 1053.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4456 | 1 | 0 | 38909.4456 | 1 | 0 | 1112.5 | 1185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4463 | 1 | 0 | 38909.4463 | 1 | 0 | 1171 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.447 | 1 | 0 | 38909.447 | 1 | 0 | 1230 | 1303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4477 | 1 | 0 | 38909.4477 | 1 | 0 | 1288.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4483 | 1 | 0 | 38909.4483 | 1 | 0 | 1347.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.449 | 1 | 0 | 38909.449 | 1 | 0 | 1406.5 | 1479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4497 | 1 | 0 | 38909.4497 | 1 | 0 | 1465 | 1538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4504 | 1 | 0 | 38909.4504 | 1 | 0 | 1524 | 1597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4511 | 1 | 0 | 38909.4511 | 1 | 0 | 1582.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4517 | 1 | 0 | 38909.4517 | 1 | 0 | 1641.5 | 1714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4524 | 1 | 0 | 38909.4524 | 1 | 0 | 1700 | 1773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4531 | 1 | 0 | 38909.4531 | 1 | 0 | 1759 | 1832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4538 | 1 | 0 | 38909.4538 | 1 | 0 | 1818 | 1891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4545 | 1 | 0 | 38909.4545 | 1 | 0 | 1876.5 | 1949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4551 | 1 | 0 | 38909.4552 | 1 | 0 | 1935.5 | 2008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4558 | 1 | 0 | 38909.4558 | 1 | 0 | 1994 | 2067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4565 | 1 | 0 | 38909.4565 | 1 | 0 | 2053 | 2126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4572 | 1 | 0 | 38909.4572 | 1 | 0 | 2111.5 | 2184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4579 | 1 | 0 | 38909.4579 | 1 | 0 | 2170.5 | 2243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4585 | 1 | 0 | 38909.4586 | 1 | 0 | 2229.5 | 2302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4592 | 1 | 0 | 38909.4592 | 1 | 0 | 2288.5 | 2361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4599 | 1 | 0 | 38909.4599 | 1 | 0 | 2347 | 2420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-4
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38909.432 | 1 | 0 | 38909.432 | 1 | 0 | -66.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4327 | 1 | 0 | 38909.4327 | 1 | 0 | -7.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4333 | 1 | 0 | 38909.4333 | 1 | 0 | 51.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.434 | 1 | 0 | 38909.434 | 1 | 0 | 110 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4347 | 1 | 0 | 38909.4347 | 1 | 0 | 169 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4354 | 1 | 0 | 38909.4354 | 1 | 0 | 227.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4361 | 1 | 0 | 38909.4361 | 1 | 0 | 286.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4367 | 1 | 0 | 38909.4367 | 1 | 0 | 345.5 | 418.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4374 | 1 | 0 | 38909.4374 | 1 | 0 | 404 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4381 | 1 | 0 | 38909.4381 | 1 | 0 | 463 | 536 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4388 | 1 | 0 | 38909.4388 | 1 | 0 | 521.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4395 | 1 | 0 | 38909.4395 | 1 | 0 | 580.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4401 | 1 | 0 | 38909.4402 | 1 | 0 | 639 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4408 | 1 | 0 | 38909.4408 | 1 | 0 | 698 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4415 | 1 | 0 | 38909.4415 | 1 | 0 | 756.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4422 | 1 | 0 | 38909.4422 | 1 | 0 | 815.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4429 | 1 | 0 | 38909.4429 | 1 | 0 | 874.5 | 947.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4435 | 1 | 0 | 38909.4436 | 1 | 0 | 933 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4442 | 1 | 0 | 38909.4442 | 1 | 0 | 992 | 1065 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4449 | 1 | 0 | 38909.4449 | 1 | 0 | 1050.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4456 | 1 | 0 | 38909.4456 | 1 | 0 | 1109.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4463 | 1 | 0 | 38909.4463 | 1 | 0 | 1168.5 | 1241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4469 | 1 | 0 | 38909.447 | 1 | 0 | 1227 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4476 | 1 | 0 | 38909.4476 | 1 | 0 | 1286 | 1359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4483 | 1 | 0 | 38909.4483 | 1 | 0 | 1344.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.449 | 1 | 0 | 38909.449 | 1 | 0 | 1403.5 | 1476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4497 | 1 | 0 | 38909.4497 | 1 | 0 | 1462.5 | 1535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4503 | 1 | 0 | 38909.4504 | 1 | 0 | 1521 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.451 | 1 | 0 | 38909.451 | 1 | 0 | 1580 | 1653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4517 | 1 | 0 | 38909.4517 | 1 | 0 | 1638.5 | 1711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4524 | 1 | 0 | 38909.4524 | 1 | 0 | 1697.5 | 1770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4531 | 1 | 0 | 38909.4531 | 1 | 0 | 1756.5 | 1829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4537 | 1 | 0 | 38909.4538 | 1 | 0 | 1815 | 1888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4544 | 1 | 1 | 38909.4544 | 1 | 0 | 1873.5 | 1946.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4551 | 1 | 0 | 38909.4551 | 1 | 0 | 1932.5 | 2005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4558 | 1 | 0 | 38909.4558 | 1 | 0 | 1991.5 | 2064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4565 | 1 | 0 | 38909.4565 | 1 | 0 | 2050 | 2123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4571 | 1 | 0 | 38909.4572 | 1 | 0 | 2109 | 2182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4578 | 1 | 0 | 38909.4578 | 1 | 0 | 2167.5 | 2240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4585 | 1 | 0 | 38909.4585 | 1 | 0 | 2226.5 | 2299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4592 | 1 | 0 | 38909.4592 | 1 | 0 | 2285.5 | 2358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4599 | 1 | 0 | 38909.4599 | 1 | 0 | 2344 | 2417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-3
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38909.4319 | 1 | 0 | 38909.432 | 1 | 0 | -69 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4326 | 1 | 0 | 38909.4326 | 1 | 0 | -10.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4333 | 1 | 0 | 38909.4333 | 1 | 0 | 48.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.434 | 1 | 0 | 38909.434 | 1 | 0 | 107.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4347 | 1 | 0 | 38909.4347 | 1 | 0 | 166 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4353 | 1 | 0 | 38909.4354 | 1 | 0 | 225 | 298 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.436 | 1 | 0 | 38909.436 | 1 | 0 | 283.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4367 | 1 | 0 | 38909.4367 | 1 | 0 | 342.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4374 | 1 | 0 | 38909.4374 | 1 | 0 | 401.5 | 474.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4381 | 1 | 0 | 38909.4381 | 1 | 0 | 460 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4387 | 1 | 0 | 38909.4388 | 1 | 0 | 519 | 592 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4394 | 1 | 0 | 38909.4394 | 1 | 0 | 577.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4401 | 1 | 0 | 38909.4401 | 1 | 0 | 636.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4408 | 1 | 0 | 38909.4408 | 1 | 0 | 695 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4415 | 1 | 0 | 38909.4415 | 1 | 0 | 754 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4421 | 1 | 0 | 38909.4422 | 1 | 0 | 812.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4428 | 1 | 0 | 38909.4428 | 1 | 0 | 871.5 | 944.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4435 | 1 | 0 | 38909.4435 | 1 | 0 | 930.5 | 1003.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4442 | 1 | 0 | 38909.4442 | 1 | 0 | 989 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4449 | 1 | 0 | 38909.4449 | 1 | 0 | 1048 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4455 | 1 | 0 | 38909.4456 | 1 | 0 | 1106.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4462 | 1 | 0 | 38909.4462 | 1 | 0 | 1165.5 | 1238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4469 | 1 | 0 | 38909.4469 | 1 | 0 | 1224.5 | 1297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4476 | 1 | 0 | 38909.4476 | 1 | 0 | 1283 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4483 | 1 | 0 | 38909.4483 | 1 | 0 | 1342 | 1415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4489 | 1 | 0 | 38909.449 | 1 | 0 | 1400.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4496 | 1 | 0 | 38909.4496 | 1 | 0 | 1459.5 | 1532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4503 | 1 | 0 | 38909.4503 | 1 | 0 | 1518.5 | 1591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.451 | 1 | 0 | 38909.451 | 1 | 0 | 1577 | 1650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4517 | 1 | 0 | 38909.4517 | 1 | 0 | 1636 | 1709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4523 | 1 | 0 | 38909.4524 | 1 | 0 | 1694.5 | 1767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.453 | 1 | 0 |  | 1 | 0 | 1753 | 1826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4537 | 1 | 0 | 38909.4537 | 1 | 0 | 1812.5 | 1885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4544 | 1 | 0 | 38909.4544 | 1 | 0 | 1871 | 1944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4551 | 1 | 0 | 38909.4551 | 1 | 0 | 1929.5 | 2002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4558 | 1 | 0 | 38909.4558 | 1 | 0 | 1988.5 | 2061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4564 | 1 | 0 | 38909.4564 | 1 | 0 | 2047.5 | 2120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4571 | 1 | 0 | 38909.4571 | 1 | 0 | 2106 | 2179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4578 | 1 | 0 | 38909.4578 | 1 | 0 | 2165 | 2238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4585 | 1 | 0 | 38909.4585 | 1 | 0 | 2224 | 2297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4592 | 1 | 0 | 38909.4592 | 1 | 0 | 2282.5 | 2355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4598 | 1 | 0 | 38909.4598 | 16 | 0 | 2341.5 | 2414.5 | 0.06105 | 0 | 0.9768 | 0 | 0.0006105 | 0 | 0.009768 | 0 | 0.0006105 | 0.009768 | 211202 | 13106.375 | 211201.9994

## C1-2
Penlight Test 14 |  |  | 2006-07-11 | 10:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Tray
300 C | 6.1 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38909.4319 | 1 | 0 | 38909.4319 | 1 | 0 | -72 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4326 | 1 | 0 | 38909.4326 | 1 | 0 | -13 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4333 | 1 | 0 | 38909.4333 | 1 | 0 | 45.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4339 | 1 | 0 | 38909.434 | 1 | 0 | 104.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4346 | 1 | 0 | 38909.4346 | 1 | 0 | 163.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4353 | 1 | 0 | 38909.4353 | 1 | 0 | 222 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.436 | 1 | 0 | 38909.436 | 1 | 0 | 281 | 354 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4367 | 1 | 0 | 38909.4367 | 1 | 0 | 339.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4373 | 1 | 0 | 38909.4374 | 1 | 0 | 398.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.438 | 1 | 0 | 38909.438 | 1 | 0 | 457.5 | 530.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4387 | 1 | 0 | 38909.4387 | 1 | 0 | 516 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4394 | 1 | 0 | 38909.4394 | 1 | 0 | 574.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4401 | 1 | 0 | 38909.4401 | 1 | 0 | 633.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4408 | 1 | 0 | 38909.4408 | 1 | 0 | 692.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4414 | 1 | 0 | 38909.4414 | 1 | 0 | 751.5 | 824.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4421 | 1 | 0 | 38909.4421 | 1 | 0 | 810 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4428 | 1 | 0 | 38909.4428 | 1 | 0 | 868.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4435 | 1 | 1 | 38909.4435 | 1 | 0 | 927.5 | 1000.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38909.4442 | 1 | 0 | 38909.4442 | 1 | 0 | 986.5 | 1059.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4448 | 1 | 0 | 38909.4448 | 1 | 0 | 1045 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4455 | 1 | 0 | 38909.4455 | 1 | 0 | 1104 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4462 | 1 | 0 | 38909.4462 | 1 | 0 | 1162.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4469 | 1 | 0 | 38909.4469 | 1 | 0 | 1221.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4476 | 1 | 0 | 38909.4476 | 1 | 0 | 1280.5 | 1353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4482 | 1 | 0 | 38909.4483 | 1 | 0 | 1339 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4489 | 1 | 0 | 38909.4489 | 1 | 0 | 1398 | 1471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4496 | 1 | 0 | 38909.4496 | 1 | 0 | 1456.5 | 1529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4503 | 1 | 0 | 38909.4503 | 1 | 0 | 1515.5 | 1588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.451 | 1 | 0 | 38909.451 | 1 | 0 | 1574.5 | 1647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4516 | 1 | 0 | 38909.4517 | 1 | 0 | 1633 | 1706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4523 | 1 | 0 | 38909.4523 | 1 | 0 | 1692 | 1765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.453 | 1 | 0 | 38909.453 | 1 | 0 | 1750.5 | 1823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4537 | 1 | 0 | 38909.4537 | 1 | 0 | 1809.5 | 1882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4544 | 1 | 0 | 38909.4544 | 1 | 0 | 1868 | 1941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.455 | 1 | 0 | 38909.4551 | 1 | 0 | 1927 | 2000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4557 | 1 | 0 | 38909.4557 | 1 | 0 | 1985.5 | 2058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4564 | 1 | 0 | 38909.4564 | 1 | 0 | 2044.5 | 2117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4571 | 1 | 0 | 38909.4571 | 1 | 0 | 2103.5 | 2176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4578 | 1 | 0 | 38909.4578 | 1 | 0 | 2162 | 2235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4584 | 1 | 0 | 38909.4585 | 1 | 0 | 2221 | 2294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4591 | 1 | 0 | 38909.4591 | 1 | 0 | 2279.5 | 2352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38909.4598 | 1 | 0 | 38909.4598 | 1 | 0 | 2338.5 | 2411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 14 |  |  | 2006-07-11 | 10:23
38909.4319 | 1 | 0 | 1 | PE | 7-C | Tray
38909.4326 | 1 | 0 | 1 | 300 C | 6.1 kW/m2 |  | Conductors
38909.4333 | 1 | 0 | 1
38909.4339 | 1 | 0 | 1
38909.4346 | 1 | 0 | 1
38909.4353 | 1 | 0 | 1
38909.436 | 1 | 0 | 1
38909.4367 | 1 | 0 | 1
38909.4373 | 1 | 0 | 1
38909.438 | 1 | 0 | 1
38909.4387 | 1 | 0 | 1
38909.4394 | 1 | 0 | 1
38909.4401 | 1 | 0 | 1
38909.4408 | 1 | 0 | 1
38909.4414 | 1 | 0 | 1
38909.4421 | 1 | 0 | 1
38909.4428 | 1 | 0 | 1
38909.4435 | 1 | 1 | 1
38909.4442 | 1 | 0 | 1
38909.4448 | 1 | 0 | 1
38909.4455 | 1 | 0 | 1
38909.4462 | 1 | 0 | 1
38909.4469 | 1 | 0 | 1
38909.4476 | 1 | 0 | 1
38909.4482 | 1 | 0 | 1
38909.4489 | 1 | 0 | 1
38909.4496 | 1 | 0 | 1
38909.4503 | 1 | 0 | 1
38909.451 | 1 | 0 | 1
38909.4516 | 1 | 0 | 1
38909.4523 | 1 | 0 | 1
38909.453 | 1 | 0 | 1
38909.4537 | 1 | 0 | 1
38909.4544 | 1 | 0 | 1
38909.455 | 1 | 0 | 1
38909.4557 | 1 | 0 | 1
38909.4564 | 1 | 0 | 1
38909.4571 | 1 | 0 | 1
38909.4578 | 1 | 0 | 1
38909.4584 | 1 | 0 | 1
38909.4591 | 1 | 0 | 1
38909.4598 | 1 | 0 | 1
38909.4319 | 1 | 0 | 2
38909.4326 | 1 | 0 | 2
38909.4333 | 1 | 0 | 2
38909.434 | 1 | 0 | 2
38909.4346 | 1 | 0 | 2
38909.4353 | 1 | 0 | 2
38909.436 | 1 | 0 | 2
38909.4367 | 1 | 0 | 2
38909.4374 | 1 | 0 | 2
38909.438 | 1 | 0 | 2
38909.4387 | 1 | 0 | 2
38909.4394 | 1 | 0 | 2
38909.4401 | 1 | 0 | 2
38909.4408 | 1 | 0 | 2
38909.4414 | 1 | 0 | 2
38909.4421 | 1 | 0 | 2
38909.4428 | 1 | 0 | 2
38909.4435 | 1 | 0 | 2
38909.4442 | 1 | 0 | 2
38909.4448 | 1 | 0 | 2
38909.4455 | 1 | 0 | 2
38909.4462 | 1 | 0 | 2
38909.4469 | 1 | 0 | 2
38909.4476 | 1 | 0 | 2
38909.4483 | 1 | 0 | 2
38909.4489 | 1 | 0 | 2
38909.4496 | 1 | 0 | 2
38909.4503 | 1 | 0 | 2
38909.451 | 1 | 0 | 2
38909.4517 | 1 | 0 | 2
38909.4523 | 1 | 0 | 2
38909.453 | 1 | 0 | 2
38909.4537 | 1 | 0 | 2
38909.4544 | 1 | 0 | 2
38909.4551 | 1 | 0 | 2
38909.4557 | 1 | 0 | 2
38909.4564 | 1 | 0 | 2
38909.4571 | 1 | 0 | 2
38909.4578 | 1 | 0 | 2
38909.4585 | 1 | 0 | 2
38909.4591 | 1 | 0 | 2
38909.4598 | 1 | 0 | 2
38909.4319 | 1 | 0 | 3
38909.4326 | 1 | 0 | 3
38909.4333 | 1 | 0 | 3
38909.434 | 1 | 0 | 3
38909.4347 | 1 | 0 | 3
38909.4353 | 1 | 0 | 3
38909.436 | 1 | 0 | 3
38909.4367 | 1 | 0 | 3
38909.4374 | 1 | 0 | 3
38909.4381 | 1 | 0 | 3
38909.4387 | 1 | 0 | 3
38909.4394 | 1 | 0 | 3
38909.4401 | 1 | 0 | 3
38909.4408 | 1 | 0 | 3
38909.4415 | 1 | 0 | 3
38909.4421 | 1 | 0 | 3
38909.4428 | 1 | 0 | 3
38909.4435 | 1 | 0 | 3
38909.4442 | 1 | 0 | 3
38909.4449 | 1 | 0 | 3
38909.4455 | 1 | 0 | 3
38909.4462 | 1 | 0 | 3
38909.4469 | 1 | 0 | 3
38909.4476 | 1 | 0 | 3
38909.4483 | 1 | 0 | 3
38909.4489 | 1 | 0 | 3
38909.4496 | 1 | 0 | 3
38909.4503 | 1 | 0 | 3
38909.451 | 1 | 0 | 3
38909.4517 | 1 | 0 | 3
38909.4523 | 1 | 0 | 3
38909.453 | 1 | 0 | 3
38909.4537 | 1 | 0 | 3
38909.4544 | 1 | 0 | 3
38909.4551 | 1 | 0 | 3
38909.4558 | 1 | 0 | 3
38909.4564 | 1 | 0 | 3
38909.4571 | 1 | 0 | 3
38909.4578 | 1 | 0 | 3
38909.4585 | 1 | 0 | 3
38909.4592 | 1 | 0 | 3
38909.4598 | 1 | 0 | 3
38909.432 | 1 | 0 | 4
38909.4326 | 1 | 0 | 4
38909.4333 | 1 | 0 | 4
38909.434 | 1 | 0 | 4
38909.4347 | 1 | 0 | 4
38909.4354 | 1 | 0 | 4
38909.436 | 1 | 0 | 4
38909.4367 | 1 | 0 | 4
38909.4374 | 1 | 0 | 4
38909.4381 | 1 | 0 | 4
38909.4388 | 1 | 0 | 4
38909.4394 | 1 | 0 | 4
38909.4401 | 1 | 0 | 4
38909.4408 | 1 | 0 | 4
38909.4415 | 1 | 0 | 4
38909.4422 | 1 | 0 | 4
38909.4428 | 1 | 0 | 4
38909.4435 | 1 | 0 | 4
38909.4442 | 1 | 0 | 4
38909.4449 | 1 | 0 | 4
38909.4456 | 1 | 0 | 4
38909.4462 | 1 | 0 | 4
38909.4469 | 1 | 0 | 4
38909.4476 | 1 | 0 | 4
38909.4483 | 1 | 0 | 4
38909.449 | 1 | 0 | 4
38909.4496 | 1 | 0 | 4
38909.4503 | 1 | 0 | 4
38909.451 | 1 | 0 | 4
38909.4517 | 1 | 0 | 4
38909.4524 | 1 | 0 | 4
38909.4537 | 1 | 0 | 4
38909.4544 | 1 | 0 | 4
38909.4551 | 1 | 0 | 4
38909.4558 | 1 | 0 | 4
38909.4564 | 1 | 0 | 4
38909.4571 | 1 | 0 | 4
38909.4578 | 1 | 0 | 4
38909.4585 | 1 | 0 | 4
38909.4592 | 1 | 0 | 4
38909.4598 | 16 | 0 | 4
38909.432 | 1 | 0 | 5
38909.4327 | 1 | 0 | 5
38909.4333 | 1 | 0 | 5
38909.434 | 1 | 0 | 5
38909.4347 | 1 | 0 | 5
38909.4354 | 1 | 0 | 5
38909.4361 | 1 | 0 | 5
38909.4367 | 1 | 0 | 5
38909.4374 | 1 | 0 | 5
38909.4381 | 1 | 0 | 5
38909.4388 | 1 | 0 | 5
38909.4395 | 1 | 0 | 5
38909.4401 | 1 | 0 | 5
38909.4408 | 1 | 0 | 5
38909.4415 | 1 | 0 | 5
38909.4422 | 1 | 0 | 5
38909.4429 | 1 | 0 | 5
38909.4435 | 1 | 0 | 5
38909.4442 | 1 | 0 | 5
38909.4449 | 1 | 0 | 5
38909.4456 | 1 | 0 | 5
38909.4463 | 1 | 0 | 5
38909.4469 | 1 | 0 | 5
38909.4476 | 1 | 0 | 5
38909.4483 | 1 | 0 | 5
38909.449 | 1 | 0 | 5
38909.4497 | 1 | 0 | 5
38909.4503 | 1 | 0 | 5
38909.451 | 1 | 0 | 5
38909.4517 | 1 | 0 | 5
38909.4524 | 1 | 0 | 5
38909.4531 | 1 | 0 | 5
38909.4537 | 1 | 0 | 5
38909.4544 | 1 | 1 | 5
38909.4551 | 1 | 0 | 5
38909.4558 | 1 | 0 | 5
38909.4565 | 1 | 0 | 5
38909.4571 | 1 | 0 | 5
38909.4578 | 1 | 0 | 5
38909.4585 | 1 | 0 | 5
38909.4592 | 1 | 0 | 5
38909.4599 | 1 | 0 | 5
38909.432 | 1 | 0 | 6
38909.4327 | 1 | 0 | 6
38909.4333 | 1 | 0 | 6
38909.434 | 1 | 0 | 6
38909.4347 | 1 | 0 | 6
38909.4354 | 1 | 0 | 6
38909.4361 | 1 | 0 | 6
38909.4367 | 1 | 0 | 6
38909.4374 | 1 | 0 | 6
38909.4381 | 1 | 0 | 6
38909.4388 | 1 | 0 | 6
38909.4395 | 1 | 0 | 6
38909.4402 | 1 | 0 | 6
38909.4408 | 1 | 0 | 6
38909.4415 | 1 | 0 | 6
38909.4422 | 1 | 0 | 6
38909.4429 | 1 | 0 | 6
38909.4436 | 1 | 0 | 6
38909.4442 | 1 | 0 | 6
38909.4449 | 1 | 0 | 6
38909.4456 | 1 | 0 | 6
38909.4463 | 1 | 0 | 6
38909.447 | 1 | 0 | 6
38909.4476 | 1 | 0 | 6
38909.4483 | 1 | 0 | 6
38909.449 | 1 | 0 | 6
38909.4497 | 1 | 0 | 6
38909.4504 | 1 | 0 | 6
38909.451 | 1 | 0 | 6
38909.4517 | 1 | 0 | 6
38909.4524 | 1 | 0 | 6
38909.4531 | 1 | 0 | 6
38909.4538 | 1 | 0 | 6
38909.4544 | 1 | 0 | 6
38909.4551 | 1 | 0 | 6
38909.4558 | 1 | 0 | 6
38909.4565 | 1 | 0 | 6
38909.4572 | 1 | 0 | 6
38909.4578 | 1 | 0 | 6
38909.4585 | 1 | 0 | 6
38909.4592 | 1 | 0 | 6
38909.4599 | 1 | 0 | 6
38909.432 | 1 | 0 | 7
38909.4327 | 1 | 0 | 7
38909.4334 | 1 | 0 | 7
38909.434 | 1 | 0 | 7
38909.4347 | 1 | 0 | 7
38909.4354 | 1 | 0 | 7
38909.4361 | 1 | 0 | 7
38909.4368 | 1 | 0 | 7
38909.4374 | 1 | 0 | 7
38909.4381 | 1 | 0 | 7
38909.4388 | 1 | 0 | 7
38909.4395 | 1 | 0 | 7
38909.4402 | 1 | 0 | 7
38909.4408 | 1 | 0 | 7
38909.4415 | 1 | 0 | 7
38909.4422 | 1 | 0 | 7
38909.4429 | 1 | 0 | 7
38909.4436 | 1 | 0 | 7
38909.4442 | 1 | 0 | 7
38909.4449 | 1 | 0 | 7
38909.4456 | 1 | 0 | 7
38909.4463 | 1 | 0 | 7
38909.447 | 1 | 0 | 7
38909.4477 | 1 | 0 | 7
38909.4483 | 1 | 0 | 7
38909.449 | 1 | 0 | 7
38909.4497 | 1 | 0 | 7
38909.4504 | 1 | 0 | 7
38909.4511 | 1 | 0 | 7
38909.4517 | 1 | 0 | 7
38909.4524 | 1 | 0 | 7
38909.4531 | 1 | 0 | 7
38909.4538 | 1 | 0 | 7
38909.4545 | 1 | 0 | 7
38909.4551 | 1 | 0 | 7
38909.4558 | 1 | 0 | 7
38909.4565 | 1 | 0 | 7
38909.4572 | 1 | 0 | 7
38909.4579 | 1 | 0 | 7
38909.4585 | 1 | 0 | 7
38909.4592 | 1 | 0 | 7
38909.4599 | 1 | 0 | 7
38909.432 | 1 | 0 | 8
38909.4327 | 1 | 0 | 8
38909.4334 | 1 | 0 | 8
38909.4341 | 1 | 0 | 8
38909.4347 | 1 | 0 | 8
38909.4354 | 1 | 0 | 8
38909.4361 | 1 | 0 | 8
38909.4368 | 1 | 0 | 8
38909.4375 | 1 | 0 | 8
38909.4381 | 1 | 0 | 8
38909.4388 | 1 | 0 | 8
38909.4395 | 1 | 0 | 8
38909.4402 | 1 | 0 | 8
38909.4409 | 1 | 0 | 8
38909.4415 | 1 | 0 | 8
38909.4422 | 1 | 0 | 8
38909.4429 | 1 | 0 | 8
38909.4436 | 1 | 0 | 8
38909.4443 | 1 | 1 | 8
38909.4449 | 1 | 0 | 8
38909.4456 | 1 | 0 | 8
38909.4463 | 1 | 0 | 8
38909.447 | 1 | 0 | 8
38909.4477 | 1 | 0 | 8
38909.4483 | 1 | 0 | 8
38909.449 | 1 | 0 | 8
38909.4497 | 1 | 0 | 8
38909.4504 | 1 | 0 | 8
38909.4511 | 1 | 0 | 8
38909.4517 | 1 | 0 | 8
38909.4524 | 1 | 0 | 8
38909.4531 | 1 | 0 | 8
38909.4538 | 1 | 0 | 8
38909.4545 | 1 | 0 | 8
38909.4552 | 1 | 0 | 8
38909.4558 | 1 | 0 | 8
38909.4565 | 1 | 0 | 8
38909.4572 | 1 | 0 | 8
38909.4579 | 1 | 0 | 8
38909.4586 | 1 | 0 | 8
38909.4592 | 1 | 0 | 8
38909.4599 | 1 | 0 | 8
38909.432 | 1 | 0 | 9
38909.4327 | 1 | 0 | 9
38909.4334 | 1 | 0 | 9
38909.4341 | 1 | 0 | 9
38909.4348 | 1 | 0 | 9
38909.4354 | 1 | 0 | 9
38909.4361 | 1 | 0 | 9
38909.4368 | 1 | 0 | 9
38909.4375 | 1 | 0 | 9
38909.4382 | 1 | 0 | 9
38909.4388 | 1 | 0 | 9
38909.4395 | 1 | 0 | 9
38909.4402 | 1 | 0 | 9
38909.4409 | 1 | 0 | 9
38909.4416 | 1 | 0 | 9
38909.4422 | 1 | 0 | 9
38909.4429 | 1 | 0 | 9
38909.4436 | 1 | 0 | 9
38909.4443 | 1 | 0 | 9
38909.445 | 1 | 0 | 9
38909.4456 | 1 | 0 | 9
38909.4463 | 1 | 0 | 9
38909.447 | 1 | 0 | 9
38909.4477 | 1 | 0 | 9
38909.4484 | 1 | 0 | 9
38909.449 | 1 | 0 | 9
38909.4497 | 1 | 0 | 9
38909.4504 | 1 | 0 | 9
38909.4511 | 1 | 0 | 9
38909.4518 | 1 | 0 | 9
38909.4524 | 1 | 0 | 9
38909.4531 | 1 | 0 | 9
38909.4538 | 1 | 0 | 9
38909.4545 | 1 | 0 | 9
38909.4552 | 1 | 0 | 9
38909.4558 | 1 | 0 | 9
38909.4565 | 1 | 0 | 9
38909.4572 | 1 | 0 | 9
38909.4579 | 1 | 0 | 9
38909.4586 | 1 | 0 | 9
38909.4592 | 1 | 0 | 9
38909.4599 | 1 | 0 | 9
38909.432 | 1 | 0 | 10
38909.4327 | 1 | 0 | 10
38909.4334 | 1 | 0 | 10
38909.4341 | 1 | 0 | 10
38909.4348 | 1 | 0 | 10
38909.4355 | 1 | 0 | 10
38909.4361 | 1 | 0 | 10
38909.4368 | 1 | 0 | 10
38909.4375 | 1 | 0 | 10
38909.4382 | 1 | 0 | 10
38909.4389 | 1 | 0 | 10
38909.4395 | 1 | 0 | 10
38909.4402 | 1 | 0 | 10
38909.4409 | 1 | 0 | 10
38909.4416 | 1 | 0 | 10
38909.4423 | 1 | 0 | 10
38909.4429 | 1 | 0 | 10
38909.4436 | 2 | 0 | 10
38909.4443 | 1 | 0 | 10
38909.445 | 1 | 0 | 10
38909.4457 | 1 | 0 | 10
38909.4463 | 1 | 0 | 10
38909.447 | 1 | 0 | 10
38909.4477 | 1 | 0 | 10
38909.4484 | 1 | 0 | 10
38909.4491 | 1 | 0 | 10
38909.4497 | 1 | 0 | 10
38909.4504 | 1 | 0 | 10
38909.4511 | 1 | 0 | 10
38909.4518 | 1 | 0 | 10
38909.4525 | 1 | 0 | 10
38909.4531 | 1 | 0 | 10
38909.4538 | 1 | 0 | 10
38909.4545 | 1 | 0 | 10
38909.4552 | 1 | 0 | 10
38909.4559 | 1 | 0 | 10
38909.4565 | 1 | 0 | 10
38909.4572 | 1 | 0 | 10
38909.4579 | 1 | 0 | 10
38909.4586 | 1 | 0 | 10
38909.4593 | 1 | 0 | 10
38909.4599 | 1 | 0 | 10
38909.4321 | 1 | 0 | 11
38909.4327 | 1 | 0 | 11
38909.4334 | 1 | 0 | 11
38909.4341 | 1 | 0 | 11
38909.4348 | 1 | 0 | 11
38909.4355 | 1 | 0 | 11
38909.4361 | 1 | 0 | 11
38909.4368 | 1 | 0 | 11
38909.4375 | 1 | 0 | 11
38909.4382 | 1 | 0 | 11
38909.4389 | 1 | 0 | 11
38909.4395 | 1 | 0 | 11
38909.4402 | 1 | 0 | 11
38909.4409 | 1 | 0 | 11
38909.4416 | 1 | 0 | 11
38909.4423 | 1 | 0 | 11
38909.443 | 1 | 0 | 11
38909.4436 | 1 | 0 | 11
38909.4443 | 1 | 0 | 11
38909.445 | 1 | 0 | 11
38909.4457 | 1 | 0 | 11
38909.4464 | 1 | 0 | 11
38909.447 | 1 | 0 | 11
38909.4477 | 1 | 0 | 11
38909.4484 | 1 | 0 | 11
38909.4491 | 1 | 0 | 11
38909.4498 | 1164 | 1141 | 11
38909.4504 | 1034 | 1000 | 11
38909.4511 | 1013 | 1054 | 11
38909.4518 | 974 | 934 | 11
38909.4525 | 563 | 582 | 11
38909.4532 | 1 | 0 | 11
38909.4538 | 34 | 75 | 11
38909.4545 | 1 | 0 | 11
38909.4552 | 1 | 0 | 11
38909.4559 | 362 | 367 | 11
38909.4566 | 1 | 0 | 11
38909.4572 | 1 | 0 | 11
38909.4579 | 1 | 0 | 11
38909.4586 | 1 | 1 | 11
38909.4593 | 1 | 0 | 11
38909.46 | 1 | 0 | 11
38909.4321 | 1 | 0 | 12
38909.4328 | 1 | 0 | 12
38909.4334 | 1 | 0 | 12
38909.4341 | 1 | 0 | 12
38909.4348 | 1 | 0 | 12
38909.4355 | 1 | 0 | 12
38909.4362 | 1 | 0 | 12
38909.4368 | 1 | 0 | 12
38909.4375 | 1 | 0 | 12
38909.4382 | 1 | 0 | 12
38909.4389 | 1 | 0 | 12
38909.4396 | 1 | 0 | 12
38909.4402 | 1 | 0 | 12
38909.4409 | 1 | 0 | 12
38909.4416 | 1 | 0 | 12
38909.4423 | 2 | 0 | 12
38909.443 | 1 | 0 | 12
38909.4436 | 1 | 0 | 12
38909.4443 | 1 | 0 | 12
38909.445 | 1 | 0 | 12
38909.4457 | 1 | 0 | 12
38909.4464 | 1 | 0 | 12
38909.447 | 1 | 0 | 12
38909.4477 | 1 | 0 | 12
38909.4484 | 1 | 0 | 12
38909.4491 | 1 | 0 | 12
38909.4498 | 1024 | 1065 | 12
38909.4505 | 1077 | 1045 | 12
38909.4511 | 1122 | 1093 | 12
38909.4518 | 1185 | 1177 | 12
38909.4525 | 981 | 970 | 12
38909.4532 | 1 | 0 | 12
38909.4539 | 274 | 210 | 12
38909.4545 | 1 | 0 | 12
38909.4552 | 1 | 0 | 12
38909.4559 | 787 | 815 | 12
38909.4566 | 1 | 0 | 12
38909.4573 | 1 | 0 | 12
38909.4579 | 1 | 0 | 12
38909.4586 | 1 | 0 | 12
38909.4593 | 1 | 0 | 12
38909.46 | 1 | 0 | 12
38909.4321 | 1 | 0 | 13
38909.4328 | 1 | 0 | 13
38909.4335 | 1 | 0 | 13
38909.4341 | 1 | 0 | 13
38909.4348 | 1 | 0 | 13
38909.4355 | 1 | 0 | 13
38909.4362 | 1 | 0 | 13
38909.4369 | 1 | 0 | 13
38909.4375 | 1 | 0 | 13
38909.4382 | 1 | 0 | 13
38909.4389 | 1 | 0 | 13
38909.4396 | 1 | 0 | 13
38909.4403 | 1 | 0 | 13
38909.4409 | 1 | 0 | 13
38909.4416 | 1 | 0 | 13
38909.4423 | 1 | 0 | 13
38909.443 | 1 | 0 | 13
38909.4437 | 1 | 0 | 13
38909.4443 | 1 | 0 | 13
38909.445 | 1 | 0 | 13
38909.4457 | 1 | 0 | 13
38909.4464 | 1 | 0 | 13
38909.4471 | 1 | 0 | 13
38909.4477 | 1 | 0 | 13
38909.4484 | 1 | 0 | 13
38909.4491 | 1 | 0 | 13
38909.4498 | 4 | 13 | 13
38909.4505 | 4 | 13 | 13
38909.4511 | 5 | 11 | 13
38909.4518 | 4 | 13 | 13
38909.4525 | 2 | 3 | 13
38909.4532 | 1 | 0 | 13
38909.4539 | 2 | 3 | 13
38909.4545 | 1 | 0 | 13
38909.4552 | 1 | 0 | 13
38909.4559 | 3 | 9 | 13
38909.4566 | 1 | 0 | 13
38909.4573 | 1 | 0 | 13
38909.458 | 1 | 0 | 13
38909.4586 | 1 | 0 | 13
38909.4593 | 1 | 0 | 13
38909.46 | 1 | 0 | 13
38909.4321 | 1 | 0 | 14
38909.4328 | 1 | 0 | 14
38909.4335 | 1 | 0 | 14
38909.4342 | 1 | 0 | 14
38909.4348 | 1 | 0 | 14
38909.4355 | 1 | 0 | 14
38909.4362 | 1 | 0 | 14
38909.4369 | 1 | 0 | 14
38909.4376 | 1 | 0 | 14
38909.4382 | 1 | 0 | 14
38909.4389 | 1 | 0 | 14
38909.4396 | 1 | 0 | 14
38909.4403 | 1 | 0 | 14
38909.441 | 1 | 0 | 14
38909.4416 | 1 | 0 | 14
38909.4423 | 1 | 0 | 14
38909.443 | 1 | 0 | 14
38909.4437 | 1 | 0 | 14
38909.4444 | 1 | 0 | 14
38909.445 | 1 | 0 | 14
38909.4457 | 2 | 0 | 14
38909.4464 | 1 | 0 | 14
38909.4471 | 1 | 0 | 14
38909.4478 | 1 | 0 | 14
38909.4484 | 1 | 0 | 14
38909.4491 | 1 | 0 | 14
38909.4498 | 3 | 9 | 14
38909.4505 | 2 | 9 | 14
38909.4512 | 3 | 7 | 14
38909.4519 | 2 | 8 | 14
38909.4525 | 2 | 1 | 14
38909.4532 | 1 | 0 | 14
38909.4539 | 2 | 1 | 14
38909.4546 | 1 | 0 | 14
38909.4553 | 1 | 0 | 14
38909.4559 | 2 | 3 | 14
38909.4566 | 1 | 0 | 14
38909.4573 | 1 | 0 | 14
38909.458 | 1 | 0 | 14
38909.4586 | 1 | 0 | 14
38909.4593 | 1 | 0 | 14
38909.46 | 1 | 0 | 14
38909.4321 | 1 | 0 | 15
38909.4328 | 1 | 0 | 15
38909.4335 | 1 | 0 | 15
38909.4342 | 1 | 0 | 15
38909.4348 | 1 | 0 | 15
38909.4355 | 1 | 0 | 15
38909.4362 | 1 | 0 | 15
38909.4369 | 1 | 0 | 15
38909.4376 | 1 | 0 | 15
38909.4383 | 1 | 0 | 15
38909.4389 | 1 | 0 | 15
38909.4396 | 1 | 0 | 15
38909.4403 | 1 | 0 | 15
38909.441 | 1 | 0 | 15
38909.4417 | 1 | 0 | 15
38909.4423 | 1 | 0 | 15
38909.443 | 1 | 0 | 15
38909.4437 | 1 | 0 | 15
38909.4444 | 1 | 0 | 15
38909.4451 | 1 | 0 | 15
38909.4457 | 1 | 0 | 15
38909.4464 | 1 | 0 | 15
38909.4471 | 2 | 0 | 15
38909.4478 | 1 | 0 | 15
38909.4485 | 1 | 0 | 15
38909.4491 | 1 | 0 | 15
38909.4498 | 2 | 7 | 15
38909.4505 | 2 | 5 | 15
38909.4512 | 2 | 5 | 15
38909.4519 | 2 | 7 | 15
38909.4525 | 1 | 0 | 15
38909.4532 | 1 | 0 | 15
38909.4539 | 2 | 1 | 15
38909.4546 | 1 | 0 | 15
38909.4553 | 1 | 0 | 15
38909.4559 | 1 | 1 | 15
38909.4566 | 2 | 0 | 15
38909.4573 | 1 | 0 | 15
38909.458 | 1 | 0 | 15
38909.4587 | 1 | 0 | 15
38909.4594 | 1 | 0 | 15
38909.46 | 1 | 0 | 15
38909.4321 | 1 | 0 | 16
38909.4328 | 1 | 0 | 16
38909.4335 | 1 | 0 | 16
38909.4342 | 1 | 0 | 16
38909.4349 | 1 | 0 | 16
38909.4355 | 1 | 0 | 16
38909.4362 | 1 | 0 | 16
38909.4369 | 1 | 0 | 16
38909.4376 | 1 | 0 | 16
38909.4383 | 1 | 0 | 16
38909.4389 | 1 | 0 | 16
38909.4396 | 1 | 0 | 16
38909.4403 | 1 | 0 | 16
38909.441 | 1 | 0 | 16
38909.4417 | 1 | 0 | 16
38909.4423 | 1 | 0 | 16
38909.443 | 1 | 0 | 16
38909.4437 | 1 | 0 | 16
38909.4444 | 1 | 0 | 16
38909.4451 | 1 | 0 | 16
38909.4458 | 1 | 0 | 16
38909.4464 | 1 | 0 | 16
38909.4471 | 1 | 0 | 16
38909.4478 | 1 | 0 | 16
38909.4485 | 1 | 0 | 16
38909.4492 | 1 | 0 | 16
38909.4498 | 2 | 5 | 16
38909.4505 | 2 | 4 | 16
38909.4512 | 2 | 4 | 16
38909.4519 | 2 | 5 | 16
38909.4526 | 1 | 1 | 16
38909.4532 | 1 | 0 | 16
38909.4539 | 1 | 1 | 16
38909.4546 | 1 | 0 | 16
38909.4553 | 1 | 0 | 16
38909.456 | 2 | 1 | 16
38909.4566 | 1 | 0 | 16
38909.4573 | 1 | 0 | 16
38909.458 | 1 | 0 | 16
38909.4587 | 1 | 0 | 16
38909.4594 | 1 | 0 | 16
38909.46 | 1 | 0 | 16
38909.4322 | 1 | 0 | 17
38909.4328 | 1 | 0 | 17
38909.4335 | 1 | 0 | 17
38909.4342 | 1 | 0 | 17
38909.4349 | 1 | 0 | 17
38909.4356 | 1 | 0 | 17
38909.4362 | 1 | 0 | 17
38909.4369 | 1 | 0 | 17
38909.4376 | 1 | 0 | 17
38909.4383 | 1 | 0 | 17
38909.439 | 1 | 0 | 17
38909.4397 | 1 | 0 | 17
38909.4403 | 1 | 0 | 17
38909.441 | 1 | 0 | 17
38909.4417 | 1 | 0 | 17
38909.4424 | 1 | 0 | 17
38909.443 | 1 | 0 | 17
38909.4437 | 1 | 1 | 17
38909.4444 | 1 | 0 | 17
38909.4451 | 1 | 0 | 17
38909.4458 | 1 | 0 | 17
38909.4464 | 1 | 0 | 17
38909.4471 | 1 | 0 | 17
38909.4478 | 1 | 0 | 17
38909.4485 | 1 | 0 | 17
38909.4492 | 1 | 0 | 17
38909.4498 | 2 | 4 | 17
38909.4505 | 2 | 3 | 17
38909.4512 | 1 | 3 | 17
38909.4519 | 1 | 2 | 17
38909.4526 | 1 | 0 | 17
38909.4533 | 1 | 0 | 17
38909.4539 | 1 | 1 | 17
38909.4546 | 1 | 0 | 17
38909.4553 | 1 | 0 | 17
38909.456 | 1 | 1 | 17
38909.4567 | 1 | 1 | 17
38909.4573 | 1 | 0 | 17
38909.458 | 1 | 0 | 17
38909.4587 | 1 | 0 | 17
38909.4594 | 1 | 0 | 17
38909.4601 | 1 | 0 | 17
38909.4322 | 1 | 0 | 18
38909.4329 | 1 | 0 | 18
38909.4335 | 1 | 0 | 18
38909.4342 | 1 | 0 | 18
38909.4349 | 1 | 0 | 18
38909.4356 | 1 | 0 | 18
38909.4363 | 1 | 0 | 18
38909.4369 | 1 | 0 | 18
38909.4376 | 1 | 0 | 18
38909.4383 | 1 | 0 | 18
38909.439 | 1 | 0 | 18
38909.4397 | 1 | 0 | 18
38909.4403 | 1 | 0 | 18
38909.441 | 1 | 0 | 18
38909.4417 | 1 | 0 | 18
38909.4424 | 1 | 0 | 18
38909.4431 | 1 | 0 | 18
38909.4437 | 1 | 0 | 18
38909.4444 | 1 | 0 | 18
38909.4451 | 1 | 0 | 18
38909.4458 | 1 | 0 | 18
38909.4465 | 1 | 0 | 18
38909.4472 | 1 | 0 | 18
38909.4478 | 1 | 0 | 18
38909.4485 | 1 | 0 | 18
38909.4492 | 1 | 0 | 18
38909.4499 | 1 | 2 | 18
38909.4506 | 2 | 2 | 18
38909.4512 | 1 | 3 | 18
38909.4519 | 2 | 1 | 18
38909.4526 | 1 | 0 | 18
38909.4533 | 1 | 0 | 18
38909.4539 | 1 | 0 | 18
38909.4546 | 1 | 0 | 18
38909.4553 | 1 | 0 | 18
38909.456 | 1 | 0 | 18
38909.4567 | 1 | 0 | 18
38909.4573 | 1 | 0 | 18
38909.458 | 1 | 0 | 18
38909.4587 | 1 | 0 | 18
38909.4594 | 1 | 0 | 18
38909.4601 | 1 | 0 | 18
38909.4322 | 1 | 0 | 19
38909.4329 | 1 | 0 | 19
38909.4336 | 1 | 0 | 19
38909.4342 | 1 | 0 | 19
38909.4349 | 1 | 0 | 19
38909.4356 | 1 | 0 | 19
38909.4363 | 1 | 0 | 19
38909.437 | 1 | 0 | 19
38909.4376 | 1 | 0 | 19
38909.4383 | 1 | 0 | 19
38909.439 | 1 | 0 | 19
38909.4397 | 1 | 0 | 19
38909.4404 | 1 | 0 | 19
38909.441 | 1 | 0 | 19
38909.4417 | 1 | 0 | 19
38909.4424 | 1 | 1 | 19
38909.4431 | 1 | 0 | 19
38909.4438 | 1 | 0 | 19
38909.4444 | 1 | 0 | 19
38909.4451 | 1 | 0 | 19
38909.4458 | 2 | 0 | 19
38909.4465 | 1 | 0 | 19
38909.4472 | 1 | 0 | 19
38909.4478 | 1 | 0 | 19
38909.4485 | 1 | 0 | 19
38909.4492 | 1 | 0 | 19
38909.4499 | 2 | 1 | 19
38909.4506 | 1 | 1 | 19
38909.4512 | 2 | 1 | 19
38909.4519 | 1 | 1 | 19
38909.4526 | 1 | 0 | 19
38909.4533 | 1 | 0 | 19
38909.454 | 1 | 0 | 19
38909.4547 | 1 | 0 | 19
38909.4553 | 1 | 0 | 19
38909.456 | 1 | 1 | 19
38909.4567 | 1 | 0 | 19
38909.4574 | 1 | 0 | 19
38909.4581 | 1 | 0 | 19
38909.4587 | 1 | 0 | 19
38909.4594 | 1 | 0 | 19
38909.4601 | 1 | 0 | 19
38909.4322 | 1 | 0 | 20
38909.4329 | 1 | 0 | 20
38909.4336 | 1 | 0 | 20
38909.4342 | 1 | 0 | 20
38909.4349 | 1 | 0 | 20
38909.4356 | 1 | 0 | 20
38909.4363 | 1 | 0 | 20
38909.437 | 1 | 0 | 20
38909.4377 | 1 | 0 | 20
38909.4383 | 1 | 0 | 20
38909.439 | 1 | 0 | 20
38909.4397 | 1 | 0 | 20
38909.4404 | 1 | 0 | 20
38909.4411 | 1 | 0 | 20
38909.4417 | 1 | 0 | 20
38909.4424 | 1 | 0 | 20
38909.4431 | 1 | 1 | 20
38909.4438 | 1 | 0 | 20
38909.4445 | 1 | 0 | 20
38909.4451 | 1 | 0 | 20
38909.4458 | 1 | 0 | 20
38909.4465 | 1 | 0 | 20
38909.4472 | 1 | 0 | 20
38909.4479 | 1 | 0 | 20
38909.4485 | 1 | 0 | 20
38909.4492 | 1 | 0 | 20
38909.4499 | 1 | 1 | 20
38909.4506 | 1 | 1 | 20
38909.4513 | 2 | 1 | 20
38909.4519 | 2 | 1 | 20
38909.4526 | 1 | 0 | 20
38909.4533 | 1 | 0 | 20
38909.454 | 1 | 0 | 20
38909.4547 | 1 | 0 | 20
38909.4553 | 1 | 0 | 20
38909.456 | 1 | 0 | 20
38909.4567 | 1 | 0 | 20
38909.4574 | 1 | 0 | 20
38909.4581 | 1 | 0 | 20
38909.4587 | 1 | 0 | 20
38909.4594 | 1 | 0 | 20
38909.4601 | 1 | 0 | 20
38909.4322 | 1 | 0 | 21
38909.4329 | 1 | 0 | 21
38909.4336 | 1 | 0 | 21
38909.4343 | 1 | 0 | 21
38909.435 | 1 | 0 | 21
38909.4356 | 1 | 0 | 21
38909.4363 | 1 | 0 | 21
38909.437 | 1 | 0 | 21
38909.4377 | 1 | 0 | 21
38909.4383 | 1 | 0 | 21
38909.439 | 1 | 0 | 21
38909.4397 | 1 | 0 | 21
38909.4404 | 1 | 0 | 21
38909.4411 | 1 | 0 | 21
38909.4417 | 1 | 1 | 21
38909.4424 | 1 | 0 | 21
38909.4431 | 1 | 0 | 21
38909.4438 | 1 | 0 | 21
38909.4445 | 1 | 0 | 21
38909.4452 | 1 | 0 | 21
38909.4458 | 1 | 0 | 21
38909.4465 | 1 | 0 | 21
38909.4472 | 1 | 0 | 21
38909.4479 | 1 | 0 | 21
38909.4486 | 1 | 0 | 21
38909.4492 | 1 | 0 | 21
38909.4499 | 1 | 1 | 21
38909.4506 | 2 | 1 | 21
38909.4513 | 2 | 1 | 21
38909.452 | 1 | 0 | 21
38909.4526 | 1 | 0 | 21
38909.4533 | 1 | 0 | 21
38909.454 | 1 | 1 | 21
38909.4547 | 1 | 0 | 21
38909.4554 | 1 | 0 | 21
38909.456 | 1 | 0 | 21
38909.4567 | 1 | 0 | 21
38909.4574 | 1 | 0 | 21
38909.4581 | 1 | 0 | 21
38909.4588 | 1 | 0 | 21
38909.4594 | 1 | 0 | 21
38909.4601 | 1 | 0 | 21
38909.4322 | 1 | 0 | 22
38909.4329 | 1 | 0 | 22
38909.4336 | 1 | 0 | 22
38909.4343 | 1 | 0 | 22
38909.435 | 1 | 0 | 22
38909.4356 | 1 | 0 | 22
38909.4363 | 1 | 0 | 22
38909.437 | 1 | 0 | 22
38909.4377 | 1 | 0 | 22
38909.4384 | 1 | 0 | 22
38909.4391 | 1 | 0 | 22
38909.4397 | 1 | 0 | 22
38909.4404 | 1 | 0 | 22
38909.4411 | 1 | 0 | 22
38909.4418 | 1 | 0 | 22
38909.4425 | 1 | 0 | 22
38909.4431 | 1 | 0 | 22
38909.4438 | 1 | 0 | 22
38909.4445 | 1 | 0 | 22
38909.4452 | 1 | 0 | 22
38909.4459 | 1 | 0 | 22
38909.4465 | 1 | 0 | 22
38909.4472 | 1 | 0 | 22
38909.4479 | 1 | 0 | 22
38909.4486 | 1 | 0 | 22
38909.4493 | 1 | 0 | 22
38909.4499 | 1 | 0 | 22
38909.4506 | 1 | 1 | 22
38909.4513 | 2 | 1 | 22
38909.452 | 2 | 1 | 22
38909.4527 | 1 | 0 | 22
38909.4533 | 1 | 0 | 22
38909.454 | 1 | 0 | 22
38909.4547 | 1 | 0 | 22
38909.4554 | 1 | 0 | 22
38909.4561 | 1 | 0 | 22
38909.4567 | 1 | 0 | 22
38909.4574 | 1 | 0 | 22
38909.4581 | 1 | 0 | 22
38909.4588 | 1 | 0 | 22
38909.4595 | 1 | 0 | 22
38909.4601 | 1 | 0 | 22
38909.4323 | 1 | 0 | 23
38909.4329 | 1 | 0 | 23
38909.4336 | 1 | 0 | 23
38909.4343 | 1 | 0 | 23
38909.435 | 1 | 0 | 23
38909.4357 | 1 | 0 | 23
38909.4363 | 1 | 0 | 23
38909.437 | 1 | 0 | 23
38909.4377 | 1 | 0 | 23
38909.4384 | 1 | 0 | 23
38909.4391 | 1 | 0 | 23
38909.4397 | 1 | 0 | 23
38909.4404 | 1 | 0 | 23
38909.4411 | 1 | 0 | 23
38909.4418 | 1 | 0 | 23
38909.4425 | 1 | 0 | 23
38909.4431 | 1 | 0 | 23
38909.4438 | 1 | 0 | 23
38909.4445 | 1 | 0 | 23
38909.4452 | 1 | 0 | 23
38909.4459 | 1 | 0 | 23
38909.4466 | 1 | 0 | 23
38909.4472 | 1 | 0 | 23
38909.4479 | 1 | 0 | 23
38909.4486 | 1 | 0 | 23
38909.4493 | 1 | 0 | 23
38909.45 | 1 | 1 | 23
38909.4506 | 1 | 1 | 23
38909.4513 | 1 | 1 | 23
38909.452 | 1 | 1 | 23
38909.4527 | 1 | 0 | 23
38909.4534 | 1 | 0 | 23
38909.454 | 1 | 0 | 23
38909.4547 | 1 | 0 | 23
38909.4554 | 1 | 0 | 23
38909.4561 | 1 | 0 | 23
38909.4568 | 1 | 0 | 23
38909.4574 | 1 | 0 | 23
38909.4581 | 1 | 0 | 23
38909.4588 | 1 | 0 | 23
38909.4595 | 1 | 0 | 23
38909.4602 | 1 | 0 | 23
38909.4323 | 1 | 0 | 24
38909.433 | 1 | 0 | 24
38909.4336 | 1 | 0 | 24
38909.4343 | 1 | 0 | 24
38909.435 | 1 | 0 | 24
38909.4357 | 1 | 0 | 24
38909.4364 | 1 | 0 | 24
38909.437 | 1 | 0 | 24
38909.4377 | 1 | 0 | 24
38909.4384 | 1 | 0 | 24
38909.4391 | 1 | 0 | 24
38909.4398 | 1 | 0 | 24
38909.4404 | 1 | 0 | 24
38909.4411 | 1 | 0 | 24
38909.4418 | 1 | 0 | 24
38909.4425 | 1 | 0 | 24
38909.4432 | 1 | 0 | 24
38909.4438 | 1 | 0 | 24
38909.4445 | 1 | 0 | 24
38909.4452 | 1 | 0 | 24
38909.4459 | 1 | 0 | 24
38909.4466 | 1 | 0 | 24
38909.4472 | 1 | 0 | 24
38909.4479 | 1 | 0 | 24
38909.4486 | 1 | 0 | 24
38909.4493 | 1 | 0 | 24
38909.45 | 1 | 0 | 24
38909.4506 | 1 | 1 | 24
38909.4513 | 1 | 1 | 24
38909.452 | 1 | 0 | 24
38909.4527 | 1 | 0 | 24
38909.4534 | 1 | 0 | 24
38909.4541 | 1 | 0 | 24
38909.4547 | 1 | 0 | 24
38909.4554 | 1 | 0 | 24
38909.4561 | 1 | 0 | 24
38909.4568 | 1 | 0 | 24
38909.4575 | 1 | 0 | 24
38909.4581 | 1 | 0 | 24
38909.4588 | 1 | 0 | 24
38909.4595 | 1 | 0 | 24
38909.4602 | 1 | 0 | 24
38909.4323 | 1 | 0 | 25
38909.433 | 1 | 0 | 25
38909.4337 | 1 | 0 | 25
38909.4343 | 1 | 0 | 25
38909.435 | 1 | 0 | 25
38909.4357 | 1 | 0 | 25
38909.4364 | 1 | 0 | 25
38909.4371 | 1 | 0 | 25
38909.4377 | 1 | 0 | 25
38909.4384 | 1 | 0 | 25
38909.4391 | 1 | 0 | 25
38909.4398 | 1 | 0 | 25
38909.4405 | 1 | 0 | 25
38909.4411 | 1 | 0 | 25
38909.4418 | 1 | 0 | 25
38909.4425 | 1 | 0 | 25
38909.4432 | 2 | 0 | 25
38909.4439 | 1 | 0 | 25
38909.4445 | 1 | 0 | 25
38909.4452 | 1 | 0 | 25
38909.4459 | 1 | 0 | 25
38909.4466 | 1 | 0 | 25
38909.4473 | 1 | 0 | 25
38909.4479 | 1 | 0 | 25
38909.4486 | 1 | 0 | 25
38909.4493 | 1 | 0 | 25
38909.45 | 1 | 0 | 25
38909.4507 | 1 | 1 | 25
38909.4513 | 1 | 0 | 25
38909.452 | 1 | 0 | 25
38909.4527 | 1 | 0 | 25
38909.4534 | 1 | 0 | 25
38909.4541 | 1 | 0 | 25
38909.4547 | 1 | 0 | 25
38909.4554 | 1 | 0 | 25
38909.4561 | 1 | 1 | 25
38909.4568 | 1 | 0 | 25
38909.4575 | 1 | 0 | 25
38909.4581 | 1 | 0 | 25
38909.4588 | 1 | 0 | 25
38909.4595 | 1 | 0 | 25
38909.4602 | 1 | 0 | 25
38909.4323 | 1 | 0 | 26
38909.433 | 1 | 0 | 26
38909.4337 | 1 | 0 | 26
38909.4344 | 1 | 0 | 26
38909.435 | 1 | 0 | 26
38909.4357 | 1 | 0 | 26
38909.4364 | 1 | 0 | 26
38909.4371 | 1 | 0 | 26
38909.4378 | 1 | 0 | 26
38909.4384 | 1 | 0 | 26
38909.4391 | 1 | 0 | 26
38909.4398 | 1 | 0 | 26
38909.4405 | 1 | 0 | 26
38909.4412 | 1 | 0 | 26
38909.4418 | 1 | 0 | 26
38909.4425 | 1 | 0 | 26
38909.4432 | 1 | 0 | 26
38909.4439 | 1 | 0 | 26
38909.4446 | 1 | 0 | 26
38909.4452 | 1 | 0 | 26
38909.4459 | 1 | 0 | 26
38909.4466 | 1 | 0 | 26
38909.4473 | 1 | 0 | 26
38909.448 | 1 | 0 | 26
38909.4486 | 1 | 0 | 26
38909.4493 | 1 | 0 | 26
38909.45 | 1 | 0 | 26
38909.4507 | 1 | 0 | 26
38909.4514 | 1 | 0 | 26
38909.452 | 1 | 0 | 26
38909.4527 | 1 | 0 | 26
38909.4534 | 2 | 0 | 26
38909.4541 | 1 | 0 | 26
38909.4548 | 1 | 0 | 26
38909.4554 | 1 | 0 | 26
38909.4561 | 1 | 0 | 26
38909.4568 | 1 | 0 | 26
38909.4575 | 1 | 0 | 26
38909.4582 | 1 | 0 | 26
38909.4588 | 1 | 0 | 26
38909.4595 | 1 | 0 | 26
38909.4602 | 1 | 0 | 26
38909.4323 | 1 | 0 | 27
38909.433 | 1 | 0 | 27
38909.4337 | 1 | 0 | 27
38909.4344 | 1 | 0 | 27
38909.435 | 1 | 0 | 27
38909.4357 | 1 | 0 | 27
38909.4364 | 1 | 0 | 27
38909.4371 | 1 | 0 | 27
38909.4384 | 1 | 0 | 27
38909.4391 | 1 | 0 | 27
38909.4398 | 1 | 0 | 27
38909.4405 | 1 | 0 | 27
38909.4412 | 1 | 0 | 27
38909.4419 | 1 | 0 | 27
38909.4425 | 1 | 0 | 27
38909.4432 | 1 | 0 | 27
38909.4439 | 1 | 0 | 27
38909.4446 | 1 | 0 | 27
38909.4453 | 1 | 0 | 27
38909.4459 | 1 | 0 | 27
38909.4466 | 1 | 0 | 27
38909.4473 | 1 | 0 | 27
38909.448 | 1 | 0 | 27
38909.4487 | 1 | 0 | 27
38909.4493 | 1 | 0 | 27
38909.45 | 1 | 0 | 27
38909.4507 | 1 | 0 | 27
38909.4514 | 1 | 1 | 27
38909.4521 | 1 | 1 | 27
38909.4527 | 1 | 0 | 27
38909.4534 | 1 | 0 | 27
38909.4541 | 1 | 0 | 27
38909.4548 | 1 | 0 | 27
38909.4555 | 1 | 0 | 27
38909.4561 | 1 | 0 | 27
38909.4568 | 1 | 0 | 27
38909.4575 | 1 | 0 | 27
38909.4582 | 1 | 0 | 27
38909.4589 | 1 | 0 | 27
38909.4595 | 1 | 0 | 27
38909.4602 | 1 | 0 | 27
38909.4323 | 1 | 0 | 28
38909.433 | 1 | 0 | 28
38909.4337 | 1 | 0 | 28
38909.4344 | 1 | 0 | 28
38909.4351 | 1 | 0 | 28
38909.4357 | 1 | 0 | 28
38909.4364 | 1 | 0 | 28
38909.4371 | 1 | 0 | 28
38909.4378 | 1 | 0 | 28
38909.4385 | 1 | 0 | 28
38909.4391 | 1 | 0 | 28
38909.4398 | 1 | 0 | 28
38909.4405 | 1 | 0 | 28
38909.4412 | 1 | 0 | 28
38909.4419 | 1 | 0 | 28
38909.4425 | 1 | 0 | 28
38909.4432 | 1 | 0 | 28
38909.4439 | 1 | 0 | 28
38909.4446 | 1 | 0 | 28
38909.4453 | 1 | 0 | 28
38909.4459 | 1 | 0 | 28
38909.4466 | 1 | 0 | 28
38909.4473 | 1 | 0 | 28
38909.448 | 1 | 0 | 28
38909.4487 | 1 | 0 | 28
38909.4494 | 1 | 0 | 28
38909.45 | 1 | 0 | 28
38909.4507 | 1 | 1 | 28
38909.4514 | 1 | 0 | 28
38909.4521 | 1 | 0 | 28
38909.4528 | 1 | 0 | 28
38909.4534 | 1 | 0 | 28
38909.4541 | 1 | 0 | 28
38909.4548 | 1 | 0 | 28
38909.4555 | 1 | 0 | 28
38909.4562 | 1 | 0 | 28
38909.4568 | 1 | 0 | 28
38909.4575 | 1 | 0 | 28
38909.4582 | 1 | 0 | 28
38909.4589 | 1 | 0 | 28
38909.4596 | 1 | 0 | 28
38909.4602 | 1 | 0 | 28
38909.4324 | 1 | 0 | 29
38909.433 | 1 | 0 | 29
38909.4337 | 1 | 0 | 29
38909.4344 | 1 | 0 | 29
38909.4351 | 1 | 0 | 29
38909.4358 | 1 | 0 | 29
38909.4364 | 2 | 0 | 29
38909.4371 | 1 | 0 | 29
38909.4378 | 1 | 0 | 29
38909.4385 | 1 | 0 | 29
38909.4392 | 1 | 0 | 29
38909.4398 | 1 | 0 | 29
38909.4405 | 1 | 0 | 29
38909.4412 | 1 | 0 | 29
38909.4419 | 1 | 0 | 29
38909.4426 | 1 | 0 | 29
38909.4432 | 1 | 0 | 29
38909.4439 | 1 | 0 | 29
38909.4446 | 1 | 0 | 29
38909.4453 | 1 | 0 | 29
38909.446 | 1 | 0 | 29
38909.4466 | 1 | 0 | 29
38909.4473 | 1 | 0 | 29
38909.448 | 1 | 0 | 29
38909.4487 | 1 | 0 | 29
38909.4494 | 1 | 0 | 29
38909.45 | 1 | 0 | 29
38909.4507 | 1 | 1 | 29
38909.4514 | 1 | 0 | 29
38909.4521 | 1 | 0 | 29
38909.4528 | 1 | 0 | 29
38909.4534 | 1 | 1 | 29
38909.4541 | 1 | 0 | 29
38909.4548 | 1 | 0 | 29
38909.4555 | 1 | 0 | 29
38909.4562 | 1 | 0 | 29
38909.4569 | 1 | 0 | 29
38909.4575 | 1 | 0 | 29
38909.4582 | 1 | 0 | 29
38909.4589 | 1 | 0 | 29
38909.4596 | 1 | 0 | 29
38909.4603 | 1271 | 0 | 29
38909.4324 | 1 | 0 | 30
38909.4331 | 1 | 0 | 30
38909.4337 | 1 | 0 | 30
38909.4344 | 1 | 0 | 30
38909.4351 | 1 | 0 | 30
38909.4358 | 1 | 0 | 30
38909.4365 | 1 | 0 | 30
38909.4371 | 1 | 0 | 30
38909.4378 | 1 | 0 | 30
38909.4385 | 1 | 0 | 30
38909.4392 | 1 | 0 | 30
38909.4399 | 1 | 0 | 30
38909.4405 | 1 | 0 | 30
38909.4412 | 1 | 0 | 30
38909.4419 | 1 | 0 | 30
38909.4426 | 1 | 1 | 30
38909.4433 | 1 | 0 | 30
38909.4439 | 1 | 0 | 30
38909.4446 | 1 | 0 | 30
38909.4453 | 1 | 0 | 30
38909.446 | 1 | 0 | 30
38909.4467 | 1 | 0 | 30
38909.4473 | 1 | 0 | 30
38909.448 | 1 | 0 | 30
38909.4487 | 1 | 0 | 30
38909.4494 | 1 | 0 | 30
38909.4501 | 1 | 0 | 30
38909.4507 | 1 | 1 | 30
38909.4514 | 1 | 0 | 30
38909.4521 | 1 | 0 | 30
38909.4528 | 1 | 0 | 30
38909.4535 | 1 | 0 | 30
38909.4541 | 1 | 0 | 30
38909.4548 | 1 | 0 | 30
38909.4555 | 1 | 0 | 30
38909.4562 | 1 | 0 | 30
38909.4569 | 1 | 0 | 30
38909.4575 | 1 | 0 | 30
38909.4582 | 1 | 0 | 30
38909.4589 | 1 | 0 | 30
38909.4596 | 1 | 0 | 30
38909.4603 | 2 | 0 | 30
38909.4324 | 1 | 0 | 31
38909.4331 | 1 | 0 | 31
38909.4337 | 1 | 0 | 31
38909.4344 | 1 | 0 | 31
38909.4351 | 1 | 0 | 31
38909.4358 | 1 | 0 | 31
38909.4365 | 1 | 0 | 31
38909.4372 | 1 | 0 | 31
38909.4378 | 1 | 0 | 31
38909.4385 | 1 | 0 | 31
38909.4392 | 1 | 0 | 31
38909.4399 | 1 | 0 | 31
38909.4406 | 1 | 0 | 31
38909.4412 | 1 | 0 | 31
38909.4419 | 1 | 0 | 31
38909.4426 | 1 | 0 | 31
38909.4433 | 1 | 0 | 31
38909.444 | 1 | 0 | 31
38909.4446 | 1 | 0 | 31
38909.4453 | 1 | 0 | 31
38909.446 | 1 | 0 | 31
38909.4467 | 1 | 0 | 31
38909.4474 | 1 | 0 | 31
38909.448 | 1 | 0 | 31
38909.4487 | 1 | 0 | 31
38909.4494 | 1 | 0 | 31
38909.4501 | 1 | 0 | 31
38909.4508 | 1 | 0 | 31
38909.4514 | 1 | 0 | 31
38909.4521 | 1 | 0 | 31
38909.4528 | 1 | 0 | 31
38909.4535 | 1 | 0 | 31
38909.4542 | 1 | 0 | 31
38909.4548 | 1 | 0 | 31
38909.4555 | 1 | 0 | 31
38909.4562 | 1 | 0 | 31
38909.4569 | 1 | 0 | 31
38909.4576 | 1 | 0 | 31
38909.4582 | 1 | 0 | 31
38909.4589 | 1 | 0 | 31
38909.4596 | 1 | 0 | 31
38909.4603 | 1 | 0 | 31
38909.4324 | 1 | 0 | 32
38909.4331 | 1 | 0 | 32
38909.4338 | 1 | 0 | 32
38909.4344 | 1 | 0 | 32
38909.4351 | 1 | 0 | 32
38909.4358 | 1 | 0 | 32
38909.4365 | 1 | 0 | 32
38909.4372 | 1 | 0 | 32
38909.4378 | 1 | 0 | 32
38909.4385 | 1 | 0 | 32
38909.4392 | 1 | 0 | 32
38909.4399 | 1 | 0 | 32
38909.4406 | 1 | 0 | 32
38909.4413 | 1 | 0 | 32
38909.4419 | 1 | 0 | 32
38909.4426 | 1 | 0 | 32
38909.4433 | 1 | 0 | 32
38909.444 | 1 | 0 | 32
38909.4447 | 1 | 0 | 32
38909.4453 | 1 | 0 | 32
38909.446 | 1 | 0 | 32
38909.4467 | 1 | 0 | 32
38909.4474 | 1 | 0 | 32
38909.4481 | 1 | 0 | 32
38909.4487 | 1 | 0 | 32
38909.4494 | 1 | 0 | 32
38909.4501 | 1 | 0 | 32
38909.4508 | 1 | 0 | 32
38909.4515 | 1 | 0 | 32
38909.4521 | 1 | 0 | 32
38909.4528 | 1 | 0 | 32
38909.4535 | 1 | 0 | 32
38909.4542 | 1 | 0 | 32
38909.4549 | 1 | 0 | 32
38909.4555 | 1 | 0 | 32
38909.4562 | 1 | 1 | 32
38909.4569 | 1 | 0 | 32
38909.4576 | 1 | 0 | 32
38909.4583 | 1 | 0 | 32
38909.4589 | 1 | 0 | 32
38909.4596 | 1 | 0 | 32
38909.4603 | 1 | 0 | 32
38909.4324 | 1 | 0 | 33
38909.4331 | 1 | 0 | 33
38909.4338 | 1 | 0 | 33
38909.4345 | 1 | 0 | 33
38909.4351 | 1 | 0 | 33
38909.4358 | 1 | 0 | 33
38909.4365 | 1 | 0 | 33
38909.4372 | 1 | 0 | 33
38909.4379 | 1 | 0 | 33
38909.4385 | 1 | 0 | 33
38909.4392 | 1 | 0 | 33
38909.4399 | 1 | 0 | 33
38909.4406 | 1 | 0 | 33
38909.4413 | 1 | 0 | 33
38909.4419 | 1 | 0 | 33
38909.4426 | 1 | 0 | 33
38909.4433 | 1 | 0 | 33
38909.444 | 1 | 0 | 33
38909.4447 | 1 | 0 | 33
38909.4453 | 1 | 0 | 33
38909.446 | 1 | 0 | 33
38909.4467 | 1 | 0 | 33
38909.4474 | 1 | 0 | 33
38909.4481 | 1 | 0 | 33
38909.4488 | 1 | 0 | 33
38909.4494 | 1 | 0 | 33
38909.4501 | 1 | 0 | 33
38909.4508 | 1 | 0 | 33
38909.4515 | 1 | 0 | 33
38909.4522 | 1 | 1 | 33
38909.4528 | 1 | 0 | 33
38909.4535 | 1 | 0 | 33
38909.4542 | 1 | 0 | 33
38909.4549 | 1 | 0 | 33
38909.4556 | 1 | 0 | 33
38909.4562 | 1 | 0 | 33
38909.4569 | 1 | 0 | 33
38909.4576 | 1 | 0 | 33
38909.4583 | 1 | 0 | 33
38909.459 | 1 | 0 | 33
38909.4596 | 1 | 0 | 33
38909.4603 | 1 | 0 | 33
38909.4324 | 1 | 0 | 34
38909.4331 | 1 | 0 | 34
38909.4338 | 1 | 0 | 34
38909.4345 | 1 | 0 | 34
38909.4352 | 1 | 0 | 34
38909.4358 | 1 | 0 | 34
38909.4365 | 1 | 0 | 34
38909.4372 | 1 | 0 | 34
38909.4379 | 1 | 0 | 34
38909.4386 | 1 | 0 | 34
38909.4392 | 1 | 0 | 34
38909.4399 | 1 | 0 | 34
38909.4406 | 1 | 0 | 34
38909.4413 | 1 | 0 | 34
38909.442 | 1 | 0 | 34
38909.4426 | 1 | 0 | 34
38909.4433 | 1 | 1 | 34
38909.444 | 1 | 0 | 34
38909.4447 | 1 | 0 | 34
38909.4454 | 1 | 0 | 34
38909.446 | 1 | 0 | 34
38909.4467 | 1 | 0 | 34
38909.4474 | 1 | 0 | 34
38909.4481 | 1 | 0 | 34
38909.4488 | 1 | 0 | 34
38909.4494 | 1 | 0 | 34
38909.4501 | 1 | 0 | 34
38909.4508 | 1 | 0 | 34
38909.4515 | 1 | 0 | 34
38909.4522 | 1 | 0 | 34
38909.4528 | 1 | 0 | 34
38909.4535 | 1 | 0 | 34
38909.4542 | 1 | 0 | 34
38909.4549 | 1 | 0 | 34
38909.4556 | 1 | 0 | 34
38909.4563 | 1 | 0 | 34
38909.4569 | 1 | 0 | 34
38909.4576 | 1 | 0 | 34
38909.4583 | 1 | 0 | 34
38909.459 | 1 | 0 | 34
38909.4597 | 1 | 0 | 34
38909.4603 | 1 | 0 | 34
38909.4325 | 1 | 0 | 35
38909.4331 | 1 | 0 | 35
38909.4338 | 1 | 0 | 35
38909.4345 | 1 | 0 | 35
38909.4352 | 1 | 0 | 35
38909.4359 | 1 | 0 | 35
38909.4365 | 1 | 0 | 35
38909.4372 | 1 | 0 | 35
38909.4379 | 1 | 0 | 35
38909.4386 | 1 | 0 | 35
38909.4393 | 1 | 0 | 35
38909.4399 | 1 | 0 | 35
38909.4406 | 1 | 0 | 35
38909.4413 | 1 | 0 | 35
38909.442 | 1 | 0 | 35
38909.4427 | 1 | 0 | 35
38909.4433 | 1 | 0 | 35
38909.444 | 1 | 0 | 35
38909.4447 | 1 | 0 | 35
38909.4454 | 1 | 0 | 35
38909.4461 | 1 | 0 | 35
38909.4467 | 1 | 0 | 35
38909.4474 | 1 | 0 | 35
38909.4481 | 1 | 0 | 35
38909.4488 | 1 | 0 | 35
38909.4495 | 1 | 0 | 35
38909.4502 | 1 | 0 | 35
38909.4508 | 1 | 0 | 35
38909.4515 | 1 | 0 | 35
38909.4522 | 1 | 1 | 35
38909.4529 | 1 | 0 | 35
38909.4536 | 1 | 0 | 35
38909.4542 | 1 | 0 | 35
38909.4549 | 1 | 0 | 35
38909.4556 | 1 | 0 | 35
38909.4563 | 1 | 0 | 35
38909.4569 | 1 | 0 | 35
38909.4576 | 1 | 0 | 35
38909.4583 | 1 | 0 | 35
38909.459 | 1 | 0 | 35
38909.4597 | 1 | 0 | 35
38909.4603 | 1 | 0 | 35
38909.4325 | 1 | 0 | 36
38909.4331 | 1 | 0 | 36
38909.4338 | 1 | 0 | 36
38909.4345 | 1 | 0 | 36
38909.4352 | 1 | 0 | 36
38909.4359 | 1 | 0 | 36
38909.4366 | 1 | 0 | 36
38909.4372 | 1 | 0 | 36
38909.4379 | 1 | 0 | 36
38909.4386 | 1 | 0 | 36
38909.4393 | 1 | 0 | 36
38909.44 | 1 | 0 | 36
38909.4406 | 1 | 0 | 36
38909.4413 | 1 | 0 | 36
38909.442 | 1 | 0 | 36
38909.4427 | 1 | 0 | 36
38909.4434 | 1 | 0 | 36
38909.444 | 1 | 0 | 36
38909.4447 | 1 | 0 | 36
38909.4454 | 1 | 0 | 36
38909.4461 | 1 | 0 | 36
38909.4468 | 1 | 0 | 36
38909.4474 | 1 | 0 | 36
38909.4481 | 1 | 0 | 36
38909.4488 | 1 | 0 | 36
38909.4495 | 1 | 0 | 36
38909.4502 | 1 | 0 | 36
38909.4508 | 1 | 0 | 36
38909.4515 | 1 | 0 | 36
38909.4522 | 1 | 0 | 36
38909.4529 | 1 | 0 | 36
38909.4536 | 1 | 0 | 36
38909.4542 | 1 | 0 | 36
38909.4549 | 1 | 0 | 36
38909.4556 | 1 | 0 | 36
38909.4563 | 1 | 0 | 36
38909.457 | 1 | 0 | 36
38909.4577 | 1 | 0 | 36
38909.4583 | 1 | 0 | 36
38909.459 | 1 | 0 | 36
38909.4597 | 1 | 0 | 36
38909.4604 | 1 | 0 | 36
38909.4325 | 1 | 0 | 37
38909.4332 | 1 | 0 | 37
38909.4338 | 1 | 0 | 37
38909.4345 | 1 | 0 | 37
38909.4352 | 1 | 0 | 37
38909.4359 | 1 | 0 | 37
38909.4366 | 1 | 0 | 37
38909.4372 | 1 | 0 | 37
38909.4379 | 1 | 0 | 37
38909.4386 | 1 | 0 | 37
38909.4393 | 1 | 0 | 37
38909.44 | 1 | 0 | 37
38909.4406 | 1 | 0 | 37
38909.4413 | 1 | 0 | 37
38909.442 | 1 | 0 | 37
38909.4427 | 1 | 0 | 37
38909.4434 | 1 | 0 | 37
38909.4441 | 1 | 0 | 37
38909.4447 | 1 | 0 | 37
38909.4454 | 1 | 0 | 37
38909.4461 | 1 | 0 | 37
38909.4468 | 1 | 0 | 37
38909.4475 | 1 | 0 | 37
38909.4481 | 1 | 0 | 37
38909.4488 | 1 | 0 | 37
38909.4495 | 1 | 0 | 37
38909.4502 | 1 | 0 | 37
38909.4509 | 1 | 0 | 37
38909.4515 | 1 | 0 | 37
38909.4522 | 1 | 0 | 37
38909.4529 | 1 | 0 | 37
38909.4536 | 1 | 0 | 37
38909.4543 | 1 | 0 | 37
38909.4549 | 1 | 0 | 37
38909.4556 | 1 | 0 | 37
38909.4563 | 1 | 0 | 37
38909.457 | 1 | 0 | 37
38909.4577 | 1 | 0 | 37
38909.4583 | 1 | 0 | 37
38909.459 | 1 | 0 | 37
38909.4597 | 1 | 0 | 37
38909.4604 | 1 | 0 | 37
38909.4325 | 1 | 0 | 38
38909.4332 | 1 | 0 | 38
38909.4339 | 1 | 0 | 38
38909.4345 | 1 | 0 | 38
38909.4352 | 1 | 0 | 38
38909.4359 | 1 | 0 | 38
38909.4366 | 1 | 0 | 38
38909.4373 | 1 | 0 | 38
38909.4379 | 1 | 0 | 38
38909.4386 | 1 | 0 | 38
38909.4393 | 1 | 0 | 38
38909.44 | 1 | 0 | 38
38909.4407 | 1 | 0 | 38
38909.4413 | 1 | 0 | 38
38909.442 | 1 | 0 | 38
38909.4427 | 1 | 0 | 38
38909.4434 | 1 | 0 | 38
38909.4441 | 1 | 0 | 38
38909.4447 | 1 | 0 | 38
38909.4454 | 1 | 0 | 38
38909.4461 | 1 | 0 | 38
38909.4468 | 1 | 0 | 38
38909.4475 | 1 | 0 | 38
38909.4481 | 1 | 0 | 38
38909.4488 | 1 | 0 | 38
38909.4495 | 1 | 0 | 38
38909.4502 | 1 | 0 | 38
38909.4509 | 1 | 0 | 38
38909.4516 | 1 | 0 | 38
38909.4522 | 1 | 0 | 38
38909.4529 | 1 | 0 | 38
38909.4536 | 1 | 0 | 38
38909.4543 | 1 | 0 | 38
38909.455 | 1 | 0 | 38
38909.4556 | 1 | 0 | 38
38909.4563 | 1 | 0 | 38
38909.457 | 1 | 0 | 38
38909.4577 | 1 | 0 | 38
38909.4584 | 1 | 0 | 38
38909.459 | 1 | 0 | 38
38909.4597 | 1 | 0 | 38
38909.4604 | 1 | 0 | 38
38909.4325 | 1 | 0 | 39
38909.4332 | 1 | 0 | 39
38909.4339 | 1 | 0 | 39
38909.4346 | 1 | 0 | 39
38909.4352 | 1 | 0 | 39
38909.4359 | 1 | 0 | 39
38909.4366 | 1 | 0 | 39
38909.4373 | 1 | 0 | 39
38909.438 | 1 | 0 | 39
38909.4386 | 1 | 0 | 39
38909.4393 | 1 | 0 | 39
38909.44 | 1 | 0 | 39
38909.4407 | 1 | 0 | 39
38909.4414 | 1 | 0 | 39
38909.442 | 1 | 0 | 39
38909.4427 | 1 | 0 | 39
38909.4434 | 1 | 0 | 39
38909.4441 | 1 | 0 | 39
38909.4448 | 1 | 0 | 39
38909.4455 | 1 | 0 | 39
38909.4461 | 1 | 0 | 39
38909.4468 | 1 | 0 | 39
38909.4475 | 1 | 0 | 39
38909.4482 | 1 | 0 | 39
38909.4489 | 1 | 0 | 39
38909.4495 | 1 | 0 | 39
38909.4502 | 1 | 0 | 39
38909.4509 | 1 | 0 | 39
38909.4516 | 1 | 0 | 39
38909.4522 | 1 | 0 | 39
38909.4529 | 1 | 0 | 39
38909.4536 | 1 | 0 | 39
38909.4543 | 1 | 0 | 39
38909.455 | 1 | 0 | 39
38909.4557 | 1 | 0 | 39
38909.4563 | 1 | 0 | 39
38909.457 | 1 | 0 | 39
38909.4577 | 1 | 0 | 39
38909.4584 | 1 | 0 | 39
38909.4591 | 1 | 0 | 39
38909.4597 | 1 | 0 | 39
38909.4604 | 1 | 0 | 39
38909.4325 | 1 | 0 | 40
38909.4332 | 1 | 0 | 40
38909.4339 | 1 | 0 | 40
38909.4346 | 1 | 0 | 40
38909.4353 | 1 | 0 | 40
38909.4359 | 1 | 0 | 40
38909.4366 | 2 | 1 | 40
38909.4373 | 1 | 0 | 40
38909.438 | 1 | 0 | 40
38909.4387 | 1 | 0 | 40
38909.4393 | 1 | 0 | 40
38909.44 | 1 | 0 | 40
38909.4407 | 1 | 0 | 40
38909.4414 | 1 | 0 | 40
38909.4421 | 1 | 1 | 40
38909.4427 | 1 | 0 | 40
38909.4434 | 1 | 0 | 40
38909.4441 | 1 | 0 | 40
38909.4448 | 1 | 0 | 40
38909.4455 | 1 | 0 | 40
38909.4461 | 1 | 0 | 40
38909.4468 | 1 | 0 | 40
38909.4475 | 1 | 0 | 40
38909.4482 | 1 | 0 | 40
38909.4489 | 1 | 0 | 40
38909.4495 | 1 | 0 | 40
38909.4502 | 1 | 0 | 40
38909.4509 | 1 | 0 | 40
38909.4516 | 1 | 0 | 40
38909.4523 | 1 | 0 | 40
38909.453 | 1 | 0 | 40
38909.4536 | 1 | 0 | 40
38909.4543 | 1 | 0 | 40
38909.455 | 1 | 0 | 40
38909.4557 | 1 | 0 | 40
38909.4564 | 1 | 0 | 40
38909.457 | 1 | 0 | 40
38909.4577 | 1 | 0 | 40
38909.4584 | 1 | 0 | 40
38909.4591 | 1 | 0 | 40
38909.4598 | 1 | 0 | 40
38909.4604 | 1 | 0 | 40
38909.4325 | 1 | 0 | 41
38909.4332 | 1 | 0 | 41
38909.4339 | 1 | 0 | 41
38909.4346 | 1 | 0 | 41
38909.4353 | 1 | 0 | 41
38909.4359 | 1 | 0 | 41
38909.4366 | 1 | 0 | 41
38909.4373 | 1 | 0 | 41
38909.438 | 1 | 0 | 41
38909.4387 | 1 | 0 | 41
38909.4394 | 1 | 0 | 41
38909.44 | 1 | 0 | 41
38909.4407 | 1 | 0 | 41
38909.4414 | 1 | 0 | 41
38909.4421 | 1 | 0 | 41
38909.4428 | 1 | 0 | 41
38909.4434 | 1 | 0 | 41
38909.4441 | 1 | 0 | 41
38909.4448 | 1 | 0 | 41
38909.4455 | 1 | 0 | 41
38909.4462 | 1 | 0 | 41
38909.4468 | 1 | 0 | 41
38909.4475 | 1 | 0 | 41
38909.4482 | 1 | 0 | 41
38909.4489 | 1 | 0 | 41
38909.4496 | 1 | 0 | 41
38909.4502 | 1 | 0 | 41
38909.4509 | 1 | 0 | 41
38909.4516 | 1 | 0 | 41
38909.4523 | 1 | 0 | 41
38909.453 | 1 | 0 | 41
38909.4536 | 1 | 0 | 41
38909.4543 | 1 | 0 | 41
38909.455 | 1 | 0 | 41
38909.4557 | 1 | 0 | 41
38909.4564 | 1 | 0 | 41
38909.457 | 1 | 0 | 41
38909.4577 | 1 | 0 | 41
38909.4584 | 1 | 0 | 41
38909.4591 | 1 | 0 | 41
38909.4598 | 1 | 0 | 41
38909.4605 | 1 | 0 | 41
38909.4326 | 1 | 0 | 42
38909.4333 | 1 | 0 | 42
38909.4339 | 1 | 0 | 42
38909.4346 | 1 | 0 | 42
38909.4353 | 1 | 0 | 42
38909.436 | 1 | 0 | 42
38909.4367 | 1 | 0 | 42
38909.4373 | 1 | 0 | 42
38909.438 | 1 | 0 | 42
38909.4387 | 1 | 0 | 42
38909.4394 | 1 | 0 | 42
38909.4401 | 1 | 0 | 42
38909.4407 | 1 | 0 | 42
38909.4414 | 1 | 0 | 42
38909.4421 | 1 | 0 | 42
38909.4428 | 1 | 0 | 42
38909.4434 | 1 | 0 | 42
38909.4441 | 1 | 0 | 42
38909.4448 | 1 | 0 | 42
38909.4455 | 1 | 0 | 42
38909.4462 | 1 | 0 | 42
38909.4469 | 1 | 0 | 42
38909.4475 | 1 | 0 | 42
38909.4482 | 1 | 0 | 42
38909.4489 | 1 | 0 | 42
38909.4496 | 1 | 0 | 42
38909.4503 | 1 | 0 | 42
38909.4509 | 1 | 0 | 42
38909.4516 | 1 | 1 | 42
38909.4523 | 1 | 0 | 42
38909.453 | 1 | 0 | 42
38909.4537 | 1 | 0 | 42
38909.4543 | 1 | 0 | 42
38909.455 | 1 | 0 | 42
38909.4557 | 1 | 0 | 42
38909.4564 | 1 | 0 | 42
38909.4571 | 1 | 0 | 42
38909.4577 | 1 | 0 | 42
38909.4584 | 1 | 0 | 42
38909.4591 | 1 | 0 | 42
38909.4598 | 1 | 0 | 42
38909.4605 | 1 | 0 | 42