## Test Facts
Last row in IRMS data sheets: | 36
Time when Penlight power was initiated: | 91

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 15
Test conditions: Cable: 7-conductor, 12 AWG, PE insulated, PVC jacketed, industrial grade control cable. Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 325C, nominal 7.2 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 91 seconds of baseline data monitoring. Special Note: Test setup included a thermocouple on the inner surface of one center tray rung.
DAQ Time | Penlight Time | Event | Interpretation
91 | 0 | Initated Penlight Heating
897-939 | 806-848 | Conductor 7 shorts to conductors 1 & 6 at less than 100 ohms (18 & 63); conductors 4 & 5 short together at less than 100 ohms (69) | Initial failures are by conductor to conductor shorting
953 | 862 | Conductor 1 shorts to conductor 6 at less than 100 ohms (50)
973-977 | 882-886 | Conductors 4 & 5 short to ground at less than 1000 ohms (742 & 625) | Very erratic/intermittent shorting behavior noted for both conductor-to-conductor and ground shorting conditions
1001-1029 | 910-938 | Conductor 2 shorts to conductors 1, 6 & 7 at less than 100 ohms (4, 68 & 51)
1007-1040 | 916-949 | Conductors 1, 6 & 7 all short to ground at less than 1000 ohms (916, 685 & 520)
1137 | 1046 | Conductor 2 shorts to ground at less than 1000 ohms (720)
1165-1171 | 1074-1080 | Conductor 7 shorts to conductors 4 & 5 at less than 100 ohms (15 & 66); conductors 5 & 6 short together at less than 100 ohms (27)
1183-1221 | 1072-1130 | Conductor 1 shorts to conductors 4 & 5 at less than 100 ohms (21 & 55); conductors 4 & 6 short together at less than 100 ohms (66)
1256-1258 | 1165-1167 | Conductor 2 shorts to conductors 4 & 5 at less than 100 ohms (67 & 18)
1301-1334 | 1210-1243 | The existing ground faults on conductors 1, 4, 5, 6 & 7 all degrade to less than 100 ohms (15, <1, <1, 6 & 3)
1415 | 1324 | Conductor 1 shorts to conductor 3 at less than 100 ohms (<1)
1489 | 1398 | The existing ground fault on conductor 2 degrades to less than 100 ohms (14)
1723 | 1632 | Conductor 2 shorts to conductor 3 at less than 100 ohms (<1)
Additional Observations
Observation 1 | The progression of failure modes for this cable did not follow that expected for a typical thermoplastic-insulated cable: shorting to ground followed by conductor-to-conductor shorts.
Observation 2 | It took 806 s (13.4 min.) from the start of Penlight heating for the first conductor-to-conductor short to occur, and it took 882 s (14.7 min.) for the first ground short.
Observation 3 | There were more failures evident at this heat flux than were noted in Test 14.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 15 |  |  | 2006-07-11 | 12:55
PE | 7-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums Overall
-83.0833 | 239538 |  | -71.4167 | 214338 | -63.5833 | 214338 | -58.4167 | 253738 | -55 | 240338 | -52.75 | 246938 | -50.4167 | 233638 | -83.0833 | 214338
-24.3333 | 239538 |  | -12.6667 | 214338 | -4.6667 | 214338 | 0.5 | 253738 | 3.6667 | 47987.6 | 6 | 246938 | 8.3333 | 233638 | -24.3333 | 47987.6
34.5 | 239538 |  | 46.1667 | 214338 | 54.1667 | 214338 | 59.25 | 126919 | 62.5 | 240338 | 64.8333 | 246938 | 67.0833 | 127469 | 34.5 | 126919
93.3333 | 239538 |  | 105 | 121819 | 112.8333 | 214338 | 118.0833 | 126919 | 121.25 | 240338 | 123.5833 | 246938 | 126.0833 | 233638 | 93.3333 | 121819
152.0833 | 239538 |  | 163.75 | 214338 | 171.75 | 214338 | 176.8333 | 127169 | 180.0833 | 240338 | 182.5 | 246938 | 184.8333 | 233638 | 152.0833 | 127169
210.9167 | 239538 |  | 222.5833 | 214338 | 230.4167 | 214338 | 235.5833 | 253738 | 239 | 240338 | 241.25 | 246938 | 243.5833 | 233638 | 210.9167 | 214338
269.6667 | 239538 |  | 281.3333 | 214338 | 289.3333 | 107119 | 294.5 | 253738 | 297.6667 | 240338 | 300 | 246938 | 302.3333 | 233638 | 269.6667 | 107119
328.5 | 239538 |  | 340.1667 | 214338 | 348.1667 | 214338 | 353.25 | 253738 | 356.5 | 126819 | 358.8333 | 246938 | 361.0833 | 127469 | 328.5 | 126819
387.3333 | 239538 |  | 399 | 214338 | 406.8333 | 214338 | 412 | 253738 | 415.25 | 126819 | 417.5833 | 246938 | 420 | 233638 | 387.3333 | 126819
446.0833 | 239538 |  | 457.6667 | 214338 | 465.6667 | 214338 | 470.75 | 253738 | 474 | 240338 | 476.5 | 246938 | 478.6667 | 233638 | 446.0833 | 214338
504.8333 | 239538 |  | 516.5833 | 214338 | 524.4167 | 214338 | 529.5833 | 253738 | 533 | 126819 | 535.25 | 246938 | 537.5 | 125069 | 504.8333 | 125069
563.5833 | 239538 |  | 575.3333 | 214338 | 583.25 | 214338 | 588.4167 | 253738 | 591.6667 | 240338 | 594 | 246938 | 596.25 | 233638 | 563.5833 | 214338
622.5 | 239538 |  | 634.0833 | 214338 | 642 | 214338 | 647.1667 | 253738 | 650.5 | 240338 | 652.8333 | 246938 | 655.0833 | 125019 | 622.5 | 125019
681.3333 | 239538 |  | 692.9167 | 214338 | 700.8333 | 214338 | 706 | 253738 | 709.25 | 240338 | 711.5 | 246938 | 714 | 233638 | 681.3333 | 214338
740.0833 | 239538 |  | 751.75 | 214338 | 759.6667 | 214338 | 764.5833 | 253738 | 768 | 240338 | 770.4167 | 246938 | 772.6667 | 233638 | 740.0833 | 214338
798.8333 | 1966.6903 |  | 810.5833 | 42931.4639 | 818.3333 | 71668.5829 | 823.5833 | 9420.7888 | 827 | 6521.231 | 829.0833 | 14127.7316 | 831.4167 | 5046.1106 | 798.8333 | 1966.6903
857.6667 | 3951.5774 |  | 869.25 | 30697.1203 | 877.25 | 43043.9099 | 882.4167 | 742.4262 | 885.5 | 625.5079 | 888 | 14681.015 | 890.25 | 5053.9975 | 857.6667 | 625.5079
916.4167 | 915.7705 |  | 928 | 3595.8037 | 935.9167 | 36350.1791 | 941.0833 | 1574.581 | 944.3333 | 3001.546 | 946.6667 | 685.0546 | 949.0833 | 519.6966 | 916.4167 | 519.6966
975.25 | 863.4509 |  | 986.8333 | 1757.5871 | 994.75 | 28271.9495 | 999.8333 | 2658.2362 | 1003.0833 | 63384.5 | 1005.5 | 5791.4856 | 1007.9167 | 2238.8704 | 975.25 | 863.4509
1033.9167 | 1705.5714 |  | 1045.75 | 720.4919 | 1053.5 | 43043.9363 | 1058.5833 | 2113.8225 | 1062 | 2765.4512 | 1064.3333 | 365.6736 | 1066.5833 | 336.9423 | 1033.9167 | 336.9423
1092.75 | 1377.1548 |  | 1104.3333 | 30734 | 1112.3333 | 30734 | 1117.5 | 638.1479 | 1120.75 | 1493.7448 | 1123 | 3134.4421 | 1125.3333 | 617.9077 | 1092.75 | 617.9077
1151.5 | 658.9496 |  | 1163.25 | 4470.8327 | 1171.1667 | 35862.0174 | 1176.3333 | 3519.0738 | 1179.5 | 1652.3663 | 1181.8333 | 1281.2731 | 1184.0833 | 4277.7746 | 1151.5 | 658.9496
1210.3333 | 14.9354 |  | 1222 | 882.5563 | 1229.8333 | 4579.4425 | 1235.0833 | 0.64977 | 1238.25 | 0.66661 | 1240.5833 | 5.8443 | 1243.0833 | 3.4599 | 1210.3333 | 0.64977
1269.0833 | 2.3229 |  | 1280.75 | 1671.7154 | 1288.75 | 2507.3087 | 1293.75 | 1.0081 | 1297.0833 | 8.0854 | 1299.5 | 0.65187 | 1301.75 | 0.72653 | 1269.0833 | 0.65187
1327.9167 | 0.68824 |  | 1339.5833 | 1892.7899 | 1347.4167 | 71379.3333 | 1352.5833 | 3.9861 | 1356 | 0.68593 | 1358.25 | 0.70852 | 1360.5833 | 1.9267 | 1327.9167 | 0.68593
1386.6667 | 0.64336 |  | 1398.3333 | 14.2477 | 1406.3333 | 71379.3333 | 1411.5 | 0.64884 | 1414.6667 | 0.65129 | 1417 | 0.64615 | 1419.3333 | 2.0893 | 1386.6667 | 0.64336
1445.5 | 9.9405 |  | 1457.1667 | 18772.5059 | 1465.1667 | 1657.9416 | 1470.25 | 0.65775 | 1473.5 | 0.65889 | 1475.8333 | 7.0249 | 1478.0833 | 0.65253 | 1445.5 | 0.65253
1504.3333 | 1364.1722 |  | 1516 | 1961.3889 | 1523.8333 | 6887.3633 | 1529.0833 | 2.789 | 1532.25 | 2.0971 | 1534.5833 | 1002.8482 | 1537.0833 | 240.7963 | 1504.3333 | 2.0971
1563.0833 | 8441.2667 |  | 1574.5833 | 8233.8878 | 1582.5833 | 8920.4813 | 1587.75 | 3.6422 | 1591.0833 | 8.7787 | 1593.5 | 13.3443 | 1595.75 | 7.8808 | 1563.0833 | 3.6422
1621.9167 | 0.64377 |  | 1633.5833 | 0.76974 | 1641.4167 | 9115.0235 | 1646.5833 | 3.8704 | 1650 | 5.4504 | 1652.25 | 0.64542 | 1654.5833 | 11.2299 | 1621.9167 | 0.64377
1680.6667 | 0.98525 |  | 1692.3333 | 0.6411 | 1700.3333 | 36555.3808 | 1705.5 | 16.2355 | 1708.6667 | 33.4284 | 1711 | 1.0902 | 1713.3333 | 15.9415 | 1680.6667 | 0.6411

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 15 |  |  | 2006-07-11 | 12:55
PE | 7-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | Minimums
-83.0833 | 109552106.74 |  | -71.4167 | 240904.6667 | -63.5833 | 243938 | -58.4167 | 254921.3333 | -55 | 251588 | -52.75 | 254238 | -50.4167 | 250004.6667 | -83.0833 | 240904.6667
-24.3333 | 250338 |  | -12.6667 | 240904.6667 | -4.6667 | 243938 | 0.5 | 254921.3333 | 3.6667 | 198376.4333 | 6 | 254238 | 8.3333 | 250004.6667 | -24.3333 | 198376.4333
34.5 | 250338 |  | 46.1667 | 240904.6667 | 54.1667 | 243938 | 59.25 | 233751.5 | 62.5 | 251588 | 64.8333 | 254238 | 67.0833 | 228743.1667 | 34.5 | 228743.1667
93.3333 | 250338 |  | 105 | 220584.8333 | 112.8333 | 243938 | 118.0833 | 233751.5 | 121.25 | 251588 | 123.5833 | 254238 | 126.0833 | 250004.6667 | 93.3333 | 220584.8333
152.0833 | 250338 |  | 163.75 | 240904.6667 | 171.75 | 243938 | 176.8333 | 233709.8333 | 180.0833 | 251588 | 182.5 | 254238 | 184.8333 | 250004.6667 | 152.0833 | 233709.8333
210.9167 | 250338 |  | 222.5833 | 240904.6667 | 230.4167 | 243938 | 235.5833 | 254921.3333 | 239 | 251588 | 241.25 | 254238 | 243.5833 | 250004.6667 | 210.9167 | 240904.6667
269.6667 | 250338 |  | 281.3333 | 240904.6667 | 289.3333 | 226068.1667 | 294.5 | 254921.3333 | 297.6667 | 251588 | 300 | 254238 | 302.3333 | 250004.6667 | 269.6667 | 226068.1667
328.5 | 250338 |  | 340.1667 | 240904.6667 | 348.1667 | 243938 | 353.25 | 254921.3333 | 356.5 | 230434.8333 | 358.8333 | 254238 | 361.0833 | 228743.1667 | 328.5 | 228743.1667
387.3333 | 250338 |  | 399 | 240904.6667 | 406.8333 | 243938 | 412 | 254921.3333 | 415.25 | 230434.8333 | 417.5833 | 254238 | 420 | 250004.6667 | 387.3333 | 230434.8333
446.0833 | 250338 |  | 457.6667 | 240904.6667 | 465.6667 | 243938 | 470.75 | 254921.3333 | 474 | 251588 | 476.5 | 254238 | 478.6667 | 250004.6667 | 446.0833 | 240904.6667
504.8333 | 250338 |  | 516.5833 | 240904.6667 | 524.4167 | 243938 | 529.5833 | 254921.3333 | 533 | 230434.8333 | 535.25 | 254238 | 537.5 | 229143.1667 | 504.8333 | 229143.1667
563.5833 | 250338 |  | 575.3333 | 240904.6667 | 583.25 | 243938 | 588.4167 | 254921.3333 | 591.6667 | 251588 | 594 | 254238 | 596.25 | 250004.6667 | 563.5833 | 240904.6667
622.5 | 250338 |  | 634.0833 | 240904.6667 | 642 | 243938 | 647.1667 | 254921.3333 | 650.5 | 251588 | 652.8333 | 254238 | 655.0833 | 229151.5 | 622.5 | 229151.5
681.3333 | 250338 |  | 692.9167 | 240904.6667 | 700.8333 | 243938 | 706 | 254921.3333 | 709.25 | 251588 | 711.5 | 254238 | 714 | 250004.6667 | 681.3333 | 240904.6667
740.0833 | 250338 |  | 751.75 | 240904.6667 | 759.6667 | 243938 | 764.5833 | 254921.3333 | 768 | 251588 | 770.4167 | 254238 | 772.6667 | 250004.6667 | 740.0833 | 240904.6667
798.8333 | 208959.4484 |  | 810.5833 | 242075347.094 | 818.3333 | 220159.7638 | 823.5833 | 180287.3623 | 827 | 210368.532 | 829.0833 | 109189030.627 | 831.4167 | 108619889.0394 | 798.8333 | 180287.3623
857.6667 | 266579734.4896 |  | 869.25 | 201171920.0934 | 877.25 | 323364619.205 | 882.4167 | 148965.3139 | 885.5 | 309683086.4776 | 888 | 155311.6769 | 890.25 | 108617534.1779 | 857.6667 | 148965.3139
916.4167 | 69856.1452 |  | 928 | 62251.7841 | 935.9167 | 109163475.38 | 941.0833 | 100291.6146 | 944.3333 | 200589139.7572 | 946.6667 | 97352.3457 | 949.0833 | 128485.0508 | 916.4167 | 62251.7841
975.25 | 54774623.2513 |  | 986.8333 | 59326.6823 | 994.75 | 114336.1319 | 999.8333 | 121778.005 | 1003.0833 | 104387922.3329 | 1005.5 | 109107534.8782 | 1007.9167 | 108536353.0384 | 975.25 | 59326.6823
1033.9167 | 54794810.9435 |  | 1045.75 | 91038111.9622 | 1053.5 | 374086293.5903 | 1058.5833 | 83482.8275 | 1062 | 128319.0311 | 1064.3333 | 87751.8197 | 1066.5833 | 85596.9273 | 1033.9167 | 83482.8275
1092.75 | 21070.813 |  | 1104.3333 | 61929.4727 | 1112.3333 | 109187042.4057 | 1117.5 | 43198.1808 | 1120.75 | 59291.4477 | 1123 | 101649203.9517 | 1125.3333 | 66403.5852 | 1092.75 | 21070.813
1151.5 | 14070.5938 |  | 1163.25 | 11755.9353 | 1171.1667 | 48510.9727 | 1176.3333 | 16388.276 | 1179.5 | 16994.5442 | 1181.8333 | 269219.8524 | 1184.0833 | 33275.2146 | 1151.5 | 11755.9353
1210.3333 | 94.7884 |  | 1222 | 15077.0983 | 1229.8333 | 14115.8373 | 1235.0833 | 24.2215 | 1238.25 | 18.0309 | 1240.5833 | 22.1267 | 1243.0833 | 74.8092 | 1210.3333 | 18.0309
1269.0833 | 11.8252 |  | 1280.75 | 54646.1638 | 1288.75 | 78103.8636 | 1293.75 | 22.387 | 1297.0833 | 13.6772 | 1299.5 | 27.3038 | 1301.75 | 83.3435 | 1269.0833 | 11.8252
1327.9167 | 11.5984 |  | 1339.5833 | 80655.9094 | 1347.4167 | 93056.8342 | 1352.5833 | 16.3938 | 1356 | 74.5144 | 1358.25 | 11.292 | 1360.5833 | 10.6465 | 1327.9167 | 10.6465
1386.6667 | 11.6882 |  | 1398.3333 | 53744.8422 | 1406.3333 | 88108.1667 | 1411.5 | 11.9419 | 1414.6667 | 8.4559 | 1417 | 18.3282 | 1419.3333 | 13.109 | 1386.6667 | 8.4559
1445.5 | 2209.539 |  | 1457.1667 | 47240.7727 | 1465.1667 | 37465.9673 | 1470.25 | 19.4455 | 1473.5 | 19.8318 | 1475.8333 | 16710.8468 | 1478.0833 | 5889.8075 | 1445.5 | 19.4455
1504.3333 | 65067.3175 |  | 1516 | 1166665.6865 | 1523.8333 | 107588.6957 | 1529.0833 | 12.3146 | 1532.25 | 162.9816 | 1534.5833 | 66319.5984 | 1537.0833 | 49461.5342 | 1504.3333 | 12.3146
1563.0833 | 45688.478 |  | 1574.5833 | 32820.0508 | 1582.5833 | 23995913.4976 | 1587.75 | 14.7345 | 1591.0833 | 23.7234 | 1593.5 | 27840.3792 | 1595.75 | 53777.2234 | 1563.0833 | 14.7345
1621.9167 | 8.4241 |  | 1633.5833 | 20.6485 | 1641.4167 | 62649.6834 | 1646.5833 | 29.8706 | 1650 | 27.1839 | 1652.25 | 15.5613 | 1654.5833 | 19.2138 | 1621.9167 | 8.4241
1680.6667 | 11.9249 |  | 1692.3333 | 5.858 | 1700.3333 | 843352.0135 | 1705.5 | 189.4209 | 1708.6667 | 551.2689 | 1711 | 9.2018 | 1713.3333 | 22.3549 | 1680.6667 | 5.858

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 15 |  |  | 2006-07-11 | 12:55
PE | 7-C | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-90 | 243737.9994 | -87.5 | 239537.9994 | -84.5 | 255937.9994 | -81.5 | 256437.9994 | -79 | 255938.0781 | -76 | 250237.9994 | -73.5 | 214337.9994 | -70.5 | 256337.9994 | -67.5 | 240337.9994 | -65 | 257037.9994 | -62 | 233637.9994 | -59.5 | 253937.9994 | -56.5 | 253037.9994 | -53.5 | 246937.9994 | -51 | 255837.9994 | -48 | 253737.9994 | -45.5 | 254437.9994 | -42.5 | 255137.9994 | -39.5 | 255837.9994 | -37 | 250137.9994 | -34 | 255037.9994 | -90 | 214337.9994
-31.5 | 243737.9994 | -28.5 | 239537.9994 | -25.5 | 255937.9994 | -23 | 256437.9994 | -20 | 256137.9994 | -17.5 | 250237.9994 | -14.5 | 214337.9994 | -11.5 | 256337.9994 | -9 | 240337.9994 | -6 | 257037.9994 | -3.5 | 233637.9994 | -0.5 | 253937.9994 | 2.5 | 253037.9994 | 5 | 246937.9994 | 8 | 255837.9994 | 10.5 | 253737.9994 | 13.5 | 254437.9994 | 16.5 | 255137.9994 | 19 | 255837.9994 | 22 | 250137.9994 | 24.5 | 255037.9994 | -31.5 | 214337.9994
27.5 | 243737.9994 | 30.5 | 239537.9994 | 33 | 255937.9994 | 36 | 256437.9994 | 38.5 | 256137.9994 | 41.5 | 250237.9994 | 44.5 | 214337.9994 | 47 | 256337.9994 | 50 | 240337.9994 | 52.5 | 257037.9994 | 55.5 | 233637.9994 | 58.5 | 253937.9994 | 61 | 253037.9994 | 64 | 246937.9994 | 66.5 | 255837.9994 | 69.5 | 253737.9994 | 72.5 | 254437.9994 | 75 | 255137.9994 | 78 | 255837.9994 | 80.5 | 250137.9994 | 83.5 | 255037.9994 | 27.5 | 214337.9994
86.5 | 243737.9994 | 89 | 239537.9994 | 92 | 255937.9994 | 94.5 | 256437.9994 | 97.5 | 256137.9994 | 100.5 | 250237.9994 | 103 | 214337.9994 | 106 | 256337.9994 | 108.5 | 240337.9994 | 111.5 | 257037.9994 | 114.5 | 233637.9994 | 117 | 253937.9994 | 120 | 253037.9994 | 122.5 | 246937.9994 | 125.5 | 255837.9994 | 128.5 | 253737.9994 | 131 | 254437.9994 | 134 | 255137.9994 | 136.5 | 255837.9994 | 139.5 | 250137.9994 | 142.5 | 255037.9994 | 86.5 | 214337.9994
145 | 243737.9994 | 148 | 239537.9994 | 150.5 | 255937.9994 | 153.5 | 256437.9994 | 156.5 | 256137.9994 | 159 | 250237.9994 | 162 | 214337.9994 | 164.5 | 256337.9994 | 167.5 | 240337.9994 | 170.5 | 257037.9994 | 173 | 233637.9994 | 176 | 253937.9994 | 178.5 | 253037.9994 | 181.5 | 246937.9994 | 184.5 | 255837.9994 | 187 | 253737.9994 | 190 | 127168.9988 | 193 | 255137.9994 | 195.5 | 255837.9994 | 198.5 | 250137.9994 | 201 | 255037.9994 | 145 | 127168.9988
204 | 243737.9994 | 206.5 | 239537.9994 | 209.5 | 255937.9994 | 212.5 | 256437.9994 | 215 | 256137.9994 | 218 | 250237.9994 | 220.5 | 214337.9994 | 223.5 | 256337.9994 | 226.5 | 240337.9994 | 229 | 257037.9994 | 232 | 233637.9994 | 234.5 | 253937.9994 | 237.5 | 253037.9994 | 240.5 | 246937.9994 | 243 | 255837.9994 | 246 | 253737.9994 | 248.5 | 254437.9994 | 251.5 | 255137.9994 | 254.5 | 255837.9994 | 257 | 250137.9994 | 260 | 255037.9994 | 204 | 214337.9994
262.5 | 243737.9994 | 265.5 | 239537.9994 | 268.5 | 255937.9994 | 271 | 256437.9994 | 274 | 256137.9994 | 276.5 | 250237.9994 | 279.5 | 214337.9994 | 282.5 | 256337.9994 | 285 | 240337.9994 | 288 | 257037.9994 | 290.5 | 233637.9994 | 293.5 | 253937.9994 | 296.5 | 253037.9994 | 299 | 246937.9994 | 302 | 255837.9994 | 304.5 | 253737.9994 | 307.5 | 254437.9994 | 310.5 | 255137.9994 | 313 | 255837.9994 | 316 | 250137.9994 | 318.5 | 255037.9994 | 262.5 | 214337.9994
321.5 | 243737.9994 | 324.5 | 239537.9994 | 327 | 255937.9994 | 330 | 256437.9994 | 332.5 | 256137.9994 | 335.5 | 250237.9994 | 338.5 | 214337.9994 | 341 | 256337.9994 | 344 | 240337.9994 | 346.5 | 257037.9994 | 349.5 | 233637.9994 | 352.5 | 253937.9994 | 355 | 253037.9994 | 358 | 246937.9994 | 360.5 | 255837.9994 | 363.5 | 253737.9994 | 366.5 | 254437.9994 | 369 | 255137.9994 | 372 | 255837.9994 | 374.5 | 250137.9994 | 377.5 | 255037.9994 | 321.5 | 214337.9994
380.5 | 243737.9994 | 383 | 239537.9994 | 386 | 255937.9994 | 388.5 | 256437.9994 | 391.5 | 256137.9994 | 394.5 | 250237.9994 | 397 | 214337.9994 | 400 | 256337.9994 | 402.5 | 240337.9994 | 405.5 | 257037.9994 | 408.5 | 233637.9994 | 411 | 253937.9994 | 414 | 253037.9994 | 416.5 | 246937.9994 | 419.5 | 255837.9994 | 422.5 | 253737.9994 | 425 | 254437.9994 | 427.5 | 255137.9994 | 430.5 | 255837.9994 | 433.5 | 250137.9994 | 436.5 | 255037.9994 | 380.5 | 214337.9994
439 | 243737.9994 | 442 | 239537.9994 | 444.5 | 255937.9994 | 447.5 | 256437.9994 | 450.5 | 256137.9994 | 453 | 250237.9994 | 455.5 | 214337.9994 | 458.5 | 256337.9994 | 461.5 | 240337.9994 | 464.5 | 257037.9994 | 467 | 233637.9994 | 470 | 253937.9994 | 472.5 | 253037.9994 | 475.5 | 246937.9994 | 478.5 | 255837.9994 | 481 | 253737.9994 | 484 | 254437.9994 | 486.5 | 255137.9994 | 489.5 | 255837.9994 | 492 | 250137.9994 | 495 | 255037.9994 | 439 | 214337.9994
498 | 243737.9994 | 500.5 | 239537.9994 | 503.5 | 255937.9994 | 506.5 | 256437.9994 | 509 | 256137.9994 | 511.5 | 250237.9994 | 514.5 | 214337.9994 | 517.5 | 256337.9994 | 520.5 | 240337.9994 | 523 | 257037.9994 | 526 | 233637.9994 | 528.5 | 253937.9994 | 531.5 | 253037.9994 | 534.5 | 246937.9994 | 537 | 255837.9994 | 540 | 253737.9994 | 542.5 | 254437.9994 | 545.5 | 255137.9994 | 548.5 | 255837.9994 | 551 | 250137.9994 | 554 | 255037.9994 | 498 | 214337.9994
556.5 | 243737.9994 | 559.5 | 239537.9994 | 562 | 255937.9994 | 565 | 256437.9994 | 568 | 256137.9994 | 570.5 | 250237.9994 | 573.5 | 214337.9994 | 576.5 | 256337.9994 | 579 | 240337.9994 | 582 | 257037.9994 | 584.5 | 233637.9994 | 587.5 | 253937.9994 | 590.5 | 253037.9994 | 593 | 246937.9994 | 595.5 | 255837.9994 | 598.5 | 253737.9994 | 601.5 | 254437.9994 | 604.5 | 255137.9994 | 607 | 255837.9994 | 610 | 250137.9994 | 612.5 | 255037.9994 | 556.5 | 214337.9994
615.5 | 243737.9994 | 618.5 | 239537.9994 | 621 | 255937.9994 | 624 | 256437.9994 | 626.5 | 256137.9994 | 629.5 | 250237.9994 | 632 | 214337.9994 | 635 | 256337.9994 | 638 | 240337.9994 | 640.5 | 257037.9994 | 643.5 | 233637.9994 | 646 | 253937.9994 | 649 | 253037.9994 | 652 | 246937.9994 | 654.5 | 255837.9994 | 657.5 | 253737.9994 | 660.5 | 254437.9994 | 663 | 255137.9994 | 666 | 255837.9994 | 668.5 | 250137.9994 | 671.5 | 255037.9994 | 615.5 | 214337.9994
674.5 | 243737.9994 | 677 | 239537.9994 | 680 | 255937.9994 | 682.5 | 256437.9994 | 685.5 | 256137.9994 | 688.5 | 250237.9994 | 691 | 214337.9994 | 693.5 | 256337.9994 | 696.5 | 240337.9994 | 699.5 | 257037.9994 | 702.5 | 233637.9994 | 705 | 253937.9994 | 708 | 253037.9994 | 710.5 | 246937.9994 | 713.5 | 255837.9994 | 716.5 | 253737.9994 | 719 | 254437.9994 | 722 | 255137.9994 | 724.5 | 255837.9994 | 727.5 | 250137.9994 | 730 | 255037.9994 | 674.5 | 214337.9994
733 | 243737.9994 | 736 | 239537.9994 | 738.5 | 255937.9994 | 741.5 | 256437.9994 | 744.5 | 256137.9994 | 747 | 250237.9994 | 750 | 214337.9994 | 752.5 | 256337.9994 | 755.5 | 240337.9994 | 758.5 | 257037.9994 | 761 | 233637.9994 | 763.5 | 253937.9994 | 766.5 | 253037.9994 | 769.5 | 246937.9994 | 772.5 | 255837.9994 | 775 | 253737.9994 | 777.5 | 254437.9994 | 780.5 | 255137.9994 | 783.5 | 255837.9994 | 786 | 250137.9994 | 789 | 255037.9994 | 733 | 214337.9994
792 | 243737.9994 | 794.5 | 239537.9994 | 797.5 | 255937.9994 | 800.5 | 256437.9994 | 803 | 256137.9994 | 805.5 | 17.7589 | 808.5 | 30462.9233 | 811.5 | 127969.078 | 814.5 | 240138.0832 | 817 | 257037.9994 | 820 | 233438.0856 | 822.5 | 253937.9994 | 825.5 | 253037.9994 | 828 | 246937.9994 | 831 | 255837.9994 | 834 | 68.8453 | 836.5 | 36191.4506 | 839.5 | 127468.9804 | 842.5 | 255637.9609 | 845 | 250137.9994 | 847.5 | 63.0462 | 792 | 17.7589
850.5 | 30329.9749 | 853.5 | 119569.0835 | 856.5 | 255738.0781 | 859 | 256238.078 | 862 | 50.2556 | 864.5 | 24.4453 | 867.5 | 23649.28 | 870 | 51087.9035 | 873 | 120068.9792 | 876 | 256838.0778 | 878.5 | 233438.0856 | 881.5 | 253738.0787 | 884 | 252838.079 | 887 | 246937.9994 | 890 | 255638.0781 | 892.5 | 33.811 | 895.5 | 31655.0437 | 898.5 | 127468.9804 | 901 | 255638.0391 | 903.5 | 249938.0799 | 906.5 | 68.3836 | 850.5 | 24.4453
909.5 | 4.133 | 912 | 23794.2239 | 915 | 51047.717 | 918 | 128019.1169 | 920.5 | 15.7835 | 923.5 | 42.7481 | 926 | 21274.4075 | 929 | 51107.8024 | 931.5 | 120068.9792 | 934.5 | 68.399 | 937.5 | 50.571 | 940 | 25224.3055 | 943 | 42006.642 | 946 | 82146.0944 | 948.5 | 255638.0781 | 951.5 | 27.9633 | 954 | 28115.729 | 957 | 84912.745 | 959.5 | 255538.1172 | 962.5 | 249938.04 | 965.5 | 43.9362 | 909.5 | 4.133
968.5 | 40.0606 | 971 | 23794.3439 | 973.5 | 42523.1235 | 976.5 | 128019.0585 | 979.5 | 35.4812 | 982.5 | 58.4375 | 985 | 21274.4075 | 987.5 | 42573.2075 | 990.5 | 79946.097 | 993.5 | 29.836 | 996 | 3.7251 | 999 | 22931.2365 | 1001.5 | 41990.0867 | 1004.5 | 82146.0944 | 1007.5 | 127769.0586 | 1010 | 62.8424 | 1013 | 28126.7533 | 1016 | 84912.6536 | 1018.5 | 255637.9609 | 1021.5 | 249938.04 | 1024 | 68.2783 | 968.5 | 3.7251
1027 | 20.2772 | 1029.5 | 23794.3439 | 1032.5 | 42506.6514 | 1035.5 | 128019.0779 | 1038 | 52.3128 | 1041 | 59.0371 | 1044 | 21264.3984 | 1046.5 | 51107.8024 | 1049.5 | 120019.1039 | 1052.5 | 125.8959 | 1055 | 233438.0856 | 1057.5 | 253738.0787 | 1060.5 | 252838.079 | 1063.5 | 246638.1619 | 1066 | 255638.0781 | 1069 | 12.9898 | 1071.5 | 3438.5154 | 1074.5 | 14.6676 | 1077.5 | 26.6752 | 1080 | 66.1077 | 1083 | 19.5039 | 1027 | 12.9898
1085.5 | 24184.5707 | 1088.5 | 34048.7253 | 1091.5 | 21.4466 | 1094.5 | 55.4564 | 1097 | 62.5152 | 1099.5 | 55.1845 | 1102.5 | 21244.6757 | 1105.5 | 31867.7694 | 1108 | 39873.4422 | 1111 | 51227.9026 | 1113.5 | 58209.8415 | 1116.5 | 63309.6965 | 1119.5 | 84212.7719 | 1122 | 123368.9798 | 1125 | 255638.0781 | 1127.5 | 65.0966 | 1130.5 | 66.1777 | 1133.5 | 12.1052 | 1136 | 22.933 | 1139 | 23.205 | 1141.5 | 14.2653 | 1085.5 | 12.1052
1144.5 | 35.4837 | 1147.5 | 23774.46 | 1150 | 69.7412 | 1153 | 29.3662 | 1155.5 | 39.5374 | 1158.5 | 47.5694 | 1161.5 | 21254.5325 | 1164.5 | 67.2553 | 1167 | 17.7437 | 1169.5 | 512.6786 | 1172.5 | 185.3681 | 1175.5 | 31567.657 | 1178 | 35977.2733 | 1181 | 35105.855 | 1183.5 | 42456.7488 | 1186.5 | 49.0186 | 1189.5 | 14.9504 | 1192 | 59.4731 | 1195 | 25.6782 | 1197.5 | 45.7543 | 1200.5 | 50.3494 | 1144.5 | 14.9504
1203.5 | 2814.8564 | 1206 | 3713.2413 | 1209 | 26.8926 | 1211.5 | 11.9388 | 1214.5 | 6.4535 | 1217.5 | 7.9994 | 1220 | 26605.3592 | 1223 | 8639.5783 | 1225.5 | 6840.8143 | 1228.5 | 13563.686 | 1231.5 | 11595.2426 | 1234 | 7351.7047 | 1237 | 7673.1128 | 1239.5 | 13379.4451 | 1242.5 | 4340.7886 | 1245.5 | 13.5485 | 1248 | 176.9708 | 1251 | 2417.5678 | 1253.5 | 1288.8944 | 1256.5 | 904.2058 | 1259.5 | 1548.1474 | 1203.5 | 6.4535
1262 | 28284.8915 | 1265 | 5247.9909 | 1267.5 | 5375.1929 | 1270.5 | 5439.3947 | 1273.5 | 3817.146 | 1276 | 4011.9265 | 1279 | 71379.3315 | 1281.5 | 111449.9135 | 1284.5 | 17956.1432 | 1287.5 | 102652.4791 | 1290 | 1683.0521 | 1293 | 2531.3339 | 1295.5 | 126468.9988 | 1298.5 | 82245.9982 | 1301.5 | 207706.6468 | 1304 | 9.8417 | 1307 | 94.8025 | 1309.5 | 13.5121 | 1312.5 | 10501.9249 | 1315.5 | 1569.4109 | 1318 | 11529.8805 | 1262 | 9.8417
1321 | 1650.7856 | 1323.5 | 0.76476 | 1326.5 | 2544.0733 | 1329.5 | 16.238 | 1332 | 15.7207 | 1335 | 21.5301 | 1337.5 | 71379.3315 | 1340.5 | 85379.3315 | 1343.5 | 80045.9982 | 1346 | 128468.9988 | 1349 | 116768.9988 | 1351.5 | 84579.3315 | 1354.5 | 202564.976 | 1357.5 | 82245.9982 | 1360 | 127868.9988 | 1363 | 11625.6512 | 1365.5 | 21.4619 | 1368.5 | 6.7574 | 1371.5 | 522.1227 | 1374 | 2062.8228 | 1377 | 4128.8261 | 1321 | 0.76476
1379.5 | 21.1925 | 1382.5 | 7.8848 | 1385.5 | 261.5293 | 1388 | 1171.1857 | 1391 | 0.91097 | 1393.5 | 17.5262 | 1396.5 | 53509.4976 | 1399.5 | 85379.3315 | 1402 | 80045.9982 | 1405 | 24459.5117 | 1407.5 | 110.0306 | 1410.5 | 84579.3315 | 1413.5 | 84279.3315 | 1416 | 123418.9988 | 1419 | 85212.6648 | 1421.5 | 161.162 | 1424.5 | 11245.1479 | 1427.5 | 133.6895 | 1430 | 25.8499 | 1433 | 2112.3772 | 1435.5 | 0.90147 | 1379.5 | 0.90147
1438.5 | 21884.0183 | 1441.5 | 4330.017 | 1444 | 12613.5896 | 1447 | 5943.7949 | 1449.5 | 75.5405 | 1452.5 | 65.5641 | 1455.5 | 26630.1043 | 1458 | 16560.2905 | 1461 | 17396.8897 | 1463.5 | 250443.0538 | 1466.5 | 30557.3511 | 1469.5 | 1658.0608 | 1472 | 69953.9737 | 1475 | 16188.9296 | 1477.5 | 1657.2933 | 1480.5 | 6143.6682 | 1483.5 | 2309.2601 | 1486 | 55892.2427 | 1489 | 16.2355 | 1491.5 | 0.85881 | 1494.5 | 39.8802 | 1438.5 | 0.85881
1497.5 | 28167.1245 | 1500 | 118769.7301 | 1503 | 18583.3101 | 1505.5 | 60196.8794 | 1508.5 | 65.7886 | 1511.5 | 29.1608 | 1514 | 26617.7261 | 1517 | 1928.0449 | 1519.5 | 11809.3365 | 1522.5 | 125971.8004 | 1525.5 | 233038.4706 | 1528 | 6884.65 | 1531 | 227847.6334 | 1533.5 | 82245.9982 | 1536.5 | 127868.9988 | 1539.5 | 3096.1647 | 1542 | 5.7697 | 1545 | 54695.1083 | 1547.5 | 10.7122 | 1550.5 | 5031.9601 | 1553.5 | 45.9365 | 1497.5 | 5.7697
1556 | 4921.5418 | 1559 | 59759.4583 | 1561.5 | 22762.6159 | 1564.5 | 84446.6379 | 1567.5 | 46.5105 | 1570 | 68.5962 | 1572 | 23693.199 | 1575.5 | 7721.5747 | 1578.5 | 17604.2611 | 1581.5 | 1355.0107 | 1584 | 46507.5456 | 1587 | 8916.9671 | 1589.5 | 46155.7506 | 1592.5 | 246438.3238 | 1595.5 | 255538.1172 | 1598 | 3465.2048 | 1601 | 16758.7555 | 1603.5 | 18178.466 | 1606.5 | 5402.2648 | 1609.5 | 11153.5588 | 1612 | 11.9701 | 1556 | 11.9701
1615 | 0.091039 | 1617.5 | 36592.1333 | 1620.5 | 0.54644 | 1623.5 | 332.8631 | 1626 | 27.3523 | 1629 | 0.85969 | 1631.5 | 0.52941 | 1634.5 | 19.7825 | 1637.5 | 13.3779 | 1640 | 6839.0469 | 1643 | 151.8156 | 1645.5 | 9450.9369 | 1648.5 | 13063.1703 | 1651.5 | 82245.9982 | 1654 | 85212.6648 | 1657 | 10.6384 | 1659.5 | 4133.9817 | 1662.5 | 8292.7763 | 1665.5 | 301.0035 | 1668 | 42.2548 | 1671 | 11.2609 | 1615 | 0.091039
1673.5 | 23.0825 | 1676.5 | 0.46347 | 1679.5 | 0.34378 | 1682 | 18.0074 | 1685 | 2.9183 | 1687.5 | 20.0871 | 1690.5 | 1.3757 | 1693.5 | 214.824 | 1696 | 17.203 | 1699 | 0.91873 | 1701.5 | 10.7773 | 1704.5 | 86107.8698 | 1707.5 | 84279.3315 | 1710 | 42895.7734 | 1713 | 85212.6648 | 1715.5 | 37.0133 | 1718.5 | 133.3226 | 1721.5 | 7743.2127 | 1724 | 7330.5363 | 1727 | 22083.3632 | 1729.5 | 2055.1068 | 1673.5 | 0.34378

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -91 | 30.2622 | 26.6764 | 26.5709 | 26.5662 | 26.7727 | 26.4651 | 26.2295 | 28.3385
0.6409 | -90.3591 | 30.2669 | 26.677 | 26.5701 | 26.5662 | 26.7821 | 26.4683 | 26.2258 | 28.3418
1.5622 | -89.4378 | 30.2676 | 26.6786 | 26.5672 | 26.5635 | 26.7768 | 26.4678 | 26.2237 | 28.3502
2.5637 | -88.4363 | 30.2664 | 26.684 | 26.571 | 26.5609 | 26.778 | 26.4649 | 26.2182 | 28.3353
3.5651 | -87.4349 | 30.2597 | 26.6813 | 26.5647 | 26.5624 | 26.7762 | 26.4716 | 26.2216 | 28.3469
4.5666 | -86.4334 | 30.2661 | 26.6787 | 26.572 | 26.5647 | 26.779 | 26.4617 | 26.219 | 28.3276
5.568 | -85.432 | 30.2645 | 26.6804 | 26.5633 | 26.5662 | 26.7727 | 26.4646 | 26.2167 | 28.3416
6.5594 | -84.4406 | 30.267 | 26.6753 | 26.5625 | 26.5616 | 26.7811 | 26.464 | 26.2199 | 28.3271
7.5609 | -83.4391 | 30.2684 | 26.6805 | 26.5802 | 26.5592 | 26.7796 | 26.4692 | 26.2236 | 28.3299
8.5623 | -82.4377 | 30.267 | 26.6812 | 26.578 | 26.5646 | 26.7836 | 26.4645 | 26.2267 | 28.3414
9.5638 | -81.4362 | 30.2597 | 26.6856 | 26.578 | 26.5674 | 26.7763 | 26.4703 | 26.2172 | 28.3341
10.5652 | -80.4348 | 30.2584 | 26.6775 | 26.5779 | 26.5602 | 26.7771 | 26.469 | 26.2244 | 28.337
11.5666 | -79.4334 | 30.2661 | 26.6824 | 26.579 | 26.5652 | 26.7818 | 26.4652 | 26.2208 | 28.3438
12.5681 | -78.4319 | 30.2587 | 26.688 | 26.5702 | 26.5653 | 26.7853 | 26.471 | 26.225 | 28.3374
13.5595 | -77.4405 | 30.2638 | 26.6865 | 26.5779 | 26.5638 | 26.7885 | 26.4724 | 26.2223 | 28.3489
14.5609 | -76.4391 | 30.2683 | 26.687 | 26.5763 | 26.5688 | 26.7772 | 26.4734 | 26.2217 | 28.3371
15.5624 | -75.4376 | 30.2628 | 26.6833 | 26.5658 | 26.564 | 26.779 | 26.4664 | 26.2222 | 28.3403
16.5638 | -74.4362 | 30.261 | 26.6874 | 26.577 | 26.5683 | 26.7873 | 26.4804 | 26.2195 | 28.3356
17.5653 | -73.4347 | 30.2663 | 26.6863 | 26.5808 | 26.5665 | 26.7812 | 26.4724 | 26.2212 | 28.344
18.5667 | -72.4333 | 30.2664 | 26.6857 | 26.5785 | 26.5637 | 26.7839 | 26.4784 | 26.2253 | 28.3363
19.5681 | -71.4319 | 30.2656 | 26.6846 | 26.5735 | 26.5719 | 26.7805 | 26.4707 | 26.2235 | 28.3477
20.5696 | -70.4304 | 30.261 | 26.6823 | 26.5787 | 26.5717 | 26.7848 | 26.4734 | 26.2219 | 28.3317
21.561 | -69.439 | 30.2685 | 26.6938 | 26.5775 | 26.5716 | 26.7887 | 26.4759 | 26.2214 | 28.3475
22.5624 | -68.4376 | 30.2658 | 26.6847 | 26.5837 | 26.575 | 26.7912 | 26.4725 | 26.2267 | 28.3381
23.5639 | -67.4361 | 30.2703 | 26.6863 | 26.5808 | 26.5695 | 26.7923 | 26.4766 | 26.2207 | 28.3449
24.5653 | -66.4347 | 30.2675 | 26.6904 | 26.5823 | 26.5731 | 26.7796 | 26.4758 | 26.226 | 28.3414
25.5668 | -65.4332 | 30.2692 | 26.6881 | 26.5821 | 26.576 | 26.7908 | 26.4827 | 26.2298 | 28.3297
26.5682 | -64.4318 | 30.266 | 26.6849 | 26.5836 | 26.5681 | 26.7807 | 26.4795 | 26.2231 | 28.3479
27.5596 | -63.4404 | 30.2681 | 26.695 | 26.5869 | 26.5693 | 26.7927 | 26.4788 | 26.2306 | 28.3507
28.5611 | -62.4389 | 30.2705 | 26.692 | 26.586 | 26.5738 | 26.785 | 26.4729 | 26.2297 | 28.3425
29.5625 | -61.4375 | 30.2747 | 26.6933 | 26.5904 | 26.5732 | 26.7823 | 26.4792 | 26.2313 | 28.3587
30.5639 | -60.4361 | 30.2686 | 26.6982 | 26.5845 | 26.5713 | 26.7821 | 26.478 | 26.2294 | 28.3533
31.5654 | -59.4346 | 30.2648 | 26.6993 | 26.5978 | 26.5771 | 26.7857 | 26.4769 | 26.2309 | 28.3472
32.5668 | -58.4332 | 30.2684 | 26.7 | 26.5768 | 26.5766 | 26.7866 | 26.483 | 26.2306 | 28.3503
33.5583 | -57.4417 | 30.2689 | 26.6907 | 26.5876 | 26.5749 | 26.7941 | 26.4832 | 26.2317 | 28.3512
34.5597 | -56.4403 | 30.2684 | 26.7027 | 26.584 | 26.5803 | 26.7984 | 26.4735 | 26.2414 | 28.3481
35.5611 | -55.4389 | 30.2645 | 26.6969 | 26.5895 | 26.5775 | 26.8059 | 26.4858 | 26.2398 | 28.3359
36.5626 | -54.4374 | 30.2622 | 26.6975 | 26.604 | 26.5788 | 26.7964 | 26.4807 | 26.2307 | 28.3598
37.564 | -53.436 | 30.2632 | 26.6924 | 26.5819 | 26.5777 | 26.7976 | 26.4818 | 26.2372 | 28.3507
38.5655 | -52.4345 | 30.2563 | 26.6972 | 26.5938 | 26.5797 | 26.7966 | 26.4802 | 26.2349 | 28.3569
39.5669 | -51.4331 | 30.2601 | 26.6979 | 26.5856 | 26.5826 | 26.7917 | 26.4824 | 26.2331 | 28.3541
40.5683 | -50.4317 | 30.2566 | 26.7001 | 26.5892 | 26.581 | 26.8023 | 26.4822 | 26.2329 | 28.3427
41.5598 | -49.4402 | 30.2551 | 26.6958 | 26.59 | 26.5823 | 26.8008 | 26.4864 | 26.2378 | 28.3461
42.5612 | -48.4388 | 30.2547 | 26.698 | 26.5913 | 26.5817 | 26.796 | 26.4855 | 26.2341 | 28.3558
43.5626 | -47.4374 | 30.2532 | 26.7011 | 26.5901 | 26.5902 | 26.8012 | 26.4879 | 26.2313 | 28.3535
44.5641 | -46.4359 | 30.2575 | 26.7022 | 26.5885 | 26.5805 | 26.7955 | 26.4818 | 26.2381 | 28.3547
45.5655 | -45.4345 | 30.2538 | 26.7053 | 26.6076 | 26.5864 | 26.7952 | 26.4862 | 26.2374 | 28.3471
46.567 | -44.433 | 30.2569 | 26.7013 | 26.5896 | 26.5843 | 26.7983 | 26.4819 | 26.2359 | 28.3509
47.5684 | -43.4316 | 30.2508 | 26.6969 | 26.5954 | 26.579 | 26.8031 | 26.4826 | 26.233 | 28.3517
48.5598 | -42.4402 | 30.2531 | 26.7019 | 26.5973 | 26.583 | 26.7987 | 26.4833 | 26.2406 | 28.3579
49.5613 | -41.4387 | 30.26 | 26.7021 | 26.5897 | 26.5874 | 26.7965 | 26.4846 | 26.2377 | 28.3535
50.5627 | -40.4373 | 30.2527 | 26.7007 | 26.5964 | 26.5879 | 26.8105 | 26.4861 | 26.2406 | 28.3501
51.5641 | -39.4359 | 30.2552 | 26.7042 | 26.5966 | 26.5877 | 26.8102 | 26.4865 | 26.2327 | 28.3594
52.5656 | -38.4344 | 30.2501 | 26.7014 | 26.5952 | 26.5908 | 26.8022 | 26.4875 | 26.2356 | 28.348
53.567 | -37.433 | 30.2557 | 26.7057 | 26.5941 | 26.5861 | 26.8021 | 26.4855 | 26.2385 | 28.3535
54.5585 | -36.4415 | 30.2564 | 26.7074 | 26.6019 | 26.5911 | 26.8099 | 26.482 | 26.2371 | 28.3657
55.5599 | -35.4401 | 30.2492 | 26.7067 | 26.5943 | 26.5861 | 26.7933 | 26.4843 | 26.2374 | 28.3591
56.5613 | -34.4387 | 30.2479 | 26.71 | 26.5974 | 26.5878 | 26.8058 | 26.489 | 26.2322 | 28.3608
57.5628 | -33.4372 | 30.2508 | 26.7059 | 26.5999 | 26.5891 | 26.8027 | 26.491 | 26.2382 | 28.3616
58.5642 | -32.4358 | 30.2443 | 26.7042 | 26.6038 | 26.5923 | 26.8111 | 26.4891 | 26.2393 | 28.3625
59.5657 | -31.4343 | 30.2576 | 26.7074 | 26.6078 | 26.5899 | 26.8084 | 26.4843 | 26.2331 | 28.3485
60.5671 | -30.4329 | 30.2461 | 26.7051 | 26.6031 | 26.5954 | 26.8042 | 26.4902 | 26.2303 | 28.3535
61.5585 | -29.4415 | 30.242 | 26.707 | 26.6137 | 26.5876 | 26.7983 | 26.4869 | 26.2357 | 28.3493
62.56 | -28.44 | 30.2498 | 26.7012 | 26.6002 | 26.5957 | 26.806 | 26.4901 | 26.2385 | 28.3595
63.5614 | -27.4386 | 30.2513 | 26.7024 | 26.6111 | 26.589 | 26.8157 | 26.4852 | 26.2392 | 28.3615
64.5628 | -26.4372 | 30.2508 | 26.7156 | 26.6068 | 26.5913 | 26.8131 | 26.4899 | 26.2361 | 28.3539
65.5643 | -25.4357 | 30.2481 | 26.7076 | 26.6127 | 26.5949 | 26.8054 | 26.4874 | 26.2369 | 28.3643
66.5657 | -24.4343 | 30.2517 | 26.7104 | 26.6039 | 26.5938 | 26.8135 | 26.4897 | 26.2377 | 28.3553
67.5672 | -23.4328 | 30.2456 | 26.7129 | 26.6185 | 26.5926 | 26.8036 | 26.4903 | 26.2365 | 28.3571
68.5686 | -22.4314 | 30.2454 | 26.7095 | 26.6158 | 26.5916 | 26.8124 | 26.4944 | 26.2369 | 28.3586
69.56 | -21.44 | 30.2522 | 26.7123 | 26.608 | 26.5896 | 26.8103 | 26.4968 | 26.2399 | 28.3565
70.5615 | -20.4385 | 30.244 | 26.7156 | 26.6153 | 26.5953 | 26.811 | 26.4927 | 26.2411 | 28.3546
71.5629 | -19.4371 | 30.2483 | 26.7153 | 26.6086 | 26.5935 | 26.8066 | 26.4896 | 26.2381 | 28.3613
72.5643 | -18.4357 | 30.2477 | 26.7161 | 26.615 | 26.5922 | 26.8131 | 26.4991 | 26.2359 | 28.3619
73.5658 | -17.4342 | 30.2523 | 26.7103 | 26.6206 | 26.5883 | 26.8075 | 26.4968 | 26.2386 | 28.3584
74.5672 | -16.4328 | 30.245 | 26.7154 | 26.6101 | 26.5986 | 26.8136 | 26.4972 | 26.2397 | 28.3546
75.5586 | -15.4414 | 30.2541 | 26.7129 | 26.6077 | 26.5945 | 26.8156 | 26.4941 | 26.2415 | 28.3512
76.5601 | -14.4399 | 30.2454 | 26.7168 | 26.6101 | 26.5953 | 26.8079 | 26.4975 | 26.2429 | 28.3445
77.5615 | -13.4385 | 30.2504 | 26.7208 | 26.615 | 26.5983 | 26.8124 | 26.4963 | 26.2427 | 28.3546
78.563 | -12.437 | 30.2512 | 26.7154 | 26.6147 | 26.5968 | 26.8125 | 26.4997 | 26.2364 | 28.3627
79.5644 | -11.4356 | 30.2487 | 26.7144 | 26.6186 | 26.5939 | 26.814 | 26.5017 | 26.2399 | 28.3598
80.5658 | -10.4342 | 30.2528 | 26.7187 | 26.6207 | 26.5989 | 26.8115 | 26.4975 | 26.2428 | 28.3483
81.5673 | -9.4327 | 30.2511 | 26.7179 | 26.6197 | 26.5985 | 26.817 | 26.5007 | 26.2396 | 28.3498
82.5587 | -8.4413 | 30.25 | 26.7132 | 26.6171 | 26.5983 | 26.8093 | 26.4913 | 26.2396 | 28.355
83.5702 | -7.4298 | 30.2553 | 26.713 | 26.616 | 26.5988 | 26.8171 | 26.505 | 26.2406 | 28.3626
84.5616 | -6.4384 | 30.2558 | 26.7127 | 26.6195 | 26.6042 | 26.8114 | 26.4998 | 26.2365 | 28.3541
85.563 | -5.437 | 30.2506 | 26.7125 | 26.6238 | 26.6038 | 26.8115 | 26.5041 | 26.2406 | 28.3579
86.5645 | -4.4355 | 30.2565 | 26.7145 | 26.6276 | 26.6043 | 26.819 | 26.5011 | 26.2378 | 28.3488
87.5659 | -3.4341 | 30.2604 | 26.7154 | 26.6222 | 26.5996 | 26.819 | 26.5159 | 26.2369 | 28.2772
88.5674 | -2.4326 | 30.2559 | 26.7136 | 26.6166 | 26.6018 | 26.8175 | 26.5084 | 26.2433 | 28.3368
89.5688 | -1.4312 | 30.2878 | 26.7136 | 26.6244 | 26.6046 | 26.8196 | 26.5092 | 26.2403 | 28.3375
90.5602 | -0.4398 | 30.6255 | 26.7157 | 26.6265 | 26.5996 | 26.8153 | 26.5143 | 26.2357 | 28.3434
91.5617 | 0.5617 | 31.522 | 26.7146 | 26.6154 | 26.6096 | 26.8245 | 26.5096 | 26.2433 | 28.343
92.5631 | 1.5631 | 33.0323 | 26.7196 | 26.6237 | 26.6106 | 26.8213 | 26.5047 | 26.245 | 28.3609
93.5645 | 2.5645 | 35.0754 | 26.7244 | 26.6196 | 26.6072 | 26.8233 | 26.5079 | 26.243 | 28.3754
94.566 | 3.566 | 37.5804 | 26.7215 | 26.6266 | 26.6121 | 26.8306 | 26.5138 | 26.2496 | 28.4036
95.5674 | 4.5674 | 40.4723 | 26.7358 | 26.6133 | 26.619 | 26.8309 | 26.5096 | 26.2671 | 28.4183
96.5588 | 5.5588 | 43.7017 | 26.7399 | 26.6259 | 26.6269 | 26.8581 | 26.5175 | 26.2753 | 28.4443
97.5603 | 6.5603 | 47.2203 | 26.758 | 26.6214 | 26.6297 | 26.8692 | 26.5194 | 26.2899 | 28.4801
98.5617 | 7.5617 | 50.9672 | 26.7861 | 26.6245 | 26.6573 | 26.8954 | 26.5293 | 26.3038 | 28.5262
99.5632 | 8.5632 | 54.9236 | 26.8074 | 26.6325 | 26.6722 | 26.9265 | 26.5416 | 26.3336 | 28.5637
100.5646 | 9.5646 | 59.0672 | 26.8303 | 26.63 | 26.6907 | 26.9617 | 26.5511 | 26.3662 | 28.6193
101.566 | 10.566 | 63.3821 | 26.88 | 26.6326 | 26.718 | 27.006 | 26.5664 | 26.3898 | 28.691
102.5675 | 11.5675 | 67.8504 | 26.926 | 26.6425 | 26.7471 | 27.0593 | 26.5936 | 26.4445 | 28.7692
103.5589 | 12.5589 | 72.5094 | 26.9836 | 26.6475 | 26.7939 | 27.1302 | 26.6168 | 26.4939 | 28.8469
104.5604 | 13.5604 | 77.2318 | 27.0516 | 26.6452 | 26.8373 | 27.1919 | 26.6453 | 26.5447 | 28.9213
105.5618 | 14.5618 | 82.0426 | 27.129 | 26.6559 | 26.8793 | 27.2653 | 26.6824 | 26.611 | 29.0247
106.5632 | 15.5632 | 86.9527 | 27.2124 | 26.662 | 26.9409 | 27.3669 | 26.7225 | 26.6865 | 29.1524
107.5647 | 16.5647 | 92.0048 | 27.3114 | 26.6743 | 27.0098 | 27.4591 | 26.7673 | 26.779 | 29.2672
108.5661 | 17.5661 | 97.1599 | 27.4232 | 26.6845 | 27.0884 | 27.5702 | 26.8183 | 26.8734 | 29.42
109.5676 | 18.5676 | 102.4079 | 27.5463 | 26.6921 | 27.1686 | 27.6911 | 26.8795 | 26.9859 | 29.5606
110.569 | 19.569 | 107.7257 | 27.6787 | 26.6921 | 27.2695 | 27.8155 | 26.9504 | 27.1012 | 29.7167
111.5604 | 20.5604 | 113.0451 | 27.8281 | 26.7168 | 27.3782 | 27.9691 | 27.0169 | 27.2318 | 29.9002
112.5619 | 21.5619 | 118.4474 | 27.9796 | 26.7263 | 27.4905 | 28.1246 | 27.103 | 27.3766 | 30.0779
113.5633 | 22.5633 | 123.8745 | 28.1601 | 26.7384 | 27.6218 | 28.3044 | 27.201 | 27.5292 | 30.2778
114.5647 | 23.5647 | 129.4027 | 28.3495 | 26.7668 | 27.756 | 28.4876 | 27.2977 | 27.7039 | 30.493
115.5662 | 24.5662 | 135.0139 | 28.5476 | 26.795 | 27.9086 | 28.6876 | 27.409 | 27.8845 | 30.7516
116.5676 | 25.5676 | 140.6297 | 28.7721 | 26.8213 | 28.0746 | 28.9135 | 27.536 | 28.0844 | 31
117.559 | 26.559 | 146.2603 | 29.0116 | 26.8507 | 28.2527 | 29.1497 | 27.6545 | 28.3043 | 31.2615
118.5605 | 27.5605 | 151.8858 | 29.2701 | 26.8775 | 28.444 | 29.394 | 27.8068 | 28.5347 | 31.5503
119.5619 | 28.5619 | 157.5293 | 29.5491 | 26.9169 | 28.6412 | 29.6549 | 27.9477 | 28.7808 | 31.8618
120.5634 | 29.5634 | 163.1299 | 29.8345 | 26.9514 | 28.8579 | 29.9522 | 28.1134 | 29.0349 | 32.1838
121.5648 | 30.5648 | 168.6933 | 30.1473 | 26.9975 | 29.0856 | 30.246 | 28.2864 | 29.3117 | 32.5174
122.5662 | 31.5662 | 174.2562 | 30.4627 | 27.0444 | 29.34 | 30.5705 | 28.4658 | 29.6058 | 32.8857
123.5677 | 32.5677 | 179.7975 | 30.8058 | 27.0999 | 29.6042 | 30.8911 | 28.659 | 29.9163 | 33.2362
124.5691 | 33.5691 | 185.3329 | 31.1728 | 27.1434 | 29.8839 | 31.251 | 28.8693 | 30.2366 | 33.637
125.5706 | 34.5706 | 190.9039 | 31.5507 | 27.1987 | 30.1655 | 31.6193 | 29.0843 | 30.5811 | 34.0769
126.562 | 35.562 | 196.4364 | 31.9516 | 27.2626 | 30.4858 | 32.0087 | 29.312 | 30.9483 | 34.5082
127.5634 | 36.5634 | 201.9897 | 32.37 | 27.3374 | 30.8045 | 32.4165 | 29.565 | 31.3202 | 34.9676
128.5649 | 37.5649 | 207.5179 | 32.822 | 27.4013 | 31.1458 | 32.8427 | 29.8172 | 31.7105 | 35.4512
129.5663 | 38.5663 | 212.9986 | 33.2881 | 27.4865 | 31.5092 | 33.2746 | 30.0813 | 32.1225 | 35.9766
130.5677 | 39.5677 | 218.4712 | 33.771 | 27.5568 | 31.8822 | 33.7486 | 30.3529 | 32.5459 | 36.5086
131.5692 | 40.5692 | 223.9311 | 34.2672 | 27.6456 | 32.2776 | 34.2375 | 30.6466 | 32.9946 | 37.0959
132.5606 | 41.5606 | 229.358 | 34.8011 | 27.7433 | 32.6944 | 34.7506 | 30.9433 | 33.4606 | 37.7119
133.5621 | 42.5621 | 234.9199 | 35.3427 | 27.8307 | 33.1264 | 35.2739 | 31.2516 | 33.944 | 38.3199
134.5635 | 43.5635 | 240.4383 | 35.9159 | 27.9444 | 33.58 | 35.8452 | 31.5892 | 34.4486 | 38.9531
135.5649 | 44.5649 | 245.8688 | 36.5003 | 28.0536 | 34.0519 | 36.4027 | 31.9212 | 34.9732 | 39.6419
136.5664 | 45.5664 | 251.4268 | 37.1109 | 28.1628 | 34.5489 | 37.0153 | 32.2778 | 35.5125 | 40.3135
137.5678 | 46.5678 | 257.0227 | 37.7493 | 28.2899 | 35.0601 | 37.6569 | 32.6528 | 36.0664 | 41.0943
138.5592 | 47.5592 | 262.4766 | 38.4 | 28.4176 | 35.5846 | 38.3178 | 33.0353 | 36.6405 | 41.8348
139.5607 | 48.5607 | 267.8548 | 39.0879 | 28.5497 | 36.1377 | 38.9984 | 33.4354 | 37.229 | 42.6247
140.5621 | 49.5621 | 273.1635 | 39.7931 | 28.6994 | 36.7111 | 39.7122 | 33.8519 | 37.8446 | 43.4281
141.5636 | 50.5636 | 278.5839 | 40.5282 | 28.84 | 37.3006 | 40.447 | 34.2841 | 38.4799 | 44.2776
142.565 | 51.565 | 283.9248 | 41.2802 | 29.0025 | 37.9244 | 41.2141 | 34.7317 | 39.1463 | 45.1289
143.5664 | 52.5664 | 289.4284 | 42.0352 | 29.16 | 38.5522 | 41.9944 | 35.1901 | 39.8318 | 46.0507
144.5679 | 53.5679 | 294.8262 | 42.8274 | 29.3355 | 39.219 | 42.8282 | 35.6727 | 40.518 | 46.9159
145.5593 | 54.5593 | 300.1449 | 43.6524 | 29.5134 | 39.8937 | 43.6706 | 36.1698 | 41.2355 | 47.8684
146.5607 | 55.5607 | 305.2268 | 44.5114 | 29.7076 | 40.5966 | 44.5547 | 36.6752 | 41.984 | 48.8978
147.5622 | 56.5622 | 309.753 | 45.3993 | 29.8967 | 41.3189 | 45.4637 | 37.1945 | 42.7511 | 49.8794
148.5636 | 57.5636 | 313.9865 | 46.3208 | 30.1096 | 42.0663 | 46.4084 | 37.7321 | 43.5404 | 50.9182
149.5651 | 58.5651 | 318.0024 | 47.2734 | 30.3184 | 42.8274 | 47.3754 | 38.2878 | 44.3488 | 51.9839
150.5665 | 59.5665 | 321.7352 | 48.2405 | 30.5482 | 43.6065 | 48.3757 | 38.8594 | 45.1676 | 53.0589
151.5679 | 60.5679 | 325.3787 | 49.2124 | 30.7726 | 44.4075 | 49.4014 | 39.4434 | 46.0122 | 54.1559
152.5694 | 61.5694 | 328.9557 | 50.2157 | 31.0149 | 45.2224 | 50.4541 | 40.039 | 46.856 | 55.2954
153.5608 | 62.5608 | 332.1758 | 51.2473 | 31.2607 | 46.0604 | 51.51 | 40.6411 | 47.7234 | 56.4164
154.5622 | 63.5622 | 335.322 | 52.3085 | 31.5121 | 46.9015 | 52.6064 | 41.2646 | 48.5964 | 57.5164
155.5637 | 64.5637 | 338.2281 | 53.3996 | 31.7823 | 47.7633 | 53.72 | 41.8976 | 49.4894 | 58.6827
156.5651 | 65.5651 | 340.7139 | 54.5019 | 32.0608 | 48.6554 | 54.8513 | 42.5488 | 50.3784 | 59.828
157.5666 | 66.5666 | 342.8964 | 55.6325 | 32.3351 | 49.5389 | 55.978 | 43.1992 | 51.2787 | 61.0125
158.568 | 67.568 | 344.8411 | 56.784 | 32.6283 | 50.4375 | 57.1381 | 43.8728 | 52.1833 | 62.1596
159.5594 | 68.5594 | 346.4717 | 57.9696 | 32.9276 | 51.3377 | 58.3112 | 44.5466 | 53.1042 | 63.3242
160.5609 | 69.5609 | 347.7785 | 59.1298 | 33.2244 | 52.2483 | 59.4834 | 45.2357 | 54.0247 | 64.4997
161.5623 | 70.5623 | 348.789 | 60.3164 | 33.5549 | 53.1788 | 60.6581 | 45.9332 | 54.9365 | 65.6701
162.5638 | 71.5638 | 349.6411 | 61.5185 | 33.8756 | 54.1073 | 61.8537 | 46.6332 | 55.8497 | 66.8408
163.5652 | 72.5652 | 350.2991 | 62.7203 | 34.1913 | 55.0417 | 63.0338 | 47.332 | 56.7614 | 68.0558
164.5666 | 73.5666 | 350.9087 | 63.9199 | 34.5365 | 55.974 | 64.2218 | 48.0579 | 57.6568 | 69.2221
165.5681 | 74.5681 | 351.4638 | 65.1249 | 34.8993 | 56.9152 | 65.4073 | 48.7872 | 58.5577 | 70.3911
166.5695 | 75.5695 | 351.8031 | 66.3145 | 35.2488 | 57.8529 | 66.5998 | 49.5091 | 59.4391 | 71.5588
167.591 | 76.591 | 351.9892 | 67.5343 | 35.6123 | 58.8238 | 67.8141 | 50.2564 | 60.334 | 72.7563
168.5624 | 77.5624 | 352.0702 | 68.6718 | 35.9706 | 59.7392 | 68.9543 | 50.9569 | 61.1744 | 73.8857
169.5638 | 78.5638 | 352.0757 | 69.8517 | 36.3355 | 60.6689 | 70.1207 | 51.6873 | 62.0306 | 75.0186
170.5653 | 79.5653 | 352.0925 | 70.9968 | 36.7051 | 61.6019 | 71.2563 | 52.4159 | 62.8718 | 76.1507
171.5667 | 80.5667 | 352.0031 | 72.145 | 37.0975 | 62.5223 | 72.3716 | 53.1435 | 63.7079 | 77.3141
172.5681 | 81.5681 | 352.0914 | 73.2774 | 37.4825 | 63.4352 | 73.4845 | 53.8747 | 64.5375 | 78.4364
173.5696 | 82.5696 | 351.9456 | 74.3857 | 37.8739 | 64.3328 | 74.5802 | 54.5982 | 65.3381 | 79.5664
174.561 | 83.561 | 351.7157 | 75.475 | 38.2749 | 65.2127 | 75.6645 | 55.3176 | 66.1402 | 80.6939
175.5624 | 84.5624 | 351.426 | 76.5529 | 38.6765 | 66.09 | 76.7257 | 56.0219 | 66.9262 | 81.8046
176.5639 | 85.5639 | 351.1418 | 77.607 | 39.0849 | 66.962 | 77.7877 | 56.7364 | 67.7063 | 82.9121
177.5653 | 86.5653 | 350.8183 | 78.6375 | 39.4928 | 67.8212 | 78.8257 | 57.4403 | 68.4694 | 84.0029
178.5668 | 87.5668 | 350.5182 | 79.6671 | 39.9048 | 68.6682 | 79.8522 | 58.145 | 69.2292 | 85.1268
179.5682 | 88.5682 | 350.1948 | 80.6672 | 40.3312 | 69.5013 | 80.8576 | 58.8342 | 69.9725 | 86.2291
180.5596 | 89.5596 | 349.9257 | 81.6671 | 40.7397 | 70.3211 | 81.8768 | 59.51 | 70.7019 | 87.3181
181.5611 | 90.5611 | 349.6306 | 82.6466 | 41.1735 | 71.1291 | 82.8539 | 60.181 | 71.4155 | 88.41
182.5625 | 91.5625 | 349.2669 | 83.6231 | 41.5988 | 71.9403 | 83.8293 | 60.8533 | 72.1289 | 89.5007
183.564 | 92.564 | 348.9871 | 84.5646 | 42.0264 | 72.7399 | 84.8042 | 61.5102 | 72.8303 | 90.593
184.5654 | 93.5654 | 348.5801 | 85.5065 | 42.4631 | 73.5363 | 85.7619 | 62.1593 | 73.5214 | 91.6613
185.5668 | 94.5668 | 348.0648 | 86.4326 | 42.8797 | 74.3095 | 86.7005 | 62.8013 | 74.2069 | 92.7196
186.5583 | 95.5583 | 347.5426 | 87.3334 | 43.3294 | 75.084 | 87.6209 | 63.4396 | 74.8614 | 93.7784
187.5597 | 96.5597 | 347.062 | 88.2349 | 43.7625 | 75.8427 | 88.543 | 64.0622 | 75.5136 | 94.8148
188.5611 | 97.5611 | 346.6352 | 89.1089 | 44.2071 | 76.597 | 89.4325 | 64.6781 | 76.1526 | 95.8746
189.5626 | 98.5626 | 346.1372 | 89.9756 | 44.6489 | 77.3512 | 90.3225 | 65.2889 | 76.7944 | 96.904
190.564 | 99.564 | 345.684 | 90.82 | 45.0959 | 78.0854 | 91.1909 | 65.8955 | 77.4223 | 97.92
191.5655 | 100.5655 | 345.2826 | 91.6413 | 45.5434 | 78.8111 | 92.0532 | 66.491 | 78.0372 | 98.9346
192.5669 | 101.5669 | 344.7631 | 92.4538 | 45.9796 | 79.5151 | 92.8984 | 67.0787 | 78.6415 | 99.9468
193.5683 | 102.5683 | 344.1932 | 93.262 | 46.4283 | 80.2223 | 93.7191 | 67.6689 | 79.2406 | 100.936
194.5598 | 103.5598 | 343.6833 | 94.0571 | 46.878 | 80.9198 | 94.5296 | 68.2376 | 79.8255 | 101.9356
195.5612 | 104.5612 | 343.3188 | 94.8313 | 47.3083 | 81.5958 | 95.3275 | 68.8113 | 80.3999 | 102.92
196.5626 | 105.5626 | 342.9644 | 95.6089 | 47.763 | 82.2681 | 96.1206 | 69.3667 | 80.981 | 103.9078
197.5641 | 106.5641 | 342.492 | 96.3595 | 48.226 | 82.9277 | 96.8903 | 69.9119 | 81.5346 | 104.8932
198.5655 | 107.5655 | 341.9126 | 97.0966 | 48.6699 | 83.5826 | 97.6636 | 70.4581 | 82.0982 | 105.8537
199.567 | 108.567 | 341.3807 | 97.8245 | 49.1367 | 84.2198 | 98.4285 | 71.0015 | 82.6413 | 106.8069
200.5684 | 109.5684 | 340.9788 | 98.5395 | 49.5655 | 84.8573 | 99.1661 | 71.5251 | 83.1792 | 107.7565
201.5598 | 110.5598 | 340.5267 | 99.2421 | 50.0235 | 85.4815 | 99.9022 | 72.0516 | 83.7134 | 108.6932
202.5613 | 111.5613 | 340.0007 | 99.9278 | 50.4716 | 86.0987 | 100.6019 | 72.5708 | 84.233 | 109.6152
203.5627 | 112.5627 | 339.4419 | 100.6075 | 50.9245 | 86.7093 | 101.3278 | 73.083 | 84.7457 | 110.5348
204.5641 | 113.5641 | 338.797 | 101.2696 | 51.3706 | 87.3019 | 102.0241 | 73.5881 | 85.2541 | 111.4451
205.5656 | 114.5656 | 338.2616 | 101.9213 | 51.8186 | 87.8798 | 102.717 | 74.0748 | 85.7435 | 112.3542
206.567 | 115.567 | 337.8243 | 102.543 | 52.2639 | 88.4524 | 103.3707 | 74.5678 | 86.242 | 113.2305
207.5585 | 116.5585 | 337.3504 | 103.1704 | 52.712 | 89.0187 | 104.0474 | 75.0448 | 86.738 | 114.1305
208.5599 | 117.5599 | 336.716 | 103.7945 | 53.157 | 89.5738 | 104.704 | 75.5144 | 87.2112 | 115.0165
209.5613 | 118.5613 | 336.2077 | 104.4138 | 53.6139 | 90.119 | 105.3435 | 75.9781 | 87.6787 | 115.8814
210.5628 | 119.5628 | 335.7677 | 105.0354 | 54.0614 | 90.6628 | 105.9865 | 76.4385 | 88.1448 | 116.7145
211.5642 | 120.5642 | 335.3204 | 105.637 | 54.5042 | 91.1971 | 106.6067 | 76.9004 | 88.6005 | 117.5699
212.5657 | 121.5657 | 334.8254 | 106.2414 | 54.9471 | 91.714 | 107.2079 | 77.3508 | 89.042 | 118.3957
213.5671 | 122.5671 | 334.1258 | 106.8225 | 55.386 | 92.2259 | 107.8079 | 77.7868 | 89.4767 | 119.2217
214.5585 | 123.5585 | 333.4214 | 107.4035 | 55.8328 | 92.7385 | 108.373 | 78.2222 | 89.9049 | 120.0359
215.56 | 124.56 | 332.7286 | 107.9802 | 56.2856 | 93.2316 | 108.9528 | 78.6552 | 90.3325 | 120.8501
216.5614 | 125.5614 | 332.1303 | 108.5401 | 56.7221 | 93.716 | 109.5144 | 79.0824 | 90.7532 | 121.6652
217.5628 | 126.5628 | 331.5614 | 109.1004 | 57.1716 | 94.1889 | 110.0572 | 79.5016 | 91.1676 | 122.4808
218.5643 | 127.5643 | 330.9258 | 109.6512 | 57.6147 | 94.6526 | 110.6241 | 79.9226 | 91.5757 | 123.2906
219.5657 | 128.5657 | 330.3136 | 110.1927 | 58.0632 | 95.1187 | 111.1691 | 80.328 | 91.9726 | 124.0844
220.5672 | 129.5672 | 329.7851 | 110.7175 | 58.51 | 95.5828 | 111.7005 | 80.7409 | 92.3715 | 124.8679
221.5686 | 130.5686 | 329.157 | 111.2401 | 58.9506 | 96.0404 | 112.2355 | 81.1439 | 92.7645 | 125.6003
222.56 | 131.56 | 328.5354 | 111.7636 | 59.3895 | 96.4831 | 112.7648 | 81.5499 | 93.1453 | 126.3502
223.5615 | 132.5615 | 327.8904 | 112.2791 | 59.828 | 96.9277 | 113.2781 | 81.9344 | 93.5276 | 127.097
224.7332 | 133.7332 | 327.2511 | 112.8711 | 60.3347 | 97.4445 | 113.8589 | 82.3955 | 93.9552 | 127.9563
225.5643 | 134.5643 | 326.8146 | 113.2948 | 60.6971 | 97.8066 | 114.2711 | 82.7131 | 94.261 | 128.5823
226.5658 | 135.5658 | 326.2494 | 113.7912 | 61.1351 | 98.2376 | 114.763 | 83.0834 | 94.6237 | 129.3231
227.5672 | 136.5672 | 325.6968 | 114.2862 | 61.572 | 98.6632 | 115.2501 | 83.4628 | 94.9765 | 130.0482
228.5687 | 137.5687 | 325.2038 | 114.7684 | 61.9968 | 99.0936 | 115.7359 | 83.8324 | 95.327 | 130.755
229.5601 | 138.5601 | 324.6958 | 115.2421 | 62.4271 | 99.5098 | 116.1877 | 84.1923 | 95.6786 | 131.47
230.5615 | 139.5615 | 324.1119 | 115.7068 | 62.8653 | 99.9198 | 116.6574 | 84.5569 | 96.0249 | 132.1517
231.563 | 140.563 | 323.5632 | 116.1742 | 63.2883 | 100.3374 | 117.1087 | 84.9057 | 96.3614 | 132.8466
232.5644 | 141.5644 | 323.0275 | 116.6258 | 63.7288 | 100.7475 | 117.5387 | 85.2631 | 96.6914 | 133.5428
233.5659 | 142.5659 | 322.5889 | 117.08 | 64.1486 | 101.1418 | 117.9806 | 85.6123 | 97.0197 | 134.2211
234.5673 | 143.5673 | 322.235 | 117.5273 | 64.5708 | 101.5384 | 118.4172 | 85.9559 | 97.3416 | 134.8796
235.5587 | 144.5587 | 321.8799 | 117.9641 | 64.994 | 101.9215 | 118.8416 | 86.3024 | 97.6673 | 135.5709
236.5602 | 145.5602 | 321.5889 | 118.399 | 65.4332 | 102.307 | 119.2652 | 86.6382 | 97.9803 | 136.2518
237.5616 | 146.5616 | 321.4053 | 118.8265 | 65.8402 | 102.6853 | 119.6714 | 86.9725 | 98.2861 | 136.8652
238.563 | 147.563 | 321.2205 | 119.2522 | 66.2702 | 103.0537 | 120.0728 | 87.306 | 98.5863 | 137.5567
239.5645 | 148.5645 | 320.9909 | 119.6743 | 66.6921 | 103.4153 | 120.4933 | 87.6344 | 98.8966 | 138.1956
240.5659 | 149.5659 | 320.9146 | 120.0926 | 67.1145 | 103.7694 | 120.8986 | 87.9524 | 99.1934 | 138.8514
241.5674 | 150.5674 | 320.8979 | 120.5047 | 67.5368 | 104.1221 | 121.3104 | 88.2699 | 99.4853 | 139.4822
242.5688 | 151.5688 | 320.9459 | 120.9154 | 67.9535 | 104.4704 | 121.6949 | 88.5849 | 99.7815 | 140.1513
243.5602 | 152.5602 | 321.0653 | 121.3282 | 68.3749 | 104.8164 | 122.0969 | 88.9078 | 100.0764 | 140.7831
244.5617 | 153.5617 | 321.2919 | 121.7314 | 68.7926 | 105.179 | 122.5008 | 89.218 | 100.3688 | 141.4141
245.5631 | 154.5631 | 321.6358 | 122.1342 | 69.2087 | 105.5335 | 122.9005 | 89.522 | 100.667 | 142.0973
246.5645 | 155.5645 | 321.8892 | 122.5414 | 69.6167 | 105.8833 | 123.2878 | 89.8387 | 100.9637 | 142.7072
247.566 | 156.566 | 322.2717 | 122.9524 | 70.0358 | 106.2306 | 123.6936 | 90.1529 | 101.2586 | 143.3826
248.5674 | 157.5674 | 322.6299 | 123.3667 | 70.4358 | 106.58 | 124.0813 | 90.4637 | 101.5551 | 143.9914
249.5588 | 158.5588 | 322.9732 | 123.7704 | 70.8452 | 106.9306 | 124.4809 | 90.769 | 101.8463 | 144.6508
250.5603 | 159.5603 | 323.3808 | 124.1843 | 71.25 | 107.2828 | 124.8854 | 91.0877 | 102.15 | 145.277
251.5617 | 160.5617 | 323.8535 | 124.5995 | 71.669 | 107.6384 | 125.2788 | 91.398 | 102.4461 | 145.9151
252.5632 | 161.5632 | 324.4631 | 125.0041 | 72.0695 | 107.9884 | 125.6862 | 91.7103 | 102.7487 | 146.5441
253.5646 | 162.5646 | 325.0739 | 125.4188 | 72.4727 | 108.3394 | 126.0855 | 92.0164 | 103.0471 | 147.1956
254.566 | 163.566 | 325.6482 | 125.8187 | 72.8848 | 108.7047 | 126.4955 | 92.3306 | 103.3552 | 147.8255
255.5675 | 164.5675 | 326.2163 | 126.2345 | 73.2923 | 109.0597 | 126.8894 | 92.6499 | 103.6611 | 148.4658
256.5589 | 165.5589 | 326.7641 | 126.6465 | 73.7061 | 109.4189 | 127.2887 | 92.9664 | 103.9725 | 149.1415
257.5604 | 166.5604 | 327.3504 | 127.0595 | 74.0991 | 109.7758 | 127.7087 | 93.2857 | 104.2836 | 149.7574
258.5618 | 167.5618 | 327.9313 | 127.4864 | 74.4951 | 110.1234 | 128.1168 | 93.6038 | 104.5909 | 150.4373
259.5632 | 168.5632 | 328.4564 | 127.913 | 74.9018 | 110.4812 | 128.5372 | 93.9319 | 104.9174 | 151.0505
260.5647 | 169.5647 | 328.9695 | 128.3534 | 75.2985 | 110.843 | 128.9585 | 94.2491 | 105.2307 | 151.7099
261.5661 | 170.5661 | 329.5277 | 128.7899 | 75.7092 | 111.1982 | 129.3905 | 94.585 | 105.5484 | 152.3704
262.5676 | 171.5676 | 330.1028 | 129.2378 | 76.1043 | 111.5667 | 129.8144 | 94.9085 | 105.8681 | 153.0119
263.569 | 172.569 | 330.6594 | 129.6857 | 76.5073 | 111.9224 | 130.2442 | 95.2306 | 106.1943 | 153.6549
264.5604 | 173.5604 | 331.0348 | 130.127 | 76.905 | 112.2939 | 130.6913 | 95.5683 | 106.5088 | 154.2829
265.5619 | 174.5619 | 331.3406 | 130.5811 | 77.305 | 112.6566 | 131.1331 | 95.9025 | 106.8275 | 154.9434
266.5633 | 175.5633 | 331.7896 | 131.035 | 77.7046 | 113.0154 | 131.5545 | 96.2358 | 107.1505 | 155.5698
267.5647 | 176.5647 | 332.1888 | 131.4901 | 78.1051 | 113.3818 | 132.0067 | 96.5674 | 107.4742 | 156.228
268.5662 | 177.5662 | 332.5547 | 131.9329 | 78.5006 | 113.7411 | 132.433 | 96.8996 | 107.7947 | 156.8551
269.5676 | 178.5676 | 332.8465 | 132.3947 | 78.8841 | 114.1137 | 132.8625 | 97.2324 | 108.115 | 157.5005
270.559 | 179.559 | 333.1983 | 132.8486 | 79.2847 | 114.4851 | 133.2959 | 97.5699 | 108.4369 | 158.1162
271.5605 | 180.5605 | 333.4353 | 133.3071 | 79.6835 | 114.8563 | 133.7251 | 97.8962 | 108.7618 | 158.7471
272.5619 | 181.5619 | 333.5418 | 133.7759 | 80.0627 | 115.2305 | 134.1651 | 98.2345 | 109.0819 | 159.3708
273.5634 | 182.5634 | 333.7274 | 134.2321 | 80.4624 | 115.592 | 134.5853 | 98.566 | 109.405 | 159.9538
274.5648 | 183.5648 | 333.7522 | 134.685 | 80.8575 | 115.9602 | 135.0065 | 98.9022 | 109.7259 | 160.5783
275.5662 | 184.5662 | 333.8488 | 135.1285 | 81.2482 | 116.3246 | 135.4301 | 99.2356 | 110.0574 | 161.1734
276.5677 | 185.5677 | 333.9763 | 135.5657 | 81.6375 | 116.6919 | 135.8304 | 99.5648 | 110.3913 | 161.7825
277.5691 | 186.5691 | 334.037 | 135.9967 | 82.029 | 117.0476 | 136.24 | 99.8946 | 110.7132 | 162.3618
278.5606 | 187.5606 | 333.9082 | 136.4229 | 82.4139 | 117.4119 | 136.6308 | 100.2233 | 111.0369 | 162.9646
279.562 | 188.562 | 333.8375 | 136.8534 | 82.8071 | 117.7626 | 137.0255 | 100.5642 | 111.3676 | 163.5571
280.5634 | 189.5634 | 333.7868 | 137.2804 | 83.1874 | 118.1197 | 137.4177 | 100.89 | 111.6862 | 164.1443
281.5649 | 190.5649 | 333.8353 | 137.708 | 83.5746 | 118.4646 | 137.8059 | 101.2136 | 112.0075 | 164.7376
282.5663 | 191.5663 | 333.8315 | 138.1481 | 83.9578 | 118.8184 | 138.2059 | 101.5453 | 112.3353 | 165.3001
283.5677 | 192.5677 | 333.8767 | 138.5744 | 84.3452 | 119.174 | 138.5976 | 101.8658 | 112.6559 | 165.8951
284.5692 | 193.5692 | 333.8983 | 139.0041 | 84.7393 | 119.5111 | 138.9849 | 102.1927 | 112.9707 | 166.4783
285.5606 | 194.5606 | 333.8571 | 139.4105 | 85.1042 | 119.8418 | 139.3739 | 102.5063 | 113.2811 | 167.0598
286.5621 | 195.5621 | 333.7805 | 139.8302 | 85.4822 | 120.1817 | 139.7617 | 102.827 | 113.605 | 167.6328
287.5635 | 196.5635 | 333.7518 | 140.2385 | 85.8717 | 120.5153 | 140.1392 | 103.1471 | 113.9073 | 168.2087
288.5649 | 197.5649 | 333.9079 | 140.6423 | 86.2429 | 120.85 | 140.5255 | 103.4558 | 114.2218 | 168.7552
289.5664 | 198.5664 | 333.9102 | 141.0477 | 86.6311 | 121.1813 | 140.887 | 103.779 | 114.5329 | 169.3325
290.5678 | 199.5678 | 333.881 | 141.4308 | 87.017 | 121.5106 | 141.2632 | 104.0893 | 114.8432 | 169.9023
291.5592 | 200.5592 | 333.8377 | 141.8347 | 87.3903 | 121.8404 | 141.6183 | 104.3962 | 115.1452 | 170.462
292.5607 | 201.5607 | 333.7745 | 142.2253 | 87.7579 | 122.1616 | 142.0009 | 104.7097 | 115.4499 | 171.0106
293.5621 | 202.5621 | 333.7419 | 142.6162 | 88.1375 | 122.4773 | 142.3577 | 105.0162 | 115.7562 | 171.5865
294.5636 | 203.5636 | 333.6065 | 143.0013 | 88.5105 | 122.7969 | 142.7251 | 105.3312 | 116.0584 | 172.1541
295.565 | 204.565 | 333.5424 | 143.3894 | 88.873 | 123.1122 | 143.0737 | 105.6338 | 116.3475 | 172.6693
296.5664 | 205.5664 | 333.4672 | 143.7662 | 89.2388 | 123.423 | 143.4237 | 105.9393 | 116.6322 | 173.2043
297.5679 | 206.5679 | 333.4351 | 144.151 | 89.6238 | 123.7394 | 143.7931 | 106.2471 | 116.9277 | 173.7041
298.5593 | 207.5593 | 333.2867 | 144.5301 | 89.9979 | 124.0437 | 144.1197 | 106.5407 | 117.2193 | 174.2271
299.5607 | 208.5607 | 333.2371 | 144.8929 | 90.3691 | 124.3629 | 144.4314 | 106.8485 | 117.5041 | 174.7646
300.5622 | 209.5622 | 333.0879 | 145.2511 | 90.7271 | 124.6715 | 144.764 | 107.1426 | 117.7856 | 175.3025
301.5636 | 210.5636 | 333.0855 | 145.6135 | 91.0859 | 124.9674 | 145.0862 | 107.4483 | 118.0693 | 175.8004
302.5651 | 211.5651 | 333.1266 | 145.9728 | 91.4562 | 125.2687 | 145.3944 | 107.7379 | 118.349 | 176.3178
303.5665 | 212.5665 | 333.0278 | 146.3255 | 91.8163 | 125.5615 | 145.7202 | 108.0323 | 118.6234 | 176.8007
304.5679 | 213.5679 | 332.8844 | 146.6902 | 92.1805 | 125.8577 | 146.034 | 108.3218 | 118.8974 | 177.3039
305.5694 | 214.5694 | 332.7622 | 147.0597 | 92.533 | 126.1517 | 146.3267 | 108.6123 | 119.1761 | 177.801
306.5608 | 215.5608 | 332.6335 | 147.4279 | 92.8846 | 126.4496 | 146.6244 | 108.9053 | 119.4441 | 178.2767
307.5623 | 216.5623 | 332.5467 | 147.8054 | 93.232 | 126.7358 | 146.9216 | 109.1909 | 119.7197 | 178.8073
308.5637 | 217.5637 | 332.4877 | 148.1764 | 93.5964 | 127.0235 | 147.2238 | 109.4891 | 119.9885 | 179.2922
309.5651 | 218.5651 | 332.3186 | 148.5497 | 93.9638 | 127.3088 | 147.5385 | 109.7833 | 120.263 | 179.7851
310.5666 | 219.5666 | 332.142 | 148.9149 | 94.3087 | 127.5957 | 147.864 | 110.0751 | 120.5335 | 180.2793
311.558 | 220.558 | 331.9002 | 149.2862 | 94.6563 | 127.8865 | 148.1888 | 110.3583 | 120.8098 | 180.7916
312.5594 | 221.5594 | 331.8052 | 149.6524 | 95.015 | 128.1687 | 148.5153 | 110.651 | 121.0815 | 181.2749
313.5609 | 222.5609 | 331.855 | 150.0047 | 95.3592 | 128.4552 | 148.8511 | 110.9406 | 121.3436 | 181.7731
314.5623 | 223.5623 | 331.9487 | 150.3765 | 95.7107 | 128.7382 | 149.1882 | 111.2275 | 121.614 | 182.2567
315.5638 | 224.5638 | 331.9414 | 150.7389 | 96.0639 | 129.0347 | 149.5175 | 111.5091 | 121.8733 | 182.7424
316.5652 | 225.5652 | 331.878 | 151.0954 | 96.4149 | 129.3193 | 149.8452 | 111.7942 | 122.1281 | 183.2195
317.5666 | 226.5666 | 331.7486 | 151.4574 | 96.7549 | 129.6055 | 150.1527 | 112.0772 | 122.3923 | 183.6973
318.5681 | 227.5681 | 331.7983 | 151.8157 | 97.1056 | 129.8835 | 150.4583 | 112.3593 | 122.6389 | 184.1487
319.5595 | 228.5595 | 331.8494 | 152.1754 | 97.4462 | 130.1631 | 150.7434 | 112.637 | 122.8905 | 184.5754
320.5609 | 229.5609 | 331.832 | 152.529 | 97.7825 | 130.4366 | 151.0314 | 112.9251 | 123.135 | 185.0382
321.5624 | 230.5624 | 331.7458 | 152.8802 | 98.1308 | 130.7133 | 151.325 | 113.2049 | 123.3721 | 185.483
322.5638 | 231.5638 | 331.7138 | 153.2415 | 98.4698 | 130.9878 | 151.5946 | 113.4817 | 123.6167 | 185.8907
323.5653 | 232.5653 | 331.6702 | 153.582 | 98.8236 | 131.2459 | 151.8593 | 113.7572 | 123.8653 | 186.3146
324.5667 | 233.5667 | 331.5647 | 153.9187 | 99.1581 | 131.4996 | 152.1282 | 114.032 | 124.1043 | 186.7245
325.5681 | 234.5681 | 331.6004 | 154.266 | 99.4969 | 131.7681 | 152.384 | 114.3164 | 124.3455 | 187.1876
326.5696 | 235.5696 | 331.6648 | 154.6063 | 99.8323 | 132.0277 | 152.632 | 114.5846 | 124.5908 | 187.6193
327.561 | 236.561 | 331.6086 | 154.9372 | 100.1746 | 132.2836 | 152.8802 | 114.8708 | 124.8264 | 188.064
328.5624 | 237.5624 | 331.5624 | 155.2802 | 100.5062 | 132.5432 | 153.142 | 115.1377 | 125.0589 | 188.4684
329.5639 | 238.5639 | 331.5544 | 155.6121 | 100.8462 | 132.8043 | 153.4182 | 115.4138 | 125.2919 | 188.9166
330.5653 | 239.5653 | 331.5556 | 155.9326 | 101.1872 | 133.0553 | 153.7209 | 115.6913 | 125.5371 | 189.323
331.5668 | 240.5668 | 331.6826 | 156.258 | 101.5158 | 133.3123 | 153.9924 | 115.9539 | 125.7759 | 189.7581
332.5582 | 241.5582 | 331.8667 | 156.5761 | 101.8471 | 133.5687 | 154.2856 | 116.2274 | 126.0106 | 190.1651
333.5596 | 242.5596 | 331.7906 | 156.9056 | 102.1893 | 133.8231 | 154.5627 | 116.4942 | 126.2428 | 190.5997
334.5611 | 243.5611 | 331.7228 | 157.2258 | 102.5161 | 134.0616 | 154.8411 | 116.7642 | 126.4807 | 191.0311
335.5625 | 244.5625 | 331.8015 | 157.5434 | 102.8491 | 134.2956 | 155.1043 | 117.0283 | 126.7141 | 191.4272
336.564 | 245.564 | 331.8583 | 157.869 | 103.1839 | 134.5407 | 155.3783 | 117.2949 | 126.9294 | 191.8231
337.5654 | 246.5654 | 331.9093 | 158.1799 | 103.519 | 134.7823 | 155.6411 | 117.5676 | 127.1586 | 192.2091
338.5668 | 247.5668 | 331.94 | 158.4987 | 103.8455 | 135.0252 | 155.899 | 117.8323 | 127.3819 | 192.6046
339.5683 | 248.5683 | 331.9187 | 158.8119 | 104.1861 | 135.2727 | 156.1564 | 118.0962 | 127.6066 | 192.9539
340.5797 | 249.5797 | 331.9936 | 159.1303 | 104.531 | 135.5289 | 156.3893 | 118.3703 | 127.8314 | 193.3632
341.5611 | 250.5611 | 332.0813 | 159.4312 | 104.8554 | 135.7734 | 156.6298 | 118.6315 | 128.0505 | 193.7389
342.5626 | 251.5626 | 332.0567 | 159.7339 | 105.2044 | 136.0313 | 156.8606 | 118.8985 | 128.2802 | 194.1312
343.564 | 252.564 | 331.952 | 160.035 | 105.561 | 136.279 | 157.0996 | 119.1634 | 128.4981 | 194.4827
344.5655 | 253.5655 | 331.8146 | 160.3272 | 105.9548 | 136.5288 | 157.3436 | 119.4233 | 128.7179 | 194.8741
345.5669 | 254.5669 | 331.7692 | 160.6154 | 106.3031 | 136.7829 | 157.565 | 119.6868 | 128.9432 | 195.2486
346.5683 | 255.5683 | 331.72 | 160.9081 | 106.6656 | 137.0287 | 157.7811 | 119.9503 | 129.1631 | 195.6185
347.5598 | 256.5598 | 331.6705 | 161.1849 | 107.0212 | 137.2805 | 158.0211 | 120.2105 | 129.3858 | 196.0035
348.5612 | 257.5612 | 331.6561 | 161.4637 | 107.3684 | 137.5267 | 158.2317 | 120.4676 | 129.6009 | 196.3608
349.5626 | 258.5626 | 331.6193 | 161.7385 | 107.7096 | 137.7727 | 158.4682 | 120.7386 | 129.8231 | 196.7575
350.5641 | 259.5641 | 331.6818 | 162.0086 | 108.048 | 138.0229 | 158.6844 | 120.9926 | 130.0388 | 197.1342
351.5655 | 260.5655 | 331.6118 | 162.2707 | 108.387 | 138.268 | 158.9306 | 121.2493 | 130.2572 | 197.5336
352.567 | 261.567 | 331.5975 | 162.5516 | 108.7266 | 138.5113 | 159.1591 | 121.5034 | 130.4692 | 197.9117
353.5584 | 262.5584 | 331.8539 | 162.8271 | 109.0583 | 138.7539 | 159.4068 | 121.7632 | 130.6861 | 198.2773
354.5598 | 263.5598 | 331.9411 | 163.1042 | 109.3911 | 138.9979 | 159.6479 | 122.0073 | 130.9025 | 198.649
355.5613 | 264.5613 | 331.972 | 163.3705 | 109.7253 | 139.2463 | 159.9123 | 122.2675 | 131.111 | 199.0084
356.5627 | 265.5627 | 332.0144 | 163.6404 | 110.0643 | 139.496 | 160.1598 | 122.5204 | 131.3274 | 199.3832
357.5642 | 266.5642 | 332.0521 | 163.9076 | 110.3914 | 139.7493 | 160.4387 | 122.7673 | 131.5479 | 199.7257
358.5656 | 267.5656 | 332.1223 | 164.1862 | 110.7341 | 139.992 | 160.6804 | 123.0185 | 131.7529 | 200.076
359.567 | 268.567 | 332.2253 | 164.459 | 111.0692 | 140.2378 | 160.9396 | 123.2745 | 131.964 | 200.4588
360.5685 | 269.5685 | 332.2434 | 164.7358 | 111.4024 | 140.4865 | 161.1959 | 123.5264 | 132.1812 | 200.8063
361.5599 | 270.5599 | 332.4062 | 165.0109 | 111.7357 | 140.731 | 161.4413 | 123.7738 | 132.3883 | 201.1625
362.5613 | 271.5613 | 332.5016 | 165.2907 | 112.0735 | 140.9725 | 161.683 | 124.0261 | 132.5967 | 201.4882
363.5628 | 272.5628 | 332.6193 | 165.5729 | 112.3969 | 141.211 | 161.8886 | 124.286 | 132.8019 | 201.8458
364.5642 | 273.5642 | 332.7974 | 165.8533 | 112.744 | 141.4518 | 162.0983 | 124.532 | 133.0099 | 202.1459
365.5657 | 274.5657 | 332.8749 | 166.1415 | 113.0768 | 141.7007 | 162.3111 | 124.7812 | 133.2086 | 202.492
366.5671 | 275.5671 | 332.8721 | 166.4356 | 113.4051 | 141.9472 | 162.5207 | 125.0305 | 133.4154 | 202.7703
367.5685 | 276.5685 | 332.7904 | 166.7324 | 113.7489 | 142.193 | 162.7213 | 125.2792 | 133.6133 | 203.0555
368.56 | 277.56 | 332.9147 | 167.0164 | 114.0908 | 142.441 | 162.9013 | 125.5263 | 133.8266 | 203.3744
369.5614 | 278.5614 | 333.0155 | 167.2994 | 114.4229 | 142.6804 | 163.0803 | 125.7691 | 134.0232 | 203.6494
370.5628 | 279.5628 | 333.0963 | 167.5972 | 114.7664 | 142.9178 | 163.2933 | 126.014 | 134.2303 | 204.0244
371.5643 | 280.5643 | 333.0805 | 167.8908 | 115.1272 | 143.1557 | 163.5052 | 126.2587 | 134.4221 | 204.3411
372.5657 | 281.5657 | 333.0133 | 168.1985 | 115.4896 | 143.4 | 163.7398 | 126.507 | 134.6233 | 204.6961
373.5672 | 282.5672 | 332.9869 | 168.4942 | 115.8389 | 143.6281 | 163.9881 | 126.7478 | 134.828 | 205.023
374.5586 | 283.5586 | 332.9046 | 168.8015 | 116.193 | 143.8661 | 164.2326 | 126.9876 | 135.0179 | 205.3522
375.56 | 284.56 | 332.8442 | 169.118 | 116.5483 | 144.095 | 164.4694 | 127.2315 | 135.2097 | 205.647
376.5615 | 285.5615 | 332.7401 | 169.4353 | 116.9298 | 144.3282 | 164.719 | 127.4713 | 135.3967 | 205.9824
377.5629 | 286.5629 | 332.7381 | 169.7606 | 117.3078 | 144.5504 | 164.9673 | 127.7053 | 135.5777 | 206.3134
378.5643 | 287.5643 | 332.651 | 170.0925 | 117.6692 | 144.7874 | 165.2005 | 127.95 | 135.7785 | 206.6135
379.5658 | 288.5658 | 332.6478 | 170.4132 | 118.0639 | 145.0131 | 165.4252 | 128.1788 | 135.9579 | 206.9429
380.5672 | 289.5672 | 332.6493 | 170.7452 | 118.4452 | 145.2436 | 165.6452 | 128.4214 | 136.1431 | 207.2184
381.5687 | 290.5687 | 332.6015 | 171.0773 | 118.8337 | 145.4785 | 165.8683 | 128.6586 | 136.322 | 207.4874
382.5601 | 291.5601 | 332.4761 | 171.4124 | 119.2261 | 145.7136 | 166.0733 | 128.8967 | 136.5049 | 207.753
383.5615 | 292.5615 | 332.3561 | 171.7535 | 119.6306 | 145.9566 | 166.2685 | 129.1299 | 136.6927 | 208.0729
384.563 | 293.563 | 332.1921 | 172.0936 | 120.0429 | 146.1965 | 166.4869 | 129.3592 | 136.8754 | 208.407
385.5644 | 294.5644 | 332.0196 | 172.4335 | 120.455 | 146.4469 | 166.7099 | 129.5959 | 137.0538 | 208.6875
386.5659 | 295.5659 | 331.9687 | 172.7789 | 120.8628 | 146.6858 | 166.9361 | 129.8273 | 137.2352 | 209.0148
387.5673 | 296.5673 | 331.9792 | 173.1288 | 121.2497 | 146.9453 | 167.1656 | 130.0516 | 137.4174 | 209.3043
388.5687 | 297.5687 | 331.9951 | 173.4816 | 121.6378 | 147.2083 | 167.3806 | 130.2793 | 137.5981 | 209.5968
389.5602 | 298.5602 | 331.8702 | 173.8255 | 122.0192 | 147.457 | 167.6092 | 130.5102 | 137.7734 | 209.8612
390.5616 | 299.5616 | 331.846 | 174.174 | 122.4182 | 147.7303 | 167.8152 | 130.7308 | 137.9523 | 210.1858
391.563 | 300.563 | 331.7492 | 174.5049 | 122.8391 | 147.9956 | 168.0078 | 130.9631 | 138.1289 | 210.4224
392.5645 | 301.5645 | 331.6268 | 174.8516 | 123.2402 | 148.2621 | 168.219 | 131.1882 | 138.3067 | 210.6875
393.5659 | 302.5659 | 331.3461 | 175.1913 | 123.6406 | 148.5319 | 168.4128 | 131.409 | 138.4823 | 210.9352
394.5674 | 303.5674 | 331.2931 | 175.5332 | 124.0389 | 148.7904 | 168.5976 | 131.6303 | 138.6681 | 211.2234
395.5688 | 304.5688 | 331.3199 | 175.8956 | 124.4384 | 149.0616 | 168.8049 | 131.8447 | 138.8292 | 211.5221
396.5602 | 305.5602 | 331.1713 | 176.2434 | 124.8547 | 149.3177 | 168.9996 | 132.0673 | 139.0022 | 211.7921
397.5617 | 306.5617 | 331.0443 | 176.5794 | 125.2556 | 149.5817 | 169.1761 | 132.2746 | 139.1779 | 212.0987
398.5631 | 307.5631 | 330.9313 | 176.9025 | 125.6677 | 149.8424 | 169.3774 | 132.4895 | 139.3524 | 212.3634
399.5645 | 308.5645 | 331.0412 | 177.2422 | 126.0782 | 150.1056 | 169.5778 | 132.711 | 139.5157 | 212.57
400.566 | 309.566 | 331.1375 | 177.5794 | 126.4932 | 150.3676 | 169.7732 | 132.9235 | 139.6833 | 212.7629
401.5674 | 310.5674 | 331.2184 | 177.9427 | 126.8922 | 150.6188 | 169.9745 | 133.1234 | 139.8559 | 213.0175
402.5589 | 311.5589 | 331.3322 | 178.2975 | 127.2822 | 150.8919 | 170.159 | 133.3372 | 140.0202 | 213.2471
403.5603 | 312.5603 | 331.4289 | 178.6505 | 127.7087 | 151.1556 | 170.3743 | 133.5343 | 140.1828 | 213.4957
404.5617 | 313.5617 | 331.4452 | 178.998 | 128.1109 | 151.4248 | 170.5644 | 133.7445 | 140.3546 | 213.723
405.5632 | 314.5632 | 331.5428 | 179.351 | 128.5177 | 151.7068 | 170.7597 | 133.9555 | 140.5264 | 213.995
406.5646 | 315.5646 | 331.5635 | 179.7022 | 128.9162 | 151.9787 | 170.9687 | 134.1531 | 140.6925 | 214.2675
407.5661 | 316.5661 | 331.5821 | 180.0567 | 129.328 | 152.2589 | 171.184 | 134.3587 | 140.8582 | 214.5228
408.5675 | 317.5675 | 331.6608 | 180.4207 | 129.7663 | 152.5431 | 171.4135 | 134.5622 | 141.0279 | 214.7864
409.5689 | 318.5689 | 331.6895 | 180.7716 | 130.1892 | 152.8324 | 171.6346 | 134.762 | 141.2043 | 215.0346
410.5604 | 319.5604 | 331.749 | 181.1258 | 130.5792 | 153.1302 | 171.8697 | 134.9563 | 141.3695 | 215.3003
411.5618 | 320.5618 | 331.7925 | 181.4759 | 130.9489 | 153.4227 | 172.0683 | 135.156 | 141.5335 | 215.5176
412.5632 | 321.5632 | 331.8195 | 181.8332 | 131.3134 | 153.7143 | 172.2602 | 135.3434 | 141.702 | 215.7725
413.5647 | 322.5647 | 331.8876 | 182.1845 | 131.6718 | 154.0077 | 172.4596 | 135.5421 | 141.868 | 216.0137
414.5661 | 323.5661 | 332.0265 | 182.539 | 132.0309 | 154.3118 | 172.6644 | 135.7329 | 142.0399 | 216.2769
415.5676 | 324.5676 | 332.0824 | 182.8781 | 132.3951 | 154.6066 | 172.8831 | 135.9252 | 142.2163 | 216.522
416.559 | 325.559 | 332.0774 | 183.2095 | 132.7248 | 154.9115 | 173.099 | 136.114 | 142.3887 | 216.7347
417.5604 | 326.5604 | 332.1504 | 183.5539 | 133.073 | 155.204 | 173.2824 | 136.3084 | 142.5575 | 216.9591
418.5619 | 327.5619 | 332.2637 | 183.8991 | 133.4111 | 155.5004 | 173.4637 | 136.486 | 142.7366 | 217.1857
419.5633 | 328.5633 | 332.367 | 184.2469 | 133.7487 | 155.788 | 173.6662 | 136.6623 | 142.9012 | 217.4552
420.5647 | 329.5647 | 332.3639 | 184.5956 | 134.0998 | 156.0743 | 173.8528 | 136.8442 | 143.0709 | 217.6576
421.5662 | 330.5662 | 332.3656 | 184.9429 | 134.4655 | 156.3652 | 174.0512 | 137.0196 | 143.2438 | 217.9005
422.5676 | 331.5676 | 332.5172 | 185.2947 | 134.8256 | 156.6545 | 174.2367 | 137.1997 | 143.4074 | 218.0865
423.559 | 332.559 | 332.6183 | 185.6518 | 135.1825 | 156.9273 | 174.4227 | 137.3624 | 143.5797 | 218.323
424.5605 | 333.5605 | 332.7282 | 186.006 | 135.5374 | 157.2141 | 174.6101 | 137.5368 | 143.7397 | 218.5236
425.5619 | 334.5619 | 332.8069 | 186.3452 | 135.9085 | 157.4935 | 174.8056 | 137.6995 | 143.9079 | 218.7134
426.5634 | 335.5634 | 332.9128 | 186.6843 | 136.279 | 157.7744 | 175.0024 | 137.8578 | 144.0567 | 218.9038
427.5648 | 336.5648 | 333.014 | 187.0179 | 136.6382 | 158.0602 | 175.1924 | 138.0073 | 144.2135 | 219.0553
428.5662 | 337.5662 | 333.0312 | 187.3305 | 137.0065 | 158.3361 | 175.3553 | 138.1653 | 144.3711 | 219.2596
429.5677 | 338.5677 | 332.9665 | 187.6557 | 137.3732 | 158.6259 | 175.5249 | 138.3174 | 144.5199 | 219.4367
430.5691 | 339.5691 | 332.8705 | 187.977 | 137.734 | 158.9093 | 175.6965 | 138.4501 | 144.6809 | 219.6634
431.5606 | 340.5606 | 332.7496 | 188.2954 | 138.1093 | 159.2048 | 175.8689 | 138.5969 | 144.8392 | 219.8078
432.562 | 341.562 | 332.6539 | 188.6133 | 138.4549 | 159.4957 | 176.0641 | 138.7374 | 144.9986 | 220.0167
433.5634 | 342.5634 | 332.5504 | 188.9343 | 138.8364 | 159.7847 | 176.2568 | 138.8726 | 145.1527 | 220.2176
434.5649 | 343.5649 | 332.4404 | 189.2587 | 139.2045 | 160.0952 | 176.4447 | 138.9948 | 145.3145 | 220.4314
435.5663 | 344.5663 | 332.2161 | 189.5804 | 139.5572 | 160.3848 | 176.6515 | 139.118 | 145.4707 | 220.6427
436.5678 | 345.5678 | 332.1416 | 189.902 | 139.9269 | 160.6869 | 176.8498 | 139.2492 | 145.629 | 220.8138
437.5592 | 346.5592 | 332.2131 | 190.2025 | 140.2692 | 160.9834 | 177.0519 | 139.3596 | 145.779 | 220.9924
438.5606 | 347.5606 | 332.2886 | 190.5137 | 140.6377 | 161.2774 | 177.2385 | 139.4763 | 145.9393 | 221.1613
439.5621 | 348.5621 | 332.3308 | 190.825 | 140.983 | 161.5723 | 177.4201 | 139.5829 | 146.0943 | 221.3999
440.5635 | 349.5635 | 332.3182 | 191.1323 | 141.3386 | 161.8555 | 177.5887 | 139.6894 | 146.2399 | 221.5493
441.5649 | 350.5649 | 332.2939 | 191.456 | 141.698 | 162.1527 | 177.7481 | 139.7947 | 146.3835 | 221.7619
442.5664 | 351.5664 | 332.2275 | 191.7747 | 142.0421 | 162.4319 | 177.8964 | 139.9071 | 146.5302 | 221.942
443.5678 | 352.5678 | 332.1484 | 192.084 | 142.3975 | 162.7116 | 178.0488 | 140.0026 | 146.6807 | 222.1743
444.5592 | 353.5592 | 332.0524 | 192.3988 | 142.7473 | 163.0055 | 178.223 | 140.1102 | 146.8236 | 222.3548
445.5607 | 354.5607 | 331.9209 | 192.7158 | 143.1116 | 163.287 | 178.3582 | 140.2136 | 146.986 | 222.5082
446.5621 | 355.5621 | 331.8142 | 193.0352 | 143.4614 | 163.5626 | 178.5154 | 140.3241 | 147.1381 | 222.7002
447.5636 | 356.5636 | 331.6923 | 193.3505 | 143.8083 | 163.8359 | 178.6681 | 140.4287 | 147.2856 | 222.9097
448.565 | 357.565 | 331.5287 | 193.6694 | 144.1705 | 164.1239 | 178.8248 | 140.5359 | 147.4488 | 223.1317
449.5664 | 358.5664 | 331.4804 | 193.9908 | 144.5296 | 164.4018 | 179.0145 | 140.6463 | 147.6097 | 223.3007
450.5679 | 359.5679 | 331.5854 | 194.3051 | 144.885 | 164.6769 | 179.2067 | 140.7648 | 147.7712 | 223.5188
451.5693 | 360.5693 | 331.7213 | 194.5826 | 145.2414 | 164.9663 | 179.4058 | 140.8798 | 147.9339 | 223.7108
452.5608 | 361.5608 | 331.7548 | 194.8853 | 145.5853 | 165.244 | 179.6176 | 140.9873 | 148.0905 | 223.8951
453.5622 | 362.5622 | 331.8779 | 195.1977 | 145.9382 | 165.5269 | 179.8086 | 141.1108 | 148.2505 | 224.0405
454.5636 | 363.5636 | 332.0575 | 195.5203 | 146.2855 | 165.8187 | 180.012 | 141.2305 | 148.4018 | 224.2305
455.5651 | 364.5651 | 332.1361 | 195.8534 | 146.6324 | 166.1051 | 180.2211 | 141.3462 | 148.5586 | 224.4152
456.5665 | 365.5665 | 332.2142 | 196.1729 | 146.9718 | 166.3865 | 180.427 | 141.4693 | 148.7209 | 224.5588
457.568 | 366.568 | 332.2019 | 196.4736 | 147.326 | 166.6696 | 180.6225 | 141.5982 | 148.8761 | 224.7474
458.5694 | 367.5694 | 332.259 | 196.756 | 147.6782 | 166.9574 | 180.8191 | 141.7344 | 149.0343 | 224.9014
459.5608 | 368.5608 | 332.2008 | 197.047 | 148.0307 | 167.2259 | 181.0232 | 141.8536 | 149.188 | 225.1383
460.5623 | 369.5623 | 332.1259 | 197.3299 | 148.3672 | 167.4947 | 181.2473 | 141.9936 | 149.3431 | 225.3152
461.5637 | 370.5637 | 332.1647 | 197.6131 | 148.7144 | 167.786 | 181.46 | 142.1263 | 149.5097 | 225.5199
462.5651 | 371.5651 | 332.1932 | 197.8806 | 149.0641 | 168.0568 | 181.6874 | 142.2759 | 149.6676 | 225.6924
463.5666 | 372.5666 | 332.207 | 198.175 | 149.3905 | 168.3368 | 181.9071 | 142.4168 | 149.823 | 225.9073
464.568 | 373.568 | 332.1031 | 198.4946 | 149.7492 | 168.6097 | 182.1183 | 142.5648 | 149.9876 | 226.0882
465.5594 | 374.5594 | 332.1342 | 198.823 | 150.084 | 168.8891 | 182.3227 | 142.7231 | 150.1417 | 226.2711
466.5609 | 375.5609 | 332.072 | 199.1511 | 150.4001 | 169.1681 | 182.5198 | 142.8784 | 150.3049 | 226.4737
467.5824 | 376.5824 | 332.0327 | 199.4691 | 150.7581 | 169.4526 | 182.7337 | 143.0424 | 150.4632 | 226.6631
468.5638 | 377.5638 | 331.9459 | 199.7675 | 151.0844 | 169.7317 | 182.9456 | 143.2008 | 150.6226 | 226.821
469.5652 | 378.5652 | 331.7788 | 200.065 | 151.4263 | 170.0156 | 183.164 | 143.3631 | 150.7838 | 227.0027
470.5666 | 379.5666 | 331.6766 | 200.3572 | 151.7616 | 170.2939 | 183.3934 | 143.541 | 150.9438 | 227.2156
471.5681 | 380.5681 | 331.5405 | 200.6474 | 152.1039 | 170.5772 | 183.6171 | 143.7105 | 151.1015 | 227.3775
472.5695 | 381.5695 | 331.4566 | 200.9669 | 152.431 | 170.8552 | 183.8466 | 143.8887 | 151.2684 | 227.5858
473.5609 | 382.5609 | 331.5301 | 201.2737 | 152.775 | 171.1376 | 184.0793 | 144.0589 | 151.437 | 227.7586
474.5624 | 383.5624 | 331.5812 | 201.5599 | 153.1179 | 171.4196 | 184.3028 | 144.2336 | 151.6016 | 227.9395
475.5638 | 384.5638 | 331.7199 | 201.8127 | 153.4469 | 171.7101 | 184.507 | 144.3987 | 151.7616 | 228.1016
476.5653 | 385.5653 | 331.9465 | 202.0733 | 153.792 | 171.9967 | 184.6984 | 144.5834 | 151.9326 | 228.226
477.5667 | 386.5667 | 332.149 | 202.345 | 154.1333 | 172.2869 | 184.8793 | 144.7535 | 152.0986 | 228.3916
478.5681 | 387.5681 | 332.2177 | 202.6404 | 154.4588 | 172.582 | 185.056 | 144.9307 | 152.2594 | 228.5724
479.5696 | 388.5696 | 332.2785 | 202.9355 | 154.7889 | 172.8669 | 185.2242 | 145.1093 | 152.423 | 228.7161
480.561 | 389.561 | 332.3674 | 203.2435 | 155.1175 | 173.1482 | 185.3586 | 145.2823 | 152.593 | 228.8417
481.5625 | 390.5625 | 332.4221 | 203.5128 | 155.449 | 173.4204 | 185.4978 | 145.4602 | 152.7582 | 228.9894
482.5639 | 391.5639 | 332.4487 | 203.7816 | 155.7803 | 173.7012 | 185.6282 | 145.6378 | 152.928 | 229.124
483.5653 | 392.5653 | 332.3376 | 204.0375 | 156.1031 | 173.9748 | 185.7659 | 145.8213 | 153.0905 | 229.2737
484.5668 | 393.5668 | 332.1759 | 204.3069 | 156.4488 | 174.2416 | 185.8968 | 146.0007 | 153.264 | 229.4368
485.5582 | 394.5582 | 331.9924 | 204.578 | 156.7626 | 174.5146 | 186.0348 | 146.1866 | 153.441 | 229.5947
486.5596 | 395.5596 | 331.9084 | 204.8564 | 157.1034 | 174.7867 | 186.1861 | 146.367 | 153.6165 | 229.7429
487.5611 | 396.5611 | 331.8046 | 205.117 | 157.4207 | 175.0533 | 186.3544 | 146.5565 | 153.7843 | 229.9219
488.5625 | 397.5625 | 331.7537 | 205.3879 | 157.7414 | 175.3193 | 186.5455 | 146.7483 | 153.9665 | 230.0465
489.564 | 398.564 | 331.7488 | 205.6732 | 158.0731 | 175.5838 | 186.7283 | 146.9279 | 154.1276 | 230.2434
490.5654 | 399.5654 | 331.7894 | 205.9452 | 158.3935 | 175.8468 | 186.9398 | 147.1169 | 154.3034 | 230.3909
491.5668 | 400.5668 | 331.8025 | 206.2142 | 158.7188 | 176.1196 | 187.1581 | 147.3037 | 154.4737 | 230.5756
492.5583 | 401.5583 | 331.7973 | 206.4793 | 159.0443 | 176.3917 | 187.3844 | 147.4905 | 154.6401 | 230.7447
493.5597 | 402.5597 | 331.8125 | 206.7528 | 159.3845 | 176.6565 | 187.6008 | 147.6698 | 154.8031 | 230.924
494.5611 | 403.5611 | 331.8399 | 207.0135 | 159.7087 | 176.9206 | 187.7917 | 147.856 | 154.9699 | 231.1139
495.5626 | 404.5626 | 331.8855 | 207.3024 | 160.0312 | 177.1729 | 187.9495 | 148.0483 | 155.1297 | 231.2414
496.564 | 405.564 | 332.0046 | 207.5265 | 160.3545 | 177.4312 | 188.0937 | 148.2344 | 155.2909 | 231.4092
497.5655 | 406.5655 | 331.9614 | 207.7622 | 160.6839 | 177.6677 | 188.2763 | 148.4328 | 155.4659 | 231.5448
498.5669 | 407.5669 | 331.9914 | 208.02 | 160.9995 | 177.9111 | 188.4347 | 148.6084 | 155.6218 | 231.7328
499.5683 | 408.5683 | 332.2146 | 208.2965 | 161.3056 | 178.1408 | 188.6426 | 148.8041 | 155.7913 | 231.845
500.5698 | 409.5698 | 332.4877 | 208.5754 | 161.6366 | 178.3777 | 188.8489 | 148.9922 | 155.9742 | 232.0187
501.5612 | 410.5612 | 332.6176 | 208.861 | 161.9693 | 178.6019 | 189.063 | 149.1857 | 156.15 | 232.1995
502.5626 | 411.5626 | 332.6497 | 209.138 | 162.2767 | 178.8302 | 189.2823 | 149.3678 | 156.3202 | 232.3272
503.5641 | 412.5641 | 332.6968 | 209.421 | 162.5973 | 179.0639 | 189.4871 | 149.5637 | 156.5038 | 232.5247
504.5655 | 413.5655 | 332.7456 | 209.7062 | 162.9017 | 179.2905 | 189.6958 | 149.7492 | 156.6832 | 232.6818
505.567 | 414.567 | 332.65 | 209.9876 | 163.2099 | 179.5194 | 189.9179 | 149.9446 | 156.8738 | 232.858
506.5684 | 415.5684 | 332.5742 | 210.2633 | 163.5564 | 179.7527 | 190.1324 | 150.1357 | 157.0481 | 233.0178
507.5598 | 416.5598 | 332.5461 | 210.5476 | 163.8746 | 179.9822 | 190.3645 | 150.3247 | 157.2359 | 233.1823
508.5613 | 417.5613 | 332.583 | 210.8163 | 164.1797 | 180.2046 | 190.5866 | 150.5269 | 157.4218 | 233.3347
509.5627 | 418.5627 | 332.6167 | 211.0746 | 164.497 | 180.433 | 190.8128 | 150.7207 | 157.5919 | 233.5063
510.5642 | 419.5642 | 332.5198 | 211.3414 | 164.7922 | 180.663 | 191.0511 | 150.9152 | 157.7723 | 233.6549
511.5656 | 420.5656 | 332.4034 | 211.5645 | 165.1206 | 180.8943 | 191.2974 | 151.1162 | 157.9519 | 233.832
512.567 | 421.567 | 332.3245 | 211.8282 | 165.4256 | 181.1242 | 191.54 | 151.3093 | 158.1353 | 233.9804
513.5585 | 422.5585 | 332.2146 | 211.9966 | 165.7371 | 181.3468 | 191.7703 | 151.497 | 158.3121 | 234.1395
514.5699 | 423.5699 | 332.1649 | 212.2469 | 166.0487 | 181.5637 | 192.0012 | 151.6934 | 158.4957 | 234.2822
515.5613 | 424.5613 | 332.2397 | 212.5041 | 166.3652 | 181.7935 | 192.2187 | 151.8929 | 158.6767 | 234.4102
516.5628 | 425.5628 | 332.2235 | 212.7413 | 166.6588 | 182.0132 | 192.3968 | 152.0933 | 158.8612 | 234.5817
517.5642 | 426.5642 | 332.2244 | 212.9747 | 166.982 | 182.2213 | 192.5811 | 152.2891 | 159.0529 | 234.7062
518.5657 | 427.5657 | 332.2113 | 213.225 | 167.2836 | 182.4459 | 192.7412 | 152.4839 | 159.2295 | 234.8458
519.5671 | 428.5671 | 332.2139 | 213.4533 | 167.5832 | 182.6626 | 192.921 | 152.6728 | 159.405 | 235.0121
520.5685 | 429.5685 | 332.1718 | 213.6093 | 167.8942 | 182.8655 | 193.1125 | 152.8783 | 159.5881 | 235.1485
521.56 | 430.56 | 332.0868 | 213.8733 | 168.191 | 183.0793 | 193.3116 | 153.0734 | 159.7644 | 235.3011
522.5614 | 431.5614 | 331.9255 | 214.1409 | 168.5054 | 183.2919 | 193.5396 | 153.2727 | 159.9559 | 235.4573
523.5628 | 432.5628 | 331.8055 | 214.3874 | 168.8191 | 183.5059 | 193.7656 | 153.4739 | 160.1376 | 235.6241
524.5643 | 433.5643 | 331.8465 | 214.6423 | 169.1186 | 183.7211 | 193.9697 | 153.6726 | 160.3203 | 235.7189
525.5657 | 434.5657 | 331.9762 | 214.9089 | 169.4115 | 183.9426 | 194.1333 | 153.851 | 160.5079 | 235.8719
526.5672 | 435.5672 | 332.2225 | 215.1827 | 169.7317 | 184.1535 | 194.2794 | 154.055 | 160.6737 | 235.9824
527.5586 | 436.5586 | 332.4477 | 215.4149 | 170.0328 | 184.3714 | 194.4118 | 154.2473 | 160.8547 | 236.1269
528.56 | 437.56 | 332.48 | 215.6195 | 170.3287 | 184.5804 | 194.5603 | 154.4362 | 161.0352 | 236.2412
529.5615 | 438.5615 | 332.4983 | 215.8364 | 170.6394 | 184.7979 | 194.7385 | 154.631 | 161.2039 | 236.4046
530.5629 | 439.5629 | 332.4471 | 216.0893 | 170.9301 | 185.0229 | 194.9096 | 154.825 | 161.3831 | 236.4992
531.5644 | 440.5644 | 332.4349 | 216.3296 | 171.2388 | 185.241 | 195.0584 | 155.0214 | 161.5604 | 236.5774
532.5658 | 441.5658 | 332.3682 | 216.5138 | 171.5458 | 185.4532 | 195.2096 | 155.2134 | 161.734 | 236.6905
533.5672 | 442.5672 | 332.3534 | 216.7125 | 171.8345 | 185.6655 | 195.3664 | 155.4022 | 161.9123 | 236.8215
534.5587 | 443.5587 | 332.4102 | 216.9826 | 172.1365 | 185.8571 | 195.5509 | 155.6001 | 162.0829 | 236.9734
535.5601 | 444.5601 | 332.376 | 217.2511 | 172.4318 | 186.063 | 195.7357 | 155.7963 | 162.2577 | 237.0926
536.5615 | 445.5615 | 332.3196 | 217.5038 | 172.729 | 186.2615 | 195.9514 | 155.9958 | 162.4347 | 237.2287
537.563 | 446.563 | 332.2409 | 217.7234 | 173.0228 | 186.4407 | 196.1596 | 156.1904 | 162.6079 | 237.3619
538.5644 | 447.5644 | 332.2125 | 217.9821 | 173.3311 | 186.6327 | 196.3643 | 156.3914 | 162.7743 | 237.5036
539.5659 | 448.5659 | 332.2545 | 218.2447 | 173.624 | 186.8001 | 196.5452 | 156.5897 | 162.9406 | 237.6073
540.5673 | 449.5673 | 332.1708 | 218.4514 | 173.9129 | 186.9784 | 196.7164 | 156.7835 | 163.0993 | 237.7172
541.5687 | 450.5687 | 332.1034 | 218.6615 | 174.2032 | 187.1453 | 196.9034 | 156.9887 | 163.2678 | 237.8008
542.5602 | 451.5602 | 332.1709 | 218.9142 | 174.4972 | 187.3214 | 197.096 | 157.1774 | 163.4336 | 237.9228
543.5616 | 452.5616 | 332.3029 | 219.1661 | 174.7888 | 187.4943 | 197.2518 | 157.3796 | 163.5876 | 238.0103
544.563 | 453.563 | 332.3304 | 219.4181 | 175.071 | 187.6554 | 197.4089 | 157.5775 | 163.7473 | 238.0757
545.5645 | 454.5645 | 332.3493 | 219.6727 | 175.3578 | 187.8228 | 197.5349 | 157.7839 | 163.9017 | 238.1306
546.5659 | 455.5659 | 332.2736 | 219.9726 | 175.6397 | 187.9824 | 197.6622 | 157.9794 | 164.059 | 238.2439
547.5674 | 456.5674 | 332.3163 | 220.2632 | 175.9217 | 188.1366 | 197.794 | 158.183 | 164.2206 | 238.3221
548.5688 | 457.5688 | 332.4168 | 220.5261 | 176.2064 | 188.2918 | 197.919 | 158.3845 | 164.3873 | 238.4251
549.5602 | 458.5602 | 332.3896 | 220.7668 | 176.4792 | 188.4504 | 198.0548 | 158.588 | 164.5428 | 238.5143
550.5617 | 459.5617 | 332.3297 | 221.053 | 176.7552 | 188.5938 | 198.1861 | 158.7773 | 164.7015 | 238.6174
551.5631 | 460.5631 | 332.3041 | 221.2925 | 177.047 | 188.7449 | 198.3018 | 158.9886 | 164.8574 | 238.6567
552.5645 | 461.5645 | 332.2858 | 221.5506 | 177.3271 | 188.8894 | 198.3917 | 159.1817 | 165.0127 | 238.7244
553.566 | 462.566 | 332.2186 | 221.7988 | 177.6149 | 189.0401 | 198.4896 | 159.3807 | 165.1663 | 238.8036
554.5674 | 463.5674 | 332.1923 | 222.0392 | 177.8958 | 189.1926 | 198.6262 | 159.586 | 165.3225 | 238.9028
555.5589 | 464.5589 | 332.0753 | 222.2631 | 178.1615 | 189.3448 | 198.7882 | 159.7786 | 165.4742 | 239.0143
556.5703 | 465.5703 | 331.9684 | 222.4083 | 178.4315 | 189.501 | 198.9691 | 159.9887 | 165.631 | 239.1143
557.5617 | 466.5617 | 331.9163 | 222.659 | 178.7052 | 189.6518 | 199.1752 | 160.185 | 165.7835 | 239.1952
558.5632 | 467.5632 | 331.8313 | 222.8822 | 178.9886 | 189.8037 | 199.4081 | 160.3851 | 165.9363 | 239.3232
559.5646 | 468.5646 | 331.7552 | 223.0738 | 179.2538 | 189.9594 | 199.62 | 160.5827 | 166.0892 | 239.4382
560.5661 | 469.5661 | 331.7365 | 223.1996 | 179.5294 | 190.1221 | 199.8532 | 160.7869 | 166.2521 | 239.5295
561.5675 | 470.5675 | 331.7922 | 223.3895 | 179.809 | 190.275 | 200.0573 | 160.9862 | 166.4033 | 239.6108
562.5689 | 471.5689 | 331.8146 | 223.5236 | 180.0661 | 190.444 | 200.2681 | 161.1777 | 166.5613 | 239.6697
563.5604 | 472.5604 | 331.8125 | 223.736 | 180.3478 | 190.6078 | 200.419 | 161.3749 | 166.7154 | 239.7578
564.5618 | 473.5618 | 331.8131 | 223.9606 | 180.6121 | 190.7741 | 200.5612 | 161.5715 | 166.8668 | 239.8272
565.5632 | 474.5632 | 331.8194 | 224.2319 | 180.8792 | 190.9338 | 200.6599 | 161.7682 | 167.0228 | 239.8729
566.5647 | 475.5647 | 331.7456 | 224.4733 | 181.1483 | 191.0903 | 200.7588 | 161.9642 | 167.1766 | 239.9684
567.5661 | 476.5661 | 331.7375 | 224.6787 | 181.4175 | 191.2431 | 200.8861 | 162.1588 | 167.3317 | 240.0506
568.5676 | 477.5676 | 331.7452 | 224.8818 | 181.6811 | 191.395 | 201.0228 | 162.3492 | 167.489 | 240.1199
569.559 | 478.559 | 331.6262 | 225.1147 | 181.9471 | 191.5492 | 201.1782 | 162.5448 | 167.6327 | 240.1906
570.5604 | 479.5604 | 331.5365 | 225.3197 | 182.2177 | 191.7026 | 201.3417 | 162.7371 | 167.7924 | 240.2842
571.5619 | 480.5619 | 331.5281 | 225.539 | 182.4664 | 191.8627 | 201.5326 | 162.9284 | 167.9427 | 240.3835
572.5633 | 481.5633 | 331.5376 | 225.7075 | 182.7465 | 192.0132 | 201.7319 | 163.1177 | 168.111 | 240.485
573.5647 | 482.5647 | 331.4616 | 225.8336 | 183.0009 | 192.1761 | 201.912 | 163.3086 | 168.2679 | 240.5803
574.5662 | 483.5662 | 331.3739 | 225.9219 | 183.2766 | 192.3355 | 202.1043 | 163.503 | 168.4313 | 240.6641
575.5676 | 484.5676 | 331.2575 | 226.0956 | 183.5315 | 192.4887 | 202.3021 | 163.6917 | 168.6002 | 240.7525
576.5691 | 485.5691 | 331.2118 | 226.2863 | 183.7944 | 192.6465 | 202.508 | 163.8726 | 168.7597 | 240.8658
577.5605 | 486.5605 | 331.2 | 226.5691 | 184.0529 | 192.8052 | 202.6862 | 164.0639 | 168.9342 | 240.9469
578.5619 | 487.5619 | 331.2184 | 226.8307 | 184.3155 | 192.9713 | 202.8986 | 164.2494 | 169.1065 | 241.0733
579.5634 | 488.5634 | 331.3332 | 227.0441 | 184.5677 | 193.1265 | 203.1057 | 164.4356 | 169.2682 | 241.1812
580.5648 | 489.5648 | 331.55 | 227.2299 | 184.8303 | 193.2807 | 203.2889 | 164.6127 | 169.4378 | 241.2483
581.5663 | 490.5663 | 331.6997 | 227.4386 | 185.0774 | 193.4458 | 203.4893 | 164.8033 | 169.6051 | 241.3306
582.5677 | 491.5677 | 331.87 | 227.4937 | 185.3256 | 193.6126 | 203.6813 | 164.9804 | 169.764 | 241.4343
583.5691 | 492.5691 | 331.9782 | 227.7124 | 185.5899 | 193.7723 | 203.8336 | 165.158 | 169.9251 | 241.5021
584.5706 | 493.5706 | 331.9513 | 227.9674 | 185.8369 | 193.927 | 203.9435 | 165.3417 | 170.089 | 241.486
585.582 | 494.582 | 331.99 | 228.1587 | 186.0894 | 194.0835 | 204.0175 | 165.5209 | 170.2562 | 241.5266
586.5634 | 495.5634 | 332.1415 | 228.3911 | 186.3437 | 194.2236 | 204.0931 | 165.6942 | 170.4043 | 241.5892
587.5649 | 496.5649 | 332.2641 | 228.6132 | 186.5955 | 194.3746 | 204.1924 | 165.8799 | 170.5556 | 241.6553
588.5663 | 497.5663 | 332.2832 | 228.7902 | 186.8439 | 194.5029 | 204.2913 | 166.0603 | 170.712 | 241.7111
589.5678 | 498.5678 | 332.3379 | 229.0168 | 187.0826 | 194.631 | 204.4014 | 166.2286 | 170.8562 | 241.8015
590.5592 | 499.5592 | 332.4876 | 229.2658 | 187.3471 | 194.7627 | 204.4961 | 166.4034 | 171.0078 | 241.8927
591.5606 | 500.5606 | 332.5239 | 229.4704 | 187.5866 | 194.8832 | 204.6139 | 166.587 | 171.1582 | 241.945
592.5621 | 501.5621 | 332.5841 | 229.4139 | 187.8492 | 195.0082 | 204.7422 | 166.7635 | 171.3148 | 242.0087
593.5635 | 502.5635 | 332.6179 | 229.5555 | 188.0886 | 195.1244 | 204.8732 | 166.9333 | 171.4588 | 242.1112
594.5649 | 503.5649 | 332.627 | 229.7082 | 188.3466 | 195.2455 | 205.0008 | 167.1154 | 171.6218 | 242.2182
595.5664 | 504.5664 | 332.665 | 229.9307 | 188.5834 | 195.3634 | 205.1497 | 167.2883 | 171.7729 | 242.3386
596.5678 | 505.5678 | 332.6267 | 230.1088 | 188.8248 | 195.4768 | 205.2877 | 167.4687 | 171.9201 | 242.402
597.5592 | 506.5592 | 332.659 | 230.3393 | 189.0817 | 195.6068 | 205.4391 | 167.6419 | 172.0696 | 242.5008
598.5607 | 507.5607 | 332.7297 | 230.4708 | 189.3309 | 195.7166 | 205.613 | 167.8101 | 172.2176 | 242.6048
599.5621 | 508.5621 | 332.7319 | 230.5671 | 189.5616 | 195.8403 | 205.7953 | 167.9817 | 172.3765 | 242.7072
600.5636 | 509.5636 | 332.6703 | 230.7163 | 189.8107 | 195.9693 | 205.9833 | 168.1555 | 172.5268 | 242.7719
601.565 | 510.565 | 332.6561 | 230.8688 | 190.0633 | 196.09 | 206.1729 | 168.3258 | 172.6704 | 242.8874
602.5664 | 511.5664 | 332.5165 | 231.0889 | 190.2906 | 196.2143 | 206.3427 | 168.4964 | 172.8235 | 242.9641
603.5679 | 512.5679 | 332.4552 | 231.232 | 190.5406 | 196.3383 | 206.4943 | 168.65 | 172.9851 | 243.0661
604.5693 | 513.5693 | 332.5055 | 231.4244 | 190.7758 | 196.4622 | 206.638 | 168.8159 | 173.1408 | 243.1472
605.5608 | 514.5608 | 332.5051 | 231.5287 | 191.017 | 196.5898 | 206.8118 | 168.9708 | 173.2925 | 243.2482
606.5622 | 515.5622 | 332.4535 | 231.6365 | 191.2495 | 196.7213 | 207.0031 | 169.1262 | 173.4566 | 243.3307
607.5636 | 516.5636 | 332.495 | 231.7601 | 191.4871 | 196.8402 | 207.1682 | 169.2807 | 173.6096 | 243.4284
608.5651 | 517.5651 | 332.502 | 231.9094 | 191.7209 | 196.9623 | 207.345 | 169.4381 | 173.7671 | 243.4965
609.5665 | 518.5665 | 332.3812 | 232.1017 | 191.9513 | 197.0985 | 207.5116 | 169.5925 | 173.9274 | 243.5983
610.568 | 519.568 | 332.246 | 232.2718 | 192.1916 | 197.2235 | 207.6976 | 169.7501 | 174.0874 | 243.7011
611.5594 | 520.5594 | 332.1753 | 232.44 | 192.4236 | 197.3571 | 207.874 | 169.9059 | 174.247 | 243.7937
612.5608 | 521.5608 | 332.1864 | 232.575 | 192.6548 | 197.4835 | 208.0396 | 170.056 | 174.4105 | 243.873
613.5623 | 522.5623 | 332.2325 | 232.7366 | 192.8866 | 197.6195 | 208.2084 | 170.2138 | 174.576 | 243.9356
614.5637 | 523.5637 | 332.2758 | 232.9486 | 193.1094 | 197.7482 | 208.3663 | 170.3695 | 174.7412 | 244.0267
615.5651 | 524.5651 | 332.2614 | 233.1409 | 193.3457 | 197.8718 | 208.5349 | 170.5261 | 174.8977 | 244.1289
616.5666 | 525.5666 | 332.221 | 233.3065 | 193.5744 | 197.993 | 208.688 | 170.6855 | 175.054 | 244.2104
617.568 | 526.568 | 332.1272 | 233.3901 | 193.7944 | 198.1111 | 208.8705 | 170.8356 | 175.2057 | 244.3088
618.5594 | 527.5594 | 331.954 | 233.498 | 194.0291 | 198.2452 | 209.0367 | 170.9997 | 175.3634 | 244.4043
619.5609 | 528.5609 | 331.9039 | 233.6704 | 194.2642 | 198.3717 | 209.2114 | 171.1549 | 175.5078 | 244.5179
620.5623 | 529.5623 | 331.864 | 233.8429 | 194.4779 | 198.5022 | 209.3936 | 171.3027 | 175.6572 | 244.6061
621.5638 | 530.5638 | 331.9111 | 233.9279 | 194.7075 | 198.6344 | 209.5514 | 171.4522 | 175.8008 | 244.7097
622.5652 | 531.5652 | 331.8325 | 234.1112 | 194.9274 | 198.7673 | 209.7178 | 171.6023 | 175.9388 | 244.7775
623.5666 | 532.5666 | 331.914 | 234.1864 | 195.1544 | 198.9022 | 209.8688 | 171.7545 | 176.088 | 244.8655
624.5681 | 533.5681 | 331.9735 | 234.398 | 195.3793 | 199.0471 | 210.0138 | 171.8991 | 176.2357 | 244.9492
625.5695 | 534.5695 | 331.9582 | 234.5645 | 195.5951 | 199.1829 | 210.1764 | 172.0444 | 176.3797 | 245.0349
626.561 | 535.561 | 331.9426 | 234.6909 | 195.8069 | 199.3342 | 210.3359 | 172.1878 | 176.5332 | 245.1318
627.5624 | 536.5624 | 331.9691 | 234.7984 | 196.039 | 199.4672 | 210.4898 | 172.3367 | 176.6849 | 245.2187
628.5638 | 537.5638 | 331.9764 | 234.8306 | 196.2488 | 199.6171 | 210.6481 | 172.4765 | 176.8377 | 245.3064
629.5653 | 538.5653 | 331.9406 | 235.041 | 196.4899 | 199.7608 | 210.8255 | 172.6245 | 176.9922 | 245.4043
630.5667 | 539.5667 | 331.8437 | 235.1701 | 196.7044 | 199.917 | 210.9851 | 172.7737 | 177.1515 | 245.5041
631.5682 | 540.5682 | 331.9107 | 235.328 | 196.923 | 200.062 | 211.1545 | 172.9228 | 177.2976 | 245.5814
632.5596 | 541.5596 | 331.9062 | 235.4658 | 197.1382 | 200.207 | 211.3122 | 173.0723 | 177.4471 | 245.6838
633.561 | 542.561 | 331.9357 | 235.5919 | 197.3464 | 200.3522 | 211.4815 | 173.2181 | 177.5955 | 245.7674
634.5625 | 543.5625 | 331.9434 | 235.6664 | 197.5782 | 200.4988 | 211.6501 | 173.3645 | 177.7379 | 245.8765
635.5639 | 544.5639 | 332.0032 | 235.8702 | 197.7861 | 200.6537 | 211.8264 | 173.5056 | 177.8754 | 245.9972
636.5653 | 545.5653 | 331.9438 | 236.046 | 198.0059 | 200.8066 | 211.999 | 173.6454 | 178.017 | 246.0433
637.5668 | 546.5668 | 331.9865 | 236.1696 | 198.2204 | 200.9511 | 212.1595 | 173.7911 | 178.1597 | 246.1311
638.5582 | 547.5582 | 332.0663 | 236.2497 | 198.4343 | 201.1067 | 212.299 | 173.9279 | 178.2978 | 246.1956
639.5596 | 548.5596 | 332.0945 | 236.3077 | 198.6444 | 201.2564 | 212.4081 | 174.076 | 178.4437 | 246.2472
640.5611 | 549.5611 | 332.11 | 236.326 | 198.8664 | 201.4154 | 212.5155 | 174.2133 | 178.59 | 246.3242
641.5625 | 550.5625 | 332.2335 | 236.5637 | 199.0707 | 201.5636 | 212.5965 | 174.3556 | 178.7381 | 246.4266
642.564 | 551.564 | 332.3306 | 236.6877 | 199.2827 | 201.7052 | 212.693 | 174.5012 | 178.8848 | 246.5145
643.5654 | 552.5654 | 332.332 | 236.817 | 199.4872 | 201.8486 | 212.826 | 174.6359 | 179.0362 | 246.5996
644.5668 | 553.5668 | 332.3148 | 236.9172 | 199.6899 | 201.9925 | 212.9713 | 174.778 | 179.1762 | 246.7072
645.5683 | 554.5683 | 332.3155 | 237.1198 | 199.8967 | 202.1373 | 213.1259 | 174.9214 | 179.3199 | 246.7972
646.5697 | 555.5697 | 332.3833 | 237.2821 | 200.0809 | 202.2737 | 213.2812 | 175.0603 | 179.4608 | 246.9038
647.5611 | 556.5611 | 332.6217 | 237.5069 | 200.3006 | 202.4114 | 213.4292 | 175.2047 | 179.6124 | 246.9722
648.5626 | 557.5626 | 332.7595 | 237.5721 | 200.491 | 202.5529 | 213.571 | 175.3388 | 179.7521 | 247.0749
649.564 | 558.564 | 332.7999 | 237.6261 | 200.6838 | 202.694 | 213.7331 | 175.4782 | 179.8963 | 247.1635
650.5655 | 559.5655 | 332.7698 | 237.7328 | 200.8947 | 202.8312 | 213.8852 | 175.61 | 180.0387 | 247.2718
651.5669 | 560.5669 | 332.7386 | 237.8692 | 201.0989 | 202.9801 | 214.0486 | 175.748 | 180.187 | 247.3485
652.5683 | 561.5683 | 332.8288 | 238.0226 | 201.2935 | 203.1188 | 214.2071 | 175.8827 | 180.3335 | 247.4409
653.5598 | 562.5598 | 332.8379 | 238.1199 | 201.4981 | 203.2618 | 214.3614 | 176.019 | 180.4784 | 247.529
654.5612 | 563.5612 | 332.8475 | 238.3 | 201.6934 | 203.4051 | 214.5085 | 176.1629 | 180.6216 | 247.6241
655.5627 | 564.5627 | 332.8611 | 238.2693 | 201.8954 | 203.5496 | 214.6798 | 176.2887 | 180.7582 | 247.7223
656.5641 | 565.5641 | 332.8304 | 238.298 | 202.0942 | 203.696 | 214.8406 | 176.422 | 180.9014 | 247.803
657.5655 | 566.5655 | 332.7918 | 238.5155 | 202.3002 | 203.8433 | 214.9953 | 176.5575 | 181.0472 | 247.9037
658.567 | 567.567 | 332.7045 | 238.6022 | 202.4992 | 203.9926 | 215.1545 | 176.6765 | 181.1868 | 247.983
659.5584 | 568.5584 | 332.7308 | 238.6678 | 202.705 | 204.1364 | 215.3026 | 176.8023 | 181.3384 | 248.061
660.5598 | 569.5598 | 332.6744 | 238.8077 | 202.9066 | 204.2887 | 215.4549 | 176.923 | 181.4883 | 248.1391
661.5613 | 570.5613 | 332.6665 | 239.0411 | 203.1173 | 204.4418 | 215.5983 | 177.0486 | 181.6383 | 248.223
662.5627 | 571.5627 | 332.6317 | 239.0661 | 203.3218 | 204.5876 | 215.7401 | 177.1652 | 181.7822 | 248.3105
663.5642 | 572.5642 | 332.6256 | 239.2944 | 203.5177 | 204.744 | 215.8974 | 177.2889 | 181.9259 | 248.3809
664.5656 | 573.5656 | 332.7484 | 239.4939 | 203.7269 | 204.8921 | 216.0382 | 177.4105 | 182.0712 | 248.4765
665.567 | 574.567 | 332.7808 | 239.6283 | 203.9433 | 205.0531 | 216.1988 | 177.523 | 182.2165 | 248.5534
666.5585 | 575.5585 | 332.7596 | 239.6736 | 204.143 | 205.2078 | 216.3567 | 177.6376 | 182.3614 | 248.645
667.5699 | 576.5699 | 332.7888 | 239.7625 | 204.3586 | 205.36 | 216.5035 | 177.7484 | 182.5002 | 248.7122
668.5613 | 577.5613 | 332.8378 | 239.6249 | 204.5628 | 205.516 | 216.6507 | 177.8555 | 182.6412 | 248.7922
669.5628 | 578.5628 | 332.8035 | 239.8089 | 204.7694 | 205.6844 | 216.8158 | 177.9653 | 182.7873 | 248.867
670.5642 | 579.5642 | 332.6765 | 240.0601 | 204.9914 | 205.8392 | 216.9541 | 178.0819 | 182.924 | 248.9612
671.5657 | 580.5657 | 332.5799 | 240.1805 | 205.2009 | 205.986 | 217.0946 | 178.19 | 183.0594 | 249.0348
672.5671 | 581.5671 | 332.567 | 240.3463 | 205.4244 | 206.144 | 217.2464 | 178.3105 | 183.189 | 249.1033
673.5685 | 582.5685 | 332.5805 | 240.5171 | 205.6181 | 206.2957 | 217.3858 | 178.4156 | 183.3372 | 249.2018
674.57 | 583.57 | 332.55 | 240.6859 | 205.8385 | 206.4522 | 217.5297 | 178.5298 | 183.4718 | 249.2508
675.5614 | 584.5614 | 332.602 | 240.8645 | 206.0416 | 206.5977 | 217.6766 | 178.6467 | 183.6148 | 249.3296
676.5628 | 585.5628 | 332.6477 | 241.0168 | 206.2722 | 206.7487 | 217.8309 | 178.7561 | 183.7577 | 249.3968
677.5643 | 586.5643 | 332.6748 | 241.1082 | 206.4785 | 206.9042 | 217.98 | 178.8724 | 183.9005 | 249.4583
678.5657 | 587.5657 | 332.5899 | 241.0313 | 206.6908 | 207.0606 | 218.105 | 178.9806 | 184.0476 | 249.5057
679.5672 | 588.5672 | 332.5242 | 241.1506 | 206.8985 | 207.2049 | 218.208 | 179.0853 | 184.1946 | 249.5698
680.5686 | 589.5686 | 332.5112 | 241.387 | 207.116 | 207.3611 | 218.3115 | 179.1987 | 184.3402 | 249.6486
681.56 | 590.56 | 332.5338 | 241.5496 | 207.3144 | 207.5045 | 218.4443 | 179.3094 | 184.4909 | 249.7143
682.5615 | 591.5615 | 332.4818 | 241.7641 | 207.5233 | 207.6484 | 218.5661 | 179.4259 | 184.6365 | 249.7816
683.5629 | 592.5629 | 332.3418 | 241.965 | 207.7369 | 207.7934 | 218.7099 | 179.5316 | 184.7897 | 249.8381
684.5644 | 593.5644 | 332.2655 | 242.0688 | 207.9334 | 207.9384 | 218.8595 | 179.6442 | 184.9279 | 249.9061
685.5658 | 594.5658 | 332.2733 | 242.1187 | 208.1496 | 208.0825 | 219.0081 | 179.7679 | 185.0809 | 249.9699
686.5672 | 595.5672 | 332.4139 | 242.2262 | 208.3569 | 208.2305 | 219.1568 | 179.8749 | 185.2167 | 250.0319
687.5587 | 596.5587 | 332.4225 | 242.3544 | 208.5588 | 208.3744 | 219.313 | 179.9938 | 185.3573 | 250.0983
688.5701 | 597.5701 | 332.4145 | 242.2031 | 208.7697 | 208.5177 | 219.4665 | 180.1087 | 185.5004 | 250.1695
689.5615 | 598.5615 | 332.4827 | 242.3632 | 208.9718 | 208.6714 | 219.6169 | 180.2168 | 185.6481 | 250.2278
690.563 | 599.563 | 332.5514 | 242.4186 | 209.1804 | 208.8162 | 219.7783 | 180.3326 | 185.7869 | 250.2891
691.5644 | 600.5644 | 332.5979 | 242.7238 | 209.376 | 208.9646 | 219.9383 | 180.4386 | 185.9206 | 250.3579
692.5659 | 601.5659 | 332.5409 | 242.8673 | 209.5833 | 209.1146 | 220.088 | 180.5546 | 186.0471 | 250.4235
693.5673 | 602.5673 | 332.5401 | 243.0244 | 209.7847 | 209.2743 | 220.2344 | 180.6682 | 186.1743 | 250.4678
694.5687 | 603.5687 | 332.6498 | 243.1844 | 209.9827 | 209.4341 | 220.3806 | 180.7799 | 186.302 | 250.5402
695.5602 | 604.5602 | 332.7696 | 243.1357 | 210.1769 | 209.5912 | 220.5277 | 180.8897 | 186.4174 | 250.5728
696.5616 | 605.5616 | 332.8061 | 243.4056 | 210.3867 | 209.7432 | 220.6697 | 181.0022 | 186.5432 | 250.643
697.563 | 606.563 | 332.7918 | 243.4985 | 210.5876 | 209.9064 | 220.7942 | 181.1036 | 186.6535 | 250.7154
698.5645 | 607.5645 | 332.7288 | 243.6501 | 210.7948 | 210.0665 | 220.9165 | 181.1985 | 186.7654 | 250.7517
699.5659 | 608.5659 | 332.5822 | 243.7867 | 211.0023 | 210.2263 | 221.0536 | 181.3126 | 186.874 | 250.8307
700.5674 | 609.5674 | 332.5522 | 244.0589 | 211.1992 | 210.3887 | 221.192 | 181.4211 | 186.9856 | 250.8814
701.5588 | 610.5588 | 332.7051 | 244.2957 | 211.4124 | 210.5477 | 221.3384 | 181.527 | 187.0899 | 250.9443
702.5602 | 611.5602 | 332.758 | 244.4512 | 211.6005 | 210.7006 | 221.4968 | 181.6415 | 187.2087 | 251.0192
703.5617 | 612.5617 | 332.6585 | 244.4731 | 211.7954 | 210.8643 | 221.6447 | 181.7484 | 187.3249 | 251.0799
704.5631 | 613.5631 | 332.6017 | 244.5921 | 211.9824 | 211.0255 | 221.8115 | 181.8587 | 187.4431 | 251.1336
705.5646 | 614.5646 | 332.5615 | 244.6867 | 212.2066 | 211.1755 | 221.9693 | 181.9801 | 187.5605 | 251.1975
706.566 | 615.566 | 332.5482 | 244.8211 | 212.4033 | 211.3313 | 222.1295 | 182.0936 | 187.6795 | 251.274
707.5674 | 616.5674 | 332.5404 | 244.6132 | 212.6019 | 211.4869 | 222.2858 | 182.2117 | 187.8095 | 251.3443
708.5589 | 617.5589 | 332.54 | 244.8532 | 212.794 | 211.6424 | 222.4631 | 182.3282 | 187.9346 | 251.4035
709.5603 | 618.5603 | 332.5429 | 245.0379 | 212.9898 | 211.8018 | 222.6188 | 182.4372 | 188.0649 | 251.4685
710.5617 | 619.5617 | 332.5329 | 245.1418 | 213.1824 | 211.9536 | 222.8023 | 182.5563 | 188.1947 | 251.5331
711.5632 | 620.5632 | 332.5676 | 245.4128 | 213.3749 | 212.1031 | 222.9643 | 182.6769 | 188.3177 | 251.6028
712.5646 | 621.5646 | 332.6083 | 245.3848 | 213.5576 | 212.2681 | 223.1396 | 182.7935 | 188.4367 | 251.6451
713.5661 | 622.5661 | 332.5762 | 245.5048 | 213.7502 | 212.4193 | 223.297 | 182.9011 | 188.5632 | 251.7292
714.5675 | 623.5675 | 332.6392 | 245.7324 | 213.9401 | 212.5653 | 223.4715 | 183.0087 | 188.6834 | 251.7865
715.5689 | 624.5689 | 332.7054 | 245.8339 | 214.132 | 212.7235 | 223.6375 | 183.1245 | 188.7982 | 251.8591
716.5604 | 625.5604 | 332.7054 | 245.8025 | 214.3277 | 212.8767 | 223.8022 | 183.2293 | 188.9169 | 251.8957
717.5618 | 626.5618 | 332.6335 | 245.9108 | 214.5232 | 213.0333 | 223.9644 | 183.3492 | 189.0265 | 251.9755
718.5632 | 627.5632 | 332.6323 | 246.0916 | 214.719 | 213.1977 | 224.1171 | 183.4727 | 189.1498 | 252.025
719.5647 | 628.5647 | 332.6495 | 246.1016 | 214.905 | 213.3367 | 224.2559 | 183.5881 | 189.2547 | 252.0856
720.5661 | 629.5661 | 332.6304 | 246.1566 | 215.1033 | 213.5049 | 224.3978 | 183.7092 | 189.3667 | 252.1364
721.5676 | 630.5676 | 332.6794 | 246.2874 | 215.2955 | 213.6649 | 224.5321 | 183.8322 | 189.4771 | 252.2062
722.559 | 631.559 | 332.7917 | 246.0462 | 215.4795 | 213.8242 | 224.6703 | 183.9648 | 189.5819 | 252.2381
723.5604 | 632.5604 | 332.8673 | 246.2764 | 215.677 | 213.9814 | 224.8217 | 184.0927 | 189.6882 | 252.2795
724.5619 | 633.5619 | 332.8995 | 246.5327 | 215.8733 | 214.1355 | 224.9508 | 184.2302 | 189.7918 | 252.3229
725.5633 | 634.5633 | 332.9934 | 246.7564 | 216.0617 | 214.2966 | 225.1073 | 184.3614 | 189.8962 | 252.3898
726.5647 | 635.5647 | 333.1808 | 246.9982 | 216.2506 | 214.4546 | 225.2422 | 184.5 | 189.9864 | 252.4467
727.5662 | 636.5662 | 333.3825 | 247.0658 | 216.4375 | 214.5999 | 225.3777 | 184.6312 | 190.0794 | 252.511
728.5676 | 637.5676 | 333.3989 | 247.116 | 216.6145 | 214.7536 | 225.5283 | 184.772 | 190.1792 | 252.5503
729.5591 | 638.5591 | 333.3013 | 247.1666 | 216.7987 | 214.9208 | 225.6709 | 184.9098 | 190.2777 | 252.6131
730.5605 | 639.5605 | 333.3019 | 247.1747 | 217.0043 | 215.0792 | 225.8205 | 185.0503 | 190.38 | 252.6828
731.5619 | 640.5619 | 333.2636 | 247.4904 | 217.1905 | 215.2292 | 225.9627 | 185.1843 | 190.4838 | 252.7409
732.5634 | 641.5634 | 333.2656 | 247.4172 | 217.3754 | 215.387 | 226.111 | 185.3188 | 190.5807 | 252.7868
733.5648 | 642.5648 | 333.2048 | 247.5598 | 217.5766 | 215.5466 | 226.2569 | 185.4556 | 190.6865 | 252.8442
734.5663 | 643.5663 | 333.0651 | 247.361 | 217.7657 | 215.6987 | 226.4043 | 185.5941 | 190.7945 | 252.8893
735.5677 | 644.5677 | 333.0243 | 247.6495 | 217.9616 | 215.8448 | 226.5354 | 185.727 | 190.8999 | 252.9407
736.5691 | 645.5691 | 333.0125 | 247.84 | 218.1518 | 216.0146 | 226.6868 | 185.8734 | 191.0189 | 252.9938
737.5706 | 646.5706 | 332.9976 | 248.0344 | 218.347 | 216.1556 | 226.8476 | 185.9972 | 191.1242 | 253.0475
738.562 | 647.562 | 332.9695 | 248.0609 | 218.5357 | 216.3143 | 226.9993 | 186.135 | 191.2411 | 253.1013
739.5634 | 648.5634 | 333.1066 | 248.0035 | 218.7296 | 216.4655 | 227.1507 | 186.2698 | 191.3565 | 253.143
740.5649 | 649.5649 | 333.0632 | 247.8133 | 218.9188 | 216.6097 | 227.3192 | 186.4044 | 191.4765 | 253.2086
741.5663 | 650.5663 | 333.0103 | 248.1182 | 219.1232 | 216.7615 | 227.4929 | 186.5368 | 191.5989 | 253.2627
742.5678 | 651.5678 | 333.0069 | 248.2341 | 219.3146 | 216.9171 | 227.6621 | 186.6679 | 191.7068 | 253.3313
743.5592 | 652.5592 | 333.0167 | 248.4269 | 219.5079 | 217.0687 | 227.8245 | 186.7987 | 191.8195 | 253.387
744.5606 | 653.5606 | 333.0185 | 248.4611 | 219.7054 | 217.2165 | 227.9937 | 186.9269 | 191.9409 | 253.4189
745.5621 | 654.5621 | 332.9476 | 248.6296 | 219.9112 | 217.3709 | 228.1518 | 187.0599 | 192.0495 | 253.499
746.5635 | 655.5635 | 332.8947 | 248.9751 | 220.1184 | 217.5232 | 228.3125 | 187.1862 | 192.1627 | 253.5402
747.5649 | 656.5649 | 332.9186 | 248.9936 | 220.3272 | 217.6747 | 228.4709 | 187.314 | 192.2664 | 253.5926
748.5664 | 657.5664 | 332.9905 | 249.1078 | 220.5292 | 217.8255 | 228.6351 | 187.4437 | 192.3867 | 253.6621
749.5678 | 658.5678 | 332.9653 | 249.3836 | 220.7248 | 217.9838 | 228.7959 | 187.5762 | 192.5016 | 253.7182
750.5593 | 659.5593 | 332.9833 | 249.5698 | 220.9146 | 218.1312 | 228.9579 | 187.7051 | 192.6182 | 253.7535
751.5607 | 660.5607 | 332.8907 | 249.7745 | 221.1072 | 218.2893 | 229.1179 | 187.8386 | 192.7246 | 253.8233
752.5621 | 661.5621 | 332.9168 | 249.9236 | 221.2893 | 218.4419 | 229.2801 | 187.9653 | 192.8307 | 253.886
753.5636 | 662.5636 | 333.0191 | 249.8665 | 221.4937 | 218.5969 | 229.4212 | 188.0951 | 192.9356 | 253.9393
754.565 | 663.565 | 333.1047 | 249.8819 | 221.6687 | 218.7457 | 229.5557 | 188.2193 | 193.0489 | 253.9833
755.5665 | 664.5665 | 333.1926 | 250.0923 | 221.8549 | 218.8948 | 229.6761 | 188.3437 | 193.1594 | 254.0467
756.5679 | 665.5679 | 333.1879 | 250.1981 | 222.0422 | 219.0545 | 229.7845 | 188.4741 | 193.2757 | 254.1161
757.5693 | 666.5693 | 333.3319 | 250.443 | 222.2297 | 219.2036 | 229.9137 | 188.5892 | 193.3862 | 254.1534
758.5608 | 667.5608 | 333.4186 | 250.5919 | 222.3997 | 219.3451 | 230.0335 | 188.7164 | 193.5038 | 254.2139
759.5622 | 668.5622 | 333.5192 | 250.6352 | 222.5732 | 219.493 | 230.159 | 188.8388 | 193.6276 | 254.2696
760.5636 | 669.5636 | 333.4493 | 250.6746 | 222.752 | 219.6432 | 230.2907 | 188.96 | 193.7495 | 254.3449
761.5651 | 670.5651 | 333.4153 | 250.7926 | 222.9249 | 219.7895 | 230.4376 | 189.0887 | 193.8703 | 254.3962
762.5665 | 671.5665 | 333.3503 | 250.8361 | 223.0951 | 219.9363 | 230.5815 | 189.2147 | 193.9798 | 254.4352
763.568 | 672.568 | 333.3236 | 250.9411 | 223.2715 | 220.0806 | 230.715 | 189.3345 | 194.0943 | 254.4734
764.5594 | 673.5594 | 333.3025 | 251.0344 | 223.4327 | 220.228 | 230.8616 | 189.4535 | 194.2138 | 254.5419
765.5608 | 674.5608 | 333.3545 | 250.9955 | 223.6001 | 220.3585 | 230.9776 | 189.5784 | 194.3319 | 254.5777
766.5723 | 675.5723 | 333.3258 | 251.3062 | 223.7635 | 220.5093 | 231.111 | 189.6992 | 194.4583 | 254.6199
767.5937 | 676.5937 | 333.2323 | 251.4168 | 223.9351 | 220.6471 | 231.2382 | 189.8212 | 194.5756 | 254.6831
768.5651 | 677.5651 | 333.2872 | 251.3908 | 224.0938 | 220.7832 | 231.3621 | 189.9389 | 194.6921 | 254.7316
769.5666 | 678.5666 | 333.3309 | 251.0606 | 224.2557 | 220.913 | 231.4945 | 190.0606 | 194.8157 | 254.7618
770.568 | 679.568 | 333.3714 | 251.4261 | 224.4158 | 221.0586 | 231.6307 | 190.1804 | 194.9397 | 254.7919
771.5594 | 680.5594 | 333.3987 | 251.5779 | 224.5758 | 221.1908 | 231.7534 | 190.2979 | 195.0586 | 254.8453
772.5609 | 681.5609 | 333.3345 | 251.6363 | 224.7363 | 221.3245 | 231.8672 | 190.417 | 195.1792 | 254.899
773.5623 | 682.5623 | 333.2313 | 251.656 | 224.8864 | 221.4514 | 231.9733 | 190.5355 | 195.3018 | 254.9573
774.5638 | 683.5638 | 333.1614 | 251.9073 | 225.0284 | 221.5953 | 232.0793 | 190.6501 | 195.4274 | 255.0075
775.5652 | 684.5652 | 333.1088 | 251.7929 | 225.1914 | 221.7207 | 232.2127 | 190.7734 | 195.539 | 255.0661
776.5666 | 685.5666 | 333.0232 | 251.9666 | 225.3469 | 221.8577 | 232.3266 | 190.8924 | 195.6577 | 255.1191
777.5681 | 686.5681 | 332.94 | 251.7525 | 225.4898 | 221.9806 | 232.4703 | 191.0218 | 195.772 | 255.1757
778.5695 | 687.5695 | 332.8473 | 251.9337 | 225.6278 | 222.1131 | 232.6025 | 191.1465 | 195.8909 | 255.2222
779.561 | 688.561 | 332.8405 | 252.0401 | 225.7799 | 222.2366 | 232.709 | 191.2679 | 196.0025 | 255.2327
780.5624 | 689.5624 | 332.8557 | 252.2816 | 225.924 | 222.361 | 232.8095 | 191.3971 | 196.1122 | 255.2618
781.5638 | 690.5638 | 332.8765 | 252.3101 | 226.066 | 222.4854 | 232.902 | 191.524 | 196.2259 | 255.2919
782.5653 | 691.5653 | 332.9279 | 252.3657 | 226.2066 | 222.6098 | 233.0125 | 191.6421 | 196.3355 | 255.3264
783.5667 | 692.5667 | 332.7988 | 252.4168 | 226.345 | 222.7279 | 233.1211 | 191.7762 | 196.4434 | 255.362
784.5682 | 693.5682 | 332.7219 | 252.4673 | 226.4822 | 222.8589 | 233.2299 | 191.9028 | 196.5575 | 255.4196
785.5596 | 694.5596 | 332.6447 | 252.527 | 226.6105 | 222.9718 | 233.3574 | 192.03 | 196.6569 | 255.4446
786.561 | 695.561 | 332.7243 | 252.6199 | 226.7459 | 223.0962 | 233.478 | 192.1609 | 196.7575 | 255.5213
787.5625 | 696.5625 | 332.714 | 252.7008 | 226.872 | 223.2207 | 233.5966 | 192.295 | 196.8652 | 255.5576
788.5639 | 697.5639 | 332.6347 | 252.8716 | 227.0141 | 223.3462 | 233.7253 | 192.4333 | 196.9661 | 255.5668
789.5653 | 698.5653 | 332.6058 | 253.0455 | 227.1486 | 223.4691 | 233.8552 | 192.566 | 197.0676 | 255.6249
790.5668 | 699.5668 | 332.6278 | 253.3078 | 227.2802 | 223.5937 | 233.9884 | 192.7037 | 197.1741 | 255.6526
791.5582 | 700.5582 | 332.6474 | 253.5671 | 227.4053 | 223.7142 | 234.1119 | 192.8333 | 197.2622 | 255.6861
792.5596 | 701.5596 | 332.5844 | 253.5539 | 227.5463 | 223.8426 | 234.2209 | 192.9671 | 197.3604 | 255.6872
793.5611 | 702.5611 | 332.6016 | 253.6863 | 227.676 | 223.962 | 234.2954 | 193.0985 | 197.4412 | 255.7092
794.5625 | 703.5625 | 332.6683 | 253.9739 | 227.8079 | 224.0941 | 234.3608 | 193.2317 | 197.535 | 255.7396
795.564 | 704.564 | 332.7332 | 253.937 | 227.9477 | 224.212 | 234.4195 | 193.365 | 197.6257 | 255.753
796.5654 | 705.5654 | 332.7702 | 254.1227 | 228.0887 | 224.336 | 234.4974 | 193.4981 | 197.7068 | 255.7654
797.5668 | 706.5668 | 332.7682 | 254.0452 | 228.2197 | 224.4552 | 234.5631 | 193.6265 | 197.7973 | 255.7891
798.5683 | 707.5683 | 332.6192 | 254.0995 | 228.3358 | 224.5671 | 234.6319 | 193.753 | 197.8826 | 255.811
799.5697 | 708.5697 | 332.5248 | 254.2334 | 228.4812 | 224.6808 | 234.711 | 193.8864 | 197.9733 | 255.8354
800.5612 | 709.5612 | 332.47 | 254.399 | 228.609 | 224.7972 | 234.8064 | 194.0172 | 198.0604 | 255.8588
801.5626 | 710.5626 | 332.4084 | 254.5194 | 228.7373 | 224.9143 | 234.8969 | 194.1494 | 198.1484 | 255.8902
802.564 | 711.564 | 332.3195 | 254.7296 | 228.8687 | 225.0213 | 234.98 | 194.2716 | 198.2396 | 255.8858
803.5655 | 712.5655 | 332.2569 | 254.8666 | 229.0057 | 225.1237 | 235.044 | 194.4119 | 198.3195 | 255.8648
804.5669 | 713.5669 | 331.9241 | 254.8424 | 229.1377 | 225.239 | 235.1169 | 194.5355 | 198.4082 | 255.8893
805.5684 | 714.5684 | 331.7275 | 254.897 | 229.258 | 225.3533 | 235.1887 | 194.6639 | 198.4987 | 255.9015
806.5598 | 715.5598 | 331.6013 | 254.9533 | 229.3949 | 225.4596 | 235.2773 | 194.7912 | 198.5863 | 255.9197
807.5612 | 716.5612 | 331.4685 | 254.8694 | 229.5124 | 225.5718 | 235.3716 | 194.9197 | 198.6668 | 255.9495
808.5627 | 717.5627 | 331.2745 | 254.9767 | 229.6432 | 225.6758 | 235.4729 | 195.0503 | 198.7525 | 255.9968
809.5641 | 718.5641 | 331.0652 | 254.9877 | 229.7644 | 225.7857 | 235.5925 | 195.1696 | 198.8367 | 256.0134
810.5655 | 719.5655 | 330.9331 | 255.0216 | 229.9022 | 225.889 | 235.7133 | 195.2924 | 198.918 | 256.0321
811.567 | 720.567 | 330.8104 | 255.1543 | 230.0241 | 226.0021 | 235.8512 | 195.4192 | 199.0046 | 256.0481
812.5684 | 721.5684 | 330.6364 | 255.1616 | 230.1531 | 226.116 | 235.9845 | 195.5462 | 199.0891 | 256.0746
813.5598 | 722.5598 | 330.5945 | 255.1495 | 230.2704 | 226.2208 | 236.1369 | 195.6533 | 199.1771 | 256.1057
814.5613 | 723.5613 | 330.6597 | 255.2121 | 230.3938 | 226.3389 | 236.2883 | 195.784 | 199.2624 | 256.1327
815.5627 | 724.5627 | 330.6915 | 255.3553 | 230.5186 | 226.4522 | 236.4196 | 195.8963 | 199.3463 | 256.1612
816.5642 | 725.5642 | 330.8111 | 255.4351 | 230.6466 | 226.5622 | 236.5758 | 196.0156 | 199.4484 | 256.1984
817.5656 | 726.5656 | 330.8847 | 255.5397 | 230.7646 | 226.6792 | 236.7176 | 196.1414 | 199.5345 | 256.2118
818.567 | 727.567 | 330.9245 | 255.6054 | 230.8889 | 226.7969 | 236.86 | 196.2639 | 199.6239 | 256.2464
819.5685 | 728.5685 | 330.9893 | 255.5696 | 231.0059 | 226.9126 | 237.008 | 196.3786 | 199.7233 | 256.273
820.5699 | 729.5699 | 331.036 | 255.6396 | 231.1372 | 227.0202 | 237.1496 | 196.4846 | 199.8226 | 256.3278
821.5613 | 730.5613 | 331.1843 | 255.7694 | 231.262 | 227.1475 | 237.2878 | 196.5979 | 199.9189 | 256.3602
822.5628 | 731.5628 | 331.2978 | 255.9396 | 231.3808 | 227.2639 | 237.4133 | 196.7005 | 200.0155 | 256.4014
823.5642 | 732.5642 | 331.4074 | 256.1153 | 231.4901 | 227.3885 | 237.548 | 196.8137 | 200.1208 | 256.4348
824.5657 | 733.5657 | 331.5137 | 256.1167 | 231.6267 | 227.5071 | 237.68 | 196.9181 | 200.2294 | 256.4593
825.5671 | 734.5671 | 331.7711 | 256.3208 | 231.7386 | 227.6308 | 237.827 | 197.0216 | 200.3342 | 256.5115
826.5685 | 735.5685 | 332.0442 | 256.5914 | 231.8873 | 227.7465 | 237.9604 | 197.1329 | 200.4372 | 256.5384
827.56 | 736.56 | 332.2717 | 256.7259 | 232.0124 | 227.8659 | 238.1109 | 197.2468 | 200.5515 | 256.5808
828.5614 | 737.5614 | 332.3764 | 256.9195 | 232.1305 | 227.9901 | 238.2454 | 197.343 | 200.6673 | 256.6162
829.5629 | 738.5629 | 332.4142 | 257.045 | 232.2493 | 228.1172 | 238.3934 | 197.4521 | 200.7855 | 256.6696
830.5643 | 739.5643 | 332.5305 | 257.2097 | 232.3777 | 228.2349 | 238.5396 | 197.5654 | 200.8977 | 256.6841
831.5657 | 740.5657 | 332.4962 | 257.204 | 232.487 | 228.3595 | 238.6757 | 197.6781 | 201.0063 | 256.7502
832.5672 | 741.5672 | 332.5762 | 257.2949 | 232.6165 | 228.4825 | 238.8111 | 197.7868 | 201.1261 | 256.7952
833.5586 | 742.5586 | 332.6169 | 257.3206 | 232.7186 | 228.6085 | 238.9556 | 197.8916 | 201.2389 | 256.8381
834.56 | 743.56 | 332.7502 | 257.5392 | 232.8391 | 228.7278 | 239.0954 | 198.0051 | 201.3581 | 256.8311
835.5615 | 744.5615 | 332.839 | 257.7754 | 232.9644 | 228.849 | 239.2403 | 198.1161 | 201.469 | 256.8657
836.5629 | 745.5629 | 332.8131 | 257.9172 | 233.0855 | 228.9701 | 239.3675 | 198.2219 | 201.5844 | 256.9019
837.5644 | 746.5644 | 332.8428 | 258.0479 | 233.2041 | 229.1016 | 239.4933 | 198.3405 | 201.6962 | 256.9641
838.5658 | 747.5658 | 332.9326 | 258.2414 | 233.3367 | 229.2221 | 239.6264 | 198.4645 | 201.8107 | 256.9922
839.5672 | 748.5672 | 332.9336 | 258.3493 | 233.4552 | 229.3451 | 239.7376 | 198.5856 | 201.9245 | 257.0485
840.5687 | 749.5687 | 332.9751 | 258.6233 | 233.5713 | 229.4725 | 239.8611 | 198.6978 | 202.0367 | 257.0869
841.5701 | 750.5701 | 333.0164 | 258.8088 | 233.6936 | 229.5926 | 239.9965 | 198.8237 | 202.1546 | 257.1219
842.5615 | 751.5615 | 333.0008 | 258.9097 | 233.8025 | 229.7197 | 240.1136 | 198.936 | 202.2655 | 257.1647
843.563 | 752.563 | 332.9621 | 259.0106 | 233.9262 | 229.8438 | 240.2209 | 199.0628 | 202.3865 | 257.1965
844.5644 | 753.5644 | 332.9878 | 259.2397 | 234.0348 | 229.9653 | 240.339 | 199.1801 | 202.5072 | 257.245
845.5659 | 754.5659 | 333.0429 | 259.4238 | 234.1683 | 230.0981 | 240.463 | 199.3106 | 202.6146 | 257.2911
846.5673 | 755.5673 | 333.0681 | 259.5675 | 234.2829 | 230.222 | 240.5732 | 199.4215 | 202.7176 | 257.3153
847.5687 | 756.5687 | 333.0263 | 259.6034 | 234.3926 | 230.3416 | 240.6914 | 199.548 | 202.819 | 257.3795
848.5602 | 757.5602 | 333.0784 | 259.6976 | 234.5064 | 230.4665 | 240.7865 | 199.6611 | 202.9285 | 257.3998
849.5616 | 758.5616 | 333.0729 | 259.8104 | 234.6245 | 230.5831 | 240.9012 | 199.787 | 203.0336 | 257.4372
850.563 | 759.563 | 333.0672 | 259.9264 | 234.7316 | 230.711 | 241.0325 | 199.904 | 203.1296 | 257.4467
851.5645 | 760.5645 | 333.0393 | 260.1261 | 234.8559 | 230.8333 | 241.151 | 200.0293 | 203.2321 | 257.4978
852.5659 | 761.5659 | 333.0237 | 260.2609 | 234.9817 | 230.9603 | 241.2822 | 200.15 | 203.3413 | 257.5214
853.5674 | 762.5674 | 333.0734 | 260.4184 | 235.0982 | 231.0808 | 241.3978 | 200.2705 | 203.447 | 257.5587
854.5588 | 763.5588 | 333.0994 | 260.466 | 235.2153 | 231.2016 | 241.5297 | 200.3792 | 203.554 | 257.5858
855.5602 | 764.5602 | 333.0792 | 260.6037 | 235.3244 | 231.329 | 241.6396 | 200.4898 | 203.6607 | 257.6159
856.5617 | 765.5617 | 333.0709 | 260.6758 | 235.4527 | 231.45 | 241.7539 | 200.6042 | 203.762 | 257.6575
857.5631 | 766.5631 | 333.1109 | 260.8538 | 235.5709 | 231.5712 | 241.8743 | 200.7085 | 203.8674 | 257.7067
858.5646 | 767.5646 | 333.1513 | 261.0764 | 235.6861 | 231.6828 | 241.9977 | 200.8099 | 203.9692 | 257.7215
859.566 | 768.566 | 333.0304 | 261.2111 | 235.8002 | 231.8013 | 242.111 | 200.9201 | 204.0658 | 257.7718
860.5674 | 769.5674 | 332.947 | 261.31 | 235.9242 | 231.922 | 242.2264 | 201.0204 | 204.1748 | 257.8032
861.5689 | 770.5689 | 333.0259 | 261.4947 | 236.039 | 232.049 | 242.3313 | 201.1216 | 204.2696 | 257.859
862.5703 | 771.5703 | 333.0771 | 261.6466 | 236.1595 | 232.1617 | 242.443 | 201.2367 | 204.3741 | 257.9082
863.5617 | 772.5617 | 333.033 | 261.7775 | 236.2776 | 232.279 | 242.5691 | 201.3364 | 204.4766 | 257.9417
864.5632 | 773.5632 | 333.0081 | 261.9231 | 236.4006 | 232.3926 | 242.6982 | 201.4476 | 204.5837 | 257.9827
865.5646 | 774.5646 | 333.0096 | 262.1284 | 236.5076 | 232.5223 | 242.8199 | 201.5492 | 204.6886 | 258.0094
866.5661 | 775.5661 | 333.0048 | 262.2285 | 236.6286 | 232.6369 | 242.9441 | 201.6527 | 204.7865 | 258.0506
867.5675 | 776.5675 | 333.0825 | 262.3893 | 236.7501 | 232.7513 | 243.0864 | 201.7638 | 204.8964 | 258.106
868.5689 | 777.5689 | 333.0883 | 262.491 | 236.8705 | 232.8735 | 243.1984 | 201.8699 | 205.001 | 258.12
869.5604 | 778.5604 | 333.096 | 262.6322 | 236.9878 | 232.9861 | 243.3298 | 201.9739 | 205.0964 | 258.1668
870.5618 | 779.5618 | 333.183 | 262.7217 | 237.0959 | 233.1041 | 243.4418 | 202.0794 | 205.2051 | 258.2041
871.5632 | 780.5632 | 333.3435 | 262.835 | 237.207 | 233.2217 | 243.5479 | 202.1914 | 205.3042 | 258.2071
872.5647 | 781.5647 | 333.4819 | 262.8614 | 237.3344 | 233.3393 | 243.669 | 202.307 | 205.4052 | 258.2407
873.5661 | 782.5661 | 333.4683 | 262.888 | 237.4519 | 233.4575 | 243.7848 | 202.4274 | 205.5037 | 258.2768
874.5676 | 783.5676 | 333.4278 | 262.9467 | 237.5702 | 233.5694 | 243.9025 | 202.5512 | 205.6031 | 258.3098
875.559 | 784.559 | 333.5325 | 263.0901 | 237.6793 | 233.69 | 244.0108 | 202.6706 | 205.7005 | 258.333
876.5604 | 785.5604 | 333.6119 | 263.2503 | 237.7973 | 233.8018 | 244.1205 | 202.7991 | 205.7932 | 258.3573
877.5619 | 786.5619 | 333.6692 | 263.3735 | 237.9119 | 233.9216 | 244.2233 | 202.9269 | 205.8742 | 258.4066
878.5633 | 787.5633 | 333.6421 | 263.5367 | 238.0355 | 234.0328 | 244.3264 | 203.051 | 205.9697 | 258.4304
879.5648 | 788.5648 | 333.5693 | 263.66 | 238.1493 | 234.1511 | 244.4247 | 203.1926 | 206.0481 | 258.4346
880.5662 | 789.5662 | 333.4893 | 263.8483 | 238.2579 | 234.26 | 244.5247 | 203.3159 | 206.1344 | 258.4616
881.5676 | 790.5676 | 333.4886 | 264.0328 | 238.3804 | 234.374 | 244.6266 | 203.4557 | 206.2088 | 258.4507
882.5691 | 791.5691 | 333.4163 | 264.2013 | 238.4878 | 234.4817 | 244.7195 | 203.5819 | 206.2924 | 258.4879
883.5605 | 792.5605 | 333.3045 | 264.3258 | 238.5947 | 234.5917 | 244.8203 | 203.7159 | 206.3687 | 258.5246
884.5619 | 793.5619 | 333.2895 | 264.503 | 238.7159 | 234.7018 | 244.9245 | 203.8553 | 206.4514 | 258.5569
885.5634 | 794.5634 | 333.2367 | 264.6353 | 238.8221 | 234.8079 | 245.0292 | 203.9801 | 206.5291 | 258.5766
886.5648 | 795.5648 | 333.1577 | 264.7712 | 238.9376 | 234.9164 | 245.1489 | 204.1119 | 206.614 | 258.6056
887.5763 | 796.5763 | 333.1389 | 264.9622 | 239.0433 | 235.0257 | 245.2609 | 204.2485 | 206.6931 | 258.6342
888.5677 | 797.5677 | 333.1038 | 265.0759 | 239.1725 | 235.1332 | 245.3746 | 204.3803 | 206.7791 | 258.68
889.5691 | 798.5691 | 333.0459 | 265.1917 | 239.275 | 235.229 | 245.4792 | 204.5063 | 206.8758 | 258.7139
890.5606 | 799.5606 | 332.915 | 265.4163 | 239.3746 | 235.329 | 245.5696 | 204.6392 | 206.9581 | 258.7369
891.562 | 800.562 | 332.8747 | 265.5365 | 239.4814 | 235.4369 | 245.6674 | 204.7739 | 207.0544 | 258.7751
892.5634 | 801.5634 | 332.8127 | 265.6121 | 239.5856 | 235.5425 | 245.7617 | 204.9064 | 207.1402 | 258.7962
893.5649 | 802.5649 | 332.81 | 265.7147 | 239.6939 | 235.6378 | 245.8631 | 205.0431 | 207.228 | 258.8159
894.5663 | 803.5663 | 332.7233 | 265.8329 | 239.8024 | 235.7412 | 245.9555 | 205.176 | 207.3145 | 258.8237
895.5678 | 804.5678 | 332.6745 | 265.926 | 239.9117 | 235.8443 | 246.0368 | 205.3209 | 207.4059 | 258.8671
896.5592 | 805.5592 | 332.6738 | 266.0629 | 240.0188 | 235.9443 | 246.1323 | 205.458 | 207.497 | 258.8855 | Time of first failure
897.5606 | 806.5606 | 332.6149 | 266.1747 | 240.1213 | 236.0353 | 246.2455 | 205.5949 | 207.5839 | 258.906 | 806 | 0
898.5621 | 807.5621 | 332.6146 | 266.2941 | 240.2348 | 236.1349 | 246.3385 | 205.7273 | 207.6681 | 258.923 | 806 | 900
899.5635 | 808.5635 | 332.5914 | 266.4327 | 240.3467 | 236.2355 | 246.4414 | 205.8555 | 207.7582 | 258.959
900.5649 | 809.5649 | 332.5524 | 266.5775 | 240.4541 | 236.3303 | 246.5365 | 205.9915 | 207.8436 | 258.9721
901.5664 | 810.5664 | 332.6264 | 266.6915 | 240.5574 | 236.4299 | 246.6336 | 206.1235 | 207.943 | 258.9967
902.5678 | 811.5678 | 332.8295 | 266.7953 | 240.6658 | 236.5218 | 246.7213 | 206.2639 | 208.0324 | 259.0115
903.5693 | 812.5693 | 332.9069 | 266.8918 | 240.7748 | 236.6236 | 246.8258 | 206.3965 | 208.1239 | 259.0371
904.5607 | 813.5607 | 332.9478 | 267.0249 | 240.8814 | 236.7288 | 246.91 | 206.5312 | 208.206 | 259.0899
905.5621 | 814.5621 | 332.9404 | 267.1301 | 240.9779 | 236.8266 | 247.0039 | 206.664 | 208.2952 | 259.1295
906.5636 | 815.5636 | 332.9534 | 267.2725 | 241.0805 | 236.929 | 247.0968 | 206.8038 | 208.378 | 259.1752
907.565 | 816.565 | 332.8706 | 267.4278 | 241.1757 | 237.0298 | 247.2009 | 206.926 | 208.4614 | 259.2021
908.5665 | 817.5665 | 332.8076 | 267.6045 | 241.2727 | 237.126 | 247.3228 | 207.0646 | 208.5499 | 259.2003
909.5679 | 818.5679 | 332.7907 | 267.6351 | 241.3722 | 237.224 | 247.4276 | 207.1964 | 208.6353 | 259.213
910.5593 | 819.5593 | 332.7742 | 267.7609 | 241.4874 | 237.3286 | 247.5524 | 207.3296 | 208.7156 | 259.2217
911.5608 | 820.5608 | 332.6855 | 267.8475 | 241.5828 | 237.4309 | 247.6524 | 207.4487 | 208.7954 | 259.268
912.5622 | 821.5622 | 332.5378 | 268.0058 | 241.6877 | 237.5306 | 247.7354 | 207.5795 | 208.8852 | 259.2823
913.5636 | 822.5636 | 332.468 | 268.0873 | 241.7881 | 237.6248 | 247.8452 | 207.7051 | 208.9589 | 259.2977
914.5651 | 823.5651 | 332.4658 | 268.1981 | 241.8836 | 237.7235 | 247.9417 | 207.839 | 209.0428 | 259.3293
915.5665 | 824.5665 | 332.4354 | 268.3483 | 241.9783 | 237.8234 | 248.0318 | 207.9742 | 209.117 | 259.3427
916.568 | 825.568 | 332.4422 | 268.4871 | 242.0808 | 237.9211 | 248.1181 | 208.1031 | 209.1899 | 259.3473
917.5594 | 826.5594 | 332.4657 | 268.5679 | 242.1861 | 238.0186 | 248.1986 | 208.2433 | 209.2688 | 259.391
918.5608 | 827.5608 | 332.4977 | 268.6136 | 242.2827 | 238.1091 | 248.2712 | 208.3717 | 209.3371 | 259.4305
919.5623 | 828.5623 | 332.4265 | 268.7068 | 242.3954 | 238.205 | 248.3519 | 208.5154 | 209.4113 | 259.4326
920.5637 | 829.5637 | 332.4155 | 268.7967 | 242.5091 | 238.2973 | 248.4303 | 208.6393 | 209.4823 | 259.4406
921.5651 | 830.5651 | 332.3477 | 268.9201 | 242.6185 | 238.3899 | 248.4835 | 208.7796 | 209.5524 | 259.4692
922.5666 | 831.5666 | 332.2538 | 269.0016 | 242.7425 | 238.479 | 248.5772 | 208.9116 | 209.6227 | 259.5071
923.568 | 832.568 | 332.2218 | 269.0334 | 242.8366 | 238.5671 | 248.6689 | 209.0431 | 209.6849 | 259.5343
924.5695 | 833.5695 | 332.1614 | 269.118 | 242.9363 | 238.6571 | 248.759 | 209.173 | 209.753 | 259.5765
925.5609 | 834.5609 | 332.0875 | 269.2123 | 243.0399 | 238.7463 | 248.8587 | 209.3087 | 209.8235 | 259.6023
926.5623 | 835.5623 | 331.9939 | 269.3123 | 243.1293 | 238.8375 | 248.9644 | 209.4325 | 209.8851 | 259.6124
927.5638 | 836.5638 | 331.8371 | 269.3285 | 243.2283 | 238.922 | 249.0712 | 209.5628 | 209.9505 | 259.6262
928.5652 | 837.5652 | 331.7775 | 269.4089 | 243.3143 | 239.0108 | 249.1699 | 209.6808 | 210.0199 | 259.6472
929.5667 | 838.5667 | 331.7077 | 269.5278 | 243.4242 | 239.0978 | 249.2641 | 209.8055 | 210.087 | 259.6666
930.5681 | 839.5681 | 331.6345 | 269.6158 | 243.517 | 239.1828 | 249.3442 | 209.9349 | 210.1492 | 259.7006
931.5695 | 840.5695 | 331.6387 | 269.6578 | 243.5958 | 239.2753 | 249.4351 | 210.0602 | 210.2191 | 259.7388
932.561 | 841.561 | 331.6368 | 269.7901 | 243.6823 | 239.3601 | 249.516 | 210.1858 | 210.2793 | 259.7455
933.5624 | 842.5624 | 331.5585 | 269.865 | 243.7687 | 239.4537 | 249.6057 | 210.317 | 210.3471 | 259.761
934.5638 | 843.5638 | 331.4761 | 269.9711 | 243.8658 | 239.5383 | 249.6897 | 210.4507 | 210.4095 | 259.7673
935.5653 | 844.5653 | 331.5156 | 270.1019 | 243.9518 | 239.6198 | 249.7818 | 210.5801 | 210.4749 | 259.7763
936.5667 | 845.5667 | 331.5457 | 270.2205 | 244.0351 | 239.7076 | 249.8711 | 210.7226 | 210.5412 | 259.8211
937.5682 | 846.5682 | 331.6949 | 270.3129 | 244.1149 | 239.7994 | 249.9411 | 210.8599 | 210.611 | 259.8443
938.5596 | 847.5596 | 331.867 | 270.4195 | 244.179 | 239.8876 | 250.0215 | 210.99 | 210.6761 | 259.8459
939.561 | 848.561 | 332.0514 | 270.4621 | 244.2566 | 239.9758 | 250.0967 | 211.1246 | 210.7454 | 259.8503
940.5625 | 849.5625 | 332.179 | 270.5658 | 244.332 | 240.0632 | 250.1735 | 211.2724 | 210.8242 | 259.859
941.5639 | 850.5639 | 332.3049 | 270.6837 | 244.4079 | 240.1504 | 250.2286 | 211.4147 | 210.8996 | 259.8546
942.5653 | 851.5653 | 332.4317 | 270.8159 | 244.5016 | 240.2389 | 250.3052 | 211.5611 | 210.9692 | 259.8316
943.5668 | 852.5668 | 332.4528 | 270.9662 | 244.5773 | 240.3276 | 250.3814 | 211.7157 | 211.0453 | 259.8292
944.5582 | 853.5582 | 332.4092 | 271.1269 | 244.6726 | 240.4163 | 250.438 | 211.8613 | 211.1148 | 259.8356
945.5697 | 854.5697 | 332.4156 | 271.2593 | 244.7605 | 240.5088 | 250.5042 | 212.0308 | 211.1847 | 259.8439
946.5911 | 855.5911 | 332.5141 | 271.369 | 244.878 | 240.5954 | 250.5792 | 212.1923 | 211.2644 | 259.8849
947.5625 | 856.5625 | 332.624 | 271.4875 | 245 | 240.6759 | 250.638 | 212.348 | 211.3307 | 259.8889
948.564 | 857.564 | 332.6293 | 271.5755 | 245.1036 | 240.7607 | 250.7165 | 212.5092 | 211.3992 | 259.8874
949.5654 | 858.5654 | 332.6486 | 271.6289 | 245.192 | 240.8492 | 250.778 | 212.676 | 211.4679 | 259.918
950.5668 | 859.5668 | 332.6479 | 271.6112 | 245.2792 | 240.9375 | 250.8738 | 212.8747 | 211.5318 | 259.9266
951.5683 | 860.5683 | 332.6599 | 271.6708 | 245.359 | 241.0208 | 250.9691 | 213.0774 | 211.6019 | 259.94
952.5597 | 861.5597 | 332.6798 | 271.7067 | 245.4665 | 241.1082 | 251.0344 | 213.3105 | 211.6734 | 259.9609
953.5612 | 862.5612 | 332.655 | 271.76 | 245.5385 | 241.197 | 251.1228 | 213.5688 | 211.7388 | 259.9731
954.5626 | 863.5626 | 332.6124 | 271.8092 | 245.6414 | 241.2787 | 251.2105 | 213.8883 | 211.8104 | 260.0144
955.564 | 864.564 | 332.5697 | 271.8199 | 245.7329 | 241.3664 | 251.2932 | 214.2737 | 211.8763 | 260.0084
956.5655 | 865.5655 | 332.576 | 271.8426 | 245.8314 | 241.4613 | 251.3766 | 214.7789 | 211.9478 | 260.0362
957.5669 | 866.5669 | 332.6053 | 271.9442 | 245.9382 | 241.5436 | 251.4446 | 215.3308 | 212.014 | 260.0508
958.5684 | 867.5684 | 332.5957 | 271.9941 | 246.0409 | 241.6358 | 251.506 | 215.8454 | 212.0836 | 260.0601
959.5598 | 868.5598 | 332.5993 | 272.0564 | 246.1121 | 241.7185 | 251.5615 | 216.2921 | 212.1464 | 260.0804
960.5612 | 869.5612 | 332.5946 | 272.1707 | 246.2146 | 241.8127 | 251.6295 | 216.7176 | 212.2176 | 260.1091
961.5627 | 870.5627 | 332.4036 | 272.2896 | 246.3066 | 241.9016 | 251.7038 | 217.122 | 212.2829 | 260.1023
962.5641 | 871.5641 | 332.2677 | 272.4414 | 246.3786 | 241.979 | 251.7601 | 217.4919 | 212.3473 | 260.122
963.5655 | 872.5655 | 332.0497 | 272.4878 | 246.4777 | 242.0752 | 251.8159 | 217.8443 | 212.4055 | 260.1271
964.567 | 873.567 | 331.8869 | 272.5988 | 246.5644 | 242.1577 | 251.8669 | 218.1966 | 212.4651 | 260.1313
965.5584 | 874.5584 | 331.7592 | 272.6231 | 246.6496 | 242.2467 | 251.9149 | 218.5109 | 212.5198 | 260.1314
966.5699 | 875.5699 | 331.6158 | 272.7396 | 246.7448 | 242.3322 | 251.9433 | 218.8265 | 212.584 | 260.131
967.5613 | 876.5613 | 331.7214 | 272.8867 | 246.8498 | 242.4166 | 251.9889 | 219.1279 | 212.6396 | 260.1328
968.5627 | 877.5627 | 331.9705 | 272.965 | 246.9498 | 242.5053 | 252.0261 | 219.4169 | 212.7057 | 260.1556
969.5642 | 878.5642 | 332.1162 | 273.0268 | 247.037 | 242.5879 | 252.0388 | 219.6944 | 212.7609 | 260.1097
970.5656 | 879.5656 | 332.1711 | 273.0872 | 247.1286 | 242.6628 | 252.0801 | 219.9695 | 212.8197 | 260.0827
971.567 | 880.567 | 332.2334 | 273.2119 | 247.2352 | 242.746 | 252.1196 | 220.2345 | 212.8933 | 260.0263
972.5685 | 881.5685 | 332.3982 | 273.3116 | 247.3431 | 242.8264 | 252.1572 | 220.4819 | 212.9553 | 259.9746
973.5699 | 882.5699 | 332.5851 | 273.3497 | 247.4461 | 242.906 | 252.169 | 220.7341 | 213.0247 | 259.9273
974.5614 | 883.5614 | 332.7513 | 273.4519 | 247.5317 | 242.981 | 252.1982 | 220.9772 | 213.0887 | 259.9534
975.5628 | 884.5628 | 332.7668 | 273.5152 | 247.6354 | 243.0621 | 252.2331 | 221.1885 | 213.1509 | 259.9666
976.5642 | 885.5642 | 332.8653 | 273.5407 | 247.7113 | 243.1308 | 252.267 | 221.4155 | 213.21 | 259.9733
977.5657 | 886.5657 | 332.9773 | 273.6367 | 247.8028 | 243.1994 | 252.3182 | 221.6592 | 213.2784 | 259.9931
978.5671 | 887.5671 | 333.0305 | 273.7672 | 247.887 | 243.2821 | 252.3604 | 221.8717 | 213.3326 | 259.9244
979.5686 | 888.5686 | 332.9925 | 273.8275 | 247.979 | 243.3503 | 252.4001 | 222.0718 | 213.3948 | 259.8695
980.56 | 889.56 | 332.9308 | 273.8938 | 248.063 | 243.4286 | 252.4185 | 222.2716 | 213.4423 | 259.8698
981.5614 | 890.5614 | 332.888 | 273.9929 | 248.1569 | 243.493 | 252.4619 | 222.4759 | 213.5055 | 259.8684
982.5629 | 891.5629 | 332.813 | 274.1157 | 248.2439 | 243.5605 | 252.4956 | 222.667 | 213.5566 | 259.8796
983.5643 | 892.5643 | 332.7925 | 274.2251 | 248.3319 | 243.6335 | 252.5278 | 222.849 | 213.6123 | 259.8766
984.5657 | 893.5657 | 332.7076 | 274.3148 | 248.4219 | 243.7089 | 252.5687 | 223.0238 | 213.6678 | 259.9083
985.5672 | 894.5672 | 332.6127 | 274.3541 | 248.5264 | 243.7724 | 252.623 | 223.1988 | 213.7251 | 259.912
986.5586 | 895.5586 | 332.4581 | 274.4149 | 248.6182 | 243.8473 | 252.6718 | 223.3742 | 213.7725 | 259.9466
987.5701 | 896.5701 | 332.3536 | 274.4521 | 248.7124 | 243.9179 | 252.7259 | 223.5525 | 213.8294 | 259.9452
988.5615 | 897.5615 | 332.3071 | 274.535 | 248.8021 | 243.9859 | 252.7588 | 223.7256 | 213.8806 | 259.9652
989.5629 | 898.5629 | 332.3372 | 274.5935 | 248.8857 | 244.0537 | 252.8345 | 223.887 | 213.9271 | 259.9728
990.5644 | 899.5644 | 332.2918 | 274.6435 | 248.9674 | 244.1229 | 252.8859 | 224.0215 | 213.9843 | 259.9676
991.5658 | 900.5658 | 332.2185 | 274.7006 | 249.0266 | 244.1973 | 252.9325 | 224.1658 | 214.0269 | 259.952
992.5672 | 901.5672 | 332.1102 | 274.7383 | 249.1074 | 244.2672 | 253.008 | 224.2991 | 214.0845 | 259.9287
993.5687 | 902.5687 | 332.042 | 274.7806 | 249.1887 | 244.3395 | 253.0571 | 224.417 | 214.1259 | 259.9598
994.5601 | 903.5601 | 332.095 | 274.8597 | 249.2651 | 244.4021 | 253.1237 | 224.4848 | 214.1731 | 259.9135
995.5615 | 904.5615 | 332.0097 | 274.9775 | 249.3505 | 244.4743 | 253.1703 | 224.5838 | 214.2223 | 259.9545
996.563 | 905.563 | 331.9124 | 274.9685 | 249.4259 | 244.5418 | 253.223 | 224.7021 | 214.2711 | 259.9168
997.5644 | 906.5644 | 331.8521 | 275.0238 | 249.4903 | 244.6118 | 253.247 | 224.8337 | 214.3308 | 259.9243
998.5659 | 907.5659 | 331.7434 | 275.0591 | 249.5834 | 244.6788 | 253.2723 | 224.9524 | 214.3829 | 259.9058
999.5673 | 908.5673 | 331.595 | 275.1422 | 249.6679 | 244.7512 | 253.2915 | 225.0289 | 214.4442 | 259.9185
1000.5687 | 909.5687 | 331.6265 | 275.1694 | 249.737 | 244.8153 | 253.327 | 225.1423 | 214.5054 | 259.937
1001.5602 | 910.5602 | 331.7456 | 275.1981 | 249.8084 | 244.8794 | 253.3786 | 225.2225 | 214.5738 | 259.9629
1002.5616 | 911.5616 | 331.8793 | 275.2542 | 249.8874 | 244.9376 | 253.4172 | 225.3233 | 214.639 | 259.974
1003.5631 | 912.5631 | 331.927 | 275.2917 | 249.9638 | 244.9932 | 253.4461 | 225.4007 | 214.6988 | 259.9811
1004.5645 | 913.5645 | 331.9893 | 275.3727 | 250.0324 | 245.0549 | 253.508 | 225.476 | 214.7635 | 260.0199
1005.5659 | 914.5659 | 332.011 | 275.4591 | 250.0991 | 245.1098 | 253.5543 | 225.5619 | 214.8324 | 260.0271
1006.5674 | 915.5674 | 332.097 | 275.5413 | 250.1784 | 245.166 | 253.6334 | 225.6489 | 214.8939 | 260.0292
1007.5588 | 916.5588 | 332.2213 | 275.6562 | 250.2505 | 245.2279 | 253.6955 | 225.7266 | 214.9598 | 260.0407
1008.5602 | 917.5602 | 332.2474 | 275.6426 | 250.3238 | 245.2738 | 253.7661 | 225.8029 | 215.02 | 260.027
1009.5617 | 918.5617 | 332.3186 | 275.7297 | 250.3715 | 245.3361 | 253.8346 | 225.8966 | 215.0838 | 260.0691
1010.5631 | 919.5631 | 332.3531 | 275.84 | 250.4603 | 245.389 | 253.8942 | 225.9785 | 215.1548 | 260.0683
1011.5646 | 920.5646 | 332.3522 | 275.9003 | 250.5217 | 245.446 | 253.9676 | 226.0646 | 215.2234 | 260.075
1012.566 | 921.566 | 332.3904 | 275.8537 | 250.5897 | 245.5095 | 254.0421 | 226.1489 | 215.2864 | 260.0928
1013.5674 | 922.5674 | 332.4219 | 275.9485 | 250.6678 | 245.564 | 254.0875 | 226.2221 | 215.3394 | 260.1276
1014.5689 | 923.5689 | 332.448 | 275.9998 | 250.7419 | 245.6176 | 254.1786 | 226.3147 | 215.3979 | 260.1217
1015.5603 | 924.5603 | 332.446 | 276.0929 | 250.8143 | 245.6709 | 254.2569 | 226.4019 | 215.4555 | 260.1393
1016.5617 | 925.5617 | 332.5249 | 276.1835 | 250.8969 | 245.7323 | 254.3448 | 226.4468 | 215.5045 | 260.0857
1017.5632 | 926.5632 | 332.5285 | 276.2115 | 250.9635 | 245.7941 | 254.4092 | 226.5379 | 215.5651 | 260.0203
1018.5646 | 927.5646 | 332.4973 | 276.3013 | 251.0326 | 245.8495 | 254.4599 | 226.6281 | 215.6166 | 260.0021
1019.5661 | 928.5661 | 332.4925 | 276.3408 | 251.1097 | 245.9051 | 254.5045 | 226.7326 | 215.6695 | 260.005
1020.5675 | 929.5675 | 332.5576 | 276.3707 | 251.1729 | 245.9657 | 254.5457 | 226.8301 | 215.7277 | 259.993
1021.5689 | 930.5689 | 332.5769 | 276.4408 | 251.2497 | 246.0231 | 254.5947 | 226.9242 | 215.7848 | 260.0384
1022.5604 | 931.5604 | 332.5156 | 276.5529 | 251.319 | 246.085 | 254.6367 | 227.0143 | 215.8317 | 260.0339
1023.5618 | 932.5618 | 332.5076 | 276.5467 | 251.3856 | 246.1417 | 254.6964 | 227.1097 | 215.8866 | 260.0414
1024.5632 | 933.5632 | 332.4962 | 276.5638 | 251.461 | 246.2053 | 254.7366 | 227.2088 | 215.9438 | 260.0665
1025.5647 | 934.5647 | 332.5518 | 276.5764 | 251.5234 | 246.2556 | 254.7844 | 227.331 | 215.9876 | 260.0577
1026.5661 | 935.5661 | 332.6128 | 276.6269 | 251.6186 | 246.3207 | 254.8473 | 227.3998 | 216.0383 | 260.0473
1027.5676 | 936.5676 | 332.5945 | 276.7247 | 251.7005 | 246.3721 | 254.8868 | 227.5053 | 216.0863 | 260.034
1028.559 | 937.559 | 332.6666 | 276.7918 | 251.7649 | 246.4279 | 254.93 | 227.5897 | 216.1308 | 260.0593
1029.5604 | 938.5604 | 332.7052 | 276.8974 | 251.8315 | 246.4838 | 254.9492 | 227.6828 | 216.1832 | 260.0699
1030.5619 | 939.5619 | 332.6631 | 276.9497 | 251.8858 | 246.5368 | 255.0083 | 227.7911 | 216.2306 | 260.0938
1031.5633 | 940.5633 | 332.5529 | 276.9952 | 251.9361 | 246.59 | 255.0486 | 227.8946 | 216.2907 | 260.061
1032.5648 | 941.5648 | 332.4918 | 277.005 | 252.0041 | 246.6401 | 255.1002 | 227.9813 | 216.3436 | 260.0706
1033.5662 | 942.5662 | 332.4277 | 277.0019 | 252.0577 | 246.6943 | 255.1252 | 228.0622 | 216.391 | 260.0486
1034.5676 | 943.5676 | 332.5082 | 277.0634 | 252.1304 | 246.7463 | 255.158 | 228.1516 | 216.4526 | 260.0348
1035.5691 | 944.5691 | 332.593 | 277.0716 | 252.1945 | 246.7934 | 255.1918 | 228.239 | 216.4931 | 260.0436
1036.5605 | 945.5605 | 332.7764 | 277.0925 | 252.2726 | 246.8484 | 255.2346 | 228.3266 | 216.5468 | 260.0364
1037.5619 | 946.5619 | 332.8113 | 277.0783 | 252.351 | 246.8946 | 255.2731 | 228.4096 | 216.5968 | 260.0491
1038.5634 | 947.5634 | 332.7772 | 277.0655 | 252.4026 | 246.9491 | 255.3211 | 228.4998 | 216.6515 | 260.0568
1039.5648 | 948.5648 | 332.8101 | 277.1524 | 252.4737 | 246.9988 | 255.3678 | 228.5938 | 216.7017 | 260.0936
1040.5663 | 949.5663 | 332.8235 | 277.218 | 252.5335 | 247.0505 | 255.4191 | 228.6731 | 216.7502 | 260.1294
1041.5677 | 950.5677 | 332.8237 | 277.2359 | 252.5989 | 247.0989 | 255.468 | 228.7628 | 216.8039 | 260.1243
1042.5591 | 951.5591 | 332.7837 | 277.2467 | 252.6602 | 247.1441 | 255.5295 | 228.8618 | 216.8549 | 260.0975
1043.5606 | 952.5606 | 332.7089 | 277.3199 | 252.722 | 247.2021 | 255.5842 | 228.9356 | 216.9078 | 260.1064
1044.562 | 953.562 | 332.6389 | 277.3432 | 252.7812 | 247.2478 | 255.6411 | 229.0228 | 216.9597 | 260.1427
1045.5634 | 954.5634 | 332.6412 | 277.3871 | 252.8501 | 247.2997 | 255.7114 | 229.0864 | 217.0189 | 260.1495
1046.5649 | 955.5649 | 332.5939 | 277.4791 | 252.916 | 247.3533 | 255.7563 | 229.1664 | 217.0683 | 260.163
1047.5663 | 956.5663 | 332.6112 | 277.5158 | 252.9907 | 247.3984 | 255.8255 | 229.2232 | 217.1123 | 260.1714
1048.5678 | 957.5678 | 332.6304 | 277.5727 | 253.0644 | 247.4478 | 255.8774 | 229.3155 | 217.1751 | 260.1657
1049.5592 | 958.5592 | 332.5721 | 277.6184 | 253.123 | 247.4974 | 255.9324 | 229.4175 | 217.2217 | 260.1744
1050.5606 | 959.5606 | 332.5184 | 277.5785 | 253.1924 | 247.5491 | 256.0042 | 229.5081 | 217.2734 | 260.1706
1051.5621 | 960.5621 | 332.4786 | 277.4906 | 253.2675 | 247.596 | 256.0385 | 229.5324 | 217.3304 | 260.1785
1052.5635 | 961.5635 | 332.3995 | 277.5987 | 253.3493 | 247.6529 | 256.0938 | 229.6169 | 217.3784 | 260.1762
1053.565 | 962.565 | 332.3688 | 277.656 | 253.4274 | 247.6987 | 256.1343 | 229.669 | 217.4478 | 260.2106
1054.5664 | 963.5664 | 332.3829 | 277.6459 | 253.4982 | 247.7528 | 256.1805 | 229.7691 | 217.5044 | 260.2177
1055.5678 | 964.5678 | 332.3718 | 277.6087 | 253.5619 | 247.8056 | 256.2194 | 229.8499 | 217.5696 | 260.2456
1056.5693 | 965.5693 | 332.4707 | 277.6695 | 253.6226 | 247.854 | 256.2924 | 229.8622 | 217.6414 | 260.2412
1057.5607 | 966.5607 | 332.498 | 277.6863 | 253.6817 | 247.906 | 256.3468 | 229.913 | 217.7094 | 260.2304
1058.5621 | 967.5621 | 332.4848 | 277.6871 | 253.7395 | 247.9604 | 256.3987 | 229.9616 | 217.7782 | 260.2287
1059.5636 | 968.5636 | 332.5223 | 277.6311 | 253.7942 | 248.0091 | 256.4339 | 230.0294 | 217.8598 | 260.2332
1060.565 | 969.565 | 332.4936 | 277.6306 | 253.8737 | 248.0593 | 256.4787 | 230.0941 | 217.9319 | 260.2373
1061.5665 | 970.5665 | 332.4254 | 277.6798 | 253.9788 | 248.112 | 256.5324 | 230.1167 | 217.9985 | 260.2253
1062.5679 | 971.5679 | 332.3962 | 277.7066 | 254.08 | 248.1628 | 256.5743 | 230.2012 | 218.081 | 260.2079
1063.5693 | 972.5693 | 332.4628 | 277.763 | 254.1766 | 248.2155 | 256.632 | 230.2651 | 218.1623 | 260.1795
1064.5608 | 973.5608 | 332.5101 | 277.7916 | 254.246 | 248.2717 | 256.6807 | 230.3498 | 218.2391 | 260.1726
1065.5622 | 974.5622 | 332.4592 | 277.7277 | 254.3035 | 248.3164 | 256.7135 | 230.4334 | 218.3152 | 260.1846
1066.5636 | 975.5636 | 332.3583 | 277.7721 | 254.3657 | 248.3632 | 256.7408 | 230.5338 | 218.3922 | 260.1761
1067.5651 | 976.5651 | 332.3392 | 277.7667 | 254.4258 | 248.416 | 256.7601 | 230.6171 | 218.4538 | 260.1967
1068.5665 | 977.5665 | 332.3147 | 277.8135 | 254.4829 | 248.4568 | 256.7889 | 230.7004 | 218.5253 | 260.1858
1069.568 | 978.568 | 332.4687 | 277.8874 | 254.539 | 248.5041 | 256.811 | 230.787 | 218.5962 | 260.1983
1070.5594 | 979.5594 | 332.5428 | 277.8861 | 254.621 | 248.5542 | 256.8316 | 230.8699 | 218.6666 | 260.2119
1071.5608 | 980.5608 | 332.617 | 277.9316 | 254.6951 | 248.5982 | 256.8677 | 230.9468 | 218.7293 | 260.2269
1072.5623 | 981.5623 | 332.6884 | 277.8167 | 254.75 | 248.645 | 256.9116 | 231.0412 | 218.7976 | 260.2179
1073.5637 | 982.5637 | 332.7345 | 277.8474 | 254.7953 | 248.6893 | 256.9517 | 231.1281 | 218.857 | 260.2232
1074.5651 | 983.5651 | 332.7794 | 277.8448 | 254.8435 | 248.7294 | 256.9902 | 231.2264 | 218.926 | 260.2631
1075.5666 | 984.5666 | 332.705 | 277.9444 | 254.9134 | 248.7772 | 257.047 | 231.3222 | 218.9901 | 260.2641
1076.568 | 985.568 | 332.6582 | 278.0123 | 254.9625 | 248.8093 | 257.0841 | 231.4002 | 219.0441 | 260.2587
1077.5695 | 986.5695 | 332.5738 | 278.083 | 255.0017 | 248.8542 | 257.1398 | 231.504 | 219.0983 | 260.2511
1078.5609 | 987.5609 | 332.4631 | 278.0753 | 255.0448 | 248.8864 | 257.1958 | 231.5826 | 219.1658 | 260.2748
1079.5623 | 988.5623 | 332.4652 | 278.0995 | 255.0965 | 248.9202 | 257.2427 | 231.6716 | 219.2189 | 260.3025
1080.5638 | 989.5638 | 332.4636 | 278.1682 | 255.1604 | 248.957 | 257.2956 | 231.7503 | 219.2767 | 260.3305
1081.5652 | 990.5652 | 332.3225 | 278.1408 | 255.2405 | 248.9936 | 257.3444 | 231.8335 | 219.3357 | 260.3473
1082.5667 | 991.5667 | 332.1285 | 278.2065 | 255.3191 | 249.0215 | 257.3967 | 231.9036 | 219.3948 | 260.3451
1083.5681 | 992.5681 | 331.9584 | 278.2806 | 255.3752 | 249.0608 | 257.457 | 231.9851 | 219.4535 | 260.3581
1084.5595 | 993.5595 | 331.7234 | 278.335 | 255.4389 | 249.0905 | 257.5174 | 232.0598 | 219.5047 | 260.3608
1085.561 | 994.561 | 331.6005 | 278.3457 | 255.5078 | 249.1303 | 257.5724 | 232.1011 | 219.5582 | 260.3506
1086.5624 | 995.5624 | 331.5277 | 278.4382 | 255.5492 | 249.1662 | 257.614 | 232.1462 | 219.6042 | 260.3378
1087.5638 | 996.5638 | 331.5295 | 278.4879 | 255.6285 | 249.1943 | 257.6563 | 232.2063 | 219.6649 | 260.3552
1088.5653 | 997.5653 | 331.5387 | 278.5166 | 255.6977 | 249.2289 | 257.6954 | 232.262 | 219.7201 | 260.3273
1089.5667 | 998.5667 | 331.433 | 278.5937 | 255.7623 | 249.261 | 257.7382 | 232.314 | 219.7754 | 260.3416
1090.5581 | 999.5581 | 331.3727 | 278.5929 | 255.8454 | 249.2952 | 257.7804 | 232.3925 | 219.8305 | 260.3356
1091.5596 | 1000.5596 | 331.3112 | 278.6328 | 255.955 | 249.3292 | 257.8199 | 232.4494 | 219.8842 | 260.3421
1092.561 | 1001.561 | 331.2558 | 278.6414 | 256.0067 | 249.3663 | 257.8601 | 232.4887 | 219.9379 | 260.3335
1093.5625 | 1002.5625 | 331.3426 | 278.6989 | 256.0508 | 249.3969 | 257.9095 | 232.542 | 219.9968 | 260.3308
1094.5639 | 1003.5639 | 331.4575 | 278.7505 | 256.0907 | 249.4285 | 257.9328 | 232.6073 | 220.0551 | 260.3601
1095.5653 | 1004.5653 | 331.5378 | 278.7474 | 256.1107 | 249.4579 | 257.9612 | 232.6693 | 220.1093 | 260.3728
1096.5668 | 1005.5668 | 331.6544 | 278.7411 | 256.1256 | 249.4926 | 257.9957 | 232.7382 | 220.164 | 260.4001
1097.5682 | 1006.5682 | 331.718 | 278.7452 | 256.1448 | 249.5158 | 258.0474 | 232.8166 | 220.225 | 260.4094
1098.5697 | 1007.5697 | 331.7791 | 278.8105 | 256.1562 | 249.5418 | 258.0952 | 232.8872 | 220.2805 | 260.4434
1099.5611 | 1008.5611 | 331.8429 | 278.8721 | 256.1627 | 249.5631 | 258.1515 | 232.9347 | 220.3312 | 260.4611
1100.5625 | 1009.5625 | 332.0198 | 278.8767 | 256.1905 | 249.59 | 258.2145 | 232.9913 | 220.3876 | 260.4384
1101.564 | 1010.564 | 332.2838 | 278.9104 | 256.2325 | 249.6071 | 258.2722 | 233.0434 | 220.4426 | 260.4267
1102.5654 | 1011.5654 | 332.4315 | 278.9667 | 256.2716 | 249.6383 | 258.3463 | 233.1105 | 220.4898 | 260.4246
1103.5669 | 1012.5669 | 332.6186 | 278.9952 | 256.2922 | 249.6641 | 258.4203 | 233.1348 | 220.5429 | 260.4456
1104.5683 | 1013.5683 | 332.7683 | 279.0049 | 256.3008 | 249.6964 | 258.4703 | 233.1975 | 220.5944 | 260.4518
1105.5697 | 1014.5697 | 332.8567 | 279.0304 | 256.3345 | 249.7246 | 258.5196 | 233.2429 | 220.6456 | 260.471
1106.5612 | 1015.5612 | 332.8668 | 279.0464 | 256.374 | 249.7579 | 258.5752 | 233.267 | 220.699 | 260.4939
1107.5626 | 1016.5626 | 332.9027 | 279.0481 | 256.4186 | 249.7859 | 258.6386 | 233.3476 | 220.7537 | 260.507
1108.564 | 1017.564 | 332.886 | 279.0147 | 256.4569 | 249.819 | 258.6821 | 233.4357 | 220.8033 | 260.5684
1109.5655 | 1018.5655 | 332.8659 | 279.0309 | 256.511 | 249.8546 | 258.7305 | 233.4889 | 220.8524 | 260.5794
1110.5669 | 1019.5669 | 332.7465 | 279.033 | 256.5809 | 249.8816 | 258.7849 | 233.5453 | 220.8996 | 260.588
1111.5684 | 1020.5684 | 332.63 | 279.0264 | 256.6832 | 249.9143 | 258.8521 | 233.5884 | 220.9466 | 260.6093
1112.5598 | 1021.5598 | 332.4807 | 279.0217 | 256.766 | 249.9488 | 258.9065 | 233.6448 | 220.9924 | 260.6095
1113.5612 | 1022.5612 | 332.3656 | 279.1068 | 256.8421 | 249.9835 | 258.9729 | 233.693 | 221.0465 | 260.5932
1114.5627 | 1023.5627 | 332.3116 | 279.1966 | 256.9147 | 250.0156 | 259.0129 | 233.7392 | 221.1033 | 260.6036
1115.5641 | 1024.5641 | 332.3115 | 279.2298 | 256.9943 | 250.0551 | 259.063 | 233.8047 | 221.1565 | 260.6212
1116.5655 | 1025.5655 | 332.3103 | 279.239 | 257.0523 | 250.0815 | 259.1041 | 233.8792 | 221.2134 | 260.6354
1117.567 | 1026.567 | 332.3633 | 279.2955 | 257.1187 | 250.1149 | 259.1585 | 233.9477 | 221.2792 | 260.613
1118.5684 | 1027.5684 | 332.4281 | 279.3701 | 257.2251 | 250.1486 | 259.2241 | 233.9845 | 221.333 | 260.6349
1119.5699 | 1028.5699 | 332.4137 | 279.3298 | 257.3514 | 250.1838 | 259.2973 | 234.0408 | 221.3902 | 260.6538
1120.5613 | 1029.5613 | 332.4267 | 279.3044 | 257.4671 | 250.2147 | 259.3841 | 234.11 | 221.4425 | 260.6873
1121.5627 | 1030.5627 | 332.3682 | 279.3486 | 257.5626 | 250.2601 | 259.4722 | 234.1822 | 221.4953 | 260.6994
1122.5642 | 1031.5642 | 332.2066 | 279.4208 | 257.6605 | 250.2811 | 259.5612 | 234.2466 | 221.5402 | 260.7222
1123.5656 | 1032.5656 | 332.0959 | 279.5108 | 257.7383 | 250.3235 | 259.6555 | 234.3074 | 221.5928 | 260.7261
1124.5771 | 1033.5771 | 332.0505 | 279.4699 | 257.8375 | 250.3503 | 259.7245 | 234.3734 | 221.6413 | 260.7565
1125.5585 | 1034.5585 | 331.9351 | 279.4932 | 257.9134 | 250.3901 | 259.7974 | 234.4396 | 221.6822 | 260.7248
1126.5599 | 1035.5599 | 331.8368 | 279.4968 | 257.9748 | 250.428 | 259.877 | 234.4853 | 221.7274 | 260.7224
1127.6515 | 1036.6515 | 331.8063 | 279.3566 | 258.0505 | 250.4713 | 259.9425 | 234.5581 | 221.7769 | 260.72
1128.5628 | 1037.5628 | 331.7065 | 279.3089 | 258.1155 | 250.5173 | 260.0033 | 234.621 | 221.831 | 260.7051
1129.5642 | 1038.5642 | 331.604 | 279.3794 | 258.1961 | 250.5512 | 260.066 | 234.6719 | 221.8862 | 260.6828
1130.5657 | 1039.5657 | 331.545 | 279.2862 | 258.2967 | 250.5981 | 260.1227 | 234.6635 | 221.9442 | 260.6779
1131.5671 | 1040.5671 | 331.5348 | 279.3501 | 258.3673 | 250.6301 | 260.185 | 234.7102 | 221.9997 | 260.6799
1132.5686 | 1041.5686 | 331.5963 | 279.356 | 258.3482 | 250.6638 | 260.2455 | 234.7552 | 222.0498 | 260.708
1133.56 | 1042.56 | 331.676 | 279.287 | 258.3405 | 250.6994 | 260.3154 | 234.7889 | 222.0993 | 260.6924
1134.5614 | 1043.5614 | 331.7528 | 279.2366 | 258.3645 | 250.7376 | 260.3744 | 234.8167 | 222.1512 | 260.6718
1135.5629 | 1044.5629 | 331.8097 | 279.2842 | 258.3982 | 250.77 | 260.4246 | 234.8552 | 222.203 | 260.6858
1136.5643 | 1045.5643 | 331.9211 | 279.236 | 258.4415 | 250.8 | 260.4716 | 234.8864 | 222.2589 | 260.6781
1137.5657 | 1046.5657 | 331.9911 | 279.3233 | 258.4846 | 250.8243 | 260.5474 | 234.9125 | 222.3039 | 260.6967
1138.5672 | 1047.5672 | 332.0566 | 279.3128 | 258.4988 | 250.855 | 260.6029 | 234.9701 | 222.3568 | 260.7168
1139.5686 | 1048.5686 | 332.1616 | 279.2718 | 258.5061 | 250.8827 | 260.6499 | 235.0057 | 222.3997 | 260.7294
1140.5701 | 1049.5701 | 332.2797 | 279.1986 | 258.5493 | 250.9019 | 260.7019 | 235.0517 | 222.4509 | 260.7485
1141.5615 | 1050.5615 | 332.4477 | 279.0309 | 258.584 | 250.9292 | 260.7612 | 235.0947 | 222.4974 | 260.7548
1142.5629 | 1051.5629 | 332.5256 | 278.9877 | 258.6245 | 250.9598 | 260.8167 | 235.13 | 222.5407 | 260.7655
1143.5644 | 1052.5644 | 332.5725 | 278.926 | 258.6893 | 250.9891 | 260.8697 | 235.131 | 222.5876 | 260.7846
1144.5658 | 1053.5658 | 332.6075 | 278.7737 | 258.7533 | 251.016 | 260.9338 | 235.1649 | 222.64 | 260.7981
1145.5672 | 1054.5672 | 332.7131 | 278.8554 | 258.795 | 251.0426 | 260.9804 | 235.2075 | 222.6837 | 260.8155
1146.5687 | 1055.5687 | 332.8256 | 278.7112 | 258.8173 | 251.0761 | 261.0223 | 235.1984 | 222.7327 | 260.8364
1147.5701 | 1056.5701 | 332.873 | 278.657 | 258.9331 | 251.0804 | 261.4325 | 235.6929 | 222.693 | 260.7055
1148.5616 | 1057.5616 | 332.9001 | 278.8166 | 258.8851 | 251.1389 | 261.1467 | 235.3246 | 222.8289 | 260.8753
1149.563 | 1058.563 | 332.9756 | 278.923 | 258.8818 | 251.1699 | 261.2142 | 235.3591 | 222.8821 | 260.8705
1150.5644 | 1059.5644 | 333.1073 | 278.8139 | 258.8061 | 251.2034 | 261.2718 | 235.4148 | 222.9293 | 260.8516
1151.5659 | 1060.5659 | 333.1834 | 278.904 | 258.683 | 251.236 | 261.3466 | 235.4328 | 222.9971 | 260.8595
1152.5673 | 1061.5673 | 333.3078 | 278.9735 | 258.6442 | 251.2726 | 261.4044 | 235.4772 | 223.0462 | 260.8369
1153.5688 | 1062.5688 | 333.2841 | 279.0238 | 258.6189 | 251.297 | 261.4441 | 235.5189 | 223.1028 | 260.8229
1154.5602 | 1063.5602 | 333.2744 | 278.9914 | 258.6105 | 251.3333 | 261.4766 | 235.5919 | 223.1609 | 260.8066
1155.5616 | 1064.5616 | 333.3449 | 279.0425 | 258.6027 | 251.3646 | 261.4928 | 235.6578 | 223.2165 | 260.7857
1156.5631 | 1065.5631 | 333.4232 | 279.0309 | 258.6186 | 251.3956 | 261.5091 | 235.6852 | 223.2647 | 260.7964
1157.5645 | 1066.5645 | 333.4323 | 279.0623 | 258.6896 | 251.4328 | 261.5462 | 235.6634 | 223.3274 | 260.8176
1158.5659 | 1067.5659 | 333.5155 | 279.0505 | 258.7487 | 251.4525 | 261.5566 | 235.6426 | 223.3776 | 260.8367
1159.5674 | 1068.5674 | 333.5647 | 279.0605 | 258.7999 | 251.4861 | 261.6027 | 235.6804 | 223.4332 | 260.8655
1160.5588 | 1069.5588 | 333.5778 | 279.2221 | 258.8577 | 251.5124 | 261.6445 | 235.7228 | 223.488 | 260.9031
1161.5602 | 1070.5602 | 333.538 | 279.3182 | 258.8781 | 251.5394 | 261.7178 | 235.7907 | 223.5357 | 260.9038
1162.5617 | 1071.5617 | 333.582 | 279.1384 | 258.9416 | 251.5653 | 261.7801 | 235.8737 | 223.5994 | 260.953
1163.5631 | 1072.5631 | 333.6706 | 279.0577 | 258.9714 | 251.5913 | 261.8337 | 235.9359 | 223.6583 | 260.9789
1164.5646 | 1073.5646 | 333.5926 | 279.0934 | 259.0075 | 251.6115 | 261.9063 | 235.9988 | 223.7093 | 261.0254
1165.566 | 1074.566 | 333.5386 | 279.1014 | 259.0772 | 251.6318 | 261.9622 | 236.0427 | 223.7677 | 261.0742
1166.5674 | 1075.5674 | 333.5466 | 279.0567 | 259.1209 | 251.6545 | 262.0336 | 236.0975 | 223.8249 | 261.1046
1167.5589 | 1076.5589 | 333.4725 | 279.1056 | 259.1478 | 251.6871 | 262.1113 | 236.1442 | 223.8853 | 261.0957
1168.5603 | 1077.5603 | 333.4008 | 279.1512 | 259.1594 | 251.7133 | 262.1962 | 236.2135 | 223.9523 | 261.1139
1169.5617 | 1078.5617 | 333.4003 | 279.0421 | 259.2305 | 251.7393 | 262.2666 | 236.2678 | 223.9995 | 261.1314
1170.5632 | 1079.5632 | 333.395 | 279.021 | 259.32 | 251.7689 | 262.317 | 236.3227 | 224.0571 | 261.1073
1171.5646 | 1080.5646 | 333.4727 | 279.1821 | 259.3853 | 251.8011 | 262.357 | 236.3755 | 224.1056 | 261.1154
1172.5661 | 1081.5661 | 333.7168 | 279.1879 | 259.4359 | 251.8318 | 262.4011 | 236.4445 | 224.1581 | 261.1067
1173.5675 | 1082.5675 | 333.783 | 279.1207 | 259.4867 | 251.8682 | 262.4317 | 236.4988 | 224.2072 | 261.1693
1174.5689 | 1083.5689 | 333.8231 | 279.1208 | 259.5475 | 251.9032 | 262.4728 | 236.5423 | 224.2504 | 261.2004
1175.5604 | 1084.5604 | 333.919 | 279.1561 | 259.5969 | 251.9311 | 262.5121 | 236.603 | 224.3005 | 261.2268
1176.5618 | 1085.5618 | 333.9397 | 279.1937 | 259.6243 | 251.965 | 262.5364 | 236.6503 | 224.3475 | 261.2232
1177.5633 | 1086.5633 | 333.967 | 279.3471 | 259.6797 | 251.9964 | 262.5551 | 236.7022 | 224.3959 | 261.2479
1178.5647 | 1087.5647 | 334.0094 | 279.3775 | 259.7104 | 252.0326 | 262.5743 | 236.7626 | 224.4367 | 261.2578
1179.5661 | 1088.5661 | 334.0684 | 279.4221 | 259.7582 | 252.0674 | 262.5926 | 236.8104 | 224.48 | 261.2801
1180.5676 | 1089.5676 | 334.0652 | 279.504 | 259.7835 | 252.1005 | 262.6044 | 236.8536 | 224.5255 | 261.3346
1181.569 | 1090.569 | 333.975 | 279.6385 | 259.8292 | 252.1251 | 262.6262 | 236.912 | 224.5631 | 261.3532
1182.5604 | 1091.5604 | 333.9688 | 279.6557 | 259.9033 | 252.1598 | 262.6508 | 236.9532 | 224.6094 | 261.3605
1183.5619 | 1092.5619 | 333.9866 | 279.6902 | 259.9825 | 252.187 | 262.6629 | 236.993 | 224.6418 | 261.3511
1184.5633 | 1093.5633 | 333.957 | 279.7196 | 260.0498 | 252.2102 | 262.6811 | 237.0421 | 224.6833 | 261.3999
1185.5648 | 1094.5648 | 333.9556 | 279.6869 | 260.1163 | 252.231 | 262.6955 | 237.0948 | 224.7214 | 261.3987
1186.5662 | 1095.5662 | 333.9826 | 279.7082 | 260.1665 | 252.2582 | 262.7239 | 237.1438 | 224.759 | 261.4143
1187.5777 | 1096.5777 | 334.0071 | 279.7852 | 260.1591 | 252.2885 | 262.7662 | 237.2095 | 224.7985 | 261.426
1188.5591 | 1097.5591 | 333.9492 | 279.8557 | 260.1501 | 252.309 | 262.8064 | 237.2702 | 224.8381 | 261.4564
1189.5705 | 1098.5705 | 333.9615 | 279.9459 | 260.175 | 252.3358 | 262.8283 | 237.3104 | 224.8741 | 261.5007
1190.5619 | 1099.5619 | 333.9854 | 279.9168 | 260.179 | 252.3593 | 262.8619 | 237.3741 | 224.9269 | 261.5278
1191.5634 | 1100.5634 | 333.9554 | 279.8551 | 260.142 | 252.3747 | 262.8819 | 237.4302 | 224.9659 | 261.5294
1192.5648 | 1101.5648 | 333.8673 | 279.7415 | 260.0723 | 252.4018 | 262.9261 | 237.4631 | 225.0085 | 261.5643
1193.5663 | 1102.5663 | 333.7071 | 279.7131 | 260.0089 | 252.4237 | 262.9414 | 237.5191 | 225.0574 | 261.5634
1194.5677 | 1103.5677 | 333.5467 | 279.7375 | 260.026 | 252.4474 | 262.9641 | 237.5701 | 225.098 | 261.5614
1195.5691 | 1104.5691 | 333.4577 | 279.8016 | 260.1105 | 252.4729 | 263.017 | 237.6044 | 225.1377 | 261.5882
1196.5606 | 1105.5606 | 333.3218 | 279.8553 | 260.2228 | 252.493 | 263.0636 | 237.6544 | 225.178 | 261.5961
1197.562 | 1106.562 | 333.169 | 279.9006 | 260.3243 | 252.5049 | 263.1099 | 237.6954 | 225.221 | 261.6291
1198.5634 | 1107.5634 | 333.0472 | 279.9399 | 260.423 | 252.5296 | 263.1375 | 237.7395 | 225.26 | 261.6306
1199.5649 | 1108.5649 | 333.0445 | 280.0178 | 260.4822 | 252.5435 | 263.1791 | 237.7573 | 225.3074 | 261.645
1200.5663 | 1109.5663 | 333.1105 | 280.0177 | 260.5148 | 252.5606 | 263.1982 | 237.7985 | 225.345 | 261.6523
1201.5678 | 1110.5678 | 333.0841 | 279.9372 | 260.5368 | 252.5773 | 263.2321 | 237.8094 | 225.3894 | 261.6622
1202.5592 | 1111.5592 | 333.0283 | 280.0364 | 260.56 | 252.5928 | 263.2674 | 237.8364 | 225.4359 | 261.6803
1203.5606 | 1112.5606 | 333.0506 | 280.1216 | 260.5665 | 252.6183 | 263.3023 | 237.8783 | 225.4749 | 261.7024
1204.5621 | 1113.5621 | 333.0131 | 280.1109 | 260.5602 | 252.6326 | 263.3308 | 237.9049 | 225.5143 | 261.7348
1205.5635 | 1114.5635 | 332.9442 | 280.1221 | 260.5963 | 252.6597 | 263.3789 | 237.9378 | 225.5601 | 261.7377
1206.565 | 1115.565 | 332.7556 | 280.0655 | 260.6709 | 252.6779 | 263.4035 | 237.9901 | 225.5951 | 261.7843
1207.5664 | 1116.5664 | 332.5547 | 280.1454 | 260.7314 | 252.6907 | 263.4371 | 238.0579 | 225.6386 | 261.7472
1208.5678 | 1117.5678 | 332.3098 | 280.1264 | 260.8145 | 252.7134 | 263.4547 | 238.1194 | 225.6727 | 261.7583
1209.5593 | 1118.5593 | 332.0562 | 280.1136 | 260.863 | 252.738 | 263.4524 | 238.1785 | 225.7037 | 261.7543
1210.5607 | 1119.5607 | 331.868 | 280.1639 | 260.9077 | 252.7626 | 263.4636 | 238.2328 | 225.7425 | 261.7646
1211.5621 | 1120.5621 | 331.7211 | 280.0932 | 260.9468 | 252.7843 | 263.4694 | 238.2914 | 225.7751 | 261.7179
1212.5636 | 1121.5636 | 331.5555 | 280.0535 | 260.9506 | 252.8041 | 263.4739 | 238.3516 | 225.8191 | 261.6772
1213.565 | 1122.565 | 331.4478 | 280.0771 | 260.9206 | 252.8297 | 263.4982 | 238.3771 | 225.8565 | 261.7026
1214.5665 | 1123.5665 | 331.351 | 280.0638 | 260.9219 | 252.8463 | 263.5149 | 238.418 | 225.8936 | 261.7028
1215.5679 | 1124.5679 | 331.3069 | 279.9502 | 260.9281 | 252.8633 | 263.5176 | 238.4667 | 225.9286 | 261.7052
1216.5693 | 1125.5693 | 331.281 | 279.9925 | 260.9425 | 252.8897 | 263.5495 | 238.5216 | 225.9612 | 261.715
1217.5608 | 1126.5608 | 331.3119 | 279.9777 | 260.9241 | 252.9073 | 263.5723 | 238.5565 | 226.0036 | 261.7341
1218.5622 | 1127.5622 | 331.405 | 279.9526 | 260.9059 | 252.9231 | 263.5836 | 238.5957 | 226.0364 | 261.7354
1219.5636 | 1128.5636 | 331.4002 | 279.9788 | 260.891 | 252.9357 | 263.6039 | 238.6322 | 226.0693 | 261.7422
1220.5651 | 1129.5651 | 331.3127 | 280.0034 | 260.9387 | 252.9541 | 263.6296 | 238.6728 | 226.1014 | 261.7826
1221.5665 | 1130.5665 | 331.2735 | 279.9636 | 261.0158 | 252.9698 | 263.6558 | 238.6809 | 226.1405 | 261.8081
1222.568 | 1131.568 | 331.3542 | 279.9637 | 261.0461 | 252.9838 | 263.6781 | 238.7147 | 226.1775 | 261.8159
1223.5594 | 1132.5594 | 331.3826 | 280.0118 | 261.0539 | 252.9989 | 263.7081 | 238.7526 | 226.2142 | 261.8487
1224.5608 | 1133.5608 | 331.3148 | 280.0201 | 261.026 | 253.0145 | 263.7437 | 238.7937 | 226.2527 | 261.8617
1225.5623 | 1134.5623 | 331.3926 | 279.9787 | 261.0665 | 253.0364 | 263.7673 | 238.8522 | 226.2852 | 261.8505
1226.5637 | 1135.5637 | 331.4959 | 280.0471 | 261.0965 | 253.0419 | 263.7914 | 238.8988 | 226.3279 | 261.8208
1227.5652 | 1136.5652 | 331.6391 | 280.0415 | 261.1448 | 253.0575 | 263.8112 | 238.9395 | 226.3577 | 261.841
1228.5666 | 1137.5666 | 331.7203 | 280.0996 | 261.1914 | 253.0771 | 263.8032 | 238.9715 | 226.3944 | 261.8734
1229.568 | 1138.568 | 331.818 | 280.1146 | 261.2397 | 253.0928 | 263.8264 | 238.9884 | 226.4341 | 261.9074
1230.5695 | 1139.5695 | 331.8966 | 280.2018 | 261.2608 | 253.1116 | 263.8508 | 239.0437 | 226.464 | 261.9332
1231.5609 | 1140.5609 | 331.8579 | 280.269 | 261.2751 | 253.1314 | 263.8669 | 239.0717 | 226.5017 | 261.9591
1232.5623 | 1141.5623 | 331.9051 | 280.3633 | 261.2955 | 253.1525 | 263.8856 | 239.1196 | 226.539 | 261.9893
1233.5638 | 1142.5638 | 332.0116 | 280.3847 | 261.2906 | 253.1631 | 263.8913 | 239.1574 | 226.5779 | 262.0204
1234.5652 | 1143.5652 | 332.0884 | 280.3915 | 261.2963 | 253.1815 | 263.9024 | 239.1971 | 226.6078 | 262.0455
1235.5667 | 1144.5667 | 332.0009 | 280.415 | 261.2918 | 253.2032 | 263.9256 | 239.2206 | 226.643 | 262.0561
1236.5681 | 1145.5681 | 332.0184 | 280.3732 | 261.2917 | 253.2181 | 263.9495 | 239.24 | 226.6808 | 262.0842
1237.5695 | 1146.5695 | 332.133 | 280.3547 | 261.2599 | 253.2342 | 263.9793 | 239.2881 | 226.7177 | 262.1164
1238.561 | 1147.561 | 332.1234 | 280.4631 | 261.172 | 253.2563 | 264.0085 | 239.31 | 226.7551 | 262.1061
1239.5624 | 1148.5624 | 332.1104 | 280.3041 | 261.103 | 253.2768 | 264.0438 | 239.3714 | 226.7979 | 262.1308
1240.5638 | 1149.5638 | 332.0563 | 280.3863 | 261.0389 | 253.2955 | 264.0566 | 239.4253 | 226.8288 | 262.1356
1241.5653 | 1150.5653 | 332.0468 | 280.2714 | 261.0027 | 253.3182 | 264.0892 | 239.458 | 226.8677 | 262.1531
1242.5667 | 1151.5667 | 332.0414 | 280.3096 | 260.9857 | 253.3461 | 264.1249 | 239.5026 | 226.9006 | 262.1767
1243.5682 | 1152.5682 | 332.0892 | 280.3785 | 260.9701 | 253.3621 | 264.1369 | 239.559 | 226.9407 | 262.1637
1244.5596 | 1153.5596 | 332.2797 | 280.309 | 260.9818 | 253.3876 | 264.1555 | 239.6016 | 226.9769 | 262.1944
1245.561 | 1154.561 | 332.3997 | 280.2773 | 261.0035 | 253.4099 | 264.1933 | 239.6339 | 227.0266 | 262.2043
1246.5625 | 1155.5625 | 332.445 | 280.2864 | 261.0585 | 253.4343 | 264.2125 | 239.6573 | 227.0624 | 262.2342
1247.5639 | 1156.5639 | 332.4099 | 280.3655 | 261.0775 | 253.4689 | 264.2499 | 239.701 | 227.1048 | 262.2638
1248.5653 | 1157.5653 | 332.4193 | 280.434 | 261.1359 | 253.4989 | 264.2835 | 239.7521 | 227.1483 | 262.2696
1249.5668 | 1158.5668 | 332.4234 | 280.5007 | 261.2182 | 253.5248 | 264.3039 | 239.7973 | 227.1851 | 262.2842
1250.5582 | 1159.5582 | 332.3308 | 280.5598 | 261.2499 | 253.5533 | 264.3229 | 239.8433 | 227.2253 | 262.3004
1251.5597 | 1160.5597 | 332.2177 | 280.6592 | 261.2023 | 253.5819 | 264.3327 | 239.8928 | 227.2658 | 262.3119
1252.5611 | 1161.5611 | 332.2274 | 280.5551 | 261.3055 | 253.6143 | 264.3547 | 239.9275 | 227.3049 | 262.3185
1253.5625 | 1162.5625 | 332.1204 | 280.6109 | 261.43 | 253.6419 | 264.3869 | 239.9885 | 227.3437 | 262.3474
1254.564 | 1163.564 | 332.0838 | 280.6623 | 261.5085 | 253.6783 | 264.4131 | 240.0105 | 227.3724 | 262.3388
1255.5654 | 1164.5654 | 332.0475 | 280.7659 | 261.4856 | 253.7191 | 264.4422 | 240.0525 | 227.4061 | 262.3624
1256.5669 | 1165.5669 | 332.0956 | 280.7863 | 261.4511 | 253.7459 | 264.4724 | 240.0744 | 227.44 | 262.3916
1257.5683 | 1166.5683 | 332.1031 | 280.8026 | 261.3994 | 253.7797 | 264.5006 | 240.1193 | 227.4841 | 262.3849
1258.5597 | 1167.5597 | 332.1417 | 280.8146 | 261.4634 | 253.8096 | 264.5307 | 240.169 | 227.5127 | 262.4034
1259.5612 | 1168.5612 | 332.1383 | 280.8448 | 261.5851 | 253.8484 | 264.5599 | 240.2091 | 227.5488 | 262.4028
1260.5626 | 1169.5626 | 332.1293 | 280.8445 | 261.7019 | 253.8841 | 264.5864 | 240.25 | 227.578 | 262.4078
1261.564 | 1170.564 | 332.1366 | 280.8564 | 261.7809 | 253.9163 | 264.6119 | 240.2884 | 227.6068 | 262.43
1262.5655 | 1171.5655 | 332.1159 | 280.8527 | 261.8491 | 253.9533 | 264.6433 | 240.3617 | 227.6392 | 262.4358
1263.5669 | 1172.5669 | 332.0733 | 280.8943 | 261.9074 | 253.9814 | 264.6555 | 240.434 | 227.6643 | 262.4307
1264.5684 | 1173.5684 | 332.0904 | 280.7458 | 261.9444 | 254.0162 | 264.6864 | 240.5142 | 227.6878 | 262.3977
1265.5698 | 1174.5698 | 332.2103 | 280.8012 | 261.9556 | 254.0284 | 264.7682 | 240.6758 | 227.6947 | 262.3627
1266.5612 | 1175.5612 | 332.1846 | 280.9089 | 261.9092 | 254.0635 | 264.72 | 240.6421 | 227.7397 | 262.387
1267.5627 | 1176.5627 | 332.0929 | 280.9102 | 261.918 | 254.0913 | 264.691 | 240.6406 | 227.769 | 262.4371
1268.5641 | 1177.5641 | 332.0061 | 280.8041 | 261.9885 | 254.0829 | 264.9341 | 240.983 | 227.7345 | 262.282
1269.5655 | 1178.5655 | 332.0375 | 280.9427 | 261.982 | 254.13 | 264.7745 | 240.83 | 227.8112 | 262.3733
1270.567 | 1179.567 | 332.1412 | 281.007 | 261.7953 | 254.156 | 264.6964 | 240.7803 | 227.8516 | 262.4703
1271.5684 | 1180.5684 | 332.1994 | 281.1315 | 261.7158 | 254.1781 | 264.7096 | 240.7875 | 227.878 | 262.4592
1272.5699 | 1181.5699 | 332.2792 | 281.1826 | 261.6773 | 254.1861 | 264.7394 | 240.7934 | 227.91 | 262.4919
1273.5613 | 1182.5613 | 332.3636 | 281.2265 | 261.6506 | 254.2043 | 264.7593 | 240.8366 | 227.9395 | 262.502
1274.5627 | 1183.5627 | 332.2986 | 281.1784 | 261.6287 | 254.2278 | 264.779 | 240.8595 | 227.9604 | 262.5117
1275.5642 | 1184.5642 | 332.2254 | 281.1866 | 261.6333 | 254.2454 | 264.8015 | 240.898 | 227.9825 | 262.4796
1276.5656 | 1185.5656 | 332.2238 | 281.1721 | 261.6736 | 254.2637 | 264.8043 | 240.9541 | 228.0069 | 262.4854
1277.5671 | 1186.5671 | 332.2122 | 281.232 | 261.7003 | 254.2846 | 264.7968 | 240.9849 | 228.0308 | 262.4971
1278.5685 | 1187.5685 | 332.1404 | 281.3041 | 261.7277 | 254.3083 | 264.8095 | 241.0274 | 228.0541 | 262.5056
1279.5599 | 1188.5599 | 332.1944 | 281.4104 | 261.7373 | 254.324 | 264.8107 | 241.0507 | 228.0792 | 262.5385
1280.5614 | 1189.5614 | 332.2098 | 281.3769 | 261.7619 | 254.3379 | 264.8299 | 241.0386 | 228.0928 | 262.5381
1281.5628 | 1190.5628 | 332.223 | 281.3877 | 261.7764 | 254.3572 | 264.8344 | 241.0224 | 228.1163 | 262.5951
1282.5642 | 1191.5642 | 332.3292 | 281.4507 | 261.8099 | 254.3749 | 264.8471 | 241.0637 | 228.1368 | 262.5815
1283.5657 | 1192.5657 | 332.4488 | 281.5817 | 261.8456 | 254.3938 | 264.8471 | 241.103 | 228.1646 | 262.6145
1284.5671 | 1193.5671 | 332.6093 | 281.7291 | 261.8696 | 254.4135 | 264.8673 | 241.1423 | 228.1831 | 262.6189
1285.5686 | 1194.5686 | 332.5772 | 281.7303 | 261.8827 | 254.4357 | 264.8762 | 241.1845 | 228.1968 | 262.6591
1286.56 | 1195.56 | 332.5445 | 281.7888 | 261.8873 | 254.4558 | 264.8997 | 241.2265 | 228.2192 | 262.67
1287.5614 | 1196.5614 | 332.4921 | 281.825 | 261.9032 | 254.4802 | 264.9032 | 241.2742 | 228.2477 | 262.6887
1288.5629 | 1197.5629 | 332.3778 | 281.9165 | 261.9397 | 254.5028 | 264.9089 | 241.2827 | 228.2667 | 262.6976
1289.5643 | 1198.5643 | 332.3989 | 281.9681 | 261.9734 | 254.523 | 264.9414 | 241.3273 | 228.2845 | 262.6823
1290.5657 | 1199.5657 | 332.4407 | 282.0271 | 261.9679 | 254.5486 | 264.9452 | 241.3573 | 228.3135 | 262.7151
1291.5672 | 1200.5672 | 332.4803 | 282.0563 | 261.98 | 254.5717 | 264.967 | 241.3702 | 228.33 | 262.721
1292.5686 | 1201.5686 | 332.4662 | 282.1414 | 261.9922 | 254.606 | 264.9872 | 241.3959 | 228.3552 | 262.7545
1293.56 | 1202.56 | 332.5189 | 282.2182 | 262.0036 | 254.624 | 265.0121 | 241.4166 | 228.3727 | 262.7633
1294.5615 | 1203.5615 | 332.5865 | 282.1951 | 262.0135 | 254.6442 | 265.0317 | 241.4515 | 228.4068 | 262.8194
1295.5629 | 1204.5629 | 332.5064 | 282.2227 | 262.025 | 254.6721 | 265.0497 | 241.4989 | 228.4282 | 262.8264
1296.5644 | 1205.5644 | 332.4144 | 282.2598 | 262.0399 | 254.7003 | 265.0742 | 241.543 | 228.4538 | 262.8279
1297.5658 | 1206.5658 | 332.3139 | 282.348 | 262.0697 | 254.7402 | 265.085 | 241.5916 | 228.4723 | 262.8648
1298.5672 | 1207.5672 | 332.3463 | 282.3337 | 262.1549 | 254.7645 | 265.1328 | 241.6782 | 228.4896 | 262.8366
1299.5587 | 1208.5587 | 332.2921 | 282.3493 | 262.1564 | 254.793 | 265.1106 | 241.663 | 228.5203 | 262.8759
1300.5601 | 1209.5601 | 332.2094 | 282.3194 | 262.1927 | 254.8315 | 265.1599 | 241.7352 | 228.5407 | 262.6911
1301.5616 | 1210.5616 | 332.2307 | 282.2897 | 262.2029 | 254.852 | 265.1708 | 241.7497 | 228.5719 | 262.8445
1302.563 | 1211.563 | 332.2087 | 282.2063 | 262.2092 | 254.8878 | 265.1581 | 241.7614 | 228.596 | 262.8335
1303.5644 | 1212.5644 | 332.1647 | 282.2201 | 262.2207 | 254.924 | 265.1648 | 241.8041 | 228.6261 | 262.8177
1304.5659 | 1213.5659 | 332.1202 | 282.1979 | 262.2495 | 254.9446 | 265.201 | 241.8772 | 228.653 | 262.7572
1305.5673 | 1214.5673 | 332.0648 | 282.267 | 262.2648 | 254.974 | 265.1999 | 241.9192 | 228.6833 | 262.7629
1306.5688 | 1215.5688 | 332.0012 | 282.2687 | 262.2907 | 255.0113 | 265.1883 | 241.9585 | 228.7175 | 262.7548
1307.5702 | 1216.5702 | 331.9966 | 282.2103 | 262.3313 | 255.0351 | 265.195 | 242.0342 | 228.7375 | 262.7617
1308.5616 | 1217.5616 | 332.0675 | 282.2391 | 262.3685 | 255.0711 | 265.1979 | 242.0998 | 228.7738 | 262.7737
1309.5631 | 1218.5631 | 332.1425 | 282.2565 | 262.3797 | 255.0893 | 265.152 | 242.1445 | 228.8017 | 262.7354
1310.5645 | 1219.5645 | 332.1517 | 282.1923 | 262.4062 | 255.1073 | 265.1352 | 242.2122 | 228.831 | 262.7466
1311.5659 | 1220.5659 | 332.1223 | 282.2574 | 262.4091 | 255.1183 | 265.0931 | 242.258 | 228.8664 | 262.7303
1312.5674 | 1221.5674 | 332.1101 | 282.2129 | 262.4333 | 255.1398 | 265.063 | 242.3059 | 228.9079 | 262.7394
1313.5688 | 1222.5688 | 332.2316 | 282.2442 | 262.4375 | 255.159 | 265.0387 | 242.3685 | 228.9415 | 262.7338
1314.5602 | 1223.5602 | 332.298 | 282.3339 | 262.4643 | 255.1608 | 265.0522 | 242.4075 | 228.9826 | 262.7589
1315.5617 | 1224.5617 | 332.3676 | 282.3761 | 262.476 | 255.1766 | 265.0489 | 242.4348 | 229.0201 | 262.6081
1316.5631 | 1225.5631 | 332.3817 | 282.4524 | 262.476 | 255.1799 | 265.0376 | 242.453 | 229.0669 | 262.7781
1317.5646 | 1226.5646 | 332.4107 | 282.547 | 262.4731 | 255.1854 | 265.0582 | 242.4786 | 229.1019 | 262.8228
1318.566 | 1227.566 | 332.4921 | 282.6566 | 262.5097 | 255.208 | 265.0712 | 242.5065 | 229.1436 | 262.8365
1319.5674 | 1228.5674 | 332.651 | 282.6297 | 262.5227 | 255.2091 | 265.0884 | 242.5309 | 229.1762 | 262.8425
1320.5689 | 1229.5689 | 332.7603 | 282.6919 | 262.5309 | 255.2159 | 265.1114 | 242.5419 | 229.2072 | 262.8753
1321.5703 | 1230.5703 | 332.8514 | 282.7024 | 262.5485 | 255.2265 | 265.1299 | 242.5531 | 229.2414 | 262.9368
1322.5618 | 1231.5618 | 332.9733 | 282.7289 | 262.5739 | 255.2315 | 265.1645 | 242.6068 | 229.2748 | 262.9032
1323.5632 | 1232.5632 | 333.0701 | 282.7958 | 262.5945 | 255.2414 | 265.1925 | 242.6447 | 229.3051 | 262.9523
1324.5646 | 1233.5646 | 333.1271 | 282.7308 | 262.6329 | 255.2522 | 265.2231 | 242.6798 | 229.3317 | 262.9682
1325.5661 | 1234.5661 | 333.0336 | 282.7661 | 262.6738 | 255.2616 | 265.2392 | 242.7338 | 229.3596 | 262.9848
1326.5675 | 1235.5675 | 333.0637 | 282.7656 | 262.6831 | 255.2739 | 265.2719 | 242.7792 | 229.3824 | 263.0126
1327.569 | 1236.569 | 332.9811 | 282.7519 | 262.6964 | 255.2881 | 265.2937 | 242.8343 | 229.4034 | 263.0109
1328.5604 | 1237.5604 | 332.8943 | 282.7701 | 262.7301 | 255.3043 | 265.3309 | 242.9021 | 229.4283 | 262.9905
1329.5618 | 1238.5618 | 332.7949 | 282.646 | 262.7396 | 255.3186 | 265.3392 | 242.9421 | 229.451 | 263.0341
1330.5633 | 1239.5633 | 332.8092 | 282.6571 | 262.7655 | 255.3483 | 265.359 | 242.9745 | 229.472 | 263.0741
1331.5647 | 1240.5647 | 332.8354 | 282.6637 | 262.7875 | 255.3683 | 265.3863 | 243.0009 | 229.4948 | 263.0656
1332.5661 | 1241.5661 | 332.8053 | 282.8089 | 262.8287 | 255.3918 | 265.3984 | 243.043 | 229.5144 | 263.0974
1333.5676 | 1242.5676 | 332.8071 | 282.8785 | 262.8453 | 255.4157 | 265.4049 | 243.1133 | 229.5356 | 263.1313
1334.569 | 1243.569 | 332.7641 | 282.8519 | 262.8658 | 255.4356 | 265.4338 | 243.1437 | 229.56 | 263.1371
1335.5604 | 1244.5604 | 332.6547 | 282.8948 | 262.871 | 255.4548 | 265.4529 | 243.1656 | 229.5936 | 263.1369
1336.5619 | 1245.5619 | 332.711 | 282.8432 | 262.914 | 255.4642 | 265.4751 | 243.2127 | 229.6218 | 263.1202
1337.5633 | 1246.5633 | 332.7966 | 282.9146 | 262.9251 | 255.4883 | 265.503 | 243.2502 | 229.6471 | 263.1129
1338.5648 | 1247.5648 | 332.8186 | 282.9921 | 262.9321 | 255.4908 | 265.5168 | 243.2641 | 229.6729 | 263.0802
1339.5662 | 1248.5662 | 332.833 | 283.0343 | 262.9527 | 255.5085 | 265.4907 | 243.291 | 229.7065 | 263.0866
1340.5676 | 1249.5676 | 332.8553 | 283.1246 | 262.9752 | 255.5055 | 265.4943 | 243.309 | 229.7388 | 263.0508
1341.5591 | 1250.5591 | 332.9642 | 283.1366 | 262.9859 | 255.5179 | 265.4777 | 243.3284 | 229.7728 | 263.0649
1342.5605 | 1251.5605 | 333.0964 | 283.2053 | 263.0147 | 255.5185 | 265.4777 | 243.3761 | 229.8061 | 263.0877
1343.5619 | 1252.5619 | 333.1514 | 283.2235 | 263.0263 | 255.522 | 265.5018 | 243.4121 | 229.8429 | 263.1063
1344.5634 | 1253.5634 | 333.2006 | 283.1969 | 263.0194 | 255.5377 | 265.5107 | 243.4363 | 229.8822 | 263.1005
1345.5648 | 1254.5648 | 333.2132 | 283.2206 | 263.04 | 255.5432 | 265.5357 | 243.4515 | 229.9159 | 263.1626
1346.5663 | 1255.5663 | 333.2064 | 283.2862 | 263.0558 | 255.5709 | 265.5627 | 243.4457 | 229.955 | 263.1628
1347.5677 | 1256.5677 | 333.2703 | 283.342 | 263.0777 | 255.5859 | 265.606 | 243.4634 | 229.9846 | 263.1959
1348.5691 | 1257.5691 | 333.2723 | 283.3881 | 263.0783 | 255.6054 | 265.6429 | 243.4658 | 230.0211 | 263.2172
1349.5606 | 1258.5606 | 333.2259 | 283.3905 | 263.1052 | 255.6221 | 265.6712 | 243.4855 | 230.0515 | 263.2388
1350.562 | 1259.562 | 333.2251 | 283.4389 | 263.1366 | 255.6426 | 265.7011 | 243.5204 | 230.0804 | 263.2538
1351.5635 | 1260.5635 | 333.2291 | 283.5013 | 263.1474 | 255.6584 | 265.7202 | 243.5471 | 230.1092 | 263.215
1352.5649 | 1261.5649 | 333.1525 | 283.4918 | 263.1691 | 255.6767 | 265.7462 | 243.5812 | 230.1355 | 263.2404
1353.5663 | 1262.5663 | 333.033 | 283.5302 | 263.2083 | 255.6996 | 265.7611 | 243.6407 | 230.1574 | 263.2313
1354.5678 | 1263.5678 | 332.8603 | 283.4736 | 263.2265 | 255.7231 | 265.7889 | 243.6579 | 230.1868 | 263.2724
1355.5592 | 1264.5592 | 332.7743 | 283.3682 | 263.2423 | 255.747 | 265.806 | 243.6707 | 230.2042 | 263.2671
1356.5606 | 1265.5606 | 332.5736 | 283.4125 | 263.2667 | 255.7633 | 265.8211 | 243.7169 | 230.2327 | 263.2607
1357.5621 | 1266.5621 | 332.4818 | 283.3171 | 263.2664 | 255.7857 | 265.8557 | 243.7717 | 230.2499 | 263.2495
1358.5635 | 1267.5635 | 332.5066 | 283.1996 | 263.2846 | 255.8066 | 265.8753 | 243.8136 | 230.2721 | 263.2255
1359.565 | 1268.565 | 332.4823 | 283.0384 | 263.2995 | 255.8293 | 265.8944 | 243.8681 | 230.2936 | 263.2544
1360.5664 | 1269.5664 | 332.4941 | 282.9364 | 263.3196 | 255.8518 | 265.9077 | 243.9208 | 230.3117 | 263.2055
1361.5678 | 1270.5678 | 332.4376 | 282.91 | 263.3483 | 255.8749 | 265.8963 | 243.9664 | 230.3386 | 263.2276
1362.5693 | 1271.5693 | 332.304 | 282.9485 | 263.3651 | 255.8908 | 265.87 | 244.0172 | 230.3554 | 263.2101
1363.5607 | 1272.5607 | 332.2513 | 282.9634 | 263.3755 | 255.9053 | 265.8666 | 244.0482 | 230.3813 | 263.2441
1364.5621 | 1273.5621 | 332.169 | 282.9461 | 263.394 | 255.9213 | 265.8467 | 244.0805 | 230.397 | 263.2232
1365.5636 | 1274.5636 | 332.1074 | 282.9741 | 263.4152 | 255.9261 | 265.8457 | 244.1218 | 230.4218 | 263.2024
1366.565 | 1275.565 | 332.0985 | 283.0321 | 263.4377 | 255.9265 | 265.8344 | 244.1624 | 230.4411 | 263.1797
1367.5665 | 1276.5665 | 332.0597 | 282.9973 | 263.4543 | 255.9218 | 265.8237 | 244.1963 | 230.4569 | 263.1967
1368.5679 | 1277.5679 | 332.0575 | 282.9969 | 263.4641 | 255.9398 | 265.8435 | 244.233 | 230.4853 | 263.2258
1369.5693 | 1278.5693 | 332.0892 | 283.0546 | 263.4905 | 255.9498 | 265.8669 | 244.2871 | 230.5093 | 263.2213
1370.5608 | 1279.5608 | 332.1288 | 282.9815 | 263.5146 | 255.9582 | 265.8706 | 244.3222 | 230.5317 | 263.2136
1371.5622 | 1280.5622 | 332.1476 | 282.9871 | 263.516 | 255.9706 | 265.8965 | 244.3683 | 230.5547 | 263.2204
1372.5636 | 1281.5636 | 332.2003 | 282.982 | 263.5282 | 255.9854 | 265.9168 | 244.3963 | 230.5753 | 263.2405
1373.5651 | 1282.5651 | 332.3006 | 282.9537 | 263.5484 | 256.0052 | 265.9396 | 244.4385 | 230.6022 | 263.2588
1374.5665 | 1283.5665 | 332.3601 | 283.0733 | 263.5556 | 256.0141 | 265.9647 | 244.4705 | 230.6268 | 263.2852
1375.568 | 1284.568 | 332.4115 | 282.8456 | 263.5854 | 256.0316 | 266.0171 | 244.5159 | 230.6497 | 263.3042
1376.5594 | 1285.5594 | 332.4256 | 282.8314 | 263.594 | 256.0542 | 266.0424 | 244.5532 | 230.6758 | 263.3016
1377.5608 | 1286.5608 | 332.3647 | 282.856 | 263.6041 | 256.0754 | 266.0877 | 244.581 | 230.6937 | 263.329
1378.5623 | 1287.5623 | 332.3072 | 282.8272 | 263.62 | 256.0834 | 266.1176 | 244.5902 | 230.7155 | 263.3306
1379.5637 | 1288.5637 | 332.3478 | 282.8474 | 263.6446 | 256.116 | 266.1439 | 244.6366 | 230.746 | 263.3279
1380.5652 | 1289.5652 | 332.3387 | 282.839 | 263.6662 | 256.129 | 266.1534 | 244.6697 | 230.776 | 263.3271
1381.5666 | 1290.5666 | 332.4031 | 282.7972 | 263.6717 | 256.1518 | 266.1787 | 244.6832 | 230.8035 | 263.3443
1382.568 | 1291.568 | 332.4968 | 282.844 | 263.6771 | 256.1699 | 266.1946 | 244.6753 | 230.832 | 263.3388
1383.5595 | 1292.5595 | 332.5803 | 282.8972 | 263.7146 | 256.182 | 266.2069 | 244.6821 | 230.8563 | 263.3599
1384.5609 | 1293.5609 | 332.6668 | 282.9821 | 263.7368 | 256.1966 | 266.2188 | 244.7032 | 230.8868 | 263.3786
1385.5623 | 1294.5623 | 332.7645 | 283.0213 | 263.7439 | 256.2105 | 266.235 | 244.7438 | 230.9195 | 263.4113
1386.5638 | 1295.5638 | 332.8502 | 283.0337 | 263.7561 | 256.2342 | 266.2458 | 244.7662 | 230.9435 | 263.4177
1387.5652 | 1296.5652 | 332.9145 | 283.1056 | 263.7715 | 256.2541 | 266.2609 | 244.7787 | 230.9704 | 263.4371
1388.5667 | 1297.5667 | 332.8748 | 283.0754 | 263.7911 | 256.2764 | 266.274 | 244.7872 | 231.0005 | 263.4714
1389.5681 | 1298.5681 | 332.7647 | 283.044 | 263.8164 | 256.3031 | 266.2925 | 244.8056 | 231.0299 | 263.4624
1390.5695 | 1299.5695 | 332.6526 | 282.9631 | 263.8179 | 256.3301 | 266.3152 | 244.8153 | 231.047 | 263.4445
1391.561 | 1300.561 | 332.6575 | 282.9117 | 263.8309 | 256.3602 | 266.3126 | 244.82 | 231.0685 | 263.4862
1392.5624 | 1301.5624 | 332.6017 | 282.9202 | 263.8512 | 256.3813 | 266.3296 | 244.8326 | 231.0867 | 263.4818
1393.5638 | 1302.5638 | 332.6117 | 283.0079 | 263.8661 | 256.3984 | 266.3417 | 244.8599 | 231.1136 | 263.4759
1394.5653 | 1303.5653 | 332.5783 | 283.0665 | 263.8929 | 256.4281 | 266.3461 | 244.8775 | 231.1389 | 263.4792
1395.5667 | 1304.5667 | 332.5815 | 283.0599 | 263.9173 | 256.4572 | 266.359 | 244.8948 | 231.1589 | 263.4858
1396.5682 | 1305.5682 | 332.5768 | 283.1018 | 263.9415 | 256.4679 | 266.3598 | 244.9262 | 231.1789 | 263.4822
1397.5596 | 1306.5596 | 332.671 | 283.1179 | 263.9515 | 256.4859 | 266.3606 | 244.9617 | 231.2059 | 263.469
1398.561 | 1307.561 | 332.7468 | 283.181 | 263.9595 | 256.5114 | 266.3755 | 244.9691 | 231.222 | 263.5082
1399.5625 | 1308.5625 | 332.6718 | 283.2911 | 263.9812 | 256.5217 | 266.3867 | 244.9907 | 231.2468 | 263.5091
1400.5639 | 1309.5639 | 332.6682 | 283.1969 | 263.9909 | 256.5313 | 266.4011 | 245.0198 | 231.2756 | 263.4981
1401.5654 | 1310.5654 | 332.7661 | 283.258 | 264.0133 | 256.5456 | 266.4227 | 245.04 | 231.2992 | 263.538
1402.5668 | 1311.5668 | 332.8807 | 283.3532 | 264.0306 | 256.5632 | 266.4417 | 245.0744 | 231.3184 | 263.5642
1403.5682 | 1312.5682 | 332.7782 | 283.345 | 264.0611 | 256.5792 | 266.473 | 245.1213 | 231.3446 | 263.5942
1404.5697 | 1313.5697 | 332.6871 | 283.4115 | 264.0678 | 256.6075 | 266.4995 | 245.1346 | 231.3689 | 263.5834
1405.5611 | 1314.5611 | 332.5087 | 283.4586 | 264.0779 | 256.6242 | 266.5201 | 245.1531 | 231.3945 | 263.5881
1406.5625 | 1315.5625 | 332.5088 | 283.3166 | 264.0977 | 256.6441 | 266.5394 | 245.19 | 231.4106 | 263.6054
1407.564 | 1316.564 | 332.509 | 283.3873 | 264.1091 | 256.6698 | 266.5669 | 245.2149 | 231.4261 | 263.6081
1408.5654 | 1317.5654 | 332.5687 | 283.4257 | 264.1131 | 256.6948 | 266.5969 | 245.2637 | 231.4483 | 263.6123
1409.5669 | 1318.5669 | 332.5226 | 283.4169 | 264.146 | 256.717 | 266.671 | 245.357 | 231.4559 | 263.5923
1410.5683 | 1319.5683 | 332.5088 | 283.4306 | 264.1442 | 256.7491 | 266.6515 | 245.3317 | 231.4813 | 263.6611
1411.5597 | 1320.5597 | 332.4865 | 283.3757 | 264.1627 | 256.7696 | 266.698 | 245.3575 | 231.5046 | 263.686
1412.5612 | 1321.5612 | 332.424 | 283.3961 | 264.1975 | 256.7956 | 266.7304 | 245.397 | 231.5219 | 263.6597
1413.5626 | 1322.5626 | 332.3977 | 283.3863 | 264.2098 | 256.8194 | 266.7519 | 245.396 | 231.548 | 263.6941
1414.564 | 1323.564 | 332.4589 | 283.4561 | 264.2524 | 256.8376 | 266.773 | 245.4314 | 231.5739 | 263.6842
1415.5655 | 1324.5655 | 332.5776 | 283.5318 | 264.3345 | 256.855 | 266.7876 | 245.4696 | 231.5927 | 263.702
1416.5669 | 1325.5669 | 332.7504 | 283.5701 | 264.3755 | 256.8823 | 266.7831 | 245.4986 | 231.6221 | 263.6842
1417.5684 | 1326.5684 | 332.8113 | 283.5801 | 264.4079 | 256.9136 | 266.7961 | 245.5346 | 231.6434 | 263.6819
1418.5698 | 1327.5698 | 332.7582 | 283.6344 | 264.4181 | 256.9386 | 266.7928 | 245.567 | 231.6689 | 263.6926
1419.5612 | 1328.5612 | 332.7657 | 283.6488 | 264.4541 | 256.9662 | 266.7975 | 245.6011 | 231.6992 | 263.7241
1420.5627 | 1329.5627 | 332.7885 | 283.6362 | 264.4628 | 256.9893 | 266.7997 | 245.6148 | 231.7234 | 263.7368
1421.5641 | 1330.5641 | 332.7081 | 283.5451 | 264.4706 | 257.0134 | 266.7965 | 245.6638 | 231.7462 | 263.7275
1422.5655 | 1331.5655 | 332.7993 | 283.3043 | 264.4967 | 257.0392 | 266.7889 | 245.7052 | 231.771 | 263.7413
1423.567 | 1332.567 | 332.7725 | 283.2686 | 264.5134 | 257.0637 | 266.8111 | 245.7537 | 231.7912 | 263.7487
1424.5584 | 1333.5584 | 332.7254 | 283.0755 | 264.5252 | 257.0913 | 266.8105 | 245.8045 | 231.8055 | 263.714
1425.5599 | 1334.5599 | 332.7223 | 283.1168 | 264.5409 | 257.1308 | 266.833 | 245.8521 | 231.8248 | 263.6918
1426.5613 | 1335.5613 | 332.649 | 283.0791 | 264.5518 | 257.1559 | 266.8583 | 245.9146 | 231.8479 | 263.6931
1427.5627 | 1336.5627 | 332.5085 | 283.1487 | 264.5586 | 257.1899 | 266.8739 | 245.978 | 231.8715 | 263.694
1428.5642 | 1337.5642 | 332.4528 | 282.9832 | 264.572 | 257.2162 | 266.893 | 246.016 | 231.8885 | 263.6681
1429.5656 | 1338.5656 | 332.347 | 283.0238 | 264.5782 | 257.239 | 266.894 | 246.0587 | 231.908 | 263.6794
1430.5671 | 1339.5671 | 332.1812 | 283.094 | 264.5951 | 257.2632 | 266.8892 | 246.1053 | 231.9263 | 263.676
1431.5585 | 1340.5585 | 332.1492 | 283.1695 | 264.6193 | 257.2782 | 266.9062 | 246.1253 | 231.9435 | 263.6944
1432.5699 | 1341.5699 | 332.1289 | 283.2178 | 264.6358 | 257.3107 | 266.9204 | 246.1276 | 231.9751 | 263.7203
1433.5614 | 1342.5614 | 332.0639 | 283.2023 | 264.6389 | 257.3252 | 266.933 | 246.1511 | 231.9988 | 263.7586
1434.5628 | 1343.5628 | 332.0298 | 283.2765 | 264.6398 | 257.3483 | 266.9439 | 246.1853 | 232.0219 | 263.7685
1435.5642 | 1344.5642 | 331.9561 | 283.3425 | 264.6518 | 257.3779 | 266.9738 | 246.2491 | 232.0468 | 263.7744
1436.5657 | 1345.5657 | 331.8806 | 283.3858 | 264.6758 | 257.3905 | 266.9955 | 246.2917 | 232.0724 | 263.8115
1437.5671 | 1346.5671 | 331.9702 | 283.4364 | 264.6923 | 257.4045 | 267.0087 | 246.3367 | 232.0969 | 263.8133
1438.5686 | 1347.5686 | 331.915 | 283.4589 | 264.7112 | 257.4197 | 267.0387 | 246.3534 | 232.1302 | 263.7795
1439.56 | 1348.56 | 331.8943 | 283.4511 | 264.732 | 257.4408 | 267.0688 | 246.3702 | 232.1466 | 263.7827
1440.5614 | 1349.5614 | 331.913 | 283.4792 | 264.7406 | 257.4703 | 267.0653 | 246.3903 | 232.1714 | 263.8003
1441.5629 | 1350.5629 | 331.9317 | 283.5587 | 264.7627 | 257.4814 | 267.0575 | 246.3935 | 232.1857 | 263.8123
1442.5643 | 1351.5643 | 331.909 | 283.618 | 264.7758 | 257.5058 | 267.0711 | 246.4321 | 232.2044 | 263.8162
1443.5657 | 1352.5657 | 331.8497 | 283.5087 | 264.7841 | 257.5286 | 267.0849 | 246.4651 | 232.227 | 263.8176
1444.5672 | 1353.5672 | 331.7874 | 283.4582 | 264.8038 | 257.5468 | 267.0793 | 246.5043 | 232.2461 | 263.836
1445.5686 | 1354.5686 | 331.8659 | 283.503 | 264.8074 | 257.5606 | 267.0845 | 246.5469 | 232.2693 | 263.8291
1446.5701 | 1355.5701 | 331.8971 | 283.5766 | 264.8262 | 257.5804 | 267.0816 | 246.5952 | 232.2917 | 263.7912
1447.5615 | 1356.5615 | 331.8692 | 283.6565 | 264.8346 | 257.6013 | 267.0882 | 246.6103 | 232.313 | 263.8111
1448.5629 | 1357.5629 | 331.8632 | 283.6039 | 264.8544 | 257.6138 | 267.089 | 246.6396 | 232.3372 | 263.7754
1449.5644 | 1358.5644 | 331.9994 | 283.7007 | 264.8696 | 257.631 | 267.0873 | 246.6679 | 232.3626 | 263.727
1450.5658 | 1359.5658 | 332.1564 | 283.7603 | 264.8733 | 257.645 | 267.0744 | 246.7014 | 232.3897 | 263.7302
1451.5673 | 1360.5673 | 332.1884 | 283.7833 | 264.8797 | 257.6558 | 267.0549 | 246.7275 | 232.4082 | 263.7314
1452.5687 | 1361.5687 | 332.267 | 283.8668 | 264.9119 | 257.671 | 267.037 | 246.7626 | 232.4399 | 263.741
1453.5601 | 1362.5601 | 332.2632 | 283.8092 | 264.9468 | 257.6804 | 267.0238 | 246.8018 | 232.4588 | 263.7086
1454.5616 | 1363.5616 | 332.2338 | 283.8958 | 264.9613 | 257.6954 | 267.0222 | 246.8352 | 232.4856 | 263.7464
1455.563 | 1364.563 | 332.2861 | 283.9706 | 264.9778 | 257.6946 | 267.0212 | 246.8588 | 232.5056 | 263.7715
1456.5644 | 1365.5644 | 332.2643 | 283.9407 | 264.9927 | 257.7033 | 267.026 | 246.8846 | 232.5316 | 263.7438
1457.5659 | 1366.5659 | 332.2926 | 283.922 | 264.9951 | 257.7091 | 267.0307 | 246.9241 | 232.5512 | 263.7366
1458.5673 | 1367.5673 | 332.3248 | 283.8949 | 265.0141 | 257.7095 | 267.0316 | 246.9597 | 232.5773 | 263.7458
1459.5688 | 1368.5688 | 332.3592 | 283.9678 | 265.0272 | 257.7131 | 267.0484 | 247.0049 | 232.606 | 263.7431
1460.5602 | 1369.5602 | 332.4378 | 284.0237 | 265.0607 | 257.7144 | 267.0499 | 247.0285 | 232.6255 | 263.7516
1461.5616 | 1370.5616 | 332.5179 | 284.0309 | 265.0943 | 257.7266 | 267.0553 | 247.0574 | 232.6463 | 263.7885
1462.5631 | 1371.5631 | 332.6364 | 284.1575 | 265.124 | 257.7288 | 267.0729 | 247.1029 | 232.6743 | 263.8087
1463.5645 | 1372.5645 | 332.7322 | 284.2092 | 265.1232 | 257.7404 | 267.0998 | 247.145 | 232.7047 | 263.8057
1464.5659 | 1373.5659 | 332.7085 | 284.2829 | 265.1297 | 257.752 | 267.1091 | 247.1697 | 232.7285 | 263.8068
1465.5674 | 1374.5674 | 332.591 | 284.2142 | 265.1343 | 257.7529 | 267.1307 | 247.2032 | 232.7504 | 263.8329
1466.5588 | 1375.5588 | 332.5819 | 284.2948 | 265.1241 | 257.7633 | 267.1604 | 247.239 | 232.782 | 263.8368
1467.5602 | 1376.5602 | 332.618 | 284.2938 | 265.1283 | 257.7738 | 267.1876 | 247.2601 | 232.8025 | 263.8311
1468.5617 | 1377.5617 | 332.6184 | 284.3259 | 265.1436 | 257.7868 | 267.1833 | 247.2882 | 232.834 | 263.8285
1469.5631 | 1378.5631 | 332.6133 | 284.337 | 265.142 | 257.7951 | 267.1978 | 247.3355 | 232.857 | 263.8118
1470.5646 | 1379.5646 | 332.6255 | 284.3426 | 265.1535 | 257.8037 | 267.2174 | 247.3472 | 232.8752 | 263.8225
1471.566 | 1380.566 | 332.6276 | 284.3372 | 265.1716 | 257.8208 | 267.2215 | 247.3568 | 232.8964 | 263.8488
1472.5674 | 1381.5674 | 332.6539 | 284.2055 | 265.1861 | 257.8285 | 267.2402 | 247.3794 | 232.9121 | 263.8647
1473.5689 | 1382.5689 | 332.6408 | 284.1847 | 265.1927 | 257.8379 | 267.247 | 247.3938 | 232.9331 | 263.881
1474.5603 | 1383.5603 | 332.6488 | 284.1446 | 265.2091 | 257.8429 | 267.2802 | 247.4019 | 232.9507 | 263.8819
1475.5618 | 1384.5618 | 332.5536 | 284.2161 | 265.2026 | 257.8528 | 267.3021 | 247.4306 | 232.965 | 263.878
1476.5632 | 1385.5632 | 332.5487 | 284.0148 | 265.2273 | 257.8598 | 267.3188 | 247.4601 | 232.977 | 263.8599
1477.5646 | 1386.5646 | 332.5092 | 284.0082 | 265.2409 | 257.8587 | 267.3333 | 247.4996 | 232.9915 | 263.8526
1478.5661 | 1387.5661 | 332.4931 | 284.0165 | 265.2508 | 257.8738 | 267.3589 | 247.5378 | 233.0089 | 263.8453
1479.5675 | 1388.5675 | 332.3264 | 284.0954 | 265.2721 | 257.8776 | 267.3801 | 247.5731 | 233.0172 | 263.83
1480.569 | 1389.569 | 332.2497 | 284.1684 | 265.2795 | 257.8799 | 267.3968 | 247.6062 | 233.0292 | 263.7984
1481.5604 | 1390.5604 | 332.2053 | 284.2509 | 265.2972 | 257.8841 | 267.4219 | 247.6235 | 233.0461 | 263.7776
1482.5618 | 1391.5618 | 332.0902 | 284.3073 | 265.3151 | 257.8861 | 267.4512 | 247.6188 | 233.0617 | 263.7995
1483.5633 | 1392.5633 | 331.9185 | 284.3119 | 265.3221 | 257.8906 | 267.4689 | 247.6274 | 233.0742 | 263.7732
1484.5647 | 1393.5647 | 331.8504 | 284.3663 | 265.328 | 257.8888 | 267.4913 | 247.6139 | 233.0887 | 263.7178
1485.5661 | 1394.5661 | 331.8761 | 284.36 | 265.3575 | 257.8994 | 267.5066 | 247.6161 | 233.1122 | 263.6855
1486.5676 | 1395.5676 | 331.8345 | 284.3012 | 265.3667 | 257.9026 | 267.5109 | 247.6496 | 233.1183 | 263.6765
1487.569 | 1396.569 | 331.8148 | 284.2846 | 265.3824 | 257.9032 | 267.521 | 247.6798 | 233.1372 | 263.6657
1488.7006 | 1397.7006 | 331.8497 | 284.252 | 265.4008 | 257.9099 | 267.5195 | 247.7201 | 233.1613 | 263.6514
1489.5619 | 1398.5619 | 331.8867 | 284.2755 | 265.4105 | 257.9094 | 267.5039 | 247.7508 | 233.1804 | 263.6763
1490.5633 | 1399.5633 | 331.8496 | 284.2626 | 265.4192 | 257.9209 | 267.4807 | 247.7732 | 233.1994 | 263.6696
1491.5648 | 1400.5648 | 331.9224 | 284.303 | 265.4291 | 257.9239 | 267.462 | 247.8041 | 233.2172 | 263.6602
1492.5662 | 1401.5662 | 331.954 | 284.278 | 265.4464 | 257.9241 | 267.4415 | 247.8428 | 233.2363 | 263.663
1493.5676 | 1402.5676 | 331.9553 | 284.2803 | 265.4657 | 257.932 | 267.418 | 247.8654 | 233.2595 | 263.6718
1494.5691 | 1403.5691 | 332.0272 | 284.2731 | 265.4827 | 257.9345 | 267.3855 | 247.8878 | 233.275 | 263.6941
1495.5705 | 1404.5705 | 332.1137 | 284.2451 | 265.5016 | 257.9369 | 267.3823 | 247.9142 | 233.2977 | 263.665
1496.562 | 1405.562 | 332.1856 | 284.394 | 265.5125 | 257.9352 | 267.3667 | 247.9374 | 233.3281 | 263.6769
1497.5634 | 1406.5634 | 332.2397 | 284.3774 | 265.5405 | 257.9329 | 267.3588 | 247.9634 | 233.3376 | 263.6121
1498.5648 | 1407.5648 | 332.364 | 284.4559 | 265.5516 | 257.9333 | 267.3417 | 247.9871 | 233.3654 | 263.5719
1499.5663 | 1408.5663 | 332.4226 | 284.4532 | 265.5635 | 257.9298 | 267.3259 | 247.9951 | 233.3859 | 263.5549
1500.5677 | 1409.5677 | 332.4854 | 284.4796 | 265.5889 | 257.9352 | 267.3096 | 247.9993 | 233.4108 | 263.5375
1501.5691 | 1410.5691 | 332.4745 | 284.5307 | 265.602 | 257.9308 | 267.3059 | 248.0172 | 233.4254 | 263.5543
1502.5606 | 1411.5606 | 332.6256 | 284.5829 | 265.6127 | 257.9324 | 267.2966 | 248.0451 | 233.4481 | 263.5682
1503.562 | 1412.562 | 332.8808 | 284.2664 | 266.0147 | 257.8913 | 267.8551 | 248.811 | 233.3881 | 262.094
1504.5635 | 1413.5635 | 333.0448 | 284.5114 | 265.6398 | 257.9285 | 267.2811 | 248.0715 | 233.4858 | 263.625
1505.5649 | 1414.5649 | 333.1649 | 284.6336 | 265.6633 | 257.9275 | 267.2713 | 248.0977 | 233.5107 | 263.6364
1506.5663 | 1415.5663 | 333.3047 | 284.6676 | 265.6848 | 257.9252 | 267.2699 | 248.0996 | 233.5235 | 263.6219
1507.5678 | 1416.5678 | 333.4 | 284.7011 | 265.6875 | 257.9298 | 267.2594 | 248.0827 | 233.5461 | 263.6401
1508.5592 | 1417.5592 | 333.4559 | 284.7846 | 265.7094 | 257.929 | 267.2608 | 248.0736 | 233.5662 | 263.6168
1509.5606 | 1418.5606 | 333.3518 | 284.8382 | 265.7176 | 257.9341 | 267.2512 | 248.0799 | 233.5771 | 263.6161
1510.5621 | 1419.5621 | 333.2811 | 284.9402 | 265.7403 | 257.9309 | 267.2583 | 248.0987 | 233.5908 | 263.6096
1511.5635 | 1420.5635 | 333.2566 | 285.0491 | 265.7521 | 257.9302 | 267.256 | 248.1051 | 233.6128 | 263.5994
1512.565 | 1421.565 | 333.1233 | 285.0424 | 265.764 | 257.932 | 267.2694 | 248.1046 | 233.6357 | 263.5989
1513.5664 | 1422.5664 | 333.1523 | 285.09 | 265.7866 | 257.9205 | 267.2661 | 248.1066 | 233.6434 | 263.6429
1514.5678 | 1423.5678 | 333.0485 | 285.118 | 265.8055 | 257.9241 | 267.2666 | 248.1274 | 233.6612 | 263.6411
1515.5593 | 1424.5593 | 332.8687 | 285.2069 | 265.818 | 257.928 | 267.2768 | 248.1456 | 233.6699 | 263.6664
1516.5607 | 1425.5607 | 332.8644 | 285.2488 | 265.8329 | 257.9294 | 267.2773 | 248.1621 | 233.6841 | 263.6606
1517.5621 | 1426.5621 | 332.8559 | 285.3248 | 265.8539 | 257.9278 | 267.2748 | 248.1714 | 233.6916 | 263.6615
1518.5736 | 1427.5736 | 332.7509 | 285.4026 | 265.8649 | 257.9351 | 267.2876 | 248.1713 | 233.6934 | 263.6588
1519.565 | 1428.565 | 332.6954 | 285.4968 | 265.887 | 257.9414 | 267.3032 | 248.1731 | 233.7063 | 263.6814
1520.5665 | 1429.5665 | 332.6951 | 285.5743 | 265.9097 | 257.9407 | 267.3102 | 248.1671 | 233.7102 | 263.6978
1521.5679 | 1430.5679 | 332.6285 | 285.6302 | 265.9273 | 257.9519 | 267.3469 | 248.1616 | 233.7181 | 263.7107
1522.5693 | 1431.5693 | 332.613 | 285.6049 | 265.9431 | 257.9588 | 267.386 | 248.1691 | 233.7244 | 263.7224
1523.5608 | 1432.5608 | 332.5337 | 285.5958 | 265.9651 | 257.9718 | 267.401 | 248.1877 | 233.7332 | 263.7108
1524.5622 | 1433.5622 | 332.3858 | 285.5044 | 265.9921 | 257.9745 | 267.413 | 248.2118 | 233.7381 | 263.717
1525.5637 | 1434.5637 | 332.3011 | 285.4721 | 266.0117 | 257.9804 | 267.434 | 248.2416 | 233.7476 | 263.6886
1526.5651 | 1435.5651 | 332.2641 | 285.5339 | 266.0371 | 257.9905 | 267.4443 | 248.2668 | 233.7498 | 263.6901
1527.5665 | 1436.5665 | 332.2243 | 285.5102 | 266.0494 | 258.0003 | 267.4352 | 248.2823 | 233.7583 | 263.6725
1528.568 | 1437.568 | 332.1114 | 285.5592 | 266.0658 | 258.0036 | 267.4291 | 248.2947 | 233.7646 | 263.697
1529.5594 | 1438.5594 | 331.9229 | 285.5365 | 266.071 | 258.0145 | 267.451 | 248.3148 | 233.7719 | 263.6678
1530.5608 | 1439.5608 | 331.7839 | 285.5333 | 266.0895 | 258.0318 | 267.4503 | 248.3381 | 233.7776 | 263.6713
1531.5623 | 1440.5623 | 331.7225 | 285.5078 | 266.109 | 258.0421 | 267.4514 | 248.3594 | 233.7882 | 263.6179
1532.5637 | 1441.5637 | 331.7956 | 285.5107 | 266.1452 | 258.0552 | 267.4296 | 248.3846 | 233.7923 | 263.5462
1533.5652 | 1442.5652 | 331.8261 | 285.5579 | 266.1586 | 258.0595 | 267.3978 | 248.4046 | 233.8067 | 263.5099
1534.5666 | 1443.5666 | 331.839 | 285.6403 | 266.1689 | 258.0596 | 267.3553 | 248.423 | 233.8137 | 263.5153
1535.568 | 1444.568 | 331.8799 | 285.6017 | 266.216 | 258.0573 | 267.3429 | 248.5207 | 233.825 | 263.3785
1536.5695 | 1445.5695 | 331.8834 | 285.6594 | 266.2045 | 258.0588 | 267.2488 | 248.4755 | 233.8384 | 263.5689
1537.5609 | 1446.5609 | 331.8088 | 285.67 | 266.2226 | 258.0469 | 267.235 | 248.5086 | 233.8445 | 263.5819
1538.5623 | 1447.5623 | 331.7094 | 285.6364 | 266.2163 | 258.0447 | 267.2159 | 248.5123 | 233.8532 | 263.6015
1539.5638 | 1448.5638 | 331.5828 | 285.6863 | 266.2342 | 258.0414 | 267.2114 | 248.4864 | 233.8522 | 263.6151
1540.5652 | 1449.5652 | 331.3149 | 285.7014 | 266.2482 | 258.038 | 267.2059 | 248.4832 | 233.8636 | 263.5931
1541.5667 | 1450.5667 | 330.9998 | 285.6542 | 266.2574 | 258.0217 | 267.2102 | 248.4989 | 233.8713 | 263.5769
1542.5681 | 1451.5681 | 330.7325 | 285.5063 | 266.2745 | 258.0124 | 267.1944 | 248.4886 | 233.8766 | 263.5697
1543.5695 | 1452.5695 | 330.4876 | 285.3423 | 266.2856 | 258.0025 | 267.2114 | 248.4962 | 233.8784 | 263.5314
1544.561 | 1453.561 | 330.1508 | 285.368 | 266.3007 | 257.9972 | 267.2004 | 248.4932 | 233.8814 | 263.4911
1545.5624 | 1454.5624 | 329.8426 | 285.3922 | 266.3196 | 257.9983 | 267.1946 | 248.4817 | 233.8845 | 263.498
1546.5638 | 1455.5638 | 329.3823 | 285.3318 | 266.3274 | 257.9816 | 267.1958 | 248.4728 | 233.8834 | 263.4911
1547.5653 | 1456.5653 | 329.0252 | 285.2798 | 266.3493 | 257.9804 | 267.2057 | 248.4727 | 233.8818 | 263.4604
1548.5667 | 1457.5667 | 328.6269 | 285.2667 | 266.3406 | 257.9787 | 267.1958 | 248.4556 | 233.88 | 263.4796
1549.5582 | 1458.5582 | 328.3052 | 285.1666 | 266.3536 | 257.9716 | 267.1878 | 248.4122 | 233.8835 | 263.4589
1550.5596 | 1459.5596 | 327.9689 | 285.0626 | 266.3653 | 257.9691 | 267.1956 | 248.3646 | 233.8829 | 263.4398
1551.561 | 1460.561 | 327.6539 | 285.0308 | 266.3761 | 257.9559 | 267.1854 | 248.3433 | 233.8747 | 263.3919
1552.5625 | 1461.5625 | 327.1437 | 284.9287 | 266.3717 | 257.9503 | 267.1647 | 248.3124 | 233.8686 | 263.3763
1553.5639 | 1462.5639 | 326.5823 | 284.8354 | 266.3961 | 257.9474 | 267.1339 | 248.3055 | 233.8591 | 263.3438
1554.5654 | 1463.5654 | 326.0194 | 284.7575 | 266.4102 | 257.9497 | 267.1057 | 248.2507 | 233.854 | 263.2777
1555.5668 | 1464.5668 | 325.5115 | 284.7704 | 266.4084 | 257.9441 | 267.057 | 248.2113 | 233.8397 | 263.2218
1556.5582 | 1465.5582 | 325.1329 | 284.7419 | 266.4339 | 257.9426 | 267.008 | 248.1798 | 233.823 | 263.2147
1557.5597 | 1466.5597 | 324.8634 | 284.727 | 266.442 | 257.9404 | 266.9621 | 248.1679 | 233.8102 | 263.1447
1558.5611 | 1467.5611 | 324.6012 | 284.6619 | 266.4432 | 257.9353 | 266.9114 | 248.125 | 233.7928 | 263.1319
1559.5625 | 1468.5625 | 324.3118 | 284.5957 | 266.4455 | 257.9304 | 266.8622 | 248.1004 | 233.7731 | 263.0871
1560.564 | 1469.564 | 324.0317 | 283.8872 | 267.0069 | 257.8306 | 268.0765 | 249.8657 | 233.4619 | 259.9656
1561.5654 | 1470.5654 | 323.6431 | 284.4946 | 266.438 | 257.9301 | 266.7855 | 248.0806 | 233.7424 | 263.0306
1562.5669 | 1471.5669 | 323.2355 | 284.4249 | 266.4416 | 257.9328 | 266.7307 | 248.045 | 233.7205 | 262.9817
1563.5683 | 1472.5683 | 322.7572 | 284.2559 | 266.4304 | 257.9295 | 266.6918 | 247.991 | 233.7064 | 262.9424
1564.5597 | 1473.5597 | 322.4257 | 284.1468 | 266.4414 | 257.9167 | 266.6404 | 247.95 | 233.684 | 262.9014
1565.5612 | 1474.5612 | 322.1203 | 283.9864 | 266.4364 | 257.9194 | 266.5925 | 247.8797 | 233.664 | 262.8275
1566.5626 | 1475.5626 | 321.656 | 283.951 | 266.4392 | 257.9112 | 266.5322 | 247.8247 | 233.6399 | 262.7618
1567.564 | 1476.564 | 321.227 | 283.8794 | 266.4417 | 257.9064 | 266.4671 | 247.7638 | 233.6235 | 262.6745
1568.5655 | 1477.5655 | 320.7717 | 283.8149 | 266.4195 | 257.8949 | 266.4047 | 247.7025 | 233.6032 | 262.5949
1569.5669 | 1478.5669 | 320.358 | 283.7452 | 266.4136 | 257.8862 | 266.321 | 247.6496 | 233.5727 | 262.53
1570.5584 | 1479.5584 | 319.992 | 283.5697 | 266.4027 | 257.8779 | 266.2554 | 247.6025 | 233.5562 | 262.4692
1571.5698 | 1480.5698 | 319.6258 | 283.4639 | 266.3982 | 257.8661 | 266.1873 | 247.562 | 233.532 | 262.4022
1572.5612 | 1481.5612 | 319.2323 | 283.3905 | 266.3832 | 257.8508 | 266.1057 | 247.5131 | 233.5071 | 262.3037
1573.5627 | 1482.5627 | 318.7763 | 283.267 | 266.3718 | 257.8302 | 266.0631 | 247.4755 | 233.4698 | 262.2717
1574.5641 | 1483.5641 | 318.333 | 283.1896 | 266.3573 | 257.8072 | 265.9889 | 247.4179 | 233.4501 | 262.196
1575.5656 | 1484.5656 | 317.8734 | 283.1338 | 266.3633 | 257.788 | 265.9402 | 247.3526 | 233.4203 | 262.1458
1576.567 | 1485.567 | 317.4824 | 282.9949 | 266.3475 | 257.7752 | 265.8848 | 247.2853 | 233.3869 | 262.0727
1577.5684 | 1486.5684 | 317.1182 | 282.8949 | 266.3374 | 257.7475 | 265.8223 | 247.2316 | 233.3551 | 261.9961
1578.5699 | 1487.5699 | 316.7129 | 282.7478 | 266.3272 | 257.7296 | 265.766 | 247.1805 | 233.3221 | 261.9031
1579.5613 | 1488.5613 | 316.3039 | 282.5896 | 266.3141 | 257.7099 | 265.6785 | 247.1017 | 233.2849 | 261.8115
1580.5627 | 1489.5627 | 315.9771 | 282.499 | 266.296 | 257.6956 | 265.6019 | 247.0287 | 233.2455 | 261.6877
1581.5642 | 1490.5642 | 315.6405 | 282.4029 | 266.2882 | 257.6755 | 265.5287 | 246.9596 | 233.2148 | 261.5908
1582.5656 | 1491.5656 | 315.2076 | 282.2629 | 266.291 | 257.6549 | 265.521 | 246.9751 | 233.1644 | 261.4052
1583.5671 | 1492.5671 | 314.7397 | 282.1217 | 266.2616 | 257.6394 | 265.3639 | 246.8001 | 233.1344 | 261.3714
1584.5685 | 1493.5685 | 314.1945 | 281.991 | 266.2465 | 257.6229 | 265.2634 | 246.7206 | 233.0911 | 261.2863
1585.5699 | 1494.5699 | 313.6804 | 281.7811 | 266.243 | 257.5962 | 265.2097 | 246.6864 | 233.044 | 261.1322
1586.5614 | 1495.5614 | 313.1154 | 281.6028 | 266.2064 | 257.5791 | 265.0925 | 246.6002 | 233.0088 | 261.1007
1587.5628 | 1496.5628 | 312.565 | 281.4156 | 266.1966 | 257.5602 | 265.0014 | 246.5267 | 232.9594 | 260.9999
1588.5642 | 1497.5642 | 312.0713 | 281.318 | 266.1905 | 257.5364 | 264.9253 | 246.4392 | 232.9187 | 260.8411
1589.5657 | 1498.5657 | 311.6976 | 281.1956 | 266.1759 | 257.5068 | 264.8278 | 246.3435 | 232.8744 | 260.78
1590.5671 | 1499.5671 | 311.3957 | 281.0123 | 266.1517 | 257.4751 | 264.7579 | 246.2491 | 232.8262 | 260.6606
1591.5585 | 1500.5585 | 310.9799 | 280.8779 | 266.1297 | 257.4455 | 264.6641 | 246.0997 | 232.7892 | 260.5608
1592.56 | 1501.56 | 310.4793 | 280.7293 | 266.1523 | 257.4109 | 264.6953 | 246.1712 | 232.7132 | 259.8576
1593.5614 | 1502.5614 | 309.9449 | 280.6196 | 266.0858 | 257.3818 | 264.4901 | 245.8342 | 232.6944 | 260.3553
1594.5629 | 1503.5629 | 309.4215 | 280.4741 | 266.0731 | 257.3545 | 264.4016 | 245.7445 | 232.6496 | 260.1978
1595.5643 | 1504.5643 | 309.0457 | 280.3623 | 266.0606 | 257.3142 | 264.3652 | 245.7126 | 232.5994 | 259.8332
1596.5657 | 1505.5657 | 308.6842 | 280.2669 | 265.9984 | 257.2798 | 264.2097 | 245.5338 | 232.5586 | 259.9626
1597.5672 | 1506.5672 | 308.199 | 280.0797 | 265.9808 | 257.2475 | 264.1112 | 245.4346 | 232.5084 | 259.8448
1598.5586 | 1507.5586 | 307.7136 | 279.9162 | 265.9645 | 257.1997 | 264.0103 | 245.3502 | 232.4583 | 259.7404
1599.5601 | 1508.5601 | 307.3133 | 279.8035 | 265.9225 | 257.1749 | 263.9176 | 245.2702 | 232.411 | 259.6215
1600.5615 | 1509.5615 | 306.8573 | 279.5092 | 265.8915 | 257.1372 | 263.8081 | 245.2068 | 232.3588 | 259.5038
1601.5629 | 1510.5629 | 306.2524 | 279.3717 | 265.8577 | 257.0976 | 263.7036 | 245.1127 | 232.3018 | 259.3751
1602.5644 | 1511.5644 | 305.7696 | 279.2297 | 265.8221 | 257.0647 | 263.6192 | 245.0119 | 232.2448 | 259.2387
1603.5658 | 1512.5658 | 305.3994 | 278.9701 | 265.7858 | 257.0166 | 263.5018 | 244.8815 | 232.1842 | 259.0954
1604.5673 | 1513.5673 | 304.9889 | 278.8015 | 265.7493 | 256.9746 | 263.3967 | 244.7845 | 232.1314 | 258.9619
1605.5687 | 1514.5687 | 304.4515 | 278.6356 | 265.7048 | 256.9313 | 263.2756 | 244.6924 | 232.0572 | 258.8271
1606.5701 | 1515.5701 | 303.9193 | 278.4228 | 265.6827 | 256.8848 | 263.1784 | 244.5896 | 232.0014 | 258.6962
1607.5616 | 1516.5616 | 303.4284 | 278.195 | 265.639 | 256.8421 | 263.0685 | 244.4915 | 231.9392 | 258.5642
1608.563 | 1517.563 | 302.9975 | 277.8947 | 265.5984 | 256.7931 | 262.9632 | 244.3938 | 231.8786 | 258.4393
1609.5644 | 1518.5644 | 302.5227 | 277.6855 | 265.5593 | 256.7409 | 262.8355 | 244.2994 | 231.8081 | 258.2666
1610.5659 | 1519.5659 | 302.0138 | 277.2579 | 265.5147 | 256.6902 | 262.7155 | 244.2017 | 231.7463 | 258.0832
1611.5673 | 1520.5673 | 301.5152 | 276.9822 | 265.4781 | 256.6303 | 262.5816 | 244.1046 | 231.677 | 257.9087
1612.5688 | 1521.5688 | 301.0507 | 276.7436 | 265.4201 | 256.5801 | 262.4468 | 244.0205 | 231.6092 | 257.7444
1613.5602 | 1522.5602 | 300.5337 | 276.4397 | 265.3728 | 256.5349 | 262.322 | 243.9396 | 231.552 | 257.5934
1614.5616 | 1523.5616 | 300.0111 | 276.2717 | 265.3326 | 256.4772 | 262.2 | 243.8625 | 231.4923 | 257.4456
1615.5631 | 1524.5631 | 299.5081 | 276.027 | 265.2848 | 256.426 | 262.0761 | 243.76 | 231.4276 | 257.2918
1616.5645 | 1525.5645 | 299.0745 | 275.8873 | 265.2366 | 256.3754 | 261.9662 | 243.6499 | 231.3746 | 257.1302
1617.5659 | 1526.5659 | 298.6605 | 275.7383 | 265.1852 | 256.3174 | 261.8437 | 243.5579 | 231.3202 | 256.9586
1618.5674 | 1527.5674 | 298.2256 | 275.4931 | 265.1267 | 256.2727 | 261.7212 | 243.4436 | 231.2569 | 256.8078
1619.5688 | 1528.5688 | 297.7617 | 275.3488 | 265.1139 | 256.2138 | 261.6962 | 243.461 | 231.1671 | 256.2988
1620.5603 | 1529.5603 | 297.2098 | 275.2037 | 265.0316 | 256.1599 | 261.4838 | 243.1693 | 231.14 | 256.4617
1621.5617 | 1530.5617 | 296.7121 | 274.9932 | 264.9659 | 256.0981 | 261.3235 | 243.015 | 231.0802 | 256.3174
1622.5631 | 1531.5631 | 296.3353 | 274.7815 | 264.9103 | 256.0288 | 261.1754 | 242.8825 | 231.0317 | 256.1471
1623.5646 | 1532.5646 | 296.0119 | 274.4623 | 264.8657 | 255.9676 | 261.0374 | 242.7706 | 230.968 | 255.9976
1624.566 | 1533.566 | 295.6781 | 274.1667 | 264.8176 | 255.902 | 260.8991 | 242.6548 | 230.9178 | 255.8289
1625.5675 | 1534.5675 | 295.2937 | 273.7988 | 264.761 | 255.8401 | 260.7696 | 242.5419 | 230.8687 | 255.6776
1626.5689 | 1535.5689 | 294.8607 | 273.4146 | 264.7063 | 255.7725 | 260.6457 | 242.4269 | 230.8094 | 255.5027
1627.5703 | 1536.5703 | 294.4677 | 273.3017 | 264.644 | 255.7027 | 260.5318 | 242.3165 | 230.7392 | 255.3307
1628.5618 | 1537.5618 | 294.1435 | 273.0577 | 264.5847 | 255.6314 | 260.4251 | 242.2161 | 230.6823 | 255.1513
1629.5632 | 1538.5632 | 293.6196 | 272.9355 | 264.5266 | 255.5708 | 260.3231 | 242.1036 | 230.619 | 254.9684
1630.5646 | 1539.5646 | 293.1565 | 272.784 | 264.4736 | 255.505 | 260.2223 | 241.9993 | 230.5576 | 254.8166
1631.5661 | 1540.5661 | 292.7798 | 272.6357 | 264.3991 | 255.4307 | 260.119 | 241.853 | 230.4937 | 254.6321
1632.5675 | 1541.5675 | 292.332 | 272.4765 | 264.3431 | 255.3494 | 260.0235 | 241.7089 | 230.434 | 254.446
1633.5589 | 1542.5589 | 291.8617 | 272.3891 | 264.3082 | 255.2741 | 259.9482 | 241.6247 | 230.3526 | 254.0382
1634.5604 | 1543.5604 | 291.4075 | 272.2016 | 264.2248 | 255.2096 | 259.7808 | 241.3805 | 230.2978 | 254.1136
1635.5618 | 1544.5618 | 290.966 | 271.9936 | 264.1471 | 255.133 | 259.6527 | 241.2078 | 230.2336 | 253.9478
1636.5633 | 1545.5633 | 290.5775 | 271.8525 | 264.0936 | 255.0596 | 259.5428 | 241.0634 | 230.1621 | 253.7775
1637.5647 | 1546.5647 | 290.2259 | 271.7014 | 264.0131 | 254.9779 | 259.4209 | 240.9226 | 230.0964 | 253.6145
1638.5661 | 1547.5661 | 289.8105 | 271.4546 | 263.9544 | 254.8894 | 259.2996 | 240.7796 | 230.023 | 253.4544
1639.5676 | 1548.5676 | 289.4463 | 271.3599 | 263.8876 | 254.8118 | 259.1811 | 240.6331 | 229.9402 | 253.2979
1640.559 | 1549.559 | 289.1561 | 271.2405 | 263.815 | 254.7303 | 259.0668 | 240.4823 | 229.8626 | 253.136
1641.5604 | 1550.5604 | 288.7994 | 271.0401 | 263.7555 | 254.6399 | 258.9388 | 240.3224 | 229.7836 | 252.958
1642.5619 | 1551.5619 | 288.3768 | 270.8325 | 263.6735 | 254.5552 | 258.8201 | 240.1583 | 229.7115 | 252.7962
1643.5633 | 1552.5633 | 287.9929 | 270.7071 | 263.6031 | 254.481 | 258.7111 | 239.9949 | 229.6285 | 252.623
1644.5648 | 1553.5648 | 287.5731 | 270.5029 | 263.5401 | 254.4189 | 258.5902 | 239.8618 | 229.5457 | 252.4011
1645.5662 | 1554.5662 | 287.186 | 270.3248 | 263.4588 | 254.3296 | 258.4707 | 239.7046 | 229.4662 | 252.2481
1646.5676 | 1555.5676 | 286.808 | 270.1241 | 263.4006 | 254.2491 | 258.3282 | 239.5427 | 229.3789 | 252.0663
1647.5691 | 1556.5691 | 286.4712 | 269.9881 | 263.3155 | 254.1742 | 258.2133 | 239.4068 | 229.2992 | 251.8721
1648.5605 | 1557.5605 | 286.1065 | 269.8029 | 263.2424 | 254.0929 | 258.0736 | 239.2359 | 229.213 | 251.6895
1649.562 | 1558.562 | 285.6931 | 269.5759 | 263.1724 | 254.012 | 257.9339 | 239.0521 | 229.126 | 251.5182
1650.5634 | 1559.5634 | 285.2868 | 269.4322 | 263.0909 | 253.942 | 257.8034 | 238.8575 | 229.0327 | 251.3249
1651.5648 | 1560.5648 | 284.8765 | 269.1959 | 263.0395 | 253.8519 | 257.7042 | 238.7677 | 228.9391 | 249.9978
1652.5663 | 1561.5663 | 284.4948 | 268.9498 | 262.9433 | 253.7767 | 257.5272 | 238.5514 | 228.8677 | 250.926
1653.5677 | 1562.5677 | 284.186 | 268.794 | 262.8813 | 253.6913 | 257.4094 | 238.4383 | 228.762 | 250.4701
1654.5692 | 1563.5692 | 283.8431 | 268.6556 | 262.7855 | 253.6096 | 257.2666 | 238.2359 | 228.684 | 250.5726
1655.5606 | 1564.5606 | 283.421 | 268.4578 | 262.697 | 253.5203 | 257.1139 | 238.0692 | 228.5872 | 250.3834
1656.562 | 1565.562 | 282.9501 | 268.3026 | 262.6186 | 253.4311 | 256.9872 | 237.9254 | 228.5006 | 250.2106
1657.5635 | 1566.5635 | 282.4986 | 268.173 | 262.5276 | 253.3362 | 256.8471 | 237.7872 | 228.4087 | 250.019
1658.5649 | 1567.5649 | 282.0304 | 267.9938 | 262.4593 | 253.2416 | 256.7092 | 237.6326 | 228.3052 | 249.8449
1659.5663 | 1568.5663 | 281.4919 | 267.8572 | 262.3564 | 253.1444 | 256.5618 | 237.4784 | 228.2098 | 249.6556
1660.5678 | 1569.5678 | 281.0694 | 267.7099 | 262.288 | 253.0455 | 256.4222 | 237.3077 | 228.1163 | 249.4778
1661.5592 | 1570.5592 | 280.711 | 267.4757 | 262.1998 | 252.9398 | 256.2709 | 237.1407 | 228.0153 | 249.2798
1662.5606 | 1571.5606 | 280.2865 | 267.2013 | 262.1063 | 252.8405 | 256.1245 | 236.9514 | 227.9213 | 249.0906
1663.5621 | 1572.5621 | 279.8382 | 267.0059 | 262.0248 | 252.7447 | 255.979 | 236.8172 | 227.8255 | 248.8823
1664.5635 | 1573.5635 | 279.3485 | 266.8311 | 261.9385 | 252.639 | 255.7967 | 236.6731 | 227.7225 | 248.6441
1665.565 | 1574.565 | 278.8301 | 266.5275 | 261.8373 | 252.536 | 255.6202 | 236.5237 | 227.6194 | 248.4244
1666.5664 | 1575.5664 | 278.302 | 266.3477 | 261.7488 | 252.442 | 255.4124 | 236.4081 | 227.5321 | 248.2054
1667.5678 | 1576.5678 | 277.8977 | 266.0662 | 261.673 | 252.338 | 255.1942 | 236.2985 | 227.4323 | 248.0148
1668.5693 | 1577.5693 | 277.542 | 265.9262 | 261.5696 | 252.2403 | 255.0032 | 236.1734 | 227.344 | 247.8082
1669.5607 | 1578.5607 | 277.1415 | 265.5997 | 261.4861 | 252.1401 | 254.8175 | 236.0525 | 227.2523 | 247.6032
1670.5622 | 1579.5622 | 276.7233 | 265.48 | 261.3841 | 252.0334 | 254.6241 | 235.9183 | 227.1543 | 247.4053
1671.5636 | 1580.5636 | 276.3485 | 265.2507 | 261.2848 | 251.9354 | 254.4544 | 235.783 | 227.051 | 247.2005
1672.565 | 1581.565 | 275.9398 | 264.9732 | 261.2034 | 251.821 | 254.2975 | 235.6207 | 226.9573 | 246.9878
1673.5665 | 1582.5665 | 275.5362 | 264.7902 | 261.1039 | 251.7148 | 254.1517 | 235.4626 | 226.8536 | 246.7972
1674.5679 | 1583.5679 | 275.187 | 264.6091 | 261.0126 | 251.6025 | 253.9948 | 235.3058 | 226.7512 | 246.5825
1675.5694 | 1584.5694 | 274.8641 | 264.4403 | 260.9105 | 251.495 | 253.8292 | 235.1632 | 226.6486 | 246.3896
1676.5608 | 1585.5608 | 274.5691 | 264.2112 | 261.3161 | 251.3633 | 253.9203 | 235.6936 | 226.4555 | 240.8768
1677.5622 | 1586.5622 | 274.2913 | 264.1302 | 260.7047 | 251.2607 | 253.5041 | 234.8304 | 226.444 | 245.9567
1678.5637 | 1587.5637 | 273.9703 | 263.9035 | 260.6418 | 251.1397 | 253.3691 | 234.6974 | 226.3376 | 245.0911
1679.5651 | 1588.5651 | 273.6393 | 263.6884 | 260.5795 | 251.0147 | 253.2607 | 234.6706 | 226.2152 | 244.5442
1680.5665 | 1589.5665 | 273.2773 | 263.5131 | 260.4072 | 250.8999 | 253.043 | 234.3574 | 226.1338 | 245.3356
1681.558 | 1590.558 | 272.8394 | 263.2302 | 260.3181 | 250.7854 | 252.8988 | 234.2199 | 226.0241 | 245.0469
1682.5594 | 1591.5594 | 272.3855 | 262.9678 | 260.2004 | 250.6627 | 252.7325 | 234.0739 | 225.9239 | 244.9795
1683.5608 | 1592.5608 | 271.9149 | 262.6625 | 260.0894 | 250.5405 | 252.5856 | 233.9479 | 225.8143 | 244.7605
1684.5623 | 1593.5623 | 271.4448 | 262.4102 | 260.0088 | 250.4253 | 252.4213 | 233.8151 | 225.7057 | 244.546
1685.5637 | 1594.5637 | 270.9466 | 262.231 | 259.898 | 250.2936 | 252.2727 | 233.6818 | 225.5929 | 244.3072
1686.5652 | 1595.5652 | 270.4729 | 262.0587 | 259.8042 | 250.1715 | 252.1095 | 233.5159 | 225.4757 | 244.111
1687.5666 | 1596.5666 | 270.0052 | 261.7913 | 259.6923 | 250.0472 | 251.9574 | 233.345 | 225.3706 | 243.9107
1688.568 | 1597.568 | 269.5821 | 261.6286 | 259.5943 | 249.907 | 251.8012 | 233.193 | 225.2646 | 243.7185
1689.5695 | 1598.5695 | 269.1631 | 261.4737 | 259.4811 | 249.7825 | 251.6419 | 233.0417 | 225.1491 | 243.4661
1690.5609 | 1599.5609 | 268.7673 | 261.3146 | 259.3667 | 249.6587 | 251.4864 | 232.9083 | 225.043 | 243.2489
1691.5623 | 1600.5623 | 268.35 | 261.0284 | 259.2559 | 249.527 | 251.3262 | 232.785 | 224.9319 | 243.0268
1692.5638 | 1601.5638 | 267.924 | 260.7157 | 259.1312 | 249.4025 | 251.1597 | 232.6473 | 224.8313 | 242.7842
1693.5652 | 1602.5652 | 267.5195 | 260.4349 | 259.0408 | 249.2784 | 250.982 | 232.5077 | 224.7152 | 242.5716
1694.5667 | 1603.5667 | 267.1528 | 260.22 | 258.9266 | 249.1518 | 250.7974 | 232.3368 | 224.6099 | 242.3539
1695.5681 | 1604.5681 | 266.8006 | 259.9776 | 258.814 | 249.0187 | 250.6077 | 232.1802 | 224.5047 | 242.1182
1696.5695 | 1605.5695 | 266.4349 | 259.8566 | 258.6952 | 248.8889 | 250.4194 | 232.0074 | 224.3857 | 241.9026
1697.561 | 1606.561 | 266.0339 | 259.6464 | 258.5926 | 248.7547 | 250.2555 | 231.8307 | 224.2855 | 241.7069
1698.5624 | 1607.5624 | 265.6451 | 259.4409 | 258.4672 | 248.6158 | 250.09 | 231.6821 | 224.1799 | 241.4841
1699.5639 | 1608.5639 | 265.2892 | 259.2124 | 258.3493 | 248.4715 | 249.9426 | 231.5031 | 224.0622 | 241.2799
1700.5653 | 1609.5653 | 264.9243 | 259.0076 | 258.2327 | 248.3345 | 249.7738 | 231.332 | 223.9611 | 241.0639
1701.5667 | 1610.5667 | 264.5182 | 258.7729 | 258.1132 | 248.2004 | 249.6149 | 231.1831 | 223.8407 | 240.8297
1702.5582 | 1611.5582 | 264.1782 | 258.6096 | 258.0012 | 248.063 | 249.4422 | 231.0131 | 223.7382 | 240.6192
1703.5596 | 1612.5596 | 263.891 | 258.3895 | 257.8782 | 247.9351 | 249.2799 | 230.8259 | 223.6196 | 240.3892
1704.561 | 1613.561 | 263.5411 | 258.153 | 257.7658 | 247.7921 | 249.1162 | 230.6564 | 223.4994 | 240.1884
1705.5625 | 1614.5625 | 263.2324 | 257.9775 | 257.6383 | 247.6568 | 248.9599 | 230.4554 | 223.3866 | 239.9844
1706.5639 | 1615.5639 | 262.8622 | 257.6714 | 257.5142 | 247.5151 | 248.7995 | 230.2877 | 223.2653 | 239.7575
1707.5654 | 1616.5654 | 262.546 | 257.4996 | 257.3981 | 247.3801 | 248.6384 | 230.143 | 223.1426 | 239.5697
1708.5668 | 1617.5668 | 262.2226 | 257.312 | 257.2799 | 247.2451 | 248.4744 | 229.9733 | 223.0232 | 239.33
1709.5682 | 1618.5682 | 261.8633 | 257.1414 | 257.1637 | 247.105 | 248.3173 | 229.8424 | 222.9121 | 239.1162
1710.5697 | 1619.5697 | 261.5205 | 256.8324 | 257.0436 | 246.9632 | 248.1415 | 229.7034 | 222.7972 | 238.8774
1711.5611 | 1620.5611 | 261.2414 | 256.3013 | 257.5257 | 246.7584 | 248.9048 | 230.6572 | 222.5521 | 237.2291
1712.5625 | 1621.5625 | 260.8266 | 256.4381 | 256.7957 | 246.6933 | 247.7857 | 229.4194 | 222.5649 | 238.398
1713.564 | 1622.564 | 260.4323 | 256.1589 | 256.6667 | 246.5456 | 247.5956 | 229.2367 | 222.4509 | 238.1864
1714.5654 | 1623.5654 | 260.0449 | 255.9787 | 256.5321 | 246.4062 | 247.3809 | 229.0694 | 222.3394 | 237.9587
1715.5669 | 1624.5669 | 259.5895 | 255.7825 | 256.4184 | 246.2707 | 247.1852 | 228.922 | 222.2192 | 237.7266
1716.5683 | 1625.5683 | 259.1693 | 255.6168 | 256.2953 | 246.1296 | 246.9653 | 228.7627 | 222.093 | 237.5149
1717.5697 | 1626.5697 | 258.7294 | 255.3692 | 256.1614 | 245.9909 | 246.7701 | 228.5909 | 221.9687 | 237.2942
1718.5612 | 1627.5612 | 258.315 | 255.1835 | 256.026 | 245.8403 | 246.5616 | 228.4327 | 221.8447 | 237.0757
1719.5626 | 1628.5626 | 257.9276 | 255.0005 | 255.8992 | 245.6945 | 246.3805 | 228.274 | 221.7312 | 236.8541
1720.564 | 1629.564 | 257.561 | 254.8317 | 255.7512 | 245.5493 | 246.1791 | 228.1101 | 221.6127 | 236.6418
1721.5655 | 1630.5655 | 257.2445 | 254.5166 | 255.6332 | 245.4078 | 245.997 | 227.9449 | 221.4926 | 236.4182
1722.5669 | 1631.5669 | 256.9668 | 254.3938 | 255.5081 | 245.2631 | 245.8183 | 227.7531 | 221.3801 | 236.2004
1723.5584 | 1632.5584 | 256.6416 | 254.2689 | 255.3741 | 245.1153 | 245.6532 | 227.5854 | 221.2571 | 235.9984
1724.5598 | 1633.5598 | 256.2969 | 254.0799 | 255.2488 | 244.9714 | 245.5007 | 227.426 | 221.1439 | 235.7648
1725.5612 | 1634.5612 | 255.9187 | 253.8397 | 255.1128 | 244.826 | 245.3462 | 227.2567 | 221.0285 | 235.553
1726.5627 | 1635.5627 | 255.5605 | 253.6234 | 254.9649 | 244.6759 | 245.1952 | 227.0895 | 220.9157 | 235.3332
1727.5641 | 1636.5641 | 255.1932 | 253.4747 | 254.8425 | 244.5318 | 245.0401 | 226.9335 | 220.803 | 235.1298
1728.5656 | 1637.5656 | 254.8807 | 253.2912 | 254.6948 | 244.3818 | 244.8801 | 226.7351 | 220.6944 | 234.9
1729.567 | 1638.567 | 254.5451 | 253.1171 | 254.5702 | 244.2439 | 244.7237 | 226.553 | 220.5772 | 234.7164
1730.5584 | 1639.5584 | 254.2139 | 252.9132 | 254.4254 | 244.0978 | 244.5758 | 226.4023 | 220.4585 | 234.5032
1731.5699 | 1640.5699 | 253.9373 | 252.6292 | 254.3068 | 243.9612 | 244.416 | 226.226 | 220.3408 | 234.2939
1732.5613 | 1641.5613 | 253.6364 | 252.4639 | 254.1685 | 243.8204 | 244.2753 | 226.0277 | 220.2211 | 234.0802
1733.5627 | 1642.5627 | 253.3461 | 252.2618 | 254.0304 | 243.6782 | 244.1444 | 225.8257 | 220.1085 | 233.8745
1734.5642 | 1643.5642 | 253.0866 | 252.084 | 253.8933 | 243.5357 | 244.0133 | 225.6572 | 219.989 | 233.6428
1735.5656 | 1644.5656 | 252.7617 | 251.9133 | 253.7655 | 243.4036 | 243.8714 | 225.509 | 219.8693 | 233.4523
1736.5671 | 1645.5671 | 252.4236 | 251.7198 | 253.6255 | 243.2681 | 243.7348 | 225.3492 | 219.7504 | 233.2288
1737.5685 | 1646.5685 | 252.1518 | 251.5337 | 253.4819 | 243.1371 | 243.5914 | 225.1732 | 219.6256 | 232.9936
1738.5699 | 1647.5699 | 251.8737 | 251.1734 | 253.7215 | 242.9663 | 243.9824 | 225.7303 | 219.4196 | 230.7235
1739.5614 | 1648.5614 | 251.5108 | 251.1498 | 253.213 | 242.8677 | 243.3192 | 224.8404 | 219.3833 | 232.5796
1740.5628 | 1649.5628 | 251.2117 | 250.9796 | 253.0872 | 242.7383 | 243.1737 | 224.6888 | 219.2571 | 232.3534
1741.5642 | 1650.5642 | 250.8811 | 250.8692 | 252.9443 | 242.5997 | 243.0394 | 224.5639 | 219.131 | 232.1469
1742.5657 | 1651.5657 | 250.5302 | 250.6566 | 252.8016 | 242.4623 | 242.8952 | 224.3945 | 219.0104 | 231.919
1743.5671 | 1652.5671 | 250.2001 | 250.3772 | 252.6825 | 242.3259 | 242.7474 | 224.1345 | 218.8831 | 231.702
1744.5586 | 1653.5586 | 249.878 | 250.0646 | 252.5371 | 242.1915 | 242.6064 | 223.9334 | 218.7582 | 231.4775
1745.57 | 1654.57 | 249.5602 | 249.8269 | 252.4023 | 242.0551 | 242.4538 | 223.775 | 218.6313 | 231.2359
1746.5614 | 1655.5614 | 249.2195 | 249.5007 | 252.2639 | 241.9255 | 242.2994 | 223.6183 | 218.5087 | 231.0064
1747.5629 | 1656.5629 | 248.8277 | 249.2123 | 252.1232 | 241.7804 | 242.1522 | 223.4129 | 218.3795 | 230.7666
1748.5643 | 1657.5643 | 248.4734 | 248.9351 | 251.989 | 241.642 | 241.9732 | 223.1878 | 218.2651 | 230.5576
1749.5658 | 1658.5658 | 248.1173 | 248.5244 | 251.8356 | 241.5109 | 241.8038 | 223.0204 | 218.135 | 230.3569
1750.5672 | 1659.5672 | 247.7656 | 248.2997 | 251.6991 | 241.3792 | 241.6481 | 222.8864 | 218.0105 | 230.1348
1751.5686 | 1660.5686 | 247.4134 | 248.022 | 251.5573 | 241.2443 | 241.4789 | 222.7442 | 217.887 | 229.9133
1752.5601 | 1661.5601 | 247.0225 | 247.8501 | 251.4038 | 241.1026 | 241.3213 | 222.5221 | 217.7665 | 229.6758
1753.5615 | 1662.5615 | 246.6973 | 247.6363 | 251.2801 | 240.963 | 241.1601 | 222.3294 | 217.6417 | 229.4434
1754.5629 | 1663.5629 | 246.4037 | 247.4449 | 251.1316 | 240.8189 | 240.9865 | 222.1321 | 217.5176 | 229.2519
1755.5644 | 1664.5644 | 246.0473 | 247.3126 | 250.9962 | 240.6861 | 240.8263 | 221.9607 | 217.3964 | 229.0446
1756.5658 | 1665.5658 | 245.6647 | 247.0437 | 250.8414 | 240.5485 | 240.6696 | 221.7698 | 217.2569 | 228.825
1757.5673 | 1666.5673 | 245.2983 | 246.7773 | 250.7009 | 240.4062 | 240.4803 | 221.6111 | 217.1379 | 228.5854
1758.5687 | 1667.5687 | 244.9404 | 246.5752 | 250.5502 | 240.2784 | 240.3198 | 221.4532 | 217.0112 | 228.344
1759.5601 | 1668.5601 | 244.6108 | 246.3303 | 250.4036 | 240.1331 | 240.1484 | 221.2526 | 216.8837 | 228.1141
1760.5616 | 1669.5616 | 244.2794 | 246.0619 | 250.2726 | 240.0003 | 239.9754 | 221.1044 | 216.7541 | 227.889
1761.563 | 1670.563 | 243.9617 | 245.892 | 250.117 | 239.8608 | 239.7914 | 220.9393 | 216.6286 | 227.6748
1762.5644 | 1671.5644 | 243.6523 | 245.6236 | 249.961 | 239.7197 | 239.6071 | 220.7787 | 216.4906 | 227.45
1763.5659 | 1672.5659 | 243.2614 | 245.3341 | 249.8073 | 239.5792 | 239.4349 | 220.6408 | 216.3639 | 227.1916
1764.5673 | 1673.5673 | 242.9311 | 245.1737 | 249.6631 | 239.4405 | 239.239 | 220.4684 | 216.2343 | 226.9933
1765.5587 | 1674.5587 | 242.6082 | 244.9404 | 249.525 | 239.2961 | 239.0612 | 220.2967 | 216.1116 | 226.7797
1766.5602 | 1675.5602 | 242.3101 | 244.7674 | 249.3769 | 239.1469 | 238.8788 | 220.137 | 215.9723 | 226.5787
1767.5616 | 1676.5616 | 241.9745 | 244.6081 | 249.2294 | 238.9988 | 238.7013 | 219.9483 | 215.8415 | 226.3616
1768.5631 | 1677.5631 | 241.6902 | 244.4032 | 249.075 | 238.8501 | 238.5215 | 219.7724 | 215.7216 | 226.1322
1769.5645 | 1678.5645 | 241.3725 | 244.1973 | 248.9202 | 238.697 | 238.321 | 219.6278 | 215.5884 | 225.8925
1770.5659 | 1679.5659 | 241.0317 | 243.9786 | 248.766 | 238.541 | 238.132 | 219.4362 | 215.4581 | 225.6699
1771.5674 | 1680.5674 | 240.7575 | 243.7338 | 248.626 | 238.3957 | 237.9299 | 219.2603 | 215.3253 | 225.4458
1772.5588 | 1681.5588 | 240.4936 | 243.5308 | 248.4703 | 238.2386 | 237.7356 | 219.0839 | 215.1919 | 225.2416
1773.5603 | 1682.5603 | 240.1491 | 243.3295 | 248.3136 | 238.0762 | 237.5614 | 218.8929 | 215.0582 | 225.0165
1774.5617 | 1683.5617 | 239.858 | 243.0983 | 248.1586 | 237.9166 | 237.3815 | 218.6984 | 214.9222 | 224.7822
1775.5631 | 1684.5631 | 239.564 | 242.9068 | 248.0055 | 237.76 | 237.1888 | 218.5154 | 214.795 | 224.5856
1776.5646 | 1685.5646 | 239.2679 | 242.6742 | 247.8562 | 237.5959 | 237.0272 | 218.3647 | 214.6541 | 224.3554
1777.566 | 1686.566 | 238.9929 | 242.4279 | 247.6914 | 237.4316 | 236.8362 | 218.1617 | 214.5237 | 224.1711
1778.5675 | 1687.5675 | 238.7239 | 242.2362 | 247.5418 | 237.2623 | 236.6605 | 217.9692 | 214.3828 | 223.9354
1779.5689 | 1688.5689 | 238.3601 | 242.0513 | 247.3845 | 237.0939 | 236.477 | 217.7935 | 214.2423 | 223.699
1780.5703 | 1689.5703 | 238.0368 | 241.7917 | 247.2138 | 236.9352 | 236.2848 | 217.6333 | 214.1111 | 223.4813
1781.5618 | 1690.5618 | 237.7716 | 241.6012 | 247.0561 | 236.7695 | 236.0741 | 217.4731 | 213.9667 | 223.2814
1782.5632 | 1691.5632 | 237.4279 | 241.3413 | 246.8965 | 236.6086 | 235.8773 | 217.3007 | 213.8286 | 223.07
1783.5646 | 1692.5646 | 237.1025 | 241.1179 | 246.7321 | 236.4352 | 235.689 | 217.1342 | 213.6867 | 222.8574
1784.5661 | 1693.5661 | 236.8081 | 240.9147 | 246.5791 | 236.2692 | 235.4851 | 216.9465 | 213.5404 | 222.6331
1785.5675 | 1694.5675 | 236.5051 | 240.6569 | 246.4074 | 236.0944 | 235.2966 | 216.7679 | 213.3942 | 222.3981
1786.5589 | 1695.5589 | 236.1734 | 240.4501 | 246.2471 | 235.9264 | 235.0971 | 216.6346 | 213.2508 | 222.1545
1787.5704 | 1696.5704 | 235.8538 | 240.2699 | 246.094 | 235.7547 | 234.9102 | 216.4956 | 213.1185 | 221.9297
1788.5618 | 1697.5618 | 235.5023 | 240.046 | 245.9298 | 235.5804 | 234.7096 | 216.3369 | 212.9738 | 221.7098
1789.5633 | 1698.5633 | 235.2077 | 239.8456 | 245.7582 | 235.4092 | 234.5198 | 216.1763 | 212.8422 | 221.4897
1790.5647 | 1699.5647 | 234.8913 | 239.6033 | 245.6059 | 235.2357 | 234.3392 | 216.037 | 212.7047 | 221.2203
1791.5661 | 1700.5661 | 234.6128 | 239.4415 | 245.4237 | 235.0589 | 234.1342 | 215.8598 | 212.5663 | 221.0184
1792.5676 | 1701.5676 | 234.3333 | 239.1809 | 245.2608 | 234.8891 | 233.951 | 215.698 | 212.4284 | 220.8185
1793.569 | 1702.569 | 234.0478 | 238.8461 | 245.0998 | 234.7085 | 233.7598 | 215.5554 | 212.2883 | 220.5619
1794.5605 | 1703.5605 | 233.7599 | 238.6291 | 244.9331 | 234.5313 | 233.5641 | 215.3915 | 212.1525 | 220.3684
1795.5619 | 1704.5619 | 233.4544 | 238.4051 | 244.762 | 234.3514 | 233.3726 | 215.2119 | 212.0134 | 220.1613
1796.5633 | 1705.5633 | 233.1566 | 238.135 | 244.5969 | 234.1752 | 233.1851 | 215.061 | 211.8819 | 219.9341
1797.5648 | 1706.5648 | 232.8458 | 237.9234 | 244.4301 | 234.0031 | 232.9997 | 214.8869 | 211.744 | 219.6969
1798.5662 | 1707.5662 | 232.5246 | 237.8155 | 244.2674 | 233.8195 | 232.8156 | 214.7004 | 211.6059 | 219.4801
1799.5677 | 1708.5677 | 232.1666 | 237.5818 | 244.0956 | 233.6441 | 232.6426 | 214.5418 | 211.4695 | 219.2743

## C6-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 155.7619 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38909.5379 | 1 | 0 | 38909.5379 | 1 | 0 | -34 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5386 | 1 | 0 | 38909.5386 | 1 | 0 | 24.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5393 | 1 | 0 | 38909.5393 | 2 | 0 | 83.5 | 174.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255038 | 127469 | 255037.9994
38909.54 | 1 | 0 | 38909.54 | 1 | 0 | 142.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5406 | 1 | 0 | 38909.5406 | 1 | 0 | 201 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5413 | 1 | 0 | 38909.5413 | 1 | 0 | 260 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.542 | 1 | 0 | 38909.542 | 1 | 0 | 318.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5427 | 1 | 0 | 38909.5427 | 2 | 0 | 377.5 | 468.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 255038 | 127469 | 255037.9994
38909.5434 | 1 | 0 | 38909.5434 | 1 | 0 | 436.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.544 | 1 | 0 | 38909.5441 | 1 | 0 | 495 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5447 | 1 | 0 | 38909.5447 | 1 | 0 | 554 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5454 | 1 | 0 | 38909.5454 | 1 | 0 | 612.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5461 | 1 | 0 | 38909.5461 | 1 | 0 | 671.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5467 | 1 | 0 | 38909.5468 | 1 | 0 | 730 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5474 | 1 | 0 | 38909.5475 | 1 | 0 | 789 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38909.5481 | 984 | 954 | 38909.5481 | 1107 | 1161 | 847.5 | 938.5 | 60.0733 | 58.2418 | 67.5824 | 70.8791 | 0.60073 | 0.58242 | 0.67582 | 0.70879 | 0.018315 | 0.032967 | 14127.7316 | 5046.1106 | 63.0462
38909.5488 | 927 | 957 | 38909.5488 | 982 | 1020 | 906.5 | 997.5 | 56.5934 | 58.4249 | 59.9512 | 62.2711 | 0.56593 | 0.58425 | 0.59951 | 0.62271 | 0.018315 | 0.023199 | 14681.015 | 5053.9975 | 68.3836
38909.5495 | 1029 | 999 | 38909.5495 | 1143 | 922 | 965.5 | 1056.5 | 62.8205 | 60.989 | 69.7802 | 56.2882 | 0.62821 | 0.60989 | 0.6978 | 0.56288 | 0.018315 | 0.13492 | 685.0546 | 519.6966 | 43.9362
38909.5502 | 967 | 937 | 38909.5502 | 988 | 958 | 1024 | 1115 | 59.0354 | 57.2039 | 60.3175 | 58.486 | 0.59035 | 0.57204 | 0.60317 | 0.58486 | 0.018315 | 0.018315 | 8404.6 | 8404.6 | 68.2783
38909.5508 | 1103 | 1156 | 38909.5509 | 1201 | 931 | 1083 | 1174 | 67.3382 | 70.5739 | 73.3211 | 56.8376 | 0.67338 | 0.70574 | 0.73321 | 0.56838 | 0.032357 | 0.16484 | 365.6736 | 336.9423 | 19.5039
38909.5515 | 1181 | 1199 | 38909.5515 | 1062 | 1032 | 1141.5 | 1232.5 | 72.1001 | 73.199 | 64.8352 | 63.0037 | 0.721 | 0.73199 | 0.64835 | 0.63004 | 0.010989 | 0.018315 | 8772.345 | 50411.8842 | 14.2653
38909.5522 | 995 | 1034 | 38909.5522 | 1082 | 1053 | 1200.5 | 1291.5 | 60.7448 | 63.1258 | 66.0562 | 64.2857 | 0.60745 | 0.63126 | 0.66056 | 0.64286 | 0.02381 | 0.017705 | 4385.5034 | 29451.9605 | 50.3494
38909.5529 | 2411 | 1 | 38909.5529 | 2270 | 1 | 1259.5 | 1350.5 | 147.1917 | 0.06105 | 138.5836 | 0.06105 | 1.4719 | 0.0006105 | 1.3858 | 0.0006105 | 1.4713 | 1.3852 | 5.8443 | 12.4953 | 1548.1474
38909.5536 | 2007 | 1 | 38909.5536 | 2011 | 1 | 1318 | 1409 | 122.5275 | 0.06105 | 122.7717 | 0.06105 | 1.2253 | 0.0006105 | 1.2277 | 0.0006105 | 1.2247 | 1.2271 | 27.1879 | 26.9339 | 11529.8805
38909.5542 | 2270 | 1 | 38909.5543 | 2177 | 1 | 1377 | 1468 | 138.5836 | 0.06105 | 132.906 | 0.06105 | 1.3858 | 0.0006105 | 1.3291 | 0.0006105 | 1.3852 | 1.3284 | 12.4328 | 17.2688 | 4128.8261
38909.5549 | 2535 | 0 | 38909.5549 | 1956 | 0 | 1435.5 | 1526.5 | 154.7619 | 0 | 119.4139 | 0 | 1.5476 | 0 | 1.1941 | 0 | 1.5476 | 1.1941 | 0.64615 | 30.4387 | 0.90147
38909.5556 | 1039 | 1080 | 38909.5556 | 1068 | 1037 | 1494.5 | 1585.5 | 63.431 | 65.9341 | 65.2015 | 63.3089 | 0.63431 | 0.65934 | 0.65201 | 0.63309 | 0.025031 | 0.018926 | 4109.4828 | 25727.7501 | 39.8802
38909.5563 | 1010 | 1051 | 38909.5563 | 1206 | 1183 | 1553.5 | 1644.5 | 61.6606 | 64.1636 | 73.6264 | 72.2222 | 0.61661 | 0.64164 | 0.73626 | 0.72222 | 0.025031 | 0.014042 | 2679.8118 | 6362.6717 | 45.9365
38909.557 | 2251 | 0 | 38909.557 | 2365 | 0 | 1612 | 1703 | 137.4237 | 0 | 144.3834 | 0 | 1.3742 | 0 | 1.4438 | 0 | 1.3742 | 1.4438 | 13.3443 | 7.8808 | 11.9701
38909.5576 | 2265 | 0 | 38909.5577 | 2206 | 0 | 1671 | 1762 | 138.2784 | 0 | 134.6764 | 0 | 1.3828 | 0 | 1.3468 | 0 | 1.3828 | 1.3468 | 12.6437 | 15.6564 | 11.2609
38909.5583 | 2442 | 1 | 38909.5583 | 2072 | 1 | 1729.5 | 1820.5 | 149.0842 | 0.06105 | 126.4957 | 0.06105 | 1.4908 | 0.0006105 | 1.265 | 0.0006105 | 1.4902 | 1.2643 | 4.4888 | 23.399 | 2055.1068

## C5-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 152.7705 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38909.5379 | 1 | 0 | 38909.5379 | 1 | 0 | -37 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5386 | 1 | 0 | 38909.5386 | 1 | 0 | 22 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5392 | 1 | 0 | 38909.5392 | 1 | 0 | 80.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5399 | 1 | 0 | 38909.5399 | 1 | 0 | 139.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5406 | 1 | 0 | 38909.5406 | 1 | 0 | 198.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5413 | 1 | 0 | 38909.5413 | 1 | 0 | 257 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.542 | 1 | 0 | 38909.542 | 1 | 0 | 316 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5426 | 1 | 0 | 38909.5427 | 1 | 0 | 374.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5433 | 1 | 0 | 38909.5433 | 1 | 0 | 433.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.544 | 1 | 0 | 38909.544 | 1 | 0 | 492 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5447 | 1 | 0 | 38909.5447 | 1 | 0 | 551 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5454 | 1 | 0 | 38909.5454 | 1 | 0 | 610 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.546 | 1 | 0 | 38909.5461 | 2 | 0 | 668.5 | 759.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250138 | 125019 | 250137.9994
38909.5467 | 1 | 0 | 38909.5467 | 1 | 0 | 727.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5474 | 1 | 0 | 38909.5474 | 1 | 0 | 786 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5481 | 1 | 0 | 38909.5481 | 2 | 1 | 845 | 936 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 250138 | 250138 | 250137.9994
38909.5488 | 1 | 1 | 38909.5488 | 1 | 0 | 903.5 | 994.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 625690190.44 | 250138 | 249938.0799
38909.5494 | 1 | 1 | 38909.5495 | 2 | 1 | 962.5 | 1053.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 625439952.44 | 250037.96 | 249938.04
38909.5501 | 1 | 1 | 38909.5501 | 2 | 1 | 1021.5 | 1112.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 625439952.44 | 250037.96 | 249938.04
38909.5508 | 957 | 927 | 38909.5508 | 1161 | 1133 | 1080 | 1171 | 58.4249 | 56.5934 | 70.8791 | 69.1697 | 0.58425 | 0.56593 | 0.70879 | 0.6917 | 0.018315 | 0.017094 | 7158.7133 | 11019.1843 | 66.1077
38909.5515 | 1135 | 1105 | 38909.5515 | 1159 | 1194 | 1139 | 1230 | 69.2918 | 67.4603 | 70.757 | 72.8938 | 0.69292 | 0.6746 | 0.70757 | 0.72894 | 0.018315 | 0.021368 | 31821.2583 | 4299.1198 | 23.205
38909.5522 | 1034 | 1004 | 38909.5522 | 1011 | 982 | 1197.5 | 1288.5 | 63.1258 | 61.2943 | 61.7216 | 59.9512 | 0.63126 | 0.61294 | 0.61722 | 0.59951 | 0.018315 | 0.017705 | 7705.304 | 9174.5998 | 45.7543
38909.5528 | 2231 | 1 | 38909.5529 | 2419 | 1 | 1256.5 | 1347.5 | 136.2027 | 0.06105 | 147.6801 | 0.06105 | 1.362 | 0.0006105 | 1.4768 | 0.0006105 | 1.3614 | 1.4762 | 12.3293 | 3.4599 | 904.2058
38909.5535 | 2295 | 1 | 38909.5535 | 2313 | 1 | 1315.5 | 1406.5 | 140.1099 | 0.06105 | 141.2088 | 0.06105 | 1.4011 | 0.0006105 | 1.4121 | 0.0006105 | 1.4005 | 1.4115 | 9.0882 | 8.2303 | 1569.4109
38909.5542 | 2266 | 1 | 38909.5542 | 2284 | 1 | 1374 | 1465 | 138.3394 | 0.06105 | 139.4383 | 0.06105 | 1.3834 | 0.0006105 | 1.3944 | 0.0006105 | 1.3828 | 1.3938 | 10.4844 | 9.6056 | 2062.8228
38909.5549 | 2297 | 1 | 38909.5549 | 2245 | 1 | 1433 | 1524 | 140.232 | 0.06105 | 137.0574 | 0.06105 | 1.4023 | 0.0006105 | 1.3706 | 0.0006105 | 1.4017 | 1.37 | 8.979 | 11.5269 | 2112.3772
38909.5556 | 2486 | 0 | 38909.5556 | 60 | 0 | 1491.5 | 1582.5 | 151.7705 | 0 | 3.663 | 0 | 1.5177 | 0 | 0.03663 | 0 | 1.5177 | 0.03663 | 0.65889 | 4070.6333 | 0.85881
38909.5563 | 2451 | 1 | 38909.5563 | 3 | 0 | 1550.5 | 1641.5 | 149.6337 | 0.06105 | 0.18315 | 0 | 1.4963 | 0.0006105 | 0.0018315 | 0 | 1.4957 | 0.0018315 | 2.0971 | 83312.6667 | 5031.9601
38909.5569 | 1964 | 1 | 38909.5569 | 1983 | 0 | 1609.5 | 1700.5 | 119.9023 | 0.06105 | 121.0623 | 0 | 1.199 | 0.0006105 | 1.2106 | 0 | 1.1984 | 1.2106 | 27.4798 | 26.1916 | 11153.5588
38909.5576 | 1746 | 0 | 38909.5576 | 2013 | 0 | 1668 | 1759 | 106.5934 | 0 | 122.8938 | 0 | 1.0659 | 0 | 1.2289 | 0 | 1.0659 | 1.2289 | 43.3207 | 24.311 | 42.2548
38909.5583 | 1397 | 1 | 38909.5583 | 2002 | 0 | 1727 | 1818 | 85.2869 | 0.06105 | 122.2222 | 0 | 0.85287 | 0.0006105 | 1.2222 | 0 | 0.85226 | 1.2222 | 79.4095 | 24.994 | 22083.3632

## C5-6
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.2503 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38909.5378 | 1 | 0 | 38909.5379 | 1 | 0 | -39.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5385 | 1 | 0 | 38909.5385 | 1 | 0 | 19 | 110 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5392 | 1 | 0 | 38909.5392 | 1 | 0 | 78 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5399 | 1 | 0 | 38909.5399 | 1 | 0 | 136.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5406 | 1 | 0 | 38909.5406 | 1 | 0 | 195.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5413 | 1 | 0 | 38909.5413 | 1 | 0 | 254.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5419 | 1 | 0 | 38909.5419 | 1 | 0 | 313 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5426 | 1 | 0 | 38909.5426 | 1 | 0 | 372 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5433 | 1 | 0 | 38909.5433 | 1 | 0 | 430.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.544 | 1 | 0 | 38909.544 | 1 | 0 | 489.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5447 | 1 | 0 | 38909.5447 | 1 | 0 | 548.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5453 | 1 | 0 | 38909.5453 | 1 | 0 | 607 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.546 | 1 | 0 | 38909.546 | 1 | 0 | 666 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5467 | 1 | 0 | 38909.5467 | 1 | 0 | 724.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5474 | 1 | 0 | 38909.5474 | 1 | 0 | 783.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5481 | 2 | 1 | 38909.5481 | 1 | 1 | 842.5 | 933.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255737.9609 | 654274884.4661 | 255637.9609
38909.5487 | 1 | 1 | 38909.5488 | 2 | 1 | 901 | 992 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 654274884.44 | 255737.9609 | 255638.0391
38909.5494 | 2 | 1 | 38909.5494 | 2 | 1 | 959.5 | 1050.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255538.1172
38909.5501 | 2 | 1 | 38909.5501 | 1 | 1 | 1018.5 | 1109.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255737.9609 | 654274884.4661 | 255637.9609
38909.5508 | 1144 | 1114 | 38909.5508 | 961 | 929 | 1077.5 | 1168.5 | 69.8413 | 68.0098 | 58.6691 | 56.7155 | 0.69841 | 0.6801 | 0.58669 | 0.56716 | 0.018315 | 0.019536 | 9976.178 | 7045.1028 | 26.6752
38909.5514 | 1108 | 1175 | 38909.5515 | 1055 | 1025 | 1136 | 1227 | 67.6435 | 71.7338 | 64.4078 | 62.5763 | 0.67643 | 0.71734 | 0.64408 | 0.62576 | 0.040904 | 0.018315 | 1493.7448 | 3895.3912 | 22.933
38909.5521 | 1101 | 1153 | 38909.5522 | 1175 | 1149 | 1195 | 1286 | 67.2161 | 70.3907 | 71.7338 | 70.1465 | 0.67216 | 0.70391 | 0.71734 | 0.70147 | 0.031746 | 0.015873 | 1652.3663 | 3179.8043 | 25.6782
38909.5528 | 2451 | 1 | 38909.5528 | 2255 | 1 | 1253.5 | 1344.5 | 149.6337 | 0.06105 | 137.6679 | 0.06105 | 1.4963 | 0.0006105 | 1.3767 | 0.0006105 | 1.4957 | 1.3761 | 4.437 | 13.6404 | 1288.8944
38909.5535 | 2114 | 1 | 38909.5535 | 1983 | 21 | 1312.5 | 1403.5 | 129.0598 | 0.06105 | 121.0623 | 1.2821 | 1.2906 | 0.0006105 | 1.2106 | 0.012821 | 1.29 | 1.1978 | 21.1104 | 30.9462 | 10501.9249
38909.5542 | 2475 | 1 | 38909.5542 | 2401 | 1 | 1371.5 | 1462.5 | 151.0989 | 0.06105 | 146.5812 | 0.06105 | 1.511 | 0.0006105 | 1.4658 | 0.0006105 | 1.5104 | 1.4652 | 3.4314 | 6.6803 | 522.1227
38909.5548 | 2014 | 0 | 38909.5549 | 1999 | 0 | 1430 | 1521 | 122.9548 | 0 | 122.0391 | 0 | 1.2295 | 0 | 1.2204 | 0 | 1.2295 | 1.2204 | 27.0794 | 28.033 | 25.8499
38909.5555 | 2177 | 0 | 38909.5556 | 4 | 1 | 1489 | 1580 | 132.906 | 0 | 0.2442 | 0.06105 | 1.3291 | 0 | 0.002442 | 0.0006105 | 1.3291 | 0.0018315 | 17.5645 | 85212.6667 | 16.2355
38909.5562 | 2283 | 0 | 38909.5562 | 3 | 1 | 1547.5 | 1638.5 | 139.3773 | 0 | 0.18315 | 0.06105 | 1.3938 | 0 | 0.0018315 | 0.0006105 | 1.3938 | 0.001221 | 12.106 | 127869 | 10.7122
38909.5569 | 2181 | 1 | 38909.5569 | 2193 | 0 | 1606.5 | 1697.5 | 133.1502 | 0.06105 | 133.8828 | 0 | 1.3315 | 0.0006105 | 1.3388 | 0 | 1.3309 | 1.3388 | 17.4047 | 16.7068 | 5402.2648
38909.5576 | 2089 | 1 | 38909.5576 | 2543 | 1 | 1665.5 | 1756.5 | 127.5336 | 0.06105 | 155.2503 | 0.06105 | 1.2753 | 0.0006105 | 1.5525 | 0.0006105 | 1.2747 | 1.5519 | 24.3334 | 0.64542 | 301.0035
38909.5583 | 1548 | 2 | 38909.5583 | 2188 | 1 | 1724 | 1815 | 94.5055 | 0.1221 | 133.5775 | 0.06105 | 0.94505 | 0.001221 | 1.3358 | 0.0006105 | 0.94383 | 1.3352 | 65.921 | 16.993 | 7330.5363

## C4-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 155.823 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38909.5378 | 1 | 0 | 38909.5378 | 1 | 0 | -42.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5385 | 1 | 0 | 38909.5385 | 1 | 0 | 16.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5392 | 1 | 0 | 38909.5392 | 1 | 0 | 75 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5398 | 1 | 0 | 38909.5399 | 1 | 0 | 134 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5405 | 1 | 0 | 38909.5406 | 1 | 0 | 193 | 284 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5412 | 1 | 0 | 38909.5412 | 1 | 0 | 251.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5419 | 1 | 0 | 38909.5419 | 1 | 0 | 310.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5426 | 1 | 0 | 38909.5426 | 1 | 0 | 369 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5433 | 1 | 0 | 38909.5433 | 1 | 0 | 427.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5439 | 1 | 0 | 38909.5439 | 1 | 0 | 486.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5446 | 1 | 0 | 38909.5446 | 1 | 0 | 545.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5453 | 1 | 0 | 38909.5453 | 1 | 0 | 604.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.546 | 1 | 0 | 38909.546 | 1 | 0 | 663 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5467 | 1 | 0 | 38909.5467 | 1 | 0 | 722 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.5473 | 1 | 0 | 38909.5473 | 1 | 0 | 780.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
38909.548 | 1 | 2 | 38909.548 | 1 | 1 | 839.5 | 930.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255137.9216 | 650953790.5757 | 127468.9804
38909.5487 | 1 | 2 | 38909.5487 | 1 | 1 | 898.5 | 989.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255137.9216 | 650953790.5757 | 127468.9804
38909.5494 | 1 | 3 | 38909.5494 | 3 | 2 | 957 | 1048 | 0.06105 | 0.18315 | 0.18315 | 0.1221 | 0.0006105 | 0.0018315 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 127643.9853 | 255338.0785 | 84912.745
38909.5501 | 2 | 3 | 38909.5501 | 1 | 1 | 1016 | 1107 | 0.1221 | 0.18315 | 0.06105 | 0.06105 | 0.001221 | 0.0018315 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255037.8824 | 650698552.4789 | 84912.6536
38909.5507 | 1200 | 1175 | 38909.5508 | 1206 | 1193 | 1074.5 | 1165.5 | 73.2601 | 71.7338 | 73.6264 | 72.8327 | 0.7326 | 0.71734 | 0.73626 | 0.72833 | 0.015263 | 0.0079365 | 2279.3243 | 3422.4137 | 14.6676
38909.5514 | 1203 | 1183 | 38909.5514 | 1075 | 932 | 1133.5 | 1224.5 | 73.4432 | 72.2222 | 65.6288 | 56.8987 | 0.73443 | 0.72222 | 0.65629 | 0.56899 | 0.01221 | 0.087302 | 638.1479 | 617.9077 | 12.1052
38909.5521 | 1000 | 969 | 38909.5521 | 1049 | 1018 | 1192 | 1283 | 61.0501 | 59.1575 | 64.0415 | 62.149 | 0.6105 | 0.59158 | 0.64042 | 0.62149 | 0.018926 | 0.018926 | 8133.4839 | 8133.4839 | 59.4731
38909.5528 | 2018 | 2 | 38909.5528 | 2321 | 1 | 1251 | 1342 | 123.199 | 0.1221 | 141.6972 | 0.06105 | 1.232 | 0.001221 | 1.417 | 0.0006105 | 1.2308 | 1.4164 | 26.7728 | 9.9894 | 2417.5678
38909.5535 | 2222 | 0 | 38909.5535 | 2299 | 0 | 1309.5 | 1400.5 | 135.6532 | 0 | 140.3541 | 0 | 1.3565 | 0 | 1.4035 | 0 | 1.3565 | 1.4035 | 14.8686 | 11.0213 | 13.5121
38909.5541 | 2359 | 0 | 38909.5542 | 2317 | 1 | 1368.5 | 1459.5 | 144.0171 | 0 | 141.453 | 0.06105 | 1.4402 | 0 | 1.4145 | 0.0006105 | 1.4402 | 1.4139 | 8.1975 | 10.2064 | 6.7574
38909.5548 | 2536 | 1 | 38909.5548 | 2344 | 1 | 1427.5 | 1518.5 | 154.823 | 0.06105 | 143.1013 | 0.06105 | 1.5482 | 0.0006105 | 1.431 | 0.0006105 | 1.5476 | 1.4304 | 0.64884 | 9.5199 | 133.6895
38909.5555 | 1961 | 1 | 38909.5555 | 136 | 0 | 1486 | 1577 | 119.7192 | 0.06105 | 8.3028 | 0 | 1.1972 | 0.0006105 | 0.083028 | 0 | 1.1966 | 0.083028 | 30.1733 | 1776.75 | 55892.2427
38909.5562 | 2004 | 1 | 38909.5562 | 2 | 0 | 1545 | 1636 | 122.3443 | 0.06105 | 0.1221 | 0 | 1.2234 | 0.0006105 | 0.001221 | 0 | 1.2228 | 0.001221 | 27.3779 | 127519 | 54695.1083
38909.5569 | 1971 | 1 | 38909.5569 | 1801 | 35 | 1603.5 | 1694.5 | 120.3297 | 0.06105 | 109.9512 | 2.1368 | 1.2033 | 0.0006105 | 1.0995 | 0.021368 | 1.2027 | 1.0781 | 29.5446 | 45.6063 | 18178.466
38909.5575 | 1730 | 1 | 38909.5576 | 2295 | 1 | 1662.5 | 1753.5 | 105.6166 | 0.06105 | 140.1099 | 0.06105 | 1.0562 | 0.0006105 | 1.4011 | 0.0006105 | 1.0556 | 1.4005 | 47.8101 | 11.2299 | 8292.7763
38909.5582 | 1531 | 2 | 38909.5582 | 2165 | 1 | 1721.5 | 1812.5 | 93.4676 | 0.1221 | 132.1734 | 0.06105 | 0.93468 | 0.001221 | 1.3217 | 0.0006105 | 0.93346 | 1.3211 | 67.2919 | 17.9134 | 7743.2127

## C4-6
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 155.3956 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38909.5378 | 1 | 0 | 38909.5378 | 1 | 0 | -45.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5385 | 1 | 0 | 38909.5385 | 1 | 0 | 13.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5391 | 1 | 0 | 38909.5392 | 1 | 0 | 72.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5398 | 1 | 0 | 38909.5398 | 1 | 0 | 131 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5405 | 2 | 0 | 38909.5405 | 1 | 0 | 190 | 281 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127169 | 254438 | 127168.9988
38909.5412 | 1 | 0 | 38909.5412 | 1 | 0 | 248.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5419 | 1 | 0 | 38909.5419 | 1 | 0 | 307.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5425 | 1 | 0 | 38909.5426 | 1 | 0 | 366.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5432 | 1 | 0 | 38909.5432 | 1 | 0 | 425 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5439 | 1 | 0 | 38909.5439 | 1 | 0 | 484 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5446 | 1 | 0 | 38909.5446 | 1 | 0 | 542.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5453 | 1 | 0 | 38909.5453 | 1 | 0 | 601.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5459 | 1 | 0 | 38909.546 | 1 | 0 | 660.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5466 | 1 | 0 | 38909.5466 | 1 | 0 | 719 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.5473 | 1 | 0 | 38909.5473 | 1 | 0 | 777.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
38909.548 | 2 | 7 | 38909.548 | 2 | 5 | 836.5 | 927.5 | 0.1221 | 0.42735 | 0.1221 | 0.30525 | 0.001221 | 0.0042735 | 0.001221 | 0.0030525 | 0.0030525 | 0.0018315 | 50951.4633 | 85057.564 | 36191.4506
38909.5487 | 2 | 8 | 38909.5487 | 1 | 4 | 895.5 | 986.5 | 0.1221 | 0.4884 | 0.06105 | 0.2442 | 0.001221 | 0.004884 | 0.0006105 | 0.002442 | 0.003663 | 0.0018315 | 42456.2021 | 85079.8592 | 31655.0437
38909.5493 | 2 | 9 | 38909.5494 | 1 | 5 | 954 | 1045 | 0.1221 | 0.54945 | 0.06105 | 0.30525 | 0.001221 | 0.0054945 | 0.0006105 | 0.0030525 | 0.0042735 | 0.002442 | 36407.3361 | 63828.6476 | 28115.729
38909.55 | 2 | 9 | 38909.55 | 2 | 5 | 1013 | 1104 | 0.1221 | 0.54945 | 0.1221 | 0.30525 | 0.001221 | 0.0054945 | 0.001221 | 0.0030525 | 0.0042735 | 0.0018315 | 36388.9326 | 85169.4218 | 28126.7533
38909.5507 | 59 | 69 | 38909.5507 | 1037 | 1005 | 1071.5 | 1162.5 | 3.602 | 4.2125 | 63.3089 | 61.3553 | 0.03602 | 0.042125 | 0.63309 | 0.61355 | 0.006105 | 0.019536 | 28588.9876 | 5295.4116 | 3438.5154
38909.5514 | 950 | 948 | 38909.5514 | 1093 | 1062 | 1130.5 | 1221.5 | 57.9976 | 57.8755 | 66.7277 | 64.8352 | 0.57998 | 0.57875 | 0.66728 | 0.64835 | 0.001221 | 0.018926 | 4947.7405 | 3134.4421 | 66.1777
38909.5521 | 1197 | 1173 | 38909.5521 | 1202 | 1181 | 1189.5 | 1280.5 | 73.0769 | 71.6117 | 73.3822 | 72.1001 | 0.73077 | 0.71612 | 0.73382 | 0.721 | 0.014652 | 0.012821 | 5600.2498 | 1520605.7259 | 14.9504
38909.5527 | 2529 | 2 | 38909.5528 | 1957 | 1 | 1248 | 1339 | 154.3956 | 0.1221 | 119.475 | 0.06105 | 1.544 | 0.001221 | 1.1947 | 0.0006105 | 1.5427 | 1.1941 | 0.64977 | 32.6497 | 176.9708
38909.5534 | 2398 | 1 | 38909.5534 | 2529 | 1 | 1307 | 1398 | 146.398 | 0.06105 | 154.3956 | 0.06105 | 1.464 | 0.0006105 | 1.544 | 0.0006105 | 1.4634 | 1.5433 | 6.5689 | 0.65187 | 94.8025
38909.5541 | 2074 | 0 | 38909.5541 | 1981 | 0 | 1365.5 | 1456.5 | 126.6178 | 0 | 120.9402 | 0 | 1.2662 | 0 | 1.2094 | 0 | 1.2662 | 1.2094 | 22.7281 | 28.4897 | 21.4619
38909.5548 | 1989 | 1 | 38909.5548 | 2030 | 0 | 1424.5 | 1515.5 | 121.4286 | 0.06105 | 123.9316 | 0 | 1.2143 | 0.0006105 | 1.2393 | 0 | 1.2137 | 1.2393 | 28.0425 | 25.3882 | 11245.1479
38909.5555 | 2317 | 1 | 38909.5555 | 2288 | 1 | 1483.5 | 1574.5 | 141.453 | 0.06105 | 139.6825 | 0.06105 | 1.4145 | 0.0006105 | 1.3968 | 0.0006105 | 1.4139 | 1.3962 | 9.8988 | 11.304 | 2309.2601
38909.5561 | 2374 | 0 | 38909.5562 | 2 | 1 | 1542 | 1633 | 144.9328 | 0 | 0.1221 | 0.06105 | 1.4493 | 0 | 0.001221 | 0.0006105 | 1.4493 | 0.0006105 | 7.219 | 254438 | 5.7697
38909.5568 | 2376 | 1 | 38909.5569 | 3 | 1 | 1601 | 1692 | 145.0549 | 0.06105 | 0.18315 | 0.06105 | 1.4505 | 0.0006105 | 0.0018315 | 0.0006105 | 1.4499 | 0.001221 | 7.1318 | 21148.1615 | 16758.7555
38909.5575 | 2061 | 2 | 38909.5575 | 2110 | 1 | 1659.5 | 1750.5 | 125.8242 | 0.1221 | 128.8156 | 0.06105 | 1.2582 | 0.001221 | 1.2882 | 0.0006105 | 1.257 | 1.2875 | 23.636 | 20.6854 | 4133.9817
38909.5582 | 1673 | 7 | 38909.5582 | 2518 | 3 | 1718.5 | 1809.5 | 102.1368 | 0.42735 | 153.7241 | 0.18315 | 1.0214 | 0.0042735 | 1.5372 | 0.0018315 | 1.0171 | 1.5354 | 85.2006 | 1.0902 | 133.3226

## C4-5
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 154.9683 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38909.5377 | 1 | 0 | 38909.5378 | 1 | 0 | -48 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5384 | 1 | 0 | 38909.5384 | 2 | 0 | 10.5 | 101.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253738 | 126819 | 253737.9994
38909.5391 | 1 | 0 | 38909.5391 | 1 | 0 | 69.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5398 | 1 | 0 | 38909.5398 | 1 | 0 | 128.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5405 | 1 | 0 | 38909.5405 | 1 | 0 | 187 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5411 | 1 | 0 | 38909.5412 | 1 | 0 | 246 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5418 | 1 | 0 | 38909.5418 | 1 | 0 | 304.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5425 | 1 | 0 | 38909.5425 | 2 | 0 | 363.5 | 454.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253738 | 126819 | 253737.9994
38909.5432 | 1 | 0 | 38909.5432 | 2 | 0 | 422.5 | 513.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253738 | 126819 | 253737.9994
38909.5439 | 1 | 0 | 38909.5439 | 1 | 0 | 481 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5445 | 1 | 0 | 38909.5446 | 2 | 0 | 540 | 631 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253738 | 126819 | 253737.9994
38909.5452 | 1 | 0 | 38909.5452 | 1 | 0 | 598.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5459 | 1 | 0 | 38909.5459 | 1 | 0 | 657.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5466 | 1 | 0 | 38909.5466 | 1 | 0 | 716.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.5473 | 1 | 0 | 38909.5473 | 1 | 0 | 775 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253738 | 253738 | 253737.9994
38909.548 | 960 | 929 | 38909.548 | 967 | 933 | 834 | 925 | 58.6081 | 56.7155 | 59.0354 | 56.9597 | 0.58608 | 0.56716 | 0.59035 | 0.5696 | 0.018926 | 0.020757 | 9420.7888 | 6521.231 | 68.8453
38909.5486 | 1078 | 1049 | 38909.5486 | 1200 | 1054 | 892.5 | 983.5 | 65.812 | 64.0415 | 73.2601 | 64.3468 | 0.65812 | 0.64042 | 0.7326 | 0.64347 | 0.017705 | 0.089133 | 742.4262 | 625.5079 | 33.811
38909.5493 | 1078 | 1133 | 38909.5493 | 1159 | 1133 | 951.5 | 1042.5 | 65.812 | 69.1697 | 70.757 | 69.1697 | 0.65812 | 0.6917 | 0.70757 | 0.6917 | 0.033578 | 0.015873 | 1574.581 | 3001.546 | 27.9633
38909.55 | 927 | 989 | 38909.55 | 1018 | 1060 | 1010 | 1101 | 56.5934 | 60.3785 | 62.149 | 64.7131 | 0.56593 | 0.60379 | 0.62149 | 0.64713 | 0.037851 | 0.025641 | 2658.2362 | 71583.1745 | 62.8424
38909.5507 | 1178 | 1199 | 38909.5507 | 1191 | 1199 | 1069 | 1160 | 71.917 | 73.199 | 72.7106 | 73.199 | 0.71917 | 0.73199 | 0.72711 | 0.73199 | 0.012821 | 0.004884 | 2113.8225 | 2765.4512 | 12.9898
38909.5514 | 966 | 945 | 38909.5514 | 996 | 964 | 1127.5 | 1218.5 | 58.9744 | 57.6923 | 60.8059 | 58.8523 | 0.58974 | 0.57692 | 0.60806 | 0.58852 | 0.012821 | 0.019536 | 70429.8396 | 5035.3133 | 65.0966
38909.552 | 1038 | 1004 | 38909.552 | 1201 | 1179 | 1186.5 | 1277.5 | 63.37 | 61.2943 | 73.3211 | 71.978 | 0.6337 | 0.61294 | 0.73321 | 0.71978 | 0.020757 | 0.013431 | 3519.0738 | 11626.2229 | 49.0186
38909.5527 | 2474 | 3 | 38909.5527 | 2522 | 2 | 1245.5 | 1336.5 | 151.0379 | 0.18315 | 153.9683 | 0.1221 | 1.5104 | 0.0018315 | 1.5397 | 0.001221 | 1.5085 | 1.5385 | 3.1856 | 0.66661 | 13.5485
38909.5534 | 2282 | 0 | 38909.5534 | 2235 | 0 | 1304 | 1395 | 139.3162 | 0 | 136.4469 | 0 | 1.3932 | 0 | 1.3645 | 0 | 1.3932 | 1.3645 | 11.2349 | 13.574 | 9.8417
38909.5541 | 1967 | 1 | 38909.5541 | 2021 | 0 | 1363 | 1454 | 120.0855 | 0.06105 | 123.3822 | 0 | 1.2009 | 0.0006105 | 1.2338 | 0 | 1.2002 | 1.2338 | 29.1209 | 25.6002 | 11625.6512
38909.5548 | 2520 | 1 | 38909.5548 | 2303 | 0 | 1421.5 | 1512.5 | 153.8462 | 0.06105 | 140.5983 | 0 | 1.5385 | 0.0006105 | 1.406 | 0 | 1.5379 | 1.406 | 0.7325 | 10.2206 | 161.162
38909.5554 | 2245 | 1 | 38909.5555 | 2005 | 0 | 1480.5 | 1571.5 | 137.0574 | 0.06105 | 122.4054 | 0 | 1.3706 | 0.0006105 | 1.2241 | 0 | 1.37 | 1.2241 | 13.0959 | 26.6025 | 6143.6682
38909.5561 | 2038 | 1 | 38909.5561 | 2381 | 0 | 1539.5 | 1630.5 | 124.42 | 0.06105 | 145.3602 | 0 | 1.2442 | 0.0006105 | 1.4536 | 0 | 1.2436 | 1.4536 | 24.7484 | 6.6098 | 3096.1647
38909.5568 | 2108 | 1 | 38909.5568 | 2334 | 1 | 1598 | 1689 | 128.6935 | 0.06105 | 142.4908 | 0.06105 | 1.2869 | 0.0006105 | 1.4249 | 0.0006105 | 1.2863 | 1.4243 | 20.5372 | 8.7787 | 3465.2048
38909.5575 | 2163 | 545 | 38909.5575 | 1966 | 642 | 1657 | 1748 | 132.0513 | 33.2723 | 120.0244 | 39.1941 | 1.3205 | 0.33272 | 1.2002 | 0.39194 | 0.98779 | 0.8083 | 66.0194 | 51.934 | 10.6384
38909.5582 | 1138 | 1013 | 38909.5582 | 1092 | 1024 | 1715.5 | 1806.5 | 69.475 | 61.8437 | 66.6667 | 62.5153 | 0.69475 | 0.61844 | 0.66667 | 0.62515 | 0.076313 | 0.041514 | 882.9762 | 3015.0876 | 37.0133

## C3-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.2503 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38909.5377 | 1 | 0 | 38909.5377 | 1 | 0 | -51 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5384 | 1 | 0 | 38909.5384 | 1 | 0 | 8 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5391 | 1 | 0 | 38909.5391 | 1 | 0 | 66.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5398 | 1 | 0 | 38909.5398 | 1 | 0 | 125.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5404 | 1 | 0 | 38909.5405 | 1 | 0 | 184.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5411 | 1 | 0 | 38909.5411 | 1 | 0 | 243 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5418 | 1 | 0 | 38909.5418 | 1 | 0 | 302 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5425 | 1 | 0 | 38909.5425 | 1 | 0 | 360.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5432 | 1 | 0 | 38909.5432 | 1 | 0 | 419.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5438 | 1 | 0 | 38909.5439 | 1 | 0 | 478.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5445 | 1 | 0 | 38909.5445 | 1 | 0 | 537 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5452 | 1 | 0 | 38909.5452 | 1 | 0 | 595.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5459 | 1 | 0 | 38909.5459 | 1 | 0 | 654.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5466 | 1 | 0 | 38909.5466 | 1 | 0 | 713.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5472 | 1 | 0 | 38909.5473 | 1 | 0 | 772.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5479 | 1 | 0 | 38909.5479 | 1 | 0 | 831 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
38909.5486 | 1 | 1 | 38909.5486 | 1 | 0 | 890 | 981 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 654530822.44 | 255838 | 255638.0781
38909.5493 | 1 | 1 | 38909.5493 | 1 | 0 | 948.5 | 1039.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 654530822.44 | 255838 | 255638.0781
38909.55 | 1 | 2 | 38909.55 | 2 | 1 | 1007.5 | 1098.5 | 0.06105 | 0.1221 | 0.1221 | 0.06105 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 256038.1565 | 255837.9218 | 127769.0586
38909.5506 | 1 | 1 | 38909.5507 | 1 | 0 | 1066 | 1157 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 654530822.44 | 255838 | 255638.0781
38909.5513 | 1 | 1 | 38909.5513 | 1 | 0 | 1125 | 1216 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 654530822.44 | 255838 | 255638.0781
38909.552 | 2 | 6 | 38909.552 | 2 | 6 | 1183.5 | 1274.5 | 0.1221 | 0.3663 | 0.1221 | 0.3663 | 0.001221 | 0.003663 | 0.001221 | 0.003663 | 0.002442 | 0.002442 | 64084.5 | 64084.5 | 42456.7488
38909.5527 | 3 | 3 | 38909.5527 | 2429 | 3 | 1242.5 | 1333.5 | 0.18315 | 0.18315 | 148.2906 | 0.18315 | 0.0018315 | 0.0018315 | 1.4829 | 0.0018315 | 0 | 1.4811 | 4579.4425 | 5.3741 | 4340.7886
38909.5534 | 3 | 1 | 38909.5534 | 2023 | 1 | 1301.5 | 1392.5 | 0.18315 | 0.06105 | 123.5043 | 0.06105 | 0.0018315 | 0.0006105 | 1.235 | 0.0006105 | 0.001221 | 1.2344 | 144451.3616 | 434.2479 | 207706.6468
38909.554 | 2 | 0 | 38909.5541 | 2511 | 0 | 1360 | 1451 | 0.1221 | 0 | 153.2967 | 0 | 0.001221 | 0 | 1.533 | 0 | 0.001221 | 1.533 | 127869 | 1.9267 | 127868.9988
38909.5547 | 3 | 0 | 38909.5547 | 2507 | 0 | 1419 | 1510 | 0.18315 | 0 | 153.0525 | 0 | 0.0018315 | 0 | 1.5305 | 0 | 0.0018315 | 1.5305 | 85212.6667 | 2.0893 | 85212.6648
38909.5554 | 2 | 1 | 38909.5554 | 2543 | 0 | 1477.5 | 1568.5 | 0.1221 | 0.06105 | 155.2503 | 0 | 0.001221 | 0.0006105 | 1.5525 | 0 | 0.0006105 | 1.5525 | 1657.9416 | 0.65253 | 1657.2933
38909.5561 | 2 | 0 | 38909.5561 | 752 | 1 | 1536.5 | 1627.5 | 0.1221 | 0 | 45.9096 | 0.06105 | 0.001221 | 0 | 0.4591 | 0.0006105 | 0.001221 | 0.45849 | 127869 | 240.7963 | 127868.9988
38909.5568 | 2 | 1 | 38909.5568 | 2 | 1 | 1595.5 | 1686.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255538.1172
38909.5574 | 3 | 0 | 38909.5575 | 2107 | 0 | 1654 | 1745 | 0.18315 | 0 | 128.6325 | 0 | 0.0018315 | 0 | 1.2863 | 0 | 0.0018315 | 1.2863 | 85212.6667 | 21.4703 | 85212.6648
38909.5581 | 3 | 0 | 38909.5581 | 2035 | 1 | 1713 | 1804 | 0.18315 | 0 | 124.2369 | 0.06105 | 0.0018315 | 0 | 1.2424 | 0.0006105 | 0.0018315 | 1.2418 | 85212.6667 | 25.8299 | 85212.6648

## C3-6
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 150.8168 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38909.5377 | 1 | 0 | 38909.5377 | 1 | 0 | -53.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5384 | 1 | 0 | 38909.5384 | 1 | 0 | 5 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.539 | 1 | 0 | 38909.5391 | 1 | 0 | 64 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5397 | 1 | 0 | 38909.5397 | 1 | 0 | 122.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5404 | 1 | 0 | 38909.5404 | 1 | 0 | 181.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5411 | 1 | 0 | 38909.5411 | 1 | 0 | 240.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5418 | 1 | 0 | 38909.5418 | 1 | 0 | 299 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5424 | 1 | 0 | 38909.5425 | 1 | 0 | 358 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5431 | 1 | 0 | 38909.5431 | 1 | 0 | 416.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5438 | 1 | 0 | 38909.5438 | 1 | 0 | 475.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5445 | 1 | 0 | 38909.5445 | 1 | 0 | 534.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5452 | 1 | 0 | 38909.5452 | 1 | 0 | 593 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5458 | 1 | 0 | 38909.5459 | 1 | 0 | 652 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5465 | 1 | 0 | 38909.5465 | 1 | 0 | 710.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5472 | 1 | 0 | 38909.5472 | 1 | 0 | 769.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5479 | 1 | 0 | 38909.5479 | 1 | 0 | 828 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5486 | 1 | 0 | 38909.5486 | 1 | 0 | 887 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38909.5492 | 2 | 3 | 38909.5493 | 1 | 2 | 946 | 1037 | 0.1221 | 0.18315 | 0.06105 | 0.1221 | 0.001221 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 247138 | 247138 | 82146.0944
38909.5499 | 2 | 3 | 38909.5499 | 1 | 2 | 1004.5 | 1095.5 | 0.1221 | 0.18315 | 0.06105 | 0.1221 | 0.001221 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 247138 | 247138 | 82146.0944
38909.5506 | 1 | 1 | 38909.5506 | 2 | 0 | 1063.5 | 1154.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 304768410.22 | 123419 | 246638.1619
38909.5513 | 1 | 2 | 38909.5513 | 1 | 1 | 1122 | 1213 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 246937.919 | 609783558.7436 | 123368.9798
38909.552 | 2 | 7 | 38909.552 | 2 | 6 | 1181 | 1272 | 0.1221 | 0.42735 | 0.1221 | 0.3663 | 0.001221 | 0.0042735 | 0.001221 | 0.003663 | 0.0030525 | 0.002442 | 49479.5136 | 61897.1448 | 35105.855
38909.5527 | 2 | 3 | 38909.5527 | 2108 | 3 | 1239.5 | 1330.5 | 0.1221 | 0.18315 | 128.6935 | 0.18315 | 0.001221 | 0.0018315 | 1.2869 | 0.0018315 | 0.0006105 | 1.2851 | 15026.7033 | 19.4469 | 13379.4451
38909.5533 | 3 | 0 | 38909.5533 | 2014 | 1 | 1298.5 | 1389.5 | 0.18315 | 0 | 122.9548 | 0.06105 | 0.0018315 | 0 | 1.2295 | 0.0006105 | 0.0018315 | 1.2289 | 82246 | 22.7213 | 82245.9982
38909.554 | 3 | 0 | 38909.554 | 2454 | 1 | 1357.5 | 1448.5 | 0.18315 | 0 | 149.8168 | 0.06105 | 0.0018315 | 0 | 1.4982 | 0.0006105 | 0.0018315 | 1.4976 | 82246 | 0.70852 | 82245.9982
38909.5547 | 2 | 0 | 38909.5547 | 2046 | 0 | 1416 | 1507 | 0.1221 | 0 | 124.9084 | 0 | 0.001221 | 0 | 1.2491 | 0 | 0.001221 | 1.2491 | 123419 | 20.7419 | 123418.9988
38909.5554 | 3 | 1 | 38909.5554 | 2342 | 1 | 1475 | 1566 | 0.18315 | 0.06105 | 142.9792 | 0.06105 | 0.0018315 | 0.0006105 | 1.4298 | 0.0006105 | 0.001221 | 1.4292 | 15197.9256 | 7.0249 | 16188.9296
38909.5561 | 3 | 0 | 38909.5561 | 226 | 2 | 1533.5 | 1624.5 | 0.18315 | 0 | 13.7973 | 0.1221 | 0.0018315 | 0 | 0.13797 | 0.001221 | 0.0018315 | 0.13675 | 82246 | 1002.8482 | 82245.9982
38909.5567 | 3 | 1 | 38909.5567 | 3 | 1 | 1592.5 | 1683.5 | 0.18315 | 0.06105 | 0.18315 | 0.06105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.0006105 | 0.001221 | 0.001221 | 123419 | 123419 | 246438.3238
38909.5574 | 3 | 0 | 38909.5574 | 2025 | 0 | 1651.5 | 1742.5 | 0.18315 | 0 | 123.6264 | 0 | 0.0018315 | 0 | 1.2363 | 0 | 0.0018315 | 1.2363 | 82246 | 21.9941 | 82245.9982
38909.5581 | 3 | 1 | 38909.5581 | 2217 | 0 | 1710 | 1801 | 0.18315 | 0.06105 | 135.348 | 0 | 0.0018315 | 0.0006105 | 1.3535 | 0 | 0.001221 | 1.3535 | 36555.3808 | 21.0539 | 42895.7734

## C3-5
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 154.5409 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38909.5377 | 1 | 0 | 38909.5377 | 1 | 0 | -56.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5383 | 1 | 0 | 38909.5383 | 1 | 0 | 2.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.539 | 1 | 0 | 38909.539 | 1 | 0 | 61 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5397 | 1 | 0 | 38909.5397 | 1 | 0 | 120 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5404 | 1 | 0 | 38909.5404 | 1 | 0 | 178.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5411 | 1 | 0 | 38909.5411 | 1 | 0 | 237.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5417 | 1 | 0 | 38909.5417 | 1 | 0 | 296.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5424 | 1 | 0 | 38909.5424 | 1 | 0 | 355 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5431 | 1 | 0 | 38909.5431 | 1 | 0 | 414 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5438 | 1 | 0 | 38909.5438 | 1 | 0 | 472.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5445 | 1 | 0 | 38909.5445 | 1 | 0 | 531.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5451 | 1 | 0 | 38909.5452 | 1 | 0 | 590.5 | 681.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5458 | 1 | 0 | 38909.5458 | 1 | 0 | 649 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5465 | 1 | 0 | 38909.5465 | 1 | 0 | 708 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5472 | 1 | 0 | 38909.5472 | 1 | 0 | 766.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5479 | 1 | 0 | 38909.5479 | 1 | 0 | 825.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
38909.5485 | 1 | 1 | 38909.5486 | 1 | 0 | 884 | 975 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 640282294.44 | 253038 | 252838.079
38909.5492 | 2 | 6 | 38909.5492 | 2 | 5 | 943 | 1034 | 0.1221 | 0.3663 | 0.1221 | 0.30525 | 0.001221 | 0.003663 | 0.001221 | 0.0030525 | 0.002442 | 0.0018315 | 63346.9035 | 84535.0797 | 42006.642
38909.5499 | 2 | 6 | 38909.5499 | 1 | 5 | 1001.5 | 1092.5 | 0.1221 | 0.3663 | 0.06105 | 0.30525 | 0.001221 | 0.003663 | 0.0006105 | 0.0030525 | 0.002442 | 0.002442 | 63384.5 | 63384.5 | 41990.0867
38909.5506 | 1 | 1 | 38909.5506 | 1 | 0 | 1060.5 | 1151.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 640282294.44 | 253038 | 252838.079
38909.5513 | 1 | 3 | 38909.5513 | 1 | 2 | 1119.5 | 1210.5 | 0.06105 | 0.18315 | 0.06105 | 0.1221 | 0.0006105 | 0.0018315 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 126593.9259 | 253438.3958 | 84212.7719
38909.5519 | 2 | 7 | 38909.552 | 2 | 6 | 1178 | 1269 | 0.1221 | 0.42735 | 0.1221 | 0.3663 | 0.001221 | 0.0042735 | 0.001221 | 0.003663 | 0.0030525 | 0.002442 | 50699.5157 | 63422.1413 | 35977.2733
38909.5526 | 3 | 3 | 38909.5526 | 2301 | 4 | 1237 | 1328 | 0.18315 | 0.18315 | 140.4762 | 0.2442 | 0.0018315 | 0.0018315 | 1.4048 | 0.002442 | 0 | 1.4023 | 8452.7091 | 10.0294 | 7673.1128
38909.5533 | 2 | 0 | 38909.5533 | 2201 | 0 | 1295.5 | 1386.5 | 0.1221 | 0 | 134.3712 | 0 | 0.001221 | 0 | 1.3437 | 0 | 0.001221 | 1.3437 | 126469 | 15.0104 | 126468.9988
38909.554 | 3 | 1 | 38909.554 | 2049 | 0 | 1354.5 | 1445.5 | 0.18315 | 0.06105 | 125.0916 | 0 | 0.0018315 | 0.0006105 | 1.2509 | 0 | 0.001221 | 1.2509 | 112488.0049 | 403.7328 | 202564.976
38909.5547 | 3 | 0 | 38909.5547 | 2515 | 0 | 1413.5 | 1504.5 | 0.18315 | 0 | 153.5409 | 0 | 0.0018315 | 0 | 1.5354 | 0 | 0.0018315 | 1.5354 | 84279.3333 | 0.65129 | 84279.3315
38909.5553 | 3 | 1 | 38909.5554 | 2199 | 1 | 1472 | 1563 | 0.18315 | 0.06105 | 134.2491 | 0.06105 | 0.0018315 | 0.0006105 | 1.3425 | 0.0006105 | 0.001221 | 1.3419 | 54810.8544 | 38.2714 | 69953.9737
38909.556 | 3 | 1 | 38909.556 | 2014 | 1 | 1531 | 1622 | 0.18315 | 0.06105 | 122.9548 | 0.06105 | 0.0018315 | 0.0006105 | 1.2295 | 0.0006105 | 0.001221 | 1.2289 | 133723.0377 | 915.4049 | 227847.6334
38909.5567 | 2 | 1 | 38909.5567 | 2193 | 1 | 1589.5 | 1680.5 | 0.1221 | 0.06105 | 133.8828 | 0.06105 | 0.001221 | 0.0006105 | 1.3388 | 0.0006105 | 0.0006105 | 1.3382 | 46174.0057 | 22.3317 | 46155.7506
38909.5574 | 3 | 1 | 38909.5574 | 2423 | 1 | 1648.5 | 1739.5 | 0.18315 | 0.06105 | 147.9243 | 0.06105 | 0.0018315 | 0.0006105 | 1.4792 | 0.0006105 | 0.001221 | 1.4786 | 12426.0772 | 5.4504 | 13063.1703
38909.5581 | 3 | 0 | 38909.5581 | 1605 | 1 | 1707.5 | 1798.5 | 0.18315 | 0 | 97.9853 | 0.06105 | 0.0018315 | 0 | 0.97985 | 0.0006105 | 0.0018315 | 0.97924 | 84279.3333 | 57.8167 | 84279.3315

## C3-4
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 155.0904 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38909.5376 | 1 | 0 | 38909.5376 | 1 | 0 | -59.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5383 | 1 | 0 | 38909.5383 | 1 | 0 | -0.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.539 | 1 | 0 | 38909.539 | 2 | 0 | 58.5 | 149.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253938 | 126919 | 253937.9994
38909.5397 | 1 | 0 | 38909.5397 | 2 | 0 | 117 | 208 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 253938 | 126919 | 253937.9994
38909.5403 | 1 | 0 | 38909.5404 | 1 | 0 | 176 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.541 | 1 | 0 | 38909.541 | 1 | 0 | 234.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5417 | 1 | 0 | 38909.5417 | 1 | 0 | 293.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5424 | 1 | 0 | 38909.5424 | 1 | 0 | 352.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5431 | 1 | 0 | 38909.5431 | 1 | 0 | 411 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5437 | 1 | 0 | 38909.5438 | 1 | 0 | 470 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5444 | 1 | 0 | 38909.5444 | 1 | 0 | 528.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5451 | 1 | 0 | 38909.5451 | 1 | 0 | 587.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5458 | 1 | 0 | 38909.5458 | 1 | 0 | 646 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5465 | 1 | 0 | 38909.5465 | 1 | 0 | 705 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5471 | 1 | 0 | 38909.5472 | 1 | 0 | 763.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5478 | 1 | 0 | 38909.5478 | 1 | 0 | 822.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253938 | 253938 | 253937.9994
38909.5485 | 1 | 1 | 38909.5485 | 1 | 0 | 881.5 | 972.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 644845078.44 | 253938 | 253738.0787
38909.5492 | 3 | 10 | 38909.5492 | 2 | 7 | 940 | 1031 | 0.18315 | 0.6105 | 0.1221 | 0.42735 | 0.0018315 | 0.006105 | 0.001221 | 0.0042735 | 0.0042735 | 0.0030525 | 36350.1791 | 50963.8836 | 25224.3055
38909.5499 | 2 | 11 | 38909.5499 | 2 | 7 | 999 | 1090 | 0.1221 | 0.67155 | 0.1221 | 0.42735 | 0.001221 | 0.0067155 | 0.001221 | 0.0042735 | 0.0054945 | 0.0030525 | 28271.9495 | 51020.2474 | 22931.2365
38909.5505 | 1 | 1 | 38909.5506 | 1 | 0 | 1057.5 | 1148.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 644845078.44 | 253938 | 253738.0787
38909.5512 | 2 | 4 | 38909.5512 | 1 | 3 | 1116.5 | 1207.5 | 0.1221 | 0.2442 | 0.06105 | 0.18315 | 0.001221 | 0.002442 | 0.0006105 | 0.0018315 | 0.001221 | 0.001221 | 127119 | 127119 | 63309.6965
38909.5519 | 3 | 8 | 38909.5519 | 3 | 7 | 1175.5 | 1266.5 | 0.18315 | 0.4884 | 0.18315 | 0.42735 | 0.0018315 | 0.004884 | 0.0018315 | 0.0042735 | 0.0030525 | 0.002442 | 50875.4812 | 63653.4533 | 31567.657
38909.5526 | 3 | 4 | 38909.5526 | 2262 | 3 | 1234 | 1325 | 0.18315 | 0.2442 | 138.0952 | 0.18315 | 0.0018315 | 0.002442 | 1.381 | 0.0018315 | 0.0006105 | 1.3791 | 8065.4772 | 13.1321 | 7351.7047
38909.5533 | 3 | 1 | 38909.5533 | 2516 | 0 | 1293 | 1384 | 0.18315 | 0.06105 | 153.602 | 0 | 0.0018315 | 0.0006105 | 1.536 | 0 | 0.001221 | 1.536 | 2507.3087 | 1.0081 | 2531.3339
38909.5539 | 3 | 0 | 38909.554 | 2443 | 0 | 1351.5 | 1442.5 | 0.18315 | 0 | 149.1453 | 0 | 0.0018315 | 0 | 1.4915 | 0 | 0.0018315 | 1.4915 | 84579.3333 | 3.9861 | 84579.3315
38909.5546 | 3 | 0 | 38909.5546 | 2212 | 0 | 1410.5 | 1501.5 | 0.18315 | 0 | 135.0427 | 0 | 0.0018315 | 0 | 1.3504 | 0 | 0.0018315 | 1.3504 | 84579.3333 | 14.8454 | 84579.3315
38909.5553 | 2 | 1 | 38909.5553 | 2524 | 1 | 1469.5 | 1560.5 | 0.1221 | 0.06105 | 154.0904 | 0.06105 | 0.001221 | 0.0006105 | 1.5409 | 0.0006105 | 0.0006105 | 1.5403 | 1658.7143 | 0.65775 | 1658.0608
38909.556 | 2 | 1 | 38909.556 | 2475 | 0 | 1528 | 1619 | 0.1221 | 0.06105 | 151.0989 | 0 | 0.001221 | 0.0006105 | 1.511 | 0 | 0.0006105 | 1.511 | 6887.3633 | 2.789 | 6884.65
38909.5567 | 2 | 1 | 38909.5567 | 2457 | 1 | 1587 | 1678 | 0.1221 | 0.06105 | 150 | 0.06105 | 0.001221 | 0.0006105 | 1.5 | 0.0006105 | 0.0006105 | 1.4994 | 8920.4813 | 3.6422 | 8916.9671
38909.5573 | 3 | 1 | 38909.5574 | 2458 | 0 | 1645.5 | 1736.5 | 0.18315 | 0.06105 | 150.0611 | 0 | 0.0018315 | 0.0006105 | 1.5006 | 0 | 0.001221 | 1.5006 | 9115.0235 | 3.8704 | 9450.9369
38909.558 | 3 | 1 | 38909.558 | 1709 | 1 | 1704.5 | 1795.5 | 0.18315 | 0.06105 | 104.3346 | 0.06105 | 0.0018315 | 0.0006105 | 1.0433 | 0.0006105 | 0.001221 | 1.0427 | 4662966.3669 | 51.3984 | 86107.8698

## C2-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 142.6972 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38909.5376 | 1 | 0 | 38909.5376 | 1 | 0 | -62 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5383 | 1 | 0 | 38909.5383 | 1 | 0 | -3.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5389 | 1 | 0 | 38909.539 | 1 | 0 | 55.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5396 | 1 | 0 | 38909.5396 | 1 | 0 | 114.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5403 | 1 | 0 | 38909.5403 | 1 | 0 | 173 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.541 | 1 | 0 | 38909.541 | 1 | 0 | 232 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5417 | 1 | 0 | 38909.5417 | 1 | 0 | 290.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5423 | 1 | 0 | 38909.5424 | 1 | 0 | 349.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.543 | 1 | 0 | 38909.543 | 1 | 0 | 408.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5437 | 1 | 0 | 38909.5437 | 1 | 0 | 467 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5444 | 1 | 0 | 38909.5444 | 1 | 0 | 526 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5451 | 1 | 0 | 38909.5451 | 1 | 0 | 584.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5458 | 1 | 0 | 38909.5458 | 1 | 0 | 643.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5464 | 1 | 0 | 38909.5464 | 1 | 0 | 702.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5471 | 1 | 0 | 38909.5471 | 1 | 0 | 761 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 233638 | 233638 | 233637.9994
38909.5478 | 1 | 1 | 38909.5478 | 1 | 0 | 820 | 911 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 545867150.44 | 233638 | 233438.0856
38909.5485 | 1 | 1 | 38909.5485 | 1 | 0 | 878.5 | 969.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 545867150.44 | 233638 | 233438.0856
38909.5492 | 947 | 919 | 38909.5492 | 1135 | 1106 | 937.5 | 1028.5 | 57.8144 | 56.105 | 69.2918 | 67.5214 | 0.57814 | 0.56105 | 0.69292 | 0.67521 | 0.017094 | 0.017705 | 9341.2875 | 7006.8395 | 50.571
38909.5498 | 1186 | 1198 | 38909.5498 | 1011 | 981 | 996 | 1087 | 72.4054 | 73.138 | 61.7216 | 59.8901 | 0.72405 | 0.73138 | 0.61722 | 0.5989 | 0.007326 | 0.018315 | 1757.5871 | 2238.8704 | 3.7251
38909.5505 | 1 | 1 | 38909.5505 | 1 | 0 | 1055 | 1146 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 545867150.44 | 233638 | 233438.0856
38909.5512 | 2 | 4 | 38909.5512 | 1 | 4 | 1113.5 | 1204.5 | 0.1221 | 0.2442 | 0.06105 | 0.2442 | 0.001221 | 0.002442 | 0.0006105 | 0.002442 | 0.001221 | 0.0018315 | 117069.3004 | 77968.1333 | 58209.8415
38909.5519 | 621 | 601 | 38909.5519 | 20 | 23 | 1172.5 | 1263.5 | 37.9121 | 36.6911 | 1.221 | 1.4042 | 0.37912 | 0.36691 | 0.01221 | 0.014042 | 0.01221 | 0.0018315 | 8898.2316 | 84528.9687 | 185.3681
38909.5526 | 3 | 4 | 38909.5526 | 1915 | 4 | 1231.5 | 1322.5 | 0.18315 | 0.2442 | 116.9109 | 0.2442 | 0.0018315 | 0.002442 | 1.1691 | 0.002442 | 0.0006105 | 1.1667 | 13653.1613 | 24.8482 | 11595.2426
38909.5532 | 3 | 1 | 38909.5533 | 2321 | 1 | 1290 | 1381 | 0.18315 | 0.06105 | 141.6972 | 0.06105 | 0.0018315 | 0.0006105 | 1.417 | 0.0006105 | 0.001221 | 1.4164 | 1671.7154 | 0.72653 | 1683.0521
38909.5539 | 2 | 0 | 38909.5539 | 2284 | 0 | 1349 | 1440 | 0.1221 | 0 | 139.4383 | 0 | 0.001221 | 0 | 1.3944 | 0 | 0.001221 | 1.3944 | 116769 | 2.3371 | 116768.9988
38909.5546 | 2072 | 35 | 38909.5546 | 1948 | 1 | 1407.5 | 1498.5 | 126.4957 | 2.1368 | 118.9255 | 0.06105 | 1.265 | 0.021368 | 1.1893 | 0.0006105 | 1.2436 | 1.1886 | 14.2477 | 20.0713 | 110.0306
38909.5553 | 2 | 1 | 38909.5553 | 2095 | 1 | 1466.5 | 1557.5 | 0.1221 | 0.06105 | 127.8999 | 0.06105 | 0.001221 | 0.0006105 | 1.279 | 0.0006105 | 0.0006105 | 1.2784 | 30570.4413 | 15.0617 | 30557.3511
38909.556 | 3 | 1 | 38909.556 | 4 | 1 | 1525.5 | 1616.5 | 0.18315 | 0.06105 | 0.2442 | 0.06105 | 0.0018315 | 0.0006105 | 0.002442 | 0.0006105 | 0.001221 | 0.0018315 | 116794.059 | 77801.5381 | 233038.4706
38909.5566 | 3 | 5 | 38909.5567 | 23 | 19 | 1584 | 1675 | 0.18315 | 0.30525 | 1.4042 | 1.16 | 0.0018315 | 0.0030525 | 0.014042 | 0.0116 | 0.001221 | 0.002442 | 117223.4481 | 58094.9058 | 46507.5456
38909.5573 | 1781 | 50 | 38909.5573 | 1987 | 0 | 1643 | 1734 | 108.7302 | 3.0525 | 121.3065 | 0 | 1.0873 | 0.030525 | 1.2131 | 0 | 1.0568 | 1.2131 | 38.4386 | 17.6336 | 151.8156
38909.558 | 2086 | 0 | 38909.558 | 2016 | 0 | 1701.5 | 1792.5 | 127.3504 | 0 | 123.0769 | 0 | 1.2735 | 0 | 1.2308 | 0 | 1.2735 | 1.2308 | 12.0508 | 15.9415 | 10.7773

## C2-6
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.9829 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38909.5375 | 1 | 0 | 38909.5376 | 1 | 0 | -65 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5382 | 1 | 0 | 38909.5383 | 1 | 0 | -6 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5389 | 1 | 0 | 38909.5389 | 1 | 0 | 52.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5396 | 1 | 0 | 38909.5396 | 1 | 0 | 111.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5403 | 1 | 0 | 38909.5403 | 1 | 0 | 170.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5409 | 1 | 0 | 38909.541 | 1 | 0 | 229 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5416 | 1 | 0 | 38909.5417 | 1 | 0 | 288 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5423 | 1 | 0 | 38909.5423 | 1 | 0 | 346.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.543 | 1 | 0 | 38909.543 | 1 | 0 | 405.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5437 | 1 | 0 | 38909.5437 | 1 | 0 | 464.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5444 | 1 | 0 | 38909.5444 | 1 | 0 | 523 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.545 | 1 | 0 | 38909.5451 | 1 | 0 | 582 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5457 | 1 | 0 | 38909.5457 | 1 | 0 | 640.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5464 | 1 | 0 | 38909.5464 | 1 | 0 | 699.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5471 | 1 | 0 | 38909.5471 | 1 | 0 | 758.5 | 849.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5478 | 1 | 0 | 38909.5478 | 1 | 0 | 817 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257038 | 257038 | 257037.9994
38909.5484 | 1 | 1 | 38909.5485 | 1 | 0 | 876 | 967 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 660685334.44 | 257038 | 256838.0778
38909.5491 | 936 | 967 | 38909.5491 | 1044 | 1015 | 934.5 | 1025.5 | 57.1429 | 59.0354 | 63.7363 | 61.9658 | 0.57143 | 0.59035 | 0.63736 | 0.61966 | 0.018926 | 0.017705 | 7854.3405 | 9500.2807 | 68.399
38909.5498 | 1131 | 1105 | 38909.5498 | 1167 | 1197 | 993.5 | 1084.5 | 69.0476 | 67.4603 | 71.2454 | 73.0769 | 0.69048 | 0.6746 | 0.71245 | 0.73077 | 0.015873 | 0.018315 | 20813.937 | 5791.4856 | 29.836
38909.5505 | 599 | 873 | 38909.5505 | 1 | 2 | 1052.5 | 1143.5 | 36.569 | 53.2967 | 0.06105 | 0.1221 | 0.36569 | 0.53297 | 0.0006105 | 0.001221 | 0.16728 | 0.0006105 | 720.4919 | 355805.3402 | 125.8959
38909.5512 | 2 | 5 | 38909.5512 | 2 | 5 | 1111 | 1202 | 0.1221 | 0.30525 | 0.1221 | 0.30525 | 0.001221 | 0.0030525 | 0.001221 | 0.0030525 | 0.0018315 | 0.0018315 | 85812.6667 | 85812.6667 | 51227.9026
38909.5518 | 315 | 367 | 38909.5519 | 478 | 459 | 1169.5 | 1260.5 | 19.2308 | 22.4054 | 29.1819 | 28.022 | 0.19231 | 0.22405 | 0.29182 | 0.28022 | 0.031746 | 0.0116 | 4470.8327 | 23969.6628 | 512.6786
38909.5525 | 3 | 5 | 38909.5525 | 2011 | 5 | 1228.5 | 1319.5 | 0.18315 | 0.30525 | 122.7717 | 0.30525 | 0.0018315 | 0.0030525 | 1.2277 | 0.0030525 | 0.001221 | 1.2247 | 16154.5068 | 35.9742 | 13563.686
38909.5532 | 3 | 1 | 38909.5532 | 2176 | 1 | 1287.5 | 1378.5 | 0.18315 | 0.06105 | 132.8449 | 0.06105 | 0.0018315 | 0.0006105 | 1.3284 | 0.0006105 | 0.001221 | 1.3278 | 73360.4783 | 66.6205 | 102652.4791
38909.5539 | 2 | 0 | 38909.5539 | 2436 | 0 | 1346 | 1437 | 0.1221 | 0 | 148.7179 | 0 | 0.001221 | 0 | 1.4872 | 0 | 0.001221 | 1.4872 | 128469 | 5.5575 | 128468.9988
38909.5546 | 3 | 1 | 38909.5546 | 2394 | 0 | 1405 | 1496 | 0.18315 | 0.06105 | 146.1538 | 0 | 0.0018315 | 0.0006105 | 1.4615 | 0 | 0.001221 | 1.4615 | 22340.6389 | 10.5303 | 24459.5117
38909.5552 | 3 | 1 | 38909.5553 | 65 | 2 | 1463.5 | 1554.5 | 0.18315 | 0.06105 | 3.9683 | 0.1221 | 0.0018315 | 0.0006105 | 0.039683 | 0.001221 | 0.001221 | 0.038462 | 130053.4625 | 3978.4781 | 250443.0538
38909.5559 | 2 | 2 | 38909.5559 | 49 | 1 | 1522.5 | 1613.5 | 0.1221 | 0.1221 | 2.9915 | 0.06105 | 0.001221 | 0.001221 | 0.029915 | 0.0006105 | 0 | 0.029304 | 6750990.3379 | 5254.9567 | 125971.8004
38909.5566 | 140 | 166 | 38909.5566 | 601 | 581 | 1581.5 | 1672.5 | 8.547 | 10.1343 | 36.6911 | 35.4701 | 0.08547 | 0.10134 | 0.36691 | 0.3547 | 0.015873 | 0.01221 | 9798.1805 | 14003.7961 | 1355.0107
38909.5573 | 2256 | 1 | 38909.5573 | 2012 | 0 | 1640 | 1731 | 137.7289 | 0.06105 | 122.8327 | 0 | 1.3773 | 0.0006105 | 1.2283 | 0 | 1.3767 | 1.2283 | 14.0082 | 27.8022 | 6839.0469
38909.558 | 2555 | 0 | 38909.558 | 2332 | 0 | 1699 | 1790 | 155.9829 | 0 | 142.3687 | 0 | 1.5598 | 0 | 1.4237 | 0 | 1.5598 | 1.4237 | 0.6411 | 10.265 | 0.91873

## C2-5
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 146.7875 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38909.5375 | 1 | 0 | 38909.5375 | 1 | 0 | -67.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5382 | 1 | 0 | 38909.5382 | 5 | 0 | -9 | 82 | 0.06105 | 0 | 0.30525 | 0 | 0.0006105 | 0 | 0.0030525 | 0 | 0.0006105 | 0.0030525 | 240338 | 47987.6 | 240337.9994
38909.5389 | 1 | 0 | 38909.5389 | 1 | 0 | 50 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5396 | 1 | 0 | 38909.5396 | 1 | 0 | 108.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5402 | 1 | 0 | 38909.5403 | 1 | 0 | 167.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5409 | 1 | 0 | 38909.5409 | 1 | 0 | 226.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5416 | 1 | 0 | 38909.5416 | 1 | 0 | 285 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5423 | 1 | 0 | 38909.5423 | 1 | 0 | 344 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.543 | 1 | 0 | 38909.543 | 1 | 0 | 402.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5436 | 1 | 0 | 38909.5437 | 1 | 0 | 461.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5443 | 1 | 0 | 38909.5443 | 1 | 0 | 520.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.545 | 1 | 0 | 38909.545 | 1 | 0 | 579 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5457 | 1 | 0 | 38909.5457 | 1 | 0 | 638 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5464 | 1 | 0 | 38909.5464 | 1 | 0 | 696.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.547 | 1 | 0 | 38909.5471 | 1 | 0 | 755.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240338 | 240338 | 240337.9994
38909.5477 | 1 | 1 | 38909.5477 | 1 | 0 | 814.5 | 905.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 577623542.44 | 240338 | 240138.0832
38909.5484 | 1 | 2 | 38909.5484 | 1 | 1 | 873 | 964 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240337.9168 | 577623342.4775 | 120068.9792
38909.5491 | 1 | 2 | 38909.5491 | 1 | 1 | 931.5 | 1022.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 240337.9168 | 577623342.4775 | 120068.9792
38909.5498 | 2 | 3 | 38909.5498 | 1 | 2 | 990.5 | 1081.5 | 0.1221 | 0.18315 | 0.06105 | 0.1221 | 0.001221 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 240538 | 240538 | 79946.097
38909.5505 | 1 | 2 | 38909.5505 | 1 | 2 | 1049.5 | 1140.5 | 0.06105 | 0.1221 | 0.06105 | 0.1221 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 240538 | 240538 | 120019.1039
38909.5511 | 2 | 6 | 38909.5511 | 2 | 6 | 1108 | 1199 | 0.1221 | 0.3663 | 0.1221 | 0.3663 | 0.001221 | 0.003663 | 0.001221 | 0.003663 | 0.002442 | 0.002442 | 60209.5 | 60209.5 | 39873.4422
38909.5518 | 1119 | 1090 | 38909.5518 | 656 | 589 | 1167 | 1258 | 68.315 | 66.5446 | 40.0488 | 35.9585 | 0.68315 | 0.66545 | 0.40049 | 0.35958 | 0.017705 | 0.040904 | 7190.0574 | 9799.6791 | 17.7437
38909.5525 | 3 | 5 | 38909.5525 | 2097 | 5 | 1225.5 | 1316.5 | 0.18315 | 0.30525 | 128.022 | 0.30525 | 0.0018315 | 0.0030525 | 1.2802 | 0.0030525 | 0.001221 | 1.2772 | 7497.1375 | 16.6497 | 6840.8143
38909.5532 | 3 | 1 | 38909.5532 | 2266 | 1 | 1284.5 | 1375.5 | 0.18315 | 0.06105 | 138.3394 | 0.06105 | 0.0018315 | 0.0006105 | 1.3834 | 0.0006105 | 0.001221 | 1.3828 | 16713.3729 | 8.0854 | 17956.1432
38909.5539 | 3 | 0 | 38909.5539 | 2388 | 0 | 1343.5 | 1434.5 | 0.18315 | 0 | 145.7875 | 0 | 0.0018315 | 0 | 1.4579 | 0 | 0.0018315 | 1.4579 | 80046 | 0.68593 | 80045.9982
38909.5545 | 3 | 0 | 38909.5545 | 2387 | 0 | 1402 | 1493 | 0.18315 | 0 | 145.7265 | 0 | 0.0018315 | 0 | 1.4573 | 0 | 0.0018315 | 1.4573 | 80046 | 0.72811 | 80045.9982
38909.5552 | 3 | 2 | 38909.5552 | 2100 | 1 | 1461 | 1552 | 0.18315 | 0.1221 | 128.2051 | 0.06105 | 0.0018315 | 0.001221 | 1.2821 | 0.0006105 | 0.0006105 | 1.2814 | 18772.5059 | 16.9606 | 17396.8897
38909.5559 | 3 | 2 | 38909.5559 | 2189 | 1 | 1519.5 | 1610.5 | 0.18315 | 0.1221 | 133.6386 | 0.06105 | 0.0018315 | 0.001221 | 1.3364 | 0.0006105 | 0.0006105 | 1.3358 | 12431.0133 | 10.9184 | 11809.3365
38909.5566 | 2 | 2 | 38909.5566 | 2052 | 2 | 1578.5 | 1669.5 | 0.1221 | 0.1221 | 125.2747 | 0.1221 | 0.001221 | 0.001221 | 1.2527 | 0.001221 | 0 | 1.2515 | 20647.4796 | 17.1892 | 17604.2611
38909.5573 | 2097 | 0 | 38909.5573 | 2177 | 0 | 1637.5 | 1728.5 | 128.022 | 0 | 132.906 | 0 | 1.2802 | 0 | 1.3291 | 0 | 1.2802 | 1.3291 | 14.6581 | 10.4446 | 13.3779
38909.5579 | 2030 | 0 | 38909.558 | 1803 | 1 | 1696 | 1787 | 123.9316 | 0 | 110.0733 | 0.06105 | 1.2393 | 0 | 1.1007 | 0.0006105 | 1.2393 | 1.1001 | 18.4424 | 33.4284 | 17.203

## C2-4
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.5556 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38909.5375 | 1 | 0 | 38909.5375 | 1 | 0 | -70.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5382 | 1 | 0 | 38909.5382 | 1 | 0 | -11.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5388 | 1 | 0 | 38909.5389 | 1 | 0 | 47 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5395 | 1 | 0 | 38909.5395 | 1 | 0 | 106 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5402 | 1 | 0 | 38909.5402 | 1 | 0 | 164.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5409 | 1 | 0 | 38909.5409 | 1 | 0 | 223.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5416 | 1 | 0 | 38909.5416 | 1 | 0 | 282.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5422 | 1 | 0 | 38909.5423 | 1 | 0 | 341 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5429 | 1 | 0 | 38909.543 | 1 | 0 | 400 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5436 | 1 | 0 | 38909.5436 | 1 | 0 | 458.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5443 | 1 | 0 | 38909.5443 | 1 | 0 | 517.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.545 | 1 | 0 | 38909.545 | 1 | 0 | 576.5 | 667.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5456 | 1 | 0 | 38909.5457 | 1 | 0 | 635 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5463 | 1 | 0 | 38909.5463 | 1 | 0 | 693.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.547 | 1 | 0 | 38909.547 | 1 | 0 | 752.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38909.5477 | 2 | 2 | 38909.5477 | 1 | 0 | 811.5 | 902.5 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 328417682.22 | 256338 | 127969.078
38909.5484 | 2 | 5 | 38909.5484 | 1 | 4 | 870 | 961 | 0.1221 | 0.30525 | 0.06105 | 0.2442 | 0.001221 | 0.0030525 | 0.0006105 | 0.002442 | 0.0018315 | 0.0018315 | 85579.3333 | 85579.3333 | 51087.9035
38909.5491 | 2 | 5 | 38909.5491 | 2 | 4 | 929 | 1020 | 0.1221 | 0.30525 | 0.1221 | 0.2442 | 0.001221 | 0.0030525 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 85523.662 | 128419.3129 | 51107.8024
38909.5497 | 2 | 6 | 38909.5497 | 2 | 4 | 987.5 | 1078.5 | 0.1221 | 0.3663 | 0.1221 | 0.2442 | 0.001221 | 0.003663 | 0.001221 | 0.002442 | 0.002442 | 0.001221 | 64134.3535 | 128519.783 | 42573.2075
38909.5504 | 2 | 5 | 38909.5504 | 2 | 4 | 1046.5 | 1137.5 | 0.1221 | 0.30525 | 0.1221 | 0.2442 | 0.001221 | 0.0030525 | 0.001221 | 0.002442 | 0.0018315 | 0.001221 | 85523.662 | 128419.3129 | 51107.8024
38909.5511 | 2 | 8 | 38909.5511 | 2 | 7 | 1105.5 | 1196.5 | 0.1221 | 0.4884 | 0.1221 | 0.42735 | 0.001221 | 0.004884 | 0.001221 | 0.0042735 | 0.003663 | 0.0030525 | 42817.3691 | 51415.714 | 31867.7694
38909.5518 | 936 | 969 | 38909.5518 | 928 | 960 | 1164.5 | 1255.5 | 57.1429 | 59.1575 | 56.6545 | 58.6081 | 0.57143 | 0.59158 | 0.56654 | 0.58608 | 0.020147 | 0.019536 | 7543.353 | 8490.2824 | 67.2553
38909.5525 | 2 | 6 | 38909.5525 | 2156 | 6 | 1223 | 1314 | 0.1221 | 0.3663 | 131.6239 | 0.3663 | 0.001221 | 0.003663 | 1.3162 | 0.003663 | 0.002442 | 1.3126 | 9287.6279 | 25.4354 | 8639.5783
38909.5531 | 2 | 1 | 38909.5531 | 1968 | 1 | 1281.5 | 1372.5 | 0.1221 | 0.06105 | 120.1465 | 0.06105 | 0.001221 | 0.0006105 | 1.2015 | 0.0006105 | 0.0006105 | 1.2009 | 111493.4252 | 77.0277 | 111449.9135
38909.5538 | 3 | 0 | 38909.5538 | 2088 | 0 | 1340.5 | 1431.5 | 0.18315 | 0 | 127.4725 | 0 | 0.0018315 | 0 | 1.2747 | 0 | 0.0018315 | 1.2747 | 85379.3333 | 22.8151 | 85379.3315
38909.5545 | 3 | 0 | 38909.5545 | 2399 | 0 | 1399.5 | 1490.5 | 0.18315 | 0 | 146.4591 | 0 | 0.0018315 | 0 | 1.4646 | 0 | 0.0018315 | 1.4646 | 85379.3333 | 6.8937 | 85379.3315
38909.5552 | 3 | 4 | 38909.5552 | 1977 | 3 | 1458 | 1549 | 0.18315 | 0.2442 | 120.696 | 0.18315 | 0.0018315 | 0.002442 | 1.207 | 0.0018315 | 0.0006105 | 1.2051 | 20585.1636 | 34.9563 | 16560.2905
38909.5559 | 2 | 5 | 38909.5559 | 2472 | 3 | 1517 | 1608 | 0.1221 | 0.30525 | 150.9158 | 0.18315 | 0.001221 | 0.0030525 | 1.5092 | 0.0018315 | 0.0018315 | 1.5073 | 1961.3889 | 3.9172 | 1928.0449
38909.5565 | 2 | 5 | 38909.5566 | 2237 | 3 | 1575.5 | 1666.5 | 0.1221 | 0.30525 | 136.569 | 0.18315 | 0.001221 | 0.0030525 | 1.3657 | 0.0018315 | 0.0018315 | 1.3639 | 8233.8878 | 17.781 | 7721.5747
38909.5572 | 2118 | 0 | 38909.5572 | 2031 | 1 | 1634.5 | 1725.5 | 129.304 | 0 | 123.9927 | 0.06105 | 1.293 | 0 | 1.2399 | 0.0006105 | 1.293 | 1.2393 | 21.0755 | 26.3241 | 19.7825
38909.5579 | 2548 | 1 | 38909.5579 | 2228 | 1 | 1693.5 | 1784.5 | 155.5556 | 0.06105 | 136.0195 | 0.06105 | 1.5556 | 0.0006105 | 1.3602 | 0.0006105 | 1.5549 | 1.3596 | 0.64467 | 16.2355 | 214.824

## C2-3
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 130.9145 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38909.5375 | 1 | 0 | 38909.5375 | 1 | 0 | -73.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5381 | 1 | 0 | 38909.5381 | 1 | 0 | -14.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5388 | 1 | 0 | 38909.5388 | 1 | 0 | 44.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5395 | 1 | 0 | 38909.5395 | 1 | 0 | 103 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5402 | 1 | 0 | 38909.5402 | 1 | 0 | 162 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5409 | 1 | 0 | 38909.5409 | 1 | 0 | 220.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5415 | 1 | 0 | 38909.5416 | 2 | 0 | 279.5 | 370.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 214338 | 107119 | 214337.9994
38909.5422 | 1 | 0 | 38909.5422 | 1 | 0 | 338.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5429 | 1 | 0 | 38909.5429 | 1 | 0 | 397 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5436 | 1 | 0 | 38909.5436 | 1 | 0 | 455.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5443 | 1 | 0 | 38909.5443 | 1 | 0 | 514.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5449 | 1 | 0 | 38909.545 | 1 | 0 | 573.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5456 | 1 | 0 | 38909.5456 | 1 | 0 | 632 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5463 | 1 | 0 | 38909.5463 | 1 | 0 | 691 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.547 | 1 | 0 | 38909.547 | 1 | 0 | 750 | 841 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214338 | 214338 | 214337.9994
38909.5477 | 2 | 7 | 38909.5477 | 1 | 4 | 808.5 | 899.5 | 0.1221 | 0.42735 | 0.06105 | 0.2442 | 0.001221 | 0.0042735 | 0.0006105 | 0.002442 | 0.0030525 | 0.0018315 | 42931.4639 | 71668.5829 | 30462.9233
38909.5483 | 2 | 9 | 38909.5484 | 2 | 7 | 867.5 | 958.5 | 0.1221 | 0.54945 | 0.1221 | 0.42735 | 0.001221 | 0.0054945 | 0.001221 | 0.0042735 | 0.0042735 | 0.0030525 | 30697.1203 | 43043.9099 | 23649.28
38909.549 | 2 | 10 | 38909.549 | 2 | 7 | 926 | 1017 | 0.1221 | 0.6105 | 0.1221 | 0.42735 | 0.001221 | 0.006105 | 0.001221 | 0.0042735 | 0.004884 | 0.0030525 | 26857.694 | 43072.1203 | 21274.4075
38909.5497 | 2 | 10 | 38909.5497 | 2 | 7 | 985 | 1076 | 0.1221 | 0.6105 | 0.1221 | 0.42735 | 0.001221 | 0.006105 | 0.001221 | 0.0042735 | 0.004884 | 0.0030525 | 26857.694 | 43072.1203 | 21274.4075
38909.5504 | 3 | 10 | 38909.5504 | 2 | 7 | 1044 | 1135 | 0.18315 | 0.6105 | 0.1221 | 0.42735 | 0.0018315 | 0.006105 | 0.001221 | 0.0042735 | 0.0042735 | 0.0030525 | 30693.0089 | 43043.9363 | 21264.3984
38909.5511 | 3 | 10 | 38909.5511 | 2 | 9 | 1102.5 | 1193.5 | 0.18315 | 0.6105 | 0.1221 | 0.54945 | 0.0018315 | 0.006105 | 0.001221 | 0.0054945 | 0.0042735 | 0.0042735 | 30734 | 30734 | 21244.6757
38909.5517 | 3 | 10 | 38909.5518 | 2 | 8 | 1161.5 | 1252.5 | 0.18315 | 0.6105 | 0.1221 | 0.4884 | 0.0018315 | 0.006105 | 0.001221 | 0.004884 | 0.0042735 | 0.003663 | 30713.4907 | 35862.0174 | 21254.5325
38909.5524 | 3 | 8 | 38909.5524 | 2 | 7 | 1220 | 1311 | 0.18315 | 0.4884 | 0.1221 | 0.42735 | 0.0018315 | 0.004884 | 0.001221 | 0.0042735 | 0.0030525 | 0.0030525 | 42987.6 | 42987.6 | 26605.3592
38909.5531 | 3 | 0 | 38909.5531 | 3 | 1 | 1279 | 1370 | 0.18315 | 0 | 0.18315 | 0.06105 | 0.0018315 | 0 | 0.0018315 | 0.0006105 | 0.0018315 | 0.001221 | 71379.3333 | 107119 | 71379.3315
38909.5538 | 3 | 0 | 38909.5538 | 3 | 0 | 1337.5 | 1428.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 71379.3333 | 71379.3333 | 71379.3315
38909.5545 | 4 | 0 | 38909.5545 | 3 | 0 | 1396.5 | 1487.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 53509.5 | 71379.3333 | 53509.4976
38909.5552 | 3 | 8 | 38909.5552 | 2 | 5 | 1455.5 | 1546.5 | 0.18315 | 0.4884 | 0.1221 | 0.30525 | 0.0018315 | 0.004884 | 0.001221 | 0.0030525 | 0.0030525 | 0.0018315 | 42923.3964 | 71691.0348 | 26630.1043
38909.5558 | 3 | 8 | 38909.5558 | 2 | 6 | 1514 | 1605 | 0.18315 | 0.4884 | 0.1221 | 0.3663 | 0.0018315 | 0.004884 | 0.001221 | 0.003663 | 0.0030525 | 0.002442 | 42955.4742 | 53747.1845 | 26617.7261
38909.5565 | 2 | 9 |  | 2 | 1 | 1572 | 1663 | 0.1221 | 0.54945 | 0.1221 | 0.06105 | 0.001221 | 0.0054945 | 0.001221 | 0.0006105 | 0.0042735 | 0.0006105 | 30623.7469 | 214939.8732 | 23693.199
38909.5572 | 2128 | 0 | 38909.5572 | 2 | 0 | 1631.5 | 1722.5 | 129.9145 | 0 | 0.1221 | 0 | 1.2991 | 0 | 0.001221 | 0 | 1.2991 | 0.001221 | 0.76974 | 107119 | 0.52941
38909.5579 | 2089 | 0 | 38909.5579 | 3 | 0 | 1690.5 | 1781.5 | 127.5336 | 0 | 0.18315 | 0 | 1.2753 | 0 | 0.0018315 | 0 | 1.2753 | 0.0018315 | 2.651 | 71379.3333 | 1.3757

## C1-7
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 152.8315 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38909.5374 | 1 | 0 | 38909.5374 | 1 | 0 | -76 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5381 | 1 | 0 | 38909.5381 | 1 | 0 | -17.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5388 | 1 | 0 | 38909.5388 | 1 | 0 | 41.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5395 | 1 | 0 | 38909.5395 | 1 | 0 | 100.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5401 | 1 | 0 | 38909.5402 | 1 | 0 | 159 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5408 | 1 | 0 | 38909.5408 | 1 | 0 | 218 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5415 | 1 | 0 | 38909.5415 | 1 | 0 | 276.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5422 | 1 | 0 | 38909.5422 | 1 | 0 | 335.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5429 | 1 | 0 | 38909.5429 | 1 | 0 | 394.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5435 | 1 | 0 | 38909.5436 | 1 | 0 | 453 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5442 | 1 | 0 | 38909.5442 | 2 | 0 | 511.5 | 602.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250238 | 125069 | 250237.9994
38909.5449 | 1 | 0 | 38909.5449 | 1 | 0 | 570.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5456 | 1 | 0 | 38909.5456 | 1 | 0 | 629.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5463 | 1 | 0 | 38909.5463 | 1 | 0 | 688.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5469 | 1 | 0 | 38909.547 | 1 | 0 | 747 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38909.5476 | 1114 | 1179 | 38909.5476 | 1014 | 1128 | 805.5 | 896.5 | 68.0098 | 71.978 | 61.9048 | 68.8645 | 0.6801 | 0.71978 | 0.61905 | 0.68864 | 0.039683 | 0.069597 | 1966.6903 | 20883.5502 | 17.7589
38909.5483 | 1128 | 1102 | 38909.5483 | 1143 | 1115 | 864.5 | 955.5 | 68.8645 | 67.2772 | 69.7802 | 68.0708 | 0.68864 | 0.67277 | 0.6978 | 0.68071 | 0.015873 | 0.017094 | 14229.6526 | 6746.4944 | 24.4453
38909.549 | 952 | 1072 | 38909.549 | 943 | 915 | 923.5 | 1014.5 | 58.1197 | 65.4457 | 57.5702 | 55.8608 | 0.5812 | 0.65446 | 0.5757 | 0.55861 | 0.07326 | 0.017094 | 915.7705 | 2169.73 | 42.7481
38909.5497 | 980 | 950 | 38909.5497 | 1062 | 1154 | 982.5 | 1073.5 | 59.8291 | 57.9976 | 64.8352 | 70.4518 | 0.59829 | 0.57998 | 0.64835 | 0.70452 | 0.018315 | 0.056166 | 2489.8196 | 3046.3996 | 58.4375
38909.5503 | 945 | 976 | 38909.5504 | 1035 | 1006 | 1041 | 1132 | 57.6923 | 59.5849 | 63.1868 | 61.4164 | 0.57692 | 0.59585 | 0.63187 | 0.61416 | 0.018926 | 0.017705 | 7588.6078 | 9327.0233 | 59.0371
38909.551 | 997 | 967 | 38909.551 | 1083 | 1054 | 1099.5 | 1190.5 | 60.8669 | 59.0354 | 66.1172 | 64.3468 | 0.60867 | 0.59035 | 0.66117 | 0.64347 | 0.018315 | 0.017705 | 7690.7143 | 9286.4664 | 55.1845
38909.5517 | 1024 | 995 | 38909.5517 | 1009 | 1048 | 1158.5 | 1249.5 | 62.5153 | 60.7448 | 61.5995 | 63.9805 | 0.62515 | 0.60745 | 0.616 | 0.6398 | 0.017705 | 0.02381 | 25772.0814 | 4277.7746 | 47.5694
38909.5524 | 1960 | 604 | 38909.5524 | 2156 | 594 | 1217.5 | 1308.5 | 119.6581 | 36.8742 | 131.6239 | 36.2637 | 1.1966 | 0.36874 | 1.3162 | 0.36264 | 0.82784 | 0.9536 | 35.9899 | 392.6884 | 7.9994
38909.5531 | 2250 | 1 | 38909.5531 | 2107 | 1 | 1276 | 1367 | 137.3626 | 0.06105 | 128.6325 | 0.06105 | 1.3736 | 0.0006105 | 1.2863 | 0.0006105 | 1.373 | 1.2857 | 11.2929 | 18.9009 | 4011.9265
38909.5537 | 2039 | 0 | 38909.5538 | 2043 | 0 | 1335 | 1426 | 124.4811 | 0 | 124.7253 | 0 | 1.2448 | 0 | 1.2473 | 0 | 1.2448 | 1.2473 | 22.7749 | 22.5345 | 21.5301
38909.5544 | 2107 | 0 | 38909.5544 | 2384 | 0 | 1393.5 | 1484.5 | 128.6325 | 0 | 145.5433 | 0 | 1.2863 | 0 | 1.4554 | 0 | 1.2863 | 1.4554 | 18.8125 | 5.0076 | 17.5262
38909.5551 | 939 | 935 | 38909.5551 | 1057 | 1025 | 1452.5 | 1543.5 | 57.326 | 57.0818 | 64.5299 | 62.5763 | 0.57326 | 0.57082 | 0.6453 | 0.62576 | 0.002442 | 0.019536 | 5404.3549 | 3747.9974 | 65.5641
38909.5558 | 1101 | 1070 | 38909.5558 | 949 | 1064 | 1511.5 | 1602.5 | 67.2161 | 65.3236 | 57.9365 | 64.9573 | 0.67216 | 0.65324 | 0.57937 | 0.64957 | 0.018926 | 0.070208 | 1390.9868 | 1532.5325 | 29.1608
38909.5565 | 945 | 920 | 38909.5565 | 934 | 961 | 1570 | 1661 | 57.6923 | 56.1661 | 57.0208 | 58.6691 | 0.57692 | 0.56166 | 0.57021 | 0.58669 | 0.015263 | 0.016484 | 10848.3824 | 8650.7557 | 68.5962
38909.5572 | 2487 | 0 | 38909.5572 | 2003 | 0 | 1629 | 1720 | 151.8315 | 0 | 122.2833 | 0 | 1.5183 | 0 | 1.2228 | 0 | 1.5183 | 1.2228 | 0.65862 | 24.9815 | 0.85969
38909.5578 | 2063 | 0 | 38909.5578 | 1986 | 0 | 1687.5 | 1778.5 | 125.9463 | 0 | 121.2454 | 0 | 1.2595 | 0 | 1.2125 | 0 | 1.2595 | 1.2125 | 21.3466 | 26.0514 | 20.0871

## C1-6
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.4335 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38909.5374 | 1 | 1 | 38909.5374 | 1 | 0 | -79 | 12 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38909.5381 | 1 | 0 | 38909.5381 | 1 | 0 | -20 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5387 | 1 | 0 | 38909.5388 | 1 | 0 | 38.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5394 | 1 | 0 | 38909.5394 | 1 | 0 | 97.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5401 | 1 | 0 | 38909.5401 | 1 | 0 | 156.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5408 | 1 | 0 | 38909.5408 | 1 | 0 | 215 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5415 | 1 | 0 | 38909.5415 | 1 | 0 | 274 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5422 | 1 | 0 | 38909.5422 | 1 | 0 | 332.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5428 | 1 | 0 | 38909.5428 | 1 | 0 | 391.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5435 | 1 | 0 | 38909.5435 | 1 | 0 | 450.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5442 | 1 | 0 | 38909.5442 | 1 | 0 | 509 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5449 | 1 | 0 | 38909.5449 | 1 | 0 | 568 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5456 | 1 | 0 | 38909.5456 | 1 | 0 | 626.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5462 | 1 | 0 | 38909.5462 | 1 | 0 | 685.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5469 | 1 | 0 | 38909.5469 | 1 | 0 | 744.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5476 | 1 | 0 | 38909.5476 | 1 | 0 | 803 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38909.5483 | 999 | 1040 | 38909.5483 | 1052 | 1024 | 862 | 953 | 60.989 | 63.4921 | 64.2247 | 62.5153 | 0.60989 | 0.63492 | 0.64225 | 0.62515 | 0.025031 | 0.017094 | 3951.5774 | 72395.2265 | 50.2556
38909.549 | 1197 | 1177 | 38909.549 | 1075 | 1048 | 920.5 | 1011.5 | 73.0769 | 71.8559 | 65.6288 | 63.9805 | 0.73077 | 0.71856 | 0.65629 | 0.6398 | 0.01221 | 0.016484 | 39250.906 | 7124.0914 | 15.7835
38909.5496 | 1103 | 1076 | 38909.5497 | 1108 | 1162 | 979.5 | 1070.5 | 67.3382 | 65.6899 | 67.6435 | 70.9402 | 0.67338 | 0.6569 | 0.67643 | 0.7094 | 0.016484 | 0.032967 | 4630.4583 | 23821.2955 | 35.4812
38909.5503 | 992 | 1030 | 38909.5503 | 1093 | 1065 | 1038 | 1129 | 60.5617 | 62.8816 | 66.7277 | 65.0183 | 0.60562 | 0.62882 | 0.66728 | 0.65018 | 0.023199 | 0.017094 | 4484.0541 | 34580.39 | 52.3128
38909.551 | 993 | 962 | 38909.551 | 1053 | 1024 | 1097 | 1188 | 60.6227 | 58.7302 | 64.2857 | 62.5153 | 0.60623 | 0.5873 | 0.64286 | 0.62515 | 0.018926 | 0.017705 | 7323.9766 | 10050.1218 | 62.5152
38909.5517 | 965 | 1120 | 38909.5517 | 933 | 950 | 1155.5 | 1246.5 | 58.9133 | 68.3761 | 56.9597 | 57.9976 | 0.58913 | 0.68376 | 0.5696 | 0.57998 | 0.094628 | 0.010379 | 658.9496 | 1281.2731 | 39.5374
38909.5524 | 2153 | 310 | 38909.5524 | 2234 | 739 | 1214.5 | 1305.5 | 131.4408 | 18.9255 | 136.3858 | 45.116 | 1.3144 | 0.18926 | 1.3639 | 0.45116 | 1.1252 | 0.9127 | 66.7759 | 25.2046 | 6.4535
38909.553 | 2280 | 1 | 38909.5531 | 2216 | 1 | 1273.5 | 1364.5 | 139.1941 | 0.06105 | 135.2869 | 0.06105 | 1.3919 | 0.0006105 | 1.3529 | 0.0006105 | 1.3913 | 1.3523 | 12.4253 | 15.695 | 3817.146
38909.5537 | 2189 | 0 | 38909.5537 | 2250 | 0 | 1332 | 1423 | 133.6386 | 0 | 137.3626 | 0 | 1.3364 | 0 | 1.3736 | 0 | 1.3364 | 1.3736 | 17.0571 | 13.8836 | 15.7207
38909.5544 | 2546 | 0 | 38909.5544 | 2056 | 0 | 1391 | 1482 | 155.4335 | 0 | 125.5189 | 0 | 1.5543 | 0 | 1.2552 | 0 | 1.5543 | 1.2552 | 0.64336 | 24.6294 | 0.91097
38909.5551 | 948 | 914 | 38909.5551 | 967 | 932 | 1449.5 | 1540.5 | 57.8755 | 55.7998 | 59.0354 | 56.8987 | 0.57875 | 0.558 | 0.59035 | 0.56899 | 0.020757 | 0.021368 | 7745.9568 | 6946.1242 | 75.5405
38909.5558 | 943 | 971 | 38909.5558 | 1069 | 1038 | 1508.5 | 1599.5 | 57.5702 | 59.2796 | 65.2625 | 63.37 | 0.5757 | 0.5928 | 0.65263 | 0.6337 | 0.017094 | 0.018926 | 12041.1051 | 6672.9734 | 65.7886
38909.5564 | 1055 | 1025 | 38909.5565 | 1129 | 1099 | 1567.5 | 1658.5 | 64.4078 | 62.5763 | 68.9255 | 67.094 | 0.64408 | 0.62576 | 0.68926 | 0.67094 | 0.018315 | 0.018315 | 8441.2667 | 8441.2667 | 46.5105
38909.5571 | 1993 | 0 | 38909.5571 | 2339 | 1 | 1626 | 1717 | 121.6728 | 0 | 142.7961 | 0.06105 | 1.2167 | 0 | 1.428 | 0.0006105 | 1.2167 | 1.4274 | 28.569 | 9.5971 | 27.3523
38909.5578 | 2454 | 0 | 38909.5578 | 2529 | 0 | 1685 | 1776 | 149.8168 | 0 | 154.3956 | 0 | 1.4982 | 0 | 1.544 | 0 | 1.4982 | 1.544 | 4.4165 | 1.3199 | 2.9183

## C1-5
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.6166 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38909.5374 | 1 | 0 | 38909.5374 | 1 | 0 | -81.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.538 | 1 | 0 | 38909.5381 | 1 | 0 | -23 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5387 | 1 | 0 | 38909.5387 | 1 | 0 | 36 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5394 | 1 | 0 | 38909.5394 | 1 | 0 | 94.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5401 | 1 | 0 | 38909.5401 | 1 | 0 | 153.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5408 | 1 | 0 | 38909.5408 | 1 | 0 | 212.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5414 | 1 | 0 | 38909.5415 | 1 | 0 | 271 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5421 | 1 | 0 | 38909.5421 | 1 | 0 | 330 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5428 | 1 | 0 | 38909.5428 | 1 | 0 | 388.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5435 | 1 | 0 | 38909.5435 | 1 | 0 | 447.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5442 | 1 | 0 | 38909.5442 | 1 | 0 | 506.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5448 | 1 | 0 | 38909.5449 | 1 | 0 | 565 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5455 | 1 | 0 | 38909.5455 | 1 | 0 | 624 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5462 | 1 | 0 | 38909.5462 | 1 | 0 | 682.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5469 | 1 | 0 | 38909.5469 | 1 | 0 | 741.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5476 | 1 | 0 | 38909.5476 | 1 | 0 | 800.5 | 891.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
38909.5482 | 1 | 1 | 38909.5483 | 1 | 0 | 859 | 950 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 657604478.44 | 256438 | 256238.078
38909.5489 | 1 | 2 | 38909.5489 | 2 | 0 | 918 | 1009 | 0.06105 | 0.1221 | 0.1221 | 0 | 0.0006105 | 0.001221 | 0.001221 | 0 | 0.0006105 | 0.001221 | 256838.7814 | 128169 | 128019.1169
38909.5496 | 2 | 2 | 38909.5496 | 2 | 1 | 976.5 | 1067.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 328545751.22 | 256337.922 | 128019.0585
38909.5503 | 2 | 2 | 38909.5503 | 1 | 2 | 1035.5 | 1126.5 | 0.1221 | 0.1221 | 0.06105 | 0.1221 | 0.001221 | 0.001221 | 0.0006105 | 0.001221 | 0 | 0.0006105 | 328673820.22 | 256437.844 | 128019.0779
38909.551 | 1018 | 986 | 38909.551 | 1119 | 1170 | 1094.5 | 1185.5 | 62.149 | 60.1954 | 68.315 | 71.4286 | 0.62149 | 0.60195 | 0.68315 | 0.71429 | 0.019536 | 0.031136 | 27099.5213 | 3750.4741 | 55.4564
38909.5516 | 1133 | 1104 | 38909.5517 | 1068 | 1038 | 1153 | 1244 | 69.1697 | 67.3993 | 65.2015 | 63.37 | 0.6917 | 0.67399 | 0.65201 | 0.6337 | 0.017705 | 0.018315 | 9693.9366 | 7761.5519 | 29.3662
38909.5523 | 2053 | 738 | 38909.5523 | 1904 | 850 | 1211.5 | 1302.5 | 125.3358 | 45.0549 | 116.2393 | 51.8926 | 1.2534 | 0.45055 | 1.1624 | 0.51893 | 0.80281 | 0.64347 | 313.9709 | 64.0733 | 11.9388
38909.553 | 2152 | 1 | 38909.553 | 2227 | 0 | 1270.5 | 1361.5 | 131.3797 | 0.06105 | 135.9585 | 0 | 1.3138 | 0.0006105 | 1.3596 | 0 | 1.3132 | 1.3596 | 19.277 | 15.1944 | 5439.3947
38909.5537 | 2182 | 0 | 38909.5537 | 2488 | 1 | 1329.5 | 1420.5 | 133.2112 | 0 | 151.8926 | 0.06105 | 1.3321 | 0 | 1.5189 | 0.0006105 | 1.3321 | 1.5183 | 17.5701 | 3.1516 | 16.238
38909.5544 | 2172 | 1 | 38909.5544 | 2489 | 1 | 1388 | 1479 | 132.6007 | 0.06105 | 151.9536 | 0.06105 | 1.326 | 0.0006105 | 1.5195 | 0.0006105 | 1.3254 | 1.5189 | 18.3952 | 3.0767 | 1171.1857
38909.555 | 2191 | 1 | 38909.5551 | 2157 | 0 | 1447 | 1538 | 133.7607 | 0.06105 | 131.685 | 0 | 1.3376 | 0.0006105 | 1.3168 | 0 | 1.337 | 1.3168 | 17.1363 | 18.9328 | 5943.7949
38909.5557 | 5 | 1 | 38909.5557 | 1962 | 0 | 1505.5 | 1596.5 | 0.30525 | 0.06105 | 119.7802 | 0 | 0.0030525 | 0.0006105 | 1.1978 | 0 | 0.002442 | 1.1978 | 342151.4184 | 30.7533 | 60196.8794
38909.5564 | 2 | 1 | 38909.5564 | 2056 | 1 | 1564.5 | 1655.5 | 0.1221 | 0.06105 | 125.5189 | 0.06105 | 0.001221 | 0.0006105 | 1.2552 | 0.0006105 | 0.0006105 | 1.2546 | 84479.5942 | 49.1565 | 84446.6379
38909.5571 | 2549 | 1 | 38909.5571 | 2044 | 1 | 1623.5 | 1714.5 | 155.6166 | 0.06105 | 124.7863 | 0.06105 | 1.5562 | 0.0006105 | 1.2479 | 0.0006105 | 1.5556 | 1.2473 | 0.64377 | 27.6204 | 332.8631
38909.5578 | 2150 | 0 | 38909.5578 | 1645 | 0 | 1682 | 1773 | 131.2576 | 0 | 100.4274 | 0 | 1.3126 | 0 | 1.0043 | 0 | 1.3126 | 1.0043 | 19.32 | 55.9502 | 18.0074

## C1-4
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 156.3114 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38909.5373 | 1 | 0 | 38909.5373 | 1 | 0 | -84.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.538 | 1 | 0 | 38909.538 | 1 | 0 | -25.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5387 | 1 | 0 | 38909.5387 | 1 | 0 | 33 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5394 | 1 | 0 | 38909.5394 | 1 | 0 | 92 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.54 | 1 | 0 | 38909.5401 | 1 | 0 | 150.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5407 | 1 | 0 | 38909.5407 | 1 | 0 | 209.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5414 | 1 | 0 | 38909.5414 | 1 | 0 | 268.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5421 | 1 | 0 | 38909.5421 | 1 | 0 | 327 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5428 | 1 | 0 | 38909.5428 | 1 | 0 | 386 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5434 | 1 | 0 | 38909.5435 | 1 | 0 | 444.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5441 | 1 | 0 | 38909.5441 | 1 | 0 | 503.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5448 | 1 | 0 | 38909.5448 | 1 | 0 | 562 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5455 | 1 | 0 | 38909.5455 | 1 | 0 | 621 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5462 | 1 | 0 | 38909.5462 | 1 | 0 | 680 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5469 | 1 | 0 | 38909.5469 | 1 | 0 | 738.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5475 | 1 | 0 | 38909.5475 | 1 | 0 | 797.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38909.5482 | 1 | 1 | 38909.5482 | 1 | 0 | 856.5 | 947.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 655042598.44 | 255938 | 255738.0781
38909.5489 | 2 | 5 | 38909.5489 | 2 | 3 | 915 | 1006 | 0.1221 | 0.30525 | 0.1221 | 0.18315 | 0.001221 | 0.0030525 | 0.001221 | 0.0018315 | 0.0018315 | 0.0006105 | 85334.7295 | 256740.5889 | 51047.717
38909.5496 | 2 | 6 | 38909.5496 | 2 | 3 | 973.5 | 1064.5 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 63996.846 | 257042.9482 | 42523.1235
38909.5503 | 1 | 6 | 38909.5503 | 2 | 5 | 1032.5 | 1123.5 | 0.06105 | 0.3663 | 0.1221 | 0.30525 | 0.0006105 | 0.003663 | 0.001221 | 0.0030525 | 0.0030525 | 0.0018315 | 51259.4948 | 85557.5176 | 42506.6514
38909.5509 | 1195 | 1120 | 38909.5509 | 962 | 929 | 1091.5 | 1182.5 | 72.9548 | 68.3761 | 58.7302 | 56.7155 | 0.72955 | 0.68376 | 0.5873 | 0.56716 | 0.045788 | 0.020147 | 1377.1548 | 4638.643 | 21.4466
38909.5516 | 966 | 935 | 38909.5516 | 1024 | 994 | 1150 | 1241 | 58.9744 | 57.0818 | 62.5153 | 60.6838 | 0.58974 | 0.57082 | 0.62515 | 0.60684 | 0.018926 | 0.018315 | 7764.8413 | 8933.1128 | 69.7412
38909.5523 | 2238 | 853 | 38909.5523 | 2230 | 986 | 1209 | 1300 | 136.63 | 52.0757 | 136.1416 | 60.1954 | 1.3663 | 0.52076 | 1.3614 | 0.60195 | 0.84554 | 0.75946 | 121.7038 | 76.1532 | 26.8926
38909.553 | 2278 | 1 | 38909.553 | 2073 | 1 | 1267.5 | 1358.5 | 139.072 | 0.06105 | 126.5568 | 0.06105 | 1.3907 | 0.0006105 | 1.2656 | 0.0006105 | 1.3901 | 1.265 | 12.4245 | 23.6139 | 5375.1929
38909.5537 | 2313 | 1 | 38909.5537 | 2296 | 0 | 1326.5 | 1417.5 | 141.2088 | 0.06105 | 140.1709 | 0 | 1.4121 | 0.0006105 | 1.4017 | 0 | 1.4115 | 1.4017 | 10.7402 | 11.5148 | 2544.0733
38909.5543 | 2544 | 1 | 38909.5544 | 2125 | 0 | 1385.5 | 1476.5 | 155.3114 | 0.06105 | 129.7314 | 0 | 1.5531 | 0.0006105 | 1.2973 | 0 | 1.5525 | 1.2973 | 0.64536 | 20.4885 | 261.5293
38909.555 | 1981 | 1 | 38909.555 | 2002 | 0 | 1444 | 1535 | 120.9402 | 0.06105 | 122.2222 | 0 | 1.2094 | 0.0006105 | 1.2222 | 0 | 1.2088 | 1.2222 | 29.3147 | 27.8911 | 12613.5896
38909.5557 | 2 | 1 | 38909.5557 | 2398 | 1 | 1503 | 1594 | 0.1221 | 0.06105 | 146.398 | 0.06105 | 0.001221 | 0.0006105 | 1.464 | 0.0006105 | 0.0006105 | 1.4634 | 18590.5767 | 7.8359 | 18583.3101
38909.5564 | 2 | 1 | 38909.5564 | 2367 | 1 | 1561.5 | 1652.5 | 0.1221 | 0.06105 | 144.5055 | 0.06105 | 0.001221 | 0.0006105 | 1.4451 | 0.0006105 | 0.0006105 | 1.4444 | 22771.5166 | 9.7704 | 22762.6159
38909.5571 | 2535 | 0 | 38909.5571 | 2296 | 1 | 1620.5 | 1711.5 | 154.7619 | 0 | 140.1709 | 0.06105 | 1.5476 | 0 | 1.4017 | 0.0006105 | 1.5476 | 1.4011 | 1.0012 | 11.5634 | 0.54644
38909.5577 | 2530 | 0 | 38909.5578 | 1919 | 0 | 1679.5 | 1770.5 | 154.4567 | 0 | 117.1551 | 0 | 1.5446 | 0 | 1.1716 | 0 | 1.5446 | 1.1716 | 1.2008 | 33.4226 | 0.34378

## C1-3
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 146.2991 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38909.5373 | 1 | 0 | 38909.5373 | 1 | 0 | -87.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.538 | 1 | 0 | 38909.538 | 1 | 0 | -28.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5387 | 1 | 0 | 38909.5387 | 1 | 0 | 30.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5393 | 1 | 0 | 38909.5394 | 1 | 0 | 89 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.54 | 1 | 0 | 38909.54 | 1 | 0 | 148 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5407 | 1 | 0 | 38909.5407 | 1 | 0 | 206.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5414 | 1 | 0 | 38909.5414 | 1 | 0 | 265.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5421 | 1 | 0 | 38909.5421 | 1 | 0 | 324.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5427 | 1 | 0 | 38909.5428 | 1 | 0 | 383 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5434 | 1 | 0 | 38909.5434 | 1 | 0 | 442 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5441 | 1 | 0 | 38909.5441 | 1 | 0 | 500.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5448 | 1 | 0 | 38909.5448 | 1 | 0 | 559.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5455 | 1 | 0 | 38909.5455 | 1 | 0 | 618.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5461 | 1 | 0 | 38909.5462 | 1 | 0 | 677 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5468 | 1 | 0 | 38909.5468 | 1 | 0 | 736 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5475 | 1 | 0 | 38909.5475 | 1 | 0 | 794.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
38909.5482 | 2 | 2 | 38909.5482 | 1 | 0 | 853.5 | 944.5 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 286772498.22 | 239538 | 119569.0835
38909.5489 | 3 | 10 | 38909.5489 | 2 | 6 | 912 | 1003 | 0.18315 | 0.6105 | 0.1221 | 0.3663 | 0.0018315 | 0.006105 | 0.001221 | 0.003663 | 0.0042735 | 0.002442 | 34272.5778 | 60122.6374 | 23794.2239
38909.5495 | 2 | 10 | 38909.5496 | 2 | 7 | 971 | 1062 | 0.1221 | 0.6105 | 0.1221 | 0.42735 | 0.001221 | 0.006105 | 0.001221 | 0.0042735 | 0.004884 | 0.0030525 | 30007.7131 | 48112.0653 | 23794.3439
38909.5502 | 2 | 10 | 38909.5502 | 2 | 7 | 1029.5 | 1120.5 | 0.1221 | 0.6105 | 0.1221 | 0.42735 | 0.001221 | 0.006105 | 0.001221 | 0.0042735 | 0.004884 | 0.0030525 | 30007.7131 | 48112.0653 | 23794.3439
38909.5509 | 2 | 7 | 38909.5509 | 2 | 6 | 1088.5 | 1179.5 | 0.1221 | 0.42735 | 0.1221 | 0.3663 | 0.001221 | 0.0042735 | 0.001221 | 0.003663 | 0.0030525 | 0.002442 | 47999.5109 | 60047.1493 | 34048.7253
38909.5516 | 3 | 10 | 38909.5516 | 3 | 9 | 1147.5 | 1238.5 | 0.18315 | 0.6105 | 0.18315 | 0.54945 | 0.0018315 | 0.006105 | 0.0018315 | 0.0054945 | 0.0042735 | 0.003663 | 34313.4928 | 40064.8083 | 23774.46
38909.5523 | 2086 | 8 | 38909.5523 | 3 | 7 | 1206 | 1297 | 127.3504 | 0.4884 | 0.18315 | 0.42735 | 1.2735 | 0.004884 | 0.0018315 | 0.0042735 | 1.2686 | 0.002442 | 14.9354 | 5583.0914 | 3713.2413
38909.5529 | 2342 | 1 | 38909.553 | 3 | 1 | 1265 | 1356 | 142.9792 | 0.06105 | 0.18315 | 0.06105 | 1.4298 | 0.0006105 | 0.0018315 | 0.0006105 | 1.4292 | 0.001221 | 2.3229 | 5830.5113 | 5247.9909
38909.5536 | 2380 | 0 | 38909.5536 | 3 | 0 | 1323.5 | 1414.5 | 145.2991 | 0 | 0.18315 | 0 | 1.453 | 0 | 0.0018315 | 0 | 1.453 | 0.0018315 | 0.68824 | 79779.3333 | 0.76476
38909.5543 | 2194 | 0 | 38909.5543 | 3 | 0 | 1382.5 | 1473.5 | 133.9438 | 0 | 0.18315 | 0 | 1.3394 | 0 | 0.0018315 | 0 | 1.3394 | 0.0018315 | 9.2242 | 79779.3333 | 7.8848
38909.555 | 1598 | 18 | 38909.555 | 3 | 0 | 1441.5 | 1532.5 | 97.558 | 1.0989 | 0.18315 | 0 | 0.97558 | 0.010989 | 0.0018315 | 0 | 0.96459 | 0.0018315 | 50.5311 | 79779.3333 | 4330.017
38909.5557 | 18 | 2 | 38909.5557 | 2 | 1 | 1500 | 1591 | 1.0989 | 0.1221 | 0.1221 | 0.06105 | 0.010989 | 0.001221 | 0.001221 | 0.0006105 | 0.009768 | 0.0006105 | 14865.6458 | 241059.5884 | 118769.7301
38909.5563 | 2 | 4 | 38909.5564 | 2 | 2 | 1559 | 1650 | 0.1221 | 0.2442 | 0.1221 | 0.1221 | 0.001221 | 0.002442 | 0.001221 | 0.001221 | 0.001221 | 0 | 119718.8329 | 143326189.6251 | 59759.4583
38909.557 | 2029 | 1 | 38909.557 | 3 | 0 | 1617.5 | 1708.5 | 123.8706 | 0.06105 | 0.18315 | 0 | 1.2387 | 0.0006105 | 0.0018315 | 0 | 1.2381 | 0.0018315 | 18.1154 | 79779.3333 | 36592.1333
38909.5577 | 2373 | 0 | 38909.5577 | 3 | 1 | 1676.5 | 1767.5 | 144.8718 | 0 | 0.18315 | 0.06105 | 1.4487 | 0 | 0.0018315 | 0.0006105 | 1.4487 | 0.001221 | 0.98525 | 119719 | 0.46347

## C1-2
Penlight Test 15 |  |  | 2006-07-11 | 12:55 |  | Vs = |  | 148.8632 |  | R = | 100
PE | 7-C | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38909.5373 | 1 | 0 | 38909.5373 | 1 | 0 | -90 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5379 | 1 | 0 | 38909.538 | 1 | 0 | -31.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5386 | 1 | 0 | 38909.5386 | 1 | 0 | 27.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5393 | 1 | 0 | 38909.5393 | 2 | 0 | 86.5 | 177.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 243738 | 121819 | 243737.9994
38909.54 | 1 | 0 | 38909.54 | 1 | 0 | 145 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5407 | 1 | 0 | 38909.5407 | 1 | 0 | 204 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5413 | 1 | 0 | 38909.5414 | 1 | 0 | 262.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.542 | 1 | 0 | 38909.542 | 1 | 0 | 321.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5427 | 1 | 0 | 38909.5427 | 1 | 0 | 380.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5434 | 1 | 0 | 38909.5434 | 1 | 0 | 439 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5441 | 1 | 0 | 38909.5441 | 1 | 0 | 498 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5447 | 1 | 0 | 38909.5448 | 1 | 0 | 556.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5454 | 1 | 0 | 38909.5454 | 1 | 0 | 615.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5461 | 1 | 0 | 38909.5461 | 1 | 0 | 674.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5468 | 1 | 0 | 38909.5468 | 1 | 0 | 733 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5475 | 1 | 0 | 38909.5475 | 1 | 0 | 792 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38909.5481 | 2 | 8 | 38909.5482 | 2 | 4 | 850.5 | 941.5 | 0.1221 | 0.4884 | 0.1221 | 0.2442 | 0.001221 | 0.004884 | 0.001221 | 0.002442 | 0.003663 | 0.001221 | 40650.6073 | 122421.3099 | 30329.9749
38909.5488 | 1202 | 1186 | 38909.5488 | 1171 | 1147 | 909.5 | 1000.5 | 73.3822 | 72.4054 | 71.4896 | 70.0244 | 0.73382 | 0.72405 | 0.7149 | 0.70024 | 0.009768 | 0.014652 | 2524.1058 | 3595.8037 | 4.133
38909.5495 | 938 | 1055 | 38909.5495 | 982 | 1022 | 968.5 | 1059.5 | 57.265 | 64.4078 | 59.9512 | 62.3932 | 0.57265 | 0.64408 | 0.59951 | 0.62393 | 0.071429 | 0.02442 | 863.4509 | 1858.522 | 40.0606
38909.5502 | 1076 | 1128 | 38909.5502 | 1066 | 1039 | 1027 | 1118 | 65.6899 | 68.8645 | 65.0794 | 63.431 | 0.6569 | 0.68864 | 0.65079 | 0.63431 | 0.031746 | 0.016484 | 1705.5714 | 4046.1702 | 20.2772
38909.5509 | 3 | 10 | 38909.5509 | 2 | 9 | 1085.5 | 1176.5 | 0.18315 | 0.6105 | 0.1221 | 0.54945 | 0.0018315 | 0.006105 | 0.001221 | 0.0054945 | 0.0042735 | 0.0042735 | 34934 | 34934 | 24184.5707
38909.5516 | 1052 | 1021 | 38909.5516 | 1148 | 1119 | 1144.5 | 1235.5 | 64.2247 | 62.3321 | 70.0855 | 68.315 | 0.64225 | 0.62332 | 0.70085 | 0.68315 | 0.018926 | 0.017705 | 6220.2608 | 11719.6461 | 35.4837
38909.5522 | 2115 | 10 | 38909.5522 | 129 | 52 | 1203.5 | 1294.5 | 129.1209 | 0.6105 | 7.8755 | 3.1746 | 1.2912 | 0.006105 | 0.078755 | 0.031746 | 1.2851 | 0.047009 | 15.3542 | 882.5563 | 2814.8564
38909.5529 | 2154 | 1 | 38909.5529 | 4 | 1 | 1262 | 1353 | 131.5018 | 0.06105 | 0.2442 | 0.06105 | 1.315 | 0.0006105 | 0.002442 | 0.0006105 | 1.3144 | 0.0018315 | 13.2085 | 53258.6574 | 28284.8915
38909.5536 | 2420 | 1 | 38909.5536 | 4 | 1 | 1321 | 1412 | 147.7411 | 0.06105 | 0.2442 | 0.06105 | 1.4774 | 0.0006105 | 0.002442 | 0.0006105 | 1.4768 | 0.0018315 | 0.7598 | 1892.7899 | 1650.7856
38909.5543 | 1992 | 0 | 38909.5543 | 3 | 0 | 1379.5 | 1470.5 | 121.6117 | 0 | 0.18315 | 0 | 1.2161 | 0 | 0.0018315 | 0 | 1.2161 | 0.0018315 | 22.4086 | 81179.3333 | 21.1925
38909.555 | 2218 | 1 | 38909.555 | 6 | 0 | 1438.5 | 1529.5 | 135.409 | 0.06105 | 0.3663 | 0 | 1.3541 | 0.0006105 | 0.003663 | 0 | 1.3535 | 0.003663 | 9.9405 | 40539.6667 | 21884.0183
38909.5556 | 174 | 8 | 38909.5556 | 32 | 38 | 1497.5 | 1588.5 | 10.6227 | 0.4884 | 1.9536 | 2.3199 | 0.10623 | 0.004884 | 0.019536 | 0.023199 | 0.10134 | 0.003663 | 1364.1722 | 74861.8457 | 28167.1245
38909.5563 | 56 | 47 | 38909.5563 | 90 | 113 | 1556 | 1647 | 3.4188 | 2.8694 | 5.4945 | 6.8987 | 0.034188 | 0.028694 | 0.054945 | 0.068987 | 0.0054945 | 0.014042 | 27871.275 | 10393.5616 | 4921.5418
38909.557 | 2401 | 0 | 38909.557 | 1848 | 41 | 1615 | 1706 | 146.5812 | 0 | 112.8205 | 2.5031 | 1.4658 | 0 | 1.1282 | 0.025031 | 1.4658 | 1.1032 | 1.5569 | 34.9408 | 0.091039
38909.5577 | 1962 | 0 | 38909.5577 | 2422 | 1 | 1673.5 | 1764.5 | 119.7802 | 0 | 147.8632 | 0.06105 | 1.1978 | 0 | 1.4786 | 0.0006105 | 1.1978 | 1.478 | 24.2803 | 0.71789 | 23.0825

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 15 |  |  | 2006-07-11 | 12:55
38909.5373 | 1 | 0 | 1 | PE | 7-C | Tray
38909.5379 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38909.5386 | 1 | 0 | 1
38909.5393 | 1 | 0 | 1
38909.54 | 1 | 0 | 1
38909.5407 | 1 | 0 | 1
38909.5413 | 1 | 0 | 1
38909.542 | 1 | 0 | 1
38909.5427 | 1 | 0 | 1
38909.5434 | 1 | 0 | 1
38909.5441 | 1 | 0 | 1
38909.5447 | 1 | 0 | 1
38909.5454 | 1 | 0 | 1
38909.5461 | 1 | 0 | 1
38909.5468 | 1 | 0 | 1
38909.5475 | 1 | 0 | 1
38909.5481 | 2 | 8 | 1
38909.5488 | 1202 | 1186 | 1
38909.5495 | 938 | 1055 | 1
38909.5502 | 1076 | 1128 | 1
38909.5509 | 3 | 10 | 1
38909.5516 | 1052 | 1021 | 1
38909.5522 | 2115 | 10 | 1
38909.5529 | 2154 | 1 | 1
38909.5536 | 2420 | 1 | 1
38909.5543 | 1992 | 0 | 1
38909.555 | 2218 | 1 | 1
38909.5556 | 174 | 8 | 1
38909.5563 | 56 | 47 | 1
38909.557 | 2401 | 0 | 1
38909.5577 | 1962 | 0 | 1
38909.5373 | 1 | 0 | 2
38909.538 | 1 | 0 | 2
38909.5386 | 1 | 0 | 2
38909.5393 | 2 | 0 | 2
38909.54 | 1 | 0 | 2
38909.5407 | 1 | 0 | 2
38909.5414 | 1 | 0 | 2
38909.542 | 1 | 0 | 2
38909.5427 | 1 | 0 | 2
38909.5434 | 1 | 0 | 2
38909.5441 | 1 | 0 | 2
38909.5448 | 1 | 0 | 2
38909.5454 | 1 | 0 | 2
38909.5461 | 1 | 0 | 2
38909.5468 | 1 | 0 | 2
38909.5475 | 1 | 0 | 2
38909.5482 | 2 | 4 | 2
38909.5488 | 1171 | 1147 | 2
38909.5495 | 982 | 1022 | 2
38909.5502 | 1066 | 1039 | 2
38909.5509 | 2 | 9 | 2
38909.5516 | 1148 | 1119 | 2
38909.5522 | 129 | 52 | 2
38909.5529 | 4 | 1 | 2
38909.5536 | 4 | 1 | 2
38909.5543 | 3 | 0 | 2
38909.555 | 6 | 0 | 2
38909.5556 | 32 | 38 | 2
38909.5563 | 90 | 113 | 2
38909.557 | 1848 | 41 | 2
38909.5577 | 2422 | 1 | 2
38909.5373 | 1 | 0 | 3
38909.538 | 1 | 0 | 3
38909.5387 | 1 | 0 | 3
38909.5393 | 1 | 0 | 3
38909.54 | 1 | 0 | 3
38909.5407 | 1 | 0 | 3
38909.5414 | 1 | 0 | 3
38909.5421 | 1 | 0 | 3
38909.5427 | 1 | 0 | 3
38909.5434 | 1 | 0 | 3
38909.5441 | 1 | 0 | 3
38909.5448 | 1 | 0 | 3
38909.5455 | 1 | 0 | 3
38909.5461 | 1 | 0 | 3
38909.5468 | 1 | 0 | 3
38909.5475 | 1 | 0 | 3
38909.5482 | 2 | 2 | 3
38909.5489 | 3 | 10 | 3
38909.5495 | 2 | 10 | 3
38909.5502 | 2 | 10 | 3
38909.5509 | 2 | 7 | 3
38909.5516 | 3 | 10 | 3
38909.5523 | 2086 | 8 | 3
38909.5529 | 2342 | 1 | 3
38909.5536 | 2380 | 0 | 3
38909.5543 | 2194 | 0 | 3
38909.555 | 1598 | 18 | 3
38909.5557 | 18 | 2 | 3
38909.5563 | 2 | 4 | 3
38909.557 | 2029 | 1 | 3
38909.5577 | 2373 | 0 | 3
38909.5373 | 1 | 0 | 4
38909.538 | 1 | 0 | 4
38909.5387 | 1 | 0 | 4
38909.5394 | 1 | 0 | 4
38909.54 | 1 | 0 | 4
38909.5407 | 1 | 0 | 4
38909.5414 | 1 | 0 | 4
38909.5421 | 1 | 0 | 4
38909.5428 | 1 | 0 | 4
38909.5434 | 1 | 0 | 4
38909.5441 | 1 | 0 | 4
38909.5448 | 1 | 0 | 4
38909.5455 | 1 | 0 | 4
38909.5462 | 1 | 0 | 4
38909.5468 | 1 | 0 | 4
38909.5475 | 1 | 0 | 4
38909.5482 | 1 | 1 | 4
38909.5489 | 2 | 6 | 4
38909.5496 | 2 | 7 | 4
38909.5502 | 2 | 7 | 4
38909.5509 | 2 | 6 | 4
38909.5516 | 3 | 9 | 4
38909.5523 | 3 | 7 | 4
38909.553 | 3 | 1 | 4
38909.5536 | 3 | 0 | 4
38909.5543 | 3 | 0 | 4
38909.555 | 3 | 0 | 4
38909.5557 | 2 | 1 | 4
38909.5564 | 2 | 2 | 4
38909.557 | 3 | 0 | 4
38909.5577 | 3 | 1 | 4
38909.5373 | 1 | 0 | 5
38909.538 | 1 | 0 | 5
38909.5387 | 1 | 0 | 5
38909.5394 | 1 | 0 | 5
38909.54 | 1 | 0 | 5
38909.5407 | 1 | 0 | 5
38909.5414 | 1 | 0 | 5
38909.5421 | 1 | 0 | 5
38909.5428 | 1 | 0 | 5
38909.5434 | 1 | 0 | 5
38909.5441 | 1 | 0 | 5
38909.5448 | 1 | 0 | 5
38909.5455 | 1 | 0 | 5
38909.5462 | 1 | 0 | 5
38909.5469 | 1 | 0 | 5
38909.5475 | 1 | 0 | 5
38909.5482 | 1 | 1 | 5
38909.5489 | 2 | 5 | 5
38909.5496 | 2 | 6 | 5
38909.5503 | 1 | 6 | 5
38909.5509 | 1195 | 1120 | 5
38909.5516 | 966 | 935 | 5
38909.5523 | 2238 | 853 | 5
38909.553 | 2278 | 1 | 5
38909.5537 | 2313 | 1 | 5
38909.5543 | 2544 | 1 | 5
38909.555 | 1981 | 1 | 5
38909.5557 | 2 | 1 | 5
38909.5564 | 2 | 1 | 5
38909.5571 | 2535 | 0 | 5
38909.5577 | 2530 | 0 | 5
38909.5373 | 1 | 0 | 6
38909.538 | 1 | 0 | 6
38909.5387 | 1 | 0 | 6
38909.5394 | 1 | 0 | 6
38909.5401 | 1 | 0 | 6
38909.5407 | 1 | 0 | 6
38909.5414 | 1 | 0 | 6
38909.5421 | 1 | 0 | 6
38909.5428 | 1 | 0 | 6
38909.5435 | 1 | 0 | 6
38909.5441 | 1 | 0 | 6
38909.5448 | 1 | 0 | 6
38909.5455 | 1 | 0 | 6
38909.5462 | 1 | 0 | 6
38909.5469 | 1 | 0 | 6
38909.5475 | 1 | 0 | 6
38909.5482 | 1 | 1 | 6
38909.5489 | 2 | 3 | 6
38909.5496 | 2 | 3 | 6
38909.5503 | 2 | 5 | 6
38909.5509 | 962 | 929 | 6
38909.5516 | 1024 | 994 | 6
38909.5523 | 2230 | 986 | 6
38909.553 | 2073 | 1 | 6
38909.5537 | 2296 | 0 | 6
38909.5544 | 2125 | 0 | 6
38909.555 | 2002 | 0 | 6
38909.5557 | 2398 | 1 | 6
38909.5564 | 2367 | 1 | 6
38909.5571 | 2296 | 1 | 6
38909.5578 | 1919 | 0 | 6
38909.5374 | 1 | 0 | 7
38909.538 | 1 | 0 | 7
38909.5387 | 1 | 0 | 7
38909.5394 | 1 | 0 | 7
38909.5401 | 1 | 0 | 7
38909.5408 | 1 | 0 | 7
38909.5414 | 1 | 0 | 7
38909.5421 | 1 | 0 | 7
38909.5428 | 1 | 0 | 7
38909.5435 | 1 | 0 | 7
38909.5442 | 1 | 0 | 7
38909.5448 | 1 | 0 | 7
38909.5455 | 1 | 0 | 7
38909.5462 | 1 | 0 | 7
38909.5469 | 1 | 0 | 7
38909.5476 | 1 | 0 | 7
38909.5482 | 1 | 1 | 7
38909.5489 | 1 | 2 | 7
38909.5496 | 2 | 2 | 7
38909.5503 | 2 | 2 | 7
38909.551 | 1018 | 986 | 7
38909.5516 | 1133 | 1104 | 7
38909.5523 | 2053 | 738 | 7
38909.553 | 2152 | 1 | 7
38909.5537 | 2182 | 0 | 7
38909.5544 | 2172 | 1 | 7
38909.555 | 2191 | 1 | 7
38909.5557 | 5 | 1 | 7
38909.5564 | 2 | 1 | 7
38909.5571 | 2549 | 1 | 7
38909.5578 | 2150 | 0 | 7
38909.5374 | 1 | 0 | 8
38909.5381 | 1 | 0 | 8
38909.5387 | 1 | 0 | 8
38909.5394 | 1 | 0 | 8
38909.5401 | 1 | 0 | 8
38909.5408 | 1 | 0 | 8
38909.5415 | 1 | 0 | 8
38909.5421 | 1 | 0 | 8
38909.5428 | 1 | 0 | 8
38909.5435 | 1 | 0 | 8
38909.5442 | 1 | 0 | 8
38909.5449 | 1 | 0 | 8
38909.5455 | 1 | 0 | 8
38909.5462 | 1 | 0 | 8
38909.5469 | 1 | 0 | 8
38909.5476 | 1 | 0 | 8
38909.5483 | 1 | 0 | 8
38909.5489 | 2 | 1 | 8
38909.5496 | 2 | 2 | 8
38909.5503 | 1 | 2 | 8
38909.551 | 1119 | 1170 | 8
38909.5517 | 1068 | 1038 | 8
38909.5523 | 1904 | 850 | 8
38909.553 | 2227 | 0 | 8
38909.5537 | 2488 | 1 | 8
38909.5544 | 2489 | 1 | 8
38909.5551 | 2157 | 0 | 8
38909.5557 | 1962 | 0 | 8
38909.5564 | 2056 | 1 | 8
38909.5571 | 2044 | 1 | 8
38909.5578 | 1645 | 0 | 8
38909.5374 | 1 | 1 | 9
38909.5381 | 1 | 0 | 9
38909.5387 | 1 | 0 | 9
38909.5394 | 1 | 0 | 9
38909.5401 | 1 | 0 | 9
38909.5408 | 1 | 0 | 9
38909.5415 | 1 | 0 | 9
38909.5422 | 1 | 0 | 9
38909.5428 | 1 | 0 | 9
38909.5435 | 1 | 0 | 9
38909.5442 | 1 | 0 | 9
38909.5449 | 1 | 0 | 9
38909.5456 | 1 | 0 | 9
38909.5462 | 1 | 0 | 9
38909.5469 | 1 | 0 | 9
38909.5476 | 1 | 0 | 9
38909.5483 | 999 | 1040 | 9
38909.549 | 1197 | 1177 | 9
38909.5496 | 1103 | 1076 | 9
38909.5503 | 992 | 1030 | 9
38909.551 | 993 | 962 | 9
38909.5517 | 965 | 1120 | 9
38909.5524 | 2153 | 310 | 9
38909.553 | 2280 | 1 | 9
38909.5537 | 2189 | 0 | 9
38909.5544 | 2546 | 0 | 9
38909.5551 | 948 | 914 | 9
38909.5558 | 943 | 971 | 9
38909.5564 | 1055 | 1025 | 9
38909.5571 | 1993 | 0 | 9
38909.5578 | 2454 | 0 | 9
38909.5374 | 1 | 0 | 10
38909.5381 | 1 | 0 | 10
38909.5388 | 1 | 0 | 10
38909.5394 | 1 | 0 | 10
38909.5401 | 1 | 0 | 10
38909.5408 | 1 | 0 | 10
38909.5415 | 1 | 0 | 10
38909.5422 | 1 | 0 | 10
38909.5428 | 1 | 0 | 10
38909.5435 | 1 | 0 | 10
38909.5442 | 1 | 0 | 10
38909.5449 | 1 | 0 | 10
38909.5456 | 1 | 0 | 10
38909.5462 | 1 | 0 | 10
38909.5469 | 1 | 0 | 10
38909.5476 | 1 | 0 | 10
38909.5483 | 1052 | 1024 | 10
38909.549 | 1075 | 1048 | 10
38909.5497 | 1108 | 1162 | 10
38909.5503 | 1093 | 1065 | 10
38909.551 | 1053 | 1024 | 10
38909.5517 | 933 | 950 | 10
38909.5524 | 2234 | 739 | 10
38909.5531 | 2216 | 1 | 10
38909.5537 | 2250 | 0 | 10
38909.5544 | 2056 | 0 | 10
38909.5551 | 967 | 932 | 10
38909.5558 | 1069 | 1038 | 10
38909.5565 | 1129 | 1099 | 10
38909.5571 | 2339 | 1 | 10
38909.5578 | 2529 | 0 | 10
38909.5374 | 1 | 0 | 11
38909.5381 | 1 | 0 | 11
38909.5388 | 1 | 0 | 11
38909.5395 | 1 | 0 | 11
38909.5401 | 1 | 0 | 11
38909.5408 | 1 | 0 | 11
38909.5415 | 1 | 0 | 11
38909.5422 | 1 | 0 | 11
38909.5429 | 1 | 0 | 11
38909.5435 | 1 | 0 | 11
38909.5442 | 1 | 0 | 11
38909.5449 | 1 | 0 | 11
38909.5456 | 1 | 0 | 11
38909.5463 | 1 | 0 | 11
38909.5469 | 1 | 0 | 11
38909.5476 | 1114 | 1179 | 11
38909.5483 | 1128 | 1102 | 11
38909.549 | 952 | 1072 | 11
38909.5497 | 980 | 950 | 11
38909.5503 | 945 | 976 | 11
38909.551 | 997 | 967 | 11
38909.5517 | 1024 | 995 | 11
38909.5524 | 1960 | 604 | 11
38909.5531 | 2250 | 1 | 11
38909.5537 | 2039 | 0 | 11
38909.5544 | 2107 | 0 | 11
38909.5551 | 939 | 935 | 11
38909.5558 | 1101 | 1070 | 11
38909.5565 | 945 | 920 | 11
38909.5572 | 2487 | 0 | 11
38909.5578 | 2063 | 0 | 11
38909.5374 | 1 | 0 | 12
38909.5381 | 1 | 0 | 12
38909.5388 | 1 | 0 | 12
38909.5395 | 1 | 0 | 12
38909.5402 | 1 | 0 | 12
38909.5408 | 1 | 0 | 12
38909.5415 | 1 | 0 | 12
38909.5422 | 1 | 0 | 12
38909.5429 | 1 | 0 | 12
38909.5436 | 1 | 0 | 12
38909.5442 | 2 | 0 | 12
38909.5449 | 1 | 0 | 12
38909.5456 | 1 | 0 | 12
38909.5463 | 1 | 0 | 12
38909.547 | 1 | 0 | 12
38909.5476 | 1014 | 1128 | 12
38909.5483 | 1143 | 1115 | 12
38909.549 | 943 | 915 | 12
38909.5497 | 1062 | 1154 | 12
38909.5504 | 1035 | 1006 | 12
38909.551 | 1083 | 1054 | 12
38909.5517 | 1009 | 1048 | 12
38909.5524 | 2156 | 594 | 12
38909.5531 | 2107 | 1 | 12
38909.5538 | 2043 | 0 | 12
38909.5544 | 2384 | 0 | 12
38909.5551 | 1057 | 1025 | 12
38909.5558 | 949 | 1064 | 12
38909.5565 | 934 | 961 | 12
38909.5572 | 2003 | 0 | 12
38909.5578 | 1986 | 0 | 12
38909.5375 | 1 | 0 | 13
38909.5381 | 1 | 0 | 13
38909.5388 | 1 | 0 | 13
38909.5395 | 1 | 0 | 13
38909.5402 | 1 | 0 | 13
38909.5409 | 1 | 0 | 13
38909.5415 | 1 | 0 | 13
38909.5422 | 1 | 0 | 13
38909.5429 | 1 | 0 | 13
38909.5436 | 1 | 0 | 13
38909.5443 | 1 | 0 | 13
38909.5449 | 1 | 0 | 13
38909.5456 | 1 | 0 | 13
38909.5463 | 1 | 0 | 13
38909.547 | 1 | 0 | 13
38909.5477 | 2 | 7 | 13
38909.5483 | 2 | 9 | 13
38909.549 | 2 | 10 | 13
38909.5497 | 2 | 10 | 13
38909.5504 | 3 | 10 | 13
38909.5511 | 3 | 10 | 13
38909.5517 | 3 | 10 | 13
38909.5524 | 3 | 8 | 13
38909.5531 | 3 | 0 | 13
38909.5538 | 3 | 0 | 13
38909.5545 | 4 | 0 | 13
38909.5552 | 3 | 8 | 13
38909.5558 | 3 | 8 | 13
38909.5565 | 2 | 9 | 13
38909.5572 | 2128 | 0 | 13
38909.5579 | 2089 | 0 | 13
38909.5375 | 1 | 0 | 14
38909.5381 | 1 | 0 | 14
38909.5388 | 1 | 0 | 14
38909.5395 | 1 | 0 | 14
38909.5402 | 1 | 0 | 14
38909.5409 | 1 | 0 | 14
38909.5416 | 2 | 0 | 14
38909.5422 | 1 | 0 | 14
38909.5429 | 1 | 0 | 14
38909.5436 | 1 | 0 | 14
38909.5443 | 1 | 0 | 14
38909.545 | 1 | 0 | 14
38909.5456 | 1 | 0 | 14
38909.5463 | 1 | 0 | 14
38909.547 | 1 | 0 | 14
38909.5477 | 1 | 4 | 14
38909.5484 | 2 | 7 | 14
38909.549 | 2 | 7 | 14
38909.5497 | 2 | 7 | 14
38909.5504 | 2 | 7 | 14
38909.5511 | 2 | 9 | 14
38909.5518 | 2 | 8 | 14
38909.5524 | 2 | 7 | 14
38909.5531 | 3 | 1 | 14
38909.5538 | 3 | 0 | 14
38909.5545 | 3 | 0 | 14
38909.5552 | 2 | 5 | 14
38909.5558 | 2 | 6 | 14
38909.5572 | 2 | 0 | 14
38909.5579 | 3 | 0 | 14
38909.5375 | 1 | 0 | 15
38909.5382 | 1 | 0 | 15
38909.5388 | 1 | 0 | 15
38909.5395 | 1 | 0 | 15
38909.5402 | 1 | 0 | 15
38909.5409 | 1 | 0 | 15
38909.5416 | 1 | 0 | 15
38909.5422 | 1 | 0 | 15
38909.5429 | 1 | 0 | 15
38909.5436 | 1 | 0 | 15
38909.5443 | 1 | 0 | 15
38909.545 | 1 | 0 | 15
38909.5456 | 1 | 0 | 15
38909.5463 | 1 | 0 | 15
38909.547 | 1 | 0 | 15
38909.5477 | 2 | 2 | 15
38909.5484 | 2 | 5 | 15
38909.5491 | 2 | 5 | 15
38909.5497 | 2 | 6 | 15
38909.5504 | 2 | 5 | 15
38909.5511 | 2 | 8 | 15
38909.5518 | 936 | 969 | 15
38909.5525 | 2 | 6 | 15
38909.5531 | 2 | 1 | 15
38909.5538 | 3 | 0 | 15
38909.5545 | 3 | 0 | 15
38909.5552 | 3 | 4 | 15
38909.5559 | 2 | 5 | 15
38909.5565 | 2 | 5 | 15
38909.5572 | 2118 | 0 | 15
38909.5579 | 2548 | 1 | 15
38909.5375 | 1 | 0 | 16
38909.5382 | 1 | 0 | 16
38909.5389 | 1 | 0 | 16
38909.5395 | 1 | 0 | 16
38909.5402 | 1 | 0 | 16
38909.5409 | 1 | 0 | 16
38909.5416 | 1 | 0 | 16
38909.5423 | 1 | 0 | 16
38909.543 | 1 | 0 | 16
38909.5436 | 1 | 0 | 16
38909.5443 | 1 | 0 | 16
38909.545 | 1 | 0 | 16
38909.5457 | 1 | 0 | 16
38909.5463 | 1 | 0 | 16
38909.547 | 1 | 0 | 16
38909.5477 | 1 | 1 | 16
38909.5484 | 1 | 4 | 16
38909.5491 | 2 | 4 | 16
38909.5497 | 2 | 4 | 16
38909.5504 | 2 | 4 | 16
38909.5511 | 2 | 7 | 16
38909.5518 | 928 | 960 | 16
38909.5525 | 2156 | 6 | 16
38909.5531 | 1968 | 1 | 16
38909.5538 | 2088 | 0 | 16
38909.5545 | 2399 | 0 | 16
38909.5552 | 1977 | 3 | 16
38909.5559 | 2472 | 3 | 16
38909.5566 | 2237 | 3 | 16
38909.5572 | 2031 | 1 | 16
38909.5579 | 2228 | 1 | 16
38909.5375 | 1 | 0 | 17
38909.5382 | 1 | 0 | 17
38909.5389 | 1 | 0 | 17
38909.5396 | 1 | 0 | 17
38909.5402 | 1 | 0 | 17
38909.5409 | 1 | 0 | 17
38909.5416 | 1 | 0 | 17
38909.5423 | 1 | 0 | 17
38909.543 | 1 | 0 | 17
38909.5436 | 1 | 0 | 17
38909.5443 | 1 | 0 | 17
38909.545 | 1 | 0 | 17
38909.5457 | 1 | 0 | 17
38909.5464 | 1 | 0 | 17
38909.547 | 1 | 0 | 17
38909.5477 | 1 | 1 | 17
38909.5484 | 1 | 2 | 17
38909.5491 | 1 | 2 | 17
38909.5498 | 2 | 3 | 17
38909.5505 | 1 | 2 | 17
38909.5511 | 2 | 6 | 17
38909.5518 | 1119 | 1090 | 17
38909.5525 | 3 | 5 | 17
38909.5532 | 3 | 1 | 17
38909.5539 | 3 | 0 | 17
38909.5545 | 3 | 0 | 17
38909.5552 | 3 | 2 | 17
38909.5559 | 3 | 2 | 17
38909.5566 | 2 | 2 | 17
38909.5573 | 2097 | 0 | 17
38909.5579 | 2030 | 0 | 17
38909.5375 | 1 | 0 | 18
38909.5382 | 5 | 0 | 18
38909.5389 | 1 | 0 | 18
38909.5396 | 1 | 0 | 18
38909.5403 | 1 | 0 | 18
38909.5409 | 1 | 0 | 18
38909.5416 | 1 | 0 | 18
38909.5423 | 1 | 0 | 18
38909.543 | 1 | 0 | 18
38909.5437 | 1 | 0 | 18
38909.5443 | 1 | 0 | 18
38909.545 | 1 | 0 | 18
38909.5457 | 1 | 0 | 18
38909.5464 | 1 | 0 | 18
38909.5471 | 1 | 0 | 18
38909.5477 | 1 | 1 | 18
38909.5484 | 1 | 1 | 18
38909.5491 | 1 | 1 | 18
38909.5498 | 1 | 2 | 18
38909.5505 | 1 | 2 | 18
38909.5511 | 2 | 6 | 18
38909.5518 | 656 | 589 | 18
38909.5525 | 2097 | 5 | 18
38909.5532 | 2266 | 1 | 18
38909.5539 | 2388 | 0 | 18
38909.5545 | 2387 | 0 | 18
38909.5552 | 2100 | 1 | 18
38909.5559 | 2189 | 1 | 18
38909.5566 | 2052 | 2 | 18
38909.5573 | 2177 | 0 | 18
38909.558 | 1803 | 1 | 18
38909.5375 | 1 | 0 | 19
38909.5382 | 1 | 0 | 19
38909.5389 | 1 | 0 | 19
38909.5396 | 1 | 0 | 19
38909.5403 | 1 | 0 | 19
38909.5409 | 1 | 0 | 19
38909.5416 | 1 | 0 | 19
38909.5423 | 1 | 0 | 19
38909.543 | 1 | 0 | 19
38909.5437 | 1 | 0 | 19
38909.5444 | 1 | 0 | 19
38909.545 | 1 | 0 | 19
38909.5457 | 1 | 0 | 19
38909.5464 | 1 | 0 | 19
38909.5471 | 1 | 0 | 19
38909.5478 | 1 | 0 | 19
38909.5484 | 1 | 1 | 19
38909.5491 | 936 | 967 | 19
38909.5498 | 1131 | 1105 | 19
38909.5505 | 599 | 873 | 19
38909.5512 | 2 | 5 | 19
38909.5518 | 315 | 367 | 19
38909.5525 | 3 | 5 | 19
38909.5532 | 3 | 1 | 19
38909.5539 | 2 | 0 | 19
38909.5546 | 3 | 1 | 19
38909.5552 | 3 | 1 | 19
38909.5559 | 2 | 2 | 19
38909.5566 | 140 | 166 | 19
38909.5573 | 2256 | 1 | 19
38909.558 | 2555 | 0 | 19
38909.5376 | 1 | 0 | 20
38909.5383 | 1 | 0 | 20
38909.5389 | 1 | 0 | 20
38909.5396 | 1 | 0 | 20
38909.5403 | 1 | 0 | 20
38909.541 | 1 | 0 | 20
38909.5417 | 1 | 0 | 20
38909.5423 | 1 | 0 | 20
38909.543 | 1 | 0 | 20
38909.5437 | 1 | 0 | 20
38909.5444 | 1 | 0 | 20
38909.5451 | 1 | 0 | 20
38909.5457 | 1 | 0 | 20
38909.5464 | 1 | 0 | 20
38909.5471 | 1 | 0 | 20
38909.5478 | 1 | 1 | 20
38909.5485 | 1 | 1 | 20
38909.5491 | 1044 | 1015 | 20
38909.5498 | 1167 | 1197 | 20
38909.5505 | 1 | 2 | 20
38909.5512 | 2 | 5 | 20
38909.5519 | 478 | 459 | 20
38909.5525 | 2011 | 5 | 20
38909.5532 | 2176 | 1 | 20
38909.5539 | 2436 | 0 | 20
38909.5546 | 2394 | 0 | 20
38909.5553 | 65 | 2 | 20
38909.5559 | 49 | 1 | 20
38909.5566 | 601 | 581 | 20
38909.5573 | 2012 | 0 | 20
38909.558 | 2332 | 0 | 20
38909.5376 | 1 | 0 | 21
38909.5383 | 1 | 0 | 21
38909.5389 | 1 | 0 | 21
38909.5396 | 1 | 0 | 21
38909.5403 | 1 | 0 | 21
38909.541 | 1 | 0 | 21
38909.5417 | 1 | 0 | 21
38909.5423 | 1 | 0 | 21
38909.543 | 1 | 0 | 21
38909.5437 | 1 | 0 | 21
38909.5444 | 1 | 0 | 21
38909.5451 | 1 | 0 | 21
38909.5458 | 1 | 0 | 21
38909.5464 | 1 | 0 | 21
38909.5471 | 1 | 0 | 21
38909.5478 | 1 | 1 | 21
38909.5485 | 1 | 1 | 21
38909.5492 | 947 | 919 | 21
38909.5498 | 1186 | 1198 | 21
38909.5505 | 1 | 1 | 21
38909.5512 | 2 | 4 | 21
38909.5519 | 621 | 601 | 21
38909.5526 | 3 | 4 | 21
38909.5532 | 3 | 1 | 21
38909.5539 | 2 | 0 | 21
38909.5546 | 2072 | 35 | 21
38909.5553 | 2 | 1 | 21
38909.556 | 3 | 1 | 21
38909.5566 | 3 | 5 | 21
38909.5573 | 1781 | 50 | 21
38909.558 | 2086 | 0 | 21
38909.5376 | 1 | 0 | 22
38909.5383 | 1 | 0 | 22
38909.539 | 1 | 0 | 22
38909.5396 | 1 | 0 | 22
38909.5403 | 1 | 0 | 22
38909.541 | 1 | 0 | 22
38909.5417 | 1 | 0 | 22
38909.5424 | 1 | 0 | 22
38909.543 | 1 | 0 | 22
38909.5437 | 1 | 0 | 22
38909.5444 | 1 | 0 | 22
38909.5451 | 1 | 0 | 22
38909.5458 | 1 | 0 | 22
38909.5464 | 1 | 0 | 22
38909.5471 | 1 | 0 | 22
38909.5478 | 1 | 0 | 22
38909.5485 | 1 | 1 | 22
38909.5492 | 1135 | 1106 | 22
38909.5498 | 1011 | 981 | 22
38909.5505 | 1 | 1 | 22
38909.5512 | 1 | 4 | 22
38909.5519 | 20 | 23 | 22
38909.5526 | 1915 | 4 | 22
38909.5533 | 2321 | 1 | 22
38909.5539 | 2284 | 0 | 22
38909.5546 | 1948 | 1 | 22
38909.5553 | 2095 | 1 | 22
38909.556 | 4 | 1 | 22
38909.5567 | 23 | 19 | 22
38909.5573 | 1987 | 0 | 22
38909.558 | 2016 | 0 | 22
38909.5376 | 1 | 0 | 23
38909.5383 | 1 | 0 | 23
38909.539 | 1 | 0 | 23
38909.5397 | 1 | 0 | 23
38909.5403 | 1 | 0 | 23
38909.541 | 1 | 0 | 23
38909.5417 | 1 | 0 | 23
38909.5424 | 1 | 0 | 23
38909.5431 | 1 | 0 | 23
38909.5437 | 1 | 0 | 23
38909.5444 | 1 | 0 | 23
38909.5451 | 1 | 0 | 23
38909.5458 | 1 | 0 | 23
38909.5465 | 1 | 0 | 23
38909.5471 | 1 | 0 | 23
38909.5478 | 1 | 0 | 23
38909.5485 | 1 | 1 | 23
38909.5492 | 3 | 10 | 23
38909.5499 | 2 | 11 | 23
38909.5505 | 1 | 1 | 23
38909.5512 | 2 | 4 | 23
38909.5519 | 3 | 8 | 23
38909.5526 | 3 | 4 | 23
38909.5533 | 3 | 1 | 23
38909.5539 | 3 | 0 | 23
38909.5546 | 3 | 0 | 23
38909.5553 | 2 | 1 | 23
38909.556 | 2 | 1 | 23
38909.5567 | 2 | 1 | 23
38909.5573 | 3 | 1 | 23
38909.558 | 3 | 1 | 23
38909.5376 | 1 | 0 | 24
38909.5383 | 1 | 0 | 24
38909.539 | 2 | 0 | 24
38909.5397 | 2 | 0 | 24
38909.5404 | 1 | 0 | 24
38909.541 | 1 | 0 | 24
38909.5417 | 1 | 0 | 24
38909.5424 | 1 | 0 | 24
38909.5431 | 1 | 0 | 24
38909.5438 | 1 | 0 | 24
38909.5444 | 1 | 0 | 24
38909.5451 | 1 | 0 | 24
38909.5458 | 1 | 0 | 24
38909.5465 | 1 | 0 | 24
38909.5472 | 1 | 0 | 24
38909.5478 | 1 | 0 | 24
38909.5485 | 1 | 0 | 24
38909.5492 | 2 | 7 | 24
38909.5499 | 2 | 7 | 24
38909.5506 | 1 | 1 | 24
38909.5512 | 1 | 3 | 24
38909.5519 | 3 | 7 | 24
38909.5526 | 2262 | 3 | 24
38909.5533 | 2516 | 0 | 24
38909.554 | 2443 | 0 | 24
38909.5546 | 2212 | 0 | 24
38909.5553 | 2524 | 1 | 24
38909.556 | 2475 | 0 | 24
38909.5567 | 2457 | 1 | 24
38909.5574 | 2458 | 0 | 24
38909.558 | 1709 | 1 | 24
38909.5377 | 1 | 0 | 25
38909.5383 | 1 | 0 | 25
38909.539 | 1 | 0 | 25
38909.5397 | 1 | 0 | 25
38909.5404 | 1 | 0 | 25
38909.5411 | 1 | 0 | 25
38909.5417 | 1 | 0 | 25
38909.5424 | 1 | 0 | 25
38909.5431 | 1 | 0 | 25
38909.5438 | 1 | 0 | 25
38909.5445 | 1 | 0 | 25
38909.5451 | 1 | 0 | 25
38909.5458 | 1 | 0 | 25
38909.5465 | 1 | 0 | 25
38909.5472 | 1 | 0 | 25
38909.5479 | 1 | 0 | 25
38909.5485 | 1 | 1 | 25
38909.5492 | 2 | 6 | 25
38909.5499 | 2 | 6 | 25
38909.5506 | 1 | 1 | 25
38909.5513 | 1 | 3 | 25
38909.5519 | 2 | 7 | 25
38909.5526 | 3 | 3 | 25
38909.5533 | 2 | 0 | 25
38909.554 | 3 | 1 | 25
38909.5547 | 3 | 0 | 25
38909.5553 | 3 | 1 | 25
38909.556 | 3 | 1 | 25
38909.5567 | 2 | 1 | 25
38909.5574 | 3 | 1 | 25
38909.5581 | 3 | 0 | 25
38909.5377 | 1 | 0 | 26
38909.5383 | 1 | 0 | 26
38909.539 | 1 | 0 | 26
38909.5397 | 1 | 0 | 26
38909.5404 | 1 | 0 | 26
38909.5411 | 1 | 1 | 26
38909.5417 | 1 | 0 | 26
38909.5424 | 1 | 0 | 26
38909.5431 | 1 | 0 | 26
38909.5438 | 1 | 0 | 26
38909.5445 | 1 | 0 | 26
38909.5452 | 1 | 0 | 26
38909.5458 | 1 | 0 | 26
38909.5465 | 1 | 0 | 26
38909.5472 | 1 | 0 | 26
38909.5479 | 1 | 0 | 26
38909.5486 | 1 | 0 | 26
38909.5492 | 2 | 5 | 26
38909.5499 | 1 | 5 | 26
38909.5506 | 1 | 1 | 26
38909.5513 | 1 | 2 | 26
38909.552 | 2 | 6 | 26
38909.5526 | 2301 | 4 | 26
38909.5533 | 2201 | 0 | 26
38909.554 | 2049 | 0 | 26
38909.5547 | 2515 | 0 | 26
38909.5554 | 2199 | 1 | 26
38909.556 | 2014 | 1 | 26
38909.5567 | 2193 | 1 | 26
38909.5574 | 2423 | 1 | 26
38909.5581 | 1605 | 1 | 26
38909.5377 | 1 | 0 | 27
38909.5384 | 1 | 0 | 27
38909.539 | 1 | 0 | 27
38909.5397 | 1 | 0 | 27
38909.5404 | 1 | 0 | 27
38909.5411 | 1 | 0 | 27
38909.5418 | 1 | 0 | 27
38909.5424 | 1 | 0 | 27
38909.5431 | 1 | 0 | 27
38909.5438 | 1 | 0 | 27
38909.5445 | 1 | 0 | 27
38909.5452 | 1 | 0 | 27
38909.5458 | 1 | 0 | 27
38909.5465 | 1 | 0 | 27
38909.5472 | 1 | 0 | 27
38909.5479 | 1 | 0 | 27
38909.5486 | 1 | 0 | 27
38909.5492 | 2 | 3 | 27
38909.5499 | 2 | 3 | 27
38909.5506 | 1 | 1 | 27
38909.5513 | 1 | 2 | 27
38909.552 | 2 | 7 | 27
38909.5527 | 2 | 3 | 27
38909.5533 | 3 | 0 | 27
38909.554 | 3 | 0 | 27
38909.5547 | 2 | 0 | 27
38909.5554 | 3 | 1 | 27
38909.5561 | 3 | 0 | 27
38909.5567 | 3 | 1 | 27
38909.5574 | 3 | 0 | 27
38909.5581 | 3 | 1 | 27
38909.5377 | 1 | 0 | 28
38909.5384 | 1 | 1 | 28
38909.5391 | 1 | 0 | 28
38909.5397 | 1 | 0 | 28
38909.5404 | 1 | 0 | 28
38909.5411 | 1 | 0 | 28
38909.5418 | 1 | 0 | 28
38909.5425 | 1 | 0 | 28
38909.5431 | 1 | 0 | 28
38909.5438 | 1 | 0 | 28
38909.5445 | 1 | 0 | 28
38909.5452 | 1 | 0 | 28
38909.5459 | 1 | 0 | 28
38909.5465 | 1 | 0 | 28
38909.5472 | 1 | 0 | 28
38909.5479 | 1 | 0 | 28
38909.5486 | 1 | 1 | 28
38909.5493 | 1 | 2 | 28
38909.5499 | 1 | 2 | 28
38909.5506 | 2 | 0 | 28
38909.5513 | 1 | 1 | 28
38909.552 | 2 | 6 | 28
38909.5527 | 2108 | 3 | 28
38909.5533 | 2014 | 1 | 28
38909.554 | 2454 | 1 | 28
38909.5547 | 2046 | 0 | 28
38909.5554 | 2342 | 1 | 28
38909.5561 | 226 | 2 | 28
38909.5567 | 3 | 1 | 28
38909.5574 | 2025 | 0 | 28
38909.5581 | 2217 | 0 | 28
38909.5377 | 1 | 0 | 29
38909.5384 | 1 | 0 | 29
38909.5391 | 1 | 0 | 29
38909.5398 | 1 | 0 | 29
38909.5404 | 1 | 0 | 29
38909.5411 | 1 | 0 | 29
38909.5418 | 1 | 0 | 29
38909.5425 | 1 | 0 | 29
38909.5432 | 1 | 0 | 29
38909.5438 | 1 | 0 | 29
38909.5445 | 1 | 0 | 29
38909.5452 | 1 | 0 | 29
38909.5459 | 1 | 0 | 29
38909.5466 | 1 | 0 | 29
38909.5472 | 1 | 0 | 29
38909.5479 | 1 | 0 | 29
38909.5486 | 1 | 1 | 29
38909.5493 | 1 | 1 | 29
38909.55 | 1 | 2 | 29
38909.5506 | 1 | 1 | 29
38909.5513 | 1 | 1 | 29
38909.552 | 2 | 6 | 29
38909.5527 | 3 | 3 | 29
38909.5534 | 3 | 1 | 29
38909.554 | 2 | 0 | 29
38909.5547 | 3 | 0 | 29
38909.5554 | 2 | 1 | 29
38909.5561 | 2 | 0 | 29
38909.5568 | 2 | 1 | 29
38909.5574 | 3 | 0 | 29
38909.5581 | 3 | 0 | 29
38909.5377 | 1 | 0 | 30
38909.5384 | 1 | 0 | 30
38909.5391 | 1 | 0 | 30
38909.5398 | 1 | 0 | 30
38909.5405 | 1 | 0 | 30
38909.5411 | 1 | 0 | 30
38909.5418 | 1 | 0 | 30
38909.5425 | 1 | 0 | 30
38909.5432 | 1 | 0 | 30
38909.5439 | 1 | 0 | 30
38909.5445 | 1 | 0 | 30
38909.5452 | 1 | 0 | 30
38909.5459 | 1 | 0 | 30
38909.5466 | 1 | 0 | 30
38909.5473 | 1 | 0 | 30
38909.5479 | 1 | 0 | 30
38909.5486 | 1 | 0 | 30
38909.5493 | 1 | 1 | 30
38909.55 | 2 | 1 | 30
38909.5507 | 1 | 1 | 30
38909.5513 | 1 | 1 | 30
38909.552 | 2 | 6 | 30
38909.5527 | 2429 | 3 | 30
38909.5534 | 2023 | 1 | 30
38909.5541 | 2511 | 0 | 30
38909.5547 | 2507 | 0 | 30
38909.5554 | 2543 | 0 | 30
38909.5561 | 752 | 1 | 30
38909.5568 | 2 | 1 | 30
38909.5575 | 2107 | 0 | 30
38909.5581 | 2035 | 1 | 30
38909.5377 | 1 | 0 | 31
38909.5384 | 1 | 0 | 31
38909.5391 | 1 | 0 | 31
38909.5398 | 1 | 0 | 31
38909.5405 | 1 | 0 | 31
38909.5411 | 1 | 0 | 31
38909.5418 | 1 | 0 | 31
38909.5425 | 1 | 0 | 31
38909.5432 | 1 | 0 | 31
38909.5439 | 1 | 0 | 31
38909.5445 | 1 | 0 | 31
38909.5452 | 1 | 0 | 31
38909.5459 | 1 | 0 | 31
38909.5466 | 1 | 0 | 31
38909.5473 | 1 | 0 | 31
38909.548 | 960 | 929 | 31
38909.5486 | 1078 | 1049 | 31
38909.5493 | 1078 | 1133 | 31
38909.55 | 927 | 989 | 31
38909.5507 | 1178 | 1199 | 31
38909.5514 | 966 | 945 | 31
38909.552 | 1038 | 1004 | 31
38909.5527 | 2474 | 3 | 31
38909.5534 | 2282 | 0 | 31
38909.5541 | 1967 | 1 | 31
38909.5548 | 2520 | 1 | 31
38909.5554 | 2245 | 1 | 31
38909.5561 | 2038 | 1 | 31
38909.5568 | 2108 | 1 | 31
38909.5575 | 2163 | 545 | 31
38909.5582 | 1138 | 1013 | 31
38909.5378 | 1 | 0 | 32
38909.5384 | 2 | 0 | 32
38909.5391 | 1 | 0 | 32
38909.5398 | 1 | 0 | 32
38909.5405 | 1 | 0 | 32
38909.5412 | 1 | 0 | 32
38909.5418 | 1 | 0 | 32
38909.5425 | 2 | 0 | 32
38909.5432 | 2 | 0 | 32
38909.5439 | 1 | 0 | 32
38909.5446 | 2 | 0 | 32
38909.5452 | 1 | 0 | 32
38909.5459 | 1 | 0 | 32
38909.5466 | 1 | 0 | 32
38909.5473 | 1 | 0 | 32
38909.548 | 967 | 933 | 32
38909.5486 | 1200 | 1054 | 32
38909.5493 | 1159 | 1133 | 32
38909.55 | 1018 | 1060 | 32
38909.5507 | 1191 | 1199 | 32
38909.5514 | 996 | 964 | 32
38909.552 | 1201 | 1179 | 32
38909.5527 | 2522 | 2 | 32
38909.5534 | 2235 | 0 | 32
38909.5541 | 2021 | 0 | 32
38909.5548 | 2303 | 0 | 32
38909.5555 | 2005 | 0 | 32
38909.5561 | 2381 | 0 | 32
38909.5568 | 2334 | 1 | 32
38909.5575 | 1966 | 642 | 32
38909.5582 | 1092 | 1024 | 32
38909.5378 | 1 | 0 | 33
38909.5385 | 1 | 0 | 33
38909.5391 | 1 | 0 | 33
38909.5398 | 1 | 0 | 33
38909.5405 | 2 | 0 | 33
38909.5412 | 1 | 0 | 33
38909.5419 | 1 | 0 | 33
38909.5425 | 1 | 0 | 33
38909.5432 | 1 | 0 | 33
38909.5439 | 1 | 0 | 33
38909.5446 | 1 | 0 | 33
38909.5453 | 1 | 0 | 33
38909.5459 | 1 | 0 | 33
38909.5466 | 1 | 0 | 33
38909.5473 | 1 | 0 | 33
38909.548 | 2 | 7 | 33
38909.5487 | 2 | 8 | 33
38909.5493 | 2 | 9 | 33
38909.55 | 2 | 9 | 33
38909.5507 | 59 | 69 | 33
38909.5514 | 950 | 948 | 33
38909.5521 | 1197 | 1173 | 33
38909.5527 | 2529 | 2 | 33
38909.5534 | 2398 | 1 | 33
38909.5541 | 2074 | 0 | 33
38909.5548 | 1989 | 1 | 33
38909.5555 | 2317 | 1 | 33
38909.5561 | 2374 | 0 | 33
38909.5568 | 2376 | 1 | 33
38909.5575 | 2061 | 2 | 33
38909.5582 | 1673 | 7 | 33
38909.5378 | 1 | 0 | 34
38909.5385 | 1 | 0 | 34
38909.5392 | 1 | 0 | 34
38909.5398 | 1 | 0 | 34
38909.5405 | 1 | 0 | 34
38909.5412 | 1 | 0 | 34
38909.5419 | 1 | 0 | 34
38909.5426 | 1 | 0 | 34
38909.5432 | 1 | 0 | 34
38909.5439 | 1 | 0 | 34
38909.5446 | 1 | 0 | 34
38909.5453 | 1 | 0 | 34
38909.546 | 1 | 0 | 34
38909.5466 | 1 | 0 | 34
38909.5473 | 1 | 0 | 34
38909.548 | 2 | 5 | 34
38909.5487 | 1 | 4 | 34
38909.5494 | 1 | 5 | 34
38909.55 | 2 | 5 | 34
38909.5507 | 1037 | 1005 | 34
38909.5514 | 1093 | 1062 | 34
38909.5521 | 1202 | 1181 | 34
38909.5528 | 1957 | 1 | 34
38909.5534 | 2529 | 1 | 34
38909.5541 | 1981 | 0 | 34
38909.5548 | 2030 | 0 | 34
38909.5555 | 2288 | 1 | 34
38909.5562 | 2 | 1 | 34
38909.5569 | 3 | 1 | 34
38909.5575 | 2110 | 1 | 34
38909.5582 | 2518 | 3 | 34
38909.5378 | 1 | 0 | 35
38909.5385 | 1 | 0 | 35
38909.5392 | 1 | 0 | 35
38909.5398 | 1 | 0 | 35
38909.5405 | 1 | 0 | 35
38909.5412 | 1 | 0 | 35
38909.5419 | 1 | 0 | 35
38909.5426 | 1 | 0 | 35
38909.5433 | 1 | 0 | 35
38909.5439 | 1 | 0 | 35
38909.5446 | 1 | 0 | 35
38909.5453 | 1 | 0 | 35
38909.546 | 1 | 0 | 35
38909.5467 | 1 | 0 | 35
38909.5473 | 1 | 0 | 35
38909.548 | 1 | 2 | 35
38909.5487 | 1 | 2 | 35
38909.5494 | 1 | 3 | 35
38909.5501 | 2 | 3 | 35
38909.5507 | 1200 | 1175 | 35
38909.5514 | 1203 | 1183 | 35
38909.5521 | 1000 | 969 | 35
38909.5528 | 2018 | 2 | 35
38909.5535 | 2222 | 0 | 35
38909.5541 | 2359 | 0 | 35
38909.5548 | 2536 | 1 | 35
38909.5555 | 1961 | 1 | 35
38909.5562 | 2004 | 1 | 35
38909.5569 | 1971 | 1 | 35
38909.5575 | 1730 | 1 | 35
38909.5582 | 1531 | 2 | 35
38909.5378 | 1 | 0 | 36
38909.5385 | 1 | 0 | 36
38909.5392 | 1 | 0 | 36
38909.5399 | 1 | 0 | 36
38909.5406 | 1 | 0 | 36
38909.5412 | 1 | 0 | 36
38909.5419 | 1 | 0 | 36
38909.5426 | 1 | 0 | 36
38909.5433 | 1 | 0 | 36
38909.5439 | 1 | 0 | 36
38909.5446 | 1 | 0 | 36
38909.5453 | 1 | 0 | 36
38909.546 | 1 | 0 | 36
38909.5467 | 1 | 0 | 36
38909.5473 | 1 | 0 | 36
38909.548 | 1 | 1 | 36
38909.5487 | 1 | 1 | 36
38909.5494 | 3 | 2 | 36
38909.5501 | 1 | 1 | 36
38909.5508 | 1206 | 1193 | 36
38909.5514 | 1075 | 932 | 36
38909.5521 | 1049 | 1018 | 36
38909.5528 | 2321 | 1 | 36
38909.5535 | 2299 | 0 | 36
38909.5542 | 2317 | 1 | 36
38909.5548 | 2344 | 1 | 36
38909.5555 | 136 | 0 | 36
38909.5562 | 2 | 0 | 36
38909.5569 | 1801 | 35 | 36
38909.5576 | 2295 | 1 | 36
38909.5582 | 2165 | 1 | 36
38909.5378 | 1 | 0 | 37
38909.5385 | 1 | 0 | 37
38909.5392 | 1 | 0 | 37
38909.5399 | 1 | 0 | 37
38909.5406 | 1 | 0 | 37
38909.5413 | 1 | 0 | 37
38909.5419 | 1 | 0 | 37
38909.5426 | 1 | 0 | 37
38909.5433 | 1 | 0 | 37
38909.544 | 1 | 0 | 37
38909.5447 | 1 | 0 | 37
38909.5453 | 1 | 0 | 37
38909.546 | 1 | 0 | 37
38909.5467 | 1 | 0 | 37
38909.5474 | 1 | 0 | 37
38909.5481 | 2 | 1 | 37
38909.5487 | 1 | 1 | 37
38909.5494 | 2 | 1 | 37
38909.5501 | 2 | 1 | 37
38909.5508 | 1144 | 1114 | 37
38909.5514 | 1108 | 1175 | 37
38909.5521 | 1101 | 1153 | 37
38909.5528 | 2451 | 1 | 37
38909.5535 | 2114 | 1 | 37
38909.5542 | 2475 | 1 | 37
38909.5548 | 2014 | 0 | 37
38909.5555 | 2177 | 0 | 37
38909.5562 | 2283 | 0 | 37
38909.5569 | 2181 | 1 | 37
38909.5576 | 2089 | 1 | 37
38909.5583 | 1548 | 2 | 37
38909.5379 | 1 | 0 | 38
38909.5385 | 1 | 0 | 38
38909.5392 | 1 | 0 | 38
38909.5399 | 1 | 0 | 38
38909.5406 | 1 | 0 | 38
38909.5413 | 1 | 0 | 38
38909.5419 | 1 | 0 | 38
38909.5426 | 1 | 0 | 38
38909.5433 | 1 | 0 | 38
38909.544 | 1 | 0 | 38
38909.5447 | 1 | 0 | 38
38909.5453 | 1 | 0 | 38
38909.546 | 1 | 0 | 38
38909.5467 | 1 | 0 | 38
38909.5474 | 1 | 0 | 38
38909.5481 | 1 | 1 | 38
38909.5488 | 2 | 1 | 38
38909.5494 | 2 | 1 | 38
38909.5501 | 1 | 1 | 38
38909.5508 | 961 | 929 | 38
38909.5515 | 1055 | 1025 | 38
38909.5522 | 1175 | 1149 | 38
38909.5528 | 2255 | 1 | 38
38909.5535 | 1983 | 21 | 38
38909.5542 | 2401 | 1 | 38
38909.5549 | 1999 | 0 | 38
38909.5556 | 4 | 1 | 38
38909.5562 | 3 | 1 | 38
38909.5569 | 2193 | 0 | 38
38909.5576 | 2543 | 1 | 38
38909.5583 | 2188 | 1 | 38
38909.5379 | 1 | 0 | 39
38909.5386 | 1 | 0 | 39
38909.5392 | 1 | 0 | 39
38909.5399 | 1 | 0 | 39
38909.5406 | 1 | 0 | 39
38909.5413 | 1 | 0 | 39
38909.542 | 1 | 0 | 39
38909.5426 | 1 | 0 | 39
38909.5433 | 1 | 0 | 39
38909.544 | 1 | 0 | 39
38909.5447 | 1 | 0 | 39
38909.5454 | 1 | 0 | 39
38909.546 | 1 | 0 | 39
38909.5467 | 1 | 0 | 39
38909.5474 | 1 | 0 | 39
38909.5481 | 1 | 0 | 39
38909.5488 | 1 | 1 | 39
38909.5494 | 1 | 1 | 39
38909.5501 | 1 | 1 | 39
38909.5508 | 957 | 927 | 39
38909.5515 | 1135 | 1105 | 39
38909.5522 | 1034 | 1004 | 39
38909.5528 | 2231 | 1 | 39
38909.5535 | 2295 | 1 | 39
38909.5542 | 2266 | 1 | 39
38909.5549 | 2297 | 1 | 39
38909.5556 | 2486 | 0 | 39
38909.5563 | 2451 | 1 | 39
38909.5569 | 1964 | 1 | 39
38909.5576 | 1746 | 0 | 39
38909.5583 | 1397 | 1 | 39
38909.5379 | 1 | 0 | 40
38909.5386 | 1 | 1 | 40
38909.5392 | 1 | 0 | 40
38909.5399 | 1 | 0 | 40
38909.5406 | 1 | 0 | 40
38909.5413 | 1 | 0 | 40
38909.542 | 1 | 0 | 40
38909.5427 | 1 | 0 | 40
38909.5433 | 1 | 0 | 40
38909.544 | 1 | 0 | 40
38909.5447 | 1 | 0 | 40
38909.5454 | 1 | 0 | 40
38909.5461 | 2 | 0 | 40
38909.5467 | 1 | 0 | 40
38909.5474 | 1 | 0 | 40
38909.5481 | 2 | 1 | 40
38909.5488 | 1 | 0 | 40
38909.5495 | 2 | 1 | 40
38909.5501 | 2 | 1 | 40
38909.5508 | 1161 | 1133 | 40
38909.5515 | 1159 | 1194 | 40
38909.5522 | 1011 | 982 | 40
38909.5529 | 2419 | 1 | 40
38909.5535 | 2313 | 1 | 40
38909.5542 | 2284 | 1 | 40
38909.5549 | 2245 | 1 | 40
38909.5556 | 60 | 0 | 40
38909.5563 | 3 | 0 | 40
38909.5569 | 1983 | 0 | 40
38909.5576 | 2013 | 0 | 40
38909.5583 | 2002 | 0 | 40
38909.5379 | 1 | 0 | 41
38909.5386 | 1 | 0 | 41
38909.5393 | 1 | 0 | 41
38909.54 | 1 | 0 | 41
38909.5406 | 1 | 0 | 41
38909.5413 | 1 | 0 | 41
38909.542 | 1 | 0 | 41
38909.5427 | 1 | 0 | 41
38909.5434 | 1 | 0 | 41
38909.544 | 1 | 0 | 41
38909.5447 | 1 | 0 | 41
38909.5454 | 1 | 0 | 41
38909.5461 | 1 | 0 | 41
38909.5467 | 1 | 0 | 41
38909.5474 | 1 | 0 | 41
38909.5481 | 984 | 954 | 41
38909.5488 | 927 | 957 | 41
38909.5495 | 1029 | 999 | 41
38909.5502 | 967 | 937 | 41
38909.5508 | 1103 | 1156 | 41
38909.5515 | 1181 | 1199 | 41
38909.5522 | 995 | 1034 | 41
38909.5529 | 2411 | 1 | 41
38909.5536 | 2007 | 1 | 41
38909.5542 | 2270 | 1 | 41
38909.5549 | 2535 | 0 | 41
38909.5556 | 1039 | 1080 | 41
38909.5563 | 1010 | 1051 | 41
38909.557 | 2251 | 0 | 41
38909.5576 | 2265 | 0 | 41
38909.5583 | 2442 | 1 | 41
38909.5379 | 1 | 0 | 42
38909.5386 | 1 | 0 | 42
38909.5393 | 2 | 0 | 42
38909.54 | 1 | 0 | 42
38909.5406 | 1 | 0 | 42
38909.5413 | 1 | 0 | 42
38909.542 | 1 | 0 | 42
38909.5427 | 2 | 0 | 42
38909.5434 | 1 | 0 | 42
38909.5441 | 1 | 0 | 42
38909.5447 | 1 | 0 | 42
38909.5454 | 1 | 0 | 42
38909.5461 | 1 | 0 | 42
38909.5468 | 1 | 0 | 42
38909.5475 | 1 | 0 | 42
38909.5481 | 1107 | 1161 | 42
38909.5488 | 982 | 1020 | 42
38909.5495 | 1143 | 922 | 42
38909.5502 | 988 | 958 | 42
38909.5509 | 1201 | 931 | 42
38909.5515 | 1062 | 1032 | 42
38909.5522 | 1082 | 1053 | 42
38909.5529 | 2270 | 1 | 42
38909.5536 | 2011 | 1 | 42
38909.5543 | 2177 | 1 | 42
38909.5549 | 1956 | 0 | 42
38909.5556 | 1068 | 1037 | 42
38909.5563 | 1206 | 1183 | 42
38909.557 | 2365 | 0 | 42
38909.5577 | 2206 | 0 | 42
38909.5583 | 2072 | 1 | 42