## Test Facts
Last row in IRMS data sheets: | 27
Time when Penlight power was initiated: | 89

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Test 18
Test conditions: Cable: 7-conductor, 12 AWG, Silicone rubber (SR) insulated, Aramid braid jacketed, control cable (Cable Item #9). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 700C, nominal 50.8 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: Shroud temperature and one cable temperature (see thermocouple map). One thermocouple was attached to the inside of the center tray rung. Shroud power: Initiated after 89 seconds of baseline data monitoring. Special Note: The cable tray was struck with a hammer several times after the flames had extinguished. Additionally, the cable was physically shaken using a pair of insulated pliers when the hammer blows caused no electrical failure response.
DAQ Time | Penlight Time | Event | Interpretation
89 | 0 | Initated Penlight Heating
~203 | 114 | Cables ignite and burn | No electrical failures detected
317 | 228 | Power to Penlight is shutoff
~600 | 511 | Flame extinguish; struck cable tray 3 times with hammer | No electrical failures detected
~780 | 691 | Struck cable tray 3 more times with hammer | No electrical failures detected
~960 | 871 | Physically shook test cable by hand with insulated pliers | No electrical failures detected
Additional Observations
Observation 1 | No electrical failures were detected during this test, despite the application of physical shock and rough handling.
Observation 2 | It took 114 s (1.9 min.) from the start of Penlight heating for the cables to ignite and burn.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable" | Within cable just below cable jacket, center position

## C-C Individuals
Conductor to Conductor Resistances
Test 18 |  |  | 2006-07-27 | 11:37
SR | 7-C | Tray
700 C | 50.8 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-88.5 | 211201.9994 | -85.5 | 211201.9994 | -83 | 211201.9994 | -80 | 211201.9994 | -77.5 | 211201.9994 | -74.5 | 211201.9994 | -71.5 | 211002.0947 | -69 | 211201.9994 | -66 | 211201.9994 | -63.5 | 211201.9994 | -60.5 | 211201.9994 | -57.5 | 211201.9994 | -55 | 211201.9994 | -52 | 211201.9994 | -49.5 | 211201.9994 | -46.5 | 211201.9994 | -43.5 | 211201.9994 | -41 | 211201.9994 | -38 | 211201.9994 | -35.5 | 211201.9994 | -32.5 | 211201.9994 | -88.5 | 211002.0947
-29.5 | 211201.9994 | -27 | 211201.9994 | -24 | 211201.9994 | -21.5 | 211201.9994 | -18.5 | 211201.9994 | -15.5 | 211201.9994 | -13 | 211201.9994 | -10 | 211201.9994 | -7.5 | 70333.9982 | -4.5 | 211201.9994 | -1.5 | 211201.9994 | 1 | 211201.9994 | 4 | 211201.9994 | 6.5 | 211201.9994 | 9.5 | 211201.9994 | 12.5 | 211201.9994 | 15 | 211201.9994 | 18 | 211201.9994 | 20.5 | 211201.9994 | 23.5 | 211201.9994 | 26.5 | 211201.9994 | -29.5 | 70333.9982
28 | 211201.9994 | 32 | 105550.9988 | 34.5 | 211201.9994 | 37.5 | 211201.9994 | 40.5 | 211201.9994 | 43 | 211201.9994 | 46 | 211201.9994 | 48.5 | 211201.9994 | 51.5 | 211201.9994 | 54.5 | 211201.9994 | 57 | 211201.9994 | 60 | 211201.9994 | 62.5 | 211201.9994 | 65.5 | 211201.9994 | 68.5 | 211201.9994 | 71 | 211201.9994 | 74 | 211201.9994 | 76.5 | 211201.9994 | 79.5 | 211201.9994 | 82.5 | 211201.9994 | 85 | 211201.9994 | 28 | 105550.9988
88 | 211201.9994 | 90.5 | 211201.9994 | 93.5 | 211201.9994 | 96.5 | 211201.9994 | 99 | 211201.9994 | 102 | 211201.9994 | 104.5 | 211201.9994 | 107.5 | 211201.9994 | 110.5 | 211201.9994 | 113 | 211201.9994 | 116 | 211201.9994 | 118.5 | 211201.9994 | 121.5 | 211201.9994 | 124.5 | 211201.9994 | 127 | 211201.9994 | 130 | 211201.9994 | 132.5 | 211201.9994 | 135.5 | 211201.9994 | 138.5 | 211201.9994 | 141 | 211201.9994 | 144 | 211201.9994 | 88 | 211201.9994
146.5 | 211201.9994 | 149.5 | 211201.9994 | 152.5 | 211201.9994 | 155 | 211201.9994 | 158 | 211201.9994 | 160.5 | 211201.9994 | 163.5 | 211201.9994 | 166.5 | 211201.9994 | 169 | 211201.9994 | 172 | 211201.9994 | 174.5 | 211201.9994 | 177.5 | 211201.9994 | 180.5 | 211201.9994 | 183 | 211201.9994 | 186 | 211201.9994 | 188.5 | 211201.9994 | 191.5 | 211201.9994 | 194.5 | 211201.9994 | 197 | 211201.9994 | 200 | 211201.9994 | 202.5 | 211201.9994 | 146.5 | 211201.9994
205.5 | 211201.9994 | 208.5 | 211201.9994 | 211 | 211201.9994 | 214 | 211201.9994 | 216.5 | 211201.9994 | 219.5 | 211201.9994 | 222.5 | 211201.9994 | 225 | 211201.9994 | 228 | 211201.9994 | 230.5 | 211201.9994 | 233.5 | 211201.9994 | 236.5 | 211201.9994 | 239 | 211201.9994 | 242 | 211201.9994 | 244.5 | 211201.9994 | 247.5 | 211201.9994 | 250.5 | 211201.9994 | 253 | 211201.9994 | 256 | 211201.9994 | 258.5 | 211201.9994 | 261.5 | 211201.9994 | 205.5 | 211201.9994
264.5 | 211201.9994 | 267 | 211201.9994 | 270 | 211201.9994 | 272.5 | 211002.0947 | 275.5 | 211201.9994 | 278.5 | 211201.9994 | 281 | 211201.9994 | 284 | 211201.9994 | 286.5 | 211201.9994 | 289.5 | 211201.9994 | 292.5 | 211201.9994 | 295 | 211201.9994 | 298 | 211201.9994 | 300.5 | 211201.9994 | 303.5 | 211201.9994 | 306.5 | 211201.9994 | 309 | 211201.9994 | 312 | 211201.9994 | 314.5 | 211201.9994 | 317.5 | 211201.9994 | 320.5 | 211201.9994 | 264.5 | 211002.0947
323 | 211201.9994 | 326 | 211201.9994 | 328.5 | 211201.9994 | 331.5 | 211201.9994 | 334.5 | 211201.9994 | 337 | 211201.9994 | 340 | 211201.9994 | 342.5 | 211201.9994 | 345.5 | 211201.9994 | 348.5 | 211201.9994 | 351 | 211201.9994 | 354 | 211201.9994 | 356.5 | 211201.9994 | 359.5 | 211201.9994 | 362.5 | 211201.9994 | 365 | 211201.9994 | 368 | 211201.9994 | 370.5 | 211201.9994 | 373.5 | 211201.9994 | 376.5 | 211201.9994 | 379 | 211201.9994 | 323 | 211201.9994
382 | 211201.9994 | 384.5 | 211201.9994 | 387.5 | 211201.9994 | 390.5 | 211201.9994 | 393 | 211201.9994 | 395.5 | 211201.9994 | 398.5 | 211002.0947 | 401.5 | 211201.9994 | 404.5 | 211201.9994 | 407 | 211201.9994 | 410 | 211201.9994 | 412.5 | 211201.9994 | 415.5 | 211201.9994 | 418.5 | 211201.9994 | 421 | 211201.9994 | 424 | 211201.9994 | 426.5 | 211201.9994 | 429.5 | 211201.9994 | 432.5 | 211201.9994 | 435 | 211201.9994 | 438 | 211201.9994 | 382 | 211002.0947
440.5 | 211201.9994 | 443.5 | 211201.9994 | 446 | 211201.9994 | 448 | 211201.9994 | 451.5 | 211201.9994 | 454.5 | 211201.9994 | 457.5 | 211201.9994 | 460 | 211201.9994 | 463 | 211201.9994 | 466 | 211201.9994 | 468.5 | 211201.9994 | 471.5 | 211201.9994 | 474 | 211201.9994 | 477 | 211201.9994 | 479.5 | 211201.9994 | 482.5 | 211201.9994 | 485.5 | 211201.9994 | 488.5 | 211201.9994 | 491 | 211201.9994 | 494 | 211201.9994 | 496.5 | 211201.9994 | 440.5 | 211201.9994
499.5 | 211201.9994 | 502.5 | 211201.9994 | 505 | 211201.9994 | 507.5 | 211201.9994 | 510.5 | 211201.9994 | 513.5 | 211201.9994 | 516.5 | 211201.9994 | 519 | 211201.9994 | 521.5 | 211201.9994 | 524.5 | 211201.9994 | 527.5 | 211201.9994 | 530 | 211201.9994 | 533 | 211201.9994 | 536 | 211002.0947 | 538.5 | 211201.9994 | 541.5 | 211201.9994 | 544.5 | 211201.9994 | 547 | 211201.9994 | 550 | 211201.9994 | 552.5 | 211201.9994 | 555.5 | 211201.9994 | 499.5 | 211002.0947
558.5 | 211201.9994 | 561 | 211201.9994 | 564 | 211201.9994 | 566.5 | 211201.9994 | 569.5 | 211201.9994 | 572 | 211201.9994 | 575 | 211201.9994 | 578 | 211201.9994 | 580.5 | 211201.9994 | 583.5 | 211201.9994 | 586.5 | 211201.9994 | 589 | 211201.9994 | 592 | 211201.9994 | 594.5 | 211201.9994 | 597.5 | 211201.9994 | 600.5 | 211201.9994 | 603 | 211201.9994 | 606 | 211201.9994 | 608.5 | 211201.9994 | 611.5 | 211201.9994 | 614.5 | 211201.9994 | 558.5 | 211201.9994
617 | 211201.9994 | 620 | 211201.9994 | 622.5 | 211201.9994 | 625.5 | 211201.9994 | 628.5 | 211201.9994 | 631 | 211201.9994 | 634 | 211201.9994 | 636.5 | 211201.9994 | 639.5 | 211201.9994 | 642.5 | 211201.9994 | 645 | 211201.9994 | 648 | 211201.9994 | 650.5 | 211201.9994 | 653.5 | 211201.9994 | 656.5 | 211201.9994 | 659 | 211201.9994 | 662 | 211201.9994 | 664.5 | 211201.9994 | 667.5 | 211201.9994 | 670.5 | 211201.9994 | 673 | 211201.9994 | 617 | 211201.9994
675.5 | 211201.9994 | 678.5 | 211201.9994 | 681.5 | 211201.9994 | 684 | 211201.9994 | 687 | 211201.9994 | 690 | 211201.9994 | 692.5 | 211201.9994 | 695.5 | 211201.9994 | 698 | 211201.9994 | 701 | 211201.9994 | 703.5 | 211201.9994 | 706.5 | 211201.9994 | 709.5 | 211201.9994 | 712.5 | 211201.9994 | 715 | 211201.9994 | 718 | 211201.9994 | 720.5 | 211201.9994 | 723.5 | 105550.9988 | 726 | 211201.9994 | 729 | 211201.9994 | 731.5 | 211201.9994 | 675.5 | 105550.9988
734.5 | 211201.9994 | 737.5 | 211201.9994 | 740.5 | 211201.9994 | 743 | 211201.9994 | 746 | 211201.9994 | 748.5 | 211201.9994 | 751.5 | 211201.9994 | 754.5 | 211201.9994 | 757 | 211201.9994 | 760 | 211201.9994 | 762.5 | 211201.9994 | 765.5 | 211201.9994 | 768.5 | 211201.9994 | 771 | 211201.9994 | 773.5 | 211201.9994 | 776.5 | 211201.9994 | 779.5 | 211201.9994 | 782.5 | 211201.9994 | 785 | 211201.9994 | 788 | 211201.9994 | 790.5 | 211201.9994 | 734.5 | 211201.9994
793.5 | 211201.9994 | 796.5 | 211201.9994 | 799 | 211201.9994 | 801.5 | 211201.9994 | 804.5 | 211201.9994 | 807.5 | 211201.9994 | 810.5 | 211201.9994 | 813 | 211201.9994 | 815.5 | 211201.9994 | 818.5 | 211201.9994 | 821.5 | 211201.9994 | 824.5 | 211201.9994 | 827 | 211201.9994 | 830 | 211201.9994 | 832.5 | 211201.9994 | 835.5 | 211201.9994 | 838.5 | 211201.9994 | 841 | 211201.9994 | 843.5 | 211201.9994 | 846.5 | 211201.9994 | 849.5 | 211201.9994 | 793.5 | 211201.9994
852 | 211201.9994 | 855 | 211201.9994 | 857.5 | 211201.9994 | 860.5 | 211201.9994 | 863.5 | 211201.9994 | 866.5 | 211201.9994 | 869 | 211201.9994 | 871.5 | 211201.9994 | 874.5 | 211201.9994 | 877.5 | 211201.9994 | 880 | 211201.9994 | 883 | 211201.9994 | 885.5 | 211201.9994 | 888.5 | 211201.9994 | 891.5 | 211201.9994 | 894 | 211201.9994 | 897 | 211201.9994 | 900 | 211201.9994 | 902.5 | 211201.9994 | 905.5 | 211201.9994 | 908.5 | 211201.9994 | 852 | 211201.9994
911 | 211201.9994 | 914 | 211201.9994 | 916.5 | 211201.9994 | 919.5 | 211201.9994 | 922 | 211201.9994 | 925 | 211201.9994 | 927.5 | 211201.9994 | 931 | 211201.9994 | 933.5 | 211201.9994 | 936 | 211201.9994 | 939 | 211201.9994 | 942 | 211201.9994 | 944.5 | 211201.9994 | 947.5 | 211201.9994 | 950 | 211201.9994 | 953 | 211201.9994 | 955.5 | 211201.9994 | 958.5 | 211201.9994 | 961.5 | 211201.9994 | 964 | 211201.9994 | 967 | 211201.9994 | 911 | 211201.9994
969.5 | 211201.9994 | 972.5 | 211201.9994 | 975.5 | 211201.9994 | 978.5 | 211201.9994 | 981 | 211201.9994 | 983.5 | 211201.9994 | 986.5 | 211201.9994 | 989.5 | 211201.9994 | 992 | 211201.9994 | 995 | 211201.9994 | 997.5 | 211201.9994 | 1000.5 | 211201.9994 | 1003.5 | 211201.9994 | 1006 | 211201.9994 | 1009 | 211201.9994 | 1011.5 | 211201.9994 | 1014.5 | 211201.9994 | 1017.5 | 211201.9994 | 1020 | 211201.9994 | 1023 | 211201.9994 | 1025.5 | 211201.9994 | 969.5 | 211201.9994
1028.5 | 211201.9994 | 1031.5 | 211201.9994 | 1034 | 211201.9994 | 1037 | 211201.9994 | 1039.5 | 211201.9994 | 1042.5 | 211201.9994 | 1045.5 | 211201.9994 | 1048 | 211201.9994 | 1051 | 211201.9994 | 1053.5 | 211201.9994 | 1056.5 | 211201.9994 | 1059.5 | 211201.9994 | 1062 | 211201.9994 | 1065 | 211201.9994 | 1067.5 | 211201.9994 | 1070.5 | 211201.9994 | 1073.5 | 211201.9994 | 1076 | 211201.9994 | 1079 | 211201.9994 | 1081.5 | 211201.9994 | 1084.5 | 211201.9994 | 1028.5 | 211201.9994
1087.5 | 211201.9994 | 1090 | 211201.9994 | 1093 | 211201.9994 | 1095.5 | 211201.9994 | 1098.5 | 211201.9994 | 1101.5 | 211201.9994 | 1104 | 211201.9994 | 1107 | 211201.9994 | 1109.5 | 211201.9994 | 1112.5 | 211201.9994 | 1115.5 | 211201.9994 | 1118 | 211201.9994 | 1121 | 211201.9994 | 1123.5 | 211201.9994 | 1126.5 | 211201.9994 | 1129.5 | 211201.9994 | 1132 | 211201.9994 | 1135 | 211201.9994 | 1137.5 | 211201.9994 | 1140.5 | 211201.9994 | 1143.5 | 211201.9994 | 1087.5 | 211201.9994
1146 | 211201.9994 | 1149 | 211201.9994 | 1151.5 | 211201.9994 | 1154.5 | 211201.9994 | 1157.5 | 211201.9994 | 1160 | 211201.9994 | 1163 | 211201.9994 | 1165.5 | 211201.9994 | 1168.5 | 211201.9994 | 1171.5 | 211201.9994 | 1174 | 211201.9994 | 1177 | 211201.9994 | 1179.5 | 211201.9994 | 1182.5 | 211201.9994 | 1185.5 | 211201.9994 | 1188 | 211201.9994 | 1191 | 211201.9994 | 1193.5 | 211201.9994 | 1196.5 | 211201.9994 | 1199.5 | 211201.9994 | 1202 | 211201.9994 | 1146 | 211201.9994

## C-G Min
Average Conductor to Ground Resistances
Test 18 |  |  | 2006-07-27 | 11:37
SR | 7-C | Tray
700 C | 50.8 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-81.5 | 211202 |  | -69.8333 | 211202 | -61.8333 | 211202 | -56.75 | 211202 | -53.5 | 211202 | -51.1667 | 211202 | -48.9167 | 211202 | -81.5 | 211202
-22.6667 | 211202 |  | -11 | 70334 | -3.1667 | 211202 | 2.0833 | 211202 | 5.25 | 211202 | 7.5833 | 211202 | 10.0833 | 211202 | -22.6667 | 70334
35.9167 | 105551 |  | 47.5833 | 211202 | 55.75 | 211202 | 60.75 | 211202 | 64.0833 | 211202 | 66.5 | 211202 | 68.75 | 211202 | 35.9167 | 105551
94.9167 | 211202 |  | 106.5833 | 211202 | 114.4167 | 211202 | 119.5833 | 211202 | 123 | 211202 | 125.25 | 211202 | 127.5833 | 211202 | 94.9167 | 211202
153.6667 | 211202 |  | 165.3333 | 211202 | 173.3333 | 211202 | 178.5 | 211202 | 181.6667 | 211202 | 184 | 211202 | 186.3333 | 211202 | 153.6667 | 211202
212.5 | 211202 |  | 224.1667 | 211202 | 232.1667 | 211202 | 237.25 | 211202 | 240.5 | 211202 | 242.8333 | 211202 | 245.0833 | 211202 | 212.5 | 211202
271.3333 | 211202 |  | 283 | 211202 | 290.8333 | 211202 | 296.0833 | 211202 | 299.25 | 211202 | 301.5833 | 211202 | 304.0833 | 211202 | 271.3333 | 211202
330.0833 | 211202 |  | 341.75 | 211202 | 349.75 | 211202 | 354.75 | 211202 | 358.0833 | 211202 | 360.5 | 211202 | 362.75 | 211202 | 330.0833 | 211202
388.8333 | 211202 |  | 400.5833 | 211202 | 408.4167 | 211202 | 413.5833 | 211202 | 417 | 211202 | 419.25 | 211202 | 421.5 | 211202 | 388.8333 | 211202
447.3333 | 211202 |  | 459.25 | 211202 | 467.1667 | 211202 | 472.3333 | 211202 | 475.4167 | 211202 | 477.9167 | 211202 | 480.25 | 105551 | 447.3333 | 105551
506.4167 | 211202 |  | 518.0833 | 211202 | 526.0833 | 211202 | 531.1667 | 211202 | 534.3333 | 211202 | 536.8333 | 211202 | 539.0833 | 211202 | 506.4167 | 211202
565.25 | 211202 |  | 577 | 211202 | 584.8333 | 211202 | 590.0833 | 211202 | 593.25 | 211202 | 595.5833 | 211202 | 598 | 211202 | 565.25 | 211202
624.0833 | 211202 |  | 635.75 | 211202 | 643.75 | 211202 | 648.75 | 211202 | 652.0833 | 211202 | 654.5 | 211202 | 656.75 | 211202 | 624.0833 | 211202
682.75 | 211202 |  | 694.3333 | 211202 | 702.4167 | 211202 | 707.5833 | 105551 | 710.75 | 211202 | 713.0833 | 211202 | 715.4167 | 211202 | 682.75 | 105551
741.6667 | 211202 |  | 753.3333 | 211202 | 761.25 | 211202 | 766.5 | 211202 | 769.6667 | 211202 | 772 | 211202 | 774.25 | 211202 | 741.6667 | 211202
800.4167 | 211202 |  | 812.0833 | 211202 | 820.1667 | 211202 | 825.25 | 211202 | 828.25 | 211202 | 830.75 | 211202 | 833.0833 | 211202 | 800.4167 | 211202
859.1667 | 211202 |  | 870.75 | 211202 | 878.75 | 211202 | 883.8333 | 211202 | 887.0833 | 211202 | 889.5833 | 211202 | 892 | 211202 | 859.1667 | 211202
918 | 211202 |  | 929.6667 | 211202 | 937.5833 | 211202 | 942.75 | 211202 | 946 | 211202 | 948.25 | 211202 | 950.5833 | 211202 | 918 | 211202
976.75 | 211202 |  | 988.3333 | 211202 | 996.3333 | 211202 | 1001.5 | 211202 | 1004.75 | 211202 | 1007 | 211202 | 1009.3333 | 211202 | 976.75 | 211202
1035.5 | 211202 |  | 1047.1667 | 211202 | 1055.1667 | 211202 | 1060.25 | 211202 | 1063.5 | 211202 | 1065.8333 | 211202 | 1068.0833 | 211202 | 1035.5 | 211202
1094.3333 | 211202 |  | 1106 | 211202 | 1113.8333 | 211202 | 1119.0833 | 211202 | 1122.25 | 211202 | 1124.5833 | 211202 | 1127.0833 | 211202 | 1094.3333 | 211202
1153.0833 | 211202 |  | 1164.75 | 211202 | 1172.75 | 211202 | 1177.75 | 211202 | 1181.0833 | 211202 | 1183.5 | 211202 | 1185.75 | 211202 | 1153.0833 | 211202

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable | Tray Rung
0 | -89 | 19.2 | 26.5 | 21.6
1 | -88 | 19.1 | 26.5 | 21.6
2 | -87 | 19.2 | 26.5 | 21.6
3 | -86 | 19.2 | 26.5 | 21.6
4 | -85 | 19.2 | 26.5 | 21.6
5 | -84 | 19.2 | 26.5 | 21.6
6 | -83 | 19.2 | 26.5 | 21.6
7 | -82 | 19.1 | 26.5 | 21.6
8 | -81 | 19.2 | 26.5 | 21.6
9 | -80 | 19.1 | 26.5 | 21.6
10 | -79 | 19.2 | 26.5 | 21.6
11 | -78 | 19.2 | 26.5 | 21.6
12 | -77 | 19.2 | 26.5 | 21.6
13 | -76 | 19.2 | 26.5 | 21.6
14 | -75 | 19.2 | 26.5 | 21.6
15 | -74 | 19.2 | 26.5 | 21.6
16 | -73 | 19.2 | 26.5 | 21.6
17 | -72 | 19.2 | 26.5 | 21.6
18 | -71 | 19.2 | 26.5 | 21.6
19 | -70 | 19.2 | 26.5 | 21.6
20 | -69 | 19.2 | 26.5 | 21.6
21 | -68 | 19.2 | 26.5 | 21.6
22 | -67 | 19.1 | 26.5 | 21.6
23 | -66 | 19.1 | 26.5 | 21.6
24 | -65 | 19.2 | 26.5 | 21.6
25 | -64 | 19.2 | 26.5 | 21.6
26 | -63 | 19.2 | 26.5 | 21.6
27 | -62 | 19.2 | 26.5 | 21.6
28 | -61 | 19.2 | 26.5 | 21.6
29 | -60 | 19.2 | 26.5 | 21.6
30 | -59 | 19.2 | 26.5 | 21.6
31 | -58 | 19.2 | 26.5 | 21.6
32 | -57 | 19.2 | 26.5 | 21.6
33 | -56 | 19.2 | 26.5 | 21.6
34 | -55 | 19.2 | 26.5 | 21.6
35 | -54 | 19.2 | 26.5 | 21.6
36 | -53 | 19.2 | 26.5 | 21.6
37 | -52 | 19.2 | 26.5 | 21.6
38 | -51 | 19.2 | 26.5 | 21.6
39 | -50 | 19.2 | 26.5 | 21.6
40 | -49 | 19.2 | 26.5 | 21.6
41 | -48 | 19.2 | 26.5 | 21.6
42 | -47 | 19.2 | 26.5 | 21.6
43 | -46 | 19.2 | 26.5 | 21.6
44 | -45 | 19.2 | 26.5 | 21.6
45 | -44 | 19.2 | 26.5 | 21.6
46 | -43 | 19.2 | 26.5 | 21.6
47 | -42 | 19.2 | 26.5 | 21.6
48 | -41 | 19.2 | 26.5 | 21.6
49 | -40 | 19.2 | 26.5 | 21.6
50 | -39 | 19.2 | 26.5 | 21.6
51 | -38 | 19.1 | 26.5 | 21.6
52 | -37 | 19.2 | 26.5 | 21.6
53 | -36 | 19.2 | 26.5 | 21.6
54 | -35 | 19.2 | 26.5 | 21.6
55 | -34 | 19.1 | 26.5 | 21.6
56 | -33 | 19.2 | 26.5 | 21.6
57 | -32 | 19.2 | 26.5 | 21.6
58 | -31 | 19.2 | 26.5 | 21.6
59 | -30 | 19.2 | 26.5 | 21.6
60 | -29 | 19.1 | 26.5 | 21.6
61 | -28 | 19.2 | 26.5 | 21.6
62 | -27 | 19.2 | 26.5 | 21.6
63 | -26 | 19.2 | 26.5 | 21.6
64 | -25 | 19.2 | 26.5 | 21.6
65 | -24 | 19.2 | 26.5 | 21.6
66 | -23 | 19.2 | 26.5 | 21.6
67 | -22 | 19.2 | 26.5 | 21.6
68 | -21 | 19.2 | 26.5 | 21.6
69 | -20 | 19.2 | 26.5 | 21.6
70 | -19 | 19.2 | 26.5 | 21.6
71 | -18 | 19.2 | 26.5 | 21.6
72 | -17 | 19.2 | 26.5 | 21.6
73 | -16 | 19.1 | 26.5 | 21.6
74 | -15 | 19.2 | 26.5 | 21.6
75 | -14 | 19.2 | 26.5 | 21.6
76 | -13 | 19.2 | 26.5 | 21.6
77 | -12 | 19.2 | 26.5 | 21.6
78 | -11 | 19.2 | 26.5 | 21.6
79 | -10 | 19.2 | 26.5 | 21.6
80 | -9 | 19.2 | 26.5 | 21.6
81 | -8 | 19.2 | 26.5 | 21.6
82 | -7 | 19.2 | 26.5 | 21.6
83 | -6 | 19.2 | 26.5 | 21.6
84 | -5 | 19.1 | 26.5 | 21.6
85 | -4 | 19.2 | 26.5 | 21.4
86 | -3 | 19.1 | 27.2 | 20.1
87 | -2 | 19.2 | 27.5 | 19.7
88 | -1 | 19.4 | 27.5 | 19.7
89 | 0 | 20.3 | 27.5 | 19.7
90 | 1 | 22 | 27.5 | 19.8
91 | 2 | 24.2 | 27.6 | 19.6
92 | 3 | 27 | 28.1 | 18.8
93 | 4 | 30.1 | 28.1 | 18.8
94 | 5 | 33.6 | 28.1 | 18.8
95 | 6 | 37.4 | 28.1 | 18.8
96 | 7 | 41.4 | 28.2 | 18.9
97 | 8 | 45.7 | 28.2 | 19
98 | 9 | 50.1 | 28.2 | 19
99 | 10 | 54.7 | 28.3 | 19.1
100 | 11 | 59.4 | 28.4 | 19.1
101 | 12 | 64.2 | 28.4 | 19.2
102 | 13 | 69.2 | 28.5 | 19.3
103 | 14 | 74.2 | 28.6 | 19.4
104 | 15 | 79.4 | 28.8 | 19.5
105 | 16 | 84.7 | 28.9 | 19.6
106 | 17 | 90.1 | 29 | 19.7
107 | 18 | 95.4 | 29.2 | 19.8
108 | 19 | 100.9 | 29.4 | 20
109 | 20 | 106.4 | 29.6 | 20.2
110 | 21 | 111.9 | 29.8 | 20.3
111 | 22 | 117.5 | 30 | 20.5
112 | 23 | 123.2 | 30.2 | 20.8
113 | 24 | 128.9 | 30.4 | 21
114 | 25 | 134.6 | 30.7 | 21.2
115 | 26 | 140.3 | 31 | 21.5
116 | 27 | 145.9 | 31.3 | 21.7
117 | 28 | 151.4 | 31.6 | 22
118 | 29 | 157.1 | 31.9 | 22.3
119 | 30 | 162.8 | 32.3 | 22.6
120 | 31 | 168.4 | 32.6 | 23
121 | 32 | 174.2 | 33 | 23.3
122 | 33 | 180 | 33.4 | 23.7
123 | 34 | 185.6 | 33.9 | 24.1
124 | 35 | 191.2 | 34.3 | 24.5
125 | 36 | 196.9 | 34.7 | 24.9
126 | 37 | 202.8 | 35.2 | 25.4
127 | 38 | 208.5 | 35.7 | 25.9
128 | 39 | 214.2 | 36.2 | 26.4
129 | 40 | 219.9 | 36.8 | 26.9
130 | 41 | 225.6 | 37.3 | 27.5
131 | 42 | 231.2 | 37.9 | 28
132 | 43 | 237 | 38.5 | 28.6
133 | 44 | 242.7 | 39.2 | 29.2
134 | 45 | 248.4 | 39.8 | 29.9
135 | 46 | 254 | 40.5 | 30.6
136 | 47 | 259.6 | 41.2 | 31.3
137 | 48 | 265.1 | 41.9 | 32
138 | 49 | 270.7 | 42.6 | 32.7
139 | 50 | 276.3 | 43.4 | 33.5
140 | 51 | 281.8 | 44.2 | 34.4
141 | 52 | 287.4 | 45 | 35.2
142 | 53 | 292.8 | 45.9 | 36.1
143 | 54 | 298.2 | 46.7 | 37.1
144 | 55 | 303.8 | 47.6 | 37.9
145 | 56 | 309.4 | 48.5 | 38.8
146 | 57 | 314.9 | 49.4 | 39.8
147 | 58 | 320.4 | 50.4 | 40.9
148 | 59 | 325.8 | 51.4 | 42
149 | 60 | 331.1 | 52.4 | 43.2
150 | 61 | 336.3 | 53.5 | 44.2
151 | 62 | 341.6 | 54.5 | 45.4
152 | 63 | 346.7 | 55.6 | 46.5
153 | 64 | 351.9 | 56.7 | 47.8
154 | 65 | 357.1 | 57.9 | 49
155 | 66 | 362.3 | 59 | 50.4
156 | 67 | 367.3 | 60.2 | 51.7
157 | 68 | 372.3 | 61.4 | 53
158 | 69 | 377.3 | 62.7 | 54.4
159 | 70 | 382.3 | 63.9 | 55.9
160 | 71 | 387.3 | 65.2 | 57.5
161 | 72 | 392.2 | 66.5 | 58.9
162 | 73 | 397.1 | 67.9 | 60.5
163 | 74 | 402 | 69.2 | 62.1
164 | 75 | 407 | 70.6 | 63.7
165 | 76 | 411.6 | 72.1 | 65.4
166 | 77 | 416.3 | 73.6 | 67.1
167 | 78 | 421.1 | 75.1 | 68.9
168 | 79 | 425.9 | 76.7 | 70.8
169 | 80 | 430.7 | 78.3 | 72.7
170 | 81 | 435.2 | 79.9 | 74.5
171 | 82 | 439.6 | 81.6 | 76.3
172 | 83 | 444.1 | 83.3 | 78.3
173 | 84 | 448.6 | 85.1 | 80.4
174 | 85 | 453.1 | 86.9 | 82.4
175 | 86 | 457.6 | 88.8 | 84.5
176 | 87 | 461.9 | 90.7 | 86.7
177 | 88 | 466 | 92.7 | 88.8
178 | 89 | 470 | 94.8 | 91
179 | 90 | 474.1 | 96.9 | 93.2
180 | 91 | 478.5 | 99 | 95.5
181 | 92 | 482.6 | 101.1 | 97.9
182 | 93 | 486.8 | 103.3 | 100.2
183 | 94 | 491 | 105.6 | 102.7
184 | 95 | 495.1 | 107.9 | 105.2
185 | 96 | 499.1 | 110.3 | 107.7
186 | 97 | 503 | 112.7 | 110.2
187 | 98 | 506.9 | 115.2 | 112.8
188 | 99 | 510.7 | 117.7 | 115.4
189 | 100 | 514.7 | 120.2 | 118.1
190 | 101 | 518.6 | 122.9 | 120.8
191 | 102 | 522.2 | 125.5 | 123.5
192 | 103 | 526.1 | 128.2 | 126.4
193 | 104 | 529.7 | 130.9 | 129.2
194 | 105 | 533.1 | 133.7 | 132
195 | 106 | 536.5 | 136.5 | 134.9
196 | 107 | 540 | 139.3 | 137.8
197 | 108 | 543.5 | 142.2 | 140.7
198 | 109 | 547 | 145.2 | 143.6
199 | 110 | 550.4 | 148.2 | 146.5
200 | 111 | 553.4 | 151.2 | 149.6
201 | 112 | 556.4 | 154.1 | 152.7
202 | 113 | 559.5 | 157.2 | 155.8
203 | 114 | 562.6 | 160.3 | 159
204 | 115 | 565.9 | 163.3 | 162.2
205 | 116 | 569.2 | 166.5 | 165.4
206 | 117 | 572.3 | 169.4 | 169.2
207 | 118 | 575.3 | 172.2 | 173.2
208 | 119 | 578.1 | 175.4 | 176.6
209 | 120 | 581 | 178.6 | 180
210 | 121 | 583.8 | 181.9 | 183.4
211 | 122 | 586.8 | 185.2 | 186.9
212 | 123 | 589.7 | 189.1 | 190.7
213 | 124 | 592.7 | 194.4 | 194.9
214 | 125 | 595.7 | 200.7 | 199.6
215 | 126 | 598.7 | 207.4 | 204.6
216 | 127 | 601.6 | 214.3 | 209.9
217 | 128 | 604.7 | 221.1 | 215.4
218 | 129 | 607.7 | 227.9 | 221
219 | 130 | 610.8 | 235.1 | 226.7
220 | 131 | 613.9 | 242.5 | 232.3
221 | 132 | 616.8 | 249.9 | 238.1
222 | 133 | 619.6 | 257 | 243.9
223 | 134 | 622.2 | 263.7 | 249.7
224 | 135 | 625 | 270 | 255.3
225 | 136 | 627.5 | 276.1 | 260.9
226 | 137 | 629.9 | 282.1 | 266.4
227 | 138 | 632.5 | 288 | 271.7
228 | 139 | 634.9 | 294 | 277.1
229 | 140 | 637.3 | 299.7 | 282.5
230 | 141 | 639.9 | 305.4 | 287.8
231 | 142 | 642.3 | 311.3 | 293
232 | 143 | 644.7 | 317.7 | 298.1
233 | 144 | 647.1 | 324.3 | 303
234 | 145 | 649.6 | 330.6 | 308
235 | 146 | 652 | 336.4 | 313.3
236 | 147 | 654.5 | 342.6 | 318.6
237 | 148 | 656.8 | 348.7 | 323.7
238 | 149 | 659 | 354.8 | 328.9
239 | 150 | 661 | 360.8 | 334
240 | 151 | 662.5 | 367 | 339.2
241 | 152 | 664 | 373 | 344.2
242 | 153 | 665.5 | 378.7 | 349.3
243 | 154 | 666.7 | 384 | 354.4
244 | 155 | 668.1 | 389.4 | 359.6
245 | 156 | 669.5 | 395.2 | 364.6
246 | 157 | 670.9 | 400.9 | 369.5
247 | 158 | 672.7 | 406.2 | 374.5
248 | 159 | 674.3 | 411.4 | 379.6
249 | 160 | 675.8 | 416.5 | 384.7
250 | 161 | 677.4 | 421.6 | 389.8
251 | 162 | 679.2 | 426.5 | 395
252 | 163 | 680.8 | 430.8 | 400.4
253 | 164 | 682.2 | 435.1 | 405.6
254 | 165 | 683.7 | 439.3 | 410.5
255 | 166 | 685.4 | 443.6 | 415.5
256 | 167 | 686.5 | 447.3 | 420.5
257 | 168 | 687.4 | 450.7 | 425.5
258 | 169 | 688.3 | 454.2 | 430.4
259 | 170 | 689.2 | 457.8 | 435.2
260 | 171 | 689.9 | 461.3 | 440
261 | 172 | 690.5 | 464.4 | 444.9
262 | 173 | 691 | 467.3 | 449.7
263 | 174 | 691.4 | 470.3 | 454.5
264 | 175 | 691.7 | 473.1 | 459.2
265 | 176 | 691.9 | 475.7 | 463.9
266 | 177 | 692.2 | 478.4 | 468.4
267 | 178 | 692.4 | 481.3 | 473
268 | 179 | 692.4 | 484.3 | 477.6
269 | 180 | 692.6 | 487.5 | 482
270 | 181 | 692.8 | 490.8 | 486.4
271 | 182 | 693.2 | 494 | 490.7
272 | 183 | 694 | 497.3 | 494.7
273 | 184 | 694.8 | 500.3 | 498.7
274 | 185 | 695.6 | 503.4 | 502.7
275 | 186 | 696.2 | 506.5 | 507
276 | 187 | 696.8 | 509.6 | 511.2
277 | 188 | 697.1 | 512.5 | 515.4
278 | 189 | 697.2 | 515.2 | 519.5
279 | 190 | 697 | 518.1 | 523.7
280 | 191 | 697.1 | 521.1 | 527.8
281 | 192 | 697.2 | 524 | 531.9
282 | 193 | 697.2 | 526.8 | 535.8
283 | 194 | 697.3 | 529.6 | 539.8
284 | 195 | 697.5 | 532.2 | 543.8
285 | 196 | 697.8 | 534.8 | 547.6
286 | 197 | 698 | 537.4 | 551.4
287 | 198 | 698.1 | 540 | 555.1
288 | 199 | 698.2 | 542.7 | 559
289 | 200 | 698.3 | 545.2 | 563
290 | 201 | 698.5 | 547.6 | 566.8
291 | 202 | 698.6 | 550.1 | 570.3
292 | 203 | 698.5 | 552.4 | 573.8
293 | 204 | 698.6 | 554.7 | 577.2
294 | 205 | 698.8 | 557 | 580.6
295 | 206 | 698.9 | 559.2 | 583.8
296 | 207 | 699.1 | 561.3 | 586.9
297 | 208 | 699.4 | 563.5 | 590
298 | 209 | 699.7 | 565.8 | 593.1
299 | 210 | 699.8 | 568.1 | 596.2
300 | 211 | 699.7 | 570.4 | 599.4
301 | 212 | 699.7 | 572.8 | 602.4
302 | 213 | 699.7 | 575.3 | 605.2
303 | 214 | 699.4 | 577.9 | 608
304 | 215 | 699.3 | 580.3 | 610.7
305 | 216 | 699.4 | 582.7 | 613.3
306 | 217 | 699.6 | 585.2 | 615.8
307 | 218 | 699.7 | 587.7 | 618.3
308 | 219 | 699.6 | 590.3 | 620.9
309 | 220 | 699.8 | 592.8 | 623.4
310 | 221 | 700.1 | 595.4 | 625.8
311 | 222 | 700.5 | 597.9 | 628.3
312 | 223 | 700.9 | 600.3 | 631.1
313 | 224 | 701 | 602.3 | 634.5
314 | 225 | 701.1 | 604.8 | 636.8
315 | 226 | 700.7 | 607.3 | 638.9
316 | 227 | 700.1 | 609.7 | 641
317 | 228 | 699.3 | 612.1 | 643
318 | 229 | 698.2 | 614.3 | 644.9
319 | 230 | 696.8 | 616.6 | 646.8
320 | 231 | 695.3 | 618.8 | 648.6
321 | 232 | 693.7 | 620.9 | 650.2
322 | 233 | 692 | 623 | 651.8
323 | 234 | 690.2 | 625 | 653.4
324 | 235 | 688.4 | 626.8 | 654.8
325 | 236 | 686.9 | 628.4 | 656.2
326 | 237 | 685.2 | 629.9 | 657.5
327 | 238 | 683.4 | 631.3 | 658.8
328 | 239 | 681.6 | 632.7 | 660
329 | 240 | 679.8 | 634.1 | 661.1
330 | 241 | 677.9 | 635.3 | 662.2
331 | 242 | 675.9 | 636.5 | 663.2
332 | 243 | 674.1 | 637.6 | 664.2
333 | 244 | 672.4 | 638.6 | 665.1
334 | 245 | 670.8 | 639.7 | 666
335 | 246 | 669.3 | 640.9 | 667
336 | 247 | 667.6 | 641.9 | 667.8
337 | 248 | 666.1 | 642.9 | 668.7
338 | 249 | 664.4 | 643.9 | 669.5
339 | 250 | 662.6 | 644.9 | 670.3
340 | 251 | 660.9 | 645.8 | 671
341 | 252 | 659.4 | 646.7 | 671.6
342 | 253 | 657.8 | 647.6 | 672.3
343 | 254 | 656.3 | 648.5 | 672.9
344 | 255 | 654.9 | 649.3 | 673.5
345 | 256 | 653.4 | 650.1 | 674
346 | 257 | 651.7 | 650.9 | 674.6
347 | 258 | 650.3 | 651.6 | 675.1
348 | 259 | 649.1 | 652.3 | 675.5
349 | 260 | 647.6 | 653 | 675.9
350 | 261 | 646 | 653.5 | 676.3
351 | 262 | 644.7 | 654 | 676.6
352 | 263 | 643.5 | 654.5 | 676.9
353 | 264 | 642.2 | 655 | 677.2
354 | 265 | 641 | 655.4 | 677.4
355 | 266 | 639.6 | 655.8 | 677.7
356 | 267 | 638 | 656.2 | 677.8
357 | 268 | 636.6 | 656.6 | 678
358 | 269 | 635 | 656.9 | 678.2
359 | 270 | 633.6 | 657.2 | 678.3
360 | 271 | 632.2 | 657.5 | 678.4
361 | 272 | 630.8 | 657.8 | 678.5
362 | 273 | 629.3 | 658.1 | 678.5
363 | 274 | 627.7 | 658.3 | 678.6
364 | 275 | 626.1 | 658.6 | 678.5
365 | 276 | 624.7 | 658.8 | 678.5
366 | 277 | 623.3 | 658.9 | 678.5
367 | 278 | 621.7 | 659.1 | 678.4
368 | 279 | 620.3 | 659.3 | 678.3
369 | 280 | 619 | 659.4 | 678.1
370 | 281 | 617.7 | 659.6 | 678
371 | 282 | 616.5 | 659.7 | 677.8
372 | 283 | 615.3 | 659.8 | 677.7
373 | 284 | 613.8 | 659.9 | 677.4
374 | 285 | 612.2 | 660 | 677.2
375 | 286 | 610.8 | 660 | 676.9
376 | 287 | 609.4 | 660 | 676.6
377 | 288 | 607.7 | 660 | 676.3
378 | 289 | 606.2 | 660.2 | 676
379 | 290 | 604.6 | 660.3 | 675.7
380 | 291 | 603 | 660.4 | 675.4
381 | 292 | 601.6 | 660.4 | 675
382 | 293 | 600.2 | 660.5 | 674.7
383 | 294 | 598.9 | 660.6 | 674.3
384 | 295 | 597.5 | 660.6 | 673.9
385 | 296 | 596 | 660.6 | 673.4
386 | 297 | 594.8 | 660.7 | 673
387 | 298 | 593.6 | 660.7 | 672.5
388 | 299 | 592.1 | 660.8 | 672.1
389 | 300 | 590.8 | 660.8 | 671.7
390 | 301 | 589.6 | 660.9 | 671.1
391 | 302 | 588.5 | 660.9 | 670.6
392 | 303 | 587.2 | 661 | 670
393 | 304 | 585.9 | 661.1 | 669.5
394 | 305 | 584.5 | 661.2 | 668.9
395 | 306 | 583.1 | 661.3 | 668.4
396 | 307 | 582 | 661.4 | 667.8
397 | 308 | 580.7 | 661.5 | 667.2
398 | 309 | 579.3 | 661.5 | 666.6
399 | 310 | 578 | 661.6 | 666
400 | 311 | 576.6 | 661.7 | 665.3
401 | 312 | 575.3 | 661.8 | 664.7
402 | 313 | 573.9 | 662 | 664
403 | 314 | 572.4 | 662.1 | 663.4
404 | 315 | 571.1 | 662.3 | 662.7
405 | 316 | 570 | 662.6 | 662
406 | 317 | 568.7 | 662.9 | 661.3
407 | 318 | 567.3 | 663.2 | 660.6
408 | 319 | 566 | 663.6 | 659.8
409 | 320 | 564.7 | 663.9 | 659.1
410 | 321 | 563.4 | 664.2 | 658.3
411 | 322 | 562.1 | 664.6 | 657.5
412 | 323 | 560.9 | 665 | 656.7
413 | 324 | 559.5 | 665.2 | 656
414 | 325 | 558.2 | 665.6 | 655.2
415 | 326 | 557 | 665.9 | 654.5
416 | 327 | 555.8 | 666.1 | 653.7
417 | 328 | 554.4 | 666.5 | 652.8
418 | 329 | 553.1 | 666.9 | 651.9
419 | 330 | 551.9 | 667.3 | 651
420 | 331 | 550.9 | 667.7 | 650.1
421 | 332 | 549.9 | 668.2 | 649.2
422 | 333 | 548.7 | 668.7 | 648.3
423 | 334 | 547.5 | 669 | 647.4
424 | 335 | 546.3 | 669.3 | 646.3
425 | 336 | 545.3 | 669.4 | 645.3
426 | 337 | 544.4 | 669.5 | 644.3
427 | 338 | 543.2 | 669.6 | 643.3
428 | 339 | 542 | 669.8 | 642.2
429 | 340 | 540.7 | 670.1 | 641.2
430 | 341 | 539.6 | 670.1 | 640.1
431 | 342 | 538.2 | 670.2 | 639
432 | 343 | 537 | 670.4 | 637.9
433 | 344 | 536.1 | 670.6 | 636.8
434 | 345 | 535 | 670.7 | 635.7
435 | 346 | 533.9 | 671 | 634.5
436 | 347 | 532.6 | 671.4 | 633.4
437 | 348 | 531.4 | 671.7 | 632.3
438 | 349 | 530.5 | 672.1 | 631.1
439 | 350 | 529.6 | 672.2 | 629.9
440 | 351 | 528.7 | 672.3 | 628.7
441 | 352 | 527.5 | 672.4 | 627.5
442 | 353 | 526.5 | 672.4 | 626.4
443 | 354 | 525.7 | 672.5 | 625.1
444 | 355 | 524.5 | 672.6 | 623.9
445 | 356 | 523.4 | 672.6 | 622.7
446 | 357 | 522.3 | 672.6 | 621.4
447 | 358 | 521.4 | 672.7 | 620.2
448 | 359 | 520.6 | 672.7 | 618.9
449 | 360 | 519.5 | 672.8 | 617.6
450 | 361 | 518.5 | 672.9 | 616.4
451 | 362 | 517.5 | 673 | 615
452 | 363 | 516.6 | 673.1 | 613.7
453 | 364 | 515.4 | 673.2 | 612.4
454 | 365 | 514.2 | 673.3 | 611
455 | 366 | 513 | 673.4 | 609.7
456 | 367 | 511.9 | 673.5 | 608.3
457 | 368 | 510.8 | 673.6 | 606.9
458 | 369 | 509.6 | 673.6 | 605.6
459 | 370 | 508.4 | 673.7 | 604.2
460 | 371 | 507.4 | 673.8 | 602.8
461 | 372 | 506.7 | 673.8 | 601.4
462 | 373 | 505.9 | 673.8 | 600
463 | 374 | 504.9 | 673.8 | 598.5
464 | 375 | 503.8 | 673.8 | 597.1
465 | 376 | 502.8 | 673.8 | 595.7
466 | 377 | 501.8 | 673.7 | 594.3
467 | 378 | 500.7 | 673.7 | 592.9
468 | 379 | 499.6 | 673.7 | 591.5
469 | 380 | 498.4 | 673.8 | 590.1
470 | 381 | 497.4 | 674 | 588.7
471 | 382 | 496.5 | 674.1 | 587.4
472 | 383 | 495.4 | 674.2 | 586
473 | 384 | 494.4 | 674.3 | 584.7
474 | 385 | 493.3 | 674.3 | 583.4
475 | 386 | 492.4 | 674.5 | 582
476 | 387 | 491.3 | 674.5 | 580.6
477 | 388 | 490.4 | 674.5 | 579.3
478 | 389 | 489.4 | 674.5 | 578
479 | 390 | 488.5 | 674.4 | 576.6
480 | 391 | 487.5 | 674.5 | 575.2
481 | 392 | 486.5 | 674.5 | 573.9
482 | 393 | 485.8 | 674.5 | 572.5
483 | 394 | 485.2 | 674.5 | 571.2
484 | 395 | 484.4 | 674.5 | 569.8
485 | 396 | 483.6 | 674.5 | 568.5
486 | 397 | 482.8 | 674.5 | 567.1
487 | 398 | 482 | 674.4 | 565.8
488 | 399 | 481.2 | 674.4 | 564.6
489 | 400 | 480.3 | 674.3 | 563.3
490 | 401 | 479.4 | 674.2 | 562.1
491 | 402 | 478.5 | 674 | 560.8
492 | 403 | 477.6 | 673.9 | 559.4
493 | 404 | 476.9 | 673.8 | 558.1
494 | 405 | 476.2 | 673.8 | 556.9
495 | 406 | 475.4 | 673.7 | 555.6
496 | 407 | 474.7 | 673.5 | 554.4
497 | 408 | 473.9 | 673.4 | 553.1
498 | 409 | 473.1 | 673.4 | 551.9
499 | 410 | 472.2 | 673.4 | 550.6
500 | 411 | 471.4 | 673.2 | 549.4
501 | 412 | 470.5 | 673 | 548.1
502 | 413 | 469.6 | 672.7 | 546.9
503 | 414 | 468.8 | 672.4 | 545.7
504 | 415 | 467.9 | 672 | 544.5
505 | 416 | 466.9 | 671.5 | 543.2
506 | 417 | 466 | 671.1 | 542
507 | 418 | 465.2 | 670.6 | 540.7
508 | 419 | 464.4 | 670.2 | 539.5
509 | 420 | 463.6 | 669.7 | 538.3
510 | 421 | 462.7 | 669.3 | 537.1
511 | 422 | 461.9 | 668.9 | 535.9
512 | 423 | 460.9 | 668.5 | 534.7
513 | 424 | 460 | 668.1 | 533.5
514 | 425 | 459.1 | 667.6 | 532.3
515 | 426 | 458.2 | 667.2 | 531.1
516 | 427 | 457.2 | 666.7 | 529.9
517 | 428 | 456.2 | 666.3 | 528.8
518 | 429 | 455.2 | 665.8 | 527.6
519 | 430 | 454.2 | 665.5 | 526.5
520 | 431 | 453.1 | 665.1 | 525.3
521 | 432 | 452 | 664.7 | 524.1
522 | 433 | 451.1 | 664.3 | 523
523 | 434 | 450.3 | 664 | 521.9
524 | 435 | 449.3 | 663.6 | 520.7
525 | 436 | 448.2 | 663.3 | 519.6
526 | 437 | 447.2 | 663 | 518.5
527 | 438 | 446.2 | 662.7 | 517.4
528 | 439 | 445.5 | 662.4 | 516.3
529 | 440 | 444.7 | 662.1 | 515.2
530 | 441 | 444 | 661.8 | 514.1
531 | 442 | 443.4 | 661.5 | 513.1
532 | 443 | 442.7 | 661.1 | 512
533 | 444 | 442 | 660.8 | 510.9
534 | 445 | 441.3 | 660.4 | 509.9
535 | 446 | 440.5 | 660.1 | 508.8
536 | 447 | 439.6 | 659.8 | 507.7
537 | 448 | 438.6 | 659.4 | 506.7
538 | 449 | 437.4 | 659.1 | 505.6
539 | 450 | 436.5 | 658.8 | 504.5
540 | 451 | 435.6 | 658.6 | 503.5
541 | 452 | 434.7 | 658.3 | 502.4
542 | 453 | 433.9 | 658 | 501.4
543 | 454 | 433.1 | 657.8 | 500.4
544 | 455 | 432.1 | 657.5 | 499.5
545 | 456 | 431.2 | 657.3 | 498.5
546 | 457 | 430.4 | 657.1 | 497.4
547 | 458 | 429.6 | 656.9 | 496.4
548 | 459 | 429.1 | 656.5 | 495.5
549 | 460 | 428.5 | 656.2 | 494.5
550 | 461 | 427.7 | 655.8 | 493.5
551 | 462 | 427.1 | 655.6 | 492.5
552 | 463 | 426.6 | 655.3 | 491.6
553 | 464 | 426.1 | 655 | 490.6
554 | 465 | 425.4 | 654.7 | 489.7
555 | 466 | 424.8 | 654.5 | 488.8
556 | 467 | 424.1 | 654.3 | 487.9
557 | 468 | 423.2 | 654 | 487
558 | 469 | 422.2 | 653.8 | 486
559 | 470 | 421.3 | 653.5 | 485.1
560 | 471 | 420.3 | 653.3 | 484.2
561 | 472 | 419.5 | 653.1 | 483.3
562 | 473 | 418.7 | 652.7 | 482.5
563 | 474 | 417.9 | 652.4 | 481.7
564 | 475 | 417.2 | 652 | 480.8
565 | 476 | 416.6 | 651.7 | 479.9
566 | 477 | 415.9 | 651.4 | 479
567 | 478 | 415.3 | 651.1 | 478.2
568 | 479 | 414.6 | 650.9 | 477.3
569 | 480 | 413.7 | 650.6 | 476.4
570 | 481 | 413.1 | 650.3 | 475.6
571 | 482 | 412.3 | 650 | 474.7
572 | 483 | 411.6 | 649.7 | 473.9
573 | 484 | 410.7 | 649.4 | 473
574 | 485 | 410 | 649.1 | 472.2
575 | 486 | 409.3 | 648.8 | 471.3
576 | 487 | 408.5 | 648.5 | 470.5
577 | 488 | 407.8 | 648.2 | 469.6
578 | 489 | 407.1 | 647.9 | 468.8
579 | 490 | 406.4 | 647.7 | 468
580 | 491 | 405.5 | 647.5 | 467.2
581 | 492 | 404.7 | 647.3 | 466.4
582 | 493 | 404 | 647 | 465.6
583 | 494 | 403.2 | 646.7 | 464.8
584 | 495 | 402.4 | 646.4 | 464
585 | 496 | 401.6 | 646.1 | 463.2
586 | 497 | 400.9 | 645.9 | 462.4
587 | 498 | 400.2 | 645.7 | 461.6
588 | 499 | 399.6 | 645.4 | 460.7
589 | 500 | 398.7 | 645.1 | 460
590 | 501 | 397.9 | 644.8 | 459.1
591 | 502 | 397.1 | 644.5 | 458.3
592 | 503 | 396.4 | 644.2 | 457.5
593 | 504 | 395.9 | 643.9 | 456.7
594 | 505 | 395.2 | 643.6 | 456
595 | 506 | 394.7 | 643.2 | 455.2
596 | 507 | 394.1 | 642.8 | 454.4
597 | 508 | 393.6 | 642.4 | 453.6
598 | 509 | 393 | 642.1 | 452.9
599 | 510 | 392.4 | 641.7 | 452.1
600 | 511 | 391.6 | 641.3 | 451.4
601 | 512 | 390.8 | 640.8 | 450.6
602 | 513 | 390 | 640.5 | 449.8
603 | 514 | 389.4 | 640 | 449.1
604 | 515 | 388.9 | 639.6 | 448.3
605 | 516 | 388.2 | 639.1 | 447.6
606 | 517 | 387.4 | 638.6 | 446.9
607 | 518 | 386.7 | 638.2 | 446.1
608 | 519 | 386.1 | 637.8 | 445.4
609 | 520 | 385.5 | 637.3 | 444.6
610 | 521 | 384.8 | 636.9 | 443.9
611 | 522 | 384.2 | 636.4 | 443.2
612 | 523 | 383.5 | 636 | 442.4
613 | 524 | 382.8 | 635.5 | 441.7
614 | 525 | 382 | 635 | 441
615 | 526 | 381.4 | 634.5 | 440.3
616 | 527 | 381 | 634.1 | 439.5
617 | 528 | 380.5 | 633.6 | 438.8
618 | 529 | 379.9 | 633.1 | 438.1
619 | 530 | 379.4 | 632.6 | 437.4
620 | 531 | 379 | 632.2 | 436.7
621 | 532 | 378.6 | 631.6 | 436
622 | 533 | 378.2 | 631.1 | 435.3
623 | 534 | 377.6 | 630.6 | 434.6
624 | 535 | 376.9 | 630 | 433.9
625 | 536 | 376.2 | 629.5 | 433.2
626 | 537 | 375.5 | 629 | 432.5
627 | 538 | 375 | 628.4 | 431.8
628 | 539 | 374.5 | 627.8 | 431.1
629 | 540 | 373.9 | 627.2 | 430.4
630 | 541 | 373.2 | 626.5 | 429.7
631 | 542 | 372.6 | 625.9 | 429
632 | 543 | 372 | 625.3 | 428.3
633 | 544 | 371.3 | 624.6 | 427.7
634 | 545 | 370.6 | 623.9 | 427
635 | 546 | 369.9 | 623.3 | 426.3
636 | 547 | 369.2 | 622.6 | 425.6
637 | 548 | 368.6 | 622 | 425
638 | 549 | 368 | 621.3 | 424.3
639 | 550 | 367.3 | 620.6 | 423.6
640 | 551 | 366.7 | 619.9 | 422.9
641 | 552 | 366 | 619.2 | 422.2
642 | 553 | 365.3 | 618.5 | 421.6
643 | 554 | 364.7 | 617.8 | 420.9
644 | 555 | 364.2 | 617 | 420.2
645 | 556 | 363.6 | 616.2 | 419.5
646 | 557 | 363 | 615.4 | 418.8
647 | 558 | 362.4 | 614.6 | 418.1
648 | 559 | 361.8 | 613.7 | 417.5
649 | 560 | 361.3 | 612.9 | 416.8
650 | 561 | 360.7 | 612 | 416.1
651 | 562 | 360.1 | 611.1 | 415.5
652 | 563 | 359.5 | 610.2 | 414.8
653 | 564 | 358.9 | 609.3 | 414.1
654 | 565 | 358.4 | 608.4 | 413.5
655 | 566 | 357.8 | 607.5 | 412.8
656 | 567 | 357.1 | 606.6 | 412.1
657 | 568 | 356.4 | 605.7 | 411.5
658 | 569 | 355.8 | 604.8 | 410.8
659 | 570 | 355.2 | 603.9 | 410.2
660 | 571 | 354.6 | 602.9 | 409.5
661 | 572 | 354.2 | 601.9 | 408.8
662 | 573 | 353.7 | 600.9 | 408.1
663 | 574 | 353.1 | 599.9 | 407.5
664 | 575 | 352.5 | 598.9 | 406.8
665 | 576 | 352 | 597.8 | 406.2
666 | 577 | 351.5 | 596.7 | 405.5
667 | 578 | 351.1 | 595.7 | 404.8
668 | 579 | 350.6 | 594.6 | 404.2
669 | 580 | 350.1 | 593.5 | 403.5
670 | 581 | 349.5 | 592.4 | 402.9
671 | 582 | 348.9 | 591.3 | 402.2
672 | 583 | 348.4 | 590.1 | 401.6
673 | 584 | 347.8 | 589 | 400.9
674 | 585 | 347.3 | 587.9 | 400.3
675 | 586 | 346.7 | 586.7 | 399.6
676 | 587 | 346.2 | 585.6 | 399
677 | 588 | 345.6 | 584.4 | 398.4
678 | 589 | 345 | 583.3 | 397.7
679 | 590 | 344.4 | 582.1 | 397.1
680 | 591 | 343.7 | 580.9 | 396.4
681 | 592 | 343.1 | 579.7 | 395.8
682 | 593 | 342.6 | 578.5 | 395.2
683 | 594 | 342.1 | 577.3 | 394.5
684 | 595 | 341.6 | 576.1 | 393.9
685 | 596 | 341.1 | 574.9 | 393.2
686 | 597 | 340.7 | 573.7 | 392.6
687 | 598 | 340.3 | 572.4 | 392
688 | 599 | 339.9 | 571.2 | 391.4
689 | 600 | 339.6 | 569.9 | 390.7
690 | 601 | 339.1 | 568.7 | 390.1
691 | 602 | 338.6 | 567.4 | 389.4
692 | 603 | 338.2 | 566.2 | 388.8
693 | 604 | 337.7 | 565 | 388.2
694 | 605 | 337.2 | 563.7 | 387.6
695 | 606 | 336.8 | 562.5 | 387
696 | 607 | 336.4 | 561.3 | 386.4
697 | 608 | 336 | 560 | 385.7
698 | 609 | 335.5 | 558.8 | 385.1
699 | 610 | 335.1 | 557.6 | 384.5
700 | 611 | 334.6 | 556.4 | 383.9
701 | 612 | 334 | 555.2 | 383.3
702 | 613 | 333.5 | 554 | 382.7
703 | 614 | 332.9 | 552.8 | 382
704 | 615 | 332.3 | 551.6 | 381.4
705 | 616 | 331.5 | 550.4 | 380.8
706 | 617 | 331 | 549.2 | 380.3
707 | 618 | 330.3 | 548 | 379.6
708 | 619 | 329.7 | 546.7 | 379
709 | 620 | 329.1 | 545.5 | 378.3
710 | 621 | 328.5 | 544.3 | 377.6
711 | 622 | 328 | 543 | 376.9
712 | 623 | 327.5 | 541.8 | 376.2
713 | 624 | 327.2 | 540.5 | 375.5
714 | 625 | 326.8 | 539.3 | 374.9
715 | 626 | 326.1 | 538 | 374.2
716 | 627 | 325.5 | 536.8 | 373.6
717 | 628 | 325.1 | 535.6 | 372.9
718 | 629 | 324.6 | 534.4 | 372.3
719 | 630 | 324.2 | 533.2 | 371.7
720 | 631 | 323.7 | 532 | 371.1
721 | 632 | 323.2 | 530.8 | 370.5
722 | 633 | 322.8 | 529.7 | 369.9
723 | 634 | 322.3 | 528.5 | 369.2
724 | 635 | 321.9 | 527.4 | 368.6
725 | 636 | 321.4 | 526.3 | 368
726 | 637 | 320.8 | 525.2 | 367.4
727 | 638 | 320.2 | 524.1 | 366.8
728 | 639 | 319.6 | 523 | 366.1
729 | 640 | 319 | 521.9 | 365.5
730 | 641 | 318.3 | 520.8 | 364.9
731 | 642 | 317.8 | 519.8 | 364.3
732 | 643 | 317.3 | 518.7 | 363.7
733 | 644 | 316.8 | 517.6 | 363
734 | 645 | 316.3 | 516.6 | 362.4
735 | 646 | 315.7 | 515.5 | 361.8
736 | 647 | 315.3 | 514.5 | 361.2
737 | 648 | 314.8 | 513.4 | 360.6
738 | 649 | 314.4 | 512.4 | 360
739 | 650 | 313.9 | 511.4 | 359.4
740 | 651 | 313.5 | 510.4 | 358.8
741 | 652 | 313 | 509.4 | 358.1
742 | 653 | 312.4 | 508.4 | 357.6
743 | 654 | 311.9 | 507.4 | 357
744 | 655 | 311.4 | 506.4 | 356.4
745 | 656 | 310.9 | 505.4 | 355.8
746 | 657 | 310.3 | 504.5 | 355.2
747 | 658 | 309.9 | 503.5 | 354.6
748 | 659 | 309.4 | 502.5 | 354
749 | 660 | 308.8 | 501.6 | 353.4
750 | 661 | 308.3 | 500.6 | 352.8
751 | 662 | 307.8 | 499.8 | 352.3
752 | 663 | 307.4 | 498.9 | 351.7
753 | 664 | 306.9 | 497.9 | 351.1
754 | 665 | 306.4 | 497 | 350.6
755 | 666 | 305.9 | 496 | 350
756 | 667 | 305.3 | 495.1 | 349.4
757 | 668 | 304.8 | 494.2 | 348.9
758 | 669 | 304.3 | 493.2 | 348.3
759 | 670 | 303.8 | 492.3 | 347.8
760 | 671 | 303.3 | 491.3 | 347.2
761 | 672 | 302.9 | 490.3 | 346.6
762 | 673 | 302.5 | 489.4 | 346.1
763 | 674 | 302.1 | 488.4 | 345.5
764 | 675 | 301.6 | 487.5 | 345
765 | 676 | 301.1 | 486.6 | 344.5
766 | 677 | 300.6 | 485.6 | 343.9
767 | 678 | 300.2 | 484.7 | 343.4
768 | 679 | 299.8 | 483.7 | 342.9
769 | 680 | 299.5 | 482.8 | 342.3
770 | 681 | 299.1 | 481.9 | 341.8
771 | 682 | 298.7 | 481 | 341.3
772 | 683 | 298.3 | 480.1 | 340.7
773 | 684 | 297.8 | 479.2 | 340.2
774 | 685 | 297.4 | 478.3 | 339.6
775 | 686 | 297 | 477.3 | 339.1
776 | 687 | 296.6 | 476.4 | 338.5
777 | 688 | 296.1 | 475.5 | 338
778 | 689 | 295.6 | 474.6 | 337.4
779 | 690 | 295.2 | 473.7 | 336.9
780 | 691 | 294.8 | 472.8 | 336.4
781 | 692 | 294.4 | 471.9 | 335.8
782 | 693 | 293.9 | 471 | 335.3
783 | 694 | 293.4 | 470.1 | 334.7
784 | 695 | 293 | 469.2 | 334.1
785 | 696 | 292.5 | 468.3 | 333.6
786 | 697 | 292.1 | 467.4 | 333.1
787 | 698 | 291.7 | 466.5 | 332.5
788 | 699 | 291.4 | 465.6 | 332
789 | 700 | 291 | 464.7 | 331.5
790 | 701 | 290.7 | 463.9 | 331
791 | 702 | 290.2 | 463 | 330.4
792 | 703 | 289.8 | 462.1 | 329.9
793 | 704 | 289.4 | 461.3 | 329.4
794 | 705 | 289.2 | 460.4 | 328.8
795 | 706 | 288.9 | 459.5 | 328.3
796 | 707 | 288.5 | 458.6 | 327.8
797 | 708 | 288 | 457.7 | 327.2
798 | 709 | 287.6 | 456.8 | 326.7
799 | 710 | 287.1 | 456 | 326.2
800 | 711 | 286.5 | 455.1 | 325.6
801 | 712 | 286.1 | 454.2 | 325.1
802 | 713 | 285.7 | 453.3 | 324.6
803 | 714 | 285.4 | 452.4 | 324.1
804 | 715 | 284.9 | 451.5 | 323.6
805 | 716 | 284.4 | 450.6 | 323.1
806 | 717 | 283.8 | 449.7 | 322.6
807 | 718 | 283.4 | 448.8 | 322
808 | 719 | 283 | 447.9 | 321.5
809 | 720 | 282.6 | 447.1 | 321
810 | 721 | 282.2 | 446.2 | 320.5
811 | 722 | 281.8 | 445.3 | 320
812 | 723 | 281.4 | 444.4 | 319.5
813 | 724 | 281 | 443.5 | 319
814 | 725 | 280.6 | 442.7 | 318.5
815 | 726 | 280.3 | 441.8 | 317.9
816 | 727 | 279.9 | 440.9 | 317.4
817 | 728 | 279.5 | 440 | 316.9
818 | 729 | 279 | 439.1 | 316.4
819 | 730 | 278.6 | 438.2 | 315.9
820 | 731 | 278.3 | 437.3 | 315.4
821 | 732 | 277.8 | 436.4 | 314.9
822 | 733 | 277.5 | 435.6 | 314.4
823 | 734 | 277.2 | 434.7 | 313.9
824 | 735 | 276.9 | 433.8 | 313.4
825 | 736 | 276.6 | 433 | 313
826 | 737 | 276.2 | 432.1 | 312.5
827 | 738 | 275.8 | 431.2 | 312
828 | 739 | 275.3 | 430.4 | 311.6
829 | 740 | 274.9 | 429.5 | 311.1
830 | 741 | 274.7 | 428.7 | 310.6
831 | 742 | 274.5 | 427.8 | 310.1
832 | 743 | 274 | 427 | 309.7
833 | 744 | 273.5 | 426.1 | 309.2
834 | 745 | 273.1 | 425.3 | 308.7
835 | 746 | 272.7 | 424.5 | 308.2
836 | 747 | 272.3 | 423.6 | 307.8
837 | 748 | 272.1 | 422.7 | 307.3
838 | 749 | 271.7 | 421.9 | 306.9
839 | 750 | 271.3 | 421 | 306.4
840 | 751 | 271 | 420.2 | 306
841 | 752 | 270.6 | 419.3 | 305.5
842 | 753 | 270.1 | 418.5 | 305
843 | 754 | 269.8 | 417.6 | 304.6
844 | 755 | 269.4 | 416.8 | 304.1
845 | 756 | 269.1 | 416 | 303.6
846 | 757 | 268.9 | 415.1 | 303.2
847 | 758 | 268.6 | 414.3 | 302.7
848 | 759 | 268.2 | 413.4 | 302.3
849 | 760 | 267.8 | 412.6 | 301.8
850 | 761 | 267.4 | 411.8 | 301.4
851 | 762 | 267.1 | 410.9 | 300.9
852 | 763 | 266.8 | 410.1 | 300.4
853 | 764 | 266.4 | 409.3 | 300
854 | 765 | 266 | 408.5 | 299.5
855 | 766 | 265.6 | 407.7 | 299.1
856 | 767 | 265.2 | 406.9 | 298.6
857 | 768 | 264.8 | 406.1 | 298.1
858 | 769 | 264.4 | 405.3 | 297.7
859 | 770 | 264 | 404.5 | 297.2
860 | 771 | 263.6 | 403.7 | 296.8
861 | 772 | 263.3 | 402.9 | 296.3
862 | 773 | 263 | 402.1 | 295.9
863 | 774 | 262.6 | 401.4 | 295.4
864 | 775 | 262.2 | 400.6 | 295
865 | 776 | 261.8 | 399.8 | 294.5
866 | 777 | 261.4 | 399 | 294.1
867 | 778 | 261 | 398.2 | 293.6
868 | 779 | 260.6 | 397.4 | 293.2
869 | 780 | 260.2 | 396.6 | 292.7
870 | 781 | 259.9 | 395.8 | 292.3
871 | 782 | 259.6 | 395 | 291.8
872 | 783 | 259.3 | 394.2 | 291.4
873 | 784 | 259.1 | 393.5 | 290.9
874 | 785 | 258.7 | 392.7 | 290.5
875 | 786 | 258.4 | 392 | 290.1
876 | 787 | 258 | 391.2 | 289.6
877 | 788 | 257.6 | 390.4 | 289.2
878 | 789 | 257.3 | 389.7 | 288.8
879 | 790 | 257 | 388.9 | 288.4
880 | 791 | 256.7 | 388.2 | 287.9
881 | 792 | 256.4 | 387.4 | 287.5
882 | 793 | 256 | 386.7 | 287.1
883 | 794 | 255.7 | 385.9 | 286.6
884 | 795 | 255.4 | 385.2 | 286.2
885 | 796 | 255.2 | 384.5 | 285.8
886 | 797 | 255 | 383.7 | 285.3
887 | 798 | 254.6 | 383 | 284.9
888 | 799 | 254.2 | 382 | 284.5
889 | 800 | 253.9 | 381 | 284.1
890 | 801 | 253.6 | 380 | 283.7
891 | 802 | 253.4 | 379 | 283.3
892 | 803 | 253.1 | 378 | 282.9
893 | 804 | 252.9 | 377 | 282.4
894 | 805 | 252.6 | 376 | 282
895 | 806 | 252.4 | 375 | 281.6
896 | 807 | 252.1 | 374.1 | 281.3
897 | 808 | 251.7 | 373.2 | 280.8
898 | 809 | 251.2 | 372.3 | 280.4
899 | 810 | 250.9 | 371.4 | 280.1
900 | 811 | 250.6 | 370.4 | 279.7
901 | 812 | 250.3 | 369.5 | 279.3
902 | 813 | 249.9 | 368.6 | 278.8
903 | 814 | 249.4 | 367.7 | 278.4
904 | 815 | 248.9 | 366.8 | 278
905 | 816 | 248.4 | 366 | 277.6
906 | 817 | 248 | 365.2 | 277.2
907 | 818 | 247.7 | 364.3 | 276.8
908 | 819 | 247.4 | 363.5 | 276.4
909 | 820 | 247 | 362.7 | 276
910 | 821 | 246.6 | 361.9 | 275.6
911 | 822 | 246.3 | 361.2 | 275.2
912 | 823 | 245.9 | 360.4 | 274.8
913 | 824 | 245.6 | 359.6 | 274.4
914 | 825 | 245.2 | 358.9 | 274.1
915 | 826 | 244.8 | 358.1 | 273.7
916 | 827 | 244.5 | 357.4 | 273.3
917 | 828 | 244.1 | 356.6 | 272.9
918 | 829 | 243.8 | 355.9 | 272.5
919 | 830 | 243.4 | 355.2 | 272.1
920 | 831 | 243.1 | 354.4 | 271.7
921 | 832 | 242.8 | 353.7 | 271.3
922 | 833 | 242.4 | 353 | 270.9
923 | 834 | 242 | 352.3 | 270.5
924 | 835 | 241.6 | 351.5 | 270.1
925 | 836 | 241.3 | 350.8 | 269.7
926 | 837 | 241.1 | 350.1 | 269.3
927 | 838 | 240.8 | 349.4 | 268.9
928 | 839 | 240.5 | 348.7 | 268.6
929 | 840 | 240.2 | 348 | 268.2
930 | 841 | 239.8 | 347.4 | 267.8
931 | 842 | 239.6 | 346.7 | 267.4
932 | 843 | 239.5 | 346 | 267
933 | 844 | 239.3 | 345.4 | 266.6
934 | 845 | 239.2 | 344.7 | 266.3
935 | 846 | 239 | 344.1 | 265.9
936 | 847 | 238.7 | 343.4 | 265.5
937 | 848 | 238.4 | 342.8 | 265.1
938 | 849 | 238 | 342.2 | 264.7
939 | 850 | 237.7 | 341.6 | 264.4
940 | 851 | 237.4 | 340.9 | 264
941 | 852 | 237.1 | 340.3 | 263.6
942 | 853 | 236.8 | 339.6 | 263.3
943 | 854 | 236.3 | 339 | 262.9
944 | 855 | 236 | 338.3 | 262.6
945 | 856 | 235.8 | 337.7 | 262.2
946 | 857 | 235.4 | 337.1 | 261.8
947 | 858 | 235 | 336.5 | 261.5
948 | 859 | 234.6 | 335.8 | 261.1
949 | 860 | 234.3 | 335.2 | 260.7
950 | 861 | 233.9 | 334.6 | 260.3
951 | 862 | 233.6 | 334 | 259.9
952 | 863 | 233.2 | 333.4 | 259.6
953 | 864 | 233 | 332.8 | 259.2
954 | 865 | 232.8 | 332.2 | 258.8
955 | 866 | 232.5 | 331.7 | 258.5
956 | 867 | 232.3 | 331.1 | 258.1
957 | 868 | 232.1 | 330.5 | 257.7
958 | 869 | 231.8 | 329.9 | 257.4
959 | 870 | 231.5 | 329.3 | 257
960 | 871 | 231.3 | 328.7 | 256.7
961 | 872 | 231.2 | 328.1 | 256.3
962 | 873 | 230.9 | 327.5 | 256
963 | 874 | 230.7 | 326.9 | 255.6
964 | 875 | 230.5 | 326.3 | 255.3
965 | 876 | 230.2 | 325.8 | 254.9
966 | 877 | 229.9 | 325.2 | 254.6
967 | 878 | 229.7 | 324.6 | 254.2
968 | 879 | 229.5 | 324 | 253.9
969 | 880 | 229.2 | 323.5 | 253.5
970 | 881 | 228.9 | 322.9 | 253.2
971 | 882 | 228.7 | 322.3 | 252.8
972 | 883 | 228.6 | 321.7 | 252.5
973 | 884 | 228.3 | 321.2 | 252.1
974 | 885 | 228 | 320.6 | 251.8
975 | 886 | 227.6 | 320.1 | 251.4
976 | 887 | 227.3 | 319.6 | 251.1
977 | 888 | 227.1 | 319 | 250.7
978 | 889 | 226.8 | 318.4 | 250.4
979 | 890 | 226.5 | 317.9 | 250
980 | 891 | 226.2 | 317.3 | 249.7
981 | 892 | 226 | 316.8 | 249.3
982 | 893 | 225.7 | 316.2 | 249
983 | 894 | 225.4 | 315.6 | 248.6
984 | 895 | 225 | 315 | 248.3
985 | 896 | 224.6 | 314.5 | 247.9
986 | 897 | 224.2 | 313.9 | 247.6
987 | 898 | 224 | 313.4 | 247.3
988 | 899 | 223.7 | 312.8 | 246.9
989 | 900 | 223.4 | 312.3 | 246.6
990 | 901 | 223.2 | 311.7 | 246.2
991 | 902 | 222.8 | 311.2 | 245.9
992 | 903 | 222.6 | 310.6 | 245.5
993 | 904 | 222.3 | 310.1 | 245.2
994 | 905 | 222 | 309.6 | 244.8
995 | 906 | 221.7 | 309.1 | 244.5
996 | 907 | 221.4 | 308.5 | 244.1
997 | 908 | 221.2 | 308 | 243.8
998 | 909 | 220.9 | 307.4 | 243.4
999 | 910 | 220.6 | 306.9 | 243.1
1000 | 911 | 220.4 | 306.4 | 242.8
1001 | 912 | 220.2 | 305.9 | 242.4
1002 | 913 | 219.9 | 305.3 | 242.1
1003 | 914 | 219.6 | 304.8 | 241.7
1004 | 915 | 219.3 | 304.3 | 241.4
1005 | 916 | 219.1 | 303.8 | 241.1
1006 | 917 | 218.8 | 303.2 | 240.7
1007 | 918 | 218.5 | 302.7 | 240.4
1008 | 919 | 218.1 | 302.2 | 240.1
1009 | 920 | 217.8 | 301.7 | 239.8
1010 | 921 | 217.6 | 301.2 | 239.4
1011 | 922 | 217.3 | 300.7 | 239.1
1012 | 923 | 217 | 300.2 | 238.8
1013 | 924 | 216.8 | 299.7 | 238.5
1014 | 925 | 216.5 | 299.2 | 238.1
1015 | 926 | 216.2 | 298.7 | 237.8
1016 | 927 | 215.9 | 298.3 | 237.5
1017 | 928 | 215.7 | 297.8 | 237.1
1018 | 929 | 215.5 | 297.3 | 236.8
1019 | 930 | 215.2 | 296.9 | 236.5
1020 | 931 | 214.9 | 296.4 | 236.2
1021 | 932 | 214.7 | 296 | 235.8
1022 | 933 | 214.5 | 295.5 | 235.5
1023 | 934 | 214.3 | 295.1 | 235.2
1024 | 935 | 214 | 294.6 | 234.9
1025 | 936 | 213.7 | 294.2 | 234.6
1026 | 937 | 213.5 | 293.8 | 234.2
1027 | 938 | 213.3 | 293.3 | 233.9
1028 | 939 | 213 | 292.9 | 233.6
1029 | 940 | 212.8 | 292.4 | 233.3
1030 | 941 | 212.5 | 292 | 233
1031 | 942 | 212.1 | 291.5 | 232.6
1032 | 943 | 211.7 | 291.1 | 232.3
1033 | 944 | 211.4 | 290.6 | 232
1034 | 945 | 211.1 | 290.2 | 231.7
1035 | 946 | 210.9 | 289.7 | 231.4
1036 | 947 | 210.6 | 289.3 | 231.1
1037 | 948 | 210.2 | 288.8 | 230.8
1038 | 949 | 210 | 288.4 | 230.5
1039 | 950 | 209.7 | 287.9 | 230.2
1040 | 951 | 209.5 | 287.5 | 229.9
1041 | 952 | 209.3 | 287 | 229.6
1042 | 953 | 209 | 286.6 | 229.3
1043 | 954 | 208.7 | 286.1 | 229
1044 | 955 | 208.4 | 285.7 | 228.7
1045 | 956 | 208.2 | 285.3 | 228.4
1046 | 957 | 207.9 | 284.8 | 228.1
1047 | 958 | 207.7 | 284.4 | 227.8
1048 | 959 | 207.4 | 284 | 227.5
1049 | 960 | 207.1 | 283.5 | 227.2
1050 | 961 | 206.8 | 283.1 | 226.9
1051 | 962 | 206.6 | 282.7 | 226.6
1052 | 963 | 206.4 | 282.2 | 226.3
1053 | 964 | 206.1 | 281.8 | 226
1054 | 965 | 205.9 | 281.4 | 225.7
1055 | 966 | 205.6 | 281 | 225.4
1056 | 967 | 205.3 | 280.5 | 225.1
1057 | 968 | 205.1 | 280.1 | 224.8
1058 | 969 | 204.9 | 279.7 | 224.5
1059 | 970 | 204.8 | 279.3 | 224.2
1060 | 971 | 204.6 | 278.9 | 223.9
1061 | 972 | 204.3 | 278.5 | 223.6
1062 | 973 | 204 | 278.1 | 223.4
1063 | 974 | 203.8 | 277.6 | 223.1
1064 | 975 | 203.6 | 277.2 | 222.8
1065 | 976 | 203.4 | 276.8 | 222.5
1066 | 977 | 203.3 | 276.4 | 222.1
1067 | 978 | 203.1 | 276 | 221.8
1068 | 979 | 202.9 | 275.5 | 221.5
1069 | 980 | 202.7 | 275.1 | 221.2
1070 | 981 | 202.5 | 274.7 | 220.9
1071 | 982 | 202.3 | 274.3 | 220.6
1072 | 983 | 202 | 273.9 | 220.2
1073 | 984 | 201.9 | 273.5 | 219.9
1074 | 985 | 201.7 | 273.2 | 219.6
1075 | 986 | 201.4 | 272.7 | 219.3
1076 | 987 | 201.2 | 272.3 | 219
1077 | 988 | 201 | 271.9 | 218.7
1078 | 989 | 200.7 | 271.5 | 218.4
1079 | 990 | 200.5 | 271.2 | 218.1
1080 | 991 | 200.3 | 270.8 | 217.8
1081 | 992 | 200.1 | 270.4 | 217.5
1082 | 993 | 199.9 | 270 | 217.2
1083 | 994 | 199.6 | 269.5 | 217
1084 | 995 | 199.4 | 269.2 | 216.7
1085 | 996 | 199.1 | 268.8 | 216.4
1086 | 997 | 198.9 | 268.4 | 216.1
1087 | 998 | 198.7 | 268 | 215.8
1088 | 999 | 198.4 | 267.6 | 215.5
1089 | 1000 | 198.2 | 267.2 | 215.2
1090 | 1001 | 198 | 266.8 | 214.9
1091 | 1002 | 197.8 | 266.4 | 214.6
1092 | 1003 | 197.6 | 266 | 214.3
1093 | 1004 | 197.4 | 265.7 | 214
1094 | 1005 | 197.3 | 265.3 | 213.7
1095 | 1006 | 197.1 | 264.9 | 213.4
1096 | 1007 | 196.9 | 264.5 | 213.2
1097 | 1008 | 196.7 | 264.1 | 212.9
1098 | 1009 | 196.4 | 263.8 | 212.6
1099 | 1010 | 196.2 | 263.4 | 212.3
1100 | 1011 | 196 | 263 | 212
1101 | 1012 | 195.7 | 262.6 | 211.8
1102 | 1013 | 195.4 | 262.2 | 211.5
1103 | 1014 | 195 | 261.8 | 211.2
1104 | 1015 | 194.7 | 261.5 | 210.9
1105 | 1016 | 194.4 | 261.1 | 210.7
1106 | 1017 | 194.1 | 260.7 | 210.4
1107 | 1018 | 193.8 | 260.3 | 210.1
1108 | 1019 | 193.5 | 259.9 | 209.8
1109 | 1020 | 193.3 | 259.6 | 209.6
1110 | 1021 | 193.1 | 259.2 | 209.3
1111 | 1022 | 192.9 | 258.8 | 209
1112 | 1023 | 192.6 | 258.4 | 208.8
1113 | 1024 | 192.4 | 258 | 208.5
1114 | 1025 | 192.2 | 257.6 | 208.2
1115 | 1026 | 192 | 257.3 | 208
1116 | 1027 | 191.8 | 256.9 | 207.7
1117 | 1028 | 191.6 | 256.5 | 207.4
1118 | 1029 | 191.4 | 256.1 | 207.1
1119 | 1030 | 191.2 | 255.8 | 206.8
1120 | 1031 | 191 | 255.4 | 206.6
1121 | 1032 | 190.8 | 255 | 206.3
1122 | 1033 | 190.5 | 254.7 | 206.1
1123 | 1034 | 190.3 | 254.3 | 205.8
1124 | 1035 | 190 | 254 | 205.5
1125 | 1036 | 189.7 | 253.6 | 205.3
1126 | 1037 | 189.5 | 253.3 | 205
1127 | 1038 | 189.4 | 252.9 | 204.8
1128 | 1039 | 189.3 | 252.6 | 204.5
1129 | 1040 | 189 | 252.2 | 204.3
1130 | 1041 | 188.8 | 251.8 | 204
1131 | 1042 | 188.6 | 251.5 | 203.8
1132 | 1043 | 188.4 | 251.1 | 203.5
1133 | 1044 | 188.2 | 250.8 | 203.2
1134 | 1045 | 188 | 250.4 | 203
1135 | 1046 | 187.9 | 250.1 | 202.7
1136 | 1047 | 187.7 | 249.7 | 202.5
1137 | 1048 | 187.5 | 249.4 | 202.3
1138 | 1049 | 187.3 | 249 | 202
1139 | 1050 | 187.1 | 248.7 | 201.7
1140 | 1051 | 186.9 | 248.3 | 201.5
1141 | 1052 | 186.7 | 248 | 201.3
1142 | 1053 | 186.5 | 247.6 | 201
1143 | 1054 | 186.3 | 247.3 | 200.8
1144 | 1055 | 186.1 | 247 | 200.5
1145 | 1056 | 185.9 | 246.6 | 200.3
1146 | 1057 | 185.7 | 246.3 | 200.1
1147 | 1058 | 185.5 | 245.9 | 199.8
1148 | 1059 | 185.3 | 245.6 | 199.6
1149 | 1060 | 185.1 | 245.3 | 199.3
1150 | 1061 | 184.9 | 244.9 | 199.1
1151 | 1062 | 184.7 | 244.6 | 198.8
1152 | 1063 | 184.5 | 244.2 | 198.6
1153 | 1064 | 184.3 | 243.9 | 198.4
1154 | 1065 | 184.1 | 243.5 | 198.2
1155 | 1066 | 183.9 | 241.8 | 200.5
1156 | 1067 | 183.7 | 241.5 | 200.4
1157 | 1068 | 183.6 | 241.1 | 200.1
1158 | 1069 | 183.4 | 240.8 | 199.9
1159 | 1070 | 183.2 | 240.5 | 199.6
1160 | 1071 | 183 | 240.1 | 199.4
1161 | 1072 | 182.8 | 239.8 | 199.2
1162 | 1073 | 182.5 | 239.5 | 198.9
1163 | 1074 | 182.3 | 239.1 | 198.7
1164 | 1075 | 182 | 238.8 | 198.4
1165 | 1076 | 181.7 | 238.5 | 198.2
1166 | 1077 | 181.4 | 238.1 | 198
1167 | 1078 | 181.1 | 237.8 | 197.7
1168 | 1079 | 180.8 | 237.5 | 197.5
1169 | 1080 | 180.6 | 237.1 | 197.3
1170 | 1081 | 180.3 | 236.8 | 197
1171 | 1082 | 180.1 | 236.5 | 196.8
1172 | 1083 | 179.8 | 236.1 | 196.5
1173 | 1084 | 179.6 | 235.8 | 196.3
1174 | 1085 | 179.5 | 235.5 | 196.1
1175 | 1086 | 179.4 | 235.2 | 195.8
1176 | 1087 | 179.1 | 234.8 | 195.6
1177 | 1088 | 179 | 234.5 | 195.3
1178 | 1089 | 178.9 | 234.2 | 195.1
1179 | 1090 | 178.8 | 233.9 | 194.9
1180 | 1091 | 178.6 | 233.6 | 194.6
1181 | 1092 | 178.5 | 233.3 | 194.4
1182 | 1093 | 178.4 | 233 | 194.2
1183 | 1094 | 178.2 | 232.7 | 193.9
1184 | 1095 | 178 | 232.4 | 193.7
1185 | 1096 | 177.8 | 232.1 | 193.5
1186 | 1097 | 177.6 | 231.8 | 193.3
1187 | 1098 | 177.4 | 231.5 | 193
1188 | 1099 | 177.2 | 231.2 | 192.8
1189 | 1100 | 177.1 | 230.9 | 192.6
1190 | 1101 | 176.9 | 230.6 | 192.3
1191 | 1102 | 176.7 | 230.3 | 192.1
1192 | 1103 | 176.6 | 230 | 191.9
1193 | 1104 | 176.4 | 229.7 | 191.6
1194 | 1105 | 176.2 | 229.4 | 191.4
1195 | 1106 | 176 | 229.1 | 191.2
1196 | 1107 | 175.8 | 228.8 | 191
1197 | 1108 | 175.6 | 228.5 | 190.8
1198 | 1109 | 175.4 | 228.2 | 190.6
1199 | 1110 | 175.2 | 227.9 | 190.3
1200 | 1111 | 175.1 | 227.6 | 190.1
1201 | 1112 | 174.9 | 227.3 | 189.9
1202 | 1113 | 174.7 | 227 | 189.7
1203 | 1114 | 174.5 | 226.7 | 189.4
1204 | 1115 | 174.3 | 226.3 | 189.2
1205 | 1116 | 174.2 | 226.1 | 189
1206 | 1117 | 174 | 225.8 | 188.8
1207 | 1118 | 173.8 | 225.5 | 188.5
1208 | 1119 | 173.6 | 225.2 | 188.3
1209 | 1120 | 173.4 | 224.9 | 188.1
1210 | 1121 | 173.3 | 224.6 | 187.9
1211 | 1122 | 173.1 | 224.3 | 187.7
1212 | 1123 | 172.8 | 224 | 187.4
1213 | 1124 | 172.5 | 223.7 | 187.2
1214 | 1125 | 172.3 | 223.4 | 187
1215 | 1126 | 172.1 | 223.1 | 186.8
1216 | 1127 | 171.9 | 222.8 | 186.5
1217 | 1128 | 171.8 | 222.5 | 186.3
1218 | 1129 | 171.6 | 222.3 | 186
1219 | 1130 | 171.4 | 222 | 185.8
1220 | 1131 | 171.2 | 221.7 | 185.6
1221 | 1132 | 171 | 221.4 | 185.4
1222 | 1133 | 170.8 | 221.1 | 185.2
1223 | 1134 | 170.7 | 220.8 | 185
1224 | 1135 | 170.5 | 220.5 | 184.8
1225 | 1136 | 170.3 | 220.3 | 184.6
1226 | 1137 | 170.1 | 220 | 184.3
1227 | 1138 | 170 | 219.7 | 184.1
1228 | 1139 | 169.8 | 219.4 | 183.9
1229 | 1140 | 169.5 | 219.1 | 183.7
1230 | 1141 | 169.3 | 218.8 | 183.5
1231 | 1142 | 169.1 | 218.6 | 183.3
1232 | 1143 | 168.8 | 218.3 | 183.1
1233 | 1144 | 168.6 | 218 | 182.9
1234 | 1145 | 168.4 | 217.7 | 182.7
1235 | 1146 | 168.2 | 217.4 | 182.4
1236 | 1147 | 168 | 217.2 | 182.2
1237 | 1148 | 167.7 | 216.9 | 182
1238 | 1149 | 167.5 | 216.6 | 181.8
1239 | 1150 | 167.3 | 216.3 | 181.6
1240 | 1151 | 167.1 | 216.1 | 181.4
1241 | 1152 | 167 | 215.8 | 181.2
1242 | 1153 | 166.8 | 215.5 | 180.9
1243 | 1154 | 166.7 | 215.2 | 180.7
1244 | 1155 | 166.6 | 215 | 180.5
1245 | 1156 | 166.4 | 214.7 | 180.3
1246 | 1157 | 166.3 | 214.4 | 180.1
1247 | 1158 | 166.2 | 214.2 | 179.9
1248 | 1159 | 166.1 | 213.9 | 179.7
1249 | 1160 | 165.9 | 213.6 | 179.5
1250 | 1161 | 165.7 | 213.4 | 179.3
1251 | 1162 | 165.4 | 213.1 | 179.1
1252 | 1163 | 165.2 | 212.8 | 178.9
1253 | 1164 | 165 | 212.6 | 178.7
1254 | 1165 | 164.7 | 212.3 | 178.5
1255 | 1166 | 164.5 | 212 | 178.3
1256 | 1167 | 164.3 | 211.7 | 178.1
1257 | 1168 | 164.1 | 211.4 | 177.9
1258 | 1169 | 163.9 | 211.1 | 177.7
1259 | 1170 | 163.7 | 210.9 | 177.5
1260 | 1171 | 163.5 | 210.6 | 177.3
1261 | 1172 | 163.3 | 210.3 | 177.1
1262 | 1173 | 163.2 | 210 | 176.9
1263 | 1174 | 163.1 | 209.7 | 176.7
1264 | 1175 | 162.9 | 209.5 | 176.5
1265 | 1176 | 162.8 | 209.2 | 176.3
1266 | 1177 | 162.6 | 208.9 | 176.2
1267 | 1178 | 162.4 | 208.7 | 176
1268 | 1179 | 162.3 | 208.4 | 175.8
1269 | 1180 | 162.2 | 208.1 | 175.6
1270 | 1181 | 162 | 207.9 | 175.4
1271 | 1182 | 161.9 | 207.6 | 175.2
1272 | 1183 | 161.7 | 207.4 | 175
1273 | 1184 | 161.6 | 207.1 | 174.8
1274 | 1185 | 161.4 | 206.8 | 174.6
1275 | 1186 | 161.3 | 206.6 | 174.5
1276 | 1187 | 161.2 | 206.3 | 174.3
1277 | 1188 | 161.1 | 206.1 | 174.1
1278 | 1189 | 161 | 205.8 | 173.9
1279 | 1190 | 160.8 | 205.5 | 173.7
1280 | 1191 | 160.7 | 205.3 | 173.5
1281 | 1192 | 160.5 | 205 | 173.3
1282 | 1193 | 160.3 | 204.7 | 173.1
1283 | 1194 | 160.2 | 204.5 | 172.9
1284 | 1195 | 160 | 204.2 | 172.7
1285 | 1196 | 159.8 | 204 | 172.6
1286 | 1197 | 159.5 | 203.7 | 172.4
1287 | 1198 | 159.3 | 203.4 | 172.2
1288 | 1199 | 159.1 | 203.2 | 172
1289 | 1200 | 158.9 | 202.9 | 171.8
1290 | 1201 | 158.7 | 202.7 | 171.6
1291 | 1202 | 158.5 | 202.4 | 171.4
1292 | 1203 | 158.3 | 202.1 | 171.2

## C6-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38925.4837 | 1 | 0 | 38925.4837 | 1 | 0 | -32.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4844 | 1 | 0 | 38925.4844 | 1 | 0 | 26.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4851 | 1 | 0 | 38925.4851 | 1 | 0 | 85 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4858 | 1 | 0 | 38925.4858 | 1 | 0 | 144 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4865 | 1 | 0 | 38925.4865 | 1 | 0 | 202.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4871 | 1 | 0 | 38925.4872 | 1 | 0 | 261.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4878 | 1 | 0 | 38925.4878 | 1 | 0 | 320.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4885 | 1 | 0 | 38925.4885 | 1 | 0 | 379 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4892 | 1 | 0 | 38925.4892 | 1 | 0 | 438 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4899 | 1 | 0 | 38925.4899 | 1 | 0 | 496.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4905 | 1 | 0 | 38925.4906 | 1 | 0 | 555.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4912 | 1 | 0 | 38925.4912 | 1 | 0 | 614.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4919 | 1 | 0 | 38925.4919 | 1 | 0 | 673 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4926 | 1 | 0 | 38925.4926 | 1 | 0 | 731.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4933 | 1 | 0 | 38925.4933 | 1 | 0 | 790.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4939 | 1 | 0 | 38925.494 | 1 | 0 | 849.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4946 | 1 | 0 | 38925.4946 | 1 | 0 | 908.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4953 | 1 | 0 | 38925.4953 | 1 | 0 | 967 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.496 | 1 | 0 | 38925.496 | 1 | 0 | 1025.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4967 | 1 | 0 | 38925.4967 | 1 | 0 | 1084.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4973 | 1 | 0 | 38925.4974 | 1 | 0 | 1143.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.498 | 1 | 0 | 38925.498 | 1 | 0 | 1202 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C5-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38925.4837 | 1 | 0 | 38925.4837 | 1 | 0 | -35.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4844 | 1 | 0 | 38925.4844 | 1 | 0 | 23.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4851 | 1 | 0 | 38925.4851 | 1 | 0 | 82.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4857 | 1 | 0 | 38925.4858 | 1 | 0 | 141 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4864 | 1 | 0 | 38925.4864 | 1 | 0 | 200 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4871 | 1 | 0 | 38925.4871 | 1 | 0 | 258.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4878 | 1 | 0 | 38925.4878 | 1 | 0 | 317.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4885 | 1 | 0 | 38925.4885 | 1 | 0 | 376.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4891 | 1 | 0 | 38925.4892 | 1 | 0 | 435 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4898 | 1 | 0 | 38925.4898 | 1 | 0 | 494 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4905 | 1 | 0 | 38925.4905 | 1 | 0 | 552.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4912 | 1 | 0 | 38925.4912 | 1 | 0 | 611.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4919 | 1 | 0 | 38925.4919 | 1 | 0 | 670.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4925 | 1 | 0 | 38925.4926 | 1 | 0 | 729 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4932 | 1 | 0 | 38925.4933 | 1 | 0 | 788 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4939 | 1 | 0 | 38925.4939 | 1 | 0 | 846.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4946 | 1 | 0 | 38925.4946 | 1 | 0 | 905.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4953 | 1 | 0 | 38925.4953 | 1 | 0 | 964 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4959 | 1 | 0 | 38925.496 | 1 | 0 | 1023 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4966 | 1 | 0 | 38925.4966 | 1 | 0 | 1081.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4973 | 1 | 0 | 38925.4973 | 1 | 0 | 1140.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.498 | 1 | 0 | 38925.498 | 1 | 0 | 1199.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C5-6
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38925.4837 | 1 | 0 | 38925.4837 | 1 | 0 | -38 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4844 | 1 | 0 | 38925.4844 | 1 | 0 | 20.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.485 | 1 | 0 | 38925.485 | 1 | 0 | 79.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4857 | 1 | 0 | 38925.4857 | 1 | 0 | 138.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4864 | 1 | 0 | 38925.4864 | 1 | 0 | 197 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4871 | 1 | 0 | 38925.4871 | 1 | 0 | 256 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4878 | 1 | 0 | 38925.4878 | 1 | 0 | 314.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4884 | 1 | 0 | 38925.4884 | 1 | 0 | 373.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4891 | 1 | 0 | 38925.4891 | 1 | 0 | 432.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4898 | 1 | 0 | 38925.4898 | 1 | 0 | 491 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4905 | 1 | 0 | 38925.4905 | 1 | 0 | 550 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4912 | 1 | 0 | 38925.4912 | 1 | 0 | 608.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4918 | 1 | 0 | 38925.4919 | 1 | 0 | 667.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4925 | 1 | 0 | 38925.4925 | 1 | 0 | 726 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4932 | 1 | 0 | 38925.4932 | 1 | 0 | 785 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4939 | 1 | 0 | 38925.4939 | 1 | 0 | 843.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4946 | 1 | 0 | 38925.4946 | 1 | 0 | 902.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4952 | 1 | 0 | 38925.4953 | 1 | 0 | 961.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4959 | 1 | 0 | 38925.4959 | 1 | 0 | 1020 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4966 | 1 | 0 | 38925.4966 | 1 | 0 | 1079 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4973 | 1 | 0 | 38925.4973 | 1 | 0 | 1137.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.498 | 1 | 0 | 38925.498 | 1 | 0 | 1196.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38925.4836 | 1 | 0 | 38925.4837 | 1 | 0 | -41 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4843 | 1 | 0 | 38925.4843 | 1 | 0 | 18 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.485 | 1 | 0 | 38925.485 | 1 | 0 | 76.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4857 | 1 | 0 | 38925.4857 | 1 | 0 | 135.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4864 | 1 | 0 | 38925.4864 | 1 | 0 | 194.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.487 | 1 | 0 | 38925.4871 | 1 | 0 | 253 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4877 | 1 | 0 | 38925.4877 | 1 | 0 | 312 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4884 | 1 | 0 | 38925.4884 | 1 | 0 | 370.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4891 | 1 | 0 | 38925.4891 | 1 | 0 | 429.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4898 | 1 | 0 | 38925.4898 | 2 | 0 | 488.5 | 577.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38925.4904 | 1 | 0 | 38925.4905 | 1 | 0 | 547 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4911 | 1 | 0 | 38925.4911 | 1 | 0 | 606 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4918 | 1 | 0 | 38925.4918 | 1 | 0 | 664.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4925 | 2 | 0 | 38925.4925 | 1 | 0 | 723.5 | 812.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.4932 | 1 | 0 | 38925.4932 | 1 | 0 | 782.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4938 | 1 | 0 | 38925.4939 | 1 | 0 | 841 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4945 | 1 | 0 | 38925.4945 | 1 | 0 | 900 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4952 | 1 | 0 | 38925.4952 | 1 | 0 | 958.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4959 | 1 | 0 | 38925.4959 | 1 | 0 | 1017.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4966 | 1 | 0 | 38925.4966 | 1 | 0 | 1076 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4972 | 1 | 0 | 38925.4973 | 1 | 0 | 1135 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4979 | 1 | 0 | 38925.4979 | 1 | 0 | 1193.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-6
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38925.4836 | 1 | 0 | 38925.4836 | 1 | 0 | -43.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4843 | 1 | 0 | 38925.4843 | 1 | 0 | 15 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.485 | 1 | 0 | 38925.485 | 1 | 0 | 74 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4856 | 1 | 0 | 38925.4857 | 1 | 0 | 132.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4863 | 1 | 0 | 38925.4863 | 1 | 0 | 191.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.487 | 1 | 0 | 38925.487 | 1 | 0 | 250.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4877 | 1 | 0 | 38925.4877 | 1 | 0 | 309 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4884 | 1 | 0 | 38925.4884 | 1 | 0 | 368 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4891 | 1 | 0 | 38925.4891 | 1 | 0 | 426.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4897 | 1 | 0 | 38925.4897 | 1 | 0 | 485.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4904 | 1 | 0 | 38925.4904 | 1 | 0 | 544.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4911 | 1 | 0 | 38925.4911 | 1 | 0 | 603 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4918 | 1 | 0 | 38925.4918 | 1 | 0 | 662 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4925 | 1 | 0 | 38925.4925 | 1 | 0 | 720.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4931 | 1 | 0 | 38925.4931 | 1 | 0 | 779.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4938 | 1 | 0 | 38925.4938 | 1 | 0 | 838.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4945 | 1 | 0 | 38925.4945 | 1 | 0 | 897 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4952 | 1 | 0 | 38925.4952 | 1 | 0 | 955.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4959 | 1 | 0 | 38925.4959 | 1 | 0 | 1014.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4965 | 1 | 0 | 38925.4966 | 1 | 0 | 1073.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4972 | 1 | 0 | 38925.4972 | 1 | 0 | 1132 | 1221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4979 | 1 | 0 | 38925.4979 | 1 | 0 | 1191 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C4-5
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38925.4836 | 1 | 0 | 38925.4836 | 1 | 0 | -46.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4843 | 1 | 0 | 38925.4843 | 1 | 0 | 12.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4849 | 1 | 0 | 38925.485 | 1 | 0 | 71 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4856 | 1 | 0 | 38925.4856 | 1 | 0 | 130 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4863 | 1 | 0 | 38925.4863 | 1 | 0 | 188.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.487 | 1 | 0 | 38925.487 | 1 | 0 | 247.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4877 | 1 | 0 | 38925.4877 | 1 | 0 | 306.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4883 | 1 | 0 | 38925.4884 | 1 | 0 | 365 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.489 | 1 | 0 | 38925.489 | 1 | 0 | 424 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4897 | 1 | 0 | 38925.4897 | 1 | 0 | 482.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4904 | 1 | 0 | 38925.4904 | 1 | 0 | 541.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4911 | 1 | 0 | 38925.4911 | 1 | 0 | 600.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4917 | 1 | 0 | 38925.4918 | 1 | 0 | 659 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4924 | 1 | 0 | 38925.4924 | 1 | 0 | 718 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4931 | 1 | 0 | 38925.4931 | 1 | 0 | 776.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4938 | 1 | 0 | 38925.4938 | 1 | 0 | 835.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4945 | 1 | 0 | 38925.4945 | 1 | 0 | 894 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4951 | 1 | 0 | 38925.4952 | 1 | 0 | 953 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4958 | 1 | 0 | 38925.4958 | 1 | 0 | 1011.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4965 | 1 | 0 | 38925.4965 | 1 | 0 | 1070.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4972 | 1 | 0 | 38925.4972 | 1 | 0 | 1129.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4979 | 1 | 0 | 38925.4979 | 1 | 0 | 1188 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38925.4835 | 1 | 0 | 38925.4836 | 1 | 0 | -49.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4842 | 1 | 0 | 38925.4842 | 1 | 0 | 9.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4849 | 1 | 0 | 38925.4849 | 1 | 0 | 68.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4856 | 1 | 0 | 38925.4856 | 1 | 0 | 127 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4863 | 1 | 0 | 38925.4863 | 1 | 0 | 186 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4869 | 1 | 0 | 38925.487 | 1 | 0 | 244.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4876 | 1 | 0 | 38925.4876 | 1 | 0 | 303.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4883 | 1 | 0 | 38925.4883 | 1 | 0 | 362.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.489 | 1 | 0 | 38925.489 | 1 | 0 | 421 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4897 | 1 | 0 | 38925.4897 | 1 | 0 | 479.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4903 | 1 | 0 | 38925.4904 | 1 | 0 | 538.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.491 | 1 | 0 | 38925.491 | 1 | 0 | 597.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4917 | 1 | 0 | 38925.4917 | 1 | 0 | 656.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4924 | 1 | 0 | 38925.4924 | 1 | 0 | 715 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4931 | 1 | 0 | 38925.4931 | 1 | 0 | 773.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4938 | 1 | 0 | 38925.4938 | 1 | 0 | 832.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4944 | 1 | 0 | 38925.4944 | 1 | 0 | 891.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4951 | 1 | 0 | 38925.4951 | 1 | 0 | 950 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4958 | 1 | 0 | 38925.4958 | 1 | 0 | 1009 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4965 | 1 | 0 | 38925.4965 | 1 | 0 | 1067.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4972 | 1 | 0 | 38925.4972 | 1 | 0 | 1126.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4978 | 1 | 0 | 38925.4978 | 1 | 0 | 1185.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-6
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38925.4835 | 1 | 0 | 38925.4835 | 1 | 0 | -52 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4842 | 1 | 0 | 38925.4842 | 1 | 0 | 6.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4849 | 1 | 0 | 38925.4849 | 1 | 0 | 65.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4856 | 1 | 0 | 38925.4856 | 1 | 0 | 124.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4862 | 1 | 0 | 38925.4863 | 1 | 0 | 183 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4869 | 1 | 0 | 38925.4869 | 1 | 0 | 242 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4876 | 1 | 0 | 38925.4876 | 1 | 0 | 300.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4883 | 1 | 0 | 38925.4883 | 1 | 0 | 359.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.489 | 1 | 0 | 38925.489 | 1 | 0 | 418.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4896 | 1 | 0 | 38925.4897 | 1 | 0 | 477 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4903 | 1 | 1 | 38925.4903 | 1 | 0 | 536 | 625 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.491 | 1 | 0 | 38925.491 | 1 | 0 | 594.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4917 | 1 | 0 | 38925.4917 | 1 | 0 | 653.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4924 | 1 | 0 | 38925.4924 | 1 | 0 | 712.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.493 | 1 | 0 | 38925.4931 | 1 | 0 | 771 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4937 | 1 | 0 | 38925.4937 | 1 | 0 | 830 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4944 | 1 | 0 | 38925.4944 | 1 | 0 | 888.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4951 | 1 | 0 | 38925.4951 | 1 | 0 | 947.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4958 | 1 | 0 | 38925.4958 | 1 | 0 | 1006 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4964 | 1 | 0 | 38925.4965 | 1 | 0 | 1065 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4971 | 1 | 0 | 38925.4971 | 1 | 0 | 1123.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4978 | 1 | 0 | 38925.4978 | 1 | 0 | 1182.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-5
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38925.4835 | 1 | 0 | 38925.4835 | 1 | 0 | -55 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4842 | 1 | 0 | 38925.4842 | 1 | 0 | 4 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4848 | 1 | 0 | 38925.4848 | 1 | 0 | 62.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4855 | 1 | 0 | 38925.4855 | 1 | 0 | 121.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4862 | 1 | 0 | 38925.4862 | 1 | 0 | 180.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4869 | 1 | 0 | 38925.4869 | 1 | 0 | 239 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4876 | 1 | 0 | 38925.4876 | 1 | 0 | 298 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4882 | 1 | 0 | 38925.4883 | 1 | 0 | 356.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4889 | 1 | 0 | 38925.4889 | 1 | 0 | 415.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4896 | 1 | 0 | 38925.4896 | 1 | 0 | 474 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4903 | 1 | 0 | 38925.4903 | 1 | 0 | 533 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.491 | 1 | 0 | 38925.491 | 1 | 0 | 592 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4916 | 1 | 0 | 38925.4917 | 1 | 0 | 650.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4923 | 1 | 0 | 38925.4923 | 1 | 0 | 709.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.493 | 1 | 0 | 38925.493 | 1 | 0 | 768.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4937 | 1 | 0 | 38925.4937 | 1 | 0 | 827 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4944 | 1 | 0 | 38925.4944 | 1 | 0 | 885.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.495 | 1 | 0 | 38925.4951 | 1 | 0 | 944.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4957 | 1 | 0 | 38925.4957 | 1 | 0 | 1003.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4964 | 1 | 0 | 38925.4964 | 1 | 0 | 1062 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4971 | 1 | 0 | 38925.4971 | 1 | 0 | 1121 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4978 | 1 | 0 | 38925.4978 | 1 | 0 | 1179.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C3-4
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38925.4834 | 1 | 0 | 38925.4835 | 1 | 0 | -57.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4841 | 1 | 0 | 38925.4841 | 1 | 0 | 1 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4848 | 1 | 0 | 38925.4848 | 1 | 0 | 60 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4855 | 1 | 0 | 38925.4855 | 1 | 0 | 118.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4862 | 1 | 0 | 38925.4862 | 1 | 0 | 177.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4869 | 1 | 0 | 38925.4869 | 1 | 0 | 236.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4875 | 1 | 0 | 38925.4875 | 1 | 0 | 295 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4882 | 1 | 0 | 38925.4882 | 1 | 0 | 354 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4889 | 1 | 0 | 38925.4889 | 1 | 0 | 412.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4896 | 1 | 0 | 38925.4896 | 1 | 0 | 471.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4902 | 1 | 0 | 38925.4903 | 1 | 0 | 530 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4909 | 1 | 0 | 38925.4909 | 1 | 0 | 589 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4916 | 1 | 0 | 38925.4916 | 1 | 0 | 648 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4923 | 1 | 0 | 38925.4923 | 1 | 0 | 706.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.493 | 1 | 0 | 38925.493 | 1 | 0 | 765.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4937 | 1 | 0 | 38925.4937 | 1 | 0 | 824.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4943 | 1 | 0 | 38925.4944 | 1 | 0 | 883 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.495 | 1 | 0 | 38925.495 | 1 | 0 | 942 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4957 | 1 | 0 | 38925.4957 | 1 | 0 | 1000.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4964 | 1 | 0 | 38925.4964 | 1 | 0 | 1059.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.497 | 1 | 0 | 38925.4971 | 1 | 0 | 1118 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4977 | 1 | 0 | 38925.4978 | 1 | 0 | 1177 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38925.4834 | 1 | 0 | 38925.4834 | 1 | 0 | -60.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4841 | 1 | 0 | 38925.4841 | 1 | 0 | -1.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4848 | 1 | 0 | 38925.4848 | 1 | 0 | 57 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4855 | 1 | 0 | 38925.4855 | 1 | 0 | 116 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4861 | 1 | 0 | 38925.4861 | 1 | 0 | 174.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4868 | 1 | 0 | 38925.4868 | 1 | 0 | 233.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4875 | 1 | 0 | 38925.4875 | 1 | 0 | 292.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4882 | 1 | 0 | 38925.4882 | 1 | 0 | 351 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4889 | 1 | 0 | 38925.4889 | 1 | 0 | 410 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4895 | 1 | 0 | 38925.4895 | 1 | 0 | 468.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4902 | 1 | 0 | 38925.4902 | 1 | 0 | 527.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4909 | 1 | 0 | 38925.4909 | 1 | 0 | 586.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4916 | 1 | 0 | 38925.4916 | 1 | 0 | 645 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4923 | 1 | 0 | 38925.4923 | 1 | 0 | 703.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4929 | 1 | 0 | 38925.493 | 1 | 0 | 762.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4936 | 1 | 0 | 38925.4936 | 1 | 0 | 821.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4943 | 1 | 0 | 38925.4943 | 1 | 0 | 880 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.495 | 1 | 0 | 38925.495 | 1 | 0 | 939 | 1028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4957 | 1 | 0 | 38925.4957 | 1 | 0 | 997.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4963 | 1 | 0 | 38925.4964 | 1 | 0 | 1056.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.497 | 1 | 0 | 38925.497 | 1 | 0 | 1115.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4977 | 1 | 0 | 38925.4977 | 1 | 0 | 1174 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-6
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38925.4834 | 1 | 0 | 38925.4834 | 1 | 0 | -63.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4841 | 1 | 0 | 38925.4841 | 1 | 0 | -4.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4847 | 1 | 0 | 38925.4848 | 1 | 0 | 54.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4854 | 1 | 0 | 38925.4854 | 1 | 0 | 113 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4861 | 1 | 0 | 38925.4861 | 1 | 0 | 172 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4868 | 1 | 0 | 38925.4868 | 1 | 0 | 230.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4875 | 1 | 0 | 38925.4875 | 1 | 0 | 289.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4881 | 1 | 0 | 38925.4882 | 1 | 0 | 348.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4888 | 1 | 0 | 38925.4888 | 1 | 0 | 407 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4895 | 1 | 0 | 38925.4895 | 1 | 0 | 466 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4902 | 1 | 0 | 38925.4902 | 1 | 0 | 524.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4909 | 1 | 0 | 38925.4909 | 1 | 0 | 583.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4916 | 1 | 0 | 38925.4916 | 1 | 0 | 642.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4922 | 1 | 0 | 38925.4922 | 1 | 0 | 701 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4929 | 1 | 0 | 38925.4929 | 1 | 0 | 760 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4936 | 1 | 0 | 38925.4936 | 1 | 0 | 818.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4943 | 1 | 0 | 38925.4943 | 1 | 0 | 877.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4949 | 1 | 0 | 38925.495 | 1 | 0 | 936 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4956 | 1 | 0 | 38925.4956 | 1 | 0 | 995 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4963 | 1 | 0 | 38925.4963 | 1 | 0 | 1053.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.497 | 1 | 0 | 38925.497 | 1 | 0 | 1112.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4977 | 1 | 0 | 38925.4977 | 1 | 0 | 1171.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-5
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38925.4833 | 1 | 0 | 38925.4834 | 1 | 0 | -66 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.484 | 3 | 0 | 38925.484 | 1 | 0 | -7.5 | 81.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 70334 | 211202 | 70333.9982
38925.4847 | 1 | 0 | 38925.4847 | 1 | 0 | 51.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4854 | 1 | 0 | 38925.4854 | 1 | 0 | 110.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4861 | 1 | 0 | 38925.4861 | 1 | 0 | 169 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4867 | 1 | 0 | 38925.4868 | 1 | 0 | 228 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4874 | 1 | 0 | 38925.4874 | 1 | 0 | 286.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4881 | 1 | 0 | 38925.4881 | 1 | 0 | 345.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4888 | 1 | 0 | 38925.4888 | 1 | 0 | 404.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4895 | 1 | 0 | 38925.4895 | 1 | 0 | 463 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4902 | 1 | 0 | 38925.4902 | 1 | 0 | 521.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4908 | 1 | 0 | 38925.4908 | 1 | 0 | 580.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4915 | 1 | 0 | 38925.4915 | 1 | 0 | 639.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4922 | 1 | 0 | 38925.4922 | 1 | 0 | 698 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4929 | 1 | 0 | 38925.4929 | 1 | 0 | 757 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4936 | 1 | 0 | 38925.4936 | 1 | 0 | 815.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4942 | 1 | 0 | 38925.4942 | 1 | 0 | 874.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4949 | 1 | 0 | 38925.4949 | 1 | 0 | 933.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4956 | 1 | 0 | 38925.4956 | 1 | 0 | 992 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4963 | 1 | 0 | 38925.4963 | 1 | 0 | 1051 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.497 | 1 | 0 | 38925.497 | 1 | 0 | 1109.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4976 | 1 | 0 | 38925.4977 | 1 | 0 | 1168.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-4
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38925.4833 | 1 | 0 | 38925.4833 | 1 | 0 | -69 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.484 | 1 | 0 | 38925.484 | 1 | 0 | -10 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4847 | 1 | 0 | 38925.4847 | 1 | 0 | 48.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4854 | 1 | 0 | 38925.4854 | 1 | 0 | 107.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.486 | 1 | 0 | 38925.4861 | 1 | 0 | 166.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4867 | 1 | 0 | 38925.4867 | 1 | 0 | 225 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4874 | 1 | 0 | 38925.4874 | 1 | 0 | 284 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4881 | 1 | 0 | 38925.4881 | 1 | 0 | 342.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4888 | 1 | 0 | 38925.4888 | 1 | 0 | 401.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4894 | 1 | 0 | 38925.4895 | 1 | 0 | 460 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4901 | 1 | 0 | 38925.4901 | 1 | 0 | 519 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4908 | 1 | 0 | 38925.4908 | 1 | 0 | 578 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4915 | 1 | 0 | 38925.4915 | 1 | 0 | 636.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4922 | 1 | 0 | 38925.4922 | 1 | 0 | 695.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4928 | 1 | 0 | 38925.4929 | 1 | 0 | 754.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4935 | 1 | 0 | 38925.4935 | 1 | 0 | 813 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4942 | 1 | 0 | 38925.4942 | 1 | 0 | 871.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38925.4949 | 1 | 0 | 931 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4956 | 1 | 0 | 38925.4956 | 1 | 0 | 989.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4962 | 1 | 0 | 38925.4963 | 1 | 0 | 1048 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4969 | 1 | 0 | 38925.4969 | 1 | 0 | 1107 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4976 | 1 | 0 | 38925.4976 | 1 | 0 | 1165.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-3
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38925.4833 | 1 | 1 | 38925.4833 | 1 | 0 | -71.5 | 17.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.484 | 1 | 0 | 38925.484 | 1 | 0 | -13 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4846 | 1 | 0 | 38925.4847 | 1 | 0 | 46 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4853 | 1 | 0 | 38925.4853 | 1 | 0 | 104.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.486 | 1 | 0 | 38925.486 | 1 | 0 | 163.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4867 | 1 | 0 | 38925.4867 | 1 | 0 | 222.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4874 | 1 | 0 | 38925.4874 | 1 | 0 | 281 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.488 | 1 | 0 | 38925.4881 | 1 | 0 | 340 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4887 | 1 | 1 | 38925.4887 | 1 | 0 | 398.5 | 487.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.4894 | 1 | 0 | 38925.4894 | 1 | 0 | 457.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4901 | 1 | 0 | 38925.4901 | 1 | 0 | 516.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4908 | 1 | 0 | 38925.4908 | 1 | 0 | 575 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4914 | 1 | 0 | 38925.4915 | 1 | 0 | 634 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4921 | 1 | 0 | 38925.4921 | 1 | 0 | 692.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4928 | 1 | 0 | 38925.4928 | 1 | 0 | 751.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4935 | 1 | 0 | 38925.4935 | 1 | 0 | 810.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4942 | 1 | 0 | 38925.4942 | 1 | 0 | 869 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4948 | 1 | 0 | 38925.4949 | 1 | 0 | 927.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4955 | 1 | 0 | 38925.4955 | 1 | 0 | 986.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4962 | 1 | 0 | 38925.4962 | 1 | 0 | 1045.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4969 | 1 | 0 | 38925.4969 | 1 | 0 | 1104 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4976 | 1 | 0 | 38925.4976 | 1 | 0 | 1163 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-7
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38925.4833 | 1 | 0 | 38925.4833 | 1 | 0 | -74.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4839 | 1 | 0 | 38925.4839 | 1 | 0 | -15.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4846 | 1 | 0 | 38925.4846 | 1 | 0 | 43 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4853 | 1 | 0 | 38925.4853 | 1 | 0 | 102 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.486 | 1 | 0 | 38925.486 | 1 | 0 | 160.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4867 | 1 | 0 | 38925.4867 | 1 | 0 | 219.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4873 | 1 | 0 | 38925.4873 | 1 | 0 | 278.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.488 | 1 | 0 | 38925.488 | 1 | 0 | 337 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4887 | 1 | 0 | 38925.4887 | 1 | 0 | 395.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4894 | 1 | 0 | 38925.4894 | 1 | 0 | 454.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4901 | 1 | 0 | 38925.4901 | 1 | 0 | 513.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4907 | 1 | 0 | 38925.4908 | 1 | 0 | 572 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4914 | 1 | 0 | 38925.4914 | 1 | 0 | 631 | 720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4921 | 1 | 0 | 38925.4921 | 1 | 0 | 690 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4928 | 1 | 0 | 38925.4928 | 1 | 0 | 748.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4935 | 1 | 0 | 38925.4935 | 1 | 0 | 807.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4941 | 1 | 0 | 38925.4942 | 1 | 0 | 866.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4948 | 1 | 0 | 38925.4948 | 1 | 0 | 925 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4955 | 1 | 0 | 38925.4955 | 1 | 0 | 983.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4962 | 1 | 0 | 38925.4962 | 1 | 0 | 1042.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4969 | 1 | 0 | 38925.4969 | 1 | 0 | 1101.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4975 | 1 | 0 | 38925.4976 | 1 | 0 | 1160 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-6
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38925.4832 | 1 | 0 | 38925.4832 | 1 | 0 | -77.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4839 | 1 | 0 | 38925.4839 | 1 | 0 | -18.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4846 | 1 | 0 | 38925.4846 | 1 | 0 | 40.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4853 | 1 | 0 | 38925.4853 | 1 | 0 | 99 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4859 | 1 | 0 | 38925.486 | 1 | 0 | 158 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4866 | 1 | 0 | 38925.4866 | 1 | 0 | 216.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4873 | 1 | 0 | 38925.4873 | 1 | 0 | 275.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.488 | 1 | 0 | 38925.488 | 1 | 0 | 334.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4887 | 1 | 0 | 38925.4887 | 1 | 0 | 393 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4893 | 1 | 0 | 38925.4894 | 1 | 0 | 451.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.49 | 1 | 0 | 38925.49 | 1 | 0 | 510.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4907 | 1 | 0 | 38925.4907 | 1 | 0 | 569.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4914 | 1 | 0 | 38925.4914 | 1 | 0 | 628.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4921 | 1 | 0 | 38925.4921 | 1 | 0 | 687 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4927 | 1 | 0 | 38925.4928 | 1 | 0 | 746 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4934 | 1 | 0 | 38925.4934 | 1 | 0 | 804.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4941 | 1 | 0 | 38925.4941 | 1 | 0 | 863.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4948 | 1 | 0 | 38925.4948 | 1 | 0 | 922 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4955 | 1 | 0 | 38925.4955 | 1 | 0 | 981 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4961 | 1 | 0 | 38925.4962 | 1 | 0 | 1039.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4968 | 1 | 0 | 38925.4968 | 1 | 0 | 1098.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4975 | 1 | 0 | 38925.4975 | 1 | 0 | 1157.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-5
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38925.4832 | 1 | 0 | 38925.4832 | 1 | 0 | -80 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4839 | 1 | 0 | 38925.4839 | 1 | 0 | -21.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4845 | 1 | 0 | 38925.4846 | 1 | 0 | 37.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4852 | 1 | 0 | 38925.4852 | 1 | 0 | 96.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4859 | 1 | 0 | 38925.4859 | 1 | 0 | 155 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4866 | 1 | 0 | 38925.4866 | 1 | 0 | 214 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4873 | 1 | 1 | 38925.4873 | 1 | 0 | 272.5 | 361.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38925.488 | 1 | 0 | 38925.488 | 1 | 0 | 331.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4886 | 1 | 0 | 38925.4886 | 1 | 0 | 390.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4893 | 1 | 0 |  | 1 | 0 | 448 | 537 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.49 | 1 | 0 | 38925.49 | 1 | 0 | 507.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4907 | 1 | 0 | 38925.4907 | 1 | 0 | 566.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4914 | 1 | 0 | 38925.4914 | 1 | 0 | 625.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.492 | 1 | 0 | 38925.492 | 1 | 0 | 684 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4927 | 1 | 0 | 38925.4927 | 1 | 0 | 743 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4934 | 1 | 0 | 38925.4934 | 1 | 0 | 801.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4941 | 1 | 0 | 38925.4941 | 1 | 0 | 860.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4948 | 1 | 0 | 38925.4948 | 1 | 0 | 919.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4954 | 1 | 0 | 38925.4955 | 1 | 0 | 978.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4961 | 1 | 0 | 38925.4961 | 1 | 0 | 1037 | 1126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4968 | 1 | 0 | 38925.4968 | 1 | 0 | 1095.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4975 | 1 | 0 | 38925.4975 | 1 | 0 | 1154.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-4
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38925.4831 | 1 | 0 | 38925.4832 | 1 | 0 | -83 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4838 | 1 | 0 | 38925.4839 | 1 | 0 | -24 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4845 | 1 | 0 | 38925.4845 | 1 | 0 | 34.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4852 | 1 | 0 | 38925.4852 | 1 | 0 | 93.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4859 | 1 | 0 | 38925.4859 | 1 | 0 | 152.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4866 | 1 | 0 | 38925.4866 | 1 | 0 | 211 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4872 | 1 | 0 | 38925.4873 | 1 | 0 | 270 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4879 | 1 | 0 | 38925.4879 | 1 | 0 | 328.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4886 | 1 | 0 | 38925.4886 | 1 | 0 | 387.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4893 | 1 | 0 | 38925.4893 | 1 | 0 | 446 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.49 | 1 | 0 | 38925.49 | 1 | 0 | 505 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4906 | 1 | 0 | 38925.4907 | 1 | 0 | 564 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4913 | 1 | 0 | 38925.4913 | 1 | 0 | 622.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.492 | 1 | 0 | 38925.492 | 1 | 0 | 681.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4927 | 1 | 0 | 38925.4927 | 1 | 0 | 740.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4934 | 1 | 0 | 38925.4934 | 1 | 0 | 799 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.494 | 1 | 0 | 38925.4941 | 1 | 0 | 857.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4947 | 1 | 0 | 38925.4947 | 1 | 0 | 916.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4954 | 1 | 0 | 38925.4954 | 1 | 0 | 975.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4961 | 1 | 0 | 38925.4961 | 1 | 0 | 1034 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4968 | 1 | 0 | 38925.4968 | 1 | 0 | 1093 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4974 | 1 | 0 | 38925.4975 | 1 | 0 | 1151.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-3
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38925.4831 | 1 | 0 | 38925.4831 | 1 | 0 | -85.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4838 | 1 | 0 | 38925.4838 | 1 | 0 | -27 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4845 | 2 | 0 | 38925.4845 | 1 | 0 | 32 | 121 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38925.4852 | 1 | 0 | 38925.4852 | 1 | 0 | 90.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4858 | 1 | 0 | 38925.4859 | 1 | 0 | 149.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4865 | 1 | 0 | 38925.4865 | 1 | 0 | 208.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4872 | 1 | 0 | 38925.4872 | 1 | 0 | 267 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4879 | 1 | 0 | 38925.4879 | 1 | 0 | 326 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4886 | 1 | 0 | 38925.4886 | 1 | 0 | 384.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4892 | 1 | 0 | 38925.4893 | 1 | 0 | 443.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4899 | 1 | 0 | 38925.4899 | 1 | 0 | 502.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4906 | 1 | 0 | 38925.4906 | 1 | 0 | 561 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4913 | 1 | 0 | 38925.4913 | 1 | 0 | 620 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.492 | 1 | 0 | 38925.492 | 1 | 0 | 678.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4927 | 1 | 0 | 38925.4927 | 1 | 0 | 737.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4933 | 1 | 0 | 38925.4933 | 1 | 0 | 796.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.494 | 1 | 0 | 38925.494 | 1 | 0 | 855 | 944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4947 | 1 | 0 | 38925.4947 | 1 | 0 | 914 | 1003 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4954 | 1 | 0 | 38925.4954 | 1 | 0 | 972.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4961 | 1 | 0 | 38925.4961 | 1 | 0 | 1031.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4967 | 1 | 0 | 38925.4967 | 1 | 0 | 1090 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4974 | 1 | 0 | 38925.4974 | 1 | 0 | 1149 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-2
Test 18 |  |  | 2006-07-27 | 11:37 |  | Vs = |  | 129 |  | R = | 100
SR | 7-C | Tray
700 C | 50.8 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38925.4831 | 1 | 0 | 38925.4831 | 1 | 0 | -88.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4838 | 1 | 0 | 38925.4838 | 1 | 0 | -29.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4844 | 1 | 0 |  | 1 | 0 | 28 | 117 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4851 | 1 | 0 | 38925.4852 | 1 | 0 | 88 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4858 | 1 | 0 | 38925.4858 | 1 | 0 | 146.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4865 | 1 | 0 | 38925.4865 | 1 | 0 | 205.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4872 | 1 | 0 | 38925.4872 | 1 | 0 | 264.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4878 | 1 | 0 | 38925.4879 | 1 | 0 | 323 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4885 | 1 | 0 | 38925.4886 | 1 | 0 | 382 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4892 | 1 | 0 | 38925.4892 | 1 | 0 | 440.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4899 | 1 | 0 | 38925.4899 | 1 | 0 | 499.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4906 | 1 | 0 | 38925.4906 | 1 | 0 | 558.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4912 | 1 | 0 | 38925.4913 | 1 | 0 | 617 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4919 | 1 | 0 | 38925.4919 | 1 | 0 | 675.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4926 | 1 | 0 | 38925.4926 | 1 | 0 | 734.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4933 | 1 | 0 | 38925.4933 | 1 | 0 | 793.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.494 | 1 | 0 | 38925.494 | 1 | 0 | 852 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4947 | 1 | 0 | 38925.4947 | 1 | 0 | 911 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4953 | 1 | 0 | 38925.4953 | 1 | 0 | 969.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.496 | 1 | 0 | 38925.496 | 1 | 0 | 1028.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4967 | 1 | 0 | 38925.4967 | 1 | 0 | 1087.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38925.4974 | 1 | 0 | 38925.4974 | 1 | 0 | 1146 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Test 18 |  |  | 2006-07-27 | 11:37
38925.4831 | 1 | 0 | 1 | SR | 7-C | Tray
38925.4838 | 1 | 0 | 1 | 700 C | 50.8 kW/m2 |  | Conductors
38925.4844 | 1 | 0 | 1
38925.4851 | 1 | 0 | 1
38925.4858 | 1 | 0 | 1
38925.4865 | 1 | 0 | 1
38925.4872 | 1 | 0 | 1
38925.4878 | 1 | 0 | 1
38925.4885 | 1 | 0 | 1
38925.4892 | 1 | 0 | 1
38925.4899 | 1 | 0 | 1
38925.4906 | 1 | 0 | 1
38925.4912 | 1 | 0 | 1
38925.4919 | 1 | 0 | 1
38925.4926 | 1 | 0 | 1
38925.4933 | 1 | 0 | 1
38925.494 | 1 | 0 | 1
38925.4947 | 1 | 0 | 1
38925.4953 | 1 | 0 | 1
38925.496 | 1 | 0 | 1
38925.4967 | 1 | 0 | 1
38925.4974 | 1 | 0 | 1
1
38925.4831 | 1 | 0 | 2
38925.4838 | 1 | 0 | 2
38925.4852 | 1 | 0 | 2
38925.4858 | 1 | 0 | 2
38925.4865 | 1 | 0 | 2
38925.4872 | 1 | 0 | 2
38925.4879 | 1 | 0 | 2
38925.4886 | 1 | 0 | 2
38925.4892 | 1 | 0 | 2
38925.4899 | 1 | 0 | 2
38925.4906 | 1 | 0 | 2
38925.4913 | 1 | 0 | 2
38925.4919 | 1 | 0 | 2
38925.4926 | 1 | 0 | 2
38925.4933 | 1 | 0 | 2
38925.494 | 1 | 0 | 2
38925.4947 | 1 | 0 | 2
38925.4953 | 1 | 0 | 2
38925.496 | 1 | 0 | 2
38925.4967 | 1 | 0 | 2
38925.4974 | 1 | 0 | 2
2
38925.4831 | 1 | 0 | 3
38925.4838 | 1 | 0 | 3
38925.4845 | 2 | 0 | 3
38925.4852 | 1 | 0 | 3
38925.4858 | 1 | 0 | 3
38925.4865 | 1 | 0 | 3
38925.4872 | 1 | 0 | 3
38925.4879 | 1 | 0 | 3
38925.4886 | 1 | 0 | 3
38925.4892 | 1 | 0 | 3
38925.4899 | 1 | 0 | 3
38925.4906 | 1 | 0 | 3
38925.4913 | 1 | 0 | 3
38925.492 | 1 | 0 | 3
38925.4927 | 1 | 0 | 3
38925.4933 | 1 | 0 | 3
38925.494 | 1 | 0 | 3
38925.4947 | 1 | 0 | 3
38925.4954 | 1 | 0 | 3
38925.4961 | 1 | 0 | 3
38925.4967 | 1 | 0 | 3
38925.4974 | 1 | 0 | 3
3
38925.4831 | 1 | 0 | 4
38925.4838 | 1 | 0 | 4
38925.4845 | 1 | 0 | 4
38925.4852 | 1 | 0 | 4
38925.4859 | 1 | 0 | 4
38925.4865 | 1 | 0 | 4
38925.4872 | 1 | 0 | 4
38925.4879 | 1 | 0 | 4
38925.4886 | 1 | 0 | 4
38925.4893 | 1 | 0 | 4
38925.4899 | 1 | 0 | 4
38925.4906 | 1 | 0 | 4
38925.4913 | 1 | 0 | 4
38925.492 | 1 | 0 | 4
38925.4927 | 1 | 0 | 4
38925.4933 | 1 | 0 | 4
38925.494 | 1 | 0 | 4
38925.4947 | 1 | 0 | 4
38925.4954 | 1 | 0 | 4
38925.4961 | 1 | 0 | 4
38925.4967 | 1 | 0 | 4
38925.4974 | 1 | 0 | 4
4
38925.4831 | 1 | 0 | 5
38925.4838 | 1 | 0 | 5
38925.4845 | 1 | 0 | 5
38925.4852 | 1 | 0 | 5
38925.4859 | 1 | 0 | 5
38925.4866 | 1 | 0 | 5
38925.4872 | 1 | 0 | 5
38925.4879 | 1 | 0 | 5
38925.4886 | 1 | 0 | 5
38925.4893 | 1 | 0 | 5
38925.49 | 1 | 0 | 5
38925.4906 | 1 | 0 | 5
38925.4913 | 1 | 0 | 5
38925.492 | 1 | 0 | 5
38925.4927 | 1 | 0 | 5
38925.4934 | 1 | 0 | 5
38925.494 | 1 | 0 | 5
38925.4947 | 1 | 0 | 5
38925.4954 | 1 | 0 | 5
38925.4961 | 1 | 0 | 5
38925.4968 | 1 | 0 | 5
38925.4974 | 1 | 0 | 5
5
38925.4832 | 1 | 0 | 6
38925.4839 | 1 | 0 | 6
38925.4845 | 1 | 0 | 6
38925.4852 | 1 | 0 | 6
38925.4859 | 1 | 0 | 6
38925.4866 | 1 | 0 | 6
38925.4873 | 1 | 0 | 6
38925.4879 | 1 | 0 | 6
38925.4886 | 1 | 0 | 6
38925.4893 | 1 | 0 | 6
38925.49 | 1 | 0 | 6
38925.4907 | 1 | 0 | 6
38925.4913 | 1 | 0 | 6
38925.492 | 1 | 0 | 6
38925.4927 | 1 | 0 | 6
38925.4934 | 1 | 0 | 6
38925.4941 | 1 | 0 | 6
38925.4947 | 1 | 0 | 6
38925.4954 | 1 | 0 | 6
38925.4961 | 1 | 0 | 6
38925.4968 | 1 | 0 | 6
38925.4975 | 1 | 0 | 6
6
38925.4832 | 1 | 0 | 7
38925.4839 | 1 | 0 | 7
38925.4845 | 1 | 0 | 7
38925.4852 | 1 | 0 | 7
38925.4859 | 1 | 0 | 7
38925.4866 | 1 | 0 | 7
38925.4873 | 1 | 1 | 7
38925.488 | 1 | 0 | 7
38925.4886 | 1 | 0 | 7
38925.4893 | 1 | 0 | 7
38925.49 | 1 | 0 | 7
38925.4907 | 1 | 0 | 7
38925.4914 | 1 | 0 | 7
38925.492 | 1 | 0 | 7
38925.4927 | 1 | 0 | 7
38925.4934 | 1 | 0 | 7
38925.4941 | 1 | 0 | 7
38925.4948 | 1 | 0 | 7
38925.4954 | 1 | 0 | 7
38925.4961 | 1 | 0 | 7
38925.4968 | 1 | 0 | 7
38925.4975 | 1 | 0 | 7
7
38925.4832 | 1 | 0 | 8
38925.4839 | 1 | 0 | 8
38925.4846 | 1 | 0 | 8
38925.4852 | 1 | 0 | 8
38925.4859 | 1 | 0 | 8
38925.4866 | 1 | 0 | 8
38925.4873 | 1 | 0 | 8
38925.488 | 1 | 0 | 8
38925.4886 | 1 | 0 | 8
38925.49 | 1 | 0 | 8
38925.4907 | 1 | 0 | 8
38925.4914 | 1 | 0 | 8
38925.492 | 1 | 0 | 8
38925.4927 | 1 | 0 | 8
38925.4934 | 1 | 0 | 8
38925.4941 | 1 | 0 | 8
38925.4948 | 1 | 0 | 8
38925.4955 | 1 | 0 | 8
38925.4961 | 1 | 0 | 8
38925.4968 | 1 | 0 | 8
38925.4975 | 1 | 0 | 8
8
38925.4832 | 1 | 0 | 9
38925.4839 | 1 | 0 | 9
38925.4846 | 1 | 0 | 9
38925.4853 | 1 | 0 | 9
38925.4859 | 1 | 0 | 9
38925.4866 | 1 | 0 | 9
38925.4873 | 1 | 0 | 9
38925.488 | 1 | 0 | 9
38925.4887 | 1 | 0 | 9
38925.4893 | 1 | 0 | 9
38925.49 | 1 | 0 | 9
38925.4907 | 1 | 0 | 9
38925.4914 | 1 | 0 | 9
38925.4921 | 1 | 0 | 9
38925.4927 | 1 | 0 | 9
38925.4934 | 1 | 0 | 9
38925.4941 | 1 | 0 | 9
38925.4948 | 1 | 0 | 9
38925.4955 | 1 | 0 | 9
38925.4961 | 1 | 0 | 9
38925.4968 | 1 | 0 | 9
38925.4975 | 1 | 0 | 9
9
38925.4832 | 1 | 0 | 10
38925.4839 | 1 | 0 | 10
38925.4846 | 1 | 0 | 10
38925.4853 | 1 | 0 | 10
38925.486 | 1 | 0 | 10
38925.4866 | 1 | 0 | 10
38925.4873 | 1 | 0 | 10
38925.488 | 1 | 0 | 10
38925.4887 | 1 | 0 | 10
38925.4894 | 1 | 0 | 10
38925.49 | 1 | 0 | 10
38925.4907 | 1 | 0 | 10
38925.4914 | 1 | 0 | 10
38925.4921 | 1 | 0 | 10
38925.4928 | 1 | 0 | 10
38925.4934 | 1 | 0 | 10
38925.4941 | 1 | 0 | 10
38925.4948 | 1 | 0 | 10
38925.4955 | 1 | 0 | 10
38925.4962 | 1 | 0 | 10
38925.4968 | 1 | 0 | 10
38925.4975 | 1 | 0 | 10
10
38925.4833 | 1 | 0 | 11
38925.4839 | 1 | 0 | 11
38925.4846 | 1 | 0 | 11
38925.4853 | 1 | 0 | 11
38925.486 | 1 | 0 | 11
38925.4867 | 1 | 0 | 11
38925.4873 | 1 | 0 | 11
38925.488 | 1 | 0 | 11
38925.4887 | 1 | 0 | 11
38925.4894 | 1 | 0 | 11
38925.4901 | 1 | 0 | 11
38925.4907 | 1 | 0 | 11
38925.4914 | 1 | 0 | 11
38925.4921 | 1 | 0 | 11
38925.4928 | 1 | 0 | 11
38925.4935 | 1 | 0 | 11
38925.4941 | 1 | 0 | 11
38925.4948 | 1 | 0 | 11
38925.4955 | 1 | 0 | 11
38925.4962 | 1 | 0 | 11
38925.4969 | 1 | 0 | 11
38925.4975 | 1 | 0 | 11
11
38925.4833 | 1 | 0 | 12
38925.4839 | 1 | 0 | 12
38925.4846 | 1 | 0 | 12
38925.4853 | 1 | 0 | 12
38925.486 | 1 | 0 | 12
38925.4867 | 1 | 0 | 12
38925.4873 | 1 | 0 | 12
38925.488 | 1 | 0 | 12
38925.4887 | 1 | 0 | 12
38925.4894 | 1 | 0 | 12
38925.4901 | 1 | 0 | 12
38925.4908 | 1 | 0 | 12
38925.4914 | 1 | 0 | 12
38925.4921 | 1 | 0 | 12
38925.4928 | 1 | 0 | 12
38925.4935 | 1 | 0 | 12
38925.4942 | 1 | 0 | 12
38925.4948 | 1 | 0 | 12
38925.4955 | 1 | 0 | 12
38925.4962 | 1 | 0 | 12
38925.4969 | 1 | 0 | 12
38925.4976 | 1 | 0 | 12
12
38925.4833 | 1 | 1 | 13
38925.484 | 1 | 0 | 13
38925.4846 | 1 | 0 | 13
38925.4853 | 1 | 0 | 13
38925.486 | 1 | 0 | 13
38925.4867 | 1 | 0 | 13
38925.4874 | 1 | 0 | 13
38925.488 | 1 | 0 | 13
38925.4887 | 1 | 1 | 13
38925.4894 | 1 | 0 | 13
38925.4901 | 1 | 0 | 13
38925.4908 | 1 | 0 | 13
38925.4914 | 1 | 0 | 13
38925.4921 | 1 | 0 | 13
38925.4928 | 1 | 0 | 13
38925.4935 | 1 | 0 | 13
38925.4942 | 1 | 0 | 13
38925.4948 | 1 | 0 | 13
38925.4955 | 1 | 0 | 13
38925.4962 | 1 | 0 | 13
38925.4969 | 1 | 0 | 13
38925.4976 | 1 | 0 | 13
13
38925.4833 | 1 | 0 | 14
38925.484 | 1 | 0 | 14
38925.4847 | 1 | 0 | 14
38925.4853 | 1 | 0 | 14
38925.486 | 1 | 0 | 14
38925.4867 | 1 | 0 | 14
38925.4874 | 1 | 0 | 14
38925.4881 | 1 | 0 | 14
38925.4887 | 1 | 0 | 14
38925.4894 | 1 | 0 | 14
38925.4901 | 1 | 0 | 14
38925.4908 | 1 | 0 | 14
38925.4915 | 1 | 0 | 14
38925.4921 | 1 | 0 | 14
38925.4928 | 1 | 0 | 14
38925.4935 | 1 | 0 | 14
38925.4942 | 1 | 0 | 14
38925.4949 | 1 | 0 | 14
38925.4955 | 1 | 0 | 14
38925.4962 | 1 | 0 | 14
38925.4969 | 1 | 0 | 14
38925.4976 | 1 | 0 | 14
14
38925.4833 | 1 | 0 | 15
38925.484 | 1 | 0 | 15
38925.4847 | 1 | 0 | 15
38925.4854 | 1 | 0 | 15
38925.486 | 1 | 0 | 15
38925.4867 | 1 | 0 | 15
38925.4874 | 1 | 0 | 15
38925.4881 | 1 | 0 | 15
38925.4888 | 1 | 0 | 15
38925.4894 | 1 | 0 | 15
38925.4901 | 1 | 0 | 15
38925.4908 | 1 | 0 | 15
38925.4915 | 1 | 0 | 15
38925.4922 | 1 | 0 | 15
38925.4928 | 1 | 0 | 15
38925.4935 | 1 | 0 | 15
38925.4942 | 1 | 0 | 15
38925.4956 | 1 | 0 | 15
38925.4962 | 1 | 0 | 15
38925.4969 | 1 | 0 | 15
38925.4976 | 1 | 0 | 15
15
38925.4833 | 1 | 0 | 16
38925.484 | 1 | 0 | 16
38925.4847 | 1 | 0 | 16
38925.4854 | 1 | 0 | 16
38925.4861 | 1 | 0 | 16
38925.4867 | 1 | 0 | 16
38925.4874 | 1 | 0 | 16
38925.4881 | 1 | 0 | 16
38925.4888 | 1 | 0 | 16
38925.4895 | 1 | 0 | 16
38925.4901 | 1 | 0 | 16
38925.4908 | 1 | 0 | 16
38925.4915 | 1 | 0 | 16
38925.4922 | 1 | 0 | 16
38925.4929 | 1 | 0 | 16
38925.4935 | 1 | 0 | 16
38925.4942 | 1 | 0 | 16
38925.4949 | 1 | 0 | 16
38925.4956 | 1 | 0 | 16
38925.4963 | 1 | 0 | 16
38925.4969 | 1 | 0 | 16
38925.4976 | 1 | 0 | 16
16
38925.4833 | 1 | 0 | 17
38925.484 | 3 | 0 | 17
38925.4847 | 1 | 0 | 17
38925.4854 | 1 | 0 | 17
38925.4861 | 1 | 0 | 17
38925.4867 | 1 | 0 | 17
38925.4874 | 1 | 0 | 17
38925.4881 | 1 | 0 | 17
38925.4888 | 1 | 0 | 17
38925.4895 | 1 | 0 | 17
38925.4902 | 1 | 0 | 17
38925.4908 | 1 | 0 | 17
38925.4915 | 1 | 0 | 17
38925.4922 | 1 | 0 | 17
38925.4929 | 1 | 0 | 17
38925.4936 | 1 | 0 | 17
38925.4942 | 1 | 0 | 17
38925.4949 | 1 | 0 | 17
38925.4956 | 1 | 0 | 17
38925.4963 | 1 | 0 | 17
38925.497 | 1 | 0 | 17
38925.4976 | 1 | 0 | 17
17
38925.4834 | 1 | 0 | 18
38925.484 | 1 | 0 | 18
38925.4847 | 1 | 0 | 18
38925.4854 | 1 | 0 | 18
38925.4861 | 1 | 0 | 18
38925.4868 | 1 | 0 | 18
38925.4874 | 1 | 0 | 18
38925.4881 | 1 | 0 | 18
38925.4888 | 1 | 0 | 18
38925.4895 | 1 | 0 | 18
38925.4902 | 1 | 0 | 18
38925.4908 | 1 | 0 | 18
38925.4915 | 1 | 0 | 18
38925.4922 | 1 | 0 | 18
38925.4929 | 1 | 0 | 18
38925.4936 | 1 | 0 | 18
38925.4942 | 1 | 0 | 18
38925.4949 | 1 | 0 | 18
38925.4956 | 1 | 0 | 18
38925.4963 | 1 | 0 | 18
38925.497 | 1 | 0 | 18
38925.4977 | 1 | 0 | 18
18
38925.4834 | 1 | 0 | 19
38925.4841 | 1 | 0 | 19
38925.4847 | 1 | 0 | 19
38925.4854 | 1 | 0 | 19
38925.4861 | 1 | 0 | 19
38925.4868 | 1 | 0 | 19
38925.4875 | 1 | 0 | 19
38925.4881 | 1 | 0 | 19
38925.4888 | 1 | 0 | 19
38925.4895 | 1 | 0 | 19
38925.4902 | 1 | 0 | 19
38925.4909 | 1 | 0 | 19
38925.4916 | 1 | 0 | 19
38925.4922 | 1 | 0 | 19
38925.4929 | 1 | 0 | 19
38925.4936 | 1 | 0 | 19
38925.4943 | 1 | 0 | 19
38925.4949 | 1 | 0 | 19
38925.4956 | 1 | 0 | 19
38925.4963 | 1 | 0 | 19
38925.497 | 1 | 0 | 19
38925.4977 | 1 | 0 | 19
19
38925.4834 | 1 | 0 | 20
38925.4841 | 1 | 0 | 20
38925.4848 | 1 | 0 | 20
38925.4854 | 1 | 0 | 20
38925.4861 | 1 | 0 | 20
38925.4868 | 1 | 0 | 20
38925.4875 | 1 | 0 | 20
38925.4882 | 1 | 0 | 20
38925.4888 | 1 | 0 | 20
38925.4895 | 1 | 0 | 20
38925.4902 | 1 | 0 | 20
38925.4909 | 1 | 0 | 20
38925.4916 | 1 | 0 | 20
38925.4922 | 1 | 0 | 20
38925.4929 | 1 | 0 | 20
38925.4936 | 1 | 0 | 20
38925.4943 | 1 | 0 | 20
38925.495 | 1 | 0 | 20
38925.4956 | 1 | 0 | 20
38925.4963 | 1 | 0 | 20
38925.497 | 1 | 0 | 20
38925.4977 | 1 | 0 | 20
20
38925.4834 | 1 | 0 | 21
38925.4841 | 1 | 0 | 21
38925.4848 | 1 | 0 | 21
38925.4855 | 1 | 0 | 21
38925.4861 | 1 | 0 | 21
38925.4868 | 1 | 0 | 21
38925.4875 | 1 | 0 | 21
38925.4882 | 1 | 0 | 21
38925.4889 | 1 | 0 | 21
38925.4895 | 1 | 0 | 21
38925.4902 | 1 | 0 | 21
38925.4909 | 1 | 0 | 21
38925.4916 | 1 | 0 | 21
38925.4923 | 1 | 0 | 21
38925.4929 | 1 | 0 | 21
38925.4936 | 1 | 0 | 21
38925.4943 | 1 | 0 | 21
38925.495 | 1 | 0 | 21
38925.4957 | 1 | 0 | 21
38925.4963 | 1 | 0 | 21
38925.497 | 1 | 0 | 21
38925.4977 | 1 | 0 | 21
21
38925.4834 | 1 | 0 | 22
38925.4841 | 1 | 0 | 22
38925.4848 | 1 | 0 | 22
38925.4855 | 1 | 0 | 22
38925.4861 | 1 | 0 | 22
38925.4868 | 1 | 0 | 22
38925.4875 | 1 | 0 | 22
38925.4882 | 1 | 0 | 22
38925.4889 | 1 | 0 | 22
38925.4895 | 1 | 0 | 22
38925.4902 | 1 | 0 | 22
38925.4909 | 1 | 0 | 22
38925.4916 | 1 | 0 | 22
38925.4923 | 1 | 0 | 22
38925.493 | 1 | 0 | 22
38925.4936 | 1 | 0 | 22
38925.4943 | 1 | 0 | 22
38925.495 | 1 | 0 | 22
38925.4957 | 1 | 0 | 22
38925.4964 | 1 | 0 | 22
38925.497 | 1 | 0 | 22
38925.4977 | 1 | 0 | 22
22
38925.4834 | 1 | 0 | 23
38925.4841 | 1 | 0 | 23
38925.4848 | 1 | 0 | 23
38925.4855 | 1 | 0 | 23
38925.4862 | 1 | 0 | 23
38925.4869 | 1 | 0 | 23
38925.4875 | 1 | 0 | 23
38925.4882 | 1 | 0 | 23
38925.4889 | 1 | 0 | 23
38925.4896 | 1 | 0 | 23
38925.4902 | 1 | 0 | 23
38925.4909 | 1 | 0 | 23
38925.4916 | 1 | 0 | 23
38925.4923 | 1 | 0 | 23
38925.493 | 1 | 0 | 23
38925.4937 | 1 | 0 | 23
38925.4943 | 1 | 0 | 23
38925.495 | 1 | 0 | 23
38925.4957 | 1 | 0 | 23
38925.4964 | 1 | 0 | 23
38925.497 | 1 | 0 | 23
38925.4977 | 1 | 0 | 23
23
38925.4835 | 1 | 0 | 24
38925.4841 | 1 | 0 | 24
38925.4848 | 1 | 0 | 24
38925.4855 | 1 | 0 | 24
38925.4862 | 1 | 0 | 24
38925.4869 | 1 | 0 | 24
38925.4875 | 1 | 0 | 24
38925.4882 | 1 | 0 | 24
38925.4889 | 1 | 0 | 24
38925.4896 | 1 | 0 | 24
38925.4903 | 1 | 0 | 24
38925.4909 | 1 | 0 | 24
38925.4916 | 1 | 0 | 24
38925.4923 | 1 | 0 | 24
38925.493 | 1 | 0 | 24
38925.4937 | 1 | 0 | 24
38925.4944 | 1 | 0 | 24
38925.495 | 1 | 0 | 24
38925.4957 | 1 | 0 | 24
38925.4964 | 1 | 0 | 24
38925.4971 | 1 | 0 | 24
38925.4978 | 1 | 0 | 24
24
38925.4835 | 1 | 0 | 25
38925.4842 | 1 | 0 | 25
38925.4848 | 1 | 0 | 25
38925.4855 | 1 | 0 | 25
38925.4862 | 1 | 0 | 25
38925.4869 | 1 | 0 | 25
38925.4876 | 1 | 0 | 25
38925.4882 | 1 | 0 | 25
38925.4889 | 1 | 0 | 25
38925.4896 | 1 | 0 | 25
38925.4903 | 1 | 0 | 25
38925.491 | 1 | 0 | 25
38925.4916 | 1 | 0 | 25
38925.4923 | 1 | 0 | 25
38925.493 | 1 | 0 | 25
38925.4937 | 1 | 0 | 25
38925.4944 | 1 | 0 | 25
38925.495 | 1 | 0 | 25
38925.4957 | 1 | 0 | 25
38925.4964 | 1 | 0 | 25
38925.4971 | 1 | 0 | 25
38925.4978 | 1 | 0 | 25
25
38925.4835 | 1 | 0 | 26
38925.4842 | 1 | 0 | 26
38925.4848 | 1 | 0 | 26
38925.4855 | 1 | 0 | 26
38925.4862 | 1 | 0 | 26
38925.4869 | 1 | 0 | 26
38925.4876 | 1 | 0 | 26
38925.4883 | 1 | 0 | 26
38925.4889 | 1 | 0 | 26
38925.4896 | 1 | 0 | 26
38925.4903 | 1 | 0 | 26
38925.491 | 1 | 0 | 26
38925.4917 | 1 | 0 | 26
38925.4923 | 1 | 0 | 26
38925.493 | 1 | 0 | 26
38925.4937 | 1 | 0 | 26
38925.4944 | 1 | 0 | 26
38925.4951 | 1 | 0 | 26
38925.4957 | 1 | 0 | 26
38925.4964 | 1 | 0 | 26
38925.4971 | 1 | 0 | 26
38925.4978 | 1 | 0 | 26
26
38925.4835 | 1 | 0 | 27
38925.4842 | 1 | 0 | 27
38925.4849 | 1 | 0 | 27
38925.4856 | 1 | 0 | 27
38925.4862 | 1 | 0 | 27
38925.4869 | 1 | 0 | 27
38925.4876 | 1 | 0 | 27
38925.4883 | 1 | 0 | 27
38925.489 | 1 | 0 | 27
38925.4896 | 1 | 0 | 27
38925.4903 | 1 | 1 | 27
38925.491 | 1 | 0 | 27
38925.4917 | 1 | 0 | 27
38925.4924 | 1 | 0 | 27
38925.493 | 1 | 0 | 27
38925.4937 | 1 | 0 | 27
38925.4944 | 1 | 0 | 27
38925.4951 | 1 | 0 | 27
38925.4958 | 1 | 0 | 27
38925.4964 | 1 | 0 | 27
38925.4971 | 1 | 0 | 27
38925.4978 | 1 | 0 | 27
27
38925.4835 | 1 | 0 | 28
38925.4842 | 1 | 0 | 28
38925.4849 | 1 | 0 | 28
38925.4856 | 1 | 0 | 28
38925.4863 | 1 | 0 | 28
38925.4869 | 1 | 0 | 28
38925.4876 | 1 | 0 | 28
38925.4883 | 1 | 0 | 28
38925.489 | 1 | 0 | 28
38925.4897 | 1 | 0 | 28
38925.4903 | 1 | 0 | 28
38925.491 | 1 | 0 | 28
38925.4917 | 1 | 0 | 28
38925.4924 | 1 | 0 | 28
38925.4931 | 1 | 0 | 28
38925.4937 | 1 | 0 | 28
38925.4944 | 1 | 0 | 28
38925.4951 | 1 | 0 | 28
38925.4958 | 1 | 0 | 28
38925.4965 | 1 | 0 | 28
38925.4971 | 1 | 0 | 28
38925.4978 | 1 | 0 | 28
28
38925.4835 | 1 | 0 | 29
38925.4842 | 1 | 0 | 29
38925.4849 | 1 | 0 | 29
38925.4856 | 1 | 0 | 29
38925.4863 | 1 | 0 | 29
38925.4869 | 1 | 0 | 29
38925.4876 | 1 | 0 | 29
38925.4883 | 1 | 0 | 29
38925.489 | 1 | 0 | 29
38925.4897 | 1 | 0 | 29
38925.4903 | 1 | 0 | 29
38925.491 | 1 | 0 | 29
38925.4917 | 1 | 0 | 29
38925.4924 | 1 | 0 | 29
38925.4931 | 1 | 0 | 29
38925.4938 | 1 | 0 | 29
38925.4944 | 1 | 0 | 29
38925.4951 | 1 | 0 | 29
38925.4958 | 1 | 0 | 29
38925.4965 | 1 | 0 | 29
38925.4972 | 1 | 0 | 29
38925.4978 | 1 | 0 | 29
29
38925.4836 | 1 | 0 | 30
38925.4842 | 1 | 0 | 30
38925.4849 | 1 | 0 | 30
38925.4856 | 1 | 0 | 30
38925.4863 | 1 | 0 | 30
38925.487 | 1 | 0 | 30
38925.4876 | 1 | 0 | 30
38925.4883 | 1 | 0 | 30
38925.489 | 1 | 0 | 30
38925.4897 | 1 | 0 | 30
38925.4904 | 1 | 0 | 30
38925.491 | 1 | 0 | 30
38925.4917 | 1 | 0 | 30
38925.4924 | 1 | 0 | 30
38925.4931 | 1 | 0 | 30
38925.4938 | 1 | 0 | 30
38925.4944 | 1 | 0 | 30
38925.4951 | 1 | 0 | 30
38925.4958 | 1 | 0 | 30
38925.4965 | 1 | 0 | 30
38925.4972 | 1 | 0 | 30
38925.4978 | 1 | 0 | 30
30
38925.4836 | 1 | 0 | 31
38925.4843 | 1 | 0 | 31
38925.4849 | 1 | 0 | 31
38925.4856 | 1 | 0 | 31
38925.4863 | 1 | 0 | 31
38925.487 | 1 | 0 | 31
38925.4877 | 1 | 0 | 31
38925.4883 | 1 | 0 | 31
38925.489 | 1 | 0 | 31
38925.4897 | 1 | 0 | 31
38925.4904 | 1 | 0 | 31
38925.4911 | 1 | 0 | 31
38925.4917 | 1 | 0 | 31
38925.4924 | 1 | 0 | 31
38925.4931 | 1 | 0 | 31
38925.4938 | 1 | 0 | 31
38925.4945 | 1 | 0 | 31
38925.4951 | 1 | 0 | 31
38925.4958 | 1 | 0 | 31
38925.4965 | 1 | 0 | 31
38925.4972 | 1 | 0 | 31
38925.4979 | 1 | 0 | 31
31
38925.4836 | 1 | 0 | 32
38925.4843 | 1 | 0 | 32
38925.485 | 1 | 0 | 32
38925.4856 | 1 | 0 | 32
38925.4863 | 1 | 0 | 32
38925.487 | 1 | 0 | 32
38925.4877 | 1 | 0 | 32
38925.4884 | 1 | 0 | 32
38925.489 | 1 | 0 | 32
38925.4897 | 1 | 0 | 32
38925.4904 | 1 | 0 | 32
38925.4911 | 1 | 0 | 32
38925.4918 | 1 | 0 | 32
38925.4924 | 1 | 0 | 32
38925.4931 | 1 | 0 | 32
38925.4938 | 1 | 0 | 32
38925.4945 | 1 | 0 | 32
38925.4952 | 1 | 0 | 32
38925.4958 | 1 | 0 | 32
38925.4965 | 1 | 0 | 32
38925.4972 | 1 | 0 | 32
38925.4979 | 1 | 0 | 32
32
38925.4836 | 1 | 0 | 33
38925.4843 | 1 | 0 | 33
38925.485 | 1 | 0 | 33
38925.4856 | 1 | 0 | 33
38925.4863 | 1 | 0 | 33
38925.487 | 1 | 0 | 33
38925.4877 | 1 | 0 | 33
38925.4884 | 1 | 0 | 33
38925.4891 | 1 | 0 | 33
38925.4897 | 1 | 0 | 33
38925.4904 | 1 | 0 | 33
38925.4911 | 1 | 0 | 33
38925.4918 | 1 | 0 | 33
38925.4925 | 1 | 0 | 33
38925.4931 | 1 | 0 | 33
38925.4938 | 1 | 0 | 33
38925.4945 | 1 | 0 | 33
38925.4952 | 1 | 0 | 33
38925.4959 | 1 | 0 | 33
38925.4965 | 1 | 0 | 33
38925.4972 | 1 | 0 | 33
38925.4979 | 1 | 0 | 33
33
38925.4836 | 1 | 0 | 34
38925.4843 | 1 | 0 | 34
38925.485 | 1 | 0 | 34
38925.4857 | 1 | 0 | 34
38925.4863 | 1 | 0 | 34
38925.487 | 1 | 0 | 34
38925.4877 | 1 | 0 | 34
38925.4884 | 1 | 0 | 34
38925.4891 | 1 | 1 | 34
38925.4897 | 1 | 0 | 34
38925.4904 | 1 | 0 | 34
38925.4911 | 1 | 0 | 34
38925.4918 | 1 | 0 | 34
38925.4925 | 1 | 0 | 34
38925.4931 | 1 | 0 | 34
38925.4938 | 1 | 0 | 34
38925.4945 | 1 | 0 | 34
38925.4952 | 1 | 0 | 34
38925.4959 | 1 | 0 | 34
38925.4966 | 1 | 0 | 34
38925.4972 | 1 | 0 | 34
38925.4979 | 1 | 0 | 34
34
38925.4836 | 1 | 0 | 35
38925.4843 | 1 | 0 | 35
38925.485 | 1 | 0 | 35
38925.4857 | 1 | 0 | 35
38925.4864 | 1 | 0 | 35
38925.487 | 1 | 0 | 35
38925.4877 | 1 | 0 | 35
38925.4884 | 1 | 0 | 35
38925.4891 | 1 | 0 | 35
38925.4898 | 1 | 0 | 35
38925.4904 | 1 | 0 | 35
38925.4911 | 1 | 0 | 35
38925.4918 | 1 | 0 | 35
38925.4925 | 2 | 0 | 35
38925.4932 | 1 | 0 | 35
38925.4938 | 1 | 0 | 35
38925.4945 | 1 | 0 | 35
38925.4952 | 1 | 0 | 35
38925.4959 | 1 | 0 | 35
38925.4966 | 1 | 0 | 35
38925.4972 | 1 | 0 | 35
38925.4979 | 1 | 0 | 35
35
38925.4837 | 1 | 0 | 36
38925.4843 | 1 | 0 | 36
38925.485 | 1 | 0 | 36
38925.4857 | 1 | 0 | 36
38925.4864 | 1 | 0 | 36
38925.4871 | 1 | 0 | 36
38925.4877 | 1 | 0 | 36
38925.4884 | 1 | 0 | 36
38925.4891 | 1 | 0 | 36
38925.4898 | 2 | 0 | 36
38925.4905 | 1 | 0 | 36
38925.4911 | 1 | 0 | 36
38925.4918 | 1 | 0 | 36
38925.4925 | 1 | 0 | 36
38925.4932 | 1 | 0 | 36
38925.4939 | 1 | 0 | 36
38925.4945 | 1 | 0 | 36
38925.4952 | 1 | 0 | 36
38925.4959 | 1 | 0 | 36
38925.4966 | 1 | 0 | 36
38925.4973 | 1 | 0 | 36
38925.4979 | 1 | 0 | 36
36
38925.4837 | 1 | 0 | 37
38925.4844 | 1 | 0 | 37
38925.485 | 1 | 0 | 37
38925.4857 | 1 | 0 | 37
38925.4864 | 1 | 0 | 37
38925.4871 | 1 | 0 | 37
38925.4878 | 1 | 0 | 37
38925.4884 | 1 | 0 | 37
38925.4891 | 1 | 0 | 37
38925.4898 | 1 | 0 | 37
38925.4905 | 1 | 0 | 37
38925.4912 | 1 | 0 | 37
38925.4918 | 1 | 0 | 37
38925.4925 | 1 | 0 | 37
38925.4932 | 1 | 0 | 37
38925.4939 | 1 | 0 | 37
38925.4946 | 1 | 0 | 37
38925.4952 | 1 | 0 | 37
38925.4959 | 1 | 0 | 37
38925.4966 | 1 | 0 | 37
38925.4973 | 1 | 0 | 37
38925.498 | 1 | 0 | 37
37
38925.4837 | 1 | 0 | 38
38925.4844 | 1 | 0 | 38
38925.485 | 1 | 0 | 38
38925.4857 | 1 | 0 | 38
38925.4864 | 1 | 0 | 38
38925.4871 | 1 | 0 | 38
38925.4878 | 1 | 0 | 38
38925.4884 | 1 | 0 | 38
38925.4891 | 1 | 0 | 38
38925.4898 | 1 | 0 | 38
38925.4905 | 1 | 0 | 38
38925.4912 | 1 | 0 | 38
38925.4919 | 1 | 0 | 38
38925.4925 | 1 | 0 | 38
38925.4932 | 1 | 0 | 38
38925.4939 | 1 | 0 | 38
38925.4946 | 1 | 0 | 38
38925.4953 | 1 | 0 | 38
38925.4959 | 1 | 0 | 38
38925.4966 | 1 | 0 | 38
38925.4973 | 1 | 0 | 38
38925.498 | 1 | 0 | 38
38
38925.4837 | 1 | 0 | 39
38925.4844 | 1 | 0 | 39
38925.4851 | 1 | 0 | 39
38925.4857 | 1 | 0 | 39
38925.4864 | 1 | 0 | 39
38925.4871 | 1 | 0 | 39
38925.4878 | 1 | 0 | 39
38925.4885 | 1 | 0 | 39
38925.4891 | 1 | 0 | 39
38925.4898 | 1 | 0 | 39
38925.4905 | 1 | 0 | 39
38925.4912 | 1 | 0 | 39
38925.4919 | 1 | 0 | 39
38925.4925 | 1 | 0 | 39
38925.4932 | 1 | 0 | 39
38925.4939 | 1 | 0 | 39
38925.4946 | 1 | 0 | 39
38925.4953 | 1 | 0 | 39
38925.4959 | 1 | 0 | 39
38925.4966 | 1 | 0 | 39
38925.4973 | 1 | 0 | 39
38925.498 | 1 | 0 | 39
39
38925.4837 | 1 | 0 | 40
38925.4844 | 1 | 0 | 40
38925.4851 | 1 | 0 | 40
38925.4858 | 1 | 0 | 40
38925.4864 | 1 | 0 | 40
38925.4871 | 1 | 0 | 40
38925.4878 | 1 | 0 | 40
38925.4885 | 1 | 0 | 40
38925.4892 | 1 | 0 | 40
38925.4898 | 1 | 0 | 40
38925.4905 | 1 | 0 | 40
38925.4912 | 1 | 0 | 40
38925.4919 | 1 | 0 | 40
38925.4926 | 1 | 0 | 40
38925.4933 | 1 | 0 | 40
38925.4939 | 1 | 0 | 40
38925.4946 | 1 | 0 | 40
38925.4953 | 1 | 0 | 40
38925.496 | 1 | 0 | 40
38925.4966 | 1 | 0 | 40
38925.4973 | 1 | 0 | 40
38925.498 | 1 | 0 | 40
40
38925.4837 | 1 | 0 | 41
38925.4844 | 1 | 0 | 41
38925.4851 | 1 | 0 | 41
38925.4858 | 1 | 0 | 41
38925.4865 | 1 | 0 | 41
38925.4871 | 1 | 0 | 41
38925.4878 | 1 | 0 | 41
38925.4885 | 1 | 0 | 41
38925.4892 | 1 | 0 | 41
38925.4899 | 1 | 0 | 41
38925.4905 | 1 | 0 | 41
38925.4912 | 1 | 0 | 41
38925.4919 | 1 | 0 | 41
38925.4926 | 1 | 0 | 41
38925.4933 | 1 | 0 | 41
38925.4939 | 1 | 0 | 41
38925.4946 | 1 | 0 | 41
38925.4953 | 1 | 0 | 41
38925.496 | 1 | 0 | 41
38925.4967 | 1 | 0 | 41
38925.4973 | 1 | 0 | 41
38925.498 | 1 | 0 | 41
41
38925.4837 | 1 | 0 | 42
38925.4844 | 1 | 0 | 42
38925.4851 | 1 | 0 | 42
38925.4858 | 1 | 0 | 42
38925.4865 | 1 | 0 | 42
38925.4872 | 1 | 0 | 42
38925.4878 | 1 | 0 | 42
38925.4885 | 1 | 0 | 42
38925.4892 | 1 | 0 | 42
38925.4899 | 1 | 0 | 42
38925.4906 | 1 | 0 | 42
38925.4912 | 1 | 0 | 42
38925.4919 | 1 | 0 | 42
38925.4926 | 1 | 0 | 42
38925.4933 | 1 | 0 | 42
38925.494 | 1 | 0 | 42
38925.4946 | 1 | 0 | 42
38925.4953 | 1 | 0 | 42
38925.496 | 1 | 0 | 42
38925.4967 | 1 | 0 | 42
38925.4974 | 1 | 0 | 42
38925.498 | 1 | 0 | 42
42