## Test Facts
Last row in IRMS data sheets: | 35
Time when Penlight power was initiated: | 94

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 29
Test conditions: Cable: 7-conductor, 12 AWG, PE insulated, PVC jacketed, General Cable control cable (Cable Item #15). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: None. Cables were run horizontally through the Penlight chamber ("air drop" configuration) and secured to the raceway support brackets outside of the chamber; chamber end walls were closed and un-heated. Exposure conditions: Shroud set to temperature of 325C, nominal 7.2 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 94 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
94 | 0 | Initated Penlight Heating
939 | 845 | Conductors 6 & 7 short together at less than 100 ohms (23)
942-956 | 848-862 | Conductor 1 shorts to conductors 2, 3, 4, 6 & 7 at less than 100 ohms (8, <1, 21, 1 & 8)
949 | 855 | Conductor 1 shorts to ground (2) | Uncertain path to ground
959-970 | 865-876 | Conductor 2 shorts to conductors 3, 4, 6 & 7 at less than 100 ohms (12, 16, 21 & 5)
960-973 | 866-879 | Conductors 2, 3 & 4 all short to ground (49, 2, 116) | Uncertain paths to ground; unstable ground fault conditions
973-981 | 879-887 | Conductor 3 shorts to conductors 4, 6 & 7 at less than 100 ohms (2, 24 & 6)
979-981 | 885-887 | Conductors 6 & 7 short to ground (5 & 146) | Uncertain paths to ground; unstable ground fault conditions
987-989 | 893-895 | Conductor 4 shorts to conductors 6 & 7 at less than 100 ohms (17 & 11)
1034-1054 | 940-960 | Conductor 5 shorts to conductors 3, 4, 6 & 7 at less than 100 ohms (17, 1, 14 & <1)
1035 | 941 | Conductor 5 shorts to ground (10) | Uncertain of path to ground; unstable ground fault condition
1068-1082 | 974-988 | Conductor 5 shorts to conductors 1 & 2 at less than 100 ohms (3 & 12) | All cable conductors are shorted together
1349 | 1255 | Power to Penlight is shutoff
Additional Observations
Observation 1 | It took 845 seconds (14.1 min.) from the start of Penlight heating for the first shorting failure to occur.
Observation 2 | Although short to ground failures are indicated, it is uncertain what the paths to ground could have been.
Observation 3 | The cables did not ignite or burn during this test run. Nevertheless, damage to the cables was observed.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 29 |  |  | 2006-08-01 | 14:23
PE | 7-C | Air Drop
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-93 | 211201.9994 | -90.5 | 211201.9994 | -87.5 | 211201.9994 | -84.5 | 211201.9994 | -82 | 211201.9994 | -79 | 211201.9994 | -76.5 | 211201.9994 | -73.5 | 211201.9994 | -70.5 | 211201.9994 | -68 | 211201.9994 | -65 | 211201.9994 | -62.5 | 211201.9994 | -59.5 | 211201.9994 | -56.5 | 211201.9994 | -54 | 211201.9994 | -51 | 211201.9994 | -48.5 | 211201.9994 | -45.5 | 211201.9994 | -42.5 | 211201.9994 | -40 | 211201.9994 | -37 | 211201.9994 | -93 | 211201.9994
-34.5 | 211201.9994 | -31.5 | 211201.9994 | -28.5 | 211201.9994 | -26 | 211201.9994 | -23 | 211201.9994 | -20.5 | 211201.9994 | -17.5 | 211201.9994 | -14.5 | 211201.9994 | -12 | 211201.9994 | -9 | 211201.9994 | -6.5 | 211201.9994 | -3.5 | 211201.9994 | -0.5 | 211201.9994 | 2 | 211201.9994 | 5 | 211201.9994 | 7.5 | 211201.9994 | 10.5 | 211201.9994 | 13.5 | 211201.9994 | 16 | 211002.0947 | 19 | 211201.9994 | 21.5 | 211201.9994 | -34.5 | 211002.0947
24.5 | 211201.9994 | 27.5 | 211201.9994 | 31 | 211201.9994 | 33 | 211201.9994 | 35.5 | 211201.9994 | 38.5 | 211201.9994 | 41.5 | 211201.9994 | 44 | 211201.9994 | 47 | 211201.9994 | 49.5 | 211201.9994 | 52.5 | 211201.9994 | 55.5 | 211201.9994 | 58 | 211201.9994 | 61 | 211201.9994 | 63.5 | 211201.9994 | 66.5 | 211201.9994 | 69.5 | 211201.9994 | 72 | 211201.9994 | 75 | 211201.9994 | 77.5 | 211201.9994 | 80.5 | 211201.9994 | 24.5 | 211201.9994
83.5 | 211201.9994 | 86 | 211201.9994 | 89 | 211201.9994 | 91.5 | 211201.9994 | 94.5 | 211201.9994 | 97.5 | 211201.9994 | 100 | 211201.9994 | 103 | 211201.9994 | 105.5 | 211201.9994 | 108.5 | 211201.9994 | 111.5 | 211201.9994 | 114 | 211201.9994 | 117 | 211201.9994 | 119.5 | 211201.9994 | 122.5 | 211201.9994 | 125.5 | 211201.9994 | 128 | 211201.9994 | 131 | 211201.9994 | 133.5 | 211201.9994 | 136.5 | 211201.9994 | 139.5 | 211201.9994 | 83.5 | 211201.9994
142 | 211201.9994 | 145 | 211201.9994 | 147.5 | 211201.9994 | 150.5 | 211201.9994 | 153.5 | 211201.9994 | 156 | 211201.9994 | 159 | 211201.9994 | 161.5 | 211201.9994 | 164.5 | 211201.9994 | 167.5 | 211201.9994 | 170 | 211201.9994 | 173 | 211201.9994 | 175.5 | 211201.9994 | 178.5 | 211201.9994 | 181.5 | 211201.9994 | 184 | 211201.9994 | 187 | 211201.9994 | 189.5 | 211201.9994 | 192.5 | 211201.9994 | 195.5 | 211201.9994 | 198 | 211201.9994 | 142 | 211201.9994
201 | 211201.9994 | 203.5 | 211201.9994 | 206.5 | 211201.9994 | 209.5 | 211201.9994 | 212 | 211201.9994 | 214.5 | 211201.9994 | 217.5 | 211201.9994 | 220.5 | 211201.9994 | 223.5 | 211201.9994 | 226 | 211201.9994 | 229 | 211201.9994 | 231.5 | 211201.9994 | 234.5 | 211201.9994 | 237.5 | 211201.9994 | 240 | 211201.9994 | 243 | 211201.9994 | 245.5 | 211201.9994 | 248.5 | 211201.9994 | 251.5 | 211201.9994 | 254 | 211201.9994 | 257 | 211201.9994 | 201 | 211201.9994
259.5 | 211201.9994 | 262.5 | 211201.9994 | 265.5 | 105550.9988 | 268 | 211201.9994 | 271 | 211201.9994 | 273.5 | 211201.9994 | 276.5 | 211201.9994 | 279.5 | 211201.9994 | 282 | 211201.9994 | 285 | 211201.9994 | 287.5 | 211201.9994 | 290.5 | 211201.9994 | 293.5 | 211201.9994 | 296 | 211201.9994 | 299 | 211201.9994 | 301.5 | 211201.9994 | 304.5 | 211201.9994 | 307.5 | 211201.9994 | 310 | 211201.9994 | 313 | 211201.9994 | 315.5 | 211201.9994 | 259.5 | 105550.9988
318.5 | 211201.9994 | 321.5 | 211201.9994 | 324 | 211201.9994 | 326.5 | 211201.9994 | 329.5 | 211201.9994 | 332.5 | 211201.9994 | 335.5 | 211201.9994 | 338 | 211201.9994 | 341 | 211201.9994 | 343.5 | 211201.9994 | 346.5 | 211201.9994 | 349 | 211201.9994 | 352 | 211201.9994 | 354.5 | 211201.9994 | 357.5 | 211201.9994 | 360.5 | 211201.9994 | 363.5 | 211201.9994 | 366 | 211201.9994 | 369 | 211201.9994 | 371.5 | 211201.9994 | 374.5 | 211201.9994 | 318.5 | 211201.9994
377.5 | 211201.9994 | 380 | 211201.9994 | 383 | 211201.9994 | 385.5 | 211201.9994 | 388.5 | 211201.9994 | 391.5 | 211201.9994 | 394 | 211201.9994 | 396.5 | 211201.9994 | 399.5 | 211201.9994 | 402.5 | 211201.9994 | 405.5 | 211201.9994 | 408 | 211201.9994 | 410.5 | 211201.9994 | 413.5 | 211201.9994 | 416.5 | 211201.9994 | 419 | 211201.9994 | 422 | 211201.9994 | 425 | 211201.9994 | 427.5 | 211201.9994 | 430.5 | 211201.9994 | 433.5 | 211201.9994 | 377.5 | 211201.9994
436 | 211201.9994 | 439 | 211201.9994 | 441.5 | 211201.9994 | 444.5 | 211201.9994 | 447.5 | 211201.9994 | 450 | 211201.9994 | 453 | 211201.9994 | 455.5 | 211201.9994 | 458.5 | 211201.9994 | 461.5 | 211201.9994 | 464 | 211201.9994 | 467 | 211201.9994 | 469.5 | 211201.9994 | 472.5 | 211201.9994 | 475.5 | 211201.9994 | 478 | 211201.9994 | 481 | 211201.9994 | 483.5 | 211201.9994 | 486.5 | 211201.9994 | 489.5 | 211201.9994 | 492 | 211201.9994 | 436 | 211201.9994
495 | 211201.9994 | 497.5 | 211201.9994 | 500.5 | 211201.9994 | 503.5 | 211201.9994 | 506 | 211201.9994 | 509 | 211201.9994 | 511.5 | 211201.9994 | 514.5 | 211201.9994 | 517 | 211201.9994 | 520 | 211201.9994 | 522.5 | 211201.9994 | 525.5 | 211201.9994 | 528.5 | 211201.9994 | 531.5 | 211201.9994 | 534 | 211201.9994 | 536.5 | 211201.9994 | 539.5 | 211201.9994 | 542.5 | 211201.9994 | 545.5 | 211201.9994 | 548 | 211201.9994 | 551 | 211201.9994 | 495 | 211201.9994
553.5 | 211201.9994 | 556.5 | 211201.9994 | 559 | 211201.9994 | 562 | 211201.9994 | 565 | 211201.9994 | 567.5 | 211201.9994 | 570.5 | 211201.9994 | 573 | 211201.9994 | 576 | 211201.9994 | 578.5 | 211201.9994 | 581.5 | 211201.9994 | 584.5 | 211201.9994 | 587 | 211201.9994 | 590 | 211201.9994 | 592.5 | 211201.9994 | 595.5 | 211201.9994 | 598.5 | 211201.9994 | 601.5 | 211201.9994 | 604 | 211201.9994 | 606.5 | 211201.9994 | 609.5 | 211201.9994 | 553.5 | 211201.9994
612.5 | 211201.9994 | 615.5 | 211201.9994 | 618 | 211201.9994 | 620.5 | 211201.9994 | 623.5 | 211201.9994 | 626.5 | 211201.9994 | 629.5 | 211201.9994 | 632 | 211201.9994 | 634.5 | 211201.9994 | 637.5 | 211201.9994 | 640.5 | 211201.9994 | 643 | 211201.9994 | 646 | 211201.9994 | 648.5 | 211201.9994 | 651.5 | 211201.9994 | 654.5 | 211201.9994 | 657 | 211201.9994 | 660 | 211201.9994 | 663 | 211201.9994 | 665.5 | 211201.9994 | 668.5 | 211201.9994 | 612.5 | 211201.9994
671.5 | 211201.9994 | 674 | 211201.9994 | 677 | 211201.9994 | 679.5 | 211201.9994 | 682.5 | 211201.9994 | 685 | 211201.9994 | 688 | 211201.9994 | 690.5 | 211201.9994 | 693.5 | 211201.9994 | 696.5 | 211201.9994 | 699.5 | 211201.9994 | 702 | 211201.9994 | 705 | 211201.9994 | 707.5 | 211201.9994 | 710.5 | 211201.9994 | 713.5 | 211002.0947 | 716 | 211201.9994 | 718.5 | 211201.9994 | 721.5 | 211201.9994 | 724.5 | 211201.9994 | 727 | 211201.9994 | 671.5 | 211002.0947
730 | 211201.9994 | 732.5 | 211201.9994 | 735.5 | 211201.9994 | 738.5 | 211201.9994 | 741 | 211201.9994 | 744 | 211201.9994 | 746.5 | 211201.9994 | 749.5 | 211201.9994 | 752.5 | 211201.9994 | 755 | 211201.9994 | 758 | 211201.9994 | 760.5 | 211201.9994 | 763.5 | 211201.9994 | 766.5 | 211201.9994 | 769 | 211201.9994 | 772 | 211201.9994 | 774.5 | 211201.9994 | 777.5 | 211201.9994 | 780.5 | 211201.9994 | 783 | 211201.9994 | 786 | 211201.9994 | 730 | 211201.9994
788.5 | 211201.9994 | 791.5 | 211201.9994 | 794.5 | 211201.9994 | 797 | 211201.9994 | 800 | 211201.9994 | 802.5 | 211201.9994 | 805.5 | 211201.9994 | 808.5 | 211201.9994 | 811 | 211201.9994 | 814 | 211201.9994 | 816.5 | 211201.9994 | 819.5 | 211201.9994 | 822.5 | 211201.9994 | 825 | 211201.9994 | 828 | 211201.9994 | 831 | 211201.9994 | 833.5 | 211201.9994 | 836.5 | 211201.9994 | 839.5 | 211201.9994 | 842 | 211201.9994 | 844.5 | 22.5332 | 788.5 | 22.5332
847.5 | 8.3281 | 850.5 | 0.092758 | 853 | 21.3046 | 856 | 5527.6501 | 858.5 | 1.1449 | 861.5 | 7.8252 | 864.5 | 11.7059 | 867.5 | 16.0631 | 870.5 | 5369.5452 | 872.5 | 20.7499 | 875.5 | 4.8602 | 878.5 | 2.0099 | 881 | 5093.8636 | 884 | 23.9553 | 886.5 | 5.6813 | 889.5 | 8626.6838 | 892.5 | 16.5201 | 895 | 11.3931 | 898 | 5234.1992 | 900.5 | 7650.204 | 903.5 | 13.1188 | 847.5 | 0.092758
906.5 | 25.9207 | 909 | 9.9656 | 912 | 14.081 | 915 | 6659.4545 | 917.5 | 2.9198 | 920.5 | 17.1789 | 923 | 7.874 | 926 | 31.049 | 929 | 7667.8369 | 931.5 | 0.19573 | 934.5 | 15.6179 | 937 | 4.7016 | 940 | 17.1829 | 942.5 | 6.7313 | 945.5 | 8.4991 | 948.5 | 1.3659 | 951 | 1.1583 | 954 | 0.96886 | 956.5 | 14.0229 | 959.5 | 0.67675 | 962.5 | 23.4307 | 906.5 | 0.19573
965 | 31.0511 | 968 | 5.5987 | 970.5 | 24.0436 | 973.5 | 3.0398 | 976.5 | 28.1921 | 979.5 | 3.4465 | 982 | 7.3893 | 984.5 | 1.1979 | 987.5 | 11.9677 | 990.5 | 6.232 | 993 | 28.5427 | 996 | 2.9619 | 998.5 | 32.7913 | 1001.5 | 11.618 | 1004.5 | 41.7461 | 1007 | 6.5045 | 1010 | 8.7005 | 1012.5 | 14.9778 | 1015.5 | 19.7075 | 1018.5 | 7.6233 | 1021 | 6.5628 | 965 | 1.1979
1024 | 36.8267 | 1026.5 | 6.4765 | 1029.5 | 7.3007 | 1032.5 | 10.6522 | 1035 | 13.3776 | 1038 | 3.0816 | 1040.5 | 10.8047 | 1043.5 | 12.756 | 1046.5 | 19.1718 | 1049 | 12.3775 | 1052 | 22.109 | 1054.5 | 0.0018102 | 1057.5 | 20.7144 | 1060.5 | 0.18934 | 1063 | 0.35885 | 1066 | 0.092501 | 1068.5 | 4.0243 | 1071.5 | 11.3467 | 1074 | 2.5597 | 1077 | 22.1901 | 1080 | 8.855 | 1024 | 0.0018102
1082.5 | 8.3257 | 1085.5 | 12.089 | 1088.5 | 13.8967 | 1091 | 33.648 | 1094 | 4.1138 | 1096.5 | 9.4598 | 1099.5 | 17.5845 | 1102.5 | 24.1801 | 1105 | 8262.2229 | 1108 | 3.4758 | 1110.5 | 19.6065 | 1113.5 | 3.4635 | 1116.5 | 9.4372 | 1119 | 7.5396 | 1122 | 11.2934 | 1124.5 | 21.3175 | 1127.5 | 2.8633 | 1130.5 | 8.6852 | 1133 | 4.2769 | 1136 | 2.8563 | 1138.5 | 17.7187 | 1082.5 | 2.8563
1141.5 | 22.1995 | 1144.5 | 0.44345 | 1147 | 0.39426 | 1150 | 4307.0556 | 1152.5 | 0.87681 | 1155.5 | 1.9001 | 1158.5 | 32.7826 | 1161 | 33.4421 | 1164 | 8266.0808 | 1167 | 2631.6557 | 1169.5 | 138.6896 | 1172.5 | 2.1503 | 1175 | 4508.4308 | 1178 | 26.3911 | 1180.5 | 11.8903 | 1183.5 | 38.0553 | 1186.5 | 4.5234 | 1189 | 1.3755 | 1192 | 5.6365 | 1194.5 | 31.8982 | 1197.5 | 2.9814 | 1141.5 | 0.39426
1200.5 | 8.3381 | 1203 | 10.0938 | 1206 | 17.9715 | 1208.5 | 18.6301 | 1211.5 | 8.3104 | 1214.5 | 5.4594 | 1217 | 19.3434 | 1220 | 18.4422 | 1222.5 | 3.7435 | 1225.5 | 18.2391 | 1228.5 | 11.8734 | 1231 | 33.4645 | 1234 | 32.1476 | 1236.5 | 16.8717 | 1239.5 | 27.2475 | 1242.5 | 5.6663 | 1245 | 9.5499 | 1248 | 21.5082 | 1250.5 | 1.0236 | 1253.5 | 18.773 | 1256.5 | 23.4305 | 1200.5 | 1.0236
1259 | 17.4339 | 1262 | 12.5001 | 1264.5 | 30.1182 | 1267.5 | 13.6381 | 1270.5 | 10.7888 | 1273 | 11.7746 | 1276 | 19.111 | 1278.5 | 6.5119 | 1281.5 | 1.4801 | 1284.5 | 0.64804 | 1287 | 6.7144 | 1290 | 13.6701 | 1292 | 963.276 | 1296.5 | 20.9444 | 1299.5 | 24.512 | 1302.5 | 7.1245 | 1305 | 0.38992 | 1308 | 7.3783 | 1310.5 | 3.3253 | 1313.5 | 18.2796 | 1315 | 1.5601 | 1259 | 0.38992
1318 | 11.5946 | 1320.5 | 12.9667 | 1323.5 | 17.6968 | 1326.5 | 12.7723 | 1329 | 18.286 | 1332 | 0.82651 | 1334.5 | 11.0345 | 1337.5 | 2.4474 | 1340.5 | 4.1106 | 1343 | 17.8378 | 1346 | 7.4106 | 1348 | 4.1198 | 1351.5 | 6.51 | 1354.5 | 11.3793 | 1357 | 21.4816 | 1360 | 7.5313 | 1362.5 | 11.2856 | 1365.5 | 6.6771 | 1368.5 | 7.0675 | 1371 | 17.1878 | 1374 | 26.6298 | 1318 | 0.82651
1376.5 | 4.6744 | 1379.5 | 14.6225 | 1382.5 | 2.2497 | 1385 | 15.7574 | 1388 | 4.9474 | 1390.5 | 16.156 | 1393.5 | 1.0558 | 1396.5 | 10.2281 | 1399 | 28.1165 | 1402 | 1.5826 | 1404.5 | 7.3557 | 1407.5 | 10.1211 | 1410.5 | 13.3098 | 1413 | 23.197 | 1416 | 29.8213 | 1418.5 | 12.7101 | 1421.5 | 5.9916 | 1424.5 | 1.8508 | 1427 | 1.6747 | 1430 | 9.8872 | 1432.5 | 4.262 | 1376.5 | 1.0558
1435.5 | 1.6842 | 1438.5 | 0.81251 | 1441 | 19.5088 | 1444 | 2.8157 | 1446.5 | 21.1431 | 1449.5 | 13.0689 | 1452.5 | 26.5593 | 1455 | 0.09443 | 1458 | 1.4542 | 1460.5 | 12.4824 | 1463.5 | 23.6725 | 1466.5 | 33.1328 | 1469 | 29.4891 | 1472 | 6.3799 | 1474.5 | 0.54079 | 1477.5 | 0.54112 | 1480.5 | 24.1944 | 1483 | 9.0318 | 1486 | 36.6452 | 1488.5 | 3.6153 | 1491.5 | 14.7518 | 1435.5 | 0.09443
1494.5 | 9.3865 | 1497 | 7.1683 | 1500 | 2.6408 | 1502.5 | 9.7823 | 1505.5 | 7.7766 | 1508.5 | 0.69501 | 1511 | 9.6837 | 1514 | 11.5168 | 1516.5 | 28.4245 | 1519.5 | 0.083356 | 1522.5 | 4.679 | 1525 | 32.0422 | 1528 | 3.4331 | 1530.5 | 35.0933 | 1533.5 | 10.703 | 1536.5 | 26.3728 | 1539 | 4.4027 | 1542 | 17.0057 | 1544.5 | 3.5031 | 1547.5 | 4.1441 | 1550.5 | 16.9303 | 1494.5 | 0.083356
1553 | 17.5435 | 1556 | 17.2132 | 1558.5 | 0.23841 | 1561.5 | 5.308 | 1564.5 | 14.1656 | 1567 | 3.4177 | 1570 | 15.3707 | 1572.5 | 35.595 | 1575.5 | 6.929 | 1578.5 | 12.6323 | 1581 | 14.6331 | 1584 | 1.9765 | 1586.5 | 12.0902 | 1589.5 | 17.1429 | 1592.5 | 10.7765 | 1595 | 21.6539 | 1598 | 12.0866 | 1600.5 | 9.4998 | 1603.5 | 6.2287 | 1606 | 20.6274 | 1609 | 2.5858 | 1553 | 0.23841
1612 | 3.0342 | 1614.5 | 25.8224 | 1617.5 | 10.0702 | 1620.5 | 16.5062 | 1623 | 1.3432 | 1626 | 8.6122 | 1628.5 | 4.0134 | 1631.5 | 8.8979 | 1634.5 | 17.1329 | 1637 | 21.2677 | 1640 | 16.6476 | 1642.5 | 13.8128 | 1645.5 | 18.0912 | 1648.5 | 20.762 | 1651 | 1.0978 | 1654 | 15.3288 | 1656.5 | 19.6588 | 1659.5 | 1.2428 | 1662.5 | 12.4681 | 1665 | 10.8872 | 1668 | 6.4624 | 1612 | 1.0978

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 29 |  |  | 2006-08-01 | 14:23
PE | 7-C | Air Drop
325 C | 7.2 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-86.0833 | 211202 |  | -74.4167 | 211202 | -66.5833 | 211202 | -61.4167 | 211202 | -58 | 211202 | -55.75 | 211202 | -53.4167 | 211202 | -86.0833 | 211202
-27.3333 | 211202 |  | -15.6667 | 211202 | -7.6667 | 211202 | -2.5 | 211202 | 0.66667 | 211202 | 3 | 211202 | 5.3333 | 52725.5 | -27.3333 | 52725.5
31.6667 | 211202 |  | 43.1667 | 211202 | 51.1667 | 211202 | 56.4167 | 211202 | 59.5 | 211202 | 61.8333 | 211202 | 64.0833 | 211202 | 31.6667 | 211202
90.3333 | 211202 |  | 102 | 211202 | 109.8333 | 211202 | 115.0833 | 211202 | 118.25 | 211202 | 120.5833 | 211202 | 123.0833 | 211202 | 90.3333 | 211202
149.0833 | 211202 |  | 160.75 | 211202 | 168.75 | 211202 | 173.75 | 211202 | 177.0833 | 211202 | 179.5 | 211202 | 181.75 | 211202 | 149.0833 | 211202
207.8333 | 211202 |  | 219.5833 | 211202 | 227.4167 | 211202 | 232.5833 | 211202 | 236 | 211202 | 238.25 | 211202 | 240.5 | 211202 | 207.8333 | 211202
266.6667 | 105551 |  | 278.3333 | 211202 | 286.3333 | 211202 | 291.5 | 211202 | 294.6667 | 211202 | 297 | 211202 | 299.3333 | 211202 | 266.6667 | 105551
325.4167 | 211202 |  | 337.1667 | 211202 | 345 | 211202 | 350.1667 | 211202 | 353.4167 | 211202 | 355.75 | 211202 | 358.0833 | 211202 | 325.4167 | 211202
384.3333 | 211202 |  | 395.9167 | 211202 | 403.75 | 211202 | 408.9167 | 211202 | 412.0833 | 211202 | 414.5833 | 211202 | 417.0833 | 211202 | 384.3333 | 211202
443.0833 | 211202 |  | 454.75 | 211202 | 462.75 | 211202 | 467.75 | 211202 | 471.0833 | 211202 | 473.5 | 211202 | 475.75 | 211202 | 443.0833 | 211202
501.9167 | 211202 |  | 513.4167 | 211202 | 521.4167 | 211202 | 526.5 | 211202 | 529.8333 | 211202 | 532.25 | 211202 | 534.5 | 211202 | 501.9167 | 211202
560.5833 | 211202 |  | 572.1667 | 211202 | 580.1667 | 211202 | 585.3333 | 105551 | 588.5 | 211202 | 590.9167 | 211202 | 593.1667 | 211202 | 560.5833 | 105551
619.4167 | 211202 |  | 631.0833 | 211202 | 639 | 211202 | 644.0833 | 211202 | 647.3333 | 211202 | 649.6667 | 211202 | 652.0833 | 105551 | 619.4167 | 105551
678.25 | 211202 |  | 689.9167 | 211202 | 697.8333 | 211202 | 702.9167 | 211202 | 706.25 | 211202 | 708.5 | 211202 | 710.8333 | 211202 | 678.25 | 211202
736.9167 | 211202 |  | 748.5833 | 211202 | 756.4167 | 211202 | 761.5833 | 211202 | 765 | 211202 | 767.25 | 211202 | 769.5833 | 211202 | 736.9167 | 211202
795.6667 | 211202 |  | 807.3333 | 211202 | 815.3333 | 211202 | 820.5833 | 211202 | 823.8333 | 211202 | 826.0833 | 5657.6305 | 828.3333 | 4467.0243 | 795.6667 | 4467.0243
854.5 | 1.6524 |  | 866.3333 | 48.83 | 874.1667 | 1.5591 | 879.3333 | 115.7698 | 882.5833 | 6683.7967 | 884.8333 | 4.8431 | 887.0833 | 145.9438 | 854.5 | 1.5591
913.4167 | 65.5939 |  | 925.0833 | 165.0113 | 932.8333 | 59.8528 | 938.0833 | 6.3671 | 941.4167 | 10.3075 | 943.5833 | 64.3301 | 946.0833 | 5.4859 | 913.4167 | 5.4859
972.1667 | 35.5113 |  | 983.75 | 7.2826 | 991.75 | 64.7105 | 996.75 | 6.1647 | 1000.0833 | 72.0136 | 1002.5 | 51.2033 | 1004.8333 | 40.8869 | 972.1667 | 6.1647
1030.9167 | 78.6283 |  | 1042.5833 | 88.9264 | 1050.4167 | 112.9543 | 1055.5833 | 55.6707 | 1058.9167 | 151.9347 | 1061.1667 | 64.01 | 1063.5833 | 132.3916 | 1030.9167 | 55.6707
1089.6667 | 51.5213 |  | 1101.3333 | 65.9159 | 1109.3333 | 105.9778 | 1114.5 | 33.3145 | 1117.6667 | 68.3872 | 1120 | 30.4929 | 1122.3333 | 74.7539 | 1089.6667 | 30.4929
1148.5 | 14.1867 |  | 1160.25 | 135.8116 | 1168.1667 | 67.9271 | 1173.25 | 155.9117 | 1176.5 | 321.2454 | 1178.9167 | 249.3752 | 1181.0833 | 12.744 | 1148.5 | 12.744
1207.3333 | 69.6619 |  | 1219 | 95.3758 | 1226.8333 | 89.8385 | 1232.0833 | 183.0056 | 1235.25 | 131.6687 | 1237.5833 | 773.6273 | 1240.0833 | 304.9418 | 1207.3333 | 69.6619
1266.0833 | 122.7997 |  | 1277.75 | 7.5264 | 1286 | 150.1818 | 1291.4167 | 346.0503 | 1294.5833 | 6.0061 | 1297 | 32.3833 | 1299.3333 | 31.0717 | 1266.0833 | 6.0061
1324.9167 | 243.5841 |  | 1336.5833 | 192.0676 | 1344.3333 | 80.1062 | 1349.5 | 164.9982 | 1353 | 157.2419 | 1355.25 | 68.6631 | 1357.5833 | 222.1455 | 1324.9167 | 68.6631
1383.6667 | 76.5187 |  | 1395.3333 | 46.8034 | 1403.3333 | 185.681 | 1408.5 | 270.0908 | 1411.6667 | 228.1363 | 1414 | 88.2686 | 1416.3333 | 58.7388 | 1383.6667 | 46.8034
1442.5 | 45.0926 |  | 1454.1667 | 365.9341 | 1462.1667 | 45.3806 | 1467.25 | 5.1007 | 1470.5 | 4.5538 | 1472.8333 | 38.2822 | 1475.0833 | 290.2582 | 1442.5 | 4.5538
1501.3333 | 11.5437 |  | 1513 | 69.3261 | 1520.8333 | 32.1777 | 1526.0833 | 21.1656 | 1529.25 | 30.9596 | 1531.5833 | 16.4062 | 1534.0833 | 12.3975 | 1501.3333 | 11.5437
1560.0833 | 93.2822 |  | 1571.75 | 108.7935 | 1579.75 | 94.2801 | 1584.75 | 73.8581 | 1588 | 49.5839 | 1590.5 | 22.5181 | 1592.6667 | 26.0269 | 1560.0833 | 22.5181
1618.9167 | 49.0931 |  | 1630.5833 | 64.4681 | 1638.4167 | 152.5586 | 1643.5833 | 61.015 | 1647 | 100.8813 | 1649.25 | 51.7365 | 1651.5833 | 74.2355 | 1618.9167 | 49.0931

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -94 | 23 | 27.4 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
1 | -93 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
2 | -92 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
3 | -91 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
4 | -90 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
5 | -89 | 23 | 27.4 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
6 | -88 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
7 | -87 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
8 | -86 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
9 | -85 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
10 | -84 | 23 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
11 | -83 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
12 | -82 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
13 | -81 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
14 | -80 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
15 | -79 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
16 | -78 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
17 | -77 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
18 | -76 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
19 | -75 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
20 | -74 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
21 | -73 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
22 | -72 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.6
23 | -71 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
24 | -70 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
25 | -69 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
26 | -68 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
27 | -67 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
28 | -66 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
29 | -65 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
30 | -64 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
31 | -63 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
32 | -62 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
33 | -61 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
34 | -60 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
35 | -59 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
36 | -58 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
37 | -57 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
38 | -56 | 22.9 | 27.3 | 27.5 | 27.7 | 27.4 | 27.3 | 27.5
39 | -55 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
40 | -54 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
41 | -53 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
42 | -52 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
43 | -51 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
44 | -50 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
45 | -49 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
46 | -48 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
47 | -47 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
48 | -46 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
49 | -45 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
50 | -44 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
51 | -43 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
52 | -42 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
53 | -41 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
54 | -40 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
55 | -39 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
56 | -38 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
57 | -37 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
58 | -36 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
59 | -35 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
60 | -34 | 22.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
61 | -33 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
62 | -32 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
63 | -31 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
64 | -30 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
65 | -29 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
66 | -28 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
67 | -27 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
68 | -26 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
69 | -25 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
70 | -24 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
71 | -23 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
72 | -22 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
73 | -21 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
74 | -20 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
75 | -19 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
76 | -18 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
77 | -17 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
78 | -16 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
79 | -15 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
80 | -14 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
81 | -13 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
82 | -12 | 22.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
83 | -11 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
84 | -10 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
85 | -9 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
86 | -8 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
87 | -7 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
88 | -6 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
89 | -5 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
90 | -4 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
91 | -3 | 22.8 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
92 | -2 | 22.8 | 27.3 | 27.4 | 27.6 | 27.4 | 27.3 | 27.5
93 | -1 | 22.8 | 27.3 | 27.4 | 27.6 | 27.4 | 27.3 | 27.5
94 | 0 | 23.2 | 27.3 | 27.4 | 27.6 | 27.4 | 27.3 | 27.5
95 | 1 | 24.3 | 27.3 | 27.5 | 27.6 | 27.4 | 27.3 | 27.5
96 | 2 | 26.1 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
97 | 3 | 28.6 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.5
98 | 4 | 31.7 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.6
99 | 5 | 35.1 | 27.3 | 27.5 | 27.6 | 27.3 | 27.3 | 27.6
100 | 6 | 38.9 | 27.3 | 27.5 | 27.6 | 27.3 | 27.4 | 27.6
101 | 7 | 43.1 | 27.3 | 27.5 | 27.6 | 27.4 | 27.4 | 27.7
102 | 8 | 47.4 | 27.3 | 27.5 | 27.6 | 27.4 | 27.5 | 27.7
103 | 9 | 51.9 | 27.3 | 27.5 | 27.6 | 27.4 | 27.6 | 27.8
104 | 10 | 56.5 | 27.3 | 27.5 | 27.6 | 27.4 | 27.7 | 27.9
105 | 11 | 61.3 | 27.4 | 27.5 | 27.7 | 27.4 | 27.8 | 27.9
106 | 12 | 66.2 | 27.4 | 27.5 | 27.7 | 27.4 | 27.9 | 28
107 | 13 | 71.3 | 27.4 | 27.5 | 27.7 | 27.5 | 28 | 28.1
108 | 14 | 76.4 | 27.4 | 27.5 | 27.7 | 27.5 | 28.2 | 28.2
109 | 15 | 81.7 | 27.4 | 27.5 | 27.7 | 27.6 | 28.3 | 28.3
110 | 16 | 87 | 27.5 | 27.5 | 27.7 | 27.6 | 28.5 | 28.5
111 | 17 | 92.3 | 27.5 | 27.5 | 27.8 | 27.7 | 28.7 | 28.6
112 | 18 | 97.7 | 27.6 | 27.5 | 27.8 | 27.8 | 28.9 | 28.8
113 | 19 | 103.1 | 27.6 | 27.6 | 27.8 | 27.8 | 29.1 | 28.9
114 | 20 | 108.6 | 27.7 | 27.6 | 27.9 | 27.9 | 29.4 | 29.1
115 | 21 | 114.2 | 27.8 | 27.6 | 27.9 | 28 | 29.7 | 29.3
116 | 22 | 119.9 | 27.8 | 27.6 | 27.9 | 28.1 | 29.9 | 29.5
117 | 23 | 125.5 | 27.9 | 27.7 | 28 | 28.2 | 30.2 | 29.7
118 | 24 | 131.1 | 28 | 27.7 | 28 | 28.4 | 30.6 | 30
119 | 25 | 136.8 | 28.1 | 27.7 | 28.1 | 28.5 | 31 | 30.2
120 | 26 | 142.5 | 28.2 | 27.8 | 28.1 | 28.6 | 31.3 | 30.5
121 | 27 | 148.1 | 28.3 | 27.8 | 28.2 | 28.8 | 31.7 | 30.8
122 | 28 | 153.8 | 28.4 | 27.9 | 28.3 | 29 | 32.1 | 31.1
123 | 29 | 159.5 | 28.6 | 28 | 28.4 | 29.1 | 32.6 | 31.4
124 | 30 | 165.2 | 28.7 | 28 | 28.5 | 29.3 | 33 | 31.8
125 | 31 | 170.9 | 28.9 | 28.1 | 28.6 | 29.5 | 33.5 | 32.1
126 | 32 | 176.7 | 29.1 | 28.2 | 28.7 | 29.8 | 33.9 | 32.5
127 | 33 | 182.4 | 29.2 | 28.2 | 28.8 | 30 | 34.5 | 32.9
128 | 34 | 188.1 | 29.4 | 28.3 | 28.9 | 30.2 | 35 | 33.3
129 | 35 | 193.8 | 29.7 | 28.4 | 29 | 30.5 | 35.6 | 33.7
130 | 36 | 199.4 | 29.9 | 28.5 | 29.2 | 30.8 | 36.2 | 34.1
131 | 37 | 205.1 | 30.1 | 28.7 | 29.3 | 31.1 | 36.9 | 34.6
132 | 38 | 210.8 | 30.4 | 28.8 | 29.5 | 31.4 | 37.5 | 35.1
133 | 39 | 216.5 | 30.7 | 28.9 | 29.6 | 31.7 | 38.2 | 35.7
134 | 40 | 222.2 | 31 | 29 | 29.8 | 32.1 | 39 | 36.2
135 | 41 | 227.9 | 31.3 | 29.2 | 30 | 32.4 | 39.8 | 36.8
136 | 42 | 233.6 | 31.6 | 29.3 | 30.2 | 32.8 | 40.5 | 37.4
137 | 43 | 239.3 | 31.9 | 29.5 | 30.4 | 33.2 | 41.3 | 38
138 | 44 | 244.8 | 32.3 | 29.7 | 30.6 | 33.6 | 42.2 | 38.7
139 | 45 | 250.5 | 32.6 | 29.9 | 30.8 | 34.1 | 43 | 39.3
140 | 46 | 256 | 33 | 30.1 | 31 | 34.5 | 43.8 | 40
141 | 47 | 261.6 | 33.4 | 30.3 | 31.3 | 35 | 44.7 | 40.7
142 | 48 | 267.2 | 33.9 | 30.5 | 31.5 | 35.5 | 45.6 | 41.4
143 | 49 | 272.6 | 34.3 | 30.7 | 31.8 | 36 | 46.6 | 42.2
144 | 50 | 278.1 | 34.8 | 30.9 | 32.1 | 36.5 | 47.7 | 43
145 | 51 | 283.6 | 35.3 | 31.2 | 32.4 | 37.1 | 48.8 | 43.9
146 | 52 | 289.2 | 35.8 | 31.4 | 32.7 | 37.7 | 49.8 | 44.7
147 | 53 | 294.7 | 36.3 | 31.7 | 33 | 38.3 | 50.9 | 45.6
148 | 54 | 300.2 | 36.9 | 31.9 | 33.3 | 38.9 | 52 | 46.5
149 | 55 | 305.6 | 37.5 | 32.2 | 33.6 | 39.6 | 53.2 | 47.4
150 | 56 | 310.7 | 38 | 32.5 | 34 | 40.2 | 54.4 | 48.3
151 | 57 | 315.4 | 38.7 | 32.8 | 34.4 | 40.9 | 55.6 | 49.3
152 | 58 | 319.6 | 39.3 | 33.1 | 34.7 | 41.6 | 56.8 | 50.2
153 | 59 | 323.7 | 39.9 | 33.5 | 35.1 | 42.3 | 58 | 51.2
154 | 60 | 327.4 | 40.6 | 33.9 | 35.5 | 43 | 59.2 | 52.2
155 | 61 | 330.9 | 41.3 | 34.2 | 35.9 | 43.8 | 60.4 | 53.2
156 | 62 | 334.3 | 42 | 34.6 | 36.4 | 44.6 | 61.5 | 54.2
157 | 63 | 337.3 | 42.7 | 35 | 36.8 | 45.3 | 62.7 | 55.2
158 | 64 | 340.1 | 43.4 | 35.5 | 37.2 | 46.1 | 63.9 | 56.2
159 | 65 | 342.6 | 44.2 | 35.9 | 37.7 | 46.9 | 65.1 | 57.2
160 | 66 | 344.9 | 45 | 36.3 | 38.2 | 47.8 | 66.3 | 58.3
161 | 67 | 346.8 | 45.8 | 36.8 | 38.6 | 48.6 | 67.5 | 59.3
162 | 68 | 348.3 | 46.6 | 37.2 | 39.1 | 49.5 | 68.7 | 60.3
163 | 69 | 349.5 | 47.4 | 37.7 | 39.6 | 50.3 | 69.9 | 61.3
164 | 70 | 350.5 | 48.2 | 38.2 | 40.1 | 51.2 | 71 | 62.3
165 | 71 | 351.3 | 49 | 38.7 | 40.6 | 52 | 72.1 | 63.3
166 | 72 | 352 | 49.9 | 39.3 | 41.1 | 52.9 | 73.1 | 64.3
167 | 73 | 352.5 | 50.7 | 39.8 | 41.6 | 53.8 | 74.1 | 65.3
168 | 74 | 352.7 | 51.6 | 40.3 | 42.1 | 54.6 | 75.1 | 66.2
169 | 75 | 352.8 | 52.5 | 40.8 | 42.7 | 55.5 | 76.1 | 67.2
170 | 76 | 352.8 | 53.4 | 41.4 | 43.2 | 56.4 | 77.1 | 68.1
171 | 77 | 352.8 | 54.3 | 41.9 | 43.7 | 57.3 | 78.1 | 69.1
172 | 78 | 352.8 | 55.2 | 42.5 | 44.3 | 58.1 | 79 | 70
173 | 79 | 352.7 | 56.1 | 43 | 44.8 | 59 | 80 | 70.9
174 | 80 | 352.6 | 57 | 43.6 | 45.4 | 59.9 | 80.9 | 71.9
175 | 81 | 352.5 | 58 | 44.1 | 45.9 | 60.7 | 81.8 | 72.8
176 | 82 | 352.2 | 58.9 | 44.7 | 46.5 | 61.6 | 82.7 | 73.7
177 | 83 | 351.9 | 59.8 | 45.3 | 47 | 62.4 | 83.5 | 74.6
178 | 84 | 351.6 | 60.7 | 45.8 | 47.6 | 63.3 | 84.4 | 75.5
179 | 85 | 351.3 | 61.7 | 46.4 | 48.1 | 64.1 | 85.2 | 76.4
180 | 86 | 351 | 62.6 | 47 | 48.7 | 64.9 | 86 | 77.2
181 | 87 | 350.8 | 63.5 | 47.6 | 49.2 | 65.7 | 86.8 | 78.1
182 | 88 | 350.5 | 64.4 | 48.2 | 49.8 | 66.5 | 87.6 | 78.9
183 | 89 | 350.2 | 65.4 | 48.8 | 50.3 | 67.3 | 88.4 | 79.8
184 | 90 | 349.8 | 66.3 | 49.3 | 50.9 | 68.1 | 89.2 | 80.6
185 | 91 | 349.4 | 67.2 | 49.9 | 51.5 | 68.8 | 89.9 | 81.5
186 | 92 | 348.9 | 68.1 | 50.5 | 52 | 69.6 | 90.6 | 82.3
187 | 93 | 348.5 | 69 | 51.1 | 52.6 | 70.4 | 91.3 | 83.1
188 | 94 | 348.1 | 69.9 | 51.7 | 53.1 | 71.1 | 92 | 83.9
189 | 95 | 347.6 | 70.8 | 52.3 | 53.7 | 71.8 | 92.7 | 84.7
190 | 96 | 347.2 | 71.6 | 52.9 | 54.2 | 72.5 | 93.4 | 85.5
191 | 97 | 346.6 | 72.5 | 53.5 | 54.7 | 73.3 | 94.1 | 86.3
192 | 98 | 346.1 | 73.4 | 54.1 | 55.3 | 74 | 94.7 | 87.1
193 | 99 | 345.5 | 74.2 | 54.7 | 55.8 | 74.7 | 95.3 | 87.9
194 | 100 | 344.9 | 75.1 | 55.3 | 56.4 | 75.4 | 95.9 | 88.6
195 | 101 | 344.5 | 75.9 | 55.9 | 56.9 | 76.1 | 96.5 | 89.4
196 | 102 | 344 | 76.8 | 56.5 | 57.5 | 76.7 | 97.1 | 90.2
197 | 103 | 343.5 | 77.6 | 57 | 58 | 77.4 | 97.7 | 90.9
198 | 104 | 342.9 | 78.4 | 57.6 | 58.5 | 78.1 | 98.3 | 91.7
199 | 105 | 342.3 | 79.2 | 58.2 | 59.1 | 78.7 | 98.8 | 92.4
200 | 106 | 341.6 | 80 | 58.8 | 59.6 | 79.3 | 99.4 | 93.1
201 | 107 | 341 | 80.8 | 59.4 | 60.1 | 79.9 | 99.9 | 93.8
202 | 108 | 340.5 | 81.6 | 59.9 | 60.6 | 80.6 | 100.4 | 94.5
203 | 109 | 339.9 | 82.4 | 60.5 | 61.2 | 81.2 | 101 | 95.2
204 | 110 | 339.4 | 83.1 | 61.1 | 61.7 | 81.7 | 101.5 | 95.9
205 | 111 | 338.9 | 83.9 | 61.7 | 62.2 | 82.3 | 102 | 96.6
206 | 112 | 338.3 | 84.6 | 62.2 | 62.7 | 82.9 | 102.5 | 97.3
207 | 113 | 337.8 | 85.4 | 62.8 | 63.3 | 83.5 | 103 | 97.9
208 | 114 | 337.2 | 86.1 | 63.4 | 63.8 | 84.1 | 103.5 | 98.6
209 | 115 | 336.7 | 86.8 | 63.9 | 64.3 | 84.6 | 104 | 99.3
210 | 116 | 336.3 | 87.6 | 64.5 | 64.8 | 85.2 | 104.5 | 99.9
211 | 117 | 335.8 | 88.3 | 65.1 | 65.3 | 85.7 | 104.9 | 100.5
212 | 118 | 335.2 | 88.9 | 65.6 | 65.8 | 86.3 | 105.4 | 101.2
213 | 119 | 334.6 | 89.6 | 66.2 | 66.3 | 86.8 | 105.8 | 101.8
214 | 120 | 334.2 | 90.3 | 66.7 | 66.8 | 87.4 | 106.3 | 102.4
215 | 121 | 333.7 | 91 | 67.3 | 67.3 | 87.9 | 106.7 | 103
216 | 122 | 333.2 | 91.6 | 67.8 | 67.8 | 88.4 | 107.2 | 103.6
217 | 123 | 332.7 | 92.3 | 68.4 | 68.3 | 89 | 107.6 | 104.2
218 | 124 | 332 | 92.9 | 68.9 | 68.8 | 89.5 | 108 | 104.8
219 | 125 | 331.4 | 93.5 | 69.5 | 69.3 | 90 | 108.4 | 105.4
220 | 126 | 330.9 | 94.1 | 70 | 69.8 | 90.5 | 108.8 | 105.9
221 | 127 | 330.4 | 94.8 | 70.6 | 70.3 | 91 | 109.2 | 106.5
222 | 128 | 329.8 | 95.4 | 71.1 | 70.8 | 91.5 | 109.6 | 107
223 | 129 | 329.2 | 96 | 71.6 | 71.3 | 92 | 109.9 | 107.6
224 | 130 | 328.7 | 96.6 | 72.1 | 71.7 | 92.4 | 110.3 | 108.1
225 | 131 | 328.2 | 97.2 | 72.7 | 72.2 | 92.9 | 110.7 | 108.6
226 | 132 | 327.7 | 97.7 | 73.2 | 72.7 | 93.4 | 111.1 | 109.1
227 | 133 | 327.1 | 98.3 | 73.7 | 73.2 | 93.8 | 111.4 | 109.6
228 | 134 | 326.6 | 98.9 | 74.3 | 73.6 | 94.3 | 111.8 | 110.1
229 | 135 | 326 | 99.4 | 74.8 | 74.1 | 94.7 | 112.1 | 110.6
230 | 136 | 325.5 | 99.9 | 75.3 | 74.6 | 95.2 | 112.5 | 111.1
231 | 137 | 325 | 100.5 | 75.8 | 75 | 95.6 | 112.8 | 111.6
232 | 138 | 324.4 | 101 | 76.3 | 75.5 | 96.1 | 113.1 | 112
233 | 139 | 323.8 | 101.5 | 76.8 | 76 | 96.5 | 113.5 | 112.5
234 | 140 | 323.4 | 102 | 77.3 | 76.4 | 97 | 113.8 | 113
235 | 141 | 322.9 | 102.5 | 77.8 | 76.9 | 97.4 | 114.1 | 113.4
236 | 142 | 322.4 | 103 | 78.3 | 77.3 | 97.8 | 114.4 | 113.8
237 | 143 | 321.9 | 103.5 | 78.7 | 77.8 | 98.2 | 114.7 | 114.3
238 | 144 | 321.4 | 104 | 79.2 | 78.2 | 98.7 | 115 | 114.7
239 | 145 | 320.8 | 104.5 | 79.7 | 78.7 | 99.1 | 115.3 | 115.1
240 | 146 | 320.2 | 104.9 | 80.2 | 79.1 | 99.5 | 115.6 | 115.5
241 | 147 | 319.7 | 105.4 | 80.7 | 79.5 | 99.9 | 115.9 | 115.9
242 | 148 | 319.1 | 105.9 | 81.1 | 80 | 100.2 | 116.2 | 116.3
243 | 149 | 318.6 | 106.3 | 81.6 | 80.4 | 100.6 | 116.5 | 116.7
244 | 150 | 318 | 106.8 | 82.1 | 80.8 | 101 | 116.8 | 117.1
245 | 151 | 317.5 | 107.2 | 82.6 | 81.3 | 101.4 | 117 | 117.5
246 | 152 | 316.9 | 107.6 | 83 | 81.7 | 101.7 | 117.3 | 117.8
247 | 153 | 316.4 | 108.1 | 83.5 | 82.1 | 102.1 | 117.5 | 118.2
248 | 154 | 316.1 | 108.5 | 84 | 82.5 | 102.4 | 117.8 | 118.6
249 | 155 | 315.8 | 108.9 | 84.4 | 82.9 | 102.8 | 118 | 118.9
250 | 156 | 315.4 | 109.3 | 84.9 | 83.4 | 103.2 | 118.3 | 119.3
251 | 157 | 315.1 | 109.7 | 85.3 | 83.8 | 103.5 | 118.5 | 119.6
252 | 158 | 314.9 | 110.1 | 85.8 | 84.2 | 103.9 | 118.8 | 120
253 | 159 | 314.6 | 110.5 | 86.2 | 84.6 | 104.2 | 119.1 | 120.3
254 | 160 | 314.4 | 110.9 | 86.7 | 85 | 104.6 | 119.3 | 120.7
255 | 161 | 314.2 | 111.3 | 87.1 | 85.4 | 104.9 | 119.6 | 121
256 | 162 | 314.1 | 111.7 | 87.5 | 85.8 | 105.3 | 119.9 | 121.3
257 | 163 | 314.1 | 112.1 | 88 | 86.2 | 105.6 | 120.1 | 121.7
258 | 164 | 314.3 | 112.5 | 88.4 | 86.6 | 105.9 | 120.4 | 122
259 | 165 | 314.6 | 112.8 | 88.8 | 87 | 106.3 | 120.7 | 122.4
260 | 166 | 314.7 | 113.2 | 89.2 | 87.4 | 106.6 | 120.9 | 122.7
261 | 167 | 314.9 | 113.6 | 89.7 | 87.8 | 107 | 121.2 | 123.1
262 | 168 | 315.2 | 113.9 | 90.1 | 88.2 | 107.3 | 121.5 | 123.4
263 | 169 | 315.5 | 114.3 | 90.5 | 88.6 | 107.7 | 121.8 | 123.7
264 | 170 | 315.8 | 114.6 | 90.9 | 89 | 108 | 122.1 | 124
265 | 171 | 316.1 | 115 | 91.3 | 89.4 | 108.4 | 122.4 | 124.4
266 | 172 | 316.5 | 115.3 | 91.7 | 89.8 | 108.8 | 122.6 | 124.7
267 | 173 | 317 | 115.7 | 92.1 | 90.1 | 109.1 | 122.9 | 125.1
268 | 174 | 317.5 | 116 | 92.6 | 90.5 | 109.5 | 123.2 | 125.4
269 | 175 | 318 | 116.4 | 93 | 90.9 | 109.8 | 123.5 | 125.8
270 | 176 | 318.5 | 116.7 | 93.4 | 91.3 | 110.2 | 123.8 | 126.2
271 | 177 | 319.1 | 117.1 | 93.8 | 91.7 | 110.5 | 124.2 | 126.5
272 | 178 | 319.6 | 117.4 | 94.2 | 92 | 110.8 | 124.5 | 126.9
273 | 179 | 320.1 | 117.7 | 94.6 | 92.4 | 111.2 | 124.8 | 127.2
274 | 180 | 320.6 | 118.1 | 95 | 92.8 | 111.5 | 125.1 | 127.5
275 | 181 | 321.1 | 118.4 | 95.4 | 93.2 | 111.8 | 125.4 | 127.9
276 | 182 | 321.5 | 118.8 | 95.8 | 93.6 | 112.1 | 125.7 | 128.3
277 | 183 | 322.1 | 119.1 | 96.2 | 93.9 | 112.5 | 126 | 128.6
278 | 184 | 322.6 | 119.5 | 96.5 | 94.3 | 112.8 | 126.4 | 128.9
279 | 185 | 323 | 119.8 | 96.9 | 94.7 | 113.1 | 126.7 | 129.3
280 | 186 | 323.4 | 120.1 | 97.3 | 95 | 113.5 | 127 | 129.6
281 | 187 | 323.8 | 120.5 | 97.7 | 95.4 | 113.8 | 127.3 | 129.9
282 | 188 | 324.2 | 120.8 | 98.1 | 95.8 | 114.1 | 127.7 | 130.3
283 | 189 | 324.5 | 121.2 | 98.5 | 96.2 | 114.5 | 128 | 130.6
284 | 190 | 324.9 | 121.5 | 98.9 | 96.5 | 114.8 | 128.3 | 131
285 | 191 | 325.2 | 121.8 | 99.3 | 96.9 | 115.2 | 128.7 | 131.3
286 | 192 | 325.6 | 122.2 | 99.6 | 97.3 | 115.5 | 129 | 131.7
287 | 193 | 325.9 | 122.5 | 100 | 97.6 | 115.9 | 129.3 | 132
288 | 194 | 326.1 | 122.9 | 100.4 | 98 | 116.3 | 129.6 | 132.4
289 | 195 | 326.2 | 123.2 | 100.8 | 98.4 | 116.6 | 129.9 | 132.7
290 | 196 | 326.3 | 123.5 | 101.1 | 98.7 | 117 | 130.3 | 133.1
291 | 197 | 326.4 | 123.9 | 101.5 | 99.1 | 117.3 | 130.6 | 133.4
292 | 198 | 326.5 | 124.2 | 101.9 | 99.4 | 117.7 | 130.9 | 133.7
293 | 199 | 326.6 | 124.5 | 102.3 | 99.8 | 118 | 131.3 | 134.1
294 | 200 | 326.6 | 124.9 | 102.6 | 100.2 | 118.4 | 131.6 | 134.4
295 | 201 | 326.6 | 125.2 | 103 | 100.5 | 118.7 | 131.9 | 134.7
296 | 202 | 326.6 | 125.5 | 103.4 | 100.9 | 119.1 | 132.3 | 135
297 | 203 | 326.5 | 125.9 | 103.7 | 101.3 | 119.4 | 132.5 | 135.3
298 | 204 | 326.5 | 126.2 | 104.1 | 101.6 | 119.8 | 132.8 | 135.7
299 | 205 | 326.5 | 126.5 | 104.5 | 102 | 120.1 | 133.2 | 136
300 | 206 | 326.6 | 126.9 | 104.8 | 102.3 | 120.4 | 133.5 | 136.3
301 | 207 | 326.5 | 127.2 | 105.2 | 102.7 | 120.7 | 133.8 | 136.6
302 | 208 | 326.5 | 127.5 | 105.5 | 103 | 121.1 | 134.1 | 136.9
303 | 209 | 326.5 | 127.8 | 105.9 | 103.4 | 121.4 | 134.3 | 137.2
304 | 210 | 326.5 | 128.2 | 106.3 | 103.7 | 121.7 | 134.7 | 137.6
305 | 211 | 326.4 | 128.5 | 106.6 | 104 | 122 | 135 | 137.9
306 | 212 | 326.3 | 128.8 | 107 | 104.4 | 122.3 | 135.2 | 138.2
307 | 213 | 326.2 | 129.1 | 107.3 | 104.7 | 122.6 | 135.5 | 138.5
308 | 214 | 326.1 | 129.4 | 107.7 | 105.1 | 122.9 | 135.8 | 138.7
309 | 215 | 325.8 | 129.7 | 108 | 105.4 | 123.2 | 136.1 | 139
310 | 216 | 325.8 | 130 | 108.4 | 105.7 | 123.5 | 136.4 | 139.4
311 | 217 | 325.7 | 130.3 | 108.7 | 106.1 | 123.8 | 136.7 | 139.7
312 | 218 | 325.7 | 130.6 | 109.1 | 106.4 | 124.1 | 137 | 139.9
313 | 219 | 325.6 | 130.9 | 109.4 | 106.7 | 124.4 | 137.3 | 140.2
314 | 220 | 325.5 | 131.2 | 109.7 | 107 | 124.7 | 137.6 | 140.5
315 | 221 | 325.5 | 131.5 | 110.1 | 107.4 | 125 | 137.8 | 140.8
316 | 222 | 325.4 | 131.8 | 110.4 | 107.7 | 125.3 | 138.1 | 141.1
317 | 223 | 325.4 | 132.1 | 110.7 | 108 | 125.6 | 138.4 | 141.4
318 | 224 | 325.3 | 132.4 | 111.1 | 108.3 | 125.9 | 138.7 | 141.7
319 | 225 | 325.2 | 132.7 | 111.4 | 108.6 | 126.2 | 138.9 | 141.9
320 | 226 | 325 | 133 | 111.7 | 108.9 | 126.5 | 139.2 | 142.2
321 | 227 | 324.9 | 133.3 | 112.1 | 109.2 | 126.8 | 139.5 | 142.5
322 | 228 | 324.9 | 133.5 | 112.4 | 109.5 | 127 | 139.8 | 142.8
323 | 229 | 324.8 | 133.8 | 112.7 | 109.8 | 127.3 | 140 | 143
324 | 230 | 324.7 | 134.1 | 113 | 110.1 | 127.5 | 140.3 | 143.3
325 | 231 | 324.6 | 134.3 | 113.3 | 110.4 | 127.8 | 140.5 | 143.6
326 | 232 | 324.6 | 134.6 | 113.7 | 110.7 | 128 | 140.8 | 143.9
327 | 233 | 324.5 | 134.8 | 114 | 111 | 128.3 | 141.1 | 144.2
328 | 234 | 324.6 | 135.1 | 114.3 | 111.3 | 128.5 | 141.3 | 144.4
329 | 235 | 324.6 | 135.3 | 114.6 | 111.6 | 128.7 | 141.6 | 144.7
330 | 236 | 324.6 | 135.6 | 114.9 | 111.9 | 128.9 | 141.8 | 145
331 | 237 | 324.8 | 135.8 | 115.2 | 112.2 | 129.2 | 142.1 | 145.2
332 | 238 | 324.9 | 136 | 115.5 | 112.5 | 129.4 | 142.4 | 145.5
333 | 239 | 324.8 | 136.2 | 115.8 | 112.8 | 129.6 | 142.6 | 145.8
334 | 240 | 324.8 | 136.5 | 116.1 | 113.1 | 129.8 | 142.9 | 146
335 | 241 | 324.6 | 136.7 | 116.4 | 113.4 | 130 | 143.2 | 146.3
336 | 242 | 324.7 | 136.9 | 116.7 | 113.7 | 130.2 | 143.4 | 146.6
337 | 243 | 324.7 | 137.1 | 117 | 114 | 130.5 | 143.7 | 146.8
338 | 244 | 324.7 | 137.3 | 117.2 | 114.3 | 130.7 | 144 | 147.1
339 | 245 | 324.7 | 137.5 | 117.5 | 114.6 | 130.9 | 144.2 | 147.4
340 | 246 | 324.7 | 137.7 | 117.8 | 114.9 | 131.1 | 144.5 | 147.6
341 | 247 | 324.7 | 137.9 | 118.1 | 115.2 | 131.4 | 144.7 | 147.8
342 | 248 | 324.8 | 138.1 | 118.4 | 115.4 | 131.6 | 145 | 148.1
343 | 249 | 324.8 | 138.3 | 118.7 | 115.7 | 131.8 | 145.2 | 148.4
344 | 250 | 324.9 | 138.5 | 119 | 116 | 132.1 | 145.5 | 148.6
345 | 251 | 324.9 | 138.7 | 119.2 | 116.3 | 132.3 | 145.7 | 148.9
346 | 252 | 325 | 138.9 | 119.5 | 116.6 | 132.6 | 145.9 | 149.1
347 | 253 | 325 | 139.1 | 119.8 | 116.9 | 132.9 | 146.2 | 149.4
348 | 254 | 325 | 139.3 | 120.1 | 117.2 | 133.1 | 146.4 | 149.6
349 | 255 | 325 | 139.5 | 120.4 | 117.4 | 133.4 | 146.7 | 149.9
350 | 256 | 325 | 139.7 | 120.6 | 117.7 | 133.7 | 146.9 | 150.1
351 | 257 | 325 | 139.9 | 120.9 | 118 | 134 | 147.2 | 150.4
352 | 258 | 325 | 140.1 | 121.2 | 118.3 | 134.3 | 147.4 | 150.6
353 | 259 | 324.9 | 140.3 | 121.5 | 118.6 | 134.6 | 147.7 | 150.8
354 | 260 | 324.8 | 140.4 | 121.8 | 118.8 | 134.9 | 147.9 | 151.1
355 | 261 | 324.8 | 140.7 | 122 | 119.1 | 135.2 | 148.1 | 151.3
356 | 262 | 324.8 | 140.9 | 122.3 | 119.3 | 135.5 | 148.3 | 151.5
357 | 263 | 324.8 | 141.1 | 122.6 | 119.6 | 135.8 | 148.5 | 151.8
358 | 264 | 324.8 | 141.3 | 122.9 | 119.8 | 136.2 | 148.8 | 152.1
359 | 265 | 324.5 | 141.5 | 123.1 | 120 | 136.5 | 149 | 152.3
360 | 266 | 324.5 | 141.7 | 123.4 | 120.3 | 136.8 | 149.2 | 152.5
361 | 267 | 324.5 | 141.9 | 123.7 | 120.5 | 137.1 | 149.4 | 152.7
362 | 268 | 324.5 | 142.1 | 124 | 120.7 | 137.4 | 149.7 | 153
363 | 269 | 324.5 | 142.3 | 124.2 | 120.9 | 137.7 | 149.9 | 153.2
364 | 270 | 324.4 | 142.6 | 124.5 | 121.1 | 138.1 | 150.1 | 153.4
365 | 271 | 324.4 | 142.8 | 124.8 | 121.3 | 138.4 | 150.4 | 153.6
366 | 272 | 324.3 | 143 | 125 | 121.5 | 138.7 | 150.6 | 153.8
367 | 273 | 324.3 | 143.2 | 125.3 | 121.7 | 139.1 | 150.8 | 154.1
368 | 274 | 324.3 | 143.5 | 125.6 | 121.9 | 139.4 | 151 | 154.3
369 | 275 | 324.2 | 143.7 | 125.9 | 122.1 | 139.7 | 151.2 | 154.5
370 | 276 | 324.1 | 144 | 126.2 | 122.3 | 140 | 151.5 | 154.8
371 | 277 | 324.1 | 144.2 | 126.5 | 122.5 | 140.4 | 151.7 | 155
372 | 278 | 324.1 | 144.4 | 126.8 | 122.7 | 140.7 | 151.9 | 155.2
373 | 279 | 324 | 144.7 | 127.1 | 122.9 | 141 | 152.1 | 155.4
374 | 280 | 324.1 | 145 | 127.3 | 123.1 | 141.3 | 152.3 | 155.7
375 | 281 | 324.1 | 145.2 | 127.6 | 123.3 | 141.7 | 152.5 | 155.9
376 | 282 | 324 | 145.5 | 127.9 | 123.4 | 142 | 152.7 | 156.1
377 | 283 | 324 | 145.7 | 128.2 | 123.5 | 142.3 | 153 | 156.3
378 | 284 | 324 | 146 | 128.5 | 123.5 | 142.6 | 153.2 | 156.5
379 | 285 | 324 | 146.2 | 128.8 | 123.6 | 142.9 | 153.4 | 156.8
380 | 286 | 324 | 146.5 | 129.1 | 123.7 | 143.2 | 153.6 | 157
381 | 287 | 324.1 | 146.8 | 129.4 | 124 | 143.5 | 153.8 | 157.2
382 | 288 | 324.1 | 147.1 | 129.6 | 124.2 | 143.7 | 154.1 | 157.4
383 | 289 | 324.2 | 147.3 | 129.9 | 124.4 | 144 | 154.3 | 157.6
384 | 290 | 324.2 | 147.6 | 130.2 | 124.7 | 144.3 | 154.5 | 157.9
385 | 291 | 324.3 | 147.9 | 130.5 | 125 | 144.5 | 154.7 | 158.1
386 | 292 | 324.2 | 148.2 | 130.7 | 125.3 | 144.8 | 154.9 | 158.3
387 | 293 | 324.3 | 148.4 | 131 | 125.6 | 145.1 | 155.1 | 158.5
388 | 294 | 324.3 | 148.7 | 131.3 | 125.9 | 145.3 | 155.3 | 158.7
389 | 295 | 324.4 | 149 | 131.6 | 126.2 | 145.6 | 155.6 | 158.9
390 | 296 | 324.5 | 149.3 | 131.8 | 126.5 | 145.8 | 155.8 | 159.1
391 | 297 | 324.5 | 149.6 | 132.1 | 126.9 | 146.1 | 156 | 159.3
392 | 298 | 324.7 | 149.8 | 132.4 | 127.2 | 146.4 | 156.2 | 159.6
393 | 299 | 324.7 | 150.1 | 132.6 | 127.5 | 146.6 | 156.4 | 159.8
394 | 300 | 324.6 | 150.4 | 132.9 | 127.8 | 146.9 | 156.6 | 160
395 | 301 | 324.6 | 150.7 | 133.1 | 128.1 | 147.1 | 156.8 | 160.2
396 | 302 | 324.8 | 151 | 133.4 | 128.4 | 147.4 | 157 | 160.4
397 | 303 | 324.9 | 151.3 | 133.7 | 128.7 | 147.6 | 157.2 | 160.6
398 | 304 | 325 | 151.6 | 134 | 129 | 147.9 | 157.4 | 160.8
399 | 305 | 325.2 | 151.8 | 134.2 | 129.3 | 148.2 | 157.6 | 161
400 | 306 | 325.2 | 152.1 | 134.5 | 129.7 | 148.5 | 157.8 | 161.2
401 | 307 | 325.3 | 152.4 | 134.8 | 130.1 | 148.7 | 158 | 161.4
402 | 308 | 325.4 | 152.7 | 135.1 | 130.6 | 149 | 158.2 | 161.6
403 | 309 | 325.4 | 153 | 135.4 | 130.9 | 149.3 | 158.4 | 161.8
404 | 310 | 325.4 | 153.3 | 135.7 | 131.3 | 149.6 | 158.6 | 162
405 | 311 | 325.3 | 153.6 | 136 | 131.6 | 149.9 | 158.8 | 162.2
406 | 312 | 325.3 | 153.8 | 136.3 | 132 | 150.1 | 159 | 162.4
407 | 313 | 325.3 | 154.1 | 136.6 | 132.4 | 150.4 | 159.3 | 162.5
408 | 314 | 325.3 | 154.4 | 136.9 | 132.8 | 150.7 | 159.5 | 162.7
409 | 315 | 325.3 | 154.7 | 137.2 | 133.1 | 151 | 159.7 | 162.9
410 | 316 | 325.3 | 155 | 137.5 | 133.5 | 151.2 | 159.9 | 163.1
411 | 317 | 325.2 | 155.2 | 137.8 | 133.8 | 151.5 | 160 | 163.3
412 | 318 | 325.2 | 155.5 | 138.1 | 134.2 | 151.7 | 160.2 | 163.5
413 | 319 | 325.3 | 155.8 | 138.4 | 134.6 | 152 | 160.4 | 163.7
414 | 320 | 325.3 | 156.1 | 138.7 | 134.9 | 152.3 | 160.6 | 163.9
415 | 321 | 325.4 | 156.4 | 139 | 135.3 | 152.5 | 160.8 | 164.1
416 | 322 | 325.4 | 156.6 | 139.3 | 135.7 | 152.8 | 161 | 164.3
417 | 323 | 325.4 | 156.9 | 139.6 | 136.1 | 153 | 161.2 | 164.5
418 | 324 | 325.4 | 157.2 | 139.9 | 136.5 | 153.3 | 161.4 | 164.7
419 | 325 | 325.4 | 157.5 | 140.2 | 136.9 | 153.5 | 161.6 | 164.9
420 | 326 | 325.3 | 157.8 | 140.5 | 137.2 | 153.7 | 161.8 | 165.1
421 | 327 | 325.3 | 158.1 | 140.8 | 137.5 | 154 | 162 | 165.2
422 | 328 | 325.3 | 158.3 | 141.1 | 137.8 | 154.2 | 162.2 | 165.4
423 | 329 | 325.3 | 158.6 | 141.4 | 138.2 | 154.5 | 162.4 | 165.6
424 | 330 | 325.2 | 158.9 | 141.6 | 138.5 | 154.7 | 162.6 | 165.8
425 | 331 | 325.3 | 159.2 | 141.9 | 138.8 | 155 | 162.8 | 166
426 | 332 | 325.1 | 159.5 | 142.2 | 139.2 | 155.3 | 163 | 166.2
427 | 333 | 324.9 | 159.8 | 142.5 | 139.5 | 155.5 | 163.2 | 166.4
428 | 334 | 324.9 | 160 | 142.7 | 139.8 | 155.8 | 163.4 | 166.6
429 | 335 | 324.9 | 160.3 | 143 | 140.1 | 156 | 163.6 | 166.8
430 | 336 | 324.9 | 160.6 | 143.3 | 140.5 | 156.3 | 163.8 | 166.9
431 | 337 | 324.9 | 160.9 | 143.5 | 140.8 | 156.6 | 164 | 167.2
432 | 338 | 324.9 | 161.2 | 143.7 | 141.2 | 156.8 | 164.2 | 167.4
433 | 339 | 325 | 161.4 | 144 | 141.5 | 157 | 164.4 | 167.5
434 | 340 | 325 | 161.7 | 144.2 | 141.8 | 157.3 | 164.5 | 167.7
435 | 341 | 324.9 | 162 | 144.4 | 142.1 | 157.5 | 164.7 | 167.9
436 | 342 | 324.8 | 162.3 | 144.5 | 142.5 | 157.8 | 164.9 | 168.1
437 | 343 | 324.8 | 162.5 | 144.6 | 142.8 | 158.1 | 165.1 | 168.3
438 | 344 | 324.9 | 162.8 | 144.8 | 143.1 | 158.3 | 165.3 | 168.5
439 | 345 | 324.9 | 163.1 | 145.1 | 143.5 | 158.6 | 165.4 | 168.7
440 | 346 | 324.8 | 163.4 | 145.4 | 143.8 | 158.9 | 165.6 | 168.9
441 | 347 | 324.9 | 163.6 | 145.8 | 144.1 | 159.2 | 165.7 | 169.1
442 | 348 | 324.9 | 163.9 | 146.1 | 144.5 | 159.5 | 166 | 169.3
443 | 349 | 324.9 | 164.2 | 146.5 | 144.7 | 159.8 | 166.1 | 169.5
444 | 350 | 325 | 164.5 | 146.8 | 145 | 160.1 | 166.3 | 169.7
445 | 351 | 324.9 | 164.7 | 147.2 | 145.2 | 160.4 | 166.5 | 169.9
446 | 352 | 324.8 | 165 | 147.5 | 145.5 | 160.7 | 166.7 | 170.1
447 | 353 | 324.8 | 165.2 | 147.8 | 145.8 | 161 | 166.8 | 170.3
448 | 354 | 324.9 | 165.5 | 148.1 | 146.1 | 161.3 | 167 | 170.5
449 | 355 | 325 | 165.8 | 148.4 | 146.4 | 161.6 | 167.2 | 170.6
450 | 356 | 324.9 | 166 | 148.7 | 146.8 | 161.9 | 167.4 | 170.8
451 | 357 | 324.9 | 166.3 | 149 | 147.2 | 162.2 | 167.6 | 171
452 | 358 | 324.9 | 166.6 | 149.4 | 147.6 | 162.5 | 167.7 | 171.3
453 | 359 | 324.9 | 166.8 | 149.7 | 148 | 162.7 | 167.9 | 171.5
454 | 360 | 324.9 | 167.1 | 150 | 148.4 | 163 | 168.1 | 171.7
455 | 361 | 325 | 167.3 | 150.3 | 148.7 | 163.3 | 168.2 | 171.8
456 | 362 | 324.9 | 167.6 | 150.5 | 149.1 | 163.6 | 168.4 | 172
457 | 363 | 324.8 | 167.8 | 150.8 | 149.5 | 163.8 | 168.5 | 172.2
458 | 364 | 324.7 | 168.1 | 151.1 | 149.8 | 164.1 | 168.7 | 172.4
459 | 365 | 324.6 | 168.3 | 151.4 | 150.1 | 164.4 | 168.9 | 172.6
460 | 366 | 324.6 | 168.6 | 151.6 | 150.5 | 164.6 | 169.1 | 172.8
461 | 367 | 324.6 | 168.8 | 151.8 | 150.8 | 164.9 | 169.3 | 173
462 | 368 | 324.6 | 169.1 | 152.1 | 151.1 | 165.1 | 169.5 | 173.2
463 | 369 | 324.5 | 169.4 | 152.3 | 151.4 | 165.4 | 169.6 | 173.4
464 | 370 | 324.4 | 169.6 | 152.6 | 151.7 | 165.6 | 169.8 | 173.6
465 | 371 | 324.4 | 169.9 | 152.9 | 152.1 | 165.9 | 170 | 173.8
466 | 372 | 324.4 | 170.1 | 153.1 | 152.4 | 166.2 | 170.2 | 174
467 | 373 | 324.5 | 170.4 | 153.3 | 152.7 | 166.4 | 170.4 | 174.2
468 | 374 | 324.5 | 170.6 | 153.5 | 153.1 | 166.7 | 170.6 | 174.3
469 | 375 | 324.4 | 170.9 | 153.7 | 153.4 | 166.9 | 170.8 | 174.5
470 | 376 | 324.5 | 171.1 | 154 | 153.7 | 167.2 | 171 | 174.7
471 | 377 | 324.5 | 171.4 | 154.3 | 154 | 167.4 | 171.2 | 174.9
472 | 378 | 324.6 | 171.7 | 154.6 | 154.3 | 167.6 | 171.4 | 175.1
473 | 379 | 324.6 | 171.9 | 154.9 | 154.6 | 167.9 | 171.6 | 175.3
474 | 380 | 324.6 | 172.2 | 155.2 | 154.9 | 168.1 | 171.8 | 175.5
475 | 381 | 324.6 | 172.4 | 155.5 | 155.2 | 168.3 | 171.9 | 175.6
476 | 382 | 324.6 | 172.7 | 155.8 | 155.5 | 168.5 | 172.1 | 175.8
477 | 383 | 324.6 | 172.9 | 156 | 155.8 | 168.7 | 172.3 | 176
478 | 384 | 324.6 | 173.2 | 156.3 | 156.1 | 169 | 172.4 | 176.3
479 | 385 | 324.7 | 173.5 | 156.6 | 156.4 | 169.2 | 172.6 | 176.5
480 | 386 | 324.7 | 173.7 | 156.9 | 156.7 | 169.4 | 172.8 | 176.6
481 | 387 | 324.7 | 174 | 157.2 | 157 | 169.6 | 173 | 176.8
482 | 388 | 324.8 | 174.2 | 157.5 | 157.3 | 169.8 | 173.2 | 177
483 | 389 | 324.8 | 174.5 | 157.8 | 157.6 | 170 | 173.3 | 177.2
484 | 390 | 324.8 | 174.8 | 158.1 | 157.9 | 170.2 | 173.5 | 177.4
485 | 391 | 324.9 | 175 | 158.4 | 158.2 | 170.5 | 173.7 | 177.6
486 | 392 | 325 | 175.3 | 158.7 | 158.5 | 170.6 | 173.9 | 177.8
487 | 393 | 325 | 175.5 | 159 | 158.8 | 170.8 | 174.1 | 178
488 | 394 | 325.1 | 175.8 | 159.3 | 159.1 | 171 | 174.3 | 178.2
489 | 395 | 325.2 | 176.1 | 159.6 | 159.4 | 171.2 | 174.5 | 178.4
490 | 396 | 325.2 | 176.3 | 159.8 | 159.6 | 171.4 | 174.7 | 178.6
491 | 397 | 325.2 | 176.6 | 160.1 | 159.9 | 171.6 | 174.9 | 178.8
492 | 398 | 325.2 | 176.8 | 160.4 | 160.2 | 171.8 | 175.1 | 179
493 | 399 | 325.1 | 177.1 | 160.7 | 160.5 | 172 | 175.3 | 179.2
494 | 400 | 325 | 177.3 | 161 | 160.8 | 172.2 | 175.4 | 179.4
495 | 401 | 325.1 | 177.6 | 161.3 | 161.1 | 172.4 | 175.6 | 179.6
496 | 402 | 325.1 | 177.8 | 161.6 | 161.3 | 172.6 | 175.8 | 179.8
497 | 403 | 325.1 | 178.1 | 161.9 | 161.6 | 172.8 | 176 | 180
498 | 404 | 325.2 | 178.3 | 162.2 | 161.9 | 173 | 176.2 | 180.2
499 | 405 | 325.2 | 178.6 | 162.5 | 162.2 | 173.2 | 176.4 | 180.4
500 | 406 | 325.1 | 178.8 | 162.8 | 162.5 | 173.4 | 176.6 | 180.5
501 | 407 | 325 | 179.1 | 163.1 | 162.8 | 173.5 | 176.7 | 180.7
502 | 408 | 324.9 | 179.3 | 163.4 | 163.1 | 173.7 | 176.9 | 180.9
503 | 409 | 324.9 | 179.6 | 163.7 | 163.3 | 173.9 | 177.1 | 181
504 | 410 | 324.8 | 179.8 | 164.1 | 163.6 | 174 | 177.3 | 181.2
505 | 411 | 324.9 | 180.1 | 164.4 | 163.9 | 174.2 | 177.5 | 181.4
506 | 412 | 324.8 | 180.3 | 164.7 | 164.1 | 174.4 | 177.7 | 181.5
507 | 413 | 324.7 | 180.6 | 165 | 164.4 | 174.5 | 177.9 | 181.7
508 | 414 | 324.7 | 180.8 | 165.3 | 164.6 | 174.7 | 178 | 181.9
509 | 415 | 324.7 | 181 | 165.6 | 164.9 | 174.9 | 178.2 | 182
510 | 416 | 324.8 | 181.3 | 165.9 | 165.1 | 175.1 | 178.3 | 182.2
511 | 417 | 324.8 | 181.5 | 166.2 | 165.4 | 175.2 | 178.5 | 182.4
512 | 418 | 324.9 | 181.8 | 166.5 | 165.7 | 175.4 | 178.7 | 182.6
513 | 419 | 324.8 | 182 | 166.8 | 165.9 | 175.6 | 178.8 | 182.8
514 | 420 | 324.7 | 182.2 | 167.1 | 166.2 | 175.8 | 179 | 183
515 | 421 | 324.8 | 182.4 | 167.4 | 166.5 | 176 | 179.2 | 183.1
516 | 422 | 324.8 | 182.7 | 167.7 | 166.7 | 176.2 | 179.3 | 183.3
517 | 423 | 324.8 | 182.9 | 167.9 | 167 | 176.3 | 179.5 | 183.5
518 | 424 | 324.7 | 183.1 | 168.2 | 167.2 | 176.5 | 179.6 | 183.7
519 | 425 | 324.7 | 183.4 | 168.5 | 167.5 | 176.7 | 179.8 | 183.8
520 | 426 | 324.6 | 183.6 | 168.7 | 167.7 | 176.9 | 180 | 184
521 | 427 | 324.6 | 183.8 | 169 | 168 | 177 | 180.2 | 184.1
522 | 428 | 324.5 | 184 | 169.3 | 168.3 | 177.2 | 180.4 | 184.3
523 | 429 | 324.5 | 184.2 | 169.6 | 168.6 | 177.4 | 180.5 | 184.5
524 | 430 | 324.5 | 184.4 | 169.8 | 168.8 | 177.5 | 180.6 | 184.6
525 | 431 | 324.6 | 184.7 | 170.1 | 169.1 | 177.7 | 180.8 | 184.8
526 | 432 | 324.7 | 184.9 | 170.4 | 169.3 | 177.9 | 181 | 185
527 | 433 | 324.6 | 185.1 | 170.6 | 169.6 | 178 | 181.2 | 185.1
528 | 434 | 324.5 | 185.3 | 170.9 | 169.8 | 178.2 | 181.3 | 185.3
529 | 435 | 324.5 | 185.5 | 171.2 | 170.1 | 178.4 | 181.5 | 185.5
530 | 436 | 324.5 | 185.8 | 171.4 | 170.4 | 178.6 | 181.6 | 185.6
531 | 437 | 324.5 | 186 | 171.7 | 170.6 | 178.8 | 181.7 | 185.7
532 | 438 | 324.5 | 186.2 | 172 | 170.9 | 179 | 181.9 | 185.9
533 | 439 | 324.5 | 186.4 | 172.2 | 171.1 | 179.2 | 182 | 186.1
534 | 440 | 324.5 | 186.6 | 172.5 | 171.4 | 179.4 | 182.2 | 186.3
535 | 441 | 324.4 | 186.8 | 172.8 | 171.6 | 179.6 | 182.3 | 186.4
536 | 442 | 324.5 | 187 | 173 | 171.9 | 179.8 | 182.5 | 186.6
537 | 443 | 324.3 | 187.2 | 173.3 | 172.2 | 180 | 182.7 | 186.7
538 | 444 | 324.2 | 187.4 | 173.5 | 172.4 | 180.2 | 182.8 | 186.9
539 | 445 | 324.1 | 187.6 | 173.8 | 172.7 | 180.5 | 183 | 187
540 | 446 | 324.2 | 187.8 | 174.1 | 172.9 | 180.7 | 183.1 | 187.2
541 | 447 | 324.2 | 188 | 174.3 | 173.2 | 180.9 | 183.3 | 187.3
542 | 448 | 324.2 | 188.2 | 174.6 | 173.4 | 181.1 | 183.4 | 187.5
543 | 449 | 324.2 | 188.4 | 174.8 | 173.6 | 181.3 | 183.6 | 187.7
544 | 450 | 324.3 | 188.6 | 175.1 | 173.9 | 181.5 | 183.8 | 187.7
545 | 451 | 324.4 | 188.8 | 175.3 | 174.1 | 181.7 | 184 | 187.9
546 | 452 | 324.5 | 189 | 175.6 | 174.4 | 181.9 | 184.2 | 188.1
547 | 453 | 324.5 | 189.2 | 175.9 | 174.6 | 182.1 | 184.4 | 188.3
548 | 454 | 324.5 | 189.4 | 176.1 | 174.9 | 182.3 | 184.5 | 188.4
549 | 455 | 324.5 | 189.6 | 176.4 | 175.1 | 182.5 | 184.7 | 188.5
550 | 456 | 324.7 | 189.8 | 176.6 | 175.4 | 182.7 | 184.8 | 188.7
551 | 457 | 324.8 | 190 | 176.9 | 175.6 | 182.9 | 184.9 | 188.8
552 | 458 | 324.9 | 190.2 | 177.1 | 175.9 | 183.1 | 185.1 | 189
553 | 459 | 325 | 190.4 | 177.4 | 176.1 | 183.3 | 185.2 | 189.1
554 | 460 | 325 | 190.6 | 177.6 | 176.4 | 183.5 | 185.4 | 189.3
555 | 461 | 325.1 | 190.8 | 177.9 | 176.6 | 183.7 | 185.5 | 189.4
556 | 462 | 325.2 | 191 | 178.1 | 176.9 | 183.9 | 185.7 | 189.6
557 | 463 | 325.2 | 191.2 | 178.4 | 177.1 | 184.1 | 185.9 | 189.7
558 | 464 | 325.3 | 191.4 | 178.6 | 177.4 | 184.3 | 186.1 | 189.9
559 | 465 | 325.3 | 191.6 | 178.9 | 177.6 | 184.5 | 186.3 | 190
560 | 466 | 325.4 | 191.8 | 179.1 | 177.8 | 184.6 | 186.5 | 190.2
561 | 467 | 325.4 | 191.9 | 179.4 | 178.1 | 184.8 | 186.6 | 190.4
562 | 468 | 325.4 | 192.1 | 179.6 | 178.3 | 185 | 186.8 | 190.5
563 | 469 | 325.4 | 192.3 | 179.8 | 178.5 | 185.2 | 187 | 190.6
564 | 470 | 325.4 | 192.5 | 180.1 | 178.8 | 185.3 | 187.2 | 190.8
565 | 471 | 325.4 | 192.7 | 180.3 | 179 | 185.5 | 187.4 | 191
566 | 472 | 325.4 | 192.9 | 180.5 | 179.3 | 185.7 | 187.5 | 191.1
567 | 473 | 325.4 | 193.1 | 180.8 | 179.5 | 185.8 | 187.7 | 191.3
568 | 474 | 325.4 | 193.3 | 181 | 179.7 | 186 | 187.8 | 191.4
569 | 475 | 325.4 | 193.5 | 181.2 | 180 | 186.1 | 187.9 | 191.6
570 | 476 | 325.3 | 193.7 | 181.5 | 180.2 | 186.3 | 188.1 | 191.7
571 | 477 | 325.3 | 194 | 181.7 | 180.4 | 186.5 | 188.3 | 191.9
572 | 478 | 325.3 | 194.2 | 181.9 | 180.6 | 186.6 | 188.4 | 192
573 | 479 | 325.3 | 194.4 | 182.1 | 180.9 | 186.8 | 188.6 | 192.2
574 | 480 | 325.4 | 194.5 | 182.3 | 181.1 | 186.9 | 188.8 | 192.3
575 | 481 | 325.5 | 194.8 | 182.6 | 181.3 | 187.1 | 188.9 | 192.5
576 | 482 | 325.4 | 195 | 182.8 | 181.5 | 187.2 | 189 | 192.6
577 | 483 | 325.3 | 195.2 | 183 | 181.8 | 187.4 | 189.2 | 192.8
578 | 484 | 325.3 | 195.3 | 183.2 | 182 | 187.5 | 189.3 | 192.9
579 | 485 | 325.2 | 195.6 | 183.4 | 182.2 | 187.7 | 189.5 | 193.1
580 | 486 | 325.2 | 195.8 | 183.6 | 182.4 | 187.8 | 189.7 | 193.2
581 | 487 | 325.2 | 195.9 | 183.9 | 182.7 | 188 | 189.9 | 193.4
582 | 488 | 325.2 | 196.1 | 184.1 | 182.9 | 188.1 | 190 | 193.5
583 | 489 | 325.2 | 196.3 | 184.3 | 183.1 | 188.3 | 190.2 | 193.7
584 | 490 | 325.2 | 196.5 | 184.5 | 183.3 | 188.4 | 190.3 | 193.8
585 | 491 | 325.1 | 196.7 | 184.8 | 183.6 | 188.6 | 190.5 | 194
586 | 492 | 325.2 | 196.9 | 185 | 183.8 | 188.8 | 190.6 | 194.1
587 | 493 | 325.2 | 197.1 | 185.2 | 184 | 188.9 | 190.8 | 194.2
588 | 494 | 325.3 | 197.3 | 185.4 | 184.2 | 189.1 | 191 | 194.4
589 | 495 | 325.2 | 197.5 | 185.7 | 184.4 | 189.3 | 191.2 | 194.6
590 | 496 | 325.3 | 197.7 | 185.9 | 184.6 | 189.4 | 191.4 | 194.7
591 | 497 | 325.3 | 197.9 | 186.1 | 184.9 | 189.6 | 191.6 | 194.9
592 | 498 | 325.3 | 198.1 | 186.3 | 185.1 | 189.8 | 191.7 | 195
593 | 499 | 325.3 | 198.3 | 186.5 | 185.3 | 190 | 191.9 | 195.1
594 | 500 | 325.3 | 198.5 | 186.8 | 185.5 | 190.1 | 192.1 | 195.3
595 | 501 | 325.2 | 198.7 | 187 | 185.7 | 190.3 | 192.2 | 195.5
596 | 502 | 325.2 | 198.9 | 187.2 | 185.9 | 190.5 | 192.4 | 195.6
597 | 503 | 325.2 | 199.1 | 187.4 | 186.2 | 190.6 | 192.6 | 195.7
598 | 504 | 325.1 | 199.2 | 187.6 | 186.4 | 190.8 | 192.8 | 195.8
599 | 505 | 325.1 | 199.4 | 187.8 | 186.6 | 191 | 193 | 196
600 | 506 | 325.1 | 199.6 | 188 | 186.8 | 191.1 | 193.1 | 196.1
601 | 507 | 325 | 199.8 | 188.2 | 187 | 191.3 | 193.3 | 196.2
602 | 508 | 325.1 | 200 | 188.4 | 187.2 | 191.4 | 193.5 | 196.4
603 | 509 | 325.2 | 200.2 | 188.6 | 187.4 | 191.5 | 193.6 | 196.5
604 | 510 | 325.3 | 200.4 | 188.8 | 187.6 | 191.7 | 193.7 | 196.7
605 | 511 | 325.3 | 200.6 | 189 | 187.8 | 191.8 | 193.9 | 196.8
606 | 512 | 325.2 | 200.7 | 189.2 | 188 | 192 | 194 | 196.9
607 | 513 | 325.1 | 200.9 | 189.4 | 188.2 | 192.1 | 194.2 | 197
608 | 514 | 325.1 | 201.1 | 189.7 | 188.4 | 192.3 | 194.3 | 197.1
609 | 515 | 325.1 | 201.3 | 189.8 | 188.6 | 192.4 | 194.5 | 197.2
610 | 516 | 325.1 | 201.5 | 190.1 | 188.8 | 192.6 | 194.6 | 197.3
611 | 517 | 325 | 201.6 | 190.3 | 189 | 192.8 | 194.8 | 197.5
612 | 518 | 325 | 201.8 | 190.5 | 189.2 | 192.9 | 194.9 | 197.6
613 | 519 | 324.9 | 202 | 190.7 | 189.4 | 193.1 | 195 | 197.8
614 | 520 | 324.9 | 202.1 | 190.9 | 189.6 | 193.3 | 195.1 | 197.9
615 | 521 | 324.8 | 202.3 | 191.1 | 189.8 | 193.4 | 195.3 | 198
616 | 522 | 324.8 | 202.5 | 191.3 | 190 | 193.6 | 195.4 | 198.1
617 | 523 | 324.8 | 202.6 | 191.5 | 190.1 | 193.8 | 195.5 | 198.2
618 | 524 | 324.8 | 202.8 | 191.7 | 190.3 | 194 | 195.7 | 198.3
619 | 525 | 324.9 | 202.9 | 191.9 | 190.5 | 194.2 | 195.8 | 198.5
620 | 526 | 324.9 | 203.1 | 192.1 | 190.7 | 194.4 | 195.9 | 198.7
621 | 527 | 324.9 | 203.2 | 192.3 | 190.9 | 194.5 | 196 | 198.8
622 | 528 | 324.8 | 203.4 | 192.5 | 191.1 | 194.7 | 196.2 | 198.8
623 | 529 | 324.7 | 203.6 | 192.7 | 191.3 | 194.9 | 196.3 | 199
624 | 530 | 324.8 | 203.7 | 192.9 | 191.5 | 195 | 196.5 | 199
625 | 531 | 324.7 | 203.8 | 193.1 | 191.7 | 195.2 | 196.6 | 199.1
626 | 532 | 324.7 | 204 | 193.3 | 191.8 | 195.3 | 196.8 | 199.3
627 | 533 | 324.7 | 204.2 | 193.5 | 192 | 195.5 | 197 | 199.4
628 | 534 | 324.7 | 204.3 | 193.7 | 192.2 | 195.6 | 197.2 | 199.5
629 | 535 | 324.6 | 204.5 | 193.9 | 192.4 | 195.8 | 197.3 | 199.6
630 | 536 | 324.5 | 204.6 | 194 | 192.6 | 195.9 | 197.4 | 199.7
631 | 537 | 324.5 | 204.8 | 194.3 | 192.7 | 196.1 | 197.6 | 199.8
632 | 538 | 324.5 | 205 | 194.4 | 192.9 | 196.2 | 197.8 | 200
633 | 539 | 324.6 | 205.1 | 194.6 | 193.1 | 196.3 | 198 | 200.1
634 | 540 | 324.6 | 205.3 | 194.8 | 193.3 | 196.5 | 198.2 | 200.2
635 | 541 | 324.5 | 205.5 | 195 | 193.4 | 196.6 | 198.4 | 200.3
636 | 542 | 324.5 | 205.6 | 195.2 | 193.6 | 196.7 | 198.5 | 200.4
637 | 543 | 324.6 | 205.8 | 195.4 | 193.8 | 196.9 | 198.7 | 200.5
638 | 544 | 324.7 | 206 | 195.6 | 194 | 197 | 198.8 | 200.6
639 | 545 | 324.6 | 206.1 | 195.8 | 194.1 | 197.1 | 199 | 200.7
640 | 546 | 324.5 | 206.3 | 195.9 | 194.3 | 197.2 | 199.1 | 200.8
641 | 547 | 324.5 | 206.5 | 196.1 | 194.5 | 197.4 | 199.3 | 200.9
642 | 548 | 324.4 | 206.6 | 196.3 | 194.7 | 197.5 | 199.5 | 201
643 | 549 | 324.5 | 206.8 | 196.5 | 194.8 | 197.6 | 199.7 | 201.1
644 | 550 | 324.4 | 207 | 196.7 | 195 | 197.7 | 199.9 | 201.2
645 | 551 | 324.4 | 207.2 | 196.9 | 195.2 | 197.8 | 200.1 | 201.3
646 | 552 | 324.4 | 207.3 | 197.1 | 195.3 | 197.9 | 200.3 | 201.4
647 | 553 | 324.5 | 207.5 | 197.3 | 195.5 | 198.1 | 200.4 | 201.5
648 | 554 | 324.6 | 207.7 | 197.4 | 195.7 | 198.2 | 200.5 | 201.6
649 | 555 | 324.6 | 207.9 | 197.6 | 195.9 | 198.3 | 200.7 | 201.7
650 | 556 | 324.6 | 208 | 197.8 | 196 | 198.5 | 200.9 | 201.9
651 | 557 | 324.7 | 208.2 | 198 | 196.2 | 198.6 | 201.2 | 202
652 | 558 | 324.7 | 208.4 | 198.2 | 196.4 | 198.7 | 201.4 | 202.1
653 | 559 | 324.7 | 208.6 | 198.4 | 196.6 | 198.8 | 201.6 | 202.3
654 | 560 | 324.7 | 208.7 | 198.5 | 196.7 | 198.9 | 201.7 | 202.4
655 | 561 | 324.7 | 208.9 | 198.7 | 196.9 | 199.1 | 201.8 | 202.5
656 | 562 | 324.7 | 209.1 | 198.9 | 197.1 | 199.2 | 202 | 202.5
657 | 563 | 324.7 | 209.2 | 199.1 | 197.2 | 199.3 | 202.2 | 202.6
658 | 564 | 324.7 | 209.4 | 199.3 | 197.4 | 199.4 | 202.3 | 202.7
659 | 565 | 324.6 | 209.6 | 199.4 | 197.5 | 199.5 | 202.5 | 202.8
660 | 566 | 324.6 | 209.7 | 199.6 | 197.7 | 199.7 | 202.7 | 202.9
661 | 567 | 324.5 | 209.9 | 199.8 | 197.9 | 199.8 | 202.8 | 202.9
662 | 568 | 324.5 | 210 | 200 | 198 | 199.9 | 203 | 203.1
663 | 569 | 324.5 | 210.2 | 200.2 | 198.2 | 200 | 203.1 | 203.2
664 | 570 | 324.5 | 210.3 | 200.3 | 198.3 | 200.2 | 203.2 | 203.2
665 | 571 | 324.4 | 210.5 | 200.5 | 198.5 | 200.3 | 203.4 | 203.3
666 | 572 | 324.5 | 210.7 | 200.7 | 198.7 | 200.5 | 203.6 | 203.4
667 | 573 | 324.6 | 210.8 | 200.9 | 198.8 | 200.6 | 203.8 | 203.5
668 | 574 | 324.5 | 211 | 201.1 | 199 | 200.7 | 203.9 | 203.6
669 | 575 | 324.5 | 211.1 | 201.2 | 199.2 | 200.9 | 204 | 203.7
670 | 576 | 324.5 | 211.3 | 201.4 | 199.3 | 201 | 204.1 | 203.7
671 | 577 | 324.6 | 211.4 | 201.6 | 199.5 | 201.2 | 204.2 | 203.8
672 | 578 | 324.6 | 211.6 | 201.8 | 199.6 | 201.4 | 204.3 | 204
673 | 579 | 324.5 | 211.7 | 201.9 | 199.8 | 201.5 | 204.4 | 204.1
674 | 580 | 324.4 | 211.9 | 202.1 | 200 | 201.7 | 204.5 | 204.1
675 | 581 | 324.3 | 212 | 202.3 | 200.1 | 201.8 | 204.6 | 204.2
676 | 582 | 324.2 | 212.1 | 202.5 | 200.3 | 202 | 204.8 | 204.3
677 | 583 | 324.2 | 212.3 | 202.6 | 200.5 | 202.2 | 204.9 | 204.4
678 | 584 | 324.2 | 212.4 | 202.8 | 200.6 | 202.3 | 205 | 204.5
679 | 585 | 324.2 | 212.5 | 203 | 200.8 | 202.5 | 205.1 | 204.6
680 | 586 | 324.2 | 212.7 | 203.2 | 201 | 202.7 | 205.3 | 204.6
681 | 587 | 324.2 | 212.8 | 203.3 | 201.1 | 202.8 | 205.4 | 204.7
682 | 588 | 324.2 | 212.9 | 203.5 | 201.3 | 203 | 205.6 | 204.8
683 | 589 | 324.2 | 213.1 | 203.7 | 201.5 | 203.2 | 205.7 | 204.9
684 | 590 | 324.2 | 213.2 | 203.9 | 201.6 | 203.3 | 205.8 | 205
685 | 591 | 324.2 | 213.3 | 204 | 201.8 | 203.5 | 206 | 205.1
686 | 592 | 324.2 | 213.5 | 204.2 | 201.9 | 203.7 | 206.1 | 205.2
687 | 593 | 324.2 | 213.6 | 204.3 | 202.1 | 203.8 | 206.3 | 205.2
688 | 594 | 324.1 | 213.7 | 204.5 | 202.3 | 204 | 206.4 | 205.3
689 | 595 | 324.1 | 213.9 | 204.7 | 202.4 | 204.1 | 206.6 | 205.4
690 | 596 | 324.1 | 214 | 204.8 | 202.6 | 204.3 | 206.8 | 205.5
691 | 597 | 324 | 214.1 | 205 | 202.7 | 204.4 | 206.9 | 205.5
692 | 598 | 324 | 214.3 | 205.2 | 202.9 | 204.6 | 207.1 | 205.6
693 | 599 | 324 | 214.4 | 205.3 | 203 | 204.7 | 207.2 | 205.7
694 | 600 | 324.1 | 214.5 | 205.5 | 203.2 | 204.9 | 207.4 | 205.7
695 | 601 | 324.1 | 214.7 | 205.6 | 203.3 | 205 | 207.6 | 205.7
696 | 602 | 324.1 | 214.8 | 205.8 | 203.5 | 205.2 | 207.7 | 205.8
697 | 603 | 324.1 | 215 | 206 | 203.6 | 205.3 | 207.8 | 205.9
698 | 604 | 324.1 | 215.1 | 206.1 | 203.8 | 205.5 | 207.9 | 206
699 | 605 | 324.2 | 215.2 | 206.3 | 203.9 | 205.6 | 208.1 | 206.1
700 | 606 | 324.3 | 215.4 | 206.4 | 204.1 | 205.7 | 208.2 | 206.2
701 | 607 | 324.3 | 215.5 | 206.6 | 204.2 | 205.8 | 208.4 | 206.3
702 | 608 | 324.4 | 215.7 | 206.8 | 204.4 | 206 | 208.4 | 206.3
703 | 609 | 324.3 | 215.8 | 206.9 | 204.5 | 206.1 | 208.5 | 206.4
704 | 610 | 324.2 | 216 | 207.1 | 204.7 | 206.2 | 208.7 | 206.5
705 | 611 | 324.2 | 216.1 | 207.2 | 204.8 | 206.4 | 208.7 | 206.6
706 | 612 | 324.2 | 216.3 | 207.4 | 205 | 206.5 | 208.9 | 206.7
707 | 613 | 324.2 | 216.4 | 207.6 | 205.1 | 206.6 | 209 | 206.7
708 | 614 | 324.2 | 216.6 | 207.7 | 205.2 | 206.8 | 209.1 | 206.8
709 | 615 | 324.3 | 216.7 | 207.9 | 205.4 | 206.9 | 209.2 | 206.9
710 | 616 | 324.2 | 216.8 | 208 | 205.5 | 207.1 | 209.2 | 206.9
711 | 617 | 324.1 | 217 | 208.2 | 205.7 | 207.2 | 209.2 | 207
712 | 618 | 324.2 | 217.1 | 208.3 | 205.8 | 207.3 | 209.4 | 207.1
713 | 619 | 324.3 | 217.3 | 208.5 | 206 | 207.5 | 209.5 | 207.2
714 | 620 | 324.4 | 217.4 | 208.7 | 206.1 | 207.6 | 209.6 | 207.2
715 | 621 | 324.4 | 217.5 | 208.8 | 206.3 | 207.8 | 209.8 | 207.3
716 | 622 | 324.3 | 217.6 | 209 | 206.4 | 207.9 | 209.9 | 207.4
717 | 623 | 324.3 | 217.8 | 209.1 | 206.6 | 208.1 | 210 | 207.5
718 | 624 | 324.2 | 217.9 | 209.3 | 206.7 | 208.2 | 210.1 | 207.6
719 | 625 | 324.2 | 218 | 209.4 | 206.9 | 208.4 | 210.1 | 207.7
720 | 626 | 324.4 | 218.1 | 209.6 | 207 | 208.5 | 210.2 | 207.8
721 | 627 | 324.5 | 218.3 | 209.8 | 207.1 | 208.7 | 210.4 | 207.9
722 | 628 | 324.6 | 218.4 | 209.9 | 207.3 | 208.8 | 210.5 | 208
723 | 629 | 324.6 | 218.5 | 210.1 | 207.4 | 209 | 210.7 | 208.1
724 | 630 | 324.6 | 218.7 | 210.2 | 207.6 | 209.1 | 210.8 | 208.1
725 | 631 | 324.7 | 218.8 | 210.4 | 207.7 | 209.2 | 210.9 | 208.2
726 | 632 | 324.8 | 218.9 | 210.5 | 207.8 | 209.4 | 211.1 | 208.3
727 | 633 | 324.9 | 219 | 210.7 | 208 | 209.5 | 211.2 | 208.4
728 | 634 | 324.9 | 219.2 | 210.8 | 208.1 | 209.7 | 211.4 | 208.5
729 | 635 | 324.9 | 219.3 | 211 | 208.2 | 209.8 | 211.5 | 208.6
730 | 636 | 324.9 | 219.4 | 211.1 | 208.4 | 209.9 | 211.7 | 208.7
731 | 637 | 324.9 | 219.6 | 211.3 | 208.5 | 210.1 | 211.7 | 208.7
732 | 638 | 324.9 | 219.7 | 211.4 | 208.6 | 210.2 | 211.9 | 208.8
733 | 639 | 325 | 219.8 | 211.5 | 208.8 | 210.3 | 212 | 208.9
734 | 640 | 325.1 | 220 | 211.7 | 208.9 | 210.5 | 212 | 209
735 | 641 | 325.2 | 220.1 | 211.8 | 209.1 | 210.6 | 212.1 | 209
736 | 642 | 325.2 | 220.3 | 212 | 209.2 | 210.7 | 212.2 | 209.1
737 | 643 | 325.2 | 220.4 | 212.1 | 209.3 | 210.9 | 212.3 | 209.2
738 | 644 | 325.2 | 220.5 | 212.3 | 209.5 | 211 | 212.4 | 209.3
739 | 645 | 325.2 | 220.6 | 212.4 | 209.6 | 211.1 | 212.5 | 209.3
740 | 646 | 325.1 | 220.8 | 212.5 | 209.7 | 211.3 | 212.6 | 209.4
741 | 647 | 325.1 | 220.9 | 212.7 | 209.9 | 211.4 | 212.7 | 209.5
742 | 648 | 325.1 | 221 | 212.8 | 210 | 211.5 | 212.8 | 209.6
743 | 649 | 325.1 | 221.2 | 213 | 210.1 | 211.6 | 212.9 | 209.7
744 | 650 | 325 | 221.3 | 213.1 | 210.3 | 211.8 | 213 | 209.8
745 | 651 | 325 | 221.4 | 213.3 | 210.4 | 211.9 | 213.2 | 209.9
746 | 652 | 324.9 | 221.6 | 213.4 | 210.5 | 212 | 213.4 | 209.9
747 | 653 | 325 | 221.7 | 213.5 | 210.7 | 212.1 | 213.6 | 210
748 | 654 | 325 | 221.9 | 213.7 | 210.8 | 212.3 | 213.7 | 210.1
749 | 655 | 325 | 222 | 213.8 | 210.9 | 212.4 | 213.9 | 210.1
750 | 656 | 325 | 222.1 | 213.9 | 211 | 212.5 | 214 | 210.2
751 | 657 | 325 | 222.3 | 214.1 | 211.2 | 212.6 | 214.2 | 210.3
752 | 658 | 325 | 222.4 | 214.2 | 211.3 | 212.7 | 214.4 | 210.4
753 | 659 | 324.9 | 222.5 | 214.3 | 211.4 | 212.8 | 214.5 | 210.5
754 | 660 | 324.8 | 222.6 | 214.5 | 211.6 | 213 | 214.5 | 210.6
755 | 661 | 324.8 | 222.8 | 214.6 | 211.7 | 213.1 | 214.6 | 210.7
756 | 662 | 324.9 | 222.9 | 214.7 | 211.8 | 213.2 | 214.6 | 210.7
757 | 663 | 325 | 223.1 | 214.9 | 211.9 | 213.3 | 214.8 | 210.8
758 | 664 | 325 | 223.2 | 215 | 212.1 | 213.4 | 214.9 | 210.9
759 | 665 | 325.1 | 223.3 | 215.1 | 212.2 | 213.5 | 215.1 | 211
760 | 666 | 325.2 | 223.5 | 215.3 | 212.3 | 213.6 | 215.3 | 211.1
761 | 667 | 325.2 | 223.6 | 215.4 | 212.5 | 213.7 | 215.4 | 211.2
762 | 668 | 325.1 | 223.7 | 215.5 | 212.6 | 213.9 | 215.5 | 211.2
763 | 669 | 325.1 | 223.8 | 215.7 | 212.7 | 214 | 215.6 | 211.3
764 | 670 | 325.1 | 224 | 215.8 | 212.8 | 214.1 | 215.7 | 211.4
765 | 671 | 325.1 | 224.1 | 215.9 | 213 | 214.2 | 215.8 | 211.5
766 | 672 | 325.1 | 224.2 | 216.1 | 213.1 | 214.3 | 215.9 | 211.6
767 | 673 | 325.1 | 224.3 | 216.2 | 213.2 | 214.4 | 216 | 211.7
768 | 674 | 325.1 | 224.5 | 216.3 | 213.4 | 214.6 | 216.1 | 211.7
769 | 675 | 325 | 224.6 | 216.5 | 213.5 | 214.7 | 216.1 | 211.8
770 | 676 | 325 | 224.7 | 216.6 | 213.6 | 214.8 | 216.2 | 211.9
771 | 677 | 325.1 | 224.8 | 216.7 | 213.7 | 214.9 | 216.3 | 212
772 | 678 | 325.1 | 225 | 216.9 | 213.9 | 215.1 | 216.4 | 212
773 | 679 | 325 | 225.1 | 217 | 214 | 215.2 | 216.4 | 212.1
774 | 680 | 325 | 225.2 | 217.1 | 214.1 | 215.3 | 216.5 | 212.2
775 | 681 | 324.8 | 225.3 | 217.3 | 214.2 | 215.4 | 216.7 | 212.3
776 | 682 | 324.7 | 225.5 | 217.4 | 214.4 | 215.6 | 216.8 | 212.4
777 | 683 | 324.7 | 225.6 | 217.5 | 214.5 | 215.7 | 216.8 | 212.5
778 | 684 | 324.8 | 225.7 | 217.7 | 214.6 | 215.8 | 216.9 | 212.5
779 | 685 | 324.7 | 225.8 | 217.8 | 214.7 | 215.9 | 217 | 212.6
780 | 686 | 324.6 | 225.9 | 217.9 | 214.9 | 216.1 | 217.1 | 212.7
781 | 687 | 324.6 | 226 | 218 | 215 | 216.2 | 217.1 | 212.8
782 | 688 | 324.6 | 226.1 | 218.2 | 215.1 | 216.4 | 217.2 | 212.9
783 | 689 | 324.5 | 226.2 | 218.3 | 215.2 | 216.5 | 217.2 | 212.9
784 | 690 | 324.4 | 226.3 | 218.4 | 215.3 | 216.6 | 217.2 | 213
785 | 691 | 324.3 | 226.4 | 218.6 | 215.5 | 216.8 | 217.1 | 213.1
786 | 692 | 324.3 | 226.5 | 218.7 | 215.6 | 216.9 | 217.2 | 213.2
787 | 693 | 324.4 | 226.6 | 218.8 | 215.7 | 217.1 | 217.3 | 213.3
788 | 694 | 324.4 | 226.7 | 219 | 215.8 | 217.2 | 217.4 | 213.3
789 | 695 | 324.4 | 226.8 | 219.1 | 216 | 217.4 | 217.4 | 213.4
790 | 696 | 324.4 | 226.9 | 219.2 | 216.1 | 217.5 | 217.5 | 213.5
791 | 697 | 324.5 | 227 | 219.3 | 216.2 | 217.7 | 217.6 | 213.6
792 | 698 | 324.6 | 227.1 | 219.5 | 216.3 | 217.8 | 217.6 | 213.7
793 | 699 | 324.6 | 227.2 | 219.6 | 216.4 | 218 | 217.7 | 213.7
794 | 700 | 324.7 | 227.3 | 219.7 | 216.5 | 218.2 | 217.8 | 213.8
795 | 701 | 324.8 | 227.4 | 219.9 | 216.7 | 218.3 | 217.8 | 213.9
796 | 702 | 324.9 | 227.5 | 220 | 216.8 | 218.5 | 217.8 | 214
797 | 703 | 325.1 | 227.6 | 220.1 | 216.9 | 218.7 | 217.9 | 214.1
798 | 704 | 325.2 | 227.7 | 220.2 | 217 | 218.8 | 217.9 | 214.2
799 | 705 | 325.3 | 227.8 | 220.4 | 217.1 | 219 | 218 | 214.2
800 | 706 | 325.4 | 227.9 | 220.5 | 217.3 | 219.2 | 218.1 | 214.3
801 | 707 | 325.5 | 228 | 220.6 | 217.4 | 219.3 | 218.2 | 214.4
802 | 708 | 325.6 | 228.2 | 220.7 | 217.5 | 219.5 | 218.4 | 214.5
803 | 709 | 325.7 | 228.3 | 220.8 | 217.6 | 219.7 | 218.6 | 214.6
804 | 710 | 325.6 | 228.4 | 220.9 | 217.7 | 219.8 | 218.7 | 214.7
805 | 711 | 325.7 | 228.5 | 221.1 | 217.8 | 220 | 218.7 | 214.8
806 | 712 | 325.8 | 228.6 | 221.2 | 217.9 | 220.2 | 218.8 | 214.9
807 | 713 | 325.9 | 228.8 | 221.3 | 218.1 | 220.4 | 218.9 | 215
808 | 714 | 325.9 | 228.9 | 221.4 | 218.2 | 220.6 | 219.1 | 215
809 | 715 | 325.9 | 229 | 221.5 | 218.3 | 220.8 | 219.3 | 215.1
810 | 716 | 326 | 229.1 | 221.7 | 218.4 | 221 | 219.5 | 215.2
811 | 717 | 326 | 229.2 | 221.8 | 218.5 | 221.3 | 219.5 | 215.3
812 | 718 | 326.1 | 229.4 | 221.9 | 218.6 | 221.5 | 219.5 | 215.4
813 | 719 | 326 | 229.5 | 222 | 218.7 | 221.7 | 219.6 | 215.5
814 | 720 | 326 | 229.6 | 222.1 | 218.9 | 222 | 219.6 | 215.6
815 | 721 | 326 | 229.7 | 222.3 | 219 | 222.2 | 219.7 | 215.6
816 | 722 | 326 | 229.8 | 222.4 | 219.1 | 222.3 | 219.8 | 215.7
817 | 723 | 326.1 | 229.9 | 222.5 | 219.2 | 222.5 | 219.8 | 215.8
818 | 724 | 326.1 | 230 | 222.6 | 219.3 | 222.7 | 219.9 | 215.9
819 | 725 | 326.2 | 230.1 | 222.7 | 219.4 | 222.8 | 220 | 216
820 | 726 | 326.2 | 230.2 | 222.8 | 219.5 | 222.9 | 220.1 | 216.1
821 | 727 | 326.2 | 230.3 | 223 | 219.6 | 223.1 | 220.1 | 216.1
822 | 728 | 326.2 | 230.4 | 223.1 | 219.7 | 223.3 | 220.1 | 216.2
823 | 729 | 326.1 | 230.5 | 223.2 | 219.8 | 223.4 | 220.3 | 216.3
824 | 730 | 326.1 | 230.5 | 223.3 | 220 | 223.5 | 220.5 | 216.4
825 | 731 | 326.1 | 230.6 | 223.4 | 220.1 | 223.7 | 220.6 | 216.5
826 | 732 | 326 | 230.7 | 223.6 | 220.2 | 223.8 | 220.6 | 216.6
827 | 733 | 325.9 | 230.8 | 223.7 | 220.3 | 223.9 | 220.8 | 216.7
828 | 734 | 325.8 | 230.9 | 223.8 | 220.4 | 224 | 220.8 | 216.7
829 | 735 | 325.7 | 231 | 223.9 | 220.5 | 224.1 | 220.9 | 216.8
830 | 736 | 325.7 | 231.1 | 224 | 220.6 | 224.2 | 221.1 | 216.9
831 | 737 | 325.6 | 231.2 | 224.1 | 220.7 | 224.3 | 221.2 | 217
832 | 738 | 325.7 | 231.3 | 224.2 | 220.8 | 224.3 | 221.3 | 217.1
833 | 739 | 325.6 | 231.4 | 224.4 | 220.9 | 224.4 | 221.3 | 217.2
834 | 740 | 325.6 | 231.5 | 224.5 | 221 | 224.4 | 221.4 | 217.3
835 | 741 | 325.5 | 231.6 | 224.6 | 221.1 | 224.4 | 221.6 | 217.3
836 | 742 | 325.4 | 231.7 | 224.7 | 221.2 | 224.5 | 221.5 | 217.4
837 | 743 | 325.4 | 231.8 | 224.8 | 221.3 | 224.6 | 221.6 | 217.5
838 | 744 | 325.4 | 231.9 | 225 | 221.5 | 224.7 | 221.6 | 217.6
839 | 745 | 325.3 | 232 | 225.1 | 221.6 | 224.8 | 221.6 | 217.7
840 | 746 | 325.3 | 232.1 | 225.2 | 221.7 | 224.8 | 221.6 | 217.7
841 | 747 | 325.2 | 232.2 | 225.3 | 221.8 | 224.9 | 221.7 | 217.8
842 | 748 | 325.2 | 232.3 | 225.4 | 221.9 | 224.9 | 221.7 | 217.9
843 | 749 | 325.2 | 232.4 | 225.5 | 222 | 225 | 221.8 | 218
844 | 750 | 325.2 | 232.5 | 225.6 | 222.1 | 225.1 | 221.9 | 218.1
845 | 751 | 325.1 | 232.6 | 225.7 | 222.2 | 225.2 | 222 | 218.1
846 | 752 | 325.1 | 232.7 | 225.8 | 222.3 | 225.3 | 222 | 218.2
847 | 753 | 325 | 232.8 | 226 | 222.4 | 225.4 | 222.2 | 218.3
848 | 754 | 325 | 232.9 | 226.1 | 222.5 | 225.6 | 222.2 | 218.4
849 | 755 | 325 | 233 | 226.2 | 222.6 | 225.8 | 222.2 | 218.5
850 | 756 | 325 | 233.1 | 226.3 | 222.8 | 225.9 | 222.3 | 218.5
851 | 757 | 325.1 | 233.1 | 226.4 | 222.9 | 226 | 222.3 | 218.6
852 | 758 | 325.1 | 233.2 | 226.5 | 223 | 226.1 | 222.3 | 218.7
853 | 759 | 325.1 | 233.3 | 226.6 | 223.1 | 226.1 | 222.3 | 218.7
854 | 760 | 325.1 | 233.4 | 226.7 | 223.2 | 226.1 | 222.3 | 218.8
855 | 761 | 325.1 | 233.5 | 226.8 | 223.3 | 226.2 | 222.4 | 218.9
856 | 762 | 325.2 | 233.5 | 226.9 | 223.4 | 226.4 | 222.4 | 219
857 | 763 | 325.2 | 233.6 | 227 | 223.5 | 226.5 | 222.4 | 219.1
858 | 764 | 325.2 | 233.7 | 227.2 | 223.6 | 226.6 | 222.6 | 219.2
859 | 765 | 325.2 | 233.7 | 227.3 | 223.7 | 226.7 | 222.7 | 219.2
860 | 766 | 325.2 | 233.8 | 227.4 | 223.8 | 226.8 | 222.7 | 219.3
861 | 767 | 325.2 | 233.8 | 227.5 | 223.9 | 226.8 | 222.7 | 219.4
862 | 768 | 325.1 | 233.9 | 227.6 | 224 | 227 | 222.8 | 219.5
863 | 769 | 325.1 | 234 | 227.7 | 224.1 | 227.1 | 222.9 | 219.6
864 | 770 | 325.1 | 234 | 227.8 | 224.2 | 227.2 | 222.9 | 219.6
865 | 771 | 325.1 | 234.1 | 227.9 | 224.3 | 227.3 | 223 | 219.7
866 | 772 | 325.2 | 234.2 | 228 | 224.4 | 227.4 | 223 | 219.8
867 | 773 | 325.2 | 234.3 | 228.1 | 224.5 | 227.5 | 223 | 219.9
868 | 774 | 325.3 | 234.4 | 228.2 | 224.6 | 227.6 | 223 | 220
869 | 775 | 325.3 | 234.4 | 228.3 | 224.7 | 227.7 | 223.1 | 220
870 | 776 | 325.3 | 234.5 | 228.4 | 224.8 | 227.9 | 223.2 | 220.1
871 | 777 | 325.3 | 234.6 | 228.5 | 224.9 | 228.1 | 223.4 | 220.2
872 | 778 | 325.4 | 234.7 | 228.6 | 225 | 228.2 | 223.3 | 220.3
873 | 779 | 325.5 | 234.7 | 228.7 | 225.1 | 228.3 | 223.4 | 220.3
874 | 780 | 325.6 | 234.8 | 228.8 | 225.2 | 228.5 | 223.5 | 220.4
875 | 781 | 325.7 | 234.9 | 228.9 | 225.3 | 228.6 | 223.6 | 220.5
876 | 782 | 325.8 | 235 | 229 | 225.4 | 228.7 | 223.6 | 220.6
877 | 783 | 325.9 | 235 | 229.1 | 225.5 | 228.8 | 223.6 | 220.6
878 | 784 | 325.9 | 235.1 | 229.2 | 225.6 | 229 | 223.6 | 220.7
879 | 785 | 326.1 | 235.1 | 229.3 | 225.7 | 229.1 | 223.6 | 220.8
880 | 786 | 326.3 | 235.2 | 229.4 | 225.8 | 229.2 | 223.7 | 220.9
881 | 787 | 326.3 | 235.2 | 229.5 | 225.9 | 229.2 | 223.9 | 220.9
882 | 788 | 326.3 | 235.3 | 229.6 | 226 | 229.3 | 224.1 | 221
883 | 789 | 326.4 | 235.4 | 229.7 | 226.1 | 229.3 | 224.1 | 221.1
884 | 790 | 326.5 | 235.4 | 229.8 | 226.2 | 229.3 | 224.2 | 221.2
885 | 791 | 326.4 | 235.5 | 229.9 | 226.3 | 229.3 | 224.3 | 221.3
886 | 792 | 326.4 | 235.6 | 230 | 226.4 | 229.3 | 224.4 | 221.3
887 | 793 | 326.5 | 235.7 | 230.1 | 226.5 | 229.4 | 224.4 | 221.4
888 | 794 | 326.6 | 235.8 | 230.2 | 226.6 | 229.6 | 224.5 | 221.5
889 | 795 | 326.7 | 235.9 | 230.3 | 226.7 | 229.6 | 224.6 | 221.6
890 | 796 | 326.8 | 236 | 230.4 | 226.8 | 229.6 | 224.7 | 221.6
891 | 797 | 326.9 | 236.1 | 230.5 | 226.9 | 229.6 | 224.7 | 221.7
892 | 798 | 326.9 | 236.2 | 230.6 | 226.9 | 229.7 | 224.8 | 221.8
893 | 799 | 326.9 | 236.3 | 230.7 | 227 | 229.7 | 225 | 221.9
894 | 800 | 326.9 | 236.4 | 230.8 | 227.1 | 229.8 | 225.1 | 221.9
895 | 801 | 327 | 236.5 | 230.9 | 227.2 | 229.9 | 225.1 | 222
896 | 802 | 327.1 | 236.6 | 231 | 227.3 | 230 | 225.1 | 222.1
897 | 803 | 327.1 | 236.6 | 231.1 | 227.4 | 230 | 225.1 | 222.2
898 | 804 | 327.1 | 236.7 | 231.2 | 227.5 | 230 | 225.2 | 222.3
899 | 805 | 327.1 | 236.8 | 231.3 | 227.6 | 230 | 225.1 | 222.3
900 | 806 | 327 | 236.8 | 231.4 | 227.7 | 230.1 | 225 | 222.4
901 | 807 | 327 | 236.9 | 231.5 | 227.8 | 230.1 | 225 | 222.5
902 | 808 | 326.9 | 236.9 | 231.6 | 227.9 | 230.2 | 225 | 222.6
903 | 809 | 327 | 237 | 231.7 | 228 | 230.2 | 225.1 | 222.7
904 | 810 | 327 | 237.1 | 231.8 | 228 | 230.2 | 225.1 | 222.7
905 | 811 | 327 | 237.1 | 231.9 | 228.1 | 230.2 | 225.2 | 222.8
906 | 812 | 327 | 237.2 | 231.9 | 228.2 | 230.3 | 225.3 | 222.9
907 | 813 | 326.9 | 237.2 | 232 | 228.3 | 230.3 | 225.3 | 223
908 | 814 | 326.9 | 237.3 | 232.1 | 228.4 | 230.3 | 225.2 | 223.1
909 | 815 | 326.9 | 237.3 | 232.2 | 228.5 | 230.4 | 225.4 | 223.2
910 | 816 | 326.7 | 237.4 | 232.4 | 228.6 | 230.4 | 225.4 | 223.2
911 | 817 | 326.5 | 237.4 | 232.4 | 228.7 | 230.5 | 225.3 | 223.3
912 | 818 | 326.4 | 237.5 | 232.5 | 228.8 | 230.5 | 225.2 | 223.4
913 | 819 | 326.3 | 237.5 | 232.6 | 228.9 | 230.7 | 225.2 | 223.5
914 | 820 | 326.2 | 237.6 | 232.8 | 229 | 230.7 | 225.2 | 223.6
915 | 821 | 326.1 | 237.7 | 232.9 | 229.1 | 230.8 | 225.3 | 223.6
916 | 822 | 326.1 | 237.7 | 233 | 229.2 | 230.8 | 225.4 | 223.7
917 | 823 | 325.9 | 237.8 | 233.1 | 229.3 | 230.9 | 225.4 | 223.8
918 | 824 | 325.8 | 237.9 | 233.2 | 229.3 | 231 | 225.6 | 223.8
919 | 825 | 325.7 | 237.9 | 233.3 | 229.4 | 231.1 | 225.6 | 223.9
920 | 826 | 325.7 | 238 | 233.4 | 229.5 | 231.1 | 225.6 | 224
921 | 827 | 325.6 | 238 | 233.5 | 229.6 | 231.2 | 225.7 | 224
922 | 828 | 325.5 | 238.1 | 233.6 | 229.7 | 231.2 | 225.8 | 224.1
923 | 829 | 325.4 | 238.1 | 233.7 | 229.8 | 231.3 | 226 | 224.2
924 | 830 | 325.4 | 238.2 | 233.8 | 229.9 | 231.4 | 226 | 224.3
925 | 831 | 325.3 | 238.2 | 233.9 | 230 | 231.4 | 226 | 224.3
926 | 832 | 325.2 | 238.3 | 234 | 230.1 | 231.5 | 226 | 224.4
927 | 833 | 325.3 | 238.4 | 234 | 230.2 | 231.5 | 226 | 224.5
928 | 834 | 325.2 | 238.4 | 234.2 | 230.2 | 231.5 | 226 | 224.5
929 | 835 | 325.2 | 238.5 | 234.2 | 230.3 | 231.6 | 226.1 | 224.6
930 | 836 | 325.2 | 238.6 | 234.3 | 230.4 | 231.7 | 226.3 | 224.7
931 | 837 | 325.2 | 238.6 | 234.4 | 230.5 | 231.7 | 226.3 | 224.7
932 | 838 | 325.2 | 238.7 | 234.5 | 230.6 | 231.8 | 226.3 | 224.8
933 | 839 | 325.2 | 238.8 | 234.6 | 230.7 | 231.9 | 226.3 | 224.9
934 | 840 | 325.2 | 238.8 | 234.7 | 230.8 | 232 | 226.3 | 224.9
935 | 841 | 325.2 | 238.9 | 234.8 | 230.9 | 232 | 226.4 | 225
936 | 842 | 325.2 | 239 | 234.9 | 231 | 232.1 | 226.5 | 225.1
937 | 843 | 325.1 | 239 | 234.9 | 231 | 232.2 | 226.5 | 225.1
938 | 844 | 325 | 239.1 | 235 | 231.1 | 232.2 | 226.6 | 225.2
939 | 845 | 325 | 239.2 | 235.1 | 231.2 | 232.3 | 226.6 | 225.2 | Time of first failure
940 | 846 | 325 | 239.3 | 235.2 | 231.3 | 232.4 | 226.5 | 225.3 | 845 | 0
941 | 847 | 325 | 239.3 | 235.3 | 231.4 | 232.6 | 226.5 | 225.4 | 845 | 900
942 | 848 | 324.9 | 239.4 | 235.4 | 231.4 | 232.7 | 226.6 | 225.4
943 | 849 | 324.9 | 239.5 | 235.5 | 231.5 | 232.7 | 226.7 | 225.5
944 | 850 | 325 | 239.6 | 235.5 | 231.6 | 232.8 | 226.7 | 225.6
945 | 851 | 324.9 | 239.6 | 235.6 | 231.7 | 232.9 | 226.7 | 225.6
946 | 852 | 324.9 | 239.7 | 235.7 | 231.7 | 232.9 | 226.8 | 225.7
947 | 853 | 324.9 | 239.8 | 235.8 | 231.8 | 233 | 226.8 | 225.8
948 | 854 | 325 | 239.8 | 235.9 | 231.9 | 233 | 226.8 | 225.8
949 | 855 | 325.2 | 239.9 | 235.9 | 232 | 233.1 | 226.9 | 225.9
950 | 856 | 325.2 | 239.9 | 236 | 232 | 233.1 | 226.9 | 225.9
951 | 857 | 325.1 | 240 | 236.1 | 232.1 | 233.2 | 227 | 226
952 | 858 | 325 | 240 | 236.2 | 232.2 | 233.2 | 227 | 226.1
953 | 859 | 325.1 | 240.1 | 236.3 | 232.2 | 233.2 | 227 | 226.1
954 | 860 | 325.1 | 240.2 | 236.4 | 232.3 | 233.3 | 227.1 | 226.2
955 | 861 | 325.1 | 240.3 | 236.4 | 232.4 | 233.4 | 227.1 | 226.3
956 | 862 | 325.1 | 240.3 | 236.5 | 232.4 | 233.5 | 227.2 | 226.3
957 | 863 | 325.2 | 240.4 | 236.6 | 232.5 | 233.6 | 227.3 | 226.4
958 | 864 | 325.3 | 240.5 | 236.7 | 232.5 | 233.7 | 227.3 | 226.5
959 | 865 | 325.4 | 240.6 | 236.8 | 232.6 | 233.8 | 227.4 | 226.5
960 | 866 | 325.5 | 240.7 | 236.8 | 232.7 | 234 | 227.4 | 226.6
961 | 867 | 325.5 | 240.7 | 236.9 | 232.7 | 234.1 | 227.6 | 226.7
962 | 868 | 325.5 | 240.8 | 237 | 232.8 | 234.1 | 227.6 | 226.7
963 | 869 | 325.6 | 240.9 | 237.1 | 232.9 | 234.2 | 227.6 | 226.8
964 | 870 | 325.6 | 241 | 237.2 | 232.9 | 234.2 | 227.7 | 226.9
965 | 871 | 325.6 | 241 | 237.2 | 233 | 234.3 | 227.9 | 227
966 | 872 | 325.7 | 241.1 | 237.3 | 233 | 234.4 | 228 | 227
967 | 873 | 325.8 | 241.1 | 237.4 | 233.1 | 234.4 | 228.1 | 227.1
968 | 874 | 325.8 | 241.2 | 237.5 | 233.2 | 234.5 | 228.1 | 227.2
969 | 875 | 325.9 | 241.3 | 237.6 | 233.2 | 234.6 | 228.2 | 227.2
970 | 876 | 326.1 | 241.3 | 237.7 | 233.3 | 234.6 | 228.2 | 227.3
971 | 877 | 326.2 | 241.3 | 237.7 | 233.3 | 234.7 | 228.3 | 227.4
972 | 878 | 326.3 | 241.4 | 237.8 | 233.4 | 234.8 | 228.4 | 227.5
973 | 879 | 326.3 | 241.4 | 237.9 | 233.4 | 234.8 | 228.5 | 227.5
974 | 880 | 326.4 | 241.5 | 238 | 233.5 | 234.9 | 228.5 | 227.6
975 | 881 | 326.4 | 241.5 | 238 | 233.5 | 235 | 228.5 | 227.7
976 | 882 | 326.4 | 241.6 | 238.1 | 233.6 | 235.1 | 228.6 | 227.8
977 | 883 | 326.5 | 241.6 | 238.2 | 233.7 | 235.2 | 228.6 | 227.8
978 | 884 | 326.7 | 241.7 | 238.2 | 233.7 | 235.2 | 228.7 | 227.9
979 | 885 | 326.9 | 241.7 | 238.3 | 233.8 | 235.3 | 228.7 | 228
980 | 886 | 327 | 241.7 | 238.4 | 233.8 | 235.3 | 228.6 | 228.1
981 | 887 | 327 | 241.7 | 238.5 | 233.9 | 235.4 | 228.7 | 228.1
982 | 888 | 327 | 241.8 | 238.5 | 233.9 | 235.4 | 228.8 | 228.2
983 | 889 | 327 | 241.8 | 238.6 | 234 | 235.5 | 228.8 | 228.3
984 | 890 | 327 | 241.8 | 238.7 | 234 | 235.5 | 228.8 | 228.4
985 | 891 | 327 | 241.8 | 238.8 | 234.1 | 235.6 | 228.9 | 228.4
986 | 892 | 327 | 241.9 | 238.8 | 234.1 | 235.7 | 228.9 | 228.5
987 | 893 | 326.8 | 241.9 | 238.9 | 234.2 | 235.7 | 229 | 228.6
988 | 894 | 326.7 | 242 | 239 | 234.3 | 235.8 | 229.1 | 228.7
989 | 895 | 326.7 | 242.1 | 239 | 234.3 | 235.9 | 229.2 | 228.7
990 | 896 | 326.8 | 242.1 | 239.1 | 234.4 | 236 | 229.2 | 228.8
991 | 897 | 326.8 | 242.2 | 239.2 | 234.4 | 236 | 229.2 | 228.9
992 | 898 | 326.8 | 242.3 | 239.3 | 234.5 | 236.1 | 229.2 | 228.9
993 | 899 | 326.7 | 242.3 | 239.4 | 234.6 | 236.1 | 229.2 | 229
994 | 900 | 326.6 | 242.4 | 239.4 | 234.6 | 236.1 | 229.3 | 229.1
995 | 901 | 326.5 | 242.4 | 239.5 | 234.7 | 236.2 | 229.4 | 229.1
996 | 902 | 326.4 | 242.5 | 239.6 | 234.7 | 236.2 | 229.5 | 229.2
997 | 903 | 326.3 | 242.5 | 239.7 | 234.8 | 236.2 | 229.6 | 229.3
998 | 904 | 326.2 | 242.6 | 239.7 | 234.9 | 236.2 | 229.6 | 229.3
999 | 905 | 326.1 | 242.7 | 239.8 | 234.9 | 236.3 | 229.6 | 229.4
1000 | 906 | 326 | 242.7 | 239.9 | 235 | 236.3 | 229.7 | 229.5
1001 | 907 | 326 | 242.8 | 239.9 | 235 | 236.3 | 229.8 | 229.5
1002 | 908 | 325.9 | 242.9 | 240 | 235.1 | 236.4 | 229.8 | 229.6
1003 | 909 | 325.9 | 242.9 | 240.1 | 235.1 | 236.4 | 229.9 | 229.6
1004 | 910 | 325.8 | 243 | 240.1 | 235.2 | 236.5 | 230 | 229.7
1005 | 911 | 325.8 | 243.1 | 240.2 | 235.2 | 236.5 | 230 | 229.8
1006 | 912 | 325.7 | 243.1 | 240.3 | 235.3 | 236.6 | 230.1 | 229.9
1007 | 913 | 325.7 | 243.2 | 240.3 | 235.3 | 236.6 | 230 | 229.9
1008 | 914 | 325.6 | 243.2 | 240.4 | 235.4 | 236.7 | 230 | 230
1009 | 915 | 325.5 | 243.3 | 240.4 | 235.4 | 236.8 | 230 | 230
1010 | 916 | 325.4 | 243.3 | 240.5 | 235.5 | 236.8 | 230 | 230.1
1011 | 917 | 325.4 | 243.3 | 240.6 | 235.5 | 236.9 | 230 | 230.1
1012 | 918 | 325.4 | 243.4 | 240.6 | 235.6 | 237 | 230 | 230.2
1013 | 919 | 325.3 | 243.4 | 240.7 | 235.6 | 237 | 230.1 | 230.3
1014 | 920 | 325.4 | 243.5 | 240.8 | 235.7 | 237.1 | 230.2 | 230.4
1015 | 921 | 325.4 | 243.5 | 240.8 | 235.8 | 237.1 | 230.3 | 230.4
1016 | 922 | 325.5 | 243.5 | 240.9 | 235.8 | 237.2 | 230.3 | 230.5
1017 | 923 | 325.5 | 243.5 | 241 | 235.9 | 237.2 | 230.1 | 230.5
1018 | 924 | 325.4 | 243.5 | 241 | 235.9 | 237.3 | 230.1 | 230.6
1019 | 925 | 325.3 | 243.5 | 241.1 | 236 | 237.3 | 230 | 230.6
1020 | 926 | 325.2 | 243.6 | 241.2 | 236 | 237.3 | 229.9 | 230.7
1021 | 927 | 325.2 | 243.5 | 241.2 | 236.1 | 237.4 | 229.9 | 230.7
1022 | 928 | 325.1 | 243.5 | 241.3 | 236.1 | 237.5 | 229.8 | 230.8
1023 | 929 | 325 | 243.5 | 241.3 | 236.2 | 237.5 | 229.9 | 230.8
1024 | 930 | 325.1 | 243.5 | 241.4 | 236.2 | 237.6 | 230 | 230.9
1025 | 931 | 325.1 | 243.6 | 241.4 | 236.3 | 237.7 | 229.9 | 231
1026 | 932 | 325.1 | 243.6 | 241.5 | 236.3 | 237.8 | 229.9 | 231
1027 | 933 | 325.1 | 243.6 | 241.5 | 236.4 | 237.8 | 230 | 231.1
1028 | 934 | 325.1 | 243.7 | 241.6 | 236.5 | 237.9 | 230 | 231.1
1029 | 935 | 325.1 | 243.7 | 241.7 | 236.5 | 238 | 230.1 | 231.2
1030 | 936 | 324.9 | 243.7 | 241.7 | 236.6 | 238.1 | 230.2 | 231.2
1031 | 937 | 325 | 243.8 | 241.8 | 236.7 | 238.2 | 230 | 231.2
1032 | 938 | 325 | 243.8 | 241.8 | 236.7 | 238.2 | 230.1 | 231.3
1033 | 939 | 324.9 | 243.8 | 241.9 | 236.8 | 238.3 | 230.1 | 231.3
1034 | 940 | 324.9 | 243.9 | 242 | 236.9 | 238.4 | 230.2 | 231.4
1035 | 941 | 324.9 | 243.9 | 242 | 236.9 | 238.5 | 230.1 | 231.4
1036 | 942 | 325 | 243.9 | 242.1 | 237 | 238.6 | 230.1 | 231.5
1037 | 943 | 325 | 243.9 | 242.2 | 237.1 | 238.6 | 230.1 | 231.5
1038 | 944 | 325 | 243.9 | 242.2 | 237.1 | 238.7 | 230.2 | 231.6
1039 | 945 | 325 | 244 | 242.3 | 237.2 | 238.8 | 230.2 | 231.6
1040 | 946 | 325 | 244 | 242.3 | 237.3 | 238.9 | 230.1 | 231.7
1041 | 947 | 324.9 | 244 | 242.4 | 237.3 | 239 | 230.1 | 231.7
1042 | 948 | 325 | 244 | 242.5 | 237.4 | 239.1 | 230.1 | 231.8
1043 | 949 | 325 | 244 | 242.5 | 237.5 | 239.2 | 230.1 | 231.8
1044 | 950 | 324.9 | 244.1 | 242.6 | 237.5 | 239.3 | 230.2 | 231.9
1045 | 951 | 325 | 244.1 | 242.6 | 237.6 | 239.3 | 230.1 | 231.9
1046 | 952 | 325 | 244.1 | 242.7 | 237.7 | 239.4 | 230.1 | 232
1047 | 953 | 325.1 | 244.1 | 242.7 | 237.7 | 239.5 | 230.3 | 232
1048 | 954 | 325.2 | 244.1 | 242.8 | 237.8 | 239.6 | 230.3 | 232.1
1049 | 955 | 325.3 | 244.2 | 242.9 | 237.9 | 239.7 | 230.3 | 232.1
1050 | 956 | 325.3 | 244.2 | 242.9 | 237.9 | 239.8 | 230.4 | 232.2
1051 | 957 | 325.4 | 244.2 | 243 | 238 | 239.9 | 230.4 | 232.2
1052 | 958 | 325.6 | 244.3 | 243 | 238.1 | 240 | 230.3 | 232.3
1053 | 959 | 325.7 | 244.3 | 243.1 | 238.1 | 240.1 | 230.4 | 232.3
1054 | 960 | 325.7 | 244.3 | 243.1 | 238.2 | 240.2 | 230.6 | 232.4
1055 | 961 | 325.8 | 244.4 | 243.2 | 238.2 | 240.3 | 230.6 | 232.4
1056 | 962 | 325.7 | 244.4 | 243.2 | 238.3 | 240.4 | 230.6 | 232.5
1057 | 963 | 325.6 | 244.4 | 243.3 | 238.4 | 240.5 | 230.8 | 232.5
1058 | 964 | 325.6 | 244.5 | 243.3 | 238.4 | 240.6 | 231 | 232.6
1059 | 965 | 325.7 | 244.5 | 243.3 | 238.5 | 240.7 | 231 | 232.6
1060 | 966 | 325.7 | 244.6 | 243.4 | 238.6 | 240.8 | 231.1 | 232.7
1061 | 967 | 325.7 | 244.6 | 243.5 | 238.6 | 240.9 | 231.3 | 232.7
1062 | 968 | 325.8 | 244.7 | 243.5 | 238.7 | 240.9 | 231.4 | 232.8
1063 | 969 | 325.8 | 244.7 | 243.5 | 238.7 | 241 | 231.5 | 232.8
1064 | 970 | 326 | 244.8 | 243.6 | 238.8 | 241.1 | 231.6 | 232.9
1065 | 971 | 326.1 | 244.8 | 243.6 | 238.8 | 241.2 | 231.7 | 232.9
1066 | 972 | 326.2 | 244.9 | 243.7 | 238.9 | 241.3 | 231.7 | 233
1067 | 973 | 326.2 | 244.9 | 243.8 | 238.9 | 241.4 | 231.7 | 233.1
1068 | 974 | 326.2 | 245 | 243.8 | 239 | 241.5 | 231.7 | 233.1
1069 | 975 | 326.2 | 245 | 243.8 | 239 | 241.6 | 231.8 | 233.2
1070 | 976 | 326.3 | 245.1 | 243.9 | 239.1 | 241.6 | 231.9 | 233.2
1071 | 977 | 326.3 | 245.1 | 243.9 | 239.1 | 241.7 | 231.9 | 233.3
1072 | 978 | 326.3 | 245.2 | 244 | 239.2 | 241.7 | 232 | 233.3
1073 | 979 | 326.3 | 245.2 | 244.1 | 239.2 | 241.8 | 232 | 233.4
1074 | 980 | 326.3 | 245.3 | 244.1 | 239.3 | 241.8 | 232.1 | 233.4
1075 | 981 | 326.4 | 245.3 | 244.1 | 239.3 | 241.9 | 232.2 | 233.5
1076 | 982 | 326.3 | 245.4 | 244.2 | 239.4 | 242 | 232.4 | 233.5
1077 | 983 | 326.2 | 245.4 | 244.2 | 239.4 | 242 | 232.4 | 233.6
1078 | 984 | 326.1 | 245.5 | 244.3 | 239.5 | 242.1 | 232.4 | 233.6
1079 | 985 | 326 | 245.5 | 244.3 | 239.5 | 242.1 | 232.5 | 233.7
1080 | 986 | 326 | 245.6 | 244.4 | 239.6 | 242.2 | 232.5 | 233.7
1081 | 987 | 326 | 245.6 | 244.4 | 239.6 | 242.3 | 232.6 | 233.8
1082 | 988 | 325.9 | 245.7 | 244.5 | 239.7 | 242.3 | 232.8 | 233.8
1083 | 989 | 325.8 | 245.7 | 244.5 | 239.7 | 242.4 | 232.8 | 233.8
1084 | 990 | 325.8 | 245.8 | 244.6 | 239.7 | 242.4 | 232.8 | 233.9
1085 | 991 | 325.7 | 245.8 | 244.6 | 239.8 | 242.4 | 233 | 233.9
1086 | 992 | 325.7 | 245.9 | 244.7 | 239.8 | 242.4 | 233 | 234
1087 | 993 | 325.7 | 245.9 | 244.7 | 239.9 | 242.4 | 233 | 234
1088 | 994 | 325.7 | 246 | 244.8 | 239.9 | 242.4 | 233.1 | 234.1
1089 | 995 | 325.6 | 246 | 244.8 | 239.9 | 242.4 | 233.2 | 234.1
1090 | 996 | 325.5 | 246.1 | 244.8 | 240 | 242.4 | 233.3 | 234.2
1091 | 997 | 325.5 | 246.1 | 244.9 | 240 | 242.4 | 233.3 | 234.2
1092 | 998 | 325.4 | 246.2 | 245 | 240.1 | 242.4 | 233.3 | 234.3
1093 | 999 | 325.3 | 246.2 | 245 | 240.1 | 242.4 | 233.3 | 234.3
1094 | 1000 | 325.2 | 246.3 | 245 | 240.1 | 242.4 | 233.4 | 234.4
1095 | 1001 | 325.1 | 246.3 | 245.1 | 240.2 | 242.4 | 233.5 | 234.4
1096 | 1002 | 325.1 | 246.4 | 245.1 | 240.2 | 242.4 | 233.5 | 234.5
1097 | 1003 | 324.9 | 246.4 | 245.2 | 240.3 | 242.4 | 233.5 | 234.5
1098 | 1004 | 324.8 | 246.5 | 245.2 | 240.3 | 242.5 | 233.6 | 234.5
1099 | 1005 | 324.9 | 246.5 | 245.3 | 240.3 | 242.5 | 233.6 | 234.6
1100 | 1006 | 324.8 | 246.5 | 245.3 | 240.4 | 242.5 | 233.7 | 234.6
1101 | 1007 | 324.8 | 246.6 | 245.4 | 240.4 | 242.5 | 233.8 | 234.7
1102 | 1008 | 324.8 | 246.6 | 245.4 | 240.5 | 242.5 | 233.7 | 234.7
1103 | 1009 | 324.8 | 246.7 | 245.5 | 240.5 | 242.5 | 233.7 | 234.8
1104 | 1010 | 324.9 | 246.7 | 245.5 | 240.5 | 242.6 | 233.8 | 234.8
1105 | 1011 | 325 | 246.7 | 245.6 | 240.6 | 242.6 | 233.7 | 234.9
1106 | 1012 | 325 | 246.8 | 245.6 | 240.6 | 242.6 | 233.6 | 234.9
1107 | 1013 | 325 | 246.8 | 245.6 | 240.7 | 242.6 | 233.3 | 234.9
1108 | 1014 | 325 | 246.8 | 245.7 | 240.7 | 242.6 | 233.1 | 235
1109 | 1015 | 325.1 | 246.8 | 245.7 | 240.7 | 242.7 | 233 | 235
1110 | 1016 | 325.1 | 246.8 | 245.8 | 240.8 | 242.7 | 233.1 | 235.1
1111 | 1017 | 325 | 246.8 | 245.8 | 240.8 | 242.8 | 233.1 | 235.1
1112 | 1018 | 324.8 | 246.8 | 245.9 | 240.9 | 242.8 | 233.1 | 235.2
1113 | 1019 | 324.8 | 246.8 | 245.9 | 240.9 | 242.8 | 233.1 | 235.2
1114 | 1020 | 324.9 | 246.9 | 246 | 241 | 242.9 | 233.1 | 235.3
1115 | 1021 | 324.9 | 246.9 | 246 | 241 | 242.9 | 233 | 235.3
1116 | 1022 | 324.7 | 246.9 | 246.1 | 241 | 242.9 | 233 | 235.4
1117 | 1023 | 324.6 | 246.9 | 246.1 | 241.1 | 243 | 233 | 235.4
1118 | 1024 | 324.6 | 246.9 | 246.2 | 241.1 | 243 | 233 | 235.5
1119 | 1025 | 324.7 | 246.9 | 246.2 | 241.2 | 243.1 | 233 | 235.5
1120 | 1026 | 324.7 | 246.9 | 246.3 | 241.2 | 243.1 | 233 | 235.5
1121 | 1027 | 324.7 | 247 | 246.3 | 241.3 | 243.1 | 233 | 235.6
1122 | 1028 | 324.8 | 247 | 246.3 | 241.3 | 243.2 | 233.1 | 235.6
1123 | 1029 | 324.8 | 247 | 246.4 | 241.4 | 243.3 | 233.2 | 235.7
1124 | 1030 | 324.7 | 247.1 | 246.4 | 241.4 | 243.3 | 233.2 | 235.7
1125 | 1031 | 324.7 | 247.1 | 246.5 | 241.5 | 243.4 | 233.2 | 235.8
1126 | 1032 | 324.7 | 247.1 | 246.6 | 241.5 | 243.4 | 233.2 | 235.8
1127 | 1033 | 324.8 | 247.2 | 246.6 | 241.5 | 243.5 | 233.2 | 235.8
1128 | 1034 | 324.8 | 247.2 | 246.7 | 241.6 | 243.5 | 233.2 | 235.9
1129 | 1035 | 325 | 247.2 | 246.7 | 241.6 | 243.6 | 233.2 | 235.9
1130 | 1036 | 325 | 247.3 | 246.8 | 241.7 | 243.7 | 233.2 | 236
1131 | 1037 | 325 | 247.3 | 246.8 | 241.7 | 243.7 | 233.2 | 236
1132 | 1038 | 325.1 | 247.3 | 246.8 | 241.8 | 243.7 | 233.2 | 236
1133 | 1039 | 325.2 | 247.4 | 246.9 | 241.8 | 243.8 | 233.2 | 236.1
1134 | 1040 | 325.3 | 247.4 | 246.9 | 241.8 | 243.8 | 233.3 | 236.1
1135 | 1041 | 325.4 | 247.4 | 247 | 241.9 | 243.9 | 233.3 | 236.2
1136 | 1042 | 325.5 | 247.5 | 247 | 241.9 | 244 | 233.3 | 236.2
1137 | 1043 | 325.5 | 247.5 | 247.1 | 242 | 244.1 | 233.3 | 236.2
1138 | 1044 | 325.4 | 247.5 | 247.1 | 242 | 244.2 | 233.2 | 236.3
1139 | 1045 | 325.4 | 247.5 | 247.2 | 242 | 244.2 | 233.1 | 236.3
1140 | 1046 | 325.5 | 247.5 | 247.2 | 242.1 | 244.3 | 233 | 236.4
1141 | 1047 | 325.6 | 247.6 | 247.2 | 242.1 | 244.4 | 233 | 236.4
1142 | 1048 | 325.6 | 247.6 | 247.3 | 242.2 | 244.4 | 233 | 236.5
1143 | 1049 | 325.5 | 247.6 | 247.3 | 242.2 | 244.5 | 233 | 236.5
1144 | 1050 | 325.6 | 247.6 | 247.4 | 242.3 | 244.6 | 233.1 | 236.6
1145 | 1051 | 325.5 | 247.6 | 247.4 | 242.3 | 244.6 | 233.2 | 236.6
1146 | 1052 | 325.4 | 247.7 | 247.4 | 242.4 | 244.7 | 233.3 | 236.6
1147 | 1053 | 325.3 | 247.7 | 247.5 | 242.4 | 244.8 | 233.2 | 236.7
1148 | 1054 | 325.2 | 247.7 | 247.5 | 242.4 | 244.8 | 233.3 | 236.7
1149 | 1055 | 325.3 | 247.8 | 247.6 | 242.5 | 244.9 | 233.3 | 236.7
1150 | 1056 | 325.3 | 247.8 | 247.6 | 242.5 | 244.9 | 233.3 | 236.8
1151 | 1057 | 325.4 | 247.8 | 247.7 | 242.6 | 245 | 233.4 | 236.8
1152 | 1058 | 325.5 | 247.9 | 247.8 | 242.6 | 245 | 233.4 | 236.8
1153 | 1059 | 325.8 | 247.9 | 247.8 | 242.7 | 245.1 | 233.5 | 236.9
1154 | 1060 | 326 | 248 | 247.9 | 242.7 | 245.2 | 233.5 | 236.9
1155 | 1061 | 326 | 248 | 247.9 | 242.7 | 245.2 | 233.5 | 236.9
1156 | 1062 | 325.9 | 248 | 247.9 | 242.8 | 245.3 | 233.7 | 237
1157 | 1063 | 325.9 | 248.1 | 248 | 242.8 | 245.4 | 233.6 | 237
1158 | 1064 | 326 | 248.1 | 248 | 242.9 | 245.4 | 233.7 | 237
1159 | 1065 | 326.1 | 248.1 | 248.1 | 242.9 | 245.5 | 233.5 | 237.1
1160 | 1066 | 326.2 | 248.2 | 248.1 | 242.9 | 245.5 | 233.5 | 237.1
1161 | 1067 | 326.2 | 248.2 | 248.2 | 243 | 245.5 | 233.5 | 237.1
1162 | 1068 | 326.2 | 248.2 | 248.2 | 243 | 245.6 | 233.7 | 237.2
1163 | 1069 | 326.2 | 248.3 | 248.3 | 243 | 245.7 | 233.7 | 237.2
1164 | 1070 | 326.2 | 248.3 | 248.3 | 243.1 | 245.8 | 233.7 | 237.2
1165 | 1071 | 326.2 | 248.3 | 248.3 | 243.1 | 245.8 | 233.7 | 237.3
1166 | 1072 | 326.3 | 248.3 | 248.4 | 243.1 | 245.9 | 233.7 | 237.3
1167 | 1073 | 326.3 | 248.4 | 248.4 | 243.2 | 245.9 | 233.7 | 237.4
1168 | 1074 | 326.3 | 248.4 | 248.5 | 243.2 | 245.9 | 233.8 | 237.4
1169 | 1075 | 326.2 | 248.4 | 248.5 | 243.2 | 246 | 233.9 | 237.4
1170 | 1076 | 326.2 | 248.5 | 248.6 | 243.3 | 246.1 | 233.9 | 237.5
1171 | 1077 | 326.1 | 248.5 | 248.6 | 243.3 | 246.1 | 234 | 237.5
1172 | 1078 | 326.1 | 248.6 | 248.7 | 243.4 | 246.2 | 234.1 | 237.6
1173 | 1079 | 326.2 | 248.6 | 248.7 | 243.4 | 246.2 | 234.1 | 237.6
1174 | 1080 | 326.3 | 248.7 | 248.8 | 243.4 | 246.3 | 234.2 | 237.6
1175 | 1081 | 326.3 | 248.7 | 248.8 | 243.5 | 246.3 | 234.1 | 237.7
1176 | 1082 | 326.2 | 248.8 | 248.8 | 243.5 | 246.4 | 234 | 237.7
1177 | 1083 | 326.2 | 248.8 | 248.9 | 243.5 | 246.4 | 234 | 237.7
1178 | 1084 | 326.2 | 248.9 | 248.9 | 243.6 | 246.5 | 234.1 | 237.8
1179 | 1085 | 326.2 | 248.9 | 249 | 243.6 | 246.5 | 234.1 | 237.8
1180 | 1086 | 326.3 | 248.9 | 249 | 243.6 | 246.6 | 234.1 | 237.8
1181 | 1087 | 326.3 | 249 | 249.1 | 243.7 | 246.7 | 234.2 | 237.9
1182 | 1088 | 326.3 | 249 | 249.1 | 243.7 | 246.7 | 234.1 | 237.9
1183 | 1089 | 326.2 | 249 | 249.2 | 243.7 | 246.7 | 234.2 | 237.9
1184 | 1090 | 326.2 | 249.1 | 249.2 | 243.8 | 246.8 | 234.2 | 238
1185 | 1091 | 326.3 | 249.1 | 249.3 | 243.8 | 246.8 | 234.2 | 238
1186 | 1092 | 326.3 | 249.2 | 249.3 | 243.8 | 246.9 | 234.2 | 238
1187 | 1093 | 326.3 | 249.2 | 249.3 | 243.9 | 246.9 | 234.2 | 238
1188 | 1094 | 326.2 | 249.2 | 249.4 | 243.9 | 247 | 234.2 | 238.1
1189 | 1095 | 326.2 | 249.3 | 249.4 | 243.9 | 247 | 234.2 | 238.1
1190 | 1096 | 326.1 | 249.3 | 249.5 | 243.9 | 247.1 | 234.2 | 238.1
1191 | 1097 | 326.1 | 249.3 | 249.5 | 244 | 247.1 | 234.2 | 238.2
1192 | 1098 | 326.1 | 249.4 | 249.5 | 244 | 247.2 | 234.3 | 238.2
1193 | 1099 | 326 | 249.4 | 249.6 | 244 | 247.2 | 234.4 | 238.2
1194 | 1100 | 326 | 249.5 | 249.6 | 244 | 247.3 | 234.5 | 238.3
1195 | 1101 | 326.1 | 249.6 | 249.7 | 244.1 | 247.3 | 234.5 | 238.3
1196 | 1102 | 326.1 | 249.6 | 249.7 | 244.1 | 247.4 | 234.6 | 238.3
1197 | 1103 | 326 | 249.7 | 249.8 | 244.1 | 247.4 | 234.7 | 238.4
1198 | 1104 | 325.9 | 249.7 | 249.8 | 244.2 | 247.4 | 234.7 | 238.4
1199 | 1105 | 325.9 | 249.8 | 249.8 | 244.2 | 247.5 | 234.8 | 238.4
1200 | 1106 | 326 | 249.8 | 249.9 | 244.2 | 247.5 | 234.8 | 238.5
1201 | 1107 | 326 | 249.9 | 249.9 | 244.2 | 247.6 | 234.9 | 238.5
1202 | 1108 | 326 | 249.9 | 249.9 | 244.3 | 247.6 | 234.9 | 238.5
1203 | 1109 | 325.9 | 250 | 250 | 244.3 | 247.7 | 235 | 238.6
1204 | 1110 | 325.9 | 250 | 250 | 244.3 | 247.7 | 235 | 238.6
1205 | 1111 | 325.9 | 250 | 250 | 244.4 | 247.7 | 235 | 238.6
1206 | 1112 | 325.9 | 250.1 | 250.1 | 244.4 | 247.7 | 235.1 | 238.6
1207 | 1113 | 325.9 | 250.1 | 250.1 | 244.4 | 247.7 | 235.2 | 238.7
1208 | 1114 | 326 | 250.2 | 250.1 | 244.4 | 247.8 | 235.2 | 238.7
1209 | 1115 | 326.1 | 250.2 | 250.2 | 244.5 | 247.8 | 235.2 | 238.7
1210 | 1116 | 326.2 | 250.3 | 250.2 | 244.5 | 247.8 | 235.2 | 238.8
1211 | 1117 | 326.1 | 250.3 | 250.3 | 244.5 | 247.8 | 235.3 | 238.8
1212 | 1118 | 326 | 250.4 | 250.3 | 244.5 | 247.9 | 235.3 | 238.8
1213 | 1119 | 326 | 250.4 | 250.3 | 244.6 | 247.9 | 235.4 | 238.9
1214 | 1120 | 326 | 250.5 | 250.3 | 244.6 | 247.9 | 235.5 | 238.9
1215 | 1121 | 326 | 250.5 | 250.4 | 244.6 | 247.9 | 235.4 | 238.9
1216 | 1122 | 325.9 | 250.6 | 250.4 | 244.6 | 247.9 | 235.5 | 238.9
1217 | 1123 | 325.9 | 250.6 | 250.4 | 244.7 | 247.9 | 235.6 | 239
1218 | 1124 | 325.9 | 250.6 | 250.5 | 244.7 | 247.9 | 235.6 | 239
1219 | 1125 | 325.7 | 250.7 | 250.5 | 244.7 | 248 | 235.5 | 239
1220 | 1126 | 325.6 | 250.7 | 250.6 | 244.8 | 247.9 | 235.6 | 239.1
1221 | 1127 | 325.5 | 250.8 | 250.6 | 244.8 | 248 | 235.6 | 239.1
1222 | 1128 | 325.5 | 250.8 | 250.6 | 244.8 | 248 | 235.6 | 239.1
1223 | 1129 | 325.5 | 250.9 | 250.7 | 244.9 | 248 | 235.6 | 239.1
1224 | 1130 | 325.5 | 250.9 | 250.7 | 244.9 | 248 | 235.7 | 239.1
1225 | 1131 | 325.4 | 250.9 | 250.7 | 244.9 | 248 | 235.7 | 239.2
1226 | 1132 | 325.3 | 251 | 250.8 | 244.9 | 248 | 235.7 | 239.2
1227 | 1133 | 325.3 | 251 | 250.8 | 245 | 248 | 235.8 | 239.2
1228 | 1134 | 325.4 | 251 | 250.8 | 245 | 248.1 | 235.7 | 239.2
1229 | 1135 | 325.3 | 251.1 | 250.9 | 245 | 248.1 | 235.6 | 239.3
1230 | 1136 | 325.2 | 251.1 | 250.9 | 245.1 | 248.1 | 235.5 | 239.3
1231 | 1137 | 325.1 | 251.1 | 250.9 | 245.1 | 248.1 | 235.6 | 239.3
1232 | 1138 | 325.1 | 251.2 | 251 | 245.1 | 248.1 | 235.4 | 239.3
1233 | 1139 | 325.2 | 251.2 | 251 | 245.1 | 248.1 | 235.4 | 239.4
1234 | 1140 | 325.1 | 251.2 | 251 | 245.1 | 248.1 | 235.3 | 239.4
1235 | 1141 | 325 | 251.2 | 251.1 | 245.2 | 248.1 | 235.3 | 239.4
1236 | 1142 | 325.1 | 251.3 | 251.1 | 245.2 | 248.1 | 235.2 | 239.4
1237 | 1143 | 325.2 | 251.3 | 251.2 | 245.2 | 248.1 | 235.3 | 239.5
1238 | 1144 | 325.2 | 251.4 | 251.2 | 245.2 | 248.1 | 235.4 | 239.5
1239 | 1145 | 325.2 | 251.4 | 251.3 | 245.2 | 248.1 | 235.5 | 239.5
1240 | 1146 | 325.4 | 251.4 | 251.3 | 245.3 | 248.2 | 235.5 | 239.5
1241 | 1147 | 325.4 | 251.5 | 251.3 | 245.3 | 248.2 | 235.4 | 239.6
1242 | 1148 | 325.4 | 251.5 | 251.4 | 245.3 | 248.2 | 235.5 | 239.6
1243 | 1149 | 325.5 | 251.6 | 251.4 | 245.3 | 248.2 | 235.7 | 239.6
1244 | 1150 | 325.5 | 251.6 | 251.4 | 245.3 | 248.2 | 235.8 | 239.6
1245 | 1151 | 325.5 | 251.6 | 251.5 | 245.4 | 248.2 | 235.8 | 239.7
1246 | 1152 | 325.5 | 251.7 | 251.4 | 245.4 | 248.3 | 235.8 | 239.7
1247 | 1153 | 325.4 | 251.7 | 251.5 | 245.4 | 248.2 | 235.8 | 239.7
1248 | 1154 | 325.4 | 251.7 | 251.5 | 245.4 | 248.2 | 235.9 | 239.8
1249 | 1155 | 325.4 | 251.8 | 251.6 | 245.4 | 248.2 | 236.1 | 239.8
1250 | 1156 | 325.5 | 251.8 | 251.6 | 245.5 | 248.2 | 235.9 | 239.8
1251 | 1157 | 325.4 | 251.8 | 251.6 | 245.5 | 248.2 | 235.8 | 239.8
1252 | 1158 | 325.4 | 251.9 | 251.6 | 245.5 | 248.2 | 235.8 | 239.9
1253 | 1159 | 325.4 | 251.9 | 251.6 | 245.5 | 248.1 | 235.7 | 239.9
1254 | 1160 | 325.5 | 251.9 | 251.7 | 245.5 | 248.1 | 235.8 | 239.9
1255 | 1161 | 325.5 | 252 | 251.7 | 245.6 | 248.1 | 235.7 | 240
1256 | 1162 | 325.5 | 252 | 251.7 | 245.6 | 248.1 | 235.7 | 240
1257 | 1163 | 325.6 | 252 | 251.8 | 245.6 | 248.2 | 235.7 | 240
1258 | 1164 | 325.7 | 252 | 251.8 | 245.6 | 248.2 | 235.7 | 240
1259 | 1165 | 325.6 | 252.7 | 248.8 | 246.8 | 249.1 | 236.2 | 240
1260 | 1166 | 325.7 | 252.1 | 251.8 | 245.7 | 248.2 | 235.8 | 240.1
1261 | 1167 | 325.8 | 252.1 | 251.8 | 245.7 | 248.2 | 235.9 | 240.1
1262 | 1168 | 325.9 | 252.1 | 251.9 | 245.7 | 248.2 | 235.9 | 240.1
1263 | 1169 | 326 | 252.3 | 251.5 | 245.9 | 248.4 | 235.9 | 240.1
1264 | 1170 | 325.9 | 252.5 | 250.8 | 246.3 | 248.7 | 236 | 240.1
1265 | 1171 | 325.8 | 252.4 | 251.2 | 246.2 | 248.5 | 236 | 240.2
1266 | 1172 | 325.8 | 252.5 | 251.3 | 246.1 | 248.6 | 236.1 | 240.2
1267 | 1173 | 325.8 | 252.4 | 251.3 | 246.2 | 248.5 | 236.1 | 240.2
1268 | 1174 | 325.9 | 252.4 | 251.7 | 246 | 248.4 | 236 | 240.2
1269 | 1175 | 325.9 | 252.3 | 252 | 245.9 | 248.3 | 235.9 | 240.3
1270 | 1176 | 326 | 252.4 | 252.1 | 245.9 | 248.3 | 235.9 | 240.3
1271 | 1177 | 326.1 | 252.4 | 252.1 | 245.9 | 248.3 | 235.8 | 240.3
1272 | 1178 | 326.1 | 252.4 | 252.1 | 246 | 248.3 | 235.8 | 240.4
1273 | 1179 | 326.2 | 252.5 | 251.9 | 246 | 248.5 | 235.9 | 240.4
1274 | 1180 | 326.2 | 252.5 | 252.1 | 246 | 248.4 | 235.9 | 240.4
1275 | 1181 | 326.2 | 252.5 | 252.2 | 246 | 248.4 | 235.8 | 240.4
1276 | 1182 | 326.1 | 252.5 | 252.2 | 246 | 248.3 | 235.7 | 240.5
1277 | 1183 | 326 | 252.6 | 252.3 | 246.1 | 248.4 | 235.7 | 240.5
1278 | 1184 | 326 | 252.6 | 252.3 | 246.1 | 248.4 | 235.7 | 240.5
1279 | 1185 | 326.1 | 252.6 | 252.3 | 246.1 | 248.4 | 235.7 | 240.5
1280 | 1186 | 326.1 | 252.6 | 252.3 | 246.2 | 248.5 | 235.6 | 240.6
1281 | 1187 | 326.2 | 252.6 | 252.4 | 246.2 | 248.5 | 235.6 | 240.6
1282 | 1188 | 326.2 | 252.6 | 252.4 | 246.2 | 248.5 | 235.6 | 240.6
1283 | 1189 | 326.2 | 252.6 | 252.5 | 246.2 | 248.6 | 235.6 | 240.6
1284 | 1190 | 326.2 | 252.6 | 252.5 | 246.2 | 248.6 | 235.6 | 240.7
1285 | 1191 | 326.1 | 252.6 | 252.5 | 246.3 | 248.6 | 235.7 | 240.7
1286 | 1192 | 326 | 252.7 | 252.6 | 246.3 | 248.7 | 235.8 | 240.7
1287 | 1193 | 325.9 | 252.7 | 252.6 | 246.3 | 248.7 | 235.9 | 240.8
1288 | 1194 | 325.8 | 252.7 | 252.6 | 246.4 | 248.7 | 235.9 | 240.8
1289 | 1195 | 325.7 | 252.8 | 252.6 | 246.4 | 248.7 | 236 | 240.8
1290 | 1196 | 325.7 | 252.8 | 252.7 | 246.4 | 248.8 | 236 | 240.8
1291 | 1197 | 325.6 | 252.8 | 252.7 | 246.4 | 248.8 | 236.1 | 240.9
1292 | 1198 | 325.7 | 252.7 | 252.8 | 246.5 | 248.9 | 236 | 240.9
1293 | 1199 | 325.7 | 252.7 | 252.8 | 246.5 | 248.9 | 236 | 240.9
1294 | 1200 | 325.8 | 252.6 | 252.8 | 246.5 | 248.9 | 235.9 | 240.9
1295 | 1201 | 325.8 | 252.6 | 252.8 | 246.6 | 249 | 235.9 | 241
1296 | 1202 | 325.9 | 252.5 | 252.9 | 246.6 | 249 | 235.9 | 241
1297 | 1203 | 325.9 | 252.5 | 252.9 | 246.6 | 249 | 235.8 | 241
1298 | 1204 | 325.7 | 252.5 | 252.9 | 246.6 | 249 | 235.7 | 241
1299 | 1205 | 325.8 | 252.5 | 252.9 | 246.6 | 249.1 | 235.6 | 241.1
1300 | 1206 | 325.8 | 252.5 | 253 | 246.7 | 249.1 | 235.7 | 241.1
1301 | 1207 | 326 | 252.4 | 253 | 246.7 | 249.2 | 235.7 | 241.1
1302 | 1208 | 326 | 252.4 | 253 | 246.7 | 249.2 | 235.7 | 241.1
1303 | 1209 | 326 | 252.4 | 253 | 246.8 | 249.2 | 235.6 | 241.2
1304 | 1210 | 326 | 252.4 | 253.1 | 246.8 | 249.2 | 235.5 | 241.2
1305 | 1211 | 326 | 252.4 | 253.1 | 246.8 | 249.3 | 235.6 | 241.2
1306 | 1212 | 326 | 252.4 | 253.2 | 246.8 | 249.3 | 235.5 | 241.2
1307 | 1213 | 326 | 252.4 | 253.2 | 246.9 | 249.3 | 235.5 | 241.3
1308 | 1214 | 325.9 | 252.4 | 253.3 | 246.9 | 249.3 | 235.5 | 241.3
1309 | 1215 | 325.9 | 252.4 | 253.3 | 246.9 | 249.3 | 235.4 | 241.3
1310 | 1216 | 325.9 | 252.5 | 253.3 | 247 | 249.3 | 235.6 | 241.3
1311 | 1217 | 325.8 | 252.5 | 253.4 | 247 | 249.4 | 235.7 | 241.4
1312 | 1218 | 325.8 | 252.5 | 253.4 | 247 | 249.4 | 235.7 | 241.4
1313 | 1219 | 325.7 | 252.5 | 253.4 | 247 | 249.4 | 235.7 | 241.4
1314 | 1220 | 325.8 | 252.5 | 253.5 | 247 | 249.5 | 235.9 | 241.4
1315 | 1221 | 325.9 | 252.6 | 253.5 | 247.1 | 249.5 | 235.9 | 241.4
1316 | 1222 | 325.9 | 252.6 | 253.5 | 247.1 | 249.5 | 236.1 | 241.4
1317 | 1223 | 325.9 | 252.6 | 253.6 | 247.1 | 249.6 | 236.3 | 241.5
1318 | 1224 | 325.9 | 252.7 | 253.6 | 247.1 | 249.6 | 236.4 | 241.5
1319 | 1225 | 325.9 | 252.7 | 253.6 | 247.1 | 249.6 | 236.5 | 241.5
1320 | 1226 | 325.9 | 252.7 | 253.6 | 247.2 | 249.6 | 236.5 | 241.5
1321 | 1227 | 325.9 | 252.7 | 253.7 | 247.2 | 249.6 | 236.6 | 241.5
1322 | 1228 | 326 | 252.8 | 253.7 | 247.2 | 249.6 | 236.7 | 241.6
1323 | 1229 | 326 | 252.8 | 253.7 | 247.2 | 249.7 | 236.8 | 241.6
1324 | 1230 | 326.1 | 252.8 | 253.7 | 247.2 | 249.7 | 236.8 | 241.6
1325 | 1231 | 326.2 | 252.8 | 253.7 | 247.3 | 249.7 | 236.8 | 241.6
1326 | 1232 | 326.2 | 252.9 | 253.7 | 247.3 | 249.7 | 236.6 | 241.6
1327 | 1233 | 326.2 | 252.9 | 253.7 | 247.3 | 249.8 | 236.7 | 241.7
1328 | 1234 | 326.3 | 252.9 | 253.7 | 247.3 | 249.8 | 236.8 | 241.7
1329 | 1235 | 326.3 | 253 | 253.7 | 247.3 | 249.8 | 236.9 | 241.7
1330 | 1236 | 326.3 | 253 | 253.7 | 247.3 | 249.8 | 237 | 241.7
1331 | 1237 | 326.2 | 253 | 253.7 | 247.4 | 249.8 | 237 | 241.7
1332 | 1238 | 326.1 | 253.1 | 253.7 | 247.4 | 249.8 | 237 | 241.8
1333 | 1239 | 326.1 | 253.1 | 253.8 | 247.4 | 249.8 | 237 | 241.8
1334 | 1240 | 326.1 | 253.1 | 253.8 | 247.4 | 249.8 | 237.1 | 241.8
1335 | 1241 | 326 | 253.1 | 253.8 | 247.4 | 249.8 | 237 | 241.8
1336 | 1242 | 325.9 | 253.1 | 253.8 | 247.5 | 249.8 | 237.1 | 241.9
1337 | 1243 | 325.9 | 253.2 | 253.8 | 247.5 | 249.8 | 237 | 241.9
1338 | 1244 | 325.9 | 253.2 | 253.9 | 247.5 | 249.8 | 237.1 | 241.9
1339 | 1245 | 325.8 | 253.3 | 253.9 | 247.5 | 249.8 | 237 | 241.9
1340 | 1246 | 325.7 | 253.3 | 253.9 | 247.5 | 249.8 | 237 | 242
1341 | 1247 | 325.6 | 253.3 | 253.9 | 247.6 | 249.7 | 237.1 | 242
1342 | 1248 | 325.6 | 253.4 | 253.9 | 247.6 | 249.7 | 237.2 | 242
1343 | 1249 | 325.6 | 253.4 | 254 | 247.6 | 249.7 | 237.1 | 242
1344 | 1250 | 325.6 | 253.4 | 254 | 247.6 | 249.7 | 237.1 | 242
1345 | 1251 | 325.5 | 253.4 | 254 | 247.6 | 249.7 | 237.1 | 242.1
1346 | 1252 | 325.4 | 253.5 | 254.1 | 247.7 | 249.7 | 237 | 242.1
1347 | 1253 | 325.2 | 253.5 | 254.2 | 247.7 | 249.7 | 236.9 | 242.1
1348 | 1254 | 325.1 | 253.5 | 254.2 | 247.7 | 249.6 | 236.9 | 242.1
1349 | 1255 | 324.9 | 253.5 | 254.2 | 247.7 | 249.6 | 236.9 | 242.2
1350 | 1256 | 324.7 | 253.6 | 254.3 | 247.7 | 249.6 | 236.8 | 242.2
1351 | 1257 | 324.5 | 253.6 | 254.3 | 247.8 | 249.6 | 236.8 | 242.2
1352 | 1258 | 324.3 | 253.6 | 254.3 | 247.8 | 249.5 | 236.9 | 242.2
1353 | 1259 | 324.1 | 253.6 | 254.3 | 247.8 | 249.5 | 236.9 | 242.2
1354 | 1260 | 323.8 | 253.6 | 254.3 | 247.8 | 249.5 | 236.9 | 242.3
1355 | 1261 | 323.4 | 253.6 | 254.3 | 247.9 | 249.4 | 237 | 242.3
1356 | 1262 | 323.1 | 253.6 | 254.4 | 247.9 | 249.4 | 236.8 | 242.3
1357 | 1263 | 322.8 | 253.7 | 254.4 | 247.9 | 249.4 | 236.6 | 242.3
1358 | 1264 | 322.5 | 253.7 | 254.4 | 247.9 | 249.3 | 236.6 | 242.3
1359 | 1265 | 322.1 | 253.7 | 254.4 | 247.9 | 249.2 | 236.5 | 242.3
1360 | 1266 | 321.7 | 253.6 | 254.4 | 248 | 249.2 | 236.6 | 242.3
1361 | 1267 | 321.2 | 253.6 | 254.4 | 248 | 249.1 | 236.5 | 242.4
1362 | 1268 | 320.8 | 253.7 | 254.4 | 248 | 249.1 | 236.4 | 242.4
1363 | 1269 | 320.4 | 253.7 | 254.5 | 248 | 249.1 | 236.4 | 242.4
1364 | 1270 | 320 | 253.7 | 254.5 | 248 | 249.1 | 236.5 | 242.4
1365 | 1271 | 319.7 | 253.7 | 254.5 | 248 | 249.1 | 236.5 | 242.4
1366 | 1272 | 319.2 | 253.8 | 254.5 | 248 | 249 | 236.6 | 242.4
1367 | 1273 | 318.7 | 253.8 | 254.5 | 248 | 249 | 236.6 | 242.4
1368 | 1274 | 318.2 | 253.8 | 254.5 | 248.1 | 249 | 236.5 | 242.4
1369 | 1275 | 317.8 | 253.8 | 254.6 | 248.1 | 249 | 236.4 | 242.4
1370 | 1276 | 317.4 | 253.8 | 254.6 | 248.1 | 249 | 236.3 | 242.4
1371 | 1277 | 316.9 | 253.8 | 254.6 | 248.1 | 248.9 | 236.3 | 242.4
1372 | 1278 | 316.5 | 253.8 | 254.6 | 248.1 | 248.9 | 236.4 | 242.4
1373 | 1279 | 316.1 | 253.8 | 254.7 | 248.1 | 248.9 | 236.3 | 242.4
1374 | 1280 | 315.6 | 253.8 | 254.7 | 248.1 | 248.8 | 236.1 | 242.4
1375 | 1281 | 315.1 | 253.8 | 254.7 | 248.1 | 248.8 | 236 | 242.4
1376 | 1282 | 314.7 | 253.8 | 254.7 | 248.1 | 248.8 | 236 | 242.4
1377 | 1283 | 314.3 | 253.8 | 254.8 | 248.1 | 248.7 | 236 | 242.4
1378 | 1284 | 313.9 | 253.8 | 254.8 | 248.2 | 248.6 | 235.9 | 242.4
1379 | 1285 | 313.6 | 253.8 | 254.8 | 248.2 | 248.6 | 235.9 | 242.4
1380 | 1286 | 313.2 | 253.8 | 254.8 | 248.2 | 248.5 | 235.8 | 242.4
1381 | 1287 | 312.7 | 253.8 | 254.9 | 248.2 | 248.5 | 235.7 | 242.4
1382 | 1288 | 312.3 | 253.7 | 254.9 | 248.2 | 248.5 | 235.6 | 242.3
1383 | 1289 | 311.9 | 253.7 | 254.9 | 248.2 | 248.4 | 235.6 | 242.3
1384 | 1290 | 311.3 | 253.7 | 254.9 | 248.2 | 248.4 | 235.4 | 242.3
1385 | 1291 | 310.8 | 253.7 | 254.9 | 248.2 | 248.3 | 235.3 | 242.3
1386 | 1292 | 310.3 | 253.7 | 254.9 | 248.2 | 248.3 | 235.2 | 242.3
1387 | 1293 | 309.9 | 253.7 | 254.9 | 248.2 | 248.2 | 235.1 | 242.3
1388 | 1294 | 309.5 | 253.7 | 254.9 | 248.2 | 248.2 | 235 | 242.3
1389 | 1295 | 308.9 | 254 | 254 | 248.7 | 248.6 | 235.1 | 242.2
1390 | 1296 | 308.5 | 253.8 | 254.6 | 248.4 | 248.3 | 235 | 242.2
1391 | 1297 | 307.9 | 254.4 | 253.1 | 249 | 248.9 | 235.3 | 242.1
1392 | 1298 | 307.6 | 253.6 | 254.9 | 248.2 | 248.1 | 234.9 | 242.2
1393 | 1299 | 307.1 | 253.6 | 254.9 | 248.2 | 248 | 235 | 242.2
1394 | 1300 | 306.6 | 253.6 | 254.9 | 248.2 | 248 | 234.9 | 242.1
1395 | 1301 | 306.3 | 253.6 | 254.9 | 248.2 | 248 | 234.8 | 242.1
1396 | 1302 | 305.9 | 253.6 | 254.9 | 248.2 | 247.9 | 234.6 | 242.1
1397 | 1303 | 305.3 | 254.3 | 253.2 | 248.8 | 248.7 | 235 | 242
1398 | 1304 | 304.8 | 254.5 | 252.4 | 249.2 | 249 | 235 | 241.9
1399 | 1305 | 304.4 | 254.6 | 252.2 | 249.1 | 248.9 | 234.8 | 241.9
1400 | 1306 | 304.1 | 253.6 | 254.6 | 248.2 | 247.8 | 234.2 | 242
1401 | 1307 | 303.7 | 253.5 | 254.8 | 248.1 | 247.6 | 233.9 | 241.9
1402 | 1308 | 303.3 | 253.4 | 254.8 | 248.1 | 247.5 | 233.7 | 241.9
1403 | 1309 | 302.9 | 253.4 | 254.8 | 248.1 | 247.4 | 233.6 | 241.9
1404 | 1310 | 302.4 | 253.4 | 254.8 | 248.1 | 247.3 | 233.6 | 241.8
1405 | 1311 | 302 | 253.3 | 254.8 | 248 | 247.3 | 233.4 | 241.8
1406 | 1312 | 301.6 | 253.3 | 254.8 | 248 | 247.2 | 233.3 | 241.8
1407 | 1313 | 301.2 | 253.3 | 254.7 | 248 | 247.1 | 233.1 | 241.7
1408 | 1314 | 300.7 | 253.2 | 254.7 | 248 | 247.1 | 232.9 | 241.7
1409 | 1315 | 300.3 | 253.2 | 254.7 | 248 | 247 | 232.8 | 241.7
1410 | 1316 | 299.9 | 253.2 | 254.6 | 247.9 | 246.9 | 232.7 | 241.6
1411 | 1317 | 299.5 | 253.1 | 254.6 | 247.9 | 246.9 | 232.7 | 241.6
1412 | 1318 | 299 | 253.1 | 254.6 | 247.9 | 246.8 | 232.6 | 241.5
1413 | 1319 | 298.6 | 253 | 254.6 | 247.9 | 246.7 | 232.4 | 241.5
1414 | 1320 | 298.1 | 253 | 254.6 | 247.8 | 246.6 | 232.3 | 241.4
1415 | 1321 | 297.7 | 253 | 254.5 | 247.8 | 246.6 | 232 | 241.4
1416 | 1322 | 297.4 | 252.9 | 254.5 | 247.8 | 246.5 | 231.7 | 241.3
1417 | 1323 | 297 | 252.9 | 254.5 | 247.7 | 246.4 | 231.4 | 241.3
1418 | 1324 | 296.5 | 252.8 | 254.5 | 247.7 | 246.3 | 231.3 | 241.2
1419 | 1325 | 296.1 | 252.8 | 254.5 | 247.7 | 246.2 | 231 | 241.2
1420 | 1326 | 295.8 | 252.7 | 254.4 | 247.6 | 246.2 | 230.7 | 241.1
1421 | 1327 | 295.4 | 252.7 | 254.4 | 247.6 | 246.1 | 230.5 | 241.1
1422 | 1328 | 294.9 | 252.6 | 254.4 | 247.6 | 246 | 230.4 | 241
1423 | 1329 | 294.6 | 252.5 | 254.4 | 247.5 | 246 | 230.2 | 241
1424 | 1330 | 294.2 | 252.5 | 254.4 | 247.5 | 245.9 | 229.9 | 240.9
1425 | 1331 | 293.7 | 252.4 | 254.3 | 247.4 | 245.8 | 229.7 | 240.9
1426 | 1332 | 293.2 | 252.3 | 254.3 | 247.4 | 245.7 | 229.5 | 240.8
1427 | 1333 | 292.7 | 252.3 | 254.3 | 247.4 | 245.7 | 229.5 | 240.7
1428 | 1334 | 292.2 | 252.2 | 254.2 | 247.3 | 245.6 | 229.3 | 240.7
1429 | 1335 | 291.6 | 252.1 | 254.2 | 247.3 | 245.5 | 229.1 | 240.6
1430 | 1336 | 291.2 | 252 | 254.1 | 247.2 | 245.4 | 228.7 | 240.5
1431 | 1337 | 290.7 | 252 | 254.1 | 247.2 | 245.3 | 228.6 | 240.5
1432 | 1338 | 290.3 | 251.9 | 254.1 | 247.1 | 245.2 | 228.5 | 240.4
1433 | 1339 | 289.9 | 251.8 | 254 | 247.1 | 245.1 | 228.2 | 240.3
1434 | 1340 | 289.6 | 251.8 | 254 | 247 | 245 | 228.1 | 240.3
1435 | 1341 | 289.2 | 251.7 | 254 | 247 | 245 | 228 | 240.2
1436 | 1342 | 288.8 | 251.6 | 253.9 | 247 | 245 | 227.8 | 240.1
1437 | 1343 | 288.4 | 251.6 | 253.9 | 246.9 | 244.9 | 227.6 | 240
1438 | 1344 | 288 | 251.5 | 253.9 | 246.9 | 244.8 | 227.4 | 240
1439 | 1345 | 287.5 | 251.4 | 253.8 | 246.8 | 244.8 | 227.3 | 239.9
1440 | 1346 | 287 | 251.3 | 253.8 | 246.8 | 244.7 | 227 | 239.8
1441 | 1347 | 286.5 | 251.3 | 253.7 | 246.7 | 244.6 | 226.9 | 239.7
1442 | 1348 | 286.2 | 251.2 | 253.7 | 246.7 | 244.5 | 226.7 | 239.7
1443 | 1349 | 285.8 | 251.1 | 253.6 | 246.6 | 244.4 | 226.6 | 239.6
1444 | 1350 | 285.4 | 251 | 253.6 | 246.5 | 244.3 | 226.4 | 239.5
1445 | 1351 | 284.9 | 250.9 | 253.5 | 246.5 | 244.2 | 226.4 | 239.4
1446 | 1352 | 284.5 | 250.9 | 253.5 | 246.4 | 244.1 | 226.3 | 239.4
1447 | 1353 | 284.1 | 250.8 | 253.4 | 246.3 | 244 | 226.2 | 239.3
1448 | 1354 | 283.8 | 250.7 | 253.3 | 246.3 | 243.8 | 225.9 | 239.2
1449 | 1355 | 283.5 | 250.6 | 253.3 | 246.2 | 243.7 | 225.6 | 239.1
1450 | 1356 | 283.1 | 250.5 | 253.2 | 246.1 | 243.7 | 225.3 | 239
1451 | 1357 | 282.6 | 250.4 | 253.2 | 246.1 | 243.6 | 225.2 | 238.9
1452 | 1358 | 282.2 | 250.3 | 253.1 | 246 | 243.5 | 224.8 | 238.8
1453 | 1359 | 281.7 | 250.3 | 253 | 245.9 | 243.4 | 224.4 | 238.8
1454 | 1360 | 281.3 | 250.2 | 253 | 245.9 | 243.3 | 224.3 | 238.7
1455 | 1361 | 280.9 | 250.1 | 252.9 | 245.8 | 243.2 | 224.1 | 238.6
1456 | 1362 | 280.4 | 250 | 252.8 | 245.7 | 243.1 | 223.9 | 238.5
1457 | 1363 | 279.9 | 249.9 | 252.8 | 245.7 | 243.1 | 223.7 | 238.4
1458 | 1364 | 279.3 | 249.8 | 252.7 | 245.6 | 243 | 223.4 | 238.3
1459 | 1365 | 279 | 249.7 | 252.6 | 245.5 | 242.9 | 223.2 | 238.2
1460 | 1366 | 278.6 | 249.6 | 252.6 | 245.4 | 242.8 | 223.2 | 238.2
1461 | 1367 | 278.1 | 249.5 | 252.5 | 245.4 | 242.7 | 223 | 238.1
1462 | 1368 | 277.7 | 249.4 | 252.4 | 245.3 | 242.6 | 222.9 | 238
1463 | 1369 | 277.4 | 249.3 | 252.4 | 245.2 | 242.5 | 222.8 | 237.9
1464 | 1370 | 277.1 | 249.2 | 252.3 | 245.2 | 242.4 | 222.6 | 237.8
1465 | 1371 | 276.7 | 249.1 | 252.2 | 245.1 | 242.3 | 222.4 | 237.7
1466 | 1372 | 276.3 | 249 | 252.1 | 245 | 242.2 | 222.2 | 237.6
1467 | 1373 | 275.9 | 249 | 251.8 | 245 | 242.2 | 222.2 | 237.5
1468 | 1374 | 275.5 | 248.9 | 251.6 | 245 | 242.1 | 222.1 | 237.4
1469 | 1375 | 275.2 | 248.9 | 251.4 | 245 | 242.1 | 222.1 | 237.3
1470 | 1376 | 274.7 | 248.6 | 251.8 | 244.7 | 241.7 | 221.8 | 237.2
1471 | 1377 | 274.2 | 248.5 | 251.7 | 244.6 | 241.5 | 221.6 | 237.1
1472 | 1378 | 273.9 | 248.4 | 251.7 | 244.5 | 241.4 | 221.5 | 237
1473 | 1379 | 273.4 | 248.3 | 251.6 | 244.4 | 241.2 | 221.3 | 236.9
1474 | 1380 | 273 | 248.2 | 251.5 | 244.3 | 241.1 | 221.1 | 236.8
1475 | 1381 | 272.5 | 248.1 | 251.4 | 244.3 | 241 | 221 | 236.7
1476 | 1382 | 272.1 | 248 | 251.3 | 244.2 | 240.8 | 221 | 236.5
1477 | 1383 | 271.6 | 247.9 | 251.3 | 244.1 | 240.6 | 220.9 | 236.4
1478 | 1384 | 271.2 | 247.8 | 251.2 | 244 | 240.5 | 220.8 | 236.3
1479 | 1385 | 270.8 | 247.7 | 251 | 243.9 | 240.4 | 220.6 | 236.2
1480 | 1386 | 270.5 | 247.6 | 251 | 243.8 | 240.3 | 220.5 | 236.1
1481 | 1387 | 270 | 247.5 | 250.9 | 243.7 | 240.2 | 220.3 | 236
1482 | 1388 | 269.5 | 247.4 | 250.7 | 243.6 | 240 | 220.3 | 235.9
1483 | 1389 | 269.1 | 247.3 | 250.7 | 243.5 | 239.9 | 220.1 | 235.8
1484 | 1390 | 268.7 | 247.2 | 250.6 | 243.4 | 239.8 | 220 | 235.7
1485 | 1391 | 268.2 | 247.1 | 250.5 | 243.3 | 239.6 | 220 | 235.5
1486 | 1392 | 267.7 | 247 | 250.3 | 243.2 | 239.4 | 219.8 | 235.4
1487 | 1393 | 267.4 | 246.9 | 250.3 | 243.1 | 239.3 | 219.6 | 235.3
1488 | 1394 | 267.1 | 246.8 | 250.2 | 243 | 239.1 | 219.3 | 235.2
1489 | 1395 | 266.7 | 246.7 | 250.1 | 242.8 | 239 | 219 | 235.1
1490 | 1396 | 266.3 | 246.5 | 250 | 242.7 | 238.9 | 218.7 | 235
1491 | 1397 | 265.9 | 246.4 | 249.9 | 242.6 | 238.7 | 218.3 | 234.8
1492 | 1398 | 265.6 | 246.3 | 249.8 | 242.5 | 238.6 | 218.2 | 234.7
1493 | 1399 | 265.3 | 246.2 | 249.7 | 242.4 | 238.5 | 217.9 | 234.6
1494 | 1400 | 264.9 | 246.1 | 249.5 | 242.3 | 238.3 | 217.7 | 234.5
1495 | 1401 | 264.5 | 246 | 249.5 | 242.2 | 238.1 | 217.6 | 234.4
1496 | 1402 | 264.2 | 245.8 | 249.3 | 242.1 | 238 | 217.3 | 234.3
1497 | 1403 | 263.8 | 245.7 | 249.2 | 242 | 237.8 | 217 | 234.2
1498 | 1404 | 263.5 | 245.6 | 249.1 | 241.9 | 237.7 | 216.9 | 234.1
1499 | 1405 | 263.1 | 245.4 | 249 | 241.8 | 237.6 | 216.9 | 233.9
1500 | 1406 | 262.8 | 245.3 | 248.9 | 241.7 | 237.4 | 216.8 | 233.8
1501 | 1407 | 262.3 | 245.2 | 248.8 | 241.6 | 237.3 | 216.7 | 233.7
1502 | 1408 | 261.9 | 245.1 | 248.7 | 241.5 | 237.1 | 216.6 | 233.6
1503 | 1409 | 261.5 | 244.9 | 248.5 | 241.3 | 237 | 216.3 | 233.4
1504 | 1410 | 261 | 244.8 | 248.4 | 241.2 | 236.8 | 216.1 | 233.3
1505 | 1411 | 260.7 | 244.7 | 248.3 | 241.1 | 236.7 | 215.8 | 233.2
1506 | 1412 | 260.3 | 244.5 | 248.2 | 241 | 236.6 | 215.6 | 233.1
1507 | 1413 | 260 | 244.4 | 248.1 | 240.9 | 236.4 | 215.5 | 233
1508 | 1414 | 259.6 | 244.3 | 248 | 240.8 | 236.2 | 215.4 | 232.8
1509 | 1415 | 259.2 | 244.1 | 247.9 | 240.6 | 236.1 | 215.2 | 232.7
1510 | 1416 | 258.8 | 244 | 247.7 | 240.5 | 235.9 | 215.1 | 232.6
1511 | 1417 | 258.5 | 243.9 | 247.6 | 240.4 | 235.8 | 215 | 232.4
1512 | 1418 | 258.2 | 243.8 | 247.5 | 240.3 | 235.6 | 214.9 | 232.3
1513 | 1419 | 257.8 | 243.6 | 247.4 | 240.2 | 235.5 | 214.8 | 232.2
1514 | 1420 | 257.4 | 243.5 | 247.3 | 240.1 | 235.3 | 214.6 | 232.1
1515 | 1421 | 257 | 243.4 | 247.2 | 239.9 | 235.1 | 214.4 | 231.9
1516 | 1422 | 256.6 | 243.3 | 247.1 | 239.8 | 235 | 214.1 | 231.8
1517 | 1423 | 256.3 | 243.1 | 246.9 | 239.7 | 234.8 | 213.8 | 231.7
1518 | 1424 | 256 | 243 | 246.8 | 239.5 | 234.7 | 213.6 | 231.5
1519 | 1425 | 255.6 | 242.9 | 246.7 | 239.4 | 234.5 | 213.3 | 231.4
1520 | 1426 | 255.3 | 242.7 | 246.6 | 239.3 | 234.4 | 213.1 | 231.3
1521 | 1427 | 255 | 242.6 | 246.5 | 239.2 | 234.2 | 212.8 | 231.1
1522 | 1428 | 254.6 | 242.4 | 246.4 | 239.1 | 234 | 212.7 | 231
1523 | 1429 | 254.2 | 242.3 | 246.2 | 238.9 | 233.8 | 212.6 | 230.8
1524 | 1430 | 253.8 | 242.2 | 246.1 | 238.8 | 233.6 | 212.4 | 230.7
1525 | 1431 | 253.4 | 242 | 246 | 238.7 | 233.5 | 212.2 | 230.6
1526 | 1432 | 253.1 | 241.9 | 245.8 | 238.6 | 233.3 | 212 | 230.4
1527 | 1433 | 252.8 | 241.8 | 245.7 | 238.5 | 233.2 | 211.8 | 230.3
1528 | 1434 | 252.5 | 241.6 | 245.6 | 238.3 | 233.1 | 211.6 | 230.2
1529 | 1435 | 252.2 | 241.5 | 245.4 | 238.2 | 232.9 | 211.5 | 230
1530 | 1436 | 251.8 | 241.3 | 245.3 | 238.1 | 232.7 | 211.4 | 229.9
1531 | 1437 | 251.4 | 241.2 | 245.2 | 238 | 232.5 | 211.4 | 229.7
1532 | 1438 | 251 | 241.1 | 245.1 | 237.9 | 232.3 | 211.3 | 229.6
1533 | 1439 | 250.7 | 240.9 | 244.9 | 237.7 | 232.1 | 211.1 | 229.5
1534 | 1440 | 250.4 | 240.8 | 244.8 | 237.6 | 232 | 211 | 229.3
1535 | 1441 | 250 | 240.7 | 244.7 | 237.5 | 231.8 | 211 | 229.2
1536 | 1442 | 249.7 | 240.5 | 244.5 | 237.4 | 231.7 | 210.8 | 229
1537 | 1443 | 249.3 | 240.4 | 244.4 | 237.2 | 231.5 | 210.7 | 228.9
1538 | 1444 | 248.9 | 240.3 | 244.3 | 237.1 | 231.3 | 210.6 | 228.7
1539 | 1445 | 248.5 | 240.2 | 244.1 | 236.9 | 231.2 | 210.5 | 228.6
1540 | 1446 | 248.2 | 240 | 244 | 236.8 | 231 | 210.4 | 228.4
1541 | 1447 | 247.8 | 239.9 | 243.8 | 236.7 | 230.8 | 210.3 | 228.3
1542 | 1448 | 247.4 | 239.8 | 243.7 | 236.5 | 230.6 | 210.1 | 228.1
1543 | 1449 | 247 | 239.6 | 243.6 | 236.4 | 230.5 | 209.9 | 228
1544 | 1450 | 246.7 | 239.5 | 243.4 | 236.3 | 230.3 | 209.7 | 227.8
1545 | 1451 | 246.4 | 239.3 | 243.3 | 236.1 | 230.1 | 209.6 | 227.7
1546 | 1452 | 246 | 239.2 | 243.1 | 236 | 229.9 | 209.5 | 227.5
1547 | 1453 | 245.6 | 239.1 | 243 | 235.8 | 229.7 | 209.4 | 227.4
1548 | 1454 | 245.3 | 238.9 | 242.9 | 235.7 | 229.5 | 209.3 | 227.3
1549 | 1455 | 244.9 | 238.8 | 242.7 | 235.6 | 229.3 | 209.2 | 227.1
1550 | 1456 | 244.5 | 238.7 | 242.6 | 235.4 | 229.1 | 209.1 | 227
1551 | 1457 | 244.1 | 238.5 | 242.4 | 235.3 | 228.9 | 209 | 226.8
1552 | 1458 | 243.8 | 238.4 | 242.3 | 235.2 | 228.7 | 208.8 | 226.7
1553 | 1459 | 243.5 | 238.3 | 242.1 | 235 | 228.5 | 208.7 | 226.5
1554 | 1460 | 243.1 | 238.1 | 242 | 234.9 | 228.3 | 208.5 | 226.4
1555 | 1461 | 242.7 | 238 | 241.8 | 234.7 | 228.1 | 208.4 | 226.2
1556 | 1462 | 242.3 | 237.8 | 241.7 | 234.6 | 227.9 | 208.1 | 226.1
1557 | 1463 | 242 | 237.7 | 241.5 | 234.4 | 227.8 | 207.8 | 225.9
1558 | 1464 | 241.6 | 237.5 | 241.4 | 234.3 | 227.6 | 207.6 | 225.8
1559 | 1465 | 241.3 | 237.4 | 241.2 | 234.1 | 227.4 | 207.5 | 225.6
1560 | 1466 | 241 | 237.3 | 241.1 | 234 | 227.2 | 207.3 | 225.5
1561 | 1467 | 240.7 | 237.1 | 240.9 | 233.8 | 227 | 207.2 | 225.3
1562 | 1468 | 240.4 | 237 | 240.8 | 233.7 | 226.8 | 207 | 225.2
1563 | 1469 | 240.1 | 236.8 | 240.6 | 233.5 | 226.6 | 206.8 | 225
1564 | 1470 | 239.7 | 236.7 | 240.5 | 233.4 | 226.5 | 206.5 | 224.9
1565 | 1471 | 239.4 | 236.5 | 240.3 | 233.2 | 226.3 | 206.5 | 224.8
1566 | 1472 | 239.1 | 236.4 | 240.2 | 233.1 | 226.1 | 206.3 | 224.6
1567 | 1473 | 238.8 | 236.2 | 240 | 232.9 | 225.9 | 206.1 | 224.5
1568 | 1474 | 238.6 | 236 | 239.9 | 232.8 | 225.8 | 205.8 | 224.3
1569 | 1475 | 238.3 | 235.9 | 239.7 | 232.6 | 225.6 | 205.6 | 224.2
1570 | 1476 | 238 | 235.7 | 239.5 | 232.4 | 225.4 | 205.3 | 224
1571 | 1477 | 237.7 | 235.6 | 239.4 | 232.3 | 225.2 | 205.2 | 223.9
1572 | 1478 | 237.3 | 235.4 | 239.3 | 232.2 | 225 | 205.1 | 223.7
1573 | 1479 | 236.9 | 235.2 | 239.1 | 232 | 224.9 | 204.8 | 223.6
1574 | 1480 | 236.6 | 235.1 | 239 | 231.9 | 224.7 | 204.5 | 223.4
1575 | 1481 | 236.3 | 234.9 | 238.8 | 231.7 | 224.5 | 204.3 | 223.3
1576 | 1482 | 236 | 234.8 | 238.6 | 231.6 | 224.4 | 204 | 223.2
1577 | 1483 | 235.8 | 234.6 | 238.5 | 231.4 | 224.2 | 203.8 | 223
1578 | 1484 | 235.5 | 234.4 | 238.4 | 231.2 | 224 | 203.6 | 222.9
1579 | 1485 | 235.2 | 234.3 | 238.2 | 231.1 | 223.9 | 203.4 | 222.7
1580 | 1486 | 234.8 | 234.1 | 238 | 230.9 | 223.7 | 203.2 | 222.6
1581 | 1487 | 234.5 | 234 | 237.9 | 230.8 | 223.5 | 202.9 | 222.4
1582 | 1488 | 234.1 | 233.8 | 237.7 | 230.6 | 223.3 | 202.8 | 222.3
1583 | 1489 | 233.8 | 233.6 | 237.6 | 230.4 | 223.1 | 202.6 | 222.1
1584 | 1490 | 233.5 | 233.5 | 237.4 | 230.3 | 223 | 202.4 | 222
1585 | 1491 | 233.1 | 233.3 | 237.3 | 230.1 | 222.8 | 202.2 | 221.8
1586 | 1492 | 232.8 | 233.1 | 237.1 | 229.9 | 222.6 | 201.9 | 221.6
1587 | 1493 | 232.6 | 233 | 237 | 229.8 | 222.4 | 201.7 | 221.5
1588 | 1494 | 232.3 | 232.8 | 236.8 | 229.6 | 222.3 | 201.5 | 221.3
1589 | 1495 | 231.9 | 232.6 | 236.6 | 229.4 | 222.1 | 201.3 | 221.2
1590 | 1496 | 231.7 | 232.5 | 236.5 | 229.3 | 222 | 201.1 | 221
1591 | 1497 | 231.4 | 232.3 | 236.4 | 229.1 | 221.9 | 200.8 | 220.9
1592 | 1498 | 231.1 | 232.2 | 236.2 | 229 | 221.7 | 200.6 | 220.7
1593 | 1499 | 230.8 | 232 | 236 | 228.8 | 221.6 | 200.5 | 220.6
1594 | 1500 | 230.5 | 231.8 | 235.9 | 228.6 | 221.4 | 200.1 | 220.4
1595 | 1501 | 230.3 | 231.7 | 235.7 | 228.5 | 221.3 | 199.8 | 220.3
1596 | 1502 | 230 | 231.5 | 235.6 | 228.3 | 221.1 | 199.7 | 220.1
1597 | 1503 | 229.7 | 231.3 | 235.4 | 228.2 | 220.9 | 199.5 | 220
1598 | 1504 | 229.5 | 231.2 | 235.3 | 228 | 220.8 | 199.3 | 219.8
1599 | 1505 | 229.1 | 231 | 235.1 | 227.9 | 220.6 | 199.1 | 219.7
1600 | 1506 | 228.7 | 230.8 | 234.9 | 227.7 | 220.4 | 198.8 | 219.5
1601 | 1507 | 228.4 | 230.7 | 234.8 | 227.5 | 220.3 | 198.7 | 219.4
1602 | 1508 | 228.2 | 230.5 | 234.6 | 227.4 | 220.1 | 198.6 | 219.2
1603 | 1509 | 227.9 | 230.3 | 234.4 | 227.2 | 219.9 | 198.4 | 219.1
1604 | 1510 | 227.5 | 230.2 | 234.3 | 227.1 | 219.8 | 198.5 | 218.9
1605 | 1511 | 227.1 | 230 | 234.1 | 226.9 | 219.6 | 198.3 | 218.8
1606 | 1512 | 226.9 | 229.8 | 234 | 226.8 | 219.5 | 198.2 | 218.6
1607 | 1513 | 226.6 | 229.7 | 233.8 | 226.6 | 219.3 | 198.2 | 218.5
1608 | 1514 | 226.2 | 229.5 | 233.6 | 226.4 | 219.2 | 198.1 | 218.3
1609 | 1515 | 225.8 | 229.3 | 233.5 | 226.3 | 219 | 198.1 | 218.1
1610 | 1516 | 225.5 | 229.2 | 233.3 | 226.1 | 218.8 | 198 | 218
1611 | 1517 | 225.2 | 229 | 233.1 | 225.9 | 218.7 | 197.9 | 217.8
1612 | 1518 | 225 | 228.9 | 233 | 225.8 | 218.5 | 197.8 | 217.7
1613 | 1519 | 224.8 | 228.7 | 232.8 | 225.6 | 218.4 | 197.8 | 217.5
1614 | 1520 | 224.5 | 228.5 | 232.7 | 225.5 | 218.2 | 197.8 | 217.4
1615 | 1521 | 224.2 | 228.4 | 232.5 | 225.3 | 218.1 | 197.7 | 217.2
1616 | 1522 | 223.8 | 228.2 | 232.3 | 225.1 | 217.9 | 197.6 | 217
1617 | 1523 | 223.5 | 228.1 | 232.2 | 225 | 217.8 | 197.5 | 216.9
1618 | 1524 | 223.3 | 227.9 | 232 | 224.8 | 217.6 | 197.3 | 216.7
1619 | 1525 | 223 | 227.7 | 231.8 | 224.7 | 217.4 | 197.2 | 216.6
1620 | 1526 | 222.8 | 227.6 | 231.7 | 224.5 | 217.2 | 197 | 216.4
1621 | 1527 | 222.5 | 227.4 | 231.5 | 224.3 | 217.1 | 196.9 | 216.2
1622 | 1528 | 222.2 | 227.3 | 231.3 | 224.2 | 216.9 | 196.8 | 216.1
1623 | 1529 | 221.9 | 227.1 | 231.2 | 224 | 216.7 | 196.5 | 215.9
1624 | 1530 | 221.6 | 226.9 | 231 | 223.8 | 216.5 | 196.3 | 215.8
1625 | 1531 | 221.2 | 226.8 | 230.8 | 223.7 | 216.4 | 196.1 | 215.6
1626 | 1532 | 220.9 | 226.6 | 230.6 | 223.5 | 216.2 | 196.1 | 215.4
1627 | 1533 | 220.6 | 226.4 | 230.5 | 223.3 | 216 | 196 | 215.3
1628 | 1534 | 220.3 | 226.3 | 230.3 | 223.2 | 215.8 | 195.6 | 215.1
1629 | 1535 | 220 | 226.1 | 230.1 | 223 | 215.7 | 195.3 | 215
1630 | 1536 | 219.7 | 225.9 | 229.9 | 222.8 | 215.5 | 195.2 | 214.8
1631 | 1537 | 219.5 | 225.8 | 229.8 | 222.7 | 215.3 | 195 | 214.7
1632 | 1538 | 219.2 | 225.6 | 229.6 | 222.5 | 215.2 | 194.9 | 214.5
1633 | 1539 | 219 | 225.4 | 229.4 | 222.4 | 215 | 194.6 | 214.3
1634 | 1540 | 218.8 | 225.2 | 229.3 | 222.2 | 214.8 | 194.2 | 214.2
1635 | 1541 | 218.6 | 225.1 | 229.1 | 222 | 214.7 | 193.9 | 214
1636 | 1542 | 218.3 | 224.9 | 228.9 | 221.9 | 214.5 | 193.6 | 213.9
1637 | 1543 | 218 | 224.7 | 228.7 | 221.7 | 214.3 | 193.5 | 213.7
1638 | 1544 | 217.8 | 224.5 | 228.6 | 221.5 | 214.1 | 193.4 | 213.6
1639 | 1545 | 217.4 | 224.4 | 228.4 | 221.4 | 214 | 193.1 | 213.4
1640 | 1546 | 217.2 | 224.2 | 228.2 | 221.2 | 213.8 | 192.8 | 213.3
1641 | 1547 | 217 | 224 | 228 | 221 | 213.7 | 192.6 | 213.1
1642 | 1548 | 216.8 | 223.9 | 227.9 | 220.9 | 213.5 | 192.5 | 213
1643 | 1549 | 216.5 | 223.7 | 227.7 | 220.7 | 213.3 | 192.3 | 212.8
1644 | 1550 | 216.1 | 223.5 | 227.5 | 220.6 | 213.1 | 192.1 | 212.7
1645 | 1551 | 215.8 | 223.3 | 227.3 | 220.4 | 212.9 | 192.1 | 212.5
1646 | 1552 | 215.5 | 223.1 | 227.2 | 220.3 | 212.7 | 191.9 | 212.3
1647 | 1553 | 215.3 | 223 | 227 | 220.1 | 212.6 | 191.7 | 212.2
1648 | 1554 | 215.1 | 222.8 | 226.8 | 219.9 | 212.4 | 191.5 | 212
1649 | 1555 | 214.8 | 222.6 | 226.6 | 219.8 | 212.2 | 191.4 | 211.9
1650 | 1556 | 214.6 | 222.5 | 226.5 | 219.6 | 212 | 191.2 | 211.7
1651 | 1557 | 214.3 | 222.3 | 226.3 | 219.5 | 211.8 | 191.1 | 211.5
1652 | 1558 | 214.1 | 222.1 | 226.1 | 219.3 | 211.6 | 191 | 211.4
1653 | 1559 | 213.8 | 221.9 | 225.9 | 219.1 | 211.4 | 190.8 | 211.2
1654 | 1560 | 213.5 | 221.8 | 225.8 | 219 | 211.2 | 190.6 | 211.1
1655 | 1561 | 213.3 | 221.6 | 225.6 | 218.8 | 211.1 | 190.5 | 210.9
1656 | 1562 | 213 | 221.4 | 225.4 | 218.6 | 210.9 | 190.2 | 210.7
1657 | 1563 | 212.7 | 221.3 | 225.3 | 218.5 | 210.7 | 190 | 210.6
1658 | 1564 | 212.4 | 221.1 | 225.1 | 218.3 | 210.6 | 189.8 | 210.4
1659 | 1565 | 212.1 | 220.9 | 224.9 | 218.1 | 210.4 | 189.7 | 210.3
1660 | 1566 | 211.7 | 220.7 | 224.7 | 217.9 | 210.2 | 189.6 | 210.1
1661 | 1567 | 211.4 | 220.6 | 224.5 | 217.8 | 210.1 | 189.5 | 209.9
1662 | 1568 | 211.1 | 220.4 | 224.4 | 217.6 | 209.9 | 189.4 | 209.8
1663 | 1569 | 210.8 | 220.2 | 224.2 | 217.4 | 209.8 | 189.4 | 209.6
1664 | 1570 | 210.5 | 220.1 | 224 | 217.2 | 209.6 | 189.4 | 209.4
1665 | 1571 | 210.2 | 219.9 | 223.8 | 217.1 | 209.4 | 189.3 | 209.3
1666 | 1572 | 209.9 | 219.7 | 223.7 | 216.9 | 209.2 | 189 | 209.1
1667 | 1573 | 209.7 | 219.6 | 223.5 | 216.8 | 209 | 189 | 208.9
1668 | 1574 | 209.4 | 219.4 | 223.3 | 216.6 | 208.8 | 188.9 | 208.8
1669 | 1575 | 209.2 | 219.2 | 223.1 | 216.4 | 208.6 | 188.7 | 208.6
1670 | 1576 | 208.8 | 219.1 | 223 | 216.3 | 208.4 | 188.4 | 208.5
1671 | 1577 | 208.6 | 218.9 | 222.8 | 216.1 | 208.2 | 188.2 | 208.3
1672 | 1578 | 208.3 | 218.7 | 222.6 | 215.9 | 208 | 188 | 208.1
1673 | 1579 | 208.1 | 218.5 | 222.4 | 215.8 | 207.8 | 188 | 208
1674 | 1580 | 207.8 | 218.4 | 222.3 | 215.6 | 207.6 | 187.8 | 207.8
1675 | 1581 | 207.5 | 218.2 | 222.1 | 215.4 | 207.5 | 187.6 | 207.6
1676 | 1582 | 207.3 | 218 | 221.9 | 215.3 | 207.3 | 187.6 | 207.5
1677 | 1583 | 207 | 217.9 | 221.7 | 215.1 | 207.1 | 187.5 | 207.3
1678 | 1584 | 206.8 | 217.7 | 221.5 | 214.9 | 206.9 | 187.3 | 207.1
1679 | 1585 | 206.5 | 217.5 | 221.4 | 214.8 | 206.7 | 187.1 | 207
1680 | 1586 | 206.2 | 217.3 | 221.2 | 214.6 | 206.5 | 186.9 | 206.8
1681 | 1587 | 206 | 217.2 | 221 | 214.5 | 206.4 | 186.8 | 206.7
1682 | 1588 | 205.7 | 217 | 220.8 | 214.3 | 206.2 | 186.8 | 206.5
1683 | 1589 | 205.5 | 216.8 | 220.6 | 214.1 | 206 | 186.6 | 206.3
1684 | 1590 | 205.3 | 216.6 | 220.5 | 214 | 205.8 | 186.4 | 206.2
1685 | 1591 | 205.1 | 216.5 | 220.3 | 213.8 | 205.6 | 186.4 | 206
1686 | 1592 | 204.8 | 216.3 | 220.1 | 213.6 | 205.4 | 186.3 | 205.8
1687 | 1593 | 204.6 | 216.1 | 219.9 | 213.5 | 205.3 | 186.1 | 205.7
1688 | 1594 | 204.4 | 215.9 | 219.8 | 213.3 | 205.1 | 186 | 205.5
1689 | 1595 | 204.2 | 215.8 | 219.6 | 213.2 | 204.9 | 185.9 | 205.4
1690 | 1596 | 203.9 | 215.6 | 219.4 | 213 | 204.7 | 185.7 | 205.2
1691 | 1597 | 203.6 | 215.4 | 219.2 | 212.8 | 204.5 | 185.4 | 205.1
1692 | 1598 | 203.3 | 215.2 | 219 | 212.7 | 204.3 | 185.3 | 204.9
1693 | 1599 | 203.1 | 215 | 218.9 | 212.5 | 204.2 | 185.1 | 204.7
1694 | 1600 | 202.9 | 214.9 | 218.7 | 212.4 | 204 | 185 | 204.6
1695 | 1601 | 202.6 | 214.7 | 218.5 | 212.2 | 203.8 | 184.9 | 204.4
1696 | 1602 | 202.3 | 214.5 | 218.3 | 212 | 203.6 | 184.7 | 204.3
1697 | 1603 | 202 | 214.3 | 218.1 | 211.9 | 203.4 | 184.4 | 204.1
1698 | 1604 | 201.8 | 214.2 | 218 | 211.7 | 203.2 | 184.3 | 203.9
1699 | 1605 | 201.5 | 214 | 217.8 | 211.5 | 203 | 184.1 | 203.8
1700 | 1606 | 201.2 | 213.8 | 217.6 | 211.4 | 202.9 | 184 | 203.6
1701 | 1607 | 200.9 | 213.7 | 217.4 | 211.2 | 202.7 | 183.8 | 203.5
1702 | 1608 | 200.6 | 213.5 | 217.3 | 211 | 202.5 | 183.6 | 203.3
1703 | 1609 | 200.4 | 213.3 | 217.1 | 210.9 | 202.3 | 183.4 | 203.1
1704 | 1610 | 200.1 | 213.1 | 216.9 | 210.7 | 202.1 | 183.2 | 203
1705 | 1611 | 199.9 | 213 | 216.7 | 210.5 | 201.9 | 183.1 | 202.8
1706 | 1612 | 199.7 | 212.8 | 216.5 | 210.4 | 201.8 | 182.9 | 202.7
1707 | 1613 | 199.5 | 212.6 | 216.3 | 210.2 | 201.6 | 182.8 | 202.5
1708 | 1614 | 199.2 | 212.4 | 216.2 | 210 | 201.4 | 182.8 | 202.4
1709 | 1615 | 198.9 | 212.2 | 216 | 209.8 | 201.2 | 182.7 | 202.2
1710 | 1616 | 198.6 | 212.1 | 215.8 | 209.7 | 201 | 182.5 | 202
1711 | 1617 | 198.4 | 211.9 | 215.6 | 209.5 | 200.8 | 182.3 | 201.9
1712 | 1618 | 198.2 | 211.7 | 215.5 | 209.3 | 200.6 | 182 | 201.7
1713 | 1619 | 198 | 211.6 | 215.3 | 209.2 | 200.4 | 181.8 | 201.5
1714 | 1620 | 197.7 | 211.4 | 215.1 | 209 | 200.2 | 181.8 | 201.4
1715 | 1621 | 197.5 | 211.2 | 214.9 | 208.8 | 199.9 | 181.7 | 201.2
1716 | 1622 | 197.3 | 211 | 214.7 | 208.7 | 199.8 | 181.5 | 201.1
1717 | 1623 | 197.1 | 210.9 | 214.6 | 208.5 | 199.6 | 181.4 | 200.9
1718 | 1624 | 196.9 | 210.7 | 214.4 | 208.3 | 199.4 | 181.1 | 200.7
1719 | 1625 | 196.7 | 210.5 | 214.2 | 208.2 | 199.2 | 180.9 | 200.6
1720 | 1626 | 196.5 | 210.3 | 214 | 208 | 199 | 180.7 | 200.4

## C6-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38930.5991 | 1 | 0 | 38930.5991 | 1 | 0 | -37 | 57 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5998 | 1 | 0 | 38930.5998 | 1 | 0 | 21.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6005 | 1 | 0 | 38930.6005 | 1 | 0 | 80.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6011 | 1 | 0 | 38930.6011 | 1 | 0 | 139.5 | 233.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6018 | 1 | 0 | 38930.6018 | 1 | 0 | 198 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6025 | 1 | 0 | 38930.6025 | 1 | 0 | 257 | 351 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6032 | 1 | 0 | 38930.6032 | 1 | 0 | 315.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6039 | 1 | 0 | 38930.6039 | 1 | 0 | 374.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6045 | 1 | 0 | 38930.6045 | 1 | 0 | 433.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6052 | 1 | 0 | 38930.6052 | 1 | 0 | 492 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6059 | 1 | 0 | 38930.6059 | 1 | 0 | 551 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6066 | 1 | 0 | 38930.6066 | 1 | 0 | 609.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6073 | 1 | 0 | 38930.6073 | 2 | 0 | 668.5 | 762.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.6079 | 1 | 0 | 38930.608 | 1 | 0 | 727 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6086 | 1 | 0 | 38930.6086 | 1 | 0 | 786 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6093 | 970 | 929 | 38930.6093 | 968 | 926 | 844.5 | 938.5 | 59.2186 | 56.7155 | 59.0965 | 56.5324 | 0.59219 | 0.56716 | 0.59096 | 0.56532 | 0.025031 | 0.025641 | 5657.6305 | 4467.0243 | 22.5332
38930.61 | 1153 | 1107 | 38930.61 | 1190 | 1164 | 903.5 | 997.5 | 70.3907 | 67.5824 | 72.6496 | 71.0623 | 0.70391 | 0.67582 | 0.7265 | 0.71062 | 0.028083 | 0.015873 | 2942.4047 | 8277.9072 | 13.1188
38930.6107 | 989 | 880 | 38930.6107 | 920 | 918 | 962.5 | 1056.5 | 60.3785 | 53.7241 | 56.1661 | 56.044 | 0.60379 | 0.53724 | 0.56166 | 0.56044 | 0.066545 | 0.001221 | 415.6078 | 545.0534 | 23.4307
38930.6113 | 1130 | 1072 | 38930.6114 | 920 | 917 | 1021 | 1115 | 68.9866 | 65.4457 | 56.1661 | 55.9829 | 0.68987 | 0.65446 | 0.56166 | 0.55983 | 0.035409 | 0.0018315 | 287.5734 | 377.6873 | 6.5628
38930.612 | 1069 | 1146 | 38930.612 | 1138 | 1086 | 1080 | 1174 | 65.2625 | 69.9634 | 69.475 | 66.3004 | 0.65263 | 0.69963 | 0.69475 | 0.663 | 0.047009 | 0.031746 | 1463.496 | 20238.0587 | 8.855
38930.6127 | 1143 | 1188 | 38930.6127 | 931 | 886 | 1138.5 | 1232.5 | 69.7802 | 72.5275 | 56.8376 | 54.0904 | 0.6978 | 0.72527 | 0.56838 | 0.5409 | 0.027473 | 0.027473 | 34936.8415 | 2813.5988 | 17.7187
38930.6134 | 1079 | 1004 | 38930.6134 | 1077 | 1004 | 1197.5 | 1291.5 | 65.873 | 61.2943 | 65.7509 | 61.2943 | 0.65873 | 0.61294 | 0.65751 | 0.61294 | 0.045788 | 0.044567 | 1434.3894 | 34475.8533 | 2.9814
38930.6141 | 949 | 920 | 38930.6141 | 1091 | 1024 | 1256.5 | 1350.5 | 57.9365 | 56.1661 | 66.6056 | 62.5153 | 0.57937 | 0.56166 | 0.66606 | 0.62515 | 0.017705 | 0.040904 | 773.6273 | 757.4346 | 23.4305
38930.6147 | 1060 | 988 | 38930.6148 | 1114 | 1059 | 1315 | 1409 | 64.7131 | 60.3175 | 68.0098 | 64.652 | 0.64713 | 0.60317 | 0.6801 | 0.64652 | 0.043956 | 0.033578 | 32.3833 | 31.0717 | 1.5601
38930.6154 | 936 | 908 | 38930.6154 | 1102 | 1041 | 1374 | 1468 | 57.1429 | 55.4335 | 67.2772 | 63.5531 | 0.57143 | 0.55433 | 0.67277 | 0.63553 | 0.017094 | 0.037241 | 903.8694 | 888.2789 | 26.6298
38930.6161 | 1112 | 1051 | 38930.6161 | 991 | 894 | 1432.5 | 1526.5 | 67.8877 | 64.1636 | 60.5006 | 54.5788 | 0.67888 | 0.64164 | 0.60501 | 0.54579 | 0.037241 | 0.059219 | 547.9097 | 863.6133 | 4.262
38930.6168 | 1191 | 1092 | 38930.6168 | 942 | 842 | 1491.5 | 1585.5 | 72.7106 | 66.6667 | 57.5092 | 51.4042 | 0.72711 | 0.66667 | 0.57509 | 0.51404 | 0.06044 | 0.06105 | 2380.6319 | 1811.8483 | 14.7518
38930.6175 | 972 | 962 | 38930.6175 | 933 | 872 | 1550.5 | 1644.5 | 59.3407 | 58.7302 | 56.9597 | 53.2357 | 0.59341 | 0.5873 | 0.5696 | 0.53236 | 0.006105 | 0.037241 | 1082.6428 | 1008.4692 | 16.9303
38930.6181 | 1149 | 1102 | 38930.6182 | 1025 | 944 | 1609 | 1703 | 70.1465 | 67.2772 | 62.5763 | 57.6313 | 0.70147 | 0.67277 | 0.62576 | 0.57631 | 0.028694 | 0.049451 | 22.5181 | 26.0269 | 2.5858
38930.6188 | 1199 | 997 | 38930.6188 | 1115 | 1177 | 1668 | 1762 | 73.199 | 60.8669 | 68.0708 | 71.8559 | 0.73199 | 0.60867 | 0.68071 | 0.71856 | 0.12332 | 0.037851 | 186.899 | 347.3325 | 6.4624

## C5-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38930.5991 | 1 | 0 | 38930.5991 | 1 | 0 | -40 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5997 | 1 | 0 | 38930.5998 | 1 | 0 | 19 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6004 | 1 | 0 | 38930.6004 | 1 | 0 | 77.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6011 | 1 | 0 | 38930.6011 | 1 | 0 | 136.5 | 230.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6018 | 1 | 0 | 38930.6018 | 1 | 0 | 195.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6025 | 1 | 0 | 38930.6025 | 1 | 0 | 254 | 348 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6031 | 1 | 0 | 38930.6032 | 1 | 0 | 313 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6038 | 1 | 0 | 38930.6038 | 1 | 0 | 371.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6045 | 1 | 0 | 38930.6045 | 1 | 0 | 430.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6052 | 1 | 0 | 38930.6052 | 1 | 0 | 489.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6059 | 1 | 0 | 38930.6059 | 1 | 0 | 548 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6065 | 1 | 0 | 38930.6066 | 1 | 0 | 606.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6072 | 1 | 0 | 38930.6072 | 1 | 0 | 665.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6079 | 1 | 0 | 38930.6079 | 1 | 0 | 724.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6086 | 1 | 0 | 38930.6086 | 1 | 0 | 783 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6093 | 1 | 0 | 38930.6093 | 1 | 0 | 842 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6099 | 5 | 27 | 38930.61 | 5 | 21 | 900.5 | 994.5 | 0.30525 | 1.6484 | 0.30525 | 1.2821 | 0.0030525 | 0.016484 | 0.0030525 | 0.012821 | 0.013431 | 0.009768 | 9670.7704 | 13356.3957 | 7650.204
38930.6106 | 1046 | 1056 | 38930.6106 | 1032 | 937 | 959.5 | 1053.5 | 63.8584 | 64.4689 | 63.0037 | 57.2039 | 0.63858 | 0.64469 | 0.63004 | 0.57204 | 0.006105 | 0.057998 | 183.2179 | 184.4936 | 0.67675
38930.6113 | 1168 | 1128 | 38930.6113 | 933 | 1024 | 1018.5 | 1112.5 | 71.3065 | 68.8645 | 56.9597 | 62.5153 | 0.71306 | 0.68864 | 0.5696 | 0.62515 | 0.02442 | 0.055556 | 72.0136 | 88.6597 | 7.6233
38930.612 | 950 | 837 | 38930.612 | 1182 | 1149 | 1077 | 1171 | 57.9976 | 51.0989 | 72.1612 | 70.1465 | 0.57998 | 0.51099 | 0.72161 | 0.70147 | 0.068987 | 0.020147 | 156.065 | 132.3916 | 22.1901
38930.6127 | 1107 | 1078 | 38930.6127 | 1053 | 913 | 1136 | 1230 | 67.5824 | 65.812 | 64.2857 | 55.7387 | 0.67582 | 0.65812 | 0.64286 | 0.55739 | 0.017705 | 0.08547 | 68.3872 | 74.7539 | 2.8563
38930.6133 | 929 | 832 | 38930.6134 | 1128 | 1171 | 1194.5 | 1288.5 | 56.7155 | 50.7937 | 68.8645 | 71.4896 | 0.56716 | 0.50794 | 0.68864 | 0.7149 | 0.059219 | 0.026252 | 321.2454 | 306.3646 | 31.8982
38930.614 | 1164 | 1190 | 38930.614 | 1131 | 1073 | 1253.5 | 1347.5 | 71.0623 | 72.6496 | 69.0476 | 65.5067 | 0.71062 | 0.7265 | 0.69048 | 0.65507 | 0.015873 | 0.035409 | 793.1326 | 1270.6257 | 18.773
38930.6147 | 1177 | 1175 | 38930.6147 | 1063 | 1033 | 1313.5 | 1407.5 | 71.8559 | 71.7338 | 64.8962 | 63.0647 | 0.71856 | 0.71734 | 0.64896 | 0.63065 | 0.001221 | 0.018315 | 696.6382 | 887.7141 | 18.2796
38930.6154 | 1189 | 1159 | 38930.6154 | 995 | 992 | 1371 | 1465 | 72.5885 | 70.757 | 60.7448 | 60.5617 | 0.72589 | 0.70757 | 0.60745 | 0.60562 | 0.018315 | 0.0018315 | 388.0279 | 556.8572 | 17.1878
38930.6161 | 1073 | 1156 | 38930.6161 | 1176 | 1137 | 1430 | 1524 | 65.5067 | 70.5739 | 71.7949 | 69.4139 | 0.65507 | 0.70574 | 0.71795 | 0.69414 | 0.050672 | 0.02381 | 1039.6647 | 6786.3577 | 9.8872
38930.6167 | 1069 | 1005 | 38930.6168 | 1160 | 1116 | 1488.5 | 1582.5 | 65.2625 | 61.3553 | 70.8181 | 68.1319 | 0.65263 | 0.61355 | 0.70818 | 0.68132 | 0.039072 | 0.026862 | 754.8199 | 1352.3736 | 3.6153
38930.6174 | 1016 | 1023 | 38930.6174 | 1145 | 1097 | 1547.5 | 1641.5 | 62.0269 | 62.4542 | 69.9023 | 66.9719 | 0.62027 | 0.62454 | 0.69902 | 0.66972 | 0.0042735 | 0.029304 | 142.4445 | 134.0517 | 4.1441
38930.6181 | 1024 | 878 | 38930.6181 | 1024 | 950 | 1606 | 1700 | 62.5153 | 53.602 | 62.5153 | 57.9976 | 0.62515 | 0.53602 | 0.62515 | 0.57998 | 0.089133 | 0.045177 | 374.2248 | 605.4884 | 20.6274
38930.6188 | 1184 | 1151 | 38930.6188 | 927 | 925 | 1665 | 1759 | 72.2833 | 70.2686 | 56.5934 | 56.4713 | 0.72283 | 0.70269 | 0.56593 | 0.56471 | 0.020147 | 0.001221 | 100.8813 | 129.6311 | 10.8872

## C5-6
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38930.599 | 1 | 0 | 38930.599 | 1 | 0 | -42.5 | 51.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5997 | 1 | 1 | 38930.5997 | 1 | 0 | 16 | 110 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.6004 | 1 | 0 | 38930.6004 | 1 | 0 | 75 | 169 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6011 | 1 | 0 | 38930.6011 | 1 | 0 | 133.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6017 | 1 | 0 | 38930.6018 | 1 | 0 | 192.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6024 | 1 | 0 | 38930.6024 | 1 | 0 | 251.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6031 | 1 | 0 | 38930.6031 | 1 | 0 | 310 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6038 | 1 | 0 | 38930.6038 | 1 | 0 | 369 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6045 | 1 | 0 | 38930.6045 | 1 | 0 | 427.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6052 | 1 | 0 | 38930.6052 | 1 | 0 | 486.5 | 580.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6058 | 1 | 0 | 38930.6058 | 1 | 0 | 545.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6065 | 1 | 0 | 38930.6065 | 1 | 0 | 604 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6072 | 1 | 0 | 38930.6072 | 1 | 0 | 663 | 757 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6079 | 1 | 0 | 38930.6079 | 1 | 0 | 721.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6086 | 1 | 0 | 38930.6086 | 1 | 0 | 780.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6092 | 1 | 0 | 38930.6092 | 1 | 0 | 839.5 | 933.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6099 | 7 | 39 | 38930.6099 | 5 | 32 | 898 | 992 | 0.42735 | 2.381 | 0.30525 | 1.9536 | 0.0042735 | 0.02381 | 0.0030525 | 0.019536 | 0.019536 | 0.016484 | 6683.7967 | 7948.4247 | 5234.1992
38930.6106 | 1158 | 1111 | 38930.6106 | 1144 | 1090 | 956.5 | 1050.5 | 70.696 | 67.8266 | 69.8413 | 66.5446 | 0.70696 | 0.67827 | 0.69841 | 0.66545 | 0.028694 | 0.032967 | 1976.1615 | 83721.2735 | 14.0229
38930.6113 | 1011 | 914 | 38930.6113 | 1072 | 994 | 1015.5 | 1109.5 | 61.7216 | 55.7998 | 65.4457 | 60.6838 | 0.61722 | 0.558 | 0.65446 | 0.60684 | 0.059219 | 0.047619 | 804.0871 | 2282.0155 | 19.7075
38930.612 | 1063 | 1085 |  | 1117 | 1067 | 1074 | 1168 | 64.8962 | 66.2393 | 68.1929 | 65.1404 | 0.64896 | 0.66239 | 0.68193 | 0.6514 | 0.013431 | 0.030525 | 345.8952 | 385.345 | 2.5597
38930.6126 | 1057 | 1105 | 38930.6127 | 1162 | 1140 | 1133 | 1227 | 64.5299 | 67.4603 | 70.9402 | 69.5971 | 0.6453 | 0.6746 | 0.7094 | 0.69597 | 0.029304 | 0.013431 | 1196.8899 | 2746.6834 | 4.2769
38930.6133 | 1062 | 984 | 38930.6133 | 1183 | 1152 | 1192 | 1286 | 64.8352 | 60.0733 | 72.2222 | 70.3297 | 0.64835 | 0.60073 | 0.72222 | 0.7033 | 0.047619 | 0.018926 | 371.3307 | 479.9029 | 5.6365
38930.614 | 1086 | 1016 | 38930.614 | 1129 | 1174 | 1250.5 | 1344.5 | 66.3004 | 62.0269 | 68.9255 | 71.6728 | 0.663 | 0.62027 | 0.68926 | 0.71673 | 0.042735 | 0.027473 | 786.5491 | 1677.3176 | 1.0236
38930.6147 | 1023 | 1041 | 38930.6147 | 1094 | 1083 | 1310.5 | 1404.5 | 62.4542 | 63.5531 | 66.7888 | 66.1172 | 0.62454 | 0.63553 | 0.66789 | 0.66117 | 0.010989 | 0.0067155 | 241.6188 | 240.3423 | 3.3253
38930.6154 | 960 | 1065 | 38930.6154 | 1059 | 992 | 1368.5 | 1462.5 | 58.6081 | 65.0183 | 64.652 | 60.5617 | 0.58608 | 0.65018 | 0.64652 | 0.60562 | 0.064103 | 0.040904 | 403.962 | 590.2637 | 7.0675
38930.616 | 1098 | 1035 | 38930.6161 | 1051 | 971 | 1427 | 1521 | 67.033 | 63.1868 | 64.1636 | 59.2796 | 0.67033 | 0.63187 | 0.64164 | 0.5928 | 0.038462 | 0.04884 | 459.2445 | 654.9824 | 1.6747
38930.6167 | 944 | 852 | 38930.6167 | 1054 | 982 | 1486 | 1580 | 57.6313 | 52.0147 | 64.3468 | 59.9512 | 0.57631 | 0.52015 | 0.64347 | 0.59951 | 0.056166 | 0.043956 | 1112.2134 | 6500.0836 | 36.6452
38930.6174 | 1106 | 1047 | 38930.6174 | 1195 | 1190 | 1544.5 | 1638.5 | 67.5214 | 63.9194 | 72.9548 | 72.6496 | 0.67521 | 0.63919 | 0.72955 | 0.7265 | 0.03602 | 0.0030525 | 657.015 | 1110.6162 | 3.5031
38930.6181 | 1168 | 1132 | 38930.6181 | 1194 | 899 | 1603.5 | 1697.5 | 71.3065 | 69.1087 | 72.8938 | 54.884 | 0.71306 | 0.69109 | 0.72894 | 0.54884 | 0.021978 | 0.1801 | 49.5839 | 60.5379 | 6.2287
38930.6188 | 1151 | 1101 | 38930.6188 | 1135 | 1082 | 1662.5 | 1756.5 | 70.2686 | 67.2161 | 69.2918 | 66.0562 | 0.70269 | 0.67216 | 0.69292 | 0.66056 | 0.030525 | 0.032357 | 2649.2509 | 8044.0741 | 12.4681

## C4-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38930.599 | 1 | 0 | 38930.599 | 1 | 0 | -45.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5997 | 1 | 0 | 38930.5997 | 1 | 0 | 13.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6003 | 1 | 0 | 38930.6004 | 1 | 0 | 72 | 166 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.601 | 1 | 0 | 38930.6011 | 1 | 0 | 131 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6017 | 1 | 0 | 38930.6017 | 1 | 0 | 189.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6024 | 1 | 0 | 38930.6024 | 1 | 0 | 248.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6031 | 1 | 0 | 38930.6031 | 1 | 0 | 307.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6038 | 1 | 0 | 38930.6038 | 1 | 0 | 366 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6044 | 1 | 0 | 38930.6045 | 1 | 0 | 425 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6051 | 1 | 0 | 38930.6051 | 1 | 0 | 483.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6058 | 1 | 0 | 38930.6058 | 1 | 0 | 542.5 | 636.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6065 | 1 | 0 | 38930.6065 | 1 | 0 | 601.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6072 | 1 | 0 | 38930.6072 | 1 | 0 | 660 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6078 | 1 | 0 | 38930.6078 | 1 | 0 | 718.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6085 | 1 | 0 | 38930.6085 | 1 | 0 | 777.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6092 | 1 | 0 | 38930.6092 | 1 | 0 | 836.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6099 | 1162 | 1177 | 38930.6099 | 944 | 831 | 895 | 989 | 70.9402 | 71.8559 | 57.6313 | 50.7326 | 0.7094 | 0.71856 | 0.57631 | 0.50733 | 0.0091575 | 0.068987 | 115.7698 | 145.9438 | 11.3931
38930.6106 | 1145 | 816 | 38930.6106 | 1139 | 1178 | 954 | 1048 | 69.9023 | 49.8168 | 69.536 | 71.917 | 0.69902 | 0.49817 | 0.69536 | 0.71917 | 0.20085 | 0.02381 | 6.3671 | 5.4859 | 0.96886
38930.6112 | 1170 | 1183 | 38930.6113 | 988 | 1088 | 1012.5 | 1106.5 | 71.4286 | 72.2222 | 60.3175 | 66.4225 | 0.71429 | 0.72222 | 0.60317 | 0.66422 | 0.0079365 | 0.06105 | 218.1704 | 282.1772 | 14.9778
38930.6119 | 1145 | 1098 | 38930.6119 | 1178 | 1183 | 1071.5 | 1165.5 | 69.9023 | 67.033 | 71.917 | 72.2222 | 0.69902 | 0.67033 | 0.71917 | 0.72222 | 0.028694 | 0.0030525 | 1024.0705 | 2310.2806 | 11.3467
38930.6126 | 1174 | 1154 | 38930.6126 | 924 | 1021 | 1130.5 | 1224.5 | 71.6728 | 70.4518 | 56.4103 | 62.3321 | 0.71673 | 0.70452 | 0.5641 | 0.62332 | 0.01221 | 0.059219 | 70.0115 | 87.3424 | 8.6852
38930.6133 | 1081 | 1010 | 38930.6133 | 1008 | 1008 | 1189 | 1283 | 65.9951 | 61.6606 | 61.5385 | 61.5385 | 0.65995 | 0.61661 | 0.61538 | 0.61538 | 0.043346 | 0 | 155.9117 | 170.9182 | 1.3755
38930.614 | 1181 | 1188 | 38930.614 | 1192 | 1189 | 1248 | 1342 | 72.1001 | 72.5275 | 72.7717 | 72.5885 | 0.721 | 0.72527 | 0.72772 | 0.72589 | 0.0042735 | 0.0018315 | 19219.4253 | 55239.4876 | 21.5082
38930.6147 | 1115 | 1080 | 38930.6147 | 1154 | 1122 | 1308 | 1402 | 68.0708 | 65.9341 | 70.4518 | 68.4982 | 0.68071 | 0.65934 | 0.70452 | 0.68498 | 0.021368 | 0.019536 | 25609.8622 | 3472.3355 | 7.3783
38930.6153 | 1048 | 971 | 38930.6153 | 1115 | 1055 | 1365.5 | 1459.5 | 63.9805 | 59.2796 | 68.0708 | 64.4078 | 0.6398 | 0.5928 | 0.68071 | 0.64408 | 0.047009 | 0.03663 | 207.1617 | 222.1455 | 6.6771
38930.616 | 1099 | 1034 | 38930.616 | 948 | 842 | 1424.5 | 1518.5 | 67.094 | 63.1258 | 57.8755 | 51.4042 | 0.67094 | 0.63126 | 0.57875 | 0.51404 | 0.039683 | 0.064713 | 917.198 | 2269.7198 | 1.8508
38930.6167 | 1090 | 1129 | 38930.6167 | 1189 | 1192 | 1483 | 1577 | 66.5446 | 68.9255 | 72.5885 | 72.7717 | 0.66545 | 0.68926 | 0.72589 | 0.72772 | 0.02381 | 0.0018315 | 1226.5843 | 2542.5653 | 9.0318
38930.6174 | 1134 | 1181 | 38930.6174 | 1199 | 1180 | 1542 | 1636 | 69.2308 | 72.1001 | 73.199 | 72.0391 | 0.69231 | 0.721 | 0.73199 | 0.72039 | 0.028694 | 0.0116 | 2430.4951 | 17576.1876 | 17.0057
38930.618 | 1154 | 1192 | 38930.6181 | 1197 | 920 | 1600.5 | 1694.5 | 70.4518 | 72.7717 | 73.0769 | 56.1661 | 0.70452 | 0.72772 | 0.73077 | 0.56166 | 0.023199 | 0.16911 | 73.8581 | 94.5684 | 9.4998
38930.6187 | 1195 | 892 | 38930.6187 | 1175 | 1136 | 1659.5 | 1753.5 | 72.9548 | 54.4567 | 71.7338 | 69.3529 | 0.72955 | 0.54457 | 0.71734 | 0.69353 | 0.18498 | 0.02381 | 61.015 | 74.2355 | 1.2428

## C4-6
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38930.599 | 1 | 0 | 38930.599 | 1 | 0 | -48.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5996 | 1 | 0 | 38930.5997 | 1 | 0 | 10.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6003 | 1 | 0 | 38930.6003 | 1 | 0 | 69.5 | 163.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.601 | 1 | 0 | 38930.601 | 1 | 0 | 128 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6017 | 1 | 0 | 38930.6017 | 1 | 0 | 187 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6024 | 1 | 0 | 38930.6024 | 1 | 0 | 245.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.603 | 1 | 0 | 38930.6031 | 1 | 0 | 304.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6037 | 1 | 0 | 38930.6037 | 1 | 0 | 363.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6044 | 1 | 0 | 38930.6044 | 1 | 0 | 422 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6051 | 1 | 0 | 38930.6051 | 1 | 0 | 481 | 575 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6058 | 1 | 0 | 38930.6058 | 1 | 0 | 539.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6064 | 1 | 0 | 38930.6065 | 1 | 0 | 598.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6071 | 1 | 0 | 38930.6071 | 1 | 0 | 657 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6078 | 1 | 0 | 38930.6078 | 1 | 0 | 716 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6085 | 1 | 0 | 38930.6085 | 1 | 0 | 774.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6092 | 1 | 0 | 38930.6092 | 1 | 0 | 833.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6098 | 996 | 888 | 38930.6099 | 1149 | 817 | 892.5 | 986.5 | 60.8059 | 54.2125 | 70.1465 | 49.8779 | 0.60806 | 0.54212 | 0.70147 | 0.49878 | 0.065934 | 0.20269 | 184.2319 | 178.2016 | 16.5201
38930.6105 | 1098 | 1028 | 38930.6105 | 1022 | 923 | 951 | 1045 | 67.033 | 62.7595 | 62.3932 | 56.3492 | 0.67033 | 0.62759 | 0.62393 | 0.56349 | 0.042735 | 0.06044 | 624.2495 | 1110.1698 | 1.1583
38930.6112 | 1038 | 947 | 38930.6112 | 1042 | 1050 | 1010 | 1104 | 63.37 | 57.8144 | 63.6142 | 64.1026 | 0.6337 | 0.57814 | 0.63614 | 0.64103 | 0.055556 | 0.004884 | 174.684 | 180.5845 | 8.7005
38930.6119 | 1139 | 1086 | 38930.6119 | 1014 | 1015 | 1068.5 | 1162.5 | 69.536 | 66.3004 | 61.9048 | 61.9658 | 0.69536 | 0.663 | 0.61905 | 0.61966 | 0.032357 | 0.0006105 | 55.6707 | 64.01 | 4.0243
38930.6126 | 1041 | 955 | 38930.6126 | 1189 | 1003 | 1127.5 | 1221.5 | 63.5531 | 58.3028 | 72.5885 | 61.2332 | 0.63553 | 0.58303 | 0.72589 | 0.61233 | 0.052503 | 0.11355 | 33.3145 | 30.4929 | 2.8633
38930.6133 | 1022 | 1026 | 38930.6133 | 1025 | 937 | 1186.5 | 1280.5 | 62.3932 | 62.6374 | 62.5763 | 57.2039 | 0.62393 | 0.62637 | 0.62576 | 0.57204 | 0.002442 | 0.053724 | 262.6254 | 249.3752 | 4.5234
38930.6139 | 1137 | 1083 | 38930.6139 | 1161 | 1118 | 1245 | 1339 | 69.4139 | 66.1172 | 70.8791 | 68.254 | 0.69414 | 0.66117 | 0.70879 | 0.68254 | 0.032967 | 0.026252 | 5818.1567 | 2909.3676 | 9.5499
38930.6146 | 1088 | 1021 | 38930.6146 | 1069 | 1003 | 1305 | 1399 | 66.4225 | 62.3321 | 65.2625 | 61.2332 | 0.66422 | 0.62332 | 0.65263 | 0.61233 | 0.040904 | 0.040293 | 1797.5914 | 10232.3637 | 0.38992
38930.6153 | 1038 | 959 | 38930.6153 | 977 | 887 | 1362.5 | 1456.5 | 63.37 | 58.547 | 59.6459 | 54.1514 | 0.6337 | 0.58547 | 0.59646 | 0.54151 | 0.04823 | 0.054945 | 10787.4426 | 1389.16 | 11.2856
38930.616 | 1016 | 1013 | 38930.616 | 1027 | 939 | 1421.5 | 1515.5 | 62.0269 | 61.8437 | 62.6984 | 57.326 | 0.62027 | 0.61844 | 0.62698 | 0.57326 | 0.0018315 | 0.053724 | 279.6484 | 260.2204 | 5.9916
38930.6167 | 982 | 886 | 38930.6167 | 1078 | 1158 | 1480.5 | 1574.5 | 59.9512 | 54.0904 | 65.812 | 70.696 | 0.59951 | 0.5409 | 0.65812 | 0.70696 | 0.058608 | 0.04884 | 507.8321 | 699.2049 | 24.1944
38930.6173 | 966 | 874 | 38930.6173 | 1190 | 1191 | 1539 | 1633 | 58.9744 | 53.3578 | 72.6496 | 72.7106 | 0.58974 | 0.53358 | 0.7265 | 0.72711 | 0.056166 | 0.0006105 | 21.1656 | 16.4062 | 4.4027
38930.618 | 1020 | 937 | 38930.618 | 1122 | 1069 | 1598 | 1692 | 62.2711 | 57.2039 | 68.4982 | 65.2625 | 0.62271 | 0.57204 | 0.68498 | 0.65263 | 0.050672 | 0.032357 | 250.2072 | 264.8045 | 12.0866
38930.6187 | 1172 | 1185 | 38930.6187 | 1175 | 1136 | 1656.5 | 1750.5 | 71.5507 | 72.3443 | 71.7338 | 69.3529 | 0.71551 | 0.72344 | 0.71734 | 0.69353 | 0.0079365 | 0.02381 | 1362.2996 | 2113.2093 | 19.6588

## C4-5
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38930.5989 | 1 | 0 | 38930.5989 | 1 | 0 | -51 | 43 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5996 | 1 | 0 | 38930.5996 | 1 | 0 | 7.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6003 | 1 | 0 | 38930.6003 | 1 | 0 | 66.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.601 | 1 | 0 | 38930.601 | 1 | 0 | 125.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6016 | 1 | 0 | 38930.6017 | 1 | 0 | 184 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6023 | 1 | 0 | 38930.6023 | 1 | 0 | 243 | 337 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.603 | 1 | 0 | 38930.603 | 1 | 0 | 301.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6037 | 1 | 0 | 38930.6037 | 1 | 0 | 360.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6044 | 1 | 0 | 38930.6044 | 1 | 0 | 419 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.605 | 1 | 0 | 38930.6051 | 1 | 0 | 478 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6057 | 1 | 0 | 38930.6057 | 1 | 0 | 536.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6064 | 1 | 0 | 38930.6064 | 1 | 0 | 595.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6071 | 1 | 0 | 38930.6071 | 1 | 0 | 654.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6078 | 1 | 1 | 38930.6078 | 1 | 0 | 713.5 | 807.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38930.6084 | 1 | 0 | 38930.6085 | 1 | 0 | 772 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6091 | 1 | 0 | 38930.6092 | 1 | 0 | 831 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6098 | 6 | 24 | 38930.6098 | 6 | 19 | 889.5 | 983.5 | 0.3663 | 1.4652 | 0.3663 | 1.16 | 0.003663 | 0.014652 | 0.003663 | 0.0116 | 0.010989 | 0.0079365 | 11801.5494 | 16411.0859 | 8626.6838
38930.6105 | 1161 | 1115 | 38930.6105 | 1028 | 931 | 948.5 | 1042.5 | 70.8791 | 68.0708 | 62.7595 | 56.8376 | 0.70879 | 0.68071 | 0.62759 | 0.56838 | 0.028083 | 0.059219 | 8.7636 | 10.3075 | 1.3659
38930.6112 | 1016 | 1011 | 38930.6112 | 980 | 871 | 1007 | 1101 | 62.0269 | 61.7216 | 59.8291 | 53.1746 | 0.62027 | 0.61722 | 0.59829 | 0.53175 | 0.0030525 | 0.066545 | 346.6479 | 324.5949 | 6.5045
38930.6119 | 1091 | 1021 | 38930.6119 | 1120 | 1163 | 1066 | 1160 | 66.6056 | 62.3321 | 68.3761 | 71.0012 | 0.66606 | 0.62332 | 0.68376 | 0.71001 | 0.042735 | 0.026252 | 673.7504 | 1249.8288 | 0.092501
38930.6125 | 919 | 983 | 38930.6125 | 932 | 826 | 1124.5 | 1218.5 | 56.105 | 60.0122 | 56.8987 | 50.4274 | 0.56105 | 0.60012 | 0.56899 | 0.50427 | 0.039072 | 0.064713 | 2090.6908 | 14269.6781 | 21.3175
38930.6132 | 936 | 831 | 38930.6132 | 949 | 916 | 1183.5 | 1277.5 | 57.1429 | 50.7326 | 57.9365 | 55.9219 | 0.57143 | 0.50733 | 0.57937 | 0.55922 | 0.064103 | 0.020147 | 642.2833 | 1061.9052 | 38.0553
38930.6139 | 1129 | 1072 | 38930.6139 | 1069 | 994 | 1242.5 | 1336.5 | 68.9255 | 65.4457 | 65.2625 | 60.6838 | 0.68926 | 0.65446 | 0.65263 | 0.60684 | 0.034799 | 0.045788 | 183.0056 | 223.0084 | 5.6663
38930.6146 | 1127 | 1071 | 38930.6146 | 1114 | 1093 | 1302.5 | 1396.5 | 68.8034 | 65.3846 | 68.0098 | 66.7277 | 0.68803 | 0.65385 | 0.6801 | 0.66728 | 0.034188 | 0.012821 | 554.6381 | 879.4751 | 7.1245
38930.6153 | 1124 | 1070 | 38930.6153 | 1158 | 1191 | 1360 | 1454 | 68.6203 | 65.3236 | 70.696 | 72.7106 | 0.6862 | 0.65324 | 0.70696 | 0.72711 | 0.032967 | 0.020147 | 2028.3777 | 20416.5888 | 7.5313
38930.6159 | 1034 | 949 | 38930.6159 | 985 | 888 | 1418.5 | 1512.5 | 63.1258 | 57.9365 | 60.1343 | 54.2125 | 0.63126 | 0.57937 | 0.60134 | 0.54212 | 0.051893 | 0.059219 | 9779.929 | 1283.0047 | 12.7101
38930.6166 | 1036 | 958 | 38930.6166 | 1098 | 1139 | 1477.5 | 1571.5 | 63.2479 | 58.486 | 67.033 | 69.536 | 0.63248 | 0.58486 | 0.67033 | 0.69536 | 0.047619 | 0.025031 | 5.1007 | 4.5538 | 0.54112
38930.6173 | 924 | 940 | 38930.6173 | 1045 | 1066 | 1536.5 | 1630.5 | 56.4103 | 57.3871 | 63.7973 | 65.0794 | 0.5641 | 0.57387 | 0.63797 | 0.65079 | 0.009768 | 0.012821 | 10101.4127 | 22226.5774 | 26.3728
38930.618 | 1194 | 1188 | 38930.618 | 1184 | 1151 | 1595 | 1689 | 72.8938 | 72.5275 | 72.2833 | 70.2686 | 0.72894 | 0.72527 | 0.72283 | 0.70269 | 0.003663 | 0.020147 | 1527.2134 | 2192.8422 | 21.6539
38930.6187 | 1167 | 1129 | 38930.6187 | 1111 | 1054 | 1654 | 1748 | 71.2454 | 68.9255 | 67.8266 | 64.3468 | 0.71245 | 0.68926 | 0.67827 | 0.64347 | 0.023199 | 0.034799 | 921.1175 | 1744.8821 | 15.3288

## C3-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38930.5989 | 1 | 0 | 38930.5989 | 1 | 0 | -54 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5996 | 1 | 0 | 38930.5996 | 1 | 0 | 5 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6003 | 1 | 0 | 38930.6003 | 1 | 0 | 63.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6009 | 1 | 0 | 38930.6009 | 1 | 0 | 122.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6016 | 1 | 0 | 38930.6016 | 1 | 0 | 181.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6023 | 1 | 0 | 38930.6023 | 1 | 0 | 240 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.603 | 1 | 0 | 38930.603 | 1 | 0 | 299 | 393 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6037 | 1 | 0 | 38930.6037 | 1 | 0 | 357.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6043 | 1 | 0 | 38930.6044 | 1 | 0 | 416.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.605 | 1 | 0 | 38930.605 | 1 | 0 | 475.5 | 569.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6057 | 1 | 0 | 38930.6057 | 1 | 0 | 534 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6064 | 1 | 0 | 38930.6064 | 1 | 0 | 592.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6071 | 1 | 0 | 38930.6071 | 1 | 0 | 651.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6077 | 1 | 0 | 38930.6078 | 1 | 0 | 710.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6084 | 1 | 0 | 38930.6084 | 1 | 0 | 769 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6091 | 1 | 0 | 38930.6091 | 1 | 0 | 828 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6098 | 1020 | 1020 | 38930.6098 | 1182 | 1146 | 886.5 | 980.5 | 62.2711 | 62.2711 | 72.1612 | 69.9634 | 0.62271 | 0.62271 | 0.72161 | 0.69963 | 0 | 0.021978 | 412.0276 | 384.5018 | 5.6813
38930.6105 | 1149 | 1099 | 38930.6105 | 1191 | 1027 | 945.5 | 1039.5 | 70.1465 | 67.094 | 72.7106 | 62.6984 | 0.70147 | 0.67094 | 0.72711 | 0.62698 | 0.030525 | 0.10012 | 178.7955 | 224.6641 | 8.4991
38930.6111 | 938 | 821 | 38930.6112 | 996 | 891 | 1004.5 | 1098.5 | 57.265 | 50.1221 | 60.8059 | 54.3956 | 0.57265 | 0.50122 | 0.60806 | 0.54396 | 0.071429 | 0.064103 | 1306.041 | 3037.15 | 41.7461
38930.6118 | 1090 | 1019 | 38930.6118 | 1188 | 1163 | 1063 | 1157 | 66.5446 | 62.21 | 72.5275 | 71.0012 | 0.66545 | 0.6221 | 0.72527 | 0.71001 | 0.043346 | 0.015263 | 593.9667 | 1006.5664 | 0.35885
38930.6125 | 918 | 964 | 38930.6125 | 1190 | 1175 | 1122 | 1216 | 56.044 | 58.8523 | 72.6496 | 71.7338 | 0.56044 | 0.58852 | 0.7265 | 0.71734 | 0.028083 | 0.0091575 | 105.9778 | 89.1261 | 11.2934
38930.6132 | 1166 | 1129 | 38930.6132 | 959 | 936 | 1180.5 | 1274.5 | 71.1844 | 68.9255 | 58.547 | 57.1429 | 0.71184 | 0.68926 | 0.58547 | 0.57143 | 0.022589 | 0.014042 | 215.9729 | 281.2023 | 11.8903
38930.6139 | 979 | 876 | 38930.6139 | 927 | 887 | 1239.5 | 1333.5 | 59.768 | 53.4799 | 56.5934 | 54.1514 | 0.59768 | 0.5348 | 0.56593 | 0.54151 | 0.062882 | 0.02442 | 651.9261 | 1234.6868 | 27.2475
38930.6146 | 964 | 902 | 38930.6146 | 1063 | 1035 | 1299.5 | 1393.5 | 58.8523 | 55.0672 | 64.8962 | 63.1868 | 0.58852 | 0.55067 | 0.64896 | 0.63187 | 0.037851 | 0.017094 | 684.9601 | 852.9557 | 24.512
38930.6152 | 948 | 927 | 38930.6152 | 1198 | 1183 | 1357 | 1451 | 57.8755 | 56.5934 | 73.138 | 72.2222 | 0.57875 | 0.56593 | 0.73138 | 0.72222 | 0.012821 | 0.0091575 | 576.6851 | 512.0977 | 21.4816
38930.6159 | 965 | 876 | 38930.6159 | 1016 | 928 | 1416 | 1510 | 58.9133 | 53.4799 | 62.0269 | 56.6545 | 0.58913 | 0.5348 | 0.62027 | 0.56654 | 0.054335 | 0.053724 | 2172.958 | 2422.0392 | 29.8213
38930.6166 | 1002 | 1103 | 38930.6166 | 964 | 949 | 1474.5 | 1568.5 | 61.1722 | 67.3382 | 58.8523 | 57.9365 | 0.61172 | 0.67338 | 0.58852 | 0.57937 | 0.061661 | 0.0091575 | 230.9782 | 290.2582 | 0.54079
38930.6173 | 989 | 987 | 38930.6173 | 1024 | 944 | 1533.5 | 1627.5 | 60.3785 | 60.2564 | 62.5153 | 57.6313 | 0.60379 | 0.60256 | 0.62515 | 0.57631 | 0.001221 | 0.04884 | 380.7564 | 336.6222 | 10.703
38930.618 | 1175 | 1171 | 38930.618 | 945 | 847 | 1592.5 | 1686.5 | 71.7338 | 71.4896 | 57.6923 | 51.7094 | 0.71734 | 0.7149 | 0.57692 | 0.51709 | 0.002442 | 0.059829 | 94.2801 | 118.172 | 10.7765
38930.6186 | 1093 | 1032 | 38930.6186 | 1099 | 1039 | 1651 | 1745 | 66.7277 | 63.0037 | 67.094 | 63.431 | 0.66728 | 0.63004 | 0.67094 | 0.63431 | 0.037241 | 0.03663 | 58547.8845 | 1741.5428 | 1.0978

## C3-6
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38930.5989 | 1 | 0 | 38930.5989 | 1 | 0 | -56.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5995 | 1 | 0 | 38930.5996 | 1 | 0 | 2 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6002 | 1 | 0 | 38930.6002 | 1 | 0 | 61 | 155 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6009 | 1 | 0 | 38930.6009 | 1 | 0 | 119.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6016 | 1 | 0 | 38930.6016 | 1 | 0 | 178.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6023 | 1 | 0 | 38930.6023 | 1 | 0 | 237.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6029 | 1 | 0 | 38930.603 | 1 | 0 | 296 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6036 | 1 | 0 | 38930.6036 | 1 | 0 | 354.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6043 | 1 | 0 | 38930.6043 | 1 | 0 | 413.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.605 | 1 | 0 | 38930.605 | 1 | 0 | 472.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6057 | 1 | 0 | 38930.6057 | 1 | 0 | 531.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6063 | 1 | 0 | 38930.6064 | 1 | 0 | 590 | 684 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.607 | 1 | 0 | 38930.607 | 1 | 0 | 648.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6077 | 1 | 0 | 38930.6077 | 1 | 0 | 707.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6084 | 1 | 0 | 38930.6084 | 1 | 0 | 766.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6091 | 1 | 0 | 38930.6091 | 1 | 0 | 825 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6097 | 958 | 911 | 38930.6098 | 1049 | 1066 | 884 | 978 | 58.486 | 55.6166 | 64.0415 | 65.0794 | 0.58486 | 0.55617 | 0.64042 | 0.65079 | 0.028694 | 0.010379 | 746.8827 | 846.2968 | 23.9553
38930.6104 | 1168 | 1124 | 38930.6104 | 1033 | 939 | 942.5 | 1036.5 | 71.3065 | 68.6203 | 63.0647 | 57.326 | 0.71306 | 0.6862 | 0.63065 | 0.57326 | 0.026862 | 0.057387 | 59.8528 | 73.2292 | 6.7313
38930.6111 | 962 | 857 | 38930.6111 | 1179 | 1183 | 1001.5 | 1095.5 | 58.7302 | 52.3199 | 71.978 | 72.2222 | 0.5873 | 0.5232 | 0.71978 | 0.72222 | 0.064103 | 0.002442 | 64.7105 | 51.2033 | 11.618
38930.6118 | 1090 | 1021 | 38930.6118 | 1007 | 910 | 1060.5 | 1154.5 | 66.5446 | 62.3321 | 61.4774 | 55.5556 | 0.66545 | 0.62332 | 0.61477 | 0.55556 | 0.042125 | 0.059219 | 890.6521 | 2226.2482 | 0.18934
38930.6125 | 1050 | 968 | 38930.6125 | 1182 | 1147 | 1119 | 1213 | 64.1026 | 59.0965 | 72.1612 | 70.0244 | 0.64103 | 0.59096 | 0.72161 | 0.70024 | 0.050061 | 0.021368 | 284.015 | 331.1859 | 7.5396
38930.6131 | 924 | 911 | 38930.6132 | 1001 | 915 | 1178 | 1272 | 56.4103 | 55.6166 | 61.1111 | 55.8608 | 0.5641 | 0.55617 | 0.61111 | 0.55861 | 0.0079365 | 0.052503 | 764.8318 | 639.4704 | 26.3911
38930.6138 | 1018 | 929 | 38930.6138 | 923 | 878 | 1236.5 | 1330.5 | 62.149 | 56.7155 | 56.3492 | 53.602 | 0.62149 | 0.56716 | 0.56349 | 0.53602 | 0.054335 | 0.027473 | 760.3466 | 1688.6025 | 16.8717
38930.6145 | 1007 | 901 | 38930.6145 | 901 | 1032 | 1296.5 | 1390.5 | 61.4774 | 55.0061 | 55.0061 | 63.0037 | 0.61477 | 0.55006 | 0.55006 | 0.63004 | 0.064713 | 0.079976 | 3932.6021 | 1156.9731 | 20.9444
38930.6152 | 996 | 873 | 38930.6152 | 1133 | 1185 | 1354.5 | 1448.5 | 60.8059 | 53.2967 | 69.1697 | 72.3443 | 0.60806 | 0.53297 | 0.6917 | 0.72344 | 0.075092 | 0.031746 | 80.1062 | 68.6631 | 11.3793
38930.6159 | 938 | 851 | 38930.6159 | 1189 | 1158 | 1413 | 1507 | 57.265 | 51.9536 | 72.5885 | 70.696 | 0.57265 | 0.51954 | 0.72589 | 0.70696 | 0.053114 | 0.018926 | 185.681 | 155.9132 | 23.197
38930.6166 | 997 | 907 | 38930.6166 | 1171 | 1192 | 1472 | 1566 | 60.8669 | 55.3724 | 71.4896 | 72.7717 | 0.60867 | 0.55372 | 0.7149 | 0.72772 | 0.054945 | 0.012821 | 45.3806 | 38.2822 | 6.3799
38930.6172 | 933 | 869 | 38930.6172 | 1086 | 1025 | 1530.5 | 1624.5 | 56.9597 | 53.0525 | 66.3004 | 62.5763 | 0.5696 | 0.53053 | 0.663 | 0.62576 | 0.039072 | 0.037241 | 2524.9377 | 5033.1933 | 35.0933
38930.6179 | 961 | 951 | 38930.6179 | 1076 | 1017 | 1589.5 | 1683.5 | 58.6691 | 58.0586 | 65.6899 | 62.0879 | 0.58669 | 0.58059 | 0.6569 | 0.62088 | 0.006105 | 0.03602 | 497.3912 | 429.1275 | 17.1429
38930.6186 | 1001 | 914 | 38930.6186 | 937 | 1032 | 1648.5 | 1742.5 | 61.1111 | 55.7998 | 57.2039 | 63.0037 | 0.61111 | 0.558 | 0.57204 | 0.63004 | 0.053114 | 0.057998 | 2354.1454 | 2298.6004 | 20.762

## C3-5
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38930.5988 | 1 | 0 | 38930.5988 | 1 | 0 | -59.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5995 | 1 | 0 | 38930.5995 | 1 | 0 | -0.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6002 | 1 | 0 | 38930.6002 | 1 | 0 | 58 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6009 | 1 | 0 | 38930.6009 | 1 | 0 | 117 | 211 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6016 | 1 | 0 | 38930.6016 | 1 | 0 | 175.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6022 | 1 | 0 | 38930.6022 | 1 | 0 | 234.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6029 | 1 | 0 | 38930.6029 | 1 | 0 | 293.5 | 387.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6036 | 1 | 0 | 38930.6036 | 1 | 0 | 352 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6043 | 1 | 0 | 38930.6043 | 1 | 0 | 410.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.605 | 1 | 0 | 38930.605 | 1 | 0 | 469.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6056 | 1 | 0 | 38930.6056 | 1 | 0 | 528.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6063 | 1 | 0 | 38930.6063 | 1 | 0 | 587 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.607 | 1 | 0 | 38930.607 | 1 | 0 | 646 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6077 | 1 | 0 | 38930.6077 | 1 | 0 | 705 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6084 | 1 | 0 | 38930.6084 | 1 | 0 | 763.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.609 | 1 | 0 | 38930.6091 | 1 | 0 | 822.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6097 | 7 | 40 | 38930.6097 | 6 | 36 | 881 | 975 | 0.42735 | 2.442 | 0.3663 | 2.1978 | 0.0042735 | 0.02442 | 0.003663 | 0.021978 | 0.020147 | 0.018315 | 6491.8462 | 7155.6706 | 5093.8636
38930.6104 | 1175 | 1137 | 38930.6104 | 1113 | 1168 | 940 | 1034 | 71.7338 | 69.4139 | 67.9487 | 71.3065 | 0.71734 | 0.69414 | 0.67949 | 0.71306 | 0.023199 | 0.033578 | 1589.5224 | 5411.0147 | 17.1829
38930.6111 | 967 | 853 | 38930.6111 | 1061 | 979 | 998.5 | 1092.5 | 59.0354 | 52.0757 | 64.7741 | 59.768 | 0.59035 | 0.52076 | 0.64774 | 0.59768 | 0.069597 | 0.050061 | 741.331 | 2101.5279 | 32.7913
38930.6118 | 963 | 856 | 38930.6118 | 1135 | 1178 | 1057.5 | 1151.5 | 58.7912 | 52.2589 | 69.2918 | 71.917 | 0.58791 | 0.52259 | 0.69292 | 0.71917 | 0.065324 | 0.026252 | 171.5423 | 151.9347 | 20.7144
38930.6124 | 1075 | 1150 | 38930.6125 | 1156 | 1184 | 1116.5 | 1210.5 | 65.6288 | 70.2076 | 70.5739 | 72.2833 | 0.65629 | 0.70208 | 0.70574 | 0.72283 | 0.045788 | 0.017094 | 930.3352 | 3144.2378 | 9.4372
38930.6131 | 11 | 45 | 38930.6131 | 64 | 94 | 1175 | 1269 | 0.67155 | 2.7473 | 3.9072 | 5.7387 | 0.0067155 | 0.027473 | 0.039072 | 0.057387 | 0.020757 | 0.018315 | 6298.3901 | 7187.6385 | 4508.4308
38930.6138 | 963 | 861 | 38930.6138 | 975 | 876 | 1234 | 1328 | 58.7912 | 52.5641 | 59.5238 | 53.4799 | 0.58791 | 0.52564 | 0.59524 | 0.5348 | 0.062271 | 0.06044 | 1798.0772 | 2263.307 | 32.1476
38930.6145 | 191 | 179 |  | 154 | 132 | 1292 | 1386 | 11.6606 | 10.928 | 9.4017 | 8.0586 | 0.11661 | 0.10928 | 0.094017 | 0.080586 | 0.007326 | 0.013431 | 19119.0686 | 9193.138 | 963.276
38930.6152 | 1140 | 1089 | 38930.6152 | 1053 | 979 | 1351.5 | 1445.5 | 69.5971 | 66.4835 | 64.2857 | 59.768 | 0.69597 | 0.66484 | 0.64286 | 0.59768 | 0.031136 | 0.045177 | 130.8591 | 157.2419 | 6.51
38930.6158 | 1027 | 953 | 38930.6159 | 1028 | 951 | 1410.5 | 1504.5 | 62.6984 | 58.1807 | 62.7595 | 58.0586 | 0.62698 | 0.58181 | 0.62759 | 0.58059 | 0.045177 | 0.047009 | 3936.7804 | 2053.282 | 13.3098
38930.6165 | 959 | 864 | 38930.6165 | 1110 | 1053 | 1469 | 1563 | 58.547 | 52.7473 | 67.7656 | 64.2857 | 0.58547 | 0.52747 | 0.67766 | 0.64286 | 0.057998 | 0.034799 | 538.0518 | 723.1263 | 29.4891
38930.6172 | 1135 | 854 | 38930.6172 | 1184 | 1152 | 1528 | 1622 | 69.2918 | 52.1368 | 72.2833 | 70.3297 | 0.69292 | 0.52137 | 0.72283 | 0.7033 | 0.17155 | 0.019536 | 32.1777 | 30.9596 | 3.4331
38930.6179 | 1103 | 1170 | 38930.6179 | 974 | 888 | 1586.5 | 1680.5 | 67.3382 | 71.4286 | 59.4628 | 54.2125 | 0.67338 | 0.71429 | 0.59463 | 0.54212 | 0.040904 | 0.052503 | 458.6297 | 763.58 | 12.0902
38930.6186 | 994 | 910 | 38930.6186 | 1024 | 1035 | 1645.5 | 1739.5 | 60.6838 | 55.5556 | 62.5153 | 63.1868 | 0.60684 | 0.55556 | 0.62515 | 0.63187 | 0.051282 | 0.0067155 | 339.7484 | 370.8727 | 18.0912

## C3-4
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38930.5988 | 1 | 0 | 38930.5988 | 1 | 0 | -62.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5995 | 1 | 0 | 38930.5995 | 1 | 0 | -3.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6002 | 1 | 0 | 38930.6002 | 1 | 0 | 55.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6008 | 1 | 0 | 38930.6009 | 1 | 0 | 114 | 208 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6015 | 1 | 0 | 38930.6015 | 1 | 0 | 173 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6022 | 1 | 0 | 38930.6022 | 1 | 0 | 231.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6029 | 1 | 0 | 38930.6029 | 1 | 0 | 290.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6036 | 1 | 0 | 38930.6036 | 1 | 0 | 349 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6042 | 1 | 0 | 38930.6043 | 1 | 0 | 408 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6049 | 1 | 0 | 38930.6049 | 1 | 0 | 467 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6056 | 1 | 0 | 38930.6056 | 1 | 0 | 525.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6063 | 1 | 0 | 38930.6063 | 2 | 0 | 584.5 | 678.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38930.607 | 1 | 0 | 38930.607 | 1 | 0 | 643 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6076 | 1 | 0 | 38930.6077 | 1 | 0 | 702 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6083 | 1 | 0 | 38930.6083 | 1 | 0 | 760.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.609 | 1 | 0 | 38930.609 | 1 | 0 | 819.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6097 | 1062 | 1030 | 38930.6097 | 1072 | 1040 | 878.5 | 972.5 | 64.8352 | 62.8816 | 65.4457 | 63.4921 | 0.64835 | 0.62882 | 0.65446 | 0.63492 | 0.019536 | 0.019536 | 6503.1875 | 6503.1875 | 2.0099
38930.6104 | 1114 | 1049 | 38930.6104 | 1158 | 1109 | 937 | 1031 | 68.0098 | 64.0415 | 70.696 | 67.7045 | 0.6801 | 0.64042 | 0.70696 | 0.67705 | 0.039683 | 0.029915 | 1960.1971 | 7474.3226 | 4.7016
38930.611 | 1028 | 1121 | 38930.6111 | 1172 | 1132 | 996 | 1090 | 62.7595 | 68.4371 | 71.5507 | 69.1087 | 0.62759 | 0.68437 | 0.71551 | 0.69109 | 0.056777 | 0.02442 | 581.013 | 1195.7811 | 2.9619
38930.6117 | 1047 | 1066 | 38930.6117 | 1186 | 1157 | 1054.5 | 1148.5 | 63.9194 | 65.0794 | 72.4054 | 70.6349 | 0.63919 | 0.65079 | 0.72405 | 0.70635 | 0.0116 | 0.017705 | 1843.073 | 2744.6447 | 0.0018102
38930.6124 | 1074 | 1001 | 38930.6124 | 942 | 907 | 1113.5 | 1207.5 | 65.5678 | 61.1111 | 57.5092 | 55.3724 | 0.65568 | 0.61111 | 0.57509 | 0.55372 | 0.044567 | 0.021368 | 612.11 | 1034.6896 | 3.4635
38930.6131 | 1085 | 1051 | 38930.6131 | 1026 | 987 | 1172.5 | 1266.5 | 66.2393 | 64.1636 | 62.6374 | 60.2564 | 0.66239 | 0.64164 | 0.62637 | 0.60256 | 0.020757 | 0.02381 | 1988.46 | 5938.0861 | 2.1503
38930.6138 | 963 | 857 | 38930.6138 | 1043 | 962 | 1231 | 1325 | 58.7912 | 52.3199 | 63.6752 | 58.7302 | 0.58791 | 0.5232 | 0.63675 | 0.5873 | 0.064713 | 0.049451 | 922.8708 | 4604.2279 | 33.4645
38930.6144 | 1029 | 940 | 38930.6145 | 1092 | 1024 | 1290 | 1384 | 62.8205 | 57.3871 | 66.6667 | 62.5153 | 0.62821 | 0.57387 | 0.66667 | 0.62515 | 0.054335 | 0.041514 | 535.2205 | 827.9233 | 13.6701
38930.6151 | 1017 | 1028 |  | 1076 | 1009 | 1348 | 1442 | 62.0879 | 62.7595 | 65.6899 | 61.5995 | 0.62088 | 0.62759 | 0.6569 | 0.616 | 0.0067155 | 0.040904 | 172.8637 | 164.9982 | 4.1198
38930.6158 | 988 | 988 | 38930.6158 | 1060 | 993 | 1407.5 | 1501.5 | 60.3175 | 60.3175 | 64.7131 | 60.6227 | 0.60317 | 0.60317 | 0.64713 | 0.60623 | 0 | 0.040904 | 307.5481 | 270.0908 | 10.1211
38930.6165 | 933 | 879 | 38930.6165 | 1056 | 982 | 1466.5 | 1560.5 | 56.9597 | 53.663 | 64.4689 | 59.9512 | 0.5696 | 0.53663 | 0.64469 | 0.59951 | 0.032967 | 0.045177 | 4821.5212 | 2977.039 | 33.1328
38930.6172 | 931 | 885 | 38930.6172 | 1114 | 1063 | 1525 | 1619 | 56.8376 | 54.0293 | 68.0098 | 64.8962 | 0.56838 | 0.54029 | 0.6801 | 0.64896 | 0.028083 | 0.031136 | 29284.1522 | 2108.9697 | 32.0422
38930.6178 | 1095 | 1040 | 38930.6179 | 1091 | 1129 | 1584 | 1678 | 66.8498 | 63.4921 | 66.6056 | 68.9255 | 0.6685 | 0.63492 | 0.66606 | 0.68926 | 0.033578 | 0.023199 | 801.1647 | 1443.0914 | 1.9765
38930.6185 | 1191 | 1162 | 38930.6185 | 928 | 915 | 1642.5 | 1736.5 | 72.7106 | 70.9402 | 56.6545 | 55.8608 | 0.72711 | 0.7094 | 0.56654 | 0.55861 | 0.017705 | 0.0079365 | 152.5586 | 201.9566 | 13.8128

## C2-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38930.5988 | 1 | 0 | 38930.5988 | 1 | 0 | -65 | 29 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5994 | 1 | 0 | 38930.5995 | 4 | 0 | -6.5 | 87.5 | 0.06105 | 0 | 0.2442 | 0 | 0.0006105 | 0 | 0.002442 | 0 | 0.0006105 | 0.002442 | 211202 | 52725.5 | 211201.9994
38930.6001 | 1 | 0 | 38930.6001 | 1 | 0 | 52.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6008 | 1 | 0 | 38930.6008 | 1 | 0 | 111.5 | 205.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6015 | 1 | 0 | 38930.6015 | 1 | 0 | 170 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6022 | 1 | 0 | 38930.6022 | 1 | 0 | 229 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6028 | 1 | 0 | 38930.6029 | 1 | 0 | 287.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6035 | 1 | 0 | 38930.6035 | 1 | 0 | 346.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6042 | 1 | 0 | 38930.6042 | 1 | 0 | 405.5 | 499.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6049 | 1 | 0 | 38930.6049 | 1 | 0 | 464 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6056 | 1 | 0 | 38930.6056 | 1 | 0 | 522.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6062 | 1 | 0 | 38930.6063 | 1 | 0 | 581.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6069 | 1 | 0 | 38930.6069 | 1 | 0 | 640.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6076 | 1 | 0 | 38930.6076 | 1 | 0 | 699.5 | 793.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6083 | 1 | 0 | 38930.6083 | 1 | 0 | 758 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.609 | 1 | 0 | 38930.609 | 1 | 0 | 816.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6097 | 1099 | 1069 | 38930.6097 | 927 | 913 | 875.5 | 969.5 | 67.094 | 65.2625 | 56.5934 | 55.7387 | 0.67094 | 0.65263 | 0.56593 | 0.55739 | 0.018315 | 0.008547 | 1099.4683 | 1717.8703 | 4.8602
38930.6103 | 1167 | 1123 | 38930.6103 | 1192 | 1170 | 934.5 | 1028.5 | 71.2454 | 68.5592 | 72.7717 | 71.4286 | 0.71245 | 0.68559 | 0.72772 | 0.71429 | 0.026862 | 0.013431 | 2797.9646 | 11021.6976 | 15.6179
38930.611 | 944 | 906 | 38930.611 | 1155 | 1109 | 993 | 1087 | 57.6313 | 55.3114 | 70.5128 | 67.7045 | 0.57631 | 0.55311 | 0.70513 | 0.67705 | 0.023199 | 0.028083 | 2185.2646 | 5846.8279 | 28.5427
38930.6117 | 918 | 978 | 38930.6117 | 1043 | 961 | 1052 | 1146 | 56.044 | 59.707 | 63.6752 | 58.6691 | 0.56044 | 0.59707 | 0.63675 | 0.58669 | 0.03663 | 0.050061 | 2118.4216 | 27248.9208 | 22.109
38930.6124 | 1191 | 1169 | 38930.6124 | 1135 | 1079 | 1110.5 | 1204.5 | 72.7106 | 71.3675 | 69.2918 | 65.873 | 0.72711 | 0.71368 | 0.69292 | 0.65873 | 0.013431 | 0.034188 | 818.2411 | 1289.1036 | 19.6065
38930.6131 | 610 | 628 | 38930.6131 | 14 | 24 | 1169.5 | 1263.5 | 37.2405 | 38.3394 | 0.8547 | 1.4652 | 0.37241 | 0.38339 | 0.008547 | 0.014652 | 0.010989 | 0.006105 | 9966.8629 | 21508.1109 | 138.6896
38930.6137 | 1094 | 1162 | 38930.6137 | 1104 | 1041 | 1228.5 | 1322.5 | 66.7888 | 70.9402 | 67.3993 | 63.5531 | 0.66789 | 0.7094 | 0.67399 | 0.63553 | 0.041514 | 0.038462 | 3950.4607 | 2753.2261 | 11.8734
38930.6144 | 1012 | 1010 | 38930.6144 | 1011 | 920 | 1287 | 1381 | 61.7827 | 61.6606 | 61.7216 | 56.1661 | 0.61783 | 0.61661 | 0.61722 | 0.56166 | 0.001221 | 0.055556 | 316.7527 | 292.2487 | 6.7144
38930.6151 | 1014 | 1020 | 38930.6151 | 953 | 931 | 1346 | 1440 | 61.9048 | 62.2711 | 58.1807 | 56.8376 | 0.61905 | 0.62271 | 0.58181 | 0.56838 | 0.003663 | 0.013431 | 2101.2125 | 2202.8294 | 7.4106
38930.6158 | 1178 | 1167 | 38930.6158 | 969 | 880 | 1404.5 | 1498.5 | 71.917 | 71.2454 | 59.1575 | 53.7241 | 0.71917 | 0.71245 | 0.59158 | 0.53724 | 0.0067155 | 0.054335 | 46.8034 | 58.7388 | 7.3557
38930.6165 | 986 | 894 | 38930.6165 | 924 | 959 | 1463.5 | 1557.5 | 60.1954 | 54.5788 | 56.4103 | 58.547 | 0.60195 | 0.54579 | 0.5641 | 0.58547 | 0.056166 | 0.021368 | 618.0593 | 989.505 | 23.6725
38930.6171 | 1065 | 994 | 38930.6172 | 1165 | 1125 | 1522.5 | 1616.5 | 65.0183 | 60.6838 | 71.1233 | 68.6813 | 0.65018 | 0.60684 | 0.71123 | 0.68681 | 0.043346 | 0.02442 | 452.6632 | 619.2254 | 4.679
38930.6178 | 1020 | 945 | 38930.6178 | 959 | 871 | 1581 | 1675 | 62.2711 | 57.6923 | 58.547 | 53.1746 | 0.62271 | 0.57692 | 0.58547 | 0.53175 | 0.045788 | 0.053724 | 12922.6578 | 1420.1593 | 14.6331
38930.6185 | 1128 | 1184 | 38930.6185 | 1187 | 1127 | 1640 | 1734 | 68.8645 | 72.2833 | 72.4664 | 68.8034 | 0.68864 | 0.72283 | 0.72466 | 0.68803 | 0.034188 | 0.03663 | 2201.0239 | 10527.0714 | 16.6476

## C2-6
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38930.5987 | 1 | 0 | 38930.5987 | 1 | 0 | -68 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5994 | 1 | 0 | 38930.5994 | 1 | 0 | -9 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6001 | 1 | 0 | 38930.6001 | 1 | 0 | 49.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6008 | 1 | 0 | 38930.6008 | 1 | 0 | 108.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6015 | 1 | 0 | 38930.6015 | 1 | 0 | 167.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6021 | 1 | 0 | 38930.6022 | 1 | 0 | 226 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6028 | 1 | 0 | 38930.6028 | 1 | 0 | 285 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6035 | 1 | 0 | 38930.6035 | 1 | 0 | 343.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6042 | 1 | 0 | 38930.6042 | 1 | 0 | 402.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6049 | 1 | 0 | 38930.6049 | 1 | 0 | 461.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6055 | 1 | 0 | 38930.6056 | 1 | 0 | 520 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6062 | 1 | 0 | 38930.6062 | 1 | 0 | 578.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6069 | 1 | 0 | 38930.6069 | 1 | 0 | 637.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6076 | 1 | 0 | 38930.6076 | 1 | 0 | 696.5 | 790.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6083 | 1 | 0 | 38930.6083 | 1 | 0 | 755 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6089 | 1 | 0 | 38930.609 | 1 | 0 | 814 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6096 | 1172 | 1190 | 38930.6096 | 1193 | 1183 | 872.5 | 966.5 | 71.5507 | 72.6496 | 72.8327 | 72.2222 | 0.71551 | 0.7265 | 0.72833 | 0.72222 | 0.010989 | 0.006105 | 11630.2771 | 12009.4333 | 20.7499
38930.6103 | 1090 | 1021 | 38930.6103 | 1116 | 1170 | 931.5 | 1025.5 | 66.5446 | 62.3321 | 68.1319 | 71.4286 | 0.66545 | 0.62332 | 0.68132 | 0.71429 | 0.042125 | 0.032967 | 1278.1387 | 9248.3322 | 0.19573
38930.611 | 1123 | 1063 | 38930.611 | 927 | 1010 | 990.5 | 1084.5 | 68.5592 | 64.8962 | 56.5934 | 61.6606 | 0.68559 | 0.64896 | 0.56593 | 0.61661 | 0.03663 | 0.050672 | 589.1417 | 983.8541 | 6.232
38930.6117 | 1109 | 1148 | 38930.6117 | 1188 | 1165 | 1049 | 1143 | 67.7045 | 70.0855 | 72.5275 | 71.1233 | 0.67705 | 0.70085 | 0.72527 | 0.71123 | 0.02381 | 0.014042 | 4225.5037 | 7533.2801 | 12.3775
38930.6123 | 1112 | 1047 | 38930.6124 | 1047 | 961 | 1108 | 1202 | 67.8877 | 63.9194 | 63.9194 | 58.6691 | 0.67888 | 0.63919 | 0.63919 | 0.58669 | 0.039683 | 0.052503 | 293.6785 | 379.5462 | 3.4758
| 29 | 76 | 38930.613 | 21 | 30 | 1167 | 1261 | 1.7705 | 4.6398 | 1.2821 | 1.8315 | 0.017705 | 0.046398 | 0.012821 | 0.018315 | 0.028694 | 0.0054945 | 4462.8119 | 25120.9864 | 2631.6557
38930.6137 | 1145 | 1184 | 38930.6137 | 1193 | 1180 | 1225.5 | 1319.5 | 69.9023 | 72.2833 | 72.8327 | 72.0391 | 0.69902 | 0.72283 | 0.72833 | 0.72039 | 0.02381 | 0.0079365 | 2472.1933 | 757402.3602 | 18.2391
38930.6144 | 1051 | 1069 | 38930.6144 | 1199 | 1177 | 1284.5 | 1378.5 | 64.1636 | 65.2625 | 73.199 | 71.8559 | 0.64164 | 0.65263 | 0.73199 | 0.71856 | 0.010989 | 0.013431 | 4069.0649 | 13197.769 | 0.64804
38930.6151 | 966 | 950 | 38930.6151 | 973 | 880 | 1343 | 1437 | 58.9744 | 57.9976 | 59.4017 | 53.7241 | 0.58974 | 0.57998 | 0.59402 | 0.53724 | 0.009768 | 0.056777 | 672.697 | 614.8444 | 17.8378
38930.6157 | 995 | 1098 | 38930.6158 | 1156 | 1193 | 1402 | 1496 | 60.7448 | 67.033 | 70.5739 | 72.8327 | 0.60745 | 0.67033 | 0.70574 | 0.72833 | 0.062882 | 0.022589 | 414.0788 | 657.4782 | 1.5826
38930.6164 | 1027 | 942 | 38930.6164 | 1102 | 1044 | 1460.5 | 1554.5 | 62.6984 | 57.5092 | 67.2772 | 63.7363 | 0.62698 | 0.57509 | 0.67277 | 0.63736 | 0.051893 | 0.035409 | 365.9341 | 444.8008 | 12.4824
38930.6171 | 1046 | 1066 | 38930.6171 | 994 | 994 | 1519.5 | 1613.5 | 63.8584 | 65.0794 | 60.6838 | 60.6838 | 0.63858 | 0.65079 | 0.60684 | 0.60684 | 0.01221 | 0 | 600.5823 | 676.1203 | 0.083356
38930.6178 | 1195 | 1169 | 38930.6178 | 995 | 926 | 1578.5 | 1672.5 | 72.9548 | 71.3675 | 60.7448 | 56.5324 | 0.72955 | 0.71368 | 0.60745 | 0.56532 | 0.015873 | 0.042125 | 108.7935 | 142.9412 | 12.6323
38930.6185 | 1194 | 1189 | 38930.6185 | 1169 | 1128 | 1637 | 1731 | 72.8938 | 72.5885 | 71.3675 | 68.8645 | 0.72894 | 0.72589 | 0.71368 | 0.68864 | 0.0030525 | 0.025031 | 1075.6997 | 1478.2191 | 21.2677

## C2-5
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38930.5987 | 1 | 0 | 38930.5987 | 1 | 0 | -70.5 | 23.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5994 | 1 | 0 | 38930.5994 | 1 | 0 | -12 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6001 | 1 | 0 | 38930.6001 | 1 | 0 | 47 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6007 | 1 | 0 | 38930.6008 | 1 | 0 | 105.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6014 | 1 | 0 | 38930.6014 | 1 | 0 | 164.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6021 | 1 | 0 | 38930.6021 | 1 | 0 | 223.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6028 | 1 | 0 | 38930.6028 | 1 | 0 | 282 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6035 | 1 | 0 | 38930.6035 | 1 | 0 | 341 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6041 | 1 | 0 | 38930.6042 | 1 | 0 | 399.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6048 | 1 | 0 | 38930.6048 | 1 | 0 | 458.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6055 | 1 | 0 | 38930.6055 | 1 | 0 | 517 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6062 | 1 | 0 | 38930.6062 | 1 | 0 | 576 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6069 | 1 | 0 | 38930.6069 | 1 | 0 | 634.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6075 | 1 | 0 | 38930.6076 | 1 | 0 | 693.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6082 | 1 | 0 | 38930.6082 | 1 | 0 | 752.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6089 | 1 | 0 | 38930.6089 | 1 | 0 | 811 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6096 | 7 | 38 | 38930.6096 | 6 | 35 | 870.5 | 964.5 | 0.42735 | 2.3199 | 0.3663 | 2.1368 | 0.0042735 | 0.023199 | 0.003663 | 0.021368 | 0.018926 | 0.017705 | 6908.1265 | 7394.778 | 5369.5452
38930.6103 | 7 | 27 | 38930.6103 | 6 | 15 | 929 | 1023 | 0.42735 | 1.6484 | 0.3663 | 0.91575 | 0.0042735 | 0.016484 | 0.003663 | 0.0091575 | 0.01221 | 0.0054945 | 10590.2067 | 23785.6677 | 7667.8369
38930.6109 | 1094 | 1159 | 38930.611 | 1109 | 1151 | 987.5 | 1081.5 | 66.7888 | 70.757 | 67.7045 | 70.2686 | 0.66789 | 0.70757 | 0.67705 | 0.70269 | 0.039683 | 0.025641 | 1874.7327 | 10888.2355 | 11.9677
38930.6116 | 1005 | 903 | 38930.6116 | 977 | 955 | 1046.5 | 1140.5 | 61.3553 | 55.1282 | 59.6459 | 58.3028 | 0.61355 | 0.55128 | 0.59646 | 0.58303 | 0.062271 | 0.013431 | 412.8486 | 542.7202 | 19.1718
38930.6123 | 6 | 25 | 38930.6123 | 6 | 23 | 1105 | 1199 | 0.3663 | 1.5263 | 0.3663 | 1.4042 | 0.003663 | 0.015263 | 0.003663 | 0.014042 | 0.0116 | 0.010379 | 11207.119 | 12545.6888 | 8262.2229
38930.613 | 6 | 25 | 38930.613 | 6 | 22 | 1164 | 1258 | 0.3663 | 1.5263 | 0.3663 | 1.3431 | 0.003663 | 0.015263 | 0.003663 | 0.013431 | 0.0116 | 0.009768 | 11200.1128 | 13332.5543 | 8266.0808
38930.6137 | 1078 | 1108 | 38930.6137 | 1030 | 942 | 1222.5 | 1316.5 | 65.812 | 67.6435 | 62.8816 | 57.5092 | 0.65812 | 0.67643 | 0.62882 | 0.57509 | 0.018315 | 0.053724 | 118.7622 | 131.6687 | 3.7435
38930.6144 | 988 | 892 | 38930.6144 | 1190 | 1159 | 1281.5 | 1375.5 | 60.3175 | 54.4567 | 72.6496 | 70.757 | 0.60317 | 0.54457 | 0.7265 | 0.70757 | 0.058608 | 0.018926 | 7.5264 | 6.0061 | 1.4801
38930.615 | 1112 | 1053 | 38930.615 | 1040 | 965 | 1340.5 | 1434.5 | 67.8877 | 64.2857 | 63.4921 | 58.9133 | 0.67888 | 0.64286 | 0.63492 | 0.58913 | 0.03602 | 0.045788 | 370.0143 | 497.7889 | 4.1106
38930.6157 | 972 | 882 | 38930.6157 | 969 | 879 | 1399 | 1493 | 59.3407 | 53.8462 | 59.1575 | 53.663 | 0.59341 | 0.53846 | 0.59158 | 0.53663 | 0.054945 | 0.054945 | 2247.8 | 2247.8 | 28.1165
38930.6164 | 995 | 1101 | 38930.6164 | 1015 | 871 | 1458 | 1552 | 60.7448 | 67.2161 | 61.9658 | 53.1746 | 0.60745 | 0.67216 | 0.61966 | 0.53175 | 0.064713 | 0.087912 | 637.2778 | 1585.6138 | 1.4542
38930.6171 | 972 | 878 | 38930.6171 | 1058 | 992 | 1516.5 | 1610.5 | 59.3407 | 53.602 | 64.591 | 60.5617 | 0.59341 | 0.53602 | 0.64591 | 0.60562 | 0.057387 | 0.040293 | 807.3547 | 1855.1299 | 28.4245
38930.6178 | 965 | 1073 | 38930.6178 | 998 | 910 | 1575.5 | 1669.5 | 58.9133 | 65.5067 | 60.928 | 55.5556 | 0.58913 | 0.65507 | 0.60928 | 0.55556 | 0.065934 | 0.053724 | 1167.9106 | 11058.3321 | 6.929
38930.6184 | 1175 | 1140 | 38930.6184 | 1120 | 1179 | 1634.5 | 1728.5 | 71.7338 | 69.5971 | 68.3761 | 71.978 | 0.71734 | 0.69597 | 0.68376 | 0.71978 | 0.021368 | 0.03602 | 1269.3317 | 2930.6869 | 17.1329

## C2-4
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38930.5987 | 1 | 0 | 38930.5987 | 1 | 0 | -73.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5994 | 1 | 0 | 38930.5994 | 1 | 0 | -14.5 | 79.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6 | 1 | 0 | 38930.6 | 1 | 0 | 44 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6007 | 1 | 0 | 38930.6007 | 1 | 0 | 103 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6014 | 1 | 0 | 38930.6014 | 1 | 0 | 161.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6021 | 1 | 0 | 38930.6021 | 1 | 0 | 220.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6028 | 1 | 0 | 38930.6028 | 1 | 0 | 279.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6034 | 1 | 0 | 38930.6034 | 1 | 0 | 338 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6041 | 1 | 0 | 38930.6041 | 1 | 0 | 396.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6048 | 1 | 0 | 38930.6048 | 1 | 0 | 455.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6055 | 1 | 0 | 38930.6055 | 1 | 0 | 514.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6061 | 1 | 0 | 38930.6062 | 1 | 0 | 573 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6068 | 1 | 0 | 38930.6069 | 1 | 0 | 632 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6075 | 1 | 0 | 38930.6075 | 1 | 0 | 690.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6082 | 1 | 0 | 38930.6082 | 1 | 0 | 749.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6089 | 1 | 0 | 38930.6089 | 1 | 0 | 808.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6096 | 1169 | 1146 | 38930.6096 | 1029 | 993 | 867.5 | 961.5 | 71.3675 | 69.9634 | 62.8205 | 60.6227 | 0.71368 | 0.69963 | 0.62821 | 0.60623 | 0.014042 | 0.021978 | 702.3075 | 1028.5692 | 16.0631
38930.6102 | 965 | 856 | 38930.6103 | 1048 | 1134 | 926 | 1020 | 58.9133 | 52.2589 | 63.9805 | 69.2308 | 0.58913 | 0.52259 | 0.6398 | 0.69231 | 0.066545 | 0.052503 | 593.25 | 1012.8535 | 31.049
38930.6109 | 1113 | 829 | 38930.6109 | 1165 | 1123 | 984.5 | 1078.5 | 67.9487 | 50.6105 | 71.1233 | 68.5592 | 0.67949 | 0.50611 | 0.71123 | 0.68559 | 0.17338 | 0.025641 | 7.2826 | 6.1647 | 1.1979
38930.6116 | 1168 | 1126 | 38930.6116 | 1073 | 992 | 1043.5 | 1137.5 | 71.3065 | 68.7424 | 65.5067 | 60.5617 | 0.71306 | 0.68742 | 0.65507 | 0.60562 | 0.025641 | 0.049451 | 282.2764 | 384.5821 | 12.756
38930.6123 | 989 | 884 | 38930.6123 | 921 | 897 | 1102.5 | 1196.5 | 60.3785 | 53.9683 | 56.2271 | 54.7619 | 0.60379 | 0.53968 | 0.56227 | 0.54762 | 0.064103 | 0.014652 | 526.1441 | 813.7455 | 24.1801
38930.613 | 962 | 856 | 38930.613 | 291 | 642 | 1161 | 1255 | 58.7302 | 52.2589 | 17.7656 | 39.1941 | 0.5873 | 0.52259 | 0.17766 | 0.39194 | 0.064713 | 0.21429 | 1442.0447 | 3269.4978 | 33.4421
38930.6136 | 1181 | 1146 | 38930.6137 | 1176 | 1139 | 1220 | 1314 | 72.1001 | 69.9634 | 71.7949 | 69.536 | 0.721 | 0.69963 | 0.71795 | 0.69536 | 0.021368 | 0.022589 | 4496.7638 | 8028.8428 | 18.4422
38930.6143 | 1131 | 1072 | 38930.6143 | 1070 | 997 | 1278.5 | 1372.5 | 69.0476 | 65.4457 | 65.3236 | 60.8669 | 0.69048 | 0.65446 | 0.65324 | 0.60867 | 0.03602 | 0.044567 | 266.2877 | 346.0503 | 6.5119
38930.615 | 1031 | 1043 | 38930.615 | 1137 | 1087 | 1337.5 | 1431.5 | 62.9426 | 63.6752 | 69.4139 | 66.3614 | 0.62943 | 0.63675 | 0.69414 | 0.66361 | 0.007326 | 0.030525 | 192.0676 | 189.1708 | 2.4474
38930.6157 | 1139 | 1089 | 38930.6157 | 1153 | 1192 | 1396.5 | 1490.5 | 69.536 | 66.4835 | 70.3907 | 72.7717 | 0.69536 | 0.66484 | 0.70391 | 0.72772 | 0.030525 | 0.02381 | 6564.3638 | 3097.093 | 10.2281
38930.6164 | 1088 | 1026 | 38930.6164 | 1143 | 1186 | 1455 | 1549 | 66.4225 | 62.6374 | 69.7802 | 72.4054 | 0.66422 | 0.62637 | 0.6978 | 0.72405 | 0.037851 | 0.026252 | 1388.8958 | 8694.1229 | 0.09443
38930.617 | 964 | 869 | 38930.6171 | 1169 | 1194 | 1514 | 1608 | 58.8523 | 53.0525 | 71.3675 | 72.8938 | 0.58852 | 0.53053 | 0.71368 | 0.72894 | 0.057998 | 0.015263 | 69.3261 | 55.6191 | 11.5168
38930.6177 | 932 | 870 | 38930.6177 | 1103 | 1047 | 1572.5 | 1666.5 | 56.8987 | 53.1136 | 67.3382 | 63.9194 | 0.56899 | 0.53114 | 0.67338 | 0.63919 | 0.037851 | 0.034188 | 2028.3357 | 23052.8338 | 35.595
38930.6184 | 1002 | 916 | 38930.6184 | 1179 | 1193 | 1631.5 | 1725.5 | 61.1722 | 55.9219 | 71.978 | 72.8327 | 0.61172 | 0.55922 | 0.71978 | 0.72833 | 0.052503 | 0.008547 | 81.5877 | 71.8009 | 8.8979

## C2-3
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38930.5986 | 1 | 0 | 38930.5986 | 1 | 0 | -76.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5993 | 1 | 0 | 38930.5993 | 1 | 0 | -17.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6 | 1 | 0 | 38930.6 | 1 | 0 | 41.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6007 | 1 | 0 | 38930.6007 | 1 | 0 | 100 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6014 | 1 | 0 | 38930.6014 | 1 | 0 | 159 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.602 | 1 | 0 | 38930.602 | 1 | 0 | 217.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6027 | 1 | 0 | 38930.6027 | 1 | 0 | 276.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6034 | 1 | 0 | 38930.6034 | 1 | 0 | 335.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6041 | 1 | 0 | 38930.6041 | 1 | 0 | 394 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6048 | 1 | 0 | 38930.6048 | 1 | 0 | 453 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6054 | 1 | 0 | 38930.6055 | 1 | 0 | 511.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6061 | 1 | 0 | 38930.6061 | 1 | 0 | 570.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6068 | 1 | 0 | 38930.6068 | 1 | 0 | 629.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6075 | 1 | 0 | 38930.6075 | 1 | 0 | 688 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6082 | 1 | 0 | 38930.6082 | 1 | 0 | 746.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6088 | 1 | 0 | 38930.6089 | 1 | 0 | 805.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6095 | 1137 | 1109 | 38930.6095 | 1191 | 1189 | 864.5 | 958.5 | 69.4139 | 67.7045 | 72.7106 | 72.5885 | 0.69414 | 0.67705 | 0.72711 | 0.72589 | 0.017094 | 0.001221 | 1774.2228 | 4105.7152 | 11.7059
38930.6102 | 1067 | 1143 | 38930.6102 | 929 | 882 | 923 | 1017 | 65.1404 | 69.7802 | 56.7155 | 53.8462 | 0.6514 | 0.6978 | 0.56716 | 0.53846 | 0.046398 | 0.028694 | 635.2837 | 1289.2821 | 7.874
38930.6109 | 1127 | 1067 | 38930.6109 | 1162 | 1116 | 982 | 1076 | 68.8034 | 65.1404 | 70.9402 | 68.1319 | 0.68803 | 0.6514 | 0.7094 | 0.68132 | 0.03663 | 0.028083 | 3171.3362 | 3690.972 | 7.3893
38930.6116 | 1171 | 1183 | 38930.6116 | 950 | 829 | 1040.5 | 1134.5 | 71.4896 | 72.2222 | 57.9976 | 50.6105 | 0.7149 | 0.72222 | 0.57998 | 0.50611 | 0.007326 | 0.073871 | 88.9264 | 112.9543 | 10.8047
38930.6122 | 1165 | 1167 | 38930.6123 | 1145 | 1180 | 1099.5 | 1193.5 | 71.1233 | 71.2454 | 69.9023 | 72.0391 | 0.71123 | 0.71245 | 0.69902 | 0.72039 | 0.001221 | 0.021368 | 1180.5961 | 1490.4194 | 17.5845
38930.6129 | 962 | 859 | 38930.6129 | 998 | 901 | 1158.5 | 1252.5 | 58.7302 | 52.442 | 60.928 | 55.0061 | 0.5873 | 0.52442 | 0.60928 | 0.55006 | 0.062882 | 0.059219 | 1616.0714 | 2703.2418 | 32.7826
38930.6136 | 1192 | 1163 | 38930.6136 | 1086 | 1155 | 1217 | 1311 | 72.7717 | 71.0012 | 66.3004 | 70.5128 | 0.72772 | 0.71001 | 0.663 | 0.70513 | 0.017705 | 0.042125 | 787.42 | 1322.0896 | 19.3434
38930.6143 | 970 | 867 | 38930.6143 | 1182 | 842 | 1276 | 1370 | 59.2186 | 52.9304 | 72.1612 | 51.4042 | 0.59219 | 0.5293 | 0.72161 | 0.51404 | 0.062882 | 0.20757 | 168.017 | 150.1818 | 19.111
38930.615 | 1083 | 1162 | 38930.615 | 972 | 880 | 1334.5 | 1428.5 | 66.1172 | 70.9402 | 59.3407 | 53.7241 | 0.66117 | 0.7094 | 0.59341 | 0.53724 | 0.04823 | 0.056166 | 910.992 | 3411.0504 | 11.0345
38930.6156 | 1094 | 1030 | 38930.6157 | 1092 | 1030 | 1393.5 | 1487.5 | 66.7888 | 62.8816 | 66.6667 | 62.8816 | 0.66789 | 0.62882 | 0.66667 | 0.62882 | 0.039072 | 0.037851 | 1377.5315 | 10326.4844 | 1.0558
38930.6163 | 978 | 883 | 38930.6163 | 1077 | 1011 | 1452.5 | 1546.5 | 59.707 | 53.9072 | 65.7509 | 61.7216 | 0.59707 | 0.53907 | 0.65751 | 0.61722 | 0.057998 | 0.040293 | 705.4382 | 1339.9958 | 26.5593
38930.617 | 1007 | 922 | 38930.617 | 1192 | 1163 | 1511 | 1605 | 61.4774 | 56.2882 | 72.7717 | 71.0012 | 0.61477 | 0.56288 | 0.72772 | 0.71001 | 0.051893 | 0.017705 | 104.0171 | 94.2445 | 9.6837
38930.6177 | 1014 | 946 | 38930.6177 | 1002 | 878 | 1570 | 1664 | 61.9048 | 57.7534 | 61.1722 | 53.602 | 0.61905 | 0.57753 | 0.61172 | 0.53602 | 0.041514 | 0.075702 | 935.0942 | 1909.9378 | 15.3707
38930.6184 | 1024 | 1035 | 38930.6184 | 1003 | 917 | 1628.5 | 1722.5 | 62.5153 | 63.1868 | 61.2332 | 55.9829 | 0.62515 | 0.63187 | 0.61233 | 0.55983 | 0.0067155 | 0.052503 | 338.2028 | 332.7952 | 4.0134

## C1-7
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38930.5986 | 1 | 0 | 38930.5986 | 1 | 0 | -79 | 15 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5993 | 1 | 0 | 38930.5993 | 1 | 0 | -20.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6 | 1 | 0 | 38930.6 | 1 | 0 | 38.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6006 | 1 | 0 | 38930.6007 | 1 | 0 | 97.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6013 | 1 | 0 | 38930.6013 | 1 | 0 | 156 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.602 | 1 | 0 | 38930.602 | 1 | 0 | 214.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6027 | 1 | 0 | 38930.6027 | 1 | 0 | 273.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6034 | 1 | 0 | 38930.6034 | 1 | 0 | 332.5 | 426.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6041 | 1 | 0 | 38930.6041 | 1 | 0 | 391.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6047 | 1 | 0 | 38930.6047 | 1 | 0 | 450 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6054 | 1 | 0 | 38930.6054 | 1 | 0 | 509 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6061 | 1 | 0 | 38930.6061 | 1 | 0 | 567.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6068 | 1 | 0 | 38930.6068 | 1 | 0 | 626.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6074 | 1 | 0 | 38930.6075 | 1 | 0 | 685 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6081 | 1 | 0 | 38930.6081 | 1 | 0 | 744 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6088 | 1 | 0 | 38930.6088 | 1 | 0 | 802.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6095 | 1114 | 1084 | 38930.6095 | 1090 | 1058 | 861.5 | 955.5 | 68.0098 | 66.1783 | 66.5446 | 64.591 | 0.6801 | 0.66178 | 0.66545 | 0.64591 | 0.018315 | 0.019536 | 3123.3942 | 54607.4876 | 7.8252
38930.6102 | 926 | 1008 | 38930.6102 | 940 | 822 | 920.5 | 1014.5 | 56.5324 | 61.5385 | 57.3871 | 50.1832 | 0.56532 | 0.61538 | 0.57387 | 0.50183 | 0.050061 | 0.072039 | 2477.6467 | 2956.807 | 17.1789
38930.6109 | 1104 | 1145 | 38930.6109 | 1028 | 938 | 979.5 | 1073.5 | 67.3993 | 69.9023 | 62.7595 | 57.265 | 0.67399 | 0.69902 | 0.62759 | 0.57265 | 0.025031 | 0.054945 | 35.5113 | 40.8869 | 3.4465
38930.6115 | 1077 | 999 | 38930.6116 | 1143 | 1090 | 1038 | 1132 | 65.7509 | 60.989 | 69.7802 | 66.5446 | 0.65751 | 0.60989 | 0.6978 | 0.66545 | 0.047619 | 0.032357 | 369.5862 | 493.7749 | 3.0816
38930.6122 | 1188 | 1033 | 38930.6122 | 935 | 824 | 1096.5 | 1190.5 | 72.5275 | 63.0647 | 57.0818 | 50.3053 | 0.72527 | 0.63065 | 0.57082 | 0.50305 | 0.094628 | 0.067766 | 351.0963 | 952.3705 | 9.4598
38930.6129 | 1147 | 827 | 38930.6129 | 1144 | 1180 | 1155.5 | 1249.5 | 70.0244 | 50.4884 | 69.8413 | 72.0391 | 0.70024 | 0.50488 | 0.69841 | 0.72039 | 0.19536 | 0.021978 | 14.1867 | 12.744 | 1.9001
38930.6136 | 1018 | 1021 | 38930.6136 | 1171 | 1131 | 1214.5 | 1308.5 | 62.149 | 62.3321 | 71.4896 | 69.0476 | 0.62149 | 0.62332 | 0.7149 | 0.69048 | 0.0018315 | 0.02442 | 324.1449 | 304.9418 | 5.4594
38930.6142 | 1174 | 1133 | 38930.6143 | 957 | 853 | 1273 | 1367 | 71.6728 | 69.1697 | 58.4249 | 52.0757 | 0.71673 | 0.6917 | 0.58425 | 0.52076 | 0.025031 | 0.063492 | 169.0588 | 220.2396 | 11.7746
38930.6149 | 1085 | 1019 | 38930.615 | 1187 | 1157 | 1332 | 1426 | 66.2393 | 62.21 | 72.4664 | 70.6349 | 0.66239 | 0.6221 | 0.72466 | 0.70635 | 0.040293 | 0.018315 | 743.1615 | 1408.8083 | 0.82651
38930.6156 | 968 | 955 | 38930.6156 | 1055 | 982 | 1390.5 | 1484.5 | 59.0965 | 58.3028 | 64.4078 | 59.9512 | 0.59096 | 0.58303 | 0.64408 | 0.59951 | 0.0079365 | 0.044567 | 488.9929 | 431.8164 | 16.156
38930.6163 | 1030 | 949 | 38930.6163 | 1088 | 1022 | 1449.5 | 1543.5 | 62.8816 | 57.9365 | 66.4225 | 62.3932 | 0.62882 | 0.57937 | 0.66422 | 0.62393 | 0.049451 | 0.040293 | 687.6956 | 1240.7602 | 13.0689
38930.617 | 1117 | 1063 | 38930.617 | 1195 | 890 | 1508.5 | 1602.5 | 68.1929 | 64.8962 | 72.9548 | 54.3346 | 0.68193 | 0.64896 | 0.72955 | 0.54335 | 0.032967 | 0.1862 | 11.5437 | 12.3975 | 0.69501
38930.6177 | 1069 | 1006 | 38930.6177 | 1156 | 1116 | 1567 | 1661 | 65.2625 | 61.4164 | 70.5739 | 68.1319 | 0.65263 | 0.61416 | 0.70574 | 0.68132 | 0.038462 | 0.02442 | 616.13 | 945.0622 | 3.4177
38930.6183 | 1046 | 968 | 38930.6184 | 1096 | 1035 | 1626 | 1720 | 63.8584 | 59.0965 | 66.9109 | 63.1868 | 0.63858 | 0.59096 | 0.66911 | 0.63187 | 0.047619 | 0.037241 | 410.7618 | 532.5524 | 8.6122

## C1-6
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38930.5986 | 1 | 0 | 38930.5986 | 1 | 0 | -82 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5992 | 1 | 0 | 38930.5993 | 1 | 0 | -23 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5999 | 1 | 0 | 38930.5999 | 1 | 0 | 35.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6006 | 1 | 0 | 38930.6006 | 1 | 0 | 94.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6013 | 1 | 0 | 38930.6013 | 1 | 0 | 153.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.602 | 1 | 0 | 38930.602 | 1 | 0 | 212 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6027 | 1 | 0 | 38930.6027 | 1 | 0 | 271 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6033 | 1 | 0 | 38930.6033 | 1 | 0 | 329.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.604 | 1 | 0 | 38930.604 | 1 | 0 | 388.5 | 482.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6047 | 1 | 0 | 38930.6047 | 1 | 0 | 447.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6054 | 1 | 0 | 38930.6054 | 1 | 0 | 506 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6061 | 1 | 0 | 38930.6061 | 1 | 0 | 565 | 659 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6067 | 1 | 0 | 38930.6067 | 1 | 0 | 623.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6074 | 1 | 0 | 38930.6074 | 1 | 0 | 682.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6081 | 1 | 0 | 38930.6081 | 1 | 0 | 741 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6088 | 1 | 0 | 38930.6088 | 1 | 0 | 800 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6095 | 965 | 920 | 38930.6095 | 1183 | 1162 | 858.5 | 952.5 | 58.9133 | 56.1661 | 72.2222 | 70.9402 | 0.58913 | 0.56166 | 0.72222 | 0.7094 | 0.027473 | 0.012821 | 6.0292 | 4.8431 | 1.1449
38930.6101 | 1061 | 979 | 38930.6102 | 1092 | 1129 | 917.5 | 1011.5 | 64.7741 | 59.768 | 66.6667 | 68.9255 | 0.64774 | 0.59768 | 0.66667 | 0.68926 | 0.050061 | 0.022589 | 65.5939 | 64.3301 | 2.9198
38930.6108 | 944 | 831 | 38930.6108 | 1189 | 898 | 976.5 | 1070.5 | 57.6313 | 50.7326 | 72.5885 | 54.823 | 0.57631 | 0.50733 | 0.72589 | 0.54823 | 0.068987 | 0.17766 | 243.0447 | 225.8216 | 28.1921
38930.6115 | 1128 | 819 | 38930.6115 | 1010 | 906 | 1035 | 1129 | 68.8645 | 50 | 61.6606 | 55.3114 | 0.68864 | 0.5 | 0.61661 | 0.55311 | 0.18864 | 0.063492 | 134.744 | 194.0618 | 13.3776
38930.6122 | 1038 | 1126 | 38930.6122 | 920 | 876 | 1094 | 1188 | 63.37 | 68.7424 | 56.1661 | 53.4799 | 0.6337 | 0.68742 | 0.56166 | 0.5348 | 0.053724 | 0.026862 | 534.154 | 994.2027 | 4.1138
38930.6129 | 1054 | 1072 | 38930.6129 | 1001 | 904 | 1152.5 | 1246.5 | 64.3468 | 65.4457 | 61.1111 | 55.1893 | 0.64347 | 0.65446 | 0.61111 | 0.55189 | 0.010989 | 0.059219 | 248.3855 | 262.5125 | 0.87681
38930.6135 | 1066 | 1142 | 38930.6136 | 929 | 1013 | 1211.5 | 1305.5 | 65.0794 | 69.7192 | 56.7155 | 61.8437 | 0.65079 | 0.69719 | 0.56716 | 0.61844 | 0.046398 | 0.051282 | 1394.1422 | 127083.5615 | 8.3104
38930.6142 | 1042 | 959 | 38930.6142 | 1041 | 1134 | 1270.5 | 1364.5 | 63.6142 | 58.547 | 63.5531 | 69.2308 | 0.63614 | 0.58547 | 0.63553 | 0.69231 | 0.050672 | 0.056777 | 28971.4629 | 1209.283 | 10.7888
38930.6149 | 1181 | 1146 | 38930.6149 | 1192 | 1192 | 1329 | 1423 | 72.1001 | 69.9634 | 72.7717 | 72.7717 | 0.721 | 0.69963 | 0.72772 | 0.72772 | 0.021368 | 0 | 1574.7229 | 4738.2221 | 18.286
38930.6156 | 1096 | 1137 | 38930.6156 | 1010 | 1014 | 1388 | 1482 | 66.9109 | 69.4139 | 61.6606 | 61.9048 | 0.66911 | 0.69414 | 0.61661 | 0.61905 | 0.025031 | 0.002442 | 76.5187 | 88.2686 | 4.9474
38930.6163 | 979 | 883 | 38930.6163 | 1067 | 1092 | 1446.5 | 1540.5 | 59.768 | 53.9072 | 65.1404 | 66.6667 | 0.59768 | 0.53907 | 0.6514 | 0.66667 | 0.058608 | 0.015263 | 283.3333 | 290.2291 | 21.1431
38930.6169 | 1048 | 972 | 38930.617 | 1106 | 1044 | 1505.5 | 1599.5 | 63.9805 | 59.3407 | 67.5214 | 63.7363 | 0.6398 | 0.59341 | 0.67521 | 0.63736 | 0.046398 | 0.037851 | 354.8257 | 433.6324 | 7.7766
38930.6176 | 960 | 868 | 38930.6176 | 1180 | 1163 | 1564.5 | 1658.5 | 58.6081 | 52.9915 | 72.0391 | 71.0012 | 0.58608 | 0.52991 | 0.72039 | 0.71001 | 0.056166 | 0.010379 | 93.2822 | 75.8704 | 14.1656
38930.6183 | 1065 | 1091 | 38930.6183 | 1060 | 989 | 1623 | 1717 | 65.0183 | 66.6056 | 64.7131 | 60.3785 | 0.65018 | 0.66606 | 0.64713 | 0.60379 | 0.015873 | 0.043346 | 49.0931 | 51.7365 | 1.3432

## C1-5
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38930.5985 | 1 | 0 | 38930.5986 | 1 | 0 | -84.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5992 | 1 | 0 | 38930.5992 | 1 | 0 | -26 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5999 | 1 | 0 | 38930.5999 | 1 | 0 | 33 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6006 | 1 | 0 | 38930.6006 | 1 | 0 | 91.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6013 | 1 | 0 | 38930.6013 | 1 | 0 | 150.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6019 | 1 | 0 | 38930.602 | 1 | 0 | 209.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6026 | 1 | 0 | 38930.6026 | 1 | 0 | 268 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6033 | 1 | 0 | 38930.6033 | 1 | 0 | 326.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.604 | 1 | 0 | 38930.604 | 1 | 0 | 385.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6047 | 1 | 0 | 38930.6047 | 1 | 0 | 444.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6053 | 1 | 0 | 38930.6054 | 1 | 0 | 503.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.606 | 1 | 0 | 38930.606 | 1 | 0 | 562 | 656 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6067 | 1 | 0 | 38930.6067 | 1 | 0 | 620.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6074 | 1 | 0 | 38930.6074 | 1 | 0 | 679.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6081 | 1 | 0 | 38930.6081 | 1 | 0 | 738.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6087 | 1 | 0 | 38930.6088 | 1 | 0 | 797 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6094 | 6 | 37 | 38930.6094 | 5 | 31 | 856 | 950 | 0.3663 | 2.2589 | 0.30525 | 1.8926 | 0.003663 | 0.022589 | 0.0030525 | 0.018926 | 0.018926 | 0.015873 | 6896.6088 | 8250.4049 | 5527.6501
38930.6101 | 7 | 31 | 38930.6101 | 6 | 17 | 915 | 1009 | 0.42735 | 1.8926 | 0.3663 | 1.0379 | 0.0042735 | 0.018926 | 0.003663 | 0.010379 | 0.014652 | 0.0067155 | 8833.6091 | 19495.8097 | 6659.4545
38930.6108 | 1037 | 1044 | 38930.6108 | 996 | 986 | 973.5 | 1067.5 | 63.3089 | 63.7363 | 60.8059 | 60.1954 | 0.63309 | 0.63736 | 0.60806 | 0.60195 | 0.0042735 | 0.006105 | 6583.7878 | 11173.5677 | 3.0398
38930.6115 | 1048 | 955 | 38930.6115 | 957 | 838 | 1032.5 | 1126.5 | 63.9805 | 58.3028 | 58.4249 | 51.16 | 0.6398 | 0.58303 | 0.58425 | 0.5116 | 0.056777 | 0.07265 | 7023.3837 | 1226.9374 | 10.6522
38930.6121 | 963 | 857 | 38930.6122 | 1045 | 962 | 1091 | 1185 | 58.7912 | 52.3199 | 63.7973 | 58.7302 | 0.58791 | 0.5232 | 0.63797 | 0.5873 | 0.064713 | 0.050672 | 959.6454 | 6193.0875 | 33.648
38930.6128 | 6 | 47 | 38930.6128 | 5 | 43 | 1150 | 1244 | 0.3663 | 2.8694 | 0.30525 | 2.6252 | 0.003663 | 0.028694 | 0.0030525 | 0.026252 | 0.025031 | 0.023199 | 5245.1222 | 5669.7396 | 4307.0556
38930.6135 | 1001 | 907 | 38930.6135 | 1118 | 1057 | 1208.5 | 1302.5 | 61.1111 | 55.3724 | 68.254 | 64.5299 | 0.61111 | 0.55372 | 0.68254 | 0.6453 | 0.057387 | 0.037241 | 386.8174 | 468.784 | 18.6301
38930.6142 | 1197 | 1175 | 38930.6142 | 1023 | 934 | 1267.5 | 1361.5 | 73.0769 | 71.7338 | 62.4542 | 57.0208 | 0.73077 | 0.71734 | 0.62454 | 0.57021 | 0.013431 | 0.054335 | 122.7997 | 162.3048 | 13.6381
38930.6149 | 1019 | 934 | 38930.6149 | 1025 | 1036 | 1326.5 | 1420.5 | 62.21 | 57.0208 | 62.5763 | 63.2479 | 0.6221 | 0.57021 | 0.62576 | 0.63248 | 0.051893 | 0.0067155 | 270.889 | 292.916 | 12.7723
38930.6155 | 998 | 909 | 38930.6156 | 1140 | 1090 | 1385 | 1479 | 60.928 | 55.4945 | 69.5971 | 66.5446 | 0.60928 | 0.55495 | 0.69597 | 0.66545 | 0.054335 | 0.030525 | 228.7474 | 228.1363 | 15.7574
38930.6162 | 1128 | 1071 | 38930.6162 | 969 | 1073 | 1444 | 1538 | 68.8645 | 65.3846 | 59.1575 | 65.5067 | 0.68864 | 0.65385 | 0.59158 | 0.65507 | 0.034799 | 0.063492 | 48.2956 | 54.0209 | 2.8157
38930.6169 | 1188 | 1193 | 38930.6169 | 937 | 882 | 1502.5 | 1596.5 | 72.5275 | 72.8327 | 57.2039 | 53.8462 | 0.72527 | 0.72833 | 0.57204 | 0.53846 | 0.0030525 | 0.033578 | 59.6235 | 77.1451 | 9.7823
38930.6176 | 1082 | 1119 | 38930.6176 | 1013 | 930 | 1561.5 | 1655.5 | 66.0562 | 68.315 | 61.8437 | 56.7766 | 0.66056 | 0.68315 | 0.61844 | 0.56777 | 0.022589 | 0.050672 | 179.1478 | 207.7942 | 5.308
38930.6183 | 1135 | 1180 | 38930.6183 | 1108 | 1050 | 1620.5 | 1714.5 | 69.2918 | 72.0391 | 67.6435 | 64.1026 | 0.69292 | 0.72039 | 0.67643 | 0.64103 | 0.027473 | 0.035409 | 1103.0811 | 2702.5437 | 16.5062

## C1-4
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38930.5985 | 1 | 0 | 38930.5985 | 1 | 0 | -87.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5992 | 1 | 0 | 38930.5992 | 1 | 0 | -28.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38930.5999 | 1 | 0 | 31 | 125 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6005 | 1 | 0 | 38930.6006 | 1 | 0 | 89 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6012 | 1 | 0 | 38930.6012 | 1 | 0 | 147.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6019 | 1 | 0 | 38930.6019 | 1 | 0 | 206.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6026 | 2 | 0 | 38930.6026 | 1 | 0 | 265.5 | 359.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38930.6033 | 1 | 0 | 38930.6033 | 1 | 0 | 324 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6039 | 1 | 0 | 38930.604 | 1 | 0 | 383 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6046 | 1 | 0 | 38930.6046 | 1 | 0 | 441.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6053 | 1 | 0 | 38930.6053 | 1 | 0 | 500.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.606 | 1 | 0 | 38930.606 | 1 | 0 | 559 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6067 | 1 | 0 | 38930.6067 | 1 | 0 | 618 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6073 | 1 | 0 | 38930.6074 | 1 | 0 | 677 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.608 | 1 | 0 | 38930.608 | 1 | 0 | 735.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6087 | 1 | 0 | 38930.6087 | 1 | 0 | 794.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6094 | 1192 | 1181 | 38930.6094 | 1136 | 1108 | 853 | 947 | 72.7717 | 72.1001 | 69.3529 | 67.6435 | 0.72772 | 0.721 | 0.69353 | 0.67643 | 0.0067155 | 0.017094 | 1830.998 | 3004.9721 | 21.3046
38930.6101 | 1173 | 1185 | 38930.6101 | 926 | 872 | 912 | 1006 | 71.6117 | 72.3443 | 56.5324 | 53.2357 | 0.71612 | 0.72344 | 0.56532 | 0.53236 | 0.007326 | 0.032967 | 165.8484 | 213.5925 | 14.081
38930.6108 | 995 | 893 | 38930.6108 | 1003 | 902 | 970.5 | 1064.5 | 60.7448 | 54.5177 | 61.2332 | 55.0672 | 0.60745 | 0.54518 | 0.61233 | 0.55067 | 0.062271 | 0.061661 | 1891.258 | 2082.3204 | 24.0436
38930.6114 | 1170 | 821 | 38930.6114 | 1039 | 947 | 1029.5 | 1123.5 | 71.4286 | 50.1221 | 63.431 | 57.8144 | 0.71429 | 0.50122 | 0.63431 | 0.57814 | 0.21306 | 0.056166 | 78.6283 | 96.5497 | 7.3007
38930.6121 | 1027 | 936 | 38930.6121 | 1098 | 1031 | 1088.5 | 1182.5 | 62.6984 | 57.1429 | 67.033 | 62.9426 | 0.62698 | 0.57143 | 0.67033 | 0.62943 | 0.055556 | 0.040904 | 463.0479 | 652.0953 | 13.8967
38930.6128 | 1049 | 1069 | 38930.6128 | 1178 | 1122 | 1147 | 1241 | 64.0415 | 65.2625 | 71.917 | 68.4982 | 0.64042 | 0.65263 | 0.71917 | 0.68498 | 0.01221 | 0.034188 | 496.8905 | 550.6457 | 0.39426
38930.6135 | 1145 | 1182 | 38930.6135 | 1108 | 1149 | 1206 | 1300 | 69.9023 | 72.1612 | 67.6435 | 70.1465 | 0.69902 | 0.72161 | 0.67643 | 0.70147 | 0.022589 | 0.025031 | 3416.368 | 13640.7219 | 17.9715
38930.6142 | 949 | 843 | 38930.6142 | 1028 | 1033 | 1264.5 | 1358.5 | 57.9365 | 51.4652 | 62.7595 | 63.0647 | 0.57937 | 0.51465 | 0.62759 | 0.63065 | 0.064713 | 0.0030525 | 353.9496 | 378.2542 | 30.1182
38930.6148 | 1196 | 1188 | 38930.6148 | 926 | 945 | 1323.5 | 1417.5 | 73.0159 | 72.5275 | 56.5324 | 57.6923 | 0.73016 | 0.72527 | 0.56532 | 0.57692 | 0.004884 | 0.0116 | 261.084 | 346.1179 | 17.6968
38930.6155 | 1098 | 1039 | 38930.6155 | 936 | 860 | 1382.5 | 1476.5 | 67.033 | 63.431 | 57.1429 | 52.5031 | 0.67033 | 0.63431 | 0.57143 | 0.52503 | 0.03602 | 0.046398 | 3163.493 | 3860.3611 | 2.2497
38930.6162 | 1180 | 1192 | 38930.6162 | 1131 | 1073 | 1441 | 1535 | 72.0391 | 72.7717 | 69.0476 | 65.5067 | 0.72039 | 0.72772 | 0.69048 | 0.65507 | 0.007326 | 0.035409 | 632.538 | 879.6777 | 19.5088
38930.6169 | 1071 | 1011 | 38930.6169 | 1194 | 1192 | 1500 | 1594 | 65.3846 | 61.7216 | 72.8938 | 72.7717 | 0.65385 | 0.61722 | 0.72894 | 0.72772 | 0.03663 | 0.001221 | 465.8857 | 617.7279 | 2.6408
38930.6176 | 1004 | 1106 | 38930.6176 | 1162 | 1193 | 1558.5 | 1652.5 | 61.2943 | 67.5214 | 70.9402 | 72.8327 | 0.61294 | 0.67521 | 0.7094 | 0.72833 | 0.062271 | 0.018926 | 422.1398 | 688.1793 | 0.23841
38930.6182 | 988 | 980 | 38930.6183 | 1100 | 1041 | 1617.5 | 1711.5 | 60.3175 | 59.8291 | 67.1551 | 63.5531 | 0.60317 | 0.59829 | 0.67155 | 0.63553 | 0.004884 | 0.03602 | 240.3414 | 213.0007 | 10.0702

## C1-3
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38930.5985 | 1 | 0 | 38930.5985 | 1 | 0 | -90.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5992 | 1 | 0 | 38930.5992 | 1 | 0 | -31.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5998 | 1 | 0 | 38930.5998 | 1 | 0 | 27.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6005 | 1 | 0 | 38930.6005 | 1 | 0 | 86 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6012 | 1 | 0 | 38930.6012 | 1 | 0 | 145 | 239 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6019 | 1 | 0 | 38930.6019 | 1 | 0 | 203.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6026 | 1 | 0 | 38930.6026 | 1 | 0 | 262.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6032 | 1 | 0 | 38930.6033 | 1 | 0 | 321.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6039 | 1 | 0 | 38930.6039 | 1 | 0 | 380 | 474 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6046 | 1 | 0 | 38930.6046 | 1 | 0 | 439 | 533 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6053 | 1 | 0 | 38930.6053 | 1 | 0 | 497.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.606 | 1 | 0 | 38930.606 | 1 | 0 | 556.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6066 | 1 | 0 | 38930.6067 | 1 | 0 | 615.5 | 709.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6073 | 1 | 0 | 38930.6073 | 1 | 0 | 674 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.608 | 1 | 0 | 38930.608 | 1 | 0 | 732.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6087 | 1 | 0 | 38930.6087 | 1 | 0 | 791.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6094 | 1007 | 1043 | 38930.6094 | 1103 | 1071 | 850.5 | 944.5 | 61.4774 | 63.6752 | 67.3382 | 65.3846 | 0.61477 | 0.63675 | 0.67338 | 0.65385 | 0.021978 | 0.019536 | 1.6524 | 1.5591 | 0.092758
38930.61 | 1076 | 1152 | 38930.6101 | 1171 | 1130 | 909 | 1003 | 65.6899 | 70.3297 | 71.4896 | 68.9866 | 0.6569 | 0.7033 | 0.7149 | 0.68987 | 0.046398 | 0.025031 | 1333.5228 | 65252.467 | 9.9656
38930.6107 | 1039 | 948 | 38930.6107 | 1188 | 876 | 968 | 1062 | 63.431 | 57.8755 | 72.5275 | 53.4799 | 0.63431 | 0.57875 | 0.72527 | 0.5348 | 0.055556 | 0.19048 | 77.0523 | 72.7616 | 5.5987
38930.6114 | 1065 | 981 | 38930.6114 | 1025 | 925 | 1026.5 | 1120.5 | 65.0183 | 59.8901 | 62.5763 | 56.4713 | 0.65018 | 0.5989 | 0.62576 | 0.56471 | 0.051282 | 0.06105 | 3471.9745 | 1822.9162 | 6.4765
38930.6121 | 1022 | 928 | 38930.6121 | 1044 | 1059 | 1085.5 | 1179.5 | 62.3932 | 56.6545 | 63.7363 | 64.652 | 0.62393 | 0.56654 | 0.63736 | 0.64652 | 0.057387 | 0.0091575 | 212.0535 | 220.6885 | 12.089
38930.6128 | 1189 | 914 | 38930.6128 | 1030 | 953 | 1144.5 | 1238.5 | 72.5885 | 55.7998 | 62.8816 | 58.1807 | 0.72589 | 0.558 | 0.62882 | 0.58181 | 0.16789 | 0.047009 | 57.0186 | 67.9271 | 0.44345
38930.6134 | 1191 | 1172 | 38930.6135 | 953 | 863 | 1203 | 1297 | 72.7106 | 71.5507 | 58.1807 | 52.6862 | 0.72711 | 0.71551 | 0.58181 | 0.52686 | 0.0116 | 0.054945 | 69.6619 | 89.8385 | 10.0938
38930.6141 | 1161 | 1117 | 38930.6141 | 1076 | 1004 | 1262 | 1356 | 70.8791 | 68.1929 | 65.6899 | 61.2943 | 0.70879 | 0.68193 | 0.6569 | 0.61294 | 0.026862 | 0.043956 | 385.6984 | 550.707 | 12.5001
38930.6148 | 1015 | 930 | 38930.6148 | 1050 | 1072 | 1320.5 | 1414.5 | 61.9658 | 56.7766 | 64.1026 | 65.4457 | 0.61966 | 0.56777 | 0.64103 | 0.65446 | 0.051893 | 0.013431 | 243.5841 | 254.2535 | 12.9667
38930.6155 | 933 | 1022 | 38930.6155 | 979 | 891 | 1379.5 | 1473.5 | 56.9597 | 62.3932 | 59.768 | 54.3956 | 0.5696 | 0.62393 | 0.59768 | 0.54396 | 0.054335 | 0.053724 | 3889.8548 | 1742.1198 | 14.6225
38930.6162 | 1198 | 937 | 38930.6162 | 1083 | 1119 | 1438.5 | 1532.5 | 73.138 | 57.2039 | 66.1172 | 68.315 | 0.73138 | 0.57204 | 0.66117 | 0.68315 | 0.15934 | 0.021978 | 45.0926 | 52.9916 | 0.81251
38930.6168 | 1163 | 1192 | 38930.6169 | 973 | 881 | 1497 | 1591 | 71.0012 | 72.7717 | 59.4017 | 53.7851 | 0.71001 | 0.72772 | 0.59402 | 0.53785 | 0.017705 | 0.056166 | 42.9352 | 54.5866 | 7.1683
38930.6175 | 1012 | 931 | 38930.6175 | 1027 | 1125 | 1556 | 1650 | 61.7827 | 56.8376 | 62.6984 | 68.6813 | 0.61783 | 0.56838 | 0.62698 | 0.68681 | 0.049451 | 0.059829 | 4536.3151 | 1641.1429 | 17.2132
38930.6182 | 1000 | 873 | 38930.6182 | 1032 | 946 | 1614.5 | 1708.5 | 61.0501 | 53.2967 | 63.0037 | 57.7534 | 0.6105 | 0.53297 | 0.63004 | 0.57753 | 0.077534 | 0.052503 | 606.5416 | 1545.06 | 25.8224

## C1-2
Penlight Test 29 |  |  | 2006-08-01 | 14:23 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38930.5984 | 1 | 0 | 38930.5985 | 1 | 0 | -93 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5991 | 1 | 0 | 38930.5991 | 1 | 0 | -34.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.5998 | 1 | 0 | 38930.5998 | 1 | 0 | 24.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6005 | 1 | 0 | 38930.6005 | 1 | 0 | 83.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6012 | 1 | 0 | 38930.6012 | 1 | 0 | 142 | 236 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6018 | 1 | 0 | 38930.6019 | 1 | 0 | 201 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6025 | 1 | 0 | 38930.6025 | 1 | 0 | 259.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6032 | 1 | 0 | 38930.6032 | 1 | 0 | 318.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6039 | 1 | 0 | 38930.6039 | 1 | 0 | 377.5 | 471.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6046 | 1 | 0 | 38930.6046 | 1 | 0 | 436 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6052 | 1 | 0 | 38930.6053 | 1 | 0 | 495 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6059 | 1 | 0 | 38930.6059 | 1 | 0 | 553.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6066 | 1 | 0 | 38930.6066 | 1 | 0 | 612.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6073 | 1 | 0 | 38930.6073 | 1 | 0 | 671.5 | 765.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.608 | 1 | 0 | 38930.608 | 1 | 0 | 730 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6086 | 1 | 0 | 38930.6087 | 1 | 0 | 788.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38930.6093 | 962 | 918 | 38930.6093 | 1158 | 1188 | 847.5 | 941.5 | 58.7302 | 56.044 | 70.696 | 72.5275 | 0.5873 | 0.56044 | 0.70696 | 0.72527 | 0.026862 | 0.018315 | 59.8245 | 48.83 | 8.3281
38930.61 | 929 | 836 | 38930.61 | 1189 | 1161 | 906.5 | 1000.5 | 56.7155 | 51.0379 | 72.5885 | 70.8791 | 0.56716 | 0.51038 | 0.72589 | 0.70879 | 0.056777 | 0.017094 | 197.4578 | 165.0113 | 25.9207
38930.6107 | 970 | 859 | 38930.6107 | 935 | 819 | 965 | 1059 | 59.2186 | 52.442 | 57.0818 | 50 | 0.59219 | 0.52442 | 0.57082 | 0.5 | 0.067766 | 0.070818 | 2066.3802 | 1542.6081 | 31.0511
38930.6114 | 918 | 867 | 38930.6114 | 984 | 875 | 1024 | 1118 | 56.044 | 52.9304 | 60.0733 | 53.4188 | 0.56044 | 0.5293 | 0.60073 | 0.53419 | 0.031136 | 0.066545 | 1599.4822 | 3656.233 | 36.8267
38930.612 | 1189 | 1169 | 38930.6121 | 968 | 859 | 1082.5 | 1176.5 | 72.5885 | 71.3675 | 59.0965 | 52.442 | 0.72589 | 0.71368 | 0.59096 | 0.52442 | 0.01221 | 0.066545 | 51.5213 | 65.9159 | 8.3257
38930.6127 | 934 | 851 | 38930.6127 | 1189 | 1167 | 1141.5 | 1235.5 | 57.0208 | 51.9536 | 72.5885 | 71.2454 | 0.57021 | 0.51954 | 0.72589 | 0.71245 | 0.050672 | 0.013431 | 166.152 | 135.8116 | 22.1995
38930.6134 | 1023 | 931 | 38930.6134 | 1142 | 1091 | 1200.5 | 1294.5 | 62.4542 | 56.8376 | 69.7192 | 66.6056 | 0.62454 | 0.56838 | 0.69719 | 0.66606 | 0.056166 | 0.031136 | 102.0486 | 95.3758 | 8.3381
38930.6141 | 1155 | 1192 | 38930.6141 | 1193 | 1095 | 1259 | 1353 | 70.5128 | 72.7717 | 72.8327 | 66.8498 | 0.70513 | 0.72772 | 0.72833 | 0.6685 | 0.022589 | 0.059829 | 512.04 | 794.1443 | 17.4339
38930.6148 | 1040 | 961 | 38930.6148 | 1051 | 978 | 1318 | 1412 | 63.4921 | 58.6691 | 64.1636 | 59.707 | 0.63492 | 0.58669 | 0.64164 | 0.59707 | 0.04823 | 0.044567 | 1452.8028 | 18691.4532 | 11.5946
38930.6155 | 1114 | 1055 | 38930.6155 | 1010 | 924 | 1376.5 | 1470.5 | 68.0098 | 64.4078 | 61.6606 | 56.4103 | 0.6801 | 0.64408 | 0.61661 | 0.5641 | 0.03602 | 0.052503 | 495.5556 | 739.8528 | 4.6744
38930.6161 | 1080 | 1015 | 38930.6161 | 1178 | 1140 | 1435.5 | 1529.5 | 65.9341 | 61.9658 | 71.917 | 69.5971 | 0.65934 | 0.61966 | 0.71917 | 0.69597 | 0.039683 | 0.023199 | 861.0423 | 1846.3543 | 1.6842
38930.6168 | 1140 | 1186 | 38930.6168 | 980 | 889 | 1494.5 | 1588.5 | 69.5971 | 72.4054 | 59.8291 | 54.2735 | 0.69597 | 0.72405 | 0.59829 | 0.54274 | 0.028083 | 0.055556 | 86.1846 | 109.5111 | 9.3865
38930.6175 | 1157 | 1190 | 38930.6175 | 1087 | 1022 | 1553 | 1647 | 70.6349 | 72.6496 | 66.3614 | 62.3932 | 0.70635 | 0.7265 | 0.66361 | 0.62393 | 0.020147 | 0.039683 | 540.9913 | 828.02 | 17.5435
38930.6182 | 1124 | 1072 | 38930.6182 | 1056 | 986 | 1612 | 1706 | 68.6203 | 65.4457 | 64.4689 | 60.1954 | 0.6862 | 0.65446 | 0.64469 | 0.60195 | 0.031746 | 0.042735 | 57.6742 | 64.4681 | 3.0342

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 29 |  |  | 2006-08-01 | 14:23
38930.5984 | 1 | 0 | 1 | PE | 7-C | Air Drop
38930.5991 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38930.5998 | 1 | 0 | 1
38930.6005 | 1 | 0 | 1
38930.6012 | 1 | 0 | 1
38930.6018 | 1 | 0 | 1
38930.6025 | 1 | 0 | 1
38930.6032 | 1 | 0 | 1
38930.6039 | 1 | 0 | 1
38930.6046 | 1 | 0 | 1
38930.6052 | 1 | 0 | 1
38930.6059 | 1 | 0 | 1
38930.6066 | 1 | 0 | 1
38930.6073 | 1 | 0 | 1
38930.608 | 1 | 0 | 1
38930.6086 | 1 | 0 | 1
38930.6093 | 962 | 918 | 1
38930.61 | 929 | 836 | 1
38930.6107 | 970 | 859 | 1
38930.6114 | 918 | 867 | 1
38930.612 | 1189 | 1169 | 1
38930.6127 | 934 | 851 | 1
38930.6134 | 1023 | 931 | 1
38930.6141 | 1155 | 1192 | 1
38930.6148 | 1040 | 961 | 1
38930.6155 | 1114 | 1055 | 1
38930.6161 | 1080 | 1015 | 1
38930.6168 | 1140 | 1186 | 1
38930.6175 | 1157 | 1190 | 1
38930.6182 | 1124 | 1072 | 1
1
38930.5985 | 1 | 0 | 2
38930.5991 | 1 | 0 | 2
38930.5998 | 1 | 0 | 2
38930.6005 | 1 | 0 | 2
38930.6012 | 1 | 0 | 2
38930.6019 | 1 | 0 | 2
38930.6025 | 1 | 0 | 2
38930.6032 | 1 | 0 | 2
38930.6039 | 1 | 0 | 2
38930.6046 | 1 | 0 | 2
38930.6053 | 1 | 0 | 2
38930.6059 | 1 | 0 | 2
38930.6066 | 1 | 0 | 2
38930.6073 | 1 | 0 | 2
38930.608 | 1 | 0 | 2
38930.6087 | 1 | 1 | 2
38930.6093 | 1158 | 1188 | 2
38930.61 | 1189 | 1161 | 2
38930.6107 | 935 | 819 | 2
38930.6114 | 984 | 875 | 2
38930.6121 | 968 | 859 | 2
38930.6127 | 1189 | 1167 | 2
38930.6134 | 1142 | 1091 | 2
38930.6141 | 1193 | 1095 | 2
38930.6148 | 1051 | 978 | 2
38930.6155 | 1010 | 924 | 2
38930.6161 | 1178 | 1140 | 2
38930.6168 | 980 | 889 | 2
38930.6175 | 1087 | 1022 | 2
38930.6182 | 1056 | 986 | 2
2
38930.5985 | 1 | 0 | 3
38930.5992 | 1 | 0 | 3
38930.5998 | 1 | 0 | 3
38930.6005 | 1 | 0 | 3
38930.6012 | 1 | 0 | 3
38930.6019 | 1 | 0 | 3
38930.6026 | 1 | 0 | 3
38930.6032 | 1 | 0 | 3
38930.6039 | 1 | 0 | 3
38930.6046 | 1 | 0 | 3
38930.6053 | 1 | 0 | 3
38930.606 | 1 | 0 | 3
38930.6066 | 1 | 0 | 3
38930.6073 | 1 | 0 | 3
38930.608 | 1 | 0 | 3
38930.6087 | 1 | 0 | 3
38930.6094 | 1007 | 1043 | 3
38930.61 | 1076 | 1152 | 3
38930.6107 | 1039 | 948 | 3
38930.6114 | 1065 | 981 | 3
38930.6121 | 1022 | 928 | 3
38930.6128 | 1189 | 914 | 3
38930.6134 | 1191 | 1172 | 3
38930.6141 | 1161 | 1117 | 3
38930.6148 | 1015 | 930 | 3
38930.6155 | 933 | 1022 | 3
38930.6162 | 1198 | 937 | 3
38930.6168 | 1163 | 1192 | 3
38930.6175 | 1012 | 931 | 3
38930.6182 | 1000 | 873 | 3
3
38930.5985 | 1 | 0 | 4
38930.5992 | 1 | 0 | 4
38930.5998 | 1 | 0 | 4
38930.6005 | 1 | 0 | 4
38930.6012 | 1 | 0 | 4
38930.6019 | 1 | 0 | 4
38930.6026 | 1 | 0 | 4
38930.6033 | 1 | 0 | 4
38930.6039 | 1 | 0 | 4
38930.6046 | 1 | 0 | 4
38930.6053 | 1 | 0 | 4
38930.606 | 1 | 1 | 4
38930.6067 | 1 | 0 | 4
38930.6073 | 1 | 0 | 4
38930.608 | 1 | 0 | 4
38930.6087 | 1 | 0 | 4
38930.6094 | 1103 | 1071 | 4
38930.6101 | 1171 | 1130 | 4
38930.6107 | 1188 | 876 | 4
38930.6114 | 1025 | 925 | 4
38930.6121 | 1044 | 1059 | 4
38930.6128 | 1030 | 953 | 4
38930.6135 | 953 | 863 | 4
38930.6141 | 1076 | 1004 | 4
38930.6148 | 1050 | 1072 | 4
38930.6155 | 979 | 891 | 4
38930.6162 | 1083 | 1119 | 4
38930.6169 | 973 | 881 | 4
38930.6175 | 1027 | 1125 | 4
38930.6182 | 1032 | 946 | 4
4
38930.5985 | 1 | 0 | 5
38930.5992 | 1 | 0 | 5
38930.6005 | 1 | 0 | 5
38930.6012 | 1 | 0 | 5
38930.6019 | 1 | 0 | 5
38930.6026 | 2 | 0 | 5
38930.6033 | 1 | 0 | 5
38930.6039 | 1 | 0 | 5
38930.6046 | 1 | 0 | 5
38930.6053 | 1 | 0 | 5
38930.606 | 1 | 0 | 5
38930.6067 | 1 | 0 | 5
38930.6073 | 1 | 0 | 5
38930.608 | 1 | 0 | 5
38930.6087 | 1 | 0 | 5
38930.6094 | 1192 | 1181 | 5
38930.6101 | 1173 | 1185 | 5
38930.6108 | 995 | 893 | 5
38930.6114 | 1170 | 821 | 5
38930.6121 | 1027 | 936 | 5
38930.6128 | 1049 | 1069 | 5
38930.6135 | 1145 | 1182 | 5
38930.6142 | 949 | 843 | 5
38930.6148 | 1196 | 1188 | 5
38930.6155 | 1098 | 1039 | 5
38930.6162 | 1180 | 1192 | 5
38930.6169 | 1071 | 1011 | 5
38930.6176 | 1004 | 1106 | 5
38930.6182 | 988 | 980 | 5
5
38930.5985 | 1 | 0 | 6
38930.5992 | 1 | 0 | 6
38930.5999 | 1 | 0 | 6
38930.6006 | 1 | 0 | 6
38930.6012 | 1 | 1 | 6
38930.6019 | 1 | 0 | 6
38930.6026 | 1 | 0 | 6
38930.6033 | 1 | 0 | 6
38930.604 | 1 | 0 | 6
38930.6046 | 1 | 0 | 6
38930.6053 | 1 | 0 | 6
38930.606 | 1 | 0 | 6
38930.6067 | 1 | 0 | 6
38930.6074 | 1 | 0 | 6
38930.608 | 1 | 0 | 6
38930.6087 | 1 | 0 | 6
38930.6094 | 1136 | 1108 | 6
38930.6101 | 926 | 872 | 6
38930.6108 | 1003 | 902 | 6
38930.6114 | 1039 | 947 | 6
38930.6121 | 1098 | 1031 | 6
38930.6128 | 1178 | 1122 | 6
38930.6135 | 1108 | 1149 | 6
38930.6142 | 1028 | 1033 | 6
38930.6148 | 926 | 945 | 6
38930.6155 | 936 | 860 | 6
38930.6162 | 1131 | 1073 | 6
38930.6169 | 1194 | 1192 | 6
38930.6176 | 1162 | 1193 | 6
38930.6183 | 1100 | 1041 | 6
6
38930.5985 | 1 | 0 | 7
38930.5992 | 1 | 0 | 7
38930.5999 | 1 | 0 | 7
38930.6006 | 1 | 0 | 7
38930.6013 | 1 | 0 | 7
38930.6019 | 1 | 0 | 7
38930.6026 | 1 | 0 | 7
38930.6033 | 1 | 0 | 7
38930.604 | 1 | 0 | 7
38930.6047 | 1 | 0 | 7
38930.6053 | 1 | 0 | 7
38930.606 | 1 | 0 | 7
38930.6067 | 1 | 0 | 7
38930.6074 | 1 | 0 | 7
38930.6081 | 1 | 0 | 7
38930.6087 | 1 | 0 | 7
38930.6094 | 6 | 37 | 7
38930.6101 | 7 | 31 | 7
38930.6108 | 1037 | 1044 | 7
38930.6115 | 1048 | 955 | 7
38930.6121 | 963 | 857 | 7
38930.6128 | 6 | 47 | 7
38930.6135 | 1001 | 907 | 7
38930.6142 | 1197 | 1175 | 7
38930.6149 | 1019 | 934 | 7
38930.6155 | 998 | 909 | 7
38930.6162 | 1128 | 1071 | 7
38930.6169 | 1188 | 1193 | 7
38930.6176 | 1082 | 1119 | 7
38930.6183 | 1135 | 1180 | 7
7
38930.5986 | 1 | 0 | 8
38930.5992 | 1 | 0 | 8
38930.5999 | 1 | 0 | 8
38930.6006 | 1 | 0 | 8
38930.6013 | 1 | 0 | 8
38930.602 | 1 | 0 | 8
38930.6026 | 1 | 1 | 8
38930.6033 | 1 | 0 | 8
38930.604 | 1 | 0 | 8
38930.6047 | 1 | 0 | 8
38930.6054 | 1 | 0 | 8
38930.606 | 1 | 0 | 8
38930.6067 | 1 | 0 | 8
38930.6074 | 1 | 0 | 8
38930.6081 | 1 | 0 | 8
38930.6088 | 1 | 0 | 8
38930.6094 | 5 | 31 | 8
38930.6101 | 6 | 17 | 8
38930.6108 | 996 | 986 | 8
38930.6115 | 957 | 838 | 8
38930.6122 | 1045 | 962 | 8
38930.6128 | 5 | 43 | 8
38930.6135 | 1118 | 1057 | 8
38930.6142 | 1023 | 934 | 8
38930.6149 | 1025 | 1036 | 8
38930.6156 | 1140 | 1090 | 8
38930.6162 | 969 | 1073 | 8
38930.6169 | 937 | 882 | 8
38930.6176 | 1013 | 930 | 8
38930.6183 | 1108 | 1050 | 8
8
38930.5986 | 1 | 0 | 9
38930.5992 | 1 | 0 | 9
38930.5999 | 1 | 0 | 9
38930.6006 | 1 | 0 | 9
38930.6013 | 1 | 0 | 9
38930.602 | 1 | 0 | 9
38930.6027 | 1 | 0 | 9
38930.6033 | 1 | 0 | 9
38930.604 | 1 | 0 | 9
38930.6047 | 1 | 0 | 9
38930.6054 | 1 | 0 | 9
38930.6061 | 1 | 0 | 9
38930.6067 | 1 | 0 | 9
38930.6074 | 1 | 0 | 9
38930.6081 | 1 | 0 | 9
38930.6088 | 1 | 0 | 9
38930.6095 | 965 | 920 | 9
38930.6101 | 1061 | 979 | 9
38930.6108 | 944 | 831 | 9
38930.6115 | 1128 | 819 | 9
38930.6122 | 1038 | 1126 | 9
38930.6129 | 1054 | 1072 | 9
38930.6135 | 1066 | 1142 | 9
38930.6142 | 1042 | 959 | 9
38930.6149 | 1181 | 1146 | 9
38930.6156 | 1096 | 1137 | 9
38930.6163 | 979 | 883 | 9
38930.6169 | 1048 | 972 | 9
38930.6176 | 960 | 868 | 9
38930.6183 | 1065 | 1091 | 9
9
38930.5986 | 1 | 0 | 10
38930.5993 | 1 | 0 | 10
38930.5999 | 1 | 0 | 10
38930.6006 | 1 | 0 | 10
38930.6013 | 1 | 0 | 10
38930.602 | 1 | 0 | 10
38930.6027 | 1 | 0 | 10
38930.6033 | 1 | 0 | 10
38930.604 | 1 | 0 | 10
38930.6047 | 1 | 0 | 10
38930.6054 | 1 | 0 | 10
38930.6061 | 1 | 0 | 10
38930.6067 | 1 | 0 | 10
38930.6074 | 1 | 0 | 10
38930.6081 | 1 | 0 | 10
38930.6088 | 1 | 0 | 10
38930.6095 | 1183 | 1162 | 10
38930.6102 | 1092 | 1129 | 10
38930.6108 | 1189 | 898 | 10
38930.6115 | 1010 | 906 | 10
38930.6122 | 920 | 876 | 10
38930.6129 | 1001 | 904 | 10
38930.6136 | 929 | 1013 | 10
38930.6142 | 1041 | 1134 | 10
38930.6149 | 1192 | 1192 | 10
38930.6156 | 1010 | 1014 | 10
38930.6163 | 1067 | 1092 | 10
38930.617 | 1106 | 1044 | 10
38930.6176 | 1180 | 1163 | 10
38930.6183 | 1060 | 989 | 10
10
38930.5986 | 1 | 0 | 11
38930.5993 | 1 | 0 | 11
38930.6 | 1 | 0 | 11
38930.6006 | 1 | 0 | 11
38930.6013 | 1 | 0 | 11
38930.602 | 1 | 0 | 11
38930.6027 | 1 | 0 | 11
38930.6034 | 1 | 0 | 11
38930.6041 | 1 | 0 | 11
38930.6047 | 1 | 0 | 11
38930.6054 | 1 | 0 | 11
38930.6061 | 1 | 0 | 11
38930.6068 | 1 | 0 | 11
38930.6074 | 1 | 0 | 11
38930.6081 | 1 | 0 | 11
38930.6088 | 1 | 0 | 11
38930.6095 | 1114 | 1084 | 11
38930.6102 | 926 | 1008 | 11
38930.6109 | 1104 | 1145 | 11
38930.6115 | 1077 | 999 | 11
38930.6122 | 1188 | 1033 | 11
38930.6129 | 1147 | 827 | 11
38930.6136 | 1018 | 1021 | 11
38930.6142 | 1174 | 1133 | 11
38930.6149 | 1085 | 1019 | 11
38930.6156 | 968 | 955 | 11
38930.6163 | 1030 | 949 | 11
38930.617 | 1117 | 1063 | 11
38930.6177 | 1069 | 1006 | 11
38930.6183 | 1046 | 968 | 11
11
38930.5986 | 1 | 0 | 12
38930.5993 | 1 | 0 | 12
38930.6 | 1 | 0 | 12
38930.6007 | 1 | 0 | 12
38930.6013 | 1 | 0 | 12
38930.602 | 1 | 0 | 12
38930.6027 | 1 | 0 | 12
38930.6034 | 1 | 0 | 12
38930.6041 | 1 | 0 | 12
38930.6047 | 1 | 0 | 12
38930.6054 | 1 | 0 | 12
38930.6061 | 1 | 0 | 12
38930.6068 | 1 | 0 | 12
38930.6075 | 1 | 0 | 12
38930.6081 | 1 | 0 | 12
38930.6088 | 1 | 0 | 12
38930.6095 | 1090 | 1058 | 12
38930.6102 | 940 | 822 | 12
38930.6109 | 1028 | 938 | 12
38930.6116 | 1143 | 1090 | 12
38930.6122 | 935 | 824 | 12
38930.6129 | 1144 | 1180 | 12
38930.6136 | 1171 | 1131 | 12
38930.6143 | 957 | 853 | 12
38930.615 | 1187 | 1157 | 12
38930.6156 | 1055 | 982 | 12
38930.6163 | 1088 | 1022 | 12
38930.617 | 1195 | 890 | 12
38930.6177 | 1156 | 1116 | 12
38930.6184 | 1096 | 1035 | 12
12
38930.5986 | 1 | 0 | 13
38930.5993 | 1 | 0 | 13
38930.6 | 1 | 0 | 13
38930.6007 | 1 | 0 | 13
38930.6014 | 1 | 0 | 13
38930.602 | 1 | 0 | 13
38930.6027 | 1 | 0 | 13
38930.6034 | 1 | 0 | 13
38930.6041 | 1 | 0 | 13
38930.6048 | 1 | 0 | 13
38930.6054 | 1 | 0 | 13
38930.6061 | 1 | 0 | 13
38930.6068 | 1 | 0 | 13
38930.6075 | 1 | 0 | 13
38930.6082 | 1 | 0 | 13
38930.6088 | 1 | 0 | 13
38930.6095 | 1137 | 1109 | 13
38930.6102 | 1067 | 1143 | 13
38930.6109 | 1127 | 1067 | 13
38930.6116 | 1171 | 1183 | 13
38930.6122 | 1165 | 1167 | 13
38930.6129 | 962 | 859 | 13
38930.6136 | 1192 | 1163 | 13
38930.6143 | 970 | 867 | 13
38930.615 | 1083 | 1162 | 13
38930.6156 | 1094 | 1030 | 13
38930.6163 | 978 | 883 | 13
38930.617 | 1007 | 922 | 13
38930.6177 | 1014 | 946 | 13
38930.6184 | 1024 | 1035 | 13
13
38930.5986 | 1 | 0 | 14
38930.5993 | 1 | 0 | 14
38930.6 | 1 | 0 | 14
38930.6007 | 1 | 0 | 14
38930.6014 | 1 | 0 | 14
38930.602 | 1 | 0 | 14
38930.6027 | 1 | 0 | 14
38930.6034 | 1 | 0 | 14
38930.6041 | 1 | 0 | 14
38930.6048 | 1 | 0 | 14
38930.6055 | 1 | 0 | 14
38930.6061 | 1 | 0 | 14
38930.6068 | 1 | 0 | 14
38930.6075 | 1 | 0 | 14
38930.6082 | 1 | 0 | 14
38930.6089 | 1 | 0 | 14
38930.6095 | 1191 | 1189 | 14
38930.6102 | 929 | 882 | 14
38930.6109 | 1162 | 1116 | 14
38930.6116 | 950 | 829 | 14
38930.6123 | 1145 | 1180 | 14
38930.6129 | 998 | 901 | 14
38930.6136 | 1086 | 1155 | 14
38930.6143 | 1182 | 842 | 14
38930.615 | 972 | 880 | 14
38930.6157 | 1092 | 1030 | 14
38930.6163 | 1077 | 1011 | 14
38930.617 | 1192 | 1163 | 14
38930.6177 | 1002 | 878 | 14
38930.6184 | 1003 | 917 | 14
14
38930.5987 | 1 | 0 | 15
38930.5994 | 1 | 0 | 15
38930.6 | 1 | 0 | 15
38930.6007 | 1 | 0 | 15
38930.6014 | 1 | 0 | 15
38930.6021 | 1 | 0 | 15
38930.6028 | 1 | 0 | 15
38930.6034 | 1 | 0 | 15
38930.6041 | 1 | 0 | 15
38930.6048 | 1 | 0 | 15
38930.6055 | 1 | 0 | 15
38930.6061 | 1 | 0 | 15
38930.6068 | 1 | 0 | 15
38930.6075 | 1 | 0 | 15
38930.6082 | 1 | 0 | 15
38930.6089 | 1 | 0 | 15
38930.6096 | 1169 | 1146 | 15
38930.6102 | 965 | 856 | 15
38930.6109 | 1113 | 829 | 15
38930.6116 | 1168 | 1126 | 15
38930.6123 | 989 | 884 | 15
38930.613 | 962 | 856 | 15
38930.6136 | 1181 | 1146 | 15
38930.6143 | 1131 | 1072 | 15
38930.615 | 1031 | 1043 | 15
38930.6157 | 1139 | 1089 | 15
38930.6164 | 1088 | 1026 | 15
38930.617 | 964 | 869 | 15
38930.6177 | 932 | 870 | 15
38930.6184 | 1002 | 916 | 15
15
38930.5987 | 1 | 0 | 16
38930.5994 | 1 | 0 | 16
38930.6 | 1 | 0 | 16
38930.6007 | 1 | 0 | 16
38930.6014 | 1 | 0 | 16
38930.6021 | 1 | 0 | 16
38930.6028 | 1 | 0 | 16
38930.6034 | 1 | 0 | 16
38930.6041 | 1 | 0 | 16
38930.6048 | 1 | 0 | 16
38930.6055 | 1 | 0 | 16
38930.6062 | 1 | 0 | 16
38930.6069 | 1 | 0 | 16
38930.6075 | 1 | 0 | 16
38930.6082 | 1 | 0 | 16
38930.6089 | 1 | 0 | 16
38930.6096 | 1029 | 993 | 16
38930.6103 | 1048 | 1134 | 16
38930.6109 | 1165 | 1123 | 16
38930.6116 | 1073 | 992 | 16
38930.6123 | 921 | 897 | 16
38930.613 | 291 | 642 | 16
38930.6137 | 1176 | 1139 | 16
38930.6143 | 1070 | 997 | 16
38930.615 | 1137 | 1087 | 16
38930.6157 | 1153 | 1192 | 16
38930.6164 | 1143 | 1186 | 16
38930.6171 | 1169 | 1194 | 16
38930.6177 | 1103 | 1047 | 16
38930.6184 | 1179 | 1193 | 16
16
38930.5987 | 1 | 0 | 17
38930.5994 | 1 | 0 | 17
38930.6001 | 1 | 0 | 17
38930.6007 | 1 | 0 | 17
38930.6014 | 1 | 0 | 17
38930.6021 | 1 | 0 | 17
38930.6028 | 1 | 0 | 17
38930.6035 | 1 | 0 | 17
38930.6041 | 1 | 0 | 17
38930.6048 | 1 | 0 | 17
38930.6055 | 1 | 0 | 17
38930.6062 | 1 | 0 | 17
38930.6069 | 1 | 0 | 17
38930.6075 | 1 | 0 | 17
38930.6082 | 1 | 0 | 17
38930.6089 | 1 | 0 | 17
38930.6096 | 7 | 38 | 17
38930.6103 | 7 | 27 | 17
38930.6109 | 1094 | 1159 | 17
38930.6116 | 1005 | 903 | 17
38930.6123 | 6 | 25 | 17
38930.613 | 6 | 25 | 17
38930.6137 | 1078 | 1108 | 17
38930.6144 | 988 | 892 | 17
38930.615 | 1112 | 1053 | 17
38930.6157 | 972 | 882 | 17
38930.6164 | 995 | 1101 | 17
38930.6171 | 972 | 878 | 17
38930.6178 | 965 | 1073 | 17
38930.6184 | 1175 | 1140 | 17
17
38930.5987 | 1 | 0 | 18
38930.5994 | 1 | 0 | 18
38930.6001 | 1 | 0 | 18
38930.6008 | 1 | 0 | 18
38930.6014 | 1 | 0 | 18
38930.6021 | 1 | 0 | 18
38930.6028 | 1 | 0 | 18
38930.6035 | 1 | 0 | 18
38930.6042 | 1 | 0 | 18
38930.6048 | 1 | 0 | 18
38930.6055 | 1 | 0 | 18
38930.6062 | 1 | 0 | 18
38930.6069 | 1 | 0 | 18
38930.6076 | 1 | 0 | 18
38930.6082 | 1 | 0 | 18
38930.6089 | 1 | 0 | 18
38930.6096 | 6 | 35 | 18
38930.6103 | 6 | 15 | 18
38930.611 | 1109 | 1151 | 18
38930.6116 | 977 | 955 | 18
38930.6123 | 6 | 23 | 18
38930.613 | 6 | 22 | 18
38930.6137 | 1030 | 942 | 18
38930.6144 | 1190 | 1159 | 18
38930.615 | 1040 | 965 | 18
38930.6157 | 969 | 879 | 18
38930.6164 | 1015 | 871 | 18
38930.6171 | 1058 | 992 | 18
38930.6178 | 998 | 910 | 18
38930.6184 | 1120 | 1179 | 18
18
38930.5987 | 1 | 0 | 19
38930.5994 | 1 | 0 | 19
38930.6001 | 1 | 0 | 19
38930.6008 | 1 | 0 | 19
38930.6015 | 1 | 0 | 19
38930.6021 | 1 | 0 | 19
38930.6028 | 1 | 0 | 19
38930.6035 | 1 | 0 | 19
38930.6042 | 1 | 0 | 19
38930.6049 | 1 | 0 | 19
38930.6055 | 1 | 0 | 19
38930.6062 | 1 | 0 | 19
38930.6069 | 1 | 0 | 19
38930.6076 | 1 | 0 | 19
38930.6083 | 1 | 0 | 19
38930.6089 | 1 | 0 | 19
38930.6096 | 1172 | 1190 | 19
38930.6103 | 1090 | 1021 | 19
38930.611 | 1123 | 1063 | 19
38930.6117 | 1109 | 1148 | 19
38930.6123 | 1112 | 1047 | 19
38930.6137 | 1145 | 1184 | 19
38930.6144 | 1051 | 1069 | 19
38930.6151 | 966 | 950 | 19
38930.6157 | 995 | 1098 | 19
38930.6164 | 1027 | 942 | 19
38930.6171 | 1046 | 1066 | 19
38930.6178 | 1195 | 1169 | 19
38930.6185 | 1194 | 1189 | 19
19
38930.5987 | 1 | 0 | 20
38930.5994 | 1 | 0 | 20
38930.6001 | 1 | 0 | 20
38930.6008 | 1 | 0 | 20
38930.6015 | 1 | 0 | 20
38930.6022 | 1 | 0 | 20
38930.6028 | 1 | 0 | 20
38930.6035 | 1 | 0 | 20
38930.6042 | 1 | 0 | 20
38930.6049 | 1 | 0 | 20
38930.6056 | 1 | 0 | 20
38930.6062 | 1 | 0 | 20
38930.6069 | 1 | 1 | 20
38930.6076 | 1 | 0 | 20
38930.6083 | 1 | 0 | 20
38930.609 | 1 | 0 | 20
38930.6096 | 1193 | 1183 | 20
38930.6103 | 1116 | 1170 | 20
38930.611 | 927 | 1010 | 20
38930.6117 | 1188 | 1165 | 20
38930.6124 | 1047 | 961 | 20
38930.613 | 21 | 30 | 20
38930.6137 | 1193 | 1180 | 20
38930.6144 | 1199 | 1177 | 20
38930.6151 | 973 | 880 | 20
38930.6158 | 1156 | 1193 | 20
38930.6164 | 1102 | 1044 | 20
38930.6171 | 994 | 994 | 20
38930.6178 | 995 | 926 | 20
38930.6185 | 1169 | 1128 | 20
20
38930.5988 | 1 | 0 | 21
38930.5994 | 1 | 0 | 21
38930.6001 | 1 | 0 | 21
38930.6008 | 1 | 0 | 21
38930.6015 | 1 | 0 | 21
38930.6022 | 1 | 0 | 21
38930.6028 | 1 | 0 | 21
38930.6035 | 1 | 0 | 21
38930.6042 | 1 | 0 | 21
38930.6049 | 1 | 0 | 21
38930.6056 | 1 | 0 | 21
38930.6062 | 1 | 0 | 21
38930.6069 | 1 | 0 | 21
38930.6076 | 1 | 0 | 21
38930.6083 | 1 | 0 | 21
38930.609 | 1 | 0 | 21
38930.6097 | 1099 | 1069 | 21
38930.6103 | 1167 | 1123 | 21
38930.611 | 944 | 906 | 21
38930.6117 | 918 | 978 | 21
38930.6124 | 1191 | 1169 | 21
38930.6131 | 610 | 628 | 21
38930.6137 | 1094 | 1162 | 21
38930.6144 | 1012 | 1010 | 21
38930.6151 | 1014 | 1020 | 21
38930.6158 | 1178 | 1167 | 21
38930.6165 | 986 | 894 | 21
38930.6171 | 1065 | 994 | 21
38930.6178 | 1020 | 945 | 21
38930.6185 | 1128 | 1184 | 21
21
38930.5988 | 1 | 0 | 22
38930.5995 | 4 | 0 | 22
38930.6001 | 1 | 0 | 22
38930.6008 | 1 | 0 | 22
38930.6015 | 1 | 0 | 22
38930.6022 | 1 | 0 | 22
38930.6029 | 1 | 0 | 22
38930.6035 | 1 | 0 | 22
38930.6042 | 1 | 0 | 22
38930.6049 | 1 | 0 | 22
38930.6056 | 1 | 0 | 22
38930.6063 | 1 | 0 | 22
38930.6069 | 1 | 0 | 22
38930.6076 | 1 | 0 | 22
38930.6083 | 1 | 0 | 22
38930.609 | 1 | 0 | 22
38930.6097 | 927 | 913 | 22
38930.6103 | 1192 | 1170 | 22
38930.611 | 1155 | 1109 | 22
38930.6117 | 1043 | 961 | 22
38930.6124 | 1135 | 1079 | 22
38930.6131 | 14 | 24 | 22
38930.6137 | 1104 | 1041 | 22
38930.6144 | 1011 | 920 | 22
38930.6151 | 953 | 931 | 22
38930.6158 | 969 | 880 | 22
38930.6165 | 924 | 959 | 22
38930.6172 | 1165 | 1125 | 22
38930.6178 | 959 | 871 | 22
38930.6185 | 1187 | 1127 | 22
22
38930.5988 | 1 | 0 | 23
38930.5995 | 1 | 0 | 23
38930.6002 | 1 | 0 | 23
38930.6008 | 1 | 0 | 23
38930.6015 | 1 | 0 | 23
38930.6022 | 1 | 0 | 23
38930.6029 | 1 | 0 | 23
38930.6036 | 1 | 0 | 23
38930.6042 | 1 | 0 | 23
38930.6049 | 1 | 0 | 23
38930.6056 | 1 | 0 | 23
38930.6063 | 1 | 0 | 23
38930.607 | 1 | 0 | 23
38930.6076 | 1 | 0 | 23
38930.6083 | 1 | 0 | 23
38930.609 | 1 | 0 | 23
38930.6097 | 1062 | 1030 | 23
38930.6104 | 1114 | 1049 | 23
38930.611 | 1028 | 1121 | 23
38930.6117 | 1047 | 1066 | 23
38930.6124 | 1074 | 1001 | 23
38930.6131 | 1085 | 1051 | 23
38930.6138 | 963 | 857 | 23
38930.6144 | 1029 | 940 | 23
38930.6151 | 1017 | 1028 | 23
38930.6158 | 988 | 988 | 23
38930.6165 | 933 | 879 | 23
38930.6172 | 931 | 885 | 23
38930.6178 | 1095 | 1040 | 23
38930.6185 | 1191 | 1162 | 23
23
38930.5988 | 1 | 0 | 24
38930.5995 | 1 | 0 | 24
38930.6002 | 1 | 0 | 24
38930.6009 | 1 | 0 | 24
38930.6015 | 1 | 0 | 24
38930.6022 | 1 | 0 | 24
38930.6029 | 1 | 0 | 24
38930.6036 | 1 | 0 | 24
38930.6043 | 1 | 0 | 24
38930.6049 | 1 | 0 | 24
38930.6056 | 1 | 0 | 24
38930.6063 | 2 | 0 | 24
38930.607 | 1 | 0 | 24
38930.6077 | 1 | 0 | 24
38930.6083 | 1 | 0 | 24
38930.609 | 1 | 0 | 24
38930.6097 | 1072 | 1040 | 24
38930.6104 | 1158 | 1109 | 24
38930.6111 | 1172 | 1132 | 24
38930.6117 | 1186 | 1157 | 24
38930.6124 | 942 | 907 | 24
38930.6131 | 1026 | 987 | 24
38930.6138 | 1043 | 962 | 24
38930.6145 | 1092 | 1024 | 24
38930.6158 | 1060 | 993 | 24
38930.6165 | 1056 | 982 | 24
38930.6172 | 1114 | 1063 | 24
38930.6179 | 1091 | 1129 | 24
38930.6185 | 928 | 915 | 24
24
38930.5988 | 1 | 0 | 25
38930.5995 | 1 | 0 | 25
38930.6002 | 1 | 0 | 25
38930.6009 | 1 | 0 | 25
38930.6016 | 1 | 0 | 25
38930.6022 | 1 | 0 | 25
38930.6029 | 1 | 0 | 25
38930.6036 | 1 | 0 | 25
38930.6043 | 1 | 0 | 25
38930.605 | 1 | 0 | 25
38930.6056 | 1 | 0 | 25
38930.6063 | 1 | 0 | 25
38930.607 | 1 | 0 | 25
38930.6077 | 1 | 0 | 25
38930.6084 | 1 | 0 | 25
38930.609 | 1 | 0 | 25
38930.6097 | 7 | 40 | 25
38930.6104 | 1175 | 1137 | 25
38930.6111 | 967 | 853 | 25
38930.6118 | 963 | 856 | 25
38930.6124 | 1075 | 1150 | 25
38930.6131 | 11 | 45 | 25
38930.6138 | 963 | 861 | 25
38930.6145 | 191 | 179 | 25
38930.6152 | 1140 | 1089 | 25
38930.6158 | 1027 | 953 | 25
38930.6165 | 959 | 864 | 25
38930.6172 | 1135 | 854 | 25
38930.6179 | 1103 | 1170 | 25
38930.6186 | 994 | 910 | 25
25
38930.5988 | 1 | 0 | 26
38930.5995 | 1 | 0 | 26
38930.6002 | 1 | 0 | 26
38930.6009 | 1 | 0 | 26
38930.6016 | 1 | 0 | 26
38930.6022 | 1 | 0 | 26
38930.6029 | 1 | 0 | 26
38930.6036 | 1 | 0 | 26
38930.6043 | 1 | 0 | 26
38930.605 | 1 | 0 | 26
38930.6056 | 1 | 0 | 26
38930.6063 | 1 | 0 | 26
38930.607 | 1 | 0 | 26
38930.6077 | 1 | 0 | 26
38930.6084 | 1 | 0 | 26
38930.6091 | 1 | 0 | 26
38930.6097 | 6 | 36 | 26
38930.6104 | 1113 | 1168 | 26
38930.6111 | 1061 | 979 | 26
38930.6118 | 1135 | 1178 | 26
38930.6125 | 1156 | 1184 | 26
38930.6131 | 64 | 94 | 26
38930.6138 | 975 | 876 | 26
38930.6152 | 1053 | 979 | 26
38930.6159 | 1028 | 951 | 26
38930.6165 | 1110 | 1053 | 26
38930.6172 | 1184 | 1152 | 26
38930.6179 | 974 | 888 | 26
38930.6186 | 1024 | 1035 | 26
26
38930.5989 | 1 | 0 | 27
38930.5995 | 1 | 0 | 27
38930.6002 | 1 | 0 | 27
38930.6009 | 1 | 0 | 27
38930.6016 | 1 | 0 | 27
38930.6023 | 1 | 0 | 27
38930.6029 | 1 | 0 | 27
38930.6036 | 1 | 0 | 27
38930.6043 | 1 | 0 | 27
38930.605 | 1 | 0 | 27
38930.6057 | 1 | 0 | 27
38930.6063 | 1 | 0 | 27
38930.607 | 1 | 0 | 27
38930.6077 | 1 | 0 | 27
38930.6084 | 1 | 0 | 27
38930.6091 | 1 | 0 | 27
38930.6097 | 958 | 911 | 27
38930.6104 | 1168 | 1124 | 27
38930.6111 | 962 | 857 | 27
38930.6118 | 1090 | 1021 | 27
38930.6125 | 1050 | 968 | 27
38930.6131 | 924 | 911 | 27
38930.6138 | 1018 | 929 | 27
38930.6152 | 996 | 873 | 27
38930.6159 | 938 | 851 | 27
38930.6166 | 997 | 907 | 27
38930.6172 | 933 | 869 | 27
38930.6179 | 961 | 951 | 27
38930.6186 | 1001 | 914 | 27
27
38930.5989 | 1 | 0 | 28
38930.5996 | 1 | 0 | 28
38930.6002 | 1 | 0 | 28
38930.6009 | 1 | 0 | 28
38930.6016 | 1 | 0 | 28
38930.6023 | 1 | 0 | 28
38930.603 | 1 | 0 | 28
38930.6036 | 1 | 0 | 28
38930.6043 | 1 | 0 | 28
38930.605 | 1 | 0 | 28
38930.6057 | 1 | 0 | 28
38930.6064 | 1 | 0 | 28
38930.607 | 1 | 0 | 28
38930.6077 | 1 | 0 | 28
38930.6084 | 1 | 0 | 28
38930.6091 | 1 | 0 | 28
38930.6098 | 1049 | 1066 | 28
38930.6104 | 1033 | 939 | 28
38930.6111 | 1179 | 1183 | 28
38930.6118 | 1007 | 910 | 28
38930.6125 | 1182 | 1147 | 28
38930.6132 | 1001 | 915 | 28
38930.6138 | 923 | 878 | 28
38930.6152 | 1133 | 1185 | 28
38930.6159 | 1189 | 1158 | 28
38930.6166 | 1171 | 1192 | 28
38930.6172 | 1086 | 1025 | 28
38930.6179 | 1076 | 1017 | 28
38930.6186 | 937 | 1032 | 28
28
38930.5989 | 1 | 0 | 29
38930.5996 | 1 | 0 | 29
38930.6003 | 1 | 0 | 29
38930.6009 | 1 | 0 | 29
38930.6016 | 1 | 0 | 29
38930.6023 | 1 | 0 | 29
38930.603 | 1 | 0 | 29
38930.6037 | 1 | 0 | 29
38930.6043 | 1 | 0 | 29
38930.605 | 1 | 0 | 29
38930.6057 | 1 | 0 | 29
38930.6064 | 1 | 0 | 29
38930.6071 | 1 | 0 | 29
38930.6077 | 1 | 0 | 29
38930.6084 | 1 | 0 | 29
38930.6091 | 1 | 0 | 29
38930.6098 | 1020 | 1020 | 29
38930.6105 | 1149 | 1099 | 29
38930.6111 | 938 | 821 | 29
38930.6118 | 1090 | 1019 | 29
38930.6125 | 918 | 964 | 29
38930.6132 | 1166 | 1129 | 29
38930.6139 | 979 | 876 | 29
38930.6152 | 948 | 927 | 29
38930.6159 | 965 | 876 | 29
38930.6166 | 1002 | 1103 | 29
38930.6173 | 989 | 987 | 29
38930.618 | 1175 | 1171 | 29
38930.6186 | 1093 | 1032 | 29
29
38930.5989 | 1 | 0 | 30
38930.5996 | 1 | 0 | 30
38930.6003 | 1 | 0 | 30
38930.6009 | 1 | 0 | 30
38930.6016 | 1 | 0 | 30
38930.6023 | 1 | 0 | 30
38930.603 | 1 | 0 | 30
38930.6037 | 1 | 0 | 30
38930.6044 | 1 | 0 | 30
38930.605 | 1 | 0 | 30
38930.6057 | 1 | 0 | 30
38930.6064 | 1 | 0 | 30
38930.6071 | 1 | 0 | 30
38930.6078 | 1 | 0 | 30
38930.6084 | 1 | 0 | 30
38930.6091 | 1 | 0 | 30
38930.6098 | 1182 | 1146 | 30
38930.6105 | 1191 | 1027 | 30
38930.6112 | 996 | 891 | 30
38930.6118 | 1188 | 1163 | 30
38930.6125 | 1190 | 1175 | 30
38930.6132 | 959 | 936 | 30
38930.6139 | 927 | 887 | 30
38930.6152 | 1198 | 1183 | 30
38930.6159 | 1016 | 928 | 30
38930.6166 | 964 | 949 | 30
38930.6173 | 1024 | 944 | 30
38930.618 | 945 | 847 | 30
38930.6186 | 1099 | 1039 | 30
30
38930.5989 | 1 | 0 | 31
38930.5996 | 1 | 0 | 31
38930.6003 | 1 | 0 | 31
38930.601 | 1 | 0 | 31
38930.6016 | 1 | 0 | 31
38930.6023 | 1 | 0 | 31
38930.603 | 1 | 0 | 31
38930.6037 | 1 | 0 | 31
38930.6044 | 1 | 0 | 31
38930.605 | 1 | 0 | 31
38930.6057 | 1 | 0 | 31
38930.6064 | 1 | 0 | 31
38930.6071 | 1 | 0 | 31
38930.6078 | 1 | 1 | 31
38930.6084 | 1 | 0 | 31
38930.6091 | 1 | 0 | 31
38930.6098 | 6 | 24 | 31
38930.6105 | 1161 | 1115 | 31
38930.6112 | 1016 | 1011 | 31
38930.6119 | 1091 | 1021 | 31
38930.6125 | 919 | 983 | 31
38930.6132 | 936 | 831 | 31
38930.6139 | 1129 | 1072 | 31
38930.6153 | 1124 | 1070 | 31
38930.6159 | 1034 | 949 | 31
38930.6166 | 1036 | 958 | 31
38930.6173 | 924 | 940 | 31
38930.618 | 1194 | 1188 | 31
38930.6187 | 1167 | 1129 | 31
31
38930.5989 | 1 | 0 | 32
38930.5996 | 1 | 0 | 32
38930.6003 | 1 | 0 | 32
38930.601 | 1 | 0 | 32
38930.6017 | 1 | 0 | 32
38930.6023 | 1 | 0 | 32
38930.603 | 1 | 0 | 32
38930.6037 | 1 | 0 | 32
38930.6044 | 1 | 0 | 32
38930.6051 | 1 | 0 | 32
38930.6057 | 1 | 0 | 32
38930.6064 | 1 | 0 | 32
38930.6071 | 1 | 0 | 32
38930.6078 | 1 | 0 | 32
38930.6085 | 1 | 0 | 32
38930.6092 | 1 | 0 | 32
38930.6098 | 6 | 19 | 32
38930.6105 | 1028 | 931 | 32
38930.6112 | 980 | 871 | 32
38930.6119 | 1120 | 1163 | 32
38930.6125 | 932 | 826 | 32
38930.6132 | 949 | 916 | 32
38930.6139 | 1069 | 994 | 32
38930.6153 | 1158 | 1191 | 32
38930.6159 | 985 | 888 | 32
38930.6166 | 1098 | 1139 | 32
38930.6173 | 1045 | 1066 | 32
38930.618 | 1184 | 1151 | 32
38930.6187 | 1111 | 1054 | 32
32
38930.599 | 1 | 0 | 33
38930.5996 | 1 | 0 | 33
38930.6003 | 1 | 0 | 33
38930.601 | 1 | 0 | 33
38930.6017 | 1 | 0 | 33
38930.6024 | 1 | 0 | 33
38930.603 | 1 | 0 | 33
38930.6037 | 1 | 0 | 33
38930.6044 | 1 | 0 | 33
38930.6051 | 1 | 0 | 33
38930.6058 | 1 | 0 | 33
38930.6064 | 1 | 0 | 33
38930.6071 | 1 | 0 | 33
38930.6078 | 1 | 0 | 33
38930.6085 | 1 | 0 | 33
38930.6092 | 1 | 0 | 33
38930.6098 | 996 | 888 | 33
38930.6105 | 1098 | 1028 | 33
38930.6112 | 1038 | 947 | 33
38930.6119 | 1139 | 1086 | 33
38930.6126 | 1041 | 955 | 33
38930.6133 | 1022 | 1026 | 33
38930.6139 | 1137 | 1083 | 33
38930.6153 | 1038 | 959 | 33
38930.616 | 1016 | 1013 | 33
38930.6167 | 982 | 886 | 33
38930.6173 | 966 | 874 | 33
38930.618 | 1020 | 937 | 33
38930.6187 | 1172 | 1185 | 33
33
38930.599 | 1 | 0 | 34
38930.5997 | 1 | 0 | 34
38930.6003 | 1 | 0 | 34
38930.601 | 1 | 0 | 34
38930.6017 | 1 | 0 | 34
38930.6024 | 1 | 0 | 34
38930.6031 | 1 | 0 | 34
38930.6037 | 1 | 0 | 34
38930.6044 | 1 | 0 | 34
38930.6051 | 1 | 0 | 34
38930.6058 | 1 | 0 | 34
38930.6065 | 1 | 0 | 34
38930.6071 | 1 | 0 | 34
38930.6078 | 1 | 0 | 34
38930.6085 | 1 | 0 | 34
38930.6092 | 1 | 0 | 34
38930.6099 | 1149 | 817 | 34
38930.6105 | 1022 | 923 | 34
38930.6112 | 1042 | 1050 | 34
38930.6119 | 1014 | 1015 | 34
38930.6126 | 1189 | 1003 | 34
38930.6133 | 1025 | 937 | 34
38930.6139 | 1161 | 1118 | 34
38930.6153 | 977 | 887 | 34
38930.616 | 1027 | 939 | 34
38930.6167 | 1078 | 1158 | 34
38930.6173 | 1190 | 1191 | 34
38930.618 | 1122 | 1069 | 34
38930.6187 | 1175 | 1136 | 34
34
38930.599 | 1 | 0 | 35
38930.5997 | 1 | 0 | 35
38930.6003 | 1 | 0 | 35
38930.601 | 1 | 0 | 35
38930.6017 | 1 | 0 | 35
38930.6024 | 1 | 0 | 35
38930.6031 | 1 | 0 | 35
38930.6038 | 1 | 0 | 35
38930.6044 | 1 | 0 | 35
38930.6051 | 1 | 0 | 35
38930.6058 | 1 | 0 | 35
38930.6065 | 1 | 0 | 35
38930.6072 | 1 | 0 | 35
38930.6078 | 1 | 0 | 35
38930.6085 | 1 | 0 | 35
38930.6092 | 1 | 0 | 35
38930.6099 | 1162 | 1177 | 35
38930.6106 | 1145 | 816 | 35
38930.6112 | 1170 | 1183 | 35
38930.6119 | 1145 | 1098 | 35
38930.6126 | 1174 | 1154 | 35
38930.6133 | 1081 | 1010 | 35
38930.614 | 1181 | 1188 | 35
38930.6153 | 1048 | 971 | 35
38930.616 | 1099 | 1034 | 35
38930.6167 | 1090 | 1129 | 35
38930.6174 | 1134 | 1181 | 35
38930.618 | 1154 | 1192 | 35
38930.6187 | 1195 | 892 | 35
35
38930.599 | 1 | 0 | 36
38930.5997 | 1 | 0 | 36
38930.6004 | 1 | 0 | 36
38930.6011 | 1 | 0 | 36
38930.6017 | 1 | 0 | 36
38930.6024 | 1 | 0 | 36
38930.6031 | 1 | 0 | 36
38930.6038 | 1 | 0 | 36
38930.6045 | 1 | 0 | 36
38930.6051 | 1 | 1 | 36
38930.6058 | 1 | 0 | 36
38930.6065 | 1 | 0 | 36
38930.6072 | 1 | 0 | 36
38930.6078 | 1 | 0 | 36
38930.6085 | 1 | 0 | 36
38930.6092 | 1 | 0 | 36
38930.6099 | 944 | 831 | 36
38930.6106 | 1139 | 1178 | 36
38930.6113 | 988 | 1088 | 36
38930.6119 | 1178 | 1183 | 36
38930.6126 | 924 | 1021 | 36
38930.6133 | 1008 | 1008 | 36
38930.614 | 1192 | 1189 | 36
38930.6153 | 1115 | 1055 | 36
38930.616 | 948 | 842 | 36
38930.6167 | 1189 | 1192 | 36
38930.6174 | 1199 | 1180 | 36
38930.6181 | 1197 | 920 | 36
38930.6187 | 1175 | 1136 | 36
36
38930.599 | 1 | 0 | 37
38930.5997 | 1 | 1 | 37
38930.6004 | 1 | 0 | 37
38930.6011 | 1 | 0 | 37
38930.6017 | 1 | 0 | 37
38930.6024 | 1 | 0 | 37
38930.6031 | 1 | 0 | 37
38930.6038 | 1 | 0 | 37
38930.6045 | 1 | 0 | 37
38930.6052 | 1 | 0 | 37
38930.6058 | 1 | 0 | 37
38930.6065 | 1 | 0 | 37
38930.6072 | 1 | 0 | 37
38930.6079 | 1 | 0 | 37
38930.6086 | 1 | 0 | 37
38930.6092 | 1 | 0 | 37
38930.6099 | 7 | 39 | 37
38930.6106 | 1158 | 1111 | 37
38930.6113 | 1011 | 914 | 37
38930.612 | 1063 | 1085 | 37
38930.6126 | 1057 | 1105 | 37
38930.6133 | 1062 | 984 | 37
38930.614 | 1086 | 1016 | 37
38930.6154 | 960 | 1065 | 37
38930.616 | 1098 | 1035 | 37
38930.6167 | 944 | 852 | 37
38930.6174 | 1106 | 1047 | 37
38930.6181 | 1168 | 1132 | 37
38930.6188 | 1151 | 1101 | 37
37
38930.599 | 1 | 0 | 38
38930.5997 | 1 | 0 | 38
38930.6004 | 1 | 0 | 38
38930.6011 | 1 | 0 | 38
38930.6018 | 1 | 0 | 38
38930.6024 | 1 | 0 | 38
38930.6031 | 1 | 0 | 38
38930.6038 | 1 | 0 | 38
38930.6045 | 1 | 0 | 38
38930.6052 | 1 | 0 | 38
38930.6058 | 1 | 0 | 38
38930.6065 | 1 | 0 | 38
38930.6072 | 1 | 0 | 38
38930.6079 | 1 | 0 | 38
38930.6086 | 1 | 0 | 38
38930.6092 | 1 | 0 | 38
38930.6099 | 5 | 32 | 38
38930.6106 | 1144 | 1090 | 38
38930.6113 | 1072 | 994 | 38
38930.6127 | 1162 | 1140 | 38
38930.6133 | 1183 | 1152 | 38
38930.614 | 1129 | 1174 | 38
38930.6154 | 1059 | 992 | 38
38930.6161 | 1051 | 971 | 38
38930.6167 | 1054 | 982 | 38
38930.6174 | 1195 | 1190 | 38
38930.6181 | 1194 | 899 | 38
38930.6188 | 1135 | 1082 | 38
38
38930.5991 | 1 | 0 | 39
38930.5997 | 1 | 0 | 39
38930.6004 | 1 | 0 | 39
38930.6011 | 1 | 0 | 39
38930.6018 | 1 | 0 | 39
38930.6025 | 1 | 0 | 39
38930.6031 | 1 | 0 | 39
38930.6038 | 1 | 0 | 39
38930.6045 | 1 | 0 | 39
38930.6052 | 1 | 0 | 39
38930.6059 | 1 | 0 | 39
38930.6065 | 1 | 0 | 39
38930.6072 | 1 | 0 | 39
38930.6079 | 1 | 0 | 39
38930.6086 | 1 | 0 | 39
38930.6093 | 1 | 0 | 39
38930.6099 | 5 | 27 | 39
38930.6106 | 1046 | 1056 | 39
38930.6113 | 1168 | 1128 | 39
38930.612 | 950 | 837 | 39
38930.6127 | 1107 | 1078 | 39
38930.6133 | 929 | 832 | 39
38930.614 | 1164 | 1190 | 39
38930.6154 | 1189 | 1159 | 39
38930.6161 | 1073 | 1156 | 39
38930.6167 | 1069 | 1005 | 39
38930.6174 | 1016 | 1023 | 39
38930.6181 | 1024 | 878 | 39
38930.6188 | 1184 | 1151 | 39
39
38930.5991 | 1 | 0 | 40
38930.5998 | 1 | 0 | 40
38930.6004 | 1 | 0 | 40
38930.6011 | 1 | 0 | 40
38930.6018 | 1 | 0 | 40
38930.6025 | 1 | 0 | 40
38930.6032 | 1 | 0 | 40
38930.6038 | 1 | 0 | 40
38930.6045 | 1 | 0 | 40
38930.6052 | 1 | 0 | 40
38930.6059 | 1 | 0 | 40
38930.6066 | 1 | 0 | 40
38930.6072 | 1 | 0 | 40
38930.6079 | 1 | 0 | 40
38930.6086 | 1 | 0 | 40
38930.6093 | 1 | 0 | 40
38930.61 | 5 | 21 | 40
38930.6106 | 1032 | 937 | 40
38930.6113 | 933 | 1024 | 40
38930.612 | 1182 | 1149 | 40
38930.6127 | 1053 | 913 | 40
38930.6134 | 1128 | 1171 | 40
38930.614 | 1131 | 1073 | 40
38930.6154 | 995 | 992 | 40
38930.6161 | 1176 | 1137 | 40
38930.6168 | 1160 | 1116 | 40
38930.6174 | 1145 | 1097 | 40
38930.6181 | 1024 | 950 | 40
38930.6188 | 927 | 925 | 40
40
38930.5991 | 1 | 0 | 41
38930.5998 | 1 | 0 | 41
38930.6005 | 1 | 0 | 41
38930.6011 | 1 | 0 | 41
38930.6018 | 1 | 0 | 41
38930.6025 | 1 | 0 | 41
38930.6032 | 1 | 0 | 41
38930.6039 | 1 | 0 | 41
38930.6045 | 1 | 0 | 41
38930.6052 | 1 | 0 | 41
38930.6059 | 1 | 0 | 41
38930.6066 | 1 | 0 | 41
38930.6073 | 1 | 0 | 41
38930.6079 | 1 | 0 | 41
38930.6086 | 1 | 0 | 41
38930.6093 | 970 | 929 | 41
38930.61 | 1153 | 1107 | 41
38930.6107 | 989 | 880 | 41
38930.6113 | 1130 | 1072 | 41
38930.612 | 1069 | 1146 | 41
38930.6127 | 1143 | 1188 | 41
38930.6134 | 1079 | 1004 | 41
38930.6141 | 949 | 920 | 41
38930.6147 | 1060 | 988 | 41
38930.6154 | 936 | 908 | 41
38930.6161 | 1112 | 1051 | 41
38930.6168 | 1191 | 1092 | 41
38930.6175 | 972 | 962 | 41
38930.6181 | 1149 | 1102 | 41
38930.6188 | 1199 | 997 | 41
41
38930.5991 | 1 | 0 | 42
38930.5998 | 1 | 0 | 42
38930.6005 | 1 | 0 | 42
38930.6011 | 1 | 0 | 42
38930.6018 | 1 | 0 | 42
38930.6025 | 1 | 0 | 42
38930.6032 | 1 | 0 | 42
38930.6039 | 1 | 0 | 42
38930.6045 | 1 | 0 | 42
38930.6052 | 1 | 0 | 42
38930.6059 | 1 | 0 | 42
38930.6066 | 1 | 0 | 42
38930.6073 | 2 | 0 | 42
38930.608 | 1 | 0 | 42
38930.6086 | 1 | 0 | 42
38930.6093 | 968 | 926 | 42
38930.61 | 1190 | 1164 | 42
38930.6107 | 920 | 918 | 42
38930.6114 | 920 | 917 | 42
38930.612 | 1138 | 1086 | 42
38930.6127 | 931 | 886 | 42
38930.6134 | 1077 | 1004 | 42
38930.6141 | 1091 | 1024 | 42
38930.6148 | 1114 | 1059 | 42
38930.6154 | 1102 | 1041 | 42
38930.6161 | 991 | 894 | 42
38930.6168 | 942 | 842 | 42
38930.6175 | 933 | 872 | 42
38930.6182 | 1025 | 944 | 42
38930.6188 | 1115 | 1177 | 42
42