## Test Facts
Last row in IRMS data sheets: | 39
Time when Penlight power was initiated: | 107

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 30
Test conditions: Cable: 7-conductor, 12 AWG, PE insulated, PVC jacketed, General Cable control cable (Cable Item #15). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: None. Cables were run horizontally through the Penlight chamber ("air drop" configuration) and secured to the raceway support brackets outside of the chamber; chamber end walls were closed and un-heated. Exposure conditions: Shroud set to temperature of 325C, nominal 7.2 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 107 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
107 | 0 | Initated Penlight Heating
706-720 | 599-613 | Conductor 1 shorts to conductors 2, 3, 4, 6 & 7 at less than 100 ohms (3, 27, 16, 2 & 13)
713 | 606 | Conductor 1 shorts to ground (148) | Uncertain path to ground; unstable ground fault condition
723-726 | 616-619 | Conductor 2 shorts to conductors 3 & 4 at less than 100 ohms (2 & 14)
725 | 618 | Conductor 2 shorts to ground (66) | Uncertain path to ground; unstable ground fault condition
729 | 622 | Conductor 5 shorts to conductor 2 briefly (30) | Unsustained conductor-to-conductor short
731-734 | 624-627 | Conductor 2 shorts to conductors 6 & 7 at less than 100 ohms (10 & 17)
733 | 626 | Conductor 3 shorts to ground (167) | Uncertain path to ground; unstable ground fault condition
737 | 630 | Conductor 3 shorts to conductor 4 at less than 100 ohms (19)
738 | 631 | Conductor 4 shorts to ground (950) | Uncertain path to ground; unstable ground fault condition
740 | 633 | Conductor 5 shorts to conductor 3 briefly (5) | Unsustained conductor-to-conductor short
741-745 | 634-638 | Conductors 5, 6 & 7 all short to ground (165, 86 & 330) | Uncertain of paths to ground; unstable ground fault conditions
743-746 | 636-639 | Conductor 3 shorts to conductors 6 & 7 at less than 100 ohms (20 & 20)
748 | 641 | Conductor 5 shorts to conductor 4 briefly (14) | Unsustained conductor-to-conductor short
751-754 | 644-647 | Conductor 4 shorts to conductors 6 & 7 at less than 100 ohms (12 & 22)
757-760 | 650-653 | Conductor 5 shorts to conductors 6 & 7 briefly (5 & 11) | Unsustained conductor-to-conductor shorts
762 | 655 | Conductors 6 & 7 short together at less than 100 ohms (13)
774 | 667 | Conductor 5 shorts to conductor 1 briefly (2) | Unsustained conductor-to-conductor short
846-891 | 739-784 | All shorts involving conductor 5 recover to >1000 ohms
1185-1230 | 1078-1123 | Conductor 5 shorts to conductors 1, 2, 3, 4, 6 & 7 (259, 7, 26, 10, 54 & 7) | Sustained conductor-to-conductor shorts
1443 | 1336 | Power to Penlight is shutoff
Additional Observations
Observation 1 | It took 599 seconds (10 min.) from the start of Penlight heating for the first sustained shorting failure to occur.
Observation 2 | Although short to ground failures are indicated, it is uncertain what the paths to ground could have been.
Observation 3 | The cables did not ignite or burn during this test run. Nevertheless, damage to the cables was observed.
Observation 4 | The thermocoupled labeled Cable 2 failed during testing.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center
NOTE: The thermocouple labeled Cable 2 failed during testing.

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 30 |  |  | 2006-08-09 | 9:34
PE | 7-C | Air Drop
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C1-4 | Penlight Time | C1-5 | Penlight Time | C1-6 | Penlight Time | C1-7 | Penlight Time | C2-3 | Penlight Time | C2-4 | Penlight Time | C2-5 | Penlight Time | C2-6 | Penlight Time | C2-7 | Penlight Time | C3-4 | Penlight Time | C3-5 | Penlight Time | C3-6 | Penlight Time | C3-7 | Penlight Time | C4-5 | Penlight Time | C4-6 | Penlight Time | C4-7 | Penlight Time | C5-6 | Penlight Time | C5-7 | Penlight Time | C6-7 | Penlight Time | Minimums
-106.5 | 211201.9994 | -103.5 | 211201.9994 | -101 | 211201.9994 | -98 | 211201.9994 | -95.5 | 211201.9994 | -92.5 | 211201.9994 | -89.5 | 211201.9994 | -87 | 211201.9994 | -84 | 211201.9994 | -81.5 | 211201.9994 | -78.5 | 211201.9994 | -75.5 | 211201.9994 | -74 | 211201.9994 | -70 | 211201.9994 | -67.5 | 211201.9994 | -64.5 | 211201.9994 | -61.5 | 211201.9994 | -59 | 211201.9994 | -56 | 211201.9994 | -53.5 | 211201.9994 | -50.5 | 211201.9994 | -106.5 | 211201.9994
-47.5 | 211201.9994 | -45 | 211201.9994 | -42 | 211201.9994 | -39.5 | 211201.9994 | -36.5 | 211201.9994 | -33.5 | 211201.9994 | -31 | 211201.9994 | -28 | 211201.9994 | -25.5 | 211201.9994 | -22.5 | 211201.9994 | -19.5 | 211201.9994 | -17 | 211201.9994 | -14 | 211201.9994 | -11.5 | 211201.9994 | -8.5 | 211201.9994 | -5.5 | 211201.9994 | -3 | 211201.9994 | -1.3318e-07 | 211201.9994 | 2.5 | 211201.9994 | 5.5 | 211201.9994 | 8.5 | 211201.9994 | -47.5 | 211201.9994
11 | 211201.9994 | 14 | 211201.9994 | 16.5 | 211201.9994 | 19.5 | 211201.9994 | 22.5 | 211201.9994 | 25 | 211201.9994 | 28 | 211201.9994 | 30.5 | 211201.9994 | 33.5 | 211201.9994 | 36.5 | 211201.9994 | 39 | 211201.9994 | 42 | 211201.9994 | 44.5 | 211201.9994 | 47.5 | 211201.9994 | 50.5 | 211201.9994 | 53 | 211201.9994 | 56 | 211201.9994 | 58.5 | 211201.9994 | 61.5 | 211201.9994 | 64.5 | 211201.9994 | 67 | 211201.9994 | 11 | 211201.9994
70 | 211201.9994 | 72.5 | 211201.9994 | 75.5 | 211201.9994 | 78.5 | 211201.9994 | 81 | 211201.9994 | 84 | 211201.9994 | 86.5 | 211201.9994 | 89.5 | 211201.9994 | 92.5 | 211201.9994 | 95 | 211201.9994 | 98 | 211201.9994 | 100.5 | 211201.9994 | 103.5 | 211201.9994 | 106.5 | 211201.9994 | 109 | 211201.9994 | 112 | 211201.9994 | 114.5 | 211201.9994 | 117.5 | 211201.9994 | 120.5 | 211201.9994 | 123 | 211201.9994 | 126 | 211201.9994 | 70 | 211201.9994
128.5 | 211201.9994 | 131.5 | 211201.9994 | 134.5 | 211201.9994 | 137 | 211201.9994 | 140 | 211201.9994 | 142.5 | 211201.9994 | 145.5 | 211201.9994 | 148.5 | 211201.9994 | 151 | 211201.9994 | 154 | 211201.9994 | 156.5 | 211201.9994 | 159.5 | 211201.9994 | 162.5 | 211201.9994 | 165 | 211201.9994 | 168 | 211201.9994 | 170.5 | 211201.9994 | 173.5 | 211201.9994 | 176.5 | 211201.9994 | 179 | 211201.9994 | 182 | 211201.9994 | 184.5 | 211201.9994 | 128.5 | 211201.9994
187.5 | 211201.9994 | 190.5 | 211201.9994 | 193 | 211201.9994 | 196 | 211201.9994 | 198.5 | 211201.9994 | 201.5 | 211201.9994 | 204.5 | 211201.9994 | 207 | 211201.9994 | 210 | 211201.9994 | 212.5 | 211201.9994 | 215.5 | 211201.9994 | 218.5 | 211201.9994 | 221 | 211201.9994 | 224 | 211201.9994 | 226.5 | 105550.9988 | 229.5 | 211201.9994 | 232.5 | 211201.9994 | 235 | 211201.9994 | 238 | 211002.0947 | 240.5 | 211201.9994 | 243.5 | 211201.9994 | 187.5 | 105550.9988
246.5 | 211201.9994 | 249 | 211201.9994 | 252 | 211201.9994 | 254.5 | 211201.9994 | 257.5 | 211201.9994 | 260.5 | 211201.9994 | 263 | 211201.9994 | 266 | 211201.9994 | 268.5 | 211002.0947 | 271.5 | 211201.9994 | 274.5 | 211201.9994 | 277 | 211201.9994 | 280 | 211201.9994 | 282.5 | 211201.9994 | 285.5 | 211201.9994 | 288.5 | 211201.9994 | 291 | 211201.9994 | 294 | 211201.9994 | 296.5 | 211201.9994 | 299.5 | 211201.9994 | 302.5 | 211201.9994 | 246.5 | 211002.0947
305 | 211201.9994 | 308 | 211201.9994 | 310.5 | 211201.9994 | 313.5 | 211201.9994 | 316.5 | 211201.9994 | 319 | 211201.9994 | 321.5 | 211201.9994 | 324.5 | 211201.9994 | 327.5 | 211201.9994 | 330.5 | 211201.9994 | 333 | 211201.9994 | 336 | 211201.9994 | 338.5 | 211201.9994 | 341.5 | 211201.9994 | 344.5 | 211201.9994 | 346 | 211201.9994 | 349.5 | 211201.9994 | 352.5 | 211201.9994 | 355.5 | 211201.9994 | 358.5 | 211201.9994 | 361 | 211201.9994 | 305 | 211201.9994
364 | 211201.9994 | 366.5 | 211201.9994 | 369.5 | 211201.9994 | 372.5 | 211002.0947 | 375 | 211201.9994 | 378 | 211201.9994 | 380.5 | 211201.9994 | 383.5 | 211201.9994 | 386 | 211201.9994 | 389 | 211201.9994 | 392 | 211201.9994 | 394.5 | 211201.9994 | 397.5 | 211201.9994 | 400.5 | 211201.9994 | 403 | 211201.9994 | 406 | 211201.9994 | 408.5 | 211201.9994 | 411.5 | 211201.9994 | 414.5 | 211201.9994 | 417 | 211201.9994 | 420 | 211201.9994 | 364 | 211002.0947
422.5 | 211201.9994 | 425.5 | 211201.9994 | 428.5 | 211201.9994 | 431 | 211201.9994 | 434 | 211201.9994 | 436.5 | 211201.9994 | 439.5 | 211201.9994 | 442.5 | 211201.9994 | 445 | 211201.9994 | 448 | 211201.9994 | 450.5 | 211201.9994 | 453.5 | 211201.9994 | 456.5 | 211201.9994 | 459 | 211201.9994 | 462 | 211201.9994 | 464.5 | 211201.9994 | 467.5 | 211201.9994 | 470.5 | 211201.9994 | 473 | 211201.9994 | 476 | 211201.9994 | 478.5 | 211201.9994 | 422.5 | 211201.9994
481.5 | 211201.9994 | 484.5 | 211201.9994 | 487 | 211201.9994 | 490 | 211201.9994 | 492.5 | 211201.9994 | 495.5 | 211201.9994 | 498.5 | 211201.9994 | 501 | 211201.9994 | 503.5 | 211201.9994 | 506.5 | 211201.9994 | 509.5 | 211201.9994 | 512.5 | 211201.9994 | 515 | 211201.9994 | 518 | 211201.9994 | 520.5 | 211201.9994 | 523.5 | 211201.9994 | 526.5 | 211201.9994 | 529 | 211201.9994 | 531.5 | 211201.9994 | 534.5 | 211201.9994 | 537.5 | 211201.9994 | 481.5 | 211201.9994
540.5 | 211201.9994 | 543 | 211201.9994 | 545.5 | 211201.9994 | 548.5 | 211201.9994 | 551.5 | 211201.9994 | 554 | 211201.9994 | 557 | 211201.9994 | 560 | 211201.9994 | 562.5 | 211201.9994 | 565.5 | 211201.9994 | 568.5 | 211201.9994 | 571 | 211201.9994 | 574 | 211201.9994 | 576.5 | 211201.9994 | 579.5 | 211002.0947 | 582.5 | 211201.9994 | 585 | 211201.9994 | 588 | 105401.0947 | 590.5 | 211201.9994 | 593.5 | 211002.0947 | 596 | 211201.9994 | 540.5 | 105401.0947
599 | 3.3941 | 601.5 | 27.4224 | 604.5 | 15.5158 | 607.5 | 13914.4549 | 610 | 2.4331 | 613 | 12.5264 | 615.5 | 1.8181 | 618.5 | 13.985 | 621.5 | 29.6165 | 624 | 10.2783 | 627 | 16.5114 | 629.5 | 18.9154 | 632.5 | 4.683 | 635.5 | 20.0453 | 638.5 | 20.2676 | 641 | 14.4693 | 644 | 12.3417 | 646.5 | 21.6137 | 649.5 | 4.6995 | 652.5 | 11.0423 | 655 | 13.3394 | 599 | 1.8181
658 | 21.2758 | 660.5 | 7.5412 | 663.5 | 1.0443 | 666.5 | 2.0869 | 669 | 6.8963 | 671.5 | 12.1385 | 674.5 | 14.6472 | 677.5 | 17.555 | 680 | 3.7482 | 683 | 8.3034 | 685.5 | 9.4522 | 688.5 | 22.5737 | 691.5 | 17.0791 | 694 | 15.627 | 697 | 11.8991 | 700 | 7.0502 | 702.5 | 5.2585 | 705.5 | 3.7756 | 708 | 19.7017 | 711 | 20.8297 | 713.5 | 16.6741 | 658 | 1.0443
716.5 | 22.4974 | 719.5 | 23.8972 | 722 | 18.6655 | 725 | 2.5575 | 728 | 7.0438 | 730.5 | 22.1835 | 733.5 | 1.3028 | 736.5 | 7.7545 | 739 | 12231.3757 | 742 | 10.1628 | 744.5 | 19.1029 | 747.5 | 5.8428 | 750.5 | 13008.0843 | 753 | 4.1989 | 755.5 | 17.5304 | 758.5 | 11546.2198 | 761.5 | 5.6129 | 764 | 1.4716 | 767 | 11540.8164 | 769.5 | 13020.2763 | 772.5 | 16.7211 | 716.5 | 1.3028
775.5 | 6.7506 | 778.5 | 17.7946 | 781 | 29.8088 | 784 | 12237.0997 | 786.5 | 4.7879 | 789.5 | 15.176 | 792 | 5.1602 | 795 | 1.5444 | 797.5 | 12231.3757 | 800.5 | 22.044 | 803.5 | 7.4227 | 806 | 3.212 | 809 | 12225.4857 | 812 | 9.6792 | 814.5 | 19.3325 | 817.5 | 12231.2097 | 820.5 | 13.8707 | 823 | 9.8136 | 825.5 | 12242.8291 | 829 | 17417.8468 | 831.5 | 17.8817 | 775.5 | 1.5444
834 | 9.3725 | 837 | 5.7114 | 840 | 20.4731 | 842.5 | 12231.2097 | 845.5 | 12.7355 | 848.5 | 22.2921 | 851 | 6.0979 | 853.5 | 17.7791 | 856.5 | 12254.1698 | 859.5 | 11.6847 | 862 | 14.6978 | 865 | 8.7349 | 867.5 | 12231.2097 | 870.5 | 7.5331 | 873.5 | 0.66884 | 876 | 11578.8782 | 879 | 11.7809 | 881.5 | 6.9589 | 884.5 | 11551.7801 | 887.5 | 19019.2438 | 890.5 | 19.0349 | 834 | 0.66884
893 | 19.6186 | 895.5 | 8.3603 | 898.5 | 4.2633 | 901.5 | 16055.1371 | 904.5 | 11.0183 | 907 | 5.5191 | 909.5 | 1.7853 | 912.5 | 0.3198 | 915.5 | 11546.3791 | 918.5 | 17.1672 | 921 | 20.1539 | 923.5 | 5.632 | 926.5 | 12995.7387 | 929.5 | 18.9218 | 932 | 10.6284 | 935 | 12254.1588 | 937.5 | 4.9679 | 940.5 | 22.398 | 943.5 | 13038.6068 | 946 | 19019.4009 | 949 | 23.4481 | 893 | 0.3198
951.5 | 14.8324 | 954.5 | 16.2401 | 957.5 | 15.3633 | 960 | 11540.9832 | 963 | 1.3578 | 965.5 | 20.2481 | 968.5 | 8.2082 | 971.5 | 12.9537 | 974 | 13026.2325 | 977 | 10.4113 | 980 | 17.5796 | 982.5 | 19.0752 | 985.5 | 13032.491 | 988 | 5.4101 | 991 | 3.8643 | 993.5 | 12236.939 | 996.5 | 0.21422 | 999.5 | 5.0699 | 1002 | 17417.8468 | 1005 | 20931.0886 | 1007.5 | 2.6984 | 951.5 | 0.21422
1010.5 | 9.3879 | 1013.5 | 25.3335 | 1016 | 18.0487 | 1019 | 12225.4857 | 1021.5 | 22.8869 | 1024.5 | 17.203 | 1027.5 | 8.171 | 1030 | 18.3187 | 1033 | 12225.4857 | 1035.5 | 17.5058 | 1038.5 | 21.2207 | 1041.5 | 9.9812 | 1044 | 12231.3757 | 1047 | 8.4012 | 1049.5 | 14.0618 | 1052.5 | 16078.1734 | 1055.5 | 9.0073 | 1058 | 4.4769 | 1061 | 2273.8569 | 1063.5 | 17426.0476 | 1066.5 | 20.5888 | 1010.5 | 4.4769
1069.5 | 30.7313 | 1072 | 11.9982 | 1075 | 8.6665 | 1077.5 | 259.271 | 1080.5 | 20.9992 | 1083.5 | 14.6683 | 1086.5 | 13.5559 | 1089 | 21.9827 | 1091.5 | 6.5888 | 1094.5 | 4.1576 | 1097.5 | 8.8206 | 1100 | 12.6988 | 1102 | 25.746 | 1105.5 | 3.4554 | 1108.5 | 8.5936 | 1111.5 | 10.4038 | 1114 | 15.853 | 1116 | 262.2437 | 1119.5 | 54.4444 | 1122.5 | 6.8441 | 1125.5 | 126.0854 | 1069.5 | 3.4554
1128 | 19.3321 | 1131 | 13.2601 | 1133.5 | 14.3717 | 1136.5 | 11.3299 | 1139.5 | 34.5355 | 1142 | 16637.6119 | 1145 | 20.3107 | 1147.5 | 20.6301 | 1150.5 | 18938.2757 | 1153.5 | 17.5958 | 1156 | 349.8898 | 1159 | 13.0968 | 1161.5 | 5.4471 | 1164.5 | 15.9506 | 1167.5 | 164.6012 | 1170 | 0.28328 | 1173 | 4.0374 | 1175.5 | 326.1431 | 1178.5 | 3.6074 | 1181.5 | 1603.3073 | 1184 | 717.8301 | 1128 | 0.28328
1187 | 4.4508 | 1189.5 | 3.078 | 1192.5 | 1.6049 | 1195.5 | 18.6858 | 1198 | 25.6868 | 1201 | 14.9791 | 1203.5 | 15.7385 | 1206.5 | 15.7482 | 1209.5 | 15.2184 | 1212 | 13.4463 | 1215 | 2.8993 | 1217.5 | 19.3746 | 1220.5 | 1.4644 | 1223.5 | 17.2527 | 1226 | 17.4955 | 1229 | 15.2979 | 1231.5 | 13.9485 | 1234.5 | 19.8286 | 1237.5 | 8.2093 | 1240 | 10.5688 | 1243 | 27.0374 | 1187 | 1.4644
1245.5 | 7.7712 | 1249 | 4.6254 | 1251.5 | 3.8403 | 1254 | 18.7475 | 1257 | 22.4975 | 1259.5 | 5.2779 | 1262.5 | 6.1442 | 1265.5 | 3.187 | 1268 | 12.4567 | 1271 | 18.927 | 1273.5 | 1.0557 | 1276.5 | 12.7608 | 1279.5 | 12.4768 | 1282 | 32.2684 | 1285 | 17.8459 | 1287.5 | 14.016 | 1290.5 | 7.1495 | 1293.5 | 19.4968 | 1296 | 21.6477 | 1299 | 25.7891 | 1301.5 | 9.4667 | 1245.5 | 1.0557
1304.5 | 29.5097 | 1307.5 | 11.7742 | 1310 | 3.8961 | 1313 | 17.3669 | 1315.5 | 4.0983 | 1318.5 | 3.5195 | 1321.5 | 23.3019 | 1324 | 2.3641 | 1327 | 6.5206 | 1329.5 | 10.603 | 1332.5 | 18.9384 | 1335.5 | 6.7769 | 1338 | 19.144 | 1341 | 2.7201 | 1343.5 | 18.3839 | 1346.5 | 19.3758 | 1349.5 | 10.7235 | 1352 | 11.7817 | 1355 | 27.1983 | 1357.5 | 13.1954 | 1360.5 | 1.8323 | 1304.5 | 1.8323
1363.5 | 24.39 | 1366 | 1.7591 | 1369 | 14.1136 | 1371.5 | 27.0725 | 1374.5 | 20.3402 | 1377.5 | 4724.2049 | 1380 | 2.3723 | 1383 | 18.2888 | 1385.5 | 1.8183 | 1388.5 | 3.6974 | 1391.5 | 39.9846 | 1394 | 12.3115 | 1397 | 22.5507 | 1399.5 | 14.786 | 1402.5 | 13.9872 | 1405.5 | 16.3481 | 1408 | 10.9146 | 1411 | 20.633 | 1413.5 | 10.6102 | 1416.5 | 27.2133 | 1419.5 | 10.7978 | 1363.5 | 1.7591
1422 | 20.1814 | 1425 | 19.9599 | 1427.5 | 10.6959 | 1430.5 | 29.9464 | 1433.5 | 7.5403 | 1436 | 15.3853 | 1439 | 8.9549 | 1441.5 | 4.2127 | 1444.5 | 19.2435 | 1447.5 | 16.0839 | 1450 | 16.2971 | 1453 | 12.719 | 1455.5 | 29.7855 | 1458.5 | 3.2862 | 1461.5 | 26.2296 | 1464 | 17.3485 | 1467 | 21.305 | 1469 | 7.522 | 1472.5 | 0.40124 | 1475.5 | 3.4292 | 1478 | 33.9056 | 1422 | 0.40124
1481 | 4.1444 | 1483.5 | 9.7085 | 1486.5 | 9.3785 | 1489.5 | 20.6597 | 1492 | 8.4391 | 1495 | 8.9584 | 1497.5 | 5.7558 | 1500.5 | 5.8777 | 1503.5 | 10.2429 | 1506 | 24.3576 | 1509 | 29.7439 | 1511.5 | 19.3743 | 1514.5 | 10.3979 | 1517.5 | 10.8236 | 1520 | 11.3833 | 1523 | 3.5591 | 1525.5 | 4.4757 | 1528.5 | 14.2173 | 1531.5 | 14.5116 | 1534 | 11.2404 | 1537 | 2.831 | 1481 | 2.831
1539.5 | 12.1355 | 1542.5 | 11.0056 | 1545.5 | 14.6465 | 1548 | 9.5364 | 1551 | 8.4936 | 1553.5 | 19.6194 | 1556.5 | 20.6031 | 1559.5 | 15.257 | 1562 | 5.4356 | 1565 | 1.8763 | 1567.5 | 30.1802 | 1570.5 | 28.4488 | 1573.5 | 24.0766 | 1576 | 0.97476 | 1579 | 10.4967 | 1581.5 | 8.955 | 1584.5 | 11.9067 | 1587.5 | 7.4631 | 1590 | 14.9022 | 1593 | 17.5878 | 1595.5 | 2.3257 | 1539.5 | 0.97476
1598.5 | 14.2566 | 1601.5 | 0.88866 | 1604 | 15.6643 | 1607 | 20.2038 | 1609.5 | 18.1764 | 1612.5 | 14.6947 | 1615.5 | 27.8203 | 1618 | 20.7425 | 1621 | 24.8473 | 1623.5 | 5.9997 | 1626.5 | 19.775 | 1629.5 | 1.4618 | 1632 | 3.2337 | 1635 | 13.8344 | 1637.5 | 21.9402 | 1640.5 | 14.5816 | 1643.5 | 9.6016 | 1646 | 11.394 | 1649 | 9.2947 | 1651.5 | 15.0223 | 1654.5 | 7.6666 | 1598.5 | 0.88866
1657.5 | 5.3466 | 1660 | 0.91474 | 1663 | 9.7247 | 1665.5 | 26.0915 | 1669 | 14.7083 | 1671.5 | 11.3767 | 1674 | 28.2942 | 1677 | 18.5024 | 1679.5 | 20.7184 | 1682.5 | 15.2888 | 1685.5 | 13.3 | 1688 | 9.3773 | 1691 | 20.6521 | 1693.5 | 19.143 | 1696.5 | 10.5414 | 1699.5 | 25.3469 | 1702 | 29.7865 | 1704.5 | 29.2119 | 1707.5 | 17.3178 | 1710.5 | 5.9861 | 1713.5 | 9.4436 | 1657.5 | 0.91474
1716 | 1.1784 | 1719 | 16.2222 | 1721.5 | 16.6746 | 1724.5 | 15.2229 | 1727.5 | 17.4565 | 1730 | 6.7305 | 1733 | 3.6129 | 1735.5 | 16.7102 | 1738.5 | 3.645 | 1741.5 | 2.4449 | 1744 | 7.1971 | 1747 | 10.4153 | 1749.5 | 14.6052 | 1752.5 | 13.3191 | 1755 | 3.5838 | 1758 | 19.4163 | 1760.5 | 15.7485 | 1763.5 | 14.5419 | 1766.5 | 0.080662 | 1769.5 | 10.9497 | 1772 | 11.9332 | 1716 | 0.080662
1775 | 3.3962 | 1777.5 | 32.4209 | 1780.5 | 20.8999 | 1783.5 | 27.6723 | 1786 | 21.7124 | 1789 | 4.8718 | 1791.5 | 37.5107 | 1794.5 | 36.94 | 1797.5 | 9.0926 | 1800 | 18.7539 | 1803 | 13.2674 | 1805.5 | 9.6738 | 1808.5 | 4.8329 | 1811.5 | 21.6089 | 1814 | 16.2854 | 1817 | 2.4869 | 1819.5 | 3.1391 | 1822.5 | 26.6223 | 1825.5 | 2.2228 | 1828 | 5.861 | 1830.5 | 25.1365 | 1775 | 2.2228
1833.5 | 17.2041 | 1836.5 | 21.726 | 1839 | 20.75 | 1842 | 16.4599 | 1844.5 | 12.7202 | 1847.5 | 11.7712 | 1850.5 | 16.381 | 1853.5 | 2.9219 | 1856 | 6.9576 | 1859 | 4.6129 | 1861.5 | 17.6817 | 1864.5 | 19.0355 | 1867.5 | 1.6248 | 1870 | 21.35 | 1873 | 9.0741 | 1875.5 | 10.5462 | 1878.5 | 27.5713 | 1881.5 | 0.0013683 | 1884 | 1.5112 | 1886.5 | 12.5173 | 1889.5 | 29.9045 | 1833.5 | 0.0013683

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 30 |  |  | 2006-08-09 | 9:34
PE | 7-C | Air Drop
325 C | 7.2 kW/m2
Penlight Penlight Penlight Time | C1-G |  | Penlight Penlight Penlight Time | C2-G | Penlight Penlight Penlight Time | C3-G | Penlight Penlight Penlight Time | C4-G | Penlight Penlight Penlight Time | C5-G | Penlight Penlight Penlight Time | C6-G | Penlight Penlight Penlight Time | C7-G | Penlight Penlight Penlight Time | Minimums Overall
-99.5 | 211202 |  | -87.8333 | 211202 | -80 | 211202 | -74.75 | 211202 | -71.6667 | 211202 | -69.1667 | 211202 | -66.9167 | 211202 | -99.5 | 211202
-40.6667 | 211202 |  | -29 | 211202 | -21.1667 | 211202 | -15.9167 | 211202 | -12.75 | 211202 | -10.4167 | 211202 | -7.9167 | 211202 | -40.6667 | 211202
18.0833 | 211202 |  | 29.75 | 211202 | 37.75 | 211202 | 42.75 | 211202 | 46.0833 | 211202 | 48.5 | 211202 | 50.75 | 211202 | 18.0833 | 211202
76.9167 | 211202 |  | 88.5833 | 211202 | 96.4167 | 211202 | 101.5833 | 211202 | 105 | 211202 | 107.25 | 211202 | 109.5833 | 211202 | 76.9167 | 211202
135.6667 | 211202 |  | 147.3333 | 211202 | 155.3333 | 211202 | 160.5 | 211202 | 163.6667 | 211202 | 166 | 211202 | 168.3333 | 211202 | 135.6667 | 211202
194.5 | 211202 |  | 206.1667 | 211202 | 214.1667 | 105551 | 219.25 | 211202 | 222.5 | 211202 | 224.8333 | 211202 | 227.0833 | 211202 | 194.5 | 105551
253.3333 | 211202 |  | 265 | 211202 | 272.8333 | 211202 | 278.0833 | 211202 | 281.25 | 211202 | 283.5833 | 211202 | 286.0833 | 211202 | 253.3333 | 211202
312.0833 | 211202 |  | 323.6667 | 211202 | 331.6667 | 211202 | 336.5 | 211202 | 339.9167 | 211202 | 342.4167 | 211202 | 344.75 | 211202 | 312.0833 | 211202
370.9167 | 211202 |  | 382.5 | 211202 | 390.4167 | 211202 | 395.5833 | 211202 | 398.9167 | 211202 | 401.25 | 211202 | 403.5833 | 211202 | 370.9167 | 211202
429.6667 | 211202 |  | 441.3333 | 211202 | 449.3333 | 211202 | 454.5 | 211202 | 457.6667 | 211202 | 460 | 211202 | 462.3333 | 211202 | 429.6667 | 211202
488.5 | 211202 |  | 500.0833 | 211202 | 508.1667 | 211202 | 513.25 | 211202 | 516.3333 | 211202 | 518.75 | 211202 | 521.0833 | 211202 | 488.5 | 211202
547.1667 | 211202 |  | 559 | 211202 | 566.8333 | 211202 | 572 | 211202 | 575.25 | 211202 | 577.5 | 3741.8545 | 579.9167 | 211202 | 547.1667 | 3741.8545
605.9167 | 148.465 |  | 617.5833 | 66.3377 | 625.5 | 166.8169 | 630.6667 | 949.6733 | 634.0833 | 165.2843 | 636.3333 | 86.2032 | 638.75 | 329.9508 | 605.9167 | 66.3377
664.8333 | 46.7935 |  | 676.4167 | 38.2129 | 684.3333 | 59.5751 | 689.5833 | 201.5144 | 692.8333 | 34.523 | 695 | 59.9427 | 697.3333 | 116.4651 | 664.8333 | 34.523
723.5833 | 82.6723 |  | 735.3333 | 503.0247 | 743.25 | 46.9532 | 748.3333 | 56.5929 | 751.5833 | 353.3311 | 754 | 107.6396 | 756.0833 | 74.0784 | 723.5833 | 46.9532
782.5 | 391.5285 |  | 794 | 601.6948 | 802 | 165.0379 | 807.1667 | 86.2679 | 810.4167 | 15175.5076 | 812.75 | 446.2929 | 815.1667 | 71.8705 | 782.5 | 71.8705
841.25 | 40.8524 |  | 852.75 | 306.1279 | 860.75 | 33.2424 | 865.8333 | 100.0588 | 869.0833 | 14170.6579 | 871.5833 | 81.2645 | 873.9167 | 523.8785 | 841.25 | 33.2424
900 | 70.074 |  | 911.6667 | 128.01 | 919.4167 | 86.7434 | 924.5833 | 148.3565 | 928 | 15175.4992 | 930.4167 | 241.7017 | 932.5833 | 460.299 | 900 | 70.074
958.6667 | 18.7396 |  | 970.4167 | 54.8717 | 978.3333 | 59.3412 | 983.5 | 38.4885 | 986.6667 | 14186.8 | 989 | 20.4599 | 991.4167 | 224.5137 | 958.6667 | 18.7396
1017.5 | 68.7344 |  | 1029.1667 | 87.7829 | 1037.1667 | 126.5847 | 1042.25 | 32.0895 | 1045.5 | 11459.3008 | 1047.8333 | 73.0226 | 1050.0833 | 26.7085 | 1017.5 | 26.7085
1076.3333 | 135.8165 |  | 1088.0833 | 332.4967 | 1095.75 | 177.0357 | 1100.9167 | 65.2479 | 1104.0833 | 84.6427 | 1106.5833 | 335.6312 | 1108.9167 | 733.6882 | 1076.3333 | 65.2479
1135.0833 | 100.2853 |  | 1146.75 | 1281.0829 | 1154.75 | 127.1447 | 1159.75 | 1647.0177 | 1163.0833 | 82.2369 | 1165.5 | 958.6498 | 1167.75 | 1986.4507 | 1135.0833 | 82.2369
1193.9167 | 23.2774 |  | 1205.5833 | 18.1441 | 1213.4167 | 326.1441 | 1218.5833 | 212.9226 | 1222 | 321.0223 | 1224.25 | 196.2853 | 1226.5833 | 290.4526 | 1193.9167 | 18.1441
1252.75 | 29.1765 |  | 1264.3333 | 160.6269 | 1272.4167 | 288.1544 | 1277.5 | 34.625 | 1280.6667 | 207.3215 | 1283 | 134.6469 | 1285.3333 | 129.6802 | 1252.75 | 29.1765
1311.5 | 175.4695 |  | 1323.1667 | 72.4453 | 1331.1667 | 229.5828 | 1336.25 | 82.7927 | 1339.5 | 384.5354 | 1341.8333 | 293.1158 | 1344.0833 | 205.0398 | 1311.5 | 72.4453
1370.3333 | 48.6044 |  | 1382 | 67.4383 | 1389.8333 | 54.8115 | 1395.0833 | 66.6348 | 1398.25 | 326.7846 | 1400.5833 | 78.4404 | 1403.0833 | 288.9641 | 1370.3333 | 48.6044
1429.0833 | 188.4598 |  | 1440.75 | 92.1435 | 1448.75 | 265.3914 | 1453.6667 | 86.1654 | 1457.0833 | 400.1357 | 1459.5 | 107.2518 | 1461.6667 | 150.2545 | 1429.0833 | 86.1654
1487.9167 | 56.427 |  | 1499.5833 | 80.6952 | 1507.4167 | 72.9677 | 1512.5833 | 20.6708 | 1516 | 53.3959 | 1518.25 | 26.4222 | 1520.5833 | 39.7282 | 1487.9167 | 20.6708
1546.6667 | 95.9928 |  | 1558.3333 | 35.1854 | 1566.3333 | 209.3854 | 1571.5 | 81.3149 | 1574.6667 | 43.4371 | 1577 | 106.7337 | 1579.3333 | 433.8586 | 1546.6667 | 35.1854
1605.5 | 46.4855 |  | 1617.1667 | 220.8009 | 1625.1667 | 5.5524 | 1630.25 | 7.1261 | 1633.5 | 43.2366 | 1635.8333 | 402.6825 | 1638.0833 | 661.2554 | 1605.5 | 5.5524
1664.4167 | 18.5287 |  | 1676 | 398.5058 | 1683.8333 | 18.6574 | 1689 | 43.4164 | 1692.25 | 114.1642 | 1694.6667 | 91.1181 | 1697 | 99.0695 | 1664.4167 | 18.5287
1723.0833 | 33.5512 |  | 1734.75 | 36.2531 | 1742.6667 | 39.5088 | 1747.6667 | 88.0851 | 1751.0833 | 310.9166 | 1753.4167 | 360.4901 | 1755.6667 | 45.4233 | 1723.0833 | 33.5512
1781.9167 | 16.6606 |  | 1793.5833 | 13.1604 | 1801.4167 | 194.7393 | 1806.5833 | 383.7906 | 1810 | 45.8546 | 1812.1667 | 51.1404 | 1814.5 | 40.9885 | 1781.9167 | 13.1604
1840.5 | 405.8672 |  | 1852.3333 | 30.2294 | 1860.3333 | 50.5498 | 1865.4167 | 36.2187 | 1868.5833 | 66.4208 | 1870.9167 | 1062.9514 | 1873.25 | 66.357 | 1840.5 | 30.2294

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -107 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.7 | 27.9
1 | -106 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.7 | 27.9
2 | -105 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
3 | -104 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
4 | -103 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
5 | -102 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
6 | -101 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
7 | -100 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
8 | -99 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
9 | -98 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
10 | -97 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
11 | -96 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
12 | -95 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
13 | -94 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
14 | -93 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
15 | -92 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
16 | -91 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
17 | -90 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
18 | -89 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
19 | -88 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
20 | -87 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
21 | -86 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
22 | -85 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
23 | -84 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
24 | -83 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
25 | -82 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
26 | -81 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
27 | -80 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
28 | -79 | 23 | 28.8 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
29 | -78 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
30 | -77 | 23 | 28.9 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
31 | -76 | 23 | 28.8 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
32 | -75 | 23 | 28.8 | 29.1 | 29.2 | 28.6 | 28.6 | 27.9
33 | -74 | 23 | 28.8 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
34 | -73 | 23 | 28.8 | 29.1 | 29.2 | 28.6 | 28.6 | 27.9
35 | -72 | 23 | 28.8 | 29.1 | 29.2 | 28.7 | 28.6 | 27.9
36 | -71 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.9
37 | -70 | 23 | 28.8 | 29.1 | 29.2 | 28.6 | 28.6 | 27.9
38 | -69 | 23 | 28.8 | 29.1 | 29.2 | 28.6 | 28.6 | 27.9
39 | -68 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.9
40 | -67 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.9
41 | -66 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
42 | -65 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
43 | -64 | 23 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
44 | -63 | 22.9 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
45 | -62 | 22.9 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
46 | -61 | 23 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
47 | -60 | 22.9 | 28.8 | 29.1 | 29.1 | 28.6 | 28.6 | 27.8
48 | -59 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
49 | -58 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
50 | -57 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
51 | -56 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
52 | -55 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
53 | -54 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
54 | -53 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
55 | -52 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
56 | -51 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
57 | -50 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
58 | -49 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
59 | -48 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
60 | -47 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
61 | -46 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
62 | -45 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.6 | 27.8
63 | -44 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
64 | -43 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
65 | -42 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
66 | -41 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
67 | -40 | 22.9 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
68 | -39 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
69 | -38 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
70 | -37 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.8
71 | -36 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
72 | -35 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
73 | -34 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
74 | -33 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
75 | -32 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
76 | -31 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
77 | -30 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
78 | -29 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
79 | -28 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
80 | -27 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
81 | -26 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
82 | -25 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
83 | -24 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
84 | -23 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
85 | -22 | 22.8 | 28.8 | 29 | 29.1 | 28.6 | 28.5 | 27.7
86 | -21 | 22.8 | 28.8 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
87 | -20 | 22.8 | 28.8 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
88 | -19 | 22.8 | 28.8 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
89 | -18 | 22.8 | 28.8 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
90 | -17 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
91 | -16 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
92 | -15 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
93 | -14 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
94 | -13 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
95 | -12 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
96 | -11 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
97 | -10 | 22.8 | 28.7 | 28.9 | 29 | 28.6 | 28.5 | 27.7
98 | -9 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
99 | -8 | 22.8 | 28.7 | 28.9 | 29 | 28.6 | 28.5 | 27.7
100 | -7 | 22.8 | 28.7 | 28.9 | 29 | 28.6 | 28.5 | 27.7
101 | -6 | 22.8 | 28.7 | 28.9 | 29 | 28.6 | 28.5 | 27.7
102 | -5 | 22.8 | 28.7 | 28.9 | 29.1 | 28.6 | 28.5 | 27.7
103 | -4 | 22.8 | 28.8 | 28.8 | 29.1 | 28.6 | 28.5 | 27.7
104 | -3 | 22.7 | 28.8 | 28.8 | 29.1 | 28.6 | 28.5 | 27.7
105 | -2 | 22.9 | 28.8 | 28.8 | 29.1 | 28.6 | 28.5 | 27.7
106 | -1 | 23.6 | 28.8 | 28.8 | 29.1 | 28.6 | 28.5 | 27.7
107 | 0 | 24.8 | 28.8 | 28.8 | 29.1 | 28.6 | 28.5 | 27.7
108 | 1 | 26.6 | 28.8 | 28.8 | 29.1 | 28.6 | 28.6 | 27.7
109 | 2 | 29 | 28.8 | 28.8 | 29.1 | 28.6 | 28.6 | 27.8
110 | 3 | 31.8 | 28.7 | 28.8 | 29.1 | 28.6 | 28.6 | 27.8
111 | 4 | 35 | 28.8 | 28.8 | 29.1 | 28.6 | 28.7 | 27.9
112 | 5 | 38.5 | 28.8 | 28.8 | 29 | 28.6 | 28.8 | 27.9
113 | 6 | 42.2 | 28.8 | 28.8 | 29.1 | 28.6 | 28.8 | 28
114 | 7 | 46.3 | 28.8 | 28.8 | 29.1 | 28.7 | 28.9 | 28.1
115 | 8 | 50.5 | 28.8 | 28.8 | 29.1 | 28.7 | 29.1 | 28.2
116 | 9 | 55 | 28.8 | 28.8 | 29.1 | 28.7 | 29.3 | 28.3
117 | 10 | 59.6 | 28.8 | 28.8 | 29.1 | 28.8 | 29.4 | 28.5
118 | 11 | 64.3 | 28.8 | 28.8 | 29.1 | 28.8 | 29.7 | 28.7
119 | 12 | 69.2 | 28.9 | 28.8 | 29.1 | 28.9 | 29.9 | 28.8
120 | 13 | 74.2 | 28.9 | 28.8 | 29.1 | 28.9 | 30.2 | 29
121 | 14 | 79.4 | 28.9 | 28.8 | 29.1 | 29 | 30.6 | 29.2
122 | 15 | 84.8 | 29 | 28.9 | 29.1 | 29.1 | 31 | 29.5
123 | 16 | 90.2 | 29 | 28.9 | 29.1 | 29.2 | 31.4 | 29.7
124 | 17 | 95.7 | 29.1 | 28.9 | 29.2 | 29.3 | 31.8 | 30
125 | 18 | 101.3 | 29.1 | 28.9 | 29.2 | 29.4 | 32.2 | 30.4
126 | 19 | 106.9 | 29.2 | 28.9 | 29.2 | 29.5 | 32.7 | 30.7
127 | 20 | 112.7 | 29.3 | 28.9 | 29.3 | 29.7 | 33.2 | 31.1
128 | 21 | 118.5 | 29.4 | 28.9 | 29.3 | 29.9 | 33.7 | 31.5
129 | 22 | 124.4 | 29.5 | 28.9 | 29.3 | 30 | 34.2 | 31.9
130 | 23 | 130.3 | 29.6 | 28.9 | 29.4 | 30.2 | 34.9 | 32.3
131 | 24 | 136.3 | 29.7 | 29 | 29.4 | 30.4 | 35.7 | 32.8
132 | 25 | 142.3 | 29.9 | 29 | 29.5 | 30.7 | 36.4 | 33.3
133 | 26 | 148.3 | 30 | 29 | 29.6 | 30.9 | 37.2 | 33.9
134 | 27 | 154.3 | 30.2 | 29.1 | 29.6 | 31.2 | 38 | 34.5
135 | 28 | 160.3 | 30.4 | 29.1 | 29.7 | 31.5 | 38.9 | 35.2
136 | 29 | 166.3 | 30.5 | 29.2 | 29.8 | 31.8 | 40 | 35.8
137 | 30 | 172.4 | 30.7 | 29.2 | 29.9 | 32.1 | 41 | 36.5
138 | 31 | 178.5 | 31 | 29.3 | 30 | 32.5 | 42.2 | 37.2
139 | 32 | 184.6 | 31.2 | 29.3 | 30.1 | 32.8 | 43.3 | 38
140 | 33 | 190.7 | 31.5 | 29.4 | 30.2 | 33.2 | 44.4 | 38.7
141 | 34 | 196.9 | 31.7 | 29.4 | 30.3 | 33.6 | 45.7 | 39.6
142 | 35 | 203 | 32 | 29.5 | 30.5 | 34.1 | 47 | 40.5
143 | 36 | 209.2 | 32.3 | 29.6 | 30.6 | 34.6 | 48.5 | 41.4
144 | 37 | 215.3 | 32.7 | 29.7 | 30.7 | 35.1 | 49.8 | 42.4
145 | 38 | 221.5 | 33 | 29.8 | 30.9 | 35.6 | 51.2 | 43.4
146 | 39 | 227.6 | 33.4 | 29.9 | 31.1 | 36.1 | 52.6 | 44.4
147 | 40 | 233.7 | 33.7 | 30 | 31.2 | 36.7 | 53.9 | 45.4
148 | 41 | 239.9 | 34.1 | 30.1 | 31.4 | 37.3 | 55.4 | 46.6
149 | 42 | 246 | 34.6 | 30.2 | 31.6 | 37.9 | 57.1 | 47.8
150 | 43 | 252.1 | 35 | 30.4 | 31.8 | 38.6 | 58.6 | 49
151 | 44 | 258.2 | 35.5 | 30.5 | 32 | 39.3 | 60.2 | 50.3
152 | 45 | 264.3 | 36 | 30.7 | 32.3 | 40 | 61.9 | 51.7
153 | 46 | 270.4 | 36.5 | 30.8 | 32.5 | 40.7 | 63.5 | 53
154 | 47 | 276.5 | 37 | 31 | 32.8 | 41.5 | 65.1 | 54.4
155 | 48 | 282.5 | 37.6 | 31.2 | 33 | 42.3 | 67 | 55.8
156 | 49 | 288.6 | 38.2 | 31.3 | 33.3 | 43.1 | 68.8 | 57.2
157 | 50 | 294.5 | 38.8 | 31.5 | 33.6 | 44 | 70.9 | 58.6
158 | 51 | 300.5 | 39.5 | 31.7 | 33.9 | 44.9 | 72.9 | 60
159 | 52 | 306.3 | 40.1 | 31.9 | 34.3 | 45.8 | 74.9 | 61.6
160 | 53 | 311.8 | 40.8 | 32.1 | 34.6 | 46.8 | 76.8 | 63.2
161 | 54 | 316.8 | 41.5 | 32.3 | 35 | 47.8 | 78.9 | 64.7
162 | 55 | 321.6 | 42.2 | 32.6 | 35.3 | 48.8 | 81.1 | 66.5
163 | 56 | 326.1 | 43 | 32.9 | 35.7 | 49.8 | 83 | 68.1
164 | 57 | 330.3 | 43.8 | 33.2 | 36.1 | 50.9 | 84.9 | 69.9
165 | 58 | 334.3 | 44.6 | 33.5 | 36.5 | 51.9 | 87 | 71.6
166 | 59 | 337.9 | 45.4 | 33.8 | 36.9 | 53 | 89 | 73.3
167 | 60 | 341.2 | 46.2 | 34.1 | 37.3 | 54.2 | 91.1 | 74.9
168 | 61 | 344.1 | 47.1 | 34.4 | 37.8 | 55.3 | 93.1 | 76.6
169 | 62 | 346.8 | 48 | 34.8 | 38.2 | 56.4 | 95.1 | 78.1
170 | 63 | 349 | 48.8 | 35.2 | 38.7 | 57.6 | 97.1 | 79.7
171 | 64 | 351.1 | 49.7 | 35.6 | 39.2 | 58.8 | 98.8 | 81.2
172 | 65 | 352.7 | 50.7 | 36 | 39.7 | 59.9 | 100.6 | 82.6
173 | 66 | 354.2 | 51.6 | 36.4 | 40.2 | 61.1 | 102.2 | 84.1
174 | 67 | 355.4 | 52.6 | 36.8 | 40.7 | 62.4 | 104 | 85.5
175 | 68 | 356.4 | 53.5 | 37.2 | 41.2 | 63.6 | 105.9 | 87
176 | 69 | 357.3 | 54.5 | 37.7 | 41.8 | 64.8 | 107.6 | 88.4
177 | 70 | 358 | 55.5 | 38.1 | 42.3 | 66.1 | 109.3 | 89.7
178 | 71 | 358.6 | 56.5 | 38.6 | 42.9 | 67.3 | 111 | 91.1
179 | 72 | 359.1 | 57.5 | 39.1 | 43.5 | 68.6 | 112.7 | 92.4
180 | 73 | 359.4 | 58.5 | 39.6 | 44.1 | 69.9 | 114.4 | 93.8
181 | 74 | 359.7 | 59.5 | 40.1 | 44.6 | 71.1 | 116 | 95.1
182 | 75 | 359.9 | 60.5 | 40.6 | 45.2 | 72.4 | 117.5 | 96.3
183 | 76 | 359.9 | 61.5 | 41.1 | 45.8 | 73.7 | 119 | 97.5
184 | 77 | 359.9 | 62.5 | 41.6 | 46.4 | 75 | 120.5 | 98.8
185 | 78 | 359.8 | 63.5 | 42.2 | 47 | 76.3 | 121.8 | 99.9
186 | 79 | 359.7 | 64.5 | 42.7 | 47.7 | 77.6 | 123.1 | 101.1
187 | 80 | 359.6 | 65.5 | 43.3 | 48.3 | 78.9 | 124.3 | 102.3
188 | 81 | 359.4 | 66.5 | 43.8 | 48.9 | 80.3 | 125.6 | 103.5
189 | 82 | 359.2 | 67.5 | 44.4 | 49.5 | 81.6 | 126.9 | 104.6
190 | 83 | 358.9 | 68.5 | 45 | 50.2 | 82.9 | 128.1 | 105.8
191 | 84 | 358.6 | 69.5 | 45.6 | 50.8 | 84.2 | 129.4 | 106.9
192 | 85 | 358.3 | 70.4 | 46.2 | 51.4 | 85.4 | 130.6 | 108.1
193 | 86 | 357.9 | 71.4 | 46.7 | 52 | 86.7 | 131.7 | 109.3
194 | 87 | 357.6 | 72.4 | 47.4 | 52.7 | 88 | 132.8 | 110.4
195 | 88 | 357.2 | 73.4 | 48 | 53.3 | 89.3 | 133.9 | 111.4
196 | 89 | 356.9 | 74.3 | 48.7 | 54 | 90.5 | 135.1 | 112.6
197 | 90 | 356.5 | 75.3 | 49.4 | 54.6 | 91.8 | 136.1 | 113.7
198 | 91 | 356 | 76.2 | 50 | 55.3 | 93 | 137 | 114.7
199 | 92 | 355.5 | 77.1 | 50.6 | 55.9 | 94.3 | 137.8 | 115.7
200 | 93 | 355.1 | 78.1 | 51.2 | 56.5 | 95.5 | 138.7 | 116.7
201 | 94 | 354.7 | 79 | 51.9 | 57.2 | 96.7 | 139.6 | 117.7
202 | 95 | 354.2 | 79.9 | 52.5 | 57.8 | 98 | 140.4 | 118.6
203 | 96 | 353.7 | 80.8 | 53.1 | 58.5 | 99.2 | 141.2 | 119.5
204 | 97 | 353.3 | 81.7 | 53.7 | 59.1 | 100.4 | 142 | 120.3
205 | 98 | 352.9 | 82.6 | 54.4 | 59.8 | 101.6 | 142.9 | 121.1
206 | 99 | 352.4 | 83.5 | 55 | 60.4 | 102.8 | 143.7 | 121.9
207 | 100 | 352 | 84.3 | 55.7 | 61.1 | 104 | 144.6 | 122.6
208 | 101 | 351.5 | 85.2 | 56.3 | 61.7 | 105.2 | 145.3 | 123.3
209 | 102 | 351 | 86 | 57 | 62.4 | 106.4 | 145.9 | 124
210 | 103 | 350.5 | 86.9 | 57.7 | 63 | 107.6 | 146.5 | 124.6
211 | 104 | 350 | 87.7 | 58.2 | 63.6 | 108.8 | 147.3 | 125.2
212 | 105 | 349.5 | 88.5 | 59.1 | 64.3 | 110 | 148 | 125.9
213 | 106 | 349 | 89.4 | 59.9 | 64.9 | 111.2 | 148.8 | 126.4
214 | 107 | 348.5 | 90.2 | 60.5 | 65.5 | 112.4 | 149.5 | 127
215 | 108 | 348 | 91 | 61.2 | 66.2 | 113.6 | 150.2 | 127.5
216 | 109 | 347.5 | 91.8 | 61.8 | 66.8 | 114.7 | 150.9 | 128.1
217 | 110 | 346.9 | 92.5 | 62.4 | 67.4 | 115.9 | 151.5 | 128.6
218 | 111 | 346.4 | 93.3 | 63 | 68.1 | 117.1 | 152.1 | 129.2
219 | 112 | 345.8 | 94 | 63.7 | 68.7 | 118.2 | 152.8 | 129.8
220 | 113 | 345.3 | 94.8 | 64.3 | 69.3 | 119.3 | 153.5 | 130.3
221 | 114 | 344.8 | 95.5 | 64.9 | 69.9 | 120.4 | 154.1 | 130.8
222 | 115 | 344.3 | 96.3 | 65.6 | 70.5 | 121.5 | 154.6 | 131.4
223 | 116 | 343.8 | 97 | 66.2 | 71.1 | 122.6 | 155.1 | 131.9
224 | 117 | 343.2 | 97.7 | 66.8 | 71.8 | 123.7 | 155.5 | 132.4
225 | 118 | 342.7 | 98.4 | 67.5 | 72.4 | 124.7 | 156 | 132.8
226 | 119 | 342.1 | 99.1 | 68.1 | 73 | 125.8 | 156.5 | 133.3
227 | 120 | 341.6 | 99.8 | 68.7 | 73.6 | 126.8 | 157 | 133.7
228 | 121 | 341 | 100.5 | 69.4 | 74.2 | 127.8 | 157.4 | 134.2
229 | 122 | 340.6 | 101.2 | 70 | 74.8 | 128.8 | 157.9 | 134.6
230 | 123 | 340 | 101.8 | 70.7 | 75.3 | 129.8 | 158.4 | 135.1
231 | 124 | 339.5 | 102.5 | 71.3 | 75.9 | 130.8 | 158.8 | 135.6
232 | 125 | 338.9 | 103.2 | 71.9 | 76.5 | 131.8 | 159.3 | 136
233 | 126 | 338.4 | 103.8 | 72.6 | 77.1 | 132.7 | 159.7 | 136.4
234 | 127 | 337.9 | 104.4 | 73.2 | 77.7 | 133.7 | 160.1 | 136.9
235 | 128 | 337.4 | 105.1 | 73.8 | 78.3 | 134.6 | 160.5 | 137.3
236 | 129 | 336.8 | 105.7 | 74.5 | 78.9 | 135.5 | 161 | 137.8
237 | 130 | 336.3 | 106.4 | 75.1 | 79.4 | 136.4 | 161.4 | 138.2
238 | 131 | 335.8 | 107 | 75.7 | 80 | 137.3 | 161.8 | 138.6
239 | 132 | 335.2 | 107.6 | 76.3 | 80.6 | 138.2 | 162.2 | 138.9
240 | 133 | 334.7 | 108.2 | 76.9 | 81.1 | 139.1 | 162.6 | 139.3
241 | 134 | 334.1 | 108.8 | 77.5 | 81.7 | 140 | 163 | 139.6
242 | 135 | 333.6 | 109.4 | 78.1 | 82.3 | 140.8 | 163.4 | 140
243 | 136 | 333.1 | 110 | 78.7 | 82.8 | 141.7 | 163.8 | 140.3
244 | 137 | 332.6 | 110.6 | 79.3 | 83.4 | 142.5 | 164.2 | 140.7
245 | 138 | 332.1 | 111.2 | 79.9 | 83.9 | 143.3 | 164.7 | 141
246 | 139 | 331.6 | 111.8 | 80.5 | 84.5 | 144.1 | 165 | 141.4
247 | 140 | 331.1 | 112.3 | 81.1 | 85.1 | 144.9 | 165.3 | 141.8
248 | 141 | 330.7 | 112.9 | 81.7 | 85.6 | 145.7 | 165.6 | 142.1
249 | 142 | 330.2 | 113.5 | 82.2 | 86.2 | 146.5 | 166 | 142.4
250 | 143 | 329.8 | 114 | 82.8 | 86.7 | 147.3 | 166.3 | 142.8
251 | 144 | 329.2 | 114.5 | 83.4 | 87.2 | 148 | 166.6 | 143
252 | 145 | 328.7 | 115.1 | 84 | 87.8 | 148.8 | 166.9 | 143.3
253 | 146 | 328.2 | 115.6 | 84.5 | 88.3 | 149.5 | 167.2 | 143.6
254 | 147 | 327.7 | 116.1 | 85.1 | 88.8 | 150.3 | 167.6 | 143.9
255 | 148 | 327.2 | 116.6 | 85.7 | 89.4 | 151 | 167.8 | 144.2
256 | 149 | 326.7 | 117.1 | 86.2 | 89.9 | 151.7 | 168.1 | 144.4
257 | 150 | 326.2 | 117.6 | 86.7 | 90.4 | 152.4 | 168.4 | 144.8
258 | 151 | 325.7 | 118.1 | 87.3 | 91 | 153.1 | 168.7 | 145
259 | 152 | 325.2 | 118.6 | 87.9 | 91.5 | 153.8 | 168.9 | 145.3
260 | 153 | 324.8 | 119.1 | 88.4 | 92 | 154.5 | 169.2 | 145.6
261 | 154 | 324.3 | 119.5 | 89 | 92.5 | 155.2 | 169.4 | 145.8
262 | 155 | 323.9 | 120 | 89.5 | 93 | 155.8 | 169.6 | 146
263 | 156 | 323.4 | 120.4 | 90 | 93.5 | 156.5 | 169.8 | 146.2
264 | 157 | 322.9 | 120.9 | 90.5 | 94.1 | 157.2 | 170 | 146.4
265 | 158 | 322.4 | 121.3 | 91 | 94.6 | 157.8 | 170.2 | 146.6
266 | 159 | 321.9 | 121.7 | 91.6 | 95.1 | 158.5 | 170.5 | 146.8
267 | 160 | 321.5 | 122.1 | 92.1 | 95.5 | 159.1 | 170.7 | 147
268 | 161 | 321 | 122.5 | 92.6 | 96 | 159.7 | 170.9 | 147.2
269 | 162 | 320.6 | 122.9 | 93 | 96.5 | 160.3 | 171.1 | 147.4
270 | 163 | 320.1 | 123.3 | 93.5 | 97 | 160.9 | 171.3 | 147.6
271 | 164 | 319.6 | 123.6 | 94 | 97.5 | 161.5 | 171.5 | 147.7
272 | 165 | 319.1 | 124 | 94.5 | 98 | 162.1 | 171.7 | 147.9
273 | 166 | 318.6 | 124.4 | 95 | 98.4 | 162.7 | 171.9 | 148
274 | 167 | 318.1 | 124.7 | 95.5 | 98.9 | 163.3 | 172.1 | 148.2
275 | 168 | 317.7 | 125.1 | 96 | 99.4 | 163.8 | 172.3 | 148.3
276 | 169 | 317.3 | 125.4 | 96.5 | 99.9 | 164.4 | 172.4 | 148.4
277 | 170 | 317 | 125.8 | 97 | 100.3 | 164.9 | 172.7 | 148.6
278 | 171 | 316.7 | 126.1 | 97.5 | 100.8 | 165.5 | 172.8 | 148.8
279 | 172 | 316.4 | 126.4 | 98 | 101.2 | 166 | 173 | 149
280 | 173 | 316.2 | 126.7 | 98.5 | 101.7 | 166.5 | 173.2 | 149.2
281 | 174 | 316.1 | 127 | 99 | 102.1 | 167.1 | 173.4 | 149.4
282 | 175 | 315.9 | 127.3 | 99.5 | 102.6 | 167.6 | 173.6 | 149.6
283 | 176 | 315.8 | 127.6 | 99.9 | 103 | 168.1 | 173.8 | 149.8
284 | 177 | 315.8 | 127.9 | 100.4 | 103.5 | 168.6 | 174 | 150
285 | 178 | 315.8 | 128.2 | 100.9 | 103.9 | 169.1 | 174.2 | 150.2
286 | 179 | 315.9 | 128.4 | 101.3 | 104.3 | 169.6 | 174.4 | 150.4
287 | 180 | 316 | 128.7 | 101.8 | 104.8 | 170.1 | 174.7 | 150.6
288 | 181 | 316.2 | 129 | 102.2 | 105.2 | 170.7 | 174.9 | 150.8
289 | 182 | 316.5 | 129.2 | 102.7 | 105.6 | 171.2 | 175.1 | 151
290 | 183 | 316.8 | 129.5 | 103.2 | 106 | 171.7 | 175.2 | 151.2
291 | 184 | 317.2 | 129.7 | 103.6 | 106.5 | 172.2 | 175.5 | 151.4
292 | 185 | 317.6 | 130 | 104 | 106.9 | 172.7 | 175.7 | 151.6
293 | 186 | 318 | 130.2 | 104.4 | 107.3 | 173.2 | 176 | 151.9
294 | 187 | 318.5 | 130.4 | 104.9 | 107.7 | 173.7 | 176.2 | 152.1
295 | 188 | 319 | 130.7 | 105.3 | 108.1 | 174.2 | 176.5 | 152.3
296 | 189 | 319.5 | 130.9 | 105.7 | 108.5 | 174.7 | 176.8 | 152.6
297 | 190 | 320 | 131.1 | 106.2 | 108.9 | 175.2 | 177.1 | 152.8
298 | 191 | 320.5 | 131.3 | 106.6 | 109.3 | 175.8 | 177.3 | 153.1
299 | 192 | 321 | 131.5 | 107.1 | 109.7 | 176.3 | 177.6 | 153.4
300 | 193 | 321.6 | 131.7 | 107.5 | 110.1 | 176.8 | 177.9 | 153.6
301 | 194 | 322.2 | 131.9 | 107.9 | 110.5 | 177.4 | 178.1 | 153.9
302 | 195 | 322.7 | 132 | 108.3 | 110.9 | 177.9 | 178.4 | 154.2
303 | 196 | 323.2 | 132.2 | 108.6 | 111.4 | 178.4 | 178.7 | 154.4
304 | 197 | 323.7 | 132.4 | 109 | 111.8 | 179 | 179 | 154.7
305 | 198 | 324.1 | 132.6 | 109.4 | 112.2 | 179.5 | 179.4 | 155
306 | 199 | 324.4 | 132.7 | 109.7 | 112.5 | 180.1 | 179.7 | 155.3
307 | 200 | 324.8 | 132.9 | 110.1 | 112.9 | 180.6 | 180 | 155.6
308 | 201 | 325.2 | 133 | 110.5 | 113.3 | 181.2 | 180.3 | 155.9
309 | 202 | 325.6 | 133.2 | 110.8 | 113.7 | 181.7 | 180.6 | 156.2
310 | 203 | 325.9 | 133.3 | 111.2 | 114.1 | 182.2 | 180.9 | 156.5
311 | 204 | 326.2 | 133.5 | 111.6 | 114.5 | 182.8 | 181.2 | 156.8
312 | 205 | 326.5 | 133.6 | 112 | 114.9 | 183.3 | 181.6 | 157
313 | 206 | 326.7 | 133.7 | 112.5 | 115.3 | 183.9 | 181.9 | 157.3
314 | 207 | 326.9 | 133.9 | 113 | 115.7 | 184.4 | 182.2 | 157.6
315 | 208 | 327.1 | 134 | 113.6 | 116.1 | 184.9 | 182.5 | 157.9
316 | 209 | 327.3 | 134.2 | 114.2 | 116.5 | 185.4 | 182.8 | 158.2
317 | 210 | 327.5 | 134.3 | 114.8 | 116.9 | 186 | 183.2 | 158.5
318 | 211 | 327.7 | 134.5 | 115.8 | 117.3 | 186.5 | 183.5 | 158.8
319 | 212 | 327.9 | 134.6 | 117 | 117.7 | 187 | 183.7 | 159
320 | 213 | 328 | 134.8 | 118.4 | 118.2 | 187.4 | 184.1 | 159.3
321 | 214 | 328.1 | 135 | 120.3 | 118.6 | 187.9 | 184.4 | 159.6
322 | 215 | 328.2 | 135.2 | 121.6 | 119 | 188.4 | 184.7 | 159.8
323 | 216 | 328.2 | 135.3 | 122.2 | 119.5 | 188.9 | 185 | 160.1
324 | 217 | 328.3 | 135.6 | 122.6 | 119.9 | 189.4 | 185.3 | 160.4
325 | 218 | 328.3 | 135.8 | 123.1 | 120.3 | 190 | 185.5 | 160.6
326 | 219 | 328.3 | 136 | 123.6 | 120.8 | 190.5 | 185.9 | 160.8
327 | 220 | 328.2 | 136.2 | 124.1 | 121.2 | 191 | 186.2 | 161.1
328 | 221 | 328.2 | 136.5 | 124.6 | 121.7 | 191.5 | 186.4 | 161.3
329 | 222 | 328.1 | 136.7 | 125.1 | 122.1 | 191.9 | 186.7 | 161.6
330 | 223 | 328.1 | 136.9 | 125.6 | 122.6 | 192.4 | 187 | 161.8
331 | 224 | 328 | 137.2 | 126.1 | 123 | 192.8 | 187.3 | 162
332 | 225 | 328 | 137.4 | 126.6 | 123.4 | 193.3 | 187.6 | 162.3
333 | 226 | 327.9 | 137.7 | 127.1 | 123.9 | 193.7 | 187.9 | 162.5
334 | 227 | 327.8 | 138 | 127.7 | 124.4 | 194.1 | 188.2 | 162.7
335 | 228 | 327.7 | 138.3 | 128.1 | 124.8 | 194.5 | 188.5 | 162.9
336 | 229 | 327.6 | 138.7 | 128.6 | 125.3 | 194.9 | 188.7 | 163.2
337 | 230 | 327.6 | 139 | 129.1 | 125.7 | 195.3 | 189 | 163.4
338 | 231 | 327.5 | 139.4 | 129.6 | 126.2 | 195.7 | 189.2 | 163.7
339 | 232 | 327.4 | 139.7 | 130.1 | 126.6 | 196 | 189.4 | 163.9
340 | 233 | 327.3 | 140.1 | 130.6 | 127.1 | 196.4 | 189.6 | 164.2
341 | 234 | 327.2 | 140.5 | 131.1 | 127.5 | 196.7 | 189.8 | 164.4
342 | 235 | 327.1 | 140.9 | 131.6 | 128 | 197.1 | 190 | 164.6
343 | 236 | 327 | 141.2 | 132 | 128.4 | 197.4 | 190.3 | 164.8
344 | 237 | 326.9 | 141.6 | 132.5 | 128.8 | 197.7 | 190.6 | 165
345 | 238 | 326.8 | 142 | 133 | 129.3 | 198 | 190.8 | 165.2
346 | 239 | 326.7 | 142.4 | 133.5 | 129.7 | 198.4 | 191 | 165.4
347 | 240 | 326.6 | 142.8 | 134 | 130.2 | 198.7 | 191.2 | 165.6
348 | 241 | 326.5 | 143.2 | 134.5 | 130.6 | 198.9 | 191.4 | 165.9
349 | 242 | 326.4 | 143.6 | 135 | 131.1 | 199.2 | 191.6 | 166.1
350 | 243 | 326.4 | 144 | 135.4 | 131.6 | 199.5 | 191.8 | 166.3
351 | 244 | 326.3 | 144.4 | 135.9 | 132 | 199.8 | 192 | 166.5
352 | 245 | 326.2 | 144.8 | 136.4 | 132.5 | 200.1 | 192.2 | 166.7
353 | 246 | 326.1 | 145.2 | 136.9 | 132.9 | 200.3 | 192.5 | 166.9
354 | 247 | 326.1 | 145.5 | 137.3 | 133.4 | 200.6 | 192.7 | 167
355 | 248 | 326 | 145.9 | 137.8 | 133.8 | 200.9 | 192.9 | 167.2
356 | 249 | 326 | 146.3 | 138.3 | 134.3 | 201.1 | 193.1 | 167.3
357 | 250 | 326 | 146.7 | 138.7 | 134.7 | 201.4 | 193.3 | 167.5
358 | 251 | 326 | 147.1 | 139.1 | 135.2 | 201.6 | 193.5 | 167.6
359 | 252 | 326 | 147.5 | 139.6 | 135.6 | 201.9 | 193.7 | 167.8
360 | 253 | 326 | 147.9 | 140 | 136.1 | 202.2 | 193.9 | 167.9
361 | 254 | 326 | 148.3 | 140.5 | 136.5 | 202.4 | 194.2 | 168.1
362 | 255 | 326 | 148.7 | 140.9 | 137 | 202.6 | 194.4 | 168.3
363 | 256 | 326 | 149.1 | 141.3 | 137.4 | 202.9 | 194.6 | 168.4
364 | 257 | 326 | 149.5 | 141.8 | 137.9 | 203.1 | 194.8 | 168.6
365 | 258 | 326 | 149.9 | 142.2 | 138.3 | 203.4 | 195 | 168.8
366 | 259 | 326 | 150.3 | 142.6 | 138.7 | 203.6 | 195.2 | 168.9
367 | 260 | 326 | 150.7 | 143.1 | 139.2 | 203.8 | 195.4 | 169.1
368 | 261 | 326 | 151.2 | 143.5 | 139.6 | 204.1 | 195.6 | 169.2
369 | 262 | 325.9 | 151.6 | 143.9 | 140 | 204.3 | 195.8 | 169.4
370 | 263 | 325.9 | 152 | 144.3 | 140.5 | 204.5 | 196.1 | 169.5
371 | 264 | 325.9 | 152.4 | 144.7 | 140.9 | 204.8 | 196.3 | 169.7
372 | 265 | 325.9 | 152.8 | 145.2 | 141.3 | 205 | 196.5 | 169.8
373 | 266 | 325.9 | 153.2 | 145.6 | 141.7 | 205.2 | 196.7 | 170
374 | 267 | 326 | 153.6 | 146 | 142.2 | 205.5 | 196.9 | 170.2
375 | 268 | 326 | 154 | 146.4 | 142.6 | 205.7 | 197.1 | 170.4
376 | 269 | 326 | 154.4 | 146.9 | 143 | 205.9 | 197.3 | 170.6
377 | 270 | 326.1 | 154.8 | 147.3 | 143.5 | 206.1 | 197.5 | 170.8
378 | 271 | 326.1 | 155.2 | 147.7 | 143.9 | 206.4 | 197.8 | 170.9
379 | 272 | 326.1 | 155.6 | 148.2 | 144.3 | 206.6 | 198 | 171.1
380 | 273 | 326.1 | 156 | 148.6 | 144.7 | 206.8 | 198.2 | 171.3
381 | 274 | 326.2 | 156.4 | 149 | 145.2 | 207 | 198.5 | 171.5
382 | 275 | 326.2 | 156.7 | 149.5 | 145.6 | 207.3 | 198.7 | 171.7
383 | 276 | 326.2 | 157.1 | 149.9 | 146 | 207.5 | 198.9 | 171.9
384 | 277 | 326.2 | 157.5 | 150.4 | 146.5 | 207.7 | 199.2 | 172.1
385 | 278 | 326.3 | 157.9 | 150.8 | 146.9 | 208 | 199.4 | 172.3
386 | 279 | 326.3 | 158.2 | 151.2 | 147.3 | 208.2 | 199.6 | 172.5
387 | 280 | 326.3 | 158.6 | 151.7 | 147.7 | 208.4 | 199.9 | 172.7
388 | 281 | 326.4 | 159 | 152.1 | 148.2 | 208.6 | 200.1 | 172.9
389 | 282 | 326.5 | 159.3 | 152.6 | 148.6 | 208.8 | 200.3 | 173.1
390 | 283 | 326.5 | 159.7 | 153 | 149 | 209.1 | 200.5 | 173.3
391 | 284 | 326.6 | 160 | 153.5 | 149.5 | 209.3 | 200.7 | 173.5
392 | 285 | 326.6 | 160.4 | 153.9 | 149.9 | 209.5 | 200.9 | 173.8
393 | 286 | 326.6 | 160.7 | 154.3 | 150.3 | 209.8 | 201.2 | 173.9
394 | 287 | 326.7 | 161.1 | 154.8 | 150.7 | 210 | 201.5 | 174.2
395 | 288 | 326.8 | 161.4 | 155.2 | 151.1 | 210.2 | 201.7 | 174.4
396 | 289 | 326.8 | 161.8 | 155.7 | 151.6 | 210.4 | 202 | 174.6
397 | 290 | 326.9 | 162.1 | 156.1 | 152 | 210.7 | 202.2 | 174.8
398 | 291 | 327 | 162.4 | 156.6 | 152.4 | 210.9 | 202.5 | 175
399 | 292 | 326.9 | 162.7 | 157 | 152.8 | 211.1 | 202.8 | 175.2
400 | 293 | 327 | 163.1 | 157.4 | 153.2 | 211.3 | 203 | 175.4
401 | 294 | 327 | 163.4 | 157.9 | 153.6 | 211.6 | 203.3 | 175.6
402 | 295 | 327 | 163.6 | 158.3 | 154.1 | 211.8 | 203.5 | 175.8
403 | 296 | 327.1 | 163.9 | 158.7 | 154.5 | 212 | 203.8 | 176
404 | 297 | 327.2 | 164.1 | 159.2 | 154.9 | 212.3 | 204.1 | 176.2
405 | 298 | 327.3 | 164.4 | 159.6 | 155.3 | 212.5 | 204.3 | 176.3
406 | 299 | 327.3 | 164.8 | 160 | 155.7 | 212.7 | 204.5 | 176.5
407 | 300 | 327.3 | 165.1 | 160.5 | 156.1 | 213 | 204.8 | 176.7
408 | 301 | 327.3 | 165.5 | 160.9 | 156.5 | 213.2 | 205 | 176.9
409 | 302 | 327.3 | 165.9 | 161.3 | 156.9 | 213.4 | 205.3 | 177.1
410 | 303 | 327.3 | 166.3 | 161.8 | 157.3 | 213.7 | 205.5 | 177.3
411 | 304 | 327.4 | 166.6 | 162.2 | 157.7 | 213.9 | 205.8 | 177.4
412 | 305 | 327.4 | 167 | 162.6 | 158.1 | 214.1 | 206 | 177.6
413 | 306 | 327.4 | 167.4 | 163 | 158.6 | 214.4 | 206.2 | 177.8
414 | 307 | 327.4 | 167.8 | 163.5 | 159 | 214.6 | 206.5 | 178
415 | 308 | 327.3 | 168.2 | 163.9 | 159.4 | 214.8 | 206.8 | 178.1
416 | 309 | 327.3 | 168.6 | 164.3 | 159.8 | 215 | 207 | 178.3
417 | 310 | 327.3 | 169 | 164.7 | 160.2 | 215.3 | 207.3 | 178.5
418 | 311 | 327.2 | 169.4 | 165.2 | 160.6 | 215.5 | 207.5 | 178.7
419 | 312 | 327.2 | 169.8 | 165.6 | 160.9 | 215.7 | 207.8 | 178.9
420 | 313 | 327.2 | 170.3 | 166 | 161.3 | 216 | 208.1 | 179.1
421 | 314 | 327.2 | 170.7 | 166.4 | 161.7 | 216.2 | 208.3 | 179.3
422 | 315 | 327.2 | 171.1 | 166.8 | 162.1 | 216.4 | 208.6 | 179.5
423 | 316 | 327.1 | 171.5 | 167.2 | 162.5 | 216.6 | 208.8 | 179.6
424 | 317 | 327.1 | 171.9 | 167.6 | 162.9 | 216.8 | 209.1 | 179.8
425 | 318 | 327.1 | 172.3 | 168 | 163.3 | 217.1 | 209.3 | 180
426 | 319 | 327.1 | 172.7 | 168.4 | 163.7 | 217.3 | 209.6 | 180.2
427 | 320 | 327.1 | 173.1 | 168.8 | 164.1 | 217.5 | 209.9 | 180.3
428 | 321 | 327 | 173.5 | 169.2 | 164.5 | 217.8 | 210.1 | 180.5
429 | 322 | 327 | 173.8 | 169.5 | 164.8 | 218 | 210.4 | 180.7
430 | 323 | 327 | 174.2 | 169.9 | 165.2 | 218.2 | 210.7 | 180.8
431 | 324 | 326.9 | 174.6 | 170.3 | 165.6 | 218.4 | 211 | 181
432 | 325 | 327 | 175 | 170.7 | 166 | 218.6 | 211.2 | 181.2
433 | 326 | 326.9 | 175.3 | 171.1 | 166.4 | 218.8 | 211.4 | 181.3
434 | 327 | 326.9 | 175.7 | 171.5 | 166.7 | 219.1 | 211.6 | 181.5
435 | 328 | 327 | 176.1 | 171.8 | 167.1 | 219.3 | 211.9 | 181.7
436 | 329 | 327 | 176.4 | 172.2 | 167.5 | 219.5 | 212.2 | 181.8
437 | 330 | 326.9 | 176.8 | 172.6 | 167.9 | 219.7 | 212.4 | 182
438 | 331 | 326.9 | 177.2 | 173 | 168.2 | 219.9 | 212.7 | 182.1
439 | 332 | 326.9 | 177.5 | 173.4 | 168.6 | 220.1 | 213 | 182.2
440 | 333 | 326.9 | 177.9 | 173.8 | 169 | 220.4 | 213.2 | 182.4
441 | 334 | 326.8 | 178.3 | 174.1 | 169.4 | 220.6 | 213.5 | 182.5
442 | 335 | 326.8 | 178.7 | 174.5 | 169.7 | 220.8 | 213.8 | 182.6
443 | 336 | 326.8 | 179 | 174.9 | 170.1 | 221 | 214 | 182.8
444 | 337 | 326.8 | 179.4 | 175.2 | 170.5 | 221.2 | 214.3 | 183
445 | 338 | 326.8 | 179.8 | 175.6 | 170.8 | 221.4 | 214.6 | 183.1
446 | 339 | 326.8 | 180.2 | 176 | 171.2 | 221.6 | 214.8 | 183.3
447 | 340 | 326.8 | 180.5 | 176.3 | 171.6 | 221.8 | 215.1 | 183.4
448 | 341 | 326.8 | 180.9 | 176.7 | 171.9 | 222.1 | 215.3 | 183.6
449 | 342 | 326.7 | 181.2 | 177.1 | 172.3 | 222.3 | 215.6 | 183.8
450 | 343 | 326.7 | 181.6 | 177.4 | 172.7 | 222.5 | 215.8 | 183.9
451 | 344 | 326.7 | 182 | 177.8 | 173 | 222.7 | 216.1 | 184.1
452 | 345 | 326.6 | 182.4 | 178.1 | 173.4 | 222.9 | 216.4 | 184.2
453 | 346 | 326.6 | 182.7 | 178.5 | 173.7 | 223.1 | 216.7 | 184.4
454 | 347 | 326.5 | 183.1 | 178.9 | 174.1 | 223.3 | 216.9 | 184.5
455 | 348 | 326.4 | 183.4 | 179.2 | 174.5 | 223.5 | 217.2 | 184.7
456 | 349 | 326.4 | 183.7 | 179.6 | 174.8 | 223.7 | 217.5 | 184.8
457 | 350 | 326.4 | 184.1 | 179.9 | 175.2 | 223.9 | 217.8 | 185
458 | 351 | 326.4 | 184.4 | 180.3 | 175.5 | 224.1 | 218.1 | 185.1
459 | 352 | 326.4 | 184.7 | 180.6 | 175.9 | 224.3 | 218.3 | 185.3
460 | 353 | 326.4 | 185 | 181 | 176.2 | 224.5 | 218.6 | 185.5
461 | 354 | 326.5 | 185.4 | 181.3 | 176.6 | 224.7 | 218.9 | 185.6
462 | 355 | 326.5 | 185.7 | 181.6 | 176.9 | 224.9 | 219.2 | 185.8
463 | 356 | 326.5 | 186 | 182 | 177.3 | 225.1 | 219.5 | 185.9
464 | 357 | 326.4 | 186.3 | 182.3 | 177.6 | 225.4 | 219.8 | 186.1
465 | 358 | 326.4 | 186.6 | 182.7 | 178 | 225.6 | 220.1 | 186.3
466 | 359 | 326.4 | 186.9 | 183 | 178.3 | 225.8 | 220.3 | 186.4
467 | 360 | 326.4 | 187.3 | 183.3 | 178.7 | 226 | 220.6 | 186.6
468 | 361 | 326.5 | 187.6 | 183.7 | 179 | 226.2 | 220.8 | 186.7
469 | 362 | 326.5 | 188 | 184 | 179.4 | 226.4 | 221.2 | 186.9
470 | 363 | 326.5 | 188.3 | 184.3 | 179.7 | 226.6 | 221.5 | 187
471 | 364 | 326.5 | 188.7 | 184.7 | 180 | 226.8 | 221.8 | 187.2
472 | 365 | 326.6 | 189 | 185 | 180.4 | 227 | 222 | 187.4
473 | 366 | 326.6 | 189.3 | 185.3 | 180.7 | 227.1 | 222.3 | 187.5
474 | 367 | 326.5 | 189.6 | 185.6 | 181.1 | 227.3 | 222.6 | 187.7
475 | 368 | 326.5 | 189.9 | 185.9 | 181.4 | 227.5 | 222.9 | 187.9
476 | 369 | 326.5 | 190.3 | 186.3 | 181.7 | 227.7 | 223.2 | 188
477 | 370 | 326.6 | 190.6 | 186.6 | 182.1 | 227.9 | 223.5 | 188.2
478 | 371 | 326.6 | 191 | 186.9 | 182.4 | 228.1 | 223.8 | 188.3
479 | 372 | 326.6 | 191.4 | 187.2 | 182.7 | 228.3 | 224.1 | 188.5
480 | 373 | 326.6 | 191.8 | 187.5 | 183.1 | 228.5 | 224.3 | 188.6
481 | 374 | 326.6 | 192.1 | 187.8 | 183.4 | 228.7 | 224.6 | 188.7
482 | 375 | 326.6 | 192.5 | 188.1 | 183.7 | 228.8 | 224.9 | 188.9
483 | 376 | 326.6 | 192.9 | 188.4 | 184 | 229 | 225.2 | 189.1
484 | 377 | 326.6 | 193.2 | 188.8 | 184.4 | 229.2 | 225.5 | 189.2
485 | 378 | 326.6 | 193.6 | 189.1 | 184.7 | 229.4 | 225.8 | 189.4
486 | 379 | 326.6 | 193.9 | 189.4 | 185 | 229.6 | 226.1 | 189.5
487 | 380 | 326.6 | 194.3 | 189.7 | 185.3 | 229.8 | 226.4 | 189.7
488 | 381 | 326.7 | 194.6 | 190 | 185.6 | 229.9 | 226.7 | 189.9
489 | 382 | 326.7 | 194.9 | 190.3 | 186 | 230.1 | 227 | 190
490 | 383 | 326.7 | 195.2 | 190.6 | 186.3 | 230.3 | 227.3 | 190.1
491 | 384 | 326.7 | 195.6 | 190.9 | 186.6 | 230.5 | 227.6 | 190.3
492 | 385 | 326.7 | 195.9 | 191.2 | 186.9 | 230.6 | 227.9 | 190.4
493 | 386 | 326.7 | 196.2 | 191.5 | 187.2 | 230.8 | 228.2 | 190.6
494 | 387 | 326.7 | 196.5 | 191.8 | 187.5 | 231 | 228.5 | 190.8
495 | 388 | 326.7 | 196.9 | 192.1 | 187.8 | 231.1 | 228.8 | 190.9
496 | 389 | 326.7 | 197.2 | 192.4 | 188.1 | 231.3 | 229.1 | 191.1
497 | 390 | 326.7 | 197.5 | 192.7 | 188.4 | 231.5 | 229.4 | 191.2
498 | 391 | 326.6 | 197.8 | 193 | 188.7 | 231.6 | 229.7 | 191.3
499 | 392 | 326.6 | 198.1 | 193.3 | 189 | 231.8 | 230 | 191.5
500 | 393 | 326.6 | 198.4 | 193.6 | 189.3 | 232 | 230.3 | 191.6
501 | 394 | 326.5 | 198.7 | 193.8 | 189.6 | 232.1 | 230.6 | 191.7
502 | 395 | 326.5 | 199 | 194.2 | 189.9 | 232.3 | 230.9 | 191.9
503 | 396 | 326.5 | 199.3 | 194.5 | 190.2 | 232.4 | 231.2 | 192
504 | 397 | 326.4 | 199.6 | 194.7 | 190.5 | 232.6 | 231.5 | 192.2
505 | 398 | 326.4 | 199.9 | 195.1 | 190.8 | 232.7 | 231.8 | 192.3
506 | 399 | 326.3 | 200.2 | 195.3 | 191.1 | 232.9 | 232.1 | 192.5
507 | 400 | 326.3 | 200.5 | 195.6 | 191.4 | 233 | 232.4 | 192.6
508 | 401 | 326.3 | 200.8 | 195.9 | 191.7 | 233.2 | 232.7 | 192.8
509 | 402 | 326.3 | 201.1 | 196.2 | 192 | 233.3 | 233 | 192.9
510 | 403 | 326.2 | 201.4 | 196.5 | 192.3 | 233.5 | 233.3 | 193
511 | 404 | 326.2 | 201.7 | 196.8 | 192.6 | 233.6 | 233.6 | 193.1
512 | 405 | 326.2 | 202 | 197 | 192.9 | 233.8 | 233.9 | 193.3
513 | 406 | 326.2 | 202.3 | 197.3 | 193.2 | 233.9 | 234.2 | 193.4
514 | 407 | 326.2 | 202.6 | 197.6 | 193.5 | 234.1 | 234.5 | 193.6
515 | 408 | 326.1 | 202.9 | 197.9 | 193.8 | 234.2 | 234.8 | 193.7
516 | 409 | 326.1 | 203.2 | 198.1 | 194 | 234.3 | 235.1 | 193.8
517 | 410 | 326.1 | 203.4 | 198.4 | 194.3 | 234.5 | 235.4 | 194
518 | 411 | 326.1 | 203.7 | 198.7 | 194.6 | 234.6 | 235.7 | 194.1
519 | 412 | 326 | 203.9 | 199 | 194.9 | 234.8 | 236 | 194.2
520 | 413 | 326 | 204.2 | 199.3 | 195.2 | 234.9 | 236.3 | 194.4
521 | 414 | 326.1 | 204.5 | 199.5 | 195.5 | 235 | 236.6 | 194.6
522 | 415 | 326.1 | 204.7 | 199.8 | 195.8 | 235.2 | 236.8 | 194.7
523 | 416 | 326.2 | 205 | 200.1 | 196 | 235.3 | 237.1 | 194.8
524 | 417 | 326.2 | 205.3 | 200.4 | 196.3 | 235.4 | 237.3 | 195
525 | 418 | 326.3 | 205.5 | 200.6 | 196.6 | 235.6 | 237.6 | 195.1
526 | 419 | 326.3 | 205.8 | 200.9 | 196.9 | 235.7 | 237.9 | 195.2
527 | 420 | 326.3 | 206.1 | 201.2 | 197.2 | 235.9 | 238.1 | 195.3
528 | 421 | 326.3 | 206.4 | 201.5 | 197.5 | 236 | 238.4 | 195.4
529 | 422 | 326.3 | 206.6 | 201.7 | 197.8 | 236.2 | 238.7 | 195.5
530 | 423 | 326.3 | 206.9 | 202 | 198 | 236.3 | 238.9 | 195.6
531 | 424 | 326.3 | 207.2 | 202.3 | 198.3 | 236.4 | 239.2 | 195.7
532 | 425 | 326.3 | 207.4 | 202.6 | 198.6 | 236.6 | 239.4 | 195.8
533 | 426 | 326.3 | 207.7 | 202.8 | 198.9 | 236.7 | 239.6 | 195.9
534 | 427 | 326.3 | 208 | 203.1 | 199.2 | 236.9 | 239.9 | 196
535 | 428 | 326.4 | 208.2 | 203.4 | 199.5 | 237 | 240.1 | 196.1
536 | 429 | 326.4 | 208.5 | 203.6 | 199.7 | 237.1 | 240.4 | 196.2
537 | 430 | 326.4 | 208.7 | 203.9 | 200 | 237.3 | 240.6 | 196.3
538 | 431 | 326.4 | 209 | 204.2 | 200.3 | 237.4 | 240.8 | 196.4
539 | 432 | 326.4 | 209.3 | 204.5 | 200.6 | 237.6 | 241.1 | 196.5
540 | 433 | 326.5 | 209.5 | 204.8 | 200.9 | 237.7 | 241.3 | 196.6
541 | 434 | 326.5 | 209.8 | 205 | 201.1 | 237.8 | 241.5 | 196.7
542 | 435 | 326.5 | 210 | 205.3 | 201.4 | 238 | 241.8 | 196.8
543 | 436 | 326.5 | 210.3 | 205.6 | 201.7 | 238.1 | 242 | 196.9
544 | 437 | 326.6 | 210.5 | 205.8 | 202 | 238.2 | 242.2 | 197.1
545 | 438 | 326.6 | 210.8 | 206.1 | 202.2 | 238.4 | 242.5 | 197.2
546 | 439 | 326.6 | 211.1 | 206.4 | 202.5 | 238.5 | 242.7 | 197.3
547 | 440 | 326.6 | 211.3 | 206.7 | 202.8 | 238.6 | 242.9 | 197.4
548 | 441 | 326.6 | 211.6 | 206.9 | 203.1 | 238.8 | 243.2 | 197.6
549 | 442 | 326.6 | 211.8 | 207.2 | 203.3 | 238.9 | 243.4 | 197.7
550 | 443 | 326.6 | 212.1 | 207.5 | 203.6 | 239 | 243.6 | 197.8
551 | 444 | 326.7 | 212.3 | 207.8 | 203.9 | 239.2 | 243.8 | 197.9
552 | 445 | 326.7 | 212.6 | 208 | 204.2 | 239.3 | 244 | 198
553 | 446 | 326.7 | 212.8 | 208.3 | 204.4 | 239.5 | 244.2 | 198.1
554 | 447 | 326.8 | 213.1 | 208.5 | 204.7 | 239.6 | 244.4 | 198.2
555 | 448 | 326.8 | 213.3 | 208.8 | 205 | 239.8 | 244.7 | 198.3
556 | 449 | 326.8 | 213.6 | 209.1 | 205.2 | 239.9 | 244.9 | 198.4
557 | 450 | 326.7 | 213.8 | 209.3 | 205.5 | 240 | 245.1 | 198.5
558 | 451 | 326.7 | 214.1 | 209.6 | 205.8 | 240.2 | 245.3 | 198.6
559 | 452 | 326.7 | 214.4 | 209.9 | 206 | 240.3 | 245.5 | 198.7
560 | 453 | 326.7 | 214.6 | 210.1 | 206.3 | 240.4 | 245.7 | 198.8
561 | 454 | 326.6 | 214.9 | 210.4 | 206.6 | 240.6 | 245.9 | 198.9
562 | 455 | 326.7 | 215.1 | 210.7 | 206.8 | 240.7 | 246.1 | 199
563 | 456 | 326.7 | 215.4 | 210.9 | 207.1 | 240.9 | 246.3 | 199.1
564 | 457 | 326.7 | 215.7 | 211.2 | 207.4 | 241 | 246.5 | 199.2
565 | 458 | 326.7 | 215.9 | 211.5 | 207.6 | 241.1 | 246.7 | 199.2
566 | 459 | 326.6 | 216.2 | 211.8 | 207.9 | 241.3 | 246.9 | 199.3
567 | 460 | 326.6 | 216.4 | 212 | 208.1 | 241.4 | 247.1 | 199.4
568 | 461 | 326.6 | 216.7 | 212.3 | 208.4 | 241.5 | 247.2 | 199.5
569 | 462 | 326.5 | 216.9 | 212.5 | 208.7 | 241.7 | 247.4 | 199.6
570 | 463 | 326.5 | 217.2 | 212.8 | 208.9 | 241.8 | 247.6 | 199.7
571 | 464 | 326.5 | 217.4 | 213.1 | 209.2 | 241.9 | 247.7 | 199.8
572 | 465 | 326.5 | 217.7 | 213.3 | 209.4 | 242.1 | 247.9 | 199.8
573 | 466 | 326.4 | 217.9 | 213.6 | 209.7 | 242.2 | 248 | 199.9
574 | 467 | 326.4 | 218.2 | 213.9 | 209.9 | 242.4 | 248.2 | 200
575 | 468 | 326.3 | 218.4 | 214.1 | 210.2 | 242.5 | 248.4 | 200.1
576 | 469 | 326.3 | 218.6 | 214.4 | 210.4 | 242.6 | 248.5 | 200.2
577 | 470 | 326.3 | 218.9 | 214.6 | 210.7 | 242.8 | 248.7 | 200.3
578 | 471 | 326.2 | 219.1 | 214.9 | 210.9 | 242.9 | 248.9 | 200.4
579 | 472 | 326.2 | 219.4 |  | 211.2 | 243 | 249 | 200.5
580 | 473 | 326.2 | 219.6 |  | 211.3 | 243.1 | 249.2 | 200.6
581 | 474 | 326.2 | 219.8 |  | 211.6 | 243.3 | 249.3 | 200.6
582 | 475 | 326.2 | 220.1 |  | 211.8 | 243.4 | 249.5 | 200.7
583 | 476 | 326.2 | 220.3 |  | 212.1 | 243.5 | 249.6 | 200.8
584 | 477 | 326.3 | 220.6 |  | 212.3 | 243.7 | 249.7 | 200.9
585 | 478 | 326.2 | 220.8 |  | 212.6 | 243.8 | 249.9 | 201
586 | 479 | 326.3 | 221.1 |  | 212.8 | 243.9 | 250 | 201
587 | 480 | 326.3 | 221.3 |  | 213 | 244.1 | 250.2 | 201.1
588 | 481 | 326.3 | 221.6 |  | 213.3 | 244.2 | 250.3 | 201.2
589 | 482 | 326.2 | 221.9 |  | 213.5 | 244.4 | 250.5 | 201.3
590 | 483 | 326.2 | 222.1 |  | 213.8 | 244.5 | 250.7 | 201.4
591 | 484 | 326.3 | 222.4 |  | 214 | 244.6 | 250.8 | 201.5
592 | 485 | 326.3 | 222.6 |  | 214.3 | 244.8 | 251 | 201.6
593 | 486 | 326.3 | 222.9 |  | 214.5 | 244.9 | 251.1 | 201.7
594 | 487 | 326.3 | 223.1 |  | 214.7 | 245.1 | 251.3 | 201.7
595 | 488 | 326.3 | 223.4 |  | 215 | 245.2 | 251.4 | 201.8
596 | 489 | 326.3 | 223.6 |  | 215.2 | 245.3 | 251.6 | 201.9
597 | 490 | 326.2 | 223.8 |  | 215.4 | 245.5 | 251.7 | 202
598 | 491 | 326.2 | 224.1 |  | 215.7 | 245.6 | 251.9 | 202.1
599 | 492 | 326.3 | 224.3 |  | 215.9 | 245.8 | 252 | 202.2
600 | 493 | 326.3 | 224.5 |  | 216.1 | 245.9 | 252.2 | 202.3
601 | 494 | 326.4 | 224.7 |  | 216.4 | 246.1 | 252.3 | 202.4
602 | 495 | 326.4 | 225 |  | 216.6 | 246.2 | 252.4 | 202.5
603 | 496 | 326.5 | 225.2 |  | 216.8 | 246.4 | 252.6 | 202.6
604 | 497 | 326.5 | 225.4 |  | 217 | 246.5 | 252.7 | 202.6
605 | 498 | 326.5 | 225.7 |  | 217.3 | 246.7 | 252.9 | 202.7
606 | 499 | 326.5 | 225.9 |  | 217.5 | 246.8 | 253 | 202.8
607 | 500 | 326.6 | 226.2 |  | 217.7 | 247 | 253.2 | 202.9
608 | 501 | 326.6 | 226.4 |  | 218 | 247.1 | 253.3 | 203
609 | 502 | 326.6 | 226.6 |  | 218.2 | 247.2 | 253.4 | 203.1
610 | 503 | 326.6 | 226.9 |  | 218.4 | 247.4 | 253.6 | 203.2
611 | 504 | 326.6 | 227.1 |  | 218.6 | 247.5 | 253.7 | 203.3
612 | 505 | 326.6 | 227.3 |  | 218.9 | 247.7 | 253.8 | 203.4
613 | 506 | 326.6 | 227.6 |  | 219.1 | 247.8 | 254 | 203.5
614 | 507 | 326.6 | 227.8 |  | 219.3 | 248 | 254.2 | 203.6
615 | 508 | 326.5 | 228 |  | 219.5 | 248.1 | 254.3 | 203.7
616 | 509 | 326.5 | 228.2 |  | 219.8 | 248.3 | 254.4 | 203.8
617 | 510 | 326.5 | 228.4 |  | 220 | 248.4 | 254.6 | 203.9
618 | 511 | 326.5 | 228.7 |  | 220.2 | 248.5 | 254.7 | 204
619 | 512 | 326.5 | 228.9 |  | 220.4 | 248.7 | 254.8 | 204.1
620 | 513 | 326.5 | 229.1 |  | 220.7 | 248.8 | 255 | 204.2
621 | 514 | 326.6 | 229.3 |  | 220.9 | 249 | 255.1 | 204.3
622 | 515 | 326.6 | 229.5 |  | 221.1 | 249.1 | 255.3 | 204.4
623 | 516 | 326.5 | 229.8 |  | 221.3 | 249.2 | 255.4 | 204.5
624 | 517 | 326.5 | 230 |  | 221.5 | 249.4 | 255.5 | 204.6
625 | 518 | 326.5 | 230.2 |  | 221.7 | 249.5 | 255.7 | 204.7
626 | 519 | 326.5 | 230.4 |  | 222 | 249.6 | 255.8 | 204.8
627 | 520 | 326.5 | 230.6 |  | 222.2 | 249.8 | 256 | 204.8
628 | 521 | 326.5 | 230.8 |  | 222.4 | 249.9 | 256.1 | 204.9
629 | 522 | 326.4 | 231 |  | 222.6 | 250 | 256.2 | 205
630 | 523 | 326.4 | 231.2 |  | 222.8 | 250.1 | 256.4 | 205.1
631 | 524 | 326.4 | 231.5 |  | 223 | 250.3 | 256.5 | 205.2
632 | 525 | 326.4 | 231.7 |  | 223.2 | 250.4 | 256.6 | 205.3
633 | 526 | 326.3 | 231.9 |  | 223.4 | 250.5 | 256.7 | 205.4
634 | 527 | 326.3 | 232.1 |  | 223.7 | 250.6 | 256.8 | 205.4
635 | 528 | 326.3 | 232.3 |  | 223.9 | 250.7 | 256.9 | 205.5
636 | 529 | 326.3 | 232.4 |  | 224.1 | 250.8 | 257 | 205.6
637 | 530 | 326.3 | 232.6 |  | 224.3 | 250.9 | 257.2 | 205.7
638 | 531 | 326.3 | 232.7 |  | 224.5 | 251 | 257.3 | 205.8
639 | 532 | 326.3 | 232.9 |  | 224.7 | 251.1 | 257.4 | 205.9
640 | 533 | 326.3 | 233 |  | 224.9 | 251.2 | 257.5 | 205.9
641 | 534 | 326.3 | 233.1 |  | 225.1 | 251.3 | 257.6 | 206
642 | 535 | 326.3 | 233.3 |  | 225.3 | 251.4 | 257.7 | 206.1
643 | 536 | 326.3 | 233.4 |  | 225.5 | 251.4 | 257.8 | 206.1
644 | 537 | 326.3 | 233.5 |  | 225.7 | 251.5 | 257.9 | 206.2
645 | 538 | 326.3 | 233.7 |  | 225.9 | 251.6 | 258 | 206.3
646 | 539 | 326.3 | 233.8 |  | 226.1 | 251.7 | 258.1 | 206.4
647 | 540 | 326.3 | 233.9 |  | 226.3 | 251.8 | 258.2 | 206.4
648 | 541 | 326.3 | 234.1 |  | 226.5 | 251.9 | 258.3 | 206.5
649 | 542 | 326.3 | 234.2 |  | 226.7 | 251.9 | 258.4 | 206.6
650 | 543 | 326.3 | 234.4 |  | 226.9 | 252 | 258.5 | 206.7
651 | 544 | 326.3 | 234.5 |  | 227.1 | 252.1 | 258.6 | 206.7
652 | 545 | 326.3 | 234.6 |  | 227.3 | 252.2 | 258.7 | 206.8
653 | 546 | 326.3 | 234.8 |  | 227.5 | 252.3 | 258.8 | 206.9
654 | 547 | 326.3 | 234.9 |  | 227.7 | 252.4 | 258.9 | 206.9
655 | 548 | 326.2 | 235 |  | 227.9 | 252.4 | 259 | 207
656 | 549 | 326.2 | 235.2 |  | 228.1 | 252.5 | 259.1 | 207.1
657 | 550 | 326.2 | 235.3 |  | 228.3 | 252.6 | 259.2 | 207.2
658 | 551 | 326.1 | 235.5 |  | 228.5 | 252.6 | 259.3 | 207.2
659 | 552 | 326.1 | 235.6 |  | 228.6 | 252.7 | 259.5 | 207.3
660 | 553 | 326.2 | 235.7 |  | 228.8 | 252.8 | 259.6 | 207.4
661 | 554 | 326.2 | 235.9 |  | 229 | 252.9 | 259.7 | 207.4
662 | 555 | 326.2 | 236 |  | 229.2 | 253 | 259.8 | 207.5
663 | 556 | 326.2 | 236.2 |  | 229.4 | 253 | 259.9 | 207.6
664 | 557 | 326.2 | 236.3 |  | 229.6 | 253.1 | 260 | 207.6
665 | 558 | 326.2 | 236.5 |  | 229.8 | 253.2 | 260.2 | 207.7
666 | 559 | 326.2 | 236.6 |  | 230.1 | 253.3 | 260.2 | 207.8
667 | 560 | 326.2 | 236.8 |  | 230.3 | 253.3 | 260.3 | 207.8
668 | 561 | 326.2 | 236.9 |  | 230.5 | 253.4 | 260.4 | 207.9
669 | 562 | 326.1 | 237.1 |  | 230.7 | 253.5 | 260.5 | 208
670 | 563 | 326.1 | 237.2 |  | 230.9 | 253.6 | 260.6 | 208.1
671 | 564 | 326 | 237.4 |  | 231 | 253.6 | 260.7 | 208.1
672 | 565 | 326 | 237.5 |  | 231.2 | 253.7 | 260.8 | 208.2
673 | 566 | 326 | 237.7 |  | 231.4 | 253.8 | 260.8 | 208.3
674 | 567 | 326 | 237.9 |  | 231.6 | 253.8 | 260.9 | 208.4
675 | 568 | 325.9 | 238 |  | 231.8 | 253.9 | 261 | 208.5
676 | 569 | 326 | 238.2 |  | 232 | 254 | 261.1 | 208.5
677 | 570 | 326 | 238.4 |  | 232.2 | 254 | 261.2 | 208.6
678 | 571 | 326 | 238.6 |  | 232.4 | 254.1 | 261.3 | 208.7
679 | 572 | 326 | 238.7 |  | 232.5 | 254.2 | 261.4 | 208.8
680 | 573 | 326.1 | 238.9 |  | 232.7 | 254.3 | 261.5 | 208.9
681 | 574 | 326 | 239.1 |  | 232.8 | 254.3 | 261.5 | 208.9
682 | 575 | 326.1 | 239.2 |  | 233 | 254.4 | 261.6 | 209
683 | 576 | 326.1 | 239.4 |  | 233.1 | 254.4 | 261.7 | 209.1
684 | 577 | 326 | 239.6 |  | 233.3 | 254.5 | 261.8 | 209.2
685 | 578 | 325.9 | 239.7 |  | 233.5 | 254.6 | 261.9 | 209.3
686 | 579 | 325.9 | 239.9 |  | 233.7 | 254.6 | 262 | 209.3
687 | 580 | 325.9 | 240 |  | 233.8 | 254.7 | 262 | 209.4
688 | 581 | 325.9 | 240.2 |  | 234 | 254.8 | 262.1 | 209.5
689 | 582 | 325.8 | 240.4 |  | 234.2 | 254.8 | 262.2 | 209.6
690 | 583 | 325.8 | 240.5 |  | 234.4 | 254.9 | 262.3 | 209.7
691 | 584 | 325.8 | 240.7 |  | 234.5 | 254.9 | 262.4 | 209.8
692 | 585 | 325.8 | 240.9 |  | 234.7 | 255 | 262.5 | 209.9
693 | 586 | 325.7 | 241 |  | 234.9 | 255.1 | 262.6 | 209.9
694 | 587 | 325.7 | 241.2 |  | 235.1 | 255.1 | 262.7 | 210
695 | 588 | 325.7 | 241.3 |  | 235.2 | 255.2 | 262.8 | 210.1
696 | 589 | 325.7 | 241.5 |  | 235.4 | 255.3 | 262.8 | 210.2
697 | 590 | 325.6 | 241.7 |  | 235.6 | 255.3 | 262.9 | 210.3
698 | 591 | 325.6 | 241.8 |  | 235.7 | 255.4 | 263 | 210.4
699 | 592 | 325.5 | 242 |  | 235.9 | 255.4 | 263.1 | 210.5
700 | 593 | 325.5 | 242.2 |  | 236.1 | 255.5 | 263.1 | 210.6
701 | 594 | 325.5 | 242.3 |  | 236.2 | 255.6 | 263.2 | 210.6
702 | 595 | 325.5 | 242.4 |  | 236.4 | 255.7 | 263.3 | 210.7
703 | 596 | 325.5 | 242.6 |  | 236.7 | 255.8 | 263.3 | 210.8
704 | 597 | 325.5 | 242.7 |  | 236.8 | 255.9 | 263.4 | 210.9
705 | 598 | 325.5 | 242.9 |  | 237 | 255.9 | 263.4 | 211
706 | 599 | 325.4 | 243 |  | 237.1 | 256 | 263.5 | 211.1 | Time of first failure
707 | 600 | 325.3 | 243.2 |  | 237.3 | 256.1 | 263.6 | 211.2 | 599 | 0
708 | 601 | 325.3 | 243.4 |  | 237.5 | 256.1 | 263.6 | 211.3 | 599 | 900
709 | 602 | 325.3 | 243.5 |  | 237.7 | 256.2 | 263.7 | 211.3
710 | 603 | 325.3 | 243.7 |  | 237.8 | 256.3 | 263.8 | 211.4
711 | 604 | 325.3 | 243.9 |  | 238 | 256.4 | 263.8 | 211.5
712 | 605 | 325.3 | 244.1 |  | 238.2 | 256.4 | 263.9 | 211.6
713 | 606 | 325.3 | 244.2 |  | 238.4 | 256.5 | 264 | 211.7
714 | 607 | 325.3 | 244.4 |  | 238.5 | 256.6 | 264 | 211.8
715 | 608 | 325.4 | 244.5 |  | 238.7 | 256.7 | 264.1 | 211.9
716 | 609 | 325.4 | 244.7 |  | 238.9 | 256.8 | 264.1 | 212
717 | 610 | 325.4 | 244.9 |  | 239 | 256.8 | 264.2 | 212.1
718 | 611 | 325.3 | 245 |  | 239.2 | 256.9 | 264.3 | 212.2
719 | 612 | 325.3 | 245.2 |  | 239.4 | 257 | 264.4 | 212.3
720 | 613 | 325.3 | 245.3 |  | 239.5 | 257.1 | 264.5 | 212.4
721 | 614 | 325.3 | 245.5 |  | 239.7 | 257.2 | 264.5 | 212.5
722 | 615 | 325.3 | 245.7 |  | 239.9 | 257.3 | 264.6 | 212.5
723 | 616 | 325.2 | 246 |  | 240 | 257.3 | 264.7 | 212.6
724 | 617 | 325.2 | 246.3 |  | 240.2 | 257.4 | 264.7 | 212.7
725 | 618 | 325.2 | 246.5 |  | 240.4 | 257.5 | 264.8 | 212.8
726 | 619 | 325.2 | 246.7 |  | 240.5 | 257.6 | 264.9 | 212.9
727 | 620 | 325.2 | 246.8 |  | 240.7 | 257.6 | 265 | 213.1
728 | 621 | 325.2 | 247 |  | 240.9 | 257.7 | 265.1 | 213.2
729 | 622 | 325.2 | 247.3 |  | 241 | 257.8 | 265.2 | 213.3
730 | 623 | 325.2 | 247.4 |  | 241.2 | 257.9 | 265.3 | 213.4
731 | 624 | 325.2 | 247.6 |  | 241.3 | 257.9 | 265.4 | 213.5
732 | 625 | 325.2 | 247.7 |  | 241.5 | 258 | 265.5 | 213.6
733 | 626 | 325.3 | 247.8 |  | 241.7 | 258.1 | 265.6 | 213.7
734 | 627 | 325.3 | 248.1 |  | 241.8 | 258.2 | 265.7 | 213.8
735 | 628 | 325.4 | 248.3 |  | 242 | 258.3 | 265.8 | 213.9
736 | 629 | 325.4 | 248.4 |  | 242.2 | 258.3 | 265.9 | 214
737 | 630 | 325.4 | 248.5 |  | 242.3 | 258.4 | 266 | 214.1
738 | 631 | 325.4 | 248.6 |  | 242.5 | 258.5 | 266.1 | 214.2
739 | 632 | 325.4 | 248.7 |  | 242.7 | 258.6 | 266.2 | 214.4
740 | 633 | 325.4 | 248.7 |  | 242.8 | 258.7 | 266.3 | 214.5
741 | 634 | 325.3 | 248.8 |  | 243 | 258.7 | 266.4 | 214.6
742 | 635 | 325.3 | 249 |  | 243.2 | 258.8 | 266.4 | 214.7
743 | 636 | 325.3 | 249.1 |  | 243.3 | 258.9 | 266.5 | 214.8
744 | 637 | 325.3 | 249.3 |  | 243.5 | 259 | 266.6 | 215
745 | 638 | 325.3 | 249.5 |  | 243.7 | 259.1 | 266.7 | 215.1
746 | 639 | 325.3 | 249.6 |  | 243.8 | 259.1 | 266.8 | 215.2
747 | 640 | 325.3 | 249.8 |  | 244 | 259.2 | 266.9 | 215.3
748 | 641 | 325.3 | 250 |  | 244.2 | 259.3 | 267 | 215.4
749 | 642 | 325.3 | 250.2 |  | 244.4 | 259.3 | 267.1 | 215.6
750 | 643 | 325.4 | 250.4 |  | 244.5 | 259.4 | 267.2 | 215.7
751 | 644 | 325.4 | 250.6 |  | 244.7 | 259.5 | 267.3 | 215.8
752 | 645 | 325.4 | 250.7 |  | 244.9 | 259.6 | 267.5 | 216
753 | 646 | 325.4 | 250.9 |  | 245 | 259.6 | 267.6 | 216.1
754 | 647 | 325.4 | 251.1 |  | 245.2 | 259.7 | 267.7 | 216.2
755 | 648 | 325.4 | 251.2 |  | 245.3 | 259.8 | 267.8 | 216.3
756 | 649 | 325.5 | 251.4 |  | 245.5 | 259.8 | 268 | 216.5
757 | 650 | 325.5 | 251.6 |  | 245.7 | 259.9 | 268.1 | 216.6
758 | 651 | 325.4 | 251.7 |  | 245.8 | 260 | 268.3 | 216.7
759 | 652 | 325.4 | 251.9 |  | 246 | 260 | 268.4 | 216.9
760 | 653 | 325.5 | 252.1 |  | 246.1 | 260.1 | 268.5 | 217
761 | 654 | 325.5 | 252.2 |  | 246.3 | 260.2 | 268.5 | 217.1
762 | 655 | 325.5 | 252.4 |  | 246.5 | 260.3 | 268.6 | 217.3
763 | 656 | 325.6 | 252.6 |  | 246.6 | 260.4 | 268.7 | 217.4
764 | 657 | 325.5 | 252.7 |  | 246.8 | 260.5 | 268.8 | 217.5
765 | 658 | 325.5 | 252.9 |  | 247 | 260.6 | 268.8 | 217.7
766 | 659 | 325.6 | 253.1 |  | 247.1 | 260.6 | 268.9 | 217.8
767 | 660 | 325.6 | 253.3 |  | 247.3 | 260.8 | 269 | 218
768 | 661 | 325.6 | 253.4 |  | 247.4 | 260.8 | 269.1 | 218.1
769 | 662 | 325.6 | 253.6 |  | 247.6 | 260.9 | 269.2 | 218.2
770 | 663 | 325.6 | 253.8 |  | 247.8 | 261 | 269.3 | 218.4
771 | 664 | 325.6 | 254 |  | 247.9 | 261.1 | 269.4 | 218.5
772 | 665 | 325.6 | 254.1 |  | 248.1 | 261.2 | 269.5 | 218.7
773 | 666 | 325.6 | 254.3 |  | 248.2 | 261.3 | 269.5 | 218.8
774 | 667 | 325.6 | 254.5 |  | 248.4 | 261.4 | 269.6 | 219
775 | 668 | 325.7 | 254.7 |  | 248.5 | 261.5 | 269.7 | 219.1
776 | 669 | 325.7 | 254.9 |  | 248.7 | 261.5 | 269.9 | 219.3
777 | 670 | 325.7 | 255 |  | 248.9 | 261.6 | 270 | 219.4
778 | 671 | 325.6 | 255.2 |  | 249 | 261.7 | 270.1 | 219.6
779 | 672 | 325.6 | 255.4 |  | 249.2 | 261.8 | 270.2 | 219.7
780 | 673 | 325.6 | 255.6 |  | 249.3 | 261.9 | 270.3 | 219.9
781 | 674 | 325.6 | 255.7 |  | 249.5 | 262 | 270.4 | 220
782 | 675 | 325.6 | 255.9 |  | 249.6 | 262 | 270.5 | 220.2
783 | 676 | 325.5 | 256.1 |  | 249.8 | 262.1 | 270.6 | 220.4
784 | 677 | 325.5 | 256.2 |  | 249.9 | 262.2 | 270.7 | 220.5
785 | 678 | 325.5 | 256.4 |  | 250.1 | 262.3 | 270.7 | 220.7
786 | 679 | 325.5 | 256.6 |  | 250.2 | 262.4 | 270.8 | 220.8
787 | 680 | 325.5 | 256.8 |  | 250.4 | 262.5 | 270.9 | 221
788 | 681 | 325.4 | 257 |  | 250.5 | 262.6 | 271 | 221.2
789 | 682 | 325.4 | 257.2 |  | 250.7 | 262.7 | 271.2 | 221.3
790 | 683 | 325.4 | 257.4 |  | 250.8 | 262.8 | 271.3 | 221.5
791 | 684 | 325.4 | 257.6 |  | 251 | 262.8 | 271.4 | 221.7
792 | 685 | 325.4 | 257.9 |  | 251.1 | 262.9 | 271.5 | 221.8
793 | 686 | 325.4 | 258.1 |  | 251.3 | 263 | 271.6 | 222
794 | 687 | 325.4 | 258.4 |  | 251.4 | 263.1 | 271.7 | 222.2
795 | 688 | 325.5 | 258.6 |  | 251.6 | 263.2 | 271.8 | 222.3
796 | 689 | 325.5 | 258.8 |  | 251.7 | 263.3 | 271.9 | 222.5
797 | 690 | 325.5 | 258.9 |  | 251.9 | 263.4 | 272 | 222.6
798 | 691 | 325.5 | 258.9 |  | 252 | 263.5 | 272.1 | 222.8
799 | 692 | 325.5 | 259 |  | 252.2 | 263.6 | 272.1 | 223
800 | 693 | 325.5 | 259 |  | 252.3 | 263.6 | 272.2 | 223.2
801 | 694 | 325.5 | 259.1 |  | 252.4 | 263.8 | 272.3 | 223.4
802 | 695 | 325.6 | 259.2 |  | 252.6 | 263.8 | 272.4 | 223.5
803 | 696 | 325.6 | 259.4 |  | 252.7 | 263.9 | 272.5 | 223.7
804 | 697 | 325.6 | 259.5 |  | 252.9 | 264 | 272.6 | 223.9
805 | 698 | 325.7 | 259.6 |  | 253 | 264.1 | 272.7 | 224.1
806 | 699 | 325.6 | 259.7 |  | 253.2 | 264.2 | 272.8 | 224.3
807 | 700 | 325.6 | 259.8 |  | 253.3 | 264.3 | 272.9 | 224.4
808 | 701 | 325.6 | 260 |  | 253.5 | 264.4 | 273 | 224.6
809 | 702 | 325.6 | 260.1 |  | 253.6 | 264.5 | 273.1 | 224.8
810 | 703 | 325.6 | 260.3 |  | 253.8 | 264.6 | 273.2 | 225
811 | 704 | 325.6 | 260.4 |  | 253.9 | 264.7 | 273.3 | 225.2
812 | 705 | 325.6 | 260.6 |  | 254 | 264.8 | 273.4 | 225.4
813 | 706 | 325.6 | 260.7 |  | 254.2 | 264.9 | 273.5 | 225.6
814 | 707 | 325.6 | 260.8 |  | 254.3 | 265 | 273.6 | 225.8
815 | 708 | 325.6 | 260.9 |  | 254.5 | 265.1 | 273.7 | 226
816 | 709 | 325.5 | 261.1 |  | 254.6 | 265.2 | 273.7 | 226.2
817 | 710 | 325.5 | 261.2 |  | 254.7 | 265.3 | 273.8 | 226.4
818 | 711 | 325.5 | 261.3 |  | 254.9 | 265.4 | 273.9 | 226.6
819 | 712 | 325.4 | 261.5 |  | 255 | 265.5 | 274 | 226.8
820 | 713 | 325.4 | 261.6 |  | 255.2 | 265.6 | 274.1 | 227
821 | 714 | 325.4 | 261.7 |  | 255.3 | 265.7 | 274.3 | 227.2
822 | 715 | 325.4 | 261.9 |  | 255.4 | 265.9 | 274.4 | 227.3
823 | 716 | 325.4 | 262.1 |  | 255.6 | 265.9 | 274.5 | 227.6
824 | 717 | 325.4 | 262.3 |  | 255.7 | 266 | 274.6 | 227.8
825 | 718 | 325.3 | 262.5 |  | 255.8 | 266.1 | 274.7 | 228
826 | 719 | 325.3 | 262.7 |  | 256 | 266.2 | 274.8 | 228.2
827 | 720 | 325.3 | 262.7 |  | 256.1 | 266.3 | 274.9 | 228.4
828 | 721 | 325.3 | 262.8 |  | 256.2 | 266.4 | 275 | 228.6
829 | 722 | 325.3 | 263.1 |  | 256.4 | 266.5 | 275.1 | 228.8
830 | 723 | 325.3 | 263.3 |  | 256.5 | 266.5 | 275.2 | 229
831 | 724 | 325.3 | 263.5 |  | 256.6 | 266.6 | 275.3 | 229.2
832 | 725 | 325.2 | 263.7 |  | 256.8 | 266.7 | 275.4 | 229.4
833 | 726 | 325.2 | 263.8 |  | 256.9 | 266.7 | 275.4 | 229.6
834 | 727 | 325.2 | 263.9 |  | 257 | 266.8 | 275.5 | 229.8
835 | 728 | 325.2 | 264.1 |  | 257.1 | 266.9 | 275.6 | 230
836 | 729 | 325.3 | 264.3 |  | 257.3 | 267 | 275.6 | 230.2
837 | 730 | 325.2 | 264.4 |  | 257.4 | 267 | 275.7 | 230.4
838 | 731 | 325.2 | 264.7 |  | 257.6 | 267.2 | 275.8 | 230.6
839 | 732 | 325.2 | 264.8 |  | 257.6 | 267.2 | 275.9 | 230.8
840 | 733 | 325.2 | 264.9 |  | 257.8 | 267.3 | 275.9 | 231.1
841 | 734 | 325.1 | 265.1 |  | 257.9 | 267.4 | 276 | 231.3
842 | 735 | 325.1 | 265.3 |  | 258.1 | 267.4 | 276.1 | 231.5
843 | 736 | 325.1 | 265.4 |  | 258.2 | 267.5 | 276.1 | 231.7
844 | 737 | 325 | 265.6 |  | 258.3 | 267.6 | 276.2 | 231.9
845 | 738 | 325 | 265.7 |  | 258.5 | 267.7 | 276.3 | 232.2
846 | 739 | 324.9 | 265.9 |  | 258.6 | 267.8 | 276.4 | 232.4
847 | 740 | 324.9 | 266 |  | 258.7 | 267.8 | 276.5 | 232.6
848 | 741 | 324.9 | 266.2 |  | 258.8 | 267.9 | 276.6 | 232.8
849 | 742 | 324.9 | 266.4 |  | 258.9 | 268 | 276.6 | 233.1
850 | 743 | 324.9 | 266.5 |  | 259 | 268.1 | 276.7 | 233.3
851 | 744 | 324.9 | 266.7 |  | 259.2 | 268.2 | 276.8 | 233.5
852 | 745 | 324.9 | 266.9 |  | 259.3 | 268.2 | 276.9 | 233.8
853 | 746 | 325 | 267.1 |  | 259.4 | 268.3 | 276.9 | 234
854 | 747 | 325 | 267.3 |  | 259.5 | 268.4 | 277 | 234.3
855 | 748 | 325 | 267.5 |  | 259.7 | 268.5 | 277.1 | 234.5
856 | 749 | 325 | 267.7 |  | 259.8 | 268.5 | 277.2 | 234.8
857 | 750 | 325 | 267.9 |  | 259.9 | 268.6 | 277.3 | 235
858 | 751 | 325 | 268 |  | 260 | 268.7 | 277.5 | 235.3
859 | 752 | 325 | 268.2 |  | 260.1 | 268.7 | 277.6 | 235.5
860 | 753 | 325 | 268.3 |  | 260.2 | 268.8 | 277.7 | 235.8
861 | 754 | 324.9 | 268.4 |  | 260.4 | 268.9 | 277.8 | 236
862 | 755 | 324.9 | 268.6 |  | 260.5 | 268.9 | 277.9 | 236.3
863 | 756 | 324.9 | 268.7 |  | 260.6 | 269 | 278 | 236.5
864 | 757 | 324.9 | 268.8 |  | 260.7 | 269.1 | 278.1 | 236.8
865 | 758 | 324.9 | 268.9 |  | 260.8 | 269.1 | 278.3 | 237.1
866 | 759 | 324.9 | 269 |  | 260.9 | 269.2 | 278.4 | 237.3
867 | 760 | 324.9 | 269.1 |  | 261 | 269.3 | 278.5 | 237.6
868 | 761 | 324.9 | 269.2 |  | 261.1 | 269.3 | 278.6 | 237.8
869 | 762 | 325 | 269.3 |  | 261.2 | 269.4 | 278.7 | 238.1
870 | 763 | 325 | 269.4 |  | 261.3 | 269.4 | 278.8 | 238.4
871 | 764 | 325 | 269.5 |  | 261.4 | 269.5 | 278.9 | 238.7
872 | 765 | 325 | 269.6 |  | 261.5 | 269.6 | 279 | 238.9
873 | 766 | 325 | 269.8 |  | 261.6 | 269.6 | 279.2 | 239.2
874 | 767 | 325 | 269.9 |  | 261.7 | 269.7 | 279.3 | 239.5
875 | 768 | 325 | 270 |  | 261.8 | 269.8 | 279.4 | 239.8
876 | 769 | 325 | 270.1 |  | 261.9 | 269.8 | 279.5 | 240.1
877 | 770 | 325 | 270.2 |  | 262 | 269.9 | 279.6 | 240.4
878 | 771 | 325 | 270.3 |  | 262.1 | 269.9 | 279.7 | 240.7
879 | 772 | 325 | 270.4 |  | 262.3 | 270 | 279.7 | 241
880 | 773 | 325 | 270.5 |  | 262.4 | 270 | 279.8 | 241.3
881 | 774 | 325.1 | 270.6 |  | 262.5 | 270.1 | 279.9 | 241.6
882 | 775 | 325.1 | 270.7 |  | 262.6 | 270.2 | 280 | 241.9
883 | 776 | 325.1 | 270.9 |  | 262.7 | 270.2 | 280.1 | 242.2
884 | 777 | 325.1 | 271 |  | 262.8 | 270.3 | 280.2 | 242.5
885 | 778 | 325.1 | 271.1 |  | 262.9 | 270.3 | 280.3 | 242.8
886 | 779 | 325.1 | 271.2 |  | 263 | 270.4 | 280.4 | 243.1
887 | 780 | 325.1 | 271.3 |  | 263.1 | 270.5 | 280.4 | 243.4
888 | 781 | 325.1 | 271.4 |  | 263.2 | 270.5 | 280.5 | 243.7
889 | 782 | 325.1 | 271.5 |  | 263.3 | 270.6 | 280.6 | 244
890 | 783 | 325.1 | 271.5 |  | 263.4 | 270.7 | 280.6 | 244.3
891 | 784 | 325.1 | 271.6 |  | 263.5 | 270.7 | 280.7 | 244.6
892 | 785 | 325.1 | 271.6 |  | 263.6 | 270.8 | 280.8 | 244.9
893 | 786 | 325.1 | 271.7 |  | 263.7 | 270.8 | 280.9 | 245.2
894 | 787 | 325.1 | 271.8 |  | 263.8 | 270.9 | 280.9 | 245.5
895 | 788 | 325.1 | 271.9 |  | 263.9 | 271 | 281 | 245.9
896 | 789 | 325.1 | 271.9 |  | 264 | 271 | 281.1 | 246.2
897 | 790 | 325.1 | 272 |  | 264.1 | 271.1 | 281.2 | 246.5
898 | 791 | 325.1 | 272.1 |  | 264.2 | 271.1 | 281.3 | 246.8
899 | 792 | 325 | 272.1 |  | 264.3 | 271.2 | 281.3 | 247.1
900 | 793 | 325 | 272.2 |  | 264.4 | 271.3 | 281.4 | 247.4
901 | 794 | 325 | 272.3 |  | 264.5 | 271.3 | 281.5 | 247.7
902 | 795 | 325 | 272.3 |  | 264.5 | 271.4 | 281.5 | 247.9
903 | 796 | 325 | 272.4 |  | 264.6 | 271.4 | 281.6 | 248.2
904 | 797 | 324.9 | 272.4 |  | 264.7 | 271.5 | 281.7 | 248.5
905 | 798 | 324.9 | 272.5 |  | 264.8 | 271.5 | 281.8 | 248.8
906 | 799 | 324.9 | 272.6 |  | 264.9 | 271.6 | 281.8 | 249.1
907 | 800 | 324.9 | 272.7 |  | 265 | 271.6 | 281.9 | 249.4
908 | 801 | 324.9 | 272.8 |  | 265 | 271.7 | 282 | 249.7
909 | 802 | 324.9 | 272.9 |  | 265.1 | 271.8 | 282.1 | 250
910 | 803 | 324.9 | 273 |  | 265.2 | 271.8 | 282.1 | 250.2
911 | 804 | 324.9 | 273.1 |  | 265.3 | 271.9 | 282.2 | 250.5
912 | 805 | 324.9 | 273.2 |  | 265.4 | 271.9 | 282.3 | 250.8
913 | 806 | 324.8 | 273.2 |  | 265.5 | 272 | 282.4 | 251
914 | 807 | 324.8 | 273.3 |  | 265.5 | 272.1 | 282.5 | 251.3
915 | 808 | 324.8 | 273.4 |  | 265.6 | 272.1 | 282.5 | 251.6
916 | 809 | 324.8 | 273.5 |  | 265.7 | 272.2 | 282.6 | 251.9
917 | 810 | 324.7 | 273.6 |  | 265.8 | 272.2 | 282.8 | 252.1
918 | 811 | 324.7 | 273.7 |  | 265.9 | 272.3 | 282.9 | 252.4
919 | 812 | 324.7 | 273.8 |  | 266 | 272.4 | 283 | 252.7
920 | 813 | 324.8 | 273.8 |  | 266 | 272.4 | 283.2 | 252.9
921 | 814 | 324.8 | 273.9 |  | 266.1 | 272.5 | 283.3 | 253.2
922 | 815 | 324.8 | 274 |  | 266.2 | 272.5 | 283.4 | 253.4
923 | 816 | 324.8 | 274.1 |  | 266.3 | 272.6 | 283.5 | 253.7
924 | 817 | 324.8 | 274.2 |  | 266.4 | 272.7 | 283.6 | 254
925 | 818 | 324.8 | 274.3 |  | 266.5 | 272.7 | 283.6 | 254.2
926 | 819 | 324.8 | 274.3 |  | 266.6 | 272.8 | 283.7 | 254.4
927 | 820 | 324.8 | 274.4 |  | 266.6 | 272.9 | 283.8 | 254.7
928 | 821 | 324.8 | 274.5 |  | 266.7 | 272.9 | 283.9 | 254.9
929 | 822 | 324.8 | 274.6 |  | 266.8 | 273 | 284 | 255.2
930 | 823 | 324.8 | 274.7 |  | 266.9 | 273.1 | 284 | 255.4
931 | 824 | 324.8 | 274.7 |  | 266.9 | 273.2 | 284.1 | 255.6
932 | 825 | 324.9 | 274.8 |  | 267 | 273.2 | 284.2 | 255.8
933 | 826 | 324.9 | 274.9 |  | 267.1 | 273.3 | 284.3 | 256.1
934 | 827 | 324.9 | 274.9 |  | 267.2 | 273.4 | 284.3 | 256.3
935 | 828 | 324.9 | 275 |  | 267.3 | 273.5 | 284.4 | 256.5
936 | 829 | 324.9 | 275 |  | 267.3 | 273.5 | 284.5 | 256.7
937 | 830 | 324.9 | 275.1 |  | 267.4 | 273.6 | 284.5 | 256.9
938 | 831 | 324.9 | 275.1 |  | 267.5 | 273.7 | 284.6 | 257.1
939 | 832 | 324.9 | 275.1 |  | 267.6 | 273.8 | 284.7 | 257.3
940 | 833 | 324.9 | 275.2 |  | 267.7 | 273.9 | 284.8 | 257.5
941 | 834 | 324.9 | 275.2 |  | 267.7 | 274 | 284.8 | 257.7
942 | 835 | 324.9 | 275.3 |  | 267.8 | 274.1 | 284.9 | 257.9
943 | 836 | 324.9 | 275.4 |  | 267.9 | 274.1 | 285 | 258.1
944 | 837 | 324.9 | 275.5 |  | 267.9 | 274.2 | 285 | 258.3
945 | 838 | 324.9 | 275.6 |  | 268 | 274.3 | 285.1 | 258.5
946 | 839 | 324.9 | 275.6 |  | 268.1 | 274.4 | 285.2 | 258.7
947 | 840 | 324.9 | 275.7 |  | 268.1 | 274.5 | 285.2 | 258.8
948 | 841 | 324.9 | 275.7 |  | 268.2 | 274.6 | 285.3 | 259
949 | 842 | 325 | 275.8 |  | 268.3 | 274.6 | 285.4 | 259.2
950 | 843 | 325 | 275.9 |  | 268.3 | 274.7 | 285.5 | 259.4
951 | 844 | 325 | 276 |  | 268.4 | 274.8 | 285.5 | 259.5
952 | 845 | 325 | 276 |  | 268.5 | 274.9 | 285.6 | 259.7
953 | 846 | 325 | 276.1 |  | 268.5 | 275 | 285.7 | 259.8
954 | 847 | 325 | 276.2 |  | 268.6 | 275.1 | 285.7 | 260
955 | 848 | 325 | 276.2 |  | 268.7 | 275.2 | 285.8 | 260.2
956 | 849 | 324.9 | 276.3 |  | 268.7 | 275.2 | 285.9 | 260.3
957 | 850 | 325 | 276.4 |  | 268.8 | 275.3 | 286 | 260.5
958 | 851 | 324.9 | 276.5 |  | 268.9 | 275.4 | 286.1 | 260.6
959 | 852 | 325 | 276.6 |  | 268.9 | 275.5 | 286.1 | 260.8
960 | 853 | 325 | 276.6 |  | 269 | 275.5 | 286.2 | 260.9
961 | 854 | 325 | 276.7 |  | 269.1 | 275.6 | 286.3 | 261.1
962 | 855 | 325 | 276.8 |  | 269.1 | 275.7 | 286.4 | 261.2
963 | 856 | 325 | 276.8 |  | 269.2 | 275.8 | 286.5 | 261.4
964 | 857 | 325 | 276.9 |  | 269.2 | 275.9 | 286.5 | 261.5
965 | 858 | 325 | 277 |  | 269.3 | 276 | 286.6 | 261.7
966 | 859 | 325 | 277 |  | 269.4 | 276.1 | 286.7 | 261.8
967 | 860 | 325 | 277.1 |  | 269.4 | 276.2 | 286.7 | 261.9
968 | 861 | 325 | 277.2 |  | 269.5 | 276.3 | 286.7 | 262
969 | 862 | 324.9 | 277.3 |  | 269.6 | 276.4 | 286.8 | 262.2
970 | 863 | 324.9 | 277.3 |  | 269.6 | 276.5 | 286.9 | 262.3
971 | 864 | 324.9 | 277.4 |  | 269.7 | 276.5 | 286.9 | 262.4
972 | 865 | 324.9 | 277.4 |  | 269.7 | 276.6 | 287 | 262.5
973 | 866 | 324.9 | 277.5 |  | 269.8 | 276.7 | 287.1 | 262.6
974 | 867 | 324.9 | 277.5 |  | 269.8 | 276.9 | 287.1 | 262.8
975 | 868 | 324.9 | 277.6 |  | 269.9 | 276.9 | 287.2 | 262.9
976 | 869 | 324.9 | 277.6 |  | 270 | 277 | 287.2 | 263
977 | 870 | 324.9 | 277.7 |  | 270 | 277.1 | 287.3 | 263.1
978 | 871 | 324.9 | 277.7 |  | 270.1 | 277.2 | 287.4 | 263.2
979 | 872 | 324.9 | 277.8 |  | 270.1 | 277.3 | 287.4 | 263.3
980 | 873 | 324.9 | 277.9 |  | 270.2 | 277.4 | 287.5 | 263.5
981 | 874 | 324.9 | 277.9 |  | 270.3 | 277.5 | 287.5 | 263.6
982 | 875 | 324.9 | 278 |  | 270.3 | 277.6 | 287.6 | 263.7
983 | 876 | 324.9 | 278 |  | 270.4 | 277.7 | 287.6 | 263.8
984 | 877 | 324.9 | 278.1 |  | 270.4 | 277.8 | 287.7 | 263.9
985 | 878 | 324.9 | 278.2 |  | 270.5 | 277.9 | 287.8 | 264
986 | 879 | 324.9 | 278.3 |  | 270.6 | 278 | 287.8 | 264.1
987 | 880 | 324.9 | 278.4 |  | 270.6 | 278.1 | 287.8 | 264.2
988 | 881 | 324.9 | 278.4 |  | 270.7 | 278.1 | 287.9 | 264.3
989 | 882 | 324.9 | 278.5 |  | 270.7 | 278.2 | 287.9 | 264.4
990 | 883 | 324.9 | 278.5 |  | 270.8 | 278.3 | 288 | 264.6
991 | 884 | 324.9 | 278.6 |  | 270.9 | 278.3 | 288 | 264.6
992 | 885 | 324.9 | 278.6 |  | 271 | 278.4 | 288.1 | 264.7
993 | 886 | 324.9 | 278.6 |  | 271 | 278.5 | 288.1 | 264.9
994 | 887 | 324.9 | 278.7 |  | 271.1 | 278.5 | 288.2 | 265
995 | 888 | 324.9 | 278.7 |  | 271.1 | 278.6 | 288.2 | 265.1
996 | 889 | 324.9 | 278.7 |  | 271.2 | 278.6 | 288.3 | 265.2
997 | 890 | 324.9 | 278.8 |  | 271.2 | 278.7 | 288.3 | 265.2
998 | 891 | 324.9 | 278.8 |  | 271.3 | 278.8 | 288.3 | 265.3
999 | 892 | 324.9 | 278.9 |  | 271.4 | 278.8 | 288.4 | 265.4
1000 | 893 | 324.9 | 278.9 |  | 271.4 | 278.9 | 288.4 | 265.5
1001 | 894 | 324.9 | 278.9 |  | 271.5 | 278.9 | 288.4 | 265.6
1002 | 895 | 324.9 | 279 |  | 271.5 | 279 | 288.4 | 265.7
1003 | 896 | 324.9 | 279 |  | 271.6 | 279.1 | 288.5 | 265.8
1004 | 897 | 324.9 | 279.1 |  | 271.6 | 279.1 | 288.5 | 265.9
1005 | 898 | 324.9 | 279.1 |  | 271.7 | 279.2 | 288.5 | 266
1006 | 899 | 325 | 279.1 |  | 271.8 | 279.2 | 288.5 | 266
1007 | 900 | 324.9 | 279.2 |  | 271.8 | 279.3 | 288.5 | 266.1
1008 | 901 | 324.9 | 279.2 |  | 271.9 | 279.3 | 288.6 | 266.2
1009 | 902 | 324.9 | 279.2 |  | 272 | 279.4 | 288.6 | 266.3
1010 | 903 | 324.9 | 279.3 |  | 272 | 279.4 | 288.6 | 266.3
1011 | 904 | 324.9 | 279.3 |  | 272.1 | 279.5 | 288.7 | 266.4
1012 | 905 | 324.9 | 279.4 |  | 272.1 | 279.6 | 288.7 | 266.5
1013 | 906 | 325 | 279.4 |  | 272.2 | 279.6 | 288.8 | 266.6
1014 | 907 | 325 | 279.4 |  | 272.3 | 279.7 | 288.8 | 266.6
1015 | 908 | 325 | 279.5 |  | 272.3 | 279.7 | 288.8 | 266.7
1016 | 909 | 325 | 279.5 |  | 272.4 | 279.8 | 288.9 | 266.8
1017 | 910 | 325.1 | 279.6 |  | 272.4 | 279.8 | 288.9 | 266.9
1018 | 911 | 325.1 | 279.6 |  | 272.5 | 279.9 | 288.9 | 266.9
1019 | 912 | 325.1 | 279.6 |  | 272.5 | 279.9 | 288.9 | 267
1020 | 913 | 325.1 | 279.7 |  | 272.6 | 280 | 288.9 | 267.1
1021 | 914 | 325.1 | 279.7 |  | 272.7 | 280 | 288.9 | 267.1
1022 | 915 | 325.1 | 279.8 |  | 272.7 | 280.1 | 289 | 267.2
1023 | 916 | 325.1 | 279.8 |  | 272.8 | 280.1 | 289 | 267.3
1024 | 917 | 325.1 | 279.9 |  | 272.8 | 280.2 | 289 | 267.3
1025 | 918 | 325.1 | 279.9 |  | 272.9 | 280.2 | 289 | 267.4
1026 | 919 | 325.1 | 280 |  | 273 | 280.3 | 289.1 | 267.5
1027 | 920 | 325.1 | 280 |  | 273 | 280.3 | 289.1 | 267.5
1028 | 921 | 325.1 | 280.1 |  | 273.1 | 280.3 | 289.1 | 267.6
1029 | 922 | 325.1 | 280.1 |  | 273.1 | 280.4 | 289.1 | 267.7
1030 | 923 | 325.2 | 280.2 |  | 273.2 | 280.4 | 289.2 | 267.7
1031 | 924 | 325.1 | 280.3 |  | 273.2 | 280.5 | 289.2 | 267.8
1032 | 925 | 325.1 | 280.3 |  | 273.3 | 280.5 | 289.2 | 267.8
1033 | 926 | 325.1 | 280.4 |  | 273.3 | 280.5 | 289.2 | 267.9
1034 | 927 | 325.1 | 280.4 |  | 273.4 | 280.6 | 289.2 | 268
1035 | 928 | 325.1 | 280.5 |  | 273.5 | 280.6 | 289.3 | 268
1036 | 929 | 325.1 | 280.5 |  | 273.5 | 280.7 | 289.3 | 268.1
1037 | 930 | 325.1 | 280.6 |  | 273.6 | 280.7 | 289.3 | 268.1
1038 | 931 | 325.1 | 280.6 |  | 273.6 | 280.8 | 289.3 | 268.2
1039 | 932 | 325.1 | 280.6 |  | 273.7 | 280.8 | 289.3 | 268.3
1040 | 933 | 325.1 | 280.7 |  | 273.7 | 280.8 | 289.4 | 268.3
1041 | 934 | 325.1 | 280.7 |  | 273.8 | 280.9 | 289.4 | 268.4
1042 | 935 | 325 | 280.7 |  | 273.8 | 280.9 | 289.4 | 268.4
1043 | 936 | 325 | 280.8 |  | 273.9 | 281 | 289.5 | 268.5
1044 | 937 | 325.1 | 280.8 |  | 273.9 | 281 | 289.5 | 268.6
1045 | 938 | 325.1 | 280.9 |  | 274 | 281.1 | 289.5 | 268.6
1046 | 939 | 325.1 | 280.9 |  | 274.1 | 281.1 | 289.6 | 268.7
1047 | 940 | 325.1 | 280.9 |  | 274.1 | 281.2 | 289.6 | 268.8
1048 | 941 | 325.1 | 281 |  | 274.2 | 281.2 | 289.6 | 268.8
1049 | 942 | 325 | 281 |  | 274.2 | 281.3 | 289.6 | 268.9
1050 | 943 | 325 | 281 |  | 274.3 | 281.3 | 289.7 | 269
1051 | 944 | 325 | 281.1 |  | 274.3 | 281.3 | 289.7 | 269
1052 | 945 | 325 | 281.1 |  | 274.4 | 281.4 | 289.7 | 269.1
1053 | 946 | 325 | 281.2 |  | 274.5 | 281.4 | 289.8 | 269.2
1054 | 947 | 325 | 281.2 |  | 274.5 | 281.5 | 289.8 | 269.2
1055 | 948 | 325 | 281.3 |  | 274.6 | 281.5 | 289.8 | 269.3
1056 | 949 | 325 | 281.3 |  | 274.7 | 281.6 | 289.8 | 269.3
1057 | 950 | 325 | 281.4 |  | 274.7 | 281.6 | 289.8 | 269.4
1058 | 951 | 324.9 | 281.4 |  | 274.8 | 281.7 | 289.9 | 269.4
1059 | 952 | 324.9 | 281.4 |  | 274.8 | 281.7 | 289.9 | 269.5
1060 | 953 | 324.9 | 281.5 |  | 274.9 | 281.7 | 289.9 | 269.5
1061 | 954 | 324.9 | 281.6 |  | 274.9 | 281.8 | 289.9 | 269.6
1062 | 955 | 324.9 | 281.6 |  | 275 | 281.8 | 290 | 269.6
1063 | 956 | 324.9 | 281.7 |  | 275 | 281.9 | 290 | 269.7
1064 | 957 | 324.8 | 281.7 |  | 275.1 | 281.9 | 290 | 269.7
1065 | 958 | 324.8 | 281.7 |  | 275.1 | 281.9 | 290 | 269.8
1066 | 959 | 324.8 | 281.8 |  | 275.2 | 282 | 290 | 269.8
1067 | 960 | 324.8 | 281.8 |  | 275.2 | 282 | 290 | 269.8
1068 | 961 | 324.7 | 281.8 |  | 275.3 | 282.1 | 290 | 269.9
1069 | 962 | 324.7 | 281.9 |  | 275.3 | 282.1 | 290 | 269.9
1070 | 963 | 324.6 | 281.9 |  | 275.4 | 282.1 | 290.1 | 270
1071 | 964 | 324.6 | 281.9 |  | 275.5 | 282.2 | 290.1 | 270
1072 | 965 | 324.6 | 282 |  | 275.5 | 282.2 | 290.1 | 270
1073 | 966 | 324.6 | 282 |  | 275.6 | 282.3 | 290.1 | 270.1
1074 | 967 | 324.5 | 282.1 |  | 275.6 | 282.3 | 290.1 | 270.1
1075 | 968 | 324.5 | 282.1 |  | 275.7 | 282.4 | 290.1 | 270.1
1076 | 969 | 324.5 | 282.1 |  | 275.7 | 282.4 | 290.1 | 270.2
1077 | 970 | 324.5 | 282.1 |  | 275.8 | 282.4 | 290.2 | 270.2
1078 | 971 | 324.4 | 282.1 |  | 275.8 | 282.5 | 290.2 | 270.3
1079 | 972 | 324.4 | 282.2 |  | 275.9 | 282.5 | 290.2 | 270.3
1080 | 973 | 324.4 | 282.2 |  | 275.9 | 282.6 | 290.2 | 270.3
1081 | 974 | 324.4 | 282.3 |  | 276 | 282.6 | 290.2 | 270.4
1082 | 975 | 324.4 | 282.3 |  | 276 | 282.6 | 290.2 | 270.4
1083 | 976 | 324.4 | 282.4 |  | 276.1 | 282.7 | 290.2 | 270.4
1084 | 977 | 324.4 | 282.5 |  | 276.1 | 282.7 | 290.2 | 270.5
1085 | 978 | 324.4 | 282.5 |  | 276.1 | 282.8 | 290.3 | 270.5
1086 | 979 | 324.4 | 282.6 |  | 276.2 | 282.8 | 290.3 | 270.5
1087 | 980 | 324.4 | 282.6 |  | 276.2 | 282.8 | 290.3 | 270.6
1088 | 981 | 324.4 | 282.6 |  | 276.3 | 282.9 | 290.3 | 270.6
1089 | 982 | 324.4 | 282.7 |  | 276.3 | 282.9 | 290.4 | 270.6
1090 | 983 | 324.4 | 282.7 |  | 276.4 | 283 | 290.4 | 270.7
1091 | 984 | 324.5 | 282.8 |  | 276.5 | 283 | 290.5 | 270.7
1092 | 985 | 324.4 | 282.8 |  | 276.5 | 283.1 | 290.5 | 270.7
1093 | 986 | 324.4 | 282.8 |  | 276.6 | 283.1 | 290.5 | 270.8
1094 | 987 | 324.4 | 282.9 |  | 276.6 | 283.2 | 290.5 | 270.8
1095 | 988 | 324.4 | 282.9 |  | 276.7 | 283.2 | 290.5 | 270.8
1096 | 989 | 324.5 | 283 |  | 276.7 | 283.2 | 290.5 | 270.9
1097 | 990 | 324.5 | 283 |  | 276.8 | 283.3 | 290.5 | 270.9
1098 | 991 | 324.5 | 283.1 |  | 276.8 | 283.3 | 290.6 | 270.9
1099 | 992 | 324.5 | 283.2 |  | 276.8 | 283.4 | 290.6 | 271
1100 | 993 | 324.4 | 283.5 |  | 277.1 | 283.6 | 290.7 | 271
1101 | 994 | 324.5 | 283.2 |  | 276.9 | 283.4 | 290.6 | 271
1102 | 995 | 324.5 | 283.3 |  | 277 | 283.5 | 290.6 | 271.1
1103 | 996 | 324.5 | 283.3 |  | 277.1 | 283.5 | 290.6 | 271.1
1104 | 997 | 324.6 | 283.4 |  | 277.1 | 283.5 | 290.6 | 271.1
1105 | 998 | 324.6 | 283.4 |  | 277.2 | 283.6 | 290.6 | 271.1
1106 | 999 | 324.6 | 283.5 |  | 277.2 | 283.6 | 290.6 | 271.2
1107 | 1000 | 324.6 | 283.5 |  | 277.3 | 283.7 | 290.7 | 271.2
1108 | 1001 | 324.6 | 283.5 |  | 277.3 | 283.7 | 290.7 | 271.2
1109 | 1002 | 324.7 | 283.6 |  | 277.4 | 283.7 | 290.7 | 271.3
1110 | 1003 | 324.7 | 283.6 |  | 277.4 | 283.7 | 290.7 | 271.3
1111 | 1004 | 324.7 | 283.7 |  | 277.4 | 283.8 | 290.8 | 271.3
1112 | 1005 | 324.7 | 283.7 |  | 277.5 | 283.8 | 290.8 | 271.4
1113 | 1006 | 324.7 | 283.8 |  | 277.5 | 283.8 | 290.8 | 271.4
1114 | 1007 | 324.7 | 283.8 |  | 277.6 | 283.9 | 290.8 | 271.4
1115 | 1008 | 324.7 | 283.9 |  | 277.6 | 283.9 | 290.9 | 271.5
1116 | 1009 | 324.7 | 283.9 |  | 277.7 | 283.9 | 290.9 | 271.5
1117 | 1010 | 324.7 | 284.1 |  | 277.8 | 284.1 | 291 | 271.5
1118 | 1011 | 324.7 | 284 |  | 277.8 | 284 | 290.9 | 271.6
1119 | 1012 | 324.8 | 284 |  | 277.8 | 284 | 290.9 | 271.6
1120 | 1013 | 324.8 | 284.1 |  | 277.9 | 284.1 | 291 | 271.7
1121 | 1014 | 324.8 | 284.2 |  | 277.9 | 284.1 | 291 | 271.7
1122 | 1015 | 324.9 | 284.2 |  | 278 | 284.1 | 291 | 271.7
1123 | 1016 | 324.9 | 284.2 |  | 278 | 284.2 | 291 | 271.8
1124 | 1017 | 324.9 | 284.3 |  | 278.1 | 284.2 | 291.1 | 271.8
1125 | 1018 | 324.9 | 284.4 |  | 278.1 | 284.2 | 291.1 | 271.9
1126 | 1019 | 324.9 | 284.4 |  | 278.2 | 284.3 | 291.1 | 271.9
1127 | 1020 | 324.9 | 284.4 |  | 278.3 | 284.3 | 291.1 | 271.9
1128 | 1021 | 324.9 | 284.5 |  | 278.3 | 284.4 | 291.2 | 272
1129 | 1022 | 324.9 | 284.6 |  | 278.3 | 284.4 | 291.2 | 272
1130 | 1023 | 324.9 | 284.6 |  | 278.4 | 284.4 | 291.2 | 272
1131 | 1024 | 324.9 | 284.7 |  | 278.4 | 284.5 | 291.2 | 272.1
1132 | 1025 | 324.9 | 284.7 |  | 278.5 | 284.5 | 291.2 | 272.1
1133 | 1026 | 324.9 | 284.8 |  | 278.5 | 284.5 | 291.2 | 272.1
1134 | 1027 | 324.9 | 284.8 |  | 278.6 | 284.6 | 291.2 | 272.1
1135 | 1028 | 324.9 | 284.9 |  | 278.6 | 284.6 | 291.3 | 272.2
1136 | 1029 | 324.8 | 284.9 |  | 278.7 | 284.7 | 291.3 | 272.2
1137 | 1030 | 324.9 | 285 |  | 278.7 | 284.7 | 291.3 | 272.2
1138 | 1031 | 324.9 | 285 |  | 278.8 | 284.7 | 291.3 | 272.2
1139 | 1032 | 324.9 | 285.1 |  | 278.8 | 284.8 | 291.4 | 272.3
1140 | 1033 | 324.9 | 285.1 |  | 278.9 | 284.8 | 291.4 | 272.3
1141 | 1034 | 324.9 | 285.2 |  | 278.9 | 284.8 | 291.4 | 272.3
1142 | 1035 | 324.9 | 285.2 |  | 279 | 284.9 | 291.4 | 272.4
1143 | 1036 | 324.8 | 285.3 |  | 279 | 284.9 | 291.4 | 272.4
1144 | 1037 | 324.8 | 285.4 |  | 279 | 285 | 291.4 | 272.4
1145 | 1038 | 324.8 | 285.4 |  | 279.1 | 285 | 291.4 | 272.4
1146 | 1039 | 324.8 | 285.5 |  | 279.1 | 285 | 291.5 | 272.5
1147 | 1040 | 324.8 | 285.5 |  | 279.2 | 285.1 | 291.5 | 272.5
1148 | 1041 | 324.8 | 285.5 |  | 279.2 | 285.1 | 291.5 | 272.5
1149 | 1042 | 324.8 | 285.6 |  | 279.3 | 285.2 | 291.5 | 272.5
1150 | 1043 | 324.8 | 285.7 |  | 279.3 | 285.2 | 291.5 | 272.6
1151 | 1044 | 324.8 | 285.7 |  | 279.3 | 285.2 | 291.5 | 272.6
1152 | 1045 | 324.8 | 285.7 |  | 279.4 | 285.3 | 291.5 | 272.6
1153 | 1046 | 324.8 | 285.8 |  | 279.4 | 285.3 | 291.6 | 272.6
1154 | 1047 | 324.8 | 285.8 |  | 279.5 | 285.4 | 291.6 | 272.7
1155 | 1048 | 324.7 | 285.9 |  | 279.5 | 285.4 | 291.7 | 272.7
1156 | 1049 | 324.7 | 285.9 |  | 279.6 | 285.4 | 291.7 | 272.7
1157 | 1050 | 324.7 | 285.9 |  | 279.6 | 285.5 | 291.8 | 272.7
1158 | 1051 | 324.7 | 286 |  | 279.7 | 285.5 | 291.8 | 272.8
1159 | 1052 | 324.7 | 286 |  | 279.7 | 285.5 | 291.8 | 272.8
1160 | 1053 | 324.7 | 286.1 |  | 279.8 | 285.6 | 291.8 | 272.8
1161 | 1054 | 324.7 | 286.1 |  | 279.8 | 285.6 | 291.9 | 272.8
1162 | 1055 | 324.8 | 286.2 |  | 279.8 | 285.7 | 291.9 | 272.9
1163 | 1056 | 324.8 | 286.3 |  | 279.9 | 285.7 | 291.9 | 272.9
1164 | 1057 | 324.7 | 286.3 |  | 279.9 | 285.7 | 291.9 | 272.9
1165 | 1058 | 324.8 | 286.4 |  | 280 | 285.7 | 291.9 | 273
1166 | 1059 | 324.5 | 286.9 |  | 280.9 | 286.6 | 292.3 | 272.9
1167 | 1060 | 324.8 | 286.5 |  | 280.1 | 285.8 | 292 | 273
1168 | 1061 | 324.8 | 286.5 |  | 280.1 | 285.8 | 292 | 273
1169 | 1062 | 324.7 | 286.5 |  | 280.2 | 285.9 | 292 | 273
1170 | 1063 | 324.7 | 286.6 |  | 280.2 | 285.9 | 292 | 273.1
1171 | 1064 | 324.7 | 286.7 |  | 280.2 | 286 | 292 | 273.1
1172 | 1065 | 324.8 | 286.7 |  | 280.3 | 286 | 292 | 273.1
1173 | 1066 | 324.4 | 287.7 |  | 281 | 287 | 292.5 | 273
1174 | 1067 | 324.5 | 287.5 |  | 281.1 | 287 | 292.5 | 273
1175 | 1068 | 324.7 | 286.9 |  | 280.4 | 286.1 | 292.1 | 273.2
1176 | 1069 | 324.7 | 286.9 |  | 280.4 | 286.1 | 292 | 273.2
1177 | 1070 | 324.7 | 287 |  | 280.5 | 286.2 | 292.1 | 273.2
1178 | 1071 | 324.7 | 287 |  | 280.6 | 286.2 | 292.1 | 273.2
1179 | 1072 | 324.7 | 287 |  | 280.6 | 286.2 | 292.1 | 273.2
1180 | 1073 | 324.7 | 287.1 |  | 280.6 | 286.3 | 292.1 | 273.2
1181 | 1074 | 324.6 | 287.2 |  | 280.8 | 286.4 | 292.2 | 273.3
1182 | 1075 | 323.7 | 288.2 |  | 283.2 | 288 | 293 | 273.2
1183 | 1076 | 324.4 | 287.7 |  | 281.6 | 287.1 | 292.5 | 273.2
1184 | 1077 | 324.7 | 287.3 |  | 280.8 | 286.4 | 292.2 | 273.3
1185 | 1078 | 324.7 | 287.3 |  | 280.9 | 286.4 | 292.2 | 273.3
1186 | 1079 | 324.7 | 287.4 |  | 280.9 | 286.5 | 292.2 | 273.4
1187 | 1080 | 324.8 | 287.5 |  | 280.9 | 286.5 | 292.2 | 273.4
1188 | 1081 | 324.8 | 287.6 |  | 281 | 286.5 | 292.2 | 273.4
1189 | 1082 | 324.3 | 288.3 |  | 281.5 | 287.2 | 292.5 | 273.4
1190 | 1083 | 324.5 | 288.8 |  | 281.9 | 287.7 | 292.8 | 273.3
1191 | 1084 | 324.8 | 287.8 |  | 281.1 | 286.7 | 292.2 | 273.4
1192 | 1085 | 324.8 | 287.8 |  | 281.2 | 286.7 | 292.2 | 273.5
1193 | 1086 | 324.8 | 287.9 |  | 281.2 | 286.7 | 292.2 | 273.5
1194 | 1087 | 324.8 | 288 |  | 281.2 | 286.7 | 292.3 | 273.5
1195 | 1088 | 324.8 | 288.1 |  | 281.3 | 286.8 | 292.3 | 273.5
1196 | 1089 | 324.8 | 288.1 |  | 281.3 | 286.8 | 292.3 | 273.6
1197 | 1090 | 324.8 | 288.2 |  | 281.4 | 286.8 | 292.3 | 273.6
1198 | 1091 | 324.6 | 288.7 |  | 281.8 | 287.2 | 292.5 | 273.6
1199 | 1092 | 324.8 | 288.4 |  | 281.5 | 286.9 | 292.3 | 273.6
1200 | 1093 | 324.7 | 288.5 |  | 281.5 | 286.9 | 292.3 | 273.6
1201 | 1094 | 324.7 | 288.6 |  | 281.6 | 286.9 | 292.3 | 273.6
1202 | 1095 | 324.8 | 288.6 |  | 281.6 | 287 | 292.3 | 273.7
1203 | 1096 | 324.8 | 288.7 |  | 281.6 | 287 | 292.3 | 273.7
1204 | 1097 | 324.4 | 289.8 |  | 282.5 | 288 | 292.7 | 273.6
1205 | 1098 | 324.8 | 288.9 |  | 281.7 | 287.1 | 292.3 | 273.7
1206 | 1099 | 324.8 | 289 |  | 281.8 | 287.1 | 292.3 | 273.7
1207 | 1100 | 324.8 | 289.1 |  | 281.7 | 287.1 | 292.3 | 273.7
1208 | 1101 | 324.8 | 289.2 |  | 281.8 | 287.1 | 292.3 | 273.7
1209 | 1102 | 324.8 | 289.3 |  | 281.8 | 287.1 | 292.3 | 273.8
1210 | 1103 | 324.8 | 289.3 |  | 281.8 | 287.2 | 292.3 | 273.8
1211 | 1104 | 324.8 | 289.4 |  | 281.9 | 287.2 | 292.3 | 273.8
1212 | 1105 | 324.8 | 289.5 |  | 281.9 | 287.2 | 292.3 | 273.8
1213 | 1106 | 324.8 | 289.6 |  | 282 | 287.3 | 292.3 | 273.8
1214 | 1107 | 324.8 | 289.7 |  | 282 | 287.3 | 292.3 | 273.8
1215 | 1108 | 324.8 | 289.7 |  | 282.1 | 287.3 | 292.3 | 273.9
1216 | 1109 | 324.7 | 290.1 |  | 282.3 | 287.6 | 292.4 | 273.9
1217 | 1110 | 324.4 | 291.2 |  | 283.2 | 288.6 | 292.9 | 273.8
1218 | 1111 | 324.8 | 290 |  | 282.2 | 287.4 | 292.3 | 273.9
1219 | 1112 | 324.8 | 290 |  | 282.2 | 287.4 | 292.4 | 273.9
1220 | 1113 | 324.8 | 290.1 |  | 282.3 | 287.5 | 292.4 | 274
1221 | 1114 | 324.8 | 290.2 |  | 282.3 | 287.5 | 292.4 | 274
1222 | 1115 | 324.8 | 290.6 |  | 282.6 | 287.8 | 292.5 | 274
1223 | 1116 | 324.9 | 290.4 |  | 282.4 | 287.6 | 292.4 | 274
1224 | 1117 | 324.9 | 290.4 |  | 282.4 | 287.6 | 292.4 | 274
1225 | 1118 | 324.9 | 290.5 |  | 282.5 | 287.6 | 292.4 | 274
1226 | 1119 | 324.9 | 290.6 |  | 282.5 | 287.6 | 292.4 | 274
1227 | 1120 | 324.9 | 290.6 |  | 282.6 | 287.7 | 292.4 | 274
1228 | 1121 | 324.8 | 290.8 |  | 282.7 | 287.8 | 292.5 | 274
1229 | 1122 | 324.3 | 292.9 |  | 284.3 | 289.9 | 293.5 | 273.9
1230 | 1123 | 324.6 | 291.6 |  | 283.3 | 288.5 | 292.8 | 274
1231 | 1124 | 324.5 | 291.8 |  | 283.5 | 288.6 | 292.8 | 274
1232 | 1125 | 323.9 | 293.1 |  | 284.5 | 290.1 | 293.5 | 273.9
1233 | 1126 | 324.5 | 291.8 |  | 283.5 | 288.8 | 293.1 | 274
1234 | 1127 | 324.7 | 291.1 |  | 282.9 | 288 | 292.7 | 274.1
1235 | 1128 | 324.3 | 292 |  | 283.7 | 288.9 | 293.1 | 274
1236 | 1129 | 324.5 | 291.5 |  | 283.3 | 288.3 | 292.8 | 274.1
1237 | 1130 | 324.4 | 292.1 |  | 283.7 | 288.9 | 293.1 | 274.1
1238 | 1131 | 324.5 | 291.8 |  | 283.5 | 288.7 | 292.9 | 274.1
1239 | 1132 | 324.6 | 291.5 |  | 283.3 | 288.3 | 292.7 | 274.1
1240 | 1133 | 324.6 | 291.4 |  | 283.1 | 288.1 | 292.7 | 274.2
1241 | 1134 | 324.6 | 291.4 |  | 283.1 | 288.2 | 292.7 | 274.2
1242 | 1135 | 324.6 | 291.5 |  | 283.2 | 288.2 | 292.7 | 274.2
1243 | 1136 | 324.6 | 291.5 |  | 283.2 | 288.2 | 292.7 | 274.2
1244 | 1137 | 324.6 | 291.6 |  | 283.3 | 288.2 | 292.7 | 274.2
1245 | 1138 | 324.5 | 291.6 |  | 283.3 | 288.3 | 292.7 | 274.2
1246 | 1139 | 324.5 | 291.7 |  | 283.3 | 288.3 | 292.8 | 274.2
1247 | 1140 | 324.5 | 291.8 |  | 283.4 | 288.3 | 292.8 | 274.2
1248 | 1141 | 324.5 | 291.9 |  | 283.5 | 288.4 | 292.8 | 274.2
1249 | 1142 | 324.5 | 291.9 |  | 283.5 | 288.4 | 292.8 | 274.2
1250 | 1143 | 324.5 | 291.9 |  | 283.5 | 288.4 | 292.8 | 274.2
1251 | 1144 | 322.7 | 295.9 |  | 286.9 | 291.9 | 294.5 | 274
1252 | 1145 | 324.3 | 292.3 |  | 283.8 | 288.7 | 293 | 274.2
1253 | 1146 | 324.5 | 292.1 |  | 283.6 | 288.5 | 292.9 | 274.2
1254 | 1147 | 324.4 | 292.2 |  | 283.7 | 288.6 | 292.9 | 274.2
1255 | 1148 | 324.4 | 292.2 |  | 283.7 | 288.6 | 292.9 | 274.3
1256 | 1149 | 324.5 | 292.2 |  | 283.7 | 288.6 | 292.9 | 274.3
1257 | 1150 | 323.4 | 295.9 |  | 286.6 | 291.8 | 294.3 | 274.1
1258 | 1151 | 324.4 | 292.4 |  | 283.9 | 288.8 | 292.9 | 274.3
1259 | 1152 | 324.5 | 292.3 |  | 283.9 | 288.7 | 292.9 | 274.3
1260 | 1153 | 324.4 | 292.3 |  | 283.9 | 288.7 | 292.9 | 274.3
1261 | 1154 | 324.4 | 292.3 |  | 284 | 288.7 | 292.9 | 274.3
1262 | 1155 | 324.4 | 292.4 |  | 284 | 288.8 | 292.9 | 274.3
1263 | 1156 | 324.4 | 292.4 |  | 284 | 288.8 | 292.9 | 274.3
1264 | 1157 | 324.3 | 292.7 |  | 284.2 | 289 | 293 | 274.3
1265 | 1158 | 324.2 | 292.8 |  | 284.4 | 289.2 | 293.2 | 274.3
1266 | 1159 | 324.1 | 293.1 |  | 284.6 | 289.4 | 293.3 | 274.3
1267 | 1160 | 324.4 | 292.6 |  | 284.2 | 288.9 | 293 | 274.4
1268 | 1161 | 324.3 | 293.1 |  | 284.6 | 289.4 | 293.3 | 274.3
1269 | 1162 | 324.3 | 293.1 |  | 284.5 | 289.4 | 293.2 | 274.4
1270 | 1163 | 324.3 | 293 |  | 284.5 | 289.2 | 293.2 | 274.4
1271 | 1164 | 324.4 | 292.9 |  | 284.4 | 289.1 | 293.1 | 274.4
1272 | 1165 | 324.4 | 292.9 |  | 284.4 | 289.1 | 293.1 | 274.4
1273 | 1166 | 324.3 | 293.1 |  | 284.5 | 289.2 | 293.2 | 274.4
1274 | 1167 | 324.3 | 293.1 |  | 284.5 | 289.2 | 293.2 | 274.4
1275 | 1168 | 324.4 | 293.1 |  | 284.5 | 289.2 | 293.2 | 274.4
1276 | 1169 | 324.4 | 293.2 |  | 284.6 | 289.2 | 293.2 | 274.4
1277 | 1170 | 324.5 | 293.3 |  | 284.6 | 289.2 | 293.2 | 274.4
1278 | 1171 | 324.5 | 293.4 |  | 284.6 | 289.2 | 293.2 | 274.5
1279 | 1172 | 323.6 | 294.4 |  | 285.5 | 290.1 | 293.6 | 274.4
1280 | 1173 | 323 | 295.4 |  | 286.2 | 291.1 | 294.1 | 274.3
1281 | 1174 | 324.6 | 293.8 |  | 285 | 289.6 | 293.4 | 274.5
1282 | 1175 | 324.6 | 293.7 |  | 284.8 | 289.4 | 293.3 | 274.5
1283 | 1176 | 324.6 | 293.7 |  | 284.8 | 289.4 | 293.3 | 274.5
1284 | 1177 | 324.7 | 293.8 |  | 284.9 | 289.4 | 293.3 | 274.5
1285 | 1178 | 324.7 | 293.9 |  | 284.9 | 289.5 | 293.3 | 274.5
1286 | 1179 | 324.7 | 294 |  | 285 | 289.5 | 293.4 | 274.6
1287 | 1180 | 324.6 | 294.3 |  | 285.2 | 289.8 | 293.6 | 274.6
1288 | 1181 | 324.5 | 294.8 |  | 285.6 | 290.3 | 293.8 | 274.5
1289 | 1182 | 324.7 | 294.3 |  | 285.2 | 289.7 | 293.6 | 274.6
1290 | 1183 | 324.7 | 294.3 |  | 285.2 | 289.7 | 293.6 | 274.7
1291 | 1184 | 324.8 | 294.4 |  | 285.2 | 289.6 | 293.6 | 274.7
1292 | 1185 | 324.8 | 294.5 |  | 285.2 | 289.7 | 293.7 | 274.7
1293 | 1186 | 324.5 | 295.2 |  | 285.8 | 290.4 | 294 | 274.7
1294 | 1187 | 324.8 | 294.7 |  | 285.4 | 289.8 | 293.8 | 274.7
1295 | 1188 | 324.6 | 295.4 |  | 285.9 | 290.6 | 294.1 | 274.7
1296 | 1189 | 324.6 | 295.8 |  | 286.2 | 291 | 294.3 | 274.7
1297 | 1190 | 324.7 | 295.5 |  | 285.9 | 290.5 | 294.1 | 274.7
1298 | 1191 | 324.5 | 296.1 |  | 286.3 | 291 | 294.3 | 274.7
1299 | 1192 | 324.9 | 295.1 |  | 285.5 | 289.9 | 293.8 | 274.8
1300 | 1193 | 324.9 | 295.2 |  | 285.5 | 290 | 293.8 | 274.8
1301 | 1194 | 324.9 | 295.3 |  | 285.6 | 290 | 293.8 | 274.8
1302 | 1195 | 324.9 | 295.4 |  | 285.6 | 290 | 293.8 | 274.9
1303 | 1196 | 324.9 | 295.5 |  | 285.7 | 290.1 | 293.9 | 274.9
1304 | 1197 | 324.9 | 295.6 |  | 285.7 | 290.1 | 293.9 | 274.9
1305 | 1198 | 324.9 | 295.7 |  | 285.8 | 290.1 | 294 | 274.9
1306 | 1199 | 324.9 | 295.8 |  | 285.8 | 290.2 | 294 | 274.9
1307 | 1200 | 324.9 | 295.9 |  | 285.8 | 290.2 | 294.1 | 274.9
1308 | 1201 | 325 | 296 |  | 285.9 | 290.2 | 294.1 | 274.9
1309 | 1202 | 325 | 296.1 |  | 285.9 | 290.3 | 294.1 | 274.9
1310 | 1203 | 324.9 | 296.2 |  | 286 | 290.3 | 294.1 | 274.9
1311 | 1204 | 324.9 | 296.3 |  | 286 | 290.3 | 294.1 | 274.9
1312 | 1205 | 324.9 | 296.4 |  | 286 | 290.4 | 294.2 | 275
1313 | 1206 | 324.9 | 296.5 |  | 286.1 | 290.4 | 294.2 | 275
1314 | 1207 | 324.9 | 296.6 |  | 286.1 | 290.4 | 294.2 | 275
1315 | 1208 | 324.9 | 296.7 |  | 286.2 | 290.4 | 294.2 | 275
1316 | 1209 | 324.9 | 296.8 |  | 286.2 | 290.5 | 294.3 | 275
1317 | 1210 | 324.9 | 296.9 |  | 286.2 | 290.5 | 294.3 | 275
1318 | 1211 | 324.9 | 296.9 |  | 286.3 | 290.5 | 294.4 | 275
1319 | 1212 | 324.9 | 297 |  | 286.3 | 290.6 | 294.4 | 275
1320 | 1213 | 324.9 | 297.1 |  | 286.4 | 290.6 | 294.4 | 275
1321 | 1214 | 324.9 | 297.2 |  | 286.4 | 290.6 | 294.4 | 275
1322 | 1215 | 324.9 | 297.3 |  | 286.4 | 290.7 | 294.5 | 275
1323 | 1216 | 324.9 | 297.4 |  | 286.5 | 290.7 | 294.5 | 275
1324 | 1217 | 324.9 | 297.5 |  | 286.5 | 290.7 | 294.5 | 275
1325 | 1218 | 324.8 | 297.6 |  | 286.6 | 290.8 | 294.6 | 275
1326 | 1219 | 324.7 | 297.9 |  | 286.7 | 290.9 | 294.7 | 275
1327 | 1220 | 324.3 | 298.8 |  | 287.5 | 291.8 | 295.1 | 275
1328 | 1221 | 324.7 | 297.9 |  | 286.7 | 290.9 | 294.6 | 275
1329 | 1222 | 324.7 | 297.9 |  | 286.7 | 290.9 | 294.6 | 275
1330 | 1223 | 324.7 | 298 |  | 286.8 | 290.9 | 294.6 | 275
1331 | 1224 | 324.7 | 298.1 |  | 286.8 | 291 | 294.7 | 275
1332 | 1225 | 324.7 | 298.2 |  | 286.8 | 291 | 294.7 | 275
1333 | 1226 | 324.6 | 298.3 |  | 286.9 | 291 | 294.7 | 275
1334 | 1227 | 324.6 | 298.4 |  | 286.9 | 291.1 | 294.8 | 275
1335 | 1228 | 324.6 | 298.5 |  | 287 | 291.1 | 294.8 | 275.1
1336 | 1229 | 324.6 | 298.6 |  | 287 | 291.1 | 294.8 | 275.1
1337 | 1230 | 324.6 | 298.7 |  | 287.1 | 291.2 | 294.8 | 275.1
1338 | 1231 | 324.6 | 298.8 |  | 287.1 | 291.2 | 294.8 | 275.1
1339 | 1232 | 324.6 | 298.9 |  | 287.1 | 291.2 | 294.8 | 275.1
1340 | 1233 | 324.4 | 299.6 |  | 287.6 | 291.7 | 295 | 275.1
1341 | 1234 | 324.6 | 299.1 |  | 287.2 | 291.3 | 294.8 | 275.1
1342 | 1235 | 324.6 | 299.1 |  | 287.3 | 291.3 | 294.9 | 275.1
1343 | 1236 | 324.6 | 299.2 |  | 287.3 | 291.4 | 294.9 | 275.1
1344 | 1237 | 324.6 | 299.3 |  | 287.3 | 291.4 | 295 | 275.1
1345 | 1238 | 324.5 | 299.4 |  | 287.4 | 291.4 | 295 | 275.1
1346 | 1239 | 324.5 | 299.5 |  | 287.4 | 291.5 | 295 | 275.1
1347 | 1240 | 324.5 | 299.5 |  | 287.5 | 291.5 | 295 | 275.1
1348 | 1241 | 324.5 | 299.6 |  | 287.5 | 291.5 | 295 | 275.1
1349 | 1242 | 324.5 | 299.7 |  | 287.6 | 291.6 | 295 | 275.2
1350 | 1243 | 324.5 | 299.8 |  | 287.6 | 291.6 | 295 | 275.2
1351 | 1244 | 324.5 | 299.8 |  | 287.6 | 291.6 | 295.1 | 275.2
1352 | 1245 | 324.1 | 300.7 |  | 288.3 | 292.4 | 295.5 | 275.1
1353 | 1246 | 324.5 | 300 |  | 287.7 | 291.7 | 295.1 | 275.2
1354 | 1247 | 324.4 | 300.1 |  | 287.8 | 291.7 | 295.2 | 275.2
1355 | 1248 | 324.4 | 300.1 |  | 287.8 | 291.8 | 295.2 | 275.2
1356 | 1249 | 324.5 | 300.2 |  | 287.8 | 291.8 | 295.2 | 275.2
1357 | 1250 | 324.5 | 300.3 |  | 287.9 | 291.8 | 295.2 | 275.2
1358 | 1251 | 324.5 | 300.3 |  | 287.9 | 291.9 | 295.2 | 275.2
1359 | 1252 | 324.5 | 300.4 |  | 288 | 291.9 | 295.1 | 275.2
1360 | 1253 | 324.5 | 300.5 |  | 288 | 291.9 | 295.1 | 275.2
1361 | 1254 | 324.5 | 300.6 |  | 288 | 291.9 | 295.1 | 275.2
1362 | 1255 | 324.5 | 300.6 |  | 288.1 | 292 | 295.1 | 275.2
1363 | 1256 | 324.5 | 300.7 |  | 288.1 | 292 | 295.2 | 275.2
1364 | 1257 | 324.5 | 300.7 |  | 288.2 | 292 | 295.2 | 275.2
1365 | 1258 | 324.5 | 300.8 |  | 288.2 | 292.1 | 295.2 | 275.2
1366 | 1259 | 324.5 | 300.8 |  | 288.2 | 292.1 | 295.2 | 275.2
1367 | 1260 | 324.5 | 300.9 |  | 288.3 | 292.1 | 295.2 | 275.2
1368 | 1261 | 324.5 | 301 |  | 288.3 | 292.2 | 295.3 | 275.3
1369 | 1262 | 324.5 | 301 |  | 288.3 | 292.2 | 295.3 | 275.3
1370 | 1263 | 324.5 | 301 |  | 288.4 | 292.2 | 295.3 | 275.3
1371 | 1264 | 324.5 | 301 |  | 288.4 | 292.2 | 295.3 | 275.3
1372 | 1265 | 324.5 | 301.1 |  | 288.5 | 292.3 | 295.4 | 275.3
1373 | 1266 | 324.5 | 301.2 |  | 288.5 | 292.3 | 295.4 | 275.3
1374 | 1267 | 324.5 | 301.2 |  | 288.5 | 292.3 | 295.4 | 275.3
1375 | 1268 | 324.6 | 301.3 |  | 288.6 | 292.4 | 295.4 | 275.3
1376 | 1269 | 324.6 | 301.3 |  | 288.6 | 292.4 | 295.4 | 275.3
1377 | 1270 | 324.6 | 301.4 |  | 288.7 | 292.4 | 295.4 | 275.3
1378 | 1271 | 324.6 | 301.4 |  | 288.7 | 292.5 | 295.4 | 275.3
1379 | 1272 | 324.6 | 301.5 |  | 288.7 | 292.5 | 295.4 | 275.3
1380 | 1273 | 324.6 | 301.5 |  | 288.8 | 292.5 | 295.5 | 275.3
1381 | 1274 | 324.6 | 301.6 |  | 288.8 | 292.5 | 295.5 | 275.3
1382 | 1275 | 324.6 | 301.6 |  | 288.8 | 292.6 | 295.5 | 275.3
1383 | 1276 | 324.6 | 301.7 |  | 288.9 | 292.6 | 295.5 | 275.3
1384 | 1277 | 324.6 | 301.8 |  | 288.9 | 292.6 | 295.5 | 275.3
1385 | 1278 | 324.4 | 302.1 |  | 289.2 | 293 | 295.7 | 275.3
1386 | 1279 | 323.1 | 304.7 |  | 291.4 | 295.3 | 296.8 | 275.1
1387 | 1280 | 324.5 | 302 |  | 289 | 292.7 | 295.6 | 275.3
1388 | 1281 | 324.5 | 302 |  | 289.1 | 292.8 | 295.6 | 275.3
1389 | 1282 | 324.6 | 302.1 |  | 289.1 | 292.8 | 295.6 | 275.4
1390 | 1283 | 324.6 | 302.2 |  | 289.2 | 292.8 | 295.6 | 275.4
1391 | 1284 | 324.6 | 302.3 |  | 289.2 | 292.8 | 295.7 | 275.4
1392 | 1285 | 324.6 | 302.3 |  | 289.2 | 292.9 | 295.7 | 275.4
1393 | 1286 | 324.6 | 302.4 |  | 289.3 | 292.9 | 295.7 | 275.4
1394 | 1287 | 324.6 | 302.4 |  | 289.3 | 292.9 | 295.7 | 275.5
1395 | 1288 | 324.5 | 302.6 |  | 289.4 | 293.1 | 295.9 | 275.5
1396 | 1289 | 324.6 | 302.6 |  | 289.4 | 293 | 295.9 | 275.5
1397 | 1290 | 324.5 | 302.7 |  | 289.5 | 293.1 | 295.9 | 275.5
1398 | 1291 | 324.1 | 304.1 |  | 290.5 | 294.1 | 296.2 | 275.5
1399 | 1292 | 324.5 | 302.7 |  | 289.5 | 293.1 | 295.8 | 275.5
1400 | 1293 | 324.5 | 302.8 |  | 289.6 | 293.1 | 295.9 | 275.6
1401 | 1294 | 324.5 | 302.8 |  | 289.6 | 293.2 | 295.9 | 275.6
1402 | 1295 | 324.5 | 302.9 |  | 289.6 | 293.2 | 295.9 | 275.6
1403 | 1296 | 324.4 | 303.2 |  | 289.9 | 293.4 | 296 | 275.6
1404 | 1297 | 322.1 | 310.7 |  | 295.5 | 299.6 | 298.6 | 275.2
1405 | 1298 | 324.4 | 303.1 |  | 289.8 | 293.3 | 295.9 | 275.6
1406 | 1299 | 324.4 | 303.2 |  | 289.8 | 293.3 | 295.9 | 275.6
1407 | 1300 | 324.4 | 303.2 |  | 289.8 | 293.4 | 295.9 | 275.6
1408 | 1301 | 324.4 | 303.3 |  | 289.9 | 293.4 | 295.9 | 275.6
1409 | 1302 | 324.4 | 303.3 |  | 289.9 | 293.4 | 295.9 | 275.7
1410 | 1303 | 324.4 | 303.4 |  | 289.9 | 293.5 | 296 | 275.7
1411 | 1304 | 324.3 | 303.4 |  | 290 | 293.5 | 296 | 275.7
1412 | 1305 | 324.4 | 303.5 |  | 290.1 | 293.6 | 296 | 275.7
1413 | 1306 | 324.4 | 303.5 |  | 290.1 | 293.6 | 296 | 275.7
1414 | 1307 | 324.4 | 303.6 |  | 290.1 | 293.6 | 296 | 275.7
1415 | 1308 | 324.4 | 303.6 |  | 290.2 | 293.6 | 296.1 | 275.7
1416 | 1309 | 324.4 | 303.7 |  | 290.2 | 293.7 | 296.1 | 275.7
1417 | 1310 | 324.3 | 303.7 |  | 290.2 | 293.7 | 296.1 | 275.7
1418 | 1311 | 324.3 | 303.8 |  | 290.3 | 293.7 | 296.1 | 275.7
1419 | 1312 | 324.3 | 303.8 |  | 290.3 | 293.8 | 296.2 | 275.7
1420 | 1313 | 324.3 | 303.9 |  | 290.3 | 293.8 | 296.2 | 275.7
1421 | 1314 | 324.2 | 303.9 |  | 290.4 | 293.8 | 296.3 | 275.7
1422 | 1315 | 324.2 | 304 |  | 290.4 | 293.9 | 296.3 | 275.7
1423 | 1316 | 324.2 | 304 |  | 290.4 | 293.9 | 296.3 | 275.7
1424 | 1317 | 324.2 | 304 |  | 290.5 | 293.9 | 296.3 | 275.7
1425 | 1318 | 324.2 | 304 |  | 290.5 | 294 | 296.3 | 275.7
1426 | 1319 | 324.2 | 304 |  | 290.6 | 294 | 296.3 | 275.7
1427 | 1320 | 324.2 | 304.1 |  | 290.6 | 294 | 296.3 | 275.7
1428 | 1321 | 324.1 | 304.1 |  | 290.6 | 294.1 | 296.3 | 275.7
1429 | 1322 | 324.1 | 304.2 |  | 290.7 | 294.1 | 296.3 | 275.7
1430 | 1323 | 324.1 | 304.2 |  | 290.7 | 294.1 | 296.3 | 275.7
1431 | 1324 | 324.1 | 304.3 |  | 290.7 | 294.2 | 296.3 | 275.7
1432 | 1325 | 324.1 | 304.3 |  | 290.8 | 294.2 | 296.3 | 275.7
1433 | 1326 | 324.2 | 304.3 |  | 290.8 | 294.2 | 296.4 | 275.7
1434 | 1327 | 324.2 | 304.4 |  | 290.8 | 294.3 | 296.4 | 275.7
1435 | 1328 | 324.2 | 304.4 |  | 290.9 | 294.3 | 296.5 | 275.7
1436 | 1329 | 324.2 | 304.4 |  | 290.9 | 294.3 | 296.5 | 275.7
1437 | 1330 | 324.2 | 304.4 |  | 290.9 | 294.4 | 296.5 | 275.7
1438 | 1331 | 324.2 | 304.4 |  | 291 | 294.3 | 296.5 | 275.7
1439 | 1332 | 324.2 | 304.4 |  | 291 | 294.3 | 296.6 | 275.7
1440 | 1333 | 324.2 | 304.5 |  | 291 | 294.4 | 296.6 | 275.7
1441 | 1334 | 324.1 | 304.5 |  | 291.1 | 294.4 | 296.7 | 275.7
1442 | 1335 | 324.1 | 304.6 |  | 291.1 | 294.4 | 296.7 | 275.7
1443 | 1336 | 324 | 304.6 |  | 291.1 | 294.5 | 296.7 | 275.7
1444 | 1337 | 323.8 | 304.6 |  | 291.2 | 294.5 | 296.7 | 275.7
1445 | 1338 | 323.6 | 304.6 |  | 291.2 | 294.5 | 296.7 | 275.7
1446 | 1339 | 323.4 | 304.7 |  | 291.3 | 294.6 | 296.7 | 275.7
1447 | 1340 | 323.2 | 304.7 |  | 291.3 | 294.6 | 296.6 | 275.7
1448 | 1341 | 323 | 304.7 |  | 291.3 | 294.6 | 296.6 | 275.6
1449 | 1342 | 322.8 | 304.7 |  | 291.3 | 294.6 | 296.5 | 275.6
1450 | 1343 | 322.5 | 304.7 |  | 291.4 | 294.6 | 296.4 | 275.6
1451 | 1344 | 322.3 | 304.7 |  | 291.4 | 294.6 | 296.4 | 275.6
1452 | 1345 | 322 | 304.8 |  | 291.4 | 294.6 | 296.3 | 275.6
1453 | 1346 | 321.8 | 304.8 |  | 291.5 | 294.6 | 296.2 | 275.5
1454 | 1347 | 321.5 | 304.8 |  | 291.5 | 294.6 | 296.2 | 275.5
1455 | 1348 | 321.2 | 304.9 |  | 291.6 | 294.6 | 296.1 | 275.5
1456 | 1349 | 320.9 | 304.9 |  | 291.6 | 294.6 | 296.1 | 275.5
1457 | 1350 | 320.6 | 305 |  | 291.6 | 294.6 | 296 | 275.4
1458 | 1351 | 320.3 | 305 |  | 291.7 | 294.6 | 295.9 | 275.4
1459 | 1352 | 320 | 305 |  | 291.7 | 294.6 | 295.8 | 275.4
1460 | 1353 | 319.7 | 305 |  | 291.7 | 294.6 | 295.8 | 275.3
1461 | 1354 | 319.4 | 305.1 |  | 291.7 | 294.6 | 295.7 | 275.3
1462 | 1355 | 319.1 | 305.1 |  | 291.8 | 294.6 | 295.6 | 275.2
1463 | 1356 | 318.8 | 305.1 |  | 291.8 | 294.6 | 295.5 | 275.2
1464 | 1357 | 318.5 | 305.1 |  | 291.8 | 294.6 | 295.4 | 275.2
1465 | 1358 | 318.1 | 305.1 |  | 291.9 | 294.6 | 295.3 | 275.1
1466 | 1359 | 317.8 | 305.1 |  | 291.9 | 294.5 | 295.2 | 275.1
1467 | 1360 | 317.5 | 305.1 |  | 291.9 | 294.5 | 295.2 | 275
1468 | 1361 | 317.1 | 305.1 |  | 291.9 | 294.5 | 295.1 | 274.9
1469 | 1362 | 316.8 | 305.1 |  | 292 | 294.5 | 295 | 274.9
1470 | 1363 | 316.4 | 305.1 |  | 292 | 294.4 | 295 | 274.8
1471 | 1364 | 316.1 | 305 |  | 292 | 294.4 | 294.9 | 274.7
1472 | 1365 | 315.8 | 305 |  | 292 | 294.4 | 294.8 | 274.6
1473 | 1366 | 315.4 | 304.9 |  | 292.1 | 294.4 | 294.7 | 274.6
1474 | 1367 | 315.1 | 304.9 |  | 292.1 | 294.3 | 294.6 | 274.5
1475 | 1368 | 314.8 | 304.9 |  | 292.1 | 294.3 | 294.5 | 274.4
1476 | 1369 | 314.4 | 304.9 |  | 292.2 | 294.2 | 294.4 | 274.3
1477 | 1370 | 314.1 | 304.8 |  | 292.1 | 294.2 | 294.3 | 274.3
1478 | 1371 | 313.7 | 304.8 |  | 292.2 | 294.1 | 294.2 | 274.2
1479 | 1372 | 313.4 | 304.8 |  | 292.2 | 294.1 | 294.1 | 274.1
1480 | 1373 | 313 | 304.8 |  | 292.2 | 294 | 294 | 274
1481 | 1374 | 312.7 | 304.8 |  | 292.2 | 294 | 293.9 | 273.9
1482 | 1375 | 312.3 | 304.7 |  | 292.2 | 293.9 | 293.8 | 273.8
1483 | 1376 | 312 | 304.7 |  | 292.2 | 293.9 | 293.7 | 273.7
1484 | 1377 | 311.6 | 304.7 |  | 292.2 | 293.9 | 293.6 | 273.6
1485 | 1378 | 311.3 | 304.7 |  | 292.2 | 293.8 | 293.5 | 273.5
1486 | 1379 | 310.9 | 304.6 |  | 292.3 | 293.8 | 293.3 | 273.4
1487 | 1380 | 310.6 | 304.6 |  | 292.3 | 293.7 | 293.2 | 273.3
1488 | 1381 | 310.2 | 304.6 |  | 292.3 | 293.7 | 293.1 | 273.2
1489 | 1382 | 309.9 | 304.6 |  | 292.3 | 293.6 | 293 | 273.1
1490 | 1383 | 309.5 | 304.5 |  | 292.3 | 293.6 | 292.9 | 273
1491 | 1384 | 308.9 | 305.3 |  | 292.9 | 294.1 | 293 | 272.9
1492 | 1385 | 308.9 | 304.4 |  | 292.3 | 293.4 | 292.6 | 272.8
1493 | 1386 | 308.5 | 304.4 |  | 292.3 | 293.4 | 292.5 | 272.7
1494 | 1387 | 308.2 | 304.3 |  | 292.3 | 293.3 | 292.3 | 272.6
1495.1 | 1388.1 | 307.8 | 304.3 |  | 292.3 | 293.2 | 292.2 | 272.5
1496.1 | 1389.1 | 307.5 | 304.2 |  | 292.3 | 293.2 | 292 | 272.4
1497.1 | 1390.1 | 307.1 | 304.1 |  | 292.3 | 293.1 | 291.9 | 272.3
1498.1 | 1391.1 | 306.8 | 304.1 |  | 292.3 | 293.1 | 291.7 | 272.2
1499.1 | 1392.1 | 306.4 | 304 |  | 292.3 | 293 | 291.6 | 272.1
1500.1 | 1393.1 | 306 | 303.9 |  | 292.3 | 292.9 | 291.4 | 272
1501.1 | 1394.1 | 305.7 | 303.9 |  | 292.3 | 292.9 | 291.3 | 271.8
1502.1 | 1395.1 | 305.3 | 303.8 |  | 292.3 | 292.8 | 291.1 | 271.7
1503.1 | 1396.1 | 301 | 309.2 |  | 296.8 | 298 | 293.4 | 271.2
1504.1 | 1397.1 | 303.5 | 305.5 |  | 293.8 | 294.4 | 291.6 | 271.4
1505.1 | 1398.1 | 304.2 | 303.6 |  | 292.3 | 292.6 | 290.7 | 271.4
1506.1 | 1399.1 | 303.9 | 303.5 |  | 292.3 | 292.5 | 290.5 | 271.2
1507.1 | 1400.1 | 303.5 | 303.4 |  | 292.3 | 292.5 | 290.4 | 271.1
1508.1 | 1401.1 | 303.2 | 303.4 |  | 292.3 | 292.4 | 290.3 | 271
1509.1 | 1402.1 | 302.8 | 303.3 |  | 292.3 | 292.3 | 290.1 | 270.8
1510.1 | 1403.1 | 302.4 | 303.2 |  | 292.3 | 292.3 | 289.9 | 270.7
1511.1 | 1404.1 | 302.1 | 303.1 |  | 292.3 | 292.2 | 289.7 | 270.6
1512.1 | 1405.1 | 301.7 | 303 |  | 292.2 | 292.1 | 289.6 | 270.4
1513.1 | 1406.1 | 301.4 | 303 |  | 292.2 | 292.1 | 289.4 | 270.3
1514.1 | 1407.1 | 301 | 302.9 |  | 292.2 | 292 | 289.2 | 270.2
1515.1 | 1408.1 | 300.7 | 302.8 |  | 292.2 | 291.9 | 289 | 270
1516.1 | 1409.1 | 300.2 | 303 |  | 292.4 | 292 | 289 | 269.9
1517.1 | 1410.1 | 300 | 302.6 |  | 292.2 | 291.7 | 288.7 | 269.8
1518.1 | 1411.1 | 299.6 | 302.5 |  | 292.2 | 291.6 | 288.5 | 269.6
1519.1 | 1412.1 | 299.2 | 302.4 |  | 292.1 | 291.6 | 288.4 | 269.5
1520.1 | 1413.1 | 298.8 | 302.3 |  | 292.1 | 291.5 | 288.2 | 269.3
1521.1 | 1414.1 | 298.5 | 302.2 |  | 292.1 | 291.4 | 288 | 269.2
1522.1 | 1415.1 | 298.1 | 302.1 |  | 292.1 | 291.3 | 287.8 | 269.1
1523.1 | 1416.1 | 297.8 | 302 |  | 292.1 | 291.2 | 287.7 | 268.9
1524.1 | 1417.1 | 297.4 | 301.9 |  | 292 | 291.2 | 287.4 | 268.8
1525.1 | 1418.1 | 297.1 | 301.8 |  | 292 | 291.1 | 287.3 | 268.6
1526.1 | 1419.1 | 296.7 | 301.7 |  | 292 | 291 | 287.1 | 268.5
1527.1 | 1420.1 | 296.3 | 301.7 |  | 292 | 290.9 | 286.9 | 268.3
1528.1 | 1421.1 | 296 | 301.6 |  | 292 | 290.8 | 286.8 | 268.1
1529.1 | 1422.1 | 295.6 | 301.5 |  | 291.9 | 290.8 | 286.6 | 268
1530.1 | 1423.1 | 295.2 | 301.4 |  | 291.9 | 290.7 | 286.4 | 267.8
1531.1 | 1424.1 | 294.9 | 301.3 |  | 291.9 | 290.6 | 286.2 | 267.7
1532.1 | 1425.1 | 294.5 | 301.2 |  | 291.8 | 290.5 | 286.1 | 267.5
1533.1 | 1426.1 | 294.2 | 301.1 |  | 291.8 | 290.4 | 285.9 | 267.4
1534.1 | 1427.1 | 293.8 | 301 |  | 291.8 | 290.3 | 285.7 | 267.2
1535.1 | 1428.1 | 293.5 | 300.9 |  | 291.8 | 290.2 | 285.5 | 267.1
1536.1 | 1429.1 | 293.2 | 300.8 |  | 291.7 | 290.1 | 285.3 | 266.9
1537.1 | 1430.1 | 292.8 | 300.7 |  | 291.7 | 290 | 285.1 | 266.8
1538.1 | 1431.1 | 292.5 | 300.6 |  | 291.7 | 289.9 | 285 | 266.6
1539.1 | 1432.1 | 292.1 | 300.5 |  | 291.6 | 289.8 | 284.8 | 266.5
1540.1 | 1433.1 | 291.8 | 300.4 |  | 291.6 | 289.8 | 284.6 | 266.3
1541.1 | 1434.1 | 291.5 | 300.3 |  | 291.5 | 289.7 | 284.4 | 266.2
1542.1 | 1435.1 | 291.1 | 300.2 |  | 291.5 | 289.6 | 284.3 | 266
1543.1 | 1436.1 | 290.8 | 300 |  | 291.5 | 289.5 | 284.1 | 265.8
1544.1 | 1437.1 | 290.4 | 299.9 |  | 291.4 | 289.4 | 283.9 | 265.7
1545.1 | 1438.1 | 290.1 | 299.8 |  | 291.4 | 289.3 | 283.7 | 265.5
1546.1 | 1439.1 | 289.8 | 299.7 |  | 291.3 | 289.2 | 283.5 | 265.4
1547.1 | 1440.1 | 289.5 | 299.6 |  | 291.3 | 289.1 | 283.3 | 265.2
1548.1 | 1441.1 | 289.1 | 299.5 |  | 291.3 | 289 | 283.1 | 265
1549.1 | 1442.1 | 288.8 | 299.4 |  | 291.2 | 288.9 | 283 | 264.9
1550.1 | 1443.1 | 288.5 | 299.3 |  | 291.2 | 288.8 | 282.8 | 264.7
1551.1 | 1444.1 | 288.2 | 299.1 |  | 291.1 | 288.7 | 282.6 | 264.6
1552.1 | 1445.1 | 287.8 | 299 |  | 291.1 | 288.6 | 282.4 | 264.4
1553.1 | 1446.1 | 287.5 | 298.9 |  | 291 | 288.5 | 282.3 | 264.3
1554.1 | 1447.1 | 287.2 | 298.8 |  | 291 | 288.4 | 282.1 | 264.1
1555.1 | 1448.1 | 286.8 | 298.6 |  | 290.9 | 288.3 | 281.9 | 263.9
1556.1 | 1449.1 | 286.5 | 298.5 |  | 290.9 | 288.2 | 281.7 | 263.8
1557.1 | 1450.1 | 286.2 | 298.4 |  | 290.8 | 288.1 | 281.5 | 263.6
1558.1 | 1451.1 | 285.8 | 298.2 |  | 290.8 | 288 | 281.3 | 263.4
1559.1 | 1452.1 | 285.5 | 298.1 |  | 290.7 | 287.9 | 281.1 | 263.3
1560.1 | 1453.1 | 285.2 | 298 |  | 290.6 | 287.8 | 281 | 263.1
1561.1 | 1454.1 | 284.8 | 297.9 |  | 290.6 | 287.7 | 280.8 | 262.9
1562.1 | 1455.1 | 284.5 | 297.7 |  | 290.5 | 287.6 | 280.6 | 262.8
1563.1 | 1456.1 | 284.2 | 297.6 |  | 290.5 | 287.4 | 280.4 | 262.6
1564.1 | 1457.1 | 283.9 | 297.5 |  | 290.4 | 287.3 | 280.2 | 262.4
1565.1 | 1458.1 | 283.5 | 297.3 |  | 290.4 | 287.2 | 280.1 | 262.3
1566.1 | 1459.1 | 283.2 | 297.2 |  | 290.3 | 287.1 | 279.9 | 262.1
1567.1 | 1460.1 | 282.8 | 297.1 |  | 290.2 | 287 | 279.7 | 261.9
1568.1 | 1461.1 | 282.5 | 296.9 |  | 290.2 | 286.9 | 279.5 | 261.7
1569.1 | 1462.1 | 282.2 | 296.8 |  | 290.1 | 286.8 | 279.3 | 261.6
1570.1 | 1463.1 | 281.9 | 296.7 |  | 290.1 | 286.7 | 279.1 | 261.4
1571.1 | 1464.1 | 281.6 | 296.5 |  | 290 | 286.6 | 278.9 | 261.2
1572.1 | 1465.1 | 281.2 | 296.4 |  | 289.9 | 286.5 | 278.7 | 261
1573.1 | 1466.1 | 280.9 | 296.3 |  | 289.9 | 286.3 | 278.6 | 260.9
1574.1 | 1467.1 | 280.6 | 296.2 |  | 289.8 | 286.2 | 278.4 | 260.7
1575.1 | 1468.1 | 280.1 | 296.5 |  | 290.1 | 286.5 | 278.3 | 260.5
1576.1 | 1469.1 | 279.9 | 295.9 |  | 289.7 | 286 | 278 | 260.3
1577.1 | 1470.1 | 279.6 | 295.7 |  | 289.6 | 285.9 | 277.8 | 260.2
1578.1 | 1471.1 | 279.2 | 295.6 |  | 289.5 | 285.8 | 277.6 | 260
1579.1 | 1472.1 | 278.7 | 295.8 |  | 289.7 | 285.9 | 277.5 | 259.8
1580.1 | 1473.1 | 278.6 | 295.3 |  | 289.4 | 285.5 | 277.2 | 259.6
1581.1 | 1474.1 | 276.9 | 296.5 |  | 290.4 | 286.9 | 277.7 | 259.3
1582.1 | 1475.1 | 274.8 | 298.2 |  | 291.7 | 289.2 | 278.7 | 259
1583.1 | 1476.1 | 276.9 | 297.1 |  | 291 | 287.8 | 277.7 | 258.9
1584.1 | 1477.1 | 277.2 | 294.9 |  | 289.2 | 285.2 | 276.5 | 258.9
1585.1 | 1478.1 | 277 | 294.6 |  | 289 | 284.9 | 276.2 | 258.8
1586.1 | 1479.1 | 276.7 | 294.5 |  | 288.9 | 284.8 | 276 | 258.6
1587.1 | 1480.1 | 276.2 | 294.5 |  | 289 | 284.8 | 275.8 | 258.4
1588.1 | 1481.1 | 276 | 294.2 |  | 288.8 | 284.6 | 275.6 | 258.2
1589.1 | 1482.1 | 275.7 | 294.1 |  | 288.8 | 284.4 | 275.3 | 258
1590.1 | 1483.1 | 275.4 | 293.9 |  | 288.7 | 284.3 | 275.1 | 257.8
1591.1 | 1484.1 | 275 | 293.7 |  | 288.6 | 284.1 | 274.9 | 257.6
1592.1 | 1485.1 | 274.7 | 293.6 |  | 288.5 | 284 | 274.7 | 257.5
1593.1 | 1486.1 | 274.5 | 293.4 |  | 288.4 | 283.9 | 274.5 | 257.3
1594.1 | 1487.1 | 274.1 | 293.3 |  | 288.3 | 283.7 | 274.3 | 257.1
1595.1 | 1488.1 | 273.8 | 293.1 |  | 288.2 | 283.6 | 274.1 | 256.9
1596.1 | 1489.1 | 273.5 | 293 |  | 288.1 | 283.5 | 273.9 | 256.7
1597.1 | 1490.1 | 273.2 | 292.9 |  | 288.1 | 283.3 | 273.7 | 256.5
1598.1 | 1491.1 | 272.9 | 292.7 |  | 288 | 283.2 | 273.5 | 256.4
1599.1 | 1492.1 | 272.6 | 292.6 |  | 287.9 | 283 | 273.3 | 256.2
1600.1 | 1493.1 | 272.3 | 292.4 |  | 287.8 | 282.9 | 273.1 | 256
1601.1 | 1494.1 | 272 | 292.3 |  | 287.7 | 282.8 | 272.9 | 255.8
1602.1 | 1495.1 | 271.7 | 292.2 |  | 287.6 | 282.7 | 272.7 | 255.6
1603.1 | 1496.1 | 271.4 | 292 |  | 287.6 | 282.5 | 272.5 | 255.5
1604.1 | 1497.1 | 271.1 | 291.9 |  | 287.5 | 282.4 | 272.3 | 255.3
1605.1 | 1498.1 | 270.8 | 291.7 |  | 287.4 | 282.3 | 272.1 | 255.1
1606.1 | 1499.1 | 270.5 | 291.6 |  | 287.3 | 282.1 | 271.9 | 254.9
1607.1 | 1500.1 | 270.2 | 291.5 |  | 287.2 | 282 | 271.7 | 254.7
1608.1 | 1501.1 | 270 | 291.3 |  | 287.1 | 281.9 | 271.5 | 254.5
1609.1 | 1502.1 | 269.7 | 291.2 |  | 287 | 281.7 | 271.3 | 254.3
1610.1 | 1503.1 | 269.4 | 291 |  | 286.9 | 281.6 | 271.1 | 254.2
1611.1 | 1504.1 | 269.1 | 290.9 |  | 286.8 | 281.4 | 270.9 | 254
1612.1 | 1505.1 | 268.8 | 290.7 |  | 286.8 | 281.3 | 270.7 | 253.8
1613.1 | 1506.1 | 268.4 | 290.6 |  | 286.7 | 281.2 | 270.5 | 253.6
1614.1 | 1507.1 | 268.1 | 290.4 |  | 286.6 | 281 | 270.3 | 253.4
1615.1 | 1508.1 | 267.8 | 290.3 |  | 286.5 | 280.9 | 270.1 | 253.2
1616.1 | 1509.1 | 267.5 | 290.1 |  | 286.4 | 280.7 | 269.9 | 253
1617.1 | 1510.1 | 267.2 | 290 |  | 286.3 | 280.6 | 269.7 | 252.9
1618.1 | 1511.1 | 266.9 | 289.8 |  | 286.2 | 280.5 | 269.5 | 252.7
1619.1 | 1512.1 | 266.6 | 289.7 |  | 286.1 | 280.3 | 269.3 | 252.5
1620.1 | 1513.1 | 266.3 | 289.5 |  | 286 | 280.2 | 269.1 | 252.3
1621.1 | 1514.1 | 265.9 | 289.4 |  | 285.9 | 280 | 268.9 | 252.1
1622.1 | 1515.1 | 265.6 | 289.2 |  | 285.8 | 279.9 | 268.7 | 251.9
1623.1 | 1516.1 | 265.3 | 289.1 |  | 285.7 | 279.8 | 268.5 | 251.8
1624.1 | 1517.1 | 265 | 288.9 |  | 285.6 | 279.6 | 268.3 | 251.6
1625.1 | 1518.1 | 264.8 | 288.8 |  | 285.5 | 279.5 | 268.1 | 251.4
1626.1 | 1519.1 | 264.5 | 288.6 |  | 285.4 | 279.3 | 267.8 | 251.2
1627.1 | 1520.1 | 264.2 | 288.5 |  | 285.3 | 279.2 | 267.6 | 251
1628.1 | 1521.1 | 263.9 | 288.4 |  | 285.2 | 279.1 | 267.4 | 250.8
1629.1 | 1522.1 | 263.6 | 288.2 |  | 285.1 | 278.9 | 267.2 | 250.7
1630.1 | 1523.1 | 263.3 | 288.1 |  | 285 | 278.8 | 267 | 250.5
1631.1 | 1524.1 | 263 | 287.9 |  | 284.9 | 278.6 | 266.8 | 250.3
1632.1 | 1525.1 | 262.7 | 287.8 |  | 284.8 | 278.4 | 266.6 | 250.1
1633.1 | 1526.1 | 262.4 | 287.6 |  | 284.7 | 278.3 | 266.4 | 249.9
1634.1 | 1527.1 | 262.1 | 287.5 |  | 284.6 | 278.1 | 266.2 | 249.7
1635.1 | 1528.1 | 261.8 | 287.3 |  | 284.5 | 278 | 266 | 249.5
1636.1 | 1529.1 | 261.5 | 287.2 |  | 284.4 | 277.8 | 265.8 | 249.4
1637.1 | 1530.1 | 261.2 | 287.1 |  | 284.3 | 277.7 | 265.6 | 249.2
1638.1 | 1531.1 | 260.9 | 286.9 |  | 284.2 | 277.5 | 265.4 | 249
1639.1 | 1532.1 | 260.6 | 286.7 |  | 284.1 | 277.4 | 265.2 | 248.8
1640.1 | 1533.1 | 260.4 | 286.6 |  | 283.9 | 277.2 | 264.9 | 248.6
1641.1 | 1534.1 | 260.1 | 286.4 |  | 283.8 | 277.1 | 264.7 | 248.4
1642.1 | 1535.1 | 259.8 | 286.3 |  | 283.7 | 276.9 | 264.5 | 248.2
1643.1 | 1536.1 | 259.5 | 286.1 |  | 283.6 | 276.8 | 264.3 | 248
1644.1 | 1537.1 | 259.3 | 285.9 |  | 283.5 | 276.7 | 264.1 | 247.9
1645.1 | 1538.1 | 259 | 285.8 |  | 283.4 | 276.5 | 263.9 | 247.7
1646.1 | 1539.1 | 258.7 | 285.6 |  | 283.3 | 276.3 | 263.7 | 247.5
1647.1 | 1540.1 | 258.4 | 285.5 |  | 283.2 | 276.2 | 263.5 | 247.3
1648.1 | 1541.1 | 258.1 | 285.3 |  | 283 | 276 | 263.4 | 247.1
1649.1 | 1542.1 | 257.8 | 285.1 |  | 282.9 | 275.9 | 263.2 | 247
1650.1 | 1543.1 | 257.5 | 285 |  | 282.8 | 275.7 | 263 | 246.8
1651.1 | 1544.1 | 257.2 | 284.8 |  | 282.7 | 275.6 | 262.8 | 246.6
1652.1 | 1545.1 | 256.9 | 284.6 |  | 282.6 | 275.4 | 262.6 | 246.4
1653.1 | 1546.1 | 256.6 | 284.5 |  | 282.5 | 275.3 | 262.4 | 246.2
1654.1 | 1547.1 | 256.3 | 284.3 |  | 282.3 | 275.1 | 262.3 | 246
1655.1 | 1548.1 | 256 | 284.2 |  | 282.2 | 274.9 | 262.1 | 245.8
1656.1 | 1549.1 | 255.7 | 284 |  | 282.1 | 274.8 | 261.9 | 245.7
1657.1 | 1550.1 | 255.4 | 283.8 |  | 282 | 274.6 | 261.7 | 245.5
1658.1 | 1551.1 | 255.1 | 283.7 |  | 281.9 | 274.5 | 261.5 | 245.3
1659.1 | 1552.1 | 254.8 | 283.5 |  | 281.8 | 274.3 | 261.3 | 245.1
1660.1 | 1553.1 | 254.6 | 283.3 |  | 281.6 | 274.2 | 261.1 | 244.9
1661.1 | 1554.1 | 254.3 | 283.2 |  | 281.5 | 274 | 260.9 | 244.7
1662.1 | 1555.1 | 254 | 283 |  | 281.4 | 273.9 | 260.7 | 244.6
1663.1 | 1556.1 | 253.7 | 282.8 |  | 281.3 | 273.7 | 260.5 | 244.4
1664.1 | 1557.1 | 253.4 | 282.7 |  | 281.2 | 273.6 | 260.3 | 244.2
1665.1 | 1558.1 | 253.2 | 282.5 |  | 281.1 | 273.4 | 260.1 | 244
1666.1 | 1559.1 | 252.9 | 282.3 |  | 280.9 | 273.3 | 259.9 | 243.8
1667.1 | 1560.1 | 252.6 | 282.1 |  | 280.8 | 273.1 | 259.8 | 243.6
1668.1 | 1561.1 | 252.3 | 282 |  | 280.7 | 272.9 | 259.6 | 243.5
1669.1 | 1562.1 | 252.1 | 281.8 |  | 280.6 | 272.8 | 259.4 | 243.3
1670.1 | 1563.1 | 251.8 | 281.6 |  | 280.4 | 272.6 | 259.2 | 243.1
1671.1 | 1564.1 | 251.5 | 281.4 |  | 280.3 | 272.4 | 259 | 242.9
1672.1 | 1565.1 | 251.3 | 281.3 |  | 280.2 | 272.3 | 258.8 | 242.7
1673.1 | 1566.1 | 251 | 281.1 |  | 280.1 | 272.1 | 258.6 | 242.5
1674.1 | 1567.1 | 250.8 | 280.9 |  | 279.9 | 272 | 258.4 | 242.3
1675.1 | 1568.1 | 250.5 | 280.8 |  | 279.8 | 271.8 | 258.2 | 242.2
1676.1 | 1569.1 | 250.2 | 280.6 |  | 279.7 | 271.6 | 258 | 242
1677.1 | 1570.1 | 250 | 280.5 |  | 279.6 | 271.5 | 257.8 | 241.8
1678.1 | 1571.1 | 249.7 | 280.3 |  | 279.4 | 271.3 | 257.7 | 241.6
1679.1 | 1572.1 | 249.4 | 280.1 |  | 279.3 | 271.2 | 257.5 | 241.4
1680.1 | 1573.1 | 249.1 | 279.9 |  | 279.2 | 271 | 257.2 | 241.2
1681.1 | 1574.1 | 248.9 | 279.8 |  | 279 | 270.9 | 257 | 241.1
1682.1 | 1575.1 | 248.6 | 279.6 |  | 278.9 | 270.7 | 256.8 | 240.9
1683.1 | 1576.1 | 248.3 | 279.4 |  | 278.8 | 270.5 | 256.6 | 240.7
1684.1 | 1577.1 | 248 | 279.3 |  | 278.6 | 270.4 | 256.4 | 240.5
1685.1 | 1578.1 | 247.8 | 279.1 |  | 278.5 | 270.2 | 256.2 | 240.3
1686.1 | 1579.1 | 247.5 | 278.9 |  | 278.4 | 270.1 | 256 | 240.1
1687.1 | 1580.1 | 247.3 | 278.8 |  | 278.2 | 269.9 | 255.7 | 240
1688.1 | 1581.1 | 247 | 278.6 |  | 278.1 | 269.8 | 255.5 | 239.8
1689.1 | 1582.1 | 246.7 | 278.4 |  | 278 | 269.6 | 255.3 | 239.6
1690.1 | 1583.1 | 246.5 | 278.2 |  | 277.8 | 269.4 | 255.1 | 239.4
1691.1 | 1584.1 | 246.2 | 278.1 |  | 277.7 | 269.3 | 254.9 | 239.3
1692.1 | 1585.1 | 246 | 277.9 |  | 277.6 | 269.1 | 254.7 | 239.1
1693.1 | 1586.1 | 245.7 | 277.7 |  | 277.4 | 268.9 | 254.5 | 238.9
1694.1 | 1587.1 | 245.5 | 277.5 |  | 277.3 | 268.8 | 254.3 | 238.7
1695.1 | 1588.1 | 245.2 | 277.4 |  | 277.2 | 268.6 | 254.2 | 238.5
1696.1 | 1589.1 | 245 | 277.2 |  | 277 | 268.4 | 254 | 238.3
1697.1 | 1590.1 | 244.7 | 277 |  | 276.9 | 268.3 | 253.7 | 238.2
1698.1 | 1591.1 | 244.5 | 276.8 |  | 276.8 | 268.1 | 253.5 | 238
1699.1 | 1592.1 | 244.2 | 276.7 |  | 276.6 | 267.9 | 253.3 | 237.8
1700.1 | 1593.1 | 244 | 276.5 |  | 276.5 | 267.8 | 253.2 | 237.6
1701.1 | 1594.1 | 243.7 | 276.3 |  | 276.4 | 267.6 | 253 | 237.5
1702.1 | 1595.1 | 243.5 | 276.1 |  | 276.2 | 267.5 | 252.8 | 237.3
1703.1 | 1596.1 | 243.2 | 276 |  | 276.1 | 267.3 | 252.6 | 237.1
1704.1 | 1597.1 | 243 | 275.8 |  | 276 | 267.1 | 252.4 | 236.9
1705.1 | 1598.1 | 242.7 | 275.6 |  | 275.8 | 267 | 252.2 | 236.7
1706.1 | 1599.1 | 242.4 | 275.5 |  | 275.7 | 266.8 | 252.1 | 236.5
1707.1 | 1600.1 | 242.2 | 275.3 |  | 275.5 | 266.7 | 251.9 | 236.4
1708.1 | 1601.1 | 241.9 | 275.1 |  | 275.4 | 266.5 | 251.6 | 236.2
1709.1 | 1602.1 | 241.7 | 274.9 |  | 275.3 | 266.4 | 251.4 | 236
1710.1 | 1603.1 | 241.4 | 274.8 |  | 275.1 | 266.2 | 251.2 | 235.8
1711.1 | 1604.1 | 241.2 | 274.6 |  | 275 | 266 | 251 | 235.7
1712.1 | 1605.1 | 240.9 | 274.4 |  | 274.8 | 265.9 | 250.9 | 235.5
1713.1 | 1606.1 | 240.7 | 274.2 |  | 274.7 | 265.7 | 250.6 | 235.3
1714.1 | 1607.1 | 240.4 | 274.1 |  | 274.6 | 265.5 | 250.4 | 235.1
1715.1 | 1608.1 | 240.2 | 273.9 |  | 274.4 | 265.4 | 250.3 | 235
1716.1 | 1609.1 | 239.9 | 273.7 |  | 274.3 | 265.2 | 250.1 | 234.8
1717.1 | 1610.1 | 239.6 | 273.5 |  | 274.1 | 265 | 249.9 | 234.6
1718.1 | 1611.1 | 239.4 | 273.3 |  | 274 | 264.8 | 249.7 | 234.4
1719.1 | 1612.1 | 239.1 | 273.2 |  | 273.9 | 264.7 | 249.5 | 234.2
1720.1 | 1613.1 | 238.9 | 273 |  | 273.7 | 264.5 | 249.3 | 234.1
1721.1 | 1614.1 | 238.6 | 272.8 |  | 273.6 | 264.3 | 249.1 | 233.9
1722.1 | 1615.1 | 238.4 | 272.6 |  | 273.4 | 264.2 | 248.9 | 233.7
1723.1 | 1616.1 | 238.1 | 272.5 |  | 273.3 | 264 | 248.6 | 233.5
1724.1 | 1617.1 | 237.9 | 272.3 |  | 273.1 | 263.8 | 248.4 | 233.4
1725.1 | 1618.1 | 237.6 | 272.1 |  | 273 | 263.7 | 248.2 | 233.2
1726.1 | 1619.1 | 237.3 | 271.9 |  | 272.8 | 263.5 | 248.1 | 233
1727.1 | 1620.1 | 237.1 | 271.7 |  | 272.7 | 263.3 | 247.9 | 232.8
1728.1 | 1621.1 | 236.9 | 271.6 |  | 272.6 | 263.2 | 247.7 | 232.6
1729.1 | 1622.1 | 236.6 | 271.4 |  | 272.4 | 263 | 247.5 | 232.5
1730.1 | 1623.1 | 236.4 | 271.2 |  | 272.3 | 262.8 | 247.3 | 232.3
1731.1 | 1624.1 | 236.1 | 271 |  | 272.1 | 262.7 | 247.1 | 232.1
1732.1 | 1625.1 | 235.9 | 270.8 |  | 272 | 262.5 | 247 | 232
1733.1 | 1626.1 | 235.7 | 270.6 |  | 271.8 | 262.3 | 246.8 | 231.8
1734.1 | 1627.1 | 235.5 | 270.5 |  | 271.7 | 262.2 | 246.6 | 231.6
1735.1 | 1628.1 | 235.3 | 270.3 |  | 271.5 | 262 | 246.5 | 231.4
1736.1 | 1629.1 | 235 | 270.1 |  | 271.4 | 261.8 | 246.3 | 231.3
1737.1 | 1630.1 | 234.8 | 269.9 |  | 271.2 | 261.7 | 246.1 | 231.1
1738.1 | 1631.1 | 234.6 | 269.8 |  | 271.1 | 261.5 | 245.9 | 230.9
1739.1 | 1632.1 | 234.3 | 269.6 |  | 270.9 | 261.4 | 245.7 | 230.7
1740.1 | 1633.1 | 234.1 | 269.4 |  | 270.8 | 261.2 | 245.5 | 230.6
1741.1 | 1634.1 | 233.9 | 269.2 |  | 270.6 | 261 | 245.3 | 230.4
1742.1 | 1635.1 | 233.6 | 269.1 |  | 270.5 | 260.9 | 245.1 | 230.2
1743.1 | 1636.1 | 233.4 | 268.9 |  | 270.3 | 260.7 | 244.9 | 230
1744.1 | 1637.1 | 233.2 | 268.7 |  | 270.2 | 260.5 | 244.7 | 229.9
1745.1 | 1638.1 | 232.9 | 268.5 |  | 270 | 260.3 | 244.5 | 229.7
1746.1 | 1639.1 | 232.7 | 268.3 |  | 269.9 | 260.2 | 244.3 | 229.5
1747.1 | 1640.1 | 232.5 | 268.2 |  | 269.7 | 260 | 244.1 | 229.3
1748.1 | 1641.1 | 232.2 | 268 |  | 269.6 | 259.8 | 243.9 | 229.2
1749.1 | 1642.1 | 232 | 267.8 |  | 269.4 | 259.7 | 243.7 | 229
1750.1 | 1643.1 | 231.8 | 267.6 |  | 269.3 | 259.5 | 243.5 | 228.8
1751.1 | 1644.1 | 231.5 | 267.5 |  | 269.1 | 259.3 | 243.4 | 228.6
1752.1 | 1645.1 | 231.3 | 267.3 |  | 269 | 259.2 | 243.2 | 228.5
1753.1 | 1646.1 | 231 | 267.1 |  | 268.8 | 259 | 242.9 | 228.3
1754.1 | 1647.1 | 230.8 | 266.9 |  | 268.7 | 258.8 | 242.7 | 228.1
1755.1 | 1648.1 | 230.6 | 266.8 |  | 268.5 | 258.7 | 242.6 | 228
1756.1 | 1649.1 | 230.4 | 266.6 |  | 268.4 | 258.5 | 242.4 | 227.8
1757.1 | 1650.1 | 230.2 | 266.4 |  | 268.2 | 258.3 | 242.2 | 227.6
1758.1 | 1651.1 | 229.9 | 266.2 |  | 268.1 | 258.1 | 241.9 | 227.5
1759.1 | 1652.1 | 229.7 | 266 |  | 267.9 | 258 | 241.7 | 227.3
1760.1 | 1653.1 | 229.4 | 265.8 |  | 267.8 | 257.8 | 241.5 | 227.1
1761.1 | 1654.1 | 229.2 | 265.7 |  | 267.6 | 257.6 | 241.4 | 226.9
1762.1 | 1655.1 | 228.9 | 265.5 |  | 267.5 | 257.5 | 241.2 | 226.8
1763.1 | 1656.1 | 228.7 | 265.3 |  | 267.3 | 257.3 | 241 | 226.6
1764.1 | 1657.1 | 228.5 | 265.1 |  | 267.2 | 257.1 | 240.8 | 226.4
1765.1 | 1658.1 | 228.2 | 265 |  | 267 | 257 | 240.5 | 226.2
1766.1 | 1659.1 | 228 | 264.8 |  | 266.8 | 256.8 | 240.4 | 226.1
1767.1 | 1660.1 | 227.7 | 264.6 |  | 266.7 | 256.6 | 240.2 | 225.9
1768.1 | 1661.1 | 227.5 | 264.5 |  | 266.5 | 256.5 | 240.1 | 225.7
1769.1 | 1662.1 | 227.3 | 264.3 |  | 266.4 | 256.3 | 239.9 | 225.6
1770.1 | 1663.1 | 227.1 | 264.1 |  | 266.2 | 256.1 | 239.7 | 225.4
1771.1 | 1664.1 | 226.8 | 263.9 |  | 266.1 | 256 | 239.5 | 225.2
1772.1 | 1665.1 | 226.6 | 263.7 |  | 265.9 | 255.8 | 239.3 | 225.1
1773.1 | 1666.1 | 226.4 | 263.6 |  | 265.8 | 255.6 | 239.1 | 224.9
1774.1 | 1667.1 | 226.2 | 263.4 |  | 265.6 | 255.5 | 238.9 | 224.7
1775.1 | 1668.1 | 226 | 263.2 |  | 265.4 | 255.3 | 238.7 | 224.6
1776.1 | 1669.1 | 225.7 | 263 |  | 265.3 | 255.1 | 238.5 | 224.4
1777.1 | 1670.1 | 225.5 | 262.9 |  | 265.1 | 254.9 | 238.2 | 224.2
1778.1 | 1671.1 | 225.3 | 262.7 |  | 265 | 254.8 | 238.1 | 224.1
1779.1 | 1672.1 | 225.1 | 262.5 |  | 264.8 | 254.6 | 237.9 | 223.9
1780.1 | 1673.1 | 224.8 | 262.3 |  | 264.7 | 254.4 | 237.8 | 223.7
1781.1 | 1674.1 | 224.6 | 262.1 |  | 264.5 | 254.3 | 237.6 | 223.6
1782.1 | 1675.1 | 224.4 | 261.9 |  | 264.3 | 254.1 | 237.5 | 223.4
1783.1 | 1676.1 | 224.2 | 261.8 |  | 264.2 | 253.9 | 237.3 | 223.2
1784.1 | 1677.1 | 223.9 | 261.6 |  | 264 | 253.7 | 237.1 | 223.1
1785.1 | 1678.1 | 223.7 | 261.4 |  | 263.8 | 253.6 | 236.9 | 222.9
1786.1 | 1679.1 | 223.5 | 261.2 |  | 263.7 | 253.4 | 236.7 | 222.7
1787.1 | 1680.1 | 223.3 | 261.1 |  | 263.5 | 253.2 | 236.5 | 222.5
1788.1 | 1681.1 | 223.1 | 260.9 |  | 263.4 | 253.1 | 236.3 | 222.4
1789.1 | 1682.1 | 222.8 | 260.7 |  | 263.2 | 252.9 | 236.2 | 222.2
1790.1 | 1683.1 | 222.6 | 260.5 |  | 263.1 | 252.7 | 236 | 222
1791.1 | 1684.1 | 222.4 | 260.3 |  | 262.9 | 252.6 | 235.8 | 221.9
1792.1 | 1685.1 | 222.2 | 260.2 |  | 262.7 | 252.4 | 235.7 | 221.7
1793.1 | 1686.1 | 222 | 260 |  | 262.6 | 252.2 | 235.5 | 221.6
1794.1 | 1687.1 | 221.7 | 259.8 |  | 262.4 | 252.1 | 235.3 | 221.4
1795.1 | 1688.1 | 221.5 | 259.6 |  | 262.3 | 251.9 | 235.1 | 221.2
1796.1 | 1689.1 | 221.3 | 259.4 |  | 262.1 | 251.7 | 235 | 221.1
1797.1 | 1690.1 | 221.1 | 259.3 |  | 261.9 | 251.6 | 234.8 | 220.9
1798.1 | 1691.1 | 220.9 | 259.1 |  | 261.8 | 251.4 | 234.7 | 220.7
1799.1 | 1692.1 | 220.6 | 258.9 |  | 261.6 | 251.2 | 234.5 | 220.6
1800.1 | 1693.1 | 220.4 | 258.7 |  | 261.4 | 251.1 | 234.3 | 220.4
1801.1 | 1694.1 | 220.2 | 258.6 |  | 261.3 | 250.9 | 234.1 | 220.2
1802.1 | 1695.1 | 220 | 258.4 |  | 261.1 | 250.7 | 233.9 | 220.1
1803.1 | 1696.1 | 219.7 | 258.2 |  | 261 | 250.6 | 233.7 | 219.9
1804.1 | 1697.1 | 219.5 | 258 |  | 260.8 | 250.4 | 233.4 | 219.8
1805.1 | 1698.1 | 219.3 | 257.8 |  | 260.6 | 250.2 | 233.2 | 219.6
1806.1 | 1699.1 | 219.1 | 257.7 |  | 260.5 | 250.1 | 232.9 | 219.4
1807.1 | 1700.1 | 218.9 | 257.5 |  | 260.3 | 249.9 | 232.8 | 219.3
1808.1 | 1701.1 | 218.7 | 257.3 |  | 260.2 | 249.7 | 232.6 | 219.1
1809.1 | 1702.1 | 218.5 | 257.1 |  | 260 | 249.5 | 232.4 | 218.9
1810.1 | 1703.1 | 218.3 | 257 |  | 259.8 | 249.4 | 232.3 | 218.8
1811.1 | 1704.1 | 218.1 | 256.8 |  | 259.7 | 249.2 | 232.1 | 218.6
1812.1 | 1705.1 | 217.9 | 256.6 |  | 259.5 | 249 | 232 | 218.5
1813.1 | 1706.1 | 217.7 | 256.4 |  | 259.3 | 248.9 | 231.8 | 218.3
1814.1 | 1707.1 | 217.5 | 256.3 |  | 259.2 | 248.7 | 231.7 | 218.1
1815.1 | 1708.1 | 217.3 | 256.1 |  | 259 | 248.5 | 231.5 | 218
1816.1 | 1709.1 | 217.1 | 255.9 |  | 258.9 | 248.3 | 231.4 | 217.8
1817.1 | 1710.1 | 216.9 | 255.7 |  | 258.7 | 248.2 | 231.2 | 217.7
1818.1 | 1711.1 | 216.6 | 255.5 |  | 258.5 | 248 | 231 | 217.5
1819.1 | 1712.1 | 216.4 | 255.4 |  | 258.4 | 247.8 | 230.8 | 217.3
1820.1 | 1713.1 | 216.2 | 255.2 |  | 258.2 | 247.6 | 230.6 | 217.2
1821.1 | 1714.1 | 216 | 255 |  | 258 | 247.5 | 230.5 | 217
1822.1 | 1715.1 | 215.7 | 254.8 |  | 257.9 | 247.3 | 230.3 | 216.9
1823.1 | 1716.1 | 215.5 | 254.6 |  | 257.7 | 247.1 | 230.1 | 216.7
1824.1 | 1717.1 | 215.3 | 254.5 |  | 257.5 | 246.9 | 229.9 | 216.5
1825.1 | 1718.1 | 215.1 | 254.3 |  | 257.4 | 246.8 | 229.8 | 216.4
1826.1 | 1719.1 | 214.8 | 254.1 |  | 257.2 | 246.6 | 229.6 | 216.2
1827.1 | 1720.1 | 214.6 | 253.9 |  | 257 | 246.4 | 229.4 | 216
1828.1 | 1721.1 | 214.4 | 253.8 |  | 256.9 | 246.2 | 229.3 | 215.9
1829.1 | 1722.1 | 214.2 | 253.6 |  | 256.7 | 246.1 | 229.1 | 215.7
1830.1 | 1723.1 | 214 | 253.4 |  | 256.5 | 245.9 | 228.9 | 215.6
1831.1 | 1724.1 | 213.8 | 253.2 |  | 256.4 | 245.7 | 228.7 | 215.4
1832.1 | 1725.1 | 213.6 | 253 |  | 256.2 | 245.6 | 228.5 | 215.2
1833.1 | 1726.1 | 213.4 | 252.8 |  | 256 | 245.4 | 228.3 | 215.1
1834.1 | 1727.1 | 213.2 | 252.7 |  | 255.9 | 245.2 | 228.2 | 214.9
1835.1 | 1728.1 | 213 | 252.5 |  | 255.7 | 245 | 228 | 214.7
1836.1 | 1729.1 | 212.8 | 252.3 |  | 255.5 | 244.9 | 227.8 | 214.6
1837.1 | 1730.1 | 212.6 | 252.1 |  | 255.4 | 244.7 | 227.6 | 214.4
1838.1 | 1731.1 | 212.4 | 251.9 |  | 255.2 | 244.5 | 227.4 | 214.3
1839.1 | 1732.1 | 212.2 | 251.8 |  | 255 | 244.4 | 227.3 | 214.1
1840.1 | 1733.1 | 212 | 251.6 |  | 254.9 | 244.2 | 227.1 | 214
1841.1 | 1734.1 | 211.8 | 251.4 |  | 254.7 | 244 | 227 | 213.8
1842.1 | 1735.1 | 211.6 | 251.2 |  | 254.5 | 243.9 | 226.8 | 213.6
1843.1 | 1736.1 | 211.4 | 251.1 |  | 254.4 | 243.7 | 226.6 | 213.5
1844.1 | 1737.1 | 211.2 | 250.9 |  | 254.2 | 243.5 | 226.5 | 213.3
1845.1 | 1738.1 | 211 | 250.7 |  | 254 | 243.4 | 226.3 | 213.2
1846.1 | 1739.1 | 210.8 | 250.5 |  | 253.9 | 243.2 | 226.1 | 213
1847.1 | 1740.1 | 210.6 | 250.3 |  | 253.7 | 243 | 225.9 | 212.9
1848.1 | 1741.1 | 210.4 | 250.2 |  | 253.5 | 242.9 | 225.8 | 212.7
1849.1 | 1742.1 | 210.2 | 250 |  | 253.4 | 242.7 | 225.6 | 212.5
1850.1 | 1743.1 | 210 | 249.8 |  | 253.2 | 242.5 | 225.5 | 212.4
1851.1 | 1744.1 | 209.8 | 249.6 |  | 253 | 242.4 | 225.3 | 212.2
1852.1 | 1745.1 | 209.6 | 249.5 |  | 252.9 | 242.2 | 225.1 | 212.1
1853.1 | 1746.1 | 209.4 | 249.3 |  | 252.7 | 242 | 225 | 211.9
1854.1 | 1747.1 | 209.2 | 249.1 |  | 252.5 | 241.9 | 224.8 | 211.8
1855.1 | 1748.1 | 209 | 248.9 |  | 252.4 | 241.7 | 224.6 | 211.6
1856.1 | 1749.1 | 208.8 | 248.8 |  | 252.2 | 241.5 | 224.5 | 211.5
1857.1 | 1750.1 | 208.6 | 248.6 |  | 252.1 | 241.4 | 224.3 | 211.3
1858.1 | 1751.1 | 208.4 | 248.4 |  | 251.9 | 241.2 | 224.1 | 211.1
1859.1 | 1752.1 | 208.2 | 248.2 |  | 251.7 | 241.1 | 223.9 | 211
1860.1 | 1753.1 | 208.1 | 248 |  | 251.5 | 240.9 | 223.8 | 210.8
1861.1 | 1754.1 | 207.9 | 247.9 |  | 251.4 | 240.7 | 223.6 | 210.7
1862.1 | 1755.1 | 207.7 | 247.7 |  | 251.2 | 240.6 | 223.4 | 210.5
1863.1 | 1756.1 | 207.5 | 247.5 |  | 251.1 | 240.4 | 223.3 | 210.4
1864.1 | 1757.1 | 207.3 | 247.3 |  | 250.9 | 240.2 | 223.1 | 210.2
1865.1 | 1758.1 | 207.1 | 247.2 |  | 250.7 | 240.1 | 223 | 210.1
1866.1 | 1759.1 | 206.9 | 247 |  | 250.6 | 239.9 | 222.8 | 209.9
1867.1 | 1760.1 | 206.7 | 246.8 |  | 250.4 | 239.7 | 222.6 | 209.8
1868.1 | 1761.1 | 206.5 | 246.6 |  | 250.2 | 239.6 | 222.4 | 209.6
1869.1 | 1762.1 | 206.4 | 246.4 |  | 250.1 | 239.4 | 222.2 | 209.5
1870.1 | 1763.1 | 206.2 | 246.3 |  | 249.9 | 239.2 | 222 | 209.3
1871.1 | 1764.1 | 206 | 246.1 |  | 249.7 | 239.1 | 221.8 | 209.2
1872.1 | 1765.1 | 205.8 | 245.9 |  | 249.6 | 238.9 | 221.6 | 209
1873.1 | 1766.1 | 205.6 | 245.7 |  | 249.4 | 238.7 | 221.5 | 208.9
1874.1 | 1767.1 | 205.4 | 245.5 |  | 249.2 | 238.6 | 221.3 | 208.7
1875.1 | 1768.1 | 205.2 | 245.4 |  | 249.1 | 238.4 | 221.2 | 208.6
1876.1 | 1769.1 | 205 | 245.2 |  | 248.9 | 238.2 | 221 | 208.4
1877.1 | 1770.1 | 204.8 | 245 |  | 248.7 | 238 | 220.8 | 208.3
1878.1 | 1771.1 | 204.6 | 244.8 |  | 248.5 | 237.9 | 220.6 | 208.1
1879.1 | 1772.1 | 204.5 | 244.7 |  | 248.4 | 237.7 | 220.5 | 208
1880.1 | 1773.1 | 204.3 | 244.5 |  | 248.2 | 237.5 | 220.3 | 207.8
1881.1 | 1774.1 | 204.1 | 244.3 |  | 248 | 237.4 | 220.1 | 207.7
1882.1 | 1775.1 | 203.9 | 244.1 |  | 247.9 | 237.2 | 220 | 207.5
1883.1 | 1776.1 | 203.7 | 244 |  | 247.7 | 237 | 219.9 | 207.3
1884.1 | 1777.1 | 203.5 | 243.8 |  | 247.5 | 236.8 | 219.7 | 207.2
1885.1 | 1778.1 | 203.3 | 243.6 |  | 247.4 | 236.7 | 219.5 | 207
1886.1 | 1779.1 | 203.2 | 243.4 |  | 247.2 | 236.5 | 219.3 | 206.9
1887.1 | 1780.1 | 203 | 243.3 |  | 247 | 236.3 | 219.2 | 206.7
1888.1 | 1781.1 | 202.8 | 243.1 |  | 246.9 | 236.2 | 219 | 206.6
1889.1 | 1782.1 | 202.6 | 242.9 |  | 246.7 | 236 | 218.9 | 206.4
1890.1 | 1783.1 | 202.4 | 242.7 |  | 246.5 | 235.8 | 218.7 | 206.3
1891.1 | 1784.1 | 202.2 | 242.6 |  | 246.3 | 235.6 | 218.6 | 206.1
1892.1 | 1785.1 | 202 | 242.4 |  | 246.2 | 235.5 | 218.4 | 206
1893.1 | 1786.1 | 201.8 | 242.2 |  | 246 | 235.3 | 218.3 | 205.8
1894.1 | 1787.1 | 201.7 | 242 |  | 245.8 | 235.1 | 218.1 | 205.7
1895.1 | 1788.1 | 201.5 | 241.9 |  | 245.7 | 235 | 217.9 | 205.5
1896.1 | 1789.1 | 201.3 | 241.7 |  | 245.5 | 234.8 | 217.8 | 205.4
1897.1 | 1790.1 | 201.1 | 241.5 |  | 245.3 | 234.7 | 217.6 | 205.2
1898.1 | 1791.1 | 200.9 | 241.3 |  | 245.2 | 234.5 | 217.5 | 205.1
1899.1 | 1792.1 | 200.8 | 241.2 |  | 245 | 234.3 | 217.3 | 204.9
1900.1 | 1793.1 | 200.6 | 241 |  | 244.8 | 234.2 | 217.2 | 204.8
1901.1 | 1794.1 | 200.4 | 240.8 |  | 244.7 | 234 | 217 | 204.6
1902.1 | 1795.1 | 200.2 | 240.7 |  | 244.5 | 233.8 | 216.8 | 204.4
1903.1 | 1796.1 | 200.1 | 240.5 |  | 244.3 | 233.7 | 216.7 | 204.3
1904.1 | 1797.1 | 199.9 | 240.3 |  | 244.2 | 233.5 | 216.5 | 204.2
1905.1 | 1798.1 | 199.7 | 240.1 |  | 244 | 233.3 | 216.4 | 204
1906.1 | 1799.1 | 199.5 | 240 |  | 243.8 | 233.2 | 216.2 | 203.8
1907.1 | 1800.1 | 199.3 | 239.8 |  | 243.6 | 233 | 216 | 203.7
1908.1 | 1801.1 | 199.1 | 239.6 |  | 243.5 | 232.8 | 215.9 | 203.5
1909.1 | 1802.1 | 199 | 239.4 |  | 243.3 | 232.7 | 215.7 | 203.4
1910.1 | 1803.1 | 198.8 | 239.3 |  | 243.2 | 232.5 | 215.6 | 203.2
1911.1 | 1804.1 | 198.6 | 239.1 |  | 243 | 232.3 | 215.4 | 203.1
1912.1 | 1805.1 | 198.4 | 238.9 |  | 242.8 | 232.2 | 215.3 | 203
1913.1 | 1806.1 | 198.3 | 238.8 |  | 242.6 | 232 | 215.1 | 202.8
1914.1 | 1807.1 | 198.1 | 238.6 |  | 242.5 | 231.9 | 214.9 | 202.7
1915.1 | 1808.1 | 197.9 | 238.4 |  | 242.3 | 231.7 | 214.7 | 202.5
1916.1 | 1809.1 | 197.7 | 238.3 |  | 242.1 | 231.5 | 214.6 | 202.4
1917.1 | 1810.1 | 197.5 | 238.1 |  | 242 | 231.4 | 214.4 | 202.2
1918.1 | 1811.1 | 197.3 | 237.9 |  | 241.8 | 231.2 | 214.2 | 202.1
1919.1 | 1812.1 | 197.1 | 237.7 |  | 241.6 | 231 | 214 | 201.9
1920.1 | 1813.1 | 196.9 | 237.6 |  | 241.5 | 230.8 | 213.9 | 201.8
1921.1 | 1814.1 | 196.7 | 237.4 |  | 241.3 | 230.7 | 213.8 | 201.6
1922.1 | 1815.1 | 196.6 | 237.2 |  | 241.1 | 230.5 | 213.6 | 201.5
1923.1 | 1816.1 | 196.4 | 237.1 |  | 241 | 230.3 | 213.5 | 201.4
1924.1 | 1817.1 | 196.2 | 236.9 |  | 240.8 | 230.2 | 213.3 | 201.2
1925.1 | 1818.1 | 196.1 | 236.7 |  | 240.6 | 230 | 213.1 | 201.1
1926.1 | 1819.1 | 195.9 | 236.6 |  | 240.5 | 229.8 | 212.9 | 200.9
1927.1 | 1820.1 | 195.7 | 236.4 |  | 240.3 | 229.7 | 212.8 | 200.8
1928.1 | 1821.1 | 195.5 | 236.2 |  | 240.1 | 229.5 | 212.6 | 200.6
1929.1 | 1822.1 | 195.4 | 236 |  | 240 | 229.3 | 212.4 | 200.5
1930.1 | 1823.1 | 195.2 | 235.9 |  | 239.8 | 229.2 | 212.2 | 200.4
1931.1 | 1824.1 | 195 | 235.7 |  | 239.6 | 229 | 212 | 200.2
1932.1 | 1825.1 | 194.9 | 235.5 |  | 239.5 | 228.9 | 211.9 | 200.1
1933.1 | 1826.1 | 194.7 | 235.4 |  | 239.3 | 228.7 | 211.7 | 199.9
1934.1 | 1827.1 | 194.5 | 235.2 |  | 239.1 | 228.5 | 211.6 | 199.8
1935.1 | 1828.1 | 194.4 | 235 |  | 239 | 228.4 | 211.4 | 199.6
1936.1 | 1829.1 | 194.2 | 234.9 |  | 238.8 | 228.2 | 211.3 | 199.5
1937.1 | 1830.1 | 194.1 | 234.7 |  | 238.6 | 228 | 211.2 | 199.4
1938.1 | 1831.1 | 193.9 | 234.5 |  | 238.5 | 227.9 | 211 | 199.2
1939.1 | 1832.1 | 193.7 | 234.4 |  | 238.3 | 227.7 | 210.9 | 199.1
1940.1 | 1833.1 | 193.6 | 234.2 |  | 238.1 | 227.5 | 210.7 | 198.9
1941.1 | 1834.1 | 193.4 | 234 |  | 238 | 227.4 | 210.5 | 198.8
1942.1 | 1835.1 | 193.2 | 233.8 |  | 237.8 | 227.2 | 210.4 | 198.7
1943.1 | 1836.1 | 193.1 | 233.7 |  | 237.6 | 227 | 210.2 | 198.5
1944.1 | 1837.1 | 192.9 | 233.5 |  | 237.5 | 226.9 | 210.1 | 198.4
1945.1 | 1838.1 | 192.7 | 233.3 |  | 237.3 | 226.7 | 209.9 | 198.2
1946.1 | 1839.1 | 192.6 | 233.2 |  | 237.1 | 226.5 | 209.8 | 198.1
1947.1 | 1840.1 | 192.4 | 233 |  | 237 | 226.4 | 209.6 | 197.9
1948.1 | 1841.1 | 192.2 | 232.8 |  | 236.8 | 226.2 | 209.5 | 197.8
1949.1 | 1842.1 | 192 | 232.7 |  | 236.6 | 226 | 209.3 | 197.6
1950.1 | 1843.1 | 191.8 | 232.5 |  | 236.5 | 225.9 | 209.2 | 197.5
1951.1 | 1844.1 | 191.7 | 232.3 |  | 236.3 | 225.7 | 209 | 197.4
1952.1 | 1845.1 | 191.5 | 232.2 |  | 236.1 | 225.5 | 208.8 | 197.2
1953.1 | 1846.1 | 191.3 | 232 |  | 235.9 | 225.3 | 208.6 | 197.1
1954.1 | 1847.1 | 191.2 | 231.8 |  | 235.8 | 225.2 | 208.4 | 196.9
1955.1 | 1848.1 | 191 | 231.6 |  | 235.6 | 225 | 208.3 | 196.8
1956.1 | 1849.1 | 190.8 | 231.5 |  | 235.5 | 224.8 | 208.1 | 196.6
1957.1 | 1850.1 | 190.7 | 231.3 |  | 235.3 | 224.7 | 208 | 196.5
1958.1 | 1851.1 | 190.5 | 231.1 |  | 235.1 | 224.5 | 207.8 | 196.3
1959.1 | 1852.1 | 190.3 | 231 |  | 235 | 224.3 | 207.6 | 196.2
1960.1 | 1853.1 | 190.2 | 230.8 |  | 234.8 | 224.2 | 207.5 | 196.1
1961.1 | 1854.1 | 190 | 230.6 |  | 234.6 | 224 | 207.3 | 195.9
1962.1 | 1855.1 | 189.8 | 230.5 |  | 234.5 | 223.8 | 207.2 | 195.8
1963.1 | 1856.1 | 189.7 | 230.3 |  | 234.3 | 223.7 | 207 | 195.6
1964.1 | 1857.1 | 189.5 | 230.1 |  | 234.1 | 223.5 | 206.8 | 195.5
1965.1 | 1858.1 | 189.3 | 230 |  | 234 | 223.3 | 206.6 | 195.3
1966.1 | 1859.1 | 189.1 | 229.8 |  | 233.8 | 223.2 | 206.5 | 195.2
1967.1 | 1860.1 | 189 | 229.6 |  | 233.6 | 223 | 206.3 | 195.1
1968.1 | 1861.1 | 188.8 | 229.5 |  | 233.5 | 222.8 | 206.2 | 194.9
1969.1 | 1862.1 | 188.7 | 229.3 |  | 233.3 | 222.7 | 206 | 194.8
1970.1 | 1863.1 | 188.5 | 229.1 |  | 233.1 | 222.5 | 205.9 | 194.6
1971.1 | 1864.1 | 188.3 | 229 |  | 233 | 222.4 | 205.8 | 194.5
1972.1 | 1865.1 | 188.2 | 228.8 |  | 232.8 | 222.2 | 205.6 | 194.4
1973.1 | 1866.1 | 188 | 228.6 |  | 232.6 | 222 | 205.5 | 194.2
1974.1 | 1867.1 | 187.8 | 228.5 |  | 232.5 | 221.9 | 205.3 | 194.1
1975.1 | 1868.1 | 187.7 | 228.3 |  | 232.3 | 221.7 | 205.2 | 193.9
1976.1 | 1869.1 | 187.5 | 228.2 |  | 232.1 | 221.6 | 205 | 193.8
1977.1 | 1870.1 | 187.3 | 228 |  | 232 | 221.4 | 204.8 | 193.7
1978.1 | 1871.1 | 187.2 | 227.8 |  | 231.8 | 221.2 | 204.6 | 193.5
1979.1 | 1872.1 | 187.1 | 227.7 |  | 231.7 | 221.1 | 204.5 | 193.4
1980.1 | 1873.1 | 186.9 | 227.5 |  | 231.5 | 220.9 | 204.4 | 193.2
1981.1 | 1874.1 | 186.8 | 227.3 |  | 231.3 | 220.8 | 204.2 | 193.1
1982.1 | 1875.1 | 186.6 | 227.2 |  | 231.2 | 220.6 | 204.1 | 193
1983.1 | 1876.1 | 186.5 | 227 |  | 231 | 220.4 | 204 | 192.8

## C6-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 6 & 7
Time-41 | N11 | N12 | Time-42 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
38938.3981 | 1 | 0 | 38938.3982 | 1 | 0 | -50.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3988 | 1 | 0 | 38938.3988 | 1 | 0 | 8.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3995 | 1 | 0 | 38938.3995 | 1 | 0 | 67 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4002 | 1 | 0 | 38938.4002 | 1 | 0 | 126 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4009 | 1 | 0 | 38938.4009 | 1 | 0 | 184.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4016 | 1 | 0 | 38938.4016 | 1 | 0 | 243.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4022 | 1 | 0 | 38938.4022 | 1 | 0 | 302.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4029 | 1 | 0 | 38938.4029 | 1 | 0 | 361 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4036 | 1 | 0 | 38938.4036 | 1 | 0 | 420 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4043 | 1 | 0 | 38938.4043 | 1 | 0 | 478.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.405 | 1 | 0 | 38938.405 | 1 | 0 | 537.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4056 | 1 | 0 | 38938.4056 | 1 | 0 | 596 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4063 | 1134 | 1185 | 38938.4063 | 996 | 966 | 655 | 762 | 69.2308 | 72.3443 | 60.8059 | 58.9744 | 0.69231 | 0.72344 | 0.60806 | 0.58974 | 0.031136 | 0.018315 | 238.7012 | 329.9508 | 13.3394
38938.407 | 1183 | 1120 | 38938.407 | 1077 | 1162 | 713.5 | 820.5 | 72.2222 | 68.3761 | 65.7509 | 70.9402 | 0.72222 | 0.68376 | 0.65751 | 0.7094 | 0.038462 | 0.051893 | 1129.0088 | 5780.6709 | 16.6741
38938.4077 | 995 | 951 | 38938.4077 | 1064 | 1032 | 772.5 | 879.5 | 60.7448 | 58.0586 | 64.9573 | 63.0037 | 0.60745 | 0.58059 | 0.64957 | 0.63004 | 0.026862 | 0.019536 | 1217.137 | 1987.1891 | 16.7211
38938.4084 | 986 | 955 | 38938.4084 | 939 | 911 | 831.5 | 938.5 | 60.1954 | 58.3028 | 57.326 | 55.6166 | 0.60195 | 0.58303 | 0.57326 | 0.55617 | 0.018926 | 0.017094 | 4693.4941 | 13667.0433 | 17.8817
38938.409 | 1192 | 1191 | 38938.4091 | 1070 | 1158 | 890.5 | 997.5 | 72.7717 | 72.7106 | 65.3236 | 70.696 | 0.72772 | 0.72711 | 0.65324 | 0.70696 | 0.0006105 | 0.053724 | 403.3497 | 523.8785 | 19.0349
38938.4097 | 942 | 911 | 38938.4097 | 958 | 1077 | 949 | 1056 | 57.5092 | 55.6166 | 58.486 | 65.7509 | 0.57509 | 0.55617 | 0.58486 | 0.65751 | 0.018926 | 0.07265 | 511.5527 | 460.299 | 23.4481
38938.4104 | 1020 | 1063 | 38938.4104 | 965 | 939 | 1007.5 | 1114.5 | 62.2711 | 64.8962 | 58.9133 | 57.326 | 0.62271 | 0.64896 | 0.58913 | 0.57326 | 0.026252 | 0.015873 | 1181.2651 | 2146.191 | 2.6984
38938.4111 | 1165 | 1195 | 38938.4111 | 1157 | 1197 | 1066.5 | 1173.5 | 71.1233 | 72.9548 | 70.6349 | 73.0769 | 0.71123 | 0.72955 | 0.70635 | 0.73077 | 0.018315 | 0.02442 | 2741.1369 | 26063.702 | 20.5888
38938.4118 | 652 | 644 | 38938.4118 | 597 | 586 | 1125.5 | 1232.5 | 39.8046 | 39.3162 | 36.4469 | 35.7753 | 0.39805 | 0.39316 | 0.36447 | 0.35775 | 0.004884 | 0.0067155 | 36429.2873 | 16142.634 | 126.0854
38938.4124 | 275 | 222 | 38938.4125 | 944 | 932 | 1184 | 1291 | 16.7888 | 13.5531 | 57.6313 | 56.8987 | 0.16789 | 0.13553 | 0.57631 | 0.56899 | 0.032357 | 0.007326 | 3274.8274 | 7102.3964 | 717.8301
38938.4131 | 958 | 903 | 38938.4131 | 922 | 953 | 1243 | 1350 | 58.486 | 55.1282 | 56.2882 | 58.1807 | 0.58486 | 0.55128 | 0.56288 | 0.58181 | 0.033578 | 0.018926 | 1373.1015 | 3101.217 | 27.0374
38938.4138 | 922 | 1020 | 38938.4138 | 1187 | 1193 | 1301.5 | 1408.5 | 56.2882 | 62.2711 | 72.4664 | 72.8327 | 0.56288 | 0.62271 | 0.72466 | 0.72833 | 0.059829 | 0.003663 | 134.6469 | 129.6802 | 9.4667
38938.4145 | 1059 | 1035 | 38938.4145 | 1026 | 998 | 1360.5 | 1467.5 | 64.652 | 63.1868 | 62.6374 | 60.928 | 0.64652 | 0.63187 | 0.62637 | 0.60928 | 0.014652 | 0.017094 | 3901.4366 | 34314.678 | 1.8323
38938.4152 | 986 | 984 | 38938.4152 | 1079 | 1030 | 1419.5 | 1526.5 | 60.1954 | 60.0733 | 65.873 | 62.8816 | 0.60195 | 0.60073 | 0.65873 | 0.62882 | 0.001221 | 0.029915 | 329.0313 | 288.9641 | 10.7978
38938.4158 | 956 | 860 | 38938.4159 | 968 | 902 | 1478 | 1585 | 58.3639 | 52.5031 | 59.0965 | 55.0672 | 0.58364 | 0.52503 | 0.59096 | 0.55067 | 0.058608 | 0.040293 | 1032.8653 | 5368.1515 | 33.9056
38938.4165 | 1141 | 884 | 38938.4165 | 1168 | 1133 | 1537 | 1644 | 69.6581 | 53.9683 | 71.3065 | 69.1697 | 0.69658 | 0.53968 | 0.71306 | 0.6917 | 0.1569 | 0.021368 | 39.1609 | 39.7282 | 2.831
38938.4172 | 1034 | 1049 | 38938.4172 | 991 | 919 | 1595.5 | 1702.5 | 63.1258 | 64.0415 | 60.5006 | 56.105 | 0.63126 | 0.64042 | 0.60501 | 0.56105 | 0.0091575 | 0.043956 | 420.2056 | 433.8586 | 2.3257
38938.4179 | 1048 | 985 | 38938.4179 | 1004 | 932 | 1654.5 | 1761.5 | 63.9805 | 60.1343 | 61.2943 | 56.8987 | 0.6398 | 0.60134 | 0.61294 | 0.56899 | 0.038462 | 0.043956 | 25016.4946 | 1676.8033 | 7.6666
38938.4186 | 1137 | 1082 | 38938.4186 | 1123 | 1070 | 1713.5 | 1820.5 | 69.4139 | 66.0562 | 68.5592 | 65.3236 | 0.69414 | 0.66056 | 0.68559 | 0.65324 | 0.033578 | 0.032357 | 6613.7234 | 2688.6995 | 9.4436
38938.4192 | 1156 | 1112 | 38938.4193 | 1044 | 1054 | 1772 | 1879 | 70.5739 | 67.8877 | 63.7363 | 64.3468 | 0.70574 | 0.67888 | 0.63736 | 0.64347 | 0.026862 | 0.006105 | 414.7757 | 595.506 | 11.9332
38938.4199 | 925 | 933 | 38938.4199 | 923 | 974 | 1830.5 | 1937.5 | 56.4713 | 56.9597 | 56.3492 | 59.4628 | 0.56471 | 0.5696 | 0.56349 | 0.59463 | 0.004884 | 0.031136 | 1326.8205 | 1144.2396 | 25.1365
38938.4206 | 962 | 880 | 38938.4206 | 1030 | 971 | 1889.5 | 1996.5 | 58.7302 | 53.7241 | 62.8816 | 59.2796 | 0.5873 | 0.53724 | 0.62882 | 0.5928 | 0.050061 | 0.03602 | 1062.9514 | 3347.88 | 29.9045

## C5-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 5 & 7
Time-39 | N11 | N12 | Time-40 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
38938.3981 | 1 | 0 | 38938.3981 | 1 | 0 | -53.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3988 | 1 | 0 | 38938.3988 | 1 | 0 | 5.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3995 | 1 | 0 | 38938.3995 | 1 | 0 | 64.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4002 | 1 | 0 | 38938.4002 | 1 | 0 | 123 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4008 | 1 | 0 | 38938.4009 | 1 | 0 | 182 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4015 | 1 | 0 | 38938.4015 | 1 | 0 | 240.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4022 | 1 | 0 | 38938.4022 | 1 | 0 | 299.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4029 | 1 | 0 | 38938.4029 | 1 | 0 | 358.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4036 | 1 | 0 | 38938.4036 | 1 | 0 | 417 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4042 | 1 | 0 | 38938.4043 | 1 | 0 | 476 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4049 | 1 | 0 | 38938.4049 | 1 | 0 | 534.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4056 | 1 | 1 | 38938.4056 | 1 | 0 | 593.5 | 700.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38938.4063 | 1130 | 1106 | 38938.4063 | 1113 | 1088 | 652.5 | 759.5 | 68.9866 | 67.5214 | 67.9487 | 66.4225 | 0.68987 | 0.67521 | 0.67949 | 0.66422 | 0.014652 | 0.015263 | 6036.0908 | 14337.0218 | 11.0423
38938.407 | 1191 | 1172 | 38938.407 | 1081 | 1052 | 711 | 818 | 72.7106 | 71.5507 | 65.9951 | 64.2247 | 0.72711 | 0.71551 | 0.65995 | 0.64225 | 0.0116 | 0.017705 | 1956.9427 | 4168.5443 | 20.8297
38938.4076 | 3 | 16 | 38938.4077 | 3 | 14 | 769.5 | 876.5 | 0.18315 | 0.9768 | 0.18315 | 0.8547 | 0.0018315 | 0.009768 | 0.0018315 | 0.008547 | 0.0079365 | 0.0067155 | 16334.9157 | 19332.6293 | 13020.2763
| 3 | 12 | 38938.4083 | 3 | 11 | 829 | 936 | 0.18315 | 0.7326 | 0.18315 | 0.67155 | 0.0018315 | 0.007326 | 0.0018315 | 0.0067155 | 0.0054945 | 0.004884 | 23563.0887 | 26530.0635 | 17417.8468
38938.409 | 3 | 11 | 38938.409 | 3 | 10 | 887.5 | 994.5 | 0.18315 | 0.67155 | 0.18315 | 0.6105 | 0.0018315 | 0.0067155 | 0.0018315 | 0.006105 | 0.004884 | 0.0042735 | 26495.4592 | 30306.5485 | 19019.2438
38938.4097 | 2 | 11 | 38938.4097 | 3 | 11 | 946 | 1053 | 0.1221 | 0.67155 | 0.18315 | 0.67155 | 0.001221 | 0.0067155 | 0.0018315 | 0.0067155 | 0.0054945 | 0.004884 | 23564.3371 | 26530.0552 | 19019.4009
38938.4104 | 3 | 10 | 38938.4104 | 3 | 10 | 1005 | 1112 | 0.18315 | 0.6105 | 0.18315 | 0.6105 | 0.0018315 | 0.006105 | 0.0018315 | 0.006105 | 0.0042735 | 0.0042735 | 30286 | 30286 | 20931.0886
38938.411 | 3 | 12 | 38938.4111 | 4 | 11 | 1063.5 | 1170.5 | 0.18315 | 0.7326 | 0.2442 | 0.67155 | 0.0018315 | 0.007326 | 0.002442 | 0.0067155 | 0.0054945 | 0.0042735 | 23548.1822 | 30331.2652 | 17426.0476
38938.4117 | 993 | 1046 | 38938.4117 | 826 | 806 | 1122.5 | 1229.5 | 60.6227 | 63.8584 | 50.4274 | 49.2063 | 0.60623 | 0.63858 | 0.50427 | 0.49206 | 0.032357 | 0.01221 | 1265.3544 | 2945.2895 | 6.8441
38938.4124 | 123 | 115 | 38938.4124 | 207 | 240 | 1181.5 | 1288.5 | 7.5092 | 7.0208 | 12.6374 | 14.652 | 0.075092 | 0.070208 | 0.12637 | 0.14652 | 0.004884 | 0.020147 | 32876.6726 | 5906.4768 | 1603.3073
38938.4131 | 1146 | 1113 | 38938.4131 | 1038 | 989 | 1240 | 1347 | 69.9634 | 67.9487 | 63.37 | 60.3785 | 0.69963 | 0.67949 | 0.6337 | 0.60379 | 0.020147 | 0.029915 | 321.0223 | 414.9403 | 10.5688
38938.4138 | 949 | 924 | 38938.4138 | 1069 | 1045 | 1299 | 1406 | 57.9365 | 56.4103 | 65.2625 | 63.7973 | 0.57937 | 0.5641 | 0.65263 | 0.63797 | 0.015263 | 0.014652 | 6362.0884 | 13783.2137 | 25.7891
38938.4144 | 927 | 1023 | 38938.4145 | 957 | 950 | 1357.5 | 1464.5 | 56.5934 | 62.4542 | 58.4249 | 57.9976 | 0.56593 | 0.62454 | 0.58425 | 0.57998 | 0.058608 | 0.0042735 | 384.5354 | 481.5719 | 13.1954
38938.4151 | 924 | 930 | 38938.4151 | 1046 | 1060 | 1416.5 | 1523.5 | 56.4103 | 56.7766 | 63.8584 | 64.7131 | 0.5641 | 0.56777 | 0.63858 | 0.64713 | 0.003663 | 0.008547 | 4274.9056 | 4263.3273 | 27.2133
38938.4158 | 1101 | 1048 | 38938.4158 | 952 | 881 | 1475.5 | 1582.5 | 67.2161 | 63.9805 | 58.1197 | 53.7851 | 0.67216 | 0.6398 | 0.5812 | 0.53785 | 0.032357 | 0.043346 | 1955.015 | 84881.0662 | 3.4292
38938.4165 | 973 | 931 | 38938.4165 | 1168 | 1140 | 1534 | 1641 | 59.4017 | 56.8376 | 71.3065 | 69.5971 | 0.59402 | 0.56838 | 0.71306 | 0.69597 | 0.025641 | 0.017094 | 117.4623 | 100.2648 | 11.2404
38938.4172 | 1003 | 939 | 38938.4172 | 1045 | 980 | 1593 | 1700 | 61.2332 | 57.326 | 63.7973 | 59.8291 | 0.61233 | 0.57326 | 0.63797 | 0.59829 | 0.039072 | 0.039683 | 3625.2174 | 2813.0116 | 17.5878
38938.4178 | 1171 | 1139 | 38938.4179 | 1017 | 972 | 1651.5 | 1758.5 | 71.4896 | 69.536 | 62.0879 | 59.3407 | 0.7149 | 0.69536 | 0.62088 | 0.59341 | 0.019536 | 0.027473 | 461.2136 | 661.2554 | 15.0223
38938.4185 | 1054 | 985 | 38938.4185 | 1146 | 1095 | 1710.5 | 1817.5 | 64.3468 | 60.1343 | 69.9634 | 66.8498 | 0.64347 | 0.60134 | 0.69963 | 0.6685 | 0.042125 | 0.031136 | 330.4034 | 391.6138 | 5.9861
38938.4192 | 1021 | 956 | 38938.4192 | 1046 | 1071 | 1769.5 | 1876.5 | 62.3321 | 58.3639 | 63.8584 | 65.3846 | 0.62332 | 0.58364 | 0.63858 | 0.65385 | 0.039683 | 0.015263 | 310.9166 | 334.0018 | 10.9497
38938.4199 | 1017 | 1022 | 38938.4199 | 972 | 892 | 1828 | 1935 | 62.0879 | 62.3932 | 59.3407 | 54.4567 | 0.62088 | 0.62393 | 0.59341 | 0.54457 | 0.0030525 | 0.04884 | 445.6738 | 424.1997 | 5.861
38938.4206 | 1060 | 884 | 38938.4206 | 1062 | 1004 | 1886.5 | 1993.5 | 64.7131 | 53.9683 | 64.8352 | 61.2943 | 0.64713 | 0.53968 | 0.64835 | 0.61294 | 0.10745 | 0.035409 | 163.9467 | 189.5799 | 12.5173

## C5-6
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 5 & 6
Time-37 | N11 | N12 | Time-38 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38938.3981 | 1 | 0 | 38938.3981 | 1 | 0 | -56 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3988 | 1 | 0 | 38938.3988 | 1 | 0 | 2.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3994 | 1 | 0 | 38938.3995 | 1 | 0 | 61.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4001 | 1 | 0 | 38938.4001 | 1 | 0 | 120.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4008 | 1 | 0 | 38938.4008 | 1 | 0 | 179 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4015 | 1 | 1 | 38938.4015 | 1 | 0 | 238 | 345 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38938.4022 | 1 | 0 | 38938.4022 | 1 | 0 | 296.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4028 | 1 | 0 | 38938.4029 | 1 | 0 | 355.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4035 | 1 | 0 | 38938.4035 | 1 | 0 | 414.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4042 | 1 | 0 | 38938.4042 | 1 | 0 | 473 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4049 | 1 | 0 | 38938.4049 | 1 | 0 | 531.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4056 | 1 | 0 | 38938.4056 | 1 | 0 | 590.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4062 | 1095 | 1069 | 38938.4063 | 1183 | 1193 | 649.5 | 756.5 | 66.8498 | 65.2625 | 72.2222 | 72.8327 | 0.6685 | 0.65263 | 0.72222 | 0.72833 | 0.015873 | 0.006105 | 2435.3252 | 6764.8726 | 4.6995
38938.4069 | 1183 | 1189 | 38938.4069 | 1077 | 1127 | 708 | 815 | 72.2222 | 72.5885 | 65.7509 | 68.8034 | 0.72222 | 0.72589 | 0.65751 | 0.68803 | 0.003663 | 0.030525 | 707.2257 | 947.3909 | 19.7017
38938.4076 | 4 | 18 | 38938.4076 | 3 | 17 | 767 | 874 | 0.2442 | 1.0989 | 0.18315 | 1.0379 | 0.002442 | 0.010989 | 0.0018315 | 0.010379 | 0.008547 | 0.008547 | 15193 | 15193 | 11540.8164
38938.4083 | 3 | 17 | 38938.4083 | 3 | 15 | 825.5 | 932.5 | 0.18315 | 1.0379 | 0.18315 | 0.91575 | 0.0018315 | 0.010379 | 0.0018315 | 0.0091575 | 0.008547 | 0.007326 | 15175.5076 | 17729.5374 | 12242.8291
38938.409 | 3 | 18 | 38938.409 | 3 | 16 | 884.5 | 991.5 | 0.18315 | 1.0989 | 0.18315 | 0.9768 | 0.0018315 | 0.010989 | 0.0018315 | 0.009768 | 0.0091575 | 0.0079365 | 14170.6579 | 16373.1292 | 11551.7801
38938.4097 | 3 | 16 | 38938.4097 | 3 | 11 | 943.5 | 1050.5 | 0.18315 | 0.9768 | 0.18315 | 0.67155 | 0.0018315 | 0.009768 | 0.0018315 | 0.0067155 | 0.0079365 | 0.004884 | 16306.3732 | 26599.545 | 13038.6068
38938.4103 | 3 | 12 | 38938.4103 | 3 | 11 | 1002 | 1109 | 0.18315 | 0.7326 | 0.18315 | 0.67155 | 0.0018315 | 0.007326 | 0.0018315 | 0.0067155 | 0.0054945 | 0.004884 | 23563.0887 | 26530.0635 | 17417.8468
38938.411 | 68 | 86 | 38938.411 | 36 | 32 | 1061 | 1168 | 4.1514 | 5.2503 | 2.1978 | 1.9536 | 0.041514 | 0.052503 | 0.021978 | 0.019536 | 0.010989 | 0.002442 | 11459.3008 | 55822.6037 | 2273.8569
38938.4117 | 840 | 824 | 38938.4117 | 617 | 565 | 1119.5 | 1226.5 | 51.2821 | 50.3053 | 37.6679 | 34.4933 | 0.51282 | 0.50305 | 0.37668 | 0.34493 | 0.009768 | 0.031746 | 7608.5434 | 112652.2101 | 54.4444
38938.4124 | 1053 | 1104 | 38938.4124 | 1093 | 1170 | 1178.5 | 1285.5 | 64.2857 | 67.3993 | 66.7277 | 71.4286 | 0.64286 | 0.67399 | 0.66728 | 0.71429 | 0.031136 | 0.047009 | 637.9438 | 958.6498 | 3.6074
38938.4131 | 1132 | 1092 | 38938.4131 | 1045 | 1139 | 1237.5 | 1344.5 | 69.1087 | 66.6667 | 63.7973 | 69.536 | 0.69109 | 0.66667 | 0.63797 | 0.69536 | 0.02442 | 0.057387 | 327.1286 | 420.1807 | 8.2093
38938.4137 | 1179 | 1193 | 38938.4137 | 1192 | 1176 | 1296 | 1403 | 71.978 | 72.8327 | 72.7717 | 71.7949 | 0.71978 | 0.72833 | 0.72772 | 0.71795 | 0.008547 | 0.009768 | 8762.3738 | 35712.5776 | 21.6477
38938.4144 | 944 | 917 | 38938.4144 | 966 | 940 | 1355 | 1462 | 57.6313 | 55.9829 | 58.9744 | 57.3871 | 0.57631 | 0.55983 | 0.58974 | 0.57387 | 0.016484 | 0.015873 | 6719.139 | 9550.4519 | 27.1983
38938.4151 | 1020 | 967 | 38938.4151 | 1099 | 1064 | 1413.5 | 1520.5 | 62.2711 | 59.0354 | 67.094 | 64.9573 | 0.62271 | 0.59035 | 0.67094 | 0.64957 | 0.032357 | 0.021368 | 399.316 | 438.1056 | 10.6102
38938.4158 | 1084 | 1034 | 38938.4158 | 943 | 942 | 1472.5 | 1579.5 | 66.1783 | 63.1258 | 57.5702 | 57.5092 | 0.66178 | 0.63126 | 0.5757 | 0.57509 | 0.030525 | 0.0006105 | 400.1357 | 499.1124 | 0.40124
38938.4165 | 967 | 993 | 38938.4165 | 1199 | 1185 | 1531.5 | 1638.5 | 59.0354 | 60.6227 | 73.199 | 72.3443 | 0.59035 | 0.60623 | 0.73199 | 0.72344 | 0.015873 | 0.008547 | 1310.2108 | 1615.465 | 14.5116
38938.4171 | 1186 | 1128 | 38938.4172 | 957 | 875 | 1590 | 1697 | 72.4054 | 68.8645 | 58.4249 | 53.4188 | 0.72405 | 0.68864 | 0.58425 | 0.53419 | 0.035409 | 0.050061 | 332.6687 | 511.1898 | 14.9022
38938.4178 | 1138 | 1103 | 38938.4178 | 1024 | 983 | 1649 | 1756 | 69.475 | 67.3382 | 62.5153 | 60.0122 | 0.69475 | 0.67338 | 0.62515 | 0.60012 | 0.021368 | 0.025031 | 315.6293 | 402.6825 | 9.2947
38938.4185 | 942 | 859 | 38938.4185 | 1176 | 1190 | 1707.5 | 1814.5 | 57.5092 | 52.442 | 71.7949 | 72.6496 | 0.57509 | 0.52442 | 0.71795 | 0.7265 | 0.050672 | 0.008547 | 114.1642 | 91.1181 | 17.3178
38938.4192 | 1076 | 1038 | 38938.4192 | 1091 | 1048 | 1766.5 | 1873.5 | 65.6899 | 63.37 | 66.6056 | 63.9805 | 0.6569 | 0.6337 | 0.66606 | 0.6398 | 0.023199 | 0.026252 | 482.4506 | 586.6116 | 0.080662
38938.4199 | 1188 | 868 | 38938.4199 | 1042 | 986 | 1825.5 | 1932.5 | 72.5275 | 52.9915 | 63.6142 | 60.1954 | 0.72527 | 0.52991 | 0.63614 | 0.60195 | 0.19536 | 0.034188 | 45.8546 | 51.1404 | 2.2228
38938.4205 | 1080 | 1017 | 38938.4206 | 1052 | 988 | 1884 | 1991 | 65.9341 | 62.0879 | 64.2247 | 60.3175 | 0.65934 | 0.62088 | 0.64225 | 0.60317 | 0.038462 | 0.039072 | 5196.2056 | 2358.5494 | 1.5112

## C4-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 7
Time-35 | N11 | N12 | Time-36 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38938.398 | 1 | 0 | 38938.3981 | 1 | 0 | -59 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3987 | 1 | 0 | 38938.3988 | 1 | 0 | -1.3318e-07 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3994 | 1 | 0 | 38938.3994 | 1 | 0 | 58.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4001 | 1 | 0 | 38938.4001 | 1 | 0 | 117.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4008 | 1 | 0 | 38938.4008 | 1 | 0 | 176.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4014 | 1 | 0 | 38938.4015 | 1 | 0 | 235 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4021 | 1 | 0 | 38938.4022 | 1 | 0 | 294 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4028 | 1 | 0 | 38938.4028 | 1 | 0 | 352.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4035 | 1 | 0 | 38938.4035 | 1 | 0 | 411.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4042 | 1 | 0 | 38938.4042 | 1 | 0 | 470.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4048 | 1 | 0 | 38938.4049 | 1 | 0 | 529 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4055 | 2 | 2 | 38938.4056 | 1 | 0 | 588 | 695 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 222925823.02 | 211202 | 105401.0947
38938.4062 | 1192 | 1190 | 38938.4062 | 1141 | 1117 | 646.5 | 753.5 | 72.7717 | 72.6496 | 69.6581 | 68.1929 | 0.72772 | 0.7265 | 0.69658 | 0.68193 | 0.001221 | 0.014652 | 1630.526 | 2184.0446 | 21.6137
38938.4069 | 1019 | 1054 | 38938.4069 | 1058 | 1021 | 705.5 | 812.5 | 62.21 | 64.3468 | 64.591 | 62.3321 | 0.6221 | 0.64347 | 0.64591 | 0.62332 | 0.021368 | 0.022589 | 3767.745 | 17674.0833 | 3.7756
38938.4076 | 1185 | 897 | 38938.4076 | 1171 | 1147 | 764 | 871 | 72.3443 | 54.7619 | 71.4896 | 70.0244 | 0.72344 | 0.54762 | 0.7149 | 0.70024 | 0.17582 | 0.014652 | 61.9143 | 74.0784 | 1.4716
38938.4083 | 966 | 929 | 38938.4083 | 1198 | 930 | 823 | 930 | 58.9744 | 56.7155 | 73.138 | 56.7766 | 0.58974 | 0.56716 | 0.73138 | 0.56777 | 0.022589 | 0.16361 | 86.2679 | 71.8705 | 9.8136
38938.4089 | 1034 | 1008 | 38938.4089 | 936 | 910 | 881.5 | 988.5 | 63.1258 | 61.5385 | 57.1429 | 55.5556 | 0.63126 | 0.61538 | 0.57143 | 0.55556 | 0.015873 | 0.015873 | 8027 | 8027 | 6.9589
38938.4096 | 929 | 962 | 38938.4096 | 968 | 1006 | 940.5 | 1047.5 | 56.7155 | 58.7302 | 59.0965 | 61.4164 | 0.56716 | 0.5873 | 0.59096 | 0.61416 | 0.020147 | 0.023199 | 31549.7439 | 3289.2113 | 22.398
38938.4103 | 1051 | 1146 | 38938.4103 | 967 | 941 | 999.5 | 1106.5 | 64.1636 | 69.9634 | 59.0354 | 57.4481 | 0.64164 | 0.69963 | 0.59035 | 0.57448 | 0.057998 | 0.015873 | 175.414 | 224.5137 | 5.0699
38938.411 | 937 | 970 | 38938.411 | 1185 | 1132 | 1058 | 1165 | 57.2039 | 59.2186 | 72.3443 | 69.1087 | 0.57204 | 0.59219 | 0.72344 | 0.69109 | 0.020147 | 0.032357 | 32.0895 | 26.7085 | 4.4769
38938.4117 | 478 | 434 |  | 303 | 408 | 1116 | 1223 | 29.1819 | 26.4957 | 18.4982 | 24.9084 | 0.29182 | 0.26496 | 0.18498 | 0.24908 | 0.026862 | 0.064103 | 8166.3488 | 1809.9496 | 262.2437
38938.4123 | 441 | 380 | 38938.4123 | 266 | 354 | 1175.5 | 1282.5 | 26.9231 | 23.199 | 16.2393 | 21.6117 | 0.26923 | 0.23199 | 0.16239 | 0.21612 | 0.037241 | 0.053724 | 3728.1342 | 2352.7528 | 326.1431
38938.413 | 988 | 931 | 38938.413 | 945 | 878 | 1234.5 | 1341.5 | 60.3175 | 56.8376 | 57.6923 | 53.602 | 0.60317 | 0.56838 | 0.57692 | 0.53602 | 0.034799 | 0.040904 | 11824.0787 | 1960.6048 | 19.8286
38938.4137 | 1191 | 1176 | 38938.4137 | 1023 | 1070 | 1293.5 | 1400.5 | 72.7106 | 71.7949 | 62.4542 | 65.3236 | 0.72711 | 0.71795 | 0.62454 | 0.65324 | 0.0091575 | 0.028694 | 650.7932 | 928.3501 | 19.4968
38938.4144 | 1098 | 1155 | 38938.4144 | 1185 | 1147 | 1352 | 1459 | 67.033 | 70.5128 | 72.3443 | 70.0244 | 0.67033 | 0.70513 | 0.72344 | 0.70024 | 0.034799 | 0.023199 | 4250.2519 | 3487.4671 | 11.7817
38938.4151 | 1198 | 1176 | 38938.4151 | 1051 | 1009 | 1411 | 1518 | 73.138 | 71.7949 | 64.1636 | 61.5995 | 0.73138 | 0.71795 | 0.64164 | 0.616 | 0.013431 | 0.025641 | 825.3346 | 1323.3326 | 20.633
38938.4157 | 996 | 1037 |  | 859 | 880 | 1469 | 1576 | 60.8059 | 63.3089 | 52.442 | 53.7241 | 0.60806 | 0.63309 | 0.52442 | 0.53724 | 0.025031 | 0.012821 | 1647.238 | 3867.715 | 7.522
38938.4164 | 1177 | 1155 | 38938.4164 | 1000 | 1113 | 1528.5 | 1635.5 | 71.8559 | 70.5128 | 61.0501 | 67.9487 | 0.71856 | 0.70513 | 0.6105 | 0.67949 | 0.013431 | 0.068987 | 229.8494 | 299.8194 | 14.2173
38938.4171 | 1087 | 1124 | 38938.4171 | 1097 | 1039 | 1587.5 | 1694.5 | 66.3614 | 68.6203 | 66.9719 | 63.431 | 0.66361 | 0.6862 | 0.66972 | 0.63431 | 0.022589 | 0.035409 | 454.2845 | 595.1686 | 7.4631
38938.4178 | 1100 | 1148 | 38938.4178 | 1158 | 1194 | 1646 | 1753 | 67.1551 | 70.0855 | 70.696 | 72.8938 | 0.67155 | 0.70085 | 0.70696 | 0.72894 | 0.029304 | 0.021978 | 8935.5465 | 3131.2194 | 11.394
38938.4185 | 928 | 902 | 38938.4185 | 961 | 878 | 1704.5 | 1811.5 | 56.6545 | 55.0672 | 58.6691 | 53.602 | 0.56654 | 0.55067 | 0.58669 | 0.53602 | 0.015873 | 0.050672 | 1276.2555 | 1349.2629 | 29.2119
38938.4191 | 1164 | 1128 | 38938.4192 | 934 | 880 | 1763.5 | 1870.5 | 71.0623 | 68.8645 | 57.0208 | 53.7241 | 0.71062 | 0.68864 | 0.57021 | 0.53724 | 0.021978 | 0.032967 | 683.7691 | 1097.3568 | 14.5419
38938.4198 | 961 | 891 | 38938.4198 | 936 | 926 | 1822.5 | 1929.5 | 58.6691 | 54.3956 | 57.1429 | 56.5324 | 0.58669 | 0.54396 | 0.57143 | 0.56532 | 0.042735 | 0.006105 | 722.4748 | 996.0348 | 26.6223
38938.4205 | 1003 | 1110 | 38938.4205 | 948 | 932 | 1881.5 | 1988.5 | 61.2332 | 67.7656 | 57.8755 | 56.8987 | 0.61233 | 0.67766 | 0.57875 | 0.56899 | 0.065324 | 0.009768 | 241.9854 | 315.5977 | 0.0013683

## C4-6
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 6
Time-33 | N11 | N12 | Time-34 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38938.398 | 1 | 0 | 38938.398 | 1 | 0 | -61.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3987 | 1 | 0 | 38938.3987 | 1 | 0 | -3 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3994 | 1 | 0 | 38938.3994 | 1 | 0 | 56 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4001 | 1 | 0 | 38938.4001 | 1 | 0 | 114.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4007 | 1 | 0 | 38938.4008 | 1 | 0 | 173.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4014 | 1 | 0 | 38938.4014 | 1 | 0 | 232.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4021 | 1 | 0 | 38938.4021 | 1 | 0 | 291 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4028 | 1 | 0 | 38938.4028 | 1 | 0 | 349.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4035 | 1 | 0 | 38938.4035 | 1 | 0 | 408.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4041 | 1 | 0 | 38938.4042 | 1 | 0 | 467.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4048 | 1 | 0 | 38938.4048 | 1 | 0 | 526.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4055 | 1 | 0 | 38938.4055 | 1076 | 1131 | 585 | 692 | 0.06105 | 0 | 65.6899 | 69.0476 | 0.0006105 | 0 | 0.6569 | 0.69048 | 0.0006105 | 0.033578 | 211202 | 3741.8545 | 211201.9994
38938.4062 | 1009 | 980 | 38938.4062 | 994 | 962 | 644 | 751 | 61.5995 | 59.8291 | 60.6838 | 58.7302 | 0.616 | 0.59829 | 0.60684 | 0.5873 | 0.017705 | 0.019536 | 26810.7203 | 3938.5633 | 12.3417
38938.4069 | 1051 | 1145 | 38938.4069 | 996 | 948 | 702.5 | 809.5 | 64.1636 | 69.9023 | 60.8059 | 57.8755 | 0.64164 | 0.69902 | 0.60806 | 0.57875 | 0.057387 | 0.029304 | 201.5144 | 264.4224 | 5.2585
38938.4075 | 1048 | 1006 | 38938.4076 | 1181 | 1156 | 761.5 | 868.5 | 63.9805 | 61.4164 | 72.1001 | 70.5739 | 0.6398 | 0.61416 | 0.721 | 0.70574 | 0.025641 | 0.015263 | 1216.9918 | 2210.3817 | 5.6129
38938.4082 | 1149 | 1122 | 38938.4082 | 1196 | 1178 | 820.5 | 927.5 | 70.1465 | 68.4982 | 73.0159 | 71.917 | 0.70147 | 0.68498 | 0.73016 | 0.71917 | 0.016484 | 0.010989 | 9591.0276 | 6619.9647 | 13.8707
38938.4089 | 950 | 921 | 38938.4089 | 1192 | 1085 | 879 | 986 | 57.9976 | 56.2271 | 72.7717 | 66.2393 | 0.57998 | 0.56227 | 0.72772 | 0.66239 | 0.017705 | 0.065324 | 100.0588 | 81.2645 | 11.7809
38938.4096 | 1043 | 1016 | 38938.4096 | 1194 | 1190 | 937.5 | 1044.5 | 63.6752 | 62.0269 | 72.8938 | 72.6496 | 0.63675 | 0.62027 | 0.72894 | 0.7265 | 0.016484 | 0.002442 | 1087.5914 | 1423.2807 | 4.9679
38938.4103 | 1073 | 1048 | 38938.4103 | 1197 | 983 | 996.5 | 1103.5 | 65.5067 | 63.9805 | 73.0769 | 60.0122 | 0.65507 | 0.6398 | 0.73077 | 0.60012 | 0.015263 | 0.13065 | 38.4885 | 39.146 | 0.21422
38938.4109 | 936 | 970 | 38938.411 | 1188 | 912 | 1055.5 | 1162.5 | 57.1429 | 59.2186 | 72.5275 | 55.6777 | 0.57143 | 0.59219 | 0.72527 | 0.55678 | 0.020757 | 0.1685 | 86.3959 | 73.0226 | 9.0073
38938.4116 | 1176 | 1156 | 38938.4116 | 945 | 917 | 1114 | 1221 | 71.7949 | 70.5739 | 57.6923 | 55.9829 | 0.71795 | 0.70574 | 0.57692 | 0.55983 | 0.01221 | 0.017094 | 381.9675 | 513.0616 | 15.853
38938.4123 | 1091 | 1066 | 38938.4123 | 1146 | 1123 | 1173 | 1280 | 66.6056 | 65.0794 | 69.9634 | 68.5592 | 0.66606 | 0.65079 | 0.69963 | 0.68559 | 0.015263 | 0.014042 | 60964.7356 | 4570.4803 | 4.0374
38938.413 | 986 | 931 | 38938.413 | 1152 | 1117 | 1231.5 | 1338.5 | 60.1954 | 56.8376 | 70.3297 | 68.1929 | 0.60195 | 0.56838 | 0.7033 | 0.68193 | 0.033578 | 0.021368 | 212.9226 | 196.2853 | 13.9485
38938.4137 | 999 | 1036 | 38938.4137 | 963 | 946 | 1290.5 | 1397.5 | 60.989 | 63.2479 | 58.7912 | 57.7534 | 0.60989 | 0.63248 | 0.58791 | 0.57753 | 0.022589 | 0.010379 | 1207.3155 | 1874.3504 | 7.1495
38938.4144 | 1144 | 1120 | 38938.4144 | 1053 | 1151 | 1349.5 | 1456.5 | 69.8413 | 68.3761 | 64.2857 | 70.2686 | 0.69841 | 0.68376 | 0.64286 | 0.70269 | 0.014652 | 0.059829 | 310.651 | 388.9807 | 10.7235
38938.415 | 1198 | 1195 | 38938.415 | 1106 | 904 | 1408 | 1515 | 73.138 | 72.9548 | 67.5214 | 55.1893 | 0.73138 | 0.72955 | 0.67521 | 0.55189 | 0.0018315 | 0.12332 | 66.6348 | 87.2144 | 10.9146
38938.4157 | 912 | 980 | 38938.4157 | 1024 | 945 | 1467 | 1574 | 55.6777 | 59.8291 | 62.5153 | 57.6923 | 0.55678 | 0.59829 | 0.62515 | 0.57692 | 0.041514 | 0.04823 | 11341.7176 | 1707.0019 | 21.305
38938.4164 | 1192 | 1172 | 38938.4164 | 949 | 911 | 1525.5 | 1632.5 | 72.7717 | 71.5507 | 57.9365 | 55.6166 | 0.72772 | 0.71551 | 0.57937 | 0.55617 | 0.01221 | 0.023199 | 20.6708 | 26.4222 | 4.4757
38938.4171 | 1199 | 1188 | 38938.4171 | 995 | 916 | 1584.5 | 1691.5 | 73.199 | 72.5275 | 60.7448 | 55.9219 | 0.73199 | 0.72527 | 0.60745 | 0.55922 | 0.0067155 | 0.04823 | 81.3149 | 106.7337 | 11.9067
38938.4178 | 1135 | 1085 | 38938.4178 | 1198 | 1185 | 1643.5 | 1750.5 | 69.2918 | 66.2393 | 73.138 | 72.3443 | 0.69292 | 0.66239 | 0.73138 | 0.72344 | 0.030525 | 0.0079365 | 1234.9654 | 3716.5013 | 9.6016
38938.4184 | 928 | 901 | 38938.4184 | 1195 | 1170 | 1702 | 1809 | 56.6545 | 55.0061 | 72.9548 | 71.4286 | 0.56654 | 0.55006 | 0.72955 | 0.71429 | 0.016484 | 0.015263 | 1490.2261 | 1715.5541 | 29.7865
38938.4191 | 1172 | 1178 | 38938.4191 | 1049 | 993 | 1760.5 | 1867.5 | 71.5507 | 71.917 | 64.0415 | 60.6227 | 0.71551 | 0.71917 | 0.64042 | 0.60623 | 0.003663 | 0.034188 | 282.7777 | 360.4901 | 15.7485
38938.4198 | 1064 | 1091 | 38938.4198 | 971 | 888 | 1819.5 | 1926.5 | 64.9573 | 66.6056 | 59.2796 | 54.2125 | 0.64957 | 0.66606 | 0.5928 | 0.54212 | 0.016484 | 0.050672 | 383.7906 | 442.8994 | 3.1391
38938.4205 | 962 | 890 | 38938.4205 | 938 | 911 | 1878.5 | 1985.5 | 58.7302 | 54.3346 | 57.265 | 55.6166 | 0.5873 | 0.54335 | 0.57265 | 0.55617 | 0.043956 | 0.016484 | 894.2854 | 1569.4336 | 27.5713

## C4-5
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 4 & 5
Time-31 | N11 | N12 | Time-32 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38938.398 | 1 | 0 | 38938.398 | 1 | 0 | -64.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3987 | 1 | 0 | 38938.3987 | 1 | 0 | -5.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3993 | 1 | 0 | 38938.3994 | 1 | 0 | 53 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4 | 1 | 0 | 38938.4 | 1 | 0 | 112 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4007 | 1 | 0 | 38938.4007 | 1 | 0 | 170.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4014 | 1 | 0 | 38938.4014 | 1 | 0 | 229.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4021 | 1 | 0 | 38938.4021 | 1 | 0 | 288.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4027 | 1 | 0 |  | 1 | 0 | 346 | 453 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4034 | 1 | 0 | 38938.4034 | 1 | 0 | 406 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4041 | 1 | 0 | 38938.4041 | 1 | 0 | 464.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4048 | 1 | 0 | 38938.4048 | 1 | 0 | 523.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4055 | 1 | 0 | 38938.4055 | 1 | 0 | 582.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4061 | 964 | 998 | 38938.4062 | 1091 | 1064 | 641 | 748 | 58.8523 | 60.928 | 66.6056 | 64.9573 | 0.58852 | 0.60928 | 0.66606 | 0.64957 | 0.020757 | 0.016484 | 1441.1641 | 2182.4414 | 14.4693
38938.4068 | 1114 | 1076 | 38938.4069 | 1174 | 1190 | 700 | 807 | 68.0098 | 65.6899 | 71.6728 | 72.6496 | 0.6801 | 0.6569 | 0.71673 | 0.7265 | 0.023199 | 0.009768 | 1853.8186 | 6771.6203 | 7.0502
38938.4075 | 4 | 18 | 38938.4075 | 4 | 17 | 758.5 | 865.5 | 0.2442 | 1.0989 | 0.2442 | 1.0379 | 0.002442 | 0.010989 | 0.002442 | 0.010379 | 0.008547 | 0.0079365 | 15183.7254 | 16364.1665 | 11546.2198
38938.4082 | 4 | 17 | 38938.4082 | 3 | 16 | 817.5 | 924.5 | 0.2442 | 1.0379 | 0.18315 | 0.9768 | 0.002442 | 0.010379 | 0.0018315 | 0.009768 | 0.0079365 | 0.0079365 | 16354 | 16354 | 12231.2097
38938.4089 | 3 | 18 | 38938.4089 | 4 | 12 | 876 | 983 | 0.18315 | 1.0989 | 0.2442 | 0.7326 | 0.0018315 | 0.010989 | 0.002442 | 0.007326 | 0.0091575 | 0.004884 | 14130.4372 | 26645.6033 | 11578.8782
38938.4095 | 4 | 17 | 38938.4096 | 3 | 12 | 935 | 1042 | 0.2442 | 1.0379 | 0.18315 | 0.7326 | 0.002442 | 0.010379 | 0.0018315 | 0.007326 | 0.0079365 | 0.0054945 | 16313.4801 | 23637.8637 | 12254.1588
38938.4102 | 4 | 17 | 38938.4102 | 3 | 15 | 993.5 | 1100.5 | 0.2442 | 1.0379 | 0.18315 | 0.91575 | 0.002442 | 0.010379 | 0.0018315 | 0.0091575 | 0.0079365 | 0.007326 | 16343.851 | 17719.0175 | 12236.939
38938.4109 | 3 | 13 | 38938.4109 | 24 | 31 | 1052.5 | 1159.5 | 0.18315 | 0.79365 | 1.4652 | 1.8926 | 0.0018315 | 0.0079365 | 0.014652 | 0.018926 | 0.006105 | 0.0042735 | 21190.5794 | 30480.1404 | 16078.1734
38938.4116 | 1190 | 1194 | 38938.4116 | 945 | 918 | 1111.5 | 1218.5 | 72.6496 | 72.8938 | 57.6923 | 56.044 | 0.7265 | 0.72894 | 0.57692 | 0.56044 | 0.002442 | 0.016484 | 65.2479 | 84.6427 | 10.4038
38938.4123 | 1068 | 1042 | 38938.4123 | 1197 | 1187 | 1170 | 1277 | 65.2015 | 63.6142 | 73.0769 | 72.4664 | 0.65201 | 0.63614 | 0.73077 | 0.72466 | 0.015873 | 0.006105 | 2087.0702 | 4328.834 | 0.28328
38938.413 | 1187 | 1108 | 38938.413 | 1092 | 1054 | 1229 | 1336 | 72.4664 | 67.6435 | 66.6667 | 64.3468 | 0.72466 | 0.67643 | 0.66667 | 0.64347 | 0.04823 | 0.023199 | 576.6773 | 1358.2005 | 15.2979
38938.4136 | 1115 | 1178 | 38938.4136 | 1059 | 1025 | 1287.5 | 1394.5 | 68.0708 | 71.917 | 64.652 | 62.5763 | 0.68071 | 0.71917 | 0.64652 | 0.62576 | 0.038462 | 0.020757 | 590.169 | 1110.1948 | 14.016
38938.4143 | 1179 | 1159 | 38938.4143 | 1131 | 1108 | 1346.5 | 1453.5 | 71.978 | 70.757 | 69.0476 | 67.6435 | 0.71978 | 0.70757 | 0.69048 | 0.67643 | 0.01221 | 0.014042 | 5229.6793 | 54158.5264 | 19.3758
38938.415 | 1192 | 1103 | 38938.415 | 1124 | 1174 | 1405.5 | 1512.5 | 72.7717 | 67.3382 | 68.6203 | 71.6728 | 0.72772 | 0.67338 | 0.6862 | 0.71673 | 0.054335 | 0.030525 | 1168.1847 | 10858.4172 | 16.3481
38938.4157 | 1190 | 1119 | 38938.4157 | 1127 | 1082 | 1464 | 1571 | 72.6496 | 68.315 | 68.8034 | 66.0562 | 0.7265 | 0.68315 | 0.68803 | 0.66056 | 0.043346 | 0.027473 | 1529.7954 | 10493.4181 | 17.3485
38938.4164 | 1024 | 988 | 38938.4164 | 1172 | 900 | 1523 | 1630 | 62.5153 | 60.3175 | 71.5507 | 54.9451 | 0.62515 | 0.60317 | 0.71551 | 0.54945 | 0.021978 | 0.16606 | 57.7323 | 53.3959 | 3.5591
38938.417 | 1035 | 987 | 38938.417 | 952 | 889 | 1581.5 | 1688.5 | 63.1868 | 60.2564 | 58.1197 | 54.2735 | 0.63187 | 0.60256 | 0.5812 | 0.54274 | 0.029304 | 0.038462 | 5799.0927 | 3355.9397 | 8.955
38938.4177 | 1166 | 1127 | 38938.4177 | 1060 | 1005 | 1640.5 | 1747.5 | 71.1844 | 68.8034 | 64.7131 | 61.3553 | 0.71184 | 0.68803 | 0.64713 | 0.61355 | 0.02381 | 0.033578 | 647.3327 | 1050.3681 | 14.5816
38938.4184 | 975 | 896 | 38938.4184 | 941 | 849 | 1699.5 | 1806.5 | 59.5238 | 54.7009 | 57.4481 | 51.8315 | 0.59524 | 0.54701 | 0.57448 | 0.51832 | 0.04823 | 0.056166 | 5641.8773 | 1523.0569 | 25.3469
38938.4191 | 1192 | 1164 | 38938.4191 | 1095 | 1041 | 1758 | 1865 | 72.7717 | 71.0623 | 66.8498 | 63.5531 | 0.72772 | 0.71062 | 0.6685 | 0.63553 | 0.017094 | 0.032967 | 797.9497 | 1331.4526 | 19.4163
38938.4198 | 1059 | 1081 | 38938.4198 | 925 | 907 | 1817 | 1924 | 64.652 | 65.9951 | 56.4713 | 55.3724 | 0.64652 | 0.65995 | 0.56471 | 0.55372 | 0.013431 | 0.010989 | 4068.7622 | 27681.2111 | 2.4869
38938.4204 | 1073 | 1163 | 38938.4205 | 983 | 905 | 1875.5 | 1982.5 | 65.5067 | 71.0012 | 60.0122 | 55.2503 | 0.65507 | 0.71001 | 0.60012 | 0.5525 | 0.054945 | 0.047619 | 1116.9515 | 37367.0687 | 10.5462

## C3-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 7
Time-29 | N11 | N12 | Time-30 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38938.398 | 1 | 0 | 38938.398 | 1 | 0 | -67.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3986 | 1 | 0 | 38938.3986 | 1 | 0 | -8.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3993 | 1 | 0 | 38938.3993 | 1 | 0 | 50.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4 | 1 | 0 | 38938.4 | 1 | 0 | 109 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4007 | 1 | 0 | 38938.4007 | 1 | 0 | 168 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4014 | 2 | 0 | 38938.4014 | 1 | 0 | 226.5 | 333.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38938.402 | 1 | 0 | 38938.402 | 1 | 0 | 285.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4027 | 1 | 0 | 38938.4027 | 1 | 0 | 344.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4034 | 1 | 0 | 38938.4034 | 1 | 0 | 403 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4041 | 1 | 0 | 38938.4041 | 1 | 0 | 462 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4048 | 1 | 0 | 38938.4048 | 1 | 0 | 520.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4054 | 1 | 1 | 38938.4055 | 1 | 0 | 579.5 | 686.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38938.4061 | 1187 | 1170 | 38938.4061 | 1069 | 1042 | 638.5 | 745.5 | 72.4664 | 71.4286 | 65.2625 | 63.6142 | 0.72466 | 0.71429 | 0.65263 | 0.63614 | 0.010379 | 0.016484 | 1823.1672 | 3462.3752 | 20.2676
38938.4068 | 1143 | 1109 | 38938.4068 | 1118 | 1178 | 697 | 804 | 69.7802 | 67.7045 | 68.254 | 71.917 | 0.6978 | 0.67705 | 0.68254 | 0.71917 | 0.020757 | 0.03663 | 1043.1666 | 1880.0426 | 11.8991
38938.4075 | 1170 | 1171 | 38938.4075 | 1122 | 1175 | 755.5 | 862.5 | 71.4286 | 71.4896 | 68.4982 | 71.7338 | 0.71429 | 0.7149 | 0.68498 | 0.71734 | 0.0006105 | 0.032357 | 722.71 | 904.3598 | 17.5304
38938.4082 | 1197 | 1178 | 38938.4082 | 965 | 937 | 814.5 | 921.5 | 73.0769 | 71.917 | 58.9133 | 57.2039 | 0.73077 | 0.71917 | 0.58913 | 0.57204 | 0.0116 | 0.017094 | 467.047 | 665.0477 | 19.3325
38938.4088 | 1065 | 1041 | 38938.4089 | 1038 | 1011 | 873.5 | 980.5 | 65.0183 | 63.5531 | 63.37 | 61.7216 | 0.65018 | 0.63553 | 0.6337 | 0.61722 | 0.014652 | 0.016484 | 3216.5973 | 12130.5554 | 0.66884
38938.4095 | 1016 | 991 | 38938.4095 | 1156 | 1134 | 932 | 1039 | 62.0269 | 60.5006 | 70.5739 | 69.2308 | 0.62027 | 0.60501 | 0.70574 | 0.69231 | 0.015263 | 0.013431 | 3481.23 | 15217.0659 | 10.6284
38938.4102 | 1013 | 1057 | 38938.4102 | 968 | 943 | 991 | 1098 | 61.8437 | 64.5299 | 59.0965 | 57.5702 | 0.61844 | 0.6453 | 0.59096 | 0.5757 | 0.026862 | 0.015263 | 1096.9912 | 1878.2396 | 3.8643
38938.4109 | 1149 | 1126 | 38938.4109 | 1044 | 1017 | 1049.5 | 1156.5 | 70.1465 | 68.7424 | 63.7363 | 62.0879 | 0.70147 | 0.68742 | 0.63736 | 0.62088 | 0.014042 | 0.016484 | 1970.669 | 4344.402 | 14.0618
38938.4116 | 1069 | 1157 | 38938.4116 | 1130 | 1107 | 1108.5 | 1215.5 | 65.2625 | 70.6349 | 68.9866 | 67.5824 | 0.65263 | 0.70635 | 0.68987 | 0.67582 | 0.053724 | 0.014042 | 424.9227 | 733.6882 | 8.5936
38938.4122 | 641 | 549 | 38938.4123 | 375 | 436 | 1167.5 | 1274.5 | 39.1331 | 33.5165 | 22.8938 | 26.6178 | 0.39133 | 0.33516 | 0.22894 | 0.26618 | 0.056166 | 0.037241 | 1834.5522 | 4667.8326 | 164.6012
38938.4129 | 947 | 944 | 38938.4129 | 1067 | 1119 | 1226 | 1333 | 57.8144 | 57.6313 | 65.1404 | 68.315 | 0.57814 | 0.57631 | 0.6514 | 0.68315 | 0.0018315 | 0.031746 | 355.483 | 290.4526 | 17.4955
38938.4136 | 991 | 950 | 38938.4136 | 1055 | 1015 | 1285 | 1392 | 60.5006 | 57.9976 | 64.4078 | 61.9658 | 0.60501 | 0.57998 | 0.64408 | 0.61966 | 0.025031 | 0.02442 | 4143.4664 | 6824.3493 | 17.8459
38938.4143 | 1200 | 1191 | 38938.4143 | 937 | 971 | 1343.5 | 1450.5 | 73.2601 | 72.7106 | 57.2039 | 59.2796 | 0.7326 | 0.72711 | 0.57204 | 0.5928 | 0.0054945 | 0.020757 | 276.6022 | 370.9308 | 18.3839
38938.415 | 1049 | 914 | 38938.415 | 952 | 904 | 1402.5 | 1509.5 | 64.0415 | 55.7998 | 58.1197 | 55.1893 | 0.64042 | 0.558 | 0.5812 | 0.55189 | 0.082418 | 0.029304 | 362.4595 | 576.4542 | 13.9872
38938.4156 | 970 | 877 | 38938.4157 | 954 | 945 | 1461.5 | 1568.5 | 59.2186 | 53.5409 | 58.2418 | 57.6923 | 0.59219 | 0.53541 | 0.58242 | 0.57692 | 0.056777 | 0.0054945 | 496.5351 | 639.2165 | 26.2296
38938.4163 | 1198 | 1193 | 38938.4163 | 1123 | 911 | 1520 | 1627 | 73.138 | 72.8327 | 68.5592 | 55.6166 | 0.73138 | 0.72833 | 0.68559 | 0.55617 | 0.0030525 | 0.12943 | 72.9677 | 95.5158 | 11.3833
38938.417 | 990 | 999 | 38938.417 | 986 | 916 | 1579 | 1686 | 60.4396 | 60.989 | 60.1954 | 55.9219 | 0.6044 | 0.60989 | 0.60195 | 0.55922 | 0.0054945 | 0.042735 | 586.3868 | 547.3516 | 10.4967
38938.4177 | 1183 | 1193 | 38938.4177 | 994 | 1004 | 1637.5 | 1744.5 | 72.2222 | 72.8327 | 60.6838 | 61.2943 | 0.72222 | 0.72833 | 0.60684 | 0.61294 | 0.006105 | 0.006105 | 21230.2 | 21230.2 | 21.9402
38938.4184 | 1194 | 1166 | 38938.4184 | 1198 | 918 | 1696.5 | 1803.5 | 72.8938 | 71.1844 | 73.138 | 56.044 | 0.72894 | 0.71184 | 0.73138 | 0.56044 | 0.017094 | 0.17094 | 76.2703 | 99.0695 | 10.5414
38938.4191 | 1141 | 1098 |  | 1115 | 938 | 1755 | 1862 | 69.6581 | 67.033 | 68.0708 | 57.265 | 0.69658 | 0.67033 | 0.68071 | 0.57265 | 0.026252 | 0.10806 | 39.5088 | 45.4233 | 3.5838
38938.4197 | 1197 | 1183 | 38938.4197 | 1031 | 957 | 1814 | 1921 | 73.0769 | 72.2222 | 62.9426 | 58.4249 | 0.73077 | 0.72222 | 0.62943 | 0.58425 | 0.008547 | 0.045177 | 194.7393 | 259.2123 | 16.2854
38938.4204 | 1203 | 1178 | 38938.4204 | 1035 | 893 | 1873 | 1980 | 73.4432 | 71.917 | 63.1868 | 54.5177 | 0.73443 | 0.71917 | 0.63187 | 0.54518 | 0.015263 | 0.086691 | 50.5498 | 66.357 | 9.0741

## C3-6
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 6
Time-27 | N11 | N12 | Time-28 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38938.3979 | 1 | 0 | 38938.3979 | 1 | 0 | -70 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3986 | 1 | 0 | 38938.3986 | 1 | 0 | -11.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3993 | 1 | 0 | 38938.3993 | 1 | 0 | 47.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4 | 1 | 0 | 38938.4 | 1 | 0 | 106.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4006 | 1 | 0 | 38938.4007 | 1 | 0 | 165 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4013 | 1 | 0 | 38938.4013 | 1 | 0 | 224 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.402 | 1 | 0 | 38938.402 | 1 | 0 | 282.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4027 | 1 | 0 | 38938.4027 | 1 | 0 | 341.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4034 | 1 | 0 | 38938.4034 | 1 | 0 | 400.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.404 | 1 | 0 | 38938.4041 | 1 | 0 | 459 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4047 | 1 | 0 | 38938.4047 | 1 | 0 | 518 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4054 | 1 | 0 | 38938.4054 | 1 | 0 | 576.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4061 | 1186 | 1166 | 38938.4061 | 1156 | 1194 | 635.5 | 742.5 | 72.4054 | 71.1844 | 70.5739 | 72.8938 | 0.72405 | 0.71184 | 0.70574 | 0.72894 | 0.01221 | 0.023199 | 2006.6567 | 4450.8505 | 20.0453
38938.4068 | 1164 | 1136 | 38938.4068 | 1074 | 1033 | 694 | 801 | 71.0623 | 69.3529 | 65.5678 | 63.0647 | 0.71062 | 0.69353 | 0.65568 | 0.63065 | 0.017094 | 0.025031 | 1072.0844 | 1877.034 | 15.627
38938.4074 | 1048 | 1020 | 38938.4075 | 1195 | 1187 | 753 | 860 | 63.9805 | 62.2711 | 72.9548 | 72.4664 | 0.6398 | 0.62271 | 0.72955 | 0.72466 | 0.017094 | 0.004884 | 1328.2199 | 1954.6217 | 4.1989
38938.4081 | 980 | 1013 | 38938.4081 | 1134 | 1187 | 812 | 919 | 59.8291 | 61.8437 | 69.2308 | 72.4664 | 0.59829 | 0.61844 | 0.69231 | 0.72466 | 0.020147 | 0.032357 | 435.8088 | 446.2929 | 9.6792
38938.4088 | 1110 | 1085 | 38938.4088 | 1061 | 1035 | 870.5 | 977.5 | 67.7656 | 66.2393 | 64.7741 | 63.1868 | 0.67766 | 0.66239 | 0.64774 | 0.63187 | 0.015263 | 0.015873 | 3549.5103 | 33302.8202 | 7.5331
38938.4095 | 1152 | 1195 | 38938.4095 | 1158 | 1193 | 929.5 | 1036.5 | 70.3297 | 72.9548 | 70.696 | 72.8327 | 0.7033 | 0.72955 | 0.70696 | 0.72833 | 0.026252 | 0.021368 | 66896.9728 | 2875.1234 | 18.9218
38938.4102 | 961 | 995 | 38938.4102 | 1147 | 1125 | 988 | 1095 | 58.6691 | 60.7448 | 70.0244 | 68.6813 | 0.58669 | 0.60745 | 0.70024 | 0.68681 | 0.020757 | 0.013431 | 59.3412 | 52.1666 | 5.4101
38938.4108 | 933 | 1041 | 38938.4109 | 1191 | 1195 | 1047 | 1154 | 56.9597 | 63.5531 | 72.7106 | 72.9548 | 0.5696 | 0.63553 | 0.72711 | 0.72955 | 0.065934 | 0.002442 | 163.4904 | 169.6083 | 8.4012
38938.4115 | 971 | 1093 | 38938.4115 | 1198 | 1186 | 1105.5 | 1212.5 | 59.2796 | 66.7277 | 73.138 | 72.4054 | 0.5928 | 0.66728 | 0.73138 | 0.72405 | 0.074481 | 0.007326 | 255.1116 | 335.6312 | 3.4554
38938.4122 | 955 | 992 | 38938.4122 | 1061 | 1036 | 1164.5 | 1271.5 | 58.3028 | 60.5617 | 64.7741 | 63.2479 | 0.58303 | 0.60562 | 0.64774 | 0.63248 | 0.022589 | 0.015263 | 1349.0386 | 2031.1059 | 15.9506
38938.4129 | 1172 | 1193 | 38938.4129 | 937 | 971 | 1223.5 | 1330.5 | 71.5507 | 72.8327 | 57.2039 | 59.2796 | 0.71551 | 0.72833 | 0.57204 | 0.5928 | 0.012821 | 0.020757 | 326.1441 | 445.9332 | 17.2527
38938.4136 | 936 | 887 | 38938.4136 | 1064 | 1025 | 1282 | 1389 | 57.1429 | 54.1514 | 64.9573 | 62.5763 | 0.57143 | 0.54151 | 0.64957 | 0.62576 | 0.029915 | 0.02381 | 1936.7179 | 7533.579 | 32.2684
38938.4142 | 976 | 1097 | 38938.4143 | 931 | 935 | 1341 | 1448 | 59.5849 | 66.9719 | 56.8376 | 57.0818 | 0.59585 | 0.66972 | 0.56838 | 0.57082 | 0.073871 | 0.002442 | 229.5828 | 293.1158 | 2.7201
38938.4149 | 1174 | 1148 | 38938.4149 | 1011 | 966 | 1399.5 | 1506.5 | 71.6728 | 70.0855 | 61.7216 | 58.9744 | 0.71673 | 0.70085 | 0.61722 | 0.58974 | 0.015873 | 0.027473 | 322.2829 | 432.6115 | 14.786
38938.4156 | 1072 | 1004 | 38938.4156 | 1168 | 1193 | 1458.5 | 1565.5 | 65.4457 | 61.2943 | 71.3065 | 72.8327 | 0.65446 | 0.61294 | 0.71306 | 0.72833 | 0.041514 | 0.015263 | 546.4245 | 819.4924 | 3.2862
38938.4163 | 1017 | 980 | 38938.4163 | 1173 | 1149 | 1517.5 | 1624.5 | 62.0879 | 59.8291 | 71.6117 | 70.1465 | 0.62088 | 0.59829 | 0.71612 | 0.70147 | 0.022589 | 0.014652 | 850.2042 | 1066.2307 | 10.8236
38938.417 | 1010 | 1118 | 38938.417 | 1077 | 1127 | 1576 | 1683 | 61.6606 | 68.254 | 65.7509 | 68.8034 | 0.61661 | 0.68254 | 0.65751 | 0.68803 | 0.065934 | 0.030525 | 209.3854 | 266.96 | 0.97476
38938.4177 | 1161 | 1127 | 38938.4177 | 1064 | 1010 | 1635 | 1742 | 70.8791 | 68.8034 | 64.9573 | 61.6606 | 0.70879 | 0.68803 | 0.64957 | 0.61661 | 0.020757 | 0.032967 | 554.0876 | 817.7475 | 13.8344
38938.4183 | 1187 | 1150 | 38938.4183 | 1131 | 1187 | 1693.5 | 1800.5 | 72.4664 | 70.2076 | 69.0476 | 72.4664 | 0.72466 | 0.70208 | 0.69048 | 0.72466 | 0.022589 | 0.034188 | 1623.6437 | 5740.4 | 19.143
38938.419 | 1157 | 1111 | 38938.419 | 1090 | 1032 | 1752.5 | 1859.5 | 70.6349 | 67.8266 | 66.5446 | 63.0037 | 0.70635 | 0.67827 | 0.66545 | 0.63004 | 0.028083 | 0.035409 | 969.697 | 2112.5867 | 13.3191
38938.4197 | 1181 | 1191 | 38938.4197 | 937 | 927 | 1811.5 | 1918.5 | 72.1001 | 72.7106 | 57.2039 | 56.5934 | 0.721 | 0.72711 | 0.57204 | 0.56593 | 0.006105 | 0.006105 | 5328.9984 | 15902.0709 | 21.6089
38938.4204 | 1189 | 1204 | 38938.4204 | 1116 | 1064 | 1870 | 1977 | 72.5885 | 73.5043 | 68.1319 | 64.9573 | 0.72589 | 0.73504 | 0.68132 | 0.64957 | 0.0091575 | 0.031746 | 755.0245 | 1121.2226 | 21.35

## C3-5
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 5
Time-25 | N11 | N12 | Time-26 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38938.3979 | 1 | 0 |  | 1 | 0 | -74 | 33 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3986 | 1 | 0 | 38938.3986 | 1 | 0 | -14 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3992 | 1 | 0 | 38938.3993 | 1 | 0 | 44.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3999 | 1 | 0 | 38938.3999 | 1 | 0 | 103.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4006 | 1 | 0 | 38938.4006 | 1 | 0 | 162.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4013 | 1 | 0 | 38938.4013 | 1 | 0 | 221 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.402 | 1 | 0 | 38938.402 | 1 | 0 | 280 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4027 | 1 | 0 | 38938.4027 | 1 | 0 | 338.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4033 | 1 | 0 | 38938.4033 | 1 | 0 | 397.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.404 | 1 | 0 | 38938.404 | 1 | 0 | 456.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4047 | 1 | 0 | 38938.4047 | 1 | 0 | 515 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4054 | 1 | 0 | 38938.4054 | 1 | 0 | 574 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4061 | 997 | 1038 | 38938.4061 | 1118 | 1092 | 632.5 | 739.5 | 60.8669 | 63.37 | 68.254 | 66.6667 | 0.60867 | 0.6337 | 0.68254 | 0.66667 | 0.025031 | 0.015873 | 166.8169 | 165.2843 | 4.683
38938.4067 | 1001 | 949 | 38938.4067 | 1036 | 991 | 691.5 | 798.5 | 61.1111 | 57.9365 | 63.2479 | 60.5006 | 0.61111 | 0.57937 | 0.63248 | 0.60501 | 0.031746 | 0.027473 | 1933.8948 | 17249.5997 | 17.0791
38938.4074 | 3 | 16 | 38938.4074 | 4 | 17 | 750.5 | 857.5 | 0.18315 | 0.9768 | 0.2442 | 1.0379 | 0.0018315 | 0.009768 | 0.002442 | 0.010379 | 0.0079365 | 0.0079365 | 16354 | 16354 | 13008.0843
38938.4081 | 4 | 17 | 38938.4081 | 3 | 17 | 809 | 916 | 0.2442 | 1.0379 | 0.18315 | 1.0379 | 0.002442 | 0.010379 | 0.0018315 | 0.010379 | 0.0079365 | 0.008547 | 16364.1616 | 15184.2445 | 12225.4857
38938.4088 | 4 | 17 | 38938.4088 | 3 | 16 | 867.5 | 974.5 | 0.2442 | 1.0379 | 0.18315 | 0.9768 | 0.002442 | 0.010379 | 0.0018315 | 0.009768 | 0.0079365 | 0.0079365 | 16354 | 16354 | 12231.2097
38938.4095 | 4 | 16 | 38938.4095 | 3 | 17 | 926.5 | 1033.5 | 0.2442 | 0.9768 | 0.18315 | 1.0379 | 0.002442 | 0.009768 | 0.0018315 | 0.010379 | 0.007326 | 0.008547 | 17730.9524 | 15175.4992 | 12995.7387
38938.4101 | 3 | 16 | 38938.4102 | 3 | 12 | 985.5 | 1092.5 | 0.18315 | 0.9768 | 0.18315 | 0.7326 | 0.0018315 | 0.009768 | 0.0018315 | 0.007326 | 0.0079365 | 0.0054945 | 16315.8762 | 23637.835 | 13032.491
38938.4108 | 3 | 17 | 38938.4108 | 3 | 17 | 1044 | 1151 | 0.18315 | 1.0379 | 0.18315 | 1.0379 | 0.0018315 | 0.010379 | 0.0018315 | 0.010379 | 0.008547 | 0.008547 | 15193 | 15193 | 12231.3757
38938.4115 | 940 | 913 |  | 969 | 872 | 1102 | 1209 | 57.3871 | 55.7387 | 59.1575 | 53.2357 | 0.57387 | 0.55739 | 0.59158 | 0.53236 | 0.016484 | 0.059219 | 946.4176 | 941.7889 | 25.746
38938.4122 | 1003 | 1047 | 38938.4122 | 1032 | 1006 | 1161.5 | 1268.5 | 61.2332 | 63.9194 | 63.0037 | 61.4164 | 0.61233 | 0.63919 | 0.63004 | 0.61416 | 0.026862 | 0.015873 | 720.9983 | 952.1992 | 5.4471
38938.4129 | 1040 | 1090 | 38938.4129 | 952 | 988 | 1220.5 | 1327.5 | 63.4921 | 66.5446 | 58.1197 | 60.3175 | 0.63492 | 0.66545 | 0.5812 | 0.60317 | 0.030525 | 0.021978 | 897.7602 | 1567.8515 | 1.4644
38938.4135 | 1105 | 1154 | 38938.4136 | 931 | 890 | 1279.5 | 1386.5 | 67.4603 | 70.4518 | 56.8376 | 54.3346 | 0.6746 | 0.70452 | 0.56838 | 0.54335 | 0.029915 | 0.025031 | 1550.5904 | 7208.5412 | 12.4768
38938.4142 | 968 | 942 | 38938.4142 | 1058 | 1109 | 1338 | 1445 | 59.0965 | 57.5092 | 64.591 | 67.7045 | 0.59096 | 0.57509 | 0.64591 | 0.67705 | 0.015873 | 0.031136 | 792.4758 | 795.0278 | 19.144
38938.4149 | 970 | 930 | 38938.4149 | 1025 | 986 | 1397 | 1504 | 59.2186 | 56.7766 | 62.5763 | 60.1954 | 0.59219 | 0.56777 | 0.62576 | 0.60195 | 0.02442 | 0.02381 | 4505.0011 | 6357.7775 | 22.5507
38938.4156 | 936 | 902 | 38938.4156 | 1074 | 1019 | 1455.5 | 1562.5 | 57.1429 | 55.0672 | 65.5678 | 62.21 | 0.57143 | 0.55067 | 0.65568 | 0.6221 | 0.020757 | 0.033578 | 2127.0217 | 4227.4917 | 29.7855
38938.4163 | 1130 | 1099 | 38938.4163 | 1189 | 1168 | 1514.5 | 1621.5 | 68.9866 | 67.094 | 72.5885 | 71.3065 | 0.68987 | 0.67094 | 0.72589 | 0.71306 | 0.018926 | 0.012821 | 6743.2175 | 6692.2044 | 10.3979
38938.4169 | 943 | 872 | 38938.417 | 1170 | 1140 | 1573.5 | 1680.5 | 57.5702 | 53.2357 | 71.4286 | 69.5971 | 0.5757 | 0.53236 | 0.71429 | 0.69597 | 0.043346 | 0.018315 | 267.8608 | 238.3807 | 24.0766
38938.4176 | 1038 | 971 | 38938.4176 | 1065 | 1153 | 1632 | 1739 | 63.37 | 59.2796 | 65.0183 | 70.3907 | 0.6337 | 0.5928 | 0.65018 | 0.70391 | 0.040904 | 0.053724 | 46.4816 | 43.2366 | 3.2337
38938.4183 | 936 | 909 | 38938.4183 | 1168 | 1181 | 1691 | 1798 | 57.1429 | 55.4945 | 71.3065 | 72.1001 | 0.57143 | 0.55495 | 0.71306 | 0.721 | 0.016484 | 0.0079365 | 283.0845 | 233.8059 | 20.6521
38938.419 | 1163 | 1126 | 38938.419 | 1098 | 1042 | 1749.5 | 1856.5 | 71.0012 | 68.7424 | 67.033 | 63.6142 | 0.71001 | 0.68742 | 0.67033 | 0.63614 | 0.022589 | 0.034188 | 819.6101 | 1426.9201 | 14.6052
38938.4197 | 1063 | 992 | 38938.4197 | 1153 | 1109 | 1808.5 | 1915.5 | 64.8962 | 60.5617 | 70.3907 | 67.7045 | 0.64896 | 0.60562 | 0.70391 | 0.67705 | 0.043346 | 0.026862 | 375.6628 | 475.7536 | 4.8329
38938.4203 | 1051 | 1080 | 38938.4204 | 1206 | 1181 | 1867.5 | 1974.5 | 64.1636 | 65.9341 | 73.6264 | 72.1001 | 0.64164 | 0.65934 | 0.73626 | 0.721 | 0.017705 | 0.015263 | 44830.2202 | 4055.4214 | 1.6248

## C3-4
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 3 & 4
Time-23 | N11 | N12 | Time-24 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38938.3979 | 1 | 0 | 38938.3979 | 1 | 0 | -75.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3985 | 1 | 0 | 38938.3986 | 1 | 0 | -17 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3992 | 1 | 0 | 38938.3992 | 1 | 0 | 42 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3999 | 1 | 0 | 38938.3999 | 1 | 0 | 100.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4006 | 1 | 0 | 38938.4006 | 1 | 0 | 159.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4013 | 1 | 0 | 38938.4013 | 1 | 0 | 218.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4019 | 1 | 0 | 38938.402 | 1 | 0 | 277 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4026 | 1 | 0 | 38938.4026 | 1 | 0 | 336 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4033 | 1 | 0 | 38938.4033 | 1 | 0 | 394.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.404 | 1 | 0 | 38938.404 | 1 | 0 | 453.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4047 | 1 | 0 | 38938.4047 | 1 | 0 | 512.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4053 | 1 | 0 | 38938.4054 | 1 | 0 | 571 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.406 | 1149 | 1190 | 38938.406 | 1075 | 1047 | 629.5 | 736.5 | 70.1465 | 72.6496 | 65.6288 | 63.9194 | 0.70147 | 0.7265 | 0.65629 | 0.63919 | 0.025031 | 0.017094 | 2654.6459 | 25397.2174 | 18.9154
38938.4067 | 923 | 927 | 38938.4067 | 932 | 1035 | 688.5 | 795.5 | 56.3492 | 56.5934 | 56.8987 | 63.1868 | 0.56349 | 0.56593 | 0.56899 | 0.63187 | 0.002442 | 0.062882 | 491.4142 | 389.2304 | 22.5737
38938.4074 | 1159 | 1138 | 38938.4074 | 1122 | 918 | 747.5 | 854.5 | 70.757 | 69.475 | 68.4982 | 56.044 | 0.70757 | 0.69475 | 0.68498 | 0.56044 | 0.012821 | 0.12454 | 46.9532 | 56.5929 | 5.8428
38938.4081 | 1099 | 1067 | 38938.4081 | 1198 | 1057 | 806 | 913 | 67.094 | 65.1404 | 73.138 | 64.5299 | 0.67094 | 0.6514 | 0.73138 | 0.6453 | 0.019536 | 0.086081 | 165.0379 | 183.2022 | 3.212
38938.4087 | 1026 | 998 | 38938.4088 | 1154 | 1131 | 865 | 972 | 62.6374 | 60.928 | 70.4518 | 69.0476 | 0.62637 | 0.60928 | 0.70452 | 0.69048 | 0.017094 | 0.014042 | 2212.7165 | 4724.0276 | 8.7349
38938.4094 | 1105 | 1081 | 38938.4094 | 1097 | 1173 | 923.5 | 1030.5 | 67.4603 | 65.9951 | 66.9719 | 71.6117 | 0.6746 | 0.65995 | 0.66972 | 0.71612 | 0.014652 | 0.046398 | 422.0843 | 503.213 | 5.632
38938.4101 | 1178 | 1157 | 38938.4101 | 1170 | 1147 | 982.5 | 1089.5 | 71.917 | 70.6349 | 71.4286 | 70.0244 | 0.71917 | 0.70635 | 0.71429 | 0.70024 | 0.012821 | 0.014042 | 6541.7731 | 17250.8053 | 19.0752
38938.4108 | 1095 | 1173 | 38938.4108 | 996 | 1039 | 1041.5 | 1148.5 | 66.8498 | 71.6117 | 60.8059 | 63.431 | 0.6685 | 0.71612 | 0.60806 | 0.63431 | 0.047619 | 0.026252 | 222.408 | 308.9067 | 9.9812
38938.4115 | 1155 | 1133 | 38938.4115 | 929 | 933 | 1100 | 1207 | 70.5128 | 69.1697 | 56.7155 | 56.9597 | 0.70513 | 0.6917 | 0.56716 | 0.5696 | 0.013431 | 0.002442 | 358.9155 | 462.5986 | 12.6988
38938.4121 | 1109 | 1166 | 38938.4122 | 1077 | 1162 | 1159 | 1266 | 67.7045 | 71.1844 | 65.7509 | 70.9402 | 0.67705 | 0.71184 | 0.65751 | 0.7094 | 0.034799 | 0.051893 | 785.6512 | 1647.0177 | 13.0968
38938.4128 | 921 | 952 | 38938.4128 | 1111 | 1167 | 1217.5 | 1324.5 | 56.2271 | 58.1197 | 67.8266 | 71.2454 | 0.56227 | 0.5812 | 0.67827 | 0.71245 | 0.018926 | 0.034188 | 375.0391 | 331.8937 | 19.3746
38938.4135 | 1121 | 1179 | 38938.4135 | 1002 | 954 | 1276.5 | 1383.5 | 68.4371 | 71.978 | 61.1722 | 58.2418 | 0.68437 | 0.71978 | 0.61172 | 0.58242 | 0.035409 | 0.029304 | 288.1544 | 411.8536 | 12.7608
38938.4142 | 1034 | 1009 | 38938.4142 | 1089 | 1065 | 1335.5 | 1442.5 | 63.1258 | 61.5995 | 66.4835 | 65.0183 | 0.63126 | 0.616 | 0.66484 | 0.65018 | 0.015263 | 0.014652 | 2192.3482 | 4166.4004 | 6.7769
38938.4149 | 1008 | 979 | 38938.4149 | 1115 | 1088 | 1394 | 1501 | 61.5385 | 59.768 | 68.0708 | 66.4225 | 0.61538 | 0.59768 | 0.68071 | 0.66422 | 0.017705 | 0.016484 | 1501.4489 | 2195.2193 | 12.3115
38938.4155 | 1017 | 935 | 38938.4156 | 1044 | 1068 | 1453 | 1560 | 62.0879 | 57.0818 | 63.7363 | 65.2015 | 0.62088 | 0.57082 | 0.63736 | 0.65201 | 0.050061 | 0.014652 | 265.3914 | 282.4923 | 12.719
38938.4162 | 970 | 932 | 38938.4162 | 1155 | 1198 | 1511.5 | 1618.5 | 59.2186 | 56.8987 | 70.5128 | 73.138 | 0.59219 | 0.56899 | 0.70513 | 0.73138 | 0.023199 | 0.026252 | 585.6326 | 592.9622 | 19.3743
38938.4169 | 926 | 924 | 38938.4169 | 987 | 990 | 1570.5 | 1677.5 | 56.5324 | 56.4103 | 60.2564 | 60.4396 | 0.56532 | 0.5641 | 0.60256 | 0.6044 | 0.001221 | 0.0018315 | 81130.9063 | 172096.6022 | 28.4488
38938.4176 | 1197 | 1174 | 38938.4176 | 965 | 893 | 1629.5 | 1736.5 | 73.0769 | 71.6728 | 58.9133 | 54.5177 | 0.73077 | 0.71673 | 0.58913 | 0.54518 | 0.014042 | 0.043956 | 5.5524 | 7.1261 | 1.4618
38938.4183 | 929 | 904 | 38938.4183 | 1192 | 1192 | 1688 | 1795 | 56.7155 | 55.1893 | 72.7717 | 72.7717 | 0.56716 | 0.55189 | 0.72772 | 0.72772 | 0.015263 | 0 | 56.1903 | 43.4164 | 9.3773
38938.4189 | 1197 | 1178 | 38938.419 | 947 | 862 | 1747 | 1854 | 73.0769 | 71.917 | 57.8144 | 52.6252 | 0.73077 | 0.71917 | 0.57814 | 0.52625 | 0.0116 | 0.051893 | 67.536 | 88.0851 | 10.4153
38938.4196 | 1136 | 1086 | 38938.4196 | 1150 | 1108 | 1805.5 | 1912.5 | 69.3529 | 66.3004 | 70.2076 | 67.6435 | 0.69353 | 0.663 | 0.70208 | 0.67643 | 0.030525 | 0.025641 | 10334.7066 | 2678.4245 | 9.6738
38938.4203 | 1191 | 1158 | 38938.4203 | 1105 | 1046 | 1864.5 | 1971.5 | 72.7106 | 70.696 | 67.4603 | 63.8584 | 0.72711 | 0.70696 | 0.6746 | 0.63858 | 0.020147 | 0.03602 | 803.9783 | 1417.6895 | 19.0355

## C2-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 7
Time-21 | N11 | N12 | Time-22 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
38938.3978 | 1 | 0 | 38938.3978 | 1 | 0 | -78.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3985 | 1 | 0 | 38938.3985 | 1 | 0 | -19.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3992 | 1 | 0 | 38938.3992 | 1 | 0 | 39 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3999 | 1 | 0 | 38938.3999 | 1 | 0 | 98 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4005 | 1 | 0 | 38938.4006 | 1 | 0 | 156.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4012 | 1 | 0 | 38938.4012 | 1 | 0 | 215.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4019 | 1 | 0 | 38938.4019 | 1 | 0 | 274.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4026 | 1 | 0 | 38938.4026 | 1 | 0 | 333 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4033 | 1 | 0 | 38938.4033 | 1 | 0 | 392 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4039 | 1 | 0 | 38938.404 | 1 | 0 | 450.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4046 | 1 | 0 | 38938.4046 | 1 | 0 | 509.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4053 | 1 | 0 | 38938.4053 | 1 | 0 | 568.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.406 | 1174 | 1154 | 38938.406 | 935 | 905 | 627 | 734 | 71.6728 | 70.4518 | 57.0818 | 55.2503 | 0.71673 | 0.70452 | 0.57082 | 0.5525 | 0.01221 | 0.018315 | 558.9202 | 779.6977 | 16.5114
38938.4067 | 1170 | 1144 | 38938.4067 | 998 | 945 | 685.5 | 792.5 | 71.4286 | 69.8413 | 60.928 | 57.6923 | 0.71429 | 0.69841 | 0.60928 | 0.57692 | 0.015873 | 0.032357 | 93.5286 | 116.4651 | 9.4522
38938.4073 | 978 | 951 | 38938.4074 | 1122 | 1095 | 744.5 | 851.5 | 59.707 | 58.0586 | 68.4982 | 66.8498 | 0.59707 | 0.58059 | 0.68498 | 0.6685 | 0.016484 | 0.016484 | 7726 | 7726 | 19.1029
38938.408 | 1116 | 1088 | 38938.408 | 1110 | 1179 | 803.5 | 910.5 | 68.1319 | 66.4225 | 67.7656 | 71.978 | 0.68132 | 0.66422 | 0.67766 | 0.71978 | 0.017094 | 0.042125 | 601.6948 | 790.1123 | 7.4227
38938.4087 | 964 | 1001 | 38938.4087 | 925 | 958 | 862 | 969 | 58.8523 | 61.1111 | 56.4713 | 58.486 | 0.58852 | 0.61111 | 0.56471 | 0.58486 | 0.022589 | 0.020147 | 3717.598 | 16430.2833 | 14.6978
38938.4094 | 973 | 948 | 38938.4094 | 1085 | 1061 | 921 | 1028 | 59.4017 | 57.8755 | 66.2393 | 64.7741 | 0.59402 | 0.57875 | 0.66239 | 0.64774 | 0.015263 | 0.014652 | 5634.5722 | 19885.0194 | 20.1539
38938.4101 | 1189 | 1193 | 38938.4101 | 951 | 987 | 980 | 1087 | 72.5885 | 72.8327 | 58.0586 | 60.2564 | 0.72589 | 0.72833 | 0.58059 | 0.60256 | 0.002442 | 0.021978 | 270.9177 | 353.9321 | 17.5796
38938.4108 | 1191 | 1172 | 38938.4108 | 1167 | 1146 | 1038.5 | 1145.5 | 72.7106 | 71.5507 | 71.2454 | 69.9634 | 0.72711 | 0.71551 | 0.71245 | 0.69963 | 0.0116 | 0.012821 | 7093.8475 | 19525.0682 | 21.2207
38938.4114 | 1020 | 995 | 38938.4114 | 1020 | 1065 | 1097.5 | 1204.5 | 62.2711 | 60.7448 | 62.2711 | 65.0183 | 0.62271 | 0.60745 | 0.62271 | 0.65018 | 0.015263 | 0.027473 | 773.7627 | 855.8377 | 8.8206
38938.4121 | 440 | 367 | 38938.4121 | 102 | 142 | 1156 | 1263 | 26.862 | 22.4054 | 6.2271 | 8.6691 | 0.26862 | 0.22405 | 0.062271 | 0.086691 | 0.044567 | 0.02442 | 2507.0019 | 5856.9081 | 349.8898
38938.4128 | 1084 | 1060 | 38938.4128 | 1185 | 1168 | 1215 | 1322 | 66.1783 | 64.7131 | 72.3443 | 71.3065 | 0.66178 | 0.64713 | 0.72344 | 0.71306 | 0.014652 | 0.010379 | 6657.9704 | 12405.584 | 2.8993
38938.4135 | 1065 | 1037 | 38938.4135 | 1151 | 1122 | 1273.5 | 1380.5 | 65.0183 | 63.3089 | 70.2686 | 68.4982 | 0.65018 | 0.63309 | 0.70269 | 0.68498 | 0.017094 | 0.017705 | 4951.4035 | 15174.3956 | 1.0557
38938.4142 | 1158 | 1196 | 38938.4142 | 993 | 966 | 1332.5 | 1439.5 | 70.696 | 73.0159 | 60.6227 | 58.9744 | 0.70696 | 0.73016 | 0.60623 | 0.58974 | 0.023199 | 0.016484 | 834.5165 | 1564.6276 | 18.9384
38938.4148 | 856 | 835 | 38938.4148 | 1077 | 930 | 1391.5 | 1498.5 | 52.2589 | 50.9768 | 65.7509 | 56.7766 | 0.52259 | 0.50977 | 0.65751 | 0.56777 | 0.012821 | 0.089744 | 520.6013 | 378.7614 | 39.9846
38938.4155 | 970 | 899 | 38938.4155 | 1176 | 1135 | 1450 | 1557 | 59.2186 | 54.884 | 71.7949 | 69.2918 | 0.59219 | 0.54884 | 0.71795 | 0.69292 | 0.043346 | 0.025031 | 170.7738 | 150.2545 | 16.2971
38938.4162 | 936 | 904 | 38938.4162 | 987 | 1020 | 1509 | 1616 | 57.1429 | 55.1893 | 60.2564 | 62.2711 | 0.57143 | 0.55189 | 0.60256 | 0.62271 | 0.019536 | 0.020147 | 6503.6522 | 6502.5825 | 29.7439
38938.4169 | 955 | 876 | 38938.4169 | 922 | 956 | 1567.5 | 1674.5 | 58.3028 | 53.4799 | 56.2882 | 58.3639 | 0.58303 | 0.5348 | 0.56288 | 0.58364 | 0.04823 | 0.020757 | 842.4783 | 1498.6147 | 30.1802
38938.4176 | 1158 | 1193 | 38938.4176 | 1147 | 1110 | 1626.5 | 1733.5 | 70.696 | 72.8327 | 70.0244 | 67.7656 | 0.70696 | 0.72833 | 0.70024 | 0.67766 | 0.021368 | 0.022589 | 3888.1889 | 11429.4782 | 19.775
38938.4182 | 1166 | 1122 | 38938.4183 | 1056 | 990 | 1685.5 | 1792.5 | 71.1844 | 68.4982 | 64.4689 | 60.4396 | 0.71184 | 0.68498 | 0.64469 | 0.6044 | 0.026862 | 0.040293 | 398.5058 | 579.4175 | 13.3
38938.4189 | 959 | 1069 | 38938.4189 | 938 | 890 | 1744 | 1851 | 58.547 | 65.2625 | 57.265 | 54.3346 | 0.58547 | 0.65263 | 0.57265 | 0.54335 | 0.067155 | 0.029304 | 519.0987 | 951.8108 | 7.1971
38938.4196 | 1024 | 947 | 38938.4196 | 1102 | 1042 | 1803 | 1910 | 62.5153 | 57.8144 | 67.2772 | 63.6142 | 0.62515 | 0.57814 | 0.67277 | 0.63614 | 0.047009 | 0.03663 | 543.295 | 767.1291 | 13.2674
38938.4203 | 1138 | 1185 | 38938.4203 | 1123 | 1072 | 1861.5 | 1968.5 | 69.475 | 72.3443 | 68.5592 | 65.4457 | 0.69475 | 0.72344 | 0.68559 | 0.65446 | 0.028694 | 0.031136 | 2193.8247 | 46358.6583 | 17.6817

## C2-6
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 6
Time-19 | N11 | N12 | Time-20 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38938.3978 | 1 | 0 | 38938.3978 | 1 | 0 | -81.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3985 | 1 | 0 | 38938.3985 | 1 | 0 | -22.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3992 | 1 | 0 | 38938.3992 | 1 | 0 | 36.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3998 | 1 | 0 | 38938.3998 | 1 | 0 | 95 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4005 | 1 | 0 | 38938.4005 | 1 | 0 | 154 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4012 | 1 | 0 | 38938.4012 | 1 | 0 | 212.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4019 | 1 | 0 | 38938.4019 | 1 | 0 | 271.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4026 | 1 | 0 | 38938.4026 | 1 | 0 | 330.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4032 | 1 | 0 | 38938.4033 | 1 | 0 | 389 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4039 | 1 | 0 | 38938.4039 | 1 | 0 | 448 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4046 | 1 | 0 | 38938.4046 | 1 | 0 | 506.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4053 | 1 | 0 | 38938.4053 | 1 | 0 | 565.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4059 | 1195 | 1180 | 38938.406 | 949 | 917 | 624 | 731 | 72.9548 | 72.0391 | 57.9365 | 55.9829 | 0.72955 | 0.72039 | 0.57937 | 0.55983 | 0.0091575 | 0.019536 | 66.3377 | 86.2032 | 10.2783
38938.4066 | 1157 | 1127 | 38938.4067 | 1009 | 958 | 683 | 790 | 70.6349 | 68.8034 | 61.5995 | 58.486 | 0.70635 | 0.68803 | 0.616 | 0.58486 | 0.018315 | 0.031136 | 99.3612 | 120.9011 | 8.3034
38938.4073 | 1128 | 1101 | 38938.4073 | 1063 | 1031 | 742 | 849 | 68.8645 | 67.2161 | 64.8962 | 62.9426 | 0.68864 | 0.67216 | 0.64896 | 0.62943 | 0.016484 | 0.019536 | 1465.3911 | 2737.5178 | 10.1628
38938.408 | 973 | 929 | 38938.408 | 1048 | 1016 | 800.5 | 907.5 | 59.4017 | 56.7155 | 63.9805 | 62.0269 | 0.59402 | 0.56716 | 0.6398 | 0.62027 | 0.026862 | 0.019536 | 1577.5521 | 3286.7356 | 22.044
38938.4087 | 1010 | 982 | 38938.4087 | 1106 | 1081 | 859.5 | 966.5 | 61.6606 | 59.9512 | 67.5214 | 65.9951 | 0.61661 | 0.59951 | 0.67521 | 0.65995 | 0.017094 | 0.015263 | 1349.7982 | 1828.0854 | 11.6847
38938.4094 | 925 | 956 | 38938.4094 | 1170 | 1193 | 918.5 | 1025.5 | 56.4713 | 58.3639 | 71.4286 | 72.8327 | 0.56471 | 0.58364 | 0.71429 | 0.72833 | 0.018926 | 0.014042 | 278.5321 | 241.7017 | 17.1672
38938.41 | 1080 | 1163 | 38938.4101 | 1156 | 1134 | 977 | 1084 | 65.9341 | 71.0012 | 70.5739 | 69.2308 | 0.65934 | 0.71001 | 0.70574 | 0.69231 | 0.050672 | 0.013431 | 613.2622 | 1361.0821 | 10.4113
38938.4107 | 982 | 953 | 38938.4107 | 921 | 992 | 1035.5 | 1142.5 | 59.9512 | 58.1807 | 56.2271 | 60.5617 | 0.59951 | 0.58181 | 0.56227 | 0.60562 | 0.017705 | 0.043346 | 1217.1915 | 1490.9153 | 17.5058
38938.4114 | 1091 | 1067 | 38938.4114 | 1066 | 1041 | 1094.5 | 1201.5 | 66.6056 | 65.1404 | 65.0794 | 63.5531 | 0.66606 | 0.6514 | 0.65079 | 0.63553 | 0.014652 | 0.015263 | 2629.88 | 7179.4562 | 4.1576
38938.4121 | 985 | 957 | 38938.4121 | 1098 | 1073 | 1153.5 | 1260.5 | 60.1343 | 58.4249 | 67.033 | 65.5067 | 0.60134 | 0.58425 | 0.67033 | 0.65507 | 0.017094 | 0.015263 | 2627.0778 | 6406.3933 | 17.5958
38938.4128 | 1159 | 1136 | 38938.4128 | 1186 | 1089 | 1212 | 1319 | 70.757 | 69.3529 | 72.4054 | 66.4835 | 0.70757 | 0.69353 | 0.72405 | 0.66484 | 0.014042 | 0.059219 | 396.8789 | 522.5856 | 13.4463
38938.4134 | 977 | 952 | 38938.4135 | 985 | 957 | 1271 | 1378 | 59.6459 | 58.1197 | 60.1343 | 58.4249 | 0.59646 | 0.5812 | 0.60134 | 0.58425 | 0.015263 | 0.017094 | 23981.1771 | 4698.249 | 18.927
38938.4141 | 1054 | 936 | 38938.4141 | 956 | 932 | 1329.5 | 1436.5 | 64.3468 | 57.1429 | 58.3639 | 56.8987 | 0.64347 | 0.57143 | 0.58364 | 0.56899 | 0.072039 | 0.014652 | 309.4352 | 417.4046 | 10.603
38938.4148 | 1057 | 1153 | 38938.4148 | 970 | 1009 | 1388.5 | 1495.5 | 64.5299 | 70.3907 | 59.2186 | 61.5995 | 0.6453 | 0.70391 | 0.59219 | 0.616 | 0.058608 | 0.02381 | 67.4383 | 78.4404 | 3.6974
38938.4155 | 970 | 872 | 38938.4155 | 1144 | 1185 | 1447.5 | 1554.5 | 59.2186 | 53.2357 | 69.8413 | 72.3443 | 0.59219 | 0.53236 | 0.69841 | 0.72344 | 0.059829 | 0.025031 | 125.4632 | 107.2518 | 16.0839
38938.4162 | 969 | 907 | 38938.4162 | 1030 | 1071 | 1506 | 1613 | 59.1575 | 55.3724 | 62.8816 | 65.3846 | 0.59158 | 0.55372 | 0.62882 | 0.65385 | 0.037851 | 0.025031 | 893.1822 | 1372.5038 | 24.3576
38938.4168 | 1088 | 1045 | 38938.4169 | 993 | 937 | 1565 | 1672 | 66.4225 | 63.7973 | 60.6227 | 57.2039 | 0.66422 | 0.63797 | 0.60623 | 0.57204 | 0.026252 | 0.034188 | 1630.2309 | 5257.6616 | 1.8763
38938.4175 | 1052 | 996 | 38938.4175 | 924 | 906 | 1623.5 | 1730.5 | 64.2247 | 60.8059 | 56.4103 | 55.3114 | 0.64225 | 0.60806 | 0.5641 | 0.55311 | 0.034188 | 0.010989 | 738.2229 | 1135.3502 | 5.9997
38938.4182 | 1015 | 934 | 38938.4182 | 1093 | 1037 | 1682.5 | 1789.5 | 61.9658 | 57.0208 | 66.7277 | 63.3089 | 0.61966 | 0.57021 | 0.66728 | 0.63309 | 0.049451 | 0.034188 | 499.5259 | 672.8504 | 15.2888
38938.4189 | 1073 | 1013 | 38938.4189 | 1196 | 1176 | 1741.5 | 1848.5 | 65.5067 | 61.8437 | 73.0159 | 71.7949 | 0.65507 | 0.61844 | 0.73016 | 0.71795 | 0.03663 | 0.01221 | 683.4311 | 1098.9813 | 2.4449
38938.4196 | 1153 | 1190 | 38938.4196 | 1190 | 1161 | 1800 | 1907 | 70.3907 | 72.6496 | 72.6496 | 70.8791 | 0.70391 | 0.7265 | 0.7265 | 0.70879 | 0.022589 | 0.017705 | 138299.6538 | 3277.7095 | 18.7539
38938.4202 | 1056 | 1007 | 38938.4203 | 1142 | 1105 | 1859 | 1966 | 64.4689 | 61.4774 | 69.7192 | 67.4603 | 0.64469 | 0.61477 | 0.69719 | 0.6746 | 0.029915 | 0.022589 | 836.6205 | 1301.9753 | 4.6129

## C2-5
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 5
Time-17 | N11 | N12 | Time-18 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38938.3978 | 1 | 0 | 38938.3978 | 1 | 0 | -84 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3984 | 1 | 0 | 38938.3984 | 1 | 0 | -25.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3991 | 1 | 0 | 38938.3991 | 1 | 0 | 33.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3998 | 1 | 0 | 38938.3998 | 1 | 0 | 92.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4005 | 1 | 0 | 38938.4005 | 1 | 0 | 151 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4012 | 1 | 0 | 38938.4012 | 1 | 0 | 210 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4018 | 1 | 1 | 38938.4019 | 1 | 0 | 268.5 | 375.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38938.4025 | 1 | 0 | 38938.4025 | 1 | 0 | 327.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4032 | 1 | 0 | 38938.4032 | 1 | 0 | 386 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4039 | 1 | 0 | 38938.4039 | 1 | 0 | 445 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4046 | 1 | 0 | 38938.4046 | 1 | 0 | 503.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4052 | 1 | 0 | 38938.4053 | 1 | 0 | 562.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4059 | 936 | 905 | 38938.4059 | 1011 | 980 | 621.5 | 728.5 | 57.1429 | 55.2503 | 61.7216 | 59.8291 | 0.57143 | 0.5525 | 0.61722 | 0.59829 | 0.018926 | 0.018926 | 6716.1935 | 6716.1935 | 29.6165
38938.4066 | 928 | 1034 | 38938.4066 | 1193 | 1027 | 680 | 787 | 56.6545 | 63.1258 | 72.8327 | 62.6984 | 0.56654 | 0.63126 | 0.72833 | 0.62698 | 0.064713 | 0.10134 | 38.2129 | 34.523 | 3.7482
38938.4073 | 3 | 17 | 38938.4073 | 3 | 17 | 739 | 846 | 0.18315 | 1.0379 | 0.18315 | 1.0379 | 0.0018315 | 0.010379 | 0.0018315 | 0.010379 | 0.008547 | 0.008547 | 15193 | 15193 | 12231.3757
38938.408 | 3 | 17 | 38938.408 | 3 | 17 | 797.5 | 904.5 | 0.18315 | 1.0379 | 0.18315 | 1.0379 | 0.0018315 | 0.010379 | 0.0018315 | 0.010379 | 0.008547 | 0.008547 | 15193 | 15193 | 12231.3757
38938.4086 | 4 | 17 | 38938.4087 | 4 | 13 | 856.5 | 963.5 | 0.2442 | 1.0379 | 0.2442 | 0.79365 | 0.002442 | 0.010379 | 0.002442 | 0.0079365 | 0.0079365 | 0.0054945 | 16313.4608 | 23642.8971 | 12254.1698
38938.4093 | 3 | 18 | 38938.4093 | 3 | 17 | 915.5 | 1022.5 | 0.18315 | 1.0989 | 0.18315 | 1.0379 | 0.0018315 | 0.010989 | 0.0018315 | 0.010379 | 0.0091575 | 0.008547 | 14178.7243 | 15201.7614 | 11546.3791
38938.41 | 4 | 16 | 38938.41 | 3 | 12 | 974 | 1081 | 0.2442 | 0.9768 | 0.18315 | 0.7326 | 0.002442 | 0.009768 | 0.0018315 | 0.007326 | 0.007326 | 0.0054945 | 17674.9283 | 23622.8691 | 13026.2325
38938.4107 | 4 | 17 | 38938.4107 | 3 | 17 | 1033 | 1140 | 0.2442 | 1.0379 | 0.18315 | 1.0379 | 0.002442 | 0.010379 | 0.0018315 | 0.010379 | 0.0079365 | 0.008547 | 16364.1616 | 15184.2445 | 12225.4857
38938.4114 | 1020 | 1006 | 38938.4114 | 1029 | 1075 | 1091.5 | 1198.5 | 62.2711 | 61.4164 | 62.8205 | 65.6288 | 0.62271 | 0.61416 | 0.62821 | 0.65629 | 0.008547 | 0.028083 | 332.4967 | 319.6379 | 6.5888
38938.412 | 3 | 11 | 38938.4121 | 25 | 41 | 1150.5 | 1257.5 | 0.18315 | 0.67155 | 1.5263 | 2.5031 | 0.0018315 | 0.0067155 | 0.015263 | 0.025031 | 0.004884 | 0.009768 | 26653.378 | 13176.809 | 18938.2757
38938.4127 | 958 | 998 | 38938.4127 | 1004 | 979 | 1209.5 | 1316.5 | 58.486 | 60.928 | 61.2943 | 59.768 | 0.58486 | 0.60928 | 0.61294 | 0.59768 | 0.02442 | 0.015263 | 1565.6144 | 2954.9155 | 15.2184
38938.4134 | 1177 | 1148 | 38938.4134 | 966 | 940 | 1268 | 1375 | 71.8559 | 70.0855 | 58.9744 | 57.3871 | 0.71856 | 0.70085 | 0.58974 | 0.57387 | 0.017705 | 0.015873 | 160.6269 | 207.3215 | 12.4567
38938.4141 | 1035 | 1010 | 38938.4141 | 933 | 922 | 1327 | 1434 | 63.1868 | 61.6606 | 56.9597 | 56.2882 | 0.63187 | 0.61661 | 0.5696 | 0.56288 | 0.015263 | 0.0067155 | 1853.485 | 3045.6742 | 6.5206
38938.4148 | 1045 | 1094 | 38938.4148 | 1027 | 1000 | 1385.5 | 1492.5 | 63.7973 | 66.7888 | 62.6984 | 61.0501 | 0.63797 | 0.66789 | 0.62698 | 0.6105 | 0.029915 | 0.016484 | 278.2917 | 326.7846 | 1.8183
38938.4155 | 1200 | 1184 | 38938.4155 | 1044 | 1142 | 1444.5 | 1551.5 | 73.2601 | 72.2833 | 63.7363 | 69.7192 | 0.7326 | 0.72283 | 0.63736 | 0.69719 | 0.009768 | 0.059829 | 380.168 | 528.1888 | 19.2435
38938.4161 | 968 | 912 | 38938.4161 | 1197 | 1189 | 1503.5 | 1610.5 | 59.0965 | 55.6777 | 73.0769 | 72.5885 | 0.59096 | 0.55678 | 0.73077 | 0.72589 | 0.034188 | 0.004884 | 80.6952 | 66.9139 | 10.2429
38938.4168 | 1176 | 1142 | 38938.4168 | 1095 | 895 | 1562 | 1669 | 71.7949 | 69.7192 | 66.8498 | 54.6398 | 0.71795 | 0.69719 | 0.6685 | 0.5464 | 0.020757 | 0.1221 | 35.1854 | 43.4371 | 5.4356
38938.4175 | 979 | 903 | 38938.4175 | 983 | 910 | 1621 | 1728 | 59.768 | 55.1282 | 60.0122 | 55.5556 | 0.59768 | 0.55128 | 0.60012 | 0.55556 | 0.046398 | 0.044567 | 2302.9922 | 3374.5853 | 24.8473
38938.4182 | 1198 | 1177 | 38938.4182 | 1110 | 1059 | 1679.5 | 1786.5 | 73.138 | 71.8559 | 67.7656 | 64.652 | 0.73138 | 0.71856 | 0.67766 | 0.64652 | 0.012821 | 0.031136 | 843.5047 | 1345.4758 | 20.7184
38938.4189 | 1099 | 1054 | 38938.4189 | 1163 | 1122 | 1738.5 | 1845.5 | 67.094 | 64.3468 | 71.0012 | 68.4982 | 0.67094 | 0.64347 | 0.71001 | 0.68498 | 0.027473 | 0.025031 | 47343.7097 | 2459.2742 | 3.645
38938.4195 | 1142 | 1094 | 38938.4195 | 988 | 911 | 1797.5 | 1904.5 | 69.7192 | 66.7888 | 60.3175 | 55.6166 | 0.69719 | 0.66789 | 0.60317 | 0.55617 | 0.029304 | 0.047009 | 316.7735 | 423.1543 | 9.0926
38938.4202 | 1199 | 1107 | 38938.4202 | 983 | 918 | 1856 | 1963 | 73.199 | 67.5824 | 60.0122 | 56.044 | 0.73199 | 0.67582 | 0.60012 | 0.56044 | 0.056166 | 0.039683 | 51.9729 | 66.4208 | 6.9576

## C2-4
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 4
Time-15 | N11 | N12 | Time-16 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38938.3977 | 1 | 0 | 38938.3977 | 1 | 0 | -87 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3984 | 1 | 0 | 38938.3984 | 1 | 0 | -28 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3991 | 1 | 0 | 38938.3991 | 1 | 0 | 30.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3998 | 1 | 0 | 38938.3998 | 1 | 0 | 89.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4005 | 1 | 0 | 38938.4005 | 1 | 0 | 148.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4011 | 1 | 0 | 38938.4011 | 1 | 0 | 207 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4018 | 1 | 0 | 38938.4018 | 1 | 0 | 266 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4025 | 1 | 0 | 38938.4025 | 1 | 0 | 324.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4032 | 1 | 0 | 38938.4032 | 1 | 0 | 383.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4039 | 1 | 0 | 38938.4039 | 1 | 0 | 442.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4045 | 1 | 0 | 38938.4045 | 1 | 0 | 501 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4052 | 1 | 0 | 38938.4052 | 1 | 0 | 560 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4059 | 1156 | 1132 | 38938.4059 | 961 | 930 | 618.5 | 725.5 | 70.5739 | 69.1087 | 58.6691 | 56.7766 | 0.70574 | 0.69109 | 0.58669 | 0.56777 | 0.014652 | 0.018926 | 668.3153 | 949.6733 | 13.985
38938.4066 | 986 | 957 | 38938.4066 | 1048 | 1024 | 677.5 | 784.5 | 60.1954 | 58.4249 | 63.9805 | 62.5153 | 0.60195 | 0.58425 | 0.6398 | 0.62515 | 0.017705 | 0.014652 | 2782.8054 | 8322.1596 | 17.555
38938.4073 | 1113 | 1086 | 38938.4073 | 1147 | 1122 | 736.5 | 843.5 | 67.9487 | 66.3004 | 70.0244 | 68.4982 | 0.67949 | 0.663 | 0.70024 | 0.68498 | 0.016484 | 0.015263 | 23649.8491 | 4769.107 | 7.7545
38938.4079 | 1041 | 1089 | 38938.408 | 1138 | 1189 | 795 | 902 | 63.5531 | 66.4835 | 69.475 | 72.5885 | 0.63553 | 0.66484 | 0.69475 | 0.72589 | 0.029304 | 0.031136 | 2856.2476 | 10403.5907 | 1.5444
38938.4086 | 1180 | 1197 | 38938.4086 | 959 | 932 | 853.5 | 960.5 | 72.0391 | 73.0769 | 58.547 | 56.8987 | 0.72039 | 0.73077 | 0.58547 | 0.56899 | 0.010379 | 0.016484 | 306.1279 | 415.9411 | 17.7791
38938.4093 | 1002 | 1117 | 38938.4093 | 1013 | 985 | 912.5 | 1019.5 | 61.1722 | 68.1929 | 61.8437 | 60.1343 | 0.61172 | 0.68193 | 0.61844 | 0.60134 | 0.070208 | 0.017094 | 128.01 | 148.3565 | 0.3198
38938.41 | 1006 | 979 | 38938.41 | 978 | 952 | 971.5 | 1078.5 | 61.4164 | 59.768 | 59.707 | 58.1197 | 0.61416 | 0.59768 | 0.59707 | 0.5812 | 0.016484 | 0.015873 | 6250.204 | 10540.1895 | 12.9537
38938.4106 | 1141 | 1192 | 38938.4107 | 1182 | 1195 | 1030 | 1137 | 69.6581 | 72.7717 | 72.1612 | 72.9548 | 0.69658 | 0.72772 | 0.72161 | 0.72955 | 0.031136 | 0.0079365 | 1624.0531 | 13466.6556 | 18.3187
38938.4113 | 932 | 965 | 38938.4114 | 1041 | 1017 | 1089 | 1196 | 56.8987 | 58.9133 | 63.5531 | 62.0879 | 0.56899 | 0.58913 | 0.63553 | 0.62088 | 0.020147 | 0.014652 | 2330.1955 | 5457.1258 | 21.9827
38938.412 | 1190 | 1174 | 38938.412 | 1035 | 1010 | 1147.5 | 1254.5 | 72.6496 | 71.6728 | 63.1868 | 61.6606 | 0.7265 | 0.71673 | 0.63187 | 0.61661 | 0.009768 | 0.015263 | 1575.8637 | 2757.66 | 20.6301
38938.4127 | 1157 | 1136 | 38938.4127 | 1163 | 1192 | 1206.5 | 1313.5 | 70.6349 | 69.3529 | 71.0012 | 72.7717 | 0.70635 | 0.69353 | 0.71001 | 0.72772 | 0.012821 | 0.017705 | 3431.4937 | 16559.355 | 15.7482
38938.4134 | 1088 | 1064 | 38938.4134 | 1118 | 1180 | 1265.5 | 1372.5 | 66.4225 | 64.9573 | 68.254 | 72.0391 | 0.66422 | 0.64957 | 0.68254 | 0.72039 | 0.014652 | 0.037851 | 559.7968 | 668.7377 | 3.187
38938.4141 | 1145 | 920 | 38938.4141 | 1010 | 984 | 1324 | 1431 | 69.9023 | 56.1661 | 61.6606 | 60.0733 | 0.69902 | 0.56166 | 0.61661 | 0.60073 | 0.13736 | 0.015873 | 72.4453 | 82.7927 | 2.3641
38938.4147 | 956 | 929 | 38938.4148 | 1187 | 1200 | 1383 | 1490 | 58.3639 | 56.7155 | 72.4664 | 73.2601 | 0.58364 | 0.56716 | 0.72466 | 0.7326 | 0.016484 | 0.0079365 | 335.5863 | 292.3446 | 18.2888
38938.4154 | 998 | 1022 | 38938.4154 | 1130 | 1089 | 1441.5 | 1548.5 | 60.928 | 62.3932 | 68.9866 | 66.4835 | 0.60928 | 0.62393 | 0.68987 | 0.66484 | 0.014652 | 0.025031 | 92.1435 | 86.1654 | 4.2127
38938.4161 | 1110 | 1067 | 38938.4161 | 961 | 903 | 1500.5 | 1607.5 | 67.7656 | 65.1404 | 58.6691 | 55.1282 | 0.67766 | 0.6514 | 0.58669 | 0.55128 | 0.026252 | 0.035409 | 1554.7488 | 4959.7186 | 5.8777
38938.4168 | 1173 | 1138 | 38938.4168 | 1048 | 992 | 1559.5 | 1666.5 | 71.6117 | 69.475 | 63.9805 | 60.5617 | 0.71612 | 0.69475 | 0.6398 | 0.60562 | 0.021368 | 0.034188 | 482.9671 | 712.879 | 15.257
38938.4175 | 987 | 928 | 38938.4175 | 1070 | 1011 | 1618 | 1725 | 60.2564 | 56.6545 | 65.3236 | 61.7216 | 0.60256 | 0.56654 | 0.65324 | 0.61722 | 0.03602 | 0.03602 | 3481.3898 | 3481.3898 | 20.7425
38938.4181 | 1157 | 1189 | 38938.4182 | 1092 | 1041 | 1677 | 1784 | 70.6349 | 72.5885 | 66.6667 | 63.5531 | 0.70635 | 0.72589 | 0.66667 | 0.63553 | 0.019536 | 0.031136 | 935.5292 | 1693.9665 | 18.5024
38938.4188 | 1132 | 1186 | 38938.4188 | 1032 | 984 | 1735.5 | 1842.5 | 69.1087 | 72.4054 | 63.0037 | 60.0733 | 0.69109 | 0.72405 | 0.63004 | 0.60073 | 0.032967 | 0.029304 | 7361.1521 | 2915.9386 | 16.7102
38938.4195 | 949 | 845 | 38938.4195 | 999 | 926 | 1794.5 | 1901.5 | 57.9365 | 51.5873 | 60.989 | 56.5324 | 0.57937 | 0.51587 | 0.60989 | 0.56532 | 0.063492 | 0.044567 | 949.312 | 4538.8089 | 36.94
38938.4202 | 1206 | 1019 | 38938.4202 | 1006 | 943 | 1853.5 | 1960.5 | 73.6264 | 62.21 | 61.4164 | 57.5702 | 0.73626 | 0.6221 | 0.61416 | 0.5757 | 0.11416 | 0.038462 | 30.2294 | 36.2187 | 2.9219

## C2-3
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-13 | N11 | N12 | Time-14 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38938.3977 | 1 | 0 | 38938.3977 | 1 | 0 | -89.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3984 | 1 | 0 | 38938.3984 | 1 | 0 | -31 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3991 | 1 | 0 | 38938.3991 | 1 | 0 | 28 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3997 | 1 | 0 | 38938.3997 | 1 | 0 | 86.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4004 | 1 | 0 | 38938.4004 | 1 | 0 | 145.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4011 | 1 | 0 | 38938.4011 | 1 | 0 | 204.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4018 | 1 | 0 | 38938.4018 | 1 | 0 | 263 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4025 | 1 | 0 | 38938.4025 | 1 | 0 | 321.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4031 | 1 | 0 | 38938.4031 | 1 | 0 | 380.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4038 | 1 | 0 | 38938.4038 | 1 | 0 | 439.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4045 | 1 | 0 | 38938.4045 | 1 | 0 | 498.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4052 | 1 | 0 | 38938.4052 | 1 | 0 | 557 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4059 | 1061 | 1033 | 38938.4059 | 1177 | 1193 | 615.5 | 722.5 | 64.7741 | 63.0647 | 71.8559 | 72.8327 | 0.64774 | 0.63065 | 0.71856 | 0.72833 | 0.017094 | 0.009768 | 2558.2946 | 7872.3198 | 1.8181
38938.4065 | 961 | 997 | 38938.4066 | 1076 | 1051 | 674.5 | 781.5 | 58.6691 | 60.8669 | 65.6899 | 64.1636 | 0.58669 | 0.60867 | 0.6569 | 0.64164 | 0.021978 | 0.015263 | 1183.3019 | 1624.9325 | 14.6472
38938.4072 | 1079 | 1050 | 38938.4072 | 1084 | 1137 | 733.5 | 840.5 | 65.873 | 64.1026 | 66.1783 | 69.4139 | 0.65873 | 0.64103 | 0.66178 | 0.69414 | 0.017705 | 0.032357 | 503.0247 | 594.6971 | 1.3028
38938.4079 | 1097 | 1072 | 38938.4079 | 1040 | 1015 | 792 | 899 | 66.9719 | 65.4457 | 63.4921 | 61.9658 | 0.66972 | 0.65446 | 0.63492 | 0.61966 | 0.015263 | 0.015263 | 8352.08 | 8352.08 | 5.1602
38938.4086 | 1039 | 1012 | 38938.4086 | 1167 | 1146 | 851 | 958 | 63.431 | 61.7827 | 71.2454 | 69.9634 | 0.63431 | 0.61783 | 0.71245 | 0.69963 | 0.016484 | 0.012821 | 3349.4059 | 19976.3708 | 6.0979
38938.4093 | 1079 | 1053 | 38938.4093 | 1185 | 1166 | 909.5 | 1016.5 | 65.873 | 64.2857 | 72.3443 | 71.1844 | 0.65873 | 0.64286 | 0.72344 | 0.71184 | 0.015873 | 0.0116 | 6507.472 | 10415.1564 | 1.7853
38938.4099 | 1157 | 1194 | 38938.41 | 957 | 931 | 968.5 | 1075.5 | 70.6349 | 72.8938 | 58.4249 | 56.8376 | 0.70635 | 0.72894 | 0.58425 | 0.56838 | 0.022589 | 0.015873 | 54.8717 | 70.0177 | 8.2082
38938.4106 | 1150 | 1128 | 38938.4106 | 964 | 1086 | 1027.5 | 1134.5 | 70.2076 | 68.8645 | 58.8523 | 66.3004 | 0.70208 | 0.68864 | 0.58852 | 0.663 | 0.013431 | 0.074481 | 105.4667 | 126.5847 | 8.171
38938.4113 | 1145 | 1123 | 38938.4113 | 1175 | 1156 | 1086.5 | 1193.5 | 69.9023 | 68.5592 | 71.7338 | 70.5739 | 0.69902 | 0.68559 | 0.71734 | 0.70574 | 0.013431 | 0.0116 | 55693.4281 | 5542.4281 | 13.5559
38938.412 | 932 | 973 | 38938.412 | 1057 | 1032 | 1145 | 1252 | 56.8987 | 59.4017 | 64.5299 | 63.0037 | 0.56899 | 0.59402 | 0.6453 | 0.63004 | 0.025031 | 0.015263 | 1281.0829 | 1900.7918 | 20.3107
38938.4127 | 972 | 948 | 38938.4127 | 949 | 1067 | 1203.5 | 1310.5 | 59.3407 | 57.8755 | 57.9365 | 65.1404 | 0.59341 | 0.57875 | 0.57937 | 0.6514 | 0.014652 | 0.072039 | 377.2947 | 340.4911 | 15.7385
38938.4133 | 1071 | 1126 | 38938.4134 | 964 | 1003 | 1262.5 | 1369.5 | 65.3846 | 68.7424 | 58.8523 | 61.2332 | 0.65385 | 0.68742 | 0.58852 | 0.61233 | 0.033578 | 0.02381 | 352.2636 | 467.5946 | 6.1442
38938.414 | 959 | 932 | 38938.414 | 1132 | 1108 | 1321.5 | 1428.5 | 58.547 | 56.8987 | 69.1087 | 67.6435 | 0.58547 | 0.56899 | 0.69109 | 0.67643 | 0.016484 | 0.014652 | 2414.3642 | 4481.1806 | 23.3019
38938.4147 | 981 | 1099 | 38938.4147 | 1200 | 1194 | 1380 | 1487 | 59.8901 | 67.094 | 73.2601 | 72.8938 | 0.5989 | 0.67094 | 0.7326 | 0.72894 | 0.072039 | 0.003663 | 275.5019 | 375.2214 | 2.3723
38938.4154 | 1034 | 976 | 38938.4154 | 958 | 1071 | 1439 | 1546 | 63.1258 | 59.5849 | 58.486 | 65.3846 | 0.63126 | 0.59585 | 0.58486 | 0.65385 | 0.035409 | 0.068987 | 464.2225 | 559.5177 | 8.9549
38938.4161 | 1095 | 1142 | 38938.4161 | 1020 | 958 | 1497.5 | 1604.5 | 66.8498 | 69.7192 | 62.2711 | 58.486 | 0.6685 | 0.69719 | 0.62271 | 0.58486 | 0.028694 | 0.037851 | 96.1309 | 112.8466 | 5.7558
38938.4167 | 1195 | 1188 | 38938.4168 | 1070 | 1032 | 1556.5 | 1663.5 | 72.9548 | 72.5275 | 65.3236 | 63.0037 | 0.72955 | 0.72527 | 0.65324 | 0.63004 | 0.0042735 | 0.023199 | 709.5203 | 970.6992 | 20.6031
38938.4174 | 961 | 895 | 38938.4174 | 935 | 869 | 1615.5 | 1722.5 | 58.6691 | 54.6398 | 57.0818 | 53.0525 | 0.58669 | 0.5464 | 0.57082 | 0.53053 | 0.040293 | 0.040293 | 3101.5455 | 3101.5455 | 27.8203
38938.4181 | 965 | 883 | 38938.4181 | 946 | 854 | 1674 | 1781 | 58.9133 | 53.9072 | 57.7534 | 52.1368 | 0.58913 | 0.53907 | 0.57753 | 0.52137 | 0.050061 | 0.056166 | 4050.4487 | 1645.639 | 28.2942
38938.4188 | 1056 | 1019 | 38938.4188 | 988 | 1019 | 1733 | 1840 | 64.4689 | 62.21 | 60.3175 | 62.21 | 0.64469 | 0.6221 | 0.60317 | 0.6221 | 0.022589 | 0.018926 | 1502.556 | 3055.644 | 3.6129
38938.4195 | 941 | 840 | 38938.4195 | 1065 | 997 | 1791.5 | 1898.5 | 57.4481 | 51.2821 | 65.0183 | 60.8669 | 0.57448 | 0.51282 | 0.65018 | 0.60867 | 0.061661 | 0.041514 | 802.0116 | 1861.0814 | 37.5107
38938.4202 | 1169 | 1133 | 38938.4202 | 1117 | 1169 | 1850.5 | 1957.5 | 71.3675 | 69.1697 | 68.1929 | 71.3675 | 0.71368 | 0.6917 | 0.68193 | 0.71368 | 0.021978 | 0.031746 | 1666.2021 | 5484.8252 | 16.381

## C1-7
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 7
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
38938.3977 | 1 | 0 | 38938.3977 | 1 | 0 | -92.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3983 | 1 | 0 | 38938.3984 | 1 | 0 | -33.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.399 | 1 | 0 | 38938.399 | 1 | 0 | 25 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3997 | 1 | 0 | 38938.3997 | 1 | 0 | 84 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4004 | 1 | 0 | 38938.4004 | 1 | 0 | 142.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4011 | 1 | 0 | 38938.4011 | 1 | 0 | 201.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4017 | 1 | 0 | 38938.4018 | 1 | 0 | 260.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4024 | 1 | 0 | 38938.4024 | 1 | 0 | 319 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4031 | 1 | 0 | 38938.4031 | 1 | 0 | 378 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4038 | 1 | 0 | 38938.4038 | 1 | 0 | 436.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4045 | 1 | 0 | 38938.4045 | 1 | 0 | 495.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4051 | 1 | 0 | 38938.4052 | 1 | 0 | 554 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4058 | 926 | 1028 | 38938.4058 | 1023 | 992 | 613 | 720 | 56.5324 | 62.7595 | 62.4542 | 60.5617 | 0.56532 | 0.62759 | 0.62454 | 0.60562 | 0.062271 | 0.018926 | 345.5877 | 425.7104 | 12.5264
38938.4065 | 1153 | 1130 | 38938.4065 | 1049 | 1144 | 671.5 | 778.5 | 70.3907 | 68.9866 | 64.0415 | 69.8413 | 0.70391 | 0.68987 | 0.64042 | 0.69841 | 0.014042 | 0.057998 | 327.2775 | 417.9996 | 12.1385
38938.4072 | 1193 | 1187 | 38938.4072 | 1193 | 1177 | 730.5 | 837.5 | 72.8327 | 72.4664 | 72.8327 | 71.8559 | 0.72833 | 0.72466 | 0.72833 | 0.71856 | 0.003663 | 0.009768 | 4087.4934 | 7190.3786 | 22.1835
38938.4079 | 919 | 1011 | 38938.4079 | 1018 | 991 | 789.5 | 896.5 | 56.105 | 61.7216 | 62.149 | 60.5006 | 0.56105 | 0.61722 | 0.62149 | 0.60501 | 0.056166 | 0.016484 | 416.0602 | 518.5081 | 15.176
38938.4086 | 1197 | 1180 | 38938.4086 | 1177 | 1180 | 848.5 | 955.5 | 73.0769 | 72.0391 | 71.8559 | 72.0391 | 0.73077 | 0.72039 | 0.71856 | 0.72039 | 0.010379 | 0.0018315 | 4324.0564 | 28200.8232 | 22.2921
38938.4092 | 1099 | 1074 | 38938.4092 | 1187 | 1169 | 907 | 1014 | 67.094 | 65.5678 | 72.4664 | 71.3675 | 0.67094 | 0.65568 | 0.72466 | 0.71368 | 0.015263 | 0.010989 | 8288.6788 | 8412.8371 | 5.5191
38938.4099 | 1191 | 1191 | 38938.4099 | 1035 | 1009 | 965.5 | 1072.5 | 72.7106 | 72.7106 | 63.1868 | 61.5995 | 0.72711 | 0.72711 | 0.63187 | 0.616 | 0 | 0.015873 | 670.9391 | 866.6715 | 20.2481
38938.4106 | 949 | 983 | 38938.4106 | 925 | 1002 | 1024.5 | 1131.5 | 57.9365 | 60.0122 | 56.4713 | 61.1722 | 0.57937 | 0.60012 | 0.56471 | 0.61172 | 0.020757 | 0.047009 | 1127.2861 | 1419.318 | 17.203
38938.4113 | 960 | 999 | 38938.4113 | 1061 | 1034 | 1083.5 | 1190.5 | 58.6081 | 60.989 | 64.7741 | 63.1258 | 0.58608 | 0.60989 | 0.64774 | 0.63126 | 0.02381 | 0.016484 | 1280.8546 | 1958.0715 | 14.6683
38938.4119 | 4 | 12 | 38938.412 | 1101 | 1156 | 1142 | 1249 | 0.2442 | 0.7326 | 67.2161 | 70.5739 | 0.002442 | 0.007326 | 0.67216 | 0.70574 | 0.004884 | 0.033578 | 28516.0408 | 1986.4507 | 16637.6119
38938.4126 | 996 | 970 | 38938.4127 | 961 | 943 | 1201 | 1308 | 60.8059 | 59.2186 | 58.6691 | 57.5702 | 0.60806 | 0.59219 | 0.58669 | 0.5757 | 0.015873 | 0.010989 | 2978.7375 | 8434.9444 | 14.9791
38938.4133 | 1098 | 1075 | 38938.4133 | 1023 | 997 | 1259.5 | 1366.5 | 67.033 | 65.6288 | 62.4542 | 60.8669 | 0.67033 | 0.65629 | 0.62454 | 0.60867 | 0.014042 | 0.015873 | 1202.1747 | 1749.9026 | 5.2779
38938.414 | 967 | 1089 | 38938.414 | 1013 | 987 | 1318.5 | 1425.5 | 59.0354 | 66.4835 | 61.8437 | 60.2564 | 0.59035 | 0.66484 | 0.61844 | 0.60256 | 0.074481 | 0.015873 | 175.4695 | 205.0398 | 3.5195
38938.4147 | 47 | 42 | 38938.4147 | 1184 | 1163 | 1377.5 | 1484.5 | 2.8694 | 2.5641 | 72.2833 | 71.0012 | 0.028694 | 0.025641 | 0.72283 | 0.71001 | 0.0030525 | 0.012821 | 49707.1005 | 4978.5925 | 4724.2049
38938.4153 | 1195 | 1092 | 38938.4154 | 1126 | 1167 | 1436 | 1543 | 72.9548 | 66.6667 | 68.7424 | 71.2454 | 0.72955 | 0.66667 | 0.68742 | 0.71245 | 0.062882 | 0.025031 | 647.3072 | 2812.8823 | 15.3853
38938.416 | 1030 | 957 | 38938.4161 | 1171 | 1130 | 1495 | 1602 | 62.8816 | 58.4249 | 71.4896 | 68.9866 | 0.62882 | 0.58425 | 0.7149 | 0.68987 | 0.044567 | 0.025031 | 207.1878 | 212.7972 | 8.9584
38938.4167 | 1192 | 1166 | 38938.4167 | 1095 | 1044 | 1553.5 | 1660.5 | 72.7717 | 71.1844 | 66.8498 | 63.7363 | 0.72772 | 0.71184 | 0.6685 | 0.63736 | 0.015873 | 0.031136 | 847.6018 | 1410.5656 | 19.6194
38938.4174 | 1158 | 1123 | 38938.4174 | 1187 | 1164 | 1612.5 | 1719.5 | 70.696 | 68.5592 | 72.4664 | 71.0623 | 0.70696 | 0.68559 | 0.72466 | 0.71062 | 0.021368 | 0.014042 | 6423.9388 | 5577.7906 | 14.6947
38938.4181 | 1151 | 1190 | 38938.4181 | 963 | 891 | 1671.5 | 1778.5 | 70.2686 | 72.6496 | 58.7912 | 54.3956 | 0.70269 | 0.7265 | 0.58791 | 0.54396 | 0.02381 | 0.043956 | 112.7924 | 146.2074 | 11.3767
38938.4187 | 950 | 1064 | 38938.4188 | 1198 | 1181 | 1730 | 1837 | 57.9976 | 64.9573 | 73.138 | 72.1001 | 0.57998 | 0.64957 | 0.73138 | 0.721 | 0.069597 | 0.010379 | 223.136 | 261.2866 | 6.7305
38938.4194 | 1019 | 937 | 38938.4195 | 1196 | 1032 | 1789 | 1896 | 62.21 | 57.2039 | 73.0159 | 63.0037 | 0.6221 | 0.57204 | 0.73016 | 0.63004 | 0.050061 | 0.10012 | 46.2 | 40.9885 | 4.8718
38938.4201 | 1148 | 1100 | 38938.4201 | 1162 | 1203 | 1847.5 | 1954.5 | 70.0855 | 67.1551 | 70.9402 | 73.4432 | 0.70085 | 0.67155 | 0.7094 | 0.73443 | 0.029304 | 0.025031 | 73875.4517 | 2355.7772 | 11.7712

## C1-6
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 6
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38938.3976 | 1 | 0 | 38938.3976 | 1 | 0 | -95.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3983 | 1 | 0 | 38938.3983 | 1 | 0 | -36.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.399 | 1 | 0 | 38938.399 | 1 | 0 | 22.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3997 | 1 | 0 | 38938.3997 | 1 | 0 | 81 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4003 | 1 | 0 | 38938.4004 | 1 | 0 | 140 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.401 | 1 | 0 | 38938.401 | 1 | 0 | 198.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4017 | 1 | 0 | 38938.4017 | 1 | 0 | 257.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4024 | 1 | 0 | 38938.4024 | 1 | 0 | 316.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4031 | 1 | 0 | 38938.4031 | 1 | 0 | 375 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4037 | 1 | 0 | 38938.4038 | 1 | 0 | 434 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4044 | 1 | 0 | 38938.4044 | 1 | 0 | 492.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4051 | 1 | 0 | 38938.4051 | 1 | 0 | 551.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4058 | 1083 | 1056 | 38938.4058 | 964 | 998 | 610 | 717 | 66.1172 | 64.4689 | 58.8523 | 60.928 | 0.66117 | 0.64469 | 0.58852 | 0.60928 | 0.016484 | 0.020757 | 2656.0115 | 8963.8098 | 2.4331
38938.4065 | 1173 | 1152 | 38938.4065 | 963 | 935 | 669 | 776 | 71.6117 | 70.3297 | 58.7912 | 57.0818 | 0.71612 | 0.7033 | 0.58791 | 0.57082 | 0.012821 | 0.017094 | 48.384 | 59.9427 | 6.8963
38938.4072 | 1191 | 1067 | 38938.4072 | 952 | 919 | 728 | 835 | 72.7106 | 65.1404 | 58.1197 | 56.105 | 0.72711 | 0.6514 | 0.5812 | 0.56105 | 0.075702 | 0.020147 | 82.6723 | 107.6396 | 7.0438
38938.4078 | 1095 | 1070 | 38938.4078 | 1187 | 1168 | 786.5 | 893.5 | 66.8498 | 65.3236 | 72.4664 | 71.3065 | 0.6685 | 0.65324 | 0.72466 | 0.71306 | 0.015263 | 0.0116 | 10886.4783 | 6837.5996 | 4.7879
38938.4085 | 1000 | 938 | 38938.4085 | 1169 | 1197 | 845.5 | 952.5 | 61.0501 | 57.265 | 71.3675 | 73.0769 | 0.6105 | 0.57265 | 0.71368 | 0.73077 | 0.037851 | 0.017094 | 223.3762 | 215.0037 | 12.7355
38938.4092 | 1132 | 1105 | 38938.4092 | 1167 | 1146 | 904.5 | 1011.5 | 69.1087 | 67.4603 | 71.2454 | 69.9634 | 0.69109 | 0.6746 | 0.71245 | 0.69963 | 0.016484 | 0.012821 | 14471.002 | 5464.6735 | 11.0183
38938.4099 | 1112 | 1088 | 38938.4099 | 1175 | 909 | 963 | 1070 | 67.8877 | 66.4225 | 71.7338 | 55.4945 | 0.67888 | 0.66422 | 0.71734 | 0.55495 | 0.014652 | 0.16239 | 18.7396 | 20.4599 | 1.3578
38938.4106 | 963 | 934 | 38938.4106 | 1012 | 984 | 1021.5 | 1128.5 | 58.7912 | 57.0208 | 61.7827 | 60.0733 | 0.58791 | 0.57021 | 0.61783 | 0.60073 | 0.017705 | 0.017094 | 6008.381 | 9472.8704 | 22.8869
38938.4112 | 936 | 970 | 38938.4112 | 1050 | 1024 | 1080.5 | 1187.5 | 57.1429 | 59.2186 | 64.1026 | 62.5153 | 0.57143 | 0.59219 | 0.64103 | 0.62515 | 0.020757 | 0.015873 | 2361.2868 | 6121.2062 | 20.9992
38938.4119 | 875 | 916 | 38938.4119 | 1095 | 1151 | 1139.5 | 1246.5 | 53.4188 | 55.9219 | 66.8498 | 70.2686 | 0.53419 | 0.55922 | 0.6685 | 0.70269 | 0.025031 | 0.034188 | 2155.5848 | 5574.1028 | 34.5355
38938.4126 | 925 | 943 | 38938.4126 | 925 | 934 | 1198 | 1305 | 56.4713 | 57.5702 | 56.4713 | 57.0208 | 0.56471 | 0.5757 | 0.56471 | 0.57021 | 0.010989 | 0.0054945 | 4114.2491 | 8670.672 | 25.6868
38938.4133 | 1195 | 1185 | 38938.4133 | 1194 | 1182 | 1257 | 1364 | 72.9548 | 72.3443 | 72.8938 | 72.1612 | 0.72955 | 0.72344 | 0.72894 | 0.72161 | 0.006105 | 0.007326 | 11073.8252 | 69298.2059 | 22.4975
38938.414 | 1091 | 1066 | 38938.414 | 1030 | 1004 | 1315.5 | 1422.5 | 66.6056 | 65.0794 | 62.8816 | 61.2943 | 0.66606 | 0.65079 | 0.62882 | 0.61294 | 0.015263 | 0.015873 | 5714.9259 | 14978.9504 | 4.0983
38938.4146 | 1202 | 1186 | 38938.4147 | 1192 | 1101 | 1374.5 | 1481.5 | 73.3822 | 72.4054 | 72.7717 | 67.2161 | 0.73382 | 0.72405 | 0.72772 | 0.67216 | 0.009768 | 0.055556 | 500.8262 | 714.8738 | 20.3402
38938.4153 | 1009 | 1024 | 38938.4153 | 1191 | 1195 | 1433.5 | 1540.5 | 61.5995 | 62.5153 | 72.7106 | 72.9548 | 0.616 | 0.62515 | 0.72711 | 0.72955 | 0.0091575 | 0.002442 | 2113.6751 | 2750.3041 | 7.5403
38938.416 | 1177 | 1175 | 38938.416 | 999 | 927 | 1492 | 1599 | 71.8559 | 71.7338 | 60.989 | 56.5934 | 0.71856 | 0.71734 | 0.60989 | 0.56593 | 0.001221 | 0.043956 | 56.427 | 70.9191 | 8.4391
38938.4167 | 990 | 1006 | 38938.4167 | 1162 | 1125 | 1551 | 1658 | 60.4396 | 61.4164 | 70.9402 | 68.6813 | 0.6044 | 0.61416 | 0.7094 | 0.68681 | 0.009768 | 0.022589 | 289.6321 | 270.6192 | 8.4936
38938.4174 | 925 | 1003 | 38938.4174 | 1021 | 962 | 1609.5 | 1716.5 | 56.4713 | 61.2332 | 62.3321 | 58.7302 | 0.56471 | 0.61233 | 0.62332 | 0.5873 | 0.047619 | 0.03602 | 1278.6478 | 6726.0309 | 18.1764
| 962 | 973 | 38938.4181 | 1077 | 1113 | 1669 | 1776 | 58.7302 | 59.4017 | 65.7509 | 67.9487 | 0.5873 | 0.59402 | 0.65751 | 0.67949 | 0.0067155 | 0.021978 | 463.4892 | 409.9637 | 14.7083
38938.4187 | 998 | 943 | 38938.4187 | 1020 | 960 | 1727.5 | 1834.5 | 60.928 | 57.5702 | 62.2711 | 58.6081 | 0.60928 | 0.5757 | 0.62271 | 0.58608 | 0.033578 | 0.03663 | 8864.5446 | 2222.9254 | 17.4565
38938.4194 | 1025 | 870 | 38938.4194 | 1029 | 945 | 1786 | 1893 | 62.5763 | 53.1136 | 62.8205 | 57.6923 | 0.62576 | 0.53114 | 0.62821 | 0.57692 | 0.094628 | 0.051282 | 376.3153 | 648.6508 | 21.7124
38938.4201 | 1027 | 957 | 38938.4201 | 1030 | 954 | 1844.5 | 1951.5 | 62.6984 | 58.4249 | 62.8816 | 58.2418 | 0.62698 | 0.58425 | 0.62882 | 0.58242 | 0.042735 | 0.046398 | 8547.2293 | 1670.3351 | 12.7202

## C1-5
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 5
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38938.3976 | 1 | 0 | 38938.3976 | 1 | 0 | -98 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3983 | 1 | 0 | 38938.3983 | 1 | 0 | -39.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.399 | 1 | 0 | 38938.399 | 1 | 0 | 19.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3996 | 1 | 0 | 38938.3997 | 1 | 0 | 78.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4003 | 1 | 0 | 38938.4003 | 1 | 0 | 137 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.401 | 1 | 0 | 38938.401 | 1 | 0 | 196 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4017 | 1 | 0 | 38938.4017 | 1 | 0 | 254.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4024 | 1 | 0 | 38938.4024 | 1 | 0 | 313.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.403 | 1 | 1 | 38938.4031 | 1 | 0 | 372.5 | 479.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38938.4037 | 1 | 0 | 38938.4037 | 1 | 0 | 431 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4044 | 1 | 0 | 38938.4044 | 1 | 0 | 490 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4051 | 1 | 0 | 38938.4051 | 1 | 0 | 548.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4058 | 3 | 15 | 38938.4058 | 3 | 11 | 607.5 | 714.5 | 0.18315 | 0.91575 | 0.18315 | 0.67155 | 0.0018315 | 0.0091575 | 0.0018315 | 0.0067155 | 0.007326 | 0.004884 | 17666.5754 | 26582.1404 | 13914.4549
38938.4064 | 1008 | 1049 | 38938.4065 | 1101 | 1075 | 666.5 | 773.5 | 61.5385 | 64.0415 | 67.2161 | 65.6288 | 0.61538 | 0.64042 | 0.67216 | 0.65629 | 0.025031 | 0.015873 | 65.9173 | 64.1444 | 2.0869
38938.4071 | 1023 | 1127 | 38938.4071 | 1072 | 1123 | 725 | 832 | 62.4542 | 68.8034 | 65.4457 | 68.5592 | 0.62454 | 0.68803 | 0.65446 | 0.68559 | 0.063492 | 0.031136 | 257.7097 | 353.3311 | 2.5575
38938.4078 | 3 | 17 | 38938.4078 | 3 | 16 | 784 | 891 | 0.18315 | 1.0379 | 0.18315 | 0.9768 | 0.0018315 | 0.010379 | 0.0018315 | 0.009768 | 0.008547 | 0.0079365 | 15184.2487 | 16363.559 | 12237.0997
38938.4085 | 4 | 17 | 38938.4085 | 3 | 16 | 842.5 | 949.5 | 0.2442 | 1.0379 | 0.18315 | 0.9768 | 0.002442 | 0.010379 | 0.0018315 | 0.009768 | 0.0079365 | 0.0079365 | 16354 | 16354 | 12231.2097
38938.4092 | 4 | 13 | 38938.4092 | 3 | 12 | 901.5 | 1008.5 | 0.2442 | 0.79365 | 0.18315 | 0.7326 | 0.002442 | 0.0079365 | 0.0018315 | 0.007326 | 0.0054945 | 0.0054945 | 23578 | 23578 | 16055.1371
38938.4098 | 3 | 18 | 38938.4099 | 3 | 18 | 960 | 1067 | 0.18315 | 1.0989 | 0.18315 | 1.0989 | 0.0018315 | 0.010989 | 0.0018315 | 0.010989 | 0.0091575 | 0.0091575 | 14186.8 | 14186.8 | 11540.9832
38938.4105 | 4 | 17 | 38938.4105 | 3 | 17 | 1019 | 1126 | 0.2442 | 1.0379 | 0.18315 | 1.0379 | 0.002442 | 0.010379 | 0.0018315 | 0.010379 | 0.0079365 | 0.008547 | 16364.1616 | 15184.2445 | 12225.4857
38938.4112 | 477 | 454 | 38938.4112 | 4 | 13 | 1077.5 | 1184.5 | 29.1209 | 27.7167 | 0.2442 | 0.79365 | 0.29121 | 0.27717 | 0.002442 | 0.0079365 | 0.014042 | 0.0054945 | 7754.1281 | 23878.3634 | 259.271
38938.4119 | 922 | 952 | 38938.4119 | 1187 | 913 | 1136.5 | 1243.5 | 56.2882 | 58.1197 | 72.4664 | 55.7387 | 0.56288 | 0.5812 | 0.72466 | 0.55739 | 0.018315 | 0.16728 | 100.2853 | 82.2369 | 11.3299
38938.4126 | 1187 | 1169 | 38938.4126 | 933 | 911 | 1195.5 | 1302.5 | 72.4664 | 71.3675 | 56.9597 | 55.6166 | 0.72466 | 0.71368 | 0.5696 | 0.55617 | 0.010989 | 0.013431 | 620.0391 | 889.9978 | 18.6858
38938.4132 | 1189 | 1167 | 38938.4133 | 963 | 937 | 1254 | 1361 | 72.5885 | 71.2454 | 58.7912 | 57.2039 | 0.72589 | 0.71245 | 0.58791 | 0.57204 | 0.013431 | 0.015873 | 611.6662 | 904.1882 | 18.7475
38938.4139 | 985 | 960 | 38938.4139 | 1022 | 998 | 1313 | 1420 | 60.1343 | 58.6081 | 62.3932 | 60.928 | 0.60134 | 0.58608 | 0.62393 | 0.60928 | 0.015263 | 0.014652 | 6436.3683 | 12844.0494 | 17.3669
38938.4146 | 933 | 915 | 38938.4146 | 1073 | 1031 | 1371.5 | 1478.5 | 56.9597 | 55.8608 | 65.5067 | 62.9426 | 0.5696 | 0.55861 | 0.65507 | 0.62943 | 0.010989 | 0.025641 | 1440.3074 | 1431.29 | 27.0725
38938.4153 | 935 | 892 | 38938.4153 | 977 | 970 | 1430.5 | 1537.5 | 57.0818 | 54.4567 | 59.6459 | 59.2186 | 0.57082 | 0.54457 | 0.59646 | 0.59219 | 0.026252 | 0.0042735 | 1110.2355 | 1413.5078 | 29.9464
38938.416 | 1194 | 1166 | 38938.416 | 1110 | 1157 | 1489.5 | 1596.5 | 72.8938 | 71.1844 | 67.7656 | 70.6349 | 0.72894 | 0.71184 | 0.67766 | 0.70635 | 0.017094 | 0.028694 | 1599.2047 | 3956.9266 | 20.6597
38938.4166 | 993 | 927 | 38938.4167 | 1190 | 879 | 1548 | 1655 | 60.6227 | 56.5934 | 72.6496 | 53.663 | 0.60623 | 0.56593 | 0.7265 | 0.53663 | 0.040293 | 0.18987 | 96.3014 | 84.5004 | 9.5364
38938.4173 | 1198 | 1184 | 38938.4173 | 1062 | 1014 | 1607 | 1714 | 73.138 | 72.2833 | 64.8352 | 61.9048 | 0.73138 | 0.72283 | 0.64835 | 0.61905 | 0.008547 | 0.029304 | 567.1524 | 803.6064 | 20.2038
38938.418 | 926 | 914 | 38938.418 | 1022 | 951 | 1665.5 | 1772.5 | 56.5324 | 55.7998 | 62.3932 | 58.0586 | 0.56532 | 0.558 | 0.62393 | 0.58059 | 0.007326 | 0.043346 | 822.0735 | 690.3667 | 26.0915
38938.4187 | 970 | 967 | 38938.4187 | 973 | 893 | 1724.5 | 1831.5 | 59.2186 | 59.0354 | 59.4017 | 54.5177 | 0.59219 | 0.59035 | 0.59402 | 0.54518 | 0.0018315 | 0.04884 | 594.4482 | 510.8766 | 15.2229
38938.4194 | 967 | 880 | 38938.4194 | 923 | 953 | 1783.5 | 1890.5 | 59.0354 | 53.7241 | 56.3492 | 58.1807 | 0.59035 | 0.53724 | 0.56349 | 0.58181 | 0.053114 | 0.018315 | 680.8439 | 1082.0985 | 27.6723
38938.42 | 1008 | 939 | 38938.4201 | 1112 | 1054 | 1842 | 1949 | 61.5385 | 57.326 | 67.8877 | 64.3468 | 0.61538 | 0.57326 | 0.67888 | 0.64347 | 0.042125 | 0.035409 | 797.0844 | 1348.5035 | 16.4599

## C1-4
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38938.3976 | 1 | 0 | 38938.3976 | 1 | 0 | -101 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3982 | 1 | 0 | 38938.3983 | 1 | 0 | -42 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3989 | 1 | 0 | 38938.3989 | 1 | 0 | 16.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3996 | 1 | 0 | 38938.3996 | 1 | 0 | 75.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4003 | 1 | 0 | 38938.4003 | 1 | 0 | 134.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.401 | 1 | 0 | 38938.401 | 1 | 0 | 193 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4016 | 1 | 0 | 38938.4017 | 1 | 0 | 252 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4023 | 1 | 0 | 38938.4023 | 1 | 0 | 310.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.403 | 1 | 0 | 38938.403 | 1 | 0 | 369.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4037 | 1 | 0 | 38938.4037 | 1 | 0 | 428.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4044 | 1 | 0 | 38938.4044 | 1 | 0 | 487 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.405 | 1 | 0 | 38938.4051 | 1 | 0 | 545.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4057 | 997 | 965 | 38938.4057 | 922 | 976 | 604.5 | 711.5 | 60.8669 | 58.9133 | 56.2882 | 59.5849 | 0.60867 | 0.58913 | 0.56288 | 0.59585 | 0.019536 | 0.032967 | 2767.3943 | 11588.1584 | 15.5158
38938.4064 | 1064 | 1038 | 38938.4064 | 1146 | 1123 | 663.5 | 770.5 | 64.9573 | 63.37 | 69.9634 | 68.5592 | 0.64957 | 0.6337 | 0.69963 | 0.68559 | 0.015873 | 0.014042 | 11923.3973 | 6034.1806 | 1.0443
38938.4071 | 1169 | 1174 | 38938.4071 | 931 | 935 | 722 | 829 | 71.3675 | 71.6728 | 56.8376 | 57.0818 | 0.71368 | 0.71673 | 0.56838 | 0.57082 | 0.0030525 | 0.002442 | 1495.801 | 2020.2599 | 18.6655
38938.4078 | 932 | 907 | 38938.4078 | 1055 | 1022 | 781 | 888 | 56.8987 | 55.3724 | 64.4078 | 62.3932 | 0.56899 | 0.55372 | 0.64408 | 0.62393 | 0.015263 | 0.020147 | 9268.4609 | 7399.4625 | 29.8088
38938.4084 | 971 | 945 | 38938.4085 | 928 | 957 | 840 | 947 | 59.2796 | 57.6923 | 56.6545 | 58.4249 | 0.5928 | 0.57692 | 0.56654 | 0.58425 | 0.015873 | 0.017705 | 13183.054 | 5450.7033 | 20.4731
38938.4091 | 1060 | 1111 | 38938.4091 | 996 | 970 | 898.5 | 1005.5 | 64.7131 | 67.8266 | 60.8059 | 59.2186 | 0.64713 | 0.67827 | 0.60806 | 0.59219 | 0.031136 | 0.015873 | 351.0232 | 446.21 | 4.2633
38938.4098 | 1121 | 1175 | 38938.4098 | 1169 | 1185 | 957.5 | 1064.5 | 68.4371 | 71.7338 | 71.3675 | 72.3443 | 0.68437 | 0.71734 | 0.71368 | 0.72344 | 0.032967 | 0.009768 | 1416.8106 | 7335.5766 | 15.3633
38938.4105 | 928 | 961 | 38938.4105 | 984 | 1100 | 1016 | 1123 | 56.6545 | 58.6691 | 60.0733 | 67.1551 | 0.56654 | 0.58669 | 0.60073 | 0.67155 | 0.020147 | 0.070818 | 378.3583 | 342.9688 | 18.0487
38938.4112 | 1013 | 985 | 38938.4112 | 942 | 1059 | 1075 | 1182 | 61.8437 | 60.1343 | 57.5092 | 64.652 | 0.61844 | 0.60134 | 0.57509 | 0.64652 | 0.017094 | 0.071429 | 297.1635 | 287.8658 | 8.6665
38938.4119 | 1149 | 1127 | 38938.4119 | 1163 | 1193 | 1133.5 | 1240.5 | 70.1465 | 68.8034 | 71.0012 | 72.8327 | 0.70147 | 0.68803 | 0.71001 | 0.72833 | 0.013431 | 0.018315 | 3320.5835 | 16027.545 | 14.3717
38938.4125 | 1078 | 1054 | 38938.4125 | 971 | 1013 | 1192.5 | 1299.5 | 65.812 | 64.3468 | 59.2796 | 61.8437 | 0.65812 | 0.64347 | 0.5928 | 0.61844 | 0.014652 | 0.025641 | 678.0237 | 819.2613 | 1.6049
38938.4132 | 1156 | 1125 | 38938.4132 | 922 | 1000 | 1251.5 | 1358.5 | 70.5739 | 68.6813 | 56.2882 | 61.0501 | 0.70574 | 0.68681 | 0.56288 | 0.6105 | 0.018926 | 0.047619 | 29.1765 | 34.625 | 3.8403
38938.4139 | 1092 | 1068 | 38938.4139 | 1121 | 1180 | 1310 | 1417 | 66.6667 | 65.2015 | 68.4371 | 72.0391 | 0.66667 | 0.65201 | 0.68437 | 0.72039 | 0.014652 | 0.03602 | 630.9835 | 774.9572 | 3.8961
38938.4146 | 944 | 957 | 38938.4146 | 1165 | 1196 | 1369 | 1476 | 57.6313 | 58.4249 | 71.1233 | 73.0159 | 0.57631 | 0.58425 | 0.71123 | 0.73016 | 0.0079365 | 0.018926 | 209.4113 | 175.5187 | 14.1136
38938.4153 | 1013 | 944 | 38938.4153 | 1184 | 1154 | 1427.5 | 1534.5 | 61.8437 | 57.6313 | 72.2833 | 70.4518 | 0.61844 | 0.57631 | 0.72283 | 0.70452 | 0.042125 | 0.018315 | 188.4598 | 183.4116 | 10.6959
38938.4159 | 972 | 888 | 38938.4159 | 1158 | 1195 | 1486.5 | 1593.5 | 59.3407 | 54.2125 | 70.696 | 72.9548 | 0.59341 | 0.54212 | 0.70696 | 0.72955 | 0.051282 | 0.022589 | 60.2481 | 49.0643 | 9.3785
38938.4166 | 1144 | 1190 | 38938.4166 | 952 | 884 | 1545.5 | 1652.5 | 69.8413 | 72.6496 | 58.1197 | 53.9683 | 0.69841 | 0.7265 | 0.5812 | 0.53968 | 0.028083 | 0.041514 | 265.6613 | 373.3243 | 14.6465
38938.4173 | 1002 | 956 | 38938.4173 | 1115 | 1068 | 1604 | 1711 | 61.1722 | 58.3639 | 68.0708 | 65.2015 | 0.61172 | 0.58364 | 0.68071 | 0.65201 | 0.028083 | 0.028694 | 8988.6767 | 2841.8733 | 15.6643
38938.418 | 973 | 916 | 38938.418 | 1191 | 1192 | 1663 | 1770 | 59.4017 | 55.9219 | 72.7106 | 72.7717 | 0.59402 | 0.55922 | 0.72711 | 0.72772 | 0.034799 | 0.0006105 | 78.9145 | 66.012 | 9.7247
38938.4187 | 1128 | 1183 | 38938.4187 | 1169 | 1192 | 1721.5 | 1828.5 | 68.8645 | 72.2222 | 71.3675 | 72.7717 | 0.68864 | 0.72222 | 0.71368 | 0.72772 | 0.033578 | 0.014042 | 1943.41 | 27416.8564 | 16.6746
38938.4193 | 997 | 919 | 38938.4194 | 1082 | 1016 | 1780.5 | 1887.5 | 60.8669 | 56.105 | 66.0562 | 62.0269 | 0.60867 | 0.56105 | 0.66056 | 0.62027 | 0.047619 | 0.040293 | 1097.5401 | 3880.2961 | 20.8999
38938.42 | 946 | 936 | 38938.42 | 1064 | 1004 | 1839 | 1946 | 57.7534 | 57.1429 | 64.9573 | 61.2943 | 0.57753 | 0.57143 | 0.64957 | 0.61294 | 0.006105 | 0.03663 | 622.9134 | 527.7739 | 20.75

## C1-3
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38938.3975 | 1 | 0 | 38938.3975 | 1 | 0 | -103.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3982 | 1 | 0 | 38938.3982 | 1 | 0 | -45 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3989 | 1 | 0 | 38938.3989 | 1 | 0 | 14 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3996 | 1 | 0 | 38938.3996 | 1 | 0 | 72.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4003 | 1 | 0 | 38938.4003 | 1 | 0 | 131.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4009 | 1 | 0 | 38938.4009 | 1 | 0 | 190.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4016 | 1 | 0 | 38938.4016 | 1 | 0 | 249 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4023 | 1 | 0 | 38938.4023 | 1 | 0 | 308 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.403 | 1 | 0 | 38938.403 | 1 | 0 | 366.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4037 | 1 | 0 | 38938.4037 | 1 | 0 | 425.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4043 | 1 | 0 | 38938.4044 | 1 | 0 | 484.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.405 | 1 | 0 | 38938.405 | 1 | 0 | 543 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4057 | 947 | 913 | 38938.4057 | 1001 | 969 | 601.5 | 708.5 | 57.8144 | 55.7387 | 61.1111 | 59.1575 | 0.57814 | 0.55739 | 0.61111 | 0.59158 | 0.020757 | 0.019536 | 4794.0871 | 9433.8109 | 27.4224
38938.4064 | 1161 | 1193 | 38938.4064 | 923 | 945 | 660.5 | 767.5 | 70.8791 | 72.8327 | 56.3492 | 57.6923 | 0.70879 | 0.72833 | 0.56349 | 0.57692 | 0.019536 | 0.013431 | 46.7935 | 59.5751 | 7.5412
38938.4071 | 961 | 925 | 38938.4071 | 1109 | 1079 | 719.5 | 826.5 | 58.6691 | 56.4713 | 67.7045 | 65.873 | 0.58669 | 0.56471 | 0.67705 | 0.65873 | 0.021978 | 0.018315 | 1888.9983 | 3702.1086 | 23.8972
38938.4077 | 963 | 936 | 38938.4078 | 1182 | 1159 | 778.5 | 885.5 | 58.7912 | 57.1429 | 72.1612 | 70.757 | 0.58791 | 0.57143 | 0.72161 | 0.70757 | 0.016484 | 0.014042 | 391.5285 | 350.9223 | 17.7946
38938.4084 | 948 | 948 | 38938.4084 | 1129 | 1186 | 837 | 944 | 57.8755 | 57.8755 | 68.9255 | 72.4054 | 0.57875 | 0.57875 | 0.68926 | 0.72405 | 0 | 0.034799 | 40.8524 | 33.2424 | 5.7114
38938.4091 | 1170 | 1150 | 38938.4091 | 964 | 938 | 895.5 | 1002.5 | 71.4286 | 70.2076 | 58.8523 | 57.265 | 0.71429 | 0.70208 | 0.58852 | 0.57265 | 0.01221 | 0.015873 | 70.074 | 86.7434 | 8.3603
38938.4098 | 924 | 949 | 38938.4098 | 1085 | 1168 | 954.5 | 1061.5 | 56.4103 | 57.9365 | 66.2393 | 71.3065 | 0.5641 | 0.57937 | 0.66239 | 0.71306 | 0.015263 | 0.050672 | 214.6445 | 179.4126 | 16.2401
38938.4105 | 950 | 924 | 38938.4105 | 1011 | 1055 | 1013.5 | 1120.5 | 57.9976 | 56.4103 | 61.7216 | 64.4078 | 0.57998 | 0.5641 | 0.61722 | 0.64408 | 0.015873 | 0.026862 | 2556.3528 | 4739.6076 | 25.3335
38938.4111 | 1183 | 1145 | 38938.4112 | 924 | 957 | 1072 | 1179 | 72.2222 | 69.9023 | 56.4103 | 58.4249 | 0.72222 | 0.69902 | 0.5641 | 0.58425 | 0.023199 | 0.020147 | 135.8165 | 177.0357 | 11.9982
38938.4118 | 959 | 933 | 38938.4118 | 1113 | 1179 | 1131 | 1238 | 58.547 | 56.9597 | 67.9487 | 71.978 | 0.58547 | 0.5696 | 0.67949 | 0.71978 | 0.015873 | 0.040293 | 151.8828 | 127.1447 | 13.2601
38938.4125 | 1054 | 1027 | 38938.4125 | 1025 | 998 | 1189.5 | 1296.5 | 64.3468 | 62.6984 | 62.5763 | 60.928 | 0.64347 | 0.62698 | 0.62576 | 0.60928 | 0.016484 | 0.016484 | 7726 | 7726 | 3.078
| 1077 | 1091 | 38938.4132 | 1144 | 1111 | 1249 | 1356 | 65.7509 | 66.6056 | 69.8413 | 67.8266 | 0.65751 | 0.66606 | 0.69841 | 0.67827 | 0.008547 | 0.020147 | 927.8402 | 1117.1489 | 4.6254
38938.4139 | 1100 | 1154 | 38938.4139 | 1124 | 1100 | 1307.5 | 1414.5 | 67.1551 | 70.4518 | 68.6203 | 67.1551 | 0.67155 | 0.70452 | 0.6862 | 0.67155 | 0.032967 | 0.014652 | 1040.419 | 2661.0376 | 11.7742
38938.4145 | 1183 | 886 | 38938.4146 | 1165 | 1135 | 1366 | 1473 | 72.2222 | 54.0904 | 71.1233 | 69.2918 | 0.72222 | 0.5409 | 0.71123 | 0.69292 | 0.18132 | 0.018315 | 48.6044 | 54.8115 | 1.7591
38938.4152 | 1200 | 1175 | 38938.4152 | 1075 | 1160 | 1425 | 1532 | 73.2601 | 71.7338 | 65.6288 | 70.8181 | 0.7326 | 0.71734 | 0.65629 | 0.70818 | 0.015263 | 0.051893 | 561.7447 | 854.341 | 19.9599
38938.4159 | 1142 | 1095 | 38938.4159 | 982 | 912 | 1483.5 | 1590.5 | 69.7192 | 66.8498 | 59.9512 | 55.6777 | 0.69719 | 0.6685 | 0.59951 | 0.55678 | 0.028694 | 0.042735 | 423.986 | 601.5765 | 9.7085
38938.4166 | 1011 | 955 | 38938.4166 | 1192 | 1194 | 1542.5 | 1649.5 | 61.7216 | 58.3028 | 72.7717 | 72.8938 | 0.61722 | 0.58303 | 0.72772 | 0.72894 | 0.034188 | 0.001221 | 252.2545 | 250.7428 | 11.0056
38938.4173 | 1018 | 1125 | 38938.4173 | 1123 | 907 | 1601.5 | 1708.5 | 62.149 | 68.6813 | 68.5592 | 55.3724 | 0.62149 | 0.68681 | 0.68559 | 0.55372 | 0.065324 | 0.13187 | 46.4855 | 50.0308 | 0.88866
38938.4179 | 1185 | 877 | 38938.418 | 1041 | 1070 | 1660 | 1767 | 72.3443 | 53.5409 | 63.5531 | 65.3236 | 0.72344 | 0.53541 | 0.63553 | 0.65324 | 0.18803 | 0.017705 | 18.5287 | 18.6574 | 0.91474
38938.4186 | 1171 | 1130 | 38938.4186 | 922 | 963 | 1719 | 1826 | 71.4896 | 68.9866 | 56.2882 | 58.7912 | 0.7149 | 0.68987 | 0.56288 | 0.58791 | 0.025031 | 0.025031 | 1350.0036 | 3926.4643 | 16.2222
38938.4193 | 936 | 840 | 38938.4193 | 1041 | 1050 | 1777.5 | 1884.5 | 57.1429 | 51.2821 | 63.5531 | 64.1026 | 0.57143 | 0.51282 | 0.63553 | 0.64103 | 0.058608 | 0.0054945 | 398.294 | 421.0203 | 32.4209
38938.42 | 984 | 911 | 38938.42 | 934 | 919 | 1836.5 | 1943.5 | 60.0733 | 55.6166 | 57.0208 | 56.105 | 0.60073 | 0.55617 | 0.57021 | 0.56105 | 0.044567 | 0.0091575 | 682.1886 | 984.8682 | 21.726

## C1-2
Penlight Test 30 |  |  | 2006-08-09 | 9:34 |  | Vs = |  | 129 |  | R = | 100
PE | 7-C | Air Drop
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38938.3975 | 1 | 0 | 38938.3975 | 1 | 0 | -106.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3982 | 1 | 0 | 38938.3982 | 1 | 0 | -47.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3989 | 1 | 0 | 38938.3989 | 1 | 0 | 11 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.3995 | 1 | 0 | 38938.3996 | 1 | 0 | 70 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4002 | 1 | 0 | 38938.4002 | 1 | 0 | 128.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4009 | 1 | 0 | 38938.4009 | 1 | 0 | 187.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4016 | 1 | 0 | 38938.4016 | 1 | 0 | 246.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4023 | 1 | 0 | 38938.4023 | 1 | 0 | 305 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4029 | 1 | 0 | 38938.403 | 1 | 0 | 364 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4036 | 1 | 0 | 38938.4036 | 1 | 0 | 422.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4043 | 1 | 0 | 38938.4043 | 1 | 0 | 481.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.405 | 1 | 0 | 38938.405 | 1 | 0 | 540.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38938.4057 | 967 | 1087 | 38938.4057 | 1036 | 1005 | 599 | 706 | 59.0354 | 66.3614 | 63.2479 | 61.3553 | 0.59035 | 0.66361 | 0.63248 | 0.61355 | 0.07326 | 0.018926 | 148.465 | 166.7401 | 3.3941
38938.4063 | 1177 | 1192 | 38938.4064 | 1164 | 1141 | 658 | 765 | 71.8559 | 72.7717 | 71.0623 | 69.6581 | 0.71856 | 0.72772 | 0.71062 | 0.69658 | 0.0091575 | 0.014042 | 3579.2507 | 10689.3526 | 21.2758
38938.407 | 964 | 936 | 38938.407 | 1099 | 1066 | 716.5 | 823.5 | 58.8523 | 57.1429 | 67.094 | 65.0794 | 0.58852 | 0.57143 | 0.67094 | 0.65079 | 0.017094 | 0.020147 | 6706.3628 | 8613.4556 | 22.4974
38938.4077 | 1039 | 1006 | 38938.4077 | 985 | 956 | 775.5 | 882.5 | 63.431 | 61.4164 | 60.1343 | 58.3639 | 0.63431 | 0.61416 | 0.60134 | 0.58364 | 0.020147 | 0.017705 | 3102.6033 | 62224.1145 | 6.7506
38938.4084 | 1122 | 1096 | 38938.4084 | 1067 | 1042 | 834 | 941 | 68.4982 | 66.9109 | 65.1404 | 63.6142 | 0.68498 | 0.66911 | 0.6514 | 0.63614 | 0.015873 | 0.015263 | 51801.2874 | 4550.1947 | 9.3725
38938.4091 | 1160 | 1192 | 38938.4091 | 1141 | 1117 | 893 | 1000 | 70.8181 | 72.7717 | 69.6581 | 68.1929 | 0.70818 | 0.72772 | 0.69658 | 0.68193 | 0.019536 | 0.014652 | 16226.188 | 4562.3904 | 19.6186
38938.4097 | 1118 | 1172 | 38938.4098 | 1163 | 1194 | 951.5 | 1058.5 | 68.254 | 71.5507 | 71.0012 | 72.8938 | 0.68254 | 0.71551 | 0.71001 | 0.72894 | 0.032967 | 0.018926 | 3033.4469 | 5528.7266 | 14.8324
38938.4104 | 1162 | 1190 | 38938.4104 | 1156 | 915 | 1010.5 | 1117.5 | 70.9402 | 72.6496 | 70.5739 | 55.8608 | 0.7094 | 0.7265 | 0.70574 | 0.55861 | 0.017094 | 0.14713 | 68.7344 | 87.7829 | 9.3879
38938.4111 | 817 | 991 | 38938.4111 | 289 | 331 | 1069.5 | 1176.5 | 49.8779 | 60.5006 | 17.6435 | 20.2076 | 0.49878 | 0.60501 | 0.17643 | 0.20208 | 0.10623 | 0.025641 | 738.3101 | 64405.0096 | 30.7313
38938.4118 | 974 | 949 | 38938.4118 | 1003 | 1047 | 1128 | 1235 | 59.4628 | 57.9365 | 61.2332 | 63.9194 | 0.59463 | 0.57937 | 0.61233 | 0.63919 | 0.015263 | 0.026862 | 1933.0405 | 2797.4498 | 19.3321
38938.4125 | 938 | 911 | 38938.4125 | 1195 | 1181 | 1187 | 1294 | 57.265 | 55.6166 | 72.9548 | 72.1001 | 0.57265 | 0.55617 | 0.72955 | 0.721 | 0.016484 | 0.008547 | 23.2774 | 18.1441 | 4.4508
38938.4131 | 1117 | 1080 | 38938.4132 | 1177 | 1156 | 1245.5 | 1352.5 | 68.1929 | 65.9341 | 71.8559 | 70.5739 | 0.68193 | 0.65934 | 0.71856 | 0.70574 | 0.022589 | 0.012821 | 2645.2961 | 165518.17 | 7.7712
38938.4138 | 930 | 909 | 38938.4138 | 1011 | 985 | 1304.5 | 1411.5 | 56.7766 | 55.4945 | 61.7216 | 60.1343 | 0.56777 | 0.55495 | 0.61722 | 0.60134 | 0.012821 | 0.015873 | 83068.2087 | 4643.4777 | 29.5097
38938.4145 | 925 | 942 | 38938.4145 | 1043 | 999 | 1363.5 | 1470.5 | 56.4713 | 57.5092 | 63.6752 | 60.989 | 0.56471 | 0.57509 | 0.63675 | 0.60989 | 0.010379 | 0.026862 | 1419.5201 | 1412.4704 | 24.39
38938.4152 | 1160 | 1194 | 38938.4152 | 1187 | 1197 | 1422 | 1529 | 70.8181 | 72.8938 | 72.4664 | 73.0769 | 0.70818 | 0.72894 | 0.72466 | 0.73077 | 0.020757 | 0.006105 | 2797.193 | 1691591.6935 | 20.1814
38938.4159 | 1105 | 1058 | 38938.4159 | 1034 | 976 | 1481 | 1588 | 67.4603 | 64.591 | 63.1258 | 59.5849 | 0.6746 | 0.64591 | 0.63126 | 0.59585 | 0.028694 | 0.035409 | 517.0463 | 715.0707 | 4.1444
38938.4166 | 1195 | 1174 | 38938.4166 | 940 | 875 | 1539.5 | 1646.5 | 72.9548 | 71.6728 | 57.3871 | 53.4188 | 0.72955 | 0.71673 | 0.57387 | 0.53419 | 0.012821 | 0.039683 | 95.9928 | 125.5156 | 12.1355
38938.4172 | 959 | 956 | 38938.4172 | 1131 | 1093 | 1598.5 | 1705.5 | 58.547 | 58.3639 | 69.0476 | 66.7277 | 0.58547 | 0.58364 | 0.69048 | 0.66728 | 0.0018315 | 0.023199 | 264.7022 | 220.8009 | 14.2566
38938.4179 | 1052 | 1004 | 38938.4179 | 1174 | 1145 | 1657.5 | 1764.5 | 64.2247 | 61.2943 | 71.6728 | 69.9023 | 0.64225 | 0.61294 | 0.71673 | 0.69902 | 0.029304 | 0.017705 | 960.4649 | 1607.1864 | 5.3466
38938.4186 | 1193 | 881 | 38938.4186 | 1150 | 1105 | 1716 | 1823 | 72.8327 | 53.7851 | 70.2076 | 67.4603 | 0.72833 | 0.53785 | 0.70208 | 0.6746 | 0.19048 | 0.027473 | 33.5512 | 36.2531 | 1.1784
38938.4193 | 998 | 863 | 38938.4193 | 1175 | 1190 | 1775 | 1882 | 60.928 | 52.6862 | 71.7338 | 72.6496 | 0.60928 | 0.52686 | 0.71734 | 0.7265 | 0.082418 | 0.0091575 | 16.6606 | 13.1604 | 3.3962
38938.42 | 988 | 928 | 38938.42 | 1112 | 1184 | 1833.5 | 1940.5 | 60.3175 | 56.6545 | 67.8877 | 72.2833 | 0.60317 | 0.56654 | 0.67888 | 0.72283 | 0.03663 | 0.043956 | 405.8672 | 427.2773 | 17.2041

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 30 |  |  | 2006-08-09 | 9:34
38938.3975 | 1 | 0 | 1 | PE | 7-C | Air Drop
38938.3982 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38938.3989 | 1 | 0 | 1
38938.3995 | 1 | 0 | 1
38938.4002 | 1 | 0 | 1
38938.4009 | 1 | 0 | 1
38938.4016 | 1 | 0 | 1
38938.4023 | 1 | 0 | 1
38938.4029 | 1 | 0 | 1
38938.4036 | 1 | 0 | 1
38938.4043 | 1 | 0 | 1
38938.405 | 1 | 0 | 1
38938.4057 | 967 | 1087 | 1
38938.4063 | 1177 | 1192 | 1
38938.407 | 964 | 936 | 1
38938.4077 | 1039 | 1006 | 1
38938.4084 | 1122 | 1096 | 1
38938.4091 | 1160 | 1192 | 1
38938.4097 | 1118 | 1172 | 1
38938.4104 | 1162 | 1190 | 1
38938.4111 | 817 | 991 | 1
38938.4118 | 974 | 949 | 1
38938.4125 | 938 | 911 | 1
38938.4131 | 1117 | 1080 | 1
38938.4138 | 930 | 909 | 1
38938.4145 | 925 | 942 | 1
38938.4152 | 1160 | 1194 | 1
38938.4159 | 1105 | 1058 | 1
38938.4166 | 1195 | 1174 | 1
38938.4172 | 959 | 956 | 1
38938.4179 | 1052 | 1004 | 1
38938.4186 | 1193 | 881 | 1
38938.4193 | 998 | 863 | 1
38938.42 | 988 | 928 | 1
1
38938.3975 | 1 | 0 | 2
38938.3982 | 1 | 0 | 2
38938.3989 | 1 | 0 | 2
38938.3996 | 1 | 0 | 2
38938.4002 | 1 | 0 | 2
38938.4009 | 1 | 0 | 2
38938.4016 | 1 | 0 | 2
38938.4023 | 1 | 0 | 2
38938.403 | 1 | 0 | 2
38938.4036 | 1 | 0 | 2
38938.4043 | 1 | 0 | 2
38938.405 | 1 | 0 | 2
38938.4057 | 1036 | 1005 | 2
38938.4064 | 1164 | 1141 | 2
38938.407 | 1099 | 1066 | 2
38938.4077 | 985 | 956 | 2
38938.4084 | 1067 | 1042 | 2
38938.4091 | 1141 | 1117 | 2
38938.4098 | 1163 | 1194 | 2
38938.4104 | 1156 | 915 | 2
38938.4111 | 289 | 331 | 2
38938.4118 | 1003 | 1047 | 2
38938.4125 | 1195 | 1181 | 2
38938.4132 | 1177 | 1156 | 2
38938.4138 | 1011 | 985 | 2
38938.4145 | 1043 | 999 | 2
38938.4152 | 1187 | 1197 | 2
38938.4159 | 1034 | 976 | 2
38938.4166 | 940 | 875 | 2
38938.4172 | 1131 | 1093 | 2
38938.4179 | 1174 | 1145 | 2
38938.4186 | 1150 | 1105 | 2
38938.4193 | 1175 | 1190 | 2
38938.42 | 1112 | 1184 | 2
2
38938.3975 | 1 | 0 | 3
38938.3982 | 1 | 0 | 3
38938.3989 | 1 | 0 | 3
38938.3996 | 1 | 0 | 3
38938.4003 | 1 | 0 | 3
38938.4009 | 1 | 0 | 3
38938.4016 | 1 | 0 | 3
38938.4023 | 1 | 0 | 3
38938.403 | 1 | 0 | 3
38938.4037 | 1 | 0 | 3
38938.4043 | 1 | 0 | 3
38938.405 | 1 | 0 | 3
38938.4057 | 947 | 913 | 3
38938.4064 | 1161 | 1193 | 3
38938.4071 | 961 | 925 | 3
38938.4077 | 963 | 936 | 3
38938.4084 | 948 | 948 | 3
38938.4091 | 1170 | 1150 | 3
38938.4098 | 924 | 949 | 3
38938.4105 | 950 | 924 | 3
38938.4111 | 1183 | 1145 | 3
38938.4118 | 959 | 933 | 3
38938.4125 | 1054 | 1027 | 3
38938.4139 | 1100 | 1154 | 3
38938.4145 | 1183 | 886 | 3
38938.4152 | 1200 | 1175 | 3
38938.4159 | 1142 | 1095 | 3
38938.4166 | 1011 | 955 | 3
38938.4173 | 1018 | 1125 | 3
38938.4179 | 1185 | 877 | 3
38938.4186 | 1171 | 1130 | 3
38938.4193 | 936 | 840 | 3
38938.42 | 984 | 911 | 3
3
38938.3975 | 1 | 0 | 4
38938.3982 | 1 | 0 | 4
38938.3989 | 1 | 0 | 4
38938.3996 | 1 | 0 | 4
38938.4003 | 1 | 0 | 4
38938.4009 | 1 | 0 | 4
38938.4016 | 1 | 0 | 4
38938.4023 | 1 | 0 | 4
38938.403 | 1 | 0 | 4
38938.4037 | 1 | 0 | 4
38938.4044 | 1 | 0 | 4
38938.405 | 1 | 0 | 4
38938.4057 | 1001 | 969 | 4
38938.4064 | 923 | 945 | 4
38938.4071 | 1109 | 1079 | 4
38938.4078 | 1182 | 1159 | 4
38938.4084 | 1129 | 1186 | 4
38938.4091 | 964 | 938 | 4
38938.4098 | 1085 | 1168 | 4
38938.4105 | 1011 | 1055 | 4
38938.4112 | 924 | 957 | 4
38938.4118 | 1113 | 1179 | 4
38938.4125 | 1025 | 998 | 4
38938.4132 | 1144 | 1111 | 4
38938.4139 | 1124 | 1100 | 4
38938.4146 | 1165 | 1135 | 4
38938.4152 | 1075 | 1160 | 4
38938.4159 | 982 | 912 | 4
38938.4166 | 1192 | 1194 | 4
38938.4173 | 1123 | 907 | 4
38938.418 | 1041 | 1070 | 4
38938.4186 | 922 | 963 | 4
38938.4193 | 1041 | 1050 | 4
38938.42 | 934 | 919 | 4
4
38938.3976 | 1 | 0 | 5
38938.3982 | 1 | 0 | 5
38938.3989 | 1 | 0 | 5
38938.3996 | 1 | 0 | 5
38938.4003 | 1 | 0 | 5
38938.401 | 1 | 0 | 5
38938.4016 | 1 | 0 | 5
38938.4023 | 1 | 0 | 5
38938.403 | 1 | 0 | 5
38938.4037 | 1 | 0 | 5
38938.4044 | 1 | 0 | 5
38938.405 | 1 | 0 | 5
38938.4057 | 997 | 965 | 5
38938.4064 | 1064 | 1038 | 5
38938.4071 | 1169 | 1174 | 5
38938.4078 | 932 | 907 | 5
38938.4084 | 971 | 945 | 5
38938.4091 | 1060 | 1111 | 5
38938.4098 | 1121 | 1175 | 5
38938.4105 | 928 | 961 | 5
38938.4112 | 1013 | 985 | 5
38938.4119 | 1149 | 1127 | 5
38938.4125 | 1078 | 1054 | 5
38938.4132 | 1156 | 1125 | 5
38938.4139 | 1092 | 1068 | 5
38938.4146 | 944 | 957 | 5
38938.4153 | 1013 | 944 | 5
38938.4159 | 972 | 888 | 5
38938.4166 | 1144 | 1190 | 5
38938.4173 | 1002 | 956 | 5
38938.418 | 973 | 916 | 5
38938.4187 | 1128 | 1183 | 5
38938.4193 | 997 | 919 | 5
38938.42 | 946 | 936 | 5
5
38938.3976 | 1 | 0 | 6
38938.3983 | 1 | 0 | 6
38938.3989 | 1 | 0 | 6
38938.3996 | 1 | 0 | 6
38938.4003 | 1 | 0 | 6
38938.401 | 1 | 0 | 6
38938.4017 | 1 | 0 | 6
38938.4023 | 1 | 0 | 6
38938.403 | 1 | 0 | 6
38938.4037 | 1 | 0 | 6
38938.4044 | 1 | 0 | 6
38938.4051 | 1 | 0 | 6
38938.4057 | 922 | 976 | 6
38938.4064 | 1146 | 1123 | 6
38938.4071 | 931 | 935 | 6
38938.4078 | 1055 | 1022 | 6
38938.4085 | 928 | 957 | 6
38938.4091 | 996 | 970 | 6
38938.4098 | 1169 | 1185 | 6
38938.4105 | 984 | 1100 | 6
38938.4112 | 942 | 1059 | 6
38938.4119 | 1163 | 1193 | 6
38938.4125 | 971 | 1013 | 6
38938.4132 | 922 | 1000 | 6
38938.4139 | 1121 | 1180 | 6
38938.4146 | 1165 | 1196 | 6
38938.4153 | 1184 | 1154 | 6
38938.4159 | 1158 | 1195 | 6
38938.4166 | 952 | 884 | 6
38938.4173 | 1115 | 1068 | 6
38938.418 | 1191 | 1192 | 6
38938.4187 | 1169 | 1192 | 6
38938.4194 | 1082 | 1016 | 6
38938.42 | 1064 | 1004 | 6
6
38938.3976 | 1 | 0 | 7
38938.3983 | 1 | 0 | 7
38938.399 | 1 | 0 | 7
38938.3996 | 1 | 0 | 7
38938.4003 | 1 | 0 | 7
38938.401 | 1 | 0 | 7
38938.4017 | 1 | 0 | 7
38938.4024 | 1 | 0 | 7
38938.403 | 1 | 1 | 7
38938.4037 | 1 | 0 | 7
38938.4044 | 1 | 0 | 7
38938.4051 | 1 | 0 | 7
38938.4058 | 3 | 15 | 7
38938.4064 | 1008 | 1049 | 7
38938.4071 | 1023 | 1127 | 7
38938.4078 | 3 | 17 | 7
38938.4085 | 4 | 17 | 7
38938.4092 | 4 | 13 | 7
38938.4098 | 3 | 18 | 7
38938.4105 | 4 | 17 | 7
38938.4112 | 477 | 454 | 7
38938.4119 | 922 | 952 | 7
38938.4126 | 1187 | 1169 | 7
38938.4132 | 1189 | 1167 | 7
38938.4139 | 985 | 960 | 7
38938.4146 | 933 | 915 | 7
38938.4153 | 935 | 892 | 7
38938.416 | 1194 | 1166 | 7
38938.4166 | 993 | 927 | 7
38938.4173 | 1198 | 1184 | 7
38938.418 | 926 | 914 | 7
38938.4187 | 970 | 967 | 7
38938.4194 | 967 | 880 | 7
38938.42 | 1008 | 939 | 7
7
38938.3976 | 1 | 0 | 8
38938.3983 | 1 | 0 | 8
38938.399 | 1 | 0 | 8
38938.3997 | 1 | 0 | 8
38938.4003 | 1 | 0 | 8
38938.401 | 1 | 0 | 8
38938.4017 | 1 | 0 | 8
38938.4024 | 1 | 0 | 8
38938.4031 | 1 | 0 | 8
38938.4037 | 1 | 0 | 8
38938.4044 | 1 | 0 | 8
38938.4051 | 1 | 0 | 8
38938.4058 | 3 | 11 | 8
38938.4065 | 1101 | 1075 | 8
38938.4071 | 1072 | 1123 | 8
38938.4078 | 3 | 16 | 8
38938.4085 | 3 | 16 | 8
38938.4092 | 3 | 12 | 8
38938.4099 | 3 | 18 | 8
38938.4105 | 3 | 17 | 8
38938.4112 | 4 | 13 | 8
38938.4119 | 1187 | 913 | 8
38938.4126 | 933 | 911 | 8
38938.4133 | 963 | 937 | 8
38938.4139 | 1022 | 998 | 8
38938.4146 | 1073 | 1031 | 8
38938.4153 | 977 | 970 | 8
38938.416 | 1110 | 1157 | 8
38938.4167 | 1190 | 879 | 8
38938.4173 | 1062 | 1014 | 8
38938.418 | 1022 | 951 | 8
38938.4187 | 973 | 893 | 8
38938.4194 | 923 | 953 | 8
38938.4201 | 1112 | 1054 | 8
8
38938.3976 | 1 | 0 | 9
38938.3983 | 1 | 0 | 9
38938.399 | 1 | 0 | 9
38938.3997 | 1 | 0 | 9
38938.4003 | 1 | 0 | 9
38938.401 | 1 | 0 | 9
38938.4017 | 1 | 0 | 9
38938.4024 | 1 | 0 | 9
38938.4031 | 1 | 0 | 9
38938.4037 | 1 | 0 | 9
38938.4044 | 1 | 0 | 9
38938.4051 | 1 | 0 | 9
38938.4058 | 1083 | 1056 | 9
38938.4065 | 1173 | 1152 | 9
38938.4072 | 1191 | 1067 | 9
38938.4078 | 1095 | 1070 | 9
38938.4085 | 1000 | 938 | 9
38938.4092 | 1132 | 1105 | 9
38938.4099 | 1112 | 1088 | 9
38938.4106 | 963 | 934 | 9
38938.4112 | 936 | 970 | 9
38938.4119 | 875 | 916 | 9
38938.4126 | 925 | 943 | 9
38938.4133 | 1195 | 1185 | 9
38938.414 | 1091 | 1066 | 9
38938.4146 | 1202 | 1186 | 9
38938.4153 | 1009 | 1024 | 9
38938.416 | 1177 | 1175 | 9
38938.4167 | 990 | 1006 | 9
38938.4174 | 925 | 1003 | 9
38938.4187 | 998 | 943 | 9
38938.4194 | 1025 | 870 | 9
38938.4201 | 1027 | 957 | 9
9
38938.3976 | 1 | 0 | 10
38938.3983 | 1 | 0 | 10
38938.399 | 1 | 0 | 10
38938.3997 | 1 | 0 | 10
38938.4004 | 1 | 0 | 10
38938.401 | 1 | 0 | 10
38938.4017 | 1 | 0 | 10
38938.4024 | 1 | 0 | 10
38938.4031 | 1 | 0 | 10
38938.4038 | 1 | 0 | 10
38938.4044 | 1 | 0 | 10
38938.4051 | 1 | 0 | 10
38938.4058 | 964 | 998 | 10
38938.4065 | 963 | 935 | 10
38938.4072 | 952 | 919 | 10
38938.4078 | 1187 | 1168 | 10
38938.4085 | 1169 | 1197 | 10
38938.4092 | 1167 | 1146 | 10
38938.4099 | 1175 | 909 | 10
38938.4106 | 1012 | 984 | 10
38938.4112 | 1050 | 1024 | 10
38938.4119 | 1095 | 1151 | 10
38938.4126 | 925 | 934 | 10
38938.4133 | 1194 | 1182 | 10
38938.414 | 1030 | 1004 | 10
38938.4147 | 1192 | 1101 | 10
38938.4153 | 1191 | 1195 | 10
38938.416 | 999 | 927 | 10
38938.4167 | 1162 | 1125 | 10
38938.4174 | 1021 | 962 | 10
38938.4181 | 1077 | 1113 | 10
38938.4187 | 1020 | 960 | 10
38938.4194 | 1029 | 945 | 10
38938.4201 | 1030 | 954 | 10
10
38938.3977 | 1 | 0 | 11
38938.3983 | 1 | 0 | 11
38938.399 | 1 | 0 | 11
38938.3997 | 1 | 0 | 11
38938.4004 | 1 | 0 | 11
38938.4011 | 1 | 0 | 11
38938.4017 | 1 | 0 | 11
38938.4024 | 1 | 0 | 11
38938.4031 | 1 | 0 | 11
38938.4038 | 1 | 0 | 11
38938.4045 | 1 | 0 | 11
38938.4051 | 1 | 0 | 11
38938.4058 | 926 | 1028 | 11
38938.4065 | 1153 | 1130 | 11
38938.4072 | 1193 | 1187 | 11
38938.4079 | 919 | 1011 | 11
38938.4086 | 1197 | 1180 | 11
38938.4092 | 1099 | 1074 | 11
38938.4099 | 1191 | 1191 | 11
38938.4106 | 949 | 983 | 11
38938.4113 | 960 | 999 | 11
38938.4119 | 4 | 12 | 11
38938.4126 | 996 | 970 | 11
38938.4133 | 1098 | 1075 | 11
38938.414 | 967 | 1089 | 11
38938.4147 | 47 | 42 | 11
38938.4153 | 1195 | 1092 | 11
38938.416 | 1030 | 957 | 11
38938.4167 | 1192 | 1166 | 11
38938.4174 | 1158 | 1123 | 11
38938.4181 | 1151 | 1190 | 11
38938.4187 | 950 | 1064 | 11
38938.4194 | 1019 | 937 | 11
38938.4201 | 1148 | 1100 | 11
11
38938.3977 | 1 | 0 | 12
38938.3984 | 1 | 0 | 12
38938.399 | 1 | 0 | 12
38938.3997 | 1 | 0 | 12
38938.4004 | 1 | 0 | 12
38938.4011 | 1 | 0 | 12
38938.4018 | 1 | 0 | 12
38938.4024 | 1 | 0 | 12
38938.4031 | 1 | 0 | 12
38938.4038 | 1 | 0 | 12
38938.4045 | 1 | 0 | 12
38938.4052 | 1 | 0 | 12
38938.4058 | 1023 | 992 | 12
38938.4065 | 1049 | 1144 | 12
38938.4072 | 1193 | 1177 | 12
38938.4079 | 1018 | 991 | 12
38938.4086 | 1177 | 1180 | 12
38938.4092 | 1187 | 1169 | 12
38938.4099 | 1035 | 1009 | 12
38938.4106 | 925 | 1002 | 12
38938.4113 | 1061 | 1034 | 12
38938.412 | 1101 | 1156 | 12
38938.4127 | 961 | 943 | 12
38938.4133 | 1023 | 997 | 12
38938.414 | 1013 | 987 | 12
38938.4147 | 1184 | 1163 | 12
38938.4154 | 1126 | 1167 | 12
38938.4161 | 1171 | 1130 | 12
38938.4167 | 1095 | 1044 | 12
38938.4174 | 1187 | 1164 | 12
38938.4181 | 963 | 891 | 12
38938.4188 | 1198 | 1181 | 12
38938.4195 | 1196 | 1032 | 12
38938.4201 | 1162 | 1203 | 12
12
38938.3977 | 1 | 0 | 13
38938.3984 | 1 | 0 | 13
38938.3991 | 1 | 0 | 13
38938.3997 | 1 | 0 | 13
38938.4004 | 1 | 0 | 13
38938.4011 | 1 | 0 | 13
38938.4018 | 1 | 0 | 13
38938.4025 | 1 | 0 | 13
38938.4031 | 1 | 0 | 13
38938.4038 | 1 | 0 | 13
38938.4045 | 1 | 0 | 13
38938.4052 | 1 | 0 | 13
38938.4059 | 1061 | 1033 | 13
38938.4065 | 961 | 997 | 13
38938.4072 | 1079 | 1050 | 13
38938.4079 | 1097 | 1072 | 13
38938.4086 | 1039 | 1012 | 13
38938.4093 | 1079 | 1053 | 13
38938.4099 | 1157 | 1194 | 13
38938.4106 | 1150 | 1128 | 13
38938.4113 | 1145 | 1123 | 13
38938.412 | 932 | 973 | 13
38938.4127 | 972 | 948 | 13
38938.4133 | 1071 | 1126 | 13
38938.414 | 959 | 932 | 13
38938.4147 | 981 | 1099 | 13
38938.4154 | 1034 | 976 | 13
38938.4161 | 1095 | 1142 | 13
38938.4167 | 1195 | 1188 | 13
38938.4174 | 961 | 895 | 13
38938.4181 | 965 | 883 | 13
38938.4188 | 1056 | 1019 | 13
38938.4195 | 941 | 840 | 13
38938.4202 | 1169 | 1133 | 13
13
38938.3977 | 1 | 0 | 14
38938.3984 | 1 | 0 | 14
38938.3991 | 1 | 0 | 14
38938.3997 | 1 | 0 | 14
38938.4004 | 1 | 0 | 14
38938.4011 | 1 | 0 | 14
38938.4018 | 1 | 0 | 14
38938.4025 | 1 | 0 | 14
38938.4031 | 1 | 0 | 14
38938.4038 | 1 | 0 | 14
38938.4045 | 1 | 0 | 14
38938.4052 | 1 | 0 | 14
38938.4059 | 1177 | 1193 | 14
38938.4066 | 1076 | 1051 | 14
38938.4072 | 1084 | 1137 | 14
38938.4079 | 1040 | 1015 | 14
38938.4086 | 1167 | 1146 | 14
38938.4093 | 1185 | 1166 | 14
38938.41 | 957 | 931 | 14
38938.4106 | 964 | 1086 | 14
38938.4113 | 1175 | 1156 | 14
38938.412 | 1057 | 1032 | 14
38938.4127 | 949 | 1067 | 14
38938.4134 | 964 | 1003 | 14
38938.414 | 1132 | 1108 | 14
38938.4147 | 1200 | 1194 | 14
38938.4154 | 958 | 1071 | 14
38938.4161 | 1020 | 958 | 14
38938.4168 | 1070 | 1032 | 14
38938.4174 | 935 | 869 | 14
38938.4181 | 946 | 854 | 14
38938.4188 | 988 | 1019 | 14
38938.4195 | 1065 | 997 | 14
38938.4202 | 1117 | 1169 | 14
14
38938.3977 | 1 | 0 | 15
38938.3984 | 1 | 0 | 15
38938.3991 | 1 | 0 | 15
38938.3998 | 1 | 0 | 15
38938.4005 | 1 | 0 | 15
38938.4011 | 1 | 0 | 15
38938.4018 | 1 | 0 | 15
38938.4025 | 1 | 0 | 15
38938.4032 | 1 | 0 | 15
38938.4039 | 1 | 0 | 15
38938.4045 | 1 | 0 | 15
38938.4052 | 1 | 0 | 15
38938.4059 | 1156 | 1132 | 15
38938.4066 | 986 | 957 | 15
38938.4073 | 1113 | 1086 | 15
38938.4079 | 1041 | 1089 | 15
38938.4086 | 1180 | 1197 | 15
38938.4093 | 1002 | 1117 | 15
38938.41 | 1006 | 979 | 15
38938.4106 | 1141 | 1192 | 15
38938.4113 | 932 | 965 | 15
38938.412 | 1190 | 1174 | 15
38938.4127 | 1157 | 1136 | 15
38938.4134 | 1088 | 1064 | 15
38938.4141 | 1145 | 920 | 15
38938.4147 | 956 | 929 | 15
38938.4154 | 998 | 1022 | 15
38938.4161 | 1110 | 1067 | 15
38938.4168 | 1173 | 1138 | 15
38938.4175 | 987 | 928 | 15
38938.4181 | 1157 | 1189 | 15
38938.4188 | 1132 | 1186 | 15
38938.4195 | 949 | 845 | 15
38938.4202 | 1206 | 1019 | 15
15
38938.3977 | 1 | 0 | 16
38938.3984 | 1 | 0 | 16
38938.3991 | 1 | 0 | 16
38938.3998 | 1 | 0 | 16
38938.4005 | 1 | 0 | 16
38938.4011 | 1 | 0 | 16
38938.4018 | 1 | 0 | 16
38938.4025 | 1 | 0 | 16
38938.4032 | 1 | 0 | 16
38938.4039 | 1 | 0 | 16
38938.4045 | 1 | 0 | 16
38938.4052 | 1 | 0 | 16
38938.4059 | 961 | 930 | 16
38938.4066 | 1048 | 1024 | 16
38938.4073 | 1147 | 1122 | 16
38938.408 | 1138 | 1189 | 16
38938.4086 | 959 | 932 | 16
38938.4093 | 1013 | 985 | 16
38938.41 | 978 | 952 | 16
38938.4107 | 1182 | 1195 | 16
38938.4114 | 1041 | 1017 | 16
38938.412 | 1035 | 1010 | 16
38938.4127 | 1163 | 1192 | 16
38938.4134 | 1118 | 1180 | 16
38938.4141 | 1010 | 984 | 16
38938.4148 | 1187 | 1200 | 16
38938.4154 | 1130 | 1089 | 16
38938.4161 | 961 | 903 | 16
38938.4168 | 1048 | 992 | 16
38938.4175 | 1070 | 1011 | 16
38938.4182 | 1092 | 1041 | 16
38938.4188 | 1032 | 984 | 16
38938.4195 | 999 | 926 | 16
38938.4202 | 1006 | 943 | 16
16
38938.3978 | 1 | 0 | 17
38938.3984 | 1 | 0 | 17
38938.3991 | 1 | 0 | 17
38938.3998 | 1 | 0 | 17
38938.4005 | 1 | 0 | 17
38938.4012 | 1 | 0 | 17
38938.4018 | 1 | 1 | 17
38938.4025 | 1 | 0 | 17
38938.4032 | 1 | 0 | 17
38938.4039 | 1 | 0 | 17
38938.4046 | 1 | 0 | 17
38938.4052 | 1 | 0 | 17
38938.4059 | 936 | 905 | 17
38938.4066 | 928 | 1034 | 17
38938.4073 | 3 | 17 | 17
38938.408 | 3 | 17 | 17
38938.4086 | 4 | 17 | 17
38938.4093 | 3 | 18 | 17
38938.41 | 4 | 16 | 17
38938.4107 | 4 | 17 | 17
38938.4114 | 1020 | 1006 | 17
38938.412 | 3 | 11 | 17
38938.4127 | 958 | 998 | 17
38938.4134 | 1177 | 1148 | 17
38938.4141 | 1035 | 1010 | 17
38938.4148 | 1045 | 1094 | 17
38938.4155 | 1200 | 1184 | 17
38938.4161 | 968 | 912 | 17
38938.4168 | 1176 | 1142 | 17
38938.4175 | 979 | 903 | 17
38938.4182 | 1198 | 1177 | 17
38938.4189 | 1099 | 1054 | 17
38938.4195 | 1142 | 1094 | 17
38938.4202 | 1199 | 1107 | 17
17
38938.3978 | 1 | 0 | 18
38938.3984 | 1 | 0 | 18
38938.3991 | 1 | 0 | 18
38938.3998 | 1 | 0 | 18
38938.4005 | 1 | 0 | 18
38938.4012 | 1 | 0 | 18
38938.4019 | 1 | 0 | 18
38938.4025 | 1 | 0 | 18
38938.4032 | 1 | 0 | 18
38938.4039 | 1 | 0 | 18
38938.4046 | 1 | 0 | 18
38938.4053 | 1 | 0 | 18
38938.4059 | 1011 | 980 | 18
38938.4066 | 1193 | 1027 | 18
38938.4073 | 3 | 17 | 18
38938.408 | 3 | 17 | 18
38938.4087 | 4 | 13 | 18
38938.4093 | 3 | 17 | 18
38938.41 | 3 | 12 | 18
38938.4107 | 3 | 17 | 18
38938.4114 | 1029 | 1075 | 18
38938.4121 | 25 | 41 | 18
38938.4127 | 1004 | 979 | 18
38938.4134 | 966 | 940 | 18
38938.4141 | 933 | 922 | 18
38938.4148 | 1027 | 1000 | 18
38938.4155 | 1044 | 1142 | 18
38938.4161 | 1197 | 1189 | 18
38938.4168 | 1095 | 895 | 18
38938.4175 | 983 | 910 | 18
38938.4182 | 1110 | 1059 | 18
38938.4189 | 1163 | 1122 | 18
38938.4195 | 988 | 911 | 18
38938.4202 | 983 | 918 | 18
18
38938.3978 | 1 | 0 | 19
38938.3985 | 1 | 0 | 19
38938.3992 | 1 | 0 | 19
38938.3998 | 1 | 0 | 19
38938.4005 | 1 | 0 | 19
38938.4012 | 1 | 0 | 19
38938.4019 | 1 | 0 | 19
38938.4026 | 1 | 0 | 19
38938.4032 | 1 | 0 | 19
38938.4039 | 1 | 0 | 19
38938.4046 | 1 | 0 | 19
38938.4053 | 1 | 0 | 19
38938.4059 | 1195 | 1180 | 19
38938.4066 | 1157 | 1127 | 19
38938.4073 | 1128 | 1101 | 19
38938.408 | 973 | 929 | 19
38938.4087 | 1010 | 982 | 19
38938.4094 | 925 | 956 | 19
38938.41 | 1080 | 1163 | 19
38938.4107 | 982 | 953 | 19
38938.4114 | 1091 | 1067 | 19
38938.4121 | 985 | 957 | 19
38938.4128 | 1159 | 1136 | 19
38938.4134 | 977 | 952 | 19
38938.4141 | 1054 | 936 | 19
38938.4148 | 1057 | 1153 | 19
38938.4155 | 970 | 872 | 19
38938.4162 | 969 | 907 | 19
38938.4168 | 1088 | 1045 | 19
38938.4175 | 1052 | 996 | 19
38938.4182 | 1015 | 934 | 19
38938.4189 | 1073 | 1013 | 19
38938.4196 | 1153 | 1190 | 19
38938.4202 | 1056 | 1007 | 19
19
38938.3978 | 1 | 0 | 20
38938.3985 | 1 | 0 | 20
38938.3992 | 1 | 0 | 20
38938.3998 | 1 | 0 | 20
38938.4005 | 1 | 0 | 20
38938.4012 | 1 | 0 | 20
38938.4019 | 1 | 0 | 20
38938.4026 | 1 | 0 | 20
38938.4033 | 1 | 0 | 20
38938.4039 | 1 | 0 | 20
38938.4046 | 1 | 0 | 20
38938.4053 | 1 | 0 | 20
38938.406 | 949 | 917 | 20
38938.4067 | 1009 | 958 | 20
38938.4073 | 1063 | 1031 | 20
38938.408 | 1048 | 1016 | 20
38938.4087 | 1106 | 1081 | 20
38938.4094 | 1170 | 1193 | 20
38938.4101 | 1156 | 1134 | 20
38938.4107 | 921 | 992 | 20
38938.4114 | 1066 | 1041 | 20
38938.4121 | 1098 | 1073 | 20
38938.4128 | 1186 | 1089 | 20
38938.4135 | 985 | 957 | 20
38938.4141 | 956 | 932 | 20
38938.4148 | 970 | 1009 | 20
38938.4155 | 1144 | 1185 | 20
38938.4162 | 1030 | 1071 | 20
38938.4169 | 993 | 937 | 20
38938.4175 | 924 | 906 | 20
38938.4182 | 1093 | 1037 | 20
38938.4189 | 1196 | 1176 | 20
38938.4196 | 1190 | 1161 | 20
38938.4203 | 1142 | 1105 | 20
20
38938.3978 | 1 | 0 | 21
38938.3985 | 1 | 0 | 21
38938.3992 | 1 | 0 | 21
38938.3999 | 1 | 0 | 21
38938.4005 | 1 | 0 | 21
38938.4012 | 1 | 0 | 21
38938.4019 | 1 | 0 | 21
38938.4026 | 1 | 0 | 21
38938.4033 | 1 | 0 | 21
38938.4039 | 1 | 0 | 21
38938.4046 | 1 | 0 | 21
38938.4053 | 1 | 0 | 21
38938.406 | 1174 | 1154 | 21
38938.4067 | 1170 | 1144 | 21
38938.4073 | 978 | 951 | 21
38938.408 | 1116 | 1088 | 21
38938.4087 | 964 | 1001 | 21
38938.4094 | 973 | 948 | 21
38938.4101 | 1189 | 1193 | 21
38938.4108 | 1191 | 1172 | 21
38938.4114 | 1020 | 995 | 21
38938.4121 | 440 | 367 | 21
38938.4128 | 1084 | 1060 | 21
38938.4135 | 1065 | 1037 | 21
38938.4142 | 1158 | 1196 | 21
38938.4148 | 856 | 835 | 21
38938.4155 | 970 | 899 | 21
38938.4162 | 936 | 904 | 21
38938.4169 | 955 | 876 | 21
38938.4176 | 1158 | 1193 | 21
38938.4182 | 1166 | 1122 | 21
38938.4189 | 959 | 1069 | 21
38938.4196 | 1024 | 947 | 21
38938.4203 | 1138 | 1185 | 21
21
38938.3978 | 1 | 0 | 22
38938.3985 | 1 | 0 | 22
38938.3992 | 1 | 0 | 22
38938.3999 | 1 | 0 | 22
38938.4006 | 1 | 0 | 22
38938.4012 | 1 | 1 | 22
38938.4019 | 1 | 0 | 22
38938.4026 | 1 | 0 | 22
38938.4033 | 1 | 0 | 22
38938.404 | 1 | 0 | 22
38938.4046 | 1 | 0 | 22
38938.4053 | 1 | 0 | 22
38938.406 | 935 | 905 | 22
38938.4067 | 998 | 945 | 22
38938.4074 | 1122 | 1095 | 22
38938.408 | 1110 | 1179 | 22
38938.4087 | 925 | 958 | 22
38938.4094 | 1085 | 1061 | 22
38938.4101 | 951 | 987 | 22
38938.4108 | 1167 | 1146 | 22
38938.4114 | 1020 | 1065 | 22
38938.4121 | 102 | 142 | 22
38938.4128 | 1185 | 1168 | 22
38938.4135 | 1151 | 1122 | 22
38938.4142 | 993 | 966 | 22
38938.4148 | 1077 | 930 | 22
38938.4155 | 1176 | 1135 | 22
38938.4162 | 987 | 1020 | 22
38938.4169 | 922 | 956 | 22
38938.4176 | 1147 | 1110 | 22
38938.4183 | 1056 | 990 | 22
38938.4189 | 938 | 890 | 22
38938.4196 | 1102 | 1042 | 22
38938.4203 | 1123 | 1072 | 22
22
38938.3979 | 1 | 0 | 23
38938.3985 | 1 | 0 | 23
38938.3992 | 1 | 0 | 23
38938.3999 | 1 | 0 | 23
38938.4006 | 1 | 0 | 23
38938.4013 | 1 | 0 | 23
38938.4019 | 1 | 0 | 23
38938.4026 | 1 | 0 | 23
38938.4033 | 1 | 0 | 23
38938.404 | 1 | 0 | 23
38938.4047 | 1 | 0 | 23
38938.4053 | 1 | 0 | 23
38938.406 | 1149 | 1190 | 23
38938.4067 | 923 | 927 | 23
38938.4074 | 1159 | 1138 | 23
38938.4081 | 1099 | 1067 | 23
38938.4087 | 1026 | 998 | 23
38938.4094 | 1105 | 1081 | 23
38938.4101 | 1178 | 1157 | 23
38938.4108 | 1095 | 1173 | 23
38938.4115 | 1155 | 1133 | 23
38938.4121 | 1109 | 1166 | 23
38938.4128 | 921 | 952 | 23
38938.4135 | 1121 | 1179 | 23
38938.4142 | 1034 | 1009 | 23
38938.4149 | 1008 | 979 | 23
38938.4155 | 1017 | 935 | 23
38938.4162 | 970 | 932 | 23
38938.4169 | 926 | 924 | 23
38938.4176 | 1197 | 1174 | 23
38938.4183 | 929 | 904 | 23
38938.4189 | 1197 | 1178 | 23
38938.4196 | 1136 | 1086 | 23
38938.4203 | 1191 | 1158 | 23
23
38938.3979 | 1 | 0 | 24
38938.3986 | 1 | 0 | 24
38938.3992 | 1 | 0 | 24
38938.3999 | 1 | 0 | 24
38938.4006 | 1 | 0 | 24
38938.4013 | 1 | 0 | 24
38938.402 | 1 | 0 | 24
38938.4026 | 1 | 0 | 24
38938.4033 | 1 | 0 | 24
38938.404 | 1 | 0 | 24
38938.4047 | 1 | 0 | 24
38938.4054 | 1 | 0 | 24
38938.406 | 1075 | 1047 | 24
38938.4067 | 932 | 1035 | 24
38938.4074 | 1122 | 918 | 24
38938.4081 | 1198 | 1057 | 24
38938.4088 | 1154 | 1131 | 24
38938.4094 | 1097 | 1173 | 24
38938.4101 | 1170 | 1147 | 24
38938.4108 | 996 | 1039 | 24
38938.4115 | 929 | 933 | 24
38938.4122 | 1077 | 1162 | 24
38938.4128 | 1111 | 1167 | 24
38938.4135 | 1002 | 954 | 24
38938.4142 | 1089 | 1065 | 24
38938.4149 | 1115 | 1088 | 24
38938.4156 | 1044 | 1068 | 24
38938.4162 | 1155 | 1198 | 24
38938.4169 | 987 | 990 | 24
38938.4176 | 965 | 893 | 24
38938.4183 | 1192 | 1192 | 24
38938.419 | 947 | 862 | 24
38938.4196 | 1150 | 1108 | 24
38938.4203 | 1105 | 1046 | 24
24
38938.3979 | 1 | 0 | 25
38938.3986 | 1 | 0 | 25
38938.3992 | 1 | 0 | 25
38938.3999 | 1 | 0 | 25
38938.4006 | 1 | 0 | 25
38938.4013 | 1 | 0 | 25
38938.402 | 1 | 0 | 25
38938.4027 | 1 | 0 | 25
38938.4033 | 1 | 0 | 25
38938.404 | 1 | 0 | 25
38938.4047 | 1 | 0 | 25
38938.4054 | 1 | 0 | 25
38938.4061 | 997 | 1038 | 25
38938.4067 | 1001 | 949 | 25
38938.4074 | 3 | 16 | 25
38938.4081 | 4 | 17 | 25
38938.4088 | 4 | 17 | 25
38938.4095 | 4 | 16 | 25
38938.4101 | 3 | 16 | 25
38938.4108 | 3 | 17 | 25
38938.4115 | 940 | 913 | 25
38938.4122 | 1003 | 1047 | 25
38938.4129 | 1040 | 1090 | 25
38938.4135 | 1105 | 1154 | 25
38938.4142 | 968 | 942 | 25
38938.4149 | 970 | 930 | 25
38938.4156 | 936 | 902 | 25
38938.4163 | 1130 | 1099 | 25
38938.4169 | 943 | 872 | 25
38938.4176 | 1038 | 971 | 25
38938.4183 | 936 | 909 | 25
38938.419 | 1163 | 1126 | 25
38938.4197 | 1063 | 992 | 25
38938.4203 | 1051 | 1080 | 25
25
38938.3986 | 1 | 0 | 26
38938.3993 | 1 | 0 | 26
38938.3999 | 1 | 0 | 26
38938.4006 | 1 | 0 | 26
38938.4013 | 1 | 0 | 26
38938.402 | 1 | 0 | 26
38938.4027 | 1 | 0 | 26
38938.4033 | 1 | 0 | 26
38938.404 | 1 | 0 | 26
38938.4047 | 1 | 0 | 26
38938.4054 | 1 | 0 | 26
38938.4061 | 1118 | 1092 | 26
38938.4067 | 1036 | 991 | 26
38938.4074 | 4 | 17 | 26
38938.4081 | 3 | 17 | 26
38938.4088 | 3 | 16 | 26
38938.4095 | 3 | 17 | 26
38938.4102 | 3 | 12 | 26
38938.4108 | 3 | 17 | 26
38938.4122 | 1032 | 1006 | 26
38938.4129 | 952 | 988 | 26
38938.4136 | 931 | 890 | 26
38938.4142 | 1058 | 1109 | 26
38938.4149 | 1025 | 986 | 26
38938.4156 | 1074 | 1019 | 26
38938.4163 | 1189 | 1168 | 26
38938.417 | 1170 | 1140 | 26
38938.4176 | 1065 | 1153 | 26
38938.4183 | 1168 | 1181 | 26
38938.419 | 1098 | 1042 | 26
38938.4197 | 1153 | 1109 | 26
38938.4204 | 1206 | 1181 | 26
26
38938.3979 | 1 | 0 | 27
38938.3986 | 1 | 0 | 27
38938.3993 | 1 | 0 | 27
38938.4 | 1 | 0 | 27
38938.4006 | 1 | 0 | 27
38938.4013 | 1 | 0 | 27
38938.402 | 1 | 0 | 27
38938.4027 | 1 | 0 | 27
38938.4034 | 1 | 0 | 27
38938.404 | 1 | 0 | 27
38938.4047 | 1 | 0 | 27
38938.4054 | 1 | 0 | 27
38938.4061 | 1186 | 1166 | 27
38938.4068 | 1164 | 1136 | 27
38938.4074 | 1048 | 1020 | 27
38938.4081 | 980 | 1013 | 27
38938.4088 | 1110 | 1085 | 27
38938.4095 | 1152 | 1195 | 27
38938.4102 | 961 | 995 | 27
38938.4108 | 933 | 1041 | 27
38938.4115 | 971 | 1093 | 27
38938.4122 | 955 | 992 | 27
38938.4129 | 1172 | 1193 | 27
38938.4136 | 936 | 887 | 27
38938.4142 | 976 | 1097 | 27
38938.4149 | 1174 | 1148 | 27
38938.4156 | 1072 | 1004 | 27
38938.4163 | 1017 | 980 | 27
38938.417 | 1010 | 1118 | 27
38938.4177 | 1161 | 1127 | 27
38938.4183 | 1187 | 1150 | 27
38938.419 | 1157 | 1111 | 27
38938.4197 | 1181 | 1191 | 27
38938.4204 | 1189 | 1204 | 27
27
38938.3979 | 1 | 0 | 28
38938.3986 | 1 | 0 | 28
38938.3993 | 1 | 1 | 28
38938.4 | 1 | 0 | 28
38938.4007 | 1 | 0 | 28
38938.4013 | 1 | 0 | 28
38938.402 | 1 | 0 | 28
38938.4027 | 1 | 0 | 28
38938.4034 | 1 | 0 | 28
38938.4041 | 1 | 0 | 28
38938.4047 | 1 | 0 | 28
38938.4054 | 1 | 0 | 28
38938.4061 | 1156 | 1194 | 28
38938.4068 | 1074 | 1033 | 28
38938.4075 | 1195 | 1187 | 28
38938.4081 | 1134 | 1187 | 28
38938.4088 | 1061 | 1035 | 28
38938.4095 | 1158 | 1193 | 28
38938.4102 | 1147 | 1125 | 28
38938.4109 | 1191 | 1195 | 28
38938.4115 | 1198 | 1186 | 28
38938.4122 | 1061 | 1036 | 28
38938.4129 | 937 | 971 | 28
38938.4136 | 1064 | 1025 | 28
38938.4143 | 931 | 935 | 28
38938.4149 | 1011 | 966 | 28
38938.4156 | 1168 | 1193 | 28
38938.4163 | 1173 | 1149 | 28
38938.417 | 1077 | 1127 | 28
38938.4177 | 1064 | 1010 | 28
38938.4183 | 1131 | 1187 | 28
38938.419 | 1090 | 1032 | 28
38938.4197 | 937 | 927 | 28
38938.4204 | 1116 | 1064 | 28
28
38938.398 | 1 | 0 | 29
38938.3986 | 1 | 0 | 29
38938.3993 | 1 | 0 | 29
38938.4 | 1 | 0 | 29
38938.4007 | 1 | 0 | 29
38938.4014 | 2 | 0 | 29
38938.402 | 1 | 0 | 29
38938.4027 | 1 | 0 | 29
38938.4034 | 1 | 0 | 29
38938.4041 | 1 | 0 | 29
38938.4048 | 1 | 0 | 29
38938.4054 | 1 | 1 | 29
38938.4061 | 1187 | 1170 | 29
38938.4068 | 1143 | 1109 | 29
38938.4075 | 1170 | 1171 | 29
38938.4082 | 1197 | 1178 | 29
38938.4088 | 1065 | 1041 | 29
38938.4095 | 1016 | 991 | 29
38938.4102 | 1013 | 1057 | 29
38938.4109 | 1149 | 1126 | 29
38938.4116 | 1069 | 1157 | 29
38938.4122 | 641 | 549 | 29
38938.4129 | 947 | 944 | 29
38938.4136 | 991 | 950 | 29
38938.4143 | 1200 | 1191 | 29
38938.415 | 1049 | 914 | 29
38938.4156 | 970 | 877 | 29
38938.4163 | 1198 | 1193 | 29
38938.417 | 990 | 999 | 29
38938.4177 | 1183 | 1193 | 29
38938.4184 | 1194 | 1166 | 29
38938.4191 | 1141 | 1098 | 29
38938.4197 | 1197 | 1183 | 29
38938.4204 | 1203 | 1178 | 29
29
38938.398 | 1 | 0 | 30
38938.3986 | 1 | 0 | 30
38938.3993 | 1 | 0 | 30
38938.4 | 1 | 0 | 30
38938.4007 | 1 | 0 | 30
38938.4014 | 1 | 0 | 30
38938.402 | 1 | 0 | 30
38938.4027 | 1 | 0 | 30
38938.4034 | 1 | 0 | 30
38938.4041 | 1 | 0 | 30
38938.4048 | 1 | 0 | 30
38938.4055 | 1 | 0 | 30
38938.4061 | 1069 | 1042 | 30
38938.4068 | 1118 | 1178 | 30
38938.4075 | 1122 | 1175 | 30
38938.4082 | 965 | 937 | 30
38938.4089 | 1038 | 1011 | 30
38938.4095 | 1156 | 1134 | 30
38938.4102 | 968 | 943 | 30
38938.4109 | 1044 | 1017 | 30
38938.4116 | 1130 | 1107 | 30
38938.4123 | 375 | 436 | 30
38938.4129 | 1067 | 1119 | 30
38938.4136 | 1055 | 1015 | 30
38938.4143 | 937 | 971 | 30
38938.415 | 952 | 904 | 30
38938.4157 | 954 | 945 | 30
38938.4163 | 1123 | 911 | 30
38938.417 | 986 | 916 | 30
38938.4177 | 994 | 1004 | 30
38938.4184 | 1198 | 918 | 30
38938.4197 | 1031 | 957 | 30
38938.4204 | 1035 | 893 | 30
30
38938.398 | 1 | 0 | 31
38938.3987 | 1 | 0 | 31
38938.3993 | 1 | 0 | 31
38938.4 | 1 | 0 | 31
38938.4007 | 1 | 0 | 31
38938.4014 | 1 | 0 | 31
38938.4021 | 1 | 0 | 31
38938.4027 | 1 | 0 | 31
38938.4034 | 1 | 0 | 31
38938.4041 | 1 | 0 | 31
38938.4048 | 1 | 0 | 31
38938.4055 | 1 | 0 | 31
38938.4061 | 964 | 998 | 31
38938.4068 | 1114 | 1076 | 31
38938.4075 | 4 | 18 | 31
38938.4082 | 4 | 17 | 31
38938.4089 | 3 | 18 | 31
38938.4095 | 4 | 17 | 31
38938.4102 | 4 | 17 | 31
38938.4109 | 3 | 13 | 31
38938.4116 | 1190 | 1194 | 31
38938.4123 | 1068 | 1042 | 31
38938.413 | 1187 | 1108 | 31
38938.4136 | 1115 | 1178 | 31
38938.4143 | 1179 | 1159 | 31
38938.415 | 1192 | 1103 | 31
38938.4157 | 1190 | 1119 | 31
38938.4164 | 1024 | 988 | 31
38938.417 | 1035 | 987 | 31
38938.4177 | 1166 | 1127 | 31
38938.4184 | 975 | 896 | 31
38938.4191 | 1192 | 1164 | 31
38938.4198 | 1059 | 1081 | 31
38938.4204 | 1073 | 1163 | 31
31
38938.398 | 1 | 0 | 32
38938.3987 | 1 | 0 | 32
38938.3994 | 1 | 0 | 32
38938.4 | 1 | 0 | 32
38938.4007 | 1 | 0 | 32
38938.4014 | 1 | 0 | 32
38938.4021 | 1 | 0 | 32
38938.4034 | 1 | 0 | 32
38938.4041 | 1 | 0 | 32
38938.4048 | 1 | 0 | 32
38938.4055 | 1 | 0 | 32
38938.4062 | 1091 | 1064 | 32
38938.4069 | 1174 | 1190 | 32
38938.4075 | 4 | 17 | 32
38938.4082 | 3 | 16 | 32
38938.4089 | 4 | 12 | 32
38938.4096 | 3 | 12 | 32
38938.4102 | 3 | 15 | 32
38938.4109 | 24 | 31 | 32
38938.4116 | 945 | 918 | 32
38938.4123 | 1197 | 1187 | 32
38938.413 | 1092 | 1054 | 32
38938.4136 | 1059 | 1025 | 32
38938.4143 | 1131 | 1108 | 32
38938.415 | 1124 | 1174 | 32
38938.4157 | 1127 | 1082 | 32
38938.4164 | 1172 | 900 | 32
38938.417 | 952 | 889 | 32
38938.4177 | 1060 | 1005 | 32
38938.4184 | 941 | 849 | 32
38938.4191 | 1095 | 1041 | 32
38938.4198 | 925 | 907 | 32
38938.4205 | 983 | 905 | 32
32
38938.398 | 1 | 0 | 33
38938.3987 | 1 | 0 | 33
38938.3994 | 1 | 0 | 33
38938.4001 | 1 | 0 | 33
38938.4007 | 1 | 0 | 33
38938.4014 | 1 | 0 | 33
38938.4021 | 1 | 0 | 33
38938.4028 | 1 | 0 | 33
38938.4035 | 1 | 0 | 33
38938.4041 | 1 | 0 | 33
38938.4048 | 1 | 0 | 33
38938.4055 | 1 | 0 | 33
38938.4062 | 1009 | 980 | 33
38938.4069 | 1051 | 1145 | 33
38938.4075 | 1048 | 1006 | 33
38938.4082 | 1149 | 1122 | 33
38938.4089 | 950 | 921 | 33
38938.4096 | 1043 | 1016 | 33
38938.4103 | 1073 | 1048 | 33
38938.4109 | 936 | 970 | 33
38938.4116 | 1176 | 1156 | 33
38938.4123 | 1091 | 1066 | 33
38938.413 | 986 | 931 | 33
38938.4137 | 999 | 1036 | 33
38938.4144 | 1144 | 1120 | 33
38938.415 | 1198 | 1195 | 33
38938.4157 | 912 | 980 | 33
38938.4164 | 1192 | 1172 | 33
38938.4171 | 1199 | 1188 | 33
38938.4178 | 1135 | 1085 | 33
38938.4184 | 928 | 901 | 33
38938.4191 | 1172 | 1178 | 33
38938.4198 | 1064 | 1091 | 33
38938.4205 | 962 | 890 | 33
33
38938.398 | 1 | 0 | 34
38938.3987 | 1 | 0 | 34
38938.3994 | 1 | 0 | 34
38938.4001 | 1 | 0 | 34
38938.4008 | 1 | 0 | 34
38938.4014 | 1 | 0 | 34
38938.4021 | 1 | 0 | 34
38938.4028 | 1 | 0 | 34
38938.4035 | 1 | 0 | 34
38938.4042 | 1 | 0 | 34
38938.4048 | 1 | 0 | 34
38938.4055 | 1076 | 1131 | 34
38938.4062 | 994 | 962 | 34
38938.4069 | 996 | 948 | 34
38938.4076 | 1181 | 1156 | 34
38938.4082 | 1196 | 1178 | 34
38938.4089 | 1192 | 1085 | 34
38938.4096 | 1194 | 1190 | 34
38938.4103 | 1197 | 983 | 34
38938.411 | 1188 | 912 | 34
38938.4116 | 945 | 917 | 34
38938.4123 | 1146 | 1123 | 34
38938.413 | 1152 | 1117 | 34
38938.4137 | 963 | 946 | 34
38938.4144 | 1053 | 1151 | 34
38938.415 | 1106 | 904 | 34
38938.4157 | 1024 | 945 | 34
38938.4164 | 949 | 911 | 34
38938.4171 | 995 | 916 | 34
38938.4178 | 1198 | 1185 | 34
38938.4184 | 1195 | 1170 | 34
38938.4191 | 1049 | 993 | 34
38938.4198 | 971 | 888 | 34
38938.4205 | 938 | 911 | 34
34
38938.398 | 1 | 0 | 35
38938.3987 | 1 | 0 | 35
38938.3994 | 1 | 0 | 35
38938.4001 | 1 | 0 | 35
38938.4008 | 1 | 0 | 35
38938.4014 | 1 | 0 | 35
38938.4021 | 1 | 0 | 35
38938.4028 | 1 | 0 | 35
38938.4035 | 1 | 0 | 35
38938.4042 | 1 | 0 | 35
38938.4048 | 1 | 0 | 35
38938.4055 | 2 | 2 | 35
38938.4062 | 1192 | 1190 | 35
38938.4069 | 1019 | 1054 | 35
38938.4076 | 1185 | 897 | 35
38938.4083 | 966 | 929 | 35
38938.4089 | 1034 | 1008 | 35
38938.4096 | 929 | 962 | 35
38938.4103 | 1051 | 1146 | 35
38938.411 | 937 | 970 | 35
38938.4117 | 478 | 434 | 35
38938.4123 | 441 | 380 | 35
38938.413 | 988 | 931 | 35
38938.4137 | 1191 | 1176 | 35
38938.4144 | 1098 | 1155 | 35
38938.4151 | 1198 | 1176 | 35
38938.4157 | 996 | 1037 | 35
38938.4164 | 1177 | 1155 | 35
38938.4171 | 1087 | 1124 | 35
38938.4178 | 1100 | 1148 | 35
38938.4185 | 928 | 902 | 35
38938.4191 | 1164 | 1128 | 35
38938.4198 | 961 | 891 | 35
38938.4205 | 1003 | 1110 | 35
35
38938.3981 | 1 | 0 | 36
38938.3988 | 1 | 0 | 36
38938.3994 | 1 | 0 | 36
38938.4001 | 1 | 0 | 36
38938.4008 | 1 | 0 | 36
38938.4015 | 1 | 0 | 36
38938.4022 | 1 | 0 | 36
38938.4028 | 1 | 0 | 36
38938.4035 | 1 | 0 | 36
38938.4042 | 1 | 0 | 36
38938.4049 | 1 | 0 | 36
38938.4056 | 1 | 1 | 36
38938.4062 | 1141 | 1117 | 36
38938.4069 | 1058 | 1021 | 36
38938.4076 | 1171 | 1147 | 36
38938.4083 | 1198 | 930 | 36
38938.4089 | 936 | 910 | 36
38938.4096 | 968 | 1006 | 36
38938.4103 | 967 | 941 | 36
38938.411 | 1185 | 1132 | 36
38938.4123 | 266 | 354 | 36
38938.413 | 945 | 878 | 36
38938.4137 | 1023 | 1070 | 36
38938.4144 | 1185 | 1147 | 36
38938.4151 | 1051 | 1009 | 36
38938.4164 | 1000 | 1113 | 36
38938.4171 | 1097 | 1039 | 36
38938.4178 | 1158 | 1194 | 36
38938.4185 | 961 | 878 | 36
38938.4192 | 934 | 880 | 36
38938.4198 | 936 | 926 | 36
38938.4205 | 948 | 932 | 36
36
38938.3981 | 1 | 0 | 37
38938.3988 | 1 | 0 | 37
38938.3994 | 1 | 0 | 37
38938.4001 | 1 | 0 | 37
38938.4008 | 1 | 0 | 37
38938.4015 | 1 | 1 | 37
38938.4022 | 1 | 0 | 37
38938.4028 | 1 | 0 | 37
38938.4035 | 1 | 0 | 37
38938.4042 | 1 | 0 | 37
38938.4049 | 1 | 0 | 37
38938.4056 | 1 | 0 | 37
38938.4062 | 1095 | 1069 | 37
38938.4069 | 1183 | 1189 | 37
38938.4076 | 4 | 18 | 37
38938.4083 | 3 | 17 | 37
38938.409 | 3 | 18 | 37
38938.4097 | 3 | 16 | 37
38938.4103 | 3 | 12 | 37
38938.411 | 68 | 86 | 37
38938.4117 | 840 | 824 | 37
38938.4124 | 1053 | 1104 | 37
38938.4131 | 1132 | 1092 | 37
38938.4137 | 1179 | 1193 | 37
38938.4144 | 944 | 917 | 37
38938.4151 | 1020 | 967 | 37
38938.4158 | 1084 | 1034 | 37
38938.4165 | 967 | 993 | 37
38938.4171 | 1186 | 1128 | 37
38938.4178 | 1138 | 1103 | 37
38938.4185 | 942 | 859 | 37
38938.4192 | 1076 | 1038 | 37
38938.4199 | 1188 | 868 | 37
38938.4205 | 1080 | 1017 | 37
37
38938.3981 | 1 | 0 | 38
38938.3988 | 1 | 0 | 38
38938.3995 | 1 | 0 | 38
38938.4001 | 1 | 0 | 38
38938.4008 | 1 | 0 | 38
38938.4015 | 1 | 0 | 38
38938.4022 | 1 | 0 | 38
38938.4029 | 1 | 0 | 38
38938.4035 | 1 | 0 | 38
38938.4042 | 1 | 0 | 38
38938.4049 | 1 | 0 | 38
38938.4056 | 1 | 1 | 38
38938.4063 | 1183 | 1193 | 38
38938.4069 | 1077 | 1127 | 38
38938.4076 | 3 | 17 | 38
38938.4083 | 3 | 15 | 38
38938.409 | 3 | 16 | 38
38938.4097 | 3 | 11 | 38
38938.4103 | 3 | 11 | 38
38938.411 | 36 | 32 | 38
38938.4117 | 617 | 565 | 38
38938.4124 | 1093 | 1170 | 38
38938.4131 | 1045 | 1139 | 38
38938.4137 | 1192 | 1176 | 38
38938.4144 | 966 | 940 | 38
38938.4151 | 1099 | 1064 | 38
38938.4158 | 943 | 942 | 38
38938.4165 | 1199 | 1185 | 38
38938.4172 | 957 | 875 | 38
38938.4178 | 1024 | 983 | 38
38938.4185 | 1176 | 1190 | 38
38938.4192 | 1091 | 1048 | 38
38938.4199 | 1042 | 986 | 38
38938.4206 | 1052 | 988 | 38
38
38938.3981 | 1 | 0 | 39
38938.3988 | 1 | 0 | 39
38938.3995 | 1 | 0 | 39
38938.4002 | 1 | 0 | 39
38938.4008 | 1 | 0 | 39
38938.4015 | 1 | 0 | 39
38938.4022 | 1 | 0 | 39
38938.4029 | 1 | 0 | 39
38938.4036 | 1 | 0 | 39
38938.4042 | 1 | 0 | 39
38938.4049 | 1 | 0 | 39
38938.4056 | 1 | 1 | 39
38938.4063 | 1130 | 1106 | 39
38938.407 | 1191 | 1172 | 39
38938.4076 | 3 | 16 | 39
38938.409 | 3 | 11 | 39
38938.4097 | 2 | 11 | 39
38938.4104 | 3 | 10 | 39
38938.411 | 3 | 12 | 39
38938.4117 | 993 | 1046 | 39
38938.4124 | 123 | 115 | 39
38938.4131 | 1146 | 1113 | 39
38938.4138 | 949 | 924 | 39
38938.4144 | 927 | 1023 | 39
38938.4151 | 924 | 930 | 39
38938.4158 | 1101 | 1048 | 39
38938.4165 | 973 | 931 | 39
38938.4172 | 1003 | 939 | 39
38938.4178 | 1171 | 1139 | 39
38938.4185 | 1054 | 985 | 39
38938.4192 | 1021 | 956 | 39
38938.4199 | 1017 | 1022 | 39
38938.4206 | 1060 | 884 | 39
39
38938.3981 | 1 | 0 | 40
38938.3988 | 1 | 0 | 40
38938.3995 | 1 | 0 | 40
38938.4002 | 1 | 0 | 40
38938.4009 | 1 | 0 | 40
38938.4015 | 1 | 0 | 40
38938.4022 | 1 | 0 | 40
38938.4029 | 1 | 0 | 40
38938.4036 | 1 | 0 | 40
38938.4043 | 1 | 0 | 40
38938.4049 | 1 | 0 | 40
38938.4056 | 1 | 0 | 40
38938.4063 | 1113 | 1088 | 40
38938.407 | 1081 | 1052 | 40
38938.4077 | 3 | 14 | 40
38938.4083 | 3 | 11 | 40
38938.409 | 3 | 10 | 40
38938.4097 | 3 | 11 | 40
38938.4104 | 3 | 10 | 40
38938.4111 | 4 | 11 | 40
38938.4117 | 826 | 806 | 40
38938.4124 | 207 | 240 | 40
38938.4131 | 1038 | 989 | 40
38938.4138 | 1069 | 1045 | 40
38938.4145 | 957 | 950 | 40
38938.4151 | 1046 | 1060 | 40
38938.4158 | 952 | 881 | 40
38938.4165 | 1168 | 1140 | 40
38938.4172 | 1045 | 980 | 40
38938.4179 | 1017 | 972 | 40
38938.4185 | 1146 | 1095 | 40
38938.4192 | 1046 | 1071 | 40
38938.4199 | 972 | 892 | 40
38938.4206 | 1062 | 1004 | 40
40
38938.3981 | 1 | 0 | 41
38938.3988 | 1 | 0 | 41
38938.3995 | 1 | 0 | 41
38938.4002 | 1 | 0 | 41
38938.4009 | 1 | 0 | 41
38938.4016 | 1 | 0 | 41
38938.4022 | 1 | 0 | 41
38938.4029 | 1 | 0 | 41
38938.4036 | 1 | 0 | 41
38938.4043 | 1 | 0 | 41
38938.405 | 1 | 0 | 41
38938.4056 | 1 | 0 | 41
38938.4063 | 1134 | 1185 | 41
38938.407 | 1183 | 1120 | 41
38938.4077 | 995 | 951 | 41
38938.4084 | 986 | 955 | 41
38938.409 | 1192 | 1191 | 41
38938.4097 | 942 | 911 | 41
38938.4104 | 1020 | 1063 | 41
38938.4111 | 1165 | 1195 | 41
38938.4118 | 652 | 644 | 41
38938.4124 | 275 | 222 | 41
38938.4131 | 958 | 903 | 41
38938.4138 | 922 | 1020 | 41
38938.4145 | 1059 | 1035 | 41
38938.4152 | 986 | 984 | 41
38938.4158 | 956 | 860 | 41
38938.4165 | 1141 | 884 | 41
38938.4172 | 1034 | 1049 | 41
38938.4179 | 1048 | 985 | 41
38938.4186 | 1137 | 1082 | 41
38938.4192 | 1156 | 1112 | 41
38938.4199 | 925 | 933 | 41
38938.4206 | 962 | 880 | 41
41
38938.3982 | 1 | 0 | 42
38938.3988 | 1 | 0 | 42
38938.3995 | 1 | 0 | 42
38938.4002 | 1 | 0 | 42
38938.4009 | 1 | 0 | 42
38938.4016 | 1 | 0 | 42
38938.4022 | 1 | 0 | 42
38938.4029 | 1 | 0 | 42
38938.4036 | 1 | 0 | 42
38938.4043 | 1 | 0 | 42
38938.405 | 1 | 0 | 42
38938.4056 | 1 | 0 | 42
38938.4063 | 996 | 966 | 42
38938.407 | 1077 | 1162 | 42
38938.4077 | 1064 | 1032 | 42
38938.4084 | 939 | 911 | 42
38938.4091 | 1070 | 1158 | 42
38938.4097 | 958 | 1077 | 42
38938.4104 | 965 | 939 | 42
38938.4111 | 1157 | 1197 | 42
38938.4118 | 597 | 586 | 42
38938.4125 | 944 | 932 | 42
38938.4131 | 922 | 953 | 42
38938.4138 | 1187 | 1193 | 42
38938.4145 | 1026 | 998 | 42
38938.4152 | 1079 | 1030 | 42
38938.4159 | 968 | 902 | 42
38938.4165 | 1168 | 1133 | 42
38938.4172 | 991 | 919 | 42
38938.4179 | 1004 | 932 | 42
38938.4186 | 1123 | 1070 | 42
38938.4193 | 1044 | 1054 | 42
38938.4199 | 923 | 974 | 42
38938.4206 | 1030 | 971 | 42
42