## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 34
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, XLPE insulated, CSPE jacketed Rockbestos Firewall III control cables (Item 10). Cable specimens present: Six lengths of cable were monitored for electrical performance, a seventh length of cable was monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 175 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
175 | 0 | Initated Penlight Heating
1479 | 1304 | Conductors A1 & A2 short together at less than 100 ohms (23) | Cable A shorts internally
1484-1507 | 1309-1332 | Conductors A1 & A2 short to ground at less than 1000 ohms (303 & 455) | Cable A shorted to ground
1750-1759 | 1575-1584 | Conductors C5 & C6 short to ground at less than 1000 ohms (292 & 309) | Cable C shorted to ground
1771 | 1596 | Conductors C5 & C6 short together at less than 100 ohms (3) | Cable C shorts internally
1807 | 1632 | Conductors D7 & D8 short together at less than 100 ohms (19) | Cable D shorts internally
1908 | 1733 | Conductors B3 & B4 short together at less than 100 ohms (55) | Cable B shorts internally
2031 | 1856 | Conductors F11 & F12 short together at less than 100 ohms (26) | Cable F shorts internally
2170-2173 | 1995-1998 | Conductors E9 & E10 short to ground at less than 1000 ohms (203 & 188) | Cable E shorted to ground
2202 | 2027 | Conductors E9 & E10 short together at less than 100 ohms (7) | Cable E shorts internally
2224-2246 | 2049-2071 | The existing ground faults on conductors A1 & A2 decrease to less than 100 ohms (64 & 61)
2522-2527 | 2347-2352 | Conductors D7 & D8 short to ground at less than 100 ohms (2 & 5) | Cable D shorted to ground
2539-2543 | 2364-2368 | The existing ground faults on conductors E9 & E10 decrease to less than 100 ohms (<1 & 2)
2561-2563 | 2386-2388 | Conductors F11 & F12 short to ground at less than 100 ohms (3 & 8) | Cable F shorted to ground
Additional Observations
Observation 1 | This test showed some unusual and unexplained behavior. The first cable to fail was Cable A on top of the pyramid bundle. This is not unexpected, but the cable shorted first internally and then to ground well before other cables shorted to ground. How the cable found a path to ground is unknown. It was well issolated from the tray by the other cables, but none-the-less found a ground path.
Observation 2 | There were no cable-to-cable interactions between any of the thermoset cable pairs until after the relevant conductors had shorted to ground. In all cases, intra-cable shorting was the first mode of failure followed by shorts to the external ground.
Observation 3 | The cables did not ignite and burn as expected, but the internal cable temperatures exceeded the shroud temperature and damage to the conductors did occur.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
All Cables = XLPE, item #10
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 34 |  |  | 2006-08-24 | 13:43
XLPE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | D-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | E-F MIN IR
-174 | 228037.9994 | -171 | 223437.9994 | -168.5 | 227437.9994 | -165.5 | 223137.9994 | -162.5 | 211201.9994 | -143.5 | 227237.9994 | -140.5 | 236837.9994 | -137.5 | 228537.9994 | -135 | 229037.9994 | -115 | 238537.9994 | -112.5 | 220137.9994 | -109.5 | 218637.9994 | -107 | 244037.9994 | -104 | 253837.9994 | -101.5 | 252237.9994 | -98.5 | 254537.9994 | -90 | 226537.9994 | -87.5 | 211201.9994 | -84.5 | 243537.9994 | -81.5 | 256137.9994 | -79 | 249437.9994 | -76 | 227737.9994 | -67.5 | 232837.9994 | -59.5 | 230237.9994 | -56.5 | 249737.9994 | -53.5 | 256137.9994 | -50.5 | 251437.9994 | -42.5 | 250237.9994 | -39.5 | 238437.9994 | -37 | 253437.9994 | -34 | 256337.9994 | -31.5 | 256737.9994 | -28.5 | 257137.9994 | -25.5 | 256137.9994 | -17.5 | 250037.9994 | -14.5 | 258137.9994 | -6 | 249337.9994 | -3.5 | 255337.9994 | -0.5 | 254637.9994 | 2.5 | 255437.9994 | 5 | 256337.9994 | 8 | 255337.9994 | -155.875 | 223437.9994 | -150.125 | 211201.9994 | -99.875 | 211201.9994 | -94.25 | 243537.9994 | -88.75 | 227737.9994 | -21.5 | 250037.9994 | -49.5 | 230237.9994 | -43.75 | 251437.9994 | 0.875 | 254637.9994
10.5 | 228037.9994 | 13.5 | 223437.9994 | 16.5 | 227437.9994 | 19 | 223137.9994 | 22 | 211201.9994 | 41.5 | 227237.9994 | 44.5 | 236837.9994 | 47 | 228537.9994 | 50 | 229037.9994 | 69.5 | 238537.9994 | 72.5 | 220137.9994 | 75 | 218637.9994 | 78 | 244037.9994 | 80.5 | 126868.9988 | 83.5 | 252237.9994 | 86.5 | 254537.9994 | 94.5 | 226537.9994 | 97.5 | 211201.9994 | 100.5 | 243537.9994 | 103 | 256137.9994 | 106 | 249437.9994 | 108.5 | 227737.9994 | 117 | 232837.9994 | 125.5 | 230237.9994 | 128.5 | 249737.9994 | 131 | 256137.9994 | 134 | 251437.9994 | 142.5 | 250237.9994 | 145 | 238437.9994 | 148 | 253437.9994 | 150.5 | 256337.9994 | 153.5 | 256737.9994 | 156.5 | 257137.9994 | 159 | 256137.9994 | 167.5 | 250037.9994 | 170.5 | 258137.9994 | 178.5 | 249337.9994 | 181.5 | 255337.9994 | 184.5 | 254637.9994 | 187 | 255437.9994 | 190 | 256337.9994 | 192.5 | 255337.9994 | 29 | 223437.9994 | 34.5 | 211201.9994 | 84.875 | 211201.9994 | 90.5 | 126868.9988 | 96.125 | 227737.9994 | 163.375 | 250037.9994 | 135.375 | 230237.9994 | 140.875 | 251437.9994 | 185.75 | 254637.9994
195.5 | 228037.9994 | 198.5 | 223437.9994 | 201 | 227437.9994 | 204 | 223137.9994 | 206.5 | 211201.9994 | 226.5 | 227237.9994 | 229 | 236837.9994 | 232 | 228537.9994 | 234.5 | 229037.9994 | 254.5 | 238537.9994 | 257 | 220137.9994 | 260 | 218637.9994 | 262.5 | 244037.9994 | 265.5 | 253837.9994 | 268.5 | 252237.9994 | 271 | 254537.9994 | 279.5 | 226537.9994 | 282.5 | 211201.9994 | 285 | 243537.9994 | 288 | 256137.9994 | 290.5 | 249437.9994 | 293.5 | 227737.9994 | 302 | 232837.9994 | 310.5 | 230237.9994 | 313 | 249737.9994 | 316 | 256137.9994 | 318.5 | 251437.9994 | 327 | 250237.9994 | 330 | 238437.9994 | 332.5 | 253437.9994 | 335.5 | 256337.9994 | 338.5 | 256737.9994 | 341 | 257137.9994 | 344 | 256137.9994 | 352.5 | 250037.9994 | 355 | 258137.9994 | 363.5 | 249337.9994 | 366.5 | 255337.9994 | 369 | 254637.9994 | 372 | 255437.9994 | 374.5 | 256337.9994 | 377.5 | 255337.9994 | 213.75 | 223437.9994 | 219.25 | 211201.9994 | 269.75 | 211201.9994 | 275.25 | 243537.9994 | 280.875 | 227737.9994 | 348.125 | 250037.9994 | 320.125 | 230237.9994 | 325.625 | 251437.9994 | 370.5 | 254637.9994
380.5 | 228037.9994 | 383 | 223437.9994 | 386 | 227437.9994 | 388.5 | 223137.9994 | 391.5 | 211201.9994 | 411 | 227237.9994 | 414 | 236837.9994 | 416.5 | 228537.9994 | 419.5 | 229037.9994 | 439 | 238537.9994 | 442 | 220137.9994 | 444.5 | 218637.9994 | 447.5 | 244037.9994 | 450.5 | 253837.9994 | 453 | 252237.9994 | 456 | 254537.9994 | 464.5 | 226537.9994 | 467 | 211201.9994 | 470 | 243537.9994 | 472.5 | 256137.9994 | 475.5 | 249437.9994 | 478.5 | 227737.9994 | 486.5 | 232837.9994 | 495 | 230237.9994 | 498 | 249737.9994 | 500.5 | 256137.9994 | 503.5 | 251437.9994 | 512 | 250237.9994 | 514.5 | 238437.9994 | 517.5 | 253437.9994 | 520.5 | 256337.9994 | 523 | 256737.9994 | 526 | 257137.9994 | 528.5 | 256137.9994 | 537 | 250037.9994 | 540 | 258137.9994 | 548.5 | 249337.9994 | 551 | 255337.9994 | 554 | 254637.9994 | 556.5 | 255437.9994 | 559.5 | 256337.9994 | 562.5 | 255337.9994 | 398.5 | 223437.9994 | 404 | 211201.9994 | 454.5 | 211201.9994 | 460.125 | 243537.9994 | 465.75 | 227737.9994 | 532.875 | 250037.9994 | 504.875 | 230237.9994 | 510.5 | 251437.9994 | 555.25 | 254637.9994
565 | 228037.9994 | 568 | 223437.9994 | 570.5 | 227437.9994 | 573.5 | 223137.9994 | 576.5 | 211201.9994 | 596 | 227237.9994 | 598.5 | 236837.9994 | 601.5 | 228537.9994 | 604.5 | 229037.9994 | 624 | 238537.9994 | 626.5 | 220137.9994 | 629.5 | 218637.9994 | 632.5 | 244037.9994 | 635 | 253837.9994 | 638 | 252237.9994 | 640.5 | 254537.9994 | 649 | 226537.9994 | 652 | 211201.9994 | 654.5 | 243537.9994 | 657.5 | 256137.9994 | 660.5 | 249437.9994 | 663 | 227737.9994 | 671.5 | 232837.9994 | 680 | 230237.9994 | 682.5 | 249737.9994 | 685.5 | 256137.9994 | 688.5 | 251437.9994 | 696.5 | 250237.9994 | 699.5 | 238437.9994 | 702.5 | 253437.9994 | 705 | 256138.078 | 708 | 256737.9994 | 710.5 | 257137.9994 | 713.5 | 256137.9994 | 722 | 250037.9994 | 724.5 | 258137.9994 | 733 | 249337.9994 | 735.5 | 255337.9994 | 738.5 | 254637.9994 | 741.5 | 255437.9994 | 744.5 | 256337.9994 | 746 | 255337.9994 | 583.25 | 223437.9994 | 589 | 211201.9994 | 639.25 | 211201.9994 | 644.875 | 243537.9994 | 650.5 | 227737.9994 | 717.625 | 250037.9994 | 689.625 | 230237.9994 | 695.375 | 251437.9994 | 740 | 254637.9994
750 | 228037.9994 | 752.5 | 223437.9994 | 755.5 | 227437.9994 | 758 | 223137.9994 | 761 | 211201.9994 | 780.5 | 227237.9994 | 783.5 | 236837.9994 | 786.5 | 228537.9994 | 789 | 229037.9994 | 808.5 | 238537.9994 | 811.5 | 220137.9994 | 814 | 218637.9994 | 817 | 244037.9994 | 820 | 253837.9994 | 822.5 | 252237.9994 | 825.5 | 254537.9994 | 834 | 226537.9994 | 836.5 | 211201.9994 | 839.5 | 243537.9994 | 842 | 256137.9994 | 845 | 249437.9994 | 848 | 227737.9994 | 856.5 | 232837.9994 | 864.5 | 230237.9994 | 867.5 | 249737.9994 | 870.5 | 256137.9994 | 873 | 251437.9994 | 881.5 | 250237.9994 | 884 | 238437.9994 | 887 | 253437.9994 | 889.5 | 256337.9994 | 892.5 | 256737.9994 | 895.5 | 257137.9994 | 898.5 | 256137.9994 | 906.5 | 250037.9994 | 909.5 | 258137.9994 | 918 | 249337.9994 | 920.5 | 255337.9994 | 923.5 | 254637.9994 | 926.5 | 255437.9994 | 929 | 256337.9994 | 932 | 255337.9994 | 768 | 223437.9994 | 773.625 | 211201.9994 | 824 | 211201.9994 | 829.625 | 243537.9994 | 835.25 | 227737.9994 | 902.5 | 250037.9994 | 874.375 | 230237.9994 | 880 | 251437.9994 | 924.875 | 254637.9994
934.5 | 228037.9994 | 937.5 | 223437.9994 | 940.5 | 227437.9994 | 943 | 223137.9994 | 946 | 211201.9994 | 965.5 | 227237.9994 | 968.5 | 236837.9994 | 971 | 228537.9994 | 974 | 229037.9994 | 993.5 | 238537.9994 | 996.5 | 220137.9994 | 999 | 218637.9994 | 1002 | 244037.9994 | 1004.5 | 253837.9994 | 1007.5 | 252237.9994 | 1010 | 254537.9994 | 1018.5 | 226537.9994 | 1021.5 | 211201.9994 | 1024 | 243537.9994 | 1027 | 256137.9994 | 1030 | 249437.9994 | 1032.5 | 227737.9994 | 1041 | 232837.9994 | 1049.5 | 230237.9994 | 1052 | 249737.9994 | 1055 | 256137.9994 | 1057.5 | 251437.9994 | 1066 | 250237.9994 | 1069 | 238437.9994 | 1071.5 | 253437.9994 | 1074.5 | 256337.9994 | 1077.5 | 256737.9994 | 1080.5 | 257137.9994 | 1083 | 256137.9994 | 1091.5 | 250037.9994 | 1094 | 258137.9994 | 1102.5 | 249337.9994 | 1105.5 | 255337.9994 | 1108 | 254637.9994 | 1111 | 255437.9994 | 1113.5 | 256337.9994 | 1116.5 | 255337.9994 | 953 | 223437.9994 | 958.5 | 211201.9994 | 1008.875 | 211201.9994 | 1014.375 | 243537.9994 | 1020 | 227737.9994 | 1087.25 | 250037.9994 | 1059.125 | 230237.9994 | 1064.625 | 251437.9994 | 1109.5 | 254637.9994
1119.5 | 228037.9994 | 1122 | 223437.9994 | 1125 | 227437.9994 | 1127.5 | 223137.9994 | 1130.5 | 211201.9994 | 1150.5 | 227237.9994 | 1153 | 236837.9994 | 1155.5 | 228537.9994 | 1158.5 | 229037.9994 | 1178.5 | 238537.9994 | 1181 | 220137.9994 | 1183.5 | 218637.9994 | 1186.5 | 244037.9994 | 1189.5 | 253837.9994 | 1192 | 252237.9994 | 1195 | 254537.9994 | 1203.5 | 226537.9994 | 1206 | 211201.9994 | 1209 | 243537.9994 | 1211.5 | 256137.9994 | 1214.5 | 249437.9994 | 1217.5 | 227737.9994 | 1225.5 | 232837.9994 | 1234 | 230237.9994 | 1237 | 249737.9994 | 1239.5 | 256137.9994 | 1242.5 | 251437.9994 | 1251 | 250237.9994 | 1253.5 | 238437.9994 | 1256.5 | 253437.9994 | 1259.5 | 256337.9994 | 1262 | 256737.9994 | 1265 | 257137.9994 | 1268 | 256137.9994 | 1276 | 250037.9994 | 1279 | 258137.9994 | 1287.5 | 249337.9994 | 1290 | 255337.9994 | 1293 | 254637.9994 | 1295.5 | 255437.9994 | 1298.5 | 256337.9994 | 1301.5 | 255337.9994 | 1137.625 | 223437.9994 | 1143 | 211201.9994 | 1193.5 | 211201.9994 | 1199.125 | 243537.9994 | 1204.75 | 227737.9994 | 1272 | 250037.9994 | 1243.875 | 230237.9994 | 1249.5 | 251437.9994 | 1294.25 | 254637.9994
1304 | 22.7543 | 1307 | 31791.2895 | 1309.5 | 113519.0879 | 1312.5 | 222938.0448 | 1315.5 | 211201.9994 | 1335 | 227237.9994 | 1337.5 | 236837.9994 | 1340.5 | 228537.9994 | 1343.5 | 229037.9994 | 1363 | 238537.9994 | 1365.5 | 220137.9994 | 1368.5 | 218637.9994 | 1371.5 | 244037.9994 | 1374 | 253837.9994 | 1377 | 252237.9994 | 1379.5 | 254537.9994 | 1388 | 226537.9994 | 1391 | 211201.9994 | 1393.5 | 243537.9994 | 1396.5 | 256137.9994 | 1399.5 | 249437.9994 | 1402 | 227737.9994 | 1410.5 | 232837.9994 | 1419 | 230237.9994 | 1421.5 | 249737.9994 | 1424.5 | 256137.9994 | 1427.5 | 251437.9994 | 1435.5 | 250237.9994 | 1438.5 | 238437.9994 | 1441.5 | 253437.9994 | 1444 | 256337.9994 | 1447 | 4564.4391 | 1449.5 | 256838.1166 | 1452.5 | 256137.9994 | 1461 | 250037.9994 | 1463.5 | 258137.9994 | 1472 | 249337.9994 | 1475 | 255337.9994 | 1477.5 | 254637.9994 | 1480.5 | 255437.9994 | 1483.5 | 256337.9994 | 1486 | 127618.9988 | 1322.25 | 31791.2895 | 1328 | 211201.9994 | 1378.25 | 211201.9994 | 1383.875 | 243537.9994 | 1389.5 | 227737.9994 | 1456.625 | 250037.9994 | 1428.625 | 230237.9994 | 1434.375 | 251437.9994 | 1479.125 | 254637.9994
1489 | 1.0437 | 1491.5 | 31777.0802 | 1494.5 | 227238.0879 | 1497.5 | 222938.0896 | 1500 | 211201.9994 | 1519.5 | 227237.9994 | 1522.5 | 236837.9994 | 1525.5 | 228537.9994 | 1528 | 229037.9994 | 1547.5 | 118819.44 | 1550.5 | 220137.9994 | 1553.5 | 218637.9994 | 1556 | 244037.9994 | 1559 | 253837.9994 | 1561.5 | 252237.9994 | 1564.5 | 254537.9994 | 1573 | 226537.9994 | 1575.5 | 211201.9994 | 1578.5 | 243537.9994 | 1581.5 | 256137.9994 | 1584 | 249437.9994 | 1587 | 227737.9994 | 1595.5 | 2.7059 | 1603.5 | 230038.0868 | 1606.5 | 249538.0801 | 1609.5 | 256137.9994 | 1612 | 251437.9994 | 1620.5 | 250237.9994 | 1623.5 | 238437.9994 | 1626 | 253437.9994 | 1629 | 256337.9994 | 1631.5 | 18.9774 | 1634.5 | 42723.1229 | 1637.5 | 127968.9805 | 1645.5 | 250037.9994 | 1649 | 258137.9994 | 1657 | 249337.9994 | 1659.5 | 255337.9994 | 1662.5 | 254637.9994 | 1665.5 | 255437.9994 | 1668 | 256337.9994 | 1671 | 254638.5872 | 1507 | 31777.0802 | 1512.75 | 211201.9994 | 1563.125 | 211201.9994 | 1568.75 | 243537.9994 | 1574.25 | 227737.9994 | 1641.625 | 42723.1229 | 1613.5 | 230038.0868 | 1619.125 | 251437.9994 | 1663.875 | 254637.9994
1673.5 | 20.4916 | 1676.5 | 37106.4747 | 1679.5 | 113569.0659 | 1682 | 222938.0896 | 1685 | 211201.9994 | 1704.5 | 227237.9994 | 1707.5 | 236837.9994 | 1710 | 228537.9994 | 1713 | 229037.9994 | 1732.5 | 55.0989 | 1735.5 | 54909.4546 | 1738 | 218438.0457 | 1741 | 244037.9994 | 1743.5 | 253837.9994 | 1746.5 | 252237.9994 | 1749.5 | 254537.9994 | 1757.5 | 226537.9994 | 1760.5 | 211201.9994 | 1763.5 | 243537.9994 | 1766 | 256137.9994 | 1769 | 249437.9994 | 1771.5 | 227737.9994 | 1780 | 1.0774 | 1788.5 | 229938.1737 | 1791.5 | 249538.0801 | 1794 | 256137.9994 | 1797 | 251437.9994 | 1805.5 | 250237.9994 | 1808 | 238437.9994 | 1811 | 253437.9994 | 1813.5 | 256337.9994 | 1816.5 | 67.274 | 1819.5 | 42723.1229 | 1822 | 127968.9805 | 1830.5 | 250037.9994 | 1833.5 | 258137.9994 | 1841.5 | 249038.1203 | 1844.5 | 255337.9994 | 1847.5 | 254637.9994 | 1850 | 255437.9994 | 1853 | 256337.9994 | 1855.5 | 25.6546 | 1692 | 37106.4747 | 1697.5 | 211201.9994 | 1747.875 | 54909.4546 | 1753.5 | 243537.9994 | 1759.125 | 227737.9994 | 1826.375 | 42723.1229 | 1798.375 | 229938.1737 | 1803.875 | 251437.9994 | 1848.75 | 254637.9994
1858.5 | 3.1874 | 1861.5 | 31777.0993 | 1864 | 75679.304 | 1867 | 111419.0672 | 1869.5 | 211002.0947 | 1889.5 | 113568.9988 | 1892 | 118368.9988 | 1895 | 228537.9994 | 1897.5 | 114468.9988 | 1917.5 | 789.1013 | 1920 | 219938.0908 | 1923 | 218438.0914 | 1925.5 | 121968.9988 | 1928.5 | 253837.9994 | 1931.5 | 252237.9994 | 1934 | 254537.9994 | 1942.5 | 226537.9994 | 1945.5 | 211201.9994 | 1948 | 121718.9988 | 1951 | 256137.9994 | 1953.5 | 249437.9994 | 1956.5 | 227737.9994 | 1965 | 8.4611 | 1973.5 | 230038.0868 | 1976 | 249737.9994 | 1979 | 256137.9994 | 1981.5 | 251437.9994 | 1990 | 250237.9994 | 1993 | 238437.9994 | 1995.5 | 253437.9994 | 1998.5 | 256337.9994 | 2001.5 | 24.5462 | 2004 | 42723.1229 | 2007 | 255938.0781 | 2015 | 250037.9994 | 2018 | 258137.9994 | 2026.5 | 6.5397 | 2029.5 | 42423.1238 | 2032 | 127119.0785 | 2035 | 255238.0783 | 2037.5 | 256337.9994 | 2040.5 | 53.3794 | 1876.75 | 31777.0993 | 1882.25 | 111419.0672 | 1932.75 | 211201.9994 | 1938.25 | 121718.9988 | 1943.875 | 227737.9994 | 2011 | 42723.1229 | 1983.125 | 230038.0868 | 1988.625 | 251437.9994 | 2033.5 | 42423.1238
2043.5 | 8.6871 | 2046 | 4752.2664 | 2049 | 3712.9503 | 2051.5 | 2353.7153 | 2054.5 | 3709.371 | 2074 | 2860.3772 | 2077 | 2662.5204 | 2079.5 | 2603.697 | 2082.5 | 1743.906 | 2102 | 13.9194 | 2105 | 6879.0215 | 2107.5 | 6821.1338 | 2110.5 | 9522.0048 | 2113.5 | 11835.6886 | 2116 | 252237.9994 | 2119 | 254537.9994 | 2127.5 | 5287.105 | 2130 | 4177.6965 | 2133 | 9898.0342 | 2135.5 | 8040.3294 | 2138.5 | 249437.9994 | 2141.5 | 227737.9994 | 2149.5 | 2.0961 | 2158 | 230038.0868 | 2161 | 249438.1601 | 2163.5 | 255638.3122 | 2166.5 | 251038.1988 | 2175 | 250237.9994 | 2177.5 | 238437.9994 | 2180.5 | 252838.4339 | 2183.5 | 255738.429 | 2186 | 69.6438 | 2189 | 42723.1229 | 2191.5 | 127869.0781 | 2200 | 250037.9994 | 2202.5 | 258137.9994 | 2211 | 36.4276 | 2214 | 42423.1238 | 2217 | 127218.9804 | 2219.5 | 255237.9609 | 2222.5 | 256337.9994 | 2225.5 | 55.9421 | 2061.5 | 2662.5204 | 2067 | 1743.906 | 2117.5 | 4177.6965 | 2123.125 | 8040.3294 | 2128.75 | 227737.9994 | 2195.75 | 42723.1229 | 2167.875 | 230038.0868 | 2173.5 | 251038.1988 | 2218.25 | 42423.1238
2228 | 3.8075 | 2231 | 579.4784 | 2233.5 | 421.8844 | 2236.5 | 439.0667 | 2239 | 354.5329 | 2258.5 | 510.5347 | 2261.5 | 546.2532 | 2264.5 | 372.9819 | 2267.5 | 598.1901 | 2286.5 | 51.8991 | 2289.5 | 1065.9433 | 2292.5 | 1004.8659 | 2295 | 17976.3392 | 2298 | 17341.185 | 2300.5 | 572.6724 | 2303.5 | 611.0608 | 2312 | 1422.6087 | 2314.5 | 894.2096 | 2317.5 | 275.009 | 2320.5 | 172.0197 | 2323 | 85.824 | 2326 | 49.4632 | 2334.5 | 41.1796 | 2343 | 65532.1972 | 2345.5 | 378.2982 | 2348.5 | 429.1219 | 2351.5 | 327.4267 | 2359.5 | 314.7861 | 2362.5 | 335.7502 | 2365.5 | 357.3116 | 2368 | 342.5446 | 2370.5 | 0.50469 | 2373.5 | 26.176 | 2376.5 | 27.8097 | 2384.5 | 3.1124 | 2387.5 | 7.7477 | 2396 | 24.5776 | 2399 | 20.0631 | 2401.5 | 22.8886 | 2404.5 | 1.022 | 2407.5 | 7.8764 | 2410 | 25.6016 | 2246.125 | 421.8844 | 2251.875 | 354.5329 | 2302.125 | 894.2096 | 2307.75 | 172.0197 | 2313.25 | 49.4632 | 2380.5 | 3.1124 | 2352.625 | 314.7861 | 2358.375 | 327.4267 | 2403.125 | 1.022
2412.5 | 0.22185 | 2415.5 | 363.6281 | 2418.5 | 568.8503 | 2421 | 202.8612 | 2424 | 124.0174 | 2443.5 | 217.5165 | 2446.5 | 136.6721 | 2449 | 194.5424 | 2452 | 196.4494 | 2471.5 | 3.7486 | 2474.5 | 351.2685 | 2477.5 | 305.1373 | 2480 | 12276.142 | 2482.5 | 13790.5042 | 2485.5 | 230.2524 | 2488.5 | 263.8622 | 2496.5 | 277.8654 | 2499.5 | 199.4513 | 2502.5 | 163.9741 | 2505 | 170.2872 | 2508 | 185.9642 | 2510.5 | 122.091 | 2519 | 2.7279 | 2527.5 | 126.5387 | 2530.5 | 146.0133 | 2533 | 139.4967 | 2536 | 138.919 | 2544.5 | 131.7826 | 2546 | 129.8396 | 2550 | 165.1807 | 2552.5 | 144.2873 | 2555.5 | 18.7113 | 2558.5 | 26.1123 | 2561 | 22.5227 | 2569.5 | 9.5493 | 2572.5 | 28.4872 | 2580.5 | 1.856 | 2583.5 | 15.8425 | 2586.5 | 28.9729 | 2589 | 27.7194 | 2592 | 22.8616 | 2595 | 1.4009 | 2431 | 136.6721 | 2436.5 | 124.0174 | 2487 | 199.4513 | 2492.5 | 163.9741 | 2498.125 | 122.091 | 2565.375 | 9.5493 | 2537.125 | 126.5387 | 2542.875 | 138.919 | 2587.75 | 15.8425
2597.5 | 7.7472 | 2600.5 | 73.0457 | 2603 | 168.8039 | 2606 | 78.3148 | 2608.5 | 81.1212 | 2628.5 | 51.9066 | 2631 | 84.5385 | 2634 | 121.485 | 2636.5 | 134.6465 | 2656.5 | 62.712 | 2659 | 362.1273 | 2662 | 202.0018 | 2664.5 | 53.9477 | 2667.5 | 71.7315 | 2670.5 | 76.5848 | 2673 | 38.6451 | 2681.5 | 603.1539 | 2684.5 | 549.4124 | 2687 | 21.778 | 2690 | 33.7738 | 2692.5 | 46.8 | 2695.5 | 32.7466 | 2704 | 15.9412 | 2712.5 | 63.5544 | 2715 | 47.9553 | 2718 | 69.4528 | 2720.5 | 82.9027 | 2729 | 39.5526 | 2732 | 56.2129 | 2734.5 | 44.6492 | 2737.5 | 39.7109 | 2740.5 | 0.27142 | 2743 | 23.7378 | 2746 | 25.238 | 2754.5 | 26.6883 | 2757 | 5.5014 | 2765.5 | 17.6697 | 2768.5 | 1.2329 | 2771 | 0.95132 | 2774 | 10.6364 | 2776.5 | 13.3729 | 2779.5 | 0.5404 | 2615.75 | 51.9066 | 2621.25 | 78.3148 | 2671.75 | 202.0018 | 2677.25 | 21.778 | 2682.875 | 32.7466 | 2750.125 | 5.5014 | 2722.125 | 39.5526 | 2727.625 | 39.7109 | 2772.5 | 0.95132
2782.5 | 33.3141 | 2785 | 142.8963 | 2788 | 95.398 | 2790.5 | 32.3858 | 2793.5 | 3.7828 | 2813 | 148.3455 | 2816 | 42.5756 | 2818.5 | 107.0334 | 2821.5 | 62.7306 | 2841 | 20.6705 | 2844 | 304.9828 | 2846.5 | 483.6929 | 2849.5 | 22.2191 | 2852.5 | 39.6625 | 2855 | 15.3952 | 2858 | 30.5519 | 2866.5 | 1768.6323 | 2869 | 129.5465 | 2872 | 9368.2892 | 2874.5 | 32.8484 | 2877.5 | 35.1673 | 2880.5 | 27.5682 | 2888.5 | 69.1107 | 2897 | 50.4098 | 2900 | 48.7647 | 2902.5 | 40.2269 | 2905.5 | 59.9786 | 2914 | 53.6367 | 2916.5 | 23.9212 | 2919.5 | 37.8108 | 2922.5 | 56.8159 | 2925 | 25.4079 | 2928 | 2.4662 | 2930.5 | 0.34595 | 2939 | 18.7555 | 2942 | 24.1006 | 2950.5 | 0.8518 | 2953 | 0.74275 | 2956 | 15.1431 | 2958.5 | 7.823 | 2961.5 | 22.5589 | 2964.5 | 24.5922 | 2800.5 | 42.5756 | 2806 | 3.7828 | 2856.5 | 129.5465 | 2862.125 | 22.2191 | 2867.75 | 15.3952 | 2934.875 | 0.34595 | 2906.875 | 23.9212 | 2912.5 | 37.8108 | 2957.25 | 0.74275
2967 | 6.0563 | 2970 | 4.5968 | 2972.5 | 18.102 | 2975.5 | 45.8713 | 2978.5 | 61.913 | 2998 | 120.0606 | 3000.5 | 176.7281 | 3003.5 | 97.465 | 3006.5 | 59.0603 | 3026 | 108.1245 | 3028.5 | 56.9795 | 3031.5 | 28.8028 | 3034.5 | 30.4783 | 3037 | 15.9159 | 3040 | 18.8211 | 3042.5 | 39.9717 | 3051 | 293.3582 | 3054 | 130.1904 | 3056.5 | 18.0078 | 3059.5 | 21.6826 | 3062.5 | 11.2031 | 3065 | 4.6586 | 3073.5 | 19.3108 | 3082 | 5.07 | 3084.5 | 42.9396 | 3087.5 | 18.0363 | 3090.5 | 30.0441 | 3098.5 | 32.5847 | 3101.5 | 8.7032 | 3104.5 | 27.2993 | 3107 | 27.9104 | 3110 | 3.6408 | 3112.5 | 0.073063 | 3115.5 | 2.9615 | 3124 | 15.691 | 3126.5 | 13.4505 | 3135 | 24.963 | 3138 | 27.6689 | 3140.5 | 0.16251 | 3143.5 | 8.7293 | 3146.5 | 0.14498 | 3149 | 4.5642 | 2985.25 | 4.5968 | 2991 | 45.8713 | 3041.25 | 28.8028 | 3046.875 | 15.9159 | 3052.5 | 4.6586 | 3119.625 | 0.073063 | 3091.625 | 5.07 | 3097.375 | 18.0363 | 3142.125 | 0.14498
3152 | 0.11259 | 3154.5 | 161.3402 | 3157.5 | 478.72 | 3160.5 | 6.6807 | 3163 | 22.8865 | 3182.5 | 27.2136 | 3185.5 | 1296.329 | 3188.5 | 52.559 | 3191 | 18.8301 | 3210.5 | 5.4162 | 3213.5 | 1961.5064 | 3216.5 | 13.4171 | 3219 | 17.3724 | 3222 | 14.7773 | 3224.5 | 21.3568 | 3227.5 | 12.1563 | 3236 | 143.4457 | 3238.5 | 11.1263 | 3241.5 | 9.3505 | 3244.5 | 9.1276 | 3247 | 4.6145 | 3250 | 6.6919 | 3258.5 | 3.5587 | 3266.5 | 27.7328 | 3269.5 | 18.5535 | 3272.5 | 18.4875 | 3275 | 34.689 | 3283.5 | 17.9265 | 3286.5 | 13.7473 | 3289 | 33.6406 | 3292 | 17.4582 | 3294.5 | 28.6398 | 3297.5 | 7.1388 | 3300.5 | 7.6028 | 3308.5 | 24.2916 | 3311.5 | 9.0252 | 3320 | 1500.4316 | 3322.5 | 25.1581 | 3325.5 | 21.4985 | 3328.5 | 1.4833 | 3331 | 0.63418 | 3334 | 0.90406 | 3170 | 27.2136 | 3175.75 | 6.6807 | 3226.125 | 11.1263 | 3231.75 | 9.1276 | 3237.25 | 4.6145 | 3304.5 | 7.1388 | 3276.5 | 13.7473 | 3282.125 | 17.4582 | 3326.875 | 0.63418
3336.5 | 42.1346 | 3339.5 | 29.783 | 3342.5 | 20.2471 | 3345 | 1229.3734 | 3348 | 222.8437 | 3367.5 | 456.056 | 3370.5 | 3.1103 | 3373 | 30.017 | 3375.5 | 83.6927 | 3395.5 | 46.3699 | 3398.5 | 3857.3127 | 3401 | 3825.3886 | 3404 | 5.7814 | 3406.5 | 24.3531 | 3409.5 | 758.8817 | 3412.5 | 2567.968 | 3420.5 | 1997.2842 | 3423.5 | 43.1806 | 3426.5 | 20.23 | 3429 | 24.4859 | 3432 | 5149.153 | 3434.5 | 631.5382 | 3443 | 1.5185 | 3451.5 | 3.1155 | 3454.5 | 29.1573 | 3457 | 31.657 | 3460 | 51.347 | 3468.5 | 22.1413 | 3471 | 17.0917 | 3474 | 32.2811 | 3476.5 | 28.5037 | 3480 | 18.147 | 3482.5 | 0.91959 | 3485 | 2.5741 | 3493.5 | 7.736 | 3496.5 | 4.6987 | 3504.5 | 179.9819 | 3507.5 | 20.7073 | 3510.5 | 38.3143 | 3513 | 38.675 | 3515.5 | 55.4594 | 3518.5 | 10.5429 | 3355 | 3.1103 | 3360.375 | 30.017 | 3410.875 | 43.1806 | 3416.5 | 5.7814 | 3422.125 | 631.5382 | 3489.375 | 0.91959 | 3461.375 | 3.1155 | 3466.875 | 28.5037 | 3511.625 | 20.7073
3521.5 | 4.2523 | 3524 | 49.0234 | 3527 | 4.2192 | 3530 | 15.8381 | 3532.5 | 3.2805 | 3552.5 | 23.5605 | 3555 | 51.4843 | 3557.5 | 79.4203 | 3560.5 | 28.4923 | 3580.5 | 21.6405 | 3583 | 45.2614 | 3586 | 33.9884 | 3588.5 | 41.7268 | 3591.5 | 54.9877 | 3594 | 49.2458 | 3597 | 35.8853 | 3605.5 | 83.7972 | 3608 | 23.6149 | 3611 | 74.3039 | 3613.5 | 61.2114 | 3616.5 | 86.3479 | 3619.5 | 10.2836 | 3627.5 | 45.9871 | 3636 | 51.8234 | 3639 | 60.7642 | 3641.5 | 39.1353 | 3644.5 | 30.4597 | 3653 | 37.8999 | 3655.5 | 24.3197 | 3658.5 | 40.3097 | 3661.5 | 72.6011 | 3664 | 9.1931 | 3667 | 10.7346 | 3669.5 | 26.3186 | 3678.5 | 18.4652 | 3681 | 9.4093 | 3689.5 | 8819.0462 | 3692.5 | 7.6857 | 3695 | 23.3178 | 3698 | 30.1265 | 3700.5 | 2.1853 | 3703.5 | 14.979 | 3539.625 | 4.2192 | 3545.125 | 3.2805 | 3595.625 | 23.6149 | 3601.125 | 41.7268 | 3606.75 | 10.2836 | 3674 | 9.4093 | 3645.875 | 24.3197 | 3651.5 | 30.4597 | 3696.5 | 2.1853
3706 | 17.3214 | 3709 | 86.9303 | 3711.5 | 76.0822 | 3714.5 | 73.3574 | 3717.5 | 118.5784 | 3737 | 82.8544 | 3740 | 78.3734 | 3742.5 | 238.3684 | 3745.5 | 322.5221 | 3765 | 26.8505 | 3768 | 700.993 | 3770.5 | 632.1086 | 3773.5 | 48.1381 | 3776.5 | 46.0714 | 3779 | 14607.3483 | 3782 | 9746.5565 | 3790.5 | 83.5099 | 3793 | 346.889 | 3796 | 47.2854 | 3798.5 | 47.9255 | 3801.5 | 2052.4697 | 3804 | 1563.4328 | 3812.5 | 2.7683 | 3821 | 33.182 | 3823.5 | 43.1909 | 3826.5 | 54.9543 | 3829.5 | 28.7447 | 3837.5 | 37.8999 | 3840.5 | 24.0538 | 3843.5 | 22.7923 | 3846.5 | 22.9224 | 3849 | 0.13563 | 3851.5 | 4.6858 | 3854.5 | 10.7442 | 3863 | 0.26424 | 3865.5 | 0.9282 | 3874.5 | 14.2508 | 3877 | 9.3146 | 3880 | 34.8619 | 3882.5 | 31.0175 | 3885.5 | 31.2067 | 3888.5 | 11.3934 | 3724.375 | 76.0822 | 3730 | 73.3574 | 3780.5 | 83.5099 | 3786.125 | 46.0714 | 3791.625 | 1563.4328 | 3858.625 | 0.26424 | 3830.625 | 24.0538 | 3836.5 | 22.7923 | 3881.25 | 9.3146
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 34 |  |  | 2006-08-24 | 13:43
XLPE | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B to Gnd Min | Penlight Time | A-C to Gnd Min | Penlight Time | B-C to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-168.3 | 211202 |  | -146.1 | 227238 | -118.0556 | 218638 | -102.5 | 211202 | -88.1111 | 220138 | -79.4444 | 211202 | -55.4 | 243538 | -49.8 | 250038 | -37.6111 | 230238 | -34.3333 | 83046 | -16.7 | 253438 | -14.4 | 251438 | -133.7389 | 211202 | -120.4889 | 211202 | -97.0278 | 211202 | -81.4389 | 211202 | -73.125 | 83046 | -44.2861 | 83046 | -59.875 | 83046 | -49.6639 | 211202 | -25.7611 | 83046 | -157.2 | 211202 | -110.2778 | 211202 | -83.7778 | 211202 | -52.6 | 243538 | -35.9722 | 83046 | -15.55 | 251438
16.3 | 211202 |  | 38.7 | 227238 | 66.7222 | 126869 | 82.2778 | 211202 | 96.5556 | 220138 | 105.2778 | 211202 | 129.5 | 243538 | 135 | 250038 | 147.3333 | 230238 | 150.3889 | 227738 | 168 | 253438 | 170.3 | 251438 | 51 | 126869 | 64.2083 | 211202 | 87.7083 | 126869 | 103.375 | 126869 | 111.6806 | 126869 | 140.5556 | 227738 | 124.8889 | 211202 | 135.0333 | 211202 | 159.0056 | 227738 | 27.5 | 211202 | 74.5 | 126869 | 100.9167 | 211202 | 132.25 | 243538 | 148.8611 | 227738 | 169.15 | 251438
201.1 | 211202 |  | 223.5 | 227238 | 251.5556 | 218638 | 267.0556 | 211202 | 281.3889 | 220138 | 290.0556 | 211202 | 314.2 | 243538 | 319.9 | 250038 | 332.1111 | 230238 | 335.1667 | 227738 | 352.9 | 253438 | 355 | 251438 | 235.8028 | 211202 | 249.0111 | 211202 | 272.5139 | 211202 | 288.1778 | 211202 | 296.4722 | 211202 | 325.3444 | 227738 | 309.6806 | 211202 | 319.8361 | 211202 | 343.7944 | 227738 | 212.3 | 211202 | 259.3056 | 211202 | 285.7222 | 211202 | 317.05 | 243538 | 333.6389 | 227738 | 353.95 | 251438
385.9 | 211202 |  | 408.3 | 227238 | 436.2778 | 218638 | 451.8889 | 211202 | 466.1111 | 220138 | 474.8333 | 109269 | 499 | 243538 | 504.6 | 250038 | 516.8889 | 230238 | 520 | 227738 | 537.6 | 253438 | 540 | 251438 | 420.5917 | 211202 | 433.7861 | 109269 | 457.2778 | 109269 | 472.9417 | 211202 | 481.2639 | 211202 | 510.1222 | 227738 | 494.4583 | 109269 | 504.6361 | 109269 | 528.6222 | 227738 | 397.1 | 211202 | 444.0833 | 211202 | 470.4722 | 109269 | 501.8 | 243538 | 518.4444 | 227738 | 538.8 | 251438
570.7 | 211202 |  | 593.1 | 227238 | 621.1111 | 218638 | 636.6111 | 211202 | 650.9444 | 220138 | 659.7222 | 211202 | 683.8 | 243538 | 689.4 | 250038 | 701.6111 | 230238 | 704.7222 | 227738 | 722.2 | 253438 | 724.5 | 251438 | 605.3806 | 211202 | 618.6167 | 211202 | 642.0972 | 211202 | 657.7306 | 211202 | 666.0139 | 211202 | 694.8833 | 227738 | 679.25 | 211202 | 689.3417 | 211202 | 713.2583 | 227738 | 581.9 | 211202 | 628.8611 | 211202 | 655.3333 | 211202 | 686.6 | 243538 | 703.1667 | 227738 | 723.35 | 251438
755.4 | 211202 |  | 777.9 | 227238 | 805.7778 | 218638 | 821.3889 | 119219 | 835.7778 | 220138 | 844.3333 | 211202 | 868.6 | 243538 | 874.1 | 250038 | 886.3889 | 230238 | 889.6111 | 227738 | 907.3 | 253438 | 909.4 | 251438 | 790.1167 | 119219 | 803.3528 | 211202 | 826.8194 | 119219 | 842.4667 | 119219 | 850.7917 | 119219 | 879.675 | 227738 | 864.0278 | 211202 | 874.2028 | 211202 | 898.175 | 227738 | 766.65 | 211202 | 813.5833 | 119219 | 840.0556 | 211202 | 871.35 | 243538 | 888 | 227738 | 908.35 | 251438
940.3 | 211202 |  | 962.7 | 227238 | 990.6667 | 218638 | 1006.2222 | 211202 | 1020.4444 | 220138 | 1029.1667 | 211202 | 1053.4 | 243538 | 1058.9 | 250038 | 1071.2222 | 230238 | 1074.1667 | 227738 | 1091.9 | 253438 | 1094 | 251438 | 974.9722 | 211202 | 988.1528 | 211202 | 1011.625 | 211202 | 1027.2972 | 211202 | 1035.5694 | 211202 | 1064.4222 | 227738 | 1048.75 | 211202 | 1058.8778 | 211202 | 1082.8222 | 227738 | 951.5 | 211202 | 998.4444 | 211202 | 1024.8056 | 211202 | 1056.15 | 243538 | 1072.6944 | 227738 | 1092.95 | 251438
1124.9 | 211202 |  | 1147.4 | 227238 | 1175.3889 | 218638 | 1190.9444 | 211202 | 1205.1111 | 220138 | 1213.8333 | 211202 | 1238.1 | 243538 | 1243.6 | 250038 | 1255.8889 | 230238 | 1259.0556 | 227738 | 1276.6 | 253438 | 1279 | 251438 | 1159.6583 | 211202 | 1172.8111 | 211202 | 1196.3194 | 211202 | 1212.0083 | 211202 | 1220.3194 | 211202 | 1249.1611 | 227738 | 1233.4722 | 211202 | 1243.6361 | 211202 | 1267.6361 | 227738 | 1136.15 | 211202 | 1183.1667 | 211202 | 1209.4722 | 211202 | 1240.85 | 243538 | 1257.4722 | 227738 | 1277.8 | 251438
1309.7 | 302.6716 |  | 1332.1 | 454.6914 | 1360.1111 | 218638 | 1375.6111 | 211202 | 1389.9444 | 220138 | 1398.7222 | 211202 | 1422.8 | 60309.4581 | 1428.4 | 6328.3432 | 1440.6667 | 230238 | 1443.7222 | 227738 | 1461.5 | 127619 | 1463.7 | 251438 | 1344.3806 | 302.6716 | 1357.6167 | 302.6716 | 1381.0972 | 211202 | 1396.7306 | 6328.3432 | 1405.0278 | 211202 | 1433.8972 | 6328.3432 | 1418.2639 | 211202 | 1428.4667 | 127619 | 1452.3972 | 127619 | 1320.9 | 302.6716 | 1367.8611 | 211202 | 1394.3333 | 211202 | 1425.6 | 6328.3432 | 1442.1944 | 227738 | 1462.6 | 127619
1494.5 | 392.7088 |  | 1516.9 | 431.0007 | 1544.8333 | 79446 | 1560.4444 | 79446 | 1574.8333 | 291.9078 | 1583.5 | 309.0407 | 1607.6 | 6364.3415 | 1613.3 | 6364.3415 | 1625.3889 | 230238 | 1628.7222 | 227738 | 1646.3 | 85046 | 1648.5 | 85046 | 1529.1694 | 392.7088 | 1542.4333 | 291.9078 | 1565.9028 | 291.9078 | 1581.5444 | 6364.3415 | 1589.8472 | 79446 | 1618.7528 | 6364.3415 | 1603.1111 | 291.9078 | 1613.2833 | 291.9078 | 1637.2278 | 85046 | 1505.7 | 392.7088 | 1552.6389 | 79446 | 1579.1667 | 291.9078 | 1610.45 | 6364.3415 | 1627.0556 | 227738 | 1647.4 | 85046
1679.3 | 7496.1259 |  | 1701.7 | 10705.5679 | 1729.7222 | 5580.7447 | 1745.2778 | 40214.2049 | 1759.5556 | 590.9039 | 1768.2778 | 780.1612 | 1792.5 | 5287.8246 | 1798 | 23348.5482 | 1810.3333 | 115069 | 1813.3889 | 227738 | 1831 | 7689.7409 | 1833.3 | 10151.9151 | 1714 | 5580.7447 | 1727.2083 | 590.9039 | 1750.7083 | 590.9039 | 1766.375 | 5287.8246 | 1774.6806 | 5580.7447 | 1803.5556 | 5287.8246 | 1787.8889 | 590.9039 | 1798.0333 | 590.9039 | 1822.0056 | 7689.7409 | 1690.5 | 7496.1259 | 1737.5 | 5580.7447 | 1763.9167 | 590.9039 | 1795.25 | 5287.8246 | 1811.8611 | 115069 | 1832.15 | 7689.7409
1864.1 | 2805.1544 |  | 1886.5 | 113569 | 1914.5556 | 42426.7648 | 1930.0556 | 12224.3229 | 1944.3889 | 769.5557 | 1953.0556 | 1468.5262 | 1977.2 | 14602.0483 | 1982.8 | 7378.8839 | 1995.0556 | 203.1307 | 1998.1667 | 188.1659 | 2015.9 | 1163.2979 | 2018 | 3157.3493 | 1898.8028 | 2805.1544 | 1912.0111 | 769.5557 | 1935.5139 | 769.5557 | 1951.1528 | 7378.8839 | 1959.4583 | 188.1659 | 1988.3056 | 188.1659 | 1972.6667 | 188.1659 | 1982.8361 | 769.5557 | 2006.7806 | 188.1659 | 1875.3 | 2805.1544 | 1922.3056 | 12224.3229 | 1948.7222 | 769.5557 | 1980 | 7378.8839 | 1996.6111 | 188.1659 | 2016.95 | 1163.2979
2048.9 | 63.5354 |  | 2071.3 | 60.948 | 2099.2778 | 3627.3115 | 2114.8889 | 8011.0125 | 2129.1111 | 32514.2671 | 2137.8333 | 4727.3721 | 2162 | 5073.9339 | 2167.5 | 50876.0679 | 2179.8333 | 3170.961 | 2182.8889 | 17416.2881 | 2200.6 | 6624.4165 | 2203 | 10054.0807 | 2083.5917 | 60.948 | 2096.7861 | 60.948 | 2120.2778 | 3627.3115 | 2135.9167 | 3627.3115 | 2144.2222 | 3170.961 | 2173.0556 | 3170.961 | 2157.4167 | 3170.961 | 2167.6361 | 4727.3721 | 2191.5806 | 3170.961 | 2060.1 | 60.948 | 2107.0833 | 3627.3115 | 2133.4722 | 4727.3721 | 2164.75 | 5073.9339 | 2181.3611 | 3170.961 | 2201.8 | 6624.4165
2233.6 | 2151.0865 |  | 2256 | 948.122 | 2283.8889 | 491.9496 | 2299.4444 | 50.3881 | 2313.9444 | 327.7857 | 2322.6111 | 315.1542 | 2346.6 | 2.0413 | 2352.2 | 4.5727 | 2364.5 | 0.65915 | 2367.7222 | 2.2669 | 2385.5 | 3.4887 | 2387.7 | 7.8028 | 2268.2333 | 50.3881 | 2281.5389 | 315.1542 | 2304.9722 | 50.3881 | 2320.5333 | 2.0413 | 2328.8889 | 0.65915 | 2357.7556 | 0.65915 | 2342.1944 | 0.65915 | 2352.4389 | 3.4887 | 2376.3556 | 0.65915 | 2244.8 | 948.122 | 2291.6667 | 50.3881 | 2318.2778 | 315.1542 | 2349.4 | 2.0413 | 2366.1111 | 0.65915 | 2386.6 | 3.4887
2418.3 | 2.6395 |  | 2440.7 | 2.4627 | 2468.7778 | 68.5701 | 2484.2778 | 122.7155 | 2498.5556 | 127.1578 | 2507.2222 | 130.4715 | 2531.5 | 8.1394 | 2537 | 8.6652 | 2549.3333 | 2.3459 | 2552.2778 | 5.383 | 2570.1 | 2.9162 | 2572.4 | 3.4259 | 2453.0139 | 2.4627 | 2466.1944 | 2.4627 | 2489.7083 | 68.5701 | 2505.3889 | 8.1394 | 2513.6667 | 2.3459 | 2542.5278 | 2.3459 | 2526.8472 | 2.3459 | 2537.0694 | 2.9162 | 2561.0278 | 2.3459 | 2429.5 | 2.4627 | 2476.5278 | 68.5701 | 2502.8889 | 127.1578 | 2534.25 | 8.1394 | 2550.8056 | 2.3459 | 2571.25 | 2.9162
2603.1 | 73.4989 |  | 2625.5 | 53.8395 | 2653.5556 | 37.1447 | 2669.0556 | 22.9874 | 2683.3889 | 48.9791 | 2692.0556 | 40.6393 | 2716.2 | 0.67686 | 2721.9 | 4.3633 | 2734.1111 | 1.9976 | 2737.1667 | 0.65995 | 2754.9 | 1.0036 | 2757 | 1.3589 | 2637.8028 | 22.9874 | 2651.0111 | 40.6393 | 2674.5139 | 22.9874 | 2690.1778 | 0.67686 | 2698.4722 | 0.65995 | 2727.3444 | 0.65995 | 2711.6806 | 0.65995 | 2721.8361 | 1.0036 | 2745.7944 | 0.65995 | 2614.3 | 53.8395 | 2661.3056 | 22.9874 | 2687.7222 | 40.6393 | 2719.05 | 0.67686 | 2735.6389 | 0.65995 | 2755.95 | 1.0036
2787.9 | 5.1298 |  | 2810.3 | 9.9866 | 2838.2778 | 7.7729 | 2853.8889 | 1.9546 | 2868.1111 | 23.0792 | 2876.8333 | 25.0855 | 2901 | 0.67546 | 2906.6 | 0.87903 | 2918.8889 | 0.65862 | 2922 | 1.12 | 2939.6 | 0.65026 | 2942 | 0.65546 | 2822.5917 | 1.9546 | 2835.7861 | 5.1298 | 2859.2778 | 1.9546 | 2874.9417 | 0.67546 | 2883.2639 | 0.65862 | 2912.1222 | 0.65862 | 2896.4583 | 0.65862 | 2906.6361 | 0.65026 | 2930.6222 | 0.65026 | 2799.1 | 5.1298 | 2846.0833 | 1.9546 | 2872.4722 | 23.0792 | 2903.8 | 0.67546 | 2920.4444 | 0.65862 | 2940.8 | 0.65026
2972.7 | 1.011 |  | 2995.1 | 5.6044 | 3023.1111 | 0.75745 | 3038.6111 | 3.0477 | 3052.9444 | 6.3917 | 3061.7222 | 0.96289 | 3085.8 | 1.4746 | 3091.4 | 0.64336 | 3103.6667 | 0.65337 | 3106.7222 | 0.64743 | 3124.5 | 6.0349 | 3126.7 | 0.64718 | 3007.3806 | 0.75745 | 3020.6167 | 0.96289 | 3044.0972 | 0.75745 | 3059.7306 | 0.64336 | 3068.0278 | 0.64743 | 3096.8972 | 0.64336 | 3081.2639 | 0.64743 | 3091.4667 | 0.64718 | 3115.3972 | 0.64718 | 2983.9 | 1.011 | 3030.8611 | 0.75745 | 3057.3333 | 0.96289 | 3088.6 | 0.64336 | 3105.1944 | 0.64743 | 3125.6 | 0.64718
3157.5 | 0.1358 |  | 3179.9 | 0.25853 | 3207.8333 | 0.54492 | 3223.4444 | 0.73149 | 3237.8333 | 0.72792 | 3246.5 | 0.73612 | 3270.6 | 3.8885 | 3276.2 | 2.4357 | 3288.3889 | 0.71622 | 3291.6667 | 0.64336 | 3309.3 | 0.64514 | 3311.5 | 0.64286 | 3192.1694 | 0.1358 | 3205.4333 | 0.1358 | 3228.9028 | 0.54492 | 3244.5194 | 0.54492 | 3252.8333 | 0.54492 | 3281.7139 | 0.64336 | 3266.0972 | 0.64336 | 3276.2833 | 0.64286 | 3300.2139 | 0.64286 | 3168.7 | 0.1358 | 3215.6389 | 0.54492 | 3242.1667 | 0.72792 | 3273.4 | 2.4357 | 3290.0278 | 0.64336 | 3310.4 | 0.64286
3342.3 | 0.74765 |  | 3364.6 | 5.1994 | 3392.7222 | 7.1721 | 3408.2778 | 0.71212 | 3422.5556 | 1.2363 | 3431.2222 | 1.0555 | 3455.6 | 0.64085 | 3461.1 | 0.64185 | 3473.3333 | 2.081 | 3476.3333 | 2.3768 | 3494 | 9.8186 | 3496.2 | 0.68506 | 3376.975 | 0.71212 | 3390.1694 | 0.74765 | 3413.6944 | 0.71212 | 3429.425 | 0.64085 | 3437.6667 | 0.71212 | 3466.5917 | 0.64085 | 3450.8611 | 1.0555 | 3460.9944 | 0.68506 | 3484.9667 | 0.68506 | 3353.45 | 0.74765 | 3400.5 | 0.71212 | 3426.8889 | 1.0555 | 3458.35 | 0.64085 | 3474.8333 | 2.081 | 3495.1 | 0.68506
3527 | 6.6428 |  | 3549.4 | 21.4115 | 3577.4444 | 21.1255 | 3592.9444 | 13.8407 | 3607.1667 | 11.6423 | 3615.8889 | 18.9673 | 3640 | 10.6107 | 3645.7 | 0.64923 | 3658 | 4.7467 | 3661.0556 | 3.6951 | 3678.8 | 0.64336 | 3681 | 0.64286 | 3561.6972 | 6.6428 | 3574.8639 | 6.6428 | 3598.3611 | 11.6423 | 3614.0222 | 0.64923 | 3622.3611 | 3.6951 | 3651.1889 | 0.64923 | 3635.5278 | 3.6951 | 3645.7139 | 0.64286 | 3669.7139 | 0.64286 | 3538.2 | 6.6428 | 3585.1944 | 13.8407 | 3611.5278 | 11.6423 | 3642.85 | 0.64923 | 3659.5278 | 3.6951 | 3679.9 | 0.64286
3711.7 | 21.6846 |  | 3734.2 | 18.632 | 3762.2778 | 27.7421 | 3777.7778 | 10.4239 | 3792.0556 | 16.7935 | 3800.7778 | 24.0401 | 3824.9 | 1.6778 | 3830.5 | 0.63835 | 3842.7778 | 4.6991 | 3845.8333 | 8.5744 | 3863.6 | 0.64539 | 3866 | 1.0193 | 3746.4889 | 10.4239 | 3759.6833 | 16.7935 | 3783.2222 | 10.4239 | 3798.8639 | 0.63835 | 3807.1667 | 4.6991 | 3836.0028 | 0.63835 | 3820.3611 | 4.6991 | 3830.6083 | 0.64539 | 3854.5528 | 0.64539 | 3722.95 | 18.632 | 3770.0278 | 10.4239 | 3796.4167 | 16.7935 | 3827.7 | 0.63835 | 3844.3056 | 4.6991 | 3864.8 | 0.64539
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 155.9451 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38953.5723 | 1 | 0 | 38953.5723 | 1 | 0 |  | 8 | 183 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5744 | 1 | 0 | 38953.5744 | 1 | 0 |  | 192.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5766 | 1 | 0 | 38953.5766 | 1 | 0 |  | 377.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5787 | 1 | 0 | 38953.5787 | 1 | 0 |  | 562.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5808 | 1 | 0 |  | 1 | 0 |  | 746 | 921 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.583 | 1 | 0 | 38953.583 | 1 | 0 |  | 932 | 1107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5851 | 1 | 0 | 38953.5851 | 1 | 0 |  | 1116.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5872 | 1 | 0 | 38953.5873 | 1 | 0 |  | 1301.5 | 1476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5894 | 2 | 0 | 38953.5894 | 1 | 0 |  | 1486 | 1661 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127619 | 255338 | 127618.9988
38953.5915 | 4 | 1 | 38953.5915 | 7 | 4 |  | 1671 | 1846 | 0.2442 | 0.06105 | 0.42735 | 0.2442 | 0.002442 | 0.0006105 | 0.0042735 | 0.002442 | 0.0018315 | 0.0018315 | 85046 | 85046 | 254638.5872
38953.5937 | 1114 | 1144 | 38953.5937 | 1046 | 1096 |  | 1855.5 | 2030.5 | 68.0098 | 69.8413 | 63.8584 | 66.9109 | 0.6801 | 0.69841 | 0.63858 | 0.66911 | 0.018315 | 0.030525 | 7689.7409 | 10151.9151 | 25.6546
38953.5958 | 937 | 1043 | 38953.5958 | 937 | 910 |  | 2040.5 | 2215.5 | 57.2039 | 63.6752 | 57.2039 | 55.5556 | 0.57204 | 0.63675 | 0.57204 | 0.55556 | 0.064713 | 0.016484 | 1163.2979 | 3157.3493 | 53.3794
38953.5979 | 1016 | 983 | 38953.598 | 980 | 950 |  | 2225.5 | 2400.5 | 62.0269 | 60.0122 | 59.8291 | 57.9976 | 0.62027 | 0.60012 | 0.59829 | 0.57998 | 0.020147 | 0.018315 | 6624.4165 | 10054.0807 | 55.9421
38953.6001 | 2014 | 0 | 38953.6001 | 2206 | 0 |  | 2410 | 2585 | 122.9548 | 0 | 134.6764 | 0 | 1.2295 | 0 | 1.3468 | 0 | 1.2295 | 1.3468 | 26.8312 | 15.7924 | 25.6016
38953.6022 | 2482 | 0 | 38953.6022 | 2066 | 0 |  | 2595 | 2770 | 151.5263 | 0 | 126.1294 | 0 | 1.5153 | 0 | 1.2613 | 0 | 1.5153 | 1.2613 | 2.9162 | 23.6389 | 1.4009
38953.6044 | 2529 | 0 | 38953.6044 | 2147 | 0 |  | 2779.5 | 2954.5 | 154.3956 | 0 | 131.0745 | 0 | 1.544 | 0 | 1.3107 | 0 | 1.544 | 1.3107 | 1.0036 | 18.9744 | 0.5404
38953.6065 | 2030 | 0 | 38953.6065 | 2288 | 0 |  | 2964.5 | 3139.5 | 123.9316 | 0 | 139.6825 | 0 | 1.2393 | 0 | 1.3968 | 0 | 1.2393 | 1.3968 | 25.8315 | 11.6425 | 24.5922
38953.6086 | 2409 | 0 | 38953.6086 | 2361 | 0 |  | 3149 | 3324 | 147.0696 | 0 | 144.1392 | 0 | 1.4707 | 0 | 1.4414 | 0 | 1.4707 | 1.4414 | 6.0349 | 8.1906 | 4.5642
38953.6108 | 2538 | 0 | 38953.6108 | 2360 | 0 |  | 3334 | 3509 | 154.9451 | 0 | 144.0781 | 0 | 1.5495 | 0 | 1.4408 | 0 | 1.5495 | 1.4408 | 0.64539 | 8.2364 | 0.90406
38953.6129 | 2282 | 0 | 38953.6129 | 2537 | 0 |  | 3518.5 | 3693.5 | 139.3162 | 0 | 154.884 | 0 | 1.3932 | 0 | 1.5488 | 0 | 1.3932 | 1.5488 | 11.936 | 0.68506 | 10.5429
38953.615 | 2196 | 0 | 38953.6151 | 1981 | 0 |  | 3703.5 | 3878.5 | 134.0659 | 0 | 120.9402 | 0 | 1.3407 | 0 | 1.2094 | 0 | 1.3407 | 1.2094 | 16.3197 | 28.944 | 14.979
38953.6172 | 2265 | 0 | 38953.6172 | 2155 | 0 |  | 3888.5 | 4063.5 | 138.2784 | 0 | 131.5629 | 0 | 1.3828 | 0 | 1.3156 | 0 | 1.3828 | 1.3156 | 12.7762 | 18.5327 | 11.3934

## E10-F12
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.5556 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38953.5722 | 1 | 0 | 38953.5723 | 1 | 0 |  | 5 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5744 | 1 | 0 | 38953.5744 | 1 | 0 |  | 190 | 365 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5765 | 1 | 0 | 38953.5765 | 1 | 0 |  | 374.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5787 | 1 | 0 | 38953.5787 | 1 | 0 |  | 559.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5808 | 1 | 0 | 38953.5808 | 1 | 0 |  | 744.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5829 | 1 | 0 | 38953.583 | 1 | 0 |  | 929 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5851 | 1 | 0 | 38953.5851 | 1 | 0 |  | 1113.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5872 | 1 | 0 | 38953.5872 | 1 | 0 |  | 1298.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5894 | 1 | 0 | 38953.5894 | 1 | 0 |  | 1483.5 | 1658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5915 | 1 | 0 | 38953.5915 | 1 | 0 |  | 1668 | 1843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5936 | 1 | 0 | 38953.5936 | 1 | 0 |  | 1853 | 2028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5958 | 1 | 0 | 38953.5958 | 1 | 0 |  | 2037.5 | 2212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5979 | 1 | 0 | 38953.5979 | 1 | 0 |  | 2222.5 | 2397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.6 | 2346 | 0 | 38953.6001 | 2093 | 0 |  | 2407.5 | 2582.5 | 143.2234 | 0 | 127.7778 | 0 | 1.4322 | 0 | 1.2778 | 0 | 1.4322 | 1.2778 | 9.3086 | 22.5217 | 7.8764
38953.6022 | 2066 | 0 | 38953.6022 | 2142 | 0 |  | 2592 | 2767 | 126.1294 | 0 | 130.7692 | 0 | 1.2613 | 0 | 1.3077 | 0 | 1.2613 | 1.3077 | 24.1229 | 19.719 | 22.8616
38953.6043 | 2235 | 0 | 38953.6043 | 2530 | 0 |  | 2776.5 | 2951.5 | 136.4469 | 0 | 154.4567 | 0 | 1.3645 | 0 | 1.5446 | 0 | 1.3645 | 1.5446 | 14.7374 | 1.3589 | 13.3729
38953.6065 | 2071 | 0 | 38953.6065 | 2253 | 0 |  | 2961.5 | 3136.5 | 126.4347 | 0 | 137.5458 | 0 | 1.2643 | 0 | 1.3755 | 0 | 1.2643 | 1.3755 | 23.8233 | 13.8207 | 22.5589
38953.6086 | 2529 | 0 | 38953.6086 | 2427 | 0 |  | 3146.5 | 3321.5 | 154.3956 | 0 | 148.1685 | 0 | 1.544 | 0 | 1.4817 | 0 | 1.544 | 1.4817 | 1.399 | 5.6605 | 0.14498
38953.6107 | 2510 | 0 | 38953.6108 | 2548 | 0 |  | 3331 | 3506 | 153.2357 | 0 | 155.5556 | 0 | 1.5324 | 0 | 1.5556 | 0 | 1.5324 | 1.5556 | 2.1665 | 0.64286 | 0.63418
38953.6129 | 1639 | 0 | 38953.6129 | 2115 | 0 |  | 3515.5 | 3690.5 | 100.0611 | 0 | 129.1209 | 0 | 1.0006 | 0 | 1.2912 | 0 | 1.0006 | 1.2912 | 56.46 | 21.2473 | 55.4594
38953.615 | 2473 | 0 | 38953.615 | 2221 | 0 |  | 3700.5 | 3875.5 | 150.9768 | 0 | 135.5922 | 0 | 1.5098 | 0 | 1.3559 | 0 | 1.5098 | 1.3559 | 3.6951 | 15.4606 | 2.1853
38953.6172 | 1937 | 0 | 38953.6172 | 2361 | 0 |  | 3885.5 | 4060.5 | 118.254 | 0 | 144.1392 | 0 | 1.1825 | 0 | 1.4414 | 0 | 1.1825 | 1.4414 | 32.3893 | 8.6141 | 31.2067

## E10-F11
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.0061 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38953.5722 | 1 | 0 | 38953.5722 | 1 | 0 |  | 2.5 | 177.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5743 | 1 | 0 | 38953.5744 | 1 | 0 |  | 187 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5765 | 1 | 0 | 38953.5765 | 1 | 0 |  | 372 | 547 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5786 | 1 | 0 | 38953.5786 | 1 | 0 |  | 556.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5808 | 1 | 0 | 38953.5808 | 1 | 0 |  | 741.5 | 916.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5829 | 1 | 0 | 38953.5829 | 1 | 0 |  | 926.5 | 1101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.585 | 1 | 0 | 38953.5851 | 1 | 0 |  | 1111 | 1286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5872 | 1 | 0 | 38953.5872 | 1 | 0 |  | 1295.5 | 1470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5893 | 1 | 0 | 38953.5893 | 1 | 0 |  | 1480.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5915 | 1 | 0 | 38953.5915 | 1 | 0 |  | 1665.5 | 1840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5936 | 1 | 0 | 38953.5936 | 1 | 0 |  | 1850 | 2025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38953.5957 | 1 | 1 | 38953.5958 | 1 | 0 |  | 2035 | 2210 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 652485718.44 | 255438 | 255238.0783
38953.5979 | 2 | 1 | 38953.5979 | 1 | 1 |  | 2219.5 | 2394.5 | 0.1221 | 0.06105 | 0.06105 | 0.06105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 255337.9609 | 652230180.3297 | 255237.9609
38953.6 | 2492 | 0 | 38953.6 | 2430 | 0 |  | 2404.5 | 2579.5 | 152.1368 | 0 | 148.3516 | 0 | 1.5214 | 0 | 1.4835 | 0 | 1.5214 | 1.4835 | 2.5433 | 5.1597 | 1.022
38953.6021 | 1982 | 0 | 38953.6022 | 2207 | 0 |  | 2589 | 2764 | 121.0012 | 0 | 134.7375 | 0 | 1.21 | 0 | 1.3474 | 0 | 1.21 | 1.3474 | 28.9294 | 15.7852 | 27.7194
38953.6043 | 2281 | 0 | 38953.6043 | 2224 | 0 |  | 2774 | 2949 | 139.2552 | 0 | 135.7753 | 0 | 1.3926 | 0 | 1.3578 | 0 | 1.3926 | 1.3578 | 12.0289 | 14.9002 | 10.6364
38953.6064 | 2339 | 0 | 38953.6064 | 2503 | 0 |  | 2958.5 | 3133.5 | 142.7961 | 0 | 152.8083 | 0 | 1.428 | 0 | 1.5281 | 0 | 1.428 | 1.5281 | 9.251 | 2.0927 | 7.823
38953.6086 | 2320 | 0 | 38953.6086 | 2365 | 0 |  | 3143.5 | 3318.5 | 141.6361 | 0 | 144.3834 | 0 | 1.4164 | 0 | 1.4438 | 0 | 1.4164 | 1.4438 | 10.1457 | 8.0499 | 8.7293
38953.6107 | 2481 | 0 | 38953.6107 | 2539 | 0 |  | 3328.5 | 3503.5 | 151.4652 | 0 | 155.0061 | 0 | 1.5147 | 0 | 1.5501 | 0 | 1.5147 | 1.5501 | 2.998 | 0.64514 | 1.4833
38953.6128 | 1828 | 0 | 38953.6129 | 2060 | 0 |  | 3513 | 3688 | 111.5995 | 0 | 125.7631 | 0 | 1.116 | 0 | 1.2576 | 0 | 1.116 | 1.2576 | 39.791 | 24.0476 | 38.675
38953.615 | 1946 | 0 | 38953.615 | 2300 | 0 |  | 3698 | 3873 | 118.8034 | 0 | 140.4151 | 0 | 1.188 | 0 | 1.4042 | 0 | 1.188 | 1.4042 | 31.3145 | 11.1035 | 30.1265
38953.6171 | 1933 | 0 | 38953.6171 | 2204 | 0 |  | 3882.5 | 4057.5 | 118.0098 | 0 | 134.5543 | 0 | 1.1801 | 0 | 1.3455 | 0 | 1.1801 | 1.3455 | 32.1976 | 15.9428 | 31.0175

## E9-F12
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 155.5177 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38953.5722 | 1 | 0 | 38953.5722 | 1 | 0 |  | -0.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5743 | 1 | 0 | 38953.5743 | 1 | 0 |  | 184.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5764 | 1 | 0 | 38953.5765 | 1 | 0 |  | 369 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5786 | 1 | 0 | 38953.5786 | 1 | 0 |  | 554 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5807 | 1 | 0 | 38953.5807 | 1 | 0 |  | 738.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5829 | 1 | 0 | 38953.5829 | 1 | 0 |  | 923.5 | 1098.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.585 | 1 | 0 | 38953.585 | 1 | 0 |  | 1108 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5871 | 1 | 0 | 38953.5872 | 1 | 0 |  | 1293 | 1468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5893 | 1 | 0 | 38953.5893 | 1 | 0 |  | 1477.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5914 | 1 | 0 | 38953.5914 | 1 | 0 |  | 1662.5 | 1837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5936 | 1 | 0 | 38953.5936 | 1 | 0 |  | 1847.5 | 2022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254638 | 254638 | 254637.9994
38953.5957 | 2 | 2 | 38953.5957 | 1 | 0 |  | 2032 | 2207 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 324075236.22 | 254638 | 127119.0785
38953.5978 | 1 | 2 | 38953.5979 | 1 | 1 |  | 2217 | 2392 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 254637.9215 | 648404910.3961 | 127218.9804
38953.6 | 2052 | 0 | 38953.6 | 2363 | 0 |  | 2401.5 | 2576.5 | 125.2747 | 0 | 144.2613 | 0 | 1.2527 | 0 | 1.4426 | 0 | 1.2527 | 1.4426 | 24.1413 | 7.8028 | 22.8886
38953.6021 | 1957 | 0 | 38953.6021 | 2463 | 0 |  | 2586.5 | 2761.5 | 119.475 | 0 | 150.3663 | 0 | 1.1947 | 0 | 1.5037 | 0 | 1.1947 | 1.5037 | 30.1676 | 3.4259 | 28.9729
38953.6042 | 2486 | 0 | 38953.6043 | 2060 | 0 |  | 2771 | 2946 | 151.7705 | 0 | 125.7631 | 0 | 1.5177 | 0 | 1.2576 | 0 | 1.5177 | 1.2576 | 2.469 | 23.6592 | 0.95132
38953.6064 | 2187 | 0 | 38953.6064 | 2058 | 0 |  | 2956 | 3131 | 133.5165 | 0 | 125.641 | 0 | 1.3352 | 0 | 1.2564 | 0 | 1.3352 | 1.2564 | 16.4783 | 23.7794 | 15.1431
38953.6085 | 2505 | 0 | 38953.6085 | 2531 | 0 |  | 3140.5 | 3315.5 | 152.9304 | 0 | 154.5177 | 0 | 1.5293 | 0 | 1.5452 | 0 | 1.5293 | 1.5452 | 1.6918 | 0.64718 | 0.16251
38953.6107 | 2075 | 0 | 38953.6107 | 2242 | 0 |  | 3325.5 | 3500.5 | 126.6789 | 0 | 136.8742 | 0 | 1.2668 | 0 | 1.3687 | 0 | 1.2668 | 1.3687 | 22.7653 | 13.6209 | 21.4985
38953.6128 | 1827 | 0 | 38953.6128 | 2498 | 0 |  | 3510.5 | 3685.5 | 111.5385 | 0 | 152.5031 | 0 | 1.1154 | 0 | 1.525 | 0 | 1.1154 | 1.525 | 39.4297 | 1.9768 | 38.3143
38953.6149 | 2045 | 0 | 38953.615 | 1999 | 0 |  | 3695 | 3870 | 124.8474 | 0 | 122.0391 | 0 | 1.2485 | 0 | 1.2204 | 0 | 1.2485 | 1.2204 | 24.5663 | 27.4327 | 23.3178
38953.6171 | 1873 | 0 | 38953.6171 | 2258 | 0 |  | 3880 | 4055 | 114.3468 | 0 | 137.851 | 0 | 1.1435 | 0 | 1.3785 | 0 | 1.1435 | 1.3785 | 36.0053 | 12.8158 | 34.8619

## E9-F11
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 155.9451 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38953.5721 | 1 | 0 | 38953.5722 | 1 | 0 |  | -3.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5743 | 1 | 0 | 38953.5743 | 1 | 0 |  | 181.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5764 | 1 | 0 | 38953.5764 | 1 | 0 |  | 366.5 | 541.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5786 | 1 | 0 | 38953.5786 | 1 | 0 |  | 551 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5807 | 1 | 0 | 38953.5807 | 1 | 0 |  | 735.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5828 | 1 | 0 | 38953.5828 | 1 | 0 |  | 920.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.585 | 1 | 0 | 38953.585 | 1 | 0 |  | 1105.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5871 | 1 | 0 | 38953.5871 | 1 | 0 |  | 1290 | 1465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5892 | 1 | 0 | 38953.5893 | 1 | 0 |  | 1475 | 1650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5914 | 1 | 0 | 38953.5914 | 1 | 0 |  | 1659.5 | 1834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5935 | 1 | 0 | 38953.5935 | 1 | 0 |  | 1844.5 | 2019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38953.5957 | 2 | 6 | 38953.5957 | 2 | 3 |  | 2029.5 | 2204.5 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 63846.8456 | 256442.9599 | 42423.1238
38953.5978 | 2 | 6 | 38953.5978 | 2 | 3 |  | 2214 | 2389 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 63846.8456 | 256442.9599 | 42423.1238
38953.5999 | 2105 | 0 | 38953.6 | 2249 | 0 |  | 2399 | 2574 | 128.5104 | 0 | 137.3016 | 0 | 1.2851 | 0 | 1.373 | 0 | 1.2851 | 1.373 | 21.3482 | 13.5785 | 20.0631
38953.6021 | 2180 | 0 | 38953.6021 | 2293 | 0 |  | 2583.5 | 2758.5 | 133.0891 | 0 | 139.9878 | 0 | 1.3309 | 0 | 1.3999 | 0 | 1.3309 | 1.3999 | 17.1734 | 11.399 | 15.8425
38953.6042 | 2486 | 0 | 38953.6042 | 1988 | 0 |  | 2768.5 | 2943.5 | 151.7705 | 0 | 121.3675 | 0 | 1.5177 | 0 | 1.2137 | 0 | 1.5177 | 1.2137 | 2.7506 | 28.4899 | 1.2329
38953.6064 | 2534 | 0 | 38953.6064 | 2140 | 0 |  | 2953 | 3128 | 154.7009 | 0 | 130.6471 | 0 | 1.547 | 0 | 1.3065 | 0 | 1.547 | 1.3065 | 0.80426 | 19.3636 | 0.74275
38953.6085 | 1982 | 0 | 38953.6085 | 2328 | 0 |  | 3138 | 3313 | 121.0012 | 0 | 142.1245 | 0 | 1.21 | 0 | 1.4212 | 0 | 1.21 | 1.4212 | 28.8789 | 9.7242 | 27.6689
38953.6106 | 2021 | 0 | 38953.6106 | 2520 | 0 |  | 3322.5 | 3497.5 | 123.3822 | 0 | 153.8462 | 0 | 1.2338 | 0 | 1.5385 | 0 | 1.2338 | 1.5385 | 26.3919 | 1.3643 | 25.1581
38953.6128 | 2094 | 0 | 38953.6128 | 2326 | 0 |  | 3507.5 | 3682.5 | 127.8388 | 0 | 142.0024 | 0 | 1.2784 | 0 | 1.42 | 0 | 1.2784 | 1.42 | 21.9857 | 9.8186 | 20.7073
38953.6149 | 2341 | 0 | 38953.6149 | 2385 | 0 |  | 3692.5 | 3867.5 | 142.9182 | 0 | 145.6044 | 0 | 1.4292 | 0 | 1.456 | 0 | 1.4292 | 1.456 | 9.1149 | 7.1019 | 7.6857
38953.617 | 2307 | 0 | 38953.6171 | 2538 | 0 |  | 3877 | 4052 | 140.8425 | 0 | 154.9451 | 0 | 1.4084 | 0 | 1.5495 | 0 | 1.4084 | 1.5495 | 10.723 | 0.64539 | 9.3146

## E9-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 152.2821 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38953.5721 | 1 | 0 | 38953.5721 | 3 | 0 |  | -6 | 169 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 249338 | 83046 | 249337.9994
38953.5742 | 1 | 0 | 38953.5743 | 1 | 0 |  | 178.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5764 | 1 | 0 | 38953.5764 | 1 | 0 |  | 363.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5785 | 1 | 0 | 38953.5785 | 1 | 0 |  | 548.5 | 723.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5807 | 1 | 0 | 38953.5807 | 1 | 0 |  | 733 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5828 | 1 | 0 | 38953.5828 | 1 | 0 |  | 918 | 1093 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5849 | 1 | 0 | 38953.585 | 1 | 0 |  | 1102.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5871 | 1 | 0 | 38953.5871 | 1 | 0 |  | 1287.5 | 1462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5892 | 1 | 0 | 38953.5892 | 1 | 0 |  | 1472 | 1647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5914 | 1 | 0 | 38953.5914 | 1 | 0 |  | 1657 | 1832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38953.5935 | 2 | 1 | 38953.5935 | 2 | 1 |  | 1841.5 | 2016.5 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249038.1203
38953.5956 | 1194 | 1182 | 38953.5956 | 1184 | 908 |  | 2026.5 | 2201.5 | 72.8938 | 72.1612 | 72.2833 | 55.4335 | 0.72894 | 0.72161 | 0.72283 | 0.55433 | 0.007326 | 0.1685 | 203.1307 | 188.1659 | 6.5397
38953.5978 | 1031 | 1071 | 38953.5978 | 1159 | 1131 |  | 2211 | 2386 | 62.9426 | 65.3846 | 70.757 | 69.0476 | 0.62943 | 0.65385 | 0.70757 | 0.69048 | 0.02442 | 0.017094 | 3170.961 | 17416.2881 | 36.4276
38953.5999 | 1983 | 0 | 38953.5999 | 2124 | 0 |  | 2396 | 2571 | 121.0623 | 0 | 129.6703 | 0 | 1.2106 | 0 | 1.2967 | 0 | 1.2106 | 1.2967 | 25.7882 | 17.4379 | 24.5776
38953.602 | 2414 | 0 | 38953.6021 | 2173 | 0 |  | 2580.5 | 2755.5 | 147.3748 | 0 | 132.6618 | 0 | 1.4737 | 0 | 1.3266 | 0 | 1.4737 | 1.3266 | 3.3297 | 14.7897 | 1.856
38953.6042 | 2097 | 0 | 38953.6042 | 2298 | 0 |  | 2765.5 | 2940.5 | 128.022 | 0 | 140.293 | 0 | 1.2802 | 0 | 1.4029 | 0 | 1.2802 | 1.4029 | 18.9499 | 8.5457 | 17.6697
38953.6063 | 2478 | 0 | 38953.6063 | 2113 | 0 |  | 2950.5 | 3125.5 | 151.2821 | 0 | 128.9988 | 0 | 1.5128 | 0 | 1.29 | 0 | 1.5128 | 1.29 | 0.66102 | 18.0492 | 0.8518
38953.6085 | 1977 | 0 | 38953.6085 | 2167 | 0 |  | 3135 | 3310 | 120.696 | 0 | 132.2955 | 0 | 1.207 | 0 | 1.323 | 0 | 1.207 | 1.323 | 26.17 | 15.1075 | 24.963
38953.6106 | 2259 | 2 | 38953.6106 | 2175 | 1 |  | 3320 | 3495 | 137.9121 | 0.1221 | 132.7839 | 0.06105 | 1.3791 | 0.001221 | 1.3278 | 0.0006105 | 1.3779 | 1.3272 | 10.4919 | 14.7556 | 1500.4316
38953.6127 | 2444 | 9 | 38953.6128 | 1902 | 20 |  | 3504.5 | 3679.5 | 149.2063 | 0.54945 | 116.1172 | 1.221 | 1.4921 | 0.0054945 | 1.1612 | 0.01221 | 1.4866 | 1.149 | 2.081 | 64.3261 | 179.9819
38953.6149 | 1938 | 1 | 38953.6149 | 2099 | 1 |  | 3689.5 | 3864.5 | 118.315 | 0.06105 | 128.1441 | 0.06105 | 1.1832 | 0.0006105 | 1.2814 | 0.0006105 | 1.1825 | 1.2808 | 28.8026 | 18.8768 | 8819.0462
38953.617 | 2064 | 300 | 38953.617 | 1798 | 101 |  | 3874.5 | 4049.5 | 126.0073 | 18.315 | 109.768 | 6.1661 | 1.2601 | 0.18315 | 1.0977 | 0.061661 | 1.0769 | 1.036 | 37.4534 | 48.7889 | 14.2508

## D8-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 157.6545 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38953.572 | 1 | 0 | 38953.572 | 1 | 0 |  | -14.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5742 | 1 | 0 | 38953.5742 | 1 | 0 |  | 170.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5763 | 1 | 0 | 38953.5763 | 1 | 0 |  | 355 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5784 | 1 | 0 | 38953.5784 | 1 | 0 |  | 540 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5806 | 1 | 0 | 38953.5806 | 1 | 0 |  | 724.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5827 | 1 | 0 | 38953.5827 | 1 | 0 |  | 909.5 | 1084.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5848 | 1 | 0 | 38953.5849 | 1 | 0 |  | 1094 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.587 | 1 | 0 | 38953.587 | 1 | 0 |  | 1279 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5891 | 1 | 0 | 38953.5891 | 1 | 0 |  | 1463.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
| 1 | 0 | 38953.5913 | 1 | 0 |  | 1649 | 1824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5934 | 1 | 0 | 38953.5934 | 1 | 0 |  | 1833.5 | 2008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5955 | 1 | 0 | 38953.5956 | 1 | 0 |  | 2018 | 2193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5977 | 1 | 0 | 38953.5977 | 1 | 0 |  | 2202.5 | 2377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
38953.5998 | 2365 | 0 | 38953.5998 | 2370 | 0 |  | 2387.5 | 2562.5 | 144.3834 | 0 | 144.6886 | 0 | 1.4438 | 0 | 1.4469 | 0 | 1.4438 | 1.4469 | 9.1915 | 8.9612 | 7.7477
38953.602 | 1991 | 0 | 38953.602 | 2043 | 0 |  | 2572.5 | 2747.5 | 121.5507 | 0 | 124.7253 | 0 | 1.2155 | 0 | 1.2473 | 0 | 1.2155 | 1.2473 | 29.7027 | 26.4014 | 28.4872
38953.6041 | 2414 | 0 | 38953.6041 | 2270 | 0 |  | 2757 | 2932 | 147.3748 | 0 | 138.5836 | 0 | 1.4737 | 0 | 1.3858 | 0 | 1.4737 | 1.3858 | 6.9751 | 13.7612 | 5.5014
38953.6062 | 2060 | 0 | 38953.6062 | 2421 | 0 |  | 2942 | 3117 | 125.7631 | 0 | 147.8022 | 0 | 1.2576 | 0 | 1.478 | 0 | 1.2576 | 1.478 | 25.3583 | 6.6658 | 24.1006
38953.6084 | 2249 | 0 | 38953.6084 | 2203 | 0 |  | 3126.5 | 3301.5 | 137.3016 | 0 | 134.4933 | 0 | 1.373 | 0 | 1.3449 | 0 | 1.373 | 1.3449 | 14.8235 | 17.2211 | 13.4505
38953.6105 | 2338 | 0 | 38953.6105 | 2484 | 0 |  | 3311.5 | 3486.5 | 142.735 | 0 | 151.6484 | 0 | 1.4274 | 0 | 1.5165 | 0 | 1.4274 | 1.5165 | 10.4525 | 3.9605 | 9.0252
38953.6127 | 2432 | 0 | 38953.6127 | 2455 | 0 |  | 3496.5 | 3671.5 | 148.4737 | 0 | 149.8779 | 0 | 1.4847 | 0 | 1.4988 | 0 | 1.4847 | 1.4988 | 6.1834 | 5.1886 | 4.6987
38953.6148 | 2330 | 0 | 38953.6148 | 2488 | 0 |  | 3681 | 3856 | 142.2466 | 0 | 151.8926 | 0 | 1.4225 | 0 | 1.5189 | 0 | 1.4225 | 1.5189 | 10.8318 | 3.7934 | 9.4093
38953.6169 | 2566 | 0 | 38953.6169 | 2376 | 0 |  | 3865.5 | 4040.5 | 156.6545 | 0 | 145.0549 | 0 | 1.5665 | 0 | 1.4505 | 0 | 1.5665 | 1.4505 | 0.63835 | 8.686 | 0.9282

## D8-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 152.7094 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38953.572 | 1 | 0 | 38953.572 | 1 | 0 |  | -17.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5741 | 1 | 0 | 38953.5741 | 1 | 0 |  | 167.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5763 | 1 | 0 | 38953.5763 | 1 | 0 |  | 352.5 | 527.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5784 | 1 | 0 | 38953.5784 | 1 | 0 |  | 537 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5805 | 1 | 0 | 38953.5806 | 1 | 0 |  | 722 | 897 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5827 | 1 | 0 | 38953.5827 | 1 | 0 |  | 906.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5848 | 1 | 0 | 38953.5848 | 1 | 0 |  | 1091.5 | 1266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5869 | 1 | 0 | 38953.587 | 1 | 0 |  | 1276 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5891 | 1 | 0 | 38953.5891 | 1 | 0 |  | 1461 | 1636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5912 | 1 | 0 | 38953.5912 | 1 | 0 |  | 1645.5 | 1820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5934 | 1 | 0 | 38953.5934 | 1 | 0 |  | 1830.5 | 2005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5955 | 1 | 0 | 38953.5955 | 1 | 0 |  | 2015 | 2190 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5976 | 1 | 0 | 38953.5977 | 1 | 0 |  | 2200 | 2375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38953.5998 | 2392 | 0 | 38953.5998 | 2485 | 0 |  | 2384.5 | 2559.5 | 146.0317 | 0 | 151.7094 | 0 | 1.4603 | 0 | 1.5171 | 0 | 1.4603 | 1.5171 | 4.5727 | 0.65915 | 3.1124
38953.6019 | 2255 | 0 | 38953.6019 | 2148 | 0 |  | 2569.5 | 2744.5 | 137.6679 | 0 | 131.1355 | 0 | 1.3767 | 0 | 1.3114 | 0 | 1.3767 | 1.3114 | 10.9259 | 16.4516 | 9.5493
38953.6041 | 1956 | 0 | 38953.6041 | 2084 | 0 |  | 2754.5 | 2929.5 | 119.4139 | 0 | 127.2283 | 0 | 1.1941 | 0 | 1.2723 | 0 | 1.1941 | 1.2723 | 27.8824 | 20.0278 | 26.6883
38953.6062 | 2084 | 0 | 38953.6062 | 2314 | 0 |  | 2939 | 3114 | 127.2283 | 0 | 141.2698 | 0 | 1.2723 | 0 | 1.4127 | 0 | 1.2723 | 1.4127 | 20.0278 | 8.0977 | 18.7555
38953.6083 | 2138 | 0 | 38953.6084 | 2452 | 0 |  | 3124 | 3299 | 130.525 | 0 | 149.6947 | 0 | 1.3053 | 0 | 1.4969 | 0 | 1.3053 | 1.4969 | 16.9963 | 2.0139 | 15.691
38953.6105 | 1993 | 0 | 38953.6105 | 2163 | 0 |  | 3308.5 | 3483.5 | 121.6728 | 0 | 132.0513 | 0 | 1.2167 | 0 | 1.3205 | 0 | 1.2167 | 1.3205 | 25.5083 | 15.644 | 24.2916
38953.6126 | 2292 | 0 | 38953.6126 | 2402 | 0 |  | 3493.5 | 3668.5 | 139.9267 | 0 | 146.6422 | 0 | 1.3993 | 0 | 1.4664 | 0 | 1.3993 | 1.4664 | 9.1353 | 4.1374 | 7.736
38953.6148 | 2089 | 0 | 38953.6148 | 2021 | 0 |  | 3678.5 | 3853.5 | 127.5336 | 0 | 123.3822 | 0 | 1.2753 | 0 | 1.2338 | 0 | 1.2753 | 1.2338 | 19.7405 | 23.7694 | 18.4652
38953.6169 | 2458 | 0 | 38953.6169 | 2377 | 0 |  | 3863 | 4038 | 150.0611 | 0 | 145.116 | 0 | 1.5006 | 0 | 1.4512 | 0 | 1.5006 | 1.4512 | 1.7648 | 5.2326 | 0.26424

## D7-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.4335 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38953.5719 | 1 | 0 | 38953.5719 | 1 | 0 |  | -25.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.574 | 1 | 0 | 38953.574 | 1 | 0 |  | 159 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5762 | 1 | 0 | 38953.5762 | 1 | 0 |  | 344 | 519 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5783 | 1 | 0 | 38953.5783 | 1 | 0 |  | 528.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5804 | 1 | 0 | 38953.5805 | 1 | 0 |  | 713.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5826 | 1 | 0 | 38953.5826 | 1 | 0 |  | 898.5 | 1073.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5847 | 1 | 0 | 38953.5847 | 1 | 0 |  | 1083 | 1258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5869 | 1 | 0 | 38953.5869 | 1 | 0 |  | 1268 | 1443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.589 | 1 | 0 | 38953.589 | 1 | 0 |  | 1452.5 | 1627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5911 | 1 | 2 | 38953.5911 | 1 | 1 |  | 1637.5 | 1812.5 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 256137.9219 | 656066550.6416 | 127968.9805
38953.5933 | 1 | 2 | 38953.5933 | 1 | 1 |  | 1822 | 1997 | 0.06105 | 0.1221 | 0.06105 | 0.06105 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 256137.9219 | 656066550.6416 | 127968.9805
38953.5954 | 1 | 1 | 38953.5954 | 1 | 0 |  | 2007 | 2182 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 656066750.44 | 256138 | 255938.0781
38953.5975 | 2 | 2 | 38953.5976 | 1 | 0 |  | 2191.5 | 2366.5 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 327905306.22 | 256138 | 127869.0781
38953.5997 | 1986 | 0 | 38953.5997 | 2490 | 0 |  | 2376.5 | 2551.5 | 121.2454 | 0 | 152.0147 | 0 | 1.2125 | 0 | 1.5201 | 0 | 1.2125 | 1.5201 | 29.0222 | 2.9068 | 27.8097
38953.6018 | 2070 | 0 | 38953.6018 | 2283 | 0 |  | 2561 | 2736 | 126.3736 | 0 | 139.3773 | 0 | 1.2637 | 0 | 1.3938 | 0 | 1.2637 | 1.3938 | 23.7865 | 12.2374 | 22.5227
38953.604 | 2026 | 0 | 38953.604 | 2241 | 0 |  | 2746 | 2921 | 123.6874 | 0 | 136.8132 | 0 | 1.2369 | 0 | 1.3681 | 0 | 1.2369 | 1.3681 | 26.4748 | 14.3409 | 25.238
38953.6061 | 2532 | 0 | 38953.6061 | 2534 | 0 |  | 2930.5 | 3105.5 | 154.5788 | 0 | 154.7009 | 0 | 1.5458 | 0 | 1.547 | 0 | 1.5458 | 1.547 | 1.1998 | 1.12 | 0.34595
38953.6082 | 2453 | 0 | 38953.6083 | 2330 | 0 |  | 3115.5 | 3290.5 | 149.7558 | 0 | 142.2466 | 0 | 1.4976 | 0 | 1.4225 | 0 | 1.4976 | 1.4225 | 4.459 | 9.9734 | 2.9615
38953.6104 | 2350 | 0 | 38953.6104 | 2546 | 0 |  | 3300.5 | 3475.5 | 143.4676 | 0 | 155.4335 | 0 | 1.4347 | 0 | 1.5543 | 0 | 1.4347 | 1.5543 | 9.0374 | 0.64336 | 7.6028
38953.6125 | 2462 | 0 | 38953.6125 | 1892 | 0 |  | 3485 | 3660 | 150.3053 | 0 | 115.5067 | 0 | 1.5031 | 0 | 1.1551 | 0 | 1.5031 | 1.1551 | 4.0772 | 35.4323 | 2.5741
38953.6147 | 2009 | 0 | 38953.6147 | 2385 | 0 |  | 3669.5 | 3844.5 | 122.6496 | 0 | 145.6044 | 0 | 1.2265 | 0 | 1.456 | 0 | 1.2265 | 1.456 | 27.545 | 7.4373 | 26.3186
38953.6168 | 2285 | 0 | 38953.6168 | 2070 | 0 |  | 3854.5 | 4029.5 | 139.4994 | 0 | 126.3736 | 0 | 1.395 | 0 | 1.2637 | 0 | 1.395 | 1.2637 | 12.1392 | 23.7865 | 10.7442

## D7-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 157.044 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38953.5719 | 1 | 0 | 38953.5719 | 1 | 0 |  | -28.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.574 | 1 | 0 | 38953.574 | 1 | 0 |  | 156.5 | 331.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5761 | 1 | 0 | 38953.5761 | 1 | 0 |  | 341 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5783 | 1 | 0 | 38953.5783 | 1 | 0 |  | 526 | 701 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5804 | 1 | 0 | 38953.5804 | 1 | 0 |  | 710.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5825 | 1 | 0 | 38953.5826 | 1 | 0 |  | 895.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5847 | 1 | 0 | 38953.5847 | 1 | 0 |  | 1080.5 | 1255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.5868 | 1 | 0 | 38953.5868 | 1 | 0 |  | 1265 | 1440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 257137.9994
38953.589 | 2 | 1 | 38953.589 | 1 | 0 |  | 1449.5 | 1624.5 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257138 | 257138 | 256838.1166
38953.5911 | 2 | 6 | 38953.5911 | 2 | 3 |  | 1634.5 | 1809.5 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 64296.8467 | 258242.925 | 42723.1229
38953.5932 | 2 | 6 | 38953.5933 | 2 | 3 |  | 1819.5 | 1994.5 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 64296.8467 | 258242.925 | 42723.1229
38953.5954 | 2 | 6 | 38953.5954 | 2 | 3 |  | 2004 | 2179 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 64296.8467 | 258242.925 | 42723.1229
38953.5975 | 2 | 6 | 38953.5975 | 2 | 3 |  | 2189 | 2364 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 64296.8467 | 258242.925 | 42723.1229
38953.5997 | 2019 | 0 | 38953.5997 | 2341 | 0 |  | 2373.5 | 2548.5 | 123.2601 | 0 | 142.9182 | 0 | 1.2326 | 0 | 1.4292 | 0 | 1.2326 | 1.4292 | 27.4086 | 9.8838 | 26.176
38953.6018 | 2020 | 0 | 38953.6018 | 2122 | 0 |  | 2558.5 | 2733.5 | 123.3211 | 0 | 129.5482 | 0 | 1.2332 | 0 | 1.2955 | 0 | 1.2332 | 1.2955 | 27.3455 | 21.2243 | 26.1123
38953.6039 | 2058 | 0 | 38953.6039 | 2522 | 0 |  | 2743 | 2918 | 125.641 | 0 | 153.9683 | 0 | 1.2564 | 0 | 1.5397 | 0 | 1.2564 | 1.5397 | 24.9942 | 1.9976 | 23.7378
38953.6061 | 2474 | 0 | 38953.6061 | 2223 | 0 |  | 2928 | 3103 | 151.0379 | 0 | 135.7143 | 0 | 1.5104 | 0 | 1.3571 | 0 | 1.5104 | 1.3571 | 3.9766 | 15.7166 | 2.4662
38953.6082 | 2535 | 0 | 38953.6082 | 2473 | 0 |  | 3112.5 | 3287.5 | 154.7619 | 0 | 150.9768 | 0 | 1.5476 | 0 | 1.5098 | 0 | 1.5476 | 1.5098 | 1.4746 | 4.0186 | 0.073063
38953.6103 | 2369 | 0 | 38953.6104 | 2308 | 0 |  | 3297.5 | 3472.5 | 144.6276 | 0 | 140.9035 | 0 | 1.4463 | 0 | 1.409 | 0 | 1.4463 | 1.409 | 8.5851 | 11.4549 | 7.1388
38953.6125 | 2556 | 0 | 38953.6125 | 1941 | 0 |  | 3482.5 | 3657.5 | 156.044 | 0 | 118.4982 | 0 | 1.5604 | 0 | 1.185 | 0 | 1.5604 | 1.185 | 0.64085 | 32.5286 | 0.91959
38953.6146 | 2294 | 0 | 38953.6146 | 2014 | 0 |  | 3667 | 3842 | 140.0488 | 0 | 122.9548 | 0 | 1.4005 | 0 | 1.2295 | 0 | 1.4005 | 1.2295 | 12.1351 | 27.7249 | 10.7346
38953.6168 | 2423 | 0 | 38953.6168 | 2178 | 0 |  | 3851.5 | 4026.5 | 147.9243 | 0 | 132.967 | 0 | 1.4792 | 0 | 1.3297 | 0 | 1.4792 | 1.3297 | 6.1651 | 18.1074 | 4.6858

## D7-D8
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.7998 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38953.5718 | 1 | 0 | 38953.5718 | 1 | 0 |  | -31.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.574 | 1 | 0 | 38953.574 | 1 | 0 |  | 153.5 | 328.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5761 | 1 | 0 | 38953.5761 | 1 | 0 |  | 338.5 | 513.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5782 | 1 | 0 | 38953.5783 | 1 | 0 |  | 523 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5804 | 1 | 0 | 38953.5804 | 1 | 0 |  | 708 | 883 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5825 | 1 | 0 | 38953.5825 | 1 | 0 |  | 892.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5847 | 1 | 0 | 38953.5847 | 1 | 0 |  | 1077.5 | 1252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5868 | 1 | 0 | 38953.5868 | 1 | 0 |  | 1262 | 1437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38953.5889 | 58 | 53 | 38953.5889 | 399 | 434 |  | 1447 | 1622 | 3.5409 | 3.2357 | 24.359 | 26.4957 | 0.035409 | 0.032357 | 0.24359 | 0.26496 | 0.0030525 | 0.021368 | 60309.4581 | 6328.3432 | 4564.4391
38953.5911 | 1149 | 1190 | 38953.5911 | 919 | 960 |  | 1631.5 | 1806.5 | 70.1465 | 72.6496 | 56.105 | 58.6081 | 0.70147 | 0.7265 | 0.56105 | 0.58608 | 0.025031 | 0.025031 | 6364.3415 | 6364.3415 | 18.9774
38953.5932 | 938 | 973 | 38953.5932 | 1059 | 1033 |  | 1816.5 | 1991.5 | 57.265 | 59.4017 | 64.652 | 63.0647 | 0.57265 | 0.59402 | 0.64652 | 0.63065 | 0.021368 | 0.015873 | 5287.8246 | 23348.5482 | 67.274
38953.5953 | 1156 | 1131 | 38953.5954 | 1137 | 1110 |  | 2001.5 | 2176.5 | 70.5739 | 69.0476 | 69.4139 | 67.7656 | 0.70574 | 0.69048 | 0.69414 | 0.67766 | 0.015263 | 0.016484 | 14602.0483 | 7378.8839 | 24.5462
38953.5975 | 971 | 941 | 38953.5975 | 927 | 943 |  | 2186 | 2361 | 59.2796 | 57.4481 | 56.5934 | 57.5702 | 0.5928 | 0.57448 | 0.56593 | 0.5757 | 0.018315 | 0.009768 | 5073.9339 | 63491.7781 | 69.6438
38953.5996 | 2517 | 0 | 38953.5996 | 2366 | 0 |  | 2370.5 | 2545.5 | 153.663 | 0 | 144.4444 | 0 | 1.5366 | 0 | 1.4444 | 0 | 1.5366 | 1.4444 | 2.0413 | 8.5537 | 0.50469
38953.6018 | 2140 | 0 | 38953.6018 | 2005 | 0 |  | 2555.5 | 2730.5 | 130.6471 | 0 | 122.4054 | 0 | 1.3065 | 0 | 1.2241 | 0 | 1.3065 | 1.2241 | 20.0178 | 28.0988 | 18.7113
38953.6039 | 2536 | 0 | 38953.6039 | 2461 | 0 |  | 2740.5 | 2915.5 | 154.823 | 0 | 150.2442 | 0 | 1.5482 | 0 | 1.5024 | 0 | 1.5482 | 1.5024 | 1.2768 | 4.3633 | 0.27142
38953.606 | 2028 | 0 | 38953.6061 | 2546 | 0 |  | 2925 | 3100 | 123.8095 | 0 | 155.4335 | 0 | 1.2381 | 0 | 1.5543 | 0 | 1.2381 | 1.5543 | 26.646 | 0.87903 | 25.4079
38953.6082 | 2443 | 0 | 38953.6082 | 2466 | 0 |  | 3110 | 3285 | 149.1453 | 0 | 150.5495 | 0 | 1.4915 | 0 | 1.5055 | 0 | 1.4915 | 1.5055 | 5.1322 | 4.1517 | 3.6408
38953.6103 | 1978 | 0 | 38953.6103 | 2487 | 0 |  | 3294.5 | 3469.5 | 120.757 | 0 | 151.8315 | 0 | 1.2076 | 0 | 1.5183 | 0 | 1.2076 | 1.5183 | 29.8473 | 3.2722 | 28.6398
| 2150 | 0 | 38953.6125 | 2552 | 0 |  | 3480 | 3655 | 131.2576 | 0 | 155.7998 | 0 | 1.3126 | 0 | 1.558 | 0 | 1.3126 | 1.558 | 19.4595 | 0.64185 | 18.147
38953.6146 | 2322 | 0 | 38953.6146 | 2158 | 0 |  | 3664 | 3839 | 141.7582 | 0 | 131.746 | 0 | 1.4176 | 0 | 1.3175 | 0 | 1.4176 | 1.3175 | 10.6107 | 19.0167 | 9.1931
38953.6167 | 2526 | 0 | 38953.6167 | 2461 | 0 |  | 3849 | 4024 | 154.2125 | 0 | 150.2442 | 0 | 1.5421 | 0 | 1.5024 | 0 | 1.5421 | 1.5024 | 1.6778 | 4.3633 | 0.13563

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 34 |  |  | 2006-08-24 | 13:43
38953.5702 | 1 | 0 | 1 | XLPE | 7-C | Tray
38953.5723 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38953.5744 | 1 | 0 | 1
38953.5766 | 1 | 0 | 1
38953.5787 | 1 | 0 | 1
38953.5809 | 1 | 0 | 1
38953.583 | 1 | 0 | 1
38953.5851 | 1 | 0 | 1
38953.5873 | 1106 | 920 | 1
38953.5894 | 1159 | 1137 | 1
38953.5916 | 1048 | 1022 | 1
38953.5937 | 1139 | 1180 | 1
38953.5958 | 1170 | 904 | 1
38953.598 | 1182 | 1143 | 1
38953.6001 | 1413 | 795 | 1
38953.6022 | 1630 | 709 | 1
38953.6044 | 1815 | 233 | 1
38953.6065 | 2265 | 147 | 1
38953.6087 | 2238 | 77 | 1
38953.6108 | 2131 | 60 | 1
38953.6129 | 2078 | 268 | 1
38953.6151 | 1783 | 237 | 1
1
38953.5702 | 1 | 0 | 2
38953.5723 | 1 | 0 | 2
38953.5745 | 1 | 0 | 2
38953.5766 | 1 | 0 | 2
38953.5787 | 1 | 0 | 2
38953.5809 | 1 | 0 | 2
38953.583 | 1 | 0 | 2
38953.5852 | 1 | 0 | 2
38953.5873 | 977 | 950 | 2
38953.5894 | 932 | 1034 | 2
38953.5916 | 1006 | 981 | 2
38953.5937 | 938 | 973 | 2
38953.5958 | 1166 | 1164 | 2
38953.598 | 1035 | 1000 | 2
38953.6001 | 1532 | 815 | 2
38953.6023 | 1351 | 553 | 2
38953.6044 | 1774 | 223 | 2
38953.6065 | 2199 | 141 | 2
38953.6087 | 2152 | 75 | 2
38953.6108 | 1847 | 53 | 2
38953.613 | 1687 | 278 | 2
38953.6151 | 2033 | 279 | 2
2
38953.5702 | 1 | 0 | 3
38953.5723 | 1 | 0 | 3
38953.5745 | 1 | 0 | 3
38953.5766 | 1 | 0 | 3
38953.5788 | 1 | 0 | 3
38953.5809 | 1 | 0 | 3
38953.583 | 1 | 0 | 3
38953.5852 | 1 | 0 | 3
38953.5873 | 2 | 7 | 3
38953.5894 | 2 | 7 | 3
38953.5916 | 2 | 6 | 3
38953.5937 | 2 | 7 | 3
38953.5959 | 47 | 45 | 3
38953.598 | 300 | 284 | 3
38953.6001 | 824 | 142 | 3
38953.6023 | 1486 | 312 | 3
38953.6044 | 1678 | 73 | 3
38953.6066 | 2211 | 37 | 3
38953.6087 | 1826 | 7 | 3
38953.6108 | 2219 | 8 | 3
38953.613 | 1661 | 239 | 3
38953.6151 | 1721 | 124 | 3
3
38953.5702 | 1 | 0 | 4
38953.5723 | 1 | 0 | 4
38953.5745 | 1 | 0 | 4
38953.5766 | 1 | 0 | 4
38953.5788 | 1 | 0 | 4
38953.5809 | 1 | 0 | 4
38953.583 | 1 | 0 | 4
38953.5852 | 1 | 0 | 4
38953.5873 | 2 | 3 | 4
38953.5895 | 1 | 3 | 4
38953.5916 | 2 | 3 | 4
38953.5937 | 2 | 4 | 4
38953.5959 | 54 | 49 | 4
38953.598 | 287 | 296 | 4
38953.6002 | 1406 | 147 | 4
38953.6023 | 1478 | 358 | 4
38953.6044 | 1806 | 71 | 4
38953.6066 | 1892 | 41 | 4
38953.6087 | 2174 | 10 | 4
38953.6108 | 1868 | 7 | 4
38953.613 | 1679 | 238 | 4
38953.6151 | 1738 | 125 | 4
4
38953.5702 | 1 | 0 | 5
38953.5724 | 1 | 0 | 5
38953.5745 | 1 | 0 | 5
38953.5766 | 1 | 0 | 5
38953.5788 | 1 | 0 | 5
38953.5809 | 1 | 0 | 5
38953.5831 | 1 | 0 | 5
38953.5852 | 1 | 0 | 5
38953.5873 | 2 | 2 | 5
38953.5895 | 1 | 1 | 5
38953.5916 | 1 | 2 | 5
38953.5938 | 2 | 3 | 5
38953.5959 | 58 | 58 | 5
38953.598 | 360 | 364 | 5
38953.6002 | 868 | 180 | 5
38953.6023 | 1169 | 294 | 5
38953.6044 | 1935 | 85 | 5
38953.6066 | 2128 | 37 | 5
38953.6087 | 1859 | 7 | 5
38953.6109 | 2047 | 8 | 5
38953.613 | 1909 | 284 | 5
38953.6151 | 1799 | 139 | 5
5
38953.5702 | 1 | 0 | 6
38953.5724 | 1 | 0 | 6
38953.5745 | 1 | 0 | 6
38953.5767 | 1 | 0 | 6
38953.5788 | 1 | 0 | 6
38953.5809 | 1 | 0 | 6
38953.5831 | 1 | 0 | 6
38953.5852 | 1 | 0 | 6
38953.5873 | 1 | 1 | 6
38953.5895 | 1 | 1 | 6
38953.5916 | 2 | 1 | 6
38953.5938 | 2 | 2 | 6
38953.5959 | 72 | 66 | 6
38953.598 | 326 | 306 | 6
38953.6002 | 824 | 366 | 6
38953.6023 | 1240 | 358 | 6
38953.6045 | 1684 | 70 | 6
38953.6066 | 2162 | 36 | 6
38953.6087 | 2093 | 9 | 6
38953.6109 | 2259 | 9 | 6
38953.613 | 2026 | 287 | 6
38953.6152 | 1708 | 121 | 6
6
38953.5703 | 1 | 0 | 7
38953.5724 | 1 | 0 | 7
38953.5745 | 1 | 0 | 7
38953.5767 | 1 | 0 | 7
38953.5788 | 1 | 0 | 7
38953.5809 | 1 | 0 | 7
38953.5831 | 1 | 0 | 7
38953.5852 | 1 | 0 | 7
38953.5874 | 1 | 1 | 7
38953.5895 | 1 | 1 | 7
38953.5916 | 1 | 1 | 7
38953.5938 | 1 | 2 | 7
38953.5959 | 95 | 87 | 7
38953.5981 | 420 | 336 | 7
38953.6002 | 761 | 417 | 7
38953.6023 | 1420 | 368 | 7
38953.6045 | 2068 | 97 | 7
38953.6066 | 2148 | 41 | 7
38953.6088 | 2146 | 9 | 7
38953.6109 | 1910 | 5 | 7
38953.613 | 1779 | 180 | 7
38953.6152 | 1846 | 75 | 7
7
38953.5703 | 1 | 0 | 8
38953.5724 | 1 | 0 | 8
38953.5746 | 1 | 0 | 8
38953.5767 | 1 | 0 | 8
38953.5788 | 1 | 0 | 8
38953.581 | 1 | 0 | 8
38953.5831 | 1 | 0 | 8
38953.5852 | 1 | 0 | 8
38953.5874 | 2 | 1 | 8
38953.5895 | 1 | 0 | 8
38953.5917 | 1 | 1 | 8
38953.5938 | 2 | 1 | 8
38953.5959 | 52 | 49 | 8
38953.5981 | 368 | 353 | 8
38953.6002 | 799 | 383 | 8
38953.6024 | 1186 | 302 | 8
38953.6045 | 1760 | 99 | 8
38953.6066 | 1638 | 34 | 8
38953.6088 | 2216 | 10 | 8
38953.6109 | 1804 | 3 | 8
38953.6131 | 2029 | 184 | 8
38953.6152 | 1914 | 92 | 8
8
38953.5703 | 1 | 0 | 9
38953.5724 | 1 | 0 | 9
38953.5746 | 1 | 0 | 9
38953.5767 | 1 | 0 | 9
38953.5789 | 1 | 0 | 9
38953.581 | 1 | 0 | 9
38953.5831 | 1 | 0 | 9
38953.5853 | 1 | 0 | 9
38953.5874 | 1 | 0 | 9
38953.5895 | 1 | 0 | 9
38953.5917 | 1 | 0 | 9
38953.5938 | 1 | 1 | 9
38953.596 | 54 | 54 | 9
38953.5981 | 398 | 375 | 9
38953.6002 | 919 | 481 | 9
38953.6024 | 1299 | 312 | 9
38953.6045 | 2014 | 95 | 9
38953.6067 | 1871 | 40 | 9
38953.6088 | 2014 | 8 | 9
38953.6109 | 2011 | 5 | 9
38953.6131 | 1952 | 169 | 9
38953.6152 | 1776 | 74 | 9
9
38953.5703 | 1 | 0 | 10
38953.5725 | 1 | 0 | 10
38953.5746 | 1 | 0 | 10
38953.5767 | 1 | 0 | 10
38953.5789 | 1 | 0 | 10
38953.581 | 1 | 0 | 10
38953.5831 | 1 | 0 | 10
38953.5853 | 1 | 0 | 10
38953.5874 | 1 | 0 | 10
38953.5896 | 1 | 0 | 10
38953.5917 | 1 | 0 | 10
38953.5938 | 1 | 1 | 10
38953.596 | 67 | 65 | 10
38953.5981 | 395 | 377 | 10
38953.6003 | 772 | 396 | 10
38953.6024 | 1342 | 318 | 10
38953.6045 | 1506 | 77 | 10
38953.6067 | 1892 | 42 | 10
38953.6088 | 2074 | 10 | 10
38953.6109 | 1882 | 5 | 10
38953.6131 | 1720 | 151 | 10
38953.6152 | 1541 | 71 | 10
10
38953.5703 | 1 | 0 | 11
38953.5725 | 1 | 0 | 11
38953.5746 | 1 | 0 | 11
38953.5767 | 1 | 0 | 11
38953.5789 | 1 | 0 | 11
38953.581 | 1 | 0 | 11
38953.5832 | 1 | 0 | 11
38953.5853 | 1 | 0 | 11
38953.5874 | 1 | 0 | 11
38953.5896 | 1 | 0 | 11
38953.5917 | 1 | 0 | 11
38953.5939 | 1 | 1 | 11
38953.596 | 2 | 1 | 11
38953.5981 | 63 | 52 | 11
38953.6003 | 497 | 2 | 11
38953.6024 | 1033 | 2 | 11
38953.6045 | 1885 | 0 | 11
38953.6067 | 2063 | 0 | 11
38953.6088 | 2163 | 0 | 11
38953.611 | 2220 | 0 | 11
38953.6131 | 1522 | 0 | 11
38953.6152 | 1881 | 0 | 11
11
38953.5703 | 1 | 0 | 12
38953.5725 | 1 | 0 | 12
38953.5746 | 1 | 0 | 12
38953.5768 | 1 | 0 | 12
38953.5789 | 1 | 0 | 12
38953.581 | 1 | 0 | 12
38953.5832 | 1 | 0 | 12
38953.5853 | 1 | 0 | 12
38953.5875 | 1 | 0 | 12
38953.5896 | 1 | 0 | 12
38953.5917 | 1 | 0 | 12
38953.5939 | 2 | 0 | 12
38953.596 | 2 | 1 | 12
38953.5981 | 731 | 13 | 12
38953.6003 | 2353 | 1 | 12
38953.6024 | 2418 | 1 | 12
38953.6046 | 2053 | 0 | 12
38953.6067 | 2371 | 0 | 12
38953.6088 | 2035 | 0 | 12
38953.611 | 2460 | 0 | 12
38953.6131 | 2552 | 0 | 12
38953.6153 | 2530 | 0 | 12
12
38953.5704 | 1 | 0 | 13
38953.5725 | 1 | 0 | 13
38953.5746 | 1 | 0 | 13
38953.5768 | 1 | 0 | 13
38953.5789 | 1 | 0 | 13
38953.5811 | 1 | 0 | 13
38953.5832 | 1 | 0 | 13
38953.5853 | 1 | 0 | 13
38953.5875 | 1 | 0 | 13
38953.5896 | 1 | 0 | 13
38953.5917 | 1 | 0 | 13
38953.5939 | 1 | 0 | 13
38953.596 | 3 | 2 | 13
38953.5982 | 71 | 2 | 13
38953.6003 | 492 | 1 | 13
38953.6024 | 1213 | 1 | 13
38953.6046 | 1909 | 0 | 13
38953.6067 | 2238 | 0 | 13
38953.6089 | 1842 | 0 | 13
38953.611 | 2158 | 0 | 13
38953.6131 | 1829 | 0 | 13
38953.6153 | 1821 | 0 | 13
13
38953.5704 | 2 | 0 | 14
38953.5725 | 1 | 0 | 14
38953.5747 | 1 | 0 | 14
38953.5768 | 1 | 0 | 14
38953.5789 | 1 | 0 | 14
38953.5811 | 1 | 0 | 14
38953.5832 | 1 | 0 | 14
38953.5853 | 1 | 0 | 14
38953.5875 | 1 | 0 | 14
38953.5896 | 1 | 0 | 14
38953.5918 | 1 | 0 | 14
38953.5939 | 1 | 0 | 14
38953.596 | 3 | 1 | 14
38953.5982 | 1883 | 2 | 14
38953.6003 | 1981 | 0 | 14
38953.6025 | 2460 | 1 | 14
38953.6046 | 2347 | 0 | 14
38953.6067 | 2523 | 0 | 14
38953.6089 | 2190 | 0 | 14
38953.611 | 2547 | 0 | 14
38953.6131 | 2559 | 0 | 14
38953.6153 | 2424 | 0 | 14
14
38953.5704 | 1 | 0 | 15
38953.5725 | 1 | 0 | 15
38953.5747 | 1 | 0 | 15
38953.5768 | 1 | 0 | 15
38953.5789 | 1 | 0 | 15
38953.5811 | 1 | 0 | 15
38953.5832 | 1 | 0 | 15
38953.5854 | 1 | 0 | 15
38953.5875 | 1 | 0 | 15
38953.5896 | 1 | 0 | 15
38953.5918 | 1 | 0 | 15
38953.5939 | 1 | 0 | 15
38953.5961 | 1 | 0 | 15
38953.5982 | 92 | 1 | 15
38953.6003 | 600 | 0 | 15
38953.6025 | 1086 | 0 | 15
38953.6046 | 1605 | 0 | 15
38953.6067 | 1907 | 0 | 15
38953.6089 | 2125 | 0 | 15
38953.611 | 2174 | 0 | 15
38953.6132 | 1772 | 228 | 15
38953.6153 | 1596 | 0 | 15
15
38953.5704 | 1 | 0 | 16
38953.5725 | 1 | 0 | 16
38953.5747 | 1 | 0 | 16
38953.5768 | 1 | 0 | 16
38953.579 | 1 | 0 | 16
38953.5811 | 1 | 0 | 16
38953.5832 | 1 | 0 | 16
38953.5854 | 1 | 0 | 16
38953.5875 | 1 | 0 | 16
38953.5897 | 1 | 0 | 16
38953.5918 | 1 | 0 | 16
38953.5939 | 1 | 0 | 16
38953.5961 | 1 | 0 | 16
38953.5982 | 2 | 1 | 16
38953.6003 | 2470 | 1 | 16
38953.6025 | 2275 | 0 | 16
38953.6046 | 2018 | 0 | 16
38953.6068 | 2472 | 0 | 16
38953.6089 | 2268 | 0 | 16
38953.611 | 1962 | 0 | 16
38953.6132 | 1552 | 221 | 16
38953.6153 | 2129 | 0 | 16
16
38953.5726 | 1 | 0 | 17
38953.5747 | 1 | 0 | 17
38953.5768 | 1 | 0 | 17
38953.579 | 2 | 0 | 17
38953.5811 | 1 | 0 | 17
38953.5833 | 1 | 0 | 17
38953.5854 | 1 | 0 | 17
38953.5875 | 1 | 0 | 17
38953.5897 | 1 | 0 | 17
38953.5918 | 1 | 0 | 17
38953.5939 | 1 | 0 | 17
38953.5961 | 2 | 0 | 17
38953.5982 | 109 | 1 | 17
38953.6004 | 507 | 0 | 17
38953.6025 | 1179 | 0 | 17
38953.6046 | 1724 | 0 | 17
38953.6068 | 1780 | 0 | 17
38953.6089 | 1962 | 0 | 17
38953.6111 | 1831 | 0 | 17
38953.6132 | 1843 | 241 | 17
38953.6153 | 2008 | 0 | 17
17
38953.5704 | 1 | 0 | 18
38953.5726 | 1 | 0 | 18
38953.5747 | 1 | 0 | 18
38953.5769 | 1 | 0 | 18
38953.579 | 1 | 0 | 18
38953.5811 | 1 | 0 | 18
38953.5833 | 1 | 0 | 18
38953.5854 | 1 | 0 | 18
38953.5875 | 1 | 0 | 18
38953.5897 | 1 | 0 | 18
38953.5918 | 1 | 0 | 18
38953.594 | 1 | 0 | 18
38953.5961 | 1 | 0 | 18
38953.5982 | 2 | 1 | 18
38953.6004 | 2049 | 0 | 18
38953.6025 | 2227 | 0 | 18
38953.6047 | 2084 | 0 | 18
38953.6068 | 1994 | 0 | 18
38953.6089 | 2280 | 0 | 18
38953.6111 | 2202 | 0 | 18
38953.6132 | 1796 | 235 | 18
38953.6153 | 1995 | 0 | 18
18
38953.5705 | 1 | 0 | 19
38953.5726 | 1 | 0 | 19
38953.5747 | 1 | 0 | 19
38953.5769 | 1 | 0 | 19
38953.579 | 1 | 0 | 19
38953.5811 | 1 | 0 | 19
38953.5833 | 1 | 0 | 19
38953.5854 | 1 | 0 | 19
38953.5876 | 1 | 0 | 19
38953.5897 | 1 | 0 | 19
38953.5918 | 1 | 0 | 19
38953.594 | 1 | 0 | 19
38953.5961 | 1 | 0 | 19
38953.5983 | 178 | 3 | 19
38953.6004 | 586 | 0 | 19
38953.6025 | 1461 | 0 | 19
38953.6047 | 1666 | 0 | 19
38953.6068 | 1747 | 0 | 19
38953.6089 | 1991 | 0 | 19
38953.6111 | 2190 | 0 | 19
38953.6132 | 1794 | 0 | 19
38953.6154 | 1616 | 0 | 19
19
38953.5705 | 1 | 0 | 20
38953.5726 | 1 | 0 | 20
38953.5747 | 1 | 0 | 20
38953.5769 | 1 | 0 | 20
38953.579 | 1 | 0 | 20
38953.5812 | 1 | 0 | 20
38953.5833 | 1 | 0 | 20
38953.5854 | 1 | 0 | 20
38953.5876 | 1 | 0 | 20
38953.5897 | 1 | 0 | 20
38953.5919 | 1 | 0 | 20
38953.594 | 1 | 0 | 20
38953.5961 | 1 | 0 | 20
38953.5983 | 11 | 3 | 20
38953.6004 | 2506 | 0 | 20
38953.6025 | 2398 | 0 | 20
38953.6047 | 1957 | 0 | 20
38953.6068 | 2266 | 0 | 20
38953.609 | 2022 | 0 | 20
38953.6111 | 2169 | 0 | 20
38953.6132 | 2469 | 0 | 20
38953.6154 | 2242 | 0 | 20
20
38953.5705 | 1 | 0 | 21
38953.5726 | 1 | 0 | 21
38953.5748 | 1 | 0 | 21
38953.5769 | 1 | 0 | 21
38953.579 | 1 | 0 | 21
38953.5812 | 1 | 0 | 21
38953.5833 | 1 | 0 | 21
38953.5855 | 1 | 0 | 21
38953.5876 | 1 | 0 | 21
38953.5897 | 1 | 0 | 21
38953.5919 | 1 | 0 | 21
38953.594 | 1 | 0 | 21
38953.5961 | 1 | 0 | 21
38953.5983 | 170 | 3 | 21
38953.6004 | 582 | 0 | 21
38953.6026 | 1485 | 0 | 21
38953.6047 | 2068 | 0 | 21
38953.6068 | 1764 | 0 | 21
38953.609 | 1965 | 0 | 21
38953.6111 | 1859 | 0 | 21
38953.6133 | 1798 | 0 | 21
38953.6154 | 1767 | 0 | 21
21
38953.5705 | 1 | 0 | 22
38953.5726 | 1 | 0 | 22
38953.5748 | 1 | 0 | 22
38953.5769 | 1 | 0 | 22
38953.5791 | 1 | 0 | 22
38953.5812 | 1 | 0 | 22
38953.5833 | 1 | 0 | 22
38953.5855 | 1 | 0 | 22
38953.5876 | 1 | 0 | 22
38953.5898 | 1 | 0 | 22
38953.5919 | 1 | 0 | 22
38953.594 | 1 | 0 | 22
38953.5962 | 1 | 0 | 22
38953.5983 | 11 | 3 | 22
38953.6004 | 2213 | 0 | 22
38953.6026 | 2151 | 0 | 22
38953.6047 | 2007 | 0 | 22
38953.6069 | 2518 | 0 | 22
38953.609 | 1975 | 0 | 22
38953.6111 | 2045 | 0 | 22
38953.6133 | 2220 | 0 | 22
38953.6154 | 2332 | 0 | 22
22
38953.5705 | 1 | 0 | 23
38953.5727 | 1 | 0 | 23
38953.5748 | 1 | 0 | 23
38953.5769 | 1 | 0 | 23
38953.5791 | 1 | 0 | 23
38953.5812 | 1 | 0 | 23
38953.5834 | 1 | 0 | 23
38953.5855 | 1 | 0 | 23
38953.5876 | 1 | 0 | 23
38953.5898 | 1 | 0 | 23
38953.5919 | 1 | 0 | 23
38953.5941 | 2 | 0 | 23
38953.5962 | 76 | 74 | 23
38953.5983 | 356 | 276 | 23
38953.6005 | 849 | 395 | 23
38953.6026 | 1617 | 321 | 23
38953.6047 | 1793 | 75 | 23
38953.6069 | 2095 | 32 | 23
38953.609 | 2257 | 7 | 23
38953.6112 | 1904 | 13 | 23
38953.6133 | 1844 | 302 | 23
38953.6154 | 1580 | 144 | 23
23
38953.5705 | 1 | 0 | 24
38953.5727 | 1 | 0 | 24
38953.5748 | 1 | 0 | 24
38953.577 | 1 | 0 | 24
38953.5791 | 1 | 0 | 24
38953.5812 | 1 | 0 | 24
38953.5834 | 1 | 0 | 24
38953.5855 | 1 | 0 | 24
38953.5877 | 1 | 0 | 24
38953.5898 | 1 | 0 | 24
38953.5919 | 1 | 0 | 24
38953.5941 | 2 | 1 | 24
38953.5962 | 81 | 74 | 24
38953.5983 | 625 | 347 | 24
38953.6005 | 840 | 440 | 24
38953.6026 | 1543 | 324 | 24
38953.6048 | 1718 | 60 | 24
38953.6069 | 1778 | 32 | 24
38953.609 | 2006 | 7 | 24
38953.6112 | 1911 | 16 | 24
38953.6133 | 1549 | 242 | 24
38953.6155 | 2139 | 176 | 24
24
38953.5706 | 1 | 0 | 25
38953.5727 | 1 | 0 | 25
38953.5748 | 1 | 0 | 25
38953.577 | 1 | 0 | 25
38953.5791 | 1 | 0 | 25
38953.5813 | 1 | 0 | 25
38953.5834 | 1 | 0 | 25
38953.5855 | 1 | 0 | 25
38953.5877 | 1 | 0 | 25
38953.5898 | 1 | 0 | 25
38953.5919 | 1 | 0 | 25
38953.5941 | 2 | 0 | 25
38953.5962 | 97 | 82 | 25
38953.5984 | 463 | 290 | 25
38953.6005 | 1047 | 494 | 25
38953.6026 | 1557 | 312 | 25
38953.6048 | 2090 | 70 | 25
38953.6069 | 2133 | 30 | 25
38953.6091 | 1893 | 7 | 25
38953.6112 | 2283 | 16 | 25
38953.6133 | 1586 | 246 | 25
38953.6155 | 1758 | 163 | 25
25
38953.5706 | 1 | 0 | 26
38953.5727 | 1 | 0 | 26
38953.5748 | 1 | 0 | 26
38953.577 | 1 | 0 | 26
38953.5791 | 1 | 0 | 26
38953.5813 | 1 | 0 | 26
38953.5834 | 1 | 0 | 26
38953.5855 | 1 | 0 | 26
38953.5877 | 1 | 0 | 26
38953.5898 | 1 | 0 | 26
38953.592 | 1 | 0 | 26
38953.5941 | 2 | 1 | 26
38953.5962 | 103 | 95 | 26
38953.5984 | 447 | 375 | 26
38953.6005 | 886 | 412 | 26
38953.6027 | 1403 | 245 | 26
38953.6048 | 2101 | 72 | 26
38953.6069 | 1817 | 23 | 26
38953.6091 | 1917 | 6 | 26
38953.6112 | 2353 | 15 | 26
38953.6133 | 1931 | 301 | 26
38953.6155 | 1830 | 162 | 26
26
38953.5706 | 1 | 0 | 27
38953.5727 | 1 | 0 | 27
38953.5749 | 1 | 0 | 27
38953.577 | 1 | 0 | 27
38953.5791 | 1 | 0 | 27
38953.5813 | 1 | 0 | 27
38953.5834 | 1 | 0 | 27
38953.5856 | 1 | 0 | 27
38953.5877 | 1 | 0 | 27
38953.5898 | 1 | 0 | 27
38953.592 | 1 | 0 | 27
38953.5941 | 1 | 0 | 27
38953.5963 | 90 | 81 | 27
38953.5984 | 544 | 357 | 27
38953.6005 | 894 | 407 | 27
38953.6027 | 1592 | 198 | 27
38953.6048 | 1871 | 71 | 27
38953.6069 | 2104 | 31 | 27
38953.6091 | 1844 | 6 | 27
38953.6112 | 2005 | 11 | 27
38953.6134 | 1556 | 238 | 27
38953.6155 | 1754 | 70 | 27
27
38953.5706 | 1 | 0 | 28
38953.5727 | 1 | 0 | 28
38953.5749 | 1 | 0 | 28
38953.577 | 1 | 0 | 28
38953.5792 | 1 | 0 | 28
38953.5813 | 1 | 0 | 28
38953.5834 | 1 | 0 | 28
38953.5856 | 1 | 0 | 28
38953.5877 | 1 | 0 | 28
38953.5898 | 1 | 0 | 28
38953.592 | 1 | 0 | 28
38953.5941 | 2 | 0 | 28
38953.5963 | 110 | 103 | 28
38953.5984 | 373 | 269 | 28
38953.6005 | 858 | 398 | 28
38953.6027 | 1451 | 208 | 28
38953.6048 | 1881 | 95 | 28
38953.607 | 1907 | 33 | 28
38953.6091 | 2270 | 6 | 28
38953.6112 | 2259 | 9 | 28
38953.6134 | 1625 | 247 | 28
38953.6155 | 1562 | 71 | 28
28
38953.5706 | 1 | 0 | 29
38953.5728 | 1 | 0 | 29
38953.5749 | 1 | 0 | 29
38953.577 | 1 | 0 | 29
38953.5792 | 1 | 0 | 29
38953.5813 | 1 | 0 | 29
38953.5834 | 1 | 0 | 29
38953.5856 | 1 | 0 | 29
38953.5877 | 1 | 0 | 29
38953.5899 | 1 | 0 | 29
38953.592 | 1 | 0 | 29
38953.5941 | 2 | 0 | 29
38953.5963 | 128 | 117 | 29
38953.5984 | 457 | 258 | 29
38953.6006 | 842 | 387 | 29
38953.6027 | 1619 | 174 | 29
38953.6048 | 2098 | 92 | 29
38953.607 | 2177 | 34 | 29
38953.6091 | 2104 | 7 | 29
38953.6113 | 2184 | 8 | 29
38953.6134 | 1775 | 268 | 29
38953.6155 | 1615 | 67 | 29
29
38953.5706 | 1 | 0 | 30
38953.5728 | 1 | 0 | 30
38953.5749 | 1 | 0 | 30
38953.577 | 1 | 0 | 30
38953.5792 | 1 | 0 | 30
38953.5813 | 1 | 0 | 30
38953.5835 | 1 | 0 | 30
38953.5856 | 1 | 0 | 30
38953.5877 | 1 | 0 | 30
38953.5899 | 1 | 0 | 30
38953.592 | 1 | 0 | 30
38953.5942 | 2 | 0 | 30
38953.5963 | 144 | 137 | 30
38953.5984 | 350 | 279 | 30
38953.6006 | 1057 | 469 | 30
38953.6027 | 1456 | 180 | 30
38953.6048 | 1476 | 78 | 30
38953.607 | 1879 | 34 | 30
38953.6091 | 2275 | 7 | 30
38953.6113 | 2152 | 11 | 30
38953.6134 | 1805 | 258 | 30
38953.6155 | 1556 | 70 | 30
30
38953.5706 | 1 | 0 | 31
38953.5728 | 1 | 0 | 31
38953.5749 | 1 | 0 | 31
38953.5771 | 1 | 0 | 31
38953.5792 | 1 | 0 | 31
38953.5813 | 1 | 0 | 31
38953.5835 | 1 | 0 | 31
38953.5856 | 1 | 0 | 31
38953.5878 | 1 | 0 | 31
38953.5899 | 1 | 0 | 31
38953.592 | 1 | 0 | 31
38953.5942 | 1 | 0 | 31
38953.5963 | 4 | 2 | 31
38953.5984 | 112 | 1 | 31
38953.6006 | 736 | 2 | 31
38953.6027 | 1498 | 1 | 31
38953.6049 | 1774 | 0 | 31
38953.607 | 1923 | 0 | 31
38953.6091 | 1819 | 0 | 31
38953.6113 | 2095 | 0 | 31
38953.6134 | 1794 | 1 | 31
38953.6156 | 1695 | 0 | 31
31
38953.5707 | 1 | 0 | 32
38953.5728 | 1 | 0 | 32
38953.5749 | 1 | 0 | 32
38953.5771 | 1 | 0 | 32
38953.5792 | 1 | 0 | 32
38953.5814 | 1 | 0 | 32
38953.5835 | 1 | 0 | 32
38953.5856 | 1 | 0 | 32
38953.5878 | 1 | 0 | 32
38953.5899 | 1 | 0 | 32
38953.592 | 1 | 0 | 32
38953.5942 | 1 | 0 | 32
38953.5963 | 4 | 2 | 32
38953.5985 | 1988 | 1 | 32
38953.6006 | 1960 | 1 | 32
38953.6027 | 1967 | 0 | 32
38953.6049 | 2310 | 0 | 32
38953.607 | 1965 | 0 | 32
38953.6092 | 2557 | 0 | 32
38953.6113 | 2221 | 0 | 32
38953.6134 | 2136 | 0 | 32
38953.6156 | 1992 | 0 | 32
32
38953.5707 | 1 | 0 | 33
38953.5728 | 1 | 0 | 33
38953.575 | 1 | 0 | 33
38953.5771 | 1 | 0 | 33
38953.5792 | 1 | 0 | 33
38953.5814 | 1 | 0 | 33
38953.5835 | 1 | 0 | 33
38953.5857 | 1 | 0 | 33
38953.5878 | 1 | 0 | 33
38953.5899 | 1 | 0 | 33
38953.5921 | 1 | 0 | 33
38953.5942 | 1 | 0 | 33
38953.5963 | 4 | 1 | 33
38953.5985 | 137 | 1 | 33
38953.6006 | 720 | 1 | 33
38953.6028 | 1514 | 0 | 33
38953.6049 | 1739 | 0 | 33
38953.607 | 1969 | 0 | 33
38953.6092 | 2188 | 0 | 33
38953.6113 | 2150 | 0 | 33
38953.6134 | 1588 | 0 | 33
38953.6156 | 1673 | 0 | 33
33
38953.5707 | 1 | 0 | 34
38953.5728 | 1 | 0 | 34
38953.575 | 1 | 0 | 34
38953.5771 | 1 | 0 | 34
38953.5793 | 1 | 0 | 34
38953.5814 | 1 | 0 | 34
38953.5835 | 1 | 0 | 34
38953.5857 | 1 | 0 | 34
38953.5878 | 1 | 0 | 34
38953.5899 | 1 | 0 | 34
38953.5921 | 1 | 0 | 34
38953.5942 | 1 | 0 | 34
38953.5964 | 6 | 3 | 34
38953.5985 | 2489 | 0 | 34
38953.6006 | 2219 | 1 | 34
38953.6028 | 1951 | 0 | 34
38953.6049 | 2063 | 0 | 34
38953.6071 | 2436 | 0 | 34
38953.6092 | 2414 | 0 | 34
38953.6113 | 2251 | 0 | 34
38953.6135 | 2032 | 0 | 34
38953.6156 | 2498 | 0 | 34
34
38953.5707 | 1 | 0 | 35
38953.5729 | 1 | 0 | 35
38953.575 | 1 | 0 | 35
38953.5771 | 1 | 0 | 35
38953.5793 | 1 | 0 | 35
38953.5814 | 1 | 0 | 35
38953.5836 | 1 | 0 | 35
38953.5857 | 1 | 0 | 35
38953.5878 | 1 | 0 | 35
38953.59 | 1 | 0 | 35
38953.5921 | 1 | 0 | 35
38953.5942 | 1 | 0 | 35
38953.5964 | 1 | 0 | 35
38953.5985 | 128 | 0 | 35
38953.6007 | 737 | 0 | 35
38953.6028 | 1741 | 0 | 35
38953.6049 | 2103 | 0 | 35
38953.6071 | 1940 | 0 | 35
38953.6092 | 2119 | 0 | 35
38953.6114 | 1923 | 0 | 35
38953.6135 | 1670 | 297 | 35
38953.6156 | 1939 | 1 | 35
35
38953.5707 | 1 | 0 | 36
38953.5729 | 1 | 0 | 36
38953.575 | 1 | 0 | 36
38953.5772 | 1 | 0 | 36
38953.5793 | 1 | 0 | 36
38953.5814 | 1 | 0 | 36
38953.5836 | 1 | 0 | 36
38953.5878 | 1 | 0 | 36
38953.59 | 1 | 0 | 36
38953.5921 | 1 | 0 | 36
38953.5943 | 1 | 0 | 36
38953.5964 | 1 | 0 | 36
38953.5985 | 3 | 0 | 36
38953.6007 | 2198 | 1 | 36
38953.6028 | 1968 | 0 | 36
38953.605 | 2373 | 0 | 36
38953.6071 | 2401 | 0 | 36
38953.6092 | 2123 | 0 | 36
38953.6114 | 2259 | 0 | 36
38953.6135 | 1956 | 163 | 36
38953.6156 | 1950 | 0 | 36
36
38953.5708 | 1 | 0 | 37
38953.5729 | 1 | 0 | 37
38953.575 | 1 | 0 | 37
38953.5772 | 1 | 0 | 37
38953.5793 | 1 | 0 | 37
38953.5814 | 1 | 0 | 37
38953.5836 | 1 | 0 | 37
38953.5857 | 1 | 0 | 37
38953.5879 | 1 | 0 | 37
38953.59 | 1 | 0 | 37
38953.5921 | 1 | 0 | 37
38953.5943 | 1 | 0 | 37
38953.5964 | 1 | 0 | 37
38953.5986 | 146 | 1 | 37
38953.6007 | 731 | 0 | 37
38953.6028 | 1452 | 0 | 37
38953.605 | 1931 | 0 | 37
38953.6071 | 2250 | 0 | 37
38953.6092 | 1853 | 0 | 37
38953.6114 | 1922 | 0 | 37
38953.6135 | 1562 | 207 | 37
38953.6157 | 1664 | 0 | 37
37
38953.5708 | 1 | 0 | 38
38953.5729 | 1 | 0 | 38
38953.575 | 1 | 0 | 38
38953.5772 | 1 | 0 | 38
38953.5793 | 1 | 0 | 38
38953.5815 | 1 | 0 | 38
38953.5836 | 1 | 0 | 38
38953.5857 | 1 | 0 | 38
38953.5879 | 1 | 0 | 38
38953.59 | 1 | 0 | 38
38953.5922 | 1 | 0 | 38
38953.5943 | 1 | 0 | 38
38953.5964 | 1 | 0 | 38
38953.5986 | 2 | 0 | 38
38953.6007 | 2300 | 0 | 38
38953.6028 | 1970 | 0 | 38
38953.605 | 2053 | 0 | 38
38953.6071 | 1962 | 0 | 38
38953.6093 | 2561 | 0 | 38
38953.6114 | 2168 | 0 | 38
38953.6135 | 1853 | 108 | 38
38953.6157 | 2026 | 0 | 38
38
38953.5708 | 1 | 0 | 39
38953.5729 | 1 | 0 | 39
38953.5751 | 1 | 0 | 39
38953.5772 | 1 | 0 | 39
38953.5793 | 1 | 0 | 39
38953.5815 | 2 | 0 | 39
38953.5836 | 1 | 0 | 39
38953.5858 | 1 | 0 | 39
38953.5879 | 1 | 0 | 39
38953.59 | 1 | 0 | 39
38953.5922 | 1 | 0 | 39
38953.5943 | 1 | 0 | 39
38953.5964 | 1 | 0 | 39
38953.5986 | 251 | 6 | 39
38953.6007 | 785 | 0 | 39
38953.6029 | 1553 | 0 | 39
38953.605 | 1649 | 0 | 39
38953.6071 | 2041 | 0 | 39
38953.6093 | 1881 | 0 | 39
38953.6114 | 2169 | 0 | 39
38953.6136 | 1774 | 0 | 39
38953.6157 | 1612 | 0 | 39
39
38953.5708 | 1 | 0 | 40
38953.5729 | 1 | 0 | 40
38953.5751 | 1 | 0 | 40
38953.5772 | 1 | 0 | 40
38953.5794 | 1 | 0 | 40
38953.5815 | 1 | 0 | 40
38953.5836 | 1 | 0 | 40
38953.5858 | 1 | 0 | 40
38953.5879 | 1 | 0 | 40
38953.59 | 1 | 0 | 40
38953.5922 | 1 | 0 | 40
38953.5943 | 1 | 0 | 40
38953.5965 | 1 | 0 | 40
38953.5986 | 22 | 5 | 40
38953.6007 | 1976 | 0 | 40
38953.6029 | 2258 | 0 | 40
38953.605 | 2512 | 0 | 40
38953.6072 | 2329 | 0 | 40
38953.6093 | 2167 | 0 | 40
38953.6114 | 2170 | 0 | 40
38953.6136 | 2347 | 0 | 40
38953.6157 | 2274 | 0 | 40
40
38953.5708 | 1 | 0 | 41
38953.573 | 1 | 0 | 41
38953.5751 | 1 | 0 | 41
38953.5772 | 1 | 0 | 41
38953.5794 | 1 | 0 | 41
38953.5815 | 1 | 0 | 41
38953.5836 | 1 | 0 | 41
38953.5858 | 1 | 0 | 41
38953.5879 | 1 | 0 | 41
38953.5901 | 1 | 0 | 41
38953.5922 | 1 | 0 | 41
38953.5943 | 1 | 0 | 41
38953.5965 | 1 | 0 | 41
38953.5986 | 255 | 7 | 41
38953.6008 | 691 | 0 | 41
38953.6029 | 1557 | 0 | 41
38953.605 | 1861 | 0 | 41
38953.6072 | 2118 | 0 | 41
38953.6093 | 2110 | 0 | 41
38953.6114 | 2147 | 0 | 41
38953.6136 | 1723 | 0 | 41
38953.6157 | 1830 | 0 | 41
41
38953.5708 | 1 | 0 | 42
38953.573 | 1 | 0 | 42
38953.5751 | 1 | 0 | 42
38953.5772 | 1 | 0 | 42
38953.5794 | 1 | 0 | 42
38953.5815 | 1 | 0 | 42
38953.5837 | 1 | 0 | 42
38953.5858 | 1 | 0 | 42
38953.5879 | 1 | 0 | 42
38953.5901 | 1 | 0 | 42
38953.5922 | 1 | 0 | 42
38953.5944 | 1 | 0 | 42
38953.5965 | 1 | 0 | 42
38953.5986 | 29 | 9 | 42
38953.6008 | 2237 | 0 | 42
38953.6029 | 2177 | 0 | 42
38953.605 | 2095 | 0 | 42
38953.6072 | 2161 | 0 | 42
38953.6093 | 2391 | 0 | 42
38953.6115 | 2504 | 0 | 42
38953.6136 | 2193 | 0 | 42
38953.6157 | 2387 | 0 | 42
42
38953.5708 | 1 | 0 | 43
38953.573 | 1 | 0 | 43
38953.5751 | 1 | 0 | 43
38953.5773 | 1 | 0 | 43
38953.5794 | 1 | 0 | 43
38953.5815 | 1 | 0 | 43
38953.5837 | 1 | 0 | 43
38953.5858 | 1 | 0 | 43
38953.588 | 1 | 0 | 43
38953.5901 | 5 | 2 | 43
38953.5922 | 952 | 924 | 43
38953.5944 | 246 | 239 | 43
38953.5965 | 1088 | 1138 | 43
38953.5986 | 1002 | 873 | 43
38953.6008 | 1464 | 887 | 43
38953.6029 | 1517 | 412 | 43
38953.6051 | 2051 | 142 | 43
38953.6072 | 1779 | 104 | 43
38953.6093 | 2370 | 57 | 43
38953.6115 | 1930 | 45 | 43
38953.6136 | 1811 | 330 | 43
38953.6158 | 1913 | 263 | 43
43
38953.5709 | 1 | 0 | 44
38953.573 | 1 | 0 | 44
38953.5751 | 1 | 0 | 44
38953.5773 | 1 | 0 | 44
38953.5794 | 1 | 0 | 44
38953.5816 | 2 | 0 | 44
38953.5837 | 1 | 0 | 44
38953.5858 | 1 | 0 | 44
38953.588 | 1 | 0 | 44
38953.5901 | 4 | 1 | 44
38953.5922 | 407 | 395 | 44
38953.5944 | 254 | 236 | 44
38953.5965 | 1055 | 1102 | 44
38953.5987 | 1055 | 843 | 44
38953.6008 | 1174 | 701 | 44
38953.6029 | 1455 | 387 | 44
38953.6051 | 2122 | 149 | 44
38953.6072 | 1931 | 110 | 44
38953.6094 | 1823 | 47 | 44
38953.6115 | 2274 | 52 | 44
38953.6136 | 1925 | 368 | 44
38953.6158 | 1882 | 261 | 44
44
38953.5709 | 1 | 0 | 45
38953.573 | 1 | 0 | 45
38953.5752 | 1 | 0 | 45
38953.5773 | 1 | 0 | 45
38953.5794 | 1 | 0 | 45
38953.5816 | 1 | 0 | 45
38953.5837 | 1 | 0 | 45
38953.5858 | 1 | 0 | 45
38953.588 | 1 | 0 | 45
38953.5901 | 1 | 0 | 45
38953.5923 | 2 | 4 | 45
38953.5944 | 1 | 1 | 45
38953.5965 | 36 | 31 | 45
38953.5987 | 483 | 145 | 45
38953.6008 | 775 | 223 | 45
38953.603 | 1425 | 71 | 45
38953.6051 | 2047 | 9 | 45
38953.6072 | 2186 | 3 | 45
38953.6094 | 1917 | 1 | 45
38953.6115 | 1895 | 1 | 45
38953.6136 | 1887 | 137 | 45
38953.6158 | 1622 | 23 | 45
45
38953.5709 | 1 | 0 | 46
38953.573 | 1 | 0 | 46
38953.5752 | 1 | 0 | 46
38953.5773 | 1 | 0 | 46
38953.5794 | 1 | 0 | 46
38953.5816 | 1 | 0 | 46
38953.5837 | 1 | 0 | 46
38953.5859 | 1 | 0 | 46
38953.588 | 1 | 0 | 46
38953.5901 | 1 | 0 | 46
38953.5923 | 2 | 2 | 46
38953.5944 | 1 | 0 | 46
38953.5966 | 31 | 28 | 46
38953.5987 | 208 | 143 | 46
38953.6008 | 975 | 242 | 46
38953.603 | 1475 | 79 | 46
38953.6051 | 1818 | 11 | 46
38953.6072 | 1955 | 2 | 46
38953.6094 | 2051 | 1 | 46
38953.6115 | 1926 | 1 | 46
38953.6137 | 1666 | 115 | 46
38953.6158 | 1596 | 29 | 46
46
38953.5709 | 1 | 0 | 47
38953.573 | 1 | 0 | 47
38953.5752 | 1 | 0 | 47
38953.5773 | 1 | 0 | 47
38953.5795 | 1 | 0 | 47
38953.5816 | 1 | 0 | 47
38953.5837 | 1 | 0 | 47
38953.5859 | 1 | 0 | 47
38953.588 | 1 | 0 | 47
38953.5902 | 1 | 0 | 47
38953.5923 | 1 | 1 | 47
38953.5944 | 1 | 1 | 47
38953.5966 | 38 | 31 | 47
38953.5987 | 497 | 149 | 47
38953.6009 | 864 | 242 | 47
38953.603 | 1656 | 76 | 47
38953.6051 | 2020 | 9 | 47
38953.6073 | 2171 | 3 | 47
38953.6094 | 1909 | 0 | 47
38953.6115 | 1906 | 1 | 47
38953.6137 | 1727 | 147 | 47
38953.6158 | 1624 | 25 | 47
47
38953.5709 | 1 | 0 | 48
38953.5731 | 1 | 0 | 48
38953.5752 | 1 | 0 | 48
38953.5773 | 2 | 0 | 48
38953.5795 | 1 | 0 | 48
38953.5816 | 1 | 0 | 48
38953.5838 | 1 | 0 | 48
38953.5859 | 1 | 0 | 48
38953.588 | 1 | 0 | 48
38953.5902 | 1 | 0 | 48
38953.5923 | 2 | 1 | 48
38953.5945 | 1 | 0 | 48
38953.5966 | 37 | 33 | 48
38953.5987 | 266 | 174 | 48
38953.6009 | 898 | 216 | 48
38953.603 | 1557 | 86 | 48
38953.6051 | 1618 | 9 | 48
38953.6073 | 2063 | 2 | 48
38953.6094 | 2159 | 0 | 48
38953.6116 | 1890 | 1 | 48
38953.6137 | 1907 | 156 | 48
38953.6158 | 1576 | 28 | 48
48
38953.5709 | 1 | 0 | 49
38953.5731 | 1 | 0 | 49
38953.5752 | 1 | 0 | 49
38953.5774 | 1 | 0 | 49
38953.5795 | 1 | 0 | 49
38953.5816 | 1 | 0 | 49
38953.5838 | 1 | 0 | 49
38953.5859 | 1 | 0 | 49
38953.5881 | 1 | 0 | 49
38953.5902 | 1 | 0 | 49
38953.5923 | 1 | 0 | 49
38953.5945 | 2 | 0 | 49
38953.5966 | 30 | 25 | 49
38953.5987 | 259 | 2 | 49
38953.6009 | 835 | 2 | 49
38953.603 | 1576 | 0 | 49
38953.6052 | 1978 | 0 | 49
38953.6073 | 1855 | 0 | 49
38953.6094 | 2058 | 0 | 49
38953.6116 | 2278 | 0 | 49
38953.6137 | 1710 | 0 | 49
38953.6159 | 1637 | 0 | 49
49
38953.571 | 1 | 0 | 50
38953.5731 | 1 | 0 | 50
38953.5752 | 1 | 0 | 50
38953.5774 | 1 | 0 | 50
38953.5795 | 1 | 0 | 50
38953.5817 | 1 | 0 | 50
38953.5838 | 1 | 0 | 50
38953.5859 | 1 | 0 | 50
38953.5881 | 1 | 0 | 50
38953.5902 | 1 | 0 | 50
38953.5923 | 1 | 0 | 50
38953.5945 | 1 | 0 | 50
38953.5966 | 40 | 34 | 50
38953.5988 | 2039 | 1 | 50
38953.6009 | 2068 | 1 | 50
38953.603 | 2286 | 0 | 50
38953.6052 | 2425 | 0 | 50
38953.6073 | 1966 | 0 | 50
38953.6095 | 2350 | 0 | 50
38953.6116 | 2245 | 0 | 50
38953.6137 | 2111 | 0 | 50
38953.6159 | 2018 | 0 | 50
50
38953.571 | 1 | 0 | 51
38953.5731 | 2 | 0 | 51
38953.5753 | 1 | 0 | 51
38953.5774 | 1 | 0 | 51
38953.5795 | 1 | 0 | 51
38953.5817 | 1 | 0 | 51
38953.5838 | 1 | 0 | 51
38953.5859 | 1 | 0 | 51
38953.5881 | 1 | 0 | 51
38953.5902 | 1 | 0 | 51
38953.5924 | 1 | 0 | 51
38953.5945 | 1 | 0 | 51
38953.5966 | 28 | 21 | 51
38953.5988 | 296 | 1 | 51
38953.6009 | 809 | 1 | 51
38953.6031 | 1471 | 0 | 51
38953.6052 | 1804 | 0 | 51
38953.6073 | 2166 | 0 | 51
38953.6095 | 2187 | 0 | 51
38953.6116 | 2022 | 0 | 51
38953.6137 | 1628 | 0 | 51
38953.6159 | 1726 | 0 | 51
51
38953.571 | 1 | 0 | 52
38953.5731 | 1 | 0 | 52
38953.5753 | 1 | 0 | 52
38953.5774 | 1 | 0 | 52
38953.5795 | 1 | 0 | 52
38953.5817 | 1 | 0 | 52
38953.5838 | 1 | 0 | 52
38953.586 | 1 | 0 | 52
38953.5881 | 1 | 0 | 52
38953.5902 | 1 | 0 | 52
38953.5924 | 1 | 0 | 52
38953.5945 | 1 | 0 | 52
38953.5967 | 28 | 23 | 52
38953.5988 | 2343 | 0 | 52
38953.6009 | 2337 | 1 | 52
38953.6031 | 2004 | 0 | 52
38953.6052 | 1995 | 0 | 52
38953.6073 | 1972 | 0 | 52
38953.6095 | 2479 | 0 | 52
38953.6116 | 2178 | 0 | 52
38953.6138 | 2523 | 0 | 52
38953.6159 | 2032 | 0 | 52
52
38953.571 | 1 | 0 | 53
38953.5731 | 1 | 0 | 53
38953.5753 | 1 | 0 | 53
38953.5774 | 1 | 0 | 53
38953.5796 | 1 | 0 | 53
38953.5817 | 1 | 0 | 53
38953.5838 | 1 | 0 | 53
38953.586 | 1 | 0 | 53
38953.5881 | 1 | 0 | 53
38953.5903 | 1 | 0 | 53
38953.5924 | 1 | 0 | 53
38953.5945 | 1 | 0 | 53
38953.5967 | 1 | 0 | 53
38953.5988 | 375 | 0 | 53
38953.6009 | 763 | 0 | 53
38953.6031 | 1422 | 0 | 53
38953.6052 | 2162 | 0 | 53
38953.6074 | 2101 | 0 | 53
38953.6095 | 2058 | 0 | 53
38953.6116 | 1870 | 7 | 53
38953.6138 | 1682 | 336 | 53
38953.6159 | 1636 | 1 | 53
53
38953.571 | 1 | 0 | 54
38953.5732 | 1 | 0 | 54
38953.5753 | 1 | 0 | 54
38953.5774 | 1 | 0 | 54
38953.5796 | 1 | 0 | 54
38953.5817 | 1 | 0 | 54
38953.5839 | 1 | 0 | 54
38953.586 | 1 | 0 | 54
38953.5881 | 1 | 0 | 54
38953.5903 | 1 | 0 | 54
38953.5924 | 1 | 0 | 54
38953.5945 | 1 | 0 | 54
38953.5967 | 1 | 0 | 54
38953.5988 | 3 | 0 | 54
38953.601 | 1969 | 0 | 54
38953.6031 | 2318 | 0 | 54
38953.6052 | 2376 | 0 | 54
38953.6074 | 2507 | 0 | 54
38953.6095 | 2164 | 0 | 54
38953.6117 | 2316 | 0 | 54
38953.6138 | 1791 | 161 | 54
38953.6159 | 2108 | 1 | 54
54
38953.571 | 1 | 0 | 55
38953.5732 | 1 | 0 | 55
38953.5753 | 1 | 0 | 55
38953.5775 | 1 | 0 | 55
38953.5796 | 1 | 0 | 55
38953.5817 | 1 | 0 | 55
38953.5839 | 1 | 0 | 55
38953.586 | 1 | 0 | 55
38953.5881 | 1 | 0 | 55
38953.5903 | 1 | 0 | 55
38953.5924 | 1 | 0 | 55
38953.5946 | 1 | 0 | 55
38953.5967 | 1 | 0 | 55
38953.5988 | 358 | 0 | 55
38953.601 | 699 | 0 | 55
38953.6031 | 1822 | 0 | 55
38953.6053 | 1933 | 0 | 55
38953.6074 | 1805 | 0 | 55
38953.6095 | 2243 | 0 | 55
38953.6117 | 2251 | 1 | 55
38953.6138 | 1824 | 384 | 55
38953.6159 | 1731 | 1 | 55
55
38953.5711 | 1 | 0 | 56
38953.5732 | 1 | 0 | 56
38953.5753 | 1 | 0 | 56
38953.5775 | 1 | 0 | 56
38953.5796 | 1 | 0 | 56
38953.5817 | 1 | 0 | 56
38953.5839 | 1 | 0 | 56
38953.586 | 1 | 0 | 56
38953.5882 | 1 | 0 | 56
38953.5903 | 1 | 0 | 56
38953.5924 | 1 | 0 | 56
38953.5946 | 1 | 0 | 56
38953.5967 | 1 | 0 | 56
38953.5989 | 2 | 0 | 56
38953.601 | 2011 | 0 | 56
38953.6031 | 2115 | 0 | 56
38953.6053 | 2327 | 0 | 56
38953.6074 | 2530 | 0 | 56
38953.6095 | 2527 | 0 | 56
38953.6117 | 2325 | 1 | 56
38953.6138 | 1692 | 202 | 56
38953.616 | 2242 | 1 | 56
56
38953.5711 | 1 | 0 | 57
38953.5732 | 1 | 0 | 57
38953.5753 | 1 | 0 | 57
38953.5775 | 1 | 0 | 57
38953.5796 | 1 | 0 | 57
38953.5818 | 1 | 0 | 57
38953.5839 | 1 | 0 | 57
38953.586 | 1 | 0 | 57
38953.5882 | 1 | 0 | 57
38953.5903 | 1 | 0 | 57
38953.5925 | 1 | 0 | 57
38953.5946 | 1 | 0 | 57
38953.5967 | 2 | 0 | 57
38953.5989 | 506 | 2 | 57
38953.601 | 779 | 0 | 57
38953.6031 | 1564 | 0 | 57
38953.6053 | 2122 | 0 | 57
38953.6074 | 1822 | 0 | 57
38953.6096 | 2185 | 0 | 57
38953.6117 | 1906 | 0 | 57
38953.6138 | 1637 | 1 | 57
38953.616 | 1836 | 0 | 57
57
38953.5711 | 1 | 0 | 58
38953.5732 | 1 | 0 | 58
38953.5754 | 1 | 0 | 58
38953.5775 | 1 | 0 | 58
38953.5796 | 1 | 0 | 58
38953.5818 | 1 | 0 | 58
38953.5839 | 1 | 0 | 58
38953.5861 | 1 | 0 | 58
38953.5882 | 1 | 0 | 58
38953.5903 | 1 | 0 | 58
38953.5925 | 1 | 0 | 58
38953.5946 | 1 | 0 | 58
38953.5967 | 2 | 0 | 58
38953.5989 | 358 | 1 | 58
38953.601 | 2007 | 1 | 58
38953.6032 | 2399 | 0 | 58
38953.6053 | 2351 | 0 | 58
38953.6074 | 2290 | 0 | 58
38953.6096 | 2527 | 0 | 58
38953.6117 | 1965 | 0 | 58
38953.6139 | 2214 | 0 | 58
38953.616 | 2163 | 0 | 58
58
38953.5711 | 1 | 0 | 59
38953.5732 | 1 | 0 | 59
38953.5754 | 1 | 0 | 59
38953.5775 | 1 | 0 | 59
38953.5797 | 1 | 0 | 59
38953.5818 | 1 | 0 | 59
38953.5839 | 1 | 0 | 59
38953.5861 | 1 | 0 | 59
38953.5882 | 1 | 0 | 59
38953.5903 | 1 | 0 | 59
38953.5925 | 1 | 0 | 59
38953.5946 | 1 | 0 | 59
38953.5968 | 1 | 0 | 59
38953.5989 | 626 | 1 | 59
38953.601 | 772 | 0 | 59
38953.6032 | 1904 | 0 | 59
38953.6053 | 1800 | 0 | 59
38953.6075 | 1831 | 0 | 59
38953.6096 | 1941 | 0 | 59
38953.6117 | 1984 | 0 | 59
38953.6139 | 1657 | 0 | 59
38953.616 | 1775 | 0 | 59
59
38953.5711 | 1 | 0 | 60
38953.5733 | 1 | 0 | 60
38953.5754 | 1 | 0 | 60
38953.5775 | 1 | 0 | 60
38953.5797 | 1 | 0 | 60
38953.5818 | 1 | 0 | 60
38953.5839 | 1 | 0 | 60
38953.5861 | 1 | 0 | 60
38953.5882 | 1 | 0 | 60
38953.5904 | 1 | 0 | 60
38953.5925 | 1 | 0 | 60
38953.5946 | 1 | 0 | 60
38953.5968 | 1 | 0 | 60
38953.5989 | 1545 | 0 | 60
38953.6011 | 1965 | 0 | 60
38953.6032 | 2500 | 0 | 60
38953.6053 | 2003 | 0 | 60
38953.6075 | 2087 | 0 | 60
38953.6096 | 2397 | 0 | 60
38953.6117 | 1965 | 0 | 60
38953.6139 | 2010 | 0 | 60
38953.616 | 2377 | 0 | 60
60
38953.5711 | 1 | 0 | 61
38953.5733 | 1 | 0 | 61
38953.5754 | 1 | 0 | 61
38953.5776 | 1 | 0 | 61
38953.5797 | 1 | 0 | 61
38953.5818 | 1 | 0 | 61
38953.584 | 1 | 0 | 61
38953.5861 | 1 | 0 | 61
38953.5882 | 1 | 0 | 61
38953.5904 | 1 | 0 | 61
38953.5925 | 1 | 0 | 61
38953.5947 | 1 | 0 | 61
38953.5968 | 51 | 41 | 61
38953.5989 | 849 | 81 | 61
38953.6011 | 932 | 236 | 61
38953.6032 | 1642 | 33 | 61
38953.6054 | 1885 | 6 | 61
38953.6075 | 2200 | 2 | 61
38953.6096 | 2250 | 1 | 61
38953.6118 | 1959 | 3 | 61
38953.6139 | 1425 | 195 | 61
38953.6161 | 2070 | 41 | 61
61
38953.5712 | 1 | 0 | 62
38953.5733 | 1 | 0 | 62
38953.5754 | 1 | 0 | 62
38953.5776 | 1 | 0 | 62
38953.5797 | 1 | 0 | 62
38953.5819 | 1 | 0 | 62
38953.584 | 1 | 0 | 62
38953.5861 | 1 | 0 | 62
38953.5883 | 1 | 0 | 62
38953.5904 | 1 | 0 | 62
38953.5925 | 1 | 0 | 62
38953.5947 | 1 | 0 | 62
38953.5968 | 44 | 37 | 62
38953.599 | 443 | 99 | 62
38953.6011 | 1105 | 229 | 62
38953.6032 | 1548 | 38 | 62
38953.6054 | 1639 | 8 | 62
38953.6075 | 2066 | 2 | 62
38953.6097 | 2055 | 0 | 62
38953.6118 | 1826 | 4 | 62
38953.6139 | 1799 | 235 | 62
38953.6161 | 1844 | 33 | 62
62
38953.5712 | 1 | 0 | 63
38953.5733 | 1 | 0 | 63
38953.5755 | 1 | 0 | 63
38953.5776 | 1 | 0 | 63
38953.5797 | 1 | 0 | 63
38953.5819 | 1 | 0 | 63
38953.584 | 1 | 0 | 63
38953.5861 | 1 | 0 | 63
38953.5883 | 1 | 0 | 63
38953.5904 | 1 | 0 | 63
38953.5926 | 1 | 0 | 63
38953.5947 | 1 | 0 | 63
38953.5968 | 58 | 48 | 63
38953.599 | 608 | 136 | 63
38953.6011 | 1064 | 252 | 63
38953.6033 | 1713 | 28 | 63
38953.6054 | 2073 | 7 | 63
38953.6075 | 1838 | 2 | 63
38953.6097 | 1882 | 0 | 63
38953.6118 | 1986 | 3 | 63
38953.6139 | 1797 | 221 | 63
38953.6161 | 1824 | 23 | 63
63
38953.5712 | 1 | 0 | 64
38953.5733 | 1 | 0 | 64
38953.5755 | 1 | 0 | 64
38953.5776 | 1 | 0 | 64
38953.5797 | 1 | 0 | 64
38953.5819 | 1 | 0 | 64
38953.584 | 1 | 0 | 64
38953.5862 | 1 | 0 | 64
38953.5883 | 1 | 0 | 64
38953.5904 | 1 | 0 | 64
38953.5926 | 2 | 0 | 64
38953.5947 | 1 | 0 | 64
38953.5969 | 48 | 46 | 64
38953.599 | 391 | 134 | 64
38953.6011 | 969 | 183 | 64
38953.6033 | 1290 | 24 | 64
38953.6054 | 1633 | 7 | 64
38953.6075 | 2093 | 2 | 64
38953.6097 | 1806 | 0 | 64
38953.6118 | 2092 | 7 | 64
38953.614 | 1556 | 203 | 64
38953.6161 | 1530 | 24 | 64
64
38953.5712 | 1 | 0 | 65
38953.5733 | 1 | 0 | 65
38953.5755 | 1 | 0 | 65
38953.5776 | 1 | 0 | 65
38953.5798 | 1 | 0 | 65
38953.5819 | 1 | 0 | 65
38953.584 | 1 | 0 | 65
38953.5862 | 1 | 0 | 65
38953.5883 | 1 | 0 | 65
38953.5905 | 1 | 0 | 65
38953.5926 | 1 | 0 | 65
38953.5947 | 2 | 0 | 65
38953.5969 | 31 | 24 | 65
38953.599 | 649 | 0 | 65
38953.6011 | 921 | 0 | 65
38953.6033 | 1981 | 0 | 65
38953.6054 | 1861 | 1 | 65
38953.6076 | 2043 | 0 | 65
38953.6097 | 2201 | 0 | 65
38953.6118 | 2006 | 0 | 65
38953.614 | 1391 | 0 | 65
38953.6161 | 1643 | 0 | 65
65
38953.5712 | 1 | 0 | 66
38953.5734 | 1 | 0 | 66
38953.5755 | 1 | 0 | 66
38953.5776 | 1 | 0 | 66
38953.5798 | 1 | 0 | 66
38953.5819 | 1 | 0 | 66
38953.5841 | 1 | 0 | 66
38953.5862 | 1 | 0 | 66
38953.5883 | 1 | 0 | 66
38953.5905 | 1 | 0 | 66
38953.5926 | 1 | 0 | 66
38953.5947 | 2 | 0 | 66
38953.5969 | 37 | 31 | 66
38953.599 | 2034 | 0 | 66
38953.6012 | 2253 | 0 | 66
38953.6033 | 2420 | 0 | 66
38953.6054 | 2039 | 0 | 66
38953.6076 | 2097 | 0 | 66
38953.6097 | 2035 | 0 | 66
38953.6119 | 2356 | 0 | 66
38953.614 | 2141 | 0 | 66
38953.6161 | 2193 | 0 | 66
66
38953.5712 | 1 | 0 | 67
38953.5734 | 1 | 0 | 67
38953.5755 | 1 | 0 | 67
38953.5777 | 1 | 0 | 67
38953.5798 | 1 | 0 | 67
38953.5819 | 1 | 0 | 67
38953.5841 | 1 | 0 | 67
38953.5862 | 1 | 0 | 67
38953.5883 | 1 | 0 | 67
38953.5905 | 1 | 0 | 67
38953.5926 | 1 | 0 | 67
38953.5948 | 1 | 0 | 67
38953.5969 | 37 | 31 | 67
38953.599 | 940 | 0 | 67
38953.6012 | 946 | 0 | 67
38953.6033 | 1899 | 0 | 67
38953.6055 | 1912 | 0 | 67
38953.6076 | 2084 | 0 | 67
38953.6097 | 2318 | 0 | 67
38953.6119 | 2038 | 0 | 67
38953.614 | 1580 | 0 | 67
38953.6161 | 1720 | 0 | 67
67
38953.5713 | 1 | 0 | 68
38953.5734 | 1 | 0 | 68
38953.5755 | 1 | 0 | 68
38953.5777 | 1 | 0 | 68
38953.5798 | 1 | 0 | 68
38953.5819 | 1 | 0 | 68
38953.5841 | 1 | 0 | 68
38953.5862 | 1 | 0 | 68
38953.5884 | 1 | 0 | 68
38953.5905 | 1 | 0 | 68
38953.5926 | 1 | 0 | 68
38953.5948 | 1 | 0 | 68
38953.5969 | 46 | 44 | 68
38953.5991 | 2080 | 0 | 68
38953.6012 | 2036 | 0 | 68
38953.6033 | 2352 | 0 | 68
38953.6055 | 2439 | 0 | 68
38953.6076 | 2546 | 0 | 68
38953.6097 | 2365 | 0 | 68
38953.6119 | 2142 | 0 | 68
38953.614 | 2135 | 0 | 68
38953.6162 | 2164 | 0 | 68
68
38953.5713 | 1 | 0 | 69
38953.5734 | 1 | 0 | 69
38953.5755 | 1 | 0 | 69
38953.5777 | 1 | 0 | 69
38953.5798 | 1 | 0 | 69
38953.582 | 1 | 0 | 69
38953.5841 | 1 | 0 | 69
38953.5862 | 1 | 0 | 69
38953.5884 | 1 | 0 | 69
38953.5905 | 1 | 0 | 69
38953.5927 | 1 | 0 | 69
38953.5948 | 1 | 0 | 69
38953.5969 | 1 | 0 | 69
38953.5991 | 1337 | 0 | 69
38953.6012 | 871 | 0 | 69
38953.6033 | 1688 | 0 | 69
38953.6055 | 1831 | 0 | 69
38953.6076 | 2217 | 0 | 69
38953.6098 | 2353 | 0 | 69
38953.6119 | 1817 | 2 | 69
38953.614 | 1609 | 333 | 69
38953.6162 | 1755 | 5 | 69
69
38953.5713 | 1 | 0 | 70
38953.5734 | 1 | 0 | 70
38953.5756 | 1 | 0 | 70
38953.5777 | 1 | 0 | 70
38953.5798 | 1 | 0 | 70
38953.582 | 1 | 0 | 70
38953.5841 | 1 | 0 | 70
38953.5863 | 1 | 0 | 70
38953.5884 | 1 | 0 | 70
38953.5905 | 1 | 0 | 70
38953.5927 | 1 | 0 | 70
38953.5948 | 1 | 0 | 70
38953.5969 | 1 | 0 | 70
38953.5991 | 9 | 0 | 70
38953.6012 | 1954 | 0 | 70
38953.6034 | 2374 | 0 | 70
38953.6055 | 2479 | 0 | 70
38953.6076 | 2291 | 0 | 70
38953.6098 | 2106 | 0 | 70
38953.6119 | 2116 | 1 | 70
38953.6141 | 1551 | 324 | 70
38953.6162 | 2149 | 4 | 70
70
38953.5713 | 1 | 0 | 71
38953.5734 | 1 | 0 | 71
38953.5756 | 1 | 0 | 71
38953.5777 | 1 | 0 | 71
38953.5798 | 1 | 0 | 71
38953.582 | 1 | 0 | 71
38953.5841 | 1 | 0 | 71
38953.5863 | 1 | 0 | 71
38953.5884 | 1 | 0 | 71
38953.5905 | 1 | 0 | 71
38953.5927 | 1 | 0 | 71
38953.5948 | 1 | 0 | 71
38953.597 | 1 | 0 | 71
38953.5991 | 1515 | 0 | 71
38953.6012 | 1023 | 0 | 71
38953.6034 | 1703 | 0 | 71
38953.6055 | 1771 | 0 | 71
38953.6077 | 2150 | 0 | 71
38953.6098 | 2110 | 0 | 71
38953.6119 | 1858 | 6 | 71
38953.6141 | 1452 | 300 | 71
38953.6162 | 1645 | 6 | 71
71
38953.5713 | 1 | 0 | 72
38953.5734 | 1 | 0 | 72
38953.5756 | 1 | 0 | 72
38953.5777 | 1 | 0 | 72
38953.5799 | 1 | 0 | 72
38953.582 | 1 | 0 | 72
38953.5841 | 1 | 0 | 72
38953.5863 | 1 | 0 | 72
38953.5884 | 1 | 0 | 72
38953.5906 | 1 | 0 | 72
38953.5927 | 1 | 0 | 72
38953.5948 | 1 | 0 | 72
38953.597 | 1 | 0 | 72
38953.5991 | 607 | 0 | 72
38953.6012 | 2162 | 0 | 72
38953.6034 | 1980 | 0 | 72
38953.6055 | 2057 | 0 | 72
38953.6077 | 1963 | 0 | 72
38953.6098 | 2126 | 0 | 72
38953.6119 | 2071 | 2 | 72
38953.6141 | 2262 | 307 | 72
38953.6162 | 1943 | 10 | 72
72
38953.5713 | 1 | 0 | 73
38953.5735 | 1 | 0 | 73
38953.5756 | 1 | 0 | 73
38953.5777 | 1 | 0 | 73
38953.5799 | 1 | 0 | 73
38953.582 | 1 | 0 | 73
38953.5842 | 1 | 0 | 73
38953.5863 | 1 | 0 | 73
38953.5884 | 1 | 0 | 73
38953.5906 | 1 | 0 | 73
38953.5927 | 1 | 0 | 73
38953.5949 | 1 | 0 | 73
38953.597 | 1 | 0 | 73
38953.5991 | 1396 | 1 | 73
38953.6013 | 873 | 0 | 73
38953.6034 | 1763 | 0 | 73
38953.6055 | 1863 | 0 | 73
38953.6077 | 1862 | 0 | 73
38953.6098 | 1820 | 0 | 73
38953.612 | 1897 | 0 | 73
38953.6141 | 1976 | 1 | 73
38953.6162 | 1611 | 0 | 73
73
38953.5713 | 1 | 0 | 74
38953.5735 | 1 | 0 | 74
38953.5756 | 1 | 0 | 74
38953.5778 | 2 | 0 | 74
38953.5799 | 1 | 0 | 74
38953.582 | 1 | 0 | 74
38953.5842 | 1 | 0 | 74
38953.5863 | 1 | 0 | 74
38953.5885 | 1 | 0 | 74
38953.5906 | 1 | 0 | 74
38953.5927 | 1 | 0 | 74
38953.5949 | 1 | 0 | 74
38953.597 | 1 | 0 | 74
38953.5991 | 2441 | 0 | 74
38953.6013 | 2316 | 0 | 74
38953.6034 | 1973 | 0 | 74
38953.6056 | 2471 | 0 | 74
38953.6077 | 1958 | 0 | 74
38953.6098 | 2450 | 0 | 74
38953.612 | 2536 | 0 | 74
38953.6141 | 2389 | 0 | 74
38953.6163 | 2107 | 0 | 74
74
38953.5714 | 1 | 0 | 75
38953.5735 | 1 | 0 | 75
38953.5756 | 1 | 0 | 75
38953.5778 | 1 | 0 | 75
38953.5799 | 1 | 0 | 75
38953.5821 | 1 | 0 | 75
38953.5842 | 1 | 0 | 75
38953.5863 | 1 | 0 | 75
38953.5885 | 1 | 0 | 75
38953.5906 | 1 | 0 | 75
38953.5928 | 1 | 0 | 75
38953.5949 | 1 | 0 | 75
38953.597 | 1 | 0 | 75
38953.5992 | 1645 | 0 | 75
38953.6013 | 907 | 0 | 75
38953.6034 | 2038 | 0 | 75
38953.6056 | 1808 | 0 | 75
38953.6077 | 1910 | 0 | 75
38953.6099 | 2058 | 0 | 75
38953.612 | 1774 | 0 | 75
38953.6141 | 1740 | 0 | 75
38953.6163 | 1724 | 0 | 75
75
38953.5714 | 1 | 0 | 76
38953.5735 | 1 | 0 | 76
38953.5757 | 1 | 0 | 76
38953.5778 | 1 | 0 | 76
38953.5799 | 1 | 0 | 76
38953.5821 | 1 | 0 | 76
38953.5842 | 1 | 0 | 76
38953.5864 | 1 | 0 | 76
38953.5885 | 1 | 0 | 76
38953.5906 | 1 | 0 | 76
38953.5928 | 1 | 0 | 76
38953.5949 | 1 | 0 | 76
38953.597 | 1 | 0 | 76
38953.5992 | 1961 | 0 | 76
38953.6013 | 2400 | 0 | 76
38953.6035 | 2444 | 0 | 76
38953.6056 | 2131 | 0 | 76
38953.6077 | 2232 | 0 | 76
38953.6099 | 2155 | 0 | 76
38953.612 | 2164 | 0 | 76
38953.6142 | 2512 | 0 | 76
38953.6163 | 2161 | 0 | 76
76
38953.5714 | 1 | 0 | 77
38953.5735 | 1 | 0 | 77
38953.5757 | 1 | 0 | 77
38953.5778 | 1 | 0 | 77
38953.58 | 1 | 0 | 77
38953.5821 | 1 | 0 | 77
38953.5842 | 1 | 0 | 77
38953.5864 | 1 | 0 | 77
38953.5885 | 1 | 0 | 77
38953.5906 | 1182 | 1190 | 77
38953.5928 | 1132 | 1183 | 77
38953.5949 | 1070 | 1155 | 77
38953.5971 | 1166 | 1139 | 77
38953.5992 | 1159 | 808 | 77
38953.6013 | 1651 | 709 | 77
38953.6035 | 1707 | 413 | 77
38953.6056 | 1617 | 260 | 77
38953.6078 | 2056 | 173 | 77
38953.6099 | 2101 | 105 | 77
38953.612 | 2181 | 151 | 77
38953.6142 | 1715 | 303 | 77
38953.6163 | 1991 | 320 | 77
77
38953.5714 | 1 | 0 | 78
38953.5736 | 1 | 0 | 78
38953.5757 | 1 | 0 | 78
38953.5778 | 1 | 0 | 78
38953.58 | 1 | 0 | 78
38953.5821 | 1 | 0 | 78
38953.5842 | 1 | 0 | 78
38953.5864 | 1 | 0 | 78
38953.5885 | 1 | 0 | 78
38953.5907 | 1131 | 1106 | 78
38953.5928 | 1138 | 1186 | 78
38953.5949 | 955 | 928 | 78
38953.5971 | 1121 | 1092 | 78
38953.5992 | 1090 | 791 | 78
38953.6014 | 1466 | 541 | 78
38953.6035 | 1851 | 495 | 78
38953.6056 | 1646 | 259 | 78
38953.6078 | 1900 | 157 | 78
38953.6099 | 2313 | 116 | 78
38953.612 | 1970 | 132 | 78
38953.6142 | 1636 | 290 | 78
38953.6163 | 1673 | 342 | 78
78
38953.5714 | 1 | 0 | 79
38953.5736 | 1 | 0 | 79
38953.5757 | 1 | 0 | 79
38953.5778 | 1 | 0 | 79
38953.58 | 1 | 0 | 79
38953.5821 | 1 | 0 | 79
38953.5843 | 1 | 0 | 79
38953.5864 | 1 | 0 | 79
38953.5885 | 1 | 0 | 79
38953.5907 | 2 | 6 | 79
38953.5928 | 2 | 6 | 79
38953.595 | 2 | 6 | 79
38953.5971 | 5 | 7 | 79
38953.5992 | 520 | 4 | 79
38953.6014 | 1176 | 2 | 79
38953.6035 | 1471 | 1 | 79
38953.6056 | 1939 | 1 | 79
38953.6078 | 1731 | 0 | 79
38953.6099 | 1799 | 0 | 79
38953.6121 | 1823 | 0 | 79
38953.6142 | 1511 | 1 | 79
38953.6163 | 1601 | 0 | 79
79
38953.5714 | 1 | 0 | 80
38953.5736 | 1 | 0 | 80
38953.5757 | 1 | 0 | 80
38953.5779 | 1 | 0 | 80
38953.58 | 1 | 0 | 80
38953.5821 | 1 | 0 | 80
38953.5843 | 1 | 0 | 80
38953.5864 | 1 | 0 | 80
38953.5886 | 1 | 0 | 80
38953.5907 | 2 | 3 | 80
38953.5928 | 2 | 3 | 80
38953.595 | 2 | 3 | 80
38953.5971 | 5 | 4 | 80
38953.5992 | 1934 | 1 | 80
38953.6014 | 2291 | 1 | 80
38953.6035 | 2051 | 0 | 80
38953.6057 | 1982 | 0 | 80
38953.6078 | 2489 | 0 | 80
38953.6099 | 2501 | 0 | 80
38953.6121 | 2477 | 0 | 80
38953.6142 | 2386 | 1 | 80
38953.6164 | 2184 | 0 | 80
80
38953.5715 | 1 | 0 | 81
38953.5736 | 1 | 0 | 81
38953.5757 | 2 | 0 | 81
38953.5779 | 1 | 0 | 81
38953.58 | 1 | 0 | 81
38953.5822 | 1 | 0 | 81
38953.5843 | 1 | 0 | 81
38953.5864 | 1 | 0 | 81
38953.5886 | 1 | 0 | 81
38953.5907 | 2 | 2 | 81
38953.5928 | 1 | 2 | 81
38953.595 | 1 | 2 | 81
38953.5971 | 4 | 2 | 81
38953.5993 | 471 | 1 | 81
38953.6014 | 821 | 0 | 81
38953.6035 | 1419 | 0 | 81
38953.6057 | 1666 | 0 | 81
38953.6078 | 2052 | 0 | 81
38953.61 | 2165 | 0 | 81
38953.6142 | 1881 | 0 | 81
38953.6164 | 1682 | 0 | 81
81
38953.5715 | 1 | 0 | 82
38953.5736 | 1 | 0 | 82
38953.5758 | 1 | 0 | 82
38953.5779 | 1 | 0 | 82
38953.58 | 1 | 0 | 82
38953.5822 | 1 | 0 | 82
38953.5843 | 1 | 0 | 82
38953.5864 | 1 | 0 | 82
38953.5886 | 1 | 0 | 82
38953.5907 | 1 | 1 | 82
38953.5929 | 1 | 1 | 82
38953.595 | 1 | 1 | 82
38953.5971 | 5 | 2 | 82
38953.5993 | 2422 | 1 | 82
38953.6014 | 2511 | 0 | 82
38953.6036 | 2388 | 0 | 82
38953.6057 | 2013 | 0 | 82
38953.6078 | 2443 | 0 | 82
38953.61 | 2233 | 0 | 82
38953.6121 | 2356 | 0 | 82
38953.6142 | 2213 | 0 | 82
38953.6164 | 2273 | 0 | 82
82
38953.5715 | 1 | 0 | 83
38953.5736 | 1 | 0 | 83
38953.5758 | 1 | 0 | 83
38953.5779 | 1 | 0 | 83
38953.58 | 1 | 0 | 83
38953.5822 | 1 | 0 | 83
38953.5843 | 1 | 0 | 83
38953.5865 | 1 | 0 | 83
38953.5886 | 1 | 0 | 83
38953.5907 | 1 | 1 | 83
38953.5929 | 1 | 1 | 83
38953.595 | 1 | 1 | 83
38953.5972 | 1 | 1 | 83
38953.5993 | 478 | 1 | 83
38953.6014 | 1014 | 0 | 83
38953.6036 | 1401 | 0 | 83
38953.6057 | 1522 | 0 | 83
38953.6078 | 2165 | 0 | 83
38953.61 | 1788 | 0 | 83
38953.6121 | 2205 | 0 | 83
38953.6143 | 1508 | 0 | 83
38953.6164 | 1716 | 0 | 83
83
38953.5715 | 1 | 0 | 84
38953.5736 | 1 | 0 | 84
38953.5758 | 1 | 0 | 84
38953.5779 | 1 | 0 | 84
38953.5801 | 1 | 0 | 84
38953.5822 | 1 | 0 | 84
38953.5843 | 1 | 0 | 84
38953.5865 | 1 | 0 | 84
38953.5886 | 1 | 0 | 84
38953.5908 | 1 | 1 | 84
38953.5929 | 2 | 0 | 84
38953.595 | 1 | 0 | 84
38953.5972 | 1 | 0 | 84
38953.5993 | 1476 | 0 | 84
38953.6014 | 2095 | 0 | 84
38953.6036 | 1990 | 0 | 84
38953.6057 | 2074 | 0 | 84
38953.6079 | 1995 | 0 | 84
38953.61 | 2287 | 0 | 84
38953.6121 | 1935 | 0 | 84
38953.6143 | 2199 | 0 | 84
38953.6164 | 2200 | 0 | 84
84
38953.5715 | 1 | 0 | 85
38953.5737 | 1 | 0 | 85
38953.5758 | 1 | 0 | 85
38953.5779 | 1 | 0 | 85
38953.5801 | 1 | 0 | 85
38953.5822 | 1 | 0 | 85
38953.5844 | 1 | 0 | 85
38953.5865 | 1 | 0 | 85
38953.5886 | 1 | 0 | 85
38953.5908 | 1 | 1 | 85
38953.5929 | 1 | 1 | 85
38953.595 | 1 | 0 | 85
38953.5972 | 1 | 1 | 85
38953.5993 | 522 | 0 | 85
38953.6015 | 1013 | 0 | 85
38953.6036 | 1677 | 0 | 85
38953.6057 | 1668 | 0 | 85
38953.6079 | 1735 | 0 | 85
38953.61 | 2085 | 0 | 85
38953.6122 | 1917 | 0 | 85
38953.6143 | 1545 | 0 | 85
38953.6164 | 1732 | 0 | 85
85
38953.5715 | 1 | 0 | 86
38953.5737 | 1 | 0 | 86
38953.5758 | 1 | 0 | 86
38953.578 | 1 | 0 | 86
38953.5801 | 1 | 0 | 86
38953.5822 | 1 | 0 | 86
38953.5844 | 1 | 0 | 86
38953.5865 | 1 | 0 | 86
38953.5886 | 1 | 0 | 86
38953.5908 | 1 | 0 | 86
38953.5929 | 1 | 0 | 86
38953.5951 | 1 | 0 | 86
38953.5972 | 2 | 0 | 86
38953.5993 | 2443 | 0 | 86
38953.6015 | 2265 | 0 | 86
38953.6036 | 2482 | 0 | 86
38953.6058 | 2408 | 0 | 86
38953.6079 | 2140 | 0 | 86
38953.61 | 2137 | 0 | 86
38953.6122 | 1970 | 0 | 86
38953.6143 | 2162 | 0 | 86
38953.6164 | 2047 | 0 | 86
86
38953.5716 | 1 | 0 | 87
38953.5737 | 1 | 0 | 87
38953.5758 | 1 | 0 | 87
38953.578 | 1 | 0 | 87
38953.5801 | 1 | 0 | 87
38953.5823 | 1 | 0 | 87
38953.5844 | 1 | 0 | 87
38953.5865 | 1 | 0 | 87
38953.5887 | 1 | 0 | 87
38953.5908 | 1 | 0 | 87
38953.5929 | 1 | 0 | 87
38953.5951 | 1 | 0 | 87
38953.5972 | 3 | 1 | 87
38953.5994 | 484 | 0 | 87
38953.6015 | 1067 | 0 | 87
38953.6036 | 1504 | 0 | 87
38953.6058 | 1813 | 0 | 87
38953.6079 | 2147 | 0 | 87
38953.6101 | 2139 | 0 | 87
38953.6122 | 1929 | 0 | 87
38953.6143 | 1827 | 0 | 87
38953.6165 | 1643 | 0 | 87
87
38953.5716 | 1 | 0 | 88
38953.5737 | 1 | 0 | 88
38953.5759 | 1 | 0 | 88
38953.578 | 1 | 0 | 88
38953.5801 | 1 | 0 | 88
38953.5823 | 1 | 0 | 88
38953.5844 | 1 | 0 | 88
38953.5865 | 1 | 0 | 88
38953.5887 | 1 | 0 | 88
38953.5908 | 1 | 0 | 88
38953.593 | 1 | 0 | 88
38953.5951 | 1 | 0 | 88
38953.5972 | 2 | 0 | 88
38953.5994 | 2476 | 0 | 88
38953.6015 | 2454 | 0 | 88
38953.6037 | 2482 | 0 | 88
38953.6058 | 2364 | 0 | 88
38953.6079 | 2165 | 0 | 88
38953.6101 | 2306 | 0 | 88
38953.6122 | 2324 | 0 | 88
38953.6143 | 2546 | 0 | 88
38953.6165 | 2313 | 0 | 88
88
38953.5716 | 1 | 0 | 89
38953.5737 | 1 | 0 | 89
38953.5759 | 1 | 0 | 89
38953.578 | 1 | 0 | 89
38953.5802 | 1 | 0 | 89
38953.5823 | 1 | 0 | 89
38953.5844 | 1 | 0 | 89
38953.5866 | 1 | 0 | 89
38953.5887 | 1 | 0 | 89
38953.5908 | 1 | 0 | 89
38953.593 | 1 | 0 | 89
38953.5951 | 1 | 0 | 89
38953.5973 | 3 | 1 | 89
38953.5994 | 588 | 0 | 89
38953.6015 | 1050 | 0 | 89
38953.6037 | 1369 | 0 | 89
38953.6058 | 1563 | 0 | 89
38953.608 | 1917 | 0 | 89
38953.6101 | 1852 | 0 | 89
38953.6122 | 1651 | 0 | 89
38953.6144 | 1911 | 0 | 89
38953.6165 | 1936 | 0 | 89
89
38953.5716 | 1 | 0 | 90
38953.5738 | 1 | 0 | 90
38953.5759 | 1 | 0 | 90
38953.578 | 1 | 0 | 90
38953.5802 | 1 | 0 | 90
38953.5823 | 1 | 0 | 90
38953.5844 | 1 | 0 | 90
38953.5866 | 1 | 0 | 90
38953.5887 | 1 | 0 | 90
38953.5909 | 1 | 0 | 90
38953.593 | 1 | 0 | 90
38953.5951 | 1 | 0 | 90
38953.5973 | 2 | 1 | 90
38953.5994 | 2184 | 0 | 90
38953.6016 | 2009 | 0 | 90
38953.6037 | 2401 | 0 | 90
38953.6058 | 2499 | 0 | 90
38953.608 | 2471 | 0 | 90
38953.6101 | 2286 | 0 | 90
38953.6122 | 2185 | 0 | 90
38953.6144 | 2343 | 0 | 90
38953.6165 | 2490 | 0 | 90
90
38953.5716 | 1 | 0 | 91
38953.5738 | 1 | 0 | 91
38953.5759 | 1 | 0 | 91
38953.578 | 1 | 0 | 91
38953.5802 | 1 | 0 | 91
38953.5823 | 1 | 0 | 91
38953.5845 | 1 | 0 | 91
38953.5866 | 1 | 0 | 91
38953.5887 | 1 | 0 | 91
38953.5909 | 1 | 0 | 91
38953.593 | 1 | 0 | 91
38953.5952 | 1 | 0 | 91
38953.5973 | 4 | 2 | 91
38953.5994 | 571 | 0 | 91
38953.6016 | 888 | 0 | 91
38953.6037 | 1419 | 0 | 91
38953.6058 | 1997 | 0 | 91
38953.608 | 1742 | 0 | 91
38953.6101 | 1978 | 0 | 91
38953.6123 | 1714 | 0 | 91
38953.6144 | 1925 | 0 | 91
38953.6165 | 1948 | 0 | 91
91
38953.5716 | 1 | 0 | 92
38953.5738 | 1 | 0 | 92
38953.5759 | 1 | 0 | 92
38953.5781 | 1 | 0 | 92
38953.5802 | 1 | 0 | 92
38953.5823 | 1 | 0 | 92
38953.5845 | 1 | 0 | 92
38953.5866 | 1 | 0 | 92
38953.5888 | 1 | 0 | 92
38953.5909 | 1 | 0 | 92
38953.593 | 1 | 0 | 92
38953.5952 | 1 | 0 | 92
38953.5973 | 7 | 2 | 92
38953.5994 | 2460 | 0 | 92
38953.6016 | 1976 | 0 | 92
38953.6037 | 2183 | 0 | 92
38953.6059 | 2541 | 0 | 92
38953.608 | 2503 | 0 | 92
38953.6101 | 2275 | 0 | 92
38953.6123 | 2552 | 0 | 92
38953.6144 | 2296 | 0 | 92
38953.6166 | 2419 | 0 | 92
92
38953.5717 | 1 | 0 | 93
38953.5738 | 1 | 0 | 93
38953.5759 | 1 | 0 | 93
38953.5781 | 1 | 0 | 93
38953.5802 | 1 | 0 | 93
38953.5823 | 1 | 0 | 93
38953.5845 | 1 | 0 | 93
38953.5866 | 1 | 0 | 93
38953.5888 | 1 | 0 | 93
38953.5909 | 1 | 0 | 93
38953.593 | 1 | 0 | 93
38953.5952 | 1 | 0 | 93
38953.5973 | 5 | 2 | 93
38953.5995 | 498 | 0 | 93
38953.6016 | 1061 | 0 | 93
38953.6037 | 1522 | 0 | 93
38953.6059 | 1807 | 0 | 93
38953.608 | 2163 | 0 | 93
38953.6102 | 1940 | 0 | 93
38953.6123 | 2078 | 0 | 93
38953.6144 | 1934 | 0 | 93
38953.6166 | 2024 | 0 | 93
93
38953.5717 | 1 | 0 | 94
38953.5738 | 1 | 0 | 94
38953.5759 | 1 | 0 | 94
38953.5781 | 1 | 0 | 94
38953.5802 | 1 | 0 | 94
38953.5824 | 1 | 0 | 94
38953.5845 | 1 | 0 | 94
38953.5866 | 1 | 0 | 94
38953.5888 | 1 | 0 | 94
38953.5909 | 1 | 0 | 94
38953.5931 | 1 | 0 | 94
38953.5952 | 1 | 0 | 94
38953.5973 | 6 | 2 | 94
38953.5995 | 2373 | 0 | 94
38953.6016 | 2335 | 0 | 94
38953.6038 | 2446 | 0 | 94
38953.6059 | 2543 | 0 | 94
38953.608 | 2171 | 0 | 94
38953.6102 | 2261 | 0 | 94
38953.6123 | 2523 | 0 | 94
38953.6144 | 2341 | 0 | 94
38953.6166 | 2248 | 0 | 94
94
38953.5717 | 1 | 0 | 95
38953.5738 | 1 | 0 | 95
38953.576 | 1 | 0 | 95
38953.5781 | 1 | 0 | 95
38953.5802 | 1 | 0 | 95
38953.5824 | 1 | 0 | 95
38953.5845 | 1 | 0 | 95
38953.5867 | 1 | 0 | 95
38953.5888 | 1 | 0 | 95
38953.5909 | 1 | 0 | 95
38953.5931 | 1 | 0 | 95
38953.5952 | 1 | 0 | 95
38953.5973 | 1 | 0 | 95
38953.5995 | 603 | 0 | 95
38953.6016 | 1077 | 0 | 95
38953.6038 | 1780 | 0 | 95
38953.6059 | 1619 | 0 | 95
38953.608 | 1872 | 0 | 95
38953.6102 | 2100 | 0 | 95
38953.6123 | 2029 | 0 | 95
38953.6145 | 1801 | 0 | 95
38953.6166 | 1801 | 0 | 95
95
38953.5717 | 1 | 0 | 96
38953.5738 | 1 | 0 | 96
38953.576 | 1 | 0 | 96
38953.5781 | 1 | 0 | 96
38953.5803 | 1 | 0 | 96
38953.5824 | 1 | 0 | 96
38953.5845 | 1 | 0 | 96
38953.5867 | 1 | 0 | 96
38953.5888 | 1 | 0 | 96
38953.5909 | 1 | 0 | 96
38953.5931 | 1 | 0 | 96
38953.5952 | 1 | 0 | 96
38953.5974 | 2 | 0 | 96
38953.5995 | 2477 | 0 | 96
38953.6016 | 2446 | 0 | 96
38953.6038 | 2274 | 0 | 96
38953.6059 | 2487 | 0 | 96
38953.6081 | 2017 | 0 | 96
38953.6102 | 2161 | 0 | 96
38953.6123 | 2216 | 0 | 96
38953.6145 | 2025 | 0 | 96
38953.6166 | 2316 | 0 | 96
96
38953.5717 | 1 | 0 | 97
38953.5739 | 1 | 0 | 97
38953.576 | 1 | 0 | 97
38953.5781 | 1 | 0 | 97
38953.5803 | 1 | 0 | 97
38953.5824 | 1 | 0 | 97
38953.5845 | 1 | 0 | 97
38953.5867 | 1 | 0 | 97
38953.5888 | 1 | 0 | 97
38953.591 | 1 | 0 | 97
38953.5931 | 1 | 0 | 97
38953.5952 | 1 | 0 | 97
38953.5974 | 1 | 0 | 97
38953.5995 | 547 | 0 | 97
38953.6017 | 1035 | 0 | 97
38953.6038 | 1518 | 0 | 97
38953.6059 | 1907 | 0 | 97
38953.6081 | 2168 | 0 | 97
38953.6102 | 2074 | 0 | 97
38953.6123 | 2016 | 0 | 97
38953.6145 | 1901 | 0 | 97
38953.6166 | 1905 | 0 | 97
97
38953.5717 | 1 | 0 | 98
38953.5739 | 1 | 0 | 98
38953.576 | 1 | 0 | 98
38953.5781 | 1 | 0 | 98
38953.5803 | 1 | 0 | 98
38953.5824 | 1 | 0 | 98
38953.5846 | 1 | 0 | 98
38953.5867 | 1 | 0 | 98
38953.5888 | 1 | 0 | 98
38953.591 | 1 | 0 | 98
38953.5931 | 1 | 0 | 98
38953.5953 | 1 | 0 | 98
38953.5974 | 1 | 0 | 98
38953.5995 | 2147 | 0 | 98
38953.6038 | 2369 | 0 | 98
38953.6059 | 2129 | 0 | 98
38953.6081 | 2170 | 0 | 98
38953.6102 | 2169 | 0 | 98
38953.6124 | 2330 | 0 | 98
38953.6145 | 2300 | 1 | 98
38953.6166 | 2197 | 0 | 98
98
38953.5717 | 1 | 0 | 99
38953.5739 | 1 | 0 | 99
38953.576 | 1 | 0 | 99
38953.5782 | 1 | 0 | 99
38953.5803 | 1 | 0 | 99
38953.5824 | 1 | 0 | 99
38953.5846 | 1 | 0 | 99
38953.5867 | 1 | 0 | 99
38953.5889 | 1 | 0 | 99
38953.591 | 1 | 0 | 99
38953.5931 | 1 | 0 | 99
38953.5953 | 1 | 0 | 99
38953.5974 | 4 | 1 | 99
38953.5996 | 554 | 0 | 99
38953.6017 | 954 | 0 | 99
38953.6038 | 1740 | 0 | 99
38953.606 | 1825 | 0 | 99
38953.6081 | 1973 | 0 | 99
38953.6102 | 1881 | 0 | 99
38953.6124 | 1900 | 0 | 99
38953.6145 | 1793 | 0 | 99
38953.6167 | 2044 | 0 | 99
99
38953.5718 | 1 | 0 | 100
38953.5739 | 1 | 0 | 100
38953.576 | 1 | 0 | 100
38953.5782 | 1 | 0 | 100
38953.5803 | 1 | 0 | 100
38953.5825 | 1 | 0 | 100
38953.5846 | 1 | 0 | 100
38953.5867 | 1 | 0 | 100
38953.5889 | 1 | 0 | 100
38953.591 | 1 | 0 | 100
38953.5932 | 1 | 0 | 100
38953.5953 | 1 | 0 | 100
38953.5974 | 3 | 1 | 100
38953.5996 | 2362 | 0 | 100
38953.6017 | 1988 | 0 | 100
38953.6038 | 1953 | 0 | 100
38953.606 | 2519 | 0 | 100
38953.6081 | 2195 | 0 | 100
38953.6103 | 2352 | 0 | 100
38953.6124 | 2241 | 0 | 100
38953.6145 | 2329 | 0 | 100
38953.6167 | 2470 | 0 | 100
100
38953.5718 | 1 | 0 | 101
38953.5739 | 1 | 0 | 101
38953.5761 | 1 | 0 | 101
38953.5782 | 1 | 0 | 101
38953.5803 | 1 | 1 | 101
38953.5825 | 1 | 0 | 101
38953.5846 | 1 | 0 | 101
38953.5868 | 1 | 0 | 101
38953.5889 | 1 | 0 | 101
38953.591 | 1 | 0 | 101
38953.5932 | 1 | 0 | 101
38953.5953 | 1 | 0 | 101
38953.5975 | 4 | 1 | 101
38953.5996 | 579 | 0 | 101
38953.6017 | 1047 | 0 | 101
38953.6039 | 1821 | 0 | 101
38953.606 | 1625 | 0 | 101
38953.6081 | 1986 | 0 | 101
38953.6103 | 2159 | 0 | 101
38953.6124 | 1977 | 0 | 101
38953.6146 | 1478 | 0 | 101
38953.6167 | 2065 | 0 | 101
101
38953.5718 | 1 | 0 | 102
38953.5739 | 1 | 0 | 102
38953.5761 | 1 | 0 | 102
38953.5782 | 1 | 0 | 102
38953.5804 | 1 | 0 | 102
38953.5825 | 1 | 0 | 102
38953.5846 | 1 | 0 | 102
38953.5868 | 1 | 0 | 102
38953.5889 | 1 | 0 | 102
38953.5911 | 1 | 0 | 102
38953.5932 | 1 | 0 | 102
38953.5953 | 1 | 0 | 102
38953.5975 | 3 | 1 | 102
38953.5996 | 2005 | 0 | 102
38953.6017 | 2303 | 0 | 102
38953.6039 | 2224 | 0 | 102
38953.606 | 2504 | 0 | 102
38953.6082 | 2223 | 0 | 102
38953.6103 | 2320 | 0 | 102
38953.6124 | 2390 | 0 | 102
38953.6146 | 2548 | 0 | 102
38953.6167 | 2114 | 0 | 102
102
38953.5718 | 1 | 0 | 103
38953.574 | 1 | 0 | 103
38953.5761 | 1 | 0 | 103
38953.5782 | 1 | 0 | 103
38953.5804 | 1 | 0 | 103
38953.5825 | 1 | 0 | 103
38953.5847 | 1 | 0 | 103
38953.5868 | 1 | 0 | 103
38953.5889 | 58 | 53 | 103
38953.5911 | 1149 | 1190 | 103
38953.5932 | 938 | 973 | 103
38953.5953 | 1156 | 1131 | 103
38953.5975 | 971 | 941 | 103
38953.5996 | 2517 | 0 | 103
38953.6018 | 2140 | 0 | 103
38953.6039 | 2536 | 0 | 103
38953.606 | 2028 | 0 | 103
38953.6082 | 2443 | 0 | 103
38953.6103 | 1978 | 0 | 103
38953.6146 | 2322 | 0 | 103
38953.6167 | 2526 | 0 | 103
103
38953.5718 | 1 | 0 | 104
38953.574 | 1 | 0 | 104
38953.5761 | 1 | 0 | 104
38953.5783 | 1 | 0 | 104
38953.5804 | 1 | 0 | 104
38953.5825 | 1 | 0 | 104
38953.5847 | 1 | 0 | 104
38953.5868 | 1 | 0 | 104
38953.5889 | 399 | 434 | 104
38953.5911 | 919 | 960 | 104
38953.5932 | 1059 | 1033 | 104
38953.5954 | 1137 | 1110 | 104
38953.5975 | 927 | 943 | 104
38953.5996 | 2366 | 0 | 104
38953.6018 | 2005 | 0 | 104
38953.6039 | 2461 | 0 | 104
38953.6061 | 2546 | 0 | 104
38953.6082 | 2466 | 0 | 104
38953.6103 | 2487 | 0 | 104
38953.6125 | 2552 | 0 | 104
38953.6146 | 2158 | 0 | 104
38953.6167 | 2461 | 0 | 104
104
38953.5719 | 1 | 0 | 105
38953.574 | 1 | 0 | 105
38953.5761 | 1 | 0 | 105
38953.5783 | 1 | 0 | 105
38953.5804 | 1 | 0 | 105
38953.5825 | 1 | 0 | 105
38953.5847 | 1 | 0 | 105
38953.5868 | 1 | 0 | 105
38953.589 | 2 | 1 | 105
38953.5911 | 2 | 6 | 105
38953.5932 | 2 | 6 | 105
38953.5954 | 2 | 6 | 105
38953.5975 | 2 | 6 | 105
38953.5997 | 2019 | 0 | 105
38953.6018 | 2020 | 0 | 105
38953.6039 | 2058 | 0 | 105
38953.6061 | 2474 | 0 | 105
38953.6082 | 2535 | 0 | 105
38953.6103 | 2369 | 0 | 105
38953.6125 | 2556 | 0 | 105
38953.6146 | 2294 | 0 | 105
38953.6168 | 2423 | 0 | 105
105
38953.5719 | 1 | 0 | 106
38953.574 | 1 | 0 | 106
38953.5761 | 1 | 0 | 106
38953.5783 | 1 | 0 | 106
38953.5804 | 1 | 0 | 106
38953.5826 | 1 | 0 | 106
38953.5847 | 1 | 0 | 106
38953.5868 | 1 | 0 | 106
38953.589 | 1 | 0 | 106
38953.5911 | 2 | 3 | 106
38953.5933 | 2 | 3 | 106
38953.5954 | 2 | 3 | 106
38953.5975 | 2 | 3 | 106
38953.5997 | 2341 | 0 | 106
38953.6018 | 2122 | 0 | 106
38953.6039 | 2522 | 0 | 106
38953.6061 | 2223 | 0 | 106
38953.6082 | 2473 | 0 | 106
38953.6104 | 2308 | 0 | 106
38953.6125 | 1941 | 0 | 106
38953.6146 | 2014 | 0 | 106
38953.6168 | 2178 | 0 | 106
106
38953.5719 | 1 | 0 | 107
38953.574 | 1 | 0 | 107
38953.5762 | 1 | 0 | 107
38953.5783 | 1 | 0 | 107
38953.5804 | 1 | 0 | 107
38953.5826 | 1 | 0 | 107
38953.5847 | 1 | 0 | 107
38953.5869 | 1 | 0 | 107
38953.589 | 1 | 0 | 107
38953.5911 | 1 | 2 | 107
38953.5933 | 1 | 2 | 107
38953.5954 | 1 | 1 | 107
38953.5975 | 2 | 2 | 107
38953.5997 | 1986 | 0 | 107
38953.6018 | 2070 | 0 | 107
38953.604 | 2026 | 0 | 107
38953.6061 | 2532 | 0 | 107
38953.6082 | 2453 | 0 | 107
38953.6104 | 2350 | 0 | 107
38953.6125 | 2462 | 0 | 107
38953.6147 | 2009 | 0 | 107
38953.6168 | 2285 | 0 | 107
107
38953.5719 | 1 | 0 | 108
38953.574 | 1 | 0 | 108
38953.5762 | 1 | 0 | 108
38953.5783 | 1 | 0 | 108
38953.5805 | 1 | 0 | 108
38953.5826 | 1 | 0 | 108
38953.5847 | 1 | 0 | 108
38953.5869 | 1 | 0 | 108
38953.589 | 1 | 0 | 108
38953.5911 | 1 | 1 | 108
38953.5933 | 1 | 1 | 108
38953.5954 | 1 | 1 | 108
38953.5976 | 1 | 1 | 108
38953.5997 | 2490 | 0 | 108
38953.6018 | 2283 | 0 | 108
38953.604 | 2241 | 0 | 108
38953.6061 | 2534 | 0 | 108
38953.6083 | 2330 | 0 | 108
38953.6104 | 2546 | 0 | 108
38953.6125 | 1892 | 0 | 108
38953.6147 | 2385 | 0 | 108
38953.6168 | 2070 | 0 | 108
108
38953.5719 | 1 | 0 | 109
38953.5741 | 1 | 0 | 109
38953.5762 | 1 | 0 | 109
38953.5783 | 1 | 0 | 109
38953.5805 | 1 | 0 | 109
38953.5826 | 1 | 0 | 109
38953.5847 | 1 | 0 | 109
38953.5869 | 1 | 0 | 109
38953.589 | 1 | 0 | 109
38953.5912 | 1 | 1 | 109
38953.5933 | 2 | 1 | 109
38953.5954 | 1 | 1 | 109
38953.5976 | 2 | 1 | 109
38953.5997 | 1963 | 0 | 109
38953.6019 | 2260 | 0 | 109
38953.604 | 2120 | 0 | 109
38953.6061 | 2108 | 0 | 109
38953.6083 | 2379 | 0 | 109
38953.6104 | 2532 | 0 | 109
38953.6125 | 2195 | 0 | 109
38953.6147 | 2372 | 0 | 109
38953.6168 | 2409 | 0 | 109
109
38953.5719 | 1 | 0 | 110
38953.5741 | 1 | 0 | 110
38953.5762 | 1 | 0 | 110
38953.5783 | 1 | 0 | 110
38953.5805 | 1 | 0 | 110
38953.5826 | 1 | 0 | 110
38953.5848 | 1 | 0 | 110
38953.5869 | 1 | 0 | 110
38953.589 | 1 | 0 | 110
38953.5912 | 1 | 0 | 110
38953.5933 | 1 | 0 | 110
38953.5955 | 2 | 0 | 110
38953.5976 | 2 | 1 | 110
38953.5997 | 2068 | 0 | 110
38953.6019 | 2027 | 0 | 110
38953.604 | 2298 | 0 | 110
38953.6061 | 2491 | 0 | 110
38953.6083 | 1980 | 0 | 110
38953.6104 | 2257 | 0 | 110
38953.6126 | 2541 | 0 | 110
38953.6147 | 2237 | 0 | 110
38953.6168 | 2246 | 0 | 110
110
38953.5719 | 1 | 0 | 111
38953.5741 | 1 | 0 | 111
38953.5762 | 1 | 0 | 111
38953.5784 | 1 | 0 | 111
38953.5805 | 1 | 0 | 111
38953.5826 | 1 | 0 | 111
38953.5848 | 1 | 0 | 111
38953.5869 | 1 | 0 | 111
38953.5891 | 1 | 0 | 111
38953.5912 | 1 | 0 | 111
38953.5933 | 2 | 0 | 111
38953.5955 | 1 | 1 | 111
38953.5976 | 2 | 1 | 111
38953.5997 | 2329 | 0 | 111
38953.6019 | 2396 | 0 | 111
38953.604 | 2469 | 0 | 111
38953.6062 | 2478 | 0 | 111
38953.6083 | 2211 | 0 | 111
38953.6104 | 2554 | 0 | 111
38953.6126 | 2118 | 0 | 111
38953.6147 | 2219 | 0 | 111
38953.6169 | 2458 | 0 | 111
111
38953.572 | 1 | 0 | 112
38953.5741 | 1 | 0 | 112
38953.5762 | 1 | 0 | 112
38953.5784 | 1 | 0 | 112
38953.5805 | 1 | 0 | 112
38953.5827 | 1 | 0 | 112
38953.5848 | 1 | 0 | 112
38953.5869 | 1 | 0 | 112
38953.5891 | 1 | 0 | 112
38953.5912 | 1 | 0 | 112
38953.5933 | 1 | 0 | 112
38953.5955 | 1 | 0 | 112
38953.5976 | 1 | 0 | 112
38953.5998 | 2447 | 0 | 112
38953.6019 | 2493 | 0 | 112
38953.604 | 2289 | 0 | 112
38953.6062 | 2001 | 0 | 112
38953.6083 | 2375 | 0 | 112
38953.6105 | 1972 | 0 | 112
38953.6126 | 2100 | 0 | 112
38953.6147 | 2536 | 0 | 112
38953.6169 | 2388 | 0 | 112
112
38953.572 | 1 | 0 | 113
38953.5741 | 1 | 0 | 113
38953.5763 | 1 | 0 | 113
38953.5784 | 1 | 0 | 113
38953.5805 | 1 | 0 | 113
38953.5827 | 1 | 0 | 113
38953.5848 | 1 | 0 | 113
38953.5869 | 1 | 0 | 113
38953.5891 | 1 | 0 | 113
38953.5912 | 1 | 0 | 113
38953.5934 | 1 | 0 | 113
38953.5955 | 1 | 0 | 113
38953.5976 | 1 | 0 | 113
38953.5998 | 2392 | 0 | 113
38953.6019 | 2255 | 0 | 113
38953.6041 | 1956 | 0 | 113
38953.6062 | 2084 | 0 | 113
38953.6083 | 2138 | 0 | 113
38953.6105 | 1993 | 0 | 113
38953.6126 | 2292 | 0 | 113
38953.6148 | 2089 | 0 | 113
38953.6169 | 2458 | 0 | 113
113
38953.572 | 1 | 0 | 114
38953.5741 | 1 | 0 | 114
38953.5763 | 1 | 0 | 114
38953.5784 | 1 | 0 | 114
38953.5806 | 1 | 0 | 114
38953.5827 | 1 | 0 | 114
38953.5848 | 1 | 0 | 114
38953.587 | 1 | 0 | 114
38953.5891 | 1 | 0 | 114
38953.5912 | 1 | 0 | 114
38953.5934 | 1 | 0 | 114
38953.5955 | 1 | 0 | 114
38953.5977 | 1 | 0 | 114
38953.5998 | 2485 | 0 | 114
38953.6019 | 2148 | 0 | 114
38953.6041 | 2084 | 0 | 114
38953.6062 | 2314 | 0 | 114
38953.6084 | 2452 | 0 | 114
38953.6105 | 2163 | 0 | 114
38953.6126 | 2402 | 0 | 114
38953.6148 | 2021 | 0 | 114
38953.6169 | 2377 | 0 | 114
114
38953.572 | 1 | 0 | 115
38953.5742 | 1 | 0 | 115
38953.5763 | 1 | 0 | 115
38953.5784 | 1 | 0 | 115
38953.5806 | 1 | 0 | 115
38953.5827 | 1 | 0 | 115
38953.5848 | 1 | 0 | 115
38953.587 | 1 | 0 | 115
38953.5891 | 1 | 0 | 115
38953.5934 | 1 | 0 | 115
38953.5955 | 1 | 0 | 115
38953.5977 | 1 | 0 | 115
38953.5998 | 2365 | 0 | 115
38953.602 | 1991 | 0 | 115
38953.6041 | 2414 | 0 | 115
38953.6062 | 2060 | 0 | 115
38953.6084 | 2249 | 0 | 115
38953.6105 | 2338 | 0 | 115
38953.6127 | 2432 | 0 | 115
38953.6148 | 2330 | 0 | 115
38953.6169 | 2566 | 0 | 115
115
38953.572 | 1 | 0 | 116
38953.5742 | 1 | 0 | 116
38953.5763 | 1 | 0 | 116
38953.5784 | 1 | 0 | 116
38953.5806 | 1 | 0 | 116
38953.5827 | 1 | 0 | 116
38953.5849 | 1 | 0 | 116
38953.587 | 1 | 0 | 116
38953.5891 | 1 | 0 | 116
38953.5913 | 1 | 0 | 116
38953.5934 | 1 | 0 | 116
38953.5956 | 1 | 0 | 116
38953.5977 | 1 | 0 | 116
38953.5998 | 2370 | 0 | 116
38953.602 | 2043 | 0 | 116
38953.6041 | 2270 | 0 | 116
38953.6062 | 2421 | 0 | 116
38953.6084 | 2203 | 0 | 116
38953.6105 | 2484 | 0 | 116
38953.6127 | 2455 | 0 | 116
38953.6148 | 2488 | 0 | 116
38953.6169 | 2376 | 0 | 116
116
38953.572 | 1 | 0 | 117
38953.5742 | 1 | 0 | 117
38953.5763 | 1 | 0 | 117
38953.5785 | 1 | 0 | 117
38953.5806 | 1 | 0 | 117
38953.5827 | 1 | 0 | 117
38953.5849 | 1 | 0 | 117
38953.587 | 1 | 0 | 117
38953.5892 | 1 | 0 | 117
38953.5913 | 1 | 0 | 117
38953.5934 | 1 | 0 | 117
38953.5956 | 1 | 0 | 117
38953.5977 | 2 | 0 | 117
38953.5998 | 2284 | 0 | 117
38953.602 | 1969 | 0 | 117
38953.6041 | 2090 | 0 | 117
38953.6063 | 2504 | 0 | 117
38953.6084 | 2536 | 0 | 117
38953.6105 | 1980 | 0 | 117
38953.6127 | 1992 | 0 | 117
38953.6148 | 2249 | 0 | 117
117
38953.5721 | 1 | 0 | 118
38953.5742 | 1 | 0 | 118
38953.5763 | 1 | 0 | 118
38953.5785 | 1 | 0 | 118
38953.5806 | 1 | 0 | 118
38953.5828 | 2 | 0 | 118
38953.5849 | 1 | 0 | 118
38953.587 | 1 | 0 | 118
38953.5892 | 1 | 0 | 118
38953.5913 | 1 | 0 | 118
38953.5934 | 1 | 0 | 118
38953.5956 | 1 | 0 | 118
38953.5977 | 1 | 0 | 118
38953.5999 | 1960 | 0 | 118
38953.602 | 2366 | 0 | 118
38953.6041 | 2501 | 0 | 118
38953.6063 | 2203 | 0 | 118
38953.6084 | 2051 | 0 | 118
38953.6106 | 2281 | 0 | 118
38953.6127 | 2301 | 0 | 118
38953.6148 | 2160 | 0 | 118
38953.617 | 2442 | 0 | 118
118
38953.5721 | 1 | 0 | 119
38953.5742 | 1 | 0 | 119
38953.5764 | 1 | 0 | 119
38953.5785 | 1 | 0 | 119
38953.5806 | 1 | 0 | 119
38953.5828 | 1 | 0 | 119
38953.5849 | 1 | 0 | 119
38953.587 | 1 | 0 | 119
38953.5892 | 1 | 0 | 119
38953.5913 | 1 | 0 | 119
38953.5935 | 1 | 0 | 119
38953.5956 | 1 | 0 | 119
38953.5977 | 2 | 0 | 119
38953.5999 | 2108 | 0 | 119
38953.602 | 2231 | 0 | 119
38953.6042 | 2392 | 0 | 119
38953.6063 | 2544 | 0 | 119
38953.6084 | 1971 | 0 | 119
38953.6106 | 1990 | 0 | 119
38953.6127 | 2150 | 0 | 119
38953.6148 | 2477 | 0 | 119
38953.617 | 2378 | 0 | 119
119
38953.5721 | 1 | 0 | 120
38953.5742 | 1 | 0 | 120
38953.5764 | 1 | 0 | 120
38953.5785 | 1 | 0 | 120
38953.5806 | 1 | 0 | 120
38953.5828 | 1 | 0 | 120
38953.5849 | 1 | 0 | 120
38953.5871 | 1 | 0 | 120
38953.5892 | 1 | 0 | 120
38953.5913 | 1 | 0 | 120
38953.5935 | 1 | 0 | 120
38953.5956 | 1 | 0 | 120
38953.5978 | 1 | 0 | 120
38953.5999 | 2331 | 0 | 120
38953.602 | 2270 | 0 | 120
38953.6042 | 2529 | 0 | 120
38953.6063 | 2376 | 0 | 120
38953.6084 | 2177 | 0 | 120
38953.6106 | 2547 | 0 | 120
38953.6127 | 2295 | 0 | 120
38953.6149 | 2092 | 0 | 120
38953.617 | 2396 | 0 | 120
120
38953.5721 | 1 | 0 | 121
38953.5742 | 1 | 0 | 121
38953.5764 | 1 | 0 | 121
38953.5785 | 1 | 0 | 121
38953.5807 | 1 | 0 | 121
38953.5828 | 1 | 0 | 121
38953.5849 | 1 | 0 | 121
38953.5871 | 1 | 0 | 121
38953.5892 | 1 | 0 | 121
38953.5914 | 1 | 0 | 121
38953.5935 | 2 | 1 | 121
38953.5956 | 1194 | 1182 | 121
38953.5978 | 1031 | 1071 | 121
38953.5999 | 1983 | 0 | 121
38953.602 | 2414 | 0 | 121
38953.6042 | 2097 | 0 | 121
38953.6063 | 2478 | 0 | 121
38953.6085 | 1977 | 0 | 121
38953.6106 | 2259 | 2 | 121
38953.6127 | 2444 | 9 | 121
38953.6149 | 1938 | 1 | 121
38953.617 | 2064 | 300 | 121
121
38953.5721 | 3 | 0 | 122
38953.5743 | 1 | 0 | 122
38953.5764 | 1 | 0 | 122
38953.5785 | 1 | 0 | 122
38953.5807 | 1 | 0 | 122
38953.5828 | 1 | 0 | 122
38953.585 | 1 | 0 | 122
38953.5871 | 1 | 0 | 122
38953.5892 | 1 | 0 | 122
38953.5914 | 1 | 0 | 122
38953.5935 | 2 | 1 | 122
38953.5956 | 1184 | 908 | 122
38953.5978 | 1159 | 1131 | 122
38953.5999 | 2124 | 0 | 122
38953.6021 | 2173 | 0 | 122
38953.6042 | 2298 | 0 | 122
38953.6063 | 2113 | 0 | 122
38953.6085 | 2167 | 0 | 122
38953.6106 | 2175 | 1 | 122
38953.6128 | 1902 | 20 | 122
38953.6149 | 2099 | 1 | 122
38953.617 | 1798 | 101 | 122
122
38953.5721 | 1 | 0 | 123
38953.5743 | 1 | 0 | 123
38953.5764 | 1 | 0 | 123
38953.5786 | 1 | 0 | 123
38953.5807 | 1 | 0 | 123
38953.5828 | 1 | 0 | 123
38953.585 | 1 | 0 | 123
38953.5871 | 1 | 0 | 123
38953.5892 | 1 | 0 | 123
38953.5914 | 1 | 0 | 123
38953.5935 | 1 | 0 | 123
38953.5957 | 2 | 6 | 123
38953.5978 | 2 | 6 | 123
38953.5999 | 2105 | 0 | 123
38953.6021 | 2180 | 0 | 123
38953.6042 | 2486 | 0 | 123
38953.6064 | 2534 | 0 | 123
38953.6085 | 1982 | 0 | 123
38953.6106 | 2021 | 0 | 123
38953.6128 | 2094 | 0 | 123
38953.6149 | 2341 | 0 | 123
38953.617 | 2307 | 0 | 123
123
38953.5722 | 1 | 0 | 124
38953.5743 | 1 | 0 | 124
38953.5764 | 1 | 0 | 124
38953.5786 | 1 | 0 | 124
38953.5807 | 1 | 0 | 124
38953.5828 | 1 | 0 | 124
38953.585 | 1 | 0 | 124
38953.5871 | 1 | 0 | 124
38953.5893 | 1 | 0 | 124
38953.5914 | 1 | 0 | 124
38953.5935 | 1 | 0 | 124
38953.5957 | 2 | 3 | 124
38953.5978 | 2 | 3 | 124
38953.6 | 2249 | 0 | 124
38953.6021 | 2293 | 0 | 124
38953.6042 | 1988 | 0 | 124
38953.6064 | 2140 | 0 | 124
38953.6085 | 2328 | 0 | 124
38953.6106 | 2520 | 0 | 124
38953.6128 | 2326 | 0 | 124
38953.6149 | 2385 | 0 | 124
38953.6171 | 2538 | 0 | 124
124
38953.5722 | 1 | 0 | 125
38953.5743 | 1 | 0 | 125
38953.5764 | 1 | 0 | 125
38953.5786 | 1 | 0 | 125
38953.5807 | 1 | 0 | 125
38953.5829 | 1 | 0 | 125
38953.585 | 1 | 0 | 125
38953.5871 | 1 | 0 | 125
38953.5893 | 1 | 0 | 125
38953.5914 | 1 | 0 | 125
38953.5936 | 1 | 0 | 125
38953.5957 | 2 | 2 | 125
38953.5978 | 1 | 2 | 125
38953.6 | 2052 | 0 | 125
38953.6021 | 1957 | 0 | 125
38953.6042 | 2486 | 0 | 125
38953.6064 | 2187 | 0 | 125
38953.6085 | 2505 | 0 | 125
38953.6107 | 2075 | 0 | 125
38953.6128 | 1827 | 0 | 125
38953.6149 | 2045 | 0 | 125
38953.6171 | 1873 | 0 | 125
125
38953.5722 | 1 | 0 | 126
38953.5743 | 1 | 0 | 126
38953.5765 | 1 | 0 | 126
38953.5786 | 1 | 0 | 126
38953.5807 | 1 | 0 | 126
38953.5829 | 1 | 0 | 126
38953.585 | 1 | 0 | 126
38953.5872 | 1 | 0 | 126
38953.5893 | 1 | 0 | 126
38953.5914 | 1 | 0 | 126
38953.5936 | 1 | 0 | 126
38953.5957 | 1 | 1 | 126
38953.5979 | 1 | 1 | 126
38953.6 | 2363 | 0 | 126
38953.6021 | 2463 | 0 | 126
38953.6043 | 2060 | 0 | 126
38953.6064 | 2058 | 0 | 126
38953.6085 | 2531 | 0 | 126
38953.6107 | 2242 | 0 | 126
38953.6128 | 2498 | 0 | 126
38953.615 | 1999 | 0 | 126
38953.6171 | 2258 | 0 | 126
126
38953.5722 | 1 | 0 | 127
38953.5743 | 1 | 0 | 127
38953.5765 | 1 | 0 | 127
38953.5786 | 1 | 0 | 127
38953.5808 | 1 | 0 | 127
38953.5829 | 1 | 0 | 127
38953.585 | 1 | 0 | 127
38953.5872 | 1 | 0 | 127
38953.5893 | 1 | 0 | 127
38953.5915 | 1 | 0 | 127
38953.5936 | 1 | 0 | 127
38953.5957 | 1 | 1 | 127
38953.5979 | 2 | 1 | 127
38953.6 | 2492 | 0 | 127
38953.6021 | 1982 | 0 | 127
38953.6043 | 2281 | 0 | 127
38953.6064 | 2339 | 0 | 127
38953.6086 | 2320 | 0 | 127
38953.6107 | 2481 | 0 | 127
38953.6128 | 1828 | 0 | 127
38953.615 | 1946 | 0 | 127
38953.6171 | 1933 | 0 | 127
127
38953.5722 | 1 | 0 | 128
38953.5744 | 1 | 0 | 128
38953.5765 | 1 | 0 | 128
38953.5786 | 1 | 0 | 128
38953.5808 | 1 | 0 | 128
38953.5829 | 1 | 0 | 128
38953.5851 | 1 | 0 | 128
38953.5872 | 1 | 0 | 128
38953.5893 | 1 | 0 | 128
38953.5915 | 1 | 0 | 128
38953.5936 | 1 | 0 | 128
38953.5958 | 1 | 1 | 128
38953.5979 | 1 | 1 | 128
38953.6 | 2430 | 0 | 128
38953.6022 | 2207 | 0 | 128
38953.6043 | 2224 | 0 | 128
38953.6064 | 2503 | 0 | 128
38953.6086 | 2365 | 0 | 128
38953.6107 | 2539 | 0 | 128
38953.6129 | 2060 | 0 | 128
38953.615 | 2300 | 0 | 128
38953.6171 | 2204 | 0 | 128
128
38953.5722 | 1 | 0 | 129
38953.5744 | 1 | 0 | 129
38953.5765 | 1 | 0 | 129
38953.5787 | 1 | 0 | 129
38953.5808 | 1 | 0 | 129
38953.5829 | 1 | 0 | 129
38953.5851 | 1 | 0 | 129
38953.5872 | 1 | 0 | 129
38953.5894 | 1 | 0 | 129
38953.5915 | 1 | 0 | 129
38953.5936 | 1 | 0 | 129
38953.5958 | 1 | 0 | 129
38953.5979 | 1 | 0 | 129
38953.6 | 2346 | 0 | 129
38953.6022 | 2066 | 0 | 129
38953.6043 | 2235 | 0 | 129
38953.6065 | 2071 | 0 | 129
38953.6086 | 2529 | 0 | 129
38953.6107 | 2510 | 0 | 129
38953.6129 | 1639 | 0 | 129
38953.615 | 2473 | 0 | 129
38953.6172 | 1937 | 0 | 129
129
38953.5723 | 1 | 0 | 130
38953.5744 | 1 | 0 | 130
38953.5765 | 1 | 0 | 130
38953.5787 | 1 | 0 | 130
38953.5808 | 1 | 0 | 130
38953.583 | 1 | 0 | 130
38953.5851 | 1 | 0 | 130
38953.5872 | 1 | 0 | 130
38953.5894 | 1 | 0 | 130
38953.5915 | 1 | 0 | 130
38953.5936 | 1 | 0 | 130
38953.5958 | 1 | 0 | 130
38953.5979 | 1 | 1 | 130
38953.6001 | 2093 | 0 | 130
38953.6022 | 2142 | 0 | 130
38953.6043 | 2530 | 0 | 130
38953.6065 | 2253 | 0 | 130
38953.6086 | 2427 | 0 | 130
38953.6108 | 2548 | 0 | 130
38953.6129 | 2115 | 0 | 130
38953.615 | 2221 | 0 | 130
38953.6172 | 2361 | 0 | 130
130
38953.5723 | 1 | 0 | 131
38953.5744 | 1 | 0 | 131
38953.5766 | 1 | 0 | 131
38953.5787 | 1 | 0 | 131
38953.5808 | 1 | 0 | 131
38953.583 | 1 | 0 | 131
38953.5851 | 1 | 0 | 131
38953.5872 | 1 | 0 | 131
38953.5894 | 2 | 0 | 131
38953.5915 | 4 | 1 | 131
38953.5937 | 1114 | 1144 | 131
38953.5958 | 937 | 1043 | 131
38953.5979 | 1016 | 983 | 131
38953.6001 | 2014 | 0 | 131
38953.6022 | 2482 | 0 | 131
38953.6044 | 2529 | 0 | 131
38953.6065 | 2030 | 0 | 131
38953.6086 | 2409 | 0 | 131
38953.6108 | 2538 | 0 | 131
38953.6129 | 2282 | 0 | 131
38953.615 | 2196 | 0 | 131
38953.6172 | 2265 | 0 | 131
131
38953.5723 | 1 | 0 | 132
38953.5744 | 1 | 0 | 132
38953.5766 | 1 | 0 | 132
38953.5787 | 1 | 0 | 132
38953.583 | 1 | 0 | 132
38953.5851 | 1 | 0 | 132
38953.5873 | 1 | 0 | 132
38953.5894 | 1 | 0 | 132
38953.5915 | 7 | 4 | 132
38953.5937 | 1046 | 1096 | 132
38953.5958 | 937 | 910 | 132
38953.598 | 980 | 950 | 132
38953.6001 | 2206 | 0 | 132
38953.6022 | 2066 | 0 | 132
38953.6044 | 2147 | 0 | 132
38953.6065 | 2288 | 0 | 132
38953.6086 | 2361 | 0 | 132
38953.6108 | 2360 | 0 | 132
38953.6129 | 2537 | 0 | 132
38953.6151 | 1981 | 0 | 132
38953.6172 | 2155 | 0 | 132
132

## C6-F12
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.5556 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38953.5718 | 1 | 0 | 38953.5718 | 1 | 0 |  | -34 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5739 | 1 | 0 | 38953.5739 | 1 | 0 |  | 150.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5761 | 1 | 0 | 38953.5761 | 1 | 0 |  | 335.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5782 | 1 | 0 | 38953.5782 | 1 | 0 |  | 520.5 | 695.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5803 | 1 | 1 | 38953.5804 | 1 | 0 |  | 705 | 880 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 657091702.44 | 256338 | 256138.078
38953.5825 | 1 | 0 | 38953.5825 | 1 | 0 |  | 889.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5846 | 1 | 0 | 38953.5846 | 1 | 0 |  | 1074.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5868 | 1 | 0 | 38953.5868 | 1 | 0 |  | 1259.5 | 1434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5889 | 1 | 0 | 38953.5889 | 1 | 0 |  | 1444 | 1619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.591 | 1 | 0 | 38953.5911 | 1 | 0 |  | 1629 | 1804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5932 | 1 | 0 | 38953.5932 | 1 | 0 |  | 1813.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5953 | 1 | 0 | 38953.5953 | 1 | 0 |  | 1998.5 | 2173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38953.5975 | 4 | 1 | 38953.5975 | 3 | 1 |  | 2183.5 | 2358.5 | 0.2442 | 0.06105 | 0.18315 | 0.06105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.001221 | 85368.2063 | 128144.0537 | 255738.429
38953.5996 | 579 | 0 | 38953.5996 | 2005 | 0 |  | 2368 | 2543 | 35.348 | 0 | 122.4054 | 0 | 0.35348 | 0 | 1.2241 | 0 | 0.35348 | 1.2241 | 342.8981 | 27.8993 | 342.5446
38953.6017 | 1047 | 0 | 38953.6017 | 2303 | 0 |  | 2552.5 | 2727.5 | 63.9194 | 0 | 140.5983 | 0 | 0.63919 | 0 | 1.406 | 0 | 0.63919 | 1.406 | 144.9265 | 11.3495 | 144.2873
38953.6039 | 1821 | 0 | 38953.6039 | 2224 | 0 |  | 2737.5 | 2912.5 | 111.1722 | 0 | 135.7753 | 0 | 1.1117 | 0 | 1.3578 | 0 | 1.1117 | 1.3578 | 40.8226 | 15.3049 | 39.7109
38953.606 | 1625 | 0 | 38953.606 | 2504 | 0 |  | 2922.5 | 3097.5 | 99.2063 | 0 | 152.8694 | 0 | 0.99206 | 0 | 1.5287 | 0 | 0.99206 | 1.5287 | 57.808 | 2.4113 | 56.8159
38953.6081 | 1986 | 0 | 38953.6082 | 2223 | 0 |  | 3107 | 3282 | 121.2454 | 0 | 135.7143 | 0 | 1.2125 | 0 | 1.3571 | 0 | 1.2125 | 1.3571 | 29.1229 | 15.3567 | 27.9104
38953.6103 | 2159 | 0 | 38953.6103 | 2320 | 0 |  | 3292 | 3467 | 131.8071 | 0 | 141.6361 | 0 | 1.3181 | 0 | 1.4164 | 0 | 1.3181 | 1.4164 | 18.7763 | 10.5336 | 17.4582
38953.6124 | 1977 | 0 | 38953.6124 | 2390 | 0 |  | 3476.5 | 3651.5 | 120.696 | 0 | 145.9096 | 0 | 1.207 | 0 | 1.4591 | 0 | 1.207 | 1.4591 | 29.7107 | 7.2962 | 28.5037
38953.6146 | 1478 | 0 | 38953.6146 | 2548 | 0 |  | 3661.5 | 3836.5 | 90.232 | 0 | 155.5556 | 0 | 0.90232 | 0 | 1.5556 | 0 | 0.90232 | 1.5556 | 73.5034 | 0.64286 | 72.6011
38953.6167 | 2065 | 0 | 38953.6167 | 2114 | 0 |  | 3846.5 | 4021.5 | 126.0684 | 0 | 129.0598 | 0 | 1.2607 | 0 | 1.2906 | 0 | 1.2607 | 1.2906 | 24.1831 | 21.3046 | 22.9224

## C6-F11
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 154.7851 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38953.5717 | 1 | 0 | 38953.5718 | 1 | 0 |  | -37 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5739 | 1 | 0 | 38953.5739 | 1 | 0 |  | 148 | 323 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.576 | 1 | 0 | 38953.576 | 1 | 0 |  | 332.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5782 | 1 | 0 | 38953.5782 | 1 | 0 |  | 517.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5803 | 1 | 0 | 38953.5803 | 1 | 0 |  | 702.5 | 877.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5824 | 1 | 0 | 38953.5825 | 1 | 0 |  | 887 | 1062 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5846 | 1 | 0 | 38953.5846 | 1 | 0 |  | 1071.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5867 | 1 | 0 | 38953.5867 | 1 | 0 |  | 1256.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5889 | 1 | 0 | 38953.5889 | 1 | 0 |  | 1441.5 | 1616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.591 | 1 | 0 | 38953.591 | 1 | 0 |  | 1626 | 1801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5931 | 1 | 0 | 38953.5932 | 1 | 0 |  | 1811 | 1986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5953 | 1 | 0 | 38953.5953 | 1 | 0 |  | 1995.5 | 2170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
38953.5974 | 4 | 1 | 38953.5974 | 3 | 1 |  | 2180.5 | 2355.5 | 0.2442 | 0.06105 | 0.18315 | 0.06105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.001221 | 84401.5395 | 126694.0544 | 252838.4339
38953.5996 | 554 | 0 | 38953.5996 | 2362 | 0 |  | 2365.5 | 2540.5 | 33.8217 | 0 | 144.2002 | 0 | 0.33822 | 0 | 1.442 | 0 | 0.33822 | 1.442 | 357.6498 | 7.3404 | 357.3116
38953.6017 | 954 | 0 | 38953.6017 | 1988 | 0 |  | 2550 | 2725 | 58.2418 | 0 | 121.3675 | 0 | 0.58242 | 0 | 1.2137 | 0 | 0.58242 | 1.2137 | 165.7631 | 27.5342 | 165.1807
38953.6038 | 1740 | 0 | 38953.6038 | 1953 | 0 |  | 2734.5 | 2909.5 | 106.2271 | 0 | 119.2308 | 0 | 1.0623 | 0 | 1.1923 | 0 | 1.0623 | 1.1923 | 45.7115 | 29.8198 | 44.6492
38953.606 | 1825 | 0 | 38953.606 | 2519 | 0 |  | 2919.5 | 3094.5 | 111.4164 | 0 | 153.7851 | 0 | 1.1142 | 0 | 1.5379 | 0 | 1.1142 | 1.5379 | 38.9249 | 0.65026 | 37.8108
38953.6081 | 1973 | 0 | 38953.6081 | 2195 | 0 |  | 3104.5 | 3279.5 | 120.4518 | 0 | 134.0049 | 0 | 1.2045 | 0 | 1.34 | 0 | 1.2045 | 1.34 | 28.5038 | 15.5071 | 27.2993
38953.6102 | 1881 | 0 | 38953.6103 | 2352 | 0 |  | 3289 | 3464 | 114.8352 | 0 | 143.5897 | 0 | 1.1484 | 0 | 1.4359 | 0 | 1.1484 | 1.4359 | 34.7889 | 7.7968 | 33.6406
38953.6124 | 1900 | 0 | 38953.6124 | 2241 | 0 |  | 3474 | 3649 | 115.9951 | 0 | 136.8132 | 0 | 1.16 | 0 | 1.3681 | 0 | 1.16 | 1.3681 | 33.4411 | 13.1361 | 32.2811
38953.6145 | 1793 | 0 | 38953.6145 | 2329 | 0 |  | 3658.5 | 3833.5 | 109.4628 | 0 | 142.1856 | 0 | 1.0946 | 0 | 1.4219 | 0 | 1.0946 | 1.4219 | 41.4044 | 8.8613 | 40.3097
38953.6167 | 2044 | 0 | 38953.6167 | 2470 | 0 |  | 3843.5 | 4018.5 | 124.7863 | 0 | 150.7937 | 0 | 1.2479 | 0 | 1.5079 | 0 | 1.2479 | 1.5079 | 24.0401 | 2.647 | 22.7923

## C6-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 145.6276 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38953.5717 | 1 | 0 | 38953.5717 | 1 | 0 |  | -39.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5739 | 1 | 0 | 38953.5739 | 1 | 0 |  | 145 | 320 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.576 | 1 | 0 | 38953.576 | 1 | 0 |  | 330 | 505 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5781 | 1 | 0 | 38953.5781 | 1 | 0 |  | 514.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5803 | 1 | 0 | 38953.5803 | 1 | 0 |  | 699.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5824 | 1 | 0 | 38953.5824 | 1 | 0 |  | 884 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5845 | 1 | 0 | 38953.5846 | 1 | 0 |  | 1069 | 1244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5867 | 1 | 0 | 38953.5867 | 1 | 0 |  | 1253.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5888 | 1 | 0 | 38953.5888 | 1 | 0 |  | 1438.5 | 1613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.591 | 1 | 0 | 38953.591 | 1 | 0 |  | 1623.5 | 1798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5931 | 1 | 0 | 38953.5931 | 1 | 0 |  | 1808 | 1983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5952 | 1 | 0 | 38953.5953 | 1 | 0 |  | 1993 | 2168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5974 | 1 | 0 | 38953.5974 | 1 | 0 |  | 2177.5 | 2352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238438 | 238438 | 238437.9994
38953.5995 | 547 | 0 | 38953.5995 | 2147 | 0 |  | 2362.5 | 2537.5 | 33.3944 | 0 | 131.0745 | 0 | 0.33394 | 0 | 1.3107 | 0 | 0.33394 | 1.3107 | 336.0841 | 11.1029 | 335.7502
38953.6017 | 1035 | 0 |  | 2258 | 0 |  | 2546 | 2721 | 63.1868 | 0 | 137.851 | 0 | 0.63187 | 0 | 1.3785 | 0 | 0.63187 | 1.3785 | 130.4715 | 5.6413 | 129.8396
38953.6038 | 1518 | 0 | 38953.6038 | 2369 | 0 |  | 2732 | 2907 | 92.674 | 0 | 144.6276 | 0 | 0.92674 | 0 | 1.4463 | 0 | 0.92674 | 1.4463 | 57.1397 | 0.69143 | 56.2129
38953.6059 | 1907 | 0 | 38953.6059 | 2129 | 0 |  | 2916.5 | 3091.5 | 116.4225 | 0 | 129.9756 | 0 | 1.1642 | 0 | 1.2998 | 0 | 1.1642 | 1.2998 | 25.0855 | 12.0423 | 23.9212
38953.6081 | 2168 | 0 | 38953.6081 | 2170 | 0 |  | 3101.5 | 3276.5 | 132.3565 | 0 | 132.4786 | 0 | 1.3236 | 0 | 1.3248 | 0 | 1.3236 | 1.3248 | 10.0268 | 9.9253 | 8.7032
38953.6102 | 2074 | 0 | 38953.6102 | 2169 | 0 |  | 3286.5 | 3461.5 | 126.6178 | 0 | 132.4176 | 0 | 1.2662 | 0 | 1.3242 | 0 | 1.2662 | 1.3242 | 15.0135 | 9.976 | 13.7473
38953.6123 | 2016 | 0 | 38953.6124 | 2330 | 0 |  | 3471 | 3646 | 123.0769 | 0 | 142.2466 | 0 | 1.2308 | 0 | 1.4225 | 0 | 1.2308 | 1.4225 | 18.3224 | 2.3768 | 17.0917
38953.6145 | 1901 | 0 | 38953.6145 | 2300 | 1 |  | 3655.5 | 3830.5 | 116.0562 | 0 | 140.4151 | 0.06105 | 1.1606 | 0 | 1.4042 | 0.0006105 | 1.1606 | 1.4035 | 25.4803 | 3.7573 | 24.3197
38953.6166 | 1905 | 0 | 38953.6166 | 2197 | 0 |  | 3840.5 | 4015.5 | 116.3004 | 0 | 134.127 | 0 | 1.163 | 0 | 1.3413 | 0 | 1.163 | 1.3413 | 25.2168 | 8.5744 | 24.0538

## C6-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 152.8315 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38953.5717 | 1 | 0 | 38953.5717 | 1 | 0 |  | -42.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5738 | 1 | 0 | 38953.5738 | 1 | 0 |  | 142.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.576 | 1 | 0 | 38953.576 | 1 | 0 |  | 327 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5781 | 1 | 0 | 38953.5781 | 1 | 0 |  | 512 | 687 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5802 | 1 | 0 | 38953.5803 | 1 | 0 |  | 696.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5824 | 1 | 0 | 38953.5824 | 1 | 0 |  | 881.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5845 | 1 | 0 | 38953.5845 | 1 | 0 |  | 1066 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5867 | 1 | 0 | 38953.5867 | 1 | 0 |  | 1251 | 1426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5888 | 1 | 0 | 38953.5888 | 1 | 0 |  | 1435.5 | 1610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5909 | 1 | 0 | 38953.5909 | 1 | 0 |  | 1620.5 | 1795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5931 | 1 | 0 | 38953.5931 | 1 | 0 |  | 1805.5 | 1980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5952 | 1 | 0 | 38953.5952 | 1 | 0 |  | 1990 | 2165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38953.5973 | 1 | 0 | 38953.5974 | 2 | 0 |  | 2175 | 2350 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250238 | 125069 | 250237.9994
38953.5995 | 603 | 0 | 38953.5995 | 2477 | 0 |  | 2359.5 | 2534.5 | 36.8132 | 0 | 151.221 | 0 | 0.36813 | 0 | 1.5122 | 0 | 0.36813 | 1.5122 | 315.1542 | 1.065 | 314.7861
38953.6016 | 1077 | 0 | 38953.6016 | 2446 | 0 |  | 2544.5 | 2719.5 | 65.7509 | 0 | 149.3284 | 0 | 0.65751 | 0 | 1.4933 | 0 | 0.65751 | 1.4933 | 132.4401 | 2.3459 | 131.7826
38953.6038 | 1780 | 0 | 38953.6038 | 2274 | 0 |  | 2729 | 2904 | 108.6691 | 0 | 138.8278 | 0 | 1.0867 | 0 | 1.3883 | 0 | 1.0867 | 1.3883 | 40.6393 | 10.0871 | 39.5526
38953.6059 | 1619 | 0 | 38953.6059 | 2487 | 0 |  | 2914 | 3089 | 98.84 | 0 | 151.8315 | 0 | 0.9884 | 0 | 1.5183 | 0 | 0.9884 | 1.5183 | 54.6251 | 0.65862 | 53.6367
38953.608 | 1872 | 0 | 38953.6081 | 2017 | 0 |  | 3098.5 | 3273.5 | 114.2857 | 0 | 123.138 | 0 | 1.1429 | 0 | 1.2314 | 0 | 1.1429 | 1.2314 | 33.7276 | 24.114 | 32.5847
38953.6102 | 2100 | 0 | 38953.6102 | 2161 | 0 |  | 3283.5 | 3458.5 | 128.2051 | 0 | 131.9292 | 0 | 1.2821 | 0 | 1.3193 | 0 | 1.2821 | 1.3193 | 19.2086 | 15.8436 | 17.9265
38953.6123 | 2029 | 0 | 38953.6123 | 2216 | 0 |  | 3468.5 | 3643.5 | 123.8706 | 0 | 135.2869 | 0 | 1.2387 | 0 | 1.3529 | 0 | 1.2387 | 1.3529 | 23.38 | 12.9684 | 22.1413
38953.6145 | 1801 | 0 | 38953.6145 | 2025 | 0 |  | 3653 | 3828 | 109.9512 | 0 | 123.6264 | 0 | 1.0995 | 0 | 1.2363 | 0 | 1.0995 | 1.2363 | 38.9994 | 23.6237 | 37.8999
38953.6166 | 1801 | 0 | 38953.6166 | 2316 | 0 |  | 3837.5 | 4012.5 | 109.9512 | 0 | 141.3919 | 0 | 1.0995 | 0 | 1.4139 | 0 | 1.0995 | 1.4139 | 38.9994 | 8.0907 | 37.8999

## C5-F12
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 153.5641 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38953.5716 | 1 | 0 | 38953.5716 | 1 | 0 |  | -50.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5737 | 1 | 0 | 38953.5738 | 1 | 0 |  | 134 | 309 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5759 | 1 | 0 | 38953.5759 | 1 | 0 |  | 318.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.578 | 1 | 0 | 38953.578 | 1 | 0 |  | 503.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5802 | 1 | 0 | 38953.5802 | 1 | 0 |  | 688.5 | 863.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5823 | 1 | 0 | 38953.5823 | 1 | 0 |  | 873 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5844 | 1 | 0 | 38953.5844 | 1 | 0 |  | 1057.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5866 | 1 | 0 | 38953.5866 | 1 | 0 |  | 1242.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5887 | 1 | 0 | 38953.5887 | 1 | 0 |  | 1427.5 | 1602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5908 | 1 | 0 | 38953.5909 | 1 | 0 |  | 1612 | 1787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.593 | 1 | 0 | 38953.593 | 1 | 0 |  | 1797 | 1972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5951 | 1 | 0 | 38953.5951 | 1 | 0 |  | 1981.5 | 2156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251438 | 251438 | 251437.9994
38953.5973 | 3 | 1 | 38953.5973 | 2 | 1 |  | 2166.5 | 2341.5 | 0.18315 | 0.06105 | 0.1221 | 0.06105 | 0.0018315 | 0.0006105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 125643.9751 | 251538.1992 | 251038.1988
38953.5994 | 588 | 0 | 38953.5994 | 2184 | 0 |  | 2351.5 | 2526.5 | 35.8974 | 0 | 133.3333 | 0 | 0.35897 | 0 | 1.3333 | 0 | 0.35897 | 1.3333 | 327.7857 | 15.1731 | 327.4267
38953.6015 | 1050 | 0 | 38953.6016 | 2009 | 0 |  | 2536 | 2711 | 64.1026 | 0 | 122.6496 | 0 | 0.64103 | 0 | 1.2265 | 0 | 0.64103 | 1.2265 | 139.56 | 25.2056 | 138.919
38953.6037 | 1369 | 0 | 38953.6037 | 2401 | 0 |  | 2720.5 | 2895.5 | 83.5775 | 0 | 146.5812 | 0 | 0.83578 | 0 | 1.4658 | 0 | 0.83578 | 1.4658 | 83.7385 | 4.7638 | 82.9027
38953.6058 | 1563 | 0 | 38953.6058 | 2499 | 0 |  | 2905.5 | 3080.5 | 95.4212 | 0 | 152.5641 | 0 | 0.95421 | 0 | 1.5256 | 0 | 0.95421 | 1.5256 | 60.9328 | 0.65546 | 59.9786
38953.608 | 1917 | 0 | 38953.608 | 2471 | 0 |  | 3090.5 | 3265.5 | 117.033 | 0 | 150.8547 | 0 | 1.1703 | 0 | 1.5085 | 0 | 1.1703 | 1.5085 | 31.2144 | 1.796 | 30.0441
38953.6101 | 1852 | 0 | 38953.6101 | 2286 | 0 |  | 3275 | 3450 | 113.0647 | 0 | 139.5604 | 0 | 1.1306 | 0 | 1.3956 | 0 | 1.1306 | 1.3956 | 35.8197 | 10.0341 | 34.689
38953.6122 | 1651 | 0 | 38953.6122 | 2185 | 0 |  | 3460 | 3635 | 100.7937 | 0 | 133.3944 | 0 | 1.0079 | 0 | 1.3339 | 0 | 1.0079 | 1.3339 | 52.3549 | 15.1204 | 51.347
38953.6144 | 1911 | 0 | 38953.6144 | 2343 | 0 |  | 3644.5 | 3819.5 | 116.6667 | 0 | 143.0403 | 0 | 1.1667 | 0 | 1.4304 | 0 | 1.1667 | 1.4304 | 31.6264 | 7.3572 | 30.4597
38953.6165 | 1936 | 0 | 38953.6165 | 2490 | 0 |  | 3829.5 | 4004.5 | 118.1929 | 0 | 152.0147 | 0 | 1.1819 | 0 | 1.5201 | 0 | 1.1819 | 1.5201 | 29.9267 | 1.0193 | 28.7447

## C5-F11
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.4335 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38953.5716 | 1 | 0 | 38953.5716 | 1 | 0 |  | -53.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5737 | 1 | 0 | 38953.5737 | 1 | 0 |  | 131 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5758 | 1 | 0 | 38953.5759 | 1 | 0 |  | 316 | 491 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.578 | 1 | 0 | 38953.578 | 1 | 0 |  | 500.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5801 | 1 | 0 | 38953.5801 | 1 | 0 |  | 685.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5823 | 1 | 0 | 38953.5823 | 1 | 0 |  | 870.5 | 1045.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5844 | 1 | 0 | 38953.5844 | 1 | 0 |  | 1055 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5865 | 1 | 0 | 38953.5865 | 1 | 0 |  | 1239.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5887 | 1 | 0 | 38953.5887 | 1 | 0 |  | 1424.5 | 1599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5908 | 1 | 0 | 38953.5908 | 1 | 0 |  | 1609.5 | 1784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5929 | 1 | 0 | 38953.593 | 1 | 0 |  | 1794 | 1969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5951 | 1 | 0 | 38953.5951 | 1 | 0 |  | 1979 | 2154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5972 | 3 | 1 | 38953.5972 | 2 | 0 |  | 2163.5 | 2338.5 | 0.18315 | 0.06105 | 0.1221 | 0 | 0.0018315 | 0.0006105 | 0.001221 | 0 | 0.001221 | 0.001221 | 128019 | 128019 | 255638.3122
38953.5994 | 484 | 0 | 38953.5994 | 2476 | 0 |  | 2348.5 | 2523.5 | 29.5482 | 0 | 151.16 | 0 | 0.29548 | 0 | 1.5116 | 0 | 0.29548 | 1.5116 | 429.4174 | 3.4887 | 429.1219
38953.6015 | 1067 | 0 | 38953.6015 | 2454 | 0 |  | 2533 | 2708 | 65.1404 | 0 | 149.8168 | 0 | 0.6514 | 0 | 1.4982 | 0 | 0.6514 | 1.4982 | 140.1481 | 4.4165 | 139.4967
38953.6036 | 1504 | 0 | 38953.6037 | 2482 | 0 |  | 2718 | 2893 | 91.8193 | 0 | 151.5263 | 0 | 0.91819 | 0 | 1.5153 | 0 | 0.91819 | 1.5153 | 70.371 | 3.2385 | 69.4528
38953.6058 | 1813 | 0 | 38953.6058 | 2364 | 0 |  | 2902.5 | 3077.5 | 110.6838 | 0 | 144.3223 | 0 | 1.1068 | 0 | 1.4432 | 0 | 1.1068 | 1.4432 | 41.3337 | 8.3917 | 40.2269
38953.6079 | 2147 | 0 | 38953.6079 | 2165 | 0 |  | 3087.5 | 3262.5 | 131.0745 | 0 | 132.1734 | 0 | 1.3107 | 0 | 1.3217 | 0 | 1.3107 | 1.3217 | 19.347 | 18.3547 | 18.0363
38953.6101 | 2139 | 0 | 38953.6101 | 2306 | 0 |  | 3272.5 | 3447.5 | 130.5861 | 0 | 140.7814 | 0 | 1.3059 | 0 | 1.4078 | 0 | 1.3059 | 1.4078 | 19.7934 | 11.118 | 18.4875
38953.6122 | 1929 | 0 | 38953.6122 | 2324 | 0 |  | 3457 | 3632 | 117.7656 | 0 | 141.8803 | 0 | 1.1777 | 0 | 1.4188 | 0 | 1.1777 | 1.4188 | 32.8346 | 10.2573 | 31.657
38953.6143 | 1827 | 0 | 38953.6143 | 2546 | 0 |  | 3641.5 | 3816.5 | 111.5385 | 0 | 155.4335 | 0 | 1.1154 | 0 | 1.5543 | 0 | 1.1154 | 1.5543 | 40.2507 | 0.64336 | 39.1353
38953.6165 | 1643 | 0 | 38953.6165 | 2313 | 0 |  | 3826.5 | 4001.5 | 100.3053 | 0 | 141.2088 | 0 | 1.0031 | 0 | 1.4121 | 0 | 1.0031 | 1.4121 | 55.9574 | 10.7817 | 54.9543

## C5-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 152.5263 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38953.5715 | 1 | 0 | 38953.5715 | 1 | 0 |  | -56.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5737 | 1 | 0 | 38953.5737 | 1 | 0 |  | 128.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5758 | 1 | 0 | 38953.5758 | 1 | 0 |  | 313 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5779 | 1 | 0 | 38953.578 | 1 | 0 |  | 498 | 673 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5801 | 1 | 0 | 38953.5801 | 1 | 0 |  | 682.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5822 | 1 | 0 | 38953.5822 | 1 | 0 |  | 867.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5844 | 1 | 0 | 38953.5844 | 1 | 0 |  | 1052 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5865 | 1 | 0 | 38953.5865 | 1 | 0 |  | 1237 | 1412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5886 | 1 | 0 | 38953.5886 | 1 | 0 |  | 1421.5 | 1596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5908 | 1 | 1 | 38953.5908 | 1 | 0 |  | 1606.5 | 1781.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 623690686.44 | 249738 | 249538.0801
38953.5929 | 1 | 1 | 38953.5929 | 1 | 0 |  | 1791.5 | 1966.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 623690686.44 | 249738 | 249538.0801
38953.595 | 1 | 0 | 38953.5951 | 1 | 0 |  | 1976 | 2151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38953.5972 | 1 | 1 | 38953.5972 | 2 | 0 |  | 2161 | 2336 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 311720474.22 | 124819 | 249438.1601
38953.5993 | 522 | 0 | 38953.5993 | 2443 | 0 |  | 2345.5 | 2520.5 | 31.8681 | 0 | 149.1453 | 0 | 0.31868 | 0 | 1.4915 | 0 | 0.31868 | 1.4915 | 378.6169 | 2.2669 | 378.2982
38953.6015 | 1013 | 0 | 38953.6015 | 2265 | 0 |  | 2530.5 | 2705.5 | 61.8437 | 0 | 138.2784 | 0 | 0.61844 | 0 | 1.3828 | 0 | 0.61844 | 1.3828 | 146.6318 | 10.3038 | 146.0133
38953.6036 | 1677 | 0 | 38953.6036 | 2482 | 0 |  | 2715 | 2890 | 102.381 | 0 | 151.5263 | 0 | 1.0238 | 0 | 1.5153 | 0 | 1.0238 | 1.5153 | 48.9791 | 0.65995 | 47.9553
38953.6057 | 1668 | 0 | 38953.6058 | 2408 | 0 |  | 2900 | 3075 | 101.8315 | 0 | 147.0085 | 0 | 1.0183 | 0 | 1.4701 | 0 | 1.0183 | 1.4701 | 49.783 | 3.7533 | 48.7647
38953.6079 | 1735 | 0 | 38953.6079 | 2140 | 0 |  | 3084.5 | 3259.5 | 105.9219 | 0 | 130.6471 | 0 | 1.0592 | 0 | 1.3065 | 0 | 1.0592 | 1.3065 | 43.9988 | 16.7467 | 42.9396
38953.61 | 2085 | 0 | 38953.61 | 2137 | 0 |  | 3269.5 | 3444.5 | 127.2894 | 0 | 130.464 | 0 | 1.2729 | 0 | 1.3046 | 0 | 1.2729 | 1.3046 | 19.8264 | 16.9106 | 18.5535
38953.6122 | 1917 | 0 | 38953.6122 | 1970 | 0 |  | 3454.5 | 3629.5 | 117.033 | 0 | 120.2686 | 0 | 1.1703 | 0 | 1.2027 | 0 | 1.1703 | 1.2027 | 30.3276 | 26.8213 | 29.1573
38953.6143 | 1545 | 0 | 38953.6143 | 2162 | 0 |  | 3639 | 3814 | 94.3223 | 0 | 131.9902 | 0 | 0.94322 | 0 | 1.3199 | 0 | 0.94322 | 1.3199 | 61.7074 | 15.5587 | 60.7642
38953.6164 | 1732 | 0 | 38953.6164 | 2047 | 0 |  | 3823.5 | 3998.5 | 105.7387 | 0 | 124.9695 | 0 | 1.0574 | 0 | 1.2497 | 0 | 1.0574 | 1.2497 | 44.2483 | 22.0508 | 43.1909

## C5-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 140.6215 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38953.5715 | 1 | 0 | 38953.5715 | 1 | 0 |  | -59.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5736 | 1 | 0 | 38953.5736 | 1 | 0 |  | 125.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5758 | 1 | 0 | 38953.5758 | 1 | 0 |  | 310.5 | 485.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5779 | 1 | 0 | 38953.5779 | 1 | 0 |  | 495 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.58 | 1 | 0 | 38953.5801 | 1 | 0 |  | 680 | 855 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5822 | 1 | 0 | 38953.5822 | 1 | 0 |  | 864.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5843 | 1 | 0 | 38953.5843 | 1 | 0 |  | 1049.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5865 | 1 | 0 | 38953.5865 | 1 | 0 |  | 1234 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5886 | 1 | 0 | 38953.5886 | 1 | 0 |  | 1419 | 1594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230238 | 230238 | 230237.9994
38953.5907 | 1 | 1 | 38953.5908 | 1 | 0 |  | 1603.5 | 1778.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 530095366.44 | 230238 | 230038.0868
38953.5929 | 1 | 1 | 38953.5929 | 2 | 0 |  | 1788.5 | 1963.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 264932564.22 | 115069 | 229938.1737
38953.595 | 1 | 1 | 38953.595 | 1 | 0 |  | 1973.5 | 2148.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 530095366.44 | 230238 | 230038.0868
38953.5972 | 1 | 1 | 38953.5972 | 1 | 0 |  | 2158 | 2333 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 530095366.44 | 230238 | 230038.0868
38953.5993 | 478 | 1 | 38953.5993 | 1476 | 0 |  | 2343 | 2518 | 29.1819 | 0.06105 | 90.1099 | 0 | 0.29182 | 0.0006105 | 0.9011 | 0 | 0.29121 | 0.9011 | 384.1158 | 56.0556 | 65532.1972
38953.6014 | 1014 | 0 | 38953.6014 | 2095 | 0 |  | 2527.5 | 2702.5 | 61.9048 | 0 | 127.8999 | 0 | 0.61905 | 0 | 1.279 | 0 | 0.61905 | 1.279 | 127.1578 | 9.9465 | 126.5387
38953.6036 | 1401 | 0 | 38953.6036 | 1990 | 0 |  | 2712.5 | 2887.5 | 85.5311 | 0 | 121.4896 | 0 | 0.85531 | 0 | 1.2149 | 0 | 0.85531 | 1.2149 | 64.4097 | 15.7477 | 63.5544
38953.6057 | 1522 | 0 | 38953.6057 | 2074 | 0 |  | 2897 | 3072 | 92.9182 | 0 | 126.6178 | 0 | 0.92918 | 0 | 1.2662 | 0 | 0.92918 | 1.2662 | 51.339 | 11.0598 | 50.4098
38953.6078 | 2165 | 0 | 38953.6079 | 1995 | 0 |  | 3082 | 3257 | 132.1734 | 0 | 121.7949 | 0 | 1.3217 | 0 | 1.2179 | 0 | 1.3217 | 1.2179 | 6.3917 | 15.4576 | 5.07
38953.61 | 1788 | 0 | 38953.61 | 2287 | 0 |  | 3266.5 | 3441.5 | 109.1575 | 0 | 139.6215 | 0 | 1.0916 | 0 | 1.3962 | 0 | 1.0916 | 1.3962 | 28.8244 | 0.71622 | 27.7328
38953.6121 | 2205 | 0 | 38953.6121 | 1935 | 0 |  | 3451.5 | 3626.5 | 134.6154 | 0 | 118.1319 | 0 | 1.3462 | 0 | 1.1813 | 0 | 1.3462 | 1.1813 | 4.4617 | 19.0377 | 3.1155
38953.6143 | 1508 | 0 | 38953.6143 | 2199 | 0 |  | 3636 | 3811 | 92.0635 | 0 | 134.2491 | 0 | 0.92063 | 0 | 1.3425 | 0 | 0.92063 | 1.3425 | 52.744 | 4.7467 | 51.8234
38953.6164 | 1716 | 0 | 38953.6164 | 2200 | 0 |  | 3821 | 3996 | 104.7619 | 0 | 134.3101 | 0 | 1.0476 | 0 | 1.3431 | 0 | 1.0476 | 1.3431 | 34.2296 | 4.6991 | 33.182

## C5-C6
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 142.2088 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38953.5714 | 1 | 0 | 38953.5714 | 1 | 0 |  | -67.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5735 | 1 | 0 | 38953.5736 | 1 | 0 |  | 117 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5757 | 1 | 0 | 38953.5757 | 1 | 0 |  | 302 | 477 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5778 | 1 | 0 | 38953.5778 | 1 | 0 |  | 486.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.58 | 1 | 0 | 38953.58 | 1 | 0 |  | 671.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5821 | 1 | 0 | 38953.5821 | 1 | 0 |  | 856.5 | 1031.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5842 | 1 | 0 | 38953.5842 | 1 | 0 |  | 1041 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5864 | 1 | 0 | 38953.5864 | 1 | 0 |  | 1225.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5885 | 1 | 0 | 38953.5885 | 1 | 0 |  | 1410.5 | 1585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232838 | 232838 | 232837.9994
38953.5906 | 1182 | 1190 | 38953.5907 | 1131 | 1106 |  | 1595.5 | 1770.5 | 72.1612 | 72.6496 | 69.0476 | 67.5214 | 0.72161 | 0.7265 | 0.69048 | 0.67521 | 0.004884 | 0.015263 | 291.9078 | 309.0407 | 2.7059
38953.5928 | 1132 | 1183 | 38953.5928 | 1138 | 1186 |  | 1780 | 1955 | 69.1087 | 72.2222 | 69.475 | 72.4054 | 0.69109 | 0.72222 | 0.69475 | 0.72405 | 0.031136 | 0.029304 | 590.9039 | 780.1612 | 1.0774
38953.5949 | 1070 | 1155 | 38953.5949 | 955 | 928 |  | 1965 | 2140 | 65.3236 | 70.5128 | 58.3028 | 56.6545 | 0.65324 | 0.70513 | 0.58303 | 0.56654 | 0.051893 | 0.016484 | 769.5557 | 1468.5262 | 8.4611
38953.5971 | 1166 | 1139 | 38953.5971 | 1121 | 1092 |  | 2149.5 | 2324.5 | 71.1844 | 69.536 | 68.4371 | 66.6667 | 0.71184 | 0.69536 | 0.68437 | 0.66667 | 0.016484 | 0.017705 | 40029.9265 | 4727.3721 | 2.0961
38953.5992 | 1159 | 808 | 38953.5992 | 1090 | 791 |  | 2334.5 | 2509.5 | 70.757 | 49.3284 | 66.5446 | 48.2906 | 0.70757 | 0.49328 | 0.66545 | 0.48291 | 0.21429 | 0.18254 | 419.4882 | 1122.252 | 41.1796
38953.6013 | 1651 | 709 | 38953.6014 | 1466 | 541 |  | 2519 | 2694 | 100.7937 | 43.2845 | 89.4994 | 33.0281 | 1.0079 | 0.43284 | 0.89499 | 0.33028 | 0.57509 | 0.56471 | 128.3541 | 171.4723 | 2.7279
38953.6035 | 1707 | 413 | 38953.6035 | 1851 | 495 |  | 2704 | 2879 | 104.2125 | 25.2137 | 113.0037 | 30.2198 | 1.0421 | 0.25214 | 1.13 | 0.3022 | 0.78999 | 0.82784 | 158.1456 | 45.8659 | 15.9412
38953.6056 | 1617 | 260 | 38953.6056 | 1646 | 259 |  | 2888.5 | 3063.5 | 98.7179 | 15.873 | 100.4884 | 15.812 | 0.98718 | 0.15873 | 1.0049 | 0.15812 | 0.82845 | 0.84676 | 74.0191 | 65.894 | 69.1107
38953.6078 | 2056 | 173 | 38953.6078 | 1900 | 157 |  | 3073.5 | 3248.5 | 125.5189 | 10.5617 | 115.9951 | 9.5849 | 1.2552 | 0.10562 | 1.16 | 0.095849 | 1.1496 | 1.0641 | 17.796 | 49.8826 | 19.3108
38953.6099 | 2101 | 105 | 38953.6099 | 2313 | 116 |  | 3258.5 | 3433.5 | 128.2662 | 6.4103 | 141.2088 | 7.0818 | 1.2827 | 0.064103 | 1.4121 | 0.070818 | 1.2186 | 1.3413 | 4.2624 | 3.1231 | 3.5587
38953.612 | 2181 | 151 | 38953.612 | 1970 | 132 |  | 3443 | 3618 | 133.1502 | 9.2186 | 120.2686 | 8.0586 | 1.3315 | 0.092186 | 1.2027 | 0.080586 | 1.2393 | 1.1221 | 7.3877 | 701.1701 | 1.5185
38953.6142 | 1715 | 303 | 38953.6142 | 1636 | 290 |  | 3627.5 | 3802.5 | 104.7009 | 18.4982 | 99.8779 | 17.7045 | 1.047 | 0.18498 | 0.99878 | 0.17705 | 0.86203 | 0.82173 | 59.1947 | 80.9937 | 45.9871
38953.6163 | 1991 | 320 | 38953.6163 | 1673 | 342 |  | 3812.5 | 3987.5 | 121.5507 | 19.536 | 102.1368 | 20.8791 | 1.2155 | 0.19536 | 1.0214 | 0.20879 | 1.0201 | 0.81258 | 16.7935 | 93.0368 | 2.7683

## B4-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 139.0952 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38953.5713 | 1 | 0 | 38953.5713 | 1 | 0 |  | -76 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5734 | 1 | 0 | 38953.5734 | 1 | 0 |  | 108.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5756 | 1 | 0 | 38953.5756 | 1 | 0 |  | 293.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5777 | 1 | 0 | 38953.5777 | 1 | 0 |  | 478.5 | 653.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5798 | 1 | 0 | 38953.5799 | 1 | 0 |  | 663 | 838 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.582 | 1 | 0 | 38953.582 | 1 | 0 |  | 848 | 1023 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5841 | 1 | 0 | 38953.5841 | 1 | 0 |  | 1032.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5863 | 1 | 0 | 38953.5863 | 1 | 0 |  | 1217.5 | 1392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5884 | 1 | 0 | 38953.5884 | 1 | 0 |  | 1402 | 1577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5905 | 1 | 0 | 38953.5906 | 1 | 0 |  | 1587 | 1762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5927 | 1 | 0 | 38953.5927 | 1 | 0 |  | 1771.5 | 1946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5948 | 1 | 0 | 38953.5948 | 1 | 0 |  | 1956.5 | 2131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.597 | 1 | 0 | 38953.597 | 1 | 0 |  | 2141.5 | 2316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227738 | 227738 | 227737.9994
38953.5991 | 1515 | 0 | 38953.5991 | 607 | 0 |  | 2326 | 2501 | 92.4908 | 0 | 37.0574 | 0 | 0.92491 | 0 | 0.37057 | 0 | 0.92491 | 0.37057 | 50.3881 | 275.3509 | 49.4632
38953.6012 | 1023 | 0 | 38953.6012 | 2162 | 0 |  | 2510.5 | 2685.5 | 62.4542 | 0 | 131.9902 | 0 | 0.62454 | 0 | 1.3199 | 0 | 0.62454 | 1.3199 | 122.7155 | 5.383 | 122.091
38953.6034 | 1703 | 0 | 38953.6034 | 1980 | 0 |  | 2695.5 | 2870.5 | 103.9683 | 0 | 120.8791 | 0 | 1.0397 | 0 | 1.2088 | 0 | 1.0397 | 1.2088 | 33.7863 | 15.0697 | 32.7466
38953.6055 | 1771 | 0 | 38953.6055 | 2057 | 0 |  | 2880.5 | 3055.5 | 108.1197 | 0 | 125.58 | 0 | 1.0812 | 0 | 1.2558 | 0 | 1.0812 | 1.2558 | 28.6494 | 10.7623 | 27.5682
38953.6077 | 2150 | 0 | 38953.6077 | 1963 | 0 |  | 3065 | 3240 | 131.2576 | 0 | 119.8413 | 0 | 1.3126 | 0 | 1.1984 | 0 | 1.3126 | 1.1984 | 5.9712 | 16.0662 | 4.6586
38953.6098 | 2110 | 0 | 38953.6098 | 2126 | 0 |  | 3250 | 3425 | 128.8156 | 0 | 129.7924 | 0 | 1.2882 | 0 | 1.2979 | 0 | 1.2882 | 1.2979 | 7.9801 | 7.1675 | 6.6919
38953.6119 | 1858 | 6 | 38953.6119 | 2071 | 2 |  | 3434.5 | 3609.5 | 113.431 | 0.3663 | 126.4347 | 0.1221 | 1.1343 | 0.003663 | 1.2643 | 0.001221 | 1.1306 | 1.2631 | 23.4537 | 10.0647 | 631.5382
38953.6141 | 1452 | 300 | 38953.6141 | 2262 | 307 |  | 3619.5 | 3794.5 | 88.6447 | 18.315 | 138.0952 | 18.7424 | 0.88645 | 0.18315 | 1.381 | 0.18742 | 0.7033 | 1.1935 | 13.8407 | 6.2258 | 10.2836
38953.6162 | 1645 | 6 | 38953.6162 | 1943 | 10 |  | 3804 | 3979 | 100.4274 | 0.3663 | 118.6203 | 0.6105 | 1.0043 | 0.003663 | 1.1862 | 0.006105 | 1.0006 | 1.1801 | 39.4661 | 17.5807 | 1563.4328

## B4-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 152.3431 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38953.5713 | 1 | 0 | 38953.5713 | 1 | 0 |  | -79 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5734 | 1 | 0 | 38953.5734 | 1 | 0 |  | 106 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5755 | 1 | 0 | 38953.5756 | 1 | 0 |  | 290.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5777 | 1 | 0 | 38953.5777 | 1 | 0 |  | 475.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5798 | 1 | 0 | 38953.5798 | 1 | 0 |  | 660.5 | 835.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.582 | 1 | 0 | 38953.582 | 1 | 0 |  | 845 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5841 | 1 | 0 | 38953.5841 | 1 | 0 |  | 1030 | 1205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5862 | 1 | 0 | 38953.5863 | 1 | 0 |  | 1214.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5884 | 1 | 0 | 38953.5884 | 1 | 0 |  | 1399.5 | 1574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5905 | 1 | 0 | 38953.5905 | 1 | 0 |  | 1584 | 1759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5927 | 1 | 0 | 38953.5927 | 1 | 0 |  | 1769 | 1944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5948 | 1 | 0 | 38953.5948 | 1 | 0 |  | 1953.5 | 2128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5969 | 1 | 0 | 38953.5969 | 1 | 0 |  | 2138.5 | 2313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38953.5991 | 1337 | 0 | 38953.5991 | 9 | 0 |  | 2323 | 2498 | 81.6239 | 0 | 0.54945 | 0 | 0.81624 | 0 | 0.0054945 | 0 | 0.81624 | 0.0054945 | 86.6402 | 27626.4444 | 85.824
38953.6012 | 871 | 0 | 38953.6012 | 1954 | 0 |  | 2508 | 2683 | 53.1746 | 0 | 119.2918 | 0 | 0.53175 | 0 | 1.1929 | 0 | 0.53175 | 1.1929 | 186.496 | 27.7062 | 185.9642
38953.6033 | 1688 | 0 | 38953.6034 | 2374 | 0 |  | 2692.5 | 2867.5 | 103.0525 | 0 | 144.9328 | 0 | 1.0305 | 0 | 1.4493 | 0 | 1.0305 | 1.4493 | 47.8306 | 5.1129 | 46.8
38953.6055 | 1831 | 0 | 38953.6055 | 2479 | 0 |  | 2877.5 | 3052.5 | 111.7827 | 0 | 151.3431 | 0 | 1.1178 | 0 | 1.5134 | 0 | 1.1178 | 1.5134 | 36.2851 | 0.66075 | 35.1673
38953.6076 | 2217 | 0 | 38953.6076 | 2291 | 0 |  | 3062.5 | 3237.5 | 135.348 | 0 | 139.8657 | 0 | 1.3535 | 0 | 1.3987 | 0 | 1.3535 | 1.3987 | 12.5566 | 8.921 | 11.2031
38953.6098 | 2353 | 0 | 38953.6098 | 2106 | 0 |  | 3247 | 3422 | 143.6508 | 0 | 128.5714 | 0 | 1.4365 | 0 | 1.2857 | 0 | 1.4365 | 1.2857 | 6.051 | 18.4891 | 4.6145
38953.6119 | 1817 | 2 | 38953.6119 | 2116 | 1 |  | 3432 | 3607 | 110.928 | 0.1221 | 129.1819 | 0.06105 | 1.1093 | 0.001221 | 1.2918 | 0.0006105 | 1.1081 | 1.2912 | 37.607 | 17.9602 | 5149.153
38953.614 | 1609 | 333 | 38953.6141 | 1551 | 324 |  | 3616.5 | 3791.5 | 98.2295 | 20.3297 | 94.6886 | 19.7802 | 0.9823 | 0.2033 | 0.94689 | 0.1978 | 0.779 | 0.74908 | 91.5561 | 108.1617 | 86.3479
38953.6162 | 1755 | 5 | 38953.6162 | 2149 | 4 |  | 3801.5 | 3976.5 | 107.1429 | 0.30525 | 131.1966 | 0.2442 | 1.0714 | 0.0030525 | 1.312 | 0.002442 | 1.0684 | 1.3095 | 43.0661 | 16.2185 | 2052.4697

## B4-D8
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 156.4335 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38953.5712 | 1 | 0 | 38953.5713 | 1 | 0 |  | -81.5 | 93.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5734 | 1 | 0 | 38953.5734 | 1 | 0 |  | 103 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5755 | 1 | 0 | 38953.5755 | 1 | 0 |  | 288 | 463 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5777 | 1 | 0 | 38953.5777 | 1 | 0 |  | 472.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5798 | 1 | 0 | 38953.5798 | 1 | 0 |  | 657.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5819 | 1 | 0 | 38953.5819 | 1 | 0 |  | 842 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5841 | 1 | 0 | 38953.5841 | 1 | 0 |  | 1027 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5862 | 1 | 0 | 38953.5862 | 1 | 0 |  | 1211.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5883 | 1 | 0 | 38953.5884 | 1 | 0 |  | 1396.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5905 | 1 | 0 | 38953.5905 | 1 | 0 |  | 1581.5 | 1756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5926 | 1 | 0 | 38953.5926 | 1 | 0 |  | 1766 | 1941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5948 | 1 | 0 | 38953.5948 | 1 | 0 |  | 1951 | 2126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
38953.5969 | 37 | 31 | 38953.5969 | 46 | 44 |  | 2135.5 | 2310.5 | 2.2589 | 1.8926 | 2.8083 | 2.6862 | 0.022589 | 0.018926 | 0.028083 | 0.026862 | 0.003663 | 0.001221 | 42254.1461 | 132729.6903 | 8040.3294
38953.599 | 940 | 0 | 38953.5991 | 2080 | 0 |  | 2320.5 | 2495.5 | 57.3871 | 0 | 126.9841 | 0 | 0.57387 | 0 | 1.2698 | 0 | 0.57387 | 1.2698 | 172.5936 | 23.1913 | 172.0197
38953.6012 | 946 | 0 | 38953.6012 | 2036 | 0 |  | 2505 | 2680 | 57.7534 | 0 | 124.2979 | 0 | 0.57753 | 0 | 1.243 | 0 | 0.57753 | 1.243 | 170.8647 | 25.8536 | 170.2872
38953.6033 | 1899 | 0 | 38953.6033 | 2352 | 0 |  | 2690 | 2865 | 115.9341 | 0 | 143.5897 | 0 | 1.1593 | 0 | 1.4359 | 0 | 1.1593 | 1.4359 | 34.9331 | 8.9447 | 33.7738
38953.6055 | 1912 | 0 | 38953.6055 | 2439 | 0 |  | 2874.5 | 3049.5 | 116.7277 | 0 | 148.9011 | 0 | 1.1673 | 0 | 1.489 | 0 | 1.1673 | 1.489 | 34.0157 | 5.0586 | 32.8484
38953.6076 | 2084 | 0 | 38953.6076 | 2546 | 0 |  | 3059.5 | 3234.5 | 127.2283 | 0 | 155.4335 | 0 | 1.2723 | 0 | 1.5543 | 0 | 1.2723 | 1.5543 | 22.9549 | 0.64336 | 21.6826
38953.6097 | 2318 | 0 | 38953.6097 | 2365 | 0 |  | 3244.5 | 3419.5 | 141.514 | 0 | 144.3834 | 0 | 1.4151 | 0 | 1.4438 | 0 | 1.4151 | 1.4438 | 10.5427 | 8.3459 | 9.1276
38953.6119 | 2038 | 0 | 38953.6119 | 2142 | 0 |  | 3429 | 3604 | 124.42 | 0 | 130.7692 | 0 | 1.2442 | 0 | 1.3077 | 0 | 1.2442 | 1.3077 | 25.7301 | 19.6256 | 24.4859
38953.614 | 1580 | 0 | 38953.614 | 2135 | 0 |  | 3613.5 | 3788.5 | 96.4591 | 0 | 130.3419 | 0 | 0.96459 | 0 | 1.3034 | 0 | 0.96459 | 1.3034 | 62.1759 | 20.0178 | 61.2114
38953.6161 | 1720 | 0 | 38953.6162 | 2164 | 0 |  | 3798.5 | 3973.5 | 105.0061 | 0 | 132.1123 | 0 | 1.0501 | 0 | 1.3211 | 0 | 1.0501 | 1.3211 | 48.9756 | 18.4094 | 47.9255

## B4-D7
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 148.7411 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38953.5712 | 1 | 0 | 38953.5712 | 1 | 0 |  | -84.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5733 | 1 | 0 | 38953.5734 | 1 | 0 |  | 100.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5755 | 1 | 0 | 38953.5755 | 1 | 0 |  | 285 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5776 | 1 | 0 | 38953.5776 | 1 | 0 |  | 470 | 645 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5798 | 1 | 0 | 38953.5798 | 1 | 0 |  | 654.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5819 | 1 | 0 | 38953.5819 | 1 | 0 |  | 839.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.584 | 1 | 0 | 38953.5841 | 1 | 0 |  | 1024 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5862 | 1 | 0 | 38953.5862 | 1 | 0 |  | 1209 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5883 | 1 | 0 | 38953.5883 | 1 | 0 |  | 1393.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5905 | 1 | 0 | 38953.5905 | 1 | 0 |  | 1578.5 | 1753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5926 | 1 | 0 | 38953.5926 | 1 | 0 |  | 1763.5 | 1938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243538 | 243538 | 243537.9994
38953.5947 | 2 | 0 | 38953.5947 | 2 | 0 |  | 1948 | 2123 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 121719 | 121719 | 121718.9988
38953.5969 | 31 | 24 | 38953.5969 | 37 | 31 |  | 2133 | 2308 | 1.8926 | 1.4652 | 2.2589 | 1.8926 | 0.018926 | 0.014652 | 0.022589 | 0.018926 | 0.0042735 | 0.003663 | 34655.2636 | 40594.8857 | 9898.0342
38953.599 | 649 | 0 | 38953.599 | 2034 | 0 |  | 2317.5 | 2492.5 | 39.6215 | 0 | 124.1758 | 0 | 0.39621 | 0 | 1.2418 | 0 | 0.39621 | 1.2418 | 275.4052 | 19.7827 | 275.009
38953.6011 | 921 | 0 | 38953.6012 | 2253 | 0 |  | 2502.5 | 2677.5 | 56.2271 | 0 | 137.5458 | 0 | 0.56227 | 0 | 1.3755 | 0 | 0.56227 | 1.3755 | 164.5364 | 8.1394 | 163.9741
38953.6033 | 1981 | 0 | 38953.6033 | 2420 | 0 |  | 2687 | 2862 | 120.9402 | 0 | 147.7411 | 0 | 1.2094 | 0 | 1.4774 | 0 | 1.2094 | 1.4774 | 22.9874 | 0.67686 | 21.778
38953.6054 | 1861 | 1 | 38953.6054 | 2039 | 0 |  | 2872 | 3047 | 113.6142 | 0.06105 | 124.4811 | 0 | 1.1361 | 0.0006105 | 1.2448 | 0 | 1.1355 | 1.2448 | 31.02 | 19.489 | 9368.2892
38953.6076 | 2043 | 0 | 38953.6076 | 2097 | 0 |  | 3056.5 | 3231.5 | 124.7253 | 0 | 128.022 | 0 | 1.2473 | 0 | 1.2802 | 0 | 1.2473 | 1.2802 | 19.255 | 16.1841 | 18.0078
38953.6097 | 2201 | 0 | 38953.6097 | 2035 | 0 |  | 3241.5 | 3416.5 | 134.3712 | 0 | 124.2369 | 0 | 1.3437 | 0 | 1.2424 | 0 | 1.3437 | 1.2424 | 10.6942 | 19.7238 | 9.3505
38953.6118 | 2006 | 0 | 38953.6119 | 2356 | 0 |  | 3426.5 | 3601.5 | 122.4664 | 0 | 143.8339 | 0 | 1.2247 | 0 | 1.4383 | 0 | 1.2247 | 1.4383 | 21.4546 | 3.4117 | 20.23
38953.614 | 1391 | 0 | 38953.614 | 2141 | 0 |  | 3611 | 3786 | 84.9206 | 0 | 130.7082 | 0 | 0.84921 | 0 | 1.3071 | 0 | 0.84921 | 1.3071 | 75.1531 | 13.7964 | 74.3039
38953.6161 | 1643 | 0 | 38953.6161 | 2193 | 0 |  | 3796 | 3971 | 100.3053 | 0 | 133.8828 | 0 | 1.0031 | 0 | 1.3388 | 0 | 1.0031 | 1.3388 | 48.2885 | 11.098 | 47.2854

## B4-C6
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38953.5712 | 1 | 0 | 38953.5712 | 1 | 0 |  | -87.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5733 | 1 | 0 | 38953.5733 | 1 | 0 |  | 97.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5755 | 1 | 0 | 38953.5755 | 1 | 0 |  | 282.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5776 | 1 | 0 | 38953.5776 | 1 | 0 |  | 467 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5797 | 1 | 0 | 38953.5797 | 1 | 0 |  | 652 | 827 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5819 | 1 | 0 | 38953.5819 | 1 | 0 |  | 836.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.584 | 1 | 0 | 38953.584 | 1 | 0 |  | 1021.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5861 | 1 | 0 | 38953.5862 | 1 | 0 |  | 1206 | 1381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5883 | 1 | 0 | 38953.5883 | 1 | 0 |  | 1391 | 1566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5904 | 1 | 0 | 38953.5904 | 1 | 0 |  | 1575.5 | 1750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5926 | 1 | 0 | 38953.5926 | 2 | 0 |  | 1760.5 | 1935.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38953.5947 | 1 | 0 | 38953.5947 | 1 | 0 |  | 1945.5 | 2120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5968 | 58 | 48 | 38953.5969 | 48 | 46 |  | 2130 | 2305 | 3.5409 | 2.9304 | 2.9304 | 2.8083 | 0.035409 | 0.029304 | 0.029304 | 0.028083 | 0.006105 | 0.001221 | 20635.439 | 116202.8197 | 4177.6965
38953.599 | 608 | 136 | 38953.599 | 391 | 134 |  | 2314.5 | 2489.5 | 37.1184 | 8.3028 | 23.8706 | 8.1807 | 0.37118 | 0.083028 | 0.23871 | 0.081807 | 0.28816 | 0.1569 | 330.8451 | 795.3989 | 894.2096
38953.6011 | 1064 | 252 | 38953.6011 | 969 | 183 |  | 2499.5 | 2674.5 | 64.9573 | 15.3846 | 59.1575 | 11.1722 | 0.64957 | 0.15385 | 0.59158 | 0.11172 | 0.49573 | 0.47985 | 157.8913 | 170.7244 | 199.4513
38953.6033 | 1713 | 28 | 38953.6033 | 1290 | 24 |  | 2684.5 | 2859.5 | 104.5788 | 1.7094 | 78.7546 | 1.4652 | 1.0458 | 0.017094 | 0.78755 | 0.014652 | 1.0287 | 0.77289 | 24.3131 | 70.507 | 549.4124
38953.6054 | 2073 | 7 | 38953.6054 | 1633 | 7 |  | 2869 | 3044 | 126.5568 | 0.42735 | 99.6947 | 0.42735 | 1.2656 | 0.0042735 | 0.99695 | 0.0042735 | 1.2613 | 0.99267 | 1.9546 | 37.8605 | 129.5465
38953.6075 | 1838 | 2 | 38953.6075 | 2093 | 2 |  | 3054 | 3229 | 112.21 | 0.1221 | 127.7778 | 0.1221 | 1.1221 | 0.001221 | 1.2778 | 0.001221 | 1.1209 | 1.2766 | 16.8901 | 0.96289 | 130.1904
38953.6097 | 1882 | 0 | 38953.6097 | 1806 | 0 |  | 3238.5 | 3413.5 | 114.8962 | 0 | 110.2564 | 0 | 1.149 | 0 | 1.1026 | 0 | 1.149 | 1.1026 | 12.2752 | 17 | 11.1263
38953.6118 | 1986 | 3 | 38953.6118 | 2092 | 7 |  | 3423.5 | 3598.5 | 121.2454 | 0.18315 | 127.7167 | 0.42735 | 1.2125 | 0.0018315 | 1.2772 | 0.0042735 | 1.2106 | 1.2729 | 7.4771 | 1.0555 | 43.1806
38953.6139 | 1797 | 221 | 38953.614 | 1556 | 203 |  | 3608 | 3783 | 109.707 | 13.4921 | 94.9939 | 12.3932 | 1.0971 | 0.13492 | 0.94994 | 0.12393 | 0.96215 | 0.82601 | 22.6598 | 121.8486 | 23.6149
38953.6161 | 1824 | 23 | 38953.6161 | 1530 | 24 |  | 3793 | 3968 | 111.3553 | 1.4042 | 93.4066 | 1.4652 | 1.1136 | 0.014042 | 0.93407 | 0.014652 | 1.0995 | 0.91941 | 16.5408 | 42.8406 | 346.889

## B4-C5
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 138.3626 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38953.5711 | 1 | 0 | 38953.5712 | 1 | 0 |  | -90 | 85 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5733 | 1 | 0 | 38953.5733 | 1 | 0 |  | 94.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5754 | 1 | 0 | 38953.5754 | 1 | 0 |  | 279.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5776 | 1 | 0 | 38953.5776 | 1 | 0 |  | 464.5 | 639.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5797 | 1 | 0 | 38953.5797 | 1 | 0 |  | 649 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5818 | 1 | 0 | 38953.5819 | 1 | 0 |  | 834 | 1009 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.584 | 1 | 0 | 38953.584 | 1 | 0 |  | 1018.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5861 | 1 | 0 | 38953.5861 | 1 | 0 |  | 1203.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5882 | 1 | 0 | 38953.5883 | 1 | 0 |  | 1388 | 1563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5904 | 1 | 0 | 38953.5904 | 1 | 0 |  | 1573 | 1748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5925 | 1 | 0 | 38953.5925 | 1 | 0 |  | 1757.5 | 1932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5947 | 1 | 0 | 38953.5947 | 1 | 0 |  | 1942.5 | 2117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 226538 | 226538 | 226537.9994
38953.5968 | 51 | 41 | 38953.5968 | 44 | 37 |  | 2127.5 | 2302.5 | 3.1136 | 2.5031 | 2.6862 | 2.2589 | 0.031136 | 0.025031 | 0.026862 | 0.022589 | 0.006105 | 0.0042735 | 22436.7237 | 32514.2671 | 5287.105
38953.5989 | 849 | 81 | 38953.599 | 443 | 99 |  | 2312 | 2487 | 51.8315 | 4.9451 | 27.0452 | 6.044 | 0.51832 | 0.049451 | 0.27045 | 0.06044 | 0.46886 | 0.21001 | 187.7172 | 626.0294 | 1422.6087
38953.6011 | 932 | 236 | 38953.6011 | 1105 | 229 |  | 2496.5 | 2671.5 | 56.8987 | 14.4078 | 67.4603 | 13.9805 | 0.56899 | 0.14408 | 0.6746 | 0.1398 | 0.42491 | 0.5348 | 248.6231 | 148.1555 | 277.8654
38953.6032 | 1642 | 33 | 38953.6032 | 1548 | 38 |  | 2681.5 | 2856.5 | 100.2442 | 2.0147 | 94.5055 | 2.3199 | 1.0024 | 0.020147 | 0.94505 | 0.023199 | 0.9823 | 0.92186 | 40.4404 | 50.7318 | 603.1539
38953.6054 | 1885 | 6 | 38953.6054 | 1639 | 8 |  | 2866.5 | 3041.5 | 115.0794 | 0.3663 | 100.0611 | 0.4884 | 1.1508 | 0.003663 | 1.0006 | 0.004884 | 1.1471 | 0.99573 | 20.4628 | 39.4107 | 1768.6323
38953.6075 | 2200 | 2 | 38953.6075 | 2066 | 2 |  | 3051 | 3226 | 134.3101 | 0.1221 | 126.1294 | 0.1221 | 1.3431 | 0.001221 | 1.2613 | 0.001221 | 1.3419 | 1.2601 | 3.0477 | 10.0271 | 293.3582
38953.6096 | 2250 | 1 | 38953.6097 | 2055 | 0 |  | 3236 | 3411 | 137.3626 | 0.06105 | 125.4579 | 0 | 1.3736 | 0.0006105 | 1.2546 | 0 | 1.373 | 1.2546 | 0.73149 | 10.2861 | 143.4457
38953.6118 | 1959 | 3 | 38953.6118 | 1826 | 4 |  | 3420.5 | 3595.5 | 119.5971 | 0.18315 | 111.4774 | 0.2442 | 1.196 | 0.0018315 | 1.1148 | 0.002442 | 1.1941 | 1.1123 | 15.8137 | 24.5104 | 1997.2842
38953.6139 | 1425 | 195 | 38953.6139 | 1799 | 235 |  | 3605.5 | 3780.5 | 86.9963 | 11.9048 | 109.8291 | 14.3468 | 0.86996 | 0.11905 | 1.0983 | 0.14347 | 0.75092 | 0.95482 | 128.7227 | 33.8329 | 83.7972
38953.6161 | 2070 | 41 | 38953.6161 | 1844 | 33 |  | 3790.5 | 3965.5 | 126.3736 | 2.5031 | 112.5763 | 2.0147 | 1.2637 | 0.025031 | 1.1258 | 0.020147 | 1.2387 | 1.1056 | 10.4239 | 28.2638 | 83.5099

## B3-E10
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 155.4567 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38953.571 | 1 | 0 | 38953.5711 | 1 | 0 |  | -98.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5732 | 1 | 0 | 38953.5732 | 1 | 0 |  | 86.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5753 | 1 | 0 | 38953.5753 | 1 | 0 |  | 271 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5775 | 1 | 0 | 38953.5775 | 1 | 0 |  | 456 | 631 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5796 | 1 | 0 | 38953.5796 | 1 | 0 |  | 640.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5817 | 1 | 0 | 38953.5817 | 1 | 0 |  | 825.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5839 | 1 | 0 | 38953.5839 | 1 | 0 |  | 1010 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.586 | 1 | 0 | 38953.586 | 1 | 0 |  | 1195 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5881 | 1 | 0 | 38953.5882 | 1 | 0 |  | 1379.5 | 1554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5903 | 1 | 0 | 38953.5903 | 1 | 0 |  | 1564.5 | 1739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5924 | 1 | 0 | 38953.5924 | 1 | 0 |  | 1749.5 | 1924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5946 | 1 | 0 | 38953.5946 | 1 | 0 |  | 1934 | 2109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5967 | 1 | 0 | 38953.5967 | 1 | 0 |  | 2119 | 2294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
38953.5988 | 358 | 0 | 38953.5989 | 2 | 0 |  | 2303.5 | 2478.5 | 21.8559 | 0 | 0.1221 | 0 | 0.21856 | 0 | 0.001221 | 0 | 0.21856 | 0.001221 | 611.2793 | 127219 | 611.0608
38953.601 | 699 | 0 | 38953.601 | 2011 | 0 |  | 2488.5 | 2663.5 | 42.674 | 0 | 122.7717 | 0 | 0.42674 | 0 | 1.2277 | 0 | 0.42674 | 1.2277 | 264.289 | 26.6226 | 263.8622
38953.6031 | 1822 | 0 | 38953.6031 | 2115 | 0 |  | 2673 | 2848 | 111.2332 | 0 | 129.1209 | 0 | 1.1123 | 0 | 1.2912 | 0 | 1.1123 | 1.2912 | 39.7574 | 20.3962 | 38.6451
38953.6053 | 1933 | 0 | 38953.6053 | 2327 | 0 |  | 2858 | 3033 | 118.0098 | 0 | 142.0635 | 0 | 1.1801 | 0 | 1.4206 | 0 | 1.1801 | 1.4206 | 31.732 | 9.4276 | 30.5519
38953.6074 | 1805 | 0 | 38953.6074 | 2530 | 0 |  | 3042.5 | 3217.5 | 110.1954 | 0 | 154.4567 | 0 | 1.102 | 0 | 1.5446 | 0 | 1.102 | 1.5446 | 41.0737 | 0.64743 | 39.9717
38953.6095 | 2243 | 0 | 38953.6095 | 2527 | 0 |  | 3227.5 | 3402.5 | 136.9353 | 0 | 154.2735 | 0 | 1.3694 | 0 | 1.5427 | 0 | 1.3694 | 1.5427 | 13.5256 | 0.76692 | 12.1563
38953.6117 | 2251 | 1 | 38953.6117 | 2325 | 1 |  | 3412.5 | 3587.5 | 137.4237 | 0.06105 | 141.9414 | 0.06105 | 1.3742 | 0.0006105 | 1.4194 | 0.0006105 | 1.3736 | 1.4188 | 13.1893 | 9.557 | 2567.968
38953.6138 | 1824 | 384 | 38953.6138 | 1692 | 202 |  | 3597 | 3772 | 111.3553 | 23.4432 | 103.2967 | 12.3321 | 1.1136 | 0.23443 | 1.033 | 0.12332 | 0.87912 | 0.90965 | 81.9906 | 68.7005 | 35.8853
38953.6159 | 1731 | 1 | 38953.616 | 2242 | 1 |  | 3782 | 3957 | 105.6777 | 0.06105 | 136.8742 | 0.06105 | 1.0568 | 0.0006105 | 1.3687 | 0.0006105 | 1.0562 | 1.3681 | 47.333 | 13.5951 | 9746.5565

## B3-E9
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 154.0525 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38953.571 | 1 | 0 | 38953.571 | 1 | 0 |  | -101.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5731 | 1 | 0 | 38953.5732 | 1 | 0 |  | 83.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5753 | 1 | 0 | 38953.5753 | 1 | 0 |  | 268.5 | 443.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5774 | 1 | 0 | 38953.5774 | 1 | 0 |  | 453 | 628 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5796 | 1 | 0 | 38953.5796 | 1 | 0 |  | 638 | 813 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5817 | 1 | 0 | 38953.5817 | 1 | 0 |  | 822.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5838 | 1 | 0 | 38953.5839 | 1 | 0 |  | 1007.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.586 | 1 | 0 | 38953.586 | 1 | 0 |  | 1192 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5881 | 1 | 0 | 38953.5881 | 1 | 0 |  | 1377 | 1552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5903 | 1 | 0 | 38953.5903 | 1 | 0 |  | 1561.5 | 1736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5924 | 1 | 0 | 38953.5924 | 1 | 0 |  | 1746.5 | 1921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5945 | 1 | 0 | 38953.5945 | 1 | 0 |  | 1931.5 | 2106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5967 | 1 | 0 | 38953.5967 | 1 | 0 |  | 2116 | 2291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
38953.5988 | 375 | 0 | 38953.5988 | 3 | 0 |  | 2300.5 | 2475.5 | 22.8938 | 0 | 0.18315 | 0 | 0.22894 | 0 | 0.0018315 | 0 | 0.22894 | 0.0018315 | 572.9013 | 84012.6667 | 572.6724
38953.6009 | 763 | 0 | 38953.601 | 1969 | 0 |  | 2485.5 | 2660.5 | 46.5812 | 0 | 120.2076 | 0 | 0.46581 | 0 | 1.2021 | 0 | 0.46581 | 1.2021 | 230.7182 | 28.1554 | 230.2524
38953.6031 | 1422 | 0 | 38953.6031 | 2318 | 0 |  | 2670.5 | 2845.5 | 86.8132 | 0 | 141.514 | 0 | 0.86813 | 0 | 1.4151 | 0 | 0.86813 | 1.4151 | 77.4529 | 8.8602 | 76.5848
38953.6052 | 2162 | 0 | 38953.6052 | 2376 | 0 |  | 2855 | 3030 | 131.9902 | 0 | 145.0549 | 0 | 1.3199 | 0 | 1.4505 | 0 | 1.3199 | 1.4505 | 16.7151 | 6.2029 | 15.3952
38953.6074 | 2101 | 0 | 38953.6074 | 2507 | 0 |  | 3040 | 3215 | 128.2662 | 0 | 153.0525 | 0 | 1.2827 | 0 | 1.5305 | 0 | 1.2827 | 1.5305 | 20.1038 | 0.65337 | 18.8211
38953.6095 | 2058 | 0 | 38953.6095 | 2164 | 0 |  | 3224.5 | 3399.5 | 125.641 | 0 | 132.1123 | 0 | 1.2564 | 0 | 1.3211 | 0 | 1.2564 | 1.3211 | 22.6132 | 16.6072 | 21.3568
38953.6116 | 1870 | 7 | 38953.6117 | 2316 | 0 |  | 3409.5 | 3584.5 | 114.1636 | 0.42735 | 141.3919 | 0 | 1.1416 | 0.0042735 | 1.4139 | 0 | 1.1374 | 1.4139 | 36.6075 | 8.9542 | 758.8817
38953.6138 | 1682 | 336 | 38953.6138 | 1791 | 161 |  | 3594 | 3769 | 102.6862 | 20.5128 | 109.3407 | 9.8291 | 1.0269 | 0.20513 | 1.0934 | 0.098291 | 0.82173 | 0.99512 | 128.3062 | 48.6787 | 49.2458
38953.6159 | 1636 | 1 | 38953.6159 | 2108 | 1 |  | 3779 | 3954 | 99.8779 | 0.06105 | 128.6935 | 0.06105 | 0.99878 | 0.0006105 | 1.2869 | 0.0006105 | 0.99817 | 1.2863 | 54.4428 | 19.7315 | 14607.3483

## B3-D8
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 155.0293 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38953.571 | 1 | 0 | 38953.571 | 1 | 0 |  | -104 | 71 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5731 | 2 | 0 | 38953.5731 | 1 | 0 |  | 80.5 | 255.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126869 | 253838 | 126868.9988
38953.5753 | 1 | 0 | 38953.5753 | 1 | 0 |  | 265.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5774 | 1 | 0 | 38953.5774 | 1 | 0 |  | 450.5 | 625.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5795 | 1 | 0 | 38953.5795 | 1 | 0 |  | 635 | 810 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5817 | 1 | 0 | 38953.5817 | 1 | 0 |  | 820 | 995 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5838 | 1 | 0 | 38953.5838 | 1 | 0 |  | 1004.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5859 | 1 | 0 | 38953.586 | 1 | 0 |  | 1189.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5881 | 1 | 0 | 38953.5881 | 1 | 0 |  | 1374 | 1549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5902 | 1 | 0 | 38953.5902 | 1 | 0 |  | 1559 | 1734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5924 | 1 | 0 | 38953.5924 | 1 | 0 |  | 1743.5 | 1918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5945 | 1 | 0 | 38953.5945 | 1 | 0 |  | 1928.5 | 2103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
38953.5966 | 28 | 21 | 38953.5967 | 28 | 23 |  | 2113.5 | 2288.5 | 1.7094 | 1.2821 | 1.7094 | 1.4042 | 0.017094 | 0.012821 | 0.017094 | 0.014042 | 0.0042735 | 0.0030525 | 36089.6664 | 50876.0679 | 11835.6886
38953.5988 | 296 | 1 | 38953.5988 | 2343 | 0 |  | 2298 | 2473 | 18.0708 | 0.06105 | 143.0403 | 0 | 0.18071 | 0.0006105 | 1.4304 | 0 | 0.1801 | 1.4304 | 792.5204 | 8.3816 | 17341.185
38953.6009 | 809 | 1 | 38953.6009 | 2337 | 1 |  | 2482.5 | 2657.5 | 49.3895 | 0.06105 | 142.674 | 0.06105 | 0.49389 | 0.0006105 | 1.4267 | 0.0006105 | 0.49328 | 1.4261 | 217.259 | 8.6652 | 13790.5042
38953.6031 | 1471 | 0 | 38953.6031 | 2004 | 0 |  | 2667.5 | 2842.5 | 89.8046 | 0 | 122.3443 | 0 | 0.89805 | 0 | 1.2234 | 0 | 0.89805 | 1.2234 | 72.6295 | 26.7156 | 71.7315
38953.6052 | 1804 | 0 | 38953.6052 | 1995 | 0 |  | 2852.5 | 3027.5 | 110.1343 | 0 | 121.7949 | 0 | 1.1013 | 0 | 1.2179 | 0 | 1.1013 | 1.2179 | 40.7639 | 27.2872 | 39.6625
38953.6073 | 2166 | 0 | 38953.6073 | 1972 | 0 |  | 3037 | 3212 | 132.2344 | 0 | 120.3907 | 0 | 1.3223 | 0 | 1.2039 | 0 | 1.3223 | 1.2039 | 17.2382 | 28.7718 | 15.9159
38953.6095 | 2187 | 0 | 38953.6095 | 2479 | 0 |  | 3222 | 3397 | 133.5165 | 0 | 151.3431 | 0 | 1.3352 | 0 | 1.5134 | 0 | 1.3352 | 1.5134 | 16.1125 | 2.4357 | 14.7773
38953.6116 | 2022 | 0 | 38953.6116 | 2178 | 0 |  | 3406.5 | 3581.5 | 123.4432 | 0 | 132.967 | 0 | 1.2344 | 0 | 1.3297 | 0 | 1.2344 | 1.3297 | 25.5875 | 16.5923 | 24.3531
38953.6137 | 1628 | 0 | 38953.6138 | 2523 | 0 |  | 3591.5 | 3766.5 | 99.3895 | 0 | 154.0293 | 0 | 0.99389 | 0 | 1.5403 | 0 | 0.99389 | 1.5403 | 55.9816 | 0.64923 | 54.9877
38953.6159 | 1726 | 0 | 38953.6159 | 2032 | 0 |  | 3776.5 | 3951.5 | 105.3724 | 0 | 124.0537 | 0 | 1.0537 | 0 | 1.2405 | 0 | 1.0537 | 1.2405 | 47.1251 | 24.9695 | 46.0714

## B3-D7
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 149.0464 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38953.5709 | 1 | 0 | 38953.571 | 1 | 0 |  | -107 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5731 | 1 | 0 | 38953.5731 | 1 | 0 |  | 78 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5752 | 1 | 0 | 38953.5752 | 1 | 0 |  | 262.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5774 | 1 | 0 | 38953.5774 | 1 | 0 |  | 447.5 | 622.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5795 | 1 | 0 | 38953.5795 | 1 | 0 |  | 632.5 | 807.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5816 | 1 | 0 | 38953.5817 | 1 | 0 |  | 817 | 992 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5838 | 1 | 0 | 38953.5838 | 1 | 0 |  | 1002 | 1177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5859 | 1 | 0 | 38953.5859 | 1 | 0 |  | 1186.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5881 | 1 | 0 | 38953.5881 | 1 | 0 |  | 1371.5 | 1546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5902 | 1 | 0 | 38953.5902 | 1 | 0 |  | 1556 | 1731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5923 | 1 | 0 | 38953.5923 | 1 | 0 |  | 1741 | 1916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
38953.5945 | 2 | 0 | 38953.5945 | 1 | 0 |  | 1925.5 | 2100.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121969 | 244038 | 121968.9988
38953.5966 | 30 | 25 | 38953.5966 | 40 | 34 |  | 2110.5 | 2285.5 | 1.8315 | 1.5263 | 2.442 | 2.0757 | 0.018315 | 0.015263 | 0.02442 | 0.020757 | 0.0030525 | 0.003663 | 48830.5519 | 40492.9104 | 9522.0048
38953.5987 | 259 | 2 | 38953.5988 | 2039 | 1 |  | 2295 | 2470 | 15.812 | 0.1221 | 124.4811 | 0.06105 | 0.15812 | 0.001221 | 1.2448 | 0.0006105 | 0.1569 | 1.2442 | 884.0169 | 19.745 | 17976.3392
38953.6009 | 835 | 2 | 38953.6009 | 2068 | 1 |  | 2480 | 2655 | 50.9768 | 0.1221 | 126.2515 | 0.06105 | 0.50977 | 0.001221 | 1.2625 | 0.0006105 | 0.50855 | 1.2619 | 195.4398 | 18.0683 | 12276.142
38953.603 | 1576 | 0 | 38953.603 | 2286 | 0 |  | 2664.5 | 2839.5 | 96.2149 | 0 | 139.5604 | 0 | 0.96215 | 0 | 1.3956 | 0 | 0.96215 | 1.3956 | 54.9099 | 6.797 | 53.9477
38953.6052 | 1978 | 0 | 38953.6052 | 2425 | 0 |  | 2849.5 | 3024.5 | 120.757 | 0 | 148.0464 | 0 | 1.2076 | 0 | 1.4805 | 0 | 1.2076 | 1.4805 | 23.4267 | 0.67546 | 22.2191
38953.6073 | 1855 | 0 | 38953.6073 | 1966 | 0 |  | 3034.5 | 3209.5 | 113.2479 | 0 | 120.0244 | 0 | 1.1325 | 0 | 1.2002 | 0 | 1.1325 | 1.2002 | 31.6108 | 24.1801 | 30.4783
38953.6094 | 2058 | 0 | 38953.6095 | 2350 | 0 |  | 3219 | 3394 | 125.641 | 0 | 143.4676 | 0 | 1.2564 | 0 | 1.4347 | 0 | 1.2564 | 1.4347 | 18.6288 | 3.8885 | 17.3724
38953.6116 | 2278 | 0 | 38953.6116 | 2245 | 0 |  | 3404 | 3579 | 139.072 | 0 | 137.0574 | 0 | 1.3907 | 0 | 1.3706 | 0 | 1.3907 | 1.3706 | 7.1721 | 8.7474 | 5.7814
38953.6137 | 1710 | 0 | 38953.6137 | 2111 | 0 |  | 3588.5 | 3763.5 | 104.3956 | 0 | 128.8767 | 0 | 1.044 | 0 | 1.2888 | 0 | 1.044 | 1.2888 | 42.7708 | 15.6504 | 41.7268
38953.6159 | 1637 | 0 | 38953.6159 | 2018 | 0 |  | 3773.5 | 3948.5 | 99.9389 | 0 | 123.199 | 0 | 0.99939 | 0 | 1.232 | 0 | 0.99939 | 1.232 | 49.1374 | 20.9802 | 48.1381

## B3-C6
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 133.5397 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38953.5709 | 1 | 0 | 38953.5709 | 1 | 0 |  | -109.5 | 65.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.573 | 1 | 0 | 38953.5731 | 1 | 0 |  | 75 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5752 | 1 | 0 | 38953.5752 | 1 | 0 |  | 260 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5773 | 1 | 0 | 38953.5773 | 2 | 0 |  | 444.5 | 619.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 218638 | 109269 | 218637.9994
38953.5795 | 1 | 0 | 38953.5795 | 1 | 0 |  | 629.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5816 | 1 | 0 | 38953.5816 | 1 | 0 |  | 814 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5837 | 1 | 0 | 38953.5838 | 1 | 0 |  | 999 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5859 | 1 | 0 | 38953.5859 | 1 | 0 |  | 1183.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.588 | 1 | 0 | 38953.588 | 1 | 0 |  | 1368.5 | 1543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5902 | 1 | 0 | 38953.5902 | 1 | 0 |  | 1553.5 | 1728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 218638 | 218638 | 218637.9994
38953.5923 | 1 | 1 | 38953.5923 | 2 | 1 |  | 1738 | 1913 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 477807012.44 | 218537.9543 | 218438.0457
38953.5944 | 1 | 1 | 38953.5945 | 1 | 0 |  | 1923 | 2098 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 478025750.44 | 218638 | 218438.0914
38953.5966 | 38 | 31 | 38953.5966 | 37 | 33 |  | 2107.5 | 2282.5 | 2.3199 | 1.8926 | 2.2589 | 2.0147 | 0.023199 | 0.018926 | 0.022589 | 0.020147 | 0.0042735 | 0.002442 | 30953.6205 | 55231.5749 | 6821.1338
38953.5987 | 497 | 149 | 38953.5987 | 266 | 174 |  | 2292.5 | 2467.5 | 30.3419 | 9.0965 | 16.2393 | 10.6227 | 0.30342 | 0.090965 | 0.16239 | 0.10623 | 0.21245 | 0.056166 | 491.9496 | 3392.8348 | 1004.8659
38953.6009 | 864 | 242 | 38953.6009 | 898 | 216 |  | 2477.5 | 2652.5 | 52.7473 | 14.7741 | 54.823 | 13.1868 | 0.52747 | 0.14774 | 0.54823 | 0.13187 | 0.37973 | 0.41636 | 259.6855 | 215.3192 | 305.1373
38953.603 | 1656 | 76 | 38953.603 | 1557 | 86 |  | 2662 | 2837 | 101.0989 | 4.6398 | 95.0549 | 5.2503 | 1.011 | 0.046398 | 0.95055 | 0.052503 | 0.96459 | 0.89805 | 37.1447 | 50.8587 | 202.0018
38953.6051 | 2020 | 9 | 38953.6051 | 1618 | 9 |  | 2846.5 | 3021.5 | 123.3211 | 0.54945 | 98.779 | 0.54945 | 1.2332 | 0.0054945 | 0.98779 | 0.0054945 | 1.2277 | 0.9823 | 8.4227 | 37.9045 | 483.6929
38953.6073 | 2171 | 3 | 38953.6073 | 2063 | 2 |  | 3031.5 | 3206.5 | 132.5397 | 0.18315 | 125.9463 | 0.1221 | 1.3254 | 0.0018315 | 1.2595 | 0.001221 | 1.3236 | 1.2582 | 0.77099 | 6.9039 | 28.8028
38953.6094 | 1909 | 0 | 38953.6094 | 2159 | 0 |  | 3216.5 | 3391.5 | 116.5446 | 0 | 131.8071 | 0 | 1.1654 | 0 | 1.3181 | 0 | 1.1654 | 1.3181 | 14.5825 | 1.3145 | 13.4171
38953.6115 | 1906 | 1 | 38953.6116 | 1890 | 1 |  | 3401 | 3576 | 116.3614 | 0.06105 | 115.3846 | 0.06105 | 1.1636 | 0.0006105 | 1.1538 | 0.0006105 | 1.163 | 1.1532 | 14.8198 | 15.7992 | 3825.3886
38953.6137 | 1727 | 147 | 38953.6137 | 1907 | 156 |  | 3586 | 3761 | 105.4335 | 8.9744 | 116.4225 | 9.5238 | 1.0543 | 0.089744 | 1.1642 | 0.095238 | 0.96459 | 1.069 | 57.1915 | 18.9673 | 33.9884
38953.6158 | 1624 | 25 | 38953.6158 | 1576 | 28 |  | 3770.5 | 3945.5 | 99.1453 | 1.5263 | 96.2149 | 1.7094 | 0.99145 | 0.015263 | 0.96215 | 0.017094 | 0.97619 | 0.94505 | 36.611 | 41.5475 | 632.1086

## B3-C5
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 134.4554 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38953.5709 | 1 | 0 | 38953.5709 | 1 | 0 |  | -112.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.573 | 1 | 0 | 38953.573 | 1 | 0 |  | 72.5 | 247.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5752 | 1 | 0 | 38953.5752 | 1 | 0 |  | 257 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5773 | 1 | 0 | 38953.5773 | 1 | 0 |  | 442 | 617 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5794 | 1 | 0 | 38953.5794 | 1 | 0 |  | 626.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5816 | 1 | 0 | 38953.5816 | 1 | 0 |  | 811.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5837 | 1 | 0 | 38953.5837 | 1 | 0 |  | 996.5 | 1171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5858 | 1 | 0 | 38953.5859 | 1 | 0 |  | 1181 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.588 | 1 | 0 | 38953.588 | 1 | 0 |  | 1365.5 | 1540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5901 | 1 | 0 | 38953.5901 | 1 | 0 |  | 1550.5 | 1725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220138 | 220138 | 220137.9994
38953.5923 | 2 | 4 | 38953.5923 | 2 | 2 |  | 1735.5 | 1910.5 | 0.1221 | 0.2442 | 0.1221 | 0.1221 | 0.001221 | 0.002442 | 0.001221 | 0.001221 | 0.001221 | 0 | 110018.8182 | 121041603.6088 | 54909.4546
38953.5944 | 1 | 1 | 38953.5944 | 1 | 0 |  | 1920 | 2095 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 484607390.44 | 220138 | 219938.0908
38953.5965 | 36 | 31 | 38953.5966 | 31 | 28 |  | 2105 | 2280 | 2.1978 | 1.8926 | 1.8926 | 1.7094 | 0.021978 | 0.018926 | 0.018926 | 0.017094 | 0.0030525 | 0.0018315 | 43693.8861 | 73959.1549 | 6879.0215
38953.5987 | 483 | 145 | 38953.5987 | 208 | 143 |  | 2289.5 | 2464.5 | 29.4872 | 8.8523 | 12.6984 | 8.7302 | 0.29487 | 0.088523 | 0.12698 | 0.087302 | 0.20635 | 0.039683 | 512.7859 | 5373.7871 | 1065.9433
38953.6008 | 775 | 223 | 38953.6008 | 975 | 242 |  | 2474.5 | 2649.5 | 47.3138 | 13.6142 | 59.5238 | 14.7741 | 0.47314 | 0.13614 | 0.59524 | 0.14774 | 0.337 | 0.4475 | 330.3095 | 186.0413 | 351.2685
38953.603 | 1425 | 71 | 38953.603 | 1475 | 79 |  | 2659 | 2834 | 86.9963 | 4.3346 | 90.0488 | 4.823 | 0.86996 | 0.043346 | 0.90049 | 0.04823 | 0.82662 | 0.85226 | 63.2049 | 57.2285 | 362.1273
38953.6051 | 2047 | 9 | 38953.6051 | 1818 | 11 |  | 2844 | 3019 | 124.9695 | 0.54945 | 110.989 | 0.67155 | 1.2497 | 0.0054945 | 1.1099 | 0.0067155 | 1.2442 | 1.1032 | 7.7729 | 23.0792 | 304.9828
38953.6072 | 2186 | 3 | 38953.6072 | 1955 | 2 |  | 3028.5 | 3203.5 | 133.4554 | 0.18315 | 119.3529 | 0.1221 | 1.3346 | 0.0018315 | 1.1935 | 0.001221 | 1.3327 | 1.1923 | 0.75745 | 14.6469 | 56.9795
38953.6094 | 1917 | 1 | 38953.6094 | 2051 | 1 |  | 3213.5 | 3388.5 | 117.033 | 0.06105 | 125.2137 | 0.06105 | 1.1703 | 0.0006105 | 1.2521 | 0.0006105 | 1.1697 | 1.2515 | 15.0002 | 7.4085 | 1961.5064
38953.6115 | 1895 | 1 | 38953.6115 | 1926 | 1 |  | 3398.5 | 3573.5 | 115.6899 | 0.06105 | 117.5824 | 0.06105 | 1.1569 | 0.0006105 | 1.1758 | 0.0006105 | 1.1563 | 1.1752 | 16.2889 | 14.4033 | 3857.3127
38953.6136 | 1887 | 137 | 38953.6137 | 1666 | 115 |  | 3583 | 3758 | 115.2015 | 8.3639 | 101.7094 | 7.0208 | 1.152 | 0.083639 | 1.0171 | 0.070208 | 1.0684 | 0.94689 | 21.1255 | 53.2845 | 45.2614
38953.6158 | 1622 | 23 | 38953.6158 | 1596 | 29 |  | 3768 | 3943 | 99.0232 | 1.4042 | 97.4359 | 1.7705 | 0.99023 | 0.014042 | 0.97436 | 0.017705 | 0.97619 | 0.95665 | 37.6262 | 40.6987 | 700.993

## B3-B4
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 145.6886 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38953.5708 | 1 | 0 | 38953.5709 | 1 | 0 |  | -115 | 60 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.573 | 1 | 0 | 38953.573 | 1 | 0 |  | 69.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5751 | 1 | 0 | 38953.5751 | 1 | 0 |  | 254.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5773 | 1 | 0 | 38953.5773 | 1 | 0 |  | 439 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5794 | 1 | 0 | 38953.5794 | 1 | 0 |  | 624 | 799 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5815 | 1 | 0 | 38953.5816 | 2 | 0 |  | 808.5 | 983.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 238538 | 119219 | 238537.9994
38953.5837 | 1 | 0 | 38953.5837 | 1 | 0 |  | 993.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5858 | 1 | 0 | 38953.5858 | 1 | 0 |  | 1178.5 | 1353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.588 | 1 | 0 | 38953.588 | 1 | 0 |  | 1363 | 1538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38953.5901 | 5 | 2 | 38953.5901 | 4 | 1 |  | 1547.5 | 1722.5 | 0.30525 | 0.1221 | 0.2442 | 0.06105 | 0.0030525 | 0.001221 | 0.002442 | 0.0006105 | 0.0018315 | 0.0018315 | 79446 | 79446 | 118819.44
38953.5922 | 952 | 924 | 38953.5922 | 407 | 395 |  | 1732.5 | 1907.5 | 58.1197 | 56.4103 | 24.8474 | 24.1148 | 0.5812 | 0.5641 | 0.24847 | 0.24115 | 0.017094 | 0.007326 | 5580.7447 | 40214.2049 | 55.0989
38953.5944 | 246 | 239 | 38953.5944 | 254 | 236 |  | 1917.5 | 2092.5 | 15.0183 | 14.591 | 15.5067 | 14.4078 | 0.15018 | 0.14591 | 0.15507 | 0.14408 | 0.0042735 | 0.010989 | 42426.7648 | 12224.3229 | 789.1013
38953.5965 | 1088 | 1138 | 38953.5965 | 1055 | 1102 |  | 2102 | 2277 | 66.4225 | 69.475 | 64.4078 | 67.2772 | 0.66422 | 0.69475 | 0.64408 | 0.67277 | 0.030525 | 0.028694 | 3627.3115 | 8011.0125 | 13.9194
38953.5986 | 1002 | 873 | 38953.5987 | 1055 | 843 |  | 2286.5 | 2461.5 | 61.1722 | 53.2967 | 64.4078 | 51.4652 | 0.61172 | 0.53297 | 0.64408 | 0.51465 | 0.078755 | 0.12943 | 8307.3117 | 777.137 | 51.8991
38953.6008 | 1464 | 887 | 38953.6008 | 1174 | 701 |  | 2471.5 | 2646.5 | 89.3773 | 54.1514 | 71.6728 | 42.7961 | 0.89377 | 0.54151 | 0.71673 | 0.42796 | 0.35226 | 0.28877 | 177.3221 | 1560.8542 | 3.7486
38953.6029 | 1517 | 412 | 38953.6029 | 1455 | 387 |  | 2656.5 | 2831.5 | 92.6129 | 25.1526 | 88.8278 | 23.6264 | 0.92613 | 0.25153 | 0.88828 | 0.23626 | 0.6746 | 0.65201 | 110.3742 | 129.8318 | 62.712
38953.6051 | 2051 | 142 | 38953.6051 | 2122 | 149 |  | 2841 | 3016 | 125.2137 | 8.6691 | 129.5482 | 9.0965 | 1.2521 | 0.086691 | 1.2955 | 0.090965 | 1.1654 | 1.2045 | 30.0664 | 17.8946 | 20.6705
38953.6072 | 1779 | 104 | 38953.6072 | 1931 | 110 |  | 3026 | 3201 | 108.6081 | 6.3492 | 117.8877 | 6.7155 | 1.0861 | 0.063492 | 1.1789 | 0.067155 | 1.0226 | 1.1117 | 46.2433 | 28.7646 | 108.1245
38953.6093 | 2370 | 57 | 38953.6094 | 1823 | 47 |  | 3210.5 | 3385.5 | 144.6886 | 3.4799 | 111.2943 | 2.8694 | 1.4469 | 0.034799 | 1.1129 | 0.028694 | 1.4121 | 1.0842 | 0.54492 | 8.2255 | 5.4162
38953.6115 | 1930 | 45 | 38953.6115 | 2274 | 52 |  | 3395.5 | 3570.5 | 117.8266 | 2.7473 | 138.8278 | 3.1746 | 1.1783 | 0.027473 | 1.3883 | 0.031746 | 1.1508 | 1.3565 | 43.7636 | 5.3433 | 46.3699
38953.6136 | 1811 | 330 | 38953.6136 | 1925 | 368 |  | 3580.5 | 3755.5 | 110.5617 | 20.1465 | 117.5214 | 22.4664 | 1.1056 | 0.20147 | 1.1752 | 0.22466 | 0.90415 | 0.95055 | 84.9759 | 41.0504 | 21.6405
38953.6158 | 1913 | 263 | 38953.6158 | 1882 | 261 |  | 3765 | 3940 | 116.7888 | 16.0562 | 114.8962 | 15.9341 | 1.1679 | 0.16056 | 1.149 | 0.15934 | 1.0073 | 0.98962 | 41.9115 | 50.526 | 26.8505

## A2-C6
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 139.8889 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38953.5706 | 1 | 0 | 38953.5706 | 1 | 0 |  | -135 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5728 | 1 | 0 | 38953.5728 | 1 | 0 |  | 50 | 225 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5749 | 1 | 0 | 38953.5749 | 1 | 0 |  | 234.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.577 | 1 | 0 | 38953.577 | 1 | 0 |  | 419.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5792 | 1 | 0 | 38953.5792 | 1 | 0 |  | 604.5 | 779.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5813 | 1 | 0 | 38953.5813 | 1 | 0 |  | 789 | 964 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5834 | 1 | 0 | 38953.5835 | 1 | 0 |  | 974 | 1149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5856 | 1 | 0 | 38953.5856 | 1 | 0 |  | 1158.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5877 | 1 | 0 | 38953.5877 | 1 | 0 |  | 1343.5 | 1518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5899 | 1 | 0 | 38953.5899 | 1 | 0 |  | 1528 | 1703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.592 | 1 | 0 | 38953.592 | 1 | 0 |  | 1713 | 1888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229038 | 229038 | 229037.9994
38953.5941 | 2 | 0 | 38953.5942 | 2 | 0 |  | 1897.5 | 2072.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114469 | 114469 | 114468.9988
38953.5963 | 128 | 117 | 38953.5963 | 144 | 137 |  | 2082.5 | 2257.5 | 7.8144 | 7.1429 | 8.7912 | 8.3639 | 0.078144 | 0.071429 | 0.087912 | 0.083639 | 0.0067155 | 0.0042735 | 20303.1901 | 33949.4418 | 1743.906
38953.5984 | 457 | 258 | 38953.5984 | 350 | 279 |  | 2267.5 | 2442.5 | 27.8999 | 15.7509 | 21.3675 | 17.033 | 0.279 | 0.15751 | 0.21368 | 0.17033 | 0.12149 | 0.043346 | 948.122 | 4669.7639 | 598.1901
38953.6006 | 842 | 387 | 38953.6006 | 1057 | 469 |  | 2452 | 2627 | 51.4042 | 23.6264 | 64.5299 | 28.6325 | 0.51404 | 0.23626 | 0.6453 | 0.28632 | 0.27778 | 0.35897 | 481.187 | 251.6407 | 196.4494
38953.6027 | 1619 | 174 | 38953.6027 | 1456 | 180 |  | 2636.5 | 2811.5 | 98.84 | 10.6227 | 88.8889 | 10.989 | 0.9884 | 0.10623 | 0.88889 | 0.10989 | 0.88217 | 0.779 | 53.8395 | 88.7123 | 134.6465
38953.6048 | 2098 | 92 | 38953.6048 | 1476 | 78 |  | 2821.5 | 2996.5 | 128.083 | 5.6166 | 90.1099 | 4.7619 | 1.2808 | 0.056166 | 0.9011 | 0.047619 | 1.2247 | 0.85348 | 9.9866 | 132.1618 | 62.7306
38953.607 | 2177 | 34 | 38953.607 | 1879 | 34 |  | 3006.5 | 3181.5 | 132.906 | 2.0757 | 114.7131 | 2.0757 | 1.3291 | 0.020757 | 1.1471 | 0.020757 | 1.3083 | 1.1264 | 5.6044 | 33.3012 | 59.0603
38953.6091 | 2104 | 7 | 38953.6091 | 2275 | 7 |  | 3191 | 3366 | 128.4493 | 0.42735 | 138.8889 | 0.42735 | 1.2845 | 0.0042735 | 1.3889 | 0.0042735 | 1.2802 | 1.3846 | 16.3498 | 0.73612 | 18.8301
38953.6113 | 2184 | 8 | 38953.6113 | 2152 | 11 |  | 3375.5 | 3550.5 | 133.3333 | 0.4884 | 131.3797 | 0.67155 | 1.3333 | 0.004884 | 1.3138 | 0.0067155 | 1.3284 | 1.3071 | 5.1994 | 7.2239 | 83.6927
38953.6134 | 1775 | 268 | 38953.6134 | 1805 | 258 |  | 3560.5 | 3735.5 | 108.3639 | 16.3614 | 110.1954 | 15.7509 | 1.0836 | 0.16361 | 1.102 | 0.15751 | 0.92002 | 0.94444 | 57.1687 | 44.3897 | 28.4923
38953.6155 | 1615 | 67 | 38953.6155 | 1556 | 70 |  | 3745.5 | 3920.5 | 98.5958 | 4.0904 | 94.9939 | 4.2735 | 0.98596 | 0.040904 | 0.94994 | 0.042735 | 0.94505 | 0.9072 | 47.4301 | 54.9441 | 322.5221

## A2-C5
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 139.5836 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38953.5706 | 1 | 0 | 38953.5706 | 1 | 0 |  | -137.5 | 37.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5727 | 1 | 0 | 38953.5727 | 1 | 0 |  | 47 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5749 | 1 | 0 | 38953.5749 | 1 | 0 |  | 232 | 407 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.577 | 1 | 0 | 38953.577 | 1 | 0 |  | 416.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5791 | 1 | 0 | 38953.5792 | 1 | 0 |  | 601.5 | 776.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5813 | 1 | 0 | 38953.5813 | 1 | 0 |  | 786.5 | 961.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5834 | 1 | 0 | 38953.5834 | 1 | 0 |  | 971 | 1146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5856 | 1 | 0 | 38953.5856 | 1 | 0 |  | 1155.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5877 | 1 | 0 | 38953.5877 | 1 | 0 |  | 1340.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5898 | 1 | 0 | 38953.5898 | 1 | 0 |  | 1525.5 | 1700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.592 | 1 | 0 | 38953.592 | 1 | 0 |  | 1710 | 1885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228538 | 228538 | 228537.9994
38953.5941 | 1 | 0 | 38953.5941 | 2 | 0 |  | 1895 | 2070 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 228538 | 114219 | 228537.9994
38953.5963 | 90 | 81 | 38953.5963 | 110 | 103 |  | 2079.5 | 2254.5 | 5.4945 | 4.9451 | 6.7155 | 6.2882 | 0.054945 | 0.049451 | 0.067155 | 0.062882 | 0.0054945 | 0.0042735 | 25087.8503 | 33028.2863 | 2603.697
38953.5984 | 544 | 357 | 38953.5984 | 373 | 269 |  | 2264.5 | 2439.5 | 33.2112 | 21.7949 | 22.7717 | 16.4225 | 0.33211 | 0.21795 | 0.22772 | 0.16422 | 0.11416 | 0.063492 | 1009.6863 | 2473.4074 | 372.9819
38953.6005 | 894 | 407 | 38953.6005 | 858 | 398 |  | 2449 | 2624 | 54.5788 | 24.8474 | 52.381 | 24.2979 | 0.54579 | 0.24847 | 0.52381 | 0.24298 | 0.29731 | 0.28083 | 359.3348 | 408.9969 | 194.5424
38953.6027 | 1592 | 198 | 38953.6027 | 1451 | 208 |  | 2634 | 2809 | 97.1917 | 12.0879 | 88.5836 | 12.6984 | 0.97192 | 0.12088 | 0.88584 | 0.12698 | 0.85104 | 0.75885 | 58.6764 | 94.02 | 121.485
38953.6048 | 1871 | 71 | 38953.6048 | 1881 | 95 |  | 2818.5 | 2993.5 | 114.2247 | 4.3346 | 114.8352 | 5.7998 | 1.1422 | 0.043346 | 1.1484 | 0.057998 | 1.0989 | 1.0904 | 26.8117 | 28.315 | 107.0334
38953.6069 | 2104 | 31 | 38953.607 | 1907 | 33 |  | 3003.5 | 3178.5 | 128.4493 | 1.8926 | 116.4225 | 2.0147 | 1.2845 | 0.018926 | 1.1642 | 0.020147 | 1.2656 | 1.1441 | 9.3591 | 24.9362 | 97.465
38953.6091 | 1844 | 6 | 38953.6091 | 2270 | 6 |  | 3188.5 | 3363.5 | 112.5763 | 0.3663 | 138.5836 | 0.3663 | 1.1258 | 0.003663 | 1.3858 | 0.003663 | 1.1221 | 1.3822 | 43.6387 | 0.72792 | 52.559
38953.6112 | 2005 | 11 | 38953.6112 | 2259 | 9 |  | 3373 | 3548 | 122.4054 | 0.67155 | 137.9121 | 0.54945 | 1.2241 | 0.0067155 | 1.3791 | 0.0054945 | 1.2173 | 1.3736 | 25.4817 | 1.2363 | 30.017
38953.6134 | 1556 | 238 | 38953.6134 | 1625 | 247 |  | 3557.5 | 3732.5 | 94.9939 | 14.5299 | 99.2063 | 15.0794 | 0.94994 | 0.1453 | 0.99206 | 0.15079 | 0.80464 | 0.84127 | 78.0293 | 62.309 | 79.4203
38953.6155 | 1754 | 70 | 38953.6155 | 1562 | 71 |  | 3742.5 | 3917.5 | 107.0818 | 4.2735 | 95.3602 | 4.3346 | 1.0708 | 0.042735 | 0.9536 | 0.043346 | 1.0281 | 0.91026 | 34.1264 | 56.4621 | 238.3684

## A2-B4
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 144.6508 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38953.5706 | 1 | 0 | 38953.5706 | 1 | 0 |  | -140.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5727 | 1 | 0 | 38953.5727 | 1 | 0 |  | 44.5 | 219.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5748 | 1 | 0 | 38953.5748 | 1 | 0 |  | 229 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.577 | 1 | 0 | 38953.577 | 1 | 0 |  | 414 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5791 | 1 | 0 | 38953.5791 | 1 | 0 |  | 598.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5813 | 1 | 0 | 38953.5813 | 1 | 0 |  | 783.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5834 | 1 | 0 | 38953.5834 | 1 | 0 |  | 968.5 | 1143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5855 | 1 | 0 | 38953.5855 | 1 | 0 |  | 1153 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5877 | 1 | 0 | 38953.5877 | 1 | 0 |  | 1337.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5898 | 1 | 0 | 38953.5898 | 1 | 0 |  | 1522.5 | 1697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5919 | 1 | 0 | 38953.592 | 1 | 0 |  | 1707.5 | 1882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236838 | 236838 | 236837.9994
38953.5941 | 2 | 0 | 38953.5941 | 2 | 1 |  | 1892 | 2067 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 118369 | 236838 | 118368.9988
38953.5962 | 97 | 82 | 38953.5962 | 103 | 95 |  | 2077 | 2252 | 5.9219 | 5.0061 | 6.2882 | 5.7998 | 0.059219 | 0.050061 | 0.062882 | 0.057998 | 0.0091575 | 0.004884 | 15423.9138 | 30692.8155 | 2662.5204
38953.5984 | 463 | 290 | 38953.5984 | 447 | 375 |  | 2261.5 | 2436.5 | 28.2662 | 17.7045 | 27.2894 | 22.8938 | 0.28266 | 0.17705 | 0.27289 | 0.22894 | 0.10562 | 0.043956 | 1140.8826 | 4912.7143 | 546.2532
38953.6005 | 1047 | 494 | 38953.6005 | 886 | 412 |  | 2446.5 | 2621.5 | 63.9194 | 30.1587 | 54.0904 | 25.1526 | 0.63919 | 0.30159 | 0.5409 | 0.25153 | 0.33761 | 0.28938 | 299.9325 | 440.6483 | 136.6721
38953.6026 | 1557 | 312 | 38953.6027 | 1403 | 245 |  | 2631 | 2806 | 95.0549 | 19.0476 | 85.6532 | 14.9573 | 0.95055 | 0.19048 | 0.85653 | 0.14957 | 0.76007 | 0.70696 | 84.1754 | 111.4701 | 84.5385
38953.6048 | 2090 | 70 | 38953.6048 | 2101 | 72 |  | 2816 | 2991 | 127.5946 | 4.2735 | 128.2662 | 4.3956 | 1.2759 | 0.042735 | 1.2827 | 0.043956 | 1.2332 | 1.2387 | 17.4807 | 16.5962 | 42.5756
38953.6069 | 2133 | 30 | 38953.6069 | 1817 | 23 |  | 3000.5 | 3175.5 | 130.2198 | 1.8315 | 110.928 | 1.4042 | 1.3022 | 0.018315 | 1.1093 | 0.014042 | 1.2839 | 1.0952 | 11.7239 | 34.5709 | 176.7281
38953.6091 | 1893 | 7 | 38953.6091 | 1917 | 6 |  | 3185.5 | 3360.5 | 115.5678 | 0.42735 | 117.033 | 0.3663 | 1.1557 | 0.0042735 | 1.1703 | 0.003663 | 1.1514 | 1.1667 | 25.6561 | 23.9657 | 1296.329
38953.6112 | 2283 | 16 | 38953.6112 | 2353 | 15 |  | 3370.5 | 3545.5 | 139.3773 | 0.9768 | 143.6508 | 0.91575 | 1.3938 | 0.009768 | 1.4365 | 0.0091575 | 1.384 | 1.4274 | 427.9538 | 0.71212 | 3.1103
38953.6133 | 1586 | 246 | 38953.6133 | 1931 | 301 |  | 3555 | 3730 | 96.8254 | 15.0183 | 117.8877 | 18.3761 | 0.96825 | 0.15018 | 1.1789 | 0.18376 | 0.81807 | 0.99512 | 144.4748 | 30.8358 | 51.4843
38953.6155 | 1758 | 163 | 38953.6155 | 1830 | 162 |  | 3740 | 3915 | 107.326 | 9.9512 | 111.7216 | 9.8901 | 1.0733 | 0.099512 | 1.1172 | 0.098901 | 0.97375 | 1.0183 | 51.5544 | 39.8428 | 78.3734

## A2-B3
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 138.79 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38953.5705 | 1 | 0 | 38953.5705 | 1 | 0 |  | -143.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5727 | 1 | 0 | 38953.5727 | 1 | 0 |  | 41.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5748 | 1 | 0 | 38953.5748 | 1 | 0 |  | 226.5 | 401.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5769 | 1 | 0 | 38953.577 | 1 | 0 |  | 411 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5791 | 1 | 0 | 38953.5791 | 1 | 0 |  | 596 | 771 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5812 | 1 | 0 | 38953.5812 | 1 | 0 |  | 780.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5834 | 1 | 0 | 38953.5834 | 1 | 0 |  | 965.5 | 1140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5855 | 1 | 0 | 38953.5855 | 1 | 0 |  | 1150.5 | 1325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5876 | 1 | 0 | 38953.5877 | 1 | 0 |  | 1335 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5898 | 1 | 0 | 38953.5898 | 1 | 0 |  | 1519.5 | 1694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5919 | 1 | 0 | 38953.5919 | 1 | 0 |  | 1704.5 | 1879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227238 | 227238 | 227237.9994
38953.5941 | 2 | 0 | 38953.5941 | 2 | 1 |  | 1889.5 | 2064.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 113569 | 227238 | 113568.9988
38953.5962 | 76 | 74 | 38953.5962 | 81 | 74 |  | 2074 | 2249 | 4.6398 | 4.5177 | 4.9451 | 4.5177 | 0.046398 | 0.045177 | 0.049451 | 0.045177 | 0.001221 | 0.0042735 | 124445.6849 | 31588.0489 | 2860.3772
38953.5983 | 356 | 276 | 38953.5983 | 625 | 347 |  | 2258.5 | 2433.5 | 21.7338 | 16.8498 | 38.1563 | 21.1844 | 0.21734 | 0.1685 | 0.38156 | 0.21184 | 0.04884 | 0.16972 | 5557.9714 | 606.5646 | 510.5347
38953.6005 | 849 | 395 | 38953.6005 | 840 | 440 |  | 2443.5 | 2618.5 | 51.8315 | 24.1148 | 51.2821 | 26.862 | 0.51832 | 0.24115 | 0.51282 | 0.26862 | 0.27717 | 0.2442 | 379.0686 | 504.8428 | 217.5165
38953.6026 | 1617 | 321 | 38953.6026 | 1543 | 324 |  | 2628.5 | 2803.5 | 98.7179 | 19.5971 | 94.2002 | 19.7802 | 0.98718 | 0.19597 | 0.942 | 0.1978 | 0.79121 | 0.7442 | 67.6068 | 98.7322 | 51.9066
38953.6047 | 1793 | 75 | 38953.6048 | 1718 | 60 |  | 2813 | 2988 | 109.4628 | 4.5788 | 104.884 | 3.663 | 1.0946 | 0.045788 | 1.0488 | 0.03663 | 1.0488 | 1.0122 | 31.6095 | 37.8277 | 148.3455
38953.6069 | 2095 | 32 | 38953.6069 | 1778 | 32 |  | 2998 | 3173 | 127.8999 | 1.9536 | 108.547 | 1.9536 | 1.279 | 0.019536 | 1.0855 | 0.019536 | 1.2595 | 1.0659 | 9.0407 | 35.5865 | 120.0606
38953.609 | 2257 | 7 | 38953.609 | 2006 | 7 |  | 3182.5 | 3357.5 | 137.79 | 0.42735 | 122.4664 | 0.42735 | 1.3779 | 0.0042735 | 1.2247 | 0.0042735 | 1.3736 | 1.2204 | 0.737 | 25.4842 | 27.2136
38953.6112 | 1904 | 13 | 38953.6112 | 1911 | 16 |  | 3367.5 | 3542.5 | 116.2393 | 0.79365 | 116.6667 | 0.9768 | 1.1624 | 0.0079365 | 1.1667 | 0.009768 | 1.1545 | 1.1569 | 20.2305 | 19.9558 | 456.056
38953.6133 | 1844 | 302 | 38953.6133 | 1549 | 242 |  | 3552.5 | 3727.5 | 112.5763 | 18.4371 | 94.5665 | 14.7741 | 1.1258 | 0.18437 | 0.94567 | 0.14774 | 0.94139 | 0.79792 | 32.9443 | 126.5453 | 23.5605
38953.6154 | 1580 | 144 | 38953.6155 | 2139 | 176 |  | 3737 | 3912 | 96.4591 | 8.7912 | 130.5861 | 10.7448 | 0.96459 | 0.087912 | 1.3059 | 0.10745 | 0.87668 | 1.1984 | 75.6195 | 27.7421 | 82.8544

## A1-C6
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 129 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38953.5703 | 1 | 0 | 38953.5703 | 1 | 0 |  | -162.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5724 | 1 | 0 | 38953.5725 | 1 | 0 |  | 22 | 197 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5746 | 1 | 0 | 38953.5746 | 1 | 0 |  | 206.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5767 | 1 | 0 | 38953.5767 | 1 | 0 |  | 391.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5789 | 1 | 0 | 38953.5789 | 1 | 0 |  | 576.5 | 751.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.581 | 1 | 0 | 38953.581 | 1 | 0 |  | 761 | 936 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5831 | 1 | 0 | 38953.5831 | 1 | 0 |  | 946 | 1121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5853 | 1 | 0 | 38953.5853 | 1 | 0 |  | 1130.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5874 | 1 | 0 | 38953.5874 | 1 | 0 |  | 1315.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5895 | 1 | 0 | 38953.5896 | 1 | 0 |  | 1500 | 1675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5917 | 1 | 0 | 38953.5917 | 1 | 0 |  | 1685 | 1860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38953.5938 | 1 | 1 | 38953.5938 | 1 | 0 |  | 1869.5 | 2044.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38953.596 | 54 | 54 | 38953.596 | 67 | 65 |  | 2054.5 | 2229.5 | 3.2967 | 3.2967 | 4.0904 | 3.9683 | 0.032967 | 0.032967 | 0.040904 | 0.039683 | 0 | 0.001221 | 3897487.13 | 102215.7653 | 3709.371
38953.5981 | 398 | 375 | 38953.5981 | 395 | 377 |  | 2239 | 2414 | 24.2979 | 22.8938 | 24.1148 | 23.0159 | 0.24298 | 0.22894 | 0.24115 | 0.23016 | 0.014042 | 0.010989 | 8561.2998 | 12635.7862 | 354.5329
38953.6002 | 919 | 481 | 38953.6003 | 772 | 396 |  | 2424 | 2599 | 56.105 | 29.3651 | 47.1306 | 24.1758 | 0.56105 | 0.29365 | 0.47131 | 0.24176 | 0.2674 | 0.22955 | 347.0335 | 512.0547 | 124.0174
38953.6024 | 1299 | 312 | 38953.6024 | 1342 | 318 |  | 2608.5 | 2783.5 | 79.304 | 19.0476 | 81.9292 | 19.4139 | 0.79304 | 0.19048 | 0.81929 | 0.19414 | 0.60256 | 0.62515 | 119.6827 | 101.6778 | 81.1212
38953.6045 | 2014 | 95 | 38953.6045 | 1506 | 77 |  | 2793.5 | 2968.5 | 122.9548 | 5.7998 | 91.9414 | 4.7009 | 1.2295 | 0.057998 | 0.91941 | 0.047009 | 1.1716 | 0.87241 | 5.1298 | 842.8641 | 3.7828
38953.6067 | 1871 | 40 | 38953.6067 | 1892 | 42 |  | 2978.5 | 3153.5 | 114.2247 | 2.442 | 115.5067 | 2.5641 | 1.1422 | 0.02442 | 1.1551 | 0.025641 | 1.1178 | 1.1294 | 15.6677 | 13.9715 | 61.913
38953.6088 | 2014 | 8 | 38953.6088 | 2074 | 10 |  | 3163 | 3338 | 122.9548 | 0.4884 | 126.6178 | 0.6105 | 1.2295 | 0.004884 | 1.2662 | 0.006105 | 1.2247 | 1.2601 | 6.1263 | 2.0529 | 22.8865
38953.6109 | 2011 | 5 | 38953.6109 | 1882 | 5 |  | 3348 | 3523 | 122.7717 | 0.30525 | 114.8962 | 0.30525 | 1.2277 | 0.0030525 | 1.149 | 0.0030525 | 1.2247 | 1.1459 | 5.1854 | 12.9745 | 222.8437
38953.6131 | 1952 | 169 | 38953.6131 | 1720 | 151 |  | 3532.5 | 3707.5 | 119.1697 | 10.3175 | 105.0061 | 9.2186 | 1.1917 | 0.10317 | 1.0501 | 0.092186 | 1.0885 | 0.95788 | 8.6698 | 227.6017 | 3.2805
38953.6152 | 1776 | 74 | 38953.6152 | 1541 | 71 |  | 3717.5 | 3892.5 | 108.4249 | 4.5177 | 94.0781 | 4.3346 | 1.0842 | 0.045177 | 0.94078 | 0.043346 | 1.0391 | 0.89744 | 21.6846 | 50.0639 | 118.5784

## A1-C5
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 136.2869 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38953.5703 | 1 | 0 | 38953.5703 | 1 | 0 |  | -165.5 | 9.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5724 | 1 | 0 | 38953.5724 | 1 | 0 |  | 19 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5745 | 1 | 0 | 38953.5746 | 1 | 0 |  | 204 | 379 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5767 | 1 | 0 | 38953.5767 | 1 | 0 |  | 388.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5788 | 1 | 0 | 38953.5788 | 1 | 0 |  | 573.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5809 | 1 | 0 | 38953.581 | 1 | 0 |  | 758 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5831 | 1 | 0 | 38953.5831 | 1 | 0 |  | 943 | 1118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5852 | 1 | 0 | 38953.5852 | 1 | 0 |  | 1127.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223138 | 223138 | 223137.9994
38953.5874 | 1 | 1 | 38953.5874 | 2 | 1 |  | 1312.5 | 1487.5 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 497682432.44 | 223037.9552 | 222938.0448
38953.5895 | 1 | 1 | 38953.5895 | 1 | 0 |  | 1497.5 | 1672.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 497905670.44 | 223138 | 222938.0896
38953.5916 | 1 | 1 | 38953.5917 | 1 | 0 |  | 1682 | 1857 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 497905670.44 | 223138 | 222938.0896
38953.5938 | 1 | 2 | 38953.5938 | 2 | 1 |  | 1867 | 2042 | 0.06105 | 0.1221 | 0.1221 | 0.06105 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 223338.1795 | 223137.9103 | 111419.0672
38953.5959 | 95 | 87 | 38953.5959 | 52 | 49 |  | 2051.5 | 2226.5 | 5.7998 | 5.3114 | 3.1746 | 2.9915 | 0.057998 | 0.053114 | 0.031746 | 0.029915 | 0.004884 | 0.0018315 | 27098.2817 | 77341.0187 | 2353.7153
38953.5981 | 420 | 336 | 38953.5981 | 368 | 353 |  | 2236.5 | 2411.5 | 25.641 | 20.5128 | 22.4664 | 21.5507 | 0.25641 | 0.20513 | 0.22466 | 0.21551 | 0.051282 | 0.0091575 | 2151.0865 | 132196.2869 | 439.0667
38953.6002 | 761 | 417 | 38953.6002 | 799 | 383 |  | 2421 | 2596 | 46.4591 | 25.4579 | 48.779 | 23.3822 | 0.46459 | 0.25458 | 0.48779 | 0.23382 | 0.21001 | 0.25397 | 609.9093 | 405.8224 | 202.8612
38953.6023 | 1420 | 368 | 38953.6024 | 1186 | 302 |  | 2606 | 2781 | 86.6911 | 22.4664 | 72.4054 | 18.4371 | 0.86691 | 0.22466 | 0.72405 | 0.18437 | 0.64225 | 0.53968 | 95.2858 | 184.5276 | 78.3148
38953.6045 | 2068 | 97 | 38953.6045 | 1760 | 99 |  | 2790.5 | 2965.5 | 126.2515 | 5.9219 | 107.4481 | 6.044 | 1.2625 | 0.059219 | 1.0745 | 0.06044 | 1.2033 | 1.014 | 8.8379 | 87.3446 | 32.3858
38953.6066 | 2148 | 41 | 38953.6066 | 1638 | 34 |  | 2975.5 | 3150.5 | 131.1355 | 2.5031 | 100 | 2.0757 | 1.3114 | 0.025031 | 1 | 0.020757 | 1.2863 | 0.97924 | 4.1092 | 76.5369 | 45.8713
38953.6088 | 2146 | 9 | 38953.6088 | 2216 | 10 |  | 3160.5 | 3335.5 | 131.0134 | 0.54945 | 135.2869 | 0.6105 | 1.3101 | 0.0054945 | 1.3529 | 0.006105 | 1.3046 | 1.3468 | 8.7452 | 0.78311 | 6.6807
38953.6109 | 1910 | 5 | 38953.6109 | 1804 | 3 |  | 3345 | 3520 | 116.6056 | 0.30525 | 110.1343 | 0.18315 | 1.1661 | 0.0030525 | 1.1013 | 0.0018315 | 1.163 | 1.0995 | 17.1098 | 24.0195 | 1229.3734
38953.613 | 1779 | 180 | 38953.6131 | 2029 | 184 |  | 3530 | 3705 | 108.6081 | 10.989 | 123.8706 | 11.2332 | 1.0861 | 0.10989 | 1.2387 | 0.11233 | 0.97619 | 1.1264 | 856.9277 | 11.6423 | 15.8381
38953.6152 | 1846 | 75 | 38953.6152 | 1914 | 92 |  | 3714.5 | 3889.5 | 112.6984 | 4.5788 | 116.8498 | 5.6166 | 1.127 | 0.045788 | 1.1685 | 0.056166 | 1.0812 | 1.1123 | 27.1806 | 21.4611 | 73.3574

## A1-B4
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 138.9121 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38953.5702 | 1 | 0 | 38953.5702 | 1 | 0 |  | -168.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5724 | 1 | 0 | 38953.5724 | 1 | 0 |  | 16.5 | 191.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5745 | 1 | 0 | 38953.5745 | 1 | 0 |  | 201 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5766 | 1 | 0 | 38953.5767 | 1 | 0 |  | 386 | 561 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5788 | 1 | 0 | 38953.5788 | 1 | 0 |  | 570.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5809 | 1 | 0 | 38953.5809 | 1 | 0 |  | 755.5 | 930.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5831 | 1 | 0 | 38953.5831 | 1 | 0 |  | 940.5 | 1115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5852 | 1 | 0 | 38953.5852 | 1 | 0 |  | 1125 | 1300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 227438 | 227438 | 227437.9994
38953.5873 | 2 | 2 | 38953.5873 | 1 | 0 |  | 1309.5 | 1484.5 | 0.1221 | 0.1221 | 0.06105 | 0 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0 | 0.0006105 | 258526500.22 | 227438 | 113519.0879
38953.5895 | 1 | 1 | 38953.5895 | 1 | 0 |  | 1494.5 | 1669.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 517280438.44 | 227438 | 227238.0879
38953.5916 | 1 | 2 | 38953.5916 | 2 | 1 |  | 1679.5 | 1854.5 | 0.06105 | 0.1221 | 0.1221 | 0.06105 | 0.0006105 | 0.001221 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 227638.1761 | 227437.912 | 113569.0659
38953.5938 | 2 | 3 | 38953.5938 | 2 | 2 |  | 1864 | 2039 | 0.1221 | 0.18315 | 0.1221 | 0.1221 | 0.001221 | 0.0018315 | 0.001221 | 0.001221 | 0.0006105 | 0 | 227337.7361 | 258412531.2466 | 75679.304
38953.5959 | 58 | 58 | 38953.5959 | 72 | 66 |  | 2049 | 2224 | 3.5409 | 3.5409 | 4.3956 | 4.0293 | 0.035409 | 0.035409 | 0.043956 | 0.040293 | 0 | 0.003663 | 1402845.6162 | 36694.2273 | 3712.9503
38953.598 | 360 | 364 | 38953.598 | 326 | 306 |  | 2233.5 | 2408.5 | 21.978 | 22.2222 | 19.9023 | 18.6813 | 0.21978 | 0.22222 | 0.19902 | 0.18681 | 0.002442 | 0.01221 | 699957.3861 | 9768.2519 | 421.8844
38953.6002 | 868 | 180 | 38953.6002 | 824 | 366 |  | 2418.5 | 2593.5 | 52.9915 | 10.989 | 50.3053 | 22.3443 | 0.52991 | 0.10989 | 0.50305 | 0.22344 | 0.42002 | 0.27961 | 215.7781 | 503.2851 | 568.8503
38953.6023 | 1169 | 294 | 38953.6023 | 1240 | 358 |  | 2603 | 2778 | 71.3675 | 17.9487 | 75.7021 | 21.8559 | 0.71368 | 0.17949 | 0.75702 | 0.21856 | 0.53419 | 0.53846 | 160.871 | 157.0039 | 168.8039
38953.6044 | 1935 | 85 | 38953.6045 | 1684 | 70 |  | 2788 | 2963 | 118.1319 | 5.1893 | 102.8083 | 4.2735 | 1.1813 | 0.051893 | 1.0281 | 0.042735 | 1.1294 | 0.98535 | 20.415 | 46.5245 | 95.398
38953.6066 | 2128 | 37 | 38953.6066 | 2162 | 36 |  | 2972.5 | 3147.5 | 129.9145 | 2.2589 | 131.9902 | 2.1978 | 1.2991 | 0.022589 | 1.3199 | 0.021978 | 1.2766 | 1.2979 | 9.7073 | 6.4599 | 18.102
38953.6087 | 1859 | 7 | 38953.6087 | 2093 | 9 |  | 3157.5 | 3332.5 | 113.4921 | 0.42735 | 127.7778 | 0.54945 | 1.1349 | 0.0042735 | 1.2778 | 0.0054945 | 1.1306 | 1.2723 | 23.4781 | 8.9154 | 478.72
38953.6109 | 2047 | 8 | 38953.6109 | 2259 | 9 |  | 3342.5 | 3517.5 | 124.9695 | 0.4884 | 137.9121 | 0.54945 | 1.2497 | 0.004884 | 1.3791 | 0.0054945 | 1.2448 | 1.3736 | 23.8256 | 0.74043 | 20.2471
38953.613 | 1909 | 284 | 38953.613 | 2026 | 287 |  | 3527 | 3702 | 116.5446 | 17.3382 | 123.6874 | 17.5214 | 1.1654 | 0.17338 | 1.2369 | 0.17521 | 0.99206 | 1.0617 | 11.1243 | 17.0211 | 4.2192
38953.6151 | 1799 | 139 | 38953.6152 | 1708 | 121 |  | 3711.5 | 3886.5 | 109.8291 | 8.486 | 104.2735 | 7.3871 | 1.0983 | 0.08486 | 1.0427 | 0.073871 | 1.0134 | 0.96886 | 35.1427 | 45.6574 | 76.0822

## A1-B3
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 136.4701 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38953.5702 | 1 | 0 | 38953.5702 | 1 | 0 |  | -171 | 4 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5723 | 1 | 0 | 38953.5723 | 1 | 0 |  | 13.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5745 | 1 | 0 | 38953.5745 | 1 | 0 |  | 198.5 | 373.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5766 | 1 | 0 | 38953.5766 | 1 | 0 |  | 383 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5788 | 1 | 0 | 38953.5788 | 1 | 0 |  | 568 | 743 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5809 | 1 | 0 | 38953.5809 | 1 | 0 |  | 752.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.583 | 1 | 0 | 38953.583 | 1 | 0 |  | 937.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5852 | 1 | 0 | 38953.5852 | 1 | 0 |  | 1122 | 1297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38953.5873 | 2 | 7 | 38953.5873 | 2 | 3 |  | 1307 | 1482 | 0.1221 | 0.42735 | 0.1221 | 0.18315 | 0.001221 | 0.0042735 | 0.001221 | 0.0018315 | 0.0030525 | 0.0006105 | 44695.4294 | 224847.1959 | 31791.2895
38953.5894 | 2 | 7 | 38953.5895 | 1 | 3 |  | 1491.5 | 1666.5 | 0.1221 | 0.42735 | 0.06105 | 0.18315 | 0.001221 | 0.0042735 | 0.0006105 | 0.0018315 | 0.0030525 | 0.001221 | 44723.457 | 112094.9603 | 31777.0802
38953.5916 | 2 | 6 | 38953.5916 | 2 | 3 |  | 1676.5 | 1851.5 | 0.1221 | 0.3663 | 0.1221 | 0.18315 | 0.001221 | 0.003663 | 0.001221 | 0.0018315 | 0.002442 | 0.0006105 | 55871.8236 | 224543.6721 | 37106.4747
38953.5937 | 2 | 7 | 38953.5937 | 2 | 4 |  | 1861.5 | 2036.5 | 0.1221 | 0.42735 | 0.1221 | 0.2442 | 0.001221 | 0.0042735 | 0.001221 | 0.002442 | 0.0030525 | 0.001221 | 44723.4192 | 112170.6192 | 31777.0993
38953.5959 | 47 | 45 | 38953.5959 | 54 | 49 |  | 2046 | 2221 | 2.8694 | 2.7473 | 3.2967 | 2.9915 | 0.028694 | 0.027473 | 0.032967 | 0.029915 | 0.001221 | 0.0030525 | 115315.6144 | 44001.5434 | 4752.2664
38953.598 | 300 | 284 | 38953.598 | 287 | 296 |  | 2231 | 2406 | 18.315 | 17.3382 | 17.5214 | 18.0708 | 0.18315 | 0.17338 | 0.17521 | 0.18071 | 0.009768 | 0.0054945 | 12882.736 | 29070.0961 | 579.4784
38953.6001 | 824 | 142 | 38953.6002 | 1406 | 147 |  | 2415.5 | 2590.5 | 50.3053 | 8.6691 | 85.8364 | 8.9744 | 0.50305 | 0.086691 | 0.85836 | 0.089744 | 0.41636 | 0.76862 | 297.1873 | 68.5701 | 363.6281
38953.6023 | 1486 | 312 | 38953.6023 | 1478 | 358 |  | 2600.5 | 2775.5 | 90.7204 | 19.0476 | 90.232 | 21.8559 | 0.9072 | 0.19048 | 0.90232 | 0.21856 | 0.71673 | 0.68376 | 84.4634 | 108.7959 | 73.0457
38953.6044 | 1678 | 73 | 38953.6044 | 1806 | 71 |  | 2785 | 2960 | 102.442 | 4.4567 | 110.2564 | 4.3346 | 1.0244 | 0.044567 | 1.1026 | 0.043346 | 0.97985 | 1.0592 | 41.6258 | 27.4464 | 142.8963
38953.6066 | 2211 | 37 | 38953.6066 | 1892 | 41 |  | 2970 | 3145 | 134.9817 | 2.2589 | 115.5067 | 2.5031 | 1.3498 | 0.022589 | 1.1551 | 0.025031 | 1.3272 | 1.13 | 1.011 | 15.5763 | 4.5968
38953.6087 | 1826 | 7 | 38953.6087 | 2174 | 10 |  | 3154.5 | 3329.5 | 111.4774 | 0.42735 | 132.7228 | 0.6105 | 1.1148 | 0.0042735 | 1.3272 | 0.006105 | 1.1105 | 1.3211 | 25.966 | 2.8878 | 161.3402
38953.6108 | 2219 | 8 | 38953.6108 | 1868 | 7 |  | 3339.5 | 3514.5 | 135.4701 | 0.4884 | 114.0415 | 0.42735 | 1.3547 | 0.004884 | 1.1404 | 0.0042735 | 1.3498 | 1.1361 | 0.74765 | 39.7282 | 29.783
38953.613 | 1661 | 239 | 38953.613 | 1679 | 238 |  | 3524 | 3699 | 101.4042 | 14.591 | 102.5031 | 14.5299 | 1.014 | 0.14591 | 1.025 | 0.1453 | 0.86813 | 0.87973 | 58.7975 | 53.6932 | 49.0234
38953.6151 | 1721 | 124 | 38953.6151 | 1738 | 125 |  | 3709 | 3884 | 105.0672 | 7.5702 | 106.105 | 7.6313 | 1.0507 | 0.075702 | 1.0611 | 0.076313 | 0.97497 | 0.98474 | 40.441 | 38.1453 | 86.9303

## A1-A2
Penlight Test 34 |  |  | 2006-08-24 | 13:43 |  |  | Vs = |  | 139.2784 |  | R = | 100
XLPE | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38953.5702 | 1 | 0 | 38953.5702 | 1 | 0 |  | -174 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5723 | 1 | 0 | 38953.5723 | 1 | 0 |  | 10.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5744 | 1 | 0 | 38953.5745 | 1 | 0 |  | 195.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5766 | 1 | 0 | 38953.5766 | 1 | 0 |  | 380.5 | 555.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5787 | 1 | 0 | 38953.5787 | 1 | 0 |  | 565 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5809 | 1 | 0 | 38953.5809 | 1 | 0 |  | 750 | 925 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.583 | 1 | 0 | 38953.583 | 1 | 0 |  | 934.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5851 | 1 | 0 | 38953.5852 | 1 | 0 |  | 1119.5 | 1294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228038 | 228038 | 228037.9994
38953.5873 | 1106 | 920 | 38953.5873 | 977 | 950 |  | 1304 | 1479 | 67.5214 | 56.1661 | 59.6459 | 57.9976 | 0.67521 | 0.56166 | 0.59646 | 0.57998 | 0.11355 | 0.016484 | 302.6716 | 454.6914 | 22.7543
38953.5894 | 1159 | 1137 | 38953.5894 | 932 | 1034 |  | 1489 | 1664 | 70.757 | 69.4139 | 56.8987 | 63.1258 | 0.70757 | 0.69414 | 0.56899 | 0.63126 | 0.013431 | 0.062271 | 392.7088 | 431.0007 | 1.0437
38953.5916 | 1048 | 1022 | 38953.5916 | 1006 | 981 |  | 1673.5 | 1848.5 | 63.9805 | 62.3932 | 61.4164 | 59.8901 | 0.6398 | 0.62393 | 0.61416 | 0.5989 | 0.015873 | 0.015263 | 7496.1259 | 10705.5679 | 20.4916
38953.5937 | 1139 | 1180 | 38953.5937 | 938 | 973 |  | 1858.5 | 2033.5 | 69.536 | 72.0391 | 57.265 | 59.4017 | 0.69536 | 0.72039 | 0.57265 | 0.59402 | 0.025031 | 0.021368 | 2805.1544 | 428029.2851 | 3.1874
38953.5958 | 1170 | 904 | 38953.5958 | 1166 | 1164 |  | 2043.5 | 2218.5 | 71.4286 | 55.1893 | 71.1844 | 71.0623 | 0.71429 | 0.55189 | 0.71184 | 0.71062 | 0.16239 | 0.001221 | 63.5354 | 60.948 | 8.6871
38953.598 | 1182 | 1143 | 38953.598 | 1035 | 1000 |  | 2228 | 2403 | 72.1612 | 69.7802 | 63.1868 | 61.0501 | 0.72161 | 0.6978 | 0.63187 | 0.6105 | 0.02381 | 0.021368 | 2641.2134 | 43558.6054 | 3.8075
38953.6001 | 1413 | 795 | 38953.6001 | 1532 | 815 |  | 2412.5 | 2587.5 | 86.2637 | 48.5348 | 93.5287 | 49.7558 | 0.86264 | 0.48535 | 0.93529 | 0.49756 | 0.37729 | 0.43773 | 2.6395 | 2.4627 | 0.22185
38953.6022 | 1630 | 709 | 38953.6023 | 1351 | 553 |  | 2597.5 | 2772.5 | 99.5116 | 43.2845 | 82.4786 | 33.7607 | 0.99512 | 0.43284 | 0.82479 | 0.33761 | 0.56227 | 0.48718 | 73.4989 | 2039.9412 | 7.7472
38953.6044 | 1815 | 233 | 38953.6044 | 1774 | 223 |  | 2782.5 | 2957.5 | 110.8059 | 14.2247 | 108.3028 | 13.6142 | 1.1081 | 0.14225 | 1.083 | 0.13614 | 0.96581 | 0.94689 | 41.8482 | 49.8349 | 33.3141
38953.6065 | 2265 | 147 | 38953.6065 | 2199 | 141 |  | 2967 | 3142 | 138.2784 | 8.9744 | 134.2491 | 8.6081 | 1.3828 | 0.089744 | 1.3425 | 0.086081 | 1.293 | 1.2564 | 15.1334 | 7.3143 | 6.0563
38953.6087 | 2238 | 77 | 38953.6087 | 2152 | 75 |  | 3152 | 3327 | 136.63 | 4.7009 | 131.3797 | 4.5788 | 1.3663 | 0.047009 | 1.3138 | 0.045788 | 1.3193 | 1.268 | 0.1358 | 0.25853 | 0.11259
38953.6108 | 2131 | 60 | 38953.6108 | 1847 | 53 |  | 3336.5 | 3511.5 | 130.0977 | 3.663 | 112.7595 | 3.2357 | 1.301 | 0.03663 | 1.1276 | 0.032357 | 1.2643 | 1.0952 | 7.8466 | 38.8342 | 42.1346
38953.6129 | 2078 | 268 | 38953.613 | 1687 | 278 |  | 3521.5 | 3696.5 | 126.862 | 16.3614 | 102.9915 | 16.9719 | 1.2686 | 0.16361 | 1.0299 | 0.16972 | 1.105 | 0.8602 | 6.6428 | 21.4115 | 4.2523
38953.6151 | 1783 | 237 | 38953.6151 | 2033 | 279 |  | 3706 | 3881 | 108.8523 | 14.4689 | 124.1148 | 17.033 | 1.0885 | 0.14469 | 1.2411 | 0.17033 | 0.94383 | 1.0708 | 181.8929 | 18.632 | 17.3214

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -175 | 18.9 | 25.9 | 21.9 | 25.8 | 27.5 | 23.6 | 23.5 | 26.9
1 | -174 | 18.9 | 25.9 | 21.9 | 25.8 | 27.5 | 23.6 | 23.5 | 26.9
2 | -173 | 18.9 | 25.9 | 21.9 | 25.8 | 27.5 | 23.6 | 23.5 | 26.9
3 | -172 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
4 | -171 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
5 | -170 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
6 | -169 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
7 | -168 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
8 | -167 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
9 | -166 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
10 | -165 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
11 | -164 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
12 | -163 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
13 | -162 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
14 | -161 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
15 | -160 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
16 | -159 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 27
17 | -158 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
18 | -157 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
19 | -156 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
20 | -155 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
21 | -154 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
22 | -153 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
23 | -152 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
24 | -151 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
25 | -150 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
26 | -149 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
27 | -148 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
28 | -147 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
29 | -146 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 27
30 | -145 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 26.9
31 | -144 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 26.9
32 | -143 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 26.9
33 | -142 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
34 | -141 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
35 | -140 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
36 | -139 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27
37 | -138 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 27
38 | -137 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.5 | 27
39 | -136 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
40 | -135 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
41 | -134 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
42 | -133 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
43 | -132 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
44 | -131 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
45 | -130 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
46 | -129 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
47 | -128 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
48 | -127 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
49 | -126 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
50 | -125 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.5 | 27.1
51 | -124 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
52 | -123 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
53 | -122 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
54 | -121 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
55 | -120 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
56 | -119 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
57 | -118 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
58 | -117 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
59 | -116 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
60 | -115 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
61 | -114 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
62 | -113 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
63 | -112 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
64 | -111 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
65 | -110 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
66 | -109 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
67 | -108 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
68 | -107 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
69 | -106 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27
70 | -105 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
71 | -104 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
72 | -103 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
73 | -102 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
74 | -101 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27
75 | -100 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
76 | -99 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
77 | -98 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
78 | -97 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
79 | -96 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
80 | -95 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
81 | -94 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
82 | -93 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
83 | -92 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
84 | -91 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
85 | -90 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
86 | -89 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
87 | -88 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
88 | -87 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
89 | -86 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
90 | -85 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
91 | -84 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
92 | -83 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
93 | -82 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
94 | -81 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
95 | -80 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
96 | -79 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
97 | -78 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
98 | -77 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
99 | -76 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
100 | -75 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
101 | -74 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
102 | -73 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27
103 | -72 | 18.9 | 25.9 | 21.9 | 25.8 | 27.7 | 23.6 | 23.6 | 27
104 | -71 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
105 | -70 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
106 | -69 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
107 | -68 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
108 | -67 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
109 | -66 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
110 | -65 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
111 | -64 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
112 | -63 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
113 | -62 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.1
114 | -61 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
115 | -60 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
116 | -59 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
117 | -58 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
118 | -57 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
119 | -56 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
120 | -55 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
121 | -54 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
122 | -53 | 18.9 | 25.9 | 21.9 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
123 | -52 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
124 | -51 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
125 | -50 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
126 | -49 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
127 | -48 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
128 | -47 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
129 | -46 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
130 | -45 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
131 | -44 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.1
132 | -43 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
133 | -42 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
134 | -41 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
135 | -40 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
136 | -39 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
137 | -38 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
138 | -37 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
139 | -36 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
140 | -35 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.2
141 | -34 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
142 | -33 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
143 | -32 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
144 | -31 | 18.9 | 25.9 | 21.8 | 25.8 | 27.6 | 23.6 | 23.6 | 27.3
145 | -30 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.3
146 | -29 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
147 | -28 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
148 | -27 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
149 | -26 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
150 | -25 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
151 | -24 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
152 | -23 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
153 | -22 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.2
154 | -21 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.2
155 | -20 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
156 | -19 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.3
157 | -18 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
158 | -17 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.2
159 | -16 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.3
160 | -15 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.3
161 | -14 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
162 | -13 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
163 | -12 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
164 | -11 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
165 | -10 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.3
166 | -9 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
167 | -8 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
168 | -7 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
169 | -6 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.2
170 | -5 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
171 | -4 | 18.9 | 25.9 | 21.8 | 25.8 | 27.7 | 23.6 | 23.6 | 27.2
172 | -3 | 18.9 | 25.9 | 21.8 | 25.9 | 27.7 | 23.6 | 23.6 | 27.3
173 | -2 | 18.9 | 26.3 | 21 | 26.1 | 28.5 | 23.7 | 23.6 | 27.1
174 | -1 | 18.9 | 26.5 | 20.7 | 26.3 | 29 | 23.8 | 23.6 | 27.1
175 | 0 | 19.1 | 26.5 | 20.6 | 26.3 | 29.1 | 23.8 | 23.6 | 27.1
176 | 1 | 19.8 | 26.5 | 20.6 | 26.3 | 29.1 | 23.8 | 23.6 | 27.1
177 | 2 | 21.1 | 26.5 | 20.6 | 26.3 | 29 | 23.8 | 23.6 | 27.1
178 | 3 | 22.9 | 26.5 | 20.6 | 26.3 | 29 | 23.8 | 23.6 | 27.1
179 | 4 | 25.1 | 26.5 | 20.6 | 26.3 | 29 | 23.8 | 23.6 | 27.1
180 | 5 | 27.8 | 26.5 | 20.6 | 26.3 | 29 | 23.8 | 23.6 | 27.2
181 | 6 | 30.8 | 26.5 | 20.6 | 26.3 | 29 | 23.9 | 23.7 | 27.2
182 | 7 | 34.1 | 26.5 | 20.7 | 26.3 | 29 | 23.9 | 23.7 | 27.2
183 | 8 | 37.7 | 26.5 | 20.7 | 26.3 | 29 | 23.9 | 23.7 | 27.2
184 | 9 | 41.5 | 26.5 | 20.7 | 26.3 | 29 | 24 | 23.8 | 27.3
185 | 10 | 45.5 | 26.5 | 20.7 | 26.3 | 29.1 | 24.1 | 23.8 | 27.3
186 | 11 | 49.7 | 26.5 | 20.7 | 26.3 | 29.1 | 24.2 | 23.9 | 27.4
187 | 12 | 54 | 26.6 | 20.7 | 26.3 | 29.1 | 24.2 | 24 | 27.5
188 | 13 | 58.5 | 26.6 | 20.7 | 26.3 | 29.1 | 24.4 | 24 | 27.6
189 | 14 | 63.2 | 26.6 | 20.7 | 26.3 | 29.1 | 24.5 | 24.1 | 27.7
190 | 15 | 68 | 26.6 | 20.7 | 26.3 | 29.2 | 24.6 | 24.2 | 27.7
191 | 16 | 72.9 | 26.6 | 20.8 | 26.3 | 29.2 | 24.7 | 24.3 | 27.8
192 | 17 | 77.9 | 26.7 | 20.8 | 26.3 | 29.2 | 24.8 | 24.4 | 27.9
193 | 18 | 82.9 | 26.7 | 20.8 | 26.3 | 29.3 | 24.9 | 24.5 | 28
194 | 19 | 88.1 | 26.7 | 20.9 | 26.3 | 29.3 | 25 | 24.6 | 28.1
195 | 20 | 93.5 | 26.8 | 20.9 | 26.4 | 29.4 | 25.2 | 24.7 | 28.2
196 | 21 | 98.9 | 26.8 | 21 | 26.4 | 29.5 | 25.3 | 24.8 | 28.3
197 | 22 | 104.3 | 26.9 | 21 | 26.4 | 29.5 | 25.5 | 25 | 28.4
198 | 23 | 109.7 | 26.9 | 21.1 | 26.4 | 29.6 | 25.7 | 25.1 | 28.6
199 | 24 | 115.3 | 27 | 21.1 | 26.5 | 29.7 | 25.9 | 25.3 | 28.7
200 | 25 | 120.8 | 27.1 | 21.2 | 26.5 | 29.8 | 26.1 | 25.5 | 28.8
201 | 26 | 126.4 | 27.1 | 21.2 | 26.5 | 29.9 | 26.3 | 25.6 | 29
202 | 27 | 132.1 | 27.2 | 21.4 | 26.6 | 29.9 | 26.5 | 25.8 | 29.2
203 | 28 | 137.6 | 27.3 | 21.4 | 26.6 | 30 | 26.8 | 26 | 29.5
204 | 29 | 143.3 | 27.4 | 21.5 | 26.7 | 30.2 | 27 | 26.2 | 29.8
205 | 30 | 149 | 27.5 | 21.6 | 26.7 | 30.3 | 27.3 | 26.4 | 30
206 | 31 | 154.7 | 27.6 | 21.7 | 26.8 | 30.4 | 27.6 | 26.6 | 30.2
207 | 32 | 160.3 | 27.7 | 21.9 | 26.8 | 30.5 | 27.9 | 26.9 | 30.5
208 | 33 | 165.9 | 27.8 | 22 | 26.9 | 30.6 | 28.2 | 27.1 | 30.7
209 | 34 | 171.6 | 27.9 | 22.1 | 26.9 | 30.8 | 28.5 | 27.4 | 31
210 | 35 | 177.3 | 28.1 | 22.3 | 27 | 30.9 | 28.9 | 27.6 | 31.4
211 | 36 | 183 | 28.2 | 22.5 | 27.1 | 31.1 | 29.2 | 27.9 | 31.7
212 | 37 | 188.7 | 28.4 | 22.6 | 27.2 | 31.3 | 29.5 | 28.2 | 32.1
213 | 38 | 194.4 | 28.5 | 22.8 | 27.3 | 31.5 | 29.9 | 28.5 | 32.4
214 | 39 | 200 | 28.7 | 23 | 27.4 | 31.6 | 30.3 | 28.8 | 32.8
215 | 40 | 205.5 | 28.9 | 23.1 | 27.5 | 31.9 | 30.7 | 29.1 | 33.2
216 | 41 | 211.2 | 29.1 | 23.3 | 27.6 | 32.1 | 31.2 | 29.5 | 33.6
217 | 42 | 216.8 | 29.3 | 23.6 | 27.7 | 32.3 | 31.6 | 29.8 | 34
218 | 43 | 222.4 | 29.5 | 23.8 | 27.8 | 32.5 | 32 | 30.2 | 34.4
219 | 44 | 228 | 29.7 | 24 | 27.9 | 32.8 | 32.5 | 30.6 | 34.9
220 | 45 | 233.5 | 29.9 | 24.3 | 28.1 | 33 | 33 | 31 | 35.5
221 | 46 | 239.1 | 30.1 | 24.5 | 28.2 | 33.3 | 33.5 | 31.4 | 36
222 | 47 | 244.9 | 30.4 | 24.8 | 28.4 | 33.6 | 34 | 31.8 | 36.5
223 | 48 | 250.4 | 30.7 | 25 | 28.5 | 33.9 | 34.6 | 32.3 | 37
224 | 49 | 255.8 | 30.9 | 25.3 | 28.7 | 34.2 | 35.1 | 32.7 | 37.6
225 | 50 | 261.3 | 31.2 | 25.6 | 28.9 | 34.5 | 35.7 | 33.2 | 38.2
226 | 51 | 266.8 | 31.5 | 25.9 | 29.1 | 34.9 | 36.3 | 33.7 | 38.8
227 | 52 | 272.3 | 31.9 | 26.2 | 29.3 | 35.2 | 36.9 | 34.2 | 39.4
228 | 53 | 277.6 | 32.2 | 26.6 | 29.5 | 35.6 | 37.5 | 34.8 | 40.1
229 | 54 | 282.8 | 32.5 | 26.9 | 29.7 | 35.9 | 38.2 | 35.3 | 40.8
230 | 55 | 288.1 | 32.9 | 27.4 | 29.9 | 36.3 | 38.9 | 35.9 | 41.6
231 | 56 | 293.4 | 33.2 | 27.7 | 30.1 | 36.7 | 39.5 | 36.4 | 42.3
232 | 57 | 298.6 | 33.6 | 28.1 | 30.3 | 37.1 | 40.2 | 37 | 43.1
233 | 58 | 303.8 | 34 | 28.5 | 30.6 | 37.5 | 41 | 37.6 | 43.9
234 | 59 | 309.1 | 34.4 | 29 | 30.8 | 37.9 | 41.8 | 38.2 | 44.8
235 | 60 | 314.2 | 34.9 | 29.4 | 31.1 | 38.4 | 42.6 | 38.9 | 45.7
236 | 61 | 319.3 | 35.3 | 29.8 | 31.4 | 38.9 | 43.4 | 39.5 | 46.5
237 | 62 | 324.5 | 35.7 | 30.3 | 31.7 | 39.3 | 44.3 | 40.2 | 47.5
238 | 63 | 329.6 | 36.2 | 30.8 | 32 | 39.8 | 45.1 | 40.9 | 48.4
239 | 64 | 334.6 | 36.7 | 31.3 | 32.3 | 40.3 | 45.9 | 41.6 | 49.3
240 | 65 | 339.7 | 37.2 | 31.9 | 32.6 | 40.8 | 46.8 | 42.3 | 50.3
241 | 66 | 344.6 | 37.7 | 32.4 | 32.9 | 41.4 | 47.7 | 43.1 | 51.4
242 | 67 | 349.5 | 38.2 | 33 | 33.3 | 41.9 | 48.6 | 43.9 | 52.4
243 | 68 | 354.5 | 38.7 | 33.5 | 33.6 | 42.5 | 49.6 | 44.6 | 53.5
244 | 69 | 359.3 | 39.3 | 34.1 | 34 | 43.1 | 50.5 | 45.4 | 54.6
245 | 70 | 364.2 | 39.9 | 34.7 | 34.3 | 43.7 | 51.4 | 46.3 | 55.7
246 | 71 | 369 | 40.5 | 35.3 | 34.7 | 44.3 | 52.4 | 47.1 | 56.8
247 | 72 | 373.8 | 41.1 | 35.9 | 35.1 | 44.9 | 53.5 | 48 | 58.1
248 | 73 | 378.5 | 41.7 | 36.6 | 35.6 | 45.6 | 54.5 | 48.8 | 59.3
249 | 74 | 383.3 | 42.4 | 37.3 | 36 | 46.3 | 55.6 | 49.7 | 60.6
250 | 75 | 388 | 43 | 37.9 | 36.4 | 46.9 | 56.6 | 50.6 | 61.9
251 | 76 | 392.5 | 43.7 | 38.6 | 36.8 | 47.6 | 57.8 | 51.6 | 63.2
252 | 77 | 397 | 44.4 | 39.4 | 37.3 | 48.3 | 58.9 | 52.5 | 64.6
253 | 78 | 401.5 | 45.1 | 40.1 | 37.8 | 49.1 | 60.2 | 53.4 | 65.9
254 | 79 | 406 | 45.8 | 40.9 | 38.2 | 49.8 | 61.4 | 54.4 | 67.4
255 | 80 | 410.7 | 46.5 | 41.7 | 38.7 | 50.5 | 62.5 | 55.5 | 68.9
256 | 81 | 415.2 | 47.3 | 42.4 | 39.2 | 51.3 | 63.7 | 56.5 | 70.4
257 | 82 | 419.6 | 48 | 43.3 | 39.8 | 52.1 | 65 | 57.5 | 71.9
258 | 83 | 424.1 | 48.8 | 44.1 | 40.3 | 53 | 66.3 | 58.6 | 73.5
259 | 84 | 428.5 | 49.6 | 44.9 | 40.9 | 53.8 | 67.5 | 59.6 | 75.1
260 | 85 | 432.7 | 50.4 | 45.8 | 41.4 | 54.7 | 68.9 | 60.8 | 76.7
261 | 86 | 436.9 | 51.2 | 46.7 | 42 | 55.6 | 70.2 | 61.8 | 78.4
262 | 87 | 441.2 | 52.1 | 47.6 | 42.6 | 56.5 | 71.5 | 63 | 80.1
263 | 88 | 445.4 | 53 | 48.5 | 43.2 | 57.5 | 73 | 64.1 | 81.9
264 | 89 | 449.4 | 53.9 | 49.5 | 43.8 | 58.4 | 74.3 | 65.3 | 83.7
265 | 90 | 453.6 | 54.8 | 50.5 | 44.4 | 59.4 | 75.7 | 66.5 | 85.5
266 | 91 | 457.7 | 55.8 | 51.5 | 45.1 | 60.4 | 77.2 | 67.7 | 87.4
267 | 92 | 461.7 | 56.7 | 52.6 | 45.7 | 61.4 | 78.6 | 68.9 | 89.3
268 | 93 | 465.7 | 57.7 | 53.6 | 46.4 | 62.4 | 80.2 | 70.2 | 91.2
269 | 94 | 469.7 | 58.8 | 54.7 | 47.1 | 63.4 | 81.7 | 71.4 | 93.2
270 | 95 | 473.7 | 59.8 | 55.8 | 47.8 | 64.4 | 83.3 | 72.7 | 95.2
271 | 96 | 477.9 | 60.7 | 57 | 48.4 | 65.3 | 84.7 | 74 | 97.2
272 | 97 | 481.6 | 61.9 | 58.1 | 49.2 | 66.4 | 86.4 | 75.3 | 99.2
273 | 98 | 485.1 | 63 | 59.2 | 49.9 | 67.5 | 87.9 | 76.6 | 101.3
274 | 99 | 488.4 | 64.1 | 60.4 | 50.7 | 68.6 | 89.4 | 77.9 | 103.4
275 | 100 | 491.3 | 65.2 | 61.5 | 51.4 | 69.7 | 90.9 | 79.2 | 105.6
276 | 101 | 494 | 66.3 | 62.7 | 52.2 | 70.9 | 92.5 | 80.4 | 107.7
277 | 102 | 496.6 | 67.5 | 63.9 | 53 | 72 | 94.1 | 81.7 | 109.9
278 | 103 | 499 | 68.6 | 65.1 | 53.8 | 73.1 | 95.7 | 83 | 112.1
279 | 104 | 501.1 | 69.8 | 66.3 | 54.6 | 74.3 | 97.2 | 84.2 | 114.3
280 | 105 | 503.4 | 71 | 67.5 | 55.4 | 75.5 | 98.6 | 85.5 | 116.5
281 | 106 | 505.6 | 72.2 | 68.7 | 56.2 | 76.7 | 100.2 | 86.8 | 118.7
282 | 107 | 507.7 | 73.4 | 69.9 | 57.1 | 77.9 | 101.8 | 88.1 | 120.9
283 | 108 | 509.7 | 74.7 | 71.1 | 58 | 79.1 | 103.4 | 89.4 | 123.1
284 | 109 | 511.6 | 75.9 | 72.4 | 58.8 | 80.3 | 104.9 | 90.6 | 125.3
285 | 110 | 513.3 | 77.1 | 73.7 | 59.7 | 81.5 | 106.4 | 91.8 | 127.6
286 | 111 | 515 | 78.3 | 75 | 60.5 | 82.6 | 107.8 | 93 | 129.7
287 | 112 | 516.3 | 79.5 | 76.4 | 61.4 | 83.7 | 109.1 | 94.2 | 132
288 | 113 | 517.3 | 80.7 | 77.7 | 62.3 | 84.9 | 110.6 | 95.4 | 134.2
289 | 114 | 518.3 | 81.9 | 79 | 63.1 | 86 | 112 | 96.7 | 136.4
290 | 115 | 519.1 | 83.1 | 80.4 | 64 | 87.1 | 113.5 | 97.9 | 138.5
291 | 116 | 519.5 | 84.4 | 81.7 | 64.9 | 88.3 | 114.9 | 99.1 | 140.7
292 | 117 | 519.5 | 85.6 | 83 | 65.8 | 89.5 | 116.2 | 100.3 | 142.8
293 | 118 | 519.3 | 86.9 | 84.3 | 66.7 | 90.7 | 117.6 | 101.4 | 144.9
294 | 119 | 519.3 | 88.2 | 85.5 | 67.6 | 92 | 119 | 102.5 | 147
295 | 120 | 519.3 | 89.5 | 86.8 | 68.5 | 93.2 | 120.4 | 103.5 | 149.1
296 | 121 | 519.3 | 90.8 | 88.1 | 69.5 | 94.4 | 121.6 | 104.5 | 151.2
297 | 122 | 519.2 | 92 | 89.4 | 70.4 | 95.6 | 122.7 | 105.6 | 153.3
298 | 123 | 518.9 | 93.3 | 90.6 | 71.3 | 96.8 | 124 | 106.6 | 155.3
299 | 124 | 518.8 | 94.6 | 91.9 | 72.2 | 97.9 | 125.1 | 107.6 | 157.4
300 | 125 | 518.6 | 95.8 | 93.2 | 73.1 | 99.1 | 126.4 | 108.7 | 159.5
301 | 126 | 518.6 | 97.1 | 94.5 | 74.1 | 100.3 | 127.6 | 109.7 | 161.5
302 | 127 | 518.6 | 98.3 | 95.8 | 75 | 101.4 | 128.9 | 110.7 | 163.5
303 | 128 | 518.7 | 99.6 | 97.1 | 75.8 | 102.5 | 130 | 111.7 | 165.6
304 | 129 | 518.7 | 100.8 | 98.4 | 76.8 | 103.7 | 131.1 | 112.8 | 167.4
305 | 130 | 518.7 | 102 | 99.6 | 77.7 | 104.8 | 132.2 | 113.7 | 169.4
306 | 131 | 518.8 | 103.3 | 100.9 | 78.6 | 105.9 | 133.4 | 114.5 | 171.4
307 | 132 | 518.9 | 104.5 | 102.1 | 79.5 | 107.1 | 134.5 | 115.4 | 173.3
308 | 133 | 518.8 | 105.7 | 103.3 | 80.4 | 108.2 | 135.6 | 116.4 | 175.3
309 | 134 | 519 | 106.9 | 104.5 | 81.3 | 109.3 | 136.8 | 117.4 | 177.3
310 | 135 | 519.1 | 108.2 | 105.7 | 82.2 | 110.4 | 138.1 | 118.3 | 179.2
311 | 136 | 519.1 | 109.4 | 106.8 | 83.1 | 111.6 | 139.2 | 119.1 | 181.1
312 | 137 | 519.1 | 110.6 | 107.9 | 84 | 112.7 | 140.4 | 120 | 183
313 | 138 | 519.2 | 111.8 | 109.1 | 84.9 | 113.7 | 141.5 | 120.8 | 184.9
314 | 139 | 519.2 | 113 | 110.2 | 85.8 | 114.8 | 142.6 | 121.8 | 186.8
315 | 140 | 519.4 | 114.2 | 111.3 | 86.7 | 115.9 | 143.6 | 122.7 | 188.7
316 | 141 | 519.4 | 115.4 | 112.4 | 87.6 | 116.9 | 144.7 | 123.6 | 190.5
317 | 142 | 519.5 | 116.6 | 113.5 | 88.5 | 117.9 | 145.8 | 124.5 | 192.2
318 | 143 | 519.6 | 117.8 | 114.5 | 89.3 | 118.9 | 146.8 | 125.4 | 194
319 | 144 | 519.9 | 118.9 | 115.6 | 90.2 | 119.9 | 147.8 | 126.2 | 195.9
320 | 145 | 520.2 | 120.1 | 116.6 | 91.1 | 120.9 | 148.8 | 127 | 197.8
321 | 146 | 520.5 | 121.2 | 117.7 | 92 | 121.9 | 149.8 | 127.8 | 199.6
322 | 147 | 520.8 | 122.3 | 118.7 | 92.9 | 122.9 | 150.5 | 128.7 | 201.4
323 | 148 | 520.9 | 123.4 | 119.7 | 93.7 | 123.8 | 151.3 | 129.5 | 203.2
324 | 149 | 521.5 | 124.5 | 120.7 | 94.6 | 124.6 | 152.2 | 130.4 | 205
325 | 150 | 521.9 | 125.6 | 121.7 | 95.4 | 125.5 | 153.2 | 131.2 | 206.8
326 | 151 | 522.2 | 126.7 | 122.6 | 96.3 | 126.4 | 154 | 132.1 | 208.5
327 | 152 | 522.6 | 127.8 | 123.5 | 97.1 | 127.3 | 154.9 | 132.9 | 210.3
328 | 153 | 523 | 128.8 | 124.4 | 97.9 | 128.1 | 155.8 | 133.6 | 212
329 | 154 | 523.2 | 129.8 | 125.3 | 98.8 | 128.9 | 156.9 | 134.3 | 213.8
330 | 155 | 523.4 | 130.9 | 126.1 | 99.6 | 129.7 | 157.9 | 135 | 215.5
331 | 156 | 523.4 | 131.9 | 126.9 | 100.5 | 130.6 | 158.9 | 135.8 | 217.2
332 | 157 | 523.4 | 132.8 | 127.7 | 101.3 | 131.5 | 159.9 | 136.6 | 218.9
333 | 158 | 523.5 | 133.8 | 128.5 | 102.2 | 132.3 | 160.9 | 137.4 | 220.6
334 | 159 | 523.6 | 134.8 | 129.3 | 103 | 133.1 | 162.1 | 138.2 | 222.3
335 | 160 | 523.9 | 135.7 | 130.1 | 103.9 | 133.9 | 163 | 138.9 | 223.9
336 | 161 | 524.1 | 136.6 | 130.8 | 104.7 | 134.6 | 164.2 | 139.7 | 225.5
337 | 162 | 524.1 | 137.5 | 131.6 | 105.6 | 135.4 | 165.1 | 140.5 | 227.2
338 | 163 | 524.1 | 138.4 | 132.3 | 106.4 | 136.2 | 165.9 | 141.2 | 228.8
339 | 164 | 524.1 | 139.3 | 133.1 | 107.3 | 136.9 | 166.8 | 141.9 | 230.4
340 | 165 | 524 | 140.1 | 133.8 | 108.1 | 137.6 | 167.7 | 142.6 | 232
341 | 166 | 523.9 | 140.9 | 134.6 | 109 | 138.4 | 168.6 | 143.3 | 233.6
342 | 167 | 523.7 | 141.8 | 135.3 | 109.9 | 139.1 | 169.5 | 144 | 235.2
343 | 168 | 523.6 | 142.6 | 136 | 110.8 | 139.8 | 170.2 | 144.7 | 236.8
344 | 169 | 523.4 | 143.4 | 136.7 | 111.6 | 140.5 | 171 | 145.4 | 238.4
345 | 170 | 523.3 | 144.3 | 137.5 | 112.5 | 141.2 | 171.8 | 146 | 239.9
346 | 171 | 523.1 | 145.1 | 138.2 | 113.3 | 141.8 | 172.4 | 146.7 | 241.4
347 | 172 | 523.1 | 145.9 | 138.9 | 114.2 | 142.4 | 173.1 | 147.4 | 242.9
348 | 173 | 523.1 | 146.7 | 139.7 | 115 | 143.1 | 173.8 | 148.1 | 244.5
349 | 174 | 523 | 147.6 | 140.4 | 115.8 | 143.7 | 174.3 | 148.7 | 246
350 | 175 | 522.9 | 148.4 | 141.1 | 116.6 | 144.4 | 175.1 | 149.2 | 247.4
351 | 176 | 522.8 | 149.3 | 141.8 | 117.5 | 145 | 176 | 149.8 | 248.9
352 | 177 | 522.7 | 150.1 | 142.5 | 118.4 | 145.7 | 176.8 | 150.5 | 250.4
353 | 178 | 522.4 | 151 | 143.3 | 119.3 | 146.3 | 177.5 | 151.1 | 251.8
354 | 179 | 522.2 | 151.8 | 144 | 120.2 | 147 | 178.2 | 151.9 | 253.2
355 | 180 | 521.8 | 152.6 | 144.8 | 121.1 | 147.6 | 178.9 | 152.5 | 254.5
356 | 181 | 521.6 | 153.4 | 145.5 | 122.1 | 148.2 | 179.6 | 153.3 | 255.9
357 | 182 | 521.1 | 154.3 | 146.2 | 123 | 148.8 | 180.4 | 153.9 | 257.2
358 | 183 | 520.9 | 155.1 | 147 | 124 | 149.5 | 181.1 | 154.5 | 258.6
359 | 184 | 520.9 | 155.9 | 147.7 | 125 | 150.1 | 181.8 | 154.9 | 259.9
360 | 185 | 520.8 | 156.8 | 148.5 | 125.9 | 150.7 | 182.6 | 155.5 | 261.2
361 | 186 | 521 | 157.6 | 149.3 | 126.9 | 151.3 | 183.4 | 156.2 | 262.6
362 | 187 | 521 | 158.4 | 150.1 | 127.8 | 151.9 | 184.1 | 156.9 | 263.9
363 | 188 | 520.8 | 159.3 | 150.8 | 128.8 | 152.5 | 184.7 | 157.3 | 265.2
364 | 189 | 520.8 | 160.1 | 151.7 | 129.8 | 153.2 | 185.6 | 157.6 | 266.5
365 | 190 | 521 | 161 | 152.5 | 130.8 | 153.8 | 186.3 | 158.1 | 267.8
366 | 191 | 521.3 | 161.8 | 153.3 | 131.8 | 154.5 | 187.1 | 158.8 | 269.1
367 | 192 | 521.3 | 162.7 | 154.2 | 132.8 | 155.2 | 187.8 | 159.3 | 270.3
368 | 193 | 521.5 | 163.5 | 155 | 133.7 | 155.8 | 188.7 | 159.6 | 271.5
369 | 194 | 521.5 | 164.4 | 155.9 | 134.7 | 156.5 | 189.7 | 160 | 272.7
370 | 195 | 521.6 | 165.3 | 156.8 | 135.7 | 157.3 | 190.5 | 160.6 | 273.9
371 | 196 | 521.6 | 166.2 | 157.7 | 136.6 | 158 | 191.4 | 161.2 | 275.1
372 | 197 | 521.4 | 167.2 | 158.6 | 137.6 | 158.7 | 192.1 | 161.9 | 276.2
373 | 198 | 521.2 | 168.1 | 159.5 | 138.5 | 159.5 | 192.8 | 162.4 | 277.5
374 | 199 | 521.2 | 169 | 160.4 | 139.4 | 160.2 | 193.5 | 163 | 278.7
375 | 200 | 521.3 | 169.9 | 161.4 | 140.3 | 161 | 194.2 | 163.6 | 279.9
376 | 201 | 521.4 | 170.8 | 162.3 | 141.2 | 161.8 | 194.8 | 164.1 | 281
377 | 202 | 521.5 | 171.8 | 163.1 | 142.1 | 162.6 | 195.4 | 164.7 | 282.2
378 | 203 | 521.7 | 172.7 | 164 | 143 | 163.4 | 196.1 | 165.3 | 283.3
379 | 204 | 521.9 | 173.6 | 164.9 | 143.9 | 164.1 | 196.7 | 165.8 | 284.4
380 | 205 | 522.1 | 174.6 | 165.8 | 144.8 | 164.9 | 197.4 | 166.2 | 285.5
381 | 206 | 522.1 | 175.5 | 166.7 | 145.8 | 165.7 | 198 | 166.7 | 286.7
382 | 207 | 522 | 176.5 | 167.5 | 146.7 | 166.5 | 198.6 | 167.2 | 287.8
383 | 208 | 521.8 | 177.4 | 168.4 | 147.6 | 167.2 | 199.4 | 167.6 | 288.9
384 | 209 | 521.9 | 178.3 | 169.3 | 148.5 | 168 | 200 | 168.1 | 290
385 | 210 | 521.8 | 179.3 | 170.1 | 149.4 | 168.8 | 200.7 | 168.6 | 291.1
386 | 211 | 521.8 | 180.2 | 171 | 150.3 | 169.5 | 201.5 | 169 | 292.2
387 | 212 | 521.8 | 181.1 | 171.8 | 151.2 | 170.2 | 202.3 | 169.4 | 293.2
388 | 213 | 521.9 | 182.1 | 172.7 | 152.1 | 171 | 203.2 | 169.8 | 294.2
389 | 214 | 521.9 | 183 | 173.5 | 153 | 171.7 | 204.1 | 170.2 | 295.2
390 | 215 | 521.7 | 183.9 | 174.3 | 153.9 | 172.5 | 204.9 | 170.7 | 296.2
391 | 216 | 521.6 | 184.8 | 175.2 | 154.8 | 173.3 | 205.8 | 171.4 | 297.2
392 | 217 | 521.4 | 185.7 | 176 | 155.6 | 174.1 | 206.7 | 171.9 | 298.2
393 | 218 | 521.4 | 186.6 | 176.8 | 156.5 | 174.8 | 207.5 | 172.3 | 299.2
394 | 219 | 521.2 | 187.5 | 177.6 | 157.4 | 175.6 | 208.2 | 172.9 | 300.2
395 | 220 | 521 | 188.4 | 178.3 | 158.3 | 176.5 | 208.9 | 173.5 | 301.2
396 | 221 | 520.9 | 189.2 | 179.1 | 159.1 | 177.3 | 209.7 | 174.1 | 302.1
397 | 222 | 520.9 | 189.9 | 179.8 | 160 | 178.2 | 210.6 | 174.7 | 303.1
398 | 223 | 521 | 190.2 | 180.4 | 160.9 | 179 | 211.4 | 175.3 | 304.1
399 | 224 | 521 | 190.2 | 181 | 161.7 | 179.8 | 212.2 | 175.9 | 304.9
400 | 225 | 521.1 | 190.2 | 181.4 | 162.6 | 180.7 | 212.8 | 176.4 | 305.9
401 | 226 | 521.1 | 190.3 | 181.9 | 163.4 | 181.6 | 213.4 | 176.8 | 306.8
402 | 227 | 521.1 | 190.4 | 182.2 | 164.3 | 182.5 | 214 | 177.2 | 307.7
403 | 228 | 521.2 | 190.6 | 182.5 | 165.1 | 183.4 | 214.6 | 177.6 | 308.6
404 | 229 | 521.1 | 190.8 | 182.7 | 166 | 184.3 | 215.2 | 178 | 309.5
405 | 230 | 521.2 | 191 | 183 | 166.8 | 185.2 | 215.7 | 178.4 | 310.5
406 | 231 | 521.3 | 191.3 | 183.1 | 167.6 | 186 | 216 | 178.7 | 311.3
407 | 232 | 521.5 | 191.5 | 183.3 | 168.5 | 187 | 216.6 | 179.1 | 312.2
408 | 233 | 521.7 | 191.7 | 183.4 | 169.3 | 187.9 | 217 | 179.5 | 313.1
409 | 234 | 521.8 | 192.1 | 183.6 | 170.2 | 188.7 | 217.5 | 180 | 314
410 | 235 | 521.8 | 192.6 | 183.7 | 171 | 189.6 | 218.1 | 180.5 | 314.9
411 | 236 | 522 | 193.1 | 183.9 | 171.8 | 190.4 | 218.7 | 180.8 | 315.7
412 | 237 | 522.2 | 193.6 | 184.2 | 172.7 | 191.2 | 219.4 | 181.1 | 316.5
413 | 238 | 522.2 | 194 | 184.5 | 173.5 | 192 | 219.9 | 181.6 | 317.4
414 | 239 | 522.1 | 194.5 | 184.8 | 174.3 | 192.7 | 220.5 | 181.8 | 318.3
415 | 240 | 522.1 | 195 | 185.1 | 175.2 | 193.6 | 221.3 | 182.1 | 319
416 | 241 | 522.2 | 195.5 | 185.5 | 176 | 194.4 | 222 | 182.7 | 319.7
417 | 242 | 522.3 | 195.9 | 185.9 | 176.8 | 195 | 222.6 | 183.4 | 320.6
418 | 243 | 522 | 196.3 | 186.4 | 177.6 | 195.6 | 223.1 | 184 | 321.4
419 | 244 | 522 | 196.8 | 186.9 | 178.4 | 196.2 | 223.8 | 184.4 | 322.2
420 | 245 | 521.9 | 197.2 | 187.5 | 179.2 | 196.8 | 224.5 | 184.7 | 323
421 | 246 | 521.9 | 197.7 | 188 | 180 | 197.4 | 225.4 | 185.3 | 323.7
422 | 247 | 521.7 | 198.2 | 188.7 | 180.8 | 198 | 226.3 | 186 | 324.5
423 | 248 | 521.7 | 198.7 | 189.3 | 181.7 | 198.6 | 227.1 | 186.5 | 325.3
424 | 249 | 521.7 | 199.2 | 190 | 182.5 | 199.2 | 227.7 | 186.9 | 326.1
425 | 250 | 521.7 | 199.7 | 190.8 | 183.3 | 199.8 | 228.3 | 187.3 | 326.8
426 | 251 | 521.6 | 200.3 | 191.6 | 184.1 | 200.4 | 228.9 | 187.6 | 327.6
427 | 252 | 521.5 | 200.9 | 192.4 | 184.9 | 201 | 229.3 | 187.9 | 328.3
428 | 253 | 521.6 | 201.6 | 193.2 | 185.7 | 201.7 | 229.7 | 188.2 | 329.1
429 | 254 | 521.6 | 202.2 | 194 | 186.5 | 202.3 | 230.1 | 188.5 | 329.8
430 | 255 | 521.4 | 202.8 | 194.9 | 187.3 | 202.8 | 230.6 | 188.8 | 330.5
431 | 256 | 521.3 | 203.5 | 195.7 | 188.1 | 203.4 | 231 | 189.2 | 331.3
432 | 257 | 521.4 | 204.1 | 196.6 | 188.9 | 203.9 | 231.3 | 189.6 | 332
433 | 258 | 521.7 | 204.7 | 197.3 | 189.6 | 204.5 | 231.6 | 190 | 332.7
434 | 259 | 521.5 | 205.2 | 198.2 | 190.4 | 205.1 | 232 | 190.5 | 333.5
435 | 260 | 521.6 | 205.7 | 199.1 | 191.1 | 205.7 | 232.3 | 191.1 | 334.2
436 | 261 | 521.5 | 206.1 | 200 | 191.9 | 206.3 | 232.7 | 191.5 | 334.9
437 | 262 | 521.6 | 206.5 | 200.9 | 192.7 | 206.9 | 233.3 | 192 | 335.6
438 | 263 | 521.6 | 207 | 201.7 | 193.4 | 207.6 | 233.9 | 192.5 | 336.3
439 | 264 | 521.5 | 207.4 | 202.5 | 194.2 | 208.2 | 234.5 | 193 | 337.1
440 | 265 | 521.2 | 207.9 | 203.4 | 194.9 | 208.8 | 235.1 | 193.4 | 337.8
441 | 266 | 521 | 208.4 | 204.2 | 195.6 | 209.5 | 235.8 | 193.8 | 338.6
442 | 267 | 520.9 | 208.8 | 205.1 | 196.3 | 210.2 | 236.3 | 194.3 | 339.3
443 | 268 | 521 | 209.3 | 206 | 197 | 210.9 | 236.9 | 194.8 | 340
444 | 269 | 521.1 | 209.7 | 207.1 | 197.7 | 211.5 | 237.4 | 195.1 | 340.7
445 | 270 | 521.1 | 210.2 | 208.3 | 198.4 | 212.1 | 237.8 | 195.5 | 341.4
446 | 271 | 521.1 | 210.8 | 209.8 | 199.1 | 212.6 | 238.1 | 195.9 | 342.2
447 | 272 | 521 | 211.4 | 211.2 | 199.8 | 213.2 | 238.4 | 196.3 | 342.8
448 | 273 | 521 | 211.9 | 212.7 | 200.5 | 213.7 | 238.9 | 196.6 | 343.4
449 | 274 | 521.2 | 212.4 | 214 | 201.2 | 214.3 | 239.4 | 196.9 | 344
450 | 275 | 521.3 | 213 | 215.2 | 201.8 | 214.9 | 239.8 | 197.2 | 344.6
451 | 276 | 521.2 | 213.6 | 216.3 | 202.4 | 215.5 | 240.5 | 197.5 | 345.3
452 | 277 | 521.3 | 214.1 | 217.3 | 203.1 | 216 | 240.8 | 197.6 | 345.9
453 | 278 | 521.4 | 214.7 | 218.4 | 203.7 | 216.5 | 241.3 | 197.8 | 346.5
454 | 279 | 521.7 | 215.3 | 219.5 | 204.3 | 217 | 241.8 | 198.2 | 347.1
455 | 280 | 522 | 215.8 | 220.4 | 204.9 | 217.4 | 242.3 | 198.8 | 347.6
456 | 281 | 522.2 | 216.3 | 221.4 | 205.5 | 217.9 | 242.8 | 199.3 | 348.1
457 | 282 | 522.3 | 216.8 | 222.3 | 206.1 | 218.4 | 243.2 | 199.5 | 348.6
458 | 283 | 522.4 | 217.3 | 223.3 | 206.7 | 218.8 | 243.7 | 199.8 | 349.2
459 | 284 | 522.5 | 217.9 | 224.1 | 207.3 | 219.2 | 244.4 | 200.3 | 349.7
460 | 285 | 522.6 | 218.4 | 224.9 | 207.8 | 219.6 | 245.2 | 200.7 | 350.2
461 | 286 | 522.6 | 219 | 225.7 | 208.4 | 220 | 245.9 | 201.1 | 350.8
462 | 287 | 522.6 | 219.7 | 226.4 | 208.9 | 220.4 | 246.5 | 201.6 | 351.3
463 | 288 | 522.5 | 220.3 | 227.2 | 209.5 | 220.8 | 247.2 | 202.1 | 351.8
464 | 289 | 522.5 | 220.9 | 228 | 210 | 221.2 | 248 | 202.6 | 352.3
465 | 290 | 522.4 | 221.5 | 228.7 | 210.5 | 221.5 | 248.6 | 203.1 | 352.8
466 | 291 | 522.2 | 222.1 | 229.3 | 211 | 221.8 | 248.8 | 203.7 | 353.4
467 | 292 | 522.2 | 222.6 | 230 | 211.6 | 222.1 | 249.1 | 204.2 | 353.9
468 | 293 | 522.3 | 223.2 | 230.6 | 212.1 | 222.4 | 249.4 | 204.8 | 354.4
469 | 294 | 522.3 | 223.7 | 231.2 | 212.6 | 222.7 | 249.6 | 205.3 | 354.9
470 | 295 | 522.3 | 224.3 | 231.9 | 213.1 | 223 | 250 | 205.6 | 355.4
471 | 296 | 522.2 | 224.9 | 232.4 | 213.6 | 223.4 | 250.4 | 205.8 | 355.9
472 | 297 | 522 | 225.6 | 232.9 | 214.1 | 223.7 | 250.8 | 206.2 | 356.4
473 | 298 | 521.9 | 226.3 | 233.5 | 214.6 | 224 | 251.1 | 206.5 | 356.8
474 | 299 | 522 | 227 | 234.1 | 215.1 | 224.4 | 251.5 | 206.7 | 357.3
475 | 300 | 521.7 | 227.8 | 234.7 | 215.6 | 224.7 | 252 | 207 | 357.7
476 | 301 | 521.5 | 228.5 | 235.2 | 216.1 | 225 | 252.4 | 207.3 | 358.1
477 | 302 | 521.6 | 229.3 | 235.8 | 216.6 | 225.3 | 252.7 | 207.6 | 358.6
478 | 303 | 521.6 | 230.1 | 236.3 | 217.1 | 225.7 | 253 | 207.8 | 359
479 | 304 | 521.6 | 230.8 | 236.9 | 217.6 | 225.9 | 253.3 | 208.1 | 359.5
480 | 305 | 521.6 | 231.6 | 237.5 | 218.1 | 226.2 | 253.7 | 208.3 | 360
481 | 306 | 521.5 | 232.4 | 238.1 | 218.6 | 226.5 | 254.1 | 208.5 | 360.4
482 | 307 | 521.5 | 233.3 | 238.6 | 219.2 | 226.9 | 254.6 | 209.1 | 360.8
483 | 308 | 521.4 | 234.2 | 239.2 | 219.7 | 227.2 | 254.9 | 209.4 | 361.2
484 | 309 | 521.2 | 235 | 239.7 | 220.3 | 227.5 | 255.4 | 209.9 | 361.5
485 | 310 | 521 | 235.9 | 240.2 | 220.8 | 227.9 | 255.9 | 210.3 | 361.9
486 | 311 | 520.9 | 236.6 | 240.7 | 221.4 | 228.2 | 256.4 | 211 | 362.2
487 | 312 | 520.9 | 237.4 | 241.2 | 222 | 228.6 | 257.1 | 211.4 | 362.6
488 | 313 | 521 | 238.1 | 241.7 | 222.7 | 229 | 257.4 | 211.9 | 363
489 | 314 | 521.1 | 238.9 | 242.5 | 223.3 | 229.4 | 257.8 | 212.3 | 363.4
490 | 315 | 521.3 | 239.5 | 243.2 | 223.9 | 229.7 | 258.2 | 212.5 | 363.8
491 | 316 | 521.4 | 240.1 | 243.8 | 224.5 | 230.1 | 258.5 | 212.7 | 364.1
492 | 317 | 521.7 | 240.7 | 244.4 | 225.2 | 230.5 | 258.8 | 212.9 | 364.4
493 | 318 | 521.7 | 241.3 | 245.1 | 225.9 | 230.9 | 259 | 213.2 | 364.9
494 | 319 | 521.6 | 242 | 245.8 | 226.5 | 231.3 | 259.3 | 213.5 | 365.4
495 | 320 | 521.6 | 242.8 | 246.4 | 227.2 | 231.7 | 260 | 213.6 | 365.7
496 | 321 | 521.6 | 243.8 | 247.1 | 228 | 232.1 | 260.2 | 213.8 | 366.1
497 | 322 | 521.8 | 244.8 | 247.7 | 228.8 | 232.5 | 260.5 | 214.2 | 366.4
498 | 323 | 522 | 245.9 | 248.3 | 229.7 | 232.9 | 260.8 | 214.5 | 366.8
499 | 324 | 522 | 247.4 | 248.8 | 230.7 | 233.4 | 261.2 | 214.8 | 367.1
500 | 325 | 522.1 | 249.2 | 249.2 | 232.7 | 233.9 | 261.5 | 215.1 | 367.5
501 | 326 | 521.7 | 250.9 | 249.7 | 236.1 | 234.3 | 261.8 | 215.5 | 367.8
502 | 327 | 521.5 | 252.3 | 250.2 | 238.6 | 234.7 | 261.9 | 215.7 | 368.1
503 | 328 | 521.3 | 252.4 | 250.7 | 240.7 | 235.2 | 262.4 | 216.1 | 368.4
504 | 329 | 521.2 | 252.6 | 251.1 | 242.7 | 235.7 | 262.9 | 216.4 | 368.8
505 | 330 | 521.2 | 252.8 | 251.7 | 244.3 | 236.1 | 263.3 | 216.7 | 369.2
506 | 331 | 521.1 | 253.1 | 252.2 | 245.9 | 236.6 | 263.6 | 216.9 | 369.6
507 | 332 | 521.2 | 253.5 | 252.7 | 247.4 | 237 | 263.9 | 217.2 | 369.9
508 | 333 | 521.3 | 253.9 | 253.2 | 248.6 | 237.4 | 264.2 | 217.7 | 370.2
509 | 334 | 521.2 | 254.3 | 253.7 | 249.7 | 237.8 | 264.7 | 218.1 | 370.5
510 | 335 | 521.1 | 254.7 | 254.1 | 251 | 238.3 | 265.1 | 218.4 | 370.8
511 | 336 | 521 | 255.1 | 254.6 | 252.2 | 238.8 | 265.3 | 218.6 | 371.1
512 | 337 | 521.1 | 255.4 | 255.1 | 253.5 | 239.2 | 265.6 | 218.9 | 371.4
513 | 338 | 521.3 | 255.7 | 255.6 | 254.8 | 239.6 | 266 | 219.3 | 371.7
514 | 339 | 521.2 | 256.1 | 256 | 256.3 | 240.1 | 266.3 | 219.6 | 371.9
515 | 340 | 521.1 | 256.5 | 256.5 | 257.7 | 240.7 | 266.5 | 220.1 | 372.2
516 | 341 | 521 | 256.9 | 256.9 | 259 | 241.2 | 266.9 | 220.3 | 372.5
517 | 342 | 520.9 | 257.2 | 257.4 | 260.3 | 241.7 | 267.2 | 220.7 | 372.8
518 | 343 | 520.8 | 257.6 | 257.8 | 261.5 | 242.3 | 267.5 | 220.9 | 373
519 | 344 | 520.7 | 258.1 | 258.3 | 262.6 | 242.8 | 267.9 | 221.3 | 373.3
520 | 345 | 520.9 | 258.5 | 258.7 | 263.4 | 243.4 | 268.4 | 221.7 | 373.5
521 | 346 | 521 | 258.8 | 259.3 | 264 | 243.9 | 268.5 | 222.1 | 373.8
522 | 347 | 521 | 258.8 | 259.7 | 264.4 | 244.5 | 268.7 | 222.5 | 374.1
523 | 348 | 521.1 | 258.9 | 260.2 | 264.9 | 245.1 | 269.2 | 222.8 | 374.5
524 | 349 | 521.1 | 259.1 | 260.6 | 264.7 | 245.7 | 269.6 | 223 | 374.7
525 | 350 | 521.1 | 259.3 | 261 | 264.6 | 246.4 | 270 | 223.3 | 375
526 | 351 | 521.1 | 259.6 | 261.5 | 265.3 | 247 | 270.3 | 223.4 | 375.2
527 | 352 | 521 | 259.9 | 262 | 265.9 | 247.7 | 270.7 | 223.7 | 375.5
528 | 353 | 520.6 | 260.3 | 262.6 | 266.4 | 248.5 | 271.1 | 224 | 375.7
529 | 354 | 520.4 | 260.6 | 263.2 | 266.9 | 249.1 | 271.3 | 224.4 | 376
530 | 355 | 520.3 | 260.9 | 263.7 | 267.3 | 249.7 | 271.5 | 224.8 | 376.3
531 | 356 | 520.3 | 261.3 | 264.3 | 267.7 | 250.2 | 271.9 | 225.2 | 376.5
532 | 357 | 520.3 | 261.6 | 264.9 | 268.2 | 250.7 | 272.3 | 225.7 | 376.8
533 | 358 | 520.3 | 262 | 265.5 | 268.5 | 251.2 | 272.7 | 226.1 | 377
534 | 359 | 520.3 | 262.5 | 266 | 268.8 | 251.9 | 272.9 | 226.4 | 377.3
535 | 360 | 520.1 | 262.8 | 266.9 | 269.1 | 252.3 | 273 | 226.7 | 377.5
536 | 361 | 520 | 263.2 | 267.8 | 269.2 | 252.9 | 273.3 | 227 | 377.7
537 | 362 | 519.8 | 263.7 | 268.3 | 269.4 | 253.7 | 273.6 | 227.3 | 377.9
538 | 363 | 519.7 | 264.2 | 269 | 269.6 | 254.3 | 274.1 | 227.6 | 378.2
539 | 364 | 519.4 | 264.7 | 269.4 | 269.9 | 255 | 274.4 | 227.9 | 378.4
540 | 365 | 519.2 | 265.2 | 269.8 | 270.3 | 255.7 | 274.8 | 228.3 | 378.6
541 | 366 | 519.3 | 265.6 | 270.3 | 270.6 | 256.5 | 275 | 228.4 | 378.8
542 | 367 | 519.4 | 266 | 270.8 | 270.9 | 257.6 | 275.3 | 228.5 | 379
543 | 368 | 519.5 | 266.4 | 271.2 | 271.1 | 258.9 | 275.8 | 228.9 | 379.2
544 | 369 | 519.6 | 266.9 | 271.7 | 271.3 | 260 | 276.1 | 229.2 | 379.4
545 | 370 | 519.6 | 267.3 | 272.1 | 271.5 | 261 | 276.6 | 229.5 | 379.6
546 | 371 | 519.9 | 267.8 | 272.4 | 271.7 | 262.2 | 276.8 | 229.8 | 379.8
547 | 372 | 520.1 | 268.3 | 272.7 | 271.9 | 263.6 | 277.3 | 230.1 | 380.1
548 | 373 | 520.2 | 268.8 | 273.1 | 272.1 | 264.9 | 277.6 | 230.4 | 380.3
549 | 374 | 520.3 | 269.2 | 273.5 | 272.4 | 265.9 | 278.1 | 230.8 | 380.5
550 | 375 | 520.2 | 269.6 | 273.9 | 272.7 | 266.8 | 278.4 | 231.1 | 380.7
551 | 376 | 520.1 | 270 | 274.4 | 272.9 | 267.8 | 278.7 | 231.4 | 380.9
552 | 377 | 520.3 | 270.5 | 274.8 | 273 | 268.7 | 278.9 | 231.7 | 381.1
553 | 378 | 520.4 | 270.9 | 275.3 | 273.2 | 269.6 | 279.3 | 232.1 | 381.3
554 | 379 | 520.4 | 271.4 | 275.8 | 273.4 | 270.8 | 279.7 | 232.5 | 381.5
555 | 380 | 520.5 | 271.8 | 276.1 | 273.6 | 272.1 | 279.9 | 232.8 | 381.7
556 | 381 | 520.4 | 272.3 | 276.5 | 273.9 | 273.2 | 280.4 | 233.1 | 382
557 | 382 | 520.4 | 272.7 | 276.8 | 274.2 | 274.3 | 280.9 | 233.5 | 382.1
558 | 383 | 520.3 | 273.1 | 277.1 | 274.5 | 275.2 | 281.1 | 233.8 | 382.3
559 | 384 | 520.3 | 273.6 | 277.4 | 274.8 | 276.2 | 281.3 | 234.2 | 382.5
560 | 385 | 520.3 | 273.9 | 277.7 | 275.1 | 277.1 | 281.5 | 234.5 | 382.7
561 | 386 | 520.6 | 274.2 | 277.9 | 275.4 | 278.1 | 281.9 | 234.8 | 383
562 | 387 | 520.9 | 274.5 | 278.2 | 275.8 | 279 | 282.2 | 235.1 | 383.2
563 | 388 | 521 | 274.7 | 278.5 | 276.1 | 279.9 | 282.5 | 235.3 | 383.3
564 | 389 | 521.1 | 275 | 278.8 | 276.5 | 280.7 | 282.9 | 235.7 | 383.5
565 | 390 | 521.1 | 275.2 | 279.1 | 276.8 | 281.5 | 283.3 | 236 | 383.7
566 | 391 | 521.2 | 275.4 | 279.4 | 277.2 | 282.3 | 283.7 | 236 | 383.9
567 | 392 | 521.4 | 275.6 | 279.6 | 277.5 | 283.1 | 284.1 | 236.3 | 384.1
568 | 393 | 521.4 | 275.8 | 279.9 | 277.9 | 283.9 | 284.5 | 236.6 | 384.3
569 | 394 | 521.3 | 276.1 | 280.1 | 278.3 | 284.5 | 284.8 | 236.9 | 384.5
570 | 395 | 521.3 | 276.3 | 280.4 | 278.7 | 285.2 | 285.1 | 237.3 | 384.6
571 | 396 | 521.2 | 276.6 | 280.6 | 279.1 | 285.9 | 285.3 | 237.6 | 384.8
572 | 397 | 521.1 | 276.8 | 280.9 | 279.4 | 286.5 | 285.6 | 237.9 | 385
573 | 398 | 520.9 | 277.1 | 281.1 | 279.8 | 287.2 | 285.9 | 238.1 | 385.1
574 | 399 | 520.7 | 277.4 | 281.4 | 280.2 | 287.7 | 286.3 | 238.3 | 385.3
575 | 400 | 520.5 | 277.7 | 281.6 | 280.6 | 288.2 | 286.6 | 238.6 | 385.4
576 | 401 | 520.3 | 278 | 281.8 | 281 | 288.8 | 287 | 238.7 | 385.6
577 | 402 | 520.1 | 278.3 | 282.1 | 281.3 | 289.3 | 287.3 | 239 | 385.8
578 | 403 | 520 | 278.5 | 282.3 | 281.7 | 289.9 | 287.6 | 239.4 | 386
579 | 404 | 520 | 278.8 | 282.6 | 282.1 | 290.4 | 287.8 | 239.8 | 386.1
580 | 405 | 519.9 | 279.2 | 282.8 | 282.5 | 291 | 288.1 | 240 | 386.3
581 | 406 | 519.9 | 279.5 | 283 | 283 | 291.5 | 288.4 | 240.3 | 386.5
582 | 407 | 520 | 279.8 | 283.3 | 283.5 | 292 | 288.6 | 240.6 | 386.7
583 | 408 | 519.8 | 280.2 | 283.6 | 283.9 | 292.5 | 288.9 | 240.9 | 386.9
584 | 409 | 519.6 | 280.5 | 283.8 | 284.3 | 292.9 | 289.1 | 241.2 | 387.1
585 | 410 | 519.4 | 280.8 | 284 | 284.7 | 293.4 | 289.3 | 241.5 | 387.3
586 | 411 | 519.2 | 281.2 | 284.3 | 285.1 | 293.8 | 289.6 | 241.8 | 387.4
587 | 412 | 519.1 | 281.5 | 284.6 | 285.5 | 294.2 | 290 | 242.1 | 387.6
588 | 413 | 519.1 | 281.8 | 284.8 | 285.9 | 294.7 | 290.1 | 242.4 | 387.8
589 | 414 | 519.1 | 282.2 | 285.1 | 286.3 | 295.2 | 290.5 | 242.6 | 388
590 | 415 | 519.4 | 282.5 | 285.3 | 286.7 | 295.6 | 290.7 | 242.9 | 388.2
591 | 416 | 519.7 | 282.9 | 285.7 | 287 | 296 | 290.9 | 243.2 | 388.3
592 | 417 | 519.9 | 283.2 | 286 | 287.3 | 296.4 | 291.2 | 243.5 | 388.5
593 | 418 | 520.1 | 283.5 | 286.3 | 287.6 | 296.8 | 291.5 | 243.8 | 388.7
594 | 419 | 520.5 | 283.8 | 286.5 | 287.9 | 297.2 | 291.9 | 244.1 | 388.9
595 | 420 | 520.7 | 284.2 | 286.9 | 288.2 | 297.6 | 292.4 | 244.4 | 389
596 | 421 | 520.8 | 284.5 | 287.2 | 288.5 | 297.9 | 292.9 | 244.8 | 389.2
597 | 422 | 520.9 | 284.9 | 287.5 | 288.8 | 298.3 | 293.3 | 245.1 | 389.4
598 | 423 | 521.1 | 285.2 | 287.8 | 289.1 | 298.6 | 293.5 | 245.5 | 389.5
599 | 424 | 521.3 | 285.6 | 288.1 | 289.4 | 298.9 | 293.8 | 245.8 | 389.7
600 | 425 | 521.4 | 285.9 | 288.7 | 289.6 | 299.3 | 294.1 | 246.1 | 389.9
601 | 426 | 521.6 | 286.3 | 289 | 290 | 299.6 | 294.3 | 246.4 | 390.1
602 | 427 | 521.9 | 286.6 | 289.3 | 290.3 | 300 | 294.5 | 246.7 | 390.3
603 | 428 | 522 | 287 | 289.6 | 290.6 | 300.4 | 294.8 | 247.1 | 390.4
604 | 429 | 522 | 287.4 | 289.9 | 290.9 | 300.7 | 295.1 | 247.4 | 390.6
605 | 430 | 521.8 | 287.7 | 290.2 | 291.2 | 301.1 | 295.2 | 247.8 | 390.8
606 | 431 | 521.7 | 288.1 | 290.6 | 291.5 | 301.4 | 295.4 | 248.2 | 391.1
607 | 432 | 521.7 | 288.5 | 291 | 291.9 | 301.7 | 295.6 | 248.5 | 391.3
608 | 433 | 521.6 | 288.8 | 291.3 | 292.2 | 302.1 | 295.9 | 248.8 | 391.4
609 | 434 | 521.5 | 289.2 | 291.7 | 292.5 | 302.4 | 296.2 | 249.2 | 391.6
610 | 435 | 521.5 | 289.5 | 292 | 292.9 | 302.7 | 296.7 | 249.5 | 391.8
611 | 436 | 521.4 | 289.9 | 292.4 | 293.3 | 303.1 | 297.1 | 249.9 | 392
612 | 437 | 521.4 | 290.3 | 292.8 | 293.6 | 303.5 | 297.5 | 250.2 | 392.2
613 | 438 | 521.5 | 290.7 | 293.1 | 293.9 | 303.8 | 297.9 | 250.5 | 392.3
614 | 439 | 521.5 | 291.1 | 293.5 | 294.3 | 304.1 | 298.2 | 250.8 | 392.5
615 | 440 | 521.5 | 291.5 | 293.9 | 294.6 | 304.4 | 298.5 | 251.1 | 392.7
616 | 441 | 521.3 | 291.9 | 294.3 | 294.9 | 304.8 | 298.8 | 251.5 | 392.8
617 | 442 | 521.4 | 292.3 | 294.8 | 295.2 | 305.1 | 299 | 251.7 | 393
618 | 443 | 521.6 | 292.7 | 295.2 | 295.6 | 305.4 | 299.2 | 252 | 393.1
619 | 444 | 521.7 | 293.1 | 295.6 | 295.9 | 305.8 | 299.7 | 252.3 | 393.3
620 | 445 | 521.7 | 293.5 | 296 | 296.2 | 306.1 | 300 | 252.6 | 393.5
621 | 446 | 521.9 | 293.9 | 296.4 | 296.5 | 306.5 | 300.4 | 253 | 393.6
622 | 447 | 522.2 | 294.2 | 296.8 | 296.8 | 306.8 | 300.7 | 253.2 | 393.8
623 | 448 | 522.3 | 294.6 | 297.2 | 297.1 | 307.2 | 301.2 | 253.5 | 394
624 | 449 | 522.3 | 295 | 297.7 | 297.4 | 307.5 | 301.5 | 253.8 | 394.1
625 | 450 | 522.3 | 295.4 | 298 | 297.8 | 307.8 | 301.9 | 254.1 | 394.3
626 | 451 | 522.6 | 295.7 | 298.5 | 298.1 | 308.2 | 302.3 | 254.4 | 394.4
627 | 452 | 522.5 | 296.1 | 298.9 | 298.4 | 308.5 | 302.7 | 254.7 | 394.6
628 | 453 | 522.4 | 296.5 | 299.3 | 298.8 | 308.8 | 303.1 | 254.9 | 394.8
629 | 454 | 522.4 | 296.9 | 299.8 | 299.1 | 309.2 | 303.5 | 255.1 | 395
630 | 455 | 522.5 | 297.3 | 300.2 | 299.5 | 309.6 | 303.8 | 255.3 | 395.1
631 | 456 | 522.5 | 297.7 | 300.7 | 299.8 | 309.9 | 304.2 | 255.5 | 395.3
632 | 457 | 522.6 | 298.1 | 301.1 | 300.2 | 310.2 | 304.5 | 255.8 | 395.4
633 | 458 | 522.6 | 298.5 | 301.6 | 300.5 | 310.6 | 304.8 | 256 | 395.6
634 | 459 | 522.5 | 298.9 | 302.1 | 300.9 | 311 | 305.1 | 256.2 | 395.8
635 | 460 | 522.5 | 299.2 | 302.6 | 301.2 | 311.4 | 305.4 | 256.5 | 395.9
636 | 461 | 522.5 | 299.7 | 303 | 301.5 | 311.7 | 305.7 | 256.8 | 396.1
637 | 462 | 522.5 | 300 | 303.5 | 301.9 | 312.1 | 305.9 | 257.1 | 396.2
638 | 463 | 522.5 | 300.4 | 303.9 | 302.2 | 312.4 | 306.1 | 257.2 | 396.4
639 | 464 | 522.4 | 300.8 | 304.3 | 302.6 | 312.8 | 306.3 | 257.5 | 396.6
640 | 465 | 522.2 | 301.2 | 304.8 | 302.9 | 313.1 | 306.6 | 257.8 | 396.7
641 | 466 | 522.2 | 301.6 | 305.3 | 303.2 | 313.5 | 307.1 | 257.9 | 396.9
642 | 467 | 522.1 | 302 | 305.7 | 303.6 | 313.9 | 307.5 | 258.1 | 397
643 | 468 | 521.9 | 302.4 | 306.2 | 304 | 314.3 | 308 | 258.3 | 397.1
644 | 469 | 521.6 | 302.8 | 306.6 | 304.3 | 314.7 | 308.4 | 258.5 | 397.3
645 | 470 | 521.2 | 303.2 | 307.1 | 304.7 | 315.1 | 308.6 | 258.6 | 397.4
646 | 471 | 521.1 | 303.6 | 307.6 | 305.1 | 315.5 | 308.8 | 258.8 | 397.6
647 | 472 | 521.1 | 304 | 308 | 305.4 | 315.8 | 309.1 | 259 | 397.7
648 | 473 | 521.1 | 304.4 | 308.5 | 305.8 | 316.2 | 309.5 | 259.1 | 397.9
649 | 474 | 521 | 304.8 | 308.9 | 306.2 | 316.6 | 309.8 | 259.4 | 398
650 | 475 | 520.6 | 305.2 | 309.4 | 306.6 | 317 | 310.1 | 259.6 | 398.1
651 | 476 | 520.4 | 305.6 | 309.8 | 307 | 317.4 | 310.3 | 259.8 | 398.3
652 | 477 | 520.4 | 306 | 310.3 | 307.4 | 317.7 | 310.6 | 260.1 | 398.4
653 | 478 | 520.4 | 306.4 | 310.7 | 307.8 | 318.1 | 310.9 | 260.3 | 398.5
654 | 479 | 520.3 | 306.8 | 311.2 | 308.2 | 318.5 | 311.1 | 260.6 | 398.6
655 | 480 | 520.2 | 307.2 | 311.7 | 308.6 | 318.9 | 311.4 | 260.7 | 398.6
656 | 481 | 520 | 307.6 | 312.2 | 309 | 319.4 | 311.6 | 260.9 | 398.8
657 | 482 | 519.8 | 308 | 312.6 | 309.3 | 319.8 | 312 | 261.1 | 398.9
658 | 483 | 519.9 | 308.4 | 313.1 | 309.7 | 320.1 | 312.2 | 261.3 | 399
659 | 484 | 519.8 | 308.8 | 313.6 | 310.1 | 320.5 | 312.4 | 261.5 | 399.2
660 | 485 | 519.6 | 309.2 | 314 | 310.5 | 320.9 | 312.6 | 261.7 | 399.3
661 | 486 | 519.6 | 309.5 | 314.5 | 311 | 321.3 | 312.9 | 261.9 | 399.4
662 | 487 | 519.7 | 309.9 | 315 | 311.3 | 321.8 | 313.1 | 262.2 | 399.5
663 | 488 | 519.8 | 310.2 | 315.4 | 311.7 | 322.2 | 313.4 | 262.4 | 399.6
664 | 489 | 519.7 | 310.6 | 315.9 | 312.1 | 322.6 | 313.6 | 262.5 | 399.7
665 | 490 | 519.8 | 311 | 316.3 | 312.5 | 323 | 313.9 | 262.7 | 399.8
666 | 491 | 520 | 311.3 | 316.8 | 312.9 | 323.4 | 314.2 | 262.7 | 399.9
667 | 492 | 520 | 311.7 | 317.3 | 313.3 | 323.8 | 314.4 | 262.8 | 400.1
668 | 493 | 520.3 | 312 | 317.7 | 313.7 | 324.2 | 314.7 | 262.9 | 400.2
669 | 494 | 520.6 | 312.4 | 318.2 | 314.1 | 324.7 | 315 | 263.1 | 400.3
670 | 495 | 520.6 | 312.8 | 318.7 | 314.6 | 325.1 | 315.3 | 263.3 | 400.3
671 | 496 | 520.5 | 313.2 | 319.1 | 315 | 325.6 | 315.5 | 263.4 | 400.5
672 | 497 | 520.5 | 313.5 | 319.6 | 315.4 | 326 | 315.8 | 263.7 | 400.6
673 | 498 | 520.4 | 313.9 | 320 | 315.8 | 326.4 | 316.1 | 263.9 | 400.8
674 | 499 | 520.4 | 314.3 | 320.4 | 316.2 | 326.9 | 316.3 | 264.1 | 400.8
675 | 500 | 520.4 | 314.7 | 320.9 | 316.6 | 327.3 | 316.5 | 264.4 | 400.9
676 | 501 | 520.4 | 315.1 | 321.3 | 317 | 327.7 | 316.8 | 264.7 | 401
677 | 502 | 520.4 | 315.4 | 321.7 | 317.4 | 328.1 | 317 | 264.8 | 401.1
678 | 503 | 520.5 | 315.8 | 322.2 | 317.8 | 328.5 | 317.3 | 265.1 | 401.2
679 | 504 | 520.6 | 316.1 | 322.7 | 318.3 | 328.9 | 317.6 | 265.4 | 401.3
680 | 505 | 520.6 | 316.5 | 323.1 | 318.7 | 329.3 | 317.9 | 265.8 | 401.4
681 | 506 | 520.7 | 316.9 | 323.5 | 319.1 | 329.7 | 318.3 | 265.9 | 401.5
682 | 507 | 520.8 | 317.3 | 323.9 | 319.6 | 330.1 | 318.6 | 266.2 | 401.6
683 | 508 | 520.9 | 317.6 | 324.4 | 320 | 330.6 | 318.8 | 266.4 | 401.7
684 | 509 | 520.8 | 317.9 | 324.8 | 320.5 | 331 | 319.1 | 266.5 | 401.8
685 | 510 | 520.8 | 318.3 | 325.2 | 320.9 | 331.4 | 319.3 | 266.8 | 401.9
686 | 511 | 521 | 318.7 | 325.6 | 321.3 | 331.8 | 319.6 | 266.9 | 402
687 | 512 | 521 | 319 | 326 | 321.7 | 332.2 | 319.9 | 267.1 | 402.2
688 | 513 | 521.1 | 319.4 | 326.4 | 322.1 | 332.6 | 320.1 | 267.2 | 402.3
689 | 514 | 521.2 | 319.8 | 326.8 | 322.5 | 333 | 320.3 | 267.3 | 402.3
690 | 515 | 521.2 | 320.2 | 327.2 | 322.9 | 333.4 | 320.6 | 267.5 | 402.5
691 | 516 | 521.3 | 320.5 | 327.6 | 323.3 | 333.8 | 320.9 | 267.7 | 402.6
692 | 517 | 521.4 | 320.9 | 328.1 | 323.7 | 334.2 | 321.3 | 267.9 | 402.7
693 | 518 | 521.6 | 321.3 | 328.5 | 324 | 334.6 | 321.6 | 268.2 | 402.8
694 | 519 | 521.9 | 321.6 | 329 | 324.4 | 334.9 | 322 | 268.3 | 402.9
695 | 520 | 521.9 | 322 | 329.4 | 324.8 | 335.3 | 322.3 | 268.6 | 403
696 | 521 | 521.8 | 322.4 | 329.8 | 325.2 | 335.7 | 322.6 | 268.9 | 403.1
697 | 522 | 521.7 | 322.7 | 330.2 | 325.5 | 336 | 322.9 | 269.1 | 403.3
698 | 523 | 521.5 | 323.1 | 330.6 | 325.9 | 336.4 | 323.2 | 269.4 | 403.4
699 | 524 | 521.5 | 323.5 | 331 | 326.2 | 336.7 | 323.4 | 269.7 | 403.6
700 | 525 | 521.4 | 323.9 | 331.4 | 326.5 | 337.1 | 323.7 | 269.9 | 403.7
701 | 526 | 521.5 | 324.3 | 331.9 | 326.9 | 337.5 | 324.1 | 270.2 | 403.8
702 | 527 | 521.5 | 324.6 | 332.3 | 327.3 | 337.9 | 324.4 | 270.3 | 403.8
703 | 528 | 521.6 | 325 | 332.7 | 327.6 | 338.2 | 324.7 | 270.5 | 403.9
704 | 529 | 521.5 | 325.3 | 333.1 | 327.9 | 338.5 | 325 | 270.8 | 404
705 | 530 | 521.7 | 325.7 | 333.5 | 328.1 | 338.9 | 325.3 | 271 | 404.2
706 | 531 | 521.9 | 326 | 333.8 | 328.5 | 339.2 | 325.6 | 271.2 | 404.2
707 | 532 | 521.7 | 326.3 | 334.2 | 328.8 | 339.5 | 325.9 | 271.4 | 404.3
708 | 533 | 521.8 | 326.6 | 334.6 | 329.1 | 339.9 | 326.2 | 271.7 | 404.4
709 | 534 | 521.8 | 327 | 335 | 329.3 | 340.2 | 326.5 | 271.8 | 404.5
710 | 535 | 521.6 | 327.3 | 335.4 | 329.6 | 340.5 | 326.8 | 272 | 404.6
711 | 536 | 521.5 | 327.7 | 335.8 | 329.9 | 340.9 | 327.1 | 272.2 | 404.7
712 | 537 | 521.4 | 328 | 336.2 | 330.3 | 341.2 | 327.3 | 272.4 | 404.8
713 | 538 | 521.3 | 328.3 | 336.6 | 330.6 | 341.6 | 327.6 | 272.5 | 404.9
714 | 539 | 521.2 | 328.6 | 336.9 | 330.8 | 341.9 | 327.8 | 272.7 | 405
715 | 540 | 521.1 | 329 | 337.3 | 331.1 | 342.3 | 328.1 | 272.9 | 405.1
716 | 541 | 520.9 | 329.3 | 337.7 | 331.3 | 342.7 | 328.3 | 273.1 | 405.2
717 | 542 | 520.7 | 329.6 | 338 | 331.6 | 343 | 328.5 | 273.3 | 405.2
718 | 543 | 520.5 | 330 | 338.4 | 332 | 343.4 | 328.8 | 273.5 | 405.3
719 | 544 | 520.6 | 330.3 | 338.7 | 332.3 | 343.7 | 329.1 | 273.7 | 405.4
720 | 545 | 520.5 | 330.6 | 339.1 | 332.7 | 344 | 329.4 | 273.9 | 405.5
721 | 546 | 520.4 | 330.9 | 339.5 | 333 | 344.3 | 329.7 | 274.1 | 405.6
722 | 547 | 520.6 | 331.3 | 339.8 | 333.3 | 344.6 | 329.9 | 274.3 | 405.7
723 | 548 | 520.7 | 331.6 | 340.1 | 333.7 | 344.9 | 330.2 | 274.4 | 405.8
724 | 549 | 520.7 | 331.9 | 340.5 | 334 | 345.2 | 330.4 | 274.6 | 405.9
725 | 550 | 520.8 | 332.3 | 340.8 | 334.3 | 345.5 | 330.6 | 274.9 | 406
726 | 551 | 521 | 332.6 | 341.2 | 334.7 | 345.8 | 330.7 | 275 | 406
727 | 552 | 521.1 | 332.9 | 341.5 | 335 | 346.2 | 330.9 | 275.2 | 406.1
728 | 553 | 521 | 333.3 | 341.9 | 335.3 | 346.5 | 330.9 | 275.5 | 406.2
729 | 554 | 521.2 | 333.6 | 342.2 | 335.6 | 346.8 | 331.1 | 275.8 | 406.3
730 | 555 | 521.3 | 333.9 | 342.6 | 335.9 | 347.1 | 331.3 | 276 | 406.3
731 | 556 | 521.5 | 334.2 | 342.9 | 336.2 | 347.4 | 331.6 | 276.2 | 406.4
732 | 557 | 521.6 | 334.6 | 343.3 | 336.5 | 347.6 | 331.9 | 276.3 | 406.5
733 | 558 | 521.9 | 334.9 | 343.6 | 336.8 | 347.9 | 332.2 | 276.5 | 406.6
734 | 559 | 522.2 | 335.2 | 343.9 | 337.1 | 348.2 | 332.6 | 276.8 | 406.7
735 | 560 | 522.2 | 335.5 | 344.3 | 337.4 | 348.5 | 332.9 | 276.9 | 406.7
736 | 561 | 522.4 | 335.8 | 344.6 | 337.7 | 348.8 | 333.2 | 277.2 | 406.8
737 | 562 | 522.4 | 336.1 | 345 | 338 | 349 | 333.5 | 277.3 | 406.8
738 | 563 | 522.4 | 336.4 | 345.3 | 338.3 | 349.3 | 333.7 | 277.6 | 406.9
739 | 564 | 522.6 | 336.7 | 345.6 | 338.6 | 349.5 | 333.9 | 277.8 | 407
740 | 565 | 522.5 | 337.1 | 345.9 | 338.9 | 349.8 | 334 | 278 | 407.1
741 | 566 | 522.5 | 337.4 | 346.3 | 339.2 | 350.1 | 334.2 | 278.4 | 407.2
742 | 567 | 522.6 | 337.7 | 346.6 | 339.5 | 350.4 | 334.4 | 278.6 | 407.2
743 | 568 | 522.8 | 338 | 346.9 | 339.8 | 350.7 | 334.5 | 278.9 | 407.3
744 | 569 | 523.1 | 338.3 | 347.3 | 340.1 | 350.9 | 334.7 | 279 | 407.3
745 | 570 | 523.3 | 338.6 | 347.6 | 340.4 | 351.2 | 334.8 | 279.3 | 407.4
746 | 571 | 523.4 | 338.9 | 347.9 | 340.7 | 351.5 | 335 | 279.5 | 407.5
747 | 572 | 523.3 | 339.3 | 348.2 | 341 | 351.7 | 335.2 | 279.7 | 407.5
748 | 573 | 523.3 | 339.6 | 348.5 | 341.2 | 352 | 335.4 | 279.9 | 407.6
749 | 574 | 523.2 | 339.9 | 348.8 | 341.5 | 352.3 | 335.6 | 280 | 407.6
750 | 575 | 523 | 340.2 | 349.1 | 341.8 | 352.5 | 335.8 | 280.3 | 407.7
751 | 576 | 522.7 | 340.5 | 349.4 | 342.1 | 352.8 | 336.1 | 280.4 | 407.8
752 | 577 | 522.6 | 340.8 | 349.7 | 342.4 | 353 | 336.4 | 280.6 | 407.8
753 | 578 | 522.5 | 341.1 | 350 | 342.7 | 353.2 | 336.7 | 280.8 | 407.8
754 | 579 | 522.5 | 341.4 | 350.4 | 343 | 353.4 | 337 | 281 | 407.9
755 | 580 | 522.5 | 341.6 | 350.7 | 343.2 | 353.6 | 337.3 | 281.3 | 408
756 | 581 | 522.7 | 341.9 | 351 | 343.5 | 353.8 | 337.5 | 281.6 | 408.1
757 | 582 | 522.6 | 342.2 | 351.3 | 343.8 | 354 | 337.6 | 281.8 | 408.1
758 | 583 | 522.5 | 342.5 | 351.6 | 344 | 354.3 | 337.8 | 281.9 | 408.1
759 | 584 | 522.4 | 342.8 | 351.9 | 344.3 | 354.5 | 338 | 282 | 408.2
760 | 585 | 522.4 | 343.1 | 352.2 | 344.6 | 354.7 | 338.2 | 282.2 | 408.2
761 | 586 | 522.3 | 343.4 | 352.5 | 344.9 | 354.9 | 338.4 | 282.5 | 408.2
762 | 587 | 522.3 | 343.6 | 352.7 | 345.2 | 355.1 | 338.8 | 282.7 | 408.3
763 | 588 | 522.2 | 343.9 | 353 | 345.4 | 355.3 | 339.1 | 282.7 | 408.3
764 | 589 | 522.4 | 344.2 | 353.3 | 345.7 | 355.5 | 339.4 | 282.8 | 408.4
765 | 590 | 522.5 | 344.5 | 353.6 | 345.9 | 355.7 | 339.6 | 282.9 | 408.4
766 | 591 | 522.5 | 344.8 | 353.7 | 346.2 | 356 | 339.8 | 283.2 | 408.5
767 | 592 | 522.4 | 345.1 | 354 | 346.4 | 356.2 | 340 | 283.4 | 408.5
768 | 593 | 522.3 | 345.4 | 354.3 | 346.7 | 356.4 | 340.3 | 283.6 | 408.5
769 | 594 | 522.2 | 345.7 | 354.5 | 346.9 | 356.6 | 340.5 | 283.9 | 408.5
770 | 595 | 522.1 | 346 | 354.8 | 347.2 | 356.8 | 340.7 | 284 | 408.6
771 | 596 | 522 | 346.2 | 355.1 | 347.4 | 357 | 340.9 | 284.3 | 408.7
772 | 597 | 521.8 | 346.5 | 355.3 | 347.7 | 357.2 | 341.1 | 284.5 | 408.7
773 | 598 | 521.8 | 346.8 | 355.5 | 348 | 357.5 | 341.2 | 284.6 | 408.8
774 | 599 | 521.7 | 347.1 | 355.8 | 348.2 | 357.7 | 341.3 | 284.8 | 408.8
775 | 600 | 521.8 | 347.3 | 356 | 348.5 | 358 | 341.6 | 285 | 408.8
776 | 601 | 521.7 | 347.6 | 356.3 | 348.7 | 358.3 | 341.8 | 285.2 | 408.9
777 | 602 | 521.4 | 347.9 | 356.6 | 349 | 358.6 | 342 | 285.4 | 408.9
778 | 603 | 521.4 | 348.2 | 356.9 | 349.2 | 358.9 | 342.1 | 285.6 | 409
779 | 604 | 521.3 | 348.5 | 357.2 | 349.5 | 359.1 | 342.3 | 285.8 | 409
780 | 605 | 521.3 | 348.8 | 357.4 | 349.8 | 359.4 | 342.5 | 286.1 | 409.1
781 | 606 | 521.2 | 349 | 357.5 | 350 | 359.6 | 342.7 | 286.2 | 409.1
782 | 607 | 521.2 | 349.3 | 357.6 | 350.3 | 359.9 | 342.9 | 286.3 | 409.2
783 | 608 | 521.1 | 349.6 | 357.7 | 350.5 | 360.1 | 343.1 | 286.4 | 409.2
784 | 609 | 521.1 | 349.9 | 357.8 | 350.8 | 360.3 | 343.3 | 286.6 | 409.2
785 | 610 | 521.3 | 350.1 | 358 | 351 | 360.5 | 343.5 | 286.8 | 409.1
786 | 611 | 521.5 | 350.4 | 358.1 | 351.3 | 360.7 | 343.6 | 287 | 409.1
787 | 612 | 521.6 | 350.8 | 358.3 | 351.5 | 360.9 | 343.8 | 287.2 | 409.2
788 | 613 | 521.5 | 351 | 358.6 | 351.7 | 361 | 343.9 | 287.4 | 409.2
789 | 614 | 521.6 | 351.3 | 358.9 | 352 | 361.1 | 344.1 | 287.6 | 409.2
790 | 615 | 521.7 | 351.5 | 359.3 | 352.2 | 361.2 | 344.2 | 287.7 | 409.2
791 | 616 | 521.5 | 351.8 | 359.6 | 352.4 | 361.3 | 344.3 | 287.9 | 409.2
792 | 617 | 521.5 | 352 | 360 | 352.6 | 361.4 | 344.4 | 288.1 | 409.3
793 | 618 | 521.6 | 352.2 | 360.3 | 352.8 | 361.6 | 344.5 | 288.3 | 409.3
794 | 619 | 521.8 | 352.5 | 360.6 | 353 | 361.7 | 344.7 | 288.5 | 409.3
795 | 620 | 521.8 | 352.7 | 360.9 | 353.2 | 361.9 | 344.9 | 288.7 | 409.4
796 | 621 | 521.7 | 353 | 361.1 | 353.4 | 362.1 | 345.1 | 288.9 | 409.4
797 | 622 | 521.6 | 353.2 | 361.4 | 353.6 | 362.4 | 345.2 | 289.2 | 409.5
798 | 623 | 521.8 | 353.5 | 361.7 | 353.8 | 362.7 | 345.3 | 289.5 | 409.5
799 | 624 | 521.7 | 353.7 | 361.9 | 354 | 363 | 345.4 | 289.7 | 409.6
800 | 625 | 521.4 | 354 | 362.2 | 354.2 | 363.2 | 345.5 | 289.8 | 409.6
801 | 626 | 521.1 | 354.2 | 362.5 | 354.5 | 363.5 | 345.6 | 289.9 | 409.7
802 | 627 | 521 | 354.5 | 362.7 | 354.8 | 363.7 | 345.7 | 290 | 409.7
803 | 628 | 521 | 354.8 | 363 | 355.2 | 364 | 345.9 | 290.1 | 409.8
804 | 629 | 521 | 355 | 363.3 | 355.5 | 364.2 | 346.1 | 290.1 | 409.8
805 | 630 | 521 | 355.3 | 363.5 | 355.8 | 364.5 | 346.3 | 290.3 | 409.8
806 | 631 | 521.1 | 355.7 | 363.7 | 356 | 364.7 | 346.5 | 290.4 | 409.9
807 | 632 | 521.1 | 356 | 364 | 356.2 | 365 | 346.6 | 290.5 | 409.9
808 | 633 | 521.2 | 356.4 | 364.3 | 356.5 | 365.2 | 346.7 | 290.7 | 410
809 | 634 | 521.3 | 356.6 | 364.6 | 356.8 | 365.4 | 347 | 290.9 | 410
810 | 635 | 521.3 | 356.8 | 365 | 357 | 365.7 | 347.2 | 291.1 | 410.1
811 | 636 | 521.4 | 357 | 365.3 | 357.2 | 365.9 | 347.4 | 291.2 | 410.1
812 | 637 | 521.7 | 357.3 | 365.6 | 357.4 | 366.1 | 347.5 | 291.4 | 410.2
813 | 638 | 522 | 357.6 | 366.1 | 357.8 | 366.4 | 347.7 | 291.5 | 410.2
814 | 639 | 522.3 | 357.9 | 366.5 | 358 | 366.6 | 347.7 | 291.7 | 410.3
815 | 640 | 522.6 | 358.6 | 367 | 358.1 | 366.9 | 347.8 | 291.8 | 410.3
816 | 641 | 523 | 359.1 | 367.4 | 358.4 | 367.1 | 347.8 | 292 | 410.3
817 | 642 | 523.4 | 359.5 | 367.8 | 358.6 | 367.3 | 348 | 292.3 | 410.1
818 | 643 | 523.4 | 359.8 | 368.3 | 358.8 | 367.5 | 348.1 | 292.6 | 410.1
819 | 644 | 523.5 | 360.1 | 368.6 | 359 | 367.6 | 348.1 | 292.7 | 410.1
820 | 645 | 523.7 | 360.3 | 369 | 359.1 | 367.7 | 348.2 | 293 | 410.2
821 | 646 | 523.8 | 360.5 | 369.3 | 359.3 | 367.9 | 348.2 | 293.1 | 410.2
822 | 647 | 523.7 | 360.7 | 369.7 | 359.5 | 368 | 348.3 | 293.2 | 410.2
823 | 648 | 523.6 | 360.8 | 370.1 | 359.7 | 368.2 | 348.4 | 293.4 | 410.2
824 | 649 | 523.4 | 361 | 370.5 | 360 | 368.3 | 348.6 | 293.5 | 410.2
825 | 650 | 523.2 | 361.1 | 370.8 | 360.2 | 368.5 | 348.7 | 293.7 | 410.3
826 | 651 | 523.2 | 361.3 | 371.1 | 360.4 | 368.7 | 348.7 | 293.8 | 410.4
827 | 652 | 523.1 | 361.5 | 371.4 | 360.6 | 368.9 | 348.9 | 293.9 | 410.4
828 | 653 | 522.9 | 361.8 | 371.6 | 360.8 | 369.1 | 348.9 | 294.1 | 410.4
829 | 654 | 522.9 | 362.1 | 371.9 | 361 | 369.4 | 349 | 294.3 | 410.5
830 | 655 | 522.8 | 362.6 | 372.2 | 361.2 | 369.6 | 349.2 | 294.4 | 410.5
831 | 656 | 522.7 | 363 | 372.5 | 361.4 | 369.8 | 349.2 | 294.5 | 410.5
832 | 657 | 522.4 | 363.3 | 372.8 | 361.7 | 370 | 349.3 | 294.7 | 410.5
833 | 658 | 522.4 | 363.5 | 373.2 | 361.8 | 370.2 | 349.4 | 294.8 | 410.6
834 | 659 | 522.3 | 363.7 | 373.5 | 362 | 370.4 | 349.4 | 294.8 | 410.6
835 | 660 | 522 | 363.9 | 373.8 | 362.2 | 370.6 | 349.4 | 294.9 | 410.6
836 | 661 | 521.9 | 364.1 | 374.2 | 362.4 | 370.9 | 349.5 | 295 | 410.7
837 | 662 | 521.8 | 364.4 | 374.4 | 362.6 | 371.1 | 349.6 | 295 | 410.8
838 | 663 | 521.8 | 364.6 | 374.7 | 362.8 | 371.3 | 349.6 | 295.2 | 410.8
839 | 664 | 521.8 | 364.9 | 375 | 363 | 371.5 | 349.7 | 295.3 | 410.9
840 | 665 | 522 | 365.1 | 375.4 | 363.2 | 371.7 | 349.8 | 295.4 | 410.9
841 | 666 | 522 | 365.3 | 375.7 | 363.4 | 371.9 | 349.9 | 295.5 | 410.9
842 | 667 | 522.2 | 365.5 | 375.9 | 363.6 | 372.1 | 350 | 295.6 | 411
843 | 668 | 522.5 | 365.8 | 376.2 | 363.8 | 372.3 | 350 | 295.7 | 411
844 | 669 | 522.7 | 366 | 376.4 | 364 | 372.6 | 350.1 | 295.8 | 411
845 | 670 | 522.8 | 366.2 | 376.7 | 364.2 | 372.8 | 350.2 | 295.9 | 411.1
846 | 671 | 522.8 | 366.5 | 377 | 364.3 | 373 | 350.3 | 295.9 | 411.1
847 | 672 | 522.9 | 366.7 | 377.2 | 364.5 | 373.2 | 350.5 | 296 | 411.1
848 | 673 | 523 | 367 | 377.5 | 364.8 | 373.4 | 350.6 | 296.2 | 411.2
849 | 674 | 522.9 | 367.3 | 377.7 | 365 | 373.6 | 350.6 | 296.3 | 411.3
850 | 675 | 522.9 | 367.7 | 378 | 365.1 | 373.8 | 350.7 | 296.3 | 411.3
851 | 676 | 522.8 | 367.9 | 378.2 | 365.4 | 374.1 | 350.8 | 296.4 | 411.4
852 | 677 | 522.8 | 368.1 | 378.5 | 365.6 | 374.3 | 350.9 | 296.5 | 411.4
853 | 678 | 522.8 | 368.4 | 378.8 | 365.8 | 374.6 | 351 | 296.6 | 411.4
854 | 679 | 522.8 | 368.7 | 379 | 366.1 | 374.8 | 351.2 | 296.7 | 411.5
855 | 680 | 522.8 | 368.9 | 379.3 | 366.3 | 375.1 | 351.2 | 296.8 | 411.6
856 | 681 | 522.7 | 369.2 | 379.5 | 366.6 | 375.4 | 351.3 | 296.8 | 411.7
857 | 682 | 522.8 | 369.5 | 379.8 | 366.8 | 375.7 | 351.3 | 296.9 | 411.7
858 | 683 | 522.9 | 369.7 | 380 | 367.1 | 376 | 351.4 | 296.9 | 411.7
859 | 684 | 522.8 | 370 | 380.3 | 367.3 | 376.3 | 351.4 | 297.1 | 411.8
860 | 685 | 522.7 | 370.3 | 380.5 | 367.6 | 376.6 | 351.4 | 297.2 | 411.8
861 | 686 | 522.5 | 370.6 | 380.8 | 367.8 | 376.9 | 351.5 | 297.3 | 411.8
862 | 687 | 522.5 | 370.9 | 381 | 368.1 | 377.2 | 351.5 | 297.4 | 411.9
863 | 688 | 522.5 | 371.3 | 381.3 | 368.3 | 377.4 | 351.6 | 297.5 | 411.9
864 | 689 | 522.5 | 371.7 | 381.5 | 368.6 | 377.7 | 351.6 | 297.7 | 412
865 | 690 | 522.6 | 371.9 | 381.8 | 368.8 | 378 | 351.6 | 297.7 | 412
866 | 691 | 522.5 | 372.2 | 382.1 | 369 | 378.2 | 351.6 | 297.9 | 412.1
867 | 692 | 522.4 | 372.4 | 382.3 | 369.3 | 378.5 | 351.6 | 298 | 412.2
868 | 693 | 522.5 | 372.7 | 382.6 | 369.5 | 378.7 | 351.6 | 298.1 | 412.2
869 | 694 | 522.4 | 372.9 | 382.9 | 369.8 | 378.9 | 351.7 | 298.2 | 412.2
870 | 695 | 522.3 | 373.2 | 383.1 | 370 | 379.2 | 351.9 | 298.2 | 412.3
871 | 696 | 522.3 | 373.5 | 383.4 | 370.3 | 379.4 | 352 | 298.3 | 412.3
872 | 697 | 522.3 | 373.7 | 383.6 | 370.5 | 379.5 | 352.1 | 298.5 | 412.3
873 | 698 | 522.4 | 374 | 383.8 | 370.7 | 379.7 | 352.3 | 298.5 | 412.4
874 | 699 | 522.7 | 374.2 | 384.1 | 370.9 | 379.9 | 352.4 | 298.6 | 412.4
875 | 700 | 522.7 | 374.4 | 384.3 | 371.1 | 380.1 | 352.6 | 298.8 | 412.5
876 | 701 | 522.8 | 374.6 | 384.6 | 371.3 | 380.2 | 352.7 | 298.9 | 412.5
877 | 702 | 522.8 | 374.8 | 384.8 | 371.5 | 380.4 | 352.8 | 299 | 412.6
878 | 703 | 522.8 | 375 | 385 | 371.7 | 380.5 | 352.9 | 299.2 | 412.6
879 | 704 | 522.9 | 375.2 | 385.3 | 371.9 | 380.6 | 352.9 | 299.3 | 412.6
880 | 705 | 523.1 | 375.4 | 385.5 | 372.1 | 380.8 | 353 | 299.4 | 412.6
881 | 706 | 523.1 | 375.6 | 385.8 | 372.2 | 380.9 | 353.1 | 299.6 | 412.5
882 | 707 | 523.1 | 375.8 | 385.9 | 372.4 | 381 | 353.1 | 299.7 | 412.6
883 | 708 | 523 | 376 | 386.2 | 372.6 | 381 | 353.1 | 299.8 | 412.6
884 | 709 | 523.2 | 376.2 | 386.4 | 372.7 | 381.1 | 353.2 | 300 | 412.7
885 | 710 | 523.4 | 376.3 | 386.7 | 372.9 | 381.1 | 353.2 | 300.1 | 412.7
886 | 711 | 523.4 | 376.5 | 386.9 | 373 | 381.2 | 353.2 | 300.2 | 412.7
887 | 712 | 523.3 | 376.7 | 387.1 | 373.1 | 381.2 | 353.2 | 300.3 | 412.6
888 | 713 | 523.3 | 376.9 | 387.4 | 373.3 | 381.2 | 353.3 | 300.4 | 412.6
889 | 714 | 523.1 | 377.1 | 387.6 | 373.4 | 381.2 | 353.3 | 300.5 | 412.6
890 | 715 | 523.1 | 377.4 | 387.8 | 373.5 | 381.3 | 353.1 | 300.6 | 412.5
891 | 716 | 523.1 | 377.5 | 388.1 | 373.6 | 381.2 | 353 | 300.7 | 412.5
892 | 717 | 522.9 | 377.7 | 388.3 | 373.7 | 381.3 | 352.9 | 300.9 | 412.5
893 | 718 | 522.6 | 377.9 | 388.5 | 373.8 | 381.3 | 352.8 | 301 | 412.5
894 | 719 | 522.5 | 378.1 | 388.7 | 373.9 | 381.2 | 352.7 | 301.1 | 412.5
895 | 720 | 522.4 | 378.4 | 388.9 | 374 | 381.2 | 352.6 | 301.2 | 412.5
896 | 721 | 522.6 | 378.6 | 389.2 | 374 | 381.1 | 352.6 | 301.3 | 412.5
897 | 722 | 522.7 | 378.7 | 389.7 | 374 | 380.8 | 352.5 | 301.4 | 412.5
898 | 723 | 522.7 | 378.9 | 389.9 | 374.1 | 380.7 | 352.4 | 301.5 | 412.6
899 | 724 | 522.8 | 379.1 | 390.2 | 374.2 | 380.8 | 352.5 | 301.7 | 412.6
900 | 725 | 522.7 | 379.4 | 390.4 | 374.3 | 380.8 | 352.5 | 301.8 | 412.6
901 | 726 | 522.7 | 379.6 | 390.7 | 374.3 | 380.8 | 352.5 | 301.8 | 412.6
902 | 727 | 522.9 | 379.8 | 390.9 | 374.4 | 380.9 | 352.7 | 302 | 412.6
903 | 728 | 522.8 | 380 | 391.2 | 374.5 | 381 | 352.7 | 302.1 | 412.7
904 | 729 | 522.8 | 380.3 | 391.4 | 374.6 | 381 | 352.8 | 302.3 | 412.7
905 | 730 | 522.9 | 380.5 | 391.7 | 374.7 | 381.2 | 353 | 302.4 | 412.8
906 | 731 | 523 | 380.6 | 391.9 | 374.8 | 381.3 | 353.1 | 302.5 | 412.8
907 | 732 | 523.2 | 380.7 | 392.2 | 374.9 | 381.4 | 353.2 | 302.6 | 412.8
908 | 733 | 523.3 | 380.9 | 392.4 | 374.9 | 381.5 | 353.3 | 302.7 | 412.9
909 | 734 | 523.3 | 381.1 | 392.7 | 375 | 381.6 | 353.4 | 302.9 | 412.9
910 | 735 | 523.2 | 381.3 | 392.9 | 375.1 | 381.7 | 353.5 | 303 | 412.9
911 | 736 | 523.2 | 381.5 | 393.1 | 375.2 | 381.8 | 353.6 | 303.1 | 413
912 | 737 | 523 | 381.7 | 393.1 | 375.3 | 381.9 | 353.7 | 303.1 | 413
913 | 738 | 522.9 | 381.8 | 393 | 375.4 | 382 | 353.7 | 303.2 | 413
914 | 739 | 522.9 | 382 | 393 | 375.5 | 382 | 353.7 | 303.3 | 413
915 | 740 | 522.8 | 382.2 | 393 | 375.6 | 382.1 | 353.7 | 303.3 | 413
916 | 741 | 522.7 | 382.3 | 393.1 | 375.7 | 382.1 | 353.7 | 303.4 | 413
917 | 742 | 522.6 | 382.5 | 393.1 | 375.7 | 382.2 | 353.8 | 303.6 | 413.1
918 | 743 | 522.4 | 382.7 | 393.2 | 375.8 | 382.3 | 353.8 | 303.7 | 413.2
919 | 744 | 522.1 | 382.9 | 393.3 | 375.9 | 382.5 | 353.9 | 303.8 | 413.2
920 | 745 | 522.2 | 383 | 393.5 | 376 | 382.6 | 354 | 304 | 413.3
921 | 746 | 522.5 | 383.2 | 393.7 | 376 | 382.7 | 354 | 304.1 | 413.3
922 | 747 | 522.6 | 383.4 | 393.8 | 376.1 | 382.9 | 353.9 | 304.3 | 413.4
923 | 748 | 522.5 | 383.6 | 393.9 | 376.2 | 383 | 353.9 | 304.4 | 413.3
924 | 749 | 522.6 | 383.7 | 394.1 | 376.3 | 383.2 | 353.9 | 304.6 | 413.4
925 | 750 | 522.6 | 384 | 394.3 | 376.4 | 383.3 | 353.9 | 304.7 | 413.4
926 | 751 | 522.6 | 384.1 | 394.4 | 376.5 | 383.5 | 353.9 | 304.8 | 413.5
927 | 752 | 522.7 | 384.3 | 394.6 | 376.6 | 383.6 | 354 | 305 | 413.5
928 | 753 | 522.7 | 384.5 | 394.7 | 376.7 | 383.7 | 354 | 305.1 | 413.5
929 | 754 | 522.8 | 384.7 | 394.9 | 376.8 | 383.8 | 354.2 | 305.2 | 413.5
930 | 755 | 523 | 384.9 | 395 | 376.9 | 384 | 354.3 | 305.4 | 413.6
931 | 756 | 523.3 | 385 | 395.2 | 377 | 384.1 | 354.2 | 305.5 | 413.6
932 | 757 | 523.4 | 385.1 | 395.3 | 377.1 | 384.2 | 354.2 | 305.6 | 413.6
933 | 758 | 523.5 | 385.3 | 395.5 | 377.2 | 384.3 | 354.2 | 305.7 | 413.7
934 | 759 | 523.4 | 385.4 | 395.6 | 377.2 | 384.4 | 354.2 | 305.8 | 413.7
935 | 760 | 523.3 | 385.5 | 395.8 | 377.3 | 384.5 | 354.2 | 306 | 413.7
936 | 761 | 523.3 | 385.7 | 395.9 | 377.4 | 384.6 | 354.3 | 306.1 | 413.7
937 | 762 | 523.3 | 385.9 | 396.1 | 377.5 | 384.6 | 354.3 | 306.2 | 413.7
938 | 763 | 523.2 | 386.1 | 396.2 | 377.6 | 384.8 | 354.4 | 306.3 | 413.7
939 | 764 | 523.1 | 386.3 | 396.4 | 377.7 | 384.8 | 354.5 | 306.5 | 413.8
940 | 765 | 523 | 386.5 | 396.5 | 377.7 | 385 | 354.7 | 306.6 | 413.8
941 | 766 | 522.9 | 386.7 | 396.7 | 377.8 | 385.1 | 354.8 | 306.7 | 413.9
942 | 767 | 522.9 | 386.9 | 396.9 | 377.9 | 385.2 | 354.8 | 306.8 | 413.9
943 | 768 | 522.9 | 387.1 | 397.1 | 378 | 385.4 | 354.8 | 306.9 | 413.9
944 | 769 | 523 | 387.4 | 397.3 | 378.1 | 385.5 | 354.8 | 307.1 | 413.9
945 | 770 | 523 | 387.6 | 397.5 | 378.1 | 385.7 | 354.8 | 307.2 | 413.8
946 | 771 | 523 | 387.9 | 397.6 | 378.2 | 385.8 | 354.9 | 307.4 | 413.9
947 | 772 | 523 | 388.2 | 397.8 | 378.3 | 385.9 | 354.9 | 307.5 | 413.9
948 | 773 | 522.9 | 388.5 | 398 | 378.4 | 386.1 | 355.1 | 307.7 | 414
949 | 774 | 522.8 | 388.7 | 398.1 | 378.5 | 386.2 | 355.2 | 307.8 | 414
950 | 775 | 522.8 | 389 | 398.3 | 378.6 | 386.4 | 355.4 | 307.9 | 414
951 | 776 | 522.7 | 389.3 | 398.5 | 378.7 | 386.5 | 355.5 | 308 | 414
952 | 777 | 522.5 | 389.6 | 398.7 | 378.7 | 386.6 | 355.6 | 308.2 | 413.9
953 | 778 | 522.4 | 389.9 | 398.8 | 378.8 | 386.7 | 355.6 | 308.3 | 413.9
954 | 779 | 522.5 | 390.1 | 399 | 378.9 | 386.8 | 355.6 | 308.5 | 413.9
955 | 780 | 522.6 | 390.4 | 399.2 | 379 | 386.8 | 355.6 | 308.7 | 413.9
956 | 781 | 522.8 | 390.7 | 399.4 | 379.1 | 386.9 | 355.7 | 308.8 | 413.9
957 | 782 | 523.1 | 390.9 | 399.6 | 379.1 | 386.9 | 355.8 | 308.9 | 413.9
958 | 783 | 523 | 391.2 | 399.8 | 379.2 | 386.9 | 356 | 309.1 | 413.9
959 | 784 | 522.9 | 391.4 | 399.9 | 379.3 | 386.9 | 356.1 | 309.2 | 413.9
960 | 785 | 523.2 | 391.7 | 400.1 | 379.3 | 386.9 | 356.2 | 309.3 | 413.6
961 | 786 | 523.5 | 391.9 | 400.3 | 379.4 | 386.9 | 356.3 | 309.4 | 413.7
962 | 787 | 523.8 | 392.2 | 400.5 | 379.5 | 386.9 | 356.3 | 309.5 | 413.7
963 | 788 | 523.8 | 392.4 | 400.7 | 379.5 | 386.9 | 356.4 | 309.6 | 413.6
964 | 789 | 523.8 | 392.7 | 400.8 | 379.6 | 386.9 | 356.5 | 309.6 | 413.6
965 | 790 | 523.8 | 392.9 | 401 | 379.6 | 386.8 | 356.6 | 309.7 | 413.5
966 | 791 | 523.8 | 393.2 | 401.2 | 379.7 | 386.8 | 356.8 | 309.8 | 413.4
967 | 792 | 523.7 | 393.4 | 401.4 | 379.7 | 386.7 | 356.9 | 310 | 413.3
968 | 793 | 523.7 | 393.7 | 401.6 | 379.7 | 386.7 | 357.1 | 310 | 413.3
969 | 794 | 523.6 | 393.9 | 401.7 | 379.8 | 386.6 | 357.1 | 310.2 | 413.2
970 | 795 | 523.5 | 394.1 | 401.9 | 379.8 | 386.5 | 357.2 | 310.3 | 413.1
971 | 796 | 523.4 | 394.4 | 402.1 | 379.8 | 386.5 | 357.3 | 310.4 | 412.9
972 | 797 | 523.4 | 394.6 | 402.3 | 379.9 | 386.4 | 357.4 | 310.2 | 412.7
973 | 798 | 523.6 | 394.8 | 402.5 | 379.9 | 386.4 | 357.3 | 310.2 | 412.6
974 | 799 | 523.9 | 395 | 402.7 | 379.9 | 386.3 | 357.2 | 310.3 | 412.4
975 | 800 | 524 | 395.2 | 402.9 | 380 | 386.2 | 357.1 | 310.5 | 412.2
976 | 801 | 524.1 | 395.4 | 403 | 380 | 386.1 | 357.1 | 310.7 | 412.2
977 | 802 | 524.2 | 395.6 | 403.2 | 380 | 386.1 | 357.2 | 310.8 | 412.1
978 | 803 | 524.1 | 395.7 | 403.4 | 380 | 386 | 357.2 | 311 | 412
979 | 804 | 523.9 | 395.9 | 403.6 | 380.1 | 385.9 | 357.2 | 311.1 | 411.8
980 | 805 | 523.8 | 396.1 | 403.7 | 380.1 | 385.8 | 357.2 | 311.3 | 411.5
981 | 806 | 523.7 | 396.3 | 403.9 | 380.1 | 385.7 | 357.2 | 311.4 | 411.4
982 | 807 | 523.5 | 396.5 | 404 | 380.2 | 385.6 | 357.3 | 311.6 | 411.4
983 | 808 | 523.3 | 396.7 | 404.2 | 380.2 | 385.6 | 357.5 | 311.8 | 411.3
984 | 809 | 523.3 | 396.8 | 404.4 | 380.2 | 385.5 | 357.6 | 311.9 | 411.2
985 | 810 | 523.5 | 397 | 404.5 | 380.3 | 385.4 | 357.7 | 312.1 | 411.1
986 | 811 | 523.5 | 397.2 | 404.7 | 380.3 | 385.3 | 357.8 | 312.2 | 411.1
987 | 812 | 523.5 | 397.4 | 404.8 | 380.4 | 385.2 | 358 | 312.3 | 411
988 | 813 | 523.3 | 397.5 | 405 | 380.4 | 385.1 | 358.1 | 312.5 | 410.9
989 | 814 | 523.4 | 397.7 | 405.2 | 380.4 | 385 | 358.3 | 312.6 | 410.9
990 | 815 | 523.5 | 397.9 | 405.4 | 380.5 | 385 | 358.3 | 312.7 | 410.9
991 | 816 | 523.4 | 398.1 | 405.6 | 380.5 | 384.9 | 358.2 | 312.8 | 410.7
992 | 817 | 523.5 | 398.2 | 405.8 | 380.6 | 384.8 | 358.1 | 313 | 410.6
993 | 818 | 523.3 | 398.4 | 405.9 | 380.6 | 384.7 | 358 | 313.1 | 410.5
994 | 819 | 523 | 398.6 | 406.1 | 380.7 | 384.6 | 358 | 313.2 | 410.5
995 | 820 | 523.1 | 398.7 | 406.2 | 380.7 | 384.5 | 358 | 313.4 | 410.4
996 | 821 | 523 | 398.9 | 406.4 | 380.7 | 384.5 | 358 | 313.5 | 410.3
997 | 822 | 523 | 399 | 406.5 | 380.8 | 384.4 | 357.9 | 313.6 | 410.3
998 | 823 | 523.1 | 399.2 | 406.7 | 380.8 | 384.3 | 357.9 | 313.8 | 410.3
999 | 824 | 523.2 | 399.4 | 406.8 | 380.9 | 384.2 | 357.8 | 314 | 410.2
1000 | 825 | 523.4 | 399.5 | 406.9 | 380.9 | 384.1 | 357.8 | 314.1 | 410.2
1001 | 826 | 523.3 | 399.7 | 407.1 | 380.9 | 384.1 | 357.9 | 314.3 | 410.3
1002 | 827 | 523.2 | 399.8 | 407.2 | 381 | 384 | 358 | 314.5 | 410.3
1003 | 828 | 523.2 | 400 | 407.3 | 381 | 384 | 358.1 | 314.6 | 410.2
1004 | 829 | 523.1 | 400.1 | 407.4 | 381.1 | 384 | 358.3 | 314.8 | 410.2
1005 | 830 | 523.1 | 400.3 | 407.5 | 381.1 | 384.1 | 358.2 | 315 | 410.2
1006 | 831 | 523.1 | 400.4 | 407.7 | 381.2 | 384.1 | 358.1 | 315.2 | 410.2
1007 | 832 | 523.2 | 400.6 | 407.8 | 381.2 | 384.1 | 358 | 315.3 | 410.2
1008 | 833 | 523.4 | 400.7 | 407.9 | 381.3 | 384.1 | 357.9 | 315.5 | 410.3
1009 | 834 | 523.6 | 400.9 | 408 | 381.4 | 384.2 | 357.8 | 315.7 | 410.3
1010 | 835 | 523.4 | 401.1 | 408.1 | 381.4 | 384.3 | 357.8 | 315.8 | 410.4
1011 | 836 | 523.3 | 401.2 | 408.3 | 381.5 | 384.3 | 357.8 | 315.9 | 410.5
1012 | 837 | 523.3 | 401.3 | 408.4 | 381.5 | 384.4 | 357.9 | 316.1 | 410.5
1013 | 838 | 523.4 | 401.5 | 408.5 | 381.6 | 384.5 | 358 | 316.2 | 410.6
1014 | 839 | 523.6 | 401.6 | 408.7 | 381.7 | 384.6 | 358.1 | 316.3 | 410.6
1015 | 840 | 523.6 | 401.8 | 408.8 | 381.7 | 384.7 | 358.2 | 316.4 | 410.6
1016 | 841 | 523.7 | 402 | 409 | 381.8 | 384.7 | 358.4 | 316.6 | 410.7
1017 | 842 | 523.8 | 402.1 | 409.1 | 381.9 | 384.8 | 358.5 | 316.6 | 410.7
1018 | 843 | 523.8 | 402.3 | 409.2 | 382 | 384.9 | 358.4 | 316.8 | 410.7
1019 | 844 | 523.7 | 402.5 | 409.3 | 382 | 384.9 | 358.4 | 316.9 | 410.8
1020 | 845 | 523.5 | 402.7 | 409.4 | 382.1 | 385 | 358.4 | 317 | 410.8
1021 | 846 | 523.4 | 402.8 | 409.5 | 382.2 | 385.1 | 358.5 | 317.1 | 410.8
1022 | 847 | 523.3 | 403 | 409.6 | 382.3 | 385.2 | 358.6 | 317.2 | 410.8
1023 | 848 | 523.2 | 403.2 | 409.7 | 382.3 | 385.3 | 358.6 | 317.4 | 410.9
1024 | 849 | 523.4 | 403.3 | 409.8 | 382.4 | 385.4 | 358.8 | 317.5 | 411
1025 | 850 | 523.3 | 403.4 | 409.9 | 382.5 | 385.5 | 359 | 317.6 | 411.1
1026 | 851 | 523 | 403.6 | 410 | 382.6 | 385.7 | 359.2 | 317.7 | 411.2
1027 | 852 | 522.8 | 403.7 | 410.1 | 382.7 | 385.9 | 359.4 | 317.9 | 411.3
1028 | 853 | 522.8 | 403.8 | 410.3 | 382.8 | 386.1 | 359.6 | 318 | 411.5
1029 | 854 | 522.9 | 403.9 | 410.3 | 382.9 | 386.3 | 359.8 | 318.1 | 411.6
1030 | 855 | 523.1 | 404 | 410.4 | 383 | 386.5 | 360 | 318.2 | 411.6
1031 | 856 | 523 | 404.1 | 410.5 | 383.1 | 386.7 | 360.1 | 318.4 | 411.6
1032 | 857 | 523.1 | 404.3 | 410.6 | 383.2 | 386.9 | 360.2 | 318.5 | 411.7
1033 | 858 | 523.1 | 404.4 | 410.8 | 383.3 | 387.1 | 360.3 | 318.6 | 411.8
1034 | 859 | 523.2 | 404.5 | 410.8 | 383.4 | 387.3 | 360.5 | 318.7 | 411.8
1035 | 860 | 523.1 | 404.6 | 410.9 | 383.6 | 387.4 | 360.6 | 318.8 | 411.7
1036 | 861 | 523.1 | 404.8 | 411 | 383.7 | 387.6 | 360.8 | 319 | 411.9
1037 | 862 | 523.2 | 404.9 | 411.1 | 383.8 | 387.8 | 360.9 | 319.1 | 411.9
1038 | 863 | 523.4 | 405 | 411.2 | 383.9 | 387.9 | 361 | 319.2 | 412
1039 | 864 | 523.6 | 405.2 | 411.3 | 384 | 388 | 361.2 | 319.4 | 411.9
1040 | 865 | 523.6 | 405.3 | 411.4 | 384.1 | 388.1 | 361.3 | 319.5 | 411.8
1041 | 866 | 523.5 | 405.4 | 411.5 | 384.2 | 388.2 | 361.3 | 319.6 | 411.8
1042 | 867 | 523.7 | 405.5 | 411.6 | 384.3 | 388.3 | 361.5 | 319.7 | 411.9
1043 | 868 | 523.8 | 405.6 | 411.7 | 384.4 | 388.4 | 361.7 | 319.8 | 411.8
1044 | 869 | 523.7 | 405.7 | 411.8 | 384.5 | 388.5 | 361.9 | 319.8 | 411.8
1045 | 870 | 523.7 | 405.8 | 411.9 | 384.6 | 388.5 | 362.1 | 319.9 | 411.7
1046 | 871 | 523.8 | 406 | 411.9 | 384.6 | 388.6 | 362.1 | 320 | 411.7
1047 | 872 | 523.7 | 406.1 | 412 | 384.7 | 388.6 | 362.2 | 320 | 411.7
1048 | 873 | 523.4 | 406.2 | 412.1 | 384.8 | 388.7 | 362.2 | 320.2 | 411.6
1049 | 874 | 523.2 | 406.3 | 412.2 | 384.9 | 388.7 | 362.3 | 320.3 | 411.6
1050 | 875 | 523.1 | 406.4 | 412.3 | 384.9 | 388.7 | 362.3 | 320.4 | 411.6
1051 | 876 | 522.9 | 406.5 | 412.4 | 385 | 388.8 | 362.3 | 320.6 | 411.7
1052 | 877 | 522.6 | 406.6 | 412.5 | 385.1 | 388.8 | 362.2 | 320.7 | 411.8
1053 | 878 | 522.6 | 406.7 | 412.6 | 385.2 | 388.9 | 362.2 | 320.8 | 411.8
1054 | 879 | 522.5 | 406.8 | 412.7 | 385.2 | 388.9 | 362.1 | 320.9 | 411.8
1055 | 880 | 522.6 | 406.9 | 412.8 | 385.3 | 389 | 362.1 | 321 | 411.9
1056 | 881 | 522.7 | 407 | 412.9 | 385.3 | 389.1 | 362.1 | 321.1 | 412
1057 | 882 | 523 | 407.2 | 413 | 385.4 | 389.2 | 362 | 321.3 | 412
1058 | 883 | 523.2 | 407.3 | 413.1 | 385.5 | 389.2 | 361.9 | 321.4 | 412.1
1059 | 884 | 523.4 | 407.4 | 413.2 | 385.5 | 389.3 | 362 | 321.5 | 412.1
1060 | 885 | 523.6 | 407.5 | 413.2 | 385.6 | 389.4 | 362.1 | 321.7 | 412.1
1061 | 886 | 523.8 | 407.6 | 413.4 | 385.7 | 389.5 | 362.2 | 321.8 | 412.1
1062 | 887 | 523.9 | 407.7 | 413.4 | 385.7 | 389.6 | 362.4 | 321.9 | 412.2
1063 | 888 | 524 | 407.7 | 413.5 | 385.8 | 389.7 | 362.4 | 322 | 412.3
1064 | 889 | 524.1 | 407.8 | 413.6 | 385.9 | 389.7 | 362.4 | 322.2 | 412.4
1065 | 890 | 524.3 | 407.8 | 413.6 | 386 | 389.9 | 362.5 | 322.3 | 412.4
1066 | 891 | 524.5 | 407.9 | 413.7 | 386 | 389.9 | 362.6 | 322.5 | 412.5
1067 | 892 | 524.5 | 408 | 413.8 | 386.1 | 390 | 362.7 | 322.7 | 412.5
1068 | 893 | 524.3 | 408.1 | 413.9 | 386.2 | 390.1 | 362.8 | 322.8 | 412.5
1069 | 894 | 524.4 | 408.1 | 414 | 386.2 | 390.2 | 363 | 322.9 | 412.5
1070 | 895 | 524.5 | 408.2 | 414.1 | 386.3 | 390.2 | 363.1 | 323.1 | 412.6
1071 | 896 | 524.4 | 408.3 | 414.2 | 386.4 | 390.3 | 363.1 | 323.2 | 412.7
1072 | 897 | 524.1 | 408.4 | 414.2 | 386.5 | 390.4 | 363.2 | 323.3 | 412.8
1073 | 898 | 524.1 | 408.5 | 414.3 | 386.6 | 390.5 | 363.2 | 323.4 | 412.8
1074 | 899 | 524.1 | 408.7 | 414.4 | 386.7 | 390.5 | 363.2 | 323.5 | 412.8
1075 | 900 | 524 | 408.8 | 414.5 | 386.7 | 390.6 | 363.2 | 323.6 | 412.8
1076 | 901 | 524 | 408.9 | 414.5 | 386.8 | 390.7 | 363.1 | 323.6 | 412.8
1077 | 902 | 523.9 | 409.1 | 414.6 | 386.9 | 390.8 | 363.1 | 323.7 | 412.8
1078 | 903 | 523.8 | 409.2 | 414.7 | 387 | 390.9 | 363.2 | 323.8 | 412.9
1079 | 904 | 523.8 | 409.3 | 414.8 | 387.1 | 391 | 363.2 | 323.8 | 412.9
1080 | 905 | 523.7 | 409.4 | 414.9 | 387.1 | 391 | 363.2 | 323.9 | 412.8
1081 | 906 | 523.6 | 409.6 | 414.9 | 387.2 | 391 | 363.2 | 324 | 412.8
1082 | 907 | 523.6 | 409.7 | 414.9 | 387.3 | 391 | 363.3 | 324 | 412.8
1083 | 908 | 523.7 | 409.8 | 415 | 387.4 | 391 | 363.3 | 324 | 412.8
1084 | 909 | 523.4 | 409.9 | 415 | 387.5 | 391.1 | 363.3 | 324.1 | 412.7
1085 | 910 | 523.1 | 409.9 | 415 | 387.5 | 391.1 | 363.3 | 324.1 | 412.6
1086 | 911 | 523 | 410 | 415.1 | 387.6 | 391.1 | 363.2 | 324.1 | 412.6
1087 | 912 | 523 | 410.1 | 415.1 | 387.7 | 391.1 | 363.1 | 324.1 | 412.6
1088 | 913 | 522.9 | 410.2 | 415.1 | 387.8 | 391.1 | 363.2 | 324.2 | 412.6
1089 | 914 | 522.8 | 410.3 | 415.1 | 387.8 | 391.1 | 363.3 | 324.3 | 412.6
1090 | 915 | 522.6 | 410.4 | 415.2 | 387.9 | 391 | 363.5 | 324.4 | 412.6
1091 | 916 | 522.5 | 410.4 | 415.3 | 388 | 391 | 363.6 | 324.4 | 412.7
1092 | 917 | 522.6 | 410.5 | 415.3 | 388 | 391 | 363.9 | 324.5 | 412.7
1093 | 918 | 522.6 | 410.6 | 415.4 | 388.1 | 391 | 364.2 | 324.6 | 412.8
1094 | 919 | 522.4 | 410.7 | 415.4 | 388.2 | 391 | 364.3 | 324.7 | 412.8
1095 | 920 | 522.3 | 410.7 | 415.5 | 388.2 | 391.1 | 364.4 | 324.9 | 412.8
1096 | 921 | 522.5 | 410.8 | 415.6 | 388.3 | 391.1 | 364.3 | 325 | 412.9
1097 | 922 | 522.7 | 410.9 | 415.6 | 388.4 | 391.1 | 364.2 | 325 | 412.9
1098 | 923 | 522.8 | 410.9 | 415.6 | 388.4 | 391.1 | 364.2 | 325.1 | 412.8
1099 | 924 | 522.8 | 411 | 415.7 | 388.5 | 391.2 | 364.2 | 325.2 | 412.8
1100 | 925 | 523 | 411.1 | 415.8 | 388.6 | 391.2 | 364.3 | 325.4 | 412.8
1101 | 926 | 523 | 411.2 | 415.8 | 388.7 | 391.3 | 364.3 | 325.4 | 412.6
1102 | 927 | 522.9 | 411.2 | 415.9 | 388.8 | 391.3 | 364.4 | 325.5 | 412.6
1103 | 928 | 523 | 411.3 | 416 | 388.8 | 391.3 | 364.6 | 325.5 | 412.6
1104 | 929 | 523.1 | 411.4 | 416 | 388.9 | 391.3 | 364.8 | 325.6 | 412.6
1105 | 930 | 523.1 | 411.5 | 416.2 | 388.9 | 391.2 | 365 | 325.6 | 412.6
1106 | 931 | 523.1 | 411.5 | 416.4 | 389 | 391.1 | 365.2 | 325.7 | 412.6
1107 | 932 | 523.1 | 411.5 | 416.5 | 389 | 391 | 365.3 | 325.8 | 412.6
1108 | 933 | 523.2 | 411.6 | 416.6 | 389.1 | 391 | 365.4 | 325.8 | 412.5
1109 | 934 | 523.3 | 411.7 | 416.7 | 389.2 | 390.9 | 365.5 | 325.9 | 412.5
1110 | 935 | 523.1 | 411.8 | 416.8 | 389.3 | 390.9 | 365.6 | 326 | 412.5
1111 | 936 | 522.9 | 411.9 | 416.8 | 389.3 | 390.9 | 365.7 | 326.1 | 412.6
1112 | 937 | 522.8 | 412 | 417 | 389.4 | 390.9 | 365.7 | 326.2 | 412.6
1113 | 938 | 522.8 | 412.1 | 417.1 | 389.5 | 390.9 | 365.7 | 326.3 | 412.6
1114 | 939 | 522.6 | 412.2 | 417.1 | 389.5 | 390.9 | 365.7 | 326.4 | 412.7
1115 | 940 | 522.3 | 412.3 | 417.1 | 389.6 | 390.9 | 365.7 | 326.5 | 412.7
1116 | 941 | 522.1 | 412.4 | 417.1 | 389.7 | 390.9 | 365.6 | 326.5 | 412.8
1117 | 942 | 522 | 412.5 | 417.2 | 389.8 | 391 | 365.7 | 326.6 | 412.8
1118 | 943 | 521.9 | 412.6 | 417.3 | 389.9 | 391.1 | 365.8 | 326.7 | 412.8
1119 | 944 | 522.1 | 412.6 | 417.3 | 390 | 391.3 | 365.9 | 326.8 | 412.9
1120 | 945 | 522.2 | 412.7 | 417.5 | 390.1 | 391.4 | 365.8 | 326.8 | 413
1121 | 946 | 522 | 412.8 | 417.5 | 390.2 | 391.6 | 365.9 | 326.8 | 413
1122 | 947 | 521.9 | 412.9 | 417.6 | 390.3 | 391.7 | 365.9 | 326.8 | 413
1123 | 948 | 521.9 | 413 | 417.8 | 390.4 | 391.9 | 366 | 326.8 | 413.1
1124 | 949 | 522.1 | 413 | 417.8 | 390.5 | 392.1 | 366 | 326.9 | 413.1
1125 | 950 | 522.4 | 413.1 | 417.9 | 390.7 | 392.2 | 366 | 326.9 | 413.1
1126 | 951 | 522.8 | 413.2 | 418 | 390.8 | 392.4 | 366 | 327 | 413.1
1127 | 952 | 523.1 | 413.3 | 418.1 | 390.9 | 392.5 | 365.9 | 327 | 413.1
1128 | 953 | 523.4 | 413.4 | 418.1 | 391 | 392.6 | 365.8 | 327.1 | 413.1
1129 | 954 | 523.5 | 413.5 | 418.2 | 391.1 | 392.8 | 365.9 | 327.1 | 413.1
1130 | 955 | 523.7 | 413.6 | 418.3 | 391.2 | 392.9 | 366 | 327.3 | 413.1
1131 | 956 | 523.8 | 413.6 | 418.2 | 391.3 | 393 | 366 | 327.3 | 413.1
1132 | 957 | 523.9 | 413.7 | 418.2 | 391.4 | 393 | 366.1 | 327.4 | 413.1
1133 | 958 | 524.2 | 413.7 | 418.3 | 391.5 | 393.1 | 366.2 | 327.5 | 413.2
1134 | 959 | 524.3 | 413.8 | 418.3 | 391.6 | 393.1 | 366.4 | 327.5 | 413.2
1135 | 960 | 524.4 | 413.9 | 418.3 | 391.7 | 393.2 | 366.6 | 327.7 | 413.3
1136 | 961 | 524.3 | 414 | 418.3 | 391.8 | 393.3 | 366.6 | 327.8 | 413.3
1137 | 962 | 524.3 | 414.1 | 418.4 | 392 | 393.3 | 366.5 | 327.9 | 413.3
1138 | 963 | 524.2 | 414.1 | 418.5 | 392 | 393.4 | 366.5 | 327.9 | 413.4
1139 | 964 | 524.2 | 414.2 | 418.5 | 392.2 | 393.4 | 366.5 | 328 | 413.5
1140 | 965 | 524.4 | 414.3 | 418.7 | 392.3 | 393.5 | 366.6 | 328.1 | 413.6
1141 | 966 | 524.4 | 414.4 | 418.9 | 392.4 | 393.6 | 366.8 | 328.2 | 413.6
1142 | 967 | 524.4 | 414.4 | 419 | 392.5 | 393.7 | 367 | 328.3 | 413.8
1143 | 968 | 524.3 | 414.5 | 419 | 392.6 | 393.7 | 367.2 | 328.4 | 413.9
1144 | 969 | 524.2 | 414.5 | 419 | 392.7 | 393.8 | 367.3 | 328.4 | 414
1145 | 970 | 524 | 414.6 | 419.1 | 392.8 | 394 | 367.4 | 328.6 | 414
1146 | 971 | 523.8 | 414.7 | 419.2 | 392.9 | 394.1 | 367.4 | 328.8 | 414
1147 | 972 | 523.6 | 414.8 | 419.2 | 393 | 394.3 | 367.5 | 328.9 | 414.1
1148 | 973 | 523.5 | 414.9 | 419.2 | 393.2 | 394.4 | 367.5 | 328.9 | 414.1
1149 | 974 | 523.6 | 415 | 419.3 | 393.3 | 394.5 | 367.6 | 329 | 414.2
1150 | 975 | 523.6 | 415.1 | 419.4 | 393.4 | 394.7 | 367.6 | 329.1 | 414.2
1151 | 976 | 523.4 | 415.2 | 419.4 | 393.5 | 394.8 | 367.7 | 329.1 | 414.3
1152 | 977 | 523.4 | 415.3 | 419.5 | 393.6 | 394.9 | 367.8 | 329.2 | 414.4
1153 | 978 | 523.1 | 415.4 | 419.5 | 393.7 | 395.1 | 367.9 | 329.2 | 414.4
1154 | 979 | 523 | 415.6 | 419.6 | 393.8 | 395.3 | 367.9 | 329.2 | 414.5
1155 | 980 | 523 | 415.7 | 419.6 | 393.9 | 395.4 | 368 | 329.2 | 414.5
1156 | 981 | 522.9 | 415.9 | 419.7 | 394.1 | 395.6 | 368.1 | 329.3 | 414.5
1157 | 982 | 522.9 | 416 | 419.8 | 394.2 | 395.7 | 368.2 | 329.3 | 414.5
1158 | 983 | 522.8 | 416.1 | 419.8 | 394.3 | 395.9 | 368.3 | 329.3 | 414.6
1159 | 984 | 522.8 | 416.3 | 419.9 | 394.4 | 396 | 368.3 | 329.4 | 414.6
1160 | 985 | 522.7 | 416.4 | 420 | 394.5 | 396.1 | 368.3 | 329.4 | 414.7
1161 | 986 | 522.4 | 416.5 | 420 | 394.6 | 396.2 | 368.4 | 329.4 | 414.6
1162 | 987 | 522.3 | 416.6 | 420 | 394.7 | 396.3 | 368.5 | 329.5 | 414.7
1163 | 988 | 522.1 | 416.7 | 420 | 394.8 | 396.4 | 368.5 | 329.6 | 414.7
1164 | 989 | 522.2 | 416.8 | 420 | 394.9 | 396.5 | 368.6 | 329.6 | 414.7
1165 | 990 | 522.3 | 416.8 | 420 | 395 | 396.6 | 368.5 | 329.6 | 414.7
1166 | 991 | 522.5 | 416.8 | 420 | 395.1 | 396.6 | 368.5 | 329.7 | 414.7
1167 | 992 | 522.5 | 416.9 | 420.1 | 395.1 | 396.6 | 368.5 | 329.7 | 414.8
1168 | 993 | 522.6 | 417 | 420.1 | 395.2 | 396.7 | 368.5 | 329.8 | 414.8
1169 | 994 | 522.7 | 417 | 420.1 | 395.3 | 396.7 | 368.6 | 329.8 | 414.9
1170 | 995 | 522.7 | 417.1 | 420.1 | 395.4 | 396.8 | 368.6 | 329.8 | 414.9
1171 | 996 | 522.5 | 417.1 | 420.2 | 395.5 | 396.8 | 368.7 | 329.9 | 414.9
1172 | 997 | 522.4 | 417.2 | 420.1 | 395.5 | 396.9 | 368.7 | 329.8 | 415
1173 | 998 | 522.3 | 417.2 | 420.1 | 395.6 | 397 | 368.8 | 329.8 | 415
1174 | 999 | 522.1 | 417.2 | 420 | 395.7 | 397.1 | 369 | 329.8 | 415
1175 | 1000 | 521.9 | 417.3 | 420.1 | 395.8 | 397.2 | 369.2 | 329.8 | 414.9
1176 | 1001 | 521.9 | 417.3 | 420.2 | 395.9 | 397.4 | 369.2 | 329.8 | 414.9
1177 | 1002 | 522 | 417.4 | 420.2 | 396 | 397.5 | 369.3 | 329.8 | 414.9
1178 | 1003 | 522 | 417.5 | 420.2 | 396 | 397.6 | 369.3 | 329.8 | 415
1179 | 1004 | 522 | 417.5 | 420.2 | 396.1 | 397.8 | 369.4 | 329.8 | 415
1180 | 1005 | 522.2 | 417.5 | 420.3 | 396.2 | 397.9 | 369.4 | 329.9 | 415
1181 | 1006 | 522.3 | 417.7 | 420.4 | 396.3 | 398 | 369.5 | 330 | 415
1182 | 1007 | 522.3 | 417.8 | 420.4 | 396.4 | 398.1 | 369.5 | 330.1 | 415
1183 | 1008 | 522.3 | 417.9 | 420.4 | 396.5 | 398.2 | 369.5 | 330.2 | 415
1184 | 1009 | 522.1 | 417.9 | 420.4 | 396.5 | 398.3 | 369.4 | 330.2 | 415.1
1185 | 1010 | 522 | 418 | 420.4 | 396.6 | 398.4 | 369.4 | 330.2 | 415.1
1186 | 1011 | 522 | 418 | 420.5 | 396.7 | 398.5 | 369.4 | 330.3 | 415.2
1187 | 1012 | 521.9 | 418.1 | 420.7 | 396.8 | 398.6 | 369.3 | 330.3 | 415.4
1188 | 1013 | 521.9 | 418.1 | 420.9 | 396.9 | 398.7 | 369.3 | 330.3 | 415.4
1189 | 1014 | 521.9 | 418.1 | 421 | 396.9 | 398.8 | 369.4 | 330.4 | 415.4
1190 | 1015 | 522 | 418.1 | 421 | 397 | 398.9 | 369.5 | 330.4 | 415.4
1191 | 1016 | 522 | 418.1 | 421.1 | 397.1 | 399.1 | 369.5 | 330.5 | 415.4
1192 | 1017 | 522.1 | 418.2 | 421 | 397.2 | 399.2 | 369.6 | 330.5 | 415.4
1193 | 1018 | 522.1 | 418.3 | 421 | 397.3 | 399.3 | 369.6 | 330.5 | 415.4
1194 | 1019 | 522.3 | 418.4 | 421.1 | 397.4 | 399.4 | 369.6 | 330.6 | 415.4
1195 | 1020 | 522.5 | 418.5 | 421.2 | 397.5 | 399.5 | 369.6 | 330.7 | 415.4
1196 | 1021 | 522.5 | 418.5 | 421.3 | 397.5 | 399.5 | 369.6 | 330.6 | 415.4
1197 | 1022 | 522.6 | 418.5 | 421.4 | 397.6 | 399.6 | 369.6 | 330.7 | 415.5
1198 | 1023 | 522.8 | 418.5 | 421.4 | 397.7 | 399.6 | 369.6 | 330.8 | 415.5
1199 | 1024 | 523 | 418.6 | 421.4 | 397.7 | 399.7 | 369.6 | 330.8 | 415.5
1200 | 1025 | 523.2 | 418.7 | 421.5 | 397.8 | 399.7 | 369.5 | 330.8 | 415.5
1201 | 1026 | 523 | 418.7 | 421.5 | 397.9 | 399.8 | 369.5 | 330.9 | 415.5
1202 | 1027 | 523 | 418.8 | 421.6 | 398 | 399.9 | 369.5 | 330.9 | 415.5
1203 | 1028 | 522.9 | 418.9 | 421.7 | 398.1 | 399.9 | 369.5 | 331 | 415.7
1204 | 1029 | 522.9 | 419 | 421.8 | 398.1 | 400 | 369.5 | 331.2 | 415.8
1205 | 1030 | 522.8 | 419 | 422 | 398.2 | 400.1 | 369.5 | 331.2 | 415.8
1206 | 1031 | 522.8 | 419.1 | 422 | 398.3 | 400.2 | 369.4 | 331.2 | 415.9
1207 | 1032 | 522.9 | 419.2 | 421.9 | 398.4 | 400.3 | 369.3 | 331.2 | 415.9
1208 | 1033 | 523.1 | 419.2 | 421.9 | 398.5 | 400.4 | 369.1 | 331.3 | 416
1209 | 1034 | 523.2 | 419.3 | 422 | 398.6 | 400.5 | 368.9 | 331.3 | 415.8
1210 | 1035 | 523.2 | 419.4 | 422 | 398.6 | 400.6 | 368.7 | 331.4 | 415.8
1211 | 1036 | 523.4 | 419.5 | 422 | 398.7 | 400.7 | 368.6 | 331.4 | 415.9
1212 | 1037 | 523.4 | 419.5 | 422 | 398.8 | 400.7 | 368.5 | 331.4 | 415.9
1213 | 1038 | 523.5 | 419.6 | 421.9 | 398.9 | 400.8 | 368.4 | 331.3 | 415.7
1214 | 1039 | 523.5 | 419.7 | 421.9 | 399 | 400.8 | 368.1 | 331.3 | 415.8
1215 | 1040 | 523.5 | 419.7 | 421.9 | 399.1 | 400.8 | 367.9 | 331.4 | 415.7
1216 | 1041 | 523.5 | 419.8 | 421.9 | 399.2 | 400.8 | 367.8 | 331.5 | 415.6
1217 | 1042 | 523.7 | 419.8 | 422 | 399.2 | 400.8 | 367.8 | 331.6 | 415.5
1218 | 1043 | 523.7 | 419.8 | 422.1 | 399.3 | 400.7 | 367.8 | 331.7 | 415.4
1219 | 1044 | 523.6 | 419.8 | 422.1 | 399.4 | 400.7 | 367.9 | 331.7 | 415.3
1220 | 1045 | 523.6 | 419.8 | 422.3 | 399.5 | 400.6 | 368.1 | 331.8 | 415.2
1221 | 1046 | 523.6 | 419.8 | 422.4 | 399.5 | 400.6 | 368.1 | 331.9 | 415.2
1222 | 1047 | 523.3 | 419.8 | 422.5 | 399.6 | 400.5 | 368.2 | 331.9 | 415.2
1223 | 1048 | 523.1 | 419.8 | 422.5 | 399.7 | 400.5 | 368.1 | 332 | 415.2
1224 | 1049 | 522.8 | 419.8 | 422.5 | 399.7 | 400.5 | 368.1 | 332 | 415.2
1225 | 1050 | 522.5 | 419.9 | 422.5 | 399.8 | 400.5 | 368.2 | 332 | 415.2
1226 | 1051 | 522.5 | 419.9 | 422.4 | 399.9 | 400.5 | 368.1 | 332.1 | 415.1
1227 | 1052 | 522.5 | 420 | 422.4 | 399.9 | 400.5 | 368.1 | 332.1 | 415.1
1228 | 1053 | 522.4 | 420 | 422.3 | 400 | 400.4 | 368 | 332.2 | 415
1229 | 1054 | 522.2 | 420.1 | 422.3 | 400 | 400.4 | 368 | 332.2 | 415
1230 | 1055 | 522.3 | 420.1 | 422.3 | 400.1 | 400.4 | 368 | 332.2 | 414.9
1231 | 1056 | 522.1 | 420.2 | 422.2 | 400.2 | 400.4 | 367.9 | 332.3 | 414.7
1232 | 1057 | 521.9 | 420.2 | 422.2 | 400.2 | 400.3 | 367.7 | 332.3 | 414.7
1233 | 1058 | 521.6 | 420.3 | 422.1 | 400.3 | 400.3 | 367.7 | 332.3 | 414.7
1234 | 1059 | 521.6 | 420.4 | 422.1 | 400.4 | 400.3 | 367.7 | 332.4 | 414.6
1235 | 1060 | 521.6 | 420.4 | 422.1 | 400.4 | 400.3 | 367.8 | 332.4 | 414.5
1236 | 1061 | 521.5 | 420.4 | 422.2 | 400.4 | 400.3 | 367.9 | 332.6 | 414.4
1237 | 1062 | 521.4 | 420.5 | 422.3 | 400.5 | 400.2 | 368 | 332.6 | 414.4
1238 | 1063 | 521.2 | 420.5 | 422.3 | 400.5 | 400.2 | 367.9 | 332.7 | 414.3
1239 | 1064 | 521.2 | 420.5 | 422.3 | 400.6 | 400.2 | 368 | 332.7 | 414.2
1240 | 1065 | 521.4 | 420.6 | 422.2 | 400.6 | 400.2 | 368 | 332.7 | 414.2
1241 | 1066 | 521.5 | 420.6 | 422.2 | 400.7 | 400.2 | 368.2 | 332.9 | 414.2
1242 | 1067 | 521.8 | 420.7 | 422.2 | 400.7 | 400.2 | 368.3 | 333 | 414.1
1243 | 1068 | 522.1 | 420.8 | 422.2 | 400.8 | 400.1 | 368.3 | 333 | 414.1
1244 | 1069 | 522.1 | 420.9 | 422.2 | 400.8 | 400.1 | 368.4 | 333.1 | 414.1
1245 | 1070 | 522.2 | 420.9 | 422.1 | 400.9 | 400.1 | 368.4 | 333.1 | 414.1
1246 | 1071 | 522.3 | 421 | 422.1 | 400.9 | 400.1 | 368.4 | 333.2 | 414.1
1247 | 1072 | 522.3 | 421 | 422.1 | 400.9 | 400.1 | 368.4 | 333.3 | 414.2
1248 | 1073 | 522.5 | 421 | 422.1 | 401 | 400.1 | 368.5 | 333.5 | 414.2
1249 | 1074 | 522.7 | 421.1 | 422.1 | 401 | 400.2 | 368.5 | 333.6 | 414.3
1250 | 1075 | 522.9 | 421.1 | 422.1 | 401.1 | 400.3 | 368.4 | 333.7 | 414.4
1251 | 1076 | 523.2 | 421.2 | 422.1 | 401.2 | 400.4 | 368.4 | 333.7 | 414.4
1252 | 1077 | 523.4 | 421.2 | 422.1 | 401.2 | 400.5 | 368.6 | 333.8 | 414.4
1253 | 1078 | 523.5 | 421.2 | 422.3 | 401.2 | 400.4 | 368.6 | 333.7 | 414.5
1254 | 1079 | 523.3 | 421.2 | 422.3 | 401.3 | 400.5 | 368.7 | 333.7 | 414.5
1255 | 1080 | 523.3 | 421.3 | 422.3 | 401.4 | 400.5 | 368.6 | 333.7 | 414.5
1256 | 1081 | 523.5 | 421.4 | 422.4 | 401.5 | 400.6 | 368.5 | 333.8 | 414.4
1257 | 1082 | 523.5 | 421.4 | 422.4 | 401.5 | 400.7 | 368.5 | 333.7 | 414.4
1258 | 1083 | 523.4 | 421.5 | 422.3 | 401.6 | 400.7 | 368.6 | 333.7 | 414.4
1259 | 1084 | 523.1 | 421.7 | 422.3 | 401.7 | 400.7 | 368.5 | 333.8 | 414.4
1260 | 1085 | 523 | 421.8 | 422.3 | 401.8 | 400.8 | 368.4 | 333.8 | 414.5
1261 | 1086 | 523 | 421.8 | 422.3 | 401.8 | 400.8 | 368.3 | 333.8 | 414.5
1262 | 1087 | 523.1 | 421.9 | 422.6 | 401.9 | 400.9 | 368.3 | 333.9 | 414.5
1263 | 1088 | 523.2 | 421.9 | 422.7 | 402 | 401 | 368.1 | 333.9 | 414.6
1264 | 1089 | 523.4 | 421.9 | 422.7 | 402 | 401.1 | 368 | 333.9 | 414.6
1265 | 1090 | 523.3 | 422 | 422.6 | 402.1 | 401.2 | 367.8 | 334 | 414.6
1266 | 1091 | 523.3 | 422 | 422.6 | 402.2 | 401.3 | 367.7 | 334.1 | 414.6
1267 | 1092 | 523.4 | 422.1 | 422.6 | 402.3 | 401.4 | 367.6 | 334.1 | 414.6
1268 | 1093 | 523.6 | 422.2 | 422.6 | 402.3 | 401.5 | 367.6 | 334.1 | 414.7
1269 | 1094 | 523.7 | 422.2 | 422.6 | 402.4 | 401.6 | 367.6 | 334.2 | 414.7
1270 | 1095 | 523.8 | 422.3 | 422.6 | 402.5 | 401.7 | 367.6 | 334.3 | 414.7
1271 | 1096 | 523.8 | 422.4 | 422.5 | 402.6 | 401.7 | 367.7 | 334.4 | 414.7
1272 | 1097 | 523.8 | 422.4 | 422.4 | 402.6 | 401.8 | 367.7 | 334.4 | 414.7
1273 | 1098 | 523.9 | 422.6 | 422.3 | 402.7 | 401.8 | 367.9 | 334.5 | 414.7
1274 | 1099 | 523.9 | 422.6 | 422.3 | 402.8 | 401.9 | 368 | 334.6 | 414.7
1275 | 1100 | 523.7 | 422.7 | 422.2 | 402.9 | 402 | 368.2 | 334.8 | 414.7
1276 | 1101 | 523.7 | 422.8 | 422.3 | 403 | 402.1 | 368.3 | 334.9 | 414.6
1277 | 1102 | 523.7 | 422.8 | 422.3 | 403.1 | 402.2 | 368.4 | 334.9 | 414.7
1278 | 1103 | 523.5 | 422.9 | 422.2 | 403.1 | 402.3 | 368.5 | 334.9 | 414.8
1279 | 1104 | 523.5 | 422.9 | 422.2 | 403.2 | 402.4 | 368.5 | 334.9 | 414.8
1280 | 1105 | 523.5 | 423 | 422.1 | 403.3 | 402.5 | 368.6 | 334.8 | 415
1281 | 1106 | 523.6 | 423.1 | 422.2 | 403.4 | 402.7 | 368.7 | 334.8 | 415
1282 | 1107 | 523.7 | 423.2 | 422.2 | 403.5 | 402.8 | 368.8 | 334.9 | 415.1
1283 | 1108 | 523.6 | 423.3 | 422.2 | 403.7 | 403 | 368.8 | 334.9 | 415.1
1284 | 1109 | 523.6 | 423.4 | 422.2 | 403.8 | 403.1 | 368.9 | 334.9 | 415.3
1285 | 1110 | 523.6 | 423.5 | 422.2 | 403.9 | 403.3 | 369 | 335 | 415.4
1286 | 1111 | 523.6 | 423.5 | 422.3 | 404 | 403.4 | 369.1 | 335 | 415.4
1287 | 1112 | 523.7 | 423.6 | 422.3 | 404.1 | 403.6 | 369.2 | 335 | 415.5
1288 | 1113 | 523.8 | 423.7 | 422.3 | 404.2 | 403.7 | 369.2 | 334.9 | 415.5
1289 | 1114 | 523.9 | 423.8 | 422.4 | 404.3 | 403.9 | 369.2 | 335 | 415.6
1290 | 1115 | 524 | 423.9 | 422.4 | 404.5 | 404.1 | 369.2 | 335 | 415.7
1291 | 1116 | 523.8 | 424 | 422.4 | 404.6 | 404.2 | 369.2 | 335 | 415.7
1292 | 1117 | 523.6 | 424 | 422.3 | 404.7 | 404.4 | 369.2 | 335.1 | 415.8
1293 | 1118 | 523.5 | 424.1 | 422.3 | 404.8 | 404.6 | 369.1 | 335.1 | 415.9
1294 | 1119 | 523.5 | 424.2 | 422.3 | 404.9 | 404.8 | 369.1 | 335.2 | 416
1295 | 1120 | 523.5 | 424.2 | 422.3 | 405 | 404.9 | 369.2 | 335.2 | 416.1
1296 | 1121 | 523.6 | 424.3 | 422.2 | 405.1 | 405.1 | 369.2 | 335.3 | 416.1
1297 | 1122 | 523.6 | 424.4 | 422.3 | 405.2 | 405.3 | 369.1 | 335.3 | 416.2
1298 | 1123 | 523.6 | 424.4 | 422.3 | 405.4 | 405.5 | 369.2 | 335.3 | 416.3
1299 | 1124 | 523.5 | 424.5 | 422.3 | 405.5 | 405.6 | 369.2 | 335.3 | 416.3
1300 | 1125 | 523.5 | 424.5 | 422.3 | 405.6 | 405.8 | 369.2 | 335.3 | 416.3
1301 | 1126 | 523.4 | 424.6 | 422.3 | 405.7 | 405.9 | 369.2 | 335.3 | 416.3
1302 | 1127 | 523.4 | 424.7 | 422.3 | 405.8 | 406.1 | 369.3 | 335.3 | 416.3
1303 | 1128 | 523.5 | 424.7 | 422.2 | 406 | 406.2 | 369.3 | 335.3 | 416.4
1304 | 1129 | 523.7 | 424.8 | 422.3 | 406.1 | 406.3 | 369.3 | 335.3 | 416.5
1305 | 1130 | 523.6 | 424.8 | 422.3 | 406.2 | 406.5 | 369.2 | 335.4 | 416.6
1306 | 1131 | 523.5 | 424.9 | 422.2 | 406.3 | 406.6 | 369.1 | 335.4 | 416.6
1307 | 1132 | 523.7 | 424.9 | 422.2 | 406.4 | 406.7 | 369.1 | 335.5 | 416.5
1308 | 1133 | 523.7 | 424.9 | 422.2 | 406.5 | 406.9 | 369.1 | 335.6 | 416.6
1309 | 1134 | 523.9 | 425 | 422.2 | 406.6 | 407 | 369.1 | 335.8 | 416.6
1310 | 1135 | 524.1 | 425 | 422.3 | 406.7 | 407.1 | 369.1 | 335.8 | 416.6
1311 | 1136 | 524.1 | 425 | 422.3 | 406.8 | 407.2 | 369 | 335.8 | 416.6
1312 | 1137 | 524 | 425 | 422.3 | 406.9 | 407.3 | 369 | 335.8 | 416.6
1313 | 1138 | 523.9 | 425 | 422.3 | 406.9 | 407.4 | 368.9 | 335.8 | 416.6
1314 | 1139 | 523.9 | 425.1 | 422.4 | 407 | 407.5 | 368.8 | 335.8 | 416.7
1315 | 1140 | 523.9 | 425.1 | 422.4 | 407.1 | 407.5 | 368.8 | 335.8 | 416.7
1316 | 1141 | 523.9 | 425.2 | 422.4 | 407.2 | 407.6 | 368.8 | 335.8 | 416.8
1317 | 1142 | 524.1 | 425.3 | 422.3 | 407.3 | 407.7 | 368.8 | 335.8 | 416.8
1318 | 1143 | 524.1 | 425.3 | 422.3 | 407.3 | 407.7 | 368.9 | 335.8 | 416.9
1319 | 1144 | 524 | 425.2 | 422.3 | 407.4 | 407.8 | 369 | 335.9 | 416.8
1320 | 1145 | 523.9 | 425.2 | 422.3 | 407.4 | 407.8 | 369 | 335.9 | 416.8
1321 | 1146 | 523.8 | 425.2 | 422.3 | 407.5 | 407.9 | 369.1 | 335.9 | 416.8
1322 | 1147 | 523.7 | 425.2 | 422.3 | 407.6 | 408 | 369.1 | 335.8 | 416.8
1323 | 1148 | 523.6 | 425.2 | 422.3 | 407.7 | 408 | 369.1 | 335.8 | 416.8
1324 | 1149 | 523.5 | 425.2 | 422.3 | 407.7 | 408.1 | 369.1 | 336 | 416.9
1325 | 1150 | 523.1 | 425.2 | 422.4 | 407.8 | 408.1 | 369.1 | 336.1 | 416.9
1326 | 1151 | 522.8 | 425.2 | 422.5 | 407.8 | 408.1 | 369.2 | 336.1 | 416.9
1327 | 1152 | 522.6 | 425.3 | 422.4 | 407.9 | 408.2 | 369.3 | 336.1 | 417
1328 | 1153 | 522.7 | 425.3 | 422.4 | 408 | 408.2 | 369.4 | 336 | 417.1
1329 | 1154 | 522.9 | 425.4 | 422.5 | 408 | 408.3 | 369.5 | 336 | 417.2
1330 | 1155 | 523 | 425.4 | 422.5 | 408.1 | 408.4 | 369.6 | 335.9 | 417.2
1331 | 1156 | 523.1 | 425.4 | 422.4 | 408.2 | 408.5 | 369.7 | 335.8 | 417.3
1332 | 1157 | 523.1 | 425.4 | 422.3 | 408.2 | 408.6 | 369.7 | 335.7 | 417.4
1333 | 1158 | 523.1 | 425.4 | 422.3 | 408.3 | 408.7 | 369.8 | 335.8 | 417.3
1334 | 1159 | 523.3 | 425.5 | 422.3 | 408.4 | 408.8 | 369.8 | 335.7 | 417.4
1335 | 1160 | 523.3 | 425.5 | 422.3 | 408.4 | 408.9 | 369.8 | 335.8 | 417.4
1336 | 1161 | 523.4 | 425.6 | 422.4 | 408.5 | 409 | 369.8 | 335.8 | 417.5
1337 | 1162 | 523.4 | 425.7 | 422.5 | 408.6 | 409.1 | 369.8 | 335.8 | 417.6
1338 | 1163 | 523.2 | 425.8 | 422.6 | 408.7 | 409.2 | 369.9 | 335.8 | 417.6
1339 | 1164 | 523.1 | 425.8 | 422.7 | 408.7 | 409.3 | 369.9 | 335.8 | 417.7
1340 | 1165 | 523 | 425.8 | 422.7 | 408.8 | 409.5 | 369.9 | 335.8 | 417.7
1341 | 1166 | 523.1 | 425.8 | 422.6 | 408.9 | 409.6 | 369.9 | 335.9 | 417.8
1342 | 1167 | 523.3 | 425.8 | 422.6 | 409 | 409.8 | 369.9 | 335.8 | 417.9
1343 | 1168 | 523.2 | 425.9 | 422.5 | 409.1 | 410 | 369.9 | 335.8 | 418
1344 | 1169 | 523.1 | 425.9 | 422.5 | 409.2 | 410.1 | 369.9 | 335.8 | 418.1
1345 | 1170 | 522.8 | 425.9 | 422.4 | 409.3 | 410.3 | 369.9 | 335.8 | 418.1
1346 | 1171 | 522.7 | 425.9 | 422.4 | 409.4 | 410.4 | 369.9 | 335.7 | 418.2
1347 | 1172 | 522.8 | 425.9 | 422.5 | 409.5 | 410.6 | 369.9 | 335.7 | 418.3
1348 | 1173 | 522.9 | 426 | 422.5 | 409.6 | 410.7 | 369.9 | 335.7 | 418.2
1349 | 1174 | 522.9 | 426.1 | 422.5 | 409.8 | 410.8 | 370 | 335.7 | 418.2
1350 | 1175 | 522.8 | 426.2 | 422.5 | 409.9 | 410.9 | 370 | 335.7 | 418.2
1351 | 1176 | 522.8 | 426.2 | 422.5 | 410 | 411 | 370.1 | 335.7 | 418.3
1352 | 1177 | 522.8 | 426.2 | 422.5 | 410.1 | 411 | 370.1 | 335.8 | 418.3
1353 | 1178 | 523 | 426.2 | 422.6 | 410.2 | 411.1 | 370.1 | 335.8 | 418.3
1354 | 1179 | 523.1 | 426.2 | 422.6 | 410.3 | 411.2 | 370.2 | 335.8 | 418.3
1355 | 1180 | 523.1 | 426.2 | 422.6 | 410.3 | 411.3 | 370.3 | 335.7 | 418.2
1356 | 1181 | 523.2 | 426.2 | 422.6 | 410.4 | 411.3 | 370.1 | 335.7 | 418.1
1357 | 1182 | 523.5 | 426.2 | 422.6 | 410.5 | 411.4 | 370 | 335.7 | 418
1358 | 1183 | 523.7 | 426.1 | 422.7 | 410.6 | 411.4 | 369.9 | 335.7 | 418
1359 | 1184 | 523.9 | 426.1 | 422.9 | 410.6 | 411.4 | 369.9 | 335.6 | 418
1360 | 1185 | 524 | 426.2 | 422.8 | 410.7 | 411.3 | 369.9 | 335.6 | 418
1361 | 1186 | 524.3 | 426.3 | 422.9 | 410.8 | 411.3 | 369.9 | 335.6 | 418
1362 | 1187 | 524.5 | 426.3 | 422.8 | 410.8 | 411.2 | 370 | 335.5 | 417.8
1363 | 1188 | 524.5 | 426.4 | 422.7 | 410.9 | 411.2 | 370 | 335.6 | 417.8
1364 | 1189 | 524.4 | 426.4 | 422.8 | 410.9 | 411.1 | 369.9 | 335.6 | 417.8
1365 | 1190 | 524.2 | 426.5 | 422.9 | 411 | 411.1 | 369.9 | 335.6 | 417.7
1366 | 1191 | 524.3 | 426.5 | 422.9 | 411 | 411 | 369.9 | 335.7 | 417.7
1367 | 1192 | 524.1 | 426.5 | 422.8 | 411.1 | 410.9 | 369.8 | 335.8 | 417.7
1368 | 1193 | 523.9 | 426.5 | 422.9 | 411.1 | 410.9 | 369.7 | 335.8 | 417.6
1369 | 1194 | 523.9 | 426.5 | 423 | 411.2 | 410.8 | 369.6 | 335.8 | 417.6
1370 | 1195 | 523.7 | 426.5 | 423.1 | 411.2 | 410.8 | 369.7 | 335.9 | 417.6
1371 | 1196 | 523.7 | 426.4 | 423.1 | 411.3 | 410.7 | 369.7 | 335.9 | 417.6
1372 | 1197 | 523.5 | 426.3 | 423.2 | 411.3 | 410.6 | 369.8 | 335.9 | 417.7
1373 | 1198 | 523.5 | 426.3 | 423.1 | 411.3 | 410.6 | 369.7 | 335.9 | 417.7
1374 | 1199 | 523.5 | 426.4 | 423.1 | 411.4 | 410.6 | 369.7 | 335.9 | 417.7
1375 | 1200 | 523.4 | 426.4 | 423.2 | 411.4 | 410.5 | 369.8 | 335.9 | 417.6
1376 | 1201 | 523.4 | 426.5 | 423.3 | 411.5 | 410.5 | 369.9 | 335.9 | 417.5
1377 | 1202 | 523.2 | 426.5 | 423.4 | 411.5 | 410.5 | 370 | 336.1 | 417.5
1378 | 1203 | 523.1 | 426.6 | 423.5 | 411.5 | 410.5 | 370 | 336.1 | 417.5
1379 | 1204 | 522.9 | 426.6 | 423.4 | 411.6 | 410.5 | 369.9 | 336.1 | 417.5
1380 | 1205 | 522.7 | 426.6 | 423.3 | 411.6 | 410.5 | 369.8 | 336.1 | 417.5
1381 | 1206 | 522.4 | 426.6 | 423.2 | 411.7 | 410.5 | 369.7 | 336 | 417.6
1382 | 1207 | 522.3 | 426.6 | 423.1 | 411.7 | 410.4 | 369.7 | 336 | 417.7
1383 | 1208 | 522 | 426.6 | 422.9 | 411.8 | 410.5 | 369.7 | 336 | 417.7
1384 | 1209 | 521.8 | 426.7 | 422.9 | 411.8 | 410.5 | 369.7 | 336 | 417.8
1385 | 1210 | 521.8 | 426.7 | 422.9 | 411.9 | 410.6 | 369.7 | 336 | 417.8
1386 | 1211 | 521.8 | 426.7 | 422.9 | 411.9 | 410.6 | 369.8 | 336 | 417.8
1387 | 1212 | 521.7 | 426.8 | 422.9 | 412 | 410.7 | 369.9 | 336.1 | 417.9
1388 | 1213 | 521.4 | 426.9 | 422.9 | 412 | 410.8 | 369.9 | 336.2 | 418
1389 | 1214 | 521.5 | 427 | 422.8 | 412.1 | 410.9 | 370 | 336.2 | 418
1390 | 1215 | 521.6 | 427 | 422.9 | 412.2 | 411 | 369.9 | 336.2 | 418
1391 | 1216 | 521.5 | 427.1 | 422.9 | 412.3 | 411.2 | 369.9 | 336.3 | 418
1392 | 1217 | 521.5 | 427.2 | 423 | 412.4 | 411.3 | 369.9 | 336.5 | 418
1393 | 1218 | 521.5 | 427.2 | 423 | 412.5 | 411.5 | 369.9 | 336.5 | 418.1
1394 | 1219 | 521.6 | 427.2 | 423 | 412.6 | 411.6 | 370 | 336.6 | 418.2
1395 | 1220 | 521.7 | 427.2 | 423.1 | 412.7 | 411.8 | 370 | 336.6 | 418.2
1396 | 1221 | 521.6 | 427.3 | 423.1 | 412.8 | 412 | 370 | 336.6 | 418.3
1397 | 1222 | 521.7 | 427.3 | 423.2 | 412.9 | 412.2 | 370.1 | 336.6 | 418.3
1398 | 1223 | 521.8 | 427.4 | 423.1 | 413 | 412.3 | 370.1 | 336.6 | 418.3
1399 | 1224 | 521.9 | 427.4 | 423 | 413.2 | 412.5 | 370.1 | 336.6 | 418.4
1400 | 1225 | 522 | 427.5 | 423 | 413.3 | 412.7 | 370.2 | 336.6 | 418.5
1401 | 1226 | 522.1 | 427.6 | 423.1 | 413.4 | 412.8 | 370.2 | 336.6 | 418.6
1402 | 1227 | 522.2 | 427.6 | 423.1 | 413.5 | 413 | 370.3 | 336.7 | 418.6
1403 | 1228 | 522.3 | 427.7 | 423 | 413.7 | 413.2 | 370.4 | 336.7 | 418.7
1404 | 1229 | 522.4 | 427.8 | 423 | 413.8 | 413.3 | 370.6 | 336.7 | 418.7
1405 | 1230 | 522.4 | 427.8 | 423 | 413.9 | 413.5 | 370.6 | 336.7 | 418.7
1406 | 1231 | 522.3 | 427.9 | 423.2 | 414 | 413.6 | 370.7 | 336.6 | 418.8
1407 | 1232 | 522.2 | 428 | 423.4 | 414.1 | 413.7 | 370.8 | 336.7 | 418.8
1408 | 1233 | 522.1 | 428 | 423.6 | 414.2 | 413.8 | 370.9 | 336.7 | 419
1409 | 1234 | 522.1 | 428.1 | 423.6 | 414.3 | 413.9 | 371 | 336.7 | 419
1410 | 1235 | 522.3 | 428.1 | 423.6 | 414.4 | 414.1 | 371.1 | 336.7 | 419
1411 | 1236 | 522.6 | 428.2 | 423.6 | 414.5 | 414.2 | 371 | 336.8 | 419
1412 | 1237 | 522.9 | 428.2 | 423.8 | 414.6 | 414.3 | 371.1 | 336.9 | 419
1413 | 1238 | 522.9 | 428.3 | 424 | 414.6 | 414.4 | 371.1 | 337 | 418.9
1414 | 1239 | 522.8 | 428.3 | 424.2 | 414.7 | 414.5 | 371.1 | 337 | 418.9
1415 | 1240 | 522.8 | 428.3 | 424.2 | 414.8 | 414.5 | 371.1 | 337 | 418.8
1416 | 1241 | 523 | 428.3 | 424.1 | 414.9 | 414.6 | 371.1 | 336.9 | 418.8
1417 | 1242 | 522.9 | 428.4 | 424.1 | 414.9 | 414.6 | 371.3 | 336.9 | 418.8
1418 | 1243 | 522.8 | 428.4 | 424 | 415 | 414.7 | 371.3 | 336.9 | 418.8
1419 | 1244 | 522.6 | 428.4 | 424.1 | 415.1 | 414.7 | 371.4 | 336.9 | 418.8
1420 | 1245 | 522.8 | 428.5 | 424.2 | 415.1 | 414.7 | 371.3 | 336.8 | 418.8
1421 | 1246 | 522.8 | 428.5 | 424.3 | 415.2 | 414.7 | 371.3 | 336.8 | 418.8
1422 | 1247 | 522.8 | 428.5 | 424.4 | 415.2 | 414.7 | 371.2 | 336.8 | 418.8
1423 | 1248 | 523 | 428.5 | 424.5 | 415.3 | 414.7 | 371.1 | 336.8 | 418.8
1424 | 1249 | 523.2 | 428.6 | 424.7 | 415.3 | 414.7 | 371 | 336.8 | 418.8
1425 | 1250 | 523.5 | 428.6 | 424.8 | 415.3 | 414.6 | 371 | 336.8 | 418.8
1426 | 1251 | 523.5 | 428.6 | 424.9 | 415.4 | 414.6 | 370.9 | 336.9 | 418.9
1427 | 1252 | 523.5 | 428.7 | 425 | 415.4 | 414.6 | 370.7 | 336.9 | 419
1428 | 1253 | 523.6 | 428.7 | 424.9 | 415.4 | 414.6 | 370.5 | 336.9 | 419
1429 | 1254 | 523.6 | 428.8 | 424.9 | 415.5 | 414.6 | 370.5 | 336.9 | 419
1430 | 1255 | 523.8 | 428.9 | 425.1 | 415.5 | 414.6 | 370.4 | 336.9 | 419.1
1431 | 1256 | 523.8 | 429 | 425.4 | 415.5 | 414.6 | 370.5 | 336.9 | 419.1
1432 | 1257 | 523.7 | 429 | 425.5 | 415.5 | 414.6 | 370.4 | 336.9 | 419.1
1433 | 1258 | 523.6 | 429 | 425.5 | 415.6 | 414.7 | 370.5 | 336.8 | 419.1
1434 | 1259 | 523.5 | 428.9 | 425.5 | 415.6 | 414.7 | 370.6 | 336.8 | 419.1
1435 | 1260 | 523.5 | 428.9 | 425.7 | 415.6 | 414.7 | 370.7 | 336.8 | 419.1
1436 | 1261 | 523.4 | 429 | 425.8 | 415.7 | 414.7 | 370.6 | 336.7 | 419.1
1437 | 1262 | 523.5 | 429 | 425.9 | 415.7 | 414.8 | 370.5 | 336.7 | 419.1
1438 | 1263 | 523.5 | 429 | 426 | 415.7 | 414.8 | 370.4 | 336.7 | 419
1439 | 1264 | 523.4 | 429 | 426 | 415.8 | 414.8 | 370.5 | 336.7 | 419.1
1440 | 1265 | 523.5 | 429.1 | 426 | 415.8 | 414.8 | 370.6 | 336.6 | 419.1
1441 | 1266 | 523.3 | 429.2 | 426 | 415.8 | 414.8 | 370.6 | 336.6 | 419
1442 | 1267 | 523.3 | 429.2 | 426.1 | 415.9 | 414.8 | 370.6 | 336.6 | 419.1
1443 | 1268 | 523.7 | 429.1 | 426.2 | 415.9 | 414.8 | 370.5 | 336.7 | 419
1444 | 1269 | 524 | 429 | 426.3 | 415.9 | 414.8 | 370.5 | 336.7 | 418.9
1445 | 1270 | 524.1 | 429.1 | 426.3 | 415.9 | 414.7 | 370.5 | 336.7 | 418.8
1446 | 1271 | 524 | 429.1 | 426.4 | 415.9 | 414.7 | 370.5 | 336.8 | 418.8
1447 | 1272 | 523.8 | 429.1 | 426.5 | 415.9 | 414.6 | 370.6 | 336.8 | 418.9
1448 | 1273 | 523.6 | 429.1 | 426.5 | 415.9 | 414.6 | 370.7 | 336.8 | 418.9
1449 | 1274 | 523.5 | 429.1 | 426.6 | 415.9 | 414.5 | 371 | 336.8 | 418.9
1450 | 1275 | 523.3 | 429.2 | 426.9 | 415.9 | 414.4 | 371.1 | 336.9 | 418.9
1451 | 1276 | 523.1 | 429.2 | 427 | 415.9 | 414.3 | 371.2 | 336.8 | 418.8
1452 | 1277 | 522.9 | 429.2 | 427 | 415.9 | 414.2 | 371.2 | 336.8 | 418.7
1453 | 1278 | 522.9 | 429.3 | 426.9 | 415.9 | 414.1 | 371.2 | 336.9 | 418.7
1454 | 1279 | 523.2 | 429.3 | 427 | 415.9 | 414 | 371.3 | 336.9 | 418.7
1455 | 1280 | 523.3 | 429.3 | 427.1 | 415.9 | 414 | 371.4 | 337 | 418.7
1456 | 1281 | 523.3 | 429.4 | 427.2 | 415.9 | 413.9 | 371.5 | 337 | 418.7
1457 | 1282 | 523.2 | 429.4 | 427.3 | 415.9 | 413.8 | 371.6 | 337 | 418.7
1458 | 1283 | 523 | 429.5 | 427.5 | 415.9 | 413.8 | 371.6 | 337.1 | 418.6
1459 | 1284 | 523.2 | 429.5 | 427.7 | 415.8 | 413.7 | 371.6 | 337 | 418.5
1460 | 1285 | 523 | 429.5 | 427.8 | 415.8 | 413.6 | 371.5 | 337.1 | 418.5
1461 | 1286 | 522.9 | 429.5 | 427.7 | 415.8 | 413.6 | 371.4 | 337 | 418.5
1462 | 1287 | 522.7 | 429.6 | 427.7 | 415.8 | 413.5 | 371.3 | 337 | 418.5
1463 | 1288 | 522.6 | 429.6 | 427.7 | 415.8 | 413.4 | 371 | 337 | 418.3
1464 | 1289 | 522.5 | 429.7 | 427.8 | 415.8 | 413.3 | 370.8 | 337 | 418.3
1465 | 1290 | 522.4 | 429.6 | 427.9 | 415.8 | 413.2 | 370.6 | 337 | 418.2
1466 | 1291 | 522.3 | 429.7 | 428.1 | 415.8 | 413.1 | 370.5 | 337 | 418.2
1467 | 1292 | 522.4 | 429.6 | 428.2 | 415.8 | 413 | 370.3 | 337 | 418.1
1468 | 1293 | 522.5 | 429.6 | 428.2 | 415.8 | 412.9 | 370.3 | 337 | 418
1469 | 1294 | 522.5 | 429.6 | 428.2 | 415.8 | 412.8 | 370.1 | 336.9 | 418
1470 | 1295 | 522.5 | 429.7 | 428.4 | 415.7 | 412.6 | 370.1 | 336.9 | 418
1471 | 1296 | 522.5 | 429.8 | 428.6 | 415.7 | 412.5 | 370 | 337 | 418
1472 | 1297 | 522.5 | 429.8 | 428.7 | 415.7 | 412.4 | 369.9 | 337 | 417.9
1473 | 1298 | 522.3 | 429.8 | 428.9 | 415.7 | 412.3 | 369.9 | 337.1 | 417.9
1474 | 1299 | 522.3 | 429.8 | 429 | 415.7 | 412.2 | 369.9 | 337.1 | 417.9
1475 | 1300 | 522.3 | 429.9 | 429.1 | 415.7 | 412.1 | 369.9 | 337.1 | 417.9
1476 | 1301 | 522.2 | 430 | 429.2 | 415.7 | 412 | 369.9 | 337.1 | 418
1477 | 1302 | 522.3 | 430.1 | 429.2 | 415.7 | 412 | 369.8 | 337.1 | 418
1478 | 1303 | 522.4 | 430.2 | 429.3 | 415.7 | 412 | 369.7 | 337.2 | 418
1479 | 1304 | 522.6 | 430.2 | 429.4 | 415.7 | 412 | 369.7 | 337.2 | 418.1
1480 | 1305 | 522.7 | 430.2 | 429.5 | 415.7 | 412 | 369.8 | 337.2 | 418.1
1481 | 1306 | 522.7 | 430.3 | 429.5 | 415.7 | 412 | 369.7 | 337.2 | 418.2
1482 | 1307 | 522.8 | 430.3 | 429.6 | 415.8 | 412.1 | 369.7 | 337.3 | 418.2
1483 | 1308 | 522.9 | 430.4 | 429.6 | 415.8 | 412.2 | 369.6 | 337.3 | 418.2
1484 | 1309 | 523.1 | 430.5 | 429.8 | 415.8 | 412.3 | 369.6 | 337.3 | 418.2
1485 | 1310 | 523 | 430.6 | 430 | 415.9 | 412.4 | 369.6 | 337.4 | 418.1
1486 | 1311 | 523 | 430.7 | 430.1 | 415.9 | 412.5 | 369.5 | 337.4 | 418
1487 | 1312 | 522.9 | 430.8 | 430 | 416 | 412.6 | 369.6 | 337.4 | 418.1
1488 | 1313 | 522.8 | 430.9 | 430.2 | 416 | 412.7 | 369.7 | 337.4 | 418.2
1489 | 1314 | 522.7 | 431 | 430.3 | 416.1 | 412.8 | 369.8 | 337.4 | 418.1
1490 | 1315 | 522.6 | 431.1 | 430.4 | 416.2 | 412.8 | 369.9 | 337.4 | 418
1491 | 1316 | 522.6 | 431.2 | 430.6 | 416.2 | 412.9 | 370 | 337.4 | 418
1492 | 1317 | 522.6 | 431.3 | 430.8 | 416.3 | 413 | 369.9 | 337.4 | 418
1493 | 1318 | 522.5 | 431.4 | 430.8 | 416.3 | 413 | 370 | 337.4 | 418
1494 | 1319 | 522.5 | 431.5 | 430.7 | 416.3 | 413.1 | 370 | 337.4 | 417.9
1495 | 1320 | 522.6 | 431.6 | 430.8 | 416.4 | 413.1 | 370.1 | 337.4 | 417.8
1496 | 1321 | 522.8 | 431.7 | 430.9 | 416.4 | 413.1 | 370 | 337.4 | 417.8
1497 | 1322 | 522.8 | 431.8 | 431.1 | 416.4 | 413.1 | 370 | 337.4 | 417.8
1498 | 1323 | 522.8 | 431.8 | 431.2 | 416.5 | 413.1 | 370 | 337.4 | 417.7
1499 | 1324 | 522.8 | 431.8 | 431.2 | 416.5 | 413.1 | 370 | 337.4 | 417.7
1500 | 1325 | 523 | 431.9 | 431.3 | 416.5 | 413 | 370 | 337.4 | 417.7
1501 | 1326 | 523.2 | 432 | 431.4 | 416.6 | 413 | 370 | 337.4 | 417.7
1502 | 1327 | 523.4 | 432 | 431.5 | 416.6 | 413 | 370.1 | 337.5 | 417.8
1503 | 1328 | 523.6 | 432.1 | 431.5 | 416.7 | 412.9 | 370.1 | 337.5 | 417.9
1504 | 1329 | 523.6 | 432.1 | 431.6 | 416.7 | 412.9 | 370.1 | 337.6 | 417.9
1505 | 1330 | 523.4 | 432.1 | 431.6 | 416.7 | 412.9 | 370.1 | 337.6 | 417.8
1506 | 1331 | 523.5 | 432.1 | 431.7 | 416.8 | 412.9 | 370.1 | 337.5 | 417.8
1507 | 1332 | 523.6 | 432.2 | 431.8 | 416.8 | 412.8 | 370.2 | 337.5 | 417.8
1508 | 1333 | 523.7 | 432.3 | 431.9 | 416.8 | 412.8 | 370.2 | 337.5 | 417.9
1509 | 1334 | 523.9 | 432.4 | 432 | 416.9 | 412.8 | 370.2 | 337.5 | 417.9
1510 | 1335 | 524.1 | 432.4 | 432.1 | 416.9 | 412.8 | 370.2 | 337.5 | 418
1511 | 1336 | 523.9 | 432.4 | 432.1 | 416.9 | 412.8 | 370.1 | 337.4 | 418
1512 | 1337 | 523.8 | 432.4 | 432.3 | 416.9 | 412.8 | 370.1 | 337.5 | 418.1
1513 | 1338 | 523.8 | 432.5 | 432.4 | 416.9 | 412.9 | 370 | 337.5 | 418.1
1514 | 1339 | 523.9 | 432.4 | 432.5 | 417 | 412.9 | 369.9 | 337.5 | 418.1
1515 | 1340 | 523.8 | 432.4 | 432.6 | 417 | 412.9 | 369.9 | 337.5 | 418.1
1516 | 1341 | 523.6 | 432.5 | 432.6 | 417.1 | 412.9 | 369.8 | 337.7 | 418
1517 | 1342 | 523.4 | 432.5 | 432.9 | 417.1 | 413 | 369.9 | 337.6 | 418
1518 | 1343 | 523.4 | 432.6 | 432.9 | 417.1 | 413 | 369.9 | 337.6 | 418.1
1519 | 1344 | 523.5 | 432.6 | 433.1 | 417.1 | 413 | 370 | 337.6 | 418.1
1520 | 1345 | 523.3 | 432.6 | 433.5 | 417.2 | 413 | 370 | 337.6 | 418.1
1521 | 1346 | 523.2 | 432.7 | 433.6 | 417.2 | 413.1 | 370 | 337.6 | 418
1522 | 1347 | 523.1 | 432.8 | 433.8 | 417.3 | 413 | 370 | 337.6 | 418.1
1523 | 1348 | 523.1 | 432.9 | 433.8 | 417.3 | 413 | 370 | 337.6 | 418.2
1524 | 1349 | 523.1 | 432.9 | 433.7 | 417.4 | 413 | 370 | 337.5 | 418.1
1525 | 1350 | 522.9 | 433 | 433.8 | 417.4 | 413 | 370 | 337.6 | 418.2
1526 | 1351 | 522.6 | 432.9 | 433.9 | 417.4 | 413 | 369.9 | 337.6 | 418.2
1527 | 1352 | 522.7 | 432.9 | 433.9 | 417.5 | 413 | 369.9 | 337.6 | 418.2
1528 | 1353 | 522.8 | 432.9 | 434.1 | 417.5 | 412.9 | 370 | 337.6 | 418.3
1529 | 1354 | 522.9 | 432.9 | 434 | 417.5 | 412.9 | 369.9 | 337.6 | 418.4
1530 | 1355 | 523 | 433 | 434.1 | 417.5 | 412.9 | 369.8 | 337.6 | 418.4
1531 | 1356 | 523.3 | 433.1 | 434.3 | 417.6 | 412.9 | 369.8 | 337.7 | 418.4
1532 | 1357 | 523.3 | 433.2 | 434.3 | 417.6 | 413 | 369.9 | 337.6 | 418.5
1533 | 1358 | 523.3 | 433.1 | 434.4 | 417.7 | 413 | 370 | 337.5 | 418.5
1534 | 1359 | 523.2 | 433.1 | 434.4 | 417.7 | 413.1 | 370 | 337.5 | 418.5
1535 | 1360 | 523.1 | 433.1 | 434.4 | 417.8 | 413.2 | 370.1 | 337.5 | 418.6
1536 | 1361 | 523 | 433.1 | 434.6 | 417.8 | 413.2 | 370.1 | 337.5 | 418.7
1537 | 1362 | 523 | 433.1 | 434.8 | 417.9 | 413.3 | 370.1 | 337.4 | 418.8
1538 | 1363 | 523.1 | 433.1 | 435 | 417.9 | 413.4 | 370.1 | 337.4 | 418.9
1539 | 1364 | 523 | 433.2 | 435 | 418 | 413.4 | 370.1 | 337.3 | 418.9
1540 | 1365 | 522.9 | 433.2 | 435 | 418.1 | 413.5 | 370.1 | 337.3 | 418.9
1541 | 1366 | 523 | 433.3 | 435 | 418.1 | 413.6 | 370.2 | 337.2 | 419
1542 | 1367 | 523.1 | 433.3 | 435.1 | 418.1 | 413.6 | 370.2 | 337.1 | 419
1543 | 1368 | 523.4 | 433.5 | 435.3 | 418.2 | 413.7 | 370.3 | 337.1 | 419
1544 | 1369 | 523.5 | 433.4 | 435.7 | 418.2 | 413.8 | 370.4 | 337.1 | 419
1545 | 1370 | 523.6 | 433.4 | 435.6 | 418.3 | 413.9 | 370.5 | 337.1 | 419
1546 | 1371 | 523.8 | 433.4 | 435.6 | 418.3 | 413.9 | 370.6 | 337.1 | 419
1547 | 1372 | 524 | 433.4 | 435.7 | 418.4 | 414 | 370.7 | 337.1 | 419.1
1548 | 1373 | 524.3 | 433.5 | 435.8 | 418.4 | 414.1 | 370.8 | 337.1 | 419.2
1549 | 1374 | 524.6 | 433.6 | 435.9 | 418.4 | 414.2 | 370.9 | 337.1 | 419.3
1550 | 1375 | 524.7 | 433.7 | 435.9 | 418.5 | 414.3 | 371.1 | 337.1 | 419.3
1551 | 1376 | 524.8 | 433.7 | 436.1 | 418.6 | 414.4 | 371.2 | 337.1 | 419.2
1552 | 1377 | 525.1 | 433.8 | 436.2 | 418.6 | 414.5 | 371.3 | 337.1 | 419.2
1553 | 1378 | 525.3 | 433.9 | 436.3 | 418.7 | 414.5 | 371.3 | 337.1 | 419.2
1554 | 1379 | 525.2 | 433.8 | 436.4 | 418.7 | 414.6 | 371.5 | 337.1 | 419.3
1555 | 1380 | 525.3 | 433.9 | 436.4 | 418.7 | 414.7 | 371.6 | 337.1 | 419.3
1556 | 1381 | 525.4 | 433.9 | 436.6 | 418.8 | 414.8 | 371.7 | 337.2 | 419.4
1557 | 1382 | 525.4 | 433.9 | 436.8 | 418.9 | 414.8 | 371.8 | 337.2 | 419.4
1558 | 1383 | 525.4 | 434 | 436.8 | 418.9 | 414.9 | 371.8 | 337.1 | 419.4
1559 | 1384 | 525.6 | 434.2 | 436.9 | 419 | 415 | 371.7 | 337.1 | 419.5
1560 | 1385 | 525.5 | 434.3 | 437 | 419.1 | 415 | 371.7 | 337.1 | 419.5
1561 | 1386 | 525.3 | 434.3 | 437.1 | 419.1 | 415.1 | 371.6 | 337.1 | 419.5
1562 | 1387 | 525.3 | 434.4 | 437.2 | 419.2 | 415.2 | 371.6 | 337.2 | 419.6
1563 | 1388 | 525.2 | 434.5 | 437.4 | 419.3 | 415.2 | 371.7 | 337.2 | 419.7
1564 | 1389 | 524.8 | 434.4 | 437.5 | 419.3 | 415.3 | 371.7 | 337.3 | 419.7
1565 | 1390 | 524.5 | 434.4 | 437.8 | 419.4 | 415.4 | 371.8 | 337.3 | 419.7
1566 | 1391 | 524.4 | 434.5 | 437.8 | 419.5 | 415.5 | 372 | 337.3 | 419.8
1567 | 1392 | 524.3 | 434.5 | 437.9 | 419.6 | 415.6 | 372.1 | 337.3 | 419.9
1568 | 1393 | 524.2 | 434.4 | 438 | 419.7 | 415.6 | 372.2 | 337.3 | 419.9
1569 | 1394 | 524.2 | 434.4 | 438.1 | 419.8 | 415.7 | 372.1 | 337.4 | 419.9
1570 | 1395 | 524.4 | 434.5 | 438.3 | 419.8 | 415.7 | 371.9 | 337.4 | 419.9
1571 | 1396 | 524.6 | 434.5 | 438.5 | 419.9 | 415.7 | 371.8 | 337.5 | 419.9
1572 | 1397 | 524.7 | 434.5 | 438.6 | 419.9 | 415.7 | 371.7 | 337.6 | 419.9
1573 | 1398 | 524.6 | 434.7 | 438.7 | 420 | 415.7 | 371.7 | 337.7 | 420
1574 | 1399 | 524.6 | 434.7 | 439.1 | 420 | 415.7 | 371.7 | 337.8 | 420
1575 | 1400 | 524.5 | 434.7 | 439.3 | 420.1 | 415.7 | 371.8 | 337.8 | 420.1
1576 | 1401 | 524.4 | 434.6 | 439.3 | 420.1 | 415.8 | 371.8 | 337.8 | 420.2
1577 | 1402 | 524.3 | 434.7 | 439.3 | 420.2 | 415.8 | 371.9 | 337.7 | 420.3
1578 | 1403 | 524.1 | 434.8 | 439.3 | 420.3 | 415.8 | 372 | 337.7 | 420.3
1579 | 1404 | 524.1 | 434.9 | 439.3 | 420.4 | 415.9 | 372 | 337.7 | 420.3
1580 | 1405 | 524.1 | 434.8 | 439.4 | 420.5 | 415.9 | 372 | 337.7 | 420.3
1581 | 1406 | 524.1 | 434.9 | 439.6 | 420.6 | 416 | 372 | 337.7 | 420.3
1582 | 1407 | 524 | 434.8 | 439.8 | 420.7 | 416 | 372 | 337.7 | 420.4
1583 | 1408 | 524 | 434.9 | 439.9 | 420.8 | 416 | 372 | 337.8 | 420.5
1584 | 1409 | 524.2 | 435 | 440 | 420.8 | 416.1 | 372.1 | 337.8 | 420.6
1585 | 1410 | 524.3 | 435.1 | 440.3 | 420.9 | 416.2 | 372.1 | 337.8 | 420.6
1586 | 1411 | 524.3 | 435.2 | 440.3 | 421 | 416.3 | 372 | 337.9 | 420.7
1587 | 1412 | 524.4 | 435.2 | 440.4 | 421.1 | 416.5 | 372 | 337.9 | 420.9
1588 | 1413 | 524.6 | 435.2 | 440.6 | 421.3 | 416.6 | 372 | 337.9 | 420.9
1589 | 1414 | 524.5 | 435.2 | 440.7 | 421.5 | 416.8 | 372 | 337.9 | 421
1590 | 1415 | 524.5 | 435.3 | 440.5 | 421.6 | 416.9 | 371.8 | 337.9 | 421.1
1591 | 1416 | 524.5 | 435.3 | 440.8 | 421.7 | 417.1 | 371.7 | 337.9 | 421.2
1592 | 1417 | 524.2 | 435.4 | 441.1 | 421.9 | 417.2 | 371.7 | 337.9 | 421.2
1593 | 1418 | 524 | 435.5 | 441.2 | 422 | 417.3 | 371.8 | 338 | 421.2
1594 | 1419 | 523.9 | 435.7 | 441.4 | 422.2 | 417.4 | 371.9 | 338 | 421.2
1595 | 1420 | 524 | 435.7 | 441.7 | 422.3 | 417.5 | 371.9 | 338 | 421.2
1596 | 1421 | 524.1 | 435.7 | 441.7 | 422.4 | 417.6 | 371.8 | 337.9 | 421.2
1597 | 1422 | 524 | 435.8 | 441.9 | 422.6 | 417.6 | 371.7 | 337.9 | 421.2
1598 | 1423 | 524 | 435.8 | 442.2 | 422.7 | 417.6 | 371.7 | 337.8 | 421.2
1599 | 1424 | 523.9 | 435.7 | 442.1 | 422.8 | 417.6 | 371.8 | 337.8 | 421
1600 | 1425 | 523.6 | 435.9 | 442.1 | 423 | 417.6 | 372 | 337.7 | 421.1
1601 | 1426 | 523.4 | 436 | 442.2 | 423.2 | 417.6 | 372 | 337.7 | 421.1
1602 | 1427 | 523.3 | 436 | 442.3 | 423.3 | 417.5 | 372.1 | 337.7 | 421.1
1603 | 1428 | 523 | 436 | 442.5 | 423.4 | 417.5 | 372.2 | 337.7 | 421
1604 | 1429 | 522.4 | 436 | 442.4 | 423.5 | 417.4 | 372.3 | 337.6 | 421
1605 | 1430 | 522.1 | 436.1 | 442.7 | 423.7 | 417.3 | 372.3 | 337.6 | 421
1606 | 1431 | 522 | 436.1 | 443.2 | 423.8 | 417.3 | 372.3 | 337.6 | 421
1607 | 1432 | 522 | 436 | 443.3 | 423.9 | 417.2 | 372.3 | 337.6 | 421.1
1608 | 1433 | 522 | 436.1 | 443.4 | 424 | 417.2 | 372.3 | 337.7 | 421.1
1609 | 1434 | 521.9 | 436.2 | 443.3 | 424.1 | 417.1 | 372.4 | 337.8 | 421.2
1610 | 1435 | 521.8 | 436.2 | 443.3 | 424.3 | 417.1 | 372.5 | 337.7 | 421.2
1611 | 1436 | 521.6 | 436.1 | 443.5 | 424.4 | 417.1 | 372.5 | 337.7 | 421.3
1612 | 1437 | 521.6 | 436.2 | 443.5 | 424.5 | 417.1 | 372.6 | 337.8 | 421.3
1613 | 1438 | 521.7 | 436.3 | 443.6 | 424.6 | 417.2 | 372.7 | 337.7 | 421.4
1614 | 1439 | 521.7 | 436.4 | 443.6 | 424.7 | 417.2 | 372.7 | 337.6 | 421.4
1615 | 1440 | 521.8 | 436.5 | 443.7 | 424.8 | 417.3 | 372.8 | 337.6 | 421.5
1616 | 1441 | 521.9 | 436.5 | 444 | 424.9 | 417.5 | 372.9 | 337.4 | 421.5
1617 | 1442 | 522.1 | 436.6 | 444.3 | 425 | 417.6 | 373 | 337.4 | 421.5
1618 | 1443 | 522.3 | 436.7 | 444.5 | 425 | 417.8 | 373.1 | 337.4 | 421.5
1619 | 1444 | 522.5 | 436.7 | 444.5 | 425.1 | 418 | 373.2 | 337.2 | 421.6
1620 | 1445 | 522.7 | 436.8 | 444.5 | 425.2 | 418.2 | 373.2 | 337 | 421.7
1621 | 1446 | 522.9 | 436.9 | 444.7 | 425.3 | 418.4 | 373.3 | 336.8 | 421.8
1622 | 1447 | 522.8 | 436.9 | 445 | 425.4 | 418.6 | 373.3 | 336.8 | 421.8
1623 | 1448 | 522.7 | 436.9 | 445 | 425.6 | 418.8 | 373.4 | 336.7 | 421.8
1624 | 1449 | 522.9 | 437 | 444.9 | 425.7 | 419 | 373.4 | 336.8 | 421.9
1625 | 1450 | 523 | 437.1 | 444.9 | 425.9 | 419.2 | 373.5 | 336.8 | 422
1626 | 1451 | 523 | 437.1 | 445 | 426 | 419.4 | 373.6 | 336.7 | 422
1627 | 1452 | 522.9 | 437.2 | 445.2 | 426.2 | 419.6 | 373.6 | 336.8 | 422.1
1628 | 1453 | 522.8 | 437.3 | 445.3 | 426.4 | 419.9 | 373.7 | 336.8 | 422.1
1629 | 1454 | 522.8 | 437.3 | 445.5 | 426.6 | 420.1 | 373.8 | 336.8 | 422.2
1630 | 1455 | 522.7 | 437.3 | 445.6 | 426.7 | 420.3 | 373.8 | 336.8 | 422.2
1631 | 1456 | 522.6 | 437.4 | 445.6 | 427 | 420.5 | 373.7 | 336.7 | 422.3
1632 | 1457 | 522.5 | 437.6 | 445.7 | 427.3 | 420.7 | 373.8 | 336.7 | 422.3
1633 | 1458 | 522.6 | 437.7 | 445.9 | 427.4 | 420.9 | 373.9 | 336.7 | 422.4
1634 | 1459 | 522.6 | 437.8 | 446.3 | 427.5 | 421.1 | 374 | 336.8 | 422.5
1635 | 1460 | 522.5 | 437.9 | 446.3 | 427.7 | 421.3 | 373.9 | 336.8 | 422.5
1636 | 1461 | 522.6 | 438 | 446.5 | 427.9 | 421.5 | 373.9 | 336.8 | 422.5
1637 | 1462 | 522.8 | 437.9 | 446.6 | 428.2 | 421.7 | 373.9 | 336.8 | 422.5
1638 | 1463 | 522.8 | 438 | 446.8 | 428.3 | 421.9 | 374 | 336.8 | 422.6
1639 | 1464 | 522.7 | 438.1 | 447.1 | 428.4 | 422.1 | 374.1 | 336.7 | 422.7
1640 | 1465 | 522.8 | 438.3 | 447.2 | 428.4 | 422.3 | 374.2 | 336.7 | 422.8
1641 | 1466 | 522.8 | 438.5 | 447.4 | 428.5 | 422.4 | 374.4 | 336.7 | 422.9
1642 | 1467 | 522.8 | 438.6 | 447.5 | 428.6 | 422.6 | 374.5 | 336.7 | 423
1643 | 1468 | 522.8 | 438.7 | 447.8 | 428.9 | 422.8 | 374.6 | 336.7 | 423
1644 | 1469 | 522.7 | 438.8 | 447.9 | 429.2 | 423 | 374.7 | 336.7 | 423.1
1645 | 1470 | 522.5 | 438.7 | 447.9 | 429.2 | 423.2 | 374.7 | 336.7 | 423.1
1646 | 1471 | 522.4 | 438.7 | 448.1 | 429.2 | 423.4 | 374.8 | 336.6 | 423.1
1647 | 1472 | 522.5 | 438.8 | 448.2 | 429.5 | 423.7 | 375 | 336.6 | 423.1
1648 | 1473 | 522.5 | 438.8 | 448.3 | 429.8 | 423.9 | 375.1 | 336.5 | 423.2
1649 | 1474 | 522.5 | 439.1 | 448.3 | 429.9 | 424.1 | 375.1 | 336.4 | 423.3
1650 | 1475 | 522.6 | 439.2 | 448.5 | 430 | 424.4 | 375.2 | 336.4 | 423.4
1651 | 1476 | 522.6 | 439.3 | 448.8 | 430.3 | 424.6 | 375.1 | 336.4 | 423.4
1652 | 1477 | 522.5 | 439.4 | 449 | 430.6 | 424.8 | 375.1 | 336.4 | 423.4
1653 | 1478 | 522.2 | 439.5 | 449 | 430.9 | 425 | 375.1 | 336.4 | 423.4
1654 | 1479 | 522 | 439.4 | 448.8 | 431 | 425.3 | 375 | 336.5 | 423.5
1655 | 1480 | 522.1 | 439.4 | 448.9 | 431.1 | 425.5 | 375 | 336.6 | 423.5
1656 | 1481 | 522.3 | 439.6 | 449.1 | 431.4 | 425.7 | 375 | 336.7 | 423.5
1657 | 1482 | 522.3 | 439.8 | 449.3 | 431.6 | 426 | 375 | 336.7 | 423.6
1658 | 1483 | 522.5 | 440 | 449.4 | 431.7 | 426.2 | 374.9 | 336.7 | 423.7
1659 | 1484 | 522.8 | 440.1 | 449.4 | 431.8 | 426.4 | 374.8 | 336.7 | 423.8
1660 | 1485 | 522.8 | 440.2 | 449.6 | 431.8 | 426.6 | 374.7 | 336.7 | 423.8
1661 | 1486 | 522.8 | 440.3 | 449.7 | 431.9 | 426.8 | 374.7 | 336.6 | 424
1662 | 1487 | 522.9 | 440.3 | 450 | 432 | 427.1 | 374.6 | 336.6 | 424.1
1663 | 1488 | 523 | 440.2 | 449.9 | 432.1 | 427.3 | 374.6 | 336.6 | 424.2
1664 | 1489 | 523.1 | 440.1 | 450.1 | 432.2 | 427.5 | 374.6 | 336.5 | 424.2
1665 | 1490 | 523.2 | 440.4 | 450.3 | 432.3 | 427.7 | 374.6 | 336.5 | 424.2
1666 | 1491 | 523.5 | 440.5 | 450.4 | 432.4 | 427.8 | 374.6 | 336.5 | 424.3
1667 | 1492 | 523.5 | 440.6 | 450.6 | 432.5 | 428 | 374.6 | 336.5 | 424.3
1668 | 1493 | 523.6 | 440.7 | 450.8 | 432.5 | 428.2 | 374.5 | 336.5 | 424.2
1669 | 1494 | 523.5 | 440.7 | 451 | 432.6 | 428.3 | 374.5 | 336.5 | 424.3
1670 | 1495 | 523.4 | 440.7 | 451.1 | 432.7 | 428.5 | 374.6 | 336.6 | 424.4
1671 | 1496 | 523.4 | 440.5 | 451.1 | 432.9 | 428.6 | 374.6 | 336.6 | 424.5
1672 | 1497 | 523.4 | 440.7 | 451.2 | 433.2 | 428.8 | 374.5 | 336.6 | 424.5
1673 | 1498 | 523.2 | 441 | 451.2 | 433.4 | 429 | 374.4 | 336.7 | 424.6
1674 | 1499 | 523 | 441 | 451.3 | 433.6 | 429.2 | 374.3 | 336.7 | 424.7
1675 | 1500 | 522.9 | 441 | 451.4 | 433.8 | 429.3 | 374.2 | 336.7 | 424.8
1676 | 1501 | 522.8 | 441.1 | 451.5 | 433.9 | 429.4 | 374.2 | 336.9 | 424.8
1677 | 1502 | 522.6 | 441.2 | 451.6 | 434.1 | 429.6 | 374.1 | 336.9 | 424.9
1678 | 1503 | 522.6 | 441.4 | 451.7 | 434.3 | 429.7 | 374 | 336.9 | 424.9
1679 | 1504 | 522.4 | 441.3 | 451.8 | 434.5 | 429.8 | 373.9 | 336.9 | 424.9
1680 | 1505 | 522.5 | 441.3 | 451.9 | 434.5 | 430 | 373.7 | 336.9 | 424.8
1681 | 1506 | 522.4 | 441.3 | 451.9 | 434.7 | 430.1 | 373.6 | 337 | 424.8
1682 | 1507 | 522.2 | 441.4 | 452 | 434.9 | 430.2 | 373.5 | 336.9 | 424.7
1683 | 1508 | 522.1 | 441.4 | 452.1 | 435.1 | 430.3 | 373.4 | 337 | 424.7
1684 | 1509 | 522.1 | 441.2 | 452.2 | 435.3 | 430.5 | 373.3 | 336.9 | 424.6
1685 | 1510 | 522 | 441.3 | 452.4 | 435.4 | 430.6 | 373.3 | 336.9 | 424.6
1686 | 1511 | 522.1 | 441.3 | 452.5 | 435.6 | 430.7 | 373.2 | 336.8 | 424.7
1687 | 1512 | 522.1 | 441.4 | 452.7 | 435.8 | 430.7 | 373.2 | 336.8 | 424.8
1688 | 1513 | 521.9 | 441.3 | 452.8 | 435.9 | 430.8 | 373.2 | 336.8 | 424.8
1689 | 1514 | 521.7 | 441.5 | 452.8 | 436 | 430.9 | 373.2 | 336.9 | 424.8
1690 | 1515 | 521.6 | 441.7 | 453 | 436 | 430.8 | 373.3 | 336.8 | 424.8
1691 | 1516 | 521.6 | 441.8 | 453.1 | 436.1 | 430.7 | 373.5 | 336.9 | 424.8
1692 | 1517 | 521.7 | 441.9 | 453.2 | 436.1 | 430.7 | 373.6 | 336.8 | 424.8
1693 | 1518 | 521.9 | 441.9 | 453.3 | 436.2 | 430.7 | 373.6 | 336.8 | 424.8
1694 | 1519 | 522.1 | 441.9 | 453.4 | 436.3 | 430.8 | 373.6 | 336.8 | 424.8
1695 | 1520 | 522.4 | 441.9 | 453.6 | 436.4 | 430.9 | 373.5 | 336.9 | 424.8
1696 | 1521 | 522.4 | 442 | 453.6 | 436.6 | 431 | 373.4 | 336.9 | 424.8
1697 | 1522 | 522.3 | 442 | 453.7 | 436.7 | 431.1 | 373.4 | 337 | 424.8
1698 | 1523 | 522.5 | 441.9 | 453.8 | 436.9 | 431.2 | 373.3 | 336.9 | 424.8
1699 | 1524 | 522.8 | 442 | 453.9 | 436.9 | 431.2 | 373.4 | 337 | 424.9
1700 | 1525 | 522.9 | 442.2 | 454 | 436.8 | 431.3 | 373.4 | 337 | 424.8
1701 | 1526 | 522.9 | 442.2 | 454.2 | 436.8 | 431.3 | 373.4 | 337 | 424.8
1702 | 1527 | 522.9 | 442.1 | 454.3 | 436.8 | 431.3 | 373.3 | 337 | 424.9
1703 | 1528 | 522.9 | 442.3 | 454.4 | 436.9 | 431.3 | 373.3 | 337 | 424.9
1704 | 1529 | 522.9 | 442.4 | 454.6 | 437 | 431.3 | 373.3 | 337.1 | 425
1705 | 1530 | 522.9 | 442.4 | 454.6 | 437 | 431.3 | 373.3 | 337.1 | 425.1
1706 | 1531 | 523 | 442.4 | 454.7 | 437 | 431.2 | 373.4 | 337 | 425.2
1707 | 1532 | 523.1 | 442.3 | 454.8 | 437.1 | 431.3 | 373.4 | 337 | 425.2
1708 | 1533 | 522.9 | 442.4 | 455 | 437.1 | 431.3 | 373.5 | 337 | 425.1
1709 | 1534 | 522.7 | 442.5 | 455.1 | 436.9 | 431.3 | 373.6 | 336.9 | 425.1
1710 | 1535 | 522.7 | 442.4 | 455.2 | 437 | 431.4 | 373.6 | 337 | 425.1
1711 | 1536 | 522.8 | 442.7 | 455.3 | 437.1 | 431.4 | 373.6 | 336.9 | 425.1
1712 | 1537 | 522.8 | 442.9 | 455.4 | 437.1 | 431.3 | 373.4 | 337.1 | 425.1
1713 | 1538 | 523 | 442.9 | 455.5 | 437 | 431.3 | 373.2 | 337 | 425.1
1714 | 1539 | 523 | 442.9 | 455.5 | 436.9 | 431.3 | 373 | 337 | 425.1
1715 | 1540 | 523.1 | 442.5 | 455.6 | 436.8 | 431.2 | 372.9 | 337.1 | 425.2
1716 | 1541 | 523.2 | 442.9 | 455.7 | 436.8 | 431.2 | 372.8 | 337.1 | 425.4
1717 | 1542 | 523.3 | 443.2 | 455.8 | 437 | 431.2 | 372.8 | 337.1 | 425.5
1718 | 1543 | 523.2 | 443.2 | 455.7 | 437.2 | 431.2 | 372.7 | 337 | 425.5
1719 | 1544 | 523.2 | 443.2 | 455.9 | 437.2 | 431.2 | 372.5 | 337 | 425.4
1720 | 1545 | 523.3 | 443.3 | 456 | 437.2 | 431.3 | 372.3 | 337.1 | 425.4
1721 | 1546 | 523.5 | 443.3 | 456.1 | 437.2 | 431.3 | 372.3 | 337.2 | 425.4
1722 | 1547 | 523.5 | 443.4 | 456.2 | 437.3 | 431.3 | 372.3 | 337.1 | 425.4
1723 | 1548 | 523.4 | 443.4 | 456.4 | 437.2 | 431.3 | 372.4 | 337.1 | 425.5
1724 | 1549 | 523.4 | 443.5 | 456.4 | 437.1 | 431.3 | 372.5 | 337.1 | 425.5
1725 | 1550 | 523.3 | 443.5 | 456.6 | 436.9 | 431.4 | 372.5 | 337.2 | 425.6
1726 | 1551 | 523.1 | 443.6 | 456.8 | 436.9 | 431.4 | 372.6 | 337.1 | 425.7
1727 | 1552 | 523.1 | 443.8 | 456.9 | 437 | 431.6 | 372.7 | 337.1 | 425.7
1728 | 1553 | 522.9 | 443.9 | 457 | 437 | 431.6 | 372.8 | 337.1 | 425.7
1729 | 1554 | 523 | 444 | 457.1 | 436.9 | 431.7 | 372.8 | 337.1 | 425.7
1730 | 1555 | 523 | 444.1 | 457.1 | 436.9 | 431.8 | 372.8 | 337.1 | 425.7
1731 | 1556 | 522.8 | 444.2 | 457.2 | 436.8 | 431.9 | 372.8 | 337.1 | 425.6
1732 | 1557 | 522.5 | 444.1 | 457.3 | 436.8 | 431.9 | 372.9 | 337.2 | 425.6
1733 | 1558 | 522.3 | 443.8 | 457.3 | 436.8 | 432 | 373 | 337.2 | 425.6
1734 | 1559 | 522.2 | 443.9 | 457.5 | 436.9 | 432.1 | 373.1 | 337.2 | 425.6
1735 | 1560 | 522.4 | 444.3 | 457.7 | 436.7 | 432.2 | 373.2 | 337.2 | 425.6
1736 | 1561 | 522.3 | 444.7 | 457.9 | 436.5 | 432.3 | 373.1 | 337.3 | 425.7
1737 | 1562 | 522.2 | 444.7 | 458 | 436.4 | 432.3 | 373.1 | 337.3 | 425.7
1738 | 1563 | 522.3 | 444.7 | 458.2 | 436.3 | 432.4 | 373.1 | 337.4 | 425.7
1739 | 1564 | 522.3 | 444.8 | 458.3 | 436.3 | 432.3 | 373.1 | 337.4 | 425.7
1740 | 1565 | 522.3 | 444.8 | 458.5 | 436.2 | 432.3 | 373.1 | 337.4 | 425.7
1741 | 1566 | 522.3 | 444.8 | 458.6 | 436.2 | 432.3 | 373.1 | 337.4 | 425.8
1742 | 1567 | 522.5 | 444.8 | 458.7 | 436.2 | 432.3 | 373.1 | 337.4 | 425.8
1743 | 1568 | 522.7 | 444.7 | 458.8 | 436.1 | 432.3 | 373.1 | 337.4 | 425.8
1744 | 1569 | 522.8 | 444.8 | 458.8 | 436.2 | 432.4 | 373.1 | 337.3 | 425.8
1745 | 1570 | 522.8 | 444.9 | 459 | 436.2 | 432.4 | 373.1 | 337.3 | 425.8
1746 | 1571 | 522.7 | 444.9 | 459.1 | 436.3 | 432.4 | 373.1 | 337.3 | 425.7
1747 | 1572 | 522.6 | 445 | 459.2 | 436.3 | 432.5 | 373 | 337.2 | 425.7
1748 | 1573 | 522.5 | 445 | 459.4 | 436.4 | 432.5 | 372.9 | 337.2 | 425.8
1749 | 1574 | 522.5 | 445 | 459.4 | 436.5 | 432.6 | 372.9 | 337.1 | 425.8
1750 | 1575 | 522.5 | 445.1 | 459.6 | 436.6 | 432.7 | 372.9 | 337.1 | 425.8
1751 | 1576 | 522.5 | 445.2 | 459.8 | 436.8 | 432.8 | 372.8 | 337.1 | 425.9
1752 | 1577 | 522.6 | 445.3 | 460 | 436.9 | 432.8 | 372.8 | 336.8 | 425.9
1753 | 1578 | 522.7 | 445.3 | 460.1 | 437 | 432.9 | 372.7 | 336.7 | 426
1754 | 1579 | 522.9 | 445.4 | 460.2 | 437.1 | 433 | 372.7 | 336.8 | 425.9
1755 | 1580 | 523.1 | 445.5 | 460.3 | 437 | 433 | 372.8 | 336.7 | 425.8
1756 | 1581 | 523.1 | 445.6 | 460.4 | 437.1 | 433.1 | 372.9 | 336.8 | 425.7
1757 | 1582 | 523.1 | 445.8 | 460.6 | 437.1 | 433.1 | 373 | 336.7 | 425.7
1758 | 1583 | 523 | 445.9 | 460.7 | 437.1 | 433.1 | 373 | 336.7 | 425.7
1759 | 1584 | 523 | 445.9 | 460.8 | 437 | 433.2 | 373 | 336.7 | 425.7
1760 | 1585 | 522.8 | 446 | 460.9 | 437 | 433.2 | 373 | 336.7 | 425.7
1761 | 1586 | 522.9 | 446.1 | 461.1 | 437 | 433.3 | 373 | 336.7 | 425.6
1762 | 1587 | 523 | 446.2 | 461.2 | 437.1 | 433.3 | 373 | 336.7 | 425.6
1763 | 1588 | 522.9 | 446.3 | 461.3 | 437.1 | 433.4 | 373 | 336.7 | 425.4
1764 | 1589 | 523 | 446.4 | 461.5 | 437.2 | 433.4 | 373 | 336.7 | 425.5
1765 | 1590 | 522.9 | 446.5 | 461.7 | 437.3 | 433.4 | 373.1 | 336.8 | 425.5
1766 | 1591 | 522.8 | 446.6 | 461.7 | 437.4 | 433.5 | 373.1 | 336.8 | 425.5
1767 | 1592 | 522.8 | 446.6 | 461.9 | 437.4 | 433.4 | 373.1 | 336.9 | 425.4
1768 | 1593 | 523 | 446.7 | 462.1 | 437.4 | 433.4 | 373.1 | 337 | 425.4
1769 | 1594 | 523 | 446.8 | 462.2 | 437.4 | 433.3 | 373.1 | 337 | 425.3
1770 | 1595 | 523.1 | 446.9 | 462.3 | 437.5 | 433.3 | 373 | 337 | 425.3
1771 | 1596 | 523.2 | 447 | 462.4 | 437.5 | 433.3 | 373 | 337.1 | 425.3
1772 | 1597 | 523.2 | 447 | 462.6 | 437.5 | 433.3 | 373 | 337.1 | 425.4
1773 | 1598 | 523.3 | 447 | 462.7 | 437.5 | 433.3 | 373 | 337.1 | 425.4
1774 | 1599 | 523.2 | 447.1 | 462.8 | 437.5 | 433.3 | 373.1 | 337.2 | 425.4
1775 | 1600 | 523.2 | 447.1 | 462.9 | 437.6 | 433.3 | 373.1 | 337.3 | 425.4
1776 | 1601 | 523.3 | 447.3 | 463.1 | 437.6 | 433.3 | 373.1 | 337.3 | 425.4
1777 | 1602 | 523.5 | 447.5 | 463.3 | 437.6 | 433.4 | 373.2 | 337.3 | 425.4
1778 | 1603 | 523.7 | 447.6 | 463.5 | 437.6 | 433.5 | 373.3 | 337.2 | 425.4
1779 | 1604 | 524 | 447.6 | 463.6 | 437.6 | 433.7 | 373.4 | 337.2 | 425.4
1780 | 1605 | 523.9 | 447.8 | 463.7 | 437.7 | 433.8 | 373.4 | 337.2 | 425.4
1781 | 1606 | 523.8 | 447.8 | 463.8 | 437.9 | 433.9 | 373.3 | 337.2 | 425.4
1782 | 1607 | 523.8 | 447.9 | 464 | 438 | 434 | 373.3 | 337.2 | 425.4
1783 | 1608 | 524 | 448 | 464.2 | 438.2 | 434.1 | 373.2 | 337.2 | 425.3
1784 | 1609 | 524.1 | 448.1 | 464.3 | 438.2 | 434.2 | 373 | 337.2 | 425.3
1785 | 1610 | 524 | 448.2 | 464.5 | 438.3 | 434.2 | 372.8 | 337.3 | 425.2
1786 | 1611 | 523.9 | 448.3 | 464.7 | 438.3 | 434.2 | 372.8 | 337.3 | 425.2
1787 | 1612 | 524 | 448.4 | 464.9 | 438.2 | 434.2 | 372.8 | 337.4 | 425.3
1788 | 1613 | 524.1 | 448.4 | 465 | 438.2 | 434.2 | 372.8 | 337.3 | 425.3
1789 | 1614 | 524.1 | 448.5 | 465.2 | 438.2 | 434.2 | 372.9 | 337.4 | 425.3
1790 | 1615 | 523.9 | 448.6 | 465.4 | 438.2 | 434.1 | 373 | 337.4 | 425.4
1791 | 1616 | 523.9 | 448.6 | 465.5 | 438.2 | 434.1 | 373.1 | 337.4 | 425.3
1792 | 1617 | 523.8 | 448.7 | 465.7 | 438.1 | 434.1 | 373.3 | 337.4 | 425.3
1793 | 1618 | 523.8 | 448.9 | 465.8 | 438 | 434 | 373.5 | 337.5 | 425.3
1794 | 1619 | 524 | 449 | 466.1 | 438.1 | 434 | 373.5 | 337.5 | 425.2
1795 | 1620 | 523.9 | 449.1 | 466.3 | 438.1 | 433.9 | 373.5 | 337.6 | 425.1
1796 | 1621 | 523.8 | 449.3 | 466.5 | 438.3 | 433.9 | 373.5 | 337.7 | 425.1
1797 | 1622 | 523.8 | 449.4 | 466.6 | 438.4 | 433.8 | 373.5 | 337.6 | 425
1798 | 1623 | 523.8 | 449.6 | 466.8 | 438.6 | 433.7 | 373.6 | 337.6 | 424.9
1799 | 1624 | 523.7 | 449.6 | 466.7 | 438.6 | 433.6 | 373.5 | 337.6 | 424.7
1800 | 1625 | 523.8 | 449.8 | 467.1 | 438.6 | 433.6 | 373.5 | 337.6 | 424.7
1801 | 1626 | 524 | 449.9 | 467.2 | 438.8 | 433.6 | 373.5 | 337.7 | 424.7
1802 | 1627 | 524.1 | 450 | 467.5 | 438.7 | 433.5 | 373.6 | 337.8 | 424.6
1803 | 1628 | 524.4 | 450.1 | 467.6 | 438.7 | 433.5 | 373.7 | 337.8 | 424.7
1804 | 1629 | 524.4 | 450.3 | 467.7 | 438.7 | 433.5 | 373.9 | 337.8 | 424.7
1805 | 1630 | 524.4 | 450.3 | 467.9 | 438.8 | 433.5 | 374.1 | 337.8 | 424.7
1806 | 1631 | 524.3 | 450.4 | 468.1 | 438.9 | 433.4 | 374.3 | 337.9 | 424.6
1807 | 1632 | 524.3 | 450.6 | 468.3 | 438.8 | 433.4 | 374.3 | 337.9 | 424.7
1808 | 1633 | 524.4 | 450.8 | 468.4 | 438.8 | 433.4 | 374.2 | 337.9 | 424.8
1809 | 1634 | 524.6 | 450.9 | 468.5 | 438.8 | 433.4 | 374.2 | 337.9 | 424.8
1810 | 1635 | 524.6 | 451 | 468.7 | 438.8 | 433.4 | 374.2 | 337.9 | 424.8
1811 | 1636 | 524.5 | 451.2 | 468.8 | 438.8 | 433.4 | 374.2 | 338 | 424.8
1812 | 1637 | 524.6 | 451.4 | 468.9 | 438.8 | 433.4 | 374.1 | 338 | 424.9
1813 | 1638 | 524.7 | 451.5 | 469.1 | 438.8 | 433.4 | 374.1 | 337.9 | 424.9
1814 | 1639 | 524.8 | 451.7 | 469.2 | 438.8 | 433.4 | 373.9 | 337.9 | 424.9
1815 | 1640 | 524.8 | 451.9 | 469.3 | 438.8 | 433.4 | 373.8 | 337.9 | 424.8
1816 | 1641 | 524.9 | 452 | 469.4 | 438.8 | 433.5 | 373.8 | 337.8 | 424.8
1817 | 1642 | 524.7 | 452.2 | 469.5 | 438.8 | 433.5 | 373.7 | 337.8 | 424.8
1818 | 1643 | 524.6 | 452.4 | 469.7 | 438.8 | 433.6 | 373.7 | 337.9 | 424.8
1819 | 1644 | 524.6 | 452.5 | 469.8 | 438.8 | 433.7 | 373.7 | 338 | 424.8
1820 | 1645 | 524.7 | 452.6 | 469.9 | 438.9 | 433.7 | 373.6 | 338 | 424.8
1821 | 1646 | 524.7 | 452.8 | 470.1 | 438.9 | 433.8 | 373.5 | 338 | 424.9
1822 | 1647 | 524.7 | 453 | 470.2 | 438.8 | 433.9 | 373.3 | 337.9 | 424.9
1823 | 1648 | 524.8 | 453.1 | 470.3 | 438.9 | 434 | 373.2 | 337.9 | 424.9
1824 | 1649 | 524.7 | 453.3 | 470.4 | 438.9 | 434.2 | 373.1 | 338 | 424.9
1825 | 1650 | 524.5 | 453.4 | 470.5 | 438.9 | 434.3 | 373.1 | 338.1 | 424.8
1826 | 1651 | 524.3 | 453.5 | 470.6 | 438.9 | 434.4 | 373.2 | 338.2 | 424.9
1827 | 1652 | 524.1 | 453.6 | 470.6 | 439 | 434.6 | 373.2 | 338.2 | 424.9
1828 | 1653 | 523.9 | 453.8 | 470.8 | 439 | 434.7 | 373.3 | 338.2 | 424.9
1829 | 1654 | 523.8 | 454.1 | 470.9 | 439.1 | 434.8 | 373.4 | 338.2 | 424.9
1830 | 1655 | 523.8 | 454.3 | 471 | 439.1 | 435 | 373.6 | 338.3 | 424.8
1831 | 1656 | 523.9 | 454.5 | 471.1 | 439.1 | 435.1 | 373.6 | 338.2 | 424.8
1832 | 1657 | 524.1 | 454.6 | 471.2 | 439.1 | 435.2 | 373.7 | 338.2 | 424.8
1833 | 1658 | 524.1 | 454.8 | 471.3 | 439.2 | 435.2 | 373.9 | 338.2 | 424.8
1834 | 1659 | 524.2 | 455.1 | 471.4 | 439.2 | 435.3 | 374 | 338.1 | 424.8
1835 | 1660 | 524.2 | 455.3 | 471.5 | 439.1 | 435.3 | 374.1 | 338.1 | 424.8
1836 | 1661 | 524.3 | 455.5 | 471.6 | 439.1 | 435.3 | 374.1 | 338.1 | 424.7
1837 | 1662 | 524.3 | 455.7 | 471.8 | 439.1 | 435.3 | 374 | 338.1 | 424.7
1838 | 1663 | 524.3 | 455.8 | 472 | 439.2 | 435.3 | 374 | 338.2 | 424.7
1839 | 1664 | 524.4 | 456.1 | 472.1 | 439.2 | 435.2 | 373.9 | 338.2 | 424.7
1840 | 1665 | 524.4 | 456.3 | 472.3 | 439.2 | 435.2 | 373.8 | 338.2 | 424.7
1841 | 1666 | 524.3 | 456.5 | 472.4 | 439.2 | 435.2 | 373.7 | 338.2 | 424.6
1842 | 1667 | 524.1 | 456.8 | 472.5 | 439.2 | 435.2 | 373.8 | 338.1 | 424.6
1843 | 1668 | 523.9 | 457 | 472.7 | 439.2 | 435.2 | 373.9 | 338.1 | 424.6
1844 | 1669 | 523.5 | 457.2 | 472.8 | 439.2 | 435.2 | 374 | 338.1 | 424.6
1845 | 1670 | 523.3 | 457.3 | 472.9 | 439.2 | 435.3 | 374.2 | 338 | 424.5
1846 | 1671 | 523.2 | 457.5 | 473.1 | 439.2 | 435.3 | 374.2 | 338.1 | 424.5
1847 | 1672 | 523.1 | 457.7 | 473.2 | 439.3 | 435.3 | 374.2 | 338.1 | 424.5
1848 | 1673 | 522.8 | 457.9 | 473.4 | 439.3 | 435.3 | 374.2 | 338.1 | 424.6
1849 | 1674 | 522.5 | 458.1 | 473.6 | 439.3 | 435.3 | 374.2 | 338.1 | 424.5
1850 | 1675 | 522.3 | 458.3 | 473.7 | 439.3 | 435.3 | 374.1 | 338.2 | 424.5
1851 | 1676 | 522.5 | 458.5 | 473.9 | 439.3 | 435.3 | 374 | 338.2 | 424.6
1852 | 1677 | 522.6 | 458.7 | 474 | 439.4 | 435.3 | 374 | 338.2 | 424.7
1853 | 1678 | 522.5 | 458.8 | 474.2 | 439.4 | 435.3 | 374 | 338.3 | 424.7
1854 | 1679 | 522.4 | 459.1 | 474.3 | 439.4 | 435.3 | 374.1 | 338.3 | 424.6
1855 | 1680 | 522.5 | 459.3 | 474.4 | 439.5 | 435.4 | 373.9 | 338.3 | 424.6
1856 | 1681 | 522.5 | 459.4 | 474.6 | 439.5 | 435.5 | 373.7 | 338.4 | 424.6
1857 | 1682 | 522.6 | 459.6 | 474.7 | 439.6 | 435.6 | 373.5 | 338.6 | 424.5
1858 | 1683 | 522.7 | 459.8 | 474.9 | 439.7 | 435.8 | 373.4 | 338.7 | 424.6
1859 | 1684 | 522.6 | 460 | 475 | 439.8 | 435.9 | 373.3 | 338.7 | 424.6
1860 | 1685 | 522.6 | 460.2 | 475.2 | 439.9 | 436.1 | 373.3 | 338.7 | 424.7
1861 | 1686 | 522.7 | 460.4 | 475.4 | 440 | 436.3 | 373.3 | 338.7 | 424.8
1862 | 1687 | 522.9 | 460.6 | 475.5 | 440.2 | 436.5 | 373.4 | 338.7 | 424.8
1863 | 1688 | 523.1 | 460.7 | 475.7 | 440.3 | 436.7 | 373.5 | 338.7 | 424.9
1864 | 1689 | 523.1 | 460.9 | 475.8 | 440.5 | 436.9 | 373.6 | 338.8 | 424.8
1865 | 1690 | 523.4 | 461.1 | 476 | 440.6 | 437.1 | 373.6 | 338.9 | 424.8
1866 | 1691 | 523.6 | 461.3 | 476.2 | 440.6 | 437.3 | 373.6 | 338.9 | 424.8
1867 | 1692 | 523.5 | 461.6 | 476.4 | 440.6 | 437.4 | 373.8 | 339 | 424.9
1868 | 1693 | 523.2 | 461.8 | 476.5 | 440.7 | 437.5 | 373.9 | 339 | 424.9
1869 | 1694 | 523.1 | 461.9 | 476.7 | 440.7 | 437.6 | 373.9 | 339 | 424.9
1870 | 1695 | 523 | 462.1 | 476.9 | 440.8 | 437.7 | 374 | 339 | 425
1871 | 1696 | 523 | 462.2 | 477 | 440.8 | 437.7 | 374 | 339 | 424.9
1872 | 1697 | 522.9 | 462.4 | 477.2 | 440.9 | 437.8 | 374.1 | 339.1 | 424.8
1873 | 1698 | 522.8 | 462.5 | 477.4 | 441 | 437.9 | 374.2 | 339 | 424.8
1874 | 1699 | 522.9 | 462.7 | 477.6 | 441.1 | 437.9 | 374.4 | 339 | 424.8
1875 | 1700 | 522.7 | 462.9 | 477.8 | 441.2 | 438 | 374.5 | 338.9 | 424.8
1876 | 1701 | 522.6 | 463.1 | 478 | 441.1 | 438 | 374.5 | 338.8 | 424.8
1877 | 1702 | 522.6 | 463.3 | 478.3 | 441.1 | 438 | 374.5 | 338.8 | 424.8
1878 | 1703 | 522.5 | 463.4 | 478.5 | 441.2 | 438 | 374.6 | 338.7 | 424.9
1879 | 1704 | 522.2 | 463.6 | 478.7 | 441.3 | 438 | 374.6 | 338.6 | 425
1880 | 1705 | 522 | 463.7 | 479 | 441.3 | 438.1 | 374.6 | 338.6 | 425
1881 | 1706 | 522.2 | 463.8 | 479.2 | 441.3 | 438.1 | 374.6 | 338.6 | 425.1
1882 | 1707 | 522.4 | 463.9 | 479.4 | 441.3 | 438.2 | 374.6 | 338.5 | 425.1
1883 | 1708 | 522.5 | 464 | 479.6 | 441.4 | 438.3 | 374.5 | 338.4 | 425.1
1884 | 1709 | 522.7 | 464.2 | 479.7 | 441.5 | 438.4 | 374.4 | 338.4 | 425
1885 | 1710 | 522.7 | 464.3 | 479.9 | 441.5 | 438.6 | 374.4 | 338.4 | 425
1886 | 1711 | 522.8 | 464.5 | 480 | 441.6 | 438.7 | 374.3 | 338.3 | 425.1
1887 | 1712 | 522.8 | 464.6 | 480.2 | 441.7 | 438.9 | 374.3 | 338.3 | 425.1
1888 | 1713 | 522.9 | 464.8 | 480.4 | 441.7 | 439 | 374.3 | 338.3 | 425.3
1889 | 1714 | 523 | 465 | 480.6 | 441.8 | 439.2 | 374.2 | 338.3 | 425.3
1890 | 1715 | 523 | 465.2 | 480.8 | 441.9 | 439.3 | 374.2 | 338.3 | 425.4
1891 | 1716 | 523 | 465.4 | 481 | 442 | 439.4 | 374.1 | 338.3 | 425.5
1892 | 1717 | 523 | 465.6 | 481.2 | 442.1 | 439.5 | 374 | 338.2 | 425.5
1893 | 1718 | 523.1 | 465.8 | 481.4 | 442.1 | 439.7 | 374 | 338.3 | 425.5
1894 | 1719 | 523.1 | 466 | 481.5 | 442.2 | 439.8 | 374 | 338.3 | 425.7
1895 | 1720 | 523.1 | 466.2 | 481.7 | 442.3 | 439.9 | 373.9 | 338.4 | 425.8
1896 | 1721 | 522.8 | 466.4 | 481.9 | 442.3 | 440 | 373.9 | 338.4 | 425.9
1897 | 1722 | 522.8 | 466.6 | 482.1 | 442.4 | 440.1 | 374 | 338.3 | 426
1898 | 1723 | 522.6 | 466.8 | 482.4 | 442.5 | 440.2 | 374.1 | 338.3 | 426
1899 | 1724 | 522.5 | 467 | 482.6 | 442.6 | 440.3 | 374.1 | 338.3 | 426
1900 | 1725 | 522.3 | 467.1 | 482.9 | 442.7 | 440.4 | 374.1 | 338.3 | 426
1901 | 1726 | 522.3 | 467.3 | 483.1 | 442.8 | 440.6 | 374 | 338.3 | 426
1902 | 1727 | 522.3 | 467.5 | 483.4 | 442.8 | 440.7 | 373.9 | 338.3 | 426.2
1903 | 1728 | 522.4 | 467.7 | 483.6 | 442.9 | 440.9 | 373.9 | 338.3 | 426.3
1904 | 1729 | 522.4 | 467.9 | 483.8 | 443.1 | 441 | 373.9 | 338.3 | 426.4
1905 | 1730 | 522.5 | 468.1 | 484.1 | 443.3 | 441.3 | 373.9 | 338.2 | 426.4
1906 | 1731 | 522.6 | 468.3 | 484.3 | 443.4 | 441.5 | 374 | 338.2 | 426.5
1907 | 1732 | 522.7 | 468.5 | 484.6 | 443.5 | 441.7 | 374 | 338.2 | 426.5
1908 | 1733 | 522.8 | 468.6 | 484.8 | 443.5 | 442 | 373.9 | 338.2 | 426.6
1909 | 1734 | 522.9 | 468.8 | 485 | 443.6 | 442.2 | 373.8 | 338.2 | 426.7
1910 | 1735 | 522.7 | 469 | 485.3 | 443.8 | 442.4 | 373.6 | 338.2 | 426.8
1911 | 1736 | 522.8 | 469.2 | 485.6 | 443.9 | 442.6 | 373.5 | 338.3 | 426.9
1912 | 1737 | 523 | 469.4 | 485.8 | 444 | 442.8 | 373.5 | 338.3 | 426.9
1913 | 1738 | 523 | 469.6 | 486.1 | 444.2 | 443 | 373.5 | 338.4 | 427
1914 | 1739 | 522.8 | 469.8 | 486.3 | 444.3 | 443.3 | 373.5 | 338.5 | 427
1915 | 1740 | 522.9 | 469.9 | 486.6 | 444.4 | 443.5 | 373.4 | 338.6 | 427
1916 | 1741 | 523 | 470.1 | 486.8 | 444.5 | 443.7 | 373.4 | 338.7 | 427
1917 | 1742 | 523.1 | 470.3 | 487.1 | 444.7 | 444 | 373.4 | 338.8 | 427
1918 | 1743 | 523.2 | 470.5 | 487.3 | 444.8 | 444.2 | 373.3 | 338.8 | 427.1
1919 | 1744 | 523.2 | 470.8 | 487.5 | 444.9 | 444.4 | 373.3 | 338.9 | 427.2
1920 | 1745 | 522.9 | 471 | 487.7 | 445 | 444.6 | 373.2 | 339.1 | 427.2
1921 | 1746 | 522.9 | 471.2 | 487.9 | 445.2 | 444.8 | 373.2 | 339.1 | 427.3
1922 | 1747 | 522.7 | 471.5 | 488 | 445.3 | 445 | 373.3 | 339.1 | 427.3
1923 | 1748 | 522.5 | 471.8 | 488.2 | 445.4 | 445.1 | 373.4 | 339.2 | 427.4
1924 | 1749 | 522.4 | 472 | 488.3 | 445.5 | 445.3 | 373.4 | 339.2 | 427.4
1925 | 1750 | 522.5 | 472.2 | 488.5 | 445.6 | 445.4 | 373.4 | 339.3 | 427.3
1926 | 1751 | 522.4 | 472.4 | 488.7 | 445.7 | 445.5 | 373.4 | 339.2 | 427.3
1927 | 1752 | 522.5 | 472.5 | 489 | 445.8 | 445.7 | 373.4 | 339.3 | 427.3
1928 | 1753 | 522.6 | 472.7 | 489.2 | 445.9 | 445.8 | 373.4 | 339.2 | 427.4
1929 | 1754 | 522.7 | 472.9 | 489.4 | 445.9 | 446 | 373.4 | 339.3 | 427.4
1930 | 1755 | 522.7 | 473.1 | 489.6 | 446 | 446.1 | 373.5 | 339.3 | 427.3
1931 | 1756 | 522.8 | 473.3 | 489.8 | 446.1 | 446.2 | 373.7 | 339.3 | 427.4
1932 | 1757 | 523 | 473.6 | 490 | 446.2 | 446.3 | 373.9 | 339.4 | 427.4
1933 | 1758 | 523.1 | 473.8 | 490.2 | 446.2 | 446.3 | 374 | 339.4 | 427.5
1934 | 1759 | 523.3 | 474.1 | 490.4 | 446.3 | 446.4 | 374.1 | 339.5 | 427.5
1935 | 1760 | 523.2 | 474.3 | 490.6 | 446.4 | 446.4 | 374.1 | 339.4 | 427.6
1936 | 1761 | 523.2 | 474.6 | 490.8 | 446.5 | 446.4 | 374.1 | 339.4 | 427.6
1937 | 1762 | 523.2 | 474.9 | 491 | 446.5 | 446.3 | 374.2 | 339.4 | 427.6
1938 | 1763 | 523.3 | 475.2 | 491.2 | 446.6 | 446.3 | 374.2 | 339.4 | 427.6
1939 | 1764 | 523.4 | 475.4 | 491.4 | 446.6 | 446.2 | 374.2 | 339.3 | 427.6
1940 | 1765 | 523.2 | 475.7 | 491.7 | 446.6 | 446.2 | 374.1 | 339.2 | 427.7
1941 | 1766 | 523.1 | 475.9 | 492 | 446.7 | 446.2 | 374 | 339.2 | 427.7
1942 | 1767 | 523.3 | 476.2 | 492.2 | 446.7 | 446.1 | 374 | 339.2 | 427.7
1943 | 1768 | 523.4 | 476.4 | 492.5 | 446.7 | 446 | 374 | 339.2 | 427.7
1944 | 1769 | 523.5 | 476.6 | 492.8 | 446.7 | 446 | 373.9 | 339.2 | 427.8
1945 | 1770 | 523.6 | 476.8 | 493.1 | 446.7 | 446 | 373.7 | 339.2 | 427.9
1946 | 1771 | 523.7 | 477 | 493.4 | 446.7 | 446 | 373.6 | 339.2 | 427.9
1947 | 1772 | 523.9 | 477.2 | 493.6 | 446.7 | 446 | 373.5 | 339.2 | 427.9
1948 | 1773 | 523.9 | 477.5 | 493.9 | 446.8 | 445.9 | 373.4 | 339.2 | 427.9
1949 | 1774 | 524 | 477.8 | 494.3 | 446.9 | 445.9 | 373.1 | 339.3 | 427.9
1950 | 1775 | 523.9 | 478.1 | 494.6 | 446.9 | 445.8 | 373 | 339.3 | 427.8
1951 | 1776 | 523.8 | 478.4 | 494.8 | 447 | 445.8 | 372.9 | 339.4 | 427.7
1952 | 1777 | 523.7 | 478.7 | 495.1 | 447 | 445.7 | 373 | 339.5 | 427.7
1953 | 1778 | 523.6 | 479 | 495.3 | 447 | 445.6 | 373 | 339.6 | 427.7
1954 | 1779 | 523.7 | 479.3 | 495.6 | 447.2 | 445.6 | 373.1 | 339.6 | 427.6
1955 | 1780 | 523.6 | 479.6 | 495.9 | 447.3 | 445.6 | 373.2 | 339.6 | 427.7
1956 | 1781 | 523.5 | 479.9 | 496.2 | 447.4 | 445.6 | 373.2 | 339.6 | 427.8
1957 | 1782 | 523.3 | 480.1 | 496.6 | 447.5 | 445.6 | 373.3 | 339.6 | 427.8
1958 | 1783 | 523.1 | 480.4 | 496.9 | 447.6 | 445.8 | 373.4 | 339.6 | 428
1959 | 1784 | 523 | 480.6 | 497.3 | 447.7 | 445.9 | 373.4 | 339.5 | 428
1960 | 1785 | 522.8 | 480.8 | 497.7 | 447.8 | 446.2 | 373.5 | 339.5 | 428.1
1961 | 1786 | 522.6 | 481 | 498 | 447.9 | 446.4 | 373.5 | 339.5 | 428.2
1962 | 1787 | 522.4 | 481.3 | 498.3 | 448 | 446.6 | 373.5 | 339.5 | 428.2
1963 | 1788 | 522.3 | 481.5 | 498.6 | 448.2 | 446.8 | 373.4 | 339.5 | 428.2
1964 | 1789 | 522.4 | 481.8 | 498.9 | 448.3 | 446.9 | 373.4 | 339.5 | 428.2
1965 | 1790 | 522.4 | 482 | 499.2 | 448.5 | 447.1 | 373.4 | 339.6 | 428.2
1966 | 1791 | 522.4 | 482.2 | 499.5 | 448.7 | 447.3 | 373.4 | 339.5 | 428.2
1967 | 1792 | 522.2 | 482.5 | 499.7 | 448.8 | 447.4 | 373.5 | 339.5 | 428.3
1968 | 1793 | 522.3 | 482.7 | 500 | 449 | 447.6 | 373.6 | 339.5 | 428.3
1969 | 1794 | 522.4 | 483 | 500.1 | 449.2 | 447.8 | 373.6 | 339.5 | 428.4
1970 | 1795 | 522.3 | 483.3 | 500.4 | 449.3 | 448 | 373.6 | 339.5 | 428.4
1971 | 1796 | 522.2 | 483.6 | 500.6 | 449.4 | 448.1 | 373.7 | 339.5 | 428.3
1972 | 1797 | 522 | 483.9 | 500.9 | 449.5 | 448.2 | 373.7 | 339.4 | 428.4
1973 | 1798 | 521.8 | 484.3 | 501.1 | 449.5 | 448.2 | 373.7 | 339.4 | 428.3
1974 | 1799 | 521.7 | 484.6 | 501.4 | 449.6 | 448.3 | 373.8 | 339.4 | 428.3
1975 | 1800 | 521.6 | 484.9 | 501.8 | 449.7 | 448.3 | 373.8 | 339.5 | 428.3
1976 | 1801 | 521.6 | 485.2 | 502.1 | 449.8 | 448.3 | 373.7 | 339.4 | 428.4
1977 | 1802 | 521.6 | 485.5 | 502.5 | 449.8 | 448.3 | 373.8 | 339.3 | 428.4
1978 | 1803 | 521.7 | 485.8 | 502.8 | 449.9 | 448.3 | 373.8 | 339.3 | 428.4
1979 | 1804 | 521.6 | 486.1 | 503.1 | 450 | 448.3 | 373.9 | 339.3 | 428.4
1980 | 1805 | 521.8 | 486.4 | 503.5 | 450 | 448.3 | 373.8 | 339.3 | 428.4
1981 | 1806 | 521.9 | 486.7 | 503.9 | 450.2 | 448.2 | 373.9 | 339.3 | 428.4
1982 | 1807 | 522 | 487 | 504.3 | 450.2 | 448.2 | 373.9 | 339.3 | 428.4
1983 | 1808 | 522 | 487.3 | 504.7 | 450.2 | 448.2 | 374 | 339.3 | 428.3
1984 | 1809 | 521.7 | 487.6 | 505.1 | 450.3 | 448.3 | 373.9 | 339.2 | 428.3
1985 | 1810 | 521.7 | 487.9 | 505.5 | 450.3 | 448.3 | 373.9 | 339.3 | 428.3
1986 | 1811 | 521.8 | 488.1 | 505.9 | 450.4 | 448.4 | 373.9 | 339.2 | 428.4
1987 | 1812 | 522.1 | 488.4 | 506.2 | 450.5 | 448.5 | 373.9 | 339.3 | 428.5
1988 | 1813 | 522.2 | 488.7 | 506.6 | 450.5 | 448.6 | 373.8 | 339.2 | 428.5
1989 | 1814 | 522.2 | 488.9 | 506.9 | 450.7 | 448.7 | 373.8 | 339.3 | 428.5
1990 | 1815 | 522.4 | 489.2 | 507.2 | 450.8 | 448.9 | 373.9 | 339.3 | 428.5
1991 | 1816 | 522.6 | 489.4 | 507.6 | 450.9 | 449 | 374.1 | 339.3 | 428.5
1992 | 1817 | 522.7 | 489.7 | 507.9 | 451 | 449.2 | 374 | 339.4 | 428.3
1993 | 1818 | 522.8 | 489.9 | 508.2 | 451.1 | 449.3 | 374 | 339.4 | 428.3
1994 | 1819 | 522.9 | 490.2 | 508.6 | 451.2 | 449.4 | 374 | 339.4 | 428.2
1995 | 1820 | 522.9 | 490.4 | 508.9 | 451.3 | 449.5 | 373.9 | 339.5 | 428.3
1996 | 1821 | 523 | 490.7 | 509.3 | 451.4 | 449.5 | 373.9 | 339.6 | 428.3
1997 | 1822 | 522.9 | 491 | 509.7 | 451.4 | 449.5 | 373.9 | 339.6 | 428.3
1998 | 1823 | 522.7 | 491.3 | 510 | 451.5 | 449.5 | 374.1 | 339.6 | 428.5
1999 | 1824 | 522.4 | 491.7 | 510.4 | 451.6 | 449.5 | 374.1 | 339.6 | 428.5
2000 | 1825 | 522.1 | 492 | 510.7 | 451.6 | 449.4 | 374.2 | 339.5 | 428.4
2001 | 1826 | 522 | 492.3 | 511 | 451.7 | 449.4 | 374.3 | 339.5 | 428.4
2002 | 1827 | 521.7 | 492.6 | 511.3 | 451.8 | 449.4 | 374.4 | 339.5 | 428.4
2003 | 1828 | 521.6 | 492.9 | 511.6 | 451.8 | 449.5 | 374.4 | 339.5 | 428.4
2004 | 1829 | 521.6 | 493.2 | 511.9 | 451.8 | 449.5 | 374.3 | 339.6 | 428.5
2005 | 1830 | 521.7 | 493.6 | 512.3 | 451.9 | 449.6 | 374.4 | 339.5 | 428.5
2006 | 1831 | 521.8 | 493.9 | 512.6 | 451.9 | 449.6 | 374.5 | 339.6 | 428.5
2007 | 1832 | 521.9 | 494.2 | 512.9 | 452 | 449.7 | 374.7 | 339.6 | 428.5
2008 | 1833 | 522.1 | 494.4 | 513.2 | 452.1 | 449.9 | 374.8 | 339.7 | 428.5
2009 | 1834 | 522.3 | 494.7 | 513.5 | 452.2 | 450.1 | 374.8 | 339.7 | 428.5
2010 | 1835 | 522.5 | 495 | 513.7 | 452.4 | 450.4 | 374.8 | 339.8 | 428.6
2011 | 1836 | 522.8 | 495.3 | 514 | 452.5 | 450.6 | 374.8 | 339.8 | 428.6
2012 | 1837 | 522.9 | 495.6 | 514.2 | 452.6 | 450.9 | 374.7 | 339.8 | 428.7
2013 | 1838 | 523.1 | 496 | 514.4 | 452.6 | 451.1 | 374.6 | 339.8 | 428.7
2014 | 1839 | 523.3 | 496.3 | 514.7 | 452.8 | 451.2 | 374.6 | 339.9 | 428.7
2015 | 1840 | 523.5 | 496.6 | 514.9 | 452.9 | 451.4 | 374.7 | 339.9 | 428.8
2016 | 1841 | 523.7 | 496.9 | 515.1 | 453.1 | 451.6 | 374.7 | 339.9 | 429
2017 | 1842 | 523.6 | 497.2 | 515.4 | 453.2 | 451.9 | 374.8 | 340 | 429
2018 | 1843 | 523.5 | 497.5 | 515.6 | 453.2 | 452.1 | 374.8 | 340.1 | 429.1
2019 | 1844 | 523.6 | 497.8 | 515.9 | 453.4 | 452.4 | 374.8 | 340.2 | 429.2
2020 | 1845 | 523.8 | 498.1 | 516.1 | 453.6 | 452.6 | 374.8 | 340.3 | 429.3
2021 | 1846 | 523.8 | 498.4 | 516.3 | 453.7 | 452.9 | 374.8 | 340.3 | 429.3
2022 | 1847 | 523.7 | 498.7 | 516.6 | 453.8 | 453.1 | 374.8 | 340.3 | 429.4
2023 | 1848 | 523.6 | 499 | 516.9 | 453.9 | 453.3 | 374.8 | 340.3 | 429.4
2024 | 1849 | 523.3 | 499.2 | 517.2 | 454.1 | 453.5 | 374.8 | 340.3 | 429.5
2025 | 1850 | 523 | 499.5 | 517.4 | 454.3 | 453.7 | 374.9 | 340.3 | 429.5
2026 | 1851 | 522.7 | 499.9 | 517.7 | 454.4 | 453.9 | 375 | 340.4 | 429.5
2027 | 1852 | 522.4 | 500 | 518 | 454.5 | 454.1 | 375.1 | 340.4 | 429.6
2028 | 1853 | 522.1 | 500.3 | 518.3 | 454.7 | 454.2 | 375.2 | 340.2 | 429.6
2029 | 1854 | 522.2 | 500.6 | 518.5 | 454.8 | 454.3 | 375.3 | 340.2 | 429.7
2030 | 1855 | 522.3 | 500.9 | 518.7 | 454.9 | 454.4 | 375.3 | 340.2 | 429.7
2031 | 1856 | 522.3 | 501.1 | 518.9 | 455 | 454.4 | 375.4 | 340.2 | 429.8
2032 | 1857 | 522.3 | 501.4 | 519.2 | 455.1 | 454.5 | 375.6 | 340.1 | 429.8
2033 | 1858 | 522.4 | 501.6 | 519.4 | 455.2 | 454.6 | 375.6 | 340.1 | 429.7
2034 | 1859 | 522.8 | 501.8 | 519.8 | 455.4 | 454.7 | 375.6 | 340.2 | 429.7
2035 | 1860 | 523 | 502 | 520.1 | 455.5 | 454.8 | 375.6 | 340.2 | 429.7
2036 | 1861 | 523 | 502.4 | 520.4 | 455.6 | 455 | 375.6 | 340.2 | 429.8
2037 | 1862 | 523 | 502.6 | 520.7 | 455.8 | 455.1 | 375.4 | 340.2 | 429.9
2038 | 1863 | 523.1 | 502.9 | 521 | 455.9 | 455.3 | 375.2 | 340.2 | 430
2039 | 1864 | 523.2 | 503.2 | 521.3 | 456 | 455.5 | 375.1 | 340.2 | 430.2
2040 | 1865 | 523.4 | 503.5 | 521.6 | 456.2 | 455.7 | 375 | 340.3 | 430.2
2041 | 1866 | 523.6 | 503.8 | 521.9 | 456.3 | 455.9 | 374.9 | 340.3 | 430.3
2042 | 1867 | 523.9 | 504.1 | 522.3 | 456.5 | 456.2 | 374.9 | 340.4 | 430.3
2043 | 1868 | 524 | 504.4 | 522.6 | 456.7 | 456.4 | 375 | 340.5 | 430.3
2044 | 1869 | 524 | 504.6 | 523 | 456.8 | 456.7 | 375.1 | 340.6 | 430.5
2045 | 1870 | 524.1 | 504.8 | 523.4 | 457.1 | 457 | 375.3 | 340.6 | 430.6
2046 | 1871 | 524.2 | 505 | 523.8 | 457.3 | 457.2 | 375.4 | 340.7 | 430.6
2047 | 1872 | 524.2 | 505.2 | 524.2 | 457.5 | 457.6 | 375.5 | 340.7 | 430.7
2048 | 1873 | 524.2 | 505.4 | 524.7 | 457.6 | 457.8 | 375.6 | 340.7 | 430.8
2049 | 1874 | 524.1 | 505.6 | 525.1 | 457.9 | 458.1 | 375.7 | 340.7 | 431
2050 | 1875 | 524 | 505.9 | 525.4 | 458 | 458.4 | 375.8 | 340.6 | 431.1
2051 | 1876 | 524 | 506.1 | 525.8 | 458.2 | 458.6 | 376 | 340.5 | 431.2
2052 | 1877 | 524 | 506.3 | 526.2 | 458.4 | 458.8 | 376 | 340.5 | 431.2
2053 | 1878 | 524.2 | 506.5 | 526.6 | 458.5 | 459 | 376.1 | 340.5 | 431.3
2054 | 1879 | 524.2 | 506.8 | 527 | 458.7 | 459.1 | 376.2 | 340.5 | 431.4
2055 | 1880 | 524.2 | 507.1 | 527.3 | 458.9 | 459.2 | 376.2 | 340.5 | 431.4
2056 | 1881 | 524.2 | 507.4 | 527.7 | 459.1 | 459.2 | 376.2 | 340.6 | 431.4
2057 | 1882 | 524.2 | 507.7 | 528.1 | 459.3 | 459.1 | 376.1 | 340.6 | 431.6
2058 | 1883 | 524 | 508.1 | 528.5 | 459.4 | 459.1 | 376.2 | 340.7 | 431.5
2059 | 1884 | 524 | 508.4 | 529 | 459.6 | 459.1 | 376.2 | 340.8 | 431.5
2060 | 1885 | 523.8 | 508.7 | 529.6 | 459.7 | 459.1 | 376.1 | 340.8 | 431.5
2061 | 1886 | 523.6 | 508.9 | 530.1 | 459.8 | 459.2 | 376.1 | 340.9 | 431.5
2062 | 1887 | 523.3 | 509.2 | 530.7 | 459.9 | 459.2 | 376.1 | 340.9 | 431.6
2063 | 1888 | 523.1 | 509.4 | 531.2 | 460 | 459.3 | 376.1 | 340.9 | 431.5
2064 | 1889 | 523.2 | 509.7 | 531.8 | 460.2 | 459.4 | 376.2 | 340.9 | 431.5
2065 | 1890 | 523.1 | 509.9 | 532.4 | 460.4 | 459.6 | 376.3 | 340.9 | 431.5
2066 | 1891 | 522.8 | 510.1 | 532.8 | 460.5 | 459.7 | 376.2 | 340.9 | 431.6
2067 | 1892 | 522.4 | 510.3 | 533.3 | 460.6 | 459.9 | 376.3 | 341 | 431.7
2068 | 1893 | 522.1 | 510.6 | 533.7 | 460.7 | 460 | 376.4 | 341 | 431.7
2069 | 1894 | 521.9 | 510.9 | 534 | 460.9 | 460.1 | 376.4 | 340.9 | 431.7
2070 | 1895 | 521.7 | 511.2 | 534.4 | 461 | 460.3 | 376.4 | 340.9 | 431.7
2071 | 1896 | 521.6 | 511.4 | 534.8 | 461.1 | 460.3 | 376.4 | 340.8 | 431.8
2072 | 1897 | 521.5 | 511.8 | 535.1 | 461.2 | 460.4 | 376.4 | 340.8 | 431.8
2073 | 1898 | 521.6 | 512.1 | 535.4 | 461.2 | 460.4 | 376.2 | 340.7 | 431.7
2074 | 1899 | 521.8 | 512.5 | 535.8 | 461.3 | 460.4 | 376.2 | 340.7 | 431.7
2075 | 1900 | 522 | 512.9 | 536.1 | 461.4 | 460.4 | 376.1 | 340.8 | 431.7
2076 | 1901 | 521.9 | 513.2 | 536.4 | 461.5 | 460.4 | 375.9 | 340.7 | 431.7
2077 | 1902 | 522.1 | 513.6 | 536.8 | 461.5 | 460.3 | 375.9 | 340.7 | 431.7
2078 | 1903 | 522.1 | 514 | 537.1 | 461.6 | 460.3 | 375.9 | 340.6 | 431.6
2079 | 1904 | 522.3 | 514.3 | 537.4 | 461.6 | 460.3 | 375.9 | 340.6 | 431.6
2080 | 1905 | 522.2 | 514.6 | 537.6 | 461.6 | 460.3 | 375.8 | 340.6 | 431.7
2081 | 1906 | 522.1 | 514.9 | 537.9 | 461.7 | 460.2 | 375.8 | 340.6 | 431.7
2082 | 1907 | 522.3 | 515.3 | 538.2 | 461.8 | 460.2 | 375.8 | 340.5 | 431.6
2083 | 1908 | 522.4 | 515.6 | 538.5 | 461.8 | 460.1 | 375.7 | 340.5 | 431.5
2084 | 1909 | 522.6 | 516 | 538.8 | 461.8 | 460 | 375.7 | 340.4 | 431.5
2085 | 1910 | 522.7 | 516.3 | 539.1 | 461.8 | 459.9 | 375.7 | 340.3 | 431.6
2086 | 1911 | 522.7 | 516.6 | 539.4 | 461.9 | 459.8 | 375.7 | 340.2 | 431.6
2087 | 1912 | 522.8 | 516.8 | 539.7 | 462 | 459.7 | 375.7 | 340.2 | 431.6
2088 | 1913 | 523 | 517 | 540 | 462 | 459.7 | 375.7 | 340.2 | 431.5
2089 | 1914 | 523.1 | 517.2 | 540.4 | 462 | 459.6 | 375.7 | 340.2 | 431.5
2090 | 1915 | 523.3 | 517.5 | 540.7 | 462.1 | 459.6 | 375.7 | 340.3 | 431.4
2091 | 1916 | 523.4 | 517.7 | 541 | 462.1 | 459.5 | 375.6 | 340.4 | 431.4
2092 | 1917 | 523.5 | 517.9 | 541.3 | 462.2 | 459.5 | 375.6 | 340.3 | 431.4
2093 | 1918 | 523.5 | 518.1 | 541.6 | 462.2 | 459.6 | 375.6 | 340.3 | 431.5
2094 | 1919 | 523.6 | 518.3 | 541.9 | 462.3 | 459.7 | 375.6 | 340.3 | 431.5
2095 | 1920 | 523.8 | 518.6 | 542.1 | 462.4 | 459.8 | 375.5 | 340.2 | 431.6
2096 | 1921 | 523.6 | 518.9 | 542.4 | 462.4 | 459.9 | 375.6 | 340.2 | 431.6
2097 | 1922 | 523.6 | 519.2 | 542.6 | 462.4 | 459.9 | 375.7 | 340.1 | 431.6
2098 | 1923 | 523.8 | 519.5 | 542.8 | 462.5 | 460 | 375.9 | 340 | 431.5
2099 | 1924 | 523.8 | 519.7 | 543.1 | 462.5 | 460.1 | 376 | 340 | 431.6
2100 | 1925 | 524 | 520 | 543.4 | 462.6 | 460.2 | 376 | 340 | 431.6
2101 | 1926 | 523.9 | 520.2 | 543.6 | 462.7 | 460.3 | 376 | 339.9 | 431.7
2102 | 1927 | 523.8 | 520.3 | 543.9 | 462.8 | 460.5 | 376 | 339.9 | 431.8
2103 | 1928 | 523.8 | 520.5 | 544.2 | 463 | 460.6 | 375.9 | 340 | 431.9
2104 | 1929 | 523.7 | 520.7 | 544.3 | 463.1 | 460.9 | 375.9 | 339.9 | 431.9
2105 | 1930 | 523.5 | 520.9 | 544.6 | 463.2 | 461.1 | 375.8 | 339.9 | 432
2106 | 1931 | 523.4 | 521.1 | 544.8 | 463.3 | 461.3 | 375.8 | 339.9 | 432
2107 | 1932 | 523.3 | 521.4 | 545.1 | 463.4 | 461.6 | 375.8 | 339.9 | 432.1
2108 | 1933 | 523 | 521.6 | 545.4 | 463.6 | 461.8 | 375.7 | 340.1 | 432.2
2109 | 1934 | 522.8 | 521.9 | 545.6 | 463.8 | 462 | 375.7 | 340.1 | 432.2
2110 | 1935 | 522.9 | 522.2 | 545.9 | 464 | 462.2 | 375.8 | 340.1 | 432.3
2111 | 1936 | 522.9 | 522.6 | 546.1 | 464.1 | 462.3 | 375.9 | 340.1 | 432.3
2112 | 1937 | 522.8 | 522.9 | 546.3 | 464.2 | 462.4 | 375.9 | 340.1 | 432.4
2113 | 1938 | 522.5 | 523.2 | 546.5 | 464.4 | 462.5 | 375.9 | 340.1 | 432.4
2114 | 1939 | 522.3 | 523.5 | 546.7 | 464.5 | 462.5 | 375.9 | 340.1 | 432.5
2115 | 1940 | 522 | 523.8 | 546.9 | 464.7 | 462.6 | 376 | 340.1 | 432.6
2116 | 1941 | 521.7 | 524 | 547.1 | 464.7 | 462.6 | 376 | 340.2 | 432.6
2117 | 1942 | 521.5 | 524.3 | 547.2 | 464.9 | 462.7 | 376 | 340.1 | 432.5
2118 | 1943 | 521.5 | 524.5 | 547.4 | 465 | 462.7 | 375.8 | 340.1 | 432.5
2119 | 1944 | 521.5 | 524.7 | 547.6 | 465.1 | 462.7 | 375.8 | 340.2 | 432.6
2120 | 1945 | 521.7 | 525 | 547.8 | 465.2 | 462.8 | 375.7 | 340.2 | 432.6
2121 | 1946 | 522.1 | 525.2 | 548 | 465.4 | 462.8 | 375.6 | 340.2 | 432.6
2122 | 1947 | 522.3 | 525.3 | 548.1 | 465.5 | 462.8 | 375.5 | 340.3 | 432.6
2123 | 1948 | 522.4 | 525.4 | 548.2 | 465.6 | 462.9 | 375.5 | 340.3 | 432.5
2124 | 1949 | 522.5 | 525.6 | 548.4 | 465.7 | 463 | 375.5 | 340.4 | 432.5
2125 | 1950 | 522.7 | 525.7 | 548.5 | 465.8 | 463.1 | 375.4 | 340.4 | 432.6
2126 | 1951 | 522.9 | 525.8 | 548.6 | 465.9 | 463.3 | 375.4 | 340.5 | 432.6
2127 | 1952 | 522.9 | 525.9 | 548.8 | 466 | 463.4 | 375.5 | 340.5 | 432.6
2128 | 1953 | 522.9 | 526 | 548.9 | 466.1 | 463.5 | 375.6 | 340.4 | 432.7
2129 | 1954 | 523 | 526.2 | 549.1 | 466.2 | 463.6 | 375.6 | 340.5 | 432.8
2130 | 1955 | 523.2 | 526.4 | 549.2 | 466.3 | 463.7 | 375.6 | 340.4 | 432.7
2131 | 1956 | 523.4 | 526.6 | 549.5 | 466.3 | 463.8 | 375.7 | 340.4 | 432.6
2132 | 1957 | 523.8 | 526.9 | 549.7 | 466.4 | 463.8 | 375.7 | 340.3 | 432.7
2133 | 1958 | 523.8 | 527.2 | 549.8 | 466.5 | 463.9 | 375.8 | 340.3 | 432.7
2134 | 1959 | 523.7 | 527.6 | 550 | 466.5 | 463.9 | 375.8 | 340.3 | 432.6
2135 | 1960 | 523.5 | 527.9 | 550.2 | 466.5 | 463.8 | 375.7 | 340.2 | 432.6
2136 | 1961 | 523.2 | 528.1 | 550.3 | 466.5 | 463.8 | 375.6 | 340.2 | 432.6
2137 | 1962 | 523.2 | 528.4 | 550.5 | 466.5 | 463.9 | 375.7 | 340.2 | 432.6
2138 | 1963 | 523.2 | 528.5 | 550.6 | 466.5 | 464 | 375.6 | 340.2 | 432.8
2139 | 1964 | 523.2 | 528.7 | 550.8 | 466.5 | 464.1 | 375.6 | 340.1 | 432.9
2140 | 1965 | 523.3 | 528.8 | 550.9 | 466.5 | 464.2 | 375.7 | 340.1 | 433
2141 | 1966 | 523.3 | 529 | 551.1 | 466.6 | 464.4 | 375.8 | 340 | 433
2142 | 1967 | 523.2 | 529.1 | 551.4 | 466.6 | 464.5 | 375.9 | 339.9 | 433
2143 | 1968 | 523.3 | 529.4 | 551.6 | 466.6 | 464.6 | 376 | 339.9 | 433.1
2144 | 1969 | 523.4 | 529.6 | 551.6 | 466.6 | 464.6 | 376 | 339.9 | 433.1
2145 | 1970 | 523.4 | 529.8 | 551.8 | 466.6 | 464.6 | 376 | 340 | 433.1
2146 | 1971 | 523.5 | 530.1 | 552 | 466.5 | 464.6 | 375.9 | 340 | 433.1
2147 | 1972 | 523.6 | 530.3 | 552.2 | 466.6 | 464.6 | 375.7 | 340.1 | 433.3
2148 | 1973 | 523.6 | 530.5 | 552.4 | 466.6 | 464.5 | 375.6 | 340.2 | 433.3
2149 | 1974 | 523.5 | 530.7 | 552.6 | 466.6 | 464.5 | 375.5 | 340.2 | 433.3
2150 | 1975 | 523.5 | 530.9 | 552.7 | 466.6 | 464.6 | 375.3 | 340.3 | 433.2
2151 | 1976 | 523.6 | 531.1 | 552.8 | 466.6 | 464.7 | 375.2 | 340.4 | 433.3
2152 | 1977 | 523.7 | 531.4 | 552.8 | 466.6 | 464.7 | 375.2 | 340.6 | 433.3
2153 | 1978 | 523.8 | 531.6 | 553 | 466.6 | 464.8 | 375.2 | 340.7 | 433.3
2154 | 1979 | 523.7 | 531.8 | 553.2 | 466.6 | 464.9 | 375.4 | 340.7 | 433.4
2155 | 1980 | 523.6 | 532 | 553.4 | 466.6 | 465 | 375.5 | 340.7 | 433.5
2156 | 1981 | 523.8 | 532.3 | 553.5 | 466.5 | 465.1 | 375.5 | 340.9 | 433.4
2157 | 1982 | 523.9 | 532.5 | 553.7 | 466.6 | 465.1 | 375.5 | 340.9 | 433.4
2158 | 1983 | 524 | 532.7 | 553.8 | 466.6 | 465.1 | 375.6 | 340.9 | 433.4
2159 | 1984 | 523.9 | 532.9 | 553.9 | 466.8 | 465 | 375.7 | 341 | 433.4
2160 | 1985 | 523.8 | 533.1 | 554 | 466.8 | 465 | 375.8 | 341 | 433.4
2161 | 1986 | 523.9 | 533.2 | 554 | 466.8 | 465 | 375.9 | 341 | 433.4
2162 | 1987 | 523.8 | 533.4 | 554.1 | 466.8 | 465 | 375.9 | 341 | 433.4
2163 | 1988 | 523.8 | 533.5 | 554.2 | 466.9 | 465 | 375.9 | 341 | 433.3
2164 | 1989 | 523.8 | 533.6 | 554.2 | 467 | 464.9 | 375.9 | 341 | 433.4
2165 | 1990 | 523.8 | 533.8 | 554.3 | 467 | 464.9 | 375.9 | 341.1 | 433.3
2166 | 1991 | 523.8 | 534 | 554.3 | 467.1 | 464.9 | 376 | 341.1 | 433.3
2167 | 1992 | 523.8 | 534.1 | 554.4 | 467.2 | 464.9 | 376 | 341.1 | 433.3
2168 | 1993 | 524 | 534.3 | 554.5 | 467.2 | 464.9 | 376 | 341.1 | 433.3
2169 | 1994 | 524 | 534.4 | 554.7 | 467.1 | 464.8 | 376.1 | 341.1 | 433.1
2170 | 1995 | 523.9 | 534.6 | 554.7 | 467.2 | 464.8 | 376.2 | 341.2 | 433.2
2171 | 1996 | 523.9 | 534.8 | 554.8 | 467.2 | 464.9 | 376.2 | 341.3 | 433.3
2172 | 1997 | 523.9 | 534.9 | 554.9 | 467.2 | 464.9 | 376.2 | 341.4 | 433.3
2173 | 1998 | 523.7 | 535.1 | 555 | 467.3 | 465 | 376.3 | 341.4 | 433.3
2174 | 1999 | 523.5 | 535.3 | 555.1 | 467.3 | 465.2 | 376.4 | 341.4 | 433.4
2175 | 2000 | 523.5 | 535.5 | 555.3 | 467.3 | 465.3 | 376.3 | 341.5 | 433.4
2176 | 2001 | 523.4 | 535.8 | 555.5 | 467.4 | 465.4 | 376.2 | 341.6 | 433.4
2177 | 2002 | 523.3 | 536.1 | 555.7 | 467.6 | 465.5 | 376.2 | 341.5 | 433.5
2178 | 2003 | 523.1 | 536.4 | 555.8 | 467.6 | 465.7 | 376.2 | 341.5 | 433.5
2179 | 2004 | 523 | 536.6 | 556 | 467.5 | 465.8 | 376.1 | 341.6 | 433.6
2180 | 2005 | 522.9 | 536.8 | 556.1 | 467.6 | 466 | 375.9 | 341.7 | 433.5
2181 | 2006 | 522.8 | 537 | 556.2 | 467.4 | 466.1 | 375.9 | 341.7 | 433.6
2182 | 2007 | 522.8 | 537.1 | 556.3 | 467.4 | 466.3 | 375.9 | 341.8 | 433.5
2183 | 2008 | 522.7 | 537.3 | 556.4 | 467.7 | 466.5 | 375.9 | 341.8 | 433.6
2184 | 2009 | 522.5 | 537.4 | 556.5 | 467.8 | 466.7 | 376 | 341.8 | 433.6
2185 | 2010 | 522.3 | 537.6 | 556.6 | 467.7 | 466.8 | 376.1 | 341.7 | 433.7
2186 | 2011 | 522.2 | 537.7 | 556.6 | 467.7 | 466.9 | 376.3 | 341.7 | 433.7
2187 | 2012 | 522.4 | 537.7 | 556.6 | 467.9 | 467 | 376.4 | 341.7 | 433.7
2188 | 2013 | 522.2 | 537.8 | 556.6 | 468 | 467 | 376.5 | 341.7 | 433.8
2189 | 2014 | 522.2 | 537.8 | 556.6 | 468.1 | 467 | 376.6 | 341.7 | 433.8
2190 | 2015 | 522.2 | 538 | 556.5 | 468.1 | 467 | 376.6 | 341.6 | 433.9
2191 | 2016 | 522.4 | 538.1 | 556.5 | 468.3 | 467 | 376.5 | 341.7 | 433.9
2192 | 2017 | 522.6 | 538.3 | 556.6 | 468.3 | 467 | 376.5 | 341.6 | 433.9
2193 | 2018 | 522.6 | 538.6 | 556.7 | 468.3 | 467.1 | 376.5 | 341.6 | 433.8
2194 | 2019 | 522.6 | 538.8 | 556.8 | 468.4 | 467.2 | 376.5 | 341.6 | 433.9
2195 | 2020 | 522.4 | 539.1 | 556.8 | 468.5 | 467.3 | 376.6 | 341.5 | 434
2196 | 2021 | 522.4 | 539.3 | 556.8 | 468.6 | 467.5 | 376.7 | 341.5 | 434
2197 | 2022 | 522.3 | 539.5 | 556.8 | 468.8 | 467.7 | 376.7 | 341.4 | 434.1
2198 | 2023 | 522.2 | 539.7 | 556.7 | 468.9 | 467.9 | 376.6 | 341.4 | 434.1
2199 | 2024 | 522.1 | 539.8 | 556.6 | 468.9 | 468 | 376.5 | 341.3 | 434.1
2200 | 2025 | 522 | 540 | 556.6 | 468.9 | 468.2 | 376.3 | 341.4 | 434
2201 | 2026 | 522 | 540.2 | 556.6 | 469 | 468.3 | 376.3 | 341.3 | 434
2202 | 2027 | 522 | 540.3 | 556.6 | 469 | 468.4 | 376.3 | 341.4 | 434.1
2203 | 2028 | 522 | 540.6 | 556.7 | 469.1 | 468.6 | 376.4 | 341.4 | 434.2
2204 | 2029 | 522.2 | 541 | 557 | 469 | 468.8 | 376.4 | 341.4 | 434.3
2205 | 2030 | 522.3 | 541.3 | 557.2 | 469.1 | 469 | 376.4 | 341.4 | 434.3
2206 | 2031 | 522.5 | 541.6 | 557.5 | 469.1 | 469.2 | 376.5 | 341.5 | 434.4
2207 | 2032 | 522.8 | 541.8 | 557.7 | 469.2 | 469.4 | 376.6 | 341.5 | 434.5
2208 | 2033 | 523.1 | 542.1 | 557.9 | 469.3 | 469.6 | 376.7 | 341.5 | 434.6
2209 | 2034 | 523.3 | 542.3 | 558 | 469.4 | 469.8 | 376.7 | 341.5 | 434.6
2210 | 2035 | 523.5 | 542.6 | 558.1 | 469.4 | 470 | 376.8 | 341.6 | 434.8
2211 | 2036 | 523.7 | 542.9 | 558.2 | 468.2 | 470.2 | 376.9 | 341.6 | 434.8
2212 | 2037 | 523.6 | 543.1 | 558.2 | 467 | 470.3 | 376.9 | 341.6 | 434.8
2213 | 2038 | 523.5 | 543.4 | 558.3 | 466.4 | 470.5 | 377 | 341.5 | 434.8
2214 | 2039 | 523.6 | 543.6 | 558.4 | 466.1 | 470.7 | 377.1 | 341.5 | 434.8
2215 | 2040 | 523.6 | 543.8 | 558.5 | 465.8 | 470.9 | 377.1 | 341.4 | 434.9
2216 | 2041 | 523.6 | 544 | 558.6 | 465.7 | 471 | 377 | 341.4 | 434.9
2217 | 2042 | 523.4 | 544.1 | 558.8 | 465.6 | 471.2 | 377.1 | 341.4 | 435.1
2218 | 2043 | 523.4 | 544.3 | 559 | 465.6 | 471.4 | 377.2 | 341.4 | 435.1
2219 | 2044 | 523.2 | 544.4 | 559.1 | 465.7 | 471.6 | 377.2 | 341.3 | 435.1
2220 | 2045 | 523 | 544.6 | 559.1 | 465.7 | 471.8 | 377.2 | 341.3 | 435.1
2221 | 2046 | 522.8 | 544.8 | 559.1 | 465.7 | 471.9 | 377.1 | 341.2 | 435.2
2222 | 2047 | 522.8 | 545 | 559 | 465.8 | 472.1 | 377 | 341.1 | 435.2
2223 | 2048 | 522.7 | 545.2 | 558.9 | 465.9 | 472.3 | 377 | 341 | 435.2
2224 | 2049 | 522.6 | 545.5 | 558.9 | 466 | 472.4 | 377 | 341.1 | 435.2
2225 | 2050 | 522.7 | 545.7 | 558.9 | 466 | 472.5 | 377 | 341.1 | 435.3
2226 | 2051 | 522.8 | 546 | 558.9 | 466 | 472.6 | 377 | 341.1 | 435.3
2227 | 2052 | 522.9 | 546.2 | 558.9 | 466.1 | 472.6 | 377 | 341.1 | 435.3
2228 | 2053 | 522.9 | 546.4 | 559 | 466.2 | 472.7 | 377 | 341.1 | 435.4
2229 | 2054 | 522.7 | 546.6 | 559 | 466.2 | 472.8 | 377.1 | 341.1 | 435.5
2230 | 2055 | 522.5 | 546.8 | 559.1 | 466.3 | 473 | 377.1 | 341.1 | 435.5
2231 | 2056 | 522.2 | 547 | 559.2 | 466.3 | 473.1 | 377.2 | 341 | 435.6
2232 | 2057 | 522 | 547.2 | 559.4 | 466.4 | 473.4 | 377.3 | 341 | 435.7
2233 | 2058 | 522.2 | 547.4 | 559.4 | 466.5 | 473.6 | 377.3 | 341 | 435.7
2234 | 2059 | 522.2 | 547.6 | 559.4 | 466.6 | 473.9 | 377.4 | 341.1 | 435.8
2235 | 2060 | 522.2 | 547.8 | 559.2 | 466.7 | 474.2 | 377.4 | 341 | 435.8
2236 | 2061 | 522.2 | 548 | 559.1 | 466.9 | 474.5 | 377.4 | 341 | 435.9
2237 | 2062 | 522.4 | 548.1 | 558.9 | 467 | 474.8 | 377.4 | 341 | 435.9
2238 | 2063 | 522.3 | 548.1 | 558.7 | 467.2 | 475.1 | 377.3 | 341 | 436
2239 | 2064 | 522.1 | 548.1 | 558.6 | 467.3 | 475.3 | 377.2 | 341 | 436
2240 | 2065 | 522 | 548.2 | 558.4 | 467.5 | 475.6 | 377.2 | 340.9 | 436
2241 | 2066 | 522 | 548.2 | 558.3 | 467.6 | 475.9 | 377.1 | 341 | 436.1
2242 | 2067 | 522.1 | 548.4 | 558.3 | 467.7 | 476.1 | 377 | 341 | 436.2
2243 | 2068 | 522.2 | 548.5 | 558.3 | 467.8 | 476.3 | 377 | 341 | 436.2
2244 | 2069 | 522.2 | 548.7 | 558.2 | 467.9 | 476.5 | 377 | 341 | 436.3
2245 | 2070 | 522.3 | 548.7 | 558.3 | 468 | 476.6 | 377 | 340.8 | 436.3
2246 | 2071 | 522.4 | 548.8 | 558.4 | 468 | 476.8 | 377.1 | 340.8 | 436.3
2247 | 2072 | 522.4 | 548.9 | 558.4 | 468.1 | 476.9 | 377.1 | 340.9 | 436.4
2248 | 2073 | 522.3 | 549 | 558.4 | 468.1 | 476.9 | 377.2 | 340.8 | 436.5
2249 | 2074 | 522.3 | 549.1 | 558.3 | 468.2 | 477 | 377.1 | 340.7 | 436.5
2250 | 2075 | 522.3 | 549.2 | 558.3 | 468.3 | 477.2 | 377.2 | 340.7 | 436.6
2251 | 2076 | 522.4 | 549.3 | 558.3 | 468.3 | 477.4 | 377.3 | 340.6 | 436.7
2252 | 2077 | 522.3 | 549.4 | 558.3 | 468.4 | 477.5 | 377.5 | 340.4 | 436.8
2253 | 2078 | 522.3 | 549.5 | 558.3 | 468.5 | 477.8 | 377.7 | 340.4 | 436.8
2254 | 2079 | 522.4 | 549.6 | 558.4 | 468.6 | 478 | 377.8 | 340.3 | 436.8
2255 | 2080 | 522.3 | 549.6 | 558.4 | 468.7 | 478.2 | 377.9 | 340.3 | 436.8
2256 | 2081 | 522.1 | 549.7 | 558.4 | 468.8 | 478.4 | 378 | 340.2 | 436.8
2257 | 2082 | 522 | 549.7 | 558.4 | 469 | 478.6 | 378.1 | 340.2 | 436.9
2258 | 2083 | 522 | 549.8 | 558.3 | 469.1 | 478.8 | 378.1 | 340.3 | 437
2259 | 2084 | 521.9 | 549.9 | 558.1 | 469.3 | 479 | 378.1 | 340.4 | 437.1
2260 | 2085 | 521.8 | 550 | 557.9 | 469.4 | 479.2 | 378.1 | 340.3 | 437
2261 | 2086 | 521.7 | 550.1 | 557.7 | 469.6 | 479.3 | 378.1 | 340.3 | 437
2262 | 2087 | 521.4 | 550.2 | 557.5 | 469.8 | 479.5 | 378.1 | 340.2 | 436.9
2263 | 2088 | 521.2 | 550.3 | 557.2 | 469.9 | 479.7 | 378.2 | 340.1 | 437
2264 | 2089 | 521.4 | 550.3 | 557 | 470.1 | 479.8 | 378.2 | 340 | 437
2265 | 2090 | 521.5 | 550.4 | 556.9 | 470.2 | 480 | 378 | 339.9 | 437
2266 | 2091 | 521.4 | 550.5 | 556.9 | 470.4 | 480.2 | 377.9 | 339.8 | 437
2267 | 2092 | 521.3 | 550.5 | 556.9 | 470.6 | 480.4 | 377.9 | 339.8 | 437
2268 | 2093 | 521.3 | 550.5 | 556.8 | 470.7 | 480.6 | 377.9 | 339.6 | 437
2269 | 2094 | 521.3 | 550.6 | 556.8 | 470.9 | 480.8 | 377.9 | 339.6 | 437.1
2270 | 2095 | 521.3 | 550.7 | 556.6 | 471.1 | 481 | 377.8 | 339.6 | 437.2
2271 | 2096 | 521.4 | 550.9 | 556.5 | 471.3 | 481.2 | 377.7 | 339.6 | 437.3
2272 | 2097 | 521.4 | 551.1 | 556.4 | 471.4 | 481.4 | 377.7 | 339.5 | 437.3
2273 | 2098 | 521.7 | 551.2 | 556.2 | 471.6 | 481.5 | 377.8 | 339.4 | 437.4
2274 | 2099 | 521.7 | 551.3 | 556 | 471.8 | 481.7 | 377.9 | 339.4 | 437.5
2275 | 2100 | 521.7 | 551.4 | 555.8 | 471.9 | 481.9 | 378 | 339.3 | 437.6
2276 | 2101 | 521.6 | 551.5 | 555.7 | 472.1 | 482.1 | 378.2 | 339.2 | 437.7
2277 | 2102 | 521.5 | 551.5 | 555.6 | 472.2 | 482.3 | 378.4 | 339.2 | 437.8
2278 | 2103 | 521.5 | 551.6 | 555.5 | 472.3 | 482.5 | 378.5 | 339.1 | 437.8
2279 | 2104 | 521.5 | 551.7 | 555.4 | 472.4 | 482.7 | 378.6 | 339.2 | 437.8
2280 | 2105 | 521.4 | 551.8 | 555.4 | 472.5 | 482.9 | 378.7 | 339.2 | 437.8
2281 | 2106 | 521.4 | 551.9 | 555.3 | 472.7 | 483 | 378.8 | 339.1 | 437.8
2282 | 2107 | 521.6 | 551.9 | 555.1 | 472.8 | 483.2 | 378.8 | 339.2 | 437.8
2283 | 2108 | 521.7 | 552 | 555 | 472.9 | 483.4 | 378.8 | 339.1 | 437.9
2284 | 2109 | 521.6 | 552 | 554.8 | 473 | 483.6 | 378.8 | 338.9 | 438
2285 | 2110 | 521.4 | 552.1 | 554.6 | 473.2 | 483.9 | 378.9 | 338.8 | 438
2286 | 2111 | 521.3 | 552.2 | 554.4 | 473.3 | 484.1 | 378.9 | 338.8 | 438
2287 | 2112 | 521.2 | 552.3 | 554.1 | 473.4 | 484.2 | 378.9 | 338.8 | 438
2288 | 2113 | 521.1 | 552.4 | 554 | 473.5 | 484.4 | 379 | 338.8 | 438
2289 | 2114 | 521.1 | 552.5 | 553.9 | 473.6 | 484.5 | 379.2 | 338.8 | 438.1
2290 | 2115 | 521 | 552.6 | 553.7 | 473.7 | 484.7 | 379.4 | 338.9 | 438.2
2291 | 2116 | 520.9 | 552.7 | 553.5 | 473.8 | 484.8 | 379.6 | 339 | 438.2
2292 | 2117 | 520.8 | 552.8 | 553.4 | 473.8 | 484.9 | 379.7 | 339 | 438.2
2293 | 2118 | 520.8 | 552.8 | 553.3 | 473.9 | 485 | 379.7 | 339.1 | 438.3
2294 | 2119 | 521 | 552.8 | 553.3 | 474 | 485.2 | 379.7 | 339.2 | 438.3
2295 | 2120 | 521.2 | 552.9 | 553.3 | 474 | 485.3 | 379.8 | 339.3 | 438.4
2296 | 2121 | 521.2 | 553.1 | 553.4 | 474.1 | 485.4 | 379.7 | 339.3 | 438.4
2297 | 2122 | 521.4 | 553.2 | 553.4 | 474.2 | 485.6 | 379.7 | 339.5 | 438.5
2298 | 2123 | 521.4 | 553.4 | 553.3 | 474.3 | 485.8 | 379.7 | 339.6 | 438.6
2299 | 2124 | 521.3 | 553.6 | 553.1 | 474.5 | 486 | 379.7 | 339.7 | 438.7
2300 | 2125 | 521.4 | 553.8 | 553 | 474.6 | 486.2 | 379.7 | 339.9 | 438.7
2301 | 2126 | 521.5 | 553.9 | 552.8 | 474.8 | 486.3 | 379.6 | 340.1 | 438.7
2302 | 2127 | 521.8 | 554.1 | 552.6 | 474.9 | 486.4 | 379.5 | 340.1 | 438.7
2303 | 2128 | 522.1 | 554.1 | 552.3 | 475.1 | 486.5 | 379.5 | 340.2 | 438.8
2304 | 2129 | 522.3 | 554.2 | 552.1 | 475.2 | 486.7 | 379.5 | 340.2 | 438.9
2305 | 2130 | 522.6 | 554.3 | 551.9 | 475.3 | 486.8 | 379.5 | 340.3 | 438.9
2306 | 2131 | 523 | 554.4 | 551.7 | 475.5 | 486.9 | 379.4 | 340.4 | 439
2307 | 2132 | 523.3 | 554.5 | 551.6 | 475.6 | 487.1 | 379.3 | 340.5 | 439.1
2308 | 2133 | 523.5 | 554.6 | 551.5 | 475.7 | 487.2 | 379.2 | 340.5 | 439.1
2309 | 2134 | 523.7 | 554.7 | 551.4 | 475.8 | 487.3 | 379.2 | 340.6 | 439.2
2310 | 2135 | 523.9 | 554.8 | 551.3 | 475.8 | 487.5 | 379.2 | 340.7 | 439.3
2311 | 2136 | 523.9 | 554.9 | 551.2 | 475.9 | 487.6 | 379.1 | 340.7 | 439.4
2312 | 2137 | 523.7 | 555.1 | 551.1 | 476 | 487.7 | 379 | 340.8 | 439.5
2313 | 2138 | 523.6 | 555.2 | 550.9 | 476.1 | 487.8 | 379 | 340.8 | 439.6
2314 | 2139 | 523.6 | 555.4 | 550.8 | 476.1 | 487.9 | 379 | 340.9 | 439.5
2315 | 2140 | 523.7 | 555.5 | 550.8 | 476.2 | 487.9 | 379 | 340.9 | 439.6
2316 | 2141 | 523.7 | 555.6 | 550.8 | 476.2 | 487.9 | 379.1 | 340.9 | 439.6
2317 | 2142 | 523.6 | 555.7 | 550.8 | 476.2 | 487.9 | 379.2 | 341 | 439.7
2318 | 2143 | 523.6 | 555.8 | 550.8 | 476.2 | 487.9 | 379.4 | 341.1 | 439.6
2319 | 2144 | 523.6 | 556 | 550.9 | 476.2 | 487.8 | 379.5 | 341 | 439.6
2320 | 2145 | 523.6 | 556.2 | 550.9 | 476.2 | 487.7 | 379.6 | 341 | 439.5
2321 | 2146 | 523.6 | 556.4 | 550.7 | 476.2 | 487.7 | 379.5 | 341 | 439.5
2322 | 2147 | 523.6 | 556.6 | 550.6 | 476.2 | 487.6 | 379.3 | 341 | 439.5
2323 | 2148 | 523.7 | 556.8 | 550.5 | 476.2 | 487.5 | 379 | 341 | 439.6
2324 | 2149 | 523.5 | 557 | 550.4 | 476.2 | 487.4 | 378.7 | 341 | 439.5
2325 | 2150 | 523.2 | 557.2 | 550.3 | 476.1 | 487.3 | 378.5 | 341 | 439.4
2326 | 2151 | 522.9 | 557.4 | 550.2 | 476.1 | 487.1 | 378.5 | 341 | 439.4
2327 | 2152 | 522.9 | 557.6 | 550 | 476 | 487 | 378.4 | 341 | 439.3
2328 | 2153 | 522.6 | 557.8 | 549.9 | 476 | 486.9 | 378.4 | 341 | 439.3
2329 | 2154 | 522.5 | 558 | 549.8 | 475.9 | 486.7 | 378.4 | 340.9 | 439.2
2330 | 2155 | 522.5 | 558.1 | 549.7 | 475.8 | 486.6 | 378.4 | 340.9 | 439
2331 | 2156 | 522.6 | 558.2 | 549.6 | 475.8 | 486.4 | 378.5 | 340.9 | 438.9
2332 | 2157 | 522.5 | 558.3 | 549.3 | 475.8 | 486.3 | 378.5 | 340.9 | 438.9
2333 | 2158 | 522.6 | 558.5 | 549.2 | 475.7 | 486.2 | 378.6 | 340.9 | 438.9
2334 | 2159 | 522.5 | 558.6 | 549.1 | 475.7 | 486 | 378.8 | 341 | 438.8
2335 | 2160 | 522.3 | 558.8 | 549 | 475.7 | 485.9 | 378.9 | 341 | 438.8
2336 | 2161 | 522.1 | 558.9 | 548.9 | 475.6 | 485.9 | 378.9 | 341.1 | 438.8
2337 | 2162 | 522 | 559 | 548.9 | 475.6 | 485.9 | 378.9 | 341 | 438.8
2338 | 2163 | 521.9 | 559.1 | 548.8 | 475.6 | 486 | 378.9 | 340.9 | 438.9
2339 | 2164 | 522 | 559.2 | 548.7 | 475.7 | 486.2 | 379.1 | 340.9 | 438.9
2340 | 2165 | 522.1 | 559.3 | 548.5 | 475.8 | 486.5 | 379 | 340.9 | 439
2341 | 2166 | 522.1 | 559.3 | 548.3 | 475.9 | 486.7 | 379 | 340.9 | 439
2342 | 2167 | 522.1 | 559.3 | 548.1 | 476.1 | 487 | 378.9 | 340.9 | 438.9
2343 | 2168 | 522.1 | 559.4 | 547.8 | 476.2 | 487.2 | 378.6 | 340.9 | 439
2344 | 2169 | 521.9 | 559.6 | 547.6 | 476.4 | 487.4 | 378.4 | 340.9 | 439.1
2345 | 2170 | 521.9 | 559.8 | 547.3 | 476.5 | 487.6 | 378.3 | 340.9 | 439.1
2346 | 2171 | 521.9 | 559.9 | 547 | 476.7 | 487.7 | 378.2 | 340.9 | 439.1
2347 | 2172 | 521.9 | 560 | 546.8 | 476.8 | 487.8 | 378.2 | 340.9 | 439.1
2348 | 2173 | 521.9 | 560.1 | 546.7 | 476.9 | 487.9 | 378.1 | 341 | 439.1
2349 | 2174 | 522 | 560.2 | 546.6 | 476.9 | 487.9 | 378.2 | 341 | 439.1
2350 | 2175 | 522.2 | 560.4 | 546.4 | 477 | 487.9 | 378.2 | 341.1 | 439
2351 | 2176 | 522.2 | 560.5 | 546.2 | 477.1 | 488 | 378.2 | 341.1 | 438.9
2352 | 2177 | 522.3 | 560.5 | 545.9 | 477.2 | 488 | 378.2 | 341.1 | 438.9
2353 | 2178 | 522.4 | 560.5 | 545.7 | 477.2 | 488 | 378.3 | 341.2 | 438.9
2354 | 2179 | 522.5 | 560.3 | 545.5 | 477.3 | 487.9 | 378.3 | 341.2 | 438.8
2355 | 2180 | 522.7 | 560.2 | 545.4 | 477.3 | 487.9 | 378.4 | 341.2 | 438.8
2356 | 2181 | 522.9 | 560.1 | 545.3 | 477.4 | 487.9 | 378.4 | 341.2 | 438.8
2357 | 2182 | 523.2 | 560.1 | 545.2 | 477.4 | 487.9 | 378.5 | 341.4 | 438.7
2358 | 2183 | 523.4 | 560 | 545.1 | 477.5 | 487.9 | 378.5 | 341.4 | 438.8
2359 | 2184 | 523.7 | 560 | 544.9 | 477.6 | 488 | 378.6 | 341.5 | 438.8
2360 | 2185 | 523.8 | 559.9 | 544.8 | 477.7 | 488.2 | 378.7 | 341.6 | 438.8
2361 | 2186 | 523.8 | 559.9 | 544.6 | 477.8 | 488.4 | 378.8 | 341.6 | 438.9
2362 | 2187 | 524 | 559.9 | 544.5 | 477.9 | 488.7 | 378.9 | 341.7 | 439
2363 | 2188 | 524.2 | 560 | 544.4 | 478.1 | 488.9 | 379 | 341.8 | 439.1
2364 | 2189 | 524.3 | 560.1 | 544.2 | 478.3 | 489.2 | 379 | 341.8 | 439.2
2365 | 2190 | 524.2 | 560.3 | 544.2 | 478.4 | 489.3 | 379 | 341.9 | 439.4
2366 | 2191 | 524.1 | 560.4 | 544 | 478.6 | 489.5 | 379.1 | 341.9 | 439.4
2367 | 2192 | 523.9 | 560.5 | 543.9 | 478.7 | 489.7 | 379.2 | 342 | 439.5
2368 | 2193 | 523.7 | 560.6 | 543.8 | 478.8 | 489.9 | 379.3 | 342 | 439.4
2369 | 2194 | 523.7 | 560.6 | 543.6 | 479 | 490 | 379.4 | 342.1 | 439.4
2370 | 2195 | 523.5 | 560.7 | 543.5 | 479.1 | 490 | 379.4 | 342.2 | 439.3
2371 | 2196 | 523.4 | 560.8 | 543.4 | 479.2 | 490.1 | 379.4 | 342.2 | 439.3
2372 | 2197 | 523.4 | 560.8 | 543.3 | 479.3 | 490.2 | 379.4 | 342.3 | 439.4
2373 | 2198 | 523.2 | 560.8 | 543.2 | 479.5 | 490.3 | 379.4 | 342.3 | 439.5
2374 | 2199 | 523.2 | 560.9 | 543 | 479.6 | 490.5 | 379.5 | 342.3 | 439.5
2375 | 2200 | 523.3 | 560.9 | 542.9 | 479.7 | 490.8 | 379.5 | 342.3 | 439.6
2376 | 2201 | 523.4 | 561 | 542.8 | 479.9 | 491 | 379.5 | 342.4 | 439.6
2377 | 2202 | 523.5 | 561 | 542.7 | 480 | 491.2 | 379.4 | 342.3 | 439.6
2378 | 2203 | 523.6 | 561.2 | 542.5 | 480.2 | 491.4 | 379.4 | 342.4 | 439.6
2379 | 2204 | 523.8 | 561.2 | 542.5 | 480.3 | 491.6 | 379.4 | 342.5 | 439.7
2380 | 2205 | 523.8 | 561.3 | 542.4 | 480.4 | 491.8 | 379.3 | 342.5 | 439.7
2381 | 2206 | 523.6 | 561.3 | 542.3 | 480.5 | 492 | 379.3 | 342.5 | 439.8
2382 | 2207 | 523.5 | 561.4 | 542.2 | 480.7 | 492.3 | 379.2 | 342.5 | 439.9
2383 | 2208 | 523.6 | 561.4 | 542 | 480.9 | 492.7 | 379.1 | 342.5 | 440
2384 | 2209 | 523.7 | 561.5 | 542 | 481.1 | 492.9 | 379 | 342.5 | 440.1
2385 | 2210 | 523.9 | 561.7 | 541.9 | 481.3 | 493.2 | 378.9 | 342.6 | 440.1
2386 | 2211 | 524 | 561.9 | 541.8 | 481.5 | 493.4 | 378.9 | 342.6 | 440.1
2387 | 2212 | 524 | 562.2 | 541.7 | 481.7 | 493.6 | 378.8 | 342.7 | 440.1
2388 | 2213 | 523.9 | 562.4 | 541.6 | 481.9 | 493.8 | 378.9 | 342.7 | 440.1
2389 | 2214 | 523.7 | 562.6 | 541.4 | 482 | 493.9 | 378.9 | 342.7 | 440.1
2390 | 2215 | 523.6 | 562.8 | 541.3 | 482.2 | 494 | 378.9 | 342.8 | 440.1
2391 | 2216 | 523.4 | 562.9 | 541.2 | 482.3 | 494.1 | 379 | 342.8 | 440
2392 | 2217 | 523.2 | 563 | 541 | 482.4 | 494.1 | 379 | 342.7 | 440
2393 | 2218 | 522.9 | 563.1 | 540.8 | 482.5 | 494.1 | 379.1 | 342.6 | 440
2394 | 2219 | 522.7 | 563.1 | 540.7 | 482.6 | 494.2 | 379.2 | 342.5 | 440
2395 | 2220 | 522.6 | 563.1 | 540.6 | 482.7 | 494.3 | 379.2 | 342.6 | 440.1
2396 | 2221 | 522.4 | 563.2 | 540.5 | 482.8 | 494.4 | 379.1 | 342.5 | 440
2397 | 2222 | 522.1 | 563.3 | 540.4 | 483 | 494.5 | 378.9 | 342.5 | 439.9
2398 | 2223 | 521.9 | 563.3 | 540.4 | 483.1 | 494.7 | 378.8 | 342.5 | 439.9
2399 | 2224 | 521.7 | 563.4 | 540.3 | 483.3 | 494.9 | 378.7 | 342.4 | 439.9
2400 | 2225 | 521.5 | 563.5 | 540.2 | 483.4 | 495.1 | 378.6 | 342.4 | 440
2401 | 2226 | 521.5 | 563.6 | 540 | 483.6 | 495.3 | 378.6 | 342.3 | 440.2
2402 | 2227 | 521.6 | 563.7 | 539.9 | 483.8 | 495.5 | 378.6 | 342.3 | 440.3
2403 | 2228 | 521.7 | 563.8 | 539.8 | 484 | 495.6 | 378.7 | 342.3 | 440.2
2404 | 2229 | 521.8 | 563.8 | 539.7 | 484.1 | 495.7 | 378.7 | 342.3 | 440.2
2405 | 2230 | 522 | 563.8 | 539.6 | 484.3 | 495.8 | 378.8 | 342.3 | 440.2
2406 | 2231 | 522 | 563.8 | 539.5 | 484.4 | 496 | 379.1 | 342.4 | 440.3
2407 | 2232 | 522.1 | 563.9 | 539.5 | 484.6 | 496.2 | 379.3 | 342.4 | 440.2
2408 | 2233 | 522.3 | 564 | 539.4 | 484.8 | 496.4 | 379.4 | 342.4 | 440.3
2409 | 2234 | 522.4 | 564.1 | 539.3 | 485 | 496.7 | 379.5 | 342.4 | 440.3
2410 | 2235 | 522.4 | 564.1 | 539.2 | 485.2 | 497 | 379.6 | 342.5 | 440.3
2411 | 2236 | 522.4 | 564.2 | 539.1 | 485.4 | 497.4 | 379.8 | 342.6 | 440.4
2412 | 2237 | 522.3 | 564.2 | 539 | 485.7 | 497.8 | 380 | 342.6 | 440.4
2413 | 2238 | 522.5 | 564.3 | 538.9 | 486 | 498.2 | 380.1 | 342.7 | 440.4
2414 | 2239 | 522.4 | 564.4 | 538.7 | 486.3 | 498.6 | 380.1 | 342.7 | 440.4
2415 | 2240 | 522.3 | 564.5 | 538.5 | 486.6 | 499 | 380 | 342.7 | 440.6
2416 | 2241 | 522.2 | 564.6 | 538.3 | 486.9 | 499.4 | 380 | 342.7 | 440.7
2417 | 2242 | 522 | 564.6 | 538.1 | 487.2 | 499.8 | 380 | 342.7 | 440.8
2418 | 2243 | 521.9 | 564.7 | 538 | 487.5 | 500.1 | 379.8 | 342.7 | 440.9
2419 | 2244 | 521.9 | 564.7 | 537.8 | 487.7 | 500.5 | 379.6 | 342.8 | 441
2420 | 2245 | 521.7 | 564.7 | 537.7 | 488 | 500.8 | 379.5 | 342.8 | 441
2421 | 2246 | 521.6 | 564.8 | 537.4 | 488.3 | 501.3 | 379.6 | 342.7 | 441
2422 | 2247 | 521.6 | 564.8 | 537.6 | 488.5 | 501.4 | 379.6 | 342.7 | 441.1
2423 | 2248 | 521.6 | 564.9 | 537.5 | 488.7 | 501.7 | 379.5 | 342.7 | 441.1
2424 | 2249 | 521.6 | 564.9 | 537.4 | 488.9 | 502 | 379.5 | 342.8 | 441.1
2425 | 2250 | 521.7 | 564.9 | 537.4 | 489.1 | 502.2 | 379.5 | 342.8 | 441.1
2426 | 2251 | 521.7 | 565 | 537.4 | 489.3 | 502.5 | 379.4 | 342.8 | 441.2
2427 | 2252 | 521.8 | 565.1 | 537.3 | 489.5 | 502.9 | 379.5 | 342.9 | 441.2
2428 | 2253 | 522.2 | 565.1 | 537.4 | 489.6 | 503.2 | 379.5 | 342.9 | 441.2
2429 | 2254 | 522.6 | 565.1 | 537.4 | 489.8 | 503.5 | 379.5 | 342.9 | 441.4
2430 | 2255 | 523 | 565.1 | 537.4 | 490 | 503.9 | 379.5 | 342.9 | 441.6
2431 | 2256 | 523.2 | 565 | 537.4 | 490.2 | 504.2 | 379.6 | 342.9 | 441.6
2432 | 2257 | 523.4 | 564.9 | 537.4 | 490.4 | 504.5 | 379.5 | 343.1 | 441.6
2433 | 2258 | 523.6 | 564.9 | 537.4 | 490.7 | 504.8 | 379.5 | 343.2 | 441.8
2434 | 2259 | 523.8 | 565 | 537.4 | 490.9 | 505.1 | 379.5 | 343.2 | 441.9
2435 | 2260 | 523.8 | 565.2 | 537.4 | 491.1 | 505.4 | 379.5 | 343.2 | 441.9
2436 | 2261 | 523.9 | 565.4 | 537.5 | 491.2 | 505.6 | 379.5 | 343.3 | 441.9
2437 | 2262 | 524.1 | 565.6 | 537.5 | 491.4 | 505.9 | 379.6 | 343.3 | 441.9
2438 | 2263 | 524.3 | 565.7 | 537.6 | 491.6 | 506 | 379.6 | 343.3 | 442
2439 | 2264 | 524.3 | 565.7 | 537.6 | 491.7 | 506.2 | 379.7 | 343.3 | 442
2440 | 2265 | 524.3 | 565.7 | 537.7 | 491.9 | 506.4 | 379.8 | 343.3 | 442
2441 | 2266 | 524.3 | 565.8 | 537.7 | 492 | 506.6 | 379.8 | 343.2 | 442.1
2442 | 2267 | 524.2 | 565.9 | 537.8 | 492.1 | 506.8 | 379.8 | 343.3 | 442.1
2443 | 2268 | 524.3 | 565.9 | 537.9 | 492.2 | 506.9 | 379.7 | 343.3 | 442.2
2444 | 2269 | 524.2 | 566 | 538 | 492.3 | 507.2 | 379.8 | 343.3 | 442.2
2445 | 2270 | 524 | 566 | 538.1 | 492.4 | 507.4 | 379.9 | 343.3 | 442.2
2446 | 2271 | 523.8 | 566 | 538.2 | 492.5 | 507.6 | 379.9 | 343.3 | 442.3
2447 | 2272 | 523.6 | 566.1 | 538.3 | 492.7 | 507.8 | 380 | 343.4 | 442.5
2448 | 2273 | 523.7 | 566.1 | 538.4 | 492.9 | 508.1 | 380.1 | 343.4 | 442.6
2449 | 2274 | 523.7 | 566.2 | 538.5 | 493 | 508.4 | 380.2 | 343.3 | 442.7
2450 | 2275 | 523.8 | 566.3 | 538.6 | 493.2 | 508.6 | 380.2 | 343.4 | 442.7
2451 | 2276 | 523.9 | 566.4 | 538.7 | 493.4 | 508.9 | 380.1 | 343.4 | 442.7
2452 | 2277 | 524.1 | 566.5 | 538.8 | 493.6 | 509.1 | 380.1 | 343.5 | 442.7
2453 | 2278 | 524.2 | 566.6 | 538.9 | 493.8 | 509.3 | 379.9 | 343.5 | 442.8
2454 | 2279 | 524.2 | 566.8 | 539 | 493.9 | 509.6 | 379.9 | 343.6 | 442.8
2455 | 2280 | 524 | 566.9 | 539 | 494.1 | 509.8 | 379.9 | 343.6 | 443
2456 | 2281 | 523.9 | 567 | 539.2 | 494.2 | 509.9 | 380 | 343.6 | 443.1
2457 | 2282 | 523.8 | 567.1 | 539.3 | 494.3 | 510.1 | 380.1 | 343.5 | 443.1
2458 | 2283 | 523.5 | 567.2 | 539.4 | 494.5 | 510.3 | 380 | 343.5 | 443.2
2459 | 2284 | 523.2 | 567.2 | 539.4 | 494.6 | 510.5 | 380 | 343.5 | 443.2
2460 | 2285 | 523.1 | 567.3 | 539.6 | 494.7 | 510.6 | 380 | 343.4 | 443.2
2461 | 2286 | 523 | 567.3 | 539.6 | 494.9 | 510.8 | 380.1 | 343.3 | 443.2
2462 | 2287 | 522.9 | 567.4 | 539.7 | 495.1 | 511 | 380.1 | 343.3 | 443.3
2463 | 2288 | 522.9 | 567.5 | 539.8 | 495.2 | 511.2 | 380.1 | 343.3 | 443.5
2464 | 2289 | 523.1 | 567.6 | 539.9 | 495.3 | 511.3 | 380.1 | 343.3 | 443.6
2465 | 2290 | 523 | 567.7 | 540 | 495.5 | 511.4 | 380.1 | 343.2 | 443.6
2466 | 2291 | 522.8 | 567.7 | 540.1 | 495.6 | 511.5 | 380 | 343.1 | 443.6
2467 | 2292 | 522.7 | 567.7 | 540.2 | 495.7 | 511.5 | 380 | 343.1 | 443.6
2468 | 2293 | 522.5 | 567.7 | 540.3 | 495.8 | 511.6 | 379.9 | 343 | 443.6
2469 | 2294 | 522.6 | 567.8 | 540.5 | 495.9 | 511.6 | 379.8 | 343 | 443.6
2470 | 2295 | 522.5 | 567.8 | 540.7 | 496 | 511.6 | 379.7 | 343.1 | 443.6
2471 | 2296 | 522.3 | 567.8 | 540.8 | 496 | 511.7 | 379.8 | 343.1 | 443.6
2472 | 2297 | 522.2 | 567.8 | 540.9 | 496.2 | 511.8 | 379.7 | 343 | 443.6
2473 | 2298 | 522 | 567.8 | 541.1 | 496.2 | 511.9 | 379.6 | 343.1 | 443.6
2474 | 2299 | 521.9 | 567.8 | 541.2 | 496.4 | 512 | 379.5 | 343.1 | 443.6
2475 | 2300 | 521.8 | 567.8 | 541.3 | 496.5 | 512.2 | 379.5 | 342.9 | 443.5
2476 | 2301 | 521.7 | 567.9 | 541.3 | 496.6 | 512.4 | 379.5 | 342.8 | 443.5
2477 | 2302 | 521.5 | 567.8 | 541.4 | 496.8 | 512.6 | 379.5 | 342.8 | 443.6
2478 | 2303 | 521.3 | 567.8 | 541.6 | 496.9 | 512.9 | 379.6 | 342.8 | 443.6
2479 | 2304 | 521.4 | 567.9 | 541.6 | 497.1 | 513.1 | 379.7 | 342.8 | 443.6
2480 | 2305 | 521.5 | 568 | 541.8 | 497.3 | 513.3 | 379.7 | 342.8 | 443.6
2481 | 2306 | 521.5 | 568.2 | 541.9 | 497.4 | 513.5 | 379.6 | 342.8 | 443.6
2482 | 2307 | 521.4 | 568.3 | 542 | 497.6 | 513.7 | 379.5 | 342.8 | 443.7
2483 | 2308 | 521.3 | 568.5 | 542.1 | 497.7 | 513.8 | 379.4 | 342.9 | 443.7
2484 | 2309 | 521.4 | 568.5 | 542.2 | 497.8 | 513.9 | 379.2 | 342.7 | 443.7
2485 | 2310 | 521.7 | 568.6 | 542.3 | 497.9 | 514.1 | 379.1 | 343 | 443.7
2486 | 2311 | 521.8 | 568.6 | 542.4 | 498 | 514.3 | 379 | 343 | 443.7
2487 | 2312 | 521.7 | 568.4 | 542.6 | 498.1 | 514.5 | 378.9 | 343 | 443.7
2488 | 2313 | 521.8 | 568.3 | 542.7 | 498.2 | 514.7 | 379 | 343 | 443.7
2489 | 2314 | 522 | 568.3 | 542.9 | 498.3 | 514.9 | 379.1 | 343.1 | 443.8
2490 | 2315 | 521.9 | 568.3 | 543 | 498.4 | 515.2 | 379.1 | 343.1 | 443.8
2491 | 2316 | 521.7 | 568.3 | 543.2 | 498.6 | 515.4 | 379.2 | 343.1 | 443.9
2492.1 | 2317.1 | 521.5 | 568.4 | 543.4 | 498.7 | 515.6 | 379.2 | 343.1 | 444
2493.1 | 2318.1 | 521.5 | 568.5 | 543.5 | 498.9 | 515.9 | 379.3 | 343.1 | 444.1
2494.1 | 2319.1 | 521.7 | 568.7 | 543.6 | 499 | 516.1 | 379.5 | 343.2 | 444.1
2495.1 | 2320.1 | 521.7 | 568.8 | 543.8 | 499.2 | 516.3 | 379.6 | 343.2 | 444.1
2496.1 | 2321.1 | 521.9 | 569.1 | 543.9 | 499.3 | 516.6 | 379.7 | 343.2 | 444.2
2497.1 | 2322.1 | 521.9 | 569.2 | 544 | 499.4 | 516.8 | 379.8 | 343.2 | 444.2
2498.1 | 2323.1 | 522 | 569.3 | 544.2 | 499.5 | 516.9 | 379.9 | 343.2 | 444.1
2499.1 | 2324.1 | 521.9 | 569.3 | 544.3 | 499.7 | 517 | 379.9 | 343.3 | 444
2500.1 | 2325.1 | 521.7 | 569.3 | 544.4 | 499.8 | 517.1 | 380.1 | 343.3 | 444
2501.1 | 2326.1 | 521.6 | 569.2 | 544.6 | 499.9 | 517.2 | 380.2 | 343.3 | 444
2502.1 | 2327.1 | 521.6 | 569 | 544.7 | 500 | 517.3 | 380.3 | 343.3 | 444.1
2503.1 | 2328.1 | 521.5 | 569 | 544.9 | 500 | 517.5 | 380.1 | 343.3 | 444.1
2504.1 | 2329.1 | 521.6 | 569 | 545 | 500.1 | 517.7 | 379.9 | 343.3 | 444
2505.1 | 2330.1 | 521.5 | 569 | 545.1 | 500.3 | 517.9 | 379.8 | 343.3 | 444.1
2506.1 | 2331.1 | 521.6 | 569 | 545.2 | 500.4 | 518.1 | 379.8 | 343.4 | 444.1
2507.1 | 2332.1 | 521.7 | 569 | 545.3 | 500.5 | 518.4 | 379.8 | 343.4 | 444.1
2508.1 | 2333.1 | 522 | 569.1 | 545.5 | 500.7 | 518.6 | 379.8 | 343.5 | 444.2
2509.1 | 2334.1 | 522.3 | 569.3 | 545.6 | 500.8 | 518.9 | 379.8 | 343.5 | 444.2
2510.1 | 2335.1 | 522.3 | 569.4 | 545.7 | 501 | 519.2 | 379.8 | 343.5 | 444.3
2511.1 | 2336.1 | 522.2 | 569.6 | 545.8 | 501.1 | 519.4 | 379.7 | 343.5 | 444.3
2512.1 | 2337.1 | 522.3 | 569.7 | 546 | 501.2 | 519.7 | 379.6 | 343.5 | 444.2
2513.1 | 2338.1 | 522.5 | 569.7 | 546.1 | 501.4 | 519.9 | 379.7 | 343.4 | 444.2
2514.1 | 2339.1 | 522.5 | 569.8 | 546.2 | 501.5 | 520.2 | 379.8 | 343.4 | 444.2
2515.1 | 2340.1 | 522.5 | 569.8 | 546.3 | 501.6 | 520.4 | 379.9 | 343.4 | 444.2
2516.1 | 2341.1 | 522.6 | 569.8 | 546.5 | 501.7 | 520.6 | 380 | 343.3 | 444.2
2517.1 | 2342.1 | 522.9 | 569.7 | 546.6 | 501.9 | 520.9 | 380 | 343.1 | 444.2
2518.1 | 2343.1 | 523 | 569.7 | 546.7 | 502 | 521.2 | 380 | 343.1 | 444.4
2519.1 | 2344.1 | 523.2 | 569.6 | 546.8 | 502.1 | 521.5 | 380.2 | 343.2 | 444.5
2520.1 | 2345.1 | 523.4 | 569.6 | 547 | 502.3 | 521.9 | 380.2 | 343.2 | 444.5
2521.1 | 2346.1 | 523.7 | 569.7 | 547.1 | 502.5 | 522.4 | 380.2 | 343.2 | 444.5
2522.1 | 2347.1 | 523.8 | 569.7 | 547.2 | 502.7 | 522.8 | 380.3 | 343.2 | 444.6
2523.1 | 2348.1 | 523.8 | 569.7 | 547.4 | 502.8 | 523.2 | 380.3 | 343.2 | 444.6
2524.1 | 2349.1 | 523.8 | 569.7 | 547.4 | 503.1 | 523.8 | 380.5 | 343.2 | 444.6
2525.1 | 2350.1 | 523.7 | 569.9 | 547.1 | 503.4 | 524.6 | 380.6 | 343.2 | 444.5
2526.1 | 2351.1 | 523.6 | 570 | 547.2 | 503.6 | 525 | 380.6 | 343.3 | 444.6
2527.1 | 2352.1 | 523.5 | 570.2 | 547.4 | 503.8 | 525.3 | 380.7 | 343.4 | 444.6
2528.1 | 2353.1 | 523.6 | 570.5 | 547.5 | 503.9 | 525.6 | 380.9 | 343.3 | 444.6
2529.1 | 2354.1 | 523.6 | 570.7 | 547.7 | 504.1 | 525.8 | 380.9 | 343.3 | 444.5
2530.1 | 2355.1 | 523.4 | 570.9 | 547.9 | 504.2 | 525.9 | 381 | 343.4 | 444.5
2531.1 | 2356.1 | 523.2 | 571.1 | 548 | 504.4 | 526.1 | 381.1 | 343.4 | 444.5
2532.1 | 2357.1 | 523.1 | 571.1 | 548.1 | 504.5 | 526.3 | 381.1 | 343.4 | 444.5
2533.1 | 2358.1 | 522.6 | 571.1 | 548.3 | 504.6 | 526.4 | 381.1 | 343.5 | 444.5
2534.1 | 2359.1 | 522.5 | 570.9 | 548.4 | 504.7 | 526.6 | 381.1 | 343.4 | 444.4
2535.1 | 2360.1 | 522.5 | 570.9 | 548.5 | 504.9 | 526.9 | 381.2 | 343.4 | 444.4
2536.1 | 2361.1 | 522.3 | 570.9 | 548.6 | 505 | 527.2 | 381.3 | 343.5 | 444.4
2537.1 | 2362.1 | 522.1 | 570.9 | 548.8 | 505.1 | 527.4 | 381.1 | 343.4 | 444.5
2538.1 | 2363.1 | 521.7 | 571 | 548.9 | 505.3 | 527.8 | 381.1 | 343.4 | 444.6
2539.1 | 2364.1 | 521.4 | 571 | 549 | 505.5 | 528.2 | 381 | 343.5 | 444.6
2540.1 | 2365.1 | 521.3 | 570.9 | 549.1 | 505.6 | 528.5 | 381.1 | 343.5 | 444.7
2541.1 | 2366.1 | 521.5 | 570.8 | 549.2 | 505.8 | 528.9 | 381 | 343.4 | 444.8
2542.1 | 2367.1 | 521.5 | 570.6 | 549.3 | 506 | 529.4 | 381 | 343.5 | 444.9
2543.1 | 2368.1 | 521.5 | 570.6 | 549.4 | 506.3 | 529.8 | 381.1 | 343.5 | 445
2544.1 | 2369.1 | 521.5 | 570.5 | 549.5 | 506.5 | 530.2 | 381.2 | 343.6 | 445
2545.1 | 2370.1 | 521.7 | 570.4 | 549.5 | 506.8 | 530.7 | 381.3 | 343.6 | 445
2546.1 | 2371.1 | 521.7 | 570.4 | 549.6 | 507.1 | 531.2 | 381.2 | 343.6 | 445.1
2547.1 | 2372.1 | 521.5 | 570.4 | 549.7 | 507.3 | 531.6 | 381.2 | 343.6 | 445.2
2548.1 | 2373.1 | 521.3 | 570.4 | 549.8 | 507.5 | 532.1 | 381.1 | 343.5 | 445.2
2549.1 | 2374.1 | 521 | 570.6 | 549.8 | 507.8 | 532.6 | 381.1 | 343.5 | 445.3
2550.1 | 2375.1 | 521.1 | 570.7 | 549.9 | 508 | 533 | 381.2 | 343.5 | 445.3
2551.1 | 2376.1 | 521.3 | 570.9 | 550 | 508.2 | 533.4 | 381.3 | 343.4 | 445.3
2552.1 | 2377.1 | 521.4 | 571.1 | 550 | 508.4 | 533.8 | 381.4 | 343.3 | 445.2
2553.1 | 2378.1 | 521.5 | 571.3 | 550.1 | 508.6 | 534.2 | 381.3 | 343.3 | 445.3
2554.1 | 2379.1 | 521.6 | 571.4 | 550.2 | 508.7 | 534.5 | 381.2 | 343.2 | 445.4
2555.1 | 2380.1 | 521.6 | 571.4 | 550.3 | 508.8 | 534.9 | 381.1 | 343.2 | 445.3
2556.1 | 2381.1 | 521.6 | 571.4 | 550.4 | 509 | 535.3 | 381.1 | 343.2 | 445.3
2557.1 | 2382.1 | 521.7 | 571.3 | 550.5 | 509.1 | 535.6 | 381.2 | 343.3 | 445.3
2558.1 | 2383.1 | 521.6 | 571.2 | 550.6 | 509.1 | 535.8 | 381.1 | 343.3 | 445.2
2559.1 | 2384.1 | 521.3 | 571.2 | 550.7 | 509.3 | 536.2 | 381 | 343.4 | 445.3
2560.1 | 2385.1 | 521.3 | 571.1 | 550.8 | 509.4 | 536.6 | 381 | 343.5 | 445.4
2561.1 | 2386.1 | 521 | 571.1 | 551 | 509.5 | 536.9 | 381 | 343.4 | 445.4
2562.1 | 2387.1 | 520.9 | 571.1 | 551.2 | 509.7 | 537.2 | 381 | 343.5 | 445.4
2563.1 | 2388.1 | 521 | 571.2 | 551.2 | 509.9 | 537.7 | 381.2 | 343.6 | 445.5
2564.1 | 2389.1 | 521.2 | 571.3 | 551.3 | 510.1 | 538.1 | 381.3 | 343.6 | 445.5
2565.1 | 2390.1 | 521.3 | 571.2 | 551.5 | 510.3 | 538.5 | 381.3 | 343.6 | 445.6
2566.1 | 2391.1 | 521.2 | 571.2 | 551.5 | 510.6 | 539 | 381.4 | 343.7 | 445.6
2567.1 | 2392.1 | 521.2 | 571.3 | 551.6 | 510.8 | 539.5 | 381.4 | 343.7 | 445.7
2568.1 | 2393.1 | 521.1 | 571.4 | 551.7 | 511.1 | 539.9 | 381.4 | 343.6 | 445.7
2569.1 | 2394.1 | 521.2 | 571.5 | 551.7 | 511.3 | 540.3 | 381.4 | 343.5 | 445.6
2570.1 | 2395.1 | 521.3 | 571.6 | 551.7 | 511.6 | 540.8 | 381.3 | 343.5 | 445.7
2571.1 | 2396.1 | 521.4 | 571.6 | 551.8 | 511.8 | 541.2 | 381.2 | 343.5 | 445.8
2572.1 | 2397.1 | 521.5 | 571.6 | 551.9 | 512 | 541.5 | 381.2 | 343.6 | 445.7
2573.1 | 2398.1 | 521.7 | 571.6 | 551.9 | 512.2 | 542 | 381.2 | 343.6 | 445.7
2574.1 | 2399.1 | 522 | 571.6 | 552 | 512.4 | 542.3 | 381.2 | 343.7 | 445.8
2575.1 | 2400.1 | 522.3 | 571.7 | 552.1 | 512.6 | 542.6 | 381.3 | 343.7 | 445.8
2576.1 | 2401.1 | 522.3 | 571.8 | 552.2 | 512.7 | 542.9 | 381.3 | 343.8 | 445.8
2577.1 | 2402.1 | 522.5 | 571.8 | 552.2 | 512.9 | 543.3 | 381.2 | 343.8 | 446
2578.1 | 2403.1 | 522.6 | 571.8 | 552.3 | 513 | 543.6 | 381.2 | 343.8 | 446
2579.1 | 2404.1 | 522.7 | 571.7 | 552.5 | 513.1 | 543.9 | 381.3 | 343.9 | 446
2580.1 | 2405.1 | 522.6 | 571.7 | 552.5 | 513.2 | 544.2 | 381.3 | 343.9 | 446.1
2581.1 | 2406.1 | 522.8 | 571.7 | 552.6 | 513.3 | 544.6 | 381.4 | 344.1 | 446.1
2582.1 | 2407.1 | 522.9 | 571.7 | 552.7 | 513.5 | 544.9 | 381.5 | 344.1 | 446.1
2583.1 | 2408.1 | 522.8 | 571.7 | 552.8 | 513.6 | 545.3 | 381.5 | 344 | 446.2
2584.1 | 2409.1 | 522.7 | 571.9 | 552.9 | 513.8 | 545.8 | 381.5 | 344 | 446.2
2585.1 | 2410.1 | 522.8 | 571.9 | 553 | 514 | 546.3 | 381.6 | 344 | 446.2
2586.1 | 2411.1 | 522.9 | 572 | 553.1 | 514.1 | 546.8 | 381.6 | 344 | 446.3
2587.1 | 2412.1 | 523 | 572 | 553.1 | 514.4 | 547.5 | 381.6 | 344 | 446.4
2588.1 | 2413.1 | 523.1 | 572.1 | 553.2 | 514.6 | 548.1 | 381.7 | 344.1 | 446.4
2589.1 | 2414.1 | 522.9 | 572.1 | 553.4 | 514.7 | 548.7 | 381.8 | 344 | 446.5
2590.1 | 2415.1 | 522.9 | 572.2 | 553.5 | 514.9 | 549.4 | 382 | 344 | 446.6
2591.1 | 2416.1 | 522.8 | 572.3 | 553.6 | 515.1 | 550.1 | 382.1 | 344 | 446.7
2592.1 | 2417.1 | 523.1 | 572.5 | 553.6 | 515.3 | 550.8 | 382.2 | 343.9 | 446.7
2593.1 | 2418.1 | 523.3 | 572.6 | 553.8 | 515.4 | 551.4 | 382.3 | 343.8 | 446.7
2594.1 | 2419.1 | 523.2 | 572.8 | 553.8 | 515.6 | 552.2 | 382.5 | 343.6 | 446.6
2595.1 | 2420.1 | 522.8 | 572.9 | 553.9 | 515.8 | 552.8 | 382.6 | 343.5 | 446.6
2596.1 | 2421.1 | 522.6 | 572.9 | 554 | 516 | 553.4 | 382.7 | 343.5 | 446.7
2597.1 | 2422.1 | 522.6 | 572.9 | 554.1 | 516.1 | 554 | 382.9 | 343.5 | 446.8
2598.1 | 2423.1 | 522.7 | 572.9 | 554.1 | 516.3 | 554.6 | 383.1 | 343.6 | 446.8
2599.1 | 2424.1 | 522.7 | 572.8 | 554.2 | 516.5 | 555.1 | 383.2 | 343.6 | 446.9
2600.1 | 2425.1 | 522.8 | 572.8 | 554.3 | 516.6 | 555.6 | 383.4 | 343.5 | 446.9
2601.1 | 2426.1 | 522.7 | 572.9 | 554.4 | 516.7 | 556.1 | 383.5 | 343.6 | 446.9
2602.1 | 2427.1 | 522.8 | 573 | 554.5 | 516.9 | 556.6 | 383.7 | 343.6 | 446.8
2603.1 | 2428.1 | 522.8 | 573.1 | 554.7 | 517 | 557 | 383.9 | 343.6 | 446.7
2604.1 | 2429.1 | 522.8 | 573.2 | 554.9 | 517.1 | 557.5 | 384.1 | 343.6 | 446.8
2605.1 | 2430.1 | 523 | 573.3 | 555 | 517.4 | 558.1 | 384.2 | 343.6 | 446.8
2606.1 | 2431.1 | 523.1 | 573.3 | 555.1 | 517.6 | 558.8 | 384.3 | 343.7 | 446.8
2607.1 | 2432.1 | 523.2 | 573.2 | 555.3 | 517.8 | 559.3 | 384.3 | 343.5 | 446.8
2608.1 | 2433.1 | 523.4 | 573.2 | 555.3 | 518 | 560 | 384.5 | 343.7 | 446.8
2609.1 | 2434.1 | 523.5 | 573.3 | 555.4 | 518.2 | 560.7 | 384.5 | 343.8 | 446.8
2610.1 | 2435.1 | 523.6 | 573.3 | 555.5 | 518.4 | 561.2 | 384.5 | 343.7 | 446.8
2611.1 | 2436.1 | 523.7 | 573.2 | 555.7 | 518.5 | 561.8 | 384.5 | 343.7 | 446.8
2612.1 | 2437.1 | 523.6 | 573.2 | 555.7 | 518.7 | 562.4 | 384.5 | 343.9 | 446.8
2613.1 | 2438.1 | 523.6 | 573.2 | 555.9 | 518.9 | 563 | 384.5 | 344 | 446.8
2614.1 | 2439.1 | 523.6 | 573.3 | 556 | 519.1 | 563.4 | 384.5 | 344.1 | 446.8
2615.1 | 2440.1 | 523.4 | 573.5 | 556.1 | 519.3 | 564.1 | 384.6 | 344.1 | 446.7
2616.1 | 2441.1 | 523.5 | 573.5 | 556.2 | 519.5 | 564.7 | 384.6 | 344 | 446.7
2617.1 | 2442.1 | 523.5 | 573.6 | 556.4 | 519.6 | 565.3 | 384.5 | 344.1 | 446.8
2618.1 | 2443.1 | 523.6 | 573.8 | 556.6 | 519.8 | 565.9 | 384.6 | 344.1 | 446.9
2619.1 | 2444.1 | 523.5 | 573.9 | 556.7 | 520.1 | 566.5 | 384.7 | 344.1 | 447
2620.1 | 2445.1 | 523.5 | 574 | 556.8 | 520.3 | 567 | 384.9 | 344.1 | 446.9
2621.1 | 2446.1 | 523.3 | 574.1 | 557 | 520.4 | 567.5 | 384.9 | 344 | 446.8
2622.1 | 2447.1 | 523.2 | 574.2 | 557.1 | 520.6 | 568 | 384.9 | 343.8 | 446.7
2623.1 | 2448.1 | 523 | 574.3 | 557.2 | 520.8 | 568.6 | 385 | 343.6 | 446.6
2624.1 | 2449.1 | 522.8 | 574.4 | 557.4 | 521 | 569 | 385.1 | 343.6 | 446.5
2625.1 | 2450.1 | 522.9 | 574.6 | 557.6 | 521.1 | 569.5 | 385.2 | 343.6 | 446.5
2626.1 | 2451.1 | 522.9 | 574.8 | 557.7 | 521.2 | 570 | 385.2 | 343.5 | 446.4
2627.1 | 2452.1 | 523.2 | 575 | 557.8 | 521.3 | 570.4 | 385.3 | 343.7 | 446.3
2628.1 | 2453.1 | 523.1 | 575 | 558 | 521.3 | 570.7 | 385.3 | 343.7 | 446.2
2629.1 | 2454.1 | 522.9 | 575 | 558 | 521.4 | 571.1 | 385.3 | 343.6 | 446.3
2630.1 | 2455.1 | 522.7 | 575 | 558.1 | 521.5 | 571.5 | 385.3 | 343.6 | 446.2
2631.1 | 2456.1 | 522.5 | 575 | 558.2 | 521.6 | 571.8 | 385.3 | 343.7 | 446.3
2632.1 | 2457.1 | 522.2 | 575 | 558.3 | 521.6 | 572 | 385.3 | 343.7 | 446.2
2633.1 | 2458.1 | 522.1 | 575.1 | 558.5 | 521.7 | 572.3 | 385.3 | 343.6 | 446.1
2634.1 | 2459.1 | 521.9 | 575.1 | 558.6 | 521.8 | 572.6 | 385.1 | 343.6 | 446
2635.1 | 2460.1 | 522 | 575 | 558.8 | 521.8 | 572.7 | 384.9 | 343.6 | 445.9
2636.1 | 2461.1 | 522.1 | 575 | 558.9 | 521.8 | 573 | 384.8 | 343.6 | 445.8
2637.1 | 2462.1 | 522.3 | 575 | 559.1 | 521.9 | 573.2 | 384.8 | 343.6 | 445.8
2638.1 | 2463.1 | 522.3 | 575 | 559.3 | 522 | 573.5 | 384.8 | 343.6 | 445.8
2639.1 | 2464.1 | 522.2 | 574.9 | 559.5 | 522 | 573.6 | 384.6 | 343.6 | 445.7
2640.1 | 2465.1 | 522.3 | 574.9 | 559.6 | 522.2 | 573.9 | 384.5 | 343.6 | 445.4
2641.1 | 2466.1 | 522.2 | 574.9 | 559.7 | 522.3 | 574.1 | 384.5 | 343.6 | 445.3
2642.1 | 2467.1 | 522.1 | 574.9 | 559.9 | 522.4 | 574.1 | 384.5 | 343.6 | 445.3
2643.1 | 2468.1 | 522 | 575 | 560 | 522.5 | 574.3 | 384.4 | 343.7 | 445.3
2644.1 | 2469.1 | 521.9 | 575.1 | 560.1 | 522.6 | 574.5 | 384.4 | 343.6 | 445.3
2645.1 | 2470.1 | 522 | 575.1 | 560.3 | 522.7 | 574.7 | 384.3 | 343.4 | 445.2
2646.1 | 2471.1 | 522.2 | 575 | 560.5 | 522.8 | 574.8 | 384.2 | 343.4 | 445.2
2647.1 | 2472.1 | 522.1 | 575 | 560.6 | 523 | 575.1 | 384.1 | 343.4 | 445.2
2648.1 | 2473.1 | 522.1 | 574.8 | 560.8 | 523.1 | 575.3 | 384.1 | 343.4 | 445.3
2649.1 | 2474.1 | 522.2 | 574.8 | 561 | 523.2 | 575.4 | 384.1 | 343.4 | 445.2
2650.1 | 2475.1 | 522.4 | 574.9 | 561.2 | 523.4 | 575.6 | 384.1 | 343.4 | 445.2
2651.1 | 2476.1 | 522.5 | 575 | 561.4 | 523.6 | 575.8 | 384.2 | 343.5 | 445.1
2652.1 | 2477.1 | 522.6 | 575 | 561.7 | 523.8 | 575.9 | 384.3 | 343.5 | 445.2
2653.1 | 2478.1 | 522.8 | 575.1 | 562 | 524 | 576.3 | 384.3 | 343.5 | 445.2
2654.1 | 2479.1 | 522.8 | 575.3 | 562.1 | 524.3 | 576.7 | 384.2 | 343.7 | 445.3
2655.1 | 2480.1 | 522.8 | 575.4 | 562.3 | 524.6 | 577.1 | 384.1 | 343.8 | 445.4
2656.1 | 2481.1 | 523 | 575.6 | 562.5 | 524.9 | 577.4 | 384 | 343.8 | 445.5
2657.1 | 2482.1 | 523.2 | 575.8 | 562.5 | 525.2 | 577.8 | 383.9 | 343.9 | 445.7
2658.1 | 2483.1 | 523.4 | 576 | 562.7 | 525.6 | 578.3 | 383.7 | 344 | 445.7
2659.1 | 2484.1 | 523.4 | 576.3 | 562.8 | 525.9 | 578.8 | 383.5 | 344.1 | 445.8
2660.1 | 2485.1 | 523.4 | 576.6 | 563 | 526.2 | 579.3 | 383.4 | 344.1 | 445.9
2661.1 | 2486.1 | 523.3 | 577 | 563.1 | 526.5 | 579.9 | 383.4 | 344.1 | 445.9
2662.1 | 2487.1 | 523.3 | 577.2 | 563.2 | 526.7 | 580.4 | 383.3 | 344.2 | 445.6
2663.1 | 2488.1 | 523.3 | 577.4 | 563.5 | 526.9 | 580.7 | 383.4 | 344.2 | 445.6
2664.1 | 2489.1 | 523.2 | 577.6 | 563.6 | 527.2 | 581.1 | 383.4 | 344.3 | 445.6
2665.1 | 2490.1 | 523.3 | 577.7 | 563.7 | 527.4 | 581.5 | 383.4 | 344 | 445.3
2666.1 | 2491.1 | 523.3 | 577.8 | 563.8 | 527.6 | 581.8 | 383.5 | 343.9 | 445.3
2667.1 | 2492.1 | 523.2 | 578 | 563.9 | 527.8 | 581.9 | 383.5 | 343.9 | 445.3
2668.1 | 2493.1 | 523.2 | 578 | 563.9 | 528 | 582.2 | 383.5 | 344 | 445.3
2669.1 | 2494.1 | 523 | 578.1 | 564 | 528.2 | 582.3 | 383.5 | 344.1 | 445.2
2670.1 | 2495.1 | 522.8 | 578 | 564.1 | 528.3 | 582.4 | 383.5 | 344.2 | 445.3
2671.1 | 2496.1 | 522.8 | 578 | 564.1 | 528.5 | 582.5 | 383.5 | 344.2 | 445.2
2672.1 | 2497.1 | 522.8 | 578 | 564.2 | 528.7 | 582.7 | 383.5 | 344.2 | 445.1
2673.1 | 2498.1 | 522.8 | 578 | 564.3 | 528.9 | 582.9 | 383.4 | 344.3 | 445
2674.1 | 2499.1 | 522.7 | 578 | 564.4 | 529.1 | 583.1 | 383.4 | 344.5 | 445
2675.1 | 2500.1 | 522.8 | 578 | 564.5 | 529.2 | 583.3 | 383.4 | 344.4 | 445
2676.1 | 2501.1 | 523 | 578 | 564.6 | 529.4 | 583.5 | 383.4 | 344.5 | 445
2677.1 | 2502.1 | 523.1 | 577.9 | 564.9 | 529.5 | 583.6 | 383.4 | 344.6 | 444.9
2678.1 | 2503.1 | 523 | 578 | 565 | 529.7 | 583.8 | 383.4 | 344.6 | 444.9
2679.1 | 2504.1 | 523.1 | 578.1 | 565.2 | 529.8 | 584 | 383.5 | 344.8 | 444.8
2680.1 | 2505.1 | 523 | 578.1 | 565.5 | 530 | 584 | 383.4 | 344.9 | 444.8
2681.1 | 2506.1 | 523 | 578.1 | 565.7 | 530.1 | 584.1 | 383.4 | 344.9 | 444.8
2682.1 | 2507.1 | 522.8 | 578.2 | 565.9 | 530.3 | 584.4 | 383.6 | 344.9 | 444.7
2683.1 | 2508.1 | 522.8 | 578.3 | 566.1 | 530.5 | 584.7 | 383.8 | 344.9 | 444.8
2684.1 | 2509.1 | 522.8 | 578.4 | 566.4 | 530.7 | 584.9 | 384 | 344.9 | 444.8
2685.1 | 2510.1 | 522.7 | 578.6 | 566.5 | 531 | 585.3 | 384.2 | 344.9 | 444.8
2686.1 | 2511.1 | 522.7 | 578.8 | 566.7 | 531.2 | 585.6 | 384.3 | 344.8 | 444.9
2687.1 | 2512.1 | 522.7 | 578.9 | 567 | 531.4 | 585.9 | 384.4 | 344.8 | 444.9
2688.1 | 2513.1 | 522.6 | 579.1 | 567.2 | 531.7 | 586.1 | 384.5 | 344.8 | 445
2689.1 | 2514.1 | 522.7 | 579.4 | 567.4 | 531.9 | 586.4 | 384.6 | 344.8 | 445
2690.1 | 2515.1 | 522.9 | 579.6 | 567.6 | 532.2 | 586.7 | 384.6 | 344.8 | 445
2691.1 | 2516.1 | 523 | 579.8 | 567.9 | 532.4 | 587 | 384.6 | 344.7 | 445
2692.1 | 2517.1 | 522.9 | 579.9 | 568.1 | 532.7 | 587.2 | 384.6 | 344.5 | 445.1
2693.1 | 2518.1 | 522.7 | 580.1 | 568.3 | 532.9 | 587.5 | 384.7 | 344.4 | 445.3
2694.1 | 2519.1 | 522.5 | 580.4 | 568.4 | 533.2 | 587.6 | 384.8 | 344.4 | 445.4
2695.1 | 2520.1 | 522.4 | 580.6 | 568.6 | 533.5 | 587.9 | 384.9 | 344.5 | 445.4
2696.1 | 2521.1 | 522.5 | 580.8 | 568.7 | 533.8 | 588.1 | 385 | 344.5 | 445.5
2697.1 | 2522.1 | 522.6 | 581 | 568.8 | 534 | 588.4 | 385.2 | 344.5 | 445.6
2698.1 | 2523.1 | 522.4 | 581.2 | 569 | 534.2 | 588.5 | 385.3 | 344.5 | 445.7
2699.1 | 2524.1 | 522.3 | 581.4 | 569.1 | 534.5 | 588.7 | 385.3 | 344.5 | 445.7
2700.1 | 2525.1 | 522.3 | 581.5 | 569.3 | 534.8 | 589 | 385.4 | 344.6 | 445.8
2701.1 | 2526.1 | 522.3 | 581.7 | 569.5 | 535 | 589.3 | 385.3 | 344.7 | 445.8
2702.1 | 2527.1 | 522.2 | 581.9 | 569.7 | 535.3 | 589.7 | 385.2 | 344.8 | 446
2703.1 | 2528.1 | 522 | 582 | 569.7 | 535.6 | 590.1 | 385.2 | 344.9 | 446.1
2704.1 | 2529.1 | 522 | 582.1 | 569.9 | 535.9 | 590.5 | 385.3 | 344.9 | 446.2
2705.1 | 2530.1 | 521.9 | 582.3 | 570.1 | 536.1 | 590.8 | 385.3 | 344.9 | 446.2
2706.1 | 2531.1 | 521.8 | 582.4 | 570.2 | 536.4 | 591.1 | 385.4 | 345 | 446.2
2707.1 | 2532.1 | 521.7 | 582.6 | 570.4 | 536.7 | 591.3 | 385.6 | 345 | 446.2
2708.1 | 2533.1 | 521.8 | 582.7 | 570.6 | 537 | 591.6 | 385.7 | 345 | 446.3
2709.1 | 2534.1 | 521.9 | 582.8 | 570.9 | 537.2 | 591.9 | 385.9 | 344.9 | 446.4
2710.1 | 2535.1 | 522 | 583 | 571 | 537.5 | 592.4 | 385.9 | 345 | 446.5
2711.1 | 2536.1 | 522 | 583 | 571.1 | 537.8 | 592.9 | 385.9 | 345 | 446.6
2712.1 | 2537.1 | 521.9 | 583 | 571.4 | 538 | 593.2 | 385.8 | 345.1 | 446.8
2713.1 | 2538.1 | 521.9 | 583.1 | 571.5 | 538.3 | 593.5 | 385.7 | 345.1 | 447
2714.1 | 2539.1 | 521.8 | 583.2 | 571.7 | 538.5 | 593.8 | 385.7 | 345.2 | 447.1
2715.1 | 2540.1 | 521.7 | 583.4 | 572 | 538.8 | 594 | 385.6 | 345.1 | 447.3
2716.1 | 2541.1 | 522 | 583.5 | 572.3 | 539 | 594.3 | 385.6 | 345.2 | 447.4
2717.1 | 2542.1 | 522 | 583.7 | 572.5 | 539.3 | 594.5 | 385.4 | 345.2 | 447.5
2718.1 | 2543.1 | 522.2 | 583.9 | 572.7 | 539.6 | 594.8 | 385.3 | 345.3 | 447.5
2719.1 | 2544.1 | 522.2 | 584.1 | 573.1 | 539.9 | 595 | 385.4 | 345.2 | 447.6
2720.1 | 2545.1 | 521.9 | 584.3 | 573.3 | 540.2 | 595.3 | 385.4 | 345.2 | 447.7
2721.1 | 2546.1 | 521.8 | 584.4 | 573.5 | 540.5 | 595.6 | 385.5 | 345.2 | 447.8
2722.1 | 2547.1 | 521.8 | 584.6 | 573.8 | 540.8 | 595.8 | 385.4 | 345.1 | 447.8
2723.1 | 2548.1 | 521.9 | 584.7 | 574 | 541 | 596.1 | 385.3 | 345.1 | 448
2724.1 | 2549.1 | 521.8 | 584.9 | 574.3 | 541.3 | 596.6 | 385.2 | 345.1 | 448.1
2725.1 | 2550.1 | 521.9 | 585 | 574.5 | 541.6 | 596.9 | 385.2 | 345.1 | 448.1
2726.1 | 2551.1 | 522 | 585.1 | 574.9 | 541.8 | 597.2 | 385.2 | 345.2 | 448.2
2727.1 | 2552.1 | 521.9 | 585.2 | 575.1 | 542.1 | 597.5 | 385.3 | 345.3 | 448.4
2728.1 | 2553.1 | 521.8 | 585.3 | 575.3 | 542.3 | 597.7 | 385.4 | 345.4 | 448.4
2729.1 | 2554.1 | 521.5 | 585.4 | 575.6 | 542.5 | 597.9 | 385.4 | 345.5 | 448.4
2730.1 | 2555.1 | 521.5 | 585.5 | 575.9 | 542.7 | 597.9 | 385.4 | 345.6 | 448.5
2731.1 | 2556.1 | 521.5 | 585.6 | 576.2 | 543 | 598.1 | 385.4 | 345.7 | 448.5
2732.1 | 2557.1 | 521.5 | 585.7 | 576.5 | 543.1 | 598.2 | 385.3 | 345.8 | 448.6
2733.1 | 2558.1 | 521.5 | 585.7 | 576.8 | 543.3 | 598.2 | 385.2 | 345.9 | 448.6
2734.1 | 2559.1 | 521.8 | 585.9 | 577.1 | 543.5 | 598.4 | 385.2 | 346 | 448.6
2735.1 | 2560.1 | 521.9 | 586.1 | 577.4 | 543.7 | 598.7 | 385.3 | 346 | 448.8
2736.1 | 2561.1 | 521.8 | 586.3 | 577.7 | 543.9 | 599 | 385.4 | 346.1 | 448.8
2737.1 | 2562.1 | 521.7 | 586.5 | 578 | 544.1 | 599.2 | 385.4 | 346 | 448.9
2738.1 | 2563.1 | 521.7 | 586.7 | 578.3 | 544.4 | 599.6 | 385.4 | 346 | 449.1
2739.1 | 2564.1 | 521.7 | 586.9 | 578.6 | 544.6 | 599.9 | 385.5 | 346.1 | 449.1
2740.1 | 2565.1 | 521.7 | 587.1 | 579 | 544.9 | 600 | 385.4 | 346 | 449.1
2741.1 | 2566.1 | 521.8 | 587.3 | 579.2 | 545.1 | 600.2 | 385.4 | 346.1 | 449.2
2742.1 | 2567.1 | 521.8 | 587.5 | 579.4 | 545.4 | 600.5 | 385.4 | 346.1 | 449.2
2743.1 | 2568.1 | 521.8 | 587.6 | 579.7 | 545.6 | 600.8 | 385.5 | 346.1 | 449.2
2744.1 | 2569.1 | 521.8 | 587.8 | 580 | 545.9 | 601.1 | 385.6 | 346.2 | 449.2
2745.1 | 2570.1 | 521.8 | 588 | 580.2 | 546.1 | 601.5 | 385.7 | 346.1 | 449.2
2746.1 | 2571.1 | 521.9 | 588.2 | 580.5 | 546.3 | 601.8 | 385.7 | 346.1 | 449.3
2747.1 | 2572.1 | 521.9 | 588.3 | 580.8 | 546.5 | 601.9 | 385.8 | 346.1 | 449.3
2748.1 | 2573.1 | 522 | 588.5 | 581.1 | 546.6 | 602 | 385.8 | 346.2 | 449.4
2749.1 | 2574.1 | 522.2 | 588.6 | 581.4 | 546.8 | 602 | 386 | 346.3 | 449.5
2750.1 | 2575.1 | 522.5 | 588.8 | 581.8 | 546.9 | 602 | 386 | 346.2 | 449.6
2751.1 | 2576.1 | 522.7 | 589 | 582.2 | 547.1 | 602.2 | 386.1 | 346.2 | 449.6
2752.1 | 2577.1 | 522.8 | 589.3 | 582.5 | 547.3 | 602.7 | 386.3 | 346.2 | 449.7
2753.1 | 2578.1 | 522.7 | 589.6 | 582.9 | 547.5 | 603 | 386.4 | 346.2 | 449.8
2754.1 | 2579.1 | 522.3 | 589.8 | 583.3 | 547.6 | 603.1 | 386.5 | 346.2 | 449.8
2755.1 | 2580.1 | 522.3 | 590.1 | 583.7 | 547.9 | 603.3 | 386.5 | 346.3 | 449.8
2756.1 | 2581.1 | 522.2 | 590.4 | 584.1 | 548.1 | 603.6 | 386.4 | 346.3 | 449.8
2757.1 | 2582.1 | 522.3 | 590.7 | 584.5 | 548.3 | 604.1 | 386.3 | 346.3 | 449.8
2758.1 | 2583.1 | 522.5 | 590.9 | 584.9 | 548.5 | 604.5 | 386.1 | 346.3 | 449.9
2759.1 | 2584.1 | 522.6 | 591.1 | 585.2 | 548.7 | 605.1 | 385.9 | 346.2 | 449.8
2760.1 | 2585.1 | 522.8 | 591.4 | 585.6 | 548.8 | 605.6 | 385.9 | 346.2 | 449.7
2761.1 | 2586.1 | 522.8 | 591.6 | 586.1 | 549 | 605.9 | 385.9 | 346.2 | 449.7
2762.1 | 2587.1 | 522.9 | 591.8 | 586.5 | 549.2 | 606.3 | 385.9 | 346.3 | 449.7
2763.1 | 2588.1 | 523.1 | 592.1 | 586.9 | 549.4 | 606.6 | 385.9 | 346.3 | 449.7
2764.1 | 2589.1 | 522.8 | 592.2 | 587.2 | 549.5 | 606.6 | 385.9 | 346.3 | 449.7
2765.1 | 2590.1 | 522.6 | 592.3 | 587.6 | 549.7 | 606.6 | 385.9 | 346.4 | 449.6
2766.1 | 2591.1 | 522.5 | 592.3 | 587.9 | 549.9 | 606.6 | 386 | 346.4 | 449.6
2767.1 | 2592.1 | 522.5 | 592.3 | 588.2 | 550.1 | 606.6 | 386 | 346.6 | 449.6
2768.1 | 2593.1 | 522.5 | 592.3 | 588.6 | 550.3 | 606.6 | 386.1 | 346.6 | 449.7
2769.1 | 2594.1 | 522.5 | 592.6 | 588.9 | 550.5 | 606.8 | 386.1 | 346.5 | 449.7
2770.1 | 2595.1 | 522.4 | 592.8 | 589.3 | 550.7 | 606.9 | 386.2 | 346.6 | 449.8
2771.1 | 2596.1 | 522.2 | 593.1 | 589.7 | 550.9 | 607.2 | 386.2 | 346.6 | 449.9
2772.1 | 2597.1 | 522.1 | 593.3 | 590.1 | 551.1 | 607.6 | 386.4 | 346.6 | 450
2773.1 | 2598.1 | 522.1 | 593.5 | 590.5 | 551.3 | 608.2 | 386.5 | 346.7 | 450
2774.1 | 2599.1 | 521.8 | 593.7 | 591 | 551.5 | 608.8 | 386.6 | 346.7 | 450
2775.1 | 2600.1 | 521.9 | 593.8 | 591.4 | 551.7 | 609.2 | 386.6 | 346.7 | 449.8
2776.1 | 2601.1 | 522.1 | 594.1 | 591.8 | 551.9 | 609.8 | 386.7 | 346.8 | 449.8
2777.1 | 2602.1 | 522.2 | 594.5 | 592.2 | 552.1 | 610.3 | 386.8 | 346.9 | 449.7
2778.1 | 2603.1 | 522.4 | 594.9 | 592.7 | 552.2 | 610.7 | 386.9 | 347 | 449.8
2779.1 | 2604.1 | 522.3 | 595.2 | 593.2 | 552.4 | 611 | 386.9 | 346.9 | 449.6
2780.1 | 2605.1 | 522.1 | 595.5 | 593.6 | 552.6 | 611.2 | 386.9 | 346.9 | 449.5
2781.1 | 2606.1 | 522 | 595.8 | 594 | 552.8 | 611.2 | 386.9 | 347 | 449.6
2782.1 | 2607.1 | 521.9 | 596.1 | 594.5 | 553 | 611.3 | 387 | 347 | 449.5
2783.1 | 2608.1 | 522.1 | 596.4 | 594.9 | 553.2 | 611.5 | 387 | 346.9 | 449.5
2784.1 | 2609.1 | 522.1 | 596.6 | 595.2 | 553.5 | 611.8 | 386.7 | 347.1 | 449.5
2785.1 | 2610.1 | 522.3 | 596.8 | 595.6 | 553.7 | 612 | 386.6 | 347 | 449.6
2786.1 | 2611.1 | 522.3 | 597.2 | 596.1 | 553.9 | 612.3 | 386.6 | 347 | 449.6
2787.1 | 2612.1 | 522.2 | 597.5 | 596.4 | 554.2 | 612.5 | 386.6 | 347 | 449.5
2788.1 | 2613.1 | 522.1 | 597.6 | 596.8 | 554.4 | 612.5 | 386.5 | 347 | 449.4
2789.1 | 2614.1 | 522.3 | 597.6 | 597.2 | 554.6 | 612.6 | 386.3 | 347 | 449.5
2790.1 | 2615.1 | 522.6 | 597.7 | 597.6 | 554.9 | 612.6 | 386.1 | 347 | 449.5
2791.1 | 2616.1 | 522.7 | 597.8 | 598.1 | 555.1 | 612.7 | 386 | 347 | 449.5
2792.1 | 2617.1 | 522.7 | 598 | 598.5 | 555.3 | 612.9 | 385.8 | 346.9 | 449.6
2793.1 | 2618.1 | 522.6 | 598.3 | 598.9 | 555.6 | 613 | 385.8 | 346.9 | 449.7
2794.1 | 2619.1 | 522.6 | 598.6 | 599.3 | 555.9 | 613.2 | 385.8 | 347 | 449.8
2795.1 | 2620.1 | 522.7 | 598.9 | 599.8 | 556.1 | 613.4 | 385.9 | 347 | 449.8
2796.1 | 2621.1 | 522.8 | 599 | 600.3 | 556.4 | 613.4 | 386 | 347.1 | 449.8
2797.1 | 2622.1 | 522.8 | 599.2 | 600.7 | 556.6 | 613.5 | 386.1 | 347.1 | 449.8
2798.1 | 2623.1 | 522.7 | 599.4 | 601.1 | 556.9 | 613.6 | 386.1 | 347.1 | 449.7
2799.1 | 2624.1 | 522.7 | 599.6 | 601.7 | 557.1 | 613.5 | 386.1 | 347.1 | 449.8
2800.1 | 2625.1 | 522.8 | 599.7 | 602.2 | 557.3 | 613.5 | 385.9 | 347.1 | 449.9
2801.1 | 2626.1 | 522.8 | 600 | 602.7 | 557.6 | 613.6 | 385.8 | 347.1 | 449.9
2802.1 | 2627.1 | 522.6 | 600.1 | 603.4 | 557.8 | 613.6 | 385.5 | 347.1 | 449.9
2803.1 | 2628.1 | 522.4 | 600.4 | 604 | 558.1 | 613.8 | 385.4 | 347.3 | 449.8
2804.1 | 2629.1 | 522.3 | 600.9 | 604.5 | 558.4 | 614 | 385.4 | 347.3 | 449.8
2805.1 | 2630.1 | 522.2 | 601.4 | 604.9 | 558.7 | 614.1 | 385.4 | 347.3 | 449.7
2806.1 | 2631.1 | 522.2 | 601.6 | 605.3 | 559 | 614.3 | 385.4 | 347.4 | 449.8
2807.1 | 2632.1 | 522.3 | 601.8 | 605.8 | 559.2 | 614.2 | 385.4 | 347.3 | 449.9
2808.1 | 2633.1 | 522.3 | 602.1 | 606.1 | 559.6 | 614.2 | 385.5 | 347.3 | 449.9
2809.1 | 2634.1 | 522.2 | 602.4 | 606.6 | 559.9 | 614.2 | 385.5 | 347.4 | 449.9
2810.1 | 2635.1 | 522.3 | 602.7 | 607.3 | 560.1 | 614.3 | 385.5 | 347.4 | 450
2811.1 | 2636.1 | 522.1 | 603 | 607.7 | 560.4 | 614.5 | 385.5 | 347.4 | 450
2812.1 | 2637.1 | 522 | 603.4 | 608.1 | 560.7 | 614.6 | 385.6 | 347.4 | 450.1
2813.1 | 2638.1 | 522.1 | 603.8 | 608.6 | 561 | 614.5 | 385.7 | 347.5 | 450.2
2814.1 | 2639.1 | 522.1 | 604.2 | 609 | 561.3 | 614.3 | 385.7 | 347.4 | 450.2
2815.1 | 2640.1 | 522.1 | 604.5 | 609.4 | 561.6 | 614.4 | 385.7 | 347.4 | 450.2
2816.1 | 2641.1 | 522.2 | 604.8 | 609.9 | 561.9 | 614.3 | 385.8 | 347.4 | 450.3
2817.1 | 2642.1 | 522.3 | 605.2 | 610.4 | 562.2 | 614.2 | 385.7 | 347.5 | 450.4
2818.1 | 2643.1 | 522.4 | 605.6 | 610.8 | 562.6 | 614.4 | 385.6 | 347.6 | 450.4
2819.1 | 2644.1 | 522.4 | 605.8 | 611.2 | 562.9 | 614.4 | 385.6 | 347.6 | 450.5
2820.1 | 2645.1 | 522.3 | 606.1 | 611.6 | 563.3 | 614.3 | 385.6 | 347.7 | 450.6
2821.1 | 2646.1 | 522.3 | 606.2 | 612 | 563.7 | 614.3 | 385.7 | 347.8 | 450.7
2822.1 | 2647.1 | 522.5 | 606.5 | 612.3 | 564.1 | 614.4 | 385.7 | 347.8 | 450.8
2823.1 | 2648.1 | 522.7 | 606.9 | 612.6 | 564.5 | 614.5 | 385.6 | 347.9 | 451
2824.1 | 2649.1 | 522.8 | 607.1 | 613 | 564.9 | 614.6 | 385.5 | 347.9 | 451.1
2825.1 | 2650.1 | 522.8 | 607.4 | 613.2 | 565.4 | 615.1 | 385.5 | 348 | 451.2
2826.1 | 2651.1 | 522.9 | 607.7 | 613.5 | 565.8 | 615.7 | 385.4 | 348 | 451.3
2827.1 | 2652.1 | 522.8 | 608 | 613.7 | 566.2 | 616.2 | 385.3 | 348 | 451.4
2828.1 | 2653.1 | 522.8 | 608.2 | 613.9 | 566.5 | 616.5 | 385.3 | 348 | 451.5
2829.1 | 2654.1 | 522.9 | 608.7 | 614.1 | 566.9 | 617.1 | 385.3 | 348 | 451.6
2830.1 | 2655.1 | 522.9 | 609 | 614.3 | 567.2 | 617.7 | 385.2 | 348 | 451.7
2831.1 | 2656.1 | 522.9 | 609.2 | 614.6 | 567.4 | 618.1 | 385.1 | 348 | 451.8
2832.1 | 2657.1 | 523 | 609.5 | 614.7 | 567.6 | 618.4 | 385 | 348 | 451.7
2833.1 | 2658.1 | 522.9 | 609.7 | 614.8 | 567.8 | 618.4 | 385 | 348 | 451.8
2834.1 | 2659.1 | 522.6 | 609.8 | 615.1 | 567.9 | 618.1 | 385.1 | 348.1 | 451.9
2835.1 | 2660.1 | 522.5 | 609.9 | 615.3 | 568.1 | 617.6 | 385.1 | 348.1 | 452
2836.1 | 2661.1 | 522.4 | 610.2 | 615.5 | 568.2 | 617.7 | 385.1 | 348.2 | 451.9
2837.1 | 2662.1 | 522.3 | 610.4 | 615.7 | 568.4 | 617.8 | 385.1 | 348.2 | 451.8
2838.1 | 2663.1 | 522.2 | 610.6 | 616.1 | 568.6 | 617.6 | 385.2 | 348.3 | 451.8
2839.1 | 2664.1 | 522.3 | 610.9 | 616.3 | 568.8 | 617.6 | 385.3 | 348.4 | 451.8
2840.1 | 2665.1 | 522.6 | 611.1 | 616.5 | 569.1 | 617.8 | 385.3 | 348.5 | 451.8
2841.1 | 2666.1 | 522.7 | 611.2 | 616.8 | 569.3 | 617.7 | 385.3 | 348.5 | 452
2842.1 | 2667.1 | 522.6 | 611.4 | 617 | 569.6 | 617.4 | 385.3 | 348.4 | 452.1
2843.1 | 2668.1 | 522.5 | 611.5 | 617.2 | 569.9 | 617.5 | 385.3 | 348.4 | 452.1
2844.1 | 2669.1 | 522.4 | 611.6 | 617.4 | 570.1 | 617.5 | 385.3 | 348.5 | 452.1
2845.1 | 2670.1 | 522.3 | 611.6 | 617.7 | 570.3 | 617.3 | 385.3 | 348.5 | 452.1
2846.1 | 2671.1 | 522.2 | 611.8 | 617.9 | 570.6 | 617.2 | 385.4 | 348.5 | 452.2
2847.1 | 2672.1 | 522.2 | 611.9 | 618 | 570.9 | 617.5 | 385.6 | 348.4 | 452.3
2848.1 | 2673.1 | 522 | 612 | 618.2 | 571.2 | 618 | 385.8 | 348.4 | 452.5
2849.1 | 2674.1 | 522.1 | 612.2 | 618.4 | 571.5 | 618.5 | 386 | 348.3 | 452.6
2850.1 | 2675.1 | 522.1 | 612.5 | 618.4 | 571.8 | 619 | 386 | 348.3 | 452.5
2851.1 | 2676.1 | 522.2 | 612.8 | 618.6 | 572 | 619.1 | 386 | 348.3 | 452.6
2852.1 | 2677.1 | 522.1 | 613.2 | 618.8 | 572.3 | 619.1 | 385.9 | 348.4 | 452.6
2853.1 | 2678.1 | 522.2 | 613.6 | 618.9 | 572.5 | 619.5 | 386 | 348.4 | 452.6
2854.1 | 2679.1 | 522.3 | 614 | 619.1 | 572.7 | 619.7 | 386 | 348.4 | 452.5
2855.1 | 2680.1 | 522.5 | 614.3 | 619.3 | 572.9 | 619.7 | 386 | 348.4 | 452.6
2856.1 | 2681.1 | 522.6 | 614.6 | 619.5 | 573.2 | 619.9 | 386 | 348.4 | 452.8
2857.1 | 2682.1 | 522.6 | 614.9 | 619.6 | 573.4 | 620.1 | 386.1 | 348.4 | 452.8
2858.1 | 2683.1 | 522.5 | 615.2 | 619.7 | 573.6 | 620.3 | 386.2 | 348.4 | 452.8
2859.1 | 2684.1 | 522.5 | 615.2 | 619.9 | 573.8 | 620.3 | 386.2 | 348.3 | 452.9
2860.1 | 2685.1 | 522.5 | 615.3 | 620 | 574 | 620.4 | 386.2 | 348.3 | 452.9
2861.1 | 2686.1 | 522.5 | 615.4 | 620.1 | 574.2 | 620.3 | 386.1 | 348.3 | 452.8
2862.1 | 2687.1 | 522.7 | 615.6 | 620.2 | 574.5 | 620.2 | 386 | 348.4 | 452.7
2863.1 | 2688.1 | 522.7 | 615.7 | 620.5 | 574.7 | 620.1 | 386 | 348.4 | 452.7
2864.1 | 2689.1 | 522.6 | 615.9 | 620.6 | 574.9 | 620.2 | 386.1 | 348.4 | 452.7
2865.1 | 2690.1 | 522.6 | 616 | 620.7 | 575.2 | 620.5 | 386.1 | 348.4 | 452.7
2866.1 | 2691.1 | 522.8 | 616 | 620.9 | 575.4 | 620.5 | 386 | 348.4 | 452.8
2867.1 | 2692.1 | 523 | 616.1 | 621 | 575.6 | 620.5 | 385.9 | 348.4 | 452.7
2868.1 | 2693.1 | 522.9 | 616.3 | 621.1 | 575.9 | 620.2 | 385.9 | 348.5 | 452.6
2869.1 | 2694.1 | 522.8 | 616.3 | 621.3 | 576.1 | 619.8 | 385.9 | 348.4 | 452.6
2870.1 | 2695.1 | 522.7 | 616.3 | 621.5 | 576.3 | 619.8 | 385.9 | 348.4 | 452.5
2871.1 | 2696.1 | 522.8 | 616.4 | 621.5 | 576.6 | 620 | 385.9 | 348.4 | 452.6
2872.1 | 2697.1 | 522.9 | 616.6 | 621.7 | 576.9 | 620.1 | 385.9 | 348.4 | 452.6
2873.1 | 2698.1 | 522.9 | 617 | 621.9 | 577.1 | 620.2 | 386.1 | 348.4 | 452.5
2874.1 | 2699.1 | 522.8 | 617.3 | 621.9 | 577.4 | 620.3 | 386.1 | 348.4 | 452.6
2875.1 | 2700.1 | 522.7 | 617.5 | 621.9 | 577.7 | 620.5 | 386.1 | 348.4 | 452.7
2876.1 | 2701.1 | 522.7 | 617.5 | 622 | 578 | 620.5 | 386 | 348.4 | 452.9
2877.1 | 2702.1 | 522.7 | 617.5 | 622 | 578.2 | 620.5 | 386 | 348.3 | 453
2878.1 | 2703.1 | 522.6 | 617.8 | 621.9 | 578.5 | 620.9 | 386 | 348.3 | 453
2879.1 | 2704.1 | 522.4 | 618.1 | 622 | 578.8 | 621.4 | 385.9 | 348.3 | 453
2880.1 | 2705.1 | 522.5 | 618.4 | 622.2 | 579.1 | 621.7 | 385.8 | 348.4 | 453
2881.1 | 2706.1 | 522.5 | 618.7 | 622.2 | 579.3 | 621.9 | 385.9 | 348.4 | 453
2882.1 | 2707.1 | 522.6 | 618.8 | 622.1 | 579.6 | 621.9 | 386 | 348.4 | 453
2883.1 | 2708.1 | 522.5 | 618.7 | 622.3 | 579.9 | 621.8 | 386.1 | 348.4 | 453.1
2884.1 | 2709.1 | 522.4 | 618.7 | 622.5 | 580.2 | 621.5 | 386.1 | 348.5 | 453
2885.1 | 2710.1 | 522.4 | 618.8 | 622.6 | 580.5 | 621.1 | 386 | 348.5 | 453
2886.1 | 2711.1 | 522.4 | 618.9 | 622.7 | 580.8 | 620.6 | 385.9 | 348.5 | 453
2887.1 | 2712.1 | 522.2 | 619.1 | 622.8 | 581.1 | 620 | 386 | 348.5 | 453
2888.1 | 2713.1 | 522.2 | 619.4 | 622.8 | 581.4 | 619.7 | 386 | 348.6 | 452.9
2889.1 | 2714.1 | 522.2 | 619.7 | 622.9 | 581.8 | 619.4 | 386.1 | 348.5 | 453
2890.1 | 2715.1 | 522.1 | 619.9 | 622.9 | 582.2 | 619.3 | 386.2 | 348.5 | 453
2891.1 | 2716.1 | 522.1 | 620.3 | 622.9 | 582.7 | 619.2 | 386.2 | 348.4 | 453
2892.1 | 2717.1 | 522.2 | 620.7 | 622.7 | 583.1 | 619.3 | 386.3 | 348.2 | 453.2
2893.1 | 2718.1 | 522.1 | 620.9 | 622.7 | 583.6 | 619.6 | 386.4 | 348.2 | 453.4
2894.1 | 2719.1 | 521.9 | 621.2 | 622.7 | 584 | 619.8 | 386.4 | 348.2 | 453.5
2895.1 | 2720.1 | 521.7 | 621.4 | 622.5 | 584.4 | 620 | 386.4 | 348.2 | 453.5
2896.1 | 2721.1 | 521.7 | 621.6 | 622.3 | 584.9 | 620.5 | 386.3 | 348.1 | 453.5
2897.1 | 2722.1 | 521.7 | 621.9 | 622.2 | 585.3 | 620.9 | 386.2 | 348 | 453.6
2898.1 | 2723.1 | 521.8 | 622.2 | 622.1 | 585.7 | 621 | 386.1 | 347.9 | 453.6
2899.1 | 2724.1 | 521.9 | 622.6 | 621.9 | 586.1 | 621.2 | 386.1 | 347.9 | 453.7
2900.1 | 2725.1 | 522.3 | 622.9 | 621.8 | 586.4 | 621.3 | 386.1 | 348 | 453.6
2901.1 | 2726.1 | 522.5 | 623.1 | 621.8 | 586.8 | 621.5 | 386.2 | 348 | 453.6
2902.1 | 2727.1 | 522.7 | 623.2 | 621.7 | 587.2 | 621.5 | 386.1 | 348.1 | 453.8
2903.1 | 2728.1 | 522.8 | 623.3 | 621.6 | 587.5 | 621.6 | 386.1 | 348.2 | 454
2904.1 | 2729.1 | 522.9 | 623.5 | 621.4 | 587.8 | 621.6 | 386.1 | 348.2 | 454.2
2905.1 | 2730.1 | 523 | 623.6 | 621.4 | 588.1 | 621.4 | 386 | 348.2 | 454.2
2906.1 | 2731.1 | 523.1 | 623.8 | 621.1 | 588.5 | 621.2 | 385.9 | 348.2 | 454.3
2907.1 | 2732.1 | 523.1 | 624 | 620.9 | 588.9 | 621.1 | 386 | 348.3 | 454.5
2908.1 | 2733.1 | 523.1 | 624.2 | 620.8 | 589.2 | 621.4 | 386 | 348.3 | 454.5
2909.1 | 2734.1 | 523.2 | 624.4 | 620.6 | 589.6 | 621.6 | 386.1 | 348.5 | 454.6
2910.1 | 2735.1 | 523.3 | 624.6 | 620.4 | 590 | 621.8 | 386.2 | 348.5 | 454.6
2911.1 | 2736.1 | 523.5 | 624.7 | 620.3 | 590.4 | 622 | 386.2 | 348.6 | 454.5
2912.1 | 2737.1 | 523.6 | 624.8 | 620.1 | 590.8 | 621.9 | 386.1 | 348.6 | 454.5
2913.1 | 2738.1 | 523.7 | 625.1 | 619.8 | 591.2 | 621.8 | 386.1 | 348.8 | 454.6
2914.1 | 2739.1 | 523.5 | 625.4 | 619.6 | 591.5 | 621.7 | 386.2 | 348.8 | 454.6
2915.1 | 2740.1 | 523.6 | 625.6 | 619.4 | 591.9 | 621.6 | 386.2 | 348.7 | 454.6
2916.1 | 2741.1 | 523.6 | 625.6 | 619.2 | 592.3 | 621.8 | 386.3 | 348.7 | 454.7
2917.1 | 2742.1 | 523.5 | 625.6 | 619 | 592.7 | 621.7 | 386.2 | 348.8 | 454.8
2918.1 | 2743.1 | 523.4 | 625.7 | 618.8 | 593 | 621.3 | 386.2 | 348.8 | 454.9
2919.1 | 2744.1 | 523.5 | 625.9 | 618.7 | 593.4 | 621.2 | 386.2 | 348.8 | 455
2920.1 | 2745.1 | 523.7 | 626.2 | 618.3 | 593.9 | 621.6 | 386.3 | 348.9 | 455.2
2921.1 | 2746.1 | 523.7 | 626.5 | 618.1 | 594.3 | 621.8 | 386.3 | 348.9 | 455.2
2922.1 | 2747.1 | 523.4 | 626.7 | 617.8 | 594.7 | 621.8 | 386.3 | 348.9 | 455.3
2923.1 | 2748.1 | 523.1 | 627.1 | 617.4 | 595.2 | 621.9 | 386.3 | 348.9 | 455.3
2924.1 | 2749.1 | 523.1 | 627.2 | 617.1 | 595.6 | 622.1 | 386.3 | 349 | 455.4
2925.1 | 2750.1 | 523 | 627.4 | 617 | 596 | 622 | 386.2 | 349.1 | 455.5
2926.1 | 2751.1 | 523.1 | 627.6 | 616.8 | 596.5 | 621.9 | 386.2 | 349.1 | 455.7
2927.1 | 2752.1 | 523 | 627.8 | 616.4 | 596.9 | 622 | 386.2 | 349.2 | 455.8
2928.1 | 2753.1 | 523 | 627.9 | 616.2 | 597.4 | 622.2 | 386.3 | 349.4 | 456
2929.1 | 2754.1 | 522.9 | 628.1 | 615.9 | 597.8 | 622.5 | 386.2 | 349.5 | 456.2
2930.1 | 2755.1 | 522.7 | 628.4 | 615.5 | 598.2 | 623 | 386.2 | 349.7 | 456.4
2931.1 | 2756.1 | 522.6 | 628.6 | 615.1 | 598.7 | 623.2 | 386.1 | 349.7 | 456.4
2932.1 | 2757.1 | 522.6 | 628.7 | 614.9 | 599 | 622.8 | 386.1 | 349.7 | 456.5
2933.1 | 2758.1 | 522.5 | 628.9 | 614.7 | 599.4 | 622.5 | 386.1 | 349.7 | 456.6
2934.1 | 2759.1 | 522.1 | 629 | 614.3 | 599.8 | 622.5 | 386.1 | 349.7 | 456.6
2935.1 | 2760.1 | 522 | 629.2 | 614.1 | 600.2 | 622.6 | 386.2 | 349.6 | 456.7
2936.1 | 2761.1 | 522.1 | 629.2 | 613.9 | 600.6 | 622.7 | 386.2 | 349.7 | 456.8
2937.1 | 2762.1 | 522.2 | 629.3 | 613.6 | 601.1 | 623 | 386.1 | 349.8 | 456.9
2938.1 | 2763.1 | 522.2 | 629.4 | 613.2 | 601.6 | 623.4 | 386.1 | 349.8 | 457
2939.1 | 2764.1 | 522.1 | 629.5 | 613 | 602 | 623.6 | 386.2 | 349.7 | 457.1
2940.1 | 2765.1 | 522.2 | 629.6 | 612.8 | 602.5 | 623.9 | 386.2 | 349.7 | 457.1
2941.1 | 2766.1 | 522.1 | 629.6 | 612.5 | 603 | 624.2 | 386.2 | 349.6 | 457
2942.1 | 2767.1 | 521.9 | 629.7 | 612.2 | 603.4 | 624.5 | 386.2 | 349.6 | 457.1
2943.1 | 2768.1 | 522 | 629.6 | 612 | 603.9 | 624.5 | 386.2 | 349.6 | 457.1
2944.1 | 2769.1 | 522.2 | 629.8 | 611.8 | 604.3 | 624.5 | 386.1 | 349.5 | 457.1
2945.1 | 2770.1 | 522.3 | 629.8 | 611.5 | 604.8 | 624.5 | 386 | 349.5 | 457.1
2946.1 | 2771.1 | 522.4 | 629.9 | 611.2 | 605.2 | 624.7 | 386 | 349.5 | 457.2
2947.1 | 2772.1 | 522.6 | 630.1 | 611 | 605.6 | 625 | 386 | 349.5 | 457.3
2948.1 | 2773.1 | 522.7 | 630.5 | 610.7 | 606.1 | 625.5 | 386 | 349.4 | 457.4
2949.1 | 2774.1 | 522.8 | 630.8 | 610.5 | 606.6 | 626.1 | 386 | 349.4 | 457.5
2950.1 | 2775.1 | 522.7 | 630.9 | 610.4 | 607 | 626.5 | 386.1 | 349.4 | 457.6
2951.1 | 2776.1 | 522.7 | 631.1 | 610.1 | 607.4 | 626.6 | 386.1 | 349.5 | 457.6
2952.1 | 2777.1 | 522.8 | 631.2 | 609.8 | 607.9 | 626.3 | 386.2 | 349.5 | 457.5
2953.1 | 2778.1 | 522.8 | 631.2 | 609.7 | 608.3 | 625.9 | 386.3 | 349.7 | 457.5
2954.1 | 2779.1 | 522.7 | 631 | 609.5 | 608.7 | 625.9 | 386.4 | 349.6 | 457.6
2955.1 | 2780.1 | 522.5 | 631.1 | 609.2 | 609.2 | 626.3 | 386.5 | 349.6 | 457.7
2956.1 | 2781.1 | 522.4 | 631 | 609 | 609.7 | 626.1 | 386.6 | 349.6 | 457.8
2957.1 | 2782.1 | 522.3 | 630.8 | 608.9 | 610.1 | 625.9 | 386.6 | 349.6 | 457.8
2958.1 | 2783.1 | 522.2 | 630.7 | 608.8 | 610.5 | 626.1 | 386.6 | 349.7 | 457.8
2959.1 | 2784.1 | 522.3 | 630.6 | 608.6 | 610.9 | 626.3 | 386.7 | 349.9 | 457.7
2960.1 | 2785.1 | 522.5 | 630.7 | 608.5 | 611.3 | 626.2 | 386.8 | 350 | 457.6
2961.1 | 2786.1 | 522.6 | 631 | 608.4 | 611.7 | 626.2 | 387 | 350.1 | 457.6
2962.1 | 2787.1 | 522.4 | 631.1 | 608.1 | 612.2 | 626.6 | 387.2 | 350.1 | 457.6
2963.1 | 2788.1 | 522.6 | 631.1 | 608 | 612.6 | 626.7 | 387.4 | 350.2 | 457.7
2964.1 | 2789.1 | 522.7 | 631 | 607.9 | 613 | 626.6 | 387.5 | 350.1 | 457.8
2965.1 | 2790.1 | 522.9 | 631 | 607.7 | 613.4 | 626.6 | 387.7 | 350.2 | 457.8
2966.1 | 2791.1 | 522.9 | 631.2 | 607.6 | 613.8 | 626.7 | 387.7 | 350.3 | 457.8
2967.1 | 2792.1 | 522.8 | 631.3 | 607.5 | 614.2 | 626.6 | 387.7 | 350.3 | 457.9
2968.1 | 2793.1 | 522.8 | 631.3 | 607.4 | 614.6 | 626.1 | 387.8 | 350.3 | 458
2969.1 | 2794.1 | 522.9 | 631.5 | 607.2 | 615 | 626 | 388 | 350.3 | 458
2970.1 | 2795.1 | 523.2 | 631.5 | 607.1 | 615.3 | 626.1 | 388 | 350.3 | 458
2971.1 | 2796.1 | 523.2 | 631.6 | 607.1 | 615.7 | 626.6 | 388.1 | 350.3 | 458.1
2972.1 | 2797.1 | 523.3 | 631.9 | 607 | 616.1 | 627.2 | 388.1 | 350.3 | 457.8
2973.1 | 2798.1 | 523.5 | 632.1 | 606.9 | 616.5 | 627.7 | 388.1 | 350.3 | 458
2974.1 | 2799.1 | 523.5 | 632 | 606.9 | 616.9 | 627.9 | 388 | 350.4 | 458.2
2975.1 | 2800.1 | 523.4 | 632.2 | 606.9 | 617.3 | 627.5 | 388 | 350.5 | 458.2
2976.1 | 2801.1 | 523.5 | 632.2 | 606.8 | 617.6 | 627.3 | 388 | 350.5 | 458.3
2977.1 | 2802.1 | 523.7 | 632.2 | 606.7 | 617.9 | 627.5 | 388.1 | 350.5 | 458.2
2978.1 | 2803.1 | 523.6 | 632 | 606.8 | 618.3 | 627.4 | 388.1 | 350.5 | 458.1
2979.1 | 2804.1 | 523.4 | 632 | 606.7 | 618.6 | 627.3 | 388.1 | 350.6 | 458
2980.1 | 2805.1 | 523.5 | 632 | 606.6 | 619 | 627.3 | 388.1 | 350.6 | 458.2
2981.1 | 2806.1 | 523.5 | 631.9 | 606.6 | 619.3 | 627 | 388 | 350.7 | 458.2
2982.1 | 2807.1 | 523.4 | 631.9 | 606.6 | 619.6 | 626.8 | 387.9 | 350.8 | 458.1
2983.1 | 2808.1 | 523.3 | 631.7 | 606.5 | 620 | 627 | 387.9 | 350.8 | 458.2
2984.1 | 2809.1 | 523.2 | 631.6 | 606.4 | 620.4 | 627.4 | 388.1 | 350.9 | 458.2
2985.1 | 2810.1 | 523.3 | 631.7 | 606.5 | 620.7 | 627.6 | 388.3 | 350.8 | 458.5
2986.1 | 2811.1 | 523.4 | 631.7 | 606.4 | 621.1 | 627.6 | 388.5 | 350.8 | 458.6
2987.1 | 2812.1 | 523.4 | 631.8 | 606.4 | 621.4 | 627.6 | 388.6 | 350.8 | 458.6
2988.1 | 2813.1 | 523.2 | 631.8 | 606.4 | 621.7 | 627.9 | 388.7 | 350.9 | 458.6
2989.1 | 2814.1 | 523.1 | 631.9 | 606.4 | 622 | 628.2 | 388.7 | 350.9 | 458.7
2990.1 | 2815.1 | 523 | 631.9 | 606.3 | 622.4 | 628.5 | 388.8 | 350.9 | 458.8
2991.1 | 2816.1 | 522.9 | 631.9 | 606.3 | 622.7 | 628.4 | 388.9 | 350.8 | 458.9
2992.1 | 2817.1 | 522.8 | 631.8 | 606.4 | 623 | 628.3 | 389 | 350.8 | 458.9
2993.1 | 2818.1 | 522.7 | 631.8 | 606.4 | 623.2 | 628.4 | 389 | 350.8 | 459
2994.1 | 2819.1 | 522.5 | 631.8 | 606.3 | 623.5 | 628.5 | 389 | 350.8 | 459
2995.1 | 2820.1 | 522.3 | 631.7 | 606.3 | 623.8 | 628.3 | 389 | 350.7 | 459.1
2996.1 | 2821.1 | 522.4 | 631.7 | 606.4 | 624.1 | 628.1 | 388.9 | 350.7 | 459.2
2997.1 | 2822.1 | 522.4 | 631.8 | 606.3 | 624.4 | 628.1 | 388.9 | 350.8 | 459.2
2998.1 | 2823.1 | 522.3 | 631.9 | 606.3 | 624.7 | 628.3 | 388.9 | 350.8 | 459.2
2999.1 | 2824.1 | 522.4 | 631.9 | 606.3 | 624.9 | 628.2 | 388.9 | 350.8 | 459.4
3000.1 | 2825.1 | 522.2 | 631.9 | 606.3 | 625.2 | 628.2 | 388.9 | 350.8 | 459.6
3001.1 | 2826.1 | 522.2 | 631.9 | 606.3 | 625.5 | 628.2 | 389 | 350.8 | 459.7
3002.1 | 2827.1 | 522.2 | 631.9 | 606.3 | 625.9 | 628.3 | 389 | 350.8 | 459.7
3003.1 | 2828.1 | 522.3 | 631.6 | 606.4 | 626.2 | 628.4 | 388.9 | 350.8 | 459.8
3004.1 | 2829.1 | 522.5 | 631.6 | 606.3 | 626.6 | 628.7 | 389 | 350.8 | 459.9
3005.1 | 2830.1 | 522.6 | 631.3 | 606.3 | 627 | 629.1 | 389 | 350.8 | 459.8
3006.1 | 2831.1 | 522.5 | 631.1 | 606.4 | 627.3 | 629.2 | 389 | 350.8 | 459.9
3007.1 | 2832.1 | 522.5 | 631.3 | 606.3 | 627.6 | 629.6 | 389 | 350.8 | 460.1
3008.1 | 2833.1 | 522.5 | 631.5 | 606.3 | 627.9 | 630 | 389.1 | 350.9 | 460.3
3009.1 | 2834.1 | 522.5 | 631.4 | 606.4 | 628.2 | 630.3 | 389.1 | 350.9 | 460.4
3010.1 | 2835.1 | 522.5 | 631.4 | 606.5 | 628.5 | 630.4 | 389.1 | 350.9 | 460.5
3011.1 | 2836.1 | 522.5 | 631.2 | 606.4 | 628.9 | 630.4 | 389.1 | 351 | 460.5
3012.1 | 2837.1 | 522.3 | 631 | 606.5 | 629.2 | 630.6 | 389.2 | 351 | 460.5
3013.1 | 2838.1 | 522.2 | 631 | 606.6 | 629.4 | 630.6 | 389.1 | 350.9 | 460.5
3014.1 | 2839.1 | 521.9 | 630.9 | 606.6 | 629.6 | 630.3 | 389 | 350.8 | 460.5
3015.1 | 2840.1 | 521.7 | 630.9 | 606.6 | 629.8 | 629.9 | 389 | 350.8 | 460.4
3016.1 | 2841.1 | 521.4 | 630.8 | 606.6 | 629.9 | 629.8 | 389 | 350.7 | 460.4
3017.1 | 2842.1 | 521.3 | 630.7 | 606.8 | 630.1 | 629.9 | 389 | 350.6 | 460.5
3018.1 | 2843.1 | 521.3 | 630.7 | 606.7 | 630.5 | 630.4 | 389 | 350.5 | 460.5
3019.1 | 2844.1 | 521.1 | 630.7 | 606.7 | 630.8 | 630.3 | 389 | 350.4 | 460.6
3020.1 | 2845.1 | 521 | 630.5 | 606.8 | 631.1 | 630.4 | 388.8 | 350.4 | 460.6
3021.1 | 2846.1 | 521 | 630.3 | 606.8 | 631.4 | 630.5 | 388.7 | 350.3 | 460.6
3022.1 | 2847.1 | 521 | 630.3 | 606.9 | 631.6 | 630.3 | 388.6 | 350.3 | 460.6
3023.1 | 2848.1 | 521.3 | 630.1 | 606.9 | 631.9 | 630.5 | 388.6 | 350.3 | 460.5
3024.1 | 2849.1 | 521.4 | 630 | 607 | 632.2 | 630.3 | 388.6 | 350.3 | 460.5
3025.1 | 2850.1 | 521.7 | 630 | 607 | 632.5 | 630.6 | 388.6 | 350.2 | 460.6
3026.1 | 2851.1 | 521.8 | 630.1 | 607 | 632.8 | 631 | 388.7 | 350.2 | 460.7
3027.1 | 2852.1 | 521.9 | 630.1 | 607.1 | 633.1 | 631 | 388.7 | 350.3 | 460.8
3028.1 | 2853.1 | 522 | 630.1 | 607.2 | 633.4 | 630.9 | 388.7 | 350.3 | 460.8
3029.1 | 2854.1 | 522.1 | 630.1 | 607.2 | 633.6 | 630.7 | 388.7 | 350.4 | 460.7
3030.1 | 2855.1 | 522.3 | 630 | 607.3 | 633.8 | 630.5 | 388.9 | 350.4 | 460.8
3031.1 | 2856.1 | 522.4 | 629.9 | 607.4 | 634 | 630.7 | 389 | 350.5 | 460.8
3032.1 | 2857.1 | 522.6 | 629.8 | 607.4 | 634.4 | 630.9 | 388.9 | 350.5 | 460.9
3033.1 | 2858.1 | 522.6 | 629.7 | 607.4 | 634.6 | 631 | 389 | 350.6 | 461
3034.1 | 2859.1 | 522.4 | 629.5 | 607.6 | 634.9 | 630.9 | 389 | 350.6 | 461
3035.1 | 2860.1 | 522.4 | 629.4 | 607.6 | 635.2 | 630.9 | 389.1 | 350.6 | 461.1
3036.1 | 2861.1 | 522.4 | 629.4 | 607.6 | 635.4 | 631 | 389.2 | 350.6 | 461.2
3037.1 | 2862.1 | 522.5 | 629.3 | 607.7 | 635.7 | 631 | 389.3 | 350.7 | 461.3
3038.1 | 2863.1 | 522.7 | 629.2 | 607.8 | 636 | 631.1 | 389.4 | 350.8 | 461.5
3039.1 | 2864.1 | 522.9 | 629 | 607.8 | 636.4 | 631.5 | 389.4 | 350.8 | 461.6
3040.1 | 2865.1 | 522.9 | 629 | 607.9 | 636.7 | 632 | 389.4 | 350.9 | 461.8
3041.1 | 2866.1 | 523.1 | 629.1 | 608 | 637 | 632.3 | 389.4 | 350.9 | 461.9
3042.1 | 2867.1 | 523.2 | 629.2 | 608 | 637.3 | 632.8 | 389.6 | 351 | 462
3043.1 | 2868.1 | 523.3 | 629.2 | 608.1 | 637.6 | 633 | 389.6 | 351.1 | 461.9
3044.1 | 2869.1 | 523.3 | 629.1 | 608.2 | 637.9 | 632.9 | 389.6 | 351.1 | 461.8
3045.1 | 2870.1 | 523.3 | 628.9 | 608.3 | 638.1 | 632.7 | 389.5 | 351.1 | 461.9
3046.1 | 2871.1 | 523.4 | 628.8 | 608.3 | 638.4 | 632.8 | 389.5 | 351.1 | 461.9
3047.1 | 2872.1 | 523.5 | 628.6 | 608.4 | 638.7 | 633 | 389.4 | 351.2 | 462
3048.1 | 2873.1 | 523.5 | 628.5 | 608.5 | 639 | 633.3 | 389.4 | 351.2 | 462.1
3049.1 | 2874.1 | 523.5 | 628.5 | 608.6 | 639.3 | 633.6 | 389.4 | 351.3 | 462.2
3050.1 | 2875.1 | 523.4 | 628.4 | 608.6 | 639.5 | 633.8 | 389.3 | 351.3 | 462.1
3051.1 | 2876.1 | 523.4 | 628.4 | 608.8 | 639.7 | 633.9 | 389.3 | 351.5 | 462.1
3052.1 | 2877.1 | 523.4 | 628.3 | 608.9 | 639.9 | 634 | 389.3 | 351.6 | 461.9
3053.1 | 2878.1 | 523.4 | 628.1 | 609 | 640.2 | 634 | 389.3 | 351.6 | 461.9
3054.1 | 2879.1 | 523.2 | 628 | 609.1 | 640.4 | 633.9 | 389.1 | 351.6 | 461.9
3055.1 | 2880.1 | 523 | 627.9 | 609.2 | 640.7 | 633.8 | 389 | 351.5 | 461.8
3056.1 | 2881.1 | 522.9 | 627.9 | 609.3 | 641 | 633.9 | 389 | 351.6 | 461.9
3057.1 | 2882.1 | 522.7 | 627.9 | 609.3 | 641.3 | 634.1 | 389 | 351.7 | 461.9
3058.1 | 2883.1 | 522.5 | 627.8 | 609.4 | 641.5 | 634 | 389.1 | 351.6 | 461.9
3059.1 | 2884.1 | 522.3 | 627.6 | 609.6 | 641.7 | 633.9 | 389.1 | 351.6 | 462
3060.1 | 2885.1 | 522.2 | 627.4 | 609.6 | 642 | 633.9 | 389.1 | 351.6 | 461.9
3061.1 | 2886.1 | 522.2 | 627.3 | 609.7 | 642.2 | 633.4 | 389.1 | 351.7 | 461.8
3062.1 | 2887.1 | 522.3 | 627.2 | 609.8 | 642.3 | 632.8 | 389 | 351.7 | 461.8
3063.1 | 2888.1 | 522.3 | 627.1 | 609.9 | 642.5 | 632.5 | 388.9 | 351.8 | 461.8
3064.1 | 2889.1 | 522.2 | 627 | 610 | 642.7 | 632.6 | 388.9 | 351.8 | 461.8
3065.1 | 2890.1 | 522.1 | 627 | 610.1 | 642.9 | 632.7 | 389 | 351.8 | 461.9
3066.1 | 2891.1 | 522 | 626.9 | 610.2 | 643.1 | 632.9 | 388.9 | 351.8 | 461.9
3067.1 | 2892.1 | 521.9 | 626.9 | 610.3 | 643.4 | 633.2 | 388.9 | 351.8 | 461.9
3068.1 | 2893.1 | 522 | 626.9 | 610.3 | 643.7 | 633.2 | 389 | 351.7 | 462
3069.1 | 2894.1 | 522.1 | 626.8 | 610.5 | 643.8 | 633.2 | 389.2 | 351.7 | 462
3070.1 | 2895.1 | 522.1 | 626.8 | 610.5 | 644 | 633.5 | 389.4 | 351.7 | 462
3071.1 | 2896.1 | 522.1 | 626.8 | 610.5 | 644.2 | 634 | 389.7 | 351.7 | 462
3072.1 | 2897.1 | 522 | 626.7 | 610.6 | 644.5 | 634.3 | 389.8 | 351.7 | 462.1
3073.1 | 2898.1 | 522.1 | 626.6 | 610.6 | 644.8 | 634.3 | 389.8 | 351.6 | 462.1
3074.1 | 2899.1 | 522.3 | 626.4 | 610.6 | 645.1 | 634.2 | 389.9 | 351.6 | 462.1
3075.1 | 2900.1 | 522.4 | 626.3 | 610.7 | 645.3 | 634.2 | 390.1 | 351.8 | 462.1
3076.1 | 2901.1 | 522.5 | 626 | 610.9 | 645.4 | 634.2 | 390.2 | 351.8 | 462.1
3077.1 | 2902.1 | 522.6 | 625.8 | 610.9 | 645.6 | 634.3 | 390.2 | 351.8 | 462.1
3078.1 | 2903.1 | 522.7 | 625.7 | 611 | 645.9 | 634.3 | 390.1 | 352 | 462.2
3079.1 | 2904.1 | 522.7 | 625.7 | 611.1 | 646.1 | 634.3 | 390.1 | 352 | 462.3
3080.1 | 2905.1 | 522.7 | 625.8 | 611.3 | 646.3 | 634.5 | 390 | 352 | 462.3
3081.1 | 2906.1 | 522.9 | 625.8 | 611.3 | 646.6 | 635 | 390 | 352 | 462.4
3082.1 | 2907.1 | 523.1 | 625.7 | 611.4 | 646.8 | 635.1 | 390 | 352 | 462.4
3083.1 | 2908.1 | 523.3 | 625.5 | 611.6 | 647 | 635 | 389.9 | 352.1 | 462.4
3084.1 | 2909.1 | 523.4 | 625.2 | 611.7 | 647.2 | 635.1 | 389.7 | 352.1 | 462.4
3085.1 | 2910.1 | 523.7 | 625 | 611.8 | 647.4 | 635.2 | 389.7 | 352.1 | 462.4
3086.1 | 2911.1 | 523.8 | 624.8 | 611.9 | 647.6 | 635.2 | 389.7 | 352.1 | 462.4
3087.1 | 2912.1 | 524 | 624.6 | 612.1 | 647.8 | 635.1 | 389.7 | 352.1 | 462.5
3088.1 | 2913.1 | 523.9 | 624.5 | 612.2 | 648.1 | 635.2 | 389.7 | 352.1 | 462.5
3089.1 | 2914.1 | 523.9 | 624.4 | 612.3 | 648.3 | 635.5 | 389.6 | 352.1 | 462.6
3090.1 | 2915.1 | 523.8 | 624.3 | 612.5 | 648.5 | 635.8 | 389.6 | 352.1 | 462.7
3091.1 | 2916.1 | 523.6 | 624.3 | 612.6 | 648.8 | 636.1 | 389.7 | 352.1 | 462.7
3092.1 | 2917.1 | 523.4 | 624.3 | 612.7 | 649 | 636.3 | 389.7 | 352.1 | 462.8
3093.1 | 2918.1 | 523.5 | 624.1 | 612.8 | 649.2 | 636.3 | 389.7 | 352.2 | 462.7
3094.1 | 2919.1 | 523.6 | 623.8 | 612.9 | 649.3 | 636.1 | 389.7 | 352.2 | 462.7
3095.1 | 2920.1 | 523.9 | 623.6 | 613 | 649.5 | 635.8 | 389.7 | 352.2 | 462.8
3096.1 | 2921.1 | 524 | 623.4 | 613 | 649.6 | 635.6 | 389.7 | 352.2 | 462.8
3097.1 | 2922.1 | 524 | 623.2 | 613.2 | 649.8 | 635.7 | 389.8 | 352.2 | 462.9
3098.1 | 2923.1 | 524.1 | 623 | 613.2 | 650 | 635.7 | 389.9 | 352.1 | 462.8
3099.1 | 2924.1 | 524.1 | 622.8 | 613.3 | 650.3 | 635.7 | 389.9 | 352.1 | 462.7
3100.1 | 2925.1 | 523.9 | 622.6 | 613.5 | 650.5 | 635.7 | 390 | 352.1 | 462.6
3101.1 | 2926.1 | 523.8 | 622.5 | 613.6 | 650.8 | 635.8 | 390.1 | 352.2 | 462.4
3102.1 | 2927.1 | 523.7 | 622.4 | 613.7 | 651.1 | 635.9 | 390.2 | 352 | 462.5
3103.1 | 2928.1 | 523.6 | 622.3 | 613.8 | 651.4 | 635.9 | 390.3 | 352.1 | 462.6
3104.1 | 2929.1 | 523.7 | 622.2 | 613.9 | 651.6 | 636 | 390.3 | 352.1 | 462.6
3105.1 | 2930.1 | 523.5 | 622.2 | 614 | 651.9 | 636.1 | 390.4 | 352.1 | 462.7
3106.1 | 2931.1 | 523.6 | 622.2 | 614.1 | 652.1 | 636.1 | 390.5 | 352.1 | 462.7
3107.1 | 2932.1 | 523.5 | 622.2 | 614.3 | 652.2 | 636 | 390.6 | 352.2 | 462.8
3108.1 | 2933.1 | 523.5 | 622.2 | 614.5 | 652.4 | 636.1 | 390.6 | 352.3 | 462.9
3109.1 | 2934.1 | 523.5 | 622.2 | 614.5 | 652.6 | 636.4 | 390.6 | 352.3 | 463
3110.1 | 2935.1 | 523.5 | 622.3 | 614.6 | 652.8 | 636.7 | 390.7 | 352.4 | 463.1
3111.1 | 2936.1 | 523.6 | 622.3 | 614.8 | 653 | 636.6 | 390.8 | 352.3 | 463.1
3112.1 | 2937.1 | 523.6 | 622.4 | 614.9 | 653.2 | 636.9 | 390.8 | 352.3 | 463.2
3113.1 | 2938.1 | 523.5 | 622.4 | 615 | 653.5 | 637.1 | 390.9 | 352.4 | 463.2
3114.1 | 2939.1 | 523.5 | 622.3 | 615.2 | 653.7 | 637.3 | 391 | 352.5 | 463.2
3115.1 | 2940.1 | 523.8 | 622.2 | 615.3 | 653.9 | 637.4 | 391.1 | 352.5 | 463.3
3116.1 | 2941.1 | 523.7 | 622.3 | 615.4 | 654.2 | 637.5 | 391.1 | 352.5 | 463.4
3117.1 | 2942.1 | 523.8 | 622.3 | 615.5 | 654.4 | 637.4 | 390.9 | 352.5 | 463.5
3118.1 | 2943.1 | 523.7 | 622.2 | 615.7 | 654.5 | 637.1 | 390.7 | 352.5 | 463.3
3119.1 | 2944.1 | 523.5 | 622.2 | 615.8 | 654.7 | 637.2 | 390.7 | 352.4 | 463.2
3120.1 | 2945.1 | 523.6 | 622.3 | 615.9 | 654.9 | 637.4 | 390.7 | 352.5 | 463
3121.1 | 2946.1 | 523.4 | 622.3 | 616 | 655.2 | 637.6 | 390.7 | 352.5 | 463.1
3122.1 | 2947.1 | 523.3 | 622.3 | 616.1 | 655.4 | 637.7 | 390.7 | 352.5 | 463.1
3123.1 | 2948.1 | 523.3 | 622.3 | 616.2 | 655.7 | 637.7 | 390.6 | 352.5 | 463.1
3124.1 | 2949.1 | 523.2 | 622.4 | 616.2 | 655.9 | 637.4 | 390.3 | 352.5 | 463
3125.1 | 2950.1 | 523.1 | 622.3 | 616.4 | 656 | 637.2 | 390.3 | 352.5 | 463.1
3126.1 | 2951.1 | 523 | 622.3 | 616.5 | 656.1 | 637.3 | 390.2 | 352.5 | 463
3127.1 | 2952.1 | 523 | 622.3 | 616.6 | 656.3 | 637.8 | 390.1 | 352.5 | 463
3128.1 | 2953.1 | 523.1 | 622.2 | 616.7 | 656.5 | 638 | 390 | 352.5 | 462.9
3129.1 | 2954.1 | 523.3 | 622.1 | 616.9 | 656.6 | 638 | 389.9 | 352.5 | 462.9
3130.1 | 2955.1 | 523.3 | 622 | 616.9 | 656.7 | 638 | 389.9 | 352.6 | 462.8
3131.1 | 2956.1 | 523.2 | 621.9 | 617 | 656.9 | 638 | 389.9 | 352.6 | 462.8
3132.1 | 2957.1 | 523 | 621.8 | 617.2 | 657.1 | 638.2 | 390 | 352.7 | 462.8
3133.1 | 2958.1 | 522.8 | 621.7 | 617.2 | 657.3 | 638.5 | 390.1 | 352.8 | 462.7
3134.1 | 2959.1 | 522.6 | 621.7 | 617.3 | 657.5 | 638.7 | 390.1 | 352.9 | 462.4
3135.1 | 2960.1 | 522.6 | 621.6 | 617.4 | 657.8 | 639 | 390.2 | 352.9 | 462.2
3136.1 | 2961.1 | 522.8 | 621.6 | 617.5 | 658 | 639 | 390.3 | 352.9 | 462.2
3137.1 | 2962.1 | 522.9 | 621.6 | 617.5 | 658.2 | 639.1 | 390.4 | 352.9 | 462.2
3138.1 | 2963.1 | 522.9 | 621.5 | 617.6 | 658.3 | 639 | 390.4 | 353 | 462.1
3139.1 | 2964.1 | 522.9 | 621.5 | 617.7 | 658.4 | 638.9 | 390.4 | 353 | 462
3140.1 | 2965.1 | 523 | 621.4 | 617.8 | 658.6 | 638.9 | 390.4 | 353 | 461.9
3141.1 | 2966.1 | 523.1 | 621.3 | 617.9 | 658.8 | 639 | 390.5 | 353 | 461.8
3142.1 | 2967.1 | 523 | 621.3 | 618 | 659 | 639 | 390.4 | 353 | 461.9
3143.1 | 2968.1 | 523 | 621.2 | 618.1 | 659.2 | 639 | 390.4 | 353.1 | 461.8
3144.1 | 2969.1 | 522.8 | 621.2 | 618.1 | 659.4 | 639 | 390.4 | 353.1 | 461.7
3145.1 | 2970.1 | 522.7 | 621.2 | 618.2 | 659.6 | 639 | 390.4 | 353.2 | 461.6
3146.1 | 2971.1 | 522.7 | 621.1 | 618.4 | 659.8 | 638.9 | 390.5 | 353.2 | 461.5
3147.1 | 2972.1 | 522.5 | 621 | 618.4 | 659.9 | 638.8 | 390.5 | 353.1 | 461.3
3148.1 | 2973.1 | 522.5 | 621 | 618.4 | 660.2 | 638.9 | 390.7 | 353.1 | 461.2
3149.1 | 2974.1 | 522.7 | 621 | 618.6 | 660.3 | 638.9 | 390.8 | 353 | 461.2
3150.1 | 2975.1 | 522.7 | 620.9 | 618.7 | 660.5 | 638.7 | 390.9 | 353.1 | 461.2
3151.1 | 2976.1 | 522.5 | 620.9 | 618.7 | 660.6 | 638.4 | 391 | 353.1 | 461.3
3152.1 | 2977.1 | 522.4 | 620.8 | 618.8 | 660.7 | 638.4 | 391.2 | 353.1 | 461.3
3153.1 | 2978.1 | 522.3 | 620.8 | 619 | 660.8 | 638.3 | 391.3 | 353.1 | 461.5
3154.1 | 2979.1 | 522.3 | 620.8 | 619.1 | 661 | 638.5 | 391.5 | 353.1 | 461.5
3155.1 | 2980.1 | 522.5 | 620.8 | 619.1 | 661.2 | 638.8 | 391.6 | 353.1 | 461.7
3156.1 | 2981.1 | 522.5 | 620.8 | 619.2 | 661.5 | 639 | 391.7 | 353.2 | 461.8
3157.1 | 2982.1 | 522.6 | 620.7 | 619.4 | 661.9 | 639 | 391.9 | 353.2 | 461.9
3158.1 | 2983.1 | 522.5 | 620.7 | 619.4 | 662.2 | 639.3 | 392 | 353.2 | 461.9
3159.1 | 2984.1 | 522.3 | 620.7 | 619.5 | 662.6 | 639.4 | 392.3 | 353.2 | 461.6
3160.1 | 2985.1 | 522.2 | 620.6 | 619.7 | 662.9 | 639.6 | 392.4 | 353.1 | 461.7
3161.1 | 2986.1 | 522.3 | 620.5 | 619.8 | 663.2 | 640 | 392.4 | 353.1 | 461.8
3162.1 | 2987.1 | 522.4 | 620.4 | 619.8 | 663.4 | 640.3 | 392.4 | 353.1 | 461.7
3163.1 | 2988.1 | 522 | 620.2 | 620 | 663.6 | 640.3 | 392.5 | 352.9 | 461.8
3164.1 | 2989.1 | 521.6 | 620.1 | 620.1 | 663.7 | 640.4 | 392.6 | 352.8 | 461.8
3165.1 | 2990.1 | 521.7 | 620 | 620.1 | 663.9 | 640.5 | 392.7 | 352.7 | 461.8
3166.1 | 2991.1 | 521.7 | 619.9 | 620.2 | 664.1 | 640.4 | 392.8 | 352.7 | 461.7
3167.1 | 2992.1 | 521.8 | 619.7 | 620.4 | 664.2 | 640.2 | 393 | 352.7 | 461.7
3168.1 | 2993.1 | 521.8 | 619.6 | 620.5 | 664.4 | 640 | 393.1 | 352.8 | 461.6
3169.1 | 2994.1 | 521.7 | 619.6 | 620.5 | 664.7 | 639.8 | 393 | 352.7 | 461.4
3170.1 | 2995.1 | 521.8 | 619.5 | 620.7 | 664.8 | 639.5 | 393.1 | 352.7 | 461.2
3171.1 | 2996.1 | 521.7 | 619.5 | 620.8 | 664.9 | 639 | 393.3 | 352.6 | 461.3
3172.1 | 2997.1 | 521.7 | 619.5 | 620.9 | 665.1 | 638.9 | 393.5 | 352.6 | 461.4
3173.1 | 2998.1 | 521.8 | 619.5 | 621 | 665.2 | 638.8 | 393.6 | 352.7 | 461.4
3174.1 | 2999.1 | 521.8 | 619.5 | 621.2 | 665.2 | 638.8 | 393.7 | 352.7 | 461.4
3175.1 | 3000.1 | 521.8 | 619.5 | 621.3 | 665.3 | 639 | 393.8 | 352.6 | 461.4
3176.1 | 3001.1 | 521.9 | 619.5 | 621.4 | 665.5 | 639.3 | 394 | 352.5 | 461.5
3177.1 | 3002.1 | 521.9 | 619.5 | 621.6 | 665.7 | 639.6 | 394 | 352.5 | 461.5
3178.1 | 3003.1 | 522 | 619.5 | 621.7 | 666 | 639.8 | 394.1 | 352.5 | 461.4
3179.1 | 3004.1 | 522 | 619.6 | 621.7 | 666.3 | 640.1 | 394.2 | 352.6 | 461.3
3180.1 | 3005.1 | 522.4 | 619.6 | 621.9 | 666.6 | 640.2 | 394.2 | 352.6 | 461.2
3181.1 | 3006.1 | 522.6 | 619.5 | 622.1 | 666.8 | 640.4 | 394.1 | 352.6 | 461.2
3182.1 | 3007.1 | 522.7 | 619.5 | 622.2 | 667 | 640.7 | 394.1 | 352.6 | 461.3
3183.1 | 3008.1 | 522.8 | 619.5 | 622.2 | 667.2 | 640.9 | 394.2 | 352.6 | 461.1
3184.1 | 3009.1 | 523 | 619.4 | 622.4 | 667.4 | 641.1 | 394.3 | 352.5 | 461.1
3185.1 | 3010.1 | 523.2 | 619.3 | 622.5 | 667.5 | 641 | 394.4 | 352.6 | 461.1
3186.1 | 3011.1 | 523.2 | 619.3 | 622.6 | 667.6 | 641 | 394.4 | 352.7 | 461.1
3187.1 | 3012.1 | 523 | 619.2 | 622.7 | 667.7 | 640.9 | 394.4 | 352.9 | 461
3188.1 | 3013.1 | 522.9 | 619 | 622.8 | 667.7 | 640.5 | 394.4 | 352.9 | 461
3189.1 | 3014.1 | 522.8 | 619 | 622.9 | 667.8 | 640.2 | 394.4 | 352.9 | 460.8
3190.1 | 3015.1 | 522.6 | 618.9 | 622.9 | 667.9 | 640 | 394.4 | 353 | 460.7
3191.1 | 3016.1 | 522.7 | 618.9 | 623 | 668 | 639.8 | 394.4 | 353.1 | 460.7
3192.1 | 3017.1 | 523 | 618.9 | 623.1 | 668.1 | 639.6 | 394.5 | 353.2 | 460.8
3193.1 | 3018.1 | 523.2 | 619 | 623.2 | 668.2 | 639.6 | 394.6 | 353.2 | 460.8
3194.1 | 3019.1 | 523.5 | 619 | 623.3 | 668.3 | 639.7 | 394.7 | 353.3 | 460.9
3195.1 | 3020.1 | 523.5 | 619 | 623.4 | 668.4 | 639.9 | 394.8 | 353.4 | 460.9
3196.1 | 3021.1 | 523.7 | 619 | 623.5 | 668.7 | 639.9 | 394.9 | 353.4 | 461
3197.1 | 3022.1 | 523.7 | 619 | 623.5 | 669 | 640.1 | 394.8 | 353.5 | 461.1
3198.1 | 3023.1 | 523.6 | 619.1 | 623.6 | 669.3 | 640.5 | 394.9 | 353.6 | 461.3
3199.1 | 3024.1 | 523.6 | 619.1 | 623.7 | 669.6 | 640.9 | 394.9 | 353.6 | 461.4
3200.1 | 3025.1 | 523.7 | 619.1 | 623.7 | 669.9 | 641.2 | 394.9 | 353.7 | 461.4
3201.1 | 3026.1 | 523.4 | 619.1 | 623.7 | 670.1 | 641.1 | 394.9 | 353.7 | 461.4
3202.1 | 3027.1 | 523.2 | 619.1 | 623.8 | 670.1 | 641 | 394.9 | 353.8 | 461.5
3203.1 | 3028.1 | 523.2 | 619.1 | 623.9 | 670.3 | 641.1 | 394.7 | 353.8 | 461.5
3204.1 | 3029.1 | 523 | 619.1 | 623.9 | 670.4 | 641.2 | 394.6 | 353.8 | 461.6
3205.1 | 3030.1 | 523 | 619.2 | 624 | 670.6 | 641.4 | 394.4 | 353.8 | 461.6
3206.1 | 3031.1 | 522.8 | 619.2 | 624.1 | 670.7 | 641.4 | 394.4 | 353.7 | 461.6
3207.1 | 3032.1 | 522.6 | 619.3 | 624 | 670.9 | 641.8 | 394.3 | 353.7 | 461.7
3208.1 | 3033.1 | 522.6 | 619.3 | 624.1 | 671.1 | 642 | 394.3 | 353.6 | 461.7
3209.1 | 3034.1 | 522.5 | 619.4 | 624.2 | 671.1 | 641.9 | 394.4 | 353.6 | 461.8
3210.1 | 3035.1 | 522.6 | 619.4 | 624.2 | 671.2 | 642 | 394.4 | 353.5 | 461.9
3211.1 | 3036.1 | 522.5 | 619.5 | 624.2 | 671.4 | 642.1 | 394.5 | 353.6 | 461.9
3212.1 | 3037.1 | 522.4 | 619.5 | 624.3 | 671.6 | 642.2 | 394.5 | 353.7 | 462
3213.1 | 3038.1 | 522.4 | 619.4 | 624.4 | 671.9 | 642.1 | 394.4 | 353.7 | 462.1
3214.1 | 3039.1 | 522.4 | 619.5 | 624.4 | 672 | 642 | 394.3 | 353.8 | 462.1
3215.1 | 3040.1 | 522.5 | 619.4 | 624.4 | 672.1 | 641.9 | 394.1 | 353.9 | 462.1
3216.1 | 3041.1 | 522.5 | 619.4 | 624.5 | 672.2 | 641.8 | 394 | 353.9 | 462.1
3217.1 | 3042.1 | 522.6 | 619.4 | 624.5 | 672.4 | 641.9 | 393.9 | 353.9 | 462.1
3218.1 | 3043.1 | 522.6 | 619.4 | 624.5 | 672.6 | 642.2 | 393.9 | 353.9 | 462.1
3219.1 | 3044.1 | 522.4 | 619.4 | 624.5 | 672.7 | 642.2 | 393.9 | 353.9 | 462.1
3220.1 | 3045.1 | 522.3 | 619.3 | 624.6 | 672.9 | 642.2 | 394 | 354 | 462.3
3221.1 | 3046.1 | 522.5 | 619.3 | 624.6 | 673.1 | 642.2 | 394 | 354.1 | 462.3
3222.1 | 3047.1 | 522.7 | 619.2 | 624.6 | 673.2 | 642 | 393.8 | 354.1 | 462.3
3223.1 | 3048.1 | 522.5 | 619.2 | 624.7 | 673.2 | 641.9 | 393.8 | 354.1 | 462.3
3224.1 | 3049.1 | 522.1 | 619.1 | 624.8 | 673.3 | 642 | 393.8 | 354.1 | 462.3
3225.1 | 3050.1 | 521.9 | 619.1 | 624.8 | 673.4 | 642.1 | 393.8 | 353.9 | 462.4
3226.1 | 3051.1 | 521.8 | 619.1 | 624.8 | 673.6 | 642.1 | 393.8 | 353.8 | 462.5
3227.1 | 3052.1 | 521.9 | 619.1 | 624.9 | 673.7 | 642.1 | 393.8 | 353.7 | 462.6
3228.1 | 3053.1 | 521.8 | 619.2 | 624.9 | 673.9 | 642.2 | 394 | 353.6 | 462.7
3229.1 | 3054.1 | 521.8 | 619.2 | 624.9 | 674 | 642.1 | 394 | 353.6 | 462.6
3230.1 | 3055.1 | 522 | 619.3 | 625.1 | 673.9 | 641.9 | 394.2 | 353.5 | 462.8
3231.1 | 3056.1 | 522.1 | 619.3 | 625.1 | 673.9 | 641.9 | 394.4 | 353.5 | 462.8
3232.1 | 3057.1 | 522.2 | 619.4 | 625.1 | 673.9 | 642 | 394.5 | 353.6 | 462.9
3233.1 | 3058.1 | 522.2 | 619.4 | 625.1 | 673.9 | 641.9 | 394.5 | 353.6 | 462.9
3234.1 | 3059.1 | 522.3 | 619.3 | 625.2 | 674 | 641.9 | 394.6 | 353.7 | 462.9
3235.1 | 3060.1 | 522.3 | 619.3 | 625.2 | 674.3 | 642.1 | 394.6 | 353.7 | 462.9
3236.1 | 3061.1 | 522.6 | 619.3 | 625.2 | 674.5 | 642.4 | 394.6 | 353.8 | 463.2
3237.1 | 3062.1 | 522.9 | 619.3 | 625.3 | 674.7 | 642.4 | 394.5 | 353.8 | 463.3
3238.1 | 3063.1 | 523 | 619.3 | 625.4 | 674.8 | 642.6 | 394.5 | 353.8 | 463.4
3239.1 | 3064.1 | 523 | 619.3 | 625.4 | 674.9 | 642.9 | 394.5 | 353.8 | 463.5
3240.1 | 3065.1 | 523.1 | 619.3 | 625.4 | 675.1 | 643.1 | 394.5 | 353.7 | 463.5
3241.1 | 3066.1 | 523 | 619.2 | 625.6 | 675.1 | 643.3 | 394.5 | 353.7 | 463.5
3242.1 | 3067.1 | 522.9 | 619.2 | 625.5 | 675.2 | 643.5 | 394.5 | 353.8 | 463.5
3243.1 | 3068.1 | 522.8 | 619.2 | 625.6 | 675.1 | 643.5 | 394.4 | 353.8 | 463.4
3244.1 | 3069.1 | 522.9 | 619.1 | 625.7 | 675 | 643.2 | 394.4 | 353.7 | 463.5
3245.1 | 3070.1 | 522.8 | 619.1 | 625.7 | 675 | 643 | 394.4 | 353.7 | 463.5
3246.1 | 3071.1 | 522.9 | 619 | 625.8 | 675 | 642.9 | 394.3 | 353.7 | 463.6
3247.1 | 3072.1 | 523.1 | 619 | 625.9 | 675 | 642.8 | 394.2 | 353.7 | 463.7
3248.1 | 3073.1 | 523.3 | 619 | 626 | 674.9 | 642.5 | 394.1 | 353.7 | 463.8
3249.1 | 3074.1 | 523.3 | 619.1 | 626 | 675 | 642.7 | 394.1 | 353.7 | 463.6
3250.1 | 3075.1 | 523.4 | 619.1 | 626.1 | 675 | 642.6 | 394.1 | 353.8 | 463.6
3251.1 | 3076.1 | 523.4 | 619.1 | 626.2 | 674.9 | 642.4 | 394.1 | 353.8 | 463.7
3252.1 | 3077.1 | 523.4 | 619.1 | 626.2 | 674.8 | 642.2 | 394.1 | 353.7 | 463.8
3253.1 | 3078.1 | 523.3 | 619.2 | 626.3 | 674.6 | 642.1 | 394.2 | 353.7 | 464
3254.1 | 3079.1 | 523.3 | 619.3 | 626.3 | 674.5 | 642 | 394.3 | 353.8 | 464.1
3255.1 | 3080.1 | 523.2 | 619.3 | 626.5 | 674.5 | 641.9 | 394.4 | 353.8 | 464.1
3256.1 | 3081.1 | 523.2 | 619.4 | 626.4 | 674.6 | 642.2 | 394.4 | 353.8 | 464.1
3257.1 | 3082.1 | 523.3 | 619.4 | 626.4 | 674.7 | 642.5 | 394.4 | 353.7 | 464.3
3258.1 | 3083.1 | 523.5 | 619.5 | 626.5 | 674.9 | 642.7 | 394.5 | 353.8 | 464.4
3259.1 | 3084.1 | 523.4 | 619.5 | 626.5 | 675.1 | 643 | 394.6 | 353.7 | 464.4
3260.1 | 3085.1 | 523.3 | 619.6 | 626.5 | 675.4 | 643.3 | 394.7 | 353.5 | 464.4
3261.1 | 3086.1 | 523.1 | 619.6 | 626.5 | 675.6 | 643.5 | 394.8 | 353.5 | 464.5
3262.1 | 3087.1 | 523 | 619.6 | 626.5 | 675.8 | 643.6 | 394.9 | 353.5 | 464.5
3263.1 | 3088.1 | 523 | 619.6 | 626.5 | 675.8 | 643.8 | 394.9 | 353.5 | 464.5
3264.1 | 3089.1 | 523 | 619.6 | 626.6 | 675.8 | 643.8 | 394.9 | 353.5 | 464.5
3265.1 | 3090.1 | 522.8 | 619.6 | 626.7 | 675.8 | 643.8 | 394.8 | 353.5 | 464.5
3266.1 | 3091.1 | 522.6 | 619.6 | 626.7 | 675.8 | 643.7 | 394.8 | 353.5 | 464.6
3267.1 | 3092.1 | 522.6 | 619.6 | 626.7 | 675.8 | 643.9 | 394.8 | 353.5 | 464.7
3268.1 | 3093.1 | 522.5 | 619.6 | 626.7 | 675.8 | 643.9 | 394.8 | 353.5 | 464.8
3269.1 | 3094.1 | 522.6 | 619.5 | 626.8 | 675.7 | 643.9 | 394.8 | 353.5 | 465
3270.1 | 3095.1 | 522.5 | 619.5 | 626.8 | 675.7 | 644.1 | 394.9 | 353.6 | 465.1
3271.1 | 3096.1 | 522.3 | 619.5 | 626.9 | 675.7 | 644.2 | 395 | 353.6 | 465.2
3272.1 | 3097.1 | 522.2 | 619.5 | 627 | 675.6 | 644.1 | 395.2 | 353.6 | 465.3
3273.1 | 3098.1 | 522.3 | 619.4 | 627 | 675.5 | 644.2 | 395.4 | 353.6 | 465.4
3274.1 | 3099.1 | 522.3 | 619.4 | 627 | 675.6 | 644.3 | 395.4 | 353.7 | 465.4
3275.1 | 3100.1 | 522.6 | 619.3 | 627.1 | 675.7 | 644.2 | 395.3 | 353.8 | 465.5
3276.1 | 3101.1 | 522.8 | 619.2 | 627.2 | 675.7 | 644.2 | 395.3 | 353.8 | 465.6
3277.1 | 3102.1 | 522.9 | 619.2 | 627.1 | 675.9 | 644.4 | 395.2 | 353.9 | 465.7
3278.1 | 3103.1 | 522.9 | 619.1 | 627.2 | 676 | 644.6 | 395.1 | 353.9 | 465.7
3279.1 | 3104.1 | 522.7 | 619 | 627.3 | 676.2 | 644.8 | 394.9 | 353.9 | 465.7
3280.1 | 3105.1 | 522.5 | 618.9 | 627.3 | 676.4 | 645 | 394.8 | 353.8 | 465.8
3281.1 | 3106.1 | 522.3 | 618.9 | 627.3 | 676.6 | 645.1 | 394.7 | 353.9 | 465.8
3282.1 | 3107.1 | 522.4 | 618.8 | 627.4 | 676.6 | 645.2 | 394.7 | 353.9 | 465.8
3283.1 | 3108.1 | 522.3 | 618.7 | 627.5 | 676.6 | 645.1 | 394.8 | 353.9 | 465.8
3284.1 | 3109.1 | 522.2 | 618.7 | 627.5 | 676.6 | 645.1 | 394.9 | 354 | 465.8
3285.1 | 3110.1 | 522.1 | 618.6 | 627.5 | 676.5 | 644.8 | 395.1 | 354.1 | 465.8
3286.1 | 3111.1 | 521.9 | 618.5 | 627.7 | 676.4 | 644.7 | 395.1 | 354.2 | 466
3287.1 | 3112.1 | 521.4 | 618.4 | 627.7 | 676.4 | 644.6 | 395 | 354.2 | 466.1
3288.1 | 3113.1 | 521.3 | 618.4 | 627.7 | 676.4 | 644.7 | 395 | 354.2 | 466.2
3289.1 | 3114.1 | 521.4 | 618.3 | 627.7 | 676.4 | 644.7 | 395 | 354.2 | 466.3
3290.1 | 3115.1 | 521.4 | 618.3 | 627.8 | 676.2 | 644.6 | 395 | 354.3 | 466.4
3291.1 | 3116.1 | 521.4 | 618.2 | 627.8 | 676.1 | 644.6 | 394.9 | 354.3 | 466.4
3292.1 | 3117.1 | 521.4 | 618.2 | 627.8 | 676 | 644.5 | 394.8 | 354.3 | 466.3
3293.1 | 3118.1 | 521.6 | 618.1 | 627.9 | 675.9 | 644.3 | 394.7 | 354.4 | 466.4
3294.1 | 3119.1 | 521.6 | 618 | 627.9 | 675.9 | 644.4 | 394.6 | 354.4 | 466.4
3295.1 | 3120.1 | 521.7 | 617.9 | 627.8 | 676 | 644.6 | 394.4 | 354.5 | 466.4
3296.1 | 3121.1 | 521.8 | 617.8 | 627.9 | 676 | 644.7 | 394.3 | 354.5 | 466.4
3297.1 | 3122.1 | 521.8 | 617.7 | 627.9 | 676.1 | 644.7 | 394.1 | 354.7 | 466.6
3298.1 | 3123.1 | 521.9 | 617.7 | 627.9 | 676.2 | 645 | 394.1 | 354.7 | 466.8
3299.1 | 3124.1 | 522.2 | 617.6 | 627.9 | 676.4 | 645.1 | 394.2 | 354.7 | 466.8
3300.1 | 3125.1 | 522.2 | 617.5 | 627.9 | 676.3 | 645 | 394.3 | 354.8 | 466.8
3301.1 | 3126.1 | 522.4 | 617.4 | 627.9 | 676.4 | 645.1 | 394.3 | 354.8 | 466.8
3302.1 | 3127.1 | 522.5 | 617.3 | 627.9 | 676.5 | 645.2 | 394.3 | 354.9 | 467
3303.1 | 3128.1 | 522.6 | 617.2 | 628 | 676.5 | 645.2 | 394.3 | 354.9 | 466.9
3304.1 | 3129.1 | 522.6 | 617.1 | 628 | 676.5 | 645.2 | 394.3 | 354.9 | 466.9
3305.1 | 3130.1 | 522.4 | 617 | 628 | 676.6 | 645.3 | 394.3 | 354.9 | 466.8
3306.1 | 3131.1 | 522.1 | 617 | 628 | 676.6 | 645.3 | 394.3 | 354.9 | 466.8
3307.1 | 3132.1 | 522.4 | 616.9 | 628 | 676.6 | 645.1 | 394.3 | 355 | 466.8
3308.1 | 3133.1 | 522.7 | 616.8 | 628.1 | 676.6 | 644.9 | 394.2 | 355.1 | 466.8
3309.1 | 3134.1 | 522.8 | 616.8 | 628.1 | 676.5 | 644.7 | 394.1 | 355.2 | 466.7
3310.1 | 3135.1 | 522.8 | 616.7 | 628.1 | 676.3 | 644.4 | 394 | 355.2 | 466.6
3311.1 | 3136.1 | 522.7 | 616.6 | 628.2 | 676.1 | 644.2 | 394 | 355.4 | 466.6
3312.1 | 3137.1 | 522.6 | 616.6 | 628.2 | 676 | 644.2 | 393.9 | 355.3 | 466.6
3313.1 | 3138.1 | 522.6 | 616.5 | 628.2 | 675.9 | 644.2 | 393.9 | 355.4 | 466.6
3314.1 | 3139.1 | 522.6 | 616.4 | 628.3 | 676 | 644.3 | 393.8 | 355.4 | 466.6
3315.1 | 3140.1 | 522.6 | 616.3 | 628.3 | 676 | 644.4 | 393.9 | 355.4 | 466.6
3316.1 | 3141.1 | 522.6 | 616.3 | 628.2 | 676.1 | 644.7 | 394.1 | 355.3 | 466.5
3317.1 | 3142.1 | 522.4 | 616.2 | 628.2 | 676.1 | 644.9 | 394.1 | 355.3 | 466.3
3318.1 | 3143.1 | 522.5 | 616.1 | 628.3 | 676.1 | 644.8 | 394.1 | 355.3 | 466.2
3319.1 | 3144.1 | 522.3 | 616 | 628.3 | 676.1 | 644.7 | 394.1 | 355.3 | 466.1
3320.1 | 3145.1 | 522.3 | 615.9 | 628.3 | 676 | 644.5 | 394.2 | 355.3 | 466
3321.1 | 3146.1 | 522.3 | 615.8 | 628.3 | 675.8 | 644.3 | 394.3 | 355.3 | 466
3322.1 | 3147.1 | 522.3 | 615.7 | 628.3 | 675.7 | 643.9 | 394.3 | 355.4 | 466.2
3323.1 | 3148.1 | 522.4 | 615.6 | 628.3 | 675.6 | 643.6 | 394.4 | 355.4 | 466.3
3324.1 | 3149.1 | 522.4 | 615.5 | 628.3 | 675.5 | 643.4 | 394.4 | 355.5 | 466.3
3325.1 | 3150.1 | 522.5 | 615.4 | 628.4 | 675.4 | 643.2 | 394.3 | 355.5 | 466.3
3326.1 | 3151.1 | 522.5 | 615.3 | 628.3 | 675.3 | 643.2 | 394.3 | 355.6 | 466.2
3327.1 | 3152.1 | 522.4 | 615.2 | 628.3 | 675.2 | 643.1 | 394.4 | 355.6 | 466.1
3328.1 | 3153.1 | 522.4 | 615 | 628.4 | 675.2 | 642.9 | 394.4 | 355.7 | 466
3329.1 | 3154.1 | 522.3 | 615 | 628.2 | 675.1 | 642.9 | 394.2 | 355.7 | 466.1
3330.1 | 3155.1 | 522.4 | 614.9 | 628.1 | 674.9 | 642.7 | 394.2 | 355.6 | 466.1
3331.1 | 3156.1 | 522.3 | 614.8 | 628.1 | 674.8 | 642.4 | 394.1 | 355.7 | 466
3332.1 | 3157.1 | 522.4 | 614.7 | 628.2 | 674.6 | 642.3 | 394.1 | 355.7 | 466
3333.1 | 3158.1 | 522.3 | 614.7 | 628.1 | 674.4 | 642.4 | 394 | 355.8 | 465.9
3334.1 | 3159.1 | 522.1 | 614.7 | 628 | 674.3 | 642.4 | 394 | 355.8 | 465.7
3335.1 | 3160.1 | 522.2 | 614.6 | 628 | 674.4 | 642.4 | 393.9 | 355.9 | 465.7
3336.1 | 3161.1 | 522.4 | 614.7 | 627.9 | 674.7 | 642.6 | 393.9 | 356 | 465.7
3337.1 | 3162.1 | 522.6 | 614.8 | 627.6 | 675 | 643.1 | 393.9 | 356 | 465.7
3338.1 | 3163.1 | 522.7 | 615 | 627.2 | 675.3 | 643.9 | 393.9 | 356 | 465.8
3339.1 | 3164.1 | 522.6 | 614.9 | 627.3 | 675.4 | 644.1 | 393.9 | 356 | 465.9
3340.1 | 3165.1 | 522.6 | 614.9 | 627.2 | 675.5 | 644.4 | 393.9 | 356.1 | 465.8
3341.1 | 3166.1 | 522.7 | 614.8 | 627.1 | 675.6 | 644.6 | 394 | 356.1 | 465.9
3342.1 | 3167.1 | 522.9 | 614.6 | 627.2 | 675.6 | 644.7 | 394 | 356.1 | 466
3343.1 | 3168.1 | 523.1 | 614.5 | 627.2 | 675.6 | 644.7 | 393.9 | 356.1 | 465.7
3344.1 | 3169.1 | 523.3 | 614.4 | 627.2 | 675.6 | 644.7 | 394 | 356.1 | 465.8
3345.1 | 3170.1 | 523.4 | 614.3 | 627.2 | 675.5 | 644.4 | 394.1 | 356.1 | 465.9
3346.1 | 3171.1 | 523.5 | 614.1 | 627.2 | 675.5 | 644.1 | 394.2 | 356.2 | 465.9
3347.1 | 3172.1 | 523.6 | 614.1 | 627.1 | 675.4 | 644.1 | 394.1 | 356.1 | 465.9
3348.1 | 3173.1 | 523.4 | 614 | 627 | 675.4 | 643.9 | 394.1 | 356.2 | 465.7
3349.1 | 3174.1 | 523.3 | 614.6 | 626 | 675.6 | 644.7 | 394.2 | 356.1 | 465.5
3350.1 | 3175.1 | 523.2 | 614.8 | 625.5 | 675.7 | 644.9 | 394.3 | 356.1 | 465.4
3351.1 | 3176.1 | 522.9 | 614.8 | 625.5 | 675.6 | 644.8 | 394.4 | 356.1 | 465.2
3352.1 | 3177.1 | 522.8 | 614.7 | 625.6 | 675.6 | 644.7 | 394.4 | 356 | 465.1
3353.1 | 3178.1 | 522.9 | 614.6 | 625.7 | 675.5 | 644.4 | 394.5 | 356.1 | 465.2
3354.1 | 3179.1 | 522.6 | 614.7 | 625.5 | 675.6 | 644.5 | 394.5 | 356 | 465.2
3355.1 | 3180.1 | 522.1 | 614.7 | 625.4 | 675.5 | 644.4 | 394.5 | 356 | 465.2
3356.1 | 3181.1 | 521.7 | 614.6 | 625.5 | 675.3 | 644.1 | 394.6 | 355.8 | 465.1
3357.1 | 3182.1 | 521.5 | 614.6 | 625.5 | 675.2 | 643.9 | 394.6 | 355.8 | 465
3358.1 | 3183.1 | 521.3 | 614.6 | 625.5 | 675 | 643.6 | 394.6 | 355.7 | 465
3359.1 | 3184.1 | 521.3 | 614.5 | 625.5 | 674.9 | 643.6 | 394.7 | 355.7 | 465.1
3360.1 | 3185.1 | 521.4 | 614.4 | 625.6 | 674.7 | 643.5 | 394.8 | 355.7 | 465.1
3361.1 | 3186.1 | 521.5 | 614.5 | 625.4 | 674.7 | 643.6 | 394.9 | 355.6 | 465.1
3362.1 | 3187.1 | 521.4 | 614.4 | 625.4 | 674.7 | 643.8 | 395 | 355.6 | 465.1
3363.1 | 3188.1 | 521.3 | 614.3 | 625.5 | 674.8 | 643.8 | 394.9 | 355.6 | 465.2
3364.1 | 3189.1 | 521.4 | 614.2 | 625.4 | 674.9 | 644.1 | 394.7 | 355.6 | 465.2
3365.1 | 3190.1 | 521.4 | 614.3 | 625.3 | 675 | 644.3 | 394.6 | 355.6 | 465.3
3366.1 | 3191.1 | 521.3 | 614.3 | 625.3 | 674.9 | 644.3 | 394.6 | 355.6 | 465.3
3367.1 | 3192.1 | 521.4 | 614.2 | 625.4 | 674.8 | 644.2 | 394.8 | 355.7 | 465.4
3368.1 | 3193.1 | 521.2 | 614.2 | 625.2 | 674.8 | 644.3 | 395 | 355.7 | 465.5
3369.1 | 3194.1 | 521.2 | 614.2 | 625.1 | 674.9 | 644.4 | 395.2 | 355.7 | 465.7
3370.1 | 3195.1 | 521.4 | 614 | 625.3 | 675.1 | 644.4 | 395.2 | 355.8 | 465.8
3371.1 | 3196.1 | 521.7 | 614 | 625.2 | 675.1 | 644.4 | 395.3 | 355.8 | 465.9
3372.1 | 3197.1 | 522 | 614 | 625.1 | 675.1 | 644.4 | 395.4 | 355.8 | 465.9
3373.1 | 3198.1 | 522.1 | 613.8 | 625.2 | 675.1 | 644.3 | 395.5 | 355.8 | 466.1
3374.1 | 3199.1 | 522.1 | 613.7 | 625.3 | 675.1 | 644.2 | 395.5 | 355.8 | 466.3
3375.1 | 3200.1 | 522.3 | 613.6 | 625.1 | 675.4 | 644.5 | 395.5 | 355.8 | 466.3
3376.1 | 3201.1 | 522.1 | 613.6 | 625.1 | 675.4 | 644.5 | 395.5 | 355.8 | 466.6
3377.1 | 3202.1 | 522.1 | 613.4 | 625.2 | 675.4 | 644.5 | 395.5 | 355.9 | 466.6
3378.1 | 3203.1 | 522.2 | 613.4 | 625.2 | 675.5 | 644.5 | 395.4 | 355.9 | 466.6
3379.1 | 3204.1 | 522.5 | 613.4 | 625.1 | 675.5 | 644.5 | 395.4 | 355.9 | 466.7
3380.1 | 3205.1 | 522.6 | 613.2 | 625.2 | 675.4 | 644.4 | 395.4 | 355.9 | 466.6
3381.1 | 3206.1 | 522.6 | 613 | 625.4 | 675.2 | 644.2 | 395.3 | 355.9 | 466.7
3382.1 | 3207.1 | 522.8 | 612.9 | 625.2 | 675.2 | 644.4 | 395.2 | 355.9 | 466.5
3383.1 | 3208.1 | 522.8 | 612.8 | 625.1 | 675.1 | 644.3 | 395.2 | 355.8 | 466.6
3384.1 | 3209.1 | 522.9 | 612.5 | 625.3 | 674.9 | 644 | 395.1 | 355.9 | 466.6
3385.1 | 3210.1 | 522.9 | 612.4 | 625.2 | 674.9 | 643.8 | 395.1 | 355.9 | 466.4
3386.1 | 3211.1 | 522.9 | 612.4 | 625.1 | 674.9 | 643.5 | 395.1 | 355.9 | 466.2
3387.1 | 3212.1 | 522.9 | 612.2 | 625.2 | 674.8 | 643.2 | 395.1 | 355.9 | 466.1
3388.1 | 3213.1 | 522.7 | 612 | 625.4 | 674.6 | 642.8 | 395.1 | 356 | 465.9
3389.1 | 3214.1 | 522.5 | 612 | 625.2 | 674.5 | 642.8 | 395.3 | 356 | 466
3390.1 | 3215.1 | 522.6 | 611.9 | 625.2 | 674.4 | 642.6 | 395.3 | 356 | 466
3391.1 | 3216.1 | 522.6 | 611.7 | 625.4 | 674.2 | 642.3 | 395.3 | 356 | 466
3392.1 | 3217.1 | 522.7 | 611.5 | 625.4 | 674.1 | 642.2 | 395.3 | 356 | 466.1
3393.1 | 3218.1 | 522.8 | 611.5 | 625.3 | 674.1 | 642.1 | 395.4 | 356 | 466
3394.1 | 3219.1 | 522.7 | 611.4 | 625.3 | 673.9 | 641.8 | 395.5 | 356 | 466
3395.1 | 3220.1 | 522.5 | 611.2 | 625.5 | 673.8 | 641.5 | 395.5 | 356 | 466.1
3396.1 | 3221.1 | 522.4 | 611.2 | 625.2 | 673.7 | 641.5 | 395.6 | 356.1 | 466.1
3397.1 | 3222.1 | 522.4 | 611.5 | 624.5 | 673.9 | 641.9 | 395.8 | 356.1 | 466
3398.1 | 3223.1 | 522.2 | 611.8 | 623.9 | 674 | 642.2 | 395.8 | 356 | 465.9
3399.1 | 3224.1 | 522.2 | 611.8 | 623.8 | 673.8 | 642.2 | 395.9 | 356 | 466
3400.1 | 3225.1 | 522 | 611.8 | 623.6 | 673.8 | 642.4 | 396 | 356 | 465.9
3401.1 | 3226.1 | 522 | 611.7 | 623.7 | 673.8 | 642.4 | 396 | 356 | 465.9
3402.1 | 3227.1 | 522.1 | 611.6 | 623.8 | 673.7 | 642.5 | 396.1 | 356 | 466
3403.1 | 3228.1 | 522.2 | 611.6 | 623.6 | 673.7 | 642.7 | 396 | 356.1 | 466
3404.1 | 3229.1 | 522.2 | 611.6 | 623.5 | 673.5 | 642.7 | 396 | 356.1 | 466.1
3405.1 | 3230.1 | 522.2 | 611.4 | 623.8 | 673.3 | 642.6 | 395.9 | 356.1 | 466.1
3406.1 | 3231.1 | 522.3 | 611.4 | 623.7 | 673.2 | 642.8 | 395.9 | 356.2 | 466.2
3407.1 | 3232.1 | 522.5 | 611.4 | 623.4 | 673.2 | 643 | 395.8 | 356.3 | 466.1
3408.1 | 3233.1 | 522.6 | 611.3 | 623.5 | 673.1 | 643 | 395.9 | 356.4 | 466.1
3409.1 | 3234.1 | 522.9 | 611.1 | 623.7 | 672.9 | 643 | 395.9 | 356.4 | 466
3410.1 | 3235.1 | 523 | 611.2 | 623.4 | 673 | 643.4 | 395.9 | 356.4 | 466
3411.1 | 3236.1 | 523.2 | 611.1 | 623.4 | 673.1 | 643.6 | 395.8 | 356.5 | 466.1
3412.1 | 3237.1 | 523.3 | 611 | 623.5 | 673 | 643.6 | 395.9 | 356.5 | 466.1
3413.1 | 3238.1 | 523.3 | 611 | 623.5 | 673 | 643.6 | 395.9 | 356.4 | 466.2
3414.1 | 3239.1 | 523.2 | 611 | 623.2 | 673.2 | 643.9 | 395.9 | 356.4 | 466.2
3415.1 | 3240.1 | 523.3 | 611 | 623.2 | 673.2 | 643.9 | 395.8 | 356.5 | 466.4
3416.1 | 3241.1 | 523.4 | 610.8 | 623.4 | 673 | 643.8 | 395.7 | 356.5 | 466.6
3417.1 | 3242.1 | 523.4 | 610.9 | 623.1 | 673.1 | 644 | 395.6 | 356.5 | 466.6
3418.1 | 3243.1 | 523.5 | 610.9 | 623.1 | 673 | 644 | 395.6 | 356.5 | 466.6
3419.1 | 3244.1 | 523.9 | 610.7 | 623.2 | 673 | 643.9 | 395.8 | 356.5 | 466.6
3420.1 | 3245.1 | 524.2 | 610.7 | 623.1 | 673 | 644.1 | 395.9 | 356.7 | 466.7
3421.1 | 3246.1 | 524.3 | 610.7 | 623 | 673 | 644.2 | 396 | 356.7 | 466.7
3422.1 | 3247.1 | 524.4 | 610.6 | 623 | 672.8 | 644.2 | 396.1 | 356.7 | 466.6
3423.1 | 3248.1 | 524.5 | 610.4 | 623.2 | 672.6 | 643.9 | 396.1 | 356.7 | 466.7
3424.1 | 3249.1 | 524.7 | 610.4 | 622.9 | 672.6 | 644 | 396.2 | 356.7 | 466.7
3425.1 | 3250.1 | 524.9 | 610.4 | 622.9 | 672.6 | 644 | 396.2 | 356.7 | 466.6
3426.1 | 3251.1 | 525.2 | 610.2 | 623.2 | 672.4 | 643.8 | 396.2 | 356.7 | 466.7
3427.1 | 3252.1 | 525.1 | 610.1 | 623.1 | 672.3 | 643.7 | 396.2 | 356.7 | 466.7
3428.1 | 3253.1 | 524.9 | 610.1 | 623 | 672.2 | 643.6 | 396.2 | 356.8 | 466.7
3429.1 | 3254.1 | 525 | 610 | 623.1 | 672 | 643.3 | 396.1 | 356.7 | 466.7
3430.1 | 3255.1 | 525.2 | 609.8 | 623.3 | 671.7 | 643.1 | 396 | 356.7 | 466.5
3431.1 | 3256.1 | 525.1 | 609.9 | 623 | 671.6 | 643.2 | 396 | 356.7 | 466.5
3432.1 | 3257.1 | 525.1 | 609.8 | 623 | 671.5 | 643.1 | 395.9 | 356.7 | 466.6
3433.1 | 3258.1 | 525.1 | 609.6 | 623.1 | 671.3 | 642.9 | 395.9 | 356.7 | 466.8
3434.1 | 3259.1 | 524.9 | 609.6 | 623.1 | 671 | 642.9 | 395.9 | 356.7 | 466.9
3435.1 | 3260.1 | 524.9 | 609.6 | 622.9 | 670.8 | 643 | 395.9 | 356.7 | 467
3436.1 | 3261.1 | 524.8 | 609.5 | 623 | 670.5 | 642.9 | 395.9 | 356.8 | 467.2
3437.1 | 3262.1 | 524.8 | 609.3 | 623.3 | 670.2 | 642.8 | 395.9 | 356.7 | 467.4
3438.1 | 3263.1 | 524.9 | 609.3 | 623.1 | 670.2 | 643 | 396 | 356.8 | 467.5
3439.1 | 3264.1 | 525 | 609.2 | 623.1 | 670.1 | 643.2 | 396.1 | 356.8 | 467.5
3440.1 | 3265.1 | 525 | 609 | 623.2 | 670 | 643.3 | 396.1 | 356.9 | 467.4
3441.1 | 3266.1 | 524.9 | 609 | 623.1 | 669.9 | 643.5 | 396.1 | 356.9 | 467.4
3442.1 | 3267.1 | 524.7 | 609 | 622.9 | 669.7 | 643.7 | 396.1 | 357 | 467.4
3443.1 | 3268.1 | 524.4 | 608.9 | 622.8 | 669.4 | 643.7 | 396.2 | 357 | 467.5
3444.1 | 3269.1 | 524 | 608.8 | 622.9 | 669 | 643.5 | 396.3 | 357.1 | 467.6
3445.1 | 3270.1 | 523.7 | 608.8 | 622.6 | 668.8 | 643.6 | 396.4 | 357.1 | 467.5
3446.1 | 3271.1 | 523.5 | 608.7 | 622.6 | 668.4 | 643.6 | 396.4 | 357.1 | 467.6
3447.1 | 3272.1 | 523.4 | 608.5 | 622.7 | 667.9 | 643.3 | 396.4 | 357.1 | 467.7
3448.1 | 3273.1 | 523.4 | 608.4 | 622.6 | 667.4 | 643.3 | 396.4 | 357.1 | 467.7
3449.1 | 3274.1 | 523.4 | 608.4 | 622.4 | 666.8 | 643.3 | 396.4 | 357.1 | 467.8
3450.1 | 3275.1 | 523.3 | 608.2 | 622.4 | 666.1 | 643.2 | 396.3 | 357.1 | 467.9
3451.1 | 3276.1 | 523.3 | 608 | 622.5 | 665.5 | 643.1 | 396.2 | 357.1 | 468
3452.1 | 3277.1 | 523.2 | 608 | 622.3 | 665.1 | 643.2 | 396.2 | 357.2 | 468.1
3453.1 | 3278.1 | 523.2 | 607.8 | 622.2 | 664.5 | 643.2 | 396.3 | 357.2 | 468.2
3454.1 | 3279.1 | 523.2 | 607.5 | 622.3 | 663.9 | 643 | 396.3 | 357.1 | 468.3
3455.1 | 3280.1 | 523.2 | 607.4 | 622.2 | 663.3 | 643 | 396.3 | 357.1 | 468.4
3456.1 | 3281.1 | 523.3 | 607.3 | 622 | 662.6 | 642.9 | 396.1 | 357.1 | 468.4
3457.1 | 3282.1 | 523.3 | 607.1 | 622.1 | 661.8 | 642.6 | 396 | 357.1 | 468.4
3458.1 | 3283.1 | 523 | 606.8 | 622.3 | 660.9 | 642.2 | 395.9 | 357.1 | 468.5
3459.1 | 3284.1 | 522.6 | 606.8 | 622.1 | 660.3 | 642.2 | 395.8 | 357.1 | 468.4
3460.1 | 3285.1 | 522.4 | 606.7 | 622 | 659.5 | 642 | 395.8 | 357.2 | 468.4
3461.1 | 3286.1 | 522.4 | 606.5 | 622.2 | 658.7 | 641.6 | 395.8 | 357.3 | 468.4
3462.1 | 3287.1 | 522.3 | 606.4 | 622 | 658.2 | 641.4 | 395.9 | 357.2 | 468.5
3463.1 | 3288.1 | 522.2 | 606.4 | 621.8 | 657.7 | 641.4 | 396 | 357.2 | 468.3
3464.1 | 3289.1 | 522.2 | 606.3 | 621.7 | 657.3 | 641.4 | 396 | 357.3 | 468.2
3465.1 | 3290.1 | 522.1 | 606.2 | 621.8 | 656.7 | 641.2 | 396 | 357.3 | 468.2
3466.1 | 3291.1 | 521.8 | 606.3 | 621.5 | 656.4 | 641.2 | 395.9 | 357.3 | 468.2
3467.1 | 3292.1 | 521.7 | 606.2 | 621.4 | 655.9 | 641.2 | 395.9 | 357.3 | 468.3
3468.1 | 3293.1 | 521.6 | 606.1 | 621.5 | 655.4 | 641.1 | 395.9 | 357.2 | 468.4
3469.1 | 3294.1 | 521.6 | 605.3 | 622.9 | 654.5 | 640.1 | 395.9 | 357.3 | 468.4
3470.1 | 3295.1 | 521.8 | 604.7 | 623.9 | 653.7 | 639.2 | 396 | 357.2 | 468.3
3471.1 | 3296.1 | 521.9 | 604.4 | 624 | 653.1 | 638.9 | 396.1 | 357.2 | 468.4
3472.1 | 3297.1 | 521.7 | 604.3 | 624.1 | 652.7 | 638.6 | 396.2 | 357.2 | 468.5
3473.1 | 3298.1 | 521.4 | 604.2 | 623.9 | 652.3 | 638.5 | 396.3 | 357.2 | 468.4
3474.1 | 3299.1 | 520.9 | 604.2 | 623.8 | 651.9 | 638.2 | 396.4 | 357.1 | 468.2
3475.1 | 3300.1 | 520.3 | 604 | 623.9 | 651.4 | 638 | 396.3 | 357 | 468.1
3476.1 | 3301.1 | 519.5 | 603.9 | 623.8 | 651.1 | 638 | 396.3 | 357 | 468.1
3477.1 | 3302.1 | 518.6 | 603.9 | 623.6 | 650.8 | 638.1 | 396.2 | 356.9 | 468.1
3478.1 | 3303.1 | 517.5 | 603.8 | 623.6 | 650.4 | 638.2 | 396.1 | 356.7 | 468.1
3479.1 | 3304.1 | 516.6 | 603.6 | 623.6 | 650.1 | 638.1 | 395.9 | 356.7 | 468
3480.1 | 3305.1 | 515.6 | 603.5 | 623.4 | 649.7 | 638.2 | 395.7 | 356.6 | 467.9
3481.1 | 3306.1 | 514.4 | 603.4 | 623.2 | 649.4 | 638.2 | 395.5 | 356.5 | 467.6
3482.1 | 3307.1 | 513.2 | 603.1 | 623.2 | 649 | 638.1 | 395.2 | 356.4 | 467.4
3483.1 | 3308.1 | 512.1 | 602.9 | 623.1 | 648.6 | 638 | 394.9 | 356.2 | 467.3
3484.1 | 3309.1 | 511 | 602.8 | 622.9 | 648.2 | 637.9 | 394.6 | 356 | 467.3
3485.1 | 3310.1 | 509.7 | 602.5 | 622.8 | 647.8 | 637.6 | 394.4 | 355.8 | 467.3
3486.1 | 3311.1 | 508.4 | 602.3 | 622.8 | 647.2 | 637.1 | 394.2 | 355.6 | 467.2
3487.1 | 3312.1 | 507.1 | 602.1 | 622.5 | 646.8 | 636.9 | 394 | 355.4 | 467
3488.1 | 3313.1 | 505.9 | 601.8 | 622.3 | 646.3 | 636.5 | 393.8 | 355.2 | 466.9
3489.1 | 3314.1 | 504.6 | 601.5 | 622.2 | 645.7 | 636.1 | 393.5 | 355 | 466.7
3490.1 | 3315.1 | 503.4 | 601.3 | 622.1 | 645.2 | 635.7 | 393.2 | 354.7 | 466.6
3491.1 | 3316.1 | 502.1 | 601.1 | 621.8 | 644.8 | 635.5 | 392.9 | 354.6 | 466.6
3492.1 | 3317.1 | 500.7 | 600.9 | 621.6 | 644.2 | 635.1 | 392.5 | 354.4 | 466.4
3493.1 | 3318.1 | 499.6 | 600.6 | 621.5 | 643.7 | 634.6 | 392.2 | 354.3 | 466.2
3494.1 | 3319.1 | 498.4 | 600.4 | 621.2 | 643.2 | 634.5 | 391.9 | 354 | 466
3495.1 | 3320.1 | 497.1 | 600.1 | 621 | 642.8 | 634.2 | 391.4 | 353.8 | 465.9
3496.1 | 3321.1 | 495.8 | 599.7 | 620.9 | 642.2 | 633.8 | 391 | 353.6 | 465.7
3497.1 | 3322.1 | 494.4 | 599.4 | 620.6 | 641.8 | 633.5 | 390.7 | 353.3 | 465.4
3498.1 | 3323.1 | 493.1 | 599.1 | 620.3 | 641.4 | 633.5 | 390.3 | 353.1 | 465.1
3499.1 | 3324.1 | 491.8 | 598.7 | 620.1 | 641.1 | 633.3 | 390 | 352.9 | 464.8
3500.1 | 3325.1 | 490.5 | 598.3 | 620 | 640.7 | 633 | 389.6 | 352.7 | 464.7
3501.1 | 3326.1 | 489.3 | 598 | 619.5 | 640.3 | 632.8 | 389.3 | 352.4 | 464.5
3502.1 | 3327.1 | 488.1 | 597.7 | 619.3 | 639.8 | 632.5 | 389 | 352.3 | 464.3
3503.1 | 3328.1 | 487 | 597.3 | 619.2 | 639.3 | 631.9 | 388.7 | 352 | 464
3504.1 | 3329.1 | 485.9 | 596.9 | 618.9 | 638.8 | 631.5 | 388.3 | 351.8 | 463.8
3505.1 | 3330.1 | 484.8 | 596.6 | 618.6 | 638.2 | 631.1 | 387.9 | 351.6 | 463.3
3506.1 | 3331.1 | 483.5 | 596.3 | 618.3 | 637.7 | 630.5 | 387.5 | 351.3 | 462.9
3507.1 | 3332.1 | 482.3 | 595.9 | 618.2 | 637.1 | 629.9 | 387.1 | 351.1 | 462.7
3508.1 | 3333.1 | 481.1 | 595.6 | 617.8 | 636.7 | 629.6 | 386.6 | 350.9 | 462.3
3509.1 | 3334.1 | 479.7 | 595.2 | 617.5 | 636.1 | 629.3 | 386.2 | 350.5 | 462
3510.1 | 3335.1 | 478.5 | 594.8 | 617.3 | 635.6 | 628.9 | 385.8 | 350.3 | 461.7
3511.1 | 3336.1 | 477.2 | 594.5 | 616.9 | 635.1 | 628.6 | 385.4 | 350 | 461.5
3512.1 | 3337.1 | 475.8 | 594.2 | 616.5 | 634.7 | 628.4 | 385.1 | 349.7 | 461.1
3513.1 | 3338.1 | 474.7 | 593.8 | 616.3 | 634.2 | 628.1 | 384.7 | 349.3 | 460.8
3514.1 | 3339.1 | 473.6 | 593.4 | 616.1 | 633.7 | 627.6 | 384.4 | 349 | 460.6
3515.1 | 3340.1 | 472.3 | 593.1 | 615.6 | 633.3 | 627.4 | 384 | 348.7 | 460.1
3516.1 | 3341.1 | 471 | 592.7 | 615.2 | 632.8 | 627 | 383.6 | 348.4 | 459.6
3517.1 | 3342.1 | 469.7 | 592.3 | 615 | 632.2 | 626.5 | 383.1 | 348.1 | 459.2
3518.1 | 3343.1 | 468.4 | 591.9 | 614.7 | 631.7 | 626 | 382.6 | 347.8 | 458.7
3519.1 | 3344.1 | 467.4 | 591.5 | 614.3 | 631.2 | 625.7 | 382 | 347.5 | 458.3
3520.1 | 3345.1 | 466.3 | 591.1 | 614 | 630.7 | 625.3 | 381.4 | 347.1 | 457.9
3521.1 | 3346.1 | 465.2 | 590.6 | 613.8 | 630.1 | 624.8 | 380.9 | 346.7 | 457.6
3522.1 | 3347.1 | 464.1 | 590.2 | 613.3 | 629.6 | 624.5 | 380.5 | 346.3 | 457.3
3523.1 | 3348.1 | 463 | 589.7 | 613 | 629 | 624 | 379.9 | 346 | 456.8
3524.1 | 3349.1 | 461.8 | 589.1 | 612.8 | 628.4 | 623.3 | 379.4 | 345.6 | 456.5
3525.1 | 3350.1 | 460.6 | 588.6 | 612.4 | 627.8 | 622.7 | 378.8 | 345.3 | 456
3526.1 | 3351.1 | 459.5 | 588.1 | 612 | 627.3 | 622.1 | 378.3 | 344.9 | 455.4
3527.1 | 3352.1 | 458.3 | 587.5 | 611.7 | 626.7 | 621.3 | 377.8 | 344.6 | 454.9
3528.1 | 3353.1 | 457.1 | 586.9 | 611.4 | 626.1 | 620.6 | 377.4 | 344.2 | 454.3
3529.1 | 3354.1 | 455.8 | 586.4 | 611 | 625.5 | 620.1 | 377 | 343.8 | 453.8
3530.1 | 3355.1 | 454.6 | 585.9 | 610.6 | 624.9 | 619.4 | 376.5 | 343.5 | 453.3
3531.1 | 3356.1 | 453.4 | 585.3 | 610.4 | 624.3 | 618.6 | 376.1 | 343.1 | 452.9
3532.1 | 3357.1 | 452.1 | 584.8 | 610 | 623.6 | 618 | 375.7 | 342.7 | 452.4
3533.1 | 3358.1 | 450.9 | 584.4 | 609.5 | 623 | 617.4 | 375.3 | 342.3 | 451.8
3534.1 | 3359.1 | 449.7 | 583.8 | 609.1 | 622.3 | 616.7 | 374.8 | 341.9 | 451.3
3535.1 | 3360.1 | 448.7 | 583.3 | 608.8 | 621.7 | 616 | 374.4 | 341.6 | 450.7
3536.1 | 3361.1 | 447.6 | 582.9 | 608.3 | 621.2 | 615.5 | 374 | 341.2 | 450.1
3537.1 | 3362.1 | 446.6 | 582.4 | 607.9 | 620.6 | 615 | 373.5 | 340.9 | 449.8
3538.1 | 3363.1 | 445.5 | 581.8 | 607.6 | 619.9 | 614.4 | 373.1 | 340.7 | 449.4
3539.1 | 3364.1 | 444.3 | 581.3 | 607.1 | 619.3 | 614 | 372.5 | 340.4 | 448.9
3540.1 | 3365.1 | 443.3 | 580.9 | 606.6 | 618.8 | 613.6 | 372 | 340.1 | 448.4
3541.1 | 3366.1 | 442.3 | 580.4 | 606.2 | 618.1 | 613 | 371.5 | 339.7 | 447.8
3542.1 | 3367.1 | 441.2 | 579.9 | 605.9 | 617.5 | 612.4 | 371 | 339.3 | 447.3
3543.1 | 3368.1 | 440.1 | 579.5 | 605.3 | 616.9 | 612 | 370.6 | 339 | 446.9
3544.1 | 3369.1 | 438.9 | 579 | 604.9 | 616.2 | 611.6 | 370.2 | 338.6 | 446.5
3545.1 | 3370.1 | 437.8 | 578.5 | 604.5 | 615.6 | 611.1 | 369.7 | 338.4 | 445.9
3546.1 | 3371.1 | 436.7 | 578 | 604.1 | 614.9 | 610.7 | 369.3 | 338 | 445.4
3547.1 | 3372.1 | 435.5 | 577.5 | 603.5 | 614.3 | 610.3 | 368.8 | 337.7 | 444.8
3548.1 | 3373.1 | 434.6 | 577 | 603.2 | 613.6 | 609.8 | 368.3 | 337.2 | 444.2
3549.1 | 3374.1 | 433.5 | 576.4 | 602.8 | 612.8 | 609.1 | 367.7 | 336.9 | 443.5
3550.1 | 3375.1 | 432.5 | 575.9 | 602.2 | 612.1 | 608.6 | 367.2 | 336.5 | 442.8
3551.1 | 3376.1 | 431.6 | 575.4 | 601.7 | 611.4 | 608 | 366.8 | 336.2 | 442
3552.1 | 3377.1 | 430.7 | 574.7 | 601.4 | 610.6 | 607.2 | 366.3 | 335.8 | 441.5
3553.1 | 3378.1 | 429.8 | 574.2 | 600.9 | 609.9 | 606.4 | 365.7 | 335.4 | 440.9
3554.1 | 3379.1 | 428.7 | 573.6 | 600.3 | 609.2 | 605.9 | 365.1 | 335 | 440.5
3555.1 | 3380.1 | 427.7 | 573.1 | 599.8 | 608.5 | 605.2 | 364.5 | 334.6 | 440
3556.1 | 3381.1 | 426.6 | 572.5 | 599.5 | 607.7 | 604.4 | 363.9 | 334.2 | 439.5
3557.1 | 3382.1 | 425.5 | 572 | 598.8 | 607 | 604 | 363.3 | 333.9 | 439
3558.1 | 3383.1 | 424.6 | 571.4 | 598.3 | 606.3 | 603.4 | 362.7 | 333.5 | 438.5
3559.1 | 3384.1 | 423.5 | 570.8 | 597.9 | 605.6 | 602.7 | 362.2 | 333 | 437.9
3560.1 | 3385.1 | 422.5 | 570.3 | 597.4 | 604.9 | 602.2 | 361.6 | 332.6 | 437.3
3561.1 | 3386.1 | 421.5 | 569.8 | 596.8 | 604.2 | 601.8 | 361.1 | 332.2 | 436.8
3562.1 | 3387.1 | 420.5 | 569.3 | 596.2 | 603.5 | 601.2 | 360.6 | 331.8 | 436.3
3563.1 | 3388.1 | 419.6 | 568.7 | 595.9 | 602.7 | 600.5 | 360.1 | 331.4 | 435.7
3564.1 | 3389.1 | 418.7 | 568.3 | 595.2 | 602 | 600.1 | 359.6 | 330.9 | 435.3
3565.1 | 3390.1 | 417.7 | 567.8 | 594.6 | 601.3 | 599.6 | 359 | 330.5 | 434.7
3566.1 | 3391.1 | 416.6 | 567.1 | 594.2 | 600.6 | 599 | 358.5 | 330.2 | 434.1
3567.1 | 3392.1 | 415.6 | 566.6 | 593.6 | 599.9 | 598.4 | 358 | 329.7 | 433.6
3568.1 | 3393.1 | 414.7 | 566.1 | 592.9 | 599.3 | 598 | 357.4 | 329.3 | 433
3569.1 | 3394.1 | 413.6 | 565.6 | 592.4 | 598.7 | 597.4 | 356.9 | 328.9 | 432.4
3570.1 | 3395.1 | 412.6 | 564.9 | 591.9 | 598 | 596.7 | 356.3 | 328.5 | 431.8
3571.1 | 3396.1 | 411.6 | 564.5 | 591.2 | 597.4 | 596.3 | 355.9 | 328.1 | 431.3
3572.1 | 3397.1 | 410.5 | 564 | 590.6 | 596.8 | 595.9 | 355.4 | 327.9 | 430.7
3573.1 | 3398.1 | 409.5 | 563.4 | 590.1 | 596.2 | 595.4 | 355 | 327.4 | 430.3
3574.1 | 3399.1 | 408.7 | 562.9 | 589.5 | 595.6 | 594.9 | 354.5 | 327 | 429.8
3575.1 | 3400.1 | 407.9 | 562.4 | 588.8 | 595 | 594.5 | 354 | 326.6 | 429.2
3576.1 | 3401.1 | 407 | 561.9 | 588.2 | 594.4 | 594 | 353.4 | 326.2 | 428.6
3577.1 | 3402.1 | 406.1 | 561.2 | 587.7 | 593.7 | 593.4 | 352.8 | 325.8 | 428
3578.1 | 3403.1 | 405.1 | 560.8 | 586.9 | 593.2 | 593.1 | 352.3 | 325.4 | 427.5
3579.1 | 3404.1 | 404.2 | 560.3 | 586.3 | 592.6 | 592.5 | 351.8 | 325 | 427
3580.1 | 3405.1 | 403.1 | 559.7 | 585.8 | 591.8 | 591.9 | 351.3 | 324.6 | 426.5
3581.1 | 3406.1 | 402 | 559.1 | 585.1 | 591.1 | 591.4 | 350.9 | 324.2 | 425.8
3582.1 | 3407.1 | 401.1 | 558.5 | 584.4 | 590.4 | 591 | 350.5 | 323.9 | 425.3
3583.1 | 3408.1 | 400.2 | 557.9 | 583.8 | 589.7 | 590.4 | 350.1 | 323.5 | 425
3584.1 | 3409.1 | 399.3 | 557.2 | 583.3 | 588.8 | 589.7 | 349.7 | 323.1 | 424.2
3585.1 | 3410.1 | 398.4 | 556.6 | 582.6 | 588 | 589.1 | 349.4 | 322.7 | 423.2
3586.1 | 3411.1 | 397.6 | 555.9 | 581.9 | 587.2 | 588.4 | 348.9 | 322.4 | 422.6
3587.1 | 3412.1 | 396.8 | 555.2 | 581.4 | 586.4 | 587.5 | 348.4 | 322 | 422.1
3588.1 | 3413.1 | 395.9 | 554.6 | 580.7 | 585.5 | 586.8 | 347.8 | 321.6 | 421.5
3589.1 | 3414.1 | 395.1 | 553.9 | 580 | 584.7 | 586.1 | 347.1 | 321.2 | 421
3590.1 | 3415.1 | 394.3 | 553.2 | 579.3 | 583.9 | 585.3 | 346.6 | 320.8 | 420.4
3591.1 | 3416.1 | 393.4 | 552.5 | 578.8 | 583 | 584.5 | 346.1 | 320.5 | 419.8
3592.1 | 3417.1 | 392.6 | 551.7 | 578.4 | 582 | 583.4 | 345.6 | 320.1 | 419.2
3593.1 | 3418.1 | 391.5 | 550.9 | 578 | 581 | 582.5 | 345.1 | 319.7 | 418.4
3594.1 | 3419.1 | 390.6 | 550.2 | 577.4 | 580 | 581.8 | 344.5 | 319.4 | 417.7
3595.1 | 3420.1 | 389.7 | 549.6 | 576.7 | 579.1 | 581.2 | 344 | 319 | 417.1
3596.1 | 3421.1 | 388.7 | 549 | 576 | 578.2 | 580.6 | 343.6 | 318.7 | 416.5
3597.1 | 3422.1 | 387.7 | 548.3 | 575.3 | 577.3 | 580 | 343.1 | 318.3 | 415.9
3598.1 | 3423.1 | 386.8 | 547.7 | 574.7 | 576.3 | 579.3 | 342.7 | 317.9 | 415.3
3599.1 | 3424.1 | 386 | 547.1 | 573.9 | 575.4 | 578.8 | 342.2 | 317.6 | 414.7
3600.1 | 3425.1 | 385.3 | 546.6 | 573.2 | 574.5 | 578.3 | 341.8 | 317.2 | 414
3601.1 | 3426.1 | 384.4 | 545.9 | 572.5 | 573.5 | 577.7 | 341.3 | 316.8 | 413.3
3602.1 | 3427.1 | 383.5 | 545.4 | 571.8 | 572.6 | 577.2 | 340.9 | 316.5 | 412.7
3603.1 | 3428.1 | 382.5 | 544.8 | 571.1 | 571.8 | 576.8 | 340.4 | 316.2 | 412.1
3604.1 | 3429.1 | 381.6 | 544.3 | 570.3 | 570.9 | 576.2 | 339.9 | 315.8 | 411.5
3605.1 | 3430.1 | 380.7 | 543.6 | 569.7 | 570.1 | 575.6 | 339.5 | 315.4 | 411
3606.1 | 3431.1 | 379.9 | 543.1 | 568.9 | 569.3 | 575.3 | 339.1 | 315 | 410.4
3607.1 | 3432.1 | 379.1 | 542.5 | 568.1 | 568.5 | 574.8 | 338.6 | 314.6 | 410
3608.1 | 3433.1 | 378.1 | 541.9 | 567.5 | 567.6 | 574.2 | 338.1 | 314.3 | 409.5
3609.1 | 3434.1 | 377.3 | 541.3 | 566.7 | 566.8 | 573.7 | 337.8 | 313.9 | 408.9
3610.1 | 3435.1 | 376.4 | 540.8 | 565.9 | 566.1 | 573.2 | 337.4 | 313.5 | 408.4
3611.1 | 3436.1 | 375.6 | 540.2 | 565.1 | 565.2 | 572.6 | 336.9 | 313.2 | 407.8
3612.1 | 3437.1 | 374.8 | 539.5 | 564.5 | 564.4 | 571.8 | 336.5 | 312.8 | 407.2
3613.1 | 3438.1 | 373.9 | 539 | 563.6 | 563.6 | 571.3 | 335.9 | 312.4 | 406.6
3614.1 | 3439.1 | 372.9 | 538.4 | 562.8 | 562.7 | 570.6 | 335.3 | 312 | 405.9
3615.1 | 3440.1 | 372.1 | 537.7 | 562.2 | 561.8 | 569.8 | 334.9 | 311.6 | 405
3616.1 | 3441.1 | 371.3 | 537.1 | 561.4 | 560.9 | 569 | 334.4 | 311.2 | 404.2
3617.1 | 3442.1 | 370.6 | 536.5 | 560.6 | 560 | 568.3 | 334.1 | 310.8 | 403.6
3618.1 | 3443.1 | 369.9 | 535.9 | 559.8 | 559 | 567.6 | 333.8 | 310.4 | 403.1
3619.1 | 3444.1 | 369.3 | 535.1 | 559.2 | 558.1 | 566.8 | 333.4 | 310.1 | 402.5
3620.1 | 3445.1 | 368.7 | 534.5 | 558.3 | 557.2 | 566.3 | 332.9 | 309.7 | 401.8
3621.1 | 3446.1 | 368 | 533.9 | 557.6 | 556.3 | 565.6 | 332.5 | 309.4 | 401
3622.1 | 3447.1 | 367.2 | 533.2 | 556.9 | 555.4 | 564.8 | 332 | 309 | 400.3
3623.1 | 3448.1 | 366.3 | 532.6 | 556.1 | 554.5 | 564.1 | 331.7 | 308.6 | 399.7
3624.1 | 3449.1 | 365.4 | 532 | 555.3 | 553.6 | 563.5 | 331.4 | 308.3 | 399.1
3625.1 | 3450.1 | 364.5 | 531.3 | 554.5 | 552.7 | 562.8 | 331.2 | 308 | 398.5
3626.1 | 3451.1 | 363.6 | 530.6 | 553.8 | 551.8 | 562 | 330.9 | 307.6 | 398
3627.1 | 3452.1 | 362.8 | 530 | 553 | 550.9 | 561.4 | 330.6 | 307.3 | 397.6
3628.1 | 3453.1 | 362 | 529.4 | 552.2 | 550.1 | 560.8 | 330.2 | 306.9 | 396.9
3629.1 | 3454.1 | 361.2 | 528.8 | 551.5 | 549.2 | 560 | 329.8 | 306.5 | 396.2
3630.1 | 3455.1 | 360.5 | 528.2 | 550.7 | 548.3 | 559.5 | 329.3 | 306.2 | 395.6
3631.1 | 3456.1 | 359.7 | 527.6 | 549.9 | 547.5 | 559 | 328.8 | 305.8 | 394.9
3632.1 | 3457.1 | 358.9 | 527 | 549.2 | 546.6 | 558.4 | 328.3 | 305.4 | 394.3
3633.1 | 3458.1 | 358.1 | 526.4 | 548.5 | 545.7 | 557.8 | 327.7 | 305 | 393.6
3634.1 | 3459.1 | 357.4 | 525.9 | 547.6 | 544.9 | 557.3 | 327.2 | 304.6 | 393.1
3635.1 | 3460.1 | 356.6 | 525.3 | 546.8 | 544.1 | 556.8 | 326.7 | 304.3 | 392.6
3636.1 | 3461.1 | 355.9 | 524.6 | 546.1 | 543.3 | 556.1 | 326.2 | 303.9 | 392
3637.1 | 3462.1 | 355.1 | 524.1 | 545.3 | 542.5 | 555.5 | 325.7 | 303.4 | 391.4
3638.1 | 3463.1 | 354.3 | 523.5 | 544.4 | 541.8 | 555 | 325.3 | 303 | 390.9
3639.1 | 3464.1 | 353.6 | 522.9 | 543.6 | 541 | 554.4 | 324.9 | 302.6 | 390.3
3640.1 | 3465.1 | 352.9 | 522.2 | 542.9 | 540.3 | 553.7 | 324.4 | 302.2 | 389.7
3641.1 | 3466.1 | 352.2 | 521.6 | 542 | 539.6 | 553.2 | 323.9 | 301.8 | 389.2
3642.1 | 3467.1 | 351.5 | 521 | 541.1 | 538.8 | 552.7 | 323.5 | 301.4 | 388.6
3643.1 | 3468.1 | 350.8 | 520.3 | 540.4 | 538.1 | 552.1 | 323.1 | 301.1 | 387.9
3644.1 | 3469.1 | 350.2 | 519.6 | 539.6 | 537.4 | 551.5 | 322.7 | 300.7 | 387.4
3645.1 | 3470.1 | 349.5 | 519 | 538.7 | 536.7 | 551.1 | 322.3 | 300.3 | 386.9
3646.1 | 3471.1 | 348.6 | 518.3 | 537.9 | 536 | 550.5 | 321.9 | 300 | 386.5
3647.1 | 3472.1 | 347.7 | 517.6 | 537.1 | 535.3 | 549.8 | 321.4 | 299.6 | 386.1
3648.1 | 3473.1 | 347.1 | 517 | 536.2 | 534.7 | 549.3 | 320.8 | 299.2 | 385.6
3649.1 | 3474.1 | 346.4 | 516.3 | 535.4 | 534 | 548.8 | 320.4 | 298.9 | 385
3650.1 | 3475.1 | 345.7 | 515.6 | 534.6 | 533.2 | 548.1 | 319.9 | 298.5 | 384.5
3651.1 | 3476.1 | 345.1 | 514.9 | 533.8 | 532.4 | 547.6 | 319.5 | 298.1 | 384.1
3652.1 | 3477.1 | 344.5 | 514.2 | 533 | 531.6 | 547 | 319 | 297.8 | 383.6
3653.1 | 3478.1 | 343.8 | 513.5 | 532.2 | 530.8 | 546.4 | 318.5 | 297.6 | 383.2
3654.1 | 3479.1 | 343.1 | 512.8 | 531.5 | 529.8 | 545.6 | 318 | 297.3 | 382.7
3655.1 | 3480.1 | 342.5 | 512.2 | 530.6 | 529 | 545.1 | 317.5 | 296.8 | 382.2
3656.1 | 3481.1 | 341.8 | 511.5 | 529.8 | 528.1 | 544.4 | 317.1 | 296.5 | 381.7
3657.1 | 3482.1 | 341.1 | 510.8 | 529 | 527.1 | 543.6 | 316.7 | 296.1 | 381.1
3658.1 | 3483.1 | 340.3 | 510.1 | 528.3 | 526.2 | 542.9 | 316.3 | 295.8 | 380.4
3659.1 | 3484.1 | 339.5 | 509.5 | 527.4 | 525.4 | 542.2 | 315.9 | 295.4 | 379.8
3660.1 | 3485.1 | 338.7 | 508.8 | 526.6 | 524.5 | 541.4 | 315.4 | 295 | 379.2
3661.1 | 3486.1 | 337.9 | 508.1 | 525.9 | 523.6 | 540.4 | 314.9 | 294.6 | 378.7
3662.1 | 3487.1 | 337.3 | 507.4 | 525.1 | 522.7 | 539.6 | 314.3 | 294.3 | 378.1
3663.1 | 3488.1 | 336.6 | 506.7 | 524.2 | 521.9 | 538.8 | 313.8 | 294 | 377.5
3664.1 | 3489.1 | 336 | 506 | 523.5 | 521 | 537.9 | 313.4 | 293.7 | 377
3665.1 | 3490.1 | 335.3 | 505.3 | 522.7 | 520.2 | 537.2 | 312.9 | 293.2 | 376.4
3666.1 | 3491.1 | 334.6 | 504.7 | 521.9 | 519.3 | 536.6 | 312.3 | 292.9 | 375.9
3667.1 | 3492.1 | 333.9 | 504 | 521.1 | 518.5 | 536 | 311.8 | 292.5 | 375.3
3668.1 | 3493.1 | 333.2 | 503.3 | 520.4 | 517.7 | 535.3 | 311.4 | 292.3 | 374.9
3669.1 | 3494.1 | 332.6 | 502.7 | 519.4 | 516.9 | 534.8 | 311 | 292 | 374.3
3670.1 | 3495.1 | 332 | 502.1 | 518.6 | 516.2 | 534.3 | 310.7 | 291.6 | 373.7
3671.1 | 3496.1 | 331.2 | 501.5 | 517.9 | 515.5 | 533.8 | 310.4 | 291.2 | 373
3672.1 | 3497.1 | 330.6 | 500.8 | 517.1 | 514.8 | 533.3 | 310.1 | 290.7 | 372.4
3673.1 | 3498.1 | 329.9 | 500.2 | 516.2 | 514.3 | 532.8 | 309.7 | 290.2 | 371.8
3674.1 | 3499.1 | 329.2 | 499.8 | 515.3 | 513.7 | 532.2 | 309.4 | 289.9 | 371.3
3675.1 | 3500.1 | 328.6 | 499.1 | 514.6 | 513.1 | 531.6 | 309 | 289.4 | 370.8
3676.1 | 3501.1 | 327.9 | 498.5 | 513.7 | 512.5 | 531 | 308.7 | 288.9 | 370.3
3677.1 | 3502.1 | 327.2 | 497.9 | 512.9 | 511.9 | 530.4 | 308.3 | 288.6 | 369.7
3678.1 | 3503.1 | 326.6 | 497.3 | 512.2 | 511.3 | 529.7 | 308 | 288.1 | 369
3679.1 | 3504.1 | 325.9 | 496.7 | 511.4 | 510.6 | 529.1 | 307.6 | 287.7 | 368.6
3680.1 | 3505.1 | 325.2 | 496.1 | 510.6 | 510 | 528.6 | 307.3 | 287.3 | 368.1
3681.1 | 3506.1 | 324.5 | 495.5 | 509.8 | 509.4 | 528 | 306.9 | 287 | 367.6
3682.1 | 3507.1 | 323.8 | 494.8 | 509.1 | 508.7 | 527.4 | 306.6 | 286.7 | 366.9
3683.1 | 3508.1 | 323.1 | 494.2 | 508.2 | 508 | 527 | 306.2 | 286.3 | 366.3
3684.1 | 3509.1 | 322.3 | 493.6 | 507.5 | 507.4 | 526.5 | 305.8 | 286 | 365.7
3685.1 | 3510.1 | 321.5 | 492.9 | 506.8 | 506.7 | 526 | 305.5 | 285.8 | 365.2
3686.1 | 3511.1 | 320.8 | 492.3 | 506 | 506 | 525.5 | 305.1 | 285.5 | 364.8
3687.1 | 3512.1 | 320.2 | 491.6 | 505.2 | 505.4 | 525.1 | 304.7 | 285.3 | 364.4
3688.1 | 3513.1 | 319.8 | 491 | 504.4 | 504.8 | 524.5 | 304.3 | 285 | 363.8
3689.1 | 3514.1 | 319.2 | 490.2 | 503.8 | 504.1 | 523.8 | 303.9 | 284.7 | 363.3
3690.1 | 3515.1 | 318.6 | 489.6 | 502.9 | 503.5 | 523.4 | 303.6 | 284.4 | 362.8
3691.1 | 3516.1 | 318 | 488.9 | 502.2 | 502.9 | 522.9 | 303.2 | 284 | 362.2
3692.1 | 3517.1 | 317.4 | 488.2 | 501.5 | 502.2 | 522.3 | 302.7 | 283.6 | 361.7
3693.1 | 3518.1 | 316.8 | 487.5 | 500.8 | 501.5 | 521.7 | 302.3 | 283.3 | 361.1
3694.1 | 3519.1 | 316.2 | 486.9 | 500.1 | 500.9 | 521.2 | 301.9 | 282.9 | 360.5
3695.1 | 3520.1 | 315.5 | 486.2 | 499.3 | 500.1 | 520.6 | 301.5 | 282.5 | 360
3696.1 | 3521.1 | 314.8 | 485.5 | 498.7 | 499.5 | 519.8 | 301.1 | 282.1 | 359.6
3697.1 | 3522.1 | 314.1 | 484.8 | 497.9 | 498.7 | 519.2 | 300.7 | 281.8 | 359.2
3698.1 | 3523.1 | 313.6 | 484.1 | 497.2 | 498 | 518.5 | 300.2 | 281.5 | 358.8
3699.1 | 3524.1 | 313.1 | 483.4 | 496.6 | 497.1 | 517.7 | 299.7 | 281.1 | 358.3
3700.1 | 3525.1 | 312.6 | 482.7 | 495.9 | 496.3 | 517 | 299.4 | 280.8 | 357.9
3701.1 | 3526.1 | 312 | 482.1 | 495.1 | 495.5 | 516.4 | 299 | 280.5 | 357.4
3702.1 | 3527.1 | 311.4 | 481.4 | 494.4 | 494.7 | 515.7 | 298.6 | 280.2 | 357
3703.1 | 3528.1 | 310.8 | 480.6 | 493.9 | 493.8 | 514.9 | 298.1 | 279.9 | 356.5
3704.1 | 3529.1 | 310.2 | 480 | 493.1 | 493 | 514.4 | 297.7 | 279.6 | 356.1
3705.1 | 3530.1 | 309.7 | 479.4 | 492.4 | 492.2 | 513.8 | 297.4 | 279.3 | 355.6
3706.1 | 3531.1 | 309 | 478.7 | 491.8 | 491.4 | 513.1 | 296.9 | 278.9 | 355
3707.1 | 3532.1 | 308.3 | 478 | 491.1 | 490.6 | 512.5 | 296.6 | 278.6 | 354.3
3708.1 | 3533.1 | 307.7 | 477.4 | 490.4 | 489.8 | 512 | 296.1 | 278.2 | 353.7
3709.1 | 3534.1 | 307.1 | 476.7 | 489.7 | 489 | 511.4 | 295.7 | 277.9 | 353.2
3710.1 | 3535.1 | 306.6 | 476 | 489.1 | 488.2 | 510.7 | 295.3 | 277.6 | 352.6
3711.1 | 3536.1 | 306.2 | 475.4 | 488.4 | 487.5 | 510.2 | 294.9 | 277.3 | 352.2
3712.1 | 3537.1 | 305.7 | 474.8 | 487.7 | 486.7 | 509.6 | 294.5 | 276.9 | 351.8
3713.1 | 3538.1 | 305.2 | 474.1 | 487.1 | 486 | 508.9 | 294.2 | 276.6 | 351.3
3714.1 | 3539.1 | 304.6 | 473.5 | 486.4 | 485.3 | 508.2 | 293.8 | 276.3 | 350.9
3715.1 | 3540.1 | 304 | 472.9 | 485.7 | 484.6 | 507.7 | 293.5 | 276 | 350.4
3716.1 | 3541.1 | 303.4 | 472.2 | 485 | 483.9 | 507 | 293.1 | 275.6 | 349.9
3717.1 | 3542.1 | 302.8 | 471.5 | 484.4 | 483.2 | 506.3 | 292.7 | 275.3 | 349.4
3718.1 | 3543.1 | 302.2 | 470.9 | 483.6 | 482.6 | 505.8 | 292.3 | 275 | 348.9
3719.1 | 3544.1 | 301.7 | 470.2 | 482.9 | 481.9 | 505.2 | 291.9 | 274.7 | 348.3
3720.1 | 3545.1 | 301.1 | 469.5 | 482.4 | 481.1 | 504.5 | 291.5 | 274.4 | 347.8
3721.1 | 3546.1 | 300.6 | 468.9 | 481.7 | 480.4 | 503.8 | 291.1 | 274.1 | 347.4
3722.1 | 3547.1 | 300 | 468.2 | 481 | 479.7 | 503.3 | 290.7 | 273.8 | 347
3723.1 | 3548.1 | 299.5 | 467.5 | 480.3 | 479 | 502.6 | 290.3 | 273.5 | 346.5
3724.1 | 3549.1 | 299 | 466.8 | 479.8 | 478.2 | 501.8 | 290 | 273.2 | 345.9
3725.1 | 3550.1 | 298.5 | 466.2 | 479 | 477.5 | 501.1 | 289.6 | 272.9 | 345.5
3726.1 | 3551.1 | 297.9 | 465.5 | 478.4 | 476.7 | 500.4 | 289.2 | 272.6 | 344.9
3727.1 | 3552.1 | 297.3 | 464.8 | 477.8 | 475.9 | 499.7 | 288.8 | 272.3 | 344.5
3728.1 | 3553.1 | 296.8 | 464.2 | 477.2 | 475.2 | 499 | 288.5 | 272 | 344
3729.1 | 3554.1 | 296.2 | 463.6 | 476.4 | 474.5 | 498.4 | 288.1 | 271.6 | 343.5
3730.1 | 3555.1 | 295.7 | 463 | 475.8 | 473.8 | 497.7 | 287.8 | 271.3 | 342.9
3731.1 | 3556.1 | 295.1 | 462.3 | 475.2 | 473.1 | 496.9 | 287.4 | 271 | 342.2
3732.1 | 3557.1 | 294.4 | 461.7 | 474.5 | 472.5 | 496.4 | 287.1 | 270.7 | 341.7
3733.1 | 3558.1 | 293.8 | 461.1 | 473.8 | 471.9 | 495.8 | 286.7 | 270.4 | 341.2
3734.1 | 3559.1 | 293.3 | 460.4 | 473.2 | 471.3 | 495.1 | 286.3 | 270.1 | 340.8
3735.1 | 3560.1 | 292.9 | 459.7 | 472.5 | 470.7 | 494.5 | 285.9 | 269.8 | 340.5
3736.1 | 3561.1 | 292.4 | 459.2 | 471.8 | 470.2 | 494 | 285.5 | 269.5 | 340.2
3737.1 | 3562.1 | 291.8 | 458.5 | 471.1 | 469.6 | 493.4 | 285.2 | 269.1 | 339.7
3738.1 | 3563.1 | 291.2 | 457.8 | 470.6 | 468.9 | 492.7 | 284.8 | 268.9 | 339.2
3739.1 | 3564.1 | 290.6 | 457.2 | 469.9 | 468.3 | 492.2 | 284.4 | 268.6 | 338.6
3740.1 | 3565.1 | 290.2 | 456.6 | 469.2 | 467.7 | 491.5 | 284.1 | 268.3 | 338.1
3741.1 | 3566.1 | 289.6 | 456 | 468.6 | 467 | 490.8 | 283.7 | 268 | 337.6
3742.1 | 3567.1 | 289 | 455.3 | 468 | 466.4 | 490.1 | 283.4 | 267.7 | 337.2
3743.1 | 3568.1 | 288.4 | 454.8 | 467.2 | 465.8 | 489.6 | 283 | 267.4 | 336.8
3744.1 | 3569.1 | 287.8 | 454.1 | 466.6 | 465.1 | 488.9 | 282.7 | 267.1 | 336.3
3745.1 | 3570.1 | 287.3 | 453.5 | 466 | 464.5 | 488.2 | 282.3 | 266.8 | 335.9
3746.1 | 3571.1 | 286.8 | 452.9 | 465.3 | 463.9 | 487.7 | 281.9 | 266.5 | 335.4
3747.1 | 3572.1 | 286.2 | 452.3 | 464.6 | 463.3 | 487.1 | 281.5 | 266.2 | 334.9
3748.1 | 3573.1 | 285.6 | 451.6 | 464 | 462.6 | 486.3 | 281.1 | 266 | 334.5
3749.1 | 3574.1 | 285.1 | 451 | 463.4 | 461.9 | 485.6 | 280.7 | 265.7 | 333.9
3750.1 | 3575.1 | 284.6 | 450.4 | 462.6 | 461.2 | 485 | 280.3 | 265.4 | 333.4
3751.1 | 3576.1 | 284.1 | 449.8 | 461.9 | 460.5 | 484.3 | 280 | 265 | 333
3752.1 | 3577.1 | 283.7 | 449.1 | 461.4 | 459.7 | 483.5 | 279.6 | 264.8 | 332.6
3753.1 | 3578.1 | 283.2 | 448.5 | 460.6 | 459 | 482.9 | 279.3 | 264.6 | 332.1
3754.1 | 3579.1 | 282.7 | 447.9 | 459.9 | 458.3 | 482.2 | 278.9 | 264.3 | 331.7
3755.1 | 3580.1 | 282.2 | 447.2 | 459.3 | 457.5 | 481.4 | 278.6 | 264 | 331.3
3756.1 | 3581.1 | 281.7 | 446.6 | 458.6 | 456.8 | 480.7 | 278.2 | 263.7 | 330.9
3757.1 | 3582.1 | 281.2 | 446.1 | 457.9 | 456.1 | 480.2 | 277.9 | 263.4 | 330.4
3758.1 | 3583.1 | 280.7 | 445.4 | 457.2 | 455.4 | 479.5 | 277.6 | 263.1 | 330
3759.1 | 3584.1 | 280.3 | 444.7 | 456.6 | 454.7 | 478.6 | 277.2 | 262.8 | 329.6
3760.1 | 3585.1 | 279.8 | 444.1 | 455.8 | 454 | 478 | 276.9 | 262.6 | 329.1
3761.1 | 3586.1 | 279.4 | 443.5 | 455.1 | 453.3 | 477.4 | 276.6 | 262.2 | 328.7
3762.1 | 3587.1 | 278.8 | 442.8 | 454.5 | 452.5 | 476.6 | 276.2 | 261.9 | 328.2
3763.1 | 3588.1 | 278.2 | 442.1 | 453.8 | 451.8 | 476 | 275.8 | 261.6 | 327.6
3764.1 | 3589.1 | 277.7 | 441.5 | 453.1 | 451.1 | 475.4 | 275.4 | 261.4 | 327.1
3765.1 | 3590.1 | 277.2 | 440.8 | 452.4 | 450.3 | 474.7 | 275 | 261.1 | 326.8
3766.1 | 3591.1 | 276.8 | 440.1 | 451.8 | 449.6 | 474 | 274.6 | 260.8 | 326.3
3767.1 | 3592.1 | 276.3 | 439.5 | 451 | 448.8 | 473.4 | 274.2 | 260.5 | 325.9
3768.1 | 3593.1 | 275.8 | 438.8 | 450.3 | 448.1 | 472.7 | 273.9 | 260.2 | 325.6
3769.1 | 3594.1 | 275.2 | 438.1 | 449.7 | 447.2 | 471.9 | 273.6 | 259.8 | 325.1
3770.1 | 3595.1 | 274.7 | 437.5 | 449 | 446.4 | 471.2 | 273.2 | 259.5 | 324.5
3771.1 | 3596.1 | 274.3 | 436.9 | 448.2 | 445.7 | 470.6 | 272.9 | 259.3 | 324
3772.1 | 3597.1 | 273.9 | 436.2 | 447.6 | 444.9 | 469.9 | 272.5 | 259 | 323.5
3773.1 | 3598.1 | 273.5 | 435.5 | 446.9 | 444.1 | 469.1 | 272.1 | 258.6 | 323.1
3774.1 | 3599.1 | 272.9 | 434.9 | 446.1 | 443.4 | 468.5 | 271.8 | 258.3 | 322.7
3775.1 | 3600.1 | 272.4 | 434.3 | 445.4 | 442.6 | 467.9 | 271.4 | 258 | 322.4
3776.1 | 3601.1 | 271.9 | 433.6 | 444.8 | 441.8 | 467.2 | 271.1 | 257.7 | 321.8
3777.1 | 3602.1 | 271.4 | 432.9 | 444.1 | 441 | 466.5 | 270.7 | 257.3 | 321.3
3778.1 | 3603.1 | 270.9 | 432.3 | 443.3 | 440.3 | 466 | 270.5 | 257 | 320.9
3779.1 | 3604.1 | 270.4 | 431.6 | 442.6 | 439.6 | 465.4 | 270.3 | 256.6 | 320.3
3780.1 | 3605.1 | 270 | 430.9 | 441.9 | 438.8 | 464.6 | 270.1 | 256.3 | 320
3781.1 | 3606.1 | 269.5 | 430.3 | 441.1 | 438 | 464.1 | 269.7 | 256 | 319.6
3782.1 | 3607.1 | 269 | 429.7 | 440.4 | 437.2 | 463.5 | 269.4 | 255.7 | 319.1
3783.1 | 3608.1 | 268.5 | 429 | 439.7 | 436.4 | 462.7 | 269 | 255.4 | 318.7
3784.1 | 3609.1 | 268.1 | 428.3 | 439 | 435.6 | 462 | 268.7 | 255.1 | 318.2
3785.1 | 3610.1 | 267.6 | 427.7 | 438.2 | 434.9 | 461.4 | 268.4 | 254.7 | 317.8
3786.1 | 3611.1 | 267.1 | 427.1 | 437.5 | 434.1 | 460.6 | 268 | 254.4 | 317.2
3787.1 | 3612.1 | 266.7 | 426.4 | 436.9 | 433.3 | 459.7 | 267.7 | 254.1 | 316.7
3788.1 | 3613.1 | 266.2 | 425.8 | 436.1 | 432.6 | 459 | 267.3 | 253.9 | 316.3
3789.1 | 3614.1 | 265.7 | 425.2 | 435.3 | 431.8 | 458.2 | 267 | 253.7 | 315.9
3790.1 | 3615.1 | 265.2 | 424.5 | 434.7 | 431 | 457.4 | 266.6 | 253.4 | 315.4
3791.1 | 3616.1 | 264.7 | 423.8 | 434 | 430.3 | 456.6 | 266.3 | 253.1 | 315.1
3792.1 | 3617.1 | 264.3 | 423.2 | 433.2 | 429.6 | 455.9 | 266 | 252.8 | 314.7
3793.1 | 3618.1 | 263.8 | 422.5 | 432.5 | 428.8 | 455.2 | 265.7 | 252.5 | 314.3
3794.1 | 3619.1 | 263.4 | 421.8 | 431.9 | 428 | 454.3 | 265.3 | 252.2 | 313.9
3795.1 | 3620.1 | 263 | 421.2 | 431.1 | 427.3 | 453.6 | 265 | 251.9 | 313.5
3796.1 | 3621.1 | 262.5 | 420.5 | 430.3 | 426.5 | 452.8 | 264.7 | 251.6 | 313.1
3797.1 | 3622.1 | 262.1 | 419.8 | 429.7 | 425.6 | 451.9 | 264.4 | 251.3 | 312.8
3798.1 | 3623.1 | 261.7 | 419.2 | 429 | 424.8 | 451.1 | 264 | 251 | 312.5
3799.1 | 3624.1 | 261.2 | 418.5 | 428.2 | 423.9 | 450.4 | 263.7 | 250.8 | 312.1
3800.1 | 3625.1 | 260.8 | 417.8 | 427.5 | 423 | 449.5 | 263.3 | 250.5 | 311.8
3801.1 | 3626.1 | 260.4 | 417 | 426.8 | 422 | 448.6 | 263 | 250.2 | 311.5
3802.1 | 3627.1 | 260 | 416.3 | 426 | 421.1 | 447.9 | 262.6 | 249.9 | 311
3803.1 | 3628.1 | 259.5 | 415.6 | 425.2 | 420.2 | 447.1 | 262.2 | 249.5 | 310.6
3804.1 | 3629.1 | 259 | 414.9 | 424.6 | 419.2 | 446.2 | 261.8 | 249.3 | 310.2
3805.1 | 3630.1 | 258.6 | 414.1 | 423.9 | 418.2 | 445.5 | 261.5 | 249 | 309.8
3806.1 | 3631.1 | 258.2 | 413.5 | 423.1 | 417.3 | 444.8 | 261.3 | 248.7 | 309.3
3807.1 | 3632.1 | 257.7 | 412.7 | 422.3 | 416.4 | 444 | 261 | 248.5 | 308.8
3808.1 | 3633.1 | 257.4 | 411.9 | 421.7 | 415.4 | 443.2 | 260.7 | 248.2 | 308.4
3809.1 | 3634.1 | 256.9 | 411.3 | 420.9 | 414.6 | 442.5 | 260.4 | 247.9 | 307.9
3810.1 | 3635.1 | 256.5 | 410.6 | 420.1 | 413.8 | 441.8 | 260.1 | 247.7 | 307.5
3811.1 | 3636.1 | 256.1 | 409.8 | 419.4 | 412.9 | 441 | 259.7 | 247.4 | 307
3812.1 | 3637.1 | 255.7 | 409.1 | 418.7 | 412.1 | 440.3 | 259.4 | 247.1 | 306.5
3813.1 | 3638.1 | 255.3 | 408.5 | 417.8 | 411.4 | 439.6 | 259 | 246.8 | 306
3814.1 | 3639.1 | 255 | 407.7 | 417 | 410.6 | 438.9 | 258.7 | 246.5 | 305.7
3815.1 | 3640.1 | 254.6 | 407 | 416.4 | 409.7 | 438 | 258.4 | 246.2 | 305.3
3816.1 | 3641.1 | 254.1 | 406.3 | 415.5 | 408.9 | 437.4 | 258 | 245.9 | 304.7
3817.1 | 3642.1 | 253.7 | 405.6 | 414.7 | 408.2 | 436.7 | 257.7 | 245.7 | 304.1
3818.1 | 3643.1 | 253.3 | 404.8 | 414 | 407.3 | 435.9 | 257.4 | 245.4 | 303.6
3819.1 | 3644.1 | 252.9 | 404.1 | 413.2 | 406.5 | 435.2 | 257 | 245.1 | 303.1
3820.1 | 3645.1 | 252.5 | 403.5 | 412.4 | 405.7 | 434.5 | 256.7 | 244.8 | 302.8
3821.1 | 3646.1 | 252.1 | 402.7 | 411.6 | 404.8 | 433.8 | 256.3 | 244.5 | 302.5
3822.1 | 3647.1 | 251.6 | 402 | 410.9 | 403.9 | 433 | 255.9 | 244.3 | 302.2
3823.1 | 3648.1 | 251.2 | 401.3 | 410.1 | 403.2 | 432.4 | 255.5 | 244.1 | 301.8
3824.1 | 3649.1 | 250.8 | 400.6 | 409.3 | 402.4 | 431.7 | 255 | 243.8 | 301.5
3825.1 | 3650.1 | 250.3 | 399.8 | 408.6 | 401.5 | 430.9 | 254.6 | 243.5 | 301
3826.1 | 3651.1 | 249.9 | 399.1 | 407.8 | 400.7 | 430.2 | 254.2 | 243.3 | 300.6
3827.1 | 3652.1 | 249.4 | 398.4 | 407 | 400 | 429.6 | 254 | 243 | 300
3828.1 | 3653.1 | 248.9 | 397.7 | 406.2 | 399.2 | 428.8 | 253.7 | 242.7 | 299.7
3829.1 | 3654.1 | 248.5 | 396.9 | 405.5 | 398.3 | 427.9 | 253.4 | 242.4 | 299.4
3830.1 | 3655.1 | 248.2 | 396.2 | 404.7 | 397.5 | 427.3 | 253.1 | 242.1 | 299
3831.1 | 3656.1 | 247.8 | 395.5 | 403.9 | 396.8 | 426.6 | 252.9 | 241.8 | 298.5
3832.1 | 3657.1 | 247.4 | 394.7 | 403.2 | 395.9 | 425.7 | 252.6 | 241.6 | 297.9
3833.1 | 3658.1 | 246.9 | 393.9 | 402.4 | 395.2 | 424.9 | 252.3 | 241.3 | 297.5
3834.1 | 3659.1 | 246.6 | 393.2 | 401.6 | 394.4 | 424.1 | 252 | 241 | 297.1
3835.1 | 3660.1 | 246.2 | 392.4 | 400.8 | 393.6 | 423.3 | 251.6 | 240.8 | 296.9
3836.1 | 3661.1 | 245.7 | 391.6 | 400.2 | 392.7 | 422.3 | 251.3 | 240.6 | 296.6
3837.1 | 3662.1 | 245.2 | 390.9 | 399.3 | 391.8 | 421.6 | 251 | 240.4 | 296
3838.1 | 3663.1 | 244.7 | 390.2 | 398.5 | 391 | 420.9 | 250.8 | 240.1 | 295.7
3839.1 | 3664.1 | 244.3 | 389.4 | 397.8 | 390 | 420.1 | 250.5 | 239.7 | 295.3
3840.1 | 3665.1 | 243.8 | 388.7 | 397.1 | 389.1 | 419.3 | 250.3 | 239.5 | 294.9
3841.1 | 3666.1 | 243.5 | 388 | 396.2 | 388.3 | 418.7 | 250 | 239.3 | 294.5
3842.1 | 3667.1 | 243.2 | 387.2 | 395.5 | 387.4 | 417.9 | 249.7 | 239 | 294
3843.1 | 3668.1 | 242.9 | 386.4 | 394.8 | 386.5 | 417 | 249.3 | 238.7 | 293.5
3844.1 | 3669.1 | 242.5 | 385.8 | 394 | 385.7 | 416.3 | 249 | 238.4 | 293
3845.1 | 3670.1 | 242 | 385 | 393.2 | 384.8 | 415.5 | 248.7 | 238.1 | 292.6
3846.1 | 3671.1 | 241.6 | 384.3 | 392.5 | 383.9 | 414.6 | 248.4 | 237.8 | 292.4
3847.1 | 3672.1 | 241.1 | 383.5 | 391.8 | 383 | 413.8 | 248.1 | 237.6 | 292.1
3848.1 | 3673.1 | 240.7 | 382.9 | 391 | 382.2 | 413.2 | 247.9 | 237.3 | 291.8
3849.1 | 3674.1 | 240.2 | 382.1 | 390.2 | 381.3 | 412.4 | 247.6 | 237 | 291.3
3850.1 | 3675.1 | 239.8 | 381.3 | 389.6 | 380.4 | 411.5 | 247.4 | 236.8 | 290.8
3851.1 | 3676.1 | 239.4 | 380.6 | 388.7 | 379.6 | 410.9 | 247.2 | 236.6 | 290.3
3852.1 | 3677.1 | 239.1 | 379.8 | 387.9 | 378.8 | 410.2 | 247 | 236.3 | 289.8
3853.1 | 3678.1 | 238.7 | 379 | 387.2 | 377.9 | 409.5 | 246.7 | 236 | 289.6
3854.1 | 3679.1 | 238.2 | 378.2 | 386.5 | 377.1 | 408.9 | 246.5 | 235.7 | 289.3
3855.1 | 3680.1 | 237.8 | 377.4 | 385.6 | 376.3 | 408.4 | 246.3 | 235.5 | 288.9
3856.1 | 3681.1 | 237.4 | 376.6 | 384.9 | 375.5 | 407.8 | 246 | 235.3 | 288.5
3857.1 | 3682.1 | 237.1 | 375.7 | 384.2 | 374.7 | 407.1 | 245.6 | 235.1 | 288.3
3858.1 | 3683.1 | 236.7 | 374.9 | 383.4 | 373.9 | 406.6 | 245.3 | 234.8 | 288
3859.1 | 3684.1 | 236.4 | 374.1 | 382.6 | 373.2 | 406.1 | 245 | 234.6 | 287.7
3860.1 | 3685.1 | 236 | 373.2 | 381.9 | 372.5 | 405.4 | 244.7 | 234.3 | 287.2
3861.1 | 3686.1 | 235.6 | 372.4 | 381.2 | 371.7 | 404.7 | 244.3 | 234 | 286.8
3862.1 | 3687.1 | 235.2 | 371.7 | 380.3 | 371 | 404 | 244 | 233.7 | 286.3
3863.1 | 3688.1 | 234.7 | 370.9 | 379.6 | 370.3 | 403.2 | 243.6 | 233.5 | 285.9
3864.1 | 3689.1 | 234.4 | 370 | 379 | 369.5 | 402.3 | 243.3 | 233.2 | 285.5
3865.1 | 3690.1 | 234 | 369.3 | 378.1 | 368.8 | 401.6 | 242.9 | 232.9 | 284.9
3866.1 | 3691.1 | 233.6 | 368.5 | 377.4 | 368 | 400.9 | 242.5 | 232.7 | 284.4
3867.1 | 3692.1 | 233.2 | 367.7 | 376.7 | 367.2 | 400 | 242.1 | 232.4 | 284
3868.1 | 3693.1 | 232.7 | 367 | 376 | 366.4 | 399.2 | 241.8 | 232.1 | 283.7
3869.1 | 3694.1 | 232.3 | 366.2 | 375.2 | 365.6 | 398.5 | 241.5 | 231.9 | 283.3
3870.1 | 3695.1 | 232 | 365.5 | 374.4 | 364.8 | 397.7 | 241.1 | 231.6 | 283
3871.1 | 3696.1 | 231.7 | 364.6 | 373.8 | 364.1 | 396.8 | 240.7 | 231.4 | 282.7
3872.1 | 3697.1 | 231.3 | 363.9 | 373 | 363.3 | 396 | 240.4 | 231.1 | 282.2
3873.1 | 3698.1 | 231 | 363.2 | 372.2 | 362.6 | 395.2 | 240.1 | 230.9 | 281.5
3874.1 | 3699.1 | 230.6 | 362.3 | 371.5 | 361.9 | 394.3 | 239.7 | 230.7 | 281.1
3875.1 | 3700.1 | 230.3 | 361.6 | 370.8 | 361.2 | 393.5 | 239.4 | 230.4 | 280.7
3876.1 | 3701.1 | 229.9 | 360.8 | 370 | 360.5 | 392.7 | 239.1 | 230.1 | 280.3
3877.1 | 3702.1 | 229.5 | 360.1 | 369.3 | 359.8 | 391.9 | 238.9 | 229.9 | 280
3878.1 | 3703.1 | 229.1 | 359.2 | 368.7 | 359.1 | 391 | 238.7 | 229.7 | 279.6
3879.1 | 3704.1 | 228.7 | 358.5 | 367.8 | 358.5 | 390.3 | 238.5 | 229.5 | 279.1
3880.1 | 3705.1 | 228.4 | 357.8 | 367.1 | 357.9 | 389.5 | 238.3 | 229.2 | 278.8
3881.1 | 3706.1 | 228.2 | 356.9 | 366.5 | 357.2 | 388.6 | 238 | 229 | 278.3
3882.1 | 3707.1 | 227.8 | 356.2 | 365.7 | 356.5 | 387.8 | 237.6 | 228.7 | 277.9
3883.1 | 3708.1 | 227.4 | 355.4 | 364.9 | 355.9 | 387.1 | 237.3 | 228.5 | 277.5
3884.1 | 3709.1 | 227 | 354.6 | 364.2 | 355.2 | 386.4 | 237.1 | 228.3 | 277.1
3885.1 | 3710.1 | 226.7 | 353.8 | 363.6 | 354.5 | 385.5 | 236.8 | 228.3 | 276.7
3886.1 | 3711.1 | 226.3 | 353 | 362.8 | 353.8 | 384.8 | 236.4 | 228 | 276.3
3887.1 | 3712.1 | 226 | 352.3 | 362.1 | 353.1 | 384.1 | 236.1 | 227.8 | 275.9
3888.1 | 3713.1 | 225.6 | 351.5 | 361.4 | 352.4 | 383.3 | 235.7 | 227.6 | 275.5
3889.1 | 3714.1 | 225.4 | 350.7 | 360.7 | 351.7 | 382.5 | 235.4 | 227.4 | 275.1
3890.1 | 3715.1 | 225.1 | 350 | 360 | 351 | 381.9 | 235 | 227.2 | 274.8
3891.1 | 3716.1 | 224.8 | 349.2 | 359.3 | 350.3 | 381.1 | 234.6 | 226.9 | 274.4
3892.1 | 3717.1 | 224.5 | 348.4 | 358.7 | 349.5 | 380.2 | 234.2 | 226.7 | 273.9
3893.1 | 3718.1 | 224.1 | 347.8 | 357.9 | 348.8 | 379.6 | 233.9 | 226.5 | 273.5
3894.1 | 3719.1 | 223.7 | 347.1 | 357.2 | 348.1 | 378.8 | 233.5 | 226.2 | 273.2
3895.1 | 3720.1 | 223.4 | 346.3 | 356.6 | 347.3 | 378 | 233.1 | 225.9 | 272.9
3896.1 | 3721.1 | 223.1 | 345.6 | 355.9 | 346.6 | 377.2 | 232.7 | 225.6 | 272.6
3897.1 | 3722.1 | 222.7 | 344.9 | 355.1 | 345.9 | 376.6 | 232.4 | 225.3 | 272.3
3898.1 | 3723.1 | 222.4 | 344.2 | 354.5 | 345.1 | 375.7 | 232 | 225.1 | 271.9
3899.1 | 3724.1 | 222 | 343.5 | 353.9 | 344.3 | 374.8 | 231.6 | 224.8 | 271.5
3900.1 | 3725.1 | 221.6 | 342.8 | 353.1 | 343.6 | 374.1 | 231.3 | 224.6 | 271.1
3901.1 | 3726.1 | 221.3 | 342.1 | 352.4 | 342.8 | 373.3 | 231 | 224.3 | 270.8
3902.1 | 3727.1 | 220.9 | 341.4 | 351.8 | 342 | 372.5 | 230.7 | 224 | 270.5
3903.1 | 3728.1 | 220.6 | 340.7 | 351.1 | 341.3 | 371.7 | 230.4 | 223.7 | 270.3
3904.1 | 3729.1 | 220.3 | 340 | 350.3 | 340.5 | 371 | 230 | 223.4 | 270.1
3905.1 | 3730.1 | 219.9 | 339.3 | 349.6 | 339.7 | 370.2 | 229.7 | 223.2 | 269.8
3906.1 | 3731.1 | 219.5 | 338.6 | 349 | 338.9 | 369.3 | 229.4 | 222.9 | 269.4
3907.1 | 3732.1 | 219.2 | 337.9 | 348.3 | 338.2 | 368.6 | 229.1 | 222.6 | 269
3908.1 | 3733.1 | 218.8 | 337.2 | 347.5 | 337.4 | 367.8 | 228.9 | 222.3 | 268.6
3909.1 | 3734.1 | 218.5 | 336.5 | 346.9 | 336.6 | 366.9 | 228.6 | 221.9 | 268.3
3910.1 | 3735.1 | 218.1 | 335.8 | 346.3 | 335.9 | 366 | 228.4 | 221.7 | 268.1
3911.1 | 3736.1 | 217.8 | 335.2 | 345.5 | 335.1 | 365.2 | 228.1 | 221.4 | 267.8
3912.1 | 3737.1 | 217.6 | 334.6 | 344.8 | 334.4 | 364.4 | 227.9 | 221.1 | 267.4
3913.1 | 3738.1 | 217.3 | 333.8 | 344.2 | 333.6 | 363.4 | 227.5 | 220.8 | 267.1
3914.1 | 3739.1 | 216.9 | 333.2 | 343.4 | 332.9 | 362.7 | 227.2 | 220.6 | 266.6
3915.1 | 3740.1 | 216.6 | 332.5 | 342.7 | 332.2 | 361.9 | 226.9 | 220.3 | 266.2
3916.1 | 3741.1 | 216.3 | 331.8 | 342.1 | 331.4 | 361 | 226.6 | 220 | 265.8
3917.1 | 3742.1 | 216 | 331.1 | 341.4 | 330.7 | 360.2 | 226.3 | 219.7 | 265.4
3918.1 | 3743.1 | 215.7 | 330.4 | 340.6 | 329.9 | 359.4 | 225.9 | 219.5 | 265.2
3919.1 | 3744.1 | 215.3 | 329.7 | 340 | 329.2 | 358.6 | 225.6 | 219.2 | 264.7
3920.1 | 3745.1 | 215 | 329 | 339.4 | 328.4 | 357.6 | 225.3 | 219 | 264.3
3921.1 | 3746.1 | 214.7 | 328.3 | 338.6 | 327.7 | 356.9 | 225 | 218.7 | 263.9
3922.1 | 3747.1 | 214.3 | 327.6 | 337.9 | 327 | 356.1 | 224.6 | 218.4 | 263.5
3923.1 | 3748.1 | 214 | 326.9 | 337.3 | 326.2 | 355.2 | 224.2 | 218.2 | 263.1
3924.1 | 3749.1 | 213.7 | 326.2 | 336.6 | 325.5 | 354.4 | 223.9 | 217.9 | 262.7
3925.1 | 3750.1 | 213.4 | 325.5 | 335.9 | 324.8 | 353.7 | 223.6 | 217.6 | 262.4
3926.1 | 3751.1 | 213 | 324.8 | 335.2 | 324.1 | 353 | 223.4 | 217.4 | 262
3927.1 | 3752.1 | 212.7 | 324 | 334.6 | 323.3 | 352.1 | 223.1 | 217.1 | 261.6
3928.1 | 3753.1 | 212.3 | 323.4 | 333.9 | 322.6 | 351.4 | 222.8 | 216.8 | 261.2
3929.1 | 3754.1 | 211.8 | 322.7 | 333.2 | 321.9 | 350.7 | 222.5 | 216.5 | 260.8

## Test Facts
Last row in IRMS data sheets: | 27
Time when Penlight power was initiated: | 175