## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 37
Test conditions: Cable: 7-conductor, 12 AWG, one XLPE insulated, Rockbestos Firewall III, control cable and two PE insulated, industrial control cables (cable items #10 & #15). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable (XLPE) was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 90 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
90 | 0 | Initated Penlight Heating
1491-1662 | 1401-1572 | Conductors B3 & B4 short to ground (206 & 53) | Cable B shorts to ground
1664-1706 | 1574-1616 | Conductors B3 & B4 short together at less than 1000 ohms (100) | Cable B is shorted internally
1765 | 1675 | Conductors A1 & A2 short together at less than 100 ohms (46) | Cable A is shorted internally
1770-1779 | 1680-1689 | Conductors A1 & A2 both short to ground at less than 1000 ohms (479 & 722) | Cable A shorts to ground
1790 | 1700 | Conductor C5 shorts to ground at less than 1000 ohms (207) | Cable C partially shorted to ground
1804 | 1714 | Conductors C5 & C6 short together at less than 1000 ohms (207) | Cable C is shorted internally
2086 | 1996 | Conductor C6 shorts to ground at less than 100 ohms (29) | Cable C is shorted to ground
2385 | 2295 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures did not progress quite as expected during this test: one of the two lower cables (B) shorted to ground first, followed by the top cable (A) then, finally, the other lower cable (C)
Observation 2 | It took 1401 seconds (23.4 min.) from the start of Penlight heating for the first short to ground failure to occur, and it took 1574 s (26.2 min.) for the first internal short failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cable A = XLPE (item #10)
Cable B = PE (item #15)
Cable C = PE (item #15)
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 37 |  |  | 2006-08-30 | 8:32
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-89.5 | 250237.9994 | -86.5 | 248437.9994 | -84 | 252837.9994 | -81 | 248537.9994 | -78.5 | 248237.9994 | -75.5 | 249337.9994 | -72.5 | 250037.9994 | -70 | 249437.9994 | -67 | 249637.9994 | -64.5 | 252437.9994 | -61.5 | 249337.9994 | -58.5 | 247437.9994 | -56 | 252837.9994 | -53 | 252337.9994 | -50.5 | 245937.9994 | -89.5 | #REF!
-47.5 | 250237.9994 | -44.5 | 248437.9994 | -42 | 252837.9994 | -39 | 248537.9994 | -36.5 | 248237.9994 | -33.5 | 249337.9994 | -30.5 | 250037.9994 | -28 | 249437.9994 | -25 | 249637.9994 | -22.5 | 252437.9994 | -19.5 | 249337.9994 | -16.5 | 247437.9994 | -14 | 252837.9994 | -11 | 252337.9994 | -8.5 | 245937.9994 | -47.5 | #REF!
-5.5 | 250237.9994 | -2.5 | 248437.9994 | -3.3528e-07 | 252837.9994 | 3 | 248338.0804 | 5.5 | 248237.9994 | 8.5 | 249337.9994 | 11.5 | 250037.9994 | 14 | 249437.9994 | 17 | 249637.9994 | 19.5 | 252437.9994 | 22.5 | 249337.9994 | 25.5 | 247437.9994 | 28 | 252837.9994 | 31 | 252337.9994 | 33.5 | 245937.9994 | -5.5 | #REF!
36.5 | 250237.9994 | 39.5 | 248437.9994 | 42 | 252837.9994 | 45 | 497175.9997 | 47.5 | 248237.9994 | 50.5 | 249337.9994 | 53.5 | 250037.9994 | 56 | 249437.9994 | 59 | 249637.9994 | 61.5 | 252437.9994 | 64.5 | 249337.9994 | 67.5 | 247437.9994 | 70 | 252837.9994 | 73 | 252337.9994 | 75.5 | 245937.9994 | 36.5 | #REF!
78.5 | 250237.9994 | 81.5 | 248437.9994 | 84 | 252837.9994 | 87 | 248338.0804 | 89.5 | 248237.9994 | 92.5 | 249337.9994 | 95.5 | 250037.9994 | 98 | 249437.9994 | 101 | 249637.9994 | 103.5 | 252437.9994 | 106.5 | 249337.9994 | 109.5 | 247437.9994 | 112 | 252837.9994 | 115 | 252337.9994 | 117.5 | 245937.9994 | 78.5 | #REF!
120.5 | 250237.9994 | 123.5 | 248437.9994 | 126 | 252837.9994 | 129 | 248537.9994 | 131.5 | 248237.9994 | 134.5 | 249337.9994 | 137.5 | 250037.9994 | 140 | 249238.0801 | 143 | 249637.9994 | 145.5 | 252437.9994 | 148.5 | 249337.9994 | 151.5 | 247437.9994 | 154 | 252837.9994 | 157 | 252337.9994 | 159.5 | 245937.9994 | 120.5 | #REF!
162.5 | 250237.9994 | 165.5 | 248437.9994 | 168 | 252837.9994 | 171 | 248537.9994 | 173.5 | 248237.9994 | 176.5 | 249337.9994 | 179.5 | 250037.9994 | 182 | 249437.9994 | 185 | 249637.9994 | 187.5 | 252437.9994 | 190.5 | 249337.9994 | 193.5 | 247437.9994 | 196 | 252837.9994 | 199 | 252337.9994 | 201.5 | 245937.9994 | 162.5 | #REF!
204.5 | 250237.9994 | 207.5 | 248437.9994 | 210 | 252837.9994 | 213 | 248537.9994 | 215.5 | 248237.9994 | 218.5 | 249337.9994 | 221.5 | 250037.9994 | 224 | 249437.9994 | 227 | 249637.9994 | 229.5 | 252437.9994 | 232.5 | 249337.9994 | 235.5 | 247437.9994 | 238 | 252837.9994 | 241 | 252337.9994 | 243.5 | 245937.9994 | 204.5 | #REF!
246.5 | 250237.9994 | 249.5 | 248437.9994 | 252 | 252837.9994 | 255 | 248537.9994 | 257.5 | 248237.9994 | 260.5 | 249337.9994 | 263.5 | 250037.9994 | 266 | 249437.9994 | 269 | 249637.9994 | 271.5 | 252437.9994 | 274.5 | 249337.9994 | 277.5 | 247437.9994 | 280 | 252837.9994 | 283 | 252337.9994 | 285.5 | 245937.9994 | 246.5 | #REF!
288.5 | 250237.9994 | 291.5 | 248437.9994 | 294 | 252837.9994 | 297 | 248537.9994 | 299.5 | 248237.9994 | 302.5 | 124618.9988 | 305.5 | 250037.9994 | 308 | 249437.9994 | 310.5 | 249637.9994 | 313.5 | 252437.9994 | 316.5 | 249337.9994 | 319.5 | 247437.9994 | 322 | 252837.9994 | 325 | 252337.9994 | 327.5 | 245937.9994 | 288.5 | #REF!
330.5 | 250237.9994 | 333.5 | 248437.9994 | 336 | 252638.0791 | 339 | 248537.9994 | 341.5 | 248237.9994 | 344.5 | 249337.9994 | 347.5 | 250037.9994 | 350 | 249437.9994 | 353 | 249438.0801 | 355.5 | 252437.9994 | 358.5 | 249337.9994 | 361.5 | 247437.9994 | 364 | 252837.9994 | 367 | 252337.9994 | 369.5 | 245937.9994 | 330.5 | #REF!
372.5 | 250237.9994 | 375.5 | 248437.9994 | 378 | 252837.9994 | 381 | 248537.9994 | 383.5 | 248237.9994 | 386.5 | 249138.0802 | 389.5 | 250037.9994 | 392 | 249437.9994 | 395 | 249637.9994 | 397.5 | 252437.9994 | 400.5 | 249337.9994 | 403 | 247437.9994 | 406 | 252837.9994 | 408.5 | 252337.9994 | 411.5 | 122918.9988 | 372.5 | #REF!
414.5 | 250237.9994 | 417 | 248437.9994 | 420 | 252837.9994 | 423 | 248537.9994 | 425.5 | 248237.9994 | 428.5 | 249337.9994 | 431.5 | 250037.9994 | 434 | 249437.9994 | 437 | 249637.9994 | 439.5 | 252437.9994 | 442.5 | 249337.9994 | 445.5 | 247437.9994 | 448 | 252837.9994 | 451 | 252337.9994 | 453.5 | 245937.9994 | 414.5 | #REF!
456.5 | 250237.9994 | 459.5 | 248437.9994 | 462 | 252837.9994 | 465 | 248537.9994 | 467.5 | 248237.9994 | 470.5 | 249337.9994 | 473.5 | 250037.9994 | 476 | 249437.9994 | 479 | 249637.9994 | 481.5 | 252437.9994 | 484.5 | 249337.9994 | 487.5 | 247437.9994 | 490 | 252837.9994 | 492.5 | 252337.9994 | 495.5 | 245937.9994 | 456.5 | #REF!
498.5 | 250237.9994 | 501 | 248437.9994 | 504 | 252837.9994 | 506.5 | 248537.9994 | 509.5 | 248237.9994 | 512.5 | 249337.9994 | 515.5 | 250037.9994 | 518 | 249437.9994 | 521 | 249637.9994 | 523.5 | 252437.9994 | 526.5 | 249337.9994 | 529.5 | 247437.9994 | 532 | 252837.9994 | 535 | 252337.9994 | 537.5 | 245937.9994 | 498.5 | #REF!
540.5 | 250237.9994 | 543.5 | 248437.9994 | 546 | 252837.9994 | 548.5 | 248537.9994 | 551.5 | 248237.9994 | 554.5 | 249337.9994 | 557.5 | 250037.9994 | 560 | 249437.9994 | 563 | 249637.9994 | 565.5 | 252437.9994 | 568.5 | 249337.9994 | 571.5 | 247437.9994 | 574 | 252837.9994 | 577 | 252337.9994 | 579.5 | 245937.9994 | 540.5 | #REF!
582.5 | 250237.9994 | 585 | 248437.9994 | 588 | 252837.9994 | 591 | 248537.9994 | 593.5 | 248237.9994 | 596.5 | 249337.9994 | 599.5 | 250037.9994 | 602 | 249437.9994 | 605 | 249637.9994 | 607.5 | 252437.9994 | 610.5 | 249337.9994 | 613.5 | 247437.9994 | 616 | 252837.9994 | 619 | 252337.9994 | 621.5 | 245937.9994 | 582.5 | #REF!
624.5 | 250237.9994 | 627.5 | 248437.9994 | 630 | 252837.9994 | 633 | 248537.9994 | 635.5 | 248237.9994 | 638.5 | 249337.9994 | 641 | 250037.9994 | 644 | 249437.9994 | 647 | 249637.9994 | 649.5 | 252437.9994 | 652.5 | 249337.9994 | 655.5 | 247238.0808 | 658 | 252837.9994 | 661 | 252337.9994 | 663.5 | 245937.9994 | 624.5 | #REF!
666.5 | 250237.9994 | 669.5 | 248437.9994 | 672 | 252837.9994 | 675 | 248537.9994 | 677.5 | 248237.9994 | 680.5 | 249337.9994 | 683.5 | 250037.9994 | 686 | 249437.9994 | 688.5 | 249637.9994 | 691.5 | 252437.9994 | 694.5 | 249337.9994 | 697.5 | 247437.9994 | 700 | 252837.9994 | 702.5 | 252337.9994 | 705.5 | 245937.9994 | 666.5 | #REF!
708.5 | 250237.9994 | 711 | 248437.9994 | 714 | 252837.9994 | 717 | 248537.9994 | 719.5 | 248237.9994 | 722.5 | 249337.9994 | 725.5 | 250037.9994 | 728 | 249437.9994 | 730.5 | 249637.9994 | 733.5 | 252437.9994 | 736.5 | 249337.9994 | 739 | 247437.9994 | 742 | 252837.9994 | 745 | 252337.9994 | 747.5 | 245937.9994 | 708.5 | #REF!
750.5 | 250237.9994 | 753 | 248437.9994 | 756 | 252837.9994 | 758.5 | 248537.9994 | 761.5 | 248237.9994 | 764.5 | 249337.9994 | 767.5 | 250037.9994 | 770 | 249437.9994 | 773 | 249637.9994 | 775.5 | 252437.9994 | 778.5 | 249337.9994 | 781 | 247437.9994 | 784 | 252837.9994 | 786.5 | 252337.9994 | 789 | 245937.9994 | 750.5 | #REF!
792.5 | 250237.9994 | 795.5 | 248437.9994 | 798 | 252837.9994 | 800.5 | 248537.9994 | 803.5 | 248237.9994 | 806.5 | 249337.9994 | 809 | 250037.9994 | 812 | 249437.9994 | 814.5 | 249637.9994 | 817.5 | 252437.9994 | 820.5 | 249337.9994 | 823.5 | 247437.9994 | 826 | 252837.9994 | 828.5 | 252337.9994 | 831.5 | 245937.9994 | 792.5 | #REF!
834.5 | 250237.9994 | 837 | 248437.9994 | 840 | 252837.9994 | 842.5 | 248537.9994 | 845.5 | 248237.9994 | 848.5 | 249337.9994 | 851 | 250037.9994 | 854 | 249437.9994 | 856.5 | 249637.9994 | 859.5 | 252437.9994 | 862.5 | 249337.9994 | 865 | 247437.9994 | 868 | 252837.9994 | 870.5 | 252337.9994 | 873.5 | 245937.9994 | 834.5 | #REF!
876.5 | 250237.9994 | 879 | 248437.9994 | 882 | 252837.9994 | 885 | 248537.9994 | 887.5 | 248237.9994 | 890.5 | 249337.9994 | 893 | 250037.9994 | 896 | 249437.9994 | 898.5 | 249637.9994 | 901.5 | 252437.9994 | 904.5 | 249337.9994 | 907 | 247437.9994 | 910 | 252837.9994 | 912.5 | 252337.9994 | 915.5 | 245937.9994 | 876.5 | #REF!
918.5 | 250237.9994 | 921 | 248437.9994 | 924 | 252837.9994 | 926.5 | 248537.9994 | 929.5 | 248237.9994 | 932.5 | 249337.9994 | 935 | 250037.9994 | 938 | 249437.9994 | 940.5 | 249637.9994 | 943.5 | 252437.9994 | 946.5 | 249337.9994 | 949 | 247437.9994 | 952 | 252837.9994 | 954.5 | 252337.9994 | 957.5 | 245937.9994 | 918.5 | #REF!
960.5 | 250237.9994 | 963.5 | 248437.9994 | 966 | 252837.9994 | 968.5 | 248537.9994 | 971.5 | 248237.9994 | 974.5 | 249337.9994 | 977.5 | 250037.9994 | 980 | 249437.9994 | 982.5 | 249637.9994 | 985.5 | 252437.9994 | 988.5 | 249337.9994 | 991 | 247437.9994 | 994 | 252837.9994 | 996.5 | 252337.9994 | 999.5 | 245937.9994 | 960.5 | #REF!
1002.5 | 250237.9994 | 1005 | 248437.9994 | 1008 | 252837.9994 | 1010.5 | 248537.9994 | 1013.5 | 248237.9994 | 1016.5 | 249337.9994 | 1019 | 250037.9994 | 1022 | 249437.9994 | 1024.5 | 249637.9994 | 1027.5 | 252437.9994 | 1030.5 | 249337.9994 | 1033 | 247437.9994 | 1036 | 252837.9994 | 1038.5 | 252337.9994 | 1041.5 | 245937.9994 | 1002.5 | #REF!
1044.5 | 250237.9994 | 1047 | 248437.9994 | 1050 | 252837.9994 | 1053 | 248537.9994 | 1055.5 | 248237.9994 | 1058.5 | 249337.9994 | 1061 | 250037.9994 | 1064 | 249437.9994 | 1066.5 | 249637.9994 | 1069.5 | 252437.9994 | 1072.5 | 249337.9994 | 1075 | 247437.9994 | 1078 | 252837.9994 | 1080.5 | 252337.9994 | 1083.5 | 245937.9994 | 1044.5 | #REF!
1086.5 | 250237.9994 | 1089 | 248437.9994 | 1092 | 252837.9994 | 1094.5 | 248537.9994 | 1097.5 | 248237.9994 | 1100.5 | 249337.9994 | 1103 | 250037.9994 | 1106 | 249437.9994 | 1108.5 | 249637.9994 | 1111.5 | 252437.9994 | 1114.5 | 249337.9994 | 1117 | 247437.9994 | 1120 | 252837.9994 | 1122.5 | 252337.9994 | 1125.5 | 245937.9994 | 1086.5 | #REF!
1128.5 | 250237.9994 | 1131 | 248437.9994 | 1134 | 252837.9994 | 1136.5 | 248537.9994 | 1139.5 | 248237.9994 | 1142.5 | 249337.9994 | 1145 | 250037.9994 | 1148 | 249437.9994 | 1150.5 | 249637.9994 | 1153.5 | 252437.9994 | 1156.5 | 249337.9994 | 1159 | 247437.9994 | 1162 | 252837.9994 | 1164.5 | 126118.9988 | 1167.5 | 245937.9994 | 1128.5 | #REF!
1170.5 | 250237.9994 | 1173 | 248437.9994 | 1176 | 252837.9994 | 1179 | 248537.9994 | 1181.5 | 124068.9988 | 1184.5 | 249337.9994 | 1187 | 250037.9994 | 1190 | 249437.9994 | 1192.5 | 249637.9994 | 1195.5 | 252437.9994 | 1198.5 | 249337.9994 | 1201 | 247437.9994 | 1204 | 252837.9994 | 1206.5 | 252337.9994 | 1209.5 | 245937.9994 | 1170.5 | #REF!
1212.5 | 250237.9994 | 1215 | 248437.9994 | 1218 | 252837.9994 | 1220.5 | 248537.9994 | 1223.5 | 248237.9994 | 1226.5 | 249337.9994 | 1229 | 250037.9994 | 1232 | 249437.9994 | 1234.5 | 249637.9994 | 1237.5 | 252437.9994 | 1240.5 | 249337.9994 | 1243 | 247437.9994 | 1246 | 252837.9994 | 1248.5 | 252337.9994 | 1251.5 | 245937.9994 | 1212.5 | #REF!
1254.5 | 250237.9994 | 1257 | 248437.9994 | 1260 | 252837.9994 | 1262.5 | 248537.9994 | 1265.5 | 248237.9994 | 1268.5 | 249337.9994 | 1271 | 250037.9994 | 1274 | 249437.9994 | 1276.5 | 249637.9994 | 1279.5 | 252437.9994 | 1282.5 | 249337.9994 | 1285 | 247437.9994 | 1288 | 252837.9994 | 1290.5 | 252337.9994 | 1293.5 | 245937.9994 | 1254.5 | #REF!
1296.5 | 250237.9994 | 1299 | 248437.9994 | 1302 | 252837.9994 | 1304.5 | 248537.9994 | 1307.5 | 248237.9994 | 1310.5 | 249337.9994 | 1313 | 250037.9994 | 1316 | 249437.9994 | 1318.5 | 249637.9994 | 1321.5 | 252437.9994 | 1324.5 | 249337.9994 | 1327 | 247437.9994 | 1330 | 252837.9994 | 1332.5 | 252337.9994 | 1335.5 | 245937.9994 | 1296.5 | #REF!
1338.5 | 250237.9994 | 1341 | 248437.9994 | 1344 | 252837.9994 | 1346.5 | 248537.9994 | 1349.5 | 248237.9994 | 1352.5 | 249337.9994 | 1355 | 250037.9994 | 1358 | 249437.9994 | 1360.5 | 249637.9994 | 1363.5 | 252437.9994 | 1366.5 | 249337.9994 | 1369 | 240540.7875 | 1372 | 252837.9994 | 1374.5 | 252337.9994 | 1377.5 | 245937.9994 | 1338.5 | #REF!
1380.5 | 250237.9994 | 1383 | 248437.9994 | 1386 | 252837.9994 | 1388.5 | 248537.9994 | 1391.5 | 248237.9994 | 1394.5 | 249337.9994 | 1397 | 250037.9994 | 1400 | 249437.9994 | 1402.5 | 249637.9994 | 1405.5 | 4491.5664 | 1408.5 | 167770.7135 | 1411 | 235742.7265 | 1414 | 252837.9994 | 1416.5 | 252337.9994 | 1419.5 | 245937.9994 | 1380.5 | #REF!
1422.5 | 250237.9994 | 1425 | 248437.9994 | 1428 | 252837.9994 | 1430.5 | 248537.9994 | 1433.5 | 248237.9994 | 1436.5 | 249337.9994 | 1439 | 250037.9994 | 1442 | 249437.9994 | 1444.5 | 249637.9994 | 1447.5 | 4576.5967 | 1450.5 | 210553.555 | 1453 | 231944.2617 | 1456 | 252837.9994 | 1458.5 | 252337.9994 | 1461.5 | 245937.9994 | 1422.5 | #REF!
1464.5 | 250237.9994 | 1467 | 248437.9994 | 1470 | 252837.9994 | 1472.5 | 248537.9994 | 1475.5 | 248237.9994 | 1478.5 | 249337.9994 | 1481 | 250037.9994 | 1484 | 249437.9994 | 1486.5 | 249637.9994 | 1489.5 | 252437.9994 | 1492.5 | 249337.9994 | 1495 | 82412.6648 | 1498 | 252837.9994 | 1500.5 | 252337.9994 | 1503.5 | 245937.9994 | 1464.5 | #REF!
1506.5 | 250237.9994 | 1509 | 248437.9994 | 1512 | 252837.9994 | 1514.5 | 248537.9994 | 1517.5 | 248237.9994 | 1520.5 | 249337.9994 | 1523 | 250037.9994 | 1526 | 249437.9994 | 1528.5 | 249637.9994 | 1531.5 | 50407.5969 | 1534.5 | 238442.3698 | 1537 | 247437.9994 | 1540 | 252837.9994 | 1542.5 | 63009.4976 | 1545.5 | 245937.9994 | 1506.5 | #REF!
1548.5 | 125068.9988 | 1551 | 248437.9994 | 1554 | 252837.9994 | 1556.5 | 248537.9994 | 1559.5 | 248237.9994 | 1562.5 | 249337.9994 | 1565 | 250037.9994 | 1568 | 249437.9994 | 1570.5 | 249637.9994 | 1573.5 | 993.0971 | 1576.5 | 124618.9988 | 1579 | 231944.2617 | 1582 | 121641.7408 | 1584.5 | 60.7626 | 1587.5 | 245937.9994 | 1548.5 | #REF!
1590.5 | 30980.2144 | 1593 | 248437.9994 | 1596 | 252837.9994 | 1598.5 | 124218.9988 | 1601.5 | 248237.9994 | 1604.5 | 249337.9994 | 1607 | 250037.9994 | 1610 | 249437.9994 | 1612.5 | 249637.9994 | 1615.5 | 99.8176 | 1618.5 | 201457.2032 | 1621 | 187086.7198 | 1624 | 9930.1419 | 1626.5 | 1.5829 | 1629.5 | 122918.9988 | 1590.5 | #REF!
1632.5 | 3380.3015 | 1635 | 248437.9994 | 1638 | 126368.9988 | 1640.5 | 124218.9988 | 1643.5 | 248237.9994 | 1646.5 | 249337.9994 | 1649 | 124968.9988 | 1652 | 249437.9994 | 1654.5 | 249637.9994 | 1657.5 | 189.7424 | 1660 | 171500.3802 | 1663 | 50397.2483 | 1666 | 36409.1882 | 1668.5 | 1.6683 | 1671.5 | 122918.9988 | 1632.5 | #REF!
1674.5 | 45.8021 | 1677 | 22242.0762 | 1680 | 126368.9988 | 1682.5 | 124218.9988 | 1685.5 | 124068.9988 | 1688.5 | 124618.9988 | 1692 | 124968.9988 | 1694 | 249437.9994 | 1696.5 | 124768.9988 | 1699.5 | 28.5176 | 1702.5 | 37632.0955 | 1705 | 35309.4484 | 1708 | 48299.7788 | 1710.5 | 12.8239 | 1713.5 | 206.6745 | 1674.5 | #REF!
1716.5 | 63.37 | 1719 | 22791.4122 | 1722 | 126368.9988 | 1724.5 | 124218.9988 | 1727.5 | 124068.9988 | 1730.5 | 124618.9988 | 1733 | 124968.9988 | 1736 | 124668.9988 | 1738.5 | 124768.9988 | 1741.5 | 7.0101 | 1744 | 32944.0111 | 1747 | 51175.9029 | 1750 | 25497.6138 | 1752.5 | 12.6673 | 1755.5 | 2335.9581 | 1716.5 | #REF!
1758 | 38.6287 | 1761 | 85417.8786 | 1764 | 84212.6648 | 1766.5 | 124218.9988 | 1769.5 | 124068.9988 | 1772.5 | 124618.9988 | 1775 | 83279.3315 | 1778 | 249437.9994 | 1780.5 | 124768.9988 | 1783.5 | 3.1841 | 1786 | 7528.934 | 1789 | 17716.5027 | 1791.5 | 42887.0729 | 1794.5 | 28.8707 | 1797.5 | 122918.9988 | 1758 | #REF!
1800.5 | 59.8531 | 1803 | 8209.0376 | 1806 | 126368.9988 | 1808.5 | 124218.9988 | 1811.5 | 124068.9988 | 1814 | 124618.9988 | 1817 | 124968.9988 | 1820 | 124668.9988 | 1822.5 | 124768.9988 | 1825.5 | 17.2058 | 1828.5 | 58567.4759 | 1831 | 53672.873 | 1834 | 15919.0966 | 1836.5 | 29.006 | 1839.5 | 22267.0842 | 1800.5 | #REF!
1842.5 | 31.7607 | 1845 | 4313.7458 | 1847.5 | 126368.9988 | 1850.5 | 124218.9988 | 1853.5 | 124068.9988 | 1856.5 | 124618.9988 | 1859 | 124968.9988 | 1861.5 | 124668.9988 | 1864.5 | 124768.9988 | 1867.5 | 12.9737 | 1870 | 59441.0669 | 1873 | 36593.5971 | 1876 | 32573.4822 | 1878.5 | 3.5398 | 1881.5 | 81912.6648 | 1842.5 | #REF!
1884.5 | 51.9918 | 1887 | 8458.7358 | 1890 | 126368.9988 | 1892.5 | 82779.3315 | 1895.5 | 124068.9988 | 1898 | 124618.9988 | 1901 | 124968.9988 | 1904 | 249437.9994 | 1906.5 | 124768.9988 | 1909.5 | 19.2642 | 1912.5 | 7269.0426 | 1915 | 11823.6531 | 1917.5 | 54073.789 | 1920.5 | 29.0738 | 1923.5 | 122918.9988 | 1884.5 | #REF!
1926.5 | 61.8758 | 1929 | 21983.5624 | 1931.5 | 126368.9988 | 1934.5 | 124218.9988 | 1937.5 | 124068.9988 | 1940.5 | 124618.9988 | 1943 | 83279.3315 | 1945.5 | 124668.9988 | 1948.5 | 124768.9988 | 1951.5 | 3.5372 | 1954 | 5880.8668 | 1957 | 23408.8182 | 1959.5 | 10803.9442 | 1962.5 | 21.8283 | 1965.5 | 13898.0743 | 1926.5 | #REF!
1968.5 | 10.0628 | 1971 | 4897.4122 | 1974 | 84212.6648 | 1976.5 | 82779.3315 | 1979.5 | 124068.9988 | 1982.5 | 83045.9982 | 1985 | 83279.3315 | 1988 | 83079.3315 | 1990.5 | 83145.9982 | 1993.5 | 12.3487 | 1996.5 | 15378.6786 | 1999 | 20123.54 | 2001.5 | 46832.688 | 2004.5 | 0.13942 | 2007.5 | 2574.2699 | 1968.5 | #REF!
2010 | 68.9372 | 2013 | 4093.3596 | 2015.5 | 63134.4976 | 2018.5 | 62059.4976 | 2021.5 | 61984.4976 | 2024 | 62259.4976 | 2027 | 49927.5969 | 2029.5 | 49807.5969 | 2032.5 | 62334.4976 | 2035.5 | 8.6372 | 2038.5 | 39554.0465 | 2041 | 51756.8666 | 2043.5 | 26867.4317 | 2046.5 | 10.5692 | 2049.5 | 6476.5452 | 2010 | #REF!
2052.5 | 70.8649 | 2055 | 50835.4845 | 2058 | 50487.5969 | 2060.5 | 41339.663 | 2063.5 | 49567.5969 | 2066.5 | 35533.9957 | 2069 | 41589.663 | 2072 | 31092.2451 | 2074.5 | 31117.2451 | 2077.5 | 27.3845 | 2080 | 50465.1771 | 2083 | 19356.4626 | 2086 | 4039.8455 | 2088.5 | 6.8259 | 2091.5 | 367.4317 | 2052.5 | #REF!
2094.5 | 53.2767 | 2097 | 41536.4389 | 2099.5 | 16762.5242 | 2102.5 | 237605.3268 | 2105.5 | 15421.1152 | 2108 | 13028.3042 | 2111 | 756.4587 | 2114 | 97637.6874 | 2116.5 | 99.5098 | 2119.5 | 11.2709 | 2122 | 4057.3146 | 2125 | 6545.8865 | 2127.5 | 21183.1684 | 2130.5 | 19.918 | 2133.5 | 379.2931 | 2094.5 | #REF!
2136 | 193.8463 | 2139 | 13949.1508 | 2141.5 | 24.1717 | 2144.5 | 11667.1862 | 2147.5 | 0.84135 | 2150 | 22.2509 | 2153 | 8.6108 | 2156 | 13359.2032 | 2158.5 | 0.7345 | 2161.5 | 3.3162 | 2164.5 | 12079.6063 | 2167 | 2870.109 | 2170 | 15058.4619 | 2172.5 | 0.87803 | 2175.5 | 63.6612 | 2136 | #REF!
2178 | 558.9794 | 2181 | 9698.8913 | 2183.5 | 4.8235 | 2186.5 | 1689.6269 | 2189.5 | 15.2902 | 2192 | 22.4364 | 2195 | 5.0989 | 2197.5 | 11870.9192 | 2200.5 | 24.793 | 2203.5 | 16.147 | 2206.5 | 30427.8155 | 2209 | 272.1539 | 2212 | 13754.9117 | 2214.5 | 1.4123 | 2217.5 | 44.7266 | 2178 | #REF!
2220 | 639.3131 | 2223 | 2977.5481 | 2225.5 | 22.1937 | 2228.5 | 28865.9595 | 2231.5 | 23.7683 | 2234 | 5.2613 | 2237 | 7.8325 | 2239.5 | 1103.3608 | 2242.5 | 24.793 | 2245.5 | 9.7157 | 2248.5 | 24892.9475 | 2251 | 2028.8725 | 2254 | 16784.7443 | 2256.5 | 0.55105 | 2259.5 | 131.2448 | 2220 | #REF!
2262 | 8267.8628 | 2265 | 884.2183 | 2267.5 | 23.6714 | 2270.5 | 2269.946 | 2273.5 | 2.7575 | 2276.5 | 26.859 | 2279 | 5.8862 | 2281.5 | 47195.8709 | 2284.5 | 1.5043 | 2287.5 | 6.3536 | 2290 | 34696.2205 | 2293 | 371.3969 | 2295.5 | 52475.6867 | 2298.5 | 28.5334 | 2301.5 | 81912.6648 | 2262 | #REF!
2304.5 | 22.0186 | 2307 | 94.4952 | 2309.5 | 7.9429 | 2312.5 | 38990.8978 | 2315.5 | 0.84214 | 2318 | 21.0887 | 2321 | 10.4022 | 2323.5 | 51854.7453 | 2326.5 | 27.4128 | 2329.5 | 8.7831 | 2332.5 | 49059.2021 | 2335 | 182.9038 | 2337.5 | 17017.7919 | 2340.5 | 4.2532 | 2343.5 | 39.9307 | 2304.5 | #REF!
2346 | 8592.7148 | 2349 | 486.2083 | 2351.5 | 0.89611 | 2354.5 | 8129.8186 | 2357.5 | 20.1882 | 2360 | 19.0615 | 2363 | 21.9814 | 2365.5 | 15989.2555 | 2368.5 | 20.392 | 2371.5 | 19.148 | 2374 | 40273.3138 | 2377 | 4015.8014 | 2379.5 | 13411.4362 | 2382.5 | 17.3277 | 2385.5 | 590.9006 | 2346 | #REF!
2388 | 23.3192 | 2391 | 6465.9321 | 2393.5 | 19.3969 | 2396.5 | 11519.4381 | 2399.5 | 0.80071 | 2402 | 10.7486 | 2405 | 16.808 | 2407.5 | 1535.5346 | 2410.5 | 18.9133 | 2413.5 | 3.4929 | 2416 | 4930.0814 | 2419 | 9550.125 | 2421.5 | 47362.9808 | 2424.5 | 0.026141 | 2427.5 | 61409.4976 | 2388 | #REF!
2430 | 9566.5774 | 2433 | 7158.8966 | 2435.5 | 9.7926 | 2438.5 | 16711.0725 | 2441.5 | 26.0306 | 2444 | 28.403 | 2447 | 8.4641 | 2449.5 | 12917.2609 | 2452.5 | 2.5483 | 2455.5 | 10.3627 | 2458 | 47323.4641 | 2461 | 1372.0772 | 2463.5 | 3833.4479 | 2466.5 | 2.9233 | 2469.5 | 482.7708 | 2430 | #REF!
2472 | 2643.0276 | 2475 | 3239.4726 | 2477.5 | 19.747 | 2480.5 | 32598.6199 | 2483.5 | 28.3066 | 2486 | 28.6071 | 2489 | 20.1686 | 2491.5 | 39590.3463 | 2494.5 | 15.5592 | 2497.5 | 27.3184 | 2500 | 37492.8529 | 2503 | 418.6785 | 2505.5 | 1535.5678 | 2508.5 | 1.2 | 2511.5 | 81912.6648 | 2472 | #REF!
2514 | 1753.9752 | 2517 | 7286.9511 | 2519.5 | 30.1523 | 2522.5 | 1535.5257 | 2525.5 | 22.6353 | 2528 | 28.7435 | 2531 | 3.6918 | 2533.5 | 31999.4832 | 2536.5 | 5.7146 | 2539.5 | 28.3162 | 2542 | 39390.5678 | 2545 | 7653.5637 | 2547.5 | 54573.196 | 2550.5 | 17.9508 | 2553.5 | 81912.6648 | 2514 | #REF!
2556 | 0.51406 | 2559 | 333.2361 | 2561.5 | 28.8578 | 2564.5 | 48878.9527 | 2567.5 | 20.973 | 2570 | 12.9311 | 2573 | 14.1076 | 2575.5 | 15261.9931 | 2578.5 | 24.2816 | 2581.5 | 30.7045 | 2584 | 1536.1502 | 2587 | 163.4005 | 2589 | 40889.445 | 2592.5 | 20.8658 | 2595.5 | 4820.7295
2598 | 6.3938 | 2601 | 833.5315 | 2603.5 | 8.1347 | 2606.5 | 5233.7866 | 2609.5 | 2.6689 | 2612 | 23.1839 | 2615 | 15.3599 | 2617.5 | 12274.348 | 2620.5 | 5.3896 | 2623.5 | 30.0134 | 2626 | 30788.548 | 2629 | 849.2225 | 2631.5 | 3635.1234 | 2634.5 | 17.0466 | 2637.5 | 122918.9988
2640 | 15.3982 | 2643 | 6324.7481 | 2645.5 | 12.3734 | 2648.5 | 27504.7734 | 2651.5 | 12.5328 | 2654 | 0.10427 | 2657 | 26.0317 | 2659.5 | 2734.7083 | 2662.5 | 25.1793 | 2665.5 | 16.0366 | 2668 | 24218.5659 | 2671 | 109.1681 | 2673.5 | 50977.4658 | 2676.5 | 29.006 | 2679.5 | 122918.9988
2682 | 11.9259 | 2685 | 253.0182 | 2687.5 | 23.2368 | 2690.5 | 26716.4924 | 2693.5 | 17.4886 | 2696 | 13.0371 | 2699 | 24.9306 | 2701.5 | 46382.1712 | 2704.5 | 1.0752 | 2707.5 | 3.0962 | 2710 | 37707.7416 | 2713 | 2742.5439 | 2715.5 | 22919.8627 | 2718.5 | 6.4509 | 2721.5 | 122918.9988
2724 | 4783.0159 | 2727 | 8962.6039 | 2729.5 | 9.153 | 2732.5 | 25217.699 | 2735.5 | 8.5043 | 2738 | 27.66 | 2741 | 3.0238 | 2743.5 | 16118.5985 | 2746.5 | 0.9472 | 2749.5 | 9.1739 | 2752 | 57568.6786 | 2755 | 931.5428 | 2757.5 | 21021.3651 | 2760.5 | 20.2126 | 2763.5 | 122918.9988
2766 | 28.1923 | 2769 | 2497.5008 | 2771.5 | 17.4499 | 2774.5 | 34310.3791 | 2777.5 | 19.9487 | 2780 | 19.5325 | 2783 | 1.1113 | 2785.5 | 49298.4565 | 2788.5 | 0.85443 | 2791.5 | 14.7276 | 2794 | 57391.9461 | 2797 | 1577.1447 | 2799.5 | 29214.8813 | 2802.5 | 23.6113 | 2805.5 | 81912.6648
2808 | 24.5193 | 2811 | 870.453 | 2813.5 | 14.8035 | 2816.5 | 5133.8671 | 2819.5 | 11.1239 | 2822 | 27.4588 | 2825 | 1.154 | 2827.5 | 13127.4701 | 2830.5 | 0.81948 | 2833.5 | 4.6102 | 2836 | 14826.1029 | 2839 | 1482.1201 | 2841.5 | 41305.3137 | 2844.5 | 12.9285 | 2847.5 | 122918.9988
2850 | 17.1852 | 2853 | 2710.8806 | 2855.5 | 14.9114 | 2858.5 | 56392.6023 | 2861.5 | 5.4858 | 2864 | 8.8429 | 2867 | 12.3037 | 2869.5 | 12627.8709 | 2872.5 | 21.601 | 2875.5 | 0.10786 | 2878 | 48698.9218 | 2881 | 8192.5387 | 2883.5 | 13127.6117 | 2886.5 | 18.0078 | 2889.5 | 81912.6648

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 37 |  |  | 2006-08-30 | 8:32
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-83.9 | 248238 |  | -74.9 | 249338 | -69.3 | 247438 | -66 | 250038 | -63.8 | 245938 | -61.5 | 245938 | -83.9 | 245938
-41.9 | 248238 |  | -32.9 | 249338 | -27.3 | 247438 | -24 | 250038 | -21.8 | 245938 | -19.5 | 245938 | -41.9 | 245938
0.1 | 248238 |  | 9.1 | 249338 | 14.7 | 247438 | 18 | 252338 | 20.2 | 245938 | 22.5 | 245938 | 0.1 | 245938
42.1 | 248238 |  | 51.1 | 249338 | 56.7 | 247438 | 60 | 250038 | 62.2 | 245938 | 64.5 | 245938 | 42.1 | 245938
84.1 | 248238 |  | 93.1 | 249338 | 98.7 | 247438 | 102 | 250038 | 104.2 | 245938 | 106.5 | 245938 | 84.1 | 245938
126.1 | 248238 |  | 135.1 | 249338 | 140.7 | 247438 | 144 | 250038 | 146.2 | 245938 | 148.5 | 245938 | 126.1 | 245938
168.1 | 248238 |  | 177.1 | 249338 | 182.7 | 247438 | 186 | 250038 | 188.2 | 245938 | 190.5 | 245938 | 168.1 | 245938
210.1 | 248238 |  | 219.1 | 249338 | 224.7 | 247438 | 228 | 250038 | 230.2 | 245938 | 232.5 | 245938 | 210.1 | 245938
252.1 | 248238 |  | 261.1 | 249338 | 266.7 | 247438 | 270 | 250038 | 272.2 | 245938 | 274.5 | 245938 | 252.1 | 245938
294.1 | 248238 |  | 303 | 124619 | 308.7 | 247438 | 312 | 250038 | 314.2 | 245938 | 316.4 | 245938 | 294.1 | 124619
336.1 | 248238 |  | 345.1 | 249338 | 350.7 | 247438 | 354 | 250038 | 356.2 | 245938 | 358.5 | 245938 | 336.1 | 245938
378.1 | 248238 |  | 387.1 | 249438 | 392.6 | 247438 | 395.9 | 250038 | 398.2 | 122919 | 400.3 | 245938 | 378.1 | 122919
420 | 248238 |  | 429.1 | 249338 | 434.6 | 247438 | 438 | 250038 | 440.2 | 245938 | 442.5 | 245938 | 420 | 245938
462.1 | 248238 |  | 471.1 | 249338 | 476.7 | 247438 | 479.9 | 250038 | 482.2 | 245938 | 484.4 | 245938 | 462.1 | 245938
503.9 | 248238 |  | 513.1 | 249338 | 518.6 | 247438 | 522 | 250038 | 524.1 | 245938 | 526.5 | 245938 | 503.9 | 245938
546 | 248238 |  | 555.1 | 249338 | 560.7 | 247438 | 564 | 250038 | 566.1 | 245938 | 568.5 | 245938 | 546 | 245938
588 | 248238 |  | 597.1 | 249338 | 602.6 | 247438 | 606 | 250038 | 608.2 | 245938 | 610.5 | 245938 | 588 | 245938
630.1 | 248238 |  | 639 | 249338 | 644.7 | 248438 | 647.9 | 250038 | 650.2 | 245938 | 652.5 | 245938 | 630.1 | 245938
672.1 | 248238 |  | 681 | 249338 | 686.7 | 247438 | 689.9 | 250038 | 692.2 | 245938 | 694.3 | 245938 | 672.1 | 245938
714 | 248238 |  | 723 | 249338 | 728.5 | 247438 | 732 | 250038 | 734.2 | 245938 | 736.3 | 245938 | 714 | 245938
755.9 | 248238 |  | 765.1 | 249338 | 770.5 | 247438 | 773.9 | 250038 | 776 | 245938 | 778.2 | 245938 | 755.9 | 245938
798 | 248238 |  | 806.9 | 249338 | 812.7 | 247438 | 815.8 | 250038 | 818.1 | 245938 | 820.3 | 245938 | 798 | 245938
839.9 | 248238 |  | 848.9 | 249338 | 854.5 | 247438 | 857.8 | 250038 | 860.1 | 245938 | 862.2 | 245938 | 839.9 | 245938
882 | 248238 |  | 890.9 | 249338 | 896.5 | 247438 | 899.8 | 250038 | 902.2 | 245938 | 904.2 | 245938 | 882 | 245938
923.9 | 248238 |  | 932.9 | 249338 | 938.5 | 247438 | 941.8 | 250038 | 944.1 | 245938 | 946.2 | 245938 | 923.9 | 245938
966 | 248238 |  | 975 | 249338 | 980.6 | 247438 | 983.9 | 250038 | 986.1 | 245938 | 988.2 | 245938 | 966 | 245938
1007.9 | 248238 |  | 1016.9 | 249338 | 1022.5 | 247438 | 1025.8 | 250038 | 1028.1 | 245938 | 1030.2 | 245938 | 1007.9 | 245938
1050 | 248238 |  | 1058.9 | 249338 | 1064.5 | 247438 | 1067.8 | 250038 | 1070.2 | 245938 | 1072.2 | 245938 | 1050 | 245938
1091.9 | 248238 |  | 1100.9 | 249338 | 1106.5 | 247438 | 1109.8 | 250038 | 1112.1 | 245938 | 1114.2 | 245938 | 1091.9 | 245938
1133.9 | 248238 |  | 1142.9 | 249338 | 1148.5 | 247438 | 1151.8 | 126119 | 1154.1 | 245938 | 1156.2 | 245938 | 1133.9 | 126119
1176 | 124069 |  | 1184.9 | 249338 | 1190.5 | 247438 | 1193.8 | 250038 | 1196.2 | 245938 | 1198.2 | 245938 | 1176 | 124069
1217.9 | 248238 |  | 1226.9 | 249338 | 1232.5 | 247438 | 1235.8 | 250038 | 1238.1 | 245938 | 1240.2 | 245938 | 1217.9 | 245938
1259.9 | 248238 |  | 1268.9 | 249338 | 1274.5 | 247438 | 1277.8 | 250038 | 1280.1 | 124619 | 1282.2 | 245938 | 1259.9 | 124619
1301.9 | 248238 |  | 1310.9 | 249338 | 1316.5 | 247438 | 1319.8 | 250038 | 1322.1 | 245938 | 1324.2 | 245938 | 1301.9 | 245938
1343.9 | 248238 |  | 1352.9 | 249338 | 1358.5 | 3593.1262 | 1361.8 | 250038 | 1364.1 | 245938 | 1366.2 | 245938 | 1343.9 | 3593.1262
1385.9 | 248238 |  | 1394.9 | 249338 | 1400.5 | 206.3121 | 1403.8 | 250038 | 1406.1 | 245938 | 1408.2 | 245938 | 1385.9 | 206.3121
1427.9 | 248238 |  | 1436.9 | 249338 | 1442.5 | 545.9539 | 1445.8 | 250038 | 1448.1 | 245938 | 1450.2 | 245938 | 1427.9 | 545.9539
1469.9 | 248238 |  | 1478.9 | 249338 | 1484.5 | 2275.6 | 1487.8 | 250038 | 1490.1 | 245938 | 1492.2 | 245938 | 1469.9 | 2275.6
1511.9 | 248238 |  | 1520.9 | 125069 | 1526.5 | 2230.27 | 1529.8 | 63009.5 | 1532.1 | 245938 | 1534.2 | 245938 | 1511.9 | 2230.27
1553.9 | 125069 |  | 1562.9 | 249338 | 1568.5 | 272.2955 | 1571.8 | 52.5909 | 1574.1 | 126369 | 1576.2 | 126119 | 1553.9 | 52.5909
1595.9 | 49935.3501 |  | 1604.9 | 62541.3002 | 1610.5 | 91.5806 | 1613.8 | 3.078 | 1616.1 | 122919 | 1618.2 | 122919 | 1595.9 | 3.078
1637.9 | 15604.5502 |  | 1646.9 | 13742.7067 | 1652.4 | 25.6668 | 1655.8 | 3.1622 | 1658 | 122919 | 1660.2 | 84046 | 1637.9 | 3.1622
1679.9 | 479.1235 |  | 1689.1 | 722.15 | 1694.5 | 16.716 | 1698 | 10.5015 | 1700.1 | 207.1635 | 1702.2 | 122919 | 1679.9 | 10.5015
1721.9 | 4515.2652 |  | 1730.9 | 4009.5287 | 1736.4 | 8.4319 | 1739.8 | 6.7699 | 1742 | 215.0732 | 1744.2 | 82412.6667 | 1721.9 | 6.7699
1763.8 | 2177.6362 |  | 1772.8 | 2070.5864 | 1778.4 | 3.1601 | 1781.7 | 20.5138 | 1783.9 | 83046 | 1786.2 | 82412.6667 | 1763.8 | 3.1601
1805.9 | 2043.0111 |  | 1814.8 | 4695.1506 | 1820.4 | 7.0853 | 1823.8 | 2.9507 | 1826.1 | 5209.3191 | 1828.2 | 82412.6667 | 1805.9 | 2.9507
1847.8 | 888.819 |  | 1856.8 | 1020.3913 | 1862.4 | 3.6021 | 1865.7 | 1.5407 | 1867.9 | 1721.4453 | 1870.2 | 82412.6667 | 1847.8 | 1.5407
1889.9 | 9084.9439 |  | 1898.8 | 50726.2395 | 1904.4 | 3.1602 | 1907.7 | 6.153 | 1910 | 2702.6742 | 1912.2 | 17474.1429 | 1889.9 | 3.1602
1931.8 | 5579.9144 |  | 1940.8 | 3472.556 | 1946.4 | 2.4817 | 1949.6 | 4.565 | 1951.8 | 4267.4045 | 1954.2 | 3397.7183 | 1931.8 | 2.4817
1973.9 | 702.655 |  | 1982.9 | 965.0256 | 1988.5 | 4.1113 | 1991.7 | 1.3807 | 1994 | 271.7407 | 1996.2 | 28.5465 | 1973.9 | 1.3807
2015.7 | 1564.6804 |  | 2024.6 | 2773.0571 | 2030.4 | 3.4132 | 2033.6 | 1.0152 | 2035.9 | 219.1023 | 2038.2 | 409.9343 | 2015.7 | 1.0152
2057.9 | 1688.1744 |  | 2066.9 | 3822.1552 | 2072.4 | 8.6208 | 2075.8 | 1.2988 | 2078 | 161.7132 | 2080.2 | 10.0841 | 2057.9 | 1.2988
2099.8 | 2476.5953 |  | 2108.8 | 100.2711 | 2114.3 | 2.2287 | 2117.6 | 1.95 | 2119.9 | 62.6063 | 2122.2 | 11.5819 | 2099.8 | 1.95
2141.7 | 2.323 |  | 2150.7 | 2.226 | 2156.4 | 4.7876 | 2159.7 | 0.65311 | 2162.1 | 64.5739 | 2164.2 | 9.7729 | 2141.7 | 0.65311
2183.7 | 1.6941 |  | 2192.6 | 6.5324 | 2198.4 | 1.2063 | 2201.7 | 2.9099 | 2204 | 45.7571 | 2206.2 | 4.5194 | 2183.7 | 1.2063
2225.7 | 5.3156 |  | 2234.6 | 1.6057 | 2240.4 | 5.2592 | 2243.7 | 0.9752 | 2246 | 40.3476 | 2248.2 | 2.6614 | 2225.7 | 0.9752
2267.7 | 2.8741 |  | 2276.7 | 2.9847 | 2282.4 | 0.83191 | 2285.6 | 17.9896 | 2287.8 | 49.6918 | 2290.2 | 0.67021 | 2267.7 | 0.67021
2309.8 | 0.66396 |  | 2318.7 | 1.4335 | 2324.4 | 0.66343 | 2327.6 | 0.77211 | 2329.9 | 40.996 | 2332.2 | 13.4975 | 2309.8 | 0.66343
2351.7 | 2.404 |  | 2360.6 | 6.9631 | 2366.3 | 3.9325 | 2369.6 | 5.6573 | 2371.8 | 144.9635 | 2374.2 | 2.2678 | 2351.7 | 2.2678
2393.7 | 0.70479 |  | 2402.6 | 0.66102 | 2408.3 | 2.0622 | 2411.6 | 1.5438 | 2413.8 | 61409.5 | 2416.2 | 10.9947 | 2393.7 | 0.66102
2435.7 | 7.2672 |  | 2444.6 | 4.0142 | 2450.3 | 4.6385 | 2453.6 | 1.5822 | 2455.8 | 483.0284 | 2458.2 | 6.111 | 2435.7 | 1.5822
2477.7 | 15.1705 |  | 2486.6 | 5.6845 | 2492.3 | 1.918 | 2495.6 | 0.65207 | 2497.8 | 63134.5 | 2500.2 | 10.1638 | 2477.7 | 0.65207
2519.7 | 0.66343 |  | 2528.6 | 5.1442 | 2534.3 | 12.0566 | 2537.6 | 3.2775 | 2539.8 | 62059.5 | 2542.2 | 1.9339 | 2519.7 | 0.66343
2561.7 | 2.0122 |  | 2570.6 | 6.7343 | 2576.3 | 0.66128 | 2579.5 | 0.65285 | 2581.7 | 4058.9667 | 2584.2 | 2.2462 | 2561.7 | 0.65285
2603.7 | 2.1949 |  | 2612.6 | 5.5154 | 2618.3 | 0.66102 | 2621.6 | 0.65181 | 2623.8 | 1849.5156 | 2626.2 | 5.2457 | 2603.7 | 0.65181
2645.7 | 12.5116 |  | 2654.6 | 1.1509 | 2660.3 | 1.5117 | 2663.6 | 7.053 | 2665.8 | 82779.3333 | 2668.2 | 3.1838 | 2645.7 | 1.1509
2687.7 | 11.1247 |  | 2696.6 | 0.65862 | 2702.3 | 1.0728 | 2705.6 | 7.8795 | 2707.8 | 83079.3333 | 2710.2 | 3.9506 | 2687.7 | 0.65862
2729.7 | 9.0969 |  | 2738.6 | 2.4356 | 2744.3 | 0.82377 | 2747.6 | 9.123 | 2749.8 | 83046 | 2752.2 | 1.9213 | 2729.7 | 0.82377
2771.7 | 5.7289 |  | 2780.6 | 0.66022 | 2786.3 | 0.70166 | 2789.6 | 3.1558 | 2791.8 | 81912.6667 | 2794.2 | 3.0121 | 2771.7 | 0.66022
2813.7 | 2.1529 |  | 2822.6 | 2.3097 | 2828.3 | 2.8291 | 2831.6 | 4.1755 | 2833.8 | 122919 | 2836.2 | 0.78653 | 2813.7 | 0.78653
2855.7 | 6.904 |  | 2864.6 | 5.3815 | 2870.3 | 1.0279 | 2873.6 | 2.7413 | 2875.8 | 81912.6667 | 2878.2 | 1.3136 | 2855.7 | 1.0279

## C5-C6
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 150.2063 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38959.3552 | 1 | 0 | 38959.3552 | 1 | 0 |  | -50.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3556 | 1 | 0 | 38959.3556 | 1 | 0 |  | -8.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3561 | 1 | 0 | 38959.3561 | 1 | 0 |  | 33.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3566 | 1 | 0 | 38959.3566 | 1 | 0 |  | 75.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3571 | 1 | 0 | 38959.3571 | 1 | 0 |  | 117.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3576 | 1 | 0 | 38959.3576 | 1 | 0 |  | 159.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3581 | 1 | 0 | 38959.3581 | 1 | 0 |  | 201.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3586 | 1 | 0 | 38959.3586 | 1 | 0 |  | 243.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.359 | 1 | 0 | 38959.3591 | 1 | 0 |  | 285.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3595 | 1 | 0 | 38959.3595 | 1 | 0 |  | 327.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.36 | 1 | 0 | 38959.36 | 1 | 0 |  | 369.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3605 | 2 | 0 | 38959.3605 | 1 | 0 |  | 411.5 | 501.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122919 | 245938 | 122918.9988
38959.361 | 1 | 0 | 38959.361 | 1 | 0 |  | 453.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3615 | 1 | 0 | 38959.3615 | 1 | 0 |  | 495.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.362 | 1 | 0 | 38959.362 | 1 | 0 |  | 537.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3624 | 1 | 0 | 38959.3625 | 1 | 0 |  | 579.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3629 | 1 | 0 | 38959.3629 | 1 | 0 |  | 621.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3634 | 1 | 0 | 38959.3634 | 1 | 0 |  | 663.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3639 | 1 | 0 | 38959.3639 | 1 | 0 |  | 705.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3644 | 1 | 0 | 38959.3644 | 1 | 0 |  | 747.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3649 | 1 | 0 |  | 1 | 0 |  | 789 | 879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3654 | 1 | 0 | 38959.3654 | 1 | 0 |  | 831.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3658 | 1 | 0 | 38959.3659 | 1 | 0 |  | 873.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3663 | 1 | 0 | 38959.3663 | 1 | 0 |  | 915.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3668 | 1 | 0 | 38959.3668 | 1 | 0 |  | 957.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3673 | 1 | 0 | 38959.3673 | 1 | 0 |  | 999.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3678 | 1 | 0 | 38959.3678 | 1 | 0 |  | 1041.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3683 | 1 | 0 | 38959.3683 | 1 | 0 |  | 1083.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3688 | 1 | 0 | 38959.3688 | 1 | 0 |  | 1125.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3692 | 1 | 0 | 38959.3693 | 1 | 0 |  | 1167.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3697 | 1 | 0 | 38959.3697 | 1 | 0 |  | 1209.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3702 | 1 | 0 | 38959.3702 | 1 | 0 |  | 1251.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3707 | 1 | 0 | 38959.3707 | 1 | 0 |  | 1293.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3712 | 1 | 0 | 38959.3712 | 1 | 0 |  | 1335.5 | 1425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3717 | 1 | 0 | 38959.3717 | 1 | 0 |  | 1377.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3722 | 1 | 0 | 38959.3722 | 1 | 0 |  | 1419.5 | 1509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3727 | 1 | 0 | 38959.3727 | 1 | 0 |  | 1461.5 | 1551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3731 | 1 | 0 | 38959.3731 | 1 | 0 |  | 1503.5 | 1593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3736 | 1 | 0 | 38959.3736 | 1 | 0 |  | 1545.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3741 | 1 | 0 | 38959.3741 | 1 | 0 |  | 1587.5 | 1677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
38959.3746 | 2 | 0 | 38959.3746 | 2 | 0 |  | 1629.5 | 1719.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122919 | 122919 | 122918.9988
38959.3751 | 2 | 0 | 38959.3751 | 2 | 0 |  | 1671.5 | 1761.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122919 | 122919 | 122918.9988
38959.3756 | 801 | 0 | 38959.3756 | 2 | 0 |  | 1713.5 | 1803.5 | 48.9011 | 0 | 0.1221 | 0 | 0.48901 | 0 | 0.001221 | 0 | 0.48901 | 0.001221 | 207.1635 | 122919 | 206.6745
38959.3761 | 101 | 0 | 38959.3761 | 2 | 0 |  | 1755.5 | 1845.5 | 6.1661 | 0 | 0.1221 | 0 | 0.061661 | 0 | 0.001221 | 0 | 0.061661 | 0.001221 | 2336.0198 | 122919 | 2335.9581
38959.3765 | 2 | 0 | 38959.3766 | 2 | 0 |  | 1797.5 | 1887.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122919 | 122919 | 122918.9988
38959.377 | 11 | 0 | 38959.377 | 2 | 0 |  | 1839.5 | 1929.5 | 0.67155 | 0 | 0.1221 | 0 | 0.0067155 | 0 | 0.001221 | 0 | 0.0067155 | 0.001221 | 22267.0909 | 122919 | 22267.0842
38959.3775 | 3 | 0 | 38959.3775 | 2 | 0 |  | 1881.5 | 1971.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 81912.6667 | 122919 | 81912.6648
38959.378 | 2 | 0 | 38959.378 | 14 | 0 |  | 1923.5 | 2013.5 | 0.1221 | 0 | 0.8547 | 0 | 0.001221 | 0 | 0.008547 | 0 | 0.001221 | 0.008547 | 122919 | 17474.1429 | 122918.9988
38959.3785 | 73 | 17 | 38959.3785 | 8 | 0 |  | 1965.5 | 2055.5 | 4.4567 | 1.0379 | 0.4884 | 0 | 0.044567 | 0.010379 | 0.004884 | 0 | 0.034188 | 0.004884 | 4267.4045 | 30654.75 | 13898.0743
38959.379 | 92 | 0 | 38959.379 | 1955 | 41 |  | 2007.5 | 2097.5 | 5.6166 | 0 | 119.3529 | 2.5031 | 0.056166 | 0 | 1.1935 | 0.025031 | 0.056166 | 1.1685 | 2574.3261 | 28.5465 | 2574.2699
38959.3795 | 681 | 22 | 38959.3795 | 470 | 4 |  | 2049.5 | 2139.5 | 41.5751 | 1.3431 | 28.6935 | 0.2442 | 0.41575 | 0.013431 | 0.28694 | 0.002442 | 0.40232 | 0.28449 | 272.1324 | 428.4717 | 6476.5452
38959.3799 | 526 | 0 | 38959.38 | 2235 | 0 |  | 2091.5 | 2181.5 | 32.1123 | 0 | 136.4469 | 0 | 0.32112 | 0 | 1.3645 | 0 | 0.32112 | 1.3645 | 367.7529 | 10.0841 | 367.4317
38959.3804 | 513 | 0 | 38959.3804 | 2205 | 0 |  | 2133.5 | 2223.5 | 31.3187 | 0 | 134.6154 | 0 | 0.31319 | 0 | 1.3462 | 0 | 0.31319 | 1.3462 | 379.6062 | 11.5819 | 379.2931
38959.3809 | 1495 | 0 | 38959.3809 | 2197 | 0 |  | 2175.5 | 2265.5 | 91.2698 | 0 | 134.127 | 0 | 0.9127 | 0 | 1.3413 | 0 | 0.9127 | 1.3413 | 64.5739 | 11.9882 | 63.6612
38959.3814 | 1688 | 0 | 38959.3814 | 2188 | 0 |  | 2217.5 | 2307.5 | 103.0525 | 0 | 133.5775 | 0 | 1.0305 | 0 | 1.3358 | 0 | 1.0305 | 1.3358 | 45.7571 | 12.4488 | 44.7266
38959.3819 | 1061 | 0 | 38959.3819 | 2050 | 0 |  | 2259.5 | 2349.5 | 64.7741 | 0 | 125.1526 | 0 | 0.64774 | 0 | 1.2515 | 0 | 0.64774 | 1.2515 | 131.8926 | 20.0185 | 131.2448
38959.3824 | 3 | 0 | 38959.3824 | 2444 | 0 |  | 2301.5 | 2391.5 | 0.18315 | 0 | 149.2063 | 0 | 0.0018315 | 0 | 1.4921 | 0 | 0.0018315 | 1.4921 | 81912.6667 | 0.67021 | 81912.6648
38959.3829 | 1745 | 0 | 38959.3829 | 2136 | 0 |  | 2343.5 | 2433.5 | 106.5324 | 0 | 130.4029 | 0 | 1.0653 | 0 | 1.304 | 0 | 1.0653 | 1.304 | 40.996 | 15.1863 | 39.9307
38959.3833 | 356 | 0 | 38959.3834 | 2188 | 0 |  | 2385.5 | 2475.5 | 21.7338 | 0 | 133.5775 | 0 | 0.21734 | 0 | 1.3358 | 0 | 0.21734 | 1.3358 | 591.118 | 12.4488 | 590.9006
38959.3838 | 4 | 0 | 38959.3838 | 1971 | 0 |  | 2427.5 | 2517.5 | 0.2442 | 0 | 120.3297 | 0 | 0.002442 | 0 | 1.2033 | 0 | 0.002442 | 1.2033 | 61409.5 | 24.829 | 61409.4976
38959.3843 | 422 | 0 | 38959.3843 | 1966 | 0 |  | 2469.5 | 2559.5 | 25.7631 | 0 | 120.0244 | 0 | 0.25763 | 0 | 1.2002 | 0 | 0.25763 | 1.2002 | 483.0284 | 25.1465 | 482.7708
38959.3848 | 3 | 0 | 38959.3848 | 2158 | 1 |  | 2511.5 | 2601.5 | 0.18315 | 0 | 131.746 | 0.06105 | 0.0018315 | 0 | 1.3175 | 0.0006105 | 0.0018315 | 1.3168 | 81912.6667 | 14.0649 | 81912.6648
38959.3853 | 3 | 0 | 38959.3853 | 1916 | 0 |  | 2553.5 | 2643.5 | 0.18315 | 0 | 116.9719 | 0 | 0.0018315 | 0 | 1.1697 | 0 | 0.0018315 | 1.1697 | 81912.6667 | 28.4123 | 81912.6648
38959.3858 | 50 | 0 | 38959.3858 | 2217 | 0 |  | 2595.5 | 2685.5 | 3.0525 | 0 | 135.348 | 0 | 0.030525 | 0 | 1.3535 | 0 | 0.030525 | 1.3535 | 4820.76 | 10.9779 | 4820.7295
38959.3863 | 2 | 0 | 38959.3863 | 1979 | 0 |  | 2637.5 | 2727.5 | 0.1221 | 0 | 120.8181 | 0 | 0.001221 | 0 | 1.2082 | 0 | 0.001221 | 1.2082 | 122919 | 24.3244 | 122918.9988
38959.3867 | 2 | 0 | 38959.3868 | 2194 | 0 |  | 2679.5 | 2769.5 | 0.1221 | 0 | 133.9438 | 0 | 0.001221 | 0 | 1.3394 | 0 | 0.001221 | 1.3394 | 122919 | 12.1413 | 122918.9988
38959.3872 | 2 | 0 | 38959.3872 | 2142 | 0 |  | 2721.5 | 2811.5 | 0.1221 | 0 | 130.7692 | 0 | 0.001221 | 0 | 1.3077 | 0 | 0.001221 | 1.3077 | 122919 | 14.8637 | 122918.9988
38959.3877 | 2 | 0 | 38959.3877 | 2414 | 0 |  | 2763.5 | 2853.5 | 0.1221 | 0 | 147.3748 | 0 | 0.001221 | 0 | 1.4737 | 0 | 0.001221 | 1.4737 | 122919 | 1.9213 | 122918.9988
38959.3882 | 3 | 0 | 38959.3882 | 2077 | 0 |  | 2805.5 | 2895.5 | 0.18315 | 0 | 126.801 | 0 | 0.0018315 | 0 | 1.268 | 0 | 0.0018315 | 1.268 | 81912.6667 | 18.4584 | 81912.6648
38959.3887 | 2 | 0 | 38959.3887 | 2049 | 0 |  | 2847.5 | 2937.5 | 0.1221 | 0 | 125.0916 | 0 | 0.001221 | 0 | 1.2509 | 0 | 0.001221 | 1.2509 | 122919 | 20.0771 | 122918.9988
38959.3892 | 3 | 0 | 38959.3892 | 2215 | 0 |  | 2889.5 | 2979.5 | 0.18315 | 0 | 135.2259 | 0 | 0.0018315 | 0 | 1.3523 | 0 | 0.0018315 | 1.3523 | 81912.6667 | 11.0781 | 81912.6648

## B4-C6
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 154.1136 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38959.3551 | 1 | 0 | 38959.3551 | 1 | 0 |  | -53 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3556 | 1 | 0 | 38959.3556 | 1 | 0 |  | -11 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3561 | 1 | 0 | 38959.3561 | 1 | 0 |  | 31 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3566 | 1 | 0 | 38959.3566 | 1 | 0 |  | 73 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3571 | 1 | 0 | 38959.3571 | 1 | 0 |  | 115 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3575 | 1 | 0 | 38959.3576 | 1 | 0 |  | 157 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.358 | 1 | 0 | 38959.3581 | 1 | 0 |  | 199 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3585 | 1 | 0 | 38959.3585 | 1 | 0 |  | 241 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.359 | 1 | 0 | 38959.359 | 1 | 0 |  | 283 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3595 | 1 | 0 | 38959.3595 | 1 | 0 |  | 325 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.36 | 1 | 0 | 38959.36 | 1 | 0 |  | 367 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3605 | 1 | 0 | 38959.3605 | 1 | 0 |  | 408.5 | 498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3609 | 1 | 0 | 38959.361 | 1 | 0 |  | 451 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3614 | 1 | 0 | 38959.3614 | 1 | 0 |  | 492.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3619 | 1 | 0 | 38959.3619 | 1 | 0 |  | 535 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3624 | 1 | 0 | 38959.3624 | 1 | 0 |  | 577 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3629 | 1 | 0 | 38959.3629 | 1 | 0 |  | 619 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3634 | 1 | 0 | 38959.3634 | 1 | 0 |  | 661 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3639 | 1 | 0 | 38959.3639 | 1 | 0 |  | 702.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3644 | 1 | 0 | 38959.3644 | 1 | 0 |  | 745 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3648 | 1 | 0 | 38959.3648 | 1 | 0 |  | 786.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3653 | 1 | 0 | 38959.3653 | 1 | 0 |  | 828.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3658 | 1 | 0 | 38959.3658 | 1 | 0 |  | 870.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3663 | 1 | 0 | 38959.3663 | 1 | 0 |  | 912.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3668 | 1 | 0 | 38959.3668 | 1 | 0 |  | 954.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3673 | 1 | 0 | 38959.3673 | 1 | 0 |  | 996.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3678 | 1 | 0 | 38959.3678 | 1 | 0 |  | 1038.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3682 | 1 | 0 | 38959.3683 | 1 | 0 |  | 1080.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3687 | 1 | 0 | 38959.3687 | 1 | 0 |  | 1122.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3692 | 2 | 0 | 38959.3692 | 1 | 0 |  | 1164.5 | 1254.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126119 | 252338 | 126118.9988
38959.3697 | 1 | 0 | 38959.3697 | 1 | 0 |  | 1206.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3702 | 1 | 0 | 38959.3702 | 1 | 0 |  | 1248.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3707 | 1 | 0 | 38959.3707 | 1 | 0 |  | 1290.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3712 | 1 | 0 | 38959.3712 | 1 | 0 |  | 1332.5 | 1422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3716 | 1 | 0 | 38959.3717 | 1 | 0 |  | 1374.5 | 1464.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3721 | 1 | 0 | 38959.3721 | 1 | 0 |  | 1416.5 | 1506.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3726 | 1 | 0 | 38959.3726 | 1 | 0 |  | 1458.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3731 | 1 | 0 | 38959.3731 | 1 | 0 |  | 1500.5 | 1590.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252338 | 252338 | 252337.9994
38959.3736 | 4 | 0 | 38959.3736 | 1 | 0 |  | 1542.5 | 1632.5 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 63009.5 | 252338 | 63009.4976
38959.3741 | 1561 | 0 | 38959.3741 | 2 | 0 |  | 1584.5 | 1674.5 | 95.2991 | 0 | 0.1221 | 0 | 0.95299 | 0 | 0.001221 | 0 | 0.95299 | 0.001221 | 61.7156 | 126119 | 60.7626
38959.3746 | 2449 | 0 | 38959.3746 | 2 | 0 |  | 1626.5 | 1716.5 | 149.5116 | 0 | 0.1221 | 0 | 1.4951 | 0 | 0.001221 | 0 | 1.4951 | 0.001221 | 3.078 | 126119 | 1.5829
38959.375 | 2447 | 0 | 38959.3751 | 3 | 0 |  | 1668.5 | 1758.5 | 149.3895 | 0 | 0.18315 | 0 | 1.4939 | 0 | 0.0018315 | 0 | 1.4939 | 0.0018315 | 3.1622 | 84046 | 1.6683
38959.3755 | 2211 | 0 | 38959.3755 | 2 | 0 |  | 1710.5 | 1800.5 | 134.9817 | 0 | 0.1221 | 0 | 1.3498 | 0 | 0.001221 | 0 | 1.3498 | 0.001221 | 14.1737 | 126119 | 12.8239
38959.376 | 2214 | 0 | 38959.376 | 2 | 0 |  | 1752.5 | 1842.5 | 135.1648 | 0 | 0.1221 | 0 | 1.3516 | 0 | 0.001221 | 0 | 1.3516 | 0.001221 | 14.019 | 126119 | 12.6673
38959.3765 | 1941 | 0 | 38959.3765 | 2 | 0 |  | 1794.5 | 1884.5 | 118.4982 | 0 | 0.1221 | 0 | 1.185 | 0 | 0.001221 | 0 | 1.185 | 0.001221 | 30.0556 | 126119 | 28.8707
38959.377 | 1939 | 0 | 38959.377 | 3 | 0 |  | 1836.5 | 1926.5 | 118.3761 | 0 | 0.18315 | 0 | 1.1838 | 0 | 0.0018315 | 0 | 1.1838 | 0.0018315 | 30.1898 | 84046 | 29.006
38959.3775 | 2404 | 0 | 38959.3775 | 2 | 0 |  | 1878.5 | 1968.5 | 146.7643 | 0 | 0.1221 | 0 | 1.4676 | 0 | 0.001221 | 0 | 1.4676 | 0.001221 | 5.0075 | 126119 | 3.5398
38959.378 | 1938 | 0 | 38959.378 | 5 | 0 |  | 1920.5 | 2010.5 | 118.315 | 0 | 0.30525 | 0 | 1.1832 | 0 | 0.0030525 | 0 | 1.1832 | 0.0030525 | 30.257 | 50387.6 | 29.0738
38959.3784 | 2051 | 0 | 38959.3785 | 31 | 0 |  | 1962.5 | 2052.5 | 125.2137 | 0 | 1.8926 | 0 | 1.2521 | 0 | 0.018926 | 0 | 1.2521 | 0.018926 | 23.0804 | 8043.1613 | 21.8283
38959.3789 | 2490 | 0 | 38959.3789 | 1585 | 0 |  | 2004.5 | 2094.5 | 152.0147 | 0 | 96.7643 | 0 | 1.5201 | 0 | 0.96764 | 0 | 1.5201 | 0.96764 | 1.3807 | 59.2669 | 0.13942
38959.3794 | 2255 | 0 | 38959.3794 | 208 | 0 |  | 2046.5 | 2136.5 | 137.6679 | 0 | 12.6984 | 0 | 1.3767 | 0 | 0.12698 | 0 | 1.3767 | 0.12698 | 11.9459 | 1113.6442 | 10.5692
38959.3799 | 2332 | 0 | 38959.3799 | 598 | 0 |  | 2088.5 | 2178.5 | 142.3687 | 0 | 36.5079 | 0 | 1.4237 | 0 | 0.36508 | 0 | 1.4237 | 0.36508 | 8.2496 | 322.1371 | 6.8259
38959.3804 | 2083 | 0 | 38959.3804 | 2217 | 0 |  | 2130.5 | 2220.5 | 127.1673 | 0 | 135.348 | 0 | 1.2717 | 0 | 1.3535 | 0 | 1.2717 | 1.3535 | 21.1896 | 13.8647 | 19.918
38959.3809 | 2508 | 0 | 38959.3809 | 1975 | 0 |  | 2172.5 | 2262.5 | 153.1136 | 0 | 120.5739 | 0 | 1.5311 | 0 | 1.2057 | 0 | 1.5311 | 1.2057 | 0.65311 | 27.8167 | 0.87803
38959.3814 | 2453 | 0 | 38959.3814 | 2179 | 0 |  | 2214.5 | 2304.5 | 149.7558 | 0 | 133.0281 | 0 | 1.4976 | 0 | 1.3303 | 0 | 1.4976 | 1.3303 | 2.9099 | 15.8504 | 1.4123
38959.3819 | 2500 | 0 | 38959.3819 | 2006 | 0 |  | 2256.5 | 2346.5 | 152.6252 | 0 | 122.4664 | 0 | 1.5263 | 0 | 1.2247 | 0 | 1.5263 | 1.2247 | 0.9752 | 25.8415 | 0.55105
38959.3823 | 1946 | 0 | 38959.3823 | 2121 | 0 |  | 2298.5 | 2388.5 | 118.8034 | 0 | 129.4872 | 0 | 1.188 | 0 | 1.2949 | 0 | 1.188 | 1.2949 | 29.7215 | 19.0184 | 28.5334
38959.3828 | 2388 | 0 | 38959.3828 | 2192 | 0 |  | 2340.5 | 2430.5 | 145.7875 | 0 | 133.8217 | 0 | 1.4579 | 0 | 1.3382 | 0 | 1.4579 | 1.3382 | 5.7111 | 15.1633 | 4.2532
38959.3833 | 2128 | 0 | 38959.3833 | 2138 | 0 |  | 2382.5 | 2472.5 | 129.9145 | 0 | 130.525 | 0 | 1.2991 | 0 | 1.3053 | 0 | 1.2991 | 1.3053 | 18.6269 | 18.072 | 17.3277
38959.3838 | 2486 | 0 | 38959.3838 | 1911 | 0 |  | 2424.5 | 2514.5 | 151.7705 | 0 | 116.6667 | 0 | 1.5177 | 0 | 1.1667 | 0 | 1.5177 | 1.1667 | 1.5438 | 32.0973 | 0.026141
38959.3843 | 2418 | 0 | 38959.3843 | 2379 | 0 |  | 2466.5 | 2556.5 | 147.619 | 0 | 145.2381 | 0 | 1.4762 | 0 | 1.4524 | 0 | 1.4762 | 1.4524 | 4.3995 | 6.111 | 2.9233
38959.3848 | 2458 | 0 | 38959.3848 | 1908 | 0 |  | 2508.5 | 2598.5 | 150.0611 | 0 | 116.4835 | 0 | 1.5006 | 0 | 1.1648 | 0 | 1.5006 | 1.1648 | 2.7006 | 32.305 | 1.2
38959.3853 | 2117 | 0 | 38959.3853 | 2322 | 0 |  | 2550.5 | 2640.5 | 129.243 | 0 | 141.7582 | 0 | 1.2924 | 0 | 1.4176 | 0 | 1.2924 | 1.4176 | 19.2433 | 8.7158 | 17.9508
38959.3857 | 2067 | 0 | 38959.3858 | 2417 | 0 |  | 2592.5 | 2682.5 | 126.1905 | 0 | 147.558 | 0 | 1.2619 | 0 | 1.4756 | 0 | 1.2619 | 1.4756 | 22.1277 | 4.4427 | 20.8658
38959.3862 | 2133 | 0 | 38959.3862 | 2233 | 0 |  | 2634.5 | 2724.5 | 130.2198 | 0 | 136.3248 | 0 | 1.3022 | 0 | 1.3632 | 0 | 1.3022 | 1.3632 | 18.3488 | 13.0488 | 17.0466
38959.3867 | 1939 | 0 | 38959.3867 | 2078 | 0 |  | 2676.5 | 2766.5 | 118.3761 | 0 | 126.862 | 0 | 1.1838 | 0 | 1.2686 | 0 | 1.1838 | 1.2686 | 30.1898 | 21.4812 | 29.006
38959.3872 | 2340 | 0 | 38959.3872 | 2295 | 0 |  | 2718.5 | 2808.5 | 142.8571 | 0 | 140.1099 | 0 | 1.4286 | 0 | 1.4011 | 0 | 1.4286 | 1.4011 | 7.8795 | 9.9948 | 6.4509
38959.3877 | 2078 | 0 | 38959.3877 | 1912 | 0 |  | 2760.5 | 2850.5 | 126.862 | 0 | 116.7277 | 0 | 1.2686 | 0 | 1.1673 | 0 | 1.2686 | 1.1673 | 21.4812 | 32.0282 | 20.2126
38959.3882 | 2022 | 0 | 38959.3882 | 2044 | 0 |  | 2802.5 | 2892.5 | 123.4432 | 0 | 124.7863 | 0 | 1.2344 | 0 | 1.2479 | 0 | 1.2344 | 1.2479 | 24.8457 | 23.502 | 23.6113
38959.3887 | 2209 | 0 | 38959.3887 | 2358 | 0 |  | 2844.5 | 2934.5 | 134.8596 | 0 | 143.956 | 0 | 1.3486 | 0 | 1.4396 | 0 | 1.3486 | 1.4396 | 14.277 | 7.056 | 12.9285
38959.3891 | 2116 | 0 | 38959.3892 | 2173 | 0 |  | 2886.5 | 2976.5 | 129.1819 | 0 | 132.6618 | 0 | 1.2918 | 0 | 1.3266 | 0 | 1.2918 | 1.3266 | 19.2996 | 16.1703 | 18.0078

## B4-C5
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 154.4188 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38959.3551 | 1 | 0 | 38959.3551 | 1 | 0 |  | -56 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3556 | 1 | 0 | 38959.3556 | 1 | 0 |  | -14 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3561 | 1 | 0 | 38959.3561 | 1 | 0 |  | 28 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3565 | 1 | 0 | 38959.3566 | 1 | 0 |  | 70 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.357 | 1 | 0 | 38959.357 | 1 | 0 |  | 112 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3575 | 1 | 0 | 38959.3575 | 1 | 0 |  | 154 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.358 | 1 | 0 | 38959.358 | 1 | 0 |  | 196 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3585 | 1 | 0 | 38959.3585 | 1 | 0 |  | 238 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.359 | 1 | 0 | 38959.359 | 1 | 0 |  | 280 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3595 | 1 | 0 | 38959.3595 | 1 | 0 |  | 322 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3599 | 1 | 0 | 38959.36 | 1 | 0 |  | 364 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3604 | 1 | 0 | 38959.3605 | 1 | 0 |  | 406 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3609 | 1 | 0 | 38959.3609 | 1 | 0 |  | 448 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3614 | 1 | 0 | 38959.3614 | 1 | 0 |  | 490 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3619 | 1 | 0 | 38959.3619 | 1 | 0 |  | 532 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3624 | 1 | 0 | 38959.3624 | 1 | 0 |  | 574 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3629 | 1 | 0 | 38959.3629 | 1 | 0 |  | 616 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3633 | 1 | 0 | 38959.3634 | 1 | 0 |  | 658 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3638 | 1 | 0 | 38959.3639 | 1 | 0 |  | 700 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3643 | 1 | 0 | 38959.3643 | 1 | 0 |  | 742 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3648 | 1 | 0 | 38959.3648 | 1 | 0 |  | 784 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3653 | 1 | 0 | 38959.3653 | 1 | 0 |  | 826 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3658 | 1 | 0 | 38959.3658 | 1 | 0 |  | 868 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3663 | 1 | 0 | 38959.3663 | 1 | 0 |  | 910 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3667 | 1 | 0 | 38959.3668 | 1 | 0 |  | 952 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3672 | 1 | 0 | 38959.3673 | 1 | 0 |  | 994 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3677 | 1 | 0 | 38959.3677 | 1 | 0 |  | 1036 | 1126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3682 | 1 | 0 | 38959.3682 | 1 | 0 |  | 1078 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3687 | 1 | 0 | 38959.3687 | 1 | 0 |  | 1120 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3692 | 1 | 0 | 38959.3692 | 1 | 0 |  | 1162 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3697 | 1 | 0 | 38959.3697 | 1 | 0 |  | 1204 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3702 | 1 | 0 | 38959.3702 | 1 | 0 |  | 1246 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3706 | 1 | 0 | 38959.3707 | 1 | 0 |  | 1288 | 1378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3711 | 1 | 0 | 38959.3711 | 1 | 0 |  | 1330 | 1420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3716 | 1 | 0 | 38959.3716 | 1 | 0 |  | 1372 | 1462 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3721 | 1 | 0 | 38959.3721 | 1 | 0 |  | 1414 | 1504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3726 | 1 | 0 | 38959.3726 | 1 | 0 |  | 1456 | 1546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3731 | 1 | 0 | 38959.3731 | 1 | 0 |  | 1498 | 1588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3736 | 1 | 0 | 38959.3736 | 1 | 0 |  | 1540 | 1630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.374 | 1311 | 1 | 38959.3741 | 2 | 0 |  | 1582 | 1672 | 80.0366 | 0.06105 | 0.1221 | 0 | 0.80037 | 0.0006105 | 0.001221 | 0 | 0.79976 | 0.001221 | 93.0062 | 126369 | 121641.7408
38959.3745 | 2429 | 1 | 38959.3745 | 2 | 0 |  | 1624 | 1714 | 148.2906 | 0.06105 | 0.1221 | 0 | 1.4829 | 0.0006105 | 0.001221 | 0 | 1.4823 | 0.001221 | 4.1343 | 126369 | 9930.1419
38959.375 | 2164 | 1 | 38959.375 | 2 | 0 |  | 1666 | 1756 | 132.1123 | 0.06105 | 0.1221 | 0 | 1.3211 | 0.0006105 | 0.001221 | 0 | 1.3205 | 0.001221 | 16.8923 | 126369 | 36409.1882
38959.3755 | 2045 | 1 | 38959.3755 | 2 | 0 |  | 1708 | 1798 | 124.8474 | 0.06105 | 0.1221 | 0 | 1.2485 | 0.0006105 | 0.001221 | 0 | 1.2479 | 0.001221 | 23.6977 | 126369 | 48299.7788
38959.376 | 2273 | 1 | 38959.376 | 4 | 0 |  | 1750 | 1840 | 138.7668 | 0.06105 | 0.2442 | 0 | 1.3877 | 0.0006105 | 0.002442 | 0 | 1.3871 | 0.002442 | 11.2843 | 63134.5 | 25497.6138
38959.3765 | 2099 | 1 | 38959.3765 | 3 | 0 |  | 1791.5 | 1881.5 | 128.1441 | 0.06105 | 0.18315 | 0 | 1.2814 | 0.0006105 | 0.0018315 | 0 | 1.2808 | 0.0018315 | 20.5138 | 84212.6667 | 42887.0729
38959.377 | 2369 | 1 | 38959.377 | 3 | 0 |  | 1834 | 1924 | 144.6276 | 0.06105 | 0.18315 | 0 | 1.4463 | 0.0006105 | 0.0018315 | 0 | 1.4457 | 0.0018315 | 6.7728 | 84212.6667 | 15919.0966
38959.3774 | 2202 | 1 | 38959.3775 | 5 | 0 |  | 1876 | 1966 | 134.4322 | 0.06105 | 0.30525 | 0 | 1.3443 | 0.0006105 | 0.0030525 | 0 | 1.3437 | 0.0030525 | 14.8742 | 50487.6 | 32573.4822
38959.3779 | 1987 | 1 | 38959.3779 | 3 | 0 |  | 1917.5 | 2007.5 | 121.3065 | 0.06105 | 0.18315 | 0 | 1.2131 | 0.0006105 | 0.0018315 | 0 | 1.2125 | 0.0018315 | 27.3102 | 84212.6667 | 54073.789
38959.3784 | 2419 | 1 | 38959.3784 | 31 | 0 |  | 1959.5 | 2049.5 | 147.6801 | 0.06105 | 1.8926 | 0 | 1.4768 | 0.0006105 | 0.018926 | 0 | 1.4762 | 0.018926 | 4.565 | 8059.2903 | 10803.9442
38959.3789 | 2055 | 1 | 38959.3789 | 27 | 0 |  | 2001.5 | 2091.5 | 125.4579 | 0.06105 | 1.6484 | 0 | 1.2546 | 0.0006105 | 0.016484 | 0 | 1.254 | 0.016484 | 23.0955 | 9268.0741 | 46832.688
38959.3794 | 2154 | 1 | 38959.3794 | 719 | 1 |  | 2043.5 | 2133.5 | 131.5018 | 0.06105 | 43.895 | 0.06105 | 1.315 | 0.0006105 | 0.43895 | 0.0006105 | 1.3144 | 0.43834 | 17.4384 | 254.1721 | 26867.4317
38959.3799 | 2463 | 1 | 38959.3799 | 990 | 1 |  | 2086 | 2176 | 150.3663 | 0.06105 | 60.4396 | 0.06105 | 1.5037 | 0.0006105 | 0.6044 | 0.0006105 | 1.5031 | 0.60379 | 2.6969 | 161.7132 | 4039.8455
38959.3804 | 2195 | 1 | 38959.3804 | 927 | 1 |  | 2127.5 | 2217.5 | 134.0049 | 0.06105 | 56.5934 | 0.06105 | 1.34 | 0.0006105 | 0.56593 | 0.0006105 | 1.3394 | 0.56532 | 15.2446 | 174.2778 | 21183.1684
38959.3808 | 2155 | 1 | 38959.3809 | 1512 | 1 |  | 2170 | 2260 | 131.5629 | 0.06105 | 92.3077 | 0.06105 | 1.3156 | 0.0006105 | 0.92308 | 0.0006105 | 1.315 | 0.92247 | 17.3926 | 67.5888 | 15058.4619
38959.3813 | 2389 | 1 | 38959.3814 | 51 | 1 |  | 2212 | 2302 | 145.8486 | 0.06105 | 3.1136 | 0.06105 | 1.4585 | 0.0006105 | 0.031136 | 0.0006105 | 1.4579 | 0.030525 | 5.8786 | 7512.7183 | 13754.9117
38959.3818 | 2360 | 1 | 38959.3818 | 8 | 0 |  | 2254 | 2344 | 144.0781 | 0.06105 | 0.4884 | 0 | 1.4408 | 0.0006105 | 0.004884 | 0 | 1.4402 | 0.004884 | 7.1802 | 31517.25 | 16784.7443
38959.3823 | 2003 | 1 | 38959.3823 | 3 | 0 |  | 2295.5 | 2385.5 | 122.2833 | 0.06105 | 0.18315 | 0 | 1.2228 | 0.0006105 | 0.0018315 | 0 | 1.2222 | 0.0018315 | 26.2927 | 84212.6667 | 52475.6867
38959.3828 | 2358 | 1 | 38959.3828 | 3 | 0 |  | 2337.5 | 2427.5 | 143.956 | 0.06105 | 0.18315 | 0 | 1.4396 | 0.0006105 | 0.0018315 | 0 | 1.4389 | 0.0018315 | 7.2711 | 84212.6667 | 17017.7919
38959.3833 | 2394 | 1 | 38959.3833 | 5 | 0 |  | 2379.5 | 2469.5 | 146.1538 | 0.06105 | 0.30525 | 0 | 1.4615 | 0.0006105 | 0.0030525 | 0 | 1.4609 | 0.0030525 | 5.6573 | 50487.6 | 13411.4362
38959.3838 | 2054 | 1 | 38959.3838 | 4 | 0 |  | 2421.5 | 2511.5 | 125.3968 | 0.06105 | 0.2442 | 0 | 1.254 | 0.0006105 | 0.002442 | 0 | 1.2534 | 0.002442 | 23.1554 | 63134.5 | 47362.9808
38959.3842 | 2490 | 1 | 38959.3843 | 3 | 0 |  | 2463.5 | 2553.5 | 152.0147 | 0.06105 | 0.18315 | 0 | 1.5201 | 0.0006105 | 0.0018315 | 0 | 1.5195 | 0.0018315 | 1.5822 | 84212.6667 | 3833.4479
38959.3847 | 2513 | 1 | 38959.3847 | 4 | 0 |  | 2505.5 | 2595.5 | 153.4188 | 0.06105 | 0.2442 | 0 | 1.5342 | 0.0006105 | 0.002442 | 0 | 1.5336 | 0.002442 | 0.65207 | 63134.5 | 1535.5678
38959.3852 | 1982 | 1 | 38959.3852 | 3 | 0 |  | 2547.5 | 2637.5 | 121.0012 | 0.06105 | 0.18315 | 0 | 1.21 | 0.0006105 | 0.0018315 | 0 | 1.2094 | 0.0018315 | 27.6315 | 84212.6667 | 54573.196
38959.3857 | 2119 | 1 |  | 3 | 0 |  | 2589 | 2679 | 129.3651 | 0.06105 | 0.18315 | 0 | 1.2937 | 0.0006105 | 0.0018315 | 0 | 1.293 | 0.0018315 | 19.3758 | 84212.6667 | 40889.445
38959.3862 | 2492 | 1 | 38959.3862 | 2 | 0 |  | 2631.5 | 2721.5 | 152.1368 | 0.06105 | 0.1221 | 0 | 1.5214 | 0.0006105 | 0.001221 | 0 | 1.5208 | 0.001221 | 1.5006 | 126369 | 3635.1234
38959.3867 | 2018 | 1 | 38959.3867 | 3 | 0 |  | 2673.5 | 2763.5 | 123.199 | 0.06105 | 0.18315 | 0 | 1.232 | 0.0006105 | 0.0018315 | 0 | 1.2314 | 0.0018315 | 25.3535 | 84212.6667 | 50977.4658
38959.3872 | 2299 | 1 | 38959.3872 | 2 | 0 |  | 2715.5 | 2805.5 | 140.3541 | 0.06105 | 0.1221 | 0 | 1.4035 | 0.0006105 | 0.001221 | 0 | 1.4029 | 0.001221 | 10.0252 | 126369 | 22919.8627
38959.3877 | 2318 | 1 | 38959.3877 | 2 | 0 |  | 2757.5 | 2847.5 | 141.514 | 0.06105 | 0.1221 | 0 | 1.4151 | 0.0006105 | 0.001221 | 0 | 1.4145 | 0.001221 | 9.123 | 126369 | 21021.3651
38959.3881 | 2236 | 1 | 38959.3881 | 2 | 0 |  | 2799.5 | 2889.5 | 136.5079 | 0.06105 | 0.1221 | 0 | 1.3651 | 0.0006105 | 0.001221 | 0 | 1.3645 | 0.001221 | 13.1266 | 126369 | 29214.8813
38959.3886 | 2115 | 1 | 38959.3886 | 2 | 0 |  | 2841.5 | 2931.5 | 129.1209 | 0.06105 | 0.1221 | 0 | 1.2912 | 0.0006105 | 0.001221 | 0 | 1.2906 | 0.001221 | 19.6017 | 126369 | 41305.3137
38959.3891 | 2397 | 1 | 38959.3891 | 2 | 0 |  | 2883.5 | 2973.5 | 146.337 | 0.06105 | 0.1221 | 0 | 1.4634 | 0.0006105 | 0.001221 | 0 | 1.4628 | 0.001221 | 5.525 | 126368.9999 | 13127.6117

## B3-C6
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 151.1221 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38959.3551 | 1 | 0 | 38959.3551 | 1 | 0 |  | -58.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3555 | 1 | 0 | 38959.3556 | 1 | 0 |  | -16.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.356 | 1 | 0 | 38959.356 | 1 | 0 |  | 25.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3565 | 1 | 0 | 38959.3565 | 1 | 0 |  | 67.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.357 | 1 | 0 | 38959.357 | 1 | 0 |  | 109.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3575 | 1 | 0 | 38959.3575 | 1 | 0 |  | 151.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.358 | 1 | 0 | 38959.358 | 1 | 0 |  | 193.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3585 | 1 | 0 | 38959.3585 | 1 | 0 |  | 235.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3589 | 1 | 0 | 38959.359 | 1 | 0 |  | 277.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3594 | 1 | 0 | 38959.3594 | 1 | 0 |  | 319.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3599 | 1 | 0 | 38959.3599 | 1 | 0 |  | 361.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3604 | 1 | 0 | 38959.3604 | 1 | 0 |  | 403 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3609 | 1 | 0 | 38959.3609 | 1 | 0 |  | 445.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3614 | 1 | 0 | 38959.3614 | 1 | 0 |  | 487.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3619 | 1 | 0 | 38959.3619 | 1 | 0 |  | 529.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3623 | 1 | 0 | 38959.3624 | 1 | 0 |  | 571.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3628 | 1 | 0 | 38959.3628 | 1 | 0 |  | 613.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3633 | 1 | 1 | 38959.3633 | 1 | 0 |  | 655.5 | 745.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 612255638.44 | 247438 | 247238.0808
38959.3638 | 1 | 0 | 38959.3638 | 1 | 0 |  | 697.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3643 | 1 | 0 | 38959.3643 | 1 | 0 |  | 739 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3648 | 1 | 0 | 38959.3648 | 1 | 0 |  | 781 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3653 | 1 | 0 | 38959.3653 | 1 | 0 |  | 823.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3657 | 1 | 0 | 38959.3658 | 1 | 0 |  | 865 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3662 | 1 | 0 | 38959.3662 | 1 | 0 |  | 907 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3667 | 1 | 0 | 38959.3667 | 1 | 0 |  | 949 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3672 | 1 | 0 | 38959.3672 | 1 | 0 |  | 991 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3677 | 1 | 0 | 38959.3677 | 1 | 0 |  | 1033 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3682 | 1 | 0 | 38959.3682 | 1 | 0 |  | 1075 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3687 | 1 | 0 | 38959.3687 | 1 | 0 |  | 1117 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3691 | 1 | 0 | 38959.3692 | 1 | 0 |  | 1159 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3696 | 1 | 0 | 38959.3697 | 1 | 0 |  | 1201 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3701 | 1 | 0 | 38959.3701 | 1 | 0 |  | 1243 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3706 | 1 | 0 | 38959.3706 | 1 | 0 |  | 1285 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3711 | 1 | 0 | 38959.3711 | 1 | 0 |  | 1327 | 1417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.3716 | 68 | 1 | 38959.3716 | 1 | 0 |  | 1369 | 1459 | 4.1514 | 0.06105 | 0.06105 | 0 | 0.041514 | 0.0006105 | 0.0006105 | 0 | 0.040904 | 0.0006105 | 3593.1262 | 247438 | 240540.7875
38959.3721 | 116 | 1 | 38959.3721 | 1 | 0 |  | 1411 | 1501 | 7.0818 | 0.06105 | 0.06105 | 0 | 0.070818 | 0.0006105 | 0.0006105 | 0 | 0.070208 | 0.0006105 | 2051.642 | 247438 | 235742.7265
38959.3725 | 154 | 1 | 38959.3726 | 1 | 0 |  | 1453 | 1543 | 9.4017 | 0.06105 | 0.06105 | 0 | 0.094017 | 0.0006105 | 0.0006105 | 0 | 0.093407 | 0.0006105 | 1517.2458 | 247438 | 231944.2617
38959.373 | 3 | 0 | 38959.3731 | 1 | 0 |  | 1495 | 1585 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 82412.6667 | 247438 | 82412.6648
38959.3735 | 1 | 0 | 38959.3735 | 1 | 0 |  | 1537 | 1627 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.374 | 154 | 1 | 38959.374 | 1 | 0 |  | 1579 | 1669 | 9.4017 | 0.06105 | 0.06105 | 0 | 0.094017 | 0.0006105 | 0.0006105 | 0 | 0.093407 | 0.0006105 | 1517.2458 | 247438 | 231944.2617
38959.3745 | 602 | 1 | 38959.3745 | 2 | 0 |  | 1621 | 1711 | 36.7521 | 0.06105 | 0.1221 | 0 | 0.36752 | 0.0006105 | 0.001221 | 0 | 0.36691 | 0.001221 | 311.7109 | 123669 | 187086.7198
38959.375 | 1970 | 1 | 38959.375 | 2 | 0 |  | 1663 | 1753 | 120.2686 | 0.06105 | 0.1221 | 0 | 1.2027 | 0.0006105 | 0.001221 | 0 | 1.2021 | 0.001221 | 25.6668 | 123669.0001 | 50397.2483
38959.3755 | 2121 | 1 | 38959.3755 | 2 | 0 |  | 1705 | 1795 | 129.4872 | 0.06105 | 0.1221 | 0 | 1.2949 | 0.0006105 | 0.001221 | 0 | 1.2943 | 0.001221 | 16.716 | 123669 | 35309.4484
38959.3759 | 1962 | 1 | 38959.376 | 3 | 0 |  | 1747 | 1837 | 119.7802 | 0.06105 | 0.18315 | 0 | 1.1978 | 0.0006105 | 0.0018315 | 0 | 1.1972 | 0.0018315 | 26.1795 | 82412.6667 | 51175.9029
38959.3764 | 2297 | 1 | 38959.3765 | 3 | 0 |  | 1789 | 1879 | 140.232 | 0.06105 | 0.18315 | 0 | 1.4023 | 0.0006105 | 0.0018315 | 0 | 1.4017 | 0.0018315 | 7.7692 | 82412.6667 | 17716.5027
38959.3769 | 1937 | 1 | 38959.3769 | 3 | 0 |  | 1831 | 1921 | 118.254 | 0.06105 | 0.18315 | 0 | 1.1825 | 0.0006105 | 0.0018315 | 0 | 1.1819 | 0.0018315 | 27.8089 | 82412.6667 | 53672.873
38959.3774 | 2108 | 1 | 38959.3774 | 3 | 0 |  | 1873 | 1963 | 128.6935 | 0.06105 | 0.18315 | 0 | 1.2869 | 0.0006105 | 0.0018315 | 0 | 1.2863 | 0.0018315 | 17.4362 | 82412.6667 | 36593.5971
38959.3779 | 2356 | 1 | 38959.3779 | 3 | 0 |  | 1915 | 2005 | 143.8339 | 0.06105 | 0.18315 | 0 | 1.4383 | 0.0006105 | 0.0018315 | 0 | 1.4377 | 0.0018315 | 5.0692 | 82412.6667 | 11823.6531
38959.3784 | 2238 | 1 | 38959.3784 | 24 | 0 |  | 1957 | 2047 | 136.63 | 0.06105 | 1.4652 | 0 | 1.3663 | 0.0006105 | 0.014652 | 0 | 1.3657 | 0.014652 | 10.6116 | 10214.0833 | 23408.8182
38959.3789 | 2272 | 1 | 38959.3789 | 14 | 0 |  | 1999 | 2089 | 138.7057 | 0.06105 | 0.8547 | 0 | 1.3871 | 0.0006105 | 0.008547 | 0 | 1.3864 | 0.008547 | 8.9555 | 17581.2857 | 20123.54
38959.3794 | 1922 | 1 | 38959.3794 | 156 | 0 |  | 2041 | 2131 | 117.3382 | 0.06105 | 9.5238 | 0 | 1.1734 | 0.0006105 | 0.095238 | 0 | 1.1728 | 0.095238 | 28.8079 | 1486.7821 | 51756.8666
38959.3798 | 2279 | 1 | 38959.3799 | 23 | 0 |  | 2083 | 2173 | 139.1331 | 0.06105 | 1.4042 | 0 | 1.3913 | 0.0006105 | 0.014042 | 0 | 1.3907 | 0.014042 | 8.6208 | 10662.5217 | 19356.4626
38959.3803 | 2113 | 1 | 38959.3803 | 2027 | 0 |  | 2125 | 2215 | 128.9988 | 0.06105 | 123.7485 | 0 | 1.29 | 0.0006105 | 1.2375 | 0 | 1.2894 | 1.2375 | 17.1949 | 22.1204 | 6545.8865
38959.3808 | 2152 | 1 | 38959.3808 | 2255 | 0 |  | 2167 | 2257 | 131.3797 | 0.06105 | 137.6679 | 0 | 1.3138 | 0.0006105 | 1.3767 | 0 | 1.3132 | 1.3767 | 15.1058 | 9.7729 | 2870.109
38959.3813 | 2446 | 1 | 38959.3813 | 2238 | 0 |  | 2209 | 2299 | 149.3284 | 0.06105 | 136.63 | 0 | 1.4933 | 0.0006105 | 1.3663 | 0 | 1.4927 | 1.3663 | 1.2063 | 10.6068 | 272.1539
38959.3818 | 2352 | 1 | 38959.3818 | 2065 | 0 |  | 2251 | 2341 | 143.5897 | 0.06105 | 126.0684 | 0 | 1.4359 | 0.0006105 | 1.2607 | 0 | 1.4353 | 1.2607 | 5.2592 | 19.8731 | 2028.8725
38959.3823 | 2455 | 1 | 38959.3823 | 2001 | 0 |  | 2293 | 2383 | 149.8779 | 0.06105 | 122.1612 | 0 | 1.4988 | 0.0006105 | 1.2216 | 0 | 1.4982 | 1.2216 | 0.83191 | 23.7071 | 371.3969
38959.3828 | 2459 | 1 | 38959.3828 | 2181 | 0 |  | 2335 | 2425 | 150.1221 | 0.06105 | 133.1502 | 0 | 1.5012 | 0.0006105 | 1.3315 | 0 | 1.5006 | 1.3315 | 0.66841 | 13.4975 | 182.9038
38959.3832 | 1988 | 1 | 38959.3833 | 2271 | 0 |  | 2377 | 2467 | 121.3675 | 0.06105 | 138.6447 | 0 | 1.2137 | 0.0006105 | 1.3864 | 0 | 1.2131 | 1.3864 | 24.6664 | 8.9996 | 4015.8014
38959.3837 | 2013 | 1 | 38959.3838 | 1963 | 0 |  | 2419 | 2509 | 122.8938 | 0.06105 | 119.8413 | 0 | 1.2289 | 0.0006105 | 1.1984 | 0 | 1.2283 | 1.1984 | 23.025 | 26.1019 | 9550.125
38959.3842 | 2366 | 1 | 38959.3842 | 2162 | 0 |  | 2461 | 2551 | 144.4444 | 0.06105 | 131.9902 | 0 | 1.4444 | 0.0006105 | 1.3199 | 0 | 1.4438 | 1.3199 | 4.6385 | 14.4949 | 1372.0772
38959.3847 | 2429 | 1 | 38959.3847 | 2247 | 0 |  | 2503 | 2593 | 148.2906 | 0.06105 | 137.1795 | 0 | 1.4829 | 0.0006105 | 1.3718 | 0 | 1.4823 | 1.3718 | 1.918 | 10.1638 | 418.6785
38959.3852 | 2095 | 1 | 38959.3852 | 1976 | 0 |  | 2545 | 2635 | 127.8999 | 0.06105 | 120.6349 | 0 | 1.279 | 0.0006105 | 1.2063 | 0 | 1.2784 | 1.2063 | 18.1996 | 25.2723 | 7653.5637
38959.3857 | 2400 | 1 | 38959.3857 | 2421 | 0 |  | 2587 | 2677 | 146.5201 | 0.06105 | 147.8022 | 0 | 1.4652 | 0.0006105 | 1.478 | 0 | 1.4646 | 1.478 | 3.2016 | 2.2462 | 163.4005
38959.3862 | 2304 | 1 | 38959.3862 | 2352 | 0 |  | 2629 | 2719 | 140.6593 | 0.06105 | 143.5897 | 0 | 1.4066 | 0.0006105 | 1.4359 | 0 | 1.406 | 1.4359 | 7.5037 | 5.2457 | 849.2225
38959.3866 | 2439 | 1 | 38959.3867 | 2399 | 0 |  | 2671 | 2761 | 148.9011 | 0.06105 | 146.4591 | 0 | 1.489 | 0.0006105 | 1.4646 | 0 | 1.4884 | 1.4646 | 1.5117 | 3.1838 | 109.1681
38959.3871 | 2286 | 1 | 38959.3872 | 2115 | 0 |  | 2713 | 2803 | 139.5604 | 0.06105 | 129.1209 | 0 | 1.3956 | 0.0006105 | 1.2912 | 0 | 1.395 | 1.2912 | 8.3093 | 17.0392 | 2742.5439
38959.3876 | 2361 | 1 | 38959.3876 | 2272 | 0 |  | 2755 | 2845 | 144.1392 | 0.06105 | 138.7057 | 0 | 1.4414 | 0.0006105 | 1.3871 | 0 | 1.4408 | 1.3871 | 4.8697 | 8.9516 | 931.5428
38959.3881 | 1935 | 1 | 38959.3881 | 2403 | 0 |  | 2797 | 2887 | 118.1319 | 0.06105 | 146.7033 | 0 | 1.1813 | 0.0006105 | 1.467 | 0 | 1.1807 | 1.467 | 28.4291 | 3.0121 | 1577.1447
38959.3886 | 2364 | 1 | 38959.3886 | 2143 | 0 |  | 2839 | 2929 | 144.3223 | 0.06105 | 130.8303 | 0 | 1.4432 | 0.0006105 | 1.3083 | 0 | 1.4426 | 1.3083 | 4.7264 | 15.51 | 1482.1201
38959.3891 | 2097 | 1 | 38959.3891 | 1938 | 0 |  | 2881 | 2971 | 128.022 | 0.06105 | 118.315 | 0 | 1.2802 | 0.0006105 | 1.1832 | 0 | 1.2796 | 1.1832 | 18.0836 | 27.7286 | 8192.5387

## B3-C5
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.2821 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38959.355 | 1 | 0 | 38959.355 | 1 | 0 |  | -61.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3555 | 1 | 0 | 38959.3555 | 1 | 0 |  | -19.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.356 | 1 | 0 | 38959.356 | 1 | 0 |  | 22.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3565 | 1 | 0 | 38959.3565 | 1 | 0 |  | 64.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.357 | 1 | 0 | 38959.357 | 1 | 0 |  | 106.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3575 | 1 | 0 | 38959.3575 | 1 | 0 |  | 148.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3579 | 1 | 0 | 38959.358 | 1 | 0 |  | 190.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3584 | 1 | 0 | 38959.3584 | 1 | 0 |  | 232.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3589 | 1 | 0 | 38959.3589 | 1 | 0 |  | 274.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3594 | 1 | 0 | 38959.3594 | 1 | 0 |  | 316.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3599 | 1 | 0 | 38959.3599 | 1 | 0 |  | 358.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3604 | 1 | 0 | 38959.3604 | 1 | 0 |  | 400.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3609 | 1 | 0 | 38959.3609 | 1 | 0 |  | 442.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3613 | 1 | 0 | 38959.3614 | 1 | 0 |  | 484.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3618 | 1 | 0 | 38959.3618 | 1 | 0 |  | 526.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3623 | 1 | 0 | 38959.3623 | 1 | 0 |  | 568.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3628 | 1 | 0 | 38959.3628 | 1 | 0 |  | 610.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3633 | 1 | 0 | 38959.3633 | 1 | 0 |  | 652.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3638 | 1 | 0 | 38959.3638 | 1 | 0 |  | 694.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3643 | 1 | 0 | 38959.3643 | 1 | 0 |  | 736.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3647 | 1 | 0 | 38959.3648 | 1 | 0 |  | 778.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3652 | 1 | 0 | 38959.3652 | 1 | 0 |  | 820.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3657 | 1 | 0 | 38959.3657 | 1 | 0 |  | 862.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3662 | 1 | 0 | 38959.3662 | 1 | 0 |  | 904.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3667 | 1 | 0 | 38959.3667 | 1 | 0 |  | 946.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3672 | 1 | 0 | 38959.3672 | 1 | 0 |  | 988.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3677 | 1 | 0 | 38959.3677 | 1 | 0 |  | 1030.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3681 | 1 | 0 | 38959.3682 | 1 | 0 |  | 1072.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3686 | 1 | 0 | 38959.3686 | 1 | 0 |  | 1114.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3691 | 1 | 0 | 38959.3691 | 1 | 0 |  | 1156.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3696 | 1 | 0 | 38959.3696 | 1 | 0 |  | 1198.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3701 | 1 | 0 | 38959.3701 | 1 | 0 |  | 1240.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3706 | 1 | 0 | 38959.3706 | 2 | 0 |  | 1282.5 | 1372.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249338 | 124619 | 249337.9994
38959.3711 | 1 | 0 | 38959.3711 | 1 | 0 |  | 1324.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3716 | 1 | 0 | 38959.3716 | 1 | 0 |  | 1366.5 | 1456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.372 | 815 | 1 | 38959.372 | 1 | 0 |  | 1408.5 | 1498.5 | 49.7558 | 0.06105 | 0.06105 | 0 | 0.49756 | 0.0006105 | 0.0006105 | 0 | 0.49695 | 0.0006105 | 206.3121 | 249338 | 167770.7135
38959.3725 | 387 | 1 | 38959.3725 | 1 | 0 |  | 1450.5 | 1540.5 | 23.6264 | 0.06105 | 0.06105 | 0 | 0.23626 | 0.0006105 | 0.0006105 | 0 | 0.23565 | 0.0006105 | 545.9539 | 249338 | 210553.555
38959.373 | 1 | 0 | 38959.373 | 1 | 0 |  | 1492.5 | 1582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3735 | 108 | 1 | 38959.3735 | 1 | 0 |  | 1534.5 | 1624.5 | 6.5934 | 0.06105 | 0.06105 | 0 | 0.065934 | 0.0006105 | 0.0006105 | 0 | 0.065324 | 0.0006105 | 2230.27 | 249338 | 238442.3698
38959.374 | 2 | 0 | 38959.374 | 1 | 0 |  | 1576.5 | 1666.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124619 | 249338 | 124618.9988
38959.3745 | 478 | 1 | 38959.3745 | 1 | 0 |  | 1618.5 | 1708.5 | 29.1819 | 0.06105 | 0.06105 | 0 | 0.29182 | 0.0006105 | 0.0006105 | 0 | 0.29121 | 0.0006105 | 422.7215 | 249338 | 201457.2032
38959.3749 | 777 | 1 | 38959.375 | 2 | 0 |  | 1660 | 1750 | 47.4359 | 0.06105 | 0.1221 | 0 | 0.47436 | 0.0006105 | 0.001221 | 0 | 0.47375 | 0.001221 | 221.3121 | 124619 | 171500.3802
38959.3754 | 2116 | 1 | 38959.3755 | 7 | 0 |  | 1702.5 | 1792.5 | 129.1819 | 0.06105 | 0.42735 | 0 | 1.2918 | 0.0006105 | 0.0042735 | 0 | 1.2912 | 0.0042735 | 17.8903 | 35534 | 37632.0955
38959.3759 | 2030 | 1 | 38959.3759 | 721 | 0 |  | 1744 | 1834 | 123.9316 | 0.06105 | 44.0171 | 0 | 1.2393 | 0.0006105 | 0.44017 | 0 | 1.2387 | 0.44017 | 22.8917 | 245.9612 | 32944.0111
38959.3764 | 2418 | 1 | 38959.3764 | 3 | 0 |  | 1786 | 1876 | 147.619 | 0.06105 | 0.18315 | 0 | 1.4762 | 0.0006105 | 0.0018315 | 0 | 1.4756 | 0.0018315 | 3.1601 | 83046 | 7528.934
38959.3769 | 1907 | 1 | 38959.3769 | 3 | 0 |  | 1828.5 | 1918.5 | 116.4225 | 0.06105 | 0.18315 | 0 | 1.1642 | 0.0006105 | 0.0018315 | 0 | 1.1636 | 0.0018315 | 30.8174 | 83046 | 58567.4759
38959.3774 | 1891 | 1 | 38959.3774 | 33 | 0 |  | 1870 | 1960 | 115.4457 | 0.06105 | 2.0147 | 0 | 1.1545 | 0.0006105 | 0.020147 | 0 | 1.1538 | 0.020147 | 31.9251 | 7458.7273 | 59441.0669
38959.3779 | 2418 | 1 | 38959.3779 | 89 | 0 |  | 1912.5 | 2002.5 | 147.619 | 0.06105 | 5.4335 | 0 | 1.4762 | 0.0006105 | 0.054335 | 0 | 1.4756 | 0.054335 | 3.1602 | 2702.6742 | 7269.0426
38959.3783 | 2434 | 1 | 38959.3784 | 24 | 0 |  | 1954 | 2044 | 148.5958 | 0.06105 | 1.4652 | 0 | 1.486 | 0.0006105 | 0.014652 | 0 | 1.4853 | 0.014652 | 2.4817 | 10293.25 | 5880.8668
38959.3788 | 2283 | 1 | 38959.3789 | 671 | 0 |  | 1996.5 | 2086.5 | 139.3773 | 0.06105 | 40.9646 | 0 | 1.3938 | 0.0006105 | 0.40965 | 0 | 1.3932 | 0.40965 | 9.2644 | 271.7407 | 15378.6786
38959.3793 | 1931 | 1 | 38959.3793 | 740 | 0 |  | 2038.5 | 2128.5 | 117.8877 | 0.06105 | 45.177 | 0 | 1.1789 | 0.0006105 | 0.45177 | 0 | 1.1783 | 0.45177 | 29.1971 | 237.0784 | 39554.0465
38959.3798 | 1963 | 1 | 38959.3798 | 121 | 0 |  | 2080 | 2170 | 119.8413 | 0.06105 | 7.3871 | 0 | 1.1984 | 0.0006105 | 0.073871 | 0 | 1.1978 | 0.073871 | 27.0843 | 1961.4711 | 50465.1771
38959.3803 | 2388 | 1 | 38959.3803 | 1534 | 0 |  | 2122 | 2212 | 145.7875 | 0.06105 | 93.6508 | 0 | 1.4579 | 0.0006105 | 0.93651 | 0 | 1.4573 | 0.93651 | 4.4596 | 62.6063 | 4057.3146
38959.3808 | 2372 | 1 | 38959.3808 | 12 | 0 |  | 2164.5 | 2254.5 | 144.8107 | 0.06105 | 0.7326 | 0 | 1.4481 | 0.0006105 | 0.007326 | 0 | 1.4475 | 0.007326 | 5.1615 | 20686.5 | 12079.6063
38959.3813 | 2188 | 1 | 38959.3813 | 9 | 0 |  | 2206.5 | 2296.5 | 133.5775 | 0.06105 | 0.54945 | 0 | 1.3358 | 0.0006105 | 0.0054945 | 0 | 1.3352 | 0.0054945 | 14.0092 | 27615.3333 | 30427.8155
38959.3818 | 2113 | 1 | 38959.3818 | 862 | 0 |  | 2248.5 | 2338.5 | 128.9988 | 0.06105 | 52.6252 | 0 | 1.29 | 0.0006105 | 0.52625 | 0 | 1.2894 | 0.52625 | 18.0623 | 189.3712 | 24892.9475
38959.3822 | 2146 | 1 | 38959.3823 | 3 | 0 |  | 2290 | 2380 | 131.0134 | 0.06105 | 0.18315 | 0 | 1.3101 | 0.0006105 | 0.0018315 | 0 | 1.3095 | 0.0018315 | 16.2415 | 83046 | 34696.2205
38959.3827 | 2002 | 1 | 38959.3827 | 4 | 0 |  | 2332.5 | 2422.5 | 122.2222 | 0.06105 | 0.2442 | 0 | 1.2222 | 0.0006105 | 0.002442 | 0 | 1.2216 | 0.002442 | 24.6067 | 62259.5 | 49059.2021
38959.3832 | 2090 | 1 | 38959.3832 | 4 | 0 |  | 2374 | 2464 | 127.5946 | 0.06105 | 0.2442 | 0 | 1.2759 | 0.0006105 | 0.002442 | 0 | 1.2753 | 0.002442 | 19.3576 | 62259.5 | 40273.3138
38959.3837 | 2444 | 1 | 38959.3837 | 4 | 0 |  | 2416 | 2506 | 149.2063 | 0.06105 | 0.2442 | 0 | 1.4921 | 0.0006105 | 0.002442 | 0 | 1.4915 | 0.002442 | 2.0622 | 62259.5 | 4930.0814
38959.3842 | 1984 | 1 | 38959.3842 | 177 | 0 |  | 2458 | 2548 | 121.1233 | 0.06105 | 10.8059 | 0 | 1.2112 | 0.0006105 | 0.10806 | 0 | 1.2106 | 0.10806 | 25.7388 | 1309.2542 | 47323.4641
38959.3847 | 2118 | 1 | 38959.3847 | 3 | 0 |  | 2500 | 2590 | 129.304 | 0.06105 | 0.18315 | 0 | 1.293 | 0.0006105 | 0.0018315 | 0 | 1.2924 | 0.0018315 | 17.7789 | 83046 | 37492.8529
38959.3852 | 2099 | 1 | 38959.3852 | 3 | 0 |  | 2542 | 2632 | 128.1441 | 0.06105 | 0.18315 | 0 | 1.2814 | 0.0006105 | 0.0018315 | 0 | 1.2808 | 0.0018315 | 18.8456 | 83046 | 39390.5678
38959.3856 | 2478 | 1 | 38959.3857 | 3 | 0 |  | 2584 | 2674 | 151.2821 | 0.06105 | 0.18315 | 0 | 1.5128 | 0.0006105 | 0.0018315 | 0 | 1.5122 | 0.0018315 | 0.66128 | 83046 | 1536.1502
38959.3861 | 2185 | 1 | 38959.3861 | 4 | 0 |  | 2626 | 2716 | 133.3944 | 0.06105 | 0.2442 | 0 | 1.3339 | 0.0006105 | 0.002442 | 0 | 1.3333 | 0.002442 | 14.1658 | 62259.5 | 30788.548
38959.3866 | 2251 | 1 | 38959.3866 | 2 | 0 |  | 2668 | 2758 | 137.4237 | 0.06105 | 0.1221 | 0 | 1.3742 | 0.0006105 | 0.001221 | 0 | 1.3736 | 0.001221 | 10.8169 | 124619 | 24218.5659
38959.3871 | 2116 | 1 | 38959.3871 | 2 | 0 |  | 2710 | 2800 | 129.1819 | 0.06105 | 0.1221 | 0 | 1.2918 | 0.0006105 | 0.001221 | 0 | 1.2912 | 0.001221 | 17.8903 | 124619 | 37707.7416
38959.3876 | 1917 | 1 | 38959.3876 | 3 | 0 |  | 2752 | 2842 | 117.033 | 0.06105 | 0.18315 | 0 | 1.1703 | 0.0006105 | 0.0018315 | 0 | 1.1697 | 0.0018315 | 30.1347 | 83046 | 57568.6786
38959.3881 | 1919 | 1 | 38959.3881 | 2 | 0 |  | 2794 | 2884 | 117.1551 | 0.06105 | 0.1221 | 0 | 1.1716 | 0.0006105 | 0.001221 | 0 | 1.1709 | 0.001221 | 29.999 | 124619 | 57391.9461
38959.3886 | 2345 | 1 | 38959.3886 | 2 | 0 |  | 2836 | 2926 | 143.1624 | 0.06105 | 0.1221 | 0 | 1.4316 | 0.0006105 | 0.001221 | 0 | 1.431 | 0.001221 | 6.3729 | 124619 | 14826.1029
38959.389 | 2006 | 1 | 38959.3891 | 2 | 0 |  | 2878 | 2968 | 122.4664 | 0.06105 | 0.1221 | 0 | 1.2247 | 0.0006105 | 0.001221 | 0 | 1.2241 | 0.001221 | 24.3581 | 124619 | 48698.9218

## B3-B4
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 154.1746 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38959.355 | 1 | 0 | 38959.355 | 1 | 0 |  | -64.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3555 | 1 | 0 | 38959.3555 | 1 | 0 |  | -22.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.356 | 1 | 0 | 38959.356 | 1 | 0 |  | 19.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3564 | 1 | 0 | 38959.3565 | 1 | 0 |  | 61.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3569 | 1 | 0 | 38959.3569 | 1 | 0 |  | 103.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3574 | 1 | 0 | 38959.3574 | 1 | 0 |  | 145.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3579 | 1 | 0 | 38959.3579 | 1 | 0 |  | 187.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3584 | 1 | 0 | 38959.3584 | 1 | 0 |  | 229.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3589 | 1 | 0 | 38959.3589 | 1 | 0 |  | 271.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3594 | 1 | 0 | 38959.3594 | 1 | 0 |  | 313.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3598 | 1 | 0 | 38959.3599 | 1 | 0 |  | 355.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3603 | 1 | 0 | 38959.3603 | 1 | 0 |  | 397.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3608 | 1 | 0 | 38959.3608 | 1 | 0 |  | 439.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3613 | 1 | 0 | 38959.3613 | 1 | 0 |  | 481.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3618 | 1 | 0 | 38959.3618 | 1 | 0 |  | 523.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3623 | 1 | 0 | 38959.3623 | 1 | 0 |  | 565.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3628 | 1 | 0 | 38959.3628 | 1 | 0 |  | 607.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3633 | 1 | 0 | 38959.3633 | 1 | 0 |  | 649.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3637 | 1 | 0 | 38959.3637 | 1 | 0 |  | 691.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3642 | 1 | 0 | 38959.3642 | 1 | 0 |  | 733.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3647 | 1 | 0 | 38959.3647 | 1 | 0 |  | 775.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3652 | 1 | 0 | 38959.3652 | 1 | 0 |  | 817.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3657 | 1 | 0 | 38959.3657 | 1 | 0 |  | 859.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3662 | 1 | 0 | 38959.3662 | 1 | 0 |  | 901.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3667 | 1 | 0 | 38959.3667 | 1 | 0 |  | 943.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3671 | 1 | 0 | 38959.3672 | 1 | 0 |  | 985.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3676 | 1 | 0 | 38959.3676 | 1 | 0 |  | 1027.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3681 | 1 | 0 | 38959.3681 | 1 | 0 |  | 1069.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3686 | 1 | 0 | 38959.3686 | 1 | 0 |  | 1111.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3691 | 1 | 0 | 38959.3691 | 1 | 0 |  | 1153.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3696 | 1 | 0 | 38959.3696 | 1 | 0 |  | 1195.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3701 | 1 | 0 | 38959.3701 | 1 | 0 |  | 1237.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3705 | 1 | 0 | 38959.3706 | 1 | 0 |  | 1279.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.371 | 1 | 0 | 38959.371 | 1 | 0 |  | 1321.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3715 | 1 | 0 | 38959.3715 | 1 | 0 |  | 1363.5 | 1453.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.372 | 55 | 0 | 38959.372 | 1 | 0 |  | 1405.5 | 1495.5 | 3.3578 | 0 | 0.06105 | 0 | 0.033578 | 0 | 0.0006105 | 0 | 0.033578 | 0.0006105 | 4491.6 | 252438 | 4491.5664
38959.3725 | 54 | 0 | 38959.3725 | 1 | 0 |  | 1447.5 | 1537.5 | 3.2967 | 0 | 0.06105 | 0 | 0.032967 | 0 | 0.0006105 | 0 | 0.032967 | 0.0006105 | 4576.6296 | 252438 | 4576.5967
38959.373 | 1 | 0 | 38959.373 | 1 | 0 |  | 1489.5 | 1579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252438 | 252438 | 252437.9994
38959.3735 | 5 | 0 | 38959.3735 | 1 | 0 |  | 1531.5 | 1621.5 | 0.30525 | 0 | 0.06105 | 0 | 0.0030525 | 0 | 0.0006105 | 0 | 0.0030525 | 0.0006105 | 50407.6 | 252438 | 50407.5969
38959.3739 | 231 | 0 | 38959.374 | 1655 | 0 |  | 1573.5 | 1663.5 | 14.1026 | 0 | 101.0379 | 0 | 0.14103 | 0 | 1.0104 | 0 | 0.14103 | 1.0104 | 993.2381 | 52.5909 | 993.0971
38959.3744 | 1259 | 0 | 38959.3744 | 2298 | 0 |  | 1615.5 | 1705.5 | 76.862 | 0 | 140.293 | 0 | 0.76862 | 0 | 1.4029 | 0 | 0.76862 | 1.4029 | 100.5862 | 9.8947 | 99.8176
38959.3749 | 870 | 0 | 38959.3749 | 2187 | 0 |  | 1657.5 | 1747.5 | 53.1136 | 0 | 133.5165 | 0 | 0.53114 | 0 | 1.3352 | 0 | 0.53114 | 1.3352 | 190.2736 | 15.4723 | 189.7424
38959.3754 | 1947 | 0 | 38959.3754 | 1966 | 0 |  | 1699.5 | 1789.5 | 118.8645 | 0 | 120.0244 | 0 | 1.1886 | 0 | 1.2002 | 0 | 1.1886 | 1.2002 | 29.7062 | 28.4527 | 28.5176
38959.3759 | 2329 | 0 | 38959.3759 | 2126 | 0 |  | 1741.5 | 1831.5 | 142.1856 | 0 | 129.7924 | 0 | 1.4219 | 0 | 1.2979 | 0 | 1.4219 | 1.2979 | 8.4319 | 18.7855 | 7.0101
38959.3764 | 2413 | 0 | 38959.3764 | 2032 | 0 |  | 1783.5 | 1873.5 | 147.3138 | 0 | 124.0537 | 0 | 1.4731 | 0 | 1.2405 | 0 | 1.4731 | 1.2405 | 4.6573 | 24.2805 | 3.1841
38959.3769 | 2131 | 0 | 38959.3769 | 2453 | 0 |  | 1825.5 | 1915.5 | 130.0977 | 0 | 149.7558 | 0 | 1.301 | 0 | 1.4976 | 0 | 1.301 | 1.4976 | 18.5068 | 2.9507 | 17.2058
38959.3773 | 2209 | 0 | 38959.3774 | 2193 | 0 |  | 1867.5 | 1957.5 | 134.8596 | 0 | 133.8828 | 0 | 1.3486 | 0 | 1.3388 | 0 | 1.3486 | 1.3388 | 14.3223 | 15.1564 | 12.9737
38959.3778 | 2095 | 0 | 38959.3778 | 2379 | 0 |  | 1909.5 | 1999.5 | 127.8999 | 0 | 145.2381 | 0 | 1.279 | 0 | 1.4524 | 0 | 1.279 | 1.4524 | 20.5432 | 6.153 | 19.2642
38959.3783 | 2405 | 0 | 38959.3783 | 2281 | 0 |  | 1951.5 | 2041.5 | 146.8254 | 0 | 139.2552 | 0 | 1.4683 | 0 | 1.3926 | 0 | 1.4683 | 1.3926 | 5.0054 | 10.7137 | 3.5372
38959.3788 | 2221 | 0 | 38959.3788 | 2067 | 0 |  | 1993.5 | 2083.5 | 135.5922 | 0 | 126.1905 | 0 | 1.3559 | 0 | 1.2619 | 0 | 1.3559 | 1.2619 | 13.7046 | 22.1761 | 12.3487
38959.3793 | 2295 | 0 | 38959.3793 | 2500 | 0 |  | 2035.5 | 2125.5 | 140.1099 | 0 | 152.6252 | 0 | 1.4011 | 0 | 1.5263 | 0 | 1.4011 | 1.5263 | 10.0383 | 1.0152 | 8.6372
38959.3798 | 1964 | 0 | 38959.3798 | 2493 | 0 |  | 2077.5 | 2167.5 | 119.9023 | 0 | 152.1978 | 0 | 1.199 | 0 | 1.522 | 0 | 1.199 | 1.522 | 28.5835 | 1.2988 | 27.3845
38959.3803 | 2242 | 0 | 38959.3803 | 2408 | 0 |  | 2119.5 | 2209.5 | 136.8742 | 0 | 147.0085 | 0 | 1.3687 | 0 | 1.4701 | 0 | 1.3687 | 1.4701 | 12.6396 | 4.8746 | 11.2709
38959.3808 | 2410 | 0 | 38959.3808 | 2232 | 0 |  | 2161.5 | 2251.5 | 147.1306 | 0 | 136.2637 | 0 | 1.4713 | 0 | 1.3626 | 0 | 1.4713 | 1.3626 | 4.7876 | 13.1443 | 3.3162
38959.3812 | 2150 | 0 | 38959.3812 | 1999 | 0 |  | 2203.5 | 2293.5 | 131.2576 | 0 | 122.0391 | 0 | 1.3126 | 0 | 1.2204 | 0 | 1.3126 | 1.2204 | 17.4595 | 26.3322 | 16.147
38959.3817 | 2273 | 0 | 38959.3817 | 1944 | 0 |  | 2245.5 | 2335.5 | 138.7668 | 0 | 118.6813 | 0 | 1.3877 | 0 | 1.1868 | 0 | 1.3877 | 1.1868 | 11.1034 | 29.9064 | 9.7157
38959.3822 | 2343 | 0 | 38959.3822 | 1950 | 0 |  | 2287.5 | 2377.5 | 143.0403 | 0 | 119.0476 | 0 | 1.4304 | 0 | 1.1905 | 0 | 1.4304 | 1.1905 | 7.784 | 29.5067 | 6.3536
38959.3827 | 2292 | 0 | 38959.3827 | 2160 | 0 |  | 2329.5 | 2419.5 | 139.9267 | 0 | 131.8681 | 0 | 1.3993 | 0 | 1.3187 | 0 | 1.3993 | 1.3187 | 10.1824 | 16.9157 | 8.7831
38959.3832 | 2097 | 0 | 38959.3832 | 2371 | 0 |  | 2371.5 | 2461.5 | 128.022 | 0 | 144.7497 | 0 | 1.2802 | 0 | 1.4475 | 0 | 1.2802 | 1.4475 | 20.4282 | 6.5112 | 19.148
38959.3837 | 2406 | 0 | 38959.3837 | 2183 | 0 |  | 2413.5 | 2503.5 | 146.8864 | 0 | 133.2723 | 0 | 1.4689 | 0 | 1.3327 | 0 | 1.4689 | 1.3327 | 4.9618 | 15.6839 | 3.4929
38959.3842 | 2260 | 0 | 38959.3842 | 2444 | 0 |  | 2455.5 | 2545.5 | 137.9731 | 0 | 149.2063 | 0 | 1.3797 | 0 | 1.4921 | 0 | 1.3797 | 1.4921 | 11.7425 | 3.3298 | 10.3627
38959.3846 | 1965 | 0 | 38959.3847 | 1947 | 0 |  | 2497.5 | 2587.5 | 119.9634 | 0 | 118.8645 | 0 | 1.1996 | 0 | 1.1886 | 0 | 1.1996 | 1.1886 | 28.5181 | 29.7062 | 27.3184
38959.3851 | 1950 | 0 | 38959.3851 | 2031 | 0 |  | 2539.5 | 2629.5 | 119.0476 | 0 | 123.9927 | 0 | 1.1905 | 0 | 1.2399 | 0 | 1.1905 | 1.2399 | 29.5067 | 24.3417 | 28.3162
38959.3856 | 1915 | 0 | 38959.3856 | 2509 | 0 |  | 2581.5 | 2671.5 | 116.9109 | 0 | 153.1746 | 0 | 1.1691 | 0 | 1.5317 | 0 | 1.1691 | 1.5317 | 31.8736 | 0.65285 | 30.7045
38959.3861 | 1925 | 0 | 38959.3861 | 2079 | 0 |  | 2623.5 | 2713.5 | 117.5214 | 0 | 126.9231 | 0 | 1.1752 | 0 | 1.2692 | 0 | 1.1752 | 1.2692 | 31.1886 | 21.4709 | 30.0134
38959.3866 | 2152 | 0 | 38959.3866 | 2359 | 0 |  | 2665.5 | 2755.5 | 131.3797 | 0 | 144.0171 | 0 | 1.3138 | 0 | 1.4402 | 0 | 1.3138 | 1.4402 | 17.3504 | 7.053 | 16.0366
38959.3871 | 2415 | 0 | 38959.3871 | 2277 | 0 |  | 2707.5 | 2797.5 | 147.4359 | 0 | 139.011 | 0 | 1.4744 | 0 | 1.3901 | 0 | 1.4744 | 1.3901 | 4.5706 | 10.9082 | 3.0962
38959.3876 | 2284 | 0 | 38959.3876 | 2012 | 0 |  | 2749.5 | 2839.5 | 139.4383 | 0 | 122.8327 | 0 | 1.3944 | 0 | 1.2283 | 0 | 1.3944 | 1.2283 | 10.5683 | 25.5159 | 9.1739
38959.388 | 2176 | 0 | 38959.3881 | 1954 | 0 |  | 2791.5 | 2881.5 | 132.8449 | 0 | 119.2918 | 0 | 1.3284 | 0 | 1.1929 | 0 | 1.3284 | 1.1929 | 16.0561 | 29.2416 | 14.7276
38959.3885 | 2381 | 0 | 38959.3885 | 2286 | 0 |  | 2833.5 | 2923.5 | 145.3602 | 0 | 139.5604 | 0 | 1.4536 | 0 | 1.3956 | 0 | 1.4536 | 1.3956 | 6.0638 | 10.4716 | 4.6102
38959.389 | 2485 | 0 | 38959.389 | 2458 | 0 |  | 2875.5 | 2965.5 | 151.7094 | 0 | 150.0611 | 0 | 1.5171 | 0 | 1.5006 | 0 | 1.5171 | 1.5006 | 1.6249 | 2.7413 | 0.10786

## A2-C6
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.4652 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38959.355 | 1 | 0 | 38959.355 | 1 | 0 |  | -67 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3554 | 1 | 0 | 38959.3555 | 1 | 0 |  | -25 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3559 | 1 | 0 | 38959.3559 | 1 | 0 |  | 17 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3564 | 1 | 0 | 38959.3564 | 1 | 0 |  | 59 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3569 | 1 | 0 | 38959.3569 | 1 | 0 |  | 101 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3574 | 1 | 0 | 38959.3574 | 1 | 0 |  | 143 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3579 | 1 | 0 | 38959.3579 | 1 | 0 |  | 185 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3584 | 1 | 0 | 38959.3584 | 1 | 0 |  | 227 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3588 | 1 | 0 | 38959.3589 | 1 | 0 |  | 269 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3593 | 1 | 0 | 38959.3593 | 1 | 0 |  | 310.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3598 | 1 | 1 | 38959.3598 | 1 | 0 |  | 353 | 443 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 623191310.44 | 249638 | 249438.0801
38959.3603 | 1 | 0 | 38959.3603 | 1 | 0 |  | 395 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3608 | 1 | 0 | 38959.3608 | 1 | 0 |  | 437 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3613 | 1 | 0 | 38959.3613 | 1 | 0 |  | 479 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3618 | 1 | 0 | 38959.3618 | 1 | 0 |  | 521 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3622 | 1 | 0 | 38959.3623 | 1 | 0 |  | 563 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3627 | 1 | 0 | 38959.3628 | 1 | 0 |  | 605 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3632 | 1 | 0 | 38959.3632 | 1 | 0 |  | 647 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3637 | 1 | 0 | 38959.3637 | 1 | 0 |  | 688.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3642 | 1 | 0 | 38959.3642 | 1 | 0 |  | 730.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3647 | 1 | 0 | 38959.3647 | 1 | 0 |  | 773 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3652 | 1 | 0 | 38959.3652 | 1 | 0 |  | 814.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3656 | 1 | 0 | 38959.3657 | 1 | 0 |  | 856.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3661 | 1 | 0 | 38959.3661 | 1 | 0 |  | 898.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3666 | 1 | 0 | 38959.3666 | 1 | 0 |  | 940.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3671 | 1 | 0 | 38959.3671 | 1 | 0 |  | 982.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3676 | 1 | 0 | 38959.3676 | 1 | 0 |  | 1024.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3681 | 1 | 0 | 38959.3681 | 1 | 0 |  | 1066.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3686 | 1 | 0 | 38959.3686 | 1 | 0 |  | 1108.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3691 | 1 | 0 | 38959.3691 | 1 | 0 |  | 1150.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3695 | 1 | 0 | 38959.3695 | 1 | 0 |  | 1192.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.37 | 1 | 0 | 38959.37 | 1 | 0 |  | 1234.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3705 | 1 | 0 | 38959.3705 | 1 | 0 |  | 1276.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.371 | 1 | 0 | 38959.371 | 1 | 0 |  | 1318.5 | 1408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3715 | 1 | 0 | 38959.3715 | 1 | 0 |  | 1360.5 | 1450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.372 | 1 | 0 | 38959.372 | 1 | 0 |  | 1402.5 | 1492.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3725 | 1 | 0 | 38959.3725 | 1 | 0 |  | 1444.5 | 1534.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3729 | 1 | 0 | 38959.373 | 1 | 0 |  | 1486.5 | 1576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3734 | 1 | 0 | 38959.3734 | 1 | 0 |  | 1528.5 | 1618.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3739 | 1 | 0 | 38959.3739 | 1 | 0 |  | 1570.5 | 1660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3744 | 1 | 0 | 38959.3744 | 1 | 0 |  | 1612.5 | 1702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3749 | 1 | 0 | 38959.3749 | 1 | 0 |  | 1654.5 | 1744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
38959.3754 | 2 | 0 | 38959.3754 | 1 | 0 |  | 1696.5 | 1786.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124769 | 249638 | 124768.9988
38959.3759 | 2 | 0 | 38959.3759 | 2 | 0 |  | 1738.5 | 1828.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124769 | 124769 | 124768.9988
38959.3763 | 2 | 0 | 38959.3764 | 1 | 0 |  | 1780.5 | 1870.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124769 | 249638 | 124768.9988
38959.3768 | 2 | 0 | 38959.3768 | 2 | 0 |  | 1822.5 | 1912.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124769 | 124769 | 124768.9988
38959.3773 | 2 | 0 | 38959.3773 | 1 | 0 |  | 1864.5 | 1954.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124769 | 249638 | 124768.9988
38959.3778 | 2 | 0 | 38959.3778 | 2 | 0 |  | 1906.5 | 1996.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124769 | 124769 | 124768.9988
38959.3783 | 2 | 0 | 38959.3783 | 11 | 0 |  | 1948.5 | 2038.5 | 0.1221 | 0 | 0.67155 | 0 | 0.001221 | 0 | 0.0067155 | 0 | 0.001221 | 0.0067155 | 124769 | 22603.4545 | 124768.9988
38959.3788 | 3 | 0 | 38959.3788 | 68 | 0 |  | 1990.5 | 2080.5 | 0.18315 | 0 | 4.1514 | 0 | 0.0018315 | 0 | 0.041514 | 0 | 0.0018315 | 0.041514 | 83146 | 3572.6176 | 83145.9982
38959.3793 | 4 | 0 | 38959.3793 | 190 | 0 |  | 2032.5 | 2122.5 | 0.2442 | 0 | 11.5995 | 0 | 0.002442 | 0 | 0.116 | 0 | 0.002442 | 0.116 | 62334.5 | 1214.4105 | 62334.4976
38959.3797 | 8 | 0 | 38959.3798 | 1976 | 0 |  | 2074.5 | 2164.5 | 0.4884 | 0 | 120.6349 | 0 | 0.004884 | 0 | 1.2063 | 0 | 0.004884 | 1.2063 | 31117.25 | 26.3856 | 31117.2451
38959.3802 | 1247 | 0 | 38959.3802 | 2079 | 0 |  | 2116.5 | 2206.5 | 76.1294 | 0 | 126.9231 | 0 | 0.76129 | 0 | 1.2692 | 0 | 0.76129 | 1.2692 | 100.2711 | 20.1241 | 99.5098
38959.3807 | 2443 | 0 | 38959.3807 | 2032 | 0 |  | 2158.5 | 2248.5 | 149.1453 | 0 | 124.0537 | 0 | 1.4915 | 0 | 1.2405 | 0 | 1.4915 | 1.2405 | 2.226 | 22.9026 | 0.7345
38959.3812 | 1982 | 0 | 38959.3812 | 2169 | 0 |  | 2200.5 | 2290.5 | 121.0012 | 0 | 132.4176 | 0 | 1.21 | 0 | 1.3242 | 0 | 1.21 | 1.3242 | 26.003 | 15.1397 | 24.793
38959.3817 | 1982 | 0 | 38959.3817 | 2057 | 0 |  | 2242.5 | 2332.5 | 121.0012 | 0 | 125.58 | 0 | 1.21 | 0 | 1.2558 | 0 | 1.21 | 1.2558 | 26.003 | 21.4088 | 24.793
38959.3822 | 2425 | 0 | 38959.3822 | 1894 | 0 |  | 2284.5 | 2374.5 | 148.0464 | 0 | 115.6288 | 0 | 1.4805 | 0 | 1.1563 | 0 | 1.4805 | 1.1563 | 2.9847 | 31.8574 | 1.5043
38959.3827 | 1942 | 0 | 38959.3827 | 2189 | 0 |  | 2326.5 | 2416.5 | 118.5592 | 0 | 133.6386 | 0 | 1.1856 | 0 | 1.3364 | 0 | 1.1856 | 1.3364 | 28.5984 | 14.0877 | 27.4128
38959.3831 | 2053 | 0 | 38959.3832 | 2442 | 0 |  | 2368.5 | 2458.5 | 125.3358 | 0 | 149.0842 | 0 | 1.2534 | 0 | 1.4908 | 0 | 1.2534 | 1.4908 | 21.6454 | 2.2678 | 20.392
38959.3836 | 2078 | 0 | 38959.3836 | 2250 | 0 |  | 2410.5 | 2500.5 | 126.862 | 0 | 137.3626 | 0 | 1.2686 | 0 | 1.3736 | 0 | 1.2686 | 1.3736 | 20.1819 | 10.9947 | 18.9133
38959.3841 | 2401 | 0 | 38959.3841 | 1972 | 0 |  | 2452.5 | 2542.5 | 146.5812 | 0 | 120.3907 | 0 | 1.4658 | 0 | 1.2039 | 0 | 1.4658 | 1.2039 | 4.0142 | 26.642 | 2.5483
38959.3846 | 2137 | 0 | 38959.3846 | 2163 | 0 |  | 2494.5 | 2584.5 | 130.464 | 0 | 132.0513 | 0 | 1.3046 | 0 | 1.3205 | 0 | 1.3046 | 1.3205 | 16.8638 | 15.4591 | 15.5592
38959.3851 | 2331 | 0 | 38959.3851 | 2450 | 0 |  | 2536.5 | 2626.5 | 142.3077 | 0 | 149.5726 | 0 | 1.4231 | 0 | 1.4957 | 0 | 1.4231 | 1.4957 | 7.1377 | 1.9339 | 5.7146
38959.3856 | 1990 | 0 | 38959.3856 | 1977 | 0 |  | 2578.5 | 2668.5 | 121.4896 | 0 | 120.696 | 0 | 1.2149 | 0 | 1.207 | 0 | 1.2149 | 1.207 | 25.4965 | 26.3217 | 24.2816
38959.3861 | 2338 | 0 | 38959.3861 | 1985 | 0 |  | 2620.5 | 2710.5 | 142.735 | 0 | 121.1844 | 0 | 1.4274 | 0 | 1.2118 | 0 | 1.4274 | 1.2118 | 6.8169 | 25.8126 | 5.3896
38959.3866 | 1976 | 0 | 38959.3866 | 2283 | 0 |  | 2662.5 | 2752.5 | 120.6349 | 0 | 139.3773 | 0 | 1.2063 | 0 | 1.3938 | 0 | 1.2063 | 1.3938 | 26.3856 | 9.3903 | 25.1793
38959.387 | 2435 | 0 | 38959.387 | 2000 | 0 |  | 2704.5 | 2794.5 | 148.6569 | 0 | 122.1001 | 0 | 1.4866 | 0 | 1.221 | 0 | 1.4866 | 1.221 | 2.5618 | 24.869 | 1.0752
38959.3875 | 2438 | 0 | 38959.3875 | 2331 | 0 |  | 2746.5 | 2836.5 | 148.84 | 0 | 142.3077 | 0 | 1.4884 | 0 | 1.4231 | 0 | 1.4884 | 1.4231 | 2.4356 | 7.1377 | 0.9472
38959.388 | 2481 | 0 | 38959.388 | 2009 | 0 |  | 2788.5 | 2878.5 | 151.4652 | 0 | 122.6496 | 0 | 1.5147 | 0 | 1.2265 | 0 | 1.5147 | 1.2265 | 0.66022 | 24.3096 | 0.85443
38959.3885 | 2441 | 0 | 38959.3885 | 2248 | 0 |  | 2830.5 | 2920.5 | 149.0232 | 0 | 137.2405 | 0 | 1.4902 | 0 | 1.3724 | 0 | 1.4902 | 1.3724 | 2.3097 | 11.0934 | 0.81948
38959.389 | 2033 | 0 | 38959.389 | 2465 | 0 |  | 2872.5 | 2962.5 | 124.1148 | 0 | 150.4884 | 0 | 1.2411 | 0 | 1.5049 | 0 | 1.2411 | 1.5049 | 22.8421 | 1.3136 | 21.601

## A2-C5
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.3431 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38959.3549 | 1 | 0 | 38959.3549 | 1 | 0 |  | -70 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3554 | 1 | 0 | 38959.3554 | 1 | 0 |  | -28 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3559 | 1 | 0 | 38959.3559 | 1 | 0 |  | 14 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3564 | 1 | 0 | 38959.3564 | 1 | 0 |  | 56 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3569 | 1 | 0 | 38959.3569 | 1 | 0 |  | 98 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3573 | 1 | 1 | 38959.3574 | 1 | 0 |  | 140 | 230 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 622193158.44 | 249438 | 249238.0801
38959.3578 | 1 | 0 | 38959.3579 | 1 | 0 |  | 182 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3583 | 1 | 0 | 38959.3583 | 1 | 0 |  | 224 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3588 | 1 | 0 | 38959.3588 | 1 | 0 |  | 266 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3593 | 1 | 0 | 38959.3593 | 1 | 0 |  | 308 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3598 | 1 | 0 | 38959.3598 | 1 | 0 |  | 350 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3603 | 1 | 0 | 38959.3603 | 1 | 0 |  | 392 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3608 | 1 | 0 | 38959.3608 | 1 | 0 |  | 434 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3612 | 1 | 0 | 38959.3613 | 1 | 0 |  | 476 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3617 | 1 | 0 | 38959.3617 | 1 | 0 |  | 518 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3622 | 1 | 0 | 38959.3622 | 1 | 0 |  | 560 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3627 | 1 | 0 | 38959.3627 | 1 | 0 |  | 602 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3632 | 1 | 0 | 38959.3632 | 1 | 0 |  | 644 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3637 | 1 | 0 | 38959.3637 | 1 | 0 |  | 686 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3642 | 1 | 0 | 38959.3642 | 1 | 0 |  | 728 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3646 | 1 | 0 | 38959.3647 | 1 | 0 |  | 770 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3651 | 1 | 0 | 38959.3652 | 1 | 0 |  | 812 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3656 | 1 | 0 | 38959.3656 | 1 | 0 |  | 854 | 944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3661 | 1 | 0 | 38959.3661 | 1 | 0 |  | 896 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3666 | 1 | 0 | 38959.3666 | 1 | 0 |  | 938 | 1028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3671 | 1 | 0 | 38959.3671 | 1 | 0 |  | 980 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3676 | 1 | 0 | 38959.3676 | 1 | 0 |  | 1022 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.368 | 1 | 0 | 38959.3681 | 1 | 0 |  | 1064 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3685 | 1 | 0 | 38959.3686 | 1 | 0 |  | 1106 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.369 | 1 | 0 | 38959.369 | 1 | 0 |  | 1148 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3695 | 1 | 0 | 38959.3695 | 1 | 0 |  | 1190 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.37 | 1 | 0 | 38959.37 | 1 | 0 |  | 1232 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3705 | 1 | 0 | 38959.3705 | 1 | 0 |  | 1274 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.371 | 1 | 0 | 38959.371 | 1 | 0 |  | 1316 | 1406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3714 | 1 | 0 | 38959.3715 | 1 | 0 |  | 1358 | 1448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3719 | 1 | 0 | 38959.372 | 1 | 0 |  | 1400 | 1490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3724 | 1 | 0 | 38959.3724 | 1 | 0 |  | 1442 | 1532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3729 | 1 | 0 | 38959.3729 | 1 | 0 |  | 1484 | 1574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3734 | 1 | 0 | 38959.3734 | 1 | 0 |  | 1526 | 1616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3739 | 1 | 0 | 38959.3739 | 1 | 0 |  | 1568 | 1658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3744 | 1 | 0 | 38959.3744 | 1 | 0 |  | 1610 | 1700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3748 | 1 | 0 | 38959.3749 | 1 | 0 |  | 1652 | 1742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3753 | 1 | 0 | 38959.3754 | 1 | 0 |  | 1694 | 1784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.3758 | 2 | 0 | 38959.3758 | 792 | 0 |  | 1736 | 1826 | 0.1221 | 0 | 48.3516 | 0 | 0.001221 | 0 | 0.48352 | 0 | 0.001221 | 0.48352 | 124669 | 215.0732 | 124668.9988
38959.3763 | 1 | 0 | 38959.3763 | 2 | 0 |  | 1778 | 1868 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249438 | 124669 | 249437.9994
38959.3768 | 2 | 0 | 38959.3768 | 47 | 0 |  | 1820 | 1910 | 0.1221 | 0 | 2.8694 | 0 | 0.001221 | 0 | 0.028694 | 0 | 0.001221 | 0.028694 | 124669 | 5209.3191 | 124668.9988
38959.3773 | 2 | 0 | 38959.3773 | 137 | 0 |  | 1861.5 | 1951.5 | 0.1221 | 0 | 8.3639 | 0 | 0.001221 | 0 | 0.083639 | 0 | 0.001221 | 0.083639 | 124669 | 1721.4453 | 124668.9988
38959.3778 | 1 | 0 | 38959.3778 | 3 | 0 |  | 1904 | 1994 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 249438 | 83079.3333 | 249437.9994
38959.3783 | 2 | 0 | 38959.3783 | 5 | 0 |  | 1945.5 | 2035.5 | 0.1221 | 0 | 0.30525 | 0 | 0.001221 | 0 | 0.0030525 | 0 | 0.001221 | 0.0030525 | 124669 | 49807.6 | 124668.9988
38959.3787 | 3 | 0 | 38959.3788 | 29 | 0 |  | 1988 | 2078 | 0.18315 | 0 | 1.7705 | 0 | 0.0018315 | 0 | 0.017705 | 0 | 0.0018315 | 0.017705 | 83079.3333 | 8504.7586 | 83079.3315
38959.3792 | 5 | 0 | 38959.3792 | 782 | 0 |  | 2029.5 | 2119.5 | 0.30525 | 0 | 47.7411 | 0 | 0.0030525 | 0 | 0.47741 | 0 | 0.0030525 | 0.47741 | 49807.6 | 219.1023 | 49807.5969
38959.3797 | 8 | 0 | 38959.3797 | 507 | 0 |  | 2072 | 2162 | 0.4884 | 0 | 30.9524 | 0 | 0.004884 | 0 | 0.30952 | 0 | 0.004884 | 0.30952 | 31092.25 | 392.1854 | 31092.2451
38959.3802 | 1164 | 1 | 38959.3802 | 664 | 0 |  | 2114 | 2204 | 71.0623 | 0.06105 | 40.5372 | 0 | 0.71062 | 0.0006105 | 0.40537 | 0 | 0.71001 | 0.40537 | 114.5138 | 275.8102 | 97637.6874
38959.3807 | 2348 | 1 | 38959.3807 | 218 | 0 |  | 2156 | 2246 | 143.3455 | 0.06105 | 13.3089 | 0 | 1.4335 | 0.0006105 | 0.13309 | 0 | 1.4328 | 0.13309 | 6.2798 | 1044.6697 | 13359.2032
38959.3812 | 2315 | 1 | 38959.3812 | 844 | 0 |  | 2197.5 | 2287.5 | 141.3309 | 0.06105 | 51.5263 | 0 | 1.4133 | 0.0006105 | 0.51526 | 0 | 1.4127 | 0.51526 | 7.7969 | 195.6611 | 11870.9192
38959.3817 | 2456 | 1 | 38959.3817 | 1778 | 0 |  | 2239.5 | 2329.5 | 149.9389 | 0.06105 | 108.547 | 0 | 1.4994 | 0.0006105 | 1.0855 | 0 | 1.4988 | 1.0855 | 1.6057 | 40.3476 | 1103.3608
38959.3821 | 2009 | 1 | 38959.3822 | 69 | 0 |  | 2281.5 | 2371.5 | 122.6496 | 0.06105 | 4.2125 | 0 | 1.2265 | 0.0006105 | 0.042125 | 0 | 1.2259 | 0.042125 | 24.2225 | 3516.4928 | 47195.8709
38959.3826 | 1975 | 1 | 38959.3826 | 4 | 0 |  | 2323.5 | 2413.5 | 120.5739 | 0.06105 | 0.2442 | 0 | 1.2057 | 0.0006105 | 0.002442 | 0 | 1.2051 | 0.002442 | 26.3617 | 62284.5 | 51854.7453
38959.3831 | 2333 | 1 | 38959.3831 | 23 | 0 |  | 2365.5 | 2455.5 | 142.4298 | 0.06105 | 1.4042 | 0 | 1.4243 | 0.0006105 | 0.014042 | 0 | 1.4237 | 0.014042 | 6.9631 | 10749.4783 | 15989.2555
38959.3836 | 2479 | 1 | 38959.3836 | 4 | 0 |  | 2407.5 | 2497.5 | 151.3431 | 0.06105 | 0.2442 | 0 | 1.5134 | 0.0006105 | 0.002442 | 0 | 1.5128 | 0.002442 | 0.66102 | 62284.5 | 1535.5346
38959.3841 | 2365 | 1 | 38959.3841 | 4 | 0 |  | 2449.5 | 2539.5 | 144.3834 | 0.06105 | 0.2442 | 0 | 1.4438 | 0.0006105 | 0.002442 | 0 | 1.4432 | 0.002442 | 5.5152 | 62284.5 | 12917.2609
38959.3846 | 2098 | 1 | 38959.3846 | 3 | 0 |  | 2491.5 | 2581.5 | 128.083 | 0.06105 | 0.18315 | 0 | 1.2808 | 0.0006105 | 0.0018315 | 0 | 1.2802 | 0.0018315 | 18.9499 | 83079.3333 | 39590.3463
38959.3851 | 2174 | 1 | 38959.3851 | 3 | 0 |  | 2533.5 | 2623.5 | 132.7228 | 0.06105 | 0.18315 | 0 | 1.3272 | 0.0006105 | 0.0018315 | 0 | 1.3266 | 0.0018315 | 14.7897 | 83079.3333 | 31999.4832
38959.3855 | 2338 | 1 | 38959.3856 | 60 | 0 |  | 2575.5 | 2665.5 | 142.735 | 0.06105 | 3.663 | 0 | 1.4274 | 0.0006105 | 0.03663 | 0 | 1.4267 | 0.03663 | 6.7343 | 4058.9667 | 15261.9931
38959.386 | 2365 | 1 | 38959.386 | 128 | 0 |  | 2617.5 | 2707.5 | 144.3834 | 0.06105 | 7.8144 | 0 | 1.4438 | 0.0006105 | 0.078144 | 0 | 1.4432 | 0.078144 | 5.5154 | 1849.5156 | 12274.348
38959.3865 | 2467 | 1 | 38959.3865 | 3 | 0 |  | 2659.5 | 2749.5 | 150.6105 | 0.06105 | 0.18315 | 0 | 1.5061 | 0.0006105 | 0.0018315 | 0 | 1.5055 | 0.0018315 | 1.1509 | 83079.3333 | 2734.7083
38959.387 | 2030 | 1 | 38959.387 | 3 | 0 |  | 2701.5 | 2791.5 | 123.9316 | 0.06105 | 0.18315 | 0 | 1.2393 | 0.0006105 | 0.0018315 | 0 | 1.2387 | 0.0018315 | 22.9364 | 83079.3333 | 46382.1712
38959.3875 | 2333 | 1 | 38959.3875 | 3 | 0 |  | 2743.5 | 2833.5 | 142.4298 | 0.06105 | 0.18315 | 0 | 1.4243 | 0.0006105 | 0.0018315 | 0 | 1.4237 | 0.0018315 | 6.9631 | 83079.3333 | 16118.5985
38959.388 | 2001 | 1 | 38959.388 | 2 | 0 |  | 2785.5 | 2875.5 | 122.1612 | 0.06105 | 0.1221 | 0 | 1.2216 | 0.0006105 | 0.001221 | 0 | 1.221 | 0.001221 | 24.719 | 124669 | 49298.4565
38959.3885 | 2363 | 1 | 38959.3885 | 2 | 0 |  | 2827.5 | 2917.5 | 144.2613 | 0.06105 | 0.1221 | 0 | 1.4426 | 0.0006105 | 0.001221 | 0 | 1.442 | 0.001221 | 5.6046 | 124669 | 13127.4701
38959.3889 | 2368 | 1 | 38959.389 | 2 | 0 |  | 2869.5 | 2959.5 | 144.5665 | 0.06105 | 0.1221 | 0 | 1.4457 | 0.0006105 | 0.001221 | 0 | 1.4451 | 0.001221 | 5.3815 | 124669 | 12627.8709

## A2-B4
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.7094 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38959.3549 | 1 | 0 | 38959.3549 | 1 | 0 |  | -72.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3554 | 1 | 0 | 38959.3554 | 1 | 0 |  | -30.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3559 | 1 | 0 | 38959.3559 | 0 | 0 |  | 11.5 | 101.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250038 | 500176 | 250037.9994
38959.3564 | 1 | 0 | 38959.3564 | 1 | 0 |  | 53.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3568 | 1 | 0 | 38959.3569 | 1 | 0 |  | 95.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3573 | 1 | 0 | 38959.3573 | 1 | 0 |  | 137.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3578 | 1 | 0 | 38959.3578 | 1 | 0 |  | 179.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3583 | 1 | 0 | 38959.3583 | 1 | 0 |  | 221.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3588 | 1 | 0 | 38959.3588 | 1 | 0 |  | 263.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3593 | 1 | 0 | 38959.3593 | 1 | 0 |  | 305.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3598 | 1 | 0 | 38959.3598 | 1 | 0 |  | 347.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3602 | 1 | 0 | 38959.3603 | 1 | 0 |  | 389.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3607 | 1 | 0 | 38959.3607 | 1 | 0 |  | 431.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3612 | 1 | 0 | 38959.3612 | 1 | 0 |  | 473.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3617 | 1 | 0 | 38959.3617 | 1 | 0 |  | 515.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3622 | 1 | 0 | 38959.3622 | 1 | 0 |  | 557.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3627 | 1 | 0 | 38959.3627 | 1 | 0 |  | 599.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3631 | 1 | 0 | 38959.3632 | 1 | 0 |  | 641 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3636 | 1 | 0 | 38959.3637 | 1 | 0 |  | 683.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3641 | 1 | 0 | 38959.3641 | 1 | 0 |  | 725.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3646 | 1 | 0 | 38959.3646 | 1 | 0 |  | 767.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3651 | 1 | 0 | 38959.3651 | 1 | 0 |  | 809 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3656 | 1 | 0 | 38959.3656 | 1 | 0 |  | 851 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3661 | 1 | 0 | 38959.3661 | 1 | 0 |  | 893 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3666 | 1 | 0 | 38959.3666 | 1 | 0 |  | 935 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.367 | 1 | 0 | 38959.3671 | 1 | 0 |  | 977.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3675 | 1 | 0 | 38959.3675 | 1 | 0 |  | 1019 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.368 | 1 | 0 | 38959.368 | 1 | 0 |  | 1061 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3685 | 1 | 0 | 38959.3685 | 1 | 0 |  | 1103 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.369 | 1 | 0 | 38959.369 | 1 | 0 |  | 1145 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3695 | 1 | 0 | 38959.3695 | 1 | 0 |  | 1187 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.37 | 1 | 0 | 38959.37 | 1 | 0 |  | 1229 | 1319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3704 | 1 | 0 | 38959.3705 | 1 | 0 |  | 1271 | 1361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3709 | 1 | 0 | 38959.3709 | 1 | 0 |  | 1313 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3714 | 1 | 0 | 38959.3714 | 1 | 0 |  | 1355 | 1445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3719 | 1 | 0 | 38959.3719 | 1 | 0 |  | 1397 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3724 | 1 | 0 | 38959.3724 | 1 | 0 |  | 1439 | 1529 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3729 | 1 | 0 | 38959.3729 | 1 | 0 |  | 1481 | 1571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3734 | 1 | 0 | 38959.3734 | 1 | 0 |  | 1523 | 1613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3738 | 1 | 0 | 38959.3739 | 1 | 0 |  | 1565 | 1655 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3743 | 1 | 0 | 38959.3744 | 1 | 0 |  | 1607 | 1697 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.3748 | 2 | 0 | 38959.3748 | 1 | 0 |  | 1649 | 1739 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124969 | 250038 | 124968.9988
| 2 | 0 | 38959.3753 | 2 | 0 |  | 1692 | 1782 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124969 | 124969 | 124968.9988
38959.3758 | 2 | 0 | 38959.3758 | 2 | 0 |  | 1733 | 1823 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124969 | 124969 | 124968.9988
38959.3763 | 3 | 0 | 38959.3763 | 2 | 0 |  | 1775 | 1865 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 83279.3333 | 124969 | 83279.3315
38959.3768 | 2 | 0 | 38959.3768 | 1 | 0 |  | 1817 | 1907 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124969 | 250038 | 124968.9988
38959.3772 | 2 | 0 | 38959.3773 | 2 | 0 |  | 1859 | 1949 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124969 | 124969 | 124968.9988
38959.3777 | 2 | 0 | 38959.3778 | 2 | 0 |  | 1901 | 1991 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124969 | 124969 | 124968.9988
38959.3782 | 3 | 0 | 38959.3782 | 2 | 0 |  | 1943 | 2033 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 83279.3333 | 124969 | 83279.3315
38959.3787 | 3 | 0 | 38959.3787 | 3 | 0 |  | 1985 | 2075 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 83279.3333 | 83279.3333 | 83279.3315
38959.3792 | 5 | 0 | 38959.3792 | 5 | 0 |  | 2027 | 2117 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 49927.6 | 49927.6 | 49927.5969
38959.3797 | 6 | 0 | 38959.3797 | 8 | 1 |  | 2069 | 2159 | 0.3663 | 0 | 0.4884 | 0.06105 | 0.003663 | 0 | 0.004884 | 0.0006105 | 0.003663 | 0.0042735 | 41589.6667 | 35634 | 41589.663
38959.3802 | 292 | 0 | 38959.3802 | 1135 | 0 |  | 2111 | 2201 | 17.8266 | 0 | 69.2918 | 0 | 0.17827 | 0 | 0.69292 | 0 | 0.17827 | 0.69292 | 756.637 | 120.3859 | 756.4587
38959.3806 | 2274 | 0 | 38959.3807 | 2354 | 0 |  | 2153 | 2243 | 138.8278 | 0 | 143.7118 | 0 | 1.3883 | 0 | 1.4371 | 0 | 1.3883 | 1.4371 | 9.9991 | 6.2608 | 8.6108
38959.3811 | 2348 | 0 | 38959.3812 | 2166 | 0 |  | 2195 | 2285 | 143.3455 | 0 | 132.2344 | 0 | 1.4335 | 0 | 1.3223 | 0 | 1.4335 | 1.3223 | 6.5324 | 15.4838 | 5.0989
38959.3816 | 2290 | 0 | 38959.3816 | 2363 | 0 |  | 2237 | 2327 | 139.8046 | 0 | 144.2613 | 0 | 1.398 | 0 | 1.4426 | 0 | 1.398 | 1.4426 | 9.2306 | 5.8561 | 7.8325
38959.3821 | 2331 | 0 | 38959.3821 | 2120 | 0 |  | 2279 | 2369 | 142.3077 | 0 | 129.4261 | 0 | 1.4231 | 0 | 1.2943 | 0 | 1.4231 | 1.2943 | 7.3093 | 17.9896 | 5.8862
38959.3826 | 2238 | 0 | 38959.3826 | 2446 | 0 |  | 2321 | 2411 | 136.63 | 0 | 149.3284 | 0 | 1.3663 | 0 | 1.4933 | 0 | 1.3663 | 1.4933 | 11.7685 | 2.2641 | 10.4022
38959.3831 | 2030 | 0 | 38959.3831 | 2013 | 0 |  | 2363 | 2453 | 123.9316 | 0 | 122.8938 | 0 | 1.2393 | 0 | 1.2289 | 0 | 1.2393 | 1.2289 | 23.2207 | 24.2613 | 21.9814
38959.3836 | 2118 | 0 | 38959.3836 | 2315 | 0 |  | 2405 | 2495 | 129.304 | 0 | 141.3309 | 0 | 1.293 | 0 | 1.4133 | 0 | 1.293 | 1.4133 | 18.101 | 8.051 | 16.808
38959.3841 | 2277 | 0 | 38959.3841 | 2319 | 0 |  | 2447 | 2537 | 139.011 | 0 | 141.5751 | 0 | 1.3901 | 0 | 1.4158 | 0 | 1.3901 | 1.4158 | 9.8542 | 7.8646 | 8.4641
38959.3845 | 2060 | 0 | 38959.3846 | 2404 | 0 |  | 2489 | 2579 | 125.7631 | 0 | 146.7643 | 0 | 1.2576 | 0 | 1.4676 | 0 | 1.2576 | 1.4676 | 21.4262 | 4.0507 | 20.1686
38959.385 | 2379 | 0 | 38959.385 | 2422 | 0 |  | 2531 | 2621 | 145.2381 | 0 | 147.8632 | 0 | 1.4524 | 0 | 1.4786 | 0 | 1.4524 | 1.4786 | 5.1442 | 3.2775 | 3.6918
38959.3855 | 2167 | 0 | 38959.3855 | 2485 | 0 |  | 2573 | 2663 | 132.2955 | 0 | 151.7094 | 0 | 1.323 | 0 | 1.5171 | 0 | 1.323 | 1.5171 | 15.4305 | 0.65915 | 14.1076
38959.386 | 2144 | 0 | 38959.386 | 2348 | 0 |  | 2615 | 2705 | 130.8913 | 0 | 143.3455 | 0 | 1.3089 | 0 | 1.4335 | 0 | 1.3089 | 1.4335 | 16.6688 | 6.5324 | 15.3599
38959.3865 | 1966 | 0 | 38959.3865 | 1953 | 0 |  | 2657 | 2747 | 120.0244 | 0 | 119.2308 | 0 | 1.2002 | 0 | 1.1923 | 0 | 1.2002 | 1.1923 | 27.2319 | 28.0789 | 26.0317
38959.387 | 1983 | 0 | 38959.387 | 2224 | 0 |  | 2699 | 2789 | 121.0623 | 0 | 135.7753 | 0 | 1.2106 | 0 | 1.3578 | 0 | 1.2106 | 1.3578 | 26.1412 | 12.4721 | 24.9306
38959.3875 | 2394 | 0 | 38959.3875 | 2067 | 0 |  | 2741 | 2831 | 146.1538 | 0 | 126.1905 | 0 | 1.4615 | 0 | 1.2619 | 0 | 1.4615 | 1.2619 | 4.4854 | 21.015 | 3.0238
38959.3879 | 2438 | 0 | 38959.388 | 2164 | 0 |  | 2783 | 2873 | 148.84 | 0 | 132.1123 | 0 | 1.4884 | 0 | 1.3211 | 0 | 1.4884 | 1.3211 | 2.5997 | 15.5906 | 1.1113
38959.3884 | 2437 | 0 | 38959.3884 | 1928 | 0 |  | 2825 | 2915 | 148.779 | 0 | 117.7045 | 0 | 1.4878 | 0 | 1.177 | 0 | 1.4878 | 1.177 | 2.6418 | 29.7396 | 1.154
38959.3889 | 2201 | 0 | 38959.3889 | 2124 | 0 |  | 2867 | 2957 | 134.3712 | 0 | 129.6703 | 0 | 1.3437 | 0 | 1.2967 | 0 | 1.3437 | 1.2967 | 13.6474 | 17.7674 | 12.3037

## A2-B3
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.2821 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38959.3549 | 1 | 0 | 38959.3549 | 1 | 0 |  | -75.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3553 | 1 | 0 | 38959.3554 | 1 | 0 |  | -33.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3558 | 1 | 0 | 38959.3558 | 1 | 0 |  | 8.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3563 | 1 | 0 | 38959.3563 | 1 | 0 |  | 50.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3568 | 1 | 0 | 38959.3568 | 1 | 0 |  | 92.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3573 | 1 | 0 | 38959.3573 | 1 | 0 |  | 134.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3578 | 1 | 0 | 38959.3578 | 1 | 0 |  | 176.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3583 | 1 | 0 | 38959.3583 | 1 | 0 |  | 218.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3587 | 1 | 0 | 38959.3588 | 1 | 0 |  | 260.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3592 | 2 | 0 | 38959.3592 | 1 | 0 |  | 302.5 | 392.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124619 | 249338 | 124618.9988
38959.3597 | 1 | 0 | 38959.3597 | 1 | 0 |  | 344.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3602 | 1 | 1 | 38959.3602 | 1 | 0 |  | 386.5 | 476.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 621694382.44 | 249338 | 249138.0802
38959.3607 | 1 | 0 | 38959.3607 | 1 | 0 |  | 428.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3612 | 1 | 0 | 38959.3612 | 1 | 0 |  | 470.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3617 | 1 | 0 | 38959.3617 | 1 | 0 |  | 512.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3622 | 1 | 0 | 38959.3622 | 1 | 0 |  | 554.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3626 | 1 | 0 | 38959.3627 | 1 | 0 |  | 596.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3631 | 1 | 0 | 38959.3631 | 1 | 0 |  | 638.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3636 | 1 | 0 | 38959.3636 | 1 | 0 |  | 680.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3641 | 1 | 0 | 38959.3641 | 1 | 0 |  | 722.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3646 | 1 | 0 | 38959.3646 | 1 | 0 |  | 764.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3651 | 1 | 0 | 38959.3651 | 1 | 0 |  | 806.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3656 | 1 | 0 | 38959.3656 | 1 | 0 |  | 848.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.366 | 1 | 0 | 38959.3661 | 1 | 0 |  | 890.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3665 | 1 | 0 | 38959.3665 | 1 | 0 |  | 932.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.367 | 1 | 0 | 38959.367 | 1 | 0 |  | 974.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3675 | 1 | 0 | 38959.3675 | 1 | 0 |  | 1016.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.368 | 1 | 0 | 38959.368 | 1 | 0 |  | 1058.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3685 | 1 | 0 | 38959.3685 | 1 | 0 |  | 1100.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.369 | 1 | 0 | 38959.369 | 1 | 0 |  | 1142.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3694 | 1 | 0 | 38959.3695 | 1 | 0 |  | 1184.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3699 | 1 | 0 | 38959.3699 | 1 | 0 |  | 1226.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3704 | 1 | 0 | 38959.3704 | 1 | 0 |  | 1268.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3709 | 1 | 0 | 38959.3709 | 1 | 0 |  | 1310.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3714 | 1 | 0 | 38959.3714 | 1 | 0 |  | 1352.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38959.3719 | 1 | 0 | 38959.3719 | 5 | 0 |  | 1394.5 | 1484.5 | 0.06105 | 0 | 0.30525 | 0 | 0.0006105 | 0 | 0.0030525 | 0 | 0.0006105 | 0.0030525 | 249338 | 49787.6 | 249337.9994
38959.3724 | 1 | 0 | 38959.3724 | 99 | 0 |  | 1436.5 | 1526.5 | 0.06105 | 0 | 6.044 | 0 | 0.0006105 | 0 | 0.06044 | 0 | 0.0006105 | 0.06044 | 249338 | 2419.5758 | 249337.9994
38959.3728 | 1 | 0 | 38959.3729 | 105 | 0 |  | 1478.5 | 1568.5 | 0.06105 | 0 | 6.4103 | 0 | 0.0006105 | 0 | 0.064103 | 0 | 0.0006105 | 0.064103 | 249338 | 2275.6 | 249337.9994
38959.3733 | 1 | 0 | 38959.3733 | 2 | 0 |  | 1520.5 | 1610.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 249338 | 124619 | 249337.9994
38959.3738 | 1 | 0 | 38959.3738 | 670 | 0 |  | 1562.5 | 1652.5 | 0.06105 | 0 | 40.9035 | 0 | 0.0006105 | 0 | 0.40904 | 0 | 0.0006105 | 0.40904 | 249338 | 272.2955 | 249337.9994
38959.3743 | 1 | 0 | 38959.3743 | 1302 | 0 |  | 1604.5 | 1694.5 | 0.06105 | 0 | 79.4872 | 0 | 0.0006105 | 0 | 0.79487 | 0 | 0.0006105 | 0.79487 | 249338 | 91.5806 | 249337.9994
38959.3748 | 1 | 0 | 38959.3748 | 1076 | 0 |  | 1646.5 | 1736.5 | 0.06105 | 0 | 65.6899 | 0 | 0.0006105 | 0 | 0.6569 | 0 | 0.0006105 | 0.6569 | 249338 | 131.8197 | 249337.9994
38959.3753 | 2 | 0 | 38959.3753 | 2042 | 0 |  | 1688.5 | 1778.5 | 0.1221 | 0 | 124.6642 | 0 | 0.001221 | 0 | 1.2466 | 0 | 0.001221 | 1.2466 | 124619 | 22.1538 | 124618.9988
38959.3758 | 2 | 0 | 38959.3758 | 1873 | 0 |  | 1730.5 | 1820.5 | 0.1221 | 0 | 114.3468 | 0 | 0.001221 | 0 | 1.1435 | 0 | 0.001221 | 1.1435 | 124619 | 33.1757 | 124618.9988
38959.3763 | 2 | 0 | 38959.3763 | 2091 | 0 |  | 1772.5 | 1862.5 | 0.1221 | 0 | 127.6557 | 0 | 0.001221 | 0 | 1.2766 | 0 | 0.001221 | 1.2766 | 124619 | 19.2912 | 124618.9988
38959.3767 | 2 | 0 | 38959.3767 | 2265 | 0 |  | 1814 | 1904 | 0.1221 | 0 | 138.2784 | 0 | 0.001221 | 0 | 1.3828 | 0 | 0.001221 | 1.3828 | 124619 | 10.1272 | 124618.9988
38959.3772 | 2 | 0 | 38959.3772 | 2404 | 0 |  | 1856.5 | 1946.5 | 0.1221 | 0 | 146.7643 | 0 | 0.001221 | 0 | 1.4676 | 0 | 0.001221 | 1.4676 | 124619 | 3.7596 | 124618.9988
38959.3777 | 2 | 0 | 38959.3777 | 2218 | 0 |  | 1898 | 1988 | 0.1221 | 0 | 135.409 | 0 | 0.001221 | 0 | 1.3541 | 0 | 0.001221 | 1.3541 | 124619 | 12.4608 | 124618.9988
38959.3782 | 2 | 0 | 38959.3782 | 2409 | 0 |  | 1940.5 | 2030.5 | 0.1221 | 0 | 147.0696 | 0 | 0.001221 | 0 | 1.4707 | 0 | 0.001221 | 1.4707 | 124619 | 3.5442 | 124618.9988
38959.3787 | 3 | 0 | 38959.3787 | 2324 | 0 |  | 1982.5 | 2072.5 | 0.18315 | 0 | 141.8803 | 0 | 0.0018315 | 0 | 1.4188 | 0 | 0.0018315 | 1.4188 | 83046 | 7.3313 | 83045.9982
38959.3792 | 4 | 0 | 38959.3792 | 2118 | 0 |  | 2024 | 2114 | 0.2442 | 0 | 129.304 | 0 | 0.002442 | 0 | 1.293 | 0 | 0.002442 | 1.293 | 62259.5 | 17.7705 | 62259.4976
38959.3797 | 7 | 0 | 38959.3797 | 2275 | 0 |  | 2066.5 | 2156.5 | 0.42735 | 0 | 138.8889 | 0 | 0.0042735 | 0 | 1.3889 | 0 | 0.0042735 | 1.3889 | 35534 | 9.6431 | 35533.9957
38959.3801 | 19 | 0 | 38959.3802 | 2440 | 0 |  | 2108 | 2198 | 1.16 | 0 | 148.9621 | 0 | 0.0116 | 0 | 1.4896 | 0 | 0.0116 | 1.4896 | 13028.3158 | 2.2287 | 13028.3042
38959.3806 | 2020 | 0 | 38959.3806 | 2311 | 0 |  | 2150 | 2240 | 123.3211 | 0 | 141.0867 | 0 | 1.2332 | 0 | 1.4109 | 0 | 1.2332 | 1.4109 | 23.4842 | 7.9351 | 22.2509
38959.3811 | 2017 | 0 | 38959.3811 | 1910 | 0 |  | 2192 | 2282 | 123.138 | 0 | 116.6056 | 0 | 1.2314 | 0 | 1.1661 | 0 | 1.2314 | 1.1661 | 23.6678 | 30.5958 | 22.4364
38959.3816 | 2338 | 0 | 38959.3816 | 2342 | 0 |  | 2234 | 2324 | 142.735 | 0 | 142.9792 | 0 | 1.4274 | 0 | 1.4298 | 0 | 1.4274 | 1.4298 | 6.6886 | 6.5064 | 5.2613
38959.3821 | 1948 | 0 | 38959.3821 | 2326 | 0 |  | 2276.5 | 2366.5 | 118.9255 | 0 | 142.0024 | 0 | 1.1893 | 0 | 1.42 | 0 | 1.1893 | 1.42 | 28.0483 | 7.239 | 26.859
38959.3826 | 2039 | 0 | 38959.3826 | 2094 | 0 |  | 2318 | 2408 | 124.4811 | 0 | 127.8388 | 0 | 1.2448 | 0 | 1.2784 | 0 | 1.2448 | 1.2784 | 22.3335 | 19.1203 | 21.0887
38959.383 | 2073 | 0 | 38959.3831 | 2400 | 0 |  | 2360 | 2450 | 126.5568 | 0 | 146.5201 | 0 | 1.2656 | 0 | 1.4652 | 0 | 1.2656 | 1.4652 | 20.3271 | 3.9325 | 19.0615
38959.3835 | 2225 | 0 | 38959.3836 | 2312 | 0 |  | 2402 | 2492 | 135.8364 | 0 | 141.1477 | 0 | 1.3584 | 0 | 1.4115 | 0 | 1.3584 | 1.4115 | 12.107 | 7.8884 | 10.7486
38959.384 | 1925 | 0 | 38959.384 | 2053 | 0 |  | 2444 | 2534 | 117.5214 | 0 | 125.3358 | 0 | 1.1752 | 0 | 1.2534 | 0 | 1.1752 | 1.2534 | 29.5782 | 21.4993 | 28.403
38959.3845 | 1922 | 0 | 38959.3845 | 1931 | 0 |  | 2486 | 2576 | 117.3382 | 0 | 117.8877 | 0 | 1.1734 | 0 | 1.1789 | 0 | 1.1734 | 1.1789 | 29.7804 | 29.1756 | 28.6071
38959.385 | 1920 | 0 | 38959.385 | 2226 | 0 |  | 2528 | 2618 | 117.2161 | 0 | 135.8974 | 0 | 1.1722 | 0 | 1.359 | 0 | 1.1722 | 1.359 | 29.9156 | 12.0566 | 28.7435
38959.3855 | 2183 | 0 | 38959.3855 | 2450 | 0 |  | 2570 | 2660 | 133.2723 | 0 | 149.5726 | 0 | 1.3327 | 0 | 1.4957 | 0 | 1.3327 | 1.4957 | 14.2639 | 1.8114 | 12.9311
38959.386 | 2005 | 0 | 38959.386 | 2478 | 0 |  | 2612 | 2702 | 122.4054 | 0 | 151.2821 | 0 | 1.2241 | 0 | 1.5128 | 0 | 1.2241 | 1.5128 | 24.408 | 0.66102 | 23.1839
38959.3864 | 2460 | 0 | 38959.3865 | 2415 | 0 |  | 2654 | 2744 | 150.1832 | 0 | 147.4359 | 0 | 1.5018 | 0 | 1.4744 | 0 | 1.5018 | 1.4744 | 1.3976 | 3.287 | 0.10427
38959.3869 | 2181 | 0 | 38959.387 | 2099 | 0 |  | 2696 | 2786 | 133.1502 | 0 | 128.1441 | 0 | 1.3315 | 0 | 1.2814 | 0 | 1.3315 | 1.2814 | 14.3686 | 18.8366 | 13.0371
38959.3874 | 1936 | 0 | 38959.3874 | 2474 | 0 |  | 2738 | 2828 | 118.1929 | 0 | 151.0379 | 0 | 1.1819 | 0 | 1.5104 | 0 | 1.1819 | 1.5104 | 28.8419 | 0.82377 | 27.66
38959.3879 | 2065 | 0 | 38959.3879 | 2477 | 0 |  | 2780 | 2870 | 126.0684 | 0 | 151.221 | 0 | 1.2607 | 0 | 1.5122 | 0 | 1.2607 | 1.5122 | 20.7932 | 0.70166 | 19.5325
38959.3884 | 1939 | 0 | 38959.3884 | 2303 | 0 |  | 2822 | 2912 | 118.3761 | 0 | 140.5983 | 0 | 1.1838 | 0 | 1.406 | 0 | 1.1838 | 1.406 | 28.6426 | 8.31 | 27.4588
38959.3889 | 2263 | 0 | 38959.3889 | 2469 | 0 |  | 2864 | 2954 | 138.1563 | 0 | 150.7326 | 0 | 1.3816 | 0 | 1.5073 | 0 | 1.3816 | 1.5073 | 10.2245 | 1.0279 | 8.8429

## A1-C6
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 151.6105 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38959.3548 | 1 | 0 | 38959.3548 | 1 | 0 |  | -78.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3553 | 1 | 0 | 38959.3553 | 1 | 0 |  | -36.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3558 | 1 | 0 | 38959.3558 | 1 | 0 |  | 5.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3563 | 1 | 0 | 38959.3563 | 1 | 0 |  | 47.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3568 | 1 | 0 | 38959.3568 | 1 | 0 |  | 89.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3573 | 1 | 0 | 38959.3573 | 1 | 0 |  | 131.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3577 | 1 | 0 | 38959.3578 | 1 | 0 |  | 173.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3582 | 1 | 0 | 38959.3582 | 1 | 0 |  | 215.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3587 | 1 | 0 | 38959.3587 | 1 | 0 |  | 257.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3592 | 1 | 0 | 38959.3592 | 0 | 0 |  | 299.5 | 389.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248238 | 496576 | 248237.9994
38959.3597 | 1 | 0 | 38959.3597 | 1 | 0 |  | 341.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3602 | 1 | 0 | 38959.3602 | 1 | 0 |  | 383.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3607 | 1 | 0 | 38959.3607 | 1 | 0 |  | 425.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3611 | 1 | 0 | 38959.3612 | 1 | 0 |  | 467.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3616 | 1 | 0 | 38959.3616 | 1 | 0 |  | 509.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3621 | 1 | 0 | 38959.3621 | 1 | 0 |  | 551.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3626 | 1 | 0 | 38959.3626 | 1 | 0 |  | 593.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3631 | 1 | 0 | 38959.3631 | 1 | 0 |  | 635.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3636 | 1 | 0 | 38959.3636 | 1 | 0 |  | 677.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3641 | 1 | 0 | 38959.3641 | 1 | 0 |  | 719.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3645 | 1 | 0 | 38959.3646 | 1 | 0 |  | 761.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.365 | 1 | 0 | 38959.365 | 1 | 0 |  | 803.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3655 | 1 | 0 | 38959.3655 | 1 | 0 |  | 845.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.366 | 1 | 0 | 38959.366 | 1 | 0 |  | 887.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3665 | 1 | 0 | 38959.3665 | 1 | 0 |  | 929.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.367 | 1 | 0 | 38959.367 | 1 | 0 |  | 971.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3675 | 1 | 0 | 38959.3675 | 1 | 0 |  | 1013.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.368 | 1 | 0 | 38959.368 | 1 | 0 |  | 1055.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3684 | 1 | 0 | 38959.3684 | 1 | 0 |  | 1097.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3689 | 1 | 0 | 38959.3689 | 1 | 0 |  | 1139.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3694 | 2 | 0 | 38959.3694 | 1 | 0 |  | 1181.5 | 1271.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124069 | 248238 | 124068.9988
38959.3699 | 1 | 0 | 38959.3699 | 1 | 0 |  | 1223.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3704 | 1 | 0 | 38959.3704 | 1 | 0 |  | 1265.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3709 | 1 | 0 | 38959.3709 | 1 | 0 |  | 1307.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3714 | 1 | 0 | 38959.3714 | 1 | 0 |  | 1349.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3718 | 1 | 0 | 38959.3719 | 1 | 0 |  | 1391.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3723 | 1 | 0 | 38959.3723 | 1 | 0 |  | 1433.5 | 1523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3728 | 1 | 0 | 38959.3728 | 1 | 0 |  | 1475.5 | 1565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3733 | 1 | 0 | 38959.3733 | 1 | 0 |  | 1517.5 | 1607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3738 | 1 | 0 | 38959.3738 | 1 | 0 |  | 1559.5 | 1649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3743 | 1 | 0 | 38959.3743 | 1 | 0 |  | 1601.5 | 1691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
38959.3748 | 1 | 0 | 38959.3748 | 2 | 0 |  | 1643.5 | 1733.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248238 | 124069 | 248237.9994
38959.3752 | 2 | 0 | 38959.3753 | 1 | 0 |  | 1685.5 | 1775.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124069 | 248238 | 124068.9988
38959.3757 | 2 | 0 | 38959.3757 | 2 | 0 |  | 1727.5 | 1817.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124069 | 124069 | 124068.9988
38959.3762 | 2 | 0 | 38959.3762 | 2 | 0 |  | 1769.5 | 1859.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124069 | 124069 | 124068.9988
38959.3767 | 2 | 0 | 38959.3767 | 2 | 0 |  | 1811.5 | 1901.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124069 | 124069 | 124068.9988
38959.3772 | 2 | 0 | 38959.3772 | 2 | 0 |  | 1853.5 | 1943.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124069 | 124069 | 124068.9988
38959.3777 | 2 | 0 | 38959.3777 | 2 | 0 |  | 1895.5 | 1985.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124069 | 124069 | 124068.9988
38959.3782 | 2 | 0 | 38959.3782 | 71 | 0 |  | 1937.5 | 2027.5 | 0.1221 | 0 | 4.3346 | 0 | 0.001221 | 0 | 0.043346 | 0 | 0.001221 | 0.043346 | 124069 | 3397.7183 | 124068.9988
38959.3786 | 2 | 0 | 38959.3787 | 41 | 0 |  | 1979.5 | 2069.5 | 0.1221 | 0 | 2.5031 | 0 | 0.001221 | 0 | 0.025031 | 0 | 0.001221 | 0.025031 | 124069 | 5957.0244 | 124068.9988
38959.3791 | 4 | 0 | 38959.3791 | 487 | 0 |  | 2021.5 | 2111.5 | 0.2442 | 0 | 29.7314 | 0 | 0.002442 | 0 | 0.29731 | 0 | 0.002442 | 0.29731 | 61984.5 | 409.9343 | 61984.4976
38959.3796 | 5 | 0 | 38959.3796 | 1510 | 0 |  | 2063.5 | 2153.5 | 0.30525 | 0 | 92.1856 | 0 | 0.0030525 | 0 | 0.92186 | 0 | 0.0030525 | 0.92186 | 49567.6 | 64.4623 | 49567.5969
38959.3801 | 16 | 0 | 38959.3801 | 2094 | 0 |  | 2105.5 | 2195.5 | 0.9768 | 0 | 127.8388 | 0 | 0.009768 | 0 | 1.2784 | 0 | 0.009768 | 1.2784 | 15421.125 | 18.595 | 15421.1152
38959.3806 | 2427 | 0 | 38959.3806 | 1932 | 0 |  | 2147.5 | 2237.5 | 148.1685 | 0 | 117.9487 | 0 | 1.4817 | 0 | 1.1795 | 0 | 1.4817 | 1.1795 | 2.323 | 28.5393 | 0.84135
38959.3811 | 2130 | 0 | 38959.3811 | 2376 | 0 |  | 2189.5 | 2279.5 | 130.0366 | 0 | 145.0549 | 0 | 1.3004 | 0 | 1.4505 | 0 | 1.3004 | 1.4505 | 16.5906 | 4.5194 | 15.2902
38959.3816 | 1987 | 0 | 38959.3816 | 2419 | 0 |  | 2231.5 | 2321.5 | 121.3065 | 0 | 147.6801 | 0 | 1.2131 | 0 | 1.4768 | 0 | 1.2131 | 1.4768 | 24.9814 | 2.6614 | 23.7683
38959.382 | 2383 | 0 | 38959.3821 | 2112 | 0 |  | 2273.5 | 2363.5 | 145.4823 | 0 | 128.9377 | 0 | 1.4548 | 0 | 1.2894 | 0 | 1.4548 | 1.2894 | 4.2123 | 17.5843 | 2.7575
38959.3825 | 2467 | 0 | 38959.3825 | 2006 | 0 |  | 2315.5 | 2405.5 | 150.6105 | 0 | 122.4664 | 0 | 1.5061 | 0 | 1.2247 | 0 | 1.5061 | 1.2247 | 0.66396 | 23.7976 | 0.84214
38959.383 | 2045 | 0 | 38959.383 | 2083 | 0 |  | 2357.5 | 2447.5 | 124.8474 | 0 | 127.1673 | 0 | 1.2485 | 0 | 1.2717 | 0 | 1.2485 | 1.2717 | 21.4367 | 19.2213 | 20.1882
38959.3835 | 2466 | 0 | 38959.3835 | 2040 | 0 |  | 2399.5 | 2489.5 | 150.5495 | 0 | 124.5421 | 0 | 1.5055 | 0 | 1.2454 | 0 | 1.5055 | 1.2454 | 0.70479 | 21.7343 | 0.80071
38959.384 | 1952 | 0 | 38959.384 | 2327 | 0 |  | 2441.5 | 2531.5 | 119.1697 | 0 | 142.0635 | 0 | 1.1917 | 0 | 1.4206 | 0 | 1.1917 | 1.4206 | 27.2223 | 6.7202 | 26.0306
38959.3845 | 1918 | 0 | 38959.3845 | 2124 | 0 |  | 2483.5 | 2573.5 | 117.094 | 0 | 129.6703 | 0 | 1.1709 | 0 | 1.2967 | 0 | 1.1709 | 1.2967 | 29.4776 | 16.92 | 28.3066
38959.385 | 2005 | 0 | 38959.385 | 2297 | 0 |  | 2525.5 | 2615.5 | 122.4054 | 0 | 140.232 | 0 | 1.2241 | 0 | 1.4023 | 0 | 1.2241 | 1.4023 | 23.8594 | 8.1141 | 22.6353
38959.3855 | 2032 | 0 | 38959.3855 | 1952 | 0 |  | 2567.5 | 2657.5 | 124.0537 | 0 | 119.1697 | 0 | 1.2405 | 0 | 1.1917 | 0 | 1.2405 | 1.1917 | 22.2136 | 27.2223 | 20.973
38959.3859 | 2385 | 0 | 38959.3859 | 2214 | 0 |  | 2609.5 | 2699.5 | 145.6044 | 0 | 135.1648 | 0 | 1.456 | 0 | 1.3516 | 0 | 1.456 | 1.3516 | 4.1249 | 12.1671 | 2.6689
38959.3864 | 2181 | 0 | 38959.3864 | 2213 | 0 |  | 2651.5 | 2741.5 | 133.1502 | 0 | 135.1038 | 0 | 1.3315 | 0 | 1.351 | 0 | 1.3315 | 1.351 | 13.8643 | 12.2178 | 12.5328
38959.3869 | 2091 | 0 | 38959.3869 | 2389 | 0 |  | 2693.5 | 2783.5 | 127.6557 | 0 | 145.8486 | 0 | 1.2766 | 0 | 1.4585 | 0 | 1.2766 | 1.4585 | 18.7652 | 3.9506 | 17.4886
38959.3874 | 2260 | 0 | 38959.3874 | 2060 | 0 |  | 2735.5 | 2825.5 | 137.9731 | 0 | 125.7631 | 0 | 1.3797 | 0 | 1.2576 | 0 | 1.3797 | 1.2576 | 9.8841 | 20.5524 | 8.5043
38959.3879 | 2049 | 0 | 38959.3879 | 1947 | 0 |  | 2777.5 | 2867.5 | 125.0916 | 0 | 118.8645 | 0 | 1.2509 | 0 | 1.1886 | 0 | 1.2509 | 1.1886 | 21.1996 | 27.549 | 19.9487
38959.3884 | 2208 | 0 | 38959.3884 | 2464 | 0 |  | 2819.5 | 2909.5 | 134.7985 | 0 | 150.4274 | 0 | 1.348 | 0 | 1.5043 | 0 | 1.348 | 1.5043 | 12.4719 | 0.78653 | 11.1239
38959.3889 | 2323 | 0 | 38959.3889 | 2106 | 0 |  | 2861.5 | 2951.5 | 141.8193 | 0 | 128.5714 | 0 | 1.4182 | 0 | 1.2857 | 0 | 1.4182 | 1.2857 | 6.904 | 17.9193 | 5.4858

## A1-C5
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 151.7937 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38959.3548 | 1 | 0 | 38959.3548 | 1 | 0 |  | -81 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3553 | 1 | 0 | 38959.3553 | 1 | 0 |  | -39 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3558 | 1 | 1 | 38959.3558 | 1 | 0 |  | 3 | 93 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 617711374.44 | 248538 | 248338.0804
38959.3562 | 0 | 0 | 38959.3563 | 1 | 0 |  | 45 | 135 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497176 | 248538 | 497175.9997
38959.3567 | 1 | 1 | 38959.3568 | 1 | 0 |  | 87 | 177 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 617711374.44 | 248538 | 248338.0804
38959.3572 | 1 | 0 | 38959.3572 | 1 | 0 |  | 129 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3577 | 1 | 0 | 38959.3577 | 1 | 0 |  | 171 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3582 | 1 | 0 | 38959.3582 | 1 | 0 |  | 213 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3587 | 1 | 0 | 38959.3587 | 1 | 0 |  | 255 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3592 | 1 | 0 | 38959.3592 | 1 | 0 |  | 297 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3597 | 1 | 0 | 38959.3597 | 1 | 0 |  | 339 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3601 | 1 | 0 | 38959.3602 | 1 | 0 |  | 381 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3606 | 1 | 0 | 38959.3606 | 1 | 0 |  | 423 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3611 | 1 | 0 | 38959.3611 | 1 | 0 |  | 465 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3616 | 1 | 0 | 38959.3616 | 1 | 0 |  | 506.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3621 | 1 | 0 | 38959.3621 | 1 | 0 |  | 548.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3626 | 1 | 0 | 38959.3626 | 1 | 0 |  | 591 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3631 | 1 | 0 | 38959.3631 | 1 | 0 |  | 633 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3635 | 1 | 0 | 38959.3636 | 1 | 0 |  | 675 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.364 | 1 | 0 | 38959.3641 | 1 | 0 |  | 717 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3645 | 1 | 0 | 38959.3645 | 1 | 0 |  | 758.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.365 | 1 | 0 | 38959.365 | 1 | 0 |  | 800.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3655 | 1 | 0 | 38959.3655 | 1 | 0 |  | 842.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.366 | 1 | 0 | 38959.366 | 1 | 0 |  | 885 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3665 | 1 | 0 | 38959.3665 | 1 | 0 |  | 926.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3669 | 1 | 0 | 38959.367 | 1 | 0 |  | 968.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3674 | 1 | 0 | 38959.3674 | 1 | 0 |  | 1010.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3679 | 1 | 0 | 38959.3679 | 1 | 0 |  | 1053 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3684 | 1 | 0 | 38959.3684 | 1 | 0 |  | 1094.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3689 | 1 | 0 | 38959.3689 | 1 | 0 |  | 1136.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3694 | 1 | 0 | 38959.3694 | 1 | 0 |  | 1179 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3699 | 1 | 0 | 38959.3699 | 1 | 0 |  | 1220.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3703 | 1 | 0 | 38959.3704 | 1 | 0 |  | 1262.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3708 | 1 | 0 | 38959.3708 | 1 | 0 |  | 1304.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3713 | 1 | 0 | 38959.3713 | 1 | 0 |  | 1346.5 | 1436.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3718 | 1 | 0 | 38959.3718 | 1 | 0 |  | 1388.5 | 1478.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3723 | 1 | 0 | 38959.3723 | 1 | 0 |  | 1430.5 | 1520.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3728 | 1 | 0 | 38959.3728 | 1 | 0 |  | 1472.5 | 1562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3733 | 1 | 0 | 38959.3733 | 1 | 0 |  | 1514.5 | 1604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3737 | 1 | 0 | 38959.3738 | 1 | 0 |  | 1556.5 | 1646.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248538 | 248538 | 248537.9994
38959.3742 | 2 | 0 | 38959.3742 | 1 | 0 |  | 1598.5 | 1688.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124219 | 248538 | 124218.9988
38959.3747 | 2 | 0 | 38959.3747 | 2 | 0 |  | 1640.5 | 1730.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124219 | 124219 | 124218.9988
38959.3752 | 2 | 0 | 38959.3752 | 2 | 0 |  | 1682.5 | 1772.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124219 | 124219 | 124218.9988
38959.3757 | 2 | 0 | 38959.3757 | 243 | 0 |  | 1724.5 | 1814.5 | 0.1221 | 0 | 14.8352 | 0 | 0.001221 | 0 | 0.14835 | 0 | 0.001221 | 0.14835 | 124219 | 923.2016 | 124218.9988
38959.3762 | 2 | 0 | 38959.3762 | 2 | 0 |  | 1766.5 | 1856.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124219 | 124219 | 124218.9988
38959.3767 | 2 | 0 | 38959.3767 | 2 | 0 |  | 1808.5 | 1898.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124219 | 124219 | 124218.9988
38959.3772 | 2 | 0 | 38959.3772 | 5 | 0 |  | 1850.5 | 1940.5 | 0.1221 | 0 | 0.30525 | 0 | 0.001221 | 0 | 0.0030525 | 0 | 0.001221 | 0.0030525 | 124219 | 49627.6 | 124218.9988
38959.3776 | 3 | 0 | 38959.3777 | 2 | 1 |  | 1892.5 | 1982.5 | 0.18315 | 0 | 0.1221 | 0.06105 | 0.0018315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 82779.3333 | 248538 | 82779.3315
38959.3781 | 2 | 0 | 38959.3781 | 12 | 0 |  | 1934.5 | 2024.5 | 0.1221 | 0 | 0.7326 | 0 | 0.001221 | 0 | 0.007326 | 0 | 0.001221 | 0.007326 | 124219 | 20619.8333 | 124218.9988
38959.3786 | 3 | 0 | 38959.3786 | 34 | 0 |  | 1976.5 | 2066.5 | 0.18315 | 0 | 2.0757 | 0 | 0.0018315 | 0 | 0.020757 | 0 | 0.0018315 | 0.020757 | 82779.3333 | 7212.8824 | 82779.3315
38959.3791 | 4 | 0 | 38959.3791 | 442 | 0 |  | 2018.5 | 2108.5 | 0.2442 | 0 | 26.9841 | 0 | 0.002442 | 0 | 0.26984 | 0 | 0.002442 | 0.26984 | 62059.5 | 462.5294 | 62059.4976
38959.3796 | 6 | 0 | 38959.3796 | 67 | 0 |  | 2060.5 | 2150.5 | 0.3663 | 0 | 4.0904 | 0 | 0.003663 | 0 | 0.040904 | 0 | 0.003663 | 0.040904 | 41339.6667 | 3611.0149 | 41339.663
38959.3801 | 17 | 1 | 38959.3801 | 93 | 0 |  | 2102.5 | 2192.5 | 1.0379 | 0.06105 | 5.6777 | 0 | 0.010379 | 0.0006105 | 0.056777 | 0 | 0.009768 | 0.056777 | 15471.1979 | 2573.5269 | 237605.3268
38959.3806 | 2368 | 1 | 38959.3806 | 15 | 0 |  | 2144.5 | 2234.5 | 144.5665 | 0.06105 | 0.91575 | 0 | 1.4457 | 0.0006105 | 0.0091575 | 0 | 1.4451 | 0.0091575 | 5.0013 | 16475.8667 | 11667.1862
38959.381 | 2445 | 1 | 38959.3811 | 1446 | 0 |  | 2186.5 | 2276.5 | 149.2674 | 0.06105 | 88.2784 | 0 | 1.4927 | 0.0006105 | 0.88278 | 0 | 1.4921 | 0.88278 | 1.6941 | 71.9488 | 1689.6269
38959.3815 | 2177 | 1 | 38959.3815 | 159 | 0 |  | 2228.5 | 2318.5 | 132.906 | 0.06105 | 9.707 | 0 | 1.3291 | 0.0006105 | 0.09707 | 0 | 1.3284 | 0.09707 | 14.2183 | 1463.761 | 28865.9595
38959.382 | 2417 | 1 | 38959.382 | 1661 | 0 |  | 2270.5 | 2360.5 | 147.558 | 0.06105 | 101.4042 | 0 | 1.4756 | 0.0006105 | 1.014 | 0 | 1.475 | 1.014 | 2.8741 | 49.6918 | 2269.946
38959.3825 | 2095 | 1 | 38959.3825 | 3 | 0 |  | 2312.5 | 2402.5 | 127.8999 | 0.06105 | 0.18315 | 0 | 1.279 | 0.0006105 | 0.0018315 | 0 | 1.2784 | 0.0018315 | 18.6906 | 82779.3333 | 38990.8978
38959.383 | 2348 | 1 | 38959.383 | 1015 | 0 |  | 2354.5 | 2444.5 | 143.3455 | 0.06105 | 61.9658 | 0 | 1.4335 | 0.0006105 | 0.61966 | 0 | 1.4328 | 0.61966 | 5.8978 | 144.9635 | 8129.8186
38959.3835 | 2370 | 1 | 38959.3835 | 4 | 0 |  | 2396.5 | 2486.5 | 144.6886 | 0.06105 | 0.2442 | 0 | 1.4469 | 0.0006105 | 0.002442 | 0 | 1.4463 | 0.002442 | 4.9126 | 62059.5 | 11519.4381
38959.384 | 2318 | 1 | 38959.384 | 4 | 0 |  | 2438.5 | 2528.5 | 141.514 | 0.06105 | 0.2442 | 0 | 1.4151 | 0.0006105 | 0.002442 | 0 | 1.4145 | 0.002442 | 7.2672 | 62059.5 | 16711.0725
38959.3844 | 2159 | 1 | 38959.3845 | 3 | 0 |  | 2480.5 | 2570.5 | 131.8071 | 0.06105 | 0.18315 | 0 | 1.3181 | 0.0006105 | 0.0018315 | 0 | 1.3175 | 0.0018315 | 15.1705 | 82779.3333 | 32598.6199
38959.3849 | 2470 | 1 | 38959.3849 | 4 | 0 |  | 2522.5 | 2612.5 | 150.7937 | 0.06105 | 0.2442 | 0 | 1.5079 | 0.0006105 | 0.002442 | 0 | 1.5073 | 0.002442 | 0.66343 | 62059.5 | 1535.5257
38959.3854 | 1996 | 1 | 38959.3854 | 3 | 0 |  | 2564.5 | 2654.5 | 121.8559 | 0.06105 | 0.18315 | 0 | 1.2186 | 0.0006105 | 0.0018315 | 0 | 1.2179 | 0.0018315 | 24.5805 | 82779.3333 | 48878.9527
38959.3859 | 2433 | 1 | 38959.3859 | 2 | 0 |  | 2606.5 | 2696.5 | 148.5348 | 0.06105 | 0.1221 | 0 | 1.4853 | 0.0006105 | 0.001221 | 0 | 1.4847 | 0.001221 | 2.1949 | 124219 | 5233.7866
38959.3864 | 2210 | 1 | 38959.3864 | 3 | 0 |  | 2648.5 | 2738.5 | 134.9206 | 0.06105 | 0.18315 | 0 | 1.3492 | 0.0006105 | 0.0018315 | 0 | 1.3486 | 0.0018315 | 12.5116 | 82779.3333 | 27504.7734
38959.3869 | 2218 | 1 | 38959.3869 | 2 | 0 |  | 2690.5 | 2780.5 | 135.409 | 0.06105 | 0.1221 | 0 | 1.3541 | 0.0006105 | 0.001221 | 0 | 1.3535 | 0.001221 | 12.1056 | 124219 | 26716.4924
38959.3874 | 2233 | 1 | 38959.3874 | 2 | 0 |  | 2732.5 | 2822.5 | 136.3248 | 0.06105 | 0.1221 | 0 | 1.3632 | 0.0006105 | 0.001221 | 0 | 1.3626 | 0.001221 | 11.3522 | 124219 | 25217.699
38959.3878 | 2142 | 1 | 38959.3879 | 2 | 0 |  | 2774.5 | 2864.5 | 130.7692 | 0.06105 | 0.1221 | 0 | 1.3077 | 0.0006105 | 0.001221 | 0 | 1.3071 | 0.001221 | 16.085 | 124219 | 34310.3791
38959.3883 | 2434 | 1 | 38959.3883 | 2 | 0 |  | 2816.5 | 2906.5 | 148.5958 | 0.06105 | 0.1221 | 0 | 1.486 | 0.0006105 | 0.001221 | 0 | 1.4853 | 0.001221 | 2.1529 | 124219 | 5133.8671
38959.3888 | 1921 | 1 | 38959.3888 | 2 | 0 |  | 2858.5 | 2948.5 | 117.2772 | 0.06105 | 0.1221 | 0 | 1.1728 | 0.0006105 | 0.001221 | 0 | 1.1722 | 0.001221 | 29.4469 | 124219 | 56392.6023

## A1-B4
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 154.4188 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38959.3548 | 1 | 0 | 38959.3548 | 1 | 0 |  | -84 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3552 | 1 | 0 | 38959.3553 | 1 | 0 |  | -42 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3557 | 1 | 0 | 38959.3558 | 1 | 0 |  | -3.3528e-07 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3562 | 1 | 0 | 38959.3562 | 1 | 0 |  | 42 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3567 | 1 | 0 | 38959.3567 | 1 | 0 |  | 84 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3572 | 1 | 0 | 38959.3572 | 1 | 0 |  | 126 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3577 | 1 | 0 | 38959.3577 | 1 | 0 |  | 168 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3582 | 1 | 0 | 38959.3582 | 1 | 0 |  | 210 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3586 | 1 | 0 | 38959.3587 | 1 | 0 |  | 252 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3591 | 1 | 0 | 38959.3592 | 1 | 0 |  | 294 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3596 | 1 | 1 | 38959.3596 | 1 | 0 |  | 336 | 426 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 639270542.44 | 252838 | 252638.0791
38959.3601 | 1 | 0 | 38959.3601 | 1 | 0 |  | 378 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3606 | 1 | 0 | 38959.3606 | 1 | 0 |  | 420 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3611 | 1 | 0 | 38959.3611 | 1 | 0 |  | 462 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3616 | 1 | 0 | 38959.3616 | 1 | 0 |  | 504 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.362 | 1 | 0 | 38959.3621 | 1 | 0 |  | 546 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3625 | 1 | 0 | 38959.3626 | 1 | 0 |  | 588 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.363 | 1 | 0 | 38959.363 | 1 | 0 |  | 630 | 720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3635 | 1 | 0 | 38959.3635 | 1 | 0 |  | 672 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.364 | 1 | 0 | 38959.364 | 1 | 0 |  | 714 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3645 | 1 | 0 | 38959.3645 | 1 | 0 |  | 756 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.365 | 1 | 0 | 38959.365 | 1 | 0 |  | 798 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3655 | 1 | 0 | 38959.3655 | 1 | 0 |  | 840 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3659 | 1 | 0 | 38959.366 | 1 | 0 |  | 882 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3664 | 1 | 0 | 38959.3664 | 1 | 0 |  | 924 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3669 | 1 | 0 | 38959.3669 | 1 | 0 |  | 966 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3674 | 1 | 0 | 38959.3674 | 1 | 0 |  | 1008 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3679 | 1 | 0 | 38959.3679 | 1 | 0 |  | 1050 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3684 | 1 | 0 | 38959.3684 | 1 | 0 |  | 1092 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3689 | 1 | 0 | 38959.3689 | 1 | 0 |  | 1134 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3693 | 1 | 0 | 38959.3694 | 1 | 0 |  | 1176 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3698 | 1 | 0 | 38959.3698 | 1 | 0 |  | 1218 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3703 | 1 | 0 | 38959.3703 | 1 | 0 |  | 1260 | 1350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3708 | 1 | 0 | 38959.3708 | 1 | 0 |  | 1302 | 1392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3713 | 1 | 0 | 38959.3713 | 1 | 0 |  | 1344 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3718 | 1 | 0 | 38959.3718 | 1 | 0 |  | 1386 | 1476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3723 | 1 | 0 | 38959.3723 | 1 | 0 |  | 1428 | 1518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3727 | 1 | 0 | 38959.3728 | 1 | 0 |  | 1470 | 1560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3732 | 1 | 0 | 38959.3733 | 1 | 0 |  | 1512 | 1602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252838 | 252838 | 252837.9994
38959.3737 | 1 | 0 | 38959.3737 | 398 | 0 |  | 1554 | 1644 | 0.06105 | 0 | 24.2979 | 0 | 0.0006105 | 0 | 0.24298 | 0 | 0.0006105 | 0.24298 | 252838 | 535.5226 | 252837.9994
38959.3742 | 1 | 0 | 38959.3742 | 1921 | 0 |  | 1596 | 1686 | 0.06105 | 0 | 117.2772 | 0 | 0.0006105 | 0 | 1.1728 | 0 | 0.0006105 | 1.1728 | 252838 | 31.67 | 252837.9994
38959.3747 | 2 | 0 | 38959.3747 | 2343 | 0 |  | 1638 | 1728 | 0.1221 | 0 | 143.0403 | 0 | 0.001221 | 0 | 1.4304 | 0 | 0.001221 | 1.4304 | 126369 | 7.9548 | 126368.9988
38959.3752 | 2 | 0 | 38959.3752 | 2289 | 0 |  | 1680 | 1770 | 0.1221 | 0 | 139.7436 | 0 | 0.001221 | 0 | 1.3974 | 0 | 0.001221 | 1.3974 | 126369 | 10.5015 | 126368.9988
38959.3757 | 2 | 0 | 38959.3757 | 2369 | 0 |  | 1722 | 1812 | 0.1221 | 0 | 144.6276 | 0 | 0.001221 | 0 | 1.4463 | 0 | 0.001221 | 1.4463 | 126369 | 6.7699 | 126368.9988
38959.3761 | 3 | 0 | 38959.3762 | 1966 | 0 |  | 1764 | 1854 | 0.18315 | 0 | 120.0244 | 0 | 0.0018315 | 0 | 1.2002 | 0 | 0.0018315 | 1.2002 | 84212.6667 | 28.6562 | 84212.6648
38959.3766 | 2 | 0 | 38959.3767 | 2110 | 0 |  | 1806 | 1896 | 0.1221 | 0 | 128.8156 | 0 | 0.001221 | 0 | 1.2882 | 0 | 0.001221 | 1.2882 | 126369 | 19.8758 | 126368.9988
38959.3771 | 2 | 0 | 38959.3771 | 2491 | 0 |  | 1847.5 | 1937.5 | 0.1221 | 0 | 152.0757 | 0 | 0.001221 | 0 | 1.5208 | 0 | 0.001221 | 1.5208 | 126369 | 1.5407 | 126368.9988
38959.3776 | 2 | 0 | 38959.3776 | 1978 | 0 |  | 1890 | 1980 | 0.1221 | 0 | 120.757 | 0 | 0.001221 | 0 | 1.2076 | 0 | 0.001221 | 1.2076 | 126369 | 27.8756 | 126368.9988
38959.3781 | 2 | 0 | 38959.3781 | 1987 | 0 |  | 1931.5 | 2021.5 | 0.1221 | 0 | 121.3065 | 0 | 0.001221 | 0 | 1.2131 | 0 | 0.001221 | 1.2131 | 126369 | 27.2964 | 126368.9988
38959.3786 | 3 | 0 | 38959.3786 | 2194 | 0 |  | 1974 | 2064 | 0.18315 | 0 | 133.9438 | 0 | 0.0018315 | 0 | 1.3394 | 0 | 0.0018315 | 1.3394 | 84212.6667 | 15.2862 | 84212.6648
38959.3791 | 4 | 0 | 38959.3791 | 1982 | 0 |  | 2015.5 | 2105.5 | 0.2442 | 0 | 121.0012 | 0 | 0.002442 | 0 | 1.21 | 0 | 0.002442 | 1.21 | 63134.5 | 27.6176 | 63134.4976
38959.3795 | 5 | 0 | 38959.3796 | 2003 | 0 |  | 2058 | 2148 | 0.30525 | 0 | 122.2833 | 0 | 0.0030525 | 0 | 1.2228 | 0 | 0.0030525 | 1.2228 | 50487.6 | 26.2796 | 50487.5969
38959.38 | 15 | 0 | 38959.38 | 2481 | 0 |  | 2099.5 | 2189.5 | 0.91575 | 0 | 151.4652 | 0 | 0.0091575 | 0 | 1.5147 | 0 | 0.0091575 | 1.5147 | 16762.5333 | 1.95 | 16762.5242
38959.3805 | 2017 | 0 | 38959.3805 | 2181 | 0 |  | 2141.5 | 2231.5 | 123.138 | 0 | 133.1502 | 0 | 1.2314 | 0 | 1.3315 | 0 | 1.2314 | 1.3315 | 25.4031 | 15.9734 | 24.1717
38959.381 | 2380 | 0 | 38959.381 | 2385 | 0 |  | 2183.5 | 2273.5 | 145.2991 | 0 | 145.6044 | 0 | 1.453 | 0 | 1.456 | 0 | 1.453 | 1.456 | 6.2765 | 6.0537 | 4.8235
38959.3815 | 2049 | 0 | 38959.3815 | 1943 | 0 |  | 2225.5 | 2315.5 | 125.0916 | 0 | 118.6203 | 0 | 1.2509 | 0 | 1.1862 | 0 | 1.2509 | 1.1862 | 23.4446 | 30.1791 | 22.1937
38959.382 | 2025 | 0 | 38959.382 | 2018 | 0 |  | 2267.5 | 2357.5 | 123.6264 | 0 | 123.199 | 0 | 1.2363 | 0 | 1.232 | 0 | 1.2363 | 1.232 | 24.9077 | 25.3409 | 23.6714
38959.3825 | 2313 | 0 | 38959.3825 | 2510 | 0 |  | 2309.5 | 2399.5 | 141.2088 | 0 | 153.2357 | 0 | 1.4121 | 0 | 1.5324 | 0 | 1.4121 | 1.5324 | 9.355 | 0.77211 | 7.9429
38959.383 | 2470 | 0 | 38959.383 | 2220 | 0 |  | 2351.5 | 2441.5 | 150.7937 | 0 | 135.5311 | 0 | 1.5079 | 0 | 1.3553 | 0 | 1.5079 | 1.3553 | 2.404 | 13.936 | 0.89611
38959.3834 | 2096 | 0 | 38959.3834 | 2169 | 0 |  | 2393.5 | 2483.5 | 127.9609 | 0 | 132.4176 | 0 | 1.2796 | 0 | 1.3242 | 0 | 1.2796 | 1.3242 | 20.6765 | 16.615 | 19.3969
38959.3839 | 2275 | 0 | 38959.3839 | 2446 | 0 |  | 2435.5 | 2525.5 | 138.8889 | 0 | 149.3284 | 0 | 1.3889 | 0 | 1.4933 | 0 | 1.3889 | 1.4933 | 11.1815 | 3.4088 | 9.7926
38959.3844 | 2090 | 0 | 38959.3844 | 2356 | 0 |  | 2477.5 | 2567.5 | 127.5946 | 0 | 143.8339 | 0 | 1.2759 | 0 | 1.4383 | 0 | 1.2759 | 1.4383 | 21.023 | 7.3591 | 19.747
38959.3849 | 1926 | 0 | 38959.3849 | 2418 | 0 |  | 2519.5 | 2609.5 | 117.5824 | 0 | 147.619 | 0 | 1.1758 | 0 | 1.4762 | 0 | 1.1758 | 1.4762 | 31.3281 | 4.6063 | 30.1523
38959.3854 | 1945 | 0 | 38959.3854 | 2096 | 0 |  | 2561.5 | 2651.5 | 118.7424 | 0 | 127.9609 | 0 | 1.1874 | 0 | 1.2796 | 0 | 1.1874 | 1.2796 | 30.0452 | 20.6765 | 28.8578
38959.3859 | 2309 | 0 | 38959.3859 | 2513 | 0 |  | 2603.5 | 2693.5 | 140.9646 | 0 | 153.4188 | 0 | 1.4096 | 0 | 1.5342 | 0 | 1.4096 | 1.5342 | 9.5444 | 0.65181 | 8.1347
38959.3864 | 2224 | 0 | 38959.3864 | 2318 | 0 |  | 2645.5 | 2735.5 | 135.7753 | 0 | 141.514 | 0 | 1.3578 | 0 | 1.4151 | 0 | 1.3578 | 1.4151 | 13.7311 | 9.1191 | 12.3734
38959.3868 | 2032 | 0 | 38959.3869 | 1980 | 0 |  | 2687.5 | 2777.5 | 124.0537 | 0 | 120.8791 | 0 | 1.2405 | 0 | 1.2088 | 0 | 1.2405 | 1.2088 | 24.4774 | 27.7465 | 23.2368
38959.3873 | 2288 | 0 | 38959.3873 | 2034 | 0 |  | 2729.5 | 2819.5 | 139.6825 | 0 | 124.1758 | 0 | 1.3968 | 0 | 1.2418 | 0 | 1.3968 | 1.2418 | 10.5498 | 24.355 | 9.153
38959.3878 | 2130 | 0 | 38959.3878 | 2452 | 0 |  | 2771.5 | 2861.5 | 130.0366 | 0 | 149.6947 | 0 | 1.3004 | 0 | 1.4969 | 0 | 1.3004 | 1.4969 | 18.7502 | 3.1558 | 17.4499
38959.3883 | 2178 | 0 | 38959.3883 | 2428 | 0 |  | 2813.5 | 2903.5 | 132.967 | 0 | 148.2295 | 0 | 1.3297 | 0 | 1.4823 | 0 | 1.3297 | 1.4823 | 16.1331 | 4.1755 | 14.8035
38959.3888 | 2176 | 0 | 38959.3888 | 2262 | 0 |  | 2855.5 | 2945.5 | 132.8449 | 0 | 138.0952 | 0 | 1.3284 | 0 | 1.381 | 0 | 1.3284 | 1.381 | 16.2399 | 11.8205 | 14.9114

## A1-B3
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 151.7326 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38959.3547 | 1 | 0 | 38959.3547 | 1 | 0 |  | -86.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3552 | 1 | 0 | 38959.3552 | 1 | 0 |  | -44.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3557 | 1 | 0 | 38959.3557 | 1 | 0 |  | -2.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3562 | 1 | 0 | 38959.3562 | 1 | 0 |  | 39.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3567 | 1 | 0 | 38959.3567 | 1 | 0 |  | 81.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3572 | 1 | 0 | 38959.3572 | 1 | 0 |  | 123.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3577 | 1 | 0 | 38959.3577 | 1 | 0 |  | 165.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3581 | 1 | 0 | 38959.3581 | 1 | 0 |  | 207.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3586 | 1 | 0 | 38959.3586 | 1 | 0 |  | 249.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3591 | 1 | 0 | 38959.3591 | 1 | 0 |  | 291.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3596 | 1 | 0 | 38959.3596 | 1 | 0 |  | 333.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3601 | 1 | 0 | 38959.3601 | 1 | 0 |  | 375.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3606 | 1 | 0 | 38959.3606 | 1 | 0 |  | 417 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3611 | 1 | 0 | 38959.3611 | 1 | 0 |  | 459.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3615 | 1 | 0 | 38959.3616 | 1 | 0 |  | 501 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.362 | 1 | 0 | 38959.362 | 1 | 0 |  | 543.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3625 | 1 | 0 | 38959.3625 | 1 | 0 |  | 585 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.363 | 1 | 0 | 38959.363 | 1 | 0 |  | 627.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3635 | 1 | 0 | 38959.3635 | 1 | 0 |  | 669.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.364 | 1 | 0 | 38959.364 | 1 | 0 |  | 711 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3644 | 1 | 0 | 38959.3645 | 1 | 0 |  | 753 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3649 | 1 | 0 | 38959.365 | 1 | 0 |  | 795.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3654 | 1 | 0 | 38959.3654 | 1 | 0 |  | 837 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3659 | 1 | 0 | 38959.3659 | 1 | 0 |  | 879 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3664 | 1 | 0 | 38959.3664 | 1 | 0 |  | 921 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3669 | 1 | 0 | 38959.3669 | 1 | 0 |  | 963.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3674 | 1 | 0 | 38959.3674 | 1 | 0 |  | 1005 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3678 | 1 | 0 | 38959.3679 | 1 | 0 |  | 1047 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3683 | 1 | 0 | 38959.3684 | 1 | 0 |  | 1089 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3688 | 1 | 0 | 38959.3688 | 1 | 0 |  | 1131 | 1221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3693 | 1 | 0 | 38959.3693 | 1 | 0 |  | 1173 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3698 | 1 | 0 | 38959.3698 | 1 | 0 |  | 1215 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3703 | 1 | 0 | 38959.3703 | 1 | 0 |  | 1257 | 1347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3708 | 1 | 0 | 38959.3708 | 1 | 0 |  | 1299 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3712 | 1 | 0 | 38959.3713 | 1 | 0 |  | 1341 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3717 | 1 | 0 | 38959.3718 | 44 | 0 |  | 1383 | 1473 | 0.06105 | 0 | 2.6862 | 0 | 0.0006105 | 0 | 0.026862 | 0 | 0.0006105 | 0.026862 | 248438 | 5548.5909 | 248437.9994
38959.3722 | 1 | 0 | 38959.3722 | 369 | 0 |  | 1425 | 1515 | 0.06105 | 0 | 22.5275 | 0 | 0.0006105 | 0 | 0.22527 | 0 | 0.0006105 | 0.22527 | 248438 | 573.5447 | 248437.9994
38959.3727 | 1 | 0 | 38959.3727 | 2 | 0 |  | 1467 | 1557 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248438 | 124169 | 248437.9994
38959.3732 | 1 | 0 | 38959.3732 | 31 | 0 |  | 1509 | 1599 | 0.06105 | 0 | 1.8926 | 0 | 0.0006105 | 0 | 0.018926 | 0 | 0.0006105 | 0.018926 | 248438 | 7917.3548 | 248437.9994
38959.3737 | 1 | 0 | 38959.3737 | 1 | 0 |  | 1551 | 1641 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.3742 | 1 | 0 | 38959.3742 | 816 | 0 |  | 1593 | 1683 | 0.06105 | 0 | 49.8168 | 0 | 0.0006105 | 0 | 0.49817 | 0 | 0.0006105 | 0.49817 | 248438 | 204.5809 | 248437.9994
38959.3747 | 1 | 0 | 38959.3747 | 395 | 0 |  | 1635 | 1725 | 0.06105 | 0 | 24.1148 | 0 | 0.0006105 | 0 | 0.24115 | 0 | 0.0006105 | 0.24115 | 248438 | 529.2101 | 248437.9994
38959.3751 | 2 | 2 | 38959.3752 | 2040 | 1 |  | 1677 | 1767 | 0.1221 | 0.1221 | 124.5421 | 0.06105 | 0.001221 | 0.001221 | 1.2454 | 0.0006105 | 0 | 1.2448 | 27122.2605 | 21.843 | 22242.0762
38959.3756 | 2 | 2 | 38959.3756 | 2029 | 1 |  | 1719 | 1809 | 0.1221 | 0.1221 | 123.8706 | 0.06105 | 0.001221 | 0.001221 | 1.2387 | 0.0006105 | 0 | 1.2381 | 27942.8739 | 22.5039 | 22791.4122
38959.3761 | 2 | 1 | 38959.3761 | 1979 | 1 |  | 1761 | 1851 | 0.1221 | 0.06105 | 120.8181 | 0.06105 | 0.001221 | 0.0006105 | 1.2082 | 0.0006105 | 0.0006105 | 1.2076 | 85452.2883 | 52.4615 | 85417.8786
38959.3766 | 2 | 2 | 38959.3766 | 2321 | 1 |  | 1803 | 1893 | 0.1221 | 0.1221 | 141.6972 | 0.06105 | 0.001221 | 0.001221 | 1.417 | 0.0006105 | 0 | 1.4164 | 8797.7587 | 7.0853 | 8209.0376
38959.3771 | 2 | 2 | 38959.3771 | 2399 | 1 |  | 1845 | 1935 | 0.1221 | 0.1221 | 146.4591 | 0.06105 | 0.001221 | 0.001221 | 1.4646 | 0.0006105 | 0 | 1.464 | 4472.7349 | 3.6021 | 4313.7458
38959.3776 | 2 | 2 | 38959.3776 | 2316 | 1 |  | 1887 | 1977 | 0.1221 | 0.1221 | 141.3919 | 0.06105 | 0.001221 | 0.001221 | 1.4139 | 0.0006105 | 0 | 1.4133 | 9084.9439 | 7.3166 | 8458.7358
38959.3781 | 2 | 2 | 38959.3781 | 2045 | 0 |  | 1929 | 2019 | 0.1221 | 0.1221 | 124.8474 | 0 | 0.001221 | 0.001221 | 1.2485 | 0 | 0 | 1.2485 | 26739.1414 | 21.5345 | 21983.5624
38959.3785 | 3 | 2 | 38959.3786 | 2391 | 1 |  | 1971 | 2061 | 0.18315 | 0.1221 | 145.9707 | 0.06105 | 0.0018315 | 0.001221 | 1.4597 | 0.0006105 | 0.0006105 | 1.4591 | 5000.0859 | 4.1113 | 4897.4122
38959.379 | 3 | 2 | 38959.3791 | 2406 | 1 |  | 2013 | 2103 | 0.18315 | 0.1221 | 146.8864 | 0.06105 | 0.0018315 | 0.001221 | 1.4689 | 0.0006105 | 0.0006105 | 1.4683 | 4165.4017 | 3.4132 | 4093.3596
38959.3795 | 5 | 1 | 38959.3795 | 1976 | 1 |  | 2055 | 2145 | 0.30525 | 0.06105 | 120.6349 | 0.06105 | 0.0030525 | 0.0006105 | 1.2063 | 0.0006105 | 0.002442 | 1.2057 | 2020881.261 | 25.7914 | 50835.4845
38959.38 | 12 | 1 | 38959.38 | 2068 | 1 |  | 2097 | 2187 | 0.7326 | 0.06105 | 126.2515 | 0.06105 | 0.007326 | 0.0006105 | 1.2625 | 0.0006105 | 0.0067155 | 1.2619 | 40897.9686 | 20.1926 | 41536.4389
38959.3805 | 1886 | 1 | 38959.3805 | 1906 | 0 |  | 2139 | 2229 | 115.1404 | 0.06105 | 116.3614 | 0 | 1.1514 | 0.0006105 | 1.1636 | 0 | 1.1508 | 1.1636 | 31.8529 | 30.3977 | 13949.1508
38959.381 | 2013 | 1 | 38959.381 | 1974 | 0 |  | 2181 | 2271 | 122.8938 | 0.06105 | 120.5128 | 0 | 1.2289 | 0.0006105 | 1.2051 | 0 | 1.2283 | 1.2051 | 23.5233 | 25.9058 | 9698.8913
38959.3815 | 2060 | 1 | 38959.3815 | 2311 | 0 |  | 2223 | 2313 | 125.7631 | 0.06105 | 141.0867 | 0 | 1.2576 | 0.0006105 | 1.4109 | 0 | 1.257 | 1.4109 | 20.7934 | 7.5457 | 2977.5481
38959.3819 | 2204 | 1 | 38959.382 | 2407 | 0 |  | 2265 | 2355 | 134.5543 | 0.06105 | 146.9475 | 0 | 1.3455 | 0.0006105 | 1.4695 | 0 | 1.3449 | 1.4695 | 12.9531 | 3.2563 | 884.2183
38959.3824 | 2341 | 1 | 38959.3825 | 2469 | 0 |  | 2307 | 2397 | 142.9182 | 0.06105 | 150.7326 | 0 | 1.4292 | 0.0006105 | 1.5073 | 0 | 1.4286 | 1.5073 | 6.5949 | 0.66343 | 94.4952
38959.3829 | 2359 | 1 | 38959.3829 | 2389 | 0 |  | 2349 | 2439 | 144.0171 | 0.06105 | 145.8486 | 0 | 1.4402 | 0.0006105 | 1.4585 | 0 | 1.4396 | 1.4585 | 5.4166 | 4.0343 | 486.2083
38959.3834 | 1992 | 1 | 38959.3834 | 2159 | 0 |  | 2391 | 2481 | 121.6117 | 0.06105 | 131.8071 | 0 | 1.2161 | 0.0006105 | 1.3181 | 0 | 1.2155 | 1.3181 | 24.8631 | 15.1172 | 6465.9321
38959.3839 | 2168 | 1 | 38959.3839 | 1923 | 0 |  | 2433 | 2523 | 132.3565 | 0.06105 | 117.3993 | 0 | 1.3236 | 0.0006105 | 1.174 | 0 | 1.323 | 1.174 | 14.6692 | 29.2449 | 7158.8966
38959.3844 | 2114 | 1 | 38959.3844 | 2268 | 0 |  | 2475 | 2565 | 129.0598 | 0.06105 | 138.4615 | 0 | 1.2906 | 0.0006105 | 1.3846 | 0 | 1.29 | 1.3846 | 17.6632 | 9.5847 | 3239.4726
38959.3849 | 2105 | 1 | 38959.3849 | 2008 | 0 |  | 2517 | 2607 | 128.5104 | 0.06105 | 122.5885 | 0 | 1.2851 | 0.0006105 | 1.2259 | 0 | 1.2845 | 1.2259 | 18.1151 | 23.7739 | 7286.9511
38959.3853 | 2097 | 1 | 38959.3854 | 2464 | 0 |  | 2559 | 2649 | 128.022 | 0.06105 | 150.4274 | 0 | 1.2802 | 0.0006105 | 1.5043 | 0 | 1.2796 | 1.5043 | 19.6077 | 0.86769 | 333.2361
38959.3858 | 2278 | 1 | 38959.3859 | 2385 | 0 |  | 2601 | 2691 | 139.072 | 0.06105 | 145.6044 | 0 | 1.3907 | 0.0006105 | 1.456 | 0 | 1.3901 | 1.456 | 9.2036 | 4.2088 | 833.5315
38959.3863 | 2188 | 1 | 38959.3863 | 1955 | 0 |  | 2643 | 2733 | 133.5775 | 0.06105 | 119.3529 | 0 | 1.3358 | 0.0006105 | 1.1935 | 0 | 1.3352 | 1.1935 | 13.6206 | 27.1294 | 6324.7481
38959.3868 | 2246 | 1 | 38959.3868 | 2459 | 0 |  | 2685 | 2775 | 137.1184 | 0.06105 | 150.1221 | 0 | 1.3712 | 0.0006105 | 1.5012 | 0 | 1.3706 | 1.5012 | 11.1247 | 1.0728 | 253.0182
38959.3873 | 2062 | 1 | 38959.3873 | 1958 | 0 |  | 2727 | 2817 | 125.8852 | 0.06105 | 119.536 | 0 | 1.2589 | 0.0006105 | 1.1954 | 0 | 1.2582 | 1.1954 | 20.5795 | 26.9346 | 8962.6039
38959.3878 | 2351 | 1 | 38959.3878 | 2020 | 0 |  | 2769 | 2859 | 143.5287 | 0.06105 | 123.3211 | 0 | 1.4353 | 0.0006105 | 1.2332 | 0 | 1.4347 | 1.2332 | 5.7289 | 23.0386 | 2497.5008
38959.3883 | 2168 | 1 | 38959.3883 | 2417 | 0 |  | 2811 | 2901 | 132.3565 | 0.06105 | 147.558 | 0 | 1.3236 | 0.0006105 | 1.4756 | 0 | 1.323 | 1.4756 | 14.8889 | 2.8291 | 870.453
38959.3887 | 1920 | 1 | 38959.3888 | 2366 | 0 |  | 2853 | 2943 | 117.2161 | 0.06105 | 144.4444 | 0 | 1.1722 | 0.0006105 | 1.4444 | 0 | 1.1716 | 1.4444 | 29.7697 | 5.0456 | 2710.8806

## A1-A2
Penlight Test 37 |  |  | 2006-08-30 | 8:32 |  |  | Vs = |  | 152.8315 |  | R = | 100
XLPE & PE | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38959.3547 | 1 | 0 | 38959.3547 | 1 | 0 |  | -89.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3552 | 1 | 0 | 38959.3552 | 1 | 0 |  | -47.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3557 | 1 | 0 | 38959.3557 | 1 | 0 |  | -5.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3562 | 1 | 0 | 38959.3562 | 0 | 0 |  | 36.5 | 126.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250238 | 500576 | 250237.9994
38959.3566 | 1 | 0 | 38959.3567 | 1 | 0 |  | 78.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3571 | 1 | 0 | 38959.3571 | 1 | 0 |  | 120.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3576 | 1 | 0 | 38959.3576 | 1 | 0 |  | 162.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3581 | 1 | 0 | 38959.3581 | 1 | 0 |  | 204.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3586 | 1 | 0 | 38959.3586 | 1 | 0 |  | 246.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3591 | 1 | 0 | 38959.3591 | 1 | 0 |  | 288.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3596 | 1 | 0 | 38959.3596 | 1 | 0 |  | 330.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.36 | 1 | 0 | 38959.3601 | 1 | 0 |  | 372.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3605 | 1 | 0 | 38959.3605 | 1 | 0 |  | 414.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.361 | 1 | 0 | 38959.361 | 1 | 0 |  | 456.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3615 | 1 | 0 | 38959.3615 | 1 | 0 |  | 498.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.362 | 1 | 0 | 38959.362 | 1 | 0 |  | 540.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3625 | 1 | 0 | 38959.3625 | 1 | 0 |  | 582.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.363 | 1 | 0 | 38959.363 | 1 | 0 |  | 624.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3634 | 1 | 0 | 38959.3635 | 1 | 0 |  | 666.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3639 | 1 | 0 | 38959.3639 | 1 | 0 |  | 708.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3644 | 1 | 0 | 38959.3644 | 1 | 0 |  | 750.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3649 | 1 | 0 | 38959.3649 | 1 | 0 |  | 792.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3654 | 1 | 0 | 38959.3654 | 1 | 0 |  | 834.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3659 | 1 | 0 | 38959.3659 | 1 | 0 |  | 876.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3664 | 1 | 0 | 38959.3664 | 1 | 0 |  | 918.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3669 | 1 | 0 | 38959.3669 | 1 | 0 |  | 960.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3673 | 1 | 0 | 38959.3673 | 1 | 0 |  | 1002.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3678 | 1 | 0 | 38959.3678 | 1 | 0 |  | 1044.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3683 | 1 | 0 | 38959.3683 | 1 | 0 |  | 1086.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3688 | 1 | 0 | 38959.3688 | 1 | 0 |  | 1128.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3693 | 1 | 0 | 38959.3693 | 1 | 0 |  | 1170.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3698 | 1 | 0 | 38959.3698 | 1 | 0 |  | 1212.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3703 | 1 | 0 | 38959.3703 | 1 | 0 |  | 1254.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3707 | 1 | 0 | 38959.3708 | 1 | 0 |  | 1296.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3712 | 1 | 0 | 38959.3712 | 1 | 0 |  | 1338.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3717 | 1 | 0 | 38959.3717 | 1 | 0 |  | 1380.5 | 1470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3722 | 1 | 0 | 38959.3722 | 1 | 0 |  | 1422.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3727 | 1 | 0 | 38959.3727 | 1 | 0 |  | 1464.5 | 1554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250238 | 250238 | 250237.9994
38959.3732 | 1 | 0 | 38959.3732 | 2 | 0 |  | 1506.5 | 1596.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 250238 | 125069 | 250237.9994
38959.3737 | 2 | 0 | 38959.3737 | 2 | 1 |  | 1548.5 | 1638.5 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 125069 | 250238 | 125068.9988
38959.3741 | 13 | 8 | 38959.3742 | 13 | 9 |  | 1590.5 | 1680.5 | 0.79365 | 0.4884 | 0.79365 | 0.54945 | 0.0079365 | 0.004884 | 0.0079365 | 0.0054945 | 0.0030525 | 0.002442 | 49935.3501 | 62541.3002 | 30980.2144
38959.3746 | 85 | 69 | 38959.3746 | 116 | 98 |  | 1632.5 | 1722.5 | 5.1893 | 4.2125 | 7.0818 | 5.9829 | 0.051893 | 0.042125 | 0.070818 | 0.059829 | 0.009768 | 0.010989 | 15604.5502 | 13742.7067 | 3380.3015
38959.3751 | 1093 | 927 | 38959.3751 | 1060 | 1087 |  | 1674.5 | 1764.5 | 66.7277 | 56.5934 | 64.7131 | 66.3614 | 0.66728 | 0.56593 | 0.64713 | 0.66361 | 0.10134 | 0.016484 | 479.1235 | 722.15 | 45.8021
38959.3756 | 938 | 949 | 38959.3756 | 1118 | 1159 |  | 1716.5 | 1806.5 | 57.265 | 57.9365 | 68.254 | 70.757 | 0.57265 | 0.57937 | 0.68254 | 0.70757 | 0.0067155 | 0.025031 | 4515.2652 | 4009.5287 | 63.37
38959.3761 | 1031 | 1048 | 38959.3761 | 1189 | 1135 |  | 1758 | 1848 | 62.9426 | 63.9805 | 72.5885 | 69.2918 | 0.62943 | 0.6398 | 0.72589 | 0.69292 | 0.010379 | 0.032967 | 2177.6362 | 2070.5864 | 38.6287
38959.3766 | 992 | 938 | 38959.3766 | 1207 | 1177 |  | 1800.5 | 1890.5 | 60.5617 | 57.265 | 73.6874 | 71.8559 | 0.60562 | 0.57265 | 0.73687 | 0.71856 | 0.032967 | 0.018315 | 2043.0111 | 4695.1506 | 59.8531
38959.3771 | 1098 | 1042 | 38959.3771 | 1176 | 1174 |  | 1842.5 | 1932.5 | 67.033 | 63.6142 | 71.7949 | 71.6728 | 0.67033 | 0.63614 | 0.71795 | 0.71673 | 0.034188 | 0.001221 | 888.819 | 1020.3913 | 31.7607
38959.3775 | 987 | 997 | 38959.3776 | 948 | 921 |  | 1884.5 | 1974.5 | 60.2564 | 60.8669 | 57.8755 | 56.2271 | 0.60256 | 0.60867 | 0.57875 | 0.56227 | 0.006105 | 0.016484 | 12672.9853 | 50726.2395 | 51.9918
38959.378 | 983 | 929 | 38959.378 | 1200 | 1142 |  | 1926.5 | 2016.5 | 60.0122 | 56.7155 | 73.2601 | 69.7192 | 0.60012 | 0.56716 | 0.7326 | 0.69719 | 0.032967 | 0.035409 | 5579.9144 | 3472.556 | 61.8758
38959.3785 | 1219 | 1156 | 38959.3785 | 1128 | 1149 |  | 1968.5 | 2058.5 | 74.42 | 70.5739 | 68.8645 | 70.1465 | 0.7442 | 0.70574 | 0.68864 | 0.70147 | 0.038462 | 0.012821 | 702.655 | 965.0256 | 10.0628
38959.379 | 964 | 898 | 38959.379 | 1109 | 1131 |  | 2010 | 2100 | 58.8523 | 54.823 | 67.7045 | 69.0476 | 0.58852 | 0.54823 | 0.67705 | 0.69048 | 0.040293 | 0.013431 | 1564.6804 | 2773.0571 | 68.9372
38959.3795 | 961 | 893 | 38959.3795 | 953 | 938 |  | 2052.5 | 2142.5 | 58.6691 | 54.5177 | 58.1807 | 57.265 | 0.58669 | 0.54518 | 0.58181 | 0.57265 | 0.041514 | 0.0091575 | 1688.1744 | 3822.1552 | 70.8649
38959.38 | 1036 | 947 | 38959.38 | 976 | 892 |  | 2094.5 | 2184.5 | 63.2479 | 57.8144 | 59.5849 | 54.4567 | 0.63248 | 0.57814 | 0.59585 | 0.54457 | 0.054335 | 0.051282 | 2476.5953 | 3183.1816 | 53.2767
38959.3805 | 1870 | 39 | 38959.3805 | 2196 | 25 |  | 2136 | 2226 | 114.1636 | 2.381 | 134.0659 | 1.5263 | 1.1416 | 0.02381 | 1.3407 | 0.015263 | 1.1178 | 1.3254 | 40.5136 | 14.5727 | 193.8463
38959.3809 | 2351 | 3 | 38959.381 | 2226 | 2 |  | 2178 | 2268 | 143.5287 | 0.18315 | 135.8974 | 0.1221 | 1.4353 | 0.0018315 | 1.359 | 0.001221 | 1.4335 | 1.3578 | 6.556 | 12.6456 | 558.9794
38959.3814 | 2378 | 2 | 38959.3814 | 2246 | 1 |  | 2220 | 2310 | 145.177 | 0.1221 | 137.1184 | 0.06105 | 1.4518 | 0.001221 | 1.3712 | 0.0006105 | 1.4505 | 1.3706 | 5.3156 | 11.5615 | 639.3131
38959.3819 | 2128 | 1 | 38959.3819 | 1952 | 1 |  | 2262 | 2352 | 129.9145 | 0.06105 | 119.1697 | 0.06105 | 1.2991 | 0.0006105 | 1.1917 | 0.0006105 | 1.2985 | 1.1911 | 17.6777 | 28.3436 | 8267.8628
38959.3824 | 2031 | 0 | 38959.3824 | 2469 | 1 |  | 2304.5 | 2394.5 | 123.9927 | 0 | 150.7326 | 0.06105 | 1.2399 | 0 | 1.5073 | 0.0006105 | 1.2399 | 1.5067 | 23.2585 | 1.4335 | 22.0186
38959.3829 | 1988 | 1 | 38959.3829 | 2086 | 1 |  | 2346 | 2436 | 121.3675 | 0.06105 | 127.3504 | 0.06105 | 1.2137 | 0.0006105 | 1.2735 | 0.0006105 | 1.2131 | 1.2729 | 26.0028 | 20.0552 | 8592.7148
38959.3834 | 2010 | 0 | 38959.3834 | 2451 | 0 |  | 2388 | 2478 | 122.7106 | 0 | 149.6337 | 0 | 1.2271 | 0 | 1.4963 | 0 | 1.2271 | 1.4963 | 24.5463 | 2.1371 | 23.3192
38959.3839 | 2016 | 1 | 38959.3839 | 2012 | 1 |  | 2430 | 2520 | 123.0769 | 0.06105 | 122.8327 | 0.06105 | 1.2308 | 0.0006105 | 1.2283 | 0.0006105 | 1.2302 | 1.2277 | 24.2367 | 24.4848 | 9566.5774
38959.3843 | 2011 | 1 | 38959.3844 | 2369 | 1 |  | 2472 | 2562 | 122.7717 | 0.06105 | 144.6276 | 0.06105 | 1.2277 | 0.0006105 | 1.4463 | 0.0006105 | 1.2271 | 1.4457 | 24.7128 | 5.6845 | 2643.0276
38959.3848 | 2419 | 1 | 38959.3848 | 1983 | 1 |  | 2514 | 2604 | 147.6801 | 0.06105 | 121.0623 | 0.06105 | 1.4768 | 0.0006105 | 1.2106 | 0.0006105 | 1.4762 | 1.21 | 3.4951 | 26.6399 | 1753.9752
38959.3853 | 2454 | 0 | 38959.3853 | 2111 | 0 |  | 2556 | 2646 | 149.8168 | 0 | 128.8767 | 0 | 1.4982 | 0 | 1.2888 | 0 | 1.4982 | 1.2888 | 2.0122 | 18.5874 | 0.51406
38959.3858 | 2322 | 0 | 38959.3858 | 2322 | 1 |  | 2598 | 2688 | 141.7582 | 0 | 141.7582 | 0.06105 | 1.4176 | 0 | 1.4176 | 0.0006105 | 1.4176 | 1.417 | 7.8114 | 7.8578 | 6.3938
38959.3863 | 2145 | 0 | 38959.3863 | 2001 | 0 |  | 2640 | 2730 | 130.9524 | 0 | 122.1612 | 0 | 1.3095 | 0 | 1.2216 | 0 | 1.3095 | 1.2216 | 16.7077 | 25.1064 | 15.3982
38959.3868 | 2210 | 0 | 38959.3868 | 2487 | 0 |  | 2682 | 2772 | 134.9206 | 0 | 151.8315 | 0 | 1.3492 | 0 | 1.5183 | 0 | 1.3492 | 1.5183 | 13.2751 | 0.65862 | 11.9259
38959.3873 | 2295 | 1 | 38959.3873 | 1926 | 0 |  | 2724 | 2814 | 140.1099 | 0.06105 | 117.5824 | 0 | 1.4011 | 0.0006105 | 1.1758 | 0 | 1.4005 | 1.1758 | 9.0969 | 29.9782 | 4783.0159
38959.3877 | 1935 | 0 | 38959.3878 | 2460 | 1 |  | 2766 | 2856 | 118.1319 | 0 | 150.1832 | 0.06105 | 1.1813 | 0 | 1.5018 | 0.0006105 | 1.1813 | 1.5012 | 29.3736 | 1.8048 | 28.1923
38959.3882 | 1991 | 0 | 38959.3883 | 1978 | 0 |  | 2808 | 2898 | 121.5507 | 0 | 120.757 | 0 | 1.2155 | 0 | 1.2076 | 0 | 1.2155 | 1.2076 | 25.7348 | 26.5612 | 24.5193
38959.3887 | 2113 | 0 | 38959.3887 | 2298 | 1 |  | 2850 | 2940 | 128.9988 | 0 | 140.293 | 0.06105 | 1.29 | 0 | 1.4029 | 0.0006105 | 1.29 | 1.4023 | 18.4752 | 8.9848 | 17.1852

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -90 | 18.9 | 27.7 | 19.9 | 27.2 | 31.6 | 27.2 | 24.8 | 28.7 | 23.4 | 23.6
1 | -89 | 18.9 | 27.7 | 19.9 | 27.2 | 31.6 | 27.2 | 24.8 | 28.7 | 23.4 | 23.6
2 | -88 | 18.9 | 27.7 | 19.9 | 27.2 | 31.6 | 27.2 | 24.8 | 28.7 | 23.5 | 23.6
3 | -87 | 18.9 | 27.7 | 20 | 27.2 | 31.5 | 27.2 | 24.8 | 28.7 | 23.5 | 23.6
4 | -86 | 18.9 | 27.7 | 20 | 27.1 | 31.5 | 27.2 | 24.8 | 28.7 | 23.4 | 23.6
5 | -85 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.7 | 23.5 | 23.6
6 | -84 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.7 | 23.5 | 23.6
7 | -83 | 18.9 | 27.6 | 20.2 | 27.1 | 31.4 | 27.1 | 24.8 | 28.7 | 23.5 | 23.6
8 | -82 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.7 | 23.4 | 23.6
9 | -81 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.7 | 23.5 | 23.6
10 | -80 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
11 | -79 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.6 | 23.4 | 23.6
12 | -78 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
13 | -77 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
14 | -76 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
15 | -75 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
16 | -74 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
17 | -73 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
18 | -72 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
19 | -71 | 18.9 | 27.6 | 20.1 | 27.1 | 31.4 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
20 | -70 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
21 | -69 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
22 | -68 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.5 | 23.5 | 23.6
23 | -67 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.6 | 23.5 | 23.6
24 | -66 | 18.9 | 27.5 | 20.3 | 27 | 31.2 | 27 | 24.8 | 28.6 | 23.5 | 23.6
25 | -65 | 18.9 | 27.5 | 20.3 | 27.1 | 31.2 | 27 | 24.8 | 28.6 | 23.5 | 23.6
26 | -64 | 18.9 | 27.5 | 20.3 | 27.1 | 31.2 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
27 | -63 | 18.9 | 27.5 | 20.3 | 27.1 | 31.2 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
28 | -62 | 18.9 | 27.5 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
29 | -61 | 18.9 | 27.6 | 20.2 | 27.1 | 31.3 | 27.1 | 24.8 | 28.6 | 23.5 | 23.6
30 | -60 | 18.9 | 27.4 | 20.4 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.5 | 23.6
31 | -59 | 18.9 | 27.4 | 20.4 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.5 | 23.6
32 | -58 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.5 | 23.6
33 | -57 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
34 | -56 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.6 | 23.5 | 23.6
35 | -55 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
36 | -54 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
37 | -53 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 26.9 | 24.8 | 28.6 | 23.5 | 23.6
38 | -52 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.6 | 23.5 | 23.6
39 | -51 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
40 | -50 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
41 | -49 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
42 | -48 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
43 | -47 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
44 | -46 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
45 | -45 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.8 | 23.5 | 23.6
46 | -44 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.8 | 23.5 | 23.6
47 | -43 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.8 | 23.5 | 23.6
48 | -42 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.8 | 23.4 | 23.6
49 | -41 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
50 | -40 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
51 | -39 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
52 | -38 | 18.9 | 27.4 | 20.4 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.5 | 23.6
53 | -37 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
54 | -36 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
55 | -35 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
56 | -34 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.6 | 23.5 | 23.6
57 | -33 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
58 | -32 | 18.9 | 27.4 | 20.4 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.5 | 23.6
59 | -31 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
60 | -30 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
61 | -29 | 18.9 | 27.4 | 20.5 | 27 | 31 | 26.9 | 24.8 | 28.7 | 23.5 | 23.6
62 | -28 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
63 | -27 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
64 | -26 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 26.9 | 24.8 | 28.7 | 23.4 | 23.6
65 | -25 | 18.9 | 27.4 | 20.5 | 26.9 | 30.9 | 26.9 | 24.8 | 28.7 | 23.5 | 23.6
66 | -24 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 26.9 | 24.8 | 28.7 | 23.5 | 23.6
67 | -23 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
68 | -22 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
69 | -21 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 27 | 24.8 | 28.6 | 23.5 | 23.6
70 | -20 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.6 | 23.5 | 23.6
71 | -19 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 26.9 | 24.8 | 28.6 | 23.5 | 23.6
72 | -18 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
73 | -17 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.5 | 23.6
74 | -16 | 18.9 | 27.4 | 20.5 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
75 | -15 | 18.9 | 27.4 | 20.5 | 27 | 30.9 | 26.9 | 24.8 | 28.7 | 23.4 | 23.6
76 | -14 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.7 | 23.4 | 23.6
77 | -13 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.8 | 23.5 | 23.6
78 | -12 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.8 | 23.4 | 23.6
79 | -11 | 18.9 | 27.4 | 20.4 | 27 | 31 | 27 | 24.8 | 28.8 | 23.4 | 23.6
80 | -10 | 18.9 | 27.4 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.8 | 23.5 | 23.6
81 | -9 | 18.9 | 27.4 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.8 | 23.4 | 23.6
82 | -8 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.8 | 23.4 | 23.6
83 | -7 | 18.9 | 27.4 | 20.4 | 27 | 31.1 | 27 | 24.8 | 28.8 | 23.4 | 23.6
84 | -6 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.4 | 23.6
85 | -5 | 18.9 | 27.5 | 20.3 | 27 | 31.1 | 27 | 24.8 | 28.7 | 23.4 | 23.6
86 | -4 | 18.9 | 27.5 | 20.2 | 27.1 | 31.2 | 27.1 | 24.8 | 28.7 | 23.4 | 23.6
87 | -3 | 18.9 | 29 | 17.3 | 28 | 33.2 | 28.2 | 24.6 | 28.4 | 23.4 | 23.5
88 | -2 | 18.8 | 29.8 | 15.6 | 28.6 | 34.5 | 28.8 | 24.4 | 28.3 | 23.3 | 23.4
89 | -1 | 19 | 29.9 | 15.4 | 28.7 | 34.6 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
90 | 0 | 19.7 | 29.9 | 15.4 | 28.7 | 34.6 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
91 | 1 | 20.9 | 29.9 | 15.4 | 28.7 | 34.6 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
92 | 2 | 22.6 | 29.7 | 15.8 | 28.6 | 34.4 | 28.7 | 24.4 | 28.4 | 23.3 | 23.4
93 | 3 | 24.9 | 29.9 | 15.5 | 28.7 | 34.6 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
94 | 4 | 27.5 | 30 | 15.4 | 28.7 | 34.7 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
95 | 5 | 30.6 | 30 | 15.4 | 28.7 | 34.7 | 28.9 | 24.4 | 28.3 | 23.3 | 23.4
96 | 6 | 34 | 30 | 15.3 | 28.8 | 34.7 | 28.9 | 24.4 | 28.2 | 23.3 | 23.4
97 | 7 | 37.6 | 30.7 | 13.9 | 29.4 | 35.6 | 29.4 | 24.3 | 28.1 | 23.2 | 23.4
98 | 8 | 41.5 | 31 | 13.1 | 29.7 | 36 | 29.7 | 24.2 | 28 | 23.2 | 23.4
99 | 9 | 45.6 | 31.1 | 13.2 | 29.7 | 36 | 29.7 | 24.2 | 28.1 | 23.2 | 23.4
100 | 10 | 49.9 | 31.1 | 13.3 | 29.7 | 36 | 29.7 | 24.2 | 28.1 | 23.2 | 23.4
101 | 11 | 54.4 | 31.1 | 13.3 | 29.8 | 36 | 29.7 | 24.2 | 28.1 | 23.2 | 23.4
102 | 12 | 59.1 | 31.2 | 13.4 | 29.8 | 36 | 29.7 | 24.2 | 28.1 | 23.2 | 23.4
103 | 13 | 63.9 | 31.2 | 13.5 | 29.9 | 36 | 29.7 | 24.2 | 28.1 | 23.2 | 23.4
104 | 14 | 68.9 | 31.3 | 13.5 | 29.9 | 36 | 29.7 | 24.2 | 28.2 | 23.2 | 23.4
105 | 15 | 74 | 31.3 | 13.6 | 30 | 36.1 | 29.7 | 24.2 | 28.2 | 23.2 | 23.4
106 | 16 | 79.2 | 31.4 | 13.7 | 30 | 36.1 | 29.7 | 24.2 | 28.2 | 23.2 | 23.4
107 | 17 | 84.5 | 31.4 | 13.9 | 30.1 | 36 | 29.7 | 24.2 | 28.2 | 23.2 | 23.3
108 | 18 | 89.9 | 31.5 | 13.9 | 30.2 | 36.1 | 29.7 | 24.2 | 28.3 | 23.2 | 23.4
109 | 19 | 95.5 | 31.6 | 14 | 30.2 | 36.1 | 29.7 | 24.2 | 28.3 | 23.2 | 23.3
110 | 20 | 101.1 | 31.6 | 14.2 | 30.3 | 36.1 | 29.7 | 24.2 | 28.3 | 23.2 | 23.3
111 | 21 | 106.7 | 31.7 | 14.3 | 30.3 | 36.1 | 29.7 | 24.2 | 28.3 | 23.2 | 23.4
112 | 22 | 112.5 | 31.8 | 14.6 | 30.4 | 36 | 29.7 | 24.2 | 28.4 | 23.2 | 23.4
113 | 23 | 118.4 | 31.9 | 14.8 | 30.5 | 36 | 29.7 | 24.2 | 28.4 | 23.2 | 23.4
114 | 24 | 124.3 | 31.9 | 15.2 | 30.5 | 35.9 | 29.6 | 24.2 | 28.4 | 23.2 | 23.4
115 | 25 | 130.2 | 32 | 15.4 | 30.7 | 36 | 29.7 | 24.2 | 28.4 | 23.2 | 23.4
116 | 26 | 136.2 | 32.1 | 15.8 | 30.7 | 35.8 | 29.6 | 24.2 | 28.4 | 23.2 | 23.4
117 | 27 | 142.3 | 31.3 | 18.1 | 30 | 34.7 | 28.9 | 24.4 | 28.5 | 23.3 | 23.4
118 | 28 | 148.2 | 31.4 | 18.3 | 30.1 | 34.7 | 28.9 | 24.4 | 28.5 | 23.3 | 23.4
119 | 29 | 154.2 | 31.6 | 18.5 | 30.2 | 34.7 | 28.9 | 24.4 | 28.5 | 23.3 | 23.4
120 | 30 | 160.3 | 31.7 | 18.9 | 30.4 | 34.7 | 28.9 | 24.4 | 28.4 | 23.3 | 23.4
121 | 31 | 166.3 | 31.8 | 19.2 | 30.5 | 34.6 | 28.9 | 24.4 | 28.4 | 23.3 | 23.4
122 | 32 | 172.4 | 32 | 19.4 | 30.7 | 34.7 | 28.9 | 24.4 | 28.4 | 23.3 | 23.4
123 | 33 | 178.4 | 32.2 | 19.7 | 30.8 | 34.7 | 28.9 | 24.4 | 28.4 | 23.3 | 23.4
124 | 34 | 184.6 | 32.3 | 20.1 | 31 | 34.7 | 28.9 | 24.4 | 28.4 | 23.3 | 23.4
125 | 35 | 190.7 | 32.5 | 20.5 | 31.2 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.4
126 | 36 | 196.8 | 32.7 | 20.8 | 31.4 | 34.7 | 28.9 | 24.4 | 28.3 | 23.4 | 23.4
127 | 37 | 202.9 | 32.9 | 21 | 31.6 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
128 | 38 | 209 | 33.1 | 21.4 | 31.7 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
129 | 39 | 215.1 | 33.4 | 21.8 | 31.9 | 34.7 | 28.9 | 24.4 | 28.5 | 23.4 | 23.4
130 | 40 | 221.3 | 33.6 | 22.2 | 32.2 | 34.7 | 28.9 | 24.4 | 28.5 | 23.4 | 23.4
131 | 41 | 227.4 | 33.8 | 22.8 | 32.4 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.4
132 | 42 | 233.5 | 34.1 | 23.3 | 32.6 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
133 | 43 | 239.6 | 34.3 | 23.7 | 32.9 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
134 | 44 | 245.8 | 34.6 | 24.1 | 33.2 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
135 | 45 | 251.9 | 34.9 | 24.7 | 33.5 | 34.7 | 28.9 | 24.4 | 28.4 | 23.4 | 23.5
136 | 46 | 258.1 | 35.2 | 25.3 | 33.8 | 34.7 | 28.9 | 24.4 | 28.3 | 23.5 | 23.5
137 | 47 | 264.1 | 35.5 | 26.1 | 34.1 | 34.8 | 29 | 24.4 | 28.3 | 23.5 | 23.5
138 | 48 | 270.2 | 35.8 | 26.9 | 34.3 | 34.7 | 28.9 | 24.4 | 28.3 | 23.5 | 23.5
139 | 49 | 276.3 | 36.1 | 27.3 | 34.7 | 34.7 | 28.9 | 24.4 | 28.3 | 23.5 | 23.5
140 | 50 | 282.4 | 36.5 | 27.8 | 35 | 34.8 | 29 | 24.4 | 28.3 | 23.5 | 23.5
141 | 51 | 288.4 | 36.8 | 28.4 | 35.4 | 34.8 | 29 | 24.4 | 28.4 | 23.6 | 23.5
142 | 52 | 294.4 | 37.2 | 28.9 | 35.7 | 34.7 | 28.9 | 24.4 | 28.4 | 23.6 | 23.5
143 | 53 | 300.3 | 37.6 | 29.5 | 36.1 | 34.8 | 29 | 24.4 | 28.4 | 23.6 | 23.5
144 | 54 | 306.3 | 37.9 | 30.2 | 36.5 | 34.8 | 29 | 24.4 | 28.3 | 23.6 | 23.5
145 | 55 | 312.2 | 38.3 | 30.8 | 36.8 | 34.8 | 29 | 24.4 | 28.4 | 23.6 | 23.5
146 | 56 | 318.1 | 38.7 | 31.7 | 37.3 | 34.8 | 29 | 24.4 | 28.4 | 23.7 | 23.6
147 | 57 | 324 | 39.2 | 32.3 | 37.6 | 34.8 | 29 | 24.4 | 28.4 | 23.7 | 23.5
148 | 58 | 330 | 39.7 | 32.9 | 38.1 | 34.8 | 29 | 24.4 | 28.4 | 23.7 | 23.6
149 | 59 | 335.9 | 40.1 | 33.6 | 38.5 | 34.8 | 29 | 24.4 | 28.5 | 23.8 | 23.6
150 | 60 | 341.6 | 40.6 | 34.2 | 39 | 34.9 | 29.1 | 24.4 | 28.5 | 23.8 | 23.6
151 | 61 | 347.3 | 41 | 35 | 39.5 | 34.9 | 29 | 24.4 | 28.5 | 23.8 | 23.6
152 | 62 | 353 | 41.5 | 35.9 | 39.9 | 34.9 | 29.1 | 24.4 | 28.6 | 23.9 | 23.6
153 | 63 | 358.8 | 42 | 36.9 | 40.4 | 34.9 | 29.1 | 24.4 | 28.6 | 23.9 | 23.6
154 | 64 | 364.6 | 42.6 | 37.8 | 40.9 | 34.9 | 29.1 | 24.4 | 28.6 | 23.9 | 23.6
155 | 65 | 370.3 | 43.1 | 38.8 | 41.4 | 34.9 | 29.1 | 24.4 | 28.6 | 24 | 23.7
156 | 66 | 376 | 43.7 | 39.7 | 41.9 | 34.9 | 29.1 | 24.4 | 28.6 | 24 | 23.7
157 | 67 | 381.6 | 44.3 | 40.4 | 42.5 | 35 | 29.1 | 24.4 | 28.5 | 24.1 | 23.7
158 | 68 | 387.1 | 44.8 | 41.3 | 43 | 35 | 29.1 | 24.4 | 28.5 | 24.1 | 23.7
159 | 69 | 392.6 | 45.4 | 42.5 | 43.6 | 34.9 | 29.1 | 24.4 | 28.6 | 24.2 | 23.7
160 | 70 | 398.1 | 46 | 43.4 | 44.2 | 35 | 29.1 | 24.4 | 28.6 | 24.2 | 23.7
161 | 71 | 403.5 | 46.6 | 44.5 | 44.9 | 35 | 29.2 | 24.4 | 28.6 | 24.3 | 23.7
162 | 72 | 408.9 | 47.3 | 45.5 | 45.5 | 35 | 29.2 | 24.4 | 28.5 | 24.4 | 23.8
163 | 73 | 414.3 | 47.9 | 46.4 | 46.1 | 35.1 | 29.2 | 24.4 | 28.5 | 24.4 | 23.8
164 | 74 | 419.7 | 48.7 | 47.4 | 46.8 | 35.1 | 29.2 | 24.4 | 28.5 | 24.5 | 23.8
165 | 75 | 425 | 49.3 | 48.6 | 47.5 | 35.1 | 29.3 | 24.4 | 28.5 | 24.6 | 23.8
166 | 76 | 430.3 | 50.1 | 49.7 | 48.2 | 35.2 | 29.3 | 24.4 | 28.5 | 24.7 | 23.8
167 | 77 | 435.6 | 50.8 | 50.8 | 48.9 | 35.2 | 29.3 | 24.4 | 28.5 | 24.7 | 23.9
168 | 78 | 440.9 | 51.5 | 52.1 | 49.6 | 35.2 | 29.3 | 24.4 | 28.5 | 24.8 | 23.9
169 | 79 | 446 | 52.3 | 53.4 | 50.4 | 35.3 | 29.4 | 24.4 | 28.6 | 24.9 | 23.9
170 | 80 | 451 | 53.1 | 54.7 | 51.1 | 35.3 | 29.4 | 24.4 | 28.6 | 25 | 23.9
171 | 81 | 456 | 53.9 | 55.9 | 51.9 | 35.4 | 29.4 | 24.4 | 28.6 | 25.1 | 24
172 | 82 | 460.9 | 54.8 | 57.1 | 52.7 | 35.4 | 29.4 | 24.4 | 28.5 | 25.2 | 24
173 | 83 | 465.9 | 55.5 | 58.6 | 53.5 | 35.4 | 29.4 | 24.4 | 28.5 | 25.3 | 24.1
174 | 84 | 470.9 | 56.4 | 59.8 | 54.4 | 35.5 | 29.5 | 24.4 | 28.5 | 25.4 | 24.1
175 | 85 | 475.8 | 57.3 | 61.1 | 55.2 | 35.5 | 29.5 | 24.4 | 28.5 | 25.5 | 24.2
176 | 86 | 480.7 | 58 | 62.8 | 56 | 35.4 | 29.5 | 24.5 | 28.5 | 25.7 | 24.2
177 | 87 | 485.6 | 58.7 | 64.7 | 56.6 | 35 | 29.3 | 24.5 | 28.6 | 25.8 | 24.2
178 | 88 | 490.5 | 59.7 | 66.1 | 57.5 | 35.3 | 29.4 | 24.5 | 28.5 | 26 | 24.3
179 | 89 | 494.9 | 60.6 | 67.5 | 58.4 | 35.4 | 29.5 | 24.5 | 28.6 | 26.1 | 24.3
180 | 90 | 498.9 | 61.6 | 68.8 | 59.4 | 35.5 | 29.6 | 24.5 | 28.6 | 26.3 | 24.4
181 | 91 | 502.3 | 62.5 | 70.3 | 60.3 | 35.5 | 29.6 | 24.5 | 28.7 | 26.5 | 24.4
182 | 92 | 505.6 | 63.5 | 71.6 | 61.2 | 35.6 | 29.7 | 24.5 | 28.7 | 26.7 | 24.5
183 | 93 | 508.8 | 64.4 | 72.9 | 62.1 | 35.6 | 29.7 | 24.5 | 28.7 | 26.8 | 24.5
184 | 94 | 511.7 | 65.3 | 74.3 | 63.1 | 35.8 | 29.8 | 24.5 | 28.8 | 27 | 24.6
185 | 95 | 514.6 | 66.4 | 75.5 | 64.1 | 36.1 | 29.9 | 24.5 | 28.7 | 27.3 | 24.6
186 | 96 | 517.3 | 67.3 | 77 | 65 | 36.1 | 30 | 24.5 | 28.7 | 27.5 | 24.7
187 | 97 | 519.8 | 68.1 | 78.8 | 65.8 | 36 | 29.9 | 24.6 | 28.7 | 27.7 | 24.7
188 | 98 | 522.1 | 69 | 80.4 | 66.7 | 35.9 | 29.9 | 24.6 | 28.7 | 28 | 24.8
189 | 99 | 524 | 69.7 | 82.3 | 67.5 | 35.4 | 29.8 | 24.7 | 28.8 | 28.2 | 24.8
190 | 100 | 525.8 | 70.4 | 84 | 68.2 | 35.2 | 29.7 | 24.7 | 28.9 | 28.5 | 24.9
191 | 101 | 527.2 | 71.1 | 85.7 | 69.1 | 35.1 | 29.6 | 24.8 | 28.9 | 28.8 | 25
192 | 102 | 528.4 | 72 | 87.2 | 69.9 | 35.1 | 29.6 | 24.8 | 28.9 | 29 | 25
193 | 103 | 529.2 | 72.9 | 88.5 | 70.8 | 35.2 | 29.7 | 24.8 | 28.9 | 29.3 | 25.1
194 | 104 | 529.9 | 73.8 | 89.8 | 71.7 | 35.3 | 29.8 | 24.8 | 28.9 | 29.6 | 25.1
195 | 105 | 530.3 | 74.7 | 91.1 | 72.6 | 35.4 | 29.9 | 24.8 | 29 | 29.8 | 25.2
196 | 106 | 530.5 | 75.7 | 92.5 | 73.5 | 35.6 | 30 | 24.8 | 29.1 | 30.1 | 25.2
197 | 107 | 530.6 | 76.6 | 93.6 | 74.4 | 35.8 | 30.1 | 24.9 | 29.1 | 30.4 | 25.3
198 | 108 | 530.5 | 77.5 | 94.8 | 75.4 | 36 | 30.3 | 24.9 | 29.1 | 30.6 | 25.4
199 | 109 | 530.3 | 78.4 | 96.1 | 76.3 | 36.1 | 30.4 | 24.9 | 29 | 30.9 | 25.4
200 | 110 | 530 | 79.3 | 97.1 | 77.2 | 36.3 | 30.5 | 24.9 | 29 | 31.2 | 25.5
201 | 111 | 529.6 | 80.2 | 98.2 | 78.1 | 36.4 | 30.7 | 24.9 | 29.1 | 31.5 | 25.6
202 | 112 | 529.2 | 81.1 | 99.2 | 79 | 36.7 | 30.9 | 24.9 | 29 | 31.8 | 25.7
203 | 113 | 528.6 | 82.1 | 100.2 | 79.9 | 37 | 31.1 | 24.9 | 29 | 32.1 | 25.8
204 | 114 | 528 | 83.1 | 101.1 | 80.9 | 37.3 | 31.3 | 24.9 | 29 | 32.3 | 25.8
205 | 115 | 527.4 | 84.1 | 102 | 81.8 | 37.6 | 31.5 | 24.9 | 29 | 32.6 | 25.9
206 | 116 | 526.7 | 85 | 102.9 | 82.7 | 37.9 | 31.7 | 25 | 29 | 32.9 | 26
207 | 117 | 526.2 | 86 | 103.9 | 83.6 | 38.2 | 31.9 | 25 | 29 | 33.1 | 26.1
208 | 118 | 525.7 | 86.9 | 104.9 | 84.5 | 38.5 | 32.2 | 25 | 29.1 | 33.5 | 26.2
209 | 119 | 525.2 | 87.8 | 105.9 | 85.4 | 38.8 | 32.4 | 25 | 29.1 | 33.8 | 26.3
210 | 120 | 524.7 | 88.8 | 106.8 | 86.3 | 39.2 | 32.7 | 25 | 29.1 | 34.1 | 26.3
211 | 121 | 524.2 | 89.8 | 107.5 | 87.3 | 39.6 | 32.9 | 25 | 29 | 34.3 | 26.4
212 | 122 | 523.8 | 90.8 | 108.3 | 88.2 | 40 | 33.2 | 25 | 29 | 34.6 | 26.5
213 | 123 | 523.5 | 91.8 | 109.3 | 89.1 | 40.5 | 33.5 | 25 | 29.1 | 34.9 | 26.6
214 | 124 | 523.2 | 92.8 | 110.3 | 90 | 40.9 | 33.7 | 25 | 29.1 | 35.1 | 26.7
215 | 125 | 523 | 93.7 | 111.2 | 90.9 | 41.2 | 34 | 25.1 | 29.1 | 35.4 | 26.9
216 | 126 | 522.9 | 94.6 | 112.1 | 91.8 | 41.5 | 34.2 | 25.1 | 29.1 | 35.6 | 27
217 | 127 | 522.8 | 95.5 | 113.3 | 92.7 | 41.8 | 34.4 | 25.1 | 29.2 | 35.9 | 27.1
218 | 128 | 522.7 | 96.3 | 114.3 | 93.5 | 42 | 34.6 | 25.1 | 29.2 | 36.2 | 27.2
219 | 129 | 522.7 | 97.2 | 115.3 | 94.3 | 42.2 | 34.8 | 25.2 | 29.2 | 36.5 | 27.3
220 | 130 | 522.8 | 98 | 116.6 | 95.2 | 42.4 | 34.9 | 25.2 | 29.2 | 36.8 | 27.4
221 | 131 | 523 | 98.9 | 117.6 | 96.1 | 42.7 | 35.1 | 25.3 | 29.2 | 37.1 | 27.5
222 | 132 | 523.2 | 99.7 | 118.7 | 96.9 | 42.8 | 35.3 | 25.3 | 29.2 | 37.4 | 27.6
223 | 133 | 523.4 | 100.7 | 119.5 | 97.8 | 43.1 | 35.5 | 25.4 | 29.2 | 37.7 | 27.7
224 | 134 | 523.6 | 101.6 | 120.5 | 98.7 | 43.5 | 35.8 | 25.4 | 29.3 | 37.9 | 27.8
225 | 135 | 524 | 102.4 | 121.7 | 99.6 | 43.7 | 35.9 | 25.5 | 29.3 | 38.2 | 28
226 | 136 | 524.2 | 103.3 | 123 | 100.4 | 43.8 | 36.1 | 25.5 | 29.3 | 38.5 | 28.1
227 | 137 | 524.5 | 104.1 | 124.1 | 101.2 | 44 | 36.3 | 25.6 | 29.4 | 38.8 | 28.2
228 | 138 | 524.7 | 105 | 125.3 | 102.1 | 44.2 | 36.5 | 25.6 | 29.4 | 39.1 | 28.3
229 | 139 | 524.9 | 105.8 | 126.3 | 102.9 | 44.5 | 36.7 | 25.7 | 29.4 | 39.3 | 28.4
230 | 140 | 525.1 | 106.7 | 127.4 | 103.8 | 44.7 | 36.9 | 25.7 | 29.4 | 39.6 | 28.5
231 | 141 | 525.4 | 107.5 | 128.5 | 104.6 | 44.9 | 37 | 25.8 | 29.4 | 39.9 | 28.7
232 | 142 | 525.6 | 108.4 | 129.5 | 105.5 | 45.2 | 37.3 | 25.9 | 29.3 | 40.2 | 28.8
233 | 143 | 525.8 | 109.2 | 130.7 | 106.3 | 45.4 | 37.4 | 25.9 | 29.4 | 40.4 | 28.9
234 | 144 | 526.1 | 110.1 | 131.7 | 107.1 | 45.6 | 37.6 | 26 | 29.5 | 40.7 | 29.1
235 | 145 | 526.3 | 110.9 | 132.8 | 107.9 | 45.8 | 37.8 | 26 | 29.6 | 40.9 | 29.2
236 | 146 | 526.5 | 111.8 | 133.8 | 108.8 | 46.1 | 38 | 26.1 | 29.6 | 41.1 | 29.4
237 | 147 | 526.7 | 112.7 | 134.8 | 109.7 | 46.3 | 38.2 | 26.2 | 29.7 | 41.4 | 29.5
238 | 148 | 526.9 | 113.6 | 135.9 | 110.6 | 46.5 | 38.4 | 26.2 | 29.7 | 41.6 | 29.7
239 | 149 | 527.1 | 114.4 | 136.9 | 111.4 | 46.8 | 38.6 | 26.3 | 29.7 | 41.8 | 29.8
240 | 150 | 527.2 | 115.3 | 138 | 112.2 | 47 | 38.8 | 26.4 | 29.7 | 42.1 | 30
241 | 151 | 527.3 | 116.1 | 139 | 113.2 | 47.2 | 39 | 26.4 | 29.7 | 42.3 | 30.1
242 | 152 | 527.4 | 116.9 | 140.1 | 114 | 47.4 | 39.2 | 26.5 | 29.8 | 42.5 | 30.3
243 | 153 | 527.5 | 117.7 | 141.3 | 114.8 | 47.6 | 39.4 | 26.6 | 29.8 | 42.8 | 30.4
244 | 154 | 527.6 | 118.6 | 142.2 | 115.5 | 47.8 | 39.6 | 26.7 | 29.9 | 43 | 30.6
245 | 155 | 527.6 | 119.5 | 143.2 | 116.3 | 48.1 | 39.8 | 26.8 | 30 | 43.3 | 30.7
246 | 156 | 527.7 | 120.3 | 144.2 | 117.2 | 48.3 | 40 | 26.8 | 30 | 43.5 | 30.9
247 | 157 | 527.7 | 121.2 | 145.2 | 118.1 | 48.5 | 40.2 | 26.9 | 30.2 | 43.7 | 31.1
248 | 158 | 527.9 | 122.1 | 146.2 | 118.9 | 48.8 | 40.4 | 27 | 30.3 | 44 | 31.2
249 | 159 | 527.9 | 122.8 | 147.2 | 119.8 | 49 | 40.6 | 27.1 | 30.4 | 44.2 | 31.4
250 | 160 | 527.9 | 123.6 | 148.3 | 120.6 | 49.2 | 40.7 | 27.2 | 30.4 | 44.5 | 31.5
251 | 161 | 528 | 124.5 | 149.3 | 121.4 | 49.4 | 40.9 | 27.3 | 30.5 | 44.7 | 31.7
252 | 162 | 528 | 125.3 | 150.4 | 122.2 | 49.6 | 41.1 | 27.3 | 30.6 | 45 | 31.8
253 | 163 | 528.1 | 126.2 | 151.5 | 123 | 49.9 | 41.3 | 27.4 | 30.7 | 45.2 | 32
254 | 164 | 528 | 127 | 152.4 | 123.8 | 50.1 | 41.5 | 27.5 | 30.8 | 45.4 | 32.1
255 | 165 | 528 | 127.9 | 153.4 | 124.7 | 50.4 | 41.7 | 27.6 | 30.8 | 45.7 | 32.3
256 | 166 | 528 | 128.8 | 154.4 | 125.5 | 50.7 | 41.9 | 27.7 | 30.9 | 46 | 32.4
257 | 167 | 528 | 129.6 | 155.4 | 126.4 | 51 | 42.2 | 27.8 | 30.9 | 46.3 | 32.6
258 | 168 | 528.1 | 130.5 | 156.3 | 127.2 | 51.3 | 42.4 | 27.9 | 31 | 46.6 | 32.7
259 | 169 | 528.2 | 131.3 | 157.1 | 128.1 | 51.5 | 42.6 | 28 | 31 | 46.9 | 32.8
260 | 170 | 528.2 | 132.1 | 158.2 | 128.9 | 51.7 | 42.8 | 28.1 | 31.1 | 47.1 | 33
261 | 171 | 528.3 | 132.9 | 159.2 | 129.8 | 51.9 | 43 | 28.2 | 31.2 | 47.3 | 33.2
262 | 172 | 528.4 | 133.7 | 160.1 | 130.6 | 52.2 | 43.2 | 28.3 | 31.3 | 47.5 | 33.3
263 | 173 | 528.4 | 134.6 | 161.1 | 131.3 | 52.4 | 43.3 | 28.4 | 31.3 | 47.6 | 33.5
264 | 174 | 528.4 | 135.4 | 161.9 | 132.2 | 52.6 | 43.5 | 28.5 | 31.4 | 47.8 | 33.7
265 | 175 | 528.5 | 136.2 | 163.1 | 132.9 | 52.8 | 43.7 | 28.6 | 31.4 | 48 | 33.9
266 | 176 | 528.5 | 137 | 164.2 | 133.7 | 53 | 43.9 | 28.7 | 31.6 | 48.3 | 34
267 | 177 | 528.4 | 137.8 | 165.3 | 134.6 | 53.2 | 44.1 | 28.8 | 31.6 | 48.6 | 34.2
268 | 178 | 528.5 | 138.6 | 166.2 | 135.3 | 53.4 | 44.2 | 28.9 | 31.7 | 48.8 | 34.3
269 | 179 | 528.5 | 139.4 | 167 | 136.2 | 53.7 | 44.5 | 29 | 31.8 | 49 | 34.5
270 | 180 | 528.6 | 140.2 | 168.1 | 137 | 53.9 | 44.6 | 29.1 | 31.9 | 49.1 | 34.7
271 | 181 | 528.6 | 141 | 169.1 | 137.7 | 54.1 | 44.8 | 29.2 | 31.9 | 49.3 | 34.9
272 | 182 | 528.6 | 141.8 | 170.2 | 138.5 | 54.3 | 45 | 29.4 | 32.1 | 49.5 | 35.1
273 | 183 | 528.6 | 142.7 | 171 | 139.3 | 54.6 | 45.2 | 29.5 | 32.2 | 49.7 | 35.2
274 | 184 | 528.7 | 143.5 | 172 | 140.1 | 54.7 | 45.4 | 29.6 | 32.2 | 49.8 | 35.4
275 | 185 | 528.8 | 144.2 | 173 | 140.9 | 54.9 | 45.5 | 29.7 | 32.3 | 50 | 35.6
276 | 186 | 528.8 | 145 | 174 | 141.7 | 55.1 | 45.7 | 29.8 | 32.4 | 50.1 | 35.8
277 | 187 | 528.8 | 145.8 | 175.1 | 142.5 | 55.3 | 45.9 | 29.9 | 32.6 | 50.3 | 36
278 | 188 | 528.8 | 146.6 | 176 | 143.3 | 55.5 | 46 | 30 | 32.7 | 50.6 | 36.1
279 | 189 | 528.9 | 147.4 | 176.9 | 144.1 | 55.7 | 46.2 | 30.2 | 32.8 | 50.9 | 36.3
280 | 190 | 528.9 | 148.2 | 177.7 | 144.8 | 56 | 46.4 | 30.3 | 32.8 | 51.1 | 36.4
281 | 191 | 528.8 | 149 | 178.5 | 145.7 | 56.3 | 46.7 | 30.4 | 32.9 | 51.2 | 36.6
282 | 192 | 528.8 | 149.8 | 179.4 | 146.5 | 56.5 | 46.8 | 30.5 | 33 | 51.4 | 36.8
283 | 193 | 528.9 | 150.6 | 180.3 | 147.2 | 56.7 | 47 | 30.6 | 33.1 | 51.6 | 37
284 | 194 | 528.9 | 151.4 | 181.4 | 148.1 | 56.9 | 47.2 | 30.8 | 33.2 | 51.8 | 37.2
285 | 195 | 528.9 | 152.1 | 182.3 | 148.8 | 57.1 | 47.3 | 30.9 | 33.4 | 52 | 37.3
286 | 196 | 529 | 152.9 | 183.5 | 149.5 | 57.2 | 47.5 | 31 | 33.5 | 52.3 | 37.5
287 | 197 | 529.1 | 153.6 | 184.5 | 150.3 | 57.3 | 47.6 | 31.2 | 33.6 | 52.6 | 37.6
288 | 198 | 529.1 | 154.4 | 185.5 | 151.1 | 57.5 | 47.8 | 31.3 | 33.7 | 53 | 37.8
289 | 199 | 529.1 | 155.1 | 186.4 | 151.9 | 57.7 | 48 | 31.4 | 33.8 | 53.3 | 37.9
290 | 200 | 529.2 | 155.9 | 187.4 | 152.6 | 57.9 | 48.1 | 31.6 | 33.9 | 53.5 | 38.1
291 | 201 | 529.2 | 156.7 | 188.4 | 153.4 | 58.1 | 48.3 | 31.7 | 34 | 53.7 | 38.3
292 | 202 | 529.3 | 157.5 | 189.3 | 154.2 | 58.3 | 48.4 | 31.8 | 34.1 | 53.9 | 38.5
293 | 203 | 529.4 | 158.2 | 190.2 | 154.9 | 58.4 | 48.6 | 32 | 34.2 | 54.2 | 38.6
294 | 204 | 529.4 | 159 | 191.1 | 155.7 | 58.7 | 48.8 | 32.1 | 34.4 | 54.5 | 38.8
295 | 205 | 529.4 | 159.8 | 192 | 156.5 | 58.9 | 49 | 32.2 | 34.5 | 54.7 | 39
296 | 206 | 529.4 | 160.5 | 193 | 157.2 | 59 | 49.1 | 32.4 | 34.6 | 55 | 39.1
297 | 207 | 529.4 | 161.3 | 193.9 | 158 | 59.1 | 49.2 | 32.5 | 34.7 | 55.3 | 39.3
298 | 208 | 529.4 | 162 | 194.9 | 158.7 | 59.3 | 49.4 | 32.6 | 34.9 | 55.6 | 39.4
299 | 209 | 529.4 | 162.8 | 195.9 | 159.5 | 59.4 | 49.5 | 32.8 | 35.1 | 55.7 | 39.6
300 | 210 | 529.4 | 163.5 | 196.9 | 160.2 | 59.6 | 49.7 | 32.9 | 35.2 | 55.8 | 39.8
301 | 211 | 529.4 | 164.3 | 197.7 | 161 | 59.9 | 49.9 | 33 | 35.3 | 56 | 40
302 | 212 | 529.4 | 165.1 | 198.6 | 161.8 | 60.1 | 50.1 | 33.2 | 35.4 | 56.1 | 40.2
303 | 213 | 529.4 | 165.8 | 199.5 | 162.5 | 60.3 | 50.2 | 33.3 | 35.5 | 56.3 | 40.4
304 | 214 | 529.4 | 166.6 | 200.4 | 163.3 | 60.5 | 50.4 | 33.5 | 35.6 | 56.5 | 40.6
305 | 215 | 529.5 | 167.3 | 201.3 | 164 | 60.6 | 50.5 | 33.6 | 35.7 | 56.6 | 40.8
306 | 216 | 529.4 | 168.1 | 202.1 | 164.8 | 60.8 | 50.7 | 33.7 | 35.9 | 56.8 | 41
307 | 217 | 529.5 | 168.8 | 203.1 | 165.5 | 60.9 | 50.8 | 33.9 | 36.1 | 57 | 41.2
308 | 218 | 529.6 | 169.5 | 204.1 | 166.2 | 61.1 | 51 | 34 | 36.2 | 57.2 | 41.3
309 | 219 | 529.6 | 170.3 | 205 | 167 | 61.3 | 51.2 | 34.2 | 36.4 | 57.4 | 41.5
310 | 220 | 529.7 | 171.1 | 205.9 | 167.7 | 61.5 | 51.3 | 34.3 | 36.5 | 57.5 | 41.7
311 | 221 | 529.7 | 171.7 | 206.9 | 168.4 | 61.6 | 51.5 | 34.5 | 36.7 | 57.7 | 41.9
312 | 222 | 529.8 | 172.5 | 207.8 | 169.2 | 61.9 | 51.7 | 34.6 | 36.8 | 58 | 42.1
313 | 223 | 529.7 | 173.1 | 208.8 | 169.8 | 61.9 | 51.8 | 34.8 | 36.9 | 58.3 | 42.3
314 | 224 | 529.7 | 173.9 | 209.7 | 170.7 | 62.1 | 52 | 34.9 | 37 | 58.5 | 42.4
315 | 225 | 529.7 | 174.7 | 210.6 | 171.4 | 62.3 | 52.1 | 35 | 37.1 | 58.7 | 42.6
316 | 226 | 529.7 | 175.5 | 211.3 | 172.1 | 62.6 | 52.4 | 35.2 | 37.2 | 59 | 42.8
317 | 227 | 529.7 | 176.1 | 212.3 | 172.8 | 62.7 | 52.5 | 35.3 | 37.4 | 59.2 | 43
318 | 228 | 529.8 | 176.7 | 213.4 | 173.4 | 62.7 | 52.6 | 35.5 | 37.5 | 59.5 | 43.2
319 | 229 | 529.8 | 177.5 | 214.3 | 174.2 | 62.9 | 52.7 | 35.6 | 37.7 | 59.8 | 43.3
320 | 230 | 529.8 | 178.2 | 215.2 | 174.9 | 63 | 52.9 | 35.8 | 37.8 | 60.2 | 43.5
321 | 231 | 529.8 | 178.9 | 216.1 | 175.6 | 63.2 | 53.1 | 35.9 | 37.9 | 60.5 | 43.7
322 | 232 | 529.8 | 179.7 | 216.9 | 176.4 | 63.5 | 53.3 | 36.1 | 38.1 | 60.9 | 43.9
323 | 233 | 529.8 | 180.5 | 217.7 | 177.2 | 63.8 | 53.5 | 36.2 | 38.2 | 61.3 | 44
324 | 234 | 529.7 | 181.2 | 218.5 | 177.9 | 64 | 53.7 | 36.3 | 38.4 | 61.6 | 44.2
325 | 235 | 529.7 | 182 | 219.3 | 178.6 | 64.3 | 53.9 | 36.5 | 38.5 | 62 | 44.4
326 | 236 | 529.7 | 182.7 | 220.2 | 179.3 | 64.5 | 54.1 | 36.7 | 38.7 | 62.3 | 44.5
327 | 237 | 529.7 | 183.4 | 221.1 | 180 | 64.7 | 54.4 | 36.8 | 38.9 | 62.7 | 44.7
328 | 238 | 529.7 | 184.1 | 221.9 | 180.8 | 65 | 54.6 | 36.9 | 39 | 63 | 44.8
329 | 239 | 529.7 | 184.9 | 222.6 | 181.6 | 65.2 | 54.8 | 37.1 | 39.2 | 63.3 | 45
330 | 240 | 529.7 | 185.6 | 223.6 | 182.2 | 65.4 | 55 | 37.3 | 39.4 | 63.5 | 45.2
331 | 241 | 529.8 | 186.2 | 224.5 | 182.9 | 65.6 | 55.3 | 37.4 | 39.5 | 63.8 | 45.3
332 | 242 | 529.7 | 187 | 225.2 | 183.7 | 65.9 | 55.5 | 37.6 | 39.8 | 64.1 | 45.5
333 | 243 | 529.7 | 187.6 | 226.3 | 184.4 | 66.2 | 55.8 | 37.7 | 39.9 | 64.4 | 45.6
334 | 244 | 529.7 | 188.3 | 227.3 | 185 | 66.4 | 56 | 37.9 | 40.1 | 64.6 | 45.8
335 | 245 | 529.8 | 189 | 228.2 | 185.7 | 66.7 | 56.3 | 38 | 40.4 | 64.9 | 45.9
336 | 246 | 529.8 | 189.7 | 229.1 | 186.4 | 67 | 56.6 | 38.2 | 40.6 | 65.2 | 46.1
337 | 247 | 529.7 | 190.4 | 229.9 | 187.1 | 67.4 | 56.9 | 38.3 | 40.7 | 65.4 | 46.2
338 | 248 | 529.7 | 191.1 | 230.7 | 187.8 | 67.7 | 57.2 | 38.5 | 40.9 | 65.7 | 46.4
339 | 249 | 529.6 | 191.8 | 231.5 | 188.6 | 68 | 57.5 | 38.6 | 41 | 66 | 46.5
340 | 250 | 529.6 | 192.6 | 232.3 | 189.3 | 68.4 | 57.8 | 38.8 | 41.2 | 66.2 | 46.7
341 | 251 | 529.5 | 193.3 | 233.1 | 189.9 | 68.8 | 58.2 | 39 | 41.4 | 66.5 | 46.8
342 | 252 | 529.5 | 194 | 233.9 | 190.7 | 69.2 | 58.5 | 39.1 | 41.6 | 66.8 | 46.9
343 | 253 | 529.4 | 194.7 | 234.6 | 191.5 | 69.7 | 58.9 | 39.2 | 41.7 | 67.1 | 47.1
344 | 254 | 529.4 | 195.4 | 235.4 | 192.2 | 70.1 | 59.2 | 39.4 | 41.9 | 67.4 | 47.2
345 | 255 | 529.4 | 196.1 | 236.2 | 192.9 | 70.5 | 59.6 | 39.6 | 42.1 | 67.8 | 47.3
346 | 256 | 529.4 | 196.9 | 237.1 | 193.6 | 70.9 | 59.9 | 39.7 | 42.3 | 68.1 | 47.5
347 | 257 | 529.4 | 197.5 | 237.9 | 194.3 | 71.3 | 60.3 | 39.9 | 42.5 | 68.4 | 47.6
348 | 258 | 529.4 | 198.2 | 238.9 | 195 | 71.6 | 60.6 | 40 | 42.6 | 68.8 | 47.8
349 | 259 | 529.5 | 198.8 | 239.8 | 195.6 | 71.9 | 60.9 | 40.2 | 42.8 | 69.1 | 47.9
350 | 260 | 529.5 | 199.5 | 240.5 | 196.3 | 72.3 | 61.2 | 40.4 | 42.9 | 69.4 | 48.1
351 | 261 | 529.5 | 200.2 | 241.4 | 197 | 72.7 | 61.6 | 40.5 | 43.1 | 69.8 | 48.2
352 | 262 | 529.5 | 200.8 | 242.3 | 197.7 | 73.1 | 61.9 | 40.7 | 43.2 | 70.1 | 48.4
353 | 263 | 529.5 | 201.5 | 243.1 | 198.4 | 73.4 | 62.3 | 40.9 | 43.4 | 70.5 | 48.6
354 | 264 | 529.5 | 202.2 | 243.8 | 199 | 73.8 | 62.6 | 41 | 43.6 | 70.8 | 48.7
355 | 265 | 529.5 | 202.9 | 244.6 | 199.7 | 74.2 | 63 | 41.2 | 43.8 | 71.1 | 48.9
356 | 266 | 529.5 | 203.5 | 245.4 | 200.4 | 74.7 | 63.3 | 41.4 | 44 | 71.4 | 49
357 | 267 | 529.5 | 204.2 | 246.1 | 201.1 | 75.1 | 63.7 | 41.5 | 44.2 | 71.8 | 49.2
358 | 268 | 529.4 | 204.9 | 246.9 | 201.7 | 75.5 | 64 | 41.7 | 44.3 | 72.2 | 49.4
359 | 269 | 529.4 | 205.5 | 247.8 | 202.5 | 75.9 | 64.4 | 41.9 | 44.5 | 72.5 | 49.6
360 | 270 | 529.3 | 206.2 | 248.7 | 203.1 | 76.3 | 64.7 | 42 | 44.7 | 72.9 | 49.8
361 | 271 | 529.3 | 206.9 | 249.4 | 203.8 | 76.7 | 65.1 | 42.2 | 44.9 | 73.2 | 50
362 | 272 | 529.3 | 207.6 | 250.2 | 204.4 | 77.2 | 65.4 | 42.4 | 45.1 | 73.6 | 50.3
363 | 273 | 529.3 | 208.3 | 250.9 | 205.1 | 77.6 | 65.8 | 42.5 | 45.3 | 74 | 50.4
364 | 274 | 529.2 | 208.9 | 251.6 | 205.8 | 78 | 66.2 | 42.7 | 45.4 | 74.4 | 50.6
365 | 275 | 529.2 | 209.5 | 252.6 | 206.5 | 78.4 | 66.5 | 42.9 | 45.6 | 74.7 | 50.8
366 | 276 | 529.2 | 210.2 | 253.3 | 207.1 | 78.9 | 66.9 | 43 | 45.8 | 75.1 | 51.1
367 | 277 | 529.1 | 210.9 | 254 | 207.8 | 79.4 | 67.2 | 43.2 | 45.9 | 75.5 | 51.3
368 | 278 | 529.1 | 211.6 | 254.8 | 208.4 | 79.7 | 67.6 | 43.4 | 46.1 | 75.9 | 51.5
369 | 279 | 529 | 212.2 | 255.7 | 209.1 | 80.2 | 67.9 | 43.6 | 46.2 | 76.3 | 51.7
370 | 280 | 528.9 | 212.9 | 256.4 | 209.8 | 80.6 | 68.3 | 43.7 | 46.3 | 76.7 | 51.9
371 | 281 | 528.9 | 213.6 | 257.1 | 210.5 | 81.1 | 68.7 | 43.9 | 46.5 | 77.1 | 52.1
372 | 282 | 528.9 | 214.2 | 257.9 | 211.1 | 81.5 | 69 | 44.1 | 46.8 | 77.5 | 52.4
373 | 283 | 528.9 | 214.8 | 258.8 | 211.7 | 81.9 | 69.3 | 44.3 | 47 | 77.9 | 52.6
374 | 284 | 528.9 | 215.5 | 259.5 | 212.4 | 82.3 | 69.7 | 44.5 | 47.2 | 78.4 | 52.9
375 | 285 | 528.8 | 216.2 | 260.4 | 213.1 | 82.7 | 70.1 | 44.6 | 47.4 | 78.8 | 53.2
376 | 286 | 528.8 | 216.8 | 261.2 | 213.7 | 83.1 | 70.4 | 44.8 | 47.5 | 79.2 | 53.5
377 | 287 | 528.8 | 217.5 | 261.9 | 214.4 | 83.6 | 70.8 | 45 | 47.8 | 79.6 | 53.7
378 | 288 | 528.8 | 218.1 | 262.6 | 215.1 | 84 | 71.1 | 45.2 | 48 | 80.1 | 54
379 | 289 | 528.8 | 218.8 | 263.3 | 215.7 | 84.5 | 71.5 | 45.4 | 48.2 | 80.5 | 54.3
380 | 290 | 528.8 | 219.4 | 264.1 | 216.3 | 84.8 | 71.8 | 45.5 | 48.4 | 80.9 | 54.6
381 | 291 | 528.8 | 220 | 264.9 | 216.9 | 85.3 | 72.2 | 45.7 | 48.6 | 81.4 | 54.8
382 | 292 | 528.8 | 220.7 | 265.6 | 217.6 | 85.7 | 72.5 | 45.9 | 48.8 | 81.9 | 55.1
383 | 293 | 528.9 | 221.3 | 266.4 | 218.3 | 86.2 | 72.9 | 46.1 | 49 | 82.4 | 55.3
384 | 294 | 528.9 | 222 | 267.1 | 218.9 | 86.6 | 73.3 | 46.3 | 49.2 | 82.9 | 55.6
385 | 295 | 528.8 | 222.6 | 267.8 | 219.6 | 87.1 | 73.7 | 46.5 | 49.3 | 83.4 | 55.8
386 | 296 | 528.8 | 223.2 | 268.6 | 220.2 | 87.5 | 74 | 46.7 | 49.5 | 83.9 | 56.1
387 | 297 | 528.8 | 223.9 | 269.2 | 220.9 | 88 | 74.4 | 46.9 | 49.7 | 84.3 | 56.4
388 | 298 | 528.8 | 224.6 | 269.9 | 221.6 | 88.5 | 74.8 | 47 | 49.9 | 84.9 | 56.6
389 | 299 | 528.9 | 225.3 | 270.5 | 222.2 | 88.9 | 75.2 | 47.2 | 50.1 | 85.4 | 56.9
390 | 300 | 528.9 | 225.9 | 271.2 | 222.9 | 89.4 | 75.5 | 47.4 | 50.2 | 85.9 | 57.1
391 | 301 | 528.9 | 226.5 | 272 | 223.5 | 89.9 | 75.9 | 47.6 | 50.4 | 86.4 | 57.4
392 | 302 | 528.9 | 227.2 | 272.7 | 224.2 | 90.4 | 76.3 | 47.8 | 50.7 | 86.8 | 57.6
393 | 303 | 529 | 227.8 | 273.4 | 224.8 | 90.8 | 76.6 | 48 | 50.8 | 87.3 | 57.9
394 | 304 | 529.1 | 228.4 | 274.3 | 225.4 | 91.2 | 77 | 48.2 | 51 | 87.8 | 58.2
395 | 305 | 529.1 | 229 | 275.3 | 226 | 91.6 | 77.3 | 48.4 | 51.2 | 88.3 | 58.5
396 | 306 | 529.2 | 229.6 | 275.9 | 226.6 | 92 | 77.7 | 48.6 | 51.4 | 88.8 | 58.8
397 | 307 | 529.2 | 230.2 | 276.7 | 227.2 | 92.4 | 78 | 48.8 | 51.5 | 89.3 | 59.1
398 | 308 | 529.2 | 230.8 | 277.4 | 227.8 | 92.8 | 78.4 | 49 | 51.7 | 89.8 | 59.3
399 | 309 | 529.3 | 231.4 | 278.1 | 228.5 | 93.3 | 78.8 | 49.2 | 52 | 90.3 | 59.6
400 | 310 | 529.3 | 232.1 | 278.8 | 229.1 | 93.8 | 79.1 | 49.4 | 52.2 | 90.7 | 59.9
401 | 311 | 529.2 | 232.7 | 279.5 | 229.7 | 94.1 | 79.4 | 49.7 | 52.4 | 91.2 | 60.2
402 | 312 | 529.3 | 233.3 | 280.1 | 230.3 | 94.6 | 79.8 | 49.9 | 52.7 | 91.7 | 60.5
403 | 313 | 529.3 | 233.9 | 280.9 | 230.9 | 95.1 | 80.2 | 50.1 | 52.9 | 92.2 | 60.8
404 | 314 | 529.3 | 234.5 | 281.6 | 231.6 | 95.5 | 80.5 | 50.3 | 53.1 | 92.7 | 61
405 | 315 | 529.3 | 235.1 | 282.3 | 232.2 | 95.9 | 80.9 | 50.5 | 53.3 | 93.1 | 61.3
406 | 316 | 529.3 | 235.7 | 283 | 232.8 | 96.4 | 81.3 | 50.7 | 53.6 | 93.6 | 61.6
407 | 317 | 529.3 | 236.3 | 283.7 | 233.4 | 96.8 | 81.6 | 50.9 | 53.8 | 94.1 | 61.9
408 | 318 | 529.3 | 236.9 | 284.4 | 234 | 97.3 | 82 | 51.2 | 54.1 | 94.6 | 62.2
409 | 319 | 529.3 | 237.6 | 285 | 234.6 | 97.8 | 82.4 | 51.4 | 54.3 | 95.1 | 62.4
410 | 320 | 529.2 | 238.2 | 285.6 | 235.2 | 98.2 | 82.8 | 51.6 | 54.5 | 95.6 | 62.7
411 | 321 | 529.2 | 238.8 | 286.3 | 235.8 | 98.7 | 83.1 | 51.8 | 54.7 | 96.1 | 63
412 | 322 | 529.1 | 239.4 | 287 | 236.5 | 99.2 | 83.5 | 52 | 54.9 | 96.6 | 63.2
413 | 323 | 529.1 | 240.1 | 287.6 | 237.1 | 99.7 | 83.9 | 52.3 | 55.1 | 97.1 | 63.5
414 | 324 | 529.1 | 240.6 | 288.3 | 237.7 | 100.1 | 84.3 | 52.5 | 55.3 | 97.6 | 63.7
415 | 325 | 529.1 | 241.2 | 289 | 238.2 | 100.6 | 84.6 | 52.7 | 55.5 | 98 | 64
416 | 326 | 529.1 | 241.8 | 289.6 | 238.8 | 101.1 | 85 | 52.9 | 55.7 | 98.5 | 64.3
417 | 327 | 529.1 | 242.4 | 290.3 | 239.5 | 101.5 | 85.4 | 53.2 | 55.9 | 99 | 64.6
418 | 328 | 529.1 | 243 | 291 | 240.1 | 102 | 85.8 | 53.4 | 56.1 | 99.4 | 64.9
419 | 329 | 529.1 | 243.6 | 291.7 | 240.7 | 102.4 | 86.2 | 53.6 | 56.4 | 99.9 | 65.2
420 | 330 | 529.1 | 244.2 | 292.3 | 241.3 | 102.9 | 86.6 | 53.9 | 56.7 | 100.4 | 65.5
421 | 331 | 529 | 244.8 | 292.9 | 241.8 | 103.4 | 87 | 54.1 | 56.9 | 100.8 | 65.8
422 | 332 | 529 | 245.4 | 293.7 | 242.4 | 103.8 | 87.3 | 54.3 | 57.1 | 101.3 | 66.1
423 | 333 | 528.9 | 246 | 294.3 | 243 | 104.3 | 87.7 | 54.6 | 57.3 | 101.7 | 66.4
424 | 334 | 528.9 | 246.6 | 295 | 243.6 | 104.8 | 88.1 | 54.8 | 57.6 | 102.2 | 66.7
425 | 335 | 528.9 | 247.1 | 295.6 | 244.2 | 105.2 | 88.4 | 55 | 57.8 | 102.7 | 67
426 | 336 | 528.9 | 247.8 | 296.2 | 244.7 | 105.7 | 88.8 | 55.3 | 58.1 | 103.2 | 67.2
427 | 337 | 528.9 | 248.4 | 296.9 | 245.3 | 106.2 | 89.2 | 55.5 | 58.3 | 103.6 | 67.5
428 | 338 | 528.9 | 248.9 | 297.5 | 245.9 | 106.6 | 89.6 | 55.8 | 58.5 | 104.1 | 67.8
429 | 339 | 528.8 | 249.5 | 298.2 | 246.5 | 107 | 90 | 56 | 58.8 | 104.6 | 68
430 | 340 | 528.8 | 250.1 | 298.8 | 247.1 | 107.5 | 90.4 | 56.3 | 59 | 105.1 | 68.3
431 | 341 | 528.8 | 250.7 | 299.5 | 247.7 | 108 | 90.8 | 56.5 | 59.2 | 105.5 | 68.6
432 | 342 | 528.8 | 251.2 | 300.1 | 248.3 | 108.4 | 91.2 | 56.7 | 59.5 | 106 | 68.9
433 | 343 | 528.8 | 251.8 | 300.8 | 248.8 | 108.9 | 91.5 | 57 | 59.7 | 106.5 | 69.2
434 | 344 | 528.8 | 252.4 | 301.4 | 249.4 | 109.4 | 91.9 | 57.2 | 59.9 | 107 | 69.5
435 | 345 | 528.8 | 252.9 | 302.1 | 250 | 109.8 | 92.3 | 57.5 | 60.1 | 107.5 | 69.7
436 | 346 | 528.8 | 253.5 | 302.8 | 250.7 | 110.2 | 92.7 | 57.8 | 60.3 | 107.9 | 70
437 | 347 | 528.8 | 254.1 | 303.3 | 251.2 | 110.8 | 93.1 | 58 | 60.6 | 108.4 | 70.4
438 | 348 | 528.7 | 254.7 | 303.9 | 251.7 | 111.2 | 93.5 | 58.3 | 60.9 | 108.8 | 70.7
439 | 349 | 528.7 | 255.2 | 304.6 | 252.2 | 111.7 | 93.8 | 58.5 | 61.1 | 109.3 | 71
440 | 350 | 528.7 | 255.8 | 305.2 | 252.9 | 112.1 | 94.2 | 58.8 | 61.4 | 109.8 | 71.2
441 | 351 | 528.7 | 256.3 | 305.9 | 253.4 | 112.6 | 94.6 | 59 | 61.6 | 110.2 | 71.5
442 | 352 | 528.7 | 256.9 | 306.5 | 253.9 | 113.1 | 95 | 59.3 | 61.9 | 110.7 | 71.8
443 | 353 | 528.6 | 257.4 | 307.2 | 254.5 | 113.5 | 95.4 | 59.5 | 62.2 | 111.2 | 72.1
444 | 354 | 528.6 | 258 | 307.8 | 255 | 114 | 95.8 | 59.8 | 62.4 | 111.7 | 72.4
445 | 355 | 528.6 | 258.6 | 308.4 | 255.6 | 114.5 | 96.2 | 60 | 62.6 | 112.2 | 72.6
446 | 356 | 528.6 | 259.1 | 309 | 256.2 | 114.9 | 96.5 | 60.3 | 62.8 | 112.6 | 72.9
447 | 357 | 528.5 | 259.6 | 309.6 | 256.7 | 115.4 | 96.9 | 60.6 | 63 | 113.1 | 73.3
448 | 358 | 528.5 | 260.2 | 310.2 | 257.3 | 115.9 | 97.4 | 60.8 | 63.2 | 113.5 | 73.6
449 | 359 | 528.5 | 260.8 | 310.8 | 257.8 | 116.3 | 97.7 | 61.1 | 63.5 | 114 | 73.9
450 | 360 | 528.5 | 261.3 | 311.5 | 258.4 | 116.8 | 98.1 | 61.4 | 63.7 | 114.5 | 74.2
451 | 361 | 528.5 | 261.8 | 312 | 258.9 | 117.3 | 98.5 | 61.6 | 64 | 114.9 | 74.5
452 | 362 | 528.5 | 262.4 | 312.6 | 259.4 | 117.7 | 98.9 | 61.9 | 64.3 | 115.4 | 74.8
453 | 363 | 528.5 | 262.9 | 313.2 | 260 | 118.2 | 99.3 | 62.2 | 64.6 | 115.8 | 75.1
454 | 364 | 528.6 | 263.4 | 314 | 260.5 | 118.6 | 99.6 | 62.4 | 64.8 | 116.3 | 75.4
455 | 365 | 528.6 | 264 | 314.5 | 261.1 | 119.1 | 100 | 62.7 | 65.1 | 116.8 | 75.6
456 | 366 | 528.6 | 264.5 | 315.2 | 261.6 | 119.5 | 100.4 | 63 | 65.3 | 117.2 | 75.9
457 | 367 | 528.6 | 265 | 315.8 | 262.1 | 120 | 100.8 | 63.2 | 65.6 | 117.7 | 76.2
458 | 368 | 528.6 | 265.6 | 316.2 | 262.7 | 120.5 | 101.2 | 63.5 | 65.8 | 118.2 | 76.6
459 | 369 | 528.6 | 266.2 | 316.8 | 263.2 | 121 | 101.6 | 63.8 | 66 | 118.6 | 76.8
460 | 370 | 528.6 | 266.7 | 317.4 | 263.7 | 121.4 | 102 | 64 | 66.3 | 119.1 | 77.2
461 | 371 | 528.6 | 267.2 | 318 | 264.3 | 122 | 102.4 | 64.3 | 66.5 | 119.6 | 77.5
462 | 372 | 528.6 | 267.8 | 318.6 | 264.8 | 122.4 | 102.8 | 64.6 | 66.7 | 120 | 77.8
463 | 373 | 528.6 | 268.3 | 319.2 | 265.4 | 122.9 | 103.2 | 64.9 | 66.9 | 120.5 | 78.1
464 | 374 | 528.5 | 268.8 | 319.8 | 265.9 | 123.4 | 103.6 | 65.1 | 67.1 | 121 | 78.4
465 | 375 | 528.5 | 269.3 | 320.3 | 266.4 | 123.8 | 104 | 65.4 | 67.4 | 121.4 | 78.7
466 | 376 | 528.5 | 269.9 | 320.8 | 267 | 124.3 | 104.4 | 65.7 | 67.6 | 121.9 | 79
467 | 377 | 528.5 | 270.4 | 321.4 | 267.5 | 124.8 | 104.8 | 66 | 67.9 | 122.3 | 79.3
468 | 378 | 528.5 | 270.9 | 322 | 268.1 | 125.2 | 105.1 | 66.2 | 68.2 | 122.8 | 79.6
469 | 379 | 528.4 | 271.4 | 322.6 | 268.6 | 125.7 | 105.5 | 66.5 | 68.4 | 123.3 | 79.9
470 | 380 | 528.4 | 272 | 323.2 | 269.1 | 126.2 | 105.9 | 66.8 | 68.7 | 123.7 | 80.2
471 | 381 | 528.4 | 272.5 | 323.8 | 269.6 | 126.6 | 106.3 | 67.1 | 68.9 | 124.2 | 80.5
472 | 382 | 528.4 | 273 | 324.3 | 270.1 | 127.1 | 106.7 | 67.4 | 69.2 | 124.7 | 80.8
473 | 383 | 528.4 | 273.5 | 324.9 | 270.6 | 127.6 | 107.1 | 67.6 | 69.5 | 125.1 | 81.1
474 | 384 | 528.4 | 274 | 325.4 | 271.2 | 128 | 107.5 | 67.9 | 69.7 | 125.6 | 81.4
475 | 385 | 528.5 | 274.6 | 326 | 271.7 | 128.5 | 107.9 | 68.2 | 69.9 | 126.1 | 81.7
476 | 386 | 528.5 | 275.1 | 326.6 | 272.3 | 129 | 108.2 | 68.5 | 70.2 | 126.5 | 82
477 | 387 | 528.5 | 275.6 | 327.2 | 272.8 | 129.4 | 108.6 | 68.8 | 70.4 | 127 | 82.3
478 | 388 | 528.5 | 276.1 | 327.7 | 273.3 | 129.9 | 109 | 69 | 70.7 | 127.5 | 82.6
479 | 389 | 528.5 | 276.6 | 328.3 | 273.8 | 130.4 | 109.4 | 69.3 | 71 | 127.9 | 82.9
480 | 390 | 528.5 | 277.1 | 328.9 | 274.3 | 130.8 | 109.8 | 69.6 | 71.3 | 128.4 | 83.2
481 | 391 | 528.6 | 277.6 | 329.4 | 274.8 | 131.3 | 110.1 | 69.9 | 71.7 | 128.9 | 83.5
482 | 392 | 528.6 | 278.1 | 330.1 | 275.2 | 131.7 | 110.5 | 70.2 | 72 | 129.4 | 83.8
483 | 393 | 528.6 | 278.6 | 330.6 | 275.8 | 132.2 | 110.9 | 70.5 | 72.2 | 129.8 | 84.1
484 | 394 | 528.6 | 279.1 | 331.1 | 276.3 | 132.7 | 111.3 | 70.7 | 72.5 | 130.3 | 84.4
485 | 395 | 528.7 | 279.6 | 331.8 | 276.8 | 133.1 | 111.6 | 71 | 72.8 | 130.8 | 84.7
486 | 396 | 528.6 | 280.1 | 332.3 | 277.4 | 133.6 | 112 | 71.3 | 73.1 | 131.2 | 85
487 | 397 | 528.6 | 280.6 | 333 | 277.9 | 134.1 | 112.4 | 71.6 | 73.3 | 131.7 | 85.3
488 | 398 | 528.6 | 281.1 | 333.5 | 278.3 | 134.5 | 112.8 | 71.9 | 73.5 | 132.1 | 85.6
489 | 399 | 528.6 | 281.6 | 334 | 278.9 | 135 | 113.1 | 72.2 | 73.7 | 132.6 | 85.9
490 | 400 | 528.6 | 282.1 | 334.4 | 279.4 | 135.6 | 113.6 | 72.5 | 73.9 | 133.1 | 86.2
491 | 401 | 528.6 | 282.6 | 334.9 | 279.9 | 136 | 113.9 | 72.8 | 74.2 | 133.5 | 86.5
492 | 402 | 528.6 | 283.1 | 335.5 | 280.4 | 136.5 | 114.3 | 73.1 | 74.5 | 134 | 86.8
493 | 403 | 528.6 | 283.6 | 335.9 | 280.9 | 137 | 114.7 | 73.3 | 74.7 | 134.4 | 87.2
494 | 404 | 528.6 | 284.1 | 336.5 | 281.4 | 137.5 | 115.1 | 73.6 | 75 | 134.9 | 87.5
495 | 405 | 528.6 | 284.6 | 337 | 281.9 | 137.9 | 115.4 | 73.9 | 75.2 | 135.4 | 87.8
496 | 406 | 528.6 | 285.1 | 337.6 | 282.3 | 138.4 | 115.8 | 74.2 | 75.4 | 135.8 | 88.1
497 | 407 | 528.6 | 285.6 | 338.1 | 282.9 | 138.9 | 116.1 | 74.5 | 75.7 | 136.3 | 88.4
498 | 408 | 528.5 | 286.1 | 338.7 | 283.4 | 139.4 | 116.5 | 74.8 | 75.9 | 136.7 | 88.7
499 | 409 | 528.5 | 286.5 | 339.2 | 283.8 | 139.8 | 116.9 | 75.1 | 76.1 | 137.2 | 89.1
500 | 410 | 528.5 | 287 | 339.7 | 284.3 | 140.3 | 117.2 | 75.4 | 76.4 | 137.6 | 89.4
501 | 411 | 528.5 | 287.5 | 340.2 | 284.8 | 140.8 | 117.6 | 75.7 | 76.7 | 138 | 89.7
502 | 412 | 528.4 | 288 | 340.8 | 285.3 | 141.3 | 117.9 | 75.9 | 76.9 | 138.4 | 90.1
503 | 413 | 528.4 | 288.5 | 341.2 | 285.8 | 141.8 | 118.3 | 76.2 | 77.2 | 138.9 | 90.4
504 | 414 | 528.3 | 289 | 341.7 | 286.3 | 142.3 | 118.7 | 76.5 | 77.5 | 139.3 | 90.8
505 | 415 | 528.3 | 289.5 | 342.2 | 286.7 | 142.7 | 119 | 76.8 | 77.7 | 139.8 | 91.1
506 | 416 | 528.3 | 289.9 | 342.8 | 287.2 | 143.2 | 119.3 | 77.1 | 78 | 140.2 | 91.4
507 | 417 | 528.3 | 290.4 | 343.3 | 287.7 | 143.7 | 119.7 | 77.4 | 78.3 | 140.7 | 91.7
508 | 418 | 528.3 | 290.9 | 343.8 | 288.1 | 144.1 | 120 | 77.7 | 78.5 | 141.1 | 92.1
509 | 419 | 528.3 | 291.4 | 344.3 | 288.6 | 144.5 | 120.4 | 78 | 78.7 | 141.6 | 92.4
510 | 420 | 528.3 | 291.9 | 344.8 | 289.1 | 145 | 120.7 | 78.3 | 79 | 142 | 92.7
511 | 421 | 528.2 | 292.4 | 345.2 | 289.6 | 145.6 | 121.1 | 78.6 | 79.2 | 142.5 | 93.1
512 | 422 | 528.2 | 292.8 | 345.7 | 290.1 | 146 | 121.4 | 78.9 | 79.5 | 142.9 | 93.4
513 | 423 | 528.2 | 293.3 | 346.3 | 290.5 | 146.5 | 121.7 | 79.2 | 79.8 | 143.3 | 93.7
514 | 424 | 528.2 | 293.8 | 346.7 | 291 | 147 | 122 | 79.4 | 80.1 | 143.8 | 94
515 | 425 | 528.1 | 294.3 | 347.2 | 291.5 | 147.4 | 122.4 | 79.7 | 80.3 | 144.2 | 94.4
516 | 426 | 528.1 | 294.7 | 347.7 | 292 | 147.9 | 122.7 | 80 | 80.6 | 144.7 | 94.7
517 | 427 | 528.1 | 295.2 | 348.2 | 292.4 | 148.4 | 123 | 80.3 | 80.9 | 145.1 | 95
518 | 428 | 528.1 | 295.6 | 348.7 | 292.8 | 148.8 | 123.3 | 80.6 | 81.1 | 145.6 | 95.3
519 | 429 | 528.1 | 296.1 | 349.1 | 293.4 | 149.3 | 123.6 | 80.9 | 81.3 | 146.1 | 95.7
520 | 430 | 528.1 | 296.6 | 349.6 | 293.8 | 149.8 | 123.9 | 81.2 | 81.6 | 146.5 | 96
521 | 431 | 528 | 297.1 | 350 | 294.3 | 150.3 | 124.2 | 81.5 | 81.9 | 147 | 96.3
522 | 432 | 528 | 297.5 | 350.6 | 294.7 | 150.8 | 124.5 | 81.8 | 82.1 | 147.4 | 96.6
523 | 433 | 528 | 298 | 351.1 | 295.2 | 151.3 | 124.8 | 82.1 | 82.4 | 147.9 | 96.9
524 | 434 | 528 | 298.5 | 351.6 | 295.7 | 151.8 | 125.1 | 82.4 | 82.6 | 148.3 | 97.2
525 | 435 | 528 | 298.9 | 352 | 296.1 | 152.3 | 125.4 | 82.7 | 82.8 | 148.8 | 97.5
526 | 436 | 528 | 299.4 | 352.5 | 296.6 | 152.8 | 125.7 | 82.9 | 83.1 | 149.3 | 97.9
527 | 437 | 528 | 299.8 | 353 | 297 | 153.2 | 126 | 83.2 | 83.3 | 149.8 | 98.1
528 | 438 | 528 | 300.3 | 353.4 | 297.5 | 153.7 | 126.3 | 83.5 | 83.6 | 150.2 | 98.5
529 | 439 | 528 | 300.8 | 353.9 | 297.9 | 154.3 | 126.6 | 83.8 | 83.8 | 150.7 | 98.8
530 | 440 | 528 | 301.2 | 354.3 | 298.4 | 154.7 | 126.9 | 84.1 | 84 | 151.1 | 99.1
531 | 441 | 528 | 301.6 | 354.8 | 298.8 | 155.2 | 127.2 | 84.4 | 84.3 | 151.6 | 99.4
532 | 442 | 528 | 302.1 | 355.3 | 299.3 | 155.8 | 127.5 | 84.7 | 84.5 | 152.1 | 99.7
533 | 443 | 528.1 | 302.6 | 355.7 | 299.7 | 156.3 | 127.8 | 85 | 84.6 | 152.5 | 100
534 | 444 | 528.1 | 303 | 356.3 | 300.2 | 156.7 | 128.1 | 85.3 | 84.9 | 153 | 100.3
535 | 445 | 528 | 303.5 | 356.7 | 300.7 | 157.3 | 128.4 | 85.6 | 85.2 | 153.4 | 100.6
536 | 446 | 528 | 303.9 | 357.1 | 301.1 | 157.8 | 128.7 | 85.9 | 85.4 | 153.9 | 101
537 | 447 | 528 | 304.3 | 357.6 | 301.6 | 158.3 | 129 | 86.1 | 85.6 | 154.3 | 101.3
538 | 448 | 528 | 304.8 | 358.1 | 302 | 158.8 | 129.3 | 86.4 | 85.8 | 154.8 | 101.7
539 | 449 | 528 | 305.2 | 358.5 | 302.4 | 159.3 | 129.5 | 86.7 | 86.1 | 155.2 | 102
540 | 450 | 528.1 | 305.7 | 359 | 302.9 | 159.8 | 129.9 | 87 | 86.4 | 155.7 | 102.3
541 | 451 | 528.1 | 306.1 | 359.4 | 303.3 | 160.4 | 130.2 | 87.3 | 86.6 | 156.1 | 102.7
542 | 452 | 528.1 | 306.6 | 359.8 | 303.8 | 160.9 | 130.5 | 87.6 | 86.8 | 156.5 | 103
543 | 453 | 528 | 307 | 360.2 | 304.2 | 161.4 | 130.8 | 87.9 | 87.1 | 157 | 103.4
544 | 454 | 528.1 | 307.5 | 360.7 | 304.7 | 161.9 | 131.1 | 88.2 | 87.4 | 157.4 | 103.8
545 | 455 | 528.1 | 307.9 | 361.2 | 305.1 | 162.4 | 131.3 | 88.4 | 87.6 | 157.8 | 104.1
546 | 456 | 528.1 | 308.3 | 361.7 | 305.5 | 162.9 | 131.7 | 88.7 | 87.9 | 158.3 | 104.5
547 | 457 | 528.1 | 308.7 | 362.1 | 305.9 | 163.4 | 132 | 89 | 88.1 | 158.7 | 104.8
548 | 458 | 528.1 | 309.2 | 362.6 | 306.3 | 163.8 | 132.3 | 89.3 | 88.4 | 159.2 | 105.1
549 | 459 | 528.1 | 309.6 | 363 | 306.8 | 164.3 | 132.6 | 89.6 | 88.6 | 159.7 | 105.5
550 | 460 | 528.1 | 310.1 | 363.4 | 307.2 | 164.9 | 132.9 | 89.9 | 88.8 | 160.1 | 105.8
551 | 461 | 528.1 | 310.5 | 363.9 | 307.6 | 165.4 | 133.2 | 90.2 | 89.1 | 160.6 | 106.1
552 | 462 | 528.1 | 310.9 | 364.3 | 308 | 165.9 | 133.5 | 90.4 | 89.3 | 161 | 106.4
553 | 463 | 528 | 311.4 | 364.7 | 308.5 | 166.3 | 133.9 | 90.7 | 89.5 | 161.5 | 106.7
554 | 464 | 528 | 311.8 | 365.1 | 308.9 | 166.8 | 134.2 | 91 | 89.8 | 161.9 | 107.1
555 | 465 | 527.9 | 312.2 | 365.6 | 309.4 | 167.3 | 134.5 | 91.3 | 90 | 162.3 | 107.4
556 | 466 | 527.9 | 312.7 | 366 | 309.8 | 167.8 | 134.9 | 91.6 | 90.3 | 162.8 | 107.8
557 | 467 | 527.9 | 313.1 | 366.4 | 310.2 | 168.3 | 135.2 | 91.9 | 90.5 | 163.2 | 108.1
558 | 468 | 527.9 | 313.5 | 366.8 | 310.6 | 168.7 | 135.5 | 92.1 | 90.8 | 163.7 | 108.5
559 | 469 | 527.9 | 313.9 | 367.3 | 311 | 169.2 | 135.9 | 92.4 | 91 | 164.1 | 108.8
560 | 470 | 527.9 | 314.4 | 367.7 | 311.5 | 169.7 | 136.2 | 92.7 | 91.2 | 164.5 | 109.2
561 | 471 | 527.8 | 314.8 | 368 | 311.9 | 170.2 | 136.6 | 93 | 91.5 | 165 | 109.5
562 | 472 | 527.8 | 315.2 | 368.5 | 312.3 | 170.7 | 136.9 | 93.3 | 91.7 | 165.4 | 109.8
563 | 473 | 527.8 | 315.6 | 368.8 | 312.8 | 171.2 | 137.2 | 93.6 | 91.9 | 165.9 | 110.1
564 | 474 | 527.8 | 316.1 | 369.2 | 313.2 | 171.6 | 137.6 | 93.9 | 92.1 | 166.4 | 110.4
565 | 475 | 527.8 | 316.5 | 369.6 | 313.6 | 172.1 | 137.9 | 94.1 | 92.3 | 166.8 | 110.7
566 | 476 | 527.8 | 316.9 | 370 | 314 | 172.6 | 138.3 | 94.4 | 92.6 | 167.3 | 111.1
567 | 477 | 527.8 | 317.3 | 370.5 | 314.4 | 173.1 | 138.6 | 94.7 | 92.8 | 167.7 | 111.4
568 | 478 | 527.8 | 317.7 | 370.8 | 314.8 | 173.5 | 139 | 95 | 93 | 168.1 | 111.8
569 | 479 | 527.9 | 318.1 | 371.3 | 315.2 | 174 | 139.3 | 95.3 | 93.3 | 168.5 | 112.1
570 | 480 | 527.9 | 318.6 | 371.7 | 315.6 | 174.4 | 139.6 | 95.6 | 93.5 | 169 | 112.5
571 | 481 | 527.9 | 318.9 | 372.1 | 316 | 174.9 | 140 | 95.8 | 93.7 | 169.4 | 112.8
572 | 482 | 527.8 | 319.3 | 372.5 | 316.5 | 175.4 | 140.3 | 96.1 | 94 | 169.9 | 113.1
573 | 483 | 527.8 | 319.8 | 372.9 | 316.9 | 175.8 | 140.7 | 96.4 | 94.2 | 170.3 | 113.5
574 | 484 | 527.8 | 320.2 | 373.3 | 317.3 | 176.3 | 141.1 | 96.7 | 94.5 | 170.7 | 113.9
575 | 485 | 527.9 | 320.6 | 373.6 | 317.7 | 176.8 | 141.4 | 97 | 94.7 | 171.2 | 114.2
576 | 486 | 527.9 | 321 | 374.2 | 318.1 | 177.2 | 141.8 | 97.3 | 94.9 | 171.6 | 114.5
577 | 487 | 527.9 | 321.4 | 374.4 | 318.5 | 177.7 | 142.2 | 97.5 | 95.1 | 172 | 114.9
578 | 488 | 528 | 321.8 | 374.8 | 318.9 | 178.2 | 142.5 | 97.8 | 95.3 | 172.5 | 115.2
579 | 489 | 528 | 322.2 | 375.3 | 319.3 | 178.6 | 142.9 | 98.1 | 95.5 | 172.9 | 115.6
580 | 490 | 528.1 | 322.6 | 375.7 | 319.7 | 179 | 143.2 | 98.4 | 95.7 | 173.3 | 115.9
581 | 491 | 528.1 | 323 | 376.1 | 320.1 | 179.5 | 143.6 | 98.7 | 95.9 | 173.8 | 116.3
582 | 492 | 528.1 | 323.4 | 376.5 | 320.4 | 179.9 | 144 | 99 | 96.1 | 174.2 | 116.6
583 | 493 | 528.2 | 323.8 | 377 | 320.8 | 180.3 | 144.3 | 99.3 | 96.3 | 174.6 | 117
584 | 494 | 528.2 | 324.2 | 377.4 | 321.2 | 180.8 | 144.7 | 99.6 | 96.5 | 175 | 117.4
585 | 495 | 528.2 | 324.6 | 377.8 | 321.6 | 181.2 | 145.1 | 99.9 | 96.8 | 175.5 | 117.7
586 | 496 | 528.3 | 325 | 378.2 | 322 | 181.7 | 145.5 | 100.2 | 97 | 175.9 | 118
587 | 497 | 528.3 | 325.3 | 378.6 | 322.4 | 182.1 | 145.9 | 100.5 | 97.3 | 176.4 | 118.4
588 | 498 | 528.3 | 325.8 | 378.9 | 322.8 | 182.6 | 146.3 | 100.7 | 97.5 | 176.8 | 118.7
589 | 499 | 528.3 | 326.1 | 379.3 | 323.2 | 183 | 146.7 | 101.1 | 97.7 | 177.3 | 119
590 | 500 | 528.3 | 326.5 | 379.7 | 323.6 | 183.4 | 147.1 | 101.3 | 97.9 | 177.7 | 119.3
591 | 501 | 528.3 | 326.9 | 380.1 | 324 | 183.9 | 147.5 | 101.6 | 98.1 | 178.1 | 119.7
592 | 502 | 528.2 | 327.3 | 380.5 | 324.3 | 184.3 | 147.9 | 101.9 | 98.3 | 178.6 | 120
593 | 503 | 528.2 | 327.7 | 380.8 | 324.8 | 184.8 | 148.3 | 102.2 | 98.4 | 179 | 120.3
594 | 504 | 528.2 | 328.1 | 381.2 | 325.1 | 185.2 | 148.7 | 102.6 | 98.7 | 179.4 | 120.7
595 | 505 | 528.1 | 328.5 | 381.5 | 325.5 | 185.7 | 149.1 | 102.9 | 98.9 | 179.9 | 121
596 | 506 | 528.1 | 328.9 | 381.9 | 325.9 | 186.1 | 149.5 | 103.2 | 99.1 | 180.3 | 121.4
597 | 507 | 528 | 329.2 | 382.2 | 326.2 | 186.5 | 149.9 | 103.5 | 99.3 | 180.7 | 121.7
598 | 508 | 528 | 329.6 | 382.6 | 326.6 | 187 | 150.3 | 103.8 | 99.5 | 181.1 | 122.1
599 | 509 | 527.9 | 330 | 383 | 327 | 187.4 | 150.7 | 104.1 | 99.7 | 181.6 | 122.5
600 | 510 | 527.9 | 330.4 | 383.3 | 327.4 | 187.9 | 151.1 | 104.5 | 99.9 | 182 | 122.8
601 | 511 | 527.9 | 330.8 | 383.6 | 327.8 | 188.3 | 151.5 | 104.8 | 100.2 | 182.4 | 123.2
602 | 512 | 527.9 | 331.2 | 384 | 328.1 | 188.8 | 152 | 105.1 | 100.4 | 182.8 | 123.5
603 | 513 | 527.8 | 331.6 | 384.3 | 328.5 | 189.2 | 152.4 | 105.5 | 100.7 | 183.2 | 123.9
604 | 514 | 527.8 | 331.9 | 384.7 | 328.9 | 189.6 | 152.8 | 105.8 | 100.9 | 183.7 | 124.2
605 | 515 | 527.8 | 332.3 | 385.1 | 329.3 | 190.1 | 153.2 | 106.1 | 101.1 | 184.1 | 124.5
606 | 516 | 527.8 | 332.7 | 385.4 | 329.6 | 190.4 | 153.6 | 106.5 | 101.3 | 184.6 | 124.9
607 | 517 | 527.8 | 333 | 385.8 | 330 | 190.9 | 154 | 106.9 | 101.6 | 185 | 125.2
608 | 518 | 527.8 | 333.4 | 386.2 | 330.4 | 191.3 | 154.4 | 107.2 | 101.8 | 185.4 | 125.5
609 | 519 | 527.8 | 333.8 | 386.5 | 330.7 | 191.7 | 154.8 | 107.6 | 102 | 185.9 | 125.9
610 | 520 | 527.8 | 334.2 | 386.8 | 331.1 | 192.2 | 155.2 | 107.9 | 102.3 | 186.3 | 126.2
611 | 521 | 527.8 | 334.5 | 387.2 | 331.4 | 192.6 | 155.6 | 108.3 | 102.6 | 186.7 | 126.5
612 | 522 | 527.8 | 334.9 | 387.5 | 331.8 | 193 | 156 | 108.7 | 102.9 | 187.1 | 126.9
613 | 523 | 527.8 | 335.2 | 387.9 | 332.2 | 193.4 | 156.4 | 109 | 103.1 | 187.6 | 127.2
614 | 524 | 527.9 | 335.6 | 388.3 | 332.5 | 193.8 | 156.8 | 109.4 | 103.4 | 188 | 127.6
615 | 525 | 527.9 | 336 | 388.6 | 332.9 | 194.3 | 157.2 | 109.8 | 103.7 | 188.4 | 127.9
616 | 526 | 527.9 | 336.3 | 388.9 | 333.2 | 194.7 | 157.6 | 110.1 | 104.1 | 188.8 | 128.3
617 | 527 | 527.8 | 336.7 | 389.3 | 333.6 | 195.2 | 158 | 110.5 | 104.4 | 189.3 | 128.6
618 | 528 | 527.8 | 337 | 389.7 | 333.9 | 195.6 | 158.4 | 110.8 | 104.6 | 189.7 | 128.9
619 | 529 | 527.7 | 337.4 | 390 | 334.3 | 196.1 | 158.9 | 111.2 | 104.9 | 190.1 | 129.2
620 | 530 | 527.7 | 337.8 | 390.2 | 334.7 | 196.5 | 159.3 | 111.5 | 105.2 | 190.6 | 129.6
621 | 531 | 527.7 | 338.2 | 390.5 | 335.1 | 197 | 159.7 | 111.8 | 105.4 | 191 | 129.9
622 | 532 | 527.7 | 338.5 | 390.9 | 335.4 | 197.4 | 160.1 | 112.1 | 105.6 | 191.4 | 130.3
623 | 533 | 527.6 | 338.9 | 391.2 | 335.8 | 197.9 | 160.6 | 112.4 | 105.9 | 191.8 | 130.6
624 | 534 | 527.6 | 339.2 | 391.5 | 336.1 | 198.3 | 161 | 112.8 | 106.2 | 192.2 | 130.9
625 | 535 | 527.5 | 339.6 | 391.8 | 336.4 | 198.7 | 161.4 | 113 | 106.5 | 192.7 | 131.2
626 | 536 | 527.4 | 340 | 392.1 | 336.8 | 199.2 | 161.8 | 113.3 | 106.8 | 193.1 | 131.6
627 | 537 | 527.4 | 340.3 | 392.4 | 337.1 | 199.7 | 162.3 | 113.6 | 107.2 | 193.4 | 132
628 | 538 | 527.4 | 340.7 | 392.8 | 337.5 | 200.1 | 162.7 | 113.9 | 107.5 | 193.8 | 132.3
629 | 539 | 527.4 | 341 | 393.1 | 337.8 | 200.6 | 163.2 | 114.1 | 107.8 | 194.2 | 132.7
630 | 540 | 527.4 | 341.4 | 393.4 | 338.1 | 201 | 163.6 | 114.4 | 108.1 | 194.7 | 133.1
631 | 541 | 527.4 | 341.8 | 393.7 | 338.5 | 201.5 | 164 | 114.7 | 108.5 | 195.1 | 133.4
632 | 542 | 527.4 | 342.1 | 394 | 338.8 | 202 | 164.5 | 114.9 | 108.9 | 195.5 | 133.8
633 | 543 | 527.4 | 342.5 | 394.3 | 339.2 | 202.4 | 164.9 | 115.2 | 109.3 | 196 | 134.1
634 | 544 | 527.4 | 342.8 | 394.6 | 339.6 | 202.9 | 165.4 | 115.5 | 109.7 | 196.4 | 134.4
635 | 545 | 527.4 | 343.2 | 394.9 | 339.9 | 203.4 | 165.8 | 115.8 | 110.1 | 196.9 | 134.7
636 | 546 | 527.4 | 343.5 | 395.2 | 340.2 | 203.9 | 166.2 | 116.1 | 110.5 | 197.3 | 135.1
637 | 547 | 527.4 | 343.9 | 395.5 | 340.6 | 204.4 | 166.7 | 116.4 | 110.8 | 197.7 | 135.4
638 | 548 | 527.4 | 344.2 | 395.8 | 340.9 | 204.8 | 167.1 | 116.7 | 111.2 | 198.1 | 135.7
639 | 549 | 527.5 | 344.6 | 396.1 | 341.2 | 205.2 | 167.5 | 117 | 111.6 | 198.5 | 136
640 | 550 | 527.5 | 344.9 | 396.4 | 341.6 | 205.7 | 168 | 117.3 | 112 | 199 | 136.4
641 | 551 | 527.5 | 345.2 | 396.7 | 341.9 | 206.1 | 168.4 | 117.6 | 112.3 | 199.4 | 136.7
642 | 552 | 527.5 | 345.5 | 397.1 | 342.2 | 206.6 | 168.8 | 118 | 112.7 | 199.7 | 137
643 | 553 | 527.5 | 345.9 | 397.4 | 342.5 | 207 | 169.3 | 118.3 | 113.1 | 200.1 | 137.4
644 | 554 | 527.5 | 346.2 | 397.7 | 342.9 | 207.5 | 169.7 | 118.6 | 113.4 | 200.5 | 137.7
645 | 555 | 527.6 | 346.6 | 398 | 343.2 | 207.9 | 170.1 | 118.9 | 113.8 | 201 | 138.1
646 | 556 | 527.6 | 346.9 | 398.3 | 343.5 | 208.4 | 170.5 | 119.3 | 114.2 | 201.4 | 138.4
647 | 557 | 527.7 | 347.2 | 398.6 | 343.9 | 208.8 | 171 | 119.6 | 114.5 | 201.8 | 138.8
648 | 558 | 527.7 | 347.6 | 399 | 344.2 | 209.3 | 171.4 | 119.9 | 114.8 | 202.2 | 139.1
649 | 559 | 527.7 | 347.9 | 399.2 | 344.5 | 209.8 | 171.8 | 120.2 | 115.2 | 202.6 | 139.5
650 | 560 | 527.7 | 348.3 | 399.5 | 344.9 | 210.2 | 172.3 | 120.6 | 115.5 | 203 | 139.8
651 | 561 | 527.7 | 348.6 | 399.9 | 345.2 | 210.7 | 172.7 | 120.9 | 115.9 | 203.4 | 140.2
652 | 562 | 527.8 | 348.9 | 400.2 | 345.5 | 211.1 | 173.1 | 121.2 | 116.2 | 203.8 | 140.5
653 | 563 | 527.8 | 349.2 | 400.5 | 345.8 | 211.5 | 173.5 | 121.5 | 116.6 | 204.2 | 140.9
654 | 564 | 527.8 | 349.5 | 400.8 | 346.1 | 212 | 174 | 121.9 | 117 | 204.7 | 141.2
655 | 565 | 527.8 | 349.9 | 401.1 | 346.4 | 212.5 | 174.4 | 122.2 | 117.4 | 205.1 | 141.6
656 | 566 | 527.7 | 350.2 | 401.3 | 346.8 | 212.9 | 174.8 | 122.5 | 117.8 | 205.5 | 141.9
657 | 567 | 527.6 | 350.5 | 401.6 | 347 | 213.3 | 175.2 | 122.9 | 118.1 | 205.9 | 142.3
658 | 568 | 527.6 | 350.8 | 401.9 | 347.4 | 213.8 | 175.7 | 123.2 | 118.5 | 206.4 | 142.6
659 | 569 | 527.5 | 351.2 | 402.2 | 347.7 | 214.3 | 176.1 | 123.6 | 118.8 | 206.8 | 143
660 | 570 | 527.5 | 351.5 | 402.5 | 348 | 214.7 | 176.5 | 124 | 119.2 | 207.3 | 143.3
661 | 571 | 527.5 | 351.9 | 402.7 | 348.3 | 215.2 | 177 | 124.4 | 119.5 | 207.7 | 143.6
662 | 572 | 527.4 | 352.2 | 403 | 348.7 | 215.6 | 177.4 | 124.8 | 119.9 | 208.2 | 144
663 | 573 | 527.4 | 352.5 | 403.3 | 349 | 216.1 | 177.9 | 125.2 | 120.3 | 208.6 | 144.3
664 | 574 | 527.3 | 352.8 | 403.6 | 349.3 | 216.5 | 178.3 | 125.7 | 120.7 | 209 | 144.7
665 | 575 | 527.3 | 353.2 | 403.8 | 349.6 | 217 | 178.8 | 126.1 | 121 | 209.5 | 145
666 | 576 | 527.2 | 353.5 | 404 | 349.9 | 217.5 | 179.2 | 126.6 | 121.3 | 209.9 | 145.4
667 | 577 | 527.1 | 353.8 | 404.3 | 350.2 | 217.9 | 179.7 | 127.1 | 121.8 | 210.3 | 145.7
668 | 578 | 527.1 | 354.1 | 404.5 | 350.6 | 218.4 | 180.1 | 127.6 | 122.1 | 210.8 | 146.1
669 | 579 | 527.1 | 354.5 | 404.8 | 350.9 | 218.9 | 180.6 | 128.2 | 122.5 | 211.2 | 146.4
670 | 580 | 527.1 | 354.8 | 405 | 351.2 | 219.3 | 181 | 128.7 | 122.9 | 211.7 | 146.8
671 | 581 | 527.1 | 355.1 | 405.3 | 351.5 | 219.8 | 181.5 | 129.3 | 123.2 | 212.1 | 147.1
672 | 582 | 527.1 | 355.4 | 405.6 | 351.8 | 220.2 | 181.9 | 129.8 | 123.7 | 212.6 | 147.4
673 | 583 | 527.1 | 355.7 | 405.8 | 352.1 | 220.7 | 182.4 | 130.4 | 124.1 | 213 | 147.8
674 | 584 | 527.2 | 356 | 406.1 | 352.4 | 221.1 | 182.8 | 131 | 124.5 | 213.4 | 148.1
675 | 585 | 527.2 | 356.4 | 406.4 | 352.7 | 221.6 | 183.3 | 131.5 | 124.9 | 213.9 | 148.4
676 | 586 | 527.2 | 356.7 | 406.6 | 353 | 222.1 | 183.7 | 132.1 | 125.2 | 214.4 | 148.8
677 | 587 | 527.2 | 357 | 406.9 | 353.3 | 222.5 | 184.2 | 132.6 | 125.6 | 214.8 | 149.1
678 | 588 | 527.3 | 357.3 | 407.2 | 353.6 | 222.9 | 184.6 | 133.2 | 126 | 215.3 | 149.4
679 | 589 | 527.3 | 357.6 | 407.4 | 353.9 | 223.4 | 185.1 | 133.8 | 126.5 | 215.7 | 149.8
680 | 590 | 527.3 | 357.9 | 407.7 | 354.1 | 223.9 | 185.5 | 134.3 | 127 | 216.1 | 150.1
681 | 591 | 527.4 | 358.2 | 407.9 | 354.5 | 224.3 | 186 | 134.9 | 127.4 | 216.6 | 150.4
682 | 592 | 527.4 | 358.5 | 408.2 | 354.8 | 224.8 | 186.4 | 135.4 | 127.8 | 217 | 150.8
683 | 593 | 527.4 | 358.8 | 408.5 | 355.1 | 225.3 | 186.9 | 135.9 | 128.3 | 217.5 | 151.1
684 | 594 | 527.4 | 359.1 | 408.7 | 355.3 | 225.7 | 187.3 | 136.4 | 128.7 | 217.9 | 151.4
685 | 595 | 527.3 | 359.4 | 409 | 355.6 | 226.2 | 187.8 | 137 | 129.2 | 218.3 | 151.8
686 | 596 | 527.3 | 359.8 | 409.2 | 355.9 | 226.7 | 188.3 | 137.5 | 129.6 | 218.8 | 152.1
687 | 597 | 527.3 | 360.1 | 409.5 | 356.2 | 227.2 | 188.8 | 138 | 130.1 | 219.2 | 152.4
688 | 598 | 527.3 | 360.3 | 409.7 | 356.5 | 227.6 | 189.2 | 138.5 | 130.6 | 219.6 | 152.8
689 | 599 | 527.3 | 360.7 | 410 | 356.8 | 228.2 | 189.7 | 139 | 131.1 | 220 | 153.1
690 | 600 | 527.2 | 361 | 410.2 | 357.1 | 228.6 | 190.2 | 139.5 | 131.5 | 220.5 | 153.4
691 | 601 | 527.2 | 361.3 | 410.5 | 357.4 | 229.1 | 190.6 | 140 | 132 | 220.9 | 153.8
692 | 602 | 527.2 | 361.6 | 410.7 | 357.7 | 229.6 | 191.1 | 140.5 | 132.4 | 221.3 | 154.1
693 | 603 | 527.2 | 361.9 | 410.9 | 358 | 230.1 | 191.6 | 141 | 132.9 | 221.7 | 154.4
694 | 604 | 527.2 | 362.2 | 411.2 | 358.3 | 230.6 | 192.1 | 141.5 | 133.4 | 222.1 | 154.8
695 | 605 | 527.2 | 362.5 | 411.5 | 358.5 | 231 | 192.6 | 142 | 133.8 | 222.5 | 155.1
696 | 606 | 527.2 | 362.8 | 411.7 | 358.8 | 231.6 | 193.1 | 142.5 | 134.3 | 222.9 | 155.5
697 | 607 | 527.2 | 363.1 | 412 | 359.1 | 232 | 193.5 | 143 | 134.7 | 223.4 | 155.8
698 | 608 | 527.2 | 363.4 | 412.2 | 359.4 | 232.5 | 194 | 143.4 | 135.1 | 223.8 | 156.1
699 | 609 | 527.2 | 363.6 | 412.5 | 359.7 | 232.9 | 194.5 | 143.9 | 135.6 | 224.3 | 156.4
700 | 610 | 527.3 | 363.9 | 412.7 | 360 | 233.4 | 195 | 144.4 | 136.1 | 224.8 | 156.8
701 | 611 | 527.3 | 364.2 | 412.9 | 360.3 | 233.9 | 195.5 | 144.9 | 136.5 | 225.3 | 157.1
702 | 612 | 527.3 | 364.5 | 413.2 | 360.5 | 234.4 | 196 | 145.3 | 137 | 225.9 | 157.4
703 | 613 | 527.3 | 364.8 | 413.4 | 360.8 | 234.9 | 196.5 | 145.8 | 137.3 | 226.4 | 157.8
704 | 614 | 527.3 | 365.1 | 413.6 | 361.1 | 235.4 | 197 | 146.3 | 137.7 | 227 | 158.1
705 | 615 | 527.3 | 365.4 | 413.9 | 361.4 | 235.9 | 197.5 | 146.8 | 138.2 | 227.6 | 158.4
706 | 616 | 527.3 | 365.7 | 414.1 | 361.7 | 236.4 | 198 | 147.2 | 138.6 | 228.1 | 158.8
707 | 617 | 527.2 | 366 | 414.4 | 362 | 236.9 | 198.5 | 147.7 | 139.1 | 228.7 | 159.1
708 | 618 | 527.2 | 366.3 | 414.7 | 362.2 | 237.3 | 199 | 148.2 | 139.6 | 229.4 | 159.4
709 | 619 | 527.2 | 366.5 | 415 | 362.5 | 237.8 | 199.4 | 148.6 | 140 | 230.1 | 159.7
710 | 620 | 527.2 | 366.8 | 415.1 | 362.8 | 238.3 | 199.9 | 149.1 | 140.4 | 230.9 | 160
711 | 621 | 527.2 | 367.1 | 415.4 | 363.1 | 238.8 | 200.4 | 149.6 | 140.9 | 231.6 | 160.3
712 | 622 | 527.2 | 367.4 | 415.7 | 363.3 | 239.3 | 200.9 | 150 | 141.3 | 232.3 | 160.7
713 | 623 | 527.2 | 367.7 | 415.9 | 363.6 | 239.7 | 201.4 | 150.5 | 141.7 | 232.9 | 161
714 | 624 | 527.2 | 368 | 416.1 | 363.9 | 240.2 | 201.9 | 151 | 142.1 | 233.5 | 161.3
715 | 625 | 527.2 | 368.2 | 416.4 | 364.1 | 240.7 | 202.4 | 151.4 | 142.5 | 234.1 | 161.6
716 | 626 | 527.2 | 368.5 | 416.7 | 364.4 | 241.2 | 202.9 | 151.9 | 142.9 | 234.7 | 162
717 | 627 | 527.2 | 368.8 | 416.9 | 364.7 | 241.7 | 203.4 | 152.3 | 143.4 | 235.3 | 162.3
718 | 628 | 527.2 | 369.1 | 417.1 | 365 | 242.1 | 203.8 | 152.8 | 143.9 | 235.8 | 162.6
719 | 629 | 527.2 | 369.4 | 417.3 | 365.3 | 242.7 | 204.3 | 153.3 | 144.3 | 236.4 | 163
720 | 630 | 527.2 | 369.6 | 417.6 | 365.5 | 243.1 | 204.8 | 153.7 | 144.8 | 236.9 | 163.3
721 | 631 | 527.2 | 369.9 | 417.8 | 365.8 | 243.6 | 205.3 | 154.2 | 145.2 | 237.4 | 163.7
722 | 632 | 527.2 | 370.2 | 418.1 | 366 | 244.1 | 205.8 | 154.6 | 145.6 | 237.9 | 164
723 | 633 | 527.2 | 370.5 | 418.3 | 366.3 | 244.6 | 206.3 | 155.1 | 146 | 238.4 | 164.3
724 | 634 | 527.3 | 370.7 | 418.5 | 366.6 | 245 | 206.8 | 155.5 | 146.4 | 239 | 164.7
725 | 635 | 527.3 | 371 | 418.7 | 366.9 | 245.6 | 207.3 | 156 | 146.8 | 239.5 | 165
726 | 636 | 527.3 | 371.3 | 418.9 | 367.2 | 246.1 | 207.9 | 156.5 | 147.3 | 240 | 165.3
727 | 637 | 527.2 | 371.6 | 419.1 | 367.5 | 246.5 | 208.3 | 156.9 | 147.7 | 240.5 | 165.7
728 | 638 | 527.2 | 371.8 | 419.4 | 367.7 | 247 | 208.8 | 157.4 | 148.1 | 241 | 166
729 | 639 | 527.2 | 372.1 | 419.7 | 368 | 247.5 | 209.3 | 157.8 | 148.5 | 241.6 | 166.3
730 | 640 | 527.2 | 372.4 | 420 | 368.3 | 247.9 | 209.8 | 158.3 | 149 | 242.5 | 166.6
731 | 641 | 527.2 | 372.6 | 420.2 | 368.5 | 248.4 | 210.2 | 158.7 | 149.4 | 243.4 | 167
732 | 642 | 527.2 | 372.9 | 420.4 | 368.8 | 248.9 | 210.6 | 159.2 | 149.9 | 244.3 | 167.3
733 | 643 | 527.2 | 373.2 | 420.6 | 369.1 | 249.4 | 211 | 159.6 | 150.3 | 245 | 167.6
734 | 644 | 527.3 | 373.4 | 420.9 | 369.4 | 249.8 | 211.5 | 160.1 | 150.7 | 245.8 | 168
735 | 645 | 527.3 | 373.7 | 421.1 | 369.6 | 250.2 | 211.9 | 160.5 | 151.2 | 246.4 | 168.3
736 | 646 | 527.3 | 374 | 421.3 | 369.9 | 250.7 | 212.4 | 161 | 151.6 | 246.7 | 168.6
737 | 647 | 527.3 | 374.3 | 421.5 | 370.2 | 251.1 | 212.9 | 161.4 | 152.1 | 247.1 | 168.9
738 | 648 | 527.2 | 374.5 | 421.7 | 370.5 | 251.5 | 213.4 | 161.9 | 152.4 | 247.5 | 169.2
739 | 649 | 527.2 | 374.8 | 422 | 370.7 | 251.9 | 213.8 | 162.3 | 152.8 | 248 | 169.6
740 | 650 | 527.2 | 375.1 | 422.2 | 371 | 252.3 | 214.3 | 162.8 | 153.2 | 248.4 | 169.9
741 | 651 | 527.2 | 375.3 | 422.5 | 371.3 | 252.6 | 214.8 | 163.2 | 153.6 | 248.8 | 170.2
742 | 652 | 527.2 | 375.6 | 422.6 | 371.5 | 253 | 215.2 | 163.7 | 154 | 249.3 | 170.6
743 | 653 | 527.2 | 375.9 | 422.9 | 371.8 | 253.4 | 215.7 | 164.1 | 154.5 | 249.7 | 170.9
744 | 654 | 527.2 | 376.1 | 423.1 | 372.1 | 253.7 | 216.1 | 164.6 | 154.9 | 250.2 | 171.2
745 | 655 | 527.2 | 376.3 | 423.4 | 372.3 | 253.8 | 216.5 | 165 | 155.3 | 250.6 | 171.6
746 | 656 | 527.2 | 376.6 | 423.6 | 372.6 | 253.8 | 216.9 | 165.5 | 155.8 | 251 | 172
747 | 657 | 527.3 | 376.9 | 423.8 | 372.8 | 253.9 | 217.2 | 165.9 | 156.3 | 251.5 | 172.3
748 | 658 | 527.3 | 377.1 | 424.1 | 373.1 | 253.8 | 217.4 | 166.4 | 156.8 | 251.9 | 172.7
749 | 659 | 527.3 | 377.4 | 424.3 | 373.3 | 253.5 | 217.6 | 166.8 | 157.3 | 252.3 | 173.1
750 | 660 | 527.3 | 377.6 | 424.5 | 373.5 | 253.1 | 217.7 | 167.2 | 157.7 | 252.8 | 173.5
751 | 661 | 527.3 | 377.9 | 424.8 | 373.8 | 253 | 217.8 | 167.7 | 158.2 | 253.3 | 173.9
752 | 662 | 527.4 | 378.1 | 425 | 374 | 253.1 | 217.9 | 168.1 | 158.6 | 253.8 | 174.2
753 | 663 | 527.4 | 378.4 | 425.2 | 374.3 | 253.5 | 218 | 168.6 | 159.1 | 254.2 | 174.6
754 | 664 | 527.4 | 378.7 | 425.5 | 374.5 | 253.8 | 218.1 | 169 | 159.4 | 254.7 | 175
755 | 665 | 527.4 | 378.9 | 425.7 | 374.7 | 253.9 | 218.3 | 169.4 | 159.8 | 255.2 | 175.5
756 | 666 | 527.4 | 379.2 | 425.9 | 375 | 253.7 | 218.5 | 169.9 | 160.3 | 255.7 | 175.9
757 | 667 | 527.4 | 379.5 | 426.1 | 375.3 | 253.6 | 218.7 | 170.3 | 160.6 | 256.2 | 176.3
758 | 668 | 527.4 | 379.7 | 426.4 | 375.5 | 253.4 | 218.9 | 170.8 | 161 | 256.7 | 176.7
759 | 669 | 527.4 | 379.9 | 426.6 | 375.8 | 253.3 | 219.2 | 171.2 | 161.3 | 257.2 | 177.2
760 | 670 | 527.4 | 380.2 | 426.8 | 376.1 | 253.2 | 219.4 | 171.6 | 161.8 | 257.7 | 178
761 | 671 | 527.4 | 380.5 | 427 | 376.3 | 253 | 219.7 | 172.1 | 162.3 | 258.2 | 178.8
762 | 672 | 527.4 | 380.7 | 427.3 | 376.5 | 252.4 | 219.9 | 172.5 | 162.7 | 258.7 | 179.7
763 | 673 | 527.4 | 380.9 | 427.5 | 376.7 | 252 | 220.1 | 173 | 163.2 | 259.2 | 180.5
764 | 674 | 527.4 | 381.2 | 427.7 | 377 | 251.7 | 220.4 | 173.4 | 163.6 | 259.6 | 181.3
765 | 675 | 527.4 | 381.4 | 428 | 377.2 | 251.4 | 220.6 | 173.8 | 164.1 | 260.1 | 182.2
766 | 676 | 527.3 | 381.7 | 428.1 | 377.5 | 251.4 | 220.9 | 174.3 | 164.5 | 260.5 | 182.8
767 | 677 | 527.3 | 381.9 | 428.3 | 377.8 | 251.4 | 221.1 | 174.7 | 164.9 | 261 | 183.2
768 | 678 | 527.2 | 382.2 | 428.6 | 378 | 251.5 | 221.3 | 175.1 | 165.3 | 261.5 | 183.4
769 | 679 | 527.1 | 382.4 | 428.8 | 378.2 | 251.6 | 221.4 | 175.6 | 165.6 | 261.9 | 183.8
770 | 680 | 527.1 | 382.7 | 428.9 | 378.5 | 251.7 | 221.6 | 176 | 166 | 262.4 | 184.1
771 | 681 | 527 | 382.9 | 429.2 | 378.7 | 251.7 | 221.8 | 176.4 | 166.5 | 262.9 | 184.6
772 | 682 | 527 | 383.1 | 429.4 | 379 | 251.7 | 221.9 | 176.9 | 166.9 | 263.3 | 185.2
773 | 683 | 526.9 | 383.3 | 429.7 | 379.2 | 251.6 | 222.1 | 177.3 | 167.4 | 263.7 | 185.9
774 | 684 | 526.9 | 383.5 | 429.9 | 379.5 | 251.7 | 222.2 | 177.8 | 167.8 | 264.1 | 186.6
775 | 685 | 526.8 | 383.8 | 430.2 | 379.7 | 251.9 | 222.4 | 178.2 | 168.2 | 264.5 | 187.4
776 | 686 | 526.8 | 384 | 430.3 | 379.9 | 252.2 | 222.6 | 178.6 | 168.7 | 264.8 | 188.1
777 | 687 | 526.8 | 384.3 | 430.5 | 380.2 | 252.5 | 222.8 | 179 | 169.2 | 265.2 | 188.8
778 | 688 | 526.7 | 384.5 | 430.8 | 380.4 | 252.7 | 223 | 179.5 | 169.6 | 265.6 | 189.5
779 | 689 | 526.7 | 384.7 | 431 | 380.6 | 252.8 | 223.2 | 179.9 | 170 | 266 | 190
780 | 690 | 526.8 | 384.9 | 431.2 | 380.9 | 253.1 | 223.4 | 180.4 | 170.4 | 266.5 | 190.2
781 | 691 | 526.8 | 385.2 | 431.4 | 381.2 | 253.2 | 223.7 | 180.8 | 170.8 | 266.9 | 190.7
782 | 692 | 526.8 | 385.4 | 431.6 | 381.4 | 253.3 | 224 | 181.2 | 171.2 | 267.3 | 191.2
783 | 693 | 526.8 | 385.6 | 431.9 | 381.6 | 253.4 | 224.2 | 181.7 | 171.6 | 267.8 | 191.6
784 | 694 | 526.8 | 385.9 | 432 | 381.9 | 253.7 | 224.6 | 182.1 | 172 | 268.2 | 192.1
785 | 695 | 526.8 | 386.1 | 432.3 | 382.1 | 254.3 | 224.9 | 182.5 | 172.4 | 268.7 | 192.7
786 | 696 | 526.8 | 386.4 | 432.5 | 382.4 | 254.9 | 225.2 | 182.9 | 172.8 | 269.1 | 193.3
787 | 697 | 526.8 | 386.6 | 432.7 | 382.6 | 255.6 | 225.5 | 183.4 | 173.2 | 269.5 | 193.8
788 | 698 | 526.8 | 386.8 | 433 | 382.8 | 256.2 | 225.8 | 183.8 | 173.7 | 269.9 | 194.4
789 | 699 | 526.8 | 387 | 433.2 | 383 | 256.7 | 226.1 | 184.2 | 174.1 | 270.3 | 195
790 | 700 | 526.8 | 387.3 | 433.4 | 383.3 | 257.3 | 226.4 | 184.6 | 174.5 | 270.7 | 195.6
791 | 701 | 526.8 | 387.5 | 433.7 | 383.5 | 257.8 | 226.7 | 185.1 | 175 | 271.2 | 196.1
792 | 702 | 526.8 | 387.7 | 433.9 | 383.7 | 258.3 | 227.1 | 185.5 | 175.4 | 271.6 | 196.6
793 | 703 | 526.8 | 388 | 434.1 | 384 | 258.7 | 227.4 | 185.9 | 175.8 | 272.1 | 197
794 | 704 | 526.8 | 388.2 | 434.3 | 384.2 | 259.2 | 227.7 | 186.3 | 176.2 | 272.5 | 197.4
795 | 705 | 526.8 | 388.5 | 434.5 | 384.4 | 259.5 | 228.1 | 186.7 | 176.6 | 273 | 197.8
796 | 706 | 526.8 | 388.7 | 434.7 | 384.7 | 259.9 | 228.4 | 187.2 | 177 | 273.5 | 198.1
797 | 707 | 526.8 | 388.9 | 434.9 | 384.9 | 260.2 | 228.7 | 187.6 | 177.4 | 274 | 198.4
798 | 708 | 526.9 | 389.1 | 435.1 | 385.1 | 260.8 | 229 | 188 | 177.9 | 274.5 | 198.6
799 | 709 | 526.9 | 389.3 | 435.3 | 385.4 | 261.4 | 229.4 | 188.4 | 178.2 | 275.1 | 198.8
800 | 710 | 526.9 | 389.6 | 435.5 | 385.6 | 261.9 | 229.7 | 188.8 | 178.6 | 275.6 | 198.9
801 | 711 | 526.9 | 389.8 | 435.7 | 385.8 | 262.2 | 230.1 | 189.2 | 179 | 276.1 | 198.9
802 | 712 | 526.8 | 390 | 435.9 | 386.1 | 262.3 | 230.4 | 189.6 | 179.4 | 276.7 | 199.1
803 | 713 | 526.8 | 390.3 | 436.1 | 386.3 | 262.4 | 230.8 | 190.1 | 179.9 | 277.2 | 199.4
804 | 714 | 526.7 | 390.5 | 436.2 | 386.6 | 262.7 | 231.1 | 190.5 | 180.3 | 277.7 | 199.8
805 | 715 | 526.7 | 390.7 | 436.4 | 386.8 | 262.7 | 231.5 | 190.9 | 180.8 | 278.3 | 200.2
806 | 716 | 526.7 | 391 | 436.7 | 387 | 263.1 | 231.9 | 191.3 | 181.2 | 278.8 | 200.6
807 | 717 | 526.7 | 391.2 | 436.9 | 387.2 | 264 | 232.2 | 191.7 | 181.7 | 279.3 | 201
808 | 718 | 526.7 | 391.4 | 437 | 387.5 | 264.8 | 232.6 | 192.1 | 182.1 | 279.8 | 201.4
809 | 719 | 526.7 | 391.7 | 437.2 | 387.7 | 265.4 | 232.9 | 192.5 | 182.6 | 280.3 | 201.7
810 | 720 | 526.7 | 391.9 | 437.5 | 388 | 265.8 | 233.2 | 192.9 | 182.9 | 280.8 | 202.1
811 | 721 | 526.7 | 392.1 | 437.7 | 388.2 | 266.2 | 233.6 | 193.3 | 183.4 | 281.4 | 202.5
812 | 722 | 526.7 | 392.3 | 437.9 | 388.4 | 266.4 | 233.9 | 193.7 | 183.8 | 281.9 | 202.9
813 | 723 | 526.6 | 392.6 | 438 | 388.7 | 266.7 | 234.2 | 194.1 | 184.2 | 282.3 | 203.3
814 | 724 | 526.6 | 392.8 | 438.2 | 388.9 | 266.9 | 234.6 | 194.5 | 184.6 | 282.8 | 203.8
815 | 725 | 526.6 | 393 | 438.4 | 389.2 | 267.2 | 234.9 | 194.9 | 185 | 283.3 | 204.3
816 | 726 | 526.6 | 393.3 | 438.5 | 389.4 | 267.4 | 235.3 | 195.3 | 185.5 | 283.7 | 204.6
817 | 727 | 526.6 | 393.5 | 438.8 | 389.6 | 267.5 | 235.6 | 195.7 | 185.8 | 284.2 | 205
818 | 728 | 526.6 | 393.7 | 439.1 | 389.8 | 267.7 | 235.9 | 196.1 | 186.2 | 284.7 | 205.5
819 | 729 | 526.6 | 393.9 | 439.2 | 390.1 | 268 | 236.4 | 196.5 | 186.5 | 285.1 | 206
820 | 730 | 526.6 | 394.2 | 439.4 | 390.3 | 268.1 | 236.7 | 196.9 | 186.9 | 285.6 | 206.5
821 | 731 | 526.6 | 394.4 | 439.6 | 390.5 | 268.3 | 237.1 | 197.3 | 187.3 | 286 | 207.1
822 | 732 | 526.6 | 394.6 | 439.8 | 390.7 | 268.5 | 237.5 | 197.7 | 187.7 | 286.4 | 207.8
823 | 733 | 526.5 | 394.8 | 440 | 391 | 268.8 | 237.9 | 198.1 | 188.1 | 286.9 | 208.4
824 | 734 | 526.5 | 395 | 440.2 | 391.2 | 269 | 238.2 | 198.5 | 188.4 | 287.3 | 209
825 | 735 | 526.5 | 395.2 | 440.4 | 391.4 | 269.2 | 238.6 | 198.9 | 188.8 | 287.7 | 209.7
826 | 736 | 526.5 | 395.5 | 440.5 | 391.6 | 269.4 | 238.9 | 199.3 | 189.2 | 288.2 | 210.3
827 | 737 | 526.4 | 395.7 | 440.8 | 391.8 | 269.5 | 239.3 | 199.7 | 189.6 | 288.6 | 210.9
828 | 738 | 526.4 | 395.9 | 440.9 | 392 | 269.6 | 239.6 | 200.1 | 190 | 289.1 | 211.4
829 | 739 | 526.4 | 396.2 | 441.1 | 392.3 | 269.7 | 239.9 | 200.5 | 190.4 | 289.5 | 211.9
830 | 740 | 526.4 | 396.4 | 441.3 | 392.5 | 269.8 | 240.3 | 200.9 | 190.8 | 289.9 | 212.4
831 | 741 | 526.4 | 396.6 | 441.5 | 392.7 | 269.8 | 240.6 | 201.3 | 191.2 | 290.4 | 212.9
832 | 742 | 526.4 | 396.8 | 441.7 | 393 | 270 | 240.9 | 201.6 | 191.7 | 290.8 | 213.4
833 | 743 | 526.3 | 397 | 441.8 | 393.2 | 270.2 | 241.2 | 202 | 192 | 291.2 | 214
834 | 744 | 526.3 | 397.2 | 442.1 | 393.4 | 270.4 | 241.5 | 202.4 | 192.5 | 291.6 | 214.5
835 | 745 | 526.3 | 397.4 | 442.3 | 393.6 | 270.7 | 241.9 | 202.8 | 192.8 | 292 | 215
836 | 746 | 526.3 | 397.7 | 442.5 | 393.8 | 270.9 | 242.2 | 203.2 | 193.2 | 292.4 | 215.4
837 | 747 | 526.4 | 397.9 | 442.6 | 394 | 271.1 | 242.5 | 203.6 | 193.6 | 292.8 | 215.9
838 | 748 | 526.4 | 398.1 | 442.8 | 394.3 | 271.4 | 242.8 | 204 | 194 | 293.2 | 216.3
839 | 749 | 526.4 | 398.3 | 443 | 394.5 | 271.6 | 243.2 | 204.4 | 194.4 | 293.6 | 216.7
840 | 750 | 526.5 | 398.5 | 443.2 | 394.7 | 271.9 | 243.6 | 204.7 | 194.8 | 294.1 | 217.2
841 | 751 | 526.5 | 398.7 | 443.4 | 394.9 | 272.1 | 243.9 | 205.1 | 195.2 | 294.5 | 217.8
842 | 752 | 526.6 | 398.9 | 443.6 | 395.1 | 272.4 | 244.2 | 205.5 | 195.7 | 294.9 | 218.2
843 | 753 | 526.6 | 399.2 | 443.8 | 395.4 | 272.8 | 244.5 | 205.9 | 196.1 | 295.3 | 218.6
844 | 754 | 526.7 | 399.4 | 444 | 395.6 | 273.2 | 244.9 | 206.3 | 196.5 | 295.8 | 219.1
845 | 755 | 526.8 | 399.6 | 444.1 | 395.8 | 273.5 | 245.2 | 206.7 | 196.8 | 296.1 | 219.5
846 | 756 | 526.8 | 399.8 | 444.3 | 396 | 273.8 | 245.6 | 207 | 197.2 | 296.5 | 219.9
847 | 757 | 526.9 | 400 | 444.5 | 396.2 | 274.1 | 245.9 | 207.4 | 197.6 | 296.9 | 220.3
848 | 758 | 526.9 | 400.2 | 444.7 | 396.4 | 274.3 | 246.3 | 207.8 | 198 | 297.3 | 220.7
849 | 759 | 527 | 400.4 | 445 | 396.6 | 274.6 | 246.6 | 208.2 | 198.4 | 297.7 | 221.2
850 | 760 | 527 | 400.6 | 445.2 | 396.8 | 274.8 | 246.9 | 208.6 | 198.8 | 298.2 | 221.7
851 | 761 | 527.1 | 400.8 | 445.3 | 397.1 | 275.1 | 247.4 | 208.9 | 199.2 | 298.5 | 222.3
852 | 762 | 527.1 | 401 | 445.6 | 397.2 | 275.3 | 247.7 | 209.3 | 199.6 | 298.9 | 222.9
853 | 763 | 527.1 | 401.2 | 445.7 | 397.5 | 275.6 | 248.1 | 209.7 | 200 | 299.2 | 223.4
854 | 764 | 527.1 | 401.4 | 445.9 | 397.7 | 275.9 | 248.5 | 210.1 | 200.3 | 299.6 | 223.8
855 | 765 | 527.1 | 401.6 | 446 | 397.9 | 276.1 | 249 | 210.4 | 200.7 | 299.9 | 224.1
856 | 766 | 527 | 401.8 | 446.3 | 398.1 | 276.4 | 249.3 | 210.8 | 201.1 | 300.2 | 224.5
857 | 767 | 527 | 402 | 446.4 | 398.3 | 276.6 | 249.7 | 211.2 | 201.5 | 300.6 | 224.9
858 | 768 | 527 | 402.2 | 446.6 | 398.5 | 276.8 | 250.1 | 211.6 | 202 | 300.9 | 225.5
859 | 769 | 527.1 | 402.4 | 446.7 | 398.7 | 277.1 | 250.5 | 211.9 | 202.4 | 301.2 | 226
860 | 770 | 527.1 | 402.6 | 447 | 398.9 | 277.3 | 250.8 | 212.3 | 202.9 | 301.5 | 226.4
861 | 771 | 527.1 | 402.8 | 447.1 | 399.1 | 277.7 | 251.1 | 212.7 | 203.3 | 301.8 | 226.8
862 | 772 | 527.1 | 403 | 447.3 | 399.3 | 278 | 251.5 | 213.1 | 203.7 | 302.2 | 227.3
863 | 773 | 527.1 | 403.2 | 447.5 | 399.5 | 278.3 | 251.8 | 213.4 | 204.1 | 302.5 | 227.9
864 | 774 | 527.1 | 403.4 | 447.7 | 399.7 | 278.6 | 252.2 | 213.8 | 204.5 | 302.8 | 228.3
865 | 775 | 527.1 | 403.6 | 447.8 | 399.9 | 278.9 | 252.5 | 214.2 | 204.9 | 303.1 | 228.6
866 | 776 | 527 | 403.8 | 448.1 | 400.1 | 279.2 | 252.9 | 214.5 | 205.3 | 303.5 | 229
867 | 777 | 527 | 404 | 448.2 | 400.3 | 279.5 | 253.3 | 214.9 | 205.6 | 303.9 | 229.4
868 | 778 | 527 | 404.2 | 448.4 | 400.5 | 279.8 | 253.6 | 215.3 | 206 | 304.2 | 229.7
869 | 779 | 526.9 | 404.4 | 448.5 | 400.7 | 280.2 | 254 | 215.6 | 206.4 | 304.5 | 230.1
870 | 780 | 526.9 | 404.6 | 448.7 | 400.9 | 280.5 | 254.4 | 216 | 206.8 | 304.8 | 230.4
871 | 781 | 526.9 | 404.8 | 448.8 | 401.1 | 280.9 | 254.7 | 216.4 | 207.3 | 305.1 | 230.7
872 | 782 | 526.9 | 405 | 449 | 401.3 | 281.1 | 255.1 | 216.8 | 207.6 | 305.4 | 231
873 | 783 | 526.9 | 405.2 | 449.1 | 401.5 | 281.3 | 255.4 | 217.1 | 208 | 305.7 | 231.2
874 | 784 | 526.9 | 405.4 | 449.3 | 401.7 | 281.4 | 255.8 | 217.5 | 208.4 | 306 | 231.5
875 | 785 | 526.9 | 405.6 | 449.5 | 401.9 | 281.7 | 256.1 | 217.9 | 208.8 | 306.2 | 231.8
876 | 786 | 526.9 | 405.8 | 449.7 | 402 | 281.9 | 256.4 | 218.3 | 209.1 | 306.5 | 232.2
877 | 787 | 526.9 | 406 | 449.9 | 402.2 | 282.1 | 256.8 | 218.7 | 209.4 | 306.8 | 232.7
878 | 788 | 526.9 | 406.2 | 450 | 402.4 | 282.4 | 257.2 | 219 | 209.8 | 307.2 | 233.2
879 | 789 | 526.8 | 406.4 | 450.2 | 402.6 | 282.6 | 257.5 | 219.4 | 210.2 | 307.5 | 233.5
880 | 790 | 526.8 | 406.6 | 450.3 | 402.8 | 282.8 | 257.9 | 219.8 | 210.7 | 307.7 | 233.8
881 | 791 | 526.8 | 406.8 | 450.5 | 403 | 283.1 | 258.3 | 220.1 | 211.1 | 308 | 234
882 | 792 | 526.7 | 407 | 450.6 | 403.2 | 283.3 | 258.7 | 220.5 | 211.4 | 308.3 | 234.4
883 | 793 | 526.7 | 407.2 | 450.8 | 403.4 | 283.7 | 259 | 220.9 | 211.7 | 308.6 | 234.7
884 | 794 | 526.7 | 407.3 | 451 | 403.6 | 283.9 | 259.4 | 221.3 | 212.1 | 308.9 | 234.9
885 | 795 | 526.7 | 407.5 | 451.2 | 403.8 | 284.2 | 259.8 | 221.6 | 212.4 | 309.2 | 235.1
886 | 796 | 526.7 | 407.7 | 451.3 | 403.9 | 284.4 | 260.1 | 222 | 212.8 | 309.4 | 235.4
887 | 797 | 526.7 | 407.9 | 451.5 | 404.1 | 284.6 | 260.5 | 222.4 | 213.3 | 309.8 | 235.7
888 | 798 | 526.7 | 408.1 | 451.6 | 404.3 | 284.8 | 260.9 | 222.7 | 213.7 | 310.1 | 235.9
889 | 799 | 526.7 | 408.3 | 451.8 | 404.5 | 285 | 261.3 | 223.1 | 214.1 | 310.4 | 236.3
890 | 800 | 526.6 | 408.5 | 451.9 | 404.7 | 285.3 | 261.7 | 223.5 | 214.5 | 310.7 | 236.7
891 | 801 | 526.6 | 408.6 | 452.1 | 404.9 | 285.5 | 262 | 223.8 | 214.8 | 311 | 237
892 | 802 | 526.6 | 408.8 | 452.3 | 405.1 | 285.8 | 262.4 | 224.2 | 215.2 | 311.3 | 237.4
893 | 803 | 526.6 | 409 | 452.4 | 405.2 | 286.1 | 262.9 | 224.6 | 215.6 | 311.6 | 237.7
894 | 804 | 526.6 | 409.2 | 452.6 | 405.4 | 286.4 | 263.3 | 224.9 | 216.1 | 311.8 | 238
895 | 805 | 526.6 | 409.4 | 452.7 | 405.6 | 286.5 | 263.7 | 225.3 | 216.5 | 312 | 238.3
896 | 806 | 526.5 | 409.6 | 452.8 | 405.8 | 286.8 | 264.1 | 225.7 | 217 | 312.3 | 238.6
897 | 807 | 526.5 | 409.8 | 452.9 | 406 | 287.1 | 264.6 | 226 | 217.5 | 312.5 | 238.9
898 | 808 | 526.5 | 410 | 453.1 | 406.2 | 287.3 | 265 | 226.4 | 218 | 312.7 | 239.3
899 | 809 | 526.4 | 410.1 | 453.3 | 406.3 | 287.6 | 265.4 | 226.8 | 218.4 | 313 | 239.7
900 | 810 | 526.4 | 410.3 | 453.4 | 406.5 | 287.9 | 265.8 | 227.1 | 218.8 | 313.2 | 240.1
901 | 811 | 526.4 | 410.5 | 453.6 | 406.7 | 288.2 | 266.3 | 227.5 | 219.1 | 313.5 | 240.5
902 | 812 | 526.4 | 410.7 | 453.8 | 406.9 | 288.5 | 266.7 | 227.8 | 219.5 | 313.7 | 241
903 | 813 | 526.4 | 410.9 | 453.8 | 407.1 | 288.9 | 267.1 | 228.2 | 220 | 314 | 241.5
904 | 814 | 526.4 | 411.1 | 454 | 407.2 | 289.2 | 267.6 | 228.5 | 220.4 | 314.2 | 241.9
905 | 815 | 526.3 | 411.2 | 454.2 | 407.4 | 289.3 | 268 | 228.9 | 220.8 | 314.4 | 242.3
906 | 816 | 526.3 | 411.4 | 454.3 | 407.6 | 289.7 | 268.4 | 229.3 | 221.2 | 314.6 | 242.7
907 | 817 | 526.3 | 411.6 | 454.4 | 407.7 | 289.9 | 268.9 | 229.6 | 221.6 | 314.8 | 243
908 | 818 | 526.3 | 411.8 | 454.6 | 407.9 | 290.2 | 269.3 | 230 | 221.9 | 315.1 | 243.5
909 | 819 | 526.3 | 411.9 | 454.8 | 408.1 | 290.6 | 269.8 | 230.4 | 222.4 | 315.3 | 243.9
910 | 820 | 526.4 | 412.1 | 454.9 | 408.2 | 291 | 270.4 | 230.7 | 222.8 | 315.6 | 244.3
911 | 821 | 526.4 | 412.3 | 455.1 | 408.4 | 291.4 | 271.1 | 231.1 | 223.3 | 315.9 | 244.8
912 | 822 | 526.4 | 412.5 | 455.2 | 408.6 | 291.4 | 271.5 | 231.4 | 223.7 | 316.2 | 245.1
913 | 823 | 526.4 | 412.6 | 455.4 | 408.7 | 291.3 | 272 | 231.8 | 224.1 | 316.4 | 245.4
914 | 824 | 526.5 | 412.8 | 455.5 | 408.9 | 291.2 | 272.4 | 232.1 | 224.4 | 316.7 | 245.9
915 | 825 | 526.4 | 413 | 455.6 | 409.1 | 291.3 | 272.8 | 232.5 | 224.7 | 317 | 246.3
916 | 826 | 526.5 | 413.2 | 455.8 | 409.2 | 291.4 | 273.3 | 232.9 | 225.1 | 317.3 | 246.7
917 | 827 | 526.5 | 413.4 | 455.9 | 409.4 | 291.4 | 273.8 | 233.2 | 225.5 | 317.6 | 247.1
918 | 828 | 526.5 | 413.5 | 456 | 409.6 | 291.6 | 274.4 | 233.5 | 225.9 | 317.9 | 247.4
919 | 829 | 526.5 | 413.7 | 456.2 | 409.7 | 291.8 | 275 | 233.9 | 226.2 | 318.2 | 247.8
920 | 830 | 526.5 | 413.9 | 456.3 | 409.9 | 292 | 275.7 | 234.2 | 226.6 | 318.5 | 248.2
921 | 831 | 526.5 | 414.1 | 456.4 | 410.1 | 291.9 | 276.3 | 234.6 | 227 | 318.7 | 248.6
922 | 832 | 526.5 | 414.2 | 456.6 | 410.3 | 291.9 | 277 | 234.9 | 227.4 | 318.9 | 249
923 | 833 | 526.5 | 414.4 | 456.8 | 410.4 | 291.9 | 277.6 | 235.3 | 227.7 | 319.1 | 249.3
924 | 834 | 526.5 | 414.6 | 456.8 | 410.6 | 291.9 | 278.1 | 235.6 | 228.1 | 319.3 | 249.6
925 | 835 | 526.5 | 414.8 | 457 | 410.8 | 292 | 278.6 | 235.9 | 228.5 | 319.6 | 250
926 | 836 | 526.5 | 414.9 | 457.2 | 410.9 | 292 | 279.1 | 236.3 | 228.9 | 319.8 | 250.3
927 | 837 | 526.6 | 415 | 457.3 | 411 | 292.2 | 279.6 | 236.6 | 229.3 | 320.1 | 250.6
928 | 838 | 526.6 | 415.2 | 457.5 | 411.2 | 292.5 | 280.1 | 237 | 229.6 | 320.3 | 250.9
929 | 839 | 526.6 | 415.4 | 457.6 | 411.4 | 292.8 | 280.5 | 237.3 | 230.1 | 320.6 | 251.2
930 | 840 | 526.6 | 415.5 | 457.8 | 411.5 | 293.1 | 280.9 | 237.6 | 230.4 | 320.9 | 251.4
931 | 841 | 526.5 | 415.7 | 457.9 | 411.7 | 293.3 | 281.3 | 238 | 230.7 | 321.1 | 251.6
932 | 842 | 526.5 | 415.9 | 458 | 411.8 | 293.5 | 281.8 | 238.3 | 231.1 | 321.4 | 251.9
933 | 843 | 526.5 | 416 | 458.1 | 412 | 293.6 | 282.1 | 238.6 | 231.5 | 321.6 | 252.2
934 | 844 | 526.4 | 416.2 | 458.3 | 412.2 | 293.9 | 282.5 | 238.9 | 231.9 | 321.9 | 252.5
935 | 845 | 526.4 | 416.4 | 458.4 | 412.3 | 294.2 | 283 | 239.3 | 232.2 | 322.2 | 252.7
936 | 846 | 526.4 | 416.6 | 458.5 | 412.5 | 294.4 | 283.4 | 239.6 | 232.6 | 322.5 | 253.1
937 | 847 | 526.3 | 416.7 | 458.7 | 412.6 | 294.5 | 283.8 | 239.9 | 233 | 322.8 | 253.4
938 | 848 | 526.3 | 416.9 | 458.8 | 412.8 | 294.6 | 283.5 | 240.2 | 233.4 | 323 | 253.9
939 | 849 | 526.3 | 417.1 | 458.9 | 413 | 295 | 283.1 | 240.5 | 233.7 | 323.3 | 254.3
940 | 850 | 526.3 | 417.2 | 459.1 | 413.1 | 295.2 | 282.9 | 240.8 | 234 | 323.5 | 254.7
941 | 851 | 526.3 | 417.4 | 459.2 | 413.3 | 295.5 | 282.8 | 241.1 | 234.4 | 323.8 | 255
942 | 852 | 526.3 | 417.6 | 459.3 | 413.4 | 295.9 | 282.9 | 241.5 | 234.7 | 324.1 | 255.2
943 | 853 | 526.2 | 417.7 | 459.5 | 413.6 | 296.3 | 283 | 241.8 | 235 | 324.3 | 255.6
944 | 854 | 526.2 | 417.9 | 459.6 | 413.7 | 296.7 | 283.2 | 242.1 | 235.3 | 324.6 | 255.9
945 | 855 | 526.2 | 418.1 | 459.7 | 413.9 | 297 | 283.5 | 242.4 | 235.7 | 324.9 | 256.2
946 | 856 | 526.2 | 418.3 | 459.7 | 414 | 297.4 | 283.7 | 242.7 | 236 | 325.2 | 256.6
947 | 857 | 526.1 | 418.4 | 459.9 | 414.2 | 297.7 | 284 | 243 | 236.3 | 325.5 | 256.9
948 | 858 | 526.1 | 418.5 | 460.1 | 414.3 | 298 | 284.2 | 243.3 | 236.8 | 325.8 | 257.2
949 | 859 | 526.1 | 418.7 | 460.2 | 414.5 | 298.4 | 284.5 | 243.6 | 237.1 | 326.1 | 257.6
950 | 860 | 526.1 | 418.9 | 460.2 | 414.7 | 298.8 | 284.8 | 243.9 | 237.5 | 326.4 | 257.9
951 | 861 | 526.1 | 419 | 460.4 | 414.8 | 299.1 | 285 | 244.2 | 237.9 | 326.7 | 258.2
952 | 862 | 526.2 | 419.2 | 460.5 | 415 | 299.6 | 285.3 | 244.5 | 238.2 | 327 | 258.6
953 | 863 | 526.2 | 419.4 | 460.7 | 415.1 | 300.2 | 285.6 | 244.7 | 238.6 | 327.3 | 258.9
954 | 864 | 526.3 | 419.5 | 460.8 | 415.3 | 300.7 | 285.9 | 245 | 238.9 | 327.6 | 259.3
955 | 865 | 526.3 | 419.7 | 461 | 415.4 | 301.2 | 286.1 | 245.3 | 239.3 | 327.9 | 259.6
956 | 866 | 526.3 | 419.8 | 461.1 | 415.6 | 301.7 | 286.4 | 245.6 | 239.7 | 328.2 | 260
957 | 867 | 526.4 | 420 | 461.2 | 415.7 | 302.2 | 286.6 | 245.9 | 240 | 328.5 | 260.3
958 | 868 | 526.4 | 420.1 | 461.3 | 415.9 | 302.5 | 286.9 | 246.2 | 240.3 | 328.8 | 260.7
959 | 869 | 526.4 | 420.3 | 461.4 | 416.1 | 302.8 | 287.1 | 246.5 | 240.7 | 329.1 | 261.1
960 | 870 | 526.4 | 420.5 | 461.6 | 416.2 | 303 | 287.2 | 246.8 | 241 | 329.5 | 261.6
961 | 871 | 526.5 | 420.6 | 461.7 | 416.3 | 303.2 | 287.1 | 247.1 | 241.3 | 329.8 | 261.9
962 | 872 | 526.5 | 420.8 | 461.9 | 416.5 | 303.5 | 287.2 | 247.3 | 241.7 | 330.1 | 262.2
963 | 873 | 526.5 | 420.9 | 462.1 | 416.6 | 303.8 | 287.4 | 247.6 | 242.1 | 330.4 | 262.6
964 | 874 | 526.5 | 421 | 462.2 | 416.8 | 304 | 287.6 | 247.9 | 242.5 | 330.7 | 262.9
965 | 875 | 526.5 | 421.2 | 462.4 | 416.9 | 304.2 | 287.9 | 248.2 | 242.8 | 331 | 263.2
966 | 876 | 526.5 | 421.3 | 462.5 | 417.1 | 304.5 | 288.2 | 248.5 | 243.1 | 331.3 | 263.6
967 | 877 | 526.5 | 421.5 | 462.6 | 417.2 | 304.9 | 288.5 | 248.8 | 243.4 | 331.6 | 264.1
968 | 878 | 526.4 | 421.6 | 462.7 | 417.4 | 305.2 | 288.8 | 249 | 243.7 | 331.8 | 264.5
969 | 879 | 526.4 | 421.8 | 462.9 | 417.5 | 305.5 | 289.1 | 249.3 | 244 | 332.1 | 264.8
970 | 880 | 526.3 | 422 | 462.9 | 417.7 | 305.9 | 289.4 | 249.6 | 244.4 | 332.3 | 265.2
971 | 881 | 526.3 | 422.1 | 463 | 417.9 | 306 | 289.7 | 249.9 | 244.7 | 332.6 | 265.6
972 | 882 | 526.3 | 422.3 | 463.1 | 418 | 306 | 290.1 | 250.2 | 245 | 332.9 | 266
973 | 883 | 526.2 | 422.5 | 463.2 | 418.2 | 306.2 | 290.4 | 250.5 | 245.4 | 333.2 | 266.3
974 | 884 | 526.2 | 422.6 | 463.3 | 418.3 | 306.6 | 290.8 | 250.7 | 245.7 | 333.4 | 266.7
975 | 885 | 526.1 | 422.8 | 463.4 | 418.5 | 307 | 291.1 | 251 | 246 | 333.7 | 267
976 | 886 | 526.1 | 423 | 463.5 | 418.7 | 307.5 | 291.4 | 251.3 | 246.3 | 334 | 267.4
977 | 887 | 526.1 | 423.1 | 463.6 | 418.8 | 308 | 291.7 | 251.6 | 246.6 | 334.3 | 267.7
978 | 888 | 526.1 | 423.3 | 463.8 | 418.9 | 308.4 | 292 | 251.9 | 247 | 334.6 | 268
979 | 889 | 526 | 423.4 | 463.9 | 419.1 | 308.8 | 292.3 | 252.1 | 247.4 | 334.9 | 268.4
980 | 890 | 526 | 423.6 | 463.9 | 419.3 | 309.1 | 292.6 | 252.4 | 247.7 | 335.2 | 268.8
981 | 891 | 526 | 423.8 | 464 | 419.4 | 309.6 | 293 | 252.7 | 248 | 335.5 | 269.3
982 | 892 | 526 | 423.9 | 464.2 | 419.5 | 309.8 | 293.2 | 252.9 | 248.3 | 335.8 | 269.7
983 | 893 | 526 | 424.1 | 464.3 | 419.7 | 310.4 | 293.5 | 253.2 | 248.6 | 336.1 | 270
984 | 894 | 526 | 424.2 | 464.4 | 419.9 | 310.7 | 293.8 | 253.5 | 248.8 | 336.4 | 270.4
985 | 895 | 526 | 424.4 | 464.5 | 420 | 311 | 294 | 253.8 | 249.1 | 336.7 | 270.8
986 | 896 | 526 | 424.5 | 464.7 | 420.1 | 311.3 | 294.1 | 254.1 | 249.4 | 337 | 271.1
987 | 897 | 526 | 424.6 | 464.8 | 420.3 | 311.7 | 294.4 | 254.3 | 249.7 | 337.3 | 271.4
988 | 898 | 526 | 424.8 | 464.9 | 420.4 | 312 | 294.7 | 254.6 | 250 | 337.6 | 271.8
989 | 899 | 526 | 424.9 | 465 | 420.6 | 312.3 | 295.1 | 254.9 | 250.3 | 337.9 | 272.1
990 | 900 | 526 | 425.1 | 465.1 | 420.7 | 312.7 | 295.5 | 255.2 | 250.6 | 338.2 | 272.5
991 | 901 | 526 | 425.3 | 465.2 | 420.9 | 312.9 | 295.8 | 255.4 | 250.9 | 338.5 | 272.9
992 | 902 | 526 | 425.4 | 465.3 | 421.1 | 313.4 | 296.2 | 255.7 | 251.2 | 338.8 | 273.3
993 | 903 | 526 | 425.6 | 465.4 | 421.2 | 313.7 | 296.5 | 256 | 251.5 | 339.1 | 273.8
994 | 904 | 526 | 425.7 | 465.5 | 421.4 | 314 | 296.8 | 256.3 | 251.8 | 339.3 | 274.1
995 | 905 | 526.1 | 425.8 | 465.7 | 421.5 | 314.3 | 297.1 | 256.6 | 252.1 | 339.6 | 274.6
996 | 906 | 526.1 | 426 | 465.8 | 421.6 | 314.4 | 297.5 | 256.9 | 252.4 | 340 | 275
997 | 907 | 526.2 | 426.1 | 465.9 | 421.8 | 314.4 | 297.8 | 257.1 | 252.6 | 340.3 | 275.3
998 | 908 | 526.2 | 426.3 | 466 | 421.9 | 314.7 | 298.1 | 257.4 | 252.9 | 340.6 | 275.7
999 | 909 | 526.3 | 426.4 | 466.1 | 422 | 315 | 298.5 | 257.7 | 253.2 | 340.9 | 276
1000 | 910 | 526.3 | 426.6 | 466.3 | 422.2 | 315.2 | 298.8 | 257.9 | 253.5 | 341.2 | 276.4
1001 | 911 | 526.4 | 426.7 | 466.4 | 422.3 | 315.3 | 299 | 258.2 | 253.8 | 341.5 | 276.7
1002 | 912 | 526.4 | 426.9 | 466.5 | 422.5 | 315.5 | 299.4 | 258.5 | 254.1 | 341.8 | 277.1
1003 | 913 | 526.5 | 427 | 466.6 | 422.6 | 315.9 | 299.7 | 258.8 | 254.4 | 342.1 | 277.5
1004 | 914 | 526.6 | 427.1 | 466.7 | 422.7 | 316.2 | 299.9 | 259 | 254.7 | 342.4 | 277.9
1005 | 915 | 526.6 | 427.3 | 466.8 | 422.9 | 316.6 | 300.2 | 259.3 | 254.9 | 342.7 | 278.2
1006 | 916 | 526.7 | 427.4 | 467 | 423 | 316.9 | 300.5 | 259.6 | 255.1 | 343 | 278.6
1007 | 917 | 526.7 | 427.6 | 467.1 | 423.2 | 317 | 301 | 259.9 | 255.5 | 343.3 | 279
1008 | 918 | 526.7 | 427.7 | 467.1 | 423.3 | 317.4 | 301.4 | 260.2 | 255.8 | 343.5 | 279.4
1009 | 919 | 526.7 | 427.9 | 467.2 | 423.5 | 317.6 | 301.8 | 260.4 | 256.1 | 343.8 | 279.8
1010 | 920 | 526.8 | 428 | 467.4 | 423.6 | 317.8 | 302.2 | 260.7 | 256.4 | 344.1 | 280.2
1011 | 921 | 526.7 | 428.1 | 467.5 | 423.7 | 318.1 | 302.5 | 261 | 256.7 | 344.4 | 280.6
1012 | 922 | 526.7 | 428.3 | 467.6 | 423.9 | 318.4 | 302.9 | 261.3 | 257 | 344.7 | 280.9
1013 | 923 | 526.7 | 428.4 | 467.7 | 424 | 318.6 | 303.3 | 261.6 | 257.2 | 344.9 | 281.3
1014 | 924 | 526.7 | 428.6 | 467.8 | 424.2 | 318.9 | 303.7 | 261.8 | 257.5 | 345.2 | 281.6
1015 | 925 | 526.6 | 428.7 | 467.9 | 424.3 | 319.4 | 304 | 262.1 | 257.8 | 345.4 | 282
1016 | 926 | 526.6 | 428.8 | 468 | 424.5 | 319.7 | 304.2 | 262.4 | 258.1 | 345.7 | 282.3
1017 | 927 | 526.6 | 429 | 468.1 | 424.6 | 320.1 | 304.5 | 262.6 | 258.4 | 345.9 | 282.7
1018 | 928 | 526.5 | 429.1 | 468.2 | 424.8 | 320.2 | 304.8 | 262.9 | 258.7 | 346.2 | 283
1019 | 929 | 526.4 | 429.3 | 468.3 | 424.9 | 320.2 | 305.2 | 263.2 | 259 | 346.4 | 283.4
1020 | 930 | 526.4 | 429.4 | 468.5 | 425 | 319.9 | 305.5 | 263.5 | 259.4 | 346.6 | 283.8
1021 | 931 | 526.3 | 429.5 | 468.5 | 425.2 | 320 | 305.9 | 263.7 | 259.6 | 346.8 | 284.1
1022 | 932 | 526.3 | 429.7 | 468.6 | 425.3 | 319.9 | 306.1 | 264 | 260 | 347.1 | 284.4
1023 | 933 | 526.3 | 429.8 | 468.7 | 425.5 | 319.8 | 306.3 | 264.3 | 260.3 | 347.3 | 284.8
1024 | 934 | 526.2 | 430 | 468.8 | 425.6 | 319.8 | 306.7 | 264.6 | 260.6 | 347.5 | 285.1
1025 | 935 | 526.2 | 430.1 | 468.9 | 425.7 | 319.8 | 307 | 264.9 | 261 | 347.8 | 285.4
1026 | 936 | 526.2 | 430.2 | 469 | 425.9 | 319.9 | 307.3 | 265.1 | 261.3 | 348 | 285.8
1027 | 937 | 526.2 | 430.4 | 469.1 | 426 | 320.1 | 307.6 | 265.4 | 261.6 | 348.2 | 286.2
1028 | 938 | 526.2 | 430.5 | 469.2 | 426.1 | 320.5 | 307.9 | 265.7 | 262 | 348.5 | 286.6
1029 | 939 | 526.2 | 430.7 | 469.2 | 426.3 | 320.8 | 308.3 | 265.9 | 262.4 | 348.7 | 286.9
1030 | 940 | 526.2 | 430.8 | 469.3 | 426.4 | 321.2 | 308.6 | 266.2 | 262.8 | 348.9 | 287.2
1031 | 941 | 526.2 | 430.9 | 469.4 | 426.5 | 321.2 | 308.9 | 266.5 | 263.1 | 349.2 | 287.6
1032 | 942 | 526.2 | 431.1 | 469.5 | 426.7 | 321.1 | 309.2 | 266.8 | 263.3 | 349.4 | 288.1
1033 | 943 | 526.2 | 431.2 | 469.6 | 426.8 | 321.4 | 309.5 | 267 | 263.6 | 349.6 | 288.4
1034 | 944 | 526.2 | 431.4 | 469.7 | 426.9 | 321.8 | 309.8 | 267.3 | 263.9 | 349.9 | 288.8
1035 | 945 | 526.2 | 431.5 | 469.8 | 427.1 | 322.2 | 310 | 267.6 | 264.2 | 350.1 | 289.2
1036 | 946 | 526.2 | 431.6 | 469.8 | 427.2 | 322.7 | 310.3 | 267.9 | 264.5 | 350.4 | 289.5
1037 | 947 | 526.1 | 431.8 | 470 | 427.3 | 323 | 310.7 | 268.2 | 264.8 | 350.6 | 289.9
1038 | 948 | 526.1 | 431.9 | 470 | 427.5 | 323.3 | 310.9 | 268.4 | 265.1 | 350.9 | 290.2
1039 | 949 | 526.1 | 432 | 470.1 | 427.6 | 323.4 | 311.2 | 268.7 | 265.4 | 351.1 | 290.4
1040 | 950 | 526 | 432.2 | 470.2 | 427.7 | 323.7 | 311.5 | 269 | 265.7 | 351.4 | 290.8
1041 | 951 | 526 | 432.3 | 470.3 | 427.9 | 324.2 | 311.8 | 269.3 | 266 | 351.6 | 291.1
1042 | 952 | 526 | 432.4 | 470.4 | 428 | 324.5 | 312.1 | 269.5 | 266.3 | 351.8 | 291.5
1043 | 953 | 525.9 | 432.6 | 470.5 | 428.1 | 324.7 | 312.5 | 269.8 | 266.6 | 352.1 | 291.8
1044 | 954 | 525.9 | 432.7 | 470.6 | 428.3 | 325 | 312.8 | 270.1 | 266.9 | 352.3 | 292.1
1045 | 955 | 525.9 | 432.8 | 470.7 | 428.4 | 324.9 | 313.2 | 270.4 | 267.2 | 352.6 | 292.4
1046 | 956 | 525.9 | 432.9 | 470.8 | 428.5 | 325 | 313.5 | 270.7 | 267.5 | 352.8 | 292.7
1047 | 957 | 525.9 | 433.1 | 470.9 | 428.7 | 325.4 | 313.9 | 270.9 | 267.8 | 353.1 | 293
1048 | 958 | 525.9 | 433.2 | 470.9 | 428.8 | 325.9 | 314.1 | 271.2 | 268.1 | 353.3 | 293.4
1049 | 959 | 525.9 | 433.4 | 471 | 428.9 | 326.1 | 314.4 | 271.5 | 268.3 | 353.6 | 293.7
1050 | 960 | 525.8 | 433.5 | 471.1 | 429.1 | 326.5 | 314.8 | 271.8 | 268.6 | 353.8 | 293.9
1051 | 961 | 525.8 | 433.6 | 471.1 | 429.2 | 326.5 | 315.1 | 272.1 | 268.9 | 354 | 294.2
1052 | 962 | 525.8 | 433.8 | 471.3 | 429.3 | 326.5 | 315.4 | 272.4 | 269.2 | 354.3 | 294.6
1053 | 963 | 525.8 | 433.9 | 471.4 | 429.5 | 326.6 | 315.7 | 272.7 | 269.6 | 354.4 | 294.9
1054 | 964 | 525.8 | 434 | 471.6 | 429.6 | 326.7 | 315.9 | 273 | 269.9 | 354.6 | 294.9
1055 | 965 | 525.8 | 434.1 | 471.7 | 429.7 | 326.9 | 316.2 | 273.2 | 270.3 | 354.8 | 295.1
1056 | 966 | 525.8 | 434.1 | 471.9 | 429.8 | 327 | 316.5 | 273.6 | 270.5 | 354.9 | 294.9
1057 | 967 | 525.9 | 434.3 | 472 | 429.9 | 327.3 | 316.9 | 273.9 | 270.7 | 355.1 | 294.9
1058 | 968 | 525.9 | 434.4 | 472.1 | 430 | 327.3 | 317.2 | 274.2 | 271 | 355.3 | 295.2
1059 | 969 | 525.9 | 434.5 | 472.1 | 430.2 | 327.4 | 317.5 | 274.5 | 271.3 | 355.4 | 295.5
1060 | 970 | 525.9 | 434.7 | 472.2 | 430.3 | 327.5 | 317.8 | 274.8 | 271.6 | 355.6 | 295.9
1061 | 971 | 525.8 | 434.8 | 472.2 | 430.4 | 327.8 | 318.2 | 275.1 | 271.9 | 355.7 | 296.4
1062 | 972 | 525.8 | 435 | 472.3 | 430.6 | 328 | 318.5 | 275.4 | 272.2 | 355.9 | 296.8
1063 | 973 | 525.9 | 435.1 | 472.3 | 430.7 | 328.4 | 318.8 | 275.7 | 272.5 | 356.1 | 297.3
1064 | 974 | 525.9 | 435.2 | 472.4 | 430.8 | 328.9 | 319.1 | 276 | 272.8 | 356.3 | 297.7
1065 | 975 | 525.9 | 435.4 | 472.5 | 431 | 329.3 | 319.4 | 276.3 | 273.1 | 356.4 | 298
1066 | 976 | 525.9 | 435.5 | 472.6 | 431.1 | 329.5 | 319.6 | 276.7 | 273.3 | 356.5 | 298.4
1067 | 977 | 525.9 | 435.6 | 472.7 | 431.2 | 329.7 | 319.8 | 277 | 273.5 | 356.6 | 298.6
1068 | 978 | 525.9 | 435.7 | 472.8 | 431.3 | 330.1 | 320 | 277.3 | 273.8 | 356.6 | 299
1069 | 979 | 525.9 | 435.8 | 472.9 | 431.4 | 330.5 | 320.1 | 277.7 | 274.1 | 356.7 | 299.3
1070 | 980 | 525.9 | 435.9 | 473 | 431.5 | 330.8 | 320.2 | 278 | 274.4 | 356.8 | 299.7
1071 | 981 | 525.9 | 436.1 | 473.1 | 431.7 | 331 | 320.2 | 278.3 | 274.7 | 356.8 | 300
1072 | 982 | 525.9 | 436.2 | 473.2 | 431.8 | 331.2 | 320.2 | 278.6 | 275 | 356.9 | 300.3
1073 | 983 | 525.9 | 436.3 | 473.4 | 431.9 | 331.5 | 320.2 | 278.9 | 275.3 | 357 | 300.6
1074 | 984 | 525.9 | 436.4 | 473.4 | 432 | 332 | 320.4 | 279.3 | 275.6 | 357 | 300.9
1075 | 985 | 525.9 | 436.5 | 473.5 | 432.1 | 332.2 | 320.7 | 279.6 | 275.9 | 357 | 301.3
1076 | 986 | 525.9 | 436.6 | 473.6 | 432.3 | 332.3 | 320.9 | 279.9 | 276.3 | 357.1 | 301.6
1077 | 987 | 525.9 | 436.7 | 473.7 | 432.4 | 332.7 | 321.1 | 280.2 | 276.5 | 357.4 | 301.9
1078 | 988 | 525.9 | 436.9 | 473.7 | 432.5 | 333.2 | 321.2 | 280.5 | 276.8 | 357.5 | 302.2
1079 | 989 | 525.9 | 437 | 473.8 | 432.6 | 333.4 | 321.4 | 280.9 | 277.1 | 357.6 | 302.4
1080 | 990 | 525.9 | 437.1 | 473.9 | 432.8 | 333.9 | 321.5 | 281.2 | 277.4 | 357.7 | 302.7
1081 | 991 | 525.9 | 437.2 | 473.9 | 432.9 | 334.1 | 321.6 | 281.5 | 277.7 | 358 | 302.9
1082 | 992 | 525.9 | 437.4 | 474 | 433 | 334.5 | 321.9 | 281.8 | 278 | 358.4 | 303.1
1083 | 993 | 525.9 | 437.5 | 474.1 | 433.1 | 335 | 322.1 | 282.2 | 278.3 | 358.5 | 303.3
1084 | 994 | 525.9 | 437.6 | 474.2 | 433.2 | 335.1 | 322.2 | 282.5 | 278.7 | 358.5 | 303.5
1085 | 995 | 525.9 | 437.7 | 474.3 | 433.4 | 335.7 | 322.4 | 282.8 | 279 | 358.5 | 303.7
1086 | 996 | 525.9 | 437.8 | 474.4 | 433.5 | 336.3 | 322.6 | 283.2 | 279.3 | 358.4 | 304
1087 | 997 | 525.9 | 437.9 | 474.4 | 433.6 | 336.6 | 322.8 | 283.5 | 279.7 | 358.4 | 304.2
1088 | 998 | 525.9 | 438 | 474.5 | 433.7 | 336.9 | 323 | 283.8 | 280 | 358.3 | 304.4
1089 | 999 | 525.9 | 438.2 | 474.6 | 433.8 | 337.4 | 323.3 | 284.1 | 280.4 | 358.4 | 304.6
1090 | 1000 | 526 | 438.3 | 474.7 | 434 | 337.6 | 323.5 | 284.5 | 280.7 | 358.5 | 304.9
1091 | 1001 | 525.9 | 438.4 | 474.7 | 434.1 | 338 | 323.8 | 284.8 | 281.2 | 358.6 | 305.1
1092 | 1002 | 526 | 438.5 | 474.8 | 434.2 | 338.6 | 324.2 | 285.1 | 281.6 | 358.7 | 305.4
1093 | 1003 | 526 | 438.7 | 474.8 | 434.3 | 338.9 | 324.6 | 285.4 | 282 | 358.9 | 305.7
1094 | 1004 | 526 | 438.7 | 474.9 | 434.4 | 339.3 | 324.9 | 285.8 | 282.3 | 358.9 | 305.9
1095 | 1005 | 526 | 438.9 | 475 | 434.6 | 339.5 | 325.4 | 286.1 | 282.5 | 358.9 | 306.2
1096 | 1006 | 526 | 439 | 475.1 | 434.7 | 340.1 | 325.9 | 286.4 | 282.8 | 358.9 | 306.4
1097 | 1007 | 526 | 439.1 | 475.2 | 434.8 | 340.2 | 326.3 | 286.7 | 283 | 359 | 306.6
1098 | 1008 | 526.1 | 439.2 | 475.3 | 434.9 | 340.6 | 326.8 | 287.1 | 283.3 | 359.1 | 306.8
1099 | 1009 | 526.1 | 439.3 | 475.4 | 435 | 341.2 | 327.2 | 287.4 | 283.5 | 359.2 | 307
1100 | 1010 | 526.1 | 439.4 | 475.4 | 435.1 | 341.7 | 327.7 | 287.7 | 283.8 | 359.2 | 307.3
1101 | 1011 | 526.1 | 439.5 | 475.5 | 435.2 | 342 | 328.1 | 288 | 284.1 | 359.2 | 307.6
1102 | 1012 | 526.1 | 439.6 | 475.6 | 435.3 | 342.6 | 328.5 | 288.3 | 284.4 | 359.4 | 307.9
1103 | 1013 | 526.1 | 439.7 | 475.7 | 435.5 | 343.1 | 328.9 | 288.7 | 284.6 | 359.3 | 308.2
1104 | 1014 | 526.1 | 439.8 | 475.7 | 435.6 | 343.5 | 329.3 | 289 | 285 | 359.2 | 308.5
1105 | 1015 | 526.1 | 440 | 475.8 | 435.7 | 343.9 | 329.7 | 289.3 | 285.3 | 359.4 | 308.7
1106 | 1016 | 526.1 | 440.1 | 475.9 | 435.8 | 344.2 | 330.1 | 289.6 | 285.6 | 359.5 | 309
1107 | 1017 | 526.1 | 440.2 | 475.9 | 435.9 | 344.8 | 330.5 | 290 | 286.1 | 359.7 | 309.2
1108 | 1018 | 526.1 | 440.3 | 476 | 436 | 345.2 | 330.8 | 290.3 | 286.6 | 359.9 | 309.4
1109 | 1019 | 526.1 | 440.4 | 476 | 436.2 | 345.6 | 331.2 | 290.6 | 286.9 | 360 | 309.6
1110 | 1020 | 526.1 | 440.5 | 476.1 | 436.3 | 346.1 | 331.6 | 290.9 | 287.2 | 360.3 | 309.8
1111 | 1021 | 526.1 | 440.6 | 476.2 | 436.4 | 346.5 | 331.9 | 291.3 | 287.4 | 360.4 | 310
1112 | 1022 | 526.2 | 440.8 | 476.2 | 436.5 | 347 | 332.2 | 291.6 | 287.5 | 360.5 | 309.9
1113 | 1023 | 526.2 | 440.9 | 476.3 | 436.6 | 347.3 | 332.5 | 292 | 287.7 | 360.7 | 310.2
1114 | 1024 | 526.2 | 441 | 476.4 | 436.7 | 347.5 | 332.9 | 292.3 | 287.9 | 360.9 | 310.5
1115 | 1025 | 526.2 | 441.1 | 476.5 | 436.8 | 347.8 | 333.2 | 292.6 | 288.1 | 361 | 310.8
1116 | 1026 | 526.2 | 441.2 | 476.5 | 436.9 | 348.2 | 333.5 | 293 | 288.3 | 361.1 | 311
1117 | 1027 | 526.3 | 441.3 | 476.6 | 437 | 348.7 | 333.8 | 293.3 | 288.6 | 361.2 | 311.1
1118 | 1028 | 526.3 | 441.4 | 476.7 | 437.1 | 349 | 334.1 | 293.6 | 288.9 | 361.3 | 311.4
1119 | 1029 | 526.3 | 441.5 | 476.8 | 437.3 | 349.4 | 334.5 | 293.9 | 289.2 | 361.5 | 311.6
1120 | 1030 | 526.3 | 441.6 | 476.9 | 437.4 | 349.7 | 334.8 | 294.2 | 289.6 | 361.8 | 312
1121 | 1031 | 526.3 | 441.7 | 476.9 | 437.5 | 350 | 335.2 | 294.6 | 290 | 362 | 312.2
1122 | 1032 | 526.3 | 441.8 | 477 | 437.6 | 350.4 | 335.5 | 294.9 | 290.2 | 362.1 | 312.3
1123 | 1033 | 526.3 | 441.9 | 477.1 | 437.7 | 350.6 | 335.8 | 295.2 | 290.4 | 362.2 | 312.5
1124 | 1034 | 526.3 | 442 | 477.1 | 437.8 | 350.9 | 336.1 | 295.5 | 290.7 | 362.3 | 312.4
1125 | 1035 | 526.2 | 442.1 | 477.2 | 437.9 | 351.1 | 336.4 | 295.8 | 291 | 362.5 | 312.4
1126 | 1036 | 526.2 | 442.2 | 477.3 | 438 | 351.5 | 336.7 | 296.1 | 291.3 | 362.6 | 312.5
1127 | 1037 | 526.2 | 442.3 | 477.3 | 438.1 | 351.8 | 337 | 296.5 | 291.5 | 362.5 | 312.8
1128 | 1038 | 526.2 | 442.4 | 477.4 | 438.2 | 352.1 | 337.3 | 296.8 | 291.8 | 362.3 | 313
1129 | 1039 | 526.2 | 442.5 | 477.5 | 438.3 | 352.3 | 337.6 | 297.1 | 292 | 362.3 | 313.3
1130 | 1040 | 526.2 | 442.6 | 477.6 | 438.4 | 352.5 | 337.8 | 297.4 | 292.2 | 362.4 | 313.5
1131 | 1041 | 526.1 | 442.7 | 477.6 | 438.5 | 352.8 | 338.1 | 297.8 | 292.5 | 362.6 | 313.7
1132 | 1042 | 526.1 | 442.8 | 477.7 | 438.6 | 353 | 338.3 | 298.1 | 292.9 | 362.9 | 313.8
1133 | 1043 | 526 | 442.9 | 477.7 | 438.7 | 353.3 | 338.6 | 298.4 | 293.2 | 363.2 | 314
1134 | 1044 | 526 | 443.1 | 477.7 | 438.9 | 353.6 | 338.9 | 298.7 | 293.4 | 363.4 | 314.3
1135 | 1045 | 526 | 443.2 | 477.8 | 439 | 353.8 | 339.2 | 299 | 293.7 | 363.7 | 314.6
1136 | 1046 | 526 | 443.3 | 477.9 | 439.1 | 354.1 | 339.5 | 299.3 | 294 | 363.9 | 314.9
1137 | 1047 | 526 | 443.4 | 477.9 | 439.2 | 354.5 | 339.8 | 299.7 | 294.3 | 364.1 | 315.3
1138 | 1048 | 526 | 443.5 | 478 | 439.3 | 354.8 | 340.1 | 300 | 294.5 | 364.3 | 315.7
1139 | 1049 | 526 | 443.6 | 478.1 | 439.4 | 355.1 | 340.4 | 300.3 | 294.8 | 364.5 | 316
1140 | 1050 | 526 | 443.7 | 478.2 | 439.5 | 355.4 | 340.7 | 300.6 | 295.2 | 364.7 | 316.2
1141 | 1051 | 526 | 443.8 | 478.2 | 439.6 | 355.8 | 341 | 300.9 | 295.4 | 364.9 | 316.5
1142 | 1052 | 526.1 | 443.9 | 478.3 | 439.7 | 356.2 | 341.3 | 301.2 | 295.7 | 365.1 | 316.7
1143 | 1053 | 526 | 444 | 478.4 | 439.8 | 356.4 | 341.6 | 301.5 | 296 | 365.2 | 316.9
1144 | 1054 | 526 | 444.1 | 478.4 | 439.9 | 356.7 | 341.8 | 301.9 | 296.3 | 365.3 | 317.1
1145 | 1055 | 526 | 444.2 | 478.5 | 440 | 357 | 342.1 | 302.2 | 296.5 | 365.4 | 317.3
1146 | 1056 | 526 | 444.3 | 478.5 | 440.1 | 357.5 | 342.4 | 302.5 | 296.8 | 365.4 | 317.5
1147 | 1057 | 526 | 444.4 | 478.6 | 440.2 | 357.9 | 342.6 | 302.8 | 297.1 | 365.6 | 317.7
1148 | 1058 | 526 | 444.5 | 478.6 | 440.3 | 358.2 | 342.9 | 303.1 | 297.4 | 365.7 | 317.9
1149 | 1059 | 526 | 444.6 | 478.7 | 440.4 | 358.4 | 343.2 | 303.4 | 297.8 | 365.9 | 318.3
1150 | 1060 | 525.9 | 444.7 | 478.8 | 440.5 | 358.7 | 343.5 | 303.8 | 298.1 | 365.9 | 318.6
1151 | 1061 | 525.9 | 444.8 | 478.8 | 440.6 | 359.1 | 343.8 | 304.1 | 298.4 | 366 | 318.9
1152 | 1062 | 525.9 | 444.9 | 478.9 | 440.7 | 359.4 | 344 | 304.4 | 298.8 | 365.9 | 319.2
1153 | 1063 | 525.9 | 445 | 478.9 | 440.8 | 359.7 | 344.3 | 304.7 | 299.2 | 365.8 | 319.5
1154 | 1064 | 526 | 445.1 | 479 | 440.8 | 359.9 | 344.5 | 305 | 299.5 | 366 | 319.9
1155 | 1065 | 526 | 445.2 | 479.1 | 440.9 | 360.2 | 344.8 | 305.3 | 299.8 | 366.2 | 320.2
1156 | 1066 | 526.1 | 445.3 | 479.1 | 441 | 360.5 | 345 | 305.6 | 300.2 | 366.5 | 320.5
1157 | 1067 | 526.1 | 445.3 | 479.2 | 441.1 | 360.7 | 345.3 | 306 | 300.8 | 366.8 | 320.7
1158 | 1068 | 526.1 | 445.5 | 479.3 | 441.2 | 361 | 345.6 | 306.3 | 301 | 367 | 320.8
1159 | 1069 | 526.1 | 445.5 | 479.3 | 441.3 | 361.3 | 345.8 | 306.6 | 301.3 | 367.2 | 321.2
1160 | 1070 | 526.1 | 445.6 | 479.4 | 441.4 | 361.6 | 346.1 | 306.9 | 301.7 | 367.3 | 321.4
1161 | 1071 | 526 | 445.7 | 479.4 | 441.5 | 361.9 | 346.4 | 307.2 | 302.1 | 367.4 | 321.6
1162 | 1072 | 526 | 445.9 | 479.5 | 441.6 | 362.1 | 346.7 | 307.5 | 302.3 | 367.4 | 321.8
1163 | 1073 | 526 | 445.9 | 479.6 | 441.7 | 362.3 | 346.9 | 307.9 | 302.6 | 367.5 | 322
1164 | 1074 | 526 | 446 | 479.6 | 441.8 | 362.6 | 347.2 | 308.2 | 302.9 | 367.7 | 322.2
1165 | 1075 | 525.9 | 446.1 | 479.7 | 441.9 | 362.9 | 347.5 | 308.5 | 303.1 | 367.7 | 322.3
1166 | 1076 | 525.9 | 446.2 | 479.7 | 442 | 363.2 | 347.8 | 308.8 | 303.4 | 367.9 | 322.5
1167 | 1077 | 525.9 | 446.3 | 479.8 | 442.1 | 363.4 | 348 | 309.1 | 303.6 | 368.1 | 322.9
1168 | 1078 | 526 | 446.4 | 479.9 | 442.2 | 363.6 | 348.3 | 309.4 | 304 | 368.3 | 323.1
1169 | 1079 | 526 | 446.5 | 479.9 | 442.3 | 364 | 348.6 | 309.7 | 304.3 | 368.5 | 323.3
1170 | 1080 | 525.9 | 446.6 | 480 | 442.4 | 364.3 | 348.9 | 310 | 304.7 | 368.7 | 323.5
1171 | 1081 | 525.9 | 446.7 | 480 | 442.5 | 364.6 | 349.2 | 310.4 | 304.9 | 368.8 | 323.6
1172 | 1082 | 525.9 | 446.8 | 480 | 442.6 | 364.9 | 349.5 | 310.7 | 305.1 | 368.9 | 323.8
1173 | 1083 | 525.9 | 446.9 | 480.1 | 442.7 | 365.3 | 349.8 | 311 | 305.3 | 368.9 | 323.9
1174 | 1084 | 525.9 | 447 | 480.1 | 442.8 | 365.6 | 350.1 | 311.3 | 305.6 | 368.9 | 324.2
1175 | 1085 | 525.8 | 447.1 | 480.2 | 442.9 | 366 | 350.4 | 311.6 | 305.9 | 369.2 | 324.4
1176 | 1086 | 525.8 | 447.2 | 480.2 | 443 | 366.4 | 350.7 | 311.9 | 306.1 | 369.4 | 324.7
1177 | 1087 | 525.8 | 447.3 | 480.3 | 443 | 366.8 | 351 | 312.2 | 306.3 | 369.6 | 324.9
1178 | 1088 | 525.7 | 447.4 | 480.4 | 443.1 | 367.3 | 351.2 | 312.5 | 306.5 | 369.8 | 325
1179 | 1089 | 525.7 | 447.5 | 480.4 | 443.2 | 367.7 | 351.5 | 312.8 | 306.8 | 370 | 325.2
1180 | 1090 | 525.7 | 447.6 | 480.5 | 443.3 | 367.9 | 351.8 | 313.1 | 307.1 | 370.2 | 325.4
1181 | 1091 | 525.7 | 447.7 | 480.5 | 443.4 | 368.2 | 352.1 | 313.5 | 307.3 | 370.4 | 325.6
1182 | 1092 | 525.7 | 447.7 | 480.6 | 443.5 | 368.6 | 352.4 | 313.8 | 307.4 | 370.6 | 325.8
1183 | 1093 | 525.7 | 447.8 | 480.6 | 443.6 | 368.9 | 352.7 | 314.1 | 307.6 | 370.7 | 326
1184 | 1094 | 525.7 | 447.9 | 480.7 | 443.7 | 369.3 | 353 | 314.4 | 307.7 | 370.9 | 326.2
1185 | 1095 | 525.7 | 448 | 480.7 | 443.8 | 369.7 | 353.2 | 314.7 | 307.9 | 371.1 | 326.4
1186 | 1096 | 525.7 | 448.1 | 480.8 | 443.8 | 370 | 353.5 | 315 | 308.1 | 371.3 | 326.6
1187 | 1097 | 525.8 | 448.2 | 480.9 | 443.9 | 370.4 | 353.8 | 315.3 | 308.4 | 371.5 | 326.8
1188 | 1098 | 525.8 | 448.3 | 481 | 444 | 370.6 | 354.1 | 315.6 | 308.7 | 371.8 | 327
1189 | 1099 | 525.8 | 448.3 | 481.1 | 444.1 | 370.9 | 354.3 | 315.9 | 309 | 372.1 | 327.1
1190 | 1100 | 525.8 | 448.4 | 481.2 | 444.2 | 371.1 | 354.6 | 316.2 | 309.2 | 372.4 | 327.3
1191 | 1101 | 525.8 | 448.5 | 481.2 | 444.3 | 371.4 | 354.9 | 316.5 | 309.2 | 372.8 | 327.5
1192 | 1102 | 525.8 | 448.6 | 481.2 | 444.4 | 371.6 | 355.2 | 316.8 | 309.5 | 373 | 327.7
1193 | 1103 | 525.8 | 448.8 | 481.2 | 444.5 | 371.8 | 355.5 | 317.1 | 309.8 | 373.3 | 328.1
1194 | 1104 | 525.8 | 448.8 | 481.3 | 444.5 | 372 | 355.7 | 317.4 | 310.2 | 373.6 | 328.3
1195 | 1105 | 525.8 | 448.9 | 481.4 | 444.6 | 372.2 | 356 | 317.7 | 310.4 | 373.6 | 328.5
1196 | 1106 | 525.8 | 449 | 481.4 | 444.7 | 372.4 | 356.3 | 318 | 310.6 | 373.6 | 328.7
1197 | 1107 | 525.8 | 449.1 | 481.4 | 444.8 | 372.5 | 356.5 | 318.3 | 310.8 | 373.8 | 329
1198 | 1108 | 525.8 | 449.2 | 481.5 | 444.9 | 372.6 | 356.8 | 318.6 | 311.2 | 374.1 | 329.2
1199 | 1109 | 525.8 | 449.3 | 481.6 | 445 | 373 | 357 | 318.9 | 311.8 | 374.3 | 329.4
1200 | 1110 | 525.8 | 449.4 | 481.6 | 445.1 | 374.2 | 357.3 | 319.2 | 312 | 374.4 | 329.6
1201 | 1111 | 525.9 | 449.5 | 481.6 | 445.2 | 374.6 | 357.6 | 319.5 | 312.1 | 374.6 | 329.7
1202 | 1112 | 525.9 | 449.5 | 481.7 | 445.2 | 375 | 357.8 | 319.8 | 312.2 | 374.8 | 329.9
1203 | 1113 | 525.9 | 449.6 | 481.8 | 445.3 | 375.5 | 358 | 320.1 | 312.4 | 375.1 | 330
1204 | 1114 | 525.9 | 449.7 | 481.8 | 445.4 | 375.7 | 358.2 | 320.4 | 312.5 | 375.4 | 330.2
1205 | 1115 | 525.9 | 449.8 | 481.9 | 445.5 | 376.1 | 358.5 | 320.7 | 312.6 | 375.8 | 330.4
1206 | 1116 | 525.9 | 449.9 | 481.9 | 445.6 | 376.2 | 358.8 | 321 | 312.8 | 376 | 330.6
1207 | 1117 | 525.9 | 450 | 482 | 445.7 | 376.6 | 359.1 | 321.3 | 313 | 376.2 | 330.7
1208 | 1118 | 525.9 | 450.1 | 482.1 | 445.7 | 376.8 | 359.4 | 321.6 | 313.2 | 376.3 | 330.8
1209 | 1119 | 525.9 | 450.2 | 482.1 | 445.8 | 376.9 | 359.7 | 321.9 | 313.6 | 376.6 | 331
1210 | 1120 | 525.9 | 450.2 | 482.2 | 445.9 | 376.9 | 360 | 322.2 | 313.9 | 376.8 | 331.3
1211 | 1121 | 525.9 | 450.3 | 482.2 | 446 | 377.1 | 360.3 | 322.5 | 314.3 | 377.1 | 331.4
1212 | 1122 | 525.9 | 450.4 | 482.2 | 446.1 | 377.3 | 360.6 | 322.8 | 314.8 | 377.2 | 331.6
1213 | 1123 | 525.9 | 450.5 | 482.3 | 446.2 | 377.4 | 360.9 | 323.1 | 315.1 | 377.6 | 331.9
1214 | 1124 | 525.9 | 450.6 | 482.3 | 446.3 | 377.6 | 361.2 | 323.4 | 315.4 | 377.7 | 332.1
1215 | 1125 | 525.9 | 450.7 | 482.4 | 446.4 | 377.9 | 361.5 | 323.7 | 315.4 | 378 | 332.3
1216 | 1126 | 525.9 | 450.8 | 482.4 | 446.4 | 378.2 | 361.8 | 324 | 315.5 | 378 | 332.4
1217 | 1127 | 525.9 | 450.9 | 482.5 | 446.5 | 378.4 | 362 | 324.2 | 315.7 | 378.3 | 332.6
1218 | 1128 | 525.9 | 451 | 482.5 | 446.6 | 378.6 | 362.3 | 324.5 | 315.8 | 378.4 | 332.8
1219 | 1129 | 525.8 | 451 | 482.6 | 446.7 | 378.7 | 362.6 | 324.8 | 316 | 378.4 | 333
1220 | 1130 | 525.9 | 451.1 | 482.6 | 446.8 | 378.9 | 362.9 | 325.1 | 316.4 | 378.7 | 333.3
1221 | 1131 | 525.9 | 451.2 | 482.6 | 446.9 | 379 | 363.1 | 325.4 | 316.8 | 378.9 | 333.5
1222 | 1132 | 525.9 | 451.3 | 482.7 | 447 | 379.3 | 363.4 | 325.7 | 317.4 | 379 | 333.7
1223 | 1133 | 525.9 | 451.4 | 482.8 | 447 | 379.6 | 363.6 | 326 | 317.5 | 379.3 | 333.9
1224 | 1134 | 525.9 | 451.4 | 482.9 | 447.1 | 379.8 | 363.9 | 326.3 | 317.7 | 379.4 | 334.1
1225 | 1135 | 525.9 | 451.5 | 482.9 | 447.2 | 380.1 | 364.2 | 326.6 | 318.2 | 379.6 | 334.2
1226 | 1136 | 525.9 | 451.6 | 482.9 | 447.3 | 380.3 | 364.5 | 326.9 | 318.5 | 379.8 | 334.4
1227 | 1137 | 525.9 | 451.7 | 483 | 447.3 | 380.5 | 364.8 | 327.2 | 318.8 | 379.9 | 334.6
1228 | 1138 | 525.9 | 451.8 | 483.1 | 447.4 | 380.8 | 365 | 327.5 | 319.1 | 380.2 | 334.7
1229 | 1139 | 525.9 | 451.9 | 483.1 | 447.5 | 381 | 365.3 | 327.7 | 319.3 | 380.3 | 334.9
1230 | 1140 | 525.9 | 451.9 | 483.2 | 447.6 | 381.2 | 365.6 | 328 | 319.3 | 380.6 | 335.2
1231 | 1141 | 525.9 | 452 | 483.2 | 447.7 | 381.4 | 365.9 | 328.3 | 319.4 | 380.6 | 335.4
1232 | 1142 | 525.9 | 452.1 | 483.2 | 447.8 | 381.7 | 366.3 | 328.6 | 319.7 | 380.9 | 335.6
1233 | 1143 | 525.9 | 452.2 | 483.3 | 447.8 | 381.9 | 366.6 | 328.9 | 319.9 | 381 | 335.8
1234 | 1144 | 525.9 | 452.3 | 483.3 | 447.9 | 382.1 | 366.8 | 329.2 | 320.2 | 381.2 | 336
1235 | 1145 | 525.8 | 452.4 | 483.3 | 448 | 382.6 | 367.2 | 329.5 | 320.5 | 381.3 | 336.3
1236 | 1146 | 525.8 | 452.5 | 483.4 | 448.1 | 383 | 367.5 | 329.8 | 320.8 | 381.6 | 336.4
1237 | 1147 | 525.8 | 452.5 | 483.5 | 448.2 | 383.3 | 367.8 | 330.1 | 321.2 | 381.7 | 336.7
1238 | 1148 | 525.7 | 452.6 | 483.5 | 448.2 | 383.5 | 368.2 | 330.3 | 321.5 | 382 | 336.8
1239 | 1149 | 525.7 | 452.7 | 483.5 | 448.3 | 383.8 | 368.6 | 330.6 | 321.8 | 382.3 | 337
1240 | 1150 | 525.7 | 452.8 | 483.6 | 448.4 | 384.1 | 368.9 | 330.9 | 322.1 | 382.5 | 337.2
1241 | 1151 | 525.6 | 452.9 | 483.7 | 448.5 | 384.3 | 369.2 | 331.2 | 322.3 | 382.7 | 337.4
1242 | 1152 | 525.6 | 453 | 483.7 | 448.5 | 384.5 | 369.6 | 331.5 | 322.5 | 383 | 337.6
1243 | 1153 | 525.6 | 453 | 483.7 | 448.6 | 384.8 | 369.9 | 331.8 | 322.6 | 383.3 | 337.7
1244 | 1154 | 525.6 | 453.1 | 483.8 | 448.7 | 385 | 370.3 | 332.1 | 322.8 | 383.6 | 337.9
1245 | 1155 | 525.6 | 453.2 | 483.9 | 448.8 | 385.3 | 370.6 | 332.4 | 323.2 | 383.7 | 338.1
1246 | 1156 | 525.6 | 453.3 | 483.9 | 448.9 | 385.4 | 371 | 332.7 | 323.5 | 384.1 | 338.2
1247 | 1157 | 525.7 | 453.4 | 483.9 | 448.9 | 385.6 | 371.3 | 333 | 323.9 | 384 | 338.4
1248 | 1158 | 525.7 | 453.4 | 484 | 449 | 385.8 | 371.7 | 333.2 | 324.2 | 384.2 | 338.6
1249 | 1159 | 525.7 | 453.5 | 484 | 449.1 | 386.1 | 372 | 333.5 | 324.6 | 384.3 | 338.8
1250 | 1160 | 525.7 | 453.6 | 484 | 449.2 | 386.3 | 372.4 | 333.8 | 324.8 | 384.5 | 338.9
1251 | 1161 | 525.7 | 453.7 | 484.1 | 449.2 | 386.6 | 372.7 | 334.1 | 324.8 | 384.7 | 339.1
1252 | 1162 | 525.7 | 453.8 | 484.2 | 449.3 | 386.9 | 373 | 334.4 | 325.1 | 384.8 | 339.1
1253 | 1163 | 525.7 | 453.9 | 484.2 | 449.4 | 387.2 | 373.4 | 334.7 | 325.4 | 384.9 | 339.3
1254 | 1164 | 525.7 | 453.9 | 484.2 | 449.5 | 387.5 | 373.7 | 335 | 325.7 | 385.1 | 339.5
1255 | 1165 | 525.6 | 454 | 484.3 | 449.6 | 387.9 | 374 | 335.3 | 325.9 | 385.5 | 339.7
1256 | 1166 | 525.6 | 454.1 | 484.4 | 449.6 | 388.3 | 374.3 | 335.6 | 326.1 | 385.8 | 339.9
1257 | 1167 | 525.6 | 454.1 | 484.4 | 449.7 | 388.7 | 374.6 | 335.9 | 326.3 | 386.1 | 340.1
1258 | 1168 | 525.6 | 454.2 | 484.4 | 449.8 | 389.2 | 374.9 | 336.2 | 326.5 | 386.2 | 340.3
1259 | 1169 | 525.6 | 454.3 | 484.5 | 449.9 | 389.5 | 375.2 | 336.4 | 326.7 | 386.5 | 340.4
1260 | 1170 | 525.6 | 454.4 | 484.5 | 449.9 | 389.9 | 375.5 | 336.7 | 326.9 | 386.7 | 340.6
1261 | 1171 | 525.5 | 454.5 | 484.6 | 450 | 390.3 | 375.9 | 337 | 327.1 | 386.6 | 340.8
1262 | 1172 | 525.5 | 454.5 | 484.6 | 450.1 | 390.8 | 376.2 | 337.3 | 327.4 | 387 | 340.9
1263 | 1173 | 525.5 | 454.6 | 484.6 | 450.2 | 391.2 | 376.5 | 337.6 | 327.7 | 387.1 | 341.1
1264 | 1174 | 525.5 | 454.7 | 484.6 | 450.3 | 391.6 | 376.7 | 337.9 | 328 | 387.5 | 341.4
1265 | 1175 | 525.6 | 454.8 | 484.7 | 450.3 | 392 | 377 | 338.2 | 328.2 | 387.6 | 341.6
1266 | 1176 | 525.6 | 454.9 | 484.8 | 450.4 | 392.4 | 377.2 | 338.5 | 328.5 | 388.2 | 341.8
1267 | 1177 | 525.6 | 454.9 | 484.8 | 450.5 | 392.7 | 377.5 | 338.8 | 328.7 | 388.5 | 342
1268 | 1178 | 525.6 | 455 | 484.8 | 450.6 | 393 | 377.8 | 339 | 329.1 | 388.6 | 342.2
1269 | 1179 | 525.6 | 455.1 | 484.9 | 450.6 | 393.3 | 378 | 339.3 | 329.4 | 388.9 | 342.4
1270 | 1180 | 525.6 | 455.2 | 484.9 | 450.7 | 393.6 | 378.3 | 339.6 | 329.6 | 389 | 342.5
1271 | 1181 | 525.6 | 455.3 | 485 | 450.8 | 393.9 | 378.6 | 339.9 | 329.9 | 389.1 | 342.7
1272 | 1182 | 525.6 | 455.3 | 485 | 450.9 | 394.2 | 378.9 | 340.2 | 330.2 | 389.3 | 342.9
1273 | 1183 | 525.6 | 455.4 | 485.1 | 450.9 | 394.4 | 379.2 | 340.5 | 330.5 | 389.4 | 343
1274 | 1184 | 525.6 | 455.5 | 485.1 | 451 | 394.7 | 379.4 | 340.8 | 330.8 | 389.5 | 343.2
1275 | 1185 | 525.6 | 455.6 | 485.1 | 451.1 | 394.9 | 379.7 | 341.1 | 331.2 | 389.6 | 343.4
1276 | 1186 | 525.6 | 455.6 | 485.2 | 451.2 | 395.2 | 380 | 341.4 | 331.4 | 389.7 | 343.6
1277 | 1187 | 525.6 | 455.7 | 485.3 | 451.2 | 395.4 | 380.3 | 341.7 | 331.7 | 389.7 | 343.8
1278 | 1188 | 525.6 | 455.8 | 485.3 | 451.3 | 395.7 | 380.5 | 341.9 | 332.1 | 389.9 | 343.9
1279 | 1189 | 525.6 | 455.9 | 485.3 | 451.4 | 395.9 | 380.8 | 342.2 | 332.4 | 390 | 344
1280 | 1190 | 525.6 | 455.9 | 485.4 | 451.4 | 396.1 | 381 | 342.5 | 332.7 | 390.3 | 343.4
1281 | 1191 | 525.6 | 456 | 485.5 | 451.5 | 396.4 | 381.3 | 342.8 | 333 | 390.5 | 343.6
1282 | 1192 | 525.6 | 456.1 | 485.5 | 451.6 | 396.6 | 381.5 | 343.1 | 333.3 | 390.7 | 343.6
1283 | 1193 | 525.6 | 456.1 | 485.6 | 451.7 | 396.9 | 381.8 | 343.4 | 333.6 | 390.9 | 343.7
1284 | 1194 | 525.7 | 456.2 | 485.6 | 451.7 | 397.2 | 382 | 343.7 | 333.9 | 391 | 343.8
1285 | 1195 | 525.7 | 456.3 | 485.6 | 451.8 | 397.5 | 382.3 | 344 | 334.2 | 391.1 | 343.9
1286 | 1196 | 525.7 | 456.4 | 485.6 | 451.9 | 397.7 | 382.5 | 344.3 | 334.5 | 391.3 | 344
1287 | 1197 | 525.7 | 456.5 | 485.7 | 452 | 397.9 | 382.7 | 344.6 | 334.9 | 391.4 | 344.2
1288 | 1198 | 525.7 | 456.5 | 485.7 | 452 | 398.2 | 383 | 344.9 | 335.2 | 391.5 | 344.3
1289 | 1199 | 525.7 | 456.6 | 485.7 | 452.1 | 398.4 | 383.2 | 345.2 | 335.5 | 391.6 | 344.5
1290 | 1200 | 525.8 | 456.7 | 485.8 | 452.2 | 398.6 | 383.4 | 345.5 | 335.8 | 391.8 | 344.7
1291 | 1201 | 525.8 | 456.8 | 485.9 | 452.3 | 398.9 | 383.7 | 345.7 | 336.1 | 391.8 | 344.8
1292 | 1202 | 525.7 | 456.8 | 485.9 | 452.3 | 399.1 | 383.9 | 346 | 336.4 | 391.9 | 344.9
1293 | 1203 | 525.7 | 456.9 | 486 | 452.4 | 399.3 | 384.1 | 346.3 | 336.6 | 392.1 | 345.1
1294 | 1204 | 525.7 | 457 | 486 | 452.5 | 399.6 | 384.3 | 346.6 | 336.9 | 392.2 | 345.1
1295 | 1205 | 525.7 | 457.1 | 486 | 452.5 | 399.9 | 384.6 | 346.9 | 337.3 | 392.3 | 345.2
1296 | 1206 | 525.7 | 457.1 | 486.1 | 452.6 | 400.1 | 384.8 | 347.2 | 337.6 | 392.5 | 345.3
1297 | 1207 | 525.7 | 457.2 | 486.1 | 452.7 | 400.3 | 385.1 | 347.5 | 337.8 | 392.7 | 345.6
1298 | 1208 | 525.7 | 457.3 | 486.2 | 452.7 | 400.5 | 385.3 | 347.8 | 338 | 392.8 | 345.7
1299 | 1209 | 525.7 | 457.4 | 486.2 | 452.8 | 400.7 | 385.5 | 348.1 | 338.3 | 392.9 | 345.8
1300 | 1210 | 525.7 | 457.4 | 486.2 | 452.9 | 400.9 | 385.8 | 348.3 | 338.5 | 393.1 | 345.7
1301 | 1211 | 525.6 | 457.5 | 486.3 | 453 | 401.1 | 386 | 348.6 | 338.8 | 393.2 | 345.9
1302 | 1212 | 525.7 | 457.5 | 486.3 | 453 | 401.3 | 386.3 | 348.9 | 339.1 | 393.3 | 346
1303 | 1213 | 525.7 | 457.6 | 486.4 | 453.1 | 401.5 | 386.6 | 349.2 | 339.4 | 393.5 | 346.2
1304 | 1214 | 525.7 | 457.7 | 486.4 | 453.2 | 401.7 | 386.9 | 349.5 | 339.6 | 393.6 | 346.3
1305 | 1215 | 525.7 | 457.8 | 486.5 | 453.2 | 401.9 | 387.2 | 349.8 | 339.9 | 393.7 | 346.4
1306 | 1216 | 525.7 | 457.8 | 486.5 | 453.3 | 402.1 | 387.4 | 350.1 | 340.2 | 393.9 | 346.6
1307 | 1217 | 525.7 | 457.9 | 486.6 | 453.4 | 402.4 | 387.7 | 350.4 | 340.6 | 394.1 | 346.7
1308 | 1218 | 525.8 | 458 | 486.6 | 453.5 | 402.6 | 388 | 350.7 | 340.9 | 394.3 | 346.8
1309 | 1219 | 525.8 | 458 | 486.7 | 453.5 | 402.8 | 388.3 | 351 | 341.2 | 394.4 | 347.1
1310 | 1220 | 525.7 | 458.1 | 486.7 | 453.6 | 402.9 | 388.6 | 351.2 | 341.5 | 394.6 | 347.3
1311 | 1221 | 525.7 | 458.1 | 486.8 | 453.6 | 403.1 | 388.9 | 351.5 | 341.8 | 394.7 | 347.3
1312 | 1222 | 525.7 | 458.3 | 486.8 | 453.7 | 403.3 | 389.2 | 351.8 | 342.1 | 394.9 | 347.2
1313 | 1223 | 525.7 | 458.3 | 486.9 | 453.8 | 403.4 | 389.5 | 352.1 | 342.5 | 395.1 | 347.4
1314 | 1224 | 525.6 | 458.4 | 486.9 | 453.9 | 403.6 | 389.8 | 352.4 | 342.8 | 395.3 | 347.5
1315 | 1225 | 525.6 | 458.4 | 486.9 | 453.9 | 403.8 | 390.2 | 352.7 | 343.2 | 395.5 | 347.4
1316 | 1226 | 525.6 | 458.5 | 487 | 454 | 404 | 390.5 | 353 | 343.6 | 395.6 | 347.7
1317 | 1227 | 525.6 | 458.6 | 487 | 454.1 | 404.2 | 390.9 | 353.3 | 344 | 396 | 347.7
1318 | 1228 | 525.6 | 458.7 | 487 | 454.1 | 404.1 | 391.2 | 353.6 | 344.3 | 396.2 | 348
1319 | 1229 | 525.6 | 458.7 | 487.1 | 454.2 | 404.1 | 391.5 | 353.8 | 344.7 | 396.4 | 348.1
1320 | 1230 | 525.6 | 458.8 | 487.1 | 454.3 | 404 | 391.8 | 354.1 | 345 | 396.6 | 348.3
1321 | 1231 | 525.6 | 458.9 | 487.1 | 454.3 | 404 | 392.2 | 354.4 | 345.3 | 396.8 | 348.5
1322 | 1232 | 525.6 | 458.9 | 487.2 | 454.4 | 404 | 392.5 | 354.7 | 345.7 | 396.9 | 348.7
1323 | 1233 | 525.6 | 459 | 487.2 | 454.5 | 404.1 | 392.9 | 355 | 346.1 | 397.1 | 348.8
1324 | 1234 | 525.6 | 459.1 | 487.3 | 454.6 | 404.1 | 393.2 | 355.3 | 346.4 | 397.1 | 348.8
1325 | 1235 | 525.6 | 459.1 | 487.3 | 454.6 | 404.2 | 393.6 | 355.6 | 346.8 | 397.3 | 349
1326 | 1236 | 525.6 | 459.2 | 487.4 | 454.7 | 404.3 | 393.9 | 355.9 | 347.1 | 397.5 | 349.2
1327 | 1237 | 525.6 | 459.3 | 487.4 | 454.8 | 404.4 | 394.3 | 356.2 | 347.5 | 397.7 | 349.7
1328 | 1238 | 525.6 | 459.3 | 487.5 | 454.8 | 404.4 | 394.6 | 356.5 | 347.8 | 397.9 | 349.9
1329 | 1239 | 525.6 | 459.4 | 487.5 | 454.9 | 404.5 | 395 | 356.7 | 348.1 | 398 | 350.1
1330 | 1240 | 525.6 | 459.5 | 487.5 | 455 | 404.6 | 395.4 | 357 | 348.5 | 398.2 | 350.4
1331 | 1241 | 525.6 | 459.5 | 487.5 | 455 | 404.7 | 395.8 | 357.3 | 348.9 | 398.4 | 350.7
1332 | 1242 | 525.6 | 459.6 | 487.6 | 455.1 | 404.8 | 396.1 | 357.6 | 349.3 | 398.5 | 350.9
1333 | 1243 | 525.5 | 459.7 | 487.6 | 455.2 | 404.9 | 396.5 | 357.9 | 349.6 | 398.7 | 351
1334 | 1244 | 525.5 | 459.7 | 487.7 | 455.2 | 405 | 396.9 | 358.2 | 349.9 | 398.8 | 351.3
1335 | 1245 | 525.5 | 459.8 | 487.7 | 455.3 | 405.1 | 397.3 | 358.5 | 350.2 | 399 | 351.5
1336 | 1246 | 525.5 | 459.8 | 487.8 | 455.3 | 405.2 | 397.7 | 358.8 | 350.6 | 399.2 | 351.6
1337 | 1247 | 525.5 | 459.9 | 487.8 | 455.4 | 405.4 | 398.1 | 359.1 | 350.9 | 399.3 | 351.7
1338 | 1248 | 525.5 | 460 | 487.9 | 455.5 | 405.6 | 398.5 | 359.4 | 351.3 | 399.5 | 351.9
1339 | 1249 | 525.5 | 460 | 487.9 | 455.6 | 405.7 | 398.9 | 359.7 | 351.6 | 399.6 | 352.1
1340 | 1250 | 525.5 | 460.1 | 487.9 | 455.6 | 405.9 | 399.3 | 360 | 351.9 | 399.8 | 352.4
1341 | 1251 | 525.5 | 460.2 | 487.9 | 455.7 | 406 | 399.7 | 360.3 | 352.3 | 400 | 352.6
1342 | 1252 | 525.5 | 460.2 | 488 | 455.8 | 406.2 | 400.1 | 360.6 | 352.6 | 400.1 | 352.8
1343 | 1253 | 525.5 | 460.3 | 488 | 455.8 | 406.3 | 400.4 | 360.8 | 352.9 | 400.3 | 352.8
1344 | 1254 | 525.5 | 460.4 | 488.1 | 455.9 | 406.5 | 400.9 | 361.1 | 353.2 | 400.5 | 353
1345 | 1255 | 525.6 | 460.4 | 488.2 | 456 | 406.6 | 401.4 | 361.5 | 353.5 | 400.7 | 353.3
1346 | 1256 | 525.6 | 460.5 | 488.2 | 456 | 406.7 | 401.9 | 361.8 | 353.9 | 400.9 | 353.6
1347 | 1257 | 525.6 | 460.6 | 488.2 | 456.1 | 406.9 | 402.4 | 362.1 | 354.2 | 401 | 353.8
1348 | 1258 | 525.6 | 460.6 | 488.2 | 456.2 | 407 | 402.8 | 362.4 | 354.5 | 401.2 | 354.1
1349 | 1259 | 525.6 | 460.7 | 488.3 | 456.2 | 407.1 | 403.3 | 362.7 | 354.9 | 401.3 | 354.2
1350 | 1260 | 525.6 | 460.7 | 488.3 | 456.3 | 407.2 | 403.7 | 363 | 355.2 | 401.5 | 354.4
1351 | 1261 | 525.6 | 460.8 | 488.4 | 456.4 | 407.4 | 404.2 | 363.3 | 355.6 | 401.6 | 354.7
1352 | 1262 | 525.6 | 460.9 | 488.4 | 456.4 | 407.5 | 404.7 | 363.6 | 355.9 | 401.8 | 354.9
1353 | 1263 | 525.7 | 460.9 | 488.5 | 456.5 | 407.7 | 405.2 | 363.9 | 356.2 | 401.9 | 355
1354 | 1264 | 525.7 | 461 | 488.5 | 456.6 | 407.9 | 405.7 | 364.2 | 356.6 | 402.1 | 355.2
1355 | 1265 | 525.7 | 461 | 488.6 | 456.6 | 408 | 406.1 | 364.5 | 356.9 | 402.2 | 355.4
1356 | 1266 | 525.7 | 461.1 | 488.5 | 456.7 | 408.2 | 406.6 | 364.9 | 357.3 | 402.3 | 355.6
1357 | 1267 | 525.7 | 461.2 | 488.6 | 456.7 | 408.3 | 407.1 | 365.2 | 357.6 | 402.4 | 355.8
1358 | 1268 | 525.7 | 461.3 | 488.6 | 456.8 | 408.5 | 407.5 | 365.5 | 357.9 | 402.5 | 355.8
1359 | 1269 | 525.7 | 461.3 | 488.7 | 456.9 | 408.7 | 408 | 365.8 | 358.2 | 402.6 | 355.9
1360 | 1270 | 525.7 | 461.3 | 488.7 | 456.9 | 408.9 | 408.4 | 366.1 | 358.4 | 402.7 | 356.1
1361 | 1271 | 525.8 | 461.4 | 488.8 | 457 | 409.1 | 408.9 | 366.4 | 358.8 | 402.8 | 356.1
1362 | 1272 | 525.8 | 461.5 | 488.8 | 457 | 409.3 | 409.3 | 366.7 | 359 | 402.9 | 356.2
1363 | 1273 | 525.8 | 461.5 | 488.9 | 457.1 | 409.5 | 409.8 | 367 | 359.3 | 403 | 356.4
1364 | 1274 | 525.8 | 461.6 | 488.9 | 457.2 | 409.7 | 410.2 | 367.4 | 359.5 | 403.2 | 356.5
1365 | 1275 | 525.8 | 461.7 | 488.9 | 457.2 | 409.9 | 410.7 | 367.7 | 359.8 | 403.4 | 356.6
1366 | 1276 | 525.8 | 461.7 | 489 | 457.3 | 410 | 411.1 | 368 | 360.1 | 403.6 | 356.7
1367 | 1277 | 525.8 | 461.7 | 489.1 | 457.4 | 410.2 | 411.5 | 368.3 | 360.4 | 403.7 | 357
1368 | 1278 | 525.8 | 461.8 | 489.1 | 457.4 | 410.5 | 412 | 368.5 | 360.7 | 403.9 | 357
1369 | 1279 | 525.8 | 461.9 | 489.1 | 457.5 | 410.7 | 412.4 | 368.8 | 361 | 404 | 357.1
1370 | 1280 | 525.7 | 462 | 489.1 | 457.6 | 410.9 | 412.9 | 369.1 | 361.4 | 404.1 | 357.3
1371 | 1281 | 525.8 | 462 | 489.1 | 457.6 | 411.1 | 413.3 | 369.4 | 361.7 | 404.3 | 357.4
1372 | 1282 | 525.8 | 462.1 | 489.1 | 457.7 | 411.3 | 413.7 | 369.6 | 362 | 404.6 | 357.5
1373 | 1283 | 525.8 | 462.2 | 489.2 | 457.8 | 411.5 | 414.1 | 369.9 | 362.3 | 404.8 | 357.7
1374 | 1284 | 525.8 | 462.2 | 489.2 | 457.8 | 411.7 | 414.5 | 370.1 | 362.6 | 405 | 357.8
1375 | 1285 | 525.8 | 462.3 | 489.2 | 457.9 | 412 | 414.9 | 370.4 | 362.9 | 405.2 | 357.9
1376 | 1286 | 525.8 | 462.4 | 489.2 | 458 | 412.2 | 415.3 | 370.6 | 363.1 | 405.3 | 358.1
1377 | 1287 | 525.8 | 462.4 | 489.3 | 458 | 412.4 | 415.7 | 370.9 | 363.3 | 405.5 | 358.3
1378 | 1288 | 525.8 | 462.5 | 489.3 | 458.1 | 412.6 | 416.1 | 371.1 | 363.6 | 405.8 | 358.4
1379 | 1289 | 525.8 | 462.5 | 489.3 | 458.2 | 412.8 | 416.5 | 371.3 | 363.9 | 405.9 | 358.6
1380 | 1290 | 525.8 | 462.6 | 489.4 | 458.2 | 413 | 416.9 | 371.5 | 364.1 | 406.1 | 358.9
1381 | 1291 | 525.8 | 462.7 | 489.4 | 458.3 | 413.3 | 417.3 | 371.7 | 364.4 | 406.2 | 359
1382 | 1292 | 525.8 | 462.7 | 489.4 | 458.3 | 413.4 | 417.6 | 371.9 | 364.7 | 406.3 | 359.2
1383 | 1293 | 525.7 | 462.8 | 489.5 | 458.4 | 413.6 | 418 | 372.1 | 364.9 | 406.6 | 359.5
1384 | 1294 | 525.7 | 462.8 | 489.5 | 458.5 | 413.9 | 418.3 | 372.3 | 365.1 | 406.6 | 359.6
1385 | 1295 | 525.7 | 462.9 | 489.6 | 458.5 | 414.1 | 418.6 | 372.4 | 365.4 | 406.7 | 359.8
1386 | 1296 | 525.7 | 462.9 | 489.6 | 458.6 | 414.3 | 418.9 | 372.6 | 365.7 | 406.7 | 360
1387 | 1297 | 525.6 | 463 | 489.6 | 458.6 | 414.5 | 419.2 | 372.8 | 366 | 406.8 | 360.1
1388 | 1298 | 525.6 | 463 | 489.7 | 458.7 | 414.7 | 419.5 | 372.9 | 366.2 | 406.8 | 360.3
1389 | 1299 | 525.6 | 463.1 | 489.7 | 458.8 | 414.9 | 419.8 | 373.1 | 366.5 | 406.9 | 360.4
1390 | 1300 | 525.6 | 463.1 | 489.8 | 458.8 | 415 | 420.1 | 373.2 | 366.7 | 407 | 360.6
1391 | 1301 | 525.7 | 463.2 | 489.8 | 458.9 | 415.2 | 420.4 | 373.3 | 366.9 | 407 | 360.8
1392 | 1302 | 525.7 | 463.2 | 489.9 | 458.9 | 415.4 | 420.6 | 373.5 | 367.2 | 407.1 | 360.9
1393 | 1303 | 525.7 | 463.3 | 489.9 | 459 | 415.6 | 420.9 | 373.6 | 367.4 | 407.3 | 361.1
1394 | 1304 | 525.7 | 463.4 | 489.9 | 459.1 | 415.8 | 421.2 | 373.7 | 367.7 | 407.5 | 361.2
1395 | 1305 | 525.7 | 463.4 | 490 | 459.1 | 416 | 421.4 | 373.8 | 368 | 407.6 | 361.4
1396 | 1306 | 525.7 | 463.5 | 490 | 459.2 | 416.2 | 421.6 | 373.9 | 368.3 | 407.7 | 361.6
1397 | 1307 | 525.7 | 463.5 | 490 | 459.2 | 416.4 | 421.9 | 374 | 368.5 | 407.8 | 361.8
1398 | 1308 | 525.6 | 463.6 | 490.1 | 459.3 | 416.6 | 422.1 | 374.1 | 368.7 | 407.9 | 361.9
1399 | 1309 | 525.6 | 463.6 | 490.1 | 459.3 | 416.8 | 422.3 | 374.2 | 369 | 407.9 | 362.1
1400 | 1310 | 525.6 | 463.7 | 490.1 | 459.4 | 416.9 | 422.6 | 374.3 | 369.4 | 408.1 | 362.2
1401 | 1311 | 525.5 | 463.8 | 490.1 | 459.5 | 417.1 | 422.8 | 374.4 | 369.6 | 408.1 | 362.4
1402 | 1312 | 525.5 | 463.8 | 490.1 | 459.5 | 417.3 | 423 | 374.5 | 369.9 | 408.1 | 362.6
1403 | 1313 | 525.4 | 463.9 | 490.2 | 459.6 | 417.4 | 423.3 | 374.6 | 370.2 | 408.2 | 362.7
1404 | 1314 | 525.4 | 463.9 | 490.2 | 459.6 | 417.6 | 423.5 | 374.7 | 370.5 | 408.3 | 363
1405 | 1315 | 525.4 | 464 | 490.2 | 459.7 | 417.8 | 423.7 | 374.8 | 370.7 | 408.5 | 363.1
1406 | 1316 | 525.4 | 464 | 490.3 | 459.7 | 418 | 423.9 | 374.9 | 371 | 408.6 | 363.3
1407 | 1317 | 525.4 | 464.1 | 490.3 | 459.8 | 418.2 | 424.1 | 374.9 | 371.2 | 408.7 | 363.5
1408 | 1318 | 525.4 | 464.2 | 490.3 | 459.9 | 418.3 | 424.3 | 375 | 371.3 | 408.8 | 363.6
1409 | 1319 | 525.4 | 464.2 | 490.4 | 459.9 | 418.5 | 424.5 | 375.1 | 371.5 | 408.9 | 363.8
1410 | 1320 | 525.4 | 464.3 | 490.3 | 460 | 418.7 | 424.8 | 375.2 | 371.7 | 409 | 364
1411 | 1321 | 525.4 | 464.4 | 490.4 | 460 | 418.8 | 425 | 375.3 | 372 | 409.1 | 364.2
1412 | 1322 | 525.3 | 464.4 | 490.4 | 460.1 | 419 | 425.2 | 375.4 | 372.2 | 409.1 | 364.4
1413 | 1323 | 525.3 | 464.5 | 490.4 | 460.1 | 419.1 | 425.3 | 375.4 | 372.4 | 409.3 | 364.6
1414 | 1324 | 525.3 | 464.5 | 490.4 | 460.2 | 419.3 | 425.5 | 375.5 | 372.6 | 409.4 | 364.8
1415 | 1325 | 525.2 | 464.6 | 490.5 | 460.2 | 419.5 | 425.7 | 375.6 | 372.8 | 409.6 | 365
1416 | 1326 | 525.2 | 464.6 | 490.5 | 460.3 | 419.6 | 425.9 | 375.7 | 373 | 409.8 | 365.2
1417 | 1327 | 525.2 | 464.7 | 490.6 | 460.3 | 419.7 | 426 | 375.8 | 373.1 | 410 | 365.5
1418 | 1328 | 525.2 | 464.8 | 490.5 | 460.4 | 419.9 | 426.2 | 375.8 | 373.4 | 410.1 | 365.6
1419 | 1329 | 525.3 | 464.8 | 490.6 | 460.5 | 420.1 | 426.4 | 375.9 | 373.5 | 410.2 | 365.9
1420 | 1330 | 525.3 | 464.9 | 490.6 | 460.5 | 420.2 | 426.6 | 376 | 373.7 | 410.3 | 366.1
1421 | 1331 | 525.3 | 464.9 | 490.6 | 460.6 | 420.3 | 426.7 | 376.1 | 373.9 | 410.5 | 366.3
1422 | 1332 | 525.3 | 465 | 490.7 | 460.6 | 420.5 | 426.9 | 376.2 | 374.1 | 410.6 | 366.5
1423 | 1333 | 525.4 | 465 | 490.7 | 460.6 | 420.6 | 427 | 376.2 | 374.2 | 410.6 | 366.6
1424 | 1334 | 525.4 | 465.1 | 490.7 | 460.7 | 420.7 | 427.2 | 376.3 | 374.4 | 410.7 | 366.8
1425 | 1335 | 525.4 | 465.1 | 490.8 | 460.8 | 420.9 | 427.3 | 376.4 | 374.5 | 410.8 | 367
1426 | 1336 | 525.5 | 465.2 | 490.8 | 460.8 | 421 | 427.5 | 376.5 | 374.7 | 411 | 367.2
1427 | 1337 | 525.5 | 464.6 | 492 | 460.5 | 420 | 427.1 | 376.7 | 374.9 | 411.2 | 367.6
1428 | 1338 | 525.6 | 464.6 | 492.1 | 460.5 | 420.1 | 427.2 | 376.8 | 375.1 | 411.2 | 367.9
1429 | 1339 | 525.6 | 464.7 | 492.1 | 460.6 | 420.3 | 427.3 | 376.9 | 375.2 | 411.4 | 368
1430 | 1340 | 525.6 | 464.7 | 492.2 | 460.6 | 420.4 | 427.4 | 377 | 375.3 | 411.5 | 368.2
1431 | 1341 | 525.6 | 464.8 | 492.2 | 460.7 | 420.5 | 427.5 | 377.1 | 375.4 | 411.6 | 368.3
1432 | 1342 | 525.6 | 464.8 | 492.2 | 460.7 | 420.7 | 427.6 | 377.2 | 375.5 | 411.9 | 368.5
1433 | 1343 | 525.6 | 464.9 | 492.2 | 460.8 | 420.8 | 427.7 | 377.3 | 375.7 | 411.9 | 368.7
1434 | 1344 | 525.6 | 464.9 | 492.2 | 460.8 | 420.9 | 428 | 377.3 | 375.8 | 412.1 | 368.9
1435 | 1345 | 525.6 | 465 | 492.2 | 460.9 | 421.1 | 428.4 | 377.4 | 375.9 | 412.1 | 369.1
1436 | 1346 | 525.6 | 465 | 492.3 | 460.9 | 421.2 | 428.7 | 377.5 | 376 | 412.1 | 369.2
1437 | 1347 | 525.5 | 465.1 | 492.3 | 461 | 421.3 | 428.9 | 377.6 | 376.2 | 412.3 | 369.4
1438 | 1348 | 525.4 | 465.1 | 492.3 | 461 | 421.4 | 429.1 | 377.7 | 376.3 | 412.4 | 369.6
1439 | 1349 | 525.4 | 465.2 | 492.4 | 461.1 | 421.6 | 429.2 | 377.8 | 376.5 | 412.6 | 369.7
1440 | 1350 | 525.4 | 465.2 | 492.4 | 461.1 | 421.7 | 429.3 | 377.9 | 376.7 | 412.6 | 369.8
1441 | 1351 | 525.3 | 465.3 | 492.4 | 461.2 | 421.8 | 429.4 | 378 | 376.8 | 412.5 | 369.8
1442 | 1352 | 525.3 | 465.4 | 492.4 | 461.2 | 421.9 | 429.6 | 378.1 | 377 | 412.6 | 370
1443 | 1353 | 525.3 | 465.4 | 492.4 | 461.3 | 422.1 | 429.7 | 378.2 | 377.1 | 412.8 | 370.2
1444 | 1354 | 525.3 | 465.5 | 492.5 | 461.3 | 422.2 | 429.8 | 378.3 | 377.2 | 412.8 | 370.4
1445 | 1355 | 525.3 | 465.5 | 492.5 | 461.3 | 422.3 | 429.9 | 378.4 | 377.3 | 412.7 | 370.5
1446 | 1356 | 525.2 | 465.5 | 492.5 | 461.4 | 422.4 | 429.9 | 378.5 | 377.5 | 412.9 | 370.6
1447 | 1357 | 525.2 | 465.6 | 492.6 | 461.5 | 422.5 | 430 | 378.6 | 377.6 | 413 | 370.8
1448 | 1358 | 525.2 | 465.6 | 492.6 | 461.5 | 422.6 | 430 | 378.7 | 377.8 | 413.1 | 370.9
1449 | 1359 | 525.2 | 465.7 | 492.6 | 461.5 | 422.7 | 430 | 378.8 | 377.9 | 413.2 | 371.1
1450 | 1360 | 525.2 | 465.7 | 492.6 | 461.6 | 422.9 | 430.1 | 378.9 | 378 | 413.3 | 371.2
1451 | 1361 | 525.2 | 465.8 | 492.7 | 461.6 | 423 | 430.1 | 379 | 378.2 | 413.3 | 371.4
1452 | 1362 | 525.1 | 465.9 | 492.7 | 461.7 | 423.1 | 430.1 | 379.1 | 378.3 | 413.4 | 371.5
1453 | 1363 | 525.1 | 465.9 | 492.7 | 461.7 | 423.2 | 430.2 | 379.2 | 378.4 | 413.6 | 371.7
1454 | 1364 | 525.1 | 466 | 492.7 | 461.8 | 423.3 | 430.2 | 379.3 | 378.6 | 413.8 | 371.8
1455 | 1365 | 525.1 | 466 | 492.8 | 461.8 | 423.3 | 430.2 | 379.5 | 378.7 | 413.9 | 372.1
1456 | 1366 | 525.1 | 466.1 | 492.8 | 461.8 | 423.5 | 430.2 | 379.6 | 378.8 | 414 | 372.3
1457 | 1367 | 525.1 | 466.1 | 492.8 | 461.9 | 423.6 | 430.3 | 379.7 | 379 | 414 | 372.4
1458 | 1368 | 525.1 | 466.1 | 492.9 | 461.9 | 423.7 | 430.2 | 379.8 | 379.2 | 414.1 | 372.7
1459 | 1369 | 525.1 | 466.2 | 492.9 | 462 | 423.8 | 430.2 | 379.9 | 379.4 | 414.2 | 372.9
1460 | 1370 | 525.1 | 466.3 | 492.8 | 462.1 | 423.9 | 430.3 | 380 | 379.5 | 414.5 | 373.2
1461 | 1371 | 525.1 | 466.3 | 492.9 | 462.1 | 424 | 430.2 | 380.1 | 379.7 | 414.5 | 373.4
1462 | 1372 | 525.1 | 466.4 | 492.8 | 462.2 | 424.2 | 430.2 | 380.2 | 379.8 | 414.7 | 373.5
1463 | 1373 | 525.2 | 466.4 | 492.9 | 462.2 | 424.3 | 430.1 | 380.3 | 380 | 414.9 | 373.6
1464 | 1374 | 525.2 | 466.4 | 493 | 462.2 | 424.4 | 430.1 | 380.5 | 380.1 | 415 | 373.8
1465 | 1375 | 525.2 | 466.5 | 493 | 462.3 | 424.5 | 430.1 | 380.6 | 380.3 | 415.1 | 373.9
1466 | 1376 | 525.2 | 466.5 | 493 | 462.3 | 424.6 | 430.1 | 380.7 | 380.4 | 415.2 | 374.1
1467 | 1377 | 525.3 | 466.6 | 493.1 | 462.4 | 424.7 | 430 | 380.8 | 380.6 | 415.3 | 374.3
1468 | 1378 | 525.3 | 466.6 | 493.1 | 462.4 | 424.7 | 430.1 | 380.9 | 380.8 | 415.2 | 374.4
1469 | 1379 | 525.3 | 466.7 | 493.1 | 462.5 | 424.8 | 430.1 | 381 | 380.9 | 415.3 | 374.6
1470 | 1380 | 525.3 | 466.7 | 493.1 | 462.5 | 424.9 | 430 | 381.2 | 381.1 | 415.5 | 374.7
1471 | 1381 | 525.3 | 466.8 | 493.2 | 462.5 | 425 | 430.1 | 381.3 | 381.2 | 415.8 | 374.9
1472 | 1382 | 525.3 | 466.8 | 493.2 | 462.6 | 425 | 430.1 | 381.4 | 381.4 | 415.8 | 375
1473 | 1383 | 525.4 | 466.9 | 493.2 | 462.6 | 425.1 | 430.1 | 381.5 | 381.5 | 416 | 375.2
1474 | 1384 | 525.4 | 466.9 | 493.3 | 462.7 | 425.2 | 430.1 | 381.7 | 381.6 | 416.2 | 375.4
1475 | 1385 | 525.4 | 466.9 | 493.3 | 462.7 | 425.3 | 430 | 381.8 | 381.8 | 416.3 | 375.6
1476 | 1386 | 525.4 | 467 | 493.3 | 462.8 | 425.3 | 430.1 | 381.9 | 381.9 | 416.4 | 375.8
1477 | 1387 | 525.4 | 467.1 | 493.3 | 462.8 | 425.6 | 430.1 | 382 | 382.1 | 416.6 | 375.9
1478 | 1388 | 525.5 | 467.1 | 493.3 | 462.9 | 425.6 | 430.1 | 382.2 | 382.3 | 416.6 | 376
1479 | 1389 | 525.5 | 467.1 | 493.4 | 462.9 | 425.7 | 430.2 | 382.3 | 382.5 | 416.7 | 376.2
1480 | 1390 | 525.5 | 467.2 | 493.5 | 462.9 | 425.8 | 430.2 | 382.4 | 382.7 | 416.7 | 376.5
1481 | 1391 | 525.5 | 467.2 | 493.5 | 463 | 425.9 | 430.2 | 382.6 | 382.8 | 416.7 | 376.6
1482 | 1392 | 525.6 | 467.3 | 493.5 | 463 | 426 | 430.2 | 382.7 | 383 | 417.1 | 376.9
1483 | 1393 | 525.6 | 467.3 | 493.5 | 463.1 | 426 | 430.3 | 382.8 | 383.2 | 417.4 | 377.1
1484 | 1394 | 525.6 | 467.4 | 493.5 | 463.1 | 426.1 | 430.3 | 383 | 383.3 | 417.5 | 377.3
1485 | 1395 | 525.6 | 467.4 | 493.6 | 463.1 | 426.2 | 430.3 | 383.1 | 383.5 | 417.4 | 377.5
1486 | 1396 | 525.5 | 467.5 | 493.6 | 463.2 | 426.3 | 430.3 | 383.2 | 383.8 | 417.7 | 377.7
1487 | 1397 | 525.4 | 467.5 | 493.6 | 463.2 | 426.5 | 430.4 | 383.4 | 383.9 | 417.9 | 377.9
1488 | 1398 | 525.4 | 467.6 | 493.6 | 463.3 | 426.5 | 430.4 | 383.5 | 384.2 | 418 | 378.2
1489 | 1399 | 525.3 | 467.6 | 493.6 | 463.4 | 426.7 | 430.5 | 383.6 | 384.3 | 418.2 | 378.3
1490 | 1400 | 525.3 | 467.7 | 493.6 | 463.4 | 426.7 | 430.5 | 383.8 | 384.5 | 418.2 | 378.6
1491 | 1401 | 525.3 | 467.7 | 493.7 | 463.4 | 426.8 | 430.6 | 383.9 | 384.7 | 418.4 | 378.7
1492 | 1402 | 525.3 | 467.7 | 493.7 | 463.5 | 426.9 | 430.6 | 384.1 | 384.9 | 418.5 | 378.9
1493 | 1403 | 525.4 | 467.8 | 493.7 | 463.5 | 427.1 | 430.7 | 384.2 | 385.1 | 418.7 | 379.1
1494 | 1404 | 525.4 | 467.8 | 493.8 | 463.6 | 427.2 | 430.8 | 384.3 | 385.2 | 418.6 | 379.3
1495 | 1405 | 525.4 | 467.9 | 493.8 | 463.6 | 427.3 | 430.8 | 384.5 | 385.4 | 418.7 | 379.6
1496 | 1406 | 525.4 | 467.9 | 493.8 | 463.7 | 427.5 | 430.9 | 384.6 | 385.6 | 418.8 | 379.7
1497 | 1407 | 525.4 | 467.9 | 493.9 | 463.7 | 427.5 | 430.9 | 384.7 | 385.8 | 419 | 379.8
1498 | 1408 | 525.4 | 468 | 493.8 | 463.8 | 427.7 | 431 | 384.9 | 385.9 | 419.1 | 380
1499 | 1409 | 525.4 | 468.1 | 493.9 | 463.8 | 427.9 | 431 | 385 | 386.1 | 419.2 | 380.2
1500 | 1410 | 525.4 | 468.1 | 493.9 | 463.8 | 428 | 431 | 385.2 | 386.3 | 419.3 | 380.2
1501 | 1411 | 525.4 | 468.2 | 493.8 | 463.9 | 428 | 431.1 | 385.3 | 386.5 | 419.5 | 380.3
1502 | 1412 | 525.4 | 468.2 | 494 | 463.9 | 428.1 | 431.2 | 385.5 | 386.7 | 419.6 | 380.6
1503 | 1413 | 525.4 | 468.2 | 494 | 463.9 | 428.3 | 431.4 | 385.6 | 386.9 | 419.7 | 380.6
1504 | 1414 | 525.4 | 468.3 | 493.9 | 464 | 428.6 | 431.6 | 385.7 | 387 | 419.8 | 380.7
1505 | 1415 | 525.4 | 468.3 | 494 | 464 | 428.8 | 431.7 | 385.9 | 387.3 | 419.8 | 380.8
1506 | 1416 | 525.4 | 468.4 | 494.1 | 464.1 | 428.9 | 431.7 | 386 | 387.5 | 419.8 | 380.9
1507 | 1417 | 525.5 | 468.4 | 494.1 | 464.1 | 428.9 | 431.6 | 386.2 | 387.7 | 420 | 381.1
1508 | 1418 | 525.5 | 468.4 | 494.1 | 464.2 | 428.9 | 431.5 | 386.3 | 387.9 | 420.1 | 381.2
1509 | 1419 | 525.5 | 468.5 | 494.1 | 464.2 | 429 | 431.6 | 386.5 | 388.1 | 420.3 | 381.2
1510 | 1420 | 525.5 | 468.5 | 494.1 | 464.3 | 429.1 | 431.6 | 386.6 | 388.2 | 420.4 | 381.3
1511 | 1421 | 525.5 | 468.6 | 494.2 | 464.3 | 429.3 | 431.7 | 386.8 | 388.4 | 420.3 | 381.4
1512 | 1422 | 525.6 | 468.6 | 494.2 | 464.3 | 429.6 | 431.8 | 386.9 | 388.5 | 420.5 | 381.6
1513 | 1423 | 525.6 | 468.7 | 494.2 | 464.4 | 429.7 | 431.8 | 387.1 | 388.7 | 420.7 | 381.7
1514 | 1424 | 525.5 | 468.7 | 494.2 | 464.4 | 429.6 | 431.7 | 387.3 | 388.9 | 420.9 | 381.8
1515 | 1425 | 525.6 | 468.7 | 494.2 | 464.5 | 429.7 | 431.8 | 387.4 | 389 | 421 | 381.9
1516 | 1426 | 525.6 | 468.8 | 494.3 | 464.5 | 429.8 | 431.8 | 387.6 | 389.2 | 421.1 | 382
1517 | 1427 | 525.6 | 468.8 | 494.3 | 464.6 | 429.8 | 431.9 | 387.7 | 389.4 | 421.2 | 382.2
1518 | 1428 | 525.7 | 468.9 | 494.3 | 464.6 | 429.8 | 431.9 | 387.9 | 389.6 | 421.3 | 382.2
1519 | 1429 | 525.7 | 469 | 494.2 | 464.7 | 430 | 431.9 | 388 | 389.8 | 421.4 | 382.4
1520 | 1430 | 525.7 | 469 | 494.3 | 464.7 | 430 | 431.8 | 388.2 | 390 | 421.4 | 382.5
1521 | 1431 | 525.7 | 469 | 494.4 | 464.7 | 430 | 431.9 | 388.4 | 390.2 | 421.6 | 382.7
1522 | 1432 | 525.7 | 469 | 494.4 | 464.8 | 430.1 | 431.9 | 388.5 | 390.4 | 421.7 | 382.9
1523 | 1433 | 525.7 | 469.1 | 494.4 | 464.8 | 430.3 | 432 | 388.7 | 390.6 | 421.7 | 383.1
1524 | 1434 | 525.7 | 469.1 | 494.5 | 464.8 | 430.6 | 432.1 | 388.8 | 390.8 | 421.8 | 383.1
1525 | 1435 | 525.7 | 469.1 | 494.5 | 464.9 | 430.6 | 432.1 | 389 | 391 | 422 | 383.3
1526 | 1436 | 525.7 | 469.2 | 494.5 | 464.9 | 430.8 | 432.2 | 389.2 | 391.1 | 422.1 | 383.5
1527 | 1437 | 525.7 | 469.2 | 494.6 | 465 | 430.8 | 432.2 | 389.3 | 391.3 | 422.1 | 383.8
1528 | 1438 | 525.7 | 469.3 | 494.6 | 465 | 430.8 | 432.2 | 389.5 | 391.5 | 422.2 | 383.9
1529 | 1439 | 525.8 | 469.3 | 494.6 | 465 | 430.8 | 432.3 | 389.7 | 391.7 | 422.3 | 384
1530 | 1440 | 525.7 | 469.3 | 494.6 | 465.1 | 430.9 | 432.3 | 389.9 | 391.9 | 422.5 | 384.2
1531 | 1441 | 525.7 | 469.4 | 494.6 | 465.2 | 431.1 | 432.4 | 390 | 392.1 | 422.5 | 384.5
1532 | 1442 | 525.7 | 469.4 | 494.7 | 465.2 | 431.2 | 432.3 | 390.2 | 392.3 | 422.6 | 384.6
1533 | 1443 | 525.7 | 469.4 | 494.7 | 465.2 | 431.2 | 432.4 | 390.4 | 392.6 | 422.7 | 384.7
1534 | 1444 | 525.7 | 469.5 | 494.7 | 465.3 | 431.3 | 432.5 | 390.5 | 392.8 | 422.9 | 385.1
1535 | 1445 | 525.7 | 469.5 | 494.8 | 465.3 | 431.4 | 432.5 | 390.7 | 393 | 423 | 385.1
1536 | 1446 | 525.7 | 469.6 | 494.7 | 465.3 | 431.5 | 432.6 | 390.9 | 393.1 | 423.1 | 385.3
1537 | 1447 | 525.7 | 469.6 | 494.8 | 465.4 | 431.5 | 432.6 | 391.1 | 393.2 | 423.1 | 385.5
1538 | 1448 | 525.7 | 469.6 | 494.8 | 465.4 | 431.7 | 432.6 | 391.2 | 393.3 | 423.2 | 385.6
1539 | 1449 | 525.7 | 469.7 | 494.9 | 465.4 | 431.9 | 432.7 | 391.4 | 393.5 | 423.3 | 385.7
1540 | 1450 | 525.7 | 469.7 | 494.8 | 465.5 | 432.1 | 432.8 | 391.6 | 393.7 | 423.4 | 385.9
1541 | 1451 | 525.7 | 469.8 | 494.8 | 465.5 | 432.2 | 432.8 | 391.8 | 393.8 | 423.5 | 386.2
1542 | 1452 | 525.8 | 469.8 | 495 | 465.6 | 432.1 | 432.9 | 392 | 394 | 423.6 | 386.3
1543 | 1453 | 525.8 | 469.9 | 494.8 | 465.7 | 432.2 | 433 | 392.2 | 394.2 | 423.6 | 386.5
1544 | 1454 | 525.8 | 469.9 | 494.9 | 465.7 | 432.3 | 432.9 | 392.4 | 394.4 | 423.7 | 386.8
1545 | 1455 | 525.7 | 469.9 | 495 | 465.7 | 432.4 | 433 | 392.5 | 394.5 | 423.8 | 386.9
1546 | 1456 | 525.7 | 470 | 494.8 | 465.8 | 432.6 | 433.2 | 392.7 | 394.7 | 423.9 | 387.1
1547 | 1457 | 525.6 | 470 | 495 | 465.8 | 432.6 | 433.1 | 392.9 | 395 | 423.9 | 387.3
1548 | 1458 | 525.6 | 470 | 495 | 465.8 | 432.7 | 433.2 | 393.1 | 395.2 | 424 | 387.4
1549 | 1459 | 525.6 | 470 | 495.1 | 465.8 | 432.6 | 433.3 | 393.3 | 395.4 | 424.1 | 387.7
1550 | 1460 | 525.6 | 470.1 | 495.1 | 465.9 | 432.7 | 433.3 | 393.5 | 395.6 | 424.1 | 387.9
1551 | 1461 | 525.6 | 470.1 | 495.1 | 465.9 | 432.8 | 433.4 | 393.7 | 395.8 | 424.2 | 388.1
1552 | 1462 | 525.6 | 470.1 | 495.1 | 466 | 432.9 | 433.4 | 393.9 | 396 | 424.3 | 388.3
1553 | 1463 | 525.6 | 470.2 | 495.1 | 466 | 433 | 433.4 | 394.1 | 396.2 | 424.4 | 388.5
1554 | 1464 | 525.6 | 470.2 | 495.1 | 466 | 433.1 | 433.5 | 394.3 | 396.4 | 424.5 | 388.7
1555 | 1465 | 525.6 | 470.3 | 495.1 | 466.1 | 433.2 | 433.5 | 394.5 | 396.6 | 424.6 | 388.8
1556 | 1466 | 525.6 | 470.3 | 495.1 | 466.1 | 433.3 | 433.5 | 394.7 | 396.9 | 424.7 | 389
1557 | 1467 | 525.6 | 470.4 | 495.2 | 466.1 | 433.4 | 433.4 | 394.9 | 397.1 | 424.7 | 389.2
1558 | 1468 | 525.6 | 470.4 | 495.2 | 466.2 | 433.4 | 433.4 | 395.1 | 397.3 | 424.9 | 389.3
1559 | 1469 | 525.6 | 470.4 | 495.1 | 466.2 | 433.8 | 433.5 | 395.3 | 397.5 | 424.9 | 389.5
1560 | 1470 | 525.6 | 470.4 | 495.2 | 466.3 | 433.9 | 433.5 | 395.5 | 397.7 | 425 | 389.7
1561 | 1471 | 525.6 | 470.5 | 495.2 | 466.3 | 434 | 433.4 | 395.7 | 397.8 | 425 | 389.9
1562 | 1472 | 525.6 | 470.6 | 495.2 | 466.4 | 434.1 | 433.4 | 395.9 | 398 | 425.1 | 390.1
1563 | 1473 | 525.6 | 470.6 | 495.3 | 466.4 | 434.1 | 433.4 | 396.1 | 398.1 | 425.2 | 390.3
1564 | 1474 | 525.6 | 470.6 | 495.3 | 466.4 | 434.2 | 433.4 | 396.3 | 398.3 | 425.2 | 390.5
1565 | 1475 | 525.6 | 470.6 | 495.3 | 466.5 | 434.3 | 433.5 | 396.5 | 398.5 | 425.3 | 390.7
1566 | 1476 | 525.6 | 470.7 | 495.3 | 466.5 | 434.5 | 433.6 | 396.7 | 398.6 | 425.3 | 390.9
1567 | 1477 | 525.6 | 470.7 | 495.4 | 466.5 | 434.5 | 433.6 | 396.9 | 398.8 | 425.4 | 391.1
1568 | 1478 | 525.7 | 470.7 | 495.4 | 466.6 | 434.7 | 433.7 | 397.1 | 399.1 | 425.4 | 391.2
1569 | 1479 | 525.6 | 470.8 | 495.4 | 466.6 | 434.7 | 433.7 | 397.4 | 399.3 | 425.4 | 391.4
1570 | 1480 | 525.6 | 470.8 | 495.5 | 466.6 | 434.7 | 433.7 | 397.6 | 399.5 | 425.4 | 391.6
1571 | 1481 | 525.7 | 470.8 | 495.5 | 466.6 | 434.8 | 433.7 | 397.8 | 399.7 | 425.3 | 391.7
1572 | 1482 | 525.7 | 470.9 | 495.4 | 466.7 | 434.9 | 433.9 | 398 | 399.9 | 425.4 | 391.9
1573 | 1483 | 525.7 | 470.9 | 495.4 | 466.8 | 435.1 | 433.9 | 398.2 | 400.1 | 425.3 | 392
1574 | 1484 | 525.7 | 470.9 | 495.5 | 466.8 | 435.2 | 433.8 | 398.4 | 400.3 | 425.4 | 392.2
1575 | 1485 | 525.6 | 471 | 495.5 | 466.8 | 435.3 | 433.8 | 398.6 | 400.5 | 425.3 | 392.4
1576 | 1486 | 525.7 | 471 | 495.5 | 466.9 | 435.4 | 433.8 | 398.9 | 400.7 | 425.4 | 392.6
1577 | 1487 | 525.7 | 471.1 | 495.5 | 466.9 | 435.6 | 433.8 | 399.1 | 400.9 | 425.4 | 392.7
1578 | 1488 | 525.7 | 471.1 | 495.6 | 466.9 | 435.6 | 433.8 | 399.3 | 401.1 | 425.4 | 392.9
1579 | 1489 | 525.7 | 471.1 | 495.6 | 467 | 435.8 | 433.8 | 399.5 | 401.3 | 425.5 | 393.1
1580 | 1490 | 525.7 | 471.2 | 495.6 | 467 | 435.9 | 433.8 | 399.7 | 401.5 | 425.5 | 393.2
1581 | 1491 | 525.7 | 471.2 | 495.6 | 467 | 436 | 433.8 | 400 | 401.8 | 425.6 | 393.4
1582 | 1492 | 525.7 | 471.2 | 495.6 | 467.1 | 436 | 433.7 | 400.2 | 402 | 425.6 | 393.5
1583 | 1493 | 525.7 | 471.3 | 495.6 | 467.1 | 436.1 | 433.7 | 400.4 | 402.2 | 425.7 | 393.7
1584 | 1494 | 525.7 | 471.3 | 495.6 | 467.1 | 436.2 | 433.6 | 400.6 | 402.4 | 425.7 | 393.8
1585 | 1495 | 525.6 | 471.4 | 495.6 | 467.2 | 436.3 | 433.6 | 400.8 | 402.5 | 425.8 | 394
1586 | 1496 | 525.6 | 471.4 | 495.7 | 467.2 | 436.4 | 433.6 | 401 | 402.7 | 425.9 | 394.2
1587 | 1497 | 525.6 | 471.4 | 495.7 | 467.3 | 436.6 | 433.5 | 401.2 | 402.9 | 425.9 | 394.3
1588 | 1498 | 525.7 | 471.5 | 495.7 | 467.3 | 436.7 | 433.5 | 401.4 | 403.1 | 426 | 394.5
1589 | 1499 | 525.7 | 471.5 | 495.7 | 467.3 | 436.7 | 433.4 | 401.6 | 403.4 | 426.2 | 394.7
1590 | 1500 | 525.7 | 471.5 | 495.8 | 467.4 | 436.8 | 433.2 | 401.9 | 403.7 | 426.4 | 394.8
1591 | 1501 | 525.7 | 471.5 | 495.8 | 467.4 | 437 | 433.1 | 402.1 | 403.9 | 426.5 | 395
1592 | 1502 | 525.7 | 471.6 | 495.8 | 467.4 | 437 | 433.1 | 402.3 | 404.1 | 426.5 | 395.1
1593 | 1503 | 525.7 | 471.6 | 495.8 | 467.5 | 437.2 | 433.1 | 402.5 | 404.4 | 426.6 | 395.3
1594 | 1504 | 525.7 | 471.7 | 495.8 | 467.5 | 437.3 | 433.1 | 402.7 | 404.6 | 426.7 | 395.4
1595 | 1505 | 525.7 | 471.7 | 495.9 | 467.5 | 437.4 | 433.1 | 402.9 | 404.8 | 426.8 | 395.6
1596 | 1506 | 525.7 | 471.7 | 495.9 | 467.6 | 437.4 | 433.1 | 403.1 | 405.1 | 426.8 | 395.7
1597 | 1507 | 525.6 | 471.7 | 495.9 | 467.6 | 437.5 | 433.1 | 403.3 | 405.4 | 426.8 | 395.9
1598 | 1508 | 525.6 | 471.8 | 496 | 467.6 | 437.6 | 433.1 | 403.5 | 405.6 | 426.8 | 396
1599 | 1509 | 525.6 | 471.8 | 495.9 | 467.7 | 437.7 | 433 | 403.7 | 405.8 | 426.9 | 396.2
1600 | 1510 | 525.5 | 471.8 | 496 | 467.7 | 437.8 | 432.9 | 403.9 | 406.1 | 427 | 396.3
1601 | 1511 | 525.6 | 471.8 | 496 | 467.7 | 437.9 | 433 | 404.1 | 406.4 | 427 | 396.4
1602 | 1512 | 525.6 | 471.9 | 496 | 467.8 | 437.9 | 433.1 | 404.3 | 406.6 | 427.1 | 396.5
1603 | 1513 | 525.6 | 471.9 | 495.9 | 467.9 | 438.1 | 433.1 | 404.5 | 406.8 | 427.2 | 396.6
1604 | 1514 | 525.6 | 471.9 | 496.1 | 467.9 | 438.1 | 433 | 404.7 | 407 | 427.2 | 396.8
1605 | 1515 | 525.6 | 472 | 496 | 467.9 | 438.2 | 433 | 404.9 | 407.2 | 427.2 | 396.9
1606 | 1516 | 525.6 | 472 | 496 | 467.9 | 438.2 | 433 | 405.1 | 407.4 | 427.3 | 397.1
1607 | 1517 | 525.7 | 472.1 | 496 | 468 | 438.4 | 433 | 405.3 | 407.6 | 427.3 | 397.2
1608 | 1518 | 525.7 | 472.1 | 496.1 | 468 | 438.5 | 433 | 405.5 | 407.8 | 427.3 | 397.3
1609 | 1519 | 525.7 | 472.1 | 496.1 | 468 | 438.4 | 433 | 405.7 | 408 | 427.3 | 397.5
1610 | 1520 | 525.7 | 472.1 | 496.2 | 468.1 | 438.5 | 433 | 405.9 | 408.2 | 427.3 | 397.6
1611 | 1521 | 525.7 | 472.2 | 496.1 | 468.1 | 438.6 | 433 | 406.1 | 408.5 | 427.4 | 397.7
1612 | 1522 | 525.6 | 472.2 | 496.2 | 468.1 | 438.6 | 433 | 406.3 | 408.7 | 427.5 | 397.8
1613 | 1523 | 525.6 | 472.2 | 496.2 | 468.2 | 438.6 | 433.1 | 406.5 | 408.9 | 427.5 | 397.9
1614 | 1524 | 525.5 | 472.3 | 496.2 | 468.2 | 438.6 | 433 | 406.7 | 409.1 | 427.5 | 398
1615 | 1525 | 525.6 | 472.3 | 496.2 | 468.2 | 438.7 | 433.1 | 406.9 | 409.3 | 427.6 | 398.2
1616 | 1526 | 525.6 | 472.3 | 496.3 | 468.3 | 438.9 | 433.2 | 407.1 | 409.4 | 427.6 | 398.3
1617 | 1527 | 525.6 | 472.3 | 496.3 | 468.3 | 439 | 433.2 | 407.3 | 409.7 | 427.7 | 398.4
1618 | 1528 | 525.6 | 472.4 | 496.3 | 468.3 | 439 | 433.3 | 407.5 | 409.9 | 427.8 | 398.5
1619 | 1529 | 525.6 | 472.4 | 496.3 | 468.4 | 439.1 | 433.4 | 407.7 | 410.2 | 427.8 | 398.6
1620 | 1530 | 525.6 | 472.4 | 496.3 | 468.4 | 439.2 | 433.4 | 407.8 | 410.4 | 427.9 | 398.8
1621 | 1531 | 525.6 | 472.5 | 496.4 | 468.4 | 439.3 | 433.4 | 408 | 410.6 | 427.9 | 398.9
1622 | 1532 | 525.6 | 472.5 | 496.4 | 468.5 | 439.3 | 433.4 | 408.2 | 410.8 | 427.9 | 399
1623 | 1533 | 525.6 | 472.5 | 496.4 | 468.5 | 439.3 | 433.5 | 408.4 | 411 | 427.9 | 399.1
1624 | 1534 | 525.6 | 472.6 | 496.4 | 468.5 | 439.3 | 433.6 | 408.6 | 411.3 | 428 | 399.2
1625 | 1535 | 525.6 | 472.6 | 496.4 | 468.6 | 439.4 | 433.7 | 408.8 | 411.5 | 428 | 399.3
1626 | 1536 | 525.6 | 472.6 | 496.4 | 468.6 | 439.4 | 433.8 | 409 | 411.7 | 428 | 399.4
1627 | 1537 | 525.6 | 472.7 | 496.4 | 468.6 | 439.6 | 433.8 | 409.2 | 411.9 | 428.1 | 399.5
1628 | 1538 | 525.6 | 472.7 | 496.5 | 468.7 | 439.7 | 433.8 | 409.4 | 412.2 | 428.1 | 399.6
1629 | 1539 | 525.6 | 472.7 | 496.5 | 468.7 | 439.8 | 433.8 | 409.6 | 412.4 | 428.1 | 399.7
1630 | 1540 | 525.6 | 472.7 | 496.5 | 468.7 | 440 | 433.8 | 409.8 | 412.6 | 428.1 | 399.7
1631 | 1541 | 525.6 | 472.8 | 496.5 | 468.7 | 440 | 433.9 | 409.9 | 412.8 | 428.2 | 399.8
1632 | 1542 | 525.6 | 472.8 | 496.5 | 468.8 | 440 | 433.8 | 410.1 | 413 | 428.2 | 399.9
1633 | 1543 | 525.6 | 472.9 | 496.5 | 468.9 | 440.1 | 433.9 | 410.3 | 413.2 | 428.3 | 400
1634 | 1544 | 525.6 | 472.9 | 496.5 | 468.9 | 440.2 | 433.9 | 410.5 | 413.4 | 428.3 | 400.1
1635 | 1545 | 525.5 | 472.8 | 496.8 | 468.8 | 439.9 | 433.9 | 410.7 | 413.6 | 428.4 | 400.3
1636 | 1546 | 525.5 | 472.7 | 497 | 468.8 | 439.6 | 433.9 | 410.9 | 413.9 | 428.5 | 400.5
1637 | 1547 | 525.5 | 472.7 | 497 | 468.8 | 439.5 | 433.9 | 411.1 | 414.1 | 428.5 | 400.6
1638 | 1548 | 525.5 | 472.7 | 497 | 468.8 | 439.6 | 433.9 | 411.3 | 414.3 | 428.6 | 400.7
1639 | 1549 | 525.5 | 472.7 | 497.1 | 468.9 | 439.5 | 433.9 | 411.5 | 414.5 | 428.6 | 400.8
1640 | 1550 | 525.5 | 472.7 | 497.1 | 468.9 | 439.6 | 434 | 411.7 | 414.6 | 428.7 | 400.9
1641 | 1551 | 525.5 | 472.8 | 497.1 | 468.9 | 439.6 | 434 | 411.8 | 414.8 | 428.7 | 401
1642 | 1552 | 525.5 | 472.8 | 497.2 | 469 | 439.7 | 434 | 412 | 415 | 428.8 | 401.1
1643 | 1553 | 525.5 | 472.8 | 497.2 | 469 | 439.7 | 434 | 412.2 | 415.3 | 428.8 | 401.2
1644 | 1554 | 525.5 | 472.9 | 497.2 | 469 | 439.7 | 433.9 | 412.4 | 415.5 | 428.9 | 401.2
1645 | 1555 | 525.6 | 472.9 | 497.2 | 469 | 439.8 | 433.9 | 412.6 | 415.6 | 429 | 401.4
1646 | 1556 | 525.6 | 472.9 | 497.2 | 469.1 | 439.8 | 434 | 412.7 | 415.8 | 429.1 | 401.5
1647 | 1557 | 525.6 | 472.9 | 497.2 | 469.1 | 439.8 | 434 | 412.9 | 416 | 429.2 | 401.6
1648 | 1558 | 525.6 | 473 | 497.2 | 469.2 | 439.9 | 434.1 | 413.1 | 416.2 | 429.2 | 401.7
1649 | 1559 | 525.6 | 473 | 497.3 | 469.2 | 439.9 | 434.1 | 413.3 | 416.3 | 429.3 | 401.8
1650 | 1560 | 525.6 | 473 | 497.3 | 469.2 | 439.9 | 434.1 | 413.4 | 416.5 | 429.4 | 401.9
1651 | 1561 | 525.6 | 473.1 | 497.3 | 469.2 | 439.9 | 434.1 | 413.6 | 416.7 | 429.5 | 402
1652 | 1562 | 525.6 | 473.1 | 497.3 | 469.3 | 440 | 434.1 | 413.8 | 416.9 | 429.6 | 402.1
1653 | 1563 | 525.6 | 473.1 | 497.3 | 469.3 | 440 | 434.2 | 414 | 417.2 | 429.7 | 402.2
1654 | 1564 | 525.6 | 473.1 | 497.4 | 469.3 | 440.1 | 434.3 | 414.2 | 417.3 | 429.8 | 402.3
1655 | 1565 | 525.6 | 473.2 | 497.4 | 469.4 | 440.2 | 434.3 | 414.3 | 417.5 | 429.8 | 402.4
1656 | 1566 | 525.6 | 473.2 | 497.4 | 469.4 | 440.2 | 434.4 | 414.5 | 417.8 | 429.9 | 402.5
1657 | 1567 | 525.6 | 473.2 | 497.4 | 469.4 | 440.2 | 434.4 | 414.7 | 418 | 430 | 402.6
1658 | 1568 | 525.6 | 473.2 | 497.5 | 469.5 | 440.2 | 434.5 | 414.8 | 418.2 | 430.1 | 402.8
1659 | 1569 | 525.6 | 473.3 | 497.5 | 469.5 | 440.2 | 434.5 | 415 | 418.4 | 430.1 | 402.9
1660 | 1570 | 525.6 | 473.3 | 497.5 | 469.5 | 440.2 | 434.5 | 415.2 | 418.6 | 430.2 | 402.9
1661 | 1571 | 525.6 | 473.3 | 497.5 | 469.6 | 440.2 | 434.6 | 415.4 | 418.7 | 430.3 | 403
1662 | 1572 | 525.5 | 473.4 | 497.5 | 469.6 | 440.3 | 434.6 | 415.5 | 418.9 | 430.5 | 403.1
1663 | 1573 | 525.5 | 473.4 | 497.5 | 469.6 | 440.2 | 434.6 | 415.7 | 419 | 430.6 | 403.2
1664 | 1574 | 525.6 | 473.4 | 497.6 | 469.7 | 440.2 | 434.7 | 415.9 | 419.2 | 430.7 | 403.3
1665 | 1575 | 525.6 | 473.4 | 497.6 | 469.7 | 440.3 | 434.9 | 416 | 419.3 | 430.9 | 403.4
1666 | 1576 | 525.6 | 473.5 | 497.6 | 469.7 | 440.4 | 435 | 416.2 | 419.5 | 431 | 403.6
1667 | 1577 | 525.6 | 473.5 | 497.6 | 469.8 | 440.4 | 435.1 | 416.4 | 419.7 | 431 | 403.7
1668 | 1578 | 525.6 | 473.5 | 497.6 | 469.8 | 440.5 | 435.3 | 416.5 | 419.9 | 431.1 | 403.8
1669 | 1579 | 525.6 | 473.5 | 497.7 | 469.8 | 440.5 | 435.4 | 416.7 | 420.1 | 431.1 | 403.9
1670 | 1580 | 525.6 | 473.6 | 497.7 | 469.9 | 440.6 | 435.5 | 416.9 | 420.3 | 431.2 | 404
1671 | 1581 | 525.6 | 473.6 | 497.7 | 469.9 | 440.6 | 435.5 | 417 | 420.5 | 430.1 | 403.8
1672 | 1582 | 525.6 | 473.6 | 497.7 | 470 | 440.7 | 435.7 | 417.2 | 420.7 | 429.9 | 403.8
1673 | 1583 | 525.7 | 473.6 | 497.7 | 470 | 440.7 | 435.7 | 417.4 | 420.9 | 429.2 | 403.7
1674 | 1584 | 525.7 | 473.7 | 497.7 | 470 | 440.8 | 435.8 | 417.5 | 421.2 | 429.4 | 403.9
1675 | 1585 | 525.7 | 473.8 | 497.6 | 470.1 | 440.8 | 435.9 | 417.7 | 421.4 | 429.6 | 404
1676 | 1586 | 525.7 | 473.7 | 497.7 | 470.1 | 440.7 | 435.9 | 417.9 | 421.6 | 429.9 | 404.2
1677 | 1587 | 525.7 | 473.8 | 497.7 | 470.1 | 440.8 | 436 | 418 | 421.8 | 430.1 | 404.3
1678 | 1588 | 525.7 | 473.8 | 497.7 | 470.2 | 440.8 | 436.1 | 418.2 | 422 | 430.2 | 404.4
1679 | 1589 | 525.6 | 473.8 | 497.8 | 470.2 | 440.7 | 436.1 | 418.3 | 422.2 | 430.3 | 404.6
1680 | 1590 | 525.6 | 473.8 | 497.9 | 470.2 | 440.7 | 436.1 | 418.5 | 422.3 | 430.4 | 404.7
1681 | 1591 | 525.6 | 473.9 | 497.8 | 470.2 | 440.7 | 436.1 | 418.6 | 422.5 | 430.6 | 404.7
1682 | 1592 | 525.5 | 473.9 | 497.8 | 470.3 | 440.8 | 436.2 | 418.8 | 422.8 | 430.7 | 404.8
1683 | 1593 | 525.5 | 473.9 | 497.8 | 470.3 | 440.8 | 436.2 | 419 | 423 | 430.8 | 404.9
1684 | 1594 | 525.5 | 473.9 | 497.9 | 470.3 | 440.7 | 436.3 | 419.1 | 423.2 | 431 | 405
1685 | 1595 | 525.5 | 473.8 | 498.2 | 470.3 | 440.4 | 436.3 | 419.3 | 423.5 | 431.1 | 405.2
1686 | 1596 | 525.5 | 473.8 | 498.2 | 470.3 | 440.3 | 436.4 | 419.5 | 423.7 | 431.2 | 405.3
1687 | 1597 | 525.5 | 473.8 | 498.2 | 470.3 | 440.4 | 436.4 | 419.6 | 423.8 | 431.4 | 405.4
1688 | 1598 | 525.5 | 473.9 | 498.2 | 470.4 | 440.5 | 436.4 | 419.8 | 424 | 431.5 | 405.5
1689 | 1599 | 525.5 | 473.9 | 498.3 | 470.4 | 440.5 | 436.4 | 419.9 | 424.2 | 431.5 | 405.6
1690 | 1600 | 525.6 | 474 | 498.2 | 470.5 | 440.6 | 436.5 | 420.1 | 424.3 | 431.5 | 405.7
1691 | 1601 | 525.6 | 473.9 | 498.3 | 470.5 | 440.5 | 436.5 | 420.2 | 424.5 | 431.5 | 405.8
1692 | 1602 | 525.5 | 473.9 | 498.3 | 470.5 | 440.5 | 436.5 | 420.4 | 424.7 | 431.7 | 405.9
1693 | 1603 | 525.5 | 474 | 498.3 | 470.5 | 440.5 | 436.6 | 420.6 | 424.8 | 431.9 | 406
1694 | 1604 | 525.5 | 474 | 498.3 | 470.6 | 440.7 | 436.7 | 420.7 | 425 | 431.6 | 406
1695 | 1605 | 525.5 | 474.1 | 498.3 | 470.6 | 440.8 | 436.8 | 420.8 | 425.2 | 431.7 | 406.1
1696 | 1606 | 525.5 | 474.1 | 498.4 | 470.7 | 440.8 | 436.9 | 421 | 425.4 | 431.7 | 406.2
1697 | 1607 | 525.5 | 474.1 | 498.4 | 470.7 | 440.9 | 437 | 421.1 | 425.5 | 431.8 | 406.3
1698 | 1608 | 525.5 | 474.2 | 498.3 | 470.7 | 441 | 437 | 421.3 | 425.7 | 431.9 | 406.4
1699 | 1609 | 525.5 | 474.2 | 498.3 | 470.8 | 441.1 | 437.1 | 421.4 | 425.9 | 431.7 | 406.4
1700 | 1610 | 525.4 | 474.2 | 498.4 | 470.8 | 441 | 437.1 | 421.6 | 426.1 | 431.8 | 406.5
1701 | 1611 | 525.4 | 474.3 | 498.3 | 470.9 | 441.2 | 437.2 | 421.7 | 426.2 | 431.9 | 406.5
1702 | 1612 | 525.4 | 474.3 | 498.3 | 470.9 | 441.2 | 437.3 | 421.9 | 426.4 | 432.2 | 406.7
1703 | 1613 | 525.4 | 474.2 | 498.4 | 470.9 | 440.9 | 437.3 | 422 | 426.6 | 432.4 | 406.8
1704 | 1614 | 525.4 | 474.3 | 498.4 | 471 | 440.9 | 437.4 | 422.2 | 426.7 | 432.6 | 406.9
1705 | 1615 | 525.4 | 474.3 | 498.4 | 471 | 441.2 | 437.5 | 422.3 | 426.9 | 432.4 | 406.9
1706 | 1616 | 525.4 | 474.3 | 498.5 | 471 | 441.2 | 437.6 | 422.5 | 427.2 | 432.4 | 407
1707 | 1617 | 525.4 | 474.3 | 498.6 | 471 | 441.2 | 437.7 | 422.7 | 427.4 | 432.7 | 407.2
1708 | 1618 | 525.4 | 474.4 | 498.4 | 471.1 | 441.4 | 437.9 | 422.8 | 427.5 | 432.9 | 407.2
1709 | 1619 | 525.4 | 474.5 | 498.4 | 471.2 | 441.4 | 438 | 423 | 427.7 | 433.1 | 407.3
1710 | 1620 | 525.4 | 474.4 | 498.6 | 471.1 | 441.2 | 438.1 | 423.1 | 427.9 | 433.2 | 407.4
1711 | 1621 | 525.4 | 474.5 | 498.5 | 471.2 | 441.4 | 438.3 | 423.3 | 428 | 433.3 | 407.5
1712 | 1622 | 525.4 | 474.5 | 498.5 | 471.3 | 441.5 | 438.5 | 423.5 | 428.2 | 433.3 | 407.6
1713 | 1623 | 525.4 | 474.5 | 498.6 | 471.3 | 441.5 | 438.6 | 423.7 | 428.4 | 433.3 | 407.7
1714 | 1624 | 525.4 | 474.5 | 498.7 | 471.3 | 441.3 | 438.7 | 423.9 | 428.6 | 433.3 | 407.8
1715 | 1625 | 525.4 | 474.6 | 498.6 | 471.3 | 441.5 | 438.9 | 424.1 | 428.7 | 433.3 | 407.8
1716 | 1626 | 525.4 | 474.6 | 498.6 | 471.4 | 441.5 | 439 | 424.2 | 428.9 | 433.4 | 408
1717 | 1627 | 525.4 | 474.6 | 498.7 | 471.4 | 441.4 | 439.1 | 424.4 | 429.1 | 433.6 | 408.1
1718 | 1628 | 525.4 | 474.6 | 498.7 | 471.4 | 441.5 | 439.2 | 424.6 | 429.2 | 433.5 | 408.2
1719 | 1629 | 525.4 | 474.7 | 498.6 | 471.5 | 441.7 | 439.3 | 424.8 | 429.4 | 433.6 | 408.2
1720 | 1630 | 525.4 | 474.7 | 498.7 | 471.5 | 441.7 | 439.3 | 424.9 | 429.6 | 433.7 | 408.3
1721 | 1631 | 525.4 | 474.7 | 498.8 | 471.5 | 441.5 | 439.3 | 425.1 | 429.8 | 433.9 | 408.5
1722 | 1632 | 525.4 | 474.8 | 498.7 | 471.6 | 441.8 | 439.4 | 425.2 | 430 | 433.9 | 408.5
1723 | 1633 | 525.4 | 474.8 | 498.7 | 471.6 | 441.8 | 439.4 | 425.4 | 430.1 | 433.9 | 408.6
1724 | 1634 | 525.3 | 474.8 | 498.8 | 471.6 | 441.8 | 439.4 | 425.6 | 430.4 | 433.8 | 408.6
1725 | 1635 | 525.3 | 474.8 | 498.8 | 471.6 | 441.8 | 439.4 | 425.7 | 430.6 | 434.1 | 408.7
1726 | 1636 | 525.3 | 474.9 | 498.7 | 471.7 | 442 | 439.4 | 425.8 | 430.7 | 434.1 | 408.8
1727 | 1637 | 525.3 | 474.9 | 498.8 | 471.7 | 442 | 439.5 | 426 | 430.9 | 433.9 | 408.9
1728 | 1638 | 525.3 | 474.8 | 498.9 | 471.7 | 441.9 | 439.4 | 426.2 | 431.1 | 434.3 | 409
1729 | 1639 | 525.3 | 474.9 | 498.8 | 471.8 | 442.1 | 439.5 | 426.3 | 431.2 | 434.4 | 409.1
1730 | 1640 | 525.3 | 475 | 498.7 | 471.8 | 442.1 | 439.5 | 426.5 | 431.4 | 434.7 | 409.2
1731 | 1641 | 525.3 | 474.9 | 498.9 | 471.8 | 442 | 439.4 | 426.7 | 431.7 | 434.6 | 409.2
1732 | 1642 | 525.3 | 474.9 | 498.9 | 471.9 | 442.1 | 439.4 | 426.8 | 431.8 | 434.4 | 409.3
1733 | 1643 | 525.3 | 475 | 498.8 | 471.9 | 442.2 | 439.3 | 427 | 432 | 434.5 | 409.3
1734 | 1644 | 525.2 | 475 | 498.8 | 471.9 | 442.2 | 439.2 | 427.1 | 432.1 | 434.7 | 409.4
1735 | 1645 | 525.2 | 475 | 499 | 471.9 | 442.3 | 439.1 | 427.3 | 432.3 | 434.9 | 409.6
1736 | 1646 | 525.2 | 475.1 | 498.9 | 472 | 442.6 | 439.2 | 427.5 | 432.4 | 434.9 | 409.6
1737 | 1647 | 525.2 | 475.1 | 498.9 | 472.1 | 442.6 | 439.2 | 427.6 | 432.5 | 435.1 | 409.8
1738 | 1648 | 525.2 | 475.1 | 499 | 472.1 | 442.4 | 439.2 | 427.8 | 432.7 | 435 | 409.8
1739 | 1649 | 525.2 | 475.1 | 498.9 | 472.1 | 442.6 | 439.2 | 428 | 432.8 | 436.6 | 410.3
1740 | 1650 | 525.2 | 475.2 | 498.9 | 472.2 | 442.9 | 439.2 | 428.1 | 433 | 437.4 | 410.5
1741 | 1651 | 525.2 | 475.2 | 498.9 | 472.2 | 443 | 439.1 | 428.3 | 433.2 | 437.4 | 410.6
1742 | 1652 | 525.2 | 475.1 | 499 | 472.2 | 443 | 439 | 428.5 | 433.4 | 437.5 | 410.8
1743 | 1653 | 525.2 | 475.3 | 498.9 | 472.3 | 443.3 | 439 | 428.6 | 433.5 | 437.6 | 410.8
1744 | 1654 | 525.2 | 475.3 | 498.9 | 472.3 | 443.4 | 438.9 | 428.8 | 433.7 | 437.7 | 410.9
1745 | 1655 | 525.2 | 475.2 | 499 | 472.3 | 443.3 | 438.9 | 429.1 | 433.9 | 437.8 | 411
1746 | 1656 | 525.2 | 475.3 | 499 | 472.4 | 443.5 | 438.9 | 429.3 | 434.1 | 437.9 | 411.1
1747 | 1657 | 525.2 | 475.4 | 498.9 | 472.4 | 443.7 | 438.9 | 429.5 | 434.3 | 437.9 | 411.2
1748 | 1658 | 525.2 | 475.3 | 499 | 472.4 | 443.8 | 438.9 | 429.7 | 434.5 | 438 | 411.3
1749 | 1659 | 525.2 | 475.3 | 499.1 | 472.4 | 443.7 | 438.9 | 429.9 | 434.7 | 438 | 411.4
1750 | 1660 | 525.2 | 475.4 | 499 | 472.5 | 444 | 439 | 430 | 434.8 | 438.1 | 411.5
1751 | 1661 | 525.2 | 475.4 | 499 | 472.5 | 444.2 | 439.1 | 430.2 | 434.9 | 438.1 | 411.6
1752 | 1662 | 525.2 | 475.4 | 499.1 | 472.5 | 444.2 | 439.1 | 430.3 | 435 | 438.2 | 411.7
1753 | 1663 | 525.2 | 475.4 | 499.1 | 472.6 | 444.4 | 439.1 | 430.5 | 435.2 | 438.2 | 411.7
1754 | 1664 | 525.2 | 475.5 | 499 | 472.7 | 444.7 | 439.2 | 430.6 | 435.4 | 438.3 | 411.8
1755 | 1665 | 525.2 | 475.5 | 499.1 | 472.7 | 444.7 | 439.3 | 430.8 | 435.6 | 438.4 | 411.9
1756 | 1666 | 525.3 | 475.5 | 499.2 | 472.7 | 444.6 | 439.2 | 430.9 | 435.7 | 438.4 | 412
1757 | 1667 | 525.3 | 475.6 | 499 | 472.8 | 444.9 | 439.4 | 431.1 | 435.8 | 438.5 | 412
1758 | 1668 | 525.3 | 475.6 | 499 | 472.8 | 445 | 439.5 | 431.2 | 435.9 | 438.5 | 412.1
1759 | 1669 | 525.3 | 475.6 | 499.2 | 472.8 | 445 | 439.5 | 431.4 | 436 | 438.6 | 412.2
1760 | 1670 | 525.3 | 475.6 | 499.1 | 472.8 | 445.1 | 439.5 | 431.5 | 436.1 | 438.6 | 412.3
1761 | 1671 | 525.3 | 475.7 | 499 | 472.9 | 445.2 | 439.6 | 431.6 | 436.2 | 438.7 | 412.4
1762 | 1672 | 525.3 | 475.7 | 499.1 | 472.9 | 445.3 | 439.7 | 431.8 | 436.3 | 438.7 | 412.5
1763 | 1673 | 525.3 | 475.6 | 499.2 | 472.9 | 445.3 | 439.7 | 431.9 | 436.5 | 438.8 | 412.6
1764 | 1674 | 525.4 | 475.7 | 499.1 | 473 | 445.6 | 439.8 | 432.1 | 436.6 | 438.8 | 412.6
1765 | 1675 | 525.4 | 475.8 | 499.1 | 473 | 445.8 | 439.8 | 432.2 | 436.8 | 438.8 | 412.7
1766 | 1676 | 525.4 | 475.7 | 499.3 | 473 | 445.7 | 439.8 | 432.4 | 436.9 | 438.9 | 412.8
1767 | 1677 | 525.4 | 475.8 | 499.2 | 473 | 445.8 | 439.9 | 432.5 | 437 | 439 | 412.8
1768 | 1678 | 525.4 | 475.9 | 499.1 | 473.1 | 446.1 | 440 | 432.6 | 437.1 | 439.1 | 412.9
1769 | 1679 | 525.4 | 475.8 | 499.2 | 473.1 | 446 | 440 | 432.8 | 437.2 | 439.2 | 413
1770 | 1680 | 525.4 | 475.8 | 499.3 | 473.1 | 446 | 439.9 | 433 | 437.3 | 439.3 | 413.1
1771 | 1681 | 525.4 | 475.9 | 499.2 | 473.2 | 446.3 | 440 | 433.1 | 437.5 | 439.4 | 413.1
1772 | 1682 | 525.4 | 475.9 | 499.2 | 473.3 | 446.3 | 439.9 | 433.3 | 437.6 | 439.5 | 413.2
1773 | 1683 | 525.4 | 475.9 | 499.3 | 473.3 | 446.1 | 439.9 | 433.5 | 437.8 | 439.6 | 413.3
1774 | 1684 | 525.4 | 475.9 | 499.3 | 473.3 | 446.2 | 439.9 | 433.7 | 437.9 | 439.7 | 413.4
1775 | 1685 | 525.5 | 476 | 499.2 | 473.4 | 446.5 | 440 | 434.1 | 438 | 439.7 | 413.5
1776 | 1686 | 525.5 | 476 | 499.3 | 473.4 | 446.6 | 440 | 434.5 | 438.1 | 439.8 | 413.6
1777 | 1687 | 525.5 | 476 | 499.4 | 473.4 | 446.5 | 440 | 435 | 438.3 | 439.9 | 413.7
1778 | 1688 | 525.5 | 476.1 | 499.3 | 473.5 | 446.9 | 440 | 435.3 | 438.4 | 440 | 413.8
1779 | 1689 | 525.5 | 476.1 | 499.3 | 473.5 | 447 | 440 | 435.7 | 438.6 | 440 | 413.8
1780 | 1690 | 525.5 | 476.1 | 499.4 | 473.5 | 447 | 440 | 436.1 | 438.8 | 440.1 | 413.9
1781 | 1691 | 525.6 | 476.1 | 499.4 | 473.6 | 447.2 | 440 | 436.4 | 439 | 440.2 | 414
1782 | 1692 | 525.6 | 476.2 | 499.3 | 473.6 | 447.5 | 440.1 | 436.7 | 439.1 | 440.2 | 414.1
1783 | 1693 | 525.6 | 476 | 499.7 | 473.5 | 446.9 | 439.9 | 437 | 439.3 | 440.3 | 414.2
1784 | 1694 | 525.6 | 475.9 | 499.8 | 473.5 | 446.8 | 439.9 | 437.3 | 439.4 | 440.4 | 414.3
1785 | 1695 | 525.6 | 476 | 499.7 | 473.6 | 447 | 440 | 437.5 | 439.5 | 440.4 | 414.4
1786 | 1696 | 525.7 | 476 | 499.7 | 473.6 | 447.1 | 440.1 | 437.7 | 439.5 | 440.5 | 414.5
1787 | 1697 | 525.7 | 476 | 499.8 | 473.6 | 447 | 440.1 | 437.9 | 439.7 | 440.5 | 414.6
1788 | 1698 | 525.7 | 476 | 499.8 | 473.7 | 447.1 | 440.1 | 438.1 | 439.7 | 440.5 | 414.6
1789 | 1699 | 525.7 | 476.1 | 499.7 | 473.8 | 447.4 | 440.2 | 438.3 | 439.9 | 440.6 | 414.7
1790 | 1700 | 525.7 | 476.1 | 499.8 | 473.8 | 447.3 | 440.2 | 438.4 | 440 | 440.6 | 414.7
1791 | 1701 | 525.7 | 476.1 | 499.9 | 473.7 | 447.1 | 440.2 | 438.6 | 440.2 | 440.7 | 414.8
1792 | 1702 | 525.7 | 476.2 | 499.8 | 473.8 | 447.4 | 440.3 | 438.7 | 440.2 | 440.7 | 414.8
1793 | 1703 | 525.7 | 476.2 | 499.8 | 473.9 | 447.4 | 440.4 | 438.9 | 440.4 | 440.8 | 414.9
1794 | 1704 | 525.7 | 476.2 | 499.9 | 473.9 | 447.4 | 440.5 | 439.1 | 440.6 | 440.9 | 415
1795 | 1705 | 525.7 | 476.2 | 499.9 | 473.9 | 447.5 | 440.6 | 439.2 | 440.7 | 441 | 415
1796 | 1706 | 525.8 | 476.3 | 499.8 | 474 | 447.6 | 440.8 | 439.3 | 440.8 | 441.1 | 415.1
1797 | 1707 | 525.8 | 476.3 | 499.8 | 474 | 447.7 | 440.9 | 439.5 | 440.9 | 441.1 | 415.1
1798 | 1708 | 525.8 | 476.2 | 500 | 474 | 447.5 | 440.9 | 439.6 | 441 | 441.2 | 415.2
1799 | 1709 | 525.8 | 476.3 | 499.9 | 474.1 | 447.8 | 441.1 | 439.8 | 441.1 | 441.2 | 415.3
1800 | 1710 | 525.9 | 476.4 | 499.9 | 474.1 | 447.8 | 441.3 | 439.9 | 441.3 | 441.2 | 415.3
1801 | 1711 | 525.9 | 476.3 | 500 | 474.1 | 447.5 | 441.4 | 440.1 | 441.4 | 441.2 | 415.4
1802 | 1712 | 525.9 | 476.4 | 500 | 474.1 | 447.5 | 441.6 | 440.3 | 441.6 | 441.2 | 415.5
1803 | 1713 | 525.9 | 476.4 | 499.9 | 474.2 | 447.6 | 441.8 | 440.4 | 441.6 | 441.2 | 415.5
1804 | 1714 | 525.9 | 476.4 | 500 | 474.2 | 447.5 | 442 | 440.6 | 441.7 | 441.2 | 415.6
1805 | 1715 | 525.9 | 476.4 | 500.1 | 474.2 | 447.4 | 442.2 | 440.7 | 441.9 | 441.3 | 415.7
1806 | 1716 | 525.8 | 476.5 | 499.9 | 474.3 | 447.5 | 442.6 | 440.8 | 442 | 441.2 | 415.7
1807 | 1717 | 525.8 | 476.5 | 500 | 474.3 | 447.4 | 442.8 | 441 | 442.1 | 441.2 | 415.7
1808 | 1718 | 525.8 | 476.5 | 500.1 | 474.3 | 447.3 | 443 | 441.1 | 442.2 | 441.2 | 415.8
1809 | 1719 | 525.8 | 476.5 | 500.1 | 474.3 | 447.3 | 443.4 | 441.2 | 442.4 | 441.3 | 415.8
1810 | 1720 | 525.8 | 476.6 | 500 | 474.4 | 447.4 | 443.9 | 441.3 | 442.5 | 441.3 | 415.9
1811 | 1721 | 525.7 | 476.6 | 500 | 474.4 | 447.4 | 444.2 | 441.5 | 442.6 | 441.3 | 415.9
1812 | 1722 | 525.7 | 476.6 | 500 | 474.4 | 447.3 | 444.4 | 441.6 | 442.7 | 441.4 | 416
1813 | 1723 | 525.7 | 476.7 | 500 | 474.5 | 447.5 | 444.7 | 441.8 | 442.8 | 441.4 | 416
1814 | 1724 | 525.6 | 476.7 | 500 | 474.5 | 447.6 | 444.9 | 441.9 | 443 | 441.5 | 416.1
1815 | 1725 | 525.6 | 476.7 | 500 | 474.5 | 447.4 | 445.1 | 442.1 | 443.2 | 441.6 | 416.2
1816 | 1726 | 525.6 | 476.7 | 500 | 474.6 | 447.5 | 445.4 | 442.2 | 443.3 | 441.6 | 416.2
1817 | 1727 | 525.6 | 476.8 | 500 | 474.6 | 447.6 | 445.7 | 442.4 | 443.3 | 441.7 | 416.3
1818 | 1728 | 525.6 | 476.8 | 500 | 474.6 | 447.6 | 446 | 442.6 | 443.4 | 441.8 | 416.3
1819 | 1729 | 525.6 | 476.7 | 500.1 | 474.6 | 447.2 | 446.2 | 442.8 | 443.4 | 441.8 | 416.4
1820 | 1730 | 525.5 | 476.8 | 500 | 474.7 | 447.2 | 446.4 | 442.9 | 443.5 | 441.9 | 416.4
1821 | 1731 | 525.5 | 476.8 | 500 | 474.7 | 446.9 | 446.5 | 443.1 | 443.5 | 441.9 | 416.5
1822 | 1732 | 525.5 | 476.8 | 500.1 | 474.7 | 446.5 | 446.9 | 443.2 | 443.6 | 441.9 | 416.6
1823 | 1733 | 525.5 | 476.8 | 500.1 | 474.7 | 446.4 | 447.4 | 443.4 | 443.7 | 442 | 416.6
1824 | 1734 | 525.4 | 476.9 | 500 | 474.8 | 446.4 | 447.7 | 443.6 | 443.8 | 442 | 416.7
1825 | 1735 | 525.4 | 476.9 | 500.1 | 474.8 | 446.3 | 448.2 | 443.8 | 443.8 | 442.1 | 416.7
1826 | 1736 | 525.4 | 476.9 | 500.2 | 474.8 | 446.1 | 448.6 | 444 | 443.9 | 442.2 | 416.8
1827 | 1737 | 525.4 | 476.9 | 500.1 | 474.9 | 446.3 | 448.9 | 444.2 | 443.9 | 442.2 | 416.9
1828 | 1738 | 525.4 | 477 | 500 | 474.9 | 446.3 | 448.8 | 444.4 | 444 | 442.2 | 416.9
1829 | 1739 | 525.4 | 476.9 | 500.1 | 474.9 | 446.2 | 448.8 | 444.7 | 444.1 | 442.2 | 417
1830 | 1740 | 525.4 | 477 | 500.1 | 475 | 446.3 | 449 | 444.9 | 444.2 | 442.3 | 417
1831 | 1741 | 525.4 | 477.1 | 500 | 475.1 | 446.5 | 449.6 | 445.1 | 444.3 | 442.3 | 417.1
1832 | 1742 | 525.4 | 477 | 500.1 | 475 | 446.4 | 449.5 | 445.4 | 444.4 | 442.3 | 417.2
1833 | 1743 | 525.3 | 477 | 500.2 | 475 | 446.2 | 449.4 | 445.7 | 444.5 | 442.3 | 417.2
1834 | 1744 | 525.3 | 477.1 | 500.1 | 475.1 | 446.5 | 449.6 | 445.9 | 444.6 | 442.4 | 417.3
1835 | 1745 | 525.3 | 477.1 | 500.1 | 475.1 | 446.6 | 450 | 446.1 | 444.7 | 442.4 | 417.3
1836 | 1746 | 525.2 | 477.1 | 500.2 | 475.1 | 446.6 | 450.1 | 446.4 | 444.7 | 442.4 | 417.4
1837 | 1747 | 525.3 | 477.1 | 500.2 | 475.2 | 446.7 | 450.2 | 446.6 | 444.8 | 442.4 | 417.4
1838 | 1748 | 525.3 | 477.2 | 500.1 | 475.2 | 446.9 | 450.5 | 446.8 | 444.9 | 442.4 | 417.5
1839 | 1749 | 525.2 | 477.2 | 500.1 | 475.3 | 447 | 450.7 | 447 | 444.9 | 442.3 | 417.5
1840 | 1750 | 525.2 | 477.2 | 500.3 | 475.2 | 446.8 | 450.8 | 447.2 | 445 | 442.3 | 417.6
1841 | 1751 | 525.3 | 477.3 | 500.2 | 475.3 | 447.1 | 451 | 447.3 | 445.2 | 442.3 | 417.6
1842 | 1752 | 525.3 | 477.3 | 500.2 | 475.3 | 447.2 | 451.2 | 447.5 | 445.3 | 442.3 | 417.7
1843 | 1753 | 525.3 | 477.2 | 500.3 | 475.3 | 447.1 | 451.4 | 447.7 | 445.4 | 442.3 | 417.8
1844 | 1754 | 525.3 | 477.3 | 500.3 | 475.4 | 447.2 | 451.6 | 447.9 | 445.5 | 442.4 | 417.8
1845 | 1755 | 525.3 | 477.3 | 500.2 | 475.4 | 447.4 | 451.8 | 448.1 | 445.6 | 442.3 | 417.9
1846 | 1756 | 525.3 | 477.3 | 500.3 | 475.4 | 447.5 | 452 | 448.3 | 445.7 | 442.3 | 417.9
1847 | 1757 | 525.4 | 477.3 | 500.4 | 475.4 | 447.4 | 452 | 448.4 | 445.8 | 442.3 | 418
1848 | 1758 | 525.4 | 477.4 | 500.3 | 475.5 | 447.7 | 452.1 | 448.6 | 445.8 | 442.3 | 418
1849 | 1759 | 525.4 | 477.4 | 500.3 | 475.5 | 447.8 | 452.2 | 448.7 | 445.9 | 442.3 | 418.1
1850 | 1760 | 525.4 | 477.4 | 500.4 | 475.5 | 447.8 | 452.4 | 448.9 | 446.1 | 442.3 | 418.2
1851 | 1761 | 525.5 | 477.4 | 500.4 | 475.6 | 447.9 | 452.5 | 449.1 | 446.2 | 442.3 | 418.2
1852 | 1762 | 525.5 | 477.5 | 500.3 | 475.6 | 448.2 | 452.7 | 449.2 | 446.3 | 442.4 | 418.3
1853 | 1763 | 525.5 | 477.5 | 500.4 | 475.6 | 448.2 | 452.8 | 449.3 | 446.4 | 442.4 | 418.3
1854 | 1764 | 525.6 | 477.5 | 500.5 | 475.6 | 448.2 | 452.9 | 449.4 | 446.6 | 442.4 | 418.4
1855 | 1765 | 525.5 | 477.5 | 500.4 | 475.7 | 448.5 | 453.1 | 449.5 | 446.7 | 442.4 | 418.4
1856 | 1766 | 525.5 | 477.6 | 500.4 | 475.7 | 448.6 | 453.3 | 449.6 | 446.8 | 442.4 | 418.5
1857 | 1767 | 525.6 | 477.6 | 500.5 | 475.7 | 448.5 | 453.4 | 449.7 | 446.9 | 442.5 | 418.6
1858 | 1768 | 525.6 | 477.6 | 500.5 | 475.7 | 448.6 | 453.5 | 449.8 | 447 | 442.5 | 418.6
1859 | 1769 | 525.6 | 477.7 | 500.4 | 475.8 | 448.7 | 453.7 | 449.8 | 447.1 | 442.5 | 418.7
1860 | 1770 | 525.6 | 477.7 | 500.5 | 475.8 | 448.7 | 453.8 | 449.9 | 447.3 | 442.5 | 418.7
1861 | 1771 | 525.6 | 477.6 | 500.6 | 475.8 | 448.5 | 453.9 | 450.1 | 447.4 | 442.6 | 418.8
1862 | 1772 | 525.6 | 477.7 | 500.5 | 475.9 | 448.8 | 454 | 450.1 | 447.5 | 442.6 | 418.9
1863 | 1773 | 525.6 | 477.7 | 500.5 | 475.9 | 448.9 | 454.2 | 450.2 | 447.5 | 442.6 | 418.9
1864 | 1774 | 525.6 | 477.7 | 500.6 | 475.9 | 448.8 | 454.2 | 450.3 | 447.6 | 442.7 | 419
1865 | 1775 | 525.6 | 477.7 | 500.6 | 475.9 | 449 | 454.4 | 450.4 | 447.7 | 442.7 | 419
1866 | 1776 | 525.7 | 477.8 | 500.5 | 476 | 449.2 | 454.5 | 450.5 | 447.9 | 442.7 | 419.1
1867 | 1777 | 525.7 | 477.8 | 500.6 | 476 | 449.2 | 454.6 | 450.5 | 448 | 442.7 | 419.1
1868 | 1778 | 525.7 | 477.8 | 500.7 | 476 | 449.2 | 454.7 | 450.6 | 448.1 | 442.8 | 419.2
1869 | 1779 | 525.7 | 477.9 | 500.5 | 476.1 | 449.5 | 454.9 | 450.7 | 448.2 | 442.8 | 419.2
1870 | 1780 | 525.7 | 477.9 | 500.5 | 476.1 | 449.6 | 455.1 | 450.8 | 448.4 | 442.8 | 419.3
1871 | 1781 | 525.6 | 477.9 | 500.7 | 476.1 | 449.6 | 455.1 | 450.8 | 448.5 | 442.9 | 419.4
1872 | 1782 | 525.6 | 477.9 | 500.7 | 476.1 | 449.8 | 455.3 | 450.9 | 448.6 | 442.9 | 419.4
1873 | 1783 | 525.6 | 477.9 | 500.6 | 476.2 | 450 | 455.4 | 450.9 | 448.6 | 442.9 | 419.4
1874 | 1784 | 525.6 | 477.9 | 500.7 | 476.2 | 450.1 | 455.5 | 451 | 448.8 | 442.9 | 419.5
1875 | 1785 | 525.6 | 477.9 | 500.8 | 476.2 | 450 | 455.6 | 451 | 448.8 | 442.9 | 419.6
1876 | 1786 | 525.5 | 478 | 500.7 | 476.2 | 450.3 | 455.7 | 451.1 | 448.9 | 442.9 | 419.7
1877 | 1787 | 525.5 | 478 | 500.7 | 476.3 | 450.5 | 455.8 | 451.1 | 448.9 | 443 | 419.7
1878 | 1788 | 525.5 | 478 | 500.8 | 476.3 | 450.4 | 455.9 | 451.2 | 449 | 443.1 | 419.8
1879 | 1789 | 525.5 | 478 | 500.8 | 476.3 | 450.6 | 456 | 451.2 | 449.1 | 443.1 | 419.9
1880 | 1790 | 525.5 | 478.1 | 500.7 | 476.4 | 450.8 | 456.1 | 451.2 | 449.3 | 443.1 | 420
1881 | 1791 | 525.5 | 478.1 | 500.7 | 476.4 | 450.9 | 456.2 | 451.3 | 449.6 | 443.1 | 420
1882 | 1792 | 525.4 | 478 | 500.9 | 476.4 | 450.9 | 456.2 | 451.4 | 449.9 | 443.1 | 420.1
1883 | 1793 | 525.4 | 478.1 | 500.8 | 476.4 | 451.2 | 456.4 | 451.4 | 450.1 | 443.1 | 420.1
1884 | 1794 | 525.4 | 478.2 | 500.8 | 476.4 | 451.4 | 456.5 | 451.4 | 450.3 | 443.1 | 420.2
1885 | 1795 | 525.4 | 478.1 | 500.9 | 476.4 | 451.3 | 456.5 | 451.4 | 450.5 | 443.1 | 420.3
1886 | 1796 | 525.3 | 478.1 | 500.9 | 476.5 | 451.5 | 456.6 | 451.5 | 450.7 | 443.1 | 420.4
1887 | 1797 | 525.3 | 478.2 | 500.8 | 476.5 | 451.8 | 456.8 | 451.5 | 450.7 | 443.1 | 420.4
1888 | 1798 | 525.3 | 478.2 | 500.8 | 476.5 | 451.9 | 456.9 | 451.5 | 450.8 | 443.1 | 420.5
1889 | 1799 | 525.2 | 478.2 | 500.9 | 476.5 | 451.9 | 456.9 | 451.6 | 450.9 | 443.1 | 420.6
1890 | 1800 | 525.2 | 478.3 | 500.8 | 476.6 | 452.3 | 457.1 | 451.6 | 451 | 443.1 | 420.6
1891 | 1801 | 525.1 | 478.3 | 500.8 | 476.6 | 452.4 | 457.2 | 451.6 | 451.1 | 443.1 | 420.7
1892 | 1802 | 525.1 | 478.3 | 500.9 | 476.6 | 452.4 | 457.2 | 451.7 | 451.2 | 443 | 420.8
1893 | 1803 | 525.1 | 478.3 | 500.9 | 476.6 | 452.6 | 457.3 | 451.7 | 451.3 | 443 | 420.8
1894 | 1804 | 525.1 | 478.4 | 500.9 | 476.7 | 452.9 | 457.4 | 451.7 | 451.3 | 442.9 | 420.9
1895 | 1805 | 525.1 | 478.4 | 500.9 | 476.7 | 453 | 457.5 | 451.7 | 451.3 | 442.8 | 420.9
1896 | 1806 | 525.1 | 478.3 | 501 | 476.7 | 453.1 | 457.6 | 451.8 | 451.4 | 442.8 | 421
1897 | 1807 | 525.1 | 478.4 | 500.9 | 476.8 | 453.5 | 457.7 | 451.8 | 451.4 | 442.8 | 421
1898 | 1808 | 525.1 | 478.5 | 500.9 | 476.8 | 453.7 | 457.8 | 451.8 | 451.5 | 442.7 | 421.1
1899 | 1809 | 525.1 | 478.4 | 501 | 476.8 | 453.8 | 457.9 | 451.9 | 451.5 | 442.7 | 421.2
1900 | 1810 | 525.1 | 478.5 | 501 | 476.8 | 454.1 | 457.9 | 451.9 | 451.5 | 442.6 | 421.3
1901 | 1811 | 525.1 | 478.5 | 501 | 476.9 | 454.5 | 458 | 451.9 | 451.6 | 442.5 | 421.3
1902 | 1812 | 525.1 | 478.5 | 501 | 476.9 | 454.7 | 458.1 | 451.9 | 451.6 | 442.5 | 421.4
1903 | 1813 | 525.1 | 478.5 | 501.1 | 476.9 | 454.7 | 458.1 | 451.9 | 451.7 | 442.4 | 421.5
1904 | 1814 | 525.1 | 478.6 | 501 | 476.9 | 455.2 | 458.2 | 451.9 | 451.7 | 442.4 | 421.5
1905 | 1815 | 525.1 | 478.6 | 500.9 | 477 | 455.4 | 458.3 | 452 | 451.7 | 442.3 | 421.6
1906 | 1816 | 525.2 | 478.6 | 501 | 476.9 | 455.5 | 458.4 | 452 | 451.7 | 442.3 | 421.7
1907 | 1817 | 525.2 | 478.6 | 501 | 477 | 455.8 | 458.4 | 452 | 451.8 | 442.2 | 421.7
1908 | 1818 | 525.2 | 478.7 | 501 | 477 | 456.1 | 458.5 | 452.1 | 451.9 | 442.1 | 421.8
1909 | 1819 | 525.2 | 478.7 | 501 | 477 | 456.2 | 458.6 | 452.1 | 451.9 | 442.1 | 421.9
1910 | 1820 | 525.3 | 478.6 | 501.2 | 477 | 456.2 | 458.6 | 452.1 | 451.9 | 442 | 422
1911 | 1821 | 525.3 | 478.7 | 501 | 477.1 | 456.5 | 458.7 | 452.2 | 451.9 | 441.9 | 422
1912 | 1822 | 525.3 | 478.8 | 501 | 477.1 | 456.7 | 458.8 | 452.2 | 451.9 | 441.9 | 422.1
1913 | 1823 | 525.3 | 478.7 | 501.2 | 477.1 | 456.7 | 458.8 | 452.2 | 452 | 441.8 | 422.2
1914 | 1824 | 525.4 | 478.7 | 501.2 | 477.1 | 456.9 | 458.9 | 452.2 | 452 | 441.7 | 422.2
1915 | 1825 | 525.4 | 478.8 | 501.1 | 477.2 | 457.2 | 459 | 452.3 | 452 | 441.6 | 422.3
1916 | 1826 | 525.4 | 478.8 | 501.1 | 477.2 | 457.3 | 459 | 452.3 | 452.1 | 441.5 | 422.4
1917 | 1827 | 525.4 | 478.8 | 501.2 | 477.2 | 457.2 | 459.1 | 452.4 | 452.2 | 441.4 | 422.5
1918 | 1828 | 525.4 | 478.9 | 501.2 | 477.2 | 457.5 | 459.2 | 452.4 | 452.3 | 441.2 | 422.5
1919 | 1829 | 525.5 | 478.9 | 501.2 | 477.2 | 457.6 | 459.2 | 452.4 | 452.4 | 441.1 | 422.6
1920 | 1830 | 525.5 | 478.9 | 501.3 | 477.2 | 457.6 | 459.3 | 452.4 | 452.4 | 441 | 422.7
1921 | 1831 | 525.5 | 478.9 | 501.3 | 477.2 | 457.8 | 459.3 | 452.5 | 452.4 | 440.9 | 422.7
1922 | 1832 | 525.5 | 479 | 501.2 | 477.3 | 458 | 459.4 | 452.5 | 452.5 | 440.8 | 422.8
1923 | 1833 | 525.6 | 479 | 501.3 | 477.3 | 458.1 | 459.5 | 452.5 | 452.5 | 440.7 | 422.9
1924 | 1834 | 525.6 | 478.9 | 501.4 | 477.3 | 458 | 459.5 | 452.6 | 452.5 | 440.7 | 423
1925 | 1835 | 525.6 | 479 | 501.3 | 477.4 | 458.4 | 459.6 | 452.5 | 452.6 | 440.6 | 423
1926 | 1836 | 525.6 | 479.1 | 501.3 | 477.4 | 458.5 | 459.7 | 452.6 | 452.6 | 440.4 | 423.1
1927 | 1837 | 525.6 | 479 | 501.4 | 477.4 | 458.4 | 459.7 | 452.6 | 452.6 | 440.3 | 423.2
1928 | 1838 | 525.6 | 479 | 501.4 | 477.4 | 458.5 | 459.8 | 452.6 | 452.6 | 440.2 | 423.3
1929 | 1839 | 525.6 | 479.1 | 501.3 | 477.4 | 458.7 | 459.9 | 452.6 | 452.6 | 440.2 | 423.4
1930 | 1840 | 525.6 | 479.1 | 501.3 | 477.5 | 458.8 | 459.9 | 452.6 | 452.7 | 440.2 | 423.5
1931 | 1841 | 525.6 | 479.1 | 501.5 | 477.4 | 458.8 | 460 | 452.7 | 452.8 | 440.1 | 423.6
1932 | 1842 | 525.6 | 479.2 | 501.4 | 477.5 | 459 | 460.1 | 452.7 | 453 | 440.1 | 423.6
1933 | 1843 | 525.6 | 479.2 | 501.3 | 477.5 | 459.2 | 460.1 | 452.8 | 453 | 439.9 | 423.2
1934 | 1844 | 525.6 | 479.2 | 501.5 | 477.5 | 459.1 | 460.2 | 452.8 | 453.1 | 439.7 | 423.4
1935 | 1845 | 525.6 | 479.2 | 501.5 | 477.5 | 459.2 | 460.2 | 452.9 | 453.2 | 439.6 | 423.6
1936 | 1846 | 525.6 | 479.3 | 501.4 | 477.6 | 459.4 | 460.3 | 452.9 | 453.4 | 439.6 | 423.6
1937 | 1847 | 525.6 | 479.3 | 501.4 | 477.6 | 459.5 | 460.4 | 453 | 453.5 | 439.5 | 423.7
1938 | 1848 | 525.6 | 479.2 | 501.6 | 477.6 | 459.4 | 460.4 | 453 | 453.5 | 439.5 | 423.9
1939 | 1849 | 525.6 | 479.3 | 501.5 | 477.7 | 459.7 | 460.5 | 453.1 | 453.5 | 439.3 | 423.9
1940 | 1850 | 525.6 | 479.3 | 501.4 | 477.7 | 459.8 | 460.5 | 453.1 | 453.6 | 439.3 | 424
1941 | 1851 | 525.6 | 479.3 | 501.5 | 477.7 | 459.8 | 460.5 | 453.2 | 453.7 | 439.3 | 424.1
1942 | 1852 | 525.6 | 479.3 | 501.5 | 477.7 | 459.8 | 460.6 | 453.2 | 453.7 | 439.2 | 424.2
1943 | 1853 | 525.6 | 479.4 | 501.5 | 477.7 | 460 | 460.7 | 453.3 | 453.7 | 439.1 | 424.2
1944 | 1854 | 525.6 | 479.4 | 501.5 | 477.8 | 460.1 | 460.7 | 453.3 | 453.8 | 439 | 424.3
1945 | 1855 | 525.6 | 479.4 | 501.7 | 477.7 | 460 | 460.7 | 453.4 | 453.9 | 439 | 424.4
1946 | 1856 | 525.6 | 479.5 | 501.5 | 477.8 | 460.3 | 460.8 | 453.4 | 454 | 438.8 | 424.5
1947 | 1857 | 525.6 | 479.5 | 501.5 | 477.8 | 460.4 | 460.8 | 453.5 | 454.1 | 438.7 | 424.5
1948 | 1858 | 525.6 | 479.4 | 501.6 | 477.8 | 460.3 | 460.8 | 453.5 | 454.2 | 438.7 | 424.7
1949 | 1859 | 525.6 | 479.5 | 501.6 | 477.9 | 460.4 | 460.9 | 453.6 | 454.3 | 438.6 | 424.7
1950 | 1860 | 525.6 | 479.5 | 501.5 | 477.9 | 460.6 | 461 | 453.6 | 454.4 | 438 | 424.7
1951 | 1861 | 525.6 | 479.5 | 501.6 | 477.9 | 460.7 | 461 | 453.7 | 454.5 | 438.1 | 424.8
1952 | 1862 | 525.6 | 479.5 | 501.7 | 477.9 | 460.6 | 461 | 453.8 | 454.6 | 438.1 | 424.9
1953 | 1863 | 525.5 | 479.6 | 501.6 | 478 | 460.8 | 461.1 | 453.8 | 454.7 | 438 | 425
1954 | 1864 | 525.5 | 479.6 | 501.6 | 478 | 460.9 | 461.1 | 453.9 | 454.7 | 438 | 425.1
1955 | 1865 | 525.5 | 479.6 | 501.7 | 478 | 460.8 | 461.1 | 453.9 | 454.8 | 438 | 425.2
1956 | 1866 | 525.5 | 479.6 | 501.7 | 478 | 460.9 | 461.1 | 454 | 454.9 | 437.9 | 425.3
1957 | 1867 | 525.5 | 479.7 | 501.6 | 478.1 | 461.1 | 461.2 | 454 | 454.9 | 437.8 | 425.3
1958 | 1868 | 525.4 | 479.7 | 501.7 | 478.1 | 461.2 | 461.3 | 454.1 | 455 | 437.8 | 425.4
1959 | 1869 | 525.4 | 479.6 | 501.8 | 478.1 | 461.1 | 461.3 | 454.1 | 455.1 | 437.7 | 425.5
1960 | 1870 | 525.4 | 479.7 | 501.6 | 478.1 | 461.3 | 461.4 | 454.2 | 455.3 | 437.7 | 425.5
1961 | 1871 | 525.4 | 479.7 | 501.6 | 478.1 | 461.4 | 461.5 | 454.2 | 455.4 | 437.6 | 425.6
1962 | 1872 | 525.5 | 479.7 | 501.8 | 478.1 | 461.4 | 461.5 | 454.3 | 455.5 | 437.6 | 425.7
1963 | 1873 | 525.5 | 479.7 | 501.8 | 478.1 | 461.5 | 461.6 | 454.4 | 455.6 | 437.5 | 425.8
1964 | 1874 | 525.5 | 479.8 | 501.7 | 478.2 | 461.7 | 461.6 | 454.4 | 455.6 | 437.4 | 425.8
1965 | 1875 | 525.6 | 479.8 | 501.7 | 478.2 | 461.8 | 461.6 | 454.5 | 455.7 | 437.3 | 425.9
1966 | 1876 | 525.6 | 479.7 | 501.8 | 478.2 | 461.6 | 461.6 | 454.5 | 455.8 | 437.2 | 426
1967 | 1877 | 525.6 | 479.8 | 501.7 | 478.3 | 461.9 | 461.7 | 454.6 | 455.8 | 437.1 | 426.1
1968 | 1878 | 525.6 | 479.9 | 501.7 | 478.3 | 461.9 | 461.7 | 454.6 | 455.9 | 437.1 | 426.2
1969 | 1879 | 525.6 | 479.8 | 501.8 | 478.3 | 461.8 | 461.7 | 454.7 | 456 | 437 | 426.3
1970 | 1880 | 525.6 | 479.9 | 501.8 | 478.3 | 461.9 | 461.7 | 454.7 | 456 | 437 | 426.3
1971 | 1881 | 525.6 | 479.9 | 501.8 | 478.4 | 462.1 | 461.8 | 454.8 | 456.1 | 436.9 | 426.4
1972 | 1882 | 525.7 | 479.9 | 501.8 | 478.4 | 462.1 | 461.8 | 454.8 | 456.2 | 436.9 | 426.5
1973 | 1883 | 525.7 | 479.9 | 501.9 | 478.3 | 462 | 461.8 | 454.9 | 456.3 | 436.9 | 426.6
1974 | 1884 | 525.7 | 479.9 | 501.8 | 478.4 | 462.2 | 461.8 | 455 | 456.4 | 436.8 | 426.7
1975 | 1885 | 525.6 | 480 | 501.8 | 478.4 | 462.3 | 461.9 | 455 | 456.5 | 436.8 | 426.7
1976 | 1886 | 525.6 | 479.9 | 502 | 478.4 | 462.2 | 461.8 | 455.1 | 456.6 | 436.7 | 426.9
1977 | 1887 | 525.7 | 480 | 501.9 | 478.4 | 462.2 | 461.9 | 455.1 | 456.7 | 436.7 | 426.9
1978 | 1888 | 525.6 | 480 | 501.9 | 478.5 | 462.4 | 461.9 | 455.2 | 456.8 | 436.7 | 427
1979 | 1889 | 525.6 | 480 | 501.9 | 478.5 | 462.4 | 461.9 | 455.2 | 456.9 | 436.6 | 427
1980 | 1890 | 525.6 | 480 | 502.1 | 478.5 | 462.3 | 461.9 | 455.3 | 456.9 | 436.6 | 427.2
1981 | 1891 | 525.5 | 480.1 | 501.9 | 478.5 | 462.5 | 462 | 455.4 | 457 | 436.6 | 427.2
1982 | 1892 | 525.5 | 480.1 | 501.9 | 478.6 | 462.6 | 462 | 455.4 | 457.1 | 436.5 | 427.2
1983 | 1893 | 525.5 | 480.1 | 502 | 478.5 | 462.6 | 462 | 455.5 | 457.2 | 436.5 | 427.4
1984 | 1894 | 525.5 | 480.1 | 502 | 478.6 | 462.6 | 462.1 | 455.5 | 457.3 | 436.6 | 427.4
1985 | 1895 | 525.5 | 480.2 | 501.9 | 478.6 | 462.8 | 462.1 | 455.6 | 457.4 | 436.5 | 427.5
1986 | 1896 | 525.5 | 480.2 | 502 | 478.6 | 462.8 | 462.1 | 455.6 | 457.5 | 436.6 | 427.6
1987 | 1897 | 525.5 | 480.1 | 502.1 | 478.6 | 462.7 | 462.1 | 455.7 | 457.6 | 436.6 | 427.7
1988 | 1898 | 525.6 | 480.2 | 502 | 478.7 | 462.9 | 462.2 | 455.8 | 457.7 | 436.6 | 427.7
1989 | 1899 | 525.6 | 480.2 | 502 | 478.7 | 463 | 462.2 | 455.8 | 457.8 | 436.6 | 427.8
1990 | 1900 | 525.6 | 480.2 | 502 | 478.7 | 462.9 | 462.2 | 455.9 | 457.9 | 436.6 | 427.8
1991 | 1901 | 525.6 | 480.2 | 502.1 | 478.7 | 462.9 | 462.2 | 455.9 | 458 | 436.5 | 427.8
1992 | 1902 | 525.6 | 480.3 | 502 | 478.8 | 463.1 | 462.3 | 456 | 458.1 | 436.5 | 427.9
1993 | 1903 | 525.5 | 480.3 | 502 | 478.8 | 463.1 | 462.3 | 456 | 458.2 | 436.4 | 427.9
1994 | 1904 | 525.5 | 480.3 | 502.2 | 478.7 | 463 | 462.3 | 456.1 | 458.3 | 436.4 | 427.9
1995 | 1905 | 525.5 | 480.3 | 502.1 | 478.8 | 463.2 | 462.4 | 456.1 | 458.3 | 436.4 | 428
1996 | 1906 | 525.5 | 480.4 | 502.1 | 478.8 | 463.3 | 462.4 | 456.2 | 458.4 | 436.4 | 428
1997 | 1907 | 525.5 | 480.3 | 502.2 | 478.8 | 463.2 | 462.4 | 456.3 | 458.4 | 436.4 | 428.1
1998 | 1908 | 525.5 | 480.4 | 502.2 | 478.8 | 463.3 | 462.5 | 456.3 | 458.5 | 436.4 | 428.1
1999 | 1909 | 525.5 | 480.4 | 502.1 | 478.9 | 463.4 | 462.5 | 456.3 | 458.6 | 436.4 | 428.1
2000 | 1910 | 525.5 | 480.4 | 502.2 | 478.9 | 463.4 | 462.5 | 456.4 | 458.7 | 436.5 | 428.2
2001 | 1911 | 525.5 | 480.4 | 502.3 | 478.9 | 463.3 | 462.5 | 456.5 | 458.8 | 436.5 | 428.2
2002 | 1912 | 525.4 | 480.5 | 502.2 | 478.9 | 463.5 | 462.6 | 456.5 | 458.9 | 436.5 | 428.3
2003 | 1913 | 525.4 | 480.5 | 502.2 | 479 | 463.6 | 462.6 | 456.5 | 458.9 | 436.5 | 428.4
2004 | 1914 | 525.4 | 480.5 | 502.3 | 478.9 | 463.5 | 462.6 | 456.6 | 459 | 436.7 | 428.4
2005 | 1915 | 525.4 | 480.5 | 502.4 | 479 | 463.5 | 462.7 | 456.7 | 459 | 436.7 | 428.5
2006 | 1916 | 525.4 | 480.5 | 502.3 | 479 | 463.7 | 462.7 | 456.7 | 459.1 | 436.5 | 428.5
2007 | 1917 | 525.4 | 480.6 | 502.3 | 479 | 463.8 | 462.8 | 456.7 | 459.2 | 436.6 | 428.6
2008 | 1918 | 525.4 | 480.5 | 502.4 | 479 | 463.6 | 462.7 | 456.8 | 459.3 | 436.6 | 428.7
2009 | 1919 | 525.4 | 480.6 | 502.3 | 479.1 | 463.8 | 462.8 | 456.8 | 459.3 | 436.7 | 428.7
2010 | 1920 | 525.4 | 480.6 | 502.3 | 479.1 | 463.9 | 462.9 | 456.9 | 459.3 | 436.7 | 428.8
2011 | 1921 | 525.4 | 480.6 | 502.4 | 479.1 | 463.8 | 462.9 | 457 | 459.4 | 436.8 | 428.8
2012 | 1922 | 525.4 | 480.6 | 502.4 | 479.1 | 463.9 | 462.9 | 457 | 459.5 | 436.8 | 428.9
2013 | 1923 | 525.3 | 480.7 | 502.3 | 479.1 | 464 | 463 | 457.1 | 459.5 | 436.9 | 429
2014 | 1924 | 525.3 | 480.7 | 502.4 | 479.1 | 464 | 463 | 457.1 | 459.5 | 436.9 | 429
2015 | 1925 | 525.3 | 480.6 | 502.5 | 479.1 | 463.9 | 463 | 457.2 | 459.5 | 436.9 | 429.1
2016 | 1926 | 525.3 | 480.7 | 502.4 | 479.2 | 464.2 | 463.1 | 457.2 | 459.5 | 437 | 429.1
2017 | 1927 | 525.3 | 480.7 | 502.4 | 479.2 | 464.2 | 463.1 | 457.3 | 459.5 | 437 | 429.2
2018 | 1928 | 525.3 | 480.7 | 502.5 | 479.2 | 464.1 | 463.1 | 457.3 | 459.6 | 437 | 429.3
2019 | 1929 | 525.3 | 480.7 | 502.5 | 479.2 | 464.2 | 463.1 | 457.4 | 459.7 | 437 | 429.3
2020 | 1930 | 525.3 | 480.8 | 502.4 | 479.3 | 464.3 | 463.2 | 457.4 | 459.7 | 437 | 429.4
2021 | 1931 | 525.3 | 480.8 | 502.5 | 479.3 | 464.4 | 463.3 | 457.5 | 459.7 | 437.1 | 429.4
2022 | 1932 | 525.3 | 480.8 | 502.6 | 479.3 | 464.2 | 463.2 | 457.5 | 459.8 | 437.1 | 429.5
2023 | 1933 | 525.3 | 480.8 | 502.5 | 479.3 | 464.5 | 463.3 | 457.6 | 459.9 | 437.2 | 429.5
2024 | 1934 | 525.3 | 480.9 | 502.5 | 479.3 | 464.5 | 463.4 | 457.6 | 459.9 | 437.2 | 429.5
2025 | 1935 | 525.3 | 480.8 | 502.6 | 479.3 | 464.4 | 463.4 | 457.7 | 459.8 | 437.2 | 429.6
2026 | 1936 | 525.2 | 480.9 | 502.5 | 479.4 | 464.4 | 463.4 | 457.7 | 459.9 | 437.3 | 429.6
2027 | 1937 | 525.3 | 480.9 | 502.5 | 479.4 | 464.6 | 463.5 | 457.8 | 459.9 | 437.3 | 429.7
2028 | 1938 | 525.3 | 480.9 | 502.5 | 479.4 | 464.6 | 463.5 | 457.8 | 460.1 | 437.4 | 429.7
2029 | 1939 | 525.3 | 480.9 | 502.7 | 479.4 | 464.5 | 463.5 | 457.9 | 460.2 | 437.5 | 429.8
2030 | 1940 | 525.4 | 481 | 502.6 | 479.4 | 464.7 | 463.6 | 457.9 | 460.3 | 437.5 | 429.7
2031 | 1941 | 525.4 | 481 | 502.5 | 479.5 | 464.8 | 463.6 | 458 | 460.3 | 437.6 | 429.8
2032 | 1942 | 525.5 | 480.9 | 502.6 | 479.5 | 464.6 | 463.6 | 458 | 460.4 | 437.6 | 429.8
2033 | 1943 | 525.5 | 481 | 502.7 | 479.5 | 464.7 | 463.6 | 458.1 | 460.4 | 437.6 | 429.8
2034 | 1944 | 525.5 | 481 | 502.6 | 479.5 | 464.9 | 463.7 | 458.1 | 460.4 | 437.7 | 429.9
2035 | 1945 | 525.5 | 481 | 502.7 | 479.5 | 464.9 | 463.7 | 458.1 | 460.5 | 437.8 | 429.9
2036 | 1946 | 525.5 | 481 | 502.8 | 479.5 | 464.7 | 463.7 | 458.2 | 460.6 | 437.9 | 430
2037 | 1947 | 525.5 | 481.1 | 502.7 | 479.6 | 464.9 | 463.8 | 458.2 | 460.6 | 438 | 430
2038 | 1948 | 525.5 | 481.1 | 502.7 | 479.6 | 465 | 463.8 | 458.3 | 460.7 | 438.1 | 430
2039 | 1949 | 525.5 | 481.1 | 502.7 | 479.6 | 464.9 | 463.8 | 458.3 | 460.8 | 438.2 | 430
2040 | 1950 | 525.5 | 481.1 | 502.8 | 479.6 | 464.9 | 463.9 | 458.4 | 460.8 | 438.4 | 430
2041 | 1951 | 525.5 | 481.1 | 502.7 | 479.7 | 465.1 | 463.9 | 458.4 | 460.8 | 438.5 | 430
2042 | 1952 | 525.5 | 481.2 | 502.7 | 479.7 | 465.1 | 464 | 458.5 | 460.9 | 438.6 | 430
2043 | 1953 | 525.5 | 481.1 | 502.8 | 479.7 | 465 | 464 | 458.5 | 460.9 | 438.8 | 430.1
2044 | 1954 | 525.5 | 481.2 | 502.7 | 479.7 | 465.2 | 464 | 458.5 | 461 | 438.9 | 430
2045 | 1955 | 525.5 | 481.2 | 502.7 | 479.7 | 465.3 | 464.1 | 458.6 | 461.1 | 438.9 | 430
2046 | 1956 | 525.5 | 481.2 | 502.9 | 479.7 | 465.2 | 464.1 | 458.6 | 461.1 | 439 | 430
2047 | 1957 | 525.5 | 481.2 | 502.9 | 479.7 | 465.2 | 464.1 | 458.7 | 461 | 439.1 | 430
2048 | 1958 | 525.5 | 481.3 | 502.8 | 479.8 | 465.4 | 464.2 | 458.7 | 461 | 439.2 | 430
2049 | 1959 | 525.5 | 481.3 | 502.8 | 479.8 | 465.4 | 464.2 | 458.8 | 461.1 | 439.3 | 430
2050 | 1960 | 525.4 | 481.2 | 503 | 479.8 | 465.3 | 464.2 | 458.8 | 461.2 | 439.4 | 430.1
2051 | 1961 | 525.4 | 481.3 | 502.8 | 479.9 | 465.5 | 464.3 | 458.9 | 461.3 | 439.5 | 430
2052 | 1962 | 525.4 | 481.3 | 502.8 | 479.9 | 465.5 | 464.3 | 458.9 | 461.3 | 439.6 | 430
2053 | 1963 | 525.3 | 481.3 | 502.9 | 479.9 | 465.4 | 464.3 | 458.9 | 461.3 | 439.8 | 430
2054 | 1964 | 525.3 | 481.3 | 502.9 | 479.9 | 465.5 | 464.4 | 459 | 461.3 | 439.9 | 429.9
2055 | 1965 | 525.3 | 481.4 | 502.9 | 479.9 | 465.6 | 464.4 | 459 | 461.4 | 440.1 | 429.8
2056 | 1966 | 525.2 | 481.4 | 502.9 | 479.9 | 465.6 | 464.4 | 459 | 461.4 | 440.2 | 429.8
2057 | 1967 | 525.2 | 481.3 | 503 | 479.9 | 465.5 | 464.4 | 459.1 | 461.5 | 440.3 | 429.8
2058 | 1968 | 525.2 | 481.4 | 502.9 | 480 | 465.7 | 464.5 | 459.1 | 461.5 | 440.4 | 429.7
2059 | 1969 | 525.2 | 481.4 | 502.9 | 480 | 465.8 | 464.6 | 459.1 | 461.5 | 440.5 | 429.7
2060 | 1970 | 525.2 | 481.4 | 503.1 | 480 | 465.7 | 464.6 | 459.2 | 461.5 | 440.6 | 429.7
2061 | 1971 | 525.2 | 481.4 | 503.1 | 480 | 465.7 | 464.6 | 459.2 | 461.5 | 440.7 | 429.7
2062 | 1972 | 525.2 | 481.5 | 503 | 480 | 465.9 | 464.7 | 459.2 | 461.5 | 440.8 | 429.6
2063 | 1973 | 525.2 | 481.5 | 503 | 480 | 465.9 | 464.7 | 459.3 | 461.6 | 441 | 429.6
2064 | 1974 | 525.2 | 481.4 | 503.1 | 480 | 465.8 | 464.7 | 459.4 | 461.7 | 441.1 | 429.6
2065 | 1975 | 525.1 | 481.5 | 503 | 480.1 | 466 | 464.8 | 459.4 | 461.7 | 441.1 | 429.6
2066 | 1976 | 525.1 | 481.6 | 503 | 480.1 | 466.1 | 464.8 | 459.4 | 461.7 | 441.1 | 429.6
2067 | 1977 | 525.1 | 481.5 | 503.1 | 480.1 | 466 | 464.8 | 459.5 | 461.7 | 441.4 | 429.6
2068 | 1978 | 525.2 | 481.5 | 503.1 | 480.1 | 466 | 464.8 | 459.5 | 461.7 | 441.5 | 429.6
2069 | 1979 | 525.2 | 481.6 | 503.1 | 480.1 | 466.2 | 464.9 | 459.6 | 461.7 | 441.5 | 429.6
2070 | 1980 | 525.2 | 481.6 | 503.1 | 480.2 | 466.2 | 465 | 459.6 | 461.7 | 441.6 | 429.6
2071 | 1981 | 525.2 | 481.5 | 503.2 | 480.1 | 466.1 | 464.9 | 459.7 | 461.7 | 441.7 | 429.7
2072 | 1982 | 525.2 | 481.6 | 503.1 | 480.2 | 466.3 | 465 | 459.7 | 461.7 | 441.7 | 429.6
2073 | 1983 | 525.2 | 481.7 | 503.1 | 480.2 | 466.4 | 465.1 | 459.7 | 461.8 | 441.8 | 429.6
2074 | 1984 | 525.3 | 481.6 | 503.2 | 480.2 | 466.3 | 465.1 | 459.8 | 461.8 | 441.9 | 429.6
2075 | 1985 | 525.3 | 481.6 | 503.2 | 480.2 | 466.3 | 465.1 | 459.8 | 461.8 | 442 | 429.7
2076 | 1986 | 525.3 | 481.7 | 503.1 | 480.3 | 466.5 | 465.2 | 459.9 | 461.9 | 442.1 | 429.7
2077 | 1987 | 525.4 | 481.7 | 503.2 | 480.3 | 466.5 | 465.2 | 459.9 | 461.9 | 442.2 | 429.7
2078 | 1988 | 525.4 | 481.7 | 503.3 | 480.3 | 466.4 | 465.2 | 460 | 462 | 442.3 | 429.7
2079 | 1989 | 525.5 | 481.7 | 503.2 | 480.3 | 466.6 | 465.3 | 460 | 462.1 | 442.4 | 429.7
2080 | 1990 | 525.5 | 481.8 | 503.2 | 480.3 | 466.7 | 465.3 | 460 | 462.2 | 442.4 | 429.7
2081 | 1991 | 525.5 | 481.7 | 503.3 | 480.3 | 466.6 | 465.3 | 460.1 | 462.3 | 442.5 | 429.8
2082 | 1992 | 525.5 | 481.7 | 503.3 | 480.3 | 466.6 | 465.3 | 460.1 | 462.4 | 442.6 | 429.9
2083 | 1993 | 525.5 | 481.8 | 503.3 | 480.4 | 466.8 | 465.4 | 460.2 | 462.4 | 442.7 | 429.8
2084 | 1994 | 525.5 | 481.8 | 503.3 | 480.4 | 466.8 | 465.5 | 460.2 | 462.5 | 442.8 | 429.8
2085 | 1995 | 525.5 | 481.8 | 503.4 | 480.4 | 466.7 | 465.4 | 460.3 | 462.5 | 442.9 | 429.9
2086 | 1996 | 525.5 | 481.8 | 503.3 | 480.4 | 466.9 | 465.5 | 460.3 | 462.4 | 442.9 | 429.9
2087 | 1997 | 525.4 | 481.9 | 503.3 | 480.5 | 466.9 | 465.6 | 460.3 | 462.5 | 443 | 429.9
2088 | 1998 | 525.4 | 481.8 | 503.4 | 480.4 | 466.9 | 465.6 | 460.4 | 462.5 | 443.1 | 429.9
2089 | 1999 | 525.4 | 481.8 | 503.4 | 480.5 | 466.9 | 465.6 | 460.4 | 462.5 | 443.1 | 430
2090 | 2000 | 525.4 | 481.9 | 503.3 | 480.5 | 467.1 | 465.7 | 460.4 | 462.5 | 443.2 | 430
2091 | 2001 | 525.4 | 481.9 | 503.3 | 480.6 | 467.1 | 465.7 | 460.5 | 462.6 | 443.2 | 430
2092 | 2002 | 525.4 | 481.9 | 503.5 | 480.5 | 466.9 | 465.7 | 460.5 | 462.7 | 443.3 | 430.1
2093 | 2003 | 525.3 | 481.9 | 503.4 | 480.6 | 467.2 | 465.8 | 460.5 | 462.7 | 443.4 | 430.1
2094 | 2004 | 525.3 | 482 | 503.3 | 480.6 | 467.3 | 465.8 | 460.6 | 462.7 | 443.4 | 430
2095 | 2005 | 525.3 | 481.9 | 503.5 | 480.6 | 467.1 | 465.8 | 460.6 | 462.8 | 443.4 | 430.1
2096 | 2006 | 525.2 | 481.9 | 503.5 | 480.6 | 467.2 | 465.9 | 460.6 | 462.8 | 443.5 | 430.2
2097 | 2007 | 525.3 | 482 | 503.4 | 480.6 | 467.3 | 465.9 | 460.7 | 462.8 | 443.6 | 430.2
2098 | 2008 | 525.3 | 482 | 503.4 | 480.6 | 467.3 | 466 | 460.7 | 462.9 | 443.7 | 430.2
2099 | 2009 | 525.3 | 482.1 | 503.3 | 480.7 | 467.4 | 466 | 460.7 | 463 | 443.7 | 430.3
2100 | 2010 | 525.3 | 482 | 503.4 | 480.7 | 467.4 | 466 | 460.8 | 462.9 | 443.8 | 430.4
2101 | 2011 | 525.3 | 482.1 | 503.4 | 480.7 | 467.5 | 466.1 | 460.8 | 462.9 | 443.8 | 430.4
2102 | 2012 | 525.3 | 482 | 503.5 | 480.7 | 467.5 | 466.1 | 460.9 | 463 | 443.9 | 430.5
2103 | 2013 | 525.4 | 482 | 503.6 | 480.7 | 467.4 | 466.1 | 460.9 | 463 | 443.9 | 430.5
2104 | 2014 | 525.4 | 482.1 | 503.5 | 480.8 | 467.6 | 466.2 | 460.9 | 463 | 444 | 430.5
2105 | 2015 | 525.4 | 482.1 | 503.6 | 480.8 | 467.6 | 466.2 | 461 | 463.1 | 444.1 | 430.6
2106 | 2016 | 525.5 | 482.1 | 503.7 | 480.7 | 467.5 | 466.2 | 461 | 463.2 | 444.2 | 430.7
2107 | 2017 | 525.5 | 482.1 | 503.6 | 480.8 | 467.7 | 466.3 | 461.1 | 463.2 | 444.2 | 430.8
2108 | 2018 | 525.5 | 482.2 | 503.6 | 480.8 | 467.8 | 466.3 | 461.1 | 463.2 | 444.3 | 430.8
2109 | 2019 | 525.6 | 482.1 | 503.6 | 480.8 | 467.7 | 466.3 | 461.1 | 463.1 | 444.3 | 430.9
2110 | 2020 | 525.6 | 482.2 | 503.7 | 480.8 | 467.7 | 466.4 | 461.2 | 463.2 | 444.4 | 430.9
2111 | 2021 | 525.6 | 482.2 | 503.6 | 480.9 | 467.9 | 466.4 | 461.2 | 463.3 | 444.5 | 430.9
2112 | 2022 | 525.6 | 482.2 | 503.7 | 480.9 | 467.9 | 466.5 | 461.3 | 463.4 | 444.5 | 430.9
2113 | 2023 | 525.6 | 482.2 | 503.8 | 480.9 | 467.8 | 466.5 | 461.3 | 463.5 | 444.6 | 431
2114 | 2024 | 525.6 | 482.2 | 503.7 | 480.9 | 468 | 466.5 | 461.3 | 463.5 | 444.7 | 431.1
2115 | 2025 | 525.6 | 482.3 | 503.7 | 480.9 | 468.1 | 466.6 | 461.4 | 463.4 | 444.7 | 431.1
2116 | 2026 | 525.6 | 482.2 | 503.8 | 480.9 | 468 | 466.6 | 461.4 | 463.4 | 444.7 | 431.1
2117 | 2027 | 525.6 | 482.3 | 503.8 | 480.9 | 468 | 466.6 | 461.5 | 463.4 | 444.7 | 431
2118 | 2028 | 525.5 | 482.3 | 503.7 | 481 | 468.2 | 466.7 | 461.5 | 463.5 | 444.7 | 431
2119 | 2029 | 525.5 | 482.3 | 503.7 | 481 | 468.2 | 466.7 | 461.5 | 463.5 | 444.8 | 431.2
2120 | 2030 | 525.5 | 482.3 | 503.8 | 481 | 468 | 466.7 | 461.6 | 463.5 | 444.9 | 431.3
2121 | 2031 | 525.5 | 482.3 | 503.8 | 481 | 468.2 | 466.8 | 461.6 | 463.5 | 444.9 | 431.4
2122 | 2032 | 525.5 | 482.4 | 503.7 | 481.1 | 468.3 | 466.8 | 461.6 | 463.5 | 445 | 431.4
2123 | 2033 | 525.4 | 482.3 | 503.9 | 481 | 468.2 | 466.8 | 461.7 | 463.6 | 445.1 | 431.5
2124 | 2034 | 525.4 | 482.4 | 503.9 | 481 | 468.3 | 466.9 | 461.7 | 463.6 | 445.2 | 431.6
2125 | 2035 | 525.4 | 482.4 | 503.8 | 481.1 | 468.4 | 466.9 | 461.7 | 463.6 | 445.1 | 431.5
2126 | 2036 | 525.4 | 482.4 | 503.8 | 481.1 | 468.4 | 467 | 461.8 | 463.7 | 445.1 | 431.5
2127 | 2037 | 525.4 | 482.4 | 504 | 481.1 | 468.3 | 466.9 | 461.8 | 463.8 | 445.2 | 431.6
2128 | 2038 | 525.3 | 482.4 | 503.9 | 481.1 | 468.5 | 467 | 461.8 | 463.8 | 445.2 | 431.5
2129 | 2039 | 525.3 | 482.5 | 503.9 | 481.2 | 468.5 | 467.1 | 461.9 | 463.8 | 445.2 | 431.5
2130 | 2040 | 525.3 | 482.4 | 504 | 481.1 | 468.5 | 467 | 461.9 | 463.8 | 445.3 | 431.6
2131 | 2041 | 525.3 | 482.4 | 504 | 481.1 | 468.5 | 467.1 | 462 | 463.8 | 445.4 | 431.7
2132 | 2042 | 525.3 | 482.5 | 503.9 | 481.2 | 468.6 | 467.2 | 462 | 463.9 | 445.5 | 431.8
2133 | 2043 | 525.3 | 482.5 | 503.9 | 481.2 | 468.7 | 467.2 | 462 | 463.9 | 445.6 | 431.8
2134 | 2044 | 525.3 | 482.5 | 504.1 | 481.2 | 468.5 | 467.2 | 462.1 | 463.9 | 445.6 | 431.9
2135 | 2045 | 525.3 | 482.5 | 504 | 481.2 | 468.7 | 467.3 | 462.1 | 463.9 | 445.7 | 431.8
2136 | 2046 | 525.3 | 482.6 | 504 | 481.3 | 468.8 | 467.3 | 462.1 | 463.9 | 445.7 | 431.8
2137 | 2047 | 525.3 | 482.5 | 504.1 | 481.2 | 468.7 | 467.3 | 462.2 | 464 | 445.7 | 431.9
2138 | 2048 | 525.3 | 482.6 | 504.1 | 481.3 | 468.8 | 467.4 | 462.2 | 464 | 445.7 | 431.9
2139 | 2049 | 525.3 | 482.6 | 504 | 481.3 | 469 | 467.4 | 462.2 | 464 | 445.8 | 431.9
2140 | 2050 | 525.3 | 482.6 | 504 | 481.3 | 469 | 467.5 | 462.3 | 464 | 445.8 | 432
2141 | 2051 | 525.3 | 482.6 | 504.1 | 481.3 | 468.9 | 467.5 | 462.3 | 464 | 445.9 | 432
2142 | 2052 | 525.2 | 482.7 | 504 | 481.4 | 469.1 | 467.6 | 462.3 | 464.1 | 446 | 432
2143 | 2053 | 525.2 | 482.7 | 504 | 481.4 | 469.2 | 467.6 | 462.4 | 464 | 446 | 432
2144 | 2054 | 525.1 | 482.7 | 504.1 | 481.4 | 469.1 | 467.6 | 462.4 | 464.1 | 446.1 | 432.1
2145 | 2055 | 525.2 | 482.7 | 504.1 | 481.3 | 469.1 | 467.6 | 462.5 | 464.2 | 446.1 | 432.1
2146 | 2056 | 525.2 | 482.7 | 504.1 | 481.4 | 469.3 | 467.7 | 462.5 | 464.2 | 446.2 | 432.1
2147 | 2057 | 525.2 | 482.7 | 504.1 | 481.4 | 469.3 | 467.7 | 462.6 | 464.2 | 446.2 | 432.1
2148 | 2058 | 525.2 | 482.7 | 504.3 | 481.4 | 469.1 | 467.7 | 462.6 | 464.3 | 446.3 | 432.2
2149 | 2059 | 525.2 | 482.8 | 504.1 | 481.5 | 469.3 | 467.8 | 462.6 | 464.3 | 446.3 | 432.2
2150 | 2060 | 525.2 | 482.8 | 504.1 | 481.5 | 469.4 | 467.9 | 462.7 | 464.3 | 446.4 | 432.2
2151 | 2061 | 525.3 | 482.8 | 504.2 | 481.5 | 469.3 | 467.9 | 462.7 | 464.4 | 446.4 | 432.3
2152 | 2062 | 525.3 | 482.8 | 504.2 | 481.5 | 469.3 | 467.9 | 462.8 | 464.4 | 446.5 | 432.4
2153 | 2063 | 525.3 | 482.8 | 504.2 | 481.5 | 469.5 | 468 | 462.8 | 464.5 | 446.5 | 432.5
2154 | 2064 | 525.3 | 482.8 | 504.2 | 481.5 | 469.5 | 468 | 462.8 | 464.5 | 446.4 | 432.6
2155 | 2065 | 525.3 | 482.8 | 504.3 | 481.5 | 469.4 | 468 | 462.9 | 464.6 | 446.5 | 432.7
2156 | 2066 | 525.3 | 482.9 | 504.3 | 481.5 | 469.6 | 468 | 462.9 | 464.7 | 446.6 | 432.7
2157 | 2067 | 525.2 | 482.9 | 504.2 | 481.6 | 469.7 | 468.1 | 463 | 464.8 | 446.7 | 432.8
2158 | 2068 | 525.2 | 482.9 | 504.3 | 481.5 | 469.6 | 468.1 | 463 | 464.9 | 446.7 | 432.8
2159 | 2069 | 525.2 | 482.9 | 504.4 | 481.5 | 469.6 | 468.1 | 463.1 | 465 | 446.7 | 432.9
2160 | 2070 | 525.2 | 482.9 | 504.3 | 481.6 | 469.7 | 468.2 | 463.1 | 465 | 446.8 | 432.9
2161 | 2071 | 525.2 | 482.9 | 504.3 | 481.6 | 469.8 | 468.2 | 463.1 | 465 | 446.9 | 433
2162 | 2072 | 525.1 | 482.9 | 504.5 | 481.6 | 469.6 | 468.2 | 463.2 | 465 | 446.9 | 433
2163 | 2073 | 525 | 483 | 504.4 | 481.6 | 469.9 | 468.3 | 463.2 | 465.1 | 446.9 | 433
2164 | 2074 | 525 | 483 | 504.3 | 481.7 | 470 | 468.4 | 463.3 | 465.1 | 447 | 433.1
2165 | 2075 | 525 | 483 | 504.4 | 481.6 | 469.9 | 468.4 | 463.3 | 465.2 | 447 | 433.3
2166 | 2076 | 524.9 | 483 | 504.5 | 481.7 | 469.9 | 468.4 | 463.4 | 465.2 | 447.1 | 433.3
2167 | 2077 | 524.9 | 483.1 | 504.4 | 481.7 | 470.1 | 468.5 | 463.4 | 465.2 | 447.2 | 433.4
2168 | 2078 | 524.9 | 483 | 504.4 | 481.7 | 470.1 | 468.5 | 463.4 | 465.2 | 447.2 | 433.5
2169 | 2079 | 524.9 | 483.1 | 504.4 | 481.7 | 470.1 | 468.6 | 463.5 | 465.1 | 447.3 | 433.5
2170 | 2080 | 524.9 | 483.1 | 504.4 | 481.7 | 470.2 | 468.6 | 463.5 | 465.1 | 447.3 | 433.6
2171 | 2081 | 524.9 | 483.1 | 504.4 | 481.7 | 470.3 | 468.7 | 463.6 | 465.2 | 447.3 | 433.6
2172 | 2082 | 524.8 | 483.1 | 504.5 | 481.7 | 470.2 | 468.7 | 463.6 | 465.3 | 447.5 | 433.7
2173 | 2083 | 524.8 | 483.1 | 504.6 | 481.7 | 470.2 | 468.7 | 463.7 | 465.3 | 447.5 | 433.7
2174 | 2084 | 524.8 | 483.2 | 504.4 | 481.8 | 470.4 | 468.8 | 463.7 | 465.3 | 447.6 | 433.7
2175 | 2085 | 524.8 | 483.2 | 504.5 | 481.8 | 470.4 | 468.8 | 463.7 | 465.4 | 447.7 | 433.6
2176 | 2086 | 524.8 | 483.1 | 504.6 | 481.8 | 470.3 | 468.8 | 463.8 | 465.5 | 447.8 | 433.7
2177 | 2087 | 524.8 | 483.2 | 504.5 | 481.8 | 470.5 | 468.9 | 463.8 | 465.5 | 447.7 | 433.7
2178 | 2088 | 524.8 | 483.2 | 504.5 | 481.9 | 470.6 | 468.9 | 463.9 | 465.6 | 447.8 | 433.7
2179 | 2089 | 524.8 | 483.2 | 504.6 | 481.8 | 470.5 | 468.9 | 463.9 | 465.6 | 447.8 | 433.8
2180 | 2090 | 524.8 | 483.2 | 504.6 | 481.9 | 470.6 | 469 | 464 | 465.6 | 447.9 | 433.8
2181 | 2091 | 524.8 | 483.2 | 504.5 | 481.9 | 470.7 | 469.1 | 464 | 465.6 | 447.9 | 433.7
2182 | 2092 | 524.9 | 483.2 | 504.5 | 481.9 | 470.7 | 469.1 | 464 | 465.7 | 447.9 | 433.7
2183 | 2093 | 524.9 | 483.2 | 504.6 | 481.9 | 470.6 | 469.1 | 464.1 | 465.8 | 448 | 433.8
2184 | 2094 | 524.9 | 483.3 | 504.6 | 481.9 | 470.8 | 469.2 | 464.1 | 465.8 | 448 | 433.8
2185 | 2095 | 524.9 | 483.3 | 504.6 | 482 | 470.8 | 469.2 | 464.2 | 465.9 | 448.1 | 433.8
2186 | 2096 | 525 | 483.3 | 504.7 | 482 | 470.8 | 469.2 | 464.2 | 466 | 448.1 | 433.9
2187 | 2097 | 525 | 483.2 | 504.7 | 482 | 470.8 | 469.2 | 464.2 | 466.1 | 448.1 | 433.9
2188 | 2098 | 525 | 483.3 | 504.6 | 482 | 471 | 469.3 | 464.3 | 466.2 | 448.2 | 433.9
2189 | 2099 | 525 | 483.3 | 504.6 | 482 | 471 | 469.3 | 464.3 | 466.3 | 448.3 | 433.9
2190 | 2100 | 525 | 483.3 | 504.8 | 482 | 470.8 | 469.3 | 464.4 | 466.3 | 448.3 | 433.9
2191 | 2101 | 525.1 | 483.4 | 504.7 | 482 | 471 | 469.4 | 464.4 | 466.2 | 448.4 | 433.9
2192 | 2102 | 525.1 | 483.4 | 504.7 | 482.1 | 471.1 | 469.4 | 464.4 | 466.2 | 448.4 | 433.8
2193 | 2103 | 525.2 | 483.3 | 504.8 | 482 | 471 | 469.5 | 464.5 | 466.2 | 448.5 | 433.8
2194 | 2104 | 525.2 | 483.3 | 504.8 | 482 | 471 | 469.5 | 464.5 | 466.3 | 448.5 | 433.9
2195 | 2105 | 525.2 | 483.4 | 504.7 | 482.1 | 471.2 | 469.6 | 464.6 | 466.3 | 448.5 | 433.9
2196 | 2106 | 525.2 | 483.4 | 504.8 | 482.1 | 471.2 | 469.6 | 464.6 | 466.4 | 448.5 | 433.9
2197 | 2107 | 525.3 | 483.4 | 504.9 | 482.1 | 471.1 | 469.6 | 464.7 | 466.4 | 448.6 | 433.9
2198 | 2108 | 525.3 | 483.4 | 504.8 | 482.1 | 471.3 | 469.6 | 464.7 | 466.4 | 448.6 | 433.9
2199 | 2109 | 525.3 | 483.4 | 504.8 | 482.1 | 471.4 | 469.7 | 464.7 | 466.4 | 448.6 | 433.8
2200 | 2110 | 525.3 | 483.4 | 504.9 | 482.1 | 471.3 | 469.7 | 464.8 | 466.5 | 448.6 | 433.9
2201 | 2111 | 525.3 | 483.4 | 504.9 | 482.1 | 471.3 | 469.7 | 464.8 | 466.5 | 448.6 | 434
2202 | 2112 | 525.3 | 483.5 | 504.8 | 482.2 | 471.5 | 469.8 | 464.8 | 466.5 | 448.7 | 434
2203 | 2113 | 525.3 | 483.5 | 504.8 | 482.2 | 471.5 | 469.8 | 464.9 | 466.5 | 448.7 | 434
2204 | 2114 | 525.3 | 483.4 | 505 | 482.2 | 471.4 | 469.8 | 464.9 | 466.6 | 448.7 | 434.1
2205 | 2115 | 525.2 | 483.5 | 504.9 | 482.2 | 471.6 | 469.9 | 465 | 466.7 | 448.7 | 434
2206 | 2116 | 525.2 | 483.5 | 504.9 | 482.2 | 471.6 | 470 | 465 | 466.7 | 448.8 | 434
2207 | 2117 | 525.2 | 483.5 | 505 | 482.2 | 471.6 | 470 | 465.1 | 466.7 | 448.8 | 434
2208 | 2118 | 525.2 | 483.5 | 505 | 482.2 | 471.6 | 470 | 465.1 | 466.8 | 448.9 | 434
2209 | 2119 | 525.3 | 483.6 | 504.9 | 482.3 | 471.8 | 470.1 | 465.1 | 466.8 | 448.9 | 434
2210 | 2120 | 525.3 | 483.6 | 504.9 | 482.3 | 471.8 | 470.1 | 465.2 | 466.8 | 449 | 434
2211 | 2121 | 525.3 | 483.5 | 505.1 | 482.2 | 471.6 | 470.1 | 465.2 | 466.8 | 449.1 | 434.1
2212 | 2122 | 525.3 | 483.6 | 505 | 482.3 | 471.9 | 470.2 | 465.3 | 466.8 | 449.1 | 434.1
2213 | 2123 | 525.3 | 483.6 | 505 | 482.3 | 471.9 | 470.3 | 465.3 | 466.9 | 449.1 | 434.2
2214 | 2124 | 525.3 | 483.6 | 505.1 | 482.3 | 471.8 | 470.3 | 465.4 | 466.9 | 449.2 | 434.3
2215 | 2125 | 525.3 | 483.6 | 505.1 | 482.3 | 471.8 | 470.3 | 465.4 | 466.8 | 449.3 | 434.3
2216 | 2126 | 525.3 | 483.7 | 505 | 482.3 | 472.1 | 470.4 | 465.5 | 466.8 | 449.3 | 434.3
2217 | 2127 | 525.3 | 483.7 | 505 | 482.4 | 472.1 | 470.4 | 465.5 | 466.8 | 449.4 | 434.3
2218 | 2128 | 525.2 | 483.6 | 505.2 | 482.3 | 471.9 | 470.4 | 465.6 | 466.9 | 449.5 | 434.4
2219 | 2129 | 525.2 | 483.7 | 505.1 | 482.4 | 472.1 | 470.5 | 465.6 | 467 | 449.5 | 434.4
2220 | 2130 | 525.2 | 483.7 | 505.1 | 482.4 | 472.2 | 470.5 | 465.6 | 467 | 449.5 | 434.5
2221 | 2131 | 525.2 | 483.7 | 505.2 | 482.4 | 472.1 | 470.5 | 465.7 | 467.1 | 449.5 | 434.7
2222 | 2132 | 525.2 | 483.7 | 505.1 | 482.4 | 472.2 | 470.6 | 465.7 | 467.1 | 449.6 | 434.8
2223 | 2133 | 525.2 | 483.8 | 505.1 | 482.5 | 472.4 | 470.7 | 465.8 | 467.2 | 449.5 | 434.8
2224 | 2134 | 525.2 | 483.8 | 505.1 | 482.5 | 472.4 | 470.7 | 465.8 | 467.3 | 449.6 | 434.8
2225 | 2135 | 525.2 | 483.7 | 505.3 | 482.4 | 472.2 | 470.7 | 465.9 | 467.3 | 449.7 | 435
2226 | 2136 | 525.2 | 483.8 | 505.2 | 482.5 | 472.4 | 470.8 | 465.9 | 467.3 | 449.7 | 435
2227 | 2137 | 525.2 | 483.8 | 505.2 | 482.5 | 472.5 | 470.8 | 465.9 | 467.4 | 449.8 | 435.1
2228 | 2138 | 525.2 | 483.7 | 505.3 | 482.5 | 472.4 | 470.8 | 466 | 467.5 | 449.9 | 435.2
2229 | 2139 | 525.2 | 483.7 | 505.3 | 482.5 | 472.4 | 470.8 | 466 | 467.5 | 450 | 435.3
2230 | 2140 | 525.3 | 483.8 | 505.2 | 482.5 | 472.6 | 470.9 | 466.1 | 467.5 | 450 | 435.3
2231 | 2141 | 525.3 | 483.8 | 505.3 | 482.5 | 472.7 | 471 | 466.1 | 467.6 | 450.1 | 435.3
2232 | 2142 | 525.3 | 483.8 | 505.4 | 482.5 | 472.5 | 471 | 466.2 | 467.7 | 450.1 | 435.4
2233 | 2143 | 525.3 | 483.8 | 505.3 | 482.6 | 472.7 | 471.1 | 466.2 | 467.7 | 450.1 | 435.4
2234 | 2144 | 525.3 | 483.9 | 505.2 | 482.6 | 472.8 | 471.1 | 466.3 | 467.7 | 450.1 | 435.4
2235 | 2145 | 525.3 | 483.8 | 505.3 | 482.6 | 472.7 | 471.1 | 466.3 | 467.7 | 450.2 | 435.4
2236 | 2146 | 525.4 | 483.9 | 505.4 | 482.6 | 472.7 | 471.1 | 466.4 | 467.8 | 450.2 | 435.5
2237 | 2147 | 525.4 | 483.9 | 505.3 | 482.6 | 472.9 | 471.2 | 466.4 | 467.8 | 450.2 | 435.4
2238 | 2148 | 525.4 | 483.9 | 505.3 | 482.6 | 472.9 | 471.2 | 466.5 | 467.9 | 450.2 | 435.3
2239 | 2149 | 525.4 | 483.9 | 505.5 | 482.6 | 472.8 | 471.2 | 466.5 | 467.9 | 450.3 | 435.4
2240 | 2150 | 525.5 | 483.9 | 505.4 | 482.7 | 473 | 471.3 | 466.6 | 467.9 | 450.3 | 435.4
2241 | 2151 | 525.4 | 484 | 505.4 | 482.7 | 473.1 | 471.4 | 466.6 | 468 | 450.3 | 435.5
2242 | 2152 | 525.5 | 483.9 | 505.4 | 482.7 | 473 | 471.4 | 466.6 | 468 | 450.4 | 435.6
2243 | 2153 | 525.5 | 483.9 | 505.5 | 482.7 | 473 | 471.4 | 466.7 | 468 | 450.4 | 435.6
2244 | 2154 | 525.5 | 484 | 505.4 | 482.7 | 473.2 | 471.5 | 466.7 | 468.1 | 450.5 | 435.6
2245 | 2155 | 525.6 | 484 | 505.4 | 482.7 | 473.2 | 471.5 | 466.8 | 468.2 | 450.5 | 435.6
2246 | 2156 | 525.6 | 483.9 | 505.6 | 482.7 | 473 | 471.5 | 466.8 | 468.2 | 450.6 | 435.8
2247 | 2157 | 525.5 | 484 | 505.5 | 482.7 | 473.3 | 471.6 | 466.9 | 468.2 | 450.6 | 435.8
2248 | 2158 | 525.5 | 484 | 505.5 | 482.8 | 473.3 | 471.6 | 466.9 | 468.2 | 450.7 | 435.8
2249 | 2159 | 525.5 | 484 | 505.6 | 482.8 | 473.3 | 471.6 | 467 | 468.2 | 450.8 | 435.8
2250 | 2160 | 525.6 | 484 | 505.6 | 482.8 | 473.2 | 471.7 | 467 | 468.2 | 450.8 | 435.9
2251 | 2161 | 525.5 | 484.1 | 505.5 | 482.8 | 473.5 | 471.8 | 467.1 | 468.2 | 450.8 | 435.8
2252 | 2162 | 525.6 | 484 | 505.6 | 482.8 | 473.5 | 471.8 | 467.1 | 468.3 | 450.8 | 435.8
2253 | 2163 | 525.6 | 484 | 505.7 | 482.8 | 473.3 | 471.8 | 467.2 | 468.3 | 450.9 | 435.8
2254 | 2164 | 525.5 | 484.1 | 505.6 | 482.8 | 473.5 | 471.9 | 467.2 | 468.3 | 450.9 | 435.7
2255 | 2165 | 525.5 | 484.1 | 505.6 | 482.9 | 473.6 | 471.9 | 467.2 | 468.4 | 451 | 435.8
2256 | 2166 | 525.5 | 484.1 | 505.7 | 482.9 | 473.5 | 471.9 | 467.3 | 468.4 | 451 | 435.9
2257 | 2167 | 525.5 | 484.1 | 505.7 | 482.9 | 473.5 | 472 | 467.3 | 468.5 | 451.1 | 435.9
2258 | 2168 | 525.5 | 484.1 | 505.6 | 482.9 | 473.8 | 472.1 | 467.4 | 468.5 | 451.1 | 436
2259 | 2169 | 525.5 | 484.2 | 505.6 | 482.9 | 473.8 | 472.1 | 467.4 | 468.6 | 451.2 | 436
2260 | 2170 | 525.4 | 484.1 | 505.8 | 482.9 | 473.6 | 472.1 | 467.5 | 468.6 | 451.2 | 436.1
2261 | 2171 | 525.4 | 484.2 | 505.7 | 482.9 | 473.8 | 472.2 | 467.5 | 468.6 | 451.2 | 436.1
2262 | 2172 | 525.4 | 484.2 | 505.6 | 483 | 473.9 | 472.2 | 467.5 | 468.7 | 451.3 | 436.1
2263 | 2173 | 525.4 | 484.1 | 505.7 | 482.9 | 473.8 | 472.2 | 467.6 | 468.7 | 451.3 | 436.2
2264 | 2174 | 525.4 | 484.2 | 505.8 | 482.9 | 473.8 | 472.3 | 467.6 | 468.6 | 451.4 | 436.2
2265 | 2175 | 525.4 | 484.2 | 505.7 | 483 | 474 | 472.4 | 467.7 | 468.7 | 451.4 | 436.3
2266 | 2176 | 525.4 | 484.2 | 505.7 | 483 | 474.1 | 472.4 | 467.7 | 468.7 | 451.4 | 436.3
2267 | 2177 | 525.4 | 484.2 | 505.9 | 483 | 473.9 | 472.4 | 467.8 | 468.8 | 451.5 | 436.4
2268 | 2178 | 525.4 | 484.2 | 505.7 | 483 | 474.1 | 472.5 | 467.8 | 468.8 | 451.5 | 436.4
2269 | 2179 | 525.4 | 484.3 | 505.7 | 483.1 | 474.2 | 472.5 | 467.9 | 468.9 | 451.6 | 436.4
2270 | 2180 | 525.4 | 484.2 | 505.8 | 483 | 474.1 | 472.5 | 467.9 | 468.9 | 451.6 | 436.5
2271 | 2181 | 525.4 | 484.2 | 505.9 | 483 | 474.1 | 472.6 | 468 | 469 | 451.7 | 436.5
2272 | 2182 | 525.4 | 484.3 | 505.8 | 483.1 | 474.3 | 472.6 | 468 | 469 | 451.7 | 436.5
2273 | 2183 | 525.4 | 484.3 | 505.8 | 483.1 | 474.4 | 472.7 | 468 | 469.1 | 451.7 | 436.5
2274 | 2184 | 525.5 | 484.2 | 505.9 | 483.1 | 474.2 | 472.7 | 468.1 | 469.2 | 451.8 | 436.5
2275 | 2185 | 525.5 | 484.3 | 505.8 | 483.1 | 474.4 | 472.8 | 468.1 | 469.3 | 451.9 | 436.5
2276 | 2186 | 525.5 | 484.3 | 505.8 | 483.1 | 474.5 | 472.8 | 468.2 | 469.4 | 451.9 | 436.5
2277 | 2187 | 525.6 | 484.3 | 505.9 | 483.1 | 474.4 | 472.8 | 468.3 | 469.4 | 451.9 | 436.5
2278 | 2188 | 525.6 | 484.3 | 505.9 | 483.1 | 474.4 | 472.9 | 468.3 | 469.4 | 452 | 436.5
2279 | 2189 | 525.6 | 484.4 | 505.8 | 483.2 | 474.6 | 472.9 | 468.4 | 469.4 | 452 | 436.5
2280 | 2190 | 525.6 | 484.4 | 505.9 | 483.2 | 474.6 | 473 | 468.4 | 469.4 | 452 | 436.6
2281 | 2191 | 525.6 | 484.4 | 506 | 483.2 | 474.5 | 473 | 468.5 | 469.4 | 452.1 | 436.6
2282 | 2192 | 525.5 | 484.4 | 505.9 | 483.2 | 474.7 | 473.1 | 468.5 | 469.4 | 452.1 | 436.5
2283 | 2193 | 525.5 | 484.4 | 505.9 | 483.2 | 474.8 | 473.1 | 468.6 | 469.4 | 452.2 | 436.6
2284 | 2194 | 525.5 | 484.4 | 506 | 483.2 | 474.7 | 473.1 | 468.6 | 469.4 | 452.3 | 436.7
2285 | 2195 | 525.5 | 484.4 | 506 | 483.2 | 474.7 | 473.2 | 468.7 | 469.5 | 452.3 | 436.7
2286 | 2196 | 525.5 | 484.5 | 505.9 | 483.3 | 474.9 | 473.3 | 468.7 | 469.5 | 452.3 | 436.8
2287 | 2197 | 525.5 | 484.5 | 505.9 | 483.3 | 475 | 473.3 | 468.8 | 469.6 | 452.4 | 436.7
2288 | 2198 | 525.5 | 484.4 | 506.1 | 483.2 | 474.8 | 473.3 | 468.8 | 469.7 | 452.4 | 436.8
2289 | 2199 | 525.6 | 484.5 | 506 | 483.3 | 475 | 473.4 | 468.9 | 469.6 | 452.4 | 436.8
2290 | 2200 | 525.6 | 484.5 | 506 | 483.3 | 475.1 | 473.4 | 468.9 | 469.5 | 452.5 | 436.9
2291 | 2201 | 525.6 | 484.5 | 506.1 | 483.3 | 475 | 473.4 | 469 | 469.6 | 452.5 | 436.9
2292 | 2202 | 525.6 | 484.5 | 506.1 | 483.3 | 475 | 473.5 | 469 | 469.7 | 452.5 | 437
2293 | 2203 | 525.6 | 484.5 | 506 | 483.4 | 475.2 | 473.5 | 469 | 469.8 | 452.6 | 437
2294 | 2204 | 525.6 | 484.5 | 506 | 483.4 | 475.3 | 473.6 | 469.1 | 469.9 | 452.6 | 437.1
2295 | 2205 | 525.6 | 484.4 | 506.2 | 483.3 | 475.1 | 473.6 | 469.2 | 470 | 452.7 | 437.1
2296 | 2206 | 525.5 | 484.5 | 506.1 | 483.4 | 475.3 | 473.7 | 469.2 | 470 | 452.7 | 437.1
2297 | 2207 | 525.6 | 484.5 | 506.1 | 483.4 | 475.4 | 473.7 | 469.2 | 470.1 | 452.7 | 437.2
2298 | 2208 | 525.6 | 484.5 | 506.2 | 483.4 | 475.3 | 473.7 | 469.3 | 470.1 | 452.8 | 437.2
2299 | 2209 | 525.6 | 484.5 | 506.2 | 483.4 | 475.3 | 473.8 | 469.3 | 470.1 | 452.8 | 437.3
2300 | 2210 | 525.6 | 484.6 | 506.1 | 483.5 | 475.5 | 473.9 | 469.4 | 470.1 | 452.8 | 437.3
2301 | 2211 | 525.6 | 484.6 | 506.1 | 483.5 | 475.6 | 473.9 | 469.4 | 470 | 452.8 | 437.3
2302 | 2212 | 525.6 | 484.5 | 506.3 | 483.4 | 475.4 | 473.9 | 469.5 | 470 | 452.9 | 437.3
2303 | 2213 | 525.6 | 484.6 | 506.2 | 483.5 | 475.6 | 474 | 469.5 | 470 | 452.9 | 437.3
2304 | 2214 | 525.6 | 484.6 | 506.2 | 483.5 | 475.7 | 474 | 469.5 | 470.1 | 452.9 | 437.4
2305 | 2215 | 525.6 | 484.6 | 506.3 | 483.5 | 475.6 | 474 | 469.6 | 470.2 | 452.9 | 437.5
2306 | 2216 | 525.6 | 484.6 | 506.3 | 483.5 | 475.6 | 474.1 | 469.7 | 470.3 | 453 | 437.4
2307 | 2217 | 525.6 | 484.6 | 506.2 | 483.5 | 475.8 | 474.2 | 469.7 | 470.4 | 453.1 | 437.5
2308 | 2218 | 525.6 | 484.7 | 506.3 | 483.5 | 475.9 | 474.2 | 469.7 | 470.4 | 453.1 | 437.5
2309 | 2219 | 525.6 | 484.6 | 506.4 | 483.5 | 475.7 | 474.2 | 469.8 | 470.4 | 453.2 | 437.6
2310 | 2220 | 525.6 | 484.7 | 506.2 | 483.6 | 476 | 474.3 | 469.8 | 470.4 | 453.2 | 437.6
2311 | 2221 | 525.6 | 484.7 | 506.2 | 483.6 | 476 | 474.3 | 469.9 | 470.5 | 453.2 | 437.6
2312 | 2222 | 525.6 | 484.6 | 506.4 | 483.5 | 475.9 | 474.3 | 469.9 | 470.7 | 453.3 | 437.6
2313 | 2223 | 525.7 | 484.6 | 506.4 | 483.5 | 475.9 | 474.4 | 470 | 470.7 | 453.3 | 437.6
2314 | 2224 | 525.6 | 484.7 | 506.3 | 483.6 | 476.1 | 474.5 | 470 | 470.7 | 453.3 | 437.7
2315 | 2225 | 525.6 | 484.7 | 506.3 | 483.6 | 476.2 | 474.5 | 470.1 | 470.8 | 453.4 | 437.7
2316 | 2226 | 525.6 | 484.6 | 506.5 | 483.5 | 476 | 474.5 | 470.2 | 470.9 | 453.4 | 437.7
2317 | 2227 | 525.6 | 484.7 | 506.4 | 483.6 | 476.2 | 474.6 | 470.2 | 470.8 | 453.5 | 437.7
2318 | 2228 | 525.6 | 484.7 | 506.4 | 483.6 | 476.3 | 474.7 | 470.3 | 470.8 | 453.5 | 437.6
2319 | 2229 | 525.6 | 484.7 | 506.4 | 483.6 | 476.2 | 474.7 | 470.3 | 470.9 | 453.6 | 437.6
2320 | 2230 | 525.6 | 484.7 | 506.5 | 483.6 | 476.2 | 474.7 | 470.4 | 470.9 | 453.6 | 437.6
2321 | 2231 | 525.6 | 484.8 | 506.4 | 483.7 | 476.4 | 474.8 | 470.4 | 471 | 453.6 | 437.6
2322 | 2232 | 525.6 | 484.8 | 506.4 | 483.7 | 476.4 | 474.9 | 470.5 | 471.1 | 453.7 | 437.6
2323 | 2233 | 525.6 | 484.7 | 506.6 | 483.6 | 476.3 | 474.8 | 470.6 | 471.2 | 453.7 | 437.6
2324 | 2234 | 525.6 | 484.8 | 506.5 | 483.7 | 476.5 | 474.9 | 470.6 | 471.2 | 453.8 | 437.7
2325 | 2235 | 525.6 | 484.8 | 506.5 | 483.7 | 476.6 | 475 | 470.6 | 471.2 | 453.8 | 437.7
2326 | 2236 | 525.6 | 484.8 | 506.5 | 483.7 | 476.5 | 475 | 470.7 | 471.3 | 453.8 | 437.7
2327 | 2237 | 525.6 | 484.8 | 506.6 | 483.7 | 476.5 | 475 | 470.8 | 471.3 | 453.8 | 437.7
2328 | 2238 | 525.6 | 484.8 | 506.5 | 483.7 | 476.7 | 475.1 | 470.8 | 471.2 | 453.9 | 437.6
2329 | 2239 | 525.6 | 484.8 | 506.5 | 483.7 | 476.8 | 475.2 | 470.8 | 471.2 | 453.9 | 437.7
2330 | 2240 | 525.6 | 484.8 | 506.6 | 483.7 | 476.6 | 475.2 | 470.9 | 471.3 | 453.9 | 437.7
2331 | 2241 | 525.6 | 484.9 | 506.6 | 483.8 | 476.8 | 475.3 | 470.9 | 471.3 | 453.9 | 437.7
2332 | 2242 | 525.6 | 484.9 | 506.5 | 483.8 | 476.9 | 475.3 | 471 | 471.3 | 453.9 | 437.7
2333 | 2243 | 525.6 | 484.8 | 506.6 | 483.8 | 476.8 | 475.3 | 471 | 471.3 | 454 | 437.7
2334 | 2244 | 525.6 | 484.8 | 506.6 | 483.8 | 476.8 | 475.4 | 471.1 | 471.3 | 454 | 437.7
2335 | 2245 | 525.6 | 484.9 | 506.5 | 483.8 | 477.1 | 475.4 | 471.1 | 471.4 | 454.1 | 437.8
2336 | 2246 | 525.6 | 484.9 | 506.6 | 483.8 | 477.1 | 475.5 | 471.2 | 471.5 | 454.1 | 437.7
2337 | 2247 | 525.6 | 484.8 | 506.7 | 483.8 | 476.9 | 475.5 | 471.3 | 471.5 | 454.2 | 437.7
2338 | 2248 | 525.6 | 484.9 | 506.6 | 483.8 | 477.2 | 475.6 | 471.3 | 471.6 | 454.2 | 437.7
2339 | 2249 | 525.6 | 485 | 506.6 | 483.8 | 477.2 | 475.6 | 471.3 | 471.6 | 454.2 | 437.7
2340 | 2250 | 525.6 | 484.9 | 506.7 | 483.8 | 477.2 | 475.6 | 471.4 | 471.7 | 454.2 | 437.7
2341 | 2251 | 525.6 | 484.9 | 506.8 | 483.8 | 477.1 | 475.7 | 471.4 | 471.7 | 454.3 | 437.7
2342 | 2252 | 525.6 | 485 | 506.7 | 483.9 | 477.4 | 475.8 | 471.5 | 471.7 | 454.3 | 437.7
2343 | 2253 | 525.6 | 485 | 506.7 | 483.9 | 477.4 | 475.8 | 471.5 | 471.8 | 454.3 | 437.6
2344 | 2254 | 525.6 | 484.9 | 506.8 | 483.8 | 477.2 | 475.8 | 471.6 | 471.8 | 454.4 | 437.7
2345 | 2255 | 525.6 | 485 | 506.7 | 483.9 | 477.5 | 475.9 | 471.6 | 471.9 | 454.4 | 437.6
2346 | 2256 | 525.6 | 485 | 506.7 | 483.9 | 477.6 | 476 | 471.7 | 471.9 | 454.5 | 437.5
2347 | 2257 | 525.6 | 485 | 506.8 | 483.9 | 477.5 | 476 | 471.8 | 471.9 | 454.5 | 437.5
2348 | 2258 | 525.6 | 485 | 506.8 | 483.9 | 477.5 | 476 | 471.8 | 472 | 454.6 | 437.5
2349 | 2259 | 525.6 | 485 | 506.7 | 483.9 | 477.7 | 476.1 | 471.9 | 472 | 454.6 | 437.6
2350 | 2260 | 525.6 | 485 | 506.7 | 483.9 | 477.7 | 476.2 | 471.9 | 472.1 | 454.7 | 437.7
2351 | 2261 | 525.6 | 485 | 506.9 | 483.9 | 477.6 | 476.2 | 472 | 472.1 | 454.7 | 437.8
2352 | 2262 | 525.6 | 485 | 506.8 | 483.9 | 477.8 | 476.2 | 472 | 472.2 | 454.7 | 437.8
2353 | 2263 | 525.5 | 485.1 | 506.7 | 484 | 477.9 | 476.3 | 472.1 | 472.3 | 454.7 | 437.7
2354 | 2264 | 525.5 | 485 | 506.8 | 483.9 | 477.8 | 476.3 | 472.2 | 472.3 | 454.7 | 437.7
2355 | 2265 | 525.5 | 485 | 506.9 | 483.9 | 477.8 | 476.4 | 472.2 | 472.4 | 454.8 | 437.8
2356 | 2266 | 525.5 | 485.1 | 506.8 | 484 | 478.1 | 476.4 | 472.2 | 472.5 | 454.8 | 437.8
2357 | 2267 | 525.5 | 485.1 | 506.8 | 484 | 478.1 | 476.5 | 472.3 | 472.5 | 454.8 | 437.8
2358 | 2268 | 525.5 | 485.1 | 507 | 484 | 477.9 | 476.5 | 472.4 | 472.5 | 454.9 | 437.8
2359 | 2269 | 525.5 | 485.1 | 506.9 | 484 | 478.1 | 476.6 | 472.4 | 472.5 | 454.9 | 437.8
2360 | 2270 | 525.5 | 485.1 | 506.9 | 484 | 478.2 | 476.6 | 472.5 | 472.6 | 454.9 | 437.8
2361 | 2271 | 525.5 | 485.1 | 507 | 484 | 478.1 | 476.6 | 472.5 | 472.7 | 454.9 | 437.8
2362 | 2272 | 525.5 | 485.1 | 507 | 484 | 478.1 | 476.7 | 472.6 | 472.8 | 455 | 437.9
2363 | 2273 | 525.5 | 485.2 | 506.9 | 484 | 478.3 | 476.8 | 472.6 | 472.8 | 455 | 437.9
2364 | 2274 | 525.5 | 485.2 | 506.9 | 484 | 478.4 | 476.8 | 472.7 | 472.9 | 455 | 438
2365 | 2275 | 525.6 | 485.1 | 507 | 484 | 478.2 | 476.8 | 472.8 | 472.9 | 455 | 438.1
2366 | 2276 | 525.6 | 485.2 | 507 | 484.1 | 478.4 | 476.9 | 472.8 | 472.9 | 455.1 | 438.1
2367 | 2277 | 525.6 | 485.2 | 506.9 | 484.1 | 478.5 | 477 | 472.9 | 473 | 455.1 | 438
2368 | 2278 | 525.6 | 485.2 | 507 | 484.1 | 478.5 | 477 | 472.9 | 473 | 455.1 | 438
2369 | 2279 | 525.7 | 485.2 | 507.1 | 484.1 | 478.4 | 477 | 473 | 473.1 | 455.2 | 438
2370 | 2280 | 525.7 | 485.2 | 507 | 484.1 | 478.7 | 477.1 | 473 | 473.2 | 455.2 | 437.9
2371 | 2281 | 525.7 | 485.2 | 507 | 484.1 | 478.7 | 477.1 | 473.1 | 473.3 | 455.2 | 437.9
2372 | 2282 | 525.7 | 485.2 | 507.2 | 484.1 | 478.5 | 477.1 | 473.2 | 473.4 | 455.3 | 437.9
2373 | 2283 | 525.7 | 485.2 | 507 | 484.1 | 478.7 | 477.2 | 473.2 | 473.4 | 455.3 | 438
2374 | 2284 | 525.7 | 485.3 | 507 | 484.1 | 478.8 | 477.3 | 473.2 | 473.5 | 455.3 | 438
2375 | 2285 | 525.7 | 485.2 | 507.1 | 484.1 | 478.7 | 477.3 | 473.3 | 473.5 | 455.4 | 438
2376 | 2286 | 525.7 | 485.2 | 507.2 | 484.1 | 478.7 | 477.3 | 473.4 | 473.5 | 455.4 | 438.1
2377 | 2287 | 525.7 | 485.3 | 507.1 | 484.2 | 478.9 | 477.4 | 473.4 | 473.6 | 455.4 | 438
2378 | 2288 | 525.7 | 485.2 | 507.3 | 484.1 | 478.7 | 477.4 | 473.5 | 473.7 | 455.4 | 438.1
2379 | 2289 | 525.6 | 485 | 507.7 | 483.9 | 478.3 | 477.3 | 473.6 | 473.7 | 455.5 | 438.2
2380 | 2290 | 525.6 | 485 | 507.8 | 483.9 | 478.4 | 477.3 | 473.6 | 473.7 | 455.5 | 438.2
2381 | 2291 | 525.4 | 485 | 507.8 | 483.9 | 478.5 | 477.4 | 473.7 | 473.7 | 455.6 | 438.2
2382 | 2292 | 525.2 | 485 | 507.9 | 483.9 | 478.4 | 477.4 | 473.8 | 473.8 | 455.6 | 438.2
2383 | 2293 | 524.8 | 484.9 | 507.9 | 483.9 | 478.4 | 477.4 | 473.8 | 473.8 | 455.7 | 438.1
2384 | 2294 | 524.4 | 485 | 507.7 | 483.9 | 478.6 | 477.5 | 473.9 | 473.8 | 455.7 | 438.1
2385 | 2295 | 524 | 485 | 507.7 | 483.9 | 478.7 | 477.6 | 473.9 | 473.8 | 455.8 | 438.1
2386 | 2296 | 523.5 | 484.9 | 507.8 | 483.9 | 478.5 | 477.6 | 474 | 473.9 | 455.8 | 438.1
2387 | 2297 | 522.9 | 485 | 507.7 | 483.9 | 478.7 | 477.6 | 474.1 | 473.9 | 455.9 | 438.2
2388 | 2298 | 522.3 | 485 | 507.6 | 483.9 | 478.8 | 477.7 | 474.1 | 474 | 455.9 | 438.2
2389 | 2299 | 521.7 | 484.9 | 507.7 | 483.8 | 478.7 | 477.7 | 474.2 | 474 | 455.9 | 438.1
2390 | 2300 | 521.1 | 484.9 | 507.6 | 483.8 | 478.8 | 477.8 | 474.3 | 474 | 455.9 | 438.1
2391 | 2301 | 520.4 | 484.9 | 507.4 | 483.8 | 479 | 477.8 | 474.3 | 474.1 | 455.9 | 438
2392 | 2302 | 519.7 | 484.9 | 507.4 | 483.8 | 479 | 477.9 | 474.4 | 474.2 | 456 | 438
2393 | 2303 | 519 | 484.8 | 507.5 | 483.7 | 478.8 | 477.9 | 474.4 | 474.2 | 456 | 438
2394 | 2304 | 518.2 | 484.8 | 507.3 | 483.7 | 479 | 478 | 474.5 | 474.2 | 456 | 438
2395 | 2305 | 517.5 | 484.8 | 507.2 | 483.7 | 479.1 | 478 | 474.5 | 474.2 | 456 | 438
2396 | 2306 | 516.8 | 484.7 | 507.2 | 483.6 | 479.1 | 478 | 474.6 | 474.3 | 456.1 | 438
2397 | 2307 | 516.1 | 484.7 | 507.2 | 483.6 | 479.1 | 478.1 | 474.7 | 474.3 | 456.1 | 438
2398 | 2308 | 515.3 | 484.7 | 507 | 483.6 | 479.3 | 478.2 | 474.7 | 474.4 | 456.1 | 438.1
2399 | 2309 | 514.5 | 484.7 | 506.9 | 483.6 | 479.3 | 478.2 | 474.8 | 474.5 | 456.1 | 438.1
2400 | 2310 | 513.7 | 484.6 | 507 | 483.5 | 479.2 | 478.2 | 474.9 | 474.6 | 456.2 | 438.1
2401 | 2311 | 512.9 | 484.6 | 506.8 | 483.5 | 479.4 | 478.3 | 474.9 | 474.7 | 456.2 | 438
2402 | 2312 | 512.1 | 484.5 | 506.7 | 483.4 | 479.5 | 478.3 | 475 | 474.7 | 456.2 | 438
2403 | 2313 | 511.3 | 484.5 | 506.7 | 483.4 | 479.4 | 478.3 | 475 | 474.8 | 456.2 | 438
2404 | 2314 | 510.5 | 484.4 | 506.6 | 483.3 | 479.4 | 478.4 | 475.1 | 474.8 | 456.3 | 438
2405 | 2315 | 509.7 | 484.4 | 506.4 | 483.3 | 479.6 | 478.5 | 475.2 | 474.7 | 456.3 | 438
2406 | 2316 | 508.8 | 484.3 | 506.3 | 483.2 | 479.6 | 478.5 | 475.2 | 474.8 | 456.3 | 437.9
2407 | 2317 | 508 | 484.2 | 506.3 | 483.1 | 479.5 | 478.5 | 475.3 | 474.9 | 456.4 | 438
2408 | 2318 | 507.2 | 484.2 | 506.1 | 483.1 | 479.7 | 478.6 | 475.3 | 474.9 | 456.4 | 438
2409 | 2319 | 506.3 | 484.1 | 506 | 483 | 479.8 | 478.7 | 475.4 | 475 | 456.4 | 438
2410 | 2320 | 505.5 | 484 | 505.9 | 482.9 | 479.7 | 478.7 | 475.5 | 475.1 | 456.4 | 437.9
2411 | 2321 | 504.8 | 483.9 | 505.9 | 482.9 | 479.7 | 478.7 | 475.5 | 475.2 | 456.5 | 437.9
2412 | 2322 | 504 | 483.9 | 505.7 | 482.8 | 479.9 | 478.8 | 475.6 | 475.2 | 456.5 | 437.9
2413 | 2323 | 503.2 | 483.9 | 505.5 | 482.8 | 479.9 | 478.8 | 475.6 | 475.2 | 456.5 | 437.9
2414 | 2324 | 502.5 | 483.7 | 505.5 | 482.7 | 479.8 | 478.8 | 475.7 | 475.2 | 456.5 | 437.8
2415 | 2325 | 501.7 | 483.7 | 505.3 | 482.6 | 480 | 478.9 | 475.8 | 475.2 | 456.5 | 437.7
2416 | 2326 | 500.9 | 483.7 | 505.1 | 482.6 | 480.1 | 478.9 | 475.8 | 475.3 | 456.5 | 437.6
2417 | 2327 | 500.1 | 483.5 | 505.1 | 482.4 | 480 | 478.9 | 475.9 | 475.3 | 456.6 | 437.6
2418 | 2328 | 499.5 | 483.4 | 505 | 482.3 | 480 | 479 | 475.9 | 475.3 | 456.6 | 437.7
2419 | 2329 | 498.7 | 483.4 | 504.8 | 482.3 | 480.2 | 479.1 | 476 | 475.3 | 456.6 | 437.6
2420 | 2330 | 497.9 | 483.3 | 504.7 | 482.2 | 480.2 | 479.1 | 476 | 475.3 | 456.6 | 437.7
2421 | 2331 | 497.2 | 483.2 | 504.7 | 482.1 | 480.1 | 479.1 | 476.1 | 475.4 | 456.6 | 437.7
2422 | 2332 | 496.4 | 483.1 | 504.4 | 482.1 | 480.2 | 479.1 | 476.1 | 475.4 | 456.6 | 437.7
2423 | 2333 | 495.6 | 483.1 | 504.2 | 482 | 480.3 | 479.2 | 476.2 | 475.4 | 456.6 | 437.6
2424 | 2334 | 494.8 | 482.9 | 504.2 | 481.9 | 480.2 | 479.2 | 476.2 | 475.4 | 456.6 | 437.6
2425 | 2335 | 494 | 482.8 | 504.2 | 481.7 | 480.2 | 479.2 | 476.3 | 475.5 | 456.6 | 437.6
2426 | 2336 | 493.3 | 482.8 | 503.9 | 481.7 | 480.4 | 479.3 | 476.3 | 475.5 | 456.6 | 437.5
2427 | 2337 | 492.5 | 482.7 | 503.7 | 481.6 | 480.4 | 479.3 | 476.4 | 475.6 | 456.6 | 437.5
2428 | 2338 | 491.7 | 482.5 | 503.7 | 481.4 | 480.3 | 479.3 | 476.4 | 475.6 | 456.6 | 437.5
2429 | 2339 | 491 | 482.4 | 503.5 | 481.4 | 480.4 | 479.4 | 476.5 | 475.7 | 456.6 | 437.4
2430 | 2340 | 490.2 | 482.4 | 503.3 | 481.3 | 480.5 | 479.4 | 476.5 | 475.8 | 456.6 | 437.4
2431 | 2341 | 489.4 | 482.2 | 503.2 | 481.2 | 480.4 | 479.4 | 476.6 | 475.8 | 456.7 | 437.4
2432 | 2342 | 488.7 | 482.1 | 503.1 | 481 | 480.4 | 479.4 | 476.6 | 475.8 | 456.7 | 437.4
2433 | 2343 | 487.9 | 482 | 502.8 | 480.9 | 480.6 | 479.5 | 476.7 | 475.8 | 456.7 | 437.3
2434 | 2344 | 487.2 | 481.9 | 502.7 | 480.8 | 480.6 | 479.6 | 476.7 | 475.9 | 456.8 | 437.2
2435 | 2345 | 486.4 | 481.7 | 502.6 | 480.7 | 480.5 | 479.5 | 476.8 | 475.9 | 456.8 | 437.2
2436 | 2346 | 485.7 | 481.7 | 502.3 | 480.6 | 480.7 | 479.6 | 476.8 | 475.8 | 456.7 | 437.2
2437 | 2347 | 484.9 | 481.6 | 502.1 | 480.5 | 480.7 | 479.6 | 476.9 | 475.8 | 456.7 | 437.2
2438 | 2348 | 484.1 | 481.4 | 502.1 | 480.4 | 480.6 | 479.6 | 476.9 | 475.8 | 456.7 | 437.1
2439 | 2349 | 483.3 | 481.3 | 501.9 | 480.2 | 480.6 | 479.6 | 477 | 475.8 | 456.8 | 437.1
2440 | 2350 | 482.6 | 481.2 | 501.6 | 480.2 | 480.8 | 479.7 | 477 | 475.9 | 456.8 | 437
2441 | 2351 | 481.9 | 481.1 | 501.4 | 480.1 | 480.8 | 479.7 | 477 | 475.9 | 456.7 | 437
2442 | 2352 | 481.1 | 480.9 | 501.4 | 479.9 | 480.6 | 479.7 | 477.1 | 476 | 456.7 | 437
2443 | 2353 | 480.3 | 480.8 | 501.1 | 479.8 | 480.8 | 479.8 | 477.1 | 475.9 | 456.7 | 437
2444 | 2354 | 479.6 | 480.7 | 500.9 | 479.7 | 480.9 | 479.8 | 477.2 | 475.9 | 456.7 | 437
2445 | 2355 | 478.8 | 480.6 | 500.8 | 479.5 | 480.8 | 479.8 | 477.2 | 475.9 | 456.7 | 437
2446 | 2356 | 478.1 | 480.4 | 500.7 | 479.4 | 480.8 | 479.8 | 477.2 | 476 | 456.7 | 437
2447 | 2357 | 477.4 | 480.4 | 500.3 | 479.3 | 481 | 479.9 | 477.3 | 476.1 | 456.7 | 437
2448 | 2358 | 476.7 | 480.2 | 500.2 | 479.2 | 481 | 479.9 | 477.3 | 476.1 | 456.7 | 436.9
2449 | 2359 | 476 | 480 | 500.1 | 479 | 480.8 | 479.9 | 477.3 | 476.1 | 456.7 | 437
2450 | 2360 | 475.3 | 479.9 | 499.9 | 478.9 | 481 | 479.9 | 477.4 | 476.2 | 456.6 | 436.9
2451 | 2361 | 474.5 | 479.8 | 499.7 | 478.7 | 481 | 479.9 | 477.4 | 476.3 | 456.6 | 436.8
2452 | 2362 | 473.8 | 479.6 | 499.7 | 478.6 | 481 | 479.9 | 477.4 | 476.3 | 456.6 | 436.8
2453 | 2363 | 473 | 479.5 | 499.5 | 478.4 | 480.9 | 479.9 | 477.4 | 476.4 | 456.6 | 436.8
2454 | 2364 | 472.3 | 479.4 | 499.1 | 478.3 | 481.1 | 480 | 477.5 | 476.5 | 456.6 | 436.8
2455 | 2365 | 471.6 | 479.3 | 499 | 478.2 | 481.1 | 480 | 477.5 | 476.5 | 456.6 | 436.7
2456 | 2366 | 470.9 | 479 | 498.9 | 478 | 480.9 | 480 | 477.5 | 476.4 | 456.6 | 436.7
2457 | 2367 | 470.1 | 478.9 | 498.6 | 477.9 | 481.1 | 480 | 477.6 | 476.5 | 456.5 | 436.6
2458 | 2368 | 469.4 | 478.8 | 498.3 | 477.7 | 481.2 | 480.1 | 477.6 | 476.5 | 456.6 | 436.6
2459 | 2369 | 468.7 | 478.6 | 498.2 | 477.6 | 481.1 | 480 | 477.6 | 476.6 | 456.5 | 436.5
2460 | 2370 | 468 | 478.5 | 498 | 477.4 | 481.1 | 480 | 477.7 | 476.6 | 456.5 | 436.5
2461 | 2371 | 467.3 | 478.4 | 497.7 | 477.3 | 481.2 | 480.1 | 477.7 | 476.7 | 456.5 | 436.5
2462 | 2372 | 466.5 | 478.2 | 497.6 | 477.1 | 481.2 | 480.1 | 477.7 | 476.6 | 456.5 | 436.5
2463 | 2373 | 465.9 | 478 | 497.5 | 476.9 | 481 | 480 | 477.7 | 476.6 | 456.5 | 436.5
2464 | 2374 | 465.2 | 477.9 | 497.2 | 476.8 | 481.2 | 480.1 | 477.7 | 476.7 | 456.5 | 436.4
2465 | 2375 | 464.4 | 477.8 | 496.9 | 476.7 | 481.3 | 480.1 | 477.8 | 476.7 | 456.4 | 436.3
2466 | 2376 | 463.7 | 477.6 | 496.8 | 476.5 | 481.1 | 480.1 | 477.8 | 476.7 | 456.4 | 436.3
2467 | 2377 | 463 | 477.4 | 496.6 | 476.3 | 481.1 | 480.1 | 477.8 | 476.7 | 456.4 | 436.3
2468 | 2378 | 462.3 | 477.3 | 496.3 | 476.2 | 481.3 | 480.1 | 477.8 | 476.7 | 456.4 | 436.2
2469 | 2379 | 461.6 | 477.1 | 496.1 | 476 | 481.3 | 480.1 | 477.8 | 476.7 | 456.3 | 436.2
2470 | 2380 | 461 | 476.9 | 496 | 475.8 | 481.1 | 480.1 | 477.9 | 476.8 | 456.3 | 436.2
2471 | 2381 | 460.3 | 476.8 | 495.7 | 475.7 | 481.2 | 480.1 | 477.9 | 476.8 | 456.3 | 436.2
2472 | 2382 | 459.6 | 476.6 | 495.4 | 475.6 | 481.3 | 480.1 | 477.9 | 476.7 | 456.3 | 436.1
2473 | 2383 | 459 | 476.4 | 495.3 | 475.4 | 481.1 | 480.1 | 477.9 | 476.7 | 456.3 | 436.1
2474 | 2384 | 458.3 | 476.2 | 495.1 | 475.2 | 481.1 | 480.1 | 477.9 | 476.7 | 456.3 | 436
2475 | 2385 | 457.7 | 476.1 | 494.8 | 475.1 | 481.3 | 480.1 | 477.9 | 476.7 | 456.2 | 435.9
2476 | 2386 | 457.1 | 475.9 | 494.6 | 474.9 | 481.3 | 480.1 | 477.9 | 476.8 | 456.2 | 435.9
2477 | 2387 | 456.4 | 475.7 | 494.5 | 474.7 | 481.1 | 480.1 | 477.9 | 476.8 | 456.2 | 435.9
2478 | 2388 | 455.8 | 475.6 | 494.1 | 474.6 | 481.2 | 480.1 | 477.9 | 476.7 | 456.2 | 435.9
2479 | 2389 | 455.2 | 475.4 | 493.9 | 474.4 | 481.3 | 480.1 | 477.9 | 476.7 | 456.1 | 435.8
2480 | 2390 | 454.5 | 475.2 | 493.7 | 474.2 | 481.2 | 480.1 | 478 | 476.8 | 456.1 | 435.8
2481 | 2391 | 453.9 | 475 | 493.5 | 474 | 481.1 | 480 | 478 | 476.8 | 456.1 | 435.7
2482 | 2392 | 453.2 | 474.9 | 493.2 | 473.9 | 481.3 | 480.1 | 478 | 476.7 | 456.1 | 435.7
2483 | 2393 | 452.6 | 474.7 | 493 | 473.7 | 481.2 | 480.1 | 478 | 476.8 | 456.1 | 435.6
2484 | 2394 | 451.9 | 474.5 | 492.9 | 473.5 | 481.1 | 480 | 478 | 476.8 | 456.1 | 435.6
2485 | 2395 | 451.3 | 474.4 | 492.5 | 473.4 | 481.2 | 480 | 478 | 476.8 | 456 | 435.6
2486 | 2396 | 450.6 | 474.2 | 492.3 | 473.2 | 481.3 | 480.1 | 478 | 476.8 | 456 | 435.5
2487 | 2397 | 450 | 474 | 492.1 | 473 | 481.1 | 480 | 478 | 476.7 | 456 | 435.5
2488 | 2398 | 449.4 | 473.8 | 491.9 | 472.8 | 481.1 | 480 | 478 | 476.7 | 456 | 435.4
2489 | 2399 | 448.7 | 473.7 | 491.6 | 472.6 | 481.2 | 480 | 478 | 476.6 | 456 | 435.3
2490 | 2400 | 448.1 | 473.5 | 491.3 | 472.5 | 481.2 | 480 | 478 | 476.5 | 456 | 435.2
2491 | 2401 | 447.4 | 473.2 | 491.2 | 472.2 | 481 | 479.9 | 478.1 | 476.5 | 456 | 435.2
2492.1 | 2402.1 | 446.7 | 473.1 | 490.9 | 472.1 | 481.1 | 480 | 478 | 476.5 | 455.9 | 435.1
2493.1 | 2403.1 | 446.1 | 472.9 | 490.6 | 471.9 | 481.2 | 480 | 478 | 476.5 | 455.9 | 435.1
2494.1 | 2404.1 | 445.5 | 472.7 | 490.5 | 471.7 | 481.1 | 479.9 | 478 | 476.5 | 455.8 | 435
2495.1 | 2405.1 | 444.8 | 472.5 | 490.3 | 471.5 | 481 | 479.9 | 478 | 476.6 | 455.8 | 435
2496.1 | 2406.1 | 444.2 | 472.3 | 489.9 | 471.4 | 481.1 | 479.9 | 478 | 476.6 | 455.7 | 434.8
2497.1 | 2407.1 | 443.6 | 472.1 | 489.6 | 471.2 | 481.1 | 479.9 | 478 | 476.5 | 455.7 | 434.8
2498.1 | 2408.1 | 443 | 471.9 | 489.5 | 470.9 | 480.9 | 479.8 | 478 | 476.5 | 455.6 | 434.7
2499.1 | 2409.1 | 442.3 | 471.7 | 489.2 | 470.8 | 481 | 479.8 | 478 | 476.4 | 455.5 | 434.6
2500.1 | 2410.1 | 441.7 | 471.6 | 488.9 | 470.6 | 481 | 479.8 | 477.9 | 476.4 | 455.5 | 434.6
2501.1 | 2411.1 | 441.1 | 471.3 | 488.7 | 470.4 | 480.9 | 479.7 | 477.9 | 476.3 | 455.5 | 434.5
2502.1 | 2412.1 | 440.5 | 471.1 | 488.5 | 470.2 | 480.8 | 479.7 | 477.9 | 476.3 | 455.4 | 434.4
2503.1 | 2413.1 | 439.8 | 471 | 488.1 | 470.1 | 481 | 479.7 | 477.9 | 476.2 | 455.4 | 434.3
2504.1 | 2414.1 | 439.2 | 470.8 | 487.9 | 469.9 | 480.9 | 479.7 | 477.9 | 476.3 | 455.4 | 434.3
2505.1 | 2415.1 | 438.6 | 470.5 | 487.8 | 469.6 | 480.7 | 479.6 | 477.9 | 476.3 | 455.4 | 434.2
2506.1 | 2416.1 | 438 | 470.4 | 487.5 | 469.5 | 480.8 | 479.6 | 477.8 | 476.3 | 455.3 | 434.1
2507.1 | 2417.1 | 437.4 | 470.2 | 487.2 | 469.3 | 480.9 | 479.6 | 477.8 | 476.3 | 455.3 | 434.1
2508.1 | 2418.1 | 436.8 | 469.9 | 487 | 469.1 | 480.7 | 479.5 | 477.8 | 476.3 | 455.3 | 434.1
2509.1 | 2419.1 | 436.2 | 469.7 | 486.8 | 468.8 | 480.6 | 479.5 | 477.8 | 476.2 | 455.2 | 434
2510.1 | 2420.1 | 435.6 | 469.6 | 486.4 | 468.7 | 480.8 | 479.5 | 477.7 | 476.2 | 455.2 | 433.9
2511.1 | 2421.1 | 435 | 469.4 | 486.2 | 468.5 | 480.8 | 479.5 | 477.7 | 476.3 | 455.1 | 433.8
2512.1 | 2422.1 | 434.4 | 469.1 | 486 | 468.3 | 480.6 | 479.4 | 477.7 | 476.3 | 455.1 | 433.7
2513.1 | 2423.1 | 433.8 | 469 | 485.7 | 468.1 | 480.7 | 479.4 | 477.6 | 476.4 | 455 | 433.6
2514.1 | 2424.1 | 433.2 | 468.8 | 485.4 | 467.9 | 480.7 | 479.4 | 477.6 | 476.4 | 454.9 | 433.6
2515.1 | 2425.1 | 432.6 | 468.5 | 485.2 | 467.7 | 480.5 | 479.3 | 477.5 | 476.3 | 454.9 | 433.5
2516.1 | 2426.1 | 432 | 468.3 | 485 | 467.5 | 480.4 | 479.2 | 477.5 | 476.3 | 454.8 | 433.4
2517.1 | 2427.1 | 431.4 | 468.2 | 484.7 | 467.3 | 480.6 | 479.2 | 477.5 | 476.3 | 454.7 | 433.3
2518.1 | 2428.1 | 430.8 | 467.9 | 484.4 | 467.1 | 480.5 | 479.2 | 477.4 | 476.2 | 454.6 | 433.2
2519.1 | 2429.1 | 430.2 | 467.7 | 484.2 | 466.9 | 480.3 | 479.1 | 477.4 | 476.2 | 454.5 | 433.2
2520.1 | 2430.1 | 429.6 | 467.5 | 483.9 | 466.7 | 480.4 | 479.1 | 477.4 | 476.2 | 454.5 | 433.1
2521.1 | 2431.1 | 429.1 | 467.3 | 483.6 | 466.5 | 480.4 | 479 | 477.3 | 476.2 | 454.4 | 433
2522.1 | 2432.1 | 428.5 | 467.1 | 483.4 | 466.3 | 480.3 | 479 | 477.3 | 476.1 | 454.4 | 432.9
2523.1 | 2433.1 | 427.9 | 466.8 | 483.2 | 466 | 480.2 | 478.9 | 477.2 | 476 | 454.3 | 432.8
2524.1 | 2434.1 | 427.4 | 466.7 | 482.8 | 465.9 | 480.3 | 478.9 | 477.2 | 475.9 | 454.2 | 432.7
2525.1 | 2435.1 | 426.8 | 466.5 | 482.6 | 465.7 | 480.2 | 478.9 | 477.2 | 475.9 | 454.2 | 432.5
2526.1 | 2436.1 | 426.2 | 466.2 | 482.4 | 465.4 | 480 | 478.8 | 477.1 | 475.9 | 454.1 | 432.5
2527.1 | 2437.1 | 425.7 | 466 | 482.1 | 465.3 | 480.1 | 478.7 | 477.1 | 475.9 | 454 | 432.4
2528.1 | 2438.1 | 425.1 | 465.8 | 481.8 | 465.1 | 480.1 | 478.7 | 477 | 475.9 | 454 | 432.3
2529.1 | 2439.1 | 424.5 | 465.6 | 481.6 | 464.8 | 480 | 478.6 | 477 | 475.9 | 454 | 432.3
2530.1 | 2440.1 | 424 | 465.3 | 481.4 | 464.6 | 479.8 | 478.6 | 476.9 | 475.9 | 453.9 | 432.2
2531.1 | 2441.1 | 423.4 | 465.2 | 481 | 464.4 | 480 | 478.6 | 476.9 | 475.8 | 453.9 | 432.1
2532.1 | 2442.1 | 422.9 | 465 | 480.7 | 464.2 | 479.9 | 478.5 | 476.8 | 475.8 | 453.8 | 432
2533.1 | 2443.1 | 422.3 | 464.8 | 480.3 | 464 | 480.1 | 478.5 | 476.7 | 475.8 | 453.8 | 431.9
2534.1 | 2444.1 | 421.7 | 465.6 | 478.4 | 464.4 | 482.4 | 479.2 | 476.5 | 475.6 | 453.6 | 431.6
2535.1 | 2445.1 | 421.2 | 465.4 | 478 | 464.2 | 482.4 | 479.2 | 476.4 | 475.6 | 453.6 | 431.5
2536.1 | 2446.1 | 420.6 | 465.1 | 477.9 | 463.9 | 482.2 | 479.1 | 476.4 | 475.6 | 453.5 | 431.4
2537.1 | 2447.1 | 420.1 | 464.8 | 477.8 | 463.7 | 482.1 | 479 | 476.3 | 475.6 | 453.4 | 431.3
2538.1 | 2448.1 | 419.5 | 464.7 | 477.2 | 463.6 | 482.3 | 479.1 | 476.2 | 475.5 | 453.3 | 431.1
2539.1 | 2449.1 | 419 | 464.5 | 477 | 463.3 | 482.2 | 479 | 476.2 | 475.5 | 453.2 | 431
2540.1 | 2450.1 | 418.4 | 464.1 | 477 | 463 | 481.9 | 478.8 | 476.1 | 475.5 | 453.2 | 431
2541.1 | 2451.1 | 417.9 | 464 | 476.5 | 462.9 | 482 | 478.8 | 476 | 475.4 | 453.1 | 430.9
2542.1 | 2452.1 | 417.3 | 463.9 | 476.1 | 462.7 | 482.1 | 478.8 | 476 | 475.3 | 453 | 430.9
2543.1 | 2453.1 | 416.8 | 463.5 | 476.1 | 462.4 | 481.8 | 478.7 | 475.9 | 475.2 | 452.9 | 430.8
2544.1 | 2454.1 | 416.2 | 463.3 | 475.9 | 462.2 | 481.7 | 478.6 | 475.9 | 475.2 | 452.9 | 430.7
2545.1 | 2455.1 | 415.6 | 463.2 | 475.4 | 462.1 | 481.9 | 478.6 | 475.8 | 475 | 452.8 | 430.6
2546.1 | 2456.1 | 415.1 | 463 | 475.1 | 461.9 | 481.8 | 478.6 | 475.7 | 475 | 452.7 | 430.5
2547.1 | 2457.1 | 414.6 | 462.6 | 475.1 | 461.5 | 481.4 | 478.3 | 475.7 | 475 | 452.6 | 430.4
2548.1 | 2458.1 | 414.1 | 462.5 | 474.7 | 461.4 | 481.6 | 478.4 | 475.6 | 474.9 | 452.5 | 430.3
2549.1 | 2459.1 | 413.5 | 462.3 | 474.3 | 461.2 | 481.7 | 478.4 | 475.5 | 474.9 | 452.5 | 430.1
2550.1 | 2460.1 | 413 | 462 | 474.2 | 460.9 | 481.4 | 478.2 | 475.4 | 474.8 | 452.4 | 430.1
2551.1 | 2461.1 | 412.5 | 461.7 | 474 | 460.7 | 481.2 | 478.1 | 475.4 | 474.7 | 452.3 | 430
2552.1 | 2462.1 | 411.9 | 461.6 | 473.4 | 460.5 | 481.4 | 478.1 | 475.3 | 474.7 | 452.2 | 429.8
2553.1 | 2463.1 | 411.4 | 461.4 | 473.2 | 460.3 | 481.3 | 478 | 475.2 | 474.6 | 452.1 | 429.7
2554.1 | 2464.1 | 410.9 | 461 | 473.2 | 460 | 480.9 | 477.8 | 475.1 | 474.6 | 452 | 429.6
2555.1 | 2465.1 | 410.3 | 460.9 | 472.7 | 459.8 | 481.1 | 477.9 | 475 | 474.6 | 451.9 | 429.5
2556.1 | 2466.1 | 409.8 | 460.7 | 472.3 | 459.6 | 481.1 | 477.8 | 474.9 | 474.6 | 451.8 | 429.4
2557.1 | 2467.1 | 409.3 | 460.4 | 472.2 | 459.4 | 480.9 | 477.7 | 474.9 | 474.5 | 451.8 | 429.3
2558.1 | 2468.1 | 408.8 | 460.1 | 472.1 | 459.1 | 480.7 | 477.5 | 474.8 | 474.4 | 451.7 | 429.3
2559.1 | 2469.1 | 408.3 | 460.1 | 471.5 | 459 | 481 | 477.6 | 474.7 | 474.3 | 451.6 | 429.1
2560.1 | 2470.1 | 407.8 | 459.8 | 471.3 | 458.7 | 480.9 | 477.5 | 474.6 | 474.3 | 451.5 | 429.1
2561.1 | 2471.1 | 407.3 | 459.4 | 471.3 | 458.4 | 480.5 | 477.3 | 474.6 | 474.2 | 451.5 | 429
2562.1 | 2472.1 | 406.8 | 459.3 | 470.8 | 458.3 | 480.6 | 477.3 | 474.5 | 474.1 | 451.4 | 428.9
2563.1 | 2473.1 | 406.3 | 459.1 | 470.4 | 458.1 | 480.6 | 477.3 | 474.4 | 474.1 | 451.3 | 428.8
2564.1 | 2474.1 | 405.7 | 458.8 | 470.4 | 457.8 | 480.4 | 477.1 | 474.3 | 474.1 | 451.2 | 428.7
2565.1 | 2475.1 | 405.2 | 458.5 | 470.2 | 457.5 | 480.2 | 477 | 474.2 | 474.1 | 451.1 | 428.6
2566.1 | 2476.1 | 404.7 | 458.4 | 469.6 | 457.4 | 480.4 | 477 | 474.1 | 474 | 451.1 | 428.5
2567.1 | 2477.1 | 404.2 | 458.2 | 469.3 | 457.2 | 480.3 | 477 | 474 | 473.9 | 451 | 428.4
2568.1 | 2478.1 | 403.7 | 457.8 | 469.4 | 456.8 | 479.9 | 476.7 | 474 | 473.8 | 451 | 428.3
2569.1 | 2479.1 | 403.2 | 457.7 | 468.9 | 456.7 | 480 | 476.7 | 473.9 | 473.7 | 450.9 | 428.2
2570.1 | 2480.1 | 402.6 | 457.5 | 468.5 | 456.5 | 480.1 | 476.7 | 473.8 | 473.6 | 450.8 | 428.1
2571.1 | 2481.1 | 402.1 | 457.2 | 468.4 | 456.2 | 479.8 | 476.6 | 473.7 | 473.6 | 450.8 | 428
2572.1 | 2482.1 | 401.6 | 456.9 | 468.3 | 456 | 479.6 | 476.4 | 473.6 | 473.5 | 450.7 | 427.9
2573.1 | 2483.1 | 401.1 | 456.8 | 467.7 | 455.8 | 479.8 | 476.4 | 473.5 | 473.4 | 450.7 | 427.8
2574.1 | 2484.1 | 400.6 | 456.5 | 467.5 | 455.6 | 479.7 | 476.3 | 473.4 | 473.4 | 450.6 | 427.7
2575.1 | 2485.1 | 400.1 | 456.1 | 467.5 | 455.2 | 479.3 | 476.1 | 473.4 | 473.3 | 450.5 | 427.6
2576.1 | 2486.1 | 399.6 | 456 | 467 | 455.1 | 479.5 | 476.2 | 473.2 | 473.2 | 450.4 | 427.4
2577.1 | 2487.1 | 399.1 | 455.9 | 466.6 | 454.9 | 479.5 | 476.1 | 473.1 | 473.2 | 450.3 | 427.3
2578.1 | 2488.1 | 398.6 | 455.6 | 466.5 | 454.6 | 479.3 | 476 | 473.1 | 473.1 | 450.2 | 427.1
2579.1 | 2489.1 | 398.1 | 455.2 | 466.3 | 454.4 | 479 | 475.8 | 473 | 473.1 | 450.1 | 427
2580.1 | 2490.1 | 397.6 | 455.2 | 465.8 | 454.2 | 479.3 | 475.8 | 472.9 | 473 | 450 | 426.8
2581.1 | 2491.1 | 397.1 | 454.9 | 465.5 | 454 | 479.2 | 475.7 | 472.8 | 472.9 | 449.8 | 426.7
2582.1 | 2492.1 | 396.6 | 454.5 | 465.5 | 453.7 | 478.7 | 475.5 | 472.7 | 472.7 | 449.7 | 426.6
2583.1 | 2493.1 | 396.1 | 454.4 | 465.1 | 453.5 | 478.9 | 475.5 | 472.6 | 472.6 | 449.6 | 426.5
2584.1 | 2494.1 | 395.7 | 454.2 | 464.6 | 453.3 | 478.9 | 475.5 | 472.5 | 472.5 | 449.5 | 426.4
2585.1 | 2495.1 | 395.2 | 453.9 | 464.6 | 453 | 478.6 | 475.3 | 472.4 | 472.5 | 449.4 | 426.3
2586.1 | 2496.1 | 394.7 | 453.6 | 464.4 | 452.8 | 478.4 | 475.1 | 472.3 | 472.4 | 449.3 | 426.2
2587.1 | 2497.1 | 394.3 | 453.5 | 463.8 | 452.6 | 478.6 | 475.2 | 472.2 | 472.2 | 449.2 | 426.1
2588.1 | 2498.1 | 393.8 | 453.3 | 463.5 | 452.4 | 478.5 | 475.1 | 472.1 | 472.1 | 449.1 | 425.9
2589.1 | 2499.1 | 393.3 | 452.9 | 463.6 | 452.1 | 478.1 | 474.8 | 472 | 472.1 | 449 | 425.9
2590.1 | 2500.1 | 392.8 | 452.8 | 463.1 | 451.9 | 478.2 | 474.8 | 471.9 | 472 | 448.9 | 425.8
2591.1 | 2501.1 | 392.3 | 452.6 | 462.7 | 451.7 | 478.2 | 474.8 | 471.8 | 471.9 | 448.8 | 425.6
2592.1 | 2502.1 | 391.9 | 452.3 | 462.6 | 451.4 | 478 | 474.6 | 471.7 | 471.7 | 448.7 | 425.5
2593.1 | 2503.1 | 391.4 | 451.9 | 462.5 | 451.1 | 477.7 | 474.4 | 471.6 | 471.7 | 448.6 | 425.4
2594.1 | 2504.1 | 390.9 | 451.9 | 461.9 | 451 | 477.9 | 474.5 | 471.4 | 471.6 | 448.4 | 425.3
2595.1 | 2505.1 | 390.5 | 451.6 | 461.6 | 450.8 | 477.9 | 474.4 | 471.3 | 471.4 | 448.3 | 425.1
2596.1 | 2506.1 | 390 | 451.2 | 461.6 | 450.5 | 477.4 | 474.1 | 471.2 | 471.4 | 448.2 | 425.1
2597.1 | 2507.1 | 389.5 | 451.1 | 461.1 | 450.3 | 477.5 | 474.1 | 471.1 | 471.3 | 448.1 | 424.9
2598.1 | 2508.1 | 389 | 450.9 | 460.8 | 450.1 | 477.5 | 474.1 | 471 | 471.2 | 447.9 | 424.8
2599.1 | 2509.1 | 388.6 | 450.6 | 460.7 | 449.8 | 477.3 | 473.9 | 470.9 | 471.1 | 447.8 | 424.7
2600.1 | 2510.1 | 388.1 | 450.3 | 460.5 | 449.5 | 477.1 | 473.7 | 470.8 | 471 | 447.7 | 424.6
2601.1 | 2511.1 | 387.6 | 450.2 | 459.9 | 449.4 | 477.2 | 473.8 | 470.6 | 471 | 447.5 | 424.4
2602.1 | 2512.1 | 387.1 | 450 | 459.6 | 449.1 | 477.1 | 473.6 | 470.5 | 470.9 | 447.4 | 424.3
2603.1 | 2513.1 | 386.7 | 449.5 | 459.7 | 448.8 | 476.7 | 473.4 | 470.4 | 470.9 | 447.3 | 424.2
2604.1 | 2514.1 | 386.2 | 449.4 | 459.2 | 448.6 | 476.8 | 473.4 | 470.3 | 470.8 | 447.2 | 424
2605.1 | 2515.1 | 385.8 | 449.3 | 458.8 | 448.4 | 476.8 | 473.3 | 470.1 | 470.7 | 447.1 | 423.9
2606.1 | 2516.1 | 385.3 | 448.9 | 458.7 | 448.1 | 476.6 | 473.1 | 470 | 470.6 | 447 | 423.7
2607.1 | 2517.1 | 384.9 | 448.6 | 458.5 | 447.9 | 476.3 | 473 | 469.9 | 470.5 | 446.9 | 423.6
2608.1 | 2518.1 | 384.4 | 448.5 | 457.9 | 447.7 | 476.5 | 473 | 469.8 | 470.3 | 446.7 | 423.4
2609.1 | 2519.1 | 384 | 448.3 | 457.7 | 447.5 | 476.4 | 472.9 | 469.7 | 470.1 | 446.6 | 423.3
2610.1 | 2520.1 | 383.5 | 447.9 | 457.7 | 447.1 | 476 | 472.6 | 469.6 | 470.1 | 446.5 | 423.2
2611.1 | 2521.1 | 383.1 | 447.8 | 457.2 | 447 | 476.1 | 472.6 | 469.4 | 470 | 446.4 | 423.1
2612.1 | 2522.1 | 382.6 | 447.6 | 456.8 | 446.8 | 476.1 | 472.5 | 469.3 | 470 | 446.3 | 422.9
2613.1 | 2523.1 | 382.2 | 447.2 | 456.7 | 446.5 | 475.8 | 472.3 | 469.2 | 469.9 | 446.2 | 422.8
2614.1 | 2524.1 | 381.8 | 446.9 | 456.6 | 446.2 | 475.5 | 472.2 | 469.1 | 469.7 | 446.1 | 422.7
2615.1 | 2525.1 | 381.3 | 446.8 | 456 | 446.1 | 475.7 | 472.2 | 468.9 | 469.5 | 445.9 | 422.5
2616.1 | 2526.1 | 380.8 | 446.6 | 455.8 | 445.8 | 475.6 | 472.1 | 468.8 | 469.4 | 445.8 | 422.3
2617.1 | 2527.1 | 380.4 | 446.2 | 455.8 | 445.5 | 475.2 | 471.8 | 468.7 | 469.4 | 445.7 | 422.2
2618.1 | 2528.1 | 379.9 | 446.1 | 455.3 | 445.3 | 475.3 | 471.8 | 468.6 | 469.3 | 445.6 | 422.1
2619.1 | 2529.1 | 379.4 | 445.9 | 454.9 | 445.1 | 475.2 | 471.7 | 468.4 | 469.2 | 445.4 | 421.9
2620.1 | 2530.1 | 379 | 445.5 | 454.8 | 444.8 | 475 | 471.5 | 468.3 | 469 | 445.3 | 421.8
2621.1 | 2531.1 | 378.5 | 445.2 | 454.6 | 444.6 | 474.7 | 471.3 | 468.2 | 468.9 | 445.2 | 421.7
2622.1 | 2532.1 | 378.1 | 445.2 | 454 | 444.4 | 474.9 | 471.3 | 468 | 468.8 | 445.1 | 421.5
2623.1 | 2533.1 | 377.6 | 444.9 | 453.8 | 444.2 | 474.8 | 471.2 | 467.9 | 468.8 | 445 | 421.4
2624.1 | 2534.1 | 377.2 | 444.5 | 453.9 | 443.8 | 474.3 | 470.9 | 467.8 | 468.7 | 444.9 | 421.3
2625.1 | 2535.1 | 376.7 | 444.4 | 453.4 | 443.7 | 474.4 | 470.9 | 467.6 | 468.5 | 444.8 | 421.1
2626.1 | 2536.1 | 376.3 | 444.2 | 453 | 443.4 | 474.4 | 470.8 | 467.4 | 468.4 | 444.6 | 420.9
2627.1 | 2537.1 | 375.9 | 443.8 | 452.9 | 443.1 | 474.1 | 470.6 | 467.3 | 468.3 | 444.5 | 420.8
2628.1 | 2538.1 | 375.4 | 443.6 | 452.7 | 442.9 | 473.8 | 470.4 | 467.2 | 468.2 | 444.3 | 420.6
2629.1 | 2539.1 | 375 | 443.5 | 452.1 | 442.7 | 474 | 470.4 | 467 | 468 | 444.2 | 420.5
2630.1 | 2540.1 | 374.6 | 443.2 | 451.9 | 442.5 | 473.8 | 470.3 | 466.9 | 467.9 | 444.1 | 420.3
2631.1 | 2541.1 | 374.2 | 442.8 | 451.9 | 442.1 | 473.4 | 470 | 466.8 | 468 | 444 | 420.2
2632.1 | 2542.1 | 373.7 | 442.7 | 451.4 | 441.9 | 473.5 | 470 | 466.6 | 467.9 | 443.8 | 420
2633.1 | 2543.1 | 373.3 | 442.5 | 451 | 441.8 | 473.5 | 469.9 | 466.4 | 467.8 | 443.7 | 419.8
2634.1 | 2544.1 | 372.9 | 442.2 | 450.9 | 441.5 | 473.2 | 469.7 | 466.3 | 467.7 | 443.5 | 419.7
2635.1 | 2545.1 | 372.5 | 441.8 | 450.8 | 441.2 | 472.9 | 469.5 | 466.2 | 467.5 | 443.4 | 419.6
2636.1 | 2546.1 | 372.1 | 441.8 | 450.1 | 441 | 473.1 | 469.5 | 466 | 467.4 | 443.2 | 419.4
2637.1 | 2547.1 | 371.7 | 441.5 | 449.9 | 440.8 | 473 | 469.4 | 465.8 | 467.3 | 443.1 | 419.3
2638.1 | 2548.1 | 371.3 | 441.1 | 449.9 | 440.5 | 472.6 | 469.1 | 465.7 | 467.2 | 443 | 419.2
2639.1 | 2549.1 | 370.9 | 441 | 449.4 | 440.3 | 472.7 | 469.1 | 465.5 | 467.1 | 442.9 | 419
2640.1 | 2550.1 | 370.5 | 440.8 | 449 | 440.1 | 472.6 | 469 | 465.4 | 466.9 | 442.8 | 418.8
2641.1 | 2551.1 | 370.1 | 440.5 | 448.9 | 439.8 | 472.3 | 468.8 | 465.3 | 466.8 | 442.6 | 418.7
2642.1 | 2552.1 | 369.7 | 440.2 | 448.8 | 439.5 | 472.1 | 468.6 | 465.1 | 466.6 | 442.5 | 418.6
2643.1 | 2553.1 | 369.2 | 440.1 | 448.2 | 439.4 | 472.2 | 468.6 | 464.9 | 466.4 | 442.4 | 418.4
2644.1 | 2554.1 | 368.8 | 439.8 | 448 | 439.1 | 472.1 | 468.4 | 464.8 | 466.3 | 442.2 | 418.2
2645.1 | 2555.1 | 368.4 | 439.4 | 448 | 438.8 | 471.7 | 468.2 | 464.7 | 466.3 | 442.1 | 418.1
2646.1 | 2556.1 | 368 | 439.3 | 447.5 | 438.6 | 471.7 | 468.1 | 464.5 | 466.2 | 442 | 418
2647.1 | 2557.1 | 367.6 | 439.1 | 447.1 | 438.4 | 471.7 | 468.1 | 464.3 | 466 | 441.9 | 417.8
2648.1 | 2558.1 | 367.1 | 438.8 | 447 | 438.1 | 471.4 | 467.8 | 464.2 | 465.9 | 441.8 | 417.7
2649.1 | 2559.1 | 366.7 | 438.5 | 446.8 | 437.8 | 471.1 | 467.6 | 464.1 | 465.8 | 441.7 | 417.6
2650.1 | 2560.1 | 366.3 | 438.4 | 446.3 | 437.7 | 471.3 | 467.6 | 463.9 | 465.7 | 441.5 | 417.4
2651.1 | 2561.1 | 365.9 | 438.2 | 446 | 437.4 | 471.2 | 467.5 | 463.8 | 465.5 | 441.4 | 417.2
2652.1 | 2562.1 | 365.4 | 437.7 | 446 | 437.1 | 470.7 | 467.2 | 463.6 | 465.4 | 441.3 | 417.1
2653.1 | 2563.1 | 365 | 437.6 | 445.6 | 436.9 | 470.8 | 467.1 | 463.5 | 465.2 | 441.2 | 416.9
2654.1 | 2564.1 | 364.6 | 437.4 | 445.1 | 436.7 | 470.8 | 467.1 | 463.3 | 465 | 441.1 | 416.8
2655.1 | 2565.1 | 364.1 | 437.1 | 445 | 436.4 | 470.5 | 466.8 | 463.2 | 465 | 440.9 | 416.6
2656.1 | 2566.1 | 363.7 | 436.7 | 444.9 | 436.1 | 470.1 | 466.6 | 463 | 464.9 | 440.8 | 416.5
2657.1 | 2567.1 | 363.3 | 436.7 | 444.4 | 435.9 | 470.3 | 466.6 | 462.8 | 464.8 | 440.6 | 416.3
2658.1 | 2568.1 | 362.9 | 436.4 | 444.1 | 435.7 | 470.2 | 466.5 | 462.7 | 464.6 | 440.5 | 416.2
2659.1 | 2569.1 | 362.5 | 436 | 444.1 | 435.4 | 469.7 | 466.2 | 462.6 | 464.5 | 440.3 | 416
2660.1 | 2570.1 | 362.1 | 435.9 | 443.7 | 435.2 | 469.7 | 466.1 | 462.4 | 464.3 | 440.1 | 415.9
2661.1 | 2571.1 | 361.7 | 435.7 | 443.2 | 435 | 469.8 | 466 | 462.2 | 464.1 | 440 | 415.7
2662.1 | 2572.1 | 361.3 | 435.4 | 443.1 | 434.7 | 469.5 | 465.8 | 462.1 | 463.9 | 439.9 | 415.6
2663.1 | 2573.1 | 360.9 | 435.1 | 443 | 434.4 | 469.2 | 465.6 | 461.9 | 463.8 | 439.7 | 415.4
2664.1 | 2574.1 | 360.5 | 435 | 442.4 | 434.3 | 469.3 | 465.6 | 461.7 | 463.6 | 439.6 | 415.2
2665.1 | 2575.1 | 360.2 | 434.7 | 442.1 | 434 | 469.2 | 465.4 | 461.6 | 463.4 | 439.5 | 415.1
2666.1 | 2576.1 | 359.8 | 434.3 | 442.1 | 433.7 | 468.7 | 465.1 | 461.5 | 463.3 | 439.4 | 415
2667.1 | 2577.1 | 359.4 | 434.2 | 441.7 | 433.5 | 468.8 | 465.1 | 461.3 | 463.2 | 439.3 | 414.8
2668.1 | 2578.1 | 358.9 | 434 | 441.3 | 433.3 | 468.7 | 465 | 461.1 | 463.1 | 439.1 | 414.6
2669.1 | 2579.1 | 358.5 | 433.7 | 441.2 | 433 | 468.5 | 464.7 | 460.9 | 463 | 439 | 414.5
2670.1 | 2580.1 | 358.2 | 433.4 | 441 | 432.7 | 468.2 | 464.5 | 460.8 | 462.8 | 438.9 | 414.4
2671.1 | 2581.1 | 357.8 | 433.3 | 440.5 | 432.6 | 468.3 | 464.5 | 460.6 | 462.7 | 438.7 | 414.2
2672.1 | 2582.1 | 357.4 | 433.1 | 440.2 | 432.4 | 468.1 | 464.4 | 460.4 | 462.6 | 438.6 | 414
2673.1 | 2583.1 | 357 | 432.6 | 440.2 | 432 | 467.7 | 464.1 | 460.3 | 462.5 | 438.5 | 413.9
2674.1 | 2584.1 | 356.6 | 432.5 | 439.7 | 431.8 | 467.7 | 464 | 460.1 | 462.3 | 438.3 | 413.7
2675.1 | 2585.1 | 356.2 | 432.3 | 439.4 | 431.6 | 467.7 | 463.9 | 459.9 | 462.2 | 438.2 | 413.6
2676.1 | 2586.1 | 355.8 | 432 | 439.3 | 431.3 | 467.4 | 463.7 | 459.8 | 462 | 438.1 | 413.4
2677.1 | 2587.1 | 355.4 | 431.6 | 439.2 | 431 | 467 | 463.4 | 459.6 | 461.9 | 437.9 | 413.3
2678.1 | 2588.1 | 355 | 431.6 | 438.5 | 430.9 | 467.2 | 463.4 | 459.4 | 461.8 | 437.8 | 413.1
2679.1 | 2589.1 | 354.7 | 431.4 | 438.3 | 430.7 | 467.1 | 463.3 | 459.3 | 461.6 | 437.6 | 412.9
2680.1 | 2590.1 | 354.3 | 430.9 | 438.3 | 430.3 | 466.6 | 463 | 459.1 | 461.6 | 437.5 | 412.8
2681.1 | 2591.1 | 353.9 | 430.8 | 437.9 | 430.1 | 466.7 | 462.9 | 458.9 | 461.4 | 437.3 | 412.6
2682.1 | 2592.1 | 353.5 | 430.6 | 437.5 | 429.9 | 466.6 | 462.8 | 458.8 | 461.2 | 437.1 | 412.5
2683.1 | 2593.1 | 353.2 | 430.3 | 437.4 | 429.6 | 466.3 | 462.6 | 458.6 | 461.1 | 437 | 412.3
2684.1 | 2594.1 | 352.8 | 430 | 437.3 | 429.4 | 466 | 462.4 | 458.5 | 460.9 | 436.8 | 412.2
2685.1 | 2595.1 | 352.4 | 429.9 | 436.7 | 429.2 | 466.1 | 462.3 | 458.3 | 460.7 | 436.6 | 412
2686.1 | 2596.1 | 352 | 429.7 | 436.4 | 429 | 466 | 462.2 | 458.1 | 460.6 | 436.4 | 411.8
2687.1 | 2597.1 | 351.7 | 429.2 | 436.5 | 428.6 | 465.5 | 461.8 | 458 | 460.5 | 436.3 | 411.7
2688.1 | 2598.1 | 351.3 | 429.1 | 436 | 428.4 | 465.5 | 461.8 | 457.8 | 460.3 | 436.1 | 411.5
2689.1 | 2599.1 | 350.9 | 428.9 | 435.6 | 428.2 | 465.5 | 461.7 | 457.6 | 460.2 | 435.9 | 411.4
2690.1 | 2600.1 | 350.5 | 428.6 | 435.5 | 428 | 465.2 | 461.4 | 457.4 | 460 | 435.7 | 411.2
2691.1 | 2601.1 | 350.1 | 428.3 | 435.4 | 427.7 | 464.9 | 461.2 | 457.3 | 459.7 | 435.6 | 411.1
2692.1 | 2602.1 | 349.8 | 428.2 | 434.8 | 427.5 | 465 | 461.2 | 457.1 | 459.5 | 435.4 | 410.9
2693.1 | 2603.1 | 349.4 | 428 | 434.5 | 427.3 | 464.8 | 461 | 456.9 | 459.3 | 435.3 | 410.7
2694.1 | 2604.1 | 349 | 427.5 | 434.6 | 427 | 464.4 | 460.7 | 456.8 | 459.2 | 435.2 | 410.6
2695.1 | 2605.1 | 348.6 | 427.4 | 434.1 | 426.8 | 464.4 | 460.6 | 456.6 | 459 | 435 | 410.4
2696.1 | 2606.1 | 348.2 | 427.3 | 433.7 | 426.6 | 464.4 | 460.5 | 456.4 | 458.9 | 434.9 | 410.2
2697.1 | 2607.1 | 347.9 | 426.9 | 433.5 | 426.3 | 464.1 | 460.3 | 456.3 | 458.7 | 434.8 | 410.1
2698.1 | 2608.1 | 347.5 | 426.6 | 433.4 | 426 | 463.8 | 460.1 | 456.1 | 458.5 | 434.6 | 410
2699.1 | 2609.1 | 347.1 | 426.5 | 432.8 | 425.9 | 463.9 | 460.1 | 455.9 | 458.3 | 434.5 | 409.7
2700.1 | 2610.1 | 346.7 | 426.3 | 432.6 | 425.6 | 463.7 | 459.9 | 455.8 | 458.1 | 434.3 | 409.6
2701.1 | 2611.1 | 346.4 | 425.9 | 432.6 | 425.3 | 463.3 | 459.6 | 455.6 | 458.1 | 434.1 | 409.5
2702.1 | 2612.1 | 346 | 425.7 | 432.2 | 425.1 | 463.3 | 459.5 | 455.4 | 457.9 | 434 | 409.3
2703.1 | 2613.1 | 345.7 | 425.6 | 431.7 | 424.9 | 463.3 | 459.4 | 455.2 | 457.7 | 433.8 | 409.1
2704.1 | 2614.1 | 345.3 | 425.2 | 431.6 | 424.6 | 463 | 459.2 | 455.1 | 457.6 | 433.7 | 409
2705.1 | 2615.1 | 344.9 | 424.9 | 431.5 | 424.3 | 462.6 | 458.9 | 454.9 | 457.4 | 433.6 | 408.8
2706.1 | 2616.1 | 344.6 | 424.9 | 430.9 | 424.2 | 462.8 | 458.9 | 454.7 | 457.2 | 433.4 | 408.6
2707.1 | 2617.1 | 344.2 | 424.6 | 430.7 | 423.9 | 462.6 | 458.7 | 454.5 | 457 | 433.2 | 408.4
2708.1 | 2618.1 | 343.9 | 424.2 | 430.7 | 423.6 | 462.1 | 458.4 | 454.4 | 456.9 | 433 | 408.3
2709.1 | 2619.1 | 343.5 | 424 | 430.3 | 423.4 | 462.1 | 458.3 | 454.2 | 456.8 | 432.9 | 408.1
2710.1 | 2620.1 | 343.1 | 423.8 | 429.9 | 423.2 | 462.1 | 458.2 | 454 | 456.6 | 432.7 | 408
2711.1 | 2621.1 | 342.8 | 423.5 | 429.8 | 422.9 | 461.8 | 458 | 453.8 | 456.4 | 432.5 | 407.8
2712.1 | 2622.1 | 342.4 | 423.2 | 429.6 | 422.6 | 461.5 | 457.7 | 453.7 | 456.3 | 432.4 | 407.7
2713.1 | 2623.1 | 342 | 423.2 | 429.1 | 422.5 | 461.6 | 457.7 | 453.4 | 456.1 | 432.2 | 407.5
2714.1 | 2624.1 | 341.7 | 422.9 | 428.8 | 422.2 | 461.5 | 457.5 | 453.3 | 455.9 | 432 | 407.3
2715.1 | 2625.1 | 341.3 | 422.5 | 428.9 | 421.9 | 461 | 457.2 | 453.1 | 455.8 | 431.9 | 407.2
2716.1 | 2626.1 | 341 | 422.4 | 428.4 | 421.7 | 461 | 457.1 | 452.9 | 455.7 | 431.7 | 407
2717.1 | 2627.1 | 340.6 | 422.2 | 428 | 421.5 | 461 | 457 | 452.7 | 455.5 | 431.5 | 406.8
2718.1 | 2628.1 | 340.2 | 421.9 | 427.9 | 421.2 | 460.7 | 456.8 | 452.5 | 455.4 | 431.4 | 406.6
2719.1 | 2629.1 | 339.9 | 421.5 | 427.8 | 421 | 460.3 | 456.5 | 452.3 | 455.3 | 431.2 | 406.5
2720.1 | 2630.1 | 339.5 | 421.5 | 427.2 | 420.8 | 460.4 | 456.5 | 452.1 | 455.1 | 431.1 | 406.3
2721.1 | 2631.1 | 339.2 | 421.2 | 426.9 | 420.6 | 460.3 | 456.3 | 451.9 | 454.9 | 430.9 | 406.1
2722.1 | 2632.1 | 338.8 | 420.8 | 427 | 420.2 | 459.8 | 456 | 451.8 | 454.8 | 430.7 | 406
2723.1 | 2633.1 | 338.5 | 420.7 | 426.5 | 420.1 | 459.8 | 455.9 | 451.6 | 454.6 | 430.6 | 405.8
2724.1 | 2634.1 | 338.1 | 420.5 | 426.1 | 419.8 | 459.8 | 455.8 | 451.4 | 454.4 | 430.4 | 405.6
2725.1 | 2635.1 | 337.8 | 420.2 | 426 | 419.6 | 459.4 | 455.6 | 451.2 | 454.3 | 430.3 | 405.5
2726.1 | 2636.1 | 337.4 | 419.9 | 425.9 | 419.3 | 459.1 | 455.3 | 451 | 454.1 | 430.1 | 405.3
2727.1 | 2637.1 | 337.1 | 419.8 | 425.3 | 419.1 | 459.2 | 455.3 | 450.8 | 453.9 | 429.9 | 405.1
2728.1 | 2638.1 | 336.8 | 419.6 | 425.1 | 418.9 | 459 | 455.1 | 450.6 | 453.7 | 429.8 | 404.9
2729.1 | 2639.1 | 336.4 | 419.1 | 425.1 | 418.6 | 458.6 | 454.8 | 450.5 | 453.5 | 429.6 | 404.8
2730.1 | 2640.1 | 336.1 | 419 | 424.7 | 418.4 | 458.6 | 454.7 | 450.2 | 453.3 | 429.5 | 404.6
2731.1 | 2641.1 | 335.7 | 418.8 | 424.3 | 418.2 | 458.5 | 454.6 | 450 | 453.1 | 429.4 | 404.4
2732.1 | 2642.1 | 335.4 | 418.5 | 424.2 | 417.9 | 458.2 | 454.3 | 449.9 | 453 | 429.2 | 404.2
2733.1 | 2643.1 | 335.1 | 418.2 | 424.1 | 417.6 | 457.9 | 454.1 | 449.7 | 452.9 | 429.1 | 404.1
2734.1 | 2644.1 | 334.7 | 418.1 | 423.5 | 417.5 | 458 | 454 | 449.5 | 452.7 | 429 | 403.8
2735.1 | 2645.1 | 334.4 | 417.9 | 423.2 | 417.2 | 457.8 | 453.9 | 449.3 | 452.6 | 428.8 | 403.7
2736.1 | 2646.1 | 334.1 | 417.5 | 423.3 | 416.9 | 457.4 | 453.5 | 449.1 | 452.4 | 428.7 | 403.5
2737.1 | 2647.1 | 333.8 | 417.3 | 422.8 | 416.7 | 457.4 | 453.4 | 448.9 | 452.3 | 428.5 | 403.3
2738.1 | 2648.1 | 333.4 | 417.2 | 422.4 | 416.5 | 457.4 | 453.3 | 448.7 | 452.1 | 428.4 | 403.2
2739.1 | 2649.1 | 333.1 | 416.9 | 422.3 | 416.2 | 457.1 | 453.1 | 448.6 | 451.9 | 428.3 | 403
2740.1 | 2650.1 | 332.7 | 416.5 | 422.2 | 415.9 | 456.7 | 452.8 | 448.4 | 451.7 | 428.1 | 402.8
2741.1 | 2651.1 | 332.4 | 416.5 | 421.6 | 415.8 | 456.8 | 452.8 | 448.2 | 451.5 | 427.9 | 402.6
2742.1 | 2652.1 | 332.1 | 416.2 | 421.4 | 415.5 | 456.7 | 452.6 | 448 | 451.3 | 427.8 | 402.5
2743.1 | 2653.1 | 331.7 | 415.8 | 421.4 | 415.2 | 456.2 | 452.3 | 447.8 | 451.2 | 427.6 | 402.3
2744.1 | 2654.1 | 331.4 | 415.7 | 420.9 | 415 | 456.2 | 452.2 | 447.6 | 451 | 427.5 | 402.1
2745.1 | 2655.1 | 331 | 415.6 | 420.6 | 414.8 | 456.2 | 452.1 | 447.4 | 450.8 | 427.3 | 401.9
2746.1 | 2656.1 | 330.7 | 415.2 | 420.4 | 414.5 | 455.9 | 451.9 | 447.3 | 450.5 | 427.2 | 401.8
2747.1 | 2657.1 | 330.3 | 414.9 | 420.3 | 414.3 | 455.6 | 451.6 | 447.1 | 450.3 | 427 | 401.6
2748.1 | 2658.1 | 330 | 414.8 | 419.7 | 414.1 | 455.7 | 451.6 | 446.9 | 450.2 | 426.9 | 401.4
2749.1 | 2659.1 | 329.7 | 414.6 | 419.5 | 413.9 | 455.5 | 451.4 | 446.7 | 450 | 426.7 | 401.2
2750.1 | 2660.1 | 329.3 | 414.2 | 419.6 | 413.6 | 455 | 451.1 | 446.5 | 449.9 | 426.6 | 401.1
2751.1 | 2661.1 | 329 | 414 | 419.1 | 413.4 | 455.1 | 451 | 446.3 | 449.7 | 426.4 | 400.9
2752.1 | 2662.1 | 328.7 | 413.9 | 418.7 | 413.2 | 455 | 450.8 | 446.1 | 449.5 | 426.3 | 400.7
2753.1 | 2663.1 | 328.4 | 413.6 | 418.6 | 412.9 | 454.7 | 450.6 | 445.9 | 449.4 | 426.1 | 400.5
2754.1 | 2664.1 | 328 | 413.2 | 418.5 | 412.6 | 454.3 | 450.3 | 445.8 | 449.3 | 426 | 400.4
2755.1 | 2665.1 | 327.7 | 413.2 | 418 | 412.5 | 454.5 | 450.3 | 445.6 | 449.2 | 425.8 | 400.2
2756.1 | 2666.1 | 327.4 | 412.9 | 417.7 | 412.3 | 454.3 | 450.1 | 445.4 | 449.1 | 425.7 | 400
2757.1 | 2667.1 | 327.1 | 412.5 | 417.8 | 411.9 | 453.8 | 449.8 | 445.2 | 448.9 | 425.5 | 399.9
2758.1 | 2668.1 | 326.8 | 412.4 | 417.3 | 411.8 | 453.8 | 449.7 | 445 | 448.7 | 425.4 | 399.6
2759.1 | 2669.1 | 326.4 | 412.3 | 416.9 | 411.6 | 453.9 | 449.6 | 444.8 | 448.5 | 425.2 | 399.5
2760.1 | 2670.1 | 326.1 | 411.9 | 416.8 | 411.3 | 453.5 | 449.4 | 444.6 | 448.3 | 425.1 | 399.3
2761.1 | 2671.1 | 325.8 | 411.6 | 416.7 | 411 | 453.2 | 449.1 | 444.4 | 448.2 | 424.9 | 399.2
2762.1 | 2672.1 | 325.5 | 411.6 | 416.1 | 410.9 | 453.3 | 449.1 | 444.2 | 447.9 | 424.7 | 398.9
2763.1 | 2673.1 | 325.2 | 411.3 | 415.9 | 410.6 | 453.1 | 448.9 | 444 | 447.7 | 424.6 | 398.7
2764.1 | 2674.1 | 324.9 | 410.9 | 415.9 | 410.4 | 452.7 | 448.6 | 443.9 | 447.5 | 424.4 | 398.6
2765.1 | 2675.1 | 324.6 | 410.8 | 415.5 | 410.2 | 452.7 | 448.5 | 443.7 | 447.3 | 424.3 | 398.4
2766.1 | 2676.1 | 324.2 | 410.6 | 415.1 | 410 | 452.7 | 448.4 | 443.5 | 447 | 424.1 | 398.2
2767.1 | 2677.1 | 323.9 | 410.3 | 415 | 409.7 | 452.4 | 448.1 | 443.3 | 446.9 | 423.9 | 398.1
2768.1 | 2678.1 | 323.6 | 410 | 414.9 | 409.4 | 452 | 447.9 | 443.1 | 446.7 | 423.8 | 397.9
2769.1 | 2679.1 | 323.3 | 409.9 | 414.3 | 409.3 | 452.1 | 447.8 | 442.9 | 446.6 | 423.6 | 397.7
2770.1 | 2680.1 | 323 | 409.7 | 414.1 | 409 | 451.9 | 447.7 | 442.7 | 446.5 | 423.4 | 397.5
2771.1 | 2681.1 | 322.7 | 409.2 | 414.1 | 408.7 | 451.4 | 447.3 | 442.6 | 446.3 | 423.2 | 397.4
2772.1 | 2682.1 | 322.4 | 409.1 | 413.7 | 408.5 | 451.4 | 447.2 | 442.4 | 446.1 | 423.1 | 397.2
2773.1 | 2683.1 | 322.1 | 409 | 413.3 | 408.3 | 451.4 | 447.1 | 442.2 | 445.9 | 422.9 | 397
2774.1 | 2684.1 | 321.8 | 408.7 | 413.2 | 408.1 | 451.1 | 446.9 | 442 | 445.7 | 422.7 | 396.8
2775.1 | 2685.1 | 321.4 | 408.3 | 413.1 | 407.8 | 450.8 | 446.6 | 441.8 | 445.5 | 422.5 | 396.7
2776.1 | 2686.1 | 321.1 | 408.3 | 412.5 | 407.7 | 450.9 | 446.6 | 441.6 | 445.3 | 422.3 | 396.4
2777.1 | 2687.1 | 320.8 | 408 | 412.3 | 407.4 | 450.7 | 446.4 | 441.4 | 445.1 | 422.1 | 396.3
2778.1 | 2688.1 | 320.5 | 407.6 | 412.3 | 407.1 | 450.2 | 446.1 | 441.3 | 444.9 | 422 | 396.1
2779.1 | 2689.1 | 320.2 | 407.5 | 411.9 | 406.9 | 450.2 | 446 | 441 | 444.7 | 421.8 | 395.9
2780.1 | 2690.1 | 319.9 | 407.4 | 411.4 | 406.7 | 450.2 | 445.9 | 440.8 | 444.6 | 421.6 | 395.7
2781.1 | 2691.1 | 319.6 | 407.1 | 411.4 | 406.5 | 449.8 | 445.6 | 440.7 | 444.5 | 421.4 | 395.6
2782.1 | 2692.1 | 319.3 | 406.7 | 411.3 | 406.2 | 449.5 | 445.3 | 440.5 | 444.4 | 421.2 | 395.4
2783.1 | 2693.1 | 319 | 406.7 | 410.7 | 406 | 449.6 | 445.3 | 440.2 | 444.1 | 421 | 395.2
2784.1 | 2694.1 | 318.6 | 406.4 | 410.5 | 405.8 | 449.4 | 445.1 | 440 | 444 | 420.8 | 395
2785.1 | 2695.1 | 318.3 | 406 | 410.5 | 405.5 | 449 | 444.8 | 439.9 | 443.8 | 420.7 | 394.9
2786.1 | 2696.1 | 318 | 405.9 | 410.1 | 405.3 | 448.9 | 444.7 | 439.7 | 443.5 | 420.5 | 394.7
2787.1 | 2697.1 | 317.7 | 405.8 | 409.7 | 405.1 | 448.9 | 444.5 | 439.5 | 443.3 | 420.3 | 394.5
2788.1 | 2698.1 | 317.4 | 405.4 | 409.6 | 404.8 | 448.6 | 444.3 | 439.3 | 443.2 | 420.1 | 394.3
2789.1 | 2699.1 | 317.1 | 405.1 | 409.5 | 404.5 | 448.2 | 444 | 439.1 | 443 | 420 | 394.2
2790.1 | 2700.1 | 316.8 | 405 | 408.9 | 404.4 | 448.3 | 443.9 | 438.9 | 442.8 | 419.8 | 394
2791.1 | 2701.1 | 316.5 | 404.8 | 408.7 | 404.2 | 448.1 | 443.8 | 438.7 | 442.7 | 419.7 | 393.8
2792.1 | 2702.1 | 316.2 | 404.4 | 408.8 | 403.9 | 447.6 | 443.4 | 438.5 | 442.5 | 419.5 | 393.6
2793.1 | 2703.1 | 315.9 | 404.3 | 408.3 | 403.7 | 447.6 | 443.3 | 438.3 | 442.3 | 419.4 | 393.4
2794.1 | 2704.1 | 315.6 | 404.2 | 407.9 | 403.5 | 447.6 | 443.2 | 438 | 442.1 | 419.2 | 393.2
2795.1 | 2705.1 | 315.3 | 403.8 | 407.8 | 403.2 | 447.3 | 443 | 437.9 | 441.9 | 419.1 | 393.1
2796.1 | 2706.1 | 315.1 | 403.5 | 407.7 | 403 | 447 | 442.7 | 437.7 | 441.7 | 419 | 392.9
2797.1 | 2707.1 | 314.8 | 403.5 | 407.1 | 402.8 | 447.1 | 442.6 | 437.5 | 441.5 | 418.9 | 392.7
2798.1 | 2708.1 | 314.5 | 403.2 | 406.9 | 402.6 | 446.9 | 442.4 | 437.3 | 441.2 | 418.8 | 392.5
2799.1 | 2709.1 | 314.2 | 402.8 | 407 | 402.3 | 446.4 | 442.1 | 437.1 | 441 | 418.7 | 392.4
2800.1 | 2710.1 | 313.9 | 402.7 | 406.6 | 402.1 | 446.4 | 442 | 436.9 | 440.7 | 418.5 | 392.2
2801.1 | 2711.1 | 313.6 | 402.5 | 406.2 | 401.9 | 446.3 | 441.9 | 436.7 | 440.5 | 418.4 | 392
2802.1 | 2712.1 | 313.3 | 402.2 | 406.1 | 401.6 | 446 | 441.6 | 436.5 | 440.3 | 418.3 | 391.8
2803.1 | 2713.1 | 313 | 401.9 | 406.1 | 401.4 | 445.6 | 441.3 | 436.4 | 440.1 | 418.2 | 391.7
2804.1 | 2714.1 | 312.7 | 401.8 | 405.5 | 401.3 | 445.8 | 441.3 | 436.1 | 440 | 418.1 | 391.5
2805.1 | 2715.1 | 312.4 | 401.6 | 405.2 | 401.1 | 445.7 | 441.1 | 436 | 440 | 418 | 391.3
2806.1 | 2716.1 | 312.1 | 401.2 | 405.2 | 400.8 | 445.2 | 440.9 | 435.8 | 439.8 | 418 | 391.1
2807.1 | 2717.1 | 311.8 | 401.1 | 404.8 | 400.6 | 445.2 | 440.8 | 435.6 | 439.6 | 417.9 | 390.9
2808.1 | 2718.1 | 311.6 | 401 | 404.4 | 400.4 | 445.2 | 440.6 | 435.4 | 439.5 | 417.8 | 390.7
2809.1 | 2719.1 | 311.3 | 400.6 | 404.3 | 400.2 | 444.9 | 440.4 | 435.3 | 439.3 | 417.7 | 390.6
2810.1 | 2720.1 | 311 | 400.3 | 404.3 | 399.9 | 444.5 | 440.1 | 435.1 | 439.2 | 417.7 | 390.4
2811.1 | 2721.1 | 310.7 | 400.3 | 403.6 | 399.8 | 444.7 | 440.1 | 434.9 | 439 | 417.6 | 390.2
2812.1 | 2722.1 | 310.4 | 400.1 | 403.4 | 399.6 | 444.5 | 439.9 | 434.7 | 438.8 | 417.5 | 390
2813.1 | 2723.1 | 310.1 | 399.6 | 403.5 | 399.3 | 444.1 | 439.6 | 434.6 | 438.7 | 417.4 | 389.9
2814.1 | 2724.1 | 309.8 | 399.5 | 403.1 | 399.1 | 444.1 | 439.5 | 434.4 | 438.4 | 417.3 | 389.7
2815.1 | 2725.1 | 309.5 | 399.4 | 402.7 | 399 | 444 | 439.4 | 434.2 | 438.2 | 417.2 | 389.5
2816.1 | 2726.1 | 309.2 | 399 | 402.6 | 398.7 | 443.7 | 439.2 | 434.1 | 438 | 417.1 | 389.3
2817.1 | 2727.1 | 308.9 | 398.7 | 402.5 | 398.5 | 443.4 | 438.9 | 433.9 | 437.8 | 417 | 389.2
2818.1 | 2728.1 | 308.6 | 398.7 | 401.9 | 398.4 | 443.5 | 438.9 | 433.7 | 437.5 | 416.8 | 389
2819.1 | 2729.1 | 308.3 | 398.5 | 401.7 | 398.1 | 443.3 | 438.7 | 433.5 | 437.3 | 416.7 | 388.8
2820.1 | 2730.1 | 308 | 398 | 401.8 | 397.8 | 442.9 | 438.4 | 433.4 | 437.2 | 416.6 | 388.7
2821.1 | 2731.1 | 307.7 | 397.9 | 401.4 | 397.7 | 442.9 | 438.3 | 433.2 | 437.1 | 416.5 | 388.5
2822.1 | 2732.1 | 307.4 | 397.8 | 400.9 | 397.5 | 442.9 | 438.2 | 433 | 436.9 | 416.4 | 388.3
2823.1 | 2733.1 | 307.2 | 397.5 | 400.8 | 397.3 | 442.5 | 438 | 432.9 | 436.7 | 416.2 | 388.1
2824.1 | 2734.1 | 306.9 | 397.1 | 400.8 | 397 | 442.2 | 437.7 | 432.7 | 436.4 | 416.1 | 387.9
2825.1 | 2735.1 | 306.6 | 397.1 | 400.2 | 396.9 | 442.3 | 437.7 | 432.5 | 436.2 | 416 | 387.7
2826.1 | 2736.1 | 306.3 | 396.9 | 400 | 396.7 | 442.1 | 437.5 | 432.3 | 436.1 | 415.9 | 387.6
2827.1 | 2737.1 | 306 | 396.5 | 400 | 396.4 | 441.7 | 437.2 | 432.2 | 436 | 415.8 | 387.4
2828.1 | 2738.1 | 305.7 | 396.4 | 399.6 | 396.2 | 441.7 | 437.1 | 432 | 435.8 | 415.7 | 387.2
2829.1 | 2739.1 | 305.4 | 396.2 | 399.2 | 396.1 | 441.6 | 437 | 431.8 | 435.6 | 415.6 | 387
2830.1 | 2740.1 | 305.1 | 395.9 | 399.1 | 395.8 | 441.3 | 436.7 | 431.6 | 435.3 | 415.6 | 386.8
2831.1 | 2741.1 | 304.9 | 395.6 | 399 | 395.6 | 441 | 436.5 | 431.5 | 435.1 | 415.5 | 386.7
2832.1 | 2742.1 | 304.6 | 395.6 | 398.5 | 395.5 | 441.2 | 436.4 | 431.2 | 434.9 | 415.5 | 386.5
2833.1 | 2743.1 | 304.3 | 395.3 | 398.2 | 395.3 | 441 | 436.3 | 431.1 | 434.7 | 415.5 | 386.3
2834.1 | 2744.1 | 304 | 394.9 | 398.3 | 395 | 440.5 | 436 | 430.9 | 434.5 | 415.4 | 386.2
2835.1 | 2745.1 | 303.7 | 394.8 | 397.9 | 394.8 | 440.5 | 435.8 | 430.7 | 434.4 | 415.4 | 386
2836.1 | 2746.1 | 303.4 | 394.7 | 397.5 | 394.7 | 440.5 | 435.7 | 430.5 | 434.2 | 415.3 | 385.8
2837.1 | 2747.1 | 303.1 | 394.4 | 397.4 | 394.5 | 440.2 | 435.5 | 430.4 | 434.1 | 415.3 | 385.6
2838.1 | 2748.1 | 302.9 | 394 | 397.3 | 394.2 | 439.8 | 435.2 | 430.2 | 434 | 415.3 | 385.5
2839.1 | 2749.1 | 302.6 | 394 | 396.7 | 394.1 | 439.9 | 435.2 | 430 | 433.7 | 415.2 | 385.3
2840.1 | 2750.1 | 302.3 | 393.8 | 396.5 | 393.9 | 439.7 | 435 | 429.8 | 433.7 | 415.2 | 385.1
2841.1 | 2751.1 | 302 | 393.3 | 396.6 | 393.6 | 439.3 | 434.7 | 429.7 | 433.6 | 415.2 | 385
2842.1 | 2752.1 | 301.8 | 393.2 | 396.2 | 393.5 | 439.3 | 434.6 | 429.4 | 433.4 | 415.2 | 384.8
2843.1 | 2753.1 | 301.5 | 393.1 | 395.8 | 393.4 | 439.2 | 434.5 | 429.2 | 433.3 | 415.2 | 384.6
2844.1 | 2754.1 | 301.2 | 392.8 | 395.8 | 393.1 | 438.9 | 434.2 | 429.1 | 433.2 | 415.2 | 384.4
2845.1 | 2755.1 | 301 | 392.4 | 395.7 | 392.9 | 438.5 | 433.9 | 428.9 | 433.1 | 415.2 | 384.3
2846.1 | 2756.1 | 300.7 | 392.4 | 395.1 | 392.8 | 438.7 | 433.9 | 428.7 | 432.8 | 415.2 | 384.1
2847.1 | 2757.1 | 300.4 | 392.2 | 394.9 | 392.6 | 438.5 | 433.7 | 428.5 | 432.6 | 415.2 | 383.9
2848.1 | 2758.1 | 300.2 | 391.8 | 394.9 | 392.3 | 438 | 433.4 | 428.3 | 432.5 | 415.2 | 383.7
2849.1 | 2759.1 | 299.9 | 391.7 | 394.5 | 392.2 | 438 | 433.3 | 428.1 | 432.3 | 415.2 | 383.5
2850.1 | 2760.1 | 299.6 | 391.5 | 394.2 | 392.1 | 438 | 433.2 | 427.9 | 432.2 | 415.2 | 383.4
2851.1 | 2761.1 | 299.3 | 391.2 | 394.1 | 391.8 | 437.7 | 433 | 427.7 | 432 | 415.2 | 383.2
2852.1 | 2762.1 | 299.1 | 390.9 | 394 | 391.6 | 437.3 | 432.7 | 427.6 | 431.9 | 415.2 | 383.1
2853.1 | 2763.1 | 298.8 | 390.9 | 393.4 | 391.5 | 437.5 | 432.7 | 427.3 | 431.6 | 415.2 | 382.8
2854.1 | 2764.1 | 298.5 | 390.6 | 393.3 | 391.3 | 437.2 | 432.5 | 427.2 | 431.5 | 415.2 | 382.7
2855.1 | 2765.1 | 298.2 | 390.2 | 393.3 | 391.1 | 436.8 | 432.2 | 427 | 431.3 | 415.2 | 382.5
2856.1 | 2766.1 | 298 | 390.1 | 392.9 | 390.9 | 436.8 | 432.1 | 426.8 | 431.2 | 415.2 | 382.3
2857.1 | 2767.1 | 297.7 | 390 | 392.5 | 390.8 | 436.8 | 432 | 426.6 | 431 | 415.2 | 382.1
2858.1 | 2768.1 | 297.4 | 389.7 | 392.5 | 390.6 | 436.5 | 431.7 | 426.4 | 430.8 | 415.2 | 382
2859.1 | 2769.1 | 297.1 | 389.3 | 392.4 | 390.3 | 436.1 | 431.4 | 426.3 | 430.7 | 415.2 | 381.8
2860.1 | 2770.1 | 296.8 | 389.3 | 391.8 | 390.2 | 436.3 | 431.4 | 426 | 430.4 | 415.2 | 381.6
2861.1 | 2771.1 | 296.5 | 389.1 | 391.6 | 390.1 | 436.1 | 431.2 | 425.9 | 430.3 | 415.2 | 381.5
2862.1 | 2772.1 | 296.2 | 388.7 | 391.7 | 389.8 | 435.6 | 430.9 | 425.7 | 430.2 | 415.2 | 381.3
2863.1 | 2773.1 | 296 | 388.6 | 391.2 | 389.6 | 435.6 | 430.8 | 425.5 | 430 | 415.1 | 381.1
2864.1 | 2774.1 | 295.7 | 388.5 | 390.8 | 389.5 | 435.6 | 430.7 | 425.3 | 429.8 | 415 | 380.9
2865.1 | 2775.1 | 295.4 | 388.2 | 390.7 | 389.3 | 435.3 | 430.5 | 425.1 | 429.7 | 415 | 380.8
2866.1 | 2776.1 | 295.2 | 387.8 | 390.7 | 389 | 434.9 | 430.2 | 425 | 429.5 | 414.9 | 380.6
2867.1 | 2777.1 | 294.9 | 387.8 | 390.2 | 388.9 | 435 | 430.1 | 424.7 | 429.3 | 414.9 | 380.4
2868.1 | 2778.1 | 294.7 | 387.6 | 389.9 | 388.8 | 434.8 | 430 | 424.5 | 429.1 | 414.8 | 380.2
2869.1 | 2779.1 | 294.4 | 387.2 | 390 | 388.5 | 434.4 | 429.6 | 424.4 | 428.9 | 414.8 | 380.1
2870.1 | 2780.1 | 294.1 | 387.1 | 389.6 | 388.4 | 434.4 | 429.5 | 424.2 | 428.8 | 414.8 | 379.9
2871.1 | 2781.1 | 293.9 | 386.9 | 389.2 | 388.2 | 434.3 | 429.4 | 424 | 428.6 | 414.7 | 379.7
2872.1 | 2782.1 | 293.6 | 386.6 | 389.1 | 388 | 434 | 429.2 | 423.8 | 428.4 | 414.7 | 379.5
2873.1 | 2783.1 | 293.3 | 386.3 | 389.1 | 387.7 | 433.7 | 428.9 | 423.6 | 428.2 | 414.7 | 379.4
2874.1 | 2784.1 | 293.1 | 386.3 | 388.5 | 387.7 | 433.8 | 428.9 | 423.4 | 428.1 | 414.6 | 379.2
2875.1 | 2785.1 | 292.8 | 386 | 388.3 | 387.5 | 433.6 | 428.7 | 423.2 | 427.9 | 414.6 | 379
2876.1 | 2786.1 | 292.5 | 385.7 | 388.4 | 387.2 | 433.2 | 428.4 | 423.1 | 427.7 | 414.5 | 378.8
2877.1 | 2787.1 | 292.3 | 385.5 | 388 | 387.1 | 433.1 | 428.3 | 422.8 | 427.5 | 414.4 | 378.7
2878.1 | 2788.1 | 292 | 385.4 | 387.6 | 386.9 | 433.1 | 428.2 | 422.6 | 427.2 | 414.3 | 378.5
2879.1 | 2789.1 | 291.7 | 385.1 | 387.5 | 386.7 | 432.8 | 427.9 | 422.5 | 427 | 414.2 | 378.3
2880.1 | 2790.1 | 291.5 | 384.8 | 387.5 | 386.4 | 432.4 | 427.6 | 422.3 | 426.9 | 414.1 | 378.2
2881.1 | 2791.1 | 291.2 | 384.7 | 386.9 | 386.3 | 432.6 | 427.6 | 422.1 | 426.6 | 414 | 377.9
2882.1 | 2792.1 | 290.9 | 384.5 | 386.7 | 386.2 | 432.4 | 427.4 | 421.9 | 426.5 | 413.9 | 377.8
2883.1 | 2793.1 | 290.7 | 384.1 | 386.8 | 385.9 | 432 | 427.1 | 421.7 | 426.3 | 413.8 | 377.6
2884.1 | 2794.1 | 290.4 | 384 | 386.4 | 385.7 | 431.9 | 427 | 421.5 | 426.1 | 413.7 | 377.4
2885.1 | 2795.1 | 290.2 | 383.9 | 386 | 385.6 | 431.9 | 426.9 | 421.3 | 425.9 | 413.6 | 377.2
2886.1 | 2796.1 | 289.9 | 383.6 | 385.9 | 385.4 | 431.6 | 426.6 | 421.1 | 425.7 | 413.6 | 377.1
2887.1 | 2797.1 | 289.6 | 383.2 | 385.8 | 385.2 | 431.2 | 426.4 | 420.9 | 425.5 | 413.5 | 376.9
2888.1 | 2798.1 | 289.4 | 383.2 | 385.2 | 385.1 | 431.4 | 426.3 | 420.7 | 425.3 | 413.4 | 376.7
2889.1 | 2799.1 | 289.1 | 383 | 385 | 384.9 | 431.2 | 426.2 | 420.5 | 425 | 413.4 | 376.5
2890.1 | 2800.1 | 288.9 | 382.6 | 385.1 | 384.6 | 430.8 | 425.8 | 420.3 | 424.8 | 413.4 | 376.4
2891.1 | 2801.1 | 288.6 | 382.5 | 384.7 | 384.5 | 430.7 | 425.7 | 420.1 | 424.6 | 413.3 | 376.2
2892.1 | 2802.1 | 288.4 | 382.4 | 384.3 | 384.3 | 430.7 | 425.6 | 419.9 | 424.4 | 413.3 | 376
2893.1 | 2803.1 | 288.1 | 382.1 | 384.2 | 384.2 | 430.4 | 425.4 | 419.7 | 424.2 | 413.2 | 375.9
2894.1 | 2804.1 | 287.9 | 381.7 | 384.2 | 383.9 | 430.1 | 425.1 | 419.6 | 424.1 | 413.1 | 375.7
2895.1 | 2805.1 | 287.6 | 381.7 | 383.7 | 383.8 | 430.2 | 425.1 | 419.3 | 423.8 | 413 | 375.5
2896.1 | 2806.1 | 287.4 | 381.5 | 383.4 | 383.6 | 430 | 424.9 | 419.1 | 423.6 | 412.9 | 375.3
2897.1 | 2807.1 | 287.1 | 381.1 | 383.5 | 383.3 | 429.5 | 424.5 | 419 | 423.5 | 412.9 | 375.2
2898.1 | 2808.1 | 286.9 | 381 | 383.1 | 383.2 | 429.5 | 424.4 | 418.8 | 423.3 | 412.7 | 375
2899.1 | 2809.1 | 286.6 | 380.9 | 382.7 | 383 | 429.5 | 424.3 | 418.5 | 423.1 | 412.6 | 374.8
2900.1 | 2810.1 | 286.4 | 380.6 | 382.6 | 382.8 | 429.2 | 424.1 | 418.4 | 422.9 | 412.5 | 374.7
2901.1 | 2811.1 | 286.2 | 380.2 | 382.6 | 382.5 | 428.8 | 423.8 | 418.2 | 422.8 | 412.4 | 374.5
2902.1 | 2812.1 | 285.9 | 380.2 | 382 | 382.5 | 429 | 423.8 | 418 | 422.5 | 412.3 | 374.3
2903.1 | 2813.1 | 285.7 | 380 | 381.8 | 382.3 | 428.8 | 423.6 | 417.8 | 422.3 | 412.1 | 374.1
2904.1 | 2814.1 | 285.4 | 379.6 | 381.8 | 382 | 428.3 | 423.3 | 417.6 | 422.1 | 412 | 374
2905.1 | 2815.1 | 285.2 | 379.5 | 381.4 | 381.8 | 428.3 | 423.1 | 417.4 | 422 | 411.8 | 373.8
2906.1 | 2816.1 | 284.9 | 379.4 | 381 | 381.7 | 428.3 | 423 | 417.2 | 421.9 | 411.6 | 373.6
2907.1 | 2817.1 | 284.7 | 379.1 | 381 | 381.5 | 428 | 422.8 | 417 | 421.8 | 411.4 | 373.4
2908.1 | 2818.1 | 284.4 | 378.7 | 381 | 381.2 | 427.6 | 422.5 | 416.9 | 421.7 | 411.2 | 373.3
2909.1 | 2819.1 | 284.2 | 378.7 | 380.3 | 381.1 | 427.7 | 422.5 | 416.6 | 421.4 | 411 | 373.1
2910.1 | 2820.1 | 284 | 378.5 | 380.1 | 380.9 | 427.6 | 422.3 | 416.4 | 421.2 | 410.7 | 372.9
2911.1 | 2821.1 | 283.7 | 378.1 | 380.2 | 380.6 | 427.1 | 422 | 416.3 | 421.1 | 410.4 | 372.8
2912.1 | 2822.1 | 283.5 | 378 | 379.8 | 380.5 | 427.1 | 421.9 | 416.1 | 420.9 | 410.1 | 372.6
2913.1 | 2823.1 | 283.2 | 377.9 | 379.4 | 380.3 | 427 | 421.7 | 415.8 | 420.7 | 409.8 | 372.4
2914.1 | 2824.1 | 283 | 377.6 | 379.3 | 380.1 | 426.7 | 421.5 | 415.7 | 420.5 | 409.5 | 372.2
2915.1 | 2825.1 | 282.7 | 377.2 | 379.3 | 379.8 | 426.3 | 421.2 | 415.5 | 420.3 | 409.2 | 372.1
2916.1 | 2826.1 | 282.5 | 377.2 | 378.7 | 379.7 | 426.4 | 421.2 | 415.2 | 420.2 | 409 | 371.9
2917.1 | 2827.1 | 282.2 | 377 | 378.5 | 379.5 | 426.2 | 421 | 415 | 419.9 | 408.7 | 371.7
2918.1 | 2828.1 | 282 | 376.6 | 378.6 | 379.2 | 425.8 | 420.6 | 414.9 | 419.8 | 408.5 | 371.5
2919.1 | 2829.1 | 281.7 | 376.5 | 378.2 | 379 | 425.7 | 420.5 | 414.7 | 419.6 | 408.3 | 371.3
2920.1 | 2830.1 | 281.5 | 376.4 | 377.8 | 378.9 | 425.7 | 420.4 | 414.4 | 419.4 | 408.2 | 371.2
2921.1 | 2831.1 | 281.3 | 376.1 | 377.8 | 378.6 | 425.4 | 420.1 | 414.3 | 419.1 | 408 | 371
2922.1 | 2832.1 | 281 | 375.7 | 377.8 | 378.4 | 425 | 419.8 | 414.1 | 418.9 | 407.9 | 370.8
2923.1 | 2833.1 | 280.8 | 375.7 | 377.2 | 378.3 | 425.1 | 419.8 | 413.9 | 418.7 | 407.7 | 370.6
2924.1 | 2834.1 | 280.5 | 375.5 | 377 | 378.1 | 424.9 | 419.6 | 413.7 | 418.6 | 407.5 | 370.5
2925.1 | 2835.1 | 280.3 | 375.1 | 377.1 | 377.8 | 424.4 | 419.3 | 413.5 | 418.3 | 407.4 | 370.3
2926.1 | 2836.1 | 280.1 | 375 | 376.7 | 377.6 | 424.4 | 419.2 | 413.3 | 418.1 | 407.1 | 370.1
2927.1 | 2837.1 | 279.9 | 374.9 | 376.3 | 377.5 | 424.4 | 419.1 | 413.1 | 417.8 | 406.9 | 369.9
2928.1 | 2838.1 | 279.6 | 374.6 | 376.2 | 377.2 | 424.1 | 418.8 | 412.9 | 417.7 | 406.6 | 369.8
2929.1 | 2839.1 | 279.4 | 374.3 | 376.2 | 377 | 423.7 | 418.5 | 412.7 | 417.5 | 406.3 | 369.6
2930.1 | 2840.1 | 279.2 | 374.3 | 375.6 | 376.9 | 423.8 | 418.5 | 412.5 | 417.3 | 406.1 | 369.4
2931.1 | 2841.1 | 278.9 | 374.1 | 375.3 | 376.7 | 423.6 | 418.3 | 412.3 | 417.1 | 405.8 | 369.2
2932.1 | 2842.1 | 278.7 | 373.7 | 375.4 | 376.4 | 423.2 | 418 | 412.1 | 416.9 | 405.5 | 369.1
2933.1 | 2843.1 | 278.4 | 373.5 | 375.1 | 376.2 | 423.1 | 417.8 | 411.9 | 416.7 | 405.3 | 368.9
2934.1 | 2844.1 | 278.2 | 373.4 | 374.7 | 376 | 423 | 417.7 | 411.7 | 416.5 | 405.1 | 368.7
2935.1 | 2845.1 | 277.9 | 373.1 | 374.6 | 375.8 | 422.7 | 417.4 | 411.5 | 416.4 | 404.9 | 368.6
2936.1 | 2846.1 | 277.7 | 372.8 | 374.6 | 375.5 | 422.4 | 417.2 | 411.3 | 416.2 | 404.8 | 368.4
2937.1 | 2847.1 | 277.5 | 372.8 | 374 | 375.4 | 422.5 | 417.1 | 411.1 | 416 | 404.6 | 368.2
2938.1 | 2848.1 | 277.2 | 372.6 | 373.8 | 375.2 | 422.3 | 416.9 | 410.9 | 415.8 | 404.4 | 368
2939.1 | 2849.1 | 277 | 372.2 | 373.9 | 374.9 | 421.8 | 416.6 | 410.7 | 415.7 | 404.3 | 367.9
2940.1 | 2850.1 | 276.8 | 372.1 | 373.4 | 374.8 | 421.8 | 416.5 | 410.5 | 415.4 | 404.1 | 367.7
2941.1 | 2851.1 | 276.5 | 372 | 373.1 | 374.6 | 421.8 | 416.4 | 410.3 | 415.2 | 403.9 | 367.5
2942.1 | 2852.1 | 276.3 | 371.7 | 373 | 374.4 | 421.4 | 416.1 | 410.1 | 415.1 | 403.7 | 367.3
2943.1 | 2853.1 | 276 | 371.3 | 373 | 374.1 | 421.1 | 415.8 | 409.9 | 414.9 | 403.5 | 367.2
2944.1 | 2854.1 | 275.8 | 371.3 | 372.4 | 374 | 421.2 | 415.8 | 409.7 | 414.7 | 403.2 | 367
2945.1 | 2855.1 | 275.6 | 371.1 | 372.2 | 373.8 | 421 | 415.6 | 409.5 | 414.5 | 402.9 | 366.8
2946.1 | 2856.1 | 275.3 | 370.7 | 372.3 | 373.5 | 420.5 | 415.3 | 409.3 | 414.3 | 402.6 | 366.7
2947.1 | 2857.1 | 275.1 | 370.6 | 372 | 373.3 | 420.4 | 415.1 | 409.1 | 414.1 | 402.4 | 366.5
2948.1 | 2858.1 | 274.8 | 370.5 | 371.5 | 373.2 | 420.4 | 415 | 408.9 | 414 | 402.1 | 366.3
2949.1 | 2859.1 | 274.6 | 370.2 | 371.4 | 372.9 | 420.1 | 414.8 | 408.7 | 413.9 | 401.9 | 366.1
2950.1 | 2860.1 | 274.4 | 369.9 | 371.4 | 372.7 | 419.7 | 414.5 | 408.5 | 413.7 | 401.8 | 366
2951.1 | 2861.1 | 274.1 | 369.9 | 370.9 | 372.6 | 419.8 | 414.4 | 408.3 | 413.5 | 401.6 | 365.8
2952.1 | 2862.1 | 273.9 | 369.7 | 370.7 | 372.4 | 419.6 | 414.2 | 408.1 | 413.3 | 401.5 | 365.6
2953.1 | 2863.1 | 273.7 | 369.3 | 370.7 | 372.1 | 419.2 | 413.9 | 407.9 | 413.1 | 401.5 | 365.5
2954.1 | 2864.1 | 273.4 | 369.2 | 370.4 | 371.9 | 419.1 | 413.8 | 407.7 | 412.9 | 401.4 | 365.3
2955.1 | 2865.1 | 273.2 | 369 | 370 | 371.8 | 419.1 | 413.6 | 407.5 | 412.7 | 401.3 | 365.1
2956.1 | 2866.1 | 273 | 368.8 | 369.9 | 371.6 | 418.8 | 413.4 | 407.3 | 412.6 | 401.2 | 364.9
2957.1 | 2867.1 | 272.8 | 368.4 | 369.9 | 371.3 | 418.4 | 413.1 | 407.1 | 412.3 | 401.2 | 364.7
2958.1 | 2868.1 | 272.6 | 368.4 | 369.4 | 371.2 | 418.5 | 413.1 | 406.9 | 412 | 401.2 | 364.5
2959.1 | 2869.1 | 272.3 | 368.2 | 369.2 | 371 | 418.3 | 412.9 | 406.7 | 411.8 | 401.2 | 364.4
2960.1 | 2870.1 | 272.1 | 367.9 | 369.2 | 370.8 | 417.8 | 412.6 | 406.6 | 411.7 | 401.2 | 364.2
2961.1 | 2871.1 | 271.9 | 367.7 | 368.8 | 370.6 | 417.8 | 412.4 | 406.4 | 411.4 | 401.3 | 364
2962.1 | 2872.1 | 271.6 | 367.6 | 368.5 | 370.5 | 417.8 | 412.3 | 406.1 | 411.2 | 401.4 | 363.9
2963.1 | 2873.1 | 271.4 | 367.3 | 368.4 | 370.2 | 417.4 | 412.1 | 406 | 411.1 | 401.5 | 363.7
2964.1 | 2874.1 | 271.2 | 367 | 368.4 | 370 | 417.1 | 411.8 | 405.8 | 410.9 | 401.6 | 363.5
2965.1 | 2875.1 | 271 | 367 | 367.9 | 370 | 417.2 | 411.7 | 405.5 | 410.7 | 401.7 | 363.3
2966.1 | 2876.1 | 270.8 | 366.8 | 367.6 | 369.8 | 417 | 411.6 | 405.3 | 410.6 | 401.8 | 363.2
2967.1 | 2877.1 | 270.5 | 366.4 | 367.7 | 369.5 | 416.6 | 411.3 | 405.2 | 410.4 | 401.9 | 363
2968.1 | 2878.1 | 270.3 | 366.3 | 367.4 | 369.4 | 416.5 | 411.1 | 405 | 410.2 | 401.9 | 362.8
2969.1 | 2879.1 | 270.1 | 366.2 | 367 | 369.3 | 416.5 | 411 | 404.8 | 410 | 401.9 | 362.6
2970.1 | 2880.1 | 269.9 | 365.9 | 366.9 | 369 | 416.2 | 410.8 | 404.6 | 409.8 | 402 | 362.5
2971.1 | 2881.1 | 269.7 | 365.6 | 366.9 | 368.8 | 415.8 | 410.5 | 404.4 | 409.8 | 402 | 362.3
2972.1 | 2882.1 | 269.4 | 365.6 | 366.4 | 368.7 | 415.9 | 410.5 | 404.2 | 409.6 | 402.1 | 362.1
2973.1 | 2883.1 | 269.2 | 365.3 | 366.2 | 368.5 | 415.8 | 410.3 | 404 | 409.5 | 402.1 | 361.9
2974.1 | 2884.1 | 269 | 365 | 366.3 | 368.3 | 415.3 | 410 | 403.8 | 409.2 | 402.1 | 361.8
2975.1 | 2885.1 | 268.7 | 364.9 | 365.9 | 368.2 | 415.3 | 409.8 | 403.6 | 409.1 | 402.2 | 361.6
2976.1 | 2886.1 | 268.5 | 364.7 | 365.6 | 368 | 415.2 | 409.7 | 403.4 | 408.9 | 402.2 | 361.4
2977.1 | 2887.1 | 268.3 | 364.5 | 365.5 | 367.8 | 414.9 | 409.5 | 403.2 | 408.6 | 402.2 | 361.3
2978.1 | 2888.1 | 268 | 364.1 | 365.5 | 367.6 | 414.6 | 409.2 | 403 | 408.4 | 402.2 | 361.1
2979.1 | 2889.1 | 267.8 | 364.1 | 365 | 367.5 | 414.7 | 409.2 | 402.8 | 408.1 | 402.1 | 360.9
2980.1 | 2890.1 | 267.6 | 363.9 | 364.7 | 367.3 | 414.6 | 409 | 402.6 | 407.9 | 402 | 360.8
2981.1 | 2891.1 | 267.3 | 363.6 | 364.8 | 367 | 414.1 | 408.7 | 402.4 | 407.7 | 402 | 360.6
2982.1 | 2892.1 | 267.1 | 363.4 | 364.5 | 366.9 | 414.1 | 408.6 | 402.2 | 407.6 | 401.9 | 360.4
2983.1 | 2893.1 | 266.9 | 363.3 | 364.1 | 366.8 | 414.1 | 408.5 | 402 | 407.4 | 401.9 | 360.2
2984.1 | 2894.1 | 266.6 | 363 | 364.1 | 366.5 | 413.7 | 408.2 | 401.8 | 407.2 | 401.8 | 360.1
2985.1 | 2895.1 | 266.4 | 363.2 | 363.2 | 366.5 | 414.2 | 408.3 | 401.6 | 407 | 401.7 | 359.8
2986.1 | 2896.1 | 266.2 | 363 | 363 | 366.4 | 414 | 408.1 | 401.4 | 406.8 | 401.7 | 359.7

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 37 |  |  | 2006-08-30 | 8:32
38959.3547 | 1 | 0 | 1 | XLPE & PE | 7-C | Conduit
38959.3552 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38959.3557 | 1 | 0 | 1
38959.3562 | 1 | 0 | 1
38959.3566 | 1 | 0 | 1
38959.3571 | 1 | 0 | 1
38959.3576 | 1 | 0 | 1
38959.3581 | 1 | 0 | 1
38959.3586 | 1 | 0 | 1
38959.3591 | 1 | 0 | 1
38959.3596 | 1 | 0 | 1
38959.36 | 1 | 0 | 1
38959.3605 | 1 | 0 | 1
38959.361 | 1 | 0 | 1
38959.3615 | 1 | 0 | 1
38959.362 | 1 | 0 | 1
38959.3625 | 1 | 0 | 1
38959.363 | 1 | 0 | 1
38959.3634 | 1 | 0 | 1
38959.3639 | 1 | 0 | 1
38959.3644 | 1 | 0 | 1
38959.3649 | 1 | 0 | 1
38959.3654 | 1 | 0 | 1
38959.3659 | 1 | 0 | 1
38959.3664 | 1 | 0 | 1
38959.3669 | 1 | 0 | 1
38959.3673 | 1 | 0 | 1
38959.3678 | 1 | 0 | 1
38959.3683 | 1 | 0 | 1
38959.3688 | 1 | 0 | 1
38959.3693 | 1 | 0 | 1
38959.3698 | 1 | 0 | 1
38959.3703 | 1 | 0 | 1
38959.3707 | 1 | 0 | 1
38959.3712 | 1 | 0 | 1
38959.3717 | 1 | 0 | 1
38959.3722 | 1 | 0 | 1
38959.3727 | 1 | 0 | 1
38959.3732 | 1 | 0 | 1
38959.3737 | 2 | 0 | 1
38959.3741 | 13 | 8 | 1
38959.3746 | 85 | 69 | 1
38959.3751 | 1093 | 927 | 1
38959.3756 | 938 | 949 | 1
38959.3761 | 1031 | 1048 | 1
38959.3766 | 992 | 938 | 1
38959.3771 | 1098 | 1042 | 1
38959.3775 | 987 | 997 | 1
38959.378 | 983 | 929 | 1
38959.3785 | 1219 | 1156 | 1
38959.379 | 964 | 898 | 1
38959.3795 | 961 | 893 | 1
38959.38 | 1036 | 947 | 1
38959.3805 | 1870 | 39 | 1
38959.3809 | 2351 | 3 | 1
38959.3814 | 2378 | 2 | 1
38959.3819 | 2128 | 1 | 1
38959.3824 | 2031 | 0 | 1
38959.3829 | 1988 | 1 | 1
38959.3834 | 2010 | 0 | 1
38959.3839 | 2016 | 1 | 1
38959.3843 | 2011 | 1 | 1
38959.3848 | 2419 | 1 | 1
38959.3853 | 2454 | 0 | 1
38959.3858 | 2322 | 0 | 1
38959.3863 | 2145 | 0 | 1
38959.3868 | 2210 | 0 | 1
38959.3873 | 2295 | 1 | 1
38959.3877 | 1935 | 0 | 1
38959.3882 | 1991 | 0 | 1
38959.3887 | 2113 | 0 | 1
1
38959.3547 | 1 | 0 | 2
38959.3552 | 1 | 0 | 2
38959.3557 | 1 | 0 | 2
38959.3562 | 0 | 0 | 2
38959.3567 | 1 | 0 | 2
38959.3571 | 1 | 0 | 2
38959.3576 | 1 | 0 | 2
38959.3581 | 1 | 0 | 2
38959.3586 | 1 | 0 | 2
38959.3591 | 1 | 0 | 2
38959.3596 | 1 | 0 | 2
38959.3601 | 1 | 0 | 2
38959.3605 | 1 | 0 | 2
38959.361 | 1 | 0 | 2
38959.3615 | 1 | 0 | 2
38959.362 | 1 | 0 | 2
38959.3625 | 1 | 0 | 2
38959.363 | 1 | 0 | 2
38959.3635 | 1 | 0 | 2
38959.3639 | 1 | 0 | 2
38959.3644 | 1 | 0 | 2
38959.3649 | 1 | 0 | 2
38959.3654 | 1 | 0 | 2
38959.3659 | 1 | 0 | 2
38959.3664 | 1 | 0 | 2
38959.3669 | 1 | 0 | 2
38959.3673 | 1 | 0 | 2
38959.3678 | 1 | 0 | 2
38959.3683 | 1 | 0 | 2
38959.3688 | 1 | 0 | 2
38959.3693 | 1 | 0 | 2
38959.3698 | 1 | 0 | 2
38959.3703 | 1 | 0 | 2
38959.3708 | 1 | 0 | 2
38959.3712 | 1 | 0 | 2
38959.3717 | 1 | 0 | 2
38959.3722 | 1 | 0 | 2
38959.3727 | 1 | 0 | 2
38959.3732 | 2 | 0 | 2
38959.3737 | 2 | 1 | 2
38959.3742 | 13 | 9 | 2
38959.3746 | 116 | 98 | 2
38959.3751 | 1060 | 1087 | 2
38959.3756 | 1118 | 1159 | 2
38959.3761 | 1189 | 1135 | 2
38959.3766 | 1207 | 1177 | 2
38959.3771 | 1176 | 1174 | 2
38959.3776 | 948 | 921 | 2
38959.378 | 1200 | 1142 | 2
38959.3785 | 1128 | 1149 | 2
38959.379 | 1109 | 1131 | 2
38959.3795 | 953 | 938 | 2
38959.38 | 976 | 892 | 2
38959.3805 | 2196 | 25 | 2
38959.381 | 2226 | 2 | 2
38959.3814 | 2246 | 1 | 2
38959.3819 | 1952 | 1 | 2
38959.3824 | 2469 | 1 | 2
38959.3829 | 2086 | 1 | 2
38959.3834 | 2451 | 0 | 2
38959.3839 | 2012 | 1 | 2
38959.3844 | 2369 | 1 | 2
38959.3848 | 1983 | 1 | 2
38959.3853 | 2111 | 0 | 2
38959.3858 | 2322 | 1 | 2
38959.3863 | 2001 | 0 | 2
38959.3868 | 2487 | 0 | 2
38959.3873 | 1926 | 0 | 2
38959.3878 | 2460 | 1 | 2
38959.3883 | 1978 | 0 | 2
38959.3887 | 2298 | 1 | 2
2
38959.3547 | 1 | 0 | 3
38959.3552 | 1 | 0 | 3
38959.3557 | 1 | 0 | 3
38959.3562 | 1 | 0 | 3
38959.3567 | 1 | 0 | 3
38959.3572 | 1 | 0 | 3
38959.3577 | 1 | 0 | 3
38959.3581 | 1 | 0 | 3
38959.3586 | 1 | 0 | 3
38959.3591 | 1 | 0 | 3
38959.3596 | 1 | 0 | 3
38959.3601 | 1 | 0 | 3
38959.3606 | 1 | 0 | 3
38959.3611 | 1 | 0 | 3
38959.3615 | 1 | 0 | 3
38959.362 | 1 | 0 | 3
38959.3625 | 1 | 0 | 3
38959.363 | 1 | 0 | 3
38959.3635 | 1 | 0 | 3
38959.364 | 1 | 0 | 3
38959.3644 | 1 | 0 | 3
38959.3649 | 1 | 0 | 3
38959.3654 | 1 | 0 | 3
38959.3659 | 1 | 0 | 3
38959.3664 | 1 | 0 | 3
38959.3669 | 1 | 0 | 3
38959.3674 | 1 | 0 | 3
38959.3678 | 1 | 0 | 3
38959.3683 | 1 | 0 | 3
38959.3688 | 1 | 0 | 3
38959.3693 | 1 | 0 | 3
38959.3698 | 1 | 0 | 3
38959.3703 | 1 | 0 | 3
38959.3708 | 1 | 0 | 3
38959.3712 | 1 | 0 | 3
38959.3717 | 1 | 0 | 3
38959.3722 | 1 | 0 | 3
38959.3727 | 1 | 0 | 3
38959.3732 | 1 | 0 | 3
38959.3737 | 1 | 0 | 3
38959.3742 | 1 | 0 | 3
38959.3747 | 1 | 0 | 3
38959.3751 | 2 | 2 | 3
38959.3756 | 2 | 2 | 3
38959.3761 | 2 | 1 | 3
38959.3766 | 2 | 2 | 3
38959.3771 | 2 | 2 | 3
38959.3776 | 2 | 2 | 3
38959.3781 | 2 | 2 | 3
38959.3785 | 3 | 2 | 3
38959.379 | 3 | 2 | 3
38959.3795 | 5 | 1 | 3
38959.38 | 12 | 1 | 3
38959.3805 | 1886 | 0 | 3
38959.381 | 2013 | 0 | 3
38959.3815 | 2060 | 0 | 3
38959.3819 | 2204 | 0 | 3
38959.3824 | 2341 | 0 | 3
38959.3829 | 2359 | 0 | 3
38959.3834 | 1992 | 0 | 3
38959.3839 | 2168 | 0 | 3
38959.3844 | 2114 | 0 | 3
38959.3849 | 2105 | 0 | 3
38959.3853 | 2097 | 0 | 3
38959.3858 | 2278 | 0 | 3
38959.3863 | 2188 | 0 | 3
38959.3868 | 2246 | 0 | 3
38959.3873 | 2062 | 0 | 3
38959.3878 | 2351 | 0 | 3
38959.3883 | 2168 | 0 | 3
38959.3887 | 1920 | 0 | 3
3
38959.3547 | 1 | 0 | 4
38959.3552 | 1 | 0 | 4
38959.3557 | 1 | 0 | 4
38959.3562 | 1 | 0 | 4
38959.3567 | 1 | 1 | 4
38959.3572 | 1 | 0 | 4
38959.3577 | 1 | 0 | 4
38959.3581 | 1 | 0 | 4
38959.3586 | 1 | 0 | 4
38959.3591 | 1 | 0 | 4
38959.3596 | 1 | 0 | 4
38959.3601 | 1 | 0 | 4
38959.3606 | 1 | 0 | 4
38959.3611 | 1 | 0 | 4
38959.3616 | 1 | 0 | 4
38959.362 | 1 | 0 | 4
38959.3625 | 1 | 0 | 4
38959.363 | 1 | 0 | 4
38959.3635 | 1 | 0 | 4
38959.364 | 1 | 0 | 4
38959.3645 | 1 | 0 | 4
38959.365 | 1 | 0 | 4
38959.3654 | 1 | 0 | 4
38959.3659 | 1 | 0 | 4
38959.3664 | 1 | 0 | 4
38959.3669 | 1 | 0 | 4
38959.3674 | 1 | 0 | 4
38959.3679 | 1 | 0 | 4
38959.3684 | 1 | 0 | 4
38959.3688 | 1 | 0 | 4
38959.3693 | 1 | 0 | 4
38959.3698 | 1 | 0 | 4
38959.3703 | 1 | 0 | 4
38959.3708 | 1 | 0 | 4
38959.3713 | 1 | 0 | 4
38959.3718 | 44 | 0 | 4
38959.3722 | 369 | 0 | 4
38959.3727 | 2 | 0 | 4
38959.3732 | 31 | 0 | 4
38959.3737 | 1 | 0 | 4
38959.3742 | 816 | 0 | 4
38959.3747 | 395 | 0 | 4
38959.3752 | 2040 | 1 | 4
38959.3756 | 2029 | 1 | 4
38959.3761 | 1979 | 1 | 4
38959.3766 | 2321 | 1 | 4
38959.3771 | 2399 | 1 | 4
38959.3776 | 2316 | 1 | 4
38959.3781 | 2045 | 0 | 4
38959.3786 | 2391 | 1 | 4
38959.3791 | 2406 | 1 | 4
38959.3795 | 1976 | 1 | 4
38959.38 | 2068 | 1 | 4
38959.3805 | 1906 | 0 | 4
38959.381 | 1974 | 0 | 4
38959.3815 | 2311 | 0 | 4
38959.382 | 2407 | 0 | 4
38959.3825 | 2469 | 0 | 4
38959.3829 | 2389 | 0 | 4
38959.3834 | 2159 | 0 | 4
38959.3839 | 1923 | 0 | 4
38959.3844 | 2268 | 0 | 4
38959.3849 | 2008 | 0 | 4
38959.3854 | 2464 | 0 | 4
38959.3859 | 2385 | 0 | 4
38959.3863 | 1955 | 0 | 4
38959.3868 | 2459 | 0 | 4
38959.3873 | 1958 | 0 | 4
38959.3878 | 2020 | 0 | 4
38959.3883 | 2417 | 0 | 4
38959.3888 | 2366 | 0 | 4
4
38959.3548 | 1 | 0 | 5
38959.3552 | 1 | 0 | 5
38959.3557 | 1 | 0 | 5
38959.3562 | 1 | 0 | 5
38959.3567 | 1 | 0 | 5
38959.3572 | 1 | 0 | 5
38959.3577 | 1 | 0 | 5
38959.3582 | 1 | 0 | 5
38959.3586 | 1 | 0 | 5
38959.3591 | 1 | 0 | 5
38959.3596 | 1 | 1 | 5
38959.3601 | 1 | 0 | 5
38959.3606 | 1 | 0 | 5
38959.3611 | 1 | 0 | 5
38959.3616 | 1 | 0 | 5
38959.362 | 1 | 0 | 5
38959.3625 | 1 | 0 | 5
38959.363 | 1 | 0 | 5
38959.3635 | 1 | 0 | 5
38959.364 | 1 | 0 | 5
38959.3645 | 1 | 0 | 5
38959.365 | 1 | 0 | 5
38959.3655 | 1 | 0 | 5
38959.3659 | 1 | 0 | 5
38959.3664 | 1 | 0 | 5
38959.3669 | 1 | 0 | 5
38959.3674 | 1 | 0 | 5
38959.3679 | 1 | 0 | 5
38959.3684 | 1 | 0 | 5
38959.3689 | 1 | 0 | 5
38959.3693 | 1 | 0 | 5
38959.3698 | 1 | 0 | 5
38959.3703 | 1 | 0 | 5
38959.3708 | 1 | 0 | 5
38959.3713 | 1 | 0 | 5
38959.3718 | 1 | 0 | 5
38959.3723 | 1 | 0 | 5
38959.3727 | 1 | 0 | 5
38959.3732 | 1 | 0 | 5
38959.3737 | 1 | 0 | 5
38959.3742 | 1 | 0 | 5
38959.3747 | 2 | 0 | 5
38959.3752 | 2 | 0 | 5
38959.3757 | 2 | 0 | 5
38959.3761 | 3 | 0 | 5
38959.3766 | 2 | 0 | 5
38959.3771 | 2 | 0 | 5
38959.3776 | 2 | 0 | 5
38959.3781 | 2 | 0 | 5
38959.3786 | 3 | 0 | 5
38959.3791 | 4 | 0 | 5
38959.3795 | 5 | 0 | 5
38959.38 | 15 | 0 | 5
38959.3805 | 2017 | 0 | 5
38959.381 | 2380 | 0 | 5
38959.3815 | 2049 | 0 | 5
38959.382 | 2025 | 0 | 5
38959.3825 | 2313 | 0 | 5
38959.383 | 2470 | 0 | 5
38959.3834 | 2096 | 0 | 5
38959.3839 | 2275 | 0 | 5
38959.3844 | 2090 | 0 | 5
38959.3849 | 1926 | 0 | 5
38959.3854 | 1945 | 0 | 5
38959.3859 | 2309 | 0 | 5
38959.3864 | 2224 | 0 | 5
38959.3868 | 2032 | 0 | 5
38959.3873 | 2288 | 0 | 5
38959.3878 | 2130 | 0 | 5
38959.3883 | 2178 | 0 | 5
38959.3888 | 2176 | 0 | 5
5
38959.3548 | 1 | 0 | 6
38959.3553 | 1 | 0 | 6
38959.3558 | 1 | 0 | 6
38959.3562 | 1 | 1 | 6
38959.3567 | 1 | 0 | 6
38959.3572 | 1 | 0 | 6
38959.3577 | 1 | 0 | 6
38959.3582 | 1 | 0 | 6
38959.3587 | 1 | 0 | 6
38959.3592 | 1 | 0 | 6
38959.3596 | 1 | 0 | 6
38959.3601 | 1 | 0 | 6
38959.3606 | 1 | 0 | 6
38959.3611 | 1 | 0 | 6
38959.3616 | 1 | 0 | 6
38959.3621 | 1 | 0 | 6
38959.3626 | 1 | 0 | 6
38959.363 | 1 | 0 | 6
38959.3635 | 1 | 0 | 6
38959.364 | 1 | 0 | 6
38959.3645 | 1 | 0 | 6
38959.365 | 1 | 0 | 6
38959.3655 | 1 | 0 | 6
38959.366 | 1 | 0 | 6
38959.3664 | 1 | 0 | 6
38959.3669 | 1 | 0 | 6
38959.3674 | 1 | 0 | 6
38959.3679 | 1 | 0 | 6
38959.3684 | 1 | 0 | 6
38959.3689 | 1 | 0 | 6
38959.3694 | 1 | 0 | 6
38959.3698 | 1 | 0 | 6
38959.3703 | 1 | 0 | 6
38959.3708 | 1 | 0 | 6
38959.3713 | 1 | 0 | 6
38959.3718 | 1 | 0 | 6
38959.3723 | 1 | 0 | 6
38959.3728 | 1 | 0 | 6
38959.3733 | 1 | 0 | 6
38959.3737 | 398 | 0 | 6
38959.3742 | 1921 | 0 | 6
38959.3747 | 2343 | 0 | 6
38959.3752 | 2289 | 0 | 6
38959.3757 | 2369 | 0 | 6
38959.3762 | 1966 | 0 | 6
38959.3767 | 2110 | 0 | 6
38959.3771 | 2491 | 0 | 6
38959.3776 | 1978 | 0 | 6
38959.3781 | 1987 | 0 | 6
38959.3786 | 2194 | 0 | 6
38959.3791 | 1982 | 0 | 6
38959.3796 | 2003 | 0 | 6
38959.38 | 2481 | 0 | 6
38959.3805 | 2181 | 0 | 6
38959.381 | 2385 | 0 | 6
38959.3815 | 1943 | 0 | 6
38959.382 | 2018 | 0 | 6
38959.3825 | 2510 | 0 | 6
38959.383 | 2220 | 0 | 6
38959.3834 | 2169 | 0 | 6
38959.3839 | 2446 | 0 | 6
38959.3844 | 2356 | 0 | 6
38959.3849 | 2418 | 0 | 6
38959.3854 | 2096 | 0 | 6
38959.3859 | 2513 | 0 | 6
38959.3864 | 2318 | 0 | 6
38959.3869 | 1980 | 0 | 6
38959.3873 | 2034 | 0 | 6
38959.3878 | 2452 | 0 | 6
38959.3883 | 2428 | 0 | 6
38959.3888 | 2262 | 0 | 6
6
38959.3548 | 1 | 0 | 7
38959.3553 | 1 | 0 | 7
38959.3558 | 1 | 1 | 7
38959.3562 | 0 | 0 | 7
38959.3567 | 1 | 1 | 7
38959.3572 | 1 | 0 | 7
38959.3577 | 1 | 0 | 7
38959.3582 | 1 | 0 | 7
38959.3587 | 1 | 0 | 7
38959.3592 | 1 | 0 | 7
38959.3597 | 1 | 0 | 7
38959.3601 | 1 | 0 | 7
38959.3606 | 1 | 0 | 7
38959.3611 | 1 | 0 | 7
38959.3616 | 1 | 0 | 7
38959.3621 | 1 | 0 | 7
38959.3626 | 1 | 0 | 7
38959.3631 | 1 | 0 | 7
38959.3635 | 1 | 0 | 7
38959.364 | 1 | 0 | 7
38959.3645 | 1 | 0 | 7
38959.365 | 1 | 0 | 7
38959.3655 | 1 | 0 | 7
38959.366 | 1 | 0 | 7
38959.3665 | 1 | 0 | 7
38959.3669 | 1 | 0 | 7
38959.3674 | 1 | 0 | 7
38959.3679 | 1 | 0 | 7
38959.3684 | 1 | 0 | 7
38959.3689 | 1 | 0 | 7
38959.3694 | 1 | 0 | 7
38959.3699 | 1 | 0 | 7
38959.3703 | 1 | 0 | 7
38959.3708 | 1 | 0 | 7
38959.3713 | 1 | 0 | 7
38959.3718 | 1 | 0 | 7
38959.3723 | 1 | 0 | 7
38959.3728 | 1 | 0 | 7
38959.3733 | 1 | 0 | 7
38959.3737 | 1 | 0 | 7
38959.3742 | 2 | 0 | 7
38959.3747 | 2 | 0 | 7
38959.3752 | 2 | 0 | 7
38959.3757 | 2 | 0 | 7
38959.3762 | 2 | 0 | 7
38959.3767 | 2 | 0 | 7
38959.3772 | 2 | 0 | 7
38959.3776 | 3 | 0 | 7
38959.3781 | 2 | 0 | 7
38959.3786 | 3 | 0 | 7
38959.3791 | 4 | 0 | 7
38959.3796 | 6 | 0 | 7
38959.3801 | 17 | 0 | 7
38959.3806 | 2368 | 0 | 7
38959.381 | 2445 | 0 | 7
38959.3815 | 2177 | 0 | 7
38959.382 | 2417 | 0 | 7
38959.3825 | 2095 | 0 | 7
38959.383 | 2348 | 0 | 7
38959.3835 | 2370 | 0 | 7
38959.384 | 2318 | 0 | 7
38959.3844 | 2159 | 0 | 7
38959.3849 | 2470 | 0 | 7
38959.3854 | 1996 | 0 | 7
38959.3859 | 2433 | 0 | 7
38959.3864 | 2210 | 0 | 7
38959.3869 | 2218 | 0 | 7
38959.3874 | 2233 | 0 | 7
38959.3878 | 2142 | 0 | 7
38959.3883 | 2434 | 0 | 7
38959.3888 | 1921 | 0 | 7
7
38959.3548 | 1 | 0 | 8
38959.3553 | 1 | 0 | 8
38959.3558 | 1 | 0 | 8
38959.3563 | 1 | 0 | 8
38959.3568 | 1 | 0 | 8
38959.3572 | 1 | 0 | 8
38959.3577 | 1 | 0 | 8
38959.3582 | 1 | 0 | 8
38959.3587 | 1 | 0 | 8
38959.3592 | 1 | 0 | 8
38959.3597 | 1 | 0 | 8
38959.3602 | 1 | 0 | 8
38959.3606 | 1 | 0 | 8
38959.3611 | 1 | 0 | 8
38959.3616 | 1 | 0 | 8
38959.3621 | 1 | 0 | 8
38959.3626 | 1 | 0 | 8
38959.3631 | 1 | 0 | 8
38959.3636 | 1 | 0 | 8
38959.3641 | 1 | 0 | 8
38959.3645 | 1 | 0 | 8
38959.365 | 1 | 0 | 8
38959.3655 | 1 | 0 | 8
38959.366 | 1 | 0 | 8
38959.3665 | 1 | 0 | 8
38959.367 | 1 | 0 | 8
38959.3674 | 1 | 0 | 8
38959.3679 | 1 | 0 | 8
38959.3684 | 1 | 0 | 8
38959.3689 | 1 | 0 | 8
38959.3694 | 1 | 0 | 8
38959.3699 | 1 | 0 | 8
38959.3704 | 1 | 0 | 8
38959.3708 | 1 | 0 | 8
38959.3713 | 1 | 0 | 8
38959.3718 | 1 | 0 | 8
38959.3723 | 1 | 0 | 8
38959.3728 | 1 | 0 | 8
38959.3733 | 1 | 0 | 8
38959.3738 | 1 | 0 | 8
38959.3742 | 1 | 0 | 8
38959.3747 | 2 | 0 | 8
38959.3752 | 2 | 0 | 8
38959.3757 | 243 | 0 | 8
38959.3762 | 2 | 0 | 8
38959.3767 | 2 | 0 | 8
38959.3772 | 5 | 0 | 8
38959.3777 | 2 | 1 | 8
38959.3781 | 12 | 0 | 8
38959.3786 | 34 | 0 | 8
38959.3791 | 442 | 0 | 8
38959.3796 | 67 | 0 | 8
38959.3801 | 93 | 0 | 8
38959.3806 | 15 | 0 | 8
38959.3811 | 1446 | 0 | 8
38959.3815 | 159 | 0 | 8
38959.382 | 1661 | 0 | 8
38959.3825 | 3 | 0 | 8
38959.383 | 1015 | 0 | 8
38959.3835 | 4 | 0 | 8
38959.384 | 4 | 0 | 8
38959.3845 | 3 | 0 | 8
38959.3849 | 4 | 0 | 8
38959.3854 | 3 | 0 | 8
38959.3859 | 2 | 0 | 8
38959.3864 | 3 | 0 | 8
38959.3869 | 2 | 0 | 8
38959.3874 | 2 | 0 | 8
38959.3879 | 2 | 0 | 8
38959.3883 | 2 | 0 | 8
38959.3888 | 2 | 0 | 8
8
38959.3548 | 1 | 0 | 9
38959.3553 | 1 | 0 | 9
38959.3558 | 1 | 0 | 9
38959.3563 | 1 | 0 | 9
38959.3568 | 1 | 0 | 9
38959.3573 | 1 | 0 | 9
38959.3577 | 1 | 0 | 9
38959.3582 | 1 | 0 | 9
38959.3587 | 1 | 0 | 9
38959.3592 | 1 | 0 | 9
38959.3597 | 1 | 0 | 9
38959.3602 | 1 | 0 | 9
38959.3607 | 1 | 0 | 9
38959.3611 | 1 | 0 | 9
38959.3616 | 1 | 0 | 9
38959.3621 | 1 | 0 | 9
38959.3626 | 1 | 0 | 9
38959.3631 | 1 | 0 | 9
38959.3636 | 1 | 0 | 9
38959.3641 | 1 | 0 | 9
38959.3645 | 1 | 0 | 9
38959.365 | 1 | 0 | 9
38959.3655 | 1 | 0 | 9
38959.366 | 1 | 0 | 9
38959.3665 | 1 | 0 | 9
38959.367 | 1 | 0 | 9
38959.3675 | 1 | 0 | 9
38959.368 | 1 | 0 | 9
38959.3684 | 1 | 0 | 9
38959.3689 | 1 | 0 | 9
38959.3694 | 2 | 0 | 9
38959.3699 | 1 | 0 | 9
38959.3704 | 1 | 0 | 9
38959.3709 | 1 | 0 | 9
38959.3714 | 1 | 0 | 9
38959.3718 | 1 | 0 | 9
38959.3723 | 1 | 0 | 9
38959.3728 | 1 | 0 | 9
38959.3733 | 1 | 0 | 9
38959.3738 | 1 | 0 | 9
38959.3743 | 1 | 0 | 9
38959.3748 | 1 | 0 | 9
38959.3752 | 2 | 0 | 9
38959.3757 | 2 | 0 | 9
38959.3762 | 2 | 0 | 9
38959.3767 | 2 | 0 | 9
38959.3772 | 2 | 0 | 9
38959.3777 | 2 | 0 | 9
38959.3782 | 2 | 0 | 9
38959.3786 | 2 | 0 | 9
38959.3791 | 4 | 0 | 9
38959.3796 | 5 | 0 | 9
38959.3801 | 16 | 0 | 9
38959.3806 | 2427 | 0 | 9
38959.3811 | 2130 | 0 | 9
38959.3816 | 1987 | 0 | 9
38959.382 | 2383 | 0 | 9
38959.3825 | 2467 | 0 | 9
38959.383 | 2045 | 0 | 9
38959.3835 | 2466 | 0 | 9
38959.384 | 1952 | 0 | 9
38959.3845 | 1918 | 0 | 9
38959.385 | 2005 | 0 | 9
38959.3855 | 2032 | 0 | 9
38959.3859 | 2385 | 0 | 9
38959.3864 | 2181 | 0 | 9
38959.3869 | 2091 | 0 | 9
38959.3874 | 2260 | 0 | 9
38959.3879 | 2049 | 0 | 9
38959.3884 | 2208 | 0 | 9
38959.3889 | 2323 | 0 | 9
9
38959.3548 | 1 | 0 | 10
38959.3553 | 1 | 0 | 10
38959.3558 | 1 | 0 | 10
38959.3563 | 1 | 0 | 10
38959.3568 | 1 | 0 | 10
38959.3573 | 1 | 0 | 10
38959.3578 | 1 | 0 | 10
38959.3582 | 1 | 1 | 10
38959.3587 | 1 | 0 | 10
38959.3592 | 0 | 0 | 10
38959.3597 | 1 | 0 | 10
38959.3602 | 1 | 0 | 10
38959.3607 | 1 | 0 | 10
38959.3612 | 1 | 0 | 10
38959.3616 | 1 | 0 | 10
38959.3621 | 1 | 0 | 10
38959.3626 | 1 | 0 | 10
38959.3631 | 1 | 0 | 10
38959.3636 | 1 | 0 | 10
38959.3641 | 1 | 0 | 10
38959.3646 | 1 | 0 | 10
38959.365 | 1 | 0 | 10
38959.3655 | 1 | 0 | 10
38959.366 | 1 | 0 | 10
38959.3665 | 1 | 0 | 10
38959.367 | 1 | 0 | 10
38959.3675 | 1 | 0 | 10
38959.368 | 1 | 0 | 10
38959.3684 | 1 | 0 | 10
38959.3689 | 1 | 0 | 10
38959.3694 | 1 | 0 | 10
38959.3699 | 1 | 0 | 10
38959.3704 | 1 | 0 | 10
38959.3709 | 1 | 0 | 10
38959.3714 | 1 | 0 | 10
38959.3719 | 1 | 0 | 10
38959.3723 | 1 | 0 | 10
38959.3728 | 1 | 0 | 10
38959.3733 | 1 | 0 | 10
38959.3738 | 1 | 0 | 10
38959.3743 | 1 | 0 | 10
38959.3748 | 2 | 0 | 10
38959.3753 | 1 | 0 | 10
38959.3757 | 2 | 0 | 10
38959.3762 | 2 | 0 | 10
38959.3767 | 2 | 0 | 10
38959.3772 | 2 | 0 | 10
38959.3777 | 2 | 0 | 10
38959.3782 | 71 | 0 | 10
38959.3787 | 41 | 0 | 10
38959.3791 | 487 | 0 | 10
38959.3796 | 1510 | 0 | 10
38959.3801 | 2094 | 0 | 10
38959.3806 | 1932 | 0 | 10
38959.3811 | 2376 | 0 | 10
38959.3816 | 2419 | 0 | 10
38959.3821 | 2112 | 0 | 10
38959.3825 | 2006 | 0 | 10
38959.383 | 2083 | 0 | 10
38959.3835 | 2040 | 0 | 10
38959.384 | 2327 | 0 | 10
38959.3845 | 2124 | 0 | 10
38959.385 | 2297 | 0 | 10
38959.3855 | 1952 | 0 | 10
38959.3859 | 2214 | 0 | 10
38959.3864 | 2213 | 0 | 10
38959.3869 | 2389 | 0 | 10
38959.3874 | 2060 | 0 | 10
38959.3879 | 1947 | 0 | 10
38959.3884 | 2464 | 0 | 10
38959.3889 | 2106 | 0 | 10
10
38959.3549 | 1 | 0 | 11
38959.3553 | 1 | 0 | 11
38959.3558 | 1 | 0 | 11
38959.3563 | 1 | 0 | 11
38959.3568 | 1 | 0 | 11
38959.3573 | 1 | 0 | 11
38959.3578 | 1 | 0 | 11
38959.3583 | 1 | 0 | 11
38959.3587 | 1 | 0 | 11
38959.3592 | 2 | 0 | 11
38959.3597 | 1 | 0 | 11
38959.3602 | 1 | 1 | 11
38959.3607 | 1 | 0 | 11
38959.3612 | 1 | 0 | 11
38959.3617 | 1 | 0 | 11
38959.3622 | 1 | 0 | 11
38959.3626 | 1 | 0 | 11
38959.3631 | 1 | 0 | 11
38959.3636 | 1 | 0 | 11
38959.3641 | 1 | 0 | 11
38959.3646 | 1 | 0 | 11
38959.3651 | 1 | 0 | 11
38959.3656 | 1 | 0 | 11
38959.366 | 1 | 0 | 11
38959.3665 | 1 | 0 | 11
38959.367 | 1 | 0 | 11
38959.3675 | 1 | 0 | 11
38959.368 | 1 | 0 | 11
38959.3685 | 1 | 0 | 11
38959.369 | 1 | 0 | 11
38959.3694 | 1 | 0 | 11
38959.3699 | 1 | 0 | 11
38959.3704 | 1 | 0 | 11
38959.3709 | 1 | 0 | 11
38959.3714 | 1 | 0 | 11
38959.3719 | 1 | 0 | 11
38959.3724 | 1 | 0 | 11
38959.3728 | 1 | 0 | 11
38959.3733 | 1 | 0 | 11
38959.3738 | 1 | 0 | 11
38959.3743 | 1 | 0 | 11
38959.3748 | 1 | 0 | 11
38959.3753 | 2 | 0 | 11
38959.3758 | 2 | 0 | 11
38959.3763 | 2 | 0 | 11
38959.3767 | 2 | 0 | 11
38959.3772 | 2 | 0 | 11
38959.3777 | 2 | 0 | 11
38959.3782 | 2 | 0 | 11
38959.3787 | 3 | 0 | 11
38959.3792 | 4 | 0 | 11
38959.3797 | 7 | 0 | 11
38959.3801 | 19 | 0 | 11
38959.3806 | 2020 | 0 | 11
38959.3811 | 2017 | 0 | 11
38959.3816 | 2338 | 0 | 11
38959.3821 | 1948 | 0 | 11
38959.3826 | 2039 | 0 | 11
38959.383 | 2073 | 0 | 11
38959.3835 | 2225 | 0 | 11
38959.384 | 1925 | 0 | 11
38959.3845 | 1922 | 0 | 11
38959.385 | 1920 | 0 | 11
38959.3855 | 2183 | 0 | 11
38959.386 | 2005 | 0 | 11
38959.3864 | 2460 | 0 | 11
38959.3869 | 2181 | 0 | 11
38959.3874 | 1936 | 0 | 11
38959.3879 | 2065 | 0 | 11
38959.3884 | 1939 | 0 | 11
38959.3889 | 2263 | 0 | 11
11
38959.3549 | 1 | 0 | 12
38959.3554 | 1 | 0 | 12
38959.3558 | 1 | 0 | 12
38959.3563 | 1 | 0 | 12
38959.3568 | 1 | 0 | 12
38959.3573 | 1 | 0 | 12
38959.3578 | 1 | 0 | 12
38959.3583 | 1 | 0 | 12
38959.3588 | 1 | 0 | 12
38959.3592 | 1 | 0 | 12
38959.3597 | 1 | 0 | 12
38959.3602 | 1 | 0 | 12
38959.3607 | 1 | 0 | 12
38959.3612 | 1 | 0 | 12
38959.3617 | 1 | 0 | 12
38959.3622 | 1 | 0 | 12
38959.3627 | 1 | 0 | 12
38959.3631 | 1 | 0 | 12
38959.3636 | 1 | 0 | 12
38959.3641 | 1 | 0 | 12
38959.3646 | 1 | 0 | 12
38959.3651 | 1 | 0 | 12
38959.3656 | 1 | 0 | 12
38959.3661 | 1 | 0 | 12
38959.3665 | 1 | 0 | 12
38959.367 | 1 | 1 | 12
38959.3675 | 1 | 0 | 12
38959.368 | 1 | 0 | 12
38959.3685 | 1 | 0 | 12
38959.369 | 1 | 0 | 12
38959.3695 | 1 | 0 | 12
38959.3699 | 1 | 0 | 12
38959.3704 | 1 | 0 | 12
38959.3709 | 1 | 0 | 12
38959.3714 | 1 | 0 | 12
38959.3719 | 5 | 0 | 12
38959.3724 | 99 | 0 | 12
38959.3729 | 105 | 0 | 12
38959.3733 | 2 | 0 | 12
38959.3738 | 670 | 0 | 12
38959.3743 | 1302 | 0 | 12
38959.3748 | 1076 | 0 | 12
38959.3753 | 2042 | 0 | 12
38959.3758 | 1873 | 0 | 12
38959.3763 | 2091 | 0 | 12
38959.3767 | 2265 | 0 | 12
38959.3772 | 2404 | 0 | 12
38959.3777 | 2218 | 0 | 12
38959.3782 | 2409 | 0 | 12
38959.3787 | 2324 | 0 | 12
38959.3792 | 2118 | 0 | 12
38959.3797 | 2275 | 0 | 12
38959.3802 | 2440 | 0 | 12
38959.3806 | 2311 | 0 | 12
38959.3811 | 1910 | 0 | 12
38959.3816 | 2342 | 0 | 12
38959.3821 | 2326 | 0 | 12
38959.3826 | 2094 | 0 | 12
38959.3831 | 2400 | 0 | 12
38959.3836 | 2312 | 0 | 12
38959.384 | 2053 | 0 | 12
38959.3845 | 1931 | 0 | 12
38959.385 | 2226 | 0 | 12
38959.3855 | 2450 | 0 | 12
38959.386 | 2478 | 0 | 12
38959.3865 | 2415 | 0 | 12
38959.387 | 2099 | 0 | 12
38959.3874 | 2474 | 0 | 12
38959.3879 | 2477 | 0 | 12
38959.3884 | 2303 | 0 | 12
38959.3889 | 2469 | 0 | 12
12
38959.3549 | 1 | 0 | 13
38959.3554 | 1 | 0 | 13
38959.3559 | 1 | 0 | 13
38959.3564 | 1 | 0 | 13
38959.3568 | 1 | 0 | 13
38959.3573 | 1 | 0 | 13
38959.3578 | 1 | 0 | 13
38959.3583 | 1 | 0 | 13
38959.3588 | 1 | 0 | 13
38959.3593 | 1 | 0 | 13
38959.3598 | 1 | 0 | 13
38959.3602 | 1 | 0 | 13
38959.3607 | 1 | 0 | 13
38959.3612 | 1 | 0 | 13
38959.3617 | 1 | 0 | 13
38959.3622 | 1 | 0 | 13
38959.3627 | 1 | 0 | 13
38959.3631 | 1 | 0 | 13
38959.3636 | 1 | 0 | 13
38959.3641 | 1 | 0 | 13
38959.3646 | 1 | 0 | 13
38959.3651 | 1 | 0 | 13
38959.3656 | 1 | 0 | 13
38959.3661 | 1 | 0 | 13
38959.3666 | 1 | 0 | 13
38959.367 | 1 | 0 | 13
38959.3675 | 1 | 0 | 13
38959.368 | 1 | 0 | 13
38959.3685 | 1 | 0 | 13
38959.369 | 1 | 0 | 13
38959.3695 | 1 | 0 | 13
38959.37 | 1 | 0 | 13
38959.3704 | 1 | 0 | 13
38959.3709 | 1 | 0 | 13
38959.3714 | 1 | 0 | 13
38959.3719 | 1 | 0 | 13
38959.3724 | 1 | 0 | 13
38959.3729 | 1 | 0 | 13
38959.3734 | 1 | 0 | 13
38959.3738 | 1 | 0 | 13
38959.3743 | 1 | 0 | 13
38959.3748 | 2 | 0 | 13
38959.3758 | 2 | 0 | 13
38959.3763 | 3 | 0 | 13
38959.3768 | 2 | 0 | 13
38959.3772 | 2 | 0 | 13
38959.3777 | 2 | 0 | 13
38959.3782 | 3 | 0 | 13
38959.3787 | 3 | 0 | 13
38959.3792 | 5 | 0 | 13
38959.3797 | 6 | 0 | 13
38959.3802 | 292 | 0 | 13
38959.3806 | 2274 | 0 | 13
38959.3811 | 2348 | 0 | 13
38959.3816 | 2290 | 0 | 13
38959.3821 | 2331 | 0 | 13
38959.3826 | 2238 | 0 | 13
38959.3831 | 2030 | 0 | 13
38959.3836 | 2118 | 0 | 13
38959.3841 | 2277 | 0 | 13
38959.3845 | 2060 | 0 | 13
38959.385 | 2379 | 0 | 13
38959.3855 | 2167 | 0 | 13
38959.386 | 2144 | 0 | 13
38959.3865 | 1966 | 0 | 13
38959.387 | 1983 | 0 | 13
38959.3875 | 2394 | 0 | 13
38959.3879 | 2438 | 0 | 13
38959.3884 | 2437 | 0 | 13
38959.3889 | 2201 | 0 | 13
13
38959.3549 | 1 | 0 | 14
38959.3554 | 1 | 0 | 14
38959.3559 | 0 | 0 | 14
38959.3564 | 1 | 0 | 14
38959.3569 | 1 | 0 | 14
38959.3573 | 1 | 0 | 14
38959.3578 | 1 | 0 | 14
38959.3583 | 1 | 0 | 14
38959.3588 | 1 | 0 | 14
38959.3593 | 1 | 0 | 14
38959.3598 | 1 | 0 | 14
38959.3603 | 1 | 0 | 14
38959.3607 | 1 | 0 | 14
38959.3612 | 1 | 0 | 14
38959.3617 | 1 | 0 | 14
38959.3622 | 1 | 0 | 14
38959.3627 | 1 | 0 | 14
38959.3632 | 1 | 0 | 14
38959.3637 | 1 | 0 | 14
38959.3641 | 1 | 0 | 14
38959.3646 | 1 | 0 | 14
38959.3651 | 1 | 0 | 14
38959.3656 | 1 | 0 | 14
38959.3661 | 1 | 0 | 14
38959.3666 | 1 | 0 | 14
38959.3671 | 1 | 0 | 14
38959.3675 | 1 | 0 | 14
38959.368 | 1 | 0 | 14
38959.3685 | 1 | 0 | 14
38959.369 | 1 | 0 | 14
38959.3695 | 1 | 0 | 14
38959.37 | 1 | 0 | 14
38959.3705 | 1 | 0 | 14
38959.3709 | 1 | 0 | 14
38959.3714 | 1 | 0 | 14
38959.3719 | 1 | 0 | 14
38959.3724 | 1 | 0 | 14
38959.3729 | 1 | 0 | 14
38959.3734 | 1 | 0 | 14
38959.3739 | 1 | 0 | 14
38959.3744 | 1 | 0 | 14
38959.3748 | 1 | 0 | 14
38959.3753 | 2 | 0 | 14
38959.3758 | 2 | 0 | 14
38959.3763 | 2 | 0 | 14
38959.3768 | 1 | 0 | 14
38959.3773 | 2 | 0 | 14
38959.3778 | 2 | 0 | 14
38959.3782 | 2 | 0 | 14
38959.3787 | 3 | 0 | 14
38959.3792 | 5 | 0 | 14
38959.3797 | 8 | 1 | 14
38959.3802 | 1135 | 0 | 14
38959.3807 | 2354 | 0 | 14
38959.3812 | 2166 | 0 | 14
38959.3816 | 2363 | 0 | 14
38959.3821 | 2120 | 0 | 14
38959.3826 | 2446 | 0 | 14
38959.3831 | 2013 | 0 | 14
38959.3836 | 2315 | 0 | 14
38959.3841 | 2319 | 0 | 14
38959.3846 | 2404 | 0 | 14
38959.385 | 2422 | 0 | 14
38959.3855 | 2485 | 0 | 14
38959.386 | 2348 | 0 | 14
38959.3865 | 1953 | 0 | 14
38959.387 | 2224 | 0 | 14
38959.3875 | 2067 | 0 | 14
38959.388 | 2164 | 0 | 14
38959.3884 | 1928 | 0 | 14
38959.3889 | 2124 | 0 | 14
14
38959.3549 | 1 | 0 | 15
38959.3554 | 1 | 0 | 15
38959.3559 | 1 | 0 | 15
38959.3564 | 1 | 0 | 15
38959.3569 | 1 | 0 | 15
38959.3573 | 1 | 1 | 15
38959.3578 | 1 | 0 | 15
38959.3583 | 1 | 0 | 15
38959.3588 | 1 | 0 | 15
38959.3593 | 1 | 0 | 15
38959.3598 | 1 | 0 | 15
38959.3603 | 1 | 0 | 15
38959.3608 | 1 | 0 | 15
38959.3612 | 1 | 0 | 15
38959.3617 | 1 | 0 | 15
38959.3622 | 1 | 0 | 15
38959.3627 | 1 | 0 | 15
38959.3632 | 1 | 0 | 15
38959.3637 | 1 | 0 | 15
38959.3642 | 1 | 0 | 15
38959.3646 | 1 | 0 | 15
38959.3651 | 1 | 0 | 15
38959.3656 | 1 | 0 | 15
38959.3661 | 1 | 0 | 15
38959.3666 | 1 | 0 | 15
38959.3671 | 1 | 0 | 15
38959.3676 | 1 | 0 | 15
38959.368 | 1 | 0 | 15
38959.3685 | 1 | 0 | 15
38959.369 | 1 | 0 | 15
38959.3695 | 1 | 0 | 15
38959.37 | 1 | 0 | 15
38959.3705 | 1 | 0 | 15
38959.371 | 1 | 0 | 15
38959.3714 | 1 | 0 | 15
38959.3719 | 1 | 0 | 15
38959.3724 | 1 | 0 | 15
38959.3729 | 1 | 0 | 15
38959.3734 | 1 | 0 | 15
38959.3739 | 1 | 0 | 15
38959.3744 | 1 | 0 | 15
38959.3748 | 1 | 0 | 15
38959.3753 | 1 | 0 | 15
38959.3758 | 2 | 0 | 15
38959.3763 | 1 | 0 | 15
38959.3768 | 2 | 0 | 15
38959.3773 | 2 | 0 | 15
38959.3778 | 1 | 0 | 15
38959.3783 | 2 | 0 | 15
38959.3787 | 3 | 0 | 15
38959.3792 | 5 | 0 | 15
38959.3797 | 8 | 0 | 15
38959.3802 | 1164 | 0 | 15
38959.3807 | 2348 | 0 | 15
38959.3812 | 2315 | 0 | 15
38959.3817 | 2456 | 0 | 15
38959.3821 | 2009 | 0 | 15
38959.3826 | 1975 | 0 | 15
38959.3831 | 2333 | 0 | 15
38959.3836 | 2479 | 0 | 15
38959.3841 | 2365 | 0 | 15
38959.3846 | 2098 | 0 | 15
38959.3851 | 2174 | 0 | 15
38959.3855 | 2338 | 0 | 15
38959.386 | 2365 | 0 | 15
38959.3865 | 2467 | 0 | 15
38959.387 | 2030 | 0 | 15
38959.3875 | 2333 | 0 | 15
38959.388 | 2001 | 0 | 15
38959.3885 | 2363 | 0 | 15
38959.3889 | 2368 | 0 | 15
15
38959.3549 | 1 | 0 | 16
38959.3554 | 1 | 0 | 16
38959.3559 | 1 | 0 | 16
38959.3564 | 1 | 0 | 16
38959.3569 | 1 | 0 | 16
38959.3574 | 1 | 0 | 16
38959.3579 | 1 | 0 | 16
38959.3583 | 1 | 0 | 16
38959.3588 | 1 | 0 | 16
38959.3593 | 1 | 0 | 16
38959.3598 | 1 | 0 | 16
38959.3603 | 1 | 0 | 16
38959.3608 | 1 | 0 | 16
38959.3613 | 1 | 0 | 16
38959.3617 | 1 | 0 | 16
38959.3622 | 1 | 0 | 16
38959.3627 | 1 | 0 | 16
38959.3632 | 1 | 0 | 16
38959.3637 | 1 | 0 | 16
38959.3642 | 1 | 0 | 16
38959.3647 | 1 | 0 | 16
38959.3652 | 1 | 0 | 16
38959.3656 | 1 | 0 | 16
38959.3661 | 1 | 0 | 16
38959.3666 | 1 | 0 | 16
38959.3671 | 1 | 0 | 16
38959.3676 | 1 | 0 | 16
38959.3681 | 1 | 0 | 16
38959.3686 | 1 | 0 | 16
38959.369 | 1 | 0 | 16
38959.3695 | 1 | 0 | 16
38959.37 | 1 | 0 | 16
38959.3705 | 1 | 0 | 16
38959.371 | 1 | 0 | 16
38959.3715 | 1 | 0 | 16
38959.372 | 1 | 0 | 16
38959.3724 | 1 | 0 | 16
38959.3729 | 1 | 0 | 16
38959.3734 | 1 | 0 | 16
38959.3739 | 1 | 0 | 16
38959.3744 | 1 | 0 | 16
38959.3749 | 1 | 0 | 16
38959.3754 | 1 | 0 | 16
38959.3758 | 792 | 0 | 16
38959.3763 | 2 | 0 | 16
38959.3768 | 47 | 0 | 16
38959.3773 | 137 | 0 | 16
38959.3778 | 3 | 0 | 16
38959.3783 | 5 | 0 | 16
38959.3788 | 29 | 0 | 16
38959.3792 | 782 | 0 | 16
38959.3797 | 507 | 0 | 16
38959.3802 | 664 | 0 | 16
38959.3807 | 218 | 0 | 16
38959.3812 | 844 | 0 | 16
38959.3817 | 1778 | 0 | 16
38959.3822 | 69 | 0 | 16
38959.3826 | 4 | 0 | 16
38959.3831 | 23 | 0 | 16
38959.3836 | 4 | 0 | 16
38959.3841 | 4 | 0 | 16
38959.3846 | 3 | 0 | 16
38959.3851 | 3 | 0 | 16
38959.3856 | 60 | 0 | 16
38959.386 | 128 | 0 | 16
38959.3865 | 3 | 0 | 16
38959.387 | 3 | 0 | 16
38959.3875 | 3 | 0 | 16
38959.388 | 2 | 0 | 16
38959.3885 | 2 | 0 | 16
38959.389 | 2 | 0 | 16
16
38959.355 | 1 | 0 | 17
38959.3554 | 1 | 0 | 17
38959.3559 | 1 | 0 | 17
38959.3564 | 1 | 0 | 17
38959.3569 | 1 | 0 | 17
38959.3574 | 1 | 0 | 17
38959.3579 | 1 | 0 | 17
38959.3584 | 1 | 0 | 17
38959.3588 | 1 | 0 | 17
38959.3593 | 1 | 0 | 17
38959.3598 | 1 | 1 | 17
38959.3603 | 1 | 0 | 17
38959.3608 | 1 | 0 | 17
38959.3613 | 1 | 0 | 17
38959.3618 | 1 | 0 | 17
38959.3622 | 1 | 0 | 17
38959.3627 | 1 | 0 | 17
38959.3632 | 1 | 0 | 17
38959.3637 | 1 | 0 | 17
38959.3642 | 1 | 0 | 17
38959.3647 | 1 | 0 | 17
38959.3652 | 1 | 0 | 17
38959.3656 | 1 | 0 | 17
38959.3661 | 1 | 0 | 17
38959.3666 | 1 | 0 | 17
38959.3671 | 1 | 0 | 17
38959.3676 | 1 | 0 | 17
38959.3681 | 1 | 0 | 17
38959.3686 | 1 | 0 | 17
38959.3691 | 1 | 0 | 17
38959.3695 | 1 | 0 | 17
38959.37 | 1 | 0 | 17
38959.3705 | 1 | 0 | 17
38959.371 | 1 | 0 | 17
38959.3715 | 1 | 0 | 17
38959.372 | 1 | 0 | 17
38959.3725 | 1 | 0 | 17
38959.3729 | 1 | 0 | 17
38959.3734 | 1 | 0 | 17
38959.3739 | 1 | 0 | 17
38959.3744 | 1 | 0 | 17
38959.3749 | 1 | 0 | 17
38959.3754 | 2 | 0 | 17
38959.3759 | 2 | 0 | 17
38959.3763 | 2 | 0 | 17
38959.3768 | 2 | 0 | 17
38959.3773 | 2 | 0 | 17
38959.3778 | 2 | 0 | 17
38959.3783 | 2 | 0 | 17
38959.3788 | 3 | 0 | 17
38959.3793 | 4 | 0 | 17
38959.3797 | 8 | 0 | 17
38959.3802 | 1247 | 0 | 17
38959.3807 | 2443 | 0 | 17
38959.3812 | 1982 | 0 | 17
38959.3817 | 1982 | 0 | 17
38959.3822 | 2425 | 0 | 17
38959.3827 | 1942 | 0 | 17
38959.3831 | 2053 | 0 | 17
38959.3836 | 2078 | 0 | 17
38959.3841 | 2401 | 0 | 17
38959.3846 | 2137 | 0 | 17
38959.3851 | 2331 | 0 | 17
38959.3856 | 1990 | 0 | 17
38959.3861 | 2338 | 0 | 17
38959.3866 | 1976 | 0 | 17
38959.387 | 2435 | 0 | 17
38959.3875 | 2438 | 0 | 17
38959.388 | 2481 | 0 | 17
38959.3885 | 2441 | 0 | 17
38959.389 | 2033 | 0 | 17
17
38959.355 | 1 | 0 | 18
38959.3555 | 1 | 0 | 18
38959.3559 | 1 | 0 | 18
38959.3564 | 1 | 0 | 18
38959.3569 | 1 | 0 | 18
38959.3574 | 1 | 0 | 18
38959.3579 | 1 | 0 | 18
38959.3584 | 1 | 0 | 18
38959.3589 | 1 | 0 | 18
38959.3593 | 1 | 0 | 18
38959.3598 | 1 | 0 | 18
38959.3603 | 1 | 0 | 18
38959.3608 | 1 | 0 | 18
38959.3613 | 1 | 0 | 18
38959.3618 | 1 | 0 | 18
38959.3623 | 1 | 0 | 18
38959.3628 | 1 | 0 | 18
38959.3632 | 1 | 0 | 18
38959.3637 | 1 | 0 | 18
38959.3642 | 1 | 0 | 18
38959.3647 | 1 | 0 | 18
38959.3652 | 1 | 0 | 18
38959.3657 | 1 | 0 | 18
38959.3661 | 1 | 0 | 18
38959.3666 | 1 | 0 | 18
38959.3671 | 1 | 0 | 18
38959.3676 | 1 | 0 | 18
38959.3681 | 1 | 0 | 18
38959.3686 | 1 | 0 | 18
38959.3691 | 1 | 0 | 18
38959.3695 | 1 | 0 | 18
38959.37 | 1 | 0 | 18
38959.3705 | 1 | 0 | 18
38959.371 | 1 | 0 | 18
38959.3715 | 1 | 0 | 18
38959.372 | 1 | 0 | 18
38959.3725 | 1 | 0 | 18
38959.373 | 1 | 0 | 18
38959.3734 | 1 | 0 | 18
38959.3739 | 1 | 0 | 18
38959.3744 | 1 | 0 | 18
38959.3749 | 1 | 0 | 18
38959.3754 | 1 | 0 | 18
38959.3759 | 2 | 0 | 18
38959.3764 | 1 | 0 | 18
38959.3768 | 2 | 0 | 18
38959.3773 | 1 | 0 | 18
38959.3778 | 2 | 0 | 18
38959.3783 | 11 | 0 | 18
38959.3788 | 68 | 0 | 18
38959.3793 | 190 | 0 | 18
38959.3798 | 1976 | 0 | 18
38959.3802 | 2079 | 0 | 18
38959.3807 | 2032 | 0 | 18
38959.3812 | 2169 | 0 | 18
38959.3817 | 2057 | 0 | 18
38959.3822 | 1894 | 0 | 18
38959.3827 | 2189 | 0 | 18
38959.3832 | 2442 | 0 | 18
38959.3836 | 2250 | 0 | 18
38959.3841 | 1972 | 0 | 18
38959.3846 | 2163 | 0 | 18
38959.3851 | 2450 | 0 | 18
38959.3856 | 1977 | 0 | 18
38959.3861 | 1985 | 0 | 18
38959.3866 | 2283 | 0 | 18
38959.387 | 2000 | 0 | 18
38959.3875 | 2331 | 0 | 18
38959.388 | 2009 | 0 | 18
38959.3885 | 2248 | 0 | 18
38959.389 | 2465 | 0 | 18
18
38959.355 | 1 | 0 | 19
38959.3555 | 1 | 0 | 19
38959.356 | 1 | 0 | 19
38959.3564 | 1 | 0 | 19
38959.3569 | 1 | 0 | 19
38959.3574 | 1 | 0 | 19
38959.3579 | 1 | 0 | 19
38959.3584 | 1 | 0 | 19
38959.3589 | 1 | 0 | 19
38959.3594 | 1 | 0 | 19
38959.3598 | 1 | 0 | 19
38959.3603 | 1 | 0 | 19
38959.3608 | 1 | 0 | 19
38959.3613 | 1 | 0 | 19
38959.3618 | 1 | 0 | 19
38959.3623 | 1 | 0 | 19
38959.3628 | 1 | 0 | 19
38959.3633 | 1 | 0 | 19
38959.3637 | 1 | 0 | 19
38959.3642 | 1 | 0 | 19
38959.3647 | 1 | 0 | 19
38959.3652 | 1 | 0 | 19
38959.3657 | 1 | 0 | 19
38959.3662 | 1 | 0 | 19
38959.3667 | 1 | 0 | 19
38959.3671 | 1 | 0 | 19
38959.3676 | 1 | 0 | 19
38959.3681 | 1 | 0 | 19
38959.3686 | 1 | 0 | 19
38959.3691 | 1 | 0 | 19
38959.3696 | 1 | 0 | 19
38959.3701 | 1 | 0 | 19
38959.3705 | 1 | 0 | 19
38959.371 | 1 | 0 | 19
38959.3715 | 1 | 0 | 19
38959.372 | 55 | 0 | 19
38959.3725 | 54 | 0 | 19
38959.373 | 1 | 0 | 19
38959.3735 | 5 | 0 | 19
38959.3739 | 231 | 0 | 19
38959.3744 | 1259 | 0 | 19
38959.3749 | 870 | 0 | 19
38959.3754 | 1947 | 0 | 19
38959.3759 | 2329 | 0 | 19
38959.3764 | 2413 | 0 | 19
38959.3769 | 2131 | 0 | 19
38959.3773 | 2209 | 0 | 19
38959.3778 | 2095 | 0 | 19
38959.3783 | 2405 | 0 | 19
38959.3788 | 2221 | 0 | 19
38959.3793 | 2295 | 0 | 19
38959.3798 | 1964 | 0 | 19
38959.3803 | 2242 | 0 | 19
38959.3808 | 2410 | 0 | 19
38959.3812 | 2150 | 0 | 19
38959.3817 | 2273 | 0 | 19
38959.3822 | 2343 | 0 | 19
38959.3827 | 2292 | 0 | 19
38959.3832 | 2097 | 0 | 19
38959.3837 | 2406 | 0 | 19
38959.3842 | 2260 | 0 | 19
38959.3846 | 1965 | 0 | 19
38959.3851 | 1950 | 0 | 19
38959.3856 | 1915 | 0 | 19
38959.3861 | 1925 | 0 | 19
38959.3866 | 2152 | 0 | 19
38959.3871 | 2415 | 0 | 19
38959.3876 | 2284 | 0 | 19
38959.388 | 2176 | 0 | 19
38959.3885 | 2381 | 0 | 19
38959.389 | 2485 | 0 | 19
19
38959.355 | 1 | 0 | 20
38959.3555 | 1 | 0 | 20
38959.356 | 1 | 1 | 20
38959.3565 | 1 | 0 | 20
38959.3569 | 1 | 0 | 20
38959.3574 | 1 | 0 | 20
38959.3579 | 1 | 0 | 20
38959.3584 | 1 | 0 | 20
38959.3589 | 1 | 0 | 20
38959.3594 | 1 | 0 | 20
38959.3599 | 1 | 0 | 20
38959.3603 | 1 | 0 | 20
38959.3608 | 1 | 0 | 20
38959.3613 | 1 | 0 | 20
38959.3618 | 1 | 0 | 20
38959.3623 | 1 | 0 | 20
38959.3628 | 1 | 0 | 20
38959.3633 | 1 | 0 | 20
38959.3637 | 1 | 0 | 20
38959.3642 | 1 | 0 | 20
38959.3647 | 1 | 0 | 20
38959.3652 | 1 | 0 | 20
38959.3657 | 1 | 0 | 20
38959.3662 | 1 | 0 | 20
38959.3667 | 1 | 0 | 20
38959.3672 | 1 | 0 | 20
38959.3676 | 1 | 0 | 20
38959.3681 | 1 | 0 | 20
38959.3686 | 1 | 0 | 20
38959.3691 | 1 | 0 | 20
38959.3696 | 1 | 0 | 20
38959.3701 | 1 | 0 | 20
38959.3706 | 1 | 0 | 20
38959.371 | 1 | 0 | 20
38959.3715 | 1 | 0 | 20
38959.372 | 1 | 0 | 20
38959.3725 | 1 | 0 | 20
38959.373 | 1 | 0 | 20
38959.3735 | 1 | 0 | 20
38959.374 | 1655 | 0 | 20
38959.3744 | 2298 | 0 | 20
38959.3749 | 2187 | 0 | 20
38959.3754 | 1966 | 0 | 20
38959.3759 | 2126 | 0 | 20
38959.3764 | 2032 | 0 | 20
38959.3769 | 2453 | 0 | 20
38959.3774 | 2193 | 0 | 20
38959.3778 | 2379 | 0 | 20
38959.3783 | 2281 | 0 | 20
38959.3788 | 2067 | 0 | 20
38959.3793 | 2500 | 0 | 20
38959.3798 | 2493 | 0 | 20
38959.3803 | 2408 | 0 | 20
38959.3808 | 2232 | 0 | 20
38959.3812 | 1999 | 0 | 20
38959.3817 | 1944 | 0 | 20
38959.3822 | 1950 | 0 | 20
38959.3827 | 2160 | 0 | 20
38959.3832 | 2371 | 0 | 20
38959.3837 | 2183 | 0 | 20
38959.3842 | 2444 | 0 | 20
38959.3847 | 1947 | 0 | 20
38959.3851 | 2031 | 0 | 20
38959.3856 | 2509 | 0 | 20
38959.3861 | 2079 | 0 | 20
38959.3866 | 2359 | 0 | 20
38959.3871 | 2277 | 0 | 20
38959.3876 | 2012 | 0 | 20
38959.3881 | 1954 | 0 | 20
38959.3885 | 2286 | 0 | 20
38959.389 | 2458 | 0 | 20
20
38959.355 | 1 | 0 | 21
38959.3555 | 1 | 0 | 21
38959.356 | 1 | 0 | 21
38959.3565 | 1 | 0 | 21
38959.357 | 1 | 0 | 21
38959.3575 | 1 | 0 | 21
38959.3579 | 1 | 0 | 21
38959.3584 | 1 | 0 | 21
38959.3589 | 1 | 0 | 21
38959.3594 | 1 | 0 | 21
38959.3599 | 1 | 0 | 21
38959.3604 | 1 | 0 | 21
38959.3609 | 1 | 0 | 21
38959.3613 | 1 | 0 | 21
38959.3618 | 1 | 0 | 21
38959.3623 | 1 | 0 | 21
38959.3628 | 1 | 0 | 21
38959.3633 | 1 | 0 | 21
38959.3638 | 1 | 0 | 21
38959.3643 | 1 | 0 | 21
38959.3647 | 1 | 0 | 21
38959.3652 | 1 | 0 | 21
38959.3657 | 1 | 0 | 21
38959.3662 | 1 | 0 | 21
38959.3667 | 1 | 0 | 21
38959.3672 | 1 | 0 | 21
38959.3677 | 1 | 0 | 21
38959.3681 | 1 | 0 | 21
38959.3686 | 1 | 0 | 21
38959.3691 | 1 | 0 | 21
38959.3696 | 1 | 0 | 21
38959.3701 | 1 | 0 | 21
38959.3706 | 1 | 0 | 21
38959.3711 | 1 | 0 | 21
38959.3716 | 1 | 0 | 21
38959.372 | 815 | 0 | 21
38959.3725 | 387 | 0 | 21
38959.373 | 1 | 0 | 21
38959.3735 | 108 | 0 | 21
38959.374 | 2 | 0 | 21
38959.3745 | 478 | 0 | 21
38959.3749 | 777 | 0 | 21
38959.3754 | 2116 | 0 | 21
38959.3759 | 2030 | 0 | 21
38959.3764 | 2418 | 0 | 21
38959.3769 | 1907 | 0 | 21
38959.3774 | 1891 | 0 | 21
38959.3779 | 2418 | 0 | 21
38959.3783 | 2434 | 0 | 21
38959.3788 | 2283 | 0 | 21
38959.3793 | 1931 | 0 | 21
38959.3798 | 1963 | 0 | 21
38959.3803 | 2388 | 0 | 21
38959.3808 | 2372 | 0 | 21
38959.3813 | 2188 | 0 | 21
38959.3818 | 2113 | 0 | 21
38959.3822 | 2146 | 0 | 21
38959.3827 | 2002 | 0 | 21
38959.3832 | 2090 | 0 | 21
38959.3837 | 2444 | 0 | 21
38959.3842 | 1984 | 0 | 21
38959.3847 | 2118 | 0 | 21
38959.3852 | 2099 | 0 | 21
38959.3856 | 2478 | 0 | 21
38959.3861 | 2185 | 0 | 21
38959.3866 | 2251 | 0 | 21
38959.3871 | 2116 | 0 | 21
38959.3876 | 1917 | 0 | 21
38959.3881 | 1919 | 0 | 21
38959.3886 | 2345 | 0 | 21
38959.389 | 2006 | 0 | 21
21
38959.355 | 1 | 0 | 22
38959.3555 | 1 | 0 | 22
38959.356 | 1 | 0 | 22
38959.3565 | 1 | 0 | 22
38959.357 | 1 | 0 | 22
38959.3575 | 1 | 0 | 22
38959.358 | 1 | 0 | 22
38959.3584 | 1 | 0 | 22
38959.3589 | 1 | 0 | 22
38959.3594 | 1 | 0 | 22
38959.3599 | 1 | 0 | 22
38959.3604 | 1 | 0 | 22
38959.3609 | 1 | 0 | 22
38959.3614 | 1 | 0 | 22
38959.3618 | 1 | 0 | 22
38959.3623 | 1 | 0 | 22
38959.3628 | 1 | 0 | 22
38959.3633 | 1 | 0 | 22
38959.3638 | 1 | 0 | 22
38959.3643 | 1 | 0 | 22
38959.3648 | 1 | 0 | 22
38959.3652 | 1 | 0 | 22
38959.3657 | 1 | 0 | 22
38959.3662 | 1 | 0 | 22
38959.3667 | 1 | 0 | 22
38959.3672 | 1 | 0 | 22
38959.3677 | 1 | 0 | 22
38959.3682 | 1 | 0 | 22
38959.3686 | 1 | 0 | 22
38959.3691 | 1 | 0 | 22
38959.3696 | 1 | 0 | 22
38959.3701 | 1 | 0 | 22
38959.3706 | 2 | 0 | 22
38959.3711 | 1 | 0 | 22
38959.3716 | 1 | 0 | 22
38959.372 | 1 | 0 | 22
38959.3725 | 1 | 0 | 22
38959.373 | 1 | 0 | 22
38959.3735 | 1 | 0 | 22
38959.374 | 1 | 0 | 22
38959.3745 | 1 | 0 | 22
38959.375 | 2 | 0 | 22
38959.3755 | 7 | 0 | 22
38959.3759 | 721 | 0 | 22
38959.3764 | 3 | 0 | 22
38959.3769 | 3 | 0 | 22
38959.3774 | 33 | 0 | 22
38959.3779 | 89 | 0 | 22
38959.3784 | 24 | 0 | 22
38959.3789 | 671 | 0 | 22
38959.3793 | 740 | 0 | 22
38959.3798 | 121 | 0 | 22
38959.3803 | 1534 | 0 | 22
38959.3808 | 12 | 0 | 22
38959.3813 | 9 | 0 | 22
38959.3818 | 862 | 0 | 22
38959.3823 | 3 | 0 | 22
38959.3827 | 4 | 0 | 22
38959.3832 | 4 | 0 | 22
38959.3837 | 4 | 0 | 22
38959.3842 | 177 | 0 | 22
38959.3847 | 3 | 0 | 22
38959.3852 | 3 | 0 | 22
38959.3857 | 3 | 0 | 22
38959.3861 | 4 | 0 | 22
38959.3866 | 2 | 0 | 22
38959.3871 | 2 | 0 | 22
38959.3876 | 3 | 0 | 22
38959.3881 | 2 | 0 | 22
38959.3886 | 2 | 0 | 22
38959.3891 | 2 | 0 | 22
22
38959.3551 | 1 | 0 | 23
38959.3555 | 1 | 0 | 23
38959.356 | 1 | 0 | 23
38959.3565 | 1 | 0 | 23
38959.357 | 1 | 0 | 23
38959.3575 | 1 | 0 | 23
38959.358 | 1 | 0 | 23
38959.3585 | 1 | 0 | 23
38959.3589 | 1 | 0 | 23
38959.3594 | 1 | 0 | 23
38959.3599 | 1 | 0 | 23
38959.3604 | 1 | 0 | 23
38959.3609 | 1 | 0 | 23
38959.3614 | 1 | 0 | 23
38959.3619 | 1 | 0 | 23
38959.3623 | 1 | 0 | 23
38959.3628 | 1 | 0 | 23
38959.3633 | 1 | 1 | 23
38959.3638 | 1 | 0 | 23
38959.3643 | 1 | 0 | 23
38959.3648 | 1 | 0 | 23
38959.3653 | 1 | 0 | 23
38959.3657 | 1 | 0 | 23
38959.3662 | 1 | 0 | 23
38959.3667 | 1 | 0 | 23
38959.3672 | 1 | 0 | 23
38959.3677 | 1 | 0 | 23
38959.3682 | 1 | 0 | 23
38959.3687 | 1 | 0 | 23
38959.3691 | 1 | 0 | 23
38959.3696 | 1 | 0 | 23
38959.3701 | 1 | 0 | 23
38959.3706 | 1 | 0 | 23
38959.3711 | 1 | 0 | 23
38959.3716 | 68 | 0 | 23
38959.3721 | 116 | 0 | 23
38959.3725 | 154 | 0 | 23
38959.373 | 3 | 0 | 23
38959.3735 | 1 | 0 | 23
38959.374 | 154 | 0 | 23
38959.3745 | 602 | 0 | 23
38959.375 | 1970 | 0 | 23
38959.3755 | 2121 | 0 | 23
38959.3759 | 1962 | 0 | 23
38959.3764 | 2297 | 0 | 23
38959.3769 | 1937 | 0 | 23
38959.3774 | 2108 | 0 | 23
38959.3779 | 2356 | 0 | 23
38959.3784 | 2238 | 0 | 23
38959.3789 | 2272 | 0 | 23
38959.3794 | 1922 | 0 | 23
38959.3798 | 2279 | 0 | 23
38959.3803 | 2113 | 0 | 23
38959.3808 | 2152 | 0 | 23
38959.3813 | 2446 | 0 | 23
38959.3818 | 2352 | 0 | 23
38959.3823 | 2455 | 0 | 23
38959.3828 | 2459 | 0 | 23
38959.3832 | 1988 | 0 | 23
38959.3837 | 2013 | 0 | 23
38959.3842 | 2366 | 0 | 23
38959.3847 | 2429 | 0 | 23
38959.3852 | 2095 | 0 | 23
38959.3857 | 2400 | 0 | 23
38959.3862 | 2304 | 0 | 23
38959.3866 | 2439 | 0 | 23
38959.3871 | 2286 | 0 | 23
38959.3876 | 2361 | 0 | 23
38959.3881 | 1935 | 0 | 23
38959.3886 | 2364 | 0 | 23
38959.3891 | 2097 | 0 | 23
23
38959.3551 | 1 | 1 | 24
38959.3556 | 1 | 0 | 24
38959.356 | 1 | 0 | 24
38959.3565 | 1 | 0 | 24
38959.357 | 1 | 0 | 24
38959.3575 | 1 | 0 | 24
38959.358 | 1 | 0 | 24
38959.3585 | 1 | 0 | 24
38959.359 | 1 | 0 | 24
38959.3594 | 1 | 1 | 24
38959.3599 | 1 | 0 | 24
38959.3604 | 1 | 0 | 24
38959.3609 | 1 | 0 | 24
38959.3614 | 1 | 0 | 24
38959.3619 | 1 | 0 | 24
38959.3624 | 1 | 0 | 24
38959.3628 | 1 | 0 | 24
38959.3633 | 1 | 0 | 24
38959.3638 | 1 | 0 | 24
38959.3643 | 1 | 0 | 24
38959.3648 | 1 | 0 | 24
38959.3653 | 1 | 0 | 24
38959.3658 | 1 | 0 | 24
38959.3662 | 1 | 0 | 24
38959.3667 | 1 | 0 | 24
38959.3672 | 1 | 0 | 24
38959.3677 | 1 | 0 | 24
38959.3682 | 1 | 0 | 24
38959.3687 | 1 | 0 | 24
38959.3692 | 1 | 0 | 24
38959.3697 | 1 | 0 | 24
38959.3701 | 1 | 0 | 24
38959.3706 | 1 | 0 | 24
38959.3711 | 1 | 0 | 24
38959.3716 | 1 | 0 | 24
38959.3721 | 1 | 0 | 24
38959.3726 | 1 | 0 | 24
38959.3731 | 1 | 0 | 24
38959.3735 | 1 | 0 | 24
38959.374 | 1 | 0 | 24
38959.3745 | 2 | 0 | 24
38959.375 | 2 | 0 | 24
38959.3755 | 2 | 0 | 24
38959.376 | 3 | 0 | 24
38959.3765 | 3 | 0 | 24
38959.3769 | 3 | 0 | 24
38959.3774 | 3 | 0 | 24
38959.3779 | 3 | 0 | 24
38959.3784 | 24 | 0 | 24
38959.3789 | 14 | 0 | 24
38959.3794 | 156 | 0 | 24
38959.3799 | 23 | 0 | 24
38959.3803 | 2027 | 0 | 24
38959.3808 | 2255 | 0 | 24
38959.3813 | 2238 | 0 | 24
38959.3818 | 2065 | 0 | 24
38959.3823 | 2001 | 0 | 24
38959.3828 | 2181 | 0 | 24
38959.3833 | 2271 | 0 | 24
38959.3838 | 1963 | 0 | 24
38959.3842 | 2162 | 0 | 24
38959.3847 | 2247 | 0 | 24
38959.3852 | 1976 | 0 | 24
38959.3857 | 2421 | 0 | 24
38959.3862 | 2352 | 0 | 24
38959.3867 | 2399 | 0 | 24
38959.3872 | 2115 | 0 | 24
38959.3876 | 2272 | 0 | 24
38959.3881 | 2403 | 0 | 24
38959.3886 | 2143 | 0 | 24
38959.3891 | 1938 | 0 | 24
24
38959.3551 | 1 | 0 | 25
38959.3556 | 1 | 0 | 25
38959.3561 | 1 | 0 | 25
38959.3565 | 1 | 0 | 25
38959.357 | 1 | 0 | 25
38959.3575 | 1 | 0 | 25
38959.358 | 1 | 0 | 25
38959.3585 | 1 | 0 | 25
38959.359 | 1 | 0 | 25
38959.3595 | 1 | 0 | 25
38959.3599 | 1 | 0 | 25
38959.3604 | 1 | 0 | 25
38959.3609 | 1 | 0 | 25
38959.3614 | 1 | 0 | 25
38959.3619 | 1 | 0 | 25
38959.3624 | 1 | 0 | 25
38959.3629 | 1 | 0 | 25
38959.3633 | 1 | 0 | 25
38959.3638 | 1 | 0 | 25
38959.3643 | 1 | 0 | 25
38959.3648 | 1 | 0 | 25
38959.3653 | 1 | 0 | 25
38959.3658 | 1 | 0 | 25
38959.3663 | 1 | 0 | 25
38959.3667 | 1 | 0 | 25
38959.3672 | 1 | 0 | 25
38959.3677 | 1 | 0 | 25
38959.3682 | 1 | 0 | 25
38959.3687 | 1 | 0 | 25
38959.3692 | 1 | 0 | 25
38959.3697 | 1 | 0 | 25
38959.3702 | 1 | 0 | 25
38959.3706 | 1 | 0 | 25
38959.3711 | 1 | 0 | 25
38959.3716 | 1 | 0 | 25
38959.3721 | 1 | 0 | 25
38959.3726 | 1 | 0 | 25
38959.3731 | 1 | 0 | 25
38959.3736 | 1 | 0 | 25
38959.374 | 1311 | 0 | 25
38959.3745 | 2429 | 0 | 25
38959.375 | 2164 | 0 | 25
38959.3755 | 2045 | 0 | 25
38959.376 | 2273 | 0 | 25
38959.3765 | 2099 | 0 | 25
38959.377 | 2369 | 0 | 25
38959.3774 | 2202 | 0 | 25
38959.3779 | 1987 | 0 | 25
38959.3784 | 2419 | 0 | 25
38959.3789 | 2055 | 0 | 25
38959.3794 | 2154 | 0 | 25
38959.3799 | 2463 | 0 | 25
38959.3804 | 2195 | 0 | 25
38959.3808 | 2155 | 0 | 25
38959.3813 | 2389 | 0 | 25
38959.3818 | 2360 | 0 | 25
38959.3823 | 2003 | 0 | 25
38959.3828 | 2358 | 0 | 25
38959.3833 | 2394 | 0 | 25
38959.3838 | 2054 | 0 | 25
38959.3842 | 2490 | 0 | 25
38959.3847 | 2513 | 0 | 25
38959.3852 | 1982 | 0 | 25
38959.3857 | 2119 | 0 | 25
38959.3862 | 2492 | 0 | 25
38959.3867 | 2018 | 0 | 25
38959.3872 | 2299 | 0 | 25
38959.3877 | 2318 | 0 | 25
38959.3881 | 2236 | 0 | 25
38959.3886 | 2115 | 0 | 25
38959.3891 | 2397 | 0 | 25
25
38959.3551 | 1 | 0 | 26
38959.3556 | 1 | 0 | 26
38959.3561 | 1 | 0 | 26
38959.3566 | 1 | 0 | 26
38959.357 | 1 | 0 | 26
38959.3575 | 1 | 0 | 26
38959.358 | 1 | 0 | 26
38959.3585 | 1 | 0 | 26
38959.359 | 1 | 0 | 26
38959.3595 | 1 | 0 | 26
38959.36 | 1 | 0 | 26
38959.3605 | 1 | 0 | 26
38959.3609 | 1 | 0 | 26
38959.3614 | 1 | 0 | 26
38959.3619 | 1 | 0 | 26
38959.3624 | 1 | 0 | 26
38959.3629 | 1 | 0 | 26
38959.3634 | 1 | 0 | 26
38959.3639 | 1 | 0 | 26
38959.3643 | 1 | 0 | 26
38959.3648 | 1 | 0 | 26
38959.3653 | 1 | 0 | 26
38959.3658 | 1 | 0 | 26
38959.3663 | 1 | 0 | 26
38959.3668 | 1 | 0 | 26
38959.3673 | 1 | 0 | 26
38959.3677 | 1 | 0 | 26
38959.3682 | 1 | 0 | 26
38959.3687 | 1 | 0 | 26
38959.3692 | 1 | 0 | 26
38959.3697 | 1 | 0 | 26
38959.3702 | 1 | 0 | 26
38959.3707 | 1 | 0 | 26
38959.3711 | 1 | 0 | 26
38959.3716 | 1 | 0 | 26
38959.3721 | 1 | 0 | 26
38959.3726 | 1 | 0 | 26
38959.3731 | 1 | 0 | 26
38959.3736 | 1 | 0 | 26
38959.3741 | 2 | 0 | 26
38959.3745 | 2 | 0 | 26
38959.375 | 2 | 0 | 26
38959.3755 | 2 | 0 | 26
38959.376 | 4 | 0 | 26
38959.3765 | 3 | 0 | 26
38959.377 | 3 | 0 | 26
38959.3775 | 5 | 0 | 26
38959.3779 | 3 | 0 | 26
38959.3784 | 31 | 0 | 26
38959.3789 | 27 | 0 | 26
38959.3794 | 719 | 0 | 26
38959.3799 | 990 | 0 | 26
38959.3804 | 927 | 0 | 26
38959.3809 | 1512 | 0 | 26
38959.3814 | 51 | 0 | 26
38959.3818 | 8 | 0 | 26
38959.3823 | 3 | 0 | 26
38959.3828 | 3 | 0 | 26
38959.3833 | 5 | 0 | 26
38959.3838 | 4 | 0 | 26
38959.3843 | 3 | 0 | 26
38959.3847 | 4 | 0 | 26
38959.3852 | 3 | 0 | 26
38959.3862 | 2 | 0 | 26
38959.3867 | 3 | 0 | 26
38959.3872 | 2 | 0 | 26
38959.3877 | 2 | 0 | 26
38959.3881 | 2 | 0 | 26
38959.3886 | 2 | 0 | 26
38959.3891 | 2 | 0 | 26
26
38959.3551 | 1 | 0 | 27
38959.3556 | 1 | 0 | 27
38959.3561 | 1 | 0 | 27
38959.3566 | 1 | 0 | 27
38959.3571 | 1 | 0 | 27
38959.3575 | 1 | 0 | 27
38959.358 | 1 | 0 | 27
38959.3585 | 1 | 0 | 27
38959.359 | 1 | 0 | 27
38959.3595 | 1 | 0 | 27
38959.36 | 1 | 0 | 27
38959.3605 | 1 | 0 | 27
38959.3609 | 1 | 0 | 27
38959.3614 | 1 | 0 | 27
38959.3619 | 1 | 0 | 27
38959.3624 | 1 | 0 | 27
38959.3629 | 1 | 0 | 27
38959.3634 | 1 | 0 | 27
38959.3639 | 1 | 0 | 27
38959.3644 | 1 | 0 | 27
38959.3648 | 1 | 0 | 27
38959.3653 | 1 | 0 | 27
38959.3658 | 1 | 0 | 27
38959.3663 | 1 | 0 | 27
38959.3668 | 1 | 0 | 27
38959.3673 | 1 | 0 | 27
38959.3678 | 1 | 0 | 27
38959.3682 | 1 | 0 | 27
38959.3687 | 1 | 0 | 27
38959.3692 | 2 | 0 | 27
38959.3697 | 1 | 0 | 27
38959.3702 | 1 | 0 | 27
38959.3707 | 1 | 0 | 27
38959.3712 | 1 | 0 | 27
38959.3716 | 1 | 0 | 27
38959.3721 | 1 | 0 | 27
38959.3726 | 1 | 0 | 27
38959.3731 | 1 | 0 | 27
38959.3736 | 4 | 0 | 27
38959.3741 | 1561 | 0 | 27
38959.3746 | 2449 | 0 | 27
38959.375 | 2447 | 0 | 27
38959.3755 | 2211 | 0 | 27
38959.376 | 2214 | 0 | 27
38959.3765 | 1941 | 0 | 27
38959.377 | 1939 | 0 | 27
38959.3775 | 2404 | 0 | 27
38959.378 | 1938 | 0 | 27
38959.3784 | 2051 | 0 | 27
38959.3789 | 2490 | 0 | 27
38959.3794 | 2255 | 0 | 27
38959.3799 | 2332 | 0 | 27
38959.3804 | 2083 | 0 | 27
38959.3809 | 2508 | 0 | 27
38959.3814 | 2453 | 0 | 27
38959.3819 | 2500 | 0 | 27
38959.3823 | 1946 | 0 | 27
38959.3828 | 2388 | 0 | 27
38959.3833 | 2128 | 0 | 27
38959.3838 | 2486 | 0 | 27
38959.3843 | 2418 | 0 | 27
38959.3848 | 2458 | 0 | 27
38959.3853 | 2117 | 0 | 27
38959.3857 | 2067 | 0 | 27
38959.3862 | 2133 | 0 | 27
38959.3867 | 1939 | 0 | 27
38959.3872 | 2340 | 0 | 27
38959.3877 | 2078 | 0 | 27
38959.3882 | 2022 | 0 | 27
38959.3887 | 2209 | 0 | 27
38959.3891 | 2116 | 0 | 27
27
38959.3551 | 1 | 0 | 28
38959.3556 | 1 | 0 | 28
38959.3561 | 1 | 0 | 28
38959.3566 | 1 | 0 | 28
38959.3571 | 1 | 0 | 28
38959.3576 | 1 | 0 | 28
38959.3581 | 1 | 0 | 28
38959.3585 | 1 | 0 | 28
38959.359 | 1 | 0 | 28
38959.3595 | 1 | 0 | 28
38959.36 | 1 | 0 | 28
38959.3605 | 1 | 0 | 28
38959.361 | 1 | 0 | 28
38959.3614 | 1 | 0 | 28
38959.3619 | 1 | 0 | 28
38959.3624 | 1 | 0 | 28
38959.3629 | 1 | 0 | 28
38959.3634 | 1 | 0 | 28
38959.3639 | 1 | 0 | 28
38959.3644 | 1 | 0 | 28
38959.3648 | 1 | 0 | 28
38959.3653 | 1 | 0 | 28
38959.3658 | 1 | 0 | 28
38959.3663 | 1 | 0 | 28
38959.3668 | 1 | 0 | 28
38959.3673 | 1 | 0 | 28
38959.3678 | 1 | 0 | 28
38959.3683 | 1 | 0 | 28
38959.3687 | 1 | 0 | 28
38959.3692 | 1 | 0 | 28
38959.3697 | 1 | 0 | 28
38959.3702 | 1 | 0 | 28
38959.3707 | 1 | 0 | 28
38959.3712 | 1 | 0 | 28
38959.3717 | 1 | 0 | 28
38959.3721 | 1 | 0 | 28
38959.3726 | 1 | 0 | 28
38959.3731 | 1 | 0 | 28
38959.3736 | 1 | 0 | 28
38959.3741 | 2 | 0 | 28
38959.3746 | 2 | 0 | 28
38959.3751 | 3 | 0 | 28
38959.3755 | 2 | 0 | 28
38959.376 | 2 | 0 | 28
38959.3765 | 2 | 0 | 28
38959.377 | 3 | 0 | 28
38959.3775 | 2 | 0 | 28
38959.378 | 5 | 0 | 28
38959.3785 | 31 | 0 | 28
38959.3789 | 1585 | 0 | 28
38959.3794 | 208 | 0 | 28
38959.3799 | 598 | 0 | 28
38959.3804 | 2217 | 0 | 28
38959.3809 | 1975 | 0 | 28
38959.3814 | 2179 | 0 | 28
38959.3819 | 2006 | 0 | 28
38959.3823 | 2121 | 0 | 28
38959.3828 | 2192 | 0 | 28
38959.3833 | 2138 | 0 | 28
38959.3838 | 1911 | 0 | 28
38959.3843 | 2379 | 0 | 28
38959.3848 | 1908 | 0 | 28
38959.3853 | 2322 | 0 | 28
38959.3858 | 2417 | 0 | 28
38959.3862 | 2233 | 0 | 28
38959.3867 | 2078 | 0 | 28
38959.3872 | 2295 | 0 | 28
38959.3877 | 1912 | 0 | 28
38959.3882 | 2044 | 0 | 28
38959.3887 | 2358 | 0 | 28
38959.3892 | 2173 | 0 | 28
28
38959.3552 | 1 | 0 | 29
38959.3556 | 1 | 0 | 29
38959.3561 | 1 | 0 | 29
38959.3566 | 1 | 0 | 29
38959.3571 | 1 | 0 | 29
38959.3576 | 1 | 0 | 29
38959.3581 | 1 | 0 | 29
38959.3586 | 1 | 0 | 29
38959.359 | 1 | 0 | 29
38959.3595 | 1 | 0 | 29
38959.36 | 1 | 0 | 29
38959.3605 | 2 | 0 | 29
38959.361 | 1 | 0 | 29
38959.3615 | 1 | 0 | 29
38959.362 | 1 | 0 | 29
38959.3624 | 1 | 0 | 29
38959.3629 | 1 | 0 | 29
38959.3634 | 1 | 0 | 29
38959.3639 | 1 | 0 | 29
38959.3644 | 1 | 0 | 29
38959.3649 | 1 | 0 | 29
38959.3654 | 1 | 0 | 29
38959.3658 | 1 | 0 | 29
38959.3663 | 1 | 0 | 29
38959.3668 | 1 | 0 | 29
38959.3673 | 1 | 0 | 29
38959.3678 | 1 | 0 | 29
38959.3683 | 1 | 0 | 29
38959.3688 | 1 | 0 | 29
38959.3692 | 1 | 0 | 29
38959.3697 | 1 | 0 | 29
38959.3702 | 1 | 0 | 29
38959.3707 | 1 | 0 | 29
38959.3712 | 1 | 0 | 29
38959.3717 | 1 | 0 | 29
38959.3722 | 1 | 0 | 29
38959.3727 | 1 | 0 | 29
38959.3731 | 1 | 0 | 29
38959.3736 | 1 | 0 | 29
38959.3741 | 1 | 0 | 29
38959.3746 | 2 | 0 | 29
38959.3751 | 2 | 0 | 29
38959.3756 | 801 | 0 | 29
38959.3761 | 101 | 0 | 29
38959.3765 | 2 | 0 | 29
38959.377 | 11 | 0 | 29
38959.3775 | 3 | 0 | 29
38959.378 | 2 | 0 | 29
38959.3785 | 73 | 17 | 29
38959.379 | 92 | 0 | 29
38959.3795 | 681 | 22 | 29
38959.3799 | 526 | 0 | 29
38959.3804 | 513 | 0 | 29
38959.3809 | 1495 | 0 | 29
38959.3814 | 1688 | 0 | 29
38959.3819 | 1061 | 0 | 29
38959.3824 | 3 | 0 | 29
38959.3829 | 1745 | 0 | 29
38959.3833 | 356 | 0 | 29
38959.3838 | 4 | 0 | 29
38959.3843 | 422 | 0 | 29
38959.3848 | 3 | 0 | 29
38959.3853 | 3 | 0 | 29
38959.3858 | 50 | 0 | 29
38959.3863 | 2 | 0 | 29
38959.3867 | 2 | 0 | 29
38959.3872 | 2 | 0 | 29
38959.3877 | 2 | 0 | 29
38959.3882 | 3 | 0 | 29
38959.3887 | 2 | 0 | 29
38959.3892 | 3 | 0 | 29
29
38959.3552 | 1 | 0 | 30
38959.3556 | 1 | 0 | 30
38959.3561 | 1 | 0 | 30
38959.3566 | 1 | 0 | 30
38959.3571 | 1 | 0 | 30
38959.3576 | 1 | 0 | 30
38959.3581 | 1 | 0 | 30
38959.3586 | 1 | 0 | 30
38959.3591 | 1 | 0 | 30
38959.3595 | 1 | 0 | 30
38959.36 | 1 | 0 | 30
38959.3605 | 1 | 0 | 30
38959.361 | 1 | 0 | 30
38959.3615 | 1 | 0 | 30
38959.362 | 1 | 0 | 30
38959.3625 | 1 | 0 | 30
38959.3629 | 1 | 0 | 30
38959.3634 | 1 | 0 | 30
38959.3639 | 1 | 0 | 30
38959.3644 | 1 | 0 | 30
38959.3654 | 1 | 0 | 30
38959.3659 | 1 | 0 | 30
38959.3663 | 1 | 0 | 30
38959.3668 | 1 | 0 | 30
38959.3673 | 1 | 0 | 30
38959.3678 | 1 | 0 | 30
38959.3683 | 1 | 0 | 30
38959.3688 | 1 | 0 | 30
38959.3693 | 1 | 0 | 30
38959.3697 | 1 | 0 | 30
38959.3702 | 1 | 0 | 30
38959.3707 | 1 | 0 | 30
38959.3712 | 1 | 0 | 30
38959.3717 | 1 | 0 | 30
38959.3722 | 1 | 0 | 30
38959.3727 | 1 | 0 | 30
38959.3731 | 1 | 0 | 30
38959.3736 | 1 | 0 | 30
38959.3741 | 1 | 0 | 30
38959.3746 | 2 | 0 | 30
38959.3751 | 2 | 0 | 30
38959.3756 | 2 | 0 | 30
38959.3761 | 2 | 0 | 30
38959.3766 | 2 | 0 | 30
38959.377 | 2 | 0 | 30
38959.3775 | 2 | 0 | 30
38959.378 | 14 | 0 | 30
38959.3785 | 8 | 0 | 30
38959.379 | 1955 | 41 | 30
38959.3795 | 470 | 4 | 30
38959.38 | 2235 | 0 | 30
38959.3804 | 2205 | 0 | 30
38959.3809 | 2197 | 0 | 30
38959.3814 | 2188 | 0 | 30
38959.3819 | 2050 | 0 | 30
38959.3824 | 2444 | 0 | 30
38959.3829 | 2136 | 0 | 30
38959.3834 | 2188 | 0 | 30
38959.3838 | 1971 | 0 | 30
38959.3843 | 1966 | 0 | 30
38959.3848 | 2158 | 1 | 30
38959.3853 | 1916 | 0 | 30
38959.3858 | 2217 | 0 | 30
38959.3863 | 1979 | 0 | 30
38959.3868 | 2194 | 0 | 30
38959.3872 | 2142 | 0 | 30
38959.3877 | 2414 | 0 | 30
38959.3882 | 2077 | 0 | 30
38959.3887 | 2049 | 0 | 30
38959.3892 | 2215 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 76
Time when Penlight power was initiated: | 90