## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 44
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of PE, XLPE, XLPO, EPR, Tefzel & Silicone Rubber insulated control cables (Items 15, 10, 8, 2, 12 & 9). Cable specimens present: Six lengths of cable were monitored for electrical performance, 1 each of PE, XLPE, XLPO, EPR, Tefzel & Silicone Rubber. A seventh length of cable (EPR cable Item #2) was monitored for temperature response. No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 145 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
145 | 0 | Initated Penlight Heating
953 | 808 | Cables ignite and burn
981 | 836 | Power to Penlight is shutoff
1043-1064 | 898-919 | Conductors D7, D8, E9 & E10 all short to ground 24, 6, 446 & 309) | EPR Cable D and Tefzel Cable E short to ground
1067 | 922 | Conductors D7 & D8 short together at less than 100 ohms (16) | EPR Cable D shorts internally
1082-1084 | 937-939 | Conductor D8 shorts to conductors E9 & E10 at less than 100 ohms (4 & 9) | Cable to cable short occurs after both cables have faulted to ground
1093-1216 | 948-1068 | Conductors E9 & E10 short together (46), conductors C5 & C6 short together (19), and conductors A1 & A2 short together (3) | PE Cable A, XLPO Cable C and Tefzel Cable E are shorted internally
1246-1249 | 1101-1104 | The existing ground faults on conductors E9 & E10 decrease to much less than 100 ohms (<1 & <1)
1255-1258 | 1110-1113 | Conductor D7 shorts to conductors E9 & E10 at less than 100 ohms (27 & 9) | Cable to cable short occurs after both cables have faulted to ground
1353 | 1208 | Conductors B3 & B4 short together at less than 1000 ohms (196) | XLPE Cable B is shorted internally
1379-1389 | 1234-1244 | Conductors C5 & C6 both short to ground at less than 100 ohms (1 & 1) | XLPO Cable C shorts to ground
1535 | 1390 | Conductor B3 shorts to ground at less than 100 ohms (59)
1537 | 1392 | The existing short between conductors B3 & B4 decreases to less than 100 ohms (4)
1550 | 1405 | Conductor B4 shorts to ground at less than 100 ohms (65) | XLPE Cable B is shorted to ground
Additional Observations
Observation 1 | The silicone rubber cable (F) did not fail either internally or externally.
Observation 2 | It took 808 s (13.5min.) from the start of Penlight heating for the cable bundle to ignite, 898 s (15 min.) for the first short to ground, and 922 s (15.4 min.) for the initial internal short.
Observation 3 | No cable to cable interactions took place prior to the individual cables either shorting to ground or shorting internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A = PE Cable, Item #15
B = XLPE Cable, Item #10
C = XLPO Cable, Item #8
D = EPR Cable, Item #2
E = Tefzel Cable, Item #12
F = Silicone Rubber Cable, Item #9
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 44 |  |  | 2006-08-21 | 12:53
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-144.5 | 211201.9994 | -141.5 | 211201.9994 | -138.5 | 211201.9994 | -136 | 211201.9994 | -133 | 211201.9994 | -113.5 | 211201.9994 | -111 | 211201.9994 | -108 | 211201.9994 | -105 | 211201.9994 | -85.5 | 211201.9994 | -82.5 | 211201.9994 | -80 | 211201.9994 | -77.5 | 246937.9994 | -74.5 | 249537.9994 | -71.5 | 259037.9994 | -68.5 | 252737.9994 | -60.5 | 211201.9994 | -57.5 | 211201.9994 | -55 | 254737.9994 | -52 | 254937.9994 | -49.5 | 258337.9994 | -46.5 | 220637.9994 | -38 | 211201.9994 | -29.5 | 258737.9994 | -26.5 | 236737.9994 | -24 | 211201.9994 | -21.5 | 211201.9994 | -12.5 | 244137.9994 | -10 | 245037.9994 | -7.5 | 211201.9994 | -4.5 | 211201.9994 | -1.5 | 247537.9994 | 1 | 255337.9994 | 4 | 260137.9994 | 12.5 | 252637.9994 | 15 | 251837.9994 | 23.5 | 258637.9994 | 26.5 | 238537.9994 | 29 | 260737.9994 | 32 | 255737.9994 | 34.5 | 257937.9994 | 37.5 | 211201.9994 | -126.125 | 211201.9994 | -120.5 | 211201.9994 | -70.125 | 211201.9994 | -64.75 | 246937.9994 | -59 | 220637.9994 | -19.625 | 236737.9994 | -14.375 | 211201.9994 | 8.125 | 251837.9994 | 30.5 | 238537.9994
40.5 | 211201.9994 | 43 | 211201.9994 | 46 | 211201.9994 | 49 | 211201.9994 | 51.5 | 211201.9994 | 71 | 211201.9994 | 74 | 211201.9994 | 76.5 | 211201.9994 | 79.5 | 211201.9994 | 99 | 211201.9994 | 102 | 105550.9988 | 104.5 | 211201.9994 | 107.5 | 246937.9994 | 110.5 | 249537.9994 | 113 | 259037.9994 | 116 | 252737.9994 | 124.5 | 211201.9994 | 127 | 211201.9994 | 130 | 254737.9994 | 133 | 254937.9994 | 135.5 | 258337.9994 | 138.5 | 220637.9994 | 146.5 | 211201.9994 | 155.5 | 258737.9994 | 158 | 236737.9994 | 160.5 | 211201.9994 | 163.5 | 211201.9994 | 172 | 244137.9994 | 174.5 | 245037.9994 | 177.5 | 211201.9994 | 180.5 | 211201.9994 | 183 | 247537.9994 | 186 | 255337.9994 | 189 | 260137.9994 | 197 | 252637.9994 | 200 | 251837.9994 | 208.5 | 258637.9994 | 211 | 238537.9994 | 214 | 260737.9994 | 216.5 | 255737.9994 | 219.5 | 257937.9994 | 222.5 | 211201.9994 | 58.5 | 211201.9994 | 64.125 | 211201.9994 | 114.5 | 105550.9988 | 120.25 | 246937.9994 | 125.75 | 220637.9994 | 165 | 236737.9994 | 170.5 | 211201.9994 | 193 | 251837.9994 | 215.25 | 238537.9994
225.5 | 211201.9994 | 228 | 211201.9994 | 230.5 | 211201.9994 | 233.5 | 211201.9994 | 236.5 | 211201.9994 | 256 | 211201.9994 | 258.5 | 211201.9994 | 261.5 | 211201.9994 | 264.5 | 211201.9994 | 284 | 211201.9994 | 286.5 | 211201.9994 | 289.5 | 211201.9994 | 292.5 | 246937.9994 | 295 | 249537.9994 | 298 | 259037.9994 | 300.5 | 252737.9994 | 309 | 211201.9994 | 312 | 211201.9994 | 314.5 | 254737.9994 | 317.5 | 254937.9994 | 320.5 | 258337.9994 | 323 | 220637.9994 | 331.5 | 211201.9994 | 340 | 258737.9994 | 342.5 | 236737.9994 | 345.5 | 211201.9994 | 348.5 | 211201.9994 | 356.5 | 244137.9994 | 359.5 | 245037.9994 | 362.5 | 211201.9994 | 365 | 211201.9994 | 368 | 247537.9994 | 370.5 | 255337.9994 | 373.5 | 260137.9994 | 382 | 252637.9994 | 384.5 | 251837.9994 | 393 | 258637.9994 | 396 | 238537.9994 | 398.5 | 260737.9994 | 401.5 | 255737.9994 | 404.5 | 257937.9994 | 407 | 211201.9994 | 243.25 | 211201.9994 | 249 | 211201.9994 | 299.25 | 211201.9994 | 304.875 | 246937.9994 | 310.5 | 220637.9994 | 349.625 | 236737.9994 | 355.375 | 211201.9994 | 377.625 | 251837.9994 | 400.125 | 238537.9994
410 | 211201.9994 | 412.5 | 211201.9994 | 415.5 | 211201.9994 | 418.5 | 211201.9994 | 421 | 211201.9994 | 440.5 | 211201.9994 | 443.5 | 211201.9994 | 446.5 | 211201.9994 | 449 | 211201.9994 | 469 | 211201.9994 | 471.5 | 211201.9994 | 474.5 | 211201.9994 | 477 | 246937.9994 | 480 | 249537.9994 | 482.5 | 259037.9994 | 485.5 | 252737.9994 | 494 | 211201.9994 | 496.5 | 211201.9994 | 499.5 | 254737.9994 | 502.5 | 254937.9994 | 505 | 258337.9994 | 508 | 220637.9994 | 516.5 | 211201.9994 | 524.5 | 258737.9994 | 527.5 | 236737.9994 | 530.5 | 211201.9994 | 533 | 211201.9994 | 541.5 | 244137.9994 | 544.5 | 245037.9994 | 547 | 211201.9994 | 550 | 211201.9994 | 552.5 | 247537.9994 | 555.5 | 255337.9994 | 558.5 | 260137.9994 | 566.5 | 252637.9994 | 569.5 | 251837.9994 | 578 | 258637.9994 | 580.5 | 119218.9988 | 583.5 | 260737.9994 | 586.5 | 255737.9994 | 589 | 257937.9994 | 592 | 211201.9994 | 428 | 211201.9994 | 433.75 | 211201.9994 | 484.125 | 211201.9994 | 489.75 | 246937.9994 | 495.25 | 220637.9994 | 534.5 | 236737.9994 | 540.125 | 211201.9994 | 562.5 | 251837.9994 | 584.875 | 119218.9988
594.5 | 211201.9994 | 597.5 | 211201.9994 | 600.5 | 211201.9994 | 603 | 211201.9994 | 606 | 211201.9994 | 625.5 | 211201.9994 | 628.5 | 211201.9994 | 631 | 211201.9994 | 634 | 211201.9994 | 653.5 | 211201.9994 | 656.5 | 211201.9994 | 658 | 211201.9994 | 662 | 246937.9994 | 664.5 | 249537.9994 | 667.5 | 259037.9994 | 670.5 | 252737.9994 | 678.5 | 211201.9994 | 681.5 | 211201.9994 | 684.5 | 254737.9994 | 687 | 254937.9994 | 690 | 258337.9994 | 692.5 | 220637.9994 | 701 | 211201.9994 | 709.5 | 258737.9994 | 712.5 | 236737.9994 | 715 | 105550.9988 | 718 | 211002.0947 | 726.5 | 243838.1638 | 728 | 245037.9994 | 731.5 | 211201.9994 | 734.5 | 211201.9994 | 737.5 | 247537.9994 | 740.5 | 255337.9994 | 743 | 260137.9994 | 751.5 | 252637.9994 | 754.5 | 251837.9994 | 762.5 | 258637.9994 | 765.5 | 238537.9994 | 768.5 | 260737.9994 | 771 | 255737.9994 | 774 | 257937.9994 | 776.5 | 211201.9994 | 613 | 211201.9994 | 618.5 | 211201.9994 | 668.625 | 211201.9994 | 674.5 | 246937.9994 | 680.125 | 220637.9994 | 719.125 | 236737.9994 | 724.75 | 105550.9988 | 747.375 | 251837.9994 | 769.75 | 238537.9994
779.5 | 211201.9994 | 782.5 | 211201.9994 | 785 | 211201.9994 | 788 | 211201.9994 | 790.5 | 211201.9994 | 810.5 | 211201.9994 | 813 | 211201.9994 | 816 | 211201.9994 | 818.5 | 211201.9994 | 838.5 | 211201.9994 | 841 | 211201.9994 | 844 | 211201.9994 | 846.5 | 246937.9994 | 849.5 | 249537.9994 | 852.5 | 259037.9994 | 855 | 252737.9994 | 863.5 | 211201.9994 | 866.5 | 211201.9994 | 869 | 254737.9994 | 872 | 254937.9994 | 874.5 | 129118.9988 | 877.5 | 220637.9994 | 885.5 | 211201.9994 | 894.5 | 258737.9994 | 897 | 236737.9994 | 900 | 211201.9994 | 902.5 | 211201.9994 | 911 | 244137.9994 | 914 | 245037.9994 | 916.5 | 211201.9994 | 919.5 | 211201.9994 | 922 | 16.4287 | 925 | 6180.4313 | 928 | 12555.2991 | 936.5 | 4.289 | 939 | 9.2546 | 947 | 45.6064 | 950 | 14765.2528 | 953 | 64909.7205 | 956 | 127469.3322 | 958.5 | 257338.4263 | 961.5 | 52725.4976 | 797.75 | 211201.9994 | 803.25 | 211201.9994 | 853.75 | 211201.9994 | 859.25 | 246937.9994 | 864.875 | 129118.9988 | 904.125 | 236737.9994 | 909.625 | 211201.9994 | 932.125 | 4.289 | 954.375 | 14765.2528
964 | 3.3488 | 967 | 13927.2643 | 969.5 | 52600.5828 | 972.5 | 210702.3313 | 975.5 | 206905.9754 | 995 | 5769.478 | 998 | 4813.9737 | 1000.5 | 1357.1666 | 1003.5 | 52725.4976 | 1023 | 105550.9988 | 1026 | 105550.9988 | 1028.5 | 105550.9988 | 1031.5 | 123418.9988 | 1034.5 | 49827.5969 | 1037 | 43089.663 | 1040 | 50467.5969 | 1048 | 70333.9982 | 1051 | 70333.9982 | 1053.5 | 127318.9988 | 1056.5 | 50907.5969 | 1059.5 | 42972.9963 | 1062 | 36689.663 | 1070.5 | 19.2207 | 1079 | 43437.038 | 1082 | 60075.807 | 1084.5 | 42160.3969 | 1087.5 | 42160.3969 | 1096 | 40606.3297 | 1098.5 | 48927.5969 | 1101.5 | 42160.3969 | 1104 | 42160.3969 | 1107 | 3.3106 | 1109.5 | 28.6609 | 1112.5 | 9.4483 | 1121 | 6.439 | 1124 | 3.7757 | 1132 | 24.8379 | 1135 | 33154.4307 | 1137.5 | 1535.0518 | 1140.5 | 38362.8782 | 1143.5 | 17204.5979 | 1146.5 | 42160.3969 | 982.375 | 4813.9737 | 988 | 1357.1666 | 1038.375 | 70333.9982 | 1044 | 49827.5969 | 1049.625 | 36689.663 | 1088.875 | 40606.3297 | 1094.375 | 42160.3969 | 1116.75 | 3.7757 | 1139.125 | 1535.0518
1149 | 25.4123 | 1151.5 | 13940.4598 | 1154.5 | 52550.6775 | 1157.5 | 105101.6389 | 1160 | 210303.1358 | 1179.5 | 52725.4976 | 1182.5 | 42160.3969 | 1185.5 | 42160.3969 | 1188.5 | 42160.3969 | 1208 | 195.7535 | 1210.5 | 26225.4214 | 1213.5 | 105201.4023 | 1216 | 1726.247 | 1219 | 41506.3297 | 1222 | 43089.663 | 1224.5 | 36019.71 | 1233 | 42160.3969 | 1235.5 | 42160.3969 | 1238.5 | 42372.9963 | 1241.5 | 36333.9957 | 1244 | 32204.7451 | 1247 | 27492.2451 | 1255.5 | 0.082564 | 1264 | 1722.0077 | 1266.5 | 20823.9192 | 1269.5 | 42160.3969 | 1272.5 | 42160.3969 | 1280.5 | 48747.5969 | 1283.5 | 48927.5969 | 1286 | 42160.3969 | 1289 | 42160.3969 | 1291.5 | 4.2166 | 1294.5 | 9.8027 | 1297.5 | 36.9065 | 1305.5 | 26.3716 | 1308.5 | 0.87367 | 1317 | 8.8092 | 1319.5 | 27879.4636 | 1322.5 | 46366.7864 | 1325.5 | 11216.0369 | 1328 | 1834.4385 | 1331 | 42160.3969 | 1167 | 13940.4598 | 1172.875 | 42160.3969 | 1223.125 | 26225.4214 | 1228.75 | 1726.247 | 1234.375 | 27492.2451 | 1273.625 | 1722.0077 | 1279.25 | 42160.3969 | 1301.5 | 0.87367 | 1323.875 | 1834.4385
1333.5 | 78.6283 | 1336.5 | 25740.0028 | 1339.5 | 102708.4543 | 1342 | 210203.4198 | 1345 | 52725.4976 | 1364.5 | 42160.3969 | 1367 | 52725.4976 | 1370.5 | 52725.4976 | 1373 | 52725.4976 | 1392.5 | 3.7615 | 1395.5 | 15678.6143 | 1398.5 | 50604.3789 | 1401 | 10205.3032 | 1403.5 | 28165.5968 | 1406.5 | 2391.648 | 1409.5 | 2648.183 | 1418 | 1931.6865 | 1420.5 | 1838.4839 | 1423.5 | 1681.9966 | 1426 | 1600.1618 | 1429 | 1694.6204 | 1431.5 | 1411.815 | 1440 | 10.9428 | 1448.5 | 4727.0163 | 1451.5 | 47267.5969 | 1454 | 210402.8992 | 1457 | 52725.4976 | 1465.5 | 48747.5969 | 1468 | 48927.5969 | 1471 | 42160.3969 | 1473.5 | 52725.4976 | 1476.5 | 30.2925 | 1479.5 | 10.692 | 1482 | 38.0231 | 1490.5 | 0.88064 | 1493.5 | 12.8067 | 1501.5 | 0.85292 | 1504.5 | 1534.7775 | 1507.5 | 34871.0274 | 1510 | 42255.2562 | 1513 | 58923.6021 | 1515.5 | 42160.3969 | 1351.875 | 25740.0028 | 1357.625 | 52725.4976 | 1408.125 | 1838.4839 | 1413.5 | 1600.1618 | 1419.125 | 1411.815 | 1458.375 | 4727.0163 | 1463.875 | 42160.3969 | 1486.375 | 0.88064 | 1508.75 | 1534.7775
1518.5 | 54.0917 | 1521.5 | 24358.4102 | 1524.5 | 98417.4945 | 1527 | 210402.8992 | 1529.5 | 52725.4976 | 1549.5 | 52725.4976 | 1552 | 52725.4976 | 1555 | 52725.4976 | 1557.5 | 52725.4976 | 1577.5 | 16.0824 | 1580 | 16702.948 | 1583 | 49755.9871 | 1586 | 3486.2768 | 1588.5 | 5975.584 | 1591.5 | 2006.7379 | 1594.5 | 1732.0752 | 1602.5 | 1347.1848 | 1605.5 | 1500.6921 | 1608 | 1364.48 | 1611 | 1357.2532 | 1613.5 | 1772.6549 | 1616.5 | 1262.4813 | 1625 | 20.8035 | 1633.5 | 49261.0652 | 1636 | 8701.3439 | 1639 | 52725.4976 | 1641.5 | 52725.4976 | 1650.5 | 60959.4976 | 1653 | 61184.4976 | 1655.5 | 42160.3969 | 1658.5 | 52725.4976 | 1661.5 | 11.6353 | 1664.5 | 4.6088 | 1667 | 6.1491 | 1675.5 | 9.7542 | 1678.5 | 6.3773 | 1686.5 | 0.93249 | 1689.5 | 7222.8348 | 1692.5 | 57749.3043 | 1695 | 1534.9942 | 1698 | 1535.0198 | 1700.5 | 52725.4976 | 1536.875 | 24358.4102 | 1542.25 | 52725.4976 | 1592.75 | 1347.1848 | 1598.375 | 1357.2532 | 1604 | 1262.4813 | 1643.25 | 8701.3439 | 1648.625 | 42160.3969 | 1671.375 | 4.6088 | 1693.75 | 1534.9942
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 44 |  |  | 2006-08-21 | 12:53
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-138.7 | 211202 |  | -116.4 | 211202 | -88.3333 | 211202 | -72.8889 | 211202 | -58.5 | 211202 | -49.7778 | 211202 | -25.8 | 246938 | -20.1 | 247538 | -7.8333 | 238538 | -4.7222 | 220638 | 12.9 | 211202 | 15 | 211202 | -138.7 | 211202 | -88.3333 | 211202 | -58.5 | 211202 | -51.7806 | 211202 | -43.4444 | 211202 | -14.6139 | 220638 | -30.2083 | 211202 | -20.0944 | 211202 | 3.8361 | 211202 | -127.55 | 211202 | -80.6111 | 211202 | -54.1389 | 211202 | -22.95 | 246938 | -6.2778 | 220638 | 13.95 | 211202
46 | 211202 |  | 68.3 | 211202 | 96.2778 | 105551 | 111.9444 | 211202 | 126.2222 | 211202 | 134.8333 | 211202 | 159.1 | 246938 | 164.7 | 247538 | 176.9444 | 238538 | 180.0556 | 220638 | 197.6 | 211202 | 200 | 211202 | 46 | 105551 | 96.2778 | 105551 | 126.2222 | 211202 | 133.0056 | 105551 | 141.3056 | 105551 | 170.2 | 220638 | 154.5139 | 211202 | 164.6639 | 211202 | 188.65 | 211202 | 57.15 | 211202 | 104.1111 | 105551 | 130.5278 | 211202 | 161.9 | 246938 | 178.5 | 220638 | 198.8 | 211202
230.8 | 211202 |  | 253.2 | 211202 | 281.1111 | 211202 | 296.6111 | 105551 | 310.9444 | 211202 | 319.7222 | 211202 | 343.8 | 246938 | 349.4 | 247538 | 361.6667 | 238538 | 364.7222 | 220638 | 382.5 | 105551 | 384.7 | 211202 | 230.8 | 105551 | 281.1111 | 105551 | 310.9444 | 105551 | 317.7306 | 105551 | 326.0278 | 105551 | 354.8972 | 220638 | 339.2639 | 211202 | 349.4667 | 105551 | 373.3972 | 105551 | 242 | 211202 | 288.8611 | 105551 | 315.3333 | 211202 | 346.6 | 246938 | 363.1944 | 220638 | 383.6 | 105551
415.5 | 211202 |  | 437.9 | 211202 | 465.8889 | 211202 | 481.5 | 211202 | 495.8333 | 211202 | 504.5 | 211202 | 528.6 | 246938 | 534.2 | 247538 | 546.3889 | 119219 | 549.6667 | 220638 | 567.3 | 211202 | 569.5 | 211202 | 415.5 | 211202 | 465.8889 | 119219 | 495.8333 | 119219 | 502.5472 | 211202 | 510.8611 | 119219 | 539.7139 | 119219 | 524.0972 | 119219 | 534.2833 | 211202 | 558.2139 | 119219 | 426.7 | 211202 | 473.6944 | 211202 | 500.1667 | 211202 | 531.4 | 246938 | 548.0278 | 119219 | 568.4 | 211202
600.3 | 211202 |  | 622.7 | 211202 | 650.6111 | 211202 | 666.2778 | 211202 | 680.5556 | 105551 | 689 | 211202 | 713.5 | 246938 | 719 | 247538 | 731.3333 | 122019 | 734.2778 | 220638 | 751.9 | 211202 | 754.3 | 211202 | 600.3 | 105551 | 650.6111 | 122019 | 680.5556 | 105551 | 687.3472 | 211202 | 695.625 | 122019 | 724.5278 | 122019 | 708.7917 | 105551 | 718.9389 | 105551 | 742.9528 | 122019 | 611.5 | 211202 | 658.4444 | 211202 | 684.7778 | 105551 | 716.25 | 246938 | 732.8056 | 122019 | 753.1 | 211202
785.1 | 211202 |  | 807.5 | 211202 | 835.5556 | 211202 | 851.0556 | 129119 | 865.3333 | 211202 | 874 | 211202 | 898.1 | 24.2056 | 903.8 | 5.7481 | 916 | 445.5254 | 919.1111 | 309.4385 | 936.8 | 52725.5 | 939 | 70334 | 785.1 | 129119 | 835.5556 | 5.7481 | 865.3333 | 309.4385 | 872.1278 | 5.7481 | 880.4306 | 309.4385 | 909.2528 | 5.7481 | 893.6111 | 309.4385 | 903.7833 | 52725.5 | 927.7278 | 309.4385 | 796.3 | 211202 | 843.3056 | 129119 | 869.6667 | 211202 | 900.95 | 5.7481 | 917.5556 | 309.4385 | 937.9 | 52725.5
969.7 | 5180.1727 |  | 992.2 | 1357.2552 | 1020.2778 | 43089.6667 | 1035.6667 | 2876.0845 | 1050.0556 | 3320.0827 | 1058.7778 | 28179.2309 | 1082.8 | 0.64692 | 1088.6 | 0.66585 | 1100.7222 | 0.63219 | 1103.8889 | 0.63341 | 1121.6 | 39673 | 1123.8 | 42160.4 | 969.7 | 1357.2552 | 1020.2778 | 0.63219 | 1050.0556 | 0.63219 | 1056.8361 | 0.64692 | 1065.1389 | 0.63219 | 1094.0028 | 0.63219 | 1078.3611 | 0.63219 | 1088.5583 | 3320.0827 | 1112.5028 | 0.63219 | 980.95 | 1357.2552 | 1027.9722 | 2876.0845 | 1054.4167 | 3320.0827 | 1085.7 | 0.64692 | 1102.3056 | 0.63219 | 1122.7 | 39673
1154.5 | 21109.7439 |  | 1177 | 4927.3018 | 1204.9444 | 1691.4037 | 1220.5 | 4049.4907 | 1234.9444 | 1.0317 | 1243.5556 | 1.1155 | 1267.6 | 0.70542 | 1273.2 | 0.65441 | 1285.5 | 0.67131 | 1288.6667 | 0.65207 | 1306.3 | 42160.4 | 1308.6 | 42160.4 | 1154.5 | 1.0317 | 1204.9444 | 0.65207 | 1234.9444 | 0.65207 | 1241.5611 | 0.65441 | 1249.9028 | 0.65207 | 1278.7417 | 0.65207 | 1263.1667 | 0.65207 | 1273.35 | 1.0317 | 1297.2667 | 0.65207 | 1165.75 | 4927.3018 | 1212.7222 | 1691.4037 | 1239.25 | 1.0317 | 1270.4 | 0.65441 | 1287.0833 | 0.65207 | 1307.45 | 42160.4
1339.3 | 5118.0554 |  | 1361.7 | 6785.5372 | 1389.7778 | 58.8736 | 1405.2778 | 65.4459 | 1419.6667 | 103.0179 | 1428.3333 | 131.1123 | 1452.5 | 9.3615 | 1458 | 0.64641 | 1470.3333 | 0.63612 | 1473.3889 | 0.69643 | 1491 | 42160.4 | 1493.3 | 51507.6 | 1339.3 | 58.8736 | 1389.7778 | 0.63612 | 1419.6667 | 0.63612 | 1426.3889 | 0.64641 | 1434.6944 | 0.63612 | 1463.5556 | 0.63612 | 1447.9306 | 0.63612 | 1458.075 | 103.0179 | 1482.0056 | 0.63612 | 1350.5 | 5118.0554 | 1397.5278 | 58.8736 | 1424 | 103.0179 | 1455.25 | 0.64641 | 1471.8611 | 0.63612 | 1492.15 | 42160.4
1524.2 | 2577.8349 |  | 1546.5 | 32832.3157 | 1574.6667 | 1263.2387 | 1590.1111 | 974.5823 | 1604.3889 | 6326.3987 | 1613.1111 | 7033.7148 | 1637.4 | 1.4953 | 1643 | 2.5639 | 1655.2778 | 0.63711 | 1658.3333 | 0.6391 | 1675.9 | 47627.6 | 1678.2 | 51507.6 | 1524.2 | 974.5823 | 1574.6667 | 0.63711 | 1604.3889 | 0.63711 | 1611.2944 | 1.4953 | 1619.5972 | 0.63711 | 1648.5028 | 0.63711 | 1632.7778 | 0.63711 | 1642.9 | 6326.3987 | 1666.9278 | 0.63711 | 1535.35 | 2577.8349 | 1582.3889 | 974.5823 | 1608.75 | 6326.3987 | 1640.2 | 1.4953 | 1656.8056 | 0.63711 | 1677.05 | 47627.6
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38950.5375 | 1 | 0 | 38950.5375 | 1 | 0 |  | 37.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5396 | 1 | 0 | 38950.5396 | 1 | 0 |  | 222.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5417 | 1 | 0 | 38950.5417 | 1 | 0 |  | 407 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5439 | 1 | 0 | 38950.5439 | 1 | 0 |  | 592 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.546 | 1 | 0 | 38950.546 | 1 | 0 |  | 776.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5481 | 4 | 0 | 38950.5482 | 3 | 0 |  | 961.5 | 1106.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38950.5503 | 5 | 0 | 38950.5503 | 5 | 0 |  | 1146.5 | 1291.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5524 | 5 | 0 | 38950.5524 | 5 | 0 |  | 1331 | 1476 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5546 | 5 | 0 | 38950.5546 | 4 | 0 |  | 1515.5 | 1660.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5567 | 4 | 0 | 38950.5567 | 4 | 0 |  | 1700.5 | 1845.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## E10-F12
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 157.5324 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38950.5374 | 1 | 0 | 38950.5374 | 1 | 0 |  | 34.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38950.5396 | 1 | 0 | 38950.5396 | 1 | 0 |  | 219.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38950.5417 | 1 | 0 | 38950.5417 | 1 | 0 |  | 404.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38950.5438 | 1 | 0 | 38950.5439 | 1 | 0 |  | 589 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38950.546 | 1 | 0 | 38950.546 | 1 | 0 |  | 774 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
38950.5481 | 4 | 1 | 38950.5481 | 3 | 1 |  | 958.5 | 1103.5 | 0.2442 | 0.06105 | 0.18315 | 0.06105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0018315 | 0.001221 | 85901.5397 | 128944.0534 | 257338.4263
38950.5503 | 2407 | 1 | 38950.5503 | 5 | 0 |  | 1143.5 | 1288.5 | 146.9475 | 0.06105 | 0.30525 | 0 | 1.4695 | 0.0006105 | 0.0030525 | 0 | 1.4689 | 0.0030525 | 7.2062 | 51507.6 | 17204.5979
38950.5524 | 2561 | 1 | 38950.5524 | 5 | 0 |  | 1328 | 1473 | 156.3492 | 0.06105 | 0.30525 | 0 | 1.5635 | 0.0006105 | 0.0030525 | 0 | 1.5629 | 0.0030525 | 0.75703 | 51507.6 | 1834.4385
38950.5545 | 1989 | 1 | 38950.5545 | 5 | 0 |  | 1513 | 1658 | 121.4286 | 0.06105 | 0.30525 | 0 | 1.2143 | 0.0006105 | 0.0030525 | 0 | 1.2137 | 0.0030525 | 29.7475 | 51507.6 | 58923.6021
38950.5567 | 2564 | 1 | 38950.5567 | 5 | 0 |  | 1698 | 1843 | 156.5324 | 0.06105 | 0.30525 | 0 | 1.5653 | 0.0006105 | 0.0030525 | 0 | 1.5647 | 0.0030525 | 0.6391 | 51507.6 | 1535.0198

## E10-F11
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 156.1893 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38950.5374 | 1 | 0 | 38950.5374 | 1 | 0 |  | 32 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38950.5395 | 1 | 0 | 38950.5395 | 1 | 0 |  | 216.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38950.5417 | 1 | 0 | 38950.5417 | 1 | 0 |  | 401.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38950.5438 | 1 | 0 | 38950.5438 | 1 | 0 |  | 586.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38950.5459 | 1 | 0 | 38950.546 | 1 | 0 |  | 771 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38950.5481 | 4 | 2 | 38950.5481 | 4 | 1 |  | 956 | 1101 | 0.2442 | 0.1221 | 0.2442 | 0.06105 | 0.002442 | 0.001221 | 0.002442 | 0.0006105 | 0.001221 | 0.0018315 | 127869.1372 | 85168.2019 | 127469.3322
38950.5502 | 2173 | 1 | 38950.5502 | 5 | 0 |  | 1140.5 | 1285.5 | 132.6618 | 0.06105 | 0.30525 | 0 | 1.3266 | 0.0006105 | 0.0030525 | 0 | 1.326 | 0.0030525 | 17.7431 | 51067.6 | 38362.8782
38950.5524 | 2445 | 1 | 38950.5524 | 5 | 0 |  | 1325.5 | 1470.5 | 149.2674 | 0.06105 | 0.30525 | 0 | 1.4927 | 0.0006105 | 0.0030525 | 0 | 1.4921 | 0.0030525 | 4.6391 | 51067.6 | 11216.0369
38950.5545 | 2134 | 1 | 38950.5545 | 5 | 0 |  | 1510 | 1655 | 130.2808 | 0.06105 | 0.30525 | 0 | 1.3028 | 0.0006105 | 0.0030525 | 0 | 1.3022 | 0.0030525 | 19.8959 | 51067.6 | 42255.2562
38950.5566 | 2542 | 1 | 38950.5567 | 5 | 0 |  | 1695 | 1840 | 155.1893 | 0.06105 | 0.30525 | 0 | 1.5519 | 0.0006105 | 0.0030525 | 0 | 1.5513 | 0.0030525 | 0.64463 | 51067.6 | 1534.9942

## E9-F12
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 159.2418 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38950.5373 | 1 | 0 | 38950.5374 | 1 | 0 |  | 29 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
38950.5395 | 1 | 0 | 38950.5395 | 1 | 0 |  | 214 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
38950.5416 | 1 | 0 | 38950.5416 | 1 | 0 |  | 398.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
38950.5438 | 1 | 0 | 38950.5438 | 1 | 0 |  | 583.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
38950.5459 | 1 | 0 | 38950.5459 | 1 | 0 |  | 768.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260738 | 260738 | 260737.9994
38950.548 | 5 | 4 | 38950.5481 | 5 | 2 |  | 953 | 1098 | 0.30525 | 0.2442 | 0.30525 | 0.1221 | 0.0030525 | 0.002442 | 0.0030525 | 0.001221 | 0.0006105 | 0.0018315 | 261543.2482 | 86801.4588 | 64909.7205
38950.5502 | 2592 | 1 | 38950.5502 | 5 | 0 |  | 1137.5 | 1282.5 | 158.2418 | 0.06105 | 0.30525 | 0 | 1.5824 | 0.0006105 | 0.0030525 | 0 | 1.5818 | 0.0030525 | 0.63219 | 52067.6 | 1535.0518
38950.5523 | 2143 | 1 | 38950.5523 | 4 | 0 |  | 1322.5 | 1467.5 | 130.8303 | 0.06105 | 0.2442 | 0 | 1.3083 | 0.0006105 | 0.002442 | 0 | 1.3077 | 0.002442 | 21.7264 | 65109.5 | 46366.7864
38950.5545 | 2258 | 1 | 38950.5545 | 5 | 0 |  | 1507.5 | 1652.5 | 137.851 | 0.06105 | 0.30525 | 0 | 1.3785 | 0.0006105 | 0.0030525 | 0 | 1.3779 | 0.0030525 | 15.5242 | 52067.6 | 34871.0274
38950.5566 | 2029 | 1 | 38950.5566 | 4 | 0 |  | 1692.5 | 1837.5 | 123.8706 | 0.06105 | 0.2442 | 0 | 1.2387 | 0.0006105 | 0.002442 | 0 | 1.2381 | 0.002442 | 28.5691 | 65109.5 | 57749.3043

## E9-F11
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 145.6886 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38950.5373 | 1 | 0 | 38950.5373 | 1 | 0 |  | 26.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38950.5395 | 1 | 0 | 38950.5395 | 1 | 0 |  | 211 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38950.5416 | 1 | 0 | 38950.5416 | 1 | 0 |  | 396 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38950.5437 | 2 | 0 | 38950.5437 | 1 | 0 |  | 580.5 | 725.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119219 | 238538 | 119218.9988
38950.5459 | 1 | 0 | 38950.5459 | 1 | 0 |  | 765.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238538 | 238538 | 238537.9994
38950.548 | 5 | 16 | 38950.548 | 5 | 8 |  | 950 | 1095 | 0.30525 | 0.9768 | 0.30525 | 0.4884 | 0.0030525 | 0.009768 | 0.0030525 | 0.004884 | 0.0067155 | 0.0018315 | 21688.1618 | 80367.4914 | 14765.2528
38950.5502 | 2053 | 1 | 38950.5502 | 6 | 0 |  | 1135 | 1280 | 125.3358 | 0.06105 | 0.3663 | 0 | 1.2534 | 0.0006105 | 0.003663 | 0 | 1.2527 | 0.003663 | 16.2466 | 39673 | 33154.4307
38950.5523 | 2106 | 1 | 38950.5523 | 5 | 0 |  | 1319.5 | 1464.5 | 128.5714 | 0.06105 | 0.30525 | 0 | 1.2857 | 0.0006105 | 0.0030525 | 0 | 1.2851 | 0.0030525 | 13.3197 | 47627.6 | 27879.4636
38950.5544 | 2370 | 1 | 38950.5544 | 5 | 0 |  | 1504.5 | 1649.5 | 144.6886 | 0.06105 | 0.30525 | 0 | 1.4469 | 0.0006105 | 0.0030525 | 0 | 1.4463 | 0.0030525 | 0.69143 | 47627.6 | 1534.7775
38950.5566 | 2313 | 1 | 38950.5566 | 5 | 0 |  | 1689.5 | 1834.5 | 141.2088 | 0.06105 | 0.30525 | 0 | 1.4121 | 0.0006105 | 0.0030525 | 0 | 1.4115 | 0.0030525 | 3.1739 | 47627.6 | 7222.8348

## E9-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 157.9597 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38950.5373 | 1 | 0 | 38950.5373 | 1 | 0 |  | 23.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38950.5394 | 1 | 0 | 38950.5394 | 1 | 0 |  | 208.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38950.5416 | 1 | 0 | 38950.5416 | 1 | 0 |  | 393 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38950.5437 | 1 | 0 | 38950.5437 | 1 | 0 |  | 578 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38950.5458 | 1 | 0 | 38950.5459 | 1 | 0 |  | 762.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
38950.548 | 1016 | 980 |  | 1018 | 510 |  | 947 | 1092 | 62.0269 | 59.8291 | 62.149 | 31.1355 | 0.62027 | 0.59829 | 0.62149 | 0.31136 | 0.021978 | 0.31013 | 445.5254 | 309.4385 | 45.6064
38950.5501 | 2052 | 0 | 38950.5501 | 2034 | 0 |  | 1132 | 1277 | 125.2747 | 0 | 124.1758 | 0 | 1.2527 | 0 | 1.2418 | 0 | 1.2527 | 1.2418 | 26.0906 | 27.2065 | 24.8379
38950.5523 | 2347 | 0 | 38950.5523 | 2336 | 1 |  | 1317 | 1462 | 143.2845 | 0 | 142.6129 | 0.06105 | 1.4328 | 0 | 1.4261 | 0.0006105 | 1.4328 | 1.4255 | 10.242 | 10.8086 | 8.8092
38950.5544 | 2569 | 0 | 38950.5544 | 2496 | 0 |  | 1501.5 | 1646.5 | 156.8376 | 0 | 152.381 | 0 | 1.5684 | 0 | 1.5238 | 0 | 1.5684 | 1.5238 | 0.71545 | 3.6611 | 0.85292
38950.5565 | 2571 | 0 | 38950.5566 | 2381 | 0 |  | 1686.5 | 1831.5 | 156.9597 | 0 | 145.3602 | 0 | 1.5696 | 0 | 1.4536 | 0 | 1.5696 | 1.4536 | 0.63711 | 8.6678 | 0.93249

## D8-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 153.8083 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38950.5372 | 1 | 0 | 38950.5372 | 1 | 0 |  | 15 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251838 | 251838 | 251837.9994
38950.5393 | 1 | 0 | 38950.5394 | 1 | 0 |  | 200 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251838 | 251838 | 251837.9994
38950.5415 | 1 | 0 | 38950.5415 | 1 | 0 |  | 384.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251838 | 251838 | 251837.9994
38950.5436 | 1 | 0 | 38950.5436 | 1 | 0 |  | 569.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251838 | 251838 | 251837.9994
38950.5458 | 1 | 0 | 38950.5458 | 1 | 0 |  | 754.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251838 | 251838 | 251837.9994
38950.5479 | 2277 | 0 | 38950.5479 | 6 | 0 |  | 939 | 1084 | 139.011 | 0 | 0.3663 | 0 | 1.3901 | 0 | 0.003663 | 0 | 1.3901 | 0.003663 | 10.6447 | 41889.6667 | 9.2546
38950.55 | 2394 | 0 | 38950.55 | 2048 | 0 |  | 1124 | 1269 | 146.1538 | 0 | 125.0305 | 0 | 1.4615 | 0 | 1.2503 | 0 | 1.4615 | 1.2503 | 5.2373 | 23.0166 | 3.7757
38950.5522 | 2503 | 0 | 38950.5522 | 2357 | 0 |  | 1308.5 | 1453.5 | 152.8083 | 0 | 143.895 | 0 | 1.5281 | 0 | 1.4389 | 0 | 1.5281 | 1.4389 | 0.65441 | 6.8893 | 0.87367
38950.5543 | 2207 | 0 | 38950.5543 | 2186 | 0 |  | 1493.5 | 1638.5 | 134.7375 | 0 | 133.4554 | 0 | 1.3474 | 0 | 1.3346 | 0 | 1.3474 | 1.3346 | 14.1541 | 15.2507 | 12.8067
38950.5564 | 2337 | 0 | 38950.5565 | 2108 | 0 |  | 1678.5 | 1823.5 | 142.674 | 0 | 128.6935 | 0 | 1.4267 | 0 | 1.2869 | 0 | 1.4267 | 1.2869 | 7.804 | 19.5152 | 6.3773

## D8-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 154.2967 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38950.5372 | 1 | 0 | 38950.5372 | 1 | 0 |  | 12.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38950.5393 | 1 | 0 | 38950.5393 | 1 | 0 |  | 197 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38950.5414 | 1 | 0 | 38950.5415 | 1 | 0 |  | 382 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38950.5436 | 1 | 0 | 38950.5436 | 1 | 0 |  | 566.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38950.5457 | 1 | 0 | 38950.5457 | 1 | 0 |  | 751.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252638 | 252638 | 252637.9994
38950.5479 | 2390 | 0 | 38950.5479 | 6 | 0 |  | 936.5 | 1081.5 | 145.9096 | 0 | 0.3663 | 0 | 1.4591 | 0 | 0.003663 | 0 | 1.4591 | 0.003663 | 5.7481 | 42023 | 4.289
38950.55 | 2343 | 0 | 38950.55 | 2367 | 0 |  | 1121 | 1266 | 143.0403 | 0 | 144.5055 | 0 | 1.4304 | 0 | 1.4451 | 0 | 1.4304 | 1.4451 | 7.8694 | 6.7757 | 6.439
38950.5521 | 1981 | 0 | 38950.5521 | 2120 | 0 |  | 1305.5 | 1450.5 | 120.9402 | 0 | 129.4261 | 0 | 1.2094 | 0 | 1.2943 | 0 | 1.2094 | 1.2943 | 27.581 | 19.216 | 26.3716
38950.5543 | 2511 | 0 | 38950.5543 | 2325 | 0 |  | 1490.5 | 1635.5 | 153.2967 | 0 | 141.9414 | 0 | 1.533 | 0 | 1.4194 | 0 | 1.533 | 1.4194 | 0.65233 | 8.7045 | 0.88064
38950.5564 | 2274 | 0 | 38950.5564 | 2055 | 0 |  | 1675.5 | 1820.5 | 138.8278 | 0 | 125.4579 | 0 | 1.3883 | 0 | 1.2546 | 0 | 1.3883 | 1.2546 | 11.1425 | 22.9869 | 9.7542

## D7-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 158.8755 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38950.5371 | 1 | 0 | 38950.5371 | 1 | 0 |  | 4 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38950.5392 | 1 | 0 | 38950.5392 | 1 | 0 |  | 189 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38950.5413 | 1 | 0 | 38950.5414 | 1 | 0 |  | 373.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38950.5435 | 1 | 0 | 38950.5435 | 1 | 0 |  | 558.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38950.5456 | 1 | 0 | 38950.5456 | 1 | 0 |  | 743 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38950.5478 | 2096 | 4 | 38950.5478 | 6 | 1 |  | 928 | 1073 | 127.9609 | 0.2442 | 0.3663 | 0.06105 | 1.2796 | 0.002442 | 0.003663 | 0.0006105 | 1.2772 | 0.0030525 | 24.2056 | 298874.9498 | 12555.2991
38950.5499 | 2347 | 0 | 38950.5499 | 2586 | 0 |  | 1112.5 | 1257.5 | 143.2845 | 0 | 157.8755 | 0 | 1.4328 | 0 | 1.5788 | 0 | 1.4328 | 1.5788 | 10.8811 | 0.63341 | 9.4483
38950.552 | 1885 | 0 | 38950.552 | 2577 | 1 |  | 1297.5 | 1442.5 | 115.0794 | 0 | 157.326 | 0.06105 | 1.1508 | 0 | 1.5733 | 0.0006105 | 1.1508 | 1.5726 | 38.0573 | 1.0241 | 36.9065
38950.5542 | 1870 | 0 | 38950.5542 | 2172 | 0 |  | 1482 | 1627 | 114.1636 | 0 | 132.6007 | 0 | 1.1416 | 0 | 1.326 | 0 | 1.1416 | 1.326 | 39.1647 | 19.8149 | 38.0231
38950.5563 | 2418 | 0 | 38950.5563 | 1993 | 0 |  | 1667 | 1812 | 147.619 | 0 | 121.6728 | 0 | 1.4762 | 0 | 1.2167 | 0 | 1.4762 | 1.2167 | 7.6253 | 30.576 | 6.1491

## D7-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 155.9451 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38950.537 | 1 | 0 | 38950.537 | 1 | 0 |  | 1 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38950.5392 | 1 | 0 | 38950.5392 | 1 | 0 |  | 186 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38950.5413 | 1 | 0 | 38950.5413 | 1 | 0 |  | 370.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38950.5434 | 1 | 0 | 38950.5435 | 1 | 0 |  | 555.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38950.5456 | 1 | 0 | 38950.5456 | 1 | 0 |  | 740.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255338 | 255338 | 255337.9994
38950.5477 | 1609 | 15 | 38950.5477 | 5 | 6 |  | 925 | 1070 | 98.2295 | 0.91575 | 0.30525 | 0.3663 | 0.9823 | 0.0091575 | 0.0030525 | 0.003663 | 0.97314 | 0.0006105 | 59.3067 | 27963.2106 | 6180.4313
38950.5499 | 1967 | 0 | 38950.5499 | 2172 | 0 |  | 1109.5 | 1254.5 | 120.0855 | 0 | 132.6007 | 0 | 1.2009 | 0 | 1.326 | 0 | 1.2009 | 1.326 | 29.8617 | 17.605 | 28.6609
38950.552 | 2297 | 0 | 38950.552 | 2499 | 0 |  | 1294.5 | 1439.5 | 140.232 | 0 | 152.5641 | 0 | 1.4023 | 0 | 1.5256 | 0 | 1.4023 | 1.5256 | 11.2051 | 2.2161 | 9.8027
38950.5541 | 2279 | 0 | 38950.5542 | 2524 | 0 |  | 1479.5 | 1624.5 | 139.1331 | 0 | 154.0904 | 0 | 1.3913 | 0 | 1.5409 | 0 | 1.3913 | 1.5409 | 12.0834 | 1.2036 | 10.692
38950.5563 | 2408 | 0 | 38950.5563 | 2538 | 0 |  | 1664.5 | 1809.5 | 147.0085 | 0 | 154.9451 | 0 | 1.4701 | 0 | 1.5495 | 0 | 1.4701 | 1.5495 | 6.0789 | 0.64539 | 4.6088

## D7-D8
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 151.1832 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38950.537 | 1 | 0 | 38950.537 | 1 | 0 |  | -1.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38950.5391 | 1 | 0 | 38950.5392 | 1 | 0 |  | 183 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38950.5413 | 1 | 0 | 38950.5413 | 1 | 0 |  | 368 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38950.5434 | 1 | 0 | 38950.5434 | 1 | 0 |  | 552.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38950.5456 | 1 | 0 | 38950.5456 | 1 | 0 |  | 737.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
38950.5477 | 1216 | 1063 | 38950.5477 | 1168 | 973 |  | 922 | 1067 | 74.2369 | 64.8962 | 71.3065 | 59.4017 | 0.74237 | 0.64896 | 0.71306 | 0.59402 | 0.093407 | 0.11905 | 8655.0627 | 767.8547 | 16.4287
38950.5498 | 2364 | 0 | 38950.5498 | 2460 | 0 |  | 1107 | 1252 | 144.3223 | 0 | 150.1832 | 0 | 1.4432 | 0 | 1.5018 | 0 | 1.4432 | 1.5018 | 4.7538 | 0.66585 | 3.3106
38950.552 | 2344 | 0 | 38950.552 | 1974 | 5 |  | 1291.5 | 1436.5 | 143.1013 | 0 | 120.5128 | 0.30525 | 1.431 | 0 | 1.2051 | 0.0030525 | 1.431 | 1.2021 | 5.6476 | 25.7684 | 4.2166
38950.5541 | 1884 | 0 | 38950.5541 | 2340 | 0 |  | 1476.5 | 1621.5 | 115.0183 | 0 | 142.8571 | 0 | 1.1502 | 0 | 1.4286 | 0 | 1.1502 | 1.4286 | 31.4427 | 5.8282 | 30.2925
38950.5563 | 2192 | 0 | 38950.5563 | 1904 | 0 |  | 1661.5 | 1806.5 | 133.8217 | 0 | 116.2393 | 0 | 1.3382 | 0 | 1.1624 | 0 | 1.3382 | 1.1624 | 12.9735 | 30.062 | 11.6353

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 44 |  |  | 2006-08-21 | 12:53
38950.5353 | 1 | 0 | 1 | TS/TP Mix | 7-C | Tray
38950.5375 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38950.5396 | 1 | 0 | 1
38950.5418 | 1 | 0 | 1
38950.5439 | 1 | 0 | 1
38950.546 | 1 | 0 | 1
38950.5482 | 1064 | 1014 | 1
38950.5503 | 923 | 945 | 1
38950.5525 | 779 | 742 | 1
38950.5546 | 862 | 811 | 1
1
38950.5354 | 1 | 0 | 2
38950.5375 | 1 | 0 | 2
38950.5396 | 1 | 0 | 2
38950.5418 | 1 | 0 | 2
38950.5439 | 1 | 0 | 2
38950.5461 | 1 | 0 | 2
38950.5482 | 1157 | 1112 | 2
38950.5503 | 958 | 986 | 2
38950.5525 | 734 | 700 | 2
38950.5546 | 808 | 774 | 2
2
38950.5354 | 1 | 0 | 3
38950.5375 | 1 | 0 | 3
38950.5397 | 1 | 0 | 3
38950.5418 | 1 | 0 | 3
38950.5439 | 1 | 0 | 3
38950.5461 | 1 | 0 | 3
38950.5482 | 5 | 15 | 3
38950.5503 | 5 | 15 | 3
38950.5525 | 5 | 8 | 3
38950.5546 | 5 | 8 | 3
3
38950.5354 | 1 | 0 | 4
38950.5375 | 1 | 0 | 4
38950.5397 | 1 | 0 | 4
38950.5418 | 1 | 0 | 4
38950.5439 | 1 | 0 | 4
38950.5461 | 1 | 0 | 4
38950.5482 | 2 | 6 | 4
38950.5504 | 5 | 7 | 4
38950.5525 | 45 | 4 | 4
38950.5546 | 156 | 4 | 4
4
38950.5354 | 1 | 0 | 5
38950.5375 | 1 | 0 | 5
38950.5397 | 1 | 0 | 5
38950.5418 | 1 | 0 | 5
38950.544 | 1 | 0 | 5
38950.5461 | 1 | 0 | 5
38950.5482 | 4 | 4 | 5
38950.5504 | 5 | 4 | 5
38950.5525 | 5 | 2 | 5
38950.5547 | 4 | 2 | 5
5
38950.5354 | 1 | 0 | 6
38950.5376 | 1 | 0 | 6
38950.5397 | 1 | 0 | 6
38950.5418 | 1 | 0 | 6
38950.544 | 1 | 0 | 6
38950.5461 | 1 | 0 | 6
38950.5483 | 2 | 3 | 6
38950.5504 | 5 | 3 | 6
38950.5525 | 53 | 1 | 6
38950.5547 | 140 | 1 | 6
6
38950.5354 | 1 | 0 | 7
38950.5397 | 1 | 0 | 7
38950.5419 | 1 | 0 | 7
38950.544 | 1 | 0 | 7
38950.5461 | 1 | 0 | 7
38950.5483 | 4 | 1 | 7
38950.5504 | 5 | 2 | 7
38950.5525 | 5 | 1 | 7
38950.5547 | 4 | 1 | 7
7
38950.5355 | 1 | 0 | 8
38950.5376 | 1 | 0 | 8
38950.5397 | 1 | 0 | 8
38950.5419 | 1 | 0 | 8
38950.544 | 1 | 0 | 8
38950.5462 | 1 | 0 | 8
38950.5483 | 2 | 1 | 8
38950.5504 | 5 | 1 | 8
38950.5526 | 5 | 0 | 8
38950.5547 | 5 | 1 | 8
8
38950.5355 | 1 | 0 | 9
38950.5376 | 1 | 0 | 9
38950.5398 | 1 | 0 | 9
38950.5419 | 1 | 0 | 9
38950.544 | 1 | 0 | 9
38950.5462 | 1 | 0 | 9
38950.5483 | 41 | 1 | 9
38950.5504 | 5 | 1 | 9
38950.5526 | 4 | 0 | 9
38950.5547 | 4 | 0 | 9
9
38950.5355 | 1 | 0 | 10
38950.5376 | 1 | 0 | 10
38950.5398 | 1 | 0 | 10
38950.5419 | 1 | 0 | 10
38950.5441 | 1 | 0 | 10
38950.5462 | 1 | 0 | 10
38950.5483 | 2 | 0 | 10
38950.5505 | 5 | 1 | 10
38950.5526 | 4 | 1 | 10
38950.5547 | 4 | 0 | 10
10
38950.5355 | 1 | 0 | 11
38950.5377 | 1 | 0 | 11
38950.5398 | 1 | 0 | 11
38950.5419 | 1 | 0 | 11
38950.5441 | 1 | 0 | 11
38950.5462 | 1 | 0 | 11
38950.5483 | 2 | 0 | 11
38950.5505 | 5 | 0 | 11
38950.5526 | 4 | 0 | 11
38950.5548 | 4 | 0 | 11
11
38950.5355 | 1 | 0 | 12
38950.5377 | 1 | 0 | 12
38950.5398 | 1 | 0 | 12
38950.5419 | 1 | 0 | 12
38950.5441 | 1 | 0 | 12
38950.5462 | 1 | 0 | 12
38950.5484 | 2296 | 0 | 12
38950.5505 | 2138 | 0 | 12
38950.5526 | 2382 | 0 | 12
38950.5548 | 2185 | 0 | 12
12
38950.5355 | 1 | 0 | 13
38950.5377 | 1 | 0 | 13
38950.5398 | 1 | 0 | 13
38950.542 | 1 | 0 | 13
38950.5441 | 2 | 0 | 13
38950.5462 | 1 | 0 | 13
38950.5484 | 5 | 0 | 13
38950.5505 | 5 | 0 | 13
38950.5527 | 5 | 0 | 13
38950.5548 | 5 | 0 | 13
13
38950.5356 | 1 | 0 | 14
38950.5377 | 1 | 0 | 14
38950.5398 | 1 | 0 | 14
38950.542 | 1 | 0 | 14
38950.5441 | 1 | 0 | 14
38950.5462 | 1 | 0 | 14
38950.5484 | 2383 | 0 | 14
38950.5505 | 2415 | 0 | 14
38950.5527 | 2524 | 0 | 14
38950.5548 | 2294 | 0 | 14
14
38950.5356 | 1 | 0 | 15
38950.5377 | 1 | 0 | 15
38950.5398 | 1 | 0 | 15
38950.542 | 1 | 0 | 15
38950.5441 | 1 | 0 | 15
38950.5463 | 1 | 0 | 15
38950.5484 | 5 | 1 | 15
38950.5505 | 5 | 0 | 15
38950.5527 | 5 | 0 | 15
38950.5548 | 5 | 0 | 15
15
38950.5356 | 1 | 0 | 16
38950.5377 | 1 | 0 | 16
38950.5399 | 1 | 0 | 16
38950.542 | 1 | 0 | 16
38950.5441 | 1 | 0 | 16
38950.5463 | 1 | 0 | 16
38950.5484 | 5 | 0 | 16
38950.5506 | 2148 | 0 | 16
38950.5527 | 2461 | 0 | 16
38950.5548 | 2575 | 0 | 16
16
38950.5356 | 1 | 0 | 17
38950.5377 | 1 | 0 | 17
38950.5399 | 1 | 0 | 17
38950.542 | 1 | 0 | 17
38950.5442 | 1 | 0 | 17
38950.5463 | 1 | 0 | 17
38950.5484 | 3 | 0 | 17
38950.5506 | 5 | 0 | 17
38950.5527 | 5 | 0 | 17
38950.5548 | 5 | 0 | 17
17
38950.5356 | 1 | 0 | 18
38950.5378 | 1 | 0 | 18
38950.5399 | 1 | 0 | 18
38950.542 | 1 | 0 | 18
38950.5442 | 1 | 0 | 18
38950.5463 | 1 | 0 | 18
38950.5484 | 3 | 0 | 18
38950.5506 | 2485 | 0 | 18
38950.5527 | 2113 | 0 | 18
38950.5549 | 2119 | 0 | 18
18
38950.5356 | 1 | 0 | 19
38950.5378 | 1 | 0 | 19
38950.5399 | 1 | 0 | 19
38950.542 | 1 | 0 | 19
38950.5442 | 1 | 0 | 19
38950.5463 | 1 | 0 | 19
38950.5485 | 3 | 0 | 19
38950.5506 | 5 | 0 | 19
38950.5527 | 5 | 0 | 19
38950.5549 | 5 | 0 | 19
19
38950.5357 | 1 | 0 | 20
38950.5378 | 1 | 0 | 20
38950.5399 | 1 | 0 | 20
38950.5421 | 1 | 0 | 20
38950.5442 | 1 | 0 | 20
38950.5463 | 1 | 0 | 20
38950.5485 | 2 | 0 | 20
38950.5506 | 5 | 0 | 20
38950.5528 | 5 | 0 | 20
38950.5549 | 4 | 0 | 20
20
38950.5357 | 1 | 0 | 21
38950.5378 | 1 | 0 | 21
38950.5399 | 1 | 0 | 21
38950.5421 | 1 | 0 | 21
38950.5442 | 1 | 0 | 21
38950.5464 | 1 | 0 | 21
38950.5485 | 15 | 0 | 21
38950.5506 | 4 | 0 | 21
38950.5528 | 5 | 0 | 21
38950.5549 | 5 | 0 | 21
21
38950.5357 | 1 | 0 | 22
38950.5378 | 1 | 0 | 22
38950.54 | 1 | 0 | 22
38950.5421 | 1 | 0 | 22
38950.5442 | 1 | 0 | 22
38950.5464 | 1 | 0 | 22
38950.5485 | 2 | 0 | 22
38950.5507 | 5 | 0 | 22
38950.5528 | 5 | 0 | 22
38950.5549 | 4 | 0 | 22
22
38950.5357 | 1 | 0 | 23
38950.5378 | 1 | 0 | 23
38950.54 | 1 | 0 | 23
38950.5421 | 1 | 0 | 23
38950.5443 | 1 | 0 | 23
38950.5464 | 1 | 0 | 23
38950.5485 | 36 | 0 | 23
38950.5507 | 4 | 0 | 23
38950.5528 | 5 | 0 | 23
38950.555 | 4 | 0 | 23
23
38950.5357 | 1 | 0 | 24
38950.5379 | 1 | 0 | 24
38950.54 | 1 | 0 | 24
38950.5421 | 1 | 0 | 24
38950.5443 | 1 | 0 | 24
38950.5464 | 1 | 0 | 24
38950.5486 | 2 | 0 | 24
38950.5507 | 5 | 0 | 24
38950.5528 | 75 | 0 | 24
38950.555 | 155 | 0 | 24
24
38950.5357 | 1 | 0 | 25
38950.5379 | 1 | 0 | 25
38950.54 | 1 | 0 | 25
38950.5422 | 1 | 0 | 25
38950.5443 | 1 | 0 | 25
38950.5464 | 1 | 0 | 25
38950.5486 | 43 | 0 | 25
38950.5507 | 5 | 0 | 25
38950.5528 | 4 | 0 | 25
38950.555 | 4 | 0 | 25
25
38950.5358 | 1 | 0 | 26
38950.5379 | 1 | 0 | 26
38950.54 | 1 | 0 | 26
38950.5422 | 1 | 0 | 26
38950.5443 | 1 | 0 | 26
38950.5464 | 1 | 0 | 26
38950.5486 | 71 | 0 | 26
38950.5507 | 4 | 0 | 26
38950.555 | 4 | 0 | 26
26
38950.5358 | 1 | 0 | 27
38950.5379 | 1 | 0 | 27
38950.54 | 1 | 0 | 27
38950.5422 | 1 | 0 | 27
38950.5443 | 1 | 0 | 27
38950.5465 | 1 | 0 | 27
38950.5486 | 145 | 0 | 27
38950.5507 | 5 | 0 | 27
38950.5529 | 4 | 0 | 27
38950.555 | 4 | 0 | 27
27
38950.5358 | 1 | 0 | 28
38950.5379 | 1 | 0 | 28
38950.5401 | 1 | 0 | 28
38950.5422 | 1 | 0 | 28
38950.5443 | 1 | 0 | 28
38950.5465 | 1 | 0 | 28
38950.5486 | 2 | 0 | 28
38950.5508 | 5 | 0 | 28
38950.5529 | 4 | 0 | 28
38950.555 | 4 | 0 | 28
28
38950.5358 | 1 | 0 | 29
38950.5379 | 1 | 0 | 29
38950.5401 | 1 | 0 | 29
38950.5422 | 1 | 0 | 29
38950.5444 | 1 | 0 | 29
38950.5465 | 1 | 0 | 29
38950.5486 | 4 | 0 | 29
38950.5508 | 5 | 0 | 29
38950.5529 | 4 | 0 | 29
38950.555 | 4 | 0 | 29
29
38950.5358 | 1 | 0 | 30
38950.538 | 1 | 0 | 30
38950.5401 | 1 | 0 | 30
38950.5422 | 1 | 0 | 30
38950.5444 | 1 | 0 | 30
38950.5465 | 1 | 0 | 30
38950.5486 | 2 | 0 | 30
38950.5508 | 4 | 0 | 30
38950.5529 | 4 | 0 | 30
38950.5551 | 5 | 0 | 30
30
38950.5358 | 1 | 0 | 31
38950.538 | 1 | 0 | 31
38950.5401 | 1 | 0 | 31
38950.5422 | 1 | 0 | 31
38950.5444 | 1 | 0 | 31
38950.5465 | 1 | 0 | 31
38950.5487 | 113 | 0 | 31
38950.5508 | 4 | 0 | 31
38950.5529 | 4 | 0 | 31
38950.5551 | 4 | 0 | 31
31
38950.5358 | 1 | 0 | 32
38950.538 | 1 | 0 | 32
38950.5401 | 1 | 0 | 32
38950.5423 | 1 | 0 | 32
38950.5444 | 1 | 0 | 32
38950.5465 | 1 | 0 | 32
38950.5487 | 2228 | 0 | 32
38950.5508 | 2520 | 0 | 32
38950.553 | 2044 | 0 | 32
38950.5551 | 2378 | 0 | 32
32
38950.5359 | 1 | 0 | 33
38950.538 | 1 | 0 | 33
38950.5401 | 1 | 0 | 33
38950.5423 | 1 | 0 | 33
38950.5444 | 1 | 0 | 33
38950.5466 | 1 | 0 | 33
38950.5487 | 170 | 0 | 33
38950.5508 | 5 | 0 | 33
38950.553 | 5 | 0 | 33
38950.5551 | 4 | 0 | 33
33
38950.5359 | 1 | 0 | 34
38950.538 | 1 | 0 | 34
38950.5402 | 1 | 0 | 34
38950.5423 | 1 | 0 | 34
38950.5444 | 1 | 0 | 34
38950.5466 | 1 | 0 | 34
38950.5487 | 2506 | 0 | 34
38950.5509 | 2022 | 0 | 34
38950.553 | 2226 | 0 | 34
38950.5551 | 2287 | 0 | 34
34
38950.5359 | 1 | 0 | 35
38950.538 | 1 | 0 | 35
38950.5402 | 1 | 0 | 35
38950.5423 | 1 | 0 | 35
38950.5445 | 1 | 0 | 35
38950.5466 | 1 | 0 | 35
38950.5487 | 6 | 0 | 35
38950.5509 | 5 | 0 | 35
38950.553 | 5 | 0 | 35
38950.5551 | 4 | 0 | 35
35
38950.5359 | 1 | 0 | 36
38950.5381 | 1 | 0 | 36
38950.5402 | 1 | 0 | 36
38950.5423 | 1 | 0 | 36
38950.5445 | 1 | 0 | 36
38950.5466 | 1 | 0 | 36
38950.5487 | 5 | 0 | 36
38950.5509 | 2496 | 0 | 36
38950.553 | 2284 | 0 | 36
38950.5552 | 2557 | 0 | 36
36
38950.5359 | 1 | 0 | 37
38950.5381 | 1 | 0 | 37
38950.5402 | 1 | 0 | 37
38950.5423 | 1 | 0 | 37
38950.5445 | 1 | 0 | 37
38950.5466 | 1 | 0 | 37
38950.5488 | 4 | 0 | 37
38950.5509 | 5 | 0 | 37
38950.553 | 5 | 0 | 37
38950.5552 | 5 | 0 | 37
37
38950.5359 | 1 | 0 | 38
38950.5381 | 2 | 0 | 38
38950.5402 | 1 | 0 | 38
38950.5424 | 1 | 0 | 38
38950.5445 | 1 | 0 | 38
38950.5466 | 1 | 0 | 38
38950.5488 | 7 | 0 | 38
38950.5509 | 2591 | 0 | 38
38950.5531 | 2296 | 0 | 38
38950.5552 | 2239 | 0 | 38
38
38950.536 | 1 | 0 | 39
38950.5381 | 1 | 0 | 39
38950.5402 | 1 | 0 | 39
38950.5424 | 1 | 0 | 39
38950.5445 | 1 | 0 | 39
38950.5467 | 1 | 0 | 39
38950.5488 | 3 | 0 | 39
38950.5509 | 5 | 0 | 39
38950.5531 | 5 | 0 | 39
38950.5552 | 5 | 0 | 39
39
38950.536 | 1 | 0 | 40
38950.5381 | 1 | 0 | 40
38950.5403 | 1 | 0 | 40
38950.5424 | 1 | 0 | 40
38950.5445 | 1 | 0 | 40
38950.5467 | 1 | 0 | 40
38950.5488 | 2 | 0 | 40
38950.5509 | 5 | 0 | 40
38950.5531 | 4 | 0 | 40
38950.5552 | 5 | 0 | 40
40
38950.536 | 1 | 0 | 41
38950.5381 | 1 | 0 | 41
38950.5403 | 1 | 0 | 41
38950.5424 | 1 | 0 | 41
38950.5445 | 1 | 0 | 41
38950.5467 | 1 | 0 | 41
38950.5488 | 2 | 0 | 41
38950.551 | 5 | 0 | 41
38950.5531 | 5 | 0 | 41
38950.5552 | 4 | 0 | 41
41
38950.536 | 1 | 0 | 42
38950.5381 | 1 | 0 | 42
38950.5403 | 1 | 0 | 42
38950.5424 | 1 | 0 | 42
38950.5446 | 1 | 0 | 42
38950.5467 | 1 | 0 | 42
38950.5488 | 2 | 0 | 42
38950.551 | 5 | 0 | 42
38950.5531 | 4 | 0 | 42
38950.5553 | 4 | 0 | 42
42
38950.536 | 1 | 0 | 43
38950.5382 | 1 | 0 | 43
38950.5403 | 1 | 0 | 43
38950.5446 | 1 | 0 | 43
38950.5467 | 1 | 0 | 43
38950.5489 | 2 | 0 | 43
38950.551 | 568 | 514 | 43
38950.5531 | 1114 | 1104 | 43
38950.5553 | 1227 | 1077 | 43
43
38950.536 | 1 | 0 | 44
38950.5382 | 1 | 0 | 44
38950.5403 | 2 | 0 | 44
38950.5425 | 1 | 0 | 44
38950.5446 | 1 | 0 | 44
38950.5467 | 1 | 0 | 44
38950.5489 | 2 | 0 | 44
38950.551 | 1096 | 1043 | 44
38950.5531 | 1020 | 959 | 44
38950.5553 | 1270 | 1133 | 44
44
38950.5361 | 1 | 0 | 45
38950.5382 | 2 | 0 | 45
38950.5403 | 1 | 0 | 45
38950.5425 | 1 | 0 | 45
38950.5446 | 1 | 0 | 45
38950.5467 | 1 | 0 | 45
38950.5489 | 2 | 0 | 45
38950.551 | 5 | 8 | 45
38950.5532 | 60 | 13 | 45
38950.5553 | 95 | 12 | 45
45
38950.5361 | 1 | 0 | 46
38950.5382 | 1 | 0 | 46
38950.5403 | 1 | 0 | 46
38950.5425 | 1 | 0 | 46
38950.5446 | 1 | 0 | 46
38950.5468 | 1 | 0 | 46
38950.5489 | 2 | 0 | 46
38950.551 | 5 | 3 | 46
38950.5532 | 4 | 6 | 46
38950.5553 | 4 | 6 | 46
46
38950.5361 | 1 | 0 | 47
38950.5382 | 1 | 0 | 47
38950.5404 | 1 | 0 | 47
38950.5425 | 1 | 0 | 47
38950.5446 | 1 | 0 | 47
38950.5468 | 1 | 0 | 47
38950.5489 | 2 | 0 | 47
38950.5511 | 4 | 2 | 47
38950.5532 | 83 | 4 | 47
38950.5553 | 117 | 4 | 47
47
38950.5361 | 1 | 0 | 48
38950.5382 | 1 | 0 | 48
38950.5404 | 1 | 0 | 48
38950.5425 | 1 | 0 | 48
38950.5468 | 1 | 0 | 48
38950.5489 | 2 | 0 | 48
38950.5511 | 4 | 1 | 48
38950.5532 | 4 | 2 | 48
38950.5554 | 4 | 2 | 48
48
38950.5361 | 1 | 0 | 49
38950.5383 | 1 | 0 | 49
38950.5404 | 1 | 0 | 49
38950.5425 | 1 | 0 | 49
38950.5447 | 1 | 0 | 49
38950.5468 | 1 | 0 | 49
38950.549 | 2 | 0 | 49
38950.5511 | 5 | 1 | 49
38950.5532 | 84 | 2 | 49
38950.5554 | 103 | 1 | 49
49
38950.5361 | 1 | 0 | 50
38950.5383 | 1 | 0 | 50
38950.5404 | 1 | 0 | 50
38950.5426 | 1 | 0 | 50
38950.5447 | 1 | 0 | 50
38950.5468 | 1 | 0 | 50
38950.549 | 2419 | 0 | 50
38950.5511 | 2454 | 1 | 50
38950.5533 | 2259 | 1 | 50
38950.5554 | 2434 | 1 | 50
50
38950.5362 | 1 | 0 | 51
38950.5383 | 1 | 0 | 51
38950.5404 | 1 | 0 | 51
38950.5426 | 1 | 0 | 51
38950.5447 | 1 | 0 | 51
38950.5469 | 1 | 0 | 51
38950.549 | 5 | 0 | 51
38950.5511 | 6 | 0 | 51
38950.5533 | 74 | 1 | 51
38950.5554 | 105 | 1 | 51
51
38950.5362 | 1 | 0 | 52
38950.5383 | 1 | 0 | 52
38950.5405 | 1 | 0 | 52
38950.5426 | 1 | 0 | 52
38950.5447 | 1 | 0 | 52
38950.5469 | 1 | 0 | 52
38950.549 | 2114 | 0 | 52
38950.5511 | 2480 | 1 | 52
38950.5533 | 2206 | 0 | 52
38950.5554 | 2434 | 1 | 52
52
38950.5362 | 1 | 0 | 53
38950.5383 | 1 | 0 | 53
38950.5405 | 1 | 0 | 53
38950.5426 | 1 | 0 | 53
38950.5447 | 1 | 0 | 53
38950.5469 | 1 | 0 | 53
38950.549 | 6 | 0 | 53
38950.5512 | 6 | 0 | 53
38950.5533 | 104 | 0 | 53
38950.5554 | 123 | 0 | 53
53
38950.5362 | 1 | 0 | 54
38950.5383 | 1 | 0 | 54
38950.5405 | 1 | 0 | 54
38950.5426 | 1 | 0 | 54
38950.5448 | 1 | 0 | 54
38950.5469 | 1 | 0 | 54
38950.549 | 2023 | 31 | 54
38950.5512 | 2079 | 0 | 54
38950.5533 | 2575 | 0 | 54
38950.5555 | 2572 | 0 | 54
54
38950.5362 | 1 | 0 | 55
38950.5384 | 1 | 0 | 55
38950.5405 | 1 | 0 | 55
38950.5426 | 1 | 0 | 55
38950.5448 | 1 | 0 | 55
38950.5469 | 1 | 0 | 55
38950.5491 | 5 | 0 | 55
38950.5512 | 7 | 0 | 55
38950.5533 | 92 | 0 | 55
38950.5555 | 138 | 0 | 55
55
38950.5362 | 1 | 0 | 56
38950.5384 | 1 | 0 | 56
38950.5405 | 1 | 0 | 56
38950.5427 | 1 | 0 | 56
38950.5448 | 1 | 0 | 56
38950.5469 | 1 | 0 | 56
38950.5491 | 2013 | 10 | 56
38950.5512 | 2512 | 0 | 56
38950.5533 | 2042 | 0 | 56
38950.5555 | 2111 | 0 | 56
56
38950.5362 | 1 | 0 | 57
38950.5384 | 1 | 0 | 57
38950.5405 | 1 | 0 | 57
38950.5427 | 1 | 0 | 57
38950.5448 | 1 | 0 | 57
38950.5469 | 1 | 0 | 57
38950.5491 | 5 | 0 | 57
38950.5512 | 6 | 0 | 57
38950.5534 | 113 | 0 | 57
38950.5555 | 119 | 0 | 57
57
38950.5363 | 1 | 0 | 58
38950.5384 | 1 | 0 | 58
38950.5405 | 1 | 0 | 58
38950.5427 | 1 | 0 | 58
38950.5448 | 1 | 0 | 58
38950.547 | 1 | 0 | 58
38950.5491 | 4 | 0 | 58
38950.5512 | 5 | 0 | 58
38950.5534 | 5 | 0 | 58
38950.5555 | 4 | 0 | 58
58
38950.5363 | 1 | 0 | 59
38950.5384 | 1 | 0 | 59
38950.5406 | 1 | 0 | 59
38950.5427 | 1 | 0 | 59
38950.5448 | 1 | 0 | 59
38950.547 | 1 | 0 | 59
38950.5491 | 4 | 0 | 59
38950.5513 | 6 | 0 | 59
38950.5534 | 117 | 0 | 59
38950.5555 | 144 | 0 | 59
59
38950.5363 | 1 | 0 | 60
38950.5384 | 1 | 0 | 60
38950.5406 | 1 | 0 | 60
38950.5427 | 1 | 0 | 60
38950.5449 | 1 | 0 | 60
38950.547 | 1 | 0 | 60
38950.5491 | 4 | 0 | 60
38950.5513 | 4 | 0 | 60
38950.5534 | 4 | 0 | 60
38950.5555 | 4 | 0 | 60
60
38950.5363 | 1 | 0 | 61
38950.5385 | 1 | 0 | 61
38950.5406 | 1 | 0 | 61
38950.5427 | 1 | 0 | 61
38950.5449 | 1 | 0 | 61
38950.547 | 1 | 0 | 61
38950.5491 | 3 | 0 | 61
38950.5513 | 5 | 0 | 61
38950.5534 | 104 | 0 | 61
38950.5556 | 146 | 0 | 61
61
38950.5363 | 1 | 0 | 62
38950.5385 | 1 | 0 | 62
38950.5406 | 1 | 0 | 62
38950.5428 | 1 | 0 | 62
38950.5449 | 1 | 0 | 62
38950.547 | 1 | 0 | 62
38950.5492 | 3 | 0 | 62
38950.5513 | 4 | 0 | 62
38950.5534 | 4 | 0 | 62
38950.5556 | 4 | 0 | 62
62
38950.5364 | 1 | 0 | 63
38950.5385 | 1 | 0 | 63
38950.5406 | 1 | 0 | 63
38950.5428 | 1 | 0 | 63
38950.5449 | 1 | 0 | 63
38950.547 | 1 | 0 | 63
38950.5492 | 3 | 0 | 63
38950.5513 | 5 | 0 | 63
38950.5535 | 109 | 0 | 63
38950.5556 | 132 | 0 | 63
63
38950.5364 | 1 | 0 | 64
38950.5385 | 1 | 0 | 64
38950.5406 | 1 | 0 | 64
38950.5428 | 1 | 0 | 64
38950.5449 | 1 | 0 | 64
38950.5471 | 1 | 0 | 64
38950.5492 | 3 | 0 | 64
38950.5513 | 4 | 0 | 64
38950.5535 | 4 | 0 | 64
38950.5556 | 4 | 0 | 64
64
38950.5364 | 1 | 0 | 65
38950.5385 | 1 | 0 | 65
38950.5407 | 1 | 0 | 65
38950.5428 | 1 | 0 | 65
38950.5449 | 1 | 0 | 65
38950.5471 | 1 | 0 | 65
38950.5492 | 2 | 0 | 65
38950.5514 | 6 | 0 | 65
38950.5535 | 143 | 0 | 65
38950.5556 | 174 | 0 | 65
65
38950.5364 | 1 | 0 | 66
38950.5385 | 1 | 0 | 66
38950.5407 | 1 | 0 | 66
38950.5428 | 1 | 0 | 66
38950.545 | 1 | 0 | 66
38950.5471 | 1 | 0 | 66
38950.5492 | 2532 | 0 | 66
38950.5514 | 2008 | 0 | 66
38950.5535 | 1851 | 0 | 66
38950.5556 | 2428 | 0 | 66
66
38950.5364 | 1 | 0 | 67
38950.5386 | 1 | 0 | 67
38950.5407 | 1 | 0 | 67
38950.5428 | 1 | 0 | 67
38950.545 | 1 | 0 | 67
38950.5471 | 1 | 0 | 67
38950.5492 | 5 | 0 | 67
38950.5514 | 7 | 0 | 67
38950.5535 | 150 | 0 | 67
38950.5557 | 175 | 0 | 67
67
38950.5364 | 1 | 0 | 68
38950.5386 | 1 | 0 | 68
38950.5407 | 1 | 0 | 68
38950.5428 | 1 | 0 | 68
38950.545 | 1 | 0 | 68
38950.5471 | 1 | 0 | 68
38950.5493 | 2214 | 1 | 68
38950.5514 | 2495 | 0 | 68
38950.5535 | 2534 | 0 | 68
38950.5557 | 2039 | 0 | 68
68
38950.5364 | 1 | 0 | 69
38950.5386 | 1 | 0 | 69
38950.5407 | 1 | 0 | 69
38950.5429 | 1 | 0 | 69
38950.545 | 1 | 0 | 69
38950.5471 | 2 | 0 | 69
38950.5493 | 6 | 0 | 69
38950.5514 | 8 | 0 | 69
38950.5536 | 144 | 0 | 69
38950.5557 | 138 | 0 | 69
69
38950.5365 | 1 | 0 | 70
38950.5386 | 1 | 0 | 70
38950.5407 | 1 | 0 | 70
38950.5429 | 1 | 0 | 70
38950.545 | 1 | 0 | 70
38950.5472 | 1 | 0 | 70
38950.5493 | 2143 | 1 | 70
38950.5514 | 2262 | 0 | 70
38950.5536 | 2568 | 0 | 70
38950.5557 | 2335 | 0 | 70
70
38950.5365 | 1 | 0 | 71
38950.5386 | 1 | 0 | 71
38950.5408 | 1 | 0 | 71
38950.5429 | 1 | 0 | 71
38950.545 | 1 | 0 | 71
38950.5472 | 1 | 0 | 71
38950.5493 | 6 | 0 | 71
38950.5514 | 8 | 0 | 71
38950.5536 | 146 | 0 | 71
38950.5557 | 162 | 0 | 71
71
38950.5365 | 1 | 0 | 72
38950.5386 | 1 | 0 | 72
38950.5408 | 1 | 0 | 72
38950.5429 | 1 | 0 | 72
38950.545 | 1 | 0 | 72
38950.5472 | 1 | 0 | 72
38950.5493 | 2072 | 0 | 72
38950.5515 | 2089 | 0 | 72
38950.5536 | 2191 | 0 | 72
38950.5557 | 2016 | 0 | 72
72
38950.5365 | 1 | 0 | 73
38950.5386 | 1 | 0 | 73
38950.5408 | 1 | 0 | 73
38950.5429 | 1 | 0 | 73
38950.5451 | 1 | 0 | 73
38950.5472 | 1 | 0 | 73
38950.5493 | 5 | 0 | 73
38950.5515 | 9 | 0 | 73
38950.5536 | 170 | 0 | 73
38950.5558 | 188 | 0 | 73
73
38950.5365 | 1 | 0 | 74
38950.5387 | 1 | 0 | 74
38950.5408 | 1 | 0 | 74
38950.5429 | 1 | 0 | 74
38950.5451 | 2 | 0 | 74
38950.5472 | 1 | 0 | 74
38950.5494 | 5 | 0 | 74
38950.5515 | 5 | 0 | 74
38950.5536 | 5 | 0 | 74
38950.5558 | 5 | 0 | 74
74
38950.5365 | 1 | 0 | 75
38950.5387 | 1 | 0 | 75
38950.5408 | 1 | 0 | 75
38950.543 | 1 | 0 | 75
38950.5451 | 1 | 0 | 75
38950.5472 | 1 | 0 | 75
38950.5494 | 4 | 0 | 75
38950.5515 | 11 | 0 | 75
38950.5537 | 148 | 0 | 75
38950.5558 | 177 | 0 | 75
75
38950.5366 | 1 | 0 | 76
38950.5387 | 1 | 0 | 76
38950.5408 | 2 | 0 | 76
38950.543 | 1 | 0 | 76
38950.5451 | 1 | 0 | 76
38950.5473 | 1 | 0 | 76
38950.5494 | 4 | 0 | 76
38950.5515 | 5 | 0 | 76
38950.5537 | 4 | 0 | 76
38950.5558 | 4 | 0 | 76
76
38950.5366 | 1 | 0 | 77
38950.5387 | 1 | 0 | 77
38950.5409 | 1 | 0 | 77
38950.543 | 1 | 0 | 77
38950.5451 | 1 | 0 | 77
38950.5473 | 1 | 0 | 77
38950.5494 | 1180 | 1156 | 77
38950.5516 | 1112 | 1082 | 77
38950.5537 | 1180 | 1156 | 77
38950.5558 | 1167 | 1199 | 77
77
38950.5366 | 1 | 0 | 78
38950.5387 | 1 | 0 | 78
38950.5409 | 1 | 0 | 78
38950.543 | 1 | 0 | 78
38950.5452 | 1 | 0 | 78
38950.5473 | 2 | 2 | 78
38950.5494 | 1110 | 1081 | 78
38950.5516 | 1115 | 925 | 78
38950.5537 | 1206 | 963 | 78
38950.5558 | 1201 | 1184 | 78
78
38950.5366 | 1 | 0 | 79
38950.5387 | 1 | 0 | 79
38950.5409 | 1 | 0 | 79
38950.543 | 1 | 0 | 79
38950.5452 | 1 | 0 | 79
38950.5473 | 1 | 0 | 79
38950.5494 | 4 | 16 | 79
38950.5516 | 4 | 15 | 79
38950.5537 | 4 | 14 | 79
38950.5559 | 4 | 11 | 79
79
38950.5366 | 1 | 0 | 80
38950.5388 | 1 | 0 | 80
38950.5409 | 1 | 0 | 80
38950.543 | 1 | 0 | 80
38950.5452 | 1 | 0 | 80
38950.5473 | 1 | 0 | 80
38950.5495 | 2479 | 7 | 80
38950.5516 | 1984 | 8 | 80
38950.5537 | 1975 | 7 | 80
38950.5559 | 2357 | 6 | 80
80
38950.5366 | 1 | 0 | 81
38950.5388 | 1 | 0 | 81
38950.5409 | 1 | 0 | 81
38950.5431 | 1 | 0 | 81
38950.5452 | 1 | 0 | 81
38950.5473 | 1 | 0 | 81
38950.5495 | 6 | 5 | 81
38950.5516 | 5 | 4 | 81
38950.5537 | 5 | 4 | 81
38950.5559 | 5 | 3 | 81
81
38950.5367 | 1 | 0 | 82
38950.5388 | 1 | 0 | 82
38950.5409 | 1 | 0 | 82
38950.5431 | 1 | 0 | 82
38950.5452 | 1 | 0 | 82
38950.5473 | 1 | 0 | 82
38950.5495 | 2087 | 3 | 82
38950.5516 | 2487 | 3 | 82
38950.5538 | 2373 | 3 | 82
38950.5559 | 2456 | 3 | 82
82
38950.5367 | 1 | 0 | 83
38950.5388 | 1 | 0 | 83
38950.5409 | 1 | 0 | 83
38950.5431 | 1 | 0 | 83
38950.5452 | 1 | 0 | 83
38950.5474 | 1 | 0 | 83
38950.5495 | 6 | 1 | 83
38950.5516 | 5 | 1 | 83
38950.5538 | 5 | 2 | 83
38950.5559 | 5 | 2 | 83
83
38950.5367 | 1 | 0 | 84
38950.5388 | 1 | 0 | 84
38950.541 | 1 | 1 | 84
38950.5431 | 1 | 0 | 84
38950.5452 | 1 | 0 | 84
38950.5474 | 1 | 0 | 84
38950.5495 | 2153 | 1 | 84
38950.5517 | 2572 | 1 | 84
38950.5538 | 2503 | 1 | 84
38950.5559 | 2128 | 1 | 84
84
38950.5367 | 1 | 0 | 85
38950.5388 | 1 | 0 | 85
38950.541 | 1 | 0 | 85
38950.5431 | 1 | 0 | 85
38950.5453 | 1 | 0 | 85
38950.5474 | 1 | 0 | 85
38950.5495 | 6 | 1 | 85
38950.5517 | 5 | 1 | 85
38950.5538 | 5 | 0 | 85
38950.5559 | 5 | 1 | 85
85
38950.5367 | 1 | 0 | 86
38950.5389 | 1 | 0 | 86
38950.541 | 1 | 0 | 86
38950.5431 | 1 | 0 | 86
38950.5453 | 1 | 0 | 86
38950.5474 | 1 | 0 | 86
38950.5496 | 2075 | 1 | 86
38950.5517 | 2246 | 1 | 86
38950.5538 | 2352 | 0 | 86
38950.556 | 2301 | 0 | 86
86
38950.5367 | 1 | 0 | 87
38950.5389 | 1 | 0 | 87
38950.541 | 1 | 0 | 87
38950.5432 | 1 | 0 | 87
38950.5453 | 2 | 0 | 87
38950.5474 | 1 | 0 | 87
38950.5496 | 5 | 0 | 87
38950.5517 | 5 | 0 | 87
38950.5538 | 5 | 1 | 87
38950.556 | 4 | 0 | 87
87
38950.5368 | 1 | 0 | 88
38950.5389 | 1 | 0 | 88
38950.541 | 1 | 0 | 88
38950.5432 | 1 | 0 | 88
38950.5453 | 1 | 0 | 88
38950.5475 | 1 | 0 | 88
38950.5496 | 5 | 0 | 88
38950.5517 | 5 | 0 | 88
38950.5539 | 4 | 1 | 88
38950.556 | 4 | 0 | 88
88
38950.5368 | 1 | 0 | 89
38950.5389 | 1 | 0 | 89
38950.5411 | 1 | 0 | 89
38950.5432 | 1 | 0 | 89
38950.5453 | 1 | 1 | 89
38950.5475 | 1 | 0 | 89
38950.5496 | 5 | 0 | 89
38950.5517 | 5 | 0 | 89
38950.5539 | 4 | 0 | 89
38950.556 | 4 | 0 | 89
89
38950.5368 | 1 | 0 | 90
38950.5389 | 1 | 0 | 90
38950.5411 | 1 | 0 | 90
38950.5432 | 1 | 0 | 90
38950.5453 | 1 | 0 | 90
38950.5475 | 1 | 0 | 90
38950.5496 | 5 | 0 | 90
38950.5518 | 5 | 0 | 90
38950.5539 | 4 | 0 | 90
38950.556 | 4 | 0 | 90
90
38950.5368 | 1 | 0 | 91
38950.5389 | 1 | 0 | 91
38950.5411 | 1 | 0 | 91
38950.5432 | 1 | 0 | 91
38950.5454 | 1 | 0 | 91
38950.5475 | 1 | 0 | 91
38950.5496 | 4 | 0 | 91
38950.5518 | 4 | 0 | 91
38950.5539 | 4 | 0 | 91
38950.5561 | 4 | 0 | 91
91
38950.5368 | 1 | 0 | 92
38950.539 | 1 | 0 | 92
38950.5411 | 1 | 0 | 92
38950.5432 | 1 | 0 | 92
38950.5454 | 1 | 0 | 92
38950.5475 | 1 | 0 | 92
38950.5497 | 2509 | 0 | 92
38950.5518 | 2454 | 0 | 92
38950.5539 | 2047 | 0 | 92
38950.5561 | 2399 | 0 | 92
92
38950.5368 | 1 | 0 | 93
38950.539 | 1 | 0 | 93
38950.5411 | 1 | 0 | 93
38950.5433 | 1 | 0 | 93
38950.5454 | 1 | 0 | 93
38950.5475 | 1 | 0 | 93
38950.5497 | 5 | 0 | 93
38950.5518 | 5 | 0 | 93
38950.5539 | 5 | 0 | 93
38950.5561 | 5 | 0 | 93
93
38950.5369 | 1 | 0 | 94
38950.539 | 1 | 0 | 94
38950.5411 | 1 | 0 | 94
38950.5433 | 1 | 0 | 94
38950.5454 | 1 | 0 | 94
38950.5475 | 1 | 0 | 94
38950.5497 | 2516 | 0 | 94
38950.5518 | 2245 | 0 | 94
38950.554 | 2237 | 0 | 94
38950.5561 | 2447 | 0 | 94
94
38950.5369 | 1 | 0 | 95
38950.539 | 1 | 0 | 95
38950.5411 | 1 | 0 | 95
38950.5433 | 1 | 0 | 95
38950.5454 | 1 | 1 | 95
38950.5476 | 1 | 0 | 95
38950.5497 | 6 | 0 | 95
38950.5518 | 5 | 0 | 95
38950.554 | 5 | 0 | 95
38950.5561 | 4 | 0 | 95
95
38950.5369 | 1 | 0 | 96
38950.539 | 1 | 0 | 96
38950.5412 | 1 | 0 | 96
38950.5433 | 1 | 0 | 96
38950.5454 | 2 | 0 | 96
38950.5476 | 1 | 0 | 96
38950.5497 | 2060 | 0 | 96
38950.5519 | 2426 | 0 | 96
38950.554 | 2068 | 0 | 96
38950.5561 | 2135 | 0 | 96
96
38950.5369 | 1 | 0 | 97
38950.539 | 1 | 0 | 97
38950.5412 | 1 | 0 | 97
38950.5433 | 1 | 0 | 97
38950.5455 | 1 | 0 | 97
38950.5476 | 1 | 0 | 97
38950.5497 | 5 | 0 | 97
38950.5519 | 5 | 0 | 97
38950.554 | 5 | 0 | 97
38950.5561 | 4 | 0 | 97
97
38950.5369 | 1 | 0 | 98
38950.5391 | 1 | 0 | 98
38950.5412 | 1 | 0 | 98
38950.5433 | 1 | 0 | 98
38950.5476 | 1 | 0 | 98
38950.5497 | 2435 | 0 | 98
38950.5519 | 2174 | 0 | 98
38950.554 | 2104 | 0 | 98
38950.5562 | 2355 | 0 | 98
98
38950.5369 | 1 | 0 | 99
38950.5391 | 1 | 0 | 99
38950.5412 | 1 | 0 | 99
38950.5433 | 1 | 0 | 99
38950.5455 | 1 | 0 | 99
38950.5476 | 1 | 0 | 99
38950.5498 | 5 | 0 | 99
38950.5519 | 5 | 0 | 99
38950.554 | 5 | 0 | 99
38950.5562 | 5 | 0 | 99
99
38950.5369 | 1 | 0 | 100
38950.5391 | 1 | 0 | 100
38950.5412 | 2 | 0 | 100
38950.5434 | 1 | 0 | 100
38950.5455 | 1 | 0 | 100
38950.5476 | 1 | 0 | 100
38950.5498 | 5 | 0 | 100
38950.5519 | 5 | 0 | 100
38950.5541 | 4 | 0 | 100
38950.5562 | 4 | 0 | 100
100
38950.537 | 1 | 0 | 101
38950.5391 | 1 | 0 | 101
38950.5412 | 1 | 0 | 101
38950.5434 | 1 | 0 | 101
38950.5455 | 1 | 0 | 101
38950.5477 | 1 | 0 | 101
38950.5498 | 5 | 0 | 101
38950.5519 | 5 | 0 | 101
38950.5541 | 4 | 0 | 101
38950.5562 | 4 | 0 | 101
101
38950.537 | 1 | 0 | 102
38950.5391 | 1 | 0 | 102
38950.5413 | 1 | 0 | 102
38950.5434 | 1 | 0 | 102
38950.5455 | 1 | 0 | 102
38950.5477 | 1 | 0 | 102
38950.5498 | 4 | 0 | 102
38950.552 | 5 | 0 | 102
38950.5541 | 4 | 0 | 102
38950.5562 | 4 | 0 | 102
102
38950.537 | 1 | 0 | 103
38950.5391 | 1 | 0 | 103
38950.5413 | 1 | 0 | 103
38950.5434 | 1 | 0 | 103
38950.5456 | 1 | 0 | 103
38950.5477 | 1216 | 1063 | 103
38950.5498 | 2364 | 0 | 103
38950.552 | 2344 | 0 | 103
38950.5541 | 1884 | 0 | 103
38950.5563 | 2192 | 0 | 103
103
38950.537 | 1 | 0 | 104
38950.5392 | 1 | 0 | 104
38950.5413 | 1 | 0 | 104
38950.5434 | 1 | 0 | 104
38950.5456 | 1 | 0 | 104
38950.5477 | 1168 | 973 | 104
38950.5498 | 2460 | 0 | 104
38950.552 | 1974 | 5 | 104
38950.5541 | 2340 | 0 | 104
38950.5563 | 1904 | 0 | 104
104
38950.537 | 1 | 0 | 105
38950.5392 | 1 | 0 | 105
38950.5413 | 1 | 0 | 105
38950.5434 | 1 | 0 | 105
38950.5456 | 1 | 0 | 105
38950.5477 | 1609 | 15 | 105
38950.5499 | 1967 | 0 | 105
38950.552 | 2297 | 0 | 105
38950.5541 | 2279 | 0 | 105
38950.5563 | 2408 | 0 | 105
105
38950.537 | 1 | 0 | 106
38950.5392 | 1 | 0 | 106
38950.5413 | 1 | 0 | 106
38950.5435 | 1 | 0 | 106
38950.5456 | 1 | 0 | 106
38950.5477 | 5 | 6 | 106
38950.5499 | 2172 | 0 | 106
38950.552 | 2499 | 0 | 106
38950.5542 | 2524 | 0 | 106
38950.5563 | 2538 | 0 | 106
106
38950.5371 | 1 | 0 | 107
38950.5392 | 1 | 0 | 107
38950.5413 | 1 | 0 | 107
38950.5435 | 1 | 0 | 107
38950.5456 | 1 | 0 | 107
38950.5478 | 2096 | 4 | 107
38950.5499 | 2347 | 0 | 107
38950.552 | 1885 | 0 | 107
38950.5542 | 1870 | 0 | 107
38950.5563 | 2418 | 0 | 107
107
38950.5371 | 1 | 0 | 108
38950.5392 | 1 | 0 | 108
38950.5414 | 1 | 0 | 108
38950.5435 | 1 | 0 | 108
38950.5456 | 1 | 0 | 108
38950.5478 | 6 | 1 | 108
38950.5499 | 2586 | 0 | 108
38950.552 | 2577 | 1 | 108
38950.5542 | 2172 | 0 | 108
38950.5563 | 1993 | 0 | 108
108
38950.5371 | 1 | 0 | 109
38950.5392 | 1 | 0 | 109
38950.5414 | 1 | 0 | 109
38950.5435 | 1 | 0 | 109
38950.5456 | 1 | 0 | 109
38950.5478 | 2369 | 2 | 109
38950.5499 | 2012 | 0 | 109
38950.5521 | 2451 | 0 | 109
38950.5542 | 1776 | 0 | 109
38950.5563 | 2211 | 0 | 109
109
38950.5371 | 1 | 0 | 110
38950.5392 | 1 | 0 | 110
38950.5414 | 1 | 0 | 110
38950.5435 | 1 | 0 | 110
38950.5457 | 1 | 0 | 110
38950.5478 | 6 | 1 | 110
38950.5499 | 6 | 0 | 110
38950.5521 | 5 | 0 | 110
38950.5542 | 5 | 0 | 110
38950.5564 | 5 | 0 | 110
110
38950.5371 | 1 | 0 | 111
38950.5393 | 1 | 0 | 111
38950.5414 | 1 | 0 | 111
38950.5435 | 1 | 0 | 111
38950.5457 | 1 | 0 | 111
38950.5478 | 2386 | 1 | 111
38950.55 | 1970 | 0 | 111
38950.5521 | 2373 | 0 | 111
38950.5542 | 2110 | 0 | 111
38950.5564 | 2003 | 0 | 111
111
38950.5371 | 1 | 0 | 112
38950.5393 | 1 | 0 | 112
38950.5414 | 1 | 0 | 112
38950.5436 | 1 | 0 | 112
38950.5457 | 1 | 0 | 112
38950.5478 | 6 | 0 | 112
38950.55 | 6 | 0 | 112
38950.5521 | 5 | 0 | 112
38950.5542 | 5 | 0 | 112
38950.5564 | 5 | 0 | 112
112
38950.5372 | 1 | 0 | 113
38950.5393 | 1 | 0 | 113
38950.5414 | 1 | 0 | 113
38950.5436 | 1 | 0 | 113
38950.5457 | 1 | 0 | 113
38950.5479 | 2390 | 0 | 113
38950.55 | 2343 | 0 | 113
38950.5521 | 1981 | 0 | 113
38950.5543 | 2511 | 0 | 113
38950.5564 | 2274 | 0 | 113
113
38950.5372 | 1 | 0 | 114
38950.5393 | 1 | 0 | 114
38950.5415 | 1 | 0 | 114
38950.5436 | 1 | 0 | 114
38950.5457 | 1 | 0 | 114
38950.5479 | 6 | 0 | 114
38950.55 | 2367 | 0 | 114
38950.5521 | 2120 | 0 | 114
38950.5543 | 2325 | 0 | 114
38950.5564 | 2055 | 0 | 114
114
38950.5372 | 1 | 0 | 115
38950.5393 | 1 | 0 | 115
38950.5415 | 1 | 0 | 115
38950.5436 | 1 | 0 | 115
38950.5458 | 1 | 0 | 115
38950.5479 | 2277 | 0 | 115
38950.55 | 2394 | 0 | 115
38950.5522 | 2503 | 0 | 115
38950.5543 | 2207 | 0 | 115
38950.5564 | 2337 | 0 | 115
115
38950.5372 | 1 | 0 | 116
38950.5394 | 1 | 0 | 116
38950.5415 | 1 | 0 | 116
38950.5436 | 1 | 0 | 116
38950.5458 | 1 | 0 | 116
38950.5479 | 6 | 0 | 116
38950.55 | 2048 | 0 | 116
38950.5522 | 2357 | 0 | 116
38950.5543 | 2186 | 0 | 116
38950.5565 | 2108 | 0 | 116
116
38950.5372 | 1 | 0 | 117
38950.5394 | 1 | 0 | 117
38950.5415 | 1 | 0 | 117
38950.5436 | 1 | 0 | 117
38950.5458 | 1 | 0 | 117
38950.5479 | 2144 | 0 | 117
38950.5501 | 2047 | 0 | 117
38950.5522 | 2323 | 0 | 117
38950.5543 | 1934 | 0 | 117
38950.5565 | 2256 | 0 | 117
117
38950.5372 | 1 | 0 | 118
38950.5394 | 1 | 0 | 118
38950.5415 | 1 | 0 | 118
38950.5437 | 1 | 0 | 118
38950.5458 | 1 | 0 | 118
38950.5479 | 6 | 0 | 118
38950.5501 | 6 | 0 | 118
38950.5522 | 5 | 0 | 118
38950.5544 | 5 | 0 | 118
38950.5565 | 5 | 0 | 118
118
38950.5373 | 1 | 0 | 119
38950.5394 | 1 | 0 | 119
38950.5415 | 1 | 0 | 119
38950.5437 | 1 | 0 | 119
38950.5458 | 1 | 0 | 119
38950.548 | 2225 | 0 | 119
38950.5501 | 2346 | 0 | 119
38950.5522 | 2083 | 0 | 119
38950.5544 | 2157 | 0 | 119
38950.5565 | 2342 | 0 | 119
119
38950.5373 | 1 | 0 | 120
38950.5394 | 1 | 0 | 120
38950.5416 | 1 | 0 | 120
38950.5437 | 1 | 0 | 120
38950.5458 | 1 | 0 | 120
38950.548 | 5 | 0 | 120
38950.5501 | 6 | 0 | 120
38950.5522 | 5 | 0 | 120
38950.5544 | 5 | 0 | 120
38950.5565 | 4 | 0 | 120
120
38950.5373 | 1 | 0 | 121
38950.5394 | 1 | 0 | 121
38950.5416 | 1 | 0 | 121
38950.5437 | 1 | 0 | 121
38950.5458 | 1 | 0 | 121
38950.548 | 1016 | 980 | 121
38950.5501 | 2052 | 0 | 121
38950.5523 | 2347 | 0 | 121
38950.5544 | 2569 | 0 | 121
38950.5565 | 2571 | 0 | 121
121
38950.5373 | 1 | 0 | 122
38950.5394 | 1 | 0 | 122
38950.5416 | 1 | 0 | 122
38950.5437 | 1 | 0 | 122
38950.5459 | 1 | 0 | 122
38950.5501 | 2034 | 0 | 122
38950.5523 | 2336 | 1 | 122
38950.5544 | 2496 | 0 | 122
38950.5566 | 2381 | 0 | 122
122
38950.5373 | 1 | 0 | 123
38950.5395 | 1 | 0 | 123
38950.5416 | 1 | 0 | 123
38950.5437 | 2 | 0 | 123
38950.5459 | 1 | 0 | 123
38950.548 | 5 | 16 | 123
38950.5502 | 2053 | 0 | 123
38950.5523 | 2106 | 0 | 123
38950.5544 | 2370 | 0 | 123
38950.5566 | 2313 | 0 | 123
123
38950.5373 | 1 | 0 | 124
38950.5395 | 1 | 0 | 124
38950.5416 | 1 | 0 | 124
38950.5437 | 1 | 0 | 124
38950.5459 | 1 | 0 | 124
38950.548 | 5 | 8 | 124
38950.5502 | 6 | 0 | 124
38950.5523 | 5 | 0 | 124
38950.5544 | 5 | 0 | 124
38950.5566 | 5 | 0 | 124
124
38950.5373 | 1 | 0 | 125
38950.5395 | 1 | 0 | 125
38950.5416 | 1 | 0 | 125
38950.5438 | 1 | 0 | 125
38950.5459 | 1 | 0 | 125
38950.548 | 5 | 4 | 125
38950.5502 | 2592 | 0 | 125
38950.5523 | 2143 | 0 | 125
38950.5545 | 2258 | 0 | 125
38950.5566 | 2029 | 0 | 125
125
38950.5374 | 1 | 0 | 126
38950.5395 | 1 | 0 | 126
38950.5416 | 1 | 0 | 126
38950.5438 | 1 | 0 | 126
38950.5459 | 1 | 0 | 126
38950.5481 | 5 | 2 | 126
38950.5502 | 5 | 0 | 126
38950.5523 | 4 | 0 | 126
38950.5545 | 5 | 0 | 126
38950.5566 | 4 | 0 | 126
126
38950.5374 | 1 | 0 | 127
38950.5395 | 1 | 0 | 127
38950.5417 | 1 | 0 | 127
38950.5438 | 1 | 0 | 127
38950.5459 | 1 | 0 | 127
38950.5481 | 4 | 2 | 127
38950.5502 | 2173 | 0 | 127
38950.5524 | 2445 | 0 | 127
38950.5545 | 2134 | 0 | 127
38950.5566 | 2542 | 0 | 127
127
38950.5374 | 1 | 0 | 128
38950.5395 | 1 | 0 | 128
38950.5417 | 1 | 0 | 128
38950.5438 | 1 | 0 | 128
38950.546 | 1 | 0 | 128
38950.5481 | 4 | 1 | 128
38950.5502 | 5 | 0 | 128
38950.5524 | 5 | 0 | 128
38950.5545 | 5 | 0 | 128
38950.5567 | 5 | 0 | 128
128
38950.5374 | 1 | 0 | 129
38950.5396 | 1 | 0 | 129
38950.5417 | 1 | 0 | 129
38950.5438 | 1 | 0 | 129
38950.546 | 1 | 0 | 129
38950.5481 | 4 | 1 | 129
38950.5503 | 2407 | 0 | 129
38950.5524 | 2561 | 0 | 129
38950.5545 | 1989 | 1 | 129
38950.5567 | 2564 | 0 | 129
129
38950.5374 | 1 | 0 | 130
38950.5396 | 1 | 0 | 130
38950.5417 | 1 | 0 | 130
38950.5439 | 1 | 0 | 130
38950.546 | 1 | 0 | 130
38950.5481 | 3 | 1 | 130
38950.5503 | 5 | 0 | 130
38950.5524 | 5 | 0 | 130
38950.5545 | 5 | 0 | 130
38950.5567 | 5 | 0 | 130
130
38950.5375 | 1 | 0 | 131
38950.5396 | 1 | 0 | 131
38950.5417 | 1 | 0 | 131
38950.5439 | 1 | 0 | 131
38950.546 | 1 | 0 | 131
38950.5481 | 4 | 0 | 131
38950.5503 | 5 | 0 | 131
38950.5524 | 5 | 0 | 131
38950.5546 | 5 | 0 | 131
38950.5567 | 4 | 0 | 131
131
38950.5375 | 1 | 0 | 132
38950.5396 | 1 | 0 | 132
38950.5417 | 1 | 0 | 132
38950.5439 | 1 | 0 | 132
38950.546 | 1 | 0 | 132
38950.5482 | 3 | 0 | 132
38950.5503 | 5 | 0 | 132
38950.5524 | 5 | 0 | 132
38950.5546 | 4 | 0 | 132
38950.5567 | 4 | 0 | 132
132

## C6-F12
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38950.537 | 1 | 0 | 38950.537 | 1 | 0 |  | -4.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5391 | 1 | 0 | 38950.5391 | 1 | 0 |  | 180.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5412 | 1 | 0 | 38950.5413 | 1 | 0 |  | 365 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5434 | 1 | 0 | 38950.5434 | 1 | 0 |  | 550 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5455 | 1 | 0 | 38950.5455 | 1 | 0 |  | 734.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5477 | 1 | 0 | 38950.5477 | 1 | 0 |  | 919.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5498 | 5 | 0 | 38950.5498 | 4 | 0 |  | 1104 | 1249 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5519 | 5 | 0 | 38950.552 | 5 | 0 |  | 1289 | 1434 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5541 | 4 | 0 | 38950.5541 | 4 | 0 |  | 1473.5 | 1618.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38950.5562 | 4 | 0 | 38950.5562 | 4 | 0 |  | 1658.5 | 1803.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C6-F11
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38950.5369 | 1 | 0 | 38950.5369 | 1 | 0 |  | -7.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5391 | 1 | 0 | 38950.5391 | 1 | 0 |  | 177.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5412 | 1 | 0 | 38950.5412 | 2 | 0 |  | 362.5 | 507.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38950.5433 | 1 | 0 | 38950.5434 | 1 | 0 |  | 547 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5455 | 1 | 0 | 38950.5455 | 1 | 0 |  | 731.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5476 | 1 | 0 | 38950.5476 | 1 | 0 |  | 916.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5498 | 5 | 0 | 38950.5498 | 5 | 0 |  | 1101.5 | 1246.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5519 | 5 | 0 | 38950.5519 | 5 | 0 |  | 1286 | 1431 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.554 | 5 | 0 | 38950.5541 | 4 | 0 |  | 1471 | 1616 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5562 | 5 | 0 | 38950.5562 | 4 | 0 |  | 1655.5 | 1800.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969

## C6-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 149.6569 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38950.5369 | 1 | 0 | 38950.5369 | 1 | 0 |  | -10 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.539 | 1 | 0 | 38950.5391 | 1 | 0 |  | 174.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.5412 | 1 | 0 | 38950.5412 | 1 | 0 |  | 359.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.5433 | 1 | 0 | 38950.5433 | 1 | 0 |  | 544.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.5455 | 1 | 0 |  | 1 | 0 |  | 728 | 873 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.5476 | 1 | 0 | 38950.5476 | 1 | 0 |  | 914 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245038 | 245038 | 245037.9994
38950.5497 | 5 | 0 | 38950.5497 | 2435 | 0 |  | 1098.5 | 1243.5 | 0.30525 | 0 | 148.6569 | 0 | 0.0030525 | 0 | 1.4866 | 0 | 0.0030525 | 1.4866 | 48927.6 | 0.67269 | 48927.5969
38950.5519 | 5 | 0 | 38950.5519 | 2174 | 0 |  | 1283.5 | 1428.5 | 0.30525 | 0 | 132.7228 | 0 | 0.0030525 | 0 | 1.3272 | 0 | 0.0030525 | 1.3272 | 48927.6 | 12.759 | 48927.5969
38950.554 | 5 | 0 | 38950.554 | 2104 | 0 |  | 1468 | 1613 | 0.30525 | 0 | 128.4493 | 0 | 0.0030525 | 0 | 1.2845 | 0 | 0.0030525 | 1.2845 | 48927.6 | 16.5105 | 48927.5969
38950.5561 | 4 | 0 | 38950.5562 | 2355 | 0 |  | 1653 | 1798 | 0.2442 | 0 | 143.7729 | 0 | 0.002442 | 0 | 1.4377 | 0 | 0.002442 | 1.4377 | 61184.5 | 4.0926 | 61184.4976

## C6-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 149.1074 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38950.5369 | 1 | 0 | 38950.5369 | 1 | 0 |  | -12.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244138 | 244138 | 244137.9994
38950.539 | 1 | 0 | 38950.539 | 1 | 0 |  | 172 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244138 | 244138 | 244137.9994
38950.5411 | 1 | 0 | 38950.5412 | 1 | 0 |  | 356.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244138 | 244138 | 244137.9994
38950.5433 | 1 | 0 | 38950.5433 | 1 | 0 |  | 541.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244138 | 244138 | 244137.9994
38950.5454 | 1 | 1 | 38950.5454 | 2 | 0 |  | 726.5 | 871.5 | 0.06105 | 0.06105 | 0.1221 | 0 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 0 | 0.001221 | 297894746.22 | 122019 | 243838.1638
38950.5476 | 1 | 0 | 38950.5476 | 1 | 0 |  | 911 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244138 | 244138 | 244137.9994
38950.5497 | 6 | 0 | 38950.5497 | 2060 | 0 |  | 1096 | 1241 | 0.3663 | 0 | 125.7631 | 0 | 0.003663 | 0 | 1.2576 | 0 | 0.003663 | 1.2576 | 40606.3333 | 18.5621 | 40606.3297
38950.5518 | 5 | 0 | 38950.5519 | 2426 | 0 |  | 1280.5 | 1425.5 | 0.30525 | 0 | 148.1074 | 0 | 0.0030525 | 0 | 1.4811 | 0 | 0.0030525 | 1.4811 | 48747.6 | 0.67519 | 48747.5969
38950.554 | 5 | 0 | 38950.554 | 2068 | 0 |  | 1465.5 | 1610.5 | 0.30525 | 0 | 126.2515 | 0 | 0.0030525 | 0 | 1.2625 | 0 | 0.0030525 | 1.2625 | 48747.6 | 18.1035 | 48747.5969
38950.5561 | 4 | 0 | 38950.5561 | 2135 | 0 |  | 1650.5 | 1795.5 | 0.2442 | 0 | 130.3419 | 0 | 0.002442 | 0 | 1.3034 | 0 | 0.002442 | 1.3034 | 60959.5 | 14.3972 | 60959.4976

## C5-F12
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38950.5368 | 1 | 0 | 38950.5368 | 1 | 0 |  | -21.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5389 | 1 | 0 | 38950.5389 | 1 | 0 |  | 163.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5411 | 1 | 0 | 38950.5411 | 1 | 0 |  | 348.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5432 | 1 | 0 | 38950.5432 | 1 | 0 |  | 533 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5453 | 1 | 1 | 38950.5453 | 1 | 0 |  | 718 | 863 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 446062848.04 | 211202 | 211002.0947
38950.5475 | 1 | 0 | 38950.5475 | 1 | 0 |  | 902.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5496 | 5 | 0 | 38950.5496 | 5 | 0 |  | 1087.5 | 1232.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5517 | 5 | 0 | 38950.5518 | 5 | 0 |  | 1272.5 | 1417.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5539 | 4 | 0 | 38950.5539 | 4 | 0 |  | 1457 | 1602 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38950.556 | 4 | 0 | 38950.556 | 4 | 0 |  | 1641.5 | 1786.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C5-F11
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38950.5367 | 1 | 0 | 38950.5368 | 1 | 0 |  | -24 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5389 | 1 | 0 | 38950.5389 | 1 | 0 |  | 160.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.541 | 1 | 0 | 38950.541 | 1 | 0 |  | 345.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5432 | 1 | 0 | 38950.5432 | 1 | 0 |  | 530.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5453 | 2 | 0 | 38950.5453 | 1 | 0 |  | 715 | 860 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38950.5474 | 1 | 0 | 38950.5475 | 1 | 0 |  | 900 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5496 | 5 | 0 | 38950.5496 | 5 | 0 |  | 1084.5 | 1229.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5517 | 5 | 0 | 38950.5517 | 5 | 0 |  | 1269.5 | 1414.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5538 | 5 | 1 | 38950.5539 | 4 | 1 |  | 1454 | 1599 | 0.30525 | 0.06105 | 0.2442 | 0.06105 | 0.0030525 | 0.0006105 | 0.002442 | 0.0006105 | 0.002442 | 0.0018315 | 52719.2359 | 70345.1445 | 210402.8992
38950.556 | 4 | 0 | 38950.556 | 4 | 0 |  | 1639 | 1784 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## C5-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 144.5897 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38950.5367 | 1 | 0 | 38950.5367 | 1 | 0 |  | -26.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.5388 | 1 | 0 | 38950.5389 | 1 | 0 |  | 158 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.541 | 1 | 0 | 38950.541 | 1 | 0 |  | 342.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.5431 | 1 | 0 | 38950.5431 | 1 | 0 |  | 527.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.5453 | 1 | 0 | 38950.5453 | 1 | 0 |  | 712.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.5474 | 1 | 0 | 38950.5474 | 1 | 0 |  | 897 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 236738 | 236738 | 236737.9994
38950.5495 | 6 | 1 | 38950.5496 | 2075 | 1 |  | 1082 | 1227 | 0.3663 | 0.06105 | 126.6789 | 0.06105 | 0.003663 | 0.0006105 | 1.2668 | 0.0006105 | 0.0030525 | 1.2662 | 114161.4305 | 34.1219 | 60075.807
38950.5517 | 5 | 1 | 38950.5517 | 2246 | 1 |  | 1266.5 | 1411.5 | 0.30525 | 0.06105 | 137.1184 | 0.06105 | 0.0030525 | 0.0006105 | 1.3712 | 0.0006105 | 0.002442 | 1.3706 | 16475.804 | 9.6669 | 20823.9192
38950.5538 | 5 | 0 | 38950.5538 | 2352 | 0 |  | 1451.5 | 1596.5 | 0.30525 | 0 | 143.5897 | 0 | 0.0030525 | 0 | 1.4359 | 0 | 0.0030525 | 1.4359 | 47267.6 | 0.69643 | 47267.5969
38950.5559 | 5 | 1 | 38950.556 | 2301 | 0 |  | 1636 | 1781 | 0.30525 | 0.06105 | 140.4762 | 0 | 0.0030525 | 0.0006105 | 1.4048 | 0 | 0.002442 | 1.4048 | 7838.8438 | 3.8242 | 8701.3439

## C5-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 158.0208 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38950.5367 | 1 | 0 | 38950.5367 | 1 | 0 |  | -29.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5388 | 1 | 0 | 38950.5388 | 1 | 0 |  | 155.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5409 | 1 | 0 | 38950.541 | 1 | 0 |  | 340 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5431 | 1 | 0 | 38950.5431 | 1 | 0 |  | 524.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5452 | 1 | 0 | 38950.5452 | 1 | 0 |  | 709.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5474 | 1 | 0 | 38950.5474 | 1 | 0 |  | 894.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258738 | 258738 | 258737.9994
38950.5495 | 6 | 1 | 38950.5495 | 2153 | 1 |  | 1079 | 1224 | 0.3663 | 0.06105 | 131.4408 | 0.06105 | 0.003663 | 0.0006105 | 1.3144 | 0.0006105 | 0.0030525 | 1.3138 | 4515323.7124 | 20.2314 | 43437.038
38950.5516 | 5 | 1 | 38950.5517 | 2572 | 1 |  | 1264 | 1409 | 0.30525 | 0.06105 | 157.0208 | 0.06105 | 0.0030525 | 0.0006105 | 1.5702 | 0.0006105 | 0.002442 | 1.5696 | 1688.8885 | 0.67131 | 1722.0077
38950.5538 | 5 | 2 | 38950.5538 | 2503 | 1 |  | 1448.5 | 1593.5 | 0.30525 | 0.1221 | 152.8083 | 0.06105 | 0.0030525 | 0.001221 | 1.5281 | 0.0006105 | 0.0018315 | 1.5275 | 4645.6084 | 3.8016 | 4727.0163
38950.5559 | 5 | 2 | 38950.5559 | 2128 | 1 |  | 1633.5 | 1778.5 | 0.30525 | 0.1221 | 129.9145 | 0.06105 | 0.0030525 | 0.001221 | 1.2991 | 0.0006105 | 0.0018315 | 1.2985 | 41398.9712 | 61.7245 | 49261.0652

## C5-C6
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38950.5366 | 1 | 0 | 38950.5366 | 1 | 0 |  | -38 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5387 | 1 | 0 | 38950.5387 | 1 | 0 |  | 146.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5409 | 1 | 0 | 38950.5409 | 1 | 0 |  | 331.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.543 | 1 | 0 | 38950.543 | 1 | 0 |  | 516.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5451 | 1 | 0 | 38950.5452 | 1 | 0 |  | 701 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5473 | 1 | 0 | 38950.5473 | 2 | 1 |  | 885.5 | 1030.5 | 0.06105 | 0 | 0.1221 | 0.06105 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5494 | 1180 | 1156 | 38950.5494 | 1110 | 1081 |  | 1070.5 | 1215.5 | 72.0391 | 70.5739 | 67.7656 | 65.9951 | 0.72039 | 0.70574 | 0.67766 | 0.65995 | 0.014652 | 0.017705 | 3320.0827 | 28179.2309 | 19.2207
38950.5516 | 1112 | 1082 | 38950.5516 | 1115 | 925 |  | 1255.5 | 1400.5 | 67.8877 | 66.0562 | 68.0708 | 56.4713 | 0.67888 | 0.66056 | 0.68071 | 0.56471 | 0.018315 | 0.116 | 1.0317 | 1.1155 | 0.082564
38950.5537 | 1180 | 1156 | 38950.5537 | 1206 | 963 |  | 1440 | 1585 | 72.0391 | 70.5739 | 73.6264 | 58.7912 | 0.72039 | 0.70574 | 0.73626 | 0.58791 | 0.014652 | 0.14835 | 103.0179 | 131.1123 | 10.9428
38950.5558 | 1167 | 1199 | 38950.5558 | 1201 | 1184 |  | 1625 | 1770 | 71.2454 | 73.199 | 73.3211 | 72.2833 | 0.71245 | 0.73199 | 0.73321 | 0.72283 | 0.019536 | 0.010379 | 6326.3987 | 7033.7148 | 20.8035

## B4-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 134.7607 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38950.5365 | 1 | 0 | 38950.5365 | 1 | 0 |  | -46.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.5386 | 1 | 0 | 38950.5386 | 1 | 0 |  | 138.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.5408 | 1 | 0 | 38950.5408 | 1 | 0 |  | 323 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.5429 | 1 | 0 | 38950.5429 | 1 | 0 |  | 508 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.545 | 1 | 0 | 38950.545 | 1 | 0 |  | 692.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.5472 | 1 | 0 | 38950.5472 | 1 | 0 |  | 877.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 220638 | 220638 | 220637.9994
38950.5493 | 6 | 0 | 38950.5493 | 2072 | 0 |  | 1062 | 1207 | 0.3663 | 0 | 126.4957 | 0 | 0.003663 | 0 | 1.265 | 0 | 0.003663 | 1.265 | 36689.6667 | 6.5338 | 36689.663
38950.5514 | 8 | 0 | 38950.5515 | 2089 | 0 |  | 1247 | 1392 | 0.4884 | 0 | 127.5336 | 0 | 0.004884 | 0 | 1.2753 | 0 | 0.004884 | 1.2753 | 27492.25 | 5.6668 | 27492.2451
38950.5536 | 146 | 0 | 38950.5536 | 2191 | 0 |  | 1431.5 | 1576.5 | 8.9133 | 0 | 133.7607 | 0 | 0.089133 | 0 | 1.3376 | 0 | 0.089133 | 1.3376 | 1411.9041 | 0.7476 | 1411.815
38950.5557 | 162 | 0 | 38950.5557 | 2016 | 0 |  | 1616.5 | 1761.5 | 9.8901 | 0 | 123.0769 | 0 | 0.098901 | 0 | 1.2308 | 0 | 0.098901 | 1.2308 | 1262.5802 | 9.4931 | 1262.4813

## B4-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 157.7766 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38950.5364 | 1 | 0 | 38950.5365 | 1 | 0 |  | -49.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38950.5386 | 1 | 0 | 38950.5386 | 1 | 0 |  | 135.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38950.5407 | 1 | 0 | 38950.5407 | 1 | 0 |  | 320.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38950.5429 | 1 | 0 | 38950.5429 | 1 | 0 |  | 505 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38950.545 | 1 | 0 | 38950.545 | 1 | 0 |  | 690 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258338 | 258338 | 258337.9994
38950.5471 | 2 | 0 | 38950.5472 | 1 | 0 |  | 874.5 | 1019.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 129119 | 258338 | 129118.9988
38950.5493 | 6 | 0 | 38950.5493 | 2143 | 1 |  | 1059.5 | 1204.5 | 0.3663 | 0 | 130.8303 | 0.06105 | 0.003663 | 0 | 1.3083 | 0.0006105 | 0.003663 | 1.3077 | 42973 | 20.6527 | 42972.9963
38950.5514 | 8 | 0 | 38950.5514 | 2262 | 0 |  | 1244 | 1389 | 0.4884 | 0 | 138.0952 | 0 | 0.004884 | 0 | 1.381 | 0 | 0.004884 | 1.381 | 32204.75 | 14.252 | 32204.7451
38950.5536 | 144 | 0 | 38950.5536 | 2568 | 0 |  | 1429 | 1574 | 8.7912 | 0 | 156.7766 | 0 | 0.087912 | 0 | 1.5678 | 0 | 0.087912 | 1.5678 | 1694.7083 | 0.63785 | 1694.6204
38950.5557 | 138 | 0 | 38950.5557 | 2335 | 0 |  | 1613.5 | 1758.5 | 8.4249 | 0 | 142.5519 | 0 | 0.084249 | 0 | 1.4255 | 0 | 0.084249 | 1.4255 | 1772.7391 | 10.6801 | 1772.6549

## B4-D8
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 155.7009 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38950.5364 | 1 | 0 | 38950.5364 | 1 | 0 |  | -52 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.5386 | 1 | 0 | 38950.5386 | 1 | 0 |  | 133 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.5407 | 1 | 0 | 38950.5407 | 1 | 0 |  | 317.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.5428 | 1 | 0 | 38950.5428 | 1 | 0 |  | 502.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.545 | 1 | 0 | 38950.545 | 1 | 0 |  | 687 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.5471 | 1 | 0 | 38950.5471 | 1 | 0 |  | 872 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
38950.5492 | 5 | 0 | 38950.5493 | 2214 | 1 |  | 1056.5 | 1201.5 | 0.30525 | 0 | 135.1648 | 0.06105 | 0.0030525 | 0 | 1.3516 | 0.0006105 | 0.0030525 | 1.351 | 50907.6 | 15.2454 | 50907.5969
38950.5514 | 7 | 0 | 38950.5514 | 2495 | 0 |  | 1241.5 | 1386.5 | 0.42735 | 0 | 152.3199 | 0 | 0.0042735 | 0 | 1.5232 | 0 | 0.0042735 | 1.5232 | 36334 | 2.2196 | 36333.9957
38950.5535 | 150 | 0 | 38950.5535 | 2534 | 0 |  | 1426 | 1571 | 9.1575 | 0 | 154.7009 | 0 | 0.091575 | 0 | 1.547 | 0 | 0.091575 | 1.547 | 1600.2533 | 0.64641 | 1600.1618
38950.5557 | 175 | 0 | 38950.5557 | 2039 | 0 |  | 1611 | 1756 | 10.6838 | 0 | 124.4811 | 0 | 0.10684 | 0 | 1.2448 | 0 | 0.10684 | 1.2448 | 1357.36 | 25.0799 | 1357.2532

## B4-D7
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 155.5788 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38950.5364 | 1 | 0 | 38950.5364 | 1 | 0 |  | -55 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5385 | 1 | 0 | 38950.5385 | 1 | 0 |  | 130 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5407 | 1 | 0 | 38950.5407 | 1 | 0 |  | 314.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5428 | 1 | 0 | 38950.5428 | 1 | 0 |  | 499.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5449 | 1 | 0 | 38950.545 | 1 | 0 |  | 684.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5471 | 1 | 0 | 38950.5471 | 1 | 0 |  | 869 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38950.5492 | 2 | 0 | 38950.5492 | 2532 | 0 |  | 1053.5 | 1198.5 | 0.1221 | 0 | 154.5788 | 0 | 0.001221 | 0 | 1.5458 | 0 | 0.001221 | 1.5458 | 127319 | 0.64692 | 127318.9988
38950.5514 | 6 | 0 | 38950.5514 | 2008 | 0 |  | 1238.5 | 1383.5 | 0.3663 | 0 | 122.5885 | 0 | 0.003663 | 0 | 1.2259 | 0 | 0.003663 | 1.2259 | 42373 | 26.9114 | 42372.9963
38950.5535 | 143 | 0 | 38950.5535 | 1851 | 0 |  | 1423.5 | 1568.5 | 8.7302 | 0 | 113.0037 | 0 | 0.087302 | 0 | 1.13 | 0 | 0.087302 | 1.13 | 1682.0839 | 37.6759 | 1681.9966
38950.5556 | 174 | 0 | 38950.5556 | 2428 | 0 |  | 1608 | 1753 | 10.6227 | 0 | 148.2295 | 0 | 0.10623 | 0 | 1.4823 | 0 | 0.10623 | 1.4823 | 1364.5862 | 4.958 | 1364.48

## B4-C6
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38950.5364 | 1 | 0 | 38950.5364 | 1 | 0 |  | -57.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5385 | 1 | 0 | 38950.5385 | 1 | 0 |  | 127 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5406 | 1 | 0 | 38950.5406 | 1 | 0 |  | 312 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5428 | 1 | 0 | 38950.5428 | 1 | 0 |  | 496.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5449 | 1 | 0 | 38950.5449 | 1 | 0 |  | 681.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.547 | 1 | 0 | 38950.5471 | 1 | 0 |  | 866.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5492 | 3 | 0 | 38950.5492 | 3 | 0 |  | 1051 | 1196 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38950.5513 | 5 | 0 | 38950.5513 | 4 | 0 |  | 1235.5 | 1380.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5535 | 109 | 0 | 38950.5535 | 4 | 0 |  | 1420.5 | 1565.5 | 6.6545 | 0 | 0.2442 | 0 | 0.066545 | 0 | 0.002442 | 0 | 0.066545 | 0.002442 | 1838.5505 | 52725.5 | 1838.4839
38950.5556 | 132 | 0 | 38950.5556 | 4 | 0 |  | 1605.5 | 1750.5 | 8.0586 | 0 | 0.2442 | 0 | 0.080586 | 0 | 0.002442 | 0 | 0.080586 | 0.002442 | 1500.7727 | 52725.5 | 1500.6921

## B4-C5
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38950.5363 | 1 | 0 | 38950.5363 | 1 | 0 |  | -60.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5385 | 1 | 0 | 38950.5385 | 1 | 0 |  | 124.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5406 | 1 | 0 | 38950.5406 | 1 | 0 |  | 309 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5427 | 1 | 0 | 38950.5428 | 1 | 0 |  | 494 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5449 | 1 | 0 | 38950.5449 | 1 | 0 |  | 678.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.547 | 1 | 0 | 38950.547 | 1 | 0 |  | 863.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5491 | 3 | 0 | 38950.5492 | 3 | 0 |  | 1048 | 1193 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38950.5513 | 5 | 0 | 38950.5513 | 4 | 0 |  | 1233 | 1378 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5534 | 104 | 0 | 38950.5534 | 4 | 0 |  | 1418 | 1563 | 6.3492 | 0 | 0.2442 | 0 | 0.063492 | 0 | 0.002442 | 0 | 0.063492 | 0.002442 | 1931.75 | 52725.5 | 1931.6865
38950.5556 | 146 | 0 | 38950.5556 | 4 | 0 |  | 1602.5 | 1747.5 | 8.9133 | 0 | 0.2442 | 0 | 0.089133 | 0 | 0.002442 | 0 | 0.089133 | 0.002442 | 1347.274 | 52725.5 | 1347.1848

## B3-E10
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 154.3578 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38950.5362 | 1 | 0 | 38950.5362 | 1 | 0 |  | -68.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5384 | 1 | 0 | 38950.5384 | 1 | 0 |  | 116 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5405 | 1 | 0 | 38950.5405 | 1 | 0 |  | 300.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5426 | 1 | 0 | 38950.5427 | 1 | 0 |  | 485.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5448 | 1 | 0 | 38950.5448 | 1 | 0 |  | 670.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5469 | 1 | 0 | 38950.5469 | 1 | 0 |  | 855 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38950.5491 | 5 | 0 | 38950.5491 | 2013 | 10 |  | 1040 | 1185 | 0.30525 | 0 | 122.8938 | 0.6105 | 0.0030525 | 0 | 1.2289 | 0.006105 | 0.0030525 | 1.2228 | 50467.6 | 26.2297 | 50467.5969
38950.5512 | 7 | 0 | 38950.5512 | 2512 | 0 |  | 1224.5 | 1369.5 | 0.42735 | 0 | 153.3578 | 0 | 0.0042735 | 0 | 1.5336 | 0 | 0.0042735 | 1.5336 | 36019.7143 | 0.65207 | 36019.71
38950.5533 | 92 | 0 | 38950.5533 | 2042 | 0 |  | 1409.5 | 1554.5 | 5.6166 | 0 | 124.6642 | 0 | 0.056166 | 0 | 1.2466 | 0 | 0.056166 | 1.2466 | 2648.2391 | 23.8188 | 2648.183
38950.5555 | 138 | 0 | 38950.5555 | 2111 | 0 |  | 1594.5 | 1739.5 | 8.4249 | 0 | 128.8767 | 0 | 0.084249 | 0 | 1.2888 | 0 | 0.084249 | 1.2888 | 1732.1594 | 19.7717 | 1732.0752

## B3-E9
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 158.2039 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38950.5362 | 1 | 0 | 38950.5362 | 1 | 0 |  | -71.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.5383 | 1 | 0 | 38950.5383 | 1 | 0 |  | 113 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.5405 | 1 | 0 | 38950.5405 | 1 | 0 |  | 298 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.5426 | 1 | 0 | 38950.5426 | 1 | 0 |  | 482.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.5447 | 1 | 0 | 38950.5448 | 1 | 0 |  | 667.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.5469 | 1 | 0 | 38950.5469 | 1 | 0 |  | 852.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
38950.549 | 6 | 0 | 38950.549 | 2023 | 31 |  | 1037 | 1182 | 0.3663 | 0 | 123.5043 | 1.8926 | 0.003663 | 0 | 1.235 | 0.018926 | 0.003663 | 1.2161 | 43089.6667 | 30.0894 | 43089.663
38950.5512 | 6 | 0 | 38950.5512 | 2079 | 0 |  | 1222 | 1367 | 0.3663 | 0 | 126.9231 | 0 | 0.003663 | 0 | 1.2692 | 0 | 0.003663 | 1.2692 | 43089.6667 | 24.6455 | 43089.663
38950.5533 | 104 | 0 | 38950.5533 | 2575 | 0 |  | 1406.5 | 1551.5 | 6.3492 | 0 | 157.2039 | 0 | 0.063492 | 0 | 1.572 | 0 | 0.063492 | 1.572 | 2391.7115 | 0.63612 | 2391.648
38950.5554 | 123 | 0 | 38950.5555 | 2572 | 0 |  | 1591.5 | 1736.5 | 7.5092 | 0 | 157.0208 | 0 | 0.075092 | 0 | 1.5702 | 0 | 0.075092 | 1.5702 | 2006.813 | 0.7535 | 2006.7379

## B3-D8
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 152.4042 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38950.5362 | 1 | 0 | 38950.5362 | 1 | 0 |  | -74.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.5383 | 1 | 0 | 38950.5383 | 1 | 0 |  | 110.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.5404 | 1 | 0 | 38950.5405 | 1 | 0 |  | 295 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.5426 | 1 | 0 | 38950.5426 | 1 | 0 |  | 480 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.5447 | 1 | 0 | 38950.5447 | 1 | 0 |  | 664.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.5469 | 1 | 0 | 38950.5469 | 1 | 0 |  | 849.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
38950.549 | 5 | 0 | 38950.549 | 2114 | 0 |  | 1034.5 | 1179.5 | 0.30525 | 0 | 129.0598 | 0 | 0.0030525 | 0 | 1.2906 | 0 | 0.0030525 | 1.2906 | 49827.6 | 18.088 | 49827.5969
38950.5511 | 6 | 0 | 38950.5511 | 2480 | 1 |  | 1219 | 1364 | 0.3663 | 0 | 151.4042 | 0.06105 | 0.003663 | 0 | 1.514 | 0.0006105 | 0.003663 | 1.5134 | 41506.3333 | 0.70109 | 41506.3297
38950.5533 | 74 | 1 | 38950.5533 | 2206 | 0 |  | 1403.5 | 1548.5 | 4.5177 | 0.06105 | 134.6764 | 0 | 0.045177 | 0.0006105 | 1.3468 | 0 | 0.044567 | 1.3468 | 3703.7718 | 13.1632 | 28165.5968
38950.5554 | 105 | 1 | 38950.5554 | 2434 | 1 |  | 1588.5 | 1733.5 | 6.4103 | 0.06105 | 148.5958 | 0.06105 | 0.064103 | 0.0006105 | 1.486 | 0.0006105 | 0.063492 | 1.4853 | 3679.1848 | 2.5639 | 5975.584

## B3-D7
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 150.8168 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38950.5361 | 1 | 0 | 38950.5361 | 1 | 0 |  | -77.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.5383 | 1 | 0 | 38950.5383 | 1 | 0 |  | 107.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.5404 | 1 | 0 | 38950.5404 | 1 | 0 |  | 292.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.5425 | 1 | 0 | 38950.5426 | 1 | 0 |  | 477 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.5447 | 1 | 0 | 38950.5447 | 1 | 0 |  | 662 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.5468 | 1 | 0 | 38950.5468 | 1 | 0 |  | 846.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246938 | 246938 | 246937.9994
38950.549 | 2 | 0 | 38950.549 | 2419 | 0 |  | 1031.5 | 1176.5 | 0.1221 | 0 | 147.6801 | 0 | 0.001221 | 0 | 1.4768 | 0 | 0.001221 | 1.4768 | 123419 | 2.124 | 123418.9988
38950.5511 | 5 | 1 | 38950.5511 | 2454 | 1 |  | 1216 | 1361 | 0.30525 | 0.06105 | 149.8168 | 0.06105 | 0.0030525 | 0.0006105 | 1.4982 | 0.0006105 | 0.002442 | 1.4976 | 1691.4037 | 0.70542 | 1726.247
38950.5532 | 84 | 2 | 38950.5533 | 2259 | 1 |  | 1401 | 1546 | 5.1282 | 0.1221 | 137.9121 | 0.06105 | 0.051282 | 0.001221 | 1.3791 | 0.0006105 | 0.050061 | 1.3785 | 3935.5911 | 9.3615 | 10205.3032
38950.5554 | 103 | 1 | 38950.5554 | 2434 | 1 |  | 1586 | 1731 | 6.2882 | 0.06105 | 148.5958 | 0.06105 | 0.062882 | 0.0006105 | 1.486 | 0.0006105 | 0.062271 | 1.4853 | 6740.2552 | 1.4953 | 3486.2768

## B3-C6
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38950.5361 | 1 | 0 | 38950.5361 | 1 | 0 |  | -80 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5382 | 1 | 0 | 38950.5382 | 1 | 0 |  | 104.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5404 | 1 | 0 | 38950.5404 | 1 | 0 |  | 289.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5425 | 1 | 0 | 38950.5425 | 1 | 0 |  | 474.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5446 | 1 | 0 |  | 1 | 0 |  | 658 | 803 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5468 | 1 | 0 | 38950.5468 | 1 | 0 |  | 844 | 989 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5489 | 2 | 0 | 38950.5489 | 2 | 0 |  | 1028.5 | 1173.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38950.5511 | 4 | 2 | 38950.5511 | 4 | 1 |  | 1213.5 | 1358.5 | 0.2442 | 0.1221 | 0.2442 | 0.06105 | 0.002442 | 0.001221 | 0.002442 | 0.0006105 | 0.001221 | 0.0018315 | 105601.1662 | 70322.8643 | 105201.4023
38950.5532 | 83 | 4 | 38950.5532 | 4 | 2 |  | 1398.5 | 1543.5 | 5.0672 | 0.2442 | 0.2442 | 0.1221 | 0.050672 | 0.002442 | 0.002442 | 0.001221 | 0.04823 | 0.001221 | 2569.7642 | 109720.6789 | 50604.3789
38950.5553 | 117 | 4 | 38950.5554 | 4 | 2 |  | 1583 | 1728 | 7.1429 | 0.2442 | 0.2442 | 0.1221 | 0.071429 | 0.002442 | 0.002442 | 0.001221 | 0.068987 | 0.001221 | 1766.4453 | 111778.9004 | 49755.9871

## B3-C5
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38950.5361 | 1 | 0 | 38950.5361 | 1 | 0 |  | -82.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5382 | 2 | 0 | 38950.5382 | 1 | 0 |  | 102 | 247 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38950.5403 | 1 | 0 | 38950.5403 | 1 | 0 |  | 286.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5425 | 1 | 0 | 38950.5425 | 1 | 0 |  | 471.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5446 | 1 | 0 | 38950.5446 | 1 | 0 |  | 656.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5467 | 1 | 0 | 38950.5468 | 1 | 0 |  | 841 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5489 | 2 | 0 | 38950.5489 | 2 | 0 |  | 1026 | 1171 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38950.551 | 5 | 8 | 38950.551 | 5 | 3 |  | 1210.5 | 1355.5 | 0.30525 | 0.4884 | 0.30525 | 0.18315 | 0.0030525 | 0.004884 | 0.0030525 | 0.0018315 | 0.0018315 | 0.001221 | 70445.1816 | 105625.9109 | 26225.4214
38950.5532 | 60 | 13 | 38950.5532 | 4 | 6 |  | 1395.5 | 1540.5 | 3.663 | 0.79365 | 0.2442 | 0.3663 | 0.03663 | 0.0079365 | 0.002442 | 0.003663 | 0.028694 | 0.001221 | 4369.195 | 113225.3387 | 15678.6143
38950.5553 | 95 | 12 | 38950.5553 | 4 | 6 |  | 1580 | 1725 | 5.7998 | 0.7326 | 0.2442 | 0.3663 | 0.057998 | 0.007326 | 0.002442 | 0.003663 | 0.050672 | 0.001221 | 2431.6417 | 120291.8153 | 16702.948

## B3-B4
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38950.536 | 1 | 0 | 38950.536 | 1 | 0 |  | -85.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5382 | 1 | 0 | 38950.5382 | 1 | 0 |  | 99 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5403 | 1 | 0 | 38950.5403 | 2 | 0 |  | 284 | 429 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
| 1 | 0 | 38950.5425 | 1 | 0 |  | 469 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5446 | 1 | 0 | 38950.5446 | 1 | 0 |  | 653.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5467 | 1 | 0 | 38950.5467 | 1 | 0 |  | 838.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5489 | 2 | 0 | 38950.5489 | 2 | 0 |  | 1023 | 1168 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38950.551 | 568 | 514 | 38950.551 | 1096 | 1043 |  | 1208 | 1353 | 34.6764 | 31.3797 | 66.9109 | 63.6752 | 0.34676 | 0.3138 | 0.66911 | 0.63675 | 0.032967 | 0.032357 | 3740.3304 | 4049.4907 | 195.7535
38950.5531 | 1114 | 1104 | 38950.5531 | 1020 | 959 |  | 1392.5 | 1537.5 | 68.0098 | 67.3993 | 62.2711 | 58.547 | 0.6801 | 0.67399 | 0.62271 | 0.58547 | 0.006105 | 0.037241 | 58.8736 | 65.4459 | 3.7615
38950.5553 | 1227 | 1077 | 38950.5553 | 1270 | 1133 |  | 1577.5 | 1722.5 | 74.9084 | 65.7509 | 77.5336 | 69.1697 | 0.74908 | 0.65751 | 0.77534 | 0.6917 | 0.091575 | 0.083639 | 2243.5932 | 974.5823 | 16.0824

## A2-C6
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38950.5358 | 1 | 0 | 38950.5358 | 1 | 0 |  | -105 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5379 | 1 | 0 | 38950.538 | 1 | 0 |  | 79.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5401 | 1 | 0 | 38950.5401 | 1 | 0 |  | 264.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5422 | 1 | 0 | 38950.5422 | 1 | 0 |  | 449 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5444 | 1 | 0 | 38950.5444 | 1 | 0 |  | 634 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5465 | 1 | 0 | 38950.5465 | 1 | 0 |  | 818.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5486 | 4 | 0 | 38950.5486 | 2 | 0 |  | 1003.5 | 1148.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 52725.5 | 105551 | 52725.4976
38950.5508 | 5 | 0 | 38950.5508 | 4 | 0 |  | 1188.5 | 1333.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5529 | 4 | 0 | 38950.5529 | 4 | 0 |  | 1373 | 1518 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38950.555 | 4 | 0 | 38950.5551 | 5 | 0 |  | 1557.5 | 1702.5 | 0.2442 | 0 | 0.30525 | 0 | 0.002442 | 0 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 52725.5 | 42160.4 | 52725.4976

## A2-C5
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38950.5358 | 1 | 0 | 38950.5358 | 1 | 0 |  | -108 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5379 | 1 | 0 | 38950.5379 | 1 | 0 |  | 76.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.54 | 1 | 0 | 38950.5401 | 1 | 0 |  | 261.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5422 | 1 | 0 | 38950.5422 | 1 | 0 |  | 446.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5443 | 1 | 0 | 38950.5443 | 1 | 0 |  | 631 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5465 | 1 | 0 | 38950.5465 | 1 | 0 |  | 816 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5486 | 145 | 0 | 38950.5486 | 2 | 0 |  | 1000.5 | 1145.5 | 8.8523 | 0 | 0.1221 | 0 | 0.088523 | 0 | 0.001221 | 0 | 0.088523 | 0.001221 | 1357.2552 | 105551 | 1357.1666
38950.5507 | 5 | 0 | 38950.5508 | 5 | 0 |  | 1185.5 | 1330.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 42160.4 | 42160.4 | 42160.3969
38950.5529 | 4 | 0 | 38950.5529 | 4 | 0 |  | 1370.5 | 1515.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38950.555 | 4 | 0 | 38950.555 | 4 | 0 |  | 1555 | 1700 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## A2-B4
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38950.5357 | 1 | 0 | 38950.5358 | 1 | 0 |  | -111 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5379 | 1 | 0 | 38950.5379 | 1 | 0 |  | 74 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.54 | 1 | 0 | 38950.54 | 1 | 0 |  | 258.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5422 | 1 | 0 | 38950.5422 | 1 | 0 |  | 443.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5443 | 1 | 0 | 38950.5443 | 1 | 0 |  | 628.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5464 | 1 | 0 | 38950.5464 | 1 | 0 |  | 813 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5486 | 43 | 0 | 38950.5486 | 71 | 0 |  | 998 | 1143 | 2.6252 | 0 | 4.3346 | 0 | 0.026252 | 0 | 0.043346 | 0 | 0.026252 | 0.043346 | 4814 | 2876.0845 | 4813.9737
38950.5507 | 5 | 0 | 38950.5507 | 4 | 0 |  | 1182.5 | 1327.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38950.5528 | 4 | 0 |  | 4 | 0 |  | 1367 | 1512 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38950.555 | 4 | 0 | 38950.555 | 4 | 0 |  | 1552 | 1697 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## A2-B3
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38950.5357 | 1 | 0 | 38950.5357 | 1 | 0 |  | -113.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5378 | 1 | 0 | 38950.5379 | 1 | 0 |  | 71 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.54 | 1 | 0 | 38950.54 | 1 | 0 |  | 256 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5421 | 1 | 0 | 38950.5421 | 1 | 0 |  | 440.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5443 | 1 | 0 | 38950.5443 | 1 | 0 |  | 625.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5464 | 1 | 0 | 38950.5464 | 1 | 0 |  | 810.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5485 | 36 | 0 | 38950.5486 | 2 | 0 |  | 995 | 1140 | 2.1978 | 0 | 0.1221 | 0 | 0.021978 | 0 | 0.001221 | 0 | 0.021978 | 0.001221 | 5769.5 | 105551 | 5769.478
38950.5507 | 4 | 0 | 38950.5507 | 5 | 0 |  | 1179.5 | 1324.5 | 0.2442 | 0 | 0.30525 | 0 | 0.002442 | 0 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 52725.5 | 42160.4 | 52725.4976
38950.5528 | 5 | 0 | 38950.5528 | 75 | 0 |  | 1364.5 | 1509.5 | 0.30525 | 0 | 4.5788 | 0 | 0.0030525 | 0 | 0.045788 | 0 | 0.0030525 | 0.045788 | 42160.4 | 2717.36 | 42160.3969
38950.555 | 4 | 0 | 38950.555 | 155 | 0 |  | 1549.5 | 1694.5 | 0.2442 | 0 | 9.4628 | 0 | 0.002442 | 0 | 0.094628 | 0 | 0.002442 | 0.094628 | 52725.5 | 1263.2387 | 52725.4976

## A1-C6
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38950.5355 | 1 | 0 | 38950.5355 | 1 | 0 |  | -133 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5376 | 1 | 0 | 38950.5376 | 1 | 0 |  | 51.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5398 | 1 | 0 | 38950.5398 | 1 | 0 |  | 236.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5419 | 1 | 0 | 38950.5419 | 1 | 0 |  | 421 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.544 | 1 | 0 | 38950.5441 | 1 | 0 |  | 606 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5462 | 1 | 0 | 38950.5462 | 1 | 0 |  | 790.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5483 | 41 | 1 | 38950.5483 | 2 | 0 |  | 975.5 | 1120.5 | 2.5031 | 0.06105 | 0.1221 | 0 | 0.025031 | 0.0006105 | 0.001221 | 0 | 0.02442 | 0.001221 | 5180.1727 | 105551 | 206905.9754
38950.5504 | 5 | 1 | 38950.5505 | 5 | 1 |  | 1160 | 1305 | 0.30525 | 0.06105 | 0.30525 | 0.06105 | 0.0030525 | 0.0006105 | 0.0030525 | 0.0006105 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 210303.1358
38950.5526 | 4 | 0 | 38950.5526 | 4 | 1 |  | 1345 | 1490 | 0.2442 | 0 | 0.2442 | 0.06105 | 0.002442 | 0 | 0.002442 | 0.0006105 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38950.5547 | 4 | 0 | 38950.5547 | 4 | 0 |  | 1529.5 | 1674.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976

## A1-C5
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38950.5354 | 1 | 0 | 38950.5355 | 1 | 0 |  | -136 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 38950.5376 | 1 | 0 |  | 49 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5397 | 1 | 0 | 38950.5397 | 1 | 0 |  | 233.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5419 | 1 | 0 | 38950.5419 | 1 | 0 |  | 418.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.544 | 1 | 0 | 38950.544 | 1 | 0 |  | 603 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5461 | 1 | 0 | 38950.5462 | 1 | 0 |  | 788 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5483 | 4 | 1 | 38950.5483 | 2 | 1 |  | 972.5 | 1117.5 | 0.2442 | 0.06105 | 0.1221 | 0.06105 | 0.002442 | 0.0006105 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 70311.7532 | 211402.6648 | 210702.3313
38950.5504 | 5 | 2 | 38950.5504 | 5 | 1 |  | 1157.5 | 1302.5 | 0.30525 | 0.1221 | 0.30525 | 0.06105 | 0.0030525 | 0.001221 | 0.0030525 | 0.0006105 | 0.0018315 | 0.002442 | 70356.3031 | 52719.2329 | 105101.6389
38950.5525 | 5 | 1 | 38950.5526 | 5 | 0 |  | 1342 | 1487 | 0.30525 | 0.06105 | 0.30525 | 0 | 0.0030525 | 0.0006105 | 0.0030525 | 0 | 0.002442 | 0.0030525 | 52731.7685 | 42160.4 | 210203.4198
38950.5547 | 4 | 1 | 38950.5547 | 5 | 1 |  | 1527 | 1672 | 0.2442 | 0.06105 | 0.30525 | 0.06105 | 0.002442 | 0.0006105 | 0.0030525 | 0.0006105 | 0.0018315 | 0.002442 | 70345.1445 | 52719.2359 | 210402.8992

## A1-B4
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38950.5354 | 1 | 0 | 38950.5354 | 1 | 0 |  | -138.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5375 | 1 | 0 | 38950.5376 | 1 | 0 |  | 46 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5397 | 1 | 0 | 38950.5397 | 1 | 0 |  | 230.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5418 | 1 | 0 | 38950.5418 | 1 | 0 |  | 415.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.544 | 1 | 0 | 38950.544 | 1 | 0 |  | 600.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5461 | 1 | 0 | 38950.5461 | 1 | 0 |  | 785 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5482 | 4 | 4 | 38950.5483 | 2 | 3 |  | 969.5 | 1114.5 | 0.2442 | 0.2442 | 0.1221 | 0.18315 | 0.002442 | 0.002442 | 0.001221 | 0.0018315 | 0 | 0.0006105 | 111304285.01 | 211101.431 | 52600.5828
38950.5504 | 5 | 4 | 38950.5504 | 5 | 3 |  | 1154.5 | 1299.5 | 0.30525 | 0.2442 | 0.30525 | 0.18315 | 0.0030525 | 0.002442 | 0.0030525 | 0.0018315 | 0.0006105 | 0.001221 | 211604.4762 | 105475.7686 | 52550.6775
38950.5525 | 5 | 2 | 38950.5525 | 53 | 1 |  | 1339.5 | 1484.5 | 0.30525 | 0.1221 | 3.2357 | 0.06105 | 0.0030525 | 0.001221 | 0.032357 | 0.0006105 | 0.0018315 | 0.031746 | 71470.021 | 3961.6835 | 102708.4543
38950.5547 | 4 | 2 | 38950.5547 | 140 | 1 |  | 1524.5 | 1669.5 | 0.2442 | 0.1221 | 8.547 | 0.06105 | 0.002442 | 0.001221 | 0.08547 | 0.0006105 | 0.001221 | 0.08486 | 113443.0552 | 1419.4479 | 98417.4945

## A1-B3
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38950.5354 | 1 | 0 | 38950.5354 | 1 | 0 |  | -141.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5375 | 1 | 0 | 38950.5375 | 1 | 0 |  | 43 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5397 | 1 | 0 | 38950.5397 | 1 | 0 |  | 228 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5418 | 1 | 0 | 38950.5418 | 1 | 0 |  | 412.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5439 | 1 | 0 | 38950.5439 | 1 | 0 |  | 597.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5461 | 1 | 0 | 38950.5461 | 1 | 0 |  | 782.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5482 | 5 | 15 | 38950.5482 | 2 | 6 |  | 967 | 1112 | 0.30525 | 0.91575 | 0.1221 | 0.3663 | 0.0030525 | 0.0091575 | 0.001221 | 0.003663 | 0.006105 | 0.002442 | 21139.858 | 53152.65 | 13927.2643
38950.5503 | 5 | 15 | 38950.5504 | 5 | 7 |  | 1151.5 | 1296.5 | 0.30525 | 0.91575 | 0.30525 | 0.42735 | 0.0030525 | 0.0091575 | 0.0030525 | 0.0042735 | 0.006105 | 0.001221 | 21109.7439 | 107178.0137 | 13940.4598
38950.5525 | 5 | 8 | 38950.5525 | 45 | 4 |  | 1336.5 | 1481.5 | 0.30525 | 0.4884 | 2.7473 | 0.2442 | 0.0030525 | 0.004884 | 0.027473 | 0.002442 | 0.0018315 | 0.025031 | 74189.0913 | 5044.6146 | 25740.0028
38950.5546 | 5 | 8 | 38950.5546 | 156 | 4 |  | 1521.5 | 1666.5 | 0.30525 | 0.4884 | 9.5238 | 0.2442 | 0.0030525 | 0.004884 | 0.095238 | 0.002442 | 0.0018315 | 0.092796 | 88621.9576 | 1287.5514 | 24358.4102

## A1-A2
Penlight Test 44 |  |  | 2006-08-21 | 12:53 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38950.5353 | 1 | 0 | 38950.5354 | 1 | 0 |  | -144.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5375 | 1 | 0 | 38950.5375 | 1 | 0 |  | 40.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5396 | 1 | 0 | 38950.5396 | 1 | 0 |  | 225.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5418 | 1 | 0 | 38950.5418 | 1 | 0 |  | 410 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5439 | 1 | 0 | 38950.5439 | 1 | 0 |  | 594.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.546 | 1 | 0 | 38950.5461 | 1 | 0 |  | 779.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38950.5482 | 1064 | 1014 | 38950.5482 | 1157 | 1112 |  | 964 | 1109 | 64.9573 | 61.9048 | 70.6349 | 67.8877 | 0.64957 | 0.61905 | 0.70635 | 0.67888 | 0.030525 | 0.027473 | 5743.1552 | 3195.2677 | 3.3488
38950.5503 | 923 | 945 | 38950.5503 | 958 | 986 |  | 1149 | 1294 | 56.3492 | 57.6923 | 58.486 | 60.1954 | 0.56349 | 0.57692 | 0.58486 | 0.60195 | 0.013431 | 0.017094 | 42182.143 | 4927.3018 | 25.4123
38950.5525 | 779 | 742 | 38950.5525 | 734 | 700 |  | 1333.5 | 1478.5 | 47.558 | 45.2991 | 44.8107 | 42.735 | 0.47558 | 0.45299 | 0.44811 | 0.42735 | 0.022589 | 0.020757 | 5118.0554 | 6785.5372 | 78.6283
38950.5546 | 862 | 811 | 38950.5546 | 808 | 774 |  | 1518.5 | 1663.5 | 52.6252 | 49.5116 | 49.3284 | 47.2527 | 0.52625 | 0.49512 | 0.49328 | 0.47253 | 0.031136 | 0.020757 | 2577.8349 | 32832.3157 | 54.0917

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 44 |  |  | 2006-08-21 | 12:53
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | C5-C | Penlight Time | C6-C | Penlight Time | C7-C | Penlight Time | Minimums
-127 | 218124.6661 |  | -90.75 | 211201.9994 | -96.75 | 217157.9994 | -84.6667 | 218457.9994 | -75.75 | 219124.6661 | -71 | 216691.3327 | -34.25 | 244748.6661 | -127 | 211201.9994
57.6667 | 218124.6661 |  | 94 | 211201.9994 | 87.8333 | 199549.4993 | 100.0833 | 218457.9994 | 109 | 201516.166 | 113.5 | 216691.3327 | 150.5833 | 244748.6661 | 57.6667 | 199549.4993
242.4167 | 218124.6661 |  | 278.8333 | 211201.9994 | 272.75 | 217157.9994 | 284.75 | 218457.9994 | 293.6667 | 219124.6661 | 298.4167 | 216691.3327 | 335.1667 | 244748.6661 | 242.4167 | 211201.9994
427.1667 | 218124.6661 |  | 463.5833 | 211201.9994 | 457.5 | 217157.9994 | 469.6667 | 218457.9994 | 478.5833 | 219124.6661 | 483.1667 | 216691.3327 | 520 | 244748.6661 | 427.1667 | 211201.9994
612 | 218124.6661 |  | 648.3333 | 211201.9994 | 642.1667 | 217157.9994 | 654.5 | 218457.9994 | 663.25 | 219124.6661 | 667.8333 | 216641.3601 | 704.9167 | 244698.6935 | 612 | 211201.9994
796.75 | 218124.6661 |  | 833.1667 | 184789.2491 | 827.1667 | 217157.9994 | 839.25 | 218457.9994 | 848.0833 | 219124.6661 | 852.6667 | 216691.3327 | 889.5833 | 218335.9158 | 796.75 | 184789.2491
981.4167 | 89101.1832 |  | 1017.9167 | 17804.977 | 1011.8333 | 76628.1229 | 1023.8333 | 71825.4251 | 1032.75 | 71900.1256 | 1037.5 | 79357.0034 | 1074.4167 | 71234.8932 | 981.4167 | 17804.977
1166.1667 | 69656.8391 |  | 1202.6667 | 36898.7496 | 1196.5 | 33335.7969 | 1208.6667 | 36933.4364 | 1217.6667 | 36228.3241 | 1222.25 | 74762.1686 | 1259.0833 | 28791.4925 | 1166.1667 | 28791.4925
1351 | 65684.031 |  | 1387.3333 | 40429.3191 | 1381.4167 | 24065.4096 | 1393.5 | 26814.9801 | 1402.4167 | 47546.1962 | 1407.0833 | 34442.0663 | 1443.9167 | 18361.7488 | 1351 | 18361.7488
1535.9167 | 64615.0781 |  | 1572.1667 | 43946.9299 | 1566.25 | 24507.5337 | 1578.3333 | 25895.2386 | 1587.1667 | 55076.733 | 1591.8333 | 36281.3292 | 1628.8333 | 28254.8154 | 1535.9167 | 24507.5337
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 44 |  |  | 2006-08-21 | 12:53
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G | Penlight Time | Minimums
-138.7 | 211202 |  | -116.4 | 211202 | -88.3333 | 229362.4444 | -72.8889 | 227184.6667 | -58.5 | 219321.1111 | -49.7778 | 218621.1111 | -25.8 | 252938 | -20.1 | 251298 | -7.8333 | 254015.7778 | -4.7222 | 248826.8889 | 12.9 | 225576.4 | 15 | 230456.4 | -46.263 | 211202
46 | 211202 |  | 68.3 | 211202 | 96.2778 | 217623.4444 | 111.9444 | 227184.6667 | 126.2222 | 219321.1111 | 134.8333 | 218621.1111 | 159.1 | 252938 | 164.7 | 251298 | 176.9444 | 254015.7778 | 180.0556 | 248826.8889 | 197.6 | 225576.4 | 200 | 230456.4 | 138.4981 | 211202
230.8 | 211202 |  | 253.2 | 211202 | 281.1111 | 229362.4444 | 296.6111 | 215445.6667 | 310.9444 | 219321.1111 | 319.7222 | 218621.1111 | 343.8 | 252938 | 349.4 | 251298 | 361.6667 | 254015.7778 | 364.7222 | 248826.8889 | 382.5 | 204446.2 | 384.7 | 230456.4 | 323.2648 | 204446.2
415.5 | 211202 |  | 437.9 | 211202 | 465.8889 | 229362.4444 | 481.5 | 227184.6667 | 495.8333 | 219321.1111 | 504.5 | 218621.1111 | 528.6 | 252938 | 534.2 | 251298 | 546.3889 | 240758.1111 | 549.6667 | 248826.8889 | 567.3 | 225576.4 | 569.5 | 230456.4 | 508.0648 | 211202
600.3 | 211202 |  | 622.7 | 211202 | 650.6111 | 229362.4444 | 666.2778 | 227184.6667 | 680.5556 | 49746653.8933 | 689 | 33290910.9133 | 713.5 | 252938 | 719 | 251298 | 731.3333 | 240447 | 734.2778 | 248826.8889 | 751.9 | 225576.4 | 754.3 | 230456.4 | 692.813 | 211202
785.1 | 211202 |  | 807.5 | 211202 | 835.5556 | 229362.4444 | 851.0556 | 212827 | 865.3333 | 219321.1111 | 874 | 218621.1111 | 898.1 | 102082.915 | 903.8 | 101052.0495 | 916 | 152657.2385 | 919.1111 | 167777.4147 | 936.8 | 128133.0387 | 939 | 141696.7024 | 877.613 | 101052.0495
969.7 | 22281331.9898 |  | 992.2 | 13572.3046 | 1020.2778 | 82462.2796 | 1035.6667 | 79787.3091 | 1050.0556 | 578884.9656 | 1058.7778 | 65446.7738 | 1082.8 | 9.6535 | 1088.6 | 9.4212 | 1100.7222 | 17.4317 | 1103.8889 | 15.9293 | 1121.6 | 43444.36 | 1123.8 | 48124.3 | 1062.3407 | 9.4212
1154.5 | 79595.6333 |  | 1177 | 36826.8004 | 1204.9444 | 50159.1344 | 1220.5 | 42775.0621 | 1234.9444 | 39524.1742 | 1243.5556 | 45610.72 | 1267.6 | 16.5053 | 1273.2 | 11.3849 | 1285.5 | 11.8849 | 1288.6667 | 5.8736 | 1306.3 | 45035.28 | 1308.6 | 48619.66 | 1247.1093 | 5.8736
1339.3 | 51246.8873 |  | 1361.7 | 41424.4874 | 1389.7778 | 3048.7912 | 1405.2778 | 7434.6533 | 1419.6667 | 46477.5223 | 1428.3333 | 53133.099 | 1452.5 | 25.9456 | 1458 | 6.8888 | 1470.3333 | 5.5576 | 1473.3889 | 14.4604 | 1491 | 52785.2489 | 1493.3 | 52350.34 | 1431.8815 | 5.5576
1524.2 | 65542.6984 |  | 1546.5 | 48746.8631 | 1574.6667 | 2572.3203 | 1590.1111 | 7080.538 | 1604.3889 | 48830.8072 | 1613.1111 | 53717.1017 | 1637.4 | 6.6262 | 1643 | 15.3305 | 1655.2778 | 15.952 | 1658.3333 | 10.8027 | 1675.9 | 51374.34 | 1678.2 | 54958.72 | 1616.7574 | 6.6262
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -145 | 18.8 | 27.5 | 19.4 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
1 | -144 | 18.8 | 27.5 | 19.4 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
2 | -143 | 18.8 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.7
3 | -142 | 18.9 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.7
4 | -141 | 18.9 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.6
5 | -140 | 18.9 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.6
6 | -139 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
7 | -138 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
8 | -137 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
9 | -136 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
10 | -135 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
11 | -134 | 18.9 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.6
12 | -133 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
13 | -132 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
14 | -131 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
15 | -130 | 18.8 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.6
16 | -129 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
17 | -128 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.6
18 | -127 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
19 | -126 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
20 | -125 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
21 | -124 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
22 | -123 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
23 | -122 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
24 | -121 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
25 | -120 | 18.9 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.5
26 | -119 | 18.8 | 27.6 | 19.3 | 26.9 | 30.9 | 23.9 | 23.7 | 27.4
27 | -118 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
28 | -117 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
29 | -116 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
30 | -115 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
31 | -114 | 18.9 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
32 | -113 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
33 | -112 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
34 | -111 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
35 | -110 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
36 | -109 | 18.8 | 27.6 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
37 | -108 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
38 | -107 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
39 | -106 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
40 | -105 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
41 | -104 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
42 | -103 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
43 | -102 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
44 | -101 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
45 | -100 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
46 | -99 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
47 | -98 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
48 | -97 | 18.8 | 27.5 | 19.4 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
49 | -96 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
50 | -95 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
51 | -94 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
52 | -93 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
53 | -92 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
54 | -91 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
55 | -90 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
56 | -89 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
57 | -88 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
58 | -87 | 18.9 | 27.5 | 19.4 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
59 | -86 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
60 | -85 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
61 | -84 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
62 | -83 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
63 | -82 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
64 | -81 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
65 | -80 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
66 | -79 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
67 | -78 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
68 | -77 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
69 | -76 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
70 | -75 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
71 | -74 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
72 | -73 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
73 | -72 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
74 | -71 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
75 | -70 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
76 | -69 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
77 | -68 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
78 | -67 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
79 | -66 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
80 | -65 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
81 | -64 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
82 | -63 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
83 | -62 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.5
84 | -61 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
85 | -60 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
86 | -59 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
87 | -58 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
88 | -57 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
89 | -56 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
90 | -55 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
91 | -54 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
92 | -53 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
93 | -52 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
94 | -51 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
95 | -50 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
96 | -49 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
97 | -48 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
98 | -47 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
99 | -46 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
100 | -45 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
101 | -44 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
102 | -43 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
103 | -42 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.4
104 | -41 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
105 | -40 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
106 | -39 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
107 | -38 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
108 | -37 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
109 | -36 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
110 | -35 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
111 | -34 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
112 | -33 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
113 | -32 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
114 | -31 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
115 | -30 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
116 | -29 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
117 | -28 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
118 | -27 | 18.8 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
119 | -26 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
120 | -25 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
121 | -24 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
122 | -23 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
123 | -22 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
124 | -21 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
125 | -20 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
126 | -19 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
127 | -18 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
128 | -17 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
129 | -16 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
130 | -15 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
131 | -14 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
132 | -13 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
133 | -12 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
134 | -11 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
135 | -10 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
136 | -9 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
137 | -8 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
138 | -7 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.3
139 | -6 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
140 | -5 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
141 | -4 | 18.9 | 27.5 | 19.3 | 26.9 | 30.8 | 23.9 | 23.7 | 27.2
142 | -3 | 18.9 | 27.7 | 18.8 | 27.1 | 31 | 24 | 23.6 | 27.2
143 | -2 | 18.8 | 28.9 | 16.1 | 28 | 32.7 | 24.2 | 23.6 | 27
144 | -1 | 18.8 | 29.3 | 15.3 | 28.3 | 33.2 | 24.2 | 23.6 | 27
145 | 0 | 19.2 | 29.3 | 15.3 | 28.3 | 33.2 | 24.2 | 23.6 | 27.1
146 | 1 | 20 | 29.3 | 15.3 | 28.3 | 33.2 | 24.2 | 23.6 | 27.1
147 | 2 | 21.5 | 29.3 | 15.3 | 28.3 | 33.2 | 24.3 | 23.6 | 27.1
148 | 3 | 23.5 | 29.3 | 15.3 | 28.3 | 33.2 | 24.3 | 23.6 | 27.2
149 | 4 | 25.8 | 29.4 | 15.2 | 28.3 | 33.3 | 24.3 | 23.6 | 27.2
150 | 5 | 28.5 | 29.3 | 15.3 | 28.3 | 33.3 | 24.3 | 23.7 | 27.2
151 | 6 | 31.6 | 29.4 | 15.2 | 28.3 | 33.3 | 24.4 | 23.7 | 27.2
152 | 7 | 34.9 | 29.4 | 15.2 | 28.3 | 33.3 | 24.4 | 23.8 | 27.3
153 | 8 | 38.5 | 29.4 | 15.3 | 28.3 | 33.3 | 24.5 | 23.8 | 27.3
154 | 9 | 42.3 | 29.4 | 15.3 | 28.3 | 33.3 | 24.6 | 23.9 | 27.3
155 | 10 | 46.3 | 29.4 | 15.3 | 28.3 | 33.3 | 24.7 | 23.9 | 27.4
156 | 11 | 50.5 | 29.5 | 15.3 | 28.3 | 33.3 | 24.8 | 24 | 27.4
157 | 12 | 54.8 | 29.5 | 15.3 | 28.3 | 33.3 | 24.9 | 24.1 | 27.4
158 | 13 | 59.3 | 29.5 | 15.3 | 28.3 | 33.4 | 25 | 24.2 | 27.5
159 | 14 | 63.9 | 29.6 | 15.3 | 28.3 | 33.4 | 25.1 | 24.3 | 27.6
160 | 15 | 68.7 | 29.6 | 15.3 | 28.3 | 33.4 | 25.2 | 24.5 | 27.6
161 | 16 | 73.6 | 29.7 | 15.3 | 28.3 | 33.5 | 25.3 | 24.6 | 27.7
162 | 17 | 78.5 | 29.8 | 15.3 | 28.3 | 33.5 | 25.5 | 24.7 | 27.8
163 | 18 | 83.5 | 29.9 | 15.3 | 28.3 | 33.6 | 25.7 | 24.8 | 27.9
164 | 19 | 88.6 | 30 | 15.3 | 28.4 | 33.7 | 25.8 | 24.9 | 28.1
165 | 20 | 93.9 | 30.1 | 15.3 | 28.4 | 33.8 | 26 | 25.1 | 28.2
166 | 21 | 99.2 | 30.2 | 15.3 | 28.4 | 33.8 | 26.1 | 25.3 | 28.3
167 | 22 | 104.4 | 30.3 | 15.3 | 28.4 | 33.9 | 26.3 | 25.5 | 28.5
168 | 23 | 109.9 | 30.4 | 15.3 | 28.4 | 33.9 | 26.5 | 25.6 | 28.7
169 | 24 | 115.3 | 30.5 | 15.3 | 28.4 | 34.1 | 26.8 | 25.8 | 28.8
170 | 25 | 120.8 | 30.7 | 15.3 | 28.4 | 34.2 | 27 | 26.1 | 29
171 | 26 | 126.3 | 30.8 | 15.4 | 28.4 | 34.2 | 27.3 | 26.3 | 29.2
172 | 27 | 131.8 | 31 | 15.4 | 28.5 | 34.4 | 27.6 | 26.5 | 29.4
173 | 28 | 137.3 | 31.1 | 15.4 | 28.5 | 34.5 | 27.9 | 26.8 | 29.6
174 | 29 | 142.9 | 31.3 | 15.4 | 28.5 | 34.6 | 28.2 | 27 | 29.8
175 | 30 | 148.6 | 31.5 | 15.4 | 28.6 | 34.8 | 28.5 | 27.3 | 30.1
176 | 31 | 154.4 | 31.7 | 15.4 | 28.6 | 34.9 | 28.8 | 27.6 | 30.3
177 | 32 | 160.1 | 32 | 15.4 | 28.6 | 35.1 | 29.2 | 27.9 | 30.6
178 | 33 | 165.7 | 32.2 | 15.5 | 28.7 | 35.2 | 29.5 | 28.2 | 30.9
179 | 34 | 171.4 | 32.4 | 15.6 | 28.7 | 35.4 | 29.9 | 28.6 | 31.2
180 | 35 | 177.1 | 32.7 | 15.5 | 28.8 | 35.6 | 30.3 | 28.9 | 31.5
181 | 36 | 182.7 | 32.9 | 15.6 | 28.8 | 35.8 | 30.7 | 29.3 | 31.9
182 | 37 | 188.3 | 33.2 | 15.7 | 28.8 | 36 | 31.1 | 29.7 | 32.2
183 | 38 | 194 | 33.5 | 15.7 | 28.9 | 36.2 | 31.5 | 30.1 | 32.6
184 | 39 | 199.7 | 33.8 | 15.8 | 29 | 36.4 | 31.9 | 30.5 | 33
185 | 40 | 205.5 | 34.1 | 15.8 | 29 | 36.6 | 32.3 | 30.9 | 33.4
186 | 41 | 211.1 | 34.4 | 15.9 | 29.1 | 36.9 | 32.8 | 31.3 | 33.9
187 | 42 | 216.6 | 34.8 | 16 | 29.1 | 37.1 | 33.4 | 31.8 | 34.3
188 | 43 | 222.2 | 35.2 | 16 | 29.3 | 37.4 | 33.9 | 32.3 | 34.8
189 | 44 | 227.9 | 35.6 | 16.1 | 29.3 | 37.7 | 34.5 | 32.7 | 35.2
190 | 45 | 233.4 | 35.9 | 16.2 | 29.4 | 37.9 | 35.1 | 33.2 | 35.8
191 | 46 | 239 | 36.3 | 16.3 | 29.5 | 38.2 | 35.7 | 33.7 | 36.3
192 | 47 | 244.6 | 36.7 | 16.5 | 29.5 | 38.5 | 36.3 | 34.3 | 36.9
193 | 48 | 250.1 | 37.1 | 16.6 | 29.7 | 38.8 | 36.9 | 34.8 | 37.4
194 | 49 | 255.6 | 37.6 | 16.6 | 29.8 | 39.1 | 37.6 | 35.4 | 38
195 | 50 | 261 | 38.1 | 16.7 | 29.9 | 39.5 | 38.3 | 35.9 | 38.6
196 | 51 | 266.6 | 38.6 | 16.8 | 30 | 39.9 | 39 | 36.6 | 39.2
197 | 52 | 272 | 39.1 | 17 | 30.1 | 40.2 | 39.7 | 37.2 | 39.9
198 | 53 | 277.4 | 39.6 | 17.1 | 30.3 | 40.6 | 40.3 | 37.8 | 40.6
199 | 54 | 282.7 | 40.2 | 17.2 | 30.4 | 41 | 41.1 | 38.5 | 41.3
200 | 55 | 288 | 40.7 | 17.4 | 30.5 | 41.4 | 41.9 | 39.2 | 42.1
201 | 56 | 293.2 | 41.3 | 17.5 | 30.7 | 41.8 | 42.8 | 39.9 | 42.8
202 | 57 | 298.4 | 41.9 | 17.7 | 30.9 | 42.2 | 43.6 | 40.6 | 43.6
203 | 58 | 303.6 | 42.5 | 17.9 | 31 | 42.7 | 44.5 | 41.3 | 44.5
204 | 59 | 308.8 | 43.1 | 18 | 31.2 | 43.1 | 45.4 | 42 | 45.3
205 | 60 | 314.1 | 43.8 | 18.2 | 31.4 | 43.6 | 46.3 | 42.8 | 46.2
206 | 61 | 319.2 | 44.4 | 18.4 | 31.6 | 44.1 | 47.2 | 43.6 | 47.1
207 | 62 | 324.3 | 45.1 | 18.6 | 31.8 | 44.6 | 48.1 | 44.4 | 48
208 | 63 | 329.3 | 45.8 | 18.8 | 32 | 45.1 | 49 | 45.2 | 48.9
209 | 64 | 334.3 | 46.5 | 19 | 32.2 | 45.6 | 49.9 | 46.1 | 49.9
210 | 65 | 339.4 | 47.3 | 19.2 | 32.4 | 46.2 | 50.9 | 47 | 50.9
211 | 66 | 344.6 | 48 | 19.4 | 32.6 | 46.7 | 51.9 | 47.9 | 52
212 | 67 | 349.7 | 48.8 | 19.7 | 32.8 | 47.3 | 53 | 48.8 | 53
213 | 68 | 354.7 | 49.5 | 19.9 | 33.1 | 47.9 | 54.1 | 49.8 | 54.1
214 | 69 | 359.5 | 50.4 | 20.1 | 33.4 | 48.5 | 55 | 50.7 | 55.2
215 | 70 | 364.3 | 51.2 | 20.4 | 33.6 | 49.1 | 56 | 51.7 | 56.3
216 | 71 | 369.2 | 52 | 20.6 | 33.9 | 49.7 | 57 | 52.6 | 57.5
217 | 72 | 374.2 | 52.9 | 20.9 | 34.2 | 50.3 | 58 | 53.7 | 58.8
218 | 73 | 379 | 53.8 | 21.2 | 34.4 | 51 | 59 | 54.7 | 60
219 | 74 | 383.8 | 54.7 | 21.4 | 34.7 | 51.7 | 60.1 | 55.7 | 61.3
220 | 75 | 388.5 | 55.7 | 21.7 | 35 | 52.4 | 61.3 | 56.7 | 62.7
221 | 76 | 393.3 | 56.7 | 22 | 35.4 | 53.1 | 62.4 | 57.8 | 64
222 | 77 | 398.1 | 57.7 | 22.3 | 35.7 | 53.8 | 63.7 | 58.8 | 65.3
223 | 78 | 402.6 | 58.7 | 22.7 | 36 | 54.5 | 64.9 | 59.9 | 66.7
224 | 79 | 407 | 59.8 | 23 | 36.3 | 55.3 | 66.2 | 60.9 | 68.1
225 | 80 | 411.5 | 60.9 | 23.3 | 36.7 | 56 | 67.5 | 62 | 69.6
226 | 81 | 415.8 | 62 | 23.7 | 37 | 56.8 | 68.9 | 63.1 | 71.1
227 | 82 | 420.1 | 63.1 | 24 | 37.4 | 57.7 | 70.3 | 64.3 | 72.6
228 | 83 | 424.4 | 64.3 | 24.3 | 37.8 | 58.5 | 71.5 | 65.5 | 74.1
229 | 84 | 428.9 | 65.5 | 24.7 | 38.2 | 59.3 | 72.9 | 66.6 | 75.7
230 | 85 | 433.4 | 66.7 | 25.1 | 38.6 | 60.2 | 74.3 | 67.9 | 77.4
231 | 86 | 437.8 | 68 | 25.4 | 39 | 61.1 | 75.5 | 69 | 79.1
232 | 87 | 442.1 | 69.3 | 25.8 | 39.4 | 62.1 | 76.9 | 70.2 | 80.8
233 | 88 | 446.3 | 70.5 | 26.3 | 39.8 | 63 | 78.4 | 71.4 | 82.5
234 | 89 | 450.4 | 71.9 | 26.7 | 40.2 | 64 | 79.6 | 72.8 | 84.3
235 | 90 | 454.5 | 73.2 | 27.1 | 40.7 | 65 | 81.2 | 74.1 | 86.1
236 | 91 | 458.7 | 74.5 | 27.5 | 41.1 | 66 | 82.8 | 75.5 | 88
237 | 92 | 462.6 | 75.9 | 28 | 41.6 | 67 | 84.2 | 76.8 | 89.9
238 | 93 | 466.6 | 77.3 | 28.5 | 42.1 | 68.1 | 85.6 | 78.1 | 91.8
239 | 94 | 470.7 | 78.8 | 28.9 | 42.5 | 69.1 | 87.1 | 79.4 | 93.8
240 | 95 | 474.8 | 80.2 | 29.4 | 43 | 70.2 | 88.8 | 80.8 | 95.8
241 | 96 | 478.6 | 81.3 | 30.7 | 43.2 | 70.8 | 90.2 | 82.3 | 97.9
242 | 97 | 482.3 | 82.8 | 31 | 43.8 | 72.1 | 91.8 | 83.7 | 99.9
243 | 98 | 485.8 | 84.3 | 31.5 | 44.3 | 73.3 | 93.4 | 85.1 | 102
244 | 99 | 489 | 85.8 | 32 | 44.8 | 74.4 | 95.2 | 86.4 | 104
245 | 100 | 491.9 | 87.2 | 32.6 | 45.3 | 75.6 | 96.8 | 87.8 | 106.1
246 | 101 | 494.7 | 88.7 | 33.2 | 45.8 | 76.7 | 98.3 | 89 | 108.2
247 | 102 | 497.2 | 90.2 | 33.8 | 46.4 | 77.8 | 99.8 | 90.3 | 110.4
248 | 103 | 499.6 | 91.6 | 34.4 | 46.9 | 78.9 | 101.3 | 91.5 | 112.6
249 | 104 | 501.6 | 93.1 | 35 | 47.5 | 80 | 102.8 | 92.9 | 114.7
250 | 105 | 504 | 94.7 | 35.5 | 48 | 81.2 | 104.5 | 94.2 | 116.8
251 | 106 | 506.5 | 96.3 | 36 | 48.7 | 82.6 | 106 | 95.4 | 119
252 | 107 | 508.9 | 97.9 | 36.4 | 49.3 | 84 | 107.5 | 96.6 | 121
253 | 108 | 511.1 | 99.5 | 36.9 | 49.9 | 85.3 | 108.9 | 97.7 | 123.3
254 | 109 | 513 | 101 | 37.5 | 50.6 | 86.6 | 110.4 | 99 | 125.5
255 | 110 | 514.7 | 102.5 | 38.2 | 51.1 | 87.9 | 111.8 | 100.3 | 127.7
256 | 111 | 516.2 | 104.1 | 38.7 | 51.8 | 89.3 | 113.3 | 101.5 | 130
257 | 112 | 517.7 | 105.8 | 39.3 | 52.4 | 90.7 | 114.6 | 102.6 | 132.2
258 | 113 | 519 | 107.4 | 40 | 53 | 92.2 | 115.7 | 103.8 | 134.4
259 | 114 | 519.7 | 109.1 | 40.7 | 53.6 | 93.6 | 116.9 | 105 | 136.5
260 | 115 | 520.3 | 110.8 | 41.4 | 54.2 | 95 | 118.2 | 106.2 | 138.7
261 | 116 | 520.9 | 112.6 | 42.1 | 54.9 | 96.3 | 119.4 | 107.5 | 140.9
262 | 117 | 521.5 | 114.4 | 42.9 | 55.5 | 97.6 | 120.6 | 108.6 | 143
263 | 118 | 521.8 | 116.2 | 43.7 | 56.1 | 98.8 | 121.8 | 109.7 | 145.2
264 | 119 | 522 | 118.2 | 44.3 | 56.8 | 100.2 | 123.2 | 110.9 | 147.3
265 | 120 | 522 | 120.1 | 44.9 | 57.4 | 101.5 | 124.2 | 111.9 | 149.4
266 | 121 | 521.7 | 122.1 | 45.6 | 58.1 | 102.8 | 125.2 | 112.9 | 151.5
267 | 122 | 521.4 | 124.1 | 46.2 | 58.8 | 104.1 | 126.5 | 113.8 | 153.5
268 | 123 | 521.1 | 126.1 | 46.8 | 59.5 | 105.4 | 127.6 | 114.8 | 155.5
269 | 124 | 520.8 | 128 | 47.5 | 60.2 | 106.7 | 128.7 | 115.7 | 157.6
270 | 125 | 520.5 | 130 | 48 | 61 | 108 | 129.6 | 116.6 | 159.5
271 | 126 | 520.2 | 131.9 | 48.6 | 61.7 | 109.2 | 130.5 | 117.4 | 161.4
272 | 127 | 519.9 | 133.7 | 49.3 | 62.4 | 110.4 | 131.2 | 118.2 | 163.4
273 | 128 | 519.6 | 135.4 | 50 | 63.2 | 111.6 | 131.9 | 119 | 165.4
274 | 129 | 519.3 | 137.1 | 50.7 | 63.9 | 112.9 | 132.8 | 119.9 | 167.4
275 | 130 | 519.1 | 138.7 | 51.4 | 64.6 | 114 | 133.5 | 120.7 | 169.3
276 | 131 | 518.8 | 140.2 | 52.1 | 65.4 | 115.3 | 134.4 | 121.5 | 171.3
277 | 132 | 518.8 | 141.6 | 52.8 | 66.1 | 116.5 | 135.1 | 122.3 | 173.3
278 | 133 | 518.9 | 142.9 | 53.4 | 66.9 | 117.9 | 135.2 | 123.1 | 175.2
279 | 134 | 518.9 | 144.1 | 54.2 | 67.6 | 119.2 | 136 | 123.9 | 177.1
280 | 135 | 518.9 | 145.2 | 54.9 | 68.4 | 120.6 | 136.7 | 124.6 | 179.1
281 | 136 | 518.8 | 146.3 | 55.6 | 69.2 | 122.1 | 137.3 | 125.4 | 181
282 | 137 | 519 | 147.2 | 56.4 | 69.9 | 123.6 | 137.9 | 126.1 | 182.8
283 | 138 | 519.2 | 148.1 | 57.2 | 70.7 | 125.2 | 138.7 | 126.7 | 184.7
284 | 139 | 519.4 | 149 | 58 | 71.4 | 126.9 | 139.4 | 127.4 | 186.6
285 | 140 | 519.7 | 149.9 | 58.8 | 72.2 | 128.5 | 140.1 | 128.2 | 188.5
286 | 141 | 519.9 | 150.8 | 59.6 | 73 | 130.1 | 140.9 | 128.8 | 190.3
287 | 142 | 520.1 | 151.7 | 60.3 | 73.8 | 131.8 | 141.6 | 129.5 | 192.1
288 | 143 | 520.5 | 152.6 | 61.2 | 74.5 | 133.4 | 142.3 | 130.2 | 194
289 | 144 | 520.7 | 153.5 | 62 | 75.3 | 135 | 142.6 | 130.9 | 195.8
290 | 145 | 520.7 | 154.4 | 62.8 | 76.1 | 136.6 | 143.2 | 131.5 | 197.6
291 | 146 | 521.1 | 155.3 | 63.5 | 76.9 | 138.2 | 143.9 | 132 | 199.4
292 | 147 | 521.5 | 156.2 | 64.4 | 77.6 | 139.7 | 144.8 | 132.5 | 201.2
293 | 148 | 521.7 | 157 | 65.3 | 78.3 | 141.1 | 145.4 | 133.1 | 202.9
294 | 149 | 521.9 | 158 | 66 | 79.2 | 142.7 | 146 | 133.9 | 204.7
295 | 150 | 522 | 158.9 | 66.7 | 80 | 144.2 | 146.7 | 134.6 | 206.4
296 | 151 | 522 | 159.6 | 67.4 | 80.7 | 145.6 | 147.5 | 135.2 | 208.1
297 | 152 | 522.3 | 160.2 | 68.3 | 81.5 | 147 | 148.1 | 135.7 | 209.9
298 | 153 | 522.5 | 160.7 | 69.1 | 82.2 | 148.4 | 149 | 136.4 | 211.6
299 | 154 | 522.6 | 161.2 | 69.9 | 83 | 149.8 | 149.8 | 137 | 213.3
300 | 155 | 522.9 | 161.4 | 70.6 | 83.7 | 151.2 | 150.3 | 137.5 | 215
301 | 156 | 522.9 | 161.6 | 71.4 | 84.5 | 152.4 | 151.1 | 138.2 | 216.7
302 | 157 | 522.9 | 161.7 | 72.2 | 85.2 | 153.3 | 152.1 | 138.7 | 218.4
303 | 158 | 522.9 | 160.7 | 73 | 86 | 154.1 | 152.8 | 139.2 | 220.1
304 | 159 | 522.8 | 158.5 | 73.9 | 86.7 | 154.9 | 153.8 | 139.7 | 221.7
305 | 160 | 522.7 | 156.4 | 74.7 | 87.4 | 156.2 | 154.6 | 140.4 | 223.4
306 | 161 | 522.8 | 154.5 | 75.5 | 88.2 | 158 | 155.4 | 141 | 225
307 | 162 | 522.9 | 153 | 76.2 | 88.9 | 160.4 | 156.4 | 141.7 | 226.6
308 | 163 | 523 | 151.8 | 77.1 | 89.7 | 163.3 | 157.4 | 142.2 | 228.2
309 | 164 | 523 | 150.8 | 78.1 | 90.4 | 165.9 | 158.1 | 142.7 | 229.8
310 | 165 | 523.4 | 150.3 | 78.8 | 91.3 | 169.2 | 159.1 | 143.2 | 231.4
311 | 166 | 523.6 | 150 | 79.6 | 92 | 172.5 | 160 | 143.6 | 232.9
312 | 167 | 523.6 | 150.1 | 80.5 | 92.9 | 175.5 | 161 | 144.1 | 234.5
313 | 168 | 523.6 | 150.4 | 81.4 | 93.7 | 178.4 | 162 | 144.6 | 236.1
314 | 169 | 523.6 | 151 | 82.3 | 94.6 | 181 | 163 | 145.1 | 237.6
315 | 170 | 523.5 | 151.9 | 83.2 | 95.5 | 183.5 | 163.5 | 145.9 | 239.2
316 | 171 | 523.6 | 153.1 | 84.2 | 96.4 | 186.1 | 164.7 | 146.5 | 240.7
317 | 172 | 523.6 | 154.5 | 85 | 97.4 | 188.9 | 165.7 | 146.9 | 242.2
318 | 173 | 523.3 | 156.2 | 86 | 98.3 | 191.3 | 166.5 | 147.4 | 243.7
319 | 174 | 523.1 | 158.6 | 86.9 | 99.3 | 193.4 | 167.3 | 148.1 | 245.2
320 | 175 | 523.2 | 161.2 | 87.9 | 100.3 | 194.7 | 168.3 | 148.5 | 246.7
321 | 176 | 523.2 | 164.2 | 88.8 | 101.3 | 195.5 | 169 | 148.8 | 248.1
322 | 177 | 523.4 | 167.5 | 89.8 | 102.3 | 196.7 | 169.6 | 149.2 | 249.5
323 | 178 | 523.3 | 171.1 | 90.7 | 103.4 | 198.1 | 170.5 | 149.6 | 251
324 | 179 | 523 | 174.8 | 91.7 | 104.5 | 198.5 | 171.1 | 150.1 | 252.3
325 | 180 | 522.8 | 178.7 | 92.7 | 105.5 | 199.8 | 172 | 150.6 | 253.8
326 | 181 | 522.9 | 182.8 | 93.8 | 106.6 | 200.8 | 172.8 | 151.2 | 255.2
327 | 182 | 522.9 | 187.1 | 94.8 | 107.8 | 202.4 | 173.2 | 151.6 | 256.6
328 | 183 | 522.8 | 191.4 | 95.9 | 108.9 | 204.1 | 174 | 152.3 | 257.9
329 | 184 | 522.8 | 195.8 | 97 | 110.1 | 206.2 | 174.7 | 152.9 | 259.3
330 | 185 | 522.7 | 200.1 | 98.2 | 111.2 | 208.2 | 175.6 | 153.4 | 260.7
331 | 186 | 522.8 | 204.5 | 99.4 | 112.4 | 210.1 | 176.2 | 153.9 | 262
332 | 187 | 522.9 | 208.7 | 100.6 | 113.5 | 212.2 | 177.1 | 154.4 | 263.4
333 | 188 | 523 | 212.8 | 101.8 | 114.7 | 213.7 | 177.9 | 154.8 | 264.6
334 | 189 | 523.1 | 216.7 | 103 | 115.9 | 214.1 | 178.8 | 155.3 | 265.8
335 | 190 | 523.2 | 220.6 | 104.3 | 117.1 | 214.1 | 179.7 | 155.7 | 267.2
336 | 191 | 523.2 | 224.3 | 105.5 | 118.3 | 214.7 | 180.3 | 155.9 | 268.4
337 | 192 | 523.3 | 227.8 | 106.6 | 119.6 | 215.3 | 181.5 | 156.2 | 269.7
338 | 193 | 523.1 | 231.2 | 107.7 | 120.8 | 215.9 | 182.2 | 156.7 | 271
339 | 194 | 522.7 | 234.5 | 108.8 | 122 | 217.3 | 182.9 | 157.2 | 272.3
340 | 195 | 522.4 | 237.6 | 110 | 123.2 | 218 | 183.3 | 157.5 | 273.5
341 | 196 | 522.1 | 240.7 | 111.2 | 124.4 | 220 | 183.7 | 157.9 | 274.7
342 | 197 | 521.9 | 243.7 | 112.3 | 125.6 | 221.6 | 184.6 | 158.3 | 276
343 | 198 | 521.9 | 246.5 | 113.5 | 126.8 | 223.1 | 185.3 | 158.8 | 277.2
344 | 199 | 521.7 | 249 | 114.6 | 128 | 224.8 | 186.1 | 159.2 | 278.4
345 | 200 | 521.6 | 251.6 | 115.8 | 129.2 | 226 | 186.9 | 159.7 | 279.5
346 | 201 | 521.7 | 254.4 | 117 | 130.4 | 226.2 | 187.8 | 160.3 | 280.6
347 | 202 | 521.6 | 257.5 | 118.1 | 131.6 | 227.1 | 188.6 | 160.7 | 281.7
348 | 203 | 521.4 | 260.4 | 119.2 | 132.7 | 228.3 | 189.5 | 161.2 | 282.9
349 | 204 | 521.5 | 263 | 120.4 | 133.9 | 229.8 | 190.5 | 161.6 | 284
350 | 205 | 521.5 | 265.5 | 121.6 | 135 | 231.1 | 191.3 | 162.2 | 285.2
351 | 206 | 521.3 | 267.9 | 122.7 | 136.2 | 232.6 | 192.2 | 162.7 | 286.2
352 | 207 | 521.3 | 270 | 123.8 | 137.4 | 234.2 | 192.9 | 163.2 | 287.3
353 | 208 | 521.2 | 272.4 | 124.9 | 138.5 | 234.8 | 193.6 | 163.7 | 288.5
354 | 209 | 521.2 | 274.5 | 126 | 139.6 | 235.6 | 194.3 | 164.1 | 289.6
355 | 210 | 521.2 | 276.9 | 127.1 | 140.8 | 236.2 | 195 | 164.7 | 290.7
356 | 211 | 521.3 | 278.9 | 128.3 | 141.9 | 237.8 | 195.8 | 165.3 | 291.8
357 | 212 | 521.4 | 280.4 | 129.4 | 143 | 239.5 | 196.5 | 165.9 | 292.8
358 | 213 | 521.5 | 282.2 | 130.5 | 144.1 | 241.1 | 197.1 | 166.3 | 293.9
359 | 214 | 521.5 | 283.8 | 131.6 | 145.3 | 242.6 | 197.8 | 167 | 295
360 | 215 | 521.7 | 284.9 | 132.7 | 146.3 | 244.5 | 198.5 | 167.6 | 296
361 | 216 | 521.8 | 285.1 | 133.8 | 147.5 | 245.5 | 199.2 | 168.1 | 297.1
362 | 217 | 521.9 | 286.2 | 134.9 | 148.6 | 246 | 199.8 | 168.6 | 298.1
363 | 218 | 522 | 287 | 135.9 | 149.7 | 247.2 | 200.6 | 169.1 | 299.1
364 | 219 | 522.1 | 287.5 | 136.9 | 150.8 | 247.8 | 201.3 | 169.6 | 300.1
365 | 220 | 522.1 | 287.9 | 137.9 | 152 | 247.6 | 201.9 | 170 | 301.1
366 | 221 | 521.8 | 288.5 | 139 | 153.1 | 246.8 | 202.4 | 170.4 | 302.1
367 | 222 | 521.5 | 289.4 | 140 | 154.1 | 246.3 | 203 | 170.9 | 303.1
368 | 223 | 521.6 | 290.2 | 141 | 155.2 | 246.7 | 203.7 | 171.4 | 304
369 | 224 | 521.7 | 291 | 142 | 156.3 | 246.2 | 204.2 | 171.8 | 305
370 | 225 | 521.7 | 292.1 | 143.1 | 157.3 | 245.9 | 204.9 | 172.3 | 306
371 | 226 | 521.8 | 293.2 | 144.2 | 158.4 | 246.6 | 205.5 | 172.7 | 306.9
372 | 227 | 521.6 | 294.3 | 145.2 | 159.5 | 247.1 | 206.2 | 173.2 | 307.9
373 | 228 | 521.4 | 294.7 | 146.2 | 160.5 | 248.2 | 207 | 173.7 | 308.8
374 | 229 | 521.3 | 294.8 | 147.3 | 161.5 | 248.5 | 207.8 | 174.1 | 309.7
375 | 230 | 521.4 | 294.9 | 148.2 | 162.6 | 248.5 | 208.6 | 174.6 | 310.6
376 | 231 | 521.6 | 295.4 | 149.2 | 163.6 | 248 | 209.3 | 175 | 311.5
377 | 232 | 521.5 | 296 | 150.2 | 164.6 | 248.2 | 210 | 175.4 | 312.4
378 | 233 | 521.6 | 297 | 151.3 | 165.6 | 249.8 | 210.8 | 175.8 | 313.3
379 | 234 | 521.5 | 298.2 | 152.2 | 166.6 | 251.7 | 211.4 | 176.3 | 314.1
380 | 235 | 521.6 | 299.2 | 153.3 | 167.6 | 253.5 | 211.9 | 176.9 | 314.9
381 | 236 | 521.4 | 300 | 154.3 | 168.6 | 255 | 212.6 | 177.5 | 315.7
382 | 237 | 521.4 | 300.3 | 155.2 | 169.6 | 256.4 | 213.2 | 178.1 | 316.5
383 | 238 | 521.5 | 300.8 | 156.2 | 170.5 | 257.8 | 213.8 | 178.6 | 317.4
384 | 239 | 521.5 | 301 | 157.3 | 171.5 | 258.7 | 214.4 | 179 | 318.2
385 | 240 | 521.6 | 301.8 | 158.2 | 172.5 | 259.9 | 215 | 179.5 | 319
386 | 241 | 521.7 | 302.7 | 159.2 | 173.4 | 261.1 | 215.8 | 180 | 319.9
387 | 242 | 521.6 | 302.9 | 160.2 | 174.4 | 262.1 | 216.4 | 180.6 | 320.7
388 | 243 | 521.3 | 303.6 | 161.1 | 175.4 | 263 | 216.9 | 181.2 | 321.5
389 | 244 | 521.2 | 304.3 | 162.1 | 176.4 | 263.3 | 217.4 | 181.8 | 322.2
390 | 245 | 521.3 | 304.9 | 163 | 177.4 | 264.2 | 217.9 | 182.4 | 322.9
391 | 246 | 521.3 | 304.9 | 164 | 178.3 | 265.2 | 218.6 | 182.9 | 323.7
392 | 247 | 521.3 | 305 | 164.9 | 179.3 | 265.8 | 219.2 | 183.6 | 324.4
393 | 248 | 521 | 305 | 165.9 | 180.2 | 266.9 | 219.8 | 184.3 | 325.1
394 | 249 | 520.6 | 304.7 | 166.8 | 181.2 | 268.2 | 220.4 | 184.9 | 325.8
395 | 250 | 520.5 | 305.1 | 167.8 | 182.1 | 268.9 | 220.8 | 185.5 | 326.5
396 | 251 | 520.5 | 304.9 | 168.7 | 183.1 | 269.2 | 221.5 | 186.2 | 327.3
397 | 252 | 520.5 | 304.6 | 169.7 | 184 | 269.6 | 222.1 | 186.8 | 328.1
398 | 253 | 520.5 | 305 | 170.7 | 184.9 | 269.6 | 222.7 | 187.5 | 328.8
399 | 254 | 520.5 | 306 | 171.6 | 185.9 | 270.1 | 223.2 | 188.1 | 329.5
400 | 255 | 520.6 | 307.6 | 172.5 | 186.8 | 270.3 | 223.9 | 188.7 | 330.1
401 | 256 | 520.5 | 308.2 | 173.5 | 187.7 | 270.9 | 224.6 | 189.2 | 330.8
402 | 257 | 520.5 | 308.3 | 174.4 | 188.7 | 271.9 | 225.2 | 189.7 | 331.5
403 | 258 | 520.5 | 308.7 | 175.3 | 189.6 | 272.9 | 225.7 | 190.3 | 332.1
404 | 259 | 520.6 | 309.3 | 176.2 | 190.5 | 273.6 | 226.3 | 190.8 | 332.8
405 | 260 | 520.6 | 310 | 177.1 | 191.4 | 273.9 | 226.9 | 191.4 | 333.5
406 | 261 | 520.5 | 311.1 | 178 | 192.3 | 274.3 | 227.4 | 192 | 334.2
407 | 262 | 520.6 | 311.8 | 178.9 | 193.3 | 274.9 | 227.9 | 192.6 | 334.8
408 | 263 | 520.7 | 312.3 | 179.9 | 194.2 | 275.8 | 228.6 | 193 | 335.5
409 | 264 | 520.8 | 312.6 | 180.8 | 195.1 | 275.6 | 229.2 | 193.5 | 336
410 | 265 | 521.1 | 313.7 | 181.7 | 195.9 | 275.9 | 229.8 | 194 | 336.7
411 | 266 | 521 | 314.6 | 182.7 | 196.8 | 276.9 | 230.3 | 194.5 | 337.3
412 | 267 | 520.8 | 315.8 | 183.6 | 197.7 | 277.3 | 230.9 | 195.1 | 337.9
413 | 268 | 520.7 | 316.7 | 184.4 | 198.6 | 278 | 231.5 | 195.6 | 338.5
414 | 269 | 520.6 | 317.1 | 185.4 | 199.5 | 279 | 232 | 196.1 | 339.1
415 | 270 | 520.7 | 317.5 | 186.3 | 200.3 | 280 | 232.5 | 196.7 | 339.7
416 | 271 | 520.4 | 317.8 | 187.1 | 201.2 | 280.7 | 233 | 197.1 | 340.3
417 | 272 | 520.2 | 318.2 | 188 | 202.1 | 280.8 | 233.5 | 197.5 | 340.9
418 | 273 | 520.1 | 318.6 | 188.9 | 203 | 281.4 | 234.1 | 198.1 | 341.5
419 | 274 | 520.2 | 318.8 | 189.7 | 203.8 | 282.6 | 234.6 | 198.6 | 342.1
420 | 275 | 520.2 | 319.6 | 190.6 | 204.7 | 283.5 | 234.9 | 199.2 | 342.6
421 | 276 | 520.1 | 320.5 | 191.5 | 205.5 | 283.6 | 235.3 | 199.7 | 343.2
422 | 277 | 519.9 | 320.9 | 192.3 | 206.4 | 284.2 | 235.7 | 200.3 | 343.7
423 | 278 | 519.7 | 321.3 | 193.1 | 207.3 | 283.6 | 236.3 | 200.9 | 344.3
424 | 279 | 519.6 | 321.4 | 193.9 | 208.1 | 284 | 236.8 | 201.2 | 344.8
425 | 280 | 519.3 | 321.2 | 194.8 | 209 | 285.2 | 237.3 | 201.7 | 345.3
426 | 281 | 519.2 | 320.9 | 195.7 | 209.8 | 285.8 | 237.7 | 202.1 | 345.8
427 | 282 | 519.4 | 321 | 196.5 | 210.6 | 286.4 | 238 | 202.5 | 346.3
428 | 283 | 519.4 | 321.2 | 197.4 | 211.4 | 287.2 | 238.4 | 203 | 346.8
429 | 284 | 519.3 | 321.9 | 198.2 | 212.3 | 288 | 238.7 | 203.5 | 347.4
430 | 285 | 519.4 | 322.6 | 199 | 213.1 | 288.4 | 239.2 | 203.9 | 347.9
431 | 286 | 519.3 | 323 | 199.9 | 213.9 | 289.6 | 239.6 | 204.4 | 348.4
432 | 287 | 519.2 | 323.8 | 200.8 | 214.7 | 290.3 | 239.9 | 204.8 | 348.9
433 | 288 | 519.1 | 324.1 | 202 | 215.4 | 290.8 | 240.3 | 205.1 | 349.3
434 | 289 | 519.1 | 324.2 | 203.1 | 216.1 | 290.8 | 240.7 | 205.5 | 349.8
435 | 290 | 519.1 | 324.1 | 204.4 | 216.7 | 291.1 | 241.1 | 205.9 | 350.2
436 | 291 | 519 | 325.2 | 204.6 | 217.8 | 291.7 | 241.6 | 206.4 | 350.6
437 | 292 | 518.8 | 326.3 | 205.3 | 218.6 | 291.7 | 242.1 | 206.8 | 351.1
438 | 293 | 518.7 | 327.2 | 205.8 | 219.5 | 292.2 | 242.7 | 207.3 | 351.5
439 | 294 | 518.6 | 327.5 | 206.7 | 220.3 | 293.5 | 243.2 | 207.8 | 351.9
440 | 295 | 518.5 | 327.3 | 207.5 | 221.1 | 294.6 | 243.7 | 208.2 | 352.3
441 | 296 | 518.5 | 327.9 | 208 | 221.9 | 295.7 | 244.1 | 208.6 | 352.7
442 | 297 | 518.5 | 328.8 | 208.8 | 222.7 | 296.5 | 244.6 | 209.1 | 353.2
443 | 298 | 518.5 | 328.3 | 209.9 | 223.4 | 296.9 | 245 | 209.6 | 353.7
444 | 299 | 518.4 | 328.3 | 210.6 | 224.2 | 297.8 | 245.4 | 210 | 354.1
445 | 300 | 518.3 | 328.6 | 211.5 | 224.9 | 298.2 | 245.9 | 210.4 | 354.5
446 | 301 | 518.4 | 329 | 212.3 | 225.7 | 298.8 | 246.3 | 210.9 | 354.9
447 | 302 | 518.4 | 329.4 | 213 | 226.5 | 299.5 | 246.8 | 211.4 | 355.4
448 | 303 | 518.4 | 329.7 | 213.8 | 227.2 | 299.8 | 247 | 211.8 | 355.7
449 | 304 | 518.5 | 330 | 214.6 | 228 | 300.4 | 247.4 | 212.2 | 356.2
450 | 305 | 518.4 | 330.4 | 215.3 | 228.8 | 300.9 | 247.9 | 212.7 | 356.6
451 | 306 | 518.6 | 330.9 | 216.2 | 229.5 | 301.6 | 248.3 | 213.1 | 357
452 | 307 | 518.8 | 331.6 | 217 | 230.2 | 302.4 | 248.7 | 213.5 | 357.4
453 | 308 | 518.8 | 332.5 | 217.8 | 230.9 | 303.1 | 249.1 | 213.9 | 357.8
454 | 309 | 518.9 | 333 | 218.7 | 231.6 | 303.6 | 249.6 | 214.3 | 358.1
455 | 310 | 519.1 | 332.8 | 219.4 | 232.4 | 304.2 | 250 | 214.8 | 358.5
456 | 311 | 519.3 | 332.7 | 220.1 | 233.1 | 304.5 | 250.3 | 215.2 | 358.9
457 | 312 | 519.3 | 332.9 | 220.8 | 233.9 | 304.9 | 250.6 | 215.6 | 359.2
458 | 313 | 519.1 | 333.2 | 221.4 | 234.6 | 305.1 | 251.1 | 216.1 | 359.6
459 | 314 | 519 | 333.4 | 222.2 | 235.3 | 304.3 | 251.5 | 216.7 | 359.9
460 | 315 | 519.1 | 333.8 | 223.1 | 236 | 303.9 | 251.9 | 217.2 | 360.3
461 | 316 | 519.2 | 334.7 | 224.1 | 236.6 | 303.4 | 252.3 | 217.5 | 360.7
462 | 317 | 519.4 | 335.6 | 224.8 | 237.3 | 303.2 | 252.9 | 217.8 | 361.1
463 | 318 | 519.4 | 336.2 | 225.5 | 238.1 | 301.9 | 253.4 | 218.1 | 361.5
464 | 319 | 519.5 | 336.6 | 226.2 | 238.8 | 302.2 | 253.8 | 218.5 | 361.9
465 | 320 | 519.5 | 337.4 | 226.9 | 239.5 | 302.2 | 254.3 | 218.7 | 362.3
466 | 321 | 519.4 | 338.4 | 227.7 | 240.1 | 302.8 | 254.8 | 219.1 | 362.7
467 | 322 | 519.3 | 338.9 | 228.5 | 240.8 | 302.1 | 255.4 | 219.5 | 363
468 | 323 | 519.1 | 339.5 | 229.2 | 241.4 | 299.6 | 255.8 | 219.9 | 363.4
469 | 324 | 519.1 | 339.8 | 229.8 | 242.1 | 299.5 | 256.2 | 220.4 | 363.8
470 | 325 | 519.4 | 340.1 | 230.6 | 242.8 | 299.2 | 256.6 | 220.8 | 364.1
471 | 326 | 519.3 | 340.7 | 231.3 | 243.4 | 299.7 | 257.2 | 221.1 | 364.5
472 | 327 | 519.3 | 341.7 | 232 | 244.1 | 301 | 257.9 | 221.5 | 364.8
473 | 328 | 519.3 | 341.9 | 232.7 | 244.7 | 301.9 | 258.6 | 221.8 | 365.1
474 | 329 | 519.2 | 342.6 | 233.3 | 245.4 | 303.3 | 259 | 222.1 | 365.4
475 | 330 | 519.4 | 343.3 | 234 | 246 | 304.2 | 259.6 | 222.5 | 365.7
476 | 331 | 519.5 | 343.3 | 234.7 | 246.7 | 305.5 | 260.1 | 222.9 | 366
477 | 332 | 519.6 | 343.6 | 235.4 | 247.3 | 307 | 260.5 | 223.2 | 366.4
478 | 333 | 519.7 | 344.5 | 236.2 | 247.9 | 308.1 | 261.1 | 223.6 | 366.7
479 | 334 | 519.8 | 344.8 | 236.9 | 248.6 | 309.2 | 261.6 | 224 | 367
480 | 335 | 519.9 | 345.2 | 237.5 | 249.2 | 310.9 | 262.1 | 224.4 | 367.3
481 | 336 | 520 | 345.9 | 238.3 | 249.8 | 311.7 | 262.6 | 224.6 | 367.6
482 | 337 | 520.1 | 346.7 | 239 | 250.4 | 312.7 | 263.1 | 225 | 367.9
483 | 338 | 520.3 | 346.9 | 239.6 | 251.1 | 314.1 | 263.5 | 225.5 | 368.2
484 | 339 | 520.6 | 347.5 | 240.1 | 251.8 | 315.2 | 264 | 225.8 | 368.5
485 | 340 | 520.7 | 348.1 | 240.8 | 252.4 | 316 | 264.3 | 226.3 | 368.8
486 | 341 | 520.7 | 348.6 | 241.4 | 253.1 | 316.6 | 264.6 | 226.7 | 369.1
487 | 342 | 520.6 | 348.6 | 242.1 | 253.7 | 317.7 | 265.1 | 227.1 | 369.5
488 | 343 | 520.6 | 349.5 | 242.7 | 254.3 | 318.4 | 265.3 | 227.4 | 369.8
489 | 344 | 520.4 | 350.4 | 243.2 | 254.9 | 318.9 | 265.6 | 227.8 | 370.1
490 | 345 | 520.2 | 350.8 | 243.7 | 255.6 | 319.8 | 266 | 228.1 | 370.3
491 | 346 | 520.2 | 351.7 | 244.3 | 256.2 | 320.2 | 266.3 | 228.4 | 370.6
492 | 347 | 520.4 | 352.6 | 244.9 | 256.8 | 320.9 | 266.6 | 228.7 | 370.9
493 | 348 | 520.4 | 353.1 | 245.5 | 257.4 | 321.1 | 267 | 229.1 | 371.2
494 | 349 | 520.5 | 353.9 | 246.1 | 258.1 | 321.6 | 267.4 | 229.6 | 371.5
495 | 350 | 520.4 | 354.5 | 246.7 | 258.7 | 322.7 | 267.7 | 230.1 | 371.8
496 | 351 | 520.4 | 354.9 | 247.3 | 259.3 | 323.7 | 268 | 230.5 | 372
497 | 352 | 520.5 | 354.9 | 247.9 | 259.9 | 323.9 | 268.3 | 230.9 | 372.3
498 | 353 | 520.6 | 355.2 | 248.6 | 260.5 | 324.7 | 268.8 | 231.2 | 372.6
499 | 354 | 520.4 | 355.9 | 249.2 | 261.1 | 325.3 | 269.2 | 231.6 | 372.9
500 | 355 | 520.3 | 356.4 | 249.8 | 261.7 | 325.4 | 269.5 | 232 | 373.1
501 | 356 | 520.1 | 357 | 250.4 | 262.3 | 326.3 | 269.9 | 232.5 | 373.4
502 | 357 | 520.1 | 357.2 | 251 | 262.9 | 326.5 | 270.3 | 232.8 | 373.6
503 | 358 | 520 | 357.8 | 251.6 | 263.6 | 327.4 | 270.7 | 233.3 | 373.8
504 | 359 | 520 | 358.3 | 252.2 | 264.2 | 328.6 | 271 | 233.6 | 374.1
505 | 360 | 520.1 | 358.9 | 252.8 | 264.8 | 329.1 | 271.3 | 234.1 | 374.4
506 | 361 | 519.8 | 359.7 | 253.4 | 265.4 | 330 | 271.5 | 234.5 | 374.6
507 | 362 | 519.6 | 360.2 | 254 | 266.1 | 331 | 271.8 | 234.9 | 374.9
508 | 363 | 519.5 | 360 | 254.6 | 266.7 | 331.1 | 272.3 | 235.3 | 375.2
509 | 364 | 519.5 | 360 | 255.2 | 267.3 | 331.8 | 272.8 | 235.6 | 375.4
510 | 365 | 519.4 | 360.2 | 255.8 | 267.9 | 332 | 273.3 | 235.9 | 375.6
511 | 366 | 519.6 | 360.6 | 256.4 | 268.5 | 332.3 | 273.6 | 236.3 | 375.8
512 | 367 | 519.7 | 361 | 257.1 | 269.1 | 332.1 | 274 | 236.6 | 376
513 | 368 | 519.9 | 361.7 | 257.7 | 269.7 | 332.2 | 274.4 | 236.9 | 376.3
514 | 369 | 519.9 | 362.5 | 258.2 | 270.3 | 332.5 | 274.8 | 237.3 | 376.5
515 | 370 | 519.8 | 363.1 | 258.8 | 270.9 | 333 | 275.1 | 237.7 | 376.7
516 | 371 | 519.8 | 363.3 | 259.4 | 271.6 | 332.9 | 275.4 | 238.1 | 376.9
517 | 372 | 519.9 | 363.6 | 259.9 | 272.2 | 333.9 | 275.8 | 238.5 | 377.1
518 | 373 | 519.8 | 364.4 | 260.5 | 272.8 | 335.5 | 276.1 | 238.9 | 377.4
519 | 374 | 519.8 | 364.5 | 261.1 | 273.4 | 336.5 | 276.4 | 239.3 | 377.7
520 | 375 | 519.7 | 364.6 | 261.8 | 274 | 336.9 | 276.7 | 239.7 | 377.8
521 | 376 | 519.4 | 364.1 | 262.4 | 274.6 | 337.4 | 277.1 | 240.2 | 378.1
522 | 377 | 519.6 | 364.3 | 263 | 275.2 | 338.3 | 277.4 | 240.6 | 378.3
523 | 378 | 519.9 | 364.8 | 263.6 | 275.8 | 339.1 | 277.8 | 240.9 | 378.6
524 | 379 | 520 | 365 | 264.2 | 276.4 | 339.8 | 278.1 | 241.2 | 378.9
525 | 380 | 520.2 | 365.9 | 264.8 | 277 | 339 | 278.4 | 241.3 | 379.2
526 | 381 | 520.4 | 367.1 | 265.5 | 277.6 | 338.2 | 278.6 | 241.5 | 379.3
527 | 382 | 520.3 | 368 | 266.1 | 278.1 | 338.7 | 278.9 | 241.7 | 379.6
528 | 383 | 520.3 | 368.4 | 266.8 | 278.7 | 339.8 | 279.3 | 242 | 379.8
529 | 384 | 520.4 | 368.8 | 267.4 | 279.3 | 341 | 279.6 | 242.3 | 380
530 | 385 | 520.5 | 368.8 | 268 | 279.9 | 342 | 280 | 242.7 | 380.3
531 | 386 | 520.5 | 369.2 | 268.6 | 280.5 | 342.7 | 280.3 | 243.2 | 380.5
532 | 387 | 520.7 | 369.5 | 269.2 | 281 | 343.3 | 280.4 | 243.5 | 380.7
533 | 388 | 520.7 | 369.7 | 269.8 | 281.6 | 343.3 | 280.5 | 243.7 | 380.9
534 | 389 | 520.7 | 370 | 270.4 | 282.1 | 343.7 | 280.8 | 244 | 381.1
535 | 390 | 520.6 | 370.6 | 271 | 282.7 | 344.5 | 281.2 | 244.3 | 381.3
536 | 391 | 520.6 | 370.9 | 271.6 | 283.3 | 344.7 | 281.7 | 244.7 | 381.5
537 | 392 | 520.5 | 371.5 | 272.2 | 283.8 | 343.4 | 282.1 | 245 | 381.8
538 | 393 | 520.3 | 371.5 | 272.8 | 284.3 | 342.2 | 282.5 | 245.3 | 381.9
539 | 394 | 520.3 | 371.6 | 273.3 | 284.9 | 341.5 | 283 | 245.5 | 382.1
540 | 395 | 520.2 | 371.6 | 274 | 285.3 | 341.4 | 283.4 | 245.8 | 382.3
541 | 396 | 520.1 | 371.6 | 274.6 | 285.8 | 341.4 | 283.7 | 246.1 | 382.5
542 | 397 | 520 | 371.7 | 275.2 | 286.3 | 341.9 | 284 | 246.3 | 382.7
543 | 398 | 519.9 | 371.9 | 275.9 | 286.8 | 341.5 | 284.3 | 246.6 | 382.9
544 | 399 | 519.9 | 372.6 | 276.3 | 287.4 | 340.5 | 284.8 | 246.8 | 383.1
545 | 400 | 519.9 | 373.1 | 276.9 | 287.9 | 341.3 | 285.2 | 247.1 | 383.2
546 | 401 | 519.9 | 373.8 | 277.5 | 288.5 | 342.6 | 285.7 | 247.6 | 383.4
547 | 402 | 520.1 | 374.4 | 278 | 289.1 | 343.4 | 286 | 247.9 | 383.6
548 | 403 | 520.2 | 374.4 | 278.6 | 289.7 | 343.1 | 286.4 | 248.1 | 383.8
549 | 404 | 520.2 | 374.5 | 279.3 | 290.3 | 343.1 | 286.8 | 248.4 | 384
550 | 405 | 520.2 | 374.8 | 280 | 290.9 | 343.8 | 287.2 | 248.7 | 384.2
551 | 406 | 520.4 | 376 | 280.5 | 291.4 | 344.8 | 287.4 | 249 | 384.5
552 | 407 | 520.5 | 376.8 | 281.1 | 292 | 346 | 287.6 | 249.3 | 384.7
553 | 408 | 520.6 | 377.1 | 281.7 | 292.5 | 346.9 | 288 | 249.6 | 385
554 | 409 | 520.6 | 377.5 | 282.3 | 293.1 | 347.9 | 288.3 | 249.9 | 385.1
555 | 410 | 520.7 | 378.1 | 283 | 293.6 | 348.1 | 288.6 | 250.3 | 385.4
556 | 411 | 520.8 | 378.7 | 283.6 | 294.2 | 348.4 | 289 | 250.6 | 385.6
557 | 412 | 521 | 379.5 | 284.2 | 294.8 | 347.3 | 289.3 | 250.9 | 385.7
558 | 413 | 521 | 380.1 | 284.9 | 295.4 | 347.2 | 289.4 | 251.2 | 385.9
559 | 414 | 521.1 | 380.3 | 285.4 | 295.9 | 347.4 | 289.6 | 251.5 | 386.1
560 | 415 | 521 | 380.3 | 285.9 | 296.5 | 348.5 | 289.9 | 251.8 | 386.3
561 | 416 | 521.1 | 380.7 | 286.4 | 297.1 | 349.5 | 290.3 | 252.1 | 386.5
562 | 417 | 521.3 | 381.4 | 287.1 | 297.7 | 350.4 | 290.6 | 252.5 | 386.7
563 | 418 | 521.4 | 381.9 | 287.7 | 298.3 | 351.6 | 290.9 | 252.8 | 386.8
564 | 419 | 521.5 | 382.7 | 288.3 | 298.8 | 352.1 | 291 | 253.1 | 387
565 | 420 | 521.6 | 383.7 | 288.8 | 299.4 | 351.7 | 291.2 | 253.3 | 387.2
566 | 421 | 521.6 | 384.7 | 289.3 | 299.9 | 350.9 | 291.5 | 253.5 | 387.5
567 | 422 | 521.6 | 385.3 | 289.8 | 300.5 | 350.8 | 291.8 | 253.8 | 387.7
568 | 423 | 521.7 | 385.8 | 290.3 | 301 | 352 | 292.1 | 254.2 | 387.9
569 | 424 | 521.7 | 385.9 | 290.9 | 301.6 | 353.4 | 292.4 | 254.5 | 388
570 | 425 | 521.7 | 386.2 | 291.5 | 302.1 | 353.8 | 292.6 | 254.9 | 388.1
571 | 426 | 521.8 | 387.1 | 292 | 302.7 | 354.3 | 292.9 | 255.3 | 388.3
572 | 427 | 521.9 | 387.8 | 292.5 | 303.2 | 355.2 | 293.3 | 255.6 | 388.5
573 | 428 | 522 | 388.1 | 293.1 | 303.7 | 355.3 | 293.6 | 255.9 | 388.7
574 | 429 | 522.1 | 388.8 | 293.7 | 304.2 | 354.3 | 293.7 | 256.2 | 388.9
575 | 430 | 522.2 | 389.3 | 294.3 | 304.7 | 355.5 | 294 | 256.6 | 389.1
576 | 431 | 522.3 | 390.2 | 294.6 | 305.3 | 356.4 | 294.1 | 256.8 | 389.2
577 | 432 | 522.4 | 390.8 | 295.1 | 305.8 | 356.9 | 294.3 | 257.1 | 389.4
578 | 433 | 522.4 | 391.5 | 295.8 | 306.3 | 356.9 | 294.7 | 257.5 | 389.6
579 | 434 | 522.4 | 391.8 | 296.2 | 306.9 | 357.3 | 295 | 257.8 | 389.7
580 | 435 | 522.5 | 392.1 | 296.8 | 307.4 | 358.4 | 295.2 | 258.2 | 389.8
581 | 436 | 522.5 | 392.4 | 297.4 | 307.9 | 359.6 | 295.5 | 258.5 | 390
582 | 437 | 522.4 | 393.1 | 297.9 | 308.4 | 361 | 295.8 | 258.7 | 390.1
583 | 438 | 522.4 | 393.9 | 298.4 | 309 | 361.5 | 296.1 | 259 | 390.3
584 | 439 | 522.2 | 394.4 | 299 | 309.5 | 361.6 | 296.3 | 259.2 | 390.4
585 | 440 | 522.1 | 394.8 | 299.5 | 310 | 362.6 | 296.6 | 259.5 | 390.6
586 | 441 | 522.2 | 394.9 | 300 | 310.5 | 363 | 296.8 | 259.8 | 390.8
587 | 442 | 522.1 | 395.3 | 300.4 | 311 | 364.1 | 297.2 | 260 | 391
588 | 443 | 521.8 | 395.3 | 301 | 311.6 | 364.9 | 297.4 | 260.3 | 391.1
589 | 444 | 521.6 | 395.3 | 301.6 | 312.1 | 365.3 | 297.7 | 260.6 | 391.3
590 | 445 | 521.7 | 395.7 | 302.1 | 312.6 | 365.5 | 298 | 260.9 | 391.4
591 | 446 | 521.5 | 395.9 | 302.6 | 313.1 | 364.2 | 298.3 | 261.2 | 391.5
592 | 447 | 521.4 | 396.6 | 303.1 | 313.6 | 363.4 | 298.6 | 261.4 | 391.7
593 | 448 | 521.4 | 397.4 | 303.5 | 314.2 | 362.9 | 299 | 261.7 | 391.9
594 | 449 | 521.2 | 397.5 | 304 | 314.7 | 363.7 | 299.3 | 262 | 392.1
595 | 450 | 521 | 397.6 | 304.5 | 315.2 | 364.7 | 299.6 | 262.3 | 392.2
596 | 451 | 520.7 | 397.7 | 305 | 315.7 | 365.9 | 300 | 262.5 | 392.3
597 | 452 | 520.6 | 397.9 | 305.5 | 316.2 | 366.8 | 300.4 | 262.7 | 392.5
598 | 453 | 520.7 | 397.8 | 306 | 316.7 | 367.6 | 300.8 | 262.9 | 392.6
599 | 454 | 520.7 | 398 | 306.5 | 317.3 | 367.6 | 301.2 | 263.1 | 392.7
600 | 455 | 520.7 | 398.1 | 307 | 317.8 | 367.6 | 301.5 | 263.4 | 392.8
601 | 456 | 520.6 | 398.4 | 307.6 | 318.3 | 367.7 | 302 | 263.7 | 393
602 | 457 | 520.5 | 398.6 | 308.1 | 318.8 | 368.2 | 302.4 | 263.9 | 393.1
603 | 458 | 520.6 | 398.8 | 308.7 | 319.2 | 367.5 | 302.7 | 264.1 | 393.2
604 | 459 | 520.5 | 399.3 | 309.2 | 319.7 | 367 | 303.1 | 264.3 | 393.4
605 | 460 | 520.7 | 399.9 | 309.8 | 320.2 | 367.4 | 303.6 | 264.6 | 393.5
606 | 461 | 520.9 | 400.2 | 310.2 | 320.7 | 368.4 | 304 | 264.9 | 393.7
607 | 462 | 521.1 | 400.4 | 310.7 | 321.2 | 369.1 | 304.4 | 265.1 | 393.8
608 | 463 | 521.1 | 400.5 | 311.3 | 321.7 | 369.2 | 304.8 | 265.3 | 393.9
609 | 464 | 521.2 | 400.7 | 311.8 | 322.2 | 370 | 305.2 | 265.6 | 394
610 | 465 | 521.3 | 400.8 | 312.3 | 322.8 | 371.5 | 305.5 | 265.8 | 394.1
611 | 466 | 521.3 | 400.9 | 312.7 | 323.3 | 372.5 | 306 | 266.1 | 394.2
612 | 467 | 521.3 | 401.4 | 313.3 | 323.7 | 373 | 306.5 | 266.4 | 394.4
613 | 468 | 521.3 | 401.7 | 313.8 | 324.2 | 373 | 306.9 | 266.7 | 394.5
614 | 469 | 521.2 | 402.5 | 314.2 | 324.7 | 373 | 307.3 | 267.1 | 394.7
615 | 470 | 521 | 403.2 | 314.6 | 325.3 | 372.9 | 307.7 | 267.4 | 394.8
616 | 471 | 521 | 403.7 | 315.2 | 325.8 | 373 | 308 | 267.7 | 394.9
617 | 472 | 521.1 | 404.4 | 315.6 | 326.3 | 373.7 | 308.3 | 268 | 395.1
618 | 473 | 521.3 | 405.4 | 316.1 | 326.8 | 373.6 | 308.8 | 268.3 | 395.2
619 | 474 | 521.5 | 405.9 | 316.6 | 327.3 | 374.5 | 309.2 | 268.6 | 395.4
620 | 475 | 521.7 | 406.6 | 317 | 327.8 | 375.3 | 309.5 | 268.9 | 395.5
621 | 476 | 521.7 | 406.8 | 317.5 | 328.3 | 376.2 | 309.7 | 269.2 | 395.7
622 | 477 | 521.8 | 407.2 | 318.1 | 328.7 | 375.2 | 310.1 | 269.5 | 395.8
623 | 478 | 521.7 | 407.9 | 318.6 | 329.2 | 374.2 | 310.3 | 269.8 | 395.9
624 | 479 | 521.7 | 408.5 | 319.1 | 329.7 | 374.9 | 310.8 | 270 | 396
625 | 480 | 521.8 | 409.4 | 319.6 | 330.1 | 375.4 | 311.1 | 270.3 | 396.1
626 | 481 | 522 | 410.2 | 320.1 | 330.6 | 375.9 | 311.6 | 270.5 | 396.2
627 | 482 | 522.1 | 411 | 320.7 | 331.1 | 375.8 | 312 | 270.8 | 396.3
628 | 483 | 522.1 | 411.6 | 321.1 | 331.5 | 375.8 | 312.4 | 271 | 396.5
629 | 484 | 522.3 | 412.4 | 321.5 | 332 | 376.5 | 312.9 | 271.3 | 396.6
630 | 485 | 522.5 | 413.3 | 321.8 | 332.6 | 376.9 | 313.2 | 271.6 | 396.8
631 | 486 | 522.6 | 414.2 | 322.2 | 333 | 377.5 | 313.5 | 271.8 | 397
632 | 487 | 522.7 | 414.8 | 322.8 | 333.5 | 377 | 313.8 | 272 | 397.1
633 | 488 | 522.9 | 415.7 | 323.3 | 333.9 | 376.7 | 314.1 | 272.3 | 397.3
634 | 489 | 522.8 | 416.9 | 323.8 | 334.4 | 376.3 | 314.3 | 272.5 | 397.4
635 | 490 | 522.8 | 418 | 324.2 | 334.9 | 375.8 | 314.5 | 272.7 | 397.6
636 | 491 | 522.8 | 419.4 | 324.6 | 335.3 | 376.3 | 314.7 | 272.9 | 397.8
637 | 492 | 522.8 | 420.5 | 325.1 | 335.8 | 376.5 | 314.9 | 273.1 | 397.9
638 | 493 | 522.8 | 421.6 | 325.6 | 336.2 | 376.9 | 315 | 273.3 | 398
639 | 494 | 522.7 | 422.4 | 326 | 336.7 | 377.1 | 315.1 | 273.5 | 398.1
640 | 495 | 522.9 | 423.4 | 326.6 | 337.1 | 376.3 | 315.3 | 273.8 | 398.2
641 | 496 | 522.8 | 424.4 | 327 | 337.5 | 377 | 315.5 | 274.1 | 398.3
642 | 497 | 522.8 | 425.3 | 327.4 | 338 | 377.5 | 315.7 | 274.3 | 398.5
643 | 498 | 523 | 426.5 | 327.8 | 338.4 | 378.2 | 316 | 274.5 | 398.6
644 | 499 | 522.7 | 427.6 | 328.3 | 338.8 | 378.7 | 316.4 | 274.8 | 398.7
645 | 500 | 522.5 | 428.5 | 328.7 | 339.3 | 378.4 | 316.6 | 275.1 | 398.9
646 | 501 | 522.6 | 429.1 | 329.1 | 339.7 | 379.6 | 316.9 | 275.4 | 399
647 | 502 | 522.5 | 429.7 | 329.5 | 340.2 | 380 | 317.2 | 275.8 | 399.1
648 | 503 | 522.6 | 430.5 | 330 | 340.6 | 379.9 | 317.5 | 276.1 | 399.2
649 | 504 | 522.7 | 431.1 | 330.4 | 341 | 380.2 | 317.7 | 276.3 | 399.3
650 | 505 | 522.6 | 431.8 | 330.9 | 341.5 | 380.4 | 318 | 276.6 | 399.4
651 | 506 | 522.4 | 432.1 | 331.3 | 341.9 | 379.3 | 318.3 | 276.8 | 399.5
652 | 507 | 522.4 | 432.7 | 331.7 | 342.3 | 379 | 318.5 | 277.1 | 399.6
653 | 508 | 522.4 | 433.4 | 332 | 342.8 | 379.7 | 318.7 | 277.3 | 399.7
654 | 509 | 522.3 | 434.2 | 332.5 | 343.2 | 380.2 | 319 | 277.5 | 399.8
655 | 510 | 522.2 | 434.6 | 332.9 | 343.6 | 380.4 | 319.3 | 277.7 | 399.9
656 | 511 | 522.2 | 435.5 | 333.3 | 344 | 379.6 | 319.6 | 278 | 400
657 | 512 | 522.2 | 436.7 | 333.7 | 344.5 | 378.9 | 319.9 | 278.1 | 400.2
658 | 513 | 522 | 437.7 | 334.1 | 344.9 | 378 | 320.3 | 278.3 | 400.3
659 | 514 | 521.7 | 438.6 | 334.5 | 345.3 | 379.2 | 320.5 | 278.5 | 400.5
660 | 515 | 521.7 | 439.7 | 334.9 | 345.7 | 380.1 | 320.9 | 278.7 | 400.6
661 | 516 | 521.7 | 440.7 | 335.3 | 346.1 | 382 | 321.3 | 279 | 400.7
662 | 517 | 521.8 | 441.4 | 335.7 | 346.5 | 384.4 | 321.6 | 279.4 | 400.8
663 | 518 | 521.9 | 442.4 | 336.1 | 346.9 | 386.4 | 322 | 279.8 | 400.9
664 | 519 | 521.9 | 443.3 | 336.7 | 347.2 | 387.6 | 322.3 | 280.1 | 401
665 | 520 | 521.9 | 444.2 | 337 | 347.6 | 388.9 | 322.7 | 280.3 | 401.1
666 | 521 | 521.9 | 445.2 | 337.4 | 348 | 389.8 | 323 | 280.5 | 401.2
667 | 522 | 521.6 | 445.9 | 337.8 | 348.4 | 390.1 | 323.3 | 280.7 | 401.2
668 | 523 | 521.4 | 446.6 | 338.2 | 348.8 | 390.1 | 323.6 | 281.1 | 401.3
669 | 524 | 521.3 | 447.3 | 338.5 | 349.2 | 390.7 | 324 | 281.4 | 401.4
670 | 525 | 521.2 | 448.5 | 338.9 | 349.5 | 391 | 324.2 | 281.7 | 401.5
671 | 526 | 521.3 | 449.4 | 339.3 | 349.9 | 391.2 | 324.5 | 282 | 401.6
672 | 527 | 521.3 | 449.7 | 339.7 | 350.3 | 392 | 324.7 | 282.3 | 401.7
673 | 528 | 521.4 | 450.5 | 340.1 | 350.7 | 393.4 | 325 | 282.6 | 401.8
674 | 529 | 521.4 | 451.3 | 340.5 | 351.1 | 394.4 | 325.1 | 283 | 401.9
675 | 530 | 521.3 | 452.2 | 340.9 | 351.4 | 394.6 | 325.4 | 283.3 | 402
676 | 531 | 521.3 | 453 | 341.2 | 351.8 | 395 | 325.6 | 283.5 | 402.1
677 | 532 | 521.1 | 453.6 | 341.6 | 352.2 | 395.7 | 325.9 | 283.7 | 402.2
678 | 533 | 521.2 | 453.9 | 342 | 352.5 | 395.6 | 326.1 | 283.9 | 402.3
679 | 534 | 521.2 | 454.2 | 342.4 | 352.9 | 395.7 | 326.3 | 284.1 | 402.5
680 | 535 | 521.4 | 454.5 | 342.8 | 353.2 | 395.5 | 326.5 | 284.4 | 402.6
681 | 536 | 521.4 | 454.9 | 343.2 | 353.6 | 394.9 | 326.7 | 284.6 | 402.8
682 | 537 | 521.4 | 455 | 343.7 | 353.9 | 394.3 | 326.6 | 284.9 | 402.8
683 | 538 | 521.2 | 455.2 | 344.1 | 354.3 | 394.1 | 326.6 | 285.1 | 402.9
684 | 539 | 521.2 | 455.7 | 344.5 | 354.6 | 394.9 | 326.7 | 285.4 | 403
685 | 540 | 521.4 | 456.7 | 344.9 | 354.9 | 395.6 | 326.9 | 285.6 | 403
686 | 541 | 521.4 | 457.5 | 345.4 | 355.3 | 396.6 | 327.1 | 285.9 | 403.1
687 | 542 | 521.3 | 458.2 | 345.7 | 355.6 | 397.7 | 327.3 | 286.1 | 403.1
688 | 543 | 521.3 | 458.7 | 346.2 | 356 | 399.2 | 327.5 | 286.3 | 403.2
689 | 544 | 521.4 | 458.8 | 346.6 | 356.3 | 400.5 | 327.9 | 286.5 | 403.3
690 | 545 | 521.4 | 459.1 | 347.1 | 356.6 | 401.4 | 328.1 | 286.7 | 403.3
691 | 546 | 521.6 | 459.5 | 347.5 | 356.9 | 401.9 | 328.4 | 287 | 403.4
692 | 547 | 521.7 | 460.1 | 347.9 | 357.3 | 402.6 | 328.7 | 287.2 | 403.5
693 | 548 | 521.6 | 459.9 | 348.3 | 357.6 | 403.1 | 329 | 287.4 | 403.5
694 | 549 | 521.5 | 459.7 | 348.6 | 357.9 | 403.6 | 329.4 | 287.7 | 403.5
695 | 550 | 521.5 | 460.2 | 348.9 | 358.2 | 403.9 | 329.8 | 288 | 403.6
696 | 551 | 521.5 | 460.7 | 349.3 | 358.5 | 404.2 | 330.1 | 288.3 | 403.7
697 | 552 | 521.5 | 461 | 349.7 | 358.8 | 404.6 | 330.3 | 288.6 | 403.8
698 | 553 | 521.6 | 461.5 | 350 | 359.1 | 405.1 | 330.6 | 288.8 | 403.8
699 | 554 | 521.6 | 461.6 | 350.4 | 359.4 | 405.7 | 330.8 | 289.1 | 403.9
700 | 555 | 521.4 | 462 | 350.7 | 359.8 | 406.1 | 331.1 | 289.3 | 404
701 | 556 | 521.1 | 461.9 | 351 | 360.1 | 406.1 | 331.5 | 289.5 | 404.1
702 | 557 | 520.9 | 462.7 | 351.3 | 360.4 | 406.3 | 331.8 | 289.8 | 404.1
703 | 558 | 520.8 | 463.1 | 351.7 | 360.7 | 406.8 | 332 | 290.1 | 404.2
704 | 559 | 520.7 | 463.7 | 352 | 361 | 407.3 | 332.3 | 290.3 | 404.3
705 | 560 | 520.8 | 463.7 | 352.3 | 361.3 | 407.6 | 332.7 | 290.6 | 404.4
706 | 561 | 520.9 | 463.8 | 352.7 | 361.6 | 408.1 | 333.1 | 290.9 | 404.5
707 | 562 | 520.9 | 463.7 | 353 | 361.9 | 408.9 | 333.4 | 291.2 | 404.5
708 | 563 | 520.9 | 463.8 | 353.3 | 362.3 | 409.4 | 333.8 | 291.5 | 404.6
709 | 564 | 520.8 | 464.6 | 353.7 | 362.6 | 409.9 | 334.1 | 291.8 | 404.7
710 | 565 | 520.8 | 465.2 | 354 | 362.9 | 410.2 | 334.4 | 292 | 404.8
711 | 566 | 520.7 | 465.7 | 354.3 | 363.2 | 410.8 | 334.6 | 292.3 | 404.9
712 | 567 | 520.7 | 465.7 | 354.6 | 363.5 | 411.5 | 334.8 | 292.5 | 405
713 | 568 | 520.7 | 465.8 | 354.8 | 363.9 | 412.2 | 335 | 292.8 | 405.1
714 | 569 | 520.6 | 466.2 | 355 | 364.3 | 413 | 335.2 | 293.1 | 405.2
715 | 570 | 520.7 | 466 | 355.2 | 364.6 | 413.5 | 335.5 | 293.3 | 405.2
716 | 571 | 520.7 | 465.9 | 355.5 | 365 | 413.9 | 335.8 | 293.6 | 405.3
717 | 572 | 520.6 | 466.1 | 355.8 | 365.3 | 414.7 | 336 | 293.8 | 405.4
718 | 573 | 520.5 | 466.1 | 355.8 | 365.8 | 415.6 | 336.3 | 294 | 405.4
719 | 574 | 520.6 | 465.8 | 356 | 366.2 | 416.1 | 336.5 | 294.3 | 405.5
720 | 575 | 520.6 | 464.2 | 356.3 | 366.6 | 416 | 336.7 | 294.5 | 405.5
721 | 576 | 520.5 | 463.9 | 356.6 | 366.9 | 416.2 | 336.7 | 294.7 | 405.6
722 | 577 | 520.5 | 463.6 | 357 | 367.3 | 416.7 | 336.7 | 294.9 | 405.7
723 | 578 | 520.4 | 464 | 357.2 | 367.7 | 417.3 | 336.8 | 295.1 | 405.8
724 | 579 | 520.3 | 463.6 | 357.6 | 368 | 418 | 337 | 295.4 | 405.8
725 | 580 | 520.2 | 463.2 | 357.8 | 368.4 | 418.5 | 337.1 | 295.7 | 405.8
726 | 581 | 520.4 | 462.3 | 358.1 | 368.7 | 419 | 337.4 | 295.9 | 405.9
727 | 582 | 520.5 | 461.2 | 358.4 | 369 | 419.3 | 337.6 | 296.1 | 405.9
728 | 583 | 520.6 | 460.5 | 358.7 | 369.3 | 419.6 | 337.8 | 296.3 | 406
729 | 584 | 520.8 | 459.8 | 359.1 | 369.6 | 419.5 | 337.9 | 296.5 | 406.1
730 | 585 | 521 | 459.2 | 359.4 | 370 | 419.7 | 338.1 | 296.6 | 406.2
731 | 586 | 521 | 458.4 | 359.6 | 370.3 | 419.7 | 338.2 | 296.9 | 406.2
732 | 587 | 520.9 | 457.6 | 359.7 | 370.7 | 420.1 | 338.4 | 297.1 | 406.3
733 | 588 | 521.1 | 456.7 | 360.1 | 371 | 419.8 | 338.7 | 297.3 | 406.4
734 | 589 | 521.6 | 456.3 | 360.3 | 371.5 | 419.7 | 338.9 | 297.5 | 406.4
735 | 590 | 522 | 455.4 | 360.7 | 371.8 | 420 | 339.2 | 297.7 | 406.5
736 | 591 | 522.1 | 454.9 | 360.8 | 372.3 | 420.2 | 339.5 | 297.9 | 406.5
737 | 592 | 522.3 | 454.4 | 361.2 | 372.7 | 421.1 | 339.9 | 298.1 | 406.5
738 | 593 | 522.3 | 453.9 | 361.7 | 373.1 | 422 | 340.2 | 298.4 | 406.6
739 | 594 | 522.2 | 453.4 | 362.1 | 373.5 | 422.6 | 340.5 | 298.6 | 406.6
740 | 595 | 522 | 452.8 | 362.5 | 373.9 | 423.4 | 340.8 | 298.8 | 406.6
741 | 596 | 521.8 | 452.2 | 363.1 | 374.3 | 424.3 | 341 | 299.1 | 406.7
742 | 597 | 521.7 | 451.8 | 363.6 | 374.7 | 425.5 | 341.2 | 299.3 | 406.8
743 | 598 | 521.8 | 451.4 | 364 | 375.1 | 426.9 | 341.3 | 299.5 | 406.9
744 | 599 | 521.5 | 451.1 | 364.5 | 375.6 | 428.1 | 341.5 | 299.6 | 406.9
745 | 600 | 521.4 | 450.8 | 365.1 | 376 | 428.5 | 341.7 | 299.8 | 407
746 | 601 | 521.4 | 450.6 | 365.4 | 376.6 | 428.3 | 341.9 | 300 | 407
747 | 602 | 521.4 | 450.3 | 365.9 | 377 | 428.3 | 342 | 300.2 | 407.1
748 | 603 | 521.3 | 449.8 | 366.6 | 377.4 | 428.3 | 342.2 | 300.5 | 407.1
749 | 604 | 521.2 | 449.2 | 367 | 377.8 | 428.5 | 342.3 | 300.7 | 407.2
750 | 605 | 521.2 | 449 | 367.5 | 378.3 | 428.6 | 342.5 | 300.9 | 407.3
751 | 606 | 521.3 | 448.6 | 368.1 | 378.7 | 428.2 | 342.7 | 301 | 407.4
752 | 607 | 521.4 | 448.6 | 368.6 | 379.2 | 427.8 | 342.9 | 301.2 | 407.5
753 | 608 | 521.5 | 448.6 | 369.1 | 379.7 | 428 | 342.9 | 301.4 | 407.5
754 | 609 | 521.6 | 448.4 | 369.6 | 380.1 | 428.4 | 343 | 301.6 | 407.6
755 | 610 | 521.7 | 448.2 | 370.1 | 380.6 | 428.7 | 343.2 | 301.9 | 407.7
756 | 611 | 521.8 | 447.9 | 370.5 | 381.1 | 429.3 | 343.4 | 302.1 | 407.7
757 | 612 | 522.1 | 447.7 | 370.8 | 381.6 | 429.8 | 343.6 | 302.3 | 407.8
758 | 613 | 522.4 | 447.3 | 371.1 | 382.1 | 430.4 | 343.6 | 302.4 | 407.8
759 | 614 | 522.4 | 446.8 | 371.5 | 382.7 | 431.6 | 343.8 | 302.7 | 407.9
760 | 615 | 522.3 | 446.9 | 371.9 | 383.2 | 431.6 | 343.9 | 303 | 407.9
761 | 616 | 522.1 | 447.6 | 372.2 | 383.8 | 431.3 | 344.1 | 303.3 | 407.9
762 | 617 | 522 | 448.6 | 372.6 | 384.3 | 431 | 344.3 | 303.5 | 408
763 | 618 | 521.9 | 449 | 373.2 | 384.8 | 429.8 | 344.3 | 303.7 | 408
764 | 619 | 521.9 | 445 | 373.6 | 385.4 | 428.2 | 344.5 | 303.9 | 408.1
765 | 620 | 521.9 | 418.6 | 373.8 | 386.1 | 424.7 | 344.6 | 304.1 | 408.1
766 | 621 | 521.9 | 392 | 374.2 | 386.7 | 420.4 | 344.7 | 304.2 | 408.2
767 | 622 | 521.8 | 370.2 | 374.6 | 387.4 | 416.1 | 344.8 | 304.3 | 408.2
768 | 623 | 521.5 | 352.3 | 375 | 388 | 411.5 | 344.9 | 304.5 | 408.2
769 | 624 | 521.3 | 338.7 | 375.5 | 388.7 | 407 | 345.1 | 304.6 | 408.2
770 | 625 | 521.1 | 324.7 | 375.9 | 389.3 | 403.7 | 345.2 | 304.7 | 408.2
771 | 626 | 520.8 | 312.3 | 376.4 | 390 | 395.9 | 345.3 | 304.9 | 408.3
772 | 627 | 520.6 | 303.2 | 377 | 390.6 | 383.8 | 345.3 | 305.1 | 408.3
773 | 628 | 520.4 | 295 | 377.5 | 391.2 | 375.6 | 345.5 | 305.3 | 408.3
774 | 629 | 520.3 | 288.7 | 378.1 | 391.9 | 368 | 345.7 | 305.3 | 408.4
775 | 630 | 520.3 | 284 | 378.7 | 392.6 | 357 | 345.9 | 305.5 | 408.7
776 | 631 | 520.3 | 279.8 | 379.3 | 393.3 | 351.9 | 346.1 | 305.7 | 408.9
777 | 632 | 520.2 | 274.2 | 379.9 | 394 | 346.8 | 346.2 | 305.9 | 408.8
778 | 633 | 520.1 | 271.5 | 380.5 | 394.7 | 340.5 | 346.3 | 306.1 | 408.8
779 | 634 | 520.2 | 268.6 | 381.1 | 395.5 | 336.3 | 346.3 | 306.3 | 408.8
780 | 635 | 520.3 | 265.8 | 381.7 | 396.3 | 329.7 | 346.3 | 306.5 | 408.8
781 | 636 | 520.3 | 263.8 | 382.3 | 397 | 324.9 | 346.2 | 306.7 | 408.8
782 | 637 | 520.5 | 261.9 | 382.9 | 397.8 | 322.5 | 346.1 | 306.9 | 408.8
783 | 638 | 520.8 | 260.2 | 383.6 | 398.6 | 320.2 | 346 | 307.1 | 408.9
784 | 639 | 521 | 258.4 | 384.3 | 399.4 | 318.6 | 346.1 | 307.4 | 408.9
785 | 640 | 521.1 | 258.3 | 384.9 | 400.2 | 318.8 | 346.1 | 307.6 | 408.9
786 | 641 | 521.1 | 256 | 385.6 | 401 | 315.2 | 346.3 | 307.8 | 408.9
787 | 642 | 521.1 | 253.8 | 386.2 | 401.8 | 313 | 346.5 | 308 | 408.9
788 | 643 | 521.2 | 251.7 | 386.9 | 402.7 | 311.1 | 346.7 | 308.2 | 409
789 | 644 | 521.3 | 250.6 | 387.6 | 403.5 | 307.7 | 346.8 | 308.4 | 409
790 | 645 | 521.4 | 251.4 | 388.3 | 404.4 | 301.8 | 347 | 308.6 | 409.1
791 | 646 | 521.4 | 251.7 | 389 | 405.2 | 297 | 347.1 | 308.8 | 409.2
792 | 647 | 521.3 | 251.8 | 389.7 | 406.1 | 295.3 | 347.2 | 309 | 409.2
793 | 648 | 521.1 | 254.9 | 390.4 | 407 | 292.7 | 347.2 | 309.3 | 409.2
794 | 649 | 521.2 | 257.9 | 391.2 | 407.8 | 291.6 | 347.1 | 309.6 | 409.2
795 | 650 | 521.4 | 256.4 | 391.9 | 408.7 | 295.2 | 347.2 | 309.9 | 409.2
796 | 651 | 521.6 | 253.6 | 392.6 | 409.6 | 297.7 | 347.2 | 310.1 | 409.2
797 | 652 | 521.7 | 252.9 | 393.3 | 410.4 | 299.5 | 347.4 | 310.3 | 409.2
798 | 653 | 521.8 | 252.8 | 394 | 411.3 | 300.6 | 347.5 | 310.5 | 409.2
799 | 654 | 521.8 | 251.8 | 394.6 | 412.2 | 301.1 | 347.6 | 310.7 | 409.2
800 | 655 | 521.7 | 251.9 | 395.3 | 413.1 | 300 | 347.8 | 310.9 | 409.3
801 | 656 | 521.8 | 250.1 | 396 | 414 | 301 | 348 | 311.1 | 409.3
802 | 657 | 521.9 | 249.3 | 396.8 | 414.8 | 301 | 348.2 | 311.3 | 409.3
803 | 658 | 522.1 | 249.4 | 397.6 | 415.7 | 300.8 | 348.3 | 311.5 | 409.4
804 | 659 | 522.3 | 249.5 | 398.3 | 416.5 | 302 | 348.2 | 311.7 | 409.4
805 | 660 | 522.5 | 248.2 | 399 | 417.4 | 304.5 | 348.2 | 311.9 | 409.4
806 | 661 | 522.5 | 247.6 | 399.7 | 418.2 | 305.8 | 348.3 | 312.1 | 409.4
807 | 662 | 522.5 | 247.7 | 400.4 | 419 | 309 | 348.5 | 312.3 | 409.4
808 | 663 | 522.4 | 247 | 401.1 | 419.8 | 312.9 | 348.6 | 312.6 | 409.4
809 | 664 | 522.4 | 246.2 | 401.8 | 420.6 | 315 | 348.6 | 312.8 | 409.5
810 | 665 | 522.4 | 246.4 | 402.6 | 421.4 | 316.7 | 348.7 | 313.1 | 409.5
811 | 666 | 522.4 | 245.9 | 403.3 | 422.2 | 320.5 | 348.8 | 313.4 | 409.5
812 | 667 | 522.3 | 244.9 | 404 | 423.1 | 325.8 | 348.8 | 313.7 | 409.5
813 | 668 | 522 | 244 | 404.7 | 423.8 | 331.4 | 348.9 | 314 | 409.5
814 | 669 | 521.9 | 243.5 | 405.4 | 424.6 | 332.1 | 349 | 314.2 | 409.6
815 | 670 | 521.9 | 243.6 | 406.2 | 425.4 | 329.3 | 349.1 | 314.4 | 409.6
816 | 671 | 522 | 244.1 | 406.9 | 426.2 | 325.6 | 349.3 | 314.8 | 409.7
817 | 672 | 522.1 | 244.8 | 407.6 | 426.9 | 325.1 | 349.4 | 315 | 409.7
818 | 673 | 522 | 245.2 | 408.3 | 427.7 | 325.7 | 349.5 | 315.1 | 409.8
819 | 674 | 521.9 | 244.8 | 409.1 | 428.4 | 324.8 | 349.5 | 315.3 | 409.9
820 | 675 | 521.8 | 244.8 | 409.9 | 429.2 | 323.5 | 349.5 | 315.6 | 410
821 | 676 | 521.8 | 244.2 | 410.7 | 429.9 | 320.4 | 349.5 | 315.7 | 410
822 | 677 | 521.7 | 244.7 | 411.4 | 430.7 | 319 | 349.5 | 316 | 410
823 | 678 | 521.5 | 244.7 | 412.2 | 431.5 | 319.5 | 349.5 | 316.2 | 410.1
824 | 679 | 521.5 | 244.7 | 413 | 432.2 | 321.8 | 349.5 | 316.4 | 410.1
825 | 680 | 521.4 | 245.3 | 413.7 | 433.1 | 324.6 | 349.7 | 316.6 | 410.1
826 | 681 | 521.5 | 245 | 414.6 | 433.9 | 323.2 | 349.8 | 316.8 | 410.1
827 | 682 | 521.5 | 244.5 | 415.4 | 434.7 | 320.3 | 349.9 | 317 | 410.2
828 | 683 | 521.3 | 245.9 | 416.3 | 435.5 | 314.9 | 350 | 317.1 | 410.2
829 | 684 | 521.2 | 247.9 | 417 | 436.4 | 313.1 | 350.2 | 317.3 | 410.3
830 | 685 | 521 | 248.6 | 417.9 | 437.3 | 313.4 | 350.3 | 317.5 | 410.4
831 | 686 | 521 | 247.4 | 418.9 | 438.1 | 316.1 | 350.4 | 317.6 | 410.4
832 | 687 | 521.2 | 246.7 | 419.8 | 439.1 | 316.4 | 350.6 | 317.8 | 410.4
833 | 688 | 521.3 | 245.3 | 420.8 | 440 | 316.3 | 350.7 | 318.1 | 410.4
834 | 689 | 521.5 | 244.9 | 421.8 | 441.1 | 317.1 | 350.8 | 318.4 | 410.4
835 | 690 | 521.5 | 244.8 | 422.8 | 442.3 | 316.3 | 350.8 | 318.6 | 410.5
836 | 691 | 521.3 | 246.7 | 423.8 | 443.8 | 313.6 | 350.8 | 318.8 | 410.5
837 | 692 | 521.3 | 249.9 | 424.8 | 445.9 | 309.8 | 350.9 | 319 | 410.5
838 | 693 | 521.5 | 252.6 | 425.8 | 448.4 | 305.8 | 351.1 | 319.2 | 410.6
839 | 694 | 521.5 | 254.8 | 426.9 | 451.5 | 307.1 | 351 | 319.5 | 410.7
840 | 695 | 521.3 | 255.3 | 427.9 | 454.9 | 310.7 | 351.1 | 319.7 | 410.7
841 | 696 | 521.3 | 255.6 | 429.1 | 458.5 | 315.7 | 351.3 | 319.9 | 410.8
842 | 697 | 521.4 | 253.4 | 430.2 | 462.5 | 318.7 | 351.5 | 320.2 | 410.8
843 | 698 | 521.2 | 251.8 | 431.3 | 466.6 | 323.3 | 351.7 | 320.4 | 410.8
844 | 699 | 521.2 | 250.9 | 432.5 | 470.6 | 327.3 | 351.9 | 320.6 | 410.8
845 | 700 | 521 | 250 | 433.8 | 474.3 | 333.3 | 352 | 320.7 | 410.9
846 | 701 | 521.2 | 249.4 | 434.9 | 477.8 | 339.5 | 352.3 | 321 | 410.9
847 | 702 | 521.3 | 248.8 | 436.1 | 481.7 | 341.6 | 352.5 | 321.1 | 410.9
848 | 703 | 521.2 | 247.4 | 437.3 | 485.5 | 346.8 | 352.7 | 321.4 | 410.9
849 | 704 | 521.3 | 246 | 438.4 | 488.9 | 351.7 | 353 | 321.5 | 410.9
850 | 705 | 521.3 | 245.1 | 439.8 | 491.7 | 353.9 | 353.4 | 321.7 | 410.9
851 | 706 | 521.5 | 245 | 441.1 | 494.4 | 355.7 | 353.7 | 321.8 | 410.9
852 | 707 | 521.5 | 244.8 | 442.5 | 497 | 360.1 | 353.9 | 322 | 410.9
853 | 708 | 521.6 | 244.2 | 443.8 | 498.8 | 365.1 | 354.1 | 322.3 | 411
854 | 709 | 521.6 | 243.6 | 445.1 | 500.2 | 368.7 | 354.4 | 322.6 | 411
855 | 710 | 521.7 | 243.9 | 446.2 | 501.7 | 370.2 | 354.7 | 322.8 | 411
856 | 711 | 522 | 244.1 | 447.4 | 503.1 | 374.3 | 355 | 323 | 411.1
857 | 712 | 522.1 | 243.2 | 448.6 | 504.7 | 377.1 | 355.3 | 323.2 | 411.1
858 | 713 | 522.2 | 243.4 | 449.1 | 506.3 | 379 | 355.6 | 323.4 | 411.2
859 | 714 | 522.3 | 242.7 | 449.7 | 508 | 382.1 | 355.7 | 323.6 | 411.3
860 | 715 | 522.3 | 242.8 | 450.5 | 509.9 | 384.8 | 355.8 | 323.8 | 411.4
861 | 716 | 522.5 | 244.3 | 451.2 | 511.9 | 386.2 | 355.8 | 324 | 411.4
862 | 717 | 522.3 | 244 | 451.6 | 514.9 | 388.9 | 356 | 324.2 | 411.5
863 | 718 | 522.4 | 244.5 | 452.2 | 518.4 | 389.4 | 356.1 | 324.4 | 411.6
864 | 719 | 522.6 | 245.2 | 452.7 | 522.9 | 386.6 | 356.3 | 324.6 | 411.7
865 | 720 | 522.8 | 244.2 | 453.2 | 527.9 | 386.9 | 356.5 | 324.7 | 411.8
866 | 721 | 522.8 | 243.5 | 453.6 | 533.3 | 388.7 | 356.7 | 325 | 411.8
867 | 722 | 522.7 | 242.6 | 454.2 | 539.4 | 390.4 | 356.9 | 325.3 | 411.9
868 | 723 | 522.6 | 242.7 | 454.9 | 545.2 | 391.7 | 357.2 | 325.6 | 411.9
869 | 724 | 522.6 | 242.3 | 455.4 | 551.3 | 394 | 357.5 | 325.8 | 412
870 | 725 | 522.5 | 241.9 | 455.9 | 557.2 | 395.5 | 357.7 | 326 | 412
871 | 726 | 522.5 | 242 | 456.4 | 563.5 | 397.4 | 357.9 | 326.3 | 412
872 | 727 | 522.5 | 241.5 | 457.1 | 570.9 | 397.9 | 358.1 | 326.5 | 412
873 | 728 | 522.5 | 241.2 | 457.6 | 578 | 398.7 | 358.1 | 326.6 | 412.1
874 | 729 | 522.3 | 240.7 | 458.4 | 583.5 | 399.8 | 358.2 | 326.9 | 412
875 | 730 | 522.1 | 240.3 | 459.2 | 587.7 | 399.4 | 358.3 | 327.1 | 412.1
876 | 731 | 522 | 239.7 | 459.9 | 589.4 | 400 | 358.4 | 327.3 | 412.1
877 | 732 | 521.9 | 239.6 | 460.5 | 591.1 | 400.6 | 358.6 | 327.5 | 412.1
878 | 733 | 521.7 | 240.3 | 461.1 | 593.4 | 401 | 358.9 | 327.8 | 412.1
879 | 734 | 521.5 | 240.9 | 461.7 | 595.7 | 402.8 | 359 | 328.1 | 412.2
880 | 735 | 521.4 | 240.5 | 462.6 | 597.1 | 405 | 359.1 | 328.3 | 412.2
881 | 736 | 521.4 | 240.5 | 463.3 | 596.8 | 406.8 | 359.3 | 328.5 | 412.2
882 | 737 | 521.3 | 240.4 | 464 | 595.5 | 408.9 | 359.2 | 328.7 | 412.2
883 | 738 | 521.2 | 240.3 | 464.7 | 594.2 | 410.8 | 359.3 | 328.9 | 412.3
884 | 739 | 521.3 | 239.9 | 465.4 | 592.6 | 412 | 359.4 | 329.1 | 412.4
885 | 740 | 521.4 | 240.2 | 466.3 | 591.4 | 413.3 | 359.5 | 329.3 | 412.5
886 | 741 | 521.3 | 239.9 | 467.1 | 591.5 | 413.9 | 359.6 | 329.5 | 412.6
887 | 742 | 521.1 | 239.2 | 467.8 | 592.2 | 412.9 | 359.7 | 329.6 | 412.7
888 | 743 | 520.9 | 238.6 | 468.6 | 593.3 | 413.1 | 359.8 | 329.7 | 412.8
889 | 744 | 520.8 | 237.8 | 469.3 | 593.8 | 414.5 | 360 | 330 | 412.8
890 | 745 | 520.7 | 237.4 | 470 | 594.5 | 415.9 | 360.1 | 330.3 | 412.8
891 | 746 | 520.7 | 237.3 | 470.7 | 595.9 | 415.1 | 360.2 | 330.4 | 412.8
892 | 747 | 520.4 | 237 | 471.3 | 597.3 | 416.4 | 360.4 | 330.6 | 412.7
893 | 748 | 520.2 | 236.8 | 471.8 | 598.9 | 415.9 | 360.6 | 330.7 | 412.8
894 | 749 | 520.2 | 236.8 | 472.2 | 600.1 | 415.5 | 360.8 | 330.9 | 412.8
895 | 750 | 520.2 | 237 | 472.7 | 600.1 | 414.7 | 360.8 | 331.1 | 412.8
896 | 751 | 520.2 | 237 | 473.3 | 599.8 | 414.5 | 360.8 | 331.3 | 412.8
897 | 752 | 520.1 | 237.6 | 473.8 | 600.2 | 414.8 | 361 | 331.4 | 412.9
898 | 753 | 520.2 | 237.1 | 474.4 | 600.5 | 414.4 | 361 | 331.7 | 412.9
899 | 754 | 520.3 | 236.9 | 475.1 | 601.2 | 413.8 | 360.9 | 331.8 | 413
900 | 755 | 520.4 | 236.5 | 475.7 | 601.5 | 414.1 | 361 | 332 | 413
901 | 756 | 520.5 | 236.1 | 476.4 | 600.8 | 414.5 | 361 | 332.2 | 413
902 | 757 | 520.7 | 235.6 | 477.2 | 601.9 | 414.4 | 361 | 332.4 | 413.1
903 | 758 | 520.9 | 235.7 | 477.8 | 603.1 | 414.5 | 361.1 | 332.5 | 413.1
904 | 759 | 521 | 237.3 | 478.7 | 604.6 | 414.5 | 361.1 | 332.7 | 413.2
905 | 760 | 521.2 | 239.2 | 479.7 | 607.7 | 414 | 361 | 332.9 | 413.3
906 | 761 | 521.5 | 240.4 | 480.7 | 610.7 | 414.3 | 361 | 333.1 | 413.3
907 | 762 | 521.7 | 239.6 | 481.7 | 613.2 | 414.4 | 361 | 333.3 | 413.4
908 | 763 | 521.8 | 240.8 | 482.8 | 615.1 | 413.3 | 361.1 | 333.5 | 413.4
909 | 764 | 521.9 | 241.1 | 484 | 617.9 | 413.5 | 361 | 333.6 | 413.5
910 | 765 | 522 | 241.3 | 485.4 | 618.9 | 413.4 | 360.9 | 333.8 | 413.5
911 | 766 | 522.1 | 240.5 | 486.7 | 620.3 | 413.1 | 360.9 | 334 | 413.6
912 | 767 | 522.3 | 240.2 | 488 | 621.2 | 411.2 | 360.9 | 334 | 413.6
913 | 768 | 522.3 | 240.5 | 489.4 | 623.7 | 408.7 | 361.1 | 334.2 | 413.6
914 | 769 | 522.2 | 240.2 | 490.7 | 627.2 | 409.3 | 361.2 | 334.4 | 413.6
915 | 770 | 522.3 | 239.7 | 492.1 | 628.9 | 409.9 | 361.4 | 334.6 | 413.6
916 | 771 | 522.6 | 239.3 | 493.6 | 629.9 | 410.8 | 361.4 | 334.8 | 413.7
917 | 772 | 522.8 | 239.1 | 495.2 | 629 | 412.1 | 361.5 | 334.9 | 413.7
918 | 773 | 523.1 | 238.9 | 496.7 | 628.1 | 413.7 | 361.6 | 335.1 | 413.7
919 | 774 | 523.3 | 239.2 | 498.1 | 623.4 | 414.8 | 361.8 | 335.3 | 413.8
920 | 775 | 523.3 | 239.2 | 499.5 | 618.2 | 416.8 | 362 | 335.5 | 413.8
921 | 776 | 523.1 | 239.5 | 500.9 | 614.1 | 417.5 | 362.2 | 335.7 | 413.9
922 | 777 | 523 | 239.8 | 502.4 | 613.7 | 418.7 | 362.4 | 335.9 | 413.9
923 | 778 | 522.9 | 239.6 | 504.1 | 613.6 | 418.8 | 362.6 | 336.1 | 414
924 | 779 | 522.9 | 239.2 | 506.5 | 613.6 | 418.2 | 363 | 336.3 | 414
925 | 780 | 523 | 238.2 | 508.4 | 614.9 | 418.3 | 363.2 | 336.5 | 414.1
926 | 781 | 523.1 | 237.5 | 510.4 | 616.2 | 417.6 | 363.5 | 336.6 | 414.2
927 | 782 | 523 | 237.6 | 512.7 | 619.2 | 416.6 | 363.7 | 336.8 | 414.2
928 | 783 | 522.7 | 237.8 | 515.1 | 623.3 | 416.4 | 363.8 | 337 | 414.2
929 | 784 | 522.5 | 238.1 | 517 | 626 | 417.1 | 363.8 | 337.2 | 414.2
930 | 785 | 522.2 | 239.5 | 518.6 | 628.6 | 417 | 363.9 | 337.3 | 414.3
931 | 786 | 522.1 | 241.3 | 520.4 | 631.9 | 416.6 | 364 | 337.4 | 414.3
932 | 787 | 522 | 242.4 | 522.4 | 636.1 | 414.9 | 364 | 337.6 | 414.2
933 | 788 | 521.6 | 241.6 | 524.1 | 640.8 | 414.7 | 364 | 337.8 | 414.2
934 | 789 | 521.3 | 241.1 | 525.6 | 642.4 | 414.7 | 364.2 | 338 | 414.2
935 | 790 | 521 | 240.7 | 527.1 | 643.9 | 415.2 | 364.4 | 338.1 | 414.2
936 | 791 | 520.8 | 240.5 | 528.4 | 646.7 | 415.6 | 364.6 | 338.3 | 414.2
937 | 792 | 520.8 | 240.4 | 529.6 | 650.8 | 414.7 | 364.9 | 338.5 | 414.2
938 | 793 | 520.8 | 240.2 | 530.5 | 652.5 | 414.5 | 365 | 338.6 | 414.2
939 | 794 | 520.8 | 239.9 | 532.1 | 651.6 | 415.5 | 365.2 | 338.8 | 414.2
940 | 795 | 520.8 | 239.1 | 533.5 | 650 | 418.3 | 365.2 | 339 | 414.1
941 | 796 | 520.8 | 239.2 | 534.9 | 647.1 | 420.6 | 365.4 | 339.3 | 414.1
942 | 797 | 520.8 | 239.7 | 536.2 | 642.2 | 422.2 | 365.6 | 339.5 | 414.1
943 | 798 | 520.8 | 239.9 | 537.5 | 639.3 | 422.1 | 365.8 | 339.7 | 414.1
944 | 799 | 520.9 | 240.1 | 538.5 | 640.2 | 421.8 | 365.9 | 339.9 | 414.2
945 | 800 | 521 | 239.5 | 539.4 | 640.2 | 422.3 | 366.1 | 340.1 | 414.2
946 | 801 | 521 | 239.4 | 540.5 | 638.4 | 422 | 366.3 | 340.4 | 414.2
947 | 802 | 521.1 | 239.3 | 541.8 | 637.2 | 422.6 | 366.4 | 340.6 | 414.2
948 | 803 | 521 | 238.8 | 542.9 | 634.9 | 424 | 366.4 | 340.8 | 414.2
949 | 804 | 521 | 239.9 | 544.2 | 633.5 | 424 | 366.5 | 341 | 414.3
950 | 805 | 520.9 | 240.4 | 545.4 | 635.8 | 422.8 | 366.5 | 341.2 | 414.3
951 | 806 | 520.9 | 241.4 | 546.7 | 636.4 | 424.1 | 366.5 | 341.4 | 414.4
952 | 807 | 521 | 242 | 548 | 638.4 | 424.7 | 366.6 | 341.6 | 414.4
953 | 808 | 521.2 | 242.8 | 549.9 | 640.3 | 430.1 | 366.5 | 341.8 | 414.8
954 | 809 | 521.4 | 244.1 | 552.6 | 639.9 | 443.4 | 366.5 | 342.3 | 415.3
955 | 810 | 521.5 | 246.5 | 555.7 | 640.6 | 457.2 | 366.7 | 342.7 | 416.4
956 | 811 | 521.4 | 248.3 | 559.3 | 641.8 | 470.9 | 366.7 | 343.3 | 418.3
957 | 812 | 521.4 | 252.1 | 562 | 640.9 | 505.3 | 366.9 | 343.9 | 420.4
958 | 813 | 521.5 | 253.8 | 564.5 | 639.8 | 557.8 | 367.2 | 344.7 | 422.3
959 | 814 | 521.7 | 255.4 | 567.3 | 638 | 602.2 | 367.4 | 345.5 | 424.4
960 | 815 | 521.8 | 257.6 | 569.4 | 636.2 | 639.6 | 367.6 | 346.3 | 426.8
961 | 816 | 521.9 | 260.5 | 570 | 637.1 | 670.9 | 367.8 | 347.2 | 429.2
962 | 817 | 522 | 263.3 | 569.9 | 637.7 | 699.9 | 368 | 348.1 | 431.7
963 | 818 | 522.1 | 269.1 | 569.4 | 639.5 | 722.4 | 368.1 | 348.9 | 434.1
964 | 819 | 522.2 | 275.1 | 569.2 | 644.5 | 739.5 | 368.3 | 349.8 | 436.3
965 | 820 | 522.4 | 280.6 | 569.2 | 647.8 | 749.4 | 368.6 | 350.6 | 438.4
966 | 821 | 522.5 | 286 | 569.8 | 645.8 | 758.1 | 368.9 | 351.5 | 440.4
967 | 822 | 522.7 | 290 | 570.8 | 641.4 | 764.1 | 369.3 | 352.3 | 442.3
968 | 823 | 522.8 | 292.7 | 572.1 | 636.4 | 768.5 | 369.7 | 353.2 | 444.3
969 | 824 | 522.8 | 295 | 573.7 | 631.6 | 771.8 | 370 | 354 | 446.4
970 | 825 | 522.8 | 295.9 | 575.2 | 626.2 | 764.6 | 370.6 | 354.9 | 448.7
971 | 826 | 522.7 | 297.1 | 576.9 | 620.7 | 757.6 | 371.3 | 355.8 | 451.1
972 | 827 | 522.6 | 297.5 | 578.3 | 616.5 | 766.9 | 371.9 | 356.5 | 453.4
973 | 828 | 522.5 | 297.6 | 579.9 | 614.1 | 783.3 | 372.4 | 357.3 | 455.6
974 | 829 | 522.4 | 298.2 | 581.2 | 612.8 | 800 | 373.2 | 358 | 457.7
975 | 830 | 522.3 | 300 | 582.4 | 612.2 | 821.4 | 374.1 | 358.6 | 459.9
976 | 831 | 522.1 | 300.7 | 583.3 | 612.4 | 841.8 | 375.3 | 359.3 | 462.1
977 | 832 | 521.9 | 301.5 | 584 | 613.1 | 839.3 | 376.4 | 360 | 464.2
978 | 833 | 521.7 | 301.8 | 584.6 | 613.5 | 830.6 | 377.4 | 360.7 | 466.3
979 | 834 | 521.5 | 301.7 | 585.5 | 613.7 | 820 | 378.4 | 361.4 | 468.6
980 | 835 | 521.3 | 301.8 | 586.2 | 614.8 | 813.8 | 379.7 | 362 | 470.9
981 | 836 | 521 | 302.8 | 586.8 | 616.8 | 796.6 | 381 | 362.6 | 473.1
982 | 837 | 520.7 | 305.1 | 587.5 | 618.1 | 776.2 | 382.3 | 363.3 | 475.5
983 | 838 | 520.2 | 306.9 | 587.9 | 619.5 | 759.6 | 383.8 | 364 | 477.7
984 | 839 | 519.9 | 305.8 | 588.6 | 620.7 | 757.9 | 385.3 | 364.7 | 479.8
985 | 840 | 519.7 | 305.2 | 589.2 | 622.5 | 757.1 | 386.7 | 365.5 | 481.8
986 | 841 | 519.5 | 304.9 | 589.5 | 626.8 | 742 | 388 | 366.4 | 483.9
987 | 842 | 519.2 | 305.6 | 589.9 | 635.7 | 728.9 | 389.2 | 367.3 | 485.9
988 | 843 | 518.9 | 306.7 | 591 | 645 | 712.7 | 390.2 | 368.3 | 487.9
989 | 844 | 518.5 | 307.1 | 592.2 | 655.3 | 693.5 | 391.3 | 369.3 | 489.9
990 | 845 | 518.2 | 307.3 | 592.9 | 665.4 | 669.3 | 392.2 | 370.2 | 492
991 | 846 | 517.9 | 309.6 | 593.4 | 674.1 | 661.3 | 393.4 | 371.2 | 493.9
992 | 847 | 517.6 | 311.1 | 594.1 | 680.8 | 667 | 394.7 | 372.3 | 495.6
993 | 848 | 517 | 309.9 | 595.2 | 688 | 663.3 | 395.8 | 373.3 | 497.3
994 | 849 | 516.2 | 309.3 | 596.4 | 694.7 | 651.7 | 396.9 | 374.3 | 499
995 | 850 | 515.6 | 309.4 | 597.6 | 701.2 | 637 | 397.4 | 375.3 | 500.6
996 | 851 | 514.9 | 308.5 | 599 | 708.2 | 626.5 | 397.7 | 376.3 | 502.3
997 | 852 | 514 | 309 | 600.6 | 712.4 | 627.5 | 398.6 | 377.2 | 504
998 | 853 | 513.1 | 310.8 | 602.3 | 713.8 | 647.4 | 399.4 | 378.1 | 505.5
999 | 854 | 512.1 | 310.2 | 604.3 | 714.4 | 643.7 | 400 | 379 | 507
1000 | 855 | 511.1 | 309.1 | 607 | 713.4 | 649.9 | 400.6 | 380 | 508.2
1001 | 856 | 510 | 307.2 | 609.2 | 712.8 | 650.3 | 401.4 | 380.9 | 509.5
1002 | 857 | 508.8 | 304.7 | 611.1 | 714.5 | 649.5 | 402.3 | 382 | 511
1003 | 858 | 507.8 | 301.8 | 613.1 | 714.6 | 649.4 | 403.4 | 383.1 | 512.5
1004 | 859 | 506.9 | 299.9 | 615.4 | 715.1 | 654 | 404.3 | 384.1 | 513.9
1005 | 860 | 506 | 299.6 | 617.8 | 714.7 | 664.2 | 405.6 | 385.1 | 515.3
1006 | 861 | 505.1 | 298.5 | 620.3 | 715.4 | 660.9 | 406.8 | 386.1 | 516.6
1007 | 862 | 504.1 | 297.2 | 622.6 | 717.6 | 653.1 | 407.5 | 387 | 517.8
1008 | 863 | 503.1 | 296.8 | 624.8 | 720.5 | 650.4 | 408.2 | 387.9 | 519.1
1009 | 864 | 502.1 | 296.7 | 626.9 | 721.7 | 648.4 | 409.2 | 388.7 | 520.3
1010 | 865 | 500.9 | 297.5 | 629 | 728.1 | 638.3 | 409.9 | 389.6 | 521.6
1011 | 866 | 499.9 | 299.4 | 631.1 | 734.9 | 626.2 | 410.3 | 390.4 | 522.9
1012 | 867 | 499 | 299.7 | 633.3 | 741.7 | 619.7 | 411.2 | 391.2 | 524.2
1013 | 868 | 497.9 | 298.9 | 635.6 | 743.4 | 617.3 | 412.1 | 392.1 | 525.2
1014 | 869 | 496.8 | 299 | 637.5 | 743.7 | 617.7 | 412.8 | 392.9 | 526.1
1015 | 870 | 495.8 | 297.7 | 639.3 | 744.1 | 615.6 | 414.1 | 393.7 | 527
1016 | 871 | 494.5 | 296.4 | 641.1 | 743.2 | 613.9 | 415.1 | 394.5 | 528
1017 | 872 | 493.3 | 294.6 | 642.7 | 742 | 614.1 | 415.9 | 395.3 | 529
1018 | 873 | 492 | 292.8 | 644.1 | 739.1 | 614.7 | 417.6 | 396.1 | 529.9
1019 | 874 | 490.9 | 291.3 | 645.2 | 736.7 | 615.1 | 419.2 | 397 | 530.9
1020 | 875 | 489.9 | 289.9 | 646.2 | 734 | 613.8 | 420.4 | 397.7 | 531.9
1021 | 876 | 488.8 | 288.9 | 647.3 | 731.9 | 616.8 | 421.8 | 398.4 | 532.8
1022 | 877 | 487.7 | 288.2 | 648.3 | 735.4 | 615.8 | 423.2 | 399.2 | 533.8
1023 | 878 | 486.6 | 288.4 | 649.3 | 738.9 | 613 | 424.2 | 399.8 | 534.9
1024 | 879 | 485.6 | 288.4 | 650.3 | 742.2 | 612 | 425.7 | 400.5 | 535.9
1025 | 880 | 484.6 | 288.7 | 651.5 | 742.3 | 611.6 | 427.7 | 401.2 | 536.8
1026 | 881 | 483.5 | 288.6 | 652.5 | 744.4 | 610.8 | 429.3 | 402 | 537.7
1027 | 882 | 482.5 | 288.2 | 653.7 | 746.6 | 608.4 | 430.7 | 402.6 | 538.5
1028 | 883 | 481.6 | 287.9 | 655 | 747.5 | 606.9 | 432.1 | 403.2 | 539.3
1029 | 884 | 480.6 | 286.9 | 656.3 | 748.3 | 605.4 | 433.5 | 403.8 | 540
1030 | 885 | 479.5 | 286.7 | 657.7 | 751.7 | 599.3 | 435.3 | 404.3 | 540.9
1031 | 886 | 478.4 | 286.9 | 659 | 755.3 | 596.4 | 437.4 | 404.9 | 541.8
1032 | 887 | 477.4 | 291.6 | 659.9 | 757.8 | 590.2 | 438.8 | 405.4 | 542.4
1033 | 888 | 476.4 | 297.5 | 660.7 | 757.1 | 585.4 | 441 | 406 | 543
1034 | 889 | 475.3 | 301.6 | 661.6 | 757.6 | 584.9 | 443.7 | 406.5 | 543.8
1035 | 890 | 474.4 | 305.4 | 662.2 | 758 | 588.8 | 445 | 407.1 | 544.3
1036 | 891 | 473.3 | 305.4 | 662.7 | 757.7 | 593.2 | 446.9 | 407.6 | 544.9
1037 | 892 | 472.3 | 302.9 | 663.4 | 757.5 | 598.2 | 448.9 | 408.2 | 545.5
1038 | 893 | 471.5 | 299.9 | 664.3 | 756.9 | 603.9 | 451.3 | 408.8 | 546
1039 | 894 | 470.2 | 297.8 | 665.3 | 757.8 | 605.5 | 453.2 | 409.4 | 546.5
1040 | 895 | 469.1 | 298.4 | 666.1 | 758.7 | 602.6 | 455 | 409.9 | 547
1041 | 896 | 468.1 | 298.2 | 666.8 | 759.6 | 596.3 | 457 | 410.5 | 547.5
1042 | 897 | 467.2 | 297.2 | 667.5 | 761.2 | 594.1 | 458.7 | 411 | 547.9
1043 | 898 | 466.2 | 295.3 | 668.2 | 761.6 | 597.6 | 460.9 | 411.5 | 548.2
1044 | 899 | 465.3 | 292.8 | 668.9 | 761.2 | 602.4 | 462.9 | 412.1 | 548.4
1045 | 900 | 464.2 | 289.5 | 669.7 | 760.9 | 604.1 | 464.6 | 412.6 | 548.7
1046 | 901 | 463.2 | 286.4 | 670.5 | 760.4 | 606.1 | 466.3 | 413.1 | 548.9
1047 | 902 | 462.1 | 283.1 | 671.3 | 759.2 | 606.8 | 467.9 | 413.7 | 549.1
1048 | 903 | 461.1 | 280.9 | 671.9 | 757.3 | 606.9 | 470.3 | 414.2 | 549.3
1049 | 904 | 460 | 278.1 | 672.6 | 754.2 | 608.5 | 473.6 | 414.7 | 549.5
1050 | 905 | 459.1 | 275.3 | 673.4 | 750.7 | 605.1 | 475.8 | 415.2 | 549.7
1051 | 906 | 458.1 | 272.6 | 674.2 | 747.4 | 602.7 | 479.1 | 415.7 | 549.9
1052 | 907 | 457.2 | 271 | 675.1 | 744.3 | 603.1 | 482.4 | 416.3 | 550.2
1053 | 908 | 456.1 | 269.6 | 676.2 | 743.2 | 602.8 | 485.1 | 416.8 | 550.6
1054 | 909 | 455.2 | 268.4 | 677.4 | 744.4 | 600.1 | 487.3 | 417.2 | 551
1055 | 910 | 454.3 | 266.6 | 678.3 | 747.2 | 597.4 | 489 | 417.7 | 551.3
1056 | 911 | 453.5 | 264.9 | 679.2 | 750.7 | 593.5 | 490.4 | 418.3 | 551.4
1057 | 912 | 452.7 | 263.2 | 680.1 | 752.7 | 594.4 | 491.3 | 418.8 | 551.4
1058 | 913 | 451.8 | 261.5 | 680.6 | 753 | 595.3 | 492.1 | 419.3 | 551.2
1059 | 914 | 450.8 | 260.2 | 681 | 752.4 | 594.2 | 492.5 | 419.8 | 551
1060 | 915 | 449.8 | 258.7 | 681.1 | 751.8 | 594.3 | 492.9 | 420.4 | 550.9
1061 | 916 | 448.9 | 257 | 681.3 | 750.2 | 593 | 493 | 420.9 | 550.7
1062 | 917 | 448 | 256.4 | 681.7 | 748.4 | 590.1 | 492.4 | 421.5 | 550.7
1063 | 918 | 447.1 | 254.7 | 682.3 | 747.4 | 586.9 | 492.2 | 422 | 550.7
1064 | 919 | 446.1 | 252.7 | 682.9 | 746.1 | 587.3 | 493.8 | 422.5 | 550.7
1065 | 920 | 445.3 | 250.7 | 683.3 | 744.5 | 586.3 | 495.8 | 423.1 | 550.6
1066 | 921 | 444.4 | 249.7 | 683.6 | 743.2 | 583.2 | 497.1 | 423.6 | 550.4
1067 | 922 | 443.4 | 249.2 | 684 | 742.5 | 581.3 | 498.2 | 424.3 | 550.4
1068 | 923 | 442.4 | 248.8 | 684.6 | 742.4 | 580.8 | 499 | 424.9 | 550.4
1069 | 924 | 441.5 | 247.5 | 685 | 742.8 | 579.9 | 499.9 | 425.5 | 550.2
1070 | 925 | 440.6 | 246.5 | 685.4 | 743.2 | 580.8 | 501 | 426.2 | 550
1071 | 926 | 439.7 | 246.1 | 685.9 | 742.9 | 580.1 | 502.4 | 427 | 549.7
1072 | 927 | 438.8 | 245.4 | 686.1 | 742.7 | 574.1 | 503.7 | 427.8 | 549.5
1073 | 928 | 437.9 | 244.8 | 686.6 | 743.3 | 568.9 | 505 | 428.6 | 549.3
1074 | 929 | 437 | 243.6 | 687 | 744.2 | 568 | 506.6 | 429.5 | 549
1075 | 930 | 436.2 | 242.3 | 687.3 | 744.3 | 570 | 507.8 | 430.5 | 548.7
1076 | 931 | 435.4 | 241.6 | 687.8 | 743.8 | 570.3 | 508.9 | 431.4 | 548.2
1077 | 932 | 434.6 | 241 | 688.7 | 742.9 | 571.4 | 509.7 | 432.5 | 547.8
1078 | 933 | 433.8 | 239.2 | 689.2 | 741.9 | 572.7 | 510.7 | 433.6 | 547.5
1079 | 934 | 432.9 | 238.1 | 689.1 | 740.5 | 573.6 | 511.9 | 434.8 | 547.1
1080 | 935 | 432 | 237.5 | 688.9 | 739 | 574.1 | 512.6 | 436.3 | 546.7
1081 | 936 | 431 | 236.7 | 689 | 737.5 | 574.3 | 513.1 | 437.7 | 546.4
1082 | 937 | 429.9 | 235.2 | 689.2 | 736 | 573.7 | 514.3 | 439.1 | 546
1083 | 938 | 429 | 234.2 | 689.5 | 735 | 573.7 | 515.3 | 440.5 | 545.6
1084 | 939 | 428.1 | 233.2 | 689.8 | 734.2 | 574.2 | 516 | 441.9 | 545.1
1085 | 940 | 427.3 | 232.3 | 689.9 | 734.2 | 573.6 | 516.8 | 443.1 | 544.5
1086 | 941 | 426.5 | 231.8 | 689.8 | 734.3 | 572.8 | 517.4 | 444.3 | 543.9
1087 | 942 | 425.7 | 230.8 | 689.6 | 734.4 | 572.2 | 517.6 | 445.6 | 543.2
1088 | 943 | 424.7 | 230.3 | 689.5 | 734.3 | 570.9 | 517.8 | 446.9 | 542.6
1089 | 944 | 423.7 | 230.8 | 689.1 | 734 | 567.4 | 518.5 | 448.2 | 542.1
1090 | 945 | 422.9 | 230.7 | 688.7 | 733.6 | 564.6 | 519.3 | 449.4 | 541.8
1091 | 946 | 422.1 | 229.7 | 688.3 | 733.2 | 562.4 | 519.8 | 450.6 | 541.4
1092 | 947 | 421.3 | 228.6 | 688 | 733.4 | 557.7 | 520.2 | 451.9 | 540.9
1093 | 948 | 420.5 | 227.5 | 688.1 | 733.2 | 556.2 | 521 | 453 | 540.5
1094 | 949 | 419.7 | 226.3 | 688.4 | 733.6 | 555 | 521.7 | 454.2 | 540.1
1095 | 950 | 419 | 226.8 | 689.1 | 733.5 | 553.3 | 522.7 | 455.4 | 539.6
1096 | 951 | 418.2 | 226.8 | 689.7 | 733.1 | 552.5 | 523.6 | 456.4 | 539.1
1097 | 952 | 417.4 | 226.9 | 690 | 732.5 | 551.5 | 524.1 | 457.4 | 538.6
1098 | 953 | 416.4 | 227.2 | 690.1 | 732.6 | 550.4 | 524.9 | 458.4 | 538.1
1099 | 954 | 415.5 | 227.2 | 690.2 | 733.3 | 549.3 | 525.8 | 459.3 | 537.6
1100 | 955 | 414.8 | 227 | 690.4 | 733 | 549.3 | 526.6 | 460.2 | 537.2
1101 | 956 | 414.1 | 227.2 | 690.7 | 732.8 | 550.1 | 527.2 | 461 | 536.7
1102 | 957 | 413.3 | 227.5 | 691.1 | 732.9 | 550.4 | 527.8 | 461.7 | 536.3
1103 | 958 | 412.3 | 227.4 | 692.2 | 734 | 549.8 | 528.8 | 462.5 | 535.9
1104 | 959 | 411.5 | 227.5 | 693 | 734.6 | 549.7 | 529.7 | 463.1 | 535.5
1105 | 960 | 410.8 | 227.9 | 694.4 | 734.5 | 549.2 | 531.1 | 463.8 | 535.2
1106 | 961 | 410 | 228 | 695.1 | 733.7 | 548.5 | 533 | 464.5 | 535
1107 | 962 | 409.1 | 228.4 | 695.5 | 733.4 | 547.2 | 534.8 | 465.2 | 534.6
1108 | 963 | 408.3 | 228.7 | 696.1 | 733.4 | 548.3 | 537.2 | 465.9 | 534.2
1109 | 964 | 407.6 | 228.5 | 696.5 | 732.3 | 549 | 539.3 | 466.5 | 533.8
1110 | 965 | 406.9 | 228 | 697.1 | 731.4 | 549.8 | 541.2 | 467 | 533.4
1111 | 966 | 406.1 | 227.4 | 697.7 | 730.1 | 548.1 | 543.3 | 467.6 | 533.1
1112 | 967 | 405.2 | 226.7 | 698.7 | 729.2 | 548 | 545.2 | 467.9 | 532.7
1113 | 968 | 404.3 | 225.5 | 699.3 | 728.6 | 548.4 | 546.9 | 468.5 | 532.4
1114 | 969 | 403.5 | 224.7 | 699.6 | 727.3 | 548.7 | 548.9 | 469 | 532.1
1115 | 970 | 402.7 | 224.3 | 700 | 726.4 | 548.7 | 551.2 | 469.6 | 531.7
1116 | 971 | 402 | 224.1 | 700.8 | 726.4 | 549 | 553.3 | 470.2 | 531.3
1117 | 972 | 401.2 | 224.2 | 701.3 | 726.4 | 548.4 | 555.7 | 470.7 | 530.8
1118 | 973 | 400.5 | 223.5 | 701.4 | 725.5 | 548.3 | 557.8 | 471.3 | 530.4
1119 | 974 | 399.8 | 222.9 | 701.1 | 723.9 | 548.5 | 560.1 | 471.8 | 530
1120 | 975 | 399.1 | 223.2 | 702.6 | 723.5 | 545.4 | 563.3 | 472.2 | 529.6
1121 | 976 | 398.6 | 230.9 | 703.5 | 723.3 | 545.2 | 567 | 472.7 | 529.2
1122 | 977 | 397.9 | 238.1 | 703.9 | 722.8 | 545.8 | 571.1 | 473.1 | 528.9
1123 | 978 | 397.1 | 234.3 | 705.2 | 721.8 | 544.5 | 575.9 | 473.6 | 528.5
1124 | 979 | 396.5 | 232.6 | 709 | 720.4 | 542.4 | 580.7 | 473.9 | 528.2
1125 | 980 | 395.6 | 235 | 713.5 | 719 | 539.6 | 586 | 474.2 | 528
1126 | 981 | 394.9 | 235.8 | 715.9 | 717.6 | 537.4 | 591.5 | 474.6 | 527.7
1127 | 982 | 394.1 | 233.9 | 716.2 | 716.1 | 535.9 | 595.7 | 475.1 | 527.5
1128 | 983 | 393.4 | 230.6 | 715.8 | 714.4 | 533.4 | 599.6 | 475.7 | 527.3
1129 | 984 | 392.9 | 227.9 | 715.5 | 712.6 | 530.6 | 603 | 476.1 | 527.1
1130 | 985 | 392.4 | 225.8 | 716.1 | 711 | 529.2 | 606 | 476.5 | 526.7
1131 | 986 | 391.8 | 224.6 | 714.2 | 709.4 | 529.3 | 609.1 | 476.9 | 526.5
1132 | 987 | 391.1 | 223.6 | 712.4 | 707.6 | 532 | 612.1 | 477.2 | 526.4
1133 | 988 | 390.2 | 222.9 | 710.3 | 706 | 531.1 | 614.7 | 477.6 | 526.2
1134 | 989 | 389.5 | 222.2 | 707.9 | 704.3 | 531 | 616.9 | 478 | 525.9
1135 | 990 | 388.9 | 222.1 | 706.1 | 702.1 | 532 | 619.1 | 478.5 | 525.5
1136 | 991 | 388.3 | 221.8 | 705.1 | 700.5 | 532.8 | 621.5 | 478.9 | 525.3
1137 | 992 | 387.6 | 220.3 | 703.9 | 697.7 | 532.3 | 624.1 | 479.3 | 524.9
1138 | 993 | 386.8 | 219.5 | 702.9 | 695.7 | 530.7 | 626.1 | 479.7 | 524.7
1139 | 994 | 385.9 | 218.3 | 702.7 | 694.4 | 530.1 | 627.9 | 480.2 | 524.5
1140 | 995 | 385.1 | 218 | 701.8 | 694 | 528.9 | 629.3 | 480.7 | 524.3
1141 | 996 | 384.2 | 218 | 700 | 692.3 | 526.7 | 630.5 | 481.2 | 523.9
1142 | 997 | 383.3 | 219 | 698.3 | 690 | 523.6 | 631.3 | 481.8 | 523.6
1143 | 998 | 382.7 | 218.5 | 696.5 | 687.3 | 523.9 | 632.2 | 482.4 | 523.4
1144 | 999 | 382.1 | 217.4 | 694.8 | 684.5 | 525.3 | 633.8 | 483.2 | 522.9
1145 | 1000 | 381.2 | 216.1 | 694.1 | 682.7 | 525.1 | 635.1 | 483.6 | 522.4
1146 | 1001 | 380.6 | 215.1 | 692.9 | 681 | 526.9 | 636.9 | 484 | 522.1
1147 | 1002 | 379.9 | 215 | 691.7 | 679.8 | 527 | 638.7 | 484.4 | 521.5
1148 | 1003 | 379.2 | 214.4 | 690.7 | 678.2 | 526.9 | 639.8 | 484.8 | 521
1149 | 1004 | 378.5 | 213.3 | 690.4 | 676.6 | 527.4 | 640.6 | 485.1 | 520.6
1150 | 1005 | 377.8 | 212.4 | 690.7 | 675.8 | 526 | 641.9 | 484.9 | 520.4
1151 | 1006 | 377.2 | 211.4 | 689.9 | 675.3 | 524.6 | 643.4 | 485.6 | 520.2
1152 | 1007 | 376.5 | 210.6 | 688.8 | 674.7 | 524.2 | 644.6 | 486.3 | 519.9
1153 | 1008 | 375.9 | 209 | 687.5 | 673.9 | 523.7 | 646.6 | 486.9 | 519.6
1154 | 1009 | 375.2 | 207.9 | 685.2 | 671.6 | 523.8 | 649 | 487.5 | 519.3
1155 | 1010 | 374.5 | 206.7 | 682.7 | 668.6 | 524.3 | 650.8 | 488.1 | 518.9
1156 | 1011 | 373.8 | 205.5 | 680.3 | 665.2 | 523.9 | 652.5 | 488.6 | 518.5
1157 | 1012 | 373.1 | 204.8 | 678.7 | 662.1 | 523.3 | 653.4 | 489.1 | 518.2
1158 | 1013 | 372.3 | 205.7 | 677.7 | 661 | 523.5 | 653.5 | 489.6 | 517.9
1159 | 1014 | 371.6 | 207.1 | 677.7 | 659.8 | 523.5 | 653.2 | 489.9 | 517.5
1160 | 1015 | 370.9 | 206.9 | 675.5 | 658.3 | 524.5 | 652.5 | 490.2 | 517.2
1161 | 1016 | 370.1 | 206.5 | 674.6 | 657.5 | 525.8 | 651.8 | 490.5 | 516.8
1162 | 1017 | 369.3 | 205.8 | 675.2 | 657.8 | 527.1 | 651.5 | 490.1 | 516.4
1163 | 1018 | 368.6 | 205.2 | 674.9 | 659 | 525.4 | 651.3 | 489.1 | 516.1
1164 | 1019 | 368 | 204.1 | 673.3 | 659.2 | 523 | 650.9 | 488.2 | 515.8
1165 | 1020 | 367.4 | 203.6 | 671.2 | 658.9 | 522.1 | 650.5 | 487.5 | 515.6
1166 | 1021 | 366.7 | 204.3 | 669.3 | 658.8 | 522.4 | 650.4 | 486.9 | 515.2
1167 | 1022 | 366 | 204.6 | 668.9 | 658.6 | 523.6 | 650.1 | 486.4 | 514.8
1168 | 1023 | 365.2 | 203.4 | 668.1 | 659.2 | 521.7 | 649 | 486 | 514.4
1169 | 1024 | 364.5 | 202.8 | 668 | 659.5 | 519.3 | 648.2 | 485.6 | 514
1170 | 1025 | 363.7 | 201.9 | 667.2 | 659.2 | 519.4 | 647.4 | 485.5 | 513.6
1171 | 1026 | 362.9 | 201 | 665.1 | 658.3 | 518 | 647 | 485.4 | 513.2
1172 | 1027 | 362.2 | 200 | 662.9 | 656.6 | 517.4 | 646.3 | 485.4 | 512.7
1173 | 1028 | 361.6 | 198.2 | 660.5 | 654 | 518.1 | 645.6 | 485.5 | 512.3
1174 | 1029 | 361.1 | 196.5 | 658.6 | 652.4 | 517 | 645.1 | 485.6 | 511.8
1175 | 1030 | 360.4 | 195.1 | 657.3 | 651.7 | 514.7 | 644.6 | 485.5 | 511.4
1176 | 1031 | 359.8 | 193.7 | 655.6 | 650.7 | 513.6 | 644.2 | 485.5 | 511.1
1177 | 1032 | 359.2 | 192.3 | 653.7 | 649.5 | 511.6 | 643.5 | 485.5 | 510.8
1178 | 1033 | 358.6 | 191.3 | 651.9 | 647.6 | 510.1 | 642.3 | 485.4 | 510.3
1179 | 1034 | 358 | 190.3 | 650.2 | 646.3 | 509.5 | 641.3 | 485.5 | 509.8
1180 | 1035 | 357.3 | 189.8 | 648.4 | 644.4 | 510 | 640.4 | 485.4 | 509.5
1181 | 1036 | 356.5 | 190.2 | 646.4 | 642.1 | 508.4 | 639.3 | 485.3 | 509.1
1182 | 1037 | 355.9 | 191.3 | 644.1 | 638.9 | 505.1 | 638.1 | 485.2 | 508.7
1183 | 1038 | 355.3 | 191.1 | 641.9 | 636.3 | 503.9 | 637.5 | 485.1 | 508.4
1184 | 1039 | 354.7 | 190.3 | 639.8 | 634 | 505.2 | 636.9 | 485.1 | 508
1185 | 1040 | 354.1 | 189.9 | 637.9 | 632.5 | 504.7 | 635.9 | 485 | 507.5
1186 | 1041 | 353.6 | 189 | 636.1 | 631 | 505.3 | 634.9 | 484.9 | 507.1
1187 | 1042 | 352.8 | 187.9 | 634.4 | 629.3 | 504.4 | 634.3 | 484.8 | 506.8
1188 | 1043 | 352 | 188.7 | 630.3 | 628.3 | 505.8 | 634.5 | 484.5 | 506.4
1189 | 1044 | 351 | 190 | 625.1 | 627.2 | 507.8 | 634.9 | 484.2 | 505.9
1190 | 1045 | 350.8 | 186 | 629.8 | 622.4 | 501.5 | 631.7 | 484.6 | 505.7
1191 | 1046 | 350 | 187.6 | 624.8 | 622 | 502 | 632.1 | 484.4 | 504.9
1192 | 1047 | 349.5 | 187.4 | 624.3 | 620 | 497.5 | 630.9 | 484.5 | 504.3
1193 | 1048 | 349 | 186.9 | 625.5 | 617 | 492.1 | 629 | 484.7 | 503.9
1194 | 1049 | 348.5 | 186.4 | 624 | 615.8 | 490.2 | 627.9 | 484.7 | 503.3
1195 | 1050 | 348.1 | 185.7 | 622.4 | 615.6 | 489.9 | 626.9 | 484.7 | 502.8
1196 | 1051 | 347.6 | 184.5 | 621.1 | 614.5 | 490.2 | 624.4 | 484.7 | 502.2
1197 | 1052 | 346.9 | 182.7 | 619.7 | 612.8 | 490.4 | 622.1 | 484.8 | 501.6
1198 | 1053 | 346.2 | 181.1 | 617.8 | 612.1 | 490.3 | 620.8 | 484.8 | 500.9
1199 | 1054 | 345.5 | 179.9 | 615.4 | 612.3 | 487.3 | 619.4 | 484.9 | 500.3
1200 | 1055 | 344.9 | 178.8 | 614.2 | 612.5 | 482.9 | 618.5 | 484.9 | 500
1201 | 1056 | 344.2 | 178 | 613 | 612.1 | 478.7 | 618 | 485 | 499.7
1202 | 1057 | 343.5 | 178.9 | 610.7 | 612 | 475.7 | 617.9 | 485 | 499.3
1203 | 1058 | 342.8 | 177.7 | 608.8 | 611.8 | 473.4 | 618 | 485 | 499
1204 | 1059 | 342.1 | 176.6 | 607.6 | 611.5 | 470.8 | 618.1 | 485 | 498.6
1205 | 1060 | 341.5 | 175.7 | 606.1 | 610.9 | 467.7 | 618.6 | 485 | 498.3
1206 | 1061 | 341 | 174.5 | 604.7 | 610.4 | 465.8 | 618.9 | 485.1 | 497.9
1207 | 1062 | 340.5 | 173.8 | 603.1 | 608.7 | 465.6 | 619.5 | 485.2 | 497.6
1208 | 1063 | 339.8 | 173.7 | 601.3 | 607.2 | 466.9 | 620 | 485.4 | 497.2
1209 | 1064 | 339.4 | 173.2 | 599.2 | 606 | 467.9 | 620 | 485.6 | 496.6
1210 | 1065 | 338.8 | 172.8 | 597.2 | 605.2 | 468.6 | 620 | 485.8 | 496
1211 | 1066 | 338 | 173.9 | 592.1 | 605.5 | 467.3 | 620.9 | 485.8 | 495.4
1212 | 1067 | 337.5 | 172.1 | 592.1 | 603.5 | 460.9 | 620.2 | 486 | 495.1
1213 | 1068 | 337 | 173.5 | 588.8 | 602.8 | 456.8 | 620.8 | 486.2 | 494.6
1214 | 1069 | 336.4 | 174 | 586 | 602.5 | 453.3 | 621.9 | 486.4 | 494.1
1215 | 1070 | 335.8 | 173.9 | 583 | 601.6 | 450.1 | 622.6 | 486.5 | 493.7
1216 | 1071 | 335.2 | 175.2 | 580.1 | 600.4 | 447.8 | 623.5 | 486.5 | 493.4
1217 | 1072 | 334.6 | 177.9 | 577.3 | 599.8 | 447.3 | 624.1 | 486.5 | 492.9
1218 | 1073 | 333.9 | 179.7 | 574 | 599.4 | 445.9 | 624.9 | 486.3 | 492.2
1219 | 1074 | 333.3 | 180.4 | 571.5 | 599 | 445.4 | 625.9 | 486 | 491.7
1220 | 1075 | 332.8 | 181.3 | 568.5 | 598.2 | 444 | 623.9 | 485.6 | 491.2
1221 | 1076 | 332.4 | 181.2 | 566.5 | 596.7 | 441.5 | 612.5 | 485.4 | 490.6
1222 | 1077 | 331.8 | 181.6 | 563.4 | 595 | 438.9 | 605.2 | 485 | 490.1
1223 | 1078 | 331.2 | 181.2 | 560.9 | 593.7 | 438.2 | 598.4 | 484.7 | 489.5
1224 | 1079 | 330.6 | 179.6 | 559.9 | 592.4 | 436 | 590.7 | 484.4 | 489.1
1225 | 1080 | 330 | 177.6 | 559.9 | 591.2 | 433.8 | 585.7 | 484 | 488.6
1226 | 1081 | 329.5 | 175.4 | 560 | 589.8 | 432.2 | 581.5 | 483.7 | 488.3
1227 | 1082 | 328.9 | 173.4 | 560.1 | 588 | 430.7 | 576.8 | 483.3 | 487.9
1228 | 1083 | 328.4 | 172 | 560.3 | 585.9 | 429 | 572.2 | 482.8 | 487.3
1229 | 1084 | 327.9 | 170.4 | 560.2 | 583.4 | 428.5 | 566.7 | 482.4 | 486.7
1230 | 1085 | 327.4 | 169.3 | 559.5 | 581 | 426 | 563.9 | 482 | 486.2
1231 | 1086 | 326.7 | 168.6 | 558.8 | 578.9 | 423.5 | 563.5 | 481.5 | 485.7
1232 | 1087 | 326.2 | 167.9 | 557.6 | 576.5 | 423.6 | 562.7 | 481.1 | 485.1
1233 | 1088 | 325.7 | 167.1 | 556.1 | 574.1 | 421.7 | 562.1 | 480.6 | 484.5
1234 | 1089 | 325.2 | 166.6 | 553.5 | 572.1 | 420.8 | 560 | 480.1 | 483.8
1235 | 1090 | 324.7 | 166.7 | 550.9 | 571.3 | 420.3 | 558 | 479.6 | 483
1236 | 1091 | 324.1 | 168.6 | 547.8 | 571 | 419.7 | 555.8 | 479 | 482.4
1237 | 1092 | 323.5 | 170.4 | 545.5 | 571 | 420.5 | 555.5 | 478.4 | 481.8
1238 | 1093 | 322.9 | 171.6 | 542.3 | 570.6 | 419.2 | 555.1 | 477.8 | 481.1
1239 | 1094 | 322.4 | 170.5 | 540.3 | 569.8 | 416.6 | 554.1 | 477.4 | 480.7
1240 | 1095 | 321.9 | 168.3 | 540.3 | 568.2 | 414.1 | 552.4 | 477.1 | 480.3
1241 | 1096 | 321.4 | 166.5 | 540.7 | 565.5 | 412.8 | 551.9 | 476.7 | 479.7
1242 | 1097 | 320.8 | 164.8 | 540.4 | 563 | 412.6 | 550.9 | 476.4 | 479.1
1243 | 1098 | 320.2 | 163.7 | 539.3 | 561.4 | 411.4 | 547.6 | 476 | 478.5
1244 | 1099 | 319.8 | 162.8 | 538 | 559.9 | 409.4 | 545.3 | 475.6 | 477.9
1245 | 1100 | 319.3 | 161.9 | 537.4 | 558.4 | 408 | 543.2 | 475.1 | 477.4
1246 | 1101 | 318.7 | 161.5 | 536.4 | 556.6 | 406.3 | 539.9 | 474.6 | 476.8
1247 | 1102 | 318.2 | 160.6 | 535.6 | 554.7 | 403.9 | 537.4 | 474.1 | 476.2
1248 | 1103 | 317.6 | 159.8 | 534.6 | 553.5 | 395.5 | 536.7 | 473.5 | 475.6
1249 | 1104 | 317.1 | 158.9 | 534.3 | 552.6 | 379.1 | 534.5 | 473 | 474.9
1250 | 1105 | 316.6 | 158 | 534.1 | 551.6 | 366 | 532.9 | 472.5 | 474.3
1251 | 1106 | 316 | 157.2 | 533.5 | 550.4 | 352.6 | 532.3 | 471.9 | 473.6
1252 | 1107 | 315.4 | 156.7 | 532.2 | 548.9 | 340 | 531.6 | 471.4 | 472.8
1253 | 1108 | 315 | 155.7 | 530.9 | 547.8 | 328.5 | 530.3 | 470.8 | 472.2
1254 | 1109 | 314.4 | 154.8 | 530.1 | 546.1 | 318.2 | 527.4 | 470.2 | 471.5
1255 | 1110 | 313.9 | 154 | 529.3 | 543.9 | 308.6 | 524.1 | 469.4 | 470.7
1256 | 1111 | 313.2 | 153.7 | 528.9 | 540 | 300.6 | 520.9 | 468.8 | 469.9
1257 | 1112 | 312.7 | 154.4 | 528.4 | 536.7 | 292.4 | 519.2 | 468.2 | 469.2
1258 | 1113 | 312.2 | 154.8 | 527.9 | 533.6 | 284.1 | 510.8 | 467.5 | 468.5
1259 | 1114 | 311.8 | 154.6 | 527.4 | 530.2 | 276.2 | 504.7 | 466.9 | 467.7
1260 | 1115 | 311.5 | 155 | 526.5 | 526.4 | 268.9 | 500.6 | 466.3 | 467.1
1261 | 1116 | 311.1 | 155.4 | 525.8 | 522.3 | 262.5 | 498.1 | 465.7 | 466.4
1262 | 1117 | 310.6 | 154.7 | 525.1 | 518.8 | 257.4 | 494.7 | 465.2 | 465.8
1263 | 1118 | 310.2 | 153.5 | 524.2 | 515.4 | 252.9 | 491.9 | 464.6 | 465
1264 | 1119 | 309.6 | 153 | 523.4 | 513.2 | 251 | 490.7 | 464.1 | 464.4
1265 | 1120 | 309.1 | 151.9 | 522.4 | 512.1 | 249.4 | 489.6 | 463.6 | 463.7
1266 | 1121 | 308.6 | 151.3 | 520.9 | 511.4 | 246.8 | 487.4 | 463.2 | 463.2
1267 | 1122 | 308.1 | 150.7 | 518.3 | 511.1 | 243.5 | 487.1 | 462.8 | 462.8
1268 | 1123 | 307.5 | 150.4 | 515.8 | 511.2 | 240.6 | 485.9 | 462.3 | 462.2
1269 | 1124 | 307 | 150.6 | 513 | 511.4 | 237.7 | 484.5 | 461.7 | 461.7
1270 | 1125 | 306.6 | 151.4 | 510 | 511.5 | 237.1 | 482.4 | 461.2 | 461.1
1271 | 1126 | 306 | 151.4 | 507.3 | 510.4 | 235 | 480 | 460.6 | 460.6
1272 | 1127 | 305.4 | 151.5 | 504.8 | 509.2 | 233.1 | 476.7 | 460 | 460.1
1273 | 1128 | 304.8 | 151.1 | 503.4 | 508.4 | 232.2 | 474.7 | 459.3 | 459.6
1274 | 1129 | 304.3 | 149.5 | 502.5 | 506.7 | 230.6 | 471.2 | 458.7 | 459
1275 | 1130 | 303.8 | 148.2 | 501.4 | 505 | 228.8 | 467.9 | 458 | 458.3
1276 | 1131 | 303.2 | 147.7 | 500.6 | 503.6 | 226.9 | 464.7 | 457.4 | 457.5
1277 | 1132 | 302.6 | 147.3 | 500 | 501.9 | 225.6 | 461.5 | 456.9 | 456.8
1278 | 1133 | 301.9 | 146.5 | 499.3 | 500.4 | 224.7 | 457.4 | 456.3 | 456.1
1279 | 1134 | 301.4 | 145.9 | 498.5 | 499.5 | 223.8 | 455.2 | 455.7 | 455.4
1280 | 1135 | 300.7 | 146.2 | 497.6 | 498 | 221.2 | 453.6 | 455.1 | 454.8
1281 | 1136 | 300.3 | 145.6 | 496.8 | 495.6 | 219.6 | 452 | 454.4 | 454.2
1282 | 1137 | 299.8 | 144.8 | 495.9 | 492.9 | 218.1 | 448.6 | 453.7 | 453.4
1283 | 1138 | 299.4 | 144.2 | 494.7 | 489 | 216.2 | 445 | 453.1 | 452.7
1284 | 1139 | 299 | 143.5 | 493.4 | 485.1 | 214.8 | 441.5 | 452.4 | 452
1285 | 1140 | 298.5 | 143 | 491.7 | 481.6 | 212.8 | 438.8 | 451.7 | 451.3
1286 | 1141 | 298 | 143.1 | 490 | 477.8 | 210.6 | 436.5 | 451 | 450.6
1287 | 1142 | 297.6 | 142.9 | 488 | 474.6 | 209.1 | 433.9 | 450.3 | 449.8
1288 | 1143 | 297 | 142.9 | 486.1 | 471.6 | 207.3 | 430.2 | 449.6 | 449.1
1289 | 1144 | 296.5 | 144 | 484.2 | 468.7 | 205.1 | 427.6 | 448.8 | 448.3
1290 | 1145 | 296 | 146.4 | 482.2 | 465.9 | 202.8 | 424.3 | 448.1 | 447.6
1291 | 1146 | 295.6 | 148.8 | 479.9 | 463.2 | 200.8 | 421 | 447.4 | 447
1292 | 1147 | 295.3 | 150.6 | 478.2 | 460.4 | 199 | 418.7 | 446.7 | 446.3
1293 | 1148 | 295 | 150.9 | 476 | 457.6 | 197.4 | 415.1 | 445.9 | 445.6
1294 | 1149 | 294.6 | 151.7 | 472.5 | 454.7 | 195.7 | 413 | 445.1 | 444.9
1295 | 1150 | 294.2 | 151.8 | 470.6 | 452.1 | 194.1 | 409.8 | 444.5 | 444.2
1296 | 1151 | 293.7 | 153.6 | 466.4 | 449.7 | 192.7 | 408.1 | 443.8 | 443.4
1297 | 1152 | 293.3 | 155.1 | 457.4 | 446.6 | 191.5 | 405.1 | 443.2 | 442.7
1298 | 1153 | 293 | 155.9 | 446.1 | 443.5 | 190.2 | 402 | 442.5 | 442
1299 | 1154 | 292.6 | 155.4 | 435 | 440.9 | 189.7 | 400 | 441.9 | 441.3
1300 | 1155 | 292.1 | 154.5 | 424.9 | 438.6 | 188.8 | 396.7 | 441.1 | 440.6
1301 | 1156 | 291.6 | 154.1 | 416 | 436 | 187.7 | 393.3 | 440.4 | 439.9
1302 | 1157 | 291.1 | 153.7 | 406.4 | 433.3 | 186.8 | 390.4 | 439.6 | 439.2
1303 | 1158 | 290.6 | 152.7 | 396.8 | 431.1 | 186.1 | 386 | 438.8 | 438.5
1304 | 1159 | 290 | 151.1 | 388.1 | 428.7 | 185.4 | 383 | 438 | 437.8
1305 | 1160 | 289.5 | 150.2 | 380.4 | 426 | 184.3 | 378.5 | 437.2 | 437.1
1306 | 1161 | 289.2 | 150 | 373.3 | 422.9 | 183.3 | 373.2 | 436.3 | 436.4
1307 | 1162 | 288.7 | 148.7 | 366.8 | 419.6 | 182.5 | 369.4 | 435.5 | 435.6
1308 | 1163 | 288.2 | 147.6 | 362.1 | 416.5 | 181.8 | 365.8 | 434.6 | 434.8
1309 | 1164 | 287.7 | 147.2 | 357 | 414 | 181 | 363.6 | 433.7 | 434.1
1310 | 1165 | 287.3 | 146.2 | 352 | 411.6 | 180.4 | 359.8 | 432.8 | 433.6
1311 | 1166 | 286.7 | 146.8 | 347.5 | 409.6 | 179.3 | 356.5 | 431.9 | 432.8
1312 | 1167 | 286.3 | 148.3 | 343.6 | 407.5 | 177.7 | 353.2 | 431.1 | 432.1
1313 | 1168 | 285.8 | 147.3 | 340 | 405.4 | 176.8 | 350.8 | 430.3 | 431.5
1314 | 1169 | 285.3 | 146.4 | 336.8 | 403.7 | 176.4 | 347.9 | 429.5 | 430.8
1315 | 1170 | 285 | 145.8 | 334.7 | 401.8 | 174.8 | 344.6 | 428.8 | 430.1
1316 | 1171 | 284.7 | 145.6 | 332.6 | 400.4 | 173.9 | 342.5 | 428 | 429.3
1317 | 1172 | 284.2 | 145.7 | 330.1 | 397.9 | 173.3 | 339.9 | 427.1 | 428.5
1318 | 1173 | 283.6 | 145.9 | 328 | 393.9 | 172.6 | 337.3 | 426.3 | 427.8
1319 | 1174 | 283.1 | 146.1 | 324.8 | 389.6 | 171.7 | 334.8 | 425.4 | 427.1
1320 | 1175 | 282.7 | 144 | 322.9 | 385 | 171 | 332.8 | 424.6 | 426.3
1321 | 1176 | 282.2 | 142.1 | 321 | 380.9 | 170.5 | 331.1 | 423.7 | 425.6
1322 | 1177 | 281.8 | 140.1 | 319.9 | 376.2 | 170 | 328.4 | 422.8 | 424.9
1323 | 1178 | 281.4 | 138.6 | 319.2 | 371.6 | 169.7 | 327.3 | 422 | 424.3
1324 | 1179 | 280.8 | 137.9 | 317.4 | 367.5 | 169 | 327.6 | 421.1 | 423.7
1325 | 1180 | 280.4 | 136.6 | 316 | 363.8 | 168.6 | 327.4 | 420.3 | 423
1326 | 1181 | 280 | 135.4 | 313.5 | 360 | 167.7 | 325 | 419.4 | 422.2
1327 | 1182 | 279.6 | 134.1 | 311.7 | 356.3 | 167.2 | 321.8 | 418.6 | 421.5
1328 | 1183 | 279.2 | 133.3 | 310.4 | 353.1 | 166 | 321.1 | 417.9 | 420.6
1329 | 1184 | 278.8 | 132.1 | 308.6 | 349.4 | 165.4 | 318.4 | 417 | 419.8
1330 | 1185 | 278.4 | 131.6 | 307 | 345.2 | 164.4 | 316.8 | 416.2 | 419.1
1331 | 1186 | 278 | 130.7 | 304.9 | 342.4 | 163.9 | 315.9 | 415.4 | 418.3
1332 | 1187 | 277.6 | 129.1 | 304.2 | 338.9 | 165.4 | 314.5 | 414.5 | 417.5
1333 | 1188 | 277.2 | 128 | 304.6 | 335.6 | 166.5 | 314.4 | 413.7 | 416.9
1334 | 1189 | 276.7 | 127.1 | 305.3 | 332.7 | 166.7 | 314 | 412.8 | 416.2
1335 | 1190 | 276.2 | 126.3 | 305.7 | 329.8 | 165.2 | 312.8 | 412 | 415.5
1336 | 1191 | 275.8 | 125.4 | 305.7 | 327.3 | 163.9 | 310 | 411.1 | 414.8
1337 | 1192 | 275.4 | 124.8 | 305.3 | 325 | 163.1 | 309.5 | 410.2 | 414.1
1338 | 1193 | 275 | 124.2 | 303.7 | 322.9 | 162.1 | 307.3 | 409.4 | 413.4
1339 | 1194 | 274.6 | 123.4 | 301.6 | 321.1 | 161 | 306.9 | 408.5 | 412.6
1340 | 1195 | 274 | 122.6 | 300.9 | 319.2 | 159.7 | 307.3 | 407.6 | 411.8
1341 | 1196 | 273.4 | 121.9 | 299.3 | 317.6 | 159 | 305.3 | 406.7 | 411
1342 | 1197 | 272.9 | 121.4 | 297.8 | 316.1 | 158.3 | 305.3 | 405.8 | 410.2
1343 | 1198 | 272.4 | 120.4 | 296.6 | 314.3 | 157.1 | 304.3 | 405 | 409.4
1344 | 1199 | 271.9 | 119.6 | 296.2 | 313.2 | 156.6 | 303.5 | 404.1 | 408.7
1345 | 1200 | 271.4 | 118.9 | 295.4 | 311.7 | 155.6 | 302.4 | 403.2 | 407.9
1346 | 1201 | 271 | 118.8 | 295.3 | 309.5 | 154.3 | 302.1 | 402.4 | 407.1
1347 | 1202 | 270.6 | 118.6 | 293.8 | 307.7 | 153.6 | 300.3 | 401.5 | 406.4
1348 | 1203 | 270.1 | 118.3 | 292.9 | 306.1 | 153.2 | 299 | 400.6 | 405.7
1349 | 1204 | 269.7 | 118.2 | 292.9 | 304.4 | 153.1 | 298.4 | 399.8 | 405
1350 | 1205 | 269.2 | 117.9 | 293.4 | 302.5 | 152.3 | 297.4 | 398.9 | 404.3
1351 | 1206 | 268.9 | 117.2 | 293.6 | 300.6 | 151.1 | 294.9 | 398 | 403.6
1352 | 1207 | 268.5 | 117.6 | 293.6 | 298.9 | 150.6 | 293.9 | 397.2 | 402.8
1353 | 1208 | 268.1 | 117.9 | 293.5 | 297.5 | 152.5 | 294.3 | 396.3 | 402.1
1354 | 1209 | 267.8 | 118.5 | 293.7 | 296 | 154.7 | 292.3 | 395.4 | 401.3
1355 | 1210 | 267.4 | 119.1 | 293.7 | 294.7 | 157.4 | 290.5 | 394.6 | 400.6
1356 | 1211 | 267 | 120.1 | 293.1 | 293.4 | 158.6 | 289 | 393.7 | 399.8
1357 | 1212 | 266.7 | 120.7 | 292.8 | 292.1 | 162.1 | 287.7 | 392.8 | 399.1
1358 | 1213 | 266.3 | 120.5 | 292.5 | 290.6 | 166.3 | 286.4 | 391.9 | 398.3
1359 | 1214 | 265.9 | 120.4 | 292 | 289.9 | 168 | 285.4 | 390.9 | 397.5
1360 | 1215 | 265.5 | 120.2 | 291.4 | 288.5 | 167.9 | 284.5 | 390 | 396.7
1361 | 1216 | 265.1 | 119.9 | 291.2 | 287.2 | 168.5 | 283.2 | 389.1 | 396
1362 | 1217 | 264.6 | 119.2 | 290 | 285.7 | 168.8 | 281.5 | 388.2 | 395.3
1363 | 1218 | 264.2 | 118.8 | 289 | 284.5 | 168.1 | 279.5 | 387.2 | 394.5
1364 | 1219 | 263.8 | 118.6 | 287.9 | 283.3 | 166.6 | 277.9 | 386.3 | 393.9
1365 | 1220 | 263.4 | 117.8 | 286.5 | 281.9 | 165.5 | 278.3 | 385.3 | 393.2
1366 | 1221 | 262.9 | 117 | 284.6 | 280.7 | 163.7 | 278 | 384.4 | 392.6
1367 | 1222 | 262.4 | 116.3 | 283.1 | 279.7 | 161.4 | 276.3 | 383.5 | 391.9
1368 | 1223 | 262.1 | 115.2 | 282.6 | 278.4 | 159.4 | 275.2 | 382.5 | 391.1
1369 | 1224 | 261.7 | 114.6 | 282.3 | 277.1 | 157.6 | 273.8 | 381.5 | 390.3
1370 | 1225 | 261.4 | 114 | 281.7 | 275.6 | 155.4 | 271.2 | 380.6 | 389.6
1371 | 1226 | 261 | 113 | 280.4 | 274.2 | 154 | 269.2 | 379.7 | 388.9
1372 | 1227 | 260.6 | 112.1 | 278.2 | 273.4 | 152.5 | 267.1 | 378.7 | 388.2
1373 | 1228 | 260.2 | 111.7 | 275.7 | 272.7 | 151.2 | 266 | 377.8 | 387.4
1374 | 1229 | 259.7 | 111.8 | 273.5 | 271.3 | 149.9 | 264.9 | 376.8 | 386.7
1375 | 1230 | 259.3 | 111.3 | 272.1 | 269.4 | 148.3 | 263.3 | 375.9 | 386
1376 | 1231 | 258.9 | 110.7 | 271.1 | 267.8 | 146.5 | 262 | 375 | 385.2
1377 | 1232 | 258.4 | 110.4 | 269.1 | 266.3 | 144.9 | 260.5 | 374 | 384.4
1378 | 1233 | 258 | 110.1 | 267.3 | 264.6 | 143.9 | 259.7 | 373.1 | 383.7
1379 | 1234 | 257.7 | 109.9 | 265.1 | 263.4 | 143.1 | 259.1 | 372.2 | 383
1380 | 1235 | 257.3 | 109.7 | 263.1 | 262.1 | 142 | 258.3 | 371.3 | 382.3
1381 | 1236 | 256.9 | 109.3 | 261.2 | 260.8 | 141.1 | 256.7 | 370.4 | 381.5
1382 | 1237 | 256.5 | 109 | 259 | 259.5 | 140.5 | 255.4 | 369.5 | 380.7
1383 | 1238 | 256.2 | 108.4 | 256.4 | 258.4 | 140.2 | 254.5 | 368.6 | 380
1384 | 1239 | 255.7 | 108.2 | 254.4 | 257.3 | 139.8 | 255 | 367.7 | 379.4
1385 | 1240 | 255.2 | 108.2 | 253.3 | 256 | 139 | 254.7 | 366.7 | 378.7
1386 | 1241 | 254.8 | 108 | 252 | 254.6 | 138.1 | 254.2 | 365.8 | 377.9
1387 | 1242 | 254.4 | 107.9 | 250.3 | 253.6 | 137.8 | 253 | 364.9 | 377.1
1388 | 1243 | 254 | 107.7 | 248.2 | 252.6 | 137.8 | 252.8 | 364 | 376.4
1389 | 1244 | 253.6 | 108.1 | 246.1 | 250.6 | 137 | 251.4 | 363.1 | 375.6
1390 | 1245 | 253.2 | 108 | 244.3 | 249.6 | 137.3 | 252.1 | 362.1 | 374.9
1391 | 1246 | 252.8 | 107.4 | 242.6 | 249.1 | 137.3 | 250.1 | 361.2 | 374.1
1392 | 1247 | 252.4 | 107.3 | 241.8 | 248.2 | 137 | 250.1 | 360.3 | 373.4
1393 | 1248 | 252 | 106.8 | 240.6 | 247.3 | 137.4 | 250.4 | 359.4 | 372.6
1394 | 1249 | 251.6 | 106.3 | 239.2 | 246.4 | 136.5 | 249.4 | 358.4 | 371.8
1395 | 1250 | 251.2 | 106 | 239.1 | 245.5 | 136.3 | 247.5 | 357.5 | 371
1396 | 1251 | 250.8 | 106.1 | 240 | 244.5 | 135.7 | 247 | 356.6 | 370.2
1397 | 1252 | 250.4 | 106 | 241.4 | 243.5 | 134.7 | 246.4 | 355.6 | 369.5
1398 | 1253 | 250.1 | 105.2 | 242 | 242.3 | 133.2 | 245.1 | 354.7 | 368.8
1399 | 1254 | 249.7 | 104.9 | 241.7 | 241.3 | 132.4 | 243.9 | 353.8 | 368
1400 | 1255 | 249.3 | 104.3 | 241.7 | 240.3 | 131.7 | 243.3 | 352.8 | 367.3
1401 | 1256 | 248.9 | 103.7 | 242.3 | 239.2 | 130.9 | 243.3 | 351.9 | 366.6
1402 | 1257 | 248.6 | 103.2 | 241.6 | 238.5 | 130.3 | 242 | 350.9 | 365.8
1403 | 1258 | 248.3 | 102.8 | 239.9 | 237.6 | 129.9 | 240.1 | 349.9 | 365.1
1404 | 1259 | 248 | 102.2 | 239.1 | 236.8 | 129.5 | 238.4 | 349 | 364.4
1405 | 1260 | 247.6 | 101.7 | 237.6 | 236.2 | 128.8 | 239.1 | 348 | 363.7
1406 | 1261 | 247.2 | 101.2 | 237.1 | 235.4 | 127.8 | 238.3 | 347 | 363.1
1407 | 1262 | 246.8 | 101 | 235.9 | 234.4 | 126.7 | 236.8 | 346.1 | 362.4
1408 | 1263 | 246.5 | 101 | 234.7 | 233.4 | 126.1 | 236 | 345 | 361.7
1409 | 1264 | 246.1 | 100.7 | 234 | 232.5 | 125.8 | 235.1 | 344.1 | 361.1
1410 | 1265 | 245.7 | 100.7 | 231.9 | 231.5 | 125.9 | 234.8 | 343.1 | 360.4
1411 | 1266 | 245.4 | 100.6 | 230.5 | 230.6 | 125.3 | 234.5 | 342.1 | 359.7
1412 | 1267 | 245.2 | 100.6 | 228.9 | 229.6 | 124.6 | 234.3 | 341.1 | 359
1413 | 1268 | 244.9 | 100.7 | 226.6 | 229.1 | 124 | 232.7 | 340.1 | 358.3
1414 | 1269 | 244.5 | 100.2 | 224.6 | 227.9 | 123.5 | 232.2 | 339.2 | 357.6
1415 | 1270 | 244.1 | 100 | 224 | 226.9 | 122.9 | 232.5 | 338.2 | 356.8
1416 | 1271 | 243.6 | 99.6 | 223.7 | 226.1 | 122.5 | 231.7 | 337.2 | 356.1
1417 | 1272 | 243.3 | 99.3 | 223.8 | 224.9 | 121.8 | 231.9 | 336.2 | 355.3
1418 | 1273 | 242.9 | 99 | 223.2 | 223.8 | 121.4 | 231.1 | 335.3 | 354.6
1419 | 1274 | 242.5 | 98.5 | 221.9 | 222.8 | 121 | 230 | 334.3 | 353.9
1420 | 1275 | 242.1 | 98.4 | 221.6 | 221.5 | 120.5 | 229.4 | 333.3 | 353.2
1421 | 1276 | 241.7 | 98.2 | 221.1 | 220.4 | 120.1 | 227.4 | 332.4 | 352.5
1422 | 1277 | 241.4 | 98.5 | 219.5 | 219.9 | 120 | 227.4 | 331.4 | 351.8
1423 | 1278 | 241.1 | 99.1 | 218.6 | 218.3 | 119.4 | 225.6 | 330.5 | 351
1424 | 1279 | 240.9 | 99 | 218 | 216.9 | 118.9 | 223.7 | 329.5 | 350.3
1425 | 1280 | 240.4 | 98.4 | 216.3 | 215.7 | 119 | 221.6 | 328.6 | 349.5
1426 | 1281 | 240 | 98 | 215 | 214.9 | 119.9 | 220.9 | 327.7 | 348.7
1427 | 1282 | 239.7 | 97.7 | 213.4 | 214 | 120.1 | 219.8 | 326.8 | 348
1428 | 1283 | 239.3 | 97.6 | 211.8 | 213 | 120.2 | 219.3 | 325.8 | 347.3
1429 | 1284 | 238.9 | 97.2 | 210.6 | 212.1 | 120.1 | 218.6 | 324.9 | 346.5
1430 | 1285 | 238.5 | 97.1 | 210.1 | 211.5 | 120 | 219.4 | 324 | 345.8
1431 | 1286 | 238.1 | 96.7 | 210.3 | 210.8 | 119.5 | 219.1 | 323.1 | 345.1
1432 | 1287 | 237.8 | 96.2 | 210.4 | 209.9 | 118.7 | 218.5 | 322.2 | 344.4
1433 | 1288 | 237.4 | 95.9 | 210.1 | 209.2 | 118.1 | 217.2 | 321.3 | 343.7
1434 | 1289 | 237 | 95.9 | 209.5 | 208.3 | 117.5 | 216.3 | 320.4 | 343
1435 | 1290 | 236.6 | 95.6 | 208.5 | 207.3 | 117.1 | 214.6 | 319.4 | 342.3
1436 | 1291 | 236.2 | 94.7 | 208.5 | 206.6 | 117 | 213 | 318.5 | 341.5
1437 | 1292 | 235.8 | 94.4 | 208.7 | 205.5 | 116.7 | 211.2 | 317.6 | 340.8
1438 | 1293 | 235.5 | 94.6 | 208.6 | 204.3 | 116 | 209.4 | 316.8 | 340.1
1439 | 1294 | 235.1 | 95 | 208 | 203.5 | 115.8 | 208.4 | 315.9 | 339.4
1440 | 1295 | 234.8 | 95.7 | 207.8 | 202.9 | 115.7 | 208.1 | 315 | 338.7
1441 | 1296 | 234.4 | 95.8 | 207.3 | 202.1 | 115.4 | 206.8 | 314.1 | 338
1442 | 1297 | 234 | 95.7 | 206.5 | 201.4 | 115.3 | 205.6 | 313.3 | 337.4
1443 | 1298 | 233.6 | 95.9 | 206.3 | 200.7 | 115.2 | 204.4 | 312.4 | 336.7
1444 | 1299 | 233.3 | 96.9 | 206 | 200 | 114.8 | 203.3 | 311.6 | 336
1445 | 1300 | 233 | 97.6 | 204.6 | 199 | 114.8 | 203 | 310.7 | 335.3
1446 | 1301 | 232.6 | 98.5 | 204.2 | 197.7 | 114 | 202.1 | 309.9 | 334.6
1447 | 1302 | 232.3 | 99.2 | 203.5 | 196.2 | 113 | 202 | 309.1 | 333.8
1448 | 1303 | 232 | 99.9 | 202.7 | 194.6 | 112 | 200.4 | 308.2 | 332.9
1449 | 1304 | 231.6 | 100.6 | 201.7 | 193.4 | 111.7 | 198.9 | 307.4 | 332
1450 | 1305 | 231.2 | 100.6 | 201.7 | 192.7 | 111.7 | 198.1 | 306.6 | 331.1
1451 | 1306 | 230.9 | 100.3 | 201.5 | 192.3 | 112 | 197.2 | 305.8 | 330.2
1452 | 1307 | 230.6 | 99.8 | 200.8 | 191.7 | 111.8 | 196.7 | 305 | 329.4
1453 | 1308 | 230.4 | 99.3 | 200.2 | 191.2 | 111.8 | 195.9 | 304.1 | 328.5
1454 | 1309 | 230 | 99 | 200.5 | 190.6 | 111.6 | 195.1 | 303.3 | 327.6
1455 | 1310 | 229.7 | 98.8 | 200.8 | 189.9 | 111.1 | 195.3 | 302.5 | 326.7
1456 | 1311 | 229.4 | 98.7 | 200.5 | 189.3 | 110.8 | 194.7 | 301.8 | 325.8
1457 | 1312 | 229 | 99.2 | 199.8 | 188.6 | 110.7 | 194.6 | 301 | 325
1458 | 1313 | 228.6 | 99.9 | 198.9 | 187.6 | 110.2 | 194.5 | 300.2 | 324.2
1459 | 1314 | 228.3 | 99.9 | 197.8 | 186.4 | 109.5 | 194.7 | 299.5 | 323.4
1460 | 1315 | 227.9 | 99.6 | 196.9 | 185.8 | 109.3 | 193.6 | 298.8 | 322.6
1461 | 1316 | 227.6 | 99.7 | 195.5 | 185.1 | 109.1 | 192.1 | 298.1 | 321.8
1462 | 1317 | 227.3 | 99.9 | 194 | 184.6 | 109.2 | 190.8 | 297.5 | 321
1463 | 1318 | 226.9 | 100.4 | 192.9 | 184.5 | 109 | 189.9 | 296.8 | 320.2
1464 | 1319 | 226.6 | 99.9 | 192.2 | 183.8 | 108.7 | 189.1 | 296.1 | 319.4
1465 | 1320 | 226.4 | 99.5 | 191.4 | 183.2 | 108.5 | 188.7 | 295.4 | 318.7
1466 | 1321 | 226.1 | 99 | 191 | 182.7 | 109 | 188.8 | 294.8 | 318
1467 | 1322 | 225.8 | 98.4 | 190.6 | 182.6 | 109 | 189.1 | 294.1 | 317.2
1468 | 1323 | 225.5 | 97.5 | 191 | 182.7 | 109.6 | 188.3 | 293.4 | 316.5
1469 | 1324 | 225.2 | 97.3 | 192.1 | 182.5 | 110 | 187.5 | 292.7 | 315.7
1470 | 1325 | 224.9 | 97 | 192.4 | 181.9 | 110.8 | 187.4 | 291.9 | 315
1471 | 1326 | 224.5 | 96.6 | 192.1 | 181.8 | 110.9 | 186.8 | 291.2 | 314.3
1472 | 1327 | 224.2 | 96.4 | 193 | 181.7 | 110.6 | 186.6 | 290.4 | 313.7
1473 | 1328 | 223.9 | 96.3 | 193.9 | 181.2 | 111 | 186.3 | 289.6 | 313
1474 | 1329 | 223.6 | 96 | 195.1 | 180.6 | 111.9 | 186 | 288.8 | 312.3
1475 | 1330 | 223.3 | 95 | 195.9 | 180.1 | 111.4 | 186.4 | 288 | 311.6
1476 | 1331 | 223 | 94.8 | 196.6 | 179.3 | 110.5 | 186 | 287.2 | 310.9
1477 | 1332 | 222.7 | 94.8 | 197.2 | 178.7 | 109.7 | 184.9 | 286.4 | 310.3
1478 | 1333 | 222.4 | 94.9 | 197.9 | 178.2 | 109.6 | 184.5 | 285.6 | 309.6
1479 | 1334 | 222 | 94.7 | 198.4 | 178.1 | 109.4 | 184.1 | 284.9 | 309
1480 | 1335 | 221.7 | 94.4 | 197.9 | 178.1 | 109.9 | 182.1 | 284.1 | 308.3
1481 | 1336 | 221.3 | 94.4 | 198.5 | 178 | 109.8 | 180.6 | 283.4 | 307.7
1482 | 1337 | 220.9 | 94.3 | 199 | 177.7 | 109 | 180 | 282.6 | 307.1
1483 | 1338 | 220.5 | 94.1 | 199.7 | 177.5 | 108.2 | 180.3 | 281.9 | 306.4
1484 | 1339 | 220.1 | 93.5 | 200.3 | 177.2 | 107.7 | 179.8 | 281.1 | 305.8
1485 | 1340 | 219.7 | 93.1 | 201 | 177.1 | 107.1 | 178.2 | 280.4 | 305.1
1486 | 1341 | 219.3 | 92.7 | 201.3 | 176.9 | 107.1 | 176.6 | 279.6 | 304.5
1487 | 1342 | 218.9 | 92.4 | 201.2 | 176.6 | 107.5 | 176.2 | 278.9 | 303.9
1488 | 1343 | 218.6 | 92.2 | 200.1 | 176.3 | 107.9 | 175.6 | 278.2 | 303.2
1489 | 1344 | 218.3 | 91.9 | 199.6 | 176 | 109.5 | 175.5 | 277.4 | 302.5
1490 | 1345 | 218.1 | 91.4 | 199.2 | 175.5 | 109.3 | 175.2 | 276.7 | 302
1491 | 1346 | 217.9 | 90.9 | 199.3 | 175.3 | 108.5 | 173.5 | 275.9 | 301.4
1492 | 1347 | 217.6 | 90.2 | 199.4 | 174.7 | 107.7 | 171.8 | 275.2 | 300.8
1493 | 1348 | 217.4 | 89.8 | 198.8 | 174.3 | 107.1 | 171 | 274.4 | 300.2
1494 | 1349 | 217.1 | 89.5 | 197.8 | 174 | 106.7 | 170.8 | 273.7 | 299.5
1495 | 1350 | 216.7 | 89.3 | 197 | 173.6 | 106.2 | 169.1 | 272.9 | 299
1496 | 1351 | 216.4 | 89.6 | 196.2 | 173.1 | 105.8 | 168.1 | 272.2 | 298.4
1497 | 1352 | 216.1 | 89.7 | 195.6 | 172.8 | 105.3 | 167.4 | 271.4 | 297.9
1498 | 1353 | 215.8 | 89.4 | 194.5 | 172.5 | 104.7 | 167 | 270.8 | 297.5
1499 | 1354 | 215.4 | 89.1 | 193.4 | 172.3 | 104.6 | 166.3 | 270.1 | 296.9
1500 | 1355 | 215 | 89 | 192.4 | 171.9 | 104.2 | 165.3 | 269.4 | 296.3
1501 | 1356 | 214.7 | 88.8 | 191.5 | 171.7 | 103.8 | 164.1 | 268.8 | 295.8
1502 | 1357 | 214.4 | 88.9 | 190.3 | 171.5 | 103.5 | 163.8 | 268.3 | 295.1
1503 | 1358 | 214.2 | 88.8 | 188.9 | 171.7 | 103.9 | 163.4 | 267.8 | 294.6
1504 | 1359 | 213.9 | 88.4 | 188.5 | 171.6 | 103.8 | 162.4 | 267.3 | 294
1505 | 1360 | 213.6 | 88.1 | 188.5 | 171.2 | 103.4 | 161.7 | 266.9 | 293.5
1506 | 1361 | 213.3 | 87.6 | 188.2 | 170.7 | 103.3 | 162 | 266.5 | 292.9
1507 | 1362 | 213 | 87.1 | 187 | 170.2 | 102.7 | 161.4 | 266.1 | 292.4
1508 | 1363 | 212.8 | 86.8 | 185.3 | 169.7 | 102.4 | 160.6 | 265.7 | 291.8
1509 | 1364 | 212.6 | 86.4 | 184.7 | 169.1 | 102.2 | 159.6 | 265.4 | 291.3
1510 | 1365 | 212.3 | 86.2 | 184.4 | 168.2 | 101.7 | 158.4 | 265.1 | 290.7
1511 | 1366 | 212 | 86.3 | 183.5 | 167.6 | 101.2 | 157.4 | 264.8 | 290.2
1512 | 1367 | 211.7 | 86.2 | 182.1 | 167.1 | 100.8 | 156.6 | 264.4 | 289.7
1513 | 1368 | 211.4 | 86.6 | 181.4 | 166.3 | 100.4 | 156.5 | 264 | 289.1
1514 | 1369 | 211.1 | 86.8 | 180.8 | 165.4 | 100 | 157 | 263.6 | 288.6
1515 | 1370 | 210.8 | 86.7 | 179.7 | 164.5 | 99.6 | 156.3 | 263.2 | 288.1
1516 | 1371 | 210.5 | 86.6 | 178.4 | 163.8 | 99.3 | 155.8 | 262.7 | 287.6
1517 | 1372 | 210.2 | 86.7 | 176.9 | 162.9 | 98.8 | 154.7 | 262.1 | 287
1518 | 1373 | 209.9 | 86.7 | 176 | 162.1 | 98.1 | 154.1 | 261.5 | 286.5
1519 | 1374 | 209.6 | 87.3 | 175 | 161.3 | 97.5 | 153 | 260.8 | 286
1520 | 1375 | 209.3 | 87.8 | 173.9 | 160.7 | 97.6 | 151.9 | 260.2 | 285.5
1521 | 1376 | 209.1 | 87.7 | 173.1 | 160.3 | 97.7 | 151.2 | 259.5 | 285
1522 | 1377 | 208.8 | 87.2 | 172.7 | 159.7 | 97.8 | 150.5 | 258.8 | 284.5
1523 | 1378 | 208.5 | 86.6 | 173 | 159.1 | 97.7 | 150.3 | 258.1 | 284
1524 | 1379 | 208.2 | 86.3 | 173 | 158.8 | 97.4 | 149.5 | 257.5 | 283.4
1525 | 1380 | 207.9 | 88.6 | 173.6 | 158.7 | 97.4 | 148.6 | 256.8 | 282.9
1526 | 1381 | 207.6 | 88.2 | 173.8 | 158.3 | 97.7 | 148.6 | 256.1 | 282.4
1527 | 1382 | 207.3 | 87.2 | 174.5 | 157.5 | 98.3 | 148.9 | 255.5 | 281.9
1528 | 1383 | 207 | 87 | 175.2 | 156.8 | 98.7 | 148.1 | 254.8 | 281.5
1529 | 1384 | 206.8 | 89.5 | 176.3 | 156.4 | 99.2 | 148.3 | 254.1 | 280.9
1530 | 1385 | 206.5 | 89.5 | 176.5 | 155.7 | 101.5 | 147.6 | 253.5 | 280.5
1531 | 1386 | 206.3 | 88.6 | 176.5 | 155.3 | 104.5 | 147.6 | 252.8 | 280
1532 | 1387 | 206 | 87.5 | 176.2 | 154.4 | 106.9 | 147.5 | 252.2 | 279.4
1533 | 1388 | 205.7 | 86.9 | 176.4 | 153.7 | 107.1 | 146.6 | 251.5 | 279
1534 | 1389 | 205.4 | 86.7 | 176.9 | 153.3 | 108.4 | 145.3 | 250.9 | 278.5
1535 | 1390 | 205.2 | 86.4 | 176.9 | 153.2 | 109.4 | 144.4 | 250.3 | 278
1536 | 1391 | 204.9 | 85.8 | 177.3 | 152.9 | 111 | 144 | 249.7 | 277.4
1537 | 1392 | 204.6 | 85.3 | 177.2 | 152.3 | 112.4 | 143.4 | 249.1 | 276.9
1538 | 1393 | 204.4 | 84.7 | 177.1 | 151.9 | 113 | 143.1 | 248.5 | 276.4
1539 | 1394 | 204 | 84.1 | 176.9 | 151.3 | 113 | 142.7 | 247.9 | 275.9
1540 | 1395 | 203.7 | 83.6 | 177.3 | 150.7 | 113.7 | 142.1 | 247.3 | 275.4
1541 | 1396 | 203.4 | 83.2 | 177.2 | 149.9 | 114.5 | 141.6 | 246.7 | 274.9
1542 | 1397 | 203.1 | 82.9 | 177 | 149.4 | 114.9 | 141.2 | 246.1 | 274.4
1543 | 1398 | 202.9 | 82.9 | 176.8 | 148.9 | 115.8 | 140.9 | 245.5 | 273.9
1544 | 1399 | 202.5 | 83.5 | 176.4 | 148.5 | 117 | 140.4 | 244.9 | 273.4
1545 | 1400 | 202.1 | 83.7 | 176.2 | 148.1 | 116.4 | 140.2 | 244.3 | 272.9
1546 | 1401 | 201.8 | 83.7 | 176.2 | 147.9 | 114 | 139.5 | 243.8 | 272.4
1547 | 1402 | 201.4 | 83.5 | 176.2 | 147.9 | 112 | 139.1 | 243.2 | 272
1548 | 1403 | 201.2 | 83.2 | 176.2 | 147.7 | 111.7 | 137.8 | 242.7 | 271.5
1549 | 1404 | 200.9 | 82.6 | 176 | 147.5 | 112.6 | 136.6 | 242.1 | 271
1550 | 1405 | 200.6 | 82.7 | 175.4 | 147.1 | 111.3 | 135.9 | 241.6 | 270.6
1551 | 1406 | 200.3 | 83.1 | 174.2 | 147.2 | 109.7 | 135.4 | 241.1 | 270.2
1552 | 1407 | 200.1 | 83.5 | 173.6 | 147.8 | 109 | 134.5 | 240.5 | 269.6
1553 | 1408 | 199.9 | 83.5 | 173.7 | 148.6 | 109 | 134.3 | 240 | 269.1
1554 | 1409 | 199.4 | 82.8 | 173.9 | 148.8 | 108.4 | 134.7 | 239.4 | 268.7
1555 | 1410 | 199.1 | 82 | 173.3 | 148.6 | 107.5 | 134 | 238.9 | 268.3
1556 | 1411 | 198.9 | 81.6 | 172.9 | 148.5 | 107 | 133 | 238.3 | 267.8
1557 | 1412 | 198.6 | 81.4 | 172.5 | 148.1 | 108.4 | 133.2 | 237.7 | 267.3
1558 | 1413 | 198.3 | 81.3 | 172.3 | 147.9 | 108.8 | 133.1 | 237.1 | 266.9
1559 | 1414 | 198 | 81.2 | 172 | 147.5 | 109.1 | 133 | 236.5 | 266.4
1560 | 1415 | 197.7 | 81.2 | 171.7 | 147.5 | 110.4 | 132 | 236 | 265.9
1561 | 1416 | 197.5 | 80.6 | 171.4 | 147.6 | 111.2 | 131.6 | 235.4 | 265.5
1562 | 1417 | 197.2 | 80.4 | 171.1 | 148 | 111.3 | 131.1 | 234.8 | 265
1563 | 1418 | 197 | 80 | 171.4 | 148.6 | 110.5 | 130.7 | 234.2 | 264.5
1564 | 1419 | 196.7 | 79.5 | 171.5 | 149.1 | 111.2 | 130.5 | 233.7 | 264
1565 | 1420 | 196.3 | 79.3 | 171.3 | 149.2 | 110.6 | 130.2 | 233.1 | 263.5
1566 | 1421 | 196 | 79.5 | 171 | 149.1 | 109.4 | 129.8 | 232.6 | 263.1
1567 | 1422 | 195.8 | 79.3 | 170.7 | 148.5 | 107.6 | 129.3 | 232 | 262.7
1568 | 1423 | 195.6 | 79.2 | 170.5 | 147.9 | 105.6 | 128.6 | 231.4 | 262.3
1569 | 1424 | 195.3 | 79.2 | 169.8 | 147.6 | 103.8 | 128.2 | 230.9 | 261.9
1570 | 1425 | 195 | 78.9 | 169.5 | 147.6 | 102.5 | 128.1 | 230.3 | 261.5
1571 | 1426 | 194.7 | 78.6 | 168.9 | 147.6 | 101.5 | 127.7 | 229.7 | 261
1572 | 1427 | 194.5 | 78.6 | 168.6 | 147.5 | 101.6 | 126.9 | 229.2 | 260.6
1573 | 1428 | 194.2 | 78.6 | 168 | 147 | 102.3 | 125.9 | 228.6 | 260.1
1574 | 1429 | 194 | 78.5 | 167.6 | 146.6 | 100.9 | 126 | 228.1 | 259.7
1575 | 1430 | 193.7 | 78.3 | 167.3 | 146.1 | 100.3 | 125.2 | 227.5 | 259.2
1576 | 1431 | 193.5 | 78.2 | 166.9 | 146.4 | 101.1 | 124.4 | 227 | 258.8
1577 | 1432 | 193.3 | 78.1 | 166.5 | 146.2 | 102.4 | 124.9 | 226.4 | 258.3
1578 | 1433 | 193 | 77.9 | 166.4 | 145.5 | 103.2 | 124.9 | 225.9 | 257.8
1579 | 1434 | 192.7 | 78 | 166.2 | 145.5 | 104.2 | 124.9 | 225.3 | 257.5
1580 | 1435 | 192.4 | 78.2 | 166 | 145.5 | 105.4 | 124.6 | 224.7 | 257.2
1581 | 1436 | 192.2 | 78.3 | 165.7 | 145.5 | 105.4 | 124 | 224.2 | 256.8
1582 | 1437 | 192 | 78.6 | 165.9 | 145.4 | 106.7 | 123.7 | 223.7 | 256.4
1583 | 1438 | 191.8 | 79 | 165.6 | 145 | 108.1 | 122.8 | 223.1 | 255.9
1584 | 1439 | 191.4 | 78.9 | 165 | 144 | 109.7 | 122.7 | 222.6 | 255.4
1585 | 1440 | 191.1 | 78.6 | 164.5 | 142.9 | 109.8 | 123 | 222 | 254.9
1586 | 1441 | 190.7 | 78.2 | 163.7 | 141.8 | 108.1 | 123.4 | 221.5 | 254.5
1587 | 1442 | 190.4 | 78 | 162.8 | 140.9 | 106.3 | 123 | 220.9 | 254.2
1588 | 1443 | 190.1 | 77.7 | 162.1 | 140 | 106.6 | 123 | 220.3 | 253.8
1589 | 1444 | 189.8 | 77.3 | 161.2 | 139.3 | 106.7 | 123.1 | 219.7 | 253.3
1590 | 1445 | 189.6 | 77.1 | 160.1 | 139.2 | 105.7 | 122.7 | 219.1 | 252.8
1591 | 1446 | 189.3 | 77.2 | 159.7 | 139.2 | 104.2 | 122.2 | 218.6 | 252.4
1592 | 1447 | 189.1 | 76.9 | 159.5 | 139 | 102.6 | 121.6 | 218 | 252.1
1593 | 1448 | 188.9 | 76.6 | 159.1 | 138.8 | 101 | 121.7 | 217.4 | 251.7
1594 | 1449 | 188.6 | 76.2 | 159 | 138.5 | 99.6 | 121 | 216.8 | 251.4
1595 | 1450 | 188.4 | 75.9 | 158.3 | 138.4 | 98.3 | 121.1 | 216.3 | 251
1596 | 1451 | 188.1 | 75.6 | 157.8 | 138.4 | 97.1 | 120.9 | 215.7 | 250.7
1597 | 1452 | 187.9 | 75.4 | 157.3 | 138.2 | 95.9 | 120 | 215.1 | 250.3
1598 | 1453 | 187.7 | 75.5 | 156.4 | 138.4 | 95.1 | 119.3 | 214.6 | 249.8
1599 | 1454 | 187.4 | 75.3 | 155.7 | 138.4 | 94 | 118.9 | 214 | 249.4
1600 | 1455 | 187.1 | 75 | 155.3 | 138.3 | 92.9 | 118.9 | 213.5 | 248.9
1601 | 1456 | 186.9 | 74.9 | 154.8 | 138 | 91.7 | 119.8 | 212.9 | 248.5
1602 | 1457 | 186.7 | 75.1 | 154.3 | 137.9 | 90.6 | 119.5 | 212.4 | 248.1
1603 | 1458 | 186.5 | 75 | 153.8 | 137.9 | 89.7 | 117.9 | 211.8 | 247.7
1604 | 1459 | 186.3 | 75.1 | 153.5 | 138.2 | 89.1 | 116.9 | 211.3 | 247.3
1605 | 1460 | 186.1 | 74.7 | 153.4 | 138.7 | 88.7 | 116.4 | 210.8 | 247
1606 | 1461 | 185.9 | 74.5 | 153.3 | 138.7 | 88.6 | 115.7 | 210.3 | 246.7
1607 | 1462 | 185.6 | 74.4 | 153 | 138.4 | 88 | 116.5 | 209.8 | 246.3
1608 | 1463 | 185.4 | 74.3 | 152.4 | 138.5 | 87.5 | 117.1 | 209.3 | 246
1609 | 1464 | 185 | 74.2 | 152.1 | 138.4 | 86.9 | 117.4 | 208.8 | 245.6
1610 | 1465 | 184.8 | 74.1 | 151 | 138.3 | 86.4 | 117.5 | 208.3 | 245.2
1611 | 1466 | 184.5 | 74.2 | 149.3 | 138 | 85.9 | 116.5 | 207.8 | 244.8
1612 | 1467 | 184.2 | 74.5 | 147.9 | 137.4 | 85.6 | 115.9 | 207.3 | 244.3
1613 | 1468 | 183.9 | 74.4 | 146.6 | 137 | 85.2 | 116.1 | 206.8 | 243.9
1614 | 1469 | 183.6 | 74.2 | 145.7 | 136.8 | 85.3 | 115.5 | 206.3 | 243.6
1615 | 1470 | 183.4 | 74.2 | 144.3 | 136.4 | 85.2 | 115.2 | 205.8 | 243.2
1616 | 1471 | 183.2 | 74.6 | 143 | 135.4 | 84.7 | 115.1 | 205.3 | 242.9
1617 | 1472 | 183 | 75.5 | 142.3 | 134.3 | 84 | 114.8 | 204.9 | 242.4
1618 | 1473 | 182.7 | 76.3 | 142.3 | 133.4 | 83.5 | 113.9 | 204.4 | 242
1619 | 1474 | 182.5 | 76.6 | 141.5 | 132.3 | 83.1 | 113.4 | 203.9 | 241.6
1620 | 1475 | 182.3 | 77.8 | 141.2 | 131.1 | 82.6 | 112.9 | 203.5 | 241.2
1621 | 1476 | 182 | 78.5 | 141.3 | 130.4 | 82.4 | 112.7 | 203 | 240.8
1622 | 1477 | 181.7 | 77.9 | 140.9 | 129.7 | 82.3 | 112.3 | 202.5 | 240.4
1623 | 1478 | 181.5 | 77 | 140.2 | 129 | 82 | 112 | 202.1 | 240.1
1624 | 1479 | 181.2 | 76.8 | 139.9 | 127.9 | 81.6 | 112 | 201.6 | 239.7
1625 | 1480 | 180.9 | 76.8 | 139.3 | 127.2 | 81.6 | 111.5 | 201.2 | 239.4
1626 | 1481 | 180.6 | 76.9 | 138.6 | 126.6 | 81.4 | 110.9 | 200.7 | 239
1627 | 1482 | 180.4 | 77.3 | 138.7 | 125.9 | 81.1 | 110.7 | 200.3 | 238.7
1628 | 1483 | 180.2 | 77.5 | 139 | 125.2 | 80.9 | 110.2 | 199.9 | 238.3
1629 | 1484 | 180.1 | 77.4 | 138.9 | 124.9 | 80.8 | 109.9 | 199.4 | 237.9
1630 | 1485 | 179.8 | 77.2 | 137.9 | 125.1 | 81 | 110.1 | 199 | 237.6
1631 | 1486 | 179.6 | 76.6 | 137.5 | 125.4 | 81.6 | 110.4 | 198.6 | 237.2
1632 | 1487 | 179.4 | 75.8 | 137.1 | 125.4 | 82.4 | 110.4 | 198.1 | 236.8
1633 | 1488 | 179.2 | 75.1 | 136.9 | 125 | 83 | 110.1 | 197.7 | 236.4
1634 | 1489 | 179.1 | 74.8 | 136.8 | 124.7 | 83.6 | 110.2 | 197.3 | 236.1
1635 | 1490 | 178.9 | 74.7 | 136.7 | 124.5 | 84.6 | 109.6 | 196.8 | 235.6
1636 | 1491 | 178.7 | 74.5 | 136.9 | 124.2 | 85.5 | 109.5 | 196.4 | 235.1
1637 | 1492 | 178.4 | 74 | 137 | 124.1 | 87 | 109.6 | 196 | 234.7
1638 | 1493 | 178.2 | 73.3 | 137 | 123.9 | 88.1 | 109.6 | 195.6 | 234.4
1639 | 1494 | 178 | 73.1 | 137.1 | 124 | 87.3 | 109.2 | 195.2 | 234
1640 | 1495 | 177.7 | 72.7 | 137.5 | 124.1 | 86.6 | 108.5 | 194.8 | 233.6
1641 | 1496 | 177.4 | 72.6 | 137.7 | 124 | 86.4 | 108.2 | 194.3 | 233.2
1642 | 1497 | 177.1 | 72.7 | 137.9 | 123.9 | 87.3 | 108.4 | 193.9 | 232.9
1643 | 1498 | 176.9 | 72.3 | 137.8 | 123.6 | 86.8 | 108.2 | 193.5 | 232.6
1644 | 1499 | 176.6 | 72.1 | 137.9 | 123.5 | 85.9 | 107.9 | 193.1 | 232.2
1645 | 1500 | 176.4 | 72.1 | 138 | 123.4 | 85 | 107.8 | 192.7 | 231.8
1646 | 1501 | 176.2 | 72.2 | 137.8 | 123.5 | 84.2 | 107.9 | 192.3 | 231.3
1647 | 1502 | 176 | 71.8 | 137.9 | 123.6 | 83.5 | 108.1 | 191.9 | 231
1648 | 1503 | 175.8 | 71.5 | 138.2 | 124 | 83 | 107.7 | 191.5 | 230.6
1649 | 1504 | 175.5 | 71.3 | 138.4 | 124.3 | 82.6 | 107.5 | 191.1 | 230.3
1650 | 1505 | 175.3 | 71.2 | 138.3 | 124.3 | 81.9 | 107.7 | 190.7 | 229.9
1651 | 1506 | 175 | 71.2 | 137.7 | 124.5 | 81.7 | 106.8 | 190.3 | 229.6
1652 | 1507 | 174.8 | 71 | 136.7 | 124.4 | 81.3 | 106.6 | 189.9 | 229.3
1653 | 1508 | 174.6 | 71.1 | 135.2 | 124.4 | 81.1 | 106.2 | 189.5 | 228.9
1654 | 1509 | 174.4 | 70.8 | 134.2 | 124.5 | 80.9 | 105.2 | 189.1 | 228.6
1655 | 1510 | 174.2 | 70.8 | 133.2 | 124.1 | 80.5 | 104.6 | 188.7 | 228.3
1656 | 1511 | 174 | 70.9 | 132 | 123.7 | 80.3 | 104.3 | 188.3 | 228
1657 | 1512 | 173.7 | 71.3 | 130.8 | 123.5 | 80.3 | 103.7 | 187.9 | 227.8
1658 | 1513 | 173.5 | 71.1 | 130.5 | 123.3 | 79.8 | 103.3 | 187.5 | 227.5
1659 | 1514 | 173.3 | 71.1 | 129.8 | 123.1 | 79.4 | 103 | 187.1 | 227.2
1660 | 1515 | 173.1 | 70.8 | 129 | 122.6 | 79.1 | 102.5 | 186.7 | 226.8
1661 | 1516 | 172.9 | 70.5 | 128.4 | 122.3 | 79.2 | 102.4 | 186.4 | 226.4
1662 | 1517 | 172.6 | 70 | 127.9 | 122 | 78.7 | 101.6 | 185.9 | 226.1
1663 | 1518 | 172.4 | 69.6 | 127.5 | 121.9 | 78.3 | 101.2 | 185.6 | 225.8
1664 | 1519 | 172.1 | 69.4 | 127 | 121.8 | 78.1 | 101 | 185.2 | 225.5
1665 | 1520 | 171.9 | 69.3 | 126.6 | 121.7 | 77.6 | 100.8 | 184.8 | 225.2
1666 | 1521 | 171.7 | 68.9 | 126.4 | 121.8 | 77.4 | 100.6 | 184.4 | 224.8
1667 | 1522 | 171.5 | 68.6 | 126 | 121.8 | 77.2 | 100.8 | 184.1 | 224.4
1668 | 1523 | 171.3 | 68.3 | 125.5 | 121.7 | 76.9 | 101.3 | 183.7 | 224.1
1669 | 1524 | 171.1 | 68.4 | 124.6 | 121.7 | 76.5 | 101.2 | 183.4 | 223.7
1670 | 1525 | 170.9 | 68.5 | 123.8 | 121.9 | 76.2 | 100.9 | 183 | 223.4
1671 | 1526 | 170.7 | 68.2 | 123.6 | 121.9 | 76 | 100.7 | 182.6 | 223.1
1672 | 1527 | 170.5 | 69 | 124 | 121.9 | 75.8 | 100.7 | 182.3 | 222.9
1673 | 1528 | 170.3 | 69.1 | 124.6 | 121.9 | 75.4 | 100.7 | 181.9 | 222.5
1674 | 1529 | 170.1 | 68.8 | 124.5 | 121.6 | 75.2 | 101.1 | 181.5 | 222.2
1675 | 1530 | 169.8 | 68.4 | 124.7 | 121.5 | 74.9 | 100.6 | 181.2 | 221.8
1676 | 1531 | 169.6 | 68.2 | 125 | 121.4 | 74.8 | 100.4 | 180.8 | 221.4
1677 | 1532 | 169.4 | 67.7 | 125.1 | 121.1 | 75.3 | 99.9 | 180.5 | 221.2
1678 | 1533 | 169.1 | 67.7 | 125.3 | 120.9 | 75.4 | 99.7 | 180.1 | 220.9
1679 | 1534 | 168.9 | 67.5 | 125.5 | 120.7 | 75.3 | 99.8 | 179.7 | 220.7
1680 | 1535 | 168.7 | 67 | 125.6 | 120.4 | 74.9 | 100.2 | 179.4 | 220.3
1681 | 1536 | 168.5 | 66.7 | 125.4 | 120.3 | 74.5 | 100.2 | 179 | 220
1682 | 1537 | 168.2 | 66.4 | 125.6 | 120.1 | 74.1 | 99.8 | 178.7 | 219.8
1683 | 1538 | 168 | 66.1 | 125.5 | 120.1 | 74 | 99.2 | 178.3 | 219.6
1684 | 1539 | 167.8 | 65.8 | 125.5 | 120.1 | 73.8 | 99 | 177.9 | 219.3
1685 | 1540 | 167.6 | 65.7 | 125.6 | 120.3 | 73.6 | 98.5 | 177.6 | 218.9
1686 | 1541 | 167.4 | 65.5 | 125.6 | 120.3 | 73.4 | 98 | 177.2 | 218.6
1687 | 1542 | 167.2 | 65.3 | 125.6 | 120.3 | 73.3 | 97.8 | 176.9 | 218.2
1688 | 1543 | 167 | 65.1 | 125.5 | 120.2 | 73 | 97.6 | 176.5 | 217.8
1689 | 1544 | 166.9 | 65 | 125 | 120.3 | 72.8 | 97.9 | 176.2 | 217.5
1690 | 1545 | 166.7 | 64.6 | 124.4 | 120.4 | 72.9 | 98.3 | 175.8 | 217.1
1691 | 1546 | 166.5 | 64.7 | 123.9 | 120.3 | 73.1 | 98.6 | 175.5 | 216.9
1692 | 1547 | 166.3 | 64.7 | 122.9 | 120.1 | 73.1 | 98.7 | 175.2 | 216.5
1693 | 1548 | 166.1 | 64.7 | 122 | 119.6 | 72.8 | 98.3 | 174.8 | 216.2
1694 | 1549 | 165.9 | 64.5 | 121.1 | 119.3 | 72.7 | 97.7 | 174.5 | 215.8
1695 | 1550 | 165.6 | 64.5 | 120.1 | 119.1 | 72.9 | 97.4 | 174.2 | 215.5
1696 | 1551 | 165.4 | 64.3 | 119.3 | 119 | 73 | 97.2 | 173.9 | 215.1
1697 | 1552 | 165.2 | 64.2 | 118.5 | 118.9 | 72.8 | 97.1 | 173.5 | 214.8
1698 | 1553 | 165 | 64.3 | 117.9 | 118.8 | 72.5 | 96.9 | 173.2 | 214.4
1699 | 1554 | 164.8 | 64.2 | 117.6 | 118.4 | 72.2 | 96.7 | 172.9 | 214.1
1700 | 1555 | 164.6 | 64.4 | 117.6 | 118 | 72 | 96.6 | 172.5 | 213.8
1701 | 1556 | 164.4 | 64.3 | 117.3 | 117.7 | 71.8 | 96.5 | 172.2 | 213.5
1702 | 1557 | 164.3 | 64.2 | 117.2 | 117.1 | 71.5 | 96.6 | 171.9 | 213.2
1703 | 1558 | 164.1 | 64 | 117.1 | 116.5 | 71.4 | 96.3 | 171.5 | 212.9
1704 | 1559 | 163.9 | 63.6 | 117.3 | 116.4 | 71.3 | 96.2 | 171.2 | 212.6
1705 | 1560 | 163.8 | 63.5 | 117.7 | 116.3 | 71.2 | 96.3 | 170.9 | 212.3
1706 | 1561 | 163.6 | 63.7 | 117.9 | 116.2 | 71 | 96.2 | 170.5 | 212
1707 | 1562 | 163.4 | 63.7 | 118.1 | 116.2 | 70.9 | 96.4 | 170.2 | 211.7
1708 | 1563 | 163.1 | 63.6 | 118.5 | 116.3 | 70.7 | 96.9 | 169.9 | 211.4
1709 | 1564 | 162.9 | 63.8 | 118.8 | 116.6 | 70.6 | 97.2 | 169.6 | 211
1710 | 1565 | 162.7 | 63.6 | 118.9 | 116.7 | 70.7 | 97.4 | 169.2 | 210.7
1711 | 1566 | 162.5 | 63.6 | 119.1 | 117 | 70.7 | 97.2 | 168.9 | 210.5
1712 | 1567 | 162.2 | 63.4 | 119 | 117.2 | 70.7 | 96.8 | 168.6 | 210.2
1713 | 1568 | 162 | 63.3 | 118.9 | 117.3 | 71 | 96.4 | 168.3 | 210
1714 | 1569 | 161.7 | 63.4 | 119.1 | 117.3 | 70.8 | 96.3 | 167.9 | 209.6
1715 | 1570 | 161.5 | 63.2 | 119.2 | 117.3 | 70.8 | 96.2 | 167.6 | 209.2
1716 | 1571 | 161.3 | 63 | 118.7 | 117.4 | 71.9 | 95.9 | 167.3 | 208.9
1717 | 1572 | 161.1 | 62.9 | 118.7 | 117.6 | 73.1 | 96 | 167 | 208.6
1718 | 1573 | 160.9 | 62.9 | 118.9 | 117.6 | 73.7 | 95.7 | 166.7 | 208.2
1719 | 1574 | 160.8 | 63.1 | 119.1 | 117.5 | 74.7 | 95.3 | 166.4 | 207.9
1720 | 1575 | 160.6 | 63.2 | 119 | 117.2 | 75.8 | 95.5 | 166.1 | 207.6
1721 | 1576 | 160.3 | 63.2 | 119 | 117 | 77 | 95.3 | 165.8 | 207.3
1722 | 1577 | 160.2 | 63.6 | 118.9 | 116.9 | 78.2 | 94.7 | 165.5 | 207.1
1723 | 1578 | 160 | 63.7 | 118.8 | 116.6 | 79.9 | 94.7 | 165.2 | 206.8
1724 | 1579 | 159.8 | 63.8 | 118.9 | 116.4 | 80.6 | 94.4 | 164.9 | 206.4
1725 | 1580 | 159.6 | 64 | 118.9 | 116.1 | 82 | 93.9 | 164.6 | 206
1726 | 1581 | 159.5 | 64 | 118.4 | 115.7 | 82.9 | 93.5 | 164.3 | 205.7
1727 | 1582 | 159.3 | 63.8 | 118 | 115.7 | 83.5 | 93.1 | 164 | 205.3
1728 | 1583 | 159.1 | 63.8 | 117.9 | 115.8 | 84.2 | 92.9 | 163.7 | 205.1
1729 | 1584 | 158.9 | 63.4 | 117.6 | 115.6 | 84.7 | 92.4 | 163.4 | 204.7
1730 | 1585 | 158.7 | 63.1 | 117 | 115.4 | 84.9 | 92.4 | 163.1 | 204.4
1731 | 1586 | 158.5 | 63 | 116.7 | 115.4 | 85.7 | 92.2 | 162.8 | 204
1732 | 1587 | 158.3 | 62.6 | 116.7 | 115.6 | 86.7 | 92.3 | 162.5 | 203.6
1733 | 1588 | 158.2 | 62.4 | 117 | 116.2 | 87.7 | 92.2 | 162.2 | 203.2
1734 | 1589 | 158 | 62.5 | 117.4 | 116.9 | 87.4 | 92.1 | 161.9 | 202.9
1735 | 1590 | 157.8 | 62.7 | 117.7 | 117.3 | 87.1 | 91.9 | 161.6 | 202.6
1736 | 1591 | 157.6 | 63 | 117.8 | 115.5 | 87.7 | 91.5 | 161.3 | 202.3
1737 | 1592 | 157.4 | 63.5 | 117.4 | 114.2 | 88.8 | 91.1 | 161 | 201.9
1738 | 1593 | 157.3 | 64 | 117.2 | 112.9 | 90.6 | 90.5 | 160.7 | 201.6
1739 | 1594 | 157.1 | 64.3 | 117.3 | 111.5 | 90.9 | 90 | 160.4 | 201.3
1740 | 1595 | 156.8 | 64.5 | 117.2 | 111.2 | 91.5 | 89.7 | 160.1 | 201
1741 | 1596 | 156.5 | 64.8 | 117.3 | 110.9 | 91.7 | 89.3 | 159.8 | 200.7
1742 | 1597 | 156.4 | 65.2 | 117.6 | 111.1 | 92.1 | 89.1 | 159.5 | 200.3
1743 | 1598 | 156.2 | 65.3 | 117.7 | 111.3 | 92.6 | 88.9 | 159.2 | 200
1744 | 1599 | 156 | 65.5 | 117.6 | 111.4 | 93.2 | 88.9 | 158.9 | 199.7
1745 | 1600 | 155.9 | 65.2 | 117.6 | 111.7 | 93.2 | 88.6 | 158.6 | 199.4
1746 | 1601 | 155.7 | 64.8 | 117.5 | 111.4 | 92.6 | 88.4 | 158.3 | 199.1
1747 | 1602 | 155.5 | 64.2 | 117.6 | 110.6 | 92 | 88.2 | 158.1 | 198.9
1748 | 1603 | 155.3 | 64 | 117.5 | 110.7 | 92.3 | 88 | 157.8 | 198.7
1749 | 1604 | 155.1 | 63.8 | 117.1 | 110.9 | 92.7 | 87.7 | 157.5 | 198.4
1750 | 1605 | 155 | 63.2 | 116.8 | 110.9 | 92.5 | 87.5 | 157.3 | 198.1
1751 | 1606 | 154.8 | 62.6 | 116.8 | 111.2 | 92.2 | 87.3 | 157 | 197.7
1752 | 1607 | 154.7 | 62.2 | 116.7 | 111 | 91.8 | 86.9 | 156.7 | 197.4
1753 | 1608 | 154.5 | 62.1 | 116.7 | 111.3 | 91.4 | 86.7 | 156.4 | 197
1754 | 1609 | 154.3 | 62.2 | 116.7 | 111.5 | 91.6 | 86.5 | 156.2 | 196.7
1755 | 1610 | 154.1 | 62.5 | 116.6 | 112.3 | 92 | 86.3 | 155.9 | 196.5
1756 | 1611 | 153.9 | 62.5 | 116.4 | 112.5 | 92.1 | 86.2 | 155.6 | 196.2
1757 | 1612 | 153.7 | 62.5 | 116.4 | 112.7 | 92.1 | 86 | 155.3 | 196
1758 | 1613 | 153.4 | 62.8 | 116.1 | 112 | 92.8 | 85.5 | 155.1 | 195.8
1759 | 1614 | 153.2 | 63.5 | 116.1 | 111.6 | 93.6 | 85 | 154.8 | 195.5
1760 | 1615 | 153 | 63.2 | 115.8 | 112.2 | 93.5 | 84.8 | 154.5 | 195.2
1761 | 1616 | 152.8 | 62.9 | 115.6 | 113 | 93.6 | 84.7 | 154.2 | 194.9
1762 | 1617 | 152.7 | 62.9 | 115.4 | 113.4 | 93 | 84.6 | 154 | 194.6
1763 | 1618 | 152.5 | 63 | 115.5 | 113.4 | 92.6 | 84.5 | 153.7 | 194.3
1764 | 1619 | 152.3 | 63 | 115.4 | 113.1 | 92.3 | 84.1 | 153.4 | 194
1765 | 1620 | 152.2 | 62.8 | 115.2 | 113.4 | 91.6 | 83.5 | 153.2 | 193.8
1766 | 1621 | 152 | 62.5 | 115 | 113.1 | 91.5 | 83.2 | 152.9 | 193.5
1767 | 1622 | 151.8 | 62.3 | 114.7 | 112.1 | 91.9 | 82.8 | 152.6 | 193.3
1768 | 1623 | 151.6 | 62.5 | 114.7 | 110.2 | 92 | 82.4 | 152.3 | 193.1
1769 | 1624 | 151.4 | 62.3 | 114.7 | 108.9 | 92.6 | 82 | 152.1 | 192.8
1770 | 1625 | 151.3 | 62.1 | 114.7 | 109 | 92.6 | 82 | 151.8 | 192.6
1771 | 1626 | 151.1 | 62 | 114.2 | 108.8 | 92.9 | 82.1 | 151.5 | 192.4
1772 | 1627 | 150.9 | 61.7 | 113.4 | 109.7 | 93.3 | 82.3 | 151.3 | 192.1
1773 | 1628 | 150.7 | 61.8 | 112.7 | 109.8 | 94 | 82.3 | 151 | 191.8
1774 | 1629 | 150.6 | 61.9 | 112.3 | 109.9 | 94.2 | 81.9 | 150.8 | 191.5
1775 | 1630 | 150.5 | 62.2 | 112.3 | 109.5 | 94.9 | 81.6 | 150.5 | 191.2
1776 | 1631 | 150.3 | 62.3 | 112.2 | 109 | 95.2 | 81.5 | 150.3 | 190.8
1777 | 1632 | 150.1 | 62.1 | 112.1 | 108.3 | 95.2 | 81.5 | 150 | 190.5
1778 | 1633 | 149.9 | 61.7 | 112.2 | 108.2 | 94.6 | 81.4 | 149.8 | 190.3
1779 | 1634 | 149.6 | 61.5 | 111.9 | 107.8 | 94.6 | 81.2 | 149.6 | 190
1780 | 1635 | 149.4 | 61.2 | 111.5 | 107.2 | 94.6 | 81 | 149.3 | 189.7
1781 | 1636 | 149.2 | 60.8 | 111.1 | 106 | 95 | 81.2 | 149.1 | 189.4
1782 | 1637 | 149 | 60.9 | 110.7 | 104.8 | 95.4 | 81.1 | 148.8 | 189.1
1783 | 1638 | 148.8 | 61.1 | 110.4 | 104 | 95.4 | 80.9 | 148.6 | 188.8
1784 | 1639 | 148.7 | 61.1 | 110.1 | 103.9 | 94.7 | 80.6 | 148.3 | 188.5
1785 | 1640 | 148.4 | 60.9 | 110 | 104.6 | 94.4 | 80.5 | 148.1 | 188.1
1786 | 1641 | 148.2 | 61.1 | 109.4 | 104.7 | 94.9 | 80.3 | 147.9 | 187.7
1787 | 1642 | 148.1 | 61.1 | 108.9 | 105.1 | 94.8 | 80 | 147.6 | 187.4
1788 | 1643 | 147.9 | 61 | 108.7 | 104.7 | 94.4 | 80 | 147.4 | 187.1
1789 | 1644 | 147.8 | 60.9 | 108.6 | 104.2 | 94.1 | 79.9 | 147.2 | 186.8
1790 | 1645 | 147.7 | 61 | 108.4 | 103.9 | 94.3 | 79.6 | 146.9 | 186.5
1791 | 1646 | 147.5 | 61.5 | 107.7 | 102.7 | 95 | 79.5 | 146.7 | 186.2
1792 | 1647 | 147.3 | 61.6 | 107.6 | 102.3 | 94.7 | 79.2 | 146.4 | 185.9
1793 | 1648 | 147.2 | 61.5 | 107.3 | 102.1 | 94.1 | 79 | 146.2 | 185.5
1794 | 1649 | 147 | 61.5 | 107.3 | 102.4 | 93.9 | 79.1 | 146 | 185.2
1795 | 1650 | 146.8 | 61.4 | 107.7 | 102.7 | 93.4 | 78.9 | 145.8 | 185.1
1796 | 1651 | 146.6 | 61.9 | 107.1 | 104 | 93.9 | 78.8 | 145.5 | 184.8
1797 | 1652 | 146.4 | 61.8 | 107.5 | 105 | 93.6 | 78.8 | 145.3 | 184.6
1798 | 1653 | 146.2 | 61.8 | 107.5 | 105.3 | 93.7 | 78.7 | 145.1 | 184.3

## Test Facts
Last row in IRMS data sheets: | 15
Time when Penlight power was initiated: | 145