## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 45
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of PE, XLPE, XLPO, EPR, Tefzel & Silicone Rubber insulated control cables (Items 15, 10, 8, 2, 12 & 9). Cable specimens present: Six lengths of cable were monitored for electrical performance, 1 each of PE, XLPE, XLPO, EPR, Tefzel & Silicone Rubber. A seventh length of cable (EPR cable Item #2) was monitored for temperature response. No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 135 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
135 | 0 | Initated Penlight Heating
1031-1067 | 896-932 | Conductors C5 & C6 short together at less than 100 ohms (21); conductors D7 & D8 short together at less than 100 ohms (57) | Tefzel Cable C and EPR Cable D are shorted internally
1266 | 1131 | Cable bundle ignites and burns | NOTE: Cable instrumented with thermocouples did NOT burn (~4" separation distance from 6-cable bundle)
1290 | 1155 | Power to Penlight shutoff
1294-1353 | 1159-1218 | Conductors A1 & A2 short together at less than 100 ohms (27); conductors B3 & B4 short together at less than 100 ohms (11) | XLPE Cable A and PE Cable B are shorted internally
1380-1389 | 1245-1254 | Conductors C5 & C6 both short to ground at much less than 100 ohms (<1 & <1) | Tefzel Cable C shorts to ground
1408-1412 | 1273-1277 | Conductor C5 shorts to conductors E9 & E10 at less than 100 ohms (25 & 12) | Cable to cable interaction occurs after Cable C has shorted internally and to ground
1413-1418 | 1278-1283 | Conductors D7 & D8 both short to ground at less than 100 ohms (4 & <1) | EPR Cable D shorts to ground
1425-1429 | 1290-1294 | Condcutor C6 shorts to conductors E9 & E10 at less than 100 ohms (2 & 8) | Cable to cable interaction occurs after Cable C has shorted internally and to ground
1430-1434 | 1295-1299 | Condcutors E9 & E10 both short to ground at less than 100 ohms (30 & 26) | XLPO Cable E shorts to ground
1440-1454 | 1305-1319 | Conductors D7 & D8 short to conductors E9 & E10 at less than 100 ohms (13, 21, 16 & <1) | Cable to cable interaction occurs after both cables have shorted to ground
1462 | 1327 | Conductors E9 & E10 short together at less than 100 ohms (67) | XLPO Cable E shorts internally
1484-1507 | 1349-1372 | Conductors A1 & A2 both short to ground at less than 1000 ohms (352 & 425) | XLPE Cable A shorts to ground
1510-1513 | 1375-1378 | Conductor A2 shorts to Conductors B3 & B4 at less than 1000 ohms (425 & 509) | Cable to cable interaction occurs after both cables have shorted internally and Cable A has shorted to ground
1515-1518 | 1380-1383 | Conductor A2 shorts to Conductors C5 & C6 at less than 1000 ohms (525 & 543) | Cable to cable interaction occurs after both cables have shorted to ground
1535-1550 | 1400-1415 | Conductors B3 & B4 both short to ground at less than 1000 ohms (986 & 546) | PE Cable B is shorted to ground
Additional Observations
Observation 1 | The silicone rubber cable (F) did not fail either internally or externally.
Observation 2 | It took 896 s (14.9 min.) from the start of Penlight heating for the initial internal short to occur, 1131 s (18.9 min.) for the cable bundle to ignite, and 1245 s (20.8 min.) for the first short to ground.
Observation 3 | No cable to cable interactions took place prior to the individual cables either shorting to ground or shorting internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A = XLPE Cable, Item #10
B = PE Cable, Item #15
C = Tefzel Cable, Item #12
D = EPR Cable, Item #2
E = XLPO Cable, Item #8
F = Silicone Rubber Cable, Item #9
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 45 |  |  | 2006-08-22 | 13:41
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-134.5 | 211201.9994 | -131.5 | 211201.9994 | -129 | 211201.9994 | -126 | 242937.9994 | -123.5 | 244537.9994 | -103.5 | 211201.9994 | -101 | 211201.9994 | -98 | 260137.9994 | -95.5 | 251537.9994 | -75.5 | 211201.9994 | -73 | 251637.9994 | -70 | 255737.9994 | -67.5 | 243737.9994 | -64.5 | 237837.9994 | -61.5 | 243837.9994 | -59 | 256737.9994 | -50.5 | 240537.9994 | -47.5 | 258237.9994 | -45 | 246137.9994 | -42 | 225237.9994 | -39.5 | 235537.9994 | -36.5 | 241137.9994 | -28 | 262138.0762 | -19.5 | 253637.9994 | -17 | 255937.9994 | -14 | 261837.9994 | -11.5 | 259437.9994 | -3 | 256937.9994 | 7.5437e-07 | 240037.9994 | 2.5 | 261637.9994 | 5.5 | 261337.9994 | 8.5 | 250737.9994 | 11 | 121918.9988 | 14 | 254737.9994 | 22.5 | 255537.9994 | 25 | #VALUE! | 33.5 | 257237.9994 | 36.5 | 229637.9994 | 39 | 128418.9988 | 42 | 256737.9994 | 44.5 | 249737.9994 | 47.5 | 211201.9994 | -116.25 | 211201.9994 | -110.75 | 242937.9994 | -60.25 | 240537.9994 | -54.75 | 225237.9994 | -49.125 | 235537.9994 | -9.875 | 240037.9994 | -4.375 | 259437.9994 | 18.125 | #VALUE! | 40.5 | 128418.9988
50.5 | 211201.9994 | 53 | 211201.9994 | 56 | 211201.9994 | 58.5 | 242937.9994 | 61.5 | 244537.9994 | 81 | 211201.9994 | 84 | 211201.9994 | 86.5 | 260137.9994 | 89.5 | 251537.9994 | 109 | 211201.9994 | 112 | 251637.9994 | 114.5 | 255737.9994 | 117.5 | 243737.9994 | 120.5 | 237837.9994 | 123 | 243837.9994 | 126 | 256737.9994 | 134.5 | 240537.9994 | 137 | 258237.9994 | 140 | 246137.9994 | 142.5 | 225237.9994 | 145.5 | 235537.9994 | 148.5 | 241137.9994 | 156.5 | 262337.9994 | 165 | 253637.9994 | 168 | 255937.9994 | 170.5 | 261837.9994 | 173.5 | 259437.9994 | 182 | 256937.9994 | 184.5 | 240037.9994 | 187.5 | 261637.9994 | 190.5 | 261337.9994 | 193 | 250737.9994 | 196 | 243937.9994 | 198.5 | 254737.9994 | 207 | 255537.9994 | 210 | #VALUE! | 218.5 | 257237.9994 | 221 | 229637.9994 | 224 | 256937.9994 | 226.5 | 256737.9994 | 229.5 | 249737.9994 | 232.5 | 211201.9994 | 68.5 | 211201.9994 | 74 | 242937.9994 | 124.5 | 240537.9994 | 130.125 | 225237.9994 | 135.75 | 235537.9994 | 174.875 | 240037.9994 | 180.5 | 259437.9994 | 202.875 | #VALUE! | 225.25 | 229637.9994
235 | 211201.9994 | 238 | 211201.9994 | 240.5 | 211201.9994 | 243.5 | 242937.9994 | 246.5 | 244537.9994 | 265.5 | 211201.9994 | 268.5 | 211201.9994 | 271.5 | 260137.9994 | 274.5 | 251537.9994 | 294 | 211201.9994 | 296.5 | 251637.9994 | 299.5 | 255737.9994 | 302 | 243737.9994 | 305 | 237837.9994 | 308 | 243837.9994 | 310.5 | 128318.9988 | 319 | 240537.9994 | 322 | 258237.9994 | 324.5 | 246137.9994 | 327.5 | 225237.9994 | 330.5 | 235537.9994 | 333 | 241137.9994 | 341.5 | 262337.9994 | 350 | 253637.9994 | 352.5 | 255937.9994 | 355.5 | 261837.9994 | 358.5 | 259437.9994 | 366.5 | 256937.9994 | 369.5 | 240037.9994 | 372.5 | 261637.9994 | 375 | 261337.9994 | 378 | 250737.9994 | 380.5 | 243937.9994 | 383.5 | 254737.9994 | 392 | 255537.9994 | 394.5 | #VALUE! | 403 | 257237.9994 | 405.5 | 229637.9994 | 408.5 | 256937.9994 | 411.5 | 256737.9994 | 414.5 | 249737.9994 | 417 | 211201.9994 | 253.125 | 211201.9994 | 259 | 242937.9994 | 309.25 | 240537.9994 | 314.75 | 225237.9994 | 320.5 | 128318.9988 | 359.625 | 240037.9994 | 365.375 | 259437.9994 | 387.625 | #VALUE! | 410 | 229637.9994
420 | 211201.9994 | 422.5 | 211201.9994 | 425.5 | 211201.9994 | 428.5 | 242937.9994 | 431 | 244537.9994 | 450.5 | 211201.9994 | 453.5 | 211201.9994 | 456.5 | 260137.9994 | 459 | 251537.9994 | 478.5 | 211201.9994 | 481.5 | 251637.9994 | 484.5 | 255737.9994 | 487 | 243737.9994 | 489.5 | 237837.9994 | 492.5 | 243837.9994 | 495.5 | 256737.9994 | 504 | 240537.9994 | 506.5 | 258237.9994 | 509.5 | 246137.9994 | 512 | 225237.9994 | 515 | 235537.9994 | 518 | 241137.9994 | 526.5 | 262337.9994 | 534.5 | 253637.9994 | 537.5 | 255937.9994 | 540 | 261837.9994 | 543 | 259437.9994 | 551.5 | 256937.9994 | 554 | 240037.9994 | 557 | 261637.9994 | 560 | 261337.9994 | 562.5 | 250737.9994 | 565.5 | 243937.9994 | 568.5 | 254737.9994 | 576.5 | 255537.9994 | 580 | #VALUE! | 588 | 257237.9994 | 590.5 | 229637.9994 | 593.5 | 256937.9994 | 596 | 256737.9994 | 599 | 249737.9994 | 602 | 211201.9994 | 438 | 211201.9994 | 443.75 | 242937.9994 | 494.125 | 240537.9994 | 499.5 | 225237.9994 | 505.25 | 235537.9994 | 544.375 | 240037.9994 | 550 | 259437.9994 | 572.625 | #VALUE! | 594.75 | 229637.9994
604.5 | 211201.9994 | 607.5 | 211201.9994 | 610 | 211201.9994 | 613 | 242937.9994 | 616 | 244537.9994 | 635.5 | 211201.9994 | 638.5 | 211201.9994 | 641 | 260137.9994 | 643.5 | 251537.9994 | 663.5 | 211201.9994 | 666 | 251637.9994 | 669 | 255737.9994 | 671.5 | 243737.9994 | 674.5 | 237837.9994 | 677.5 | 243837.9994 | 680.5 | 256737.9994 | 688.5 | 240537.9994 | 691.5 | 258237.9994 | 694.5 | 246137.9994 | 697 | 225237.9994 | 700 | 235537.9994 | 702.5 | 241137.9994 | 711 | 262337.9994 | 719.5 | 253637.9994 | 722 | 255937.9994 | 725 | 261837.9994 | 728 | 259437.9994 | 736 | 256937.9994 | 739 | 240037.9994 | 742 | 261637.9994 | 744.5 | 261337.9994 | 747.5 | 250737.9994 | 750.5 | 243937.9994 | 753 | 254737.9994 | 761.5 | 255537.9994 | 764 | #VALUE! | 772.5 | 257237.9994 | 775.5 | 229637.9994 | 778 | 256937.9994 | 781 | 256737.9994 | 783.5 | 249737.9994 | 786.5 | 211201.9994 | 622.875 | 211201.9994 | 628.375 | 242937.9994 | 678.75 | 240537.9994 | 684.375 | 225237.9994 | 690.125 | 235537.9994 | 729.125 | 240037.9994 | 734.875 | 259437.9994 | 757.25 | #VALUE! | 779.5 | 229637.9994
789.5 | 211201.9994 | 792.5 | 211201.9994 | 795 | 211201.9994 | 797.5 | 242937.9994 | 800.5 | 244537.9994 | 820 | 211201.9994 | 823 | 211201.9994 | 825.5 | 260137.9994 | 828.5 | 251537.9994 | 848 | 211201.9994 | 851 | 251637.9994 | 853.5 | 255737.9994 | 856.5 | 243737.9994 | 859.5 | 237837.9994 | 862 | 243837.9994 | 865 | 256737.9994 | 873.5 | 240537.9994 | 876 | 258237.9994 | 879 | 246137.9994 | 882 | 225237.9994 | 884.5 | 235537.9994 | 887.5 | 241137.9994 | 896 | 21.0651 | 904 | 253338.1182 | 907 | 255638.1172 | 909.5 | 261837.9994 | 912.5 | 259437.9994 | 921 | 256937.9994 | 923.5 | 240037.9994 | 926.5 | 261637.9994 | 929.5 | 261337.9994 | 932 | 56.8353 | 935 | 24244.1144 | 937.5 | 84812.6144 | 946 | 255537.9994 | 949 | #VALUE! | 957.5 | 257237.9994 | 960 | 229637.9994 | 963 | 256937.9994 | 965.5 | 256737.9994 | 968.5 | 249737.9994 | 971.5 | 211201.9994 | 807.625 | 211201.9994 | 813 | 242937.9994 | 863.5 | 240537.9994 | 869.25 | 225237.9994 | 874.75 | 235537.9994 | 913.875 | 240037.9994 | 919.5 | 259437.9994 | 941.875 | #VALUE! | 964.25 | 229637.9994
974 | 211201.9994 | 977 | 211201.9994 | 979.5 | 211201.9994 | 982.5 | 242937.9994 | 985.5 | 244537.9994 | 1005 | 211201.9994 | 1007.5 | 211201.9994 | 1010.5 | 260137.9994 | 1013.5 | 251537.9994 | 1033 | 211201.9994 | 1035.5 | 251637.9994 | 1038.5 | 255737.9994 | 1041.5 | 243737.9994 | 1044 | 237837.9994 | 1047 | 243837.9994 | 1049.5 | 256737.9994 | 1058 | 240537.9994 | 1061 | 258237.9994 | 1063.5 | 246137.9994 | 1066.5 | 225237.9994 | 1069.5 | 235537.9994 | 1072 | 241137.9994 | 1080.5 | 67.8564 | 1089 | 253438.0788 | 1091.5 | 127918.9988 | 1094.5 | 261837.9994 | 1097.5 | 259437.9994 | 1105.5 | 256937.9994 | 1108.5 | 240037.9994 | 1111.5 | 261637.9994 | 1114 | 261337.9994 | 1117 | 116.7237 | 1119.5 | 47987.0925 | 1122.5 | 249741.8063 | 1131 | 1945.0277 | 1133.5 | #VALUE! | 1142 | 257237.9994 | 1145 | 229637.9994 | 1147.5 | 256937.9994 | 1150.5 | 256737.9994 | 1153.5 | 249737.9994 | 1156 | 211201.9994 | 992.25 | 211201.9994 | 998 | 242937.9994 | 1048.25 | 240537.9994 | 1053.875 | 225237.9994 | 1059.5 | 235537.9994 | 1098.625 | 127918.9988 | 1104.375 | 259437.9994 | 1126.625 | #VALUE! | 1149.125 | 229637.9994
1159 | 26.7369 | 1161.5 | 23322.696 | 1164.5 | 70300.6036 | 1167.5 | 242738.0823 | 1170 | 244537.9994 | 1189.5 | 211201.9994 | 1192.5 | 211201.9994 | 1195.5 | 260137.9994 | 1198 | 251537.9994 | 1217.5 | 11.0418 | 1220.5 | 27815.5446 | 1223.5 | 127669.0586 | 1226 | 67410.3021 | 1229 | 79212.6648 | 1231.5 | 60884.4976 | 1234.5 | 128318.9988 | 1243 | 120218.9988 | 1245.5 | 64484.4976 | 1248.5 | 61459.4976 | 1251.5 | 56234.4976 | 1254 | 58809.4976 | 1257 | 80312.6648 | 1265.5 | 26.704 | 1273.5 | 25.3923 | 1276.5 | 12.2167 | 1279.5 | 1535.0642 | 1282 | 10821.2965 | 1290.5 | 1.8343 | 1293.5 | 8.2138 | 1296 | 1535.0619 | 1299 | 1535.6469 | 1301.5 | 2.3923 | 1304.5 | 13.0001 | 1307.5 | 20.7151 | 1315.5 | 16.2069 | 1318.5 | #VALUE! | 1327 | 66.5523 | 1329.5 | 13233.0535 | 1332.5 | 87900.9572 | 1335.5 | 73423.4718 | 1338 | 78911.4572 | 1341 | 70333.9982 | 1177 | 23322.696 | 1182.75 | 242738.0823 | 1233.125 | 27815.5446 | 1238.75 | 56234.4976 | 1244.25 | 58809.4976 | 1283.5 | 1.8343 | 1289.125 | 1535.0619 | 1311.5 | #VALUE! | 1333.875 | 13233.0535
1343.5 | 15.8849 | 1346.5 | 25148.243 | 1349.5 | 99861.5287 | 1352 | 2463.9677 | 1355 | 39546.3552 | 1374.5 | 425.3814 | 1377.5 | 508.7276 | 1380 | 525.3181 | 1383 | 543.3367 | 1402.5 | 18.895 | 1405.5 | 8766.6497 | 1408 | 3068.7931 | 1411 | 1255.3636 | 1413.5 | 2543.7006 | 1416.5 | 3540.8248 | 1419.5 | 2468.3189 | 1427.5 | 1251.7902 | 1430.5 | 1475.1316 | 1433.5 | 2201.2244 | 1436 | 1702.6277 | 1439 | 1502.8898 | 1441.5 | 1799.4343 | 1450 | 20.3512 | 1458.5 | 15.1167 | 1461.5 | 22.125 | 1464 | 41374.7209 | 1467 | 1535.6296 | 1475.5 | 0.75756 | 1478 | 13.8454 | 1481 | 37366.4819 | 1483.5 | 28394.4899 | 1486.5 | 0.74091 | 1489.5 | 2.0096 | 1492 | 5.0322 | 1500.5 | 0.85363 | 1503.5 | #VALUE! | 1511.5 | 6.0314 | 1514.5 | 32181.87 | 1517.5 | 41373.5146 | 1520 | 13916.2929 | 1523 | 45982.7186 | 1525.5 | 70333.9982 | 1362 | 425.3814 | 1367.5 | 525.3181 | 1417.875 | 1251.7902 | 1423.5 | 1255.3636 | 1429.125 | 1502.8898 | 1468.375 | 0.75756 | 1473.875 | 1535.6296 | 1496.375 | #VALUE! | 1518.75 | 13916.2929
1528.5 | 0.82394 | 1531.5 | 610.0325 | 1534 | 387.7627 | 1537 | 13453.2745 | 1539.5 | 6651.5204 | 1559.5 | 425.3405 | 1562 | 323.0237 | 1565 | 64558.5539 | 1567.5 | 19256.7613 | 1587.5 | 25.5758 | 1590 | 208.5195 | 1593 | 14994.6423 | 1595.5 | 42190.7473 | 1598.5 | 14771.1152 | 1601.5 | 24293.7939 | 1604 | 5607.4836 | 1612.5 | 4048.8956 | 1615.5 | 28604.2167 | 1618 | 35076.8529 | 1621 | 32091.1386 | 1623.5 | 29354.7451 | 1626.5 | 48147.5969 | 1635 | 0.2935 | 1643.5 | 0.88933 | 1646 | 17.0512 | 1649 | 12518.8535 | 1651.5 | 24799.7197 | 1660 | 14.3748 | 1662.5 | 0.72641 | 1665.5 | 20207.0714 | 1668.5 | 39277.8129 | 1671.5 | 13.0952 | 1674 | 11.5033 | 1677 | 3.8717 | 1685.5 | 27.7698 | 1688 | #VALUE! | 1696.5 | 28.6937 | 1699.5 | 19304.3303 | 1702 | 1535.6066 | 1705 | 49580.0203 | 1707.5 | 40389.4429 | 1710.5 | 70333.9982 | 1546.75 | 323.0237 | 1552.25 | 6651.5204 | 1602.75 | 208.5195 | 1608.25 | 14771.1152 | 1613.875 | 5607.4836 | 1653 | 0.72641 | 1658.625 | 12518.8535 | 1681.125 | #VALUE! | 1703.5 | 1535.6066
1713.5 | 4.0348 | 1716 | 897.4815 | 1719 | 623.2525 | 1721.5 | 15198.1686 | 1724.5 | 8707.9025 | 1744 | 261.7696 | 1747 | 751.1659 | 1749.5 | 1678.3442 | 1752.5 | 41839.663 | 1772 | 26.4921 | 1774.5 | 6819.7895 | 1777.5 | 822.9511 | 1780.5 | 56960.4323 | 1783 | 59384.4976 | 1786 | 60884.4976 | 1788.5 | 50259.7123 | 1797.5 | 60059.4976 | 1800 | 64484.4976 | 1803 | 49147.5969 | 1805.5 | 75012.6648 | 1808.5 | 5022.5371 | 1811.5 | 80312.6648 | 1819.5 | 0.57068 | 1828 | 6.0753 | 1830.5 | 18.6775 | 1833.5 | 11620.2279 | 1836.5 | 39492.298 | 1844.5 | 11.7459 | 1847.5 | 1.9559 | 1850.5 | 35483.6892 | 1853 | 71655.6807 | 1856 | 21.2292 | 1859 | 4.9805 | 1861.5 | 26.3912 | 1870 | 75.051 | 1873 | #VALUE! | 1881 | 29.0254 | 1884 | 15810.4242 | 1887 | 52156.7077 | 1889.5 | 1536.2035 | 1892.5 | 5029.934 | 1895 | 70333.9982 | 1731.5 | 261.7696 | 1737 | 1678.3442 | 1787.375 | 822.9511 | 1793 | 49147.5969 | 1798.625 | 5022.5371 | 1837.625 | 1.9559 | 1843.375 | 11620.2279 | 1865.875 | #VALUE! | 1888.25 | 1536.2035
1897 | 17.5793 | 1901 | 2725.1252 | 1903.5 | 2350.4878 | 1906.5 | 175555.0414 | 1909.5 | 81445.9982 | 1928.5 | 25988.3745 | 1931.5 | 7328.8845 | 1934.5 | 86645.9982 | 1937.5 | 62809.4976 | 1956.5 | 20.4639 | 1959.5 | 3466.0059 | 1962.5 | 39167.0054 | 1965 | 87794.1427 | 1968 | 79212.6648 | 1971 | 81212.6648 | 1973.5 | 64109.4976 | 1982 | 80112.6648 | 1985 | 64484.4976 | 1987.5 | 61459.4976 | 1990.5 | 9289.0687 | 1993 | 78445.9982 | 1996 | 80312.6648 | 2004.5 | 28.8166 | 2013 | 15.9879 | 2015.5 | 28.6993 | 2018.5 | 20806.1787 | 2021.5 | 59346.3941 | 2029.5 | 17.7919 | 2032.5 | 4.4963 | 2035.5 | 56351.7489 | 2038 | 40575.8239 | 2040.5 | 28.7896 | 2043.5 | 23.8278 | 2046.5 | 16.4414 | 2054.5 | 43.6772 | 2057.5 | #VALUE! | 2066 | 0.68008 | 2069 | 1535.3222 | 2071.5 | 18309.4626 | 2074.5 | 16911.6207 | 2077 | 1535.5376 | 2080 | 70333.9982 | 1916.125 | 2350.4878 | 1922 | 62809.4976 | 1972.25 | 3466.0059 | 1977.75 | 9289.0687 | 1983.375 | 64109.4976 | 2022.625 | 4.4963 | 2028.375 | 20806.1787 | 2050.5 | #VALUE! | 2073 | 1535.3222
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 45 |  |  | 2006-08-22 | 13:41
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-128.9 | 211202 |  | -106.5 | 211202 | -78.4444 | 211202 | -62.9444 | 211202 | -48.6111 | 240538 | -39.9444 | 240038 | -15.8 | 121919 | -10.1 | #VALUE! | 2.1111 | 128419 | 5.1667 | #VALUE! | 22.9 | 211202 | 25 | 211202 | -128.9 | 211202 | -78.4444 | #VALUE! | -48.6111 | #VALUE! | -41.8222 | #VALUE! | -33.5278 | #VALUE! | -4.6556 | #VALUE! | -20.3194 | #VALUE! | -10.1639 | 211202 | 13.7944 | #VALUE! | -117.7 | 211202 | -70.6944 | 211202 | -44.2778 | 240038 | -12.95 | #VALUE! | 3.6389 | #VALUE! | 23.95 | 211202
55.9 | 211202 |  | 78.3 | 211202 | 106.2778 | 211202 | 121.8889 | 211202 | 136.1111 | 240538 | 144.8333 | 240038 | 169 | 243738 | 174.6 | #VALUE! | 186.8889 | 229638 | 190 | #VALUE! | 207.6 | 211202 | 210 | 211202 | 55.9 | 211202 | 106.2778 | #VALUE! | 136.1111 | #VALUE! | 142.9417 | #VALUE! | 151.2639 | #VALUE! | 180.1222 | #VALUE! | 164.4583 | #VALUE! | 174.6361 | 211202 | 198.6222 | #VALUE! | 67.1 | 211202 | 114.0833 | 211202 | 140.4722 | 240038 | 171.8 | #VALUE! | 188.4444 | #VALUE! | 208.8 | 211202
240.7 | 211202 |  | 263 | 211202 | 291 | 128319 | 306.6111 | 211202 | 320.9444 | 240538 | 329.7222 | 240038 | 353.7 | 243738 | 359.4 | #VALUE! | 371.6111 | 229638 | 374.7222 | #VALUE! | 392.4 | 211202 | 394.7 | 211202 | 240.7 | 128319 | 291 | #VALUE! | 320.9444 | #VALUE! | 327.6778 | #VALUE! | 335.9861 | #VALUE! | 364.8583 | #VALUE! | 349.25 | #VALUE! | 359.4417 | 211202 | 383.3583 | #VALUE! | 251.85 | 211202 | 298.8056 | 128319 | 325.3333 | 240038 | 356.55 | #VALUE! | 373.1667 | #VALUE! | 393.55 | 211202
425.5 | 211202 |  | 447.9 | 211202 | 475.7778 | 211202 | 491.3889 | 211202 | 505.7778 | 240538 | 514.4444 | 240038 | 538.6 | 243738 | 544.1 | #VALUE! | 556.3889 | 229638 | 559.6111 | #VALUE! | 577.1 | 211202 | 579.5 | 211202 | 425.5 | 211202 | 475.7778 | #VALUE! | 505.7778 | #VALUE! | 512.4667 | #VALUE! | 520.7917 | #VALUE! | 549.675 | #VALUE! | 534.0556 | #VALUE! | 544.2056 | 211202 | 568.15 | #VALUE! | 436.7 | 211202 | 483.5833 | 211202 | 510.1111 | 240038 | 541.35 | #VALUE! | 558 | #VALUE! | 578.3 | 211202
610.2 | 211202 |  | 632.6 | 211202 | 660.6111 | 211202 | 676.2222 | 211202 | 690.4444 | 121419 | 699.1667 | 240038 | 723.4 | 243738 | 728.9 | #VALUE! | 741.2222 | 229638 | 744.2222 | #VALUE! | 762 | 211202 | 764.1 | 211202 | 610.2 | 121419 | 660.6111 | #VALUE! | 690.4444 | #VALUE! | 697.2833 | #VALUE! | 705.5694 | #VALUE! | 734.4361 | #VALUE! | 718.7639 | #VALUE! | 728.9278 | 121419 | 752.8861 | #VALUE! | 621.4 | 211202 | 668.4167 | 211202 | 694.8056 | 121419 | 726.15 | #VALUE! | 742.7222 | #VALUE! | 763.05 | 211202
795 | 211202 |  | 817.3 | 211202 | 845.3333 | 211202 | 860.9444 | 211202 | 875.1667 | 53916.6549 | 883.8889 | 7198.4409 | 908 | 2765.2502 | 913.7 | #VALUE! | 925.8889 | 81669.5659 | 929 | #VALUE! | 946.6 | 211202 | 949 | 211202 | 795 | 7198.4409 | 845.3333 | #VALUE! | 875.1667 | #VALUE! | 881.9944 | #VALUE! | 890.2917 | #VALUE! | 919.1472 | #VALUE! | 903.4861 | #VALUE! | 913.6639 | 7198.4409 | 937.6222 | #VALUE! | 806.15 | 211202 | 853.1389 | 211202 | 879.5278 | 7198.4409 | 910.85 | #VALUE! | 927.4444 | #VALUE! | 947.8 | 211202
979.7 | 211202 |  | 1002.1 | 211202 | 1030.1111 | 211202 | 1045.6111 | 211202 | 1059.9444 | 7636.4855 | 1068.7222 | 12597.188 | 1092.8 | 2183.4542 | 1098.4 | #VALUE! | 1110.6667 | 229638 | 1113.7222 | #VALUE! | 1131.5 | 211202 | 1133.7 | 211202 | 979.7 | 7636.4855 | 1030.1111 | #VALUE! | 1059.9444 | #VALUE! | 1066.7306 | #VALUE! | 1075.0278 | #VALUE! | 1103.8972 | #VALUE! | 1088.2639 | #VALUE! | 1098.4667 | 7636.4855 | 1122.3972 | #VALUE! | 990.9 | 211202 | 1037.8611 | 211202 | 1064.3333 | 7636.4855 | 1095.6 | #VALUE! | 1112.1944 | #VALUE! | 1132.6 | 211202
1164.5 | 4832.6563 |  | 1186.9 | 15578.4359 | 1214.8333 | 1196.5494 | 1230.4444 | 14316.6698 | 1244.8333 | 0.62952 | 1253.5 | 0.62807 | 1277.6 | 3.8667 | 1283.2 | #VALUE! | 1295.3889 | 30.3796 | 1298.6667 | #VALUE! | 1316.3 | 50037.0892 | 1318.5 | 52725.5 | 1164.5 | 0.62807 | 1214.8333 | #VALUE! | 1244.8333 | #VALUE! | 1251.5194 | #VALUE! | 1259.8333 | #VALUE! | 1288.7139 | #VALUE! | 1273.0972 | #VALUE! | 1283.2833 | 0.62807 | 1307.2139 | #VALUE! | 1175.7 | 4832.6563 | 1222.6389 | 1196.5494 | 1249.1667 | 0.62807 | 1280.4 | #VALUE! | 1297.0278 | #VALUE! | 1317.4 | 50037.0892
1349.3 | 351.805 |  | 1371.7 | 425.6269 | 1399.7222 | 986.016 | 1415.2778 | 546.1835 | 1429.5556 | 0.63538 | 1438.2778 | 0.6381 | 1462.5 | 0.66966 | 1468 | #VALUE! | 1480.3333 | 0.64488 | 1483.3889 | #VALUE! | 1501 | 52247.6 | 1503.3 | 64159.5 | 1349.3 | 0.63538 | 1399.7222 | #VALUE! | 1429.5556 | #VALUE! | 1436.375 | #VALUE! | 1444.6806 | #VALUE! | 1473.5556 | #VALUE! | 1457.8889 | #VALUE! | 1468.0333 | 0.63538 | 1492.0056 | #VALUE! | 1360.5 | 351.805 | 1407.5 | 546.1835 | 1433.9167 | 0.63538 | 1465.25 | #VALUE! | 1481.8611 | #VALUE! | 1502.15 | 52247.6
1534.1 | 392.1203 |  | 1556.5 | 871.0794 | 1584.5556 | 207.2763 | 1600.0556 | 1469.6423 | 1614.3889 | 0.64974 | 1623 | 0.6552 | 1647.2 | 5.3485 | 1652.9 | #VALUE! | 1665.1111 | 0.6416 | 1668.1111 | #VALUE! | 1685.9 | 57334.5 | 1688 | 64159.5 | 1534.1 | 0.64974 | 1584.5556 | #VALUE! | 1614.3889 | #VALUE! | 1621.1778 | #VALUE! | 1629.4583 | #VALUE! | 1658.3306 | #VALUE! | 1642.6528 | #VALUE! | 1652.8222 | 0.64974 | 1676.7806 | #VALUE! | 1545.3 | 392.1203 | 1592.3056 | 207.2763 | 1618.6944 | 0.64974 | 1650.05 | #VALUE! | 1666.6111 | #VALUE! | 1686.95 | 57334.5
1718.9 | 51.911 |  | 1741.3 | 48.0225 | 1769.1111 | 771.0244 | 1784.8889 | 1758.9361 | 1799 | 0.65012 | 1807.7222 | 0.64878 | 1832 | 4.2939 | 1837.5 | #VALUE! | 1849.7778 | 0.64135 | 1852.8333 | #VALUE! | 1870.5 | 57334.5 | 1872.8 | 62359.5 | 1718.9 | 0.64878 | 1769.1111 | #VALUE! | 1799 | #VALUE! | 1805.875 | #VALUE! | 1814.1528 | #VALUE! | 1843.0278 | #VALUE! | 1827.3333 | #VALUE! | 1837.5056 | 0.64878 | 1861.4778 | #VALUE! | 1730.1 | 48.0225 | 1777 | 771.0244 | 1803.3611 | 0.64878 | 1834.75 | #VALUE! | 1851.3056 | #VALUE! | 1871.65 | 57334.5
1903.5 | 268.3105 |  | 1925.8 | 553.3354 | 1953.9444 | 350.6151 | 1969.5 | 475.2621 | 1983.9444 | 8.6916 | 1992.7222 | 0.67407 | 2016.6 | 14.8498 | 2022.2 | #VALUE! | 2034.5556 | 0.71842 | 2037.6667 | #VALUE! | 2055.5 | 57334.5 | 2057.6 | 62359.5 | 1903.5 | 0.67407 | 1953.9444 | #VALUE! | 1983.9444 | #VALUE! | 1990.5611 | #VALUE! | 1998.9167 | #VALUE! | 2027.7556 | #VALUE! | 2012.2222 | #VALUE! | 2022.4417 | 0.67407 | 2046.3306 | #VALUE! | 1914.65 | 268.3105 | 1961.7222 | 350.6151 | 1988.3333 | 0.67407 | 2019.4 | #VALUE! | 2036.1111 | #VALUE! | 2056.55 | 57334.5
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38951.5713 | 1 | 0 | 38951.5713 | 1 | 0 |  | 47.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5734 | 1 | 0 | 38951.5734 | 1 | 0 |  | 232.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5756 | 1 | 0 | 38951.5756 | 1 | 0 |  | 417 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5777 | 1 | 0 | 38951.5777 | 1 | 0 |  | 602 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5798 | 1 | 0 | 38951.5798 | 1 | 0 |  | 786.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.582 | 1 | 0 | 38951.582 | 1 | 0 |  | 971.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5841 | 1 | 0 | 38951.5841 | 1 | 0 |  | 1156 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5863 | 3 | 0 | 38951.5863 | 4 | 0 |  | 1341 | 1476 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982
38951.5884 | 3 | 0 | 38951.5884 | 3 | 0 |  | 1525.5 | 1660.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38951.5905 | 3 | 0 | 38951.5905 | 3 | 0 |  | 1710.5 | 1845.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38951.5927 | 3 | 0 | 38951.5927 | 3 | 0 |  | 1895 | 2030 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38951.5948 | 3 | 0 | 38951.5948 | 3 | 0 |  | 2080 | 2215 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982

## E10-F12
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 152.5263 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38951.5713 | 1 | 0 | 38951.5713 | 1 | 0 |  | 44.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5734 | 1 | 0 | 38951.5734 | 1 | 0 |  | 229.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5755 | 1 | 0 | 38951.5755 | 1 | 0 |  | 414.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5777 | 1 | 0 | 38951.5777 | 1 | 0 |  | 599 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5798 | 1 | 0 | 38951.5798 | 1 | 0 |  | 783.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5819 | 1 | 0 | 38951.582 | 1 | 0 |  | 968.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5841 | 1 | 0 | 38951.5841 | 1 | 0 |  | 1153.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249738 | 249738 | 249737.9994
38951.5862 | 1707 | 1 | 38951.5862 | 4 | 0 |  | 1338 | 1473 | 104.2125 | 0.06105 | 0.2442 | 0 | 1.0421 | 0.0006105 | 0.002442 | 0 | 1.0415 | 0.002442 | 46.3881 | 62359.5 | 78911.4572
38951.5884 | 2037 | 1 | 38951.5884 | 3 | 0 |  | 1523 | 1658 | 124.359 | 0.06105 | 0.18315 | 0 | 1.2436 | 0.0006105 | 0.0018315 | 0 | 1.243 | 0.0018315 | 22.6611 | 83179.3333 | 45982.7186
38951.5905 | 2093 | 1 | 38951.5905 | 3 | 0 |  | 1707.5 | 1842.5 | 127.7778 | 0.06105 | 0.18315 | 0 | 1.2778 | 0.0006105 | 0.0018315 | 0 | 1.2772 | 0.0018315 | 19.3776 | 83179.3334 | 40389.4429
38951.5926 | 2447 | 1 | 38951.5927 | 4 | 0 |  | 1892.5 | 2027.5 | 149.3895 | 0.06105 | 0.2442 | 0 | 1.4939 | 0.0006105 | 0.002442 | 0 | 1.4933 | 0.002442 | 2.1006 | 62359.5 | 5029.934
38951.5948 | 2482 | 1 | 38951.5948 | 4 | 0 |  | 2077 | 2212 | 151.5263 | 0.06105 | 0.2442 | 0 | 1.5153 | 0.0006105 | 0.002442 | 0 | 1.5147 | 0.002442 | 0.66022 | 62359.5 | 1535.5376

## E10-F11
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.7998 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38951.5712 | 1 | 0 | 38951.5712 | 1 | 0 |  | 42 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5734 | 1 | 0 | 38951.5734 | 1 | 0 |  | 226.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5755 | 1 | 0 | 38951.5755 | 1 | 0 |  | 411.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5776 | 1 | 0 | 38951.5777 | 1 | 0 |  | 596 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5798 | 1 | 0 | 38951.5798 | 1 | 0 |  | 781 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5819 | 1 | 0 | 38951.5819 | 1 | 0 |  | 965.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5841 | 1 | 0 | 38951.5841 | 1 | 0 |  | 1150.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5862 | 1832 | 1 | 38951.5862 | 4 | 0 |  | 1335.5 | 1470.5 | 111.8437 | 0.06105 | 0.2442 | 0 | 1.1184 | 0.0006105 | 0.002442 | 0 | 1.1178 | 0.002442 | 40.2174 | 64109.5 | 73423.4718
38951.5883 | 2428 | 1 | 38951.5883 | 4 | 0 |  | 1520 | 1655 | 148.2295 | 0.06105 | 0.2442 | 0 | 1.4823 | 0.0006105 | 0.002442 | 0 | 1.4817 | 0.002442 | 5.7841 | 64109.5 | 13916.2929
38951.5905 | 2071 | 1 | 38951.5905 | 3 | 0 |  | 1705 | 1840 | 126.4347 | 0.06105 | 0.18315 | 0 | 1.2643 | 0.0006105 | 0.0018315 | 0 | 1.2637 | 0.0018315 | 24.028 | 85512.6667 | 49580.0203
38951.5926 | 2552 | 1 | 38951.5926 | 3 | 0 |  | 1889.5 | 2024.5 | 155.7998 | 0.06105 | 0.18315 | 0 | 1.558 | 0.0006105 | 0.0018315 | 0 | 1.5574 | 0.0018315 | 0.6421 | 85512.6667 | 1536.2035
38951.5947 | 2398 | 1 | 38951.5948 | 4 | 0 |  | 2074.5 | 2209.5 | 146.398 | 0.06105 | 0.2442 | 0 | 1.464 | 0.0006105 | 0.002442 | 0 | 1.4634 | 0.002442 | 7.1081 | 64109.5 | 16911.6207

## E9-F12
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.9219 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38951.5712 | 2 | 0 | 38951.5712 | 1 | 0 |  | 39 | 174 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128419 | 256938 | 128418.9988
38951.5733 | 1 | 0 | 38951.5733 | 1 | 0 |  | 224 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5755 | 1 | 0 | 38951.5755 | 1 | 0 |  | 408.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5776 | 1 | 0 | 38951.5776 | 1 | 0 |  | 593.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5797 | 1 | 0 | 38951.5798 | 1 | 0 |  | 778 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5819 | 1 | 0 | 38951.5819 | 1 | 0 |  | 963 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.584 | 1 | 0 | 38951.584 | 1 | 0 |  | 1147.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5862 | 1690 | 1 | 38951.5862 | 4 | 1 |  | 1332.5 | 1467.5 | 103.1746 | 0.06105 | 0.2442 | 0.06105 | 1.0317 | 0.0006105 | 0.002442 | 0.0006105 | 1.0311 | 0.0018315 | 52.1243 | 237295.8413 | 87900.9572
38951.5883 | 2155 | 1 | 38951.5883 | 4 | 0 |  | 1517.5 | 1652.5 | 131.5629 | 0.06105 | 0.2442 | 0 | 1.3156 | 0.0006105 | 0.002442 | 0 | 1.315 | 0.002442 | 19.2841 | 64159.5 | 41373.5146
38951.5904 | 2554 | 1 | 38951.5905 | 4 | 0 |  | 1702 | 1837 | 155.9219 | 0.06105 | 0.2442 | 0 | 1.5592 | 0.0006105 | 0.002442 | 0 | 1.5586 | 0.002442 | 0.6416 | 64159.5 | 1535.6066
38951.5926 | 2047 | 1 | 38951.5926 | 4 | 0 |  | 1887 | 2022 | 124.9695 | 0.06105 | 0.2442 | 0 | 1.2497 | 0.0006105 | 0.002442 | 0 | 1.2491 | 0.002442 | 25.5807 | 64159.5 | 52156.7077
38951.5947 | 2386 | 1 | 38951.5947 | 4 | 0 |  | 2071.5 | 2206.5 | 145.6654 | 0.06105 | 0.2442 | 0 | 1.4567 | 0.0006105 | 0.002442 | 0 | 1.456 | 0.002442 | 7.7308 | 64159.5 | 18309.4626

## E9-F11
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 140.2552 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38951.5712 | 1 | 0 | 38951.5712 | 1 | 0 |  | 36.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5733 | 1 | 0 | 38951.5733 | 1 | 0 |  | 221 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5754 | 1 | 0 | 38951.5754 | 1 | 0 |  | 405.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5776 | 1 | 0 | 38951.5776 | 1 | 0 |  | 590.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5797 | 1 | 0 | 38951.5797 | 1 | 0 |  | 775.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5818 | 1 | 0 | 38951.5819 | 1 | 0 |  | 960 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.584 | 1 | 0 | 38951.584 | 1 | 0 |  | 1145 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229638 | 229638 | 229637.9994
38951.5861 | 1763 | 4 | 38951.5861 | 4 | 2 |  | 1329.5 | 1464.5 | 107.6313 | 0.2442 | 0.2442 | 0.1221 | 1.0763 | 0.002442 | 0.002442 | 0.001221 | 1.0739 | 0.001221 | 30.3796 | 50037.0892 | 13233.0535
38951.5883 | 1974 | 1 | 38951.5883 | 4 | 0 |  | 1514.5 | 1649.5 | 120.5128 | 0.06105 | 0.2442 | 0 | 1.2051 | 0.0006105 | 0.002442 | 0 | 1.2045 | 0.002442 | 16.3903 | 57334.5 | 32181.87
38951.5904 | 2103 | 1 | 38951.5904 | 4 | 0 |  | 1699.5 | 1834.5 | 128.3883 | 0.06105 | 0.2442 | 0 | 1.2839 | 0.0006105 | 0.002442 | 0 | 1.2833 | 0.002442 | 9.2474 | 57334.5 | 19304.3303
38951.5925 | 2138 | 1 | 38951.5926 | 4 | 0 |  | 1884 | 2019 | 130.525 | 0.06105 | 0.2442 | 0 | 1.3053 | 0.0006105 | 0.002442 | 0 | 1.3046 | 0.002442 | 7.4581 | 57334.5 | 15810.4242
38951.5947 | 2281 | 1 | 38951.5947 | 4 | 0 |  | 2069 | 2204 | 139.2552 | 0.06105 | 0.2442 | 0 | 1.3926 | 0.0006105 | 0.002442 | 0 | 1.3919 | 0.002442 | 0.71842 | 57334.5 | 1535.3222

## E9-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 157.105 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38951.5711 | 1 | 0 | 38951.5711 | 1 | 0 |  | 33.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5733 | 1 | 0 | 38951.5733 | 1 | 0 |  | 218.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5754 | 1 | 0 | 38951.5754 | 1 | 0 |  | 403 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5775 | 1 | 0 | 38951.5776 | 1 | 0 |  | 588 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5797 | 1 | 0 | 38951.5797 | 1 | 0 |  | 772.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5818 | 1 | 0 | 38951.5818 | 1 | 0 |  | 957.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5839 | 1 | 0 | 38951.584 | 1 | 0 |  | 1142 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
38951.5861 | 1176 | 722 | 38951.5861 | 1321 | 729 |  | 1327 | 1462 | 71.7949 | 44.0781 | 80.6471 | 44.5055 | 0.71795 | 0.44078 | 0.80647 | 0.44505 | 0.27717 | 0.36142 | 866.9191 | 246.5756 | 66.5523
38951.5882 | 2394 | 0 | 38951.5882 | 2173 | 0 |  | 1511.5 | 1646.5 | 146.1538 | 0 | 132.6618 | 0 | 1.4615 | 0 | 1.3266 | 0 | 1.4615 | 1.3266 | 7.4929 | 18.4252 | 6.0314
38951.5904 | 1981 | 0 | 38951.5904 | 2557 | 0 |  | 1696.5 | 1831.5 | 120.9402 | 0 | 156.105 | 0 | 1.2094 | 0 | 1.5611 | 0 | 1.2094 | 1.5611 | 29.9031 | 0.64059 | 28.6937
38951.5925 | 1976 | 0 | 38951.5925 | 2052 | 0 |  | 1881 | 2016 | 120.6349 | 0 | 125.2747 | 0 | 1.2063 | 0 | 1.2527 | 0 | 1.2063 | 1.2527 | 30.2318 | 25.4084 | 29.0254
38951.5946 | 2551 | 0 | 38951.5947 | 2498 | 0 |  | 2066 | 2201 | 155.7387 | 0 | 152.5031 | 0 | 1.5574 | 0 | 1.525 | 0 | 1.5574 | 1.525 | 0.8773 | 3.0176 | 0.68008

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 45 |  |  | 2006-08-22 | 13:41
38951.5692 | 1 | 0 | 1 | TS/TP Mix | 7-C | Tray
38951.5713 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38951.5734 | 1 | 0 | 1
38951.5756 | 1 | 0 | 1
38951.5777 | 1 | 0 | 1
38951.5799 | 1 | 0 | 1
38951.582 | 1 | 0 | 1
38951.5841 | 948 | 918 | 1
38951.5863 | 1020 | 915 | 1
38951.5884 | 1122 | 982 | 1
38951.5906 | 1037 | 957 | 1
38951.5927 | 1235 | 1108 | 1
1
38951.5692 | 1 | 0 | 2
38951.5713 | 1 | 1 | 2
38951.5735 | 1 | 0 | 2
38951.5756 | 1 | 0 | 2
38951.5777 | 1 | 0 | 2
38951.5799 | 1 | 0 | 2
38951.582 | 1 | 0 | 2
38951.5842 | 1052 | 1024 | 2
38951.5863 | 1251 | 1125 | 2
38951.5884 | 1036 | 924 | 2
38951.5906 | 1102 | 1096 | 2
2
38951.5692 | 1 | 0 | 3
38951.5713 | 1 | 0 | 3
38951.5735 | 1 | 0 | 3
38951.5756 | 1 | 0 | 3
38951.5778 | 1 | 0 | 3
38951.5799 | 1 | 0 | 3
38951.582 | 1 | 0 | 3
38951.5842 | 3 | 9 | 3
38951.5863 | 93 | 8 | 3
38951.5885 | 404 | 234 | 3
38951.5906 | 222 | 182 | 3
38951.5927 | 109 | 70 | 3
3
38951.5692 | 1 | 0 | 4
38951.5714 | 1 | 0 | 4
38951.5735 | 1 | 0 | 4
38951.5756 | 1 | 0 | 4
38951.5778 | 1 | 0 | 4
38951.5799 | 1 | 0 | 4
38951.5821 | 1 | 0 | 4
38951.5842 | 2 | 4 | 4
38951.5863 | 4 | 4 | 4
38951.5885 | 315 | 233 | 4
38951.5906 | 316 | 229 | 4
38951.5928 | 53 | 24 | 4
4
38951.5692 | 1 | 0 | 5
38951.5714 | 1 | 0 | 5
38951.5735 | 1 | 0 | 5
38951.5757 | 1 | 0 | 5
38951.5778 | 1 | 0 | 5
38951.5799 | 1 | 0 | 5
38951.5821 | 1 | 0 | 5
38951.5842 | 1 | 3 | 5
38951.5864 | 111 | 2 | 5
38951.5885 | 491 | 319 | 5
38951.5906 | 277 | 242 | 5
38951.5928 | 86 | 82 | 5
5
38951.5693 | 1 | 0 | 6
38951.5714 | 1 | 0 | 6
38951.5735 | 1 | 0 | 6
38951.5757 | 1 | 0 | 6
38951.5778 | 1 | 0 | 6
38951.58 | 1 | 0 | 6
38951.5821 | 1 | 0 | 6
38951.5842 | 2 | 2 | 6
38951.5864 | 4 | 1 | 6
38951.5885 | 442 | 322 | 6
38951.5906 | 419 | 319 | 6
38951.5928 | 38 | 19 | 6
6
38951.5693 | 1 | 0 | 7
38951.5714 | 1 | 0 | 7
38951.5736 | 1 | 0 | 7
38951.5757 | 1 | 0 | 7
38951.5778 | 1 | 0 | 7
38951.58 | 1 | 0 | 7
38951.5821 | 1 | 0 | 7
38951.5842 | 1 | 1 | 7
38951.5864 | 121 | 1 | 7
38951.5885 | 118 | 3 | 7
38951.5907 | 5 | 3 | 7
38951.5928 | 3 | 1 | 7
7
38951.5693 | 1 | 0 | 8
38951.5714 | 1 | 0 | 8
38951.5736 | 1 | 0 | 8
38951.5757 | 1 | 0 | 8
38951.5778 | 2 | 0 | 8
38951.58 | 1 | 0 | 8
38951.5821 | 1 | 0 | 8
38951.5843 | 1 | 1 | 8
38951.5864 | 2414 | 1 | 8
38951.5885 | 2006 | 2 | 8
38951.5907 | 2065 | 2 | 8
38951.5928 | 1979 | 1 | 8
8
38951.5693 | 1 | 0 | 9
38951.5714 | 1 | 0 | 9
38951.5736 | 1 | 0 | 9
38951.5757 | 1 | 0 | 9
38951.5779 | 1 | 0 | 9
38951.58 | 1 | 0 | 9
38951.5821 | 1 | 0 | 9
38951.5843 | 1 | 0 | 9
38951.5864 | 144 | 1 | 9
38951.5886 | 101 | 1 | 9
38951.5907 | 36 | 1 | 9
38951.5928 | 3 | 0 | 9
9
38951.5693 | 1 | 0 | 10
38951.5715 | 1 | 0 | 10
38951.5736 | 1 | 0 | 10
38951.5757 | 1 | 0 | 10
38951.5779 | 1 | 0 | 10
38951.58 | 1 | 0 | 10
38951.5822 | 1 | 0 | 10
38951.5843 | 1 | 0 | 10
38951.5864 | 2026 | 0 | 10
38951.5886 | 2377 | 1 | 10
38951.5907 | 2358 | 1 | 10
38951.5928 | 2430 | 0 | 10
10
38951.5693 | 1 | 0 | 11
38951.5715 | 1 | 0 | 11
38951.5736 | 1 | 0 | 11
38951.5758 | 1 | 0 | 11
38951.5779 | 1 | 0 | 11
38951.58 | 1 | 0 | 11
38951.5822 | 1 | 0 | 11
38951.5843 | 1 | 0 | 11
38951.5864 | 204 | 0 | 11
38951.5886 | 10 | 0 | 11
38951.5907 | 5 | 1 | 11
38951.5929 | 3 | 0 | 11
11
38951.5694 | 1 | 0 | 12
38951.5715 | 1 | 0 | 12
38951.5736 | 1 | 0 | 12
38951.5758 | 1 | 0 | 12
38951.5779 | 1 | 0 | 12
38951.58 | 1 | 0 | 12
38951.5822 | 1 | 0 | 12
38951.5843 | 950 | 0 | 12
38951.5865 | 2531 | 0 | 12
38951.5886 | 2268 | 0 | 12
38951.5907 | 2042 | 1 | 12
38951.5929 | 2004 | 0 | 12
12
38951.5694 | 1 | 0 | 13
38951.5715 | 1 | 0 | 13
38951.5736 | 1 | 0 | 13
38951.5758 | 1 | 0 | 13
38951.5779 | 1 | 0 | 13
38951.5801 | 1 | 0 | 13
38951.5822 | 1 | 0 | 13
38951.5843 | 2 | 0 | 13
38951.5865 | 265 | 0 | 13
38951.5886 | 11 | 0 | 13
38951.5908 | 4 | 0 | 13
38951.5929 | 4 | 0 | 13
13
38951.5694 | 1 | 0 | 14
38951.5715 | 1 | 0 | 14
38951.5737 | 1 | 0 | 14
38951.5758 | 1 | 0 | 14
38951.5779 | 1 | 0 | 14
38951.5801 | 1 | 0 | 14
38951.5822 | 1 | 0 | 14
38951.5844 | 1126 | 0 | 14
38951.5865 | 2260 | 0 | 14
38951.5886 | 2253 | 0 | 14
38951.5908 | 2320 | 0 | 14
38951.5929 | 2388 | 0 | 14
14
38951.5694 | 1 | 0 | 15
38951.5715 | 1 | 0 | 15
38951.5737 | 1 | 0 | 15
38951.5758 | 1 | 0 | 15
38951.578 | 1 | 0 | 15
38951.5801 | 1 | 0 | 15
38951.5822 | 1 | 0 | 15
38951.5844 | 2 | 0 | 15
38951.5865 | 206 | 0 | 15
38951.5886 | 8 | 0 | 15
38951.5908 | 4 | 0 | 15
38951.5929 | 4 | 0 | 15
15
38951.5694 | 1 | 0 | 16
38951.5716 | 1 | 0 | 16
38951.5737 | 1 | 0 | 16
38951.5758 | 1 | 0 | 16
38951.578 | 1 | 0 | 16
38951.5801 | 1 | 0 | 16
38951.5822 | 1 | 0 | 16
38951.5844 | 2 | 0 | 16
38951.5865 | 2255 | 0 | 16
38951.5887 | 2360 | 0 | 16
38951.5908 | 1972 | 0 | 16
38951.5929 | 2046 | 0 | 16
16
38951.5694 | 1 | 0 | 17
38951.5716 | 1 | 0 | 17
38951.5737 | 1 | 0 | 17
38951.5759 | 1 | 0 | 17
38951.578 | 1 | 0 | 17
38951.5801 | 1 | 0 | 17
38951.5823 | 1 | 0 | 17
38951.5844 | 2 | 0 | 17
38951.5865 | 246 | 0 | 17
38951.5887 | 6 | 0 | 17
38951.5908 | 4 | 0 | 17
38951.593 | 4 | 0 | 17
17
38951.5695 | 1 | 0 | 18
38951.5716 | 1 | 0 | 18
38951.5737 | 1 | 0 | 18
38951.5759 | 1 | 0 | 18
38951.578 | 1 | 0 | 18
38951.5801 | 1 | 0 | 18
38951.5823 | 1 | 0 | 18
38951.5844 | 2 | 0 | 18
38951.5866 | 2342 | 0 | 18
38951.5887 | 2348 | 0 | 18
38951.5908 | 2433 | 0 | 18
38951.593 | 2522 | 0 | 18
18
38951.5695 | 1 | 0 | 19
38951.5716 | 1 | 0 | 19
38951.5738 | 1 | 0 | 19
38951.5759 | 1 | 0 | 19
38951.578 | 1 | 0 | 19
38951.5802 | 1 | 0 | 19
38951.5844 | 1 | 0 | 19
38951.5866 | 258 | 0 | 19
38951.5887 | 5 | 0 | 19
38951.5909 | 4 | 0 | 19
38951.593 | 4 | 0 | 19
19
38951.5695 | 1 | 0 | 20
38951.5716 | 1 | 0 | 20
38951.5738 | 1 | 0 | 20
38951.5759 | 1 | 0 | 20
38951.578 | 1 | 0 | 20
38951.5802 | 1 | 0 | 20
38951.5823 | 1 | 0 | 20
38951.5845 | 2 | 0 | 20
38951.5866 | 4 | 0 | 20
38951.5887 | 3 | 0 | 20
38951.5909 | 3 | 0 | 20
38951.593 | 3 | 0 | 20
20
38951.5695 | 1 | 0 | 21
38951.5716 | 1 | 0 | 21
38951.5738 | 1 | 0 | 21
38951.5759 | 1 | 0 | 21
38951.5781 | 1 | 0 | 21
38951.5802 | 1 | 0 | 21
38951.5823 | 1 | 0 | 21
38951.5845 | 1 | 0 | 21
38951.5866 | 361 | 0 | 21
38951.5888 | 6 | 0 | 21
38951.5909 | 4 | 0 | 21
38951.593 | 3 | 0 | 21
21
38951.5695 | 1 | 0 | 22
38951.5717 | 1 | 0 | 22
38951.5738 | 1 | 0 | 22
38951.5759 | 1 | 0 | 22
38951.5781 | 2 | 0 | 22
38951.5802 | 1 | 0 | 22
38951.5823 | 1 | 0 | 22
38951.5845 | 1 | 0 | 22
38951.5866 | 4 | 0 | 22
38951.5888 | 4 | 0 | 22
38951.5909 | 3 | 0 | 22
38951.593 | 3 | 0 | 22
22
38951.5695 | 1 | 0 | 23
38951.5717 | 1 | 0 | 23
38951.5738 | 1 | 0 | 23
38951.5759 | 1 | 0 | 23
38951.5781 | 1 | 0 | 23
38951.5802 | 1 | 0 | 23
38951.5824 | 1 | 0 | 23
38951.5845 | 1 | 0 | 23
38951.5866 | 402 | 0 | 23
38951.5888 | 359 | 328 | 23
38951.5909 | 423 | 461 | 23
38951.5931 | 10 | 8 | 23
23
38951.5695 | 1 | 0 | 24
38951.5717 | 1 | 0 | 24
38951.5738 | 1 | 0 | 24
38951.576 | 1 | 0 | 24
38951.5781 | 1 | 0 | 24
38951.5802 | 1 | 0 | 24
38951.5824 | 1 | 0 | 24
38951.5845 | 1 | 0 | 24
38951.5867 | 4 | 0 | 24
38951.5888 | 374 | 331 | 24
38951.5909 | 319 | 281 | 24
38951.5931 | 29 | 13 | 24
24
38951.5696 | 1 | 0 | 25
38951.5717 | 1 | 0 | 25
38951.5738 | 1 | 0 | 25
38951.576 | 1 | 0 | 25
38951.5781 | 1 | 0 | 25
38951.5803 | 1 | 0 | 25
38951.5824 | 1 | 0 | 25
38951.5845 | 1 | 0 | 25
38951.5867 | 347 | 0 | 25
38951.5888 | 451 | 389 | 25
38951.5909 | 246 | 217 | 25
38951.5931 | 30 | 28 | 25
25
38951.5696 | 1 | 0 | 26
38951.5717 | 1 | 0 | 26
38951.5739 | 1 | 0 | 26
38951.576 | 1 | 0 | 26
38951.5781 | 1 | 0 | 26
38951.5803 | 1 | 0 | 26
38951.5824 | 1 | 0 | 26
38951.5845 | 1 | 0 | 26
38951.5867 | 327 | 0 | 26
38951.5888 | 501 | 464 | 26
38951.591 | 246 | 220 | 26
38951.5931 | 34 | 31 | 26
26
38951.5696 | 1 | 0 | 27
38951.5717 | 1 | 0 | 27
38951.5739 | 1 | 0 | 27
38951.576 | 1 | 0 | 27
38951.5781 | 1 | 0 | 27
38951.5803 | 1 | 0 | 27
38951.5824 | 1 | 0 | 27
38951.5846 | 1 | 0 | 27
38951.5867 | 416 | 0 | 27
38951.5888 | 9 | 3 | 27
38951.591 | 3 | 1 | 27
38951.5931 | 3 | 0 | 27
27
38951.5696 | 1 | 0 | 28
38951.5717 | 1 | 0 | 28
38951.5739 | 1 | 0 | 28
38951.576 | 1 | 0 | 28
38951.5782 | 1 | 0 | 28
38951.5803 | 1 | 0 | 28
38951.5824 | 1 | 0 | 28
38951.5846 | 1 | 0 | 28
38951.5867 | 2180 | 0 | 28
38951.5889 | 2115 | 1 | 28
38951.591 | 2586 | 1 | 28
38951.5931 | 2322 | 0 | 28
28
38951.5696 | 1 | 0 | 29
38951.5718 | 1 | 0 | 29
38951.5739 | 1 | 0 | 29
38951.576 | 1 | 0 | 29
38951.5782 | 1 | 0 | 29
38951.5803 | 1 | 0 | 29
38951.5825 | 1 | 0 | 29
38951.5846 | 1 | 0 | 29
38951.5867 | 391 | 0 | 29
38951.5889 | 13 | 0 | 29
38951.591 | 6 | 0 | 29
38951.5932 | 4 | 0 | 29
29
38951.5696 | 1 | 0 | 30
38951.5718 | 1 | 0 | 30
38951.5739 | 1 | 0 | 30
38951.5761 | 1 | 0 | 30
38951.5782 | 1 | 0 | 30
38951.5803 | 1 | 0 | 30
38951.5825 | 1 | 0 | 30
38951.5846 | 1 | 0 | 30
38951.5868 | 2187 | 0 | 30
38951.5889 | 2500 | 0 | 30
38951.591 | 2496 | 0 | 30
38951.5932 | 2438 | 0 | 30
30
38951.5697 | 1 | 0 | 31
38951.5718 | 1 | 0 | 31
38951.5739 | 1 | 0 | 31
38951.5761 | 1 | 0 | 31
38951.5782 | 1 | 0 | 31
38951.5804 | 1 | 0 | 31
38951.5825 | 1 | 0 | 31
38951.5846 | 1 | 0 | 31
38951.5868 | 364 | 0 | 31
38951.5889 | 17 | 0 | 31
38951.5911 | 35 | 0 | 31
38951.5932 | 4 | 0 | 31
31
38951.5697 | 1 | 0 | 32
38951.5718 | 1 | 0 | 32
38951.574 | 1 | 0 | 32
38951.5761 | 1 | 0 | 32
38951.5782 | 1 | 0 | 32
38951.5804 | 1 | 0 | 32
38951.5825 | 1 | 0 | 32
38951.5847 | 1488 | 0 | 32
38951.5868 | 2483 | 0 | 32
38951.5889 | 2486 | 0 | 32
38951.5911 | 2064 | 0 | 32
38951.5932 | 2211 | 0 | 32
32
38951.5697 | 1 | 0 | 33
38951.5718 | 1 | 0 | 33
38951.574 | 1 | 0 | 33
38951.5761 | 1 | 0 | 33
38951.5783 | 1 | 0 | 33
38951.5804 | 1 | 0 | 33
38951.5825 | 1 | 0 | 33
38951.5847 | 3 | 0 | 33
38951.5868 | 310 | 0 | 33
38951.5889 | 26 | 0 | 33
38951.5911 | 13 | 0 | 33
38951.5932 | 4 | 0 | 33
33
38951.5697 | 1 | 0 | 34
38951.5719 | 1 | 0 | 34
38951.574 | 1 | 0 | 34
38951.5761 | 1 | 0 | 34
38951.5783 | 1 | 0 | 34
38951.5804 | 1 | 0 | 34
38951.5825 | 1 | 0 | 34
38951.5847 | 1437 | 0 | 34
38951.5868 | 2411 | 0 | 34
38951.589 | 2084 | 0 | 34
38951.5911 | 2405 | 0 | 34
38951.5932 | 1720 | 0 | 34
34
38951.5697 | 1 | 0 | 35
38951.5719 | 1 | 0 | 35
38951.574 | 1 | 0 | 35
38951.5761 | 1 | 0 | 35
38951.5783 | 1 | 0 | 35
38951.5804 | 1 | 0 | 35
38951.5826 | 1 | 0 | 35
38951.5847 | 3 | 0 | 35
38951.5868 | 344 | 0 | 35
38951.589 | 13 | 0 | 35
38951.5911 | 14 | 0 | 35
38951.5933 | 4 | 0 | 35
35
38951.5697 | 1 | 0 | 36
38951.5719 | 1 | 0 | 36
38951.574 | 1 | 0 | 36
38951.5762 | 2 | 0 | 36
38951.5783 | 1 | 0 | 36
38951.5804 | 1 | 0 | 36
38951.5826 | 1 | 0 | 36
38951.5847 | 2 | 0 | 36
38951.5869 | 2376 | 0 | 36
38951.589 | 2241 | 0 | 36
38951.5911 | 2377 | 0 | 36
38951.5933 | 2280 | 0 | 36
36
38951.5698 | 1 | 0 | 37
38951.5719 | 1 | 0 | 37
38951.574 | 1 | 0 | 37
38951.5762 | 1 | 0 | 37
38951.5783 | 1 | 0 | 37
38951.5805 | 1 | 0 | 37
38951.5826 | 1 | 0 | 37
38951.5847 | 2 | 0 | 37
38951.5869 | 238 | 0 | 37
38951.589 | 16 | 0 | 37
38951.5911 | 13 | 0 | 37
38951.5933 | 4 | 0 | 37
37
38951.5698 | 1 | 0 | 38
38951.5719 | 1 | 0 | 38
38951.5741 | 1 | 0 | 38
38951.5762 | 1 | 0 | 38
38951.5783 | 1 | 0 | 38
38951.5805 | 1 | 0 | 38
38951.5826 | 1 | 0 | 38
38951.5847 | 2 | 0 | 38
38951.5869 | 2182 | 0 | 38
38951.589 | 2504 | 0 | 38
38951.5912 | 2043 | 0 | 38
38951.5933 | 2147 | 0 | 38
38
38951.5698 | 1 | 0 | 39
38951.5719 | 1 | 0 | 39
38951.5741 | 1 | 0 | 39
38951.5762 | 1 | 0 | 39
38951.5783 | 1 | 0 | 39
38951.5805 | 1 | 0 | 39
38951.5826 | 1 | 0 | 39
38951.5848 | 1 | 0 | 39
38951.5869 | 256 | 0 | 39
38951.589 | 29 | 0 | 39
38951.5912 | 13 | 0 | 39
38951.5933 | 3 | 0 | 39
39
38951.5698 | 1 | 0 | 40
38951.5719 | 1 | 0 | 40
38951.5741 | 1 | 0 | 40
38951.5762 | 1 | 0 | 40
38951.5784 | 1 | 0 | 40
38951.5805 | 1 | 0 | 40
38951.5826 | 1 | 0 | 40
38951.5848 | 2 | 0 | 40
38951.5869 | 4 | 0 | 40
38951.5891 | 3 | 0 | 40
38951.5912 | 3 | 0 | 40
38951.5933 | 3 | 0 | 40
40
38951.5698 | 1 | 0 | 41
38951.572 | 1 | 0 | 41
38951.5741 | 1 | 0 | 41
38951.5762 | 1 | 0 | 41
38951.5784 | 1 | 0 | 41
38951.5805 | 1 | 0 | 41
38951.5827 | 1 | 0 | 41
38951.5848 | 1 | 0 | 41
38951.5869 | 329 | 0 | 41
38951.5891 | 17 | 0 | 41
38951.5912 | 13 | 0 | 41
38951.5933 | 3 | 0 | 41
41
38951.5698 | 1 | 0 | 42
38951.572 | 1 | 0 | 42
38951.5741 | 1 | 0 | 42
38951.5763 | 1 | 0 | 42
38951.5784 | 1 | 0 | 42
38951.5805 | 1 | 0 | 42
38951.5827 | 1 | 0 | 42
38951.5848 | 1 | 0 | 42
38951.5869 | 4 | 0 | 42
38951.5891 | 3 | 0 | 42
38951.5912 | 3 | 0 | 42
38951.5934 | 3 | 0 | 42
42
38951.5699 | 1 | 0 | 43
38951.572 | 1 | 0 | 43
38951.5741 | 1 | 0 | 43
38951.5763 | 1 | 0 | 43
38951.5784 | 1 | 0 | 43
38951.5805 | 1 | 0 | 43
38951.5827 | 1 | 0 | 43
38951.5848 | 1074 | 1169 | 43
38951.587 | 1207 | 1125 | 43
38951.5891 | 985 | 886 | 43
38951.5912 | 995 | 878 | 43
38951.5934 | 1208 | 1203 | 43
43
38951.5699 | 1 | 0 | 44
38951.572 | 1 | 0 | 44
38951.5742 | 1 | 0 | 44
38951.5763 | 1 | 0 | 44
38951.5784 | 1 | 0 | 44
38951.5806 | 1 | 0 | 44
38951.5827 | 1 | 0 | 44
38951.5848 | 1157 | 1205 | 44
38951.587 | 1080 | 996 | 44
38951.5891 | 1043 | 938 | 44
38951.5913 | 1172 | 1024 | 44
38951.5934 | 993 | 956 | 44
44
38951.5699 | 1 | 0 | 45
38951.572 | 1 | 0 | 45
38951.5742 | 1 | 0 | 45
38951.5763 | 1 | 0 | 45
38951.5784 | 1 | 0 | 45
38951.5806 | 1 | 0 | 45
38951.5827 | 1 | 0 | 45
38951.5849 | 3 | 9 | 45
38951.587 | 28 | 8 | 45
38951.5891 | 27 | 8 | 45
38951.5913 | 102 | 7 | 45
38951.5934 | 3 | 8 | 45
45
38951.5699 | 1 | 0 | 46
38951.572 | 1 | 0 | 46
38951.5742 | 1 | 0 | 46
38951.5763 | 1 | 0 | 46
38951.5785 | 1 | 0 | 46
38951.5806 | 1 | 0 | 46
38951.5827 | 1 | 0 | 46
38951.5849 | 2 | 4 | 46
38951.587 | 2223 | 4 | 46
38951.5892 | 2501 | 4 | 46
38951.5913 | 2019 | 3 | 46
38951.5934 | 2273 | 3 | 46
46
38951.5699 | 1 | 0 | 47
38951.5721 | 1 | 0 | 47
38951.5742 | 1 | 0 | 47
38951.5763 | 1 | 0 | 47
38951.5785 | 1 | 0 | 47
38951.5806 | 1 | 0 | 47
38951.5828 | 1 | 0 | 47
38951.5849 | 2 | 2 | 47
38951.587 | 5 | 2 | 47
38951.5892 | 25 | 2 | 47
38951.5913 | 3 | 2 | 47
38951.5934 | 3 | 2 | 47
47
38951.5699 | 1 | 0 | 48
38951.5721 | 1 | 0 | 48
38951.5742 | 1 | 0 | 48
38951.5764 | 1 | 0 | 48
38951.5785 | 1 | 0 | 48
38951.5806 | 1 | 0 | 48
38951.5828 | 1 | 0 | 48
38951.5849 | 2 | 1 | 48
38951.587 | 2501 | 1 | 48
38951.5892 | 2404 | 2 | 48
38951.5913 | 2542 | 1 | 48
38951.5935 | 1958 | 1 | 48
48
38951.57 | 1 | 0 | 49
38951.5721 | 1 | 0 | 49
38951.5742 | 1 | 0 | 49
38951.5764 | 1 | 0 | 49
38951.5785 | 1 | 0 | 49
38951.5806 | 1 | 0 | 49
38951.5828 | 1 | 0 | 49
38951.5849 | 1 | 1 | 49
38951.5871 | 56 | 2 | 49
38951.5892 | 48 | 1 | 49
38951.5913 | 4 | 1 | 49
38951.5935 | 4 | 1 | 49
49
38951.57 | 1 | 0 | 50
38951.5721 | 1 | 0 | 50
38951.5742 | 1 | 0 | 50
38951.5764 | 1 | 0 | 50
38951.5785 | 1 | 0 | 50
38951.5807 | 1 | 0 | 50
38951.5828 | 1 | 0 | 50
38951.5849 | 1764 | 1 | 50
38951.5871 | 2422 | 1 | 50
38951.5892 | 2008 | 1 | 50
38951.5914 | 2201 | 0 | 50
38951.5935 | 1972 | 0 | 50
50
38951.57 | 1 | 0 | 51
38951.5721 | 1 | 0 | 51
38951.5743 | 1 | 0 | 51
38951.5764 | 1 | 0 | 51
38951.5785 | 1 | 0 | 51
38951.5807 | 1 | 0 | 51
38951.5828 | 1 | 0 | 51
38951.585 | 3 | 0 | 51
38951.5871 | 90 | 0 | 51
38951.5892 | 16 | 0 | 51
38951.5914 | 4 | 0 | 51
38951.5935 | 3 | 0 | 51
51
38951.57 | 1 | 0 | 52
38951.5721 | 1 | 0 | 52
38951.5743 | 1 | 0 | 52
38951.5764 | 1 | 0 | 52
38951.5786 | 1 | 0 | 52
38951.5807 | 1 | 0 | 52
38951.5828 | 1 | 0 | 52
38951.585 | 1545 | 0 | 52
38951.5871 | 2363 | 1 | 52
38951.5892 | 2036 | 1 | 52
38951.5914 | 2105 | 0 | 52
38951.5935 | 1864 | 0 | 52
52
38951.57 | 1 | 0 | 53
38951.5722 | 1 | 0 | 53
38951.5743 | 1 | 0 | 53
38951.5764 | 1 | 0 | 53
38951.5786 | 1 | 0 | 53
38951.5807 | 1 | 0 | 53
38951.5828 | 1 | 0 | 53
38951.585 | 4 | 0 | 53
38951.5871 | 67 | 0 | 53
38951.5893 | 10 | 0 | 53
38951.5914 | 4 | 0 | 53
38951.5935 | 3 | 0 | 53
53
38951.57 | 1 | 0 | 54
38951.5722 | 1 | 0 | 54
38951.5743 | 1 | 0 | 54
38951.5764 | 1 | 0 | 54
38951.5786 | 1 | 0 | 54
38951.5807 | 1 | 0 | 54
38951.5829 | 1 | 0 | 54
38951.585 | 2 | 0 | 54
38951.5871 | 2374 | 0 | 54
38951.5893 | 2423 | 0 | 54
38951.5914 | 2029 | 0 | 54
38951.5936 | 2051 | 0 | 54
54
38951.57 | 1 | 0 | 55
38951.5722 | 1 | 0 | 55
38951.5743 | 2 | 0 | 55
38951.5765 | 1 | 0 | 55
38951.5786 | 1 | 0 | 55
38951.5807 | 1 | 0 | 55
38951.5829 | 1 | 0 | 55
38951.585 | 2 | 0 | 55
38951.5872 | 100 | 0 | 55
38951.5893 | 45 | 0 | 55
38951.5914 | 4 | 1 | 55
38951.5936 | 4 | 0 | 55
55
38951.5701 | 1 | 0 | 56
38951.5722 | 1 | 0 | 56
38951.5743 | 1 | 0 | 56
38951.5765 | 1 | 0 | 56
38951.5786 | 1 | 0 | 56
38951.5808 | 1 | 0 | 56
38951.5829 | 1 | 0 | 56
38951.585 | 2 | 0 | 56
38951.5872 | 2552 | 0 | 56
38951.5893 | 2190 | 0 | 56
38951.5914 | 2337 | 0 | 56
38951.5936 | 2463 | 0 | 56
56
38951.5701 | 1 | 0 | 57
38951.5722 | 1 | 0 | 57
38951.5744 | 1 | 0 | 57
38951.5765 | 1 | 0 | 57
38951.5786 | 1 | 0 | 57
38951.5808 | 1 | 0 | 57
38951.5829 | 1 | 0 | 57
38951.5851 | 2 | 0 | 57
38951.5872 | 95 | 0 | 57
38951.5893 | 71 | 0 | 57
38951.5915 | 4 | 0 | 57
38951.5936 | 4 | 0 | 57
57
38951.5701 | 1 | 0 | 58
38951.5722 | 1 | 0 | 58
38951.5744 | 1 | 0 | 58
38951.5765 | 1 | 0 | 58
38951.5787 | 1 | 0 | 58
38951.5808 | 1 | 0 | 58
38951.5829 | 1 | 0 | 58
38951.5851 | 2 | 0 | 58
38951.5872 | 4 | 0 | 58
38951.5894 | 4 | 0 | 58
38951.5915 | 4 | 0 | 58
38951.5936 | 3 | 1 | 58
58
38951.5701 | 1 | 0 | 59
38951.5723 | 1 | 0 | 59
38951.5744 | 1 | 0 | 59
38951.5765 | 1 | 0 | 59
38951.5787 | 1 | 0 | 59
38951.5808 | 1 | 0 | 59
38951.583 | 1 | 0 | 59
38951.5851 | 2 | 0 | 59
38951.5872 | 117 | 0 | 59
38951.5894 | 53 | 0 | 59
38951.5915 | 3 | 0 | 59
38951.5936 | 3 | 0 | 59
59
38951.5701 | 1 | 0 | 60
38951.5723 | 1 | 0 | 60
38951.5744 | 2 | 0 | 60
38951.5766 | 1 | 0 | 60
38951.5787 | 1 | 0 | 60
38951.5808 | 1 | 0 | 60
38951.583 | 1 | 0 | 60
38951.5851 | 2 | 0 | 60
38951.5872 | 4 | 0 | 60
38951.5894 | 3 | 0 | 60
38951.5915 | 4 | 0 | 60
38951.5937 | 3 | 0 | 60
60
38951.5702 | 1 | 0 | 61
38951.5723 | 1 | 0 | 61
38951.5744 | 1 | 0 | 61
38951.5766 | 1 | 0 | 61
38951.5787 | 1 | 0 | 61
38951.5808 | 1 | 0 | 61
38951.583 | 1 | 0 | 61
38951.5851 | 2 | 0 | 61
38951.5873 | 178 | 0 | 61
38951.5894 | 58 | 0 | 61
38951.5915 | 4 | 0 | 61
38951.5937 | 3 | 0 | 61
61
38951.5702 | 1 | 0 | 62
38951.5723 | 1 | 0 | 62
38951.5744 | 1 | 0 | 62
38951.5766 | 1 | 0 | 62
38951.5787 | 1 | 0 | 62
38951.5809 | 1 | 0 | 62
38951.583 | 1 | 0 | 62
38951.5851 | 2208 | 0 | 62
38951.5873 | 2390 | 0 | 62
38951.5894 | 2088 | 0 | 62
38951.5916 | 2047 | 0 | 62
38951.5937 | 2199 | 0 | 62
62
38951.5702 | 1 | 0 | 63
38951.5723 | 1 | 0 | 63
38951.5745 | 1 | 0 | 63
38951.5766 | 1 | 0 | 63
38951.5787 | 1 | 0 | 63
38951.5809 | 1 | 0 | 63
38951.583 | 1 | 0 | 63
38951.5852 | 4 | 0 | 63
38951.5873 | 164 | 0 | 63
38951.5894 | 9 | 0 | 63
38951.5916 | 4 | 0 | 63
38951.5937 | 4 | 0 | 63
63
38951.5702 | 1 | 0 | 64
38951.5723 | 1 | 0 | 64
38951.5745 | 1 | 0 | 64
38951.5766 | 1 | 0 | 64
38951.5788 | 1 | 0 | 64
38951.5809 | 1 | 0 | 64
38951.583 | 1 | 0 | 64
38951.5852 | 2276 | 0 | 64
38951.5873 | 2567 | 0 | 64
38951.5894 | 2250 | 0 | 64
38951.5916 | 2284 | 0 | 64
38951.5937 | 2280 | 0 | 64
64
38951.5702 | 1 | 0 | 65
38951.5723 | 1 | 0 | 65
38951.5745 | 1 | 0 | 65
38951.5766 | 1 | 0 | 65
38951.5788 | 1 | 0 | 65
38951.5809 | 1 | 0 | 65
38951.583 | 1 | 0 | 65
38951.5852 | 4 | 0 | 65
38951.5873 | 107 | 0 | 65
38951.5895 | 7 | 0 | 65
38951.5916 | 5 | 0 | 65
38951.5937 | 4 | 0 | 65
65
38951.5702 | 1 | 0 | 66
38951.5724 | 1 | 0 | 66
38951.5745 | 1 | 0 | 66
38951.5766 | 1 | 0 | 66
38951.5788 | 1 | 0 | 66
38951.5809 | 1 | 0 | 66
38951.5831 | 2 | 0 | 66
38951.5852 | 1957 | 0 | 66
38951.5873 | 2446 | 0 | 66
38951.5895 | 2224 | 0 | 66
38951.5916 | 2361 | 0 | 66
38951.5938 | 2144 | 0 | 66
66
38951.5702 | 1 | 0 | 67
38951.5724 | 1 | 0 | 67
38951.5745 | 1 | 0 | 67
38951.5767 | 1 | 0 | 67
38951.5788 | 1 | 0 | 67
38951.5809 | 1 | 0 | 67
38951.5831 | 1 | 0 | 67
38951.5852 | 4 | 0 | 67
38951.5873 | 125 | 0 | 67
38951.5895 | 7 | 0 | 67
38951.5916 | 3 | 0 | 67
38951.5938 | 24 | 0 | 67
67
38951.5703 | 1 | 0 | 68
38951.5724 | 1 | 0 | 68
38951.5745 | 1 | 0 | 68
38951.5767 | 1 | 0 | 68
38951.5788 | 1 | 0 | 68
38951.581 | 1 | 0 | 68
38951.5831 | 2 | 0 | 68
38951.5852 | 1993 | 0 | 68
38951.5874 | 1961 | 0 | 68
38951.5895 | 2237 | 0 | 68
38951.5916 | 2125 | 0 | 68
38951.5938 | 1924 | 0 | 68
68
38951.5703 | 1 | 0 | 69
38951.5724 | 1 | 0 | 69
38951.5746 | 1 | 0 | 69
38951.5767 | 1 | 0 | 69
38951.5788 | 1 | 0 | 69
38951.581 | 1 | 0 | 69
38951.5831 | 1 | 0 | 69
38951.5852 | 4 | 0 | 69
38951.5874 | 147 | 0 | 69
38951.5895 | 8 | 0 | 69
38951.5917 | 46 | 0 | 69
38951.5938 | 3 | 0 | 69
69
38951.5703 | 1 | 0 | 70
38951.5724 | 1 | 0 | 70
38951.5746 | 1 | 0 | 70
38951.5767 | 1 | 0 | 70
38951.5789 | 1 | 0 | 70
38951.581 | 1 | 0 | 70
38951.5831 | 1 | 0 | 70
38951.5853 | 135 | 0 | 70
38951.5874 | 1996 | 0 | 70
38951.5895 | 2242 | 0 | 70
38951.5917 | 2340 | 0 | 70
38951.5938 | 2283 | 0 | 70
70
38951.5703 | 1 | 0 | 71
38951.5725 | 1 | 0 | 71
38951.5746 | 1 | 0 | 71
38951.5767 | 1 | 0 | 71
38951.5789 | 1 | 0 | 71
38951.581 | 1 | 0 | 71
38951.5831 | 1 | 0 | 71
38951.5853 | 3 | 0 | 71
38951.5874 | 127 | 0 | 71
38951.5896 | 5 | 0 | 71
38951.5917 | 3 | 0 | 71
38951.5938 | 3 | 0 | 71
71
38951.5703 | 1 | 0 | 72
38951.5725 | 1 | 0 | 72
38951.5746 | 1 | 0 | 72
38951.5767 | 1 | 0 | 72
38951.5789 | 1 | 0 | 72
38951.581 | 1 | 0 | 72
38951.5832 | 1 | 0 | 72
38951.5853 | 225 | 0 | 72
38951.5874 | 2396 | 0 | 72
38951.5896 | 2205 | 0 | 72
38951.5917 | 2018 | 0 | 72
38951.5939 | 2304 | 0 | 72
72
38951.5703 | 1 | 0 | 73
38951.5725 | 1 | 0 | 73
38951.5746 | 1 | 0 | 73
38951.5768 | 1 | 0 | 73
38951.5789 | 1 | 0 | 73
38951.581 | 1 | 0 | 73
38951.5832 | 1 | 0 | 73
38951.5853 | 3 | 0 | 73
38951.5875 | 137 | 0 | 73
38951.5896 | 5 | 0 | 73
38951.5917 | 172 | 0 | 73
38951.5939 | 4 | 0 | 73
73
38951.5704 | 1 | 0 | 74
38951.5725 | 1 | 0 | 74
38951.5746 | 1 | 0 | 74
38951.5768 | 1 | 0 | 74
38951.5789 | 1 | 0 | 74
38951.5811 | 1 | 0 | 74
38951.5832 | 1 | 0 | 74
38951.5853 | 2 | 0 | 74
38951.5875 | 4 | 0 | 74
38951.5896 | 4 | 0 | 74
38951.5917 | 3 | 0 | 74
38951.5939 | 3 | 0 | 74
74
38951.5704 | 1 | 0 | 75
38951.5725 | 1 | 0 | 75
38951.5747 | 1 | 0 | 75
38951.5768 | 1 | 0 | 75
38951.5789 | 1 | 0 | 75
38951.5811 | 1 | 0 | 75
38951.5832 | 1 | 0 | 75
38951.5853 | 2 | 0 | 75
38951.5875 | 96 | 0 | 75
38951.5896 | 5 | 0 | 75
38951.5918 | 3 | 0 | 75
38951.5939 | 3 | 0 | 75
75
38951.5704 | 1 | 0 | 76
38951.5725 | 1 | 0 | 76
38951.5747 | 1 | 0 | 76
38951.5768 | 1 | 0 | 76
38951.5789 | 1 | 0 | 76
38951.5811 | 1 | 0 | 76
38951.5832 | 1 | 0 | 76
38951.5854 | 2 | 0 | 76
38951.5875 | 4 | 0 | 76
38951.5896 | 3 | 0 | 76
38951.5918 | 3 | 0 | 76
38951.5939 | 3 | 0 | 76
76
38951.5704 | 1 | 1 | 77
38951.5725 | 1 | 0 | 77
38951.5747 | 1 | 0 | 77
38951.5768 | 1 | 0 | 77
38951.579 | 1 | 0 | 77
38951.5811 | 1196 | 1177 | 77
38951.5832 | 996 | 967 | 77
38951.5854 | 2051 | 0 | 77
38951.5875 | 2157 | 0 | 77
38951.5897 | 2591 | 0 | 77
38951.5918 | 2598 | 0 | 77
38951.5939 | 2018 | 0 | 77
77
38951.5704 | 1 | 0 | 78
38951.5726 | 1 | 0 | 78
38951.5747 | 1 | 0 | 78
38951.5768 | 1 | 0 | 78
38951.579 | 1 | 0 | 78
38951.5811 | 948 | 923 | 78
38951.5833 | 1068 | 1042 | 78
38951.5854 | 2608 | 0 | 78
38951.5875 | 2068 | 0 | 78
38951.5897 | 2132 | 0 | 78
38951.5918 | 2505 | 0 | 78
38951.5939 | 2319 | 0 | 78
78
38951.5704 | 1 | 0 | 79
38951.5726 | 1 | 0 | 79
38951.5747 | 1 | 0 | 79
38951.5769 | 1 | 0 | 79
38951.579 | 1 | 0 | 79
38951.5811 | 3 | 9 | 79
38951.5833 | 3 | 9 | 79
38951.5854 | 2018 | 0 | 79
38951.5875 | 2455 | 0 | 79
38951.5897 | 2155 | 0 | 79
38951.5918 | 2135 | 0 | 79
38951.594 | 2016 | 0 | 79
79
38951.5705 | 1 | 0 | 80
38951.5726 | 1 | 0 | 80
38951.5747 | 1 | 0 | 80
38951.5769 | 1 | 0 | 80
38951.579 | 1 | 0 | 80
38951.5811 | 2 | 4 | 80
38951.5833 | 5 | 5 | 80
38951.5854 | 2385 | 0 | 80
38951.5876 | 2054 | 0 | 80
38951.5897 | 1943 | 0 | 80
38951.5918 | 2447 | 0 | 80
38951.594 | 2331 | 0 | 80
80
38951.5705 | 1 | 0 | 81
38951.5726 | 1 | 0 | 81
38951.5747 | 1 | 0 | 81
38951.5769 | 1 | 0 | 81
38951.579 | 1 | 0 | 81
38951.5812 | 2 | 2 | 81
38951.5833 | 2 | 2 | 81
38951.5854 | 2176 | 0 | 81
38951.5876 | 2337 | 0 | 81
38951.5897 | 2587 | 0 | 81
38951.5919 | 2593 | 0 | 81
38951.594 | 2149 | 0 | 81
81
38951.5705 | 1 | 0 | 82
38951.5726 | 1 | 0 | 82
38951.5748 | 1 | 0 | 82
38951.5769 | 1 | 0 | 82
38951.579 | 1 | 0 | 82
38951.5812 | 2 | 1 | 82
38951.5833 | 4 | 1 | 82
38951.5855 | 2080 | 0 | 82
38951.5876 | 2182 | 0 | 82
38951.5897 | 2529 | 0 | 82
38951.5919 | 1699 | 0 | 82
38951.594 | 1646 | 0 | 82
82
38951.5705 | 1 | 0 | 83
38951.5726 | 1 | 0 | 83
38951.5748 | 1 | 0 | 83
38951.5769 | 1 | 0 | 83
38951.5791 | 1 | 0 | 83
38951.5812 | 2 | 1 | 83
38951.5833 | 1 | 1 | 83
38951.5855 | 2004 | 0 | 83
38951.5876 | 2179 | 0 | 83
38951.5898 | 2521 | 0 | 83
38951.5919 | 2360 | 0 | 83
38951.594 | 2163 | 0 | 83
83
38951.5705 | 1 | 0 | 84
38951.5727 | 1 | 0 | 84
38951.5748 | 1 | 0 | 84
38951.5769 | 1 | 0 | 84
38951.5791 | 1 | 0 | 84
38951.5812 | 2 | 1 | 84
38951.5834 | 1 | 1 | 84
38951.5855 | 214 | 0 | 84
38951.5876 | 2388 | 0 | 84
38951.5898 | 2396 | 0 | 84
38951.5919 | 2189 | 0 | 84
38951.5941 | 2145 | 0 | 84
84
38951.5705 | 1 | 0 | 85
38951.5727 | 1 | 0 | 85
38951.5748 | 1 | 0 | 85
38951.577 | 1 | 0 | 85
38951.5791 | 1 | 0 | 85
38951.5812 | 2 | 1 | 85
38951.5834 | 2 | 0 | 85
38951.5855 | 2254 | 0 | 85
38951.5877 | 2075 | 0 | 85
38951.5898 | 2163 | 0 | 85
38951.5919 | 2134 | 0 | 85
38951.5941 | 1971 | 0 | 85
85
38951.5706 | 1 | 0 | 86
38951.5727 | 1 | 0 | 86
38951.5748 | 1 | 0 | 86
38951.577 | 1 | 0 | 86
38951.5791 | 1 | 0 | 86
38951.5813 | 1 | 0 | 86
38951.5834 | 1 | 0 | 86
38951.5855 | 423 | 0 | 86
38951.5877 | 1970 | 0 | 86
38951.5898 | 2007 | 0 | 86
38951.5919 | 2544 | 0 | 86
38951.5941 | 2167 | 0 | 86
86
38951.5706 | 1 | 0 | 87
38951.5727 | 1 | 0 | 87
38951.5748 | 1 | 0 | 87
38951.577 | 1 | 0 | 87
38951.5791 | 1 | 0 | 87
38951.5813 | 1 | 0 | 87
38951.5834 | 1 | 0 | 87
38951.5855 | 2603 | 0 | 87
38951.5877 | 2204 | 0 | 87
38951.5898 | 2493 | 0 | 87
38951.592 | 2502 | 0 | 87
38951.5941 | 2410 | 0 | 87
87
38951.5706 | 1 | 0 | 88
38951.5727 | 1 | 0 | 88
38951.5749 | 1 | 0 | 88
38951.577 | 1 | 0 | 88
38951.5791 | 1 | 0 | 88
38951.5813 | 1 | 0 | 88
38951.5834 | 1 | 0 | 88
38951.5856 | 5 | 0 | 88
38951.5877 | 4 | 0 | 88
38951.5898 | 4 | 0 | 88
38951.592 | 4 | 0 | 88
38951.5941 | 4 | 0 | 88
88
38951.5706 | 1 | 0 | 89
38951.5727 | 1 | 0 | 89
38951.5749 | 1 | 0 | 89
38951.577 | 1 | 0 | 89
38951.5792 | 1 | 0 | 89
38951.5813 | 1 | 0 | 89
38951.5834 | 1 | 0 | 89
38951.5856 | 2486 | 0 | 89
38951.5877 | 2579 | 0 | 89
38951.5898 | 2346 | 0 | 89
38951.592 | 2199 | 0 | 89
38951.5941 | 2000 | 0 | 89
89
38951.5706 | 1 | 0 | 90
38951.5728 | 1 | 0 | 90
38951.5749 | 1 | 0 | 90
38951.577 | 1 | 0 | 90
38951.5792 | 1 | 0 | 90
38951.5813 | 1 | 0 | 90
38951.5834 | 1 | 0 | 90
38951.5856 | 4 | 0 | 90
38951.5877 | 4 | 0 | 90
38951.5899 | 4 | 0 | 90
38951.592 | 3 | 0 | 90
38951.5941 | 4 | 0 | 90
90
38951.5706 | 1 | 0 | 91
38951.5728 | 1 | 0 | 91
38951.5749 | 1 | 0 | 91
38951.577 | 1 | 0 | 91
38951.5792 | 1 | 0 | 91
38951.5813 | 1 | 0 | 91
38951.5835 | 1 | 0 | 91
38951.5856 | 2086 | 0 | 91
38951.5877 | 2186 | 0 | 91
38951.5899 | 2211 | 0 | 91
38951.592 | 1897 | 0 | 91
38951.5942 | 1974 | 0 | 91
91
38951.5706 | 1 | 0 | 92
38951.5728 | 1 | 0 | 92
38951.5749 | 1 | 0 | 92
38951.5771 | 1 | 0 | 92
38951.5792 | 1 | 0 | 92
38951.5813 | 1 | 0 | 92
38951.5835 | 10 | 0 | 92
38951.5856 | 2203 | 0 | 92
38951.5878 | 2365 | 0 | 92
38951.5899 | 2312 | 0 | 92
38951.592 | 2450 | 0 | 92
38951.5942 | 1945 | 0 | 92
92
38951.5707 | 1 | 0 | 93
38951.5728 | 1 | 0 | 93
38951.5749 | 1 | 0 | 93
38951.5771 | 1 | 0 | 93
38951.5792 | 1 | 0 | 93
38951.5814 | 1 | 0 | 93
38951.5835 | 1 | 0 | 93
38951.5856 | 2111 | 0 | 93
38951.5878 | 2422 | 0 | 93
38951.5899 | 2593 | 0 | 93
38951.592 | 1919 | 0 | 93
38951.5942 | 1972 | 0 | 93
93
38951.5707 | 1 | 0 | 94
38951.5728 | 1 | 0 | 94
38951.575 | 1 | 0 | 94
38951.5771 | 1 | 0 | 94
38951.5792 | 1 | 0 | 94
38951.5814 | 1 | 0 | 94
38951.5835 | 12 | 0 | 94
38951.5856 | 1957 | 0 | 94
38951.5878 | 2535 | 0 | 94
38951.5899 | 2291 | 0 | 94
38951.5921 | 1574 | 0 | 94
38951.5942 | 1819 | 0 | 94
94
38951.5707 | 1 | 0 | 95
38951.5728 | 1 | 0 | 95
38951.575 | 1 | 0 | 95
38951.5771 | 1 | 0 | 95
38951.5792 | 1 | 0 | 95
38951.5814 | 1 | 0 | 95
38951.5835 | 1 | 0 | 95
38951.5857 | 2487 | 0 | 95
38951.5878 | 2550 | 0 | 95
38951.5899 | 2221 | 0 | 95
38951.5921 | 2272 | 0 | 95
38951.5942 | 2158 | 0 | 95
95
38951.5707 | 1 | 0 | 96
38951.5729 | 1 | 0 | 96
38951.575 | 1 | 0 | 96
38951.5771 | 1 | 0 | 96
38951.5793 | 1 | 0 | 96
38951.5814 | 1 | 0 | 96
38951.5835 | 1 | 0 | 96
38951.5857 | 434 | 0 | 96
38951.5878 | 2163 | 0 | 96
38951.59 | 2379 | 0 | 96
38951.5921 | 2554 | 0 | 96
38951.5942 | 2146 | 0 | 96
96
38951.5707 | 1 | 0 | 97
38951.5729 | 1 | 0 | 97
38951.575 | 1 | 0 | 97
38951.5771 | 1 | 0 | 97
38951.5793 | 1 | 0 | 97
38951.5814 | 1 | 0 | 97
38951.5836 | 1 | 0 | 97
38951.5857 | 2192 | 0 | 97
38951.5878 | 2086 | 0 | 97
38951.59 | 2384 | 0 | 97
38951.5921 | 2323 | 0 | 97
38951.5943 | 2268 | 0 | 97
97
38951.5708 | 1 | 0 | 98
38951.5729 | 1 | 0 | 98
38951.575 | 1 | 0 | 98
38951.5772 | 1 | 0 | 98
38951.5793 | 1 | 0 | 98
38951.5814 | 1 | 0 | 98
38951.5836 | 1 | 0 | 98
38951.5857 | 403 | 0 | 98
38951.5879 | 2385 | 0 | 98
38951.59 | 1989 | 0 | 98
38951.5921 | 2077 | 0 | 98
38951.5943 | 2203 | 1 | 98
98
38951.5708 | 1 | 0 | 99
38951.5729 | 1 | 0 | 99
38951.575 | 1 | 0 | 99
38951.5772 | 1 | 0 | 99
38951.5793 | 1 | 0 | 99
38951.5815 | 1 | 0 | 99
38951.5836 | 1 | 0 | 99
38951.5857 | 2601 | 0 | 99
38951.5879 | 2242 | 0 | 99
38951.59 | 2414 | 0 | 99
38951.5922 | 2261 | 0 | 99
38951.5943 | 2052 | 0 | 99
99
38951.5708 | 1 | 0 | 100
38951.5729 | 1 | 0 | 100
38951.5751 | 1 | 0 | 100
38951.5772 | 1 | 0 | 100
38951.5793 | 1 | 0 | 100
38951.5815 | 1 | 0 | 100
38951.5836 | 1 | 0 | 100
38951.5858 | 5 | 0 | 100
38951.5879 | 5 | 0 | 100
38951.59 | 4 | 0 | 100
38951.5922 | 4 | 0 | 100
38951.5943 | 4 | 0 | 100
100
38951.5708 | 1 | 0 | 101
38951.5729 | 1 | 0 | 101
38951.5751 | 1 | 0 | 101
38951.5772 | 1 | 0 | 101
38951.5794 | 1 | 0 | 101
38951.5815 | 1 | 0 | 101
38951.5836 | 1 | 0 | 101
38951.5858 | 2598 | 0 | 101
38951.5879 | 2329 | 0 | 101
38951.59 | 2220 | 0 | 101
38951.5922 | 1896 | 0 | 101
38951.5943 | 2207 | 0 | 101
101
38951.5708 | 1 | 0 | 102
38951.573 | 1 | 0 | 102
38951.5751 | 1 | 0 | 102
38951.5772 | 1 | 0 | 102
38951.5794 | 1 | 0 | 102
38951.5815 | 1 | 0 | 102
38951.5836 | 1 | 0 | 102
38951.5858 | 4 | 0 | 102
38951.5879 | 4 | 0 | 102
38951.5901 | 4 | 0 | 102
38951.5922 | 3 | 0 | 102
38951.5943 | 4 | 0 | 102
102
38951.5708 | 1 | 0 | 103
38951.573 | 1 | 0 | 103
38951.5751 | 1 | 0 | 103
38951.5772 | 1 | 0 | 103
38951.5794 | 1 | 0 | 103
38951.5815 | 997 | 958 | 103
38951.5837 | 854 | 746 | 103
38951.5858 | 2415 | 0 | 103
38951.5879 | 2489 | 0 | 103
38951.5901 | 2192 | 0 | 103
38951.5922 | 2048 | 0 | 103
38951.5944 | 1930 | 0 | 103
103
38951.5708 | 1 | 0 | 104
38951.573 | 1 | 0 | 104
38951.5751 | 1 | 0 | 104
38951.5773 | 1 | 0 | 104
38951.5794 | 1 | 0 | 104
38951.5815 | 980 | 1090 | 104
38951.5837 | 956 | 850 | 104
38951.5858 | 2424 | 0 | 104
38951.588 | 2492 | 0 | 104
38951.5901 | 2394 | 0 | 104
38951.5922 | 1640 | 0 | 104
38951.5944 | 1937 | 0 | 104
104
38951.5709 | 2 | 0 | 105
38951.573 | 1 | 0 | 105
38951.5751 | 1 | 0 | 105
38951.5773 | 1 | 0 | 105
38951.5794 | 1 | 0 | 105
38951.5816 | 3 | 10 | 105
38951.5837 | 36 | 5 | 105
38951.5858 | 2135 | 0 | 105
38951.588 | 2359 | 0 | 105
38951.5901 | 2163 | 0 | 105
38951.5922 | 2294 | 0 | 105
38951.5944 | 1952 | 0 | 105
105
38951.5709 | 1 | 0 | 106
38951.573 | 1 | 0 | 106
38951.5752 | 1 | 0 | 106
38951.5773 | 1 | 0 | 106
38951.5794 | 1 | 0 | 106
38951.5816 | 2 | 5 | 106
38951.5837 | 2 | 2 | 106
38951.5858 | 464 | 0 | 106
38951.588 | 2199 | 0 | 106
38951.5901 | 2424 | 0 | 106
38951.5923 | 2261 | 0 | 106
38951.5944 | 2219 | 0 | 106
106
38951.5709 | 1 | 0 | 107
38951.573 | 1 | 0 | 107
38951.5752 | 1 | 0 | 107
38951.5773 | 1 | 0 | 107
38951.5794 | 1 | 0 | 107
38951.5816 | 1 | 3 | 107
38951.5837 | 49 | 1 | 107
38951.5859 | 2089 | 0 | 107
38951.588 | 2393 | 0 | 107
38951.5901 | 2419 | 0 | 107
38951.5923 | 1997 | 0 | 107
38951.5944 | 2164 | 0 | 107
107
38951.5709 | 1 | 0 | 108
38951.573 | 1 | 0 | 108
38951.5752 | 1 | 0 | 108
38951.5773 | 1 | 0 | 108
38951.5795 | 1 | 0 | 108
38951.5816 | 2 | 2 | 108
38951.5837 | 2 | 1 | 108
38951.5859 | 1171 | 0 | 108
38951.588 | 2532 | 0 | 108
38951.5902 | 2161 | 0 | 108
38951.5923 | 1988 | 0 | 108
38951.5944 | 2389 | 0 | 108
108
38951.5709 | 1 | 0 | 109
38951.5731 | 1 | 0 | 109
38951.5752 | 1 | 0 | 109
38951.5773 | 1 | 0 | 109
38951.5795 | 1 | 0 | 109
38951.5816 | 1 | 1 | 109
38951.5838 | 68 | 1 | 109
38951.5859 | 2161 | 0 | 109
38951.588 | 2459 | 0 | 109
38951.5902 | 2124 | 0 | 109
38951.5923 | 2476 | 0 | 109
38951.5945 | 2184 | 0 | 109
109
38951.5709 | 1 | 0 | 110
38951.5731 | 1 | 0 | 110
38951.5752 | 1 | 0 | 110
38951.5774 | 1 | 0 | 110
38951.5795 | 1 | 0 | 110
38951.5816 | 1 | 1 | 110
38951.5838 | 1 | 1 | 110
38951.5859 | 4 | 0 | 110
38951.5881 | 4 | 0 | 110
38951.5902 | 4 | 0 | 110
38951.5923 | 4 | 0 | 110
38951.5945 | 4 | 0 | 110
110
38951.571 | 1 | 0 | 111
38951.5731 | 1 | 0 | 111
38951.5752 | 1 | 0 | 111
38951.5774 | 1 | 0 | 111
38951.5795 | 1 | 0 | 111
38951.5817 | 1 | 1 | 111
38951.5838 | 89 | 1 | 111
38951.5859 | 2285 | 0 | 111
38951.5881 | 2252 | 0 | 111
38951.5902 | 2178 | 0 | 111
38951.5923 | 2044 | 0 | 111
38951.5945 | 2295 | 0 | 111
111
38951.571 | 1 | 0 | 112
38951.5731 | 1 | 0 | 112
38951.5753 | 1 | 0 | 112
38951.5774 | 1 | 0 | 112
38951.5795 | 1 | 0 | 112
38951.5817 | 1 | 0 | 112
38951.5838 | 2 | 0 | 112
38951.5859 | 5 | 0 | 112
38951.5881 | 4 | 0 | 112
38951.5902 | 4 | 0 | 112
38951.5924 | 4 | 0 | 112
38951.5945 | 4 | 0 | 112
112
38951.571 | 1 | 0 | 113
38951.5731 | 1 | 0 | 113
38951.5753 | 1 | 0 | 113
38951.5774 | 1 | 0 | 113
38951.5795 | 1 | 0 | 113
38951.5817 | 1 | 0 | 113
38951.5838 | 125 | 0 | 113
38951.586 | 2175 | 0 | 113
38951.5881 | 2497 | 0 | 113
38951.5902 | 1982 | 0 | 113
38951.5924 | 1453 | 0 | 113
38951.5945 | 1766 | 0 | 113
113
38951.571 | 1 | 0 | 114
38951.5731 | 1 | 0 | 114
38951.5753 | 1 | 0 | 114
38951.5774 | 1 | 0 | 114
38951.5796 | 1 | 0 | 114
38951.5817 | 1 | 0 | 114
38951.5838 | 1 | 0 | 114
38951.586 | 1129 | 0 | 114
38951.5881 | 2540 | 0 | 114
38951.5903 | 2510 | 0 | 114
38951.5924 | 2525 | 0 | 114
38951.5945 | 2375 | 0 | 114
114
38951.571 | 1 | 0 | 115
38951.5732 | 1 | 0 | 115
38951.5753 | 1 | 0 | 115
38951.5796 | 1 | 0 | 115
38951.5817 | 1 | 0 | 115
38951.5839 | 195 | 0 | 115
38951.586 | 2524 | 0 | 115
38951.5881 | 2427 | 0 | 115
38951.5903 | 2236 | 0 | 115
38951.5924 | 2309 | 0 | 115
38951.5945 | 1247 | 0 | 115
115
38951.571 | 1 | 0 | 116
38951.5732 | 1 | 0 | 116
38951.5753 | 1 | 0 | 116
38951.5775 | 1 | 0 | 116
38951.5796 | 1 | 0 | 116
38951.5817 | 1 | 0 | 116
38951.5839 | 1 | 0 | 116
38951.586 | 2013 | 0 | 116
38951.5881 | 2178 | 0 | 116
38951.5903 | 2248 | 0 | 116
38951.5924 | 2215 | 0 | 116
38951.5946 | 2514 | 0 | 116
116
38951.5711 | 1 | 0 | 117
38951.5732 | 1 | 0 | 117
38951.5753 | 1 | 0 | 117
38951.5775 | 1 | 0 | 117
38951.5796 | 1 | 0 | 117
38951.5817 | 1 | 0 | 117
38951.5839 | 254 | 0 | 117
38951.586 | 2420 | 0 | 117
38951.5882 | 2014 | 0 | 117
38951.5903 | 1986 | 0 | 117
38951.5924 | 2011 | 0 | 117
38951.5946 | 2145 | 0 | 117
117
38951.5711 | 1 | 0 | 118
38951.5732 | 1 | 0 | 118
38951.5753 | 1 | 0 | 118
38951.5775 | 1 | 0 | 118
38951.5796 | 1 | 0 | 118
38951.5818 | 1 | 0 | 118
38951.5839 | 1 | 0 | 118
38951.586 | 4 | 0 | 118
38951.5882 | 4 | 0 | 118
38951.5903 | 4 | 0 | 118
38951.5925 | 4 | 0 | 118
38951.5946 | 4 | 0 | 118
118
38951.5711 | 1 | 0 | 119
38951.5732 | 1 | 0 | 119
38951.5754 | 1 | 0 | 119
38951.5775 | 1 | 0 | 119
38951.5796 | 1 | 0 | 119
38951.5818 | 1 | 0 | 119
38951.5839 | 402 | 0 | 119
38951.5861 | 2300 | 0 | 119
38951.5882 | 2493 | 0 | 119
38951.5903 | 2360 | 0 | 119
38951.5925 | 2316 | 0 | 119
38951.5946 | 1698 | 0 | 119
119
38951.5711 | 1 | 0 | 120
38951.5732 | 1 | 0 | 120
38951.5754 | 1 | 0 | 120
38951.5775 | 1 | 0 | 120
38951.5797 | 1 | 0 | 120
38951.5818 | 1 | 0 | 120
38951.5839 | 2 | 0 | 120
38951.5861 | 4 | 0 | 120
38951.5882 | 4 | 0 | 120
38951.5903 | 3 | 0 | 120
38951.5925 | 4 | 0 | 120
38951.5946 | 4 | 0 | 120
120
38951.5711 | 1 | 0 | 121
38951.5733 | 1 | 0 | 121
38951.5754 | 1 | 0 | 121
38951.5775 | 1 | 0 | 121
38951.5797 | 1 | 0 | 121
38951.5818 | 1 | 0 | 121
38951.5839 | 1 | 0 | 121
38951.5861 | 1176 | 722 | 121
38951.5882 | 2394 | 0 | 121
38951.5904 | 1981 | 0 | 121
38951.5925 | 1976 | 0 | 121
38951.5946 | 2551 | 0 | 121
121
38951.5711 | 1 | 0 | 122
38951.5733 | 1 | 0 | 122
38951.5754 | 1 | 0 | 122
38951.5776 | 1 | 0 | 122
38951.5797 | 1 | 0 | 122
38951.5818 | 1 | 0 | 122
38951.584 | 1 | 0 | 122
38951.5861 | 1321 | 729 | 122
38951.5882 | 2173 | 0 | 122
38951.5904 | 2557 | 0 | 122
38951.5925 | 2052 | 0 | 122
38951.5947 | 2498 | 0 | 122
122
38951.5712 | 1 | 0 | 123
38951.5733 | 1 | 0 | 123
38951.5754 | 1 | 0 | 123
38951.5776 | 1 | 0 | 123
38951.5797 | 1 | 0 | 123
38951.5818 | 1 | 0 | 123
38951.584 | 1 | 0 | 123
38951.5861 | 1763 | 4 | 123
38951.5883 | 1974 | 0 | 123
38951.5904 | 2103 | 0 | 123
38951.5925 | 2138 | 0 | 123
38951.5947 | 2281 | 0 | 123
123
38951.5712 | 1 | 0 | 124
38951.5733 | 1 | 0 | 124
38951.5754 | 1 | 0 | 124
38951.5776 | 1 | 0 | 124
38951.5797 | 1 | 0 | 124
38951.5819 | 1 | 0 | 124
38951.584 | 1 | 0 | 124
38951.5861 | 4 | 2 | 124
38951.5883 | 4 | 0 | 124
38951.5904 | 4 | 0 | 124
38951.5926 | 4 | 0 | 124
38951.5947 | 4 | 0 | 124
124
38951.5712 | 2 | 0 | 125
38951.5733 | 1 | 0 | 125
38951.5755 | 1 | 0 | 125
38951.5776 | 1 | 0 | 125
38951.5797 | 1 | 0 | 125
38951.5819 | 1 | 0 | 125
38951.584 | 1 | 0 | 125
38951.5862 | 1690 | 1 | 125
38951.5883 | 2155 | 0 | 125
38951.5904 | 2554 | 0 | 125
38951.5926 | 2047 | 0 | 125
38951.5947 | 2386 | 0 | 125
125
38951.5712 | 1 | 0 | 126
38951.5733 | 1 | 0 | 126
38951.5755 | 1 | 0 | 126
38951.5776 | 1 | 0 | 126
38951.5798 | 1 | 0 | 126
38951.5819 | 1 | 0 | 126
38951.584 | 1 | 0 | 126
38951.5862 | 4 | 1 | 126
38951.5883 | 4 | 0 | 126
38951.5905 | 4 | 0 | 126
38951.5926 | 4 | 0 | 126
38951.5947 | 4 | 0 | 126
126
38951.5712 | 1 | 0 | 127
38951.5734 | 1 | 0 | 127
38951.5755 | 1 | 0 | 127
38951.5776 | 1 | 0 | 127
38951.5798 | 1 | 0 | 127
38951.5819 | 1 | 0 | 127
38951.5841 | 1 | 0 | 127
38951.5862 | 1832 | 0 | 127
38951.5883 | 2428 | 0 | 127
38951.5905 | 2071 | 0 | 127
38951.5926 | 2552 | 0 | 127
38951.5947 | 2398 | 0 | 127
127
38951.5712 | 1 | 0 | 128
38951.5734 | 1 | 0 | 128
38951.5755 | 1 | 0 | 128
38951.5777 | 1 | 0 | 128
38951.5798 | 1 | 0 | 128
38951.5819 | 1 | 0 | 128
38951.5841 | 1 | 0 | 128
38951.5862 | 4 | 0 | 128
38951.5883 | 4 | 0 | 128
38951.5905 | 3 | 0 | 128
38951.5926 | 3 | 0 | 128
38951.5948 | 4 | 0 | 128
128
38951.5713 | 1 | 0 | 129
38951.5734 | 1 | 0 | 129
38951.5755 | 1 | 0 | 129
38951.5777 | 1 | 0 | 129
38951.5798 | 1 | 0 | 129
38951.5819 | 1 | 0 | 129
38951.5841 | 1 | 0 | 129
38951.5862 | 1707 | 0 | 129
38951.5884 | 2037 | 0 | 129
38951.5905 | 2093 | 0 | 129
38951.5926 | 2447 | 0 | 129
38951.5948 | 2482 | 0 | 129
129
38951.5713 | 1 | 0 | 130
38951.5734 | 1 | 0 | 130
38951.5755 | 1 | 0 | 130
38951.5777 | 1 | 0 | 130
38951.5798 | 1 | 0 | 130
38951.582 | 1 | 0 | 130
38951.5841 | 1 | 0 | 130
38951.5862 | 4 | 0 | 130
38951.5884 | 3 | 0 | 130
38951.5905 | 3 | 0 | 130
38951.5927 | 4 | 0 | 130
38951.5948 | 4 | 0 | 130
130
38951.5713 | 1 | 0 | 131
38951.5734 | 1 | 0 | 131
38951.5756 | 1 | 0 | 131
38951.5777 | 1 | 0 | 131
38951.5798 | 1 | 0 | 131
38951.582 | 1 | 0 | 131
38951.5841 | 1 | 0 | 131
38951.5863 | 3 | 0 | 131
38951.5884 | 3 | 0 | 131
38951.5905 | 3 | 0 | 131
38951.5927 | 3 | 0 | 131
38951.5948 | 3 | 0 | 131
131
38951.5713 | 1 | 0 | 132
38951.5734 | 1 | 0 | 132
38951.5756 | 1 | 0 | 132
38951.5777 | 1 | 0 | 132
38951.5798 | 1 | 0 | 132
38951.582 | 1 | 0 | 132
38951.5841 | 1 | 0 | 132
38951.5863 | 4 | 0 | 132
38951.5884 | 3 | 0 | 132
38951.5905 | 3 | 0 | 132
38951.5927 | 3 | 0 | 132
38951.5948 | 3 | 0 | 132
132

## D8-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | #VALUE! |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38951.571 | 1 | 0 | 38951.571 | 1 | 0 |  | 25 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.5732 | 1 | 0 | 38951.5732 | 1 | 0 |  | 210 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.5753 | 1 | 0 | 38951.5753 | 1 | 0 |  | 394.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
| 1 | 0 | 38951.5775 | 1 | 0 |  | 580 | 715 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.5796 | 1 | 0 | 38951.5796 | 1 | 0 |  | 764 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.5817 | 1 | 0 | 38951.5817 | 1 | 0 |  | 949 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.5839 | 195 | 0 | 38951.5839 | 1 | 0 |  | 1133.5 | 1268.5 | 11.9048 | 0 | 0.06105 | 0 | 0.11905 | 0 | 0.0006105 | 0 | 0.11905 | 0.0006105 | #VALUE! | #VALUE! | #VALUE!
38951.586 | 2524 | 0 | 38951.586 | 2013 | 0 |  | 1318.5 | 1453.5 | 154.0904 | 0 | 122.8938 | 0 | 1.5409 | 0 | 1.2289 | 0 | 1.5409 | 1.2289 | #VALUE! | #VALUE! | #VALUE!
38951.5881 | 2427 | 0 | 38951.5881 | 2178 | 0 |  | 1503.5 | 1638.5 | 148.1685 | 0 | 132.967 | 0 | 1.4817 | 0 | 1.3297 | 0 | 1.4817 | 1.3297 | #VALUE! | #VALUE! | #VALUE!
38951.5903 | 2236 | 0 | 38951.5903 | 2248 | 0 |  | 1688 | 1823 | 136.5079 | 0 | 137.2405 | 0 | 1.3651 | 0 | 1.3724 | 0 | 1.3651 | 1.3724 | #VALUE! | #VALUE! | #VALUE!
38951.5924 | 2309 | 0 | 38951.5924 | 2215 | 0 |  | 1873 | 2008 | 140.9646 | 0 | 135.2259 | 0 | 1.4096 | 0 | 1.3523 | 0 | 1.4096 | 1.3523 | #VALUE! | #VALUE! | #VALUE!
38951.5945 | 1247 |  | 38951.5946 | 2514 | 0 |  | 2057.5 | 2192.5 | 76.1294 | #VALUE! | 153.4799 | 0 | 0.76129 | #VALUE! | 1.5348 | 0 | #VALUE! | 1.5348 | #VALUE! | #VALUE! | #VALUE!

## D8-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.0672 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38951.571 | 1 | 0 | 38951.571 | 1 | 0 |  | 22.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5731 | 1 | 0 | 38951.5731 | 1 | 0 |  | 207 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5753 | 1 | 0 | 38951.5753 | 1 | 0 |  | 392 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5774 | 1 | 0 | 38951.5774 | 1 | 0 |  | 576.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5795 | 1 | 0 | 38951.5796 | 1 | 0 |  | 761.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5817 | 1 | 0 | 38951.5817 | 1 | 0 |  | 946 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
38951.5838 | 125 | 0 | 38951.5838 | 1 | 0 |  | 1131 | 1266 | 7.6313 | 0 | 0.06105 | 0 | 0.076313 | 0 | 0.0006105 | 0 | 0.076313 | 0.0006105 | 1945.104 | 255538 | 1945.0277
38951.586 | 2175 | 0 | 38951.586 | 1129 | 0 |  | 1315.5 | 1450.5 | 132.7839 | 0 | 68.9255 | 0 | 1.3278 | 0 | 0.68926 | 0 | 1.3278 | 0.68926 | 17.5347 | 126.4287 | 16.2069
38951.5881 | 2497 | 0 | 38951.5881 | 2540 | 0 |  | 1500.5 | 1635.5 | 152.442 | 0 | 155.0672 | 0 | 1.5244 | 0 | 1.5507 | 0 | 1.5244 | 1.5507 | 2.3781 | 0.64488 | 0.85363
38951.5902 | 1982 | 0 | 38951.5903 | 2510 | 0 |  | 1685.5 | 1820.5 | 121.0012 | 0 | 153.2357 | 0 | 1.21 | 0 | 1.5324 | 0 | 1.21 | 1.5324 | 28.9798 | 1.8478 | 27.7698
38951.5924 | 1453 | 0 | 38951.5924 | 2525 | 0 |  | 1870 | 2005 | 88.7057 | 0 | 154.1514 | 0 | 0.88706 | 0 | 1.5415 | 0 | 0.88706 | 1.5415 | 75.9381 | 1.2428 | 75.051
38951.5945 | 1766 | 0 | 38951.5945 | 2375 | 0 |  | 2054.5 | 2189.5 | 107.8144 | 0 | 144.9939 | 0 | 1.0781 | 0 | 1.4499 | 0 | 1.0781 | 1.4499 | 44.7554 | 7.6371 | 43.6772

## D7-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 155.5788 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38951.5709 | 1 | 0 | 38951.5709 | 1 | 0 |  | 14 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38951.573 | 1 | 0 | 38951.573 | 1 | 0 |  | 198.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38951.5752 | 1 | 0 | 38951.5752 | 1 | 0 |  | 383.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38951.5773 | 1 | 0 | 38951.5773 | 1 | 0 |  | 568.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38951.5794 | 1 | 0 | 38951.5795 | 1 | 0 |  | 753 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
38951.5816 | 1 | 3 | 38951.5816 | 2 | 2 |  | 937.5 | 1072.5 | 0.06105 | 0.18315 | 0.1221 | 0.1221 | 0.0006105 | 0.0018315 | 0.001221 | 0.001221 | 0.001221 | 0 | 127368.8822 | 162164787.123 | 84812.6144
38951.5837 | 49 | 1 | 38951.5837 | 2 | 1 |  | 1122.5 | 1257.5 | 2.9915 | 0.06105 | 0.1221 | 0.06105 | 0.029915 | 0.0006105 | 0.001221 | 0.0006105 | 0.029304 | 0.0006105 | 5207.0835 | 259623.9769 | 249741.8063
38951.5859 | 2089 | 0 | 38951.5859 | 1171 | 0 |  | 1307.5 | 1442.5 | 127.5336 | 0 | 71.4896 | 0 | 1.2753 | 0 | 0.7149 | 0 | 1.2753 | 0.7149 | 21.9904 | 117.6243 | 20.7151
38951.588 | 2393 | 0 | 38951.588 | 2532 | 0 |  | 1492 | 1627 | 146.0928 | 0 | 154.5788 | 0 | 1.4609 | 0 | 1.5458 | 0 | 1.4609 | 1.5458 | 6.4931 | 0.64692 | 5.0322
38951.5901 | 2419 | 0 | 38951.5902 | 2161 | 0 |  | 1677 | 1812 | 147.6801 | 0 | 131.9292 | 0 | 1.4768 | 0 | 1.3193 | 0 | 1.4768 | 1.3193 | 5.3485 | 17.926 | 3.8717
38951.5923 | 1997 | 0 | 38951.5923 | 1988 | 0 |  | 1861.5 | 1996.5 | 121.917 | 0 | 121.3675 | 0 | 1.2192 | 0 | 1.2137 | 0 | 1.2192 | 1.2137 | 27.6104 | 28.1881 | 26.3912
38951.5944 | 2164 | 0 | 38951.5944 | 2389 | 0 |  | 2046.5 | 2181.5 | 132.1123 | 0 | 145.8486 | 0 | 1.3211 | 0 | 1.4585 | 0 | 1.3211 | 1.4585 | 17.7625 | 6.6714 | 16.4414

## D7-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 148.9853 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38951.5709 | 2 | 0 | 38951.5709 | 1 | 0 |  | 11 | 146 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 121919 | 243938 | 121918.9988
38951.573 | 1 | 0 | 38951.573 | 1 | 0 |  | 196 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38951.5751 | 1 | 0 | 38951.5752 | 1 | 0 |  | 380.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38951.5773 | 1 | 0 | 38951.5773 | 1 | 0 |  | 565.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38951.5794 | 1 | 0 | 38951.5794 | 1 | 0 |  | 750.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243938 | 243938 | 243937.9994
38951.5816 | 3 | 10 | 38951.5816 | 2 | 5 |  | 935 | 1070 | 0.18315 | 0.6105 | 0.1221 | 0.30525 | 0.0018315 | 0.006105 | 0.001221 | 0.0030525 | 0.0042735 | 0.0018315 | 34880.728 | 81669.5659 | 24244.1144
38951.5837 | 36 | 5 | 38951.5837 | 2 | 2 |  | 1119.5 | 1254.5 | 2.1978 | 0.30525 | 0.1221 | 0.1221 | 0.021978 | 0.0030525 | 0.001221 | 0.001221 | 0.018926 | 0 | 7756.0513 | 9456100.1677 | 47987.0925
38951.5858 | 2135 | 0 | 38951.5858 | 464 | 0 |  | 1304.5 | 1439.5 | 130.3419 | 0 | 28.3272 | 0 | 1.3034 | 0 | 0.28327 | 0 | 1.3034 | 0.28327 | 14.3035 | 425.944 | 13.0001
38951.588 | 2359 | 0 | 38951.588 | 2199 | 0 |  | 1489.5 | 1624.5 | 144.0171 | 0 | 134.2491 | 0 | 1.4402 | 0 | 1.3425 | 0 | 1.4402 | 1.3425 | 3.4498 | 10.9768 | 2.0096
38951.5901 | 2163 | 0 | 38951.5901 | 2424 | 0 |  | 1674 | 1809 | 132.0513 | 0 | 147.9853 | 0 | 1.3205 | 0 | 1.4799 | 0 | 1.3205 | 1.4799 | 12.8239 | 0.67574 | 11.5033
38951.5922 | 2294 | 0 | 38951.5923 | 2261 | 0 |  | 1859 | 1994 | 140.0488 | 0 | 138.0342 | 0 | 1.4005 | 0 | 1.3803 | 0 | 1.4005 | 1.3803 | 6.381 | 7.9337 | 4.9805
38951.5944 | 1952 | 0 | 38951.5944 | 2219 | 0 |  | 2043.5 | 2178.5 | 119.1697 | 0 | 135.4701 | 0 | 1.1917 | 0 | 1.3547 | 0 | 1.1917 | 1.3547 | 25.0195 | 9.9766 | 23.8278

## D7-D8
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 153.1368 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38951.5708 | 1 | 0 | 38951.5708 | 1 | 0 |  | 8.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38951.573 | 1 | 0 | 38951.573 | 1 | 0 |  | 193 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38951.5751 | 1 | 0 | 38951.5751 | 1 | 0 |  | 378 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38951.5772 | 1 | 0 | 38951.5773 | 1 | 0 |  | 562.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38951.5794 | 1 | 0 | 38951.5794 | 1 | 0 |  | 747.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250738 | 250738 | 250737.9994
38951.5815 | 997 | 958 | 38951.5815 | 980 | 1090 |  | 932 | 1067 | 60.8669 | 58.486 | 59.8291 | 66.5446 | 0.60867 | 0.58486 | 0.59829 | 0.66545 | 0.02381 | 0.067155 | 2765.2502 | 6118.9914 | 56.8353
38951.5837 | 854 | 746 | 38951.5837 | 956 | 850 |  | 1117 | 1252 | 52.1368 | 45.5433 | 58.3639 | 51.8926 | 0.52137 | 0.45543 | 0.58364 | 0.51893 | 0.065934 | 0.064713 | 2183.4542 | 2314.5373 | 116.7237
38951.5858 | 2415 | 0 | 38951.5858 | 2424 | 0 |  | 1301.5 | 1436.5 | 147.4359 | 0 | 147.9853 | 0 | 1.4744 | 0 | 1.4799 | 0 | 1.4744 | 1.4799 | 3.8667 | 3.481 | 2.3923
38951.5879 | 2489 | 0 | 38951.588 | 2492 | 0 |  | 1486.5 | 1621.5 | 151.9536 | 0 | 152.1368 | 0 | 1.5195 | 0 | 1.5214 | 0 | 1.5195 | 1.5214 | 0.77863 | 0.6573 | 0.74091
38951.5901 | 2192 | 0 | 38951.5901 | 2394 | 0 |  | 1671.5 | 1806.5 | 133.8217 | 0 | 146.1538 | 0 | 1.3382 | 0 | 1.4615 | 0 | 1.3382 | 1.4615 | 14.4334 | 4.7778 | 13.0952
38951.5922 | 2048 | 0 | 38951.5922 | 1640 | 0 |  | 1856 | 1991 | 125.0305 | 0 | 100.1221 | 0 | 1.2503 | 0 | 1.0012 | 0 | 1.2503 | 1.0012 | 22.4795 | 52.95 | 21.2292
38951.5944 | 1930 | 0 | 38951.5944 | 1937 | 0 |  | 2040.5 | 2175.5 | 117.8266 | 0 | 118.254 | 0 | 1.1783 | 0 | 1.1825 | 0 | 1.1783 | 1.1825 | 29.9679 | 29.4982 | 28.7896

## C6-F12
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 159.6081 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38951.5708 | 1 | 0 | 38951.5708 | 1 | 0 |  | 5.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5729 | 1 | 0 | 38951.573 | 1 | 0 |  | 190.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5751 | 1 | 0 | 38951.5751 | 1 | 0 |  | 375 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5772 | 1 | 0 | 38951.5772 | 1 | 0 |  | 560 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5794 | 1 | 0 | 38951.5794 | 1 | 0 |  | 744.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5815 | 1 | 0 | 38951.5815 | 1 | 0 |  | 929.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5836 | 1 | 0 | 38951.5836 | 1 | 0 |  | 1114 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
38951.5858 | 2598 | 1 | 38951.5858 | 4 | 0 |  | 1299 | 1434 | 158.6081 | 0.06105 | 0.2442 | 0 | 1.5861 | 0.0006105 | 0.002442 | 0 | 1.5855 | 0.002442 | 0.63073 | 65259.5 | 1535.6469
38951.5879 | 2329 | 1 | 38951.5879 | 4 | 0 |  | 1483.5 | 1618.5 | 142.1856 | 0.06105 | 0.2442 | 0 | 1.4219 | 0.0006105 | 0.002442 | 0 | 1.4212 | 0.002442 | 12.2586 | 65259.5 | 28394.4899
38951.59 | 2220 | 1 | 38951.5901 | 4 | 0 |  | 1668.5 | 1803.5 | 135.5311 | 0.06105 | 0.2442 | 0 | 1.3553 | 0.0006105 | 0.002442 | 0 | 1.3547 | 0.002442 | 17.7729 | 65259.5 | 39277.8129
38951.5922 | 1896 | 1 | 38951.5922 | 3 | 0 |  | 1853 | 1988 | 115.7509 | 0.06105 | 0.18315 | 0 | 1.1575 | 0.0006105 | 0.0018315 | 0 | 1.1569 | 0.0018315 | 37.9093 | 87046 | 71655.6807
38951.5943 | 2207 | 1 | 38951.5943 | 4 | 0 |  | 2038 | 2173 | 134.7375 | 0.06105 | 0.2442 | 0 | 1.3474 | 0.0006105 | 0.002442 | 0 | 1.3468 | 0.002442 | 18.4669 | 65259.5 | 40575.8239

## C6-F11
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 159.7912 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38951.5708 | 1 | 0 | 38951.5708 | 1 | 0 |  | 2.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5729 | 1 | 0 | 38951.5729 | 1 | 0 |  | 187.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.575 | 1 | 0 | 38951.5751 | 1 | 0 |  | 372.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5772 | 1 | 0 | 38951.5772 | 1 | 0 |  | 557 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5793 | 1 | 0 | 38951.5793 | 1 | 0 |  | 742 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5815 | 1 | 0 | 38951.5815 | 1 | 0 |  | 926.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5836 | 1 | 0 | 38951.5836 | 1 | 0 |  | 1111.5 | 1246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261638 | 261638 | 261637.9994
38951.5857 | 2601 | 1 | 38951.5858 | 5 | 0 |  | 1296 | 1431 | 158.7912 | 0.06105 | 0.30525 | 0 | 1.5879 | 0.0006105 | 0.0030525 | 0 | 1.5873 | 0.0030525 | 0.63 | 52247.6 | 1535.0619
38951.5879 | 2242 | 1 | 38951.5879 | 5 | 0 |  | 1481 | 1616 | 136.8742 | 0.06105 | 0.30525 | 0 | 1.3687 | 0.0006105 | 0.0030525 | 0 | 1.3681 | 0.0030525 | 16.7506 | 52247.6 | 37366.4819
38951.59 | 2414 | 1 | 38951.59 | 4 | 0 |  | 1665.5 | 1800.5 | 147.3748 | 0.06105 | 0.2442 | 0 | 1.4737 | 0.0006105 | 0.002442 | 0 | 1.4731 | 0.002442 | 8.4285 | 65334.5 | 20207.0714
38951.5922 | 2261 | 1 | 38951.5922 | 4 | 0 |  | 1850.5 | 1985.5 | 138.0342 | 0.06105 | 0.2442 | 0 | 1.3803 | 0.0006105 | 0.002442 | 0 | 1.3797 | 0.002442 | 15.769 | 65334.5 | 35483.6892
38951.5943 | 2052 | 1 | 38951.5943 | 4 | 0 |  | 2035.5 | 2170.5 | 125.2747 | 0.06105 | 0.2442 | 0 | 1.2527 | 0.0006105 | 0.002442 | 0 | 1.2521 | 0.002442 | 27.5661 | 65334.5 | 56351.7489

## C6-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 146.6044 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38951.5707 | 1 | 0 | 38951.5708 | 1 | 0 |  | 7.5437e-07 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5729 | 1 | 0 | 38951.5729 | 1 | 0 |  | 184.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.575 | 1 | 0 | 38951.575 | 1 | 0 |  | 369.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5771 | 1 | 0 | 38951.5772 | 1 | 0 |  | 554 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5793 | 1 | 0 | 38951.5793 | 1 | 0 |  | 739 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5814 | 1 | 0 | 38951.5814 | 1 | 0 |  | 923.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5836 | 1 | 0 | 38951.5836 | 1 | 0 |  | 1108.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240038 | 240038 | 240037.9994
38951.5857 | 2192 | 0 | 38951.5857 | 403 | 0 |  | 1293.5 | 1428.5 | 133.8217 | 0 | 24.6032 | 0 | 1.3382 | 0 | 0.24603 | 0 | 1.3382 | 0.24603 | 9.552 | 495.8759 | 8.2138
38951.5878 | 2086 | 0 | 38951.5879 | 2385 | 0 |  | 1478 | 1613 | 127.3504 | 0 | 145.6044 | 0 | 1.2735 | 0 | 1.456 | 0 | 1.2735 | 1.456 | 15.1189 | 0.68679 | 13.8454
38951.59 | 2384 | 0 | 38951.59 | 1989 | 0 |  | 1662.5 | 1797.5 | 145.5433 | 0 | 121.4286 | 0 | 1.4554 | 0 | 1.2143 | 0 | 1.4554 | 1.2143 | 0.72903 | 20.733 | 0.72641
38951.5921 | 2323 | 0 | 38951.5921 | 2077 | 0 |  | 1847.5 | 1982.5 | 141.8193 | 0 | 126.801 | 0 | 1.4182 | 0 | 1.268 | 0 | 1.4182 | 1.268 | 3.3741 | 15.6177 | 1.9559
38951.5943 | 2268 | 0 | 38951.5943 | 2203 | 1 |  | 2032.5 | 2167.5 | 138.4615 | 0 | 134.4933 | 0.06105 | 1.3846 | 0 | 1.3449 | 0.0006105 | 1.3846 | 1.3443 | 5.881 | 9.0545 | 4.4963

## C6-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.9219 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38951.5707 | 1 | 0 | 38951.5707 | 1 | 0 |  | -3 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5728 | 1 | 0 | 38951.5729 | 1 | 0 |  | 182 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.575 | 1 | 0 | 38951.575 | 1 | 0 |  | 366.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5771 | 1 | 0 | 38951.5771 | 1 | 0 |  | 551.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5792 | 1 | 0 | 38951.5793 | 1 | 0 |  | 736 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5814 | 1 | 0 | 38951.5814 | 1 | 0 |  | 921 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5835 | 1 | 0 | 38951.5835 | 1 | 0 |  | 1105.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38951.5857 | 2487 | 0 | 38951.5857 | 434 | 0 |  | 1290.5 | 1425.5 | 151.8315 | 0 | 26.4957 | 0 | 1.5183 | 0 | 0.26496 | 0 | 1.5183 | 0.26496 | 3.3526 | 492.2535 | 1.8343
38951.5878 | 2550 | 0 | 38951.5878 | 2163 | 0 |  | 1475.5 | 1610.5 | 155.6777 | 0 | 132.0513 | 0 | 1.5568 | 0 | 1.3205 | 0 | 1.5568 | 1.3205 | 0.79922 | 18.834 | 0.75756
38951.5899 | 2221 | 0 | 38951.59 | 2379 | 0 |  | 1660 | 1795 | 135.5922 | 0 | 145.2381 | 0 | 1.3559 | 0 | 1.4524 | 0 | 1.3559 | 1.4524 | 15.7308 | 8.0446 | 14.3748
38951.5921 | 2272 | 0 | 38951.5921 | 2554 | 0 |  | 1844.5 | 1979.5 | 138.7057 | 0 | 155.9219 | 0 | 1.3871 | 0 | 1.5592 | 0 | 1.3871 | 1.5592 | 13.1329 | 0.64135 | 11.7459
38951.5942 | 2158 | 0 | 38951.5942 | 2146 | 0 |  | 2029.5 | 2164.5 | 131.746 | 0 | 131.0134 | 0 | 1.3175 | 0 | 1.3101 | 0 | 1.3175 | 1.3101 | 19.1094 | 19.7754 | 17.7919

## C5-F12
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 158.4481 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38951.5706 | 1 | 0 | 38951.5706 | 1 | 0 |  | -11.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5727 | 1 | 0 | 38951.5728 | 1 | 0 |  | 173.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5749 | 1 | 0 | 38951.5749 | 1 | 0 |  | 358.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.577 | 1 | 0 | 38951.577 | 1 | 0 |  | 543 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5792 | 1 | 0 | 38951.5792 | 1 | 0 |  | 728 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5813 | 1 | 0 | 38951.5813 | 1 | 0 |  | 912.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5834 | 1 | 0 | 38951.5834 | 1 | 0 |  | 1097.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
38951.5856 | 2486 | 1 | 38951.5856 | 4 | 0 |  | 1282 | 1417 | 151.7705 | 0.06105 | 0.2442 | 0 | 1.5177 | 0.0006105 | 0.002442 | 0 | 1.5171 | 0.002442 | 4.4016 | 64784.5 | 10821.2965
38951.5877 | 2579 | 1 | 38951.5877 | 4 | 0 |  | 1467 | 1602 | 157.4481 | 0.06105 | 0.2442 | 0 | 1.5745 | 0.0006105 | 0.002442 | 0 | 1.5739 | 0.002442 | 0.63538 | 64784.5 | 1535.6296
38951.5898 | 2346 | 1 | 38951.5899 | 4 | 0 |  | 1651.5 | 1786.5 | 143.2234 | 0.06105 | 0.2442 | 0 | 1.4322 | 0.0006105 | 0.002442 | 0 | 1.4316 | 0.002442 | 10.6345 | 64784.5 | 24799.7197
38951.592 | 2199 | 1 | 38951.592 | 3 | 0 |  | 1836.5 | 1971.5 | 134.2491 | 0.06105 | 0.18315 | 0 | 1.3425 | 0.0006105 | 0.0018315 | 0 | 1.3419 | 0.0018315 | 18.0337 | 86412.6667 | 39492.298
38951.5941 | 2000 | 1 | 38951.5941 | 4 | 0 |  | 2021.5 | 2156.5 | 122.1001 | 0.06105 | 0.2442 | 0 | 1.221 | 0.0006105 | 0.002442 | 0 | 1.2204 | 0.002442 | 29.7839 | 64784.5 | 59346.3941

## C5-F11
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 159.9133 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38951.5706 | 1 | 0 | 38951.5706 | 1 | 0 |  | -14 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5727 | 1 | 0 | 38951.5727 | 1 | 0 |  | 170.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5748 | 1 | 0 | 38951.5749 | 1 | 0 |  | 355.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.577 | 1 | 0 | 38951.577 | 1 | 0 |  | 540 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5791 | 1 | 0 | 38951.5791 | 1 | 0 |  | 725 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5813 | 1 | 0 | 38951.5813 | 1 | 0 |  | 909.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5834 | 1 | 0 | 38951.5834 | 1 | 0 |  | 1094.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
38951.5855 | 2603 | 1 | 38951.5856 | 5 | 0 |  | 1279.5 | 1414.5 | 158.9133 | 0.06105 | 0.30525 | 0 | 1.5891 | 0.0006105 | 0.0030525 | 0 | 1.5885 | 0.0030525 | 0.62952 | 52287.6 | 1535.0642
38951.5877 | 2204 | 1 | 38951.5877 | 4 | 0 |  | 1464 | 1599 | 134.5543 | 0.06105 | 0.2442 | 0 | 1.3455 | 0.0006105 | 0.002442 | 0 | 1.3449 | 0.002442 | 18.8552 | 65384.5 | 41374.7209
38951.5898 | 2493 | 1 | 38951.5898 | 4 | 0 |  | 1649 | 1784 | 152.1978 | 0.06105 | 0.2442 | 0 | 1.522 | 0.0006105 | 0.002442 | 0 | 1.5214 | 0.002442 | 5.0714 | 65384.5 | 12518.8535
38951.592 | 2502 | 1 | 38951.592 | 4 | 0 |  | 1833.5 | 1968.5 | 152.7473 | 0.06105 | 0.2442 | 0 | 1.5275 | 0.0006105 | 0.002442 | 0 | 1.5269 | 0.002442 | 4.6933 | 65384.5 | 11620.2279
38951.5941 | 2410 | 1 | 38951.5941 | 4 | 0 |  | 2018.5 | 2153.5 | 147.1306 | 0.06105 | 0.2442 | 0 | 1.4713 | 0.0006105 | 0.002442 | 0 | 1.4707 | 0.002442 | 8.6916 | 65384.5 | 20806.1787

## C5-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.3114 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38951.5705 | 1 | 0 | 38951.5706 | 1 | 0 |  | -17 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38951.5727 | 1 | 0 | 38951.5727 | 1 | 0 |  | 168 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38951.5748 | 1 | 0 | 38951.5748 | 1 | 0 |  | 352.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38951.577 | 1 | 0 | 38951.577 | 1 | 0 |  | 537.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38951.5791 | 1 | 0 | 38951.5791 | 1 | 0 |  | 722 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255937.9994
38951.5812 | 2 | 1 | 38951.5813 | 1 | 0 |  | 907 | 1042 | 0.1221 | 0.06105 | 0.06105 | 0 | 0.001221 | 0.0006105 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255938 | 255938 | 255638.1172
38951.5834 | 2 | 0 | 38951.5834 | 1 | 0 |  | 1091.5 | 1226.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 127919 | 255938 | 127918.9988
38951.5855 | 2254 | 0 | 38951.5855 | 423 | 0 |  | 1276.5 | 1411.5 | 137.6068 | 0 | 25.8242 | 0 | 1.3761 | 0 | 0.25824 | 0 | 1.3761 | 0.25824 | 13.5927 | 505.2908 | 12.2167
38951.5877 | 2075 | 0 | 38951.5877 | 1970 | 0 |  | 1461.5 | 1596.5 | 126.6789 | 0 | 120.2686 | 0 | 1.2668 | 0 | 1.2027 | 0 | 1.2668 | 1.2027 | 23.3918 | 29.9685 | 22.125
38951.5898 | 2163 | 0 | 38951.5898 | 2007 | 0 |  | 1646 | 1781 | 132.0513 | 0 | 122.5275 | 0 | 1.3205 | 0 | 1.2253 | 0 | 1.3205 | 1.2253 | 18.3717 | 27.5725 | 17.0512
38951.5919 | 2134 | 0 | 38951.5919 | 2544 | 0 |  | 1830.5 | 1965.5 | 130.2808 | 0 | 155.3114 | 0 | 1.3028 | 0 | 1.5531 | 0 | 1.3028 | 1.5531 | 19.9803 | 0.64387 | 18.6775
38951.5941 | 1971 | 0 | 38951.5941 | 2167 | 0 |  | 2015.5 | 2150.5 | 120.3297 | 0 | 132.2955 | 0 | 1.2033 | 0 | 1.323 | 0 | 1.2033 | 1.323 | 29.9026 | 18.1532 | 28.6993

## C5-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 154.9072 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38951.5705 | 1 | 0 | 38951.5705 | 1 | 0 |  | -19.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38951.5726 | 1 | 0 | 38951.5727 | 1 | 0 |  | 165 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38951.5748 | 1 | 0 | 38951.5748 | 1 | 0 |  | 350 | 485 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38951.5769 | 1 | 0 | 38951.5769 | 1 | 0 |  | 534.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38951.5791 | 1 | 0 | 38951.5791 | 1 | 0 |  | 719.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
38951.5812 | 2 | 1 | 38951.5812 | 2 | 1 |  | 904 | 1039 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253338.1182
38951.5833 | 1 | 1 | 38951.5834 | 1 | 0 |  | 1089 | 1224 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 643322350.44 | 253638 | 253438.0788
38951.5855 | 2004 | 0 | 38951.5855 | 214 | 0 |  | 1273.5 | 1408.5 | 122.3443 | 0 | 13.0647 | 0 | 1.2234 | 0 | 0.13065 | 0 | 1.2234 | 0.13065 | 26.6158 | 1085.6916 | 25.3923
38951.5876 | 2179 | 0 | 38951.5876 | 2388 | 0 |  | 1458.5 | 1593.5 | 133.0281 | 0 | 145.7875 | 0 | 1.3303 | 0 | 1.4579 | 0 | 1.3303 | 1.4579 | 16.447 | 6.2554 | 15.1167
38951.5898 | 2521 | 0 | 38951.5898 | 2396 | 0 |  | 1643.5 | 1778.5 | 153.9072 | 0 | 146.2759 | 0 | 1.5391 | 0 | 1.4628 | 0 | 1.5391 | 1.4628 | 0.64974 | 5.9007 | 0.88933
38951.5919 | 2360 | 0 | 38951.5919 | 2189 | 0 |  | 1828 | 1963 | 144.0781 | 0 | 133.6386 | 0 | 1.4408 | 0 | 1.3364 | 0 | 1.4408 | 1.3364 | 7.5161 | 15.915 | 6.0753
38951.594 | 2163 | 0 | 38951.5941 | 2145 | 0 |  | 2013 | 2148 | 132.0513 | 0 | 130.9524 | 0 | 1.3205 | 0 | 1.3095 | 0 | 1.3205 | 1.3095 | 17.3084 | 18.2928 | 15.9879

## C5-C6
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 160.2186 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38951.5704 | 1 | 1 | 38951.5704 | 1 | 0 |  | -28 | 107 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 688212262.44 | 262338 | 262138.0762
38951.5725 | 1 | 0 | 38951.5726 | 1 | 0 |  | 156.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38951.5747 | 1 | 0 | 38951.5747 | 1 | 0 |  | 341.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38951.5768 | 1 | 0 | 38951.5768 | 1 | 0 |  | 526.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38951.579 | 1 | 0 | 38951.579 | 1 | 0 |  | 711 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
38951.5811 | 1196 | 1177 | 38951.5811 | 948 | 923 |  | 896 | 1031 | 73.0159 | 71.8559 | 57.8755 | 56.3492 | 0.73016 | 0.71856 | 0.57875 | 0.56349 | 0.0116 | 0.015263 | 53916.6549 | 7198.4409 | 21.0651
38951.5832 | 996 | 967 | 38951.5833 | 1068 | 1042 |  | 1080.5 | 1215.5 | 60.8059 | 59.0354 | 65.2015 | 63.6142 | 0.60806 | 0.59035 | 0.65201 | 0.63614 | 0.017705 | 0.015873 | 7636.4855 | 12597.188 | 67.8564
38951.5854 | 2051 | 0 | 38951.5854 | 2608 | 0 |  | 1265.5 | 1400.5 | 125.2137 | 0 | 159.2186 | 0 | 1.2521 | 0 | 1.5922 | 0 | 1.2521 | 1.5922 | 27.9561 | 0.62807 | 26.704
38951.5875 | 2157 | 0 | 38951.5875 | 2068 | 0 |  | 1450 | 1585 | 131.685 | 0 | 126.2515 | 0 | 1.3168 | 0 | 1.2625 | 0 | 1.3168 | 1.2625 | 21.6681 | 26.9043 | 20.3512
38951.5897 | 2591 | 0 | 38951.5897 | 2132 | 0 |  | 1635 | 1770 | 158.1807 | 0 | 130.1587 | 0 | 1.5818 | 0 | 1.3016 | 0 | 1.5818 | 1.3016 | 1.2883 | 23.0947 | 0.2935
38951.5918 | 2598 | 0 | 38951.5918 | 2505 | 0 |  | 1819.5 | 1954.5 | 158.6081 | 0 | 152.9304 | 0 | 1.5861 | 0 | 1.5293 | 0 | 1.5861 | 1.5293 | 1.0154 | 4.7657 | 0.57068
38951.5939 | 2018 | 0 | 38951.5939 | 2319 | 0 |  | 2004.5 | 2139.5 | 123.199 | 0 | 141.5751 | 0 | 1.232 | 0 | 1.4158 | 0 | 1.232 | 1.4158 | 30.0486 | 13.1686 | 28.8166

## B4-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 147.2759 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38951.5703 | 1 | 0 | 38951.5703 | 1 | 0 |  | -36.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5725 | 1 | 0 | 38951.5725 | 1 | 0 |  | 148.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5746 | 1 | 0 | 38951.5746 | 1 | 0 |  | 333 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5767 | 1 | 0 | 38951.5767 | 1 | 0 |  | 518 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5789 | 1 | 0 | 38951.5789 | 1 | 0 |  | 702.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.581 | 1 | 0 | 38951.581 | 1 | 0 |  | 887.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5831 | 1 | 0 | 38951.5832 | 1 | 0 |  | 1072 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
38951.5853 | 3 | 0 | 38951.5853 | 225 | 0 |  | 1257 | 1392 | 0.18315 | 0 | 13.7363 | 0 | 0.0018315 | 0 | 0.13736 | 0 | 0.0018315 | 0.13736 | 80312.6667 | 972.1689 | 80312.6648
38951.5874 | 127 | 0 | 38951.5874 | 2396 | 0 |  | 1441.5 | 1576.5 | 7.7534 | 0 | 146.2759 | 0 | 0.077534 | 0 | 1.4628 | 0 | 0.077534 | 1.4628 | 1799.5118 | 0.68364 | 1799.4343
38951.5896 | 5 | 0 | 38951.5896 | 2205 | 0 |  | 1626.5 | 1761.5 | 0.30525 | 0 | 134.6154 | 0 | 0.0030525 | 0 | 1.3462 | 0 | 0.0030525 | 1.3462 | 48147.6 | 9.405 | 48147.5969
38951.5917 | 3 | 0 | 38951.5917 | 2018 | 0 |  | 1811.5 | 1946.5 | 0.18315 | 0 | 123.199 | 0 | 0.0018315 | 0 | 1.232 | 0 | 0.0018315 | 1.232 | 80312.6667 | 19.5431 | 80312.6648
38951.5938 | 3 | 0 | 38951.5939 | 2304 | 0 |  | 1996 | 2131 | 0.18315 | 0 | 140.6593 | 0 | 0.0018315 | 0 | 1.4066 | 0 | 0.0018315 | 1.4066 | 80312.6667 | 4.704 | 80312.6648

## B4-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 143.8571 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38951.5703 | 1 | 0 | 38951.5703 | 1 | 0 |  | -39.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5724 | 1 | 0 | 38951.5724 | 1 | 0 |  | 145.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5746 | 1 | 0 | 38951.5746 | 1 | 0 |  | 330.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5767 | 1 | 0 | 38951.5767 | 1 | 0 |  | 515 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5788 | 1 | 0 | 38951.5789 | 1 | 0 |  | 700 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.581 | 1 | 0 | 38951.581 | 1 | 0 |  | 884.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5831 | 1 | 0 | 38951.5831 | 1 | 0 |  | 1069.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235538 | 235538 | 235537.9994
38951.5852 | 4 | 0 | 38951.5853 | 135 | 0 |  | 1254 | 1389 | 0.2442 | 0 | 8.2418 | 0 | 0.002442 | 0 | 0.082418 | 0 | 0.002442 | 0.082418 | 58809.5 | 1645.4667 | 58809.4976
38951.5874 | 147 | 0 | 38951.5874 | 1996 | 0 |  | 1439 | 1574 | 8.9744 | 0 | 121.8559 | 0 | 0.089744 | 0 | 1.2186 | 0 | 0.089744 | 1.2186 | 1502.9796 | 18.0551 | 1502.8898
38951.5895 | 8 | 0 | 38951.5895 | 2242 | 0 |  | 1623.5 | 1758.5 | 0.4884 | 0 | 136.8742 | 0 | 0.004884 | 0 | 1.3687 | 0 | 0.004884 | 1.3687 | 29354.75 | 5.1017 | 29354.7451
38951.5917 | 46 | 0 | 38951.5917 | 2340 | 0 |  | 1808.5 | 1943.5 | 2.8083 | 0 | 142.8571 | 0 | 0.028083 | 0 | 1.4286 | 0 | 0.028083 | 1.4286 | 5022.5652 | 0.7 | 5022.5371
38951.5938 | 3 | 0 | 38951.5938 | 2283 | 0 |  | 1993 | 2128 | 0.18315 | 0 | 139.3773 | 0 | 0.0018315 | 0 | 1.3938 | 0 | 0.0018315 | 1.3938 | 78446 | 3.2142 | 78445.9982

## B4-D8
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 137.569 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38951.5702 | 1 | 0 | 38951.5703 | 1 | 0 |  | -42 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5724 | 1 | 0 | 38951.5724 | 1 | 0 |  | 142.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5745 | 1 | 0 | 38951.5745 | 1 | 0 |  | 327.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5767 | 1 | 0 | 38951.5767 | 1 | 0 |  | 512 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5788 | 1 | 0 | 38951.5788 | 1 | 0 |  | 697 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5809 | 1 | 0 | 38951.581 | 1 | 0 |  | 882 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 225238 | 225238 | 225237.9994
38951.5831 | 1 | 0 | 38951.5831 | 2 | 0 |  | 1066.5 | 1201.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 225238 | 112569 | 225237.9994
38951.5852 | 4 | 0 | 38951.5852 | 1993 | 0 |  | 1251.5 | 1386.5 | 0.2442 | 0 | 121.6728 | 0 | 0.002442 | 0 | 1.2167 | 0 | 0.002442 | 1.2167 | 56234.5 | 13.0647 | 56234.4976
38951.5873 | 125 | 0 | 38951.5874 | 1961 | 0 |  | 1436 | 1571 | 7.6313 | 0 | 119.7192 | 0 | 0.076313 | 0 | 1.1972 | 0 | 0.076313 | 1.1972 | 1702.704 | 14.9097 | 1702.6277
38951.5895 | 7 | 0 | 38951.5895 | 2237 | 0 |  | 1621 | 1756 | 0.42735 | 0 | 136.569 | 0 | 0.0042735 | 0 | 1.3657 | 0 | 0.0042735 | 1.3657 | 32091.1429 | 0.73223 | 32091.1386
38951.5916 | 3 | 0 | 38951.5916 | 2125 | 0 |  | 1805.5 | 1940.5 | 0.18315 | 0 | 129.7314 | 0 | 0.0018315 | 0 | 1.2973 | 0 | 0.0018315 | 1.2973 | 75012.6667 | 6.0414 | 75012.6648
38951.5938 | 24 | 0 | 38951.5938 | 1924 | 0 |  | 1990.5 | 2125.5 | 1.4652 | 0 | 117.4603 | 0 | 0.014652 | 0 | 1.1746 | 0 | 0.014652 | 1.1746 | 9289.0833 | 17.1195 | 9289.0687

## B4-D7
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 150.3284 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38951.5702 | 1 | 0 | 38951.5702 | 1 | 0 |  | -45 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.5723 | 1 | 0 | 38951.5724 | 1 | 0 |  | 140 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.5745 | 1 | 0 | 38951.5745 | 1 | 0 |  | 324.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.5766 | 1 | 0 | 38951.5766 | 1 | 0 |  | 509.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.5788 | 1 | 0 | 38951.5788 | 1 | 0 |  | 694.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.5809 | 1 | 0 | 38951.5809 | 1 | 0 |  | 879 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
38951.583 | 1 | 0 | 38951.5831 | 2 | 0 |  | 1063.5 | 1198.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 246138 | 123019 | 246137.9994
38951.5852 | 4 | 0 | 38951.5852 | 1957 | 0 |  | 1248.5 | 1383.5 | 0.2442 | 0 | 119.475 | 0 | 0.002442 | 0 | 1.1947 | 0 | 0.002442 | 1.1947 | 61459.5 | 25.8242 | 61459.4976
38951.5873 | 107 | 0 | 38951.5873 | 2446 | 0 |  | 1433.5 | 1568.5 | 6.5324 | 0 | 149.3284 | 0 | 0.065324 | 0 | 1.4933 | 0 | 0.065324 | 1.4933 | 2201.2897 | 0.66966 | 2201.2244
38951.5895 | 7 | 0 | 38951.5895 | 2224 | 0 |  | 1618 | 1753 | 0.42735 | 0 | 135.7753 | 0 | 0.0042735 | 0 | 1.3578 | 0 | 0.0042735 | 1.3578 | 35076.8571 | 10.7185 | 35076.8529
38951.5916 | 5 | 0 | 38951.5916 | 2361 | 0 |  | 1803 | 1938 | 0.30525 | 0 | 144.1392 | 0 | 0.0030525 | 0 | 1.4414 | 0 | 0.0030525 | 1.4414 | 49147.6 | 4.2939 | 49147.5969
38951.5937 | 4 | 0 | 38951.5938 | 2144 | 0 |  | 1987.5 | 2122.5 | 0.2442 | 0 | 130.8913 | 0 | 0.002442 | 0 | 1.3089 | 0 | 0.002442 | 1.3089 | 61459.5 | 14.8498 | 61459.4976

## B4-C6
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 157.7155 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38951.5702 | 1 | 0 | 38951.5702 | 1 | 0 |  | -47.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5723 | 1 | 0 | 38951.5723 | 1 | 0 |  | 137 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5745 | 1 | 0 | 38951.5745 | 1 | 0 |  | 322 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5766 | 1 | 0 | 38951.5766 | 1 | 0 |  | 506.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5787 | 1 | 0 | 38951.5788 | 1 | 0 |  | 691.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5809 | 1 | 0 | 38951.5809 | 1 | 0 |  | 876 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.583 | 1 | 0 | 38951.583 | 1 | 0 |  | 1061 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258238 | 258238 | 258237.9994
38951.5852 | 4 | 0 | 38951.5852 | 2276 | 0 |  | 1245.5 | 1380.5 | 0.2442 | 0 | 138.9499 | 0 | 0.002442 | 0 | 1.3895 | 0 | 0.002442 | 1.3895 | 64484.5 | 13.5053 | 64484.4976
38951.5873 | 164 | 0 | 38951.5873 | 2567 | 0 |  | 1430.5 | 1565.5 | 10.0122 | 0 | 156.7155 | 0 | 0.10012 | 0 | 1.5672 | 0 | 0.10012 | 1.5672 | 1475.2317 | 0.6381 | 1475.1316
38951.5894 | 9 | 0 | 38951.5894 | 2250 | 0 |  | 1615.5 | 1750.5 | 0.54945 | 0 | 137.3626 | 0 | 0.0054945 | 0 | 1.3736 | 0 | 0.0054945 | 1.3736 | 28604.2222 | 14.8169 | 28604.2167
38951.5916 | 4 | 0 | 38951.5916 | 2284 | 0 |  | 1800 | 1935 | 0.2442 | 0 | 139.4383 | 0 | 0.002442 | 0 | 1.3944 | 0 | 0.002442 | 1.3944 | 64484.5 | 13.1077 | 64484.4976
38951.5937 | 4 | 0 | 38951.5937 | 2280 | 0 |  | 1985 | 2120 | 0.2442 | 0 | 139.1941 | 0 | 0.002442 | 0 | 1.3919 | 0 | 0.002442 | 1.3919 | 64484.5 | 13.3061 | 64484.4976

## B4-C5
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 146.9096 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38951.5702 | 1 | 0 | 38951.5702 | 1 | 0 |  | -50.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5723 | 1 | 0 | 38951.5723 | 1 | 0 |  | 134.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5744 | 1 | 0 | 38951.5744 | 1 | 0 |  | 319 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5766 | 1 | 0 | 38951.5766 | 1 | 0 |  | 504 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5787 | 1 | 0 | 38951.5787 | 1 | 0 |  | 688.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5808 | 1 | 0 | 38951.5809 | 1 | 0 |  | 873.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.583 | 1 | 0 | 38951.583 | 1 | 0 |  | 1058 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240538 | 240538 | 240537.9994
38951.5851 | 2 | 0 | 38951.5851 | 2208 | 0 |  | 1243 | 1378 | 0.1221 | 0 | 134.7985 | 0 | 0.001221 | 0 | 1.348 | 0 | 0.001221 | 1.348 | 120219 | 8.9846 | 120218.9988
38951.5873 | 178 | 0 | 38951.5873 | 2390 | 0 |  | 1427.5 | 1562.5 | 10.8669 | 0 | 145.9096 | 0 | 0.10867 | 0 | 1.4591 | 0 | 0.10867 | 1.4591 | 1251.8989 | 0.68536 | 1251.7902
38951.5894 | 58 | 0 | 38951.5894 | 2088 | 0 |  | 1612.5 | 1747.5 | 3.5409 | 0 | 127.4725 | 0 | 0.035409 | 0 | 1.2747 | 0 | 0.035409 | 1.2747 | 4048.931 | 15.2481 | 4048.8956
38951.5915 | 4 | 0 | 38951.5916 | 2047 | 0 |  | 1797.5 | 1932.5 | 0.2442 | 0 | 124.9695 | 0 | 0.002442 | 0 | 1.2497 | 0 | 0.002442 | 1.2497 | 60059.5 | 17.5564 | 60059.4976
38951.5937 | 3 | 0 | 38951.5937 | 2199 | 0 |  | 1982 | 2117 | 0.18315 | 0 | 134.2491 | 0 | 0.0018315 | 0 | 1.3425 | 0 | 0.0018315 | 1.3425 | 80112.6667 | 9.4307 | 80112.6648

## B3-E10
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.7998 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38951.57 | 1 | 0 | 38951.5701 | 1 | 0 |  | -59 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5722 | 1 | 0 | 38951.5722 | 1 | 0 |  | 126 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5743 | 2 | 0 | 38951.5743 | 1 | 0 |  | 310.5 | 445.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128319 | 256738 | 128318.9988
38951.5765 | 1 | 0 | 38951.5765 | 1 | 0 |  | 495.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5786 | 1 | 0 | 38951.5786 | 1 | 0 |  | 680.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5807 | 1 | 0 | 38951.5808 | 1 | 0 |  | 865 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.5829 | 1 | 0 | 38951.5829 | 1 | 0 |  | 1049.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256738 | 256738 | 256737.9994
38951.585 | 2 | 0 | 38951.585 | 2 | 0 |  | 1234.5 | 1369.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128319 | 128319 | 128318.9988
38951.5872 | 100 | 0 | 38951.5872 | 2552 | 0 |  | 1419.5 | 1554.5 | 6.105 | 0 | 155.7998 | 0 | 0.06105 | 0 | 1.558 | 0 | 0.06105 | 1.558 | 2468.38 | 0.64185 | 2468.3189
38951.5893 | 45 | 0 | 38951.5893 | 2190 | 0 |  | 1604 | 1739 | 2.7473 | 0 | 133.6996 | 0 | 0.027473 | 0 | 1.337 | 0 | 0.027473 | 1.337 | 5607.5111 | 17.2776 | 5607.4836
38951.5914 | 4 | 1 | 38951.5914 | 2337 | 0 |  | 1788.5 | 1923.5 | 0.2442 | 0.06105 | 142.674 | 0 | 0.002442 | 0.0006105 | 1.4267 | 0 | 0.0018315 | 1.4267 | 36116.6651 | 24.3886 | 50259.7123
38951.5936 | 4 | 0 | 38951.5936 | 2463 | 0 |  | 1973.5 | 2108.5 | 0.2442 | 0 | 150.3663 | 0 | 0.002442 | 0 | 1.5037 | 0 | 0.002442 | 1.5037 | 64109.5 | 4.2785 | 64109.4976

## B3-E9
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 148.9243 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38951.57 | 1 | 0 | 38951.57 | 1 | 0 |  | -61.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5722 | 1 | 0 | 38951.5722 | 1 | 0 |  | 123 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5743 | 1 | 0 | 38951.5743 | 1 | 0 |  | 308 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5764 | 1 | 0 | 38951.5764 | 1 | 0 |  | 492.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5786 | 1 | 0 | 38951.5786 | 1 | 0 |  | 677.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5807 | 1 | 0 | 38951.5807 | 1 | 0 |  | 862 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.5828 | 1 | 0 | 38951.5829 | 1 | 0 |  | 1047 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243838 | 243838 | 243837.9994
38951.585 | 4 | 0 | 38951.585 | 2 | 0 |  | 1231.5 | 1366.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 60884.5 | 121869 | 60884.4976
38951.5871 | 67 | 0 | 38951.5871 | 2374 | 0 |  | 1416.5 | 1551.5 | 4.0904 | 0 | 144.9328 | 0 | 0.040904 | 0 | 1.4493 | 0 | 0.040904 | 1.4493 | 3540.8657 | 2.754 | 3540.8248
38951.5893 | 10 | 0 | 38951.5893 | 2423 | 0 |  | 1601.5 | 1736.5 | 0.6105 | 0 | 147.9243 | 0 | 0.006105 | 0 | 1.4792 | 0 | 0.006105 | 1.4792 | 24293.8 | 0.67602 | 24293.7939
38951.5914 | 4 | 0 | 38951.5914 | 2029 | 0 |  | 1786 | 1921 | 0.2442 | 0 | 123.8706 | 0 | 0.002442 | 0 | 1.2387 | 0 | 0.002442 | 1.2387 | 60884.5 | 20.2257 | 60884.4976
38951.5935 | 3 | 0 | 38951.5936 | 2051 | 0 |  | 1971 | 2106 | 0.18315 | 0 | 125.2137 | 0 | 0.0018315 | 0 | 1.2521 | 0 | 0.0018315 | 1.2521 | 81212.6667 | 18.9361 | 81212.6648

## B3-D8
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 145.2613 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38951.57 | 1 | 0 | 38951.57 | 1 | 0 |  | -64.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5721 | 1 | 0 | 38951.5721 | 1 | 0 |  | 120.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5743 | 1 | 0 | 38951.5743 | 1 | 0 |  | 305 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5764 | 1 | 0 | 38951.5764 | 1 | 0 |  | 489.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5785 | 1 | 0 | 38951.5786 | 1 | 0 |  | 674.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5807 | 1 | 0 | 38951.5807 | 1 | 0 |  | 859.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.5828 | 1 | 0 | 38951.5828 | 1 | 0 |  | 1044 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 237838 | 237838 | 237837.9994
38951.585 | 3 | 0 | 38951.585 | 1545 | 0 |  | 1229 | 1364 | 0.18315 | 0 | 94.3223 | 0 | 0.0018315 | 0 | 0.94322 | 0 | 0.0018315 | 0.94322 | 79212.6667 | 54.0052 | 79212.6648
38951.5871 | 90 | 0 | 38951.5871 | 2363 | 1 |  | 1413.5 | 1548.5 | 5.4945 | 0 | 144.2613 | 0.06105 | 0.054945 | 0 | 1.4426 | 0.0006105 | 0.054945 | 1.442 | 2543.7556 | 0.73582 | 2543.7006
38951.5892 | 16 | 0 | 38951.5892 | 2036 | 1 |  | 1598.5 | 1733.5 | 0.9768 | 0 | 124.2979 | 0.06105 | 0.009768 | 0 | 1.243 | 0.0006105 | 0.009768 | 1.2424 | 14771.125 | 16.9229 | 14771.1152
38951.5914 | 4 | 0 | 38951.5914 | 2105 | 0 |  | 1783 | 1918 | 0.2442 | 0 | 128.5104 | 0 | 0.002442 | 0 | 1.2851 | 0 | 0.002442 | 1.2851 | 59384.5 | 13.0347 | 59384.4976
38951.5935 | 3 | 0 | 38951.5935 | 1864 | 0 |  | 1968 | 2103 | 0.18315 | 0 | 113.7973 | 0 | 0.0018315 | 0 | 1.138 | 0 | 0.0018315 | 1.138 | 79212.6667 | 27.6491 | 79212.6648

## B3-D7
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 148.8632 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38951.57 | 1 | 0 | 38951.57 | 1 | 0 |  | -67.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5721 | 1 | 0 | 38951.5721 | 1 | 0 |  | 117.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5742 | 1 | 0 | 38951.5742 | 1 | 0 |  | 302 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5764 | 1 | 0 | 38951.5764 | 1 | 0 |  | 487 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5785 | 1 | 0 | 38951.5785 | 1 | 0 |  | 671.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5806 | 1 | 0 | 38951.5807 | 1 | 0 |  | 856.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5828 | 1 | 0 | 38951.5828 | 1 | 0 |  | 1041.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 243738 | 243738 | 243737.9994
38951.5849 | 1 | 1 | 38951.5849 | 1764 | 1 |  | 1226 | 1361 | 0.06105 | 0.06105 | 107.6923 | 0.06105 | 0.0006105 | 0.0006105 | 1.0769 | 0.0006105 | 0 | 1.0763 | 93234.2215 | 38.2518 | 67410.3021
38951.5871 | 56 | 2 | 38951.5871 | 2422 | 1 |  | 1411 | 1546 | 3.4188 | 0.1221 | 147.8632 | 0.06105 | 0.034188 | 0.001221 | 1.4786 | 0.0006105 | 0.032967 | 1.478 | 986.016 | 1.066 | 1255.3636
38951.5892 | 48 | 1 | 38951.5892 | 2008 | 1 |  | 1595.5 | 1730.5 | 2.9304 | 0.06105 | 122.5885 | 0.06105 | 0.029304 | 0.0006105 | 1.2259 | 0.0006105 | 0.028694 | 1.2253 | 5646.1152 | 21.4441 | 42190.7473
38951.5913 | 4 | 1 | 38951.5914 | 2201 | 0 |  | 1780.5 | 1915.5 | 0.2442 | 0.06105 | 134.3712 | 0 | 0.002442 | 0.0006105 | 1.3437 | 0 | 0.0018315 | 1.3437 | 38813.1271 | 30.5618 | 56960.4323
38951.5935 | 4 | 1 | 38951.5935 | 1972 | 0 |  | 1965 | 2100 | 0.2442 | 0.06105 | 120.3907 | 0 | 0.002442 | 0.0006105 | 1.2039 | 0 | 0.0018315 | 1.2039 | 198189.1115 | 56.4433 | 87794.1427

## B3-C6
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 156.1893 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38951.5699 | 1 | 0 | 38951.5699 | 1 | 0 |  | -70 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5721 | 1 | 0 | 38951.5721 | 1 | 0 |  | 114.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5742 | 1 | 0 | 38951.5742 | 1 | 0 |  | 299.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5763 | 1 | 0 | 38951.5764 | 1 | 0 |  | 484.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5785 | 1 | 0 | 38951.5785 | 1 | 0 |  | 669 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5806 | 1 | 0 | 38951.5806 | 1 | 0 |  | 853.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5828 | 1 | 0 | 38951.5828 | 1 | 0 |  | 1038.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38951.5849 | 2 | 2 | 38951.5849 | 2 | 1 |  | 1223.5 | 1358.5 | 0.1221 | 0.1221 | 0.1221 | 0.06105 | 0.001221 | 0.001221 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 326753835.22 | 255637.9218 | 127669.0586
38951.587 | 5 | 2 | 38951.587 | 2501 | 1 |  | 1408 | 1543 | 0.30525 | 0.1221 | 152.6862 | 0.06105 | 0.0030525 | 0.001221 | 1.5269 | 0.0006105 | 0.0018315 | 1.5263 | 3034.6975 | 2.4649 | 3068.7931
38951.5892 | 25 | 2 | 38951.5892 | 2404 | 2 |  | 1593 | 1728 | 1.5263 | 0.1221 | 146.7643 | 0.1221 | 0.015263 | 0.001221 | 1.4676 | 0.001221 | 0.014042 | 1.4664 | 31206.5497 | 13.4391 | 14994.6423
38951.5913 | 3 | 2 | 38951.5913 | 2542 | 1 |  | 1777.5 | 1912.5 | 0.18315 | 0.1221 | 155.1893 | 0.06105 | 0.0018315 | 0.001221 | 1.5519 | 0.0006105 | 0.0006105 | 1.5513 | 826.2587 | 0.64878 | 822.9511
38951.5934 | 3 | 2 | 38951.5935 | 1958 | 1 |  | 1962.5 | 2097.5 | 0.18315 | 0.1221 | 119.536 | 0.06105 | 0.0018315 | 0.001221 | 1.1954 | 0.0006105 | 0.0006105 | 1.1947 | 46299.7279 | 44.2555 | 39167.0054

## B3-C5
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 153.6862 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38951.5699 | 1 | 0 | 38951.5699 | 1 | 0 |  | -73 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.572 | 1 | 0 | 38951.572 | 1 | 0 |  | 112 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5742 | 1 | 0 | 38951.5742 | 1 | 0 |  | 296.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5763 | 1 | 0 | 38951.5763 | 1 | 0 |  | 481.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5784 | 1 | 0 | 38951.5785 | 1 | 0 |  | 666 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5806 | 1 | 0 | 38951.5806 | 1 | 0 |  | 851 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5827 | 1 | 0 | 38951.5827 | 1 | 0 |  | 1035.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251638 | 251638 | 251637.9994
38951.5849 | 3 | 9 | 38951.5849 | 2 | 4 |  | 1220.5 | 1355.5 | 0.18315 | 0.54945 | 0.1221 | 0.2442 | 0.0018315 | 0.0054945 | 0.001221 | 0.002442 | 0.003663 | 0.001221 | 41956.1343 | 126371.3977 | 27815.5446
38951.587 | 28 | 8 | 38951.587 | 2223 | 4 |  | 1405.5 | 1540.5 | 1.7094 | 0.4884 | 135.7143 | 0.2442 | 0.017094 | 0.004884 | 1.3571 | 0.002442 | 0.01221 | 1.3547 | 6176.3906 | 39.3996 | 8766.6497
38951.5891 | 27 | 8 | 38951.5892 | 2501 | 4 |  | 1590 | 1725 | 1.6484 | 0.4884 | 152.6862 | 0.2442 | 0.016484 | 0.004884 | 1.5269 | 0.002442 | 0.0116 | 1.5244 | 207.2763 | 0.67655 | 208.5195
38951.5913 | 102 | 7 | 38951.5913 | 2019 | 3 |  | 1774.5 | 1909.5 | 6.2271 | 0.42735 | 123.2601 | 0.18315 | 0.062271 | 0.0042735 | 1.2326 | 0.0018315 | 0.057998 | 1.2308 | 3622.0511 | 24.7222 | 6819.7895
38951.5934 | 3 | 8 | 38951.5934 | 2273 | 3 |  | 1959.5 | 2094.5 | 0.18315 | 0.4884 | 138.7668 | 0.18315 | 0.0018315 | 0.004884 | 1.3877 | 0.0018315 | 0.0030525 | 1.3858 | 3627.5626 | 12.4391 | 3466.0059

## B3-B4
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38951.5699 | 1 | 0 | 38951.5699 | 1 | 0 |  | -75.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.572 | 1 | 0 | 38951.572 | 1 | 0 |  | 109 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5741 | 1 | 0 | 38951.5742 | 1 | 0 |  | 294 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5763 | 1 | 0 | 38951.5763 | 1 | 0 |  | 478.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5784 | 1 | 0 | 38951.5784 | 1 | 0 |  | 663.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5805 | 1 | 0 | 38951.5806 | 1 | 0 |  | 848 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5827 | 1 | 0 | 38951.5827 | 1 | 0 |  | 1033 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5848 | 1074 | 1169 | 38951.5848 | 1157 | 1205 |  | 1217.5 | 1352.5 | 65.5678 | 71.3675 | 70.6349 | 73.5653 | 0.65568 | 0.71368 | 0.70635 | 0.73565 | 0.057998 | 0.029304 | 1196.5494 | 14316.6698 | 11.0418
38951.587 | 1207 | 1125 | 38951.587 | 1080 | 996 |  | 1402.5 | 1537.5 | 73.6874 | 68.6813 | 65.9341 | 60.8059 | 0.73687 | 0.68681 | 0.65934 | 0.60806 | 0.050061 | 0.051282 | 1884.7675 | 3315.7134 | 18.895
38951.5891 | 985 | 886 | 38951.5891 | 1043 | 938 |  | 1587.5 | 1722.5 | 60.1343 | 54.0904 | 63.6752 | 57.265 | 0.60134 | 0.5409 | 0.63675 | 0.57265 | 0.06044 | 0.064103 | 2913.785 | 1469.6423 | 25.5758
38951.5912 | 995 | 878 | 38951.5913 | 1172 | 1024 |  | 1772 | 1907 | 60.7448 | 53.602 | 71.5507 | 62.5153 | 0.60745 | 0.53602 | 0.71551 | 0.62515 | 0.071429 | 0.090354 | 771.0244 | 3135.2125 | 26.4921
38951.5934 | 1208 | 1203 | 38951.5934 | 993 | 956 |  | 1956.5 | 2091.5 | 73.7485 | 73.4432 | 60.6227 | 58.3639 | 0.73748 | 0.73443 | 0.60623 | 0.58364 | 0.0030525 | 0.022589 | 350.6151 | 475.2621 | 20.4639

## A2-C6
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 153.6252 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38951.5696 | 1 | 0 | 38951.5696 | 1 | 0 |  | -95.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5718 | 1 | 0 | 38951.5718 | 1 | 0 |  | 89.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5739 | 1 | 0 | 38951.5739 | 1 | 0 |  | 274.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.576 | 1 | 0 | 38951.5761 | 1 | 0 |  | 459 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5782 | 1 | 0 | 38951.5782 | 1 | 0 |  | 643.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5803 | 1 | 0 | 38951.5803 | 1 | 0 |  | 828.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5825 | 1 | 0 | 38951.5825 | 1 | 0 |  | 1013.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5846 | 1 | 0 | 38951.5846 | 1 | 0 |  | 1198 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251538 | 251538 | 251537.9994
38951.5867 | 391 | 0 | 38951.5868 | 2187 | 0 |  | 1383 | 1518 | 23.8706 | 0 | 133.5165 | 0 | 0.23871 | 0 | 1.3352 | 0 | 0.23871 | 1.3352 | 543.5754 | 15.0608 | 543.3367
38951.5889 | 13 | 0 | 38951.5889 | 2500 | 0 |  | 1567.5 | 1702.5 | 0.79365 | 0 | 152.6252 | 0 | 0.0079365 | 0 | 1.5263 | 0 | 0.0079365 | 1.5263 | 19256.7692 | 0.6552 | 19256.7613
38951.591 | 6 | 0 | 38951.591 | 2496 | 0 |  | 1752.5 | 1887.5 | 0.3663 | 0 | 152.381 | 0 | 0.003663 | 0 | 1.5238 | 0 | 0.003663 | 1.5238 | 41839.6667 | 0.81651 | 41839.663
38951.5932 | 4 | 0 | 38951.5932 | 2438 | 0 |  | 1937.5 | 2072.5 | 0.2442 | 0 | 148.84 | 0 | 0.002442 | 0 | 1.4884 | 0 | 0.002442 | 1.4884 | 62809.5 | 3.2149 | 62809.4976

## A2-C5
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 158.8755 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38951.5696 | 1 | 0 | 38951.5696 | 1 | 0 |  | -98 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5717 | 1 | 0 | 38951.5717 | 1 | 0 |  | 86.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5739 | 1 | 0 | 38951.5739 | 1 | 0 |  | 271.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.576 | 1 | 0 | 38951.576 | 1 | 0 |  | 456.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5781 | 1 | 0 | 38951.5782 | 1 | 0 |  | 641 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5803 | 1 | 0 | 38951.5803 | 1 | 0 |  | 825.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5824 | 1 | 0 | 38951.5824 | 1 | 0 |  | 1010.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5846 | 1 | 0 | 38951.5846 | 1 | 0 |  | 1195.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
38951.5867 | 416 | 0 | 38951.5867 | 2180 | 0 |  | 1380 | 1515 | 25.3968 | 0 | 133.0891 | 0 | 0.25397 | 0 | 1.3309 | 0 | 0.25397 | 1.3309 | 525.5721 | 19.3752 | 525.3181
38951.5888 | 9 | 3 | 38951.5889 | 2115 | 1 |  | 1565 | 1700 | 0.54945 | 0.18315 | 129.1209 | 0.06105 | 0.0054945 | 0.0018315 | 1.2912 | 0.0006105 | 0.003663 | 1.2906 | 36982.5072 | 296.3108 | 64558.5539
38951.591 | 3 | 1 | 38951.591 | 2586 | 1 |  | 1749.5 | 1884.5 | 0.18315 | 0.06105 | 157.8755 | 0.06105 | 0.0018315 | 0.0006105 | 1.5788 | 0.0006105 | 0.001221 | 1.5781 | 1668.2148 | 0.65012 | 1678.3442
38951.5931 | 3 | 0 | 38951.5931 | 2322 | 0 |  | 1934.5 | 2069.5 | 0.18315 | 0 | 141.7582 | 0 | 0.0018315 | 0 | 1.4176 | 0 | 0.0018315 | 1.4176 | 86646 | 12.0749 | 86645.9982

## A2-B4
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38951.5696 | 1 | 0 | 38951.5696 | 1 | 0 |  | -101 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5717 | 1 | 0 | 38951.5717 | 1 | 0 |  | 84 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5738 | 1 | 0 | 38951.5739 | 1 | 0 |  | 268.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.576 | 1 | 0 | 38951.576 | 1 | 0 |  | 453.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5781 | 1 | 0 | 38951.5781 | 1 | 0 |  | 638.5 | 773.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5803 | 1 | 0 | 38951.5803 | 1 | 0 |  | 823 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5824 | 1 | 0 | 38951.5824 | 1 | 0 |  | 1007.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5845 | 1 | 0 | 38951.5845 | 1 | 0 |  | 1192.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5867 | 347 | 0 | 38951.5867 | 327 | 0 |  | 1377.5 | 1512.5 | 21.1844 | 0 | 19.9634 | 0 | 0.21184 | 0 | 0.19963 | 0 | 0.21184 | 0.19963 | 508.9395 | 546.1835 | 508.7276
38951.5888 | 451 | 389 | 38951.5888 | 501 | 464 |  | 1562 | 1697 | 27.5336 | 23.7485 | 30.5861 | 28.3272 | 0.27534 | 0.23748 | 0.30586 | 0.28327 | 0.037851 | 0.022589 | 2920.6874 | 7635.0821 | 323.0237
38951.5909 | 246 | 217 | 38951.591 | 246 | 220 |  | 1747 | 1882 | 15.0183 | 13.2479 | 15.0183 | 13.431 | 0.15018 | 0.13248 | 0.15018 | 0.13431 | 0.017705 | 0.015873 | 7088.4777 | 8154.2177 | 751.1659
38951.5931 | 30 | 28 | 38951.5931 | 34 | 31 |  | 1931.5 | 2066.5 | 1.8315 | 1.7094 | 2.0757 | 1.8926 | 0.018315 | 0.017094 | 0.020757 | 0.018926 | 0.001221 | 0.0018315 | 106277.1166 | 69981.0934 | 7328.8845

## A2-B3
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38951.5695 | 1 | 0 | 38951.5695 | 1 | 0 |  | -103.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5717 | 1 | 0 | 38951.5717 | 1 | 0 |  | 81 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5738 | 1 | 0 | 38951.5738 | 1 | 0 |  | 265.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5759 | 1 | 0 | 38951.576 | 1 | 0 |  | 450.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5781 | 1 | 0 | 38951.5781 | 1 | 0 |  | 635.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5802 | 1 | 0 | 38951.5802 | 1 | 0 |  | 820 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5824 | 1 | 0 | 38951.5824 | 1 | 0 |  | 1005 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5845 | 1 | 0 | 38951.5845 | 1 | 0 |  | 1189.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5866 | 402 | 0 | 38951.5867 | 4 | 0 |  | 1374.5 | 1509.5 | 24.5421 | 0 | 0.2442 | 0 | 0.24542 | 0 | 0.002442 | 0 | 0.24542 | 0.002442 | 425.6269 | 52725.5 | 425.3814
38951.5888 | 359 | 328 | 38951.5888 | 374 | 331 |  | 1559.5 | 1694.5 | 21.917 | 20.0244 | 22.8327 | 20.2076 | 0.21917 | 0.20024 | 0.22833 | 0.20208 | 0.018926 | 0.026252 | 7390.1822 | 4514.4627 | 425.3405
38951.5909 | 423 | 461 | 38951.5909 | 319 | 281 |  | 1744 | 1879 | 25.8242 | 28.1441 | 19.475 | 17.1551 | 0.25824 | 0.28144 | 0.19475 | 0.17155 | 0.023199 | 0.023199 | 5729.7452 | 5420.6931 | 261.7696
38951.5931 | 10 | 8 | 38951.5931 | 29 | 13 |  | 1928.5 | 2063.5 | 0.6105 | 0.4884 | 1.7705 | 0.79365 | 0.006105 | 0.004884 | 0.017705 | 0.0079365 | 0.001221 | 0.009768 | 108479.9096 | 13034.888 | 25988.3745

## A1-C6
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 149.3516 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38951.5693 | 1 | 0 | 38951.5693 | 1 | 0 |  | -123.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5714 | 1 | 0 | 38951.5715 | 1 | 0 |  | 61.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5736 | 1 | 0 | 38951.5736 | 1 | 0 |  | 246.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5757 | 1 | 0 | 38951.5757 | 1 | 0 |  | 431 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5779 | 1 | 0 | 38951.5779 | 1 | 0 |  | 616 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.58 | 1 | 0 | 38951.58 | 1 | 0 |  | 800.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5821 | 1 | 0 | 38951.5822 | 1 | 0 |  | 985.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5843 | 1 | 0 | 38951.5843 | 1 | 0 |  | 1170 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244538 | 244538 | 244537.9994
38951.5864 | 144 | 1 | 38951.5864 | 2026 | 0 |  | 1355 | 1490 | 8.7912 | 0.06105 | 123.6874 | 0 | 0.087912 | 0.0006105 | 1.2369 | 0 | 0.087302 | 1.2369 | 1666.2113 | 20.7493 | 39546.3552
38951.5886 | 101 | 1 | 38951.5886 | 2377 | 1 |  | 1539.5 | 1674.5 | 6.1661 | 0.06105 | 145.116 | 0.06105 | 0.061661 | 0.0006105 | 1.4512 | 0.0006105 | 0.06105 | 1.4505 | 3566.8887 | 2.9201 | 6651.5204
38951.5907 | 36 | 1 | 38951.5907 | 2358 | 1 |  | 1724.5 | 1859.5 | 2.1978 | 0.06105 | 143.956 | 0.06105 | 0.021978 | 0.0006105 | 1.4396 | 0.0006105 | 0.021368 | 1.4389 | 28932.2809 | 3.7497 | 8707.9025
38951.5928 | 3 | 0 | 38951.5928 | 2430 | 0 |  | 1909.5 | 2044.5 | 0.18315 | 0 | 148.3516 | 0 | 0.0018315 | 0 | 1.4835 | 0 | 0.0018315 | 1.4835 | 81446 | 0.67407 | 81445.9982

## A1-C5
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 148.3748 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38951.5693 | 1 | 0 | 38951.5693 | 1 | 0 |  | -126 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5714 | 1 | 0 | 38951.5714 | 1 | 0 |  | 58.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5736 | 1 | 0 | 38951.5736 | 1 | 0 |  | 243.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5757 | 1 | 0 | 38951.5757 | 1 | 0 |  | 428.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5778 | 1 | 0 | 38951.5778 | 2 | 0 |  | 613 | 748 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 242938 | 121419 | 242937.9994
38951.58 | 1 | 0 | 38951.58 | 1 | 0 |  | 797.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5821 | 1 | 0 | 38951.5821 | 1 | 0 |  | 982.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242938 | 242938 | 242937.9994
38951.5842 | 1 | 1 | 38951.5843 | 1 | 0 |  | 1167.5 | 1302.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 590188718.44 | 242938 | 242738.0823
38951.5864 | 121 | 1 | 38951.5864 | 2414 | 1 |  | 1352 | 1487 | 7.3871 | 0.06105 | 147.3748 | 0.06105 | 0.073871 | 0.0006105 | 1.4737 | 0.0006105 | 0.07326 | 1.4731 | 8454.7708 | 1.0789 | 2463.9677
38951.5885 | 118 | 3 | 38951.5885 | 2006 | 2 |  | 1537 | 1672 | 7.2039 | 0.18315 | 122.4664 | 0.1221 | 0.072039 | 0.0018315 | 1.2247 | 0.001221 | 0.070208 | 1.2234 | 2293.2527 | 21.1776 | 13453.2745
38951.5907 | 5 | 3 | 38951.5907 | 2065 | 2 |  | 1721.5 | 1856.5 | 0.30525 | 0.18315 | 126.0684 | 0.1221 | 0.0030525 | 0.0018315 | 1.2607 | 0.001221 | 0.001221 | 1.2595 | 16235.6244 | 23.1864 | 15198.1686
38951.5928 | 3 | 1 | 38951.5928 | 1979 | 1 |  | 1906.5 | 2041.5 | 0.18315 | 0.06105 | 120.8181 | 0.06105 | 0.0018315 | 0.0006105 | 1.2082 | 0.0006105 | 0.001221 | 1.2076 | 101900.0209 | 261.6984 | 175555.0414

## A1-B4
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38951.5692 | 1 | 0 | 38951.5693 | 1 | 0 |  | -129 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5714 | 1 | 0 | 38951.5714 | 1 | 0 |  | 56 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5735 | 1 | 0 | 38951.5735 | 1 | 0 |  | 240.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5757 | 1 | 0 | 38951.5757 | 1 | 0 |  | 425.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5778 | 1 | 0 | 38951.5778 | 1 | 0 |  | 610 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5799 | 1 | 0 | 38951.58 | 1 | 0 |  | 795 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5821 | 1 | 0 | 38951.5821 | 1 | 0 |  | 979.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5842 | 1 | 3 | 38951.5842 | 2 | 2 |  | 1164.5 | 1299.5 | 0.06105 | 0.18315 | 0.1221 | 0.1221 | 0.0006105 | 0.0018315 | 0.001221 | 0.001221 | 0.001221 | 0 | 105600.8579 | 111462761.5189 | 70300.6036
38951.5864 | 111 | 2 | 38951.5864 | 4 | 1 |  | 1349.5 | 1484.5 | 6.7766 | 0.1221 | 0.2442 | 0.06105 | 0.067766 | 0.001221 | 0.002442 | 0.0006105 | 0.066545 | 0.0018315 | 1836.7627 | 71600.0553 | 99861.5287
38951.5885 | 491 | 319 | 38951.5885 | 442 | 322 |  | 1534 | 1669 | 29.9756 | 19.475 | 26.9841 | 19.6581 | 0.29976 | 0.19475 | 0.26984 | 0.19658 | 0.10501 | 0.07326 | 1046.7037 | 1872.5692 | 387.7627
38951.5906 | 277 | 242 | 38951.5906 | 419 | 319 |  | 1719 | 1854 | 16.9109 | 14.7741 | 25.58 | 19.475 | 0.16911 | 0.14774 | 0.2558 | 0.19475 | 0.021368 | 0.06105 | 8643.477 | 1758.9361 | 623.2525
38951.5928 | 86 | 82 | 38951.5928 | 38 | 19 |  | 1903.5 | 2038.5 | 5.2503 | 5.0061 | 2.3199 | 1.16 | 0.052503 | 0.050061 | 0.023199 | 0.0116 | 0.002442 | 0.0116 | 62362.7878 | 10938.6983 | 2350.4878

## A1-B3
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38951.5692 | 1 | 0 | 38951.5692 | 1 | 0 |  | -131.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5713 | 1 | 0 | 38951.5714 | 1 | 0 |  | 53 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5735 | 1 | 0 | 38951.5735 | 1 | 0 |  | 238 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5756 | 1 | 0 | 38951.5756 | 1 | 0 |  | 422.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5778 | 1 | 0 | 38951.5778 | 1 | 0 |  | 607.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5799 | 1 | 0 | 38951.5799 | 1 | 0 |  | 792.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.582 | 1 | 0 | 38951.5821 | 1 | 0 |  | 977 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5842 | 3 | 9 | 38951.5842 | 2 | 4 |  | 1161.5 | 1296.5 | 0.18315 | 0.54945 | 0.1221 | 0.2442 | 0.0018315 | 0.0054945 | 0.001221 | 0.002442 | 0.003663 | 0.001221 | 35216.7628 | 106153.8598 | 23322.696
38951.5863 | 93 | 8 | 38951.5863 | 4 | 4 |  | 1346.5 | 1481.5 | 5.6777 | 0.4884 | 0.2442 | 0.2442 | 0.056777 | 0.004884 | 0.002442 | 0.002442 | 0.051893 | 0 | 2376.4763 | 1253008.9942 | 25148.243
38951.5885 | 404 | 234 | 38951.5885 | 315 | 233 |  | 1531.5 | 1666.5 | 24.6642 | 14.2857 | 19.2308 | 14.2247 | 0.24664 | 0.14286 | 0.19231 | 0.14225 | 0.10379 | 0.050061 | 1053.6088 | 3002.4281 | 610.0325
38951.5906 | 222 | 182 | 38951.5906 | 316 | 229 |  | 1716 | 1851 | 13.5531 | 11.1111 | 19.2918 | 13.9805 | 0.13553 | 0.11111 | 0.19292 | 0.1398 | 0.02442 | 0.053114 | 5988.7857 | 2160.4982 | 897.4815
38951.5927 | 109 | 70 | 38951.5928 | 53 | 24 |  | 1901 | 2036 | 6.6545 | 4.2735 | 3.2357 | 1.4652 | 0.066545 | 0.042735 | 0.032357 | 0.014652 | 0.02381 | 0.017705 | 5269.5699 | 7216.858 | 2725.1252

## A1-A2
Penlight Test 45 |  |  | 2006-08-22 | 13:41 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38951.5692 | 1 | 0 | 38951.5692 | 1 | 0 |  | -134.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5713 | 1 | 0 | 38951.5713 | 1 | 0 |  | 50.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5734 | 1 | 0 | 38951.5735 | 1 | 0 |  | 235 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5756 | 1 | 0 | 38951.5756 | 1 | 0 |  | 420 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5777 | 1 | 0 | 38951.5777 | 1 | 0 |  | 604.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5799 | 1 | 0 | 38951.5799 | 1 | 0 |  | 789.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.582 | 1 | 0 | 38951.582 | 1 | 0 |  | 974 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38951.5841 | 948 | 918 | 38951.5842 | 1052 | 1024 |  | 1159 | 1294 | 57.8755 | 56.044 | 64.2247 | 62.5153 | 0.57875 | 0.56044 | 0.64225 | 0.62515 | 0.018315 | 0.017094 | 4832.6563 | 15578.4359 | 26.7369
38951.5863 | 1020 | 915 | 38951.5863 | 1251 | 1125 |  | 1343.5 | 1478.5 | 62.2711 | 55.8608 | 76.3736 | 68.6813 | 0.62271 | 0.55861 | 0.76374 | 0.68681 | 0.064103 | 0.076923 | 351.805 | 444.8461 | 15.8849
38951.5884 | 1122 | 982 | 38951.5884 | 1036 | 924 |  | 1528.5 | 1663.5 | 68.4982 | 59.9512 | 63.2479 | 56.4103 | 0.68498 | 0.59951 | 0.63248 | 0.5641 | 0.08547 | 0.068376 | 392.1203 | 871.0794 | 0.82394
38951.5906 | 1037 | 957 | 38951.5906 | 1102 | 1096 |  | 1713.5 | 1848.5 | 63.3089 | 58.4249 | 67.2772 | 66.9109 | 0.63309 | 0.58425 | 0.67277 | 0.66911 | 0.04884 | 0.003663 | 51.911 | 48.0225 | 4.0348
38951.5927 | 1235 | 1108 |  | 1102 | 1096 |  | 1897 | 2032 | 75.3968 | 67.6435 | 67.2772 | 66.9109 | 0.75397 | 0.67643 | 0.67277 | 0.66911 | 0.077534 | 0.003663 | 268.3105 | 553.3354 | 17.5793

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 45 |  |  | 2006-08-22 | 13:41
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | C5-C | Penlight Time | C6-C | Penlight Time | C7-C | Penlight Time | Minimums
-117.25 | 229636.6661 |  | -80.8333 | 226080.6661 | -86.8333 | 230786.6661 | -74.75 | 229753.3327 | -65.8333 | 251838.0122 | -61.25 | 254854.6789 | -24.4167 | 244731.9994 | -117.25 | 226080.6661
67.5833 | 229636.6661 |  | 104 | 226080.6661 | 97.8333 | 230786.6661 | 110.0833 | 229753.3327 | 118.8333 | 251871.3327 | 123.5 | 254887.9994 | 160.5 | 244731.9994 | 67.5833 | 226080.6661
252.3333 | 208233.4993 |  | 288.6667 | 226080.6661 | 282.5833 | 230786.6661 | 294.75 | 229753.3327 | 303.6667 | 251871.3327 | 308.4167 | 254887.9994 | 345.0833 | 223328.8326 | 252.3333 | 208233.4993
437.1667 | 229636.6661 |  | 473.5833 | 226080.6661 | 467.4167 | 230786.6661 | 479.5833 | 229753.3327 | 488.5833 | 251871.3327 | 493.1667 | 254887.9994 | 530 | 244731.9994 | 437.1667 | 226080.6661
621.9167 | 229636.6661 |  | 658.25 | 226080.6661 | 652.1667 | 230786.6661 | 664.4167 | 229753.3327 | 673.1667 | 251871.3327 | 677.8333 | 254887.9994 | 714.75 | 244731.9994 | 621.9167 | 226080.6661
806.6667 | 229636.6661 |  | 843 | 226080.6661 | 836.9167 | 230786.6661 | 849.0833 | 229753.3327 | 857.9167 | 208101.8635 | 862.5833 | 211168.5103 | 899.5 | 244682.0192 | 806.6667 | 208101.8635
991.3333 | 229636.6661 |  | 1027.75 | 226080.6661 | 1021.75 | 230786.6661 | 1033.75 | 229753.3327 | 1042.6667 | 208126.3221 | 1047.4167 | 211176.3089 | 1084.1667 | 244698.6793 | 991.3333 | 208126.3221
1176.1667 | 118207.5195 |  | 1212.5833 | 167406.7888 | 1206.4167 | 76238.4404 | 1218.5833 | 87946.1064 | 1227.5833 | 108493.7869 | 1232.1667 | 114709.6822 | 1269 | 54591.6705 | 1176.1667 | 54591.6705
1361 | 28250.7164 |  | 1397.3333 | 12058.7745 | 1391.3333 | 6447.221 | 1403.5 | 17552.8829 | 1412.25 | 2173.8656 | 1417 | 7442.4542 | 1453.9167 | 12712.4632 | 1361 | 2173.8656
1545.75 | 4451.8163 |  | 1582.1667 | 25816.4169 | 1576.1667 | 9742.4763 | 1588.25 | 11411.0546 | 1597.1667 | 13711.7377 | 1601.75 | 11586.9682 | 1638.5833 | 25537.391 | 1545.75 | 4451.8163
1730.5 | 12615.092 |  | 1766.9167 | 19144.8293 | 1760.75 | 10964.8194 | 1773.0833 | 29182.0838 | 1781.75 | 13960.4076 | 1786.4167 | 19311.2218 | 1823.25 | 37786.5935 | 1730.5 | 10964.8194
1915.1667 | 54367.2882 |  | 1951.5 | 42187.3887 | 1945.5 | 26526.8529 | 1957.6667 | 35959.416 | 1966.6667 | 57637.4191 | 1971.4167 | 41325.6012 | 2008.0833 | 47288.4859 | 1915.1667 | 26526.8529
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 45 |  |  | 2006-08-22 | 13:41
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G | Penlight Time | Minimums
-128.9 | 224216.4 |  | -106.5 | 229056.4 | -78.4444 | 235903.7778 | -62.9444 | 231159.3333 | -48.6111 | 76693151.8267 | -39.9444 | 254704.6667 | -15.8 | 223454.2 | -10.1 | #VALUE! | 2.1111 | 233858.1111 | 5.1667 | #VALUE! | 22.9 | 244210.8 | 25 | 247730.8 | -36.3389 | #VALUE!
55.9 | 224216.4 |  | 78.3 | 229056.4 | 106.2778 | 235903.7778 | 121.8889 | 231159.3333 | 136.1111 | 254271.3333 | 144.8333 | 254704.6667 | 169 | 247858 | 174.6 | #VALUE! | 186.8889 | 248138 | 190 | #VALUE! | 207.6 | 244210.8 | 210 | 247730.8 | 148.45 | #VALUE!
240.7 | 224216.4 |  | 263 | 229056.4 | 291 | 221635 | 306.6111 | 231159.3333 | 320.9444 | 254271.3333 | 329.7222 | 254704.6667 | 353.7 | 247858 | 359.4 | #VALUE! | 371.6111 | 248138 | 374.7222 | #VALUE! | 392.4 | 244210.8 | 394.7 | 247730.8 | 333.2093 | #VALUE!
425.5 | 224216.4 |  | 447.9 | 229056.4 | 475.7778 | 235903.7778 | 491.3889 | 231159.3333 | 505.7778 | 254271.3333 | 514.4444 | 254704.6667 | 538.6 | 247858 | 544.1 | #VALUE! | 556.3889 | 248138 | 559.6111 | #VALUE! | 577.1 | 244210.8 | 579.5 | 247730.8 | 518.0074 | #VALUE!
610.2 | 224216.4 |  | 632.6 | 229056.4 | 660.6111 | 235903.7778 | 676.2222 | 231159.3333 | 690.4444 | 240769.2222 | 699.1667 | 254704.6667 | 723.4 | 247858 | 728.9 | #VALUE! | 741.2222 | 248138 | 744.2222 | #VALUE! | 762 | 244210.8 | 764.1 | 247730.8 | 702.7574 | #VALUE!
795 | 224216.4 |  | 817.3 | 229056.4 | 845.3333 | 235903.7778 | 860.9444 | 231159.3333 | 875.1667 | 231113.4061 | 883.8889 | 226355.8268 | 908 | 130978.1721 | 913.7 | #VALUE! | 925.8889 | 230108.174 | 929 | #VALUE! | 946.6 | 244210.8 | 949 | 247730.8 | 887.4852 | #VALUE!
979.7 | 224216.4 |  | 1002.1 | 229056.4 | 1030.1111 | 235903.7778 | 1045.6111 | 231159.3333 | 1059.9444 | 71663825.9917 | 1068.7222 | 226955.6876 | 1092.8 | 76380.7178 | 1098.4 | #VALUE! | 1110.6667 | 1271711.5742 | 1113.7222 | #VALUE! | 1131.5 | 244210.8 | 1133.7 | 247730.8 | 1072.2481 | #VALUE!
1164.5 | 118115781.3434 |  | 1186.9 | 189931.6872 | 1214.8333 | 36386221.5724 | 1230.4444 | 12458866.6506 | 1244.8333 | 69947.7309 | 1253.5 | 83526.9134 | 1277.6 | 20.8473 | 1283.2 | #VALUE! | 1295.3889 | 14066.023 | 1298.6667 | #VALUE! | 1316.3 | 57803.1578 | 1318.5 | 96484.9683 | 1257.0556 | #VALUE!
1349.3 | 2937.2052 |  | 1371.7 | 489.712 | 1399.7222 | 147374.3741 | 1415.2778 | 9488.3964 | 1429.5556 | 15.7263 | 1438.2778 | 12.305 | 1462.5 | 2.4914 | 1468 | #VALUE! | 1480.3333 | 11.1875 | 1483.3889 | #VALUE! | 1501 | 61882.02 | 1503.3 | 69543.3667 | 1441.863 | #VALUE!
1534.1 | 1670.5149 |  | 1556.5 | 13484.2451 | 1584.5556 | 10240.3392 | 1600.0556 | 20922.3108 | 1614.3889 | 41.0476 | 1623 | 10.843 | 1647.2 | 12.9537 | 1652.9 | #VALUE! | 1665.1111 | 6.8932 | 1668.1111 | #VALUE! | 1685.9 | 68780.0333 | 1688 | 69543.3667 | 1626.6519 | #VALUE!
1718.9 | 11970.4158 |  | 1741.3 | 11274.8254 | 1769.1111 | 23111.0353 | 1784.8889 | 38565.3183 | 1799 | 13.0393 | 1807.7222 | 10.3637 | 1832 | 18.2653 | 1837.5 | #VALUE! | 1849.7778 | 12.2143 | 1852.8333 | #VALUE! | 1870.5 | 68780.0333 | 1872.8 | 74062.3333 | 1811.3611 | #VALUE!
1903.5 | 50249.3378 |  | 1925.8 | 72953.1723 | 1953.9444 | 54805.9552 | 1969.5 | 50611.0523 | 1983.9444 | 45.7087 | 1992.7222 | 16.1825 | 2016.6 | 28.8086 | 2022.2 | #VALUE! | 2034.5556 | 9.6843 | 2037.6667 | #VALUE! | 2055.5 | 64499.4 | 2057.6 | 65379.4 | 1996.1278 | #VALUE!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -135 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.4
1 | -134 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.4
2 | -133 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.4
3 | -132 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.4
4 | -131 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
5 | -130 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
6 | -129 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.3 | 23.9 | 28.3
7 | -128 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.3 | 23.9 | 28.3
8 | -127 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.3 | 23.9 | 28.3
9 | -126 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.3 | 23.9 | 28.3
10 | -125 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
11 | -124 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
12 | -123 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
13 | -122 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.3 | 23.9 | 28.2
14 | -121 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.2 | 23.9 | 28.2
15 | -120 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.3 | 23.9 | 28.2
16 | -119 | 19.1 | 28.2 | 19 | 27.4 | 31.4 | 24.2 | 23.9 | 28.2
17 | -118 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.2 | 23.9 | 28.2
18 | -117 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.2 | 23.9 | 28.3
19 | -116 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.3 | 23.9 | 28.2
20 | -115 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.3 | 23.9 | 28.2
21 | -114 | 19.1 | 28.2 | 18.9 | 27.4 | 31.4 | 24.3 | 23.9 | 28.2
22 | -113 | 19.1 | 28 | 19.4 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
23 | -112 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
24 | -111 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
25 | -110 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
26 | -109 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
27 | -108 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
28 | -107 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
29 | -106 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
30 | -105 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.3
31 | -104 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
32 | -103 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
33 | -102 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.2
34 | -101 | 19.2 | 27.9 | 19.6 | 27.2 | 31 | 24.2 | 23.9 | 28.2
35 | -100 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
36 | -99 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
37 | -98 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
38 | -97 | 19.2 | 27.9 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
39 | -96 | 19.1 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
40 | -95 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
41 | -94 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
42 | -93 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
43 | -92 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
44 | -91 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
45 | -90 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
46 | -89 | 19.2 | 27.9 | 19.6 | 27.2 | 31.1 | 24.2 | 23.9 | 28.1
47 | -88 | 19.2 | 27.9 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
48 | -87 | 19.2 | 27.9 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
49 | -86 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
50 | -85 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
51 | -84 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
52 | -83 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
53 | -82 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
54 | -81 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
55 | -80 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
56 | -79 | 19.1 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
57 | -78 | 19.1 | 28 | 19.4 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
58 | -77 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
59 | -76 | 19.2 | 28 | 19.5 | 27.3 | 31.2 | 24.2 | 23.9 | 28.2
60 | -75 | 19.2 | 28 | 19.5 | 27.3 | 31.1 | 24.2 | 23.9 | 28.2
61 | -74 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
62 | -73 | 19.1 | 28 | 19.5 | 27.3 | 31.1 | 24.2 | 23.9 | 28.2
63 | -72 | 19.2 | 28 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
64 | -71 | 19.2 | 27.9 | 19.5 | 27.2 | 31.1 | 24.2 | 23.9 | 28.2
65 | -70 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
66 | -69 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
67 | -68 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
68 | -67 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
69 | -66 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
70 | -65 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.3
71 | -64 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.3
72 | -63 | 19.2 | 27.8 | 19.9 | 27.1 | 30.8 | 24.2 | 23.9 | 28.2
73 | -62 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
74 | -61 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
75 | -60 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 24 | 28.1
76 | -59 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 24 | 28.2
77 | -58 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 24 | 28.1
78 | -57 | 19.2 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
79 | -56 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
80 | -55 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
81 | -54 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.1
82 | -53 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
83 | -52 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
84 | -51 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
85 | -50 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
86 | -49 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
87 | -48 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
88 | -47 | 19.1 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
89 | -46 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
90 | -45 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
91 | -44 | 19.1 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
92 | -43 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
93 | -42 | 19.1 | 27.8 | 19.9 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
94 | -41 | 19.2 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.1
95 | -40 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
96 | -39 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
97 | -38 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28
98 | -37 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.1
99 | -36 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
100 | -35 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
101 | -34 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
102 | -33 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
103 | -32 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
104 | -31 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
105 | -30 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
106 | -29 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
107 | -28 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
108 | -27 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
109 | -26 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.1
110 | -25 | 19.1 | 27.8 | 19.8 | 27.2 | 30.9 | 24.2 | 23.9 | 28.1
111 | -24 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
112 | -23 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
113 | -22 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
114 | -21 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
115 | -20 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
116 | -19 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
117 | -18 | 19.1 | 27.8 | 19.8 | 27.2 | 30.9 | 24.2 | 23.9 | 28.3
118 | -17 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.3
119 | -16 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.3
120 | -15 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
121 | -14 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
122 | -13 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
123 | -12 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
124 | -11 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
125 | -10 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
126 | -9 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
127 | -8 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
128 | -7 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 23.9 | 28.2
129 | -6 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
130 | -5 | 19.1 | 27.8 | 19.8 | 27.1 | 30.9 | 24.2 | 24 | 28.2
131 | -4 | 19.1 | 27.8 | 19.8 | 27.2 | 30.9 | 24.2 | 24 | 28.2
132 | -3 | 19.1 | 28.7 | 17.7 | 27.9 | 32.1 | 24.4 | 23.9 | 28.1
133 | -2 | 19.1 | 29.4 | 16.3 | 28.4 | 33 | 24.5 | 23.9 | 28
134 | -1 | 19.2 | 29.6 | 15.8 | 28.6 | 33.4 | 24.6 | 23.8 | 28
135 | 0 | 19.8 | 29.6 | 15.7 | 28.6 | 33.4 | 24.6 | 23.9 | 28
136 | 1 | 21.1 | 29.6 | 15.7 | 28.6 | 33.4 | 24.6 | 23.9 | 28.1
137 | 2 | 22.8 | 29.6 | 15.7 | 28.6 | 33.4 | 24.6 | 23.9 | 28.1
138 | 3 | 25 | 29.6 | 15.7 | 28.6 | 33.4 | 24.6 | 23.9 | 28.1
139 | 4 | 27.6 | 29.6 | 15.8 | 28.6 | 33.3 | 24.6 | 23.9 | 28.2
140 | 5 | 30.5 | 29.6 | 15.7 | 28.6 | 33.4 | 24.6 | 24 | 28.2
141 | 6 | 33.7 | 29.6 | 15.7 | 28.6 | 33.4 | 24.7 | 24 | 28.3
142 | 7 | 37.2 | 29.7 | 15.7 | 28.6 | 33.4 | 24.7 | 24.1 | 28.3
143 | 8 | 41 | 29.7 | 15.7 | 28.6 | 33.4 | 24.7 | 24.2 | 28.3
144 | 9 | 44.9 | 29.7 | 15.7 | 28.6 | 33.4 | 24.8 | 24.3 | 28.4
145 | 10 | 49 | 29.6 | 15.8 | 28.6 | 33.4 | 24.8 | 24.4 | 28.4
146 | 11 | 53.2 | 29.7 | 15.7 | 28.6 | 33.4 | 24.9 | 24.5 | 28.5
147 | 12 | 57.6 | 29.7 | 15.8 | 28.6 | 33.4 | 25 | 24.6 | 28.6
148 | 13 | 62.2 | 29.7 | 15.7 | 28.6 | 33.4 | 25.1 | 24.7 | 28.6
149 | 14 | 66.8 | 29.7 | 15.8 | 28.6 | 33.4 | 25.1 | 24.8 | 28.7
150 | 15 | 71.6 | 29.7 | 15.8 | 28.6 | 33.4 | 25.2 | 25 | 28.8
151 | 16 | 76.5 | 29.7 | 15.8 | 28.6 | 33.4 | 25.3 | 25.1 | 28.9
152 | 17 | 81.5 | 29.8 | 15.8 | 28.6 | 33.5 | 25.4 | 25.3 | 29
153 | 18 | 86.6 | 29.8 | 15.8 | 28.6 | 33.5 | 25.5 | 25.5 | 29.1
154 | 19 | 91.7 | 29.8 | 15.8 | 28.6 | 33.5 | 25.7 | 25.7 | 29.3
155 | 20 | 97 | 29.8 | 15.9 | 28.6 | 33.5 | 25.8 | 25.9 | 29.4
156 | 21 | 102.3 | 29.9 | 15.8 | 28.7 | 33.6 | 26 | 26.1 | 29.6
157 | 22 | 107.7 | 29.9 | 15.8 | 28.7 | 33.7 | 26.1 | 26.4 | 29.8
158 | 23 | 113.2 | 30 | 15.8 | 28.7 | 33.7 | 26.3 | 26.6 | 30
159 | 24 | 118.8 | 30 | 15.9 | 28.7 | 33.7 | 26.4 | 26.9 | 30.3
160 | 25 | 124.4 | 30 | 15.9 | 28.7 | 33.7 | 26.6 | 27.2 | 30.6
161 | 26 | 130.1 | 30.1 | 15.9 | 28.7 | 33.8 | 26.7 | 27.5 | 30.9
162 | 27 | 135.7 | 30.2 | 15.9 | 28.8 | 33.9 | 26.9 | 27.8 | 31.2
163 | 28 | 141.4 | 30.3 | 15.9 | 28.8 | 34 | 27 | 28.1 | 31.5
164 | 29 | 147.1 | 30.3 | 15.9 | 28.8 | 34.1 | 27.2 | 28.5 | 31.8
165 | 30 | 152.7 | 30.4 | 16 | 28.8 | 34.1 | 27.4 | 28.8 | 32.1
166 | 31 | 158.4 | 30.5 | 16 | 28.8 | 34.2 | 27.6 | 29.2 | 32.4
167 | 32 | 164.1 | 30.5 | 16.1 | 28.9 | 34.3 | 27.8 | 29.6 | 32.8
168 | 33 | 169.8 | 30.6 | 16.1 | 28.9 | 34.4 | 28 | 30 | 33.2
169 | 34 | 175.6 | 30.7 | 16.1 | 28.9 | 34.5 | 28.2 | 30.4 | 33.6
170 | 35 | 181.3 | 30.8 | 16.2 | 29 | 34.6 | 28.4 | 30.9 | 34
171 | 36 | 186.9 | 30.9 | 16.2 | 29 | 34.8 | 28.7 | 31.3 | 34.4
172 | 37 | 192.5 | 31 | 16.3 | 29.1 | 34.9 | 28.9 | 31.8 | 34.8
173 | 38 | 198 | 31.1 | 16.4 | 29.1 | 35 | 29.1 | 32.3 | 35.3
174 | 39 | 203.7 | 31.3 | 16.4 | 29.1 | 35.1 | 29.4 | 32.8 | 35.8
175 | 40 | 209.5 | 31.4 | 16.5 | 29.2 | 35.2 | 29.7 | 33.4 | 36.3
176 | 41 | 215.1 | 31.5 | 16.6 | 29.2 | 35.4 | 30 | 33.9 | 36.9
177 | 42 | 220.7 | 31.6 | 16.7 | 29.3 | 35.5 | 30.3 | 34.5 | 37.5
178 | 43 | 226.4 | 31.8 | 16.7 | 29.4 | 35.7 | 30.6 | 35.1 | 38
179 | 44 | 232.2 | 32 | 16.8 | 29.5 | 35.9 | 31 | 35.7 | 38.6
180 | 45 | 237.9 | 32.1 | 16.8 | 29.6 | 36.1 | 31.3 | 36.4 | 39.2
181 | 46 | 243.6 | 32.3 | 16.9 | 29.6 | 36.3 | 31.7 | 37.1 | 39.9
182 | 47 | 249.2 | 32.5 | 17 | 29.7 | 36.5 | 32.1 | 37.8 | 40.6
183 | 48 | 254.6 | 32.7 | 17.1 | 29.8 | 36.7 | 32.4 | 38.5 | 41.4
184 | 49 | 260 | 32.8 | 17.3 | 29.9 | 36.9 | 32.8 | 39.3 | 42.1
185 | 50 | 265.5 | 33 | 17.4 | 30 | 37.1 | 33.2 | 40 | 42.8
186 | 51 | 270.8 | 33.2 | 17.6 | 30.1 | 37.4 | 33.6 | 40.8 | 43.6
187 | 52 | 276.3 | 33.4 | 17.7 | 30.2 | 37.6 | 34 | 41.6 | 44.4
188 | 53 | 281.7 | 33.7 | 17.8 | 30.3 | 37.9 | 34.5 | 42.4 | 45.2
189 | 54 | 286.9 | 33.9 | 17.9 | 30.5 | 38.2 | 34.9 | 43.2 | 46.1
190 | 55 | 292.1 | 34.2 | 18 | 30.6 | 38.5 | 35.4 | 44.1 | 47
191 | 56 | 297.3 | 34.4 | 18.2 | 30.8 | 38.8 | 35.9 | 44.9 | 47.9
192 | 57 | 302.6 | 34.7 | 18.3 | 30.9 | 39.1 | 36.4 | 45.8 | 48.8
193 | 58 | 307.8 | 35 | 18.5 | 31.1 | 39.4 | 36.9 | 46.7 | 49.9
194 | 59 | 313 | 35.3 | 18.7 | 31.2 | 39.7 | 37.4 | 47.7 | 50.9
195 | 60 | 318.1 | 35.6 | 18.9 | 31.4 | 40 | 38 | 48.6 | 52
196 | 61 | 323.2 | 35.9 | 19.1 | 31.6 | 40.3 | 38.6 | 49.6 | 53.1
197 | 62 | 328.4 | 36.2 | 19.2 | 31.7 | 40.6 | 39.1 | 50.6 | 54.2
198 | 63 | 333.8 | 36.5 | 19.4 | 31.9 | 41 | 39.7 | 51.6 | 55.4
199 | 64 | 339 | 36.8 | 19.7 | 32.1 | 41.4 | 40.3 | 52.7 | 56.6
200 | 65 | 344.1 | 37.2 | 19.8 | 32.4 | 41.8 | 41 | 53.7 | 57.9
201 | 66 | 349.1 | 37.5 | 20 | 32.6 | 42.1 | 41.6 | 54.8 | 59.1
202 | 67 | 354.3 | 37.9 | 20.3 | 32.8 | 42.5 | 42.2 | 55.9 | 60.5
203 | 68 | 359.2 | 38.2 | 20.6 | 33 | 42.9 | 42.8 | 57 | 61.8
204 | 69 | 364.2 | 38.6 | 20.8 | 33.3 | 43.4 | 43.6 | 58.2 | 63.1
205 | 70 | 369 | 39 | 21.1 | 33.5 | 43.8 | 44.3 | 59.3 | 64.5
206 | 71 | 373.7 | 39.4 | 21.3 | 33.7 | 44.2 | 45.1 | 60.6 | 66
207 | 72 | 378.6 | 39.8 | 21.6 | 34 | 44.6 | 45.8 | 61.8 | 67.5
208 | 73 | 383.3 | 40.2 | 21.9 | 34.3 | 45 | 46.5 | 63.1 | 69
209 | 74 | 387.9 | 40.6 | 22.2 | 34.5 | 45.5 | 47.3 | 64.4 | 70.6
210 | 75 | 392.5 | 41.1 | 22.5 | 34.8 | 46 | 48.1 | 65.8 | 72.2
211 | 76 | 397.1 | 41.6 | 22.8 | 35.1 | 46.5 | 48.8 | 67.1 | 73.8
212 | 77 | 401.6 | 42 | 23.1 | 35.4 | 47 | 49.5 | 68.4 | 75.5
213 | 78 | 406.2 | 42.5 | 23.4 | 35.7 | 47.5 | 50.4 | 69.8 | 77.2
214 | 79 | 410.9 | 43 | 23.7 | 36.1 | 48 | 51.3 | 71.1 | 79
215 | 80 | 415.3 | 43.5 | 24.1 | 36.4 | 48.6 | 52.2 | 72.7 | 80.8
216 | 81 | 419.8 | 44 | 24.3 | 36.7 | 49.1 | 53.1 | 74.2 | 82.6
217 | 82 | 424.3 | 44.5 | 24.7 | 37.1 | 49.7 | 54.1 | 75.6 | 84.4
218 | 83 | 428.6 | 45.1 | 25.1 | 37.4 | 50.2 | 54.9 | 77.1 | 86.3
219 | 84 | 432.9 | 45.6 | 25.4 | 37.8 | 50.8 | 55.8 | 78.7 | 88.3
220 | 85 | 437.3 | 46.2 | 25.8 | 38.2 | 51.4 | 56.7 | 80.2 | 90.3
221 | 86 | 441.6 | 46.7 | 26.2 | 38.6 | 52 | 57.6 | 81.7 | 92.3
222 | 87 | 445.9 | 47.3 | 26.6 | 38.9 | 52.6 | 58.7 | 83.3 | 94.4
223 | 88 | 450 | 47.9 | 27 | 39.3 | 53.2 | 59.7 | 84.8 | 96.6
224 | 89 | 453.9 | 48.5 | 27.4 | 39.7 | 53.8 | 60.7 | 86.4 | 98.7
225 | 90 | 458 | 49.1 | 27.9 | 40.2 | 54.5 | 61.7 | 88.1 | 100.9
226 | 91 | 462.2 | 49.7 | 28.3 | 40.6 | 55.1 | 62.8 | 89.8 | 103.1
227 | 92 | 466.5 | 50.3 | 28.8 | 41 | 55.7 | 63.8 | 91.3 | 105.3
228 | 93 | 470.6 | 50.9 | 29.2 | 41.5 | 56.4 | 64.7 | 92.9 | 107.7
229 | 94 | 474.6 | 51.6 | 29.7 | 41.9 | 57.1 | 65.8 | 94.6 | 110
230 | 95 | 478.7 | 52 | 30.8 | 42.1 | 57.3 | 66.9 | 96.4 | 112.4
231 | 96 | 482.5 | 52.6 | 31.4 | 42.5 | 58.1 | 68 | 98 | 114.9
232 | 97 | 486 | 53.4 | 31.8 | 43 | 58.9 | 69.3 | 99.9 | 117.3
233 | 98 | 489 | 54.1 | 32.3 | 43.5 | 59.6 | 70.5 | 101.7 | 119.8
234 | 99 | 491.9 | 54.8 | 32.8 | 44 | 60.3 | 71.7 | 103.4 | 122.3
235 | 100 | 494.6 | 55.5 | 33.4 | 44.5 | 61 | 72.7 | 105 | 124.6
236 | 101 | 497.2 | 56.2 | 34 | 45 | 61.7 | 73.7 | 106.7 | 127.1
237 | 102 | 499.6 | 57 | 34.6 | 45.5 | 62.3 | 74.9 | 108.4 | 129.6
238 | 103 | 501.9 | 57.7 | 35.2 | 46 | 63 | 76 | 110 | 131.9
239 | 104 | 504.2 | 58.5 | 35.8 | 46.6 | 63.7 | 77.2 | 111.6 | 134.4
240 | 105 | 506.4 | 59.3 | 36.3 | 47.1 | 64.5 | 78.4 | 113 | 136.9
241 | 106 | 508.4 | 60.2 | 36.7 | 47.7 | 65.4 | 79.5 | 114.8 | 139.4
242 | 107 | 510.4 | 61 | 37.3 | 48.3 | 66.3 | 80.6 | 116.5 | 141.8
243 | 108 | 512.2 | 61.8 | 37.9 | 48.8 | 67 | 81.8 | 117.8 | 144.4
244 | 109 | 513.9 | 62.7 | 38.5 | 49.4 | 67.7 | 83 | 119.5 | 146.9
245 | 110 | 515.6 | 63.5 | 39.2 | 49.9 | 68.5 | 84.2 | 121 | 149.5
246 | 111 | 517.1 | 64.3 | 39.9 | 50.5 | 69.2 | 85.4 | 122.4 | 151.9
247 | 112 | 518.3 | 65.1 | 40.5 | 51.1 | 70 | 86.6 | 123.8 | 154.2
248 | 113 | 518.9 | 66 | 41.3 | 51.6 | 70.7 | 87.7 | 125.4 | 156.7
249 | 114 | 519.6 | 66.8 | 42 | 52.2 | 71.4 | 88.7 | 126.7 | 159.1
250 | 115 | 520.1 | 67.6 | 42.7 | 52.8 | 72.2 | 89.8 | 127.9 | 161.5
251 | 116 | 520.5 | 68.5 | 43.4 | 53.4 | 73 | 90.8 | 129 | 163.8
252 | 117 | 520.9 | 69.4 | 44.1 | 54 | 73.8 | 91.8 | 130.5 | 166.2
253 | 118 | 521.2 | 70.3 | 44.7 | 54.6 | 74.7 | 92.8 | 132 | 168.6
254 | 119 | 521.3 | 71.1 | 45.4 | 55.3 | 75.5 | 93.7 | 133.4 | 171
255 | 120 | 521.5 | 72 | 46 | 55.9 | 76.3 | 94.5 | 134.8 | 173.3
256 | 121 | 521.5 | 72.9 | 46.7 | 56.6 | 77.2 | 95.4 | 136.1 | 175.6
257 | 122 | 521.2 | 73.7 | 47.4 | 57.2 | 78 | 96.3 | 136.9 | 177.9
258 | 123 | 521 | 74.6 | 48.2 | 57.8 | 78.9 | 97.2 | 137.8 | 180.1
259 | 124 | 521 | 75.6 | 48.7 | 58.5 | 79.9 | 98.3 | 138.8 | 182.3
260 | 125 | 520.9 | 76.4 | 49.5 | 59.2 | 80.8 | 99.5 | 139.7 | 184.5
261 | 126 | 520.5 | 77.4 | 50 | 59.9 | 81.8 | 100.7 | 140.6 | 186.7
262 | 127 | 520.2 | 78.3 | 50.7 | 60.6 | 82.7 | 101.7 | 141.5 | 188.9
263 | 128 | 519.8 | 79.2 | 51.4 | 61.3 | 83.6 | 102.7 | 142.2 | 191
264 | 129 | 519.6 | 80.1 | 52.1 | 62 | 84.5 | 103.8 | 143 | 193.2
265 | 130 | 519.3 | 81 | 52.8 | 62.7 | 85.4 | 104.9 | 143.9 | 195.3
266 | 131 | 519.1 | 81.8 | 53.5 | 63.3 | 86.2 | 106 | 144.6 | 197.4
267 | 132 | 518.9 | 82.7 | 54.3 | 64 | 87.1 | 106.8 | 145.7 | 199.4
268 | 133 | 518.9 | 83.6 | 55 | 64.7 | 87.9 | 107.7 | 146.3 | 201.4
269 | 134 | 518.9 | 84.4 | 55.7 | 65.4 | 88.8 | 108.6 | 147.2 | 203.5
270 | 135 | 518.7 | 85.2 | 56.5 | 66.1 | 89.6 | 109.4 | 147.7 | 205.6
271 | 136 | 518.8 | 86.1 | 57.3 | 66.8 | 90.4 | 110.3 | 148.5 | 207.6
272 | 137 | 519 | 86.9 | 58.1 | 67.5 | 91.3 | 111.2 | 149.4 | 209.7
273 | 138 | 519.1 | 87.7 | 58.8 | 68.3 | 92.2 | 112.3 | 150.1 | 211.8
274 | 139 | 519.2 | 88.5 | 59.5 | 69 | 93 | 113.2 | 150.7 | 213.8
275 | 140 | 519.3 | 89.3 | 60.4 | 69.7 | 93.9 | 114.1 | 151.4 | 215.8
276 | 141 | 519.4 | 90.1 | 61.1 | 70.5 | 94.7 | 115 | 152.1 | 217.8
277 | 142 | 519.5 | 90.9 | 61.9 | 71.2 | 95.5 | 115.8 | 152.8 | 219.7
278 | 143 | 519.6 | 91.7 | 62.7 | 71.9 | 96.4 | 116.7 | 153.6 | 221.7
279 | 144 | 519.7 | 92.5 | 63.4 | 72.7 | 97.2 | 117.4 | 154.4 | 223.6
280 | 145 | 519.9 | 93.2 | 64.2 | 73.4 | 98.1 | 118.2 | 155.2 | 225.5
281 | 146 | 520 | 94 | 65 | 74.1 | 98.8 | 119.1 | 155.8 | 227.4
282 | 147 | 520.2 | 94.7 | 65.8 | 74.9 | 99.7 | 120 | 156.4 | 229.3
283 | 148 | 520.2 | 95.5 | 66.6 | 75.6 | 100.5 | 120.8 | 157.1 | 231.1
284 | 149 | 520.2 | 96.2 | 67.3 | 76.4 | 101.3 | 121.8 | 157.7 | 233
285 | 150 | 520.2 | 96.9 | 68.1 | 77.1 | 102.1 | 122.7 | 158.3 | 234.9
286 | 151 | 520.2 | 97.6 | 68.8 | 77.8 | 102.8 | 123.6 | 158.8 | 236.7
287 | 152 | 520.1 | 98.3 | 69.6 | 78.6 | 103.6 | 124.6 | 159.5 | 238.5
288 | 153 | 520.2 | 99 | 70.4 | 79.3 | 104.3 | 125.5 | 160.1 | 240.4
289 | 154 | 520.2 | 99.6 | 71.1 | 80 | 105 | 126.3 | 160.5 | 242.2
290 | 155 | 520.2 | 100.3 | 71.9 | 80.8 | 105.8 | 127 | 161.3 | 244
291 | 156 | 520.3 | 100.9 | 72.7 | 81.5 | 106.5 | 127.8 | 161.6 | 245.8
292 | 157 | 520.5 | 101.4 | 73.5 | 82.2 | 107.2 | 128.6 | 162 | 247.5
293 | 158 | 520.7 | 102 | 74.3 | 82.9 | 107.9 | 129.5 | 162.8 | 249.2
294 | 159 | 521 | 102.5 | 75.1 | 83.7 | 108.7 | 130.3 | 163.6 | 251
295 | 160 | 521.2 | 103 | 75.8 | 84.4 | 109.4 | 131.3 | 164.3 | 252.6
296 | 161 | 521.4 | 103.5 | 76.6 | 85.1 | 110.2 | 132.1 | 165.1 | 254.4
297 | 162 | 521.4 | 103.9 | 77.5 | 85.8 | 110.9 | 132.9 | 165.8 | 256.2
298 | 163 | 521.5 | 104.4 | 78.2 | 86.6 | 111.7 | 133.8 | 166.6 | 257.8
299 | 164 | 521.6 | 104.8 | 78.9 | 87.4 | 112.5 | 134.6 | 167.4 | 259.5
300 | 165 | 521.8 | 105.2 | 79.7 | 88.1 | 113.3 | 135.5 | 168.2 | 261.2
301 | 166 | 521.9 | 105.6 | 80.5 | 88.9 | 114.1 | 136.6 | 168.9 | 262.9
302 | 167 | 521.8 | 106 | 81.3 | 89.7 | 115 | 137.5 | 169.8 | 264.6
303 | 168 | 521.7 | 106.4 | 82.1 | 90.5 | 115.8 | 138.3 | 170.4 | 266.2
304 | 169 | 521.8 | 106.8 | 82.8 | 91.3 | 116.6 | 139.1 | 170.9 | 267.7
305 | 170 | 521.9 | 107.4 | 83.6 | 92.1 | 117.5 | 139.8 | 171.7 | 269.2
306 | 171 | 521.8 | 107.9 | 84.4 | 93 | 118.3 | 140.6 | 172.7 | 270.9
307 | 172 | 522 | 108.5 | 85.3 | 93.8 | 119.1 | 141.4 | 173.6 | 272.4
308 | 173 | 522.2 | 109.1 | 86.2 | 94.7 | 119.9 | 142.2 | 174.5 | 273.8
309 | 174 | 522.1 | 109.8 | 87.1 | 95.5 | 120.7 | 142.9 | 175.5 | 275.3
310 | 175 | 522 | 110.4 | 88.1 | 96.4 | 121.4 | 143.4 | 176.3 | 276.8
311 | 176 | 521.8 | 111.2 | 89.1 | 97.2 | 122.2 | 144.1 | 177.1 | 278.2
312 | 177 | 521.6 | 112 | 90 | 98.1 | 123.1 | 144.5 | 177.7 | 279.6
313 | 178 | 521.4 | 112.9 | 90.9 | 99 | 123.9 | 145 | 178.3 | 281.1
314 | 179 | 521.4 | 113.7 | 91.9 | 99.9 | 124.8 | 145.6 | 179.1 | 282.5
315 | 180 | 521.5 | 114.6 | 92.8 | 100.8 | 125.7 | 146.1 | 180 | 284
316 | 181 | 521.6 | 115.5 | 93.8 | 101.7 | 126.6 | 146.7 | 180.8 | 285.4
317 | 182 | 521.5 | 116.3 | 94.8 | 102.6 | 127.5 | 147.2 | 181.5 | 286.7
318 | 183 | 521.5 | 117.1 | 95.7 | 103.5 | 128.4 | 147.7 | 182.2 | 288
319 | 184 | 521.6 | 117.9 | 96.7 | 104.4 | 129.3 | 148.2 | 183.1 | 289.4
320 | 185 | 521.6 | 118.9 | 97.7 | 105.3 | 130.3 | 148.4 | 183.8 | 290.8
321 | 186 | 521.6 | 119.9 | 98.7 | 106.3 | 131.2 | 148.8 | 184.5 | 292.1
322 | 187 | 521.7 | 121 | 99.7 | 107.3 | 132.2 | 149.4 | 185.1 | 293.4
323 | 188 | 521.6 | 122.2 | 100.7 | 108.2 | 133.2 | 149.9 | 185.6 | 294.8
324 | 189 | 521.4 | 123.6 | 101.7 | 109.3 | 134.3 | 150.5 | 186.4 | 296.1
325 | 190 | 521.5 | 125.2 | 102.8 | 110.2 | 135.4 | 151.1 | 187.1 | 297.3
326 | 191 | 521.6 | 126.9 | 103.7 | 111.3 | 136.5 | 151.6 | 187.7 | 298.6
327 | 192 | 521.6 | 128.8 | 104.8 | 112.3 | 137.7 | 152.1 | 188.3 | 299.9
328 | 193 | 521.6 | 130.8 | 105.9 | 113.4 | 138.9 | 152.4 | 189.1 | 301.1
329 | 194 | 521.4 | 132.9 | 107 | 114.4 | 140.1 | 153.1 | 189.7 | 302.4
330 | 195 | 521.1 | 135.1 | 108 | 115.5 | 141.3 | 153.8 | 190.2 | 303.7
331 | 196 | 521.1 | 137.3 | 109.1 | 116.5 | 142.6 | 154.6 | 190.9 | 304.9
332 | 197 | 520.9 | 139.5 | 110.2 | 117.6 | 143.8 | 155.2 | 192 | 306.1
333 | 198 | 520.7 | 141.6 | 111.4 | 118.7 | 145.1 | 156 | 192.6 | 307.2
334 | 199 | 520.4 | 143.8 | 112.5 | 119.8 | 146.3 | 156.7 | 193.3 | 308.4
335 | 200 | 520.3 | 145.9 | 113.6 | 120.9 | 147.5 | 157.5 | 193.7 | 309.6
336 | 201 | 520.3 | 147.8 | 114.7 | 122 | 148.7 | 158.2 | 194.4 | 310.7
337 | 202 | 520.3 | 149.8 | 115.8 | 123.1 | 149.9 | 158.8 | 195.1 | 311.8
338 | 203 | 520.2 | 151.7 | 116.9 | 124.2 | 151.1 | 159.4 | 195.6 | 313
339 | 204 | 520.3 | 153.5 | 118 | 125.3 | 152.2 | 160.1 | 196.2 | 314.1
340 | 205 | 520.6 | 155.3 | 119.1 | 126.4 | 153.4 | 160.8 | 197 | 315.1
341 | 206 | 520.8 | 157 | 120.2 | 127.5 | 154.5 | 161.6 | 197.7 | 316.2
342 | 207 | 520.9 | 158.5 | 121.3 | 128.7 | 155.6 | 162.4 | 198.2 | 317.3
343 | 208 | 521 | 160.1 | 122.4 | 129.8 | 156.8 | 163 | 198.9 | 318.3
344 | 209 | 520.9 | 161.7 | 123.5 | 130.9 | 157.8 | 163.7 | 199.5 | 319.4
345 | 210 | 520.8 | 163.2 | 124.6 | 132 | 158.9 | 164.4 | 200 | 320.4
346 | 211 | 521.1 | 164.6 | 125.7 | 133.1 | 160 | 165.2 | 200.7 | 321.5
347 | 212 | 521.1 | 165.8 | 126.8 | 134.2 | 161.1 | 165.9 | 201.2 | 322.5
348 | 213 | 521.1 | 167.1 | 128 | 135.3 | 162.2 | 166.7 | 201.8 | 323.5
349 | 214 | 521 | 168.4 | 129.1 | 136.4 | 163.2 | 167.3 | 202.3 | 324.6
350 | 215 | 521 | 169.7 | 130.2 | 137.5 | 164.3 | 168.2 | 202.7 | 325.7
351 | 216 | 520.9 | 170.9 | 131.3 | 138.7 | 165.3 | 169 | 203.3 | 326.8
352 | 217 | 520.6 | 172.1 | 132.4 | 139.8 | 166.3 | 169.6 | 203.9 | 327.8
353 | 218 | 520.4 | 173.4 | 133.4 | 141 | 167.4 | 170.4 | 204.4 | 328.8
354 | 219 | 520.4 | 174.6 | 134.5 | 142.1 | 168.4 | 171 | 204.9 | 329.7
355 | 220 | 520.3 | 175.8 | 135.5 | 143.3 | 169.5 | 171.7 | 205.5 | 330.6
356 | 221 | 520.2 | 176.8 | 136.5 | 144.4 | 170.5 | 172.4 | 206 | 331.5
357 | 222 | 520.1 | 178 | 137.5 | 145.5 | 171.6 | 173.2 | 206.5 | 332.4
358 | 223 | 520 | 179.1 | 138.5 | 146.7 | 172.6 | 173.8 | 206.9 | 333.4
359 | 224 | 519.8 | 180.3 | 139.5 | 147.8 | 173.6 | 174.5 | 207.4 | 334.2
360 | 225 | 519.7 | 181.5 | 140.5 | 148.9 | 174.6 | 175.1 | 207.9 | 335
361 | 226 | 519.7 | 182.6 | 141.5 | 150 | 175.7 | 175.7 | 208.6 | 335.9
362 | 227 | 519.6 | 183.8 | 142.5 | 151.1 | 176.7 | 176.3 | 209.1 | 336.7
363 | 228 | 519.7 | 184.9 | 143.6 | 152.2 | 177.6 | 176.8 | 209.6 | 337.6
364 | 229 | 519.7 | 185.9 | 144.6 | 153.3 | 178.6 | 177.6 | 210.1 | 338.5
365 | 230 | 519.7 | 186.9 | 145.6 | 154.3 | 179.6 | 178.2 | 210.6 | 339.3
366 | 231 | 519.6 | 187.8 | 146.6 | 155.4 | 180.6 | 178.9 | 211 | 340.1
367 | 232 | 519.5 | 188.8 | 147.6 | 156.5 | 181.6 | 179.7 | 211.4 | 341
368 | 233 | 519.6 | 189.9 | 148.6 | 157.5 | 182.5 | 180.5 | 211.8 | 341.8
369 | 234 | 519.8 | 190.9 | 149.6 | 158.6 | 183.5 | 181.2 | 212.2 | 342.5
370 | 235 | 520 | 191.9 | 150.6 | 159.7 | 184.5 | 181.9 | 212.7 | 343.3
371 | 236 | 520.2 | 193 | 151.6 | 160.7 | 185.5 | 182.6 | 213.3 | 344.2
372 | 237 | 520 | 194 | 152.6 | 161.7 | 186.4 | 183.2 | 213.9 | 344.9
373 | 238 | 519.9 | 195.1 | 153.6 | 162.7 | 187.3 | 183.7 | 214.4 | 345.7
374 | 239 | 520 | 196.1 | 154.6 | 163.8 | 188.3 | 184.3 | 214.8 | 346.4
375 | 240 | 519.9 | 197 | 155.7 | 164.8 | 189.2 | 184.9 | 215.1 | 347.2
376 | 241 | 520 | 198.1 | 156.6 | 165.8 | 190.2 | 185.5 | 215.5 | 347.9
377 | 242 | 519.9 | 199 | 157.6 | 166.8 | 191.1 | 186.1 | 215.9 | 348.6
378 | 243 | 519.8 | 199.9 | 158.6 | 167.8 | 192 | 186.7 | 216.2 | 349.3
379 | 244 | 519.7 | 200.9 | 159.7 | 168.8 | 192.9 | 187.4 | 216.7 | 350
380 | 245 | 519.7 | 201.9 | 160.7 | 169.8 | 193.8 | 188 | 217.2 | 350.7
381 | 246 | 519.7 | 202.8 | 161.7 | 170.8 | 194.8 | 188.5 | 217.7 | 351.4
382 | 247 | 519.7 | 203.7 | 162.7 | 171.8 | 195.7 | 189 | 218.1 | 352
383 | 248 | 519.6 | 204.6 | 163.7 | 172.7 | 196.6 | 189.6 | 218.7 | 352.6
384 | 249 | 519.4 | 205.5 | 164.6 | 173.7 | 197.5 | 190.2 | 219.2 | 353.2
385 | 250 | 519.3 | 206.5 | 165.6 | 174.7 | 198.4 | 190.8 | 219.5 | 353.7
386 | 251 | 519.4 | 207.5 | 166.5 | 175.7 | 199.4 | 191.4 | 219.9 | 354.4
387 | 252 | 519.4 | 208.6 | 167.5 | 176.7 | 200.3 | 192 | 220.3 | 355
388 | 253 | 519.4 | 209.4 | 168.4 | 177.7 | 201.2 | 192.7 | 220.8 | 355.7
389 | 254 | 519.6 | 210.2 | 169.4 | 178.7 | 202.2 | 193.3 | 221.3 | 356.3
390 | 255 | 519.5 | 211.2 | 170.3 | 179.6 | 203 | 194 | 221.9 | 356.9
391 | 256 | 519.4 | 212.1 | 171.2 | 180.6 | 203.9 | 194.7 | 222.4 | 357.6
392 | 257 | 519.6 | 213.1 | 172.2 | 181.6 | 204.9 | 195.4 | 223.1 | 358.2
393 | 258 | 519.8 | 214.2 | 173.1 | 182.6 | 205.8 | 196.1 | 223.6 | 358.8
394 | 259 | 519.9 | 215.2 | 174 | 183.6 | 206.7 | 196.8 | 224.2 | 359.4
395 | 260 | 520 | 216.1 | 175 | 184.5 | 207.5 | 197.5 | 224.8 | 360
396 | 261 | 520.2 | 216.9 | 176 | 185.4 | 208.4 | 198.2 | 225.3 | 360.6
397 | 262 | 520.5 | 217.9 | 177 | 186.3 | 209.2 | 198.9 | 225.7 | 361.3
398 | 263 | 520.7 | 219 | 177.9 | 187.3 | 210.1 | 199.6 | 226 | 361.9
399 | 264 | 520.8 | 219.9 | 178.9 | 188.2 | 210.9 | 200.3 | 226.4 | 362.5
400 | 265 | 521 | 220.8 | 179.8 | 189.1 | 211.8 | 201 | 226.8 | 363.1
401 | 266 | 521.1 | 221.7 | 180.8 | 190 | 212.6 | 201.6 | 227.1 | 363.7
402 | 267 | 521.3 | 222.8 | 181.8 | 190.9 | 213.5 | 202.3 | 227.4 | 364.3
403 | 268 | 521.4 | 223.5 | 182.7 | 191.8 | 214.3 | 202.9 | 227.8 | 364.9
404 | 269 | 521.2 | 224.3 | 183.7 | 192.7 | 215.1 | 203.6 | 228.2 | 365.5
405 | 270 | 521.2 | 225.2 | 184.6 | 193.6 | 216 | 204.2 | 228.8 | 366
406 | 271 | 521.1 | 226 | 185.5 | 194.5 | 216.9 | 204.9 | 229.2 | 366.5
407 | 272 | 520.9 | 226.8 | 186.4 | 195.4 | 217.7 | 205.5 | 229.6 | 366.9
408 | 273 | 520.6 | 227.7 | 187.3 | 196.4 | 218.6 | 206.2 | 230 | 367.4
409 | 274 | 520.9 | 228.7 | 188.2 | 197.3 | 219.5 | 206.8 | 230.4 | 367.9
410 | 275 | 521.1 | 229.5 | 189.1 | 198.1 | 220.4 | 207.4 | 231 | 368.4
411 | 276 | 521 | 230.4 | 189.9 | 199.1 | 221.3 | 208 | 231.5 | 368.9
412 | 277 | 520.9 | 231.2 | 190.9 | 199.9 | 222.1 | 208.5 | 232 | 369.5
413 | 278 | 520.8 | 232.2 | 191.7 | 200.8 | 223 | 209.1 | 232.5 | 370
414 | 279 | 520.6 | 233.1 | 192.7 | 201.7 | 223.9 | 209.7 | 233 | 370.3
415 | 280 | 520.5 | 234.1 | 193.5 | 202.6 | 224.8 | 210.3 | 233.5 | 370.8
416 | 281 | 520.3 | 234.9 | 194.4 | 203.5 | 225.6 | 210.9 | 233.7 | 371.2
417 | 282 | 520.1 | 235.8 | 195.3 | 204.3 | 226.5 | 211.6 | 233.9 | 371.6
418 | 283 | 520.2 | 236.7 | 196 | 205.2 | 227.4 | 212.2 | 234.3 | 372
419 | 284 | 520.1 | 237.6 | 196.9 | 206.1 | 228.3 | 212.8 | 234.8 | 372.4
420 | 285 | 519.9 | 238.3 | 197.7 | 207 | 229.2 | 213.5 | 234.9 | 372.7
421 | 286 | 519.6 | 239 | 198.6 | 207.8 | 230.1 | 214.1 | 235.4 | 373.1
422 | 287 | 519.5 | 239.6 | 199.4 | 208.7 | 231 | 214.6 | 235.9 | 373.5
423 | 288 | 519.4 | 239.8 | 200.3 | 209.5 | 231.8 | 215.2 | 236.3 | 373.9
424 | 289 | 519.6 | 240 | 201.1 | 210.3 | 232.7 | 215.8 | 236.6 | 374.4
425 | 290 | 519.7 | 240.3 | 202 | 211.1 | 233.5 | 216.4 | 237 | 374.9
426 | 291 | 519.8 | 240.8 | 202.8 | 212 | 234.4 | 217.1 | 237.5 | 375.3
427 | 292 | 520 | 241.5 | 203.6 | 212.8 | 235.2 | 217.8 | 238.3 | 375.7
428 | 293 | 520 | 242.3 | 204.4 | 213.6 | 236.1 | 218.4 | 238.7 | 376.1
429 | 294 | 519.8 | 243.1 | 205.2 | 214.4 | 236.9 | 219 | 239.2 | 376.5
430 | 295 | 519.6 | 243.8 | 206 | 215.3 | 237.8 | 219.6 | 239.5 | 376.9
431 | 296 | 519.7 | 244.4 | 207 | 216 | 238.5 | 220.2 | 240.1 | 377.3
432 | 297 | 519.7 | 245.1 | 207.7 | 216.9 | 239.4 | 220.7 | 240.3 | 377.6
433 | 298 | 519.7 | 245.6 | 208.5 | 217.7 | 240.3 | 221.2 | 240.8 | 378
434 | 299 | 519.7 | 246.5 | 209.2 | 218.5 | 241.2 | 221.7 | 241.2 | 378.3
435 | 300 | 519.5 | 247.2 | 210.1 | 219.3 | 242 | 222.3 | 241.6 | 378.7
436 | 301 | 519.3 | 247.9 | 210.9 | 220 | 242.8 | 222.8 | 242 | 379.1
437 | 302 | 519.3 | 248.5 | 211.7 | 220.8 | 243.6 | 223.4 | 242.2 | 379.4
438 | 303 | 519.3 | 249.2 | 212.5 | 221.6 | 244.5 | 223.9 | 242.6 | 379.8
439 | 304 | 519.4 | 249.9 | 213.3 | 222.4 | 245.3 | 224.5 | 243.1 | 380.3
440 | 305 | 519.5 | 250.5 | 214.1 | 223.2 | 246.1 | 225 | 243.4 | 380.7
441 | 306 | 519.5 | 251.3 | 214.8 | 223.9 | 246.9 | 225.5 | 243.8 | 381.1
442 | 307 | 519.4 | 252.1 | 215.6 | 224.7 | 247.7 | 226.1 | 244.1 | 381.5
443 | 308 | 519.4 | 252.8 | 216.4 | 225.5 | 248.5 | 226.7 | 244.5 | 381.8
444 | 309 | 519.6 | 253.6 | 217.1 | 226.3 | 249.3 | 227.2 | 245 | 382.2
445 | 310 | 519.8 | 254.2 | 217.9 | 227 | 250.1 | 227.8 | 245.5 | 382.6
446 | 311 | 519.9 | 254.9 | 218.7 | 227.8 | 250.9 | 228.4 | 245.9 | 382.9
447 | 312 | 519.9 | 255.6 | 219.4 | 228.6 | 251.7 | 228.9 | 246.3 | 383.3
448 | 313 | 519.9 | 256.3 | 220.2 | 229.3 | 252.4 | 229.4 | 246.8 | 383.7
449 | 314 | 520 | 257 | 220.9 | 230.1 | 253.2 | 229.9 | 247.2 | 384.1
450 | 315 | 520.2 | 257.8 | 221.7 | 230.8 | 253.9 | 230.3 | 247.4 | 384.4
451 | 316 | 520.1 | 258.5 | 222.4 | 231.6 | 254.7 | 230.7 | 247.8 | 384.7
452 | 317 | 520 | 259.3 | 223.1 | 232.4 | 255.5 | 231.2 | 248.3 | 385.1
453 | 318 | 519.8 | 260.1 | 223.8 | 233.1 | 256.3 | 231.7 | 248.7 | 385.4
454 | 319 | 519.7 | 261 | 224.5 | 233.9 | 257.1 | 232.1 | 249.2 | 385.7
455 | 320 | 519.6 | 261.7 | 225.1 | 234.7 | 257.9 | 232.6 | 249.6 | 386
456 | 321 | 519.5 | 262.4 | 225.9 | 235.4 | 258.7 | 233.1 | 250.1 | 386.3
457 | 322 | 519.5 | 263.3 | 226.6 | 236.2 | 259.4 | 233.6 | 250.5 | 386.5
458 | 323 | 519.5 | 264.1 | 227.3 | 236.9 | 260.2 | 234.1 | 250.8 | 386.8
459 | 324 | 519.4 | 264.7 | 228 | 237.7 | 261 | 234.6 | 251.1 | 387.1
460 | 325 | 519.5 | 265.3 | 228.9 | 238.4 | 261.7 | 235.1 | 251.5 | 387.4
461 | 326 | 519.6 | 266.1 | 229.6 | 239.1 | 262.5 | 235.5 | 251.9 | 387.7
462 | 327 | 519.6 | 266.9 | 230.5 | 239.8 | 263.1 | 236 | 252.2 | 388
463 | 328 | 519.7 | 267.6 | 231.2 | 240.6 | 263.9 | 236.5 | 252.6 | 388.3
464 | 329 | 519.8 | 268.3 | 232 | 241.2 | 264.6 | 236.9 | 253 | 388.7
465 | 330 | 520.1 | 269.1 | 232.7 | 241.9 | 265.3 | 237.4 | 253.4 | 389
466 | 331 | 520.3 | 269.9 | 233.4 | 242.7 | 266 | 237.9 | 254 | 389.3
467 | 332 | 520.1 | 270.5 | 234.2 | 243.3 | 266.7 | 238.4 | 254.2 | 389.6
468 | 333 | 519.9 | 271.3 | 235 | 244 | 267.3 | 238.9 | 254.6 | 389.9
469 | 334 | 519.9 | 271.8 | 235.7 | 244.7 | 268 | 239.4 | 254.8 | 390.2
470 | 335 | 520.2 | 272.5 | 236.4 | 245.4 | 268.7 | 239.8 | 255.2 | 390.4
471 | 336 | 520.1 | 273 | 237.1 | 246.1 | 269.4 | 240.3 | 255.6 | 390.6
472 | 337 | 519.8 | 273.7 | 237.7 | 246.8 | 270.2 | 240.8 | 255.8 | 390.9
473 | 338 | 519.4 | 274.3 | 238.4 | 247.5 | 270.9 | 241.3 | 256.1 | 391.2
474 | 339 | 519.1 | 275 | 239.2 | 248.2 | 271.6 | 241.7 | 256.6 | 391.5
475 | 340 | 519.1 | 275.7 | 239.8 | 248.9 | 272.4 | 242.2 | 257 | 391.7
476 | 341 | 519 | 276.3 | 240.5 | 249.6 | 273.1 | 242.6 | 257.4 | 391.9
477 | 342 | 518.8 | 277.2 | 241.1 | 250.3 | 273.8 | 243 | 257.7 | 392.1
478 | 343 | 518.7 | 278 | 241.9 | 251 | 274.6 | 243.5 | 258 | 392.2
479 | 344 | 518.7 | 278.6 | 242.5 | 251.7 | 275.3 | 243.9 | 258.3 | 392.5
480 | 345 | 518.6 | 279.3 | 243.2 | 252.4 | 276 | 244.4 | 258.7 | 392.8
481 | 346 | 518.3 | 280.1 | 243.9 | 253.1 | 276.7 | 244.8 | 259.2 | 393
482 | 347 | 518.3 | 280.8 | 244.6 | 253.8 | 277.5 | 245.3 | 259.5 | 393.3
483 | 348 | 518.3 | 281.3 | 245.2 | 254.4 | 278.2 | 245.8 | 259.7 | 393.5
484 | 349 | 518.5 | 281.7 | 245.9 | 255.1 | 278.9 | 246.3 | 260 | 393.7
485 | 350 | 518.6 | 282.2 | 246.6 | 255.8 | 279.6 | 246.7 | 260.2 | 393.9
486 | 351 | 518.8 | 282.7 | 247.2 | 256.5 | 280.3 | 247.1 | 260.4 | 394.2
487 | 352 | 518.8 | 283.4 | 248 | 257.1 | 281 | 247.6 | 260.5 | 394.5
488 | 353 | 518.9 | 284.2 | 248.6 | 257.8 | 281.6 | 248 | 260.8 | 394.7
489 | 354 | 519 | 284.9 | 249.2 | 258.4 | 282.3 | 248.4 | 261.2 | 395
490 | 355 | 519.2 | 285.6 | 249.9 | 259.1 | 283 | 248.8 | 261.6 | 395.2
491 | 356 | 519.3 | 286.2 | 250.6 | 259.7 | 283.7 | 249.3 | 262 | 395.5
492 | 357 | 519.5 | 286.9 | 251.3 | 260.4 | 284.3 | 249.7 | 262.5 | 395.7
493 | 358 | 519.6 | 287.4 | 252 | 261 | 285 | 250.1 | 262.9 | 396
494 | 359 | 519.4 | 287.8 | 252.8 | 261.6 | 285.6 | 250.5 | 263.1 | 396.3
495 | 360 | 519.3 | 288.5 | 253.5 | 262.3 | 286.3 | 250.9 | 263.3 | 396.5
496 | 361 | 519.1 | 289.2 | 254.1 | 262.9 | 286.9 | 251.3 | 263.6 | 396.7
497 | 362 | 519.1 | 289.8 | 254.8 | 263.6 | 287.6 | 251.7 | 264 | 396.9
498 | 363 | 519.1 | 290.4 | 255.4 | 264.2 | 288.3 | 252.1 | 264.3 | 397.1
499 | 364 | 519.1 | 291.2 | 256 | 264.8 | 289 | 252.5 | 264.6 | 397.3
500 | 365 | 519 | 291.8 | 256.7 | 265.5 | 289.6 | 252.9 | 264.8 | 397.6
501 | 366 | 518.7 | 292.5 | 257.3 | 266.1 | 290.4 | 253.2 | 264.8 | 397.8
502 | 367 | 518.5 | 293.2 | 257.9 | 266.8 | 291.2 | 253.6 | 264.8 | 398
503 | 368 | 518.4 | 293.7 | 258.4 | 267.4 | 292 | 254 | 265 | 398.2
504 | 369 | 518.5 | 294.3 | 259.1 | 268.1 | 292.7 | 254.4 | 265.2 | 398.4
505 | 370 | 518.4 | 294.9 | 259.7 | 268.7 | 293.4 | 254.7 | 265.6 | 398.6
506 | 371 | 518.2 | 295.6 | 260.4 | 269.3 | 294.1 | 255.1 | 266 | 398.7
507 | 372 | 518.1 | 296.2 | 260.9 | 270 | 294.8 | 255.5 | 266.3 | 399
508 | 373 | 518.1 | 296.8 | 261.6 | 270.6 | 295.5 | 255.9 | 266.5 | 399.2
509 | 374 | 518 | 297.1 | 262.2 | 271.2 | 296.2 | 256.3 | 266.8 | 399.3
510 | 375 | 517.7 | 297.7 | 262.9 | 271.8 | 296.9 | 256.7 | 267.4 | 399.4
511 | 376 | 517.8 | 298.2 | 263.5 | 272.5 | 297.6 | 257.1 | 267.9 | 399.6
512 | 377 | 517.8 | 298.7 | 264.1 | 273.1 | 298.3 | 257.4 | 268.4 | 399.7
513 | 378 | 517.7 | 299.3 | 264.8 | 273.7 | 298.9 | 257.8 | 268.8 | 399.8
514 | 379 | 517.8 | 299.9 | 265.4 | 274.3 | 299.6 | 258.1 | 269.1 | 400
515 | 380 | 517.6 | 300.6 | 266 | 275 | 300.4 | 258.5 | 269.4 | 400.1
516 | 381 | 517.5 | 301.2 | 266.7 | 275.6 | 301 | 258.8 | 269.8 | 400.3
517 | 382 | 517.6 | 301.8 | 267.2 | 276.2 | 301.7 | 259.1 | 270.3 | 400.5
518 | 383 | 517.7 | 302.5 | 267.9 | 276.8 | 302.4 | 259.5 | 270.6 | 400.7
519 | 384 | 517.9 | 303.1 | 268.4 | 277.4 | 303.1 | 259.8 | 271 | 400.8
520 | 385 | 518.2 | 303.5 | 269 | 278.1 | 303.7 | 260.1 | 271.3 | 401
521 | 386 | 518.2 | 304 | 269.6 | 278.7 | 304.3 | 260.5 | 271.5 | 401.1
522 | 387 | 518.2 | 304.4 | 270.2 | 279.3 | 305.1 | 260.9 | 272 | 401.2
523 | 388 | 518.2 | 304.9 | 270.9 | 279.9 | 305.7 | 261.2 | 272.3 | 401.4
524 | 389 | 518.4 | 305.5 | 271.5 | 280.5 | 306.3 | 261.6 | 272.5 | 401.5
525 | 390 | 518.6 | 306.1 | 272.1 | 281.1 | 307 | 261.9 | 272.8 | 401.7
526 | 391 | 518.8 | 306.7 | 272.7 | 281.7 | 307.7 | 262.3 | 273 | 401.8
527 | 392 | 519.1 | 307.2 | 273.4 | 282.3 | 308.4 | 262.6 | 273.3 | 402.1
528 | 393 | 519.4 | 307.7 | 274 | 282.9 | 309 | 263 | 273.8 | 402.2
529 | 394 | 519.5 | 308.2 | 274.6 | 283.4 | 309.6 | 263.3 | 274.2 | 402.4
530 | 395 | 519.7 | 308.7 | 275.2 | 284.1 | 310.2 | 263.7 | 274.4 | 402.6
531 | 396 | 519.8 | 309.2 | 275.8 | 284.7 | 310.8 | 264 | 274.6 | 402.8
532 | 397 | 519.8 | 309.8 | 276.4 | 285.2 | 311.5 | 264.3 | 274.9 | 403
533 | 398 | 519.9 | 310.4 | 277 | 285.8 | 312.1 | 264.7 | 275.2 | 403.1
534 | 399 | 520.3 | 310.9 | 277.6 | 286.4 | 312.7 | 265 | 275.4 | 403.3
535 | 400 | 520.6 | 311.4 | 278.2 | 286.9 | 313.3 | 265.3 | 275.7 | 403.5
536 | 401 | 520.7 | 312 | 278.8 | 287.3 | 313.9 | 265.6 | 276 | 403.6
537 | 402 | 520.7 | 312.5 | 279.5 | 287.8 | 314.4 | 265.9 | 276.3 | 403.8
538 | 403 | 520.7 | 313.2 | 280.2 | 288.3 | 314.8 | 266.2 | 276.6 | 403.9
539 | 404 | 520.9 | 313.7 | 280.9 | 288.8 | 315.3 | 266.5 | 277 | 404.1
540 | 405 | 521.1 | 314.4 | 281.5 | 289.3 | 315.9 | 266.8 | 277.4 | 404.2
541 | 406 | 521.1 | 314.9 | 282.1 | 290 | 316.4 | 267.1 | 277.7 | 404.4
542 | 407 | 521.1 | 315.5 | 282.7 | 290.6 | 317 | 267.3 | 278 | 404.6
543 | 408 | 521.2 | 316.1 | 283.3 | 291.2 | 317.5 | 267.6 | 278.3 | 404.8
544 | 409 | 521.1 | 316.8 | 283.8 | 291.9 | 318.1 | 268 | 278.6 | 404.9
545 | 410 | 520.8 | 317.3 | 284.5 | 292.5 | 318.7 | 268.2 | 278.9 | 405.1
546 | 411 | 520.8 | 317.7 | 285 | 293 | 319.2 | 268.5 | 279.2 | 405.2
547 | 412 | 520.8 | 318.3 | 285.6 | 293.6 | 319.8 | 268.8 | 279.6 | 405.3
548 | 413 | 520.7 | 318.8 | 286.2 | 294.1 | 320.4 | 269.1 | 279.7 | 405.4
549 | 414 | 520.5 | 319.3 | 286.8 | 294.6 | 321 | 269.4 | 280 | 405.6
550 | 415 | 520.4 | 319.7 | 287.4 | 295.2 | 321.6 | 269.7 | 280.2 | 405.9
551 | 416 | 520.3 | 320.1 | 288 | 295.8 | 322.1 | 270 | 280.4 | 405.9
552 | 417 | 520.1 | 320.8 | 288.5 | 296.4 | 322.8 | 270.3 | 280.7 | 406
553 | 418 | 520 | 321.4 | 289 | 297 | 323.4 | 270.6 | 280.9 | 406.1
554 | 419 | 519.9 | 321.9 | 289.6 | 297.5 | 324 | 270.9 | 281.2 | 406.3
555 | 420 | 519.6 | 322.5 | 290.2 | 298 | 324.6 | 271.2 | 281.4 | 406.5
556 | 421 | 519.6 | 323 | 290.8 | 298.6 | 325.1 | 271.5 | 281.8 | 406.6
557 | 422 | 519.6 | 323.4 | 291.3 | 299.2 | 325.7 | 271.7 | 282 | 406.8
558 | 423 | 519.5 | 323.9 | 291.9 | 299.8 | 326.3 | 272 | 282.2 | 406.9
559 | 424 | 519.5 | 324.5 | 292.5 | 300.4 | 326.8 | 272.3 | 282.5 | 407.1
560 | 425 | 519.5 | 325.1 | 293 | 301 | 327.4 | 272.6 | 282.7 | 407.2
561 | 426 | 519.5 | 325.7 | 293.6 | 301.6 | 327.9 | 272.8 | 283 | 407.3
562 | 427 | 519.6 | 326.1 | 294.2 | 302.2 | 328.5 | 273.1 | 283.2 | 407.4
563 | 428 | 519.7 | 326.5 | 294.8 | 302.8 | 329 | 273.4 | 283.5 | 407.6
564 | 429 | 519.9 | 327.1 | 295.3 | 303.3 | 329.5 | 273.6 | 283.8 | 407.6
565 | 430 | 519.9 | 327.6 | 295.9 | 303.9 | 330.1 | 273.8 | 284 | 407.7
566 | 431 | 520 | 328.1 | 296.5 | 304.5 | 330.6 | 274.1 | 284.3 | 407.8
567 | 432 | 520.2 | 328.8 | 296.9 | 305.1 | 331.2 | 274.4 | 284.5 | 407.8
568 | 433 | 520.2 | 329.7 | 296.6 | 306 | 332.3 | 274.7 | 284.7 | 407.8
569 | 434 | 520.2 | 329.9 | 297.4 | 306.5 | 332.6 | 274.9 | 284.9 | 407.9
570 | 435 | 520.3 | 330.4 | 298 | 307 | 333.2 | 275.1 | 285.1 | 408.1
571 | 436 | 520.4 | 330.8 | 298.5 | 307.5 | 333.7 | 275.4 | 285.3 | 408.2
572 | 437 | 520.2 | 331.7 | 298.6 | 308.2 | 334.6 | 275.7 | 285.4 | 408.3
573 | 438 | 520.1 | 332.3 | 298.7 | 308.9 | 335.4 | 276 | 285.5 | 408.4
574 | 439 | 520 | 332.7 | 299.2 | 309.5 | 335.9 | 276.2 | 285.7 | 408.6
575 | 440 | 519.9 | 333.3 | 299.7 | 310 | 336.5 | 276.4 | 286 | 408.7
576 | 441 | 519.8 | 333.9 | 300.3 | 310.5 | 337 | 276.6 | 286.3 | 408.8
577 | 442 | 519.8 | 334.4 | 300.9 | 311.1 | 337.4 | 276.8 | 286.6 | 408.9
578 | 443 | 519.8 | 334.8 | 301.4 | 311.7 | 338 | 277.1 | 286.8 | 409
579 | 444 | 519.5 | 335.5 | 301.9 | 312.3 | 338.5 | 277.3 | 287.2 | 409.1
580 | 445 | 519.5 | 335.6 | 303.3 | 312.5 | 338.4 | 277.4 | 287.5 | 409.3
581 | 446 | 519.5 | 336 | 304 | 313 | 338.7 | 277.7 | 287.8 | 409.4
582 | 447 | 519.5 | 337.3 | 303 | 314.1 | 340.3 | 278.1 | 287.9 | 409.4
583 | 448 | 519.5 | 337.4 | 303.9 | 314.5 | 340.5 | 278.2 | 288.1 | 409.6
584 | 449 | 519.6 | 337.9 | 304.5 | 315 | 341 | 278.4 | 288.4 | 409.7
585 | 450 | 519.7 | 338.4 | 304.9 | 315.6 | 341.6 | 278.6 | 288.6 | 409.8
586 | 451 | 519.5 | 338.8 | 305.3 | 316.3 | 342.2 | 278.9 | 288.8 | 409.9
587 | 452 | 519.3 | 339.4 | 305.8 | 316.8 | 342.7 | 279.2 | 289 | 410
588 | 453 | 519.1 | 340 | 306.2 | 317.5 | 343.3 | 279.4 | 289.2 | 410.1
589 | 454 | 519.1 | 340.3 | 306.7 | 318 | 343.8 | 279.6 | 289.4 | 410.1
590 | 455 | 519 | 340.9 | 307.2 | 318.5 | 344.2 | 279.8 | 289.6 | 410.1
591 | 456 | 518.9 | 341.4 | 307.7 | 319 | 344.7 | 280.1 | 289.6 | 410.2
592 | 457 | 518.8 | 342 | 308.2 | 319.6 | 345.2 | 280.3 | 289.9 | 410.2
593 | 458 | 518.8 | 342.3 | 308.8 | 320.1 | 345.6 | 280.5 | 290 | 410.2
594 | 459 | 518.8 | 342.6 | 309.4 | 320.6 | 346.1 | 280.8 | 290.2 | 410.2
595 | 460 | 518.8 | 342.9 | 310.3 | 321 | 346.2 | 280.9 | 290.4 | 410.3
596 | 461 | 519 | 342.8 | 311.9 | 321.1 | 346 | 281 | 290.6 | 410.4
597 | 462 | 519.2 | 343.2 | 312.5 | 321.7 | 346.4 | 281.2 | 290.8 | 410.5
598 | 463 | 519.1 | 343.6 | 313 | 322.2 | 346.9 | 281.4 | 291 | 410.6
599 | 464 | 518.9 | 344 | 313.4 | 322.8 | 347.4 | 281.6 | 291.2 | 410.7
600 | 465 | 518.9 | 344.2 | 314 | 323.3 | 347.8 | 281.9 | 291.4 | 410.8
601 | 466 | 518.8 | 344.5 | 314.5 | 323.8 | 348.3 | 282.1 | 291.5 | 410.9
602 | 467 | 518.9 | 345 | 315 | 324.3 | 348.8 | 282.4 | 291.8 | 411
603 | 468 | 518.9 | 345.4 | 315.6 | 324.8 | 349.2 | 282.6 | 292.1 | 411
604 | 469 | 519.1 | 345.9 | 315.9 | 325.4 | 349.7 | 282.9 | 292.4 | 411
605 | 470 | 519.5 | 346.3 | 316.4 | 325.9 | 350.2 | 283.1 | 292.6 | 411.1
606 | 471 | 519.6 | 346.8 | 316.9 | 326.4 | 350.7 | 283.3 | 292.8 | 411.1
607 | 472 | 519.9 | 347.3 | 317.4 | 326.9 | 351.2 | 283.5 | 293.2 | 411.3
608 | 473 | 520.1 | 347.7 | 317.9 | 327.4 | 351.7 | 283.7 | 293.4 | 411.5
609 | 474 | 520.2 | 348.2 | 318.4 | 327.9 | 352.1 | 283.9 | 293.7 | 411.6
610 | 475 | 520.1 | 348.6 | 318.9 | 328.5 | 352.5 | 284.2 | 293.8 | 411.7
611 | 476 | 520.3 | 348.8 | 319.3 | 329 | 353 | 284.5 | 294.1 | 411.9
612 | 477 | 520.4 | 349.2 | 319.9 | 329.5 | 353.4 | 284.7 | 294.4 | 412
613 | 478 | 520.5 | 349.7 | 320.1 | 330.1 | 354 | 285 | 294.6 | 412.1
614 | 479 | 520.8 | 351 | 319 | 331.2 | 355.5 | 285.4 | 294.7 | 412.1
615 | 480 | 520.9 | 351.3 | 320 | 331.6 | 355.6 | 285.6 | 294.7 | 412.1
616 | 481 | 521 | 351.8 | 320.5 | 332.1 | 356 | 285.9 | 295 | 412
617 | 482 | 521.2 | 352.4 | 320.9 | 332.6 | 356.5 | 286.2 | 295.1 | 412.1
618 | 483 | 521.1 | 352.9 | 321.2 | 333.1 | 357 | 286.5 | 295.3 | 412.2
619 | 484 | 521.2 | 353.1 | 321.9 | 333.5 | 357.2 | 286.7 | 295.6 | 412.3
620 | 485 | 521.5 | 353.2 | 323.2 | 333.7 | 357 | 286.9 | 295.9 | 412.4
621 | 486 | 521.6 | 354.3 | 322.3 | 334.7 | 358.5 | 287.3 | 296.1 | 412.4
622 | 487 | 521.6 | 354.5 | 323.2 | 335 | 358.5 | 287.6 | 296.3 | 412.5
623 | 488 | 521.7 | 354.3 | 324.8 | 335.1 | 358.1 | 287.7 | 296.7 | 412.7
624 | 489 | 521.7 | 354.6 | 325.4 | 335.5 | 358.5 | 288 | 296.9 | 412.8
625 | 490 | 521.7 | 355 | 325.9 | 336 | 358.9 | 288.3 | 297.2 | 412.9
626 | 491 | 521.6 | 355.3 | 326.4 | 336.4 | 359.3 | 288.7 | 297.3 | 412.9
627 | 492 | 521.6 | 355.8 | 326.9 | 336.9 | 359.6 | 289 | 297.5 | 413
628 | 493 | 521.7 | 356.2 | 327.3 | 337.4 | 360 | 289.3 | 297.7 | 413.1
629 | 494 | 521.8 | 356.7 | 327.8 | 337.9 | 360.3 | 289.6 | 297.9 | 413.1
630 | 495 | 521.8 | 357.3 | 328.3 | 338.3 | 360.7 | 289.9 | 298.2 | 413.2
631 | 496 | 521.6 | 357.7 | 328.8 | 338.8 | 361.1 | 290.2 | 298.5 | 413.3
632 | 497 | 521.3 | 358.1 | 329.3 | 339.2 | 361.4 | 290.5 | 298.8 | 413.3
633 | 498 | 521.1 | 358.6 | 329.8 | 339.7 | 361.8 | 290.8 | 299 | 413.4
634 | 499 | 520.9 | 359 | 330.2 | 340.2 | 362.2 | 291.1 | 299.1 | 413.5
635 | 500 | 520.9 | 359.4 | 330.6 | 340.6 | 362.6 | 291.4 | 299.3 | 413.6
636 | 501 | 521 | 359.8 | 331.1 | 341.1 | 363 | 291.7 | 299.5 | 413.7
637 | 502 | 520.7 | 360.7 | 330.1 | 342.1 | 364.3 | 292.2 | 299.6 | 413.7
638 | 503 | 520.7 | 361 | 330.6 | 342.5 | 364.7 | 292.5 | 299.8 | 413.7
639 | 504 | 520.6 | 361.5 | 331.2 | 342.9 | 365 | 292.8 | 300 | 413.9
640 | 505 | 520.4 | 362 | 331.5 | 343.4 | 365.4 | 293.1 | 300.2 | 413.9
641 | 506 | 520.2 | 362.5 | 331.7 | 344 | 366 | 293.5 | 300.4 | 413.9
642 | 507 | 520 | 362.9 | 332.1 | 344.4 | 366.4 | 293.8 | 300.6 | 413.9
643 | 508 | 519.8 | 363.3 | 332.5 | 344.9 | 366.7 | 294.1 | 300.8 | 414
644 | 509 | 519.7 | 363.7 | 332.8 | 345.4 | 367.2 | 294.5 | 300.9 | 414
645 | 510 | 519.6 | 364.1 | 333.3 | 345.8 | 367.5 | 294.8 | 301.1 | 414.1
646 | 511 | 519.5 | 364.5 | 333.7 | 346.3 | 367.9 | 295.1 | 301.2 | 414.1
647 | 512 | 519.5 | 364.7 | 334.6 | 346.5 | 367.9 | 295.4 | 301.5 | 414.1
648 | 513 | 519.5 | 364.6 | 336.1 | 346.6 | 367.4 | 295.6 | 301.8 | 414.3
649 | 514 | 519.6 | 364.8 | 337.1 | 346.8 | 367.4 | 295.8 | 302 | 414.4
650 | 515 | 519.5 | 365.4 | 337.4 | 347.2 | 368 | 296.2 | 302.2 | 414.4
651 | 516 | 519.5 | 366.1 | 337.6 | 347.7 | 368.5 | 296.5 | 302.4 | 414.5
652 | 517 | 519.8 | 366.6 | 338 | 348.1 | 368.8 | 296.9 | 302.6 | 414.5
653 | 518 | 520 | 367 | 338.5 | 348.5 | 369.2 | 297.2 | 302.8 | 414.7
654 | 519 | 520.1 | 367.3 | 338.9 | 348.9 | 369.5 | 297.5 | 303.1 | 414.7
655 | 520 | 520 | 367.7 | 339.3 | 349.3 | 369.9 | 297.9 | 303.5 | 414.7
656 | 521 | 520.2 | 368.1 | 339.7 | 349.7 | 370.2 | 298.2 | 303.7 | 414.9
657 | 522 | 520.2 | 368.4 | 340.1 | 350.1 | 370.6 | 298.5 | 304 | 414.9
658 | 523 | 520.4 | 368.8 | 340.4 | 350.5 | 370.9 | 298.8 | 304.1 | 415
659 | 524 | 520.6 | 369.2 | 340.8 | 350.9 | 371.3 | 299.1 | 304.4 | 415
660 | 525 | 520.9 | 369.6 | 341.2 | 351.3 | 371.6 | 299.4 | 304.7 | 415.2
661 | 526 | 521 | 370.1 | 341.7 | 351.7 | 371.9 | 299.7 | 305 | 415.3
662 | 527 | 521 | 370.4 | 342.2 | 352.1 | 372.2 | 300.1 | 305.2 | 415.4
663 | 528 | 521.2 | 370.8 | 342.6 | 352.5 | 372.6 | 300.4 | 305.5 | 415.5
664 | 529 | 521.4 | 371.1 | 343.1 | 352.9 | 372.9 | 300.7 | 305.8 | 415.5
665 | 530 | 521.3 | 371.5 | 343.4 | 353.2 | 373.3 | 301 | 306.1 | 415.6
666 | 531 | 521.2 | 371.9 | 343.7 | 353.7 | 373.7 | 301.4 | 306.2 | 415.6
667 | 532 | 521 | 372.3 | 344.1 | 354 | 374.1 | 301.7 | 306.4 | 415.7
668 | 533 | 521 | 372.7 | 344.4 | 354.5 | 374.5 | 302 | 306.6 | 415.8
669 | 534 | 521.1 | 373.1 | 344.8 | 354.8 | 374.8 | 302.3 | 306.9 | 415.8
670 | 535 | 521.2 | 373.4 | 345.2 | 355.2 | 375.2 | 302.6 | 307.1 | 415.9
671 | 536 | 521.3 | 373.7 | 345.6 | 355.6 | 375.5 | 303 | 307.4 | 416
672 | 537 | 521.3 | 374 | 345.9 | 356 | 375.9 | 303.3 | 307.6 | 416.1
673 | 538 | 521.1 | 374.3 | 346.1 | 356.4 | 376.4 | 303.6 | 307.8 | 416.2
674 | 539 | 520.9 | 374.6 | 346.5 | 356.8 | 376.7 | 303.9 | 307.9 | 416.1
675 | 540 | 520.7 | 375 | 346.8 | 357.2 | 377.2 | 304.3 | 308.1 | 416.1
676 | 541 | 520.6 | 375.1 | 348 | 357.3 | 377 | 304.5 | 308.5 | 416.2
677 | 542 | 520.6 | 375.4 | 348.6 | 357.6 | 377.2 | 304.9 | 308.7 | 416.3
678 | 543 | 520.8 | 375.8 | 349 | 358 | 377.6 | 305.2 | 309 | 416.4
679 | 544 | 520.7 | 376.2 | 349.3 | 358.4 | 378 | 305.5 | 309.1 | 416.4
680 | 545 | 520.7 | 376.6 | 349.6 | 358.7 | 378.4 | 305.9 | 309.4 | 416.5
681 | 546 | 520.8 | 377.1 | 350 | 359.1 | 378.8 | 306.2 | 309.3 | 416.5
682 | 547 | 520.8 | 377.6 | 350.3 | 359.5 | 379.2 | 306.5 | 309.2 | 416.5
683 | 548 | 520.8 | 378.1 | 350.7 | 359.9 | 379.6 | 306.9 | 309.1 | 416.6
684 | 549 | 520.7 | 378.5 | 351 | 360.3 | 380.1 | 307.2 | 309.2 | 416.7
685 | 550 | 520.8 | 378.8 | 351.4 | 360.6 | 380.5 | 307.5 | 309.4 | 416.7
686 | 551 | 520.9 | 379.3 | 351.7 | 361 | 381 | 307.8 | 309.5 | 416.8
687 | 552 | 520.9 | 379.7 | 352.1 | 361.4 | 381.4 | 308.1 | 309.7 | 416.8
688 | 553 | 520.9 | 380.2 | 352.5 | 361.7 | 381.8 | 308.4 | 309.8 | 416.9
689 | 554 | 521.1 | 380.8 | 352.6 | 362.2 | 382.6 | 308.8 | 310 | 417
690 | 555 | 521.3 | 381.6 | 352.5 | 362.8 | 383.5 | 309.1 | 310.4 | 417
691 | 556 | 521.3 | 382.1 | 352.8 | 363.2 | 384.1 | 309.4 | 310.7 | 417.1
692 | 557 | 521.5 | 382.6 | 353.3 | 363.6 | 384.5 | 309.7 | 311.1 | 417.2
693 | 558 | 521.5 | 383 | 353.7 | 364 | 385 | 310 | 311.5 | 417.3
694 | 559 | 521.6 | 383.4 | 354.1 | 364.4 | 385.6 | 310.3 | 311.8 | 417.4
695 | 560 | 521.6 | 383.8 | 354.6 | 364.8 | 386.1 | 310.6 | 312.1 | 417.4
696 | 561 | 521.7 | 384.3 | 355 | 365.2 | 386.7 | 310.8 | 312.4 | 417.5
697 | 562 | 521.8 | 384.8 | 355.4 | 365.6 | 387.3 | 311.1 | 312.7 | 417.6
698 | 563 | 521.8 | 385.2 | 355.9 | 366 | 387.9 | 311.4 | 312.9 | 417.7
699 | 564 | 521.8 | 385.8 | 356.3 | 366.4 | 388.5 | 311.7 | 313.2 | 417.7
700 | 565 | 521.7 | 386.3 | 356.7 | 366.8 | 389.1 | 312 | 313.3 | 417.7
701 | 566 | 521.6 | 387 | 357 | 367.2 | 389.8 | 312.2 | 313.5 | 417.8
702 | 567 | 521.5 | 387.5 | 357.8 | 367.4 | 390.1 | 312.5 | 313.7 | 417.9
703 | 568 | 521.4 | 388 | 358.8 | 367.6 | 390.4 | 312.7 | 314 | 418
704 | 569 | 521.2 | 388.6 | 359.2 | 368 | 391.1 | 312.9 | 314.3 | 418
705 | 570 | 521.2 | 389.3 | 359.6 | 368.4 | 391.8 | 313.1 | 314.6 | 418
706 | 571 | 521.1 | 390 | 359.9 | 368.7 | 392.5 | 313.4 | 315 | 418.1
707 | 572 | 521.1 | 390.8 | 360.4 | 369.1 | 393.2 | 313.6 | 315.3 | 418.2
708 | 573 | 521.1 | 391.6 | 360.7 | 369.4 | 394 | 313.8 | 315.6 | 418.3
709 | 574 | 521 | 392.4 | 361.1 | 369.8 | 394.8 | 314 | 315.8 | 418.4
710 | 575 | 520.8 | 393.3 | 361.4 | 370.2 | 395.6 | 314.3 | 316 | 418.4
711 | 576 | 520.7 | 394.1 | 361.6 | 370.6 | 396.5 | 314.5 | 316.1 | 418.5
712 | 577 | 520.8 | 394.8 | 361.9 | 370.9 | 397.4 | 314.7 | 316.3 | 418.5
713 | 578 | 520.9 | 395.5 | 362.1 | 371.3 | 398.3 | 314.9 | 316.5 | 418.5
714 | 579 | 520.8 | 396.2 | 362.4 | 371.7 | 399.2 | 315.2 | 316.6 | 418.6
715 | 580 | 520.6 | 396.8 | 362.7 | 372 | 400.1 | 315.4 | 316.8 | 418.7
716 | 581 | 520.7 | 397.4 | 363 | 372.4 | 401.1 | 315.6 | 317 | 418.7
717 | 582 | 520.8 | 398 | 363.2 | 372.8 | 402.1 | 315.8 | 317.1 | 418.7
718 | 583 | 520.9 | 398.4 | 363.5 | 373.2 | 403.1 | 316 | 317.3 | 418.8
719 | 584 | 520.9 | 399.3 | 363.3 | 373.7 | 404.5 | 316.3 | 317.6 | 418.8
720 | 585 | 520.8 | 400 | 363.1 | 374.3 | 405.8 | 316.6 | 317.8 | 418.8
721 | 586 | 520.8 | 400.5 | 363.3 | 374.7 | 406.9 | 316.8 | 317.9 | 418.9
722 | 587 | 520.8 | 401 | 363.6 | 375.1 | 408 | 317 | 318 | 419
723 | 588 | 520.7 | 401.5 | 363.9 | 375.5 | 409.2 | 317.3 | 318 | 419
724 | 589 | 520.6 | 401.9 | 364.2 | 375.9 | 410.4 | 317.5 | 318.2 | 419
725 | 590 | 520.6 | 402.3 | 364.5 | 376.3 | 411.6 | 317.7 | 318.3 | 419.1
726 | 591 | 520.6 | 402.8 | 364.7 | 376.7 | 412.9 | 317.9 | 318.6 | 419.2
727 | 592 | 520.6 | 403.2 | 365.1 | 377.1 | 414.2 | 318.1 | 318.8 | 419.2
728 | 593 | 520.5 | 403.7 | 365.3 | 377.5 | 415.6 | 318.4 | 318.9 | 419.3
729 | 594 | 520.4 | 404.1 | 365.7 | 377.9 | 416.8 | 318.6 | 319 | 419.3
730 | 595 | 520.7 | 404.5 | 366 | 378.4 | 418.2 | 318.8 | 319.2 | 419.2
731 | 596 | 520.7 | 404.9 | 366.3 | 378.9 | 419.5 | 319 | 319.6 | 419.2
732 | 597 | 520.8 | 405.2 | 366.7 | 379.3 | 421 | 319.2 | 319.9 | 419.3
733 | 598 | 520.7 | 405.4 | 367.2 | 379.8 | 422.4 | 319.4 | 320 | 419.4
734 | 599 | 520.5 | 405.5 | 367.6 | 380.2 | 423.9 | 319.6 | 320.2 | 419.4
735 | 600 | 520.4 | 405.8 | 368.1 | 380.7 | 425.5 | 319.8 | 320.6 | 419.4
736 | 601 | 520.4 | 406 | 368.5 | 381.1 | 427.2 | 320 | 321 | 419.4
737 | 602 | 520.4 | 406 | 369.4 | 381.3 | 428.6 | 320.1 | 321.1 | 419.5
738 | 603 | 520.3 | 406.7 | 369 | 382.1 | 431.1 | 320.4 | 321.1 | 419.5
739 | 604 | 520.1 | 407.1 | 369.3 | 382.5 | 433 | 320.7 | 321.3 | 419.5
740 | 605 | 519.8 | 407.6 | 369.5 | 383 | 435.1 | 320.9 | 321.5 | 419.5
741 | 606 | 519.7 | 407.9 | 370.4 | 383.3 | 436.7 | 321.1 | 321.7 | 419.6
742 | 607 | 519.6 | 408.7 | 370.3 | 384 | 439 | 321.3 | 321.9 | 419.5
743 | 608 | 519.7 | 409.1 | 370.9 | 384.4 | 441.2 | 321.5 | 322.2 | 419.5
744 | 609 | 519.9 | 409.3 | 371.4 | 384.8 | 443.6 | 321.8 | 322.4 | 419.4
745 | 610 | 520.2 | 409.2 | 372.3 | 385.2 | 445.6 | 321.9 | 322.5 | 419.5
746 | 611 | 520.3 | 409.3 | 372.6 | 385.7 | 447.9 | 322.2 | 322.7 | 419.5
747 | 612 | 520.3 | 409.4 | 373.3 | 386.2 | 450 | 322.4 | 322.8 | 419.6
748 | 613 | 520.3 | 409.3 | 374.2 | 386.6 | 452.1 | 322.6 | 322.8 | 419.6
749 | 614 | 520.5 | 408.8 | 375.6 | 386.8 | 453.7 | 322.8 | 322.9 | 419.7
750 | 615 | 520.5 | 408.6 | 376.3 | 387.3 | 455.5 | 323 | 322.9 | 419.7
751 | 616 | 520.3 | 408.8 | 376.5 | 388 | 458 | 323.3 | 323.1 | 419.7
752 | 617 | 520.3 | 408.9 | 376.9 | 388.8 | 460.7 | 323.6 | 323.5 | 419.8
753 | 618 | 520.3 | 408.9 | 377.7 | 389.3 | 463.1 | 323.9 | 323.9 | 419.8
754 | 619 | 520.4 | 409.1 | 378.5 | 389.9 | 465.2 | 324.1 | 324.1 | 419.8
755 | 620 | 520.5 | 409.3 | 379.5 | 390.4 | 467.3 | 324.3 | 324.3 | 419.9
756 | 621 | 520.5 | 409.7 | 380.3 | 391 | 469 | 324.5 | 324.6 | 420
757 | 622 | 520.5 | 410.1 | 381.3 | 391.6 | 470.3 | 324.6 | 324.8 | 420
758 | 623 | 520.8 | 410.6 | 382.3 | 392.1 | 470.9 | 324.8 | 325.1 | 420.1
759 | 624 | 520.8 | 411.3 | 383.2 | 392.7 | 472 | 325 | 325.3 | 420.1
760 | 625 | 520.9 | 412 | 384.1 | 393.3 | 472.9 | 325.2 | 325.4 | 420.2
761 | 626 | 521 | 412.9 | 385.1 | 393.8 | 473.6 | 325.4 | 325.5 | 420.3
762 | 627 | 521.1 | 413.6 | 386.2 | 394.3 | 474.2 | 325.5 | 325.8 | 420.3
763 | 628 | 521 | 414.4 | 387.6 | 394.8 | 474.2 | 325.7 | 325.9 | 420.4
764 | 629 | 520.8 | 416.1 | 387.2 | 395.9 | 474.9 | 326 | 326 | 420.4
765 | 630 | 520.7 | 417.1 | 388.7 | 396.3 | 474.3 | 326.1 | 326.1 | 420.5
766 | 631 | 520.7 | 418.5 | 389.8 | 396.9 | 473.8 | 326.3 | 326.3 | 420.5
767 | 632 | 520.6 | 420 | 390.8 | 397.6 | 473.5 | 326.5 | 326.4 | 420.5
768 | 633 | 520.7 | 421.7 | 391.7 | 398.2 | 473.3 | 326.7 | 326.6 | 420.5
769 | 634 | 520.5 | 423.5 | 392.6 | 398.9 | 473 | 326.9 | 326.8 | 420.5
770 | 635 | 520.5 | 425.2 | 394 | 399.4 | 472.5 | 327 | 327.1 | 420.6
771 | 636 | 520.7 | 426.5 | 396.1 | 399.7 | 471.5 | 327.1 | 327.5 | 420.8
772 | 637 | 520.8 | 428.6 | 396.8 | 400.4 | 471.8 | 327.3 | 327.8 | 420.8
773 | 638 | 520.7 | 430.9 | 396.6 | 401.5 | 472.8 | 327.5 | 327.9 | 420.7
774 | 639 | 520.5 | 432.5 | 398 | 402 | 472.4 | 327.7 | 328.1 | 420.8
775 | 640 | 520.3 | 434.1 | 399 | 402.7 | 472.2 | 327.9 | 328.3 | 420.8
776 | 641 | 520.3 | 435.7 | 399.9 | 403.3 | 472.1 | 328.1 | 328.5 | 420.9
777 | 642 | 520.2 | 437.2 | 400.6 | 404 | 472.3 | 328.3 | 328.8 | 420.9
778 | 643 | 520.1 | 438.6 | 401.5 | 404.7 | 472.3 | 328.5 | 329 | 420.8
779 | 644 | 520.2 | 440.1 | 402.3 | 405.4 | 472.5 | 328.6 | 329.2 | 420.8
780 | 645 | 520.5 | 441.4 | 403.2 | 406 | 472.6 | 328.8 | 329.6 | 420.8
781 | 646 | 520.7 | 442.4 | 404.9 | 406.4 | 472.9 | 328.9 | 329.8 | 420.9
782 | 647 | 520.9 | 443.6 | 405.7 | 407 | 473.5 | 329 | 329.9 | 420.9
783 | 648 | 521 | 444.9 | 406.4 | 407.8 | 473.7 | 329.2 | 330.1 | 421
784 | 649 | 520.9 | 446 | 407.2 | 408.4 | 474 | 329.4 | 330.2 | 421
785 | 650 | 521.1 | 447 | 408 | 409.1 | 474.2 | 329.5 | 330.4 | 421
786 | 651 | 521.3 | 447.9 | 408.8 | 409.8 | 474.2 | 329.7 | 330.5 | 421.1
787 | 652 | 521.5 | 448.6 | 409.6 | 410.5 | 474.4 | 329.8 | 330.6 | 421.1
788 | 653 | 521.6 | 449.5 | 410.3 | 411.1 | 474.6 | 330 | 330.7 | 421.2
789 | 654 | 521.5 | 450.3 | 411.1 | 411.8 | 474.9 | 330.3 | 330.8 | 421.2
790 | 655 | 521.8 | 451.1 | 412 | 412.5 | 475.1 | 330.5 | 331.1 | 421.2
791 | 656 | 522.1 | 451.8 | 412.8 | 413.2 | 475.2 | 330.7 | 331.2 | 421.2
792 | 657 | 522.1 | 452.3 | 413.6 | 413.9 | 474.9 | 330.9 | 331.3 | 421.3
793 | 658 | 522 | 453 | 414.3 | 414.6 | 474.5 | 331.1 | 331.4 | 421.4
794 | 659 | 522.1 | 453.7 | 415.1 | 415.3 | 473.8 | 331.3 | 331.5 | 421.4
795 | 660 | 521.9 | 454.1 | 415.9 | 416 | 473.1 | 331.4 | 331.6 | 421.5
796 | 661 | 521.8 | 454.4 | 416.7 | 416.7 | 472.3 | 331.7 | 331.7 | 421.6
797 | 662 | 521.8 | 454.5 | 417.5 | 417.4 | 471.6 | 331.9 | 331.7 | 421.6
798 | 663 | 521.7 | 454.6 | 418.2 | 418.1 | 470.9 | 332.1 | 332.1 | 421.6
799 | 664 | 521.6 | 454.7 | 419.1 | 418.8 | 470.3 | 332.3 | 332.3 | 421.6
800 | 665 | 521.6 | 454.6 | 419.9 | 419.5 | 470.3 | 332.6 | 332.5 | 421.6
801 | 666 | 521.7 | 454.3 | 420.8 | 420.2 | 470.3 | 332.8 | 332.6 | 421.5
802 | 667 | 521.8 | 454.2 | 421.7 | 420.9 | 470.4 | 333 | 332.8 | 421.6
803 | 668 | 521.9 | 453.9 | 422.6 | 421.6 | 470.1 | 333.2 | 333 | 421.6
804 | 669 | 521.9 | 454.4 | 422.1 | 422.8 | 471.2 | 333.6 | 333.1 | 421.6
805 | 670 | 522 | 454.1 | 423.1 | 423.5 | 471.5 | 333.8 | 333.3 | 421.6
806 | 671 | 522.1 | 453.7 | 424.1 | 424.2 | 471.6 | 334 | 333.5 | 421.6
807 | 672 | 522 | 453.4 | 425.1 | 424.8 | 471.7 | 334.2 | 333.6 | 421.6
808 | 673 | 522 | 453.2 | 426.1 | 425.5 | 471.6 | 334.4 | 333.8 | 421.6
809 | 674 | 521.9 | 453.1 | 427.1 | 426.2 | 471.9 | 334.6 | 333.9 | 421.7
810 | 675 | 522 | 452.9 | 428 | 426.8 | 472.4 | 334.8 | 334.1 | 421.7
811 | 676 | 522.3 | 452.8 | 429.1 | 427.5 | 472.8 | 335 | 334.2 | 421.7
812 | 677 | 522.4 | 452.7 | 429.9 | 428.1 | 473.5 | 335.2 | 334.3 | 421.8
813 | 678 | 522.3 | 452.6 | 430.8 | 428.8 | 474.2 | 335.4 | 334.5 | 421.9
814 | 679 | 522.2 | 452.5 | 431.7 | 429.4 | 474.8 | 335.6 | 334.8 | 422
815 | 680 | 522.2 | 452.3 | 432.7 | 430 | 475.1 | 335.8 | 335.1 | 422.1
816 | 681 | 522.4 | 452.3 | 433.7 | 430.6 | 475.5 | 335.9 | 335.4 | 422.1
817 | 682 | 522.5 | 452.3 | 434.5 | 431.2 | 476 | 336.1 | 335.6 | 422.2
818 | 683 | 522.6 | 452.4 | 435.2 | 431.9 | 476.5 | 336.3 | 335.8 | 422.2
819 | 684 | 522.6 | 452.6 | 435.8 | 432.6 | 476.8 | 336.4 | 336.1 | 422.3
820 | 685 | 522.6 | 452.8 | 436.4 | 433.3 | 477.2 | 336.6 | 336.4 | 422.3
821 | 686 | 522.8 | 453.1 | 436.8 | 434.1 | 477.8 | 336.8 | 336.5 | 422.3
822 | 687 | 522.8 | 453.2 | 437.1 | 434.9 | 478.2 | 337 | 336.7 | 422.3
823 | 688 | 522.8 | 453.5 | 437.4 | 435.7 | 478.7 | 337.1 | 336.9 | 422.3
824 | 689 | 522.7 | 453.7 | 437.6 | 436.5 | 478.9 | 337.3 | 337.1 | 422.3
825 | 690 | 522.4 | 454 | 437.6 | 437.4 | 479 | 337.4 | 337.2 | 422.3
826 | 691 | 522.1 | 454.6 | 437.5 | 438.3 | 479.2 | 337.7 | 337.4 | 422.3
827 | 692 | 522 | 455 | 437.3 | 439.4 | 479.4 | 337.9 | 337.5 | 422.3
828 | 693 | 522 | 455.4 | 437.1 | 440.4 | 479.7 | 338.1 | 337.7 | 422.4
829 | 694 | 522 | 455.8 | 437 | 441.5 | 479.9 | 338.3 | 338 | 422.4
830 | 695 | 521.9 | 456.2 | 436.9 | 442.7 | 480.1 | 338.5 | 338.2 | 422.4
831 | 696 | 522 | 456.6 | 436.9 | 443.9 | 480.4 | 338.7 | 338.4 | 422.4
832 | 697 | 521.9 | 456.7 | 437.5 | 445 | 480.2 | 338.9 | 338.6 | 422.5
833 | 698 | 521.9 | 456.9 | 437.5 | 446.3 | 480.5 | 339.1 | 338.6 | 422.5
834 | 699 | 521.9 | 457.3 | 436.9 | 447.7 | 481.3 | 339.4 | 338.7 | 422.4
835 | 700 | 522 | 457.5 | 437.2 | 448.8 | 481.4 | 339.5 | 338.7 | 422.5
836 | 701 | 521.9 | 457.9 | 437.4 | 449.8 | 481.5 | 339.7 | 339 | 422.4
837 | 702 | 521.8 | 458.3 | 437.7 | 450.6 | 481.7 | 339.9 | 339 | 422.4
838 | 703 | 521.9 | 458.6 | 438 | 451.3 | 481.9 | 340.2 | 339 | 422.5
839 | 704 | 521.8 | 458.9 | 438.3 | 451.9 | 482 | 340.4 | 338.9 | 422.5
840 | 705 | 521.9 | 459.3 | 438.6 | 452.3 | 482.2 | 340.6 | 339 | 422.6
841 | 706 | 521.9 | 459.5 | 439.3 | 452.7 | 482.1 | 340.8 | 339 | 422.7
842 | 707 | 522.1 | 459.8 | 439.9 | 453 | 482.1 | 340.9 | 339 | 422.7
843 | 708 | 522.1 | 459.7 | 441.3 | 453 | 481.5 | 341.1 | 339.3 | 422.7
844 | 709 | 522 | 460.1 | 441.8 | 453.3 | 481.5 | 341.4 | 339.6 | 422.7
845 | 710 | 522 | 460.6 | 442.3 | 453.6 | 481.6 | 341.6 | 339.9 | 422.8
846 | 711 | 521.9 | 461 | 442.7 | 454 | 481.7 | 341.9 | 340.1 | 422.9
847 | 712 | 521.7 | 461.5 | 442.8 | 454.5 | 481.9 | 342.1 | 340.1 | 422.9
848 | 713 | 521.5 | 462.6 | 442 | 455.3 | 482.9 | 342.5 | 340 | 422.9
849 | 714 | 521.4 | 462.9 | 442.9 | 455.5 | 482.8 | 342.6 | 340.3 | 422.9
850 | 715 | 521.5 | 463.4 | 443.4 | 455.9 | 482.9 | 342.8 | 340.5 | 423
851 | 716 | 521.4 | 463.6 | 444.9 | 456 | 482.3 | 342.9 | 340.6 | 423.1
852 | 717 | 521.2 | 464.2 | 445.4 | 456.4 | 482.4 | 343 | 340.7 | 423.2
853 | 718 | 521.2 | 464.7 | 446 | 456.8 | 482.5 | 343.2 | 340.8 | 423.2
854 | 719 | 521.4 | 465.3 | 446.5 | 457.3 | 482.8 | 343.4 | 341 | 423.2
855 | 720 | 521.4 | 465.9 | 447 | 457.8 | 483 | 343.5 | 341.3 | 423.3
856 | 721 | 521.7 | 466.4 | 447.5 | 458.4 | 483.2 | 343.7 | 341.4 | 423.3
857 | 722 | 521.8 | 466.9 | 447.9 | 459 | 483.2 | 343.8 | 341.8 | 423.2
858 | 723 | 521.9 | 467.2 | 448.8 | 459.4 | 482.8 | 343.9 | 341.9 | 423.3
859 | 724 | 521.8 | 467.8 | 449.1 | 460.1 | 482.8 | 344 | 342.1 | 423.3
860 | 725 | 521.9 | 468.2 | 449.4 | 460.8 | 482.9 | 344.1 | 342.1 | 423.4
861 | 726 | 522 | 468.7 | 449.6 | 461.5 | 483.1 | 344.3 | 342 | 423.4
862 | 727 | 522 | 469.2 | 449.5 | 462.3 | 483.6 | 344.5 | 341.8 | 423.4
863 | 728 | 521.9 | 469.7 | 449.5 | 463 | 483.8 | 344.7 | 341.9 | 423.5
864 | 729 | 521.6 | 470.5 | 448.7 | 464.1 | 484.7 | 345 | 342.1 | 423.4
865 | 730 | 521.3 | 470.9 | 448.7 | 464.9 | 485.1 | 345.2 | 342.2 | 423.5
866 | 731 | 521.3 | 471.2 | 449.2 | 465.7 | 485.2 | 345.3 | 342.2 | 423.7
867 | 732 | 521.3 | 470.9 | 450.5 | 466.2 | 484.7 | 345.4 | 342.3 | 423.8
868 | 733 | 521.4 | 471.2 | 450.7 | 467 | 485 | 345.6 | 342.4 | 423.9
869 | 734 | 521.5 | 471.4 | 451.1 | 467.7 | 485.1 | 345.8 | 342.7 | 424.1
870 | 735 | 521.6 | 471.6 | 451.4 | 468.4 | 485.2 | 345.9 | 342.9 | 424.2
871 | 736 | 521.5 | 471.8 | 451.6 | 469.2 | 485.4 | 346.1 | 343.1 | 424.2
872 | 737 | 521.4 | 472.2 | 451.9 | 469.8 | 485.6 | 346.3 | 343.3 | 424.2
873 | 738 | 521.5 | 472.5 | 452.2 | 470.5 | 485.8 | 346.6 | 343.5 | 424.3
874 | 739 | 521.8 | 473 | 452.5 | 471.2 | 486 | 346.8 | 343.6 | 424.3
875 | 740 | 521.9 | 473.8 | 452.2 | 472.1 | 486.6 | 347 | 343.9 | 424.4
876 | 741 | 522 | 474.2 | 452.6 | 472.8 | 487 | 347.2 | 343.8 | 424.4
877 | 742 | 522.1 | 474.5 | 453.1 | 473.4 | 487.2 | 347.4 | 343.9 | 424.4
878 | 743 | 522.1 | 474.9 | 453.3 | 473.9 | 487.5 | 347.6 | 344.2 | 424.4
879 | 744 | 521.9 | 475.3 | 453.6 | 474.5 | 487.7 | 347.8 | 344.3 | 424.5
880 | 745 | 522 | 475.6 | 454 | 475 | 487.9 | 348 | 344.5 | 424.5
881 | 746 | 522.1 | 475.7 | 454.8 | 475.4 | 487.7 | 348.1 | 344.6 | 424.5
882 | 747 | 522.1 | 476 | 455.1 | 476 | 487.8 | 348.3 | 344.7 | 424.6
883 | 748 | 522 | 476.4 | 455.3 | 476.5 | 488.1 | 348.4 | 344.8 | 424.6
884 | 749 | 522 | 476.8 | 455.6 | 477 | 488.2 | 348.6 | 344.9 | 424.6
885 | 750 | 522 | 477.2 | 456.2 | 477.5 | 488.3 | 348.8 | 345 | 424.6
886 | 751 | 522.1 | 477.5 | 457 | 477.9 | 488.3 | 348.9 | 345.1 | 424.6
887 | 752 | 521.9 | 477.3 | 458.5 | 478 | 487.7 | 349 | 345.2 | 424.7
888 | 753 | 521.9 | 477.7 | 459 | 478.5 | 488 | 349.1 | 345.3 | 424.8
889 | 754 | 522 | 477.9 | 459.3 | 479 | 488.3 | 349.3 | 345.5 | 424.8
890 | 755 | 521.9 | 478.9 | 458.2 | 480 | 489.8 | 349.7 | 345.7 | 424.7
891 | 756 | 521.9 | 478.6 | 459.2 | 480.2 | 489.8 | 349.9 | 346 | 424.6
892 | 757 | 521.8 | 478.7 | 459.6 | 480.5 | 490.2 | 350.1 | 346.2 | 424.6
893 | 758 | 521.7 | 478.8 | 460 | 480.9 | 490.5 | 350.4 | 346.3 | 424.6
894 | 759 | 521.7 | 479 | 460.3 | 481.4 | 490.8 | 350.7 | 346.6 | 424.7
895 | 760 | 521.8 | 479.4 | 460.5 | 481.8 | 491 | 351 | 346.8 | 424.7
896 | 761 | 521.8 | 479.8 | 460.8 | 482.2 | 491.2 | 351.2 | 347 | 424.8
897 | 762 | 521.7 | 480.3 | 461.1 | 482.7 | 491.4 | 351.5 | 347.2 | 424.9
898 | 763 | 521.8 | 480.9 | 461.6 | 483 | 491.3 | 351.8 | 347.3 | 424.9
899 | 764 | 522 | 480.8 | 463.4 | 482.9 | 490.2 | 351.9 | 347.6 | 425.1
900 | 765 | 522.1 | 481 | 463.8 | 483.2 | 489.9 | 352.1 | 347.8 | 425.1
901 | 766 | 522 | 481.3 | 464.1 | 483.7 | 489.9 | 352.3 | 347.9 | 425.1
902 | 767 | 522.1 | 481.6 | 464.5 | 484.1 | 490 | 352.6 | 348 | 425
903 | 768 | 522.2 | 481.9 | 464.8 | 484.4 | 490.4 | 352.8 | 348.1 | 425.1
904 | 769 | 522.3 | 482.1 | 465.1 | 484.8 | 490.8 | 353 | 348.3 | 425.1
905 | 770 | 522.3 | 482.1 | 465.4 | 485.2 | 490.9 | 353.2 | 348.6 | 425.2
906 | 771 | 522.5 | 482.1 | 465.8 | 485.5 | 491 | 353.4 | 348.7 | 425.2
907 | 772 | 522.4 | 482.1 | 466 | 485.9 | 491.4 | 353.6 | 348.8 | 425.3
908 | 773 | 522 | 482.2 | 466.2 | 486.3 | 491.8 | 353.8 | 348.9 | 425.2
909 | 774 | 521.7 | 482.4 | 466.4 | 486.9 | 492.1 | 354 | 349.1 | 425.2
910 | 775 | 521.7 | 482.9 | 466.6 | 487.6 | 492.4 | 354.1 | 349.1 | 425.2
911 | 776 | 521.5 | 483.1 | 466.8 | 488.5 | 492.6 | 354.2 | 349.1 | 425.2
912 | 777 | 521.4 | 483.4 | 467.1 | 489.3 | 492.7 | 354.4 | 349.2 | 425.3
913 | 778 | 521.3 | 483.7 | 467.3 | 490 | 493.1 | 354.5 | 349.2 | 425.3
914 | 779 | 521.2 | 484.1 | 467.5 | 490.6 | 493.6 | 354.7 | 349.3 | 425.3
915 | 780 | 521.2 | 484.5 | 467.8 | 491.5 | 493.7 | 354.8 | 349.3 | 425.3
916 | 781 | 521.3 | 485.1 | 468.2 | 492.4 | 493.8 | 355 | 349.3 | 425.3
917 | 782 | 521.4 | 485.7 | 468.5 | 493.2 | 494 | 355.2 | 349.4 | 425.3
918 | 783 | 521.4 | 486.3 | 468.9 | 494 | 494.5 | 355.4 | 349.4 | 425.4
919 | 784 | 521.5 | 486.9 | 469.1 | 494.8 | 495.4 | 355.6 | 349.6 | 425.5
920 | 785 | 521.6 | 487.4 | 469.5 | 495.6 | 496.3 | 355.8 | 349.7 | 425.5
921 | 786 | 521.7 | 487.9 | 469.8 | 496.4 | 497.5 | 356 | 349.8 | 425.6
922 | 787 | 521.8 | 488.3 | 470.1 | 497.1 | 498.4 | 356.2 | 350 | 425.6
923 | 788 | 521.8 | 488.6 | 470.4 | 497.8 | 498.9 | 356.4 | 350.1 | 425.7
924 | 789 | 521.7 | 489.1 | 470.7 | 498.4 | 498.9 | 356.6 | 350.3 | 425.7
925 | 790 | 521.8 | 489.6 | 470.9 | 499.1 | 498.8 | 356.9 | 350.4 | 425.8
926 | 791 | 521.9 | 490.1 | 471.2 | 499.8 | 498.8 | 357.1 | 350.6 | 425.9
927 | 792 | 522.1 | 490.5 | 471.4 | 500.4 | 498.9 | 357.4 | 350.8 | 426
928 | 793 | 522.1 | 491.1 | 471.6 | 501.2 | 499 | 357.6 | 351 | 426.1
929 | 794 | 522.3 | 491.8 | 471.8 | 502.1 | 498.9 | 357.7 | 351.2 | 426.1
930 | 795 | 522.4 | 492.2 | 472 | 502.9 | 498.5 | 357.9 | 351.4 | 426.1
931 | 796 | 522.4 | 492.3 | 472.2 | 503.6 | 498.2 | 358.1 | 351.6 | 426.1
932 | 797 | 522.4 | 492.6 | 472.6 | 504.4 | 498.3 | 358.3 | 351.9 | 426.2
933 | 798 | 522.3 | 492.9 | 472.9 | 505 | 498.4 | 358.4 | 351.9 | 426.3
934 | 799 | 522 | 493 | 473.2 | 505.7 | 499 | 358.6 | 352 | 426.3
935 | 800 | 521.9 | 493.2 | 473.4 | 506.4 | 499.6 | 358.8 | 351.9 | 426.4
936 | 801 | 522.2 | 493.4 | 473.5 | 507 | 500 | 358.9 | 352 | 426.5
937 | 802 | 522.2 | 494 | 473.7 | 507.7 | 500.3 | 359.1 | 352.1 | 426.5
938 | 803 | 522.1 | 494.6 | 473.8 | 508.3 | 500.8 | 359.2 | 352.2 | 426.6
939 | 804 | 522 | 494.9 | 474 | 508.9 | 501.1 | 359.3 | 352.3 | 426.6
940 | 805 | 521.8 | 495.2 | 474.2 | 509.5 | 501.2 | 359.4 | 352.3 | 426.7
941 | 806 | 521.9 | 495.6 | 474.4 | 510.1 | 501.5 | 359.6 | 352.4 | 426.7
942 | 807 | 521.9 | 496 | 474.6 | 510.9 | 501.7 | 359.7 | 352.6 | 426.7
943 | 808 | 521.8 | 496.5 | 474.8 | 511.4 | 501.8 | 359.8 | 352.6 | 426.7
944 | 809 | 521.8 | 496.9 | 475.1 | 511.8 | 501.9 | 359.9 | 352.6 | 426.7
945 | 810 | 521.9 | 497.2 | 475.3 | 512 | 502.4 | 360 | 352.6 | 426.7
946 | 811 | 521.7 | 497.4 | 475.6 | 512.4 | 503.5 | 360.2 | 352.6 | 426.8
947 | 812 | 521.6 | 497.3 | 475.9 | 512.7 | 504.4 | 360.3 | 352.5 | 426.9
948 | 813 | 521.5 | 497 | 476.3 | 512.9 | 505.2 | 360.4 | 352.6 | 426.9
949 | 814 | 521.4 | 497.1 | 476.6 | 513.3 | 505.7 | 360.5 | 352.6 | 426.9
950 | 815 | 521.3 | 497.3 | 476.9 | 513.5 | 506.3 | 360.6 | 352.7 | 426.9
951 | 816 | 521.2 | 497.4 | 477 | 513.7 | 507 | 360.7 | 352.7 | 426.9
952 | 817 | 521.2 | 497.3 | 477.3 | 514 | 507.9 | 360.8 | 352.7 | 427
953 | 818 | 521.1 | 497.2 | 477.6 | 514.4 | 508.7 | 360.9 | 352.9 | 427
954 | 819 | 521 | 497.3 | 477.8 | 514.8 | 509.8 | 361 | 353 | 427
955 | 820 | 521 | 498.1 | 478 | 515.2 | 510.2 | 361.1 | 353.1 | 427
956 | 821 | 521.1 | 498.4 | 478.2 | 515.8 | 510.4 | 361.2 | 353.2 | 426.9
957 | 822 | 521.2 | 498.6 | 478.3 | 516.5 | 510.9 | 361.3 | 353.1 | 426.9
958 | 823 | 521.1 | 498.5 | 478.5 | 517.2 | 511.9 | 361.4 | 353.2 | 427
959 | 824 | 521 | 498.3 | 478.6 | 518 | 513.3 | 361.5 | 353.2 | 427
960 | 825 | 521 | 498.3 | 478.9 | 518.6 | 514.1 | 361.5 | 353 | 427
961 | 826 | 521.1 | 497.9 | 479.2 | 519.1 | 515.3 | 361.6 | 353.1 | 427
962 | 827 | 521 | 497.5 | 479.4 | 519.6 | 516 | 361.7 | 353.1 | 427.1
963 | 828 | 520.9 | 497.6 | 479.7 | 519.8 | 516.3 | 361.8 | 353.1 | 427.1
964 | 829 | 520.8 | 498.2 | 480.1 | 520 | 516.7 | 361.9 | 353.2 | 427.1
965 | 830 | 521 | 498.5 | 480.4 | 520.2 | 517.2 | 362 | 353.3 | 427.1
966 | 831 | 521 | 498.5 | 480.7 | 520.5 | 518.6 | 362.1 | 353.5 | 427.1
967 | 832 | 520.9 | 498.6 | 481 | 520.9 | 519.8 | 362.2 | 353.6 | 427.2
968 | 833 | 520.8 | 498.6 | 481.3 | 521.4 | 521.1 | 362.3 | 353.7 | 427.2
969 | 834 | 520.7 | 498.5 | 481.6 | 521.8 | 521.4 | 362.4 | 353.7 | 427.3
970 | 835 | 520.7 | 499.2 | 482 | 522.1 | 521.8 | 362.5 | 353.8 | 427.4
971 | 836 | 520.7 | 499.7 | 482.4 | 522.4 | 522.1 | 362.7 | 353.8 | 427.4
972 | 837 | 520.6 | 499.8 | 482.8 | 523 | 522.7 | 362.8 | 354 | 427.4
973 | 838 | 520.7 | 500 | 483.1 | 523.4 | 523.1 | 363 | 353.9 | 427.4
974 | 839 | 520.7 | 500 | 483.4 | 523.7 | 523 | 363.2 | 353.9 | 427.4
975 | 840 | 520.8 | 500.2 | 483.6 | 524 | 522.7 | 363.3 | 353.9 | 427.4
976 | 841 | 520.6 | 500.9 | 483.7 | 524.2 | 522.6 | 363.4 | 354 | 427.4
977 | 842 | 520.5 | 501.4 | 483.9 | 524.6 | 521.9 | 363.5 | 354 | 427.4
978 | 843 | 520.5 | 502.2 | 484.1 | 525.2 | 520.8 | 363.6 | 354.2 | 427.4
979 | 844 | 520.5 | 502.7 | 484.2 | 525.7 | 520.4 | 363.7 | 354.3 | 427.4
980 | 845 | 520.6 | 502.8 | 484.3 | 526.3 | 520 | 363.8 | 354.5 | 427.4
981 | 846 | 520.6 | 503.6 | 484.5 | 526.8 | 519.7 | 363.9 | 354.6 | 427.3
982 | 847 | 520.4 | 504.1 | 484.7 | 527.2 | 519.4 | 364 | 354.7 | 427.3
983 | 848 | 520.4 | 504.2 | 484.9 | 527.5 | 519 | 364.1 | 354.6 | 427.3
984 | 849 | 520.4 | 504.7 | 485.2 | 528 | 518.6 | 364.2 | 354.6 | 427.4
985 | 850 | 520.6 | 505.1 | 485.4 | 528.4 | 518.2 | 364.3 | 354.7 | 427.5
986 | 851 | 520.8 | 505.6 | 485.6 | 528.7 | 517.5 | 364.4 | 354.7 | 427.6
987 | 852 | 520.9 | 505.9 | 485.8 | 529.4 | 516.8 | 364.5 | 354.7 | 427.7
988 | 853 | 520.9 | 506.1 | 486.1 | 529.7 | 516.5 | 364.6 | 354.8 | 427.7
989 | 854 | 521.1 | 506.3 | 486.3 | 529.9 | 516.9 | 364.7 | 354.8 | 427.7
990 | 855 | 521.3 | 505.9 | 486.6 | 530 | 517.6 | 364.8 | 354.9 | 427.7
991 | 856 | 521.6 | 505.9 | 486.9 | 530.3 | 518.6 | 364.9 | 355 | 427.8
992 | 857 | 521.6 | 506 | 487.2 | 530.5 | 519.6 | 365 | 355 | 427.9
993 | 858 | 521.5 | 505.4 | 487.5 | 530.7 | 520.1 | 365.2 | 355 | 428
994 | 859 | 521.4 | 505.5 | 487.8 | 530.9 | 521.2 | 365.4 | 355.1 | 428.1
995 | 860 | 521.5 | 506.1 | 488.3 | 531.2 | 522.1 | 365.6 | 355.2 | 428.2
996 | 861 | 521.5 | 506.7 | 488.5 | 531.3 | 522.2 | 365.8 | 355.2 | 428.2
997 | 862 | 521.5 | 506.7 | 488.7 | 531.3 | 522.4 | 365.9 | 355.3 | 428.4
998 | 863 | 521.6 | 506.6 | 488.8 | 531.4 | 523.2 | 366.1 | 355.3 | 428.3
999 | 864 | 521.7 | 506 | 489 | 531.9 | 523.9 | 366.3 | 355.3 | 428.3
1000 | 865 | 521.6 | 505.8 | 489.2 | 532.3 | 523.8 | 366.4 | 355.4 | 428.5
1001 | 866 | 521.5 | 506.2 | 489.4 | 532.7 | 523.5 | 366.5 | 355.7 | 428.6
1002 | 867 | 521.4 | 506.8 | 489.7 | 533 | 523.2 | 366.7 | 355.9 | 428.6
1003 | 868 | 521.5 | 507.1 | 489.9 | 533.5 | 522.9 | 366.8 | 355.9 | 428.6
1004 | 869 | 521.7 | 507.5 | 490.2 | 533.8 | 522.8 | 367 | 356 | 428.7
1005 | 870 | 521.9 | 507.1 | 490.8 | 534.1 | 522.8 | 367 | 356.1 | 428.7
1006 | 871 | 522.1 | 507.2 | 491.4 | 534.4 | 522.5 | 367.1 | 356.2 | 428.8
1007 | 872 | 522.3 | 507.4 | 491.7 | 534.8 | 523.3 | 367.2 | 356.4 | 428.8
1008 | 873 | 522.3 | 507.4 | 492.3 | 535.2 | 523.5 | 367.3 | 356.5 | 428.8
1009 | 874 | 522.2 | 507.4 | 492.6 | 535.3 | 523.6 | 367.5 | 356.6 | 429
1010 | 875 | 522 | 507.1 | 492.8 | 535.5 | 523.2 | 367.6 | 356.6 | 429
1011 | 876 | 522 | 506.6 | 493 | 535.9 | 522.8 | 367.7 | 356.6 | 429.1
1012 | 877 | 521.8 | 506.4 | 493.2 | 536.1 | 522.8 | 367.8 | 356.6 | 429.2
1013 | 878 | 521.7 | 506.6 | 493.3 | 536.4 | 523 | 367.9 | 356.6 | 429.2
1014 | 879 | 521.7 | 506.4 | 493.4 | 536.6 | 522.8 | 368 | 356.6 | 429.2
1015 | 880 | 521.3 | 506.2 | 493.5 | 537.1 | 522.3 | 368.2 | 356.6 | 429.1
1016 | 881 | 520.9 | 506.3 | 493.6 | 537.5 | 522 | 368.3 | 356.5 | 429.1
1017 | 882 | 521 | 507.2 | 493.8 | 538.1 | 522 | 368.4 | 356.6 | 429.1
1018 | 883 | 521 | 507.4 | 494 | 538.8 | 522 | 368.5 | 356.6 | 429.1
1019 | 884 | 520.7 | 507.8 | 494.2 | 539.2 | 521.6 | 368.6 | 356.7 | 429.1
1020 | 885 | 520.8 | 508.3 | 494.5 | 539.7 | 522.1 | 368.7 | 356.8 | 429.2
1021 | 886 | 520.9 | 508.6 | 494.7 | 540.3 | 522.6 | 368.8 | 356.9 | 429.3
1022 | 887 | 520.9 | 508.7 | 495 | 540.5 | 523.1 | 368.9 | 357.1 | 429.3
1023 | 888 | 520.6 | 508.9 | 495.2 | 540.8 | 523.2 | 368.9 | 357.3 | 429.3
1024 | 889 | 520.5 | 509.2 | 495.4 | 541 | 522.9 | 369 | 357.4 | 429.3
1025 | 890 | 520.5 | 509.5 | 495.5 | 541.3 | 522.6 | 369.1 | 357.5 | 429.3
1026 | 891 | 520.7 | 510 | 495.7 | 541.7 | 522.8 | 369.1 | 357.6 | 429.4
1027 | 892 | 520.7 | 510.4 | 495.9 | 542.3 | 523.5 | 369.2 | 357.5 | 429.4
1028 | 893 | 520.6 | 510.5 | 496.1 | 542.8 | 523 | 369.2 | 357.6 | 429.4
1029 | 894 | 520.7 | 510.6 | 496.2 | 543.4 | 522.4 | 369.3 | 357.7 | 429.4
1030 | 895 | 520.8 | 510.9 | 496.4 | 544 | 521.6 | 369.3 | 357.7 | 429.5
1031 | 896 | 520.9 | 511.4 | 496.5 | 544.6 | 521.1 | 369.4 | 357.8 | 429.5
1032 | 897 | 520.7 | 511.8 | 496.7 | 544.9 | 520.9 | 369.5 | 357.8 | 429.5
1033 | 898 | 520.5 | 512.4 | 496.9 | 545 | 520.9 | 369.5 | 357.8 | 429.5
1034 | 899 | 520.5 | 512.3 | 497.1 | 545.2 | 521 | 369.5 | 357.8 | 429.5
1035 | 900 | 520.7 | 512 | 497.4 | 545.2 | 522.2 | 369.5 | 357.9 | 429.5
1036 | 901 | 520.8 | 511.9 | 497.7 | 545 | 523.9 | 369.6 | 357.9 | 429.6
1037 | 902 | 520.9 | 511.6 | 498 | 545 | 524.3 | 369.6 | 358 | 429.6
1038 | 903 | 520.9 | 511.4 | 498.2 | 545 | 524.9 | 369.7 | 358 | 429.7
1039 | 904 | 521 | 511.1 | 498.5 | 545.6 | 525.3 | 369.7 | 358 | 429.7
1040 | 905 | 521.3 | 511.3 | 498.7 | 546.3 | 525 | 369.7 | 358.1 | 429.8
1041 | 906 | 521.5 | 511.5 | 498.9 | 546.4 | 524.7 | 369.8 | 358.3 | 429.8
1042 | 907 | 521.6 | 511.5 | 499.2 | 546.5 | 525.1 | 369.8 | 358.3 | 429.9
1043 | 908 | 521.7 | 511.7 | 499.4 | 546.4 | 525.6 | 369.8 | 358.2 | 429.9
1044 | 909 | 521.7 | 511.6 | 499.6 | 546.1 | 526.3 | 369.8 | 358.2 | 429.8
1045 | 910 | 521.7 | 511.9 | 499.8 | 546 | 526.8 | 369.8 | 358.2 | 429.9
1046 | 911 | 521.7 | 511.9 | 500 | 545.9 | 527.4 | 369.9 | 358.2 | 430
1047 | 912 | 521.7 | 512.1 | 500.4 | 546 | 528.1 | 369.9 | 358.1 | 430
1048 | 913 | 521.5 | 512.7 | 500.7 | 545.9 | 528.5 | 370 | 357.9 | 430
1049 | 914 | 521.4 | 513.1 | 500.9 | 546.1 | 528.9 | 370 | 357.8 | 430
1050 | 915 | 521.4 | 513.5 | 501.3 | 546.5 | 529.4 | 370.1 | 357.8 | 430.1
1051 | 916 | 521.4 | 513.5 | 501.6 | 546.7 | 529.6 | 370.1 | 357.7 | 430.1
1052 | 917 | 521.4 | 513.3 | 502.1 | 546.9 | 530.5 | 370.1 | 357.8 | 430.2
1053 | 918 | 521.3 | 513.4 | 502.2 | 547 | 531.2 | 370.1 | 357.9 | 430.2
1054 | 919 | 521 | 513.5 | 502.3 | 546.9 | 531.9 | 370.2 | 357.9 | 430.3
1055 | 920 | 520.8 | 513.5 | 502.4 | 546.7 | 533 | 370.2 | 358 | 430.3
1056 | 921 | 520.7 | 513.6 | 502.6 | 546.8 | 533.6 | 370.2 | 358 | 430.4
1057 | 922 | 520.7 | 513.8 | 502.8 | 547.1 | 533.7 | 370.3 | 358.1 | 430.5
1058 | 923 | 520.9 | 514.4 | 503 | 547.4 | 533.5 | 370.3 | 358.3 | 430.6
1059 | 924 | 520.7 | 514.1 | 503.2 | 547.4 | 533.8 | 370.3 | 358.5 | 430.6
1060 | 925 | 520.7 | 514.2 | 503.3 | 547.8 | 533.7 | 370.4 | 358.7 | 430.6
1061 | 926 | 520.9 | 514.1 | 503.5 | 548 | 533.1 | 370.4 | 358.8 | 430.6
1062 | 927 | 521.1 | 513.9 | 503.6 | 548.3 | 533.4 | 370.4 | 359 | 430.7
1063 | 928 | 521.5 | 514.3 | 503.7 | 549 | 532.8 | 370.4 | 359.1 | 430.6
1064 | 929 | 521.8 | 515 | 503.7 | 549.8 | 531.6 | 370.5 | 359.2 | 430.6
1065 | 930 | 521.9 | 515.4 | 503.7 | 550.6 | 530.3 | 370.5 | 359.3 | 430.7
1066 | 931 | 521.9 | 515.8 | 503.8 | 551.2 | 528.9 | 370.5 | 359.5 | 430.7
1067 | 932 | 521.9 | 516.3 | 504 | 551.6 | 528.1 | 370.5 | 359.5 | 430.8
1068 | 933 | 521.8 | 516.3 | 504.2 | 552.4 | 527.6 | 370.6 | 359.5 | 430.8
1069 | 934 | 521.7 | 516.7 | 504.3 | 553.5 | 526.8 | 370.6 | 359.5 | 430.9
1070 | 935 | 521.8 | 516.8 | 504.5 | 554.1 | 525.9 | 370.6 | 359.6 | 430.9
1071 | 936 | 521.8 | 517 | 504.7 | 554.5 | 525.1 | 370.5 | 359.7 | 430.8
1072 | 937 | 521.7 | 517 | 504.9 | 554.9 | 524.6 | 370.5 | 359.8 | 430.8
1073 | 938 | 521.8 | 517.1 | 505.1 | 554.8 | 524.2 | 370.5 | 359.9 | 430.9
1074 | 939 | 521.7 | 517.9 | 505.3 | 554.6 | 524.3 | 370.5 | 359.9 | 430.9
1075 | 940 | 521.5 | 518.2 | 505.5 | 554.5 | 524.5 | 370.5 | 359.9 | 430.9
1076 | 941 | 521.4 | 518.4 | 505.9 | 554.4 | 525.4 | 370.5 | 359.8 | 430.9
1077 | 942 | 521.4 | 518.2 | 506.2 | 554.5 | 526.3 | 370.5 | 359.8 | 430.9
1078 | 943 | 521.3 | 518.2 | 506.4 | 554.8 | 527.5 | 370.5 | 359.7 | 430.9
1079 | 944 | 521.2 | 518.1 | 506.7 | 554.7 | 528.3 | 370.5 | 359.6 | 431
1080 | 945 | 521.2 | 517.8 | 507 | 554.9 | 529.3 | 370.5 | 359.7 | 431.1
1081 | 946 | 521.3 | 517.7 | 507.2 | 555.3 | 529.3 | 370.5 | 359.9 | 431.1
1082 | 947 | 521.5 | 517.8 | 507.3 | 555.5 | 529.6 | 370.6 | 360 | 431.1
1083 | 948 | 521.6 | 518.3 | 507.5 | 555.3 | 530.5 | 370.6 | 360.1 | 431.1
1084 | 949 | 521.6 | 518.8 | 507.7 | 555.1 | 531.6 | 370.7 | 360 | 431.2
1085 | 950 | 521.7 | 518.8 | 508 | 555.1 | 532.5 | 370.7 | 360.1 | 431.2
1086 | 951 | 521.9 | 519 | 508.3 | 555.3 | 534.3 | 370.8 | 360.2 | 431.2
1087 | 952 | 522 | 519.4 | 508.6 | 555.6 | 534.7 | 370.8 | 360 | 431.3
1088 | 953 | 522.1 | 519.6 | 509 | 555.8 | 535.1 | 370.9 | 360 | 431.4
1089 | 954 | 522.2 | 519.7 | 509.3 | 556 | 535.5 | 371 | 359.9 | 431.4
1090 | 955 | 522.3 | 520.1 | 509.5 | 556.2 | 536.2 | 371.1 | 360 | 431.5
1091 | 956 | 522 | 520.6 | 509.8 | 556.2 | 537.1 | 371.2 | 360 | 431.6
1092 | 957 | 522.1 | 520.8 | 510 | 556.2 | 536.9 | 371.3 | 359.9 | 431.6
1093 | 958 | 522.2 | 520.9 | 510.3 | 556.1 | 536.8 | 371.4 | 359.9 | 431.6
1094 | 959 | 522.2 | 520.7 | 510.6 | 556.3 | 536.8 | 371.5 | 359.8 | 431.6
1095 | 960 | 522.3 | 520.8 | 510.9 | 556.9 | 536.9 | 371.7 | 359.8 | 431.7
1096 | 961 | 522.3 | 521.4 | 511 | 558.3 | 536 | 371.8 | 359.9 | 431.7
1097 | 962 | 522.1 | 521.8 | 511.1 | 558.7 | 535.2 | 371.9 | 360 | 431.7
1098 | 963 | 522 | 522.4 | 511.2 | 558.7 | 535 | 372 | 360 | 431.7
1099 | 964 | 521.8 | 522.3 | 511.3 | 558.5 | 535.2 | 372.1 | 360 | 431.8
1100 | 965 | 521.7 | 522.6 | 511.5 | 558.2 | 536.3 | 372.2 | 360 | 431.8
1101 | 966 | 521.7 | 522.9 | 511.7 | 558.1 | 536.8 | 372.3 | 359.9 | 431.7
1102 | 967 | 521.5 | 523 | 511.8 | 558.4 | 536.7 | 372.4 | 360 | 431.7
1103 | 968 | 521.6 | 523.5 | 511.9 | 559 | 536.3 | 372.4 | 360.1 | 431.8
1104 | 969 | 521.3 | 523.9 | 512.1 | 559.6 | 535.5 | 372.5 | 360.1 | 431.8
1105 | 970 | 521.3 | 524.4 | 512.3 | 560.4 | 534.5 | 372.6 | 360.2 | 431.8
1106 | 971 | 521.4 | 525.2 | 512.5 | 561.2 | 533.4 | 372.6 | 360.3 | 431.8
1107 | 972 | 521.6 | 525.6 | 512.7 | 561.7 | 532.3 | 372.6 | 360.4 | 431.8
1108 | 973 | 521.6 | 526.1 | 512.8 | 562.1 | 531.2 | 372.6 | 360.4 | 431.7
1109 | 974 | 521.8 | 525.7 | 513 | 562.4 | 530.5 | 372.6 | 360.3 | 431.7
1110 | 975 | 521.8 | 525.5 | 513.1 | 562.7 | 529.9 | 372.6 | 360.3 | 431.6
1111 | 976 | 521.8 | 525.4 | 513.3 | 562.3 | 529.7 | 372.6 | 360.2 | 431.6
1112 | 977 | 521.7 | 525.3 | 513.5 | 562 | 530.7 | 372.6 | 360.1 | 431.6
1113 | 978 | 521.4 | 525.4 | 513.8 | 561.8 | 531.5 | 372.6 | 360.2 | 431.6
1114 | 979 | 521.2 | 525 | 514 | 561.5 | 531.8 | 372.6 | 360.3 | 431.6
1115 | 980 | 521.1 | 524.4 | 514.3 | 561.2 | 532.2 | 372.6 | 360.4 | 431.7
1116 | 981 | 521.1 | 523.7 | 514.5 | 560.9 | 533.2 | 372.6 | 360.6 | 431.7
1117 | 982 | 520.9 | 523.7 | 514.8 | 560.6 | 534.3 | 372.6 | 360.7 | 431.7
1118 | 983 | 520.9 | 524.1 | 515.1 | 560.2 | 535.1 | 372.6 | 360.8 | 431.8
1119 | 984 | 520.9 | 524.2 | 515.4 | 560.4 | 536 | 372.6 | 360.8 | 431.9
1120 | 985 | 520.8 | 524.4 | 515.7 | 561.4 | 535.5 | 372.6 | 361 | 431.9
1121 | 986 | 521 | 524.8 | 515.8 | 562.7 | 534.9 | 372.6 | 360.9 | 431.9
1122 | 987 | 521 | 525.9 | 515.9 | 564 | 534.1 | 372.6 | 361 | 432
1123 | 988 | 521 | 526.5 | 516.3 | 564.8 | 533.3 | 372.6 | 360.9 | 432
1124 | 989 | 521 | 526.6 | 516.3 | 565.6 | 532.4 | 372.6 | 360.8 | 432
1125 | 990 | 521.1 | 527 | 516.4 | 566.1 | 531.7 | 372.6 | 360.7 | 432.1
1126 | 991 | 521.2 | 527.4 | 516.5 | 566.2 | 531.9 | 372.7 | 360.7 | 432.1
1127 | 992 | 521.4 | 527.5 | 516.7 | 566 | 532.9 | 372.7 | 360.6 | 432
1128 | 993 | 521.2 | 527.7 | 516.9 | 565.8 | 533.8 | 372.7 | 360.4 | 432
1129 | 994 | 521 | 527.8 | 517.1 | 565.7 | 534.5 | 372.8 | 360.4 | 432
1130 | 995 | 521.1 | 527.8 | 517.7 | 565.5 | 535 | 372.9 | 360.4 | 432
1131 | 996 | 521.1 | 528.2 | 518.1 | 565.3 | 535 | 372.9 | 360.4 | 431.9
1132 | 997 | 521.1 | 528.4 | 518.2 | 565.2 | 534.7 | 373 | 360.5 | 431.9
1133 | 998 | 521.2 | 528.1 | 518.2 | 565 | 535.7 | 373 | 360.5 | 431.9
1134 | 999 | 521.5 | 527.7 | 518.3 | 564.5 | 537.3 | 373 | 360.6 | 431.9
1135 | 1000 | 521.8 | 527.9 | 518.6 | 564.3 | 538.3 | 373.1 | 360.7 | 432
1136 | 1001 | 521.7 | 527.9 | 518.8 | 564.5 | 539 | 373.1 | 360.7 | 432.1
1137 | 1002 | 521.8 | 527.7 | 519.1 | 564.5 | 539.3 | 373.2 | 360.8 | 432.2
1138 | 1003 | 521.9 | 527.2 | 519.3 | 564.9 | 539.3 | 373.2 | 360.9 | 432.3
1139 | 1004 | 522.1 | 527.1 | 519.5 | 565.4 | 539.5 | 373.2 | 361 | 432.3
1140 | 1005 | 522.1 | 527 | 519.6 | 566.2 | 539.6 | 373.2 | 361.1 | 432.3
1141 | 1006 | 522.2 | 526.8 | 519.8 | 566.9 | 540.5 | 373.2 | 361.2 | 432.3
1142 | 1007 | 522.1 | 526.6 | 520 | 567.3 | 541.5 | 373.2 | 361.4 | 432.2
1143 | 1008 | 522.3 | 526.3 | 520.4 | 567.3 | 541.8 | 373.3 | 361.4 | 432.2
1144 | 1009 | 522.6 | 526.5 | 520.5 | 567.5 | 542.1 | 373.3 | 361.4 | 432.2
1145 | 1010 | 522.7 | 526.2 | 520.6 | 567.5 | 542.8 | 373.3 | 361.4 | 432.3
1146 | 1011 | 522.7 | 525.6 | 520.7 | 567.6 | 543.2 | 373.3 | 361.3 | 432.3
1147 | 1012 | 522.6 | 525.2 | 520.9 | 567.6 | 543.3 | 373.4 | 361.2 | 432.4
1148 | 1013 | 522.4 | 524.8 | 521.1 | 567.7 | 543.9 | 373.4 | 361.2 | 432.4
1149 | 1014 | 522.4 | 524.9 | 521.4 | 567.8 | 544.4 | 373.4 | 361.2 | 432.5
1150 | 1015 | 522.3 | 525.3 | 521.6 | 567.8 | 544.7 | 373.5 | 361.2 | 432.6
1151 | 1016 | 522 | 525.4 | 521.7 | 567.8 | 545 | 373.5 | 361.2 | 432.7
1152 | 1017 | 521.7 | 526.2 | 521.7 | 567.9 | 545.3 | 373.5 | 361.3 | 432.8
1153 | 1018 | 521.5 | 526.7 | 521.9 | 568.2 | 545 | 373.6 | 361.2 | 432.8
1154 | 1019 | 521.1 | 526.9 | 522.1 | 568.5 | 544.7 | 373.6 | 361.2 | 432.7
1155 | 1020 | 520.9 | 527.6 | 522.5 | 568.8 | 544.3 | 373.6 | 361.1 | 432.7
1156 | 1021 | 520.9 | 528.2 | 522.6 | 569.2 | 544.4 | 373.6 | 361.1 | 432.7
1157 | 1022 | 520.8 | 528.4 | 522.7 | 569.4 | 544.7 | 373.6 | 361.1 | 432.8
1158 | 1023 | 520.6 | 528.2 | 522.8 | 569.2 | 545.2 | 373.7 | 361.1 | 432.9
1159 | 1024 | 520.5 | 528.4 | 522.9 | 569.6 | 546 | 373.7 | 361.2 | 432.9
1160 | 1025 | 520.4 | 528.7 | 523 | 570.3 | 545.4 | 373.6 | 361.3 | 433
1161 | 1026 | 520.3 | 529 | 523.2 | 570.6 | 544.9 | 373.6 | 361.3 | 433
1162 | 1027 | 520.3 | 528.8 | 523.3 | 570.7 | 544.5 | 373.6 | 361.2 | 433
1163 | 1028 | 520.3 | 529.2 | 523.3 | 570.8 | 544.2 | 373.6 | 361.3 | 433
1164 | 1029 | 520.3 | 531 | 523.4 | 571 | 543.9 | 373.6 | 361.4 | 433
1165 | 1030 | 520.3 | 531.8 | 523.7 | 571.6 | 543.6 | 373.6 | 361.4 | 432.9
1166 | 1031 | 520.5 | 532 | 524.1 | 571.8 | 543 | 373.5 | 361.4 | 432.9
1167 | 1032 | 520.6 | 532.3 | 524.2 | 572 | 542.7 | 373.5 | 361.5 | 432.9
1168 | 1033 | 520.7 | 532.5 | 524.3 | 572.7 | 543.2 | 373.5 | 361.5 | 432.9
1169 | 1034 | 520.8 | 532.6 | 524.6 | 573.2 | 543 | 373.5 | 361.5 | 433
1170 | 1035 | 520.9 | 532.9 | 524.9 | 574.1 | 542.3 | 373.5 | 361.6 | 433.1
1171 | 1036 | 521.1 | 533.8 | 525.1 | 574.5 | 541.5 | 373.5 | 361.7 | 433.1
1172 | 1037 | 521.3 | 534.6 | 525.5 | 574.8 | 540.9 | 373.5 | 361.7 | 433.1
1173 | 1038 | 521.5 | 535 | 525.7 | 575.4 | 540.1 | 373.5 | 361.8 | 433.2
1174 | 1039 | 521.7 | 534.8 | 526 | 575.6 | 540.6 | 373.5 | 361.8 | 433.2
1175 | 1040 | 521.8 | 534.6 | 526.2 | 575.9 | 542.1 | 373.5 | 361.8 | 433.1
1176 | 1041 | 521.7 | 534.4 | 526.3 | 575.9 | 543.5 | 373.5 | 361.7 | 433.1
1177 | 1042 | 521.6 | 534.7 | 526.4 | 575.6 | 545.3 | 373.5 | 361.8 | 433.2
1178 | 1043 | 521.6 | 534.4 | 526.5 | 575.4 | 545.4 | 373.5 | 361.9 | 433.2
1179 | 1044 | 521.7 | 534.1 | 526.6 | 575.5 | 545.8 | 373.5 | 362 | 433.2
1180 | 1045 | 521.7 | 534.3 | 526.7 | 575.5 | 545.5 | 373.5 | 361.9 | 433.3
1181 | 1046 | 521.9 | 534.7 | 526.8 | 575.6 | 545.7 | 373.5 | 361.9 | 433.4
1182 | 1047 | 522 | 534.6 | 527 | 575.6 | 546.9 | 373.5 | 362 | 433.5
1183 | 1048 | 521.9 | 534.4 | 527.3 | 576.1 | 546.9 | 373.5 | 362 | 433.5
1184 | 1049 | 521.9 | 534.9 | 527.3 | 576.6 | 546.9 | 373.5 | 361.9 | 433.6
1185 | 1050 | 521.9 | 535.6 | 527.5 | 576.8 | 547.3 | 373.5 | 361.9 | 433.5
1186 | 1051 | 522 | 535.7 | 527.8 | 576.7 | 548 | 373.5 | 362 | 433.6
1187 | 1052 | 522.1 | 535.5 | 528 | 577.4 | 548.8 | 373.6 | 361.9 | 433.5
1188 | 1053 | 522.2 | 535.4 | 528.4 | 578 | 548.4 | 373.6 | 361.9 | 433.5
1189 | 1054 | 522.1 | 535.5 | 529 | 579 | 547.8 | 373.6 | 362 | 433.5
1190 | 1055 | 522.3 | 536.2 | 529.2 | 579.6 | 546.8 | 373.6 | 362 | 433.5
1191 | 1056 | 522.3 | 536.9 | 529.1 | 580.4 | 545.9 | 373.6 | 362.1 | 433.5
1192 | 1057 | 522.4 | 537.5 | 529.2 | 580.7 | 546 | 373.6 | 361.9 | 433.5
1193 | 1058 | 522.4 | 537.6 | 529.4 | 581.2 | 548.1 | 373.6 | 362 | 433.5
1194 | 1059 | 522.4 | 537.5 | 529.5 | 582 | 548.4 | 373.6 | 361.9 | 433.6
1195 | 1060 | 522.5 | 537.5 | 529.7 | 582.1 | 549.4 | 373.6 | 361.8 | 433.6
1196 | 1061 | 522.6 | 537.1 | 529.8 | 582 | 551.8 | 373.6 | 361.6 | 433.6
1197 | 1062 | 522.6 | 536.3 | 530 | 582.1 | 553.5 | 373.7 | 361.5 | 433.6
1198 | 1063 | 522.7 | 535.9 | 530.3 | 582.4 | 555.2 | 373.7 | 361.6 | 433.7
1199 | 1064 | 522.7 | 535.5 | 530.5 | 582.3 | 556.1 | 373.7 | 361.7 | 433.8
1200 | 1065 | 522.8 | 535.2 | 530.7 | 582.4 | 556.7 | 373.8 | 361.8 | 433.8
1201 | 1066 | 522.7 | 534.6 | 530.9 | 582.8 | 556.5 | 373.8 | 361.9 | 433.9
1202 | 1067 | 522.5 | 534.3 | 531.1 | 583.2 | 556.5 | 373.8 | 361.8 | 434
1203 | 1068 | 522.2 | 534.3 | 531.1 | 583.8 | 556.2 | 373.8 | 361.8 | 434.1
1204 | 1069 | 522 | 534.8 | 531.1 | 584.6 | 555 | 373.8 | 361.7 | 434.2
1205 | 1070 | 521.9 | 535.1 | 531.4 | 585.2 | 553.9 | 373.8 | 361.8 | 434.3
1206 | 1071 | 522.1 | 535.6 | 531.5 | 585.8 | 553 | 373.8 | 361.9 | 434.3
1207 | 1072 | 522.1 | 536.5 | 531.6 | 586.4 | 552.1 | 373.8 | 362.1 | 434.3
1208 | 1073 | 522.1 | 536.8 | 531.7 | 587 | 551 | 373.8 | 362.1 | 434.3
1209 | 1074 | 522 | 536.8 | 531.9 | 587.7 | 550.4 | 373.8 | 362 | 434.4
1210 | 1075 | 522 | 537.3 | 532 | 587.6 | 550.7 | 373.7 | 361.9 | 434.4
1211 | 1076 | 521.9 | 537.6 | 532.3 | 587.2 | 551.9 | 373.7 | 361.9 | 434.3
1212 | 1077 | 521.7 | 537.4 | 532.6 | 586.7 | 552.8 | 373.6 | 362 | 434.3
1213 | 1078 | 521.6 | 537.3 | 532.9 | 586.6 | 553.3 | 373.6 | 361.9 | 434.4
1214 | 1079 | 521.6 | 537.2 | 533 | 586.4 | 553 | 373.6 | 361.9 | 434.4
1215 | 1080 | 521.7 | 538 | 533.1 | 587 | 552.3 | 373.6 | 361.8 | 434.4
1216 | 1081 | 521.9 | 539.2 | 533.1 | 587.7 | 551.3 | 373.6 | 361.9 | 434.4
1217 | 1082 | 521.9 | 540.3 | 533.2 | 588.3 | 550.5 | 373.6 | 361.9 | 434.4
1218 | 1083 | 521.9 | 540.8 | 533.7 | 589.1 | 549.6 | 373.5 | 361.9 | 434.4
1219 | 1084 | 521.9 | 541.2 | 534.3 | 589.7 | 548.7 | 373.5 | 362 | 434.3
1220 | 1085 | 521.9 | 541.9 | 534.5 | 590.3 | 548 | 373.5 | 362.2 | 434.3
1221 | 1086 | 521.7 | 542 | 534.7 | 590.8 | 547.2 | 373.4 | 362.3 | 434.3
1222 | 1087 | 521.5 | 542.2 | 534.8 | 591 | 546.9 | 373.5 | 362.3 | 434.3
1223 | 1088 | 521.5 | 541.6 | 535 | 590.8 | 547.1 | 373.5 | 362.3 | 434.3
1224 | 1089 | 521.4 | 540.6 | 535.3 | 590 | 547.5 | 373.5 | 362.4 | 434.3
1225 | 1090 | 521.3 | 540.1 | 535.6 | 589.5 | 548.7 | 373.5 | 362.4 | 434.3
1226 | 1091 | 521.3 | 539.8 | 536 | 589.4 | 549 | 373.6 | 362.4 | 434.4
1227 | 1092 | 521.4 | 539.2 | 536.2 | 589.9 | 550.7 | 373.6 | 362.4 | 434.4
1228 | 1093 | 521.5 | 538.9 | 536.4 | 590.2 | 551.3 | 373.6 | 362.4 | 434.4
1229 | 1094 | 521.5 | 538.7 | 536.6 | 590.7 | 551.3 | 373.6 | 362.4 | 434.4
1230 | 1095 | 521.4 | 538.2 | 536.9 | 591.6 | 551.1 | 373.6 | 362.5 | 434.5
1231 | 1096 | 521.3 | 538.5 | 537.1 | 592.2 | 551.8 | 373.6 | 362.6 | 434.4
1232 | 1097 | 521.1 | 538.7 | 537.3 | 592.9 | 553.6 | 373.6 | 362.6 | 434.3
1233 | 1098 | 521 | 538.8 | 537.5 | 592.8 | 553.7 | 373.6 | 362.5 | 434.3
1234 | 1099 | 521 | 538.7 | 537.6 | 592.7 | 553.9 | 373.6 | 362.4 | 434.3
1235 | 1100 | 521 | 538.1 | 537.6 | 592.4 | 556.1 | 373.6 | 362.3 | 434.4
1236 | 1101 | 521.2 | 538 | 537.9 | 592.6 | 556.8 | 373.6 | 362.1 | 434.4
1237 | 1102 | 521.5 | 537.8 | 538.4 | 592.8 | 557.3 | 373.6 | 362 | 434.5
1238 | 1103 | 521.5 | 537.6 | 538.6 | 592.5 | 557.9 | 373.6 | 361.9 | 434.5
1239 | 1104 | 521.4 | 537.4 | 538.8 | 592.3 | 559.2 | 373.6 | 361.9 | 434.6
1240 | 1105 | 521.3 | 537.5 | 538.9 | 592.7 | 560.6 | 373.6 | 361.9 | 434.7
1241 | 1106 | 521.2 | 537.5 | 539.1 | 592.9 | 560.9 | 373.6 | 361.9 | 434.7
1242 | 1107 | 521.2 | 537.4 | 539.4 | 592.9 | 562.1 | 373.7 | 361.9 | 434.8
1243 | 1108 | 521.3 | 537.5 | 539.7 | 592.8 | 563 | 373.7 | 361.9 | 434.8
1244 | 1109 | 521.5 | 537.7 | 539.9 | 592.7 | 563.5 | 373.7 | 362 | 434.9
1245 | 1110 | 521.5 | 538.1 | 540 | 593.1 | 563.5 | 373.6 | 362 | 434.9
1246 | 1111 | 521.7 | 538.6 | 540.1 | 594 | 562.7 | 373.6 | 362 | 435
1247 | 1112 | 521.9 | 539.2 | 540.4 | 594.1 | 561.9 | 373.6 | 362.1 | 435
1248 | 1113 | 522.1 | 539.7 | 540.5 | 594.4 | 561.4 | 373.6 | 362.1 | 435.1
1249 | 1114 | 521.9 | 540.5 | 540.6 | 594.7 | 562.4 | 373.6 | 362.2 | 435.1
1250 | 1115 | 521.9 | 540.8 | 540.9 | 594.6 | 562.9 | 373.6 | 362.2 | 435.1
1251 | 1116 | 522 | 540.4 | 541 | 595 | 563.3 | 373.6 | 362 | 435.1
1252 | 1117 | 521.9 | 540.2 | 541.3 | 595.8 | 563.5 | 373.6 | 361.9 | 435.1
1253 | 1118 | 521.9 | 540.7 | 541.5 | 596 | 563.4 | 373.6 | 361.9 | 435.2
1254 | 1119 | 521.8 | 541.5 | 541.7 | 596.8 | 562.8 | 373.6 | 361.9 | 435.2
1255 | 1120 | 521.9 | 542.1 | 542 | 597.9 | 562 | 373.6 | 362.1 | 435.3
1256 | 1121 | 522.1 | 543.1 | 542.5 | 599 | 561.6 | 373.6 | 362.6 | 435.6
1257 | 1122 | 522.2 | 543.3 | 543 | 599.3 | 561.5 | 373.6 | 363.1 | 436.1
1258 | 1123 | 522.2 | 543.5 | 543.4 | 599.7 | 561.8 | 373.6 | 363.5 | 436.9
1259 | 1124 | 522.2 | 544 | 544 | 600.2 | 562.4 | 373.6 | 364.1 | 437.8
1260 | 1125 | 522.4 | 543.8 | 544.7 | 600.6 | 563.6 | 373.6 | 364.8 | 438.8
1261 | 1126 | 522.6 | 543.8 | 545.3 | 600.9 | 565.6 | 373.5 | 365.5 | 439.6
1262 | 1127 | 522.6 | 543.9 | 546 | 600.9 | 567.7 | 373.5 | 366.1 | 440.5
1263 | 1128 | 522.8 | 543.9 | 546.8 | 600.3 | 570.1 | 373.5 | 366.8 | 441.3
1264 | 1129 | 522.8 | 543.9 | 547.5 | 600.6 | 572 | 373.5 | 367.6 | 442.1
1265 | 1130 | 522.8 | 543.9 | 548.1 | 601.7 | 574.3 | 373.5 | 368.3 | 443
1266 | 1131 | 522.8 | 543.8 | 549 | 603 | 575.6 | 373.6 | 369.1 | 443.9
1267 | 1132 | 522.7 | 543.7 | 550 | 603.8 | 576.1 | 373.6 | 369.9 | 444.9
1268 | 1133 | 522.6 | 543.9 | 550.7 | 604.5 | 576.6 | 373.6 | 370.8 | 446
1269 | 1134 | 522.6 | 544.2 | 551.2 | 605 | 577.1 | 373.6 | 371.6 | 447.1
1270 | 1135 | 522.6 | 544.5 | 551.8 | 605.4 | 577.5 | 373.7 | 372.5 | 448.2
1271 | 1136 | 522.6 | 545.1 | 552.5 | 606.1 | 577.8 | 373.7 | 373.3 | 449.3
1272 | 1137 | 522.5 | 546.1 | 553.1 | 606.8 | 577.9 | 373.8 | 374.1 | 450.6
1273 | 1138 | 522.5 | 546.6 | 553.7 | 607.4 | 578.2 | 373.8 | 374.8 | 451.8
1274 | 1139 | 522.4 | 547.4 | 554.4 | 608.4 | 578.5 | 373.9 | 375.5 | 452.9
1275 | 1140 | 522.2 | 548.2 | 554.9 | 609.4 | 578.9 | 373.9 | 376.3 | 453.9
1276 | 1141 | 522 | 548.6 | 555.6 | 610.3 | 579.1 | 373.9 | 377.1 | 455.1
1277 | 1142 | 522.1 | 548.6 | 556.1 | 611.4 | 579.4 | 374 | 378 | 456.3
1278 | 1143 | 522.1 | 548.5 | 556.7 | 611.8 | 580.6 | 374 | 378.8 | 457.5
1279 | 1144 | 522.2 | 548.1 | 557.3 | 612.7 | 581.9 | 374.1 | 379.5 | 458.7
1280 | 1145 | 522.1 | 548 | 558.3 | 613.3 | 583 | 374.2 | 380.4 | 460
1281 | 1146 | 521.8 | 548 | 559.3 | 613.7 | 584.1 | 374.3 | 381.4 | 461.2
1282 | 1147 | 521.7 | 547.8 | 560.2 | 614.4 | 584.7 | 374.3 | 382.2 | 462.4
1283 | 1148 | 521.7 | 547.7 | 561 | 614.4 | 585.3 | 374.4 | 382.9 | 463.7
1284 | 1149 | 521.7 | 548.2 | 561.7 | 614.8 | 585.9 | 374.5 | 383.7 | 464.9
1285 | 1150 | 521.7 | 548.7 | 562.4 | 615.9 | 586.4 | 374.6 | 384.6 | 466.1
1286 | 1151 | 521.8 | 549.1 | 563.3 | 616.9 | 586.3 | 374.6 | 385.4 | 467.4
1287 | 1152 | 521.8 | 548.6 | 564.4 | 617.3 | 586.2 | 374.6 | 386.2 | 468.6
1288 | 1153 | 521.6 | 548.2 | 565.3 | 617.5 | 586.6 | 374.6 | 387 | 469.8
1289 | 1154 | 521.3 | 548.5 | 566 | 617.7 | 587.2 | 374.7 | 387.7 | 471
1290 | 1155 | 521 | 548.8 | 566.5 | 618.7 | 587.7 | 374.8 | 388.5 | 472.1
1291 | 1156 | 520.4 | 549.1 | 567 | 619.1 | 588.1 | 374.9 | 389.2 | 473.3
1292 | 1157 | 519.6 | 549 | 567.6 | 619.4 | 588.5 | 375 | 389.9 | 474.4
1293 | 1158 | 518.8 | 548.9 | 568.3 | 619.8 | 588.9 | 375 | 390.5 | 475.5
1294 | 1159 | 518.1 | 549.2 | 568.9 | 620 | 589.9 | 375.1 | 390.8 | 476.5
1295 | 1160 | 517.2 | 549.1 | 569.7 | 620.5 | 590.8 | 375.2 | 391.2 | 477.7
1296 | 1161 | 516 | 549.1 | 570.4 | 620.6 | 591.4 | 375.4 | 391.5 | 478.9
1297 | 1162 | 514.8 | 549.2 | 571 | 621 | 591.7 | 375.5 | 391.7 | 479.9
1298 | 1163 | 513.8 | 550 | 571.7 | 622.2 | 592.2 | 375.6 | 391.9 | 480.9
1299 | 1164 | 512.7 | 551 | 572.6 | 623.6 | 592.6 | 375.8 | 392.2 | 481.8
1300 | 1165 | 511.8 | 551.2 | 573.4 | 624.8 | 592.8 | 376 | 392.6 | 482.7
1301 | 1166 | 510.8 | 550.9 | 573.9 | 626 | 593 | 376.1 | 393.1 | 483.6
1302 | 1167 | 509.5 | 550.3 | 574.1 | 625.9 | 593.2 | 376.2 | 393.4 | 484.5
1303 | 1168 | 508.2 | 549.7 | 574.3 | 625.9 | 593.4 | 376.4 | 393.7 | 485.3
1304 | 1169 | 506.9 | 549.5 | 574.7 | 626.3 | 593.5 | 376.6 | 394.1 | 485.9
1305 | 1170 | 505.8 | 549.9 | 575.2 | 626.9 | 593.9 | 376.7 | 394.4 | 486.7
1306 | 1171 | 504.7 | 550.6 | 575.6 | 627.5 | 594.4 | 376.8 | 394.6 | 487.5
1307 | 1172 | 503.4 | 551.9 | 575.9 | 628.2 | 594.7 | 376.9 | 394.8 | 488.1
1308 | 1173 | 502.3 | 552.7 | 576.5 | 628.8 | 594.9 | 377 | 395 | 488.8
1309 | 1174 | 501.5 | 553.5 | 576.7 | 629.3 | 595.3 | 377.1 | 395.3 | 489.2
1310 | 1175 | 500.4 | 554.7 | 577 | 628.7 | 596.1 | 377.2 | 395.5 | 489.8
1311 | 1176 | 499.4 | 555.2 | 577.3 | 628.7 | 596.7 | 377.2 | 395.7 | 490.2
1312 | 1177 | 498.4 | 555.3 | 577.5 | 629.1 | 597 | 377.3 | 396 | 490.7
1313 | 1178 | 497.4 | 555.7 | 577.6 | 629.2 | 597.2 | 377.3 | 396.3 | 491.1
1314 | 1179 | 496.5 | 555.9 | 577.9 | 629.3 | 597.5 | 377.4 | 396.5 | 491.5
1315 | 1180 | 495.4 | 555.5 | 578.3 | 629.4 | 597.9 | 377.4 | 396.5 | 491.9
1316 | 1181 | 494.2 | 555.2 | 578.8 | 630.6 | 599.2 | 377.4 | 396.6 | 492.2
1317 | 1182 | 493.2 | 554.9 | 579.2 | 631.4 | 600.2 | 377.4 | 396.9 | 492.4
1318 | 1183 | 492.2 | 554.2 | 579.6 | 631.3 | 600.5 | 377.5 | 397 | 492.7
1319 | 1184 | 490.9 | 554 | 580 | 630.7 | 600.7 | 377.5 | 397.1 | 492.9
1320 | 1185 | 489.5 | 554.5 | 580.3 | 630.3 | 601.1 | 377.5 | 397.2 | 493
1321 | 1186 | 488.2 | 555 | 581.1 | 629.9 | 602 | 377.4 | 397.4 | 493.1
1322 | 1187 | 487 | 555.5 | 581.8 | 629.9 | 603 | 377.4 | 397.5 | 493.2
1323 | 1188 | 485.8 | 555.5 | 582.2 | 630.9 | 604 | 377.4 | 397.5 | 493.3
1324 | 1189 | 484.7 | 555.6 | 582.6 | 631.9 | 604.7 | 377.4 | 397.6 | 493.3
1325 | 1190 | 483.6 | 555.8 | 583.2 | 633.1 | 605.6 | 377.3 | 397.5 | 493.4
1326 | 1191 | 482.6 | 555.9 | 583.5 | 634 | 605.6 | 377.3 | 397.5 | 493.5
1327 | 1192 | 481.4 | 556.3 | 583.6 | 634.7 | 606.2 | 377.2 | 397.5 | 493.6
1328 | 1193 | 480.4 | 556.4 | 583.6 | 634.3 | 606.7 | 377.1 | 397.6 | 493.7
1329 | 1194 | 479.2 | 555.9 | 583.8 | 633.9 | 607.6 | 377 | 397.6 | 493.7
1330 | 1195 | 478.1 | 555.9 | 584.2 | 633.5 | 608.2 | 376.9 | 397.6 | 493.8
1331 | 1196 | 476.8 | 556.1 | 585.1 | 633.1 | 608.6 | 376.8 | 397.6 | 493.7
1332 | 1197 | 475.6 | 555.9 | 585.7 | 633 | 609.2 | 376.7 | 397.5 | 493.6
1333 | 1198 | 474.5 | 556.1 | 585.9 | 634.1 | 609.6 | 376.7 | 397.5 | 493.6
1334 | 1199 | 473.4 | 556.4 | 586.1 | 634.8 | 610.3 | 376.6 | 397.3 | 493.6
1335 | 1200 | 472.4 | 556.5 | 586.4 | 635.1 | 610.6 | 376.6 | 397.2 | 493.6
1336 | 1201 | 471.2 | 556.4 | 586.6 | 635.1 | 610.8 | 376.5 | 397.1 | 493.7
1337 | 1202 | 470.2 | 556.7 | 586.7 | 635.7 | 611 | 376.4 | 396.9 | 493.7
1338 | 1203 | 469.2 | 556.7 | 586.9 | 636.3 | 611.1 | 376.3 | 396.7 | 493.5
1339 | 1204 | 468.1 | 556.9 | 586.8 | 636.5 | 610.9 | 376.2 | 396.6 | 493.4
1340 | 1205 | 467 | 557.3 | 586.8 | 636.1 | 610.7 | 376.2 | 396.5 | 493.4
1341 | 1206 | 465.9 | 557.6 | 586.8 | 635.8 | 610.4 | 376 | 396.3 | 493.4
1342 | 1207 | 464.9 | 558.2 | 586.8 | 635.4 | 610.2 | 375.9 | 396.2 | 493.3
1343 | 1208 | 463.9 | 558.7 | 586.9 | 635.2 | 610.9 | 375.8 | 396.1 | 493.1
1344 | 1209 | 462.6 | 558.9 | 586.9 | 635.6 | 611.3 | 375.7 | 396 | 492.9
1345 | 1210 | 461.5 | 558.9 | 587.1 | 638.7 | 612.3 | 375.6 | 395.7 | 492.9
1346 | 1211 | 460.6 | 559 | 587.3 | 641.6 | 613.3 | 375.4 | 395.5 | 492.8
1347 | 1212 | 459.6 | 559.1 | 587.6 | 641.8 | 613.9 | 375.3 | 395.3 | 492.7
1348 | 1213 | 458.6 | 559 | 587.7 | 640.3 | 614.5 | 375.2 | 395.2 | 492.5
1349 | 1214 | 457.7 | 558.9 | 587.7 | 639.3 | 615.3 | 375.1 | 395.1 | 492.3
1350 | 1215 | 456.8 | 558.8 | 587.7 | 638.8 | 615.3 | 374.9 | 394.9 | 492
1351 | 1216 | 455.9 | 558.7 | 587.9 | 638 | 615 | 374.8 | 394.7 | 491.9
1352 | 1217 | 455.1 | 558.4 | 588.1 | 638 | 615.1 | 374.6 | 394.4 | 491.7
1353 | 1218 | 454.2 | 558.4 | 588 | 638.2 | 614.9 | 374.4 | 394.2 | 491.6
1354 | 1219 | 453.2 | 558.5 | 588 | 638.4 | 614.3 | 374.2 | 393.9 | 491.4
1355 | 1220 | 452.2 | 558.6 | 588 | 638.1 | 613.7 | 374 | 393.5 | 491.1
1356 | 1221 | 451.1 | 559 | 588.4 | 639 | 614.1 | 373.8 | 393.2 | 491
1357 | 1222 | 450 | 559.3 | 588.6 | 638.2 | 614.8 | 373.6 | 392.9 | 490.9
1358 | 1223 | 448.8 | 558.7 | 588.7 | 638.2 | 616.1 | 373.4 | 392.6 | 490.8
1359 | 1224 | 447.8 | 558.2 | 589 | 639.5 | 617.3 | 373.3 | 392.3 | 490.7
1360 | 1225 | 446.7 | 557.9 | 589.4 | 640.9 | 618.2 | 373.1 | 392 | 490.4
1361 | 1226 | 445.6 | 557.9 | 589.6 | 641.9 | 618.5 | 372.9 | 391.7 | 490.1
1362 | 1227 | 444.6 | 557.7 | 589.7 | 641.8 | 619.2 | 372.6 | 391.5 | 489.8
1363 | 1228 | 443.6 | 557.8 | 590 | 640.4 | 619.9 | 372.4 | 391.2 | 489.5
1364 | 1229 | 442.5 | 558 | 590.2 | 640.1 | 620.3 | 372.2 | 391 | 489.2
1365 | 1230 | 441.5 | 558.1 | 590.3 | 640.7 | 620.7 | 372 | 390.9 | 489
1366 | 1231 | 440.6 | 558.6 | 590.4 | 640.4 | 621.1 | 371.8 | 390.6 | 488.8
1367 | 1232 | 439.6 | 558.7 | 590.4 | 640 | 621.4 | 371.7 | 390.3 | 488.5
1368 | 1233 | 438.6 | 558.9 | 590.4 | 639 | 621.7 | 371.5 | 389.9 | 488.3
1369 | 1234 | 437.7 | 559.2 | 590.3 | 638.6 | 622 | 371.3 | 389.6 | 487.9
1370 | 1235 | 436.8 | 559.2 | 590.3 | 639.3 | 621.6 | 371.1 | 389.2 | 487.6
1371 | 1236 | 435.9 | 559.1 | 590.4 | 639.4 | 621.3 | 370.9 | 388.8 | 487.3
1372 | 1237 | 435 | 559.2 | 590.6 | 639.9 | 621.4 | 370.7 | 388.3 | 487
1373 | 1238 | 434.2 | 559.4 | 590.6 | 639.2 | 621.9 | 370.4 | 387.9 | 486.7
1374 | 1239 | 433.3 | 559.3 | 591 | 638.4 | 622.2 | 370.2 | 387.5 | 486.5
1375 | 1240 | 432.4 | 559.6 | 591.5 | 638.5 | 622.3 | 370 | 387.1 | 486.2
1376 | 1241 | 431.5 | 560.1 | 591.7 | 638.1 | 622.7 | 369.8 | 386.8 | 485.9
1377 | 1242 | 430.5 | 560.2 | 592.1 | 637.7 | 622.5 | 369.5 | 386.5 | 485.7
1378 | 1243 | 429.5 | 560.3 | 592.7 | 638 | 622 | 369.3 | 386.3 | 485.3
1379 | 1244 | 428.6 | 560.5 | 592.7 | 638.2 | 621.8 | 369.1 | 386 | 484.9
1380 | 1245 | 427.6 | 560.6 | 592.5 | 638.1 | 621.6 | 368.8 | 385.7 | 484.4
1381 | 1246 | 426.6 | 560.6 | 592.5 | 637.5 | 621.3 | 368.5 | 385.5 | 484
1382 | 1247 | 425.8 | 560.8 | 593.5 | 636.7 | 621 | 368.2 | 385.2 | 483.5
1383 | 1248 | 425.1 | 561.3 | 594.2 | 635.4 | 620.7 | 367.9 | 384.9 | 483.1
1384 | 1249 | 424.2 | 561.4 | 594.7 | 634.6 | 620.6 | 367.6 | 384.6 | 482.6
1385 | 1250 | 423.4 | 561.4 | 594.8 | 634.7 | 620.8 | 367.3 | 384.3 | 482.1
1386 | 1251 | 422.5 | 561.2 | 594.4 | 636.5 | 621.5 | 367.1 | 383.8 | 481.7
1387 | 1252 | 421.4 | 560.8 | 595.2 | 637.9 | 622.2 | 366.8 | 383.5 | 481.3
1388 | 1253 | 420.5 | 560.3 | 596.1 | 638.2 | 622.7 | 366.5 | 383 | 480.9
1389 | 1254 | 419.7 | 559.8 | 596.3 | 639 | 623.2 | 366.3 | 382.6 | 480.4
1390 | 1255 | 418.8 | 559.4 | 596.7 | 640.2 | 623.9 | 366 | 382.2 | 480
1391 | 1256 | 417.9 | 559 | 596.6 | 639 | 624.1 | 365.7 | 382 | 479.4
1392 | 1257 | 417.1 | 558.7 | 596.2 | 638.5 | 624.2 | 365.4 | 381.7 | 478.9
1393 | 1258 | 416.3 | 558.3 | 595.9 | 637.9 | 624.6 | 365.1 | 381.3 | 478.4
1394 | 1259 | 415.3 | 558.2 | 595.7 | 638.8 | 625.1 | 364.8 | 381 | 478
1395 | 1260 | 414.5 | 558 | 595.5 | 640.6 | 625.6 | 364.5 | 380.6 | 477.5
1396 | 1261 | 413.6 | 557.9 | 595.3 | 639.8 | 626.2 | 364.2 | 380.2 | 477.1
1397 | 1262 | 412.7 | 557.8 | 595.5 | 639.8 | 626.1 | 364 | 379.8 | 476.7
1398 | 1263 | 411.9 | 557.7 | 595 | 638.8 | 625.8 | 363.6 | 379.5 | 476.2
1399 | 1264 | 411.1 | 557.7 | 594.5 | 637.5 | 625.4 | 363.3 | 379.1 | 475.9
1400 | 1265 | 410.1 | 557.5 | 594.1 | 637.4 | 625.1 | 363 | 378.8 | 475.4
1401 | 1266 | 409.3 | 557.1 | 594.1 | 636.8 | 624.8 | 362.7 | 378.4 | 475
1402 | 1267 | 408.6 | 557 | 594 | 635.9 | 624.6 | 362.4 | 378.1 | 474.5
1403 | 1268 | 407.7 | 557 | 594.3 | 636.6 | 624.3 | 362 | 377.7 | 474
1404 | 1269 | 406.8 | 557 | 594.2 | 639.1 | 624.3 | 361.7 | 377.3 | 473.6
1405 | 1270 | 406 | 556.8 | 594.2 | 639.8 | 624.2 | 361.4 | 376.9 | 473.1
1406 | 1271 | 405.3 | 556.4 | 594.7 | 639.5 | 624.6 | 361 | 376.6 | 472.6
1407 | 1272 | 404.4 | 556.1 | 595 | 639.9 | 624.8 | 360.7 | 376.2 | 472.1
1408 | 1273 | 403.6 | 556.3 | 594.5 | 639.4 | 624.8 | 360.3 | 375.9 | 471.7
1409 | 1274 | 402.8 | 556.2 | 594.4 | 638 | 624.8 | 360 | 375.4 | 471.3
1410 | 1275 | 402 | 556.3 | 594.7 | 637.1 | 624.9 | 359.6 | 375 | 470.7
1411 | 1276 | 401.3 | 556.8 | 595.7 | 637.4 | 625.3 | 359.3 | 374.6 | 470.1
1412 | 1277 | 400.5 | 557.1 | 596.4 | 638.6 | 625.7 | 358.9 | 374.5 | 469.7
1413 | 1278 | 399.6 | 556.7 | 597.5 | 640.2 | 626 | 358.6 | 374.1 | 469.2
1414 | 1279 | 398.7 | 556.7 | 596.8 | 639.2 | 626.1 | 358.3 | 373.7 | 468.6
1415 | 1280 | 397.9 | 556.9 | 595.9 | 638.2 | 626.5 | 357.9 | 373.1 | 468.1
1416 | 1281 | 397.1 | 557.3 | 596 | 636.6 | 626.4 | 357.5 | 372.7 | 467.6
1417 | 1282 | 396.3 | 557.7 | 596.2 | 634.4 | 625.8 | 357.2 | 372.4 | 467
1418 | 1283 | 395.5 | 557.9 | 596.2 | 633.9 | 625 | 356.8 | 372 | 466.6
1419 | 1284 | 394.8 | 558.2 | 595.7 | 633.7 | 624.7 | 356.5 | 371.6 | 466
1420 | 1285 | 394 | 558.1 | 595.4 | 634.2 | 624.7 | 356.2 | 371.2 | 465.6
1421 | 1286 | 393 | 557.8 | 595.4 | 634.4 | 625.1 | 355.8 | 370.8 | 465.1
1422 | 1287 | 392.1 | 557.5 | 594.9 | 634.4 | 625.5 | 355.5 | 370.5 | 464.6
1423 | 1288 | 391.3 | 557.4 | 594.6 | 633.8 | 625.2 | 355.2 | 370.1 | 464.1
1424 | 1289 | 390.5 | 557.4 | 594.9 | 633.4 | 625.2 | 354.8 | 369.8 | 463.6
1425 | 1290 | 389.6 | 557.3 | 594.6 | 635.4 | 625.2 | 354.4 | 369.6 | 463.1
1426 | 1291 | 388.8 | 556.9 | 593.8 | 635.4 | 625.8 | 354.1 | 369.3 | 462.7
1427 | 1292 | 388.3 | 556.6 | 593.2 | 633.7 | 625.8 | 353.7 | 368.9 | 462.2
1428 | 1293 | 387.6 | 556.7 | 592.6 | 632.8 | 626 | 353.4 | 368.4 | 461.7
1429 | 1294 | 386.9 | 556.9 | 592.4 | 632.9 | 627.1 | 353 | 367.8 | 461.2
1430 | 1295 | 386.2 | 557.2 | 593.2 | 633.6 | 628 | 352.7 | 367.3 | 460.9
1431 | 1296 | 385.4 | 557.4 | 594.3 | 634.3 | 629 | 352.4 | 366.9 | 460.4
1432 | 1297 | 384.7 | 557.4 | 595.6 | 636.8 | 630.2 | 352 | 366.3 | 459.8
1433 | 1298 | 383.9 | 557.1 | 596.8 | 638.4 | 631.1 | 351.7 | 365.9 | 459.3
1434 | 1299 | 383 | 556.8 | 598.4 | 641.2 | 631.5 | 351.4 | 365.4 | 458.9
1435 | 1300 | 382.2 | 556.8 | 599.3 | 643.8 | 633 | 351.1 | 364.8 | 458.5
1436 | 1301 | 381.5 | 556.4 | 600.4 | 645.7 | 633.7 | 350.7 | 364.3 | 458
1437 | 1302 | 380.8 | 556 | 600.9 | 647 | 634 | 350.3 | 363.9 | 457.5
1438 | 1303 | 380.2 | 555.8 | 599.6 | 646.6 | 634.5 | 349.9 | 363.4 | 457
1439 | 1304 | 379.4 | 555.5 | 598.8 | 647.7 | 635.1 | 349.5 | 362.9 | 456.6
1440 | 1305 | 378.5 | 555.1 | 598.4 | 647.3 | 635.6 | 349.2 | 362.5 | 456.1
1441 | 1306 | 377.9 | 554.6 | 597.5 | 647.3 | 635.8 | 348.8 | 362.1 | 455.6
1442 | 1307 | 377.1 | 554.3 | 597.6 | 646.8 | 635.8 | 348.5 | 361.7 | 455.2
1443 | 1308 | 376.3 | 553.8 | 597 | 646.4 | 635.2 | 348.2 | 361.2 | 454.6
1444 | 1309 | 375.3 | 553.5 | 595.8 | 642.9 | 634.6 | 347.8 | 360.8 | 453.9
1445 | 1310 | 374.5 | 553.5 | 594.7 | 640.4 | 634.5 | 347.4 | 360.4 | 453.2
1446 | 1311 | 373.7 | 553.4 | 593.8 | 638.6 | 634.2 | 347.1 | 360 | 452.6
1447 | 1312 | 373 | 553.5 | 592.9 | 636.2 | 633 | 346.7 | 359.7 | 451.9
1448 | 1313 | 372.3 | 553.6 | 592.3 | 635.1 | 631 | 346.3 | 359.4 | 451.2
1449 | 1314 | 371.6 | 553.8 | 591.6 | 633.2 | 629.3 | 345.9 | 359.1 | 450.6
1450 | 1315 | 370.9 | 554.2 | 590.9 | 631.3 | 628.1 | 345.6 | 358.6 | 450
1451 | 1316 | 370.2 | 554.8 | 590.5 | 630.2 | 626.7 | 345.1 | 358.2 | 449.3
1452 | 1317 | 369.6 | 555.2 | 589.6 | 629.1 | 626.3 | 344.7 | 357.8 | 448.6
1453 | 1318 | 368.9 | 555.1 | 589.7 | 629.9 | 626.7 | 344.3 | 357.3 | 447.9
1454 | 1319 | 368.2 | 554.9 | 589.7 | 630.9 | 627.1 | 343.9 | 356.8 | 447.2
1455 | 1320 | 367.5 | 554.6 | 590.6 | 630.9 | 627.6 | 343.5 | 356.3 | 446.4
1456 | 1321 | 366.8 | 554.3 | 590.4 | 629.4 | 628.3 | 343.1 | 355.8 | 445.6
1457 | 1322 | 366.1 | 554.1 | 590 | 631.3 | 628.7 | 342.7 | 355.4 | 444.9
1458 | 1323 | 365.3 | 553.8 | 589 | 632.8 | 629.2 | 342.3 | 354.9 | 444.2
1459 | 1324 | 364.5 | 553.6 | 588.6 | 633.3 | 629.8 | 341.9 | 354.5 | 443.4
1460 | 1325 | 364 | 553.3 | 588 | 631.7 | 630.3 | 341.5 | 354.1 | 442.7
1461 | 1326 | 363.4 | 553.2 | 587.5 | 632.3 | 631.2 | 341.1 | 353.8 | 441.9
1462 | 1327 | 362.8 | 553.2 | 587.2 | 631.3 | 631.7 | 340.7 | 353.4 | 441.1
1463 | 1328 | 362.2 | 553.1 | 587 | 631.2 | 631.8 | 340.4 | 353 | 440.4
1464 | 1329 | 361.5 | 553 | 586.9 | 629.7 | 631.1 | 340 | 352.6 | 439.6
1465 | 1330 | 360.8 | 553.4 | 586.2 | 627.6 | 629.6 | 339.6 | 352.2 | 438.9
1466 | 1331 | 360 | 553.4 | 585.7 | 625.6 | 628.1 | 339.3 | 351.8 | 438.1
1467 | 1332 | 359.3 | 553.3 | 584.9 | 624.5 | 628.1 | 338.9 | 351.3 | 437.3
1468 | 1333 | 358.6 | 553.1 | 585 | 624.6 | 628.7 | 338.5 | 350.8 | 436.4
1469 | 1334 | 357.8 | 553.1 | 585 | 624.7 | 629.5 | 338.1 | 350.4 | 435.6
1470 | 1335 | 357.1 | 553.2 | 584.5 | 624 | 630.4 | 337.8 | 349.9 | 434.8
1471 | 1336 | 356.4 | 553 | 584.3 | 624.3 | 630.7 | 337.4 | 349.4 | 434
1472 | 1337 | 355.6 | 552.9 | 584 | 623 | 631 | 337 | 348.9 | 433.1
1473 | 1338 | 354.9 | 552.7 | 583.8 | 621.6 | 630.6 | 336.6 | 348.4 | 432.2
1474 | 1339 | 354.2 | 552.7 | 584 | 620.2 | 629 | 336.2 | 348.1 | 431.4
1475 | 1340 | 353.5 | 552.9 | 583.3 | 619.4 | 628.1 | 335.8 | 347.7 | 430.5
1476 | 1341 | 352.7 | 552.7 | 583.5 | 619.9 | 628.4 | 335.4 | 347.3 | 429.7
1477 | 1342 | 352.1 | 552.5 | 584 | 620.9 | 629.2 | 335 | 346.8 | 428.9
1478 | 1343 | 351.4 | 552.2 | 585.5 | 622.3 | 630.2 | 334.6 | 346.4 | 428.1
1479 | 1344 | 350.7 | 551.7 | 585 | 623.2 | 631.1 | 334.2 | 346 | 427.2
1480 | 1345 | 349.9 | 551.6 | 585.2 | 621.9 | 632.1 | 333.9 | 345.5 | 426.5
1481 | 1346 | 349.3 | 551.6 | 584.7 | 621.8 | 632.7 | 333.5 | 345 | 425.7
1482 | 1347 | 348.8 | 551.4 | 583.8 | 620.5 | 632.7 | 333.2 | 344.6 | 424.9
1483 | 1348 | 348.2 | 551.3 | 582.8 | 618.3 | 632.5 | 332.8 | 344.1 | 424
1484 | 1349 | 347.5 | 551.5 | 581.8 | 616.7 | 632.7 | 332.5 | 343.7 | 423.3
1485 | 1350 | 346.9 | 551.9 | 581.5 | 615.8 | 632.6 | 332.1 | 343.2 | 422.4
1486 | 1351 | 346.2 | 551.7 | 581.6 | 615.3 | 632.5 | 331.7 | 342.8 | 421.5
1487 | 1352 | 345.5 | 551.4 | 580.6 | 614.3 | 632.8 | 331.3 | 342.3 | 420.6
1488 | 1353 | 344.8 | 551.3 | 580 | 613.9 | 632.7 | 330.9 | 342 | 419.8
1489 | 1354 | 344.2 | 551.4 | 579.2 | 613.2 | 633.1 | 330.5 | 341.5 | 419
1490 | 1355 | 343.6 | 550.9 | 578.7 | 612.4 | 634.3 | 330.1 | 341.1 | 418.2
1491 | 1356 | 343 | 550.6 | 579.2 | 611.7 | 634.9 | 329.7 | 340.7 | 417.4
1492 | 1357 | 342.3 | 550.3 | 579.2 | 610.8 | 635.4 | 329.3 | 340.3 | 416.6
1493 | 1358 | 341.7 | 550 | 579.8 | 611.2 | 635.9 | 328.9 | 339.9 | 415.8
1494 | 1359 | 341 | 549.7 | 580.4 | 610.3 | 636.2 | 328.5 | 339.5 | 414.9
1495 | 1360 | 340.5 | 549.6 | 579.8 | 608.4 | 636.3 | 328.1 | 339 | 414
1496 | 1361 | 339.9 | 549.9 | 578.8 | 606.8 | 636.1 | 327.7 | 338.6 | 413.2
1497 | 1362 | 339.2 | 550.2 | 578.2 | 605.6 | 635.9 | 327.3 | 338.1 | 412.4
1498 | 1363 | 338.6 | 550.3 | 578.5 | 605 | 636 | 326.9 | 337.7 | 411.6
1499 | 1364 | 338 | 550.3 | 578.6 | 604.7 | 636 | 326.5 | 337.2 | 410.8
1500 | 1365 | 337.4 | 550.5 | 578.4 | 604.8 | 636.3 | 326.1 | 336.8 | 410
1501 | 1366 | 336.8 | 550.7 | 578.4 | 603.9 | 636.8 | 325.8 | 336.3 | 409.1
1502 | 1367 | 336.1 | 550.2 | 578.8 | 603.5 | 637.4 | 325.4 | 335.9 | 408.2
1503 | 1368 | 335.4 | 549.9 | 579.1 | 603.2 | 637.9 | 324.9 | 335.4 | 407.4
1504 | 1369 | 334.8 | 549.8 | 578.1 | 602.1 | 638.2 | 324.5 | 335 | 406.6
1505 | 1370 | 334.1 | 549.9 | 578 | 600.6 | 638.7 | 324.1 | 334.5 | 405.7
1506 | 1371 | 333.4 | 550 | 578 | 599.9 | 640 | 323.7 | 334.1 | 404.8
1507 | 1372 | 332.9 | 550.1 | 577.6 | 598.9 | 640.9 | 323.3 | 333.7 | 404
1508 | 1373 | 332.3 | 549.6 | 577.5 | 597.7 | 641.9 | 322.9 | 333.2 | 403.2
1509 | 1374 | 331.8 | 549.4 | 577.3 | 596.7 | 642.7 | 322.5 | 332.7 | 402.4
1510 | 1375 | 331.2 | 548.9 | 577.9 | 595.4 | 643.3 | 322.1 | 332.2 | 401.6
1511 | 1376 | 330.6 | 548.4 | 578 | 593.9 | 643.2 | 321.7 | 331.6 | 400.8
1512 | 1377 | 330 | 548.6 | 577.5 | 592.9 | 643.5 | 321.3 | 331.1 | 400
1513 | 1378 | 329.5 | 548.8 | 577.9 | 591.9 | 643.8 | 321 | 330.7 | 399.1
1514 | 1379 | 328.9 | 549 | 578.4 | 590.8 | 643.1 | 320.6 | 330.2 | 398.3
1515 | 1380 | 328.3 | 548.6 | 578.1 | 589.7 | 643.8 | 320.2 | 329.8 | 397.6
1516 | 1381 | 327.7 | 547.8 | 579.5 | 588.7 | 643.7 | 319.8 | 329.4 | 396.8
1517 | 1382 | 327.3 | 547 | 580.1 | 587.6 | 642.4 | 319.5 | 329 | 396
1518 | 1383 | 326.7 | 546.4 | 579.7 | 586.5 | 641.3 | 319.1 | 328.6 | 395.2
1519 | 1384 | 326 | 546.1 | 579.9 | 585.6 | 640 | 318.7 | 328.2 | 394.4
1520 | 1385 | 325.4 | 546.1 | 579 | 584.7 | 639.5 | 318.3 | 327.7 | 393.6
1521 | 1386 | 324.7 | 545.5 | 577.7 | 583.7 | 639.4 | 318 | 327.4 | 392.7
1522 | 1387 | 324 | 544.6 | 575.9 | 582.8 | 638.8 | 317.6 | 327 | 391.8
1523 | 1388 | 323.3 | 543.8 | 575.2 | 581.9 | 639.1 | 317.3 | 326.7 | 391.1
1524 | 1389 | 322.8 | 543.4 | 575.6 | 580.9 | 638.7 | 316.9 | 326.3 | 390.3
1525 | 1390 | 322.1 | 543.3 | 576 | 579.9 | 637.9 | 316.5 | 325.9 | 389.6
1526 | 1391 | 321.5 | 543.5 | 575.7 | 579 | 637.8 | 316.1 | 325.5 | 388.9
1527 | 1392 | 321 | 543.8 | 574.7 | 578 | 638 | 315.8 | 325 | 388.2
1528 | 1393 | 320.5 | 544.3 | 573.9 | 576.6 | 638.7 | 315.4 | 324.6 | 387.4
1529 | 1394 | 320 | 544.7 | 574.3 | 575.7 | 639.3 | 315 | 324 | 386.7
1530 | 1395 | 319.4 | 545 | 574 | 575.3 | 639.1 | 314.6 | 323.6 | 385.9
1531 | 1396 | 318.9 | 545.3 | 572.7 | 574.6 | 639.4 | 314.3 | 323.1 | 385.2
1532 | 1397 | 318.3 | 545.3 | 571.7 | 573.8 | 640.1 | 313.9 | 322.7 | 384.6
1533 | 1398 | 317.8 | 545.4 | 571.7 | 573.1 | 642.4 | 313.6 | 322.4 | 383.9
1534 | 1399 | 317.3 | 545.4 | 572.8 | 572.3 | 644.3 | 313.2 | 322 | 383.1
1535 | 1400 | 316.8 | 545.4 | 573 | 571.6 | 644.9 | 312.8 | 321.5 | 382.4
1536 | 1401 | 316.3 | 545.6 | 573 | 570.8 | 645.3 | 312.5 | 320.9 | 381.7
1537 | 1402 | 315.8 | 545.4 | 572.3 | 570 | 644.8 | 312.1 | 320.4 | 381
1538 | 1403 | 315.3 | 545 | 572.1 | 569.2 | 645 | 311.8 | 319.9 | 380.4
1539 | 1404 | 314.7 | 544.6 | 572.4 | 568.4 | 645 | 311.4 | 319.4 | 379.7
1540 | 1405 | 314.2 | 544.1 | 573.5 | 567.7 | 644.7 | 311.1 | 319 | 378.9
1541 | 1406 | 313.6 | 543.3 | 574 | 567.2 | 644.6 | 310.7 | 318.6 | 378.3
1542 | 1407 | 313.1 | 542.5 | 573.6 | 566.6 | 644.4 | 310.4 | 318.3 | 377.6
1543 | 1408 | 312.5 | 542.4 | 572.4 | 566 | 644.8 | 310 | 317.8 | 376.9
1544 | 1409 | 312.1 | 542.3 | 570.8 | 565.7 | 644 | 309.6 | 317.4 | 376.2
1545 | 1410 | 311.6 | 542.4 | 569.5 | 565.3 | 642.8 | 309.3 | 316.9 | 375.5
1546 | 1411 | 311.1 | 542.5 | 568.7 | 564.7 | 642.5 | 308.9 | 316.5 | 374.8
1547 | 1412 | 310.5 | 542.7 | 567.7 | 564.1 | 642.5 | 308.6 | 316.1 | 374.2
1548 | 1413 | 309.9 | 542.5 | 567.6 | 562.8 | 642.4 | 308.2 | 315.7 | 373.5
1549 | 1414 | 309.3 | 542.1 | 567.9 | 561.8 | 642.2 | 307.8 | 315.2 | 372.8
1550 | 1415 | 308.8 | 542 | 567.6 | 561 | 642.1 | 307.4 | 314.7 | 372.1
1551 | 1416 | 308.2 | 542.2 | 566.4 | 560.4 | 642.6 | 307.1 | 314.3 | 371.5
1552 | 1417 | 307.7 | 542.2 | 565.9 | 559.2 | 642.8 | 306.7 | 313.9 | 370.8
1553 | 1418 | 307.2 | 541.7 | 565.8 | 558.2 | 643.6 | 306.3 | 313.5 | 370.2
1554 | 1419 | 306.6 | 542.1 | 564.9 | 557.5 | 644.6 | 305.9 | 313.2 | 369.6
1555 | 1420 | 306 | 542.5 | 564.2 | 556.7 | 645.5 | 305.5 | 312.8 | 368.9
1556 | 1421 | 305.4 | 541.7 | 563.5 | 556 | 645.5 | 305.2 | 312.4 | 368.2
1557 | 1422 | 304.9 | 540.6 | 563.7 | 554.8 | 645.4 | 304.8 | 311.9 | 367.5
1558 | 1423 | 304.4 | 539.9 | 563.9 | 553.7 | 645.4 | 304.4 | 311.5 | 366.8
1559 | 1424 | 303.9 | 539.6 | 564.4 | 552.7 | 646.1 | 304.1 | 311.1 | 366.1
1560 | 1425 | 303.4 | 539.4 | 565.6 | 551.5 | 646.5 | 303.7 | 310.6 | 365.4
1561 | 1426 | 302.9 | 539.1 | 565.8 | 550.7 | 645.7 | 303.3 | 310.2 | 364.7
1562 | 1427 | 302.4 | 539.2 | 564.7 | 550.2 | 645.2 | 303 | 309.9 | 364.1
1563 | 1428 | 301.9 | 539 | 564 | 549.4 | 644.5 | 302.6 | 309.6 | 363.4
1564 | 1429 | 301.5 | 538.4 | 563.1 | 549 | 643.2 | 302.3 | 309.3 | 362.8
1565 | 1430 | 301 | 538.6 | 561.7 | 548.7 | 643.1 | 301.9 | 309 | 362.1
1566 | 1431 | 300.4 | 538.8 | 561.4 | 548.1 | 643 | 301.6 | 308.6 | 361.5
1567 | 1432 | 299.9 | 539.2 | 562.3 | 547.6 | 639.6 | 301.2 | 308.3 | 360.9
1568 | 1433 | 299.4 | 539.7 | 561.6 | 546.8 | 636 | 300.8 | 307.8 | 360.3
1569 | 1434 | 299 | 540.2 | 561.1 | 545.7 | 635.7 | 300.4 | 307.4 | 359.6
1570 | 1435 | 298.5 | 540.3 | 560.2 | 544.5 | 636.9 | 300 | 306.9 | 358.9
1571 | 1436 | 298.1 | 540.3 | 559.7 | 543.3 | 638.3 | 299.6 | 306.5 | 358.2
1572 | 1437 | 297.5 | 540.4 | 558.6 | 542.4 | 639.7 | 299.3 | 306 | 357.5
1573 | 1438 | 296.9 | 540.2 | 557.5 | 541.6 | 641 | 298.9 | 305.5 | 356.9
1574 | 1439 | 296.4 | 540.2 | 556.8 | 541.2 | 642.5 | 298.5 | 305.1 | 356.3
1575 | 1440 | 295.8 | 540.5 | 557 | 540.6 | 642.5 | 298.1 | 304.6 | 355.6
1576 | 1441 | 295.3 | 540.3 | 556.4 | 540.3 | 639.9 | 297.8 | 304.1 | 355
1577 | 1442 | 294.7 | 540.6 | 556.1 | 539.8 | 638.8 | 297.4 | 303.7 | 354.4
1578 | 1443 | 294.1 | 541.2 | 556.3 | 539.4 | 636.4 | 297 | 303.3 | 353.7
1579 | 1444 | 293.6 | 541.5 | 555.7 | 538.9 | 635.3 | 296.7 | 302.9 | 353
1580 | 1445 | 293.1 | 541.8 | 555.6 | 538.3 | 635.2 | 296.2 | 302.6 | 352.4
1581 | 1446 | 292.7 | 541.3 | 555 | 537.7 | 635.9 | 295.8 | 302.2 | 351.9
1582 | 1447 | 292.1 | 540.4 | 554.2 | 537 | 636.3 | 295.5 | 301.8 | 351.4
1583 | 1448 | 291.7 | 540.2 | 553.8 | 536.2 | 634.5 | 295.1 | 301.4 | 350.8
1584 | 1449 | 291.2 | 540.6 | 553.2 | 535.5 | 633.4 | 294.7 | 300.9 | 350.2
1585 | 1450 | 290.8 | 541.4 | 552.1 | 534.8 | 634.9 | 294.3 | 300.5 | 349.6
1586 | 1451 | 290.4 | 542 | 551.5 | 533.7 | 636.2 | 294 | 300.1 | 348.9
1587 | 1452 | 289.9 | 542.7 | 551.4 | 532.7 | 637.9 | 293.6 | 299.6 | 348.2
1588 | 1453 | 289.5 | 542.5 | 551.1 | 531.6 | 639.8 | 293.2 | 299.3 | 347.5
1589 | 1454 | 289 | 542.1 | 550.6 | 530.9 | 640.3 | 292.9 | 298.8 | 346.8
1590 | 1455 | 288.5 | 541.3 | 549.7 | 529.9 | 640.9 | 292.6 | 298.4 | 346.2
1591 | 1456 | 288.1 | 541.1 | 548.9 | 529.4 | 641.7 | 292.2 | 298.1 | 345.6
1592 | 1457 | 287.6 | 540.5 | 549 | 528.7 | 642.3 | 291.9 | 297.7 | 345.1
1593 | 1458 | 287.1 | 539.4 | 548.4 | 528.3 | 641.2 | 291.5 | 297.4 | 344.5
1594 | 1459 | 286.6 | 538.9 | 548.3 | 528 | 640.7 | 291.2 | 296.9 | 343.8
1595 | 1460 | 285.9 | 538.1 | 548.2 | 527.1 | 641.9 | 290.9 | 296.5 | 343.2
1596 | 1461 | 285.3 | 537.2 | 547.5 | 526.6 | 642.1 | 290.6 | 296 | 342.7
1597 | 1462 | 284.9 | 536 | 547.1 | 526.2 | 641.8 | 290.3 | 295.7 | 342.1
1598 | 1463 | 284.4 | 534.6 | 546.6 | 525.7 | 641.6 | 289.9 | 295.3 | 341.4
1599 | 1464 | 283.9 | 533.6 | 545.5 | 524.9 | 641.8 | 289.5 | 294.9 | 340.9
1600 | 1465 | 283.4 | 532.3 | 544.7 | 524.4 | 639.8 | 289.2 | 294.5 | 340.4
1601 | 1466 | 282.9 | 530.8 | 545.4 | 523.3 | 638.4 | 288.8 | 294.1 | 340
1602 | 1467 | 282.4 | 530.7 | 546.7 | 522.3 | 637.9 | 288.5 | 293.7 | 339.4
1603 | 1468 | 281.8 | 529.8 | 547.7 | 521.6 | 636.2 | 288.2 | 293.2 | 338.9
1604 | 1469 | 281.3 | 528.5 | 548.6 | 520.8 | 635.4 | 287.8 | 292.6 | 338.4
1605 | 1470 | 280.9 | 528.1 | 549.2 | 520.3 | 634 | 287.5 | 292.2 | 337.8
1606 | 1471 | 280.5 | 527.5 | 548.7 | 519.5 | 633.1 | 287.1 | 291.9 | 337.3
1607 | 1472 | 280.2 | 527.1 | 548.6 | 519.1 | 633.5 | 286.8 | 291.5 | 336.7
1608 | 1473 | 279.7 | 526.8 | 548.7 | 518.7 | 632.5 | 286.4 | 290.9 | 336.1
1609 | 1474 | 279.2 | 525.8 | 548.7 | 517.8 | 628.7 | 286 | 290.4 | 335.5
1610 | 1475 | 278.7 | 525.1 | 548.5 | 517.1 | 627.6 | 285.7 | 290 | 334.9
1611 | 1476 | 278.2 | 524.6 | 548.3 | 516.8 | 626.7 | 285.3 | 289.6 | 334.4
1612 | 1477 | 277.7 | 524.1 | 548 | 516.6 | 622.6 | 285 | 289.2 | 333.8
1613 | 1478 | 277.2 | 524.2 | 547.3 | 516.4 | 620.7 | 284.6 | 288.8 | 333.3
1614 | 1479 | 276.8 | 523.9 | 546.7 | 516.1 | 618.9 | 284.3 | 288.4 | 332.8
1615 | 1480 | 276.4 | 523.3 | 546.3 | 516.1 | 616.8 | 284 | 288.1 | 332.3
1616 | 1481 | 275.9 | 522.5 | 545.5 | 516 | 614.3 | 283.7 | 287.8 | 331.9
1617 | 1482 | 275.4 | 522 | 544.6 | 515.5 | 610.7 | 283.4 | 287.4 | 331.3
1618 | 1483 | 274.9 | 521.1 | 543.5 | 515.1 | 605.8 | 283 | 287.1 | 330.8
1619 | 1484 | 274.4 | 520 | 542.7 | 514.9 | 601.8 | 282.6 | 286.7 | 330.2
1620 | 1485 | 273.9 | 519.2 | 542.8 | 514.5 | 599 | 282.3 | 286.3 | 329.6
1621 | 1486 | 273.5 | 518.9 | 542.6 | 513.9 | 595.5 | 281.9 | 285.9 | 329.2
1622 | 1487 | 273 | 517.9 | 542.6 | 513.5 | 591.4 | 281.6 | 285.5 | 328.7
1623 | 1488 | 272.7 | 517.2 | 542.6 | 512.8 | 587.1 | 281.2 | 285 | 328.1
1624 | 1489 | 272.3 | 516.5 | 542.1 | 512.2 | 582.9 | 280.9 | 284.5 | 327.5
1625 | 1490 | 271.9 | 515.9 | 542 | 511.7 | 578.9 | 280.5 | 284.1 | 327
1626 | 1491 | 271.5 | 515.8 | 542.3 | 510.8 | 574.2 | 280.2 | 283.7 | 326.5
1627 | 1492 | 271.1 | 515.3 | 542.3 | 510.3 | 570 | 279.9 | 283.3 | 326
1628 | 1493 | 270.6 | 514.4 | 541.9 | 509.7 | 566.1 | 279.5 | 282.8 | 325.5
1629 | 1494 | 270.1 | 513.6 | 541.2 | 509.1 | 561.7 | 279.2 | 282.4 | 325
1630 | 1495 | 269.7 | 512.8 | 540.6 | 508.8 | 557.5 | 278.8 | 282.1 | 324.5
1631 | 1496 | 269.3 | 512.2 | 539.2 | 509 | 553.4 | 278.5 | 281.7 | 324
1632 | 1497 | 268.7 | 511.1 | 537.7 | 509 | 549 | 278.1 | 281.5 | 323.4
1633 | 1498 | 268.3 | 510.8 | 536.3 | 508.4 | 544.7 | 277.8 | 281.1 | 322.8
1634 | 1499 | 267.8 | 510.6 | 535.3 | 507.8 | 540.5 | 277.4 | 280.7 | 322.2
1635 | 1500 | 267.2 | 510.1 | 534.6 | 507.4 | 536.4 | 277.1 | 280.3 | 321.7
1636 | 1501 | 266.7 | 509.4 | 534 | 506.6 | 532.3 | 276.8 | 280 | 321.3
1637 | 1502 | 266.3 | 508.5 | 533.5 | 505.7 | 528.6 | 276.5 | 279.6 | 320.9
1638 | 1503 | 265.9 | 507.9 | 533.2 | 505 | 525.4 | 276.2 | 279.2 | 320.5
1639 | 1504 | 265.5 | 507.6 | 532.6 | 504.1 | 522.6 | 275.9 | 278.8 | 320
1640 | 1505 | 265.3 | 507.1 | 531.9 | 503.3 | 520 | 275.5 | 278.5 | 319.5
1641 | 1506 | 264.9 | 506.6 | 531.6 | 502.4 | 517.1 | 275.1 | 278.1 | 319
1642 | 1507 | 264.4 | 505.5 | 531.2 | 502.1 | 514.9 | 274.7 | 277.6 | 318.6
1643 | 1508 | 264 | 504.4 | 530.5 | 501.5 | 513 | 274.4 | 277.1 | 318.1
1644 | 1509 | 263.6 | 503.6 | 530.2 | 500.6 | 511.2 | 274.1 | 276.6 | 317.6
1645 | 1510 | 263.2 | 504.4 | 530 | 500 | 509.7 | 273.8 | 276.1 | 317
1646 | 1511 | 262.8 | 504.7 | 529.4 | 500 | 508.2 | 273.4 | 275.6 | 316.6
1647 | 1512 | 262.4 | 504.1 | 528.6 | 499.4 | 506.6 | 273.1 | 275.2 | 316.1
1648 | 1513 | 262 | 503.8 | 527.4 | 498.9 | 505.3 | 272.7 | 274.9 | 315.6
1649 | 1514 | 261.5 | 503.7 | 527 | 498.3 | 504 | 272.4 | 274.5 | 315.1
1650 | 1515 | 261.1 | 503.5 | 526.9 | 497.9 | 502.9 | 272 | 274.1 | 314.6
1651 | 1516 | 260.8 | 503.1 | 526.8 | 497.1 | 501.7 | 271.7 | 273.8 | 314.2
1652 | 1517 | 260.4 | 503.1 | 526.6 | 496.4 | 500.8 | 271.3 | 273.5 | 313.6
1653 | 1518 | 259.9 | 503.4 | 526.5 | 495.9 | 499.9 | 271 | 273.2 | 313.1
1654 | 1519 | 259.5 | 503.9 | 526.3 | 495.5 | 499 | 270.6 | 272.8 | 312.6
1655 | 1520 | 259.1 | 503.9 | 526.4 | 494.8 | 498.2 | 270.3 | 272.4 | 312.1
1656 | 1521 | 258.7 | 503.1 | 525.8 | 494.1 | 497.4 | 269.9 | 272 | 311.6
1657 | 1522 | 258.2 | 502.5 | 524.8 | 493.7 | 496.9 | 269.6 | 271.5 | 311.2
1658 | 1523 | 257.6 | 501.9 | 525.1 | 492.8 | 495.3 | 269.2 | 271.1 | 310.7
1659 | 1524 | 257.2 | 502 | 524.8 | 492.1 | 494.5 | 268.8 | 270.6 | 310.3
1660 | 1525 | 256.9 | 501.8 | 524.5 | 491.4 | 493.5 | 268.5 | 270.3 | 309.9
1661 | 1526 | 256.6 | 500.8 | 524.3 | 490.8 | 492.4 | 268.1 | 270 | 309.5
1662 | 1527 | 256.2 | 499.9 | 523.7 | 490.5 | 491.4 | 267.8 | 269.5 | 309.1
1663 | 1528 | 255.7 | 499.6 | 523.2 | 490.4 | 490.7 | 267.5 | 269.2 | 308.5
1664 | 1529 | 255.2 | 498.7 | 522.1 | 490.4 | 489.9 | 267.2 | 268.8 | 308.1
1665 | 1530 | 254.8 | 497.3 | 521 | 489.9 | 488.9 | 266.8 | 268.4 | 307.7
1666 | 1531 | 254.4 | 496.1 | 520.6 | 489.2 | 487.8 | 266.4 | 268 | 307.3
1667 | 1532 | 254 | 494.8 | 519.9 | 488.3 | 486.5 | 266 | 267.6 | 306.9
1668 | 1533 | 253.6 | 494.5 | 519.4 | 487.4 | 485.5 | 265.7 | 267.3 | 306.6
1669 | 1534 | 253.1 | 493.6 | 519 | 486.8 | 484.7 | 265.4 | 266.9 | 306.3
1670 | 1535 | 252.7 | 492.6 | 518.2 | 486.3 | 483.9 | 265.1 | 266.4 | 305.9
1671 | 1536 | 252.3 | 491.6 | 517.4 | 485.7 | 482.9 | 264.8 | 266 | 305.5
1672 | 1537 | 251.9 | 490.9 | 516.8 | 484.8 | 481.9 | 264.4 | 265.5 | 305
1673 | 1538 | 251.5 | 490.5 | 516.1 | 484.2 | 481.1 | 264.1 | 265.1 | 304.6
1674 | 1539 | 251.1 | 490.2 | 515.7 | 483.8 | 480.3 | 263.7 | 264.8 | 304.2
1675 | 1540 | 250.6 | 489.6 | 515.2 | 483.2 | 479.6 | 263.3 | 264.4 | 303.7
1676 | 1541 | 250.1 | 489.4 | 514.7 | 482.8 | 479 | 263 | 263.9 | 303.2
1677 | 1542 | 249.7 | 489.3 | 514.1 | 482.7 | 478.6 | 262.7 | 263.5 | 302.7
1678 | 1543 | 249.3 | 489.4 | 513 | 481.9 | 478.4 | 262.4 | 263.1 | 302.3
1679 | 1544 | 248.8 | 488.9 | 512.5 | 481.3 | 477.6 | 262.1 | 262.6 | 301.9
1680 | 1545 | 248.5 | 487.8 | 511.9 | 480.3 | 476.8 | 261.8 | 262.2 | 301.5
1681 | 1546 | 248.2 | 487.2 | 511.1 | 479.8 | 475.8 | 261.5 | 261.8 | 301
1682 | 1547 | 247.8 | 486.2 | 510.8 | 479.1 | 474.7 | 261.1 | 261.6 | 300.5
1683 | 1548 | 247.5 | 485.2 | 510 | 478.9 | 473.7 | 260.8 | 261.3 | 300.1
1684 | 1549 | 247.1 | 484.8 | 509.2 | 478.5 | 472.3 | 260.5 | 261 | 299.7
1685 | 1550 | 246.7 | 484.1 | 508.5 | 477.8 | 470.7 | 260.1 | 260.7 | 299.3
1686 | 1551 | 246.3 | 483.1 | 507.8 | 477.2 | 469.9 | 259.8 | 260.3 | 299
1687 | 1552 | 246 | 483 | 507 | 476.8 | 469.4 | 259.4 | 259.9 | 298.5
1688 | 1553 | 245.7 | 482.7 | 506.4 | 476.6 | 468.7 | 259.1 | 259.6 | 298
1689 | 1554 | 245.3 | 482.3 | 505.7 | 476.1 | 467.9 | 258.8 | 259.2 | 297.4
1690 | 1555 | 244.9 | 481.5 | 505 | 475.4 | 466.8 | 258.5 | 258.8 | 297
1691 | 1556 | 244.5 | 480.9 | 504 | 475 | 465.8 | 258.2 | 258.5 | 296.6
1692 | 1557 | 244.1 | 479.8 | 503.1 | 474.5 | 464.8 | 257.9 | 258.1 | 296.3
1693 | 1558 | 243.7 | 478.2 | 502.1 | 473.6 | 463.7 | 257.5 | 257.6 | 296
1694 | 1559 | 243.4 | 476.6 | 501 | 472.5 | 462.9 | 257.3 | 257.2 | 295.6
1695 | 1560 | 243 | 475.3 | 500.2 | 471.7 | 462.2 | 257 | 256.8 | 295.2
1696 | 1561 | 242.5 | 474.1 | 500 | 470.9 | 461.5 | 256.7 | 256.4 | 294.7
1697 | 1562 | 242.1 | 472.6 | 499.5 | 470.1 | 461 | 256.4 | 256.1 | 294.2
1698 | 1563 | 241.7 | 471.5 | 498.9 | 469.2 | 460.5 | 256.1 | 255.7 | 293.8
1699 | 1564 | 241.4 | 471 | 498.7 | 468.6 | 459.9 | 255.8 | 255.4 | 293.4
1700 | 1565 | 241.1 | 470.6 | 498.2 | 467.9 | 459.1 | 255.4 | 255 | 293
1701 | 1566 | 240.7 | 469.7 | 497.7 | 467.7 | 458.5 | 255.1 | 254.7 | 292.6
1702 | 1567 | 240.3 | 468.7 | 497.3 | 467.1 | 457.8 | 254.8 | 254.4 | 292.2
1703 | 1568 | 239.9 | 467.2 | 496.7 | 466.4 | 456.9 | 254.5 | 254 | 291.9
1704 | 1569 | 239.5 | 465.7 | 496 | 465.8 | 456 | 254.2 | 253.7 | 291.5
1705 | 1570 | 239.2 | 464.6 | 495.1 | 465.1 | 455.2 | 253.9 | 253.4 | 291
1706 | 1571 | 238.9 | 463.9 | 494.3 | 464.4 | 454.3 | 253.5 | 253 | 290.6
1707 | 1572 | 238.5 | 463.6 | 493.5 | 463.9 | 453.2 | 253.2 | 252.7 | 290.2
1708 | 1573 | 238.1 | 463.5 | 492.8 | 463.4 | 452.3 | 252.9 | 252.4 | 289.8
1709 | 1574 | 237.8 | 462.9 | 492.4 | 462.9 | 451.2 | 252.7 | 252.1 | 289.4
1710 | 1575 | 237.5 | 461.1 | 491.7 | 462 | 450 | 252.4 | 251.8 | 289.1
1711 | 1576 | 237.1 | 459.2 | 490.7 | 461.3 | 449 | 252.1 | 251.4 | 288.6
1712 | 1577 | 236.8 | 457.3 | 490 | 460.8 | 448.1 | 251.8 | 251.1 | 288.2
1713 | 1578 | 236.5 | 455.6 | 489.2 | 460.1 | 447.2 | 251.5 | 250.8 | 287.8
1714 | 1579 | 236.1 | 454.2 | 488.1 | 458.9 | 446.3 | 251.2 | 250.4 | 287.4
1715 | 1580 | 235.7 | 452.8 | 487.5 | 458.1 | 445.8 | 250.9 | 250 | 287
1716 | 1581 | 235.3 | 451.3 | 487.1 | 457.8 | 445.2 | 250.6 | 249.8 | 286.7
1717 | 1582 | 234.9 | 449.7 | 486.6 | 456.9 | 444.5 | 250.3 | 249.5 | 286.3
1718 | 1583 | 234.6 | 448.4 | 485.9 | 456.5 | 443.9 | 250 | 249.2 | 285.9
1719 | 1584 | 234.3 | 447.4 | 485.2 | 456 | 443.1 | 249.7 | 248.9 | 285.4
1720 | 1585 | 233.9 | 446.6 | 484.3 | 455.6 | 442.1 | 249.4 | 248.6 | 285
1721 | 1586 | 233.6 | 446.3 | 483.6 | 455.5 | 441.2 | 249.1 | 248.3 | 284.6
1722 | 1587 | 233.4 | 446 | 482.7 | 455.4 | 440.5 | 248.8 | 247.9 | 284.2
1723 | 1588 | 233.1 | 445.4 | 481.8 | 455 | 439.6 | 248.5 | 247.5 | 283.7
1724 | 1589 | 232.8 | 444.5 | 480.9 | 454.6 | 438.7 | 248.1 | 247.1 | 283.4
1725 | 1590 | 232.5 | 443.7 | 479.7 | 454.2 | 437.9 | 247.8 | 246.8 | 283.1
1726 | 1591 | 232.1 | 443.1 | 478.6 | 453.6 | 437.1 | 247.5 | 246.4 | 282.7
1727 | 1592 | 231.7 | 442.2 | 477.9 | 452.9 | 436.1 | 247.2 | 246.1 | 282.2
1728 | 1593 | 231.4 | 441 | 477.1 | 452 | 434.9 | 246.9 | 245.7 | 281.9
1729 | 1594 | 231 | 439.8 | 476.2 | 451.3 | 434 | 246.6 | 245.3 | 281.6
1730 | 1595 | 230.6 | 438.4 | 475.4 | 450.2 | 433 | 246.3 | 245 | 281.2
1731 | 1596 | 230.4 | 436.7 | 474.7 | 449.1 | 431.8 | 246 | 244.7 | 280.8
1732 | 1597 | 230.1 | 435.5 | 473.9 | 448.3 | 430.6 | 245.7 | 244.3 | 280.5
1733 | 1598 | 229.7 | 434.4 | 472.9 | 447.4 | 429.5 | 245.4 | 243.9 | 280.1
1734 | 1599 | 229.4 | 433.2 | 471.8 | 446.3 | 428.5 | 245.1 | 243.5 | 279.8
1735 | 1600 | 229 | 431.7 | 471 | 444.9 | 427.3 | 244.8 | 243.2 | 279.4
1736 | 1601 | 228.6 | 430 | 470.2 | 443.5 | 426.3 | 244.5 | 242.9 | 279.1
1737 | 1602 | 228.2 | 428.3 | 469.2 | 442.4 | 425.3 | 244.2 | 242.7 | 278.7
1738 | 1603 | 227.9 | 426.7 | 468.6 | 441.4 | 424.2 | 243.9 | 242.3 | 278.5
1739 | 1604 | 227.6 | 425.3 | 468.4 | 440.7 | 423.4 | 243.7 | 241.9 | 278.1
1740 | 1605 | 227.3 | 423.7 | 468.1 | 440.4 | 422.6 | 243.4 | 241.7 | 277.8
1741 | 1606 | 226.9 | 422.1 | 467.7 | 440.2 | 421.9 | 243.2 | 241.4 | 277.4
1742 | 1607 | 226.6 | 420.9 | 466.6 | 439.8 | 421.1 | 242.9 | 241.1 | 277
1743 | 1608 | 226.2 | 419.9 | 465.9 | 439.5 | 420.3 | 242.6 | 240.8 | 276.7
1744 | 1609 | 225.8 | 418.8 | 465.4 | 439 | 419.4 | 242.3 | 240.5 | 276.3
1745 | 1610 | 225.5 | 417.5 | 464.8 | 437.9 | 418.4 | 242 | 240.1 | 275.9
1746 | 1611 | 225.2 | 416.3 | 464.1 | 437.2 | 417.5 | 241.7 | 239.8 | 275.6
1747 | 1612 | 224.9 | 415 | 463.2 | 437 | 416.7 | 241.4 | 239.5 | 275.2
1748 | 1613 | 224.6 | 413.9 | 462.2 | 436.3 | 415.9 | 241.1 | 239.2 | 274.9
1749 | 1614 | 224.2 | 412.8 | 461.5 | 435.2 | 414.7 | 240.9 | 239 | 274.5
1750 | 1615 | 223.8 | 411.6 | 460.5 | 434.2 | 413.6 | 240.6 | 238.8 | 274.1
1751 | 1616 | 223.5 | 410.3 | 459.5 | 433.3 | 412.2 | 240.3 | 238.5 | 273.8
1752 | 1617 | 223.3 | 409.1 | 459.1 | 431.9 | 411 | 240 | 238.3 | 273.5
1753 | 1618 | 223 | 408 | 458.4 | 430.6 | 410.1 | 239.8 | 238 | 273.1
1754 | 1619 | 222.6 | 407 | 457.7 | 429.8 | 409.4 | 239.5 | 237.7 | 272.7
1755 | 1620 | 222.4 | 405.8 | 457 | 429 | 408.6 | 239.2 | 237.5 | 272.3
1756 | 1621 | 222.2 | 404.7 | 456.7 | 428.2 | 408 | 238.9 | 237.3 | 271.9
1757 | 1622 | 221.8 | 403.7 | 456.2 | 427.4 | 407.5 | 238.7 | 237.1 | 271.6
1758 | 1623 | 221.4 | 402.7 | 455.7 | 426.5 | 406.6 | 238.4 | 236.7 | 271.3
1759 | 1624 | 221.1 | 401.6 | 455.2 | 425.7 | 405.9 | 238.1 | 236.3 | 271
1760 | 1625 | 220.8 | 400.4 | 454.7 | 425.4 | 405.3 | 237.8 | 236 | 270.8
1761 | 1626 | 220.5 | 399.2 | 454.1 | 424.8 | 404.8 | 237.6 | 235.7 | 270.5
1762 | 1627 | 220.2 | 398.1 | 453.7 | 424.1 | 404.2 | 237.3 | 235.4 | 270.1
1763 | 1628 | 219.8 | 396.9 | 452.7 | 423.3 | 403.4 | 237 | 235.2 | 269.8
1764 | 1629 | 219.4 | 396 | 451.8 | 422.6 | 402.8 | 236.7 | 234.9 | 269.5
1765 | 1630 | 219.1 | 394.9 | 450.9 | 421.5 | 402.3 | 236.5 | 234.5 | 269.1
1766 | 1631 | 218.9 | 393.8 | 450.3 | 420.3 | 401.8 | 236.2 | 234.2 | 268.8
1767 | 1632 | 218.5 | 392.7 | 449.7 | 419.4 | 401.3 | 235.9 | 233.9 | 268.5
1768 | 1633 | 218.1 | 391.6 | 449.2 | 419 | 400.8 | 235.7 | 233.6 | 268.2
1769 | 1634 | 217.8 | 390.4 | 448.8 | 418.7 | 400.1 | 235.4 | 233.3 | 267.8
1770 | 1635 | 217.4 | 389.2 | 448.1 | 417.9 | 399.3 | 235.1 | 232.9 | 267.4
1771 | 1636 | 217 | 388 | 447 | 417.4 | 398.5 | 234.8 | 232.6 | 267.1
1772 | 1637 | 216.8 | 387 | 446.1 | 416.6 | 397.7 | 234.6 | 232.3 | 266.8
1773 | 1638 | 216.5 | 386 | 445.2 | 416.2 | 396.9 | 234.3 | 231.9 | 266.4
1774 | 1639 | 216.1 | 385.3 | 443.7 | 415.7 | 396.8 | 234.1 | 231.6 | 266.1
1775 | 1640 | 215.8 | 384.3 | 442.9 | 414.9 | 396.2 | 233.8 | 231.3 | 265.8
1776 | 1641 | 215.5 | 383.3 | 442.4 | 414.5 | 395.4 | 233.5 | 230.9 | 265.5
1777 | 1642 | 215.2 | 382.1 | 441.6 | 414 | 394.8 | 233.2 | 230.6 | 265.1
1778 | 1643 | 214.9 | 381.1 | 440.6 | 413.1 | 394.5 | 233 | 230.3 | 264.7
1779 | 1644 | 214.5 | 380 | 439.7 | 412.1 | 394.2 | 232.7 | 230 | 264.4
1780 | 1645 | 214.2 | 378.8 | 438.7 | 411.3 | 393.7 | 232.4 | 229.7 | 264
1781 | 1646 | 213.9 | 377.8 | 437.8 | 410.5 | 393.2 | 232.1 | 229.4 | 263.7
1782 | 1647 | 213.7 | 376.9 | 436.8 | 409.6 | 392.8 | 231.8 | 229 | 263.4
1783 | 1648 | 213.4 | 376 | 436 | 408.7 | 392.5 | 231.5 | 228.8 | 263
1784 | 1649 | 213.2 | 375.1 | 435.2 | 407.7 | 392 | 231.1 | 228.5 | 262.7
1785 | 1650 | 212.9 | 374.3 | 434.2 | 407 | 391.6 | 230.9 | 228.2 | 262.4
1786 | 1651 | 212.5 | 373.5 | 433.5 | 406.1 | 391.1 | 230.6 | 227.8 | 262
1787 | 1652 | 212.2 | 372.5 | 432.7 | 405.4 | 390.5 | 230.3 | 227.5 | 261.6
1788 | 1653 | 211.9 | 371.4 | 432.5 | 404.3 | 389.5 | 229.9 | 227.3 | 261.4
1789 | 1654 | 211.6 | 370.4 | 431.5 | 403.6 | 388.9 | 229.5 | 227 | 261.2
1790 | 1655 | 211.3 | 369.5 | 430.5 | 402.9 | 388.3 | 229.2 | 226.6 | 260.9
1791 | 1656 | 210.9 | 368.4 | 429.8 | 402 | 387.6 | 228.9 | 226.3 | 260.6
1792 | 1657 | 210.5 | 367.5 | 428.9 | 401.2 | 386.9 | 228.6 | 225.9 | 260.4
1793 | 1658 | 210.2 | 366.5 | 427.9 | 400.6 | 385.9 | 228.3 | 225.7 | 260.1
1794 | 1659 | 209.9 | 365.6 | 426.9 | 399.9 | 384.9 | 228 | 225.4 | 259.8
1795 | 1660 | 209.6 | 364.6 | 426 | 399.3 | 384.2 | 227.7 | 225.2 | 259.4
1796 | 1661 | 209.4 | 363.8 | 425 | 398.8 | 383.3 | 227.3 | 225.1 | 259.1
1797 | 1662 | 209.1 | 362.8 | 424.1 | 398.3 | 382.3 | 227 | 224.9 | 258.8
1798 | 1663 | 208.8 | 361.8 | 423.2 | 397.8 | 381.4 | 226.6 | 224.8 | 258.6
1799 | 1664 | 208.5 | 360.9 | 422.4 | 397.8 | 380.4 | 226.3 | 224.4 | 258.2
1800 | 1665 | 208.4 | 359.9 | 421.4 | 397.7 | 379.2 | 226 | 224.1 | 257.9
1801 | 1666 | 208.2 | 358.9 | 420.3 | 397.8 | 378 | 225.7 | 223.9 | 257.6
1802 | 1667 | 208 | 358 | 419.3 | 397.6 | 376.7 | 225.4 | 223.7 | 257.3
1803 | 1668 | 207.8 | 357 | 418.4 | 397.1 | 375.5 | 225.1 | 223.3 | 256.9
1804 | 1669 | 207.6 | 356.1 | 417.2 | 396.4 | 374.4 | 224.8 | 223 | 256.5
1805 | 1670 | 207.3 | 355.2 | 416 | 396.1 | 373.4 | 224.5 | 222.8 | 256.2
1806 | 1671 | 206.9 | 354.4 | 415 | 395.5 | 372.7 | 224.2 | 222.5 | 255.9
1807 | 1672 | 206.6 | 353.6 | 414.1 | 395.1 | 371.9 | 223.9 | 222.2 | 255.5
1808 | 1673 | 206.4 | 352.7 | 412.9 | 394.7 | 370.9 | 223.6 | 221.9 | 255.2
1809 | 1674 | 206.1 | 351.9 | 411.4 | 394.4 | 370 | 223.2 | 221.5 | 254.8
1810 | 1675 | 205.8 | 351.1 | 410.2 | 394 | 369.4 | 222.9 | 221.2 | 254.5
1811 | 1676 | 205.5 | 350.3 | 409.3 | 393 | 369 | 222.6 | 221 | 254.3
1812 | 1677 | 205.2 | 349.5 | 408.5 | 391.9 | 368.6 | 222.3 | 220.7 | 254
1813 | 1678 | 204.9 | 348.8 | 407.4 | 390.8 | 368.3 | 222 | 220.3 | 253.8
1814 | 1679 | 204.7 | 348 | 406.4 | 389.9 | 367.8 | 221.7 | 219.9 | 253.5
1815 | 1680 | 204.4 | 347.2 | 405.5 | 388.8 | 367.4 | 221.4 | 219.5 | 253.2
1816 | 1681 | 204.1 | 346.4 | 404.6 | 388 | 366.8 | 221.2 | 219.1 | 252.9
1817 | 1682 | 203.8 | 345.7 | 403.5 | 387.2 | 366.3 | 220.9 | 218.7 | 252.6
1818 | 1683 | 203.4 | 344.8 | 402.5 | 386.5 | 365.9 | 220.6 | 218.4 | 252.4
1819 | 1684 | 203.1 | 344 | 401.6 | 385.7 | 365.5 | 220.2 | 218.1 | 252
1820 | 1685 | 202.8 | 343.2 | 400.4 | 384.7 | 365.2 | 219.9 | 217.8 | 251.6
1821 | 1686 | 202.5 | 342.5 | 399.5 | 383.8 | 364.8 | 219.6 | 217.6 | 251.3
1822 | 1687 | 202.3 | 341.7 | 398.4 | 383.1 | 364.2 | 219.3 | 217.3 | 251
1823 | 1688 | 202 | 340.9 | 397.2 | 382.3 | 363.5 | 219.1 | 217 | 250.8
1824 | 1689 | 201.7 | 340.1 | 396.5 | 381.6 | 362.7 | 218.8 | 216.7 | 250.5
1825 | 1690 | 201.4 | 339.3 | 395.8 | 380.8 | 361.7 | 218.5 | 216.4 | 250.3
1826 | 1691 | 201.1 | 338.3 | 394.8 | 380.1 | 360.6 | 218.2 | 216 | 250
1827 | 1692 | 200.8 | 337.5 | 393.8 | 379.5 | 359.6 | 218 | 215.7 | 249.9
1828 | 1693 | 200.5 | 336.6 | 393.3 | 379.2 | 358.6 | 217.7 | 215.5 | 249.6
1829 | 1694 | 200.2 | 335.6 | 392.5 | 378.7 | 357.4 | 217.4 | 215.3 | 249.2
1830 | 1695 | 200 | 334.6 | 391 | 377.7 | 356.2 | 217.2 | 215.1 | 248.9
1831 | 1696 | 199.8 | 333.8 | 389.3 | 376.6 | 354.9 | 216.9 | 214.9 | 248.6
1832 | 1697 | 199.5 | 332.8 | 388.5 | 375.2 | 353.9 | 216.6 | 214.6 | 248.4
1833 | 1698 | 199.3 | 331.8 | 387.5 | 373.8 | 352.9 | 216.3 | 214.3 | 248.2
1834 | 1699 | 199 | 330.9 | 386.2 | 372.9 | 352.1 | 216.1 | 214 | 247.8
1835 | 1700 | 198.7 | 330 | 385.4 | 371.8 | 351.1 | 215.8 | 213.7 | 247.5
1836 | 1701 | 198.4 | 329 | 384.4 | 370.6 | 349.9 | 215.5 | 213.4 | 247.2
1837 | 1702 | 198.1 | 328.1 | 383.3 | 369.5 | 348.6 | 215.2 | 213.1 | 247
1838 | 1703 | 197.8 | 327.3 | 382.5 | 368.7 | 347.6 | 214.9 | 212.9 | 246.8
1839 | 1704 | 197.5 | 326.3 | 381.5 | 368 | 346.4 | 214.6 | 212.7 | 246.6
1840 | 1705 | 197.2 | 325.3 | 380.4 | 367 | 344.9 | 214.3 | 212.6 | 246.3
1841 | 1706 | 197 | 324.3 | 379.2 | 366.1 | 343.3 | 214.1 | 212.4 | 246
1842 | 1707 | 196.7 | 323.3 | 378.1 | 365.2 | 341.7 | 213.8 | 212.2 | 245.7
1843 | 1708 | 196.4 | 322.4 | 377.2 | 364.2 | 340.4 | 213.5 | 211.9 | 245.3
1844 | 1709 | 196.2 | 321.5 | 376.5 | 363.2 | 339.5 | 213.2 | 211.5 | 245
1845 | 1710 | 195.9 | 320.6 | 375.6 | 362.6 | 338.8 | 213 | 211.1 | 244.7
1846 | 1711 | 195.6 | 319.7 | 374.8 | 362 | 338.1 | 212.7 | 210.8 | 244.4
1847 | 1712 | 195.4 | 318.8 | 374.1 | 361.6 | 337.6 | 212.4 | 210.5 | 244.2
1848 | 1713 | 195.2 | 318 | 373.1 | 361.3 | 337.6 | 212.1 | 210.2 | 243.9
1849 | 1714 | 195 | 317.1 | 372.1 | 360.6 | 337.5 | 211.8 | 210 | 243.6
1850 | 1715 | 194.8 | 316.2 | 371.2 | 360 | 337.1 | 211.5 | 209.6 | 243.3
1851 | 1716 | 194.6 | 315.4 | 370.4 | 359.4 | 336.8 | 211.2 | 209.2 | 243.1
1852 | 1717 | 194.3 | 314.6 | 369.4 | 359.3 | 336.5 | 210.9 | 208.9 | 242.8
1853 | 1718 | 193.9 | 313.8 | 368.5 | 359 | 336 | 210.6 | 208.6 | 242.5
1854 | 1719 | 193.6 | 313 | 367.6 | 358.1 | 335.5 | 210.3 | 208.4 | 242.3
1855 | 1720 | 193.3 | 312.3 | 366.5 | 357 | 335.2 | 210 | 208.2 | 242
1856 | 1721 | 193.1 | 311.6 | 365.6 | 356.1 | 334.9 | 209.7 | 208 | 241.8
1857 | 1722 | 192.9 | 310.8 | 364.9 | 355.1 | 334.6 | 209.4 | 207.8 | 241.6
1858 | 1723 | 192.6 | 310.1 | 363.9 | 353.9 | 334.4 | 209.1 | 207.5 | 241.3
1859 | 1724 | 192.2 | 309.4 | 362.9 | 352.7 | 334.3 | 208.8 | 207.2 | 241
1860 | 1725 | 192 | 308.7 | 362 | 351.6 | 334 | 208.6 | 206.9 | 240.8
1861 | 1726 | 191.7 | 308 | 361.1 | 350.5 | 333.7 | 208.3 | 206.7 | 240.5
1862 | 1727 | 191.4 | 307.4 | 360.1 | 349.8 | 333.3 | 208 | 206.4 | 240.2
1863 | 1728 | 191.1 | 306.6 | 359.1 | 348.8 | 332.6 | 207.8 | 206.2 | 240
1864 | 1729 | 190.8 | 305.9 | 358.3 | 348 | 331.6 | 207.5 | 205.9 | 239.7
1865 | 1730 | 190.5 | 305.1 | 357.4 | 347.2 | 331 | 207.2 | 205.6 | 239.3
1866 | 1731 | 190.2 | 304.4 | 356.4 | 346.4 | 330.6 | 206.9 | 205.3 | 239
1867 | 1732 | 189.9 | 303.7 | 355.4 | 345.7 | 330.3 | 206.6 | 205.1 | 238.8
1868 | 1733 | 189.6 | 302.9 | 354.5 | 345.1 | 329.8 | 206.3 | 204.9 | 238.5
1869 | 1734 | 189.2 | 302.1 | 353.6 | 344.5 | 329.6 | 206 | 204.6 | 238.2
1870 | 1735 | 188.9 | 301.4 | 352.5 | 343.8 | 329.1 | 205.7 | 204.3 | 238
1871 | 1736 | 188.6 | 300.5 | 351.5 | 343.2 | 328.6 | 205.4 | 204.1 | 237.7
1872 | 1737 | 188.3 | 299.7 | 350.7 | 342.3 | 327.9 | 205.1 | 203.9 | 237.3
1873 | 1738 | 188.1 | 298.9 | 349.6 | 341.9 | 326.9 | 204.8 | 203.7 | 237
1874 | 1739 | 187.9 | 298.1 | 348.7 | 341.6 | 325.9 | 204.5 | 203.5 | 236.8
1875 | 1740 | 187.7 | 297.2 | 348 | 340.9 | 324.9 | 204.2 | 203.3 | 236.5
1876 | 1741 | 187.4 | 296.4 | 347 | 340.7 | 324.2 | 203.9 | 202.9 | 236.3
1877 | 1742 | 187.2 | 295.7 | 346 | 340.1 | 323.6 | 203.6 | 202.7 | 236
1878 | 1743 | 187 | 294.9 | 344.7 | 339.7 | 322.9 | 203.3 | 202.3 | 235.8
1879 | 1744 | 186.8 | 294.1 | 343.8 | 339.3 | 322.1 | 203 | 202 | 235.4
1880 | 1745 | 186.5 | 293.4 | 342.9 | 338.9 | 321.5 | 202.7 | 201.8 | 235
1881 | 1746 | 186.2 | 292.6 | 342 | 338.3 | 320.9 | 202.4 | 201.6 | 234.7
1882 | 1747 | 186 | 291.9 | 341 | 337.6 | 320.2 | 202.2 | 201.3 | 234.5
1883 | 1748 | 185.7 | 291.2 | 339.9 | 337 | 319.7 | 201.9 | 200.9 | 234.2
1884 | 1749 | 185.5 | 290.5 | 339 | 336.2 | 319.1 | 201.6 | 200.6 | 233.9
1885 | 1750 | 185.3 | 289.7 | 338.1 | 335.5 | 318.4 | 201.3 | 200.3 | 233.6
1886 | 1751 | 185.1 | 289 | 337.2 | 334.8 | 317.5 | 201 | 200 | 233.3
1887 | 1752 | 184.8 | 288.3 | 336.1 | 333.9 | 316.8 | 200.7 | 199.7 | 233.2
1888 | 1753 | 184.6 | 287.5 | 335.1 | 332.9 | 316.2 | 200.4 | 199.3 | 233
1889 | 1754 | 184.4 | 286.7 | 334.3 | 331.7 | 315.5 | 200.1 | 199 | 232.9
1890 | 1755 | 184.2 | 286 | 333.2 | 330.4 | 315.1 | 199.8 | 198.8 | 232.6
1891 | 1756 | 184 | 285.3 | 332.6 | 329.3 | 314.5 | 199.5 | 198.5 | 232.3
1892 | 1757 | 183.8 | 284.6 | 331.8 | 328.2 | 313.7 | 199.2 | 198.2 | 232.1
1893 | 1758 | 183.6 | 283.9 | 330.6 | 326.9 | 312.7 | 198.9 | 198 | 231.9
1894 | 1759 | 183.4 | 283.2 | 330 | 326.1 | 311.7 | 198.6 | 197.8 | 231.6
1895 | 1760 | 183.1 | 282.5 | 329.5 | 325.5 | 310.5 | 198.3 | 197.6 | 231.3
1896 | 1761 | 182.8 | 281.7 | 328.8 | 324.8 | 309.1 | 198.1 | 197.3 | 231.1
1897 | 1762 | 182.6 | 281 | 327.7 | 324 | 307.5 | 197.8 | 197 | 230.7
1898 | 1763 | 182.3 | 280.3 | 326.6 | 323.2 | 305.8 | 197.6 | 196.8 | 230.4
1899 | 1764 | 182.1 | 279.5 | 325.5 | 322.5 | 304.2 | 197.3 | 196.6 | 230.1
1900 | 1765 | 181.8 | 278.8 | 324.8 | 321.8 | 302.8 | 197.1 | 196.3 | 229.9
1901 | 1766 | 181.5 | 278.2 | 323.5 | 320.7 | 301.7 | 196.8 | 196 | 229.6
1902 | 1767 | 181.2 | 277.5 | 322.8 | 319.5 | 300.6 | 196.5 | 195.7 | 229.4
1903 | 1768 | 181 | 276.7 | 321.9 | 318.6 | 299.7 | 196.3 | 195.4 | 229.1
1904 | 1769 | 180.7 | 276.2 | 320.5 | 317.5 | 299.3 | 196.1 | 195.1 | 228.7
1905 | 1770 | 180.5 | 275.4 | 319.5 | 316.2 | 298.6 | 195.8 | 194.8 | 228.4
1906 | 1771 | 180.2 | 275 | 318 | 315.4 | 298.7 | 195.6 | 194.5 | 228.1
1907 | 1772 | 179.9 | 274.1 | 317.6 | 314.3 | 297.8 | 195.3 | 194.2 | 227.8
1908 | 1773 | 179.7 | 273.3 | 316.7 | 313.1 | 297.1 | 195 | 193.9 | 227.5
1909 | 1774 | 179.6 | 272.6 | 315.8 | 311.8 | 296.5 | 194.7 | 193.7 | 227.3
1910 | 1775 | 179.3 | 271.8 | 314.8 | 310.8 | 295.8 | 194.4 | 193.5 | 227.2
1911 | 1776 | 179.1 | 271.1 | 313.9 | 310 | 295.2 | 194.2 | 193.3 | 226.8
1912 | 1777 | 178.9 | 270.3 | 313 | 309.3 | 294.7 | 193.9 | 193 | 226.6
1913 | 1778 | 178.6 | 269.8 | 311.5 | 308.9 | 294.7 | 193.7 | 192.7 | 226.4
1914 | 1779 | 178.4 | 268.7 | 311.1 | 308 | 293.5 | 193.3 | 192.4 | 226.2
1915 | 1780 | 178.2 | 268 | 310.1 | 307.1 | 293.1 | 193 | 192.1 | 225.9
1916 | 1781 | 177.9 | 268.2 | 307.2 | 306.9 | 294.5 | 192.9 | 191.8 | 225.5
1917 | 1782 | 177.8 | 267.4 | 306.5 | 306 | 293.8 | 192.6 | 191.5 | 225.2
1918 | 1783 | 177.6 | 266.7 | 305.3 | 305.2 | 293.4 | 192.4 | 191.2 | 225
1919 | 1784 | 177.4 | 266 | 304.5 | 304.4 | 292.7 | 192.1 | 191 | 224.7
1920 | 1785 | 177.2 | 265.2 | 303.5 | 303.5 | 291.9 | 191.9 | 190.7 | 224.4
1921 | 1786 | 177 | 264.5 | 302.7 | 302.6 | 291.2 | 191.6 | 190.4 | 224.2
1922 | 1787 | 176.7 | 263.9 | 301.7 | 301.8 | 290.7 | 191.3 | 190.1 | 224
1923 | 1788 | 176.5 | 263.2 | 300.9 | 301 | 289.8 | 191.1 | 189.8 | 223.8
1924 | 1789 | 176.3 | 262.4 | 300.1 | 300 | 288.8 | 190.8 | 189.6 | 223.6
1925 | 1790 | 176.1 | 261.7 | 299.2 | 299.2 | 287.8 | 190.5 | 189.3 | 223.4
1926 | 1791 | 175.9 | 261 | 298.3 | 298.2 | 286.4 | 190.2 | 189.1 | 223.1
1927 | 1792 | 175.6 | 260.2 | 297.6 | 297.3 | 284.9 | 190 | 188.9 | 222.8
1928 | 1793 | 175.3 | 259.4 | 296.8 | 296.1 | 283.3 | 189.7 | 188.7 | 222.5
1929 | 1794 | 175.1 | 258.7 | 295.7 | 295.2 | 281.9 | 189.4 | 188.5 | 222.2
1930 | 1795 | 175 | 258 | 294.8 | 294.9 | 280.6 | 189.1 | 188.2 | 222
1931 | 1796 | 174.8 | 257.2 | 294.2 | 294.5 | 279.3 | 188.8 | 187.9 | 221.8
1932 | 1797 | 174.5 | 256.6 | 293.3 | 293.7 | 278.5 | 188.6 | 187.7 | 221.5
1933 | 1798 | 174.4 | 255.8 | 292.4 | 292.9 | 277.8 | 188.3 | 187.3 | 221.2
1934 | 1799 | 174.2 | 255 | 291.8 | 292.1 | 277 | 188 | 187.1 | 221
1935 | 1800 | 174 | 254.2 | 290.9 | 291 | 276.4 | 187.7 | 186.9 | 220.8
1936 | 1801 | 173.7 | 253.5 | 289.8 | 290.2 | 275.8 | 187.5 | 186.7 | 220.5
1937 | 1802 | 173.4 | 252.7 | 289 | 289.2 | 275 | 187.2 | 186.5 | 220.2
1938 | 1803 | 173.2 | 251.9 | 288.4 | 288.2 | 274 | 186.9 | 186.3 | 219.9
1939 | 1804 | 172.9 | 251.2 | 287.3 | 287.3 | 273.3 | 186.7 | 186 | 219.6
1940 | 1805 | 172.7 | 250.5 | 286.2 | 286.8 | 272.5 | 186.4 | 185.7 | 219.3
1941 | 1806 | 172.4 | 249.8 | 285.2 | 285.8 | 271.6 | 186.1 | 185.6 | 219.1
1942 | 1807 | 172.2 | 249.1 | 284.4 | 284.7 | 270.6 | 185.8 | 185.4 | 218.9
1943 | 1808 | 171.9 | 248.5 | 283.4 | 283.8 | 269.6 | 185.6 | 185.3 | 218.7
1944 | 1809 | 171.8 | 247.8 | 282.4 | 282.8 | 268.6 | 185.3 | 185.1 | 218.4
1945 | 1810 | 171.6 | 247 | 281.7 | 281.8 | 267.6 | 185 | 184.9 | 218.2
1946 | 1811 | 171.4 | 246.4 | 280.5 | 281.5 | 266.8 | 184.7 | 184.7 | 217.9
1947 | 1812 | 171.2 | 245.7 | 279.5 | 281.2 | 266 | 184.4 | 184.4 | 217.6
1948 | 1813 | 171 | 244.9 | 278.9 | 280.7 | 264.9 | 184.1 | 184.1 | 217.4
1949 | 1814 | 170.7 | 244.2 | 278 | 280.2 | 263.9 | 183.9 | 183.8 | 217.2
1950 | 1815 | 170.5 | 243.7 | 276.9 | 279.5 | 263 | 183.6 | 183.6 | 216.9
1951 | 1816 | 170.3 | 243 | 276.1 | 278.6 | 262 | 183.3 | 183.3 | 216.7
1952 | 1817 | 170.1 | 242.2 | 275.5 | 277.7 | 260.9 | 183 | 183 | 216.4
1953 | 1818 | 169.8 | 241.7 | 274.6 | 276.9 | 260.3 | 182.7 | 182.8 | 216
1954 | 1819 | 169.7 | 241.1 | 273.9 | 276.2 | 259.6 | 182.5 | 182.5 | 215.8
1955 | 1820 | 169.5 | 240.4 | 273.4 | 275.5 | 258.8 | 182.2 | 182.2 | 215.6
1956 | 1821 | 169.3 | 239.8 | 272.6 | 274.6 | 258.1 | 182 | 182 | 215.4
1957 | 1822 | 169.1 | 239.2 | 271.9 | 273.8 | 257.2 | 181.7 | 181.8 | 215.2
1958 | 1823 | 168.9 | 238.6 | 271.3 | 273.1 | 256 | 181.5 | 181.5 | 215
1959 | 1824 | 168.7 | 237.8 | 270.7 | 271.8 | 254.6 | 181.2 | 181.2 | 214.7
1960 | 1825 | 168.4 | 237.3 | 269.8 | 270.9 | 253.4 | 180.9 | 181 | 214.4
1961 | 1826 | 168.2 | 236.6 | 268.9 | 269.9 | 252.2 | 180.7 | 180.8 | 214.1
1962 | 1827 | 168 | 235.9 | 268.1 | 269.1 | 251 | 180.4 | 180.6 | 213.9
1963 | 1828 | 167.8 | 235.2 | 267.2 | 268.4 | 250.1 | 180.1 | 180.3 | 213.7
1964 | 1829 | 167.5 | 234.6 | 266.2 | 267.6 | 249.3 | 179.9 | 180.2 | 213.4
1965 | 1830 | 167.3 | 233.9 | 265.4 | 267.1 | 248.3 | 179.6 | 180 | 213.2
1966 | 1831 | 167.1 | 233.1 | 264.9 | 266.3 | 247 | 179.3 | 179.8 | 212.9
1967 | 1832 | 166.9 | 232.6 | 263.8 | 265.5 | 246 | 179 | 179.6 | 212.6
1968 | 1833 | 166.7 | 232 | 262.8 | 264.6 | 244.9 | 178.7 | 179.3 | 212.3
1969 | 1834 | 166.5 | 231.3 | 262.3 | 263.7 | 243.7 | 178.4 | 179 | 212
1970 | 1835 | 166.3 | 230.8 | 261.2 | 262.7 | 242.5 | 178.1 | 178.8 | 211.9
1971 | 1836 | 166.2 | 230.3 | 260.2 | 261.7 | 241.5 | 177.8 | 178.6 | 211.7
1972 | 1837 | 166 | 229.7 | 259.4 | 260.9 | 240.5 | 177.5 | 178.5 | 211.4
1973 | 1838 | 165.8 | 229.1 | 259 | 259.9 | 239.3 | 177.2 | 178.2 | 211.2
1974 | 1839 | 165.5 | 228.6 | 257.9 | 259.2 | 238.3 | 177 | 177.9 | 210.9
1975 | 1840 | 165.3 | 227.9 | 257.1 | 258.3 | 236.8 | 176.7 | 177.5 | 210.6
1976 | 1841 | 165.1 | 227.3 | 256.3 | 257.5 | 235.2 | 176.4 | 177.2 | 210.4
1977 | 1842 | 164.9 | 226.7 | 255.4 | 257 | 233.4 | 176.2 | 177 | 210.3
1978 | 1843 | 164.6 | 226.1 | 254.4 | 256.4 | 231.5 | 175.9 | 176.8 | 210
1979 | 1844 | 164.4 | 225.6 | 253.6 | 255.6 | 230.1 | 175.7 | 176.6 | 209.7
1980 | 1845 | 164.2 | 224.9 | 253.1 | 254.6 | 228.9 | 175.4 | 176.5 | 209.5
1981 | 1846 | 164 | 224.4 | 252.2 | 253.7 | 228.2 | 175.1 | 176.4 | 209.3
1982 | 1847 | 163.8 | 223.9 | 251.4 | 252.8 | 227.4 | 174.9 | 176.2 | 209.1
1983 | 1848 | 163.6 | 223.3 | 250.7 | 251.8 | 226.7 | 174.6 | 176 | 209
1984 | 1849 | 163.4 | 222.8 | 249.9 | 250.7 | 226 | 174.3 | 175.7 | 208.8
1985 | 1850 | 163.2 | 222.4 | 248.8 | 249.6 | 225.6 | 174 | 175.5 | 208.6
1986 | 1851 | 163 | 221.8 | 248.1 | 248.5 | 225 | 173.8 | 175.3 | 208.4
1987 | 1852 | 162.8 | 221.3 | 247.4 | 247.6 | 224 | 173.5 | 175 | 208.1
1988 | 1853 | 162.6 | 220.9 | 246.2 | 246.7 | 223.3 | 173.2 | 174.7 | 207.9
1989 | 1854 | 162.4 | 220.4 | 245.3 | 245.8 | 222.7 | 172.9 | 174.4 | 207.7
1990 | 1855 | 162.2 | 219.9 | 244.5 | 245.2 | 222.1 | 172.6 | 174.1 | 207.5
1991 | 1856 | 162 | 219.4 | 243.5 | 244.5 | 221.7 | 172.3 | 173.8 | 207.3
1992 | 1857 | 161.8 | 219 | 242.5 | 243.8 | 221.6 | 172.1 | 173.5 | 207.1
1993 | 1858 | 161.6 | 218.5 | 241.8 | 243.2 | 221.4 | 171.8 | 173.3 | 206.9
1994 | 1859 | 161.4 | 217.9 | 241.4 | 242.5 | 221.1 | 171.5 | 173.1 | 206.8
1995 | 1860 | 161.2 | 217.5 | 240.4 | 242 | 221 | 171.2 | 172.8 | 206.6
1996 | 1861 | 161 | 217 | 239.7 | 241.3 | 220.8 | 171 | 172.5 | 206.4
1997 | 1862 | 160.7 | 216.4 | 239.5 | 240.9 | 220.4 | 170.7 | 172.3 | 206.2
1998 | 1863 | 160.5 | 215.8 | 238.8 | 240.4 | 220.2 | 170.4 | 172.1 | 205.9
1999 | 1864 | 160.4 | 215.4 | 237.8 | 239.7 | 219.9 | 170.2 | 171.9 | 205.7
2000 | 1865 | 160.2 | 214.8 | 237.1 | 238.9 | 219.5 | 169.9 | 171.6 | 205.4
2001 | 1866 | 159.9 | 214.1 | 236.4 | 237.8 | 218.9 | 169.6 | 171.3 | 205.3
2002 | 1867 | 159.7 | 213.6 | 235.4 | 237 | 218.4 | 169.4 | 171 | 204.9
2003 | 1868 | 159.5 | 213.1 | 234.3 | 236.1 | 217.9 | 169.1 | 170.8 | 204.7
2004 | 1869 | 159.3 | 212.5 | 233.7 | 235.2 | 217.2 | 168.8 | 170.6 | 204.6
2005 | 1870 | 159.1 | 212 | 233.1 | 234.7 | 216.6 | 168.6 | 170.4 | 204.3
2006 | 1871 | 159 | 211.5 | 232.5 | 234.1 | 216.1 | 168.4 | 170.2 | 204
2007 | 1872 | 158.8 | 211 | 231.8 | 233.5 | 215.2 | 168.1 | 170 | 203.8
2008 | 1873 | 158.6 | 210.3 | 231.5 | 233 | 214.1 | 167.9 | 169.7 | 203.7
2009 | 1874 | 158.4 | 209.8 | 230.8 | 232.5 | 213.4 | 167.6 | 169.4 | 203.4
2010 | 1875 | 158.2 | 209.3 | 229.9 | 231.5 | 212.8 | 167.4 | 169.1 | 203.3
2011 | 1876 | 158 | 208.7 | 229.2 | 230.6 | 212.3 | 167.2 | 168.8 | 203.1
2012 | 1877 | 157.8 | 208.2 | 228.4 | 229.6 | 211.7 | 166.9 | 168.5 | 203.1
2013 | 1878 | 157.6 | 207.7 | 227.4 | 228.7 | 211.2 | 166.7 | 168.2 | 202.9
2014 | 1879 | 157.4 | 207.1 | 226.7 | 228.2 | 210.4 | 166.4 | 168 | 202.7
2015 | 1880 | 157.2 | 206.5 | 226.2 | 227.6 | 209.5 | 166.2 | 167.7 | 202.5
2016 | 1881 | 157.1 | 206 | 225.2 | 226.6 | 208.9 | 165.9 | 167.5 | 202.3
2017 | 1882 | 156.9 | 205.4 | 224.4 | 225.7 | 208.4 | 165.7 | 167.2 | 202.1
2018 | 1883 | 156.6 | 205 | 223.3 | 225 | 208.1 | 165.5 | 166.9 | 201.8
2019 | 1884 | 156.4 | 204.2 | 222.8 | 224.1 | 207.2 | 165.2 | 166.7 | 201.7
2020 | 1885 | 156.2 | 203.8 | 221.7 | 223.6 | 206.5 | 164.9 | 166.7 | 201.4
2021 | 1886 | 156.1 | 203.2 | 221.1 | 223.2 | 205.8 | 164.7 | 166.6 | 201.1
2022 | 1887 | 155.9 | 202.6 | 220.7 | 222.9 | 204.8 | 164.4 | 166.4 | 200.8
2023 | 1888 | 155.7 | 202.1 | 219.7 | 222.4 | 204.1 | 164.1 | 166.2 | 200.5
2024 | 1889 | 155.5 | 201.6 | 218.9 | 221.7 | 203.3 | 163.9 | 165.9 | 200.3
2025 | 1890 | 155.3 | 201.1 | 218.1 | 220.9 | 202.3 | 163.6 | 165.7 | 200.1
2026 | 1891 | 155.1 | 200.6 | 217.2 | 220.3 | 201.3 | 163.4 | 165.5 | 199.8
2027 | 1892 | 155 | 200.2 | 216.3 | 219.5 | 200.3 | 163.1 | 165.3 | 199.6
2028 | 1893 | 154.9 | 199.7 | 215.6 | 218.7 | 199.2 | 162.9 | 165.2 | 199.4
2029 | 1894 | 154.8 | 199.2 | 215.2 | 217.9 | 197.9 | 162.6 | 165 | 199.1
2030 | 1895 | 154.7 | 198.7 | 214.3 | 217.2 | 196.8 | 162.3 | 164.8 | 198.8
2031 | 1896 | 154.5 | 198.3 | 213.5 | 216.5 | 195.9 | 162.1 | 164.5 | 198.6
2032 | 1897 | 154.3 | 197.8 | 212.9 | 215.7 | 195 | 161.9 | 164.2 | 198.5
2033 | 1898 | 154.2 | 197.4 | 212.1 | 214.6 | 194.4 | 161.6 | 163.9 | 198.3
2034 | 1899 | 154 | 197 | 211.4 | 213.8 | 194 | 161.4 | 163.5 | 198.1
2035 | 1900 | 153.8 | 196.6 | 210.8 | 213 | 193.6 | 161.1 | 163.2 | 197.7
2036 | 1901 | 153.6 | 196.1 | 210.4 | 212.1 | 193.2 | 160.8 | 162.9 | 197.5
2037 | 1902 | 153.4 | 195.7 | 209.7 | 211.8 | 193.2 | 160.6 | 162.6 | 197.3
2038 | 1903 | 153.2 | 195.3 | 208.9 | 211.2 | 193 | 160.3 | 162.3 | 197.1
2039 | 1904 | 153.1 | 194.9 | 208.6 | 210.8 | 192.6 | 160.1 | 162.1 | 196.8
2040 | 1905 | 152.9 | 194.4 | 208 | 210.5 | 192.2 | 159.8 | 161.8 | 196.5
2041 | 1906 | 152.7 | 194 | 207.2 | 210.3 | 192 | 159.5 | 161.5 | 196.2
2042 | 1907 | 152.6 | 193.5 | 206.5 | 209.7 | 191.7 | 159.3 | 161.2 | 195.9
2043 | 1908 | 152.4 | 193 | 206 | 208.9 | 191.3 | 159 | 161 | 195.7
2044 | 1909 | 152.2 | 192.6 | 205.3 | 208.5 | 191.2 | 158.7 | 160.7 | 195.6
2045 | 1910 | 152 | 192.2 | 204.6 | 207.9 | 191 | 158.5 | 160.4 | 195.4
2046 | 1911 | 151.8 | 191.6 | 204.1 | 207.2 | 190.8 | 158.2 | 160.2 | 195.3
2047 | 1912 | 151.6 | 191.1 | 203.6 | 206.7 | 190.6 | 158 | 159.9 | 195.1
2048 | 1913 | 151.4 | 190.7 | 202.8 | 206.3 | 190.4 | 157.7 | 159.6 | 194.9
2049 | 1914 | 151.2 | 190.3 | 202.2 | 205.7 | 190.1 | 157.4 | 159.3 | 194.8
2050 | 1915 | 151.1 | 189.7 | 201.7 | 205.3 | 189.8 | 157.2 | 159.1 | 194.7
2051 | 1916 | 150.9 | 189.3 | 200.8 | 205.1 | 189.7 | 156.9 | 158.9 | 194.6
2052 | 1917 | 150.7 | 188.9 | 200.1 | 204.7 | 189.5 | 156.6 | 158.6 | 194.4
2053 | 1918 | 150.6 | 188.4 | 199.5 | 204 | 189.1 | 156.3 | 158.4 | 194.3
2054 | 1919 | 150.4 | 187.9 | 198.9 | 203.7 | 188.6 | 156.1 | 158.2 | 194.1
2055 | 1920 | 150.2 | 187.6 | 198 | 203.5 | 188.2 | 155.8 | 158 | 193.9
2056 | 1921 | 150 | 187.2 | 197.3 | 203.2 | 187.6 | 155.5 | 157.7 | 193.7
2057 | 1922 | 149.8 | 186.6 | 196.8 | 202.8 | 186.9 | 155.3 | 157.4 | 193.4
2058 | 1923 | 149.6 | 186.3 | 196 | 202.5 | 186.6 | 155 | 157.1 | 193.2
2059 | 1924 | 149.4 | 186 | 195.4 | 201.9 | 186.2 | 154.8 | 156.8 | 193.1
2060 | 1925 | 149.2 | 185.5 | 194.8 | 201.2 | 185.7 | 154.5 | 156.7 | 192.8
2061 | 1926 | 149 | 185.1 | 194.2 | 200.3 | 185.2 | 154.3 | 156.5 | 192.6
2062 | 1927 | 148.8 | 184.8 | 193.3 | 199.5 | 184.9 | 154.1 | 156.4 | 192.4
2063 | 1928 | 148.7 | 184.4 | 192.4 | 198.6 | 184.4 | 153.8 | 156.3 | 192.1
2064 | 1929 | 148.5 | 183.9 | 191.8 | 197.9 | 183.6 | 153.6 | 156.1 | 191.9
2065 | 1930 | 148.3 | 183.6 | 191 | 197.4 | 182.9 | 153.3 | 155.9 | 191.7
2066 | 1931 | 148.1 | 183.3 | 190.6 | 196.9 | 182.2 | 153.1 | 155.6 | 191.5
2067 | 1932 | 147.9 | 182.9 | 190.2 | 196.3 | 181.5 | 152.8 | 155.4 | 191.4
2068 | 1933 | 147.7 | 182.5 | 189.6 | 195.7 | 180.8 | 152.6 | 155.2 | 191.2
2069 | 1934 | 147.6 | 182.2 | 189.1 | 195.1 | 180.3 | 152.3 | 154.9 | 190.9
2070 | 1935 | 147.4 | 181.8 | 188.7 | 194.4 | 179.7 | 152.1 | 154.7 | 190.8
2071 | 1936 | 147.3 | 181.3 | 188.3 | 193.6 | 179 | 151.9 | 154.5 | 190.5
2072 | 1937 | 147.1 | 181 | 187.6 | 192.9 | 178.6 | 151.6 | 154.4 | 190.2
2073 | 1938 | 147 | 180.6 | 186.9 | 192.3 | 178 | 151.4 | 154.1 | 190
2074 | 1939 | 146.8 | 180.2 | 186.5 | 191.7 | 177.4 | 151.2 | 153.9 | 189.8
2075 | 1940 | 146.7 | 179.8 | 185.7 | 191.1 | 176.7 | 150.9 | 153.6 | 189.6
2076 | 1941 | 146.5 | 179.5 | 185 | 190.5 | 176.2 | 150.7 | 153.3 | 189.4
2077 | 1942 | 146.3 | 179.2 | 184.5 | 189.7 | 175.7 | 150.5 | 153.1 | 189.1
2078 | 1943 | 146.2 | 178.7 | 184.2 | 189 | 175.1 | 150.3 | 152.9 | 188.9
2079 | 1944 | 146.1 | 178.4 | 183.4 | 188.5 | 174.8 | 150 | 152.8 | 188.7
2080 | 1945 | 145.9 | 178 | 182.9 | 188.1 | 174.5 | 149.8 | 152.5 | 188.6
2081 | 1946 | 145.7 | 177.6 | 182.4 | 188 | 174.1 | 149.5 | 152.3 | 188.5
2082 | 1947 | 145.5 | 177.2 | 181.9 | 188 | 173.8 | 149.3 | 152.1 | 188.3
2083 | 1948 | 145.3 | 176.8 | 181.1 | 188 | 173.6 | 149.1 | 151.9 | 188
2084 | 1949 | 145.1 | 176.4 | 180.7 | 187.8 | 173.2 | 148.9 | 151.6 | 187.7
2085 | 1950 | 145 | 176 | 180.4 | 187.6 | 172.6 | 148.6 | 151.4 | 187.6
2086 | 1951 | 144.8 | 175.7 | 179.7 | 187.5 | 172.4 | 148.4 | 151.2 | 187.4
2087 | 1952 | 144.6 | 175.3 | 179.1 | 187.4 | 172.2 | 148.2 | 151 | 187.1
2088 | 1953 | 144.5 | 174.8 | 178.7 | 187.2 | 171.8 | 148 | 150.8 | 186.8
2089 | 1954 | 144.2 | 174.4 | 178.2 | 187 | 171.5 | 147.7 | 150.6 | 186.6
2090 | 1955 | 144 | 174.1 | 177.7 | 186.7 | 171.3 | 147.5 | 150.4 | 186.4
2091 | 1956 | 143.8 | 173.7 | 177.4 | 186.2 | 171.1 | 147.3 | 150.1 | 186.2
2092 | 1957 | 143.6 | 173.3 | 177.1 | 185.5 | 170.7 | 147.1 | 149.9 | 185.9
2093 | 1958 | 143.5 | 173 | 176.3 | 184.9 | 170.5 | 146.9 | 149.6 | 185.8
2094 | 1959 | 143.3 | 172.7 | 175.7 | 184.3 | 170.2 | 146.7 | 149.4 | 185.6
2095 | 1960 | 143.1 | 172.3 | 175.5 | 183.7 | 169.6 | 146.4 | 149.2 | 185.6
2096 | 1961 | 142.9 | 171.9 | 175 | 183.1 | 169.1 | 146.2 | 148.9 | 185.5
2097 | 1962 | 142.8 | 171.6 | 174.3 | 182.5 | 168.9 | 146 | 148.7 | 185.3
2098 | 1963 | 142.7 | 171.3 | 173.9 | 181.9 | 168.5 | 145.8 | 148.5 | 185.1
2099 | 1964 | 142.5 | 170.8 | 173.8 | 181.4 | 168 | 145.5 | 148.2 | 184.9
2100 | 1965 | 142.4 | 170.6 | 173.4 | 181.2 | 167.8 | 145.3 | 148 | 184.6
2101 | 1966 | 142.2 | 170.3 | 173.2 | 180.9 | 167.5 | 145.1 | 147.8 | 184.4
2102 | 1967 | 142 | 169.9 | 172.9 | 180.2 | 166.8 | 144.9 | 147.6 | 184.1
2103 | 1968 | 141.9 | 169.5 | 172.5 | 179.6 | 166 | 144.7 | 147.5 | 184
2104 | 1969 | 141.8 | 169.2 | 171.7 | 179 | 165.3 | 144.5 | 147.4 | 183.8
2105 | 1970 | 141.7 | 168.9 | 171.2 | 178.5 | 164.4 | 144.3 | 147.1 | 183.7
2106 | 1971 | 141.5 | 168.4 | 170.9 | 177.8 | 163.4 | 144.1 | 146.9 | 183.5
2107 | 1972 | 141.3 | 168.2 | 170.4 | 177.2 | 162.7 | 143.9 | 146.8 | 183.4
2108 | 1973 | 141.1 | 167.8 | 170.1 | 176.9 | 161.9 | 143.7 | 146.5 | 183.2
2109 | 1974 | 140.9 | 167.5 | 169.7 | 176.4 | 161.1 | 143.5 | 146.3 | 183
2110 | 1975 | 140.8 | 167.1 | 169.2 | 176.3 | 160.3 | 143.3 | 146 | 182.7
2111 | 1976 | 140.6 | 166.8 | 168.6 | 176.1 | 159.7 | 143.1 | 145.8 | 182.5
2112 | 1977 | 140.5 | 166.4 | 168.2 | 175.7 | 159.1 | 142.9 | 145.6 | 182.3
2113 | 1978 | 140.3 | 166 | 167.9 | 175.2 | 158.5 | 142.6 | 145.3 | 182.1
2114 | 1979 | 140.2 | 165.7 | 167 | 175 | 158.2 | 142.4 | 145.1 | 181.8
2115 | 1980 | 140 | 165.3 | 166.4 | 174.6 | 157.7 | 142.2 | 144.8 | 181.5
2116 | 1981 | 139.9 | 164.9 | 166.1 | 174.4 | 157.1 | 142 | 144.6 | 181.2
2117 | 1982 | 139.8 | 164.5 | 165.8 | 174.2 | 156.6 | 141.8 | 144.4 | 181
2118 | 1983 | 139.6 | 164.3 | 165.1 | 174 | 156.3 | 141.6 | 144.2 | 180.9
2119 | 1984 | 139.4 | 163.9 | 164.8 | 173.8 | 156 | 141.4 | 144 | 180.6
2120 | 1985 | 139.3 | 163.5 | 164.6 | 173.5 | 155.6 | 141.2 | 143.9 | 180.4
2121 | 1986 | 139.1 | 163.3 | 163.9 | 173.2 | 155.5 | 141 | 143.6 | 180.2
2122 | 1987 | 139 | 163 | 163.4 | 173 | 155.3 | 140.8 | 143.4 | 180.1
2123 | 1988 | 138.7 | 162.6 | 163 | 172.8 | 155.1 | 140.6 | 143.2 | 179.9
2124 | 1989 | 138.6 | 162.3 | 162.4 | 172.5 | 154.9 | 140.4 | 142.9 | 179.7
2125 | 1990 | 138.4 | 162.2 | 161.8 | 172.2 | 154.9 | 140.2 | 142.7 | 179.6
2126 | 1991 | 138.2 | 161.9 | 161.3 | 172 | 154.6 | 140 | 142.5 | 179.5
2127 | 1992 | 138 | 161.6 | 161.1 | 171.6 | 154.2 | 139.8 | 142.3 | 179.3
2128 | 1993 | 137.8 | 161.4 | 160.7 | 171.4 | 154.1 | 139.6 | 142.1 | 179.1
2129 | 1994 | 137.6 | 161.1 | 160.3 | 171.1 | 153.9 | 139.3 | 142 | 178.8
2130 | 1995 | 137.4 | 160.8 | 160 | 170.8 | 153.6 | 139.1 | 141.9 | 178.7
2131 | 1996 | 137.3 | 160.5 | 159.6 | 170.4 | 153.4 | 138.9 | 141.7 | 178.6
2132 | 1997 | 137.1 | 160.3 | 159.1 | 170.2 | 153.4 | 138.6 | 141.5 | 178.5
2133 | 1998 | 137 | 160 | 158.7 | 169.8 | 153.3 | 138.4 | 141.3 | 178.4
2134 | 1999 | 136.9 | 159.7 | 158.5 | 169.3 | 153.1 | 138.1 | 141 | 178.2
2135 | 2000 | 136.7 | 159.4 | 157.9 | 168.9 | 153 | 137.9 | 140.8 | 178
2136 | 2001 | 136.6 | 159.2 | 157.3 | 168.5 | 152.7 | 137.7 | 140.7 | 177.9
2137 | 2002 | 136.5 | 158.8 | 157 | 168.1 | 152.3 | 137.5 | 140.4 | 177.7
2138 | 2003 | 136.4 | 158.5 | 156.7 | 167.8 | 151.8 | 137.2 | 140.2 | 177.5
2139 | 2004 | 136.2 | 158.3 | 156.1 | 167.5 | 151.6 | 137 | 139.9 | 177.3
2140 | 2005 | 136 | 158 | 155.7 | 167.2 | 151.3 | 136.8 | 139.7 | 177.1
2141 | 2006 | 135.9 | 157.7 | 155.5 | 166.9 | 151 | 136.6 | 139.4 | 176.9
2142 | 2007 | 135.7 | 157.4 | 155.1 | 166.7 | 151 | 136.4 | 139.2 | 176.6
2143 | 2008 | 135.6 | 157.2 | 154.6 | 166.4 | 150.9 | 136.2 | 139 | 176.5
2144 | 2009 | 135.5 | 156.8 | 154.5 | 166 | 150.7 | 136 | 138.8 | 176.2
2145 | 2010 | 135.3 | 156.5 | 154.4 | 165.7 | 150.5 | 135.8 | 138.6 | 176
2146 | 2011 | 135.1 | 156.3 | 154 | 165.5 | 150.5 | 135.6 | 138.4 | 175.8
2147 | 2012 | 135 | 156 | 153.8 | 165.2 | 150.3 | 135.4 | 138.1 | 175.5
2148 | 2013 | 134.8 | 155.7 | 153.8 | 164.8 | 149.9 | 135.2 | 137.9 | 175.4
2149 | 2014 | 134.7 | 155.5 | 153.3 | 164.6 | 149.8 | 135 | 137.6 | 175.3
2150 | 2015 | 134.5 | 155.2 | 152.9 | 164.4 | 149.5 | 134.8 | 137.4 | 175.1
2151 | 2016 | 134.3 | 154.9 | 152.8 | 164.1 | 149.2 | 134.6 | 137.2 | 175
2152 | 2017 | 134.2 | 154.6 | 152.6 | 163.6 | 148.9 | 134.4 | 137 | 174.9
2153 | 2018 | 134.1 | 154.4 | 152.2 | 163.2 | 148.6 | 134.2 | 136.8 | 174.6
2154 | 2019 | 134 | 154.1 | 152.1 | 162.8 | 148.3 | 134 | 136.7 | 174.5
2155 | 2020 | 133.7 | 153.7 | 152 | 162.3 | 147.8 | 133.7 | 136.6 | 174.3
2156 | 2021 | 133.6 | 153.5 | 151.6 | 161.8 | 147.6 | 133.5 | 136.5 | 174.1

## Test Facts
Last row in IRMS data sheets: | 17
Time when Penlight power was initiated: | 135