## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 46
Test conditions: Cable: Bundle of six, 7-conductor, 12 AWG, mixture of PE, XLPE, TS/TP (XLPE Ins. with PVC Jacket), EPR, Tefzel & PVC insulated control cables (Items 15, 10, 3, 2, 12 & 1). Cable specimens present: Six lengths of cable were monitored for electrical performance, 1 each of PE, XLPE, TS/TP, EPR, Tefzel & PVC. A seventh length of cable (EPR cable Item #2) was monitored for temperature response. No other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls open and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23.0 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable, cable tray was grounded. Thermal response monitoring: Shroud temperature and six cable temperatures (see thermocouple map). Shroud power: Initiated after 158 seconds of baseline data monitoring. Special Note: The ends of the Penlight shroud were not enclosed
DAQ Time | Penlight Time | Event | Interpretation
158 | 0 | Initated Penlight Heating
507 | 349 | Conductor E9 shorts to ground at less than 100 ohms (13) | PVC Cable E partially shorts to ground
539 | 381 | Conductors E9 & E10 short together at less than 100 ohms (15) | PVC Cable E shorts internally
695 | 537 | Conductor E10 shorts to ground at much less than 100 ohms (<1) | PVC Cable E shorted to ground
994 | 836 | Cables ignite and burn
1029 | 871 | Power to Penlight shutoff
1043-1049 | 885-891 | Conductors D7 & D8 both short to ground at less than 100 ohms (32 & <1) | EPR Cable D shorts to ground
1068 | 910 | Conductors D7 & D8 both short together at less than 100 ohms (35) | EPR Cable D shorts internally
1267-1269 | 1109-1111 | Conductors F11 & F12 both short to ground at less than 100 ohms (1 & 2) | XLPE Cable F shorts to ground
1292 | 1134 | Conductors F11 & F12 both short together at less than 1000 ohms (474) | XLPE Cable F shorts internally
1332-1350 | 1174-1192 | Conductor A2 shorts to ground at less than 1000 ohms (236); conductor B3 shorts to ground at less than 100 ohms (32) | TS/TP Cable A and PE Cable B partially short to ground
1353 | 1195 | Conductors B3 & B4 short together at less than 100 ohms (4) | PE Cable B shorts internally
1366 | 1208 | Conductor B4 shorts to ground at less than 100 ohms (22) | PE Cable B shorted to ground
1476 | 1318 | The existing internal short between F11 & F12 decreases to less than 100 ohms (21)
1484 | 1326 | Conductor A1 shorts to ground at less than 1000 ohms (310)
1669-1692 | 1511-1534 | The existing ground faults on Conductors A1 & A2 decrease to less than 100 ohms (48 & 70) | TS/TP Cable A is shorted to ground
Additional Observations
Observation 1 | The Tefzel cable (C) did not short to ground or interact externally.
Observation 2 | It took only 349 s (5.8 min.) from the start of Penlight heating for the PVC cable to short to ground, 381 s (6.4 min.) for the PVC cable to short internally, and 836 s (13.9 min.) for the cable bundle to ignite.
Observation 3 | No cable to cable interactions took place prior to the individual cables either shorting to ground or shorting internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Cable 1 | Within cable just below cable jacket, center position
| TC2 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC3 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC4 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC5 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC6 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
A = TS/TP Cable, Item #3
B = PE Cable, Item #15
C = Tefzel Cable, Item #12
D = EPR Cable, Item #2
E = PVC Cable, Item #1
F = XLPE Cable, Item #10
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 46 |  |  | 2006-08-23 | 8:25
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B3-D7 | Penlight Time | B3-D8 | Penlight Time | B3-E9 | Penlight Time | B3-E10 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | B4-D7 | Penlight Time | B4-D8 | Penlight Time | B4-E9 | Penlight Time | B4-E10 | Penlight Time | C5-C6 | Penlight Time | C5-E9 | Penlight Time | C5-E10 | Penlight Time | C5-F11 | Penlight Time | C5-F12 | Penlight Time | C6-E9 | Penlight Time | C6-E10 | Penlight Time | C6-F11 | Penlight Time | C6-F12 | Penlight Time | D7-D8 | Penlight Time | D7-E9 | Penlight Time | D7-E10 | Penlight Time | D8-E9 | Penlight Time | D8-E10 | Penlight Time | E9-E10 | Penlight Time | E9-F11 | Penlight Time | E9-F12 | Penlight Time | E10-F11 | Penlight Time | E10-F12 | Penlight Time | F11-F12 | Penlight Time | A-B MIN IR | Penlight Time | A-C MIN IR | Penlight Time | B-C MIN IR | Penlight Time | B-D MIN IR | Penlight Time | B-E MIN IR | Penlight Time | C-E MIN IR | Penlight Time | C-F MIN IR | Penlight Time | D-E MIN IR | Penlight Time | E-F MIN IR
-157.5 | 211201.9994 | -154.5 | 211201.9994 | -151.5 | 211201.9994 | -149 | 211201.9994 | -146 | 211201.9994 | -126.5 | 211201.9994 | -123.5 | 211201.9994 | -121 | 211201.9994 | -118 | 211201.9994 | -98.5 | 219737.9994 | -95.5 | 211201.9994 | -93 | 211201.9994 | -90 | 213737.9994 | -87.5 | 222237.9994 | -84.5 | 253137.9994 | -81.5 | 256337.9994 | -73.5 | 211201.9994 | -70.5 | 211201.9994 | -67.5 | 234237.9994 | -65 | 257637.9994 | -62 | 252737.9994 | -59.5 | 253237.9994 | -51 | 211201.9994 | -42.5 | 252037.9994 | -39.5 | 254837.9994 | -37 | 230437.9994 | -34 | 229937.9994 | -25.5 | 254037.9994 | -23 | 255037.9994 | -20 | 240937.9994 | -17.5 | 244637.9994 | -14.5 | 223437.9994 | -11.5 | 255737.9994 | -9 | 248037.9994 | -0.5 | 252137.9994 | 2.5 | 257637.9994 | 10.5 | 256937.9994 | 13.5 | 249337.9994 | 16.5 | 254137.9994 | 19 | 255437.9994 | 22 | 254337.9994 | 24.5 | 247837.9994 | -139 | 211201.9994 | -133.5 | 211201.9994 | -83.125 | 211201.9994 | -77.5 | 213737.9994 | -71.875 | 252737.9994 | -32.625 | 252037.9994 | -27.125 | 229937.9994 | -4.625 | 248037.9994 | 17.75 | 249337.9994
27.5 | 211201.9994 | 30.5 | 211201.9994 | 33 | 211201.9994 | 36 | 211201.9994 | 38.5 | 211201.9994 | 58.5 | 211201.9994 | 61 | 211201.9994 | 64 | 211201.9994 | 66.5 | 211201.9994 | 86.5 | 219737.9994 | 89 | 211201.9994 | 92 | 211201.9994 | 94.5 | 213737.9994 | 97.5 | 222237.9994 | 100.5 | 253137.9994 | 103 | 128118.9988 | 111.5 | 211201.9994 | 114.5 | 211201.9994 | 117 | 234237.9994 | 120 | 257637.9994 | 122.5 | 252737.9994 | 125.5 | 253237.9994 | 134 | 211201.9994 | 142.5 | 252037.9994 | 145 | 254837.9994 | 148 | 230437.9994 | 150.5 | 229937.9994 | 159 | 254037.9994 | 161.5 | 255037.9994 | 164.5 | 240937.9994 | 167.5 | 244637.9994 | 170.5 | 223437.9994 | 173 | 255737.9994 | 176 | 248037.9994 | 184.5 | 252137.9994 | 187 | 257637.9994 | 195.5 | 256937.9994 | 198.5 | 249337.9994 | 201 | 254137.9994 | 205 | 255437.9994 | 206.5 | 254337.9994 | 209.5 | 247837.9994 | 45.75 | 211201.9994 | 51.25 | 211201.9994 | 101.75 | 211201.9994 | 107.25 | 213737.9994 | 112.875 | 128118.9988 | 152 | 252037.9994 | 157.625 | 229937.9994 | 180.125 | 248037.9994 | 202.75 | 249337.9994
212.5 | 211201.9994 | 215 | 211201.9994 | 218 | 211201.9994 | 220.5 | 211201.9994 | 223.5 | 211201.9994 | 243 | 211201.9994 | 245.5 | 105550.9988 | 248.5 | 211201.9994 | 251.5 | 211201.9994 | 271 | 219737.9994 | 274 | 211201.9994 | 276.5 | 211201.9994 | 279.5 | 213737.9994 | 282 | 222237.9994 | 285 | 253137.9994 | 287.5 | 128118.9988 | 296 | 211201.9994 | 299 | 211201.9994 | 302 | 234237.9994 | 304.5 | 257637.9994 | 307.5 | 126318.9988 | 310.5 | 253237.9994 | 318.5 | 211201.9994 | 327 | 252037.9994 | 330 | 254837.9994 | 332.5 | 230437.9994 | 335.5 | 229937.9994 | 344 | 254037.9994 | 346.5 | 255037.9994 | 349.5 | 240937.9994 | 352.5 | 244637.9994 | 355 | 223437.9994 | 358 | 255737.9994 | 360.5 | 248037.9994 | 369 | 252137.9994 | 372 | 64334.4976 | 380.5 | 15.4924 | 383 | 49738.0994 | 386 | 28282.2688 | 388.5 | 63784.4976 | 391.5 | 84712.6648 | 394 | 123868.9988 | 230.375 | 105550.9988 | 236 | 211201.9994 | 286.375 | 211201.9994 | 292 | 213737.9994 | 297.625 | 126318.9988 | 336.875 | 252037.9994 | 342.5 | 229937.9994 | 364.875 | 64334.4976 | 387.25 | 28282.2688
397 | 105550.9988 | 399.5 | 105550.9988 | 402.5 | 211201.9994 | 405.5 | 105550.9988 | 408 | 105550.9988 | 427.5 | 105550.9988 | 430.5 | 105550.9988 | 433.5 | 105550.9988 | 436.5 | 211201.9994 | 456 | 73179.3315 | 458.5 | 105550.9988 | 461.5 | 105550.9988 | 464.5 | 213737.9994 | 467 | 222237.9994 | 470 | 126518.9988 | 472.5 | 51187.5969 | 481 | 105550.9988 | 484 | 105550.9988 | 486.5 | 117068.9988 | 489.5 | 128768.9988 | 492.5 | 126318.9988 | 495 | 50567.5969 | 503.5 | 105550.9988 | 511.5 | 252037.9994 | 514.5 | 50887.5969 | 517.5 | 46007.5969 | 520 | 57409.4976 | 528.5 | 126968.9988 | 531.5 | 50927.5969 | 534 | 48107.5969 | 537 | 61084.4976 | 539.5 | 74412.6648 | 542.5 | 127818.9988 | 545.5 | 49527.5969 | 553.5 | 126018.9988 | 556.5 | 51447.5969 | 565 | 14.9044 | 568 | 49618.3598 | 570.5 | 15806.852 | 573.5 | 4427.5796 | 576.5 | 1534.3732 | 579 | 49487.5969 | 415 | 105550.9988 | 420.875 | 105550.9988 | 471.25 | 105550.9988 | 476.875 | 117068.9988 | 482.5 | 50567.5969 | 521.5 | 50887.5969 | 527.125 | 46007.5969 | 549.5 | 49527.5969 | 572.125 | 1534.3732
581.5 | 42160.3969 | 584.5 | 52725.4976 | 587.5 | 52725.4976 | 590 | 52725.4976 | 593 | 70333.9982 | 612.5 | 70333.9982 | 615.5 | 105550.9988 | 618.5 | 105550.9988 | 621 | 105550.9988 | 640.5 | 109818.9988 | 643.5 | 105550.9988 | 646 | 105550.9988 | 649 | 106818.9988 | 651.5 | 111068.9988 | 654.5 | 126518.9988 | 657.5 | 51187.5969 | 665.5 | 70333.9982 | 668.5 | 105550.9988 | 671.5 | 117068.9988 | 674 | 128768.9988 | 677 | 126318.9988 | 679.5 | 50567.5969 | 688 | 105550.9988 | 696.5 | 125968.9988 | 699.5 | 50887.5969 | 702 | 46007.5969 | 705 | 57409.4976 | 713.5 | 126968.9988 | 716.5 | 50927.5969 | 719 | 48107.5969 | 721.5 | 61084.4976 | 724.5 | 111668.9988 | 727.5 | 127818.9988 | 730 | 49527.5969 | 738.5 | 83979.3315 | 741.5 | 51447.5969 | 750 | 0.91787 | 752.5 | 1534.9171 | 755.5 | 1534.9753 | 758.5 | 37863.7684 | 761 | 10018.2742 | 763.5 | 49487.5969 | 600 | 52725.4976 | 605.625 | 52725.4976 | 655.875 | 70333.9982 | 661.5 | 106818.9988 | 667.125 | 50567.5969 | 706.5 | 50887.5969 | 711.875 | 46007.5969 | 734.375 | 49527.5969 | 756.875 | 1534.9171
766.5 | 42160.3969 | 769.5 | 52725.4976 | 772 | 52725.4976 | 775 | 70333.9982 | 777.5 | 70333.9982 | 797.5 | 70333.9982 | 800 | 105550.9988 | 803 | 105550.9988 | 806 | 105550.9988 | 825.5 | 109818.9988 | 828 | 105550.9988 | 831 | 105550.9988 | 833.5 | 106818.9988 | 836.5 | 111068.9988 | 839.5 | 126518.9988 | 842 | 51187.5969 | 850.5 | 70333.9982 | 853.5 | 70333.9982 | 856 | 117068.9988 | 859 | 128768.9988 | 861.5 | 126318.9988 | 864.5 | 50567.5969 | 873 | 105550.9988 | 881.5 | 252037.9994 | 884 | 63634.4976 | 887 | 46007.5969 | 889.5 | 76579.3315 | 898 | 126968.9988 | 901 | 50927.5969 | 903.5 | 48107.5969 | 906.5 | 81479.3315 | 909.5 | 34.524 | 912 | 3171.7229 | 915 | 397.965 | 923.5 | 22.2173 | 926 | 0.6839 | 934.5 | 25.2545 | 937.5 | 15307.2549 | 940 | 46165.2524 | 943 | 57325.6136 | 945.5 | 14110.2172 | 948.5 | 20345.5728 | 784.75 | 52725.4976 | 790.375 | 70333.9982 | 840.75 | 70333.9982 | 846.25 | 106818.9988 | 851.875 | 50567.5969 | 891.125 | 50927.5969 | 896.625 | 46007.5969 | 919.125 | 0.6839 | 941.5 | 14110.2172
951.5 | 1.9119 | 954 | 19063.7153 | 957 | 70100.9664 | 959.5 | 210502.7099 | 962.5 | 52725.4976 | 982 | 52725.4976 | 985 | 52725.4976 | 987.5 | 52725.4976 | 990.5 | 52725.4976 | 1010 | 54859.4976 | 1013 | 70333.9982 | 1015.5 | 52725.4976 | 1018.5 | 71179.3315 | 1021.5 | 55484.4976 | 1024 | 50547.5969 | 1027 | 51187.5969 | 1035.5 | 52725.4976 | 1038 | 70333.9982 | 1041 | 78012.6648 | 1043.5 | 51447.5969 | 1046.5 | 50467.5969 | 1049.5 | 50567.5969 | 1057.5 | 2.4882 | 1066 | 55437.8064 | 1069 | 50887.5969 | 1071.5 | 46007.5969 | 1074.5 | 45907.5969 | 1083 | 50727.5969 | 1085.5 | 50927.5969 | 1088.5 | 48107.5969 | 1091.5 | 48847.5969 | 1094 | 12.6773 | 1097 | 31.0347 | 1099.5 | 9.0093 | 1108 | 2.9282 | 1111 | 2.7538 | 1119.5 | 24.1329 | 1122 | 12209.609 | 1125 | 760.6418 | 1127.5 | 8635.7788 | 1130.5 | 4056.5892 | 1133.5 | 473.9904 | 969.5 | 19063.7153 | 975 | 52725.4976 | 1025.5 | 52725.4976 | 1031.125 | 51447.5969 | 1036.75 | 50467.5969 | 1075.875 | 50727.5969 | 1081.5 | 45907.5969 | 1103.875 | 2.7538 | 1126.25 | 760.6418
1136 | 37.7317 | 1139 | 26237.7028 | 1141.5 | 105151.4969 | 1144.5 | 210303.1358 | 1147.5 | 42160.3969 | 1167 | 10465.0878 | 1169.5 | 7725.9835 | 1172.5 | 203815.4405 | 1175.5 | 147921.4499 | 1195 | 3.5331 | 1197.5 | 23598.1408 | 1200.5 | 77054.7769 | 1203.5 | 170.1987 | 1206 | 50.2495 | 1209 | 79.8999 | 1211.5 | 30.8628 | 1220 | 43220.0282 | 1223 | 38429.1147 | 1225.5 | 26.4441 | 1228.5 | 31.9472 | 1231.5 | 25.8394 | 1234 | 53.1893 | 1242.5 | 20.5865 | 1251 | 3502.8312 | 1253.5 | 50887.5969 | 1256.5 | 57534.4976 | 1259.5 | 45907.5969 | 1267.5 | 63434.4976 | 1270.5 | 63684.4976 | 1273.5 | 60159.4976 | 1276 | 61084.4976 | 1279 | 8.5498 | 1281.5 | 16.3535 | 1284.5 | 3.2975 | 1293 | 16.5061 | 1295.5 | 4.6701 | 1304 | 5.8152 | 1307 | 5056.4046 | 1309.5 | 9376.6653 | 1312.5 | 7357.4179 | 1315.5 | 1193.8242 | 1318 | 21.2634 | 1154.25 | 7725.9835 | 1160 | 42160.3969 | 1210.25 | 23598.1408 | 1215.875 | 26.4441 | 1221.5 | 25.8394 | 1260.625 | 3502.8312 | 1266.375 | 45907.5969 | 1288.625 | 3.2975 | 1311.125 | 1193.8242
1321 | 18.3334 | 1323.5 | 1146.387 | 1326.5 | 44255.867 | 1329.5 | 193435.1279 | 1332 | 190540.6177 | 1351.5 | 869.1421 | 1354.5 | 920.6562 | 1357.5 | 190939.8605 | 1360 | 191838.1568 | 1379.5 | 9.0525 | 1382.5 | 45615.485 | 1385.5 | 58291.4435 | 1388 | 22.1903 | 1391 | 60.3894 | 1393.5 | 120.2759 | 1396.5 | 82.9749 | 1405 | 132650.4132 | 1407.5 | 134846.2485 | 1410.5 | 102.8924 | 1413.5 | 141.3573 | 1416 | 98.1525 | 1419 | 90.2448 | 1427.5 | 26.1913 | 1435.5 | 1701.7172 | 1438.5 | 54718.6851 | 1441.5 | 57534.4976 | 1444 | 57409.4976 | 1452.5 | 63434.4976 | 1455.5 | 63684.4976 | 1458 | 60159.4976 | 1461 | 61084.4976 | 1463.5 | 0.49959 | 1466.5 | 37.8429 | 1469.5 | 30.9114 | 1477.5 | 55.4911 | 1480.5 | 23.0654 | 1489 | 22.8486 | 1491.5 | 327.4306 | 1494.5 | 1395.4021 | 1497.5 | 108.5648 | 1500 | 698.0327 | 1503 | 0.83862 | 1339 | 869.1421 | 1344.75 | 190540.6177 | 1395.125 | 45615.485 | 1400.75 | 22.1903 | 1406.25 | 82.9749 | 1445.5 | 1701.7172 | 1451.125 | 57409.4976 | 1473.5 | 23.0654 | 1495.875 | 108.5648
1505.5 | 3.959 | 1508.5 | 113.4862 | 1511.5 | 64.2597 | 1514 | 18018.3877 | 1516.5 | 52025.1627 | 1536.5 | 14.4857 | 1539.5 | 80.1 | 1542 | 41854.4704 | 1545 | 101709.0496 | 1564.5 | 2.5302 | 1567 | 4293.8562 | 1570 | 6290.0702 | 1573 | 1.6872 | 1575.5 | 27.4629 | 1578.5 | 18.5576 | 1581.5 | 17.1807 | 1589.5 | 9184.5804 | 1592.5 | 20862.432 | 1595.5 | 13.0597 | 1598 | 20.3963 | 1601 | 36.364 | 1603.5 | 15.8029 | 1612 | 29.246 | 1620.5 | 39607.9017 | 1623.5 | 63634.4976 | 1626 | 76745.9982 | 1629 | 76579.3315 | 1637.5 | 63434.4976 | 1640 | 63684.4976 | 1643 | 60159.4976 | 1645.5 | 81479.3315 | 1648.5 | 21.9166 | 1651 | 72.4309 | 1654 | 26.5889 | 1662.5 | 23.6995 | 1665.5 | 35.3611 | 1673.5 | 26.7811 | 1676.5 | 1654.8451 | 1679.5 | 1771.8447 | 1682 | 1263.4647 | 1685 | 321.6589 | 1687.5 | 20.7762 | 1524 | 14.4857 | 1529.375 | 18018.3877 | 1579.75 | 4293.8562 | 1585.5 | 1.6872 | 1591.125 | 15.8029 | 1630.375 | 39607.9017 | 1635.875 | 60159.4976 | 1658.25 | 23.6995 | 1680.75 | 321.6589
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 46 |  |  | 2006-08-23 | 8:25
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | D7-G | Penlight Time | D8-G | Penlight Time | E9-G | Penlight Time | E10-G | Penlight Time | F11-G | Penlight Time | F12-G | Penlight Time | A-B-C to Gnd Min | Penlight Time | B-D-E to Gnd Min | Penlight Time | C-E-F to Gnd Min | Penlight Time | B-D to Gnd Min | Penlight Time | B-E to Gnd Min | Penlight Time | D-E to Gnd Min | Penlight Time | C-E to Gnd Min | Penlight Time | C-F to Gnd Min | Penlight Time | E-F to Gnd Min | Penlight Time | A to Gnd Min | Penlight Time | B to Gnd Min | Penlight Time | C to Gnd Min | Penlight Time | D to Gnd Min | Penlight Time | E to Gnd Min | Penlight Time | F to Gnd Min
-151.7 | 211202 |  | -129.3 | 211202 | -101.2778 | 211202 | -85.7222 | 211202 | -71.4444 | 211202 | -62.7222 | 211202 | -38.5 | 213738 | -33 | 222238 | -20.6667 | 126969 | -17.6111 | 248038 | -2.9802e-08 | 230438 | 2.3 | 229938 | -151.7 | 211202 | -101.2778 | 126969 | -71.4444 | 126969 | -64.625 | 211202 | -56.3194 | 126969 | -27.4444 | 126969 | -43.1111 | 126969 | -32.9667 | 211202 | -8.9944 | 126969 | -140.5 | 211202 | -93.5 | 211202 | -67.0833 | 211202 | -35.75 | 213738 | -19.1389 | 126969 | 1.15 | 229938
33.1 | 211202 |  | 55.5 | 211202 | 83.5556 | 128119 | 99.0556 | 211202 | 113.3889 | 211202 | 122 | 211202 | 146.2 | 213738 | 151.9 | 111669 | 164.1111 | 249338 | 167.2222 | 248038 | 185.1 | 230438 | 187 | 229938 | 33.1 | 128119 | 83.5556 | 111669 | 113.3889 | 211202 | 120.1778 | 111669 | 128.4861 | 128119 | 157.3583 | 111669 | 141.6806 | 211202 | 151.8722 | 211202 | 175.8583 | 229938 | 44.3 | 211202 | 91.3056 | 128119 | 117.6944 | 211202 | 149.05 | 111669 | 165.6667 | 248038 | 186.05 | 229938
217.9 | 211202 |  | 240.2 | 105551 | 268.1667 | 128119 | 283.7778 | 126319 | 298.0556 | 211202 | 306.8333 | 105551 | 331 | 213738 | 336.5 | 64334.5 | 348.8889 | 12.5999 | 351.9444 | 63784.5 | 369.5 | 49787.6 | 371.9 | 50747.6 | 217.9 | 105551 | 268.1667 | 12.5999 | 298.0556 | 12.5999 | 304.8611 | 64334.5 | 313.1944 | 12.5999 | 342.0833 | 12.5999 | 326.4306 | 12.5999 | 336.5722 | 49787.6 | 360.5583 | 12.5999 | 229.05 | 105551 | 275.9722 | 126319 | 302.4444 | 105551 | 333.75 | 64334.5 | 350.4167 | 12.5999 | 370.7 | 49787.6
402.5 | 105551 |  | 425 | 105551 | 453 | 51187.6 | 468.6111 | 50567.6 | 482.8333 | 46007.6 | 491.6111 | 48107.6 | 515.7 | 49527.6 | 521.2 | 51447.6 | 533.5556 | 0.97209 | 536.7222 | 0.6482 | 554.4 | 41473 | 556.6 | 42306.3333 | 402.5 | 46007.6 | 453 | 0.6482 | 482.8333 | 0.6482 | 489.6278 | 49527.6 | 497.9722 | 0.6482 | 526.7944 | 0.6482 | 511.1806 | 0.6482 | 521.3611 | 41473 | 545.3194 | 0.6482 | 413.75 | 105551 | 460.8056 | 50567.6 | 487.2222 | 46007.6 | 518.45 | 49527.6 | 535.1389 | 0.6482 | 555.5 | 41473
587.3 | 42160.4 |  | 609.8 | 52725.5 | 637.7222 | 51187.6 | 653.2778 | 50567.6 | 667.6111 | 46007.6 | 676.3333 | 48107.6 | 700.5 | 49527.6 | 706 | 51447.6 | 718.3889 | 0.64135 | 721.5556 | 0.64286 | 739.1 | 49487.6 | 741.3 | 49487.6 | 587.3 | 42160.4 | 637.7222 | 0.64135 | 667.6111 | 0.64135 | 674.375 | 49527.6 | 682.7361 | 0.64135 | 711.6111 | 0.64135 | 695.9722 | 0.64135 | 706.0861 | 46007.6 | 730.0861 | 0.64135 | 598.55 | 42160.4 | 645.5 | 50567.6 | 671.9722 | 46007.6 | 703.25 | 49527.6 | 719.9722 | 0.64135 | 740.2 | 49487.6
772.1 | 42160.4 |  | 794.6 | 52725.5 | 822.5556 | 51187.6 | 838.0556 | 50567.6 | 852.3889 | 46007.6 | 861.1111 | 48107.6 | 885.2 | 31.5084 | 890.9 | 0.87593 | 903.1111 | 0.65103 | 906.1667 | 0.63959 | 923.9 | 30854.3062 | 926 | 41302.01 | 772.1 | 42160.4 | 822.5556 | 0.63959 | 852.3889 | 0.63959 | 859.1778 | 0.87593 | 867.4722 | 0.63959 | 896.3444 | 0.63959 | 880.6944 | 0.63959 | 890.85 | 30854.3062 | 914.7944 | 0.63959 | 783.35 | 42160.4 | 830.3056 | 50567.6 | 856.75 | 46007.6 | 888.05 | 0.87593 | 904.6389 | 0.63959 | 924.95 | 30854.3062
956.9 | 35133.319 |  | 979.3 | 3000.7852 | 1007.2778 | 50547.6 | 1022.8889 | 50467.6 | 1037.1111 | 1682.3224 | 1045.8333 | 5092.9016 | 1070 | 0.70391 | 1075.6 | 0.63959 | 1087.8889 | 2.1093 | 1091 | 0.64615 | 1108.6 | 1.0218 | 1111 | 1.8893 | 956.9 | 1682.3224 | 1007.2778 | 0.63959 | 1037.1111 | 0.64615 | 1043.9417 | 0.63959 | 1052.2639 | 0.64615 | 1081.1222 | 0.63959 | 1065.4583 | 0.64615 | 1075.6361 | 1.0218 | 1099.6222 | 0.64615 | 968.1 | 3000.7852 | 1015.0833 | 50467.6 | 1041.4722 | 1682.3224 | 1072.8 | 0.63959 | 1089.4444 | 0.64615 | 1109.8 | 1.0218
1141.7 | 3993.5749 |  | 1164.1 | 235.775 | 1192.1111 | 32.0484 | 1207.6111 | 22.365 | 1221.9444 | 2243.2402 | 1230.7222 | 6430.9107 | 1254.8 | 4.7438 | 1260.4 | 5.9257 | 1272.6667 | 0.64437 | 1275.7222 | 5.9124 | 1293.5 | 8.2846 | 1295.7 | 3.5271 | 1141.7 | 22.365 | 1192.1111 | 0.64437 | 1221.9444 | 0.64437 | 1228.7306 | 4.7438 | 1237.0278 | 0.64437 | 1265.8972 | 0.64437 | 1250.2639 | 0.64437 | 1260.4667 | 3.5271 | 1284.3972 | 0.64437 | 1152.9 | 235.775 | 1199.8611 | 22.365 | 1226.3333 | 2243.2402 | 1257.6 | 4.7438 | 1274.1944 | 0.64437 | 1294.6 | 3.5271
1326.5 | 309.9151 |  | 1348.9 | 507.7442 | 1376.8333 | 3.1276 | 1392.4444 | 21.3576 | 1406.8333 | 1679.6756 | 1415.5 | 6923.0699 | 1439.6 | 1.8396 | 1445.2 | 5.3735 | 1457.3889 | 0.65207 | 1460.6667 | 0.64876 | 1478.3 | 0.66504 | 1480.5 | 7.5949 | 1326.5 | 3.1276 | 1376.8333 | 0.64876 | 1406.8333 | 0.64876 | 1413.5194 | 1.8396 | 1421.8333 | 0.64876 | 1450.7139 | 0.64876 | 1435.0972 | 0.64876 | 1445.2833 | 0.66504 | 1469.2139 | 0.64876 | 1337.7 | 309.9151 | 1384.6389 | 3.1276 | 1411.1667 | 1679.6756 | 1442.4 | 1.8396 | 1459.0278 | 0.64876 | 1479.4 | 0.66504
1511.2 | 48.334 |  | 1533.7 | 70.19 | 1561.6667 | 2.1286 | 1577.2778 | 4.6072 | 1591.5 | 4639.5196 | 1600.2222 | 20567.8766 | 1624.4 | 23.0259 | 1630 | 7.8851 | 1642.2778 | 6.1128 | 1645.3889 | 1.1723 | 1663 | 0.7156 | 1665.3 | 0.6738 | 1511.2 | 2.1286 | 1561.6667 | 1.1723 | 1591.5 | 0.6738 | 1598.3361 | 2.1286 | 1606.6528 | 1.1723 | 1635.5167 | 1.1723 | 1619.8472 | 1.1723 | 1630.0056 | 0.6738 | 1653.9917 | 0.6738 | 1522.45 | 48.334 | 1569.4722 | 2.1286 | 1595.8611 | 4639.5196 | 1627.2 | 7.8851 | 1643.8333 | 1.1723 | 1664.15 | 0.6738
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0
[31 empty] | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0 | #DIV/0! | 0

## F11-F12
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 151.3663 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
38952.351 | 1 | 0 | 38952.351 | 1 | 0 |  | 24.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38952.3531 | 1 | 0 | 38952.3531 | 1 | 0 |  | 209.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247838 | 247838 | 247837.9994
38952.3552 | 2 | 0 | 38952.3553 | 2 | 0 |  | 394 | 552 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 123869 | 123869 | 123868.9988
38952.3574 | 5 | 0 | 38952.3574 | 5 | 0 |  | 579 | 737 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 49487.6 | 49487.6 | 49487.5969
38952.3595 | 5 | 0 | 38952.3595 | 5 | 0 |  | 763.5 | 921.5 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 49487.6 | 49487.6 | 49487.5969
38952.3617 | 20 | 12 | 38952.3617 | 20 | 14 |  | 948.5 | 1106.5 | 1.221 | 0.7326 | 1.221 | 0.8547 | 0.01221 | 0.007326 | 0.01221 | 0.008547 | 0.004884 | 0.003663 | 30854.3062 | 41302.01 | 20345.5728
38952.3638 | 2255 | 1 | 38952.3638 | 2427 | 1 |  | 1133.5 | 1291.5 | 137.6679 | 0.06105 | 148.1685 | 0.06105 | 1.3767 | 0.0006105 | 1.4817 | 0.0006105 | 1.3761 | 1.4811 | 10.1627 | 2.1679 | 473.9904
38952.3659 | 2024 | 0 | 38952.3659 | 2025 | 0 |  | 1318 | 1476 | 123.5653 | 0 | 123.6264 | 0 | 1.2357 | 0 | 1.2363 | 0 | 1.2357 | 1.2363 | 22.499 | 22.4385 | 21.2634
38952.3681 | 2463 | 0 | 38952.3681 | 1962 | 0 |  | 1503 | 1661 | 150.3663 | 0 | 119.7802 | 0 | 1.5037 | 0 | 1.1978 | 0 | 1.5037 | 1.1978 | 0.66504 | 26.37 | 0.83862
38952.3702 | 2032 | 0 | 38952.3702 | 2009 | 0 |  | 1687.5 | 1845.5 | 124.0537 | 0 | 122.6496 | 0 | 1.2405 | 0 | 1.2265 | 0 | 1.2405 | 1.2265 | 22.0167 | 23.4136 | 20.7762

## E10-F12
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 155.3346 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
38952.3509 | 1 | 0 | 38952.3509 | 1 | 0 |  | 22 | 180 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
38952.3531 | 1 | 0 | 38952.3531 | 1 | 0 |  | 206.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254338 | 254338 | 254337.9994
38952.3552 | 3 | 0 | 38952.3552 | 3 | 0 |  | 391.5 | 549.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 84712.6667 | 84712.6667 | 84712.6648
38952.3573 | 2528 | 1 | 38952.3574 | 6 | 0 |  | 576.5 | 734.5 | 154.3346 | 0.06105 | 0.3663 | 0 | 1.5433 | 0.0006105 | 0.003663 | 0 | 1.5427 | 0.003663 | 0.6482 | 42306.3333 | 1534.3732
38952.3595 | 2443 | 1 | 38952.3595 | 5 | 0 |  | 761 | 919 | 149.1453 | 0.06105 | 0.30525 | 0 | 1.4915 | 0.0006105 | 0.0030525 | 0 | 1.4908 | 0.0030525 | 4.1515 | 50787.6 | 10018.2742
38952.3616 | 2402 | 1 | 38952.3616 | 5 | 0 |  | 945.5 | 1103.5 | 146.6422 | 0.06105 | 0.30525 | 0 | 1.4664 | 0.0006105 | 0.0030525 | 0 | 1.4658 | 0.0030525 | 5.93 | 50787.6 | 14110.2172
38952.3638 | 2281 | 1 | 38952.3638 | 2151 | 0 |  | 1130.5 | 1288.5 | 139.2552 | 0.06105 | 131.3187 | 0 | 1.3926 | 0.0006105 | 1.3132 | 0 | 1.3919 | 1.3132 | 11.5795 | 18.2882 | 4056.5892
38952.3659 | 2403 | 1 | 38952.3659 | 2328 | 0 |  | 1315.5 | 1473.5 | 146.7033 | 0.06105 | 142.1245 | 0 | 1.467 | 0.0006105 | 1.4212 | 0 | 1.4664 | 1.4212 | 5.9124 | 9.2947 | 1193.8242
38952.368 | 2471 | 1 | 38952.3681 | 2299 | 0 |  | 1500 | 1658 | 150.8547 | 0.06105 | 140.3541 | 0 | 1.5085 | 0.0006105 | 1.4035 | 0 | 1.5079 | 1.4035 | 2.9822 | 10.6733 | 698.0327
38952.3702 | 2515 | 1 | 38952.3702 | 2256 | 0 |  | 1685 | 1843 | 153.5409 | 0.06105 | 137.7289 | 0 | 1.5354 | 0.0006105 | 1.3773 | 0 | 1.5348 | 1.3773 | 1.1723 | 12.7828 | 321.6589

## E10-F11
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 156.0061 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
38952.3509 | 1 | 0 | 38952.3509 | 1 | 0 |  | 19 | 177 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
| 1 | 0 | 38952.3531 | 1 | 0 |  | 205 | 363 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
38952.3552 | 4 | 0 | 38952.3552 | 3 | 0 |  | 388.5 | 546.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 63784.5 | 85079.3333 | 63784.4976
38952.3573 | 2510 | 1 | 38952.3573 | 6 | 0 |  | 573.5 | 731.5 | 153.2357 | 0.06105 | 0.3663 | 0 | 1.5324 | 0.0006105 | 0.003663 | 0 | 1.5317 | 0.003663 | 1.8087 | 42489.6667 | 4427.5796
38952.3595 | 2175 | 1 | 38952.3595 | 5 | 0 |  | 758.5 | 916.5 | 132.7839 | 0.06105 | 0.30525 | 0 | 1.3278 | 0.0006105 | 0.0030525 | 0 | 1.3272 | 0.0030525 | 17.4968 | 51007.6 | 37863.7684
38952.3616 | 1980 | 1 | 38952.3616 | 5 | 0 |  | 943 | 1101 | 120.8791 | 0.06105 | 0.30525 | 0 | 1.2088 | 0.0006105 | 0.0030525 | 0 | 1.2082 | 0.0030525 | 29.0743 | 51007.6 | 57325.6136
38952.3637 | 2095 | 1 | 38952.3637 | 2075 | 0 |  | 1127.5 | 1285.5 | 127.8999 | 0.06105 | 126.6789 | 0 | 1.279 | 0.0006105 | 1.2668 | 0 | 1.2784 | 1.2668 | 22.0311 | 23.1508 | 8635.7788
38952.3659 | 2094 | 1 | 38952.3659 | 2147 | 0 |  | 1312.5 | 1470.5 | 127.8388 | 0.06105 | 131.0745 | 0 | 1.2784 | 0.0006105 | 1.3107 | 0 | 1.2778 | 1.3107 | 22.0995 | 19.021 | 7357.4179
38952.368 | 2539 | 1 | 38952.368 | 2375 | 0 |  | 1497.5 | 1655.5 | 155.0061 | 0.06105 | 144.9939 | 0 | 1.5501 | 0.0006105 | 1.4499 | 0 | 1.5495 | 1.4499 | 0.64876 | 7.5949 | 108.5648
38952.3701 | 2248 | 1 | 38952.3702 | 2450 | 0 |  | 1682 | 1840 | 137.2405 | 0.06105 | 149.5726 | 0 | 1.3724 | 0.0006105 | 1.4957 | 0 | 1.3718 | 1.4957 | 13.8226 | 4.3012 | 1263.4647

## E9-F12
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 155.2125 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
38952.3509 | 1 | 0 | 38952.3509 | 1 | 0 |  | 16.5 | 174.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254138 | 254138 | 254137.9994
38952.353 | 1 | 0 | 38952.353 | 1 | 0 |  | 201 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254138 | 254138 | 254137.9994
38952.3551 | 2258 | 1 | 38952.3552 | 5 | 0 |  | 386 | 544 | 137.851 | 0.06105 | 0.30525 | 0 | 1.3785 | 0.0006105 | 0.0030525 | 0 | 1.3779 | 0.0030525 | 12.5999 | 50747.6 | 28282.2688
38952.3573 | 2383 | 1 | 38952.3573 | 5 | 0 |  | 570.5 | 728.5 | 145.4823 | 0.06105 | 0.30525 | 0 | 1.4548 | 0.0006105 | 0.0030525 | 0 | 1.4542 | 0.0030525 | 6.691 | 50747.6 | 15806.852
38952.3594 | 2526 | 1 | 38952.3594 | 5 | 0 |  | 755.5 | 913.5 | 154.2125 | 0.06105 | 0.30525 | 0 | 1.5421 | 0.0006105 | 0.0030525 | 0 | 1.5415 | 0.0030525 | 0.64871 | 50747.6 | 1534.9753
38952.3616 | 2079 | 1 | 38952.3616 | 4 | 0 |  | 940 | 1098 | 126.9231 | 0.06105 | 0.2442 | 0 | 1.2692 | 0.0006105 | 0.002442 | 0 | 1.2686 | 0.002442 | 22.2993 | 63459.5 | 46165.2524
38952.3637 | 2490 | 1 | 38952.3637 | 2166 | 0 |  | 1125 | 1283 | 152.0147 | 0.06105 | 132.2344 | 0 | 1.5201 | 0.0006105 | 1.3223 | 0 | 1.5195 | 1.3223 | 2.1093 | 17.3767 | 760.6418
38952.3658 | 2172 | 1 | 38952.3658 | 1897 | 0 |  | 1309.5 | 1467.5 | 132.6007 | 0.06105 | 115.812 | 0 | 1.326 | 0.0006105 | 1.1581 | 0 | 1.3254 | 1.1581 | 17.0835 | 34.0211 | 9376.6653
38952.368 | 2487 | 1 | 38952.368 | 1890 | 0 |  | 1494.5 | 1652.5 | 151.8315 | 0.06105 | 115.3846 | 0 | 1.5183 | 0.0006105 | 1.1538 | 0 | 1.5177 | 1.1538 | 2.2303 | 34.5175 | 1395.4021
38952.3701 | 2306 | 1 | 38952.3701 | 2351 | 0 |  | 1679.5 | 1837.5 | 140.7814 | 0.06105 | 143.5287 | 0 | 1.4078 | 0.0006105 | 1.4353 | 0 | 1.4072 | 1.4353 | 10.31 | 8.1404 | 1771.8447

## E9-F11
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 152.2821 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
38952.3508 | 1 | 0 | 38952.3508 | 1 | 0 |  | 13.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38952.353 | 1 | 0 | 38952.353 | 1 | 0 |  | 198.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249338 | 249338 | 249337.9994
38952.3551 | 1995 | 1 | 38952.3551 | 5 | 0 |  | 383 | 541 | 121.7949 | 0.06105 | 0.30525 | 0 | 1.2179 | 0.0006105 | 0.0030525 | 0 | 1.2173 | 0.0030525 | 25.0442 | 49787.6 | 49738.0994
38952.3572 | 1996 | 1 | 38952.3573 | 6 | 0 |  | 568 | 726 | 121.8559 | 0.06105 | 0.3663 | 0 | 1.2186 | 0.0006105 | 0.003663 | 0 | 1.2179 | 0.003663 | 24.9815 | 41473 | 49618.3598
38952.3594 | 2478 | 1 | 38952.3594 | 5 | 0 |  | 752.5 | 910.5 | 151.2821 | 0.06105 | 0.30525 | 0 | 1.5128 | 0.0006105 | 0.0030525 | 0 | 1.5122 | 0.0030525 | 0.66128 | 49787.6 | 1534.9171
38952.3615 | 2340 | 1 | 38952.3615 | 5 | 0 |  | 937.5 | 1095.5 | 142.8571 | 0.06105 | 0.30525 | 0 | 1.4286 | 0.0006105 | 0.0030525 | 0 | 1.428 | 0.0030525 | 6.6003 | 49787.6 | 15307.2549
38952.3637 | 1974 | 1 | 38952.3637 | 1908 | 0 |  | 1122 | 1280 | 120.5128 | 0.06105 | 116.4835 | 0 | 1.2051 | 0.0006105 | 1.1648 | 0 | 1.2045 | 1.1648 | 26.4186 | 30.7327 | 12209.609
38952.3658 | 2125 | 1 | 38952.3658 | 2152 | 0 |  | 1307 | 1465 | 129.7314 | 0.06105 | 131.3797 | 0 | 1.2973 | 0.0006105 | 1.3138 | 0 | 1.2967 | 1.3138 | 17.4424 | 15.9099 | 5056.4046
38952.3679 | 2446 | 1 | 38952.368 | 2322 | 0 |  | 1491.5 | 1649.5 | 149.3284 | 0.06105 | 141.7582 | 0 | 1.4933 | 0.0006105 | 1.4176 | 0 | 1.4927 | 1.4176 | 1.9897 | 7.4238 | 327.4306
38952.3701 | 2339 | 1 | 38952.3701 | 2227 | 0 |  | 1676.5 | 1834.5 | 142.7961 | 0.06105 | 135.9585 | 0 | 1.428 | 0.0006105 | 1.3596 | 0 | 1.4274 | 1.3596 | 6.6696 | 12.0063 | 1654.8451

## E9-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 156.9219 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
38952.3508 | 1 | 0 | 38952.3508 | 1 | 0 |  | 10.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38952.3529 | 1 | 0 | 38952.353 | 1 | 0 |  | 195.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38952.3551 | 2200 | 0 | 38952.3551 | 4 | 0 |  | 380.5 | 538.5 | 134.3101 | 0 | 0.2442 | 0 | 1.3431 | 0 | 0.002442 | 0 | 1.3431 | 0.002442 | 16.8355 | 64159.5 | 15.4924
38952.3572 | 2211 | 0 | 38952.3572 | 2411 | 0 |  | 565 | 723 | 134.9817 | 0 | 147.1917 | 0 | 1.3498 | 0 | 1.4719 | 0 | 1.3498 | 1.4719 | 16.2542 | 6.6105 | 14.9044
38952.3594 | 2554 | 0 | 38952.3594 | 2408 | 0 |  | 750 | 908 | 155.9219 | 0 | 147.0085 | 0 | 1.5592 | 0 | 1.4701 | 0 | 1.5592 | 1.4701 | 0.64135 | 6.7434 | 0.91787
38952.3615 | 2032 | 0 | 38952.3615 | 2142 | 0 |  | 934.5 | 1092.5 | 124.0537 | 0 | 130.7692 | 0 | 1.2405 | 0 | 1.3077 | 0 | 1.2405 | 1.3077 | 26.4951 | 19.9991 | 25.2545
38952.3636 | 2050 | 0 | 38952.3636 | 2101 | 0 |  | 1119.5 | 1277.5 | 125.1526 | 0 | 128.2662 | 0 | 1.2515 | 0 | 1.2827 | 0 | 1.2515 | 1.2827 | 25.3844 | 22.3408 | 24.1329
38952.3658 | 2396 | 0 | 38952.3658 | 2385 | 0 |  | 1304 | 1462 | 146.2759 | 0 | 145.6044 | 0 | 1.4628 | 0 | 1.456 | 0 | 1.4628 | 1.456 | 7.278 | 7.7727 | 5.8152
38952.3679 | 2071 | 0 | 38952.3679 | 1957 | 0 |  | 1489 | 1647 | 126.4347 | 0 | 119.475 | 0 | 1.2643 | 0 | 1.1947 | 0 | 1.2643 | 1.1947 | 24.113 | 31.3429 | 22.8486
38952.37 | 2008 | 0 | 38952.3701 | 2320 | 0 |  | 1673.5 | 1831.5 | 122.5885 | 0 | 141.6361 | 0 | 1.2259 | 0 | 1.4164 | 0 | 1.2259 | 1.4164 | 28.007 | 10.7922 | 26.7811

## D8-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 157.3492 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
38952.3507 | 1 | 0 | 38952.3507 | 1 | 0 |  | 2.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38952.3528 | 1 | 0 | 38952.3529 | 1 | 0 |  | 187 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38952.355 | 4 | 0 | 38952.355 | 3 | 0 |  | 372 | 530 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 64334.5 | 85812.6667 | 64334.4976
38952.3571 | 5 | 0 | 38952.3571 | 2495 | 0 |  | 556.5 | 714.5 | 0.30525 | 0 | 152.3199 | 0 | 0.0030525 | 0 | 1.5232 | 0 | 0.0030525 | 1.5232 | 51447.6 | 3.3018 | 51447.5969
38952.3593 | 5 | 0 | 38952.3593 | 2346 | 0 |  | 741.5 | 899.5 | 0.30525 | 0 | 143.2234 | 0 | 0.0030525 | 0 | 1.4322 | 0 | 0.0030525 | 1.4322 | 51447.6 | 9.8627 | 51447.5969
38952.3614 | 2555 | 0 | 38952.3614 | 2561 | 0 |  | 926 | 1084 | 155.9829 | 0 | 156.3492 | 0 | 1.5598 | 0 | 1.5635 | 0 | 1.5598 | 1.5635 | 0.87593 | 0.63959 | 0.6839
38952.3635 | 2472 | 0 | 38952.3636 | 1998 | 0 |  | 1111 | 1269 | 150.9158 | 0 | 121.978 | 0 | 1.5092 | 0 | 1.2198 | 0 | 1.5092 | 1.2198 | 4.2629 | 28.998 | 2.7538
38952.3657 | 2428 | 0 | 38952.3657 | 2129 | 0 |  | 1295.5 | 1453.5 | 148.2295 | 0 | 129.9756 | 0 | 1.4823 | 0 | 1.2998 | 0 | 1.4823 | 1.2998 | 6.1524 | 21.0606 | 4.6701
38952.3678 | 2073 | 0 | 38952.3678 | 2117 | 0 |  | 1480.5 | 1638.5 | 126.5568 | 0 | 129.243 | 0 | 1.2656 | 0 | 1.2924 | 0 | 1.2656 | 1.2924 | 24.3309 | 21.7468 | 23.0654
38952.37 | 1888 | 0 | 38952.37 | 2165 | 0 |  | 1665.5 | 1823.5 | 115.2625 | 0 | 132.1734 | 0 | 1.1526 | 0 | 1.3217 | 0 | 1.1526 | 1.3217 | 36.5138 | 19.0476 | 35.3611

## D8-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 153.9915 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
38952.3507 | 1 | 0 | 38952.3507 | 1 | 0 |  | -0.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38952.3528 | 1 | 0 | 38952.3528 | 1 | 0 |  | 184.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
38952.3549 | 1 | 0 | 38952.355 | 1839 | 0 |  | 369 | 527 | 0.06105 | 0 | 112.2711 | 0 | 0.0006105 | 0 | 1.1227 | 0 | 0.0006105 | 1.1227 | 252138 | 37.1604 | 252137.9994
38952.3571 | 2 | 0 | 38952.3571 | 2048 | 0 |  | 553.5 | 711.5 | 0.1221 | 0 | 125.0305 | 0 | 0.001221 | 0 | 1.2503 | 0 | 0.001221 | 1.2503 | 126019 | 23.1631 | 126018.9988
38952.3592 | 3 | 0 | 38952.3592 | 2452 | 0 |  | 738.5 | 896.5 | 0.18315 | 0 | 149.6947 | 0 | 0.0018315 | 0 | 1.4969 | 0 | 0.0018315 | 1.4969 | 83979.3333 | 2.8703 | 83979.3315
38952.3614 | 2043 | 0 | 38952.3614 | 2060 | 0 |  | 923.5 | 1081.5 | 124.7253 | 0 | 125.7631 | 0 | 1.2473 | 0 | 1.2576 | 0 | 1.2473 | 1.2576 | 23.4645 | 22.4456 | 22.2173
38952.3635 | 2416 | 0 | 38952.3635 | 2257 | 0 |  | 1108 | 1266 | 147.4969 | 0 | 137.79 | 0 | 1.475 | 0 | 1.3779 | 0 | 1.475 | 1.3779 | 4.4031 | 11.7581 | 2.9282
38952.3656 | 2141 | 0 | 38952.3657 | 2506 | 0 |  | 1293 | 1451 | 130.7082 | 0 | 152.9915 | 0 | 1.3071 | 0 | 1.5299 | 0 | 1.3071 | 1.5299 | 17.8132 | 0.65363 | 16.5061
38952.3678 | 1612 | 0 | 38952.3678 | 2113 | 0 |  | 1477.5 | 1635.5 | 98.4127 | 0 | 128.9988 | 0 | 0.98413 | 0 | 1.29 | 0 | 0.98413 | 1.29 | 56.4752 | 19.3743 | 55.4911
38952.3699 | 2019 | 0 | 38952.3699 | 2103 | 0 |  | 1662.5 | 1820.5 | 123.2601 | 0 | 128.3883 | 0 | 1.2326 | 0 | 1.2839 | 0 | 1.2326 | 1.2839 | 24.9321 | 19.942 | 23.6995

## D7-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 151.4884 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
38952.3506 | 1 | 0 | 38952.3506 | 1 | 0 |  | -9 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38952.3527 | 1 | 0 | 38952.3527 | 1 | 0 |  | 176 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38952.3548 | 1 | 0 | 38952.3549 | 1 | 0 |  | 360.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248038 | 248038 | 248037.9994
38952.357 | 5 | 0 | 38952.357 | 2313 | 0 |  | 545.5 | 703.5 | 0.30525 | 0 | 141.2088 | 0 | 0.0030525 | 0 | 1.4121 | 0 | 0.0030525 | 1.4121 | 49527.6 | 7.2797 | 49527.5969
38952.3591 | 5 | 0 | 38952.3591 | 2279 | 0 |  | 730 | 888 | 0.30525 | 0 | 139.1331 | 0 | 0.0030525 | 0 | 1.3913 | 0 | 0.0030525 | 1.3913 | 49527.6 | 8.8802 | 49527.5969
38952.3613 | 498 | 0 | 38952.3613 | 2317 | 0 |  | 915 | 1073 | 30.4029 | 0 | 141.453 | 0 | 0.30403 | 0 | 1.4145 | 0 | 0.30403 | 1.4145 | 398.2691 | 7.0945 | 397.965
38952.3634 | 2248 | 0 | 38952.3634 | 2181 | 0 |  | 1099.5 | 1257.5 | 137.2405 | 0 | 133.1502 | 0 | 1.3724 | 0 | 1.3315 | 0 | 1.3724 | 1.3315 | 10.3817 | 13.7726 | 9.0093
38952.3655 | 2369 | 0 | 38952.3656 | 1960 | 0 |  | 1284.5 | 1442.5 | 144.6276 | 0 | 119.6581 | 0 | 1.4463 | 0 | 1.1966 | 0 | 1.4463 | 1.1966 | 4.7438 | 26.601 | 3.2975
38952.3677 | 1879 | 0 | 38952.3677 | 2465 | 0 |  | 1469.5 | 1627.5 | 114.7131 | 0 | 150.4884 | 0 | 1.1471 | 0 | 1.5049 | 0 | 1.1471 | 1.5049 | 32.0585 | 0.6645 | 30.9114
38952.3698 | 1942 | 0 | 38952.3698 | 1969 | 0 |  | 1654 | 1812 | 118.5592 | 0 | 120.2076 | 0 | 1.1856 | 0 | 1.2021 | 0 | 1.1856 | 1.2021 | 27.7745 | 26.0223 | 26.5889

## D7-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 156.1893 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
38952.3505 | 1 | 0 | 38952.3506 | 1 | 0 |  | -11.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38952.3527 | 1 | 0 | 38952.3527 | 1 | 0 |  | 173 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38952.3548 | 1 | 0 | 38952.3548 | 1 | 0 |  | 358 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
38952.357 | 2 | 0 | 38952.357 | 2271 | 0 |  | 542.5 | 700.5 | 0.1221 | 0 | 138.6447 | 0 | 0.001221 | 0 | 1.3864 | 0 | 0.001221 | 1.3864 | 127819 | 12.6543 | 127818.9988
38952.3591 | 2 | 0 | 38952.3591 | 2153 | 0 |  | 727.5 | 885.5 | 0.1221 | 0 | 131.4408 | 0 | 0.001221 | 0 | 1.3144 | 0 | 0.001221 | 1.3144 | 127819 | 18.8286 | 127818.9988
38952.3612 | 1950 | 1 | 38952.3613 | 2425 | 1 |  | 912 | 1070 | 119.0476 | 0.06105 | 148.0464 | 0.06105 | 1.1905 | 0.0006105 | 1.4805 | 0.0006105 | 1.1899 | 1.4799 | 31.5084 | 5.5097 | 3171.7229
38952.3634 | 1935 | 0 | 38952.3634 | 2214 | 0 |  | 1097 | 1255 | 118.1319 | 0 | 135.1648 | 0 | 1.1813 | 0 | 1.3516 | 0 | 1.1813 | 1.3516 | 32.216 | 15.5547 | 31.0347
38952.3655 | 2174 | 0 | 38952.3655 | 2542 | 0 |  | 1281.5 | 1439.5 | 132.7228 | 0 | 155.1893 | 0 | 1.3272 | 0 | 1.5519 | 0 | 1.3272 | 1.5519 | 17.6808 | 0.64437 | 16.3535
38952.3677 | 1841 | 0 | 38952.3677 | 2390 | 0 |  | 1466.5 | 1624.5 | 112.3932 | 0 | 145.9096 | 0 | 1.1239 | 0 | 1.4591 | 0 | 1.1239 | 1.4591 | 38.9669 | 7.0452 | 37.8429
38952.3698 | 1476 | 0 | 38952.3698 | 2411 | 0 |  | 1651 | 1809 | 90.1099 | 0 | 147.1917 | 0 | 0.9011 | 0 | 1.4719 | 0 | 0.9011 | 1.4719 | 73.332 | 6.1128 | 72.4309

## D7-D8
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 136.4701 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
38952.3505 | 1 | 0 | 38952.3505 | 1 | 0 |  | -14.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38952.3527 | 1 | 0 | 38952.3527 | 2 | 0 |  | 170.5 | 328.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 223438 | 111669 | 223437.9994
38952.3548 | 1 | 0 | 38952.3548 | 1 | 0 |  | 355 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223438 | 223438 | 223437.9994
38952.3569 | 3 | 0 | 38952.3569 | 2 | 0 |  | 539.5 | 697.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 74412.6667 | 111669 | 74412.6648
38952.3591 | 2 | 0 | 38952.3591 | 2 | 0 |  | 724.5 | 882.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 111669 | 111669 | 111668.9988
38952.3612 | 640 | 592 | 38952.3612 | 1782 | 133 |  | 909.5 | 1067.5 | 39.072 | 36.1416 | 108.7912 | 8.1197 | 0.39072 | 0.36142 | 1.0879 | 0.081197 | 0.029304 | 1.0067 | 67.5342 | 25.5798 | 34.524
38952.3633 | 1963 | 0 | 38952.3634 | 2219 | 0 |  | 1094 | 1252 | 119.8413 | 0 | 135.4701 | 0 | 1.1984 | 0 | 1.3547 | 0 | 1.1984 | 1.3547 | 13.8757 | 0.73817 | 12.6773
38952.3655 | 2036 | 0 | 38952.3655 | 2071 | 0 |  | 1279 | 1437 | 124.2979 | 0 | 126.4347 | 0 | 1.243 | 0 | 1.2643 | 0 | 1.243 | 1.2643 | 9.7927 | 7.9372 | 8.5498
38952.3676 | 2195 | 0 | 38952.3676 | 1761 | 0 |  | 1463.5 | 1621.5 | 134.0049 | 0 | 107.5092 | 0 | 1.34 | 0 | 1.0751 | 0 | 1.34 | 1.0751 | 1.8396 | 26.9381 | 0.49959
38952.3698 | 1817 | 0 | 38952.3698 | 2072 | 0 |  | 1648.5 | 1806.5 | 110.928 | 0 | 126.4957 | 0 | 1.1093 | 0 | 1.265 | 0 | 1.1093 | 1.265 | 23.0259 | 7.8851 | 21.9166

## C6-F12
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 149.4127 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
38952.3505 | 1 | 0 | 38952.3505 | 1 | 0 |  | -17.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244638 | 244638 | 244637.9994
38952.3526 | 1 | 0 | 38952.3526 | 1 | 0 |  | 167.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244638 | 244638 | 244637.9994
38952.3548 | 1 | 0 | 38952.3548 | 1 | 0 |  | 352.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244638 | 244638 | 244637.9994
38952.3569 | 4 | 0 | 38952.3569 | 3 | 0 |  | 537 | 695 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 61084.5 | 81479.3333 | 61084.4976
38952.359 | 4 | 0 | 38952.359 | 3 | 0 |  | 721.5 | 879.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 61084.5 | 81479.3333 | 61084.4976
38952.3612 | 3 | 0 | 38952.3612 | 2 | 0 |  | 906.5 | 1064.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 81479.3333 | 122269 | 81479.3315
38952.3633 | 5 | 0 | 38952.3633 | 2402 | 0 |  | 1091.5 | 1249.5 | 0.30525 | 0 | 146.6422 | 0 | 0.0030525 | 0 | 1.4664 | 0 | 0.0030525 | 1.4664 | 48847.6 | 1.8893 | 48847.5969
38952.3654 | 4 | 0 | 38952.3655 | 2364 | 0 |  | 1276 | 1434 | 0.2442 | 0 | 144.3223 | 0 | 0.002442 | 0 | 1.4432 | 0 | 0.002442 | 1.4432 | 61084.5 | 3.5271 | 61084.4976
38952.3676 | 4 | 0 | 38952.3676 | 2118 | 0 |  | 1461 | 1619 | 0.2442 | 0 | 129.304 | 0 | 0.002442 | 0 | 1.293 | 0 | 0.002442 | 1.293 | 61084.5 | 15.5515 | 61084.4976
38952.3697 | 3 | 0 | 38952.3697 | 2431 | 0 |  | 1645.5 | 1803.5 | 0.18315 | 0 | 148.4127 | 0 | 0.0018315 | 0 | 1.4841 | 0 | 0.0018315 | 1.4841 | 81479.3333 | 0.6738 | 81479.3315

## C6-F11
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 147.1538 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
38952.3504 | 1 | 0 | 38952.3505 | 1 | 0 |  | -20 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.3526 | 1 | 0 | 38952.3526 | 1 | 0 |  | 164.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.3547 | 1 | 0 | 38952.3547 | 1 | 0 |  | 349.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240938 | 240938 | 240937.9994
38952.3569 | 5 | 0 | 38952.3569 | 4 | 0 |  | 534 | 692 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 48107.6 | 60159.5 | 48107.5969
38952.359 | 5 | 0 | 38952.359 | 4 | 0 |  | 719 | 877 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 48107.6 | 60159.5 | 48107.5969
38952.3611 | 5 | 0 | 38952.3611 | 4 | 0 |  | 903.5 | 1061.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 48107.6 | 60159.5 | 48107.5969
38952.3633 | 5 | 0 | 38952.3633 | 2386 | 0 |  | 1088.5 | 1246.5 | 0.30525 | 0 | 145.6654 | 0 | 0.0030525 | 0 | 1.4567 | 0 | 0.0030525 | 1.4567 | 48107.6 | 1.0218 | 48107.5969
38952.3654 | 4 | 0 | 38952.3654 | 1985 | 0 |  | 1273.5 | 1431.5 | 0.2442 | 0 | 121.1844 | 0 | 0.002442 | 0 | 1.2118 | 0 | 0.002442 | 1.2118 | 60159.5 | 21.4297 | 60159.4976
38952.3675 | 4 | 0 | 38952.3676 | 2394 | 0 |  | 1458 | 1616 | 0.2442 | 0 | 146.1538 | 0 | 0.002442 | 0 | 1.4615 | 0 | 0.002442 | 1.4615 | 60159.5 | 0.68421 | 60159.4976
38952.3697 | 4 | 0 | 38952.3697 | 1981 | 0 |  | 1643 | 1801 | 0.2442 | 0 | 120.9402 | 0 | 0.002442 | 0 | 1.2094 | 0 | 0.002442 | 1.2094 | 60159.5 | 21.6749 | 60159.4976

## C6-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 155.7619 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
38952.3504 | 1 | 0 | 38952.3504 | 1 | 0 |  | -23 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38952.3525 | 1 | 0 | 38952.3526 | 1 | 0 |  | 161.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38952.3547 | 1 | 0 | 38952.3547 | 1 | 0 |  | 346.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
38952.3568 | 5 | 0 | 38952.3568 | 2336 | 0 |  | 531.5 | 689.5 | 0.30525 | 0 | 142.6129 | 0 | 0.0030525 | 0 | 1.4261 | 0 | 0.0030525 | 1.4261 | 50927.6 | 9.22 | 50927.5969
38952.359 | 5 | 0 | 38952.359 | 2437 | 0 |  | 716.5 | 874.5 | 0.30525 | 0 | 148.779 | 0 | 0.0030525 | 0 | 1.4878 | 0 | 0.0030525 | 1.4878 | 50927.6 | 4.6935 | 50927.5969
38952.3611 | 5 | 0 | 38952.3611 | 2451 | 0 |  | 901 | 1059 | 0.30525 | 0 | 149.6337 | 0 | 0.0030525 | 0 | 1.4963 | 0 | 0.0030525 | 1.4963 | 50927.6 | 4.0955 | 50927.5969
38952.3632 | 5 | 0 | 38952.3633 | 2535 | 0 |  | 1085.5 | 1243.5 | 0.30525 | 0 | 154.7619 | 0 | 0.0030525 | 0 | 1.5476 | 0 | 0.0030525 | 1.5476 | 50927.6 | 0.64615 | 50927.5969
38952.3654 | 4 | 0 | 38952.3654 | 2398 | 0 |  | 1270.5 | 1428.5 | 0.2442 | 0 | 146.398 | 0 | 0.002442 | 0 | 1.464 | 0 | 0.002442 | 1.464 | 63684.5 | 6.3962 | 63684.4976
38952.3675 | 4 | 0 | 38952.3675 | 2025 | 0 |  | 1455.5 | 1613.5 | 0.2442 | 0 | 123.6264 | 0 | 0.002442 | 0 | 1.2363 | 0 | 0.002442 | 1.2363 | 63684.5 | 25.9941 | 63684.4976
38952.3697 | 4 | 0 | 38952.3697 | 2123 | 0 |  | 1640 | 1798 | 0.2442 | 0 | 129.6093 | 0 | 0.002442 | 0 | 1.2961 | 0 | 0.002442 | 1.2961 | 63684.5 | 20.178 | 63684.4976

## C6-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 155.1514 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
38952.3504 | 1 | 0 | 38952.3504 | 2 | 0 |  | -25.5 | 132.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 254038 | 126969 | 254037.9994
38952.3525 | 1 | 0 | 38952.3525 | 1 | 0 |  | 159 | 317 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
38952.3547 | 1 | 0 | 38952.3547 | 1 | 0 |  | 344 | 502 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
38952.3568 | 2 | 0 | 38952.3568 | 1958 | 0 |  | 528.5 | 686.5 | 0.1221 | 0 | 119.536 | 0 | 0.001221 | 0 | 1.1954 | 0 | 0.001221 | 1.1954 | 126969 | 29.7947 | 126968.9988
38952.3589 | 2 | 0 | 38952.3589 | 2525 | 0 |  | 713.5 | 871.5 | 0.1221 | 0 | 154.1514 | 0 | 0.001221 | 0 | 1.5415 | 0 | 0.001221 | 1.5415 | 126969 | 0.64871 | 126968.9988
38952.3611 | 2 | 0 | 38952.3611 | 2179 | 0 |  | 898 | 1056 | 0.1221 | 0 | 133.0281 | 0 | 0.001221 | 0 | 1.3303 | 0 | 0.001221 | 1.3303 | 126969 | 16.6306 | 126968.9988
38952.3632 | 5 | 0 | 38952.3632 | 2130 | 0 |  | 1083 | 1241 | 0.30525 | 0 | 130.0366 | 0 | 0.0030525 | 0 | 1.3004 | 0 | 0.0030525 | 1.3004 | 50727.6 | 19.3136 | 50727.5969
38952.3653 | 4 | 0 | 38952.3654 | 2005 | 0 |  | 1267.5 | 1425.5 | 0.2442 | 0 | 122.4054 | 0 | 0.002442 | 0 | 1.2241 | 0 | 0.002442 | 1.2241 | 63434.5 | 26.7521 | 63434.4976
38952.3675 | 4 | 0 | 38952.3675 | 2007 | 0 |  | 1452.5 | 1610.5 | 0.2442 | 0 | 122.5275 | 0 | 0.002442 | 0 | 1.2253 | 0 | 0.002442 | 1.2253 | 63434.5 | 26.6258 | 63434.4976
38952.3696 | 4 | 0 | 38952.3696 | 2176 | 0 |  | 1637.5 | 1795.5 | 0.2442 | 0 | 132.8449 | 0 | 0.002442 | 0 | 1.3284 | 0 | 0.002442 | 1.3284 | 63434.5 | 16.7914 | 63434.4976

## C5-F12
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 140.4383 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
38952.3503 | 1 | 0 | 38952.3503 | 1 | 0 |  | -34 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38952.3524 | 1 | 0 | 38952.3524 | 1 | 0 |  | 150.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38952.3546 | 1 | 0 | 38952.3546 | 1 | 0 |  | 335.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 229938 | 229938 | 229937.9994
38952.3567 | 4 | 0 | 38952.3567 | 3 | 0 |  | 520 | 678 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 57409.5 | 76579.3333 | 57409.4976
38952.3588 | 4 | 0 | 38952.3589 | 3 | 0 |  | 705 | 863 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 57409.5 | 76579.3333 | 57409.4976
38952.361 | 3 | 0 | 38952.361 | 3 | 0 |  | 889.5 | 1047.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76579.3333 | 76579.3333 | 76579.3315
38952.3631 | 5 | 0 | 38952.3631 | 2007 | 0 |  | 1074.5 | 1232.5 | 0.30525 | 0 | 122.5275 | 0 | 0.0030525 | 0 | 1.2253 | 0 | 0.0030525 | 1.2253 | 45907.6 | 14.6178 | 45907.5969
38952.3653 | 5 | 0 | 38952.3653 | 1982 | 0 |  | 1259.5 | 1417.5 | 0.30525 | 0 | 121.0012 | 0 | 0.0030525 | 0 | 1.21 | 0 | 0.0030525 | 1.21 | 45907.6 | 16.0636 | 45907.5969
38952.3674 | 4 | 0 | 38952.3674 | 2138 | 0 |  | 1444 | 1602 | 0.2442 | 0 | 130.525 | 0 | 0.002442 | 0 | 1.3053 | 0 | 0.002442 | 1.3053 | 57409.5 | 7.5949 | 57409.4976
38952.3695 | 3 | 0 | 38952.3695 | 2284 | 0 |  | 1629 | 1787 | 0.18315 | 0 | 139.4383 | 0 | 0.0018315 | 0 | 1.3944 | 0 | 0.0018315 | 1.3944 | 76579.3333 | 0.71716 | 76579.3315

## C5-F11
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 140.7436 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
38952.3502 | 1 | 0 | 38952.3503 | 1 | 0 |  | -37 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38952.3524 | 1 | 0 | 38952.3524 | 1 | 0 |  | 148 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38952.3545 | 1 | 0 | 38952.3545 | 1 | 0 |  | 332.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 230438 | 230438 | 230437.9994
38952.3567 | 5 | 0 | 38952.3567 | 4 | 0 |  | 517.5 | 675.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 46007.6 | 57534.5 | 46007.5969
38952.3588 | 5 | 0 | 38952.3588 | 4 | 0 |  | 702 | 860 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 46007.6 | 57534.5 | 46007.5969
38952.3609 | 5 | 0 | 38952.361 | 4 | 0 |  | 887 | 1045 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 46007.6 | 57534.5 | 46007.5969
38952.3631 | 5 | 0 | 38952.3631 | 1665 | 0 |  | 1071.5 | 1229.5 | 0.30525 | 0 | 101.6484 | 0 | 0.0030525 | 0 | 1.0165 | 0 | 0.0030525 | 1.0165 | 46007.6 | 38.4613 | 46007.5969
38952.3652 | 4 | 0 | 38952.3652 | 2129 | 0 |  | 1256.5 | 1414.5 | 0.2442 | 0 | 129.9756 | 0 | 0.002442 | 0 | 1.2998 | 0 | 0.002442 | 1.2998 | 57534.5 | 8.2846 | 57534.4976
38952.3674 | 4 | 0 | 38952.3674 | 2226 | 0 |  | 1441.5 | 1599.5 | 0.2442 | 0 | 135.8974 | 0 | 0.002442 | 0 | 1.359 | 0 | 0.002442 | 1.359 | 57534.5 | 3.566 | 57534.4976
38952.3695 | 3 | 0 | 38952.3695 | 2289 | 0 |  | 1626 | 1784 | 0.18315 | 0 | 139.7436 | 0 | 0.0018315 | 0 | 1.3974 | 0 | 0.0018315 | 1.3974 | 76746 | 0.7156 | 76745.9982

## C5-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 155.6398 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
38952.3502 | 1 | 0 | 38952.3502 | 1 | 0 |  | -39.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38952.3523 | 1 | 0 | 38952.3524 | 1 | 0 |  | 145 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38952.3545 | 1 | 0 | 38952.3545 | 1 | 0 |  | 330 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
38952.3566 | 5 | 0 | 38952.3566 | 2283 | 0 |  | 514.5 | 672.5 | 0.30525 | 0 | 139.3773 | 0 | 0.0030525 | 0 | 1.3938 | 0 | 0.0030525 | 1.3938 | 50887.6 | 11.668 | 50887.5969
38952.3588 | 5 | 0 | 38952.3588 | 2533 | 0 |  | 699.5 | 857.5 | 0.30525 | 0 | 154.6398 | 0 | 0.0030525 | 0 | 1.5464 | 0 | 0.0030525 | 1.5464 | 50887.6 | 0.64666 | 50887.5969
38952.3609 | 4 | 0 | 38952.3609 | 2356 | 0 |  | 884 | 1042 | 0.2442 | 0 | 143.8339 | 0 | 0.002442 | 0 | 1.4383 | 0 | 0.002442 | 1.4383 | 63634.5 | 8.208 | 63634.4976
38952.363 | 5 | 0 | 38952.3631 | 2411 | 0 |  | 1069 | 1227 | 0.30525 | 0 | 147.1917 | 0 | 0.0030525 | 0 | 1.4719 | 0 | 0.0030525 | 1.4719 | 50887.6 | 5.7395 | 50887.5969
38952.3652 | 5 | 0 | 38952.3652 | 2286 | 1 |  | 1253.5 | 1411.5 | 0.30525 | 0 | 139.5604 | 0.06105 | 0.0030525 | 0 | 1.3956 | 0.0006105 | 0.0030525 | 1.395 | 50887.6 | 11.5702 | 50887.5969
38952.3673 | 4 | 1 | 38952.3673 | 2310 | 0 |  | 1438.5 | 1596.5 | 0.2442 | 0.06105 | 141.0256 | 0 | 0.002442 | 0.0006105 | 1.4103 | 0 | 0.0018315 | 1.4103 | 38276.7997 | 27.3978 | 54718.6851
38952.3695 | 4 | 0 | 38952.3695 | 2202 | 0 |  | 1623.5 | 1781.5 | 0.2442 | 0 | 134.4322 | 0 | 0.002442 | 0 | 1.3443 | 0 | 0.002442 | 1.3443 | 63634.5 | 15.7757 | 63634.4976

## C5-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 153.9304 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
38952.3502 | 1 | 0 | 38952.3502 | 1 | 0 |  | -42.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38952.3523 | 1 | 0 | 38952.3523 | 1 | 0 |  | 142.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
38952.3545 | 1 | 0 | 38952.3545 | 38 | 0 |  | 327 | 485 | 0.06105 | 0 | 2.3199 | 0 | 0.0006105 | 0 | 0.023199 | 0 | 0.0006105 | 0.023199 | 252038 | 6535.2105 | 252037.9994
38952.3566 | 1 | 0 | 38952.3566 | 2135 | 0 |  | 511.5 | 669.5 | 0.06105 | 0 | 130.3419 | 0 | 0.0006105 | 0 | 1.3034 | 0 | 0.0006105 | 1.3034 | 252038 | 18.0974 | 252037.9994
38952.3587 | 2 | 0 | 38952.3587 | 2267 | 0 |  | 696.5 | 854.5 | 0.1221 | 0 | 138.4005 | 0 | 0.001221 | 0 | 1.384 | 0 | 0.001221 | 1.384 | 125969 | 11.221 | 125968.9988
38952.3609 | 1 | 0 | 38952.3609 | 2245 | 0 |  | 881.5 | 1039.5 | 0.06105 | 0 | 137.0574 | 0 | 0.0006105 | 0 | 1.3706 | 0 | 0.0006105 | 1.3706 | 252038 | 12.3109 | 252037.9994
38952.363 | 5 | 1 | 38952.363 | 2060 | 1 |  | 1066 | 1224 | 0.30525 | 0.06105 | 125.7631 | 0.06105 | 0.0030525 | 0.0006105 | 1.2576 | 0.0006105 | 0.002442 | 1.257 | 543847.8567 | 28.2701 | 55437.8064
38952.3652 | 4 | 1 | 38952.3652 | 2489 | 1 |  | 1251 | 1409 | 0.2442 | 0.06105 | 151.9536 | 0.06105 | 0.002442 | 0.0006105 | 1.5195 | 0.0006105 | 0.0018315 | 1.5189 | 3409.3073 | 1.4117 | 3502.8312
38952.3673 | 4 | 1 | 38952.3673 | 2505 | 1 |  | 1435.5 | 1593.5 | 0.2442 | 0.06105 | 152.9304 | 0.06105 | 0.002442 | 0.0006105 | 1.5293 | 0.0006105 | 0.0018315 | 1.5287 | 1679.6756 | 0.68086 | 1701.7172
38952.3694 | 3 | 1 | 38952.3694 | 2278 | 1 |  | 1620.5 | 1778.5 | 0.18315 | 0.06105 | 139.072 | 0.06105 | 0.0018315 | 0.0006105 | 1.3907 | 0.0006105 | 0.001221 | 1.3901 | 34236.8802 | 18.6715 | 39607.9017

## C5-C6
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38952.3501 | 1 | 0 | 38952.3501 | 1 | 0 |  | -51 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3522 | 1 | 0 | 38952.3522 | 1 | 0 |  | 134 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3544 | 1 | 0 | 38952.3544 | 1 | 0 |  | 318.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3565 | 2 | 0 | 38952.3565 | 3 | 0 |  | 503.5 | 661.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.3586 | 2 | 0 | 38952.3587 | 2 | 0 |  | 688 | 846 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3608 | 2 | 0 | 38952.3608 | 2 | 0 |  | 873 | 1031 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3629 | 1021 | 1065 | 38952.3629 | 940 | 909 |  | 1057.5 | 1215.5 | 62.3321 | 65.0183 | 57.3871 | 55.4945 | 0.62332 | 0.65018 | 0.57387 | 0.55495 | 0.026862 | 0.018926 | 1682.3224 | 5092.9016 | 2.4882
38952.3651 | 1190 | 1167 | 38952.3651 | 1085 | 1054 |  | 1242.5 | 1400.5 | 72.6496 | 71.2454 | 66.2393 | 64.3468 | 0.7265 | 0.71245 | 0.66239 | 0.64347 | 0.014042 | 0.018926 | 2243.2402 | 6430.9107 | 20.5865
38952.3672 | 922 | 941 | 38952.3672 | 1019 | 986 |  | 1427.5 | 1585.5 | 56.2882 | 57.4481 | 62.21 | 60.1954 | 0.56288 | 0.57448 | 0.6221 | 0.60195 | 0.0116 | 0.020147 | 3654.3059 | 6923.0699 | 26.1913
38952.3693 | 933 | 912 | 38952.3694 | 1039 | 1006 |  | 1612 | 1770 | 56.9597 | 55.6777 | 63.431 | 61.4164 | 0.5696 | 0.55678 | 0.63431 | 0.61416 | 0.012821 | 0.020147 | 4639.5196 | 20567.8766 | 29.246

## B4-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 154.663 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
38952.35 | 1 | 0 | 38952.35 | 1 | 0 |  | -59.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38952.3521 | 1 | 0 | 38952.3521 | 1 | 0 |  | 125.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38952.3543 | 1 | 0 | 38952.3543 | 1 | 0 |  | 310.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253238 | 253238 | 253237.9994
38952.3564 | 5 | 0 | 38952.3564 | 1940 | 0 |  | 495 | 653 | 0.30525 | 0 | 118.4371 | 0 | 0.0030525 | 0 | 1.1844 | 0 | 0.0030525 | 1.1844 | 50567.6 | 30.5866 | 50567.5969
38952.3585 | 5 | 0 | 38952.3586 | 2517 | 0 |  | 679.5 | 837.5 | 0.30525 | 0 | 153.663 | 0 | 0.0030525 | 0 | 1.5366 | 0 | 0.0030525 | 1.5366 | 50567.6 | 0.65077 | 50567.5969
38952.3607 | 5 | 0 | 38952.3607 | 2192 | 0 |  | 864.5 | 1022.5 | 0.30525 | 0 | 133.8217 | 0 | 0.0030525 | 0 | 1.3382 | 0 | 0.0030525 | 1.3382 | 50567.6 | 15.5739 | 50567.5969
38952.3628 | 5 | 0 | 38952.3628 | 2334 | 0 |  | 1049.5 | 1207.5 | 0.30525 | 0 | 142.4908 | 0 | 0.0030525 | 0 | 1.4249 | 0 | 0.0030525 | 1.4249 | 50567.6 | 8.5424 | 50567.5969
38952.365 | 1643 | 0 | 38952.365 | 1963 | 0 |  | 1234 | 1392 | 100.3053 | 0 | 119.8413 | 0 | 1.0031 | 0 | 1.1984 | 0 | 1.0031 | 1.1984 | 54.1923 | 29.0565 | 53.1893
38952.3671 | 1326 | 0 | 38952.3671 | 2136 | 0 |  | 1419 | 1577 | 80.9524 | 0 | 130.4029 | 0 | 0.80952 | 0 | 1.304 | 0 | 0.80952 | 1.304 | 91.0543 | 18.6039 | 90.2448
38952.3692 | 2163 | 0 | 38952.3692 | 2477 | 0 |  | 1603.5 | 1761.5 | 132.0513 | 0 | 151.221 | 0 | 1.3205 | 0 | 1.5122 | 0 | 1.3205 | 1.5122 | 17.1234 | 2.2761 | 15.8029

## B4-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 154.3578 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
38952.35 | 1 | 0 | 38952.35 | 1 | 0 |  | -62 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38952.3521 | 1 | 0 | 38952.3521 | 1 | 0 |  | 122.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252738 | 252738 | 252737.9994
38952.3542 | 2 | 0 | 38952.3542 | 1 | 0 |  | 307.5 | 465.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 126319 | 252738 | 126318.9988
38952.3564 | 2 | 0 | 38952.3564 | 2292 | 0 |  | 492.5 | 650.5 | 0.1221 | 0 | 139.9267 | 0 | 0.001221 | 0 | 1.3993 | 0 | 0.001221 | 1.3993 | 126319 | 10.3133 | 126318.9988
38952.3585 | 2 | 0 | 38952.3585 | 2121 | 0 |  | 677 | 835 | 0.1221 | 0 | 129.4872 | 0 | 0.001221 | 0 | 1.2949 | 0 | 0.001221 | 1.2949 | 126319 | 19.207 | 126318.9988
38952.3606 | 2 | 0 | 38952.3607 | 1963 | 0 |  | 861.5 | 1019.5 | 0.1221 | 0 | 119.8413 | 0 | 0.001221 | 0 | 1.1984 | 0 | 0.001221 | 1.1984 | 126319 | 28.8018 | 126318.9988
38952.3628 | 5 | 0 | 38952.3628 | 2258 | 0 |  | 1046.5 | 1204.5 | 0.30525 | 0 | 137.851 | 0 | 0.0030525 | 0 | 1.3785 | 0 | 0.0030525 | 1.3785 | 50467.6 | 11.9743 | 50467.5969
38952.3649 | 1990 | 0 | 38952.3649 | 2193 | 0 |  | 1231.5 | 1389.5 | 121.4896 | 0 | 133.8828 | 0 | 1.2149 | 0 | 1.3388 | 0 | 1.2149 | 1.3388 | 27.0543 | 15.2932 | 25.8394
38952.3671 | 1271 | 0 | 38952.3671 | 2512 | 0 |  | 1416 | 1574 | 77.5946 | 0 | 153.3578 | 0 | 0.77595 | 0 | 1.5336 | 0 | 0.77595 | 1.5336 | 98.9284 | 0.65207 | 98.1525
38952.3692 | 1839 | 0 | 38952.3692 | 2226 | 0 |  | 1601 | 1759 | 112.2711 | 0 | 135.8974 | 0 | 1.1227 | 0 | 1.359 | 0 | 1.1227 | 1.359 | 37.4867 | 13.584 | 36.364

## B4-D8
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 157.3492 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
38952.3499 | 1 | 0 | 38952.3499 | 1 | 0 |  | -65 | 93 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38952.3521 | 1 | 0 | 38952.3521 | 2 | 0 |  | 120 | 278 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 257638 | 128769 | 257637.9994
38952.3542 | 1 | 0 | 38952.3542 | 1 | 0 |  | 304.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
38952.3563 | 2 | 0 | 38952.3564 | 2 | 0 |  | 489.5 | 647.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128769 | 128769 | 128768.9988
38952.3585 | 2 | 0 | 38952.3585 | 2 | 0 |  | 674 | 832 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128769 | 128769 | 128768.9988
38952.3606 | 2 | 0 | 38952.3606 | 2 | 0 |  | 859 | 1017 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 128769 | 128769 | 128768.9988
38952.3628 | 5 | 0 | 38952.3628 | 2561 | 0 |  | 1043.5 | 1201.5 | 0.30525 | 0 | 156.3492 | 0 | 0.0030525 | 0 | 1.5635 | 0 | 0.0030525 | 1.5635 | 51447.6 | 0.63959 | 51447.5969
38952.3649 | 1936 | 0 | 38952.3649 | 2057 | 0 |  | 1228.5 | 1386.5 | 118.1929 | 0 | 125.58 | 0 | 1.1819 | 0 | 1.2558 | 0 | 1.1819 | 1.2558 | 33.1291 | 25.298 | 31.9472
38952.367 | 1065 | 0 | 38952.367 | 2011 | 0 |  | 1413.5 | 1571.5 | 65.0183 | 0 | 122.7717 | 0 | 0.65018 | 0 | 1.2277 | 0 | 0.65018 | 1.2277 | 142.0075 | 28.1641 | 141.3573
38952.3692 | 2118 | 0 | 38952.3692 | 2229 | 0 |  | 1598 | 1756 | 129.304 | 0 | 136.0806 | 0 | 1.293 | 0 | 1.3608 | 0 | 1.293 | 1.3608 | 21.6893 | 15.6294 | 20.3963

## B4-D7
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 143.0635 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
38952.3499 | 1 | 0 | 38952.3499 | 1 | 0 |  | -67.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
38952.352 | 1 | 0 | 38952.352 | 1 | 0 |  | 117 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
38952.3542 | 1 | 0 | 38952.3542 | 1 | 0 |  | 302 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
38952.3563 | 2 | 0 | 38952.3563 | 2 | 0 |  | 486.5 | 644.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117069 | 117069 | 117068.9988
38952.3584 | 2 | 0 | 38952.3585 | 2 | 0 |  | 671.5 | 829.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117069 | 117069 | 117068.9988
38952.3606 | 2 | 0 | 38952.3606 | 2 | 0 |  | 856 | 1014 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 117069 | 117069 | 117068.9988
38952.3627 | 3 | 0 | 38952.3627 | 2327 | 0 |  | 1041 | 1199 | 0.18315 | 0 | 142.0635 | 0 | 0.0018315 | 0 | 1.4206 | 0 | 0.0018315 | 1.4206 | 78012.6667 | 0.70391 | 78012.6648
38952.3649 | 1837 | 0 | 38952.3649 | 2208 | 0 |  | 1225.5 | 1383.5 | 112.149 | 0 | 134.7985 | 0 | 1.1215 | 0 | 1.348 | 0 | 1.1215 | 1.348 | 27.5656 | 6.1313 | 26.4441
38952.367 | 1151 | 0 | 38952.367 | 2100 | 0 |  | 1410.5 | 1568.5 | 70.2686 | 0 | 128.2051 | 0 | 0.70269 | 0 | 1.2821 | 0 | 0.70269 | 1.2821 | 103.5951 | 11.5895 | 102.8924
38952.3691 | 2050 | 0 | 38952.3692 | 1624 | 0 |  | 1595.5 | 1753.5 | 125.1526 | 0 | 99.1453 | 0 | 1.2515 | 0 | 0.99145 | 0 | 1.2515 | 0.99145 | 14.3112 | 44.2968 | 13.0597

## B4-C6
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38952.3499 | 1 | 0 | 38952.3499 | 1 | 0 |  | -70.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.352 | 1 | 0 | 38952.352 | 1 | 0 |  | 114.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3541 | 1 | 0 | 38952.3542 | 1 | 0 |  | 299 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3563 | 2 | 0 | 38952.3563 | 2 | 0 |  | 484 | 642 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3584 | 2 | 0 | 38952.3584 | 2 | 0 |  | 668.5 | 826.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3606 | 3 | 0 | 38952.3606 | 2 | 0 |  | 853.5 | 1011.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.3627 | 3 | 0 | 38952.3627 | 4 | 0 |  | 1038 | 1196 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982
38952.3648 | 1727 | 1 | 38952.3648 | 4 | 0 |  | 1223 | 1381 | 105.4335 | 0.06105 | 0.2442 | 0 | 1.0543 | 0.0006105 | 0.002442 | 0 | 1.0537 | 0.002442 | 22.365 | 52725.5 | 38429.1147
38952.367 | 761 | 1 | 38952.367 | 4 | 0 |  | 1407.5 | 1565.5 | 46.4591 | 0.06105 | 0.2442 | 0 | 0.46459 | 0.0006105 | 0.002442 | 0 | 0.46398 | 0.002442 | 177.8978 | 52725.5 | 134846.2485
38952.3691 | 1903 | 1 | 38952.3691 | 4 | 0 |  | 1592.5 | 1750.5 | 116.1783 | 0.06105 | 0.2442 | 0 | 1.1618 | 0.0006105 | 0.002442 | 0 | 1.1612 | 0.002442 | 11.0421 | 52725.5 | 20862.432

## B4-C5
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38952.3498 | 1 | 0 | 38952.3498 | 1 | 0 |  | -73.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.352 | 1 | 0 | 38952.352 | 1 | 0 |  | 111.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3541 | 1 | 0 | 38952.3541 | 1 | 0 |  | 296 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3562 | 2 | 0 | 38952.3563 | 2 | 0 |  | 481 | 639 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3584 | 3 | 0 | 38952.3584 | 2 | 0 |  | 665.5 | 823.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.3605 | 3 | 0 | 38952.3605 | 3 | 0 |  | 850.5 | 1008.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.3627 | 4 | 0 | 38952.3627 | 3 | 0 |  | 1035.5 | 1193.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.3648 | 1679 | 1 | 38952.3648 | 4 | 0 |  | 1220 | 1378 | 102.5031 | 0.06105 | 0.2442 | 0 | 1.025 | 0.0006105 | 0.002442 | 0 | 1.0244 | 0.002442 | 25.8653 | 52725.5 | 43220.0282
38952.3669 | 783 | 1 | 38952.367 | 4 | 0 |  | 1405 | 1563 | 47.8022 | 0.06105 | 0.2442 | 0 | 0.47802 | 0.0006105 | 0.002442 | 0 | 0.47741 | 0.002442 | 170.0797 | 52725.5 | 132650.4132
38952.3691 | 2020 | 1 | 38952.3691 | 4 | 0 |  | 1589.5 | 1747.5 | 123.3211 | 0.06105 | 0.2442 | 0 | 1.2332 | 0.0006105 | 0.002442 | 0 | 1.2326 | 0.002442 | 4.6072 | 52725.5 | 9184.5804

## B3-E10
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 156.5556 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
38952.3497 | 1 | 0 | 38952.3497 | 1 | 0 |  | -81.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256338 | 256338 | 256337.9994
38952.3519 | 2 | 0 | 38952.3519 | 1 | 0 |  | 103 | 261 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128119 | 256338 | 128118.9988
38952.354 | 2 | 0 | 38952.354 | 1 | 0 |  | 287.5 | 445.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128119 | 256338 | 128118.9988
38952.3561 | 5 | 0 | 38952.3562 | 2461 | 0 |  | 472.5 | 630.5 | 0.30525 | 0 | 150.2442 | 0 | 0.0030525 | 0 | 1.5024 | 0 | 0.0030525 | 1.5024 | 51187.6 | 4.2007 | 51187.5969
38952.3583 | 5 | 0 | 38952.3583 | 2548 | 0 |  | 657.5 | 815.5 | 0.30525 | 0 | 155.5556 | 0 | 0.0030525 | 0 | 1.5556 | 0 | 0.0030525 | 1.5556 | 51187.6 | 0.64286 | 51187.5969
38952.3604 | 5 | 0 | 38952.3604 | 2035 | 0 |  | 842 | 1000 | 0.30525 | 0 | 124.2369 | 0 | 0.0030525 | 0 | 1.2424 | 0 | 0.0030525 | 1.2424 | 51187.6 | 26.0138 | 51187.5969
38952.3626 | 5 | 0 | 38952.3626 | 2051 | 0 |  | 1027 | 1185 | 0.30525 | 0 | 125.2137 | 0 | 0.0030525 | 0 | 1.2521 | 0 | 0.0030525 | 1.2521 | 51187.6 | 25.0307 | 51187.5969
38952.3647 | 1942 | 0 | 38952.3647 | 1967 | 0 |  | 1211.5 | 1369.5 | 118.5592 | 0 | 120.0855 | 0 | 1.1856 | 0 | 1.2009 | 0 | 1.1856 | 1.2009 | 32.0484 | 30.3701 | 30.8628
38952.3668 | 1395 | 0 | 38952.3669 | 2122 | 0 |  | 1396.5 | 1554.5 | 85.1648 | 0 | 129.5482 | 0 | 0.85165 | 0 | 1.2955 | 0 | 0.85165 | 1.2955 | 83.8265 | 20.8473 | 82.9749
38952.369 | 2164 | 0 | 38952.369 | 2377 | 0 |  | 1581.5 | 1739.5 | 132.1123 | 0 | 145.116 | 0 | 1.3211 | 0 | 1.4512 | 0 | 1.3211 | 1.4512 | 18.5018 | 7.883 | 17.1807

## B3-E9
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 154.602 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
38952.3497 | 1 | 0 | 38952.3497 | 1 | 0 |  | -84.5 | 73.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
38952.3518 | 1 | 0 | 38952.3519 | 1 | 0 |  | 100.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
38952.354 | 1 | 0 | 38952.354 | 1 | 0 |  | 285 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
38952.3561 | 2 | 0 | 38952.3561 | 2508 | 0 |  | 470 | 628 | 0.1221 | 0 | 153.1136 | 0 | 0.001221 | 0 | 1.5311 | 0 | 0.001221 | 1.5311 | 126519 | 0.97209 | 126518.9988
38952.3583 | 2 | 0 | 38952.3583 | 2103 | 0 |  | 654.5 | 812.5 | 0.1221 | 0 | 128.3883 | 0 | 0.001221 | 0 | 1.2839 | 0 | 0.001221 | 1.2839 | 126519 | 20.4175 | 126518.9988
38952.3604 | 2 | 0 | 38952.3604 | 2516 | 0 |  | 839.5 | 997.5 | 0.1221 | 0 | 153.602 | 0 | 0.001221 | 0 | 1.536 | 0 | 0.001221 | 1.536 | 126519 | 0.65103 | 126518.9988
38952.3625 | 5 | 0 | 38952.3625 | 1977 | 0 |  | 1024 | 1182 | 0.30525 | 0 | 120.696 | 0 | 0.0030525 | 0 | 1.207 | 0 | 0.0030525 | 1.207 | 50547.6 | 28.0921 | 50547.5969
38952.3647 | 1401 | 0 | 38952.3647 | 1964 | 0 |  | 1209 | 1367 | 85.5311 | 0 | 119.9023 | 0 | 0.85531 | 0 | 1.199 | 0 | 0.85531 | 1.199 | 80.7552 | 28.9399 | 79.8999
38952.3668 | 1146 | 0 | 38952.3668 | 2078 | 0 |  | 1393.5 | 1551.5 | 69.9634 | 0 | 126.862 | 0 | 0.69963 | 0 | 1.2686 | 0 | 0.69963 | 1.2686 | 120.9756 | 21.8662 | 120.2759
38952.3689 | 2113 | 0 | 38952.369 | 2024 | 0 |  | 1578.5 | 1736.5 | 128.9988 | 0 | 123.5653 | 0 | 1.29 | 0 | 1.2357 | 0 | 1.29 | 1.2357 | 19.8476 | 25.1176 | 18.5576

## B3-D8
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 135.7375 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
38952.3497 | 1 | 0 | 38952.3497 | 1 | 0 |  | -87.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 222238 | 222238 | 222237.9994
38952.3518 | 1 | 0 | 38952.3518 | 1 | 0 |  | 97.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 222238 | 222238 | 222237.9994
38952.3539 | 1 | 0 | 38952.354 | 1 | 0 |  | 282 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 222238 | 222238 | 222237.9994
38952.3561 | 1 | 0 | 38952.3561 | 1 | 0 |  | 467 | 625 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 222238 | 222238 | 222237.9994
38952.3582 | 2 | 0 | 38952.3582 | 2 | 0 |  | 651.5 | 809.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 111069 | 111069 | 111068.9988
38952.3604 | 2 | 0 | 38952.3604 | 2 | 0 |  | 836.5 | 994.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 111069 | 111069 | 111068.9988
38952.3625 | 4 | 0 | 38952.3625 | 2207 | 0 |  | 1021.5 | 1179.5 | 0.2442 | 0 | 134.7375 | 0 | 0.002442 | 0 | 1.3474 | 0 | 0.002442 | 1.3474 | 55484.5 | 0.74218 | 55484.4976
38952.3646 | 1471 | 0 | 38952.3647 | 2099 | 0 |  | 1206 | 1364 | 89.8046 | 0 | 128.1441 | 0 | 0.89805 | 0 | 1.2814 | 0 | 0.89805 | 1.2814 | 51.1475 | 5.9257 | 50.2495
38952.3668 | 1379 | 0 | 38952.3668 | 2110 | 0 |  | 1391 | 1549 | 84.188 | 0 | 128.8156 | 0 | 0.84188 | 0 | 1.2882 | 0 | 0.84188 | 1.2882 | 61.2313 | 5.3735 | 60.3894
38952.3689 | 1730 | 0 | 38952.3689 | 1978 | 0 |  | 1575.5 | 1733.5 | 105.6166 | 0 | 120.757 | 0 | 1.0562 | 0 | 1.2076 | 0 | 1.0562 | 1.2076 | 28.5191 | 12.4055 | 27.4629

## B3-D7
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 130.5482 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
38952.3496 | 1 | 0 | 38952.3497 | 1 | 0 |  | -90 | 68 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 213738 | 213738 | 213737.9994
38952.3518 | 1 | 0 | 38952.3518 | 1 | 0 |  | 94.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 213738 | 213738 | 213737.9994
38952.3539 | 1 | 0 | 38952.3539 | 1 | 0 |  | 279.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 213738 | 213738 | 213737.9994
38952.3561 | 1 | 0 | 38952.3561 | 2 | 0 |  | 464.5 | 622.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 213738 | 106819 | 213737.9994
38952.3582 | 2 | 0 | 38952.3582 | 2 | 0 |  | 649 | 807 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 106819 | 106819 | 106818.9988
38952.3603 | 2 | 0 | 38952.3603 | 3 | 0 |  | 833.5 | 991.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 106819 | 71179.3333 | 106818.9988
38952.3625 | 3 | 0 | 38952.3625 | 2122 | 0 |  | 1018.5 | 1176.5 | 0.18315 | 0 | 129.5482 | 0 | 0.0018315 | 0 | 1.2955 | 0 | 0.0018315 | 1.2955 | 71179.3333 | 0.77191 | 71179.3315
38952.3646 | 790 | 0 | 38952.3646 | 1910 | 0 |  | 1203.5 | 1361.5 | 48.2295 | 0 | 116.6056 | 0 | 0.4823 | 0 | 1.1661 | 0 | 0.4823 | 1.1661 | 170.681 | 11.9571 | 170.1987
38952.3667 | 1735 | 0 | 38952.3668 | 2074 | 0 |  | 1388 | 1546 | 105.9219 | 0 | 126.6178 | 0 | 1.0592 | 0 | 1.2662 | 0 | 1.0592 | 1.2662 | 23.2496 | 3.1041 | 22.1903
38952.3689 | 2077 | 0 | 38952.3689 | 1316 | 0 |  | 1573 | 1731 | 126.801 | 0 | 80.3419 | 0 | 1.268 | 0 | 0.80342 | 0 | 1.268 | 0.80342 | 2.9552 | 62.4909 | 1.6872

## B3-C6
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38952.3496 | 1 | 0 | 38952.3496 | 1 | 0 |  | -93 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3517 | 1 | 0 | 38952.3518 | 1 | 0 |  | 92 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3539 | 1 | 0 | 38952.3539 | 1 | 0 |  | 276.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.356 | 2 | 0 | 38952.356 | 2 | 0 |  | 461.5 | 619.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3581 | 2 | 0 | 38952.3582 | 2 | 0 |  | 646 | 804 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3603 | 2 | 0 | 38952.3603 | 2 | 0 |  | 831 | 989 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3624 | 4 | 0 | 38952.3624 | 4 | 0 |  | 1015.5 | 1173.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3646 | 568 | 2 | 38952.3646 | 4 | 1 |  | 1200.5 | 1358.5 | 34.6764 | 0.1221 | 0.2442 | 0.06105 | 0.34676 | 0.001221 | 0.002442 | 0.0006105 | 0.34554 | 0.0018315 | 272.9729 | 80079.3323 | 77054.7769
38952.3667 | 1528 | 1 | 38952.3667 | 4 | 0 |  | 1385.5 | 1543.5 | 93.2845 | 0.06105 | 0.2442 | 0 | 0.93284 | 0.0006105 | 0.002442 | 0 | 0.93223 | 0.002442 | 38.3118 | 52725.5 | 58291.4435
38952.3688 | 2049 | 1 | 38952.3689 | 4 | 0 |  | 1570 | 1728 | 125.0916 | 0.06105 | 0.2442 | 0 | 1.2509 | 0.0006105 | 0.002442 | 0 | 1.2503 | 0.002442 | 3.126 | 52725.5 | 6290.0702

## B3-C5
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38952.3496 | 1 | 0 | 38952.3496 | 1 | 0 |  | -95.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3517 | 1 | 0 | 38952.3517 | 1 | 0 |  | 89 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3538 | 1 | 0 | 38952.3539 | 1 | 0 |  | 274 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.356 | 2 | 0 | 38952.356 | 2 | 0 |  | 458.5 | 616.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3581 | 2 | 0 | 38952.3581 | 2 | 0 |  | 643.5 | 801.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3603 | 2 | 0 | 38952.3603 | 2 | 0 |  | 828 | 986 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3624 | 3 | 0 | 38952.3624 | 4 | 0 |  | 1013 | 1171 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 70334 | 52725.5 | 70333.9982
38952.3645 | 454 | 7 | 38952.3645 | 4 | 3 |  | 1197.5 | 1355.5 | 27.7167 | 0.42735 | 0.2442 | 0.18315 | 0.27717 | 0.0042735 | 0.002442 | 0.0018315 | 0.27289 | 0.0006105 | 371.1459 | 1100209.2197 | 23598.1408
38952.3667 | 1655 | 1 | 38952.3667 | 4 | 0 |  | 1382.5 | 1540.5 | 101.0379 | 0.06105 | 0.2442 | 0 | 1.0104 | 0.0006105 | 0.002442 | 0 | 1.0098 | 0.002442 | 27.6917 | 52725.5 | 45615.485
38952.3688 | 2069 | 1 | 38952.3688 | 4 | 0 |  | 1567 | 1725 | 126.3126 | 0.06105 | 0.2442 | 0 | 1.2631 | 0.0006105 | 0.002442 | 0 | 1.2625 | 0.002442 | 2.1286 | 52725.5 | 4293.8562

## B3-B4
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 134.2112 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38952.3495 | 1 | 0 | 38952.3495 | 1 | 0 |  | -98.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219738 | 219738 | 219737.9994
38952.3517 | 1 | 0 | 38952.3517 | 1 | 0 |  | 86.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219738 | 219738 | 219737.9994
38952.3538 | 1 | 0 | 38952.3538 | 1 | 0 |  | 271 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 219738 | 219738 | 219737.9994
38952.3559 | 3 | 0 | 38952.356 | 2 | 0 |  | 456 | 614 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 73179.3333 | 109819 | 73179.3315
38952.3581 | 2 | 0 | 38952.3581 | 3 | 0 |  | 640.5 | 798.5 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 109819 | 73179.3333 | 109818.9988
38952.3602 | 2 | 0 | 38952.3602 | 2 | 0 |  | 825.5 | 983.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 109819 | 109819 | 109818.9988
38952.3624 | 4 | 0 | 38952.3624 | 4 | 0 |  | 1010 | 1168 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 54859.5 | 54859.5 | 54859.4976
38952.3645 | 1218 | 943 | 38952.3645 | 1030 | 763 |  | 1195 | 1353 | 74.359 | 57.5702 | 62.8816 | 46.5812 | 0.74359 | 0.5757 | 0.62882 | 0.46581 | 0.16789 | 0.163 | 612.6668 | 820.1317 | 3.5331
38952.3666 | 2093 | 217 | 38952.3667 | 1808 | 256 |  | 1379.5 | 1537.5 | 127.7778 | 13.2479 | 110.3785 | 15.6288 | 1.2778 | 0.13248 | 1.1038 | 0.15629 | 1.1453 | 0.9475 | 3.6438 | 21.3576 | 9.0525
38952.3688 | 1969 | 198 | 38952.3688 | 2182 | 171 |  | 1564.5 | 1722.5 | 120.2076 | 12.0879 | 133.2112 | 10.4396 | 1.2021 | 0.12088 | 1.3321 | 0.1044 | 1.0812 | 1.2277 | 8.1537 | 18.9979 | 2.5302

## A2-C6
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38952.3493 | 1 | 0 | 38952.3493 | 1 | 0 |  | -118 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3514 | 1 | 0 | 38952.3515 | 1 | 0 |  | 66.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3536 | 1 | 0 | 38952.3536 | 2 | 0 |  | 251.5 | 409.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.3557 | 1 | 0 | 38952.3557 | 1 | 0 |  | 436.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3579 | 2 | 0 | 38952.3579 | 2 | 0 |  | 621 | 779 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.36 | 2 | 0 | 38952.36 | 2 | 0 |  | 806 | 964 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3621 | 4 | 0 | 38952.3622 | 4 | 0 |  | 990.5 | 1148.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3643 | 630 | 1 | 38952.3643 | 4 | 0 |  | 1175.5 | 1333.5 | 38.4615 | 0.06105 | 0.2442 | 0 | 0.38462 | 0.0006105 | 0.002442 | 0 | 0.384 | 0.002442 | 235.775 | 52725.5 | 147921.4499
38952.3664 | 190 | 1 | 38952.3664 | 4 | 0 |  | 1360 | 1518 | 11.5995 | 0.06105 | 0.2442 | 0 | 0.116 | 0.0006105 | 0.002442 | 0 | 0.11538 | 0.002442 | 1017.4811 | 52725.5 | 191838.1568
38952.3686 | 1094 | 1 | 38952.3686 | 4 | 1 |  | 1545 | 1703 | 66.7888 | 0.06105 | 0.2442 | 0.06105 | 0.66789 | 0.0006105 | 0.002442 | 0.0006105 | 0.66728 | 0.0018315 | 93.2316 | 109422.9586 | 101709.0496

## A2-C5
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38952.3493 | 1 | 0 | 38952.3493 | 1 | 0 |  | -121 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3514 | 1 | 0 | 38952.3514 | 1 | 0 |  | 64 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3536 | 1 | 0 | 38952.3536 | 1 | 0 |  | 248.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3557 | 2 | 0 | 38952.3557 | 2 | 0 |  | 433.5 | 591.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3578 | 2 | 0 | 38952.3578 | 2 | 0 |  | 618.5 | 776.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.36 | 2 | 0 | 38952.36 | 2 | 0 |  | 803 | 961 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3621 | 4 | 0 | 38952.3621 | 4 | 1 |  | 987.5 | 1145.5 | 0.2442 | 0 | 0.2442 | 0.06105 | 0.002442 | 0 | 0.002442 | 0.0006105 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.3642 | 70 | 1 | 38952.3643 | 4 | 0 |  | 1172.5 | 1330.5 | 4.2735 | 0.06105 | 0.2442 | 0 | 0.042735 | 0.0006105 | 0.002442 | 0 | 0.042125 | 0.002442 | 2960.9799 | 52725.5 | 203815.4405
38952.3664 | 199 | 1 | 38952.3664 | 4 | 0 |  | 1357.5 | 1515.5 | 12.149 | 0.06105 | 0.2442 | 0 | 0.12149 | 0.0006105 | 0.002442 | 0 | 0.12088 | 0.002442 | 966.686 | 52725.5 | 190939.8605
38952.3685 | 854 | 3 | 38952.3685 | 4 | 2 |  | 1542 | 1700 | 52.1368 | 0.18315 | 0.2442 | 0.1221 | 0.52137 | 0.0018315 | 0.002442 | 0.001221 | 0.51954 | 0.001221 | 147.9461 | 325387.5252 | 41854.4704

## A2-B4
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38952.3492 | 1 | 0 | 38952.3493 | 1 | 0 |  | -123.5 | 34.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3514 | 1 | 0 | 38952.3514 | 1 | 0 |  | 61 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3535 | 2 | 0 | 38952.3535 | 1 | 0 |  | 245.5 | 403.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.3557 | 2 | 0 | 38952.3557 | 2 | 0 |  | 430.5 | 588.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3578 | 2 | 0 | 38952.3578 | 2 | 0 |  | 615.5 | 773.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3599 | 2 | 0 | 38952.36 | 3 | 0 |  | 800 | 958 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 105551 | 70334 | 105550.9988
38952.3621 | 4 | 0 | 38952.3621 | 4 | 0 |  | 985 | 1143 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3642 | 27 | 0 | 38952.3642 | 42 | 0 |  | 1169.5 | 1327.5 | 1.6484 | 0 | 2.5641 | 0 | 0.016484 | 0 | 0.025641 | 0 | 0.016484 | 0.025641 | 7726 | 4931 | 7725.9835
38952.3664 | 207 | 0 | 38952.3664 | 254 | 0 |  | 1354.5 | 1512.5 | 12.6374 | 0 | 15.5067 | 0 | 0.12637 | 0 | 0.15507 | 0 | 0.12637 | 0.15507 | 920.7826 | 731.8976 | 920.6562
38952.3685 | 1202 | 404 | 38952.3685 | 1175 | 396 |  | 1539.5 | 1697.5 | 73.3822 | 24.6642 | 71.7338 | 24.1758 | 0.73382 | 0.24664 | 0.71734 | 0.24176 | 0.48718 | 0.47558 | 160.1043 | 176.4319 | 80.1

## A2-B3
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38952.3492 | 1 | 0 | 38952.3492 | 1 | 0 |  | -126.5 | 31.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3514 | 1 | 0 | 38952.3514 | 1 | 0 |  | 58.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3535 | 1 | 0 | 38952.3535 | 1 | 0 |  | 243 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3556 | 2 | 0 | 38952.3556 | 2 | 0 |  | 427.5 | 585.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3578 | 3 | 0 | 38952.3578 | 3 | 0 |  | 612.5 | 770.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.3599 | 3 | 0 | 38952.3599 | 3 | 0 |  | 797.5 | 955.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.362 | 4 | 0 | 38952.3621 | 4 | 0 |  | 982 | 1140 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3642 | 20 | 0 | 38952.3642 | 274 | 0 |  | 1167 | 1325 | 1.221 | 0 | 16.7277 | 0 | 0.01221 | 0 | 0.16728 | 0 | 0.01221 | 0.16728 | 10465.1 | 671.1752 | 10465.0878
38952.3663 | 218 | 0 | 38952.3663 | 1973 | 0 |  | 1351.5 | 1509.5 | 13.3089 | 0 | 120.4518 | 0 | 0.13309 | 0 | 1.2045 | 0 | 0.13309 | 1.2045 | 869.2752 | 7.0968 | 869.1421
38952.3685 | 1428 | 508 | 38952.3685 | 1472 | 439 |  | 1536.5 | 1694.5 | 87.1795 | 31.0134 | 89.8657 | 26.801 | 0.87179 | 0.31013 | 0.89866 | 0.26801 | 0.56166 | 0.63065 | 332.5918 | 71.1449 | 14.4857

## A1-C6
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38952.349 | 1 | 0 | 38952.349 | 1 | 0 |  | -146 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3511 | 1 | 0 | 38952.3511 | 1 | 0 |  | 38.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3533 | 1 | 0 | 38952.3533 | 1 | 0 |  | 223.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3554 | 2 | 0 | 38952.3554 | 1 | 0 |  | 408 | 566 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.3575 | 3 | 0 | 38952.3576 | 2 | 0 |  | 593 | 751 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.3597 | 3 | 0 | 38952.3597 | 2 | 0 |  | 777.5 | 935.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 70334 | 105551 | 70333.9982
38952.3618 | 4 | 0 | 38952.3618 | 4 | 0 |  | 962.5 | 1120.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.364 | 5 | 0 | 38952.364 | 4 | 0 |  | 1147.5 | 1305.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38952.3661 | 203 | 1 | 38952.3661 | 4 | 0 |  | 1332 | 1490 | 12.3932 | 0.06105 | 0.2442 | 0 | 0.12393 | 0.0006105 | 0.002442 | 0 | 0.12332 | 0.002442 | 945.5633 | 52725.5 | 190540.6177
38952.3682 | 1070 | 2 | 38952.3682 | 3 | 2 |  | 1516.5 | 1674.5 | 65.3236 | 0.1221 | 0.18315 | 0.1221 | 0.65324 | 0.001221 | 0.0018315 | 0.001221 | 0.65201 | 0.0006105 | 97.661 | 201356.755 | 52025.1627

## A1-C5
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38952.3489 | 1 | 0 | 38952.349 | 1 | 0 |  | -149 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3511 | 1 | 0 | 38952.3511 | 1 | 0 |  | 36 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3532 | 1 | 0 | 38952.3532 | 1 | 0 |  | 220.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3554 | 2 | 0 | 38952.3554 | 1 | 0 |  | 405.5 | 563.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 105551 | 211202 | 105550.9988
38952.3575 | 4 | 0 | 38952.3575 | 3 | 0 |  | 590 | 748 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.3596 | 3 | 0 | 38952.3597 | 3 | 0 |  | 775 | 933 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 70334 | 70334 | 70333.9982
38952.3618 | 4 | 1 | 38952.3618 | 4 | 1 |  | 959.5 | 1117.5 | 0.2442 | 0.06105 | 0.2442 | 0.06105 | 0.002442 | 0.0006105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0018315 | 70334 | 70334 | 210502.7099
38952.3639 | 5 | 1 | 38952.3639 | 4 | 0 |  | 1144.5 | 1302.5 | 0.30525 | 0.06105 | 0.2442 | 0 | 0.0030525 | 0.0006105 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 210303.1358
38952.3661 | 174 | 1 | 38952.3661 | 4 | 0 |  | 1329.5 | 1487.5 | 10.6227 | 0.06105 | 0.2442 | 0 | 0.10623 | 0.0006105 | 0.002442 | 0 | 0.10562 | 0.002442 | 1120.8331 | 52725.5 | 193435.1279
38952.3682 | 1024 | 6 | 38952.3682 | 4 | 4 |  | 1514 | 1672 | 62.5153 | 0.3663 | 0.2442 | 0.2442 | 0.62515 | 0.003663 | 0.002442 | 0.002442 | 0.62149 | 0 | 106.9753 | 56403.2652 | 18018.3877

## A1-B4
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38952.3489 | 1 | 0 | 38952.3489 | 1 | 0 |  | -151.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3511 | 1 | 0 | 38952.3511 | 1 | 0 |  | 33 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3532 | 1 | 0 | 38952.3532 | 1 | 0 |  | 218 | 376 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3553 | 1 | 0 | 38952.3553 | 2 | 0 |  | 402.5 | 560.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
38952.3575 | 4 | 0 | 38952.3575 | 4 | 0 |  | 587.5 | 745.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3596 | 4 | 0 | 38952.3596 | 3 | 0 |  | 772 | 930 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 52725.5 | 70334 | 52725.4976
38952.3617 | 4 | 3 | 38952.3618 | 4 | 1 |  | 957 | 1115 | 0.2442 | 0.18315 | 0.2442 | 0.06105 | 0.002442 | 0.0018315 | 0.002442 | 0.0006105 | 0.0006105 | 0.0018315 | 211805.7143 | 70311.7321 | 70100.9664
38952.3639 | 5 | 2 | 38952.3639 | 4 | 1 |  | 1141.5 | 1299.5 | 0.30525 | 0.1221 | 0.2442 | 0.06105 | 0.0030525 | 0.001221 | 0.002442 | 0.0006105 | 0.0018315 | 0.0018315 | 70334 | 70334 | 105151.4969
38952.366 | 181 | 1 | 38952.366 | 1629 | 1 |  | 1326.5 | 1484.5 | 11.0501 | 0.06105 | 99.4505 | 0.06105 | 0.1105 | 0.0006105 | 0.99451 | 0.0006105 | 0.10989 | 0.99389 | 1093.7818 | 29.7326 | 44255.867
38952.3682 | 931 | 684 | 38952.3682 | 1098 | 576 |  | 1511.5 | 1669.5 | 56.8376 | 41.7582 | 67.033 | 35.1648 | 0.56838 | 0.41758 | 0.67033 | 0.35165 | 0.15079 | 0.31868 | 757.7625 | 751.5508 | 64.2597

## A1-B3
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38952.3489 | 1 | 0 | 38952.3489 | 1 | 0 |  | -154.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.351 | 1 | 0 | 38952.351 | 1 | 0 |  | 30.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3532 | 1 | 0 | 38952.3532 | 1 | 0 |  | 215 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3553 | 2 | 0 | 38952.3553 | 2 | 0 |  | 399.5 | 557.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3574 | 4 | 0 | 38952.3575 | 4 | 0 |  | 584.5 | 742.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3596 | 4 | 0 | 38952.3596 | 4 | 0 |  | 769.5 | 927.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 52725.5 | 52725.5 | 52725.4976
38952.3617 | 5 | 11 | 38952.3617 | 4 | 4 |  | 954 | 1112 | 0.30525 | 0.67155 | 0.2442 | 0.2442 | 0.0030525 | 0.0067155 | 0.002442 | 0.002442 | 0.003663 | 0 | 35133.319 | 18524218.0849 | 19063.7153
38952.3639 | 6 | 8 | 38952.3639 | 4 | 4 |  | 1139 | 1297 | 0.3663 | 0.4884 | 0.2442 | 0.2442 | 0.003663 | 0.004884 | 0.002442 | 0.002442 | 0.001221 | 0 | 105350.2414 | 55546441.5053 | 26237.7028
38952.366 | 218 | 5 | 38952.366 | 2049 | 2 |  | 1323.5 | 1481.5 | 13.3089 | 0.30525 | 125.0916 | 0.1221 | 0.13309 | 0.0030525 | 1.2509 | 0.001221 | 0.13004 | 1.2497 | 3566.5953 | 3.1276 | 1146.387
38952.3681 | 1147 | 328 | 38952.3681 | 1327 | 477 |  | 1508.5 | 1666.5 | 70.0244 | 20.0244 | 81.0134 | 29.1209 | 0.70024 | 0.20024 | 0.81013 | 0.29121 | 0.5 | 0.51893 | 165.1882 | 140.051 | 113.4862

## A1-A2
Penlight Test 46 |  |  | 2006-08-23 | 8:25 |  |  | Vs = |  | 129 |  | R = | 100
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38952.3489 | 1 | 0 | 38952.3489 | 1 | 0 |  | -157.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.351 | 1 | 0 | 38952.351 | 1 | 0 |  | 27.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3531 | 1 | 0 | 38952.3531 | 1 | 0 |  | 212.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
38952.3553 | 2 | 0 | 38952.3553 | 2 | 0 |  | 397 | 555 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 105551 | 105551 | 105550.9988
38952.3574 | 5 | 0 | 38952.3574 | 4 | 0 |  | 581.5 | 739.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38952.3595 | 5 | 0 | 38952.3596 | 4 | 0 |  | 766.5 | 924.5 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 42160.4 | 52725.5 | 42160.3969
38952.3617 | 1028 | 1064 | 38952.3617 | 964 | 925 |  | 951.5 | 1109.5 | 62.7595 | 64.9573 | 58.8523 | 56.4713 | 0.62759 | 0.64957 | 0.58852 | 0.56471 | 0.021978 | 0.02381 | 199961.67 | 3000.7852 | 1.9119
38952.3638 | 923 | 853 | 38952.3638 | 1028 | 953 |  | 1136 | 1294 | 56.3492 | 52.0757 | 62.7595 | 58.1807 | 0.56349 | 0.52076 | 0.62759 | 0.58181 | 0.042735 | 0.045788 | 3993.5749 | 2121.8042 | 37.7317
38952.366 | 1196 | 752 | 38952.366 | 1098 | 679 |  | 1321 | 1479 | 73.0159 | 45.9096 | 67.033 | 41.453 | 0.73016 | 0.4591 | 0.67033 | 0.41453 | 0.27106 | 0.2558 | 309.9151 | 507.7442 | 18.3334
38952.3681 | 1325 | 719 | 38952.3681 | 1293 | 802 |  | 1505.5 | 1663.5 | 80.8913 | 43.895 | 78.9377 | 48.9621 | 0.80891 | 0.43895 | 0.78938 | 0.48962 | 0.36996 | 0.29976 | 48.334 | 70.19 | 3.959

## AvgC-C
Average Conductor to Conductor Resistances
Penlight Test 46 |  |  | 2006-08-23 | 8:25
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-C |  | Penlight Time | C2-C | Penlight Time | C3-C | Penlight Time | C4-C | Penlight Time | C5-C | Penlight Time | C6-C | Penlight Time | C7-C | Penlight Time | Minimums
-140 | 218724.6661 |  | -103.6667 | 217307.9994 | -109.6667 | 213047.3327 | -97.5 | 216463.9994 | -88.75 | 218007.9994 | -84 | 218341.3327 | -47.0833 | 243037.9994 | -140 | 213047.3327
44.75 | 197354.8326 |  | 81.1667 | 217307.9994 | 75.1667 | 213047.3327 | 87.25 | 216463.9994 | 96.1667 | 218007.9994 | 100.75 | 218341.3327 | 137.5833 | 221668.166 | 44.75 | 197354.8326
229.5 | 197354.8326 |  | 265.8333 | 179037.9992 | 259.8333 | 213047.3327 | 271.9167 | 198855.4993 | 280.75 | 218007.9994 | 285.5 | 218341.3327 | 322.3333 | 201006.6659 | 229.5 | 179037.9992
414.1667 | 114098.9319 |  | 450.6667 | 113815.5986 | 444.5833 | 118186.8877 | 456.75 | 119683.8877 | 465.5833 | 129965.4989 | 470.3333 | 126729.1655 | 507.0833 | 135081.5317 | 414.1667 | 113815.5986
599 | 53643.0808 |  | 635.4167 | 79772.4981 | 629.3333 | 91799.9151 | 641.5 | 93508.2485 | 650.3333 | 94280.2485 | 655 | 103251.1653 | 691.9167 | 96250.1982 | 599 | 53643.0808
783.75 | 56577.8309 |  | 820.25 | 74915.494 | 814.1667 | 91799.9151 | 826.25 | 87638.7484 | 835.1667 | 118226.4987 | 839.8333 | 97381.6652 | 876.5833 | 112404.6943 | 783.75 | 56577.8309
968.5833 | 67263.733 |  | 1005 | 35229.6488 | 998.8333 | 53481.2563 | 1011.0833 | 63126.3537 | 1019.8333 | 73621.333 | 1024.5 | 46540.096 | 1061.5 | 51169.8312 | 968.5833 | 35229.6488
1153.3333 | 63986.8878 |  | 1189.75 | 61664.4928 | 1183.75 | 22921.5734 | 1195.75 | 32426.1001 | 1204.6667 | 80743.3605 | 1209.4167 | 61503.4704 | 1246.1667 | 11197.683 | 1153.3333 | 11197.683
1338.1667 | 71579.8847 |  | 1374.5833 | 64097.8313 | 1368.4167 | 17658.9501 | 1380.5833 | 52130.855 | 1389.5833 | 94061.4658 | 1394.1667 | 106496.1926 | 1431 | 10890.8518 | 1338.1667 | 10890.8518
1522.9167 | 11707.0727 |  | 1559.3333 | 23947.1401 | 1553.25 | 1786.0193 | 1565.5 | 5034.4937 | 1574.1667 | 18831.407 | 1578.9167 | 40725.0763 | 1615.9167 | 17182.5172 | 1522.9167 | 1786.0193
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Avg
Average Conductor to Ground Resistances
Penlight Test 46 |  |  | 2006-08-23 | 8:25
TS/TP Mix | 7-C | Tray
525 C | 23.0 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | C4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | C7-G | Penlight Time | C8-G | Penlight Time | C9-G | Penlight Time | C10-G | Penlight Time | C11-G | Penlight Time | C12-G | Penlight Time | Minimums
-151.7 | 211202 |  | -129.3 | 211202 | -101.2778 | 223333.1111 | -85.7222 | 229155.3333 | -71.4444 | 224806.8889 | -62.7222 | 227851.3333 | -38.5 | 235038 | -33 | 242618 | -20.6667 | 239241.4444 | -17.6111 | 254649.1111 | -2.9802e-08 | 244798 | 2.3 | 246178 | -59.137 | 211202
33.1 | 211202 |  | 55.5 | 211202 | 83.5556 | 209086.5556 | 99.0556 | 229155.3333 | 113.3889 | 224806.8889 | 122 | 227851.3333 | 146.2 | 235038 | 151.9 | 194490.4 | 164.1111 | 253360.2222 | 167.2222 | 254649.1111 | 185.1 | 244798 | 187 | 246178 | 125.6778 | 194490.4
217.9 | 211202 |  | 240.2 | 190071.8 | 268.1667 | 209086.5556 | 283.7778 | 215108.7778 | 298.0556 | 224806.8889 | 306.8333 | 216112.3333 | 331 | 235038 | 336.5 | 203957.3 | 348.8889 | 113586.5389 | 351.9444 | 173995.4815 | 369.5 | 146022.3867 | 371.9 | 146781.0533 | 310.3889 | 113586.5389
402.5 | 126681.2 |  | 425 | 126681.2 | 453 | 123229.5481 | 468.6111 | 106083.0667 | 482.8333 | 115527.6333 | 491.6111 | 110103.1889 | 515.7 | 95129.4533 | 521.2 | 128028.52 | 533.5556 | 15.8802 | 536.7222 | 8.3694 | 554.4 | 50228.8533 | 556.6 | 60120.04 | 495.1444 | 8.3694
587.3 | 54134.18 |  | 609.8 | 87942.5 | 637.7222 | 93286.1222 | 653.2778 | 92229.4926 | 667.6111 | 85867.9667 | 676.3333 | 90538.1889 | 700.5 | 102580.72 | 706 | 97386.7867 | 718.3889 | 8.3494 | 721.5556 | 5.9743 | 739.1 | 53595.36 | 741.3 | 61816.2933 | 679.9074 | 5.9743
772.1 | 57655.88 |  | 794.6 | 87942.5 | 822.5556 | 93286.1222 | 838.0556 | 90431.0667 | 852.3889 | 99508.937 | 861.1111 | 92804.2815 | 885.2 | 37749.129 | 890.9 | 47977.584 | 903.1111 | 15.7494 | 906.1667 | 12.9587 | 923.9 | 49868.7012 | 926 | 70879.4887 | 864.6741 | 12.9587
956.9 | 113992.0406 |  | 979.3 | 42780.557 | 1007.2778 | 2109251.2909 | 1022.8889 | 59050.1888 | 1037.1111 | 105784.4977 | 1045.8333 | 46067.2557 | 1070 | 11.5898 | 1075.6 | 2.1572 | 1087.8889 | 18.7639 | 1091 | 15.409 | 1108.6 | 20.7059 | 1111 | 10.868 | 1049.45 | 2.1572
1141.7 | 54912.7432 |  | 1164.1 | 4701.9318 | 1192.1111 | 6172078.2331 | 1207.6111 | 8475.0337 | 1221.9444 | 157596.4408 | 1230.7222 | 54783.3048 | 1254.8 | 10.0611 | 1260.4 | 12.6253 | 1272.6667 | 12.8332 | 1275.7222 | 17.871 | 1293.5 | 17.4288 | 1295.7 | 17.069 | 1234.2481 | 10.0611
1326.5 | 1407.3377 |  | 1348.9 | 856.3938 | 1376.8333 | 41.0172 | 1392.4444 | 174.0612 | 1406.8333 | 41050.7535 | 1415.5 | 51798.6744 | 1439.6 | 17.5117 | 1445.2 | 28.2564 | 1457.3889 | 11.6197 | 1460.6667 | 16.692 | 1478.3 | 3.9868 | 1480.5 | 18.9414 | 1419.0556 | 3.9868
1511.2 | 235.1842 |  | 1533.7 | 160.8127 | 1561.6667 | 32.7142 | 1577.2778 | 117.0267 | 1591.5 | 82564.2248 | 1600.2222 | 78395.1582 | 1624.4 | 46.184 | 1630 | 19.4732 | 1642.2778 | 16.134 | 1645.3889 | 12.9967 | 1663 | 12.143 | 1665.3 | 9.1456 | 1603.8278 | 9.1456
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 46 |  |  | 2006-08-23 | 8:25
38952.3489 | 1 | 0 | 1 | TS/TP Mix | 7-C | Tray
38952.351 | 1 | 0 | 1 | 525 C | 23.0 kW/m2 |  | Bundle
38952.3531 | 1 | 0 | 1
38952.3553 | 2 | 0 | 1
38952.3574 | 5 | 0 | 1
38952.3595 | 5 | 0 | 1
38952.3617 | 1028 | 1064 | 1
38952.3638 | 923 | 853 | 1
38952.366 | 1196 | 752 | 1
38952.3681 | 1325 | 719 | 1
1
38952.3489 | 1 | 0 | 2
38952.351 | 1 | 0 | 2
38952.3531 | 1 | 0 | 2
38952.3553 | 2 | 0 | 2
38952.3574 | 4 | 0 | 2
38952.3596 | 4 | 0 | 2
38952.3617 | 964 | 925 | 2
38952.3638 | 1028 | 953 | 2
38952.366 | 1098 | 679 | 2
38952.3681 | 1293 | 802 | 2
2
38952.3489 | 1 | 0 | 3
38952.351 | 1 | 0 | 3
38952.3532 | 1 | 0 | 3
38952.3553 | 2 | 0 | 3
38952.3574 | 4 | 0 | 3
38952.3596 | 4 | 0 | 3
38952.3617 | 5 | 11 | 3
38952.3639 | 6 | 8 | 3
38952.366 | 218 | 5 | 3
38952.3681 | 1147 | 328 | 3
3
38952.3489 | 1 | 0 | 4
38952.351 | 1 | 0 | 4
38952.3532 | 1 | 0 | 4
38952.3553 | 2 | 0 | 4
38952.3575 | 4 | 0 | 4
38952.3596 | 4 | 0 | 4
38952.3617 | 4 | 4 | 4
38952.3639 | 4 | 4 | 4
38952.366 | 2049 | 2 | 4
38952.3681 | 1327 | 477 | 4
4
38952.3489 | 1 | 0 | 5
38952.3511 | 1 | 0 | 5
38952.3532 | 1 | 0 | 5
38952.3553 | 1 | 0 | 5
38952.3575 | 4 | 0 | 5
38952.3596 | 4 | 0 | 5
38952.3617 | 4 | 3 | 5
38952.3639 | 5 | 2 | 5
38952.366 | 181 | 1 | 5
38952.3682 | 931 | 684 | 5
5
38952.3489 | 1 | 0 | 6
38952.3511 | 1 | 0 | 6
38952.3532 | 1 | 0 | 6
38952.3553 | 2 | 0 | 6
38952.3575 | 4 | 0 | 6
38952.3596 | 3 | 0 | 6
38952.3618 | 4 | 1 | 6
38952.3639 | 4 | 1 | 6
38952.366 | 1629 | 1 | 6
38952.3682 | 1098 | 576 | 6
6
38952.3489 | 1 | 0 | 7
38952.3511 | 1 | 0 | 7
38952.3532 | 1 | 0 | 7
38952.3554 | 2 | 0 | 7
38952.3575 | 4 | 0 | 7
38952.3596 | 3 | 0 | 7
38952.3618 | 4 | 1 | 7
38952.3639 | 5 | 1 | 7
38952.3661 | 174 | 1 | 7
38952.3682 | 1024 | 6 | 7
7
38952.349 | 1 | 0 | 8
38952.3511 | 1 | 0 | 8
38952.3532 | 1 | 0 | 8
38952.3554 | 1 | 0 | 8
38952.3575 | 3 | 0 | 8
38952.3597 | 3 | 0 | 8
38952.3618 | 4 | 1 | 8
38952.3639 | 4 | 0 | 8
38952.3661 | 4 | 0 | 8
38952.3682 | 4 | 4 | 8
8
38952.349 | 1 | 0 | 9
38952.3511 | 1 | 0 | 9
38952.3533 | 1 | 0 | 9
38952.3554 | 2 | 0 | 9
38952.3575 | 3 | 0 | 9
38952.3597 | 3 | 0 | 9
38952.3618 | 4 | 0 | 9
38952.364 | 5 | 0 | 9
38952.3661 | 203 | 0 | 9
38952.3682 | 1070 | 2 | 9
9
38952.349 | 1 | 0 | 10
38952.3511 | 1 | 0 | 10
38952.3533 | 1 | 0 | 10
38952.3554 | 1 | 0 | 10
38952.3576 | 2 | 0 | 10
38952.3597 | 2 | 0 | 10
38952.3618 | 4 | 0 | 10
38952.364 | 4 | 0 | 10
38952.3661 | 4 | 0 | 10
38952.3682 | 3 | 2 | 10
10
38952.349 | 1 | 0 | 11
38952.3512 | 1 | 0 | 11
38952.3533 | 1 | 0 | 11
38952.3554 | 1 | 0 | 11
38952.3576 | 3 | 0 | 11
38952.3597 | 2 | 0 | 11
38952.3619 | 4 | 0 | 11
38952.364 | 5 | 1 | 11
38952.3661 | 194 | 0 | 11
38952.3683 | 1359 | 1 | 11
11
38952.349 | 1 | 0 | 12
38952.3512 | 1 | 0 | 12
38952.3533 | 1 | 0 | 12
38952.3555 | 2 | 0 | 12
38952.3576 | 2 | 0 | 12
38952.3597 | 3 | 0 | 12
38952.3619 | 2155 | 0 | 12
38952.364 | 2257 | 0 | 12
38952.3661 | 2055 | 0 | 12
38952.3683 | 1917 | 1 | 12
12
38952.3491 | 1 | 0 | 13
38952.3512 | 1 | 0 | 13
38952.3533 | 1 | 0 | 13
38952.3555 | 1 | 0 | 13
38952.3576 | 2 | 0 | 13
38952.3597 | 3 | 0 | 13
38952.3619 | 5 | 0 | 13
38952.364 | 7 | 0 | 13
38952.3662 | 204 | 0 | 13
38952.3683 | 768 | 1 | 13
13
38952.3491 | 1 | 0 | 14
38952.3512 | 1 | 0 | 14
38952.3533 | 1 | 0 | 14
38952.3555 | 1 | 0 | 14
38952.3576 | 2 | 0 | 14
38952.3598 | 2 | 0 | 14
38952.3619 | 2395 | 0 | 14
38952.364 | 2252 | 0 | 14
38952.3662 | 1947 | 0 | 14
38952.3683 | 1482 | 1 | 14
14
38952.3491 | 1 | 0 | 15
38952.3512 | 1 | 0 | 15
38952.3534 | 1 | 0 | 15
38952.3555 | 2 | 0 | 15
38952.3576 | 3 | 0 | 15
38952.3598 | 2 | 0 | 15
38952.3619 | 5 | 0 | 15
38952.3641 | 59 | 0 | 15
38952.3662 | 193 | 0 | 15
38952.3683 | 1242 | 1 | 15
15
38952.3491 | 1 | 0 | 16
38952.3512 | 1 | 0 | 16
38952.3534 | 1 | 0 | 16
38952.3555 | 1970 | 0 | 16
38952.3577 | 2294 | 0 | 16
38952.3598 | 2468 | 0 | 16
38952.3619 | 2397 | 0 | 16
38952.3641 | 2331 | 0 | 16
38952.3662 | 2109 | 0 | 16
38952.3683 | 2139 | 0 | 16
16
38952.3491 | 1 | 0 | 17
38952.3512 | 1 | 0 | 17
38952.3534 | 1 | 0 | 17
38952.3555 | 5 | 0 | 17
38952.3577 | 5 | 0 | 17
38952.3598 | 5 | 0 | 17
38952.3619 | 5 | 0 | 17
38952.3641 | 68 | 0 | 17
38952.3662 | 197 | 0 | 17
38952.3684 | 870 | 0 | 17
17
38952.3491 | 1 | 0 | 18
38952.3513 | 1 | 0 | 18
38952.3534 | 1 | 0 | 18
38952.3555 | 2324 | 0 | 18
38952.3577 | 2226 | 0 | 18
38952.3598 | 1978 | 0 | 18
38952.362 | 2213 | 0 | 18
38952.3641 | 2378 | 0 | 18
38952.3662 | 1980 | 0 | 18
38952.3684 | 2111 | 0 | 18
18
38952.3491 | 1 | 0 | 19
38952.3513 | 1 | 0 | 19
38952.3534 | 1 | 0 | 19
38952.3556 | 5 | 0 | 19
38952.3577 | 6 | 0 | 19
38952.3598 | 5 | 0 | 19
38952.362 | 5 | 0 | 19
38952.3641 | 484 | 0 | 19
38952.3662 | 182 | 0 | 19
38952.3684 | 851 | 0 | 19
19
38952.3492 | 1 | 0 | 20
38952.3513 | 1 | 0 | 20
38952.3534 | 1 | 0 | 20
38952.3556 | 4 | 0 | 20
38952.3577 | 4 | 0 | 20
38952.3598 | 5 | 0 | 20
38952.362 | 5 | 0 | 20
38952.3641 | 2425 | 0 | 20
38952.3663 | 2146 | 0 | 20
38952.3684 | 2403 | 0 | 20
20
38952.3492 | 1 | 0 | 21
38952.3513 | 1 | 0 | 21
38952.3535 | 1 | 0 | 21
38952.3556 | 3 | 0 | 21
38952.3577 | 4 | 0 | 21
38952.3599 | 4 | 0 | 21
38952.362 | 5 | 0 | 21
38952.3641 | 391 | 0 | 21
38952.3663 | 380 | 0 | 21
38952.3684 | 1102 | 0 | 21
21
38952.3492 | 1 | 0 | 22
38952.3513 | 1 | 0 | 22
38952.3535 | 1 | 0 | 22
38952.3556 | 3 | 0 | 22
38952.3577 | 3 | 0 | 22
38952.3599 | 3 | 0 | 22
38952.362 | 4 | 0 | 22
38952.3642 | 2230 | 0 | 22
38952.3663 | 1929 | 0 | 22
38952.3684 | 2447 | 0 | 22
22
38952.3492 | 1 | 0 | 23
38952.3514 | 1 | 0 | 23
38952.3535 | 1 | 0 | 23
38952.3556 | 2 | 0 | 23
38952.3578 | 3 | 0 | 23
38952.3599 | 3 | 0 | 23
38952.362 | 4 | 0 | 23
38952.3642 | 20 | 0 | 23
38952.3663 | 218 | 0 | 23
38952.3685 | 1428 | 508 | 23
23
38952.3492 | 1 | 0 | 24
38952.3514 | 1 | 0 | 24
38952.3535 | 1 | 0 | 24
38952.3556 | 2 | 0 | 24
38952.3578 | 3 | 0 | 24
38952.3599 | 3 | 0 | 24
38952.3621 | 4 | 0 | 24
38952.3642 | 274 | 0 | 24
38952.3663 | 1973 | 0 | 24
38952.3685 | 1472 | 439 | 24
24
38952.3492 | 1 | 0 | 25
38952.3514 | 1 | 0 | 25
38952.3535 | 2 | 0 | 25
38952.3557 | 2 | 0 | 25
38952.3578 | 2 | 0 | 25
38952.3599 | 2 | 0 | 25
38952.3621 | 4 | 0 | 25
38952.3642 | 27 | 0 | 25
38952.3664 | 207 | 0 | 25
38952.3685 | 1202 | 404 | 25
25
38952.3493 | 1 | 0 | 26
38952.3514 | 1 | 0 | 26
38952.3535 | 1 | 0 | 26
38952.3557 | 2 | 0 | 26
38952.3578 | 2 | 0 | 26
38952.36 | 3 | 0 | 26
38952.3621 | 4 | 0 | 26
38952.3642 | 42 | 0 | 26
38952.3664 | 254 | 0 | 26
38952.3685 | 1175 | 396 | 26
26
38952.3493 | 1 | 0 | 27
38952.3514 | 1 | 0 | 27
38952.3536 | 1 | 0 | 27
38952.3557 | 2 | 0 | 27
38952.3578 | 2 | 0 | 27
38952.36 | 2 | 0 | 27
38952.3621 | 4 | 0 | 27
38952.3642 | 70 | 0 | 27
38952.3664 | 199 | 0 | 27
38952.3685 | 854 | 3 | 27
27
38952.3493 | 1 | 0 | 28
38952.3514 | 1 | 0 | 28
38952.3536 | 1 | 0 | 28
38952.3557 | 2 | 0 | 28
38952.3578 | 2 | 0 | 28
38952.36 | 2 | 0 | 28
38952.3621 | 4 | 1 | 28
38952.3643 | 4 | 0 | 28
38952.3664 | 4 | 0 | 28
38952.3685 | 4 | 2 | 28
28
38952.3493 | 1 | 0 | 29
38952.3514 | 1 | 0 | 29
38952.3536 | 1 | 0 | 29
38952.3557 | 1 | 0 | 29
38952.3579 | 2 | 0 | 29
38952.36 | 2 | 0 | 29
38952.3621 | 4 | 0 | 29
38952.3643 | 630 | 0 | 29
38952.3664 | 190 | 0 | 29
38952.3686 | 1094 | 1 | 29
29
38952.3493 | 1 | 0 | 30
38952.3515 | 1 | 0 | 30
38952.3536 | 2 | 0 | 30
38952.3557 | 1 | 0 | 30
38952.3579 | 2 | 0 | 30
38952.36 | 2 | 0 | 30
38952.3622 | 4 | 0 | 30
38952.3643 | 4 | 0 | 30
38952.3664 | 4 | 0 | 30
38952.3686 | 4 | 1 | 30
30
38952.3493 | 1 | 0 | 31
38952.3515 | 1 | 0 | 31
38952.3536 | 1 | 0 | 31
38952.3558 | 2 | 0 | 31
38952.3579 | 2 | 0 | 31
38952.36 | 2 | 0 | 31
38952.3622 | 4 | 0 | 31
38952.3643 | 926 | 0 | 31
38952.3664 | 233 | 0 | 31
38952.3686 | 1357 | 0 | 31
31
38952.3494 | 1 | 0 | 32
38952.3515 | 1 | 0 | 32
38952.3536 | 1 | 0 | 32
38952.3558 | 2 | 0 | 32
38952.3579 | 2 | 0 | 32
38952.36 | 2 | 0 | 32
38952.3622 | 1824 | 0 | 32
38952.3643 | 1874 | 0 | 32
38952.3665 | 2201 | 0 | 32
38952.3686 | 1743 | 0 | 32
32
38952.3494 | 1 | 0 | 33
38952.3515 | 1 | 0 | 33
38952.3536 | 1 | 0 | 33
38952.3558 | 1 | 0 | 33
38952.3579 | 2 | 0 | 33
38952.3601 | 2 | 0 | 33
38952.3622 | 5 | 0 | 33
38952.3643 | 75 | 0 | 33
38952.3665 | 251 | 0 | 33
38952.3686 | 1385 | 0 | 33
33
38952.3494 | 1 | 0 | 34
38952.3515 | 1 | 0 | 34
38952.3537 | 1 | 0 | 34
38952.3558 | 2 | 0 | 34
38952.3579 | 2 | 0 | 34
38952.3601 | 2 | 0 | 34
38952.3622 | 2024 | 0 | 34
38952.3644 | 2473 | 0 | 34
38952.3665 | 2062 | 0 | 34
38952.3686 | 1890 | 0 | 34
34
38952.3494 | 1 | 0 | 35
38952.3515 | 1 | 0 | 35
38952.3537 | 1 | 0 | 35
38952.3558 | 1 | 0 | 35
38952.358 | 2 | 0 | 35
38952.3601 | 2 | 0 | 35
38952.3622 | 5 | 0 | 35
38952.3644 | 69 | 0 | 35
38952.3665 | 203 | 0 | 35
38952.3687 | 1422 | 0 | 35
35
38952.3494 | 1 | 0 | 36
38952.3516 | 1 | 0 | 36
38952.3537 | 1 | 0 | 36
38952.3558 | 2017 | 0 | 36
38952.358 | 2081 | 0 | 36
38952.3601 | 2489 | 0 | 36
38952.3623 | 2289 | 0 | 36
38952.3644 | 2158 | 0 | 36
38952.3665 | 2484 | 0 | 36
38952.3687 | 2339 | 0 | 36
36
38952.3494 | 1 | 0 | 37
38952.3516 | 1 | 0 | 37
38952.3537 | 1 | 0 | 37
38952.3559 | 5 | 0 | 37
38952.358 | 5 | 0 | 37
38952.3601 | 5 | 0 | 37
38952.3623 | 5 | 0 | 37
38952.3644 | 343 | 0 | 37
38952.3666 | 207 | 0 | 37
38952.3687 | 1481 | 0 | 37
37
38952.3495 | 1 | 0 | 38
38952.3516 | 1 | 0 | 38
38952.3537 | 1 | 0 | 38
38952.3559 | 2052 | 0 | 38
38952.358 | 2365 | 0 | 38
38952.3602 | 2119 | 0 | 38
38952.3623 | 2476 | 0 | 38
38952.3644 | 2420 | 0 | 38
38952.3666 | 2542 | 0 | 38
38952.3687 | 2076 | 0 | 38
38
38952.3495 | 1 | 0 | 39
38952.3516 | 1 | 0 | 39
38952.3538 | 1 | 0 | 39
38952.3559 | 5 | 0 | 39
38952.358 | 6 | 0 | 39
38952.3602 | 5 | 0 | 39
38952.3623 | 5 | 0 | 39
38952.3644 | 656 | 0 | 39
38952.3666 | 264 | 0 | 39
38952.3687 | 1455 | 0 | 39
39
38952.3495 | 1 | 0 | 40
38952.3516 | 1 | 0 | 40
38952.3538 | 1 | 0 | 40
38952.3559 | 4 | 0 | 40
38952.358 | 5 | 0 | 40
38952.3602 | 4 | 0 | 40
38952.3623 | 51 | 0 | 40
38952.3645 | 2124 | 0 | 40
38952.3666 | 2329 | 0 | 40
38952.3687 | 2344 | 0 | 40
40
38952.3495 | 0 | 0 | 41
38952.3516 | 1 | 0 | 41
38952.3538 | 1 | 0 | 41
38952.3559 | 3 | 0 | 41
38952.3581 | 4 | 0 | 41
38952.3602 | 3 | 0 | 41
38952.3623 | 4 | 0 | 41
38952.3645 | 760 | 0 | 41
38952.3666 | 223 | 0 | 41
38952.3688 | 1446 | 0 | 41
41
38952.3495 | 1 | 0 | 42
38952.3517 | 1 | 0 | 42
38952.3538 | 1 | 0 | 42
38952.3559 | 3 | 0 | 42
38952.3581 | 3 | 0 | 42
38952.3602 | 2 | 0 | 42
38952.3623 | 102 | 0 | 42
38952.3645 | 2108 | 0 | 42
38952.3666 | 1913 | 0 | 42
38952.3688 | 1989 | 0 | 42
42
38952.3495 | 1 | 0 | 43
38952.3517 | 1 | 0 | 43
38952.3538 | 1 | 0 | 43
38952.3559 | 3 | 0 | 43
38952.3581 | 2 | 0 | 43
38952.3602 | 2 | 0 | 43
38952.3624 | 4 | 0 | 43
38952.3645 | 1218 | 943 | 43
38952.3666 | 2093 | 217 | 43
38952.3688 | 1969 | 198 | 43
43
38952.3495 | 1 | 0 | 44
38952.3517 | 1 | 0 | 44
38952.3538 | 1 | 0 | 44
38952.356 | 2 | 0 | 44
38952.3581 | 3 | 0 | 44
38952.3602 | 2 | 0 | 44
38952.3624 | 4 | 0 | 44
38952.3645 | 1030 | 763 | 44
38952.3667 | 1808 | 256 | 44
38952.3688 | 2182 | 171 | 44
44
38952.3496 | 1 | 0 | 45
38952.3517 | 1 | 0 | 45
38952.3538 | 1 | 0 | 45
38952.356 | 2 | 0 | 45
38952.3581 | 2 | 0 | 45
38952.3603 | 2 | 0 | 45
38952.3624 | 3 | 0 | 45
38952.3645 | 454 | 7 | 45
38952.3667 | 1655 | 1 | 45
38952.3688 | 2069 | 1 | 45
45
38952.3496 | 1 | 0 | 46
38952.3517 | 1 | 0 | 46
38952.3539 | 1 | 0 | 46
38952.356 | 2 | 0 | 46
38952.3581 | 2 | 0 | 46
38952.3603 | 2 | 0 | 46
38952.3624 | 4 | 0 | 46
38952.3645 | 4 | 3 | 46
38952.3667 | 4 | 0 | 46
38952.3688 | 4 | 0 | 46
46
38952.3496 | 1 | 0 | 47
38952.3517 | 1 | 0 | 47
38952.3539 | 1 | 0 | 47
38952.356 | 2 | 0 | 47
38952.3581 | 2 | 0 | 47
38952.3603 | 2 | 0 | 47
38952.3624 | 4 | 0 | 47
38952.3646 | 568 | 2 | 47
38952.3667 | 1528 | 0 | 47
38952.3688 | 2049 | 0 | 47
47
38952.3496 | 1 | 0 | 48
38952.3518 | 1 | 0 | 48
38952.3539 | 1 | 0 | 48
38952.356 | 2 | 0 | 48
38952.3582 | 2 | 0 | 48
38952.3603 | 2 | 0 | 48
38952.3624 | 4 | 0 | 48
38952.3646 | 4 | 1 | 48
38952.3667 | 4 | 0 | 48
38952.3689 | 4 | 0 | 48
48
38952.3496 | 1 | 0 | 49
38952.3518 | 1 | 0 | 49
38952.3539 | 1 | 0 | 49
38952.3561 | 1 | 0 | 49
38952.3582 | 2 | 0 | 49
38952.3603 | 2 | 0 | 49
38952.3625 | 3 | 0 | 49
38952.3646 | 790 | 0 | 49
38952.3667 | 1735 | 0 | 49
38952.3689 | 2077 | 0 | 49
49
38952.3497 | 1 | 0 | 50
38952.3518 | 1 | 0 | 50
38952.3539 | 1 | 0 | 50
38952.3561 | 2 | 0 | 50
38952.3582 | 2 | 0 | 50
38952.3603 | 3 | 0 | 50
38952.3625 | 2122 | 0 | 50
38952.3646 | 1910 | 0 | 50
38952.3668 | 2074 | 0 | 50
38952.3689 | 1316 | 0 | 50
50
38952.3497 | 1 | 0 | 51
38952.3518 | 1 | 0 | 51
38952.3539 | 1 | 0 | 51
38952.3561 | 1 | 0 | 51
38952.3582 | 2 | 0 | 51
38952.3604 | 2 | 0 | 51
38952.3625 | 4 | 0 | 51
38952.3646 | 1471 | 0 | 51
38952.3668 | 1379 | 0 | 51
38952.3689 | 1730 | 0 | 51
51
38952.3497 | 1 | 0 | 52
38952.3518 | 1 | 0 | 52
38952.354 | 1 | 0 | 52
38952.3561 | 1 | 0 | 52
38952.3582 | 2 | 0 | 52
38952.3604 | 2 | 0 | 52
38952.3625 | 2207 | 0 | 52
38952.3647 | 2099 | 0 | 52
38952.3668 | 2110 | 0 | 52
38952.3689 | 1978 | 0 | 52
52
38952.3497 | 1 | 0 | 53
38952.3518 | 1 | 0 | 53
38952.354 | 1 | 0 | 53
38952.3561 | 2 | 0 | 53
38952.3583 | 2 | 0 | 53
38952.3604 | 2 | 0 | 53
38952.3625 | 5 | 0 | 53
38952.3647 | 1401 | 0 | 53
38952.3668 | 1146 | 0 | 53
38952.3689 | 2113 | 0 | 53
53
38952.3497 | 1 | 0 | 54
38952.3519 | 1 | 0 | 54
38952.354 | 1 | 0 | 54
38952.3561 | 2508 | 0 | 54
38952.3583 | 2103 | 0 | 54
38952.3604 | 2516 | 0 | 54
38952.3625 | 1977 | 0 | 54
38952.3647 | 1964 | 0 | 54
38952.3668 | 2078 | 0 | 54
38952.369 | 2024 | 0 | 54
54
38952.3497 | 1 | 0 | 55
38952.3519 | 2 | 0 | 55
38952.354 | 2 | 0 | 55
38952.3561 | 5 | 0 | 55
38952.3583 | 5 | 0 | 55
38952.3604 | 5 | 0 | 55
38952.3626 | 5 | 0 | 55
38952.3647 | 1942 | 0 | 55
38952.3668 | 1395 | 0 | 55
38952.369 | 2164 | 0 | 55
55
38952.3497 | 1 | 0 | 56
38952.3519 | 1 | 0 | 56
38952.354 | 1 | 0 | 56
38952.3562 | 2461 | 0 | 56
38952.3583 | 2548 | 0 | 56
38952.3604 | 2035 | 0 | 56
38952.3626 | 2051 | 0 | 56
38952.3647 | 1967 | 0 | 56
38952.3669 | 2122 | 0 | 56
38952.369 | 2377 | 0 | 56
56
38952.3498 | 1 | 0 | 57
38952.3519 | 1 | 0 | 57
38952.354 | 1 | 0 | 57
38952.3562 | 6 | 0 | 57
38952.3583 | 5 | 0 | 57
38952.3605 | 5 | 0 | 57
38952.3626 | 5 | 0 | 57
38952.3647 | 1714 | 0 | 57
38952.3669 | 811 | 0 | 57
57
38952.3498 | 1 | 0 | 58
38952.3519 | 1 | 0 | 58
38952.3541 | 1 | 0 | 58
38952.3562 | 4 | 0 | 58
38952.3583 | 4 | 0 | 58
38952.3605 | 4 | 0 | 58
38952.3626 | 155 | 0 | 58
38952.3647 | 2337 | 0 | 58
38952.3669 | 2015 | 0 | 58
38952.369 | 2450 | 0 | 58
58
38952.3498 | 1 | 0 | 59
38952.3519 | 1 | 0 | 59
38952.3541 | 1 | 0 | 59
38952.3562 | 3 | 0 | 59
38952.3583 | 4 | 0 | 59
38952.3605 | 4 | 0 | 59
38952.3626 | 4 | 0 | 59
38952.3648 | 1975 | 0 | 59
38952.3669 | 968 | 0 | 59
38952.369 | 1730 | 0 | 59
59
38952.3498 | 1 | 0 | 60
38952.3519 | 1 | 0 | 60
38952.3541 | 1 | 0 | 60
38952.3562 | 3 | 0 | 60
38952.3584 | 2 | 0 | 60
38952.3605 | 3 | 0 | 60
38952.3626 | 181 | 0 | 60
38952.3648 | 2257 | 0 | 60
38952.3669 | 2018 | 0 | 60
38952.3691 | 2447 | 0 | 60
60
38952.3498 | 1 | 0 | 61
38952.352 | 1 | 0 | 61
38952.3541 | 1 | 0 | 61
38952.3562 | 2 | 0 | 61
38952.3584 | 3 | 0 | 61
38952.3605 | 3 | 0 | 61
38952.3627 | 4 | 0 | 61
38952.3648 | 1679 | 0 | 61
38952.3669 | 783 | 0 | 61
38952.3691 | 2020 | 0 | 61
61
38952.3498 | 1 | 0 | 62
38952.352 | 1 | 0 | 62
38952.3541 | 1 | 0 | 62
38952.3563 | 2 | 0 | 62
38952.3584 | 2 | 0 | 62
38952.3605 | 3 | 0 | 62
38952.3627 | 3 | 0 | 62
38952.3648 | 4 | 0 | 62
38952.367 | 4 | 0 | 62
38952.3691 | 4 | 0 | 62
62
38952.3499 | 1 | 0 | 63
38952.352 | 1 | 0 | 63
38952.3541 | 1 | 0 | 63
38952.3563 | 2 | 0 | 63
38952.3584 | 2 | 0 | 63
38952.3606 | 3 | 0 | 63
38952.3627 | 3 | 0 | 63
38952.3648 | 1727 | 0 | 63
38952.367 | 761 | 0 | 63
38952.3691 | 1903 | 0 | 63
63
38952.3499 | 1 | 0 | 64
38952.352 | 1 | 0 | 64
38952.3542 | 1 | 0 | 64
38952.3563 | 2 | 0 | 64
38952.3584 | 2 | 0 | 64
38952.3606 | 2 | 0 | 64
38952.3627 | 4 | 0 | 64
38952.3648 | 4 | 0 | 64
38952.367 | 4 | 0 | 64
38952.3691 | 4 | 0 | 64
64
38952.3499 | 1 | 0 | 65
38952.352 | 1 | 0 | 65
38952.3542 | 1 | 0 | 65
38952.3563 | 2 | 0 | 65
38952.3584 | 2 | 0 | 65
38952.3606 | 2 | 0 | 65
38952.3627 | 3 | 0 | 65
38952.3649 | 1837 | 0 | 65
38952.367 | 1151 | 0 | 65
38952.3691 | 2050 | 0 | 65
65
38952.3499 | 1 | 0 | 66
38952.352 | 1 | 0 | 66
38952.3542 | 1 | 0 | 66
38952.3563 | 2 | 0 | 66
38952.3585 | 2 | 0 | 66
38952.3606 | 2 | 0 | 66
38952.3627 | 2327 | 0 | 66
38952.3649 | 2208 | 0 | 66
38952.367 | 2100 | 0 | 66
38952.3692 | 1624 | 0 | 66
66
38952.3499 | 1 | 0 | 67
38952.3521 | 1 | 0 | 67
38952.3542 | 1 | 0 | 67
38952.3563 | 2 | 0 | 67
38952.3585 | 2 | 0 | 67
38952.3606 | 2 | 0 | 67
38952.3628 | 5 | 0 | 67
38952.3649 | 1936 | 0 | 67
38952.367 | 1065 | 0 | 67
38952.3692 | 2118 | 0 | 67
67
38952.3499 | 1 | 0 | 68
38952.3521 | 2 | 0 | 68
38952.3542 | 1 | 0 | 68
38952.3564 | 2 | 0 | 68
38952.3585 | 2 | 0 | 68
38952.3606 | 2 | 0 | 68
38952.3628 | 2561 | 0 | 68
38952.3649 | 2057 | 0 | 68
38952.367 | 2011 | 0 | 68
38952.3692 | 2229 | 0 | 68
68
38952.35 | 1 | 0 | 69
38952.3521 | 1 | 0 | 69
38952.3542 | 2 | 0 | 69
38952.3564 | 2 | 0 | 69
38952.3585 | 2 | 0 | 69
38952.3606 | 2 | 0 | 69
38952.3628 | 5 | 0 | 69
38952.3649 | 1990 | 0 | 69
38952.3671 | 1271 | 0 | 69
38952.3692 | 1839 | 0 | 69
69
38952.35 | 1 | 0 | 70
38952.3521 | 1 | 0 | 70
38952.3542 | 1 | 0 | 70
38952.3564 | 2292 | 0 | 70
38952.3585 | 2121 | 0 | 70
38952.3607 | 1963 | 0 | 70
38952.3628 | 2258 | 0 | 70
38952.3649 | 2193 | 0 | 70
38952.3671 | 2512 | 0 | 70
38952.3692 | 2226 | 0 | 70
70
38952.35 | 1 | 0 | 71
38952.3521 | 1 | 0 | 71
38952.3543 | 1 | 0 | 71
38952.3564 | 5 | 0 | 71
38952.3585 | 5 | 0 | 71
38952.3607 | 5 | 0 | 71
38952.3628 | 5 | 0 | 71
38952.365 | 1643 | 0 | 71
38952.3671 | 1326 | 0 | 71
38952.3692 | 2163 | 0 | 71
71
38952.35 | 1 | 0 | 72
38952.3521 | 1 | 0 | 72
38952.3543 | 1 | 0 | 72
38952.3564 | 1940 | 0 | 72
38952.3586 | 2517 | 0 | 72
38952.3607 | 2192 | 0 | 72
38952.3628 | 2334 | 0 | 72
38952.365 | 1963 | 0 | 72
38952.3671 | 2136 | 0 | 72
38952.3692 | 2477 | 0 | 72
72
38952.35 | 1 | 0 | 73
38952.3522 | 1 | 0 | 73
38952.3543 | 1 | 0 | 73
38952.3564 | 5 | 0 | 73
38952.3586 | 5 | 0 | 73
38952.3607 | 5 | 0 | 73
38952.3628 | 4 | 0 | 73
38952.365 | 2099 | 0 | 73
38952.3671 | 1372 | 0 | 73
38952.3693 | 2023 | 0 | 73
73
38952.35 | 1 | 0 | 74
38952.3522 | 1 | 0 | 74
38952.3543 | 1 | 0 | 74
38952.3564 | 5 | 0 | 74
38952.3607 | 4 | 0 | 74
38952.3629 | 242 | 0 | 74
38952.365 | 2190 | 0 | 74
38952.3671 | 1956 | 0 | 74
38952.3693 | 2046 | 0 | 74
74
38952.3501 | 1 | 0 | 75
38952.3522 | 1 | 0 | 75
38952.3543 | 1 | 0 | 75
38952.3565 | 3 | 0 | 75
38952.3586 | 4 | 0 | 75
38952.3607 | 3 | 0 | 75
38952.3629 | 4 | 0 | 75
38952.365 | 1756 | 0 | 75
38952.3672 | 865 | 0 | 75
38952.3693 | 2169 | 0 | 75
75
38952.3501 | 1 | 0 | 76
38952.3522 | 1 | 0 | 76
38952.3544 | 1 | 0 | 76
38952.3565 | 3 | 0 | 76
38952.3586 | 3 | 0 | 76
38952.3608 | 3 | 0 | 76
38952.3629 | 1206 | 0 | 76
38952.365 | 2384 | 0 | 76
38952.3672 | 2204 | 0 | 76
38952.3693 | 1898 | 0 | 76
76
38952.3501 | 1 | 0 | 77
38952.3522 | 1 | 0 | 77
38952.3544 | 1 | 0 | 77
38952.3565 | 2 | 0 | 77
38952.3586 | 2 | 0 | 77
38952.3608 | 2 | 0 | 77
38952.3629 | 1021 | 1065 | 77
38952.3651 | 1190 | 1167 | 77
38952.3672 | 922 | 941 | 77
38952.3693 | 933 | 912 | 77
77
38952.3501 | 1 | 0 | 78
38952.3522 | 1 | 0 | 78
38952.3544 | 1 | 0 | 78
38952.3565 | 3 | 0 | 78
38952.3587 | 2 | 0 | 78
38952.3608 | 2 | 0 | 78
38952.3629 | 940 | 909 | 78
38952.3651 | 1085 | 1054 | 78
38952.3672 | 1019 | 986 | 78
38952.3694 | 1039 | 1006 | 78
78
38952.3501 | 1 | 0 | 79
38952.3523 | 1 | 0 | 79
38952.3544 | 1 | 0 | 79
38952.3565 | 2 | 0 | 79
38952.3587 | 2 | 0 | 79
38952.3608 | 2 | 0 | 79
38952.363 | 5 | 11 | 79
38952.3651 | 5 | 10 | 79
38952.3672 | 4 | 9 | 79
38952.3694 | 4 | 9 | 79
79
38952.3501 | 1 | 0 | 80
38952.3523 | 1 | 0 | 80
38952.3544 | 1 | 0 | 80
38952.3566 | 2 | 0 | 80
38952.3587 | 2 | 0 | 80
38952.3608 | 2 | 0 | 80
38952.363 | 2391 | 4 | 80
38952.3651 | 1912 | 5 | 80
38952.3672 | 1779 | 5 | 80
38952.3694 | 1438 | 4 | 80
80
38952.3502 | 1 | 0 | 81
38952.3523 | 2 | 0 | 81
38952.3544 | 1 | 0 | 81
38952.3566 | 2 | 0 | 81
38952.3587 | 2 | 0 | 81
38952.3608 | 2 | 0 | 81
38952.363 | 4 | 3 | 81
38952.3651 | 4 | 2 | 81
38952.3673 | 4 | 3 | 81
38952.3694 | 4 | 2 | 81
81
38952.3502 | 1 | 0 | 82
38952.3523 | 1 | 0 | 82
38952.3544 | 1 | 0 | 82
38952.3566 | 1 | 0 | 82
38952.3587 | 2 | 0 | 82
38952.3609 | 2 | 0 | 82
38952.363 | 2407 | 1 | 82
38952.3651 | 2242 | 2 | 82
38952.3673 | 1986 | 1 | 82
38952.3694 | 1716 | 1 | 82
82
38952.3502 | 1 | 0 | 83
38952.3523 | 1 | 0 | 83
38952.3545 | 1 | 0 | 83
38952.3566 | 1 | 0 | 83
38952.3587 | 2 | 0 | 83
38952.3609 | 1 | 0 | 83
38952.363 | 5 | 1 | 83
38952.3652 | 4 | 1 | 83
38952.3673 | 4 | 1 | 83
38952.3694 | 3 | 1 | 83
83
38952.3502 | 1 | 0 | 84
38952.3523 | 1 | 0 | 84
38952.3545 | 38 | 0 | 84
38952.3566 | 2135 | 0 | 84
38952.3587 | 2267 | 0 | 84
38952.3609 | 2245 | 0 | 84
38952.363 | 2060 | 1 | 84
38952.3652 | 2489 | 1 | 84
38952.3673 | 2505 | 1 | 84
38952.3694 | 2278 | 1 | 84
84
38952.3502 | 1 | 0 | 85
38952.3523 | 1 | 0 | 85
38952.3545 | 1 | 0 | 85
38952.3566 | 5 | 0 | 85
38952.3588 | 5 | 0 | 85
38952.3609 | 4 | 0 | 85
38952.363 | 5 | 0 | 85
38952.3652 | 5 | 0 | 85
38952.3673 | 4 | 1 | 85
38952.3695 | 4 | 0 | 85
85
38952.3502 | 1 | 0 | 86
38952.3524 | 1 | 0 | 86
38952.3545 | 1 | 0 | 86
38952.3566 | 2283 | 0 | 86
38952.3588 | 2533 | 0 | 86
38952.3609 | 2356 | 0 | 86
38952.3631 | 2411 | 0 | 86
38952.3652 | 2286 | 1 | 86
38952.3673 | 2310 | 0 | 86
38952.3695 | 2202 | 0 | 86
86
38952.3502 | 1 | 0 | 87
38952.3524 | 1 | 0 | 87
38952.3545 | 1 | 0 | 87
38952.3567 | 5 | 0 | 87
38952.3588 | 5 | 0 | 87
38952.3609 | 5 | 0 | 87
38952.3631 | 5 | 0 | 87
38952.3652 | 4 | 0 | 87
38952.3674 | 4 | 0 | 87
38952.3695 | 3 | 0 | 87
87
38952.3503 | 1 | 0 | 88
38952.3524 | 1 | 0 | 88
38952.3545 | 1 | 0 | 88
38952.3567 | 4 | 0 | 88
38952.3588 | 4 | 0 | 88
38952.361 | 4 | 0 | 88
38952.3631 | 1665 | 0 | 88
38952.3652 | 2129 | 0 | 88
38952.3674 | 2226 | 0 | 88
38952.3695 | 2289 | 0 | 88
88
38952.3503 | 1 | 0 | 89
38952.3524 | 1 | 0 | 89
38952.3546 | 1 | 0 | 89
38952.3567 | 4 | 0 | 89
38952.3588 | 4 | 0 | 89
38952.361 | 3 | 0 | 89
38952.3631 | 5 | 0 | 89
38952.3653 | 5 | 0 | 89
38952.3674 | 4 | 0 | 89
38952.3695 | 3 | 0 | 89
89
38952.3503 | 1 | 0 | 90
38952.3524 | 1 | 0 | 90
38952.3546 | 1 | 0 | 90
38952.3567 | 3 | 0 | 90
38952.3589 | 3 | 0 | 90
38952.361 | 3 | 0 | 90
38952.3631 | 2007 | 0 | 90
38952.3653 | 1982 | 0 | 90
38952.3674 | 2138 | 0 | 90
38952.3695 | 2284 | 0 | 90
90
38952.3503 | 1 | 0 | 91
38952.3525 | 1 | 0 | 91
38952.3546 | 1 | 0 | 91
38952.3567 | 2 | 0 | 91
38952.3589 | 3 | 0 | 91
38952.361 | 2 | 0 | 91
38952.3631 | 5 | 0 | 91
38952.3653 | 4 | 0 | 91
38952.3674 | 4 | 0 | 91
38952.3696 | 4 | 0 | 91
91
38952.3503 | 1 | 0 | 92
38952.3525 | 1 | 0 | 92
38952.3546 | 1 | 0 | 92
38952.3567 | 2 | 0 | 92
38952.3589 | 2 | 0 | 92
38952.361 | 2 | 0 | 92
38952.3632 | 2246 | 0 | 92
38952.3653 | 2089 | 0 | 92
38952.3674 | 1788 | 0 | 92
38952.3696 | 1677 | 0 | 92
92
38952.3503 | 1 | 0 | 93
38952.3525 | 1 | 0 | 93
38952.3546 | 1 | 0 | 93
38952.3568 | 2 | 0 | 93
38952.3589 | 3 | 0 | 93
38952.361 | 2 | 0 | 93
38952.3632 | 5 | 0 | 93
38952.3653 | 5 | 0 | 93
38952.3675 | 4 | 0 | 93
38952.3696 | 4 | 0 | 93
93
38952.3504 | 1 | 0 | 94
38952.3525 | 1 | 0 | 94
38952.3546 | 1 | 0 | 94
38952.3568 | 2 | 0 | 94
38952.3589 | 2 | 0 | 94
38952.3611 | 2 | 0 | 94
38952.3632 | 2537 | 0 | 94
38952.3653 | 2405 | 0 | 94
38952.3675 | 1988 | 0 | 94
38952.3696 | 2124 | 0 | 94
94
38952.3504 | 1 | 0 | 95
38952.3525 | 1 | 0 | 95
38952.3547 | 1 | 0 | 95
38952.3568 | 2 | 0 | 95
38952.3589 | 2 | 0 | 95
38952.3611 | 2 | 0 | 95
38952.3632 | 5 | 0 | 95
38952.3653 | 4 | 0 | 95
38952.3675 | 4 | 0 | 95
38952.3696 | 4 | 0 | 95
95
38952.3504 | 2 | 0 | 96
38952.3525 | 1 | 0 | 96
38952.3547 | 1 | 0 | 96
38952.3568 | 1958 | 0 | 96
38952.3589 | 2525 | 0 | 96
38952.3611 | 2179 | 0 | 96
38952.3632 | 2130 | 0 | 96
38952.3654 | 2005 | 0 | 96
38952.3675 | 2007 | 0 | 96
38952.3696 | 2176 | 0 | 96
96
38952.3504 | 1 | 0 | 97
38952.3525 | 1 | 0 | 97
38952.3547 | 1 | 0 | 97
38952.3568 | 5 | 0 | 97
38952.359 | 5 | 0 | 97
38952.3611 | 5 | 0 | 97
38952.3632 | 5 | 0 | 97
38952.3654 | 4 | 0 | 97
38952.3675 | 4 | 0 | 97
38952.3697 | 4 | 0 | 97
97
38952.3504 | 1 | 0 | 98
38952.3526 | 1 | 0 | 98
38952.3547 | 1 | 0 | 98
38952.3568 | 2336 | 0 | 98
38952.359 | 2437 | 0 | 98
38952.3611 | 2451 | 0 | 98
38952.3633 | 2535 | 0 | 98
38952.3654 | 2398 | 0 | 98
38952.3675 | 2025 | 0 | 98
38952.3697 | 2123 | 0 | 98
98
38952.3504 | 1 | 0 | 99
38952.3526 | 1 | 0 | 99
38952.3547 | 1 | 0 | 99
38952.3569 | 5 | 0 | 99
38952.359 | 5 | 0 | 99
38952.3611 | 5 | 0 | 99
38952.3633 | 5 | 0 | 99
38952.3654 | 4 | 0 | 99
38952.3675 | 4 | 0 | 99
38952.3697 | 4 | 0 | 99
99
38952.3505 | 1 | 0 | 100
38952.3526 | 1 | 0 | 100
38952.3547 | 1 | 0 | 100
38952.3569 | 4 | 0 | 100
38952.359 | 4 | 0 | 100
38952.3611 | 4 | 0 | 100
38952.3633 | 2386 | 0 | 100
38952.3654 | 1985 | 0 | 100
38952.3676 | 2394 | 0 | 100
38952.3697 | 1981 | 0 | 100
100
38952.3505 | 1 | 0 | 101
38952.3526 | 1 | 0 | 101
38952.3548 | 1 | 0 | 101
38952.3569 | 4 | 0 | 101
38952.359 | 4 | 0 | 101
38952.3612 | 3 | 0 | 101
38952.3633 | 5 | 0 | 101
38952.3654 | 4 | 0 | 101
38952.3676 | 4 | 0 | 101
38952.3697 | 3 | 0 | 101
101
38952.3505 | 1 | 0 | 102
38952.3526 | 1 | 0 | 102
38952.3548 | 1 | 0 | 102
38952.3569 | 3 | 0 | 102
38952.359 | 3 | 0 | 102
38952.3612 | 2 | 0 | 102
38952.3633 | 2402 | 0 | 102
38952.3655 | 2364 | 0 | 102
38952.3676 | 2118 | 0 | 102
38952.3697 | 2431 | 0 | 102
102
38952.3505 | 1 | 0 | 103
38952.3527 | 1 | 0 | 103
38952.3548 | 1 | 0 | 103
38952.3569 | 3 | 0 | 103
38952.3591 | 2 | 0 | 103
38952.3612 | 640 | 592 | 103
38952.3633 | 1963 | 0 | 103
38952.3655 | 2036 | 0 | 103
38952.3676 | 2195 | 0 | 103
38952.3698 | 1817 | 0 | 103
103
38952.3505 | 1 | 0 | 104
38952.3527 | 2 | 0 | 104
38952.3548 | 1 | 0 | 104
38952.3569 | 2 | 0 | 104
38952.3591 | 2 | 0 | 104
38952.3612 | 1782 | 133 | 104
38952.3634 | 2219 | 0 | 104
38952.3655 | 2071 | 0 | 104
38952.3676 | 1761 | 0 | 104
38952.3698 | 2072 | 0 | 104
104
38952.3505 | 1 | 0 | 105
38952.3527 | 1 | 0 | 105
38952.3548 | 1 | 0 | 105
38952.357 | 2 | 0 | 105
38952.3591 | 2 | 0 | 105
38952.3612 | 1950 | 1 | 105
38952.3634 | 1935 | 0 | 105
38952.3655 | 2174 | 0 | 105
38952.3677 | 1841 | 0 | 105
38952.3698 | 1476 | 0 | 105
105
38952.3506 | 1 | 0 | 106
38952.3527 | 1 | 0 | 106
38952.3548 | 1 | 0 | 106
38952.357 | 2271 | 0 | 106
38952.3591 | 2153 | 0 | 106
38952.3613 | 2425 | 1 | 106
38952.3634 | 2214 | 0 | 106
38952.3655 | 2542 | 0 | 106
38952.3677 | 2390 | 0 | 106
38952.3698 | 2411 | 0 | 106
106
38952.3506 | 1 | 0 | 107
38952.3527 | 1 | 0 | 107
38952.3548 | 1 | 0 | 107
38952.357 | 5 | 0 | 107
38952.3591 | 5 | 0 | 107
38952.3613 | 498 | 0 | 107
38952.3634 | 2248 | 0 | 107
38952.3655 | 2369 | 0 | 107
38952.3677 | 1879 | 0 | 107
38952.3698 | 1942 | 0 | 107
107
38952.3506 | 1 | 0 | 108
38952.3527 | 1 | 0 | 108
38952.3549 | 1 | 0 | 108
38952.357 | 2313 | 0 | 108
38952.3591 | 2279 | 0 | 108
38952.3613 | 2317 | 0 | 108
38952.3634 | 2181 | 0 | 108
38952.3656 | 1960 | 0 | 108
38952.3677 | 2465 | 0 | 108
38952.3698 | 1969 | 0 | 108
108
38952.3506 | 1 | 0 | 109
38952.3527 | 1 | 0 | 109
38952.3549 | 1 | 0 | 109
38952.357 | 5 | 0 | 109
38952.3592 | 5 | 0 | 109
38952.3613 | 837 | 0 | 109
38952.3634 | 2230 | 0 | 109
38952.3656 | 1861 | 0 | 109
38952.3677 | 1961 | 0 | 109
38952.3698 | 1472 | 0 | 109
109
38952.3506 | 1 | 0 | 110
38952.3528 | 1 | 0 | 110
38952.3549 | 1 | 0 | 110
38952.357 | 4 | 0 | 110
38952.3592 | 5 | 0 | 110
38952.3613 | 5 | 0 | 110
38952.3656 | 2216 | 0 | 110
38952.3677 | 2472 | 0 | 110
38952.3699 | 2167 | 0 | 110
110
38952.3506 | 1 | 0 | 111
38952.3528 | 1 | 0 | 111
38952.3549 | 1 | 0 | 111
38952.357 | 4 | 0 | 111
38952.3592 | 4 | 0 | 111
38952.3613 | 2435 | 0 | 111
38952.3635 | 2270 | 0 | 111
38952.3656 | 2142 | 0 | 111
38952.3677 | 1614 | 0 | 111
38952.3699 | 1365 | 0 | 111
111
38952.3506 | 1 | 0 | 112
38952.3528 | 1 | 0 | 112
38952.3549 | 1 | 0 | 112
38952.3571 | 3 | 0 | 112
38952.3592 | 3 | 0 | 112
38952.3613 | 5 | 0 | 112
38952.3635 | 2379 | 0 | 112
38952.3656 | 1965 | 0 | 112
38952.3678 | 1956 | 0 | 112
38952.3699 | 2173 | 0 | 112
112
38952.3507 | 1 | 0 | 113
38952.3528 | 1 | 0 | 113
38952.3549 | 1 | 0 | 113
38952.3571 | 2 | 0 | 113
38952.3592 | 3 | 0 | 113
38952.3614 | 2043 | 0 | 113
38952.3635 | 2416 | 0 | 113
38952.3656 | 2141 | 0 | 113
38952.3678 | 1612 | 0 | 113
38952.3699 | 2019 | 0 | 113
113
38952.3507 | 1 | 0 | 114
38952.3528 | 1 | 0 | 114
38952.355 | 1839 | 0 | 114
38952.3571 | 2048 | 0 | 114
38952.3592 | 2452 | 0 | 114
38952.3614 | 2060 | 0 | 114
38952.3635 | 2257 | 0 | 114
38952.3657 | 2506 | 0 | 114
38952.3678 | 2113 | 0 | 114
38952.3699 | 2103 | 0 | 114
114
38952.3507 | 1 | 0 | 115
38952.3528 | 1 | 0 | 115
38952.355 | 4 | 0 | 115
38952.3571 | 5 | 0 | 115
38952.3593 | 5 | 0 | 115
38952.3614 | 2555 | 0 | 115
38952.3635 | 2472 | 0 | 115
38952.3657 | 2428 | 0 | 115
38952.3678 | 2073 | 0 | 115
38952.37 | 1888 | 0 | 115
115
38952.3507 | 1 | 0 | 116
38952.3529 | 1 | 0 | 116
38952.355 | 3 | 0 | 116
38952.3571 | 2495 | 0 | 116
38952.3593 | 2346 | 0 | 116
38952.3614 | 2561 | 0 | 116
38952.3636 | 1998 | 0 | 116
38952.3657 | 2129 | 0 | 116
38952.3678 | 2117 | 0 | 116
38952.37 | 2165 | 0 | 116
116
38952.3507 | 1 | 0 | 117
38952.3529 | 1 | 0 | 117
38952.355 | 2 | 0 | 117
38952.3572 | 5 | 0 | 117
38952.3593 | 5 | 0 | 117
38952.3614 | 1989 | 0 | 117
38952.3636 | 1963 | 0 | 117
38952.3657 | 1867 | 0 | 117
38952.3678 | 1541 | 0 | 117
38952.37 | 1972 | 0 | 117
117
38952.3508 | 1 | 0 | 118
38952.3529 | 1 | 0 | 118
38952.355 | 2 | 0 | 118
38952.3572 | 5 | 0 | 118
38952.3593 | 4 | 0 | 118
38952.3614 | 5 | 0 | 118
38952.3636 | 2106 | 0 | 118
38952.3657 | 2047 | 0 | 118
38952.3679 | 2418 | 0 | 118
38952.37 | 2013 | 0 | 118
118
38952.3508 | 1 | 0 | 119
38952.3529 | 1 | 0 | 119
38952.355 | 2 | 0 | 119
38952.3572 | 4 | 0 | 119
38952.3593 | 3 | 0 | 119
38952.3615 | 1994 | 0 | 119
38952.3636 | 2107 | 0 | 119
38952.3657 | 2205 | 0 | 119
38952.3679 | 1536 | 0 | 119
38952.37 | 2046 | 0 | 119
119
38952.3508 | 1 | 0 | 120
38952.3529 | 1 | 0 | 120
38952.3551 | 2 | 0 | 120
38952.3572 | 3 | 0 | 120
38952.3593 | 3 | 0 | 120
38952.3615 | 5 | 0 | 120
38952.3636 | 2407 | 0 | 120
38952.3658 | 2150 | 0 | 120
38952.3679 | 2427 | 0 | 120
38952.37 | 2075 | 0 | 120
120
38952.3508 | 1 | 0 | 121
38952.3529 | 1 | 0 | 121
38952.3551 | 2200 | 0 | 121
38952.3572 | 2211 | 0 | 121
38952.3594 | 2554 | 0 | 121
38952.3615 | 2032 | 0 | 121
38952.3636 | 2050 | 0 | 121
38952.3658 | 2396 | 0 | 121
38952.3679 | 2071 | 0 | 121
38952.37 | 2008 | 0 | 121
121
38952.3508 | 1 | 0 | 122
38952.353 | 1 | 0 | 122
38952.3551 | 4 | 0 | 122
38952.3572 | 2411 | 0 | 122
38952.3594 | 2408 | 0 | 122
38952.3615 | 2142 | 0 | 122
38952.3636 | 2101 | 0 | 122
38952.3658 | 2385 | 0 | 122
38952.3679 | 1957 | 0 | 122
38952.3701 | 2320 | 0 | 122
122
38952.3508 | 1 | 0 | 123
38952.353 | 1 | 0 | 123
38952.3551 | 1995 | 0 | 123
38952.3572 | 1996 | 0 | 123
38952.3594 | 2478 | 0 | 123
38952.3615 | 2340 | 0 | 123
38952.3637 | 1974 | 0 | 123
38952.3658 | 2125 | 0 | 123
38952.3679 | 2446 | 0 | 123
38952.3701 | 2339 | 0 | 123
123
38952.3508 | 1 | 0 | 124
38952.353 | 1 | 0 | 124
38952.3551 | 5 | 0 | 124
38952.3573 | 6 | 0 | 124
38952.3594 | 5 | 0 | 124
38952.3615 | 5 | 0 | 124
38952.3637 | 1908 | 0 | 124
38952.3658 | 2152 | 0 | 124
38952.368 | 2322 | 0 | 124
38952.3701 | 2227 | 0 | 124
124
38952.3509 | 1 | 0 | 125
38952.353 | 1 | 0 | 125
38952.3551 | 2258 | 0 | 125
38952.3573 | 2383 | 0 | 125
38952.3594 | 2526 | 0 | 125
38952.3616 | 2079 | 0 | 125
38952.3637 | 2490 | 0 | 125
38952.3658 | 2172 | 0 | 125
38952.368 | 2487 | 0 | 125
38952.3701 | 2306 | 0 | 125
125
38952.3509 | 1 | 0 | 126
38952.353 | 1 | 0 | 126
38952.3552 | 5 | 0 | 126
38952.3573 | 5 | 0 | 126
38952.3594 | 5 | 0 | 126
38952.3616 | 4 | 0 | 126
38952.3637 | 2166 | 0 | 126
38952.3658 | 1897 | 0 | 126
38952.368 | 1890 | 0 | 126
38952.3701 | 2351 | 0 | 126
126
38952.3509 | 1 | 0 | 127
38952.3552 | 4 | 0 | 127
38952.3573 | 2510 | 0 | 127
38952.3595 | 2175 | 0 | 127
38952.3616 | 1980 | 0 | 127
38952.3637 | 2095 | 0 | 127
38952.3659 | 2094 | 0 | 127
38952.368 | 2539 | 0 | 127
38952.3701 | 2248 | 0 | 127
127
38952.3509 | 1 | 0 | 128
38952.3531 | 1 | 0 | 128
38952.3552 | 3 | 0 | 128
38952.3573 | 6 | 0 | 128
38952.3595 | 5 | 0 | 128
38952.3616 | 5 | 0 | 128
38952.3637 | 2075 | 0 | 128
38952.3659 | 2147 | 0 | 128
38952.368 | 2375 | 0 | 128
38952.3702 | 2450 | 0 | 128
128
38952.3509 | 1 | 0 | 129
38952.3531 | 1 | 0 | 129
38952.3552 | 3 | 0 | 129
38952.3573 | 2528 | 0 | 129
38952.3595 | 2443 | 0 | 129
38952.3616 | 2402 | 0 | 129
38952.3638 | 2281 | 0 | 129
38952.3659 | 2403 | 0 | 129
38952.368 | 2471 | 0 | 129
38952.3702 | 2515 | 0 | 129
129
38952.3509 | 1 | 0 | 130
38952.3531 | 1 | 0 | 130
38952.3552 | 3 | 0 | 130
38952.3574 | 6 | 0 | 130
38952.3595 | 5 | 0 | 130
38952.3616 | 5 | 0 | 130
38952.3638 | 2151 | 0 | 130
38952.3659 | 2328 | 0 | 130
38952.3681 | 2299 | 0 | 130
38952.3702 | 2256 | 0 | 130
130
38952.351 | 1 | 0 | 131
38952.3531 | 1 | 0 | 131
38952.3552 | 2 | 0 | 131
38952.3574 | 5 | 0 | 131
38952.3595 | 5 | 0 | 131
38952.3617 | 20 | 12 | 131
38952.3638 | 2255 | 1 | 131
38952.3659 | 2024 | 0 | 131
38952.3681 | 2463 | 0 | 131
38952.3702 | 2032 | 0 | 131
131
38952.351 | 1 | 0 | 132
38952.3531 | 1 | 0 | 132
38952.3553 | 2 | 0 | 132
38952.3574 | 5 | 0 | 132
38952.3595 | 5 | 0 | 132
38952.3617 | 20 | 14 | 132
38952.3638 | 2427 | 1 | 132
38952.3659 | 2025 | 0 | 132
38952.3681 | 1962 | 0 | 132
38952.3702 | 2009 | 0 | 132
132

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6 | Tray Rung
0 | -158 | 18.7 | 26.3 | 21.4 | 26.1 | 28.5 | 23.6 | 23.7 | 27.2
1 | -157 | 18.7 | 26.3 | 21.4 | 26.1 | 28.5 | 23.6 | 23.7 | 27.2
2 | -156 | 18.7 | 26.3 | 21.4 | 26.1 | 28.5 | 23.6 | 23.7 | 27.2
3 | -155 | 18.7 | 26.1 | 21.8 | 25.9 | 28 | 23.6 | 23.7 | 27.3
4 | -154 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
5 | -153 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
6 | -152 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
7 | -151 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
8 | -150 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
9 | -149 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
10 | -148 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
11 | -147 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
12 | -146 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
13 | -145 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
14 | -144 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
15 | -143 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
16 | -142 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
17 | -141 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
18 | -140 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
19 | -139 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
20 | -138 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
21 | -137 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.1
22 | -136 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.1
23 | -135 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.1
24 | -134 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
25 | -133 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
26 | -132 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
27 | -131 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
28 | -130 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
29 | -129 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
30 | -128 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
31 | -127 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
32 | -126 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
33 | -125 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
34 | -124 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
35 | -123 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
36 | -122 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
37 | -121 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
38 | -120 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
39 | -119 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.3
40 | -118 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
41 | -117 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
42 | -116 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
43 | -115 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
44 | -114 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
45 | -113 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
46 | -112 | 18.7 | 26 | 21.9 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
47 | -111 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
48 | -110 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
49 | -109 | 18.7 | 26 | 22 | 25.9 | 27.8 | 23.6 | 23.7 | 27.2
50 | -108 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
51 | -107 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.2
52 | -106 | 18.7 | 26 | 21.9 | 25.9 | 27.9 | 23.6 | 23.7 | 27.3
53 | -105 | 18.7 | 25.9 | 22.2 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
54 | -104 | 18.7 | 25.9 | 22.2 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
55 | -103 | 18.7 | 25.9 | 22.2 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
56 | -102 | 18.7 | 25.9 | 22.2 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
57 | -101 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.4
58 | -100 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
59 | -99 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.4
60 | -98 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
61 | -97 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.4
62 | -96 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
63 | -95 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.4
64 | -94 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
65 | -93 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
66 | -92 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
67 | -91 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
68 | -90 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
69 | -89 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
70 | -88 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
71 | -87 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
72 | -86 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
73 | -85 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
74 | -84 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
75 | -83 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
76 | -82 | 18.7 | 25.9 | 22.1 | 25.9 | 27.7 | 23.6 | 23.7 | 27.5
77 | -81 | 18.7 | 25.9 | 22.1 | 25.9 | 27.7 | 23.6 | 23.7 | 27.5
78 | -80 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
79 | -79 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
80 | -78 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
81 | -77 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
82 | -76 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
83 | -75 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
84 | -74 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
85 | -73 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
86 | -72 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
87 | -71 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
88 | -70 | 18.7 | 25.9 | 22.1 | 25.9 | 27.7 | 23.6 | 23.7 | 27.6
89 | -69 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
90 | -68 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
91 | -67 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
92 | -66 | 18.7 | 25.9 | 22.1 | 25.9 | 27.7 | 23.6 | 23.7 | 27.5
93 | -65 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
94 | -64 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
95 | -63 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
96 | -62 | 18.7 | 25.9 | 22.1 | 25.9 | 27.7 | 23.6 | 23.7 | 27.6
97 | -61 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
98 | -60 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
99 | -59 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
100 | -58 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
101 | -57 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
102 | -56 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.7
103 | -55 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.7
104 | -54 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.7
105 | -53 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
106 | -52 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
107 | -51 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
108 | -50 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
109 | -49 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
110 | -48 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
111 | -47 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
112 | -46 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.6
113 | -45 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
114 | -44 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
115 | -43 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
116 | -42 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
117 | -41 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.6
118 | -40 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
119 | -39 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
120 | -38 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
121 | -37 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
122 | -36 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
123 | -35 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
124 | -34 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
125 | -33 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
126 | -32 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
127 | -31 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
128 | -30 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.6 | 23.7 | 27.5
129 | -29 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
130 | -28 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
131 | -27 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
132 | -26 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.5
133 | -25 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
134 | -24 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
135 | -23 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
136 | -22 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
137 | -21 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
138 | -20 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
139 | -19 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
140 | -18 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
141 | -17 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
142 | -16 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
143 | -15 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
144 | -14 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
145 | -13 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
146 | -12 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
147 | -11 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
148 | -10 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
149 | -9 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
150 | -8 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
151 | -7 | 18.7 | 25.9 | 22.1 | 25.9 | 27.6 | 23.7 | 23.7 | 27.4
152 | -6 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.3
153 | -5 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
154 | -4 | 18.7 | 25.9 | 22.1 | 25.8 | 27.6 | 23.6 | 23.7 | 27.4
155 | -3 | 18.7 | 26 | 22 | 25.9 | 27.7 | 23.7 | 23.7 | 27.3
156 | -2 | 18.7 | 26.3 | 21.2 | 26.2 | 28.5 | 23.7 | 23.7 | 27.2
157 | -1 | 18.7 | 26.4 | 21 | 26.2 | 28.8 | 23.8 | 23.7 | 27.2
158 | 0 | 18.9 | 26.5 | 21 | 26.3 | 28.8 | 23.8 | 23.7 | 27.2
159 | 1 | 19.6 | 26.5 | 21 | 26.3 | 28.9 | 23.8 | 23.7 | 27.2
160 | 2 | 20.9 | 26.5 | 20.9 | 26.3 | 28.9 | 23.8 | 23.7 | 27.2
161 | 3 | 22.7 | 26.4 | 21 | 26.2 | 28.7 | 23.8 | 23.7 | 27.2
162 | 4 | 25 | 26.3 | 21.2 | 26.2 | 28.4 | 23.8 | 23.8 | 27.2
163 | 5 | 27.6 | 26.3 | 21.2 | 26.2 | 28.4 | 23.8 | 23.8 | 27.3
164 | 6 | 30.7 | 26.3 | 21.2 | 26.2 | 28.4 | 23.9 | 23.8 | 27.3
165 | 7 | 34 | 26.3 | 21.2 | 26.2 | 28.4 | 23.9 | 23.9 | 27.3
166 | 8 | 37.5 | 26.3 | 21.3 | 26.2 | 28.4 | 24 | 23.9 | 27.3
167 | 9 | 41.3 | 26.3 | 21.3 | 26.2 | 28.4 | 24 | 24 | 27.4
168 | 10 | 45.3 | 26.4 | 21.3 | 26.2 | 28.5 | 24.1 | 24.1 | 27.5
169 | 11 | 49.4 | 26.4 | 21.3 | 26.2 | 28.5 | 24.2 | 24.1 | 27.6
170 | 12 | 53.7 | 26.4 | 21.3 | 26.2 | 28.5 | 24.3 | 24.2 | 27.6
171 | 13 | 58.3 | 26.4 | 21.3 | 26.2 | 28.6 | 24.4 | 24.3 | 27.7
172 | 14 | 62.9 | 26.5 | 21.3 | 26.2 | 28.6 | 24.6 | 24.5 | 27.8
173 | 15 | 67.6 | 26.5 | 21.3 | 26.2 | 28.6 | 24.7 | 24.6 | 27.8
174 | 16 | 72.4 | 26.5 | 21.3 | 26.2 | 28.7 | 24.8 | 24.7 | 27.9
175 | 17 | 77.4 | 26.6 | 21.3 | 26.2 | 28.7 | 25 | 24.9 | 28.1
176 | 18 | 82.4 | 26.6 | 21.3 | 26.2 | 28.8 | 25.1 | 25 | 28.2
177 | 19 | 87.5 | 26.6 | 21.3 | 26.2 | 28.8 | 25.3 | 25.2 | 28.3
178 | 20 | 92.7 | 26.7 | 21.3 | 26.2 | 28.9 | 25.5 | 25.4 | 28.5
179 | 21 | 98.1 | 26.8 | 21.3 | 26.2 | 28.9 | 25.7 | 25.6 | 28.6
180 | 22 | 103.5 | 26.8 | 21.3 | 26.2 | 29 | 25.9 | 25.7 | 28.8
181 | 23 | 108.9 | 26.9 | 21.4 | 26.3 | 29.1 | 26.1 | 26 | 28.9
182 | 24 | 114.5 | 27 | 21.4 | 26.3 | 29.2 | 26.3 | 26.2 | 29.1
183 | 25 | 120 | 27.1 | 21.4 | 26.3 | 29.3 | 26.6 | 26.4 | 29.3
184 | 26 | 125.6 | 27.2 | 21.4 | 26.3 | 29.4 | 26.9 | 26.7 | 29.5
185 | 27 | 131.2 | 27.3 | 21.5 | 26.3 | 29.5 | 27.2 | 27 | 29.7
186 | 28 | 136.8 | 27.3 | 21.5 | 26.4 | 29.6 | 27.4 | 27.3 | 30
187 | 29 | 142.4 | 27.5 | 21.5 | 26.4 | 29.7 | 27.8 | 27.6 | 30.2
188 | 30 | 148.1 | 27.6 | 21.5 | 26.4 | 29.9 | 28.1 | 27.9 | 30.5
189 | 31 | 153.7 | 27.7 | 21.6 | 26.4 | 30 | 28.4 | 28.2 | 30.8
190 | 32 | 159.4 | 27.8 | 21.6 | 26.5 | 30.2 | 28.8 | 28.6 | 31.1
191 | 33 | 165.1 | 28 | 21.7 | 26.5 | 30.3 | 29.2 | 28.9 | 31.4
192 | 34 | 170.7 | 28.1 | 21.7 | 26.6 | 30.5 | 29.5 | 29.3 | 31.7
193 | 35 | 176.4 | 28.3 | 21.8 | 26.6 | 30.6 | 29.9 | 29.7 | 32
194 | 36 | 182 | 28.5 | 21.9 | 26.7 | 30.8 | 30.4 | 30.1 | 32.4
195 | 37 | 187.7 | 28.6 | 21.9 | 26.7 | 31 | 30.8 | 30.5 | 32.8
196 | 38 | 193.4 | 28.8 | 22 | 26.8 | 31.2 | 31.3 | 31 | 33.2
197 | 39 | 199 | 29 | 22.1 | 26.9 | 31.4 | 31.8 | 31.4 | 33.6
198 | 40 | 204.7 | 29.2 | 22.1 | 26.9 | 31.6 | 32.3 | 31.9 | 34
199 | 41 | 210.3 | 29.4 | 22.2 | 27 | 31.8 | 32.8 | 32.3 | 34.5
200 | 42 | 215.8 | 29.7 | 22.3 | 27.1 | 32.1 | 33.3 | 32.9 | 35
201 | 43 | 221.3 | 29.9 | 22.4 | 27.2 | 32.3 | 33.9 | 33.4 | 35.5
202 | 44 | 226.9 | 30.2 | 22.5 | 27.2 | 32.6 | 34.4 | 34 | 36
203 | 45 | 232.5 | 30.4 | 22.6 | 27.3 | 32.8 | 34.9 | 34.6 | 36.5
204 | 46 | 238.2 | 30.7 | 22.7 | 27.4 | 33.1 | 35.5 | 35.1 | 37.1
205 | 47 | 243.8 | 31 | 22.8 | 27.5 | 33.4 | 36.2 | 35.7 | 37.6
206 | 48 | 249.4 | 31.3 | 22.9 | 27.7 | 33.7 | 36.9 | 36.2 | 38.3
207 | 49 | 254.9 | 31.6 | 23.1 | 27.8 | 34 | 37.6 | 36.8 | 38.9
208 | 50 | 260.4 | 31.9 | 23.2 | 27.9 | 34.3 | 38.3 | 37.5 | 39.5
209 | 51 | 265.9 | 32.2 | 23.3 | 28 | 34.7 | 39 | 38.1 | 40.2
210 | 52 | 271.2 | 32.6 | 23.5 | 28.2 | 35 | 39.7 | 38.8 | 41
211 | 53 | 276.5 | 32.9 | 23.7 | 28.3 | 35.3 | 40.5 | 39.6 | 41.7
212 | 54 | 282 | 33.3 | 23.8 | 28.5 | 35.7 | 41.3 | 40.2 | 42.4
213 | 55 | 287.3 | 33.7 | 24 | 28.6 | 36.1 | 42.1 | 40.9 | 43.2
214 | 56 | 292.7 | 34 | 24.2 | 28.8 | 36.4 | 42.9 | 41.7 | 44
215 | 57 | 297.9 | 34.5 | 24.4 | 29 | 36.8 | 43.7 | 42.5 | 44.8
216 | 58 | 303.1 | 34.9 | 24.6 | 29.1 | 37.2 | 44.6 | 43.3 | 45.6
217 | 59 | 308.2 | 35.3 | 24.8 | 29.3 | 37.6 | 45.5 | 44.2 | 46.5
218 | 60 | 313.6 | 35.7 | 25 | 29.5 | 38 | 46.4 | 45.1 | 47.4
219 | 61 | 318.8 | 36.2 | 25.2 | 29.7 | 38.5 | 47.2 | 46.1 | 48.4
220 | 62 | 324 | 36.6 | 25.4 | 30 | 38.9 | 48.2 | 46.9 | 49.3
221 | 63 | 329.2 | 37.1 | 25.6 | 30.2 | 39.3 | 49.1 | 47.9 | 50.3
222 | 64 | 334.4 | 37.5 | 25.9 | 30.4 | 39.8 | 50.2 | 48.8 | 51.4
223 | 65 | 339.5 | 38 | 26.1 | 30.6 | 40.2 | 51.2 | 49.8 | 52.5
224 | 66 | 344.5 | 38.5 | 26.4 | 30.9 | 40.7 | 52.3 | 50.8 | 53.6
225 | 67 | 349.6 | 39 | 26.7 | 31.1 | 41.2 | 53.5 | 51.8 | 54.7
226 | 68 | 354.6 | 39.5 | 27 | 31.4 | 41.7 | 54.5 | 52.8 | 55.9
227 | 69 | 359.4 | 40 | 27.3 | 31.6 | 42.2 | 55.6 | 53.7 | 57
228 | 70 | 364.1 | 40.5 | 27.6 | 31.9 | 42.7 | 56.8 | 54.7 | 58.2
229 | 71 | 368.9 | 41.1 | 27.9 | 32.2 | 43.3 | 58 | 55.9 | 59.5
230 | 72 | 373.7 | 41.6 | 28.2 | 32.5 | 43.8 | 59.2 | 57 | 60.8
231 | 73 | 378.5 | 42.2 | 28.5 | 32.8 | 44.4 | 60.3 | 58.1 | 62.1
232 | 74 | 383.3 | 42.7 | 28.8 | 33.1 | 45 | 61.5 | 59.2 | 63.5
233 | 75 | 388.2 | 43.3 | 29.2 | 33.4 | 45.7 | 62.7 | 60.2 | 64.9
234 | 76 | 392.9 | 43.9 | 29.5 | 33.7 | 46.3 | 64 | 61.4 | 66.3
235 | 77 | 397.4 | 44.5 | 29.9 | 34.1 | 46.9 | 65.4 | 62.7 | 67.8
236 | 78 | 401.9 | 45.2 | 30.3 | 34.4 | 47.7 | 66.8 | 63.9 | 69.3
237 | 79 | 406.5 | 45.8 | 30.7 | 34.8 | 48.3 | 68.2 | 65.1 | 70.8
238 | 80 | 411.2 | 46.5 | 31.1 | 35.1 | 49 | 69.5 | 66.4 | 72.3
239 | 81 | 415.6 | 47.2 | 31.5 | 35.5 | 49.8 | 70.9 | 67.8 | 73.9
240 | 82 | 420.1 | 47.8 | 31.9 | 35.9 | 50.5 | 72.3 | 69.1 | 75.5
241 | 83 | 424.5 | 48.6 | 32.3 | 36.3 | 51.3 | 73.7 | 70.4 | 77.2
242 | 84 | 428.8 | 49.3 | 32.8 | 36.7 | 52 | 75.2 | 71.7 | 78.9
243 | 85 | 433.1 | 50 | 33.2 | 37.1 | 52.9 | 76.5 | 73.3 | 80.6
244 | 86 | 437.4 | 50.8 | 33.7 | 37.5 | 53.7 | 78 | 74.6 | 82.3
245 | 87 | 441.6 | 51.6 | 34.1 | 37.9 | 54.5 | 79.4 | 76 | 84.2
246 | 88 | 445.7 | 52.4 | 34.6 | 38.3 | 55.4 | 80.8 | 77.5 | 86
247 | 89 | 449.8 | 53.2 | 35.1 | 38.8 | 56.3 | 82.1 | 79 | 87.9
248 | 90 | 454 | 54 | 35.6 | 39.2 | 57.3 | 83.5 | 80.5 | 89.8
249 | 91 | 458.4 | 54.9 | 36.1 | 39.7 | 58.2 | 85 | 81.9 | 91.7
250 | 92 | 462.5 | 55.8 | 36.6 | 40.2 | 59.2 | 86.7 | 83.4 | 93.7
251 | 93 | 466.7 | 56.6 | 37.1 | 40.7 | 60.3 | 88.3 | 85.1 | 95.7
252 | 94 | 470.8 | 57.5 | 37.7 | 41.2 | 61.3 | 89.9 | 86.7 | 97.7
253 | 95 | 474.7 | 58.4 | 38.2 | 41.7 | 62.4 | 91.5 | 88.2 | 99.8
254 | 96 | 478.6 | 59.3 | 38.9 | 42.1 | 63.3 | 93.3 | 89.6 | 102
255 | 97 | 482.1 | 60.2 | 39.4 | 42.6 | 64.4 | 94.9 | 91.3 | 104.1
256 | 98 | 485.5 | 61.1 | 40 | 43.2 | 65.5 | 96.6 | 92.6 | 106.2
257 | 99 | 488.8 | 62.1 | 40.6 | 43.7 | 66.6 | 98.2 | 93.9 | 108.4
258 | 100 | 491.7 | 63 | 41.3 | 44.3 | 67.7 | 99.8 | 95.3 | 110.6
259 | 101 | 494.4 | 64 | 41.9 | 44.8 | 68.7 | 101.3 | 96.8 | 112.8
260 | 102 | 497 | 64.9 | 42.5 | 45.4 | 69.7 | 103 | 98.2 | 115
261 | 103 | 499.6 | 65.9 | 43.2 | 45.9 | 70.7 | 104.4 | 99.7 | 117.2
262 | 104 | 501.9 | 66.9 | 43.8 | 46.5 | 71.7 | 105.9 | 101.1 | 119.4
263 | 105 | 504.3 | 67.9 | 44.5 | 47.1 | 72.6 | 107.4 | 102.6 | 121.6
264 | 106 | 506.5 | 68.9 | 45.1 | 47.8 | 73.6 | 108.9 | 104.1 | 123.8
265 | 107 | 508.5 | 69.9 | 45.7 | 48.4 | 74.5 | 110.2 | 105.9 | 126
266 | 108 | 510.3 | 70.9 | 46.3 | 49 | 75.4 | 111.7 | 107.5 | 128.3
267 | 109 | 512.2 | 71.9 | 47 | 49.7 | 76.2 | 113.2 | 108.9 | 130.5
268 | 110 | 513.8 | 72.9 | 47.7 | 50.3 | 77 | 114.7 | 110.7 | 132.8
269 | 111 | 515.4 | 73.9 | 48.4 | 51 | 77.8 | 116.3 | 112.3 | 135
270 | 112 | 516.9 | 74.9 | 49.2 | 51.6 | 78.5 | 117.9 | 113.7 | 137.3
271 | 113 | 517.8 | 75.9 | 50 | 52.2 | 79.2 | 119.3 | 115 | 139.5
272 | 114 | 518.7 | 76.9 | 50.8 | 52.9 | 79.9 | 120.6 | 116.3 | 141.7
273 | 115 | 519.5 | 77.9 | 51.6 | 53.5 | 80.6 | 121.7 | 117.3 | 144
274 | 116 | 520 | 79 | 52.4 | 54.2 | 81.3 | 123 | 118.7 | 146.2
275 | 117 | 520.4 | 80 | 53.2 | 54.9 | 82.1 | 124.1 | 120 | 148.4
276 | 118 | 520.4 | 81.1 | 53.9 | 55.6 | 82.9 | 125.2 | 121.2 | 150.6
277 | 119 | 520.5 | 82.2 | 54.7 | 56.3 | 83.7 | 126.2 | 122.6 | 152.7
278 | 120 | 520.4 | 83.3 | 55.4 | 57 | 84.5 | 127.4 | 123.6 | 154.8
279 | 121 | 519.9 | 84.5 | 56.1 | 57.7 | 85.4 | 128.7 | 124.5 | 156.9
280 | 122 | 519.7 | 85.7 | 56.9 | 58.5 | 86.2 | 129.6 | 125.5 | 158.9
281 | 123 | 519.5 | 86.8 | 57.6 | 59.2 | 87 | 130.5 | 126.5 | 161
282 | 124 | 519 | 88.1 | 58.4 | 60 | 87.8 | 131.6 | 127.7 | 163
283 | 125 | 518.7 | 89.2 | 59.2 | 60.7 | 88.7 | 132.3 | 128.4 | 165
284 | 126 | 518.3 | 90.5 | 59.9 | 61.5 | 89.5 | 133.2 | 129 | 167
285 | 127 | 518.1 | 91.7 | 60.7 | 62.3 | 90.4 | 134 | 130 | 169
286 | 128 | 518.2 | 93 | 61.5 | 63.1 | 91.3 | 134.7 | 130.9 | 171
287 | 129 | 518 | 94.2 | 62.2 | 63.9 | 92.2 | 135.6 | 132 | 172.9
288 | 130 | 517.9 | 95.4 | 63 | 64.7 | 93 | 136.2 | 132.8 | 174.9
289 | 131 | 517.9 | 96.5 | 63.8 | 65.5 | 93.9 | 137.1 | 133.6 | 176.8
290 | 132 | 517.8 | 97.7 | 64.6 | 66.3 | 94.7 | 137.6 | 134.4 | 178.7
291 | 133 | 517.9 | 98.8 | 65.5 | 67.1 | 95.4 | 138.6 | 135.1 | 180.7
292 | 134 | 518 | 100 | 66.3 | 67.9 | 96.2 | 139.4 | 136.2 | 182.6
293 | 135 | 518 | 101.1 | 67.1 | 68.7 | 97 | 140.4 | 137 | 184.5
294 | 136 | 518.1 | 102.1 | 67.9 | 69.5 | 97.7 | 141.1 | 137.8 | 186.4
295 | 137 | 518.4 | 103.1 | 68.8 | 70.4 | 98.4 | 141.9 | 138.6 | 188.3
296 | 138 | 518.9 | 104.1 | 69.6 | 71.2 | 99.1 | 142.7 | 139.5 | 190.2
297 | 139 | 519.1 | 105.1 | 70.4 | 72 | 99.8 | 143.5 | 140.1 | 192.1
298 | 140 | 519.6 | 106.1 | 71.3 | 72.9 | 100.5 | 144.2 | 140.6 | 193.9
299 | 141 | 520 | 107 | 72.1 | 73.7 | 101.2 | 145.1 | 141.5 | 195.8
300 | 142 | 520.2 | 108 | 73 | 74.5 | 101.9 | 145.9 | 141.7 | 197.7
301 | 143 | 520.8 | 109 | 73.8 | 75.3 | 102.6 | 146.8 | 142 | 199.6
302 | 144 | 521 | 109.9 | 74.7 | 76.2 | 103.3 | 147.8 | 142.7 | 201.4
303 | 145 | 521.2 | 110.9 | 75.6 | 77 | 104.1 | 148.7 | 143.2 | 203
304 | 146 | 521.8 | 111.9 | 76.5 | 77.8 | 104.8 | 149.6 | 143.8 | 204.7
305 | 147 | 522 | 112.9 | 77.3 | 78.6 | 105.5 | 150.6 | 145 | 206.6
306 | 148 | 522.3 | 113.9 | 78.1 | 79.5 | 106.2 | 151.4 | 145.8 | 208.3
307 | 149 | 522.5 | 115 | 79 | 80.3 | 106.9 | 152 | 146.3 | 210.1
308 | 150 | 522.5 | 116.1 | 79.9 | 81.1 | 107.6 | 152.8 | 147 | 211.8
309 | 151 | 522.4 | 117.3 | 80.7 | 81.9 | 108.3 | 153.6 | 148.2 | 213.5
310 | 152 | 522.2 | 118.4 | 81.5 | 82.7 | 109 | 154.5 | 149.1 | 215.2
311 | 153 | 522.2 | 119.6 | 82.4 | 83.5 | 109.7 | 155.3 | 150 | 217
312 | 154 | 522.4 | 120.7 | 83.2 | 84.4 | 110.4 | 156 | 150.8 | 218.7
313 | 155 | 522.4 | 121.8 | 84 | 85.2 | 111.1 | 156.7 | 151.5 | 220.4
314 | 156 | 522.4 | 122.8 | 84.9 | 85.9 | 111.8 | 157.8 | 152 | 222.1
315 | 157 | 522.3 | 123.6 | 85.8 | 86.7 | 112.6 | 158.6 | 152.4 | 223.7
316 | 158 | 522.3 | 125 | 86.7 | 87.5 | 113.4 | 159.5 | 153.1 | 225.4
317 | 159 | 522.2 | 127.8 | 87.6 | 88.3 | 114.5 | 160.3 | 153.6 | 227
318 | 160 | 522.3 | 131.6 | 88.5 | 89.1 | 115.8 | 161.3 | 154.1 | 228.6
319 | 161 | 522.3 | 135.8 | 89.4 | 89.9 | 117.4 | 162.2 | 154.7 | 230.2
320 | 162 | 522.2 | 139.9 | 90.3 | 90.7 | 119.4 | 163.2 | 155.4 | 231.7
321 | 163 | 522.1 | 143.7 | 91.3 | 91.6 | 121.6 | 164 | 156.1 | 233.2
322 | 164 | 521.7 | 147.1 | 92.3 | 92.5 | 123.9 | 164.9 | 156.8 | 234.7
323 | 165 | 521.5 | 150.3 | 93.2 | 93.4 | 126.3 | 165.6 | 157.7 | 236.3
324 | 166 | 521.6 | 153.2 | 94.3 | 94.3 | 128.7 | 166.3 | 158.2 | 237.8
325 | 167 | 521.6 | 156.2 | 95.3 | 95.3 | 131.2 | 167.2 | 158.4 | 239.4
326 | 168 | 521.5 | 158.9 | 96.4 | 96.3 | 133.7 | 168 | 159 | 240.9
327 | 169 | 521.4 | 161.5 | 97.4 | 97.3 | 136 | 168.9 | 159.8 | 242.4
328 | 170 | 521.3 | 163.9 | 98.4 | 98.3 | 138 | 169.9 | 160.8 | 243.8
329 | 171 | 521.4 | 166.2 | 99.4 | 99.3 | 140 | 170.9 | 161.4 | 245.3
330 | 172 | 521.5 | 168.5 | 100.4 | 100.3 | 142.2 | 171.7 | 162.2 | 246.7
331 | 173 | 521.6 | 170.7 | 101.5 | 101.3 | 144.5 | 172.5 | 162.9 | 248.1
332 | 174 | 521.7 | 172.8 | 102.5 | 102.3 | 146.8 | 173.6 | 163.7 | 249.6
333 | 175 | 521.8 | 174.9 | 103.6 | 103.2 | 148.8 | 174.6 | 164.5 | 251
334 | 176 | 521.8 | 176.9 | 104.7 | 104.2 | 150.7 | 175.5 | 165.3 | 252.4
335 | 177 | 521.7 | 178.7 | 105.7 | 105.3 | 152.4 | 176.5 | 166.2 | 253.7
336 | 178 | 521.8 | 180.2 | 106.8 | 106.3 | 154 | 177.4 | 166.2 | 255.1
337 | 179 | 522.1 | 181.8 | 107.9 | 107.3 | 155.5 | 178.3 | 167.1 | 256.5
338 | 180 | 522.2 | 183.4 | 108.9 | 108.3 | 157.2 | 179.1 | 168.1 | 257.8
339 | 181 | 522.1 | 185 | 110.1 | 109.3 | 158.3 | 179.9 | 168.3 | 259.2
340 | 182 | 521.9 | 186.5 | 111.2 | 110.4 | 159.4 | 180.9 | 169.1 | 260.6
341 | 183 | 521.9 | 188.2 | 112.3 | 111.5 | 160.9 | 181.9 | 169.3 | 261.9
342 | 184 | 522 | 189.8 | 113.5 | 112.6 | 162.4 | 182.8 | 169.7 | 263.3
343 | 185 | 522.1 | 191.2 | 114.6 | 113.8 | 164.1 | 183.6 | 170.5 | 264.6
344 | 186 | 521.9 | 192.6 | 115.8 | 114.9 | 165.7 | 184.4 | 171.2 | 265.9
345 | 187 | 521.7 | 194 | 116.9 | 116.1 | 166.6 | 185.1 | 171.8 | 267.2
346 | 188 | 521.6 | 195.2 | 118.1 | 117.3 | 167.5 | 185.9 | 172.9 | 268.5
347 | 189 | 521.5 | 196.5 | 119.3 | 118.4 | 169.1 | 186.7 | 173.9 | 269.7
348 | 190 | 521.3 | 197.7 | 120.5 | 119.6 | 170.6 | 187.7 | 174.7 | 270.9
349 | 191 | 521.2 | 198.8 | 121.7 | 120.8 | 172 | 188.5 | 176.2 | 272.2
350 | 192 | 521.1 | 200 | 122.9 | 122 | 173.3 | 189.2 | 177.4 | 273.3
351 | 193 | 521 | 201.2 | 124.1 | 123.2 | 174.9 | 189.9 | 178.3 | 274.5
352 | 194 | 521 | 202.4 | 125.2 | 124.4 | 176.3 | 190.7 | 179.3 | 275.7
353 | 195 | 521.1 | 203.5 | 126.4 | 125.6 | 177.5 | 191.6 | 180.1 | 276.8
354 | 196 | 521.3 | 204.6 | 127.6 | 126.8 | 179 | 192.4 | 181 | 277.9
355 | 197 | 520.9 | 205.6 | 128.8 | 128 | 180.3 | 193.1 | 181.8 | 279
356 | 198 | 520.5 | 206.6 | 130 | 129.2 | 181.7 | 193.9 | 182.9 | 280.2
357 | 199 | 520.3 | 207.6 | 131.2 | 130.4 | 182.7 | 194.8 | 183.8 | 281.3
358 | 200 | 520.5 | 208.5 | 132.4 | 131.6 | 183.9 | 195.7 | 184.7 | 282.4
359 | 201 | 520.5 | 210 | 132.2 | 133.3 | 187.2 | 196.7 | 185.7 | 283.4
360 | 202 | 520.4 | 210.8 | 133.2 | 134.5 | 188.4 | 197.5 | 186.6 | 284.4
361 | 203 | 520.5 | 211.7 | 134.4 | 135.7 | 189.6 | 198.4 | 187.3 | 285.5
362 | 204 | 520.4 | 213 | 135.5 | 136.9 | 190.9 | 199.4 | 188.1 | 286.6
363 | 205 | 520.6 | 214.2 | 136.7 | 138 | 192 | 200.3 | 188.7 | 287.6
364 | 206 | 520.8 | 215.3 | 137.8 | 139.2 | 193.2 | 201.3 | 189.3 | 288.7
365 | 207 | 520.9 | 216.4 | 139 | 140.4 | 194.4 | 202.2 | 190 | 289.7
366 | 208 | 520.9 | 217.4 | 140.1 | 141.5 | 195.5 | 203.2 | 190.5 | 290.7
367 | 209 | 520.8 | 218.6 | 141.2 | 142.7 | 196.6 | 204 | 191.1 | 291.7
368 | 210 | 520.9 | 219.8 | 142.4 | 143.8 | 197.9 | 204.9 | 191.5 | 292.7
369 | 211 | 521 | 220.8 | 143.5 | 145 | 199.3 | 205.6 | 191.9 | 293.7
370 | 212 | 520.9 | 222 | 144.6 | 146.1 | 200.6 | 206.4 | 192.4 | 294.7
371 | 213 | 520.7 | 222.9 | 145.7 | 147.2 | 201.9 | 207.2 | 192.9 | 295.7
372 | 214 | 520.8 | 223.9 | 146.8 | 148.3 | 203 | 207.8 | 193.1 | 296.6
373 | 215 | 520.9 | 224.7 | 147.9 | 149.5 | 204.2 | 208.4 | 193.6 | 297.6
374 | 216 | 521 | 225.8 | 149 | 150.6 | 205.3 | 209.1 | 194 | 298.4
375 | 217 | 521 | 226.7 | 150.1 | 151.6 | 206.1 | 209.6 | 194.3 | 299.4
376 | 218 | 520.9 | 227.5 | 151.2 | 152.7 | 207.3 | 210.3 | 194.7 | 300.2
377 | 219 | 520.8 | 228.3 | 152.3 | 153.7 | 208.2 | 211 | 194.9 | 301.2
378 | 220 | 520.6 | 229.2 | 153.4 | 154.8 | 209.5 | 211.7 | 195.2 | 302.1
379 | 221 | 520.7 | 229.9 | 154.5 | 155.9 | 210.3 | 212.5 | 195.4 | 303
380 | 222 | 520.5 | 230.7 | 155.6 | 156.9 | 211 | 213.2 | 195.6 | 303.9
381 | 223 | 520.3 | 231.8 | 156.7 | 158 | 212.2 | 214 | 195.9 | 304.8
382 | 224 | 520.2 | 232.9 | 157.7 | 159.1 | 213.1 | 214.6 | 196.2 | 305.7
383 | 225 | 520.4 | 234 | 158.8 | 160.1 | 214.3 | 215.2 | 196.4 | 306.6
384 | 226 | 520.4 | 235.1 | 159.9 | 161.2 | 215.3 | 215.8 | 196.7 | 307.5
385 | 227 | 520.2 | 236 | 161 | 162.3 | 216.2 | 216.5 | 197 | 308.3
386 | 228 | 520.1 | 237.2 | 162 | 163.3 | 217.2 | 217.1 | 197.3 | 309.2
387 | 229 | 520.1 | 238.5 | 163.1 | 164.4 | 218.1 | 217.7 | 197.6 | 310
388 | 230 | 520.1 | 239.9 | 164.1 | 165.4 | 219 | 218.4 | 197.7 | 310.8
389 | 231 | 519.8 | 241.1 | 165.2 | 166.4 | 220.2 | 219.2 | 198 | 311.6
390 | 232 | 519.6 | 241.9 | 166.2 | 167.5 | 221 | 220 | 198.3 | 312.4
391 | 233 | 519.6 | 242.5 | 167.2 | 168.5 | 222.1 | 220.8 | 198.6 | 313.2
392 | 234 | 519.5 | 243.5 | 168.3 | 169.5 | 223.1 | 221.5 | 198.8 | 314.1
393 | 235 | 519.4 | 244.4 | 169.3 | 170.6 | 223.9 | 222.3 | 199.2 | 314.9
394 | 236 | 519.5 | 245.1 | 170.3 | 171.6 | 225.1 | 223 | 199.4 | 315.6
395 | 237 | 519.5 | 245.6 | 171.3 | 172.6 | 226 | 223.6 | 199.7 | 316.4
396 | 238 | 519.3 | 246.4 | 172.4 | 173.6 | 226.8 | 224.2 | 200 | 317.1
397 | 239 | 519.2 | 247.4 | 173.4 | 174.6 | 227.8 | 224.8 | 200.3 | 317.9
398 | 240 | 519.1 | 248.4 | 174.4 | 175.6 | 228.6 | 225.5 | 200.6 | 318.6
399 | 241 | 519.1 | 249.1 | 175.4 | 176.6 | 229.4 | 226.2 | 201 | 319.4
400 | 242 | 519 | 250.5 | 176.4 | 177.6 | 230.2 | 226.9 | 201.4 | 320.2
401 | 243 | 519.2 | 251.6 | 177.4 | 178.6 | 230.7 | 227.4 | 201.7 | 320.8
402 | 244 | 519.3 | 252.7 | 178.4 | 179.6 | 231.6 | 228 | 202 | 321.5
403 | 245 | 519.3 | 253.8 | 179.4 | 180.6 | 232.4 | 228.5 | 202.3 | 322.2
404 | 246 | 519.4 | 255 | 180.3 | 181.6 | 233.4 | 229.1 | 202.5 | 322.8
405 | 247 | 519.4 | 255.9 | 181.3 | 182.5 | 234.5 | 229.6 | 202.6 | 323.5
406 | 248 | 519.3 | 256.8 | 182.4 | 183.5 | 235.2 | 230.1 | 202.8 | 324.3
407 | 249 | 519.3 | 257.7 | 183.4 | 184.4 | 235.9 | 230.7 | 203 | 325
408 | 250 | 519.2 | 258.6 | 184.3 | 185.4 | 237 | 231.3 | 203.1 | 325.6
409 | 251 | 519.4 | 259.4 | 185.3 | 186.4 | 237.9 | 231.9 | 203.4 | 326.3
410 | 252 | 519.6 | 260.1 | 186.2 | 187.3 | 239 | 232.5 | 203.6 | 326.9
411 | 253 | 519.7 | 260.7 | 187.2 | 188.3 | 239.8 | 233.2 | 203.8 | 327.6
412 | 254 | 519.8 | 261.6 | 188.2 | 189.2 | 240.8 | 233.8 | 204 | 328.3
413 | 255 | 519.9 | 262.5 | 189.2 | 190.2 | 242.1 | 234.5 | 204.2 | 329
414 | 256 | 519.8 | 263.7 | 190.1 | 191.1 | 242.9 | 235.1 | 204.4 | 329.6
415 | 257 | 519.8 | 264.9 | 191 | 192 | 243.5 | 235.6 | 204.6 | 330.3
416 | 258 | 519.9 | 265.9 | 191.9 | 193 | 244.4 | 236.2 | 204.9 | 330.9
417 | 259 | 520.1 | 266.8 | 192.9 | 193.9 | 245.2 | 236.7 | 205.2 | 331.5
418 | 260 | 520.3 | 267.6 | 193.8 | 194.8 | 246.2 | 237.3 | 205.4 | 332.1
419 | 261 | 520.4 | 268.6 | 194.8 | 195.7 | 247 | 237.8 | 205.6 | 332.8
420 | 262 | 520.6 | 269.4 | 195.7 | 196.6 | 247.8 | 238.4 | 205.8 | 333.5
421 | 263 | 520.8 | 270.3 | 196.6 | 197.5 | 248.6 | 239 | 206.1 | 334.1
422 | 264 | 520.8 | 271.3 | 197.5 | 198.4 | 249.1 | 239.5 | 206.4 | 334.7
423 | 265 | 520.9 | 272.3 | 198.4 | 199.4 | 249.9 | 239.9 | 206.6 | 335.4
424 | 266 | 520.9 | 273.3 | 199.4 | 200.2 | 250.4 | 240.1 | 206.9 | 336
425 | 267 | 520.9 | 274.3 | 200.3 | 201.1 | 250.9 | 240.5 | 207.2 | 336.6
426 | 268 | 520.8 | 275 | 201.2 | 202 | 250.9 | 241 | 207.5 | 337.3
427 | 269 | 520.9 | 275.9 | 202.1 | 202.9 | 250.9 | 241.5 | 207.7 | 337.9
428 | 270 | 520.8 | 276.7 | 203 | 203.7 | 251.6 | 242.1 | 208 | 338.5
429 | 271 | 520.8 | 277.6 | 203.8 | 204.6 | 252.9 | 242.7 | 208.3 | 339.1
430 | 272 | 520.7 | 278.3 | 204.7 | 205.5 | 253.2 | 243.3 | 208.6 | 339.7
431 | 273 | 520.6 | 279.3 | 205.6 | 206.3 | 253.3 | 243.8 | 208.8 | 340.2
432 | 274 | 520.7 | 280.1 | 206.5 | 207.2 | 254 | 244.3 | 209.1 | 340.7
433 | 275 | 520.6 | 280.7 | 207.3 | 208 | 255.3 | 244.8 | 209.3 | 341.3
434 | 276 | 520.6 | 280.7 | 208.2 | 208.9 | 256.4 | 245.5 | 209.5 | 341.8
435 | 277 | 520.7 | 281.3 | 209 | 209.7 | 257.5 | 246.2 | 209.8 | 342.3
436 | 278 | 520.8 | 282.3 | 209.8 | 210.6 | 258.4 | 246.6 | 210 | 342.9
437 | 279 | 520.9 | 283 | 210.7 | 211.4 | 259.6 | 247.1 | 210.3 | 343.5
438 | 280 | 520.9 | 283.8 | 211.6 | 212.2 | 260.6 | 247.5 | 210.6 | 344
439 | 281 | 520.8 | 284.5 | 212.4 | 213.1 | 261.4 | 248 | 210.9 | 344.5
440 | 282 | 520.8 | 285.3 | 213.2 | 213.9 | 262 | 248.6 | 211.2 | 345
441 | 283 | 520.6 | 285.9 | 214 | 214.7 | 262.9 | 249.1 | 211.5 | 345.5
442 | 284 | 520.5 | 286.6 | 214.8 | 215.5 | 263.6 | 249.6 | 211.8 | 346
443 | 285 | 520.4 | 287.3 | 215.6 | 216.4 | 264.4 | 249.9 | 212.1 | 346.5
444 | 286 | 520.2 | 288.2 | 216.4 | 217.2 | 265.6 | 250.3 | 212.4 | 347
445 | 287 | 520.2 | 288.7 | 217.2 | 218 | 266.5 | 250.8 | 212.7 | 347.5
446 | 288 | 520.1 | 289 | 217.9 | 218.8 | 267.1 | 251.3 | 212.9 | 348
447 | 289 | 520 | 289.4 | 218.8 | 219.6 | 267.3 | 251.8 | 213.1 | 348.4
448 | 290 | 519.9 | 290 | 219.5 | 220.4 | 267.9 | 252.4 | 213.3 | 348.9
449 | 291 | 519.8 | 290.3 | 220.3 | 221.2 | 268.7 | 253 | 213.6 | 349.4
450 | 292 | 519.6 | 290.7 | 221 | 222 | 269.9 | 253.5 | 213.9 | 349.9
451 | 293 | 519.5 | 291 | 221.8 | 222.8 | 271.1 | 253.9 | 214.3 | 350.4
452 | 294 | 519.5 | 291.6 | 222.6 | 223.6 | 272.2 | 254.4 | 214.6 | 350.9
453 | 295 | 519.6 | 292.3 | 223.4 | 224.4 | 273.2 | 254.8 | 214.9 | 351.4
454 | 296 | 519.4 | 292.8 | 224.1 | 225.2 | 273.4 | 255.2 | 215.2 | 351.8
455 | 297 | 519.2 | 293.2 | 224.9 | 226 | 274.1 | 255.7 | 215.6 | 352.2
456 | 298 | 519 | 293.9 | 225.7 | 226.8 | 274.4 | 256.1 | 215.9 | 352.7
457 | 299 | 518.9 | 294.8 | 226.4 | 227.6 | 274.5 | 256.6 | 216.3 | 353.2
458 | 300 | 519 | 295.6 | 227.1 | 228.4 | 275.2 | 257.1 | 216.5 | 353.6
459 | 301 | 518.9 | 296.3 | 227.9 | 229.2 | 276.1 | 257.6 | 216.8 | 354
460 | 302 | 518.8 | 297 | 228.6 | 230 | 277 | 258.2 | 217.1 | 354.5
461 | 303 | 518.7 | 297.7 | 229.3 | 230.8 | 277.7 | 258.7 | 217.5 | 354.9
462 | 304 | 518.8 | 298.4 | 230 | 231.5 | 277.7 | 259.3 | 217.8 | 355.4
463 | 305 | 518.8 | 299.1 | 230.8 | 232.3 | 277.3 | 259.8 | 218.2 | 355.8
464 | 306 | 518.8 | 300.1 | 231.5 | 233.1 | 277.8 | 260.4 | 218.5 | 356.1
465 | 307 | 518.8 | 300.8 | 232.2 | 233.9 | 278.8 | 260.8 | 218.7 | 356.5
466 | 308 | 518.9 | 301.2 | 232.9 | 234.6 | 279.8 | 261.2 | 218.9 | 356.9
467 | 309 | 519.1 | 301.4 | 233.6 | 235.4 | 280.8 | 261.7 | 219.2 | 357.4
468 | 310 | 519.3 | 301.9 | 234.3 | 236.1 | 281.5 | 262.1 | 219.4 | 357.7
469 | 311 | 519.4 | 302.5 | 235 | 236.9 | 282.3 | 262.5 | 219.5 | 358.1
470 | 312 | 519.4 | 303.1 | 235.7 | 237.6 | 282.8 | 262.9 | 219.7 | 358.5
471 | 313 | 519.5 | 303.8 | 236.5 | 238.3 | 283.6 | 263.3 | 220 | 358.9
472 | 314 | 519.6 | 304.2 | 237.2 | 239.1 | 284.3 | 263.8 | 220.2 | 359.3
473 | 315 | 519.7 | 304.9 | 237.9 | 239.8 | 284.9 | 264.2 | 220.4 | 359.6
474 | 316 | 519.9 | 305.5 | 238.6 | 240.5 | 285.6 | 264.6 | 220.6 | 360
475 | 317 | 519.8 | 306.1 | 239.3 | 241.3 | 286.3 | 265 | 220.9 | 360.4
476 | 318 | 519.9 | 306.7 | 239.9 | 242 | 287 | 265.4 | 221.1 | 360.8
477 | 319 | 519.8 | 307.2 | 240.6 | 242.7 | 287.7 | 265.8 | 221.4 | 361.2
478 | 320 | 519.7 | 307.9 | 241.2 | 243.5 | 287.8 | 266.2 | 221.6 | 361.5
479 | 321 | 519.4 | 308.7 | 241.8 | 244.2 | 288.8 | 266.6 | 221.9 | 361.9
480 | 322 | 519.2 | 309.4 | 242.5 | 244.9 | 289.6 | 267.1 | 222.1 | 362.3
481 | 323 | 519.1 | 309.8 | 243.2 | 245.6 | 290.3 | 267.5 | 222.4 | 362.7
482 | 324 | 519 | 310.5 | 243.8 | 246.3 | 291 | 267.8 | 222.6 | 363
483 | 325 | 519 | 311.3 | 244.5 | 247 | 291.8 | 268.2 | 222.8 | 363.4
484 | 326 | 518.9 | 311.9 | 245.2 | 247.6 | 292.5 | 268.5 | 223 | 363.7
485 | 327 | 519.1 | 312.6 | 245.9 | 248.3 | 293 | 268.8 | 223.3 | 364
486 | 328 | 519.2 | 313.1 | 246.6 | 249 | 293.3 | 269.2 | 223.5 | 364.4
487 | 329 | 519.4 | 313.8 | 247.2 | 249.7 | 293.6 | 269.4 | 223.8 | 364.8
488 | 330 | 519.5 | 314.4 | 247.9 | 250.3 | 294.3 | 269.7 | 224.1 | 365.1
489 | 331 | 519.4 | 314.8 | 248.6 | 251 | 294.9 | 270 | 224.4 | 365.4
490 | 332 | 519.4 | 315.2 | 249.3 | 251.7 | 295.7 | 270.3 | 224.6 | 365.7
491 | 333 | 519.3 | 315.5 | 249.9 | 252.3 | 296.6 | 270.7 | 224.9 | 366.1
492 | 334 | 519.5 | 316 | 250.6 | 253 | 297.5 | 271 | 225.1 | 366.4
493 | 335 | 519.7 | 316.3 | 251.3 | 253.6 | 298 | 271.4 | 225.4 | 366.7
494 | 336 | 519.6 | 317 | 252 | 254.3 | 298.5 | 271.8 | 225.7 | 367
495 | 337 | 519.5 | 317.7 | 252.5 | 254.9 | 299.2 | 272.2 | 226 | 367.3
496 | 338 | 519.5 | 318.2 | 253.2 | 255.6 | 300.1 | 272.5 | 226.3 | 367.6
497 | 339 | 519.4 | 318.5 | 253.9 | 256.2 | 301 | 273 | 226.6 | 367.9
498 | 340 | 519.2 | 318.9 | 254.5 | 256.9 | 301.8 | 273.3 | 226.8 | 368.3
499 | 341 | 519.2 | 319.3 | 255.1 | 257.5 | 302.4 | 273.6 | 227.1 | 368.6
500 | 342 | 519.4 | 319.8 | 255.7 | 258.2 | 303.1 | 274 | 227.4 | 368.9
501 | 343 | 519.5 | 320 | 256.4 | 258.8 | 303.9 | 274.4 | 227.6 | 369.2
502 | 344 | 519.4 | 320.1 | 257 | 259.5 | 304.3 | 274.8 | 227.8 | 369.5
503 | 345 | 519.3 | 320.1 | 257.6 | 260.1 | 304.7 | 275.3 | 228.1 | 369.8
504 | 346 | 519.2 | 320.3 | 258.2 | 260.8 | 305.3 | 275.7 | 228.3 | 370.1
505 | 347 | 519 | 320.4 | 258.9 | 261.4 | 305.7 | 276 | 228.6 | 370.4
506 | 348 | 519.1 | 320.5 | 259.5 | 262 | 306.6 | 276.3 | 228.8 | 370.7
507 | 349 | 519.4 | 320.5 | 260.2 | 262.7 | 307.3 | 276.6 | 229 | 371
508 | 350 | 519.5 | 320.7 | 260.8 | 263.3 | 307.3 | 277 | 229.3 | 371.3
509 | 351 | 519.6 | 320.8 | 261.4 | 263.9 | 307.8 | 277.3 | 229.6 | 371.6
510 | 352 | 519.7 | 320.9 | 262 | 264.6 | 308.1 | 277.6 | 229.9 | 371.8
511 | 353 | 519.8 | 321.3 | 262.7 | 265.2 | 308.6 | 277.8 | 230.2 | 372.1
512 | 354 | 519.9 | 321.7 | 263.3 | 265.9 | 309.1 | 278 | 230.5 | 372.4
513 | 355 | 520.1 | 322.1 | 264 | 266.5 | 310 | 278.3 | 230.7 | 372.8
514 | 356 | 520.2 | 322.6 | 264.6 | 267.1 | 310.6 | 278.5 | 231 | 373.1
515 | 357 | 520.5 | 323.2 | 265.3 | 267.8 | 311.2 | 278.8 | 231.2 | 373.4
516 | 358 | 520.6 | 323.8 | 265.9 | 268.4 | 312 | 279 | 231.4 | 373.7
517 | 359 | 520.8 | 324.4 | 266.5 | 269.1 | 312.8 | 279.2 | 231.5 | 374
518 | 360 | 520.9 | 325.1 | 267.2 | 269.7 | 313.6 | 279.6 | 231.6 | 374.3
519 | 361 | 521 | 325.8 | 267.9 | 270.3 | 313.9 | 280 | 231.8 | 374.5
520 | 362 | 521 | 326.2 | 268.5 | 271 | 314.5 | 280.3 | 232 | 374.8
521 | 363 | 521 | 326.5 | 269.1 | 271.6 | 314.8 | 280.7 | 232.1 | 375.1
522 | 364 | 520.9 | 327.2 | 269.8 | 272.2 | 314.9 | 281 | 232.3 | 375.4
523 | 365 | 520.8 | 327.8 | 270.4 | 272.8 | 315.3 | 281.4 | 232.5 | 375.7
524 | 366 | 520.7 | 328.4 | 271 | 273.4 | 316 | 281.8 | 232.8 | 376
525 | 367 | 520.7 | 329 | 271.6 | 273.9 | 316.1 | 282.2 | 233 | 376.3
526 | 368 | 520.7 | 329.4 | 272.3 | 274.5 | 316.3 | 282.5 | 233.2 | 376.6
527 | 369 | 520.7 | 329.9 | 272.9 | 275.1 | 316.4 | 282.8 | 233.4 | 376.8
528 | 370 | 520.5 | 330.6 | 273.5 | 275.7 | 316.7 | 283.1 | 233.7 | 377
529 | 371 | 520.5 | 331.3 | 274.1 | 276.3 | 316.6 | 283.5 | 233.9 | 377.2
530 | 372 | 520.5 | 331.8 | 274.8 | 276.9 | 316.6 | 283.8 | 234.1 | 377.4
531 | 373 | 520.5 | 332.2 | 275.3 | 277.5 | 317.2 | 284.2 | 234.3 | 377.6
532 | 374 | 520.4 | 332.8 | 275.5 | 278.2 | 318.3 | 284.6 | 234.5 | 377.7
533 | 375 | 520.3 | 333.2 | 276.6 | 278.6 | 318.9 | 284.9 | 234.7 | 377.9
534 | 376 | 520.1 | 333.8 | 277.1 | 279.2 | 320.1 | 285.2 | 234.9 | 378.1
535 | 377 | 520.1 | 334.4 | 277.7 | 279.8 | 321 | 285.6 | 235.2 | 378.3
536 | 378 | 520.2 | 335 | 278.4 | 280.3 | 321.2 | 285.9 | 235.4 | 378.5
537 | 379 | 520 | 335.5 | 279 | 280.9 | 321.6 | 286.2 | 235.6 | 378.7
538 | 380 | 519.9 | 336 | 279.7 | 281.5 | 322 | 286.5 | 235.8 | 378.9
539 | 381 | 519.8 | 336.6 | 280.3 | 282.1 | 322.5 | 286.8 | 236.1 | 379
540 | 382 | 519.8 | 337.3 | 280.9 | 282.7 | 323.1 | 287.2 | 236.3 | 379.2
541 | 383 | 519.7 | 337.9 | 281.3 | 283.3 | 323.8 | 287.5 | 236.6 | 379.4
542 | 384 | 519.4 | 338.4 | 281.6 | 284 | 324.6 | 287.9 | 236.9 | 379.6
543 | 385 | 519.2 | 338.7 | 282.6 | 284.5 | 325 | 288.2 | 237.1 | 379.7
544 | 386 | 519.2 | 339.5 | 282.9 | 285.2 | 325.9 | 288.6 | 237.4 | 379.9
545 | 387 | 519.4 | 339.9 | 283.6 | 285.7 | 326.2 | 289 | 237.6 | 380.1
546 | 388 | 519.4 | 340.1 | 284.5 | 286.2 | 326.3 | 289.5 | 237.8 | 380.3
547 | 389 | 519.7 | 340.8 | 284.8 | 286.9 | 326.9 | 289.9 | 237.9 | 380.5
548 | 390 | 519.7 | 341 | 285.6 | 287.4 | 326.7 | 290.2 | 238 | 380.7
549 | 391 | 519.6 | 341.4 | 286.2 | 288 | 326.8 | 290.6 | 238.1 | 380.9
550 | 392 | 519.8 | 341.7 | 286.8 | 288.6 | 326.9 | 291.1 | 238.3 | 381.1
551 | 393 | 520 | 342.1 | 287.3 | 289.1 | 327.2 | 291.4 | 238.5 | 381.3
552 | 394 | 520.1 | 342.6 | 287.9 | 289.7 | 327.3 | 291.7 | 238.7 | 381.5
553 | 395 | 520.3 | 343 | 288.5 | 290.3 | 326.3 | 291.9 | 238.9 | 381.7
554 | 396 | 520.4 | 343.5 | 289 | 290.8 | 325.7 | 292.2 | 239.1 | 381.9
555 | 397 | 520.4 | 344.4 | 289.7 | 291.4 | 325.8 | 292.6 | 239.3 | 382.1
556 | 398 | 520.4 | 344.9 | 290.2 | 292 | 325.9 | 292.9 | 239.5 | 382.3
557 | 399 | 520.6 | 345.2 | 290.8 | 292.5 | 326.4 | 293.2 | 239.7 | 382.5
558 | 400 | 520.5 | 345.6 | 291.3 | 293.1 | 327.8 | 293.6 | 239.9 | 382.6
559 | 401 | 520.4 | 346 | 291.9 | 293.7 | 328.9 | 294 | 240.2 | 382.8
560 | 402 | 520.5 | 346.6 | 292.6 | 294.2 | 330.2 | 294.3 | 240.4 | 382.9
561 | 403 | 520.5 | 346.8 | 293.2 | 294.7 | 331 | 294.7 | 240.6 | 383.1
562 | 404 | 520.4 | 347.2 | 293.9 | 295.3 | 331.9 | 295.2 | 240.8 | 383.3
563 | 405 | 520.2 | 347.5 | 294.5 | 295.8 | 332.4 | 295.7 | 241 | 383.5
564 | 406 | 519.9 | 348.6 | 295.1 | 296.4 | 332.8 | 296.1 | 241.3 | 383.7
565 | 407 | 519.6 | 349.1 | 295.6 | 296.9 | 332.4 | 296.5 | 241.5 | 383.9
566 | 408 | 519.5 | 349.3 | 296.2 | 297.4 | 331.6 | 297 | 241.7 | 384
567 | 409 | 519.4 | 349.6 | 296.7 | 298 | 331.1 | 297.5 | 241.9 | 384.2
568 | 410 | 519.6 | 349.9 | 297.2 | 298.5 | 331 | 297.9 | 242.1 | 384.4
569 | 411 | 519.8 | 350.1 | 297.9 | 299 | 331.5 | 298.3 | 242.2 | 384.5
570 | 412 | 519.9 | 350.4 | 298.5 | 299.5 | 331.9 | 298.7 | 242.4 | 384.7
571 | 413 | 519.9 | 350.8 | 299.1 | 300 | 333 | 299.2 | 242.6 | 384.9
572 | 414 | 519.7 | 351.3 | 299.7 | 300.5 | 334 | 299.5 | 242.8 | 385
573 | 415 | 519.8 | 351.9 | 300.2 | 301.1 | 334.4 | 300 | 243 | 385.1
574 | 416 | 519.6 | 352.3 | 300.7 | 301.6 | 335.3 | 300.5 | 243.3 | 385.3
575 | 417 | 519.5 | 352.7 | 301.3 | 302.1 | 336.1 | 301 | 243.5 | 385.4
576 | 418 | 519.5 | 353.7 | 301.9 | 302.6 | 337.1 | 301.5 | 243.7 | 385.6
577 | 419 | 519.6 | 354.1 | 302.5 | 303.1 | 338 | 302 | 243.9 | 385.7
578 | 420 | 519.5 | 354.3 | 303.1 | 303.6 | 338.7 | 302.5 | 244 | 385.9
579 | 421 | 519.6 | 354.6 | 303.7 | 304.1 | 339 | 302.9 | 244.1 | 386.1
580 | 422 | 519.5 | 355.1 | 304.2 | 304.6 | 339.3 | 303.4 | 244.3 | 386.3
581 | 423 | 519.6 | 355.6 | 304.8 | 305.1 | 339.6 | 303.9 | 244.4 | 386.4
582 | 424 | 519.8 | 355.9 | 305.3 | 305.7 | 340.3 | 304.4 | 244.5 | 386.5
583 | 425 | 519.7 | 356.6 | 305.8 | 306.2 | 340.6 | 304.8 | 244.6 | 386.7
584 | 426 | 519.7 | 356.8 | 306.4 | 306.7 | 340.9 | 305.2 | 244.8 | 386.9
585 | 427 | 519.7 | 357.1 | 307 | 307.2 | 341.7 | 305.6 | 244.9 | 387
586 | 428 | 519.8 | 357.5 | 307.5 | 307.7 | 342.6 | 305.9 | 245.1 | 387.2
587 | 429 | 519.6 | 358 | 308.1 | 308.2 | 343.1 | 306.3 | 245.3 | 387.3
588 | 430 | 519.4 | 358.2 | 308.6 | 308.7 | 343.5 | 306.7 | 245.6 | 387.6
589 | 431 | 519.6 | 358.5 | 309.1 | 309.2 | 344.4 | 307.2 | 245.8 | 387.8
590 | 432 | 519.7 | 359.2 | 309.6 | 309.8 | 345.3 | 307.6 | 246 | 387.9
591 | 433 | 519.7 | 359.8 | 310.2 | 310.3 | 346.1 | 308 | 246.2 | 388.1
592 | 434 | 519.8 | 360.1 | 310.8 | 310.8 | 346.2 | 308.4 | 246.4 | 388.3
593 | 435 | 520 | 360.4 | 311.3 | 311.3 | 346.1 | 308.9 | 246.6 | 388.5
594 | 436 | 520.2 | 360.7 | 311.8 | 311.8 | 346.8 | 309.3 | 246.8 | 388.6
595 | 437 | 520.3 | 361 | 312.4 | 312.3 | 347.8 | 309.8 | 247 | 388.8
596 | 438 | 520.2 | 361.3 | 312.9 | 312.8 | 348.6 | 310.2 | 247.3 | 388.9
597 | 439 | 520.3 | 361.7 | 313.4 | 313.4 | 349.1 | 310.6 | 247.5 | 389.1
598 | 440 | 520.4 | 362.1 | 314 | 313.8 | 349.5 | 311 | 247.7 | 389.2
599 | 441 | 520.6 | 362.7 | 314.5 | 314.3 | 350.3 | 311.5 | 247.9 | 389.4
600 | 442 | 520.7 | 363.1 | 315 | 314.8 | 350.6 | 311.9 | 248.1 | 389.5
601 | 443 | 520.8 | 363.5 | 315.6 | 315.3 | 350.8 | 312.4 | 248.2 | 389.6
602 | 444 | 520.8 | 363.8 | 316.1 | 315.8 | 351.1 | 312.8 | 248.3 | 389.8
603 | 445 | 521 | 364.4 | 316.6 | 316.3 | 351.4 | 313.2 | 248.5 | 389.9
604 | 446 | 521.1 | 365.1 | 317.2 | 316.9 | 352.2 | 313.7 | 248.6 | 390
605 | 447 | 521.2 | 365.4 | 317.7 | 317.4 | 352.5 | 314.2 | 248.7 | 390.2
606 | 448 | 521.3 | 365.7 | 318.2 | 317.9 | 352.8 | 314.7 | 248.9 | 390.4
607 | 449 | 521.4 | 366.1 | 318.7 | 318.4 | 353.5 | 315.2 | 249 | 390.6
608 | 450 | 521.5 | 366.4 | 319.2 | 318.9 | 354 | 315.6 | 249.2 | 390.7
609 | 451 | 521.5 | 366.9 | 319.7 | 319.5 | 354.3 | 316.1 | 249.4 | 390.8
610 | 452 | 521.5 | 367 | 320.1 | 320 | 354.7 | 316.5 | 249.7 | 391
611 | 453 | 521.6 | 367.2 | 320.6 | 320.5 | 355.2 | 316.9 | 250 | 391.1
612 | 454 | 521.5 | 367.4 | 321.1 | 321 | 355.2 | 317.3 | 250.3 | 391.3
613 | 455 | 521.4 | 367.6 | 321.6 | 321.5 | 355.6 | 317.6 | 250.6 | 391.4
614 | 456 | 521.3 | 368.1 | 322.1 | 322 | 356.3 | 318 | 250.8 | 391.6
615 | 457 | 521.4 | 368.5 | 322.6 | 322.6 | 356.8 | 318.4 | 251 | 391.8
616 | 458 | 521.5 | 368.6 | 323.1 | 323.1 | 356.9 | 318.7 | 251.2 | 392
617 | 459 | 521.3 | 368.9 | 323.5 | 323.6 | 357.1 | 319.1 | 251.4 | 392.1
618 | 460 | 521.1 | 369.2 | 324 | 324.1 | 357.3 | 319.5 | 251.7 | 392.2
619 | 461 | 520.8 | 369.4 | 324.5 | 324.6 | 357.5 | 319.9 | 251.9 | 392.4
620 | 462 | 520.7 | 369.6 | 325.1 | 325.1 | 358 | 320.2 | 252.1 | 392.6
621 | 463 | 520.6 | 370 | 325.5 | 325.6 | 358.7 | 320.6 | 252.3 | 392.7
622 | 464 | 520.6 | 370.5 | 325.9 | 326.1 | 359.4 | 320.9 | 252.5 | 392.9
623 | 465 | 520.6 | 370.7 | 326.4 | 326.6 | 359.6 | 321.3 | 252.7 | 393
624 | 466 | 520.5 | 370.9 | 326.9 | 327.1 | 359.9 | 321.7 | 252.8 | 393.1
625 | 467 | 520.4 | 371.2 | 327.4 | 327.6 | 360.1 | 322.1 | 253 | 393.2
626 | 468 | 520.1 | 371.7 | 327.8 | 328.1 | 360.7 | 322.6 | 253.2 | 393.3
627 | 469 | 520 | 372.2 | 328.3 | 328.6 | 360.8 | 323.1 | 253.4 | 393.4
628 | 470 | 520 | 372.6 | 328.7 | 329.1 | 361 | 323.5 | 253.6 | 393.5
629 | 471 | 520 | 373.2 | 329.3 | 329.6 | 361.6 | 323.8 | 253.8 | 393.6
630 | 472 | 520.1 | 373.7 | 329.8 | 330.1 | 362.3 | 324.2 | 254 | 393.7
631 | 473 | 520.3 | 374.2 | 330.3 | 330.6 | 362.3 | 324.6 | 254.3 | 393.9
632 | 474 | 520.4 | 374.8 | 330.8 | 331 | 362.3 | 325 | 254.5 | 394
633 | 475 | 520.3 | 375.4 | 331.2 | 331.5 | 362.8 | 325.3 | 254.7 | 394.1
634 | 476 | 520.3 | 376.1 | 331.7 | 332 | 363.1 | 325.7 | 254.9 | 394.2
635 | 477 | 520.2 | 376.8 | 332.1 | 332.5 | 364 | 326 | 255.1 | 394.3
636 | 478 | 520 | 377.5 | 332.5 | 333 | 364.4 | 326.3 | 255.3 | 394.4
637 | 479 | 520 | 378.1 | 333 | 333.5 | 364.7 | 326.7 | 255.5 | 394.6
638 | 480 | 520.1 | 378.8 | 333.5 | 334 | 364.2 | 327 | 255.7 | 394.8
639 | 481 | 520.1 | 379.4 | 334 | 334.4 | 362.8 | 327.3 | 255.9 | 394.9
640 | 482 | 520.2 | 379.9 | 334.5 | 334.9 | 361.8 | 327.5 | 256.1 | 395.1
641 | 483 | 520.1 | 380.5 | 334.9 | 335.4 | 362.1 | 327.8 | 256.3 | 395.2
642 | 484 | 520.1 | 381 | 335.3 | 335.8 | 362.7 | 328.1 | 256.5 | 395.3
643 | 485 | 520.1 | 381.6 | 335.8 | 336.3 | 363.5 | 328.4 | 256.7 | 395.4
644 | 486 | 520.1 | 382.3 | 336.2 | 336.7 | 364.2 | 328.7 | 256.9 | 395.5
645 | 487 | 520 | 382.9 | 336.6 | 337.2 | 364.4 | 329 | 257.1 | 395.7
646 | 488 | 520 | 383.5 | 337 | 337.6 | 364 | 329.3 | 257.3 | 395.7
647 | 489 | 520 | 384 | 337.5 | 338.1 | 364 | 329.6 | 257.5 | 395.8
648 | 490 | 520 | 384.6 | 337.9 | 338.5 | 364 | 329.9 | 257.7 | 395.9
649 | 491 | 520 | 385.1 | 338.3 | 339 | 363.1 | 330.1 | 257.9 | 396
650 | 492 | 520.1 | 385.7 | 338.7 | 339.4 | 362.4 | 330.4 | 258.1 | 396.2
651 | 493 | 520.2 | 386.2 | 339.2 | 339.8 | 362.1 | 330.7 | 258.3 | 396.3
652 | 494 | 520.2 | 386.8 | 339.6 | 340.3 | 362.4 | 331 | 258.5 | 396.4
653 | 495 | 520.2 | 387.6 | 340.1 | 340.7 | 362.8 | 331.3 | 258.7 | 396.5
654 | 496 | 520.3 | 388.3 | 340.5 | 341.1 | 362.7 | 331.6 | 258.9 | 396.6
655 | 497 | 520.3 | 388.9 | 341 | 341.6 | 362.7 | 331.9 | 259.1 | 396.7
656 | 498 | 520.3 | 389.5 | 341.3 | 342 | 363.3 | 332.2 | 259.3 | 396.7
657 | 499 | 520.3 | 390.2 | 341.7 | 342.4 | 364.4 | 332.6 | 259.4 | 396.9
658 | 500 | 520.6 | 390.8 | 342.2 | 342.8 | 365 | 332.9 | 259.6 | 396.9
659 | 501 | 520.9 | 391.4 | 342.6 | 343.2 | 366.1 | 333.2 | 259.8 | 397
660 | 502 | 520.9 | 392.3 | 343 | 343.6 | 366.5 | 333.6 | 259.9 | 397.1
661 | 503 | 521 | 393.2 | 343.4 | 344 | 366.1 | 333.9 | 260.1 | 397.2
662 | 504 | 521.1 | 394 | 343.9 | 344.3 | 366.9 | 334.2 | 260.2 | 397.3
663 | 505 | 521.1 | 394.7 | 344.3 | 344.8 | 366.8 | 334.6 | 260.4 | 397.4
664 | 506 | 521 | 395.5 | 344.7 | 345.1 | 367.8 | 334.9 | 260.5 | 397.5
665 | 507 | 521 | 396.3 | 345.2 | 345.5 | 368.5 | 335.3 | 260.6 | 397.6
666 | 508 | 521.1 | 397.3 | 345.7 | 345.9 | 369.2 | 335.6 | 260.8 | 397.8
667 | 509 | 521.3 | 398.2 | 346.2 | 346.2 | 369.5 | 335.9 | 260.9 | 397.9
668 | 510 | 521.5 | 399.1 | 346.7 | 346.6 | 369.3 | 336.2 | 261.1 | 398
669 | 511 | 521.7 | 400 | 347.2 | 347 | 369.4 | 336.5 | 261.2 | 398.1
670 | 512 | 521.7 | 401 | 347.6 | 347.4 | 370 | 336.8 | 261.4 | 398.2
671 | 513 | 521.5 | 402 | 348 | 347.8 | 369.4 | 337.2 | 261.6 | 398.3
672 | 514 | 521.5 | 403 | 348.4 | 348.1 | 367.9 | 337.5 | 261.8 | 398.4
673 | 515 | 521.3 | 404 | 348.8 | 348.5 | 367.2 | 337.8 | 262 | 398.5
674 | 516 | 521.2 | 405 | 349.2 | 348.9 | 367.1 | 338.1 | 262.3 | 398.6
675 | 517 | 521 | 406 | 349.7 | 349.2 | 368.3 | 338.4 | 262.5 | 398.7
676 | 518 | 520.7 | 407 | 350.1 | 349.6 | 369.4 | 338.7 | 262.7 | 398.8
677 | 519 | 520.7 | 407.9 | 350.4 | 349.9 | 370.5 | 338.9 | 262.9 | 398.8
678 | 520 | 520.6 | 408.8 | 350.8 | 350.3 | 371.7 | 339.2 | 263.1 | 398.9
679 | 521 | 520.6 | 409.7 | 351.3 | 350.7 | 372.7 | 339.5 | 263.3 | 398.9
680 | 522 | 520.5 | 410.6 | 351.7 | 351 | 373 | 339.7 | 263.5 | 399
681 | 523 | 520.4 | 411.5 | 352 | 351.4 | 373.5 | 340 | 263.6 | 399
682 | 524 | 520.3 | 412.4 | 352.5 | 351.7 | 374.6 | 340.3 | 263.8 | 399.1
683 | 525 | 520.4 | 413.2 | 352.9 | 352.1 | 375.5 | 340.6 | 264 | 399.1
684 | 526 | 520.3 | 414.1 | 353.3 | 352.5 | 376 | 340.9 | 264.1 | 399.2
685 | 527 | 520.1 | 415 | 353.8 | 352.8 | 376.2 | 341.2 | 264.3 | 399.3
686 | 528 | 520 | 416 | 354.2 | 353.1 | 376.8 | 341.5 | 264.4 | 399.3
687 | 529 | 520.1 | 416.9 | 354.5 | 353.5 | 377.2 | 341.8 | 264.5 | 399.4
688 | 530 | 520 | 418 | 354.9 | 353.8 | 377.5 | 342 | 264.7 | 399.5
689 | 531 | 520 | 419.1 | 355.3 | 354.2 | 377.4 | 342.3 | 264.8 | 399.5
690 | 532 | 519.9 | 420.1 | 355.7 | 354.5 | 377.4 | 342.7 | 264.9 | 399.6
691 | 533 | 519.7 | 421.1 | 356.1 | 354.8 | 377.3 | 343 | 265.1 | 399.7
692 | 534 | 519.9 | 422.1 | 356.5 | 355.2 | 377.9 | 343.4 | 265.3 | 399.8
693 | 535 | 520 | 422.9 | 356.9 | 355.5 | 377.9 | 343.7 | 265.4 | 399.8
694 | 536 | 520.2 | 423.8 | 357.3 | 355.9 | 378.3 | 343.9 | 265.5 | 399.9
695 | 537 | 520.3 | 424.7 | 357.7 | 356.2 | 379.1 | 344.2 | 265.7 | 400
696 | 538 | 520.2 | 425.6 | 358.1 | 356.6 | 379.1 | 344.4 | 265.8 | 400.1
697 | 539 | 520.2 | 426.5 | 358.6 | 356.9 | 378.8 | 344.7 | 265.9 | 400.1
698 | 540 | 520 | 427.4 | 358.9 | 357.3 | 379.1 | 344.9 | 266 | 400.2
699 | 541 | 519.9 | 428.2 | 359.3 | 357.6 | 379.6 | 345.2 | 266.1 | 400.2
700 | 542 | 520 | 429.2 | 359.7 | 357.9 | 380.3 | 345.5 | 266.2 | 400.3
701 | 543 | 519.9 | 430.1 | 360.1 | 358.3 | 380.7 | 345.8 | 266.3 | 400.3
702 | 544 | 520 | 431.3 | 360.4 | 358.6 | 382 | 346.1 | 266.5 | 400.4
703 | 545 | 520.2 | 432.3 | 360.8 | 358.9 | 382.9 | 346.4 | 266.6 | 400.4
704 | 546 | 520.1 | 433.4 | 361.2 | 359.2 | 382.3 | 346.6 | 266.7 | 400.4
705 | 547 | 519.9 | 434.6 | 361.6 | 359.6 | 381.4 | 346.9 | 266.9 | 400.5
706 | 548 | 520 | 435.7 | 361.9 | 359.9 | 381.1 | 347.2 | 267 | 400.6
707 | 549 | 520 | 436.9 | 362.4 | 360.2 | 381.5 | 347.4 | 267.2 | 400.6
708 | 550 | 519.8 | 438 | 362.8 | 360.6 | 382.9 | 347.7 | 267.3 | 400.6
709 | 551 | 519.7 | 439.2 | 363.3 | 360.9 | 384.1 | 348.1 | 267.5 | 400.7
710 | 552 | 519.8 | 440.3 | 363.7 | 361.2 | 384.8 | 348.3 | 267.6 | 400.8
711 | 553 | 519.8 | 441.4 | 364.2 | 361.5 | 385.3 | 348.6 | 267.8 | 400.8
712 | 554 | 520 | 442.6 | 364.6 | 361.9 | 386 | 348.8 | 267.9 | 400.9
713 | 555 | 520.2 | 443.8 | 365 | 362.2 | 386.4 | 349.1 | 268 | 401
714 | 556 | 520.2 | 444.9 | 365.5 | 362.5 | 386.8 | 349.4 | 268.1 | 401.1
715 | 557 | 520.3 | 445.9 | 366 | 362.8 | 387.9 | 349.6 | 268.3 | 401.2
716 | 558 | 520.4 | 446.9 | 366.4 | 363.1 | 389.3 | 349.9 | 268.4 | 401.2
717 | 559 | 520.7 | 448 | 366.9 | 363.5 | 390.2 | 350.1 | 268.5 | 401.3
718 | 560 | 521 | 449.1 | 367.4 | 363.8 | 391.1 | 350.4 | 268.6 | 401.4
719 | 561 | 521.4 | 450.2 | 367.9 | 364.1 | 392.2 | 350.6 | 268.8 | 401.4
720 | 562 | 521.6 | 451.2 | 368.4 | 364.4 | 393.2 | 350.9 | 268.9 | 401.5
721 | 563 | 521.6 | 452.2 | 369 | 364.8 | 393.4 | 351.1 | 269 | 401.6
722 | 564 | 521.7 | 453.1 | 369.5 | 365.1 | 393.5 | 351.4 | 269.2 | 401.7
723 | 565 | 521.8 | 453.8 | 370 | 365.4 | 393.8 | 351.7 | 269.4 | 401.7
724 | 566 | 521.9 | 454.5 | 370.6 | 365.8 | 394.7 | 351.9 | 269.6 | 401.8
725 | 567 | 522 | 455.1 | 371.2 | 366.1 | 395.1 | 352.2 | 269.7 | 401.8
726 | 568 | 522.1 | 455.6 | 371.8 | 366.5 | 395.9 | 352.4 | 269.9 | 401.8
727 | 569 | 522.3 | 456 | 372.4 | 366.8 | 396.1 | 352.7 | 270.1 | 401.9
728 | 570 | 522.2 | 456.5 | 373 | 367.2 | 396.2 | 352.9 | 270.2 | 401.9
729 | 571 | 522.2 | 457 | 373.6 | 367.5 | 396.5 | 353.2 | 270.4 | 402
730 | 572 | 522.4 | 457.4 | 374.2 | 367.9 | 396.6 | 353.5 | 270.5 | 402
731 | 573 | 522.5 | 457.7 | 374.8 | 368.2 | 396.9 | 353.8 | 270.7 | 402
732 | 574 | 522.5 | 458.1 | 375.5 | 368.5 | 397.5 | 354.2 | 270.9 | 402
733 | 575 | 522.4 | 458.6 | 376.1 | 368.9 | 398.3 | 354.5 | 271 | 402
734 | 576 | 522.4 | 459.1 | 376.8 | 369.2 | 398.9 | 354.8 | 271.2 | 401.9
735 | 577 | 522.3 | 459.5 | 377.6 | 369.5 | 399.1 | 355 | 271.4 | 401.9
736 | 578 | 522.3 | 459.8 | 378.4 | 369.9 | 399.5 | 355.2 | 271.5 | 401.9
737 | 579 | 522.3 | 460.1 | 379.2 | 370.3 | 400.2 | 355.5 | 271.6 | 401.9
738 | 580 | 522.1 | 460.4 | 380.1 | 370.6 | 400.7 | 355.7 | 271.8 | 401.8
739 | 581 | 522.2 | 460.7 | 380.9 | 370.9 | 401.1 | 356 | 272 | 401.8
740 | 582 | 522.3 | 460.9 | 381.8 | 371.2 | 401.8 | 356.2 | 272.1 | 401.9
741 | 583 | 522.3 | 461.2 | 382.6 | 371.5 | 402.8 | 356.4 | 272.2 | 401.9
742 | 584 | 522.2 | 461.2 | 383.5 | 371.8 | 404 | 356.7 | 272.4 | 401.9
743 | 585 | 522.2 | 461 | 384.4 | 372.1 | 404.9 | 356.9 | 272.5 | 402
744 | 586 | 522.1 | 460.5 | 385.3 | 372.4 | 405.6 | 357.2 | 272.7 | 402
745 | 587 | 522.1 | 459.9 | 386.3 | 372.6 | 406.6 | 357.5 | 272.8 | 402
746 | 588 | 522 | 459.1 | 387.2 | 372.9 | 407.7 | 357.7 | 272.9 | 402
747 | 589 | 521.8 | 458.2 | 388.2 | 373.3 | 408.5 | 358 | 273.1 | 402
748 | 590 | 521.4 | 457.2 | 389.1 | 373.6 | 409.4 | 358.2 | 273.2 | 402
749 | 591 | 521.3 | 456.1 | 390.1 | 373.8 | 410.2 | 358.4 | 273.3 | 402
750 | 592 | 521.2 | 454.9 | 391.2 | 374.1 | 410.7 | 358.6 | 273.4 | 402
751 | 593 | 521.1 | 453.8 | 392.1 | 374.4 | 411.5 | 358.8 | 273.5 | 402
752 | 594 | 521 | 452.5 | 393.1 | 374.7 | 412.5 | 358.9 | 273.6 | 402
753 | 595 | 520.8 | 451.1 | 394.1 | 375 | 413.5 | 359.1 | 273.8 | 402
754 | 596 | 520.7 | 449.7 | 395 | 375.3 | 414.5 | 359.3 | 273.9 | 402.1
755 | 597 | 520.8 | 448.3 | 395.9 | 375.5 | 415.3 | 359.5 | 274 | 402.1
756 | 598 | 520.8 | 446.8 | 396.9 | 375.7 | 415.8 | 359.8 | 274.2 | 402.1
757 | 599 | 521 | 444.8 | 397.8 | 376 | 416.4 | 360 | 274.3 | 402.1
758 | 600 | 521.3 | 443.1 | 398.7 | 376.3 | 416.7 | 360.2 | 274.5 | 402.1
759 | 601 | 521.4 | 441.9 | 399.6 | 376.6 | 417 | 360.3 | 274.7 | 402.2
760 | 602 | 521.6 | 440.9 | 400.6 | 376.9 | 417.5 | 360.5 | 274.9 | 402.1
761 | 603 | 521.8 | 440.1 | 401.5 | 377.2 | 418.3 | 360.6 | 275 | 402.2
762 | 604 | 521.9 | 439.6 | 402.3 | 377.5 | 419.3 | 360.7 | 275.1 | 402.2
763 | 605 | 521.9 | 439.2 | 403 | 377.8 | 420.5 | 360.9 | 275.3 | 402.2
764 | 606 | 522 | 438.8 | 403.7 | 378.1 | 421.5 | 361 | 275.4 | 402.3
765 | 607 | 522.1 | 438.7 | 404.7 | 378.4 | 422.4 | 361.1 | 275.5 | 402.4
766 | 608 | 522.2 | 438.6 | 405.6 | 378.7 | 423.3 | 361.2 | 275.7 | 402.4
767 | 609 | 522.2 | 438.6 | 406.3 | 379.1 | 424.1 | 361.4 | 275.8 | 402.5
768 | 610 | 522.2 | 438.7 | 406.9 | 379.4 | 424.9 | 361.5 | 276 | 402.5
769 | 611 | 522.2 | 438.9 | 407.7 | 379.7 | 425.4 | 361.7 | 276.1 | 402.5
770 | 612 | 522.4 | 439.2 | 408.4 | 380 | 425.8 | 361.8 | 276.3 | 402.5
771 | 613 | 522.4 | 439.5 | 409.3 | 380.3 | 426.2 | 361.9 | 276.5 | 402.4
772 | 614 | 522.3 | 439.8 | 410.2 | 380.7 | 426.5 | 361.9 | 276.7 | 402.5
773 | 615 | 522.2 | 440.3 | 410.9 | 381 | 426.9 | 361.9 | 276.9 | 402.5
774 | 616 | 522.2 | 440.8 | 411.7 | 381.3 | 427.9 | 362.1 | 277 | 402.5
775 | 617 | 522.1 | 441.4 | 412.4 | 381.8 | 429.4 | 362.2 | 277.2 | 402.4
776 | 618 | 522.2 | 442 | 413.2 | 382.2 | 430.4 | 362.4 | 277.4 | 402.4
777 | 619 | 522.3 | 442.6 | 413.9 | 382.6 | 431.2 | 362.6 | 277.6 | 402.4
778 | 620 | 522.2 | 443.2 | 414.7 | 383 | 431.8 | 362.7 | 277.8 | 402.5
779 | 621 | 522.1 | 443.8 | 415.4 | 383.5 | 432.5 | 362.9 | 278 | 402.4
780 | 622 | 522 | 444.5 | 416.2 | 383.9 | 433.3 | 363 | 278.2 | 402.4
781 | 623 | 521.8 | 445.3 | 416.9 | 384.4 | 434.1 | 363.2 | 278.4 | 402.4
782 | 624 | 521.8 | 446 | 417.6 | 384.9 | 435.1 | 363.3 | 278.6 | 402.3
783 | 625 | 521.9 | 446.7 | 418.1 | 385.3 | 436.3 | 363.5 | 278.9 | 402.3
784 | 626 | 521.9 | 447.3 | 418.8 | 385.8 | 437.4 | 363.6 | 279.1 | 402.3
785 | 627 | 522 | 447.8 | 419.3 | 386.3 | 438.6 | 363.8 | 279.3 | 402.3
786 | 628 | 522 | 448.4 | 419.9 | 386.8 | 439.9 | 364 | 279.5 | 402.3
787 | 629 | 521.9 | 449.2 | 420.4 | 387.3 | 441 | 364.2 | 279.7 | 402.2
788 | 630 | 522 | 450.1 | 420.9 | 387.8 | 442.4 | 364.4 | 279.8 | 402.2
789 | 631 | 522 | 451 | 421.3 | 388.4 | 443.7 | 364.6 | 280 | 402.2
790 | 632 | 522.1 | 452 | 421.8 | 389 | 444.6 | 364.7 | 280.2 | 402.1
791 | 633 | 522.2 | 452.8 | 422.3 | 389.5 | 445.3 | 364.9 | 280.4 | 402.2
792 | 634 | 522.1 | 453.7 | 422.7 | 390.1 | 446.1 | 365 | 280.6 | 402.2
793 | 635 | 522.1 | 454.4 | 423.1 | 390.7 | 447 | 365.2 | 280.8 | 402.2
794 | 636 | 522.1 | 455.2 | 423.5 | 391.3 | 448.1 | 365.4 | 281 | 402.2
795 | 637 | 522.1 | 455.9 | 424 | 391.9 | 449 | 365.6 | 281.1 | 402.1
796 | 638 | 522.1 | 456.6 | 424.4 | 392.5 | 449.8 | 365.8 | 281.3 | 402.1
797 | 639 | 522.1 | 457.3 | 424.9 | 393.1 | 450.9 | 366 | 281.5 | 402.1
798 | 640 | 521.9 | 457.8 | 425.3 | 393.7 | 451.8 | 366.1 | 281.6 | 402.2
799 | 641 | 521.8 | 458.2 | 425.7 | 394.3 | 452.5 | 366.3 | 281.8 | 402.1
800 | 642 | 521.9 | 458.7 | 426.1 | 394.9 | 453.1 | 366.5 | 282 | 402.1
801 | 643 | 521.8 | 459.2 | 426.5 | 395.5 | 453.8 | 366.6 | 282.2 | 402.1
802 | 644 | 521.8 | 459.8 | 426.8 | 396.1 | 454.2 | 366.8 | 282.3 | 402.1
803 | 645 | 521.7 | 460.4 | 427.1 | 396.8 | 454.5 | 366.9 | 282.5 | 402.1
804 | 646 | 521.6 | 459.9 | 427.4 | 397.4 | 454.8 | 367 | 282.7 | 402.1
805 | 647 | 521.5 | 458.1 | 427.6 | 398 | 455.5 | 367.1 | 282.9 | 402.1
806 | 648 | 521.3 | 457.5 | 427.8 | 398.6 | 456 | 367.2 | 283 | 402.2
807 | 649 | 521.3 | 457.8 | 428.1 | 399.2 | 456.6 | 367.4 | 283.2 | 402.2
808 | 650 | 521.4 | 458.4 | 428.4 | 399.8 | 456.9 | 367.5 | 283.3 | 402.2
809 | 651 | 521.4 | 459.3 | 428.6 | 400.5 | 456.8 | 367.6 | 283.5 | 402.2
810 | 652 | 521.5 | 461.1 | 428.7 | 401.1 | 457 | 367.6 | 283.7 | 402.3
811 | 653 | 521.5 | 463.2 | 428.9 | 401.7 | 457.4 | 367.6 | 283.9 | 402.3
812 | 654 | 521.8 | 465 | 429.1 | 402.3 | 457.5 | 367.7 | 284.1 | 402.4
813 | 655 | 521.9 | 466.4 | 429.4 | 403 | 457.6 | 367.8 | 284.3 | 402.4
814 | 656 | 522.1 | 467.5 | 429.5 | 403.6 | 457.9 | 368 | 284.5 | 402.4
815 | 657 | 522.4 | 468.5 | 429.8 | 404.2 | 457.9 | 368.1 | 284.7 | 402.4
816 | 658 | 522.5 | 469.3 | 430 | 404.8 | 457.6 | 368.2 | 284.9 | 402.4
817 | 659 | 522.6 | 469.7 | 430.3 | 405.4 | 457.4 | 368.3 | 285.1 | 402.5
818 | 660 | 522.4 | 469.9 | 430.6 | 406 | 457.3 | 368.4 | 285.3 | 402.5
819 | 661 | 522.3 | 470 | 431 | 406.6 | 457.2 | 368.6 | 285.5 | 402.5
820 | 662 | 522.2 | 469.8 | 431.3 | 407.3 | 457.4 | 368.7 | 285.7 | 402.5
821 | 663 | 522.3 | 469.3 | 431.6 | 407.9 | 457.3 | 368.9 | 285.9 | 402.5
822 | 664 | 522.4 | 468.8 | 432 | 408.5 | 457 | 369 | 286.1 | 402.5
823 | 665 | 522.6 | 468 | 432.3 | 409.1 | 456.8 | 369.2 | 286.3 | 402.6
824 | 666 | 523 | 467.1 | 432.6 | 409.7 | 456.9 | 369.3 | 286.6 | 402.6
825 | 667 | 523.2 | 465.9 | 432.8 | 410.3 | 456.8 | 369.4 | 286.8 | 402.5
826 | 668 | 523.3 | 464.9 | 433.1 | 410.9 | 456.4 | 369.5 | 287 | 402.5
827 | 669 | 523.5 | 464.1 | 433.4 | 411.6 | 456 | 369.6 | 287.3 | 402.5
828 | 670 | 523.6 | 463.5 | 433.6 | 412.2 | 455.7 | 369.7 | 287.5 | 402.5
829 | 671 | 523.8 | 463 | 433.8 | 412.8 | 455.4 | 369.8 | 287.8 | 402.6
830 | 672 | 523.9 | 462.6 | 434.1 | 413.4 | 455.2 | 369.9 | 288 | 402.6
831 | 673 | 523.8 | 462.5 | 434.4 | 414 | 455 | 370 | 288.3 | 402.7
832 | 674 | 523.9 | 462.4 | 434.6 | 414.6 | 454.6 | 370.2 | 288.6 | 402.7
833 | 675 | 523.9 | 462.4 | 435 | 415.2 | 454.7 | 370.3 | 288.8 | 402.7
834 | 676 | 523.7 | 462.6 | 435.4 | 415.8 | 454.6 | 370.3 | 289 | 402.7
835 | 677 | 523.5 | 462.8 | 435.8 | 416.4 | 454.6 | 370.3 | 289.3 | 402.7
836 | 678 | 523.4 | 463.1 | 436.3 | 417 | 454.7 | 370.4 | 289.5 | 402.7
837 | 679 | 523.4 | 463.4 | 436.8 | 417.6 | 454.6 | 370.7 | 289.8 | 402.8
838 | 680 | 523.2 | 463.7 | 437.2 | 418.2 | 454.8 | 370.8 | 290 | 402.8
839 | 681 | 523 | 464.1 | 437.6 | 418.9 | 454.9 | 371 | 290.2 | 402.8
840 | 682 | 522.8 | 464.4 | 438.1 | 419.5 | 455 | 371.2 | 290.4 | 402.8
841 | 683 | 522.7 | 464.7 | 438.5 | 420.1 | 455.2 | 371.4 | 290.6 | 402.8
842 | 684 | 522.6 | 464.8 | 438.9 | 420.7 | 455.1 | 371.6 | 290.8 | 402.7
843 | 685 | 522.6 | 465 | 439.4 | 421.4 | 455 | 371.8 | 291 | 402.7
844 | 686 | 522.6 | 465.2 | 439.8 | 422 | 454.9 | 372 | 291.1 | 402.7
845 | 687 | 522.7 | 465.4 | 440.2 | 422.6 | 454.9 | 372.2 | 291.3 | 402.7
846 | 688 | 522.8 | 465.7 | 440.6 | 423.3 | 454.6 | 372.3 | 291.5 | 402.7
847 | 689 | 522.9 | 466.1 | 441.1 | 423.9 | 454.4 | 372.4 | 291.7 | 402.7
848 | 690 | 522.6 | 466.6 | 441.4 | 424.6 | 454.3 | 372.5 | 291.9 | 402.6
849 | 691 | 522.4 | 467 | 441.8 | 425.3 | 454.2 | 372.7 | 292.1 | 402.6
850 | 692 | 522.1 | 467.4 | 442.1 | 426 | 454 | 372.9 | 292.3 | 402.6
851 | 693 | 521.9 | 467.5 | 442.5 | 426.7 | 453.7 | 373 | 292.5 | 402.6
852 | 694 | 521.7 | 467.7 | 442.7 | 427.5 | 453.3 | 373.3 | 292.7 | 402.6
853 | 695 | 521.7 | 467.9 | 443 | 428.3 | 452.5 | 373.4 | 292.9 | 402.5
854 | 696 | 521.7 | 468 | 443.3 | 429.2 | 452.1 | 373.5 | 293.1 | 402.5
855 | 697 | 521.8 | 468.1 | 443.6 | 430.1 | 451.7 | 373.6 | 293.4 | 402.6
856 | 698 | 521.9 | 468.4 | 443.8 | 431 | 451.5 | 373.8 | 293.6 | 402.5
857 | 699 | 521.9 | 468.9 | 444 | 432.1 | 451.1 | 374 | 293.8 | 402.5
858 | 700 | 521.7 | 469.4 | 444.3 | 433.8 | 450.8 | 374.1 | 294 | 402.5
859 | 701 | 521.5 | 470 | 444.5 | 436.4 | 450.9 | 374.3 | 294.2 | 402.5
860 | 702 | 521.4 | 470.7 | 444.7 | 439.4 | 450.8 | 374.4 | 294.4 | 402.5
861 | 703 | 521.5 | 471.5 | 444.8 | 442.5 | 450.8 | 374.6 | 294.6 | 402.3
862 | 704 | 521.5 | 472.2 | 444.8 | 445.6 | 450.9 | 374.8 | 294.8 | 402.3
863 | 705 | 521.6 | 472.9 | 444.7 | 448.7 | 451 | 375 | 295 | 402.2
864 | 706 | 521.7 | 473.6 | 444.7 | 451.9 | 451 | 375.1 | 295.2 | 402.1
865 | 707 | 521.8 | 474.2 | 444.8 | 455.1 | 450.8 | 375.2 | 295.4 | 402.1
866 | 708 | 521.7 | 474.8 | 444.9 | 458.5 | 451.3 | 375.4 | 295.6 | 402.1
867 | 709 | 521.7 | 475.3 | 445.1 | 461.9 | 451.9 | 375.5 | 295.8 | 402.2
868 | 710 | 521.7 | 475.8 | 445.5 | 465.4 | 452.4 | 375.6 | 296 | 402.2
869 | 711 | 521.8 | 476.1 | 445.9 | 468.8 | 453 | 375.7 | 296.2 | 402.1
870 | 712 | 521.7 | 476.5 | 446.3 | 472.1 | 453.5 | 375.8 | 296.4 | 402.1
871 | 713 | 521.8 | 476.7 | 446.8 | 475.1 | 453.8 | 376 | 296.6 | 402.2
872 | 714 | 521.7 | 477 | 447.3 | 477.5 | 454.3 | 376.1 | 296.7 | 402.2
873 | 715 | 521.9 | 477.5 | 447.7 | 479.7 | 454.8 | 376.2 | 296.9 | 402.2
874 | 716 | 522.1 | 478.1 | 448.1 | 482 | 455.3 | 376.4 | 297 | 402.2
875 | 717 | 522.3 | 478.6 | 448.6 | 483.7 | 455.8 | 376.6 | 297.1 | 402.2
876 | 718 | 522.5 | 479 | 449.2 | 485.4 | 456.1 | 376.8 | 297.3 | 402.2
877 | 719 | 522.6 | 479.5 | 449.8 | 487.1 | 456.2 | 377 | 297.5 | 402.2
878 | 720 | 522.6 | 480.2 | 450.5 | 488.1 | 456.1 | 377.1 | 297.6 | 402.1
879 | 721 | 522.8 | 480.7 | 451.3 | 488.8 | 455.9 | 377.3 | 297.8 | 402
880 | 722 | 523.2 | 481.1 | 452.1 | 489.3 | 455.9 | 377.5 | 298 | 402.1
881 | 723 | 523.5 | 481.4 | 452.8 | 489.9 | 455.7 | 377.6 | 298.2 | 402.1
882 | 724 | 523.5 | 481.6 | 453.4 | 491.3 | 455.4 | 377.8 | 298.4 | 402.2
883 | 725 | 523.3 | 481.8 | 454.1 | 492.7 | 455.3 | 378 | 298.6 | 402.2
884 | 726 | 523.1 | 481.9 | 454.7 | 493.6 | 455.5 | 378.2 | 298.8 | 402.2
885 | 727 | 523.1 | 481.9 | 455.4 | 494.1 | 455.7 | 378.4 | 299 | 402.2
886 | 728 | 522.9 | 481.8 | 456.2 | 494.8 | 455.5 | 378.5 | 299.1 | 402.1
887 | 729 | 522.7 | 481.8 | 457 | 495.6 | 455.3 | 378.5 | 299.3 | 402
888 | 730 | 522.7 | 482.1 | 457.7 | 496.8 | 455.4 | 378.6 | 299.5 | 402.1
889 | 731 | 522.6 | 482.6 | 458.5 | 497.7 | 455.6 | 378.8 | 299.6 | 402.1
890 | 732 | 522.3 | 483.1 | 459.3 | 498.3 | 455.8 | 378.9 | 299.8 | 402.2
891 | 733 | 522.1 | 483.3 | 460 | 499.4 | 455.7 | 379.1 | 299.9 | 402.2
892 | 734 | 522.1 | 483.6 | 460.7 | 500.3 | 455.6 | 379.3 | 300 | 402.2
893 | 735 | 522.1 | 483.7 | 461.4 | 500.8 | 455.6 | 379.4 | 300.2 | 402.3
894 | 736 | 522 | 483.9 | 461.9 | 501.4 | 455.5 | 379.6 | 300.3 | 402.2
895 | 737 | 522 | 484.1 | 462.5 | 502.3 | 455.5 | 379.8 | 300.5 | 402.1
896 | 738 | 522 | 484.5 | 463.1 | 503.1 | 455.8 | 380 | 300.6 | 402.1
897 | 739 | 522 | 484.9 | 463.6 | 503.3 | 456 | 380.2 | 300.7 | 402.1
898 | 740 | 522.1 | 485.2 | 464.2 | 504.6 | 456 | 380.3 | 300.9 | 402.1
899 | 741 | 522.2 | 485.3 | 464.8 | 505.7 | 456.1 | 380.5 | 301 | 402.1
900 | 742 | 522.2 | 485.5 | 465.4 | 506.4 | 456.4 | 380.6 | 301.1 | 402.1
901 | 743 | 522.2 | 485.8 | 466.1 | 506.7 | 456.6 | 380.9 | 301.2 | 402.1
902 | 744 | 521.9 | 486.2 | 466.6 | 506.7 | 456.9 | 381.1 | 301.4 | 402.1
903 | 745 | 521.9 | 486.4 | 467.2 | 506.9 | 456.8 | 381.2 | 301.5 | 402.1
904 | 746 | 521.9 | 486.6 | 467.8 | 507.4 | 457.1 | 381.4 | 301.6 | 402.1
905 | 747 | 522 | 486.6 | 468.4 | 507.9 | 457.3 | 381.5 | 301.7 | 402
906 | 748 | 522.1 | 486.6 | 469 | 508.4 | 457.5 | 381.6 | 301.8 | 402
907 | 749 | 522.1 | 486.3 | 469.6 | 508.9 | 457.7 | 381.7 | 302 | 402
908 | 750 | 522.1 | 486 | 470.2 | 509.4 | 457.8 | 381.8 | 302.1 | 402
909 | 751 | 522 | 485.6 | 470.8 | 509.7 | 458.1 | 382 | 302.2 | 402
910 | 752 | 522.1 | 485.2 | 471.3 | 509.7 | 458.3 | 382.2 | 302.3 | 402
911 | 753 | 522.1 | 484.9 | 471.8 | 509.7 | 458.6 | 382.4 | 302.3 | 402.1
912 | 754 | 522.1 | 484.8 | 472.3 | 509.3 | 459.1 | 382.6 | 302.4 | 402.1
913 | 755 | 522.2 | 484.5 | 472.9 | 508.7 | 459.6 | 382.9 | 302.5 | 402.2
914 | 756 | 522.4 | 484.2 | 473.5 | 507.7 | 460.1 | 383.1 | 302.5 | 402.2
915 | 757 | 522.5 | 483.8 | 474.1 | 506.6 | 460.4 | 383.4 | 302.6 | 402.2
916 | 758 | 522.5 | 483.5 | 474.7 | 505.4 | 461.1 | 383.6 | 302.6 | 402.3
917 | 759 | 522.4 | 483.4 | 475.2 | 504.3 | 461.7 | 383.9 | 302.7 | 402.4
918 | 760 | 522.4 | 483.2 | 475.7 | 503.4 | 462.2 | 384.2 | 302.8 | 402.5
919 | 761 | 522.4 | 482.7 | 476.2 | 502.9 | 462.8 | 384.4 | 302.8 | 402.5
920 | 762 | 522.4 | 482.1 | 476.8 | 502.3 | 463.2 | 384.6 | 302.9 | 402.6
921 | 763 | 522.4 | 481.7 | 477.4 | 501.7 | 463.7 | 384.7 | 303.1 | 402.7
922 | 764 | 522.4 | 481.5 | 477.8 | 501.5 | 464.5 | 384.9 | 303.2 | 402.8
923 | 765 | 522.6 | 481.4 | 478.2 | 501.3 | 465.1 | 385 | 303.3 | 402.8
924 | 766 | 522.6 | 481.3 | 478.7 | 501.2 | 465.7 | 385.2 | 303.4 | 402.9
925 | 767 | 522.5 | 481.5 | 479.1 | 501.3 | 466.3 | 385.4 | 303.4 | 403
926 | 768 | 522.4 | 481.9 | 479.5 | 501.5 | 466.8 | 385.6 | 303.5 | 403.1
927 | 769 | 522.3 | 482.2 | 480 | 501.8 | 467.1 | 385.8 | 303.6 | 403.2
928 | 770 | 522.2 | 482.6 | 480.5 | 502.7 | 467.4 | 386 | 303.7 | 403.3
929 | 771 | 522.1 | 483.3 | 481 | 504 | 467.5 | 386.3 | 303.7 | 403.4
930 | 772 | 522.1 | 483.6 | 481.7 | 504.9 | 467.9 | 386.5 | 303.8 | 403.4
931 | 773 | 522.1 | 484 | 482.2 | 505.6 | 468.2 | 386.7 | 304 | 403.5
932 | 774 | 522.2 | 484.6 | 482.7 | 506.7 | 468.4 | 386.9 | 304.1 | 403.6
933 | 775 | 522.1 | 484.8 | 483.1 | 508 | 468.5 | 387.1 | 304.2 | 403.7
934 | 776 | 521.9 | 484.8 | 483.5 | 508.9 | 468.7 | 387.3 | 304.3 | 403.7
935 | 777 | 521.8 | 485 | 484 | 509.6 | 468.9 | 387.6 | 304.4 | 403.8
936 | 778 | 521.5 | 485.2 | 484.3 | 510 | 469.2 | 387.8 | 304.6 | 403.8
937 | 779 | 521.3 | 485.4 | 484.7 | 509.9 | 469.2 | 388 | 304.6 | 403.9
938 | 780 | 521.1 | 485.3 | 485.1 | 509.4 | 469.3 | 388.3 | 304.7 | 404
939 | 781 | 521.1 | 485.2 | 485.5 | 508.9 | 469.6 | 388.5 | 304.8 | 404.1
940 | 782 | 521.2 | 485.2 | 485.8 | 508.7 | 469.9 | 388.8 | 304.9 | 404.1
941 | 783 | 521.3 | 485.2 | 486.3 | 508.4 | 470.2 | 389 | 305 | 404.2
942 | 784 | 521.2 | 485.3 | 486.8 | 507.8 | 470.6 | 389.3 | 305 | 404.3
943 | 785 | 521.1 | 485.6 | 487.2 | 507.7 | 471.1 | 389.5 | 305.1 | 404.4
944 | 786 | 521 | 485.8 | 487.6 | 507.9 | 471.3 | 389.8 | 305.2 | 404.4
945 | 787 | 521.1 | 486 | 488 | 508.2 | 471.8 | 390 | 305.3 | 404.6
946 | 788 | 521.5 | 486.1 | 488.4 | 509.1 | 472 | 390.3 | 305.4 | 404.6
947 | 789 | 521.7 | 486.4 | 488.8 | 510.5 | 472 | 390.6 | 305.5 | 404.7
948 | 790 | 521.9 | 486.9 | 489.2 | 512 | 472 | 390.8 | 305.6 | 404.8
949 | 791 | 522.1 | 487.2 | 489.6 | 513.3 | 472.1 | 391 | 305.7 | 404.9
950 | 792 | 522.3 | 487.5 | 490 | 514.6 | 472.4 | 391.3 | 305.9 | 405
951 | 793 | 522.2 | 488.2 | 490.4 | 515.8 | 472.4 | 391.5 | 306 | 405
952 | 794 | 522.1 | 489.5 | 490.9 | 517 | 472.2 | 391.7 | 306.1 | 405
953 | 795 | 522.1 | 491 | 491.8 | 518 | 471.8 | 392 | 306.3 | 405
954 | 796 | 522.1 | 492.6 | 492.5 | 518.9 | 471.7 | 392.1 | 306.4 | 405.1
955 | 797 | 522.2 | 493.9 | 493.1 | 519.6 | 471.7 | 392.3 | 306.6 | 405.1
956 | 798 | 522.2 | 494.8 | 493.8 | 520.4 | 471.5 | 392.4 | 306.8 | 405.1
957 | 799 | 522.1 | 495.9 | 494.3 | 520.5 | 471.8 | 392.5 | 306.9 | 405.2
958 | 800 | 522.1 | 496.5 | 494.7 | 520 | 471.9 | 392.7 | 307 | 405.3
959 | 801 | 522 | 496.9 | 495.2 | 520 | 472 | 392.8 | 307.2 | 405.3
960 | 802 | 522.1 | 497.7 | 495.7 | 520.4 | 471.9 | 393 | 307.3 | 405.4
961 | 803 | 521.9 | 498.8 | 496.2 | 521.1 | 471.4 | 393.2 | 307.5 | 405.3
962 | 804 | 521.8 | 499.7 | 496.7 | 521.8 | 471.4 | 393.4 | 307.6 | 405.3
963 | 805 | 521.7 | 500 | 497.2 | 522.1 | 471.4 | 393.6 | 307.8 | 405.4
964 | 806 | 521.5 | 500.3 | 497.7 | 522.7 | 471.2 | 393.7 | 307.9 | 405.5
965 | 807 | 521.2 | 500.8 | 498.3 | 523.5 | 470.9 | 393.9 | 308 | 405.5
966 | 808 | 520.9 | 500.7 | 498.7 | 524.2 | 470.9 | 394.1 | 308.2 | 405.5
967 | 809 | 520.6 | 500.5 | 499.2 | 525 | 471 | 394.3 | 308.3 | 405.5
968 | 810 | 520.6 | 500.6 | 499.7 | 525.7 | 471 | 394.5 | 308.4 | 405.5
969 | 811 | 520.4 | 500.4 | 500.1 | 526.2 | 471.2 | 394.7 | 308.5 | 405.5
970 | 812 | 520.4 | 500.7 | 500.7 | 526.5 | 471.2 | 394.8 | 308.5 | 405.5
971 | 813 | 520.6 | 501.1 | 501.2 | 527 | 471.2 | 395 | 308.6 | 405.5
972 | 814 | 520.8 | 501.9 | 501.6 | 527.4 | 471.3 | 395.2 | 308.7 | 405.5
973 | 815 | 521.1 | 502.5 | 502.1 | 527.2 | 471.1 | 395.4 | 308.8 | 405.5
974 | 816 | 521.3 | 502.6 | 502.7 | 526.6 | 471 | 395.6 | 308.9 | 405.6
975 | 817 | 521.4 | 502.6 | 503.1 | 526.3 | 471.2 | 395.7 | 308.9 | 405.7
976 | 818 | 521.7 | 502.8 | 503.7 | 526.3 | 470.8 | 395.9 | 309 | 405.7
977 | 819 | 522 | 503.1 | 504.3 | 526.4 | 470.6 | 396.1 | 309.1 | 405.7
978 | 820 | 522.2 | 503.4 | 504.7 | 526.6 | 470.6 | 396.2 | 309.2 | 405.8
979 | 821 | 522.5 | 503.8 | 505.3 | 526.9 | 470.5 | 396.4 | 309.3 | 405.8
980 | 822 | 522.6 | 503.7 | 506 | 527.4 | 470.5 | 396.5 | 309.5 | 405.9
981 | 823 | 522.5 | 503.6 | 506.7 | 527.6 | 470.7 | 396.7 | 309.6 | 405.9
982 | 824 | 522.5 | 503.4 | 507.4 | 527.3 | 470.6 | 396.8 | 309.7 | 406
983 | 825 | 522.4 | 503.3 | 508.4 | 526.9 | 470.9 | 396.9 | 309.8 | 406.1
984 | 826 | 522.3 | 503.5 | 509 | 526.9 | 470.8 | 397.1 | 310 | 406.1
985 | 827 | 522.4 | 504.1 | 509.3 | 527.3 | 470.6 | 397.3 | 310.1 | 406.1
986 | 828 | 522.3 | 505 | 509.7 | 528.2 | 470.4 | 397.4 | 310.2 | 406.1
987 | 829 | 522.1 | 505.9 | 510.1 | 529.1 | 470.3 | 397.6 | 310.4 | 406.2
988 | 830 | 522.1 | 506.4 | 510.6 | 529.7 | 470.3 | 397.8 | 310.5 | 406.3
989 | 831 | 521.9 | 506.5 | 511.3 | 529.8 | 470.2 | 397.9 | 310.6 | 406.3
990 | 832 | 521.7 | 506.6 | 511.8 | 529.4 | 470.3 | 398 | 310.7 | 406.4
991 | 833 | 521.4 | 506.7 | 512.1 | 529 | 470.5 | 398.2 | 310.8 | 406.5
992 | 834 | 521.2 | 507 | 512.5 | 529.1 | 471.2 | 398.3 | 310.8 | 406.8
993 | 835 | 521.2 | 507.8 | 513.3 | 530 | 471.7 | 398.4 | 310.9 | 407.3
994 | 836 | 521.3 | 509.1 | 514.2 | 531 | 472.7 | 398.5 | 310.9 | 408
995 | 837 | 521.2 | 510.9 | 515.5 | 531.7 | 473.2 | 398.7 | 311 | 409.1
996 | 838 | 521.1 | 512.8 | 516.8 | 531.9 | 474 | 399 | 311.1 | 410.4
997 | 839 | 521.1 | 514.9 | 518.5 | 531.8 | 474.8 | 399.1 | 311.2 | 411.7
998 | 840 | 521 | 517.1 | 520.5 | 531.5 | 476.1 | 399.2 | 311.2 | 413.1
999 | 841 | 521.1 | 518.8 | 522.7 | 531 | 478.3 | 399.1 | 311.4 | 414.4
1000 | 842 | 521.3 | 519.7 | 525.1 | 530.4 | 482.5 | 399.5 | 311.5 | 415.9
1001 | 843 | 521.5 | 520 | 527.5 | 529.5 | 484.9 | 400 | 311.6 | 417.5
1002 | 844 | 521.5 | 520.1 | 529.8 | 528.6 | 488.3 | 400.5 | 311.7 | 419.4
1003 | 845 | 521.7 | 519.8 | 532.2 | 527.6 | 493 | 401.3 | 311.9 | 421.7
1004 | 846 | 521.9 | 519.6 | 534.9 | 526.6 | 497 | 402.5 | 312 | 424.3
1005 | 847 | 522 | 519.4 | 537.6 | 525.8 | 499.8 | 404.2 | 312.1 | 427
1006 | 848 | 522.2 | 519.6 | 540.3 | 525.1 | 501.3 | 405.9 | 312.3 | 429.6
1007 | 849 | 522.3 | 519.6 | 542.9 | 524.6 | 504.2 | 408.1 | 312.4 | 432.2
1008 | 850 | 522.3 | 519.7 | 545.6 | 524.3 | 506.1 | 410.6 | 312.5 | 434.6
1009 | 851 | 522.6 | 520.1 | 548.1 | 524.2 | 509.1 | 412.2 | 312.7 | 437.1
1010 | 852 | 522.7 | 520.5 | 550.6 | 524.3 | 511.6 | 414.1 | 312.8 | 439.8
1011 | 853 | 522.8 | 521.5 | 552.8 | 524.5 | 514 | 416.4 | 313 | 442.5
1012 | 854 | 522.8 | 522.7 | 555 | 524.9 | 516.1 | 419 | 313.1 | 445.1
1013 | 855 | 522.7 | 523.9 | 557.1 | 525.4 | 518.8 | 422.3 | 313.3 | 447.8
1014 | 856 | 522.7 | 524.8 | 559.2 | 526.1 | 520.4 | 425.8 | 313.4 | 450.5
1015 | 857 | 522.6 | 525.7 | 561.1 | 526.8 | 521.4 | 431 | 313.6 | 453.2
1016 | 858 | 522.3 | 526.5 | 563.1 | 527.6 | 522 | 436.2 | 313.7 | 455.6
1017 | 859 | 521.9 | 527.3 | 565 | 528.4 | 522.4 | 440.7 | 313.8 | 458.1
1018 | 860 | 521.7 | 528.3 | 567 | 529.1 | 522.5 | 446.2 | 314 | 460.6
1019 | 861 | 521.5 | 529.2 | 569 | 529.6 | 523 | 451.8 | 314.1 | 462.9
1020 | 862 | 521.4 | 530 | 570.8 | 530.3 | 523.6 | 459 | 314.3 | 465.2
1021 | 863 | 521.1 | 531 | 572.6 | 531.2 | 525 | 463.4 | 314.4 | 467.4
1022 | 864 | 520.8 | 531.9 | 574.3 | 532.8 | 527.5 | 469.9 | 314.6 | 469.7
1023 | 865 | 520.7 | 533 | 576.2 | 534.5 | 528.4 | 475.8 | 314.7 | 472
1024 | 866 | 520.6 | 534 | 577.8 | 536.1 | 528.7 | 481.7 | 314.8 | 474.3
1025 | 867 | 520.5 | 534.8 | 579.6 | 537.2 | 530.1 | 485.4 | 314.9 | 476.4
1026 | 868 | 520.5 | 535.7 | 581.2 | 538.3 | 532.2 | 491 | 315 | 478.5
1027 | 869 | 520.4 | 536.6 | 582.7 | 539.4 | 534 | 495.7 | 315.1 | 480.5
1028 | 870 | 520.3 | 537.5 | 584 | 540.6 | 535.9 | 501.2 | 315.3 | 482.4
1029 | 871 | 519.9 | 538.4 | 585.6 | 541.7 | 537.8 | 504.3 | 315.4 | 484.3
1030 | 872 | 519.6 | 539.2 | 586.9 | 542.6 | 540 | 509.7 | 315.5 | 486.1
1031 | 873 | 519.3 | 540.1 | 588.3 | 543.5 | 542.5 | 515.1 | 315.5 | 487.7
1032 | 874 | 518.8 | 541.1 | 589.5 | 544.4 | 545 | 521.7 | 315.6 | 489.4
1033 | 875 | 518.5 | 542.2 | 590.5 | 545.4 | 548.6 | 528.5 | 315.7 | 491
1034 | 876 | 518.2 | 543.3 | 591.5 | 546.7 | 552.6 | 534.4 | 315.7 | 492.8
1035 | 877 | 518 | 544.6 | 592.5 | 548.3 | 557.5 | 539.3 | 315.8 | 494.6
1036 | 878 | 517.8 | 545.5 | 593.5 | 550.2 | 560.6 | 547.3 | 315.9 | 496.5
1037 | 879 | 517.7 | 546.2 | 595.4 | 551.9 | 561.9 | 552.3 | 316 | 498.5
1038 | 880 | 517.5 | 547.1 | 596.8 | 553.9 | 565.2 | 559.1 | 316.2 | 500.2
1039 | 881 | 517 | 547.9 | 598.2 | 556 | 568.2 | 563.6 | 316.3 | 502
1040 | 882 | 516.6 | 549 | 599.5 | 558 | 568.8 | 569.5 | 316.4 | 503.8
1041 | 883 | 516.1 | 550.3 | 600.6 | 560.1 | 568.7 | 574.4 | 316.6 | 505.5
1042 | 884 | 515.4 | 551.3 | 601.6 | 562.1 | 569.9 | 578.4 | 316.7 | 507.1
1043 | 885 | 514.7 | 552.5 | 602.7 | 564.1 | 572.4 | 584.9 | 316.8 | 508.7
1044 | 886 | 514 | 553.9 | 603.8 | 566.2 | 576.3 | 589 | 316.9 | 510.3
1045 | 887 | 513.2 | 555.3 | 604.9 | 568.5 | 579.3 | 594.6 | 317 | 511.8
1046 | 888 | 512.5 | 556.5 | 606.1 | 571 | 580.6 | 598.7 | 317.2 | 513.4
1047 | 889 | 511.6 | 557.7 | 607.2 | 573.3 | 582 | 603.2 | 317.3 | 514.9
1048 | 890 | 510.6 | 559.1 | 608.4 | 575.8 | 583.1 | 605.8 | 317.5 | 516.3
1049 | 891 | 509.6 | 560.2 | 609.3 | 578.6 | 585.3 | 609.6 | 317.7 | 517.6
1050 | 892 | 508.6 | 561.6 | 610.2 | 582.1 | 588.5 | 613.1 | 317.8 | 518.9
1051 | 893 | 507.6 | 563.6 | 611.2 | 586.1 | 591.2 | 617.1 | 318 | 520.2
1052 | 894 | 506.5 | 566 | 612.3 | 589.9 | 592.6 | 621.5 | 318.2 | 521.4
1053 | 895 | 505.4 | 568.2 | 613.5 | 593.3 | 594.8 | 625.4 | 318.4 | 522.7
1054 | 896 | 504.3 | 570.1 | 614.9 | 595.8 | 595 | 627.7 | 318.5 | 524
1055 | 897 | 503.2 | 571.8 | 616.2 | 597.9 | 595.4 | 628.1 | 318.7 | 524.9
1056 | 898 | 502.1 | 573.4 | 617.4 | 600 | 596.7 | 628.4 | 318.8 | 525.9
1057 | 899 | 501 | 575.3 | 618.5 | 602.7 | 598.6 | 628.4 | 318.9 | 527.2
1058 | 900 | 500 | 576.7 | 619.3 | 606.3 | 600.3 | 629 | 319.1 | 528.4
1059 | 901 | 498.9 | 578.4 | 620.3 | 609.7 | 601 | 629.1 | 319.2 | 529.6
1060 | 902 | 497.8 | 579.9 | 621.3 | 612.8 | 602.2 | 627.3 | 319.3 | 530.6
1061 | 903 | 497 | 581.4 | 622.1 | 615.6 | 602.5 | 625.6 | 319.3 | 531.6
1062 | 904 | 496 | 582.9 | 622.8 | 618.1 | 602.6 | 623.8 | 319.4 | 532.5
1063 | 905 | 495 | 584.5 | 623.3 | 620.7 | 604.2 | 622.5 | 319.5 | 533.3
1064 | 906 | 493.7 | 585.7 | 623.8 | 623 | 604.7 | 620.7 | 319.7 | 534.2
1065 | 907 | 492.4 | 587 | 624.3 | 625.3 | 604.5 | 618.4 | 319.8 | 534.9
1066 | 908 | 491.2 | 589 | 624.7 | 627.5 | 604.8 | 615.6 | 319.9 | 535.7
1067 | 909 | 490.1 | 590.4 | 625.2 | 629.6 | 605.3 | 612.4 | 320 | 536.5
1068 | 910 | 489.2 | 591.6 | 625.7 | 631.7 | 606.2 | 607.7 | 320.2 | 537.2
1069 | 911 | 488.4 | 592.7 | 626.1 | 633.5 | 606.3 | 605.8 | 320.3 | 537.8
1070 | 912 | 487.3 | 593.8 | 626.5 | 635 | 606.1 | 603.5 | 320.4 | 538.5
1071 | 913 | 486.1 | 594.7 | 626.7 | 636.2 | 606.2 | 601.8 | 320.5 | 539.1
1072 | 914 | 485.2 | 595.8 | 626.7 | 638 | 607 | 600.1 | 320.7 | 539.5
1073 | 915 | 484.5 | 597.2 | 627 | 640 | 608 | 599.1 | 320.8 | 539.9
1074 | 916 | 483.6 | 598.8 | 627 | 641.4 | 608.8 | 598.3 | 320.9 | 540.4
1075 | 917 | 482.6 | 599.8 | 627 | 642 | 609.5 | 597.9 | 321 | 540.8
1076 | 918 | 481.4 | 600.5 | 627.2 | 642.3 | 610.2 | 598 | 321.1 | 541.1
1077 | 919 | 480.3 | 601.4 | 628.1 | 642.7 | 611 | 597.9 | 321.2 | 541.4
1078 | 920 | 479.3 | 601.6 | 628.1 | 642.9 | 611.6 | 598.5 | 321.4 | 541.6
1079 | 921 | 478.3 | 601.8 | 628.1 | 642.5 | 611.8 | 597.9 | 321.4 | 541.7
1080 | 922 | 477.1 | 602.3 | 628.1 | 642.1 | 612 | 598.2 | 321.5 | 542
1081 | 923 | 476.2 | 604.9 | 628 | 642.2 | 612.6 | 598.7 | 321.6 | 542.4
1082 | 924 | 475 | 607.1 | 628.1 | 642.2 | 613.3 | 598.8 | 321.7 | 542.8
1083 | 925 | 473.9 | 608.7 | 628.3 | 642.5 | 614.3 | 598.7 | 321.8 | 543.2
1084 | 926 | 473 | 610.1 | 628.5 | 642.8 | 615.2 | 598.9 | 321.8 | 543.6
1085 | 927 | 472 | 611.3 | 628.8 | 643 | 616.3 | 599.7 | 321.9 | 543.8
1086 | 928 | 471 | 612.2 | 628.9 | 644.1 | 617.9 | 599.7 | 322 | 544
1087 | 929 | 469.9 | 613.4 | 629.3 | 645.8 | 620.4 | 599.6 | 322.1 | 544.1
1088 | 930 | 469 | 615.3 | 629.6 | 647.8 | 623.7 | 599.6 | 322.2 | 544.2
1089 | 931 | 468.3 | 616.9 | 629.8 | 649.5 | 626.7 | 599.8 | 322.4 | 544.2
1090 | 932 | 467.4 | 617.7 | 630.4 | 651.3 | 631.3 | 600.6 | 322.5 | 544.4
1091 | 933 | 466.3 | 618.1 | 631 | 653.9 | 635.8 | 600.8 | 322.7 | 544.4
1092 | 934 | 465.3 | 618.4 | 631 | 656.5 | 639.8 | 601.2 | 322.9 | 544.5
1093 | 935 | 464.3 | 618.4 | 631.4 | 658.3 | 643.7 | 601 | 323 | 544.6
1094 | 936 | 463.3 | 618.4 | 631.7 | 659.2 | 647 | 600.8 | 323.2 | 544.5
1095 | 937 | 462.2 | 618.3 | 632.1 | 659.8 | 649.9 | 601.1 | 323.3 | 544.4
1096 | 938 | 461.1 | 618.4 | 632.6 | 660.8 | 652.8 | 600.8 | 323.5 | 544.4
1097 | 939 | 460.1 | 618.9 | 633.1 | 661.6 | 656 | 600.7 | 323.6 | 544.5
1098 | 940 | 459.2 | 619.6 | 633.4 | 662.7 | 659.5 | 600.8 | 323.8 | 544.6
1099 | 941 | 458.4 | 620.2 | 633.9 | 664.2 | 662.6 | 600.2 | 324 | 544.5
1100 | 942 | 457.6 | 620.8 | 634.6 | 665.8 | 665.5 | 600.3 | 324.1 | 544.5
1101 | 943 | 456.6 | 621.6 | 634.9 | 666.4 | 667.7 | 600.3 | 324.3 | 544.4
1102 | 944 | 455.6 | 623 | 635.4 | 666.5 | 669.6 | 599.6 | 324.4 | 544.4
1103 | 945 | 454.6 | 625 | 635.9 | 666.3 | 670.9 | 599.1 | 324.6 | 544.3
1104 | 946 | 453.8 | 626.9 | 636 | 665.8 | 671.8 | 598.5 | 324.7 | 544.1
1105 | 947 | 453 | 629.4 | 636.3 | 665.2 | 672.7 | 598.4 | 324.9 | 544
1106 | 948 | 452.3 | 632.7 | 636.7 | 664.4 | 673.2 | 598.8 | 325 | 544
1107 | 949 | 451.6 | 635.3 | 637.1 | 663.7 | 673.2 | 598.3 | 325.1 | 543.8
1108 | 950 | 450.5 | 637.9 | 637.5 | 663 | 673.3 | 598.5 | 325.2 | 543.5
1109 | 951 | 449.6 | 641.6 | 637.8 | 662.7 | 674.6 | 599 | 325.3 | 543.1
1110 | 952 | 448.6 | 645.8 | 638.2 | 662.7 | 675.7 | 599.5 | 325.4 | 542.5
1111 | 953 | 447.6 | 649.2 | 638.6 | 662.9 | 676.5 | 599.8 | 325.5 | 542
1112 | 954 | 446.5 | 652.3 | 638.9 | 663.3 | 677.9 | 600 | 325.6 | 541.5
1113 | 955 | 445.4 | 654.3 | 639.3 | 663.6 | 680 | 599.7 | 325.6 | 540.8
1114 | 956 | 444.5 | 654.6 | 639.8 | 663.9 | 681.3 | 600.4 | 325.7 | 540.1
1115 | 957 | 443.5 | 655.2 | 640.3 | 664.4 | 682.4 | 600.5 | 325.8 | 539.2
1116 | 958 | 442.6 | 655.9 | 640.8 | 664.9 | 682.9 | 600.7 | 325.9 | 538.4
1117 | 959 | 441.7 | 655.7 | 641.5 | 665.4 | 683.1 | 601.7 | 326 | 537.6
1118 | 960 | 440.9 | 655 | 642.1 | 665.9 | 683.3 | 602.6 | 326.2 | 536.9
1119 | 961 | 439.9 | 654.9 | 642.7 | 666.3 | 683.8 | 603.6 | 326.3 | 536.3
1120 | 962 | 439 | 654.6 | 643.2 | 666.9 | 684.4 | 604.3 | 326.4 | 535.8
1121 | 963 | 438.3 | 654.1 | 643.9 | 668 | 685.1 | 604.4 | 326.5 | 535.1
1122 | 964 | 437.4 | 653.6 | 645.1 | 669.7 | 686 | 604.2 | 326.6 | 534.4
1123 | 965 | 436.6 | 654.3 | 645.4 | 672.5 | 689.6 | 603.9 | 326.8 | 533.6
1124 | 966 | 435.8 | 656.4 | 645.6 | 675.4 | 695.1 | 603.5 | 326.9 | 532.8
1125 | 967 | 434.9 | 659.2 | 645.8 | 677.4 | 699.6 | 603.3 | 327.1 | 531.9
1126 | 968 | 434 | 660.9 | 645.8 | 679.1 | 704.7 | 602.7 | 327.2 | 531
1127 | 969 | 433 | 661.4 | 645.9 | 679.7 | 707 | 602 | 327.4 | 530.2
1128 | 970 | 432.1 | 661.5 | 645.9 | 680.1 | 707.1 | 602.1 | 327.5 | 529.3
1129 | 971 | 431.2 | 661.4 | 646.1 | 680.6 | 707.9 | 602 | 327.6 | 528.5
1130 | 972 | 430.3 | 661.8 | 646.5 | 681.6 | 709.3 | 601.8 | 327.7 | 527.8
1131 | 973 | 429.4 | 662 | 646.8 | 682.8 | 710.5 | 601.5 | 327.9 | 527.1
1132 | 974 | 428.6 | 662.9 | 647 | 683.6 | 711.8 | 602.3 | 328.1 | 526.4
1133 | 975 | 427.7 | 663.5 | 647.2 | 684.4 | 712.2 | 603.3 | 328.3 | 525.8
1134 | 976 | 426.8 | 665.2 | 647.6 | 684.6 | 712.8 | 604.5 | 328.5 | 525.1
1135 | 977 | 425.9 | 666.7 | 648.2 | 685.5 | 713.1 | 606.6 | 328.7 | 524.5
1136 | 978 | 425 | 667.1 | 648.4 | 686.1 | 711.5 | 608 | 328.9 | 523.9
1137 | 979 | 424.1 | 666.9 | 648.7 | 685.5 | 709.9 | 608.3 | 329 | 523.3
1138 | 980 | 423.2 | 667.7 | 649.2 | 685.4 | 709.8 | 608.8 | 329.2 | 522.8
1139 | 981 | 422.2 | 668.1 | 649.7 | 685.7 | 709.7 | 608.7 | 329.3 | 522.3
1140 | 982 | 421.3 | 668.5 | 650.1 | 685.5 | 709.4 | 608.8 | 329.5 | 521.8
1141 | 983 | 420.3 | 671 | 650.5 | 685.2 | 707.9 | 609 | 329.6 | 521.2
1142 | 984 | 419.4 | 673 | 650.7 | 684.8 | 706.3 | 609.3 | 329.7 | 520.7
1143 | 985 | 418.6 | 674 | 651 | 684.5 | 706.1 | 609.6 | 329.8 | 520.3
1144 | 986 | 417.8 | 674.6 | 651.3 | 684.6 | 706.4 | 609.6 | 329.9 | 519.8
1145 | 987 | 417 | 675.6 | 651.6 | 684.7 | 706 | 609.6 | 330 | 519.4
1146 | 988 | 416.1 | 675.3 | 652 | 685 | 705.9 | 609.8 | 330.1 | 519
1147 | 989 | 415.2 | 673.3 | 652.5 | 685 | 705.4 | 609.9 | 330.1 | 518.5
1148 | 990 | 414.3 | 674.7 | 652.6 | 685.4 | 704.5 | 609.9 | 330.2 | 518.1
1149 | 991 | 413.4 | 674.5 | 653.1 | 686.2 | 704 | 610.1 | 330.3 | 517.7
1150 | 992 | 412.7 | 675 | 653.5 | 687.4 | 704.2 | 610 | 330.3 | 517.2
1151 | 993 | 411.8 | 674.3 | 654.3 | 688.9 | 704.4 | 610.4 | 330.4 | 516.7
1152 | 994 | 411 | 673.8 | 654.6 | 690.4 | 706 | 611.3 | 330.5 | 516.2
1153 | 995 | 410.3 | 674.4 | 654.7 | 691.6 | 706.8 | 611.3 | 330.6 | 515.8
1154 | 996 | 409.5 | 675 | 654.9 | 692.4 | 706.1 | 611.3 | 330.7 | 515.4
1155 | 997 | 408.8 | 675.3 | 655.3 | 693.1 | 704.5 | 611.5 | 330.8 | 515
1156 | 998 | 408.1 | 674.7 | 656.1 | 694.2 | 703.4 | 611.9 | 330.8 | 514.5
1157 | 999 | 407.4 | 675.8 | 656.3 | 696.2 | 703.2 | 612.8 | 330.9 | 514.1
1158 | 1000 | 406.7 | 678.3 | 656.9 | 698 | 703.8 | 613.7 | 331 | 513.7
1159 | 1001 | 405.9 | 679.4 | 656.8 | 699.6 | 705.9 | 614.1 | 331.1 | 513.2
1160 | 1002 | 405 | 678.1 | 657.1 | 700.6 | 706.1 | 614.2 | 331.1 | 512.7
1161 | 1003 | 404.1 | 676.2 | 657.1 | 700.6 | 706.1 | 614.8 | 331.2 | 512.3
1162 | 1004 | 403.2 | 674.6 | 657.3 | 700.4 | 705.5 | 615.1 | 331.2 | 511.9
1163 | 1005 | 402.4 | 672.8 | 657.4 | 700.2 | 704.5 | 616.2 | 331.3 | 511.5
1164 | 1006 | 401.4 | 673.2 | 657.6 | 700.1 | 703.9 | 616.8 | 331.3 | 511.2
1165 | 1007 | 400.5 | 674.6 | 658 | 700.7 | 702.5 | 617.3 | 331.3 | 510.9
1166 | 1008 | 399.6 | 674.6 | 658.4 | 701.7 | 700.9 | 617.7 | 331.4 | 510.5
1167 | 1009 | 398.6 | 674.4 | 658.7 | 703.4 | 699.8 | 618.9 | 331.4 | 510
1168 | 1010 | 397.8 | 676.9 | 659 | 706.5 | 699.4 | 619.9 | 331.4 | 509.5
1169 | 1011 | 397.1 | 681.7 | 659.1 | 709.5 | 699.8 | 621.7 | 331.5 | 508.9
1170 | 1012 | 396.5 | 684.2 | 659.4 | 712.6 | 701.5 | 624.7 | 331.5 | 508.4
1171 | 1013 | 395.8 | 688.9 | 659.5 | 715.4 | 703.7 | 626.5 | 331.5 | 507.9
1172 | 1014 | 395.1 | 693.9 | 659.8 | 717.8 | 705.5 | 628 | 331.5 | 507.4
1173 | 1015 | 394.3 | 696.6 | 660.7 | 720.9 | 707.4 | 629 | 331.6 | 506.9
1174 | 1016 | 393.5 | 698.2 | 660.8 | 724 | 708 | 629.8 | 331.6 | 506.4
1175 | 1017 | 392.7 | 701.1 | 661 | 725.5 | 707.5 | 629.9 | 331.6 | 505.9
1176 | 1018 | 392.1 | 701.8 | 662 | 726.2 | 707.1 | 630 | 331.6 | 505.4
1177 | 1019 | 391.5 | 700.7 | 661.9 | 726.6 | 706.6 | 629.9 | 331.6 | 505
1178 | 1020 | 390.8 | 698.5 | 661.9 | 726.9 | 706.3 | 629.6 | 331.6 | 504.5
1179 | 1021 | 390.1 | 696.8 | 661.8 | 727.4 | 705.8 | 629.2 | 331.5 | 504.1
1180 | 1022 | 389.3 | 693.3 | 662.1 | 729.6 | 705.8 | 629 | 331.5 | 503.6
1181 | 1023 | 388.5 | 691.2 | 662.2 | 730 | 704.9 | 629.2 | 331.5 | 503.2
1182 | 1024 | 387.8 | 692.6 | 662.3 | 729.9 | 703.8 | 629.4 | 331.4 | 502.8
1183 | 1025 | 387 | 692.7 | 662.6 | 730 | 702.7 | 629.5 | 331.3 | 502.4
1184 | 1026 | 386.2 | 690.1 | 662.9 | 732.1 | 701.9 | 629.9 | 331.3 | 502
1185 | 1027 | 385.6 | 691.8 | 663.5 | 736 | 701.8 | 630 | 331.2 | 501.7
1186 | 1028 | 385 | 694.4 | 664 | 738.8 | 702.8 | 630 | 331.2 | 501.3
1187 | 1029 | 384.1 | 692.3 | 664.2 | 742.3 | 704 | 630.9 | 331.1 | 500.9
1188 | 1030 | 383.3 | 690.4 | 664.5 | 747.4 | 705.3 | 633.2 | 331.1 | 500.6
1189 | 1031 | 382.5 | 690.1 | 665 | 758.9 | 706.1 | 638.2 | 331 | 500.2
1190 | 1032 | 381.8 | 690.1 | 665.7 | 770.8 | 705.8 | 642.5 | 330.9 | 499.9
1191 | 1033 | 381.2 | 689.8 | 666.2 | 779.2 | 706 | 645.8 | 330.9 | 499.4
1192 | 1034 | 380.4 | 689 | 667 | 782.2 | 705.9 | 648.3 | 330.8 | 499
1193 | 1035 | 379.4 | 688.6 | 668 | 784.3 | 706 | 651 | 330.8 | 498.4
1194 | 1036 | 378.7 | 687.9 | 669.2 | 784.2 | 706.1 | 653 | 330.7 | 497.9
1195 | 1037 | 377.9 | 686.9 | 670.4 | 782.8 | 706 | 656 | 330.6 | 497.4
1196 | 1038 | 377.3 | 689.9 | 671.3 | 782.4 | 705.7 | 658 | 330.5 | 496.9
1197 | 1039 | 376.6 | 692.5 | 672 | 782.3 | 705.6 | 658.9 | 330.4 | 496.4
1198 | 1040 | 375.6 | 691.6 | 672.7 | 781.2 | 705.5 | 659.8 | 330.3 | 495.8
1199 | 1041 | 374.8 | 690.1 | 673.6 | 779.3 | 705.2 | 662.8 | 330.3 | 495.3
1200 | 1042 | 374.1 | 689.6 | 674.4 | 777.9 | 704.6 | 663.6 | 330.2 | 494.8
1201 | 1043 | 373.5 | 688.6 | 675.3 | 776.7 | 703.8 | 664.2 | 330.1 | 494.3
1202 | 1044 | 372.9 | 687 | 676 | 775.3 | 702.9 | 664.3 | 330 | 493.9
1203 | 1045 | 372.3 | 686.1 | 676.8 | 773.9 | 702 | 665.7 | 329.9 | 493.5
1204 | 1046 | 371.6 | 684.8 | 677.9 | 771.8 | 701.3 | 667.2 | 329.8 | 493.1
1205 | 1047 | 370.9 | 684.5 | 678.4 | 769.8 | 700.5 | 667.6 | 329.7 | 492.7
1206 | 1048 | 370.2 | 685.2 | 678.6 | 767.9 | 699.9 | 667.7 | 329.6 | 492.3
1207 | 1049 | 369.5 | 685 | 679.3 | 765.4 | 698.6 | 667.6 | 329.5 | 491.8
1208 | 1050 | 368.8 | 684.5 | 679.7 | 762.1 | 696.8 | 668.9 | 329.3 | 491.3
1209 | 1051 | 368.1 | 683.8 | 680.3 | 758.5 | 694.6 | 670.4 | 329.2 | 490.8
1210 | 1052 | 367.4 | 684.9 | 680.6 | 755.1 | 692.4 | 670.8 | 329.1 | 490.3
1211 | 1053 | 366.7 | 685.6 | 680.9 | 751.5 | 690.4 | 670 | 329 | 489.7
1212 | 1054 | 366 | 686.2 | 681.3 | 748.6 | 688.6 | 669.9 | 328.9 | 489.1
1213 | 1055 | 365.3 | 686.9 | 681.4 | 745.7 | 686.6 | 668.9 | 328.7 | 488.6
1214 | 1056 | 364.6 | 689.4 | 681.2 | 742.5 | 684.9 | 667.4 | 328.6 | 488
1215 | 1057 | 364 | 691.5 | 680.9 | 740.2 | 683.6 | 667.3 | 328.5 | 487.4
1216 | 1058 | 363.3 | 692.6 | 680.7 | 738.1 | 682.5 | 667.1 | 328.4 | 486.9
1217 | 1059 | 362.6 | 693.1 | 680.7 | 735.4 | 681.4 | 667.1 | 328.3 | 486.4
1218 | 1060 | 361.9 | 692.8 | 681.1 | 733.4 | 680.3 | 666.5 | 328.2 | 485.9
1219 | 1061 | 361.2 | 694.1 | 681.1 | 732 | 679.2 | 666.6 | 328.1 | 485.4
1220 | 1062 | 360.5 | 694.7 | 680.9 | 726.3 | 678.4 | 667.3 | 328 | 484.9
1221 | 1063 | 360 | 694.7 | 681 | 716.9 | 677.8 | 668.1 | 327.9 | 484.4
1222 | 1064 | 359.5 | 693.9 | 681.3 | 710.7 | 677.9 | 668.5 | 327.8 | 483.9
1223 | 1065 | 358.9 | 693.2 | 681.5 | 708.5 | 677.8 | 668.9 | 327.7 | 483.4
1224 | 1066 | 358.2 | 693.3 | 681.1 | 704.8 | 677.3 | 670.1 | 327.6 | 482.9
1225 | 1067 | 357.7 | 692.9 | 681.3 | 699.2 | 675.8 | 671 | 327.5 | 482.4
1226 | 1068 | 357.1 | 694.1 | 681.3 | 695.6 | 672.7 | 670.5 | 327.4 | 481.9
1227 | 1069 | 356.4 | 696.8 | 680.9 | 693.3 | 669.8 | 669.7 | 327.4 | 481.4
1228 | 1070 | 355.8 | 697.5 | 680.7 | 690.7 | 669.4 | 668.8 | 327.3 | 481
1229 | 1071 | 355.1 | 696.4 | 681.1 | 690.4 | 669.7 | 667.5 | 327.2 | 480.6
1230 | 1072 | 354.4 | 695.8 | 680.8 | 690.5 | 669 | 665.9 | 327.1 | 480
1231 | 1073 | 353.7 | 697.2 | 680 | 690.8 | 667 | 665 | 327 | 479.6
1232 | 1074 | 353 | 698 | 680.3 | 687.1 | 665.7 | 664.3 | 326.9 | 479.1
1233 | 1075 | 352.4 | 696.9 | 681.7 | 684.4 | 664.4 | 663.3 | 326.8 | 478.6
1234 | 1076 | 351.9 | 695.9 | 682.4 | 681.4 | 663.2 | 661.9 | 326.7 | 478.2
1235 | 1077 | 351.1 | 694.5 | 683.4 | 679.1 | 662.8 | 660.7 | 326.6 | 477.7
1236 | 1078 | 350.4 | 693.2 | 683.9 | 679.8 | 661.9 | 659.4 | 326.5 | 477.2
1237 | 1079 | 349.7 | 693.1 | 683 | 679.3 | 660.4 | 658 | 326.4 | 476.7
1238 | 1080 | 349.1 | 692.1 | 683.1 | 675.8 | 658 | 656.9 | 326.3 | 476.2
1239 | 1081 | 348.4 | 683.7 | 682.9 | 672 | 656.2 | 655.9 | 326.2 | 475.7
1240 | 1082 | 347.8 | 668 | 681.5 | 670.4 | 654.2 | 655 | 326.1 | 475.3
1241 | 1083 | 347.3 | 652.7 | 681.8 | 671 | 651.8 | 654 | 326 | 474.8
1242 | 1084 | 346.6 | 638.1 | 688.1 | 672.7 | 649.1 | 652.8 | 325.9 | 474.3
1243 | 1085 | 346.1 | 622.1 | 691.7 | 675.2 | 647.7 | 651.2 | 325.8 | 473.8
1244 | 1086 | 345.3 | 605.1 | 695.8 | 672.2 | 647.1 | 649.3 | 325.7 | 473.3
1245 | 1087 | 344.8 | 588.1 | 702 | 671.3 | 646.2 | 648.2 | 325.6 | 472.8
1246 | 1088 | 344.3 | 575.2 | 704.7 | 670.2 | 645 | 647.2 | 325.5 | 472.2
1247 | 1089 | 343.9 | 564.4 | 706.5 | 669.9 | 643.8 | 645.4 | 325.4 | 471.7
1248 | 1090 | 343.3 | 552.2 | 707.8 | 670.3 | 641.2 | 643.5 | 325.3 | 471.2
1249 | 1091 | 342.7 | 537.1 | 705.9 | 670.9 | 639.6 | 641 | 325.2 | 470.7
1250 | 1092 | 342.2 | 523.5 | 703.6 | 669.9 | 639 | 638.3 | 325.2 | 470.2
1251 | 1093 | 341.5 | 509.2 | 704.6 | 669.3 | 637.6 | 636 | 325.1 | 469.7
1252 | 1094 | 340.8 | 497.2 | 707.8 | 668.7 | 635.6 | 634 | 325.1 | 469.2
1253 | 1095 | 340.1 | 485.8 | 711 | 667.6 | 633.5 | 631.8 | 325 | 468.6
1254 | 1096 | 339.5 | 478.3 | 715.8 | 666.8 | 631 | 629.4 | 324.9 | 468.1
1255 | 1097 | 338.9 | 469.4 | 719.4 | 663.5 | 627.8 | 626.9 | 324.8 | 467.6
1256 | 1098 | 338.2 | 458.7 | 720.6 | 656.8 | 625.6 | 624.1 | 324.8 | 467.1
1257 | 1099 | 337.6 | 450.3 | 722.7 | 652.9 | 625.1 | 621 | 324.7 | 466.6
1258 | 1100 | 337.1 | 443 | 717.2 | 651 | 625.2 | 617.8 | 324.6 | 466.1
1259 | 1101 | 336.5 | 437.4 | 711.6 | 649.6 | 625.5 | 614.5 | 324.5 | 465.5
1260 | 1102 | 336.1 | 432.6 | 707.3 | 647.6 | 625.6 | 611 | 324.5 | 465
1261 | 1103 | 335.4 | 424.6 | 703.6 | 644.7 | 625.1 | 607.6 | 324.4 | 464.5
1262 | 1104 | 334.9 | 417.3 | 703.3 | 644.2 | 623.4 | 604.2 | 324.3 | 464
1263 | 1105 | 334.3 | 413.3 | 702.1 | 642 | 621.1 | 600.9 | 324.1 | 463.5
1264 | 1106 | 333.8 | 407.2 | 709.1 | 637.5 | 618.1 | 597.6 | 324 | 462.9
1265 | 1107 | 333.2 | 399 | 712.5 | 633.7 | 616.4 | 594.2 | 324 | 462.4
1266 | 1108 | 332.7 | 390.5 | 719.7 | 631.2 | 614.9 | 590.8 | 323.9 | 461.9
1267 | 1109 | 332 | 382.8 | 723.5 | 627.8 | 613.3 | 587.8 | 323.8 | 461.4
1268 | 1110 | 331.3 | 376.4 | 726.1 | 622 | 611.1 | 584.6 | 323.7 | 460.9
1269 | 1111 | 330.8 | 370 | 723.8 | 620.8 | 610.2 | 581.3 | 323.7 | 460.5
1270 | 1112 | 330.3 | 364.4 | 721 | 619.7 | 609.4 | 578.1 | 323.6 | 460
1271 | 1113 | 329.6 | 359.4 | 722.6 | 616.8 | 608.4 | 575.2 | 323.5 | 459.6
1272 | 1114 | 329.1 | 354.9 | 726 | 611.2 | 607.5 | 572 | 323.4 | 459.1
1273 | 1115 | 328.6 | 350.8 | 727.3 | 607 | 606.7 | 569 | 323.3 | 458.6
1274 | 1116 | 328 | 348.3 | 730.1 | 604 | 604.3 | 566 | 323.2 | 458.1
1275 | 1117 | 327.5 | 345.8 | 730.4 | 600.5 | 600.6 | 563.1 | 323.1 | 457.6
1276 | 1118 | 327 | 342.9 | 731.5 | 595.8 | 598.3 | 560.3 | 323 | 457.1
1277 | 1119 | 326.4 | 340.5 | 732.2 | 593 | 596.1 | 557.5 | 323 | 456.7
1278 | 1120 | 325.9 | 338.3 | 732.2 | 592.1 | 594.9 | 554.5 | 322.9 | 456.3
1279 | 1121 | 325.3 | 337.9 | 730.1 | 590.1 | 594.2 | 551.3 | 322.8 | 455.8
1280 | 1122 | 324.7 | 338.6 | 725.1 | 586.8 | 593.8 | 547.9 | 322.8 | 455.3
1281 | 1123 | 324.3 | 339 | 722 | 583.7 | 592.6 | 544.8 | 322.7 | 454.8
1282 | 1124 | 323.8 | 338.1 | 720.9 | 581.4 | 591.5 | 541.9 | 322.6 | 454.3
1283 | 1125 | 323.2 | 336.7 | 719 | 578.3 | 590.8 | 539.3 | 322.5 | 453.8
1284 | 1126 | 322.5 | 334.8 | 716.2 | 575.4 | 590.6 | 536.8 | 322.4 | 453.3
1285 | 1127 | 322 | 332.3 | 711.6 | 571.6 | 590.3 | 534.2 | 322.3 | 452.8
1286 | 1128 | 321.5 | 329.5 | 708.7 | 571 | 590.2 | 531.7 | 322.3 | 452.3
1287 | 1129 | 320.9 | 327.2 | 707.6 | 570.7 | 589.6 | 529.6 | 322.2 | 451.8
1288 | 1130 | 320.4 | 326 | 704.4 | 563.6 | 588.4 | 527.3 | 322.1 | 451.2
1289 | 1131 | 319.8 | 324.1 | 704.7 | 549.6 | 587.2 | 524.8 | 322 | 450.7
1290 | 1132 | 319.3 | 322.3 | 709.4 | 540.1 | 585.7 | 522.8 | 321.8 | 450.2
1291 | 1133 | 318.7 | 321.1 | 706.5 | 530.6 | 584.5 | 520.4 | 321.7 | 449.7
1292 | 1134 | 318 | 319.6 | 703.4 | 522.6 | 583.4 | 518.4 | 321.6 | 449.2
1293 | 1135 | 317.5 | 318.9 | 699.7 | 518.3 | 582.5 | 516.6 | 321.4 | 448.6
1294 | 1136 | 317 | 318.3 | 695 | 508.9 | 582.3 | 514.7 | 321.3 | 448
1295 | 1137 | 316.5 | 316 | 692.3 | 504.3 | 582.4 | 512.2 | 321.2 | 447.5
1296 | 1138 | 316 | 314 | 690.6 | 499.2 | 581.4 | 509.7 | 321 | 447
1297 | 1139 | 315.5 | 312.3 | 687.5 | 492.9 | 579.2 | 507.2 | 320.9 | 446.5
1298 | 1140 | 314.9 | 309.7 | 683 | 490.9 | 577.4 | 504.7 | 320.7 | 446
1299 | 1141 | 314.4 | 306.8 | 678.2 | 488.3 | 575.4 | 501.8 | 320.6 | 445.4
1300 | 1142 | 314 | 303 | 672 | 481.8 | 573.2 | 499.3 | 320.5 | 444.8
1301 | 1143 | 313.5 | 299.4 | 665.7 | 474.5 | 571.5 | 497 | 320.3 | 444.2
1302 | 1144 | 313.1 | 295.5 | 661.9 | 472.2 | 571 | 495.2 | 320.2 | 443.6
1303 | 1145 | 312.7 | 291.8 | 658.5 | 467.1 | 570.8 | 493.7 | 320 | 443
1304 | 1146 | 312.3 | 288.1 | 655.6 | 463.2 | 570.8 | 492.2 | 319.9 | 442.5
1305 | 1147 | 311.8 | 284.3 | 652.9 | 460.4 | 570.2 | 490.5 | 319.7 | 441.9
1306 | 1148 | 311.3 | 280.5 | 649.2 | 455 | 569.5 | 488.7 | 319.6 | 441.4
1307 | 1149 | 310.8 | 277.3 | 646.2 | 447.5 | 568.7 | 486 | 319.5 | 440.8
1308 | 1150 | 310.2 | 274.1 | 642.6 | 438.2 | 567.5 | 483.6 | 319.4 | 440.3
1309 | 1151 | 309.7 | 271.1 | 639.4 | 430.3 | 566 | 481.7 | 319.2 | 439.7
1310 | 1152 | 309.1 | 268.8 | 636.4 | 427.1 | 563.4 | 480 | 319.1 | 439
1311 | 1153 | 308.5 | 265.8 | 631.9 | 418.5 | 560.5 | 478.3 | 319 | 438.4
1312 | 1154 | 308 | 263.3 | 629 | 412.1 | 558.5 | 476.2 | 318.8 | 437.8
1313 | 1155 | 307.5 | 260.9 | 627.3 | 407.2 | 557.8 | 474.4 | 318.7 | 437.2
1314 | 1156 | 307.1 | 259.6 | 625.2 | 405.5 | 557.7 | 472.6 | 318.5 | 436.7
1315 | 1157 | 306.6 | 258 | 623.2 | 405.6 | 557.3 | 470.7 | 318.4 | 436.1
1316 | 1158 | 306.1 | 256.7 | 621 | 402.7 | 556.3 | 468.9 | 318.2 | 435.6
1317 | 1159 | 305.6 | 256 | 618.6 | 398.5 | 554.9 | 466.6 | 318 | 435
1318 | 1160 | 304.9 | 254.9 | 615.8 | 395.3 | 552.6 | 464.6 | 317.9 | 434.5
1319 | 1161 | 304.3 | 254 | 613.3 | 390.9 | 550.4 | 462.5 | 317.7 | 433.9
1320 | 1162 | 303.8 | 253.5 | 610.6 | 388.1 | 549.7 | 460.2 | 317.5 | 433.2
1321 | 1163 | 303.3 | 252.3 | 608.1 | 385.4 | 549.5 | 457.7 | 317.3 | 432.6
1322 | 1164 | 302.8 | 250.3 | 605.1 | 384.2 | 548.8 | 455 | 317.1 | 432
1323 | 1165 | 302.3 | 248.8 | 602.2 | 382.8 | 547.4 | 452.7 | 316.9 | 431.4
1324 | 1166 | 301.8 | 247.3 | 599.8 | 382 | 545.4 | 450.6 | 316.7 | 430.7
1325 | 1167 | 301.4 | 246.7 | 597.7 | 379 | 542.9 | 448.3 | 316.5 | 430
1326 | 1168 | 300.9 | 247.3 | 595.4 | 376.4 | 540 | 445.7 | 316.3 | 429.3
1327 | 1169 | 300.5 | 248.6 | 592.9 | 374.6 | 537.8 | 443.5 | 316.1 | 428.6
1328 | 1170 | 300 | 248.9 | 590.5 | 373.5 | 535.9 | 441.2 | 315.9 | 427.9
1329 | 1171 | 299.5 | 248.3 | 587.9 | 371 | 535.4 | 438.9 | 315.6 | 427.3
1330 | 1172 | 299 | 246.6 | 585.1 | 372.2 | 535 | 436.4 | 315.4 | 426.7
1331 | 1173 | 298.5 | 246.3 | 582.7 | 368.8 | 533.6 | 433.5 | 315.1 | 426.1
1332 | 1174 | 298 | 245.6 | 580.2 | 364 | 532.1 | 430.5 | 314.9 | 425.4
1333 | 1175 | 297.5 | 245.1 | 577.3 | 361.8 | 530.8 | 427.7 | 314.7 | 424.8
1334 | 1176 | 297 | 244.3 | 574.4 | 363.5 | 529.3 | 425.1 | 314.4 | 424.2
1335 | 1177 | 296.4 | 242.6 | 571.8 | 366.2 | 526.9 | 422.6 | 314.2 | 423.5
1336 | 1178 | 295.9 | 240.9 | 569 | 367 | 524.5 | 420.1 | 314 | 422.9
1337 | 1179 | 295.4 | 239.1 | 566.5 | 363.2 | 522.2 | 417.7 | 313.7 | 422.3
1338 | 1180 | 294.8 | 237.4 | 563.8 | 359.8 | 520.1 | 415.5 | 313.5 | 421.5
1339 | 1181 | 294.3 | 236.3 | 561.2 | 356.1 | 518.5 | 413.2 | 313.3 | 420.8
1340 | 1182 | 293.8 | 235.2 | 558.8 | 353.4 | 518 | 411.3 | 313.1 | 420.1
1341 | 1183 | 293.4 | 233.6 | 556.5 | 350.8 | 517.8 | 409.5 | 312.9 | 419.4
1342 | 1184 | 292.9 | 232.2 | 554 | 348.7 | 517.2 | 407.7 | 312.7 | 418.7
1343 | 1185 | 292.3 | 230.8 | 551.5 | 346.1 | 516.1 | 405.9 | 312.5 | 418.1
1344 | 1186 | 291.8 | 229.6 | 549 | 343.7 | 514.3 | 403.8 | 312.3 | 417.5
1345 | 1187 | 291.4 | 228.1 | 546.4 | 341.1 | 512.6 | 402.1 | 312.1 | 416.9
1346 | 1188 | 291 | 226.3 | 543.1 | 338.3 | 510.9 | 400.3 | 311.9 | 416.3
1347 | 1189 | 290.7 | 225.1 | 540.3 | 335.4 | 509.1 | 398.5 | 311.7 | 415.7
1348 | 1190 | 290.3 | 223.5 | 537.8 | 331.8 | 507.4 | 396.8 | 311.5 | 415
1349 | 1191 | 289.9 | 222.1 | 535.2 | 329.2 | 505.6 | 395.2 | 311.3 | 414.3
1350 | 1192 | 289.5 | 220.7 | 532.5 | 327.6 | 504 | 393.7 | 311.1 | 413.6
1351 | 1193 | 289 | 218.9 | 529.5 | 325.2 | 502.6 | 392.2 | 310.9 | 412.9
1352 | 1194 | 288.6 | 217.5 | 527.1 | 323.5 | 501.1 | 390.6 | 310.7 | 412.2
1353 | 1195 | 288.1 | 215.8 | 524.6 | 319.5 | 499.9 | 389 | 310.5 | 411.5
1354 | 1196 | 287.7 | 214.1 | 522.2 | 317.9 | 499.1 | 386.9 | 310.3 | 410.8
1355 | 1197 | 287.3 | 212.9 | 520 | 315.6 | 498.4 | 385.2 | 310.1 | 410.2
1356 | 1198 | 286.9 | 211.5 | 517.1 | 315.3 | 497.7 | 383.6 | 310 | 409.5
1357 | 1199 | 286.4 | 210.4 | 514.7 | 314.9 | 497.1 | 382.1 | 309.8 | 408.8
1358 | 1200 | 285.8 | 209.2 | 512 | 314.8 | 496 | 380.8 | 309.6 | 408.2
1359 | 1201 | 285.3 | 208.2 | 509.3 | 314.6 | 495.3 | 379.6 | 309.4 | 407.5
1360 | 1202 | 284.7 | 207.5 | 506.7 | 313.7 | 494 | 378.1 | 309.2 | 406.9
1361 | 1203 | 284.4 | 207.3 | 504.2 | 312.5 | 491.6 | 376.7 | 308.9 | 406.3
1362 | 1204 | 284 | 206.9 | 501.7 | 310.2 | 489.2 | 375.4 | 308.7 | 405.7
1363 | 1205 | 283.6 | 206.9 | 499.1 | 307.9 | 486.9 | 374 | 308.5 | 405.1
1364 | 1206 | 283.2 | 206.2 | 495.9 | 303.2 | 485 | 372.5 | 308.2 | 404.4
1365 | 1207 | 282.8 | 205 | 493.2 | 299.9 | 483.7 | 370.6 | 308 | 403.8
1366 | 1208 | 282.4 | 204.1 | 490.6 | 297.5 | 482.8 | 368.8 | 307.7 | 403.1
1367 | 1209 | 282 | 203.3 | 487.2 | 295.7 | 481.5 | 367.4 | 307.5 | 402.5
1368 | 1210 | 281.6 | 202.5 | 483.9 | 294.5 | 479.8 | 365.9 | 307.3 | 401.8
1369 | 1211 | 281.1 | 202 | 480.6 | 293.7 | 478.3 | 364.4 | 307.1 | 401.1
1370 | 1212 | 280.7 | 201.7 | 476.9 | 290.9 | 476.9 | 362.6 | 306.8 | 400.5
1371 | 1213 | 280.3 | 200.6 | 473.2 | 287.7 | 475.1 | 361.3 | 306.6 | 399.9
1372 | 1214 | 279.8 | 199.6 | 469.1 | 284.9 | 473.5 | 360.2 | 306.4 | 399.3
1373 | 1215 | 279.2 | 199.4 | 465.3 | 281.6 | 472.3 | 359 | 306.2 | 398.6
1374 | 1216 | 278.7 | 199.1 | 461.4 | 280.2 | 470.9 | 357.7 | 306 | 398
1375 | 1217 | 278.3 | 198.3 | 457.9 | 278 | 469.2 | 356.5 | 305.8 | 397.4
1376 | 1218 | 277.9 | 197.2 | 453.6 | 275.7 | 467.8 | 355.3 | 305.5 | 396.8
1377 | 1219 | 277.4 | 196.1 | 449.6 | 273.8 | 466.2 | 354 | 305.3 | 396.1
1378 | 1220 | 277 | 195.3 | 445.9 | 272.9 | 464.4 | 352.4 | 305.1 | 395.5
1379 | 1221 | 276.6 | 194.4 | 442.2 | 271 | 461.9 | 350.7 | 304.8 | 394.9
1380 | 1222 | 276.2 | 193.7 | 438.7 | 269.6 | 458.4 | 349.2 | 304.6 | 394.2
1381 | 1223 | 275.8 | 193.3 | 435 | 268.5 | 454.9 | 347.7 | 304.3 | 393.5
1382 | 1224 | 275.4 | 192.8 | 431.6 | 268.9 | 452.7 | 346.3 | 304.1 | 392.9
1383 | 1225 | 275 | 192.5 | 429.1 | 268.6 | 451.6 | 345.1 | 303.9 | 392.2
1384 | 1226 | 274.5 | 191.9 | 426.6 | 266.7 | 451.2 | 343.9 | 303.6 | 391.7
1385 | 1227 | 274.1 | 191 | 424.5 | 266.7 | 451.1 | 343 | 303.4 | 391.1
1386 | 1228 | 273.6 | 189.9 | 422.7 | 267.5 | 450.8 | 341.8 | 303.1 | 390.5
1387 | 1229 | 273.2 | 188.9 | 420.5 | 266.7 | 450.1 | 340.6 | 302.8 | 389.9
1388 | 1230 | 272.8 | 187.8 | 417.8 | 266 | 449 | 339.4 | 302.6 | 389.3
1389 | 1231 | 272.3 | 187.1 | 415.6 | 263.9 | 447.2 | 338.2 | 302.3 | 388.7
1390 | 1232 | 271.8 | 186.9 | 413.3 | 261.1 | 445.1 | 337.2 | 302 | 388
1391 | 1233 | 271.4 | 186.2 | 411.2 | 258.3 | 443.2 | 335.7 | 301.7 | 387.5
1392 | 1234 | 270.9 | 185.7 | 409.3 | 256.8 | 441.8 | 334.1 | 301.5 | 386.9
1393 | 1235 | 270.5 | 185.4 | 407.5 | 255.1 | 440.3 | 332.7 | 301.2 | 386.3
1394 | 1236 | 270.1 | 184.2 | 406.1 | 254 | 439.5 | 331.2 | 300.9 | 385.6
1395 | 1237 | 269.7 | 183.5 | 404.3 | 253.6 | 438.9 | 329.6 | 300.6 | 385
1396 | 1238 | 269.3 | 182.8 | 402.4 | 251.6 | 438.1 | 328 | 300.4 | 384.3
1397 | 1239 | 268.9 | 182.1 | 401.1 | 250.1 | 437.1 | 326.6 | 300.1 | 383.7
1398 | 1240 | 268.5 | 181.1 | 399.2 | 248.5 | 435.4 | 325.4 | 299.8 | 383.2
1399 | 1241 | 268.1 | 179.8 | 397.4 | 247.6 | 434 | 324 | 299.5 | 382.5
1400 | 1242 | 267.7 | 178.8 | 395.2 | 247.6 | 433.1 | 322.4 | 299.2 | 382
1401 | 1243 | 267.3 | 178.7 | 393.2 | 247.1 | 432.2 | 321.3 | 298.9 | 381.4
1402 | 1244 | 266.8 | 178.4 | 392.2 | 245.4 | 431.6 | 320 | 298.7 | 380.8
1403 | 1245 | 266.4 | 177.6 | 391.1 | 245 | 430.7 | 318.4 | 298.4 | 380.2
1404 | 1246 | 266 | 176.6 | 389.6 | 243.6 | 429.5 | 316.8 | 298.1 | 379.6
1405 | 1247 | 265.6 | 176.1 | 387.6 | 242.1 | 428.5 | 316 | 297.8 | 379
1406 | 1248 | 265.2 | 176 | 385.2 | 241.9 | 426.9 | 314.8 | 297.5 | 378.4
1407 | 1249 | 264.8 | 175.4 | 383.3 | 240.4 | 424.3 | 313.5 | 297.2 | 377.9
1408 | 1250 | 264.3 | 174.5 | 382.5 | 239.1 | 422.2 | 312 | 296.9 | 377.3
1409 | 1251 | 263.9 | 173.8 | 381.6 | 239.2 | 421.2 | 310.8 | 296.6 | 376.7
1410 | 1252 | 263.6 | 173.5 | 379.7 | 239.6 | 420.4 | 309.8 | 296.3 | 376.2
1411 | 1253 | 263.2 | 173.3 | 377.7 | 239.8 | 419.4 | 308.6 | 296 | 375.6
1412 | 1254 | 262.9 | 172.8 | 376.7 | 239 | 417.9 | 307.3 | 295.7 | 374.9
1413 | 1255 | 262.6 | 172 | 375.8 | 237.4 | 416.3 | 306.5 | 295.4 | 374.4
1414 | 1256 | 262.2 | 171 | 375.1 | 237.2 | 415.1 | 306.2 | 295.1 | 373.8
1415 | 1257 | 261.8 | 169.9 | 374 | 236.5 | 414.3 | 305.5 | 294.8 | 373.2
1416 | 1258 | 261.4 | 169.2 | 372.8 | 235.8 | 413.4 | 304.7 | 294.5 | 372.6
1417 | 1259 | 261.1 | 168.3 | 371.9 | 234.7 | 412.3 | 304.2 | 294.2 | 372
1418 | 1260 | 260.7 | 167.3 | 370.6 | 233.4 | 411 | 303.3 | 293.8 | 371.4
1419 | 1261 | 260.4 | 166.6 | 369.3 | 232.5 | 409.6 | 303 | 293.5 | 370.8
1420 | 1262 | 260 | 165.6 | 368 | 231.6 | 408.2 | 301.9 | 293.2 | 370.3
1421 | 1263 | 259.6 | 164.4 | 366.8 | 231.3 | 407.2 | 300.9 | 292.8 | 369.7
1422 | 1264 | 259.2 | 164.2 | 365.4 | 231.8 | 406 | 300.2 | 292.5 | 369.2
1423 | 1265 | 258.8 | 163.8 | 363.6 | 231.1 | 404.6 | 299.3 | 292.1 | 368.6
1424 | 1266 | 258.3 | 162.9 | 362.5 | 230.5 | 403.5 | 298.2 | 291.8 | 368
1425 | 1267 | 257.8 | 162.1 | 361.4 | 229.9 | 402.5 | 297.3 | 291.4 | 367.4
1426 | 1268 | 257.4 | 161.3 | 360.3 | 230.5 | 401.4 | 296.6 | 291.1 | 366.8
1427 | 1269 | 257 | 160.7 | 359.1 | 230.1 | 400.1 | 295.6 | 290.7 | 366.3
1428 | 1270 | 256.6 | 160 | 358.1 | 229.1 | 398.8 | 294.8 | 290.4 | 365.8
1429 | 1271 | 256.1 | 159.3 | 356.8 | 228 | 397.5 | 294.1 | 290 | 365.2
1430 | 1272 | 255.7 | 158.5 | 355.6 | 226 | 396.1 | 293.3 | 289.7 | 364.5
1431 | 1273 | 255.3 | 157.9 | 354.3 | 225.1 | 394.6 | 292.6 | 289.3 | 364
1432 | 1274 | 254.9 | 158.1 | 353 | 225.7 | 393.5 | 292 | 288.9 | 363.4
1433 | 1275 | 254.6 | 158.4 | 351.9 | 226.3 | 392.8 | 291.9 | 288.6 | 362.8
1434 | 1276 | 254.1 | 158.5 | 350.7 | 226.4 | 392.9 | 291.4 | 288.2 | 362.2
1435 | 1277 | 253.7 | 158.5 | 349.7 | 226.3 | 393.6 | 290.6 | 287.7 | 361.6
1436 | 1278 | 253.1 | 158.2 | 348.4 | 226 | 394.2 | 290 | 287.3 | 361
1437 | 1279 | 252.7 | 158.1 | 347.1 | 225.8 | 394.7 | 289.5 | 286.9 | 360.4
1438 | 1280 | 252.3 | 158.1 | 346.3 | 224.6 | 395.6 | 289 | 286.5 | 359.7
1439 | 1281 | 252 | 158 | 344.8 | 224.2 | 396.2 | 288.1 | 286 | 359.2
1440 | 1282 | 251.5 | 158.5 | 343.3 | 224 | 396.3 | 287.3 | 285.6 | 358.6
1441 | 1283 | 251.1 | 159.5 | 342.5 | 224.3 | 396.4 | 286.9 | 285.1 | 358
1442 | 1284 | 250.8 | 159.9 | 341.6 | 224.3 | 396.2 | 286.3 | 284.7 | 357.4
1443 | 1285 | 250.5 | 160.4 | 340.4 | 225.7 | 395.2 | 285.5 | 284.2 | 356.9
1444 | 1286 | 250.1 | 160.8 | 338.9 | 227.1 | 392.9 | 284.4 | 283.7 | 356.3
1445 | 1287 | 249.7 | 160.9 | 337.8 | 226.3 | 390.1 | 283.7 | 283.3 | 355.6
1446 | 1288 | 249.3 | 160.8 | 337 | 226.2 | 387.3 | 283 | 282.8 | 355.1
1447 | 1289 | 249 | 160.5 | 336.1 | 225.7 | 384.1 | 282.7 | 282.4 | 354.6
1448 | 1290 | 248.7 | 160.2 | 335.1 | 225.2 | 381.3 | 281.9 | 281.9 | 354
1449 | 1291 | 248.3 | 160.2 | 334.2 | 225.5 | 379.6 | 280.8 | 281.5 | 353.4
1450 | 1292 | 247.7 | 160 | 333.3 | 225.7 | 378.4 | 279.6 | 281 | 352.8
1451 | 1293 | 247.4 | 160 | 332.3 | 224.9 | 377.9 | 277.7 | 280.6 | 352.2
1452 | 1294 | 247.1 | 159.6 | 331.2 | 224.8 | 377.3 | 275.9 | 280.1 | 351.7
1453 | 1295 | 246.8 | 159.6 | 330.5 | 225.4 | 377 | 274.4 | 279.7 | 351.2
1454 | 1296 | 246.4 | 159.4 | 329.6 | 224 | 376.9 | 273.4 | 279.2 | 350.6
1455 | 1297 | 246.1 | 159.2 | 328.3 | 222.7 | 376.9 | 272.9 | 278.7 | 350
1456 | 1298 | 245.7 | 159 | 326.7 | 222.7 | 376.7 | 272.5 | 278.2 | 349.5
1457 | 1299 | 245.3 | 158.7 | 326 | 223.1 | 376.1 | 272.1 | 277.6 | 349
1458 | 1300 | 245 | 158.3 | 325.3 | 223.5 | 375.5 | 271.6 | 277.1 | 348.4
1459 | 1301 | 244.6 | 158.4 | 324.5 | 224.2 | 374.5 | 270.6 | 276.6 | 347.8
1460 | 1302 | 244.3 | 158.4 | 323.7 | 224.7 | 372.7 | 269.5 | 276.1 | 347.2
1461 | 1303 | 244 | 157.9 | 322.9 | 224.9 | 370.3 | 268.8 | 275.6 | 346.7
1462 | 1304 | 243.7 | 157.8 | 322.2 | 225 | 368.3 | 267.7 | 275.1 | 346.1
1463 | 1305 | 243.3 | 157.9 | 321.3 | 223.2 | 366.2 | 266.2 | 274.6 | 345.6
1464 | 1306 | 242.9 | 157.9 | 320.3 | 221.1 | 363.6 | 264.4 | 274.1 | 345
1465 | 1307 | 242.5 | 157.4 | 319.4 | 219.7 | 361.3 | 263.4 | 273.6 | 344.5
1466 | 1308 | 242.1 | 156.8 | 318.5 | 218.5 | 358.9 | 263 | 273.2 | 344
1467 | 1309 | 241.7 | 156.7 | 317.2 | 216.4 | 355.9 | 262.6 | 272.7 | 343.4
1468 | 1310 | 241.3 | 156.5 | 316.4 | 214.1 | 353.1 | 261.8 | 272.2 | 342.9
1469 | 1311 | 240.9 | 155.9 | 315.7 | 211.9 | 350.5 | 261.1 | 271.8 | 342.3
1470 | 1312 | 240.5 | 155 | 314.8 | 210.3 | 347.9 | 260.3 | 271.3 | 341.7
1471 | 1313 | 240.2 | 154.2 | 313.3 | 208.4 | 345.7 | 259.4 | 270.9 | 341.2
1472 | 1314 | 239.8 | 152.9 | 312.3 | 206.5 | 343.7 | 258.2 | 270.5 | 340.7
1473 | 1315 | 239.3 | 151.6 | 311.5 | 205.5 | 341.5 | 257 | 270 | 340.1
1474 | 1316 | 239 | 150.5 | 310.7 | 203.8 | 339.3 | 256.1 | 269.6 | 339.6
1475 | 1317 | 238.6 | 149.2 | 310 | 201.5 | 337.7 | 254.8 | 269.2 | 339.1
1476 | 1318 | 238.3 | 148 | 309.3 | 199.6 | 336.1 | 253.1 | 268.8 | 338.5
1477 | 1319 | 238 | 147.1 | 307.9 | 197.2 | 334.7 | 251.8 | 268.4 | 337.9
1478 | 1320 | 237.6 | 145.7 | 306.9 | 195.4 | 333.6 | 250.6 | 268 | 337.4
1479 | 1321 | 237.2 | 144.5 | 303.8 | 194.8 | 332.7 | 249.7 | 267.6 | 336.8
1480 | 1322 | 236.8 | 143.5 | 300.8 | 194.1 | 331.7 | 249.1 | 267.1 | 336.2
1481 | 1323 | 236.5 | 142.4 | 297.2 | 193.6 | 329.9 | 248.4 | 266.7 | 335.7
1482 | 1324 | 236.2 | 141.6 | 295.6 | 192.8 | 328.1 | 247.6 | 266.3 | 335.2
1483 | 1325 | 235.9 | 140.9 | 293.8 | 191.4 | 326.5 | 247 | 265.9 | 334.6
1484 | 1326 | 235.6 | 140.1 | 291.4 | 191 | 325.3 | 246.1 | 265.4 | 334.1
1485 | 1327 | 235.3 | 139.5 | 290 | 190.6 | 324.2 | 245.1 | 265 | 333.5
1486 | 1328 | 235 | 138.7 | 288.1 | 189.3 | 322.5 | 244.3 | 264.5 | 333
1487 | 1329 | 234.7 | 138.3 | 285.8 | 186.8 | 320.2 | 243.5 | 264.1 | 332.5
1488 | 1330 | 234.3 | 137.6 | 283.7 | 184.2 | 318.2 | 242.7 | 263.7 | 331.9
1489 | 1331 | 233.9 | 136.8 | 281.3 | 181.9 | 316.6 | 242.2 | 263.2 | 331.4
1490 | 1332 | 233.6 | 135.9 | 280.4 | 181.9 | 315.3 | 241.6 | 262.7 | 330.9
1491 | 1333 | 233.2 | 135.1 | 279.5 | 181 | 314 | 240.7 | 262.3 | 330.4
1492 | 1334 | 232.8 | 134 | 278.4 | 180.4 | 313 | 239.9 | 261.8 | 329.8
1493 | 1335 | 232.4 | 133.2 | 275.6 | 179.4 | 312.3 | 239.3 | 261.4 | 329.4
1494 | 1336 | 232.1 | 132.2 | 272.2 | 178.6 | 311.3 | 238.8 | 260.9 | 328.9
1495 | 1337 | 231.7 | 131.7 | 269.5 | 176.3 | 309.4 | 238.1 | 260.4 | 328.3
1496 | 1338 | 231.3 | 131 | 267.3 | 173.3 | 307.1 | 237.6 | 259.9 | 327.7
1497 | 1339 | 230.9 | 130.4 | 265.9 | 170.2 | 304.8 | 237.2 | 259.5 | 327.2
1498 | 1340 | 230.5 | 129.8 | 264 | 168.5 | 302.5 | 236.7 | 259 | 326.7
1499 | 1341 | 230.1 | 129.4 | 262.3 | 166 | 300.4 | 235.9 | 258.5 | 326.3
1500 | 1342 | 229.7 | 129.3 | 261.3 | 163.2 | 298.2 | 235 | 258 | 325.7
1501 | 1343 | 229.5 | 128.7 | 260.8 | 160.5 | 296.3 | 233.9 | 257.6 | 325.1
1502 | 1344 | 229.2 | 128.3 | 260.2 | 158.5 | 294.7 | 232.9 | 257.1 | 324.5
1503 | 1345 | 228.9 | 127.9 | 259.8 | 156.4 | 293.5 | 232.1 | 256.7 | 324
1504 | 1346 | 228.6 | 127.5 | 259.5 | 154.4 | 292.3 | 231.3 | 256.2 | 323.5
1505 | 1347 | 228.2 | 127 | 259.3 | 154.2 | 291 | 230.3 | 255.8 | 322.9
1506 | 1348 | 227.8 | 126.5 | 258.2 | 153.6 | 289.3 | 229.3 | 255.3 | 322.4
1507 | 1349 | 227.5 | 126 | 256.3 | 153 | 287.3 | 228.6 | 254.9 | 321.9
1508 | 1350 | 227.2 | 125.7 | 255.9 | 153.5 | 285.3 | 228.1 | 254.4 | 321.4
1509 | 1351 | 226.9 | 125 | 255.4 | 153.3 | 283.2 | 227.4 | 253.9 | 320.9
1510 | 1352 | 226.5 | 124.7 | 254.9 | 152.5 | 281.4 | 226.5 | 253.5 | 320.4
1511 | 1353 | 226.2 | 124.6 | 254.4 | 151.9 | 279.7 | 225.8 | 253 | 319.9
1512 | 1354 | 225.9 | 124.3 | 253.5 | 151.6 | 277.7 | 225 | 252.6 | 319.4
1513 | 1355 | 225.6 | 124.1 | 253 | 150.8 | 275.6 | 224.1 | 252.1 | 318.9
1514 | 1356 | 225.3 | 124.3 | 252.3 | 149.8 | 273.7 | 223 | 251.7 | 318.4
1515 | 1357 | 225 | 125.1 | 252.5 | 150 | 271.4 | 221.8 | 251.2 | 317.8
1516 | 1358 | 224.6 | 125.8 | 252.7 | 149.4 | 268.9 | 220.5 | 250.7 | 317.3
1517 | 1359 | 224.4 | 125.9 | 252.4 | 149.1 | 266.5 | 219.3 | 250.2 | 316.8
1518 | 1360 | 224.1 | 125.3 | 250.5 | 147.4 | 264.7 | 218.7 | 249.8 | 316.4
1519 | 1361 | 223.8 | 124.8 | 248.7 | 146.1 | 263.1 | 217.8 | 249.3 | 316
1520 | 1362 | 223.5 | 124.4 | 247.1 | 144 | 261.4 | 217 | 248.8 | 315.5
1521 | 1363 | 223.2 | 123.8 | 245.8 | 142.5 | 259.9 | 216.2 | 248.3 | 315
1522 | 1364 | 223 | 123.5 | 244.8 | 141.4 | 258.8 | 215.5 | 247.9 | 314.4
1523 | 1365 | 222.6 | 123.1 | 243.7 | 140.2 | 257.9 | 215 | 247.4 | 314
1524 | 1366 | 222.3 | 122.6 | 242.7 | 139.7 | 257.5 | 214.8 | 246.9 | 313.4
1525 | 1367 | 221.9 | 122.3 | 242.7 | 138.6 | 257.3 | 214.1 | 246.4 | 313
1526 | 1368 | 221.6 | 121.9 | 242.8 | 139 | 257.3 | 213.3 | 245.9 | 312.5
1527 | 1369 | 221.3 | 121.6 | 243 | 139.4 | 257.3 | 212.7 | 245.4 | 311.9
1528 | 1370 | 220.9 | 121.5 | 243 | 139.4 | 257.7 | 212.1 | 244.9 | 311.4
1529 | 1371 | 220.6 | 121.1 | 242.5 | 138.5 | 257.9 | 211.2 | 244.4 | 310.9
1530 | 1372 | 220.3 | 120.6 | 242 | 137.6 | 257.7 | 210.3 | 243.9 | 310.5
1531 | 1373 | 220 | 120.1 | 241.8 | 137.5 | 257.7 | 209.6 | 243.3 | 310
1532 | 1374 | 219.6 | 119.7 | 241.4 | 137.3 | 257.9 | 208.9 | 242.8 | 309.5
1533 | 1375 | 219.2 | 120 | 240.8 | 136 | 258.2 | 208.2 | 242.3 | 309
1534 | 1376 | 218.9 | 120.1 | 240.3 | 135.2 | 258.4 | 207.8 | 241.7 | 308.5
1535 | 1377 | 218.5 | 120.1 | 239.8 | 134.6 | 258.8 | 207.6 | 241.2 | 308
1536 | 1378 | 218.2 | 119.9 | 239.3 | 134.3 | 258.5 | 207.7 | 240.7 | 307.4
1537 | 1379 | 217.9 | 119.8 | 237.7 | 133.4 | 256.9 | 207.3 | 240.2 | 307
1538 | 1380 | 217.5 | 119.2 | 236.9 | 132.6 | 255.3 | 206.7 | 239.7 | 306.5
1539 | 1381 | 217.2 | 118.7 | 236.4 | 132.7 | 253.8 | 206.2 | 239.2 | 306
1540 | 1382 | 216.9 | 118.2 | 234.8 | 131.8 | 252.1 | 205.6 | 238.6 | 305.5
1541 | 1383 | 216.6 | 117.6 | 233 | 131.5 | 250.4 | 204.8 | 238.1 | 305
1542 | 1384 | 216.2 | 116.8 | 231.7 | 130.6 | 248.8 | 204.1 | 237.6 | 304.4
1543 | 1385 | 216 | 116.3 | 231.1 | 130.2 | 247.1 | 203.5 | 237.1 | 304
1544 | 1386 | 215.7 | 115.8 | 230 | 129.8 | 245.5 | 202.8 | 236.6 | 303.5
1545 | 1387 | 215.3 | 115 | 229.3 | 129.4 | 243.8 | 202.3 | 236.1 | 303.1
1546 | 1388 | 214.8 | 114.7 | 228.5 | 129.1 | 242.3 | 201.8 | 235.6 | 302.6
1547 | 1389 | 214.4 | 114.3 | 227.9 | 129.3 | 240.8 | 201.4 | 235.1 | 302.1
1548 | 1390 | 214.1 | 113.8 | 225.7 | 128.5 | 239.4 | 200.6 | 234.6 | 301.7
1549 | 1391 | 213.9 | 113 | 223.6 | 128.2 | 237.9 | 199.8 | 234.1 | 301.2
1550 | 1392 | 213.6 | 112.5 | 222 | 127.5 | 236.3 | 199.1 | 233.6 | 300.7
1551 | 1393 | 213.3 | 112 | 221.4 | 126.9 | 234.8 | 198.1 | 233.1 | 300.2
1552 | 1394 | 213 | 111.6 | 220.3 | 126.6 | 233.4 | 197.1 | 232.6 | 299.7
1553 | 1395 | 212.6 | 111 | 219.3 | 126.1 | 232 | 196.5 | 232.1 | 299.2
1554 | 1396 | 212.4 | 110.5 | 218.6 | 125.9 | 230.5 | 196 | 231.6 | 298.8
1555 | 1397 | 212.1 | 110.1 | 217.6 | 125.7 | 229.2 | 195.7 | 231.1 | 298.3
1556 | 1398 | 211.8 | 110 | 216.2 | 125 | 227.8 | 194.8 | 230.6 | 297.9
1557 | 1399 | 211.5 | 109.8 | 214.6 | 124.3 | 226.6 | 193.8 | 230.2 | 297.5
1558 | 1400 | 211.2 | 109.2 | 213.1 | 124.5 | 225.3 | 192.9 | 229.7 | 297
1559 | 1401 | 210.8 | 108.8 | 212.7 | 124.8 | 224.1 | 192.6 | 229.2 | 296.5
1560 | 1402 | 210.5 | 108.4 | 212.3 | 124.5 | 222.7 | 192.2 | 228.8 | 296
1561 | 1403 | 210.3 | 108.4 | 212.8 | 124.5 | 221.5 | 191.8 | 228.3 | 295.5
1562 | 1404 | 209.9 | 108.1 | 213.2 | 124.6 | 220.8 | 191.4 | 227.8 | 295
1563 | 1405 | 209.6 | 108.5 | 213.7 | 124.6 | 220.7 | 191 | 227.3 | 294.5
1564 | 1406 | 209.4 | 108.7 | 213.8 | 124.7 | 220.9 | 190.6 | 226.8 | 294.1
1565 | 1407 | 209.1 | 108.4 | 214 | 125.1 | 220.9 | 189.8 | 226.3 | 293.7
1566 | 1408 | 208.9 | 108.1 | 213.7 | 125.2 | 220.8 | 189.4 | 225.8 | 293.2
1567 | 1409 | 208.5 | 107.6 | 212.6 | 124.8 | 220.4 | 189 | 225.3 | 292.7
1568 | 1410 | 208.2 | 107.4 | 211.9 | 124.9 | 220.1 | 188.1 | 224.8 | 292.2
1569 | 1411 | 207.9 | 107.5 | 212.1 | 125.1 | 220.1 | 187.2 | 224.3 | 291.8
1570 | 1412 | 207.7 | 107.8 | 211.5 | 124.7 | 220.3 | 186.5 | 223.8 | 291.3
1571 | 1413 | 207.4 | 108 | 211.3 | 123.6 | 220.6 | 185.8 | 223.3 | 290.9
1572 | 1414 | 207 | 108.2 | 211.7 | 123.8 | 221.1 | 185.2 | 222.8 | 290.5
1573 | 1415 | 206.7 | 108.3 | 211.8 | 123.3 | 221.7 | 184.6 | 222.4 | 290.1
1574 | 1416 | 206.3 | 108.2 | 211.8 | 123.8 | 222 | 184.3 | 221.9 | 289.7
1575 | 1417 | 206.1 | 108.2 | 211.8 | 124.2 | 221.6 | 183.8 | 221.4 | 289.4
1576 | 1418 | 205.9 | 108.6 | 211.8 | 124.6 | 221.3 | 183.3 | 220.9 | 289
1577 | 1419 | 205.6 | 108.8 | 211.9 | 124.2 | 220.8 | 182.9 | 220.4 | 288.5
1578 | 1420 | 205.3 | 108.6 | 211.9 | 124.3 | 220.1 | 182.3 | 220 | 288.1
1579 | 1421 | 204.9 | 108.7 | 211.6 | 124.3 | 219.2 | 181.9 | 219.5 | 287.7
1580 | 1422 | 204.6 | 108.7 | 210.6 | 123.3 | 218.3 | 181.7 | 219 | 287.3
1581 | 1423 | 204.3 | 108.5 | 210.2 | 122.7 | 217.1 | 181.2 | 218.6 | 286.9
1582 | 1424 | 204 | 108.2 | 209.4 | 121.8 | 215.7 | 180.8 | 218.1 | 286.4
1583 | 1425 | 203.7 | 108.1 | 208.7 | 121.8 | 214.1 | 180.4 | 217.7 | 286.1
1584 | 1426 | 203.5 | 107.8 | 208 | 121.4 | 212.7 | 179.7 | 217.2 | 285.6
1585 | 1427 | 203.3 | 107.6 | 207.2 | 120.6 | 211.5 | 179.3 | 216.8 | 285.2
1586 | 1428 | 203 | 107.5 | 206.5 | 119.5 | 210.3 | 179.1 | 216.3 | 284.8
1587 | 1429 | 202.8 | 106.9 | 205.2 | 118.3 | 209.2 | 178.3 | 215.9 | 284.5
1588 | 1430 | 202.5 | 106.4 | 204.3 | 117.8 | 208.5 | 177.6 | 215.5 | 284.1
1589 | 1431 | 202.2 | 106 | 203.6 | 117.9 | 207.8 | 177 | 215 | 283.7
1590 | 1432 | 202 | 105.6 | 203.3 | 117.5 | 207 | 176.6 | 214.6 | 283.3
1591 | 1433 | 201.7 | 105.1 | 202.5 | 116.8 | 206.2 | 176.1 | 214.2 | 282.9
1592 | 1434 | 201.4 | 104.6 | 201.8 | 116.4 | 205.4 | 175.3 | 213.8 | 282.5
1593 | 1435 | 201.1 | 103.9 | 200.8 | 116 | 204.7 | 174.4 | 213.3 | 282
1594 | 1436 | 200.7 | 103.6 | 200.5 | 115.7 | 204.2 | 173.6 | 212.9 | 281.6
1595 | 1437 | 200.4 | 103.5 | 199.9 | 115.4 | 203.7 | 172.8 | 212.5 | 281.2
1596 | 1438 | 200.1 | 103.1 | 198.8 | 114.6 | 202.9 | 171.9 | 212.1 | 280.8
1597 | 1439 | 199.9 | 102.7 | 198.2 | 114.2 | 201.9 | 171.3 | 211.6 | 280.3
1598 | 1440 | 199.6 | 102.5 | 197.8 | 114 | 201 | 170.8 | 211.2 | 279.8
1599 | 1441 | 199.4 | 102.2 | 196.9 | 113.5 | 200 | 170.1 | 210.8 | 279.4
1600 | 1442 | 199.1 | 101.8 | 196.6 | 113.4 | 198.9 | 169.5 | 210.3 | 279
1601 | 1443 | 198.9 | 101.5 | 196.4 | 113.1 | 197.7 | 168.9 | 209.9 | 278.5
1602 | 1444 | 198.6 | 101.4 | 196.3 | 112.6 | 196.6 | 168.3 | 209.5 | 278.1
1603 | 1445 | 198.4 | 101.1 | 196.2 | 111.9 | 195.3 | 167.5 | 209 | 277.7
1604 | 1446 | 198.1 | 100.7 | 195.7 | 110.9 | 193.9 | 167.1 | 208.6 | 277.2
1605 | 1447 | 197.8 | 100.5 | 195.2 | 110.1 | 192.5 | 166.3 | 208.1 | 276.8
1606 | 1448 | 197.6 | 100.6 | 195 | 109.3 | 191.3 | 165.7 | 207.7 | 276.4
1607 | 1449 | 197.3 | 100.3 | 194.8 | 109.2 | 190.5 | 165.3 | 207.2 | 275.9
1608 | 1450 | 197 | 100.2 | 194.8 | 108.6 | 190.1 | 164.8 | 206.8 | 275.5
1609 | 1451 | 196.7 | 100 | 193.9 | 107.9 | 189.6 | 164.4 | 206.3 | 275.1
1610 | 1452 | 196.3 | 99.6 | 193.1 | 107.4 | 189.1 | 163.7 | 205.9 | 274.7
1611 | 1453 | 196 | 99.3 | 193 | 107.2 | 188.6 | 163 | 205.5 | 274.3
1612 | 1454 | 195.8 | 99.2 | 192.8 | 106.9 | 188 | 162.5 | 205 | 273.9
1613 | 1455 | 195.6 | 99 | 192.3 | 106.5 | 187.3 | 161.8 | 204.6 | 273.5
1614 | 1456 | 195.3 | 98.7 | 191.9 | 105.7 | 186.5 | 161.5 | 204.2 | 273
1615 | 1457 | 195 | 98.6 | 191.8 | 105.4 | 185.9 | 161.3 | 203.7 | 272.6
1616 | 1458 | 194.7 | 98.8 | 191.7 | 105.2 | 185.5 | 161.1 | 203.3 | 272.1
1617 | 1459 | 194.5 | 98.6 | 191.5 | 105.1 | 185.2 | 160.9 | 202.9 | 271.8
1618 | 1460 | 194.2 | 98.5 | 191.4 | 104.7 | 185.3 | 160.6 | 202.5 | 271.3
1619 | 1461 | 193.9 | 98.4 | 191.2 | 104.2 | 185.7 | 160.2 | 202 | 270.9
1620 | 1462 | 193.6 | 98.3 | 191 | 104.5 | 186 | 159.8 | 201.6 | 270.4
1621 | 1463 | 193.4 | 98.1 | 190.6 | 103.8 | 186.3 | 159.2 | 201.2 | 270
1622 | 1464 | 193.1 | 98 | 190.3 | 103.4 | 186.6 | 158.5 | 200.8 | 269.5
1623 | 1465 | 192.9 | 97.9 | 190 | 103.6 | 187 | 157.9 | 200.4 | 269.1
1624 | 1466 | 192.7 | 98 | 189.8 | 104.6 | 187.4 | 157.3 | 199.9 | 268.7
1625 | 1467 | 192.4 | 98 | 189.6 | 104.4 | 187.6 | 156.7 | 199.5 | 268.3
1626 | 1468 | 192.2 | 98 | 189.2 | 103.2 | 188 | 156.1 | 199 | 267.9
1627 | 1469 | 191.9 | 98.2 | 188.9 | 102.4 | 188.2 | 155.8 | 198.6 | 267.5
1628 | 1470 | 191.6 | 98.5 | 188.6 | 101.9 | 188.3 | 155.4 | 198.1 | 267
1629 | 1471 | 191.3 | 98.7 | 188.5 | 102 | 187.9 | 154.9 | 197.7 | 266.7
1630 | 1472 | 191.1 | 98.9 | 188.5 | 102.1 | 187.2 | 154.5 | 197.2 | 266.3
1631 | 1473 | 190.7 | 98.9 | 188.3 | 102.2 | 186.3 | 153.8 | 196.8 | 265.8
1632 | 1474 | 190.5 | 99.1 | 188.2 | 102.1 | 185.6 | 153.3 | 196.3 | 265.5
1633 | 1475 | 190.2 | 99.4 | 188 | 101.7 | 185.5 | 152.9 | 195.9 | 265.2
1634 | 1476 | 190 | 99.5 | 187.8 | 101.6 | 185.5 | 152.5 | 195.4 | 264.8
1635 | 1477 | 189.7 | 99.7 | 187.6 | 101.2 | 185.7 | 152.3 | 195 | 264.5
1636 | 1478 | 189.4 | 99.9 | 187.4 | 101.5 | 185.6 | 152.1 | 194.6 | 264.1
1637 | 1479 | 189.2 | 100.1 | 187.2 | 102 | 185.3 | 151.9 | 194.1 | 263.7
1638 | 1480 | 188.9 | 100.5 | 187.1 | 102.8 | 185 | 151.4 | 193.7 | 263.3
1639 | 1481 | 188.7 | 100.9 | 186.9 | 103 | 185.1 | 150.9 | 193.3 | 262.9
1640 | 1482 | 188.4 | 101.2 | 186.5 | 103 | 185.5 | 150.5 | 192.8 | 262.5
1641 | 1483 | 188.2 | 101.2 | 186.1 | 104.7 | 185.8 | 150.1 | 192.4 | 262.2
1642 | 1484 | 187.9 | 100.9 | 185.6 | 104.5 | 186 | 149.8 | 191.9 | 261.8
1643 | 1485 | 187.7 | 101.2 | 185.2 | 103.4 | 186.4 | 149.5 | 191.5 | 261.3
1644 | 1486 | 187.4 | 101.4 | 185 | 103.2 | 186.8 | 149.2 | 191 | 260.9
1645 | 1487 | 187.2 | 101.4 | 184.7 | 103.1 | 186.9 | 148.8 | 190.6 | 260.4
1646 | 1488 | 186.9 | 101.7 | 184.4 | 102.9 | 186.9 | 148.7 | 190.1 | 260
1647 | 1489 | 186.7 | 102.1 | 184.2 | 103 | 187 | 148.4 | 189.7 | 259.6
1648 | 1490 | 186.5 | 102.5 | 183.9 | 102.7 | 187.2 | 148.2 | 189.2 | 259.2
1649 | 1491 | 186.2 | 102.7 | 183.6 | 102.6 | 187.4 | 147.9 | 188.8 | 258.8
1650 | 1492 | 185.8 | 103 | 183.3 | 103.2 | 187.6 | 147.5 | 188.4 | 258.3
1651 | 1493 | 185.6 | 103.2 | 183 | 102.8 | 188 | 147.1 | 187.9 | 258
1652 | 1494 | 185.5 | 103.4 | 182.3 | 102.5 | 188.2 | 146.8 | 187.5 | 257.5
1653 | 1495 | 185.3 | 103.4 | 181.8 | 102.1 | 188.4 | 146.4 | 187.1 | 257.1
1654 | 1496 | 185.1 | 103.3 | 181.2 | 101.7 | 188.5 | 145.9 | 186.6 | 256.7
1655 | 1497 | 184.8 | 103.7 | 180.9 | 102 | 188.7 | 145.7 | 186.2 | 256.3
1656 | 1498 | 184.5 | 103.9 | 180.5 | 102.3 | 188.8 | 145.4 | 185.8 | 255.9
1657 | 1499 | 184.3 | 104 | 180.3 | 102.6 | 188.7 | 145.3 | 185.4 | 255.4
1658 | 1500 | 184 | 103.8 | 179.9 | 103.2 | 188.5 | 145.3 | 185 | 255.1
1659 | 1501 | 183.8 | 104.2 | 179.5 | 103.2 | 188.3 | 145.1 | 184.6 | 254.7
1660 | 1502 | 183.5 | 104.7 | 179.2 | 103.2 | 188.2 | 144.8 | 184.1 | 254.3
1661 | 1503 | 183.2 | 105 | 178.9 | 103.3 | 188.3 | 144.7 | 183.7 | 254
1662 | 1504 | 183.1 | 105.2 | 178.6 | 103.4 | 188.4 | 144.7 | 183.3 | 253.7
1663 | 1505 | 182.9 | 105.6 | 178.4 | 103.6 | 188.3 | 144.5 | 182.9 | 253.3
1664 | 1506 | 182.7 | 105.6 | 178.2 | 103.5 | 188.2 | 144 | 182.5 | 252.8
1665 | 1507 | 182.4 | 105.7 | 177.7 | 103.8 | 188.2 | 143.7 | 182.1 | 252.5
1666 | 1508 | 182.3 | 105.7 | 176.6 | 103.4 | 188.1 | 143.5 | 181.7 | 252.1
1667 | 1509 | 182.1 | 106 | 176.1 | 102.9 | 188 | 143.3 | 181.3 | 251.7
1668 | 1510 | 181.9 | 105.8 | 175.7 | 102.7 | 188 | 143.1 | 180.9 | 251.3
1669 | 1511 | 181.6 | 105.6 | 175.7 | 102.5 | 188 | 142.7 | 180.5 | 250.9
1670 | 1512 | 181.4 | 105.6 | 175.6 | 102.4 | 188 | 142.4 | 180 | 250.5
1671 | 1513 | 181.2 | 105.9 | 175.4 | 102.1 | 187.8 | 142.2 | 179.6 | 250
1672 | 1514 | 181.1 | 105.9 | 174.9 | 101.8 | 187.7 | 142.3 | 179.2 | 249.7
1673 | 1515 | 180.8 | 105.5 | 174.6 | 102 | 187.5 | 142.2 | 178.8 | 249.3
1674 | 1516 | 180.6 | 105.4 | 174.4 | 102.4 | 187.3 | 141.8 | 178.4 | 248.9
1675 | 1517 | 180.3 | 105.1 | 174.3 | 102.5 | 187.2 | 141.7 | 178.1 | 248.5
1676 | 1518 | 180.1 | 104.4 | 174.1 | 102.3 | 186.8 | 141.5 | 177.7 | 248.2
1677 | 1519 | 179.9 | 103.6 | 173.8 | 101.4 | 186.3 | 141.1 | 177.3 | 247.8
1678 | 1520 | 179.6 | 102.8 | 173.3 | 100.8 | 185.5 | 140.8 | 177 | 247.4
1679 | 1521 | 179.3 | 102.1 | 172.7 | 100.3 | 184.6 | 140.4 | 176.6 | 247.1
1680 | 1522 | 179.1 | 101.5 | 172.4 | 99.8 | 183.8 | 140.1 | 176.3 | 246.7
1681 | 1523 | 178.9 | 100.8 | 172.1 | 99.1 | 183.1 | 139.7 | 175.9 | 246.4
1682 | 1524 | 178.7 | 100 | 171.6 | 98.4 | 182.5 | 139 | 175.6 | 246
1683 | 1525 | 178.4 | 99.3 | 171.2 | 98.3 | 181.7 | 138.3 | 175.2 | 245.7
1684 | 1526 | 178.1 | 98.6 | 170.7 | 98.3 | 180.6 | 137.8 | 174.9 | 245.4
1685 | 1527 | 177.9 | 97.7 | 170.1 | 97.9 | 179.4 | 137.3 | 174.5 | 245.1
1686 | 1528 | 177.7 | 97 | 169.7 | 97.5 | 178.1 | 136.9 | 174.2 | 244.7
1687 | 1529 | 177.4 | 96.5 | 169.3 | 97.2 | 176.6 | 136.8 | 173.8 | 244.4
1688 | 1530 | 177.1 | 96.1 | 168.9 | 96.8 | 174.9 | 136.6 | 173.5 | 244
1689 | 1531 | 176.8 | 95.5 | 168.5 | 96.2 | 173.3 | 136.6 | 173.1 | 243.6
1690 | 1532 | 176.6 | 95 | 168.2 | 96.1 | 171.7 | 136.3 | 172.8 | 243.2
1691 | 1533 | 176.4 | 94.5 | 167.9 | 95.4 | 170.3 | 136 | 172.5 | 242.8
1692 | 1534 | 176.2 | 93.8 | 167.3 | 94.7 | 169 | 135.9 | 172.1 | 242.4
1693 | 1535 | 176 | 93.3 | 166.8 | 94.2 | 167.6 | 135.8 | 171.8 | 242.1
1694 | 1536 | 175.8 | 92.9 | 166.2 | 93.9 | 166.3 | 135.4 | 171.5 | 241.7
1695 | 1537 | 175.6 | 92.5 | 165.7 | 93.7 | 165.1 | 134.9 | 171.2 | 241.3
1696 | 1538 | 175.4 | 92.2 | 165.3 | 93.2 | 164 | 134.6 | 170.9 | 241
1697 | 1539 | 175.1 | 91.7 | 164.8 | 92.5 | 163 | 134.4 | 170.5 | 240.6
1698 | 1540 | 174.9 | 91.1 | 164.4 | 92.3 | 162 | 134 | 170.2 | 240.3
1699 | 1541 | 174.6 | 90.6 | 164.1 | 91.8 | 161.1 | 133.7 | 169.9 | 239.9
1700 | 1542 | 174.3 | 90.2 | 163.7 | 91.2 | 160.1 | 133.5 | 169.6 | 239.6
1701 | 1543 | 174.1 | 89.8 | 163.2 | 90.6 | 159.1 | 133.1 | 169.3 | 239.2
1702 | 1544 | 173.8 | 89.2 | 162.7 | 90.2 | 158.1 | 132.9 | 169 | 238.8
1703 | 1545 | 173.7 | 88.9 | 162.3 | 89.7 | 157.4 | 132.6 | 168.7 | 238.4
1704 | 1546 | 173.5 | 88.5 | 162 | 89.4 | 156.8 | 132.3 | 168.4 | 238
1705 | 1547 | 173.3 | 88.3 | 161.7 | 89.1 | 156.1 | 131.9 | 168 | 237.7
1706 | 1548 | 173.1 | 88.2 | 161.3 | 88.7 | 155.7 | 131.4 | 167.7 | 237.3
1707 | 1549 | 172.9 | 88.2 | 160.8 | 88.6 | 155.2 | 131.2 | 167.4 | 237
1708 | 1550 | 172.7 | 88.1 | 160.5 | 88.4 | 154.7 | 130.8 | 167.1 | 236.6
1709 | 1551 | 172.5 | 87.7 | 160.1 | 87.9 | 154 | 130.4 | 166.8 | 236.2
1710 | 1552 | 172.3 | 87.5 | 159.6 | 88 | 153.3 | 130.3 | 166.5 | 235.8
1711 | 1553 | 172 | 87.5 | 159.4 | 87.8 | 152.6 | 130 | 166.2 | 235.5
1712 | 1554 | 171.8 | 87.3 | 159.2 | 87.4 | 151.9 | 129.5 | 165.8 | 235.2
1713 | 1555 | 171.6 | 87.1 | 158.8 | 87 | 151.2 | 129.2 | 165.5 | 234.9
1714 | 1556 | 171.4 | 86.8 | 158.4 | 86.9 | 150.5 | 129.1 | 165.2 | 234.5
1715 | 1557 | 171.2 | 86.4 | 158.1 | 86.7 | 149.8 | 128.7 | 164.9 | 234.2
1716 | 1558 | 171 | 85.9 | 157.6 | 86.6 | 149.1 | 128.4 | 164.6 | 233.8
1717 | 1559 | 170.8 | 85.6 | 157.1 | 86.5 | 148.6 | 128.2 | 164.3 | 233.5
1718 | 1560 | 170.5 | 85.6 | 156.9 | 86.3 | 148.6 | 128.1 | 164 | 233.1
1719 | 1561 | 170.3 | 85.4 | 156.6 | 86 | 148.7 | 128 | 163.7 | 232.7
1720 | 1562 | 170.1 | 85.2 | 156.3 | 85.7 | 148.9 | 127.8 | 163.4 | 232.3
1721 | 1563 | 169.8 | 85.1 | 155.9 | 85.6 | 149.1 | 127.5 | 163.1 | 232
1722 | 1564 | 169.6 | 85.1 | 155.3 | 85 | 149.4 | 127.2 | 162.7 | 231.7
1723 | 1565 | 169.4 | 85.1 | 154.8 | 84.2 | 149.6 | 127.1 | 162.4 | 231.3
1724 | 1566 | 169.2 | 84.9 | 154.5 | 84.1 | 149.8 | 127 | 162.1 | 231
1725 | 1567 | 169 | 84.6 | 153.9 | 83.7 | 150 | 126.9 | 161.8 | 230.6
1726 | 1568 | 168.8 | 84.5 | 153.3 | 83.4 | 149.9 | 126.6 | 161.5 | 230.2
1727 | 1569 | 168.5 | 84.4 | 152.8 | 82.9 | 149.8 | 126.4 | 161.2 | 229.9
1728 | 1570 | 168.3 | 84.2 | 152.5 | 82.3 | 149.9 | 126.2 | 160.9 | 229.6
1729 | 1571 | 168.1 | 83.9 | 152.4 | 82.3 | 150 | 125.9 | 160.6 | 229.3
1730 | 1572 | 167.9 | 83.8 | 152.3 | 82.2 | 150.2 | 125.7 | 160.3 | 228.9
1731 | 1573 | 167.7 | 83.9 | 152 | 81.9 | 150.4 | 125.6 | 160 | 228.5
1732 | 1574 | 167.4 | 83.7 | 151.5 | 82.5 | 150.3 | 125.4 | 159.7 | 228.2
1733 | 1575 | 167 | 83.4 | 151.1 | 82.6 | 150.2 | 125.3 | 159.4 | 227.8
1734 | 1576 | 166.8 | 83.2 | 151 | 82.5 | 150.3 | 124.9 | 159.1 | 227.3
1735 | 1577 | 166.6 | 83.1 | 151 | 83 | 150.3 | 124.5 | 158.8 | 227
1736 | 1578 | 166.4 | 83.3 | 150.8 | 83.2 | 150.4 | 124.2 | 158.5 | 226.6
1737 | 1579 | 166.3 | 83.2 | 150.6 | 83.9 | 150.6 | 124 | 158.2 | 226.3
1738 | 1580 | 166.1 | 82.7 | 150.4 | 83.9 | 150.7 | 123.9 | 157.8 | 226
1739 | 1581 | 165.9 | 82.7 | 150.3 | 83.2 | 150.8 | 123.7 | 157.5 | 225.7
1740 | 1582 | 165.7 | 82.8 | 150.1 | 83 | 150.9 | 123.4 | 157.2 | 225.4
1741 | 1583 | 165.5 | 83.1 | 150 | 83.3 | 151.1 | 122.9 | 156.9 | 225
1742 | 1584 | 165.3 | 83.4 | 149.9 | 83.7 | 151.3 | 122.6 | 156.5 | 224.6
1743 | 1585 | 165.1 | 83.6 | 149.6 | 83.6 | 151.6 | 122.5 | 156.2 | 224.2
1744 | 1586 | 164.9 | 83.8 | 149.4 | 84 | 151.8 | 122.1 | 155.9 | 223.9
1745 | 1587 | 164.7 | 84.4 | 149.4 | 84.9 | 152.1 | 121.6 | 155.6 | 223.6
1746 | 1588 | 164.5 | 84.9 | 149.3 | 85.5 | 152.5 | 121.4 | 155.3 | 223.4
1747 | 1589 | 164.3 | 85.5 | 149 | 85.8 | 152.8 | 121.3 | 154.9 | 223.1
1748 | 1590 | 164.1 | 86 | 148.7 | 86.3 | 153 | 121.4 | 154.6 | 222.8
1749 | 1591 | 163.9 | 86.1 | 148.2 | 86.2 | 153.3 | 121.2 | 154.3 | 222.4
1750 | 1592 | 163.7 | 86.4 | 148.1 | 86.7 | 153.5 | 120.9 | 153.9 | 222.1
1751 | 1593 | 163.5 | 86.7 | 147.7 | 86.7 | 153.6 | 120.6 | 153.6 | 221.7
1752 | 1594 | 163.3 | 86.9 | 147.6 | 86.5 | 153.8 | 120.6 | 153.3 | 221.4
1753 | 1595 | 163.1 | 87.1 | 147.4 | 86.9 | 153.8 | 120.4 | 153 | 221.1
1754 | 1596 | 163 | 87.5 | 147.2 | 87.4 | 153.8 | 120.3 | 152.6 | 220.7
1755 | 1597 | 162.8 | 87.6 | 147.1 | 87.9 | 153.9 | 120.1 | 152.3 | 220.4
1756 | 1598 | 162.5 | 87.7 | 147 | 87.8 | 153.9 | 120.2 | 152 | 220
1757 | 1599 | 162.3 | 87.7 | 146.6 | 87.6 | 153.9 | 120.4 | 151.7 | 219.7
1758 | 1600 | 162.1 | 87.6 | 146.4 | 87.8 | 153.9 | 120.4 | 151.4 | 219.4
1759 | 1601 | 161.9 | 87.5 | 146.3 | 88.3 | 153.7 | 120.2 | 151.1 | 219.1
1760 | 1602 | 161.7 | 87.4 | 146.1 | 88.9 | 153.5 | 119.8 | 150.8 | 218.8
1761 | 1603 | 161.5 | 87.5 | 145.9 | 89.1 | 153.3 | 119.5 | 150.5 | 218.4
1762 | 1604 | 161.3 | 87.7 | 145.6 | 88.8 | 153.3 | 119.4 | 150.2 | 218
1763 | 1605 | 161.1 | 87.9 | 145.2 | 88.2 | 153.4 | 119.3 | 149.9 | 217.8
1764 | 1606 | 160.9 | 88 | 145 | 88.6 | 153.4 | 119.1 | 149.6 | 217.5
1765 | 1607 | 160.7 | 88.2 | 144.8 | 89.3 | 153.3 | 118.9 | 149.3 | 217.2
1766 | 1608 | 160.5 | 88.5 | 144.5 | 89.9 | 153.2 | 118.8 | 149 | 216.9
1767 | 1609 | 160.3 | 88.5 | 144.2 | 89.5 | 153.1 | 118.8 | 148.7 | 216.6
1768 | 1610 | 160.1 | 88.5 | 143.7 | 89.4 | 153.1 | 118.6 | 148.4 | 216.3
1769 | 1611 | 159.8 | 88.6 | 143.5 | 89.6 | 153.1 | 118.4 | 148 | 216
1770 | 1612 | 159.6 | 88.8 | 143.2 | 89.9 | 153.1 | 118.3 | 147.7 | 215.7
1771 | 1613 | 159.4 | 88.6 | 142.8 | 89.7 | 153.2 | 118.2 | 147.4 | 215.4
1772 | 1614 | 159.2 | 88.3 | 142.5 | 89.4 | 153.2 | 118 | 147.2 | 215.1
1773 | 1615 | 159 | 88.1 | 142.3 | 89.3 | 153.1 | 117.9 | 146.9 | 214.9
1774 | 1616 | 158.8 | 87.9 | 142.1 | 89.3 | 153 | 117.9 | 146.6 | 214.6
1775 | 1617 | 158.7 | 87.8 | 142.1 | 89.4 | 152.9 | 117.8 | 146.3 | 214.4
1776 | 1618 | 158.4 | 88 | 141.9 | 89.3 | 152.9 | 117.6 | 146 | 214.1
1777 | 1619 | 158.2 | 88.1 | 141.7 | 89.5 | 152.9 | 117.3 | 145.8 | 213.8
1778 | 1620 | 158 | 88.2 | 141.1 | 89.8 | 152.8 | 117.2 | 145.5 | 213.6
1779 | 1621 | 157.8 | 88.4 | 141 | 90.3 | 152.7 | 117 | 145.2 | 213.2
1780 | 1622 | 157.6 | 88.6 | 140.9 | 90.6 | 152.6 | 116.6 | 144.9 | 212.9
1781 | 1623 | 157.5 | 88.7 | 140.9 | 90.6 | 152.7 | 116.3 | 144.6 | 212.6
1782 | 1624 | 157.3 | 88.4 | 140.7 | 90.9 | 152.6 | 115.8 | 144.4 | 212.3
1783 | 1625 | 157.2 | 88.4 | 140.3 | 90.9 | 152.5 | 115.5 | 144.1 | 212
1784 | 1626 | 157 | 88.1 | 139.9 | 90.9 | 152.4 | 115.4 | 143.8 | 211.7
1785 | 1627 | 156.9 | 87.7 | 139.3 | 90.5 | 152.2 | 115.1 | 143.5 | 211.4
1786 | 1628 | 156.7 | 87.7 | 139.1 | 89.7 | 152 | 114.9 | 143.2 | 211.2
1787 | 1629 | 156.5 | 87.7 | 139 | 89.6 | 151.9 | 114.8 | 142.9 | 210.9
1788 | 1630 | 156.4 | 87.9 | 138.8 | 90.1 | 151.8 | 114.7 | 142.7 | 210.6
1789 | 1631 | 156.2 | 87.8 | 138.5 | 90.3 | 151.8 | 114.6 | 142.4 | 210.3
1790 | 1632 | 156 | 87.7 | 138.2 | 90 | 151.7 | 114.5 | 142.1 | 210
1791 | 1633 | 155.9 | 87.6 | 137.7 | 89.6 | 151.7 | 114.4 | 141.8 | 209.7
1792 | 1634 | 155.7 | 87.3 | 137.6 | 89.3 | 151.5 | 114.3 | 141.6 | 209.4
1793 | 1635 | 155.5 | 87.2 | 137.6 | 89.1 | 151.3 | 114.2 | 141.3 | 209.2
1794 | 1636 | 155.3 | 86.9 | 137.6 | 89.2 | 151.2 | 113.7 | 141 | 208.8
1795 | 1637 | 155.1 | 86.7 | 137.4 | 88.5 | 151.1 | 113.5 | 140.7 | 208.6
1796 | 1638 | 154.9 | 86.4 | 137.2 | 88.3 | 150.9 | 113.4 | 140.4 | 208.5
1797 | 1639 | 154.7 | 86.3 | 137.2 | 88.5 | 150.6 | 113.3 | 140.2 | 208.2
1798 | 1640 | 154.5 | 86.1 | 137.1 | 88.3 | 150.4 | 113.2 | 139.9 | 207.8
1799 | 1641 | 154.4 | 85.8 | 136.9 | 87.7 | 150 | 113.1 | 139.7 | 207.6
1800 | 1642 | 154.2 | 85.5 | 136.8 | 87.3 | 149.6 | 112.8 | 139.4 | 207.2
1801 | 1643 | 154.1 | 85.5 | 136.5 | 87.3 | 149.3 | 112.6 | 139.2 | 206.9
1802 | 1644 | 153.8 | 85.3 | 136.3 | 86.8 | 148.9 | 112.4 | 138.9 | 206.7
1803 | 1645 | 153.6 | 85 | 136.1 | 85.9 | 148.4 | 112.4 | 138.7 | 206.4
1804 | 1646 | 153.4 | 84.6 | 135.8 | 85.4 | 147.8 | 112.4 | 138.4 | 206.1
1805 | 1647 | 153.2 | 84.3 | 135.5 | 85.1 | 147.2 | 112.2 | 138.2 | 205.9
1806 | 1648 | 153 | 83.9 | 135.3 | 85 | 146.4 | 112 | 138 | 205.7
1807 | 1649 | 152.8 | 83.5 | 135.1 | 85.1 | 145.6 | 111.8 | 137.8 | 205.4
1808 | 1650 | 152.6 | 83.1 | 134.8 | 84.7 | 145.1 | 111.6 | 137.6 | 205.1
1809 | 1651 | 152.5 | 82.9 | 134.5 | 84.2 | 144.8 | 111.3 | 137.3 | 204.8
1810 | 1652 | 152.3 | 82.6 | 134.2 | 84.2 | 144.6 | 111 | 137.1 | 204.5
1811 | 1653 | 152.1 | 82 | 133.9 | 85.3 | 144.5 | 110.8 | 136.9 | 204.2
1812 | 1654 | 151.9 | 81.6 | 133.2 | 85 | 144.3 | 110.6 | 136.7 | 203.9
1813 | 1655 | 151.7 | 81.4 | 132.8 | 84.8 | 144.3 | 110.4 | 136.4 | 203.6
1814 | 1656 | 151.6 | 80.8 | 132.2 | 85.8 | 144.1 | 110.1 | 136.2 | 203.3
1815 | 1657 | 151.4 | 80.6 | 132 | 85.4 | 144 | 109.9 | 136 | 203
1816 | 1658 | 151.2 | 80.3 | 131.9 | 85.2 | 144 | 109.6 | 135.7 | 202.7
1817 | 1659 | 151.1 | 80.2 | 132 | 84.9 | 143.9 | 109.6 | 135.5 | 202.5
1818 | 1660 | 151 | 80.1 | 131.8 | 84.7 | 143.8 | 109.5 | 135.3 | 202.3
1819 | 1661 | 150.8 | 80.2 | 131.8 | 85 | 143.6 | 109.4 | 135 | 201.9
1820 | 1662 | 150.6 | 80.6 | 131.4 | 85.1 | 143.3 | 109.3 | 134.8 | 201.6
1821 | 1663 | 150.4 | 80.9 | 131.2 | 85.2 | 143.1 | 109.2 | 134.6 | 201.3
1822 | 1664 | 150.2 | 81.1 | 130.9 | 84.5 | 142.9 | 109.2 | 134.4 | 201

## Test Facts
Last row in IRMS data sheets: | 15
Time when Penlight power was initiated: | 158