## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 6 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Penlight Test 47
Test conditions: Cable: 7-conductor, 12 AWG, one XLPE insulated, Rockbestos Firewall III, control cable and two EPR insulated, industrial control cables (cable items #10 & #2). Cable specimens present: Three lengths of cable were monitored for electrical performance, a fourth length of cable (XLPE) was monitored for temperature response, no other cable samples present. Raceway: 2.5" Rigid metal conduit located centrally in the Penlight chamber with chamber end walls closed and un-heated. Exposure conditions: Shroud set to temperature of 525C, nominal 23 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using six channels - two for each cable (see electrical connection map), conduit was grounded. Thermal response monitoring: Shroud temperature, three conduit temperatures and six cable temperatures (see thermocouple map). Shroud power: Initiated after 127 seconds of baseline data monitoring. Special Note: Test setup included three thermocouples on the outer surface of the conduit.
DAQ Time | Penlight Time | Event | Interpretation
127 | 0 | Initated Penlight Heating
1411-1414 | 1284-1287 | Conductors C5 & C6 short to ground (437 & 60) | Cable C shorts to ground
1426-1468 | 1299-1341 | Conductors C5 & C6 short together (436, then decreases to 26) | Cable C is shorted internally
1454 | 1327 | Existing ground fault on conductor C5 decreases to less than 100 ohms (7)
1742-1746 | 1615-1619 | Conductors B3 & B4 both short to ground at less than 1000 ohms (928 & 407) | Cable B shorts to ground
1784 | 1657 | Existing ground fault on conductor B3 decreases to less than 100 ohms (29)
1789 | 1662 | Conductors B3 & B4 short together at less than 100 ohms (67) | Cable B is shorted internally
1890 | 1763 | Conductors A1 & A2 short together at less than 100 ohms (8) | Cable A is shorted internally
1896-1905 | 1742-1778 | Conductors A1 & A2 short to ground at less than 100 ohms (85 & 90) | Cable A shorts to ground intermittently
2778 | 2651 | Power to Penlight shutoff
Additional Observations
Observation 1 | Cable failures progressed as expected during this test: the two lower cables (B & C) shorted to ground well before cable (A)
Observation 2 | It took 1284 seconds (21.4 min.) from the start of Penlight heating for the first short to ground failure to occur, and it took 1299 s (21.7 min.) for the first internal short failure.
Observation 3 | No cable to cable interations occurred prior to one or both cables shorting to ground or internally.

## Thermocouple Map
Thermocouple map for TC's on and within the cable and conduit
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | Conduit 1 | Outer surface of conduit
| TC2 | = | Conduit 2 | Outer surface of conduit at mid-point
| TC3 | = | Conduit 3 | Outer surface of conduit
| TC4 | = | Cable 1 | Within cable just below cable jacket, center position
| TC5 | = | Cable 2 | At cable core between conductors, left of center conductor
| TC6 | = | Cable 3 | At cable core between conductors, right of center conductor
| TC7 | = | Cable 4 | Within cable just below cable jacket, opposite side from Cable 1, center position
| TC8 | = | Cable 5 | On outer cable surface, outboard from cable center
| TC9 | = | Cable 6 | On outer cable surface, outboard from cable center

## Elect Conn Map
Electrical connection map within the cables
Cable A = XLPE (item #10)
Cable B = EPR (item #2)
Cable C = EPR (item #2)
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Penlight Test 47 |  |  | 2006-08-30 | 11:56
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-A2 | Penlight Time | A1-B3 | Penlight Time | A1-B4 | Penlight Time | A1-C5 | Penlight Time | A1-C6 | Penlight Time | A2-B3 | Penlight Time | A2-B4 | Penlight Time | A2-C5 | Penlight Time | A2-C6 | Penlight Time | B3-B4 | Penlight Time | B3-C5 | Penlight Time | B3-C6 | Penlight Time | B4-C5 | Penlight Time | B4-C6 | Penlight Time | C5-C6 | Penlight Time | Minimums
-126.5 | 232137.9994 | -124 | 248337.9994 | -121 | 244437.9994 | -118.5 | 248437.9994 | -115.5 | 248137.9994 | -112.5 | 247437.9994 | -110 | 228337.9994 | -107 | 249037.9994 | -104.5 | 247337.9994 | -101.5 | 246237.9994 | -98.5 | 249437.9994 | -96 | 248737.9994 | -93 | 250037.9994 | -90.5 | 248937.9994 | -87.5 | 248337.9994 | -126.5 | #REF!
-84.5 | 232137.9994 | -81.5 | 248337.9994 | -79 | 244437.9994 | -76 | 248437.9994 | -73.5 | 248137.9994 | -70.5 | 247437.9994 | -67.5 | 228337.9994 | -65 | 249037.9994 | -62.5 | 247337.9994 | -59.5 | 246237.9994 | -56.5 | 249437.9994 | -54 | 248737.9994 | -51 | 250037.9994 | -48.5 | 248937.9994 | -45.5 | 248337.9994 | -84.5 | #REF!
-42.5 | 232137.9994 | -40 | 248337.9994 | -37 | 244437.9994 | -34.5 | 248437.9994 | -31.5 | 248137.9994 | -28.5 | 247437.9994 | -26 | 228337.9994 | -23 | 249037.9994 | -20 | 247337.9994 | -17.5 | 246237.9994 | -14.5 | 249437.9994 | -12 | 248737.9994 | -9 | 250037.9994 | -6.5 | 27570.8834 | -3.5 | 248337.9994 | -42.5 | #REF!
-0.5 | 232137.9994 | 2 | 248337.9994 | 5 | 244437.9994 | 7.5 | 248437.9994 | 10.5 | 248137.9994 | 13.5 | 247437.9994 | 16.5 | 228337.9994 | 19 | 249037.9994 | 21.5 | 247337.9994 | 24.5 | 246237.9994 | 27.5 | 249437.9994 | 30 | 248737.9994 | 33 | 250037.9994 | 35.5 | 248937.9994 | 38.5 | 248337.9994 | -0.5 | #REF!
41.5 | 232137.9994 | 44 | 248337.9994 | 47 | 244437.9994 | 49.5 | 248437.9994 | 52.5 | 248137.9994 | 55.5 | 247437.9994 | 58 | 228337.9994 | 61 | 249037.9994 | 63.5 | 247337.9994 | 66.5 | 246237.9994 | 69.5 | 249437.9994 | 72 | 248737.9994 | 75 | 250037.9994 | 77.5 | 248937.9994 | 80.5 | 248337.9994 | 41.5 | #REF!
83.5 | 232137.9994 | 86 | 248337.9994 | 89 | 244437.9994 | 92 | 248437.9994 | 94.5 | 248137.9994 | 97.5 | 247437.9994 | 100 | 228337.9994 | 103 | 249037.9994 | 105.5 | 247337.9994 | 108.5 | 246237.9994 | 111.5 | 249437.9994 | 114 | 248737.9994 | 117 | 250037.9994 | 119.5 | 248937.9994 | 122.5 | 248337.9994 | 83.5 | #REF!
125.5 | 232137.9994 | 128 | 248337.9994 | 131 | 244437.9994 | 134 | 248437.9994 | 136.5 | 248137.9994 | 139.5 | 247437.9994 | 142 | 228337.9994 | 145 | 249037.9994 | 147.5 | 247337.9994 | 150.5 | 246237.9994 | 153.5 | 249437.9994 | 156 | 248737.9994 | 159 | 250037.9994 | 162 | 248937.9994 | 164.5 | 248337.9994 | 125.5 | #REF!
167.5 | 232137.9994 | 170 | 248337.9994 | 173 | 244437.9994 | 175.5 | 248437.9994 | 178.5 | 248137.9994 | 181.5 | 247437.9994 | 184 | 228337.9994 | 187 | 249037.9994 | 189.5 | 247337.9994 | 192.5 | 246237.9994 | 195.5 | 249437.9994 | 198 | 248737.9994 | 201 | 250037.9994 | 203.5 | 248937.9994 | 206.5 | 248337.9994 | 167.5 | #REF!
209.5 | 232137.9994 | 212.5 | 248337.9994 | 215 | 244437.9994 | 217.5 | 248437.9994 | 220.5 | 248137.9994 | 223.5 | 247437.9994 | 226 | 228337.9994 | 229 | 249037.9994 | 231.5 | 247337.9994 | 234.5 | 246237.9994 | 237.5 | 249437.9994 | 240 | 248737.9994 | 243 | 250037.9994 | 245.5 | 248937.9994 | 248.5 | 248337.9994 | 209.5 | #REF!
251.5 | 232137.9994 | 254 | 248337.9994 | 257 | 244437.9994 | 259.5 | 248437.9994 | 262.5 | 248137.9994 | 265.5 | 247437.9994 | 268 | 228337.9994 | 271 | 249037.9994 | 273.5 | 247337.9994 | 276.5 | 246237.9994 | 279.5 | 249437.9994 | 282 | 248737.9994 | 285 | 250037.9994 | 287.5 | 248937.9994 | 290.5 | 248337.9994 | 251.5 | #REF!
293.5 | 232137.9994 | 296 | 248337.9994 | 299 | 244437.9994 | 301.5 | 248437.9994 | 304.5 | 248137.9994 | 307.5 | 247437.9994 | 310 | 228337.9994 | 313 | 249037.9994 | 315.5 | 247337.9994 | 318.5 | 246237.9994 | 321.5 | 249437.9994 | 324 | 248737.9994 | 327 | 250037.9994 | 329.5 | 248937.9994 | 332.5 | 248337.9994 | 293.5 | #REF!
335.5 | 232137.9994 | 338 | 248337.9994 | 341 | 244437.9994 | 343.5 | 248437.9994 | 346.5 | 248137.9994 | 349.5 | 247437.9994 | 352 | 228337.9994 | 355 | 249037.9994 | 357.5 | 247337.9994 | 360.5 | 246237.9994 | 363.5 | 249437.9994 | 366 | 248737.9994 | 369 | 250037.9994 | 372 | 248937.9994 | 374.5 | 248337.9994 | 335.5 | #REF!
377.5 | 232137.9994 | 380 | 248337.9994 | 383 | 244437.9994 | 385.5 | 248437.9994 | 388.5 | 248137.9994 | 391.5 | 247437.9994 | 394 | 228337.9994 | 397 | 249037.9994 | 399.5 | 247337.9994 | 402.5 | 246237.9994 | 405.5 | 249437.9994 | 408 | 248737.9994 | 411 | 250037.9994 | 413.5 | 248937.9994 | 416.5 | 248337.9994 | 377.5 | #REF!
419.5 | 232137.9994 | 422 | 248337.9994 | 425 | 244437.9994 | 427.5 | 248437.9994 | 430.5 | 248137.9994 | 433.5 | 247437.9994 | 436 | 228337.9994 | 439 | 249037.9994 | 441.5 | 247337.9994 | 444.5 | 246237.9994 | 447.5 | 249437.9994 | 450 | 248737.9994 | 453 | 250037.9994 | 455.5 | 248937.9994 | 458.5 | 248337.9994 | 419.5 | #REF!
461.5 | 232137.9994 | 464 | 248337.9994 | 467 | 244437.9994 | 469.5 | 248437.9994 | 472.5 | 248137.9994 | 475.5 | 247437.9994 | 478 | 228337.9994 | 481 | 249037.9994 | 483.5 | 247337.9994 | 486.5 | 246237.9994 | 489.5 | 249437.9994 | 492 | 248737.9994 | 495 | 250037.9994 | 497.5 | 248937.9994 | 500.5 | 248337.9994 | 461.5 | #REF!
503.5 | 232137.9994 | 506 | 248337.9994 | 509 | 244437.9994 | 511.5 | 248437.9994 | 514.5 | 248137.9994 | 517.5 | 247437.9994 | 520 | 228337.9994 | 523 | 249037.9994 | 525.5 | 247337.9994 | 528.5 | 246237.9994 | 531.5 | 249437.9994 | 534 | 248737.9994 | 537 | 250037.9994 | 539.5 | 248937.9994 | 542.5 | 248337.9994 | 503.5 | #REF!
545.5 | 232137.9994 | 548 | 248337.9994 | 551 | 244437.9994 | 553.5 | 248437.9994 | 556.5 | 248137.9994 | 559.5 | 247437.9994 | 562 | 228337.9994 | 565 | 249037.9994 | 567.5 | 247337.9994 | 570.5 | 246237.9994 | 573.5 | 249437.9994 | 576 | 248737.9994 | 579 | 250037.9994 | 581.5 | 248937.9994 | 584.5 | 248337.9994 | 545.5 | #REF!
587.5 | 232137.9994 | 590 | 248337.9994 | 593 | 244437.9994 | 595.5 | 248437.9994 | 598.5 | 248137.9994 | 601.5 | 247437.9994 | 604 | 228337.9994 | 607 | 249037.9994 | 609.5 | 247337.9994 | 612.5 | 246237.9994 | 615.5 | 249437.9994 | 618 | 248737.9994 | 621 | 250037.9994 | 623.5 | 248937.9994 | 626.5 | 248337.9994 | 587.5 | #REF!
629.5 | 232137.9994 | 632 | 248337.9994 | 635 | 244437.9994 | 637.5 | 248437.9994 | 640.5 | 248137.9994 | 643.5 | 247437.9994 | 646 | 228337.9994 | 649 | 249037.9994 | 651.5 | 247337.9994 | 654.5 | 246237.9994 | 657.5 | 249437.9994 | 660 | 248737.9994 | 663 | 250037.9994 | 665.5 | 248937.9994 | 668.5 | 248337.9994 | 629.5 | #REF!
671.5 | 232137.9994 | 674 | 248337.9994 | 677 | 244437.9994 | 679.5 | 248437.9994 | 682.5 | 248137.9994 | 685.5 | 247437.9994 | 688 | 228337.9994 | 691 | 249037.9994 | 693.5 | 247337.9994 | 696.5 | 246237.9994 | 699.5 | 249437.9994 | 702 | 248737.9994 | 705 | 250037.9994 | 707.5 | 248937.9994 | 710.5 | 248337.9994 | 671.5 | #REF!
713.5 | 232137.9994 | 716 | 248337.9994 | 719 | 244437.9994 | 721.5 | 248437.9994 | 724.5 | 248137.9994 | 727.5 | 247437.9994 | 730 | 228337.9994 | 733 | 249037.9994 | 735.5 | 247337.9994 | 738.5 | 246237.9994 | 741.5 | 249437.9994 | 744 | 248737.9994 | 747 | 250037.9994 | 749.5 | 248937.9994 | 752.5 | 248337.9994 | 713.5 | #REF!
755.5 | 232137.9994 | 758 | 248337.9994 | 761 | 244437.9994 | 763.5 | 248437.9994 | 766.5 | 248137.9994 | 769.5 | 247437.9994 | 772 | 228337.9994 | 775 | 249037.9994 | 777.5 | 247337.9994 | 780.5 | 246237.9994 | 783.5 | 249437.9994 | 786 | 248737.9994 | 788.5 | 250037.9994 | 791.5 | 248937.9994 | 794.5 | 248337.9994 | 755.5 | #REF!
797.5 | 232137.9994 | 800 | 248337.9994 | 803 | 244437.9994 | 805.5 | 248437.9994 | 808.5 | 248137.9994 | 811.5 | 247437.9994 | 814 | 228337.9994 | 817 | 249037.9994 | 819.5 | 247337.9994 | 822.5 | 246237.9994 | 825.5 | 249437.9994 | 828 | 248737.9994 | 831 | 250037.9994 | 833.5 | 248937.9994 | 836.5 | 248337.9994 | 797.5 | #REF!
839.5 | 232137.9994 | 842 | 248337.9994 | 845 | 244437.9994 | 847.5 | 248437.9994 | 850.5 | 248137.9994 | 853.5 | 247437.9994 | 856 | 228337.9994 | 859 | 249037.9994 | 861.5 | 247337.9994 | 864.5 | 246237.9994 | 867 | 249437.9994 | 870 | 248737.9994 | 873 | 250037.9994 | 875.5 | 248937.9994 | 878.5 | 248337.9994 | 839.5 | #REF!
881 | 232137.9994 | 884 | 248337.9994 | 887 | 244437.9994 | 889.5 | 248437.9994 | 892.5 | 248137.9994 | 895.5 | 247437.9994 | 898 | 228337.9994 | 900.5 | 249037.9994 | 903.5 | 247337.9994 | 906.5 | 246237.9994 | 909 | 249437.9994 | 912 | 248737.9994 | 915 | 250037.9994 | 917.5 | 248937.9994 | 920.5 | 248337.9994 | 881 | #REF!
923.5 | 232137.9994 | 926 | 248337.9994 | 928.5 | 244437.9994 | 931.5 | 248437.9994 | 934.5 | 248137.9994 | 937 | 247437.9994 | 940 | 228337.9994 | 942.5 | 249037.9994 | 945.5 | 247337.9994 | 948.5 | 246237.9994 | 951 | 249437.9994 | 954 | 248737.9994 | 956.5 | 250037.9994 | 959.5 | 248937.9994 | 962.5 | 248337.9994 | 923.5 | #REF!
965 | 232137.9994 | 968 | 248337.9994 | 970.5 | 122168.9988 | 973.5 | 248437.9994 | 976.5 | 248137.9994 | 979.5 | 247437.9994 | 982 | 228337.9994 | 984.5 | 249037.9994 | 987.5 | 247337.9994 | 990.5 | 246237.9994 | 993 | 249437.9994 | 996 | 248737.9994 | 998.5 | 250037.9994 | 1001.5 | 248937.9994 | 1004.5 | 248337.9994 | 965 | #REF!
1007 | 232137.9994 | 1010 | 248337.9994 | 1012.5 | 244437.9994 | 1015.5 | 248437.9994 | 1018.5 | 248137.9994 | 1021.5 | 247437.9994 | 1024 | 228337.9994 | 1027 | 249037.9994 | 1029.5 | 247337.9994 | 1032.5 | 246237.9994 | 1035.5 | 249437.9994 | 1038 | 248737.9994 | 1040.5 | 250037.9994 | 1043.5 | 248937.9994 | 1046.5 | 248337.9994 | 1007 | #REF!
1049.5 | 232137.9994 | 1052 | 248337.9994 | 1055 | 244437.9994 | 1057.5 | 248437.9994 | 1060.5 | 248137.9994 | 1063.5 | 247437.9994 | 1066 | 228337.9994 | 1069 | 249037.9994 | 1071.5 | 247337.9994 | 1074.5 | 246237.9994 | 1077.5 | 249437.9994 | 1080 | 248737.9994 | 1083 | 250037.9994 | 1085.5 | 248937.9994 | 1088.5 | 248337.9994 | 1049.5 | #REF!
1091 | 232137.9994 | 1094 | 248337.9994 | 1096.5 | 244437.9994 | 1099.5 | 248437.9994 | 1102.5 | 248137.9994 | 1105.5 | 247437.9994 | 1108 | 228337.9994 | 1111 | 249037.9994 | 1113.5 | 247337.9994 | 1116.5 | 246237.9994 | 1119 | 249437.9994 | 1122 | 248737.9994 | 1125 | 250037.9994 | 1127.5 | 248937.9994 | 1130.5 | 248337.9994 | 1091 | #REF!
1133.5 | 232137.9994 | 1136 | 248337.9994 | 1138.5 | 244437.9994 | 1141.5 | 248437.9994 | 1144.5 | 248137.9994 | 1147 | 247437.9994 | 1150 | 228337.9994 | 1152.5 | 249037.9994 | 1155.5 | 247337.9994 | 1158.5 | 246237.9994 | 1161 | 249437.9994 | 1164 | 248737.9994 | 1167 | 250037.9994 | 1169.5 | 248937.9994 | 1172.5 | 248337.9994 | 1133.5 | #REF!
1175 | 232137.9994 | 1178 | 248337.9994 | 1181 | 244437.9994 | 1183.5 | 248437.9994 | 1186.5 | 248137.9994 | 1189 | 247437.9994 | 1192 | 228337.9994 | 1195 | 249037.9994 | 1197.5 | 247337.9994 | 1200.5 | 246237.9994 | 1203.5 | 249437.9994 | 1206 | 248737.9994 | 1209 | 250037.9994 | 1211.5 | 248937.9994 | 1214.5 | 248337.9994 | 1175 | #REF!
1217 | 232137.9994 | 1220 | 248337.9994 | 1222.5 | 244437.9994 | 1225.5 | 248437.9994 | 1228.5 | 248137.9994 | 1231 | 247437.9994 | 1234 | 228337.9994 | 1236.5 | 249037.9994 | 1239.5 | 247337.9994 | 1242.5 | 246237.9994 | 1245 | 249437.9994 | 1248 | 248737.9994 | 1250.5 | 250037.9994 | 1253.5 | 248937.9994 | 1256.5 | 248337.9994 | 1217 | #REF!
1259.5 | 232137.9994 | 1262 | 248337.9994 | 1264.5 | 244437.9994 | 1267.5 | 248437.9994 | 1270 | 248137.9994 | 1273 | 247437.9994 | 1276 | 228337.9994 | 1279 | 249037.9994 | 1281.5 | 247337.9994 | 1284.5 | 246237.9994 | 1287 | 249437.9994 | 1290 | 248737.9994 | 1292.5 | 124968.9988 | 1295.5 | 248937.9994 | 1298.5 | 436.3005 | 1259.5 | #REF!
1301.5 | 116018.9988 | 1304 | 248337.9994 | 1307 | 244437.9994 | 1309.5 | 248437.9994 | 1312.5 | 124018.9988 | 1315.5 | 123668.9988 | 1318 | 114118.9988 | 1320.5 | 249037.9994 | 1323.5 | 123618.9988 | 1326.5 | 82012.6648 | 1329 | 124668.9988 | 1332 | 82845.9982 | 1334.5 | 124968.9988 | 1337.5 | 82912.6648 | 1340.5 | 26.1477 | 1301.5 | #REF!
1343 | 77312.6648 | 1346 | 82712.6648 | 1349 | 122168.9988 | 1351.5 | 124168.9988 | 1354.5 | 82645.9982 | 1357 | 82412.6648 | 1360 | 114118.9988 | 1363 | 124468.9988 | 1365.5 | 123618.9988 | 1368.5 | 82012.6648 | 1371.5 | 124668.9988 | 1374 | 82845.9982 | 1377 | 83279.3315 | 1379.5 | 82912.6648 | 1382.5 | 16.6244 | 1343 | #REF!
1385 | 77312.6648 | 1388 | 82712.6648 | 1390.5 | 122168.9988 | 1393.5 | 124168.9988 | 1396.5 | 82645.9982 | 1399 | 82412.6648 | 1402 | 114118.9988 | 1404.5 | 124468.9988 | 1407.5 | 82379.3315 | 1410.5 | 82012.6648 | 1413.5 | 124668.9988 | 1416 | 82845.9982 | 1419 | 83279.3315 | 1421.5 | 82912.6648 | 1424.5 | 27.4116 | 1385 | #REF!
1427 | 77312.6648 | 1430 | 82712.6648 | 1432.5 | 122168.9988 | 1435.5 | 124168.9988 | 1438.5 | 82645.9982 | 1441 | 82412.6648 | 1444 | 114118.9988 | 1446.5 | 124468.9988 | 1449.5 | 82379.3315 | 1452.5 | 82012.6648 | 1455.5 | 124668.9988 | 1458 | 82845.9982 | 1460.5 | 83279.3315 | 1463.5 | 82912.6648 | 1466.5 | 1.8324 | 1427 | #REF!
1469 | 77312.6648 | 1472 | 124118.9988 | 1475 | 122168.9988 | 1477.5 | 82745.9982 | 1480.5 | 82645.9982 | 1483 | 82412.6648 | 1486 | 114118.9988 | 1488.5 | 124468.9988 | 1491.5 | 82379.3315 | 1494.5 | 82012.6648 | 1497 | 124668.9988 | 1500 | 82845.9982 | 1502.5 | 83279.3315 | 1505.5 | 82912.6648 | 1508.5 | 2356.6107 | 1469 | #REF!
1511 | 77312.6648 | 1514 | 124118.9988 | 1516.5 | 122168.9988 | 1519.5 | 124168.9988 | 1522.5 | 82645.9982 | 1525 | 82412.6648 | 1528 | 114118.9988 | 1530.5 | 124468.9988 | 1533.5 | 82379.3315 | 1536.5 | 82012.6648 | 1539 | 124668.9988 | 1542 | 82845.9982 | 1544.5 | 83279.3315 | 1547.5 | 82912.6648 | 1550.5 | 11370.1046 | 1511 | #REF!
1553 | 77312.6648 | 1556 | 124118.9988 | 1559 | 122168.9988 | 1561.5 | 124168.9988 | 1564.5 | 82645.9982 | 1567 | 82412.6648 | 1570 | 114118.9988 | 1572.5 | 124468.9988 | 1575.5 | 82379.3315 | 1578.5 | 82012.6648 | 1581 | 124668.9988 | 1584 | 82845.9982 | 1586.5 | 83279.3315 | 1589.5 | 82912.6648 | 1592.5 | 551.4013 | 1553 | #REF!
1595 | 57959.4976 | 1598 | 124118.9988 | 1600.5 | 122168.9988 | 1603.5 | 124168.9988 | 1606.5 | 82645.9982 | 1609 | 82412.6648 | 1612 | 114118.9988 | 1614.5 | 124468.9988 | 1617.5 | 82379.3315 | 1620.5 | 10164.0687 | 1623 | 1695.1526 | 1626 | 928.1085 | 1628.5 | 783.7071 | 1631.5 | 406.9059 | 1634.5 | 18.3459 | 1595 | #REF!
1637 | 231438.6459 | 1640 | 82712.6648 | 1642.5 | 122168.9988 | 1645.5 | 124168.9988 | 1648.5 | 82645.9982 | 1651 | 82412.6648 | 1654 | 76045.9982 | 1656.5 | 124468.9988 | 1659.5 | 123618.9988 | 1662.5 | 66.7941 | 1665 | 42.5166 | 1668 | 27.686 | 1670.5 | 135.7794 | 1673.5 | 154.043 | 1676.5 | 27.8159 | 1637 | #REF!
1679 | 57709.8876 | 1682 | 124118.9988 | 1684.5 | 81412.6648 | 1687.5 | 82745.9982 | 1690 | 82645.9982 | 1693 | 82412.6648 | 1696 | 76045.9982 | 1698.5 | 124468.9988 | 1701.5 | 82379.3315 | 1704.5 | 7.23 | 1707 | 23.046 | 1710 | 30.6472 | 1712.5 | 122.8539 | 1715.5 | 123.0743 | 1718.5 | 7727.5225 | 1679 | #REF!
1721 | 1665.2898 | 1724 | 9763.5681 | 1726.5 | 81412.6648 | 1729.5 | 82745.9982 | 1732.5 | 82645.9982 | 1735 | 123668.9988 | 1738 | 76045.9982 | 1740.5 | 124468.9988 | 1743.5 | 82379.3315 | 1746.5 | 4.6711 | 1749 | 27.243 | 1752 | 16.3627 | 1754.5 | 144.3698 | 1757.5 | 117.1832 | 1760.5 | 28.8375 | 1721 | #REF!
1763 | 7.5254 | 1766 | 16246.5245 | 1768.5 | 81412.6648 | 1771.5 | 82745.9982 | 1774.5 | 124018.9988 | 1777 | 82412.6648 | 1780 | 76045.9982 | 1782.5 | 124468.9988 | 1785.5 | 82379.3315 | 1788.5 | 8.9038 | 1791 | 16.1882 | 1794 | 18.6551 | 1796.5 | 82.2832 | 1799.5 | 36.2555 | 1802.5 | 24.8434 | 1763 | #REF!
1805 | 4.0058 | 1808 | 19089.5702 | 1810.5 | 81412.6648 | 1813.5 | 124168.9988 | 1816.5 | 82645.9982 | 1819 | 123668.9988 | 1822 | 76045.9982 | 1824.5 | 124468.9988 | 1827.5 | 82379.3315 | 1830.5 | 1105.2791 | 1833 | 19.4038 | 1836 | 12.815 | 1838.5 | 12.7232 | 1841.5 | 12.0124 | 1844.5 | 9.8438 | 1805 | #REF!
1847 | 14.3053 | 1850 | 34641.0202 | 1852.5 | 96076.964 | 1855.5 | 82745.9982 | 1858.5 | 82645.9982 | 1861 | 82412.6648 | 1864 | 76045.9982 | 1866.5 | 124468.9988 | 1869.5 | 123618.9988 | 1872.5 | 5912.2265 | 1875 | 6.5202 | 1878 | 13.8302 | 1880.5 | 21.4928 | 1883.5 | 18.2857 | 1886.5 | 21.7559 | 1847 | #REF!
1889 | 8.8121 | 1892 | 31752.825 | 1894.5 | 44083.2902 | 1897.5 | 133659.2852 | 1900.5 | 82645.9982 | 1903 | 82412.6648 | 1906 | 76045.9982 | 1908.5 | 124468.9988 | 1911.5 | 123618.9988 | 1914.5 | 7076.3116 | 1917 | 6.0962 | 1920 | 20.0133 | 1922.5 | 10.5034 | 1925.5 | 32.2496 | 1928.5 | 4.238 | 1889 | #REF!
1931 | 49.0319 | 1934 | 25987.5364 | 1936.5 | 114128.0732 | 1939.5 | 82745.9982 | 1942.5 | 82645.9982 | 1945 | 82412.6648 | 1948 | 76045.9982 | 1950.5 | 82945.9982 | 1953.5 | 73996.7217 | 1956.5 | 0.23668 | 1959 | 30.6658 | 1962 | 0.53559 | 1964.5 | 20.5269 | 1967.5 | 33.7062 | 1970.5 | 4.4206 | 1931 | #REF!
1973 | 48.9899 | 1976 | 7595.9737 | 1978.5 | 124522.9273 | 1981.5 | 124168.9988 | 1984.5 | 124018.9988 | 1987 | 82412.6648 | 1990 | 114118.9988 | 1992.5 | 82945.9982 | 1995.5 | 82379.3315 | 1998.5 | 0.65765 | 2001 | 4.9812 | 2004 | 3.9085 | 2006.5 | 33.7128 | 2009.5 | 4.1291 | 2012.5 | 0.050445 | 1973 | #REF!
2015 | 4.0244 | 2018 | 16579.1868 | 2020.5 | 25747.2995 | 2023.5 | 82745.9982 | 2026.5 | 82645.9982 | 2029 | 82412.6648 | 2032 | 76045.9982 | 2034.5 | 124468.9988 | 2037.5 | 82379.3315 | 2040.5 | 27.6026 | 2043 | 24.3722 | 2046 | 30.156 | 2048.5 | 20.0496 | 2051.5 | 16.5136 | 2054.5 | 8.1559 | 2015 | #REF!
2057 | 7.5543 | 2060 | 10586.0872 | 2062.5 | 81412.6648 | 2065.5 | 82745.9982 | 2068.5 | 124018.9988 | 2071 | 82412.6648 | 2074 | 76045.9982 | 2076.5 | 124468.9988 | 2079.5 | 123618.9988 | 2082.5 | 23.395 | 2085 | 26.1187 | 2088 | 16.419 | 2090.5 | 35.3447 | 2093.5 | 7.5932 | 2096.5 | 5.7626 | 2057 | #REF!
2099 | 21.327 | 2102 | 14084.2191 | 2104.5 | 10178.5322 | 2107.5 | 124168.9988 | 2110.5 | 82645.9982 | 2113 | 82412.6648 | 2116 | 76045.9982 | 2118.5 | 82945.9982 | 2121.5 | 82379.3315 | 2124.5 | 23.0776 | 2127 | 24.8205 | 2130 | 21.708 | 2132.5 | 6.8271 | 2135.5 | 15.6744 | 2138.5 | 0.75434 | 2099 | #REF!
2141 | 29.7927 | 2144 | 13802.2705 | 2146.5 | 40145.5662 | 2149.5 | 82745.9982 | 2152.5 | 124018.9988 | 2155 | 82412.6648 | 2157.5 | 114118.9988 | 2160.5 | 124468.9988 | 2163.5 | 123618.9988 | 2166.5 | 20.2909 | 2169 | 0.9931 | 2172 | 24.2111 | 2174.5 | 12.9341 | 2177.5 | 13.1724 | 2180.5 | 0.55242 | 2141 | #REF!
2183 | 33.8765 | 2186 | 29533.2491 | 2188.5 | 81412.6648 | 2191.5 | 82745.9982 | 2194 | 11144.9199 | 2197 | 82412.6648 | 2200 | 114118.9988 | 2202.5 | 124468.9988 | 2205.5 | 82379.3315 | 2208.5 | 5.3232 | 2211 | 0.27222 | 2214 | 0.19716 | 2216.5 | 15.691 | 2219.5 | 17.7084 | 2222.5 | 12.6315 | 2183 | #REF!
2225 | 31.0927 | 2228 | 6011.6906 | 2230.5 | 15275.9443 | 2233.5 | 124168.9988 | 2236.5 | 124018.9988 | 2239 | 123668.9988 | 2241.5 | 114118.9988 | 2244.5 | 124468.9988 | 2247.5 | 123618.9988 | 2250 | 0.57339 | 2253 | 8.6901 | 2256 | 22.6351 | 2258.5 | 3.8713 | 2261.5 | 27.6549 | 2264 | 24.8434 | 2225 | #REF!
2267 | 3.3063 | 2269.5 | 2216.2799 | 2272.5 | 64192.0749 | 2275.5 | 82745.9982 | 2278.5 | 124018.9988 | 2281 | 123668.9988 | 2284 | 76045.9982 | 2286.5 | 124468.9988 | 2289.5 | 82379.3315 | 2292.5 | 0.14473 | 2295 | 5.722 | 2298 | 4.5452 | 2300.5 | 13.7852 | 2303.5 | 32.1776 | 2306.5 | 20.9008 | 2267 | #REF!
2309 | 9.8309 | 2312 | 23113.381 | 2314.5 | 122168.9988 | 2317.5 | 124168.9988 | 2320 | 124018.9988 | 2323 | 123668.9988 | 2325.5 | 114118.9988 | 2328.5 | 124468.9988 | 2331.5 | 123618.9988 | 2334.5 | 28.4228 | 2337 | 0.020138 | 2340 | 13.3471 | 2342.5 | 8.0261 | 2345.5 | 10.3148 | 2348.5 | 24.329 | 2309 | #REF!
2351 | 18.6988 | 2353.5 | 25937.5968 | 2356.5 | 81412.6648 | 2359.5 | 124168.9988 | 2362.5 | 82645.9982 | 2365 | 123668.9988 | 2368 | 114118.9988 | 2370.5 | 124468.9988 | 2373.5 | 123618.9988 | 2376.5 | 3.662 | 2379 | 6.4729 | 2382 | 29.8074 | 2384.5 | 23.0324 | 2387.5 | 5.647 | 2390.5 | 5.0181 | 2351 | #REF!
2393 | 20.5128 | 2396 | 24349.3017 | 2398.5 | 81412.6648 | 2401.5 | 82745.9982 | 2404 | 82645.9982 | 2407 | 82412.6648 | 2409.5 | 76045.9982 | 2412.5 | 124468.9988 | 2415.5 | 123618.9988 | 2418 | 25.794 | 2421 | 205.0503 | 2423.5 | 17.3836 | 2426.5 | 7.3994 | 2429.5 | 29.6349 | 2432.5 | 19.878 | 2393 | #REF!
2435 | 34.6145 | 2438 | 30891.185 | 2440.5 | 122168.9988 | 2443.5 | 82745.9982 | 2446 | 124018.9988 | 2449 | 123668.9988 | 2451.5 | 114118.9988 | 2454.5 | 124468.9988 | 2457.5 | 82379.3315 | 2460 | 22.3849 | 2463 | 7.812 | 2465.5 | 7.4574 | 2468.5 | 11.6285 | 2471.5 | 27.7895 | 2474.5 | 3.1555 | 2435 | #REF!
2477 | 44.1412 | 2480 | 6111.5698 | 2482.5 | 55569.8055 | 2485.5 | 82745.9982 | 2488 | 82645.9982 | 2491 | 82412.6648 | 2493.5 | 114118.9988 | 2496.5 | 124468.9988 | 2499.5 | 123618.9988 | 2502 | 14.4062 | 2505 | 8.1519 | 2507.5 | 7.796 | 2510.5 | 4.1869 | 2513.5 | 24.7607 | 2516.5 | 12.9497 | 2477 | #REF!
2519 | 5.9572 | 2521.5 | 17252.1203 | 2524.5 | 22821.8402 | 2527.5 | 82745.9982 | 2530 | 124018.9988 | 2533 | 82412.6648 | 2535.5 | 76045.9982 | 2538.5 | 124468.9988 | 2541.5 | 82379.3315 | 2544 | 2.5822 | 2547 | 26.5793 | 2549.5 | 16.9845 | 2552.5 | 7.2558 | 2555.5 | 3.2294 | 2558 | 5.2961
2561 | 14.5399 | 2563.5 | 31281.6545 | 2566.5 | 81412.6648 | 2569.5 | 82745.9982 | 2572 | 13404.3288 | 2575 | 82412.6648 | 2577.5 | 76045.9982 | 2580.5 | 82945.9982 | 2583.5 | 82379.3315 | 2586 | 13.4252 | 2589 | 23.1711 | 2591.5 | 4.9125 | 2594.5 | 17.774 | 2597.5 | 32.5384 | 2600 | 10.35
2603 | 0.70025 | 2605.5 | 4690.2229 | 2608.5 | 61034.4976 | 2611.5 | 62034.4976 | 2614 | 49547.5969 | 2617 | 49407.5969 | 2620 | 45587.5969 | 2622.5 | 62184.4976 | 2625.5 | 49387.5969 | 2628 | 11.8784 | 2631 | 29.0693 | 2634 | 11.8171 | 2636.5 | 12.356 | 2639.5 | 2.0818 | 2642.5 | 7.7175
2645 | 49.3595 | 2647.5 | 6007.3686 | 2650.5 | 30467.2451 | 2653.5 | 27515.3278 | 2656.5 | 27481.9945 | 2659 | 22403.4478 | 2662 | 20667.0842 | 2664.5 | 19064.4536 | 2667.5 | 17574.1343 | 2670 | 0.40057 | 2673 | 1.5511 | 2675.5 | 1.4777 | 2678.5 | 3.2012 | 2681.5 | 5.7871 | 2684 | 7.2343
2687 | 28.6071 | 2689.5 | 24449.5337 | 2692.5 | 12126.8878 | 2695.5 | 10705.986 | 2698 | 9829.5047 | 2701 | 9801.5047 | 2703.5 | 8058.4829 | 2706.5 | 11224.4411 | 2709.5 | 8147.915 | 2712 | 0.067509 | 2715 | 1.6807 | 2717.5 | 0.57805 | 2720.5 | 3.0681 | 2723.5 | 1.9075 | 2726 | 8.7459
2729 | 26.2269 | 2732 | 4115.9645 | 2734.5 | 5864.3164 | 2737.5 | 5961.8774 | 2740 | 5181.6309 | 2743 | 4570.4959 | 2745.5 | 4379.1453 | 2748.5 | 5200.7798 | 2751.5 | 4658.3913 | 2754 | 15.0139 | 2757 | 7.3301 | 2759.5 | 15.8587 | 2762.5 | 11.7319 | 2765.5 | 7.4485 | 2768 | 8.4502
2771 | 11.5904 | 2773.5 | 20529.8732 | 2776.5 | 30132.0615 | 2779.5 | 3304.5856 | 2782 | 3042.2049 | 2785 | 3114.7322 | 2787.5 | 2685.7792 | 2790.5 | 2731.0599 | 2793.5 | 2399.3133 | 2796 | 14.4612 | 2799 | 3.7534 | 2801.5 | 0.47321 | 2804.5 | 2.8471 | 2807.5 | 24.7607 | 2810 | 13.2696
2813 | 3.903 | 2815.5 | 17269.8169 | 2818.5 | 2529.3841 | 2821.5 | 2061.1298 | 2824 | 2286.8404 | 2827 | 1896.1985 | 2829.5 | 1921.5062 | 2832.5 | 2164.8238 | 2835.5 | 2170.0068 | 2838 | 23.2678 | 2841 | 16.0207 | 2843.5 | 2.305 | 2846.5 | 1.6692 | 2849.5 | 19.5753 | 2852 | 24.7789
2855 | 49.5706 | 2857.5 | 19428.7414 | 2860.5 | 1856.2277 | 2863.5 | 1888.2277 | 2866 | 1824.2468 | 2869 | 1630.9477 | 2872 | 1243.6492 | 2874.5 | 1246.5789 | 2877.5 | 1321.9512 | 2880 | 17.2771 | 2883 | 18.0049 | 2885.5 | 15.138 | 2888.5 | 21.1288 | 2891.5 | 17.9963 | 2894 | 0.71168
2897 | 2.8059 | 2899.5 | 26503.4642 | 2902.5 | 1266.0248 | 2905.5 | 1250.6377 | 2908 | 1234.4994 | 2911 | 1089.9596 | 2913.5 | 977.4083 | 2916.5 | 66.7496 | 2919.5 | 30.5389 | 2922 | 14.0227 | 2925 | 25.1426 | 2927.5 | 0.66307 | 2930.5 | 2.803 | 2933.5 | 22.3619 | 2936 | 18.9306
2939 | 14.2848 | 2941.5 | 37.3875 | 2944.5 | 943.8292 | 2947.5 | 18.394 | 2950 | 12.7515 | 2953 | 36.1916 | 2955.5 | 552.1009 | 2958.5 | 16.3359 | 2961.5 | 22.1864 | 2964 | 9.2547 | 2967 | 10.8957 | 2969.5 | 26.7499 | 2972.5 | 21.3712 | 2975.5 | 2.918 | 2978 | 16.908
2981 | 29.4259 | 2983.5 | 30.0148 | 2986.5 | 1146.9768 | 2989.5 | 26.8614 | 2992 | 25.2601 | 2995 | 10.352 | 2997.5 | 71.7618 | 3000.5 | 22.0408 | 3003.5 | 12.915 | 3006 | 16.6462 | 3009 | 1.4218 | 3011.5 | 10.0734 | 3014.5 | 24.4826 | 3017.5 | 17.0227 | 3020 | 3.5589
3023 | 26.3663 | 3025.5 | 38.5643 | 3028.5 | 4602.3118 | 3031.5 | 21.4374 | 3034 | 30.0489 | 3037 | 23.6194 | 3039.5 | 3382.7959 | 3042.5 | 33.2468 | 3045.5 | 12.2255 | 3048 | 21.6378 | 3051 | 25.2719 | 3053.5 | 9.3207 | 3056.5 | 30.9123 | 3059.5 | 25.9946 | 3062 | 11.1692
3065 | 1.9922 | 3067.5 | 10.5537 | 3070.5 | 1125.5213 | 3073.5 | 6.99 | 3076 | 7.0508 | 3079 | 6.1737 | 3081.5 | 90.7665 | 3084.5 | 6.6312 | 3087.5 | 10.8706 | 3090 | 21.948 | 3093 | 29.3442 | 3095.5 | 3.0563 | 3098.5 | 8.1717 | 3101.5 | 1.0013 | 3104 | 0.41398
3107 | 37.7073 | 3109.5 | 6.66 | 3112.5 | 5213.1764 | 3115.5 | 12.5189 | 3118 | 21.5341 | 3121 | 22.2363 | 3123.5 | 298.5526 | 3126.5 | 12.8466 | 3129.5 | 22.1243 | 3132 | 0.8245 | 3135 | 0.23073 | 3137.5 | 21.2191 | 3140.5 | 1.3252 | 3143.5 | 24.1843 | 3146 | 28.4952
3149 | 33.2651 | 3151.5 | 11.0147 | 3154.5 | 6978.3989 | 3157.5 | 33.1422 | 3160 | 32.6885 | 3163 | 32.6749 | 3165.5 | 1316.2566 | 3168.5 | 7.3958 | 3171.5 | 33.8717 | 3174 | 1.8303 | 3177 | 10.0837 | 3179.5 | 28.8409 | 3182.5 | 7.9776 | 3185.5 | 24.5039 | 3188 | 19.7588
3191 | 80.6508 | 3193.5 | 26.2796 | 3196.5 | 782.5227 | 3199.5 | 22.548 | 3202 | 15.7991 | 3205 | 20.1569 | 3207.5 | 358.9803 | 3210.5 | 20.2792 | 3213.5 | 10.3069 | 3216 | 20.8995 | 3219 | 7.6187 | 3221.5 | 9.1713 | 3224.5 | 24.1645 | 3227.5 | 6.3511 | 3230 | 7.0422
3233 | 12.1679 | 3235.5 | 27.7483 | 3238.5 | 2044.6255 | 3241.5 | 23.2365 | 3244 | 33.5672 | 3247 | 30.3803 | 3249.5 | 2047.4482 | 3252.5 | 21.1842 | 3255.5 | 25.4386 | 3258 | 3107.6669 | 3261 | 19.8179 | 3263.5 | 23.7659 | 3266.5 | 17.4313 | 3269.5 | 0.78776 | 3272 | 1.485

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 47 |  |  | 2006-08-30 | 11:56
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2
Penlight Time | A1-G |  | Penlight Time | A2-G | Penlight Time | B3-G | Penlight Time | B4-G | Penlight Time | C5-G | Penlight Time | C6-G | Penlight Time | Minimums Overall
-121.1 | 232138 |  | -112.1 | 228338 | -106.5 | 246238 | -103.2 | 228338 | -100.9 | 248338 | -98.8 | 247338 | -121.1 | 228338
-78.9 | 232138 |  | -70 | 228338 | -64.4 | 246238 | -61.1 | 228338 | -58.8 | 248338 | -56.8 | 247338 | -78.9 | 228338
-37.1 | 232138 |  | -28 | 228338 | -22.5 | 246238 | -19.2 | 27570.8889 | -16.9 | 248338 | -14.7 | 247338 | -37.1 | 27570.8889
4.9 | 232138 |  | 14 | 228338 | 19.5 | 246238 | 22.9 | 228338 | 25.1 | 248338 | 27.2 | 247338 | 4.9 | 228338
46.9 | 232138 |  | 55.9 | 228338 | 61.5 | 246238 | 64.8 | 228338 | 67.1 | 248338 | 69.2 | 247338 | 46.9 | 228338
89 | 232138 |  | 97.9 | 228338 | 103.5 | 246238 | 106.8 | 228338 | 109.2 | 248338 | 111.2 | 247338 | 89 | 228338
131 | 232138 |  | 139.9 | 228338 | 145.5 | 246238 | 148.9 | 228338 | 151.2 | 248338 | 153.3 | 247338 | 131 | 228338
172.9 | 232138 |  | 181.9 | 228338 | 187.5 | 246238 | 190.8 | 228338 | 193.1 | 248338 | 195.2 | 247338 | 172.9 | 228338
215 | 232138 |  | 223.9 | 228338 | 229.6 | 246238 | 232.8 | 228338 | 235.1 | 248338 | 237.2 | 247338 | 215 | 228338
256.9 | 232138 |  | 265.9 | 228338 | 271.5 | 246238 | 274.8 | 228338 | 277.1 | 248338 | 279.2 | 247338 | 256.9 | 228338
298.9 | 232138 |  | 307.9 | 228338 | 313.5 | 246238 | 316.8 | 228338 | 319.1 | 248338 | 321.2 | 247338 | 298.9 | 228338
340.9 | 232138 |  | 349.9 | 228338 | 355.5 | 246238 | 358.9 | 228338 | 361.1 | 248338 | 363.3 | 247338 | 340.9 | 228338
382.9 | 232138 |  | 391.9 | 228338 | 397.5 | 246238 | 400.8 | 228338 | 403.1 | 248338 | 405.2 | 247338 | 382.9 | 228338
424.9 | 232138 |  | 433.9 | 228338 | 439.5 | 246238 | 442.8 | 228338 | 445.1 | 248338 | 447.2 | 247338 | 424.9 | 228338
466.9 | 232138 |  | 475.9 | 228338 | 481.5 | 246238 | 484.8 | 228338 | 487.1 | 248338 | 489.2 | 247338 | 466.9 | 228338
508.9 | 232138 |  | 517.9 | 228338 | 523.5 | 246238 | 526.8 | 228338 | 529.1 | 248338 | 531.2 | 247338 | 508.9 | 228338
550.9 | 232138 |  | 559.9 | 228338 | 565.5 | 246238 | 568.8 | 228338 | 571.1 | 248338 | 573.2 | 247338 | 550.9 | 228338
592.9 | 232138 |  | 601.9 | 228338 | 607.5 | 246238 | 610.8 | 228338 | 613.1 | 248338 | 615.2 | 247338 | 592.9 | 228338
634.9 | 232138 |  | 643.9 | 228338 | 649.5 | 246238 | 652.8 | 228338 | 655.1 | 248338 | 657.2 | 247338 | 634.9 | 228338
676.9 | 232138 |  | 685.9 | 228338 | 691.5 | 246238 | 694.8 | 228338 | 697.1 | 248338 | 699.2 | 247338 | 676.9 | 228338
718.9 | 232138 |  | 727.9 | 228338 | 733.5 | 246238 | 736.8 | 228338 | 739.1 | 248338 | 741.2 | 247338 | 718.9 | 228338
760.9 | 232138 |  | 769.9 | 228338 | 775.5 | 124119 | 778.7 | 228338 | 781 | 248338 | 783.2 | 247338 | 760.9 | 124119
802.9 | 232138 |  | 811.9 | 228338 | 817.5 | 246238 | 820.8 | 228338 | 823.1 | 248338 | 825.2 | 247338 | 802.9 | 228338
844.9 | 232138 |  | 853.9 | 228338 | 859.4 | 246238 | 862.8 | 228338 | 865 | 248338 | 867.2 | 247338 | 844.9 | 228338
886.8 | 232138 |  | 895.7 | 228338 | 901.4 | 246238 | 904.8 | 228338 | 906.9 | 248338 | 909.2 | 247338 | 886.8 | 228338
928.8 | 232138 |  | 937.7 | 228338 | 943.3 | 246238 | 946.6 | 228338 | 948.8 | 248338 | 951.2 | 247338 | 928.8 | 228338
970.7 | 122169 |  | 979.7 | 228338 | 985.4 | 246238 | 988.6 | 228338 | 990.8 | 248338 | 993.2 | 247338 | 970.7 | 122169
1012.7 | 232138 |  | 1021.8 | 228338 | 1027.5 | 246238 | 1030.6 | 228338 | 1033 | 248338 | 1035.2 | 247338 | 1012.7 | 228338
1054.9 | 232138 |  | 1063.9 | 228338 | 1069.5 | 246238 | 1072.8 | 228338 | 1075.1 | 248338 | 1077.2 | 247338 | 1054.9 | 228338
1096.7 | 232138 |  | 1105.8 | 228338 | 1111.4 | 246238 | 1114.7 | 228338 | 1117 | 248338 | 1119.2 | 247338 | 1096.7 | 228338
1138.8 | 232138 |  | 1147.7 | 228338 | 1153.3 | 246238 | 1156.7 | 228338 | 1158.9 | 248338 | 1161.2 | 247338 | 1138.8 | 228338
1180.8 | 232138 |  | 1189.7 | 228338 | 1195.4 | 246238 | 1198.8 | 228338 | 1201.1 | 248338 | 1203.2 | 247338 | 1180.8 | 228338
1222.7 | 232138 |  | 1231.6 | 228338 | 1237.3 | 246238 | 1240.6 | 228338 | 1242.8 | 248338 | 1245.2 | 247338 | 1222.7 | 228338
1264.7 | 232138 |  | 1273.8 | 228338 | 1279.3 | 246238 | 1282.6 | 124969 | 1284.9 | 436.5832 | 1287.1 | 59.7672 | 1264.7 | 59.7672
1306.9 | 116019 |  | 1315.8 | 114119 | 1321.4 | 82012.6667 | 1324.7 | 82912.6667 | 1326.8 | 6.8345 | 1329.2 | 22.5039 | 1306.9 | 6.8345
1348.8 | 77312.6667 |  | 1357.7 | 82412.6667 | 1363.4 | 82012.6667 | 1366.8 | 82912.6667 | 1369.1 | 3.6779 | 1371.2 | 2.3183 | 1348.8 | 2.3183
1390.7 | 77312.6667 |  | 1399.6 | 82379.3333 | 1405.4 | 82012.6667 | 1408.7 | 82012.6667 | 1411 | 1.0728 | 1413.2 | 8.8054 | 1390.7 | 1.0728
1432.7 | 77312.6667 |  | 1441.6 | 77312.6667 | 1447.4 | 82012.6667 | 1450.6 | 82912.6667 | 1452.9 | 3.3006 | 1455.2 | 0.78621 | 1432.7 | 0.78621
1474.8 | 77312.6667 |  | 1483.6 | 77312.6667 | 1489.3 | 82012.6667 | 1492.7 | 81412.6667 | 1494.8 | 4.836 | 1497.2 | 1.9942 | 1474.8 | 1.9942
1516.7 | 77312.6667 |  | 1525.6 | 77312.6667 | 1531.3 | 82012.6667 | 1534.6 | 82912.6667 | 1536.8 | 2.5259 | 1539.2 | 9.3711 | 1516.7 | 2.5259
1558.8 | 77312.6667 |  | 1567.6 | 82379.3333 | 1573.3 | 82012.6667 | 1576.7 | 82912.6667 | 1578.8 | 2.2892 | 1581.2 | 4.1267 | 1558.8 | 2.2892
1600.7 | 57959.5 |  | 1609.6 | 77312.6667 | 1615.3 | 928.2562 | 1618.6 | 407.2057 | 1620.8 | 3.6007 | 1623.2 | 1.9394 | 1600.7 | 1.9394
1642.7 | 77312.6667 |  | 1651.6 | 76046 | 1657.3 | 28.8648 | 1660.6 | 136.4253 | 1662.8 | 0.66343 | 1665.2 | 1.1603 | 1642.7 | 0.66343
1684.6 | 81412.6667 |  | 1693.6 | 57934.4244 | 1699.3 | 8.6146 | 1702.6 | 100.1121 | 1704.8 | 1.0317 | 1707.1 | 3.7041 | 1684.6 | 1.0317
1726.7 | 10172.0081 |  | 1735.6 | 2628.288 | 1741.3 | 6.0887 | 1744.6 | 112.7271 | 1746.8 | 4.4604 | 1749.2 | 1.8977 | 1726.7 | 1.8977
1768.7 | 84.6914 |  | 1777.6 | 89.5669 | 1783.3 | 10.2677 | 1786.6 | 37.3624 | 1788.8 | 7.6325 | 1791.2 | 2.5353 | 1768.7 | 2.5353
1810.7 | 1184.9909 |  | 1819.6 | 1756.6912 | 1825.3 | 4.3978 | 1828.6 | 12.1024 | 1830.8 | 11.2077 | 1833.2 | 3.2175 | 1810.7 | 3.2175
1852.7 | 2097.8729 |  | 1861.6 | 5470.3678 | 1867.3 | 4.9779 | 1870.6 | 16.1865 | 1872.8 | 1.2756 | 1875.2 | 5.3376 | 1852.7 | 1.2756
1894.7 | 4783.1783 |  | 1903.6 | 10872.3852 | 1909.3 | 7.5131 | 1912.6 | 11.8685 | 1914.8 | 1.397 | 1917.2 | 2.5332 | 1894.7 | 1.397
1936.7 | 15168.0604 |  | 1945.6 | 3664.9444 | 1951.3 | 1.2487 | 1954.6 | 21.7809 | 1956.8 | 5.8534 | 1959.2 | 1.856 | 1936.7 | 1.2487
1978.7 | 7842.3642 |  | 1987.6 | 4658.0642 | 1993.3 | 2.1302 | 1996.6 | 5.5693 | 1998.8 | 1.4447 | 2001.2 | 1.7728 | 1978.7 | 1.4447
2020.7 | 219.2235 |  | 2029.6 | 247.4716 | 2035.3 | 21.8199 | 2038.6 | 11.7896 | 2040.8 | 0.70251 | 2043.2 | 1.243 | 2020.7 | 0.70251
2062.7 | 2040.98 |  | 2071.6 | 6112.0175 | 2077.3 | 6.468 | 2080.6 | 8.9882 | 2082.8 | 7.1777 | 2085.2 | 1.0363 | 2062.7 | 1.0363
2104.7 | 806.2783 |  | 2113.6 | 1568.2169 | 2119.3 | 20.5524 | 2122.6 | 4.3506 | 2124.8 | 2.2379 | 2127.2 | 5.0393 | 2104.7 | 2.2379
2146.7 | 5429.4762 |  | 2155.5 | 5429.4762 | 2161.3 | 2.4797 | 2164.5 | 11.8701 | 2166.8 | 0.95002 | 2169.2 | 2.0648 | 2146.7 | 0.95002
2188.6 | 6218.2467 |  | 2197.6 | 4637.6212 | 2203.3 | 1.6911 | 2206.6 | 14.8605 | 2208.8 | 7.2359 | 2211.1 | 4.3602 | 2188.6 | 1.6911
2230.7 | 6323.0407 |  | 2239.5 | 28651.7652 | 2245.2 | 0.91684 | 2248.4 | 5.3213 | 2250.7 | 21.1172 | 2253.1 | 10.1938 | 2230.7 | 0.91684
2272.6 | 2258.4261 |  | 2281.6 | 2948.8529 | 2287.2 | 1.6246 | 2290.6 | 15.1118 | 2292.8 | 7.6655 | 2295.2 | 1.3586 | 2272.6 | 1.3586
2314.6 | 4026.7072 |  | 2323.5 | 5294.0911 | 2329.3 | 1.5207 | 2332.5 | 9.4217 | 2334.8 | 18.8869 | 2337.1 | 1.3619 | 2314.6 | 1.3619
2356.6 | 142.8082 |  | 2365.6 | 149.9625 | 2371.2 | 5.093 | 2374.6 | 3.8087 | 2376.8 | 0.90278 | 2379.2 | 1.1977 | 2356.6 | 0.90278
2398.6 | 462.1944 |  | 2407.5 | 463.4942 | 2413.1 | 13.3416 | 2416.4 | 3.1566 | 2418.8 | 0.66075 | 2421 | 6.13 | 2398.6 | 0.66075
2440.6 | 2129.7427 |  | 2449.5 | 1722.5667 | 2455.1 | 1.8675 | 2458.4 | 9.7763 | 2460.8 | 4.6055 | 2463 | 1.1117 | 2440.6 | 1.1117
2482.6 | 553.5615 |  | 2491.5 | 460.1617 | 2497.1 | 5.1834 | 2500.4 | 4.8693 | 2502.8 | 4.1912 | 2505 | 3.6917 | 2482.6 | 3.6917
2524.5 | 274.8423 |  | 2533.5 | 451.6718 | 2539 | 4.0279 | 2542.4 | 4.6818 | 2544.7 | 0.65915 | 2546.9 | 0.74534 | 2524.5 | 0.65915
2566.5 | 12721.6844 |  | 2575.5 | 76046 | 2581 | 6.341 | 2584.4 | 11.3141 | 2586.7 | 11.7077 | 2588.9 | 2.4025 | 2566.5 | 2.4025
2608.5 | 27.1219 |  | 2617.6 | 28.3469 | 2623.1 | 3.9338 | 2626.5 | 3.5501 | 2628.8 | 2.9496 | 2631.1 | 0.66209 | 2608.5 | 0.66209
2650.6 | 3436.7313 |  | 2659.6 | 2083.9464 | 2665 | 1.8768 | 2668.5 | 4.6603 | 2670.7 | 8.6305 | 2673 | 1.4861 | 2650.6 | 1.4861
2692.5 | 4000.2261 |  | 2701.5 | 1384.7691 | 2707 | 1.4154 | 2710.4 | 3.3782 | 2712.7 | 10.1232 | 2714.9 | 2.7566 | 2692.5 | 1.4154
2734.6 | 1784.9373 |  | 2743.5 | 2173.3994 | 2749.1 | 3.4836 | 2752.4 | 3.0501 | 2754.7 | 1.5646 | 2756.9 | 0.66262 | 2734.6 | 0.66262
2776.5 | 2277.2812 |  | 2785.5 | 1136.6539 | 2791 | 1.0305 | 2794.4 | 4.3111 | 2796.7 | 4.4604 | 2798.9 | 0.66423 | 2776.5 | 0.66423
2818.5 | 918.4604 |  | 2827.5 | 1896.2742 | 2833 | 3.769 | 2836.4 | 2.8335 | 2838.7 | 10.2869 | 2840.9 | 0.94771 | 2818.5 | 0.94771
2860.5 | 1824.3256 |  | 2869.6 | 971.077 | 2875 | 16.4427 | 2878.5 | 5.9065 | 2880.7 | 2.1958 | 2882.9 | 0.6637 | 2860.5 | 0.6637
2902.5 | 186.3854 |  | 2911.5 | 31.686 | 2917 | 2.1502 | 2920.4 | 0.67435 | 2922.7 | 0.69968 | 2924.9 | 2.0784 | 2902.5 | 0.67435
2944.5 | 12.8814 |  | 2953.5 | 17.6289 | 2959 | 2.7982 | 2962.4 | 2.118 | 2964.7 | 0.74023 | 2966.9 | 0.6664 | 2944.5 | 0.6664
2986.5 | 11.0053 |  | 2995.5 | 0.91048 | 3001 | 2.9023 | 3004.4 | 2.9841 | 3006.7 | 5.0034 | 3008.9 | 6.2208 | 2986.5 | 0.91048
3028.5 | 11.7084 |  | 3037.5 | 10.1552 | 3043 | 1.5332 | 3046.4 | 17.0351 | 3048.7 | 2.9143 | 3050.9 | 1.6536 | 3028.5 | 1.5332
3070.5 | 0.29353 |  | 3079.5 | 0.7273 | 3085 | 4.5099 | 3088.4 | 2.4848 | 3090.7 | 1.9024 | 3092.9 | 0.87159 | 3070.5 | 0.29353
3112.5 | 8.0635 |  | 3121.5 | 10.9221 | 3127 | 0.66939 | 3130.4 | 2.8105 | 3132.7 | 1.8969 | 3134.9 | 16.9901 | 3112.5 | 0.66939
3154.5 | 9.9429 |  | 3163.5 | 8.7939 | 3169 | 1.3206 | 3172.4 | 9.3739 | 3174.7 | 10.9058 | 3176.9 | 1.6067 | 3154.5 | 1.3206
3196.5 | 8.7301 |  | 3205.5 | 2.9696 | 3211 | 0.6637 | 3214.4 | 7.762 | 3216.7 | 0.94733 | 3218.9 | 4.466 | 3196.5 | 0.6637
3238.5 | 5.012 |  | 3247.5 | 21.341 | 3253 | 2.6179 | 3256.4 | 2.2743 | 3258.7 | 2.9581 | 3260.9 | 1.7728 | 3238.5 | 1.7728

## C5-C6
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.6716 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
38959.4964 | 1 | 0 | 38959.4964 | 1 | 0 |  | -87.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4969 | 1 | 0 | 38959.4969 | 1 | 0 |  | -45.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4974 | 1 | 0 | 38959.4974 | 1 | 0 |  | -3.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4978 | 1 | 0 | 38959.4979 | 1 | 0 |  | 38.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4983 | 1 | 0 | 38959.4983 | 1 | 0 |  | 80.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4988 | 1 | 0 | 38959.4988 | 1 | 0 |  | 122.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4993 | 1 | 0 | 38959.4993 | 1 | 0 |  | 164.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4998 | 1 | 0 | 38959.4998 | 1 | 0 |  | 206.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5003 | 1 | 0 | 38959.5003 | 1 | 0 |  | 248.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5008 | 1 | 0 | 38959.5008 | 1 | 0 |  | 290.5 | 417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5013 | 1 | 0 | 38959.5013 | 1 | 0 |  | 332.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5017 | 1 | 0 | 38959.5017 | 1 | 0 |  | 374.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5022 | 1 | 0 | 38959.5022 | 1 | 0 |  | 416.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5027 | 1 | 0 | 38959.5027 | 1 | 0 |  | 458.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5032 | 1 | 0 | 38959.5032 | 1 | 0 |  | 500.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5037 | 1 | 0 | 38959.5037 | 1 | 0 |  | 542.5 | 669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5042 | 1 | 0 | 38959.5042 | 1 | 0 |  | 584.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5047 | 1 | 0 | 38959.5047 | 1 | 0 |  | 626.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5051 | 1 | 0 | 38959.5052 | 1 | 0 |  | 668.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5056 | 1 | 0 | 38959.5056 | 1 | 0 |  | 710.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5061 | 1 | 0 | 38959.5061 | 1 | 0 |  | 752.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5066 | 1 | 0 | 38959.5066 | 1 | 0 |  | 794.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5071 | 1 | 0 | 38959.5071 | 1 | 0 |  | 836.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5076 | 1 | 0 | 38959.5076 | 1 | 0 |  | 878.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5081 | 1 | 0 | 38959.5081 | 1 | 0 |  | 920.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5085 | 1 | 0 | 38959.5086 | 1 | 0 |  | 962.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.509 | 1 | 0 | 38959.509 | 1 | 0 |  | 1004.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5095 | 1 | 0 | 38959.5095 | 1 | 0 |  | 1046.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.51 | 1 | 0 | 38959.51 | 1 | 0 |  | 1088.5 | 1215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5105 | 1 | 0 | 38959.5105 | 1 | 0 |  | 1130.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.511 | 1 | 0 | 38959.511 | 1 | 0 |  | 1172.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5115 | 1 | 0 | 38959.5115 | 1 | 0 |  | 1214.5 | 1341.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5119 | 1 | 0 | 38959.512 | 1 | 0 |  | 1256.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5124 | 463 | 0 | 38959.5124 | 1555 | 0 |  | 1298.5 | 1425.5 | 28.2662 | 0 | 94.9328 | 0 | 0.28266 | 0 | 0.94933 | 0 | 0.28266 | 0.94933 | 436.5832 | 59.7672 | 436.3005
38959.5129 | 1951 | 0 | 38959.5129 | 2028 | 0 |  | 1340.5 | 1467.5 | 119.1087 | 0 | 123.8095 | 0 | 1.1911 | 0 | 1.2381 | 0 | 1.1911 | 1.2381 | 27.3388 | 22.5039 | 26.1477
38959.5134 | 2107 | 0 | 38959.5134 | 2111 | 0 |  | 1382.5 | 1509.5 | 128.6325 | 0 | 128.8767 | 0 | 1.2863 | 0 | 1.2888 | 0 | 1.2863 | 1.2888 | 17.9108 | 17.6874 | 16.6244
38959.5139 | 1932 | 0 | 38959.5139 | 1962 | 0 |  | 1424.5 | 1551.5 | 117.9487 | 0 | 119.7802 | 0 | 1.1795 | 0 | 1.1978 | 0 | 1.1795 | 1.1978 | 28.5911 | 26.6249 | 27.4116
38959.5144 | 2405 | 0 | 38959.5144 | 2465 | 0 |  | 1466.5 | 1593.5 | 146.8254 | 0 | 150.4884 | 0 | 1.4683 | 0 | 1.5049 | 0 | 1.4683 | 1.5049 | 3.3006 | 0.78621 | 1.8324
38959.5149 | 2370 | 1 | 38959.5149 | 1968 | 0 |  | 1508.5 | 1635.5 | 144.6886 | 0.06105 | 120.1465 | 0 | 1.4469 | 0.0006105 | 1.2015 | 0 | 1.4463 | 1.2015 | 4.836 | 26.2388 | 2356.6107
38959.5153 | 2001 | 1 | 38959.5154 | 1900 | 1 |  | 1550.5 | 1677.5 | 122.1612 | 0.06105 | 115.9951 | 0.06105 | 1.2216 | 0.0006105 | 1.16 | 0.0006105 | 1.221 | 1.1593 | 24.2082 | 30.8401 | 11370.1046
38959.5158 | 2429 | 1 | 38959.5158 | 2237 | 1 |  | 1592.5 | 1719.5 | 148.2906 | 0.06105 | 136.569 | 0.06105 | 1.4829 | 0.0006105 | 1.3657 | 0.0006105 | 1.4823 | 1.3651 | 2.2892 | 11.2839 | 551.4013
38959.5163 | 2077 | 0 | 38959.5163 | 2022 | 1 |  | 1634.5 | 1761.5 | 126.801 | 0 | 123.4432 | 0.06105 | 1.268 | 0 | 1.2344 | 0.0006105 | 1.268 | 1.2338 | 19.6139 | 22.9283 | 18.3459
38959.5168 | 1926 | 0 | 38959.5168 | 2325 | 1 |  | 1676.5 | 1803.5 | 117.5824 | 0 | 141.9414 | 0.06105 | 1.1758 | 0 | 1.4194 | 0.0006105 | 1.1758 | 1.4188 | 28.9917 | 6.901 | 27.8159
38959.5173 | 2059 | 1 | 38959.5173 | 2032 | 0 |  | 1718.5 | 1845.5 | 125.7021 | 0.06105 | 124.0537 | 0 | 1.257 | 0.0006105 | 1.2405 | 0 | 1.2564 | 1.2405 | 20.7148 | 22.2628 | 7727.5225
38959.5178 | 1911 | 0 | 38959.5178 | 1930 | 1 |  | 1760.5 | 1887.5 | 116.6667 | 0 | 117.8266 | 0.06105 | 1.1667 | 0 | 1.1783 | 0.0006105 | 1.1667 | 1.1777 | 30.0042 | 28.7911 | 28.8375
38959.5183 | 1971 | 0 | 38959.5183 | 2262 | 0 |  | 1802.5 | 1929.5 | 120.3297 | 0 | 138.0952 | 0 | 1.2033 | 0 | 1.381 | 0 | 1.2033 | 1.381 | 26.0467 | 9.8311 | 24.8434
38959.5188 | 2234 | 0 | 38959.5188 | 1984 | 0 |  | 1844.5 | 1971.5 | 136.3858 | 0 | 121.1233 | 0 | 1.3639 | 0 | 1.2112 | 0 | 1.3639 | 1.2112 | 11.2077 | 25.2208 | 9.8438
38959.5192 | 2020 | 0 | 38959.5192 | 2017 | 0 |  | 1886.5 | 2013.5 | 123.3211 | 0 | 123.138 | 0 | 1.2332 | 0 | 1.2314 | 0 | 1.2332 | 1.2314 | 22.9891 | 23.172 | 21.7559
38959.5197 | 2351 | 0 | 38959.5197 | 2423 | 0 |  | 1928.5 | 2055.5 | 143.5287 | 0 | 147.9243 | 0 | 1.4353 | 0 | 1.4792 | 0 | 1.4353 | 1.4792 | 5.6733 | 2.5332 | 4.238
38959.5202 | 2347 | 0 | 38959.5202 | 1993 | 0 |  | 1970.5 | 2097.5 | 143.2845 | 0 | 121.6728 | 0 | 1.4328 | 0 | 1.2167 | 0 | 1.4328 | 1.2167 | 5.8534 | 24.6553 | 4.4206
38959.5207 | 2449 | 0 | 38959.5207 | 2289 | 1 |  | 2012.5 | 2139.5 | 149.5116 | 0 | 139.7436 | 0.06105 | 1.4951 | 0 | 1.3974 | 0.0006105 | 1.4951 | 1.3968 | 1.4447 | 8.583 | 0.050445
38959.5212 | 2268 | 0 | 38959.5212 | 2051 | 0 |  | 2054.5 | 2181.5 | 138.4615 | 0 | 125.2137 | 0 | 1.3846 | 0 | 1.2521 | 0 | 1.3846 | 1.2521 | 9.5406 | 21.1302 | 8.1559
38959.5217 | 2318 | 0 | 38959.5217 | 2454 | 0 |  | 2096.5 | 2223.5 | 141.514 | 0 | 149.8168 | 0 | 1.4151 | 0 | 1.4982 | 0 | 1.4151 | 1.4982 | 7.1777 | 1.238 | 5.7626
38959.5222 | 2430 | 0 | 38959.5222 | 1970 | 0 |  | 2138.5 | 2265.5 | 148.3516 | 0 | 120.2686 | 0 | 1.4835 | 0 | 1.2027 | 0 | 1.4835 | 1.2027 | 2.2379 | 26.1107 | 0.75434
38959.5226 | 2461 | 0 | 38959.5227 | 2257 | 0 |  | 2180.5 | 2307.5 | 150.2442 | 0 | 137.79 | 0 | 1.5024 | 0 | 1.3779 | 0 | 1.5024 | 1.3779 | 0.95002 | 10.0744 | 0.55242
38959.5231 | 2180 | 0 | 38959.5231 | 2034 | 0 |  | 2222.5 | 2349.5 | 133.0891 | 0 | 124.1758 | 0 | 1.3309 | 0 | 1.2418 | 0 | 1.3309 | 1.2418 | 13.9624 | 22.1426 | 12.6315
38959.5236 | 1971 | 0 | 38959.5236 | 2158 | 0 |  | 2264 | 2391 | 120.3297 | 0 | 131.746 | 0 | 1.2033 | 0 | 1.3175 | 0 | 1.2033 | 1.3175 | 26.0467 | 15.1242 | 24.8434
38959.5241 | 2034 | 0 | 38959.5241 | 2140 | 0 |  | 2306.5 | 2433.5 | 124.1758 | 0 | 130.6471 | 0 | 1.2418 | 0 | 1.3065 | 0 | 1.2418 | 1.3065 | 22.1426 | 16.0925 | 20.9008
38959.5246 | 1979 | 0 | 38959.5246 | 2451 | 0 |  | 2348.5 | 2475.5 | 120.8181 | 0 | 149.6337 | 0 | 1.2082 | 0 | 1.4963 | 0 | 1.2082 | 1.4963 | 25.5371 | 1.3619 | 24.329
38959.5251 | 2334 | 0 | 38959.5251 | 2070 | 0 |  | 2390.5 | 2517.5 | 142.4908 | 0 | 126.3736 | 0 | 1.4249 | 0 | 1.2637 | 0 | 1.4249 | 1.2637 | 6.443 | 20.0184 | 5.0181
38959.5256 | 2051 | 0 | 38959.5256 | 2095 | 0 |  | 2432.5 | 2559.5 | 125.2137 | 0 | 127.8999 | 0 | 1.2521 | 0 | 1.279 | 0 | 1.2521 | 1.279 | 21.1302 | 18.5862 | 19.878
38959.526 | 2375 | 0 | 38959.5261 | 2084 | 0 |  | 2474.5 | 2601.5 | 144.9939 | 0 | 127.2283 | 0 | 1.4499 | 0 | 1.2723 | 0 | 1.4499 | 1.2723 | 4.6055 | 19.2121 | 3.1555
38959.5265 | 2174 | 0 | 38959.5265 | 1958 | 0 |  | 2516.5 | 2643.5 | 132.7228 | 0 | 119.536 | 0 | 1.3272 | 0 | 1.1954 | 0 | 1.3272 | 1.1954 | 14.2769 | 26.8836 | 12.9497
38959.527 | 2328 | 0 | 38959.527 | 2466 | 0 |  | 2558 | 2685 | 142.1245 | 0 | 150.5495 | 0 | 1.4212 | 0 | 1.5055 | 0 | 1.4212 | 1.5055 | 6.7174 | 0.74534 | 5.2961
38959.5275 | 2224 | 0 | 38959.5275 | 2414 | 0 |  | 2600 | 2727 | 135.7753 | 0 | 147.3748 | 0 | 1.3578 | 0 | 1.4737 | 0 | 1.3578 | 1.4737 | 11.7077 | 2.9155 | 10.35
38959.528 | 2277 | 0 | 38959.528 | 2051 | 0 |  | 2642.5 | 2769.5 | 139.011 | 0 | 125.2137 | 0 | 1.3901 | 0 | 1.2521 | 0 | 1.3901 | 1.2521 | 9.1076 | 21.1302 | 7.7175
38959.5285 | 2287 | 0 | 38959.5285 | 2448 | 0 |  | 2684 | 2811 | 139.6215 | 0 | 149.4505 | 0 | 1.3962 | 0 | 1.4945 | 0 | 1.3962 | 1.4945 | 8.6305 | 1.4861 | 7.2343
38959.5289 | 2256 | 0 | 38959.529 | 1976 | 0 |  | 2726 | 2853 | 137.7289 | 0 | 120.6349 | 0 | 1.3773 | 0 | 1.2063 | 0 | 1.3773 | 1.2063 | 10.1232 | 25.7277 | 8.7459
38959.5294 | 2262 | 0 | 38959.5295 | 2447 | 0 |  | 2768 | 2895 | 138.0952 | 0 | 149.3895 | 0 | 1.381 | 0 | 1.4939 | 0 | 1.381 | 1.4939 | 9.8311 | 1.5276 | 8.4502
38959.5299 | 2168 | 0 | 38959.5299 | 2036 | 0 |  | 2810 | 2937 | 132.3565 | 0 | 124.2979 | 0 | 1.3236 | 0 | 1.243 | 0 | 1.3236 | 1.243 | 14.5932 | 22.0226 | 13.2696
38959.5304 | 1972 | 0 | 38959.5304 | 2157 | 0 |  | 2852 | 2979 | 120.3907 | 0 | 131.685 | 0 | 1.2039 | 0 | 1.3168 | 0 | 1.2039 | 1.3168 | 25.9828 | 15.1776 | 24.7789
38959.5309 | 2431 | 0 | 38959.5309 | 2468 | 0 |  | 2894 | 3021 | 148.4127 | 0 | 150.6716 | 0 | 1.4841 | 0 | 1.5067 | 0 | 1.4841 | 1.5067 | 2.1958 | 0.6637 | 0.71168
38959.5314 | 2067 | 0 | 38959.5314 | 2125 | 0 |  | 2936 | 3063 | 126.1905 | 0 | 129.7314 | 0 | 1.2619 | 0 | 1.2973 | 0 | 1.2619 | 1.2973 | 20.1925 | 16.912 | 18.9306
38959.5319 | 2102 | 0 | 38959.5319 | 2389 | 0 |  | 2978 | 3105 | 128.3272 | 0 | 145.8486 | 0 | 1.2833 | 0 | 1.4585 | 0 | 1.2833 | 1.4585 | 18.1912 | 3.9925 | 16.908
38959.5323 | 2366 | 0 | 38959.5324 | 2334 | 0 |  | 3020 | 3147 | 144.4444 | 0 | 142.4908 | 0 | 1.4444 | 0 | 1.4249 | 0 | 1.4444 | 1.4249 | 5.0034 | 6.443 | 3.5589
38959.5328 | 2208 | 0 | 38959.5329 | 2005 | 0 |  | 3062 | 3189 | 134.7985 | 0 | 122.4054 | 0 | 1.348 | 0 | 1.2241 | 0 | 1.348 | 1.2241 | 12.5172 | 23.9092 | 11.1692
38959.5333 | 2438 | 0 | 38959.5333 | 1978 | 0 |  | 3104 | 3231 | 148.84 | 0 | 120.757 | 0 | 1.4884 | 0 | 1.2076 | 0 | 1.4884 | 1.2076 | 1.9024 | 25.6006 | 0.41398
38959.5338 | 1916 | 0 | 38959.5338 | 2052 | 0 |  | 3146 | 3273 | 116.9719 | 0 | 125.2747 | 0 | 1.1697 | 0 | 1.2527 | 0 | 1.1697 | 1.2527 | 29.6649 | 21.0712 | 28.4952
38959.5343 | 2053 | 0 | 38959.5343 | 2018 | 0 |  | 3188 | 3315 | 125.3358 | 0 | 123.199 | 0 | 1.2534 | 0 | 1.232 | 0 | 1.2534 | 1.232 | 21.0122 | 23.111 | 19.7588
38959.5348 | 2291 | 0 | 38959.5348 | 2110 | 0 |  | 3230 | 3357 | 139.8657 | 0 | 128.8156 | 0 | 1.3987 | 0 | 1.2882 | 0 | 1.3987 | 1.2882 | 8.4409 | 17.7431 | 7.0422
38959.5353 | 2413 | 0 | 38959.5353 | 1942 | 0 |  | 3272 | 3399 | 147.3138 | 0 | 118.5592 | 0 | 1.4731 | 0 | 1.1856 | 0 | 1.4731 | 1.1856 | 2.9581 | 27.9289 | 1.485

## B4-C6
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 152.0379 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
38959.4964 | 1 | 0 | 38959.4964 | 1 | 0 |  | -90.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4968 | 1 | 0 | 38959.4969 | 1 | 0 |  | -48.5 | 78.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4973 | 9 | 0 | 38959.4973 | 1 | 0 |  | -6.5 | 120.5 | 0.54945 | 0 | 0.06105 | 0 | 0.0054945 | 0 | 0.0006105 | 0 | 0.0054945 | 0.0006105 | 27570.8889 | 248938 | 27570.8834
38959.4978 | 1 | 0 | 38959.4978 | 1 | 0 |  | 35.5 | 162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4983 | 1 | 0 | 38959.4983 | 1 | 0 |  | 77.5 | 204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4988 | 1 | 0 | 38959.4988 | 1 | 0 |  | 119.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4993 | 1 | 0 | 38959.4993 | 1 | 0 |  | 162 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.4998 | 1 | 0 | 38959.4998 | 1 | 0 |  | 203.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5002 | 1 | 0 | 38959.5003 | 1 | 0 |  | 245.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5007 | 1 | 0 | 38959.5007 | 1 | 0 |  | 287.5 | 414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5012 | 1 | 0 | 38959.5012 | 1 | 0 |  | 329.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
| 1 | 0 | 38959.5017 | 1 | 0 |  | 372 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5022 | 1 | 0 | 38959.5022 | 1 | 0 |  | 413.5 | 540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5027 | 1 | 0 | 38959.5027 | 1 | 0 |  | 455.5 | 582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5032 | 1 | 0 | 38959.5032 | 1 | 0 |  | 497.5 | 624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5036 | 1 | 0 | 38959.5037 | 1 | 0 |  | 539.5 | 666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5041 | 1 | 0 | 38959.5041 | 1 | 0 |  | 581.5 | 708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5046 | 1 | 0 | 38959.5046 | 1 | 0 |  | 623.5 | 750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5051 | 1 | 0 | 38959.5051 | 1 | 0 |  | 665.5 | 792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5056 | 1 | 0 | 38959.5056 | 1 | 0 |  | 707.5 | 834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5061 | 1 | 0 | 38959.5061 | 1 | 0 |  | 749.5 | 876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5066 | 1 | 0 | 38959.5066 | 1 | 0 |  | 791.5 | 918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.507 | 1 | 0 | 38959.5071 | 1 | 0 |  | 833.5 | 960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5075 | 1 | 0 | 38959.5075 | 1 | 0 |  | 875.5 | 1002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.508 | 1 | 0 | 38959.508 | 1 | 0 |  | 917.5 | 1044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5085 | 1 | 0 | 38959.5085 | 1 | 0 |  | 959.5 | 1086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.509 | 1 | 0 | 38959.509 | 1 | 0 |  | 1001.5 | 1128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5095 | 1 | 0 | 38959.5095 | 1 | 0 |  | 1043.5 | 1170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.51 | 1 | 0 | 38959.51 | 1 | 0 |  | 1085.5 | 1212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5105 | 1 | 0 | 38959.5105 | 1 | 0 |  | 1127.5 | 1254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5109 | 1 | 0 | 38959.5109 | 1 | 0 |  | 1169.5 | 1296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5114 | 1 | 0 | 38959.5114 | 1 | 0 |  | 1211.5 | 1338.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5119 | 1 | 0 | 38959.5119 | 1 | 0 |  | 1253.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
38959.5124 | 1 | 0 | 38959.5124 | 1012 | 0 |  | 1295.5 | 1422.5 | 0.06105 | 0 | 61.7827 | 0 | 0.0006105 | 0 | 0.61783 | 0 | 0.0006105 | 0.61783 | 248938 | 146.085 | 248937.9994
38959.5129 | 3 | 0 | 38959.5129 | 1594 | 0 |  | 1337.5 | 1464.5 | 0.18315 | 0 | 97.3138 | 0 | 0.0018315 | 0 | 0.97314 | 0 | 0.0018315 | 0.97314 | 82912.6667 | 56.2346 | 82912.6648
38959.5134 | 3 | 0 | 38959.5134 | 2046 | 0 |  | 1379.5 | 1506.5 | 0.18315 | 0 | 124.9084 | 0 | 0.0018315 | 0 | 1.2491 | 0 | 0.0018315 | 1.2491 | 82912.6667 | 21.7195 | 82912.6648
38959.5139 | 3 | 0 | 38959.5139 | 2011 | 0 |  | 1421.5 | 1548.5 | 0.18315 | 0 | 122.7717 | 0 | 0.0018315 | 0 | 1.2277 | 0 | 0.0018315 | 1.2277 | 82912.6667 | 23.8379 | 82912.6648
38959.5143 | 3 | 0 | 38959.5144 | 2126 | 0 |  | 1463.5 | 1590.5 | 0.18315 | 0 | 129.7924 | 0 | 0.0018315 | 0 | 1.2979 | 0 | 0.0018315 | 1.2979 | 82912.6667 | 17.1392 | 82912.6648
38959.5148 | 3 | 0 | 38959.5148 | 2202 | 0 |  | 1505.5 | 1632.5 | 0.18315 | 0 | 134.4322 | 0 | 0.0018315 | 0 | 1.3443 | 0 | 0.0018315 | 1.3443 | 82912.6667 | 13.0963 | 82912.6648
38959.5153 | 3 | 0 | 38959.5153 | 2277 | 0 |  | 1547.5 | 1674.5 | 0.18315 | 0 | 139.011 | 0 | 0.0018315 | 0 | 1.3901 | 0 | 0.0018315 | 1.3901 | 82912.6667 | 9.3711 | 82912.6648
38959.5158 | 3 | 0 | 38959.5158 | 2294 | 0 |  | 1589.5 | 1716.5 | 0.18315 | 0 | 140.0488 | 0 | 0.0018315 | 0 | 1.4005 | 0 | 0.0018315 | 1.4005 | 82912.6667 | 8.5606 | 82912.6648
38959.5163 | 491 | 0 | 38959.5163 | 2443 | 0 |  | 1631.5 | 1758.5 | 29.9756 | 0 | 149.1453 | 0 | 0.29976 | 0 | 1.4915 | 0 | 0.29976 | 1.4915 | 407.2057 | 1.9394 | 406.9059
38959.5168 | 978 | 0 | 38959.5168 | 2233 | 0 |  | 1673.5 | 1800.5 | 59.707 | 0 | 136.3248 | 0 | 0.59707 | 0 | 1.3632 | 0 | 0.59707 | 1.3632 | 154.6401 | 11.5262 | 154.043
38959.5173 | 1113 | 0 | 38959.5173 | 2090 | 0 |  | 1715.5 | 1842.5 | 67.9487 | 0 | 127.5946 | 0 | 0.67949 | 0 | 1.2759 | 0 | 0.67949 | 1.2759 | 123.7538 | 19.1569 | 123.0743
38959.5177 | 1143 | 0 | 38959.5178 | 2444 | 0 |  | 1757.5 | 1884.5 | 69.7802 | 0 | 149.2063 | 0 | 0.6978 | 0 | 1.4921 | 0 | 0.6978 | 1.4921 | 117.881 | 1.8977 | 117.1832
38959.5182 | 1813 | 0 | 38959.5182 | 2208 | 0 |  | 1799.5 | 1926.5 | 110.6838 | 0 | 134.7985 | 0 | 1.1068 | 0 | 1.348 | 0 | 1.1068 | 1.348 | 37.3624 | 12.7889 | 36.2555
38959.5187 | 2197 | 0 | 38959.5187 | 1989 | 0 |  | 1841.5 | 1968.5 | 134.127 | 0 | 121.4286 | 0 | 1.3413 | 0 | 1.2143 | 0 | 1.3413 | 1.2143 | 13.3537 | 25.2076 | 12.0124
38959.5192 | 2083 | 0 | 38959.5192 | 2044 | 0 |  | 1883.5 | 2010.5 | 127.1673 | 0 | 124.7863 | 0 | 1.2717 | 0 | 1.2479 | 0 | 1.2717 | 1.2479 | 19.5574 | 21.8386 | 18.2857
38959.5197 | 1867 | 0 | 38959.5197 | 2155 | 0 |  | 1925.5 | 2052.5 | 113.9805 | 0 | 131.5629 | 0 | 1.1398 | 0 | 1.3156 | 0 | 1.1398 | 1.3156 | 33.3894 | 15.5629 | 32.2496
38959.5202 | 1847 | 0 | 38959.5202 | 2445 | 0 |  | 1967.5 | 2094.5 | 112.7595 | 0 | 149.2674 | 0 | 1.1276 | 0 | 1.4927 | 0 | 1.1276 | 1.4927 | 34.8338 | 1.856 | 33.7062
38959.5207 | 2359 | 0 | 38959.5207 | 2447 | 0 |  | 2009.5 | 2136.5 | 144.0171 | 0 | 149.3895 | 0 | 1.4402 | 0 | 1.4939 | 0 | 1.4402 | 1.4939 | 5.5693 | 1.7728 | 4.1291
38959.5211 | 2114 | 0 | 38959.5212 | 1904 | 0 |  | 2051.5 | 2178.5 | 129.0598 | 0 | 116.2393 | 0 | 1.2906 | 0 | 1.1624 | 0 | 1.2906 | 1.1624 | 17.8042 | 30.7973 | 16.5136
38959.5216 | 2285 | 0 | 38959.5216 | 2074 | 0 |  | 2093.5 | 2220.5 | 139.4994 | 0 | 126.6178 | 0 | 1.395 | 0 | 1.2662 | 0 | 1.395 | 1.2662 | 8.9882 | 20.0762 | 7.5932
38959.5221 | 2129 | 0 | 38959.5221 | 2185 | 0 |  | 2135.5 | 2262.5 | 129.9756 | 0 | 133.3944 | 0 | 1.2998 | 0 | 1.3339 | 0 | 1.2998 | 1.3339 | 16.9742 | 13.9762 | 15.6744
38959.5226 | 2175 | 0 | 38959.5226 | 2440 | 0 |  | 2177.5 | 2304.5 | 132.7839 | 0 | 148.9621 | 0 | 1.3278 | 0 | 1.4896 | 0 | 1.3278 | 1.4896 | 14.5002 | 2.0648 | 13.1724
38959.5231 | 2093 | 0 | 38959.5231 | 2245 | 0 |  | 2219.5 | 2346.5 | 127.7778 | 0 | 137.0574 | 0 | 1.2778 | 0 | 1.3706 | 0 | 1.2778 | 1.3706 | 18.9861 | 10.9301 | 17.7084
38959.5236 | 1933 | 0 | 38959.5236 | 2260 | 0 |  | 2261.5 | 2388.5 | 118.0098 | 0 | 137.9731 | 0 | 1.1801 | 0 | 1.3797 | 0 | 1.1801 | 1.3797 | 28.835 | 10.1938 | 27.6549
38959.5241 | 1868 | 0 | 38959.5241 | 2457 | 0 |  | 2303.5 | 2430.5 | 114.0415 | 0 | 150 | 0 | 1.1404 | 0 | 1.5 | 0 | 1.1404 | 1.5 | 33.318 | 1.3586 | 32.1776
38959.5245 | 2230 | 0 | 38959.5246 | 2416 | 0 |  | 2345.5 | 2472.5 | 136.1416 | 0 | 147.4969 | 0 | 1.3614 | 0 | 1.475 | 0 | 1.3614 | 1.475 | 11.6762 | 3.0786 | 10.3148
38959.525 | 2326 | 0 | 38959.525 | 2390 | 0 |  | 2387.5 | 2514.5 | 142.0024 | 0 | 145.9096 | 0 | 1.42 | 0 | 1.4591 | 0 | 1.42 | 1.4591 | 7.0671 | 4.2 | 5.647
38959.5255 | 1904 | 0 | 38959.5255 | 1964 | 0 |  | 2429.5 | 2556.5 | 116.2393 | 0 | 119.9023 | 0 | 1.1624 | 0 | 1.199 | 0 | 1.1624 | 1.199 | 30.7973 | 26.8014 | 29.6349
38959.526 | 1931 | 0 | 38959.526 | 2463 | 0 |  | 2471.5 | 2598.5 | 117.8877 | 0 | 150.3663 | 0 | 1.1789 | 0 | 1.5037 | 0 | 1.1789 | 1.5037 | 28.9684 | 1.1117 | 27.7895
38959.5265 | 1977 | 0 | 38959.5265 | 2342 | 0 |  | 2513.5 | 2640.5 | 120.696 | 0 | 142.9792 | 0 | 1.207 | 0 | 1.4298 | 0 | 1.207 | 1.4298 | 25.9676 | 6.3356 | 24.7607
38959.527 | 2379 | 0 | 38959.527 | 2080 | 0 |  | 2555.5 | 2682.5 | 145.2381 | 0 | 126.9841 | 0 | 1.4524 | 0 | 1.2698 | 0 | 1.4524 | 1.2698 | 4.6818 | 19.7298 | 3.2294
38959.5275 | 1863 | 0 | 38959.5275 | 1938 | 0 |  | 2597.5 | 2724.5 | 113.7363 | 0 | 118.315 | 0 | 1.1374 | 0 | 1.1832 | 0 | 1.1374 | 1.1832 | 33.6758 | 28.5026 | 32.5384
38959.528 | 2405 | 0 | 38959.528 | 2474 | 0 |  | 2639.5 | 2766.5 | 146.8254 | 0 | 151.0379 | 0 | 1.4683 | 0 | 1.5104 | 0 | 1.4683 | 1.5104 | 3.5501 | 0.66209 | 2.0818
38959.5284 | 2323 | 0 | 38959.5284 | 2285 | 0 |  | 2681.5 | 2808.5 | 141.8193 | 0 | 139.4994 | 0 | 1.4182 | 0 | 1.395 | 0 | 1.4182 | 1.395 | 7.2053 | 8.9882 | 5.7871
38959.5289 | 2409 | 0 | 38959.5289 | 1916 | 0 |  | 2723.5 | 2850.5 | 147.0696 | 0 | 116.9719 | 0 | 1.4707 | 0 | 1.1697 | 0 | 1.4707 | 1.1697 | 3.3782 | 29.9781 | 1.9075
38959.5294 | 2288 | 0 | 38959.5294 | 2108 | 0 |  | 2765.5 | 2892.5 | 139.6825 | 0 | 128.6935 | 0 | 1.3968 | 0 | 1.2869 | 0 | 1.3968 | 1.2869 | 8.8453 | 18.1395 | 7.4485
38959.5299 | 1977 | 0 | 38959.5299 | 1915 | 0 |  | 2807.5 | 2934.5 | 120.696 | 0 | 116.9109 | 0 | 1.207 | 0 | 1.1691 | 0 | 1.207 | 1.1691 | 25.9676 | 30.046 | 24.7607
38959.5304 | 2061 | 0 | 38959.5304 | 2467 | 0 |  | 2849.5 | 2976.5 | 125.8242 | 0 | 150.6105 | 0 | 1.2582 | 0 | 1.5061 | 0 | 1.2582 | 1.5061 | 20.8336 | 0.94771 | 19.5753
38959.5309 | 2088 | 0 | 38959.5309 | 1907 | 0 |  | 2891.5 | 3018.5 | 127.4725 | 0 | 116.4225 | 0 | 1.2747 | 0 | 1.1642 | 0 | 1.2747 | 1.1642 | 19.2711 | 30.5915 | 17.9963
38959.5314 | 2015 | 0 | 38959.5314 | 2301 | 0 |  | 2933.5 | 3060.5 | 123.0159 | 0 | 140.4762 | 0 | 1.2302 | 0 | 1.4048 | 0 | 1.2302 | 1.4048 | 23.5921 | 8.2303 | 22.3619
38959.5318 | 2386 | 0 | 38959.5319 | 2246 | 0 |  | 2975.5 | 3102.5 | 145.6654 | 0 | 137.1184 | 0 | 1.4567 | 0 | 1.3712 | 0 | 1.4567 | 1.3712 | 4.3747 | 10.8807 | 2.918
38959.5323 | 2105 | 0 | 38959.5323 | 2253 | 0 |  | 3017.5 | 3144.5 | 128.5104 | 0 | 137.5458 | 0 | 1.2851 | 0 | 1.3755 | 0 | 1.2851 | 1.3755 | 18.3078 | 10.5362 | 17.0227
38959.5328 | 1958 | 0 | 38959.5328 | 1997 | 0 |  | 3059.5 | 3186.5 | 119.536 | 0 | 121.917 | 0 | 1.1954 | 0 | 1.2192 | 0 | 1.1954 | 1.2192 | 27.19 | 24.7061 | 25.9946
38959.5333 | 2430 | 0 | 38959.5333 | 2395 | 0 |  | 3101.5 | 3228.5 | 148.3516 | 0 | 146.2149 | 0 | 1.4835 | 0 | 1.4621 | 0 | 1.4835 | 1.4621 | 2.4848 | 3.9825 | 1.0013
38959.5338 | 1986 | 0 | 38959.5338 | 1958 | 0 |  | 3143.5 | 3270.5 | 121.2454 | 0 | 119.536 | 0 | 1.2125 | 0 | 1.1954 | 0 | 1.2125 | 1.1954 | 25.3968 | 27.19 | 24.1843
38959.5343 | 1981 | 0 | 38959.5343 | 2451 | 0 |  | 3185.5 | 3312.5 | 120.9402 | 0 | 149.6337 | 0 | 1.2094 | 0 | 1.4963 | 0 | 1.2094 | 1.4963 | 25.7133 | 1.6067 | 24.5039
38959.5348 | 2311 | 0 | 38959.5348 | 2252 | 0 |  | 3227.5 | 3354.5 | 141.0867 | 0 | 137.4847 | 0 | 1.4109 | 0 | 1.3748 | 0 | 1.4109 | 1.3748 | 7.762 | 10.5853 | 6.3511
38959.5352 | 2435 | 0 | 38959.5353 | 2447 | 0 |  | 3269.5 | 3396.5 | 148.6569 | 0 | 149.3895 | 0 | 1.4866 | 0 | 1.4939 | 0 | 1.4866 | 1.4939 | 2.2743 | 1.7728 | 0.78776

## B4-C5
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 152.7094 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
38959.4963 | 1 | 0 | 38959.4963 | 1 | 0 |  | -93 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4968 | 1 | 0 | 38959.4968 | 1 | 0 |  | -51 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4973 | 1 | 0 | 38959.4973 | 1 | 0 |  | -9 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4978 | 1 | 0 | 38959.4978 | 1 | 0 |  | 33 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4983 | 1 | 0 | 38959.4983 | 1 | 0 |  | 75 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4987 | 1 | 0 | 38959.4988 | 1 | 0 |  | 117 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4992 | 1 | 0 | 38959.4993 | 1 | 0 |  | 159 | 286 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.4997 | 1 | 0 | 38959.4997 | 1 | 0 |  | 201 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5002 | 1 | 0 | 38959.5002 | 1 | 0 |  | 243 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5007 | 1 | 0 | 38959.5007 | 1 | 0 |  | 285 | 412 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5012 | 1 | 0 | 38959.5012 | 1 | 0 |  | 327 | 454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5017 | 1 | 0 | 38959.5017 | 1 | 0 |  | 369 | 496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5022 | 1 | 0 | 38959.5022 | 1 | 0 |  | 411 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5026 | 1 | 0 | 38959.5027 | 1 | 0 |  | 453 | 580 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5031 | 1 | 0 | 38959.5031 | 1 | 0 |  | 495 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5036 | 1 | 0 | 38959.5036 | 1 | 0 |  | 537 | 664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5041 | 1 | 0 | 38959.5041 | 1 | 0 |  | 579 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5046 | 1 | 0 | 38959.5046 | 1 | 0 |  | 621 | 748 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5051 | 1 | 0 | 38959.5051 | 1 | 0 |  | 663 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5056 | 1 | 0 | 38959.5056 | 1 | 0 |  | 705 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.506 | 1 | 0 | 38959.5061 | 1 | 0 |  | 747 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5065 | 1 | 0 | 38959.5065 | 1 | 0 |  | 788.5 | 915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.507 | 1 | 0 | 38959.507 | 1 | 0 |  | 831 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5075 | 1 | 0 | 38959.5075 | 1 | 0 |  | 873 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.508 | 1 | 0 | 38959.508 | 1 | 0 |  | 915 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5085 | 1 | 0 | 38959.5085 | 1 | 0 |  | 956.5 | 1083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.509 | 1 | 0 | 38959.509 | 1 | 0 |  | 998.5 | 1125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5094 | 1 | 0 | 38959.5095 | 1 | 0 |  | 1040.5 | 1167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5099 | 1 | 0 | 38959.51 | 1 | 0 |  | 1083 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5104 | 1 | 0 | 38959.5104 | 1 | 0 |  | 1125 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5109 | 1 | 0 | 38959.5109 | 1 | 0 |  | 1167 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5114 | 1 | 0 | 38959.5114 | 1 | 0 |  | 1209 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5119 | 1 | 0 | 38959.5119 | 1 | 0 |  | 1250.5 | 1377.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250038 | 250038 | 250037.9994
38959.5124 | 2 | 0 | 38959.5124 | 1 | 0 |  | 1292.5 | 1419.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 124969 | 250038 | 124968.9988
38959.5128 | 2 | 0 | 38959.5129 | 2046 | 0 |  | 1334.5 | 1461.5 | 0.1221 | 0 | 124.9084 | 0 | 0.001221 | 0 | 1.2491 | 0 | 0.001221 | 1.2491 | 124969 | 22.2571 | 124968.9988
38959.5133 | 3 | 0 | 38959.5134 | 2312 | 0 |  | 1377 | 1504 | 0.18315 | 0 | 141.1477 | 0 | 0.0018315 | 0 | 1.4115 | 0 | 0.0018315 | 1.4115 | 83279.3333 | 8.1912 | 83279.3315
38959.5138 | 3 | 0 | 38959.5138 | 2359 | 0 |  | 1419 | 1546 | 0.18315 | 0 | 144.0171 | 0 | 0.0018315 | 0 | 1.4402 | 0 | 0.0018315 | 1.4402 | 83279.3333 | 6.0356 | 83279.3315
38959.5143 | 3 | 0 | 38959.5143 | 2166 | 0 |  | 1460.5 | 1587.5 | 0.18315 | 0 | 132.2344 | 0 | 0.0018315 | 0 | 1.3223 | 0 | 0.0018315 | 1.3223 | 83279.3333 | 15.4838 | 83279.3315
38959.5148 | 3 | 0 | 38959.5148 | 1905 | 0 |  | 1502.5 | 1629.5 | 0.18315 | 0 | 116.3004 | 0 | 0.0018315 | 0 | 1.163 | 0 | 0.0018315 | 1.163 | 83279.3333 | 31.306 | 83279.3315
38959.5153 | 3 | 0 | 38959.5153 | 2124 | 0 |  | 1544.5 | 1671.5 | 0.18315 | 0 | 129.6703 | 0 | 0.0018315 | 0 | 1.2967 | 0 | 0.0018315 | 1.2967 | 83279.3333 | 17.7674 | 83279.3315
38959.5158 | 3 | 0 | 38959.5158 | 2001 | 0 |  | 1586.5 | 1713.5 | 0.18315 | 0 | 122.1612 | 0 | 0.0018315 | 0 | 1.2216 | 0 | 0.0018315 | 1.2216 | 83279.3333 | 25.0065 | 83279.3315
38959.5163 | 283 | 0 | 38959.5163 | 2067 | 0 |  | 1628.5 | 1755.5 | 17.2772 | 0 | 126.1905 | 0 | 0.17277 | 0 | 1.2619 | 0 | 0.17277 | 1.2619 | 783.8799 | 21.015 | 783.7071
38959.5167 | 1058 | 0 | 38959.5167 | 2318 | 0 |  | 1670.5 | 1797.5 | 64.591 | 0 | 141.514 | 0 | 0.64591 | 0 | 1.4151 | 0 | 0.64591 | 1.4151 | 136.4253 | 7.9111 | 135.7794
38959.5172 | 1119 | 0 | 38959.5172 | 1924 | 0 |  | 1712.5 | 1839.5 | 68.315 | 0 | 117.4603 | 0 | 0.68315 | 0 | 1.1746 | 0 | 0.68315 | 1.1746 | 123.5371 | 30.0094 | 122.8539
38959.5177 | 1021 | 0 | 38959.5177 | 2074 | 0 |  | 1754.5 | 1881.5 | 62.3321 | 0 | 126.6178 | 0 | 0.62332 | 0 | 1.2662 | 0 | 0.62332 | 1.2662 | 144.9931 | 20.6066 | 144.3698
38959.5182 | 1366 | 0 | 38959.5182 | 2324 | 0 |  | 1796.5 | 1923.5 | 83.3944 | 0 | 141.8803 | 0 | 0.83394 | 0 | 1.4188 | 0 | 0.83394 | 1.4188 | 83.1171 | 7.6325 | 82.2832
38959.5187 | 2193 | 0 | 38959.5187 | 2028 | 0 |  | 1838.5 | 1965.5 | 133.8828 | 0 | 123.8095 | 0 | 1.3388 | 0 | 1.2381 | 0 | 1.3388 | 1.2381 | 14.062 | 23.3422 | 12.7232
38959.5192 | 2038 | 0 | 38959.5192 | 2459 | 0 |  | 1880.5 | 2007.5 | 124.42 | 0 | 150.1221 | 0 | 1.2442 | 0 | 1.5012 | 0 | 1.2442 | 1.5012 | 22.737 | 1.7235 | 21.4928
38959.5197 | 2236 | 0 | 38959.5197 | 2060 | 0 |  | 1922.5 | 2049.5 | 136.5079 | 0 | 125.7631 | 0 | 1.3651 | 0 | 1.2576 | 0 | 1.3651 | 1.2576 | 11.8685 | 21.4262 | 10.5034
38959.5201 | 2054 | 0 | 38959.5202 | 2044 | 0 |  | 1964.5 | 2091.5 | 125.3968 | 0 | 124.7863 | 0 | 1.254 | 0 | 1.2479 | 0 | 1.254 | 1.2479 | 21.7809 | 22.3767 | 20.5269
38959.5206 | 1855 | 0 | 38959.5206 | 2465 | 0 |  | 2006.5 | 2133.5 | 113.2479 | 0 | 150.4884 | 0 | 1.1325 | 0 | 1.5049 | 0 | 1.1325 | 1.5049 | 34.8453 | 1.4759 | 33.7128
38959.5211 | 2062 | 0 | 38959.5211 | 2092 | 0 |  | 2048.5 | 2175.5 | 125.8852 | 0 | 127.7167 | 0 | 1.2589 | 0 | 1.2772 | 0 | 1.2589 | 1.2772 | 21.3084 | 19.5688 | 20.0496
38959.5216 | 1833 | 0 | 38959.5216 | 2166 | 0 |  | 2090.5 | 2217.5 | 111.9048 | 0 | 132.2344 | 0 | 1.119 | 0 | 1.3223 | 0 | 1.119 | 1.3223 | 36.4637 | 15.4838 | 35.3447
38959.5221 | 2311 | 0 | 38959.5221 | 1946 | 0 |  | 2132.5 | 2259.5 | 141.0867 | 0 | 118.8034 | 0 | 1.4109 | 0 | 1.188 | 0 | 1.4109 | 1.188 | 8.238 | 28.5396 | 6.8271
38959.5226 | 2189 | 0 | 38959.5226 | 2098 | 0 |  | 2174.5 | 2301.5 | 133.6386 | 0 | 128.083 | 0 | 1.3364 | 0 | 1.2808 | 0 | 1.3364 | 1.2808 | 14.2704 | 19.2269 | 12.9341
38959.5231 | 2138 | 0 | 38959.5231 | 2213 | 0 |  | 2216.5 | 2343.5 | 130.525 | 0 | 135.1038 | 0 | 1.3053 | 0 | 1.351 | 0 | 1.3053 | 1.351 | 16.9963 | 13.0312 | 15.691
38959.5235 | 2375 | 0 | 38959.5236 | 2021 | 0 |  | 2258.5 | 2385.5 | 144.9939 | 0 | 123.3822 | 0 | 1.4499 | 0 | 1.2338 | 0 | 1.4499 | 1.2338 | 5.3213 | 23.7694 | 3.8713
38959.524 | 2173 | 0 | 38959.524 | 2140 | 0 |  | 2300.5 | 2427.5 | 132.6618 | 0 | 130.6471 | 0 | 1.3266 | 0 | 1.3065 | 0 | 1.3266 | 1.3065 | 15.1118 | 16.8869 | 13.7852
38959.5245 | 2286 | 0 | 38959.5245 | 2104 | 0 |  | 2342.5 | 2469.5 | 139.5604 | 0 | 128.4493 | 0 | 1.3956 | 0 | 1.2845 | 0 | 1.3956 | 1.2845 | 9.4217 | 18.8869 | 8.0261
38959.525 | 2013 | 0 | 38959.525 | 2479 | 0 |  | 2384.5 | 2511.5 | 122.8938 | 0 | 151.3431 | 0 | 1.2289 | 0 | 1.5134 | 0 | 1.2289 | 1.5134 | 24.2613 | 0.90278 | 23.0324
38959.5255 | 2299 | 0 | 38959.5255 | 1972 | 0 |  | 2426.5 | 2553.5 | 140.3541 | 0 | 120.3907 | 0 | 1.4035 | 0 | 1.2039 | 0 | 1.4035 | 1.2039 | 8.803 | 26.8448 | 7.3994
38959.526 | 2214 | 0 | 38959.526 | 2136 | 0 |  | 2468.5 | 2595.5 | 135.1648 | 0 | 130.4029 | 0 | 1.3516 | 0 | 1.304 | 0 | 1.3516 | 1.304 | 12.9801 | 17.1058 | 11.6285
38959.5265 | 2368 | 0 | 38959.5265 | 2097 | 0 |  | 2510.5 | 2637.5 | 144.5665 | 0 | 128.022 | 0 | 1.4457 | 0 | 1.2802 | 0 | 1.4457 | 1.2802 | 5.6326 | 19.2837 | 4.1869
38959.5269 | 2302 | 0 | 38959.527 | 2485 | 0 |  | 2552.5 | 2679.5 | 140.5372 | 0 | 151.7094 | 0 | 1.4054 | 0 | 1.5171 | 0 | 1.4054 | 1.5171 | 8.6612 | 0.65915 | 7.2558
38959.5274 | 2101 | 0 | 38959.5274 | 2141 | 0 |  | 2594.5 | 2721.5 | 128.2662 | 0 | 130.7082 | 0 | 1.2827 | 0 | 1.3071 | 0 | 1.2827 | 1.3071 | 19.0566 | 16.8323 | 17.774
38959.5279 | 2200 | 0 | 38959.5279 | 2091 | 0 |  | 2636.5 | 2763.5 | 134.3101 | 0 | 127.6557 | 0 | 1.3431 | 0 | 1.2766 | 0 | 1.3431 | 1.2766 | 13.6991 | 19.626 | 12.356
38959.5284 | 2390 | 0 | 38959.5284 | 2043 | 0 |  | 2678.5 | 2805.5 | 145.9096 | 0 | 124.7253 | 0 | 1.4591 | 0 | 1.2473 | 0 | 1.4591 | 1.2473 | 4.6603 | 22.4366 | 3.2012
38959.5289 | 2393 | 0 | 38959.5289 | 2220 | 0 |  | 2720.5 | 2847.5 | 146.0928 | 0 | 135.5311 | 0 | 1.4609 | 0 | 1.3553 | 0 | 1.4609 | 1.3553 | 4.529 | 12.6748 | 3.0681
38959.5294 | 2212 | 0 | 38959.5294 | 2391 | 0 |  | 2762.5 | 2889.5 | 135.0427 | 0 | 145.9707 | 0 | 1.3504 | 0 | 1.4597 | 0 | 1.3504 | 1.4597 | 13.0823 | 4.6165 | 11.7319
38959.5299 | 2398 | 0 | 38959.5299 | 2329 | 0 |  | 2804.5 | 2931.5 | 146.398 | 0 | 142.1856 | 0 | 1.464 | 0 | 1.4219 | 0 | 1.464 | 1.4219 | 4.3111 | 7.4015 | 2.8471
38959.5303 | 2425 | 0 | 38959.5304 | 2206 | 0 |  | 2846.5 | 2973.5 | 148.0464 | 0 | 134.6764 | 0 | 1.4805 | 0 | 1.3468 | 0 | 1.4805 | 1.3468 | 3.1497 | 13.3898 | 1.6692
38959.5308 | 2044 | 0 | 38959.5308 | 2423 | 0 |  | 2888.5 | 3015.5 | 124.7863 | 0 | 147.9243 | 0 | 1.2479 | 0 | 1.4792 | 0 | 1.2479 | 1.4792 | 22.3767 | 3.2348 | 21.1288
38959.5313 | 2399 | 0 | 38959.5313 | 2484 | 0 |  | 2930.5 | 3057.5 | 146.4591 | 0 | 151.6484 | 0 | 1.4646 | 0 | 1.5165 | 0 | 1.4646 | 1.5165 | 4.2676 | 0.69968 | 2.803
38959.5318 | 2040 | 0 | 38959.5318 | 2483 | 0 |  | 2972.5 | 3099.5 | 124.5421 | 0 | 151.5873 | 0 | 1.2454 | 0 | 1.5159 | 0 | 1.2454 | 1.5159 | 22.6167 | 0.74023 | 21.3712
38959.5323 | 1990 | 0 | 38959.5323 | 1974 | 0 |  | 3014.5 | 3141.5 | 121.4896 | 0 | 120.5128 | 0 | 1.2149 | 0 | 1.2051 | 0 | 1.2149 | 1.2051 | 25.6975 | 26.7163 | 24.4826
38959.5328 | 1894 | 0 | 38959.5328 | 2386 | 0 |  | 3056.5 | 3183.5 | 115.6288 | 0 | 145.6654 | 0 | 1.1563 | 0 | 1.4567 | 0 | 1.1563 | 1.4567 | 32.0686 | 4.8357 | 30.9123
38959.5333 | 2283 | 0 | 38959.5333 | 2437 | 0 |  | 3098.5 | 3225.5 | 139.3773 | 0 | 148.779 | 0 | 1.3938 | 0 | 1.4878 | 0 | 1.3938 | 1.4878 | 9.5655 | 2.6418 | 8.1717
38959.5338 | 2433 | 0 | 38959.5338 | 2438 | 0 |  | 3140.5 | 3267.5 | 148.5348 | 0 | 148.84 | 0 | 1.4853 | 0 | 1.4884 | 0 | 1.4853 | 1.4884 | 2.8105 | 2.5997 | 1.3252
38959.5342 | 2287 | 0 | 38959.5342 | 2100 | 0 |  | 3182.5 | 3309.5 | 139.6215 | 0 | 128.2051 | 0 | 1.3962 | 0 | 1.2821 | 0 | 1.3962 | 1.2821 | 9.3739 | 19.1133 | 7.9776
38959.5347 | 1995 | 0 | 38959.5347 | 2081 | 0 |  | 3224.5 | 3351.5 | 121.7949 | 0 | 127.0452 | 0 | 1.2179 | 0 | 1.2705 | 0 | 1.2179 | 1.2705 | 25.3825 | 20.2009 | 24.1645
38959.5352 | 2107 | 0 | 38959.5352 | 2395 | 0 |  | 3266.5 | 3393.5 | 128.6325 | 0 | 146.2149 | 0 | 1.2863 | 0 | 1.4621 | 0 | 1.2863 | 1.4621 | 18.7176 | 4.4418 | 17.4313

## B3-C6
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.9158 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
38959.4963 | 1 | 0 | 38959.4963 | 1 | 0 |  | -96 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4968 | 1 | 0 | 38959.4968 | 1 | 0 |  | -54 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4973 | 1 | 0 | 38959.4973 | 1 | 0 |  | -12 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4977 | 1 | 0 | 38959.4978 | 1 | 0 |  | 30 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4982 | 1 | 0 | 38959.4983 | 1 | 0 |  | 72 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4987 | 1 | 0 | 38959.4987 | 1 | 0 |  | 114 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4992 | 1 | 0 | 38959.4992 | 1 | 0 |  | 156 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.4997 | 1 | 0 | 38959.4997 | 1 | 0 |  | 198 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5002 | 1 | 0 | 38959.5002 | 1 | 0 |  | 240 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5007 | 1 | 0 | 38959.5007 | 1 | 0 |  | 282 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5011 | 1 | 0 | 38959.5012 | 1 | 0 |  | 324 | 451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5016 | 1 | 0 | 38959.5017 | 1 | 0 |  | 366 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5021 | 1 | 0 | 38959.5021 | 1 | 0 |  | 408 | 535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5026 | 1 | 0 | 38959.5026 | 1 | 0 |  | 450 | 577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5031 | 1 | 0 | 38959.5031 | 1 | 0 |  | 492 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5036 | 1 | 0 | 38959.5036 | 1 | 0 |  | 534 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5041 | 1 | 0 | 38959.5041 | 1 | 0 |  | 576 | 703 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5045 | 1 | 0 | 38959.5046 | 1 | 0 |  | 618 | 745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.505 | 1 | 0 | 38959.5051 | 1 | 0 |  | 660 | 787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5055 | 1 | 0 | 38959.5055 | 1 | 0 |  | 702 | 829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.506 | 1 | 0 | 38959.506 | 1 | 0 |  | 744 | 871 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5065 | 1 | 0 | 38959.5065 | 1 | 0 |  | 786 | 913 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.507 | 1 | 0 | 38959.507 | 1 | 0 |  | 828 | 955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5075 | 1 | 0 | 38959.5075 | 1 | 0 |  | 870 | 997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.508 | 1 | 0 | 38959.508 | 1 | 0 |  | 912 | 1039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5084 | 1 | 0 | 38959.5085 | 1 | 0 |  | 954 | 1081 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5089 | 1 | 0 | 38959.5089 | 1 | 0 |  | 996 | 1123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5094 | 1 | 0 | 38959.5094 | 1 | 0 |  | 1038 | 1165 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5099 | 1 | 0 | 38959.5099 | 1 | 0 |  | 1080 | 1207 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5104 | 1 | 0 | 38959.5104 | 1 | 0 |  | 1122 | 1249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5109 | 1 | 0 | 38959.5109 | 1 | 0 |  | 1164 | 1291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5114 | 1 | 0 | 38959.5114 | 1 | 0 |  | 1206 | 1333 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5118 | 1 | 0 | 38959.5119 | 1 | 0 |  | 1248 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
38959.5123 | 1 | 0 | 38959.5123 | 62 | 0 |  | 1290 | 1417 | 0.06105 | 0 | 3.7851 | 0 | 0.0006105 | 0 | 0.037851 | 0 | 0.0006105 | 0.037851 | 248738 | 3913.5161 | 248737.9994
38959.5128 | 3 | 0 | 38959.5128 | 731 | 0 |  | 1332 | 1459 | 0.18315 | 0 | 44.6276 | 0 | 0.0018315 | 0 | 0.44628 | 0 | 0.0018315 | 0.44628 | 82846 | 240.4077 | 82845.9982
38959.5133 | 3 | 0 | 38959.5133 | 2432 | 0 |  | 1374 | 1501 | 0.18315 | 0 | 148.4737 | 0 | 0.0018315 | 0 | 1.4847 | 0 | 0.0018315 | 1.4847 | 82846 | 2.3183 | 82845.9982
38959.5138 | 3 | 0 | 38959.5138 | 2287 | 0 |  | 1416 | 1543 | 0.18315 | 0 | 139.6215 | 0 | 0.0018315 | 0 | 1.3962 | 0 | 0.0018315 | 1.3962 | 82846 | 8.8054 | 82845.9982
38959.5143 | 3 | 0 | 38959.5143 | 2354 | 0 |  | 1458 | 1585 | 0.18315 | 0 | 143.7118 | 0 | 0.0018315 | 0 | 1.4371 | 0 | 0.0018315 | 1.4371 | 82846 | 5.7086 | 82845.9982
38959.5148 | 3 | 0 | 38959.5148 | 2235 | 0 |  | 1500 | 1627 | 0.18315 | 0 | 136.4469 | 0 | 0.0018315 | 0 | 1.3645 | 0 | 0.0018315 | 1.3645 | 82846 | 11.3369 | 82845.9982
38959.5152 | 3 | 0 | 38959.5153 | 1938 | 0 |  | 1542 | 1669 | 0.18315 | 0 | 118.315 | 0 | 0.0018315 | 0 | 1.1832 | 0 | 0.0018315 | 1.1832 | 82846 | 28.3994 | 82845.9982
38959.5157 | 3 | 0 | 38959.5158 | 1968 | 0 |  | 1584 | 1711 | 0.18315 | 0 | 120.1465 | 0 | 0.0018315 | 0 | 1.2015 | 0 | 0.0018315 | 1.2015 | 82846 | 26.4421 | 82845.9982
38959.5162 | 242 | 0 | 38959.5162 | 2428 | 0 |  | 1626 | 1753 | 14.7741 | 0 | 148.2295 | 0 | 0.14774 | 0 | 1.4823 | 0 | 0.14774 | 1.4823 | 928.2562 | 2.4868 | 928.1085
38959.5167 | 1931 | 0 | 38959.5167 | 1975 | 0 |  | 1668 | 1795 | 117.8877 | 0 | 120.5739 | 0 | 1.1789 | 0 | 1.2057 | 0 | 1.1789 | 1.2057 | 28.8648 | 25.9939 | 27.686
38959.5172 | 1888 | 0 | 38959.5172 | 2334 | 0 |  | 1710 | 1837 | 115.2625 | 0 | 142.4908 | 0 | 1.1526 | 0 | 1.4249 | 0 | 1.1526 | 1.4249 | 31.7998 | 6.6144 | 30.6472
38959.5177 | 2115 | 0 | 38959.5177 | 2055 | 0 |  | 1752 | 1879 | 129.1209 | 0 | 125.4579 | 0 | 1.2912 | 0 | 1.2546 | 0 | 1.2912 | 1.2546 | 17.6539 | 21.0891 | 16.3627
38959.5182 | 2075 | 0 | 38959.5182 | 1885 | 0 |  | 1794 | 1921 | 126.6789 | 0 | 115.0794 | 0 | 1.2668 | 0 | 1.1508 | 0 | 1.2668 | 1.1508 | 19.9219 | 32.0095 | 18.6551
38959.5186 | 2180 | 0 | 38959.5187 | 1988 | 0 |  | 1836 | 1963 | 133.0891 | 0 | 121.3675 | 0 | 1.3309 | 0 | 1.2137 | 0 | 1.3309 | 1.2137 | 14.1459 | 25.17 | 12.815
38959.5191 | 2161 | 0 | 38959.5192 | 1960 | 0 |  | 1878 | 2005 | 131.9292 | 0 | 119.6581 | 0 | 1.3193 | 0 | 1.1966 | 0 | 1.3193 | 1.1966 | 15.1495 | 26.9582 | 13.8302
38959.5196 | 2052 | 0 | 38959.5196 | 2130 | 0 |  | 1920 | 2047 | 125.2747 | 0 | 130.0366 | 0 | 1.2527 | 0 | 1.3004 | 0 | 1.2527 | 1.3004 | 21.2661 | 16.8254 | 20.0133
38959.5201 | 2439 | 0 | 38959.5201 | 2134 | 0 |  | 1962 | 2089 | 148.9011 | 0 | 130.2808 | 0 | 1.489 | 0 | 1.3028 | 0 | 1.489 | 1.3028 | 2.0246 | 16.6064 | 0.53559
38959.5206 | 2362 | 0 | 38959.5206 | 2173 | 0 |  | 2004 | 2131 | 144.2002 | 0 | 132.6618 | 0 | 1.442 | 0 | 1.3266 | 0 | 1.442 | 1.3266 | 5.3506 | 14.5136 | 3.9085
38959.5211 | 1895 | 0 | 38959.5211 | 2445 | 0 |  | 2046 | 2173 | 115.6899 | 0 | 149.2674 | 0 | 1.1569 | 0 | 1.4927 | 0 | 1.1569 | 1.4927 | 31.3129 | 1.7742 | 30.156
38959.5216 | 2114 | 0 | 38959.5216 | 2430 | 0 |  | 2088 | 2215 | 129.0598 | 0 | 148.3516 | 0 | 1.2906 | 0 | 1.4835 | 0 | 1.2906 | 1.4835 | 17.7096 | 2.4025 | 16.419
38959.522 | 2024 | 0 | 38959.5221 | 2369 | 0 |  | 2130 | 2257 | 123.5653 | 0 | 144.6276 | 0 | 1.2357 | 0 | 1.4463 | 0 | 1.2357 | 1.4463 | 22.9437 | 5.0393 | 21.708
38959.5225 | 1984 | 0 | 38959.5226 | 2414 | 0 |  | 2172 | 2299 | 121.1233 | 0 | 147.3748 | 0 | 1.2112 | 0 | 1.4737 | 0 | 1.2112 | 1.4737 | 25.4224 | 3.0812 | 24.2111
38959.523 | 2447 | 0 | 38959.523 | 2355 | 0 |  | 2214 | 2341 | 149.3895 | 0 | 143.7729 | 0 | 1.4939 | 0 | 1.4377 | 0 | 1.4939 | 1.4377 | 1.6911 | 5.6637 | 0.19716
38959.5235 | 2009 | 0 | 38959.5235 | 2227 | 0 |  | 2256 | 2383 | 122.6496 | 0 | 135.9585 | 0 | 1.2265 | 0 | 1.3596 | 0 | 1.2265 | 1.3596 | 23.8616 | 11.7369 | 22.6351
38959.524 | 2348 | 0 | 38959.524 | 1923 | 0 |  | 2298 | 2425 | 143.3455 | 0 | 117.3993 | 0 | 1.4335 | 0 | 1.174 | 0 | 1.4335 | 1.174 | 5.9787 | 29.4009 | 4.5452
38959.5245 | 2170 | 0 | 38959.5245 | 2407 | 0 |  | 2340 | 2467 | 132.4786 | 0 | 146.9475 | 0 | 1.3248 | 0 | 1.4695 | 0 | 1.3248 | 1.4695 | 14.6719 | 3.381 | 13.3471
38959.525 | 1900 | 0 | 38959.525 | 2440 | 0 |  | 2382 | 2509 | 115.9951 | 0 | 148.9621 | 0 | 1.16 | 0 | 1.4896 | 0 | 1.16 | 1.4896 | 30.9674 | 1.9828 | 29.8074
38959.5255 | 2097 | 0 | 38959.5255 | 2146 | 0 |  | 2423.5 | 2550.5 | 128.022 | 0 | 131.0134 | 0 | 1.2802 | 0 | 1.3101 | 0 | 1.2802 | 1.3101 | 18.6638 | 15.9543 | 17.3836
38959.5259 | 2286 | 0 | 38959.5259 | 2119 | 0 |  | 2465.5 | 2592.5 | 139.5604 | 0 | 129.3651 | 0 | 1.3956 | 0 | 1.2937 | 0 | 1.3956 | 1.2937 | 8.853 | 17.4318 | 7.4574
38959.5264 | 2279 | 0 | 38959.5264 | 1913 | 0 |  | 2507.5 | 2634.5 | 139.1331 | 0 | 116.7888 | 0 | 1.3913 | 0 | 1.1679 | 0 | 1.3913 | 1.1679 | 9.1874 | 30.0774 | 7.796
38959.5269 | 2104 | 0 | 38959.5269 | 2276 | 0 |  | 2549.5 | 2676.5 | 128.4493 | 0 | 138.9499 | 0 | 1.2845 | 0 | 1.3895 | 0 | 1.2845 | 1.3895 | 18.269 | 9.3313 | 16.9845
38959.5274 | 2340 | 0 | 38959.5274 | 2430 | 0 |  | 2591.5 | 2718.5 | 142.8571 | 0 | 148.3516 | 0 | 1.4286 | 0 | 1.4835 | 0 | 1.4286 | 1.4835 | 6.341 | 2.4025 | 4.9125
38959.5279 | 2199 | 0 | 38959.5279 | 2251 | 0 |  | 2634 | 2761 | 134.2491 | 0 | 137.4237 | 0 | 1.3425 | 0 | 1.3742 | 0 | 1.3425 | 1.3742 | 13.1596 | 10.5455 | 11.8171
38959.5284 | 2417 | 0 | 38959.5284 | 2009 | 0 |  | 2675.5 | 2802.5 | 147.558 | 0 | 122.6496 | 0 | 1.4756 | 0 | 1.2265 | 0 | 1.4756 | 1.2265 | 2.9532 | 23.8616 | 1.4777
38959.5289 | 2438 | 0 | 38959.5289 | 2237 | 0 |  | 2717.5 | 2844.5 | 148.84 | 0 | 136.569 | 0 | 1.4884 | 0 | 1.3657 | 0 | 1.4884 | 1.3657 | 2.0664 | 11.2374 | 0.57805
38959.5293 | 2124 | 0 | 38959.5294 | 2472 | 0 |  | 2759.5 | 2886.5 | 129.6703 | 0 | 150.9158 | 0 | 1.2967 | 0 | 1.5092 | 0 | 1.2967 | 1.5092 | 17.1554 | 0.66262 | 15.8587
38959.5298 | 2463 | 0 | 38959.5298 | 2001 | 0 |  | 2801.5 | 2928.5 | 150.3663 | 0 | 122.1612 | 0 | 1.5037 | 0 | 1.2216 | 0 | 1.5037 | 1.2216 | 1.0305 | 24.3568 | 0.47321
38959.5303 | 2398 | 0 | 38959.5303 | 2244 | 0 |  | 2843.5 | 2970.5 | 146.398 | 0 | 136.9963 | 0 | 1.464 | 0 | 1.37 | 0 | 1.464 | 1.37 | 3.769 | 10.8904 | 2.305
38959.5308 | 2137 | 0 | 38959.5308 | 2300 | 0 |  | 2885.5 | 3012.5 | 130.464 | 0 | 140.4151 | 0 | 1.3046 | 0 | 1.4042 | 0 | 1.3046 | 1.4042 | 16.4427 | 8.1904 | 15.138
38959.5313 | 2436 | 0 | 38959.5313 | 2164 | 0 |  | 2927.5 | 3054.5 | 148.7179 | 0 | 132.1123 | 0 | 1.4872 | 0 | 1.3211 | 0 | 1.4872 | 1.3211 | 2.1502 | 14.9898 | 0.66307
38959.5318 | 1945 | 0 | 38959.5318 | 2140 | 0 |  | 2969.5 | 3096.5 | 118.7424 | 0 | 130.6471 | 0 | 1.1874 | 0 | 1.3065 | 0 | 1.1874 | 1.3065 | 27.9373 | 16.2794 | 26.7499
38959.5323 | 2233 | 0 | 38959.5323 | 1939 | 0 |  | 3011.5 | 3138.5 | 136.3248 | 0 | 118.3761 | 0 | 1.3632 | 0 | 1.1838 | 0 | 1.3632 | 1.1838 | 11.4366 | 28.3332 | 10.0734
38959.5327 | 2248 | 0 | 38959.5328 | 2429 | 0 |  | 3053.5 | 3180.5 | 137.2405 | 0 | 148.2906 | 0 | 1.3724 | 0 | 1.4829 | 0 | 1.3724 | 1.4829 | 10.6931 | 2.4446 | 9.3207
38959.5332 | 2381 | 0 | 38959.5332 | 2167 | 0 |  | 3095.5 | 3222.5 | 145.3602 | 0 | 132.2955 | 0 | 1.4536 | 0 | 1.323 | 0 | 1.4536 | 1.323 | 4.5099 | 14.8306 | 3.0563
38959.5337 | 2032 | 0 | 38959.5337 | 2127 | 0 |  | 3137.5 | 3264.5 | 124.0537 | 0 | 129.8535 | 0 | 1.2405 | 0 | 1.2985 | 0 | 1.2405 | 1.2985 | 22.4596 | 16.9901 | 21.2191
38959.5342 | 1914 | 0 | 38959.5342 | 2092 | 0 |  | 3179.5 | 3306.5 | 116.8498 | 0 | 127.7167 | 0 | 1.1685 | 0 | 1.2772 | 0 | 1.1685 | 1.2772 | 30.0094 | 18.9474 | 28.8409
38959.5347 | 2251 | 0 | 38959.5347 | 2382 | 0 |  | 3221.5 | 3348.5 | 137.4237 | 0 | 145.4212 | 0 | 1.3742 | 0 | 1.4542 | 0 | 1.3742 | 1.4542 | 10.5455 | 4.466 | 9.1713
38959.5352 | 1991 | 0 | 38959.5352 | 2000 | 0 |  | 3263.5 | 3390.5 | 121.5507 | 0 | 122.1001 | 0 | 1.2155 | 0 | 1.221 | 0 | 1.2155 | 1.221 | 24.9814 | 24.419 | 23.7659

## B3-C5
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 152.3431 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
38959.4963 | 1 | 0 | 38959.4963 | 1 | 0 |  | -98.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4967 | 1 | 0 | 38959.4968 | 1 | 0 |  | -56.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4972 | 1 | 0 | 38959.4972 | 1 | 0 |  | -14.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4977 | 1 | 0 | 38959.4977 | 1 | 0 |  | 27.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4982 | 1 | 0 | 38959.4982 | 1 | 0 |  | 69.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4987 | 1 | 0 | 38959.4987 | 1 | 0 |  | 111.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4992 | 1 | 0 | 38959.4992 | 1 | 0 |  | 153.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.4997 | 1 | 0 | 38959.4997 | 1 | 0 |  | 195.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5002 | 1 | 0 | 38959.5002 | 1 | 0 |  | 237.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5006 | 1 | 0 | 38959.5006 | 1 | 0 |  | 279.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5011 | 1 | 0 | 38959.5011 | 1 | 0 |  | 321.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5016 | 1 | 0 | 38959.5016 | 1 | 0 |  | 363.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5021 | 1 | 0 | 38959.5021 | 1 | 0 |  | 405.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5026 | 1 | 0 | 38959.5026 | 1 | 0 |  | 447.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5031 | 1 | 0 | 38959.5031 | 1 | 0 |  | 489.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5036 | 1 | 0 | 38959.5036 | 1 | 0 |  | 531.5 | 658.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.504 | 1 | 0 | 38959.5041 | 1 | 0 |  | 573.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5045 | 1 | 0 | 38959.5045 | 1 | 0 |  | 615.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.505 | 1 | 0 | 38959.505 | 1 | 0 |  | 657.5 | 784.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5055 | 1 | 0 | 38959.5055 | 1 | 0 |  | 699.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.506 | 1 | 0 | 38959.506 | 1 | 0 |  | 741.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5065 | 1 | 0 | 38959.5065 | 1 | 0 |  | 783.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.507 | 1 | 0 | 38959.507 | 1 | 0 |  | 825.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5074 | 1 | 0 | 38959.5075 | 1 | 0 |  | 867 | 994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5079 | 1 | 0 | 38959.5079 | 1 | 0 |  | 909 | 1036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5084 | 1 | 0 | 38959.5084 | 1 | 0 |  | 951 | 1078 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5089 | 1 | 0 | 38959.5089 | 1 | 0 |  | 993 | 1120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5094 | 1 | 0 | 38959.5094 | 1 | 0 |  | 1035.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5099 | 1 | 0 | 38959.5099 | 1 | 0 |  | 1077.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5103 | 1 | 0 | 38959.5104 | 1 | 0 |  | 1119 | 1246 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5108 | 1 | 0 | 38959.5109 | 1 | 0 |  | 1161 | 1288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5113 | 1 | 0 | 38959.5113 | 1 | 0 |  | 1203.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5118 | 1 | 0 | 38959.5118 | 1 | 0 |  | 1245 | 1372 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5123 | 1 | 0 | 38959.5123 | 1 | 0 |  | 1287 | 1414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
38959.5128 | 2 | 0 | 38959.5128 | 1960 | 0 |  | 1329 | 1456 | 0.1221 | 0 | 119.6581 | 0 | 0.001221 | 0 | 1.1966 | 0 | 0.001221 | 1.1966 | 124669 | 27.3153 | 124668.9988
38959.5133 | 2 | 0 | 38959.5133 | 1925 | 0 |  | 1371.5 | 1498.5 | 0.1221 | 0 | 117.5214 | 0 | 0.001221 | 0 | 1.1752 | 0 | 0.001221 | 1.1752 | 124669 | 29.6301 | 124668.9988
38959.5138 | 2 | 0 | 38959.5138 | 2276 | 0 |  | 1413.5 | 1540.5 | 0.1221 | 0 | 138.9499 | 0 | 0.001221 | 0 | 1.3895 | 0 | 0.001221 | 1.3895 | 124669 | 9.6388 | 124668.9988
38959.5142 | 2 | 0 | 38959.5143 | 2053 | 0 |  | 1455.5 | 1582.5 | 0.1221 | 0 | 125.3358 | 0 | 0.001221 | 0 | 1.2534 | 0 | 0.001221 | 1.2534 | 124669 | 21.548 | 124668.9988
38959.5147 | 2 | 0 | 38959.5147 | 2262 | 0 |  | 1497 | 1624 | 0.1221 | 0 | 138.0952 | 0 | 0.001221 | 0 | 1.381 | 0 | 0.001221 | 1.381 | 124669 | 10.3174 | 124668.9988
38959.5152 | 2 | 0 | 38959.5152 | 2322 | 0 |  | 1539 | 1666 | 0.1221 | 0 | 141.7582 | 0 | 0.001221 | 0 | 1.4176 | 0 | 0.001221 | 1.4176 | 124669 | 7.4668 | 124668.9988
38959.5157 | 2 | 0 | 38959.5157 | 2166 | 0 |  | 1581 | 1708 | 0.1221 | 0 | 132.2344 | 0 | 0.001221 | 0 | 1.3223 | 0 | 0.001221 | 1.3223 | 124669 | 15.2068 | 124668.9988
38959.5162 | 139 | 0 | 38959.5162 | 2134 | 0 |  | 1623 | 1750 | 8.486 | 0 | 130.2808 | 0 | 0.08486 | 0 | 1.3028 | 0 | 0.08486 | 1.3028 | 1695.2374 | 16.9344 | 1695.1526
38959.5167 | 1738 | 0 | 38959.5167 | 2291 | 0 |  | 1665 | 1792 | 106.105 | 0 | 139.8657 | 0 | 1.0611 | 0 | 1.3987 | 0 | 1.0611 | 1.3987 | 43.5777 | 8.921 | 42.5166
38959.5172 | 2008 | 0 | 38959.5172 | 1845 | 0 |  | 1707 | 1834 | 122.5885 | 0 | 112.6374 | 0 | 1.2259 | 0 | 1.1264 | 0 | 1.2259 | 1.1264 | 24.2719 | 35.2509 | 23.046
38959.5176 | 1943 | 0 | 38959.5177 | 1934 | 0 |  | 1749 | 1876 | 118.6203 | 0 | 118.0708 | 0 | 1.1862 | 0 | 1.1807 | 0 | 1.1862 | 1.1807 | 28.4292 | 29.0269 | 27.243
38959.5181 | 2124 | 0 | 38959.5181 | 1978 | 0 |  | 1791 | 1918 | 129.6703 | 0 | 120.757 | 0 | 1.2967 | 0 | 1.2076 | 0 | 1.2967 | 1.2076 | 17.4849 | 26.1567 | 16.1882
38959.5186 | 2068 | 0 | 38959.5186 | 2021 | 0 |  | 1833 | 1960 | 126.2515 | 0 | 123.3822 | 0 | 1.2625 | 0 | 1.2338 | 0 | 1.2625 | 1.2338 | 20.6663 | 23.4725 | 19.4038
38959.5191 | 2312 | 0 | 38959.5191 | 1992 | 1 |  | 1875 | 2002 | 141.1477 | 0 | 121.6117 | 0.06105 | 1.4115 | 0 | 1.2161 | 0.0006105 | 1.4115 | 1.2155 | 7.9317 | 25.333 | 6.5202
38959.5196 | 2321 | 0 | 38959.5196 | 2461 | 0 |  | 1917 | 2044 | 141.6972 | 0 | 150.2442 | 0 | 1.417 | 0 | 1.5024 | 0 | 1.417 | 1.5024 | 7.5131 | 1.397 | 6.0962
38959.5201 | 1893 | 0 | 38959.5201 | 2061 | 0 |  | 1959 | 2086 | 115.5678 | 0 | 125.8242 | 0 | 1.1557 | 0 | 1.2582 | 0 | 1.1557 | 1.2582 | 31.8214 | 21.0762 | 30.6658
38959.5206 | 2345 | 0 | 38959.5206 | 1912 | 0 |  | 2001 | 2128 | 143.1624 | 0 | 116.7277 | 0 | 1.4316 | 0 | 1.1673 | 0 | 1.4316 | 1.1673 | 6.4128 | 30.5115 | 4.9812
38959.521 | 1987 | 0 | 38959.5211 | 2344 | 0 |  | 2043 | 2170 | 121.3065 | 0 | 143.1013 | 0 | 1.2131 | 0 | 1.431 | 0 | 1.2131 | 1.431 | 25.5853 | 6.4582 | 24.3722
38959.5215 | 1960 | 0 | 38959.5216 | 2187 | 0 |  | 2085 | 2212 | 119.6581 | 0 | 133.5165 | 0 | 1.1966 | 0 | 1.3352 | 0 | 1.1966 | 1.3352 | 27.3153 | 14.1006 | 26.1187
38959.522 | 1980 | 0 | 38959.522 | 2400 | 0 |  | 2127 | 2254 | 120.8791 | 0 | 146.5201 | 0 | 1.2088 | 0 | 1.4652 | 0 | 1.2088 | 1.4652 | 26.0293 | 3.9742 | 24.8205
38959.5225 | 2435 | 0 | 38959.5225 | 1964 | 0 |  | 2169 | 2296 | 148.6569 | 0 | 119.9023 | 0 | 1.4866 | 0 | 1.199 | 0 | 1.4866 | 1.199 | 2.4797 | 27.056 | 0.9931
38959.523 | 2452 | 0 | 38959.523 | 2327 | 0 |  | 2211 | 2338 | 149.6947 | 0 | 142.0635 | 0 | 1.4969 | 0 | 1.4206 | 0 | 1.4969 | 1.4206 | 1.7692 | 7.2359 | 0.27222
38959.5235 | 2267 | 0 | 38959.5235 | 1921 | 0 |  | 2253 | 2380 | 138.4005 | 0 | 117.2772 | 0 | 1.384 | 0 | 1.1728 | 0 | 1.384 | 1.1728 | 10.0741 | 29.9001 | 8.6901
38959.524 | 2329 | 0 | 38959.524 | 1940 | 0 |  | 2295 | 2422 | 142.1856 | 0 | 118.4371 | 0 | 1.4219 | 0 | 1.1844 | 0 | 1.4219 | 1.1844 | 7.1438 | 28.6278 | 5.722
38959.5244 | 2458 | 0 | 38959.5245 | 2002 | 0 |  | 2337 | 2464 | 150.0611 | 0 | 122.2222 | 0 | 1.5006 | 0 | 1.2222 | 0 | 1.5006 | 1.2222 | 1.5207 | 24.6444 | 0.020138
38959.5249 | 2313 | 0 | 38959.525 | 1931 | 0 |  | 2379 | 2506 | 141.2088 | 0 | 117.8877 | 0 | 1.4121 | 0 | 1.1789 | 0 | 1.4121 | 1.1789 | 7.885 | 29.2273 | 6.4729
38959.5254 | 2182 | 1 | 38959.5254 | 2479 | 0 |  | 2421 | 2548 | 133.2112 | 0.06105 | 151.3431 | 0 | 1.3321 | 0.0006105 | 1.5134 | 0 | 1.3315 | 1.5134 | 15.44 | 0.66075 | 205.0503
38959.5259 | 2285 | 0 | 38959.5259 | 2087 | 0 |  | 2463 | 2590 | 139.4994 | 0 | 127.4115 | 0 | 1.395 | 0 | 1.2741 | 0 | 1.395 | 1.2741 | 9.207 | 19.5678 | 7.812
38959.5264 | 2278 | 0 | 38959.5264 | 2395 | 0 |  | 2505 | 2632 | 139.072 | 0 | 146.2149 | 0 | 1.3907 | 0 | 1.4621 | 0 | 1.3907 | 1.4621 | 9.5426 | 4.1912 | 8.1519
38959.5269 | 1953 | 0 | 38959.5269 | 2238 | 0 |  | 2547 | 2674 | 119.2308 | 0 | 136.63 | 0 | 1.1923 | 0 | 1.3663 | 0 | 1.1923 | 1.3663 | 27.7716 | 11.5004 | 26.5793
38959.5274 | 2006 | 0 | 38959.5274 | 1955 | 0 |  | 2589 | 2716 | 122.4664 | 0 | 119.3529 | 0 | 1.2247 | 0 | 1.1935 | 0 | 1.2247 | 1.1935 | 24.3958 | 27.6409 | 23.1711
38959.5278 | 1916 | 0 | 38959.5279 | 2044 | 0 |  | 2631 | 2758 | 116.9719 | 0 | 124.7863 | 0 | 1.1697 | 0 | 1.2479 | 0 | 1.1697 | 1.2479 | 30.239 | 22.0832 | 29.0693
38959.5283 | 2422 | 0 | 38959.5284 | 2158 | 0 |  | 2673 | 2800 | 147.8632 | 0 | 131.746 | 0 | 1.4786 | 0 | 1.3175 | 0 | 1.4786 | 1.3175 | 3.0297 | 15.6339 | 1.5511
38959.5288 | 2419 | 0 | 38959.5288 | 2235 | 0 |  | 2715 | 2842 | 147.6801 | 0 | 136.4469 | 0 | 1.4768 | 0 | 1.3645 | 0 | 1.4768 | 1.3645 | 3.1575 | 11.6501 | 1.6807
38959.5293 | 2295 | 0 | 38959.5293 | 2128 | 0 |  | 2757 | 2884 | 140.1099 | 0 | 129.9145 | 0 | 1.4011 | 0 | 1.2991 | 0 | 1.4011 | 1.2991 | 8.7312 | 17.2641 | 7.3301
38959.5298 | 2372 | 0 | 38959.5298 | 1944 | 0 |  | 2799 | 2926 | 144.8107 | 0 | 118.6813 | 0 | 1.4481 | 0 | 1.1868 | 0 | 1.4481 | 1.1868 | 5.2015 | 28.3632 | 3.7534
38959.5303 | 2127 | 0 | 38959.5303 | 2028 | 0 |  | 2841 | 2968 | 129.8535 | 0 | 123.8095 | 0 | 1.2985 | 0 | 1.2381 | 0 | 1.2985 | 1.2381 | 17.3192 | 23.0464 | 16.0207
38959.5308 | 2092 | 0 | 38959.5308 | 1955 | 0 |  | 2883 | 3010 | 127.7167 | 0 | 119.3529 | 0 | 1.2772 | 0 | 1.1935 | 0 | 1.2772 | 1.1935 | 19.282 | 27.6409 | 18.0049
38959.5312 | 1975 | 0 | 38959.5313 | 2108 | 0 |  | 2925 | 3052 | 120.5739 | 0 | 128.6935 | 0 | 1.2057 | 0 | 1.2869 | 0 | 1.2057 | 1.2869 | 26.3484 | 18.3767 | 25.1426
38959.5317 | 2223 | 0 | 38959.5318 | 2475 | 0 |  | 2967 | 3094 | 135.7143 | 0 | 151.0989 | 0 | 1.3571 | 0 | 1.511 | 0 | 1.3571 | 1.511 | 12.2528 | 0.82343 | 10.8957
38959.5322 | 2425 | 0 | 38959.5322 | 2346 | 0 |  | 3009 | 3136 | 148.0464 | 0 | 143.2234 | 0 | 1.4805 | 0 | 1.4322 | 0 | 1.4805 | 1.4322 | 2.9023 | 6.3674 | 1.4218
38959.5327 | 1973 | 0 | 38959.5327 | 2029 | 0 |  | 3051 | 3178 | 120.4518 | 0 | 123.8706 | 0 | 1.2045 | 0 | 1.2387 | 0 | 1.2045 | 1.2387 | 26.4764 | 22.9857 | 25.2719
38959.5332 | 1912 | 0 | 38959.5332 | 2184 | 0 |  | 3093 | 3220 | 116.7277 | 0 | 133.3333 | 0 | 1.1673 | 0 | 1.3333 | 0 | 1.1673 | 1.3333 | 30.5115 | 14.2573 | 29.3442
38959.5337 | 2464 | 0 | 38959.5337 | 1937 | 0 |  | 3135 | 3262 | 150.4274 | 0 | 118.254 | 0 | 1.5043 | 0 | 1.1825 | 0 | 1.5043 | 1.1825 | 1.2735 | 28.8271 | 0.23073
38959.5342 | 2239 | 0 | 38959.5342 | 2250 | 0 |  | 3177 | 3304 | 136.6911 | 0 | 137.3626 | 0 | 1.3669 | 0 | 1.3736 | 0 | 1.3669 | 1.3736 | 11.4506 | 10.9058 | 10.0837
38959.5347 | 2289 | 0 | 38959.5347 | 2157 | 0 |  | 3219 | 3346 | 139.7436 | 0 | 131.685 | 0 | 1.3974 | 0 | 1.3168 | 0 | 1.3974 | 1.3168 | 9.0162 | 15.6875 | 7.6187
38959.5351 | 2061 | 0 | 38959.5352 | 2115 | 0 |  | 3261 | 3388 | 125.8242 | 0 | 129.1209 | 0 | 1.2582 | 0 | 1.2912 | 0 | 1.2582 | 1.2912 | 21.0762 | 17.9849 | 19.8179

## B3-B4
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 150.3895 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
38959.4962 | 1 | 0 | 38959.4962 | 1 | 0 |  | -101.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4967 | 1 | 0 | 38959.4967 | 1 | 0 |  | -59.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4972 | 1 | 0 | 38959.4972 | 1 | 0 |  | -17.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4977 | 1 | 0 | 38959.4977 | 1 | 0 |  | 24.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4982 | 1 | 0 | 38959.4982 | 1 | 0 |  | 66.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4987 | 1 | 0 | 38959.4987 | 1 | 0 |  | 108.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4991 | 1 | 0 | 38959.4992 | 1 | 0 |  | 150.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.4996 | 1 | 0 | 38959.4996 | 1 | 0 |  | 192.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5001 | 1 | 0 | 38959.5001 | 1 | 0 |  | 234.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5006 | 1 | 0 | 38959.5006 | 1 | 0 |  | 276.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5011 | 1 | 0 | 38959.5011 | 1 | 0 |  | 318.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5016 | 1 | 0 | 38959.5016 | 1 | 0 |  | 360.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5021 | 1 | 0 | 38959.5021 | 1 | 0 |  | 402.5 | 529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5025 | 1 | 0 | 38959.5026 | 1 | 0 |  | 444.5 | 571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.503 | 1 | 0 | 38959.503 | 1 | 0 |  | 486.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5035 | 1 | 0 | 38959.5035 | 1 | 0 |  | 528.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.504 | 1 | 0 | 38959.504 | 1 | 0 |  | 570.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5045 | 1 | 0 | 38959.5045 | 1 | 0 |  | 612.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.505 | 1 | 0 | 38959.505 | 1 | 0 |  | 654.5 | 781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5055 | 1 | 0 | 38959.5055 | 1 | 0 |  | 696.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5059 | 1 | 0 | 38959.506 | 1 | 0 |  | 738.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5064 | 1 | 0 | 38959.5064 | 1 | 0 |  | 780.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5069 | 1 | 0 | 38959.5069 | 1 | 0 |  | 822.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5074 | 1 | 0 | 38959.5074 | 1 | 0 |  | 864.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5079 | 1 | 0 | 38959.5079 | 1 | 0 |  | 906.5 | 1033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5084 | 1 | 0 | 38959.5084 | 1 | 0 |  | 948.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5089 | 1 | 0 | 38959.5089 | 1 | 0 |  | 990.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5094 | 1 | 0 | 38959.5094 | 1 | 0 |  | 1032.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5098 | 1 | 0 | 38959.5098 | 1 | 0 |  | 1074.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5103 | 1 | 0 | 38959.5103 | 1 | 0 |  | 1116.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5108 | 1 | 0 | 38959.5108 | 1 | 0 |  | 1158.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5113 | 1 | 0 | 38959.5113 | 1 | 0 |  | 1200.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5118 | 1 | 0 | 38959.5118 | 1 | 0 |  | 1242.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5123 | 1 | 0 | 38959.5123 | 1 | 0 |  | 1284.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246238 | 246238 | 246237.9994
38959.5128 | 3 | 0 | 38959.5128 | 2 | 0 |  | 1326.5 | 1453.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5132 | 3 | 0 | 38959.5133 | 2 | 0 |  | 1368.5 | 1495.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5137 | 3 | 0 | 38959.5137 | 3 | 0 |  | 1410.5 | 1537.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82012.6667 | 82012.6667 | 82012.6648
38959.5142 | 3 | 0 | 38959.5142 | 2 | 0 |  | 1452.5 | 1579.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5147 | 3 | 0 | 38959.5147 | 2 | 0 |  | 1494.5 | 1621.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5152 | 3 | 0 | 38959.5152 | 2 | 0 |  | 1536.5 | 1663.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5157 | 3 | 0 | 38959.5157 | 2 | 0 |  | 1578.5 | 1705.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82012.6667 | 123069 | 82012.6648
38959.5162 | 24 | 0 | 38959.5162 | 103 | 0 |  | 1620.5 | 1747.5 | 1.4652 | 0 | 6.2882 | 0 | 0.014652 | 0 | 0.062882 | 0 | 0.014652 | 0.062882 | 10164.0833 | 2291.6311 | 10164.0687
38959.5166 | 1469 | 0 | 38959.5167 | 895 | 0 |  | 1662.5 | 1789.5 | 89.6825 | 0 | 54.6398 | 0 | 0.89683 | 0 | 0.5464 | 0 | 0.89683 | 0.5464 | 67.6909 | 175.238 | 66.7941
38959.5171 | 2268 | 0 | 38959.5171 | 1231 | 0 |  | 1704.5 | 1831.5 | 138.4615 | 0 | 75.1526 | 0 | 1.3846 | 0 | 0.75153 | 0 | 1.3846 | 0.75153 | 8.6146 | 100.1121 | 7.23
38959.5176 | 2322 | 0 | 38959.5176 | 1158 | 0 |  | 1746.5 | 1873.5 | 141.7582 | 0 | 70.696 | 0 | 1.4176 | 0 | 0.70696 | 0 | 1.4176 | 0.70696 | 6.0887 | 112.7271 | 4.6711
38959.5181 | 2234 | 0 | 38959.5181 | 1604 | 0 |  | 1788.5 | 1915.5 | 136.3858 | 0 | 97.9243 | 0 | 1.3639 | 0 | 0.97924 | 0 | 1.3639 | 0.97924 | 10.2677 | 53.5773 | 8.9038
38959.5186 | 2360 | 1 | 38959.5186 | 2200 | 1 |  | 1830.5 | 1957.5 | 144.0781 | 0.06105 | 134.3101 | 0.06105 | 1.4408 | 0.0006105 | 1.3431 | 0.0006105 | 1.4402 | 1.3425 | 4.3978 | 12.1024 | 1105.2791
38959.5191 | 2038 | 1 | 38959.5191 | 2121 | 1 |  | 1872.5 | 1999.5 | 124.42 | 0.06105 | 129.4872 | 0.06105 | 1.2442 | 0.0006105 | 1.2949 | 0.0006105 | 1.2436 | 1.2943 | 20.9462 | 16.1865 | 5912.2265
38959.5196 | 2063 | 1 | 38959.5196 | 2028 | 1 |  | 1914.5 | 2041.5 | 125.9463 | 0.06105 | 123.8095 | 0.06105 | 1.2595 | 0.0006105 | 1.2381 | 0.0006105 | 1.2589 | 1.2375 | 19.4609 | 21.5336 | 7076.3116
38959.52 | 2433 | 0 | 38959.5201 | 1911 | 0 |  | 1956.5 | 2083.5 | 148.5348 | 0 | 116.6667 | 0 | 1.4853 | 0 | 1.1667 | 0 | 1.4853 | 1.1667 | 1.2487 | 28.9053 | 0.23668
38959.5205 | 2412 | 0 | 38959.5205 | 2034 | 0 |  | 1998.5 | 2125.5 | 147.2527 | 0 | 124.1758 | 0 | 1.4725 | 0 | 1.2418 | 0 | 1.4725 | 1.2418 | 2.1302 | 21.1101 | 0.65765
38959.521 | 1913 | 0 | 38959.521 | 1976 | 0 |  | 2040.5 | 2167.5 | 116.7888 | 0 | 120.6349 | 0 | 1.1679 | 0 | 1.2063 | 0 | 1.1679 | 1.2063 | 28.7705 | 24.665 | 27.6026
38959.5215 | 1977 | 0 | 38959.5215 | 1831 | 0 |  | 2082.5 | 2209.5 | 120.696 | 0 | 111.7827 | 0 | 1.207 | 0 | 1.1178 | 0 | 1.207 | 1.1178 | 24.6019 | 34.5374 | 23.395
38959.522 | 1982 | 0 | 38959.522 | 2176 | 0 |  | 2124.5 | 2251.5 | 121.0012 | 0 | 132.8449 | 0 | 1.21 | 0 | 1.3284 | 0 | 1.21 | 1.3284 | 24.2876 | 13.2068 | 23.0776
38959.5225 | 2027 | 0 | 38959.5225 | 2202 | 0 |  | 2166.5 | 2293.5 | 123.7485 | 0 | 134.4322 | 0 | 1.2375 | 0 | 1.3443 | 0 | 1.2375 | 1.3443 | 21.5284 | 11.8701 | 20.2909
38959.523 | 2308 | 0 | 38959.523 | 1900 | 0 |  | 2208.5 | 2335.5 | 140.9035 | 0 | 115.9951 | 0 | 1.409 | 0 | 1.16 | 0 | 1.409 | 1.16 | 6.7322 | 29.6516 | 5.3232
38959.5234 | 2441 | 0 | 38959.5235 | 2129 | 0 |  | 2250 | 2377 | 149.0232 | 0 | 129.9756 | 0 | 1.4902 | 0 | 1.2998 | 0 | 1.4902 | 1.2998 | 0.91684 | 15.706 | 0.57339
38959.5239 | 2424 | 0 | 38959.5239 | 2077 | 0 |  | 2292.5 | 2419.5 | 147.9853 | 0 | 126.801 | 0 | 1.4799 | 0 | 1.268 | 0 | 1.4799 | 1.268 | 1.6246 | 18.6028 | 0.14473
38959.5244 | 1901 | 0 | 38959.5244 | 1846 | 0 |  | 2334.5 | 2461.5 | 116.0562 | 0 | 112.6984 | 0 | 1.1606 | 0 | 1.127 | 0 | 1.1606 | 1.127 | 29.5834 | 33.4442 | 28.4228
38959.5249 | 2344 | 0 | 38959.5249 | 2373 | 0 |  | 2376.5 | 2503.5 | 143.1013 | 0 | 144.8718 | 0 | 1.431 | 0 | 1.4487 | 0 | 1.431 | 1.4487 | 5.093 | 3.8087 | 3.662
38959.5254 | 1940 | 0 | 38959.5254 | 2388 | 0 |  | 2418 | 2545 | 118.4371 | 0 | 145.7875 | 0 | 1.1844 | 0 | 1.4579 | 0 | 1.1844 | 1.4579 | 26.9784 | 3.1566 | 25.794
38959.5259 | 1993 | 0 | 38959.5259 | 2244 | 0 |  | 2460 | 2587 | 121.6728 | 0 | 136.9963 | 0 | 1.2167 | 0 | 1.37 | 0 | 1.2167 | 1.37 | 23.6016 | 9.7763 | 22.3849
38959.5264 | 2129 | 0 | 38959.5264 | 2349 | 0 |  | 2502 | 2629 | 129.9756 | 0 | 143.4066 | 0 | 1.2998 | 0 | 1.4341 | 0 | 1.2998 | 1.4341 | 15.706 | 4.8693 | 14.4062
38959.5268 | 2368 | 0 | 38959.5269 | 2148 | 0 |  | 2544 | 2671 | 144.5665 | 0 | 131.1355 | 0 | 1.4457 | 0 | 1.3114 | 0 | 1.4457 | 1.3114 | 4.0279 | 14.6825 | 2.5822
38959.5273 | 2147 | 0 | 38959.5273 | 2213 | 0 |  | 2586 | 2713 | 131.0745 | 0 | 135.1038 | 0 | 1.3107 | 0 | 1.351 | 0 | 1.3107 | 1.351 | 14.7359 | 11.3141 | 13.4252
38959.5278 | 2176 | 0 | 38959.5278 | 1936 | 0 |  | 2628 | 2755 | 132.8449 | 0 | 118.1929 | 0 | 1.3284 | 0 | 1.1819 | 0 | 1.3284 | 1.1819 | 13.2068 | 27.2407 | 11.8784
38959.5283 | 2418 | 0 | 38959.5283 | 2092 | 0 |  | 2670 | 2797 | 147.619 | 0 | 127.7167 | 0 | 1.4762 | 0 | 1.2772 | 0 | 1.4762 | 1.2772 | 1.8768 | 17.7524 | 0.40057
38959.5288 | 2429 | 0 | 38959.5288 | 1989 | 0 |  | 2712 | 2839 | 148.2906 | 0 | 121.4286 | 0 | 1.4829 | 0 | 1.2143 | 0 | 1.4829 | 1.2143 | 1.4154 | 23.8502 | 0.067509
38959.5293 | 2118 | 0 | 38959.5293 | 1867 | 0 |  | 2754 | 2881 | 129.304 | 0 | 113.9805 | 0 | 1.293 | 0 | 1.1398 | 0 | 1.293 | 1.1398 | 16.3069 | 31.9432 | 15.0139
38959.5298 | 2128 | 0 | 38959.5298 | 2108 | 0 |  | 2796 | 2923 | 129.9145 | 0 | 128.6935 | 0 | 1.2991 | 0 | 1.2869 | 0 | 1.2991 | 1.2869 | 15.7603 | 16.8586 | 14.4612
38959.5302 | 1979 | 0 | 38959.5303 | 2164 | 0 |  | 2838 | 2965 | 120.8181 | 0 | 132.1123 | 0 | 1.2082 | 0 | 1.3211 | 0 | 1.2082 | 1.3211 | 24.476 | 13.8346 | 23.2678
38959.5307 | 2078 | 0 | 38959.5308 | 2219 | 1 |  | 2880 | 3007 | 126.862 | 0 | 135.4701 | 0.06105 | 1.2686 | 0 | 1.3547 | 0.0006105 | 1.2686 | 1.3541 | 18.5457 | 11.0631 | 17.2771
38959.5312 | 2136 | 0 | 38959.5312 | 1970 | 0 |  | 2922 | 3049 | 130.4029 | 0 | 120.2686 | 0 | 1.304 | 0 | 1.2027 | 0 | 1.304 | 1.2027 | 15.3268 | 25.0447 | 14.0227
38959.5317 | 2227 | 0 | 38959.5317 | 2065 | 0 |  | 2964 | 3091 | 135.9585 | 0 | 126.0684 | 0 | 1.3596 | 0 | 1.2607 | 0 | 1.3596 | 1.2607 | 10.6143 | 19.292 | 9.2547
38959.5322 | 2089 | 0 | 38959.5322 | 2393 | 1 |  | 3006 | 3133 | 127.5336 | 0 | 146.0928 | 0.06105 | 1.2753 | 0 | 1.4609 | 0.0006105 | 1.2753 | 1.4603 | 17.9215 | 2.9841 | 16.6462
38959.5327 | 2005 | 0 | 38959.5327 | 2056 | 0 |  | 3048 | 3175 | 122.4054 | 0 | 125.5189 | 0 | 1.2241 | 0 | 1.2552 | 0 | 1.2241 | 1.2552 | 22.8618 | 19.8142 | 21.6378
38959.5332 | 2000 | 0 | 38959.5332 | 2280 | 0 |  | 3090 | 3217 | 122.1001 | 0 | 139.1941 | 0 | 1.221 | 0 | 1.3919 | 0 | 1.221 | 1.3919 | 23.169 | 8.043 | 21.948
38959.5336 | 2447 | 0 | 38959.5337 | 2135 | 0 |  | 3132 | 3259 | 149.3895 | 0 | 130.3419 | 0 | 1.4939 | 0 | 1.3034 | 0 | 1.4939 | 1.3034 | 0.66939 | 15.3808 | 0.8245
38959.5341 | 2385 | 0 | 38959.5342 | 2034 | 0 |  | 3174 | 3301 | 145.6044 | 0 | 124.1758 | 0 | 1.456 | 0 | 1.2418 | 0 | 1.456 | 1.2418 | 3.2864 | 21.1101 | 1.8303
38959.5346 | 2017 | 0 | 38959.5346 | 2152 | 1 |  | 3216 | 3343 | 123.138 | 0 | 131.3797 | 0.06105 | 1.2314 | 0 | 1.3138 | 0.0006105 | 1.2314 | 1.3132 | 22.1309 | 14.5225 | 20.8995
38959.5351 | 2096 | 1 | 38959.5351 | 2255 | 1 |  | 3258 | 3385 | 127.9609 | 0.06105 | 137.6679 | 0.06105 | 1.2796 | 0.0006105 | 1.3767 | 0.0006105 | 1.279 | 1.3761 | 17.6268 | 9.2682 | 3107.6669

## A2-C6
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.0611 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
38959.4962 | 1 | 0 | 38959.4962 | 1 | 0 |  | -104.5 | 22.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4967 | 1 | 0 | 38959.4967 | 1 | 0 |  | -62.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4972 | 1 | 0 | 38959.4972 | 1 | 0 |  | -20 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4977 | 1 | 0 | 38959.4977 | 1 | 0 |  | 21.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4981 | 1 | 0 | 38959.4981 | 1 | 0 |  | 63.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4986 | 1 | 0 | 38959.4986 | 1 | 0 |  | 105.5 | 232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4991 | 1 | 0 | 38959.4991 | 1 | 0 |  | 147.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.4996 | 1 | 0 | 38959.4996 | 1 | 0 |  | 189.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5001 | 1 | 0 | 38959.5001 | 1 | 0 |  | 231.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5006 | 1 | 0 | 38959.5006 | 1 | 0 |  | 273.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5011 | 1 | 0 | 38959.5011 | 1 | 0 |  | 315.5 | 442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5015 | 1 | 0 | 38959.5016 | 1 | 0 |  | 357.5 | 484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.502 | 1 | 0 | 38959.502 | 1 | 0 |  | 399.5 | 526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5025 | 1 | 0 | 38959.5025 | 1 | 0 |  | 441.5 | 568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.503 | 1 | 0 | 38959.503 | 1 | 0 |  | 483.5 | 610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5035 | 1 | 0 | 38959.5035 | 1 | 0 |  | 525.5 | 652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.504 | 1 | 0 | 38959.504 | 1 | 0 |  | 567.5 | 694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5045 | 1 | 0 | 38959.5045 | 1 | 0 |  | 609.5 | 736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5049 | 1 | 0 | 38959.505 | 1 | 0 |  | 651.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5054 | 1 | 0 | 38959.5054 | 1 | 0 |  | 693.5 | 820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5059 | 1 | 0 | 38959.5059 | 1 | 0 |  | 735.5 | 862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5064 | 1 | 0 | 38959.5064 | 1 | 0 |  | 777.5 | 904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5069 | 1 | 0 | 38959.5069 | 1 | 0 |  | 819.5 | 946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5074 | 1 | 0 | 38959.5074 | 1 | 0 |  | 861.5 | 988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5079 | 1 | 0 | 38959.5079 | 1 | 0 |  | 903.5 | 1030.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5083 | 1 | 0 | 38959.5084 | 1 | 0 |  | 945.5 | 1072.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5088 | 1 | 0 | 38959.5088 | 1 | 0 |  | 987.5 | 1114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5093 | 1 | 0 | 38959.5093 | 1 | 0 |  | 1029.5 | 1156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5098 | 1 | 0 | 38959.5098 | 1 | 0 |  | 1071.5 | 1198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5103 | 1 | 0 | 38959.5103 | 1 | 0 |  | 1113.5 | 1240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5108 | 1 | 0 | 38959.5108 | 1 | 0 |  | 1155.5 | 1282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5113 | 1 | 0 | 38959.5113 | 1 | 0 |  | 1197.5 | 1324.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5117 | 1 | 0 | 38959.5118 | 1 | 0 |  | 1239.5 | 1366.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247338 | 247338 | 247337.9994
38959.5122 | 1 | 0 | 38959.5122 | 543 | 0 |  | 1281.5 | 1408.5 | 0.06105 | 0 | 33.1502 | 0 | 0.0006105 | 0 | 0.3315 | 0 | 0.0006105 | 0.3315 | 247338 | 355.6869 | 247337.9994
38959.5127 | 2 | 0 | 38959.5127 | 1302 | 0 |  | 1323.5 | 1450.5 | 0.1221 | 0 | 79.4872 | 0 | 0.001221 | 0 | 0.79487 | 0 | 0.001221 | 0.79487 | 123619 | 90.0445 | 123618.9988
38959.5132 | 2 | 0 | 38959.5132 | 2367 | 0 |  | 1365.5 | 1492.5 | 0.1221 | 0 | 144.5055 | 0 | 0.001221 | 0 | 1.4451 | 0 | 0.001221 | 1.4451 | 123619 | 4.5365 | 123618.9988
38959.5137 | 3 | 0 | 38959.5137 | 2264 | 0 |  | 1407.5 | 1534.5 | 0.18315 | 0 | 138.2173 | 0 | 0.0018315 | 0 | 1.3822 | 0 | 0.0018315 | 1.3822 | 82379.3333 | 9.2924 | 82379.3315
38959.5142 | 3 | 0 | 38959.5142 | 2340 | 0 |  | 1449.5 | 1576.5 | 0.18315 | 0 | 142.8571 | 0 | 0.0018315 | 0 | 1.4286 | 0 | 0.0018315 | 1.4286 | 82379.3333 | 5.7427 | 82379.3315
38959.5147 | 3 | 0 | 38959.5147 | 2426 | 0 |  | 1491.5 | 1618.5 | 0.18315 | 0 | 148.1074 | 0 | 0.0018315 | 0 | 1.4811 | 0 | 0.0018315 | 1.4811 | 82379.3333 | 1.9942 | 82379.3315
38959.5152 | 3 | 0 | 38959.5152 | 2027 | 0 |  | 1533.5 | 1660.5 | 0.18315 | 0 | 123.7485 | 0 | 0.0018315 | 0 | 1.2375 | 0 | 0.0018315 | 1.2375 | 82379.3333 | 22.071 | 82379.3315
38959.5156 | 3 | 0 | 38959.5156 | 1942 | 0 |  | 1575.5 | 1702.5 | 0.18315 | 0 | 118.5592 | 0 | 0.0018315 | 0 | 1.1856 | 0 | 0.0018315 | 1.1856 | 82379.3333 | 27.414 | 82379.3315
38959.5161 | 3 | 0 | 38959.5161 | 2217 | 0 |  | 1617.5 | 1744.5 | 0.18315 | 0 | 135.348 | 0 | 0.0018315 | 0 | 1.3535 | 0 | 0.0018315 | 1.3535 | 82379.3333 | 11.6094 | 82379.3315
38959.5166 | 2 | 0 | 38959.5166 | 2446 | 0 |  | 1659.5 | 1786.5 | 0.1221 | 0 | 149.3284 | 0 | 0.001221 | 0 | 1.4933 | 0 | 0.001221 | 1.4933 | 123619 | 1.1603 | 123618.9988
38959.5171 | 3 | 0 | 38959.5171 | 2386 | 0 |  | 1701.5 | 1828.5 | 0.18315 | 0 | 145.6654 | 0 | 0.0018315 | 0 | 1.4567 | 0 | 0.0018315 | 1.4567 | 82379.3333 | 3.7041 | 82379.3315
38959.5176 | 3 | 0 | 38959.5176 | 2175 | 0 |  | 1743.5 | 1870.5 | 0.18315 | 0 | 132.7839 | 0 | 0.0018315 | 0 | 1.3278 | 0 | 0.0018315 | 1.3278 | 82379.3333 | 13.7646 | 82379.3315
38959.5181 | 3 | 0 | 38959.5181 | 1958 | 0 |  | 1785.5 | 1912.5 | 0.18315 | 0 | 119.536 | 0 | 0.0018315 | 0 | 1.1954 | 0 | 0.0018315 | 1.1954 | 82379.3333 | 26.3728 | 82379.3315
38959.5186 | 3 | 0 | 38959.5186 | 1886 | 0 |  | 1827.5 | 1954.5 | 0.18315 | 0 | 115.1404 | 0 | 0.0018315 | 0 | 1.1514 | 0 | 0.0018315 | 1.1514 | 82379.3333 | 31.1972 | 82379.3315
38959.519 | 2 | 0 | 38959.5191 | 2349 | 0 |  | 1869.5 | 1996.5 | 0.1221 | 0 | 143.4066 | 0 | 0.001221 | 0 | 1.4341 | 0 | 0.001221 | 1.4341 | 123619 | 5.3376 | 123618.9988
38959.5195 | 2 | 0 | 38959.5195 | 2161 | 0 |  | 1911.5 | 2038.5 | 0.1221 | 0 | 131.9292 | 0 | 0.001221 | 0 | 1.3193 | 0 | 0.001221 | 1.3193 | 123619 | 14.5016 | 123618.9988
38959.52 | 2 | 1 | 38959.52 | 2011 | 0 |  | 1953.5 | 2080.5 | 0.1221 | 0.06105 | 122.7717 | 0 | 0.001221 | 0.0006105 | 1.2277 | 0 | 0.0006105 | 1.2277 | 74026.6632 | 42.7378 | 73996.7217
38959.5205 | 3 | 0 | 38959.5205 | 2269 | 0 |  | 1995.5 | 2122.5 | 0.18315 | 0 | 138.5226 | 0 | 0.0018315 | 0 | 1.3852 | 0 | 0.0018315 | 1.3852 | 82379.3333 | 9.0516 | 82379.3315
38959.521 | 3 | 0 | 38959.521 | 2444 | 0 |  | 2037.5 | 2164.5 | 0.18315 | 0 | 149.2063 | 0 | 0.0018315 | 0 | 1.4921 | 0 | 0.0018315 | 1.4921 | 82379.3333 | 1.243 | 82379.3315
38959.5215 | 2 | 0 | 38959.5215 | 2449 | 0 |  | 2079.5 | 2206.5 | 0.1221 | 0 | 149.5116 | 0 | 0.001221 | 0 | 1.4951 | 0 | 0.001221 | 1.4951 | 123619 | 1.0363 | 123618.9988
38959.522 | 3 | 0 | 38959.522 | 2048 | 0 |  | 2121.5 | 2248.5 | 0.18315 | 0 | 125.0305 | 0 | 0.0018315 | 0 | 1.2503 | 0 | 0.0018315 | 1.2503 | 82379.3333 | 20.8193 | 82379.3315
38959.5224 | 2 | 0 | 38959.5225 | 2205 | 0 |  | 2163.5 | 2290.5 | 0.1221 | 0 | 134.6154 | 0 | 0.001221 | 0 | 1.3462 | 0 | 0.001221 | 1.3462 | 123619 | 12.2168 | 123618.9988
38959.5229 | 3 | 0 | 38959.5229 | 2371 | 0 |  | 2205.5 | 2332.5 | 0.18315 | 0 | 144.7497 | 0 | 0.0018315 | 0 | 1.4475 | 0 | 0.0018315 | 1.4475 | 82379.3333 | 4.3602 | 82379.3315
38959.5234 | 2 | 0 | 38959.5234 | 2090 | 0 |  | 2247.5 | 2374.5 | 0.1221 | 0 | 127.5946 | 0 | 0.001221 | 0 | 1.2759 | 0 | 0.001221 | 1.2759 | 123619 | 18.3914 | 123618.9988
38959.5239 | 3 | 0 | 38959.5239 | 2016 | 0 |  | 2289.5 | 2416.5 | 0.18315 | 0 | 123.0769 | 0 | 0.0018315 | 0 | 1.2308 | 0 | 0.0018315 | 1.2308 | 82379.3333 | 22.7371 | 82379.3315
38959.5244 | 2 | 0 | 38959.5244 | 2382 | 0 |  | 2331.5 | 2458.5 | 0.1221 | 0 | 145.4212 | 0 | 0.001221 | 0 | 1.4542 | 0 | 0.001221 | 1.4542 | 123619 | 3.8783 | 123618.9988
38959.5249 | 2 | 0 | 38959.5249 | 2259 | 0 |  | 2373.5 | 2500.5 | 0.1221 | 0 | 137.9121 | 0 | 0.001221 | 0 | 1.3791 | 0 | 0.001221 | 1.3791 | 123619 | 9.5343 | 123618.9988
38959.5254 | 2 | 0 | 38959.5254 | 2160 | 0 |  | 2415.5 | 2542.5 | 0.1221 | 0 | 131.8681 | 0 | 0.001221 | 0 | 1.3187 | 0 | 0.001221 | 1.3187 | 123619 | 14.5546 | 123618.9988
38959.5258 | 3 | 0 | 38959.5259 | 2314 | 0 |  | 2457.5 | 2584.5 | 0.18315 | 0 | 141.2698 | 0 | 0.0018315 | 0 | 1.4127 | 0 | 0.0018315 | 1.4127 | 82379.3333 | 6.9309 | 82379.3315
38959.5263 | 2 | 0 | 38959.5263 | 2018 | 0 |  | 2499.5 | 2626.5 | 0.1221 | 0 | 123.199 | 0 | 0.001221 | 0 | 1.232 | 0 | 0.001221 | 1.232 | 123619 | 22.6155 | 123618.9988
38959.5268 | 3 | 0 | 38959.5268 | 1930 | 0 |  | 2541.5 | 2668.5 | 0.18315 | 0 | 117.8266 | 0 | 0.0018315 | 0 | 1.1783 | 0 | 0.0018315 | 1.1783 | 82379.3333 | 28.2062 | 82379.3315
38959.5273 | 3 | 0 | 38959.5273 | 2227 | 0 |  | 2583.5 | 2710.5 | 0.18315 | 0 | 135.9585 | 0 | 0.0018315 | 0 | 1.3596 | 0 | 0.0018315 | 1.3596 | 82379.3333 | 11.1082 | 82379.3315
38959.5278 | 5 | 0 | 38959.5278 | 2012 | 0 |  | 2625.5 | 2752.5 | 0.30525 | 0 | 122.8327 | 0 | 0.0030525 | 0 | 1.2283 | 0 | 0.0030525 | 1.2283 | 49387.6 | 22.9811 | 49387.5969
38959.5283 | 14 | 0 | 38959.5283 | 2365 | 0 |  | 2667.5 | 2794.5 | 0.8547 | 0 | 144.3834 | 0 | 0.008547 | 0 | 1.4438 | 0 | 0.008547 | 1.4438 | 17574.1429 | 4.6249 | 17574.1343
38959.5288 | 30 | 0 | 38959.5288 | 2408 | 0 |  | 2709.5 | 2836.5 | 1.8315 | 0 | 147.0085 | 0 | 0.018315 | 0 | 1.4701 | 0 | 0.018315 | 1.4701 | 8147.9333 | 2.7566 | 8147.915
38959.5292 | 52 | 0 | 38959.5293 | 2362 | 0 |  | 2751.5 | 2878.5 | 3.1746 | 0 | 144.2002 | 0 | 0.031746 | 0 | 1.442 | 0 | 0.031746 | 1.442 | 4658.4231 | 4.7578 | 4658.3913
38959.5297 | 99 | 0 | 38959.5297 | 1920 | 0 |  | 2793.5 | 2920.5 | 6.044 | 0 | 117.2161 | 0 | 0.06044 | 0 | 1.1722 | 0 | 0.06044 | 1.1722 | 2399.3737 | 28.874 | 2399.3133
38959.5302 | 109 | 0 | 38959.5302 | 2063 | 0 |  | 2835.5 | 2962.5 | 6.6545 | 0 | 125.9463 | 0 | 0.066545 | 0 | 1.2595 | 0 | 0.066545 | 1.2595 | 2170.0734 | 19.9409 | 2170.0068
38959.5307 | 174 | 0 | 38959.5307 | 2236 | 0 |  | 2877.5 | 3004.5 | 10.6227 | 0 | 136.5079 | 0 | 0.10623 | 0 | 1.3651 | 0 | 0.10623 | 1.3651 | 1322.0575 | 10.661 | 1321.9512
38959.5312 | 1879 | 0 | 38959.5312 | 2424 | 0 |  | 2919.5 | 3046.5 | 114.7131 | 0 | 147.9853 | 0 | 1.1471 | 0 | 1.4799 | 0 | 1.1471 | 1.4799 | 31.686 | 2.0784 | 30.5389
38959.5317 | 2005 | 0 | 38959.5317 | 2458 | 0 |  | 2961.5 | 3088.5 | 122.4054 | 0 | 150.0611 | 0 | 1.2241 | 0 | 1.5006 | 0 | 1.2241 | 1.5006 | 23.4105 | 0.6664 | 22.1864
38959.5322 | 2166 | 0 | 38959.5322 | 1999 | 0 |  | 3003.5 | 3130.5 | 132.2344 | 0 | 122.0391 | 0 | 1.3223 | 0 | 1.2204 | 0 | 1.3223 | 1.2204 | 14.2373 | 23.7809 | 12.915
38959.5327 | 2179 | 0 | 38959.5327 | 2161 | 0 |  | 3045.5 | 3172.5 | 133.0281 | 0 | 131.9292 | 0 | 1.3303 | 0 | 1.3193 | 0 | 1.3303 | 1.3193 | 13.5558 | 14.5016 | 12.2255
38959.5331 | 2205 | 0 | 38959.5331 | 2453 | 0 |  | 3087.5 | 3214.5 | 134.6154 | 0 | 149.7558 | 0 | 1.3462 | 0 | 1.4976 | 0 | 1.3462 | 1.4976 | 12.2168 | 0.87159 | 10.8706
38959.5336 | 2006 | 0 | 38959.5336 | 2007 | 0 |  | 3129.5 | 3256.5 | 122.4664 | 0 | 122.5275 | 0 | 1.2247 | 0 | 1.2253 | 0 | 1.2247 | 1.2253 | 23.349 | 23.2875 | 22.1243
38959.5341 | 1833 | 0 | 38959.5341 | 1906 | 0 |  | 3171.5 | 3298.5 | 111.9048 | 0 | 116.3614 | 0 | 1.119 | 0 | 1.1636 | 0 | 1.119 | 1.1636 | 34.9907 | 29.8206 | 33.8717
38959.5346 | 2216 | 0 | 38959.5346 | 2081 | 0 |  | 3213.5 | 3340.5 | 135.2869 | 0 | 127.0452 | 0 | 1.3529 | 0 | 1.2705 | 0 | 1.3529 | 1.2705 | 11.6597 | 18.9034 | 10.3069
38959.5351 | 1954 | 0 | 38959.5351 | 2346 | 0 |  | 3255.5 | 3382.5 | 119.2918 | 0 | 143.2234 | 0 | 1.1929 | 0 | 1.4322 | 0 | 1.1929 | 1.4322 | 26.6315 | 5.4723 | 25.4386

## A2-C5
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 152.0989 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
38959.4962 | 1 | 0 | 38959.4962 | 1 | 0 |  | -107 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4966 | 1 | 0 | 38959.4967 | 1 | 0 |  | -65 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4971 | 1 | 0 | 38959.4972 | 1 | 0 |  | -23 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4976 | 1 | 0 | 38959.4976 | 1 | 0 |  | 19 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4981 | 1 | 0 | 38959.4981 | 1 | 0 |  | 61 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4986 | 1 | 0 | 38959.4986 | 1 | 0 |  | 103 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4991 | 1 | 0 | 38959.4991 | 1 | 0 |  | 145 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.4996 | 1 | 0 | 38959.4996 | 1 | 0 |  | 187 | 314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5 | 1 | 0 | 38959.5001 | 1 | 0 |  | 229 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5005 | 1 | 0 | 38959.5006 | 1 | 0 |  | 271 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.501 | 1 | 0 | 38959.501 | 1 | 0 |  | 313 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5015 | 1 | 0 | 38959.5015 | 1 | 0 |  | 355 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.502 | 1 | 0 | 38959.502 | 1 | 0 |  | 397 | 524 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5025 | 1 | 0 | 38959.5025 | 1 | 0 |  | 439 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.503 | 1 | 0 | 38959.503 | 1 | 0 |  | 481 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5034 | 1 | 0 | 38959.5035 | 1 | 0 |  | 523 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5039 | 1 | 0 | 38959.504 | 1 | 0 |  | 565 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5044 | 1 | 0 | 38959.5044 | 1 | 0 |  | 607 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5049 | 1 | 0 | 38959.5049 | 1 | 0 |  | 649 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5054 | 1 | 0 | 38959.5054 | 1 | 0 |  | 691 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5059 | 1 | 0 | 38959.5059 | 1 | 0 |  | 733 | 860 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5064 | 1 | 0 | 38959.5064 | 1 | 0 |  | 775 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5069 | 1 | 0 | 38959.5069 | 1 | 0 |  | 817 | 944 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5073 | 1 | 0 | 38959.5074 | 1 | 0 |  | 859 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5078 | 1 | 0 | 38959.5078 | 1 | 0 |  | 900.5 | 1027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5083 | 1 | 0 | 38959.5083 | 1 | 0 |  | 942.5 | 1069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5088 | 1 | 0 | 38959.5088 | 1 | 0 |  | 984.5 | 1111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5093 | 1 | 0 | 38959.5093 | 1 | 0 |  | 1027 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5098 | 1 | 0 | 38959.5098 | 1 | 0 |  | 1069 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5103 | 1 | 0 | 38959.5103 | 1 | 0 |  | 1111 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5107 | 1 | 0 | 38959.5108 | 1 | 0 |  | 1152.5 | 1279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5112 | 1 | 0 | 38959.5113 | 1 | 0 |  | 1195 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5117 | 1 | 0 | 38959.5117 | 1 | 0 |  | 1236.5 | 1363.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5122 | 1 | 0 | 38959.5122 | 1 | 0 |  | 1279 | 1406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
38959.5127 | 1 | 0 | 38959.5127 | 2332 | 0 |  | 1320.5 | 1447.5 | 0.06105 | 0 | 142.3687 | 0 | 0.0006105 | 0 | 1.4237 | 0 | 0.0006105 | 1.4237 | 249038 | 6.8345 | 249037.9994
38959.5132 | 2 | 0 | 38959.5132 | 2403 | 0 |  | 1363 | 1490 | 0.1221 | 0 | 146.7033 | 0 | 0.001221 | 0 | 1.467 | 0 | 0.001221 | 1.467 | 124469 | 3.6779 | 124468.9988
38959.5137 | 2 | 0 | 38959.5137 | 2449 | 0 |  | 1404.5 | 1531.5 | 0.1221 | 0 | 149.5116 | 0 | 0.001221 | 0 | 1.4951 | 0 | 0.001221 | 1.4951 | 124469 | 1.7305 | 124468.9988
38959.5141 | 2 | 0 | 38959.5142 | 2339 | 0 |  | 1446.5 | 1573.5 | 0.1221 | 0 | 142.7961 | 0 | 0.001221 | 0 | 1.428 | 0 | 0.001221 | 1.428 | 124469 | 6.5147 | 124468.9988
38959.5146 | 2 | 0 | 38959.5146 | 2228 | 0 |  | 1488.5 | 1615.5 | 0.1221 | 0 | 136.0195 | 0 | 0.001221 | 0 | 1.3602 | 0 | 0.001221 | 1.3602 | 124469 | 11.8214 | 124468.9988
38959.5151 | 2 | 0 | 38959.5151 | 2430 | 0 |  | 1530.5 | 1657.5 | 0.1221 | 0 | 148.3516 | 0 | 0.001221 | 0 | 1.4835 | 0 | 0.001221 | 1.4835 | 124469 | 2.5259 | 124468.9988
38959.5156 | 2 | 0 | 38959.5156 | 2198 | 0 |  | 1572.5 | 1699.5 | 0.1221 | 0 | 134.188 | 0 | 0.001221 | 0 | 1.3419 | 0 | 0.001221 | 1.3419 | 124469 | 13.3476 | 124468.9988
38959.5161 | 2 | 0 | 38959.5161 | 2333 | 0 |  | 1614.5 | 1741.5 | 0.1221 | 0 | 142.4298 | 0 | 0.001221 | 0 | 1.4243 | 0 | 0.001221 | 1.4243 | 124469 | 6.7887 | 124468.9988
38959.5166 | 2 | 0 | 38959.5166 | 2058 | 0 |  | 1656.5 | 1783.5 | 0.1221 | 0 | 125.641 | 0 | 0.001221 | 0 | 1.2564 | 0 | 0.001221 | 1.2564 | 124469 | 21.0583 | 124468.9988
38959.5171 | 2 | 0 | 38959.5171 | 2376 | 0 |  | 1698.5 | 1825.5 | 0.1221 | 0 | 145.0549 | 0 | 0.001221 | 0 | 1.4505 | 0 | 0.001221 | 1.4505 | 124469 | 4.8561 | 124468.9988
38959.5175 | 2 | 0 | 38959.5176 | 2385 | 0 |  | 1740.5 | 1867.5 | 0.1221 | 0 | 145.6044 | 0 | 0.001221 | 0 | 1.456 | 0 | 0.001221 | 1.456 | 124469 | 4.4604 | 124468.9988
38959.518 | 2 | 0 | 38959.518 | 1952 | 0 |  | 1782.5 | 1909.5 | 0.1221 | 0 | 119.1697 | 0 | 0.001221 | 0 | 1.1917 | 0 | 0.001221 | 1.1917 | 124469 | 27.6322 | 124468.9988
38959.5185 | 2 | 0 | 38959.5185 | 1921 | 0 |  | 1824.5 | 1951.5 | 0.1221 | 0 | 117.2772 | 0 | 0.001221 | 0 | 1.1728 | 0 | 0.001221 | 1.1728 | 124469 | 29.6918 | 124468.9988
38959.519 | 2 | 0 | 38959.519 | 2460 | 0 |  | 1866.5 | 1993.5 | 0.1221 | 0 | 150.1832 | 0 | 0.001221 | 0 | 1.5018 | 0 | 0.001221 | 1.5018 | 124469 | 1.2756 | 124468.9988
38959.5195 | 2 | 0 | 38959.5195 | 2144 | 1 |  | 1908.5 | 2035.5 | 0.1221 | 0 | 130.8913 | 0.06105 | 0.001221 | 0 | 1.3089 | 0.0006105 | 0.001221 | 1.3083 | 124469 | 16.2566 | 124468.9988
38959.52 | 3 | 0 | 38959.52 | 2072 | 0 |  | 1950.5 | 2077.5 | 0.18315 | 0 | 126.4957 | 0 | 0.0018315 | 0 | 1.265 | 0 | 0.0018315 | 1.265 | 82946 | 20.2403 | 82945.9982
38959.5205 | 3 | 0 | 38959.5205 | 2255 | 0 |  | 1992.5 | 2119.5 | 0.18315 | 0 | 137.6679 | 0 | 0.0018315 | 0 | 1.3767 | 0 | 0.0018315 | 1.3767 | 82946 | 10.4825 | 82945.9982
38959.5209 | 2 | 0 | 38959.521 | 2475 | 1 |  | 2034.5 | 2161.5 | 0.1221 | 0 | 151.0989 | 0.06105 | 0.001221 | 0 | 1.511 | 0.0006105 | 0.001221 | 1.5104 | 124469 | 0.70251 | 124468.9988
38959.5214 | 2 | 0 | 38959.5214 | 2132 | 0 |  | 2076.5 | 2203.5 | 0.1221 | 0 | 130.1587 | 0 | 0.001221 | 0 | 1.3016 | 0 | 0.001221 | 1.3016 | 124469 | 16.8565 | 124468.9988
38959.5219 | 3 | 0 | 38959.5219 | 2313 | 0 |  | 2118.5 | 2245.5 | 0.18315 | 0 | 141.2088 | 0 | 0.0018315 | 0 | 1.4121 | 0 | 0.0018315 | 1.4121 | 82946 | 7.7121 | 82945.9982
38959.5224 | 2 | 0 | 38959.5224 | 2350 | 0 |  | 2160.5 | 2287.5 | 0.1221 | 0 | 143.4676 | 0 | 0.001221 | 0 | 1.4347 | 0 | 0.001221 | 1.4347 | 124469 | 6.0162 | 124468.9988
38959.5229 | 2 | 0 | 38959.5229 | 2086 | 0 |  | 2202.5 | 2329.5 | 0.1221 | 0 | 127.3504 | 0 | 0.001221 | 0 | 1.2735 | 0 | 0.001221 | 1.2735 | 124469 | 19.4334 | 124468.9988
38959.5234 | 2 | 0 | 38959.5234 | 2057 | 0 |  | 2244.5 | 2371.5 | 0.1221 | 0 | 125.58 | 0 | 0.001221 | 0 | 1.2558 | 0 | 0.001221 | 1.2558 | 124469 | 21.1172 | 124468.9988
38959.5239 | 2 | 0 | 38959.5239 | 2314 | 0 |  | 2286.5 | 2413.5 | 0.1221 | 0 | 141.2698 | 0 | 0.001221 | 0 | 1.4127 | 0 | 0.001221 | 1.4127 | 124469 | 7.6655 | 124468.9988
38959.5244 | 2 | 0 | 38959.5244 | 2045 | 0 |  | 2328.5 | 2455.5 | 0.1221 | 0 | 124.8474 | 0 | 0.001221 | 0 | 1.2485 | 0 | 0.001221 | 1.2485 | 124469 | 21.8279 | 124468.9988
38959.5248 | 2 | 0 | 38959.5248 | 2235 | 0 |  | 2370.5 | 2497.5 | 0.1221 | 0 | 136.4469 | 0 | 0.001221 | 0 | 1.3645 | 0 | 0.001221 | 1.3645 | 124469 | 11.4711 | 124468.9988
38959.5253 | 2 | 0 | 38959.5253 | 2050 | 0 |  | 2412.5 | 2539.5 | 0.1221 | 0 | 125.1526 | 0 | 0.001221 | 0 | 1.2515 | 0 | 0.001221 | 1.2515 | 124469 | 21.5307 | 124468.9988
38959.5258 | 2 | 0 | 38959.5258 | 2134 | 0 |  | 2454.5 | 2581.5 | 0.1221 | 0 | 130.2808 | 0 | 0.001221 | 0 | 1.3028 | 0 | 0.001221 | 1.3028 | 124469 | 16.747 | 124468.9988
38959.5263 | 2 | 0 | 38959.5263 | 2062 | 0 |  | 2496.5 | 2623.5 | 0.1221 | 0 | 125.8852 | 0 | 0.001221 | 0 | 1.2589 | 0 | 0.001221 | 1.2589 | 124469 | 20.8235 | 124468.9988
38959.5268 | 2 | 0 | 38959.5268 | 2235 | 0 |  | 2538.5 | 2665.5 | 0.1221 | 0 | 136.4469 | 0 | 0.001221 | 0 | 1.3645 | 0 | 0.001221 | 1.3645 | 124469 | 11.4711 | 124468.9988
38959.5273 | 3 | 0 | 38959.5273 | 2229 | 0 |  | 2580.5 | 2707.5 | 0.18315 | 0 | 136.0806 | 0 | 0.0018315 | 0 | 1.3608 | 0 | 0.0018315 | 1.3608 | 82946 | 11.7712 | 82945.9982
38959.5278 | 4 | 0 | 38959.5278 | 2420 | 0 |  | 2622.5 | 2749.5 | 0.2442 | 0 | 147.7411 | 0 | 0.002442 | 0 | 1.4774 | 0 | 0.002442 | 1.4774 | 62184.5 | 2.9496 | 62184.4976
38959.5282 | 13 | 0 | 38959.5283 | 2264 | 0 |  | 2664.5 | 2791.5 | 0.79365 | 0 | 138.2173 | 0 | 0.0079365 | 0 | 1.3822 | 0 | 0.0079365 | 1.3822 | 19064.4615 | 10.0433 | 19064.4536
38959.5287 | 22 | 0 | 38959.5287 | 1985 | 0 |  | 2706.5 | 2833.5 | 1.3431 | 0 | 121.1844 | 0 | 0.013431 | 0 | 1.2118 | 0 | 0.013431 | 1.2118 | 11224.4545 | 25.5103 | 11224.4411
38959.5292 | 47 | 0 | 38959.5292 | 2453 | 0 |  | 2748.5 | 2875.5 | 2.8694 | 0 | 149.7558 | 0 | 0.028694 | 0 | 1.4976 | 0 | 0.028694 | 1.4976 | 5200.8085 | 1.5646 | 5200.7798
38959.5297 | 88 | 0 | 38959.5297 | 2385 | 0 |  | 2790.5 | 2917.5 | 5.3724 | 0 | 145.6044 | 0 | 0.053724 | 0 | 1.456 | 0 | 0.053724 | 1.456 | 2731.1136 | 4.4604 | 2731.0599
38959.5302 | 110 | 0 | 38959.5302 | 2259 | 0 |  | 2832.5 | 2959.5 | 6.7155 | 0 | 137.9121 | 0 | 0.067155 | 0 | 1.3791 | 0 | 0.067155 | 1.3791 | 2164.8909 | 10.2869 | 2164.8238
38959.5307 | 185 | 0 | 38959.5307 | 2184 | 0 |  | 2874.5 | 3001.5 | 11.2943 | 0 | 133.3333 | 0 | 0.11294 | 0 | 1.3333 | 0 | 0.11294 | 1.3333 | 1246.6919 | 14.0742 | 1246.5789
38959.5312 | 1486 | 0 | 38959.5312 | 2162 | 0 |  | 2916.5 | 3043.5 | 90.7204 | 0 | 131.9902 | 0 | 0.9072 | 0 | 1.3199 | 0 | 0.9072 | 1.3199 | 67.6568 | 15.235 | 66.7496
38959.5316 | 2118 | 0 | 38959.5317 | 2142 | 0 |  | 2958.5 | 3085.5 | 129.304 | 0 | 130.7692 | 0 | 1.293 | 0 | 1.3077 | 0 | 1.293 | 1.3077 | 17.6289 | 16.3109 | 16.3359
38959.5321 | 2021 | 0 | 38959.5321 | 1988 | 0 |  | 3000.5 | 3127.5 | 123.3822 | 0 | 121.3675 | 0 | 1.2338 | 0 | 1.2137 | 0 | 1.2338 | 1.2137 | 23.2746 | 25.3209 | 22.0408
38959.5326 | 1854 | 0 | 38959.5326 | 2030 | 0 |  | 3042.5 | 3169.5 | 113.1868 | 0 | 123.9316 | 0 | 1.1319 | 0 | 1.2393 | 0 | 1.1319 | 1.2393 | 34.3786 | 22.7281 | 33.2468
38959.5331 | 2306 | 0 | 38959.5331 | 2287 | 0 |  | 3084.5 | 3211.5 | 140.7814 | 0 | 139.6215 | 0 | 1.4078 | 0 | 1.3962 | 0 | 1.4078 | 1.3962 | 8.039 | 8.9366 | 6.6312
38959.5336 | 2182 | 0 | 38959.5336 | 2445 | 0 |  | 3126.5 | 3253.5 | 133.2112 | 0 | 149.2674 | 0 | 1.3321 | 0 | 1.4927 | 0 | 1.3321 | 1.4927 | 14.1787 | 1.8969 | 12.8466
38959.5341 | 2290 | 0 | 38959.5341 | 1927 | 0 |  | 3168.5 | 3295.5 | 139.8046 | 0 | 117.6435 | 0 | 1.398 | 0 | 1.1764 | 0 | 1.398 | 1.1764 | 8.7939 | 29.288 | 7.3958
38959.5346 | 2050 | 0 | 38959.5346 | 2468 | 0 |  | 3210.5 | 3337.5 | 125.1526 | 0 | 150.6716 | 0 | 1.2515 | 0 | 1.5067 | 0 | 1.2515 | 1.5067 | 21.5307 | 0.94733 | 20.2792
38959.535 | 2035 | 0 | 38959.5351 | 2034 | 0 |  | 3252.5 | 3379.5 | 124.2369 | 0 | 124.1758 | 0 | 1.2424 | 0 | 1.2418 | 0 | 1.2424 | 1.2418 | 22.4265 | 22.4867 | 21.1842

## A2-B4
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 139.4615 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-13 | N11 | N12 | Time-14 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
38959.4961 | 1 | 0 | 38959.4961 | 1 | 0 |  | -110 | 17 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4966 | 1 | 0 | 38959.4966 | 1 | 0 |  | -67.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4971 | 1 | 0 | 38959.4971 | 1 | 0 |  | -26 | 101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4976 | 1 | 0 | 38959.4976 | 1 | 0 |  | 16.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4981 | 1 | 0 | 38959.4981 | 1 | 0 |  | 58 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4986 | 1 | 0 | 38959.4986 | 1 | 0 |  | 100 | 227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.499 | 1 | 0 | 38959.4991 | 1 | 0 |  | 142 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.4995 | 1 | 0 | 38959.4995 | 1 | 0 |  | 184 | 311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5 | 1 | 0 | 38959.5 | 1 | 0 |  | 226 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5005 | 1 | 0 | 38959.5005 | 1 | 0 |  | 268 | 395 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.501 | 1 | 0 | 38959.501 | 1 | 0 |  | 310 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5015 | 1 | 0 | 38959.5015 | 1 | 0 |  | 352 | 479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.502 | 1 | 0 | 38959.502 | 1 | 0 |  | 394 | 521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5024 | 1 | 0 | 38959.5025 | 1 | 0 |  | 436 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5029 | 1 | 0 | 38959.503 | 1 | 0 |  | 478 | 605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5034 | 1 | 0 | 38959.5034 | 1 | 0 |  | 520 | 647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5039 | 1 | 0 | 38959.5039 | 1 | 0 |  | 562 | 689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5044 | 1 | 0 | 38959.5044 | 1 | 0 |  | 604 | 731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5049 | 1 | 0 | 38959.5049 | 1 | 0 |  | 646 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5054 | 1 | 0 | 38959.5054 | 1 | 0 |  | 688 | 815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5058 | 1 | 0 | 38959.5059 | 1 | 0 |  | 730 | 857 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5063 | 1 | 0 | 38959.5064 | 1 | 0 |  | 772 | 899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5068 | 1 | 0 | 38959.5068 | 1 | 0 |  | 814 | 941 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5073 | 1 | 0 | 38959.5073 | 1 | 0 |  | 856 | 983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5078 | 1 | 0 | 38959.5078 | 1 | 0 |  | 898 | 1025 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5083 | 1 | 0 | 38959.5083 | 1 | 0 |  | 940 | 1067 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5088 | 1 | 0 | 38959.5088 | 1 | 0 |  | 982 | 1109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5092 | 1 | 0 | 38959.5093 | 1 | 0 |  | 1024 | 1151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5097 | 1 | 0 | 38959.5098 | 1 | 0 |  | 1066 | 1193 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5102 | 1 | 0 | 38959.5102 | 1 | 0 |  | 1108 | 1235 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5107 | 1 | 0 | 38959.5107 | 1 | 0 |  | 1150 | 1277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5112 | 1 | 0 | 38959.5112 | 1 | 0 |  | 1192 | 1319 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5117 | 1 | 0 | 38959.5117 | 1 | 0 |  | 1234 | 1361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5122 | 1 | 0 | 38959.5122 | 1 | 0 |  | 1276 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 228338 | 228338 | 228337.9994
38959.5127 | 2 | 0 | 38959.5127 | 2 | 0 |  | 1318 | 1445 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5131 | 2 | 0 | 38959.5132 | 2 | 0 |  | 1360 | 1487 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5136 | 2 | 0 | 38959.5136 | 2 | 0 |  | 1402 | 1529 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5141 | 2 | 0 | 38959.5141 | 2 | 1 |  | 1444 | 1571 | 0.1221 | 0 | 0.1221 | 0.06105 | 0.001221 | 0 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 114119 | 228338 | 114118.9988
38959.5146 | 2 | 0 | 38959.5146 | 2 | 0 |  | 1486 | 1613 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5151 | 2 | 0 | 38959.5151 | 2 | 0 |  | 1528 | 1655 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5156 | 2 | 0 | 38959.5156 | 2 | 0 |  | 1570 | 1697 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5161 | 2 | 0 | 38959.5161 | 2 | 0 |  | 1612 | 1739 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5165 | 3 | 0 | 38959.5166 | 2 | 0 |  | 1654 | 1781 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.517 | 3 | 0 | 38959.517 | 3 | 0 |  | 1696 | 1823 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76046 | 76046 | 76045.9982
38959.5175 | 3 | 0 | 38959.5175 | 3 | 0 |  | 1738 | 1865 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76046 | 76046 | 76045.9982
38959.518 | 3 | 0 | 38959.518 | 2 | 0 |  | 1780 | 1907 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5185 | 3 | 0 | 38959.5185 | 3 | 0 |  | 1822 | 1949 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76046 | 76046 | 76045.9982
38959.519 | 3 | 0 | 38959.519 | 2 | 0 |  | 1864 | 1991 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5195 | 3 | 0 | 38959.5195 | 2 | 0 |  | 1906 | 2033 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5199 | 3 | 0 | 38959.52 | 2 | 0 |  | 1948 | 2075 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5204 | 2 | 0 | 38959.5205 | 2 | 0 |  | 1990 | 2117 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5209 | 3 | 0 | 38959.5209 | 2 | 0 |  | 2032 | 2159 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5214 | 3 | 0 | 38959.5214 | 2 | 0 |  | 2074 | 2201 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5219 | 3 | 0 | 38959.5219 | 2 | 0 |  | 2116 | 2243 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5224 | 2 | 0 | 38959.5224 | 2 | 0 |  | 2157.5 | 2284.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5229 | 2 | 0 | 38959.5229 | 2 | 0 |  | 2200 | 2327 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5233 | 2 | 0 | 38959.5234 | 2 | 0 |  | 2241.5 | 2368.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5238 | 3 | 0 | 38959.5239 | 2 | 0 |  | 2284 | 2411 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5243 | 2 | 0 | 38959.5243 | 2 | 0 |  | 2325.5 | 2452.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5248 | 2 | 0 | 38959.5248 | 2 | 0 |  | 2368 | 2495 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5253 | 3 | 0 | 38959.5253 | 2 | 0 |  | 2409.5 | 2536.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5258 | 2 | 0 | 38959.5258 | 2 | 0 |  | 2451.5 | 2578.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5263 | 2 | 0 | 38959.5263 | 2 | 0 |  | 2493.5 | 2620.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 114119 | 114119 | 114118.9988
38959.5267 | 3 | 0 | 38959.5268 | 2 | 0 |  | 2535.5 | 2662.5 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 76046 | 114119 | 76045.9982
38959.5272 | 3 | 0 | 38959.5272 | 3 | 0 |  | 2577.5 | 2704.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 76046 | 76046 | 76045.9982
38959.5277 | 5 | 0 | 38959.5277 | 5 | 0 |  | 2620 | 2747 | 0.30525 | 0 | 0.30525 | 0 | 0.0030525 | 0 | 0.0030525 | 0 | 0.0030525 | 0.0030525 | 45587.6 | 45587.6 | 45587.5969
38959.5282 | 11 | 0 | 38959.5282 | 13 | 0 |  | 2662 | 2789 | 0.67155 | 0 | 0.79365 | 0 | 0.0067155 | 0 | 0.0079365 | 0 | 0.0067155 | 0.0079365 | 20667.0909 | 17472.1538 | 20667.0842
38959.5287 | 28 | 0 | 38959.5287 | 24 | 0 |  | 2703.5 | 2830.5 | 1.7094 | 0 | 1.4652 | 0 | 0.017094 | 0 | 0.014652 | 0 | 0.017094 | 0.014652 | 8058.5 | 9418.25 | 8058.4829
38959.5292 | 51 | 0 | 38959.5292 | 45 | 0 |  | 2745.5 | 2872.5 | 3.1136 | 0 | 2.7473 | 0 | 0.031136 | 0 | 0.027473 | 0 | 0.031136 | 0.027473 | 4379.1765 | 4976.4 | 4379.1453
38959.5297 | 82 | 0 | 38959.5297 | 93 | 0 |  | 2787.5 | 2914.5 | 5.0061 | 0 | 5.6777 | 0 | 0.050061 | 0 | 0.056777 | 0 | 0.050061 | 0.056777 | 2685.8293 | 2356.3226 | 2685.7792
38959.5302 | 113 | 0 | 38959.5302 | 124 | 0 |  | 2829.5 | 2956.5 | 6.8987 | 0 | 7.5702 | 0 | 0.068987 | 0 | 0.075702 | 0 | 0.068987 | 0.075702 | 1921.5752 | 1742.2419 | 1921.5062
38959.5306 | 170 | 0 | 38959.5307 | 148 | 0 |  | 2872 | 2999 | 10.3785 | 0 | 9.0354 | 0 | 0.10379 | 0 | 0.090354 | 0 | 0.10379 | 0.090354 | 1243.7529 | 1443.5 | 1243.6492
38959.5311 | 212 | 0 | 38959.5311 | 231 | 0 |  | 2913.5 | 3040.5 | 12.9426 | 0 | 14.1026 | 0 | 0.12943 | 0 | 0.14103 | 0 | 0.12943 | 0.14103 | 977.5377 | 888.9091 | 977.4083
38959.5316 | 1750 | 2 | 38959.5316 | 2237 | 0 |  | 2955.5 | 3082.5 | 106.8376 | 0.1221 | 136.569 | 0 | 1.0684 | 0.001221 | 1.3657 | 0 | 1.0672 | 1.3657 | 32.3167 | 2.118 | 552.1009
38959.5321 | 2264 | 2 | 38959.5321 | 2106 | 0 |  | 2997.5 | 3124.5 | 138.2173 | 0.1221 | 128.5714 | 0 | 1.3822 | 0.001221 | 1.2857 | 0 | 1.381 | 1.2857 | 0.91048 | 8.4701 | 71.7618
38959.5326 | 1903 | 2 | 38959.5326 | 1877 | 0 |  | 3039.5 | 3166.5 | 116.1783 | 0.1221 | 114.591 | 0 | 1.1618 | 0.001221 | 1.1459 | 0 | 1.1606 | 1.1459 | 20.1598 | 21.7038 | 3382.7959
38959.5331 | 2268 | 2 | 38959.5331 | 1996 | 0 |  | 3081.5 | 3208.5 | 138.4615 | 0.1221 | 121.8559 | 0 | 1.3846 | 0.001221 | 1.2186 | 0 | 1.3834 | 1.2186 | 0.7273 | 14.4479 | 90.7665
38959.5336 | 2055 | 3 | 38959.5336 | 2194 | 0 |  | 3123.5 | 3250.5 | 125.4579 | 0.18315 | 133.9438 | 0 | 1.2546 | 0.0018315 | 1.3394 | 0 | 1.2527 | 1.3394 | 11.5897 | 4.1194 | 298.5526
38959.534 | 1955 | 3 | 38959.5341 | 2008 | 0 |  | 3165.5 | 3292.5 | 119.3529 | 0.18315 | 122.5885 | 0 | 1.1935 | 0.0018315 | 1.2259 | 0 | 1.1917 | 1.2259 | 17.0645 | 13.7639 | 1316.2566
38959.5345 | 2219 | 3 | 38959.5345 | 1890 | 0 |  | 3207.5 | 3334.5 | 135.4701 | 0.18315 | 115.3846 | 0 | 1.3547 | 0.0018315 | 1.1538 | 0 | 1.3529 | 1.1538 | 2.9696 | 20.8667 | 358.9803
38959.535 | 1886 | 4 | 38959.535 | 1810 | 0 |  | 3249.5 | 3376.5 | 115.1404 | 0.2442 | 110.5006 | 0 | 1.1514 | 0.002442 | 1.105 | 0 | 1.149 | 1.105 | 21.341 | 26.2088 | 2047.4482

## A2-B3
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.1221 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-11 | N11 | N12 | Time-12 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38959.4961 | 1 | 0 | 38959.4961 | 1 | 0 |  | -112.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.4966 | 1 | 0 | 38959.4966 | 1 | 0 |  | -70.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.4971 | 1 | 0 | 38959.4971 | 1 | 0 |  | -28.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.4976 | 1 | 0 | 38959.4976 | 1 | 0 |  | 13.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.498 | 1 | 0 | 38959.4981 | 1 | 0 |  | 55.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.4985 | 1 | 0 | 38959.4985 | 1 | 0 |  | 97.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.499 | 1 | 0 | 38959.499 | 1 | 0 |  | 139.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.4995 | 1 | 0 | 38959.4995 | 1 | 0 |  | 181.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5 | 1 | 0 | 38959.5 | 1 | 0 |  | 223.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5005 | 1 | 0 | 38959.5005 | 1 | 0 |  | 265.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.501 | 1 | 0 | 38959.501 | 1 | 0 |  | 307.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5014 | 1 | 0 | 38959.5015 | 1 | 0 |  | 349.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5019 | 1 | 0 | 38959.5019 | 1 | 0 |  | 391.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5024 | 1 | 0 | 38959.5024 | 1 | 0 |  | 433.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5029 | 1 | 0 | 38959.5029 | 1 | 0 |  | 475.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5034 | 1 | 0 | 38959.5034 | 1 | 0 |  | 517.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5039 | 1 | 0 | 38959.5039 | 1 | 0 |  | 559.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5044 | 1 | 0 | 38959.5044 | 1 | 0 |  | 601.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5048 | 1 | 0 | 38959.5049 | 1 | 0 |  | 643.5 | 770.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5053 | 1 | 0 | 38959.5053 | 1 | 0 |  | 685.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5058 | 1 | 0 | 38959.5058 | 1 | 0 |  | 727.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5063 | 1 | 0 | 38959.5063 | 1 | 0 |  | 769.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5068 | 1 | 0 | 38959.5068 | 1 | 0 |  | 811.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5073 | 1 | 0 | 38959.5073 | 1 | 0 |  | 853.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5078 | 1 | 0 | 38959.5078 | 1 | 0 |  | 895.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5082 | 1 | 0 | 38959.5083 | 1 | 0 |  | 937 | 1064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5087 | 1 | 0 | 38959.5088 | 1 | 0 |  | 979.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5092 | 1 | 0 | 38959.5092 | 1 | 0 |  | 1021.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5097 | 1 | 0 | 38959.5097 | 1 | 0 |  | 1063.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5102 | 1 | 0 | 38959.5102 | 1 | 0 |  | 1105.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5107 | 1 | 0 | 38959.5107 | 1 | 0 |  | 1147 | 1274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5112 | 1 | 0 | 38959.5112 | 1 | 0 |  | 1189 | 1316 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5116 | 1 | 0 | 38959.5117 | 1 | 0 |  | 1231 | 1358 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5121 | 1 | 0 | 38959.5122 | 1 | 0 |  | 1273 | 1400 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247438 | 247438 | 247437.9994
38959.5126 | 2 | 0 | 38959.5126 | 1 | 0 |  | 1315.5 | 1442.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 123669 | 247438 | 123668.9988
38959.5131 | 3 | 0 | 38959.5131 | 2 | 1 |  | 1357 | 1484 | 0.18315 | 0 | 0.1221 | 0.06105 | 0.0018315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 82412.6667 | 247438 | 82412.6648
38959.5136 | 3 | 0 | 38959.5136 | 2 | 0 |  | 1399 | 1526 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82412.6667 | 123669 | 82412.6648
38959.5141 | 3 | 0 | 38959.5141 | 2 | 0 |  | 1441 | 1568 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82412.6667 | 123669 | 82412.6648
38959.5146 | 3 | 0 | 38959.5146 | 3 | 0 |  | 1483 | 1610 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82412.6667 | 82412.6667 | 82412.6648
38959.515 | 3 | 0 | 38959.5151 | 2 | 0 |  | 1525 | 1652 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82412.6667 | 123669 | 82412.6648
38959.5155 | 3 | 0 | 38959.5156 | 2 | 0 |  | 1567 | 1694 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82412.6667 | 123669 | 82412.6648
38959.516 | 3 | 0 | 38959.516 | 3 | 0 |  | 1609 | 1736 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 82412.6667 | 82412.6667 | 82412.6648
38959.5165 | 3 | 0 | 38959.5165 | 965 | 0 |  | 1651 | 1778 | 0.18315 | 0 | 58.9133 | 0 | 0.0018315 | 0 | 0.58913 | 0 | 0.0018315 | 0.58913 | 82412.6667 | 156.5161 | 82412.6648
38959.517 | 3 | 0 | 38959.517 | 2087 | 0 |  | 1693 | 1820 | 0.18315 | 0 | 127.4115 | 0 | 0.0018315 | 0 | 1.2741 | 0 | 0.0018315 | 1.2741 | 82412.6667 | 18.6095 | 82412.6648
38959.5175 | 2 | 0 | 38959.5175 | 1963 | 0 |  | 1735 | 1862 | 0.1221 | 0 | 119.8413 | 0 | 0.001221 | 0 | 1.1984 | 0 | 0.001221 | 1.1984 | 123669 | 26.1019 | 123668.9988
38959.518 | 3 | 0 | 38959.518 | 2237 | 0 |  | 1777 | 1904 | 0.18315 | 0 | 136.569 | 0 | 0.0018315 | 0 | 1.3657 | 0 | 0.0018315 | 1.3657 | 82412.6667 | 10.6562 | 82412.6648
38959.5184 | 2 | 0 | 38959.5185 | 1979 | 0 |  | 1819 | 1946 | 0.1221 | 0 | 120.8181 | 0 | 0.001221 | 0 | 1.2082 | 0 | 0.001221 | 1.2082 | 123669 | 25.0824 | 123668.9988
38959.5189 | 3 | 0 | 38959.519 | 2358 | 0 |  | 1861 | 1988 | 0.18315 | 0 | 143.956 | 0 | 0.0018315 | 0 | 1.4396 | 0 | 0.0018315 | 1.4396 | 82412.6667 | 4.9779 | 82412.6648
38959.5194 | 3 | 0 | 38959.5194 | 2174 | 0 |  | 1903 | 2030 | 0.18315 | 0 | 132.7228 | 0 | 0.0018315 | 0 | 1.3272 | 0 | 0.0018315 | 1.3272 | 82412.6667 | 13.8629 | 82412.6648
38959.5199 | 3 | 0 | 38959.5199 | 2030 | 0 |  | 1945 | 2072 | 0.18315 | 0 | 123.9316 | 0 | 0.0018315 | 0 | 1.2393 | 0 | 0.0018315 | 1.2393 | 82412.6667 | 21.9399 | 82412.6648
38959.5204 | 3 | 0 | 38959.5204 | 2329 | 0 |  | 1987 | 2114 | 0.18315 | 0 | 142.1856 | 0 | 0.0018315 | 0 | 1.4219 | 0 | 0.0018315 | 1.4219 | 82412.6667 | 6.2851 | 82412.6648
38959.5209 | 3 | 0 | 38959.5209 | 2032 | 0 |  | 2029 | 2156 | 0.18315 | 0 | 124.0537 | 0 | 0.0018315 | 0 | 1.2405 | 0 | 0.0018315 | 1.2405 | 82412.6667 | 21.8199 | 82412.6648
38959.5214 | 3 | 0 | 38959.5214 | 2325 | 0 |  | 2071 | 2198 | 0.18315 | 0 | 141.9414 | 0 | 0.0018315 | 0 | 1.4194 | 0 | 0.0018315 | 1.4194 | 82412.6667 | 6.468 | 82412.6648
38959.5219 | 3 | 0 | 38959.5219 | 1992 | 0 |  | 2113 | 2240 | 0.18315 | 0 | 121.6117 | 0 | 0.0018315 | 0 | 1.2161 | 0 | 0.0018315 | 1.2161 | 82412.6667 | 24.2661 | 82412.6648
38959.5223 | 3 | 0 | 38959.5224 | 1896 | 0 |  | 2155 | 2282 | 0.18315 | 0 | 115.7509 | 0 | 0.0018315 | 0 | 1.1575 | 0 | 0.0018315 | 1.1575 | 82412.6667 | 30.558 | 82412.6648
38959.5228 | 3 | 0 | 38959.5228 | 2285 | 0 |  | 2197 | 2324 | 0.18315 | 0 | 139.4994 | 0 | 0.0018315 | 0 | 1.395 | 0 | 0.0018315 | 1.395 | 82412.6667 | 8.3317 | 82412.6648
38959.5233 | 2 | 0 | 38959.5233 | 2311 | 0 |  | 2239 | 2366 | 0.1221 | 0 | 141.0867 | 0 | 0.001221 | 0 | 1.4109 | 0 | 0.001221 | 1.4109 | 123669 | 7.1129 | 123668.9988
38959.5238 | 2 | 0 | 38959.5238 | 1942 | 0 |  | 2281 | 2408 | 0.1221 | 0 | 118.5592 | 0 | 0.001221 | 0 | 1.1856 | 0 | 0.001221 | 1.1856 | 123669 | 27.4655 | 123668.9988
38959.5243 | 2 | 0 | 38959.5243 | 1948 | 0 |  | 2323 | 2450 | 0.1221 | 0 | 118.9255 | 0 | 0.001221 | 0 | 1.1893 | 0 | 0.001221 | 1.1893 | 123669 | 27.0729 | 123668.9988
38959.5248 | 2 | 0 | 38959.5248 | 2180 | 0 |  | 2365 | 2492 | 0.1221 | 0 | 133.0891 | 0 | 0.001221 | 0 | 1.3309 | 0 | 0.001221 | 1.3309 | 123669 | 13.5495 | 123668.9988
38959.5253 | 3 | 0 | 38959.5253 | 2184 | 0 |  | 2407 | 2534 | 0.18315 | 0 | 133.3333 | 0 | 0.0018315 | 0 | 1.3333 | 0 | 0.0018315 | 1.3333 | 82412.6667 | 13.3416 | 82412.6648
38959.5257 | 2 | 0 | 38959.5258 | 2430 | 0 |  | 2449 | 2576 | 0.1221 | 0 | 148.3516 | 0 | 0.001221 | 0 | 1.4835 | 0 | 0.001221 | 1.4835 | 123669 | 1.8675 | 123668.9988
38959.5262 | 3 | 0 | 38959.5263 | 1981 | 0 |  | 2491 | 2618 | 0.18315 | 0 | 120.9402 | 0 | 0.0018315 | 0 | 1.2094 | 0 | 0.0018315 | 1.2094 | 82412.6667 | 24.9561 | 82412.6648
38959.5267 | 3 | 0 | 38959.5267 | 2109 | 0 |  | 2533 | 2660 | 0.18315 | 0 | 128.7546 | 0 | 0.0018315 | 0 | 1.2875 | 0 | 0.0018315 | 1.2875 | 82412.6667 | 17.3722 | 82412.6648
38959.5272 | 3 | 0 | 38959.5272 | 2237 | 0 |  | 2575 | 2702 | 0.18315 | 0 | 136.569 | 0 | 0.0018315 | 0 | 1.3657 | 0 | 0.0018315 | 1.3657 | 82412.6667 | 10.6562 | 82412.6648
38959.5277 | 5 | 0 | 38959.5277 | 1996 | 0 |  | 2617 | 2744 | 0.30525 | 0 | 121.8559 | 0 | 0.0030525 | 0 | 1.2186 | 0 | 0.0030525 | 1.2186 | 49407.6 | 24.017 | 49407.5969
38959.5282 | 11 | 0 | 38959.5282 | 1996 | 0 |  | 2659 | 2786 | 0.67155 | 0 | 121.8559 | 0 | 0.0067155 | 0 | 1.2186 | 0 | 0.0067155 | 1.2186 | 22403.4545 | 24.017 | 22403.4478
38959.5287 | 25 | 0 | 38959.5287 | 2164 | 0 |  | 2701 | 2828 | 1.5263 | 0 | 132.1123 | 0 | 0.015263 | 0 | 1.3211 | 0 | 0.015263 | 1.3211 | 9801.52 | 14.3891 | 9801.5047
38959.5291 | 53 | 0 | 38959.5292 | 2216 | 0 |  | 2743 | 2870 | 3.2357 | 0 | 135.2869 | 0 | 0.032357 | 0 | 1.3529 | 0 | 0.032357 | 1.3529 | 4570.5283 | 11.7049 | 4570.4959
38959.5296 | 77 | 0 | 38959.5297 | 1919 | 0 |  | 2785 | 2912 | 4.7009 | 0 | 117.1551 | 0 | 0.047009 | 0 | 1.1716 | 0 | 0.047009 | 1.1716 | 3114.7792 | 28.9932 | 3114.7322
38959.5301 | 124 | 0 | 38959.5301 | 1919 | 0 |  | 2827 | 2954 | 7.5702 | 0 | 117.1551 | 0 | 0.075702 | 0 | 1.1716 | 0 | 0.075702 | 1.1716 | 1896.2742 | 28.9932 | 1896.1985
38959.5306 | 143 | 0 | 38959.5306 | 1911 | 0 |  | 2869 | 2996 | 8.7302 | 0 | 116.6667 | 0 | 0.087302 | 0 | 1.1667 | 0 | 0.087302 | 1.1667 | 1631.035 | 29.5332 | 1630.9477
38959.5311 | 208 | 0 | 38959.5311 | 2366 | 0 |  | 2911 | 3038 | 12.6984 | 0 | 144.4444 | 0 | 0.12698 | 0 | 1.4444 | 0 | 0.12698 | 1.4444 | 1090.0865 | 4.623 | 1089.9596
38959.5316 | 1803 | 0 | 38959.5316 | 2408 | 0 |  | 2953 | 3080 | 110.0733 | 0 | 147.0085 | 0 | 1.1007 | 0 | 1.4701 | 0 | 1.1007 | 1.4701 | 37.2923 | 2.7982 | 36.1916
38959.5321 | 2216 | 0 | 38959.5321 | 2022 | 0 |  | 2995 | 3122 | 135.2869 | 0 | 123.4432 | 0 | 1.3529 | 0 | 1.2344 | 0 | 1.3529 | 1.2344 | 11.7049 | 22.4224 | 10.352
38959.5325 | 1983 | 0 | 38959.5326 | 2438 | 0 |  | 3037 | 3164 | 121.0623 | 0 | 148.84 | 0 | 1.2106 | 0 | 1.4884 | 0 | 1.2106 | 1.4884 | 24.8301 | 1.5332 | 23.6194
38959.533 | 2301 | 0 | 38959.5331 | 2352 | 0 |  | 3079 | 3206 | 140.4762 | 0 | 143.5897 | 0 | 1.4048 | 0 | 1.4359 | 0 | 1.4048 | 1.4359 | 7.5784 | 5.2457 | 6.1737
38959.5335 | 2005 | 0 | 38959.5335 | 2299 | 0 |  | 3121 | 3248 | 122.4054 | 0 | 140.3541 | 0 | 1.2241 | 0 | 1.4035 | 0 | 1.2241 | 1.4035 | 23.4603 | 7.672 | 22.2363
38959.534 | 1850 | 0 | 38959.534 | 2221 | 0 |  | 3163 | 3290 | 112.9426 | 0 | 135.5922 | 0 | 1.1294 | 0 | 1.3559 | 0 | 1.1294 | 1.3559 | 33.8043 | 11.4534 | 32.6749
38959.5345 | 2039 | 0 | 38959.5345 | 2459 | 0 |  | 3205 | 3332 | 124.4811 | 0 | 150.1221 | 0 | 1.2448 | 0 | 1.5012 | 0 | 1.2448 | 1.5012 | 21.4017 | 0.66612 | 20.1569
38959.535 | 1882 | 0 | 38959.535 | 2290 | 0 |  | 3247 | 3374 | 114.8962 | 0 | 139.8046 | 0 | 1.149 | 0 | 1.398 | 0 | 1.149 | 1.398 | 31.5292 | 8.0952 | 30.3803

## A1-C6
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.5495 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
38959.4961 | 1 | 0 | 38959.4961 | 1 | 0 |  | -115.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.4966 | 1 | 0 | 38959.4966 | 1 | 0 |  | -73.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.497 | 1 | 0 | 38959.497 | 1 | 0 |  | -31.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.4975 | 1 | 0 | 38959.4975 | 1 | 0 |  | 10.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.498 | 1 | 0 | 38959.498 | 1 | 0 |  | 52.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.4985 | 1 | 0 | 38959.4985 | 1 | 0 |  | 94.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.499 | 1 | 0 | 38959.499 | 1 | 0 |  | 136.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.4995 | 1 | 0 | 38959.4995 | 1 | 0 |  | 178.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5 | 1 | 0 | 38959.5 | 1 | 0 |  | 220.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5004 | 1 | 0 | 38959.5005 | 1 | 0 |  | 262.5 | 389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5009 | 1 | 0 | 38959.5009 | 1 | 0 |  | 304.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5014 | 1 | 0 | 38959.5014 | 1 | 0 |  | 346.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5019 | 1 | 0 | 38959.5019 | 1 | 0 |  | 388.5 | 515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5024 | 1 | 0 | 38959.5024 | 1 | 0 |  | 430.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5029 | 1 | 0 | 38959.5029 | 1 | 0 |  | 472.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5034 | 1 | 0 | 38959.5034 | 1 | 0 |  | 514.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5038 | 1 | 0 | 38959.5039 | 1 | 0 |  | 556.5 | 683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5043 | 1 | 0 | 38959.5043 | 1 | 0 |  | 598.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5048 | 1 | 0 | 38959.5048 | 1 | 0 |  | 640.5 | 767.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5053 | 1 | 0 | 38959.5053 | 1 | 0 |  | 682.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5058 | 1 | 0 | 38959.5058 | 1 | 0 |  | 724.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5063 | 1 | 0 | 38959.5063 | 1 | 0 |  | 766.5 | 893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5068 | 1 | 0 | 38959.5068 | 1 | 0 |  | 808.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5072 | 1 | 0 | 38959.5073 | 1 | 0 |  | 850.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5077 | 1 | 0 | 38959.5077 | 1 | 0 |  | 892.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5082 | 1 | 0 | 38959.5082 | 1 | 0 |  | 934.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5087 | 1 | 0 | 38959.5087 | 1 | 0 |  | 976.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5092 | 1 | 0 | 38959.5092 | 1 | 0 |  | 1018.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5097 | 1 | 0 | 38959.5097 | 1 | 0 |  | 1060.5 | 1187.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5102 | 1 | 0 | 38959.5102 | 1 | 0 |  | 1102.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5106 | 1 | 0 | 38959.5107 | 1 | 0 |  | 1144.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5111 | 1 | 0 | 38959.5111 | 1 | 0 |  | 1186.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5116 | 1 | 0 | 38959.5116 | 1 | 0 |  | 1228.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5121 | 1 | 0 |  | 1 | 0 |  | 1270 | 1397 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
38959.5126 | 2 | 0 | 38959.5126 | 1481 | 0 |  | 1312.5 | 1439.5 | 0.1221 | 0 | 90.4151 | 0 | 0.001221 | 0 | 0.90415 | 0 | 0.001221 | 0.90415 | 124019 | 67.6151 | 124018.9988
38959.5131 | 3 | 0 | 38959.5131 | 1947 | 0 |  | 1354.5 | 1481.5 | 0.18315 | 0 | 118.8645 | 0 | 0.0018315 | 0 | 1.1886 | 0 | 0.0018315 | 1.1886 | 82646 | 27.4977 | 82645.9982
38959.5136 | 3 | 0 | 38959.5136 | 1919 | 0 |  | 1396.5 | 1523.5 | 0.18315 | 0 | 117.1551 | 0 | 0.0018315 | 0 | 1.1716 | 0 | 0.0018315 | 1.1716 | 82646 | 29.358 | 82645.9982
38959.5141 | 3 | 0 | 38959.5141 | 1947 | 0 |  | 1438.5 | 1565.5 | 0.18315 | 0 | 118.8645 | 0 | 0.0018315 | 0 | 1.1886 | 0 | 0.0018315 | 1.1886 | 82646 | 27.4977 | 82645.9982
38959.5145 | 3 | 0 | 38959.5145 | 2280 | 0 |  | 1480.5 | 1607.5 | 0.18315 | 0 | 139.1941 | 0 | 0.0018315 | 0 | 1.3919 | 0 | 0.0018315 | 1.3919 | 82646 | 8.8763 | 82645.9982
38959.515 | 3 | 0 | 38959.515 | 1949 | 0 |  | 1522.5 | 1649.5 | 0.18315 | 0 | 118.9866 | 0 | 0.0018315 | 0 | 1.1899 | 0 | 0.0018315 | 1.1899 | 82646 | 27.3669 | 82645.9982
38959.5155 | 3 | 0 | 38959.5155 | 2384 | 0 |  | 1564.5 | 1691.5 | 0.18315 | 0 | 145.5433 | 0 | 0.0018315 | 0 | 1.4554 | 0 | 0.0018315 | 1.4554 | 82646 | 4.1267 | 82645.9982
38959.516 | 3 | 0 | 38959.516 | 2063 | 0 |  | 1606.5 | 1733.5 | 0.18315 | 0 | 125.9463 | 0 | 0.0018315 | 0 | 1.2595 | 0 | 0.0018315 | 1.2595 | 82646 | 20.3286 | 82645.9982
38959.5165 | 3 | 0 | 38959.5165 | 1985 | 0 |  | 1648.5 | 1775.5 | 0.18315 | 0 | 121.1844 | 0 | 0.0018315 | 0 | 1.2118 | 0 | 0.0018315 | 1.2118 | 82646 | 25.0569 | 82645.9982
38959.517 | 3 | 0 |  | 1955 | 0 |  | 1690 | 1817 | 0.18315 | 0 | 119.3529 | 0 | 0.0018315 | 0 | 1.1935 | 0 | 0.0018315 | 1.1935 | 82646 | 26.976 | 82645.9982
38959.5175 | 3 | 0 | 38959.5175 | 1925 | 0 |  | 1732.5 | 1859.5 | 0.18315 | 0 | 117.5214 | 0 | 0.0018315 | 0 | 1.1752 | 0 | 0.0018315 | 1.1752 | 82646 | 28.9548 | 82645.9982
38959.5179 | 2 | 0 | 38959.518 | 2421 | 0 |  | 1774.5 | 1901.5 | 0.1221 | 0 | 147.8022 | 0 | 0.001221 | 0 | 1.478 | 0 | 0.001221 | 1.478 | 124019 | 2.5353 | 124018.9988
38959.5184 | 3 | 0 | 38959.5184 | 2405 | 0 |  | 1816.5 | 1943.5 | 0.18315 | 0 | 146.8254 | 0 | 0.0018315 | 0 | 1.4683 | 0 | 0.0018315 | 1.4683 | 82646 | 3.2175 | 82645.9982
38959.5189 | 3 | 0 | 38959.5189 | 2091 | 0 |  | 1858.5 | 1985.5 | 0.18315 | 0 | 127.6557 | 0 | 0.0018315 | 0 | 1.2766 | 0 | 0.0018315 | 1.2766 | 82646 | 18.7174 | 82645.9982
38959.5194 | 3 | 0 | 38959.5194 | 2069 | 1 |  | 1900.5 | 2027.5 | 0.18315 | 0 | 126.3126 | 0.06105 | 0.0018315 | 0 | 1.2631 | 0.0006105 | 0.0018315 | 1.2625 | 82646 | 20.0377 | 82645.9982
38959.5199 | 3 | 0 | 38959.5199 | 2385 | 0 |  | 1942.5 | 2069.5 | 0.18315 | 0 | 145.6044 | 0 | 0.0018315 | 0 | 1.456 | 0 | 0.0018315 | 1.456 | 82646 | 4.083 | 82645.9982
38959.5204 | 2 | 0 | 38959.5204 | 2249 | 0 |  | 1984.5 | 2111.5 | 0.1221 | 0 | 137.3016 | 0 | 0.001221 | 0 | 1.373 | 0 | 0.001221 | 1.373 | 124019 | 10.3771 | 124018.9988
38959.5209 | 3 | 0 | 38959.5209 | 2402 | 0 |  | 2026.5 | 2153.5 | 0.18315 | 0 | 146.6422 | 0 | 0.0018315 | 0 | 1.4664 | 0 | 0.0018315 | 1.4664 | 82646 | 3.3464 | 82645.9982
38959.5213 | 2 | 0 | 38959.5214 | 2344 | 0 |  | 2068.5 | 2195.5 | 0.1221 | 0 | 143.1013 | 0 | 0.001221 | 0 | 1.431 | 0 | 0.001221 | 1.431 | 124019 | 5.9036 | 124018.9988
38959.5218 | 3 | 0 | 38959.5218 | 2244 | 0 |  | 2110.5 | 2237.5 | 0.18315 | 0 | 136.9963 | 0 | 0.0018315 | 0 | 1.37 | 0 | 0.0018315 | 1.37 | 82646 | 10.623 | 82645.9982
38959.5223 | 2 | 0 | 38959.5223 | 2204 | 0 |  | 2152.5 | 2279.5 | 0.1221 | 0 | 134.5543 | 0 | 0.001221 | 0 | 1.3455 | 0 | 0.001221 | 1.3455 | 124019 | 12.6307 | 124018.9988
38959.5228 | 2 | 1 | 38959.5228 | 2380 | 0 |  | 2194 | 2321 | 0.1221 | 0.06105 | 145.2991 | 0 | 0.001221 | 0.0006105 | 1.453 | 0 | 0.0006105 | 1.453 | 11149.4149 | 4.7066 | 11144.9199
38959.5233 | 2 | 0 | 38959.5233 | 2030 | 0 |  | 2236.5 | 2363.5 | 0.1221 | 0 | 123.9316 | 0 | 0.001221 | 0 | 1.2393 | 0 | 0.001221 | 1.2393 | 124019 | 22.2847 | 124018.9988
38959.5238 | 2 | 0 | 38959.5238 | 2337 | 0 |  | 2278.5 | 2405.5 | 0.1221 | 0 | 142.674 | 0 | 0.001221 | 0 | 1.4267 | 0 | 0.001221 | 1.4267 | 124019 | 6.2208 | 124018.9988
38959.5242 | 2 | 0 | 38959.5243 | 1989 | 0 |  | 2320 | 2447 | 0.1221 | 0 | 121.4286 | 0 | 0.001221 | 0 | 1.2143 | 0 | 0.001221 | 1.2143 | 124019 | 24.8054 | 124018.9988
38959.5247 | 3 | 0 | 38959.5248 | 2453 | 0 |  | 2362.5 | 2489.5 | 0.18315 | 0 | 149.7558 | 0 | 0.0018315 | 0 | 1.4976 | 0 | 0.0018315 | 1.4976 | 82646 | 1.1977 | 82645.9982
38959.5252 | 3 | 0 | 38959.5252 | 2339 | 0 |  | 2404 | 2531 | 0.18315 | 0 | 142.7961 | 0 | 0.0018315 | 0 | 1.428 | 0 | 0.0018315 | 1.428 | 82646 | 6.13 | 82645.9982
38959.5257 | 2 | 0 | 38959.5257 | 2445 | 0 |  | 2446 | 2573 | 0.1221 | 0 | 149.2674 | 0 | 0.001221 | 0 | 1.4927 | 0 | 0.001221 | 1.4927 | 124019 | 1.5288 | 124018.9988
38959.5262 | 3 | 0 | 38959.5262 | 2394 | 0 |  | 2488 | 2615 | 0.18315 | 0 | 146.1538 | 0 | 0.0018315 | 0 | 1.4615 | 0 | 0.0018315 | 1.4615 | 82646 | 3.6917 | 82645.9982
38959.5267 | 2 | 0 | 38959.5267 | 2256 | 0 |  | 2530 | 2657 | 0.1221 | 0 | 137.7289 | 0 | 0.001221 | 0 | 1.3773 | 0 | 0.001221 | 1.3773 | 124019 | 10.0346 | 124018.9988
38959.5272 | 3 | 1 | 38959.5272 | 2372 | 0 |  | 2572 | 2699 | 0.18315 | 0.06105 | 144.8107 | 0 | 0.0018315 | 0.0006105 | 1.4481 | 0 | 0.001221 | 1.4481 | 12721.6844 | 5.7177 | 13404.3288
38959.5277 | 5 | 0 | 38959.5277 | 2455 | 0 |  | 2614 | 2741 | 0.30525 | 0 | 149.8779 | 0 | 0.0030525 | 0 | 1.4988 | 0 | 0.0030525 | 1.4988 | 49547.6 | 1.1153 | 49547.5969
38959.5281 | 9 | 0 | 38959.5282 | 2350 | 0 |  | 2656.5 | 2783.5 | 0.54945 | 0 | 143.4676 | 0 | 0.0054945 | 0 | 1.4347 | 0 | 0.0054945 | 1.4347 | 27482 | 5.6332 | 27481.9945
38959.5286 | 25 | 0 | 38959.5286 | 2121 | 0 |  | 2698 | 2825 | 1.5263 | 0 | 129.4872 | 0 | 0.015263 | 0 | 1.2949 | 0 | 0.015263 | 1.2949 | 9829.52 | 17.0382 | 9829.5047
38959.5291 | 47 | 0 | 38959.5291 | 2388 | 0 |  | 2740 | 2867 | 2.8694 | 0 | 145.7875 | 0 | 0.028694 | 0 | 1.4579 | 0 | 0.028694 | 1.4579 | 5181.6596 | 3.9523 | 5181.6309
38959.5296 | 79 | 0 | 38959.5296 | 2466 | 0 |  | 2782 | 2909 | 4.823 | 0 | 150.5495 | 0 | 0.04823 | 0 | 1.5055 | 0 | 0.04823 | 1.5055 | 3042.2532 | 0.66423 | 3042.2049
38959.5301 | 104 | 0 | 38959.5301 | 2275 | 0 |  | 2824 | 2951 | 6.3492 | 0 | 138.8889 | 0 | 0.063492 | 0 | 1.3889 | 0 | 0.063492 | 1.3889 | 2286.9038 | 9.1156 | 2286.8404
38959.5306 | 129 | 0 | 38959.5306 | 2254 | 0 |  | 2866 | 2993 | 7.8755 | 0 | 137.6068 | 0 | 0.078755 | 0 | 1.3761 | 0 | 0.078755 | 1.3761 | 1824.3256 | 10.1322 | 1824.2468
38959.5311 | 186 | 0 | 38959.5311 | 2242 | 0 |  | 2908 | 3035 | 11.3553 | 0 | 136.8742 | 0 | 0.11355 | 0 | 1.3687 | 0 | 0.11355 | 1.3687 | 1234.6129 | 10.7217 | 1234.4994
38959.5315 | 2176 | 0 | 38959.5316 | 2112 | 0 |  | 2950 | 3077 | 132.8449 | 0 | 128.9377 | 0 | 1.3284 | 0 | 1.2894 | 0 | 1.3284 | 1.2894 | 14.08 | 17.5369 | 12.7515
38959.532 | 1963 | 0 | 38959.532 | 2337 | 0 |  | 2992 | 3119 | 119.8413 | 0 | 142.674 | 0 | 1.1984 | 0 | 1.4267 | 0 | 1.1984 | 1.4267 | 26.4585 | 6.2208 | 25.2601
38959.5325 | 1892 | 0 | 38959.5325 | 2442 | 0 |  | 3034 | 3161 | 115.5067 | 0 | 149.0842 | 0 | 1.1551 | 0 | 1.4908 | 0 | 1.1551 | 1.4908 | 31.204 | 1.6536 | 30.0489
38959.533 | 2289 | 0 | 38959.533 | 2007 | 0 |  | 3076 | 3203 | 139.7436 | 0 | 122.5275 | 0 | 1.3974 | 0 | 1.2253 | 0 | 1.3974 | 1.2253 | 8.4482 | 23.6861 | 7.0508
38959.5335 | 2022 | 0 | 38959.5335 | 1918 | 0 |  | 3118 | 3245 | 123.4432 | 0 | 117.094 | 0 | 1.2344 | 0 | 1.1709 | 0 | 1.2344 | 1.1709 | 22.7685 | 29.4254 | 21.5341
38959.534 | 1855 | 0 | 38959.534 | 2362 | 0 |  | 3160 | 3287 | 113.2479 | 0 | 144.2002 | 0 | 1.1325 | 0 | 1.442 | 0 | 1.1325 | 1.442 | 33.821 | 5.0965 | 32.6885
38959.5345 | 2120 | 0 | 38959.5345 | 1972 | 0 |  | 3202 | 3329 | 129.4261 | 0 | 120.3907 | 0 | 1.2943 | 0 | 1.2039 | 0 | 1.2943 | 1.2039 | 17.0934 | 25.8813 | 15.7991
38959.5349 | 1843 | 0 | 38959.535 | 2399 | 0 |  | 3244 | 3371 | 112.5153 | 0 | 146.4591 | 0 | 1.1252 | 0 | 1.4646 | 0 | 1.1252 | 1.4646 | 34.6923 | 3.4756 | 33.5672

## A1-C5
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.7326 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
38959.496 | 1 | 0 | 38959.496 | 1 | 0 |  | -118.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4965 | 1 | 0 | 38959.4965 | 1 | 0 |  | -76 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.497 | 1 | 0 | 38959.497 | 1 | 0 |  | -34.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4975 | 1 | 0 | 38959.4975 | 1 | 0 |  | 7.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.498 | 1 | 0 | 38959.498 | 1 | 0 |  | 49.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4985 | 1 | 0 | 38959.4985 | 1 | 0 |  | 92 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4989 | 1 | 0 | 38959.499 | 1 | 0 |  | 134 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4994 | 1 | 0 | 38959.4994 | 1 | 0 |  | 175.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.4999 | 1 | 0 | 38959.4999 | 1 | 0 |  | 217.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5004 | 1 | 0 | 38959.5004 | 1 | 0 |  | 259.5 | 386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5009 | 1 | 0 | 38959.5009 | 1 | 0 |  | 301.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5014 | 1 | 0 | 38959.5014 | 1 | 0 |  | 343.5 | 470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5019 | 1 | 0 | 38959.5019 | 1 | 0 |  | 385.5 | 512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5023 | 1 | 0 | 38959.5024 | 1 | 0 |  | 427.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5028 | 1 | 0 | 38959.5028 | 1 | 0 |  | 469.5 | 596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5033 | 1 | 0 | 38959.5033 | 1 | 0 |  | 511.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5038 | 1 | 0 | 38959.5038 | 1 | 0 |  | 553.5 | 680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5043 | 1 | 0 | 38959.5043 | 1 | 0 |  | 595.5 | 722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5048 | 1 | 0 | 38959.5048 | 1 | 0 |  | 637.5 | 764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5053 | 1 | 0 | 38959.5053 | 1 | 0 |  | 679.5 | 806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5058 | 1 | 0 | 38959.5058 | 1 | 0 |  | 721.5 | 848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5062 | 1 | 0 | 38959.5062 | 1 | 0 |  | 763.5 | 890.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5067 | 1 | 0 | 38959.5067 | 1 | 0 |  | 805.5 | 932.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5072 | 1 | 0 | 38959.5072 | 1 | 0 |  | 847.5 | 974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5077 | 1 | 0 | 38959.5077 | 1 | 0 |  | 889.5 | 1016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5082 | 1 | 0 | 38959.5082 | 1 | 0 |  | 931.5 | 1058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5087 | 1 | 0 | 38959.5087 | 1 | 0 |  | 973.5 | 1100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5092 | 1 | 0 | 38959.5092 | 1 | 0 |  | 1015.5 | 1142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5096 | 1 | 0 | 38959.5097 | 1 | 0 |  | 1057.5 | 1184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5101 | 1 | 0 | 38959.5101 | 1 | 0 |  | 1099.5 | 1226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5106 | 1 | 0 | 38959.5106 | 1 | 0 |  | 1141.5 | 1268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5111 | 1 | 0 | 38959.5111 | 1 | 0 |  | 1183.5 | 1310.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5116 | 1 | 0 | 38959.5116 | 1 | 0 |  | 1225.5 | 1352.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5121 | 1 | 0 | 38959.5121 | 1 | 0 |  | 1267.5 | 1394.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248438 | 248438 | 248437.9994
38959.5126 | 1 | 0 | 38959.5126 | 1850 | 0 |  | 1309.5 | 1436.5 | 0.06105 | 0 | 112.9426 | 0 | 0.0006105 | 0 | 1.1294 | 0 | 0.0006105 | 1.1294 | 248438 | 34.3449 | 248437.9994
38959.513 | 2 | 0 | 38959.5131 | 1950 | 0 |  | 1351.5 | 1478.5 | 0.1221 | 0 | 119.0476 | 0 | 0.001221 | 0 | 1.1905 | 0 | 0.001221 | 1.1905 | 124169 | 27.4554 | 124168.9988
38959.5135 | 2 | 0 | 38959.5135 | 2459 | 0 |  | 1393.5 | 1520.5 | 0.1221 | 0 | 150.1221 | 0 | 0.001221 | 0 | 1.5012 | 0 | 0.001221 | 1.5012 | 124169 | 1.0728 | 124168.9988
38959.514 | 2 | 0 | 38959.514 | 1601 | 0 |  | 1435.5 | 1562.5 | 0.1221 | 0 | 97.7411 | 0 | 0.001221 | 0 | 0.97741 | 0 | 0.001221 | 0.97741 | 124169 | 55.2392 | 124168.9988
38959.5145 | 3 | 0 | 38959.5145 | 2338 | 0 |  | 1477.5 | 1604.5 | 0.18315 | 0 | 142.735 | 0 | 0.0018315 | 0 | 1.4274 | 0 | 0.0018315 | 1.4274 | 82746 | 6.3037 | 82745.9982
38959.515 | 2 | 0 | 38959.515 | 2310 | 0 |  | 1519.5 | 1646.5 | 0.1221 | 0 | 141.0256 | 0 | 0.001221 | 0 | 1.4103 | 0 | 0.001221 | 1.4103 | 124169 | 7.5922 | 124168.9988
38959.5155 | 2 | 0 | 38959.5155 | 2423 | 0 |  | 1561.5 | 1688.5 | 0.1221 | 0 | 147.9243 | 0 | 0.001221 | 0 | 1.4792 | 0 | 0.001221 | 1.4792 | 124169 | 2.5745 | 124168.9988
38959.516 | 2 | 0 | 38959.516 | 2399 | 0 |  | 1603.5 | 1730.5 | 0.1221 | 0 | 146.4591 | 0 | 0.001221 | 0 | 1.4646 | 0 | 0.001221 | 1.4646 | 124169 | 3.6007 | 124168.9988
38959.5164 | 2 | 0 | 38959.5165 | 2469 | 0 |  | 1645.5 | 1772.5 | 0.1221 | 0 | 150.7326 | 0 | 0.001221 | 0 | 1.5073 | 0 | 0.001221 | 1.5073 | 124169 | 0.66343 | 124168.9988
38959.5169 | 3 | 0 | 38959.5169 | 2460 | 0 |  | 1687.5 | 1814.5 | 0.18315 | 0 | 150.1832 | 0 | 0.0018315 | 0 | 1.5018 | 0 | 0.0018315 | 1.5018 | 82746 | 1.0317 | 82745.9982
38959.5174 | 3 | 0 | 38959.5174 | 2218 | 0 |  | 1729.5 | 1856.5 | 0.18315 | 0 | 135.409 | 0 | 0.0018315 | 0 | 1.3541 | 0 | 0.0018315 | 1.3541 | 82746 | 12.055 | 82745.9982
38959.5179 | 3 | 0 | 38959.5179 | 2092 | 0 |  | 1771.5 | 1898.5 | 0.18315 | 0 | 127.7167 | 0 | 0.0018315 | 0 | 1.2772 | 0 | 0.0018315 | 1.2772 | 82746 | 18.804 | 82745.9982
38959.5184 | 2 | 0 | 38959.5184 | 2070 | 0 |  | 1813.5 | 1940.5 | 0.1221 | 0 | 126.3736 | 0 | 0.001221 | 0 | 1.2637 | 0 | 0.001221 | 1.2637 | 124169 | 20.0667 | 124168.9988
38959.5189 | 3 | 0 | 38959.5189 | 2403 | 0 |  | 1855.5 | 1982.5 | 0.18315 | 0 | 146.7033 | 0 | 0.0018315 | 0 | 1.467 | 0 | 0.0018315 | 1.467 | 82746 | 3.4282 | 82745.9982
38959.5194 | 3 | 1 | 38959.5194 | 2061 | 0 |  | 1897.5 | 2024.5 | 0.18315 | 0.06105 | 125.8242 | 0 | 0.0018315 | 0.0006105 | 1.2582 | 0 | 0.001221 | 1.2582 | 86902.9585 | 116.7547 | 133659.2852
38959.5198 | 3 | 0 | 38959.5199 | 1980 | 0 |  | 1939.5 | 2066.5 | 0.18315 | 0 | 120.8791 | 0 | 0.0018315 | 0 | 1.2088 | 0 | 0.0018315 | 1.2088 | 82746 | 25.5242 | 82745.9982
38959.5203 | 2 | 0 | 38959.5203 | 2356 | 0 |  | 1981.5 | 2108.5 | 0.1221 | 0 | 143.8339 | 0 | 0.001221 | 0 | 1.4383 | 0 | 0.001221 | 1.4383 | 124169 | 5.4915 | 124168.9988
38959.5208 | 3 | 0 | 38959.5208 | 2403 | 0 |  | 2023.5 | 2150.5 | 0.18315 | 0 | 146.7033 | 0 | 0.0018315 | 0 | 1.467 | 0 | 0.0018315 | 1.467 | 82746 | 3.4282 | 82745.9982
38959.5213 | 3 | 0 | 38959.5213 | 2182 | 0 |  | 2065.5 | 2192.5 | 0.18315 | 0 | 133.2112 | 0 | 0.0018315 | 0 | 1.3321 | 0 | 0.0018315 | 1.3321 | 82746 | 13.9038 | 82745.9982
38959.5218 | 2 | 0 | 38959.5218 | 2041 | 0 |  | 2107.5 | 2234.5 | 0.1221 | 0 | 124.6032 | 0 | 0.001221 | 0 | 1.246 | 0 | 0.001221 | 1.246 | 124169 | 21.7727 | 124168.9988
38959.5223 | 3 | 0 | 38959.5223 | 2232 | 0 |  | 2149.5 | 2276.5 | 0.18315 | 0 | 136.2637 | 0 | 0.0018315 | 0 | 1.3626 | 0 | 0.0018315 | 1.3626 | 82746 | 11.3522 | 82745.9982
38959.5228 | 3 | 0 | 38959.5228 | 2257 | 0 |  | 2191.5 | 2318.5 | 0.18315 | 0 | 137.79 | 0 | 0.0018315 | 0 | 1.3779 | 0 | 0.0018315 | 1.3779 | 82746 | 10.1187 | 82745.9982
38959.5233 | 2 | 0 | 38959.5233 | 1984 | 0 |  | 2233.5 | 2360.5 | 0.1221 | 0 | 121.1233 | 0 | 0.001221 | 0 | 1.2112 | 0 | 0.001221 | 1.2112 | 124169 | 25.2712 | 124168.9988
38959.5237 | 3 | 0 | 38959.5238 | 1996 | 0 |  | 2275.5 | 2402.5 | 0.18315 | 0 | 121.8559 | 0 | 0.0018315 | 0 | 1.2186 | 0 | 0.0018315 | 1.2186 | 82746 | 24.518 | 82745.9982
38959.5242 | 2 | 0 | 38959.5242 | 1926 | 0 |  | 2317.5 | 2444.5 | 0.1221 | 0 | 117.5824 | 0 | 0.001221 | 0 | 1.1758 | 0 | 0.001221 | 1.1758 | 124169 | 29.0436 | 124168.9988
38959.5247 | 2 | 0 | 38959.5247 | 2203 | 0 |  | 2359.5 | 2486.5 | 0.1221 | 0 | 134.4933 | 0 | 0.001221 | 0 | 1.3449 | 0 | 0.001221 | 1.3449 | 124169 | 12.818 | 124168.9988
38959.5252 | 3 | 0 | 38959.5252 | 2156 | 0 |  | 2401.5 | 2528.5 | 0.18315 | 0 | 131.6239 | 0 | 0.0018315 | 0 | 1.3162 | 0 | 0.0018315 | 1.3162 | 82746 | 15.2774 | 82745.9982
38959.5257 | 3 | 0 | 38959.5257 | 2003 | 0 |  | 2443.5 | 2570.5 | 0.18315 | 0 | 122.2833 | 0 | 0.0018315 | 0 | 1.2228 | 0 | 0.0018315 | 1.2228 | 82746 | 24.0829 | 82745.9982
38959.5262 | 3 | 0 | 38959.5262 | 1972 | 0 |  | 2485.5 | 2612.5 | 0.18315 | 0 | 120.3907 | 0 | 0.0018315 | 0 | 1.2039 | 0 | 0.0018315 | 1.2039 | 82746 | 26.0335 | 82745.9982
38959.5267 | 3 | 0 | 38959.5267 | 2453 | 0 |  | 2527.5 | 2654.5 | 0.18315 | 0 | 149.7558 | 0 | 0.0018315 | 0 | 1.4976 | 0 | 0.0018315 | 1.4976 | 82746 | 1.32 | 82745.9982
38959.5271 | 3 | 0 | 38959.5272 | 2143 | 0 |  | 2569.5 | 2696.5 | 0.18315 | 0 | 130.8303 | 0 | 0.0018315 | 0 | 1.3083 | 0 | 0.0018315 | 1.3083 | 82746 | 15.9767 | 82745.9982
38959.5276 | 4 | 0 | 38959.5276 | 1999 | 0 |  | 2611.5 | 2738.5 | 0.2442 | 0 | 122.0391 | 0 | 0.002442 | 0 | 1.2204 | 0 | 0.002442 | 1.2204 | 62034.5 | 24.3312 | 62034.4976
38959.5281 | 9 | 0 | 38959.5281 | 1935 | 0 |  | 2653.5 | 2780.5 | 0.54945 | 0 | 118.1319 | 0 | 0.0054945 | 0 | 1.1813 | 0 | 0.0054945 | 1.1813 | 27515.3333 | 28.4434 | 27515.3278
38959.5286 | 23 | 0 | 38959.5286 | 1928 | 0 |  | 2695.5 | 2822.5 | 1.4042 | 0 | 117.7045 | 0 | 0.014042 | 0 | 1.177 | 0 | 0.014042 | 1.177 | 10706 | 28.9098 | 10705.986
38959.5291 | 41 | 0 | 38959.5291 | 2135 | 0 |  | 2737.5 | 2864.5 | 2.5031 | 0 | 130.3419 | 0 | 0.025031 | 0 | 1.3034 | 0 | 0.025031 | 1.3034 | 5961.9024 | 16.4112 | 5961.8774
38959.5296 | 73 | 0 | 38959.5296 | 2248 | 0 |  | 2779.5 | 2906.5 | 4.4567 | 0 | 137.2405 | 0 | 0.044567 | 0 | 1.3724 | 0 | 0.044567 | 1.3724 | 3304.6301 | 10.5596 | 3304.5856
38959.5301 | 115 | 0 | 38959.5301 | 2194 | 0 |  | 2821.5 | 2948.5 | 7.0208 | 0 | 133.9438 | 0 | 0.070208 | 0 | 1.3394 | 0 | 0.070208 | 1.3394 | 2061.2 | 13.2808 | 2061.1298
38959.5305 | 125 | 0 | 38959.5306 | 1971 | 0 |  | 2863.5 | 2990.5 | 7.6313 | 0 | 120.3297 | 0 | 0.076313 | 0 | 1.2033 | 0 | 0.076313 | 1.2033 | 1888.304 | 26.0974 | 1888.2277
38959.531 | 184 | 0 | 38959.531 | 1992 | 0 |  | 2905.5 | 3032.5 | 11.2332 | 0 | 121.6117 | 0 | 0.11233 | 0 | 1.2161 | 0 | 0.11233 | 1.2161 | 1250.75 | 24.7681 | 1250.6377
38959.5315 | 2077 | 0 | 38959.5315 | 2435 | 0 |  | 2947.5 | 3074.5 | 126.801 | 0 | 148.6569 | 0 | 1.268 | 0 | 1.4866 | 0 | 1.268 | 1.4866 | 19.662 | 2.069 | 18.394
38959.532 | 1941 | 0 | 38959.532 | 2294 | 0 |  | 2989.5 | 3116.5 | 118.4982 | 0 | 140.0488 | 0 | 1.185 | 0 | 1.4005 | 0 | 1.185 | 1.4005 | 28.0464 | 8.3426 | 26.8614
38959.5325 | 2026 | 0 | 38959.5325 | 2415 | 0 |  | 3031.5 | 3158.5 | 123.6874 | 0 | 147.4359 | 0 | 1.2369 | 0 | 1.4744 | 0 | 1.2369 | 1.4744 | 22.6742 | 2.9143 | 21.4374
38959.533 | 2293 | 0 | 38959.533 | 1959 | 0 |  | 3073.5 | 3200.5 | 139.9878 | 0 | 119.5971 | 0 | 1.3999 | 0 | 1.196 | 0 | 1.3999 | 1.196 | 8.3899 | 26.8698 | 6.99
38959.5335 | 2183 | 0 | 38959.5335 | 2258 | 0 |  | 3115.5 | 3242.5 | 133.2723 | 0 | 137.851 | 0 | 1.3327 | 0 | 1.3785 | 0 | 1.3327 | 1.3785 | 13.8516 | 10.07 | 12.5189
38959.5339 | 1851 | 0 | 38959.534 | 1927 | 0 |  | 3157.5 | 3284.5 | 113.0037 | 0 | 117.6435 | 0 | 1.13 | 0 | 1.1764 | 0 | 1.13 | 1.1764 | 34.2723 | 28.9766 | 33.1422
38959.5344 | 2008 | 0 | 38959.5344 | 1997 | 0 |  | 3199.5 | 3326.5 | 122.5885 | 0 | 121.917 | 0 | 1.2259 | 0 | 1.2192 | 0 | 1.2259 | 1.2192 | 23.7739 | 24.4557 | 22.548
38959.5349 | 1997 | 0 | 38959.5349 | 2376 | 0 |  | 3241.5 | 3368.5 | 121.917 | 0 | 145.0549 | 0 | 1.2192 | 0 | 1.4505 | 0 | 1.2192 | 1.4505 | 24.4557 | 4.6035 | 23.2365

## A1-B4
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 149.2906 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
38959.496 | 1 | 0 | 38959.496 | 1 | 0 |  | -121 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4965 | 1 | 0 | 38959.4965 | 1 | 0 |  | -79 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.497 | 1 | 0 | 38959.497 | 1 | 0 |  | -37 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4975 | 1 | 0 | 38959.4975 | 1 | 0 |  | 5 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4979 | 1 | 0 | 38959.498 | 1 | 0 |  | 47 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4984 | 1 | 0 | 38959.4984 | 1 | 0 |  | 89 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4989 | 1 | 0 | 38959.4989 | 1 | 0 |  | 131 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4994 | 1 | 0 | 38959.4994 | 1 | 0 |  | 173 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.4999 | 1 | 0 | 38959.4999 | 1 | 0 |  | 215 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5004 | 1 | 0 | 38959.5004 | 1 | 0 |  | 257 | 384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5009 | 1 | 0 | 38959.5009 | 1 | 0 |  | 299 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5013 | 1 | 0 | 38959.5014 | 1 | 0 |  | 341 | 468 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5018 | 1 | 0 | 38959.5019 | 1 | 0 |  | 383 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5023 | 1 | 0 | 38959.5023 | 1 | 0 |  | 425 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5028 | 1 | 0 | 38959.5028 | 1 | 0 |  | 467 | 594 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5033 | 1 | 0 | 38959.5033 | 1 | 0 |  | 509 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5038 | 1 | 0 | 38959.5038 | 1 | 0 |  | 551 | 678 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5043 | 1 | 0 | 38959.5043 | 1 | 0 |  | 593 | 720 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5047 | 1 | 0 | 38959.5048 | 1 | 0 |  | 635 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5052 | 1 | 0 | 38959.5053 | 1 | 0 |  | 677 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5057 | 1 | 0 | 38959.5057 | 1 | 0 |  | 719 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5062 | 1 | 0 | 38959.5062 | 1 | 0 |  | 761 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5067 | 1 | 0 | 38959.5067 | 1 | 0 |  | 803 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5072 | 1 | 0 | 38959.5072 | 1 | 0 |  | 845 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5077 | 1 | 0 | 38959.5077 | 1 | 0 |  | 887 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5081 | 1 | 0 | 38959.5082 | 1 | 0 |  | 928.5 | 1055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5086 | 2 | 0 | 38959.5086 | 1 | 0 |  | 970.5 | 1097.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 122169 | 244438 | 122168.9988
38959.5091 | 1 | 0 | 38959.5091 | 1 | 0 |  | 1012.5 | 1139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5096 | 1 | 0 | 38959.5096 | 1 | 0 |  | 1055 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5101 | 1 | 0 | 38959.5101 | 1 | 0 |  | 1096.5 | 1223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5106 | 1 | 0 | 38959.5106 | 1 | 0 |  | 1138.5 | 1265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5111 | 1 | 0 | 38959.5111 | 1 | 0 |  | 1181 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5116 | 1 | 0 | 38959.5116 | 1 | 0 |  | 1222.5 | 1349.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.512 | 1 | 0 | 38959.512 | 1 | 0 |  | 1264.5 | 1391.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.5125 | 1 | 0 | 38959.5125 | 1 | 0 |  | 1307 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
38959.513 | 2 | 0 | 38959.513 | 2 | 0 |  | 1349 | 1476 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.5135 | 2 | 0 | 38959.5135 | 2 | 0 |  | 1390.5 | 1517.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.514 | 2 | 0 | 38959.514 | 2 | 0 |  | 1432.5 | 1559.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.5145 | 2 | 0 | 38959.5145 | 3 | 0 |  | 1475 | 1602 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 122169 | 81412.6667 | 122168.9988
38959.515 | 2 | 0 | 38959.515 | 2 | 0 |  | 1516.5 | 1643.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.5154 | 2 | 0 | 38959.5155 | 2 | 0 |  | 1559 | 1686 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.5159 | 2 | 0 | 38959.5159 | 2 | 0 |  | 1600.5 | 1727.5 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 122169 | 122169 | 122168.9988
38959.5164 | 2 | 0 | 38959.5164 | 599 | 0 |  | 1642.5 | 1769.5 | 0.1221 | 0 | 36.569 | 0 | 0.001221 | 0 | 0.36569 | 0 | 0.001221 | 0.36569 | 122169 | 308.2437 | 122168.9988
38959.5169 | 3 | 0 | 38959.5169 | 1112 | 0 |  | 1684.5 | 1811.5 | 0.18315 | 0 | 67.8877 | 0 | 0.0018315 | 0 | 0.67888 | 0 | 0.0018315 | 0.67888 | 81412.6667 | 119.9083 | 81412.6648
38959.5174 | 3 | 0 | 38959.5174 | 972 | 0 |  | 1726.5 | 1853.5 | 0.18315 | 0 | 59.3407 | 0 | 0.0018315 | 0 | 0.59341 | 0 | 0.0018315 | 0.59341 | 81412.6667 | 151.5823 | 81412.6648
38959.5179 | 3 | 0 | 38959.5179 | 1168 | 0 |  | 1768.5 | 1895.5 | 0.18315 | 0 | 71.3065 | 0 | 0.0018315 | 0 | 0.71306 | 0 | 0.0018315 | 0.71306 | 81412.6667 | 109.3647 | 81412.6648
38959.5184 | 3 | 0 | 38959.5184 | 2153 | 0 |  | 1810.5 | 1937.5 | 0.18315 | 0 | 131.4408 | 0 | 0.0018315 | 0 | 1.3144 | 0 | 0.0018315 | 1.3144 | 81412.6667 | 13.5801 | 81412.6648
38959.5188 | 2 | 1 | 38959.5189 | 1907 | 0 |  | 1852.5 | 1979.5 | 0.1221 | 0.06105 | 116.4225 | 0 | 0.001221 | 0.0006105 | 1.1642 | 0 | 0.0006105 | 1.1642 | 96116.3014 | 64.8463 | 96076.964
38959.5193 | 3 | 1 | 38959.5193 | 2189 | 0 |  | 1894.5 | 2021.5 | 0.18315 | 0.06105 | 133.6386 | 0 | 0.0018315 | 0.0006105 | 1.3364 | 0 | 0.001221 | 1.3364 | 37356.0698 | 22.0356 | 44083.2902
38959.5198 | 3 | 1 | 38959.5198 | 1812 | 0 |  | 1936.5 | 2063.5 | 0.18315 | 0.06105 | 110.6227 | 0 | 0.0018315 | 0.0006105 | 1.1062 | 0 | 0.001221 | 1.1062 | 283719.948 | 87.7841 | 114128.0732
38959.5203 | 3 | 1 | 38959.5203 | 1840 | 0 |  | 1978.5 | 2105.5 | 0.18315 | 0.06105 | 112.3321 | 0 | 0.0018315 | 0.0006105 | 1.1233 | 0 | 0.001221 | 1.1233 | 234976.7981 | 104.103 | 124522.9273
38959.5208 | 3 | 1 | 38959.5208 | 2264 | 0 |  | 2020.5 | 2147.5 | 0.18315 | 0.06105 | 138.2173 | 0 | 0.0018315 | 0.0006105 | 1.3822 | 0 | 0.001221 | 1.3822 | 23300.5241 | 11.7896 | 25747.2995
38959.5213 | 3 | 0 | 38959.5213 | 2005 | 1 |  | 2062.5 | 2189.5 | 0.18315 | 0 | 122.4054 | 0.06105 | 0.0018315 | 0 | 1.2241 | 0.0006105 | 0.0018315 | 1.2234 | 81412.6667 | 22.025 | 81412.6648
38959.5218 | 3 | 1 | 38959.5218 | 2358 | 0 |  | 2104.5 | 2231.5 | 0.18315 | 0.06105 | 143.956 | 0 | 0.0018315 | 0.0006105 | 1.4396 | 0 | 0.001221 | 1.4396 | 9775.1582 | 4.3506 | 10178.5322
38959.5222 | 2 | 1 | 38959.5223 | 2143 | 1 |  | 2146.5 | 2273.5 | 0.1221 | 0.06105 | 130.8303 | 0.06105 | 0.001221 | 0.0006105 | 1.3083 | 0.0006105 | 0.0006105 | 1.3077 | 40162.0033 | 19.6703 | 40145.5662
38959.5227 | 3 | 0 | 38959.5227 | 2130 | 1 |  | 2188.5 | 2315.5 | 0.18315 | 0 | 130.0366 | 0.06105 | 0.0018315 | 0 | 1.3004 | 0.0006105 | 0.0018315 | 1.2998 | 81412.6667 | 14.8605 | 81412.6648
38959.5232 | 3 | 1 | 38959.5232 | 2323 | 0 |  | 2230.5 | 2357.5 | 0.18315 | 0.06105 | 141.8193 | 0 | 0.0018315 | 0.0006105 | 1.4182 | 0 | 0.001221 | 1.4182 | 14382.2881 | 6.6747 | 15275.9443
38959.5237 | 3 | 1 | 38959.5237 | 2132 | 0 |  | 2272.5 | 2399.5 | 0.18315 | 0.06105 | 130.1587 | 0 | 0.0018315 | 0.0006105 | 1.3016 | 0 | 0.001221 | 1.3016 | 50848.5719 | 35.673 | 64192.0749
38959.5242 | 2 | 0 | 38959.5242 | 2103 | 0 |  | 2314.5 | 2441.5 | 0.1221 | 0 | 128.3883 | 0 | 0.001221 | 0 | 1.2839 | 0 | 0.001221 | 1.2839 | 122169 | 16.2806 | 122168.9988
38959.5247 | 3 | 0 | 38959.5247 | 1994 | 1 |  | 2356.5 | 2483.5 | 0.18315 | 0 | 121.7338 | 0.06105 | 0.0018315 | 0 | 1.2173 | 0.0006105 | 0.0018315 | 1.2167 | 81412.6667 | 22.6984 | 81412.6648
38959.5252 | 3 | 0 | 38959.5252 | 2281 | 0 |  | 2398.5 | 2525.5 | 0.18315 | 0 | 139.2552 | 0 | 0.0018315 | 0 | 1.3926 | 0 | 0.0018315 | 1.3926 | 81412.6667 | 7.2065 | 81412.6648
38959.5256 | 2 | 0 | 38959.5257 | 2222 | 0 |  | 2440.5 | 2567.5 | 0.1221 | 0 | 135.6532 | 0 | 0.001221 | 0 | 1.3565 | 0 | 0.001221 | 1.3565 | 122169 | 10.0531 | 122168.9988
38959.5261 | 2 | 1 | 38959.5261 | 2063 | 0 |  | 2482.5 | 2609.5 | 0.1221 | 0.06105 | 125.9463 | 0 | 0.001221 | 0.0006105 | 1.2595 | 0 | 0.0006105 | 1.2595 | 55592.5578 | 29.4537 | 55569.8055
38959.5266 | 3 | 1 | 38959.5266 | 2279 | 0 |  | 2524.5 | 2651.5 | 0.18315 | 0.06105 | 139.1331 | 0 | 0.0018315 | 0.0006105 | 1.3913 | 0 | 0.001221 | 1.3913 | 20879.3974 | 10.3119 | 22821.8402
38959.5271 | 3 | 0 | 38959.5271 | 2109 | 0 |  | 2566.5 | 2693.5 | 0.18315 | 0 | 128.7546 | 0 | 0.0018315 | 0 | 1.2875 | 0 | 0.0018315 | 1.2875 | 81412.6667 | 15.9497 | 81412.6648
38959.5276 | 4 | 0 | 38959.5276 | 1913 | 0 |  | 2608.5 | 2735.5 | 0.2442 | 0 | 116.7888 | 0 | 0.002442 | 0 | 1.1679 | 0 | 0.002442 | 1.1679 | 61034.5 | 27.8296 | 61034.4976
38959.5281 | 8 | 0 | 38959.5281 | 2073 | 0 |  | 2650.5 | 2777.5 | 0.4884 | 0 | 126.5568 | 0 | 0.004884 | 0 | 1.2656 | 0 | 0.004884 | 1.2656 | 30467.25 | 17.9633 | 30467.2451
38959.5286 | 20 | 0 | 38959.5286 | 1938 | 1 |  | 2692.5 | 2819.5 | 1.221 | 0 | 118.315 | 0.06105 | 0.01221 | 0 | 1.1832 | 0.0006105 | 0.01221 | 1.1825 | 12126.9 | 26.2457 | 12126.8878
38959.5291 | 41 | 0 | 38959.5291 | 2373 | 0 |  | 2734.5 | 2861.5 | 2.5031 | 0 | 144.8718 | 0 | 0.025031 | 0 | 1.4487 | 0 | 0.025031 | 1.4487 | 5864.3415 | 3.0501 | 5864.3164
38959.5295 | 78 | 1 | 38959.5295 | 2134 | 0 |  | 2776.5 | 2903.5 | 4.7619 | 0.06105 | 130.2808 | 0 | 0.047619 | 0.0006105 | 1.3028 | 0 | 0.047009 | 1.3028 | 3374.9016 | 14.5914 | 30132.0615
38959.53 | 93 | 0 | 38959.53 | 2378 | 0 |  | 2818.5 | 2945.5 | 5.6777 | 0 | 145.177 | 0 | 0.056777 | 0 | 1.4518 | 0 | 0.056777 | 1.4518 | 2529.4409 | 2.8335 | 2529.3841
38959.5305 | 125 | 0 | 38959.5305 | 2309 | 0 |  | 2860.5 | 2987.5 | 7.6313 | 0 | 140.9646 | 0 | 0.076313 | 0 | 1.4096 | 0 | 0.076313 | 1.4096 | 1856.304 | 5.9065 | 1856.2277
38959.531 | 179 | 0 | 38959.531 | 2429 | 0 |  | 2902.5 | 3029.5 | 10.928 | 0 | 148.2906 | 0 | 0.10928 | 0 | 1.4829 | 0 | 0.10928 | 1.4829 | 1266.1341 | 0.67435 | 1266.0248
38959.5315 | 1840 | 2 | 38959.5315 | 2369 | 1 |  | 2944.5 | 3071.5 | 112.3321 | 0.1221 | 144.6276 | 0.06105 | 1.1233 | 0.001221 | 1.4463 | 0.0006105 | 1.1221 | 1.4457 | 34.0853 | 3.2295 | 943.8292
38959.532 | 2205 | 2 | 38959.532 | 2212 | 2 |  | 2986.5 | 3113.5 | 134.6154 | 0.1221 | 135.0427 | 0.1221 | 1.3462 | 0.001221 | 1.3504 | 0.001221 | 1.3449 | 1.3492 | 11.0053 | 10.6477 | 1146.9768
38959.5325 | 1811 | 2 | 38959.5325 | 2090 | 1 |  | 3028.5 | 3155.5 | 110.5617 | 0.1221 | 127.5946 | 0.06105 | 1.1056 | 0.001221 | 1.2759 | 0.0006105 | 1.1044 | 1.2753 | 35.2971 | 17.0351 | 4602.3118
38959.5329 | 2056 | 2 | 38959.533 | 2304 | 2 |  | 3070.5 | 3197.5 | 125.5189 | 0.1221 | 140.6593 | 0.1221 | 1.2552 | 0.001221 | 1.4066 | 0.001221 | 1.254 | 1.4054 | 19.2612 | 6.1694 | 1125.5213
38959.5334 | 1919 | 2 | 38959.5334 | 1961 | 2 |  | 3112.5 | 3239.5 | 117.1551 | 0.1221 | 119.7192 | 0.1221 | 1.1716 | 0.001221 | 1.1972 | 0.001221 | 1.1703 | 1.196 | 27.5744 | 24.8178 | 5213.1764
38959.5339 | 1823 | 2 | 38959.5339 | 1897 | 2 |  | 3154.5 | 3281.5 | 111.2943 | 0.1221 | 115.812 | 0.1221 | 1.1129 | 0.001221 | 1.1581 | 0.001221 | 1.1117 | 1.1569 | 34.3077 | 29.0276 | 6978.3989
38959.5344 | 2251 | 3 | 38959.5344 | 2150 | 3 |  | 3196.5 | 3323.5 | 137.4237 | 0.18315 | 131.2576 | 0.18315 | 1.3742 | 0.0018315 | 1.3126 | 0.0018315 | 1.3724 | 1.3107 | 8.7301 | 13.9816 | 782.5227
38959.5349 | 2034 | 4 | 38959.5349 | 1958 | 3 |  | 3238.5 | 3365.5 | 124.1758 | 0.2442 | 119.536 | 0.18315 | 1.2418 | 0.002442 | 1.1954 | 0.0018315 | 1.2393 | 1.1935 | 20.4253 | 25.1186 | 2044.6255

## A1-B3
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 151.6716 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38959.496 | 1 | 0 | 38959.496 | 1 | 0 |  | -124 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4965 | 1 | 0 | 38959.4965 | 1 | 0 |  | -81.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4969 | 1 | 0 | 38959.497 | 1 | 0 |  | -40 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4974 | 1 | 0 | 38959.4974 | 1 | 0 |  | 2 | 129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4979 | 1 | 0 | 38959.4979 | 1 | 0 |  | 44 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4984 | 1 | 0 | 38959.4984 | 1 | 0 |  | 86 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4989 | 1 | 0 | 38959.4989 | 1 | 0 |  | 128 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4994 | 1 | 0 | 38959.4994 | 1 | 0 |  | 170 | 297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.4999 | 1 | 0 | 38959.4999 | 1 | 0 |  | 212.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5003 | 1 | 0 | 38959.5004 | 1 | 0 |  | 254 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5008 | 1 | 0 | 38959.5008 | 1 | 0 |  | 296 | 423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5013 | 1 | 0 | 38959.5013 | 1 | 0 |  | 338 | 465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5018 | 1 | 0 | 38959.5018 | 1 | 0 |  | 380 | 507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5023 | 1 | 0 | 38959.5023 | 1 | 0 |  | 422 | 549 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5028 | 1 | 0 | 38959.5028 | 1 | 0 |  | 464 | 591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5033 | 1 | 0 | 38959.5033 | 1 | 0 |  | 506 | 633 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5037 | 1 | 0 | 38959.5038 | 1 | 0 |  | 548 | 675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5042 | 1 | 0 | 38959.5042 | 1 | 0 |  | 590 | 717 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5047 | 1 | 0 | 38959.5047 | 1 | 0 |  | 632 | 759 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5052 | 1 | 0 | 38959.5052 | 1 | 0 |  | 674 | 801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5057 | 1 | 0 | 38959.5057 | 1 | 0 |  | 716 | 843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5062 | 1 | 0 | 38959.5062 | 2 | 0 |  | 758 | 885 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 248338 | 124119 | 248337.9994
38959.5067 | 1 | 0 | 38959.5067 | 1 | 0 |  | 800 | 927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5071 | 1 | 0 | 38959.5072 | 1 | 0 |  | 842 | 969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5076 | 1 | 0 | 38959.5077 | 1 | 0 |  | 884 | 1011 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5081 | 1 | 0 | 38959.5081 | 1 | 0 |  | 926 | 1053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5086 | 1 | 0 | 38959.5086 | 1 | 0 |  | 968 | 1095 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5091 | 1 | 0 | 38959.5091 | 1 | 0 |  | 1010 | 1137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5096 | 1 | 0 | 38959.5096 | 1 | 0 |  | 1052 | 1179 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5101 | 1 | 0 | 38959.5101 | 1 | 0 |  | 1094 | 1221 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5105 | 1 | 0 | 38959.5106 | 1 | 0 |  | 1136 | 1263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.511 | 1 | 0 | 38959.5111 | 1 | 0 |  | 1178 | 1305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5115 | 1 | 0 | 38959.5115 | 1 | 0 |  | 1220 | 1347 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.512 | 1 | 0 | 38959.512 | 1 | 0 |  | 1262 | 1389 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.5125 | 1 | 0 | 38959.5125 | 1 | 0 |  | 1304 | 1431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248338 | 248338 | 248337.9994
38959.513 | 3 | 0 | 38959.513 | 2 | 1 |  | 1346 | 1473 | 0.18315 | 0 | 0.1221 | 0.06105 | 0.0018315 | 0 | 0.001221 | 0.0006105 | 0.0018315 | 0.0006105 | 82712.6667 | 248338 | 82712.6648
38959.5135 | 3 | 0 | 38959.5135 | 2 | 0 |  | 1388 | 1515 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82712.6667 | 124119 | 82712.6648
38959.5139 | 3 | 0 | 38959.514 | 2 | 0 |  | 1430 | 1557 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 82712.6667 | 124119 | 82712.6648
38959.5144 | 2 | 0 | 38959.5145 | 2 | 0 |  | 1472 | 1599 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124119 | 124119 | 124118.9988
38959.5149 | 2 | 0 | 38959.5149 | 2 | 0 |  | 1514 | 1641 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124119 | 124119 | 124118.9988
38959.5154 | 2 | 0 | 38959.5154 | 3 | 0 |  | 1556 | 1683 | 0.1221 | 0 | 0.18315 | 0 | 0.001221 | 0 | 0.0018315 | 0 | 0.001221 | 0.0018315 | 124119 | 82712.6667 | 124118.9988
38959.5159 | 2 | 0 | 38959.5159 | 2 | 0 |  | 1598 | 1725 | 0.1221 | 0 | 0.1221 | 0 | 0.001221 | 0 | 0.001221 | 0 | 0.001221 | 0.001221 | 124119 | 124119 | 124118.9988
38959.5164 | 3 | 0 | 38959.5164 | 1077 | 0 |  | 1640 | 1767 | 0.18315 | 0 | 65.7509 | 0 | 0.0018315 | 0 | 0.65751 | 0 | 0.0018315 | 0.65751 | 82712.6667 | 130.676 | 82712.6648
38959.5169 | 2 | 0 | 38959.5169 | 2092 | 0 |  | 1682 | 1809 | 0.1221 | 0 | 127.7167 | 0 | 0.001221 | 0 | 1.2772 | 0 | 0.001221 | 1.2772 | 124119 | 18.7562 | 124118.9988
38959.5173 | 3 | 2 | 38959.5174 | 2303 | 0 |  | 1724 | 1851 | 0.18315 | 0.1221 | 140.5983 | 0 | 0.0018315 | 0.001221 | 1.406 | 0 | 0.0006105 | 1.406 | 10172.0081 | 8.5491 | 9763.5681
38959.5178 | 3 | 3 | 38959.5179 | 1996 | 1 |  | 1766 | 1893 | 0.18315 | 0.18315 | 121.8559 | 0.06105 | 0.0018315 | 0.0018315 | 1.2186 | 0.0006105 | 0 | 1.2179 | 20248.1765 | 24.4801 | 16246.5245
38959.5183 | 3 | 2 | 38959.5183 | 2153 | 1 |  | 1808 | 1935 | 0.18315 | 0.1221 | 131.4408 | 0.06105 | 0.0018315 | 0.001221 | 1.3144 | 0.0006105 | 0.0006105 | 1.3138 | 20698.6247 | 18.2014 | 19089.5702
38959.5188 | 3 | 2 | 38959.5188 | 1942 | 1 |  | 1850 | 1977 | 0.18315 | 0.1221 | 118.5592 | 0.06105 | 0.0018315 | 0.001221 | 1.1856 | 0.0006105 | 0.0006105 | 1.185 | 40299.4617 | 38.7796 | 34641.0202
38959.5193 | 3 | 2 | 38959.5193 | 1978 | 1 |  | 1892 | 2019 | 0.18315 | 0.1221 | 120.757 | 0.06105 | 0.0018315 | 0.001221 | 1.2076 | 0.0006105 | 0.0006105 | 1.207 | 36445.989 | 34.433 | 31752.825
38959.5198 | 2 | 2 | 38959.5198 | 1964 | 1 |  | 1934 | 2061 | 0.1221 | 0.1221 | 119.9023 | 0.06105 | 0.001221 | 0.001221 | 1.199 | 0.0006105 | 0 | 1.1984 | 32903.1815 | 26.5094 | 25987.5364
38959.5203 | 3 | 2 | 38959.5203 | 2341 | 1 |  | 1976 | 2103 | 0.18315 | 0.1221 | 142.9182 | 0.06105 | 0.0018315 | 0.001221 | 1.4292 | 0.0006105 | 0.0006105 | 1.4286 | 7842.3642 | 6.5273 | 7595.9737
38959.5208 | 3 | 3 | 38959.5208 | 1986 | 1 |  | 2018 | 2145 | 0.18315 | 0.18315 | 121.2454 | 0.06105 | 0.0018315 | 0.0018315 | 1.2125 | 0.0006105 | 0 | 1.2118 | 20766.8709 | 25.1072 | 16579.1868
38959.5212 | 3 | 2 | 38959.5213 | 2289 | 1 |  | 2060 | 2187 | 0.18315 | 0.1221 | 139.7436 | 0.06105 | 0.0018315 | 0.001221 | 1.3974 | 0.0006105 | 0.0006105 | 1.3968 | 11067.1554 | 9.3366 | 10586.0872
38959.5217 | 3 | 3 | 38959.5217 | 2061 | 1 |  | 2102 | 2229 | 0.18315 | 0.18315 | 125.8242 | 0.06105 | 0.0018315 | 0.0018315 | 1.2582 | 0.0006105 | 0 | 1.2576 | 16999.412 | 20.5524 | 14084.2191
38959.5222 | 2 | 2 | 38959.5222 | 2208 | 1 |  | 2144 | 2271 | 0.1221 | 0.1221 | 134.7985 | 0.06105 | 0.001221 | 0.001221 | 1.348 | 0.0006105 | 0 | 1.3474 | 15543.2303 | 12.5228 | 13802.2705
38959.5227 | 2 | 2 | 38959.5227 | 1893 | 1 |  | 2186 | 2313 | 0.1221 | 0.1221 | 115.5678 | 0.06105 | 0.001221 | 0.001221 | 1.1557 | 0.0006105 | 0 | 1.1551 | 38795.6629 | 31.2568 | 29533.2491
38959.5232 | 2 | 2 | 38959.5232 | 2364 | 1 |  | 2228 | 2355 | 0.1221 | 0.1221 | 144.3223 | 0.06105 | 0.001221 | 0.001221 | 1.4432 | 0.0006105 | 0 | 1.4426 | 6323.0407 | 5.0943 | 6011.6906
38959.5237 | 2 | 2 | 38959.5237 | 2440 | 1 |  | 2269.5 | 2396.5 | 0.1221 | 0.1221 | 148.9621 | 0.06105 | 0.001221 | 0.001221 | 1.4896 | 0.0006105 | 0 | 1.489 | 2258.4261 | 1.8196 | 2216.2799
38959.5242 | 2 | 3 | 38959.5242 | 1899 | 1 |  | 2312 | 2439 | 0.1221 | 0.18315 | 115.9341 | 0.06105 | 0.001221 | 0.0018315 | 1.1593 | 0.0006105 | 0.0006105 | 1.1587 | 28444.719 | 38.8247 | 23113.381
38959.5246 | 2 | 2 | 38959.5247 | 1965 | 1 |  | 2353.5 | 2480.5 | 0.1221 | 0.1221 | 119.9634 | 0.06105 | 0.001221 | 0.001221 | 1.1996 | 0.0006105 | 0 | 1.199 | 32823.2313 | 26.445 | 25937.5968
38959.5251 | 2 | 2 | 38959.5252 | 1997 | 2 |  | 2396 | 2523 | 0.1221 | 0.1221 | 121.917 | 0.1221 | 0.001221 | 0.001221 | 1.2192 | 0.001221 | 0 | 1.2179 | 30322.2648 | 24.43 | 24349.3017
38959.5256 | 3 | 2 | 38959.5256 | 1989 | 1 |  | 2438 | 2565 | 0.18315 | 0.1221 | 121.4286 | 0.06105 | 0.0018315 | 0.001221 | 1.2143 | 0.0006105 | 0.0006105 | 1.2137 | 35316.2375 | 33.1886 | 30891.185
38959.5261 | 2 | 2 | 38959.5261 | 2362 | 1 |  | 2480 | 2607 | 0.1221 | 0.1221 | 144.2002 | 0.06105 | 0.001221 | 0.001221 | 1.442 | 0.0006105 | 0 | 1.4414 | 6433.538 | 5.1834 | 6111.5698
38959.5266 | 3 | 2 | 38959.5266 | 2181 | 1 |  | 2521.5 | 2648.5 | 0.18315 | 0.1221 | 133.1502 | 0.06105 | 0.0018315 | 0.001221 | 1.3315 | 0.0006105 | 0.0006105 | 1.3309 | 18557.2981 | 16.1663 | 17252.1203
38959.5271 | 3 | 2 | 38959.5271 | 1984 | 1 |  | 2563.5 | 2690.5 | 0.18315 | 0.1221 | 121.1233 | 0.06105 | 0.0018315 | 0.001221 | 1.2112 | 0.0006105 | 0.0006105 | 1.2106 | 35827.0937 | 33.7496 | 31281.6545
38959.5276 | 4 | 2 | 38959.5276 | 2397 | 1 |  | 2605.5 | 2732.5 | 0.2442 | 0.1221 | 146.337 | 0.06105 | 0.002442 | 0.001221 | 1.4634 | 0.0006105 | 0.001221 | 1.4628 | 4694.0078 | 3.9338 | 4690.2229
38959.528 | 8 | 2 | 38959.5281 | 2391 | 1 |  | 2647.5 | 2774.5 | 0.4884 | 0.1221 | 145.9707 | 0.06105 | 0.004884 | 0.001221 | 1.4597 | 0.0006105 | 0.003663 | 1.4591 | 5480.0405 | 5.1035 | 6007.3686
38959.5285 | 19 | 1 | 38959.5285 | 2238 | 1 |  | 2689.5 | 2816.5 | 1.16 | 0.06105 | 136.63 | 0.06105 | 0.0116 | 0.0006105 | 1.3663 | 0.0006105 | 0.010989 | 1.3657 | 27637.1039 | 11.0139 | 24449.5337
38959.529 | 37 | 2 | 38959.529 | 2446 | 1 |  | 2732 | 2859 | 2.2589 | 0.1221 | 149.3284 | 0.06105 | 0.022589 | 0.001221 | 1.4933 | 0.0006105 | 0.021368 | 1.4927 | 2648.3335 | 3.4836 | 4115.9645
38959.5295 | 60 | 1 | 38959.5295 | 2274 | 1 |  | 2773.5 | 2900.5 | 3.663 | 0.06105 | 138.8278 | 0.06105 | 0.03663 | 0.0006105 | 1.3883 | 0.0006105 | 0.03602 | 1.3877 | 5030.2686 | 9.2557 | 20529.8732
38959.53 | 89 | 2 | 38959.53 | 2126 | 1 |  | 2815.5 | 2942.5 | 5.4335 | 0.1221 | 129.7924 | 0.06105 | 0.054335 | 0.001221 | 1.2979 | 0.0006105 | 0.053114 | 1.2973 | 3187.8361 | 16.8652 | 17269.8169
38959.5305 | 131 | 2 | 38959.5305 | 2074 | 1 |  | 2857.5 | 2984.5 | 7.9976 | 0.1221 | 126.6178 | 0.06105 | 0.079976 | 0.001221 | 1.2662 | 0.0006105 | 0.078755 | 1.2656 | 1979.3366 | 19.7969 | 19428.7414
38959.531 | 169 | 1 | 38959.531 | 2200 | 1 |  | 2899.5 | 3026.5 | 10.3175 | 0.06105 | 134.3101 | 0.06105 | 0.10317 | 0.0006105 | 1.3431 | 0.0006105 | 0.10256 | 1.3425 | 1444.696 | 12.9326 | 26503.4642
38959.5314 | 1794 | 0 | 38959.5315 | 1912 | 0 |  | 2941.5 | 3068.5 | 109.5238 | 0 | 116.7277 | 0 | 1.0952 | 0 | 1.1673 | 0 | 1.0952 | 1.1673 | 38.4827 | 29.9362 | 37.3875
38959.5319 | 1894 | 0 | 38959.5319 | 2193 | 0 |  | 2983.5 | 3110.5 | 115.6288 | 0 | 133.8828 | 0 | 1.1563 | 0 | 1.3388 | 0 | 1.1563 | 1.3388 | 31.1711 | 13.2868 | 30.0148
38959.5324 | 1779 | 0 | 38959.5324 | 2030 | 0 |  | 3025.5 | 3152.5 | 108.6081 | 0 | 123.9316 | 0 | 1.0861 | 0 | 1.2393 | 0 | 1.0861 | 1.2393 | 39.6504 | 22.3833 | 38.5643
38959.5329 | 2220 | 0 | 38959.5329 | 2335 | 0 |  | 3067.5 | 3194.5 | 135.5311 | 0 | 142.5519 | 0 | 1.3553 | 0 | 1.4255 | 0 | 1.3553 | 1.4255 | 11.909 | 6.3974 | 10.5537
38959.5334 | 2299 | 0 | 38959.5334 | 2320 | 0 |  | 3109.5 | 3236.5 | 140.3541 | 0 | 141.6361 | 0 | 1.4035 | 0 | 1.4164 | 0 | 1.4035 | 1.4164 | 8.0635 | 7.0853 | 6.66
38959.5339 | 2211 | 0 | 38959.5339 | 2452 | 0 |  | 3151.5 | 3278.5 | 134.9817 | 0 | 149.6947 | 0 | 1.3498 | 0 | 1.4969 | 0 | 1.3498 | 1.4969 | 12.3645 | 1.3206 | 11.0147
38959.5344 | 1949 | 0 | 38959.5344 | 2468 | 0 |  | 3193.5 | 3320.5 | 118.9866 | 0 | 150.6716 | 0 | 1.1899 | 0 | 1.5067 | 0 | 1.1899 | 1.5067 | 27.4695 | 0.6637 | 26.2796
38959.5348 | 1927 | 0 | 38959.5349 | 2421 | 0 |  | 3235.5 | 3362.5 | 117.6435 | 0 | 147.8022 | 0 | 1.1764 | 0 | 1.478 | 0 | 1.1764 | 1.478 | 28.9248 | 2.6179 | 27.7483

## A1-A2
Penlight Test 47 |  |  | 2006-08-30 | 11:56 |  |  | Vs = |  | 141.7814 |  | R = | 100
XLPE & EPR | 7-C | Conduit
525 C | 23 kW/m2 |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38959.4959 | 1 | 0 | 38959.4959 | 1 | 0 |  | -126.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4964 | 1 | 0 | 38959.4964 | 1 | 0 |  | -84.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4969 | 1 | 0 | 38959.4969 | 1 | 0 |  | -42.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4974 | 1 | 0 | 38959.4974 | 1 | 0 |  | -0.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4979 | 1 | 0 | 38959.4979 | 1 | 0 |  | 41.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4984 | 1 | 0 | 38959.4984 | 1 | 0 |  | 83.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4989 | 1 | 0 | 38959.4989 | 1 | 0 |  | 125.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4993 | 1 | 0 | 38959.4994 | 1 | 0 |  | 167.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.4998 | 1 | 0 | 38959.4998 | 1 | 0 |  | 209.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5003 | 1 | 0 | 38959.5003 | 1 | 0 |  | 251.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5008 | 1 | 0 | 38959.5008 | 1 | 0 |  | 293.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5013 | 1 | 0 | 38959.5013 | 1 | 0 |  | 335.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5018 | 1 | 0 | 38959.5018 | 1 | 0 |  | 377.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5023 | 1 | 0 | 38959.5023 | 1 | 0 |  | 419.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5027 | 1 | 0 | 38959.5028 | 1 | 0 |  | 461.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5032 | 1 | 0 | 38959.5032 | 1 | 0 |  | 503.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5037 | 1 | 0 | 38959.5037 | 1 | 0 |  | 545.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5042 | 1 | 0 | 38959.5042 | 1 | 0 |  | 587.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5047 | 1 | 0 | 38959.5047 | 1 | 0 |  | 629.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5052 | 1 | 0 | 38959.5052 | 1 | 0 |  | 671.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5057 | 1 | 0 | 38959.5057 | 1 | 0 |  | 713.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5061 | 1 | 0 | 38959.5062 | 1 | 0 |  | 755.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5066 | 1 | 0 | 38959.5066 | 1 | 0 |  | 797.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5071 | 1 | 0 | 38959.5071 | 1 | 0 |  | 839.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5076 | 1 | 0 | 38959.5076 | 1 | 0 |  | 881 | 1008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5081 | 1 | 0 | 38959.5081 | 1 | 0 |  | 923.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5086 | 1 | 0 | 38959.5086 | 1 | 0 |  | 965 | 1092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5091 | 1 | 0 | 38959.5091 | 1 | 0 |  | 1007 | 1134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5095 | 1 | 0 | 38959.5096 | 1 | 0 |  | 1049.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.51 | 1 | 0 | 38959.51 | 1 | 0 |  | 1091 | 1218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5105 | 1 | 0 | 38959.5105 | 1 | 0 |  | 1133.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.511 | 1 | 0 | 38959.511 | 1 | 0 |  | 1175 | 1302 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5115 | 1 | 0 | 38959.5115 | 1 | 0 |  | 1217 | 1344 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.512 | 1 | 0 | 38959.512 | 1 | 0 |  | 1259.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 232138 | 232138 | 232137.9994
38959.5125 | 2 | 0 | 38959.5125 | 1 | 0 |  | 1301.5 | 1428.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 116019 | 232138 | 116018.9988
38959.5129 | 3 | 0 | 38959.513 | 2 | 0 |  | 1343 | 1470 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 77312.6667 | 116019 | 77312.6648
38959.5134 | 3 | 0 | 38959.5134 | 2 | 0 |  | 1385 | 1512 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 77312.6667 | 116019 | 77312.6648
38959.5139 | 3 | 0 | 38959.5139 | 3 | 0 |  | 1427 | 1554 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 77312.6667 | 77312.6667 | 77312.6648
38959.5144 | 3 | 0 | 38959.5144 | 3 | 0 |  | 1469 | 1596 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 77312.6667 | 77312.6667 | 77312.6648
38959.5149 | 3 | 0 | 38959.5149 | 3 | 0 |  | 1511 | 1638 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 77312.6667 | 77312.6667 | 77312.6648
38959.5154 | 3 | 0 | 38959.5154 | 2 | 0 |  | 1553 | 1680 | 0.18315 | 0 | 0.1221 | 0 | 0.0018315 | 0 | 0.001221 | 0 | 0.0018315 | 0.001221 | 77312.6667 | 116019 | 77312.6648
38959.5159 | 4 | 0 | 38959.5159 | 3 | 0 |  | 1595 | 1722 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 57959.5 | 77312.6667 | 57959.4976
38959.5163 | 4 | 1 | 38959.5164 | 4 | 1 |  | 1637 | 1764 | 0.2442 | 0.06105 | 0.2442 | 0.06105 | 0.002442 | 0.0006105 | 0.002442 | 0.0006105 | 0.0018315 | 0.0018315 | 77312.6667 | 77312.6667 | 231438.6459
38959.5168 | 6 | 4 | 38959.5169 | 6 | 2 |  | 1679 | 1806 | 0.3663 | 0.2442 | 0.3663 | 0.1221 | 0.003663 | 0.002442 | 0.003663 | 0.001221 | 0.001221 | 0.002442 | 116220.213 | 57934.4244 | 57709.8876
38959.5173 | 128 | 120 | 38959.5173 | 1081 | 1130 |  | 1721 | 1848 | 7.8144 | 7.326 | 65.9951 | 68.9866 | 0.078144 | 0.07326 | 0.65995 | 0.68987 | 0.004884 | 0.029915 | 63896.171 | 2628.288 | 1665.2898
38959.5178 | 1206 | 963 | 38959.5178 | 1198 | 1125 |  | 1763 | 1890 | 73.6264 | 58.7912 | 73.138 | 68.6813 | 0.73626 | 0.58791 | 0.73138 | 0.68681 | 0.14835 | 0.044567 | 84.6914 | 89.5669 | 7.5254
38959.5183 | 1200 | 1172 | 38959.5183 | 1177 | 1196 |  | 1805 | 1932 | 73.2601 | 71.5507 | 71.8559 | 73.0159 | 0.7326 | 0.71551 | 0.71856 | 0.73016 | 0.017094 | 0.0116 | 1184.9909 | 1756.6912 | 4.0058
38959.5188 | 1061 | 1101 | 38959.5188 | 1168 | 1135 |  | 1847 | 1974 | 64.7741 | 67.2161 | 71.3065 | 69.2918 | 0.64774 | 0.67216 | 0.71306 | 0.69292 | 0.02442 | 0.020147 | 2097.8729 | 5470.3678 | 14.3053
38959.5193 | 1130 | 1095 | 38959.5193 | 1053 | 1020 |  | 1889 | 2016 | 68.9866 | 66.8498 | 64.2857 | 62.2711 | 0.68987 | 0.6685 | 0.64286 | 0.62271 | 0.021368 | 0.020147 | 4783.1783 | 10872.3852 | 8.8121
38959.5197 | 948 | 914 | 38959.5198 | 1142 | 1182 |  | 1931 | 2058 | 57.8755 | 55.7998 | 69.7192 | 72.1612 | 0.57875 | 0.558 | 0.69719 | 0.72161 | 0.020757 | 0.02442 | 15168.0604 | 3664.9444 | 49.0319
38959.5202 | 951 | 914 | 38959.5203 | 1063 | 1023 |  | 1973 | 2100 | 58.0586 | 55.7998 | 64.8962 | 62.4542 | 0.58059 | 0.558 | 0.64896 | 0.62454 | 0.022589 | 0.02442 | 7891.4198 | 4658.0642 | 48.9899
38959.5207 | 1210 | 1179 | 38959.5207 | 1162 | 1120 |  | 2015 | 2142 | 73.8706 | 71.978 | 70.9402 | 68.3761 | 0.73871 | 0.71978 | 0.7094 | 0.68376 | 0.018926 | 0.025641 | 219.2235 | 247.4716 | 4.0244
38959.5212 | 1139 | 1099 | 38959.5212 | 1047 | 1079 |  | 2057 | 2184 | 69.536 | 67.094 | 63.9194 | 65.873 | 0.69536 | 0.67094 | 0.63919 | 0.65873 | 0.02442 | 0.019536 | 2040.98 | 6112.0175 | 7.5543
38959.5217 | 990 | 1086 | 38959.5217 | 1028 | 988 |  | 2099 | 2226 | 60.4396 | 66.3004 | 62.7595 | 60.3175 | 0.6044 | 0.663 | 0.62759 | 0.60317 | 0.058608 | 0.02442 | 806.2783 | 1568.2169 | 21.327
38959.5222 | 1032 | 990 | 38959.5222 | 1085 | 1043 |  | 2141 | 2268 | 63.0037 | 60.4396 | 66.2393 | 63.6752 | 0.63004 | 0.6044 | 0.66239 | 0.63675 | 0.025641 | 0.025641 | 5429.4762 | 5429.4762 | 29.7927
38959.5227 | 1014 | 972 | 38959.5227 | 1165 | 1122 |  | 2183 | 2310 | 61.9048 | 59.3407 | 71.1233 | 68.4982 | 0.61905 | 0.59341 | 0.71123 | 0.68498 | 0.025641 | 0.026252 | 6218.2467 | 4637.6212 | 33.8765
38959.5231 | 992 | 1014 | 38959.5232 | 1101 | 1134 |  | 2225 | 2352 | 60.5617 | 61.9048 | 67.2161 | 69.2308 | 0.60562 | 0.61905 | 0.67216 | 0.69231 | 0.013431 | 0.020147 | 7206.4543 | 28651.7652 | 31.0927
38959.5236 | 1203 | 1159 | 38959.5237 | 1062 | 1015 |  | 2267 | 2394 | 73.4432 | 70.757 | 64.8352 | 61.9658 | 0.73443 | 0.70757 | 0.64835 | 0.61966 | 0.026862 | 0.028694 | 23833.9329 | 2948.8529 | 3.3063
38959.5241 | 1132 | 1082 | 38959.5241 | 1068 | 1019 |  | 2309 | 2436 | 69.1087 | 66.0562 | 65.2015 | 62.21 | 0.69109 | 0.66056 | 0.65201 | 0.6221 | 0.030525 | 0.029915 | 4026.7072 | 5294.0911 | 9.8309
38959.5246 | 1134 | 906 | 38959.5246 | 1195 | 1145 |  | 2351 | 2478 | 69.2308 | 55.3114 | 72.9548 | 69.9023 | 0.69231 | 0.55311 | 0.72955 | 0.69902 | 0.13919 | 0.030525 | 142.8082 | 149.9625 | 18.6988
38959.5251 | 1063 | 1008 | 38959.5251 | 1165 | 1168 |  | 2393 | 2520 | 64.8962 | 61.5385 | 71.1233 | 71.3065 | 0.64896 | 0.61538 | 0.71123 | 0.71306 | 0.033578 | 0.0018315 | 462.1944 | 463.4942 | 20.5128
38959.5256 | 978 | 984 | 38959.5256 | 961 | 908 |  | 2435 | 2562 | 59.707 | 60.0733 | 58.6691 | 55.4335 | 0.59707 | 0.60073 | 0.58669 | 0.55433 | 0.003663 | 0.032357 | 2129.7427 | 1722.5667 | 34.6145
38959.5261 | 948 | 894 | 38959.5261 | 1212 | 1021 |  | 2477 | 2604 | 57.8755 | 54.5788 | 73.9927 | 62.3321 | 0.57875 | 0.54579 | 0.73993 | 0.62332 | 0.032967 | 0.11661 | 553.5615 | 460.1617 | 44.1412
38959.5266 | 1211 | 1036 | 38959.5266 | 959 | 1033 |  | 2519 | 2646 | 73.9316 | 63.2479 | 58.547 | 63.0647 | 0.73932 | 0.63248 | 0.58547 | 0.63065 | 0.10684 | 0.045177 | 274.8423 | 451.6718 | 5.9572
38959.527 | 1084 | 1081 | 38959.5271 | 1153 | 1150 |  | 2561 | 2688 | 66.1783 | 65.9951 | 70.3907 | 70.2076 | 0.66178 | 0.65995 | 0.70391 | 0.70208 | 0.0018315 | 0.0018315 | 77312.6667 | 77312.6667 | 14.5399
38959.5275 | 1204 | 1155 | 38959.5275 | 1181 | 1095 |  | 2603 | 2730 | 73.5043 | 70.5128 | 72.1001 | 66.8498 | 0.73504 | 0.70513 | 0.721 | 0.6685 | 0.029915 | 0.052503 | 27.1219 | 28.3469 | 0.70025
38959.528 | 972 | 890 | 38959.528 | 1051 | 962 |  | 2645 | 2772 | 59.3407 | 54.3346 | 64.1636 | 58.7302 | 0.59341 | 0.54335 | 0.64164 | 0.5873 | 0.050061 | 0.054335 | 3436.7313 | 2083.9464 | 49.3595
38959.5285 | 1064 | 963 | 38959.5285 | 1164 | 1054 |  | 2687 | 2814 | 64.9573 | 58.7912 | 71.0623 | 64.3468 | 0.64957 | 0.58791 | 0.71062 | 0.64347 | 0.061661 | 0.067155 | 4000.2261 | 1384.7691 | 28.6071
38959.529 | 1085 | 971 | 38959.529 | 1035 | 924 |  | 2729 | 2856 | 66.2393 | 59.2796 | 63.1868 | 56.4103 | 0.66239 | 0.5928 | 0.63187 | 0.5641 | 0.069597 | 0.067766 | 1784.9373 | 2173.3994 | 26.2269
38959.5295 | 1167 | 1026 | 38959.5295 | 1249 | 1106 |  | 2771 | 2898 | 71.2454 | 62.6374 | 76.2515 | 67.5214 | 0.71245 | 0.62637 | 0.76252 | 0.67521 | 0.086081 | 0.087302 | 2277.2812 | 1136.6539 | 11.5904
38959.53 | 1259 | 1108 | 38959.53 | 1013 | 876 |  | 2813 | 2940 | 76.862 | 67.6435 | 61.8437 | 53.4799 | 0.76862 | 0.67643 | 0.61844 | 0.5348 | 0.092186 | 0.083639 | 918.4604 | 3145.809 | 3.903
38959.5304 | 1003 | 853 | 38959.5305 | 1132 | 964 |  | 2855 | 2982 | 61.2332 | 52.0757 | 69.1087 | 58.8523 | 0.61233 | 0.52076 | 0.69109 | 0.58852 | 0.091575 | 0.10256 | 2122.5756 | 971.077 | 49.5706
38959.5309 | 1204 | 1075 | 38959.5309 | 1218 | 1012 |  | 2897 | 3024 | 73.5043 | 65.6288 | 74.359 | 61.7827 | 0.73504 | 0.65629 | 0.74359 | 0.61783 | 0.078755 | 0.12576 | 186.3854 | 228.2203 | 2.8059
38959.5314 | 2104 | 160 | 38959.5314 | 1818 | 118 |  | 2939 | 3066 | 128.4493 | 9.768 | 110.989 | 7.2039 | 1.2845 | 0.09768 | 1.1099 | 0.072039 | 1.1868 | 1.0379 | 12.8814 | 64.3383 | 14.2848
38959.5319 | 1896 | 85 | 38959.5319 | 2170 | 89 |  | 2981 | 3108 | 115.7509 | 5.1893 | 132.4786 | 5.4335 | 1.1575 | 0.051893 | 1.3248 | 0.054335 | 1.1056 | 1.2705 | 57.9426 | 7.906 | 29.4259
38959.5324 | 2002 | 83 | 38959.5324 | 2271 | 81 |  | 3023 | 3150 | 122.2222 | 5.0672 | 138.6447 | 4.9451 | 1.2222 | 0.050672 | 1.3864 | 0.049451 | 1.1716 | 1.337 | 11.7084 | 10.1552 | 26.3663
38959.5329 | 2306 | 85 | 38959.5329 | 1815 | 64 |  | 3065 | 3192 | 140.7814 | 5.1893 | 110.8059 | 3.9072 | 1.4078 | 0.051893 | 1.1081 | 0.039072 | 1.3559 | 1.069 | 0.29353 | 2.5302 | 1.9922
38959.5334 | 1965 | 74 | 38959.5334 | 2124 | 70 |  | 3107 | 3234 | 119.9634 | 4.5177 | 129.6703 | 4.2735 | 1.1996 | 0.045177 | 1.2967 | 0.042735 | 1.1545 | 1.254 | 29.451 | 10.9221 | 37.7073
38959.5338 | 2141 | 76 | 38959.5339 | 1935 | 64 |  | 3149 | 3276 | 130.7082 | 4.6398 | 118.1319 | 3.9072 | 1.3071 | 0.046398 | 1.1813 | 0.039072 | 1.2607 | 1.1422 | 9.9429 | 31.5629 | 33.2651
38959.5343 | 2044 | 67 | 38959.5344 | 1846 | 62 |  | 3191 | 3318 | 124.7863 | 4.0904 | 112.6984 | 3.7851 | 1.2479 | 0.040904 | 1.127 | 0.037851 | 1.207 | 1.0891 | 15.6226 | 34.3426 | 80.6508
38959.5348 | 2205 | 81 | 38959.5348 | 2254 | 80 |  | 3233 | 3360 | 134.6154 | 4.9451 | 137.6068 | 4.884 | 1.3462 | 0.049451 | 1.3761 | 0.04884 | 1.2967 | 1.3272 | 5.012 | 37.1589 | 12.1679

## PenTemps
DAQ Time | Penlight Time | Shroud | Conduit 1 | Conduit 2 | Conduit 3 | Cable 1 | Cable 2 | Cable 3 | Cable 4 | Cable 5 | Cable 6
0 | -127 | 23.5 | 34.8 | 30.1 | 34.8 | 39.2 | 36.6 | 35.2 | 39.3 | 32.8 | 32.6
1 | -126 | 23.5 | 34.8 | 30.1 | 34.8 | 39.3 | 36.6 | 35.2 | 39.3 | 32.8 | 32.6
2 | -125 | 23.5 | 34.8 | 30.1 | 34.8 | 39.2 | 36.6 | 35.2 | 39.3 | 32.8 | 32.6
3 | -124 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39.3 | 32.8 | 32.6
4 | -123 | 23.5 | 34.7 | 30.2 | 34.8 | 39.1 | 36.5 | 35.2 | 39.3 | 32.8 | 32.6
5 | -122 | 23.5 | 34.7 | 30.2 | 34.8 | 39.2 | 36.5 | 35.2 | 39.2 | 32.8 | 32.6
6 | -121 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39.2 | 32.8 | 32.6
7 | -120 | 23.5 | 34.7 | 30.2 | 34.8 | 39 | 36.5 | 35.2 | 39.2 | 32.8 | 32.6
8 | -119 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39.2 | 32.8 | 32.6
9 | -118 | 23.5 | 34.7 | 30.2 | 34.8 | 39 | 36.5 | 35.2 | 39.1 | 32.8 | 32.6
10 | -117 | 23.5 | 34.7 | 30.3 | 34.7 | 39 | 36.5 | 35.2 | 39.1 | 32.8 | 32.6
11 | -116 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39 | 32.8 | 32.6
12 | -115 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39 | 32.8 | 32.6
13 | -114 | 23.5 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39 | 32.8 | 32.6
14 | -113 | 23.4 | 34.7 | 30.3 | 34.7 | 39.1 | 36.5 | 35.2 | 39 | 32.8 | 32.6
15 | -112 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
16 | -111 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
17 | -110 | 23.4 | 34.7 | 30.2 | 34.7 | 39.1 | 36.5 | 35.2 | 39 | 32.7 | 32.6
18 | -109 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
19 | -108 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
20 | -107 | 23.4 | 34.7 | 30.2 | 34.7 | 39.1 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
21 | -106 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
22 | -105 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
23 | -104 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
24 | -103 | 23.4 | 34.7 | 30.3 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
25 | -102 | 23.4 | 34.7 | 30.3 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
26 | -101 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
27 | -100 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
28 | -99 | 23.4 | 34.7 | 30.3 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
29 | -98 | 23.4 | 34.7 | 30.3 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
30 | -97 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
31 | -96 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.5
32 | -95 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.6
33 | -94 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 38.9 | 32.7 | 32.5
34 | -93 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.2 | 39 | 32.7 | 32.6
35 | -92 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39 | 32.7 | 32.6
36 | -91 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39 | 32.7 | 32.6
37 | -90 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39 | 32.7 | 32.6
38 | -89 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39.1 | 32.7 | 32.5
39 | -88 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39.1 | 32.7 | 32.5
40 | -87 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.5 | 35.1 | 39 | 32.7 | 32.6
41 | -86 | 23.4 | 34.7 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.6
42 | -85 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
43 | -84 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.5
44 | -83 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.5
45 | -82 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.5
46 | -81 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.5
47 | -80 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
48 | -79 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
49 | -78 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
50 | -77 | 23.4 | 34.6 | 30.2 | 34.7 | 39 | 36.4 | 35.1 | 39 | 32.7 | 32.5
51 | -76 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
52 | -75 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
53 | -74 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
54 | -73 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
55 | -72 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
56 | -71 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
57 | -70 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
58 | -69 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
59 | -68 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
60 | -67 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
61 | -66 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
62 | -65 | 23.4 | 34.6 | 30.2 | 34.7 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
63 | -64 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
64 | -63 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
65 | -62 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
66 | -61 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
67 | -60 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
68 | -59 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
69 | -58 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
70 | -57 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
71 | -56 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.7 | 32.5
72 | -55 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
73 | -54 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
74 | -53 | 23.4 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
75 | -52 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
76 | -51 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.6 | 32.5
77 | -50 | 23.4 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
78 | -49 | 23.4 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
79 | -48 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.7 | 32.5
80 | -47 | 23.4 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.6 | 32.5
81 | -46 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.6 | 32.5
82 | -45 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39.1 | 32.6 | 32.5
83 | -44 | 23.4 | 34.6 | 30.1 | 34.6 | 39 | 36.4 | 35.1 | 39 | 32.6 | 32.5
84 | -43 | 23.4 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.6 | 32.5
85 | -42 | 23.4 | 34.6 | 30.2 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.6 | 32.5
86 | -41 | 23.3 | 34.6 | 30.1 | 34.6 | 39.1 | 36.4 | 35 | 39 | 32.6 | 32.5
87 | -40 | 23.3 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35.1 | 39 | 32.6 | 32.5
88 | -39 | 23.3 | 34.7 | 30 | 34.7 | 39.1 | 36.4 | 35 | 39 | 32.6 | 32.5
89 | -38 | 23.3 | 34.6 | 30 | 34.7 | 39.1 | 36.4 | 35 | 39 | 32.6 | 32.5
90 | -37 | 23.3 | 34.7 | 30 | 34.7 | 39.1 | 36.4 | 35 | 39 | 32.6 | 32.5
91 | -36 | 23.3 | 34.6 | 30 | 34.7 | 39.1 | 36.4 | 35 | 39 | 32.6 | 32.5
92 | -35 | 23.3 | 34.6 | 30 | 34.7 | 39 | 36.4 | 35 | 39 | 32.6 | 32.5
93 | -34 | 23.3 | 34.6 | 30.1 | 34.6 | 39 | 36.4 | 35 | 39 | 32.6 | 32.5
94 | -33 | 23.3 | 34.6 | 30.1 | 34.6 | 38.9 | 36.4 | 35 | 39 | 32.6 | 32.5
95 | -32 | 23.3 | 34.6 | 30.1 | 34.6 | 39 | 36.4 | 35 | 39 | 32.6 | 32.5
96 | -31 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.9 | 32.6 | 32.5
97 | -30 | 23.3 | 34.6 | 30 | 34.7 | 39.1 | 36.4 | 35 | 38.9 | 32.6 | 32.5
98 | -29 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.8 | 32.6 | 32.5
99 | -28 | 23.3 | 34.6 | 30 | 34.7 | 39 | 36.4 | 35 | 38.8 | 32.6 | 32.5
100 | -27 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.8 | 32.6 | 32.5
101 | -26 | 23.3 | 34.6 | 30 | 34.6 | 39.1 | 36.4 | 35 | 38.8 | 32.6 | 32.5
102 | -25 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.4 | 35 | 38.9 | 32.6 | 32.4
103 | -24 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.9 | 32.6 | 32.5
104 | -23 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 39 | 32.6 | 32.5
105 | -22 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.4 | 35 | 38.9 | 32.6 | 32.4
106 | -21 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 39 | 32.6 | 32.4
107 | -20 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 39 | 32.6 | 32.5
108 | -19 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.9 | 32.6 | 32.4
109 | -18 | 23.3 | 34.6 | 30.1 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.5
110 | -17 | 23.3 | 34.6 | 30 | 34.6 | 39 | 36.4 | 35 | 38.9 | 32.6 | 32.4
111 | -16 | 23.3 | 34.6 | 30.1 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
112 | -15 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
113 | -14 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
114 | -13 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
115 | -12 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
116 | -11 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
117 | -10 | 23.3 | 34.6 | 30.1 | 34.6 | 39 | 36.3 | 35 | 38.9 | 32.6 | 32.4
118 | -9 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
119 | -8 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
120 | -7 | 23.3 | 34.5 | 30.1 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
121 | -6 | 23.3 | 34.6 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
122 | -5 | 23.3 | 34.5 | 30 | 34.6 | 38.9 | 36.3 | 35 | 38.9 | 32.6 | 32.4
123 | -4 | 23.3 | 34.7 | 29.8 | 34.7 | 39.1 | 36.4 | 35 | 38.9 | 32.6 | 32.4
124 | -3 | 23.3 | 35.4 | 28.4 | 35.1 | 40.5 | 37 | 34.8 | 38.8 | 32.5 | 32.4
125 | -2 | 23.3 | 35.7 | 27.9 | 35.3 | 41.1 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
126 | -1 | 23.6 | 35.7 | 27.9 | 35.3 | 41.1 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
127 | 0 | 24.4 | 35.7 | 27.8 | 35.3 | 41.2 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
128 | 1 | 25.7 | 35.7 | 27.9 | 35.3 | 41.2 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
129 | 2 | 27.7 | 35.7 | 27.9 | 35.3 | 41.1 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
130 | 3 | 30.1 | 35.8 | 27.7 | 35.4 | 41.4 | 37.3 | 34.7 | 38.7 | 32.5 | 32.3
131 | 4 | 32.9 | 35.8 | 27.8 | 35.4 | 41.2 | 37.3 | 34.7 | 38.7 | 32.5 | 32.3
132 | 5 | 36 | 35.9 | 27.7 | 35.4 | 41.4 | 37.3 | 34.7 | 38.7 | 32.5 | 32.3
133 | 6 | 39.6 | 35.9 | 27.8 | 35.4 | 41.3 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
134 | 7 | 43.3 | 35.9 | 27.8 | 35.5 | 41.3 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
135 | 8 | 47.3 | 35.9 | 27.9 | 35.4 | 41.4 | 37.3 | 34.7 | 38.7 | 32.5 | 32.3
136 | 9 | 51.6 | 35.9 | 28 | 35.5 | 41.3 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
137 | 10 | 56 | 35.9 | 28 | 35.5 | 41.2 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
138 | 11 | 60.6 | 35.9 | 28.1 | 35.5 | 41.2 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
139 | 12 | 65.3 | 36 | 28.2 | 35.5 | 41.3 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
140 | 13 | 70.2 | 36 | 28.2 | 35.6 | 41.3 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
141 | 14 | 75.3 | 36.1 | 28.3 | 35.6 | 41.1 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
142 | 15 | 80.4 | 36.1 | 28.4 | 35.7 | 41.1 | 37.3 | 34.7 | 38.7 | 32.4 | 32.3
143 | 16 | 85.8 | 36.1 | 28.6 | 35.7 | 41.2 | 37.2 | 34.7 | 38.7 | 32.4 | 32.3
144 | 17 | 91.2 | 36.2 | 28.7 | 35.8 | 41.3 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
145 | 18 | 96.7 | 36.3 | 28.9 | 35.8 | 41.1 | 37.2 | 34.7 | 38.6 | 32.4 | 32.3
146 | 19 | 102.3 | 36.3 | 29 | 35.9 | 41.1 | 37.2 | 34.7 | 38.6 | 32.4 | 32.3
147 | 20 | 107.9 | 36.4 | 29.2 | 35.9 | 41.3 | 37.2 | 34.7 | 38.6 | 32.4 | 32.3
148 | 21 | 113.6 | 36.5 | 29.3 | 36 | 41.2 | 37.2 | 34.7 | 38.6 | 32.4 | 32.3
149 | 22 | 119.5 | 36.6 | 29.5 | 36.1 | 41.2 | 37.2 | 34.7 | 38.6 | 32.4 | 32.3
150 | 23 | 125.4 | 36.7 | 29.7 | 36.2 | 41.2 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
151 | 24 | 131.4 | 36.8 | 29.9 | 36.3 | 41.2 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
152 | 25 | 137.3 | 36.9 | 30.1 | 36.4 | 41.3 | 37.3 | 34.7 | 38.6 | 32.5 | 32.3
153 | 26 | 143.3 | 37 | 30.3 | 36.5 | 41.3 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
154 | 27 | 149.3 | 37.1 | 30.6 | 36.6 | 41.2 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
155 | 28 | 155.3 | 37.2 | 30.8 | 36.7 | 41.1 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
156 | 29 | 161.3 | 37.4 | 31.1 | 36.9 | 41.2 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
157 | 30 | 167.3 | 37.5 | 31.5 | 37 | 41 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
158 | 31 | 173.4 | 37.6 | 31.8 | 37.1 | 41.2 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
159 | 32 | 179.5 | 37.8 | 32.1 | 37.3 | 41.1 | 37.2 | 34.7 | 38.7 | 32.5 | 32.3
160 | 33 | 185.6 | 38 | 32.4 | 37.4 | 41.2 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
161 | 34 | 191.7 | 38.2 | 32.7 | 37.6 | 41.3 | 37.2 | 34.7 | 38.6 | 32.5 | 32.3
162 | 35 | 197.7 | 38.4 | 33 | 37.8 | 41.3 | 37.3 | 34.6 | 38.6 | 32.5 | 32.3
163 | 36 | 203.8 | 38.6 | 33.4 | 38 | 41.3 | 37.3 | 34.6 | 38.7 | 32.5 | 32.3
164 | 37 | 210 | 38.8 | 33.8 | 38.2 | 41.2 | 37.2 | 34.6 | 38.7 | 32.5 | 32.3
165 | 38 | 216.1 | 39 | 34.1 | 38.4 | 41.3 | 37.3 | 34.6 | 38.7 | 32.5 | 32.3
166 | 39 | 222.2 | 39.2 | 34.5 | 38.6 | 41.3 | 37.2 | 34.6 | 38.7 | 32.5 | 32.3
167 | 40 | 228.3 | 39.5 | 35 | 38.8 | 41.4 | 37.3 | 34.6 | 38.7 | 32.6 | 32.3
168 | 41 | 234.4 | 39.7 | 35.7 | 39 | 41.3 | 37.2 | 34.6 | 38.7 | 32.6 | 32.3
169 | 42 | 240.5 | 39.9 | 36.2 | 39.3 | 41.3 | 37.3 | 34.6 | 38.6 | 32.6 | 32.3
170 | 43 | 246.7 | 40.2 | 36.5 | 39.5 | 41.3 | 37.3 | 34.6 | 38.5 | 32.6 | 32.3
171 | 44 | 252.7 | 40.5 | 36.9 | 39.8 | 41.2 | 37.3 | 34.6 | 38.5 | 32.6 | 32.3
172 | 45 | 258.7 | 40.8 | 37.5 | 40.1 | 41.3 | 37.3 | 34.6 | 38.5 | 32.6 | 32.3
173 | 46 | 264.8 | 41.1 | 37.9 | 40.4 | 41.3 | 37.3 | 34.6 | 38.5 | 32.6 | 32.3
174 | 47 | 270.9 | 41.4 | 38.4 | 40.6 | 41.3 | 37.3 | 34.6 | 38.6 | 32.7 | 32.3
175 | 48 | 276.9 | 41.7 | 38.9 | 40.9 | 41.3 | 37.3 | 34.6 | 38.6 | 32.7 | 32.3
176 | 49 | 283 | 42.1 | 39.4 | 41.3 | 41.4 | 37.3 | 34.6 | 38.6 | 32.7 | 32.3
177 | 50 | 289 | 42.4 | 40 | 41.6 | 41.3 | 37.3 | 34.6 | 38.5 | 32.7 | 32.3
178 | 51 | 295.1 | 42.8 | 40.7 | 41.9 | 41.6 | 37.3 | 34.6 | 38.5 | 32.7 | 32.3
179 | 52 | 301.1 | 43.1 | 41.4 | 42.3 | 41.3 | 37.3 | 34.6 | 38.6 | 32.8 | 32.3
180 | 53 | 307.1 | 43.5 | 41.9 | 42.7 | 41.4 | 37.4 | 34.6 | 38.6 | 32.8 | 32.2
181 | 54 | 313 | 43.9 | 42.6 | 43.1 | 41.3 | 37.4 | 34.6 | 38.6 | 32.8 | 32.3
182 | 55 | 319 | 44.4 | 43.3 | 43.5 | 41.3 | 37.4 | 34.6 | 38.6 | 32.8 | 32.3
183 | 56 | 325 | 44.8 | 44.1 | 43.8 | 41.5 | 37.4 | 34.6 | 38.5 | 32.9 | 32.3
184 | 57 | 330.9 | 45.2 | 44.9 | 44.3 | 41.4 | 37.4 | 34.6 | 38.5 | 32.9 | 32.3
185 | 58 | 336.8 | 45.6 | 45.6 | 44.7 | 41.5 | 37.4 | 34.6 | 38.6 | 32.9 | 32.3
186 | 59 | 342.6 | 46.1 | 46.4 | 45.1 | 41.6 | 37.4 | 34.6 | 38.5 | 33 | 32.3
187 | 60 | 348.4 | 46.6 | 47 | 45.6 | 41.7 | 37.5 | 34.6 | 38.5 | 33 | 32.3
188 | 61 | 354.2 | 47 | 48.1 | 46.1 | 41.6 | 37.5 | 34.6 | 38.4 | 33 | 32.3
189 | 62 | 359.9 | 47.5 | 48.9 | 46.5 | 41.5 | 37.5 | 34.6 | 38.4 | 33.1 | 32.3
190 | 63 | 365.5 | 48 | 49.7 | 47.1 | 41.6 | 37.5 | 34.6 | 38.4 | 33.1 | 32.3
191 | 64 | 371.2 | 48.5 | 50.6 | 47.6 | 41.6 | 37.5 | 34.6 | 38.4 | 33.1 | 32.3
192 | 65 | 376.8 | 49.1 | 51.4 | 48.1 | 41.6 | 37.5 | 34.6 | 38.4 | 33.2 | 32.3
193 | 66 | 382.3 | 49.7 | 52.4 | 48.6 | 41.7 | 37.6 | 34.6 | 38.5 | 33.2 | 32.3
194 | 67 | 387.9 | 50.3 | 53.3 | 49.2 | 41.7 | 37.6 | 34.6 | 38.5 | 33.3 | 32.3
195 | 68 | 393.5 | 50.8 | 54.2 | 49.7 | 41.7 | 37.6 | 34.6 | 38.4 | 33.3 | 32.3
196 | 69 | 399 | 51.4 | 55.3 | 50.3 | 41.8 | 37.7 | 34.6 | 38.4 | 33.4 | 32.3
197 | 70 | 404.4 | 52 | 56.4 | 50.9 | 41.8 | 37.7 | 34.6 | 38.4 | 33.4 | 32.3
198 | 71 | 409.8 | 52.7 | 57.3 | 51.5 | 41.9 | 37.7 | 34.6 | 38.5 | 33.5 | 32.3
199 | 72 | 415.2 | 53.3 | 58.3 | 52.1 | 42 | 37.8 | 34.6 | 38.5 | 33.5 | 32.3
200 | 73 | 420.6 | 54 | 59.4 | 52.8 | 42.1 | 37.8 | 34.6 | 38.5 | 33.6 | 32.3
201 | 74 | 426 | 54.7 | 60.4 | 53.5 | 42.1 | 37.9 | 34.6 | 38.5 | 33.6 | 32.3
202 | 75 | 431.2 | 55.4 | 61.6 | 54.2 | 42.1 | 37.9 | 34.6 | 38.6 | 33.7 | 32.4
203 | 76 | 436.4 | 56.1 | 62.7 | 54.9 | 42.1 | 37.9 | 34.6 | 38.6 | 33.8 | 32.4
204 | 77 | 441.6 | 56.9 | 63.9 | 55.6 | 42.3 | 38 | 34.6 | 38.6 | 33.8 | 32.4
205 | 78 | 446.7 | 57.7 | 65.2 | 56.3 | 42.4 | 38 | 34.6 | 38.6 | 33.9 | 32.4
206 | 79 | 451.9 | 58.5 | 66.4 | 57.1 | 42.3 | 38.1 | 34.6 | 38.6 | 34 | 32.4
207 | 80 | 457 | 59.3 | 67.5 | 57.8 | 42.5 | 38.1 | 34.6 | 38.6 | 34.1 | 32.4
208 | 81 | 462.1 | 60.1 | 68.9 | 58.6 | 42.4 | 38.1 | 34.6 | 38.7 | 34.1 | 32.4
209 | 82 | 467.1 | 60.9 | 70.3 | 59.4 | 42.4 | 38.2 | 34.6 | 38.7 | 34.2 | 32.4
210 | 83 | 472.1 | 61.8 | 71.8 | 60.2 | 42.5 | 38.3 | 34.6 | 38.7 | 34.3 | 32.4
211 | 84 | 477 | 62.7 | 73 | 61.1 | 42.6 | 38.3 | 34.6 | 38.7 | 34.4 | 32.4
212 | 85 | 481.9 | 63.4 | 74.6 | 61.8 | 42.5 | 38.3 | 34.7 | 38.8 | 34.5 | 32.5
213 | 86 | 486.8 | 64.2 | 76 | 62.7 | 42.6 | 38.3 | 34.7 | 38.8 | 34.6 | 32.5
214 | 87 | 491.4 | 65.2 | 77.3 | 63.6 | 42.8 | 38.4 | 34.7 | 38.8 | 34.6 | 32.5
215 | 88 | 495.7 | 66.1 | 78.7 | 64.5 | 42.8 | 38.5 | 34.7 | 38.8 | 34.7 | 32.5
216 | 89 | 499.5 | 67 | 80.1 | 65.4 | 42.9 | 38.6 | 34.7 | 38.8 | 34.8 | 32.5
217 | 90 | 502.9 | 68.1 | 81.3 | 66.3 | 43.2 | 38.7 | 34.7 | 38.7 | 34.9 | 32.6
218 | 91 | 506.2 | 69 | 82.5 | 67.3 | 43.3 | 38.8 | 34.7 | 38.8 | 35 | 32.6
219 | 92 | 509.2 | 70 | 83.8 | 68.1 | 43.4 | 38.9 | 34.7 | 38.8 | 35.2 | 32.6
220 | 93 | 512.1 | 71 | 85.2 | 69.1 | 43.5 | 39 | 34.7 | 38.8 | 35.2 | 32.6
221 | 94 | 514.9 | 72 | 86.6 | 70 | 43.8 | 39.1 | 34.7 | 38.7 | 35.4 | 32.6
222 | 95 | 517.6 | 72.9 | 88.2 | 71 | 43.6 | 39.1 | 34.7 | 38.7 | 35.5 | 32.7
223 | 96 | 520.1 | 73.7 | 90.1 | 71.8 | 43.6 | 39.1 | 34.7 | 38.8 | 35.6 | 32.7
224 | 97 | 522.3 | 74.7 | 91.3 | 72.8 | 43.7 | 39.2 | 34.7 | 38.8 | 35.7 | 32.7
225 | 98 | 524.2 | 75.6 | 92.6 | 73.6 | 43.6 | 39.3 | 34.7 | 38.8 | 35.9 | 32.8
226 | 99 | 525.9 | 76.3 | 94.5 | 74.4 | 43.1 | 39.1 | 34.8 | 38.9 | 36 | 32.8
227 | 100 | 527.3 | 76.9 | 96.5 | 75 | 42.5 | 38.9 | 34.9 | 39 | 36.2 | 32.9
228 | 101 | 528.3 | 77.8 | 97.6 | 76 | 42.6 | 39 | 34.9 | 39 | 36.3 | 32.9
229 | 102 | 529.1 | 78.9 | 98.7 | 77 | 42.9 | 39.2 | 34.9 | 39 | 36.4 | 32.9
230 | 103 | 529.7 | 79.9 | 99.9 | 78.1 | 43.2 | 39.4 | 34.9 | 39.1 | 36.6 | 33
231 | 104 | 530 | 80.8 | 101.3 | 78.9 | 43.2 | 39.4 | 34.9 | 39.1 | 36.7 | 33
232 | 105 | 530.3 | 81.8 | 102.4 | 79.8 | 43.5 | 39.6 | 34.9 | 39.1 | 36.9 | 33
233 | 106 | 530.3 | 82.7 | 103.6 | 80.8 | 43.6 | 39.7 | 34.9 | 39.1 | 37 | 33
234 | 107 | 530.3 | 83.6 | 104.8 | 81.7 | 43.7 | 39.8 | 35 | 39.1 | 37.2 | 33.1
235 | 108 | 530.1 | 84.6 | 106.1 | 82.6 | 44 | 40 | 35 | 39.1 | 37.3 | 33.1
236 | 109 | 529.8 | 85.5 | 107.3 | 83.5 | 44 | 40.1 | 35 | 39.1 | 37.5 | 33.2
237 | 110 | 529.5 | 86.3 | 108.5 | 84.3 | 44.2 | 40.2 | 35 | 39.1 | 37.6 | 33.2
238 | 111 | 529.1 | 87.3 | 109.6 | 85.2 | 44.4 | 40.4 | 35 | 39.1 | 37.8 | 33.2
239 | 112 | 528.7 | 88.3 | 110.8 | 86.1 | 44.6 | 40.6 | 35 | 39.1 | 37.9 | 33.3
240 | 113 | 528.3 | 89.1 | 112 | 86.9 | 44.8 | 40.7 | 35 | 39.2 | 38.1 | 33.3
241 | 114 | 527.7 | 90.1 | 112.8 | 87.9 | 45.3 | 40.9 | 35 | 39.2 | 38.3 | 33.4
242 | 115 | 527.2 | 91.1 | 113.8 | 88.8 | 45.6 | 41.1 | 35 | 39.2 | 38.4 | 33.4
243 | 116 | 526.7 | 92.1 | 114.9 | 89.8 | 46 | 41.3 | 35 | 39.2 | 38.6 | 33.4
244 | 117 | 526.2 | 93.1 | 115.8 | 90.6 | 46.4 | 41.6 | 35 | 39.2 | 38.8 | 33.5
245 | 118 | 525.8 | 94 | 116.7 | 91.5 | 46.6 | 41.7 | 35 | 39.1 | 38.9 | 33.5
246 | 119 | 525.3 | 94.9 | 117.8 | 92.4 | 46.8 | 41.9 | 35.1 | 39.2 | 39.1 | 33.6
247 | 120 | 525 | 95.8 | 118.8 | 93.3 | 47.3 | 42.1 | 35 | 39.2 | 39.3 | 33.6
248 | 121 | 524.7 | 96.8 | 119.9 | 94.2 | 47.5 | 42.3 | 35.1 | 39.2 | 39.5 | 33.7
249 | 122 | 524.4 | 97.7 | 121 | 95.1 | 47.9 | 42.5 | 35.1 | 39.3 | 39.6 | 33.7
250 | 123 | 524.2 | 98.6 | 122.1 | 96 | 47.9 | 42.6 | 35.1 | 39.3 | 39.8 | 33.8
251 | 124 | 524 | 99.5 | 123.2 | 96.9 | 48.3 | 42.8 | 35.1 | 39.4 | 40 | 33.8
252 | 125 | 523.8 | 100.4 | 124.2 | 97.8 | 48.5 | 43 | 35.1 | 39.5 | 40.2 | 33.9
253 | 126 | 523.7 | 101.2 | 125.3 | 98.5 | 48.8 | 43.2 | 35.2 | 39.5 | 40.4 | 33.9
254 | 127 | 523.7 | 102.1 | 126.4 | 99.4 | 49 | 43.4 | 35.2 | 39.5 | 40.6 | 34
255 | 128 | 523.6 | 103 | 127.6 | 100.3 | 49.3 | 43.6 | 35.2 | 39.6 | 40.8 | 34
256 | 129 | 523.7 | 103.8 | 128.6 | 101.1 | 49.2 | 43.7 | 35.3 | 39.7 | 41 | 34.1
257 | 130 | 523.7 | 104.7 | 129.8 | 102 | 49.5 | 43.9 | 35.3 | 39.7 | 41.2 | 34.1
258 | 131 | 523.9 | 105.6 | 131.1 | 102.8 | 49.7 | 44.1 | 35.3 | 39.8 | 41.3 | 34.2
259 | 132 | 524 | 106.5 | 132.4 | 103.7 | 49.8 | 44.2 | 35.4 | 39.8 | 41.6 | 34.2
260 | 133 | 524.2 | 107.3 | 133.4 | 104.4 | 50.2 | 44.4 | 35.4 | 39.8 | 41.8 | 34.3
261 | 134 | 524.4 | 108.2 | 134.4 | 105.3 | 50.4 | 44.6 | 35.4 | 39.9 | 42 | 34.4
262 | 135 | 524.6 | 109.1 | 135.5 | 106.2 | 50.6 | 44.8 | 35.5 | 40 | 42.2 | 34.4
263 | 136 | 524.9 | 110 | 136.4 | 107.1 | 51 | 45 | 35.5 | 39.9 | 42.4 | 34.5
264 | 137 | 525.2 | 110.8 | 137.5 | 107.9 | 51.1 | 45.2 | 35.5 | 40 | 42.6 | 34.6
265 | 138 | 525.5 | 111.7 | 138.6 | 108.9 | 51.4 | 45.4 | 35.6 | 40 | 42.8 | 34.6
266 | 139 | 525.8 | 112.6 | 139.7 | 109.6 | 51.6 | 45.6 | 35.6 | 40 | 43 | 34.7
267 | 140 | 526 | 113.5 | 140.8 | 110.5 | 51.9 | 45.8 | 35.7 | 40.1 | 43.2 | 34.7
268 | 141 | 526.3 | 114.4 | 142 | 111.4 | 52.1 | 46 | 35.7 | 40.1 | 43.5 | 34.8
269 | 142 | 526.5 | 115.2 | 143.2 | 112.2 | 52.3 | 46.2 | 35.8 | 40.2 | 43.7 | 34.9
270 | 143 | 526.7 | 116.1 | 144.3 | 113 | 52.5 | 46.4 | 35.8 | 40.3 | 43.9 | 34.9
271 | 144 | 526.9 | 117 | 145.4 | 113.9 | 52.7 | 46.6 | 35.8 | 40.4 | 44.1 | 35
272 | 145 | 527.2 | 117.8 | 146.6 | 114.8 | 52.9 | 46.8 | 35.9 | 40.4 | 44.4 | 35.1
273 | 146 | 527.4 | 118.6 | 147.6 | 115.6 | 53.1 | 47 | 35.9 | 40.4 | 44.6 | 35.2
274 | 147 | 527.6 | 119.5 | 148.8 | 116.5 | 53.4 | 47.2 | 36 | 40.4 | 44.8 | 35.2
275 | 148 | 527.8 | 120.4 | 149.8 | 117.3 | 53.9 | 47.5 | 36 | 40.5 | 45 | 35.3
276 | 149 | 528 | 121.2 | 151 | 118.1 | 53.9 | 47.6 | 36.1 | 40.6 | 45.3 | 35.4
277 | 150 | 528.1 | 122.1 | 152 | 119 | 54.1 | 47.9 | 36.1 | 40.7 | 45.5 | 35.5
278 | 151 | 528.2 | 122.9 | 153.2 | 119.8 | 54.4 | 48.1 | 36.2 | 40.7 | 45.7 | 35.5
279 | 152 | 528.3 | 123.8 | 154.3 | 120.6 | 54.6 | 48.3 | 36.3 | 40.8 | 46 | 35.6
280 | 153 | 528.4 | 124.6 | 155.4 | 121.4 | 54.9 | 48.5 | 36.3 | 40.8 | 46.2 | 35.7
281 | 154 | 528.4 | 125.5 | 156.3 | 122.3 | 55.3 | 48.8 | 36.3 | 40.8 | 46.5 | 35.8
282 | 155 | 528.5 | 126.4 | 157.3 | 123.1 | 55.5 | 49 | 36.4 | 40.9 | 46.7 | 35.8
283 | 156 | 528.6 | 127.2 | 158.6 | 124 | 55.8 | 49.2 | 36.5 | 41 | 46.9 | 35.9
284 | 157 | 528.7 | 128.1 | 159.9 | 124.8 | 56.1 | 49.4 | 36.5 | 41 | 47.2 | 36
285 | 158 | 528.8 | 128.9 | 160.8 | 125.7 | 56.3 | 49.6 | 36.6 | 41.1 | 47.4 | 36.1
286 | 159 | 528.8 | 129.7 | 161.8 | 126.4 | 56.5 | 49.9 | 36.7 | 41.2 | 47.7 | 36.2
287 | 160 | 528.9 | 130.5 | 162.7 | 127.2 | 56.8 | 50.1 | 36.7 | 41.3 | 47.9 | 36.3
288 | 161 | 528.9 | 131.3 | 163.8 | 128.1 | 57.1 | 50.3 | 36.8 | 41.4 | 48.2 | 36.3
289 | 162 | 528.9 | 132.2 | 164.8 | 128.9 | 57.3 | 50.5 | 36.9 | 41.5 | 48.4 | 36.4
290 | 163 | 528.9 | 133 | 165.8 | 129.7 | 57.7 | 50.8 | 36.9 | 41.5 | 48.7 | 36.5
291 | 164 | 528.8 | 133.9 | 166.8 | 130.6 | 58 | 51 | 37 | 41.6 | 48.9 | 36.6
292 | 165 | 528.8 | 134.7 | 167.9 | 131.4 | 58.3 | 51.3 | 37.1 | 41.7 | 49.2 | 36.7
293 | 166 | 528.8 | 135.6 | 168.9 | 132.1 | 58.5 | 51.5 | 37.1 | 41.8 | 49.4 | 36.8
294 | 167 | 528.8 | 136.4 | 169.9 | 133 | 58.9 | 51.8 | 37.2 | 41.8 | 49.7 | 36.9
295 | 168 | 528.8 | 137.2 | 170.9 | 133.8 | 59.1 | 52 | 37.3 | 41.9 | 50 | 37
296 | 169 | 528.7 | 138 | 172 | 134.6 | 59.3 | 52.3 | 37.3 | 42 | 50.2 | 37
297 | 170 | 528.7 | 138.9 | 172.9 | 135.4 | 59.8 | 52.5 | 37.4 | 42.1 | 50.5 | 37.1
298 | 171 | 528.6 | 139.7 | 173.9 | 136.2 | 60.1 | 52.8 | 37.5 | 42.3 | 50.8 | 37.2
299 | 172 | 528.6 | 140.5 | 174.8 | 137 | 60.5 | 53.1 | 37.5 | 42.4 | 51 | 37.3
300 | 173 | 528.7 | 141.3 | 175.9 | 137.8 | 60.7 | 53.3 | 37.6 | 42.5 | 51.3 | 37.4
301 | 174 | 528.8 | 142.1 | 176.9 | 138.6 | 61 | 53.5 | 37.7 | 42.5 | 51.5 | 37.5
302 | 175 | 528.9 | 143 | 178 | 139.4 | 61.3 | 53.8 | 37.8 | 42.6 | 51.8 | 37.6
303 | 176 | 529 | 143.8 | 179 | 140.2 | 61.6 | 54.1 | 37.9 | 42.7 | 52.1 | 37.7
304 | 177 | 529.1 | 144.6 | 180 | 141 | 62 | 54.3 | 38 | 42.8 | 52.4 | 37.8
305 | 178 | 529.2 | 145.4 | 181 | 141.8 | 62.3 | 54.6 | 38 | 42.9 | 52.6 | 37.9
306 | 179 | 529.2 | 146.2 | 182.1 | 142.6 | 62.6 | 54.8 | 38.1 | 43 | 52.9 | 38
307 | 180 | 529.4 | 146.9 | 183.2 | 143.3 | 62.7 | 55.1 | 38.2 | 43.1 | 53.2 | 38.1
308 | 181 | 529.4 | 147.8 | 184.1 | 144.1 | 63.2 | 55.4 | 38.3 | 43.3 | 53.5 | 38.2
309 | 182 | 529.5 | 148.5 | 185.1 | 144.9 | 63.4 | 55.6 | 38.4 | 43.4 | 53.7 | 38.3
310 | 183 | 529.5 | 149.3 | 186.1 | 145.7 | 63.7 | 55.9 | 38.5 | 43.5 | 54 | 38.4
311 | 184 | 529.6 | 150.1 | 187 | 146.5 | 64 | 56.1 | 38.6 | 43.5 | 54.3 | 38.5
312 | 185 | 529.6 | 150.9 | 188 | 147.3 | 64.4 | 56.4 | 38.7 | 43.6 | 54.6 | 38.7
313 | 186 | 529.7 | 151.7 | 189 | 148 | 64.8 | 56.7 | 38.8 | 43.7 | 54.9 | 38.8
314 | 187 | 529.7 | 152.5 | 190.1 | 148.8 | 65 | 57 | 38.9 | 43.9 | 55.2 | 38.9
315 | 188 | 529.7 | 153.3 | 191 | 149.6 | 65.3 | 57.2 | 39 | 44 | 55.4 | 39
316 | 189 | 529.7 | 154.1 | 192 | 150.4 | 65.8 | 57.5 | 39 | 44.1 | 55.7 | 39.1
317 | 190 | 529.7 | 154.8 | 193 | 151.2 | 66 | 57.8 | 39.2 | 44.2 | 56 | 39.2
318 | 191 | 529.7 | 155.6 | 193.9 | 151.9 | 66.3 | 58.1 | 39.3 | 44.4 | 56.3 | 39.3
319 | 192 | 529.8 | 156.4 | 194.9 | 152.7 | 66.7 | 58.4 | 39.4 | 44.5 | 56.6 | 39.4
320 | 193 | 529.8 | 157.2 | 196 | 153.4 | 66.9 | 58.6 | 39.5 | 44.7 | 56.9 | 39.5
321 | 194 | 529.8 | 157.9 | 196.9 | 154.2 | 67.2 | 58.9 | 39.6 | 44.8 | 57.2 | 39.6
322 | 195 | 529.8 | 158.7 | 197.9 | 155 | 67.6 | 59.2 | 39.7 | 44.9 | 57.5 | 39.8
323 | 196 | 529.9 | 159.5 | 198.9 | 155.8 | 68 | 59.5 | 39.8 | 45 | 57.8 | 39.9
324 | 197 | 530 | 160.3 | 199.8 | 156.5 | 68.3 | 59.8 | 39.9 | 45.1 | 58.1 | 40
325 | 198 | 530 | 161 | 200.9 | 157.2 | 68.6 | 60 | 40 | 45.2 | 58.4 | 40.1
326 | 199 | 530.1 | 161.8 | 201.8 | 158 | 69 | 60.4 | 40.1 | 45.3 | 58.7 | 40.2
327 | 200 | 530.1 | 162.6 | 202.7 | 158.8 | 69.5 | 60.7 | 40.2 | 45.4 | 59 | 40.4
328 | 201 | 530.1 | 163.3 | 203.7 | 159.5 | 69.8 | 61 | 40.3 | 45.6 | 59.2 | 40.5
329 | 202 | 530.1 | 164.1 | 204.6 | 160.3 | 70.2 | 61.3 | 40.4 | 45.7 | 59.6 | 40.6
330 | 203 | 530.1 | 164.9 | 205.5 | 161.1 | 70.5 | 61.5 | 40.6 | 45.8 | 59.9 | 40.7
331 | 204 | 530.1 | 165.7 | 206.4 | 161.8 | 70.9 | 61.9 | 40.7 | 45.9 | 60.2 | 40.9
332 | 205 | 530.2 | 166.4 | 207.5 | 162.5 | 71.2 | 62.1 | 40.8 | 46.1 | 60.5 | 41
333 | 206 | 530.2 | 167.1 | 208.4 | 163.3 | 71.6 | 62.4 | 40.9 | 46.2 | 60.8 | 41.1
334 | 207 | 530.2 | 167.8 | 209.3 | 164 | 71.9 | 62.7 | 41 | 46.4 | 61.1 | 41.2
335 | 208 | 530.1 | 168.6 | 210.3 | 164.8 | 72.3 | 63 | 41.2 | 46.5 | 61.4 | 41.4
336 | 209 | 530.2 | 169.4 | 211.3 | 165.5 | 72.6 | 63.3 | 41.3 | 46.6 | 61.7 | 41.5
337 | 210 | 530.1 | 170.1 | 212.2 | 166.3 | 73 | 63.6 | 41.4 | 46.8 | 62 | 41.6
338 | 211 | 530.1 | 170.8 | 213.1 | 167 | 73.3 | 63.9 | 41.5 | 47 | 62.3 | 41.7
339 | 212 | 530.1 | 171.6 | 213.9 | 167.8 | 73.8 | 64.2 | 41.7 | 47.1 | 62.6 | 41.9
340 | 213 | 530.1 | 172.3 | 214.9 | 168.5 | 74.1 | 64.5 | 41.8 | 47.3 | 62.9 | 42
341 | 214 | 530 | 173.1 | 215.8 | 169.2 | 74.5 | 64.8 | 41.9 | 47.4 | 63.2 | 42.1
342 | 215 | 530 | 173.8 | 216.8 | 170 | 75 | 65.2 | 42 | 47.5 | 63.6 | 42.3
343 | 216 | 530 | 174.6 | 217.7 | 170.7 | 75.3 | 65.5 | 42.2 | 47.7 | 63.9 | 42.4
344 | 217 | 530 | 175.4 | 218.5 | 171.5 | 75.8 | 65.8 | 42.3 | 47.8 | 64.2 | 42.5
345 | 218 | 530 | 176.1 | 219.4 | 172.3 | 76.1 | 66.1 | 42.4 | 47.9 | 64.5 | 42.7
346 | 219 | 530 | 176.9 | 220.3 | 173 | 76.5 | 66.4 | 42.6 | 48 | 64.8 | 42.8
347 | 220 | 530 | 177.6 | 221.2 | 173.7 | 76.9 | 66.8 | 42.7 | 48.1 | 65.1 | 43
348 | 221 | 529.9 | 178.3 | 222.3 | 174.4 | 77.1 | 67 | 42.9 | 48.2 | 65.5 | 43.1
349 | 222 | 530 | 179.1 | 223 | 175.1 | 77.6 | 67.4 | 43 | 48.4 | 65.8 | 43.2
350 | 223 | 530 | 179.8 | 223.9 | 175.9 | 78 | 67.7 | 43.1 | 48.6 | 66.1 | 43.4
351 | 224 | 530 | 180.5 | 224.8 | 176.6 | 78.3 | 68 | 43.3 | 48.7 | 66.4 | 43.5
352 | 225 | 530.1 | 181.3 | 225.7 | 177.3 | 78.7 | 68.4 | 43.4 | 48.9 | 66.8 | 43.7
353 | 226 | 530.1 | 182 | 226.6 | 178 | 79.3 | 68.7 | 43.5 | 49 | 67.1 | 43.8
354 | 227 | 530 | 182.7 | 227.5 | 178.8 | 79.5 | 69 | 43.7 | 49.2 | 67.4 | 44
355 | 228 | 530 | 183.4 | 228.4 | 179.5 | 80 | 69.3 | 43.8 | 49.3 | 67.8 | 44.1
356 | 229 | 530 | 184.2 | 229.3 | 180.2 | 80.3 | 69.6 | 44 | 49.5 | 68.1 | 44.3
357 | 230 | 530 | 184.9 | 230.2 | 181 | 80.7 | 70 | 44.1 | 49.6 | 68.4 | 44.4
358 | 231 | 530 | 185.6 | 231 | 181.7 | 81 | 70.3 | 44.3 | 49.7 | 68.7 | 44.6
359 | 232 | 529.9 | 186.3 | 231.8 | 182.4 | 81.5 | 70.6 | 44.4 | 49.9 | 69.1 | 44.7
360 | 233 | 529.9 | 187.1 | 232.6 | 183 | 81.9 | 71 | 44.6 | 50.1 | 69.4 | 44.8
361 | 234 | 529.9 | 187.8 | 233.5 | 183.7 | 82.3 | 71.3 | 44.7 | 50.3 | 69.7 | 45
362 | 235 | 529.9 | 188.5 | 234.4 | 184.4 | 82.7 | 71.6 | 44.9 | 50.4 | 70.1 | 45.2
363 | 236 | 529.9 | 189.2 | 235.3 | 185.1 | 83.1 | 72 | 45 | 50.6 | 70.4 | 45.3
364 | 237 | 529.8 | 190 | 236.1 | 185.9 | 83.5 | 72.3 | 45.2 | 50.8 | 70.7 | 45.5
365 | 238 | 529.7 | 190.7 | 237 | 186.6 | 83.9 | 72.6 | 45.4 | 51 | 71.1 | 45.6
366 | 239 | 529.7 | 191.4 | 237.8 | 187.3 | 84.4 | 73 | 45.5 | 51.2 | 71.4 | 45.8
367 | 240 | 529.8 | 192.1 | 238.6 | 188 | 84.8 | 73.3 | 45.7 | 51.4 | 71.7 | 45.9
368 | 241 | 529.8 | 192.8 | 239.4 | 188.7 | 85.2 | 73.6 | 45.8 | 51.6 | 72.1 | 46.1
369 | 242 | 529.8 | 193.5 | 240.3 | 189.4 | 85.5 | 74 | 46 | 51.7 | 72.4 | 46.2
370 | 243 | 529.8 | 194.2 | 241.1 | 190.2 | 85.9 | 74.3 | 46.2 | 51.9 | 72.8 | 46.4
371 | 244 | 529.8 | 194.9 | 242 | 190.8 | 86.3 | 74.7 | 46.3 | 52 | 73.1 | 46.6
372 | 245 | 529.8 | 195.6 | 242.7 | 191.5 | 86.8 | 75 | 46.5 | 52.1 | 73.5 | 46.7
373 | 246 | 529.7 | 196.4 | 243.6 | 192.3 | 87.3 | 75.4 | 46.6 | 52.3 | 73.8 | 46.9
374 | 247 | 529.7 | 197 | 244.5 | 193 | 87.6 | 75.7 | 46.8 | 52.4 | 74.2 | 47.1
375 | 248 | 529.6 | 197.7 | 245.3 | 193.6 | 87.9 | 76 | 47 | 52.6 | 74.5 | 47.2
376 | 249 | 529.7 | 198.4 | 246.2 | 194.3 | 88.4 | 76.4 | 47.1 | 52.8 | 74.9 | 47.4
377 | 250 | 529.7 | 199.1 | 247.1 | 194.9 | 88.8 | 76.7 | 47.3 | 53 | 75.2 | 47.6
378 | 251 | 529.8 | 199.8 | 247.8 | 195.6 | 89.3 | 77.1 | 47.5 | 53.1 | 75.6 | 47.7
379 | 252 | 529.9 | 200.4 | 248.7 | 196.4 | 89.5 | 77.4 | 47.7 | 53.3 | 75.9 | 47.9
380 | 253 | 529.9 | 201.1 | 249.5 | 197.1 | 89.9 | 77.7 | 47.8 | 53.5 | 76.3 | 48.1
381 | 254 | 529.9 | 201.8 | 250.4 | 197.8 | 90.4 | 78.1 | 48 | 53.6 | 76.6 | 48.3
382 | 255 | 530 | 202.5 | 251.2 | 198.5 | 90.7 | 78.4 | 48.2 | 53.9 | 77 | 48.4
383 | 256 | 530 | 203.2 | 252 | 199.1 | 91 | 78.7 | 48.4 | 54.1 | 77.3 | 48.6
384 | 257 | 530 | 203.9 | 252.8 | 199.8 | 91.6 | 79.1 | 48.6 | 54.3 | 77.7 | 48.8
385 | 258 | 530 | 204.6 | 253.6 | 200.4 | 92.1 | 79.4 | 48.7 | 54.5 | 78.1 | 49
386 | 259 | 529.9 | 205.3 | 254.3 | 201.1 | 92.6 | 79.8 | 48.9 | 54.6 | 78.4 | 49.1
387 | 260 | 529.8 | 206 | 255.1 | 201.9 | 93 | 80.2 | 49.1 | 54.8 | 78.8 | 49.3
388 | 261 | 529.8 | 206.6 | 255.9 | 202.5 | 93.4 | 80.5 | 49.3 | 55 | 79.1 | 49.5
389 | 262 | 529.8 | 207.3 | 256.7 | 203.2 | 93.8 | 80.9 | 49.4 | 55.2 | 79.5 | 49.7
390 | 263 | 529.7 | 208 | 257.5 | 203.8 | 94.3 | 81.2 | 49.6 | 55.3 | 79.9 | 49.8
391 | 264 | 529.7 | 208.7 | 258.3 | 204.5 | 94.7 | 81.6 | 49.8 | 55.6 | 80.2 | 50
392 | 265 | 529.7 | 209.4 | 259.1 | 205.1 | 95.1 | 82 | 50 | 55.7 | 80.6 | 50.2
393 | 266 | 529.7 | 210.1 | 259.8 | 205.9 | 95.5 | 82.3 | 50.2 | 55.9 | 81 | 50.4
394 | 267 | 529.6 | 210.7 | 260.7 | 206.5 | 95.9 | 82.7 | 50.4 | 56.1 | 81.3 | 50.6
395 | 268 | 529.6 | 211.4 | 261.5 | 207.2 | 96.4 | 83 | 50.6 | 56.3 | 81.7 | 50.7
396 | 269 | 529.5 | 212.1 | 262.2 | 207.8 | 96.8 | 83.4 | 50.8 | 56.5 | 82.1 | 50.9
397 | 270 | 529.5 | 212.7 | 263 | 208.5 | 97.2 | 83.7 | 51 | 56.6 | 82.5 | 51.1
398 | 271 | 529.5 | 213.4 | 263.7 | 209.1 | 97.6 | 84.1 | 51.1 | 56.8 | 82.8 | 51.3
399 | 272 | 529.4 | 214 | 264.5 | 209.8 | 98 | 84.5 | 51.4 | 57 | 83.2 | 51.5
400 | 273 | 529.3 | 214.7 | 265.3 | 210.5 | 98.4 | 84.8 | 51.5 | 57.3 | 83.6 | 51.7
401 | 274 | 529.3 | 215.4 | 266 | 211.1 | 99.1 | 85.2 | 51.7 | 57.5 | 84 | 51.9
402 | 275 | 529.3 | 216 | 266.8 | 211.8 | 99.4 | 85.6 | 51.9 | 57.7 | 84.3 | 52
403 | 276 | 529.3 | 216.7 | 267.6 | 212.5 | 99.9 | 85.9 | 52.1 | 57.9 | 84.7 | 52.2
404 | 277 | 529.3 | 217.3 | 268.3 | 213.2 | 100.4 | 86.3 | 52.3 | 58.2 | 85.1 | 52.4
405 | 278 | 529.3 | 218 | 269.1 | 213.8 | 100.8 | 86.7 | 52.5 | 58.4 | 85.5 | 52.6
406 | 279 | 529.4 | 218.5 | 269.9 | 214.4 | 101.1 | 87 | 52.8 | 58.6 | 85.9 | 52.8
407 | 280 | 529.4 | 219.2 | 270.7 | 215 | 101.6 | 87.4 | 53 | 58.8 | 86.3 | 53
408 | 281 | 529.5 | 219.9 | 271.4 | 215.7 | 101.9 | 87.8 | 53.2 | 59 | 86.6 | 53.2
409 | 282 | 529.5 | 220.5 | 272.2 | 216.3 | 102.4 | 88.1 | 53.4 | 59.2 | 87 | 53.4
410 | 283 | 529.6 | 221.1 | 272.9 | 217 | 102.8 | 88.5 | 53.6 | 59.4 | 87.4 | 53.6
411 | 284 | 529.6 | 221.8 | 273.6 | 217.6 | 103.3 | 88.9 | 53.8 | 59.5 | 87.8 | 53.8
412 | 285 | 529.6 | 222.4 | 274.5 | 218.2 | 103.8 | 89.2 | 54 | 59.8 | 88.2 | 54
413 | 286 | 529.6 | 223.1 | 275.2 | 218.8 | 104.2 | 89.6 | 54.2 | 60 | 88.6 | 54.1
414 | 287 | 529.6 | 223.7 | 276 | 219.5 | 104.7 | 90 | 54.4 | 60.2 | 89 | 54.3
415 | 288 | 529.6 | 224.3 | 276.7 | 220.2 | 105 | 90.4 | 54.7 | 60.4 | 89.4 | 54.5
416 | 289 | 529.7 | 225 | 277.5 | 220.8 | 105.5 | 90.8 | 54.9 | 60.6 | 89.8 | 54.7
417 | 290 | 529.7 | 225.6 | 278.2 | 221.4 | 106 | 91.1 | 55.1 | 60.8 | 90.1 | 54.9
418 | 291 | 529.7 | 226.2 | 278.9 | 222 | 106.4 | 91.5 | 55.3 | 61 | 90.5 | 55.1
419 | 292 | 529.7 | 226.9 | 279.6 | 222.7 | 106.9 | 91.9 | 55.5 | 61.2 | 90.9 | 55.3
420 | 293 | 529.7 | 227.5 | 280.3 | 223.3 | 107.4 | 92.3 | 55.8 | 61.4 | 91.3 | 55.5
421 | 294 | 529.7 | 228.1 | 281.1 | 223.8 | 107.7 | 92.6 | 56 | 61.6 | 91.7 | 55.7
422 | 295 | 529.7 | 228.8 | 281.8 | 224.5 | 108.3 | 93 | 56.2 | 61.8 | 92.1 | 56
423 | 296 | 529.7 | 229.4 | 282.6 | 225.2 | 108.8 | 93.4 | 56.4 | 62 | 92.5 | 56.2
424 | 297 | 529.8 | 230 | 283.3 | 225.8 | 109.3 | 93.8 | 56.7 | 62.2 | 92.9 | 56.4
425 | 298 | 529.8 | 230.6 | 283.9 | 226.5 | 109.6 | 94.2 | 56.9 | 62.5 | 93.3 | 56.6
426 | 299 | 529.7 | 231.3 | 284.6 | 227.1 | 110.2 | 94.6 | 57.1 | 62.7 | 93.7 | 56.8
427 | 300 | 529.7 | 231.9 | 285.4 | 227.6 | 110.6 | 95 | 57.3 | 63 | 94.1 | 57
428 | 301 | 529.8 | 232.5 | 286.1 | 228.3 | 111.1 | 95.4 | 57.6 | 63.2 | 94.5 | 57.2
429 | 302 | 529.8 | 233.1 | 286.9 | 228.9 | 111.4 | 95.7 | 57.8 | 63.4 | 94.9 | 57.4
430 | 303 | 529.8 | 233.8 | 287.5 | 229.6 | 112 | 96.1 | 58 | 63.6 | 95.3 | 57.6
431 | 304 | 529.8 | 234.3 | 288.3 | 230.2 | 112.1 | 96.5 | 58.3 | 63.9 | 95.7 | 57.8
432 | 305 | 529.8 | 235 | 288.9 | 230.8 | 112.9 | 96.9 | 58.5 | 64.2 | 96.1 | 58
433 | 306 | 529.8 | 235.6 | 289.7 | 231.4 | 113.3 | 97.3 | 58.7 | 64.5 | 96.5 | 58.3
434 | 307 | 529.8 | 236.2 | 290.3 | 232 | 113.7 | 97.7 | 59 | 64.7 | 96.9 | 58.5
435 | 308 | 529.8 | 236.8 | 291.1 | 232.6 | 114.2 | 98.1 | 59.2 | 65 | 97.3 | 58.7
436 | 309 | 529.8 | 237.4 | 291.8 | 233.1 | 114.7 | 98.4 | 59.5 | 65.3 | 97.8 | 58.9
437 | 310 | 529.8 | 237.9 | 292.6 | 233.7 | 115 | 98.7 | 59.7 | 65.6 | 98.2 | 59.1
438 | 311 | 529.8 | 238.4 | 293.6 | 234.2 | 115.2 | 99 | 60 | 65.9 | 98.6 | 59.3
439 | 312 | 529.8 | 239.2 | 293.9 | 234.9 | 116 | 99.6 | 60.2 | 66.1 | 99 | 59.5
440 | 313 | 529.7 | 239.8 | 294.6 | 235.6 | 116.5 | 100 | 60.4 | 66.3 | 99.4 | 59.8
441 | 314 | 529.7 | 240.4 | 295.2 | 236.2 | 116.9 | 100.4 | 60.7 | 66.5 | 99.8 | 60
442 | 315 | 529.7 | 241 | 296 | 236.7 | 117.5 | 100.8 | 60.9 | 66.7 | 100.2 | 60.2
443 | 316 | 529.7 | 241.6 | 296.6 | 237.4 | 117.9 | 101.2 | 61.2 | 66.9 | 100.6 | 60.4
444 | 317 | 529.6 | 242.2 | 297.3 | 238 | 118.4 | 101.5 | 61.4 | 67.2 | 101 | 60.7
445 | 318 | 529.6 | 242.8 | 297.9 | 238.6 | 118.8 | 101.9 | 61.7 | 67.5 | 101.4 | 60.9
446 | 319 | 529.5 | 243.4 | 298.5 | 239.1 | 119.2 | 102.3 | 61.9 | 67.8 | 101.8 | 61.1
447 | 320 | 529.5 | 243.9 | 299.3 | 239.7 | 119.7 | 102.7 | 62.2 | 68.1 | 102.2 | 61.3
448 | 321 | 529.5 | 244.5 | 300 | 240.3 | 120.1 | 103.1 | 62.4 | 68.3 | 102.7 | 61.5
449 | 322 | 529.4 | 245.1 | 300.6 | 240.9 | 120.6 | 103.5 | 62.7 | 68.5 | 103.1 | 61.7
450 | 323 | 529.4 | 245.7 | 301.2 | 241.5 | 120.9 | 103.9 | 62.9 | 68.8 | 103.5 | 62
451 | 324 | 529.3 | 246.3 | 301.9 | 242.1 | 121.6 | 104.3 | 63.2 | 69 | 103.9 | 62.2
452 | 325 | 529.3 | 246.9 | 302.6 | 242.7 | 122.1 | 104.7 | 63.4 | 69.3 | 104.3 | 62.4
453 | 326 | 529.2 | 247.4 | 303.3 | 243.3 | 122.6 | 105.1 | 63.7 | 69.5 | 104.7 | 62.7
454 | 327 | 529.1 | 248 | 304 | 243.8 | 122.9 | 105.4 | 63.9 | 69.8 | 105.1 | 62.9
455 | 328 | 529 | 248.6 | 304.6 | 244.4 | 123.5 | 105.8 | 64.2 | 70.1 | 105.5 | 63.1
456 | 329 | 529 | 249.2 | 305.2 | 245 | 124 | 106.2 | 64.4 | 70.4 | 106 | 63.3
457 | 330 | 528.9 | 249.8 | 305.8 | 245.6 | 124.6 | 106.7 | 64.7 | 70.7 | 106.4 | 63.6
458 | 331 | 528.9 | 250.3 | 306.5 | 246.2 | 125 | 107 | 65 | 71 | 106.8 | 63.8
459 | 332 | 528.9 | 250.9 | 307.1 | 246.8 | 125.6 | 107.4 | 65.2 | 71.2 | 107.2 | 64
460 | 333 | 528.8 | 251.5 | 307.7 | 247.4 | 126 | 107.8 | 65.5 | 71.6 | 107.6 | 64.3
461 | 334 | 528.8 | 252.1 | 308.3 | 248 | 126.3 | 108.2 | 65.7 | 71.9 | 108 | 64.5
462 | 335 | 528.8 | 252.6 | 309 | 248.5 | 126.7 | 108.6 | 66 | 72.2 | 108.5 | 64.7
463 | 336 | 528.9 | 253.2 | 309.7 | 249.1 | 127.3 | 109 | 66.3 | 72.4 | 108.9 | 65
464 | 337 | 528.8 | 253.7 | 310.3 | 249.6 | 127.8 | 109.4 | 66.5 | 72.7 | 109.3 | 65.2
465 | 338 | 528.8 | 254.3 | 310.9 | 250.2 | 128.3 | 109.7 | 66.8 | 73 | 109.7 | 65.4
466 | 339 | 528.8 | 254.8 | 311.5 | 250.8 | 128.7 | 110.1 | 67.1 | 73.3 | 110.1 | 65.7
467 | 340 | 528.7 | 255.4 | 312.2 | 251.4 | 129.2 | 110.5 | 67.3 | 73.6 | 110.6 | 65.9
468 | 341 | 528.7 | 256 | 312.7 | 251.9 | 129.8 | 110.9 | 67.6 | 73.9 | 111 | 66.1
469 | 342 | 528.7 | 256.6 | 313.4 | 252.4 | 130.3 | 111.3 | 67.8 | 74.2 | 111.4 | 66.4
470 | 343 | 528.7 | 257.1 | 314.1 | 253 | 130.6 | 111.7 | 68.1 | 74.4 | 111.8 | 66.6
471 | 344 | 528.7 | 257.6 | 314.7 | 253.5 | 131.1 | 112.1 | 68.4 | 74.7 | 112.3 | 66.9
472 | 345 | 528.7 | 258.2 | 315.3 | 254.1 | 131.6 | 112.5 | 68.6 | 75 | 112.7 | 67.1
473 | 346 | 528.7 | 258.7 | 315.9 | 254.7 | 132.1 | 112.9 | 68.9 | 75.3 | 113.1 | 67.3
474 | 347 | 528.6 | 259.3 | 316.6 | 255.2 | 132.6 | 113.2 | 69.2 | 75.5 | 113.5 | 67.6
475 | 348 | 528.6 | 259.8 | 317.3 | 255.7 | 133 | 113.6 | 69.5 | 75.8 | 114 | 67.8
476 | 349 | 528.6 | 260.3 | 317.8 | 256.3 | 133.4 | 114 | 69.8 | 76.1 | 114.4 | 68.1
477 | 350 | 528.6 | 260.9 | 318.4 | 256.8 | 134 | 114.4 | 70 | 76.3 | 114.8 | 68.3
478 | 351 | 528.6 | 261.5 | 319 | 257.4 | 134.5 | 114.8 | 70.3 | 76.6 | 115.3 | 68.6
479 | 352 | 528.6 | 262 | 319.7 | 257.9 | 134.9 | 115.2 | 70.6 | 76.8 | 115.7 | 68.8
480 | 353 | 528.5 | 262.6 | 320.2 | 258.5 | 135.4 | 115.6 | 70.8 | 77.1 | 116.1 | 69.1
481 | 354 | 528.5 | 263.1 | 320.8 | 259.1 | 135.9 | 115.9 | 71.1 | 77.4 | 116.5 | 69.3
482 | 355 | 528.5 | 263.6 | 321.5 | 259.6 | 136.4 | 116.3 | 71.4 | 77.6 | 117 | 69.5
483 | 356 | 528.5 | 264.2 | 321.9 | 260.1 | 136.9 | 116.7 | 71.7 | 77.9 | 117.4 | 69.8
484 | 357 | 528.5 | 264.8 | 322.5 | 260.6 | 137.4 | 117.1 | 71.9 | 78.2 | 117.8 | 70
485 | 358 | 528.4 | 265.3 | 323.1 | 261.3 | 137.9 | 117.5 | 72.2 | 78.5 | 118.2 | 70.3
486 | 359 | 528.4 | 265.8 | 323.7 | 261.9 | 138.3 | 117.9 | 72.5 | 78.8 | 118.7 | 70.5
487 | 360 | 528.4 | 266.4 | 324.3 | 262.5 | 138.8 | 118.3 | 72.8 | 79.1 | 119.1 | 70.8
488 | 361 | 528.4 | 266.9 | 324.9 | 263 | 139.3 | 118.7 | 73.1 | 79.4 | 119.5 | 71
489 | 362 | 528.4 | 267.4 | 325.5 | 263.4 | 139.8 | 119.1 | 73.3 | 79.7 | 120 | 71.3
490 | 363 | 528.5 | 268 | 326.1 | 263.9 | 140.4 | 119.5 | 73.6 | 79.9 | 120.4 | 71.6
491 | 364 | 528.5 | 268.5 | 326.7 | 264.5 | 140.7 | 119.8 | 73.9 | 80.2 | 120.8 | 71.8
492 | 365 | 528.6 | 269 | 327.2 | 265.1 | 141.2 | 120.2 | 74.2 | 80.5 | 121.3 | 72.1
493 | 366 | 528.6 | 269.6 | 327.8 | 265.6 | 141.7 | 120.6 | 74.5 | 80.8 | 121.7 | 72.3
494 | 367 | 528.6 | 270.1 | 328.4 | 266.1 | 142.1 | 121 | 74.7 | 81.1 | 122.1 | 72.6
495 | 368 | 528.7 | 270.6 | 329 | 266.7 | 142.6 | 121.3 | 75 | 81.3 | 122.6 | 72.9
496 | 369 | 528.7 | 271.2 | 329.6 | 267.2 | 143.1 | 121.7 | 75.3 | 81.6 | 123 | 73.1
497 | 370 | 528.7 | 271.7 | 330.2 | 267.7 | 143.6 | 122.1 | 75.6 | 81.9 | 123.4 | 73.4
498 | 371 | 528.7 | 272.2 | 330.7 | 268.2 | 144.1 | 122.5 | 75.9 | 82.2 | 123.8 | 73.6
499 | 372 | 528.8 | 272.7 | 331.1 | 268.7 | 144.5 | 122.9 | 76.2 | 82.5 | 124.3 | 73.9
500 | 373 | 528.9 | 273.2 | 331.9 | 269.2 | 144.8 | 123.2 | 76.5 | 82.8 | 124.7 | 74.2
501 | 374 | 528.9 | 273.8 | 332.4 | 269.8 | 145.4 | 123.6 | 76.7 | 83 | 125.1 | 74.4
502 | 375 | 528.9 | 274.2 | 333 | 270.3 | 145.7 | 123.9 | 77 | 83.4 | 125.6 | 74.7
503 | 376 | 529 | 274.8 | 333.5 | 270.8 | 146.3 | 124.3 | 77.3 | 83.7 | 126 | 75
504 | 377 | 529 | 275.3 | 334.1 | 271.3 | 146.8 | 124.7 | 77.6 | 84 | 126.5 | 75.2
505 | 378 | 529 | 275.9 | 334.6 | 271.8 | 147.3 | 125.1 | 77.9 | 84.3 | 126.9 | 75.5
506 | 379 | 529 | 276.4 | 335.2 | 272.3 | 147.8 | 125.4 | 78.1 | 84.5 | 127.3 | 75.8
507 | 380 | 529.1 | 276.9 | 335.8 | 272.9 | 148.2 | 125.8 | 78.4 | 84.8 | 127.8 | 76
508 | 381 | 529.1 | 277.4 | 336.3 | 273.4 | 148.6 | 126.1 | 78.7 | 85.1 | 128.2 | 76.3
509 | 382 | 529.1 | 277.9 | 336.8 | 273.8 | 149.1 | 126.5 | 79 | 85.4 | 128.6 | 76.6
510 | 383 | 529.1 | 278.4 | 337.4 | 274.3 | 149.6 | 126.8 | 79.3 | 85.7 | 129.1 | 76.8
511 | 384 | 529.2 | 278.9 | 338 | 274.8 | 149.9 | 127.2 | 79.6 | 86 | 129.5 | 77.1
512 | 385 | 529.2 | 279.4 | 338.6 | 275.3 | 150.5 | 127.5 | 79.9 | 86.2 | 130 | 77.4
513 | 386 | 529.2 | 279.9 | 339.1 | 275.8 | 150.8 | 127.8 | 80.2 | 86.5 | 130.4 | 77.7
514 | 387 | 529.2 | 280.4 | 339.7 | 276.2 | 151.4 | 128.2 | 80.4 | 86.8 | 130.8 | 77.9
515 | 388 | 529.2 | 280.9 | 340.2 | 276.7 | 151.8 | 128.5 | 80.7 | 87.1 | 131.3 | 78.2
516 | 389 | 529.2 | 281.4 | 340.8 | 277.2 | 152.2 | 128.9 | 81 | 87.4 | 131.7 | 78.5
517 | 390 | 529.3 | 281.9 | 341.3 | 277.8 | 152.7 | 129.2 | 81.3 | 87.7 | 132.2 | 78.8
518 | 391 | 529.3 | 282.4 | 341.9 | 278.3 | 153.1 | 129.5 | 81.6 | 88 | 132.6 | 79
519 | 392 | 529.3 | 282.9 | 342.4 | 278.8 | 153.6 | 129.9 | 81.9 | 88.2 | 133 | 79.3
520 | 393 | 529.2 | 283.4 | 342.9 | 279.3 | 154 | 130.2 | 82.2 | 88.6 | 133.5 | 79.6
521 | 394 | 529.2 | 283.9 | 343.4 | 279.7 | 154.5 | 130.5 | 82.4 | 88.9 | 133.9 | 79.9
522 | 395 | 529.1 | 284.4 | 343.9 | 280.2 | 155.1 | 130.9 | 82.7 | 89.2 | 134.3 | 80.2
523 | 396 | 529.1 | 284.9 | 344.3 | 280.7 | 155.6 | 131.2 | 83 | 89.6 | 134.8 | 80.4
524 | 397 | 529 | 285.4 | 344.8 | 281.3 | 156.2 | 131.6 | 83.3 | 89.9 | 135.2 | 80.7
525 | 398 | 529 | 285.9 | 345.4 | 281.8 | 156.5 | 131.9 | 83.6 | 90.2 | 135.7 | 81
526 | 399 | 529 | 286.4 | 345.9 | 282.3 | 156.9 | 132.2 | 83.9 | 90.5 | 136.1 | 81.3
527 | 400 | 528.9 | 286.9 | 346.4 | 282.8 | 157.4 | 132.5 | 84.2 | 90.8 | 136.6 | 81.5
528 | 401 | 528.9 | 287.4 | 346.9 | 283.2 | 157.8 | 132.9 | 84.4 | 91.1 | 137 | 81.8
529 | 402 | 528.9 | 287.9 | 347.4 | 283.7 | 158.3 | 133.2 | 84.7 | 91.4 | 137.4 | 82.1
530 | 403 | 528.8 | 288.3 | 347.9 | 284.2 | 158.8 | 133.5 | 85 | 91.6 | 137.9 | 82.4
531 | 404 | 528.8 | 288.8 | 348.4 | 284.7 | 159.3 | 133.9 | 85.3 | 91.9 | 138.3 | 82.7
532 | 405 | 528.8 | 289.3 | 348.9 | 285.2 | 159.9 | 134.2 | 85.6 | 92.2 | 138.8 | 82.9
533 | 406 | 528.8 | 289.8 | 349.5 | 285.7 | 160.2 | 134.5 | 85.9 | 92.5 | 139.2 | 83.2
534 | 407 | 528.8 | 290.3 | 349.9 | 286.2 | 160.6 | 134.9 | 86.2 | 92.8 | 139.6 | 83.5
535 | 408 | 528.8 | 290.7 | 350.5 | 286.6 | 161 | 135.2 | 86.5 | 93.2 | 140.1 | 83.8
536 | 409 | 528.9 | 291.2 | 351 | 287.1 | 161.6 | 135.5 | 86.7 | 93.4 | 140.5 | 84.1
537 | 410 | 528.9 | 291.7 | 351.5 | 287.6 | 162.1 | 135.9 | 87 | 93.7 | 141 | 84.3
538 | 411 | 528.9 | 292.2 | 351.9 | 288 | 162.5 | 136.2 | 87.3 | 94.1 | 141.4 | 84.6
539 | 412 | 528.9 | 292.6 | 352.5 | 288.5 | 162.9 | 136.5 | 87.6 | 94.4 | 141.8 | 84.9
540 | 413 | 528.9 | 293.1 | 352.9 | 289 | 163.3 | 136.9 | 87.9 | 94.7 | 142.3 | 85.2
541 | 414 | 528.9 | 293.6 | 353.4 | 289.5 | 163.9 | 137.2 | 88.2 | 95 | 142.7 | 85.5
542 | 415 | 528.9 | 294.1 | 353.9 | 290 | 164.4 | 137.6 | 88.5 | 95.3 | 143.2 | 85.8
543 | 416 | 528.9 | 294.5 | 354.4 | 290.5 | 164.8 | 137.9 | 88.7 | 95.6 | 143.6 | 86
544 | 417 | 528.9 | 295 | 354.9 | 290.9 | 165.2 | 138.3 | 89 | 95.9 | 144.1 | 86.3
545 | 418 | 528.9 | 295.5 | 355.4 | 291.4 | 165.7 | 138.6 | 89.3 | 96.2 | 144.5 | 86.6
546 | 419 | 528.9 | 295.9 | 355.9 | 291.8 | 166.1 | 138.9 | 89.6 | 96.5 | 145 | 86.9
547 | 420 | 528.9 | 296.4 | 356.3 | 292.3 | 166.6 | 139.3 | 89.9 | 96.8 | 145.4 | 87.2
548 | 421 | 528.9 | 296.8 | 356.8 | 292.7 | 167.1 | 139.7 | 90.2 | 97.1 | 145.9 | 87.5
549 | 422 | 528.9 | 297.2 | 357.4 | 293.1 | 167.4 | 140 | 90.5 | 97.4 | 146.3 | 87.7
550 | 423 | 528.9 | 297.7 | 357.9 | 293.6 | 167.8 | 140.3 | 90.8 | 97.8 | 146.8 | 88
551 | 424 | 528.9 | 298.2 | 358.3 | 294.1 | 168.3 | 140.7 | 91.1 | 98.1 | 147.2 | 88.3
552 | 425 | 528.9 | 298.6 | 358.8 | 294.5 | 168.7 | 141 | 91.4 | 98.4 | 147.7 | 88.6
553 | 426 | 528.9 | 299.1 | 359.3 | 295 | 169.2 | 141.4 | 91.6 | 98.7 | 148.1 | 88.9
554 | 427 | 529 | 299.5 | 359.8 | 295.4 | 169.7 | 141.8 | 91.9 | 99 | 148.5 | 89.2
555 | 428 | 529 | 300 | 360.2 | 295.9 | 170.1 | 142.1 | 92.2 | 99.4 | 149 | 89.5
556 | 429 | 529 | 300.4 | 360.7 | 296.3 | 170.6 | 142.5 | 92.5 | 99.7 | 149.4 | 89.8
557 | 430 | 529 | 300.7 | 361.5 | 296.6 | 170.7 | 142.7 | 92.8 | 100.1 | 149.9 | 90.1
558 | 431 | 529 | 301.3 | 361.7 | 297.2 | 171.4 | 143.2 | 93.1 | 100.4 | 150.3 | 90.3
559 | 432 | 529 | 301.8 | 362.1 | 297.6 | 172 | 143.6 | 93.4 | 100.6 | 150.8 | 90.6
560 | 433 | 529 | 302.2 | 362.6 | 298.1 | 172.4 | 143.9 | 93.7 | 101 | 151.2 | 90.9
561 | 434 | 528.9 | 302.7 | 363 | 298.5 | 172.9 | 144.3 | 93.9 | 101.3 | 151.7 | 91.2
562 | 435 | 528.9 | 303.1 | 363.5 | 299 | 173.3 | 144.6 | 94.2 | 101.6 | 152.1 | 91.5
563 | 436 | 528.9 | 303.5 | 364.1 | 299.4 | 173.7 | 145 | 94.5 | 101.9 | 152.6 | 91.8
564 | 437 | 528.9 | 304 | 364.5 | 299.9 | 174.3 | 145.4 | 94.8 | 102.2 | 153 | 92.1
565 | 438 | 528.8 | 304.4 | 365 | 300.3 | 174.6 | 145.7 | 95.1 | 102.5 | 153.5 | 92.4
566 | 439 | 528.8 | 304.8 | 365.4 | 300.7 | 175 | 146.1 | 95.4 | 102.9 | 153.9 | 92.6
567 | 440 | 528.8 | 305.3 | 365.8 | 301.1 | 175.6 | 146.5 | 95.7 | 103.3 | 154.3 | 92.9
568 | 441 | 528.7 | 305.7 | 366.3 | 301.6 | 176 | 146.9 | 96 | 103.6 | 154.8 | 93.2
569 | 442 | 528.7 | 306.2 | 366.7 | 302 | 176.4 | 147.3 | 96.3 | 104 | 155.2 | 93.5
570 | 443 | 528.6 | 306.6 | 367.2 | 302.4 | 176.9 | 147.7 | 96.5 | 104.3 | 155.7 | 93.8
571 | 444 | 528.6 | 307.1 | 367.5 | 302.9 | 177.4 | 148.1 | 96.8 | 104.6 | 156.1 | 94.1
572 | 445 | 528.5 | 307.4 | 368.1 | 303.3 | 177.8 | 148.4 | 97.1 | 104.9 | 156.5 | 94.3
573 | 446 | 528.4 | 307.9 | 368.4 | 303.8 | 178.3 | 148.9 | 97.4 | 105.2 | 157 | 94.6
574 | 447 | 528.4 | 308.4 | 368.7 | 304.2 | 178.8 | 149.3 | 97.7 | 105.5 | 157.4 | 94.9
575 | 448 | 528.4 | 308.8 | 369.2 | 304.6 | 179.3 | 149.7 | 98 | 105.8 | 157.8 | 95.2
576 | 449 | 528.4 | 309.3 | 369.6 | 305.1 | 179.8 | 150.1 | 98.3 | 106.1 | 158.3 | 95.5
577 | 450 | 528.4 | 309.7 | 370 | 305.5 | 180.3 | 150.5 | 98.6 | 106.4 | 158.7 | 95.8
578 | 451 | 528.4 | 310.1 | 370.3 | 305.9 | 180.7 | 150.9 | 98.9 | 106.8 | 159.2 | 96.1
579 | 452 | 528.3 | 310.6 | 370.8 | 306.4 | 181.2 | 151.3 | 99.2 | 107.1 | 159.6 | 96.4
580 | 453 | 528.3 | 311 | 371.3 | 306.8 | 181.6 | 151.7 | 99.5 | 107.4 | 160 | 96.6
581 | 454 | 528.3 | 311.4 | 371.7 | 307.2 | 182.1 | 152.1 | 99.8 | 107.7 | 160.5 | 96.9
582 | 455 | 528.2 | 311.8 | 372.1 | 307.6 | 182.5 | 152.5 | 100.1 | 108 | 160.9 | 97.2
583 | 456 | 528.2 | 312.2 | 372.5 | 308 | 182.9 | 152.9 | 100.4 | 108.4 | 161.3 | 97.5
584 | 457 | 528.2 | 312.6 | 373 | 308.4 | 183.4 | 153.3 | 100.7 | 108.7 | 161.8 | 97.8
585 | 458 | 528.1 | 313 | 373.5 | 308.8 | 183.6 | 153.7 | 101 | 109 | 162.2 | 98.1
586 | 459 | 528.1 | 313.4 | 373.9 | 309.2 | 184.1 | 154 | 101.3 | 109.3 | 162.6 | 98.4
587 | 460 | 528.1 | 313.9 | 374.3 | 309.7 | 184.6 | 154.5 | 101.6 | 109.7 | 163.1 | 98.7
588 | 461 | 528.1 | 314.3 | 374.7 | 310.1 | 185.1 | 154.9 | 101.9 | 110 | 163.5 | 98.9
589 | 462 | 528.2 | 314.6 | 375.2 | 310.5 | 185.4 | 155.2 | 102.2 | 110.2 | 164 | 99.2
590 | 463 | 528.2 | 315 | 375.7 | 310.8 | 185.8 | 155.6 | 102.6 | 110.5 | 164.4 | 99.5
591 | 464 | 528.2 | 315.5 | 376 | 311.3 | 186.3 | 156.1 | 102.9 | 110.9 | 164.8 | 99.8
592 | 465 | 528.2 | 315.9 | 376.5 | 311.7 | 186.8 | 156.5 | 103.2 | 111.2 | 165.2 | 100.1
593 | 466 | 528.2 | 316.3 | 376.8 | 312.1 | 187.4 | 156.9 | 103.5 | 111.6 | 165.7 | 100.3
594 | 467 | 528.3 | 316.7 | 377.2 | 312.6 | 187.8 | 157.3 | 103.9 | 111.9 | 166.1 | 100.6
595 | 468 | 528.3 | 317.2 | 377.6 | 313 | 188.3 | 157.8 | 104.2 | 112.2 | 166.5 | 100.9
596 | 469 | 528.3 | 317.6 | 378 | 313.5 | 188.8 | 158.3 | 104.5 | 112.6 | 167 | 101.2
597 | 470 | 528.3 | 317.9 | 378.5 | 313.8 | 189.2 | 158.7 | 104.9 | 112.9 | 167.4 | 101.5
598 | 471 | 528.3 | 318.3 | 378.9 | 314.2 | 189.6 | 159.1 | 105.2 | 113.2 | 167.8 | 101.8
599 | 472 | 528.3 | 318.8 | 379.2 | 314.6 | 190 | 159.6 | 105.5 | 113.6 | 168.3 | 102
600 | 473 | 528.3 | 319.2 | 379.5 | 315 | 190.7 | 160.1 | 105.9 | 113.9 | 168.7 | 102.3
601 | 474 | 528.3 | 319.6 | 380.1 | 315.4 | 191 | 160.5 | 106.2 | 114.3 | 169.1 | 102.6
602 | 475 | 528.2 | 320 | 380.3 | 315.8 | 191.5 | 160.9 | 106.6 | 114.6 | 169.6 | 102.9
603 | 476 | 528.2 | 320.4 | 380.7 | 316.2 | 192 | 161.4 | 106.9 | 114.9 | 170 | 103.2
604 | 477 | 528.2 | 320.8 | 381.1 | 316.6 | 192.5 | 161.9 | 107.3 | 115.3 | 170.4 | 103.5
605 | 478 | 528.2 | 321.2 | 381.5 | 317 | 193 | 162.3 | 107.6 | 115.6 | 170.8 | 103.8
606 | 479 | 528.2 | 321.6 | 381.9 | 317.4 | 193.4 | 162.8 | 108 | 116 | 171.3 | 104
607 | 480 | 528.2 | 322 | 382.2 | 317.8 | 194 | 163.3 | 108.3 | 116.3 | 171.7 | 104.3
608 | 481 | 528.2 | 322.4 | 382.7 | 318.2 | 194.5 | 163.7 | 108.7 | 116.6 | 172.1 | 104.6
609 | 482 | 528.2 | 322.8 | 383.1 | 318.6 | 194.9 | 164.2 | 109 | 117 | 172.6 | 104.9
610 | 483 | 528.2 | 323.2 | 383.4 | 319 | 195.4 | 164.6 | 109.4 | 117.3 | 173 | 105.2
611 | 484 | 528.2 | 323.6 | 383.8 | 319.4 | 196 | 165.1 | 109.7 | 117.6 | 173.4 | 105.5
612 | 485 | 528.2 | 324 | 384.1 | 319.8 | 196.4 | 165.6 | 110.1 | 118 | 173.8 | 105.7
613 | 486 | 528.2 | 324.4 | 384.6 | 320.1 | 196.9 | 166 | 110.4 | 118.4 | 174.3 | 106
614 | 487 | 528.2 | 324.7 | 385 | 320.5 | 197.3 | 166.5 | 110.8 | 118.8 | 174.7 | 106.3
615 | 488 | 528.2 | 325.1 | 385.4 | 320.9 | 197.8 | 166.9 | 111.1 | 119.2 | 175.1 | 106.6
616 | 489 | 528.2 | 325.5 | 385.8 | 321.3 | 198.2 | 167.4 | 111.4 | 119.5 | 175.6 | 106.9
617 | 490 | 528.2 | 325.9 | 386.1 | 321.7 | 198.8 | 167.9 | 111.8 | 119.8 | 176 | 107.2
618 | 491 | 528.3 | 326.3 | 386.5 | 322.1 | 199.2 | 168.4 | 112.1 | 120.1 | 176.4 | 107.5
619 | 492 | 528.3 | 326.7 | 386.8 | 322.5 | 199.7 | 168.8 | 112.4 | 120.4 | 176.8 | 107.7
620 | 493 | 528.3 | 327.1 | 387.1 | 322.9 | 200.1 | 169.3 | 112.7 | 120.7 | 177.3 | 108
621 | 494 | 528.3 | 327.5 | 387.6 | 323.2 | 200.8 | 169.8 | 113 | 121.1 | 177.7 | 108.3
622 | 495 | 528.3 | 327.9 | 387.9 | 323.6 | 201.2 | 170.3 | 113.4 | 121.5 | 178.1 | 108.6
623 | 496 | 528.4 | 328.1 | 388.5 | 323.9 | 201.4 | 170.7 | 113.7 | 121.9 | 178.6 | 108.9
624 | 497 | 528.4 | 328.5 | 388.9 | 324.3 | 202.1 | 171.2 | 114 | 122.2 | 179 | 109.2
625 | 498 | 528.4 | 328.9 | 389.3 | 324.6 | 202.6 | 171.7 | 114.3 | 122.5 | 179.4 | 109.4
626 | 499 | 528.3 | 329.3 | 389.5 | 325.1 | 203.1 | 172.2 | 114.6 | 122.8 | 179.8 | 109.7
627 | 500 | 528.4 | 329.7 | 389.8 | 325.4 | 203.7 | 172.7 | 114.9 | 123.1 | 180.3 | 110
628 | 501 | 528.3 | 330.1 | 390.1 | 325.8 | 204.2 | 173.2 | 115.1 | 123.4 | 180.7 | 110.3
629 | 502 | 528.3 | 330.5 | 390.4 | 326.2 | 204.8 | 173.7 | 115.4 | 123.7 | 181.1 | 110.6
630 | 503 | 528.3 | 330.9 | 390.8 | 326.6 | 205.2 | 174.2 | 115.7 | 124.1 | 181.5 | 110.8
631 | 504 | 528.3 | 331.2 | 391.3 | 326.9 | 205.7 | 174.6 | 116 | 124.4 | 182 | 111.1
632 | 505 | 528.3 | 331.6 | 391.6 | 327.3 | 206.2 | 175.1 | 116.3 | 124.8 | 182.4 | 111.4
633 | 506 | 528.3 | 332 | 391.9 | 327.7 | 206.7 | 175.6 | 116.6 | 125.1 | 182.8 | 111.7
634 | 507 | 528.2 | 332.3 | 392.3 | 328.1 | 207.2 | 176.1 | 116.9 | 125.4 | 183.3 | 111.9
635 | 508 | 528.2 | 332.6 | 392.8 | 328.4 | 207.6 | 176.5 | 117.2 | 125.8 | 183.7 | 112.2
636 | 509 | 528.2 | 333 | 393.1 | 328.8 | 208.1 | 177 | 117.5 | 126.1 | 184.1 | 112.5
637 | 510 | 528.2 | 333.4 | 393.5 | 329.1 | 208.5 | 177.5 | 117.8 | 126.4 | 184.5 | 112.8
638 | 511 | 528.1 | 333.7 | 393.9 | 329.4 | 209.1 | 177.9 | 118.1 | 126.7 | 185 | 113
639 | 512 | 528.1 | 334.1 | 394.2 | 329.8 | 209.5 | 178.4 | 118.5 | 127 | 185.4 | 113.3
640 | 513 | 528.1 | 334.4 | 394.6 | 330.1 | 210 | 178.9 | 118.8 | 127.4 | 185.8 | 113.6
641 | 514 | 528.1 | 334.8 | 394.9 | 330.5 | 210.4 | 179.4 | 119.1 | 127.7 | 186.3 | 113.9
642 | 515 | 528 | 335.1 | 395.3 | 330.9 | 211 | 179.9 | 119.4 | 128 | 186.7 | 114.1
643 | 516 | 528 | 335.5 | 395.6 | 331.2 | 211.5 | 180.3 | 119.8 | 128.3 | 187.1 | 114.4
644 | 517 | 528 | 335.9 | 395.9 | 331.6 | 212 | 180.8 | 120.1 | 128.7 | 187.6 | 114.7
645 | 518 | 528 | 336.2 | 396.3 | 332 | 212.5 | 181.3 | 120.5 | 129 | 188 | 115
646 | 519 | 527.9 | 336.6 | 396.6 | 332.3 | 213 | 181.8 | 120.8 | 129.4 | 188.4 | 115.2
647 | 520 | 527.9 | 336.9 | 397.1 | 332.6 | 213.4 | 182.2 | 121.2 | 129.7 | 188.8 | 115.5
648 | 521 | 527.9 | 337.3 | 397.4 | 333 | 213.9 | 182.7 | 121.5 | 130 | 189.3 | 115.8
649 | 522 | 527.9 | 337.7 | 397.6 | 333.4 | 214.5 | 183.2 | 121.9 | 130.3 | 189.7 | 116
650 | 523 | 527.8 | 338 | 397.9 | 333.7 | 215.1 | 183.7 | 122.2 | 130.7 | 190.1 | 116.3
651 | 524 | 527.8 | 338.4 | 398.2 | 334.1 | 215.5 | 184.2 | 122.6 | 131 | 190.6 | 116.6
652 | 525 | 527.8 | 338.7 | 398.6 | 334.4 | 216 | 184.6 | 123 | 131.4 | 191 | 116.9
653 | 526 | 527.8 | 339 | 399 | 334.8 | 216.5 | 185.1 | 123.4 | 131.7 | 191.4 | 117.1
654 | 527 | 527.8 | 339.4 | 399.3 | 335.1 | 217 | 185.6 | 123.7 | 132 | 191.9 | 117.4
655 | 528 | 527.8 | 339.8 | 399.6 | 335.5 | 217.5 | 186.1 | 124.1 | 132.3 | 192.3 | 117.7
656 | 529 | 527.8 | 340.1 | 400 | 335.8 | 218 | 186.5 | 124.5 | 132.7 | 192.7 | 118
657 | 530 | 527.8 | 340.4 | 400.3 | 336.1 | 218.4 | 187 | 124.9 | 133 | 193.2 | 118.2
658 | 531 | 527.8 | 340.8 | 400.6 | 336.5 | 218.9 | 187.5 | 125.3 | 133.3 | 193.6 | 118.5
659 | 532 | 527.8 | 341.1 | 401 | 336.8 | 219.4 | 187.9 | 125.6 | 133.7 | 194 | 118.8
660 | 533 | 527.8 | 341.4 | 401.3 | 337.2 | 219.9 | 188.4 | 126 | 134 | 194.5 | 119
661 | 534 | 527.8 | 341.8 | 401.6 | 337.5 | 220.3 | 188.9 | 126.5 | 134.3 | 194.9 | 119.3
662 | 535 | 527.8 | 342.1 | 402 | 337.8 | 220.9 | 189.3 | 126.9 | 134.7 | 195.3 | 119.6
663 | 536 | 527.8 | 342.4 | 402.3 | 338.2 | 221.3 | 189.8 | 127.3 | 135 | 195.8 | 119.9
664 | 537 | 527.8 | 342.8 | 402.6 | 338.5 | 221.9 | 190.3 | 127.8 | 135.3 | 196.2 | 120.1
665 | 538 | 527.8 | 343.1 | 402.9 | 338.8 | 222.3 | 190.7 | 128.2 | 135.7 | 196.6 | 120.4
666 | 539 | 527.8 | 343.5 | 403.3 | 339.1 | 222.8 | 191.2 | 128.7 | 136.1 | 197.1 | 120.7
667 | 540 | 527.8 | 343.8 | 403.6 | 339.5 | 223.3 | 191.6 | 129.2 | 136.4 | 197.5 | 121
668 | 541 | 527.7 | 344.1 | 403.9 | 339.8 | 223.7 | 192.1 | 129.8 | 136.8 | 198 | 121.2
669 | 542 | 527.7 | 344.5 | 404.2 | 340.1 | 224.3 | 192.6 | 130.3 | 137.1 | 198.4 | 121.5
670 | 543 | 527.7 | 344.8 | 404.5 | 340.5 | 224.9 | 193.1 | 130.9 | 137.5 | 198.9 | 121.8
671 | 544 | 527.7 | 345.2 | 404.8 | 340.9 | 225.4 | 193.6 | 131.4 | 137.9 | 199.3 | 122.1
672 | 545 | 527.7 | 345.6 | 404.9 | 341.2 | 226 | 194.1 | 132 | 138.3 | 199.8 | 122.3
673 | 546 | 527.8 | 345.9 | 405.3 | 341.5 | 226.4 | 194.5 | 132.6 | 138.7 | 200.2 | 122.6
674 | 547 | 527.8 | 346.3 | 405.5 | 341.9 | 227 | 195.1 | 133.1 | 139.1 | 200.7 | 122.9
675 | 548 | 527.8 | 346.6 | 405.8 | 342.2 | 227.4 | 195.5 | 133.7 | 139.5 | 201.1 | 123.2
676 | 549 | 527.8 | 346.9 | 406.1 | 342.6 | 227.9 | 196 | 134.2 | 140 | 201.6 | 123.4
677 | 550 | 527.8 | 347.2 | 406.4 | 342.9 | 228.4 | 196.5 | 134.8 | 140.4 | 202 | 123.7
678 | 551 | 527.8 | 347.6 | 406.7 | 343.2 | 229 | 197 | 135.3 | 140.8 | 202.5 | 124
679 | 552 | 527.8 | 347.9 | 407 | 343.5 | 229.4 | 197.4 | 135.9 | 141.3 | 202.9 | 124.3
680 | 553 | 527.7 | 348.2 | 407.3 | 343.9 | 230 | 197.9 | 136.4 | 141.7 | 203.4 | 124.6
681 | 554 | 527.7 | 348.6 | 407.6 | 344.2 | 230.5 | 198.4 | 137 | 142.1 | 203.8 | 124.8
682 | 555 | 527.7 | 348.9 | 407.9 | 344.5 | 230.9 | 198.9 | 137.5 | 142.5 | 204.3 | 125.1
683 | 556 | 527.7 | 349.2 | 408.2 | 344.8 | 231.5 | 199.4 | 138 | 142.9 | 204.7 | 125.4
684 | 557 | 527.7 | 349.5 | 408.6 | 345.1 | 231.9 | 199.8 | 138.6 | 143.4 | 205.2 | 125.7
685 | 558 | 527.7 | 349.8 | 408.9 | 345.4 | 232.4 | 200.3 | 139.1 | 143.8 | 205.7 | 125.9
686 | 559 | 527.7 | 350.1 | 409.3 | 345.7 | 232.8 | 200.8 | 139.6 | 144.3 | 206.1 | 126.2
687 | 560 | 527.7 | 350.4 | 409.5 | 346 | 233.4 | 201.3 | 140.1 | 144.7 | 206.6 | 126.5
688 | 561 | 527.6 | 350.8 | 409.8 | 346.3 | 234 | 201.8 | 140.6 | 145.1 | 207.1 | 126.7
689 | 562 | 527.6 | 351.1 | 410 | 346.7 | 234.5 | 202.3 | 141.1 | 145.5 | 207.5 | 127
690 | 563 | 527.6 | 351.4 | 410.5 | 346.9 | 234.8 | 202.7 | 141.7 | 145.9 | 208 | 127.3
691 | 564 | 527.6 | 351.8 | 410.6 | 347.3 | 235.5 | 203.3 | 142.1 | 146.3 | 208.5 | 127.6
692 | 565 | 527.6 | 352 | 411 | 347.6 | 235.9 | 203.7 | 142.7 | 146.7 | 209 | 127.8
693 | 566 | 527.6 | 352.4 | 411.2 | 347.9 | 236.4 | 204.2 | 143.2 | 147.1 | 209.4 | 128.1
694 | 567 | 527.6 | 352.7 | 411.5 | 348.3 | 236.9 | 204.7 | 143.7 | 147.5 | 209.9 | 128.4
695 | 568 | 527.6 | 353 | 411.9 | 348.6 | 237.4 | 205.2 | 144.2 | 147.9 | 210.4 | 128.7
696 | 569 | 527.7 | 353.3 | 412.2 | 348.9 | 237.9 | 205.7 | 144.7 | 148.3 | 210.8 | 128.9
697 | 570 | 527.7 | 353.6 | 412.5 | 349.2 | 238.3 | 206.2 | 145.2 | 148.8 | 211.3 | 129.2
698 | 571 | 527.7 | 353.9 | 412.7 | 349.5 | 238.9 | 206.7 | 145.6 | 149.2 | 211.8 | 129.5
699 | 572 | 527.8 | 354.3 | 413 | 349.8 | 239.4 | 207.2 | 146.1 | 149.7 | 212.3 | 129.8
700 | 573 | 527.8 | 354.6 | 413.3 | 350.1 | 240.1 | 207.7 | 146.6 | 150.1 | 212.7 | 130.1
701 | 574 | 527.8 | 354.9 | 413.6 | 350.4 | 240.5 | 208.2 | 147.1 | 150.5 | 213.2 | 130.4
702 | 575 | 527.8 | 355.1 | 414 | 350.7 | 240.9 | 208.7 | 147.6 | 150.9 | 213.7 | 130.6
703 | 576 | 527.8 | 355.5 | 414.2 | 351 | 241.4 | 209.2 | 148.1 | 151.3 | 214.2 | 130.9
704 | 577 | 527.8 | 355.8 | 414.5 | 351.3 | 242 | 209.7 | 148.6 | 151.7 | 214.7 | 131.2
705 | 578 | 527.8 | 356.1 | 414.8 | 351.6 | 242.3 | 210.2 | 149.1 | 152.1 | 215.1 | 131.5
706 | 579 | 527.8 | 356.4 | 415.1 | 351.9 | 242.9 | 210.6 | 149.5 | 152.6 | 215.6 | 131.7
707 | 580 | 527.8 | 356.7 | 415.4 | 352.2 | 243.5 | 211.1 | 150 | 153 | 216.1 | 132
708 | 581 | 527.8 | 357 | 415.6 | 352.5 | 243.8 | 211.6 | 150.5 | 153.5 | 216.6 | 132.3
709 | 582 | 527.7 | 357.3 | 415.9 | 352.8 | 244.5 | 212.1 | 151 | 154 | 217 | 132.6
710 | 583 | 527.7 | 357.6 | 416.2 | 353.1 | 244.9 | 212.6 | 151.5 | 154.5 | 217.5 | 132.9
711 | 584 | 527.7 | 357.9 | 416.4 | 353.4 | 245.5 | 213.1 | 151.9 | 155 | 218 | 133.1
712 | 585 | 527.7 | 358.2 | 416.6 | 353.7 | 246 | 213.6 | 152.4 | 155.4 | 218.5 | 133.4
713 | 586 | 527.7 | 358.6 | 416.9 | 354 | 246.4 | 214.1 | 152.9 | 155.8 | 218.9 | 133.7
714 | 587 | 527.6 | 358.8 | 417.2 | 354.3 | 246.9 | 214.6 | 153.4 | 156.3 | 219.4 | 133.9
715 | 588 | 527.6 | 359.2 | 417.5 | 354.6 | 247.5 | 215.1 | 153.8 | 156.8 | 219.9 | 134.2
716 | 589 | 527.6 | 359.4 | 417.8 | 354.9 | 248 | 215.5 | 154.3 | 157.2 | 220.3 | 134.5
717 | 590 | 527.6 | 359.8 | 418 | 355.2 | 248.5 | 216 | 154.8 | 157.6 | 220.8 | 134.8
718 | 591 | 527.6 | 360.1 | 418.3 | 355.5 | 249 | 216.5 | 155.2 | 158 | 221.3 | 135.1
719 | 592 | 527.6 | 360.4 | 418.6 | 355.8 | 249.5 | 217 | 155.7 | 158.5 | 221.8 | 135.3
720 | 593 | 527.5 | 360.7 | 418.8 | 356.1 | 250 | 217.5 | 156.2 | 159 | 222.2 | 135.6
721 | 594 | 527.5 | 360.9 | 419.2 | 356.4 | 250.5 | 217.9 | 156.7 | 159.4 | 222.7 | 135.9
722 | 595 | 527.5 | 361.2 | 419.4 | 356.7 | 251 | 218.4 | 157.2 | 159.8 | 223.2 | 136.1
723 | 596 | 527.5 | 361.6 | 419.6 | 357 | 251.6 | 218.9 | 157.6 | 160.3 | 223.6 | 136.4
724 | 597 | 527.4 | 361.9 | 419.9 | 357.2 | 252.2 | 219.4 | 158.1 | 160.7 | 224.1 | 136.7
725 | 598 | 527.4 | 362.2 | 420.1 | 357.5 | 252.8 | 219.9 | 158.6 | 161.2 | 224.5 | 136.9
726 | 599 | 527.4 | 362.5 | 420.4 | 357.8 | 253.3 | 220.4 | 159 | 161.6 | 225 | 137.2
727 | 600 | 527.3 | 362.8 | 420.6 | 358.1 | 253.9 | 220.9 | 159.5 | 162.1 | 225.5 | 137.5
728 | 601 | 527.4 | 363.1 | 420.9 | 358.4 | 254.4 | 221.4 | 160 | 162.5 | 225.9 | 137.8
729 | 602 | 527.4 | 363.4 | 421.1 | 358.7 | 255 | 221.8 | 160.4 | 163 | 226.4 | 138
730 | 603 | 527.4 | 363.6 | 421.4 | 359 | 255.3 | 222.3 | 160.9 | 163.5 | 226.9 | 138.3
731 | 604 | 527.4 | 363.9 | 421.6 | 359.3 | 255.9 | 222.8 | 161.4 | 163.9 | 227.3 | 138.6
732 | 605 | 527.4 | 364.2 | 421.9 | 359.6 | 256.4 | 223.3 | 161.8 | 164.4 | 227.8 | 138.9
733 | 606 | 527.4 | 364.5 | 422.1 | 359.9 | 257 | 223.8 | 162.3 | 164.9 | 228.2 | 139.1
734 | 607 | 527.4 | 364.8 | 422.4 | 360.1 | 257.5 | 224.3 | 162.8 | 165.3 | 228.7 | 139.4
735 | 608 | 527.4 | 365.1 | 422.6 | 360.4 | 257.9 | 224.7 | 163.2 | 165.7 | 229.1 | 139.7
736 | 609 | 527.4 | 365.4 | 422.9 | 360.7 | 258.4 | 225.2 | 163.7 | 166.2 | 229.6 | 139.9
737 | 610 | 527.4 | 365.6 | 423.1 | 361 | 258.9 | 225.7 | 164.2 | 166.8 | 230 | 140.2
738 | 611 | 527.4 | 365.9 | 423.4 | 361.2 | 259.3 | 226.1 | 164.6 | 167.2 | 230.5 | 140.5
739 | 612 | 527.5 | 366.2 | 423.6 | 361.5 | 259.5 | 226.6 | 165.1 | 167.7 | 230.9 | 140.8
740 | 613 | 527.5 | 366.5 | 424 | 361.7 | 260 | 227.1 | 165.6 | 168.2 | 231.4 | 141
741 | 614 | 527.5 | 366.7 | 424.3 | 362 | 259.9 | 227.6 | 166 | 168.6 | 231.8 | 141.3
742 | 615 | 527.6 | 367 | 424.5 | 362.3 | 259.9 | 228 | 166.5 | 169 | 232.3 | 141.6
743 | 616 | 527.6 | 367.3 | 424.8 | 362.6 | 260.1 | 228.5 | 167 | 169.5 | 232.7 | 141.8
744 | 617 | 527.6 | 367.6 | 425 | 362.9 | 260.2 | 229 | 167.4 | 170 | 233.1 | 142.1
745 | 618 | 527.6 | 367.9 | 425.2 | 363.1 | 260.3 | 229.4 | 167.9 | 170.4 | 233.6 | 142.4
746 | 619 | 527.5 | 368.1 | 425.4 | 363.4 | 260.5 | 229.9 | 168.4 | 170.9 | 234 | 142.7
747 | 620 | 527.5 | 368.4 | 425.6 | 363.7 | 260.7 | 230.3 | 168.8 | 171.4 | 234.4 | 142.9
748 | 621 | 527.5 | 368.7 | 425.9 | 364 | 261 | 230.7 | 169.3 | 171.8 | 234.9 | 143.2
749 | 622 | 527.5 | 369 | 426.1 | 364.3 | 261.2 | 231.1 | 169.8 | 172.3 | 235.3 | 143.5
750 | 623 | 527.5 | 369.3 | 426.4 | 364.5 | 261.3 | 231.5 | 170.2 | 172.8 | 235.7 | 143.8
751 | 624 | 527.4 | 369.5 | 426.6 | 364.8 | 261.5 | 231.9 | 170.7 | 173.2 | 236.2 | 144.1
752 | 625 | 527.4 | 369.8 | 426.9 | 365.1 | 261.6 | 232.3 | 171.1 | 173.7 | 236.6 | 144.4
753 | 626 | 527.4 | 370 | 427.1 | 365.3 | 261.7 | 232.7 | 171.6 | 174.3 | 237 | 144.7
754 | 627 | 527.4 | 370.3 | 427.3 | 365.6 | 261.8 | 233 | 172.1 | 174.8 | 237.5 | 145
755 | 628 | 527.4 | 370.6 | 427.5 | 365.9 | 261.8 | 233.4 | 172.5 | 175.2 | 237.9 | 145.3
756 | 629 | 527.3 | 370.9 | 427.7 | 366.1 | 261.9 | 233.8 | 173 | 175.6 | 238.3 | 145.6
757 | 630 | 527.3 | 371.2 | 427.9 | 366.4 | 262 | 234.2 | 173.4 | 176.1 | 238.8 | 145.9
758 | 631 | 527.3 | 371.4 | 428.2 | 366.7 | 262.1 | 234.5 | 173.9 | 176.5 | 239.2 | 146.2
759 | 632 | 527.3 | 371.7 | 428.5 | 366.9 | 262.3 | 234.9 | 174.3 | 177 | 239.6 | 146.5
760 | 633 | 527.3 | 372 | 428.7 | 367.2 | 262.5 | 235.3 | 174.8 | 177.4 | 240.1 | 146.8
761 | 634 | 527.2 | 372.2 | 429 | 367.5 | 262.7 | 235.7 | 175.3 | 177.9 | 240.5 | 147.1
762 | 635 | 527.2 | 372.5 | 429.2 | 367.7 | 262.6 | 236.1 | 175.7 | 178.3 | 240.9 | 147.4
763 | 636 | 527.2 | 372.7 | 429.5 | 368 | 262.6 | 236.5 | 176.2 | 178.8 | 241.3 | 147.7
764 | 637 | 527.2 | 373 | 429.6 | 368.3 | 262.7 | 237 | 176.6 | 179.2 | 241.7 | 148.1
765 | 638 | 527.2 | 373.3 | 429.9 | 368.5 | 262.8 | 237.4 | 177.1 | 179.7 | 242.2 | 148.4
766 | 639 | 527.2 | 373.6 | 430.1 | 368.7 | 262.9 | 237.8 | 177.5 | 180.2 | 242.6 | 148.7
767 | 640 | 527.2 | 373.8 | 430.3 | 369 | 262.8 | 238.2 | 178 | 180.6 | 243 | 149.1
768 | 641 | 527.2 | 374.1 | 430.5 | 369.3 | 262.9 | 238.6 | 178.4 | 181.1 | 243.4 | 149.4
769 | 642 | 527.2 | 374.4 | 430.7 | 369.6 | 263.2 | 239 | 178.9 | 181.6 | 243.9 | 149.8
770 | 643 | 527.2 | 374.6 | 430.9 | 369.8 | 263.3 | 239.4 | 179.4 | 182.1 | 244.3 | 150.1
771 | 644 | 527.2 | 374.9 | 431.2 | 370.1 | 263.6 | 239.8 | 179.8 | 182.6 | 244.7 | 150.4
772 | 645 | 527.2 | 375.2 | 431.4 | 370.3 | 263.8 | 240.2 | 180.2 | 182.9 | 245.1 | 150.7
773 | 646 | 527.3 | 375.4 | 431.7 | 370.6 | 263.9 | 240.5 | 180.7 | 183.4 | 245.6 | 151
774 | 647 | 527.3 | 375.6 | 431.9 | 370.8 | 263.9 | 240.6 | 181.2 | 183.9 | 246 | 151.3
775 | 648 | 527.2 | 375.9 | 432.1 | 371.1 | 264.1 | 240.4 | 181.6 | 184.3 | 246.4 | 151.6
776 | 649 | 527.2 | 376.2 | 432.3 | 371.4 | 264.2 | 240.6 | 182.1 | 184.8 | 246.8 | 151.9
777 | 650 | 527.2 | 376.5 | 432.5 | 371.6 | 264.2 | 241.2 | 182.5 | 185.3 | 247.3 | 152.2
778 | 651 | 527.2 | 376.7 | 432.7 | 371.9 | 264.2 | 241.8 | 182.9 | 185.8 | 247.7 | 152.4
779 | 652 | 527.2 | 376.9 | 432.9 | 372.1 | 264.3 | 242.3 | 183.4 | 186.2 | 248.1 | 152.7
780 | 653 | 527.2 | 377.2 | 433.1 | 372.4 | 264.4 | 242.8 | 183.8 | 186.7 | 248.5 | 152.9
781 | 654 | 527.1 | 377.5 | 433.3 | 372.7 | 264.4 | 243.2 | 184.3 | 187.1 | 248.9 | 153.2
782 | 655 | 527.1 | 377.7 | 433.5 | 372.9 | 264.5 | 243.6 | 184.7 | 187.6 | 249.4 | 153.5
783 | 656 | 527.1 | 378 | 433.7 | 373.2 | 264.5 | 244 | 185.2 | 188 | 249.8 | 153.8
784 | 657 | 527.2 | 378.2 | 433.9 | 373.4 | 264.4 | 244.3 | 185.6 | 188.5 | 250.2 | 154.1
785 | 658 | 527.2 | 378.5 | 434.1 | 373.7 | 264.4 | 244.6 | 186.1 | 189 | 250.6 | 154.5
786 | 659 | 527.1 | 378.8 | 434.3 | 373.9 | 264.5 | 244.9 | 186.5 | 189.4 | 251.1 | 154.8
787 | 660 | 527.2 | 379 | 434.5 | 374.2 | 264.4 | 245.3 | 187 | 189.8 | 251.5 | 155.2
788 | 661 | 527.1 | 379.2 | 434.8 | 374.5 | 264.4 | 245.6 | 187.4 | 190.3 | 251.9 | 155.6
789 | 662 | 527.1 | 379.5 | 434.9 | 374.8 | 264.7 | 245.9 | 187.9 | 190.7 | 252.3 | 155.9
790 | 663 | 527.1 | 379.8 | 435.1 | 375 | 264.9 | 246.2 | 188.3 | 191.1 | 252.7 | 156.3
791 | 664 | 527.1 | 380 | 435.3 | 375.2 | 264.9 | 246.4 | 188.7 | 191.6 | 253.1 | 156.7
792 | 665 | 527.1 | 380.2 | 435.5 | 375.5 | 265.1 | 246.7 | 189.2 | 192.1 | 253.6 | 157.1
793 | 666 | 527.1 | 380.5 | 435.7 | 375.7 | 265.1 | 246.9 | 189.6 | 192.5 | 254 | 157.5
794 | 667 | 527.1 | 380.8 | 435.9 | 376 | 265.4 | 247.2 | 190.1 | 193 | 254.4 | 157.8
795 | 668 | 527.1 | 381 | 436.1 | 376.2 | 265.4 | 247.4 | 190.5 | 193.3 | 254.8 | 158.2
796 | 669 | 527.1 | 381.2 | 436.3 | 376.5 | 265.4 | 247.6 | 190.9 | 193.8 | 255.2 | 158.6
797 | 670 | 527.1 | 381.5 | 436.5 | 376.7 | 265.4 | 247.9 | 191.4 | 194.2 | 255.6 | 158.9
798 | 671 | 527.1 | 381.7 | 436.7 | 376.9 | 265.6 | 248.1 | 191.8 | 194.7 | 256.1 | 159.3
799 | 672 | 527 | 382 | 436.9 | 377.2 | 265.8 | 248.4 | 192.2 | 195.1 | 256.5 | 159.6
800 | 673 | 527 | 382.2 | 437.1 | 377.4 | 265.9 | 248.6 | 192.7 | 195.5 | 256.9 | 159.8
801 | 674 | 527 | 382.5 | 437.2 | 377.7 | 266 | 248.9 | 193.1 | 196 | 257.3 | 160.1
802 | 675 | 527 | 382.7 | 437.5 | 377.9 | 266.2 | 249.2 | 193.5 | 196.4 | 257.7 | 160.4
803 | 676 | 527 | 382.9 | 437.7 | 378.2 | 266.4 | 249.4 | 194 | 196.8 | 258.1 | 160.7
804 | 677 | 527 | 383.1 | 437.9 | 378.4 | 266.5 | 249.7 | 194.4 | 197.2 | 258.5 | 161
805 | 678 | 527 | 383.4 | 438.1 | 378.7 | 266.8 | 250 | 194.8 | 197.6 | 258.9 | 161.4
806 | 679 | 527 | 383.7 | 438.3 | 378.9 | 266.9 | 250.4 | 195.2 | 198 | 259.3 | 161.7
807 | 680 | 527 | 383.9 | 438.5 | 379.1 | 267.1 | 250.9 | 195.7 | 198.4 | 259.7 | 162
808 | 681 | 527 | 384.2 | 438.6 | 379.4 | 267.2 | 251.5 | 196.1 | 198.8 | 260.1 | 162.3
809 | 682 | 527 | 384.4 | 438.8 | 379.6 | 267.4 | 252 | 196.5 | 199.3 | 260.6 | 162.6
810 | 683 | 526.9 | 384.6 | 439 | 379.9 | 267.6 | 252.5 | 196.9 | 199.7 | 261 | 162.9
811 | 684 | 526.9 | 384.9 | 439.2 | 380.1 | 267.7 | 253 | 197.3 | 200.2 | 261.4 | 163.2
812 | 685 | 527 | 385.1 | 439.3 | 380.4 | 267.9 | 253.6 | 197.8 | 200.6 | 261.8 | 163.5
813 | 686 | 527 | 385.4 | 439.5 | 380.6 | 268.1 | 254.1 | 198.2 | 201 | 262.2 | 163.8
814 | 687 | 527 | 385.6 | 439.6 | 380.9 | 268.2 | 254.5 | 198.6 | 201.5 | 262.6 | 164.1
815 | 688 | 527 | 385.8 | 439.9 | 381.1 | 268.3 | 254.9 | 199 | 201.9 | 263.1 | 164.4
816 | 689 | 527 | 386.1 | 440.1 | 381.3 | 268.5 | 255.4 | 199.4 | 202.3 | 263.5 | 164.6
817 | 690 | 527 | 386.3 | 440.3 | 381.5 | 268.7 | 255.8 | 199.9 | 202.7 | 263.9 | 164.9
818 | 691 | 527.1 | 386.5 | 440.5 | 381.8 | 268.9 | 256.2 | 200.3 | 203 | 264.3 | 165.1
819 | 692 | 527.1 | 386.7 | 440.6 | 382 | 269.1 | 256.5 | 200.7 | 203.4 | 264.7 | 165.4
820 | 693 | 527.1 | 387 | 440.8 | 382.3 | 269.3 | 256.8 | 201.1 | 203.9 | 265.1 | 165.7
821 | 694 | 527.1 | 387.2 | 441 | 382.5 | 269.4 | 257.1 | 201.5 | 204.3 | 265.5 | 165.9
822 | 695 | 527.1 | 387.4 | 441.2 | 382.7 | 269.6 | 257.4 | 201.9 | 204.7 | 265.9 | 166.2
823 | 696 | 527.1 | 387.6 | 441.4 | 382.9 | 269.9 | 257.7 | 202.3 | 205.2 | 266.3 | 166.5
824 | 697 | 527.1 | 387.9 | 441.6 | 383.2 | 269.9 | 257.9 | 202.7 | 205.6 | 266.7 | 166.8
825 | 698 | 527.1 | 388.1 | 441.7 | 383.4 | 270.1 | 258.2 | 203.1 | 206 | 267.1 | 167.1
826 | 699 | 527.2 | 388.3 | 441.9 | 383.6 | 270.3 | 258.4 | 203.6 | 206.4 | 267.4 | 167.4
827 | 700 | 527.2 | 388.6 | 442.1 | 383.8 | 270.5 | 258.8 | 204 | 206.8 | 267.8 | 167.7
828 | 701 | 527.2 | 388.8 | 442.3 | 384.1 | 270.7 | 259.2 | 204.4 | 207.2 | 268.2 | 168
829 | 702 | 527.2 | 389 | 442.5 | 384.3 | 271 | 259.6 | 204.8 | 207.7 | 268.6 | 168.3
830 | 703 | 527.2 | 389.2 | 442.6 | 384.5 | 271.2 | 259.9 | 205.2 | 208.1 | 269 | 168.6
831 | 704 | 527.3 | 389.4 | 442.9 | 384.7 | 271.4 | 260.2 | 205.6 | 208.5 | 269.4 | 168.9
832 | 705 | 527.3 | 389.7 | 443 | 385 | 271.6 | 260.6 | 206 | 208.9 | 269.7 | 169.2
833 | 706 | 527.3 | 389.9 | 443.2 | 385.2 | 271.8 | 260.9 | 206.4 | 209.3 | 270.1 | 169.5
834 | 707 | 527.4 | 390.1 | 443.4 | 385.4 | 271.9 | 261.2 | 206.8 | 209.7 | 270.5 | 169.8
835 | 708 | 527.4 | 390.3 | 443.6 | 385.7 | 272.3 | 261.5 | 207.2 | 210.1 | 270.9 | 170.1
836 | 709 | 527.4 | 390.5 | 443.8 | 385.9 | 272.5 | 261.7 | 207.7 | 210.5 | 271.3 | 170.4
837 | 710 | 527.4 | 390.8 | 444 | 386.1 | 272.8 | 262 | 208.1 | 210.9 | 271.7 | 170.7
838 | 711 | 527.4 | 391 | 444.1 | 386.4 | 273 | 262.3 | 208.5 | 211.4 | 272.1 | 171
839 | 712 | 527.4 | 391.2 | 444.3 | 386.6 | 273.1 | 262.6 | 208.9 | 211.7 | 272.4 | 171.3
840 | 713 | 527.4 | 391.4 | 444.5 | 386.8 | 273.3 | 262.8 | 209.3 | 212.1 | 272.8 | 171.6
841 | 714 | 527.4 | 391.6 | 444.6 | 387 | 273.6 | 263.1 | 209.7 | 212.5 | 273.2 | 171.9
842 | 715 | 527.4 | 391.8 | 444.8 | 387.2 | 273.8 | 263.4 | 210.1 | 213 | 273.6 | 172.2
843 | 716 | 527.4 | 392.1 | 445 | 387.4 | 274 | 263.7 | 210.5 | 213.3 | 273.9 | 172.5
844 | 717 | 527.4 | 392.3 | 445.1 | 387.6 | 274.3 | 264 | 210.9 | 213.6 | 274.3 | 172.9
845 | 718 | 527.4 | 392.5 | 445.3 | 387.8 | 274.4 | 264.4 | 211.3 | 213.9 | 274.7 | 173.2
846 | 719 | 527.4 | 392.7 | 445.5 | 388.1 | 274.6 | 264.7 | 211.7 | 214.3 | 275.1 | 173.5
847 | 720 | 527.4 | 392.9 | 445.6 | 388.3 | 274.7 | 265.1 | 212.1 | 214.6 | 275.4 | 173.8
848 | 721 | 527.3 | 393.1 | 445.8 | 388.5 | 274.8 | 265.3 | 212.5 | 215 | 275.8 | 174.1
849 | 722 | 527.3 | 393.4 | 445.9 | 388.7 | 275 | 265.6 | 212.9 | 215.3 | 276.2 | 174.4
850 | 723 | 527.3 | 393.6 | 446.2 | 388.9 | 275.1 | 265.8 | 213.3 | 215.7 | 276.5 | 174.7
851 | 724 | 527.3 | 393.8 | 446.3 | 389.1 | 275.3 | 266.1 | 213.6 | 216 | 276.9 | 175.1
852 | 725 | 527.2 | 394 | 446.5 | 389.3 | 275.4 | 266.3 | 214 | 216.5 | 277.3 | 175.4
853 | 726 | 527.2 | 394.2 | 446.6 | 389.6 | 275.5 | 266.5 | 214.4 | 216.8 | 277.7 | 175.8
854 | 727 | 527.2 | 394.4 | 446.8 | 389.8 | 275.6 | 266.8 | 214.8 | 217.2 | 278 | 176.1
855 | 728 | 527.1 | 394.6 | 446.9 | 390 | 275.8 | 267.1 | 215.2 | 217.6 | 278.4 | 176.4
856 | 729 | 527.1 | 394.9 | 447.1 | 390.2 | 275.9 | 267.2 | 215.6 | 218 | 278.7 | 176.8
857 | 730 | 527.1 | 395 | 447.3 | 390.4 | 276 | 267.3 | 216 | 218.4 | 279.1 | 177.1
858 | 731 | 527.1 | 395.3 | 447.4 | 390.6 | 276.2 | 267.6 | 216.3 | 218.8 | 279.5 | 177.5
859 | 732 | 527.1 | 395.5 | 447.6 | 390.8 | 276.3 | 267.8 | 216.7 | 219.2 | 279.8 | 177.8
860 | 733 | 527 | 395.7 | 447.7 | 391.1 | 276.4 | 268.1 | 217.1 | 219.6 | 280.2 | 178.1
861 | 734 | 527 | 395.9 | 447.9 | 391.3 | 276.5 | 268.2 | 217.5 | 220 | 280.6 | 178.5
862 | 735 | 527 | 396.1 | 448 | 391.5 | 276.7 | 268.5 | 217.8 | 220.4 | 280.9 | 178.8
863 | 736 | 527 | 396.3 | 448.2 | 391.6 | 276.9 | 268.7 | 218.2 | 220.8 | 281.3 | 179.2
864 | 737 | 527 | 396.5 | 448.4 | 391.9 | 277 | 268.9 | 218.6 | 221.2 | 281.7 | 179.5
865 | 738 | 527 | 396.7 | 448.5 | 392.1 | 277.2 | 269.1 | 218.9 | 221.5 | 282.1 | 179.8
866 | 739 | 527 | 396.9 | 448.7 | 392.3 | 277.5 | 269.4 | 219.3 | 221.9 | 282.5 | 180.2
867 | 740 | 527 | 397.1 | 448.9 | 392.5 | 277.8 | 269.7 | 219.6 | 222.3 | 282.8 | 180.5
868 | 741 | 526.9 | 397.3 | 449 | 392.7 | 277.9 | 269.9 | 220 | 222.7 | 283.2 | 180.8
869 | 742 | 526.9 | 397.5 | 449.4 | 392.8 | 278 | 270.1 | 220.4 | 223.1 | 283.6 | 181.2
870 | 743 | 527 | 397.7 | 449.4 | 393.1 | 278.4 | 270.3 | 220.7 | 223.5 | 283.9 | 181.5
871 | 744 | 527 | 398 | 449.5 | 393.3 | 278.6 | 270.6 | 221.1 | 223.9 | 284.3 | 181.8
872 | 745 | 527 | 398.1 | 449.7 | 393.5 | 278.7 | 270.9 | 221.4 | 224.3 | 284.7 | 182.2
873 | 746 | 527 | 398.3 | 449.9 | 393.7 | 279 | 271.1 | 221.7 | 224.7 | 285 | 182.5
874 | 747 | 527 | 398.5 | 450 | 393.9 | 279.3 | 271.4 | 222.1 | 225.1 | 285.4 | 182.8
875 | 748 | 527.1 | 398.7 | 450.2 | 394.1 | 279.5 | 271.6 | 222.4 | 225.5 | 285.8 | 183.1
876 | 749 | 527.1 | 398.9 | 450.3 | 394.3 | 279.9 | 271.9 | 222.8 | 225.8 | 286.2 | 183.5
877 | 750 | 527.1 | 399.1 | 450.5 | 394.5 | 280.2 | 272.1 | 223.1 | 226.1 | 286.5 | 183.8
878 | 751 | 527.1 | 399.3 | 450.6 | 394.7 | 280.4 | 272.4 | 223.5 | 226.4 | 286.9 | 184.1
879 | 752 | 527.2 | 399.5 | 450.7 | 394.9 | 280.4 | 272.6 | 223.8 | 226.7 | 287.2 | 184.4
880 | 753 | 527.2 | 399.7 | 451 | 395.1 | 280.7 | 272.9 | 224.1 | 227 | 287.6 | 184.7
881 | 754 | 527.2 | 399.9 | 451.1 | 395.3 | 280.8 | 273.1 | 224.5 | 227.4 | 288 | 185.1
882 | 755 | 527.2 | 400.1 | 451.3 | 395.5 | 280.9 | 273.4 | 224.8 | 227.8 | 288.3 | 185.4
883 | 756 | 527.1 | 400.3 | 451.4 | 395.7 | 281.1 | 273.6 | 225.2 | 228.1 | 288.7 | 185.7
884 | 757 | 527.1 | 400.5 | 451.6 | 395.9 | 281.4 | 273.9 | 225.5 | 228.5 | 289.1 | 186
885 | 758 | 527.1 | 400.7 | 451.7 | 396.1 | 281.5 | 274.2 | 225.8 | 228.9 | 289.4 | 186.4
886 | 759 | 527.1 | 400.9 | 451.8 | 396.3 | 281.8 | 274.4 | 226.2 | 229.3 | 289.8 | 186.7
887 | 760 | 527.1 | 401.1 | 452 | 396.5 | 282.1 | 274.7 | 226.5 | 229.7 | 290.2 | 187
888 | 761 | 527.1 | 401.3 | 452.1 | 396.7 | 282.2 | 275 | 226.8 | 230.1 | 290.5 | 187.3
889 | 762 | 527.1 | 401.5 | 452.3 | 396.9 | 282.5 | 275.2 | 227.2 | 230.5 | 290.9 | 187.6
890 | 763 | 527.1 | 401.7 | 452.4 | 397.1 | 282.7 | 275.5 | 227.5 | 230.7 | 291.2 | 188
891 | 764 | 527.2 | 401.9 | 452.5 | 397.3 | 283 | 275.7 | 227.8 | 231.1 | 291.6 | 188.3
892 | 765 | 527.2 | 402.1 | 452.7 | 397.5 | 283.3 | 276 | 228.1 | 231.4 | 292 | 188.6
893 | 766 | 527.2 | 402.3 | 452.8 | 397.7 | 283.7 | 276.2 | 228.5 | 231.8 | 292.3 | 189
894 | 767 | 527.2 | 402.4 | 453 | 397.9 | 285.3 | 276.5 | 228.8 | 232.2 | 292.7 | 189.3
895 | 768 | 527.2 | 402.6 | 453.2 | 398 | 287.2 | 276.7 | 229.1 | 232.5 | 293 | 189.6
896 | 769 | 527.2 | 402.8 | 453.3 | 398.2 | 288.1 | 276.9 | 229.4 | 232.8 | 293.4 | 190
897 | 770 | 527.2 | 403 | 453.5 | 398.4 | 287.8 | 277.1 | 229.7 | 233.1 | 293.7 | 190.3
898 | 771 | 527.2 | 403.2 | 453.6 | 398.6 | 287.7 | 277.3 | 230.1 | 233.3 | 294.1 | 190.7
899 | 772 | 527.2 | 403.3 | 453.8 | 398.8 | 287.7 | 277.5 | 230.4 | 233.6 | 294.4 | 191
900 | 773 | 527.2 | 403.5 | 453.9 | 399 | 288 | 277.7 | 230.7 | 233.9 | 294.8 | 191.4
901 | 774 | 527.2 | 403.7 | 454 | 399.2 | 288.3 | 278 | 231 | 234.2 | 295.1 | 191.8
902 | 775 | 527.2 | 403.9 | 454.1 | 399.4 | 288.6 | 278.2 | 231.3 | 234.5 | 295.4 | 192.1
903 | 776 | 527.2 | 404.1 | 454.3 | 399.5 | 289 | 278.4 | 231.6 | 234.8 | 295.7 | 192.5
904 | 777 | 527.2 | 404.3 | 454.4 | 399.7 | 289.3 | 278.6 | 232 | 235.1 | 296.1 | 192.8
905 | 778 | 527.2 | 404.5 | 454.6 | 399.9 | 289.6 | 278.8 | 232.3 | 235.5 | 296.4 | 193.2
906 | 779 | 527.1 | 404.7 | 454.7 | 400.1 | 290 | 279.1 | 232.6 | 235.8 | 296.7 | 193.5
907 | 780 | 527.1 | 404.8 | 454.8 | 400.3 | 290.3 | 279.3 | 232.9 | 236.1 | 297 | 193.9
908 | 781 | 527.1 | 405 | 455 | 400.5 | 290.7 | 279.5 | 233.2 | 236.4 | 297.3 | 194.2
909 | 782 | 527 | 405.2 | 455.1 | 400.6 | 291.1 | 279.7 | 233.5 | 236.7 | 297.7 | 194.6
910 | 783 | 527 | 405.4 | 455.3 | 400.8 | 291.4 | 279.9 | 233.9 | 237.1 | 298 | 194.9
911 | 784 | 527 | 405.5 | 455.4 | 401 | 291.8 | 280.1 | 234.2 | 237.3 | 298.3 | 195.3
912 | 785 | 527 | 405.7 | 455.6 | 401.1 | 292.2 | 280.3 | 234.5 | 237.6 | 298.6 | 195.6
913 | 786 | 527 | 405.9 | 455.7 | 401.3 | 292.6 | 280.5 | 234.8 | 237.9 | 298.9 | 196
914 | 787 | 527 | 406.1 | 455.8 | 401.5 | 293.1 | 280.7 | 235.1 | 238.2 | 299.3 | 196.4
915 | 788 | 526.9 | 406.3 | 456 | 401.7 | 293.6 | 280.9 | 235.4 | 238.4 | 299.5 | 196.7
916 | 789 | 526.9 | 406.4 | 456.1 | 401.9 | 294.1 | 281.1 | 235.7 | 238.7 | 299.8 | 197.1
917 | 790 | 526.9 | 406.6 | 456.2 | 402.1 | 294.6 | 281.3 | 236 | 239 | 300.1 | 197.5
918 | 791 | 526.9 | 406.8 | 456.3 | 402.3 | 295.1 | 281.5 | 236.3 | 239.3 | 300.4 | 197.9
919 | 792 | 526.9 | 407 | 456.5 | 402.4 | 295.7 | 281.7 | 236.6 | 239.6 | 300.7 | 198.2
920 | 793 | 526.8 | 407.2 | 456.6 | 402.6 | 296.1 | 281.9 | 236.9 | 239.9 | 301.1 | 198.6
921 | 794 | 526.8 | 407.3 | 456.8 | 402.8 | 296.7 | 282.2 | 237.2 | 240.1 | 301.4 | 198.9
922 | 795 | 526.8 | 407.5 | 456.9 | 403 | 297.2 | 282.3 | 237.5 | 240.4 | 301.6 | 199.3
923 | 796 | 526.8 | 407.7 | 457 | 403.1 | 297.7 | 282.5 | 237.8 | 240.6 | 301.9 | 199.7
924 | 797 | 526.8 | 407.9 | 457.1 | 403.3 | 298.3 | 282.7 | 238.1 | 241 | 302.2 | 200
925 | 798 | 526.8 | 408 | 457.2 | 403.5 | 298.8 | 282.9 | 238.4 | 241.3 | 302.4 | 200.4
926 | 799 | 526.8 | 408.2 | 457.4 | 403.7 | 299.4 | 283.1 | 238.6 | 241.5 | 302.7 | 200.8
927 | 800 | 526.8 | 408.4 | 457.5 | 403.8 | 300.2 | 283.3 | 238.9 | 241.8 | 302.9 | 201.1
928 | 801 | 526.8 | 408.6 | 457.6 | 404 | 300.6 | 283.5 | 239.2 | 242.1 | 303.1 | 201.5
929 | 802 | 526.8 | 408.7 | 457.8 | 404.2 | 301.3 | 283.6 | 239.5 | 242.4 | 303.3 | 201.8
930 | 803 | 526.9 | 408.9 | 457.9 | 404.4 | 301.8 | 283.8 | 239.8 | 242.7 | 303.5 | 202.2
931 | 804 | 526.9 | 409.1 | 458.1 | 404.6 | 302.3 | 284 | 240 | 243 | 303.8 | 202.6
932 | 805 | 526.9 | 409.2 | 458.2 | 404.7 | 302.8 | 284.3 | 240.3 | 243.3 | 304 | 202.9
933 | 806 | 526.9 | 409.4 | 458.4 | 404.9 | 303.3 | 284.4 | 240.6 | 243.6 | 304.3 | 203.3
934 | 807 | 526.9 | 409.5 | 458.5 | 405.1 | 303.8 | 284.6 | 240.9 | 243.8 | 304.5 | 203.6
935 | 808 | 526.9 | 409.7 | 458.6 | 405.2 | 304.2 | 284.9 | 241.1 | 244.1 | 304.8 | 204
936 | 809 | 526.9 | 409.9 | 458.7 | 405.4 | 304.7 | 285.1 | 241.4 | 244.2 | 305.1 | 204.4
937 | 810 | 526.9 | 410.1 | 458.8 | 405.6 | 305.1 | 285.3 | 241.7 | 244.5 | 305.3 | 204.8
938 | 811 | 526.9 | 410.2 | 459 | 405.7 | 305.6 | 285.5 | 242 | 244.7 | 305.5 | 205.2
939 | 812 | 526.9 | 410.4 | 459.1 | 405.9 | 306 | 285.7 | 242.2 | 244.9 | 305.7 | 205.6
940 | 813 | 526.9 | 410.6 | 459.2 | 406.1 | 306.5 | 285.9 | 242.5 | 245.2 | 306 | 206
941 | 814 | 526.9 | 410.7 | 459.4 | 406.2 | 307 | 286.2 | 242.8 | 245.4 | 306.2 | 206.4
942 | 815 | 526.9 | 410.9 | 459.5 | 406.4 | 307.4 | 286.4 | 243 | 245.7 | 306.4 | 206.8
943 | 816 | 526.9 | 411.1 | 459.6 | 406.6 | 307.9 | 286.6 | 243.3 | 245.9 | 306.6 | 207.2
944 | 817 | 526.8 | 411.2 | 459.7 | 406.7 | 308.4 | 286.8 | 243.6 | 246.1 | 306.9 | 207.5
945 | 818 | 526.8 | 411.4 | 459.9 | 406.9 | 308.7 | 287.1 | 243.9 | 246.4 | 307.1 | 207.9
946 | 819 | 526.8 | 411.6 | 460 | 407.1 | 309.3 | 287.3 | 244.1 | 246.6 | 307.3 | 208.3
947 | 820 | 526.8 | 411.7 | 460.1 | 407.3 | 309.7 | 287.5 | 244.4 | 246.9 | 307.6 | 208.7
948 | 821 | 526.8 | 411.9 | 460.2 | 407.4 | 310.2 | 287.8 | 244.7 | 247.2 | 307.8 | 209
949 | 822 | 526.8 | 412.1 | 460.3 | 407.6 | 310.7 | 288.1 | 244.9 | 247.5 | 308.1 | 209.4
950 | 823 | 526.8 | 412.2 | 460.4 | 407.8 | 311.2 | 288.3 | 245.2 | 247.8 | 308.3 | 209.8
951 | 824 | 526.9 | 412.4 | 460.6 | 407.9 | 311.7 | 288.5 | 245.5 | 248 | 308.5 | 210.2
952 | 825 | 526.9 | 412.5 | 460.7 | 408.1 | 312.2 | 288.8 | 245.8 | 248.3 | 308.7 | 210.5
953 | 826 | 526.9 | 412.7 | 460.8 | 408.3 | 312.7 | 289.1 | 246 | 248.6 | 308.9 | 210.9
954 | 827 | 526.9 | 412.9 | 460.9 | 408.4 | 313.2 | 289.4 | 246.3 | 248.8 | 309.2 | 211.3
955 | 828 | 526.9 | 413 | 461.1 | 408.6 | 313.6 | 289.6 | 246.5 | 249 | 309.4 | 211.7
956 | 829 | 526.9 | 413.2 | 461.2 | 408.8 | 314 | 289.9 | 246.8 | 249.2 | 309.6 | 212.1
957 | 830 | 526.9 | 413.3 | 461.3 | 408.9 | 314.5 | 290.2 | 247.1 | 249.5 | 309.9 | 212.4
958 | 831 | 526.9 | 413.5 | 461.4 | 409.1 | 314.9 | 290.5 | 247.3 | 249.8 | 310.1 | 212.8
959 | 832 | 527 | 413.6 | 461.6 | 409.2 | 315.4 | 290.7 | 247.6 | 250.1 | 310.3 | 213.2
960 | 833 | 527 | 413.8 | 461.7 | 409.4 | 315.8 | 291 | 247.9 | 250.3 | 310.6 | 213.6
961 | 834 | 527 | 414 | 461.8 | 409.6 | 316.1 | 291.2 | 248.1 | 250.6 | 310.8 | 214
962 | 835 | 527 | 414.1 | 461.9 | 409.7 | 316.7 | 291.5 | 248.4 | 250.8 | 311 | 214.4
963 | 836 | 527 | 414.3 | 462 | 409.9 | 317.1 | 291.8 | 248.6 | 251.1 | 311.3 | 214.8
964 | 837 | 527 | 414.4 | 462.1 | 410.1 | 317.6 | 292.1 | 248.9 | 251.3 | 311.5 | 215.1
965 | 838 | 527 | 414.6 | 462.3 | 410.2 | 318.1 | 292.4 | 249.2 | 251.6 | 311.8 | 215.5
966 | 839 | 527.1 | 414.7 | 462.4 | 410.4 | 318.6 | 292.7 | 249.4 | 251.9 | 312.1 | 215.9
967 | 840 | 527.1 | 414.9 | 462.5 | 410.5 | 319.1 | 293 | 249.7 | 252.2 | 312.3 | 216.2
968 | 841 | 527.1 | 415 | 462.6 | 410.7 | 319.6 | 293.3 | 249.9 | 252.5 | 312.5 | 216.6
969 | 842 | 527.1 | 415.2 | 462.7 | 410.8 | 320 | 293.6 | 250.2 | 252.7 | 312.8 | 217
970 | 843 | 527.1 | 415.4 | 462.9 | 411 | 320.5 | 293.9 | 250.5 | 253 | 313 | 217.3
971 | 844 | 527.1 | 415.5 | 463 | 411.1 | 321.1 | 294.2 | 250.7 | 253.2 | 313.3 | 217.7
972 | 845 | 527.1 | 415.7 | 463.1 | 411.3 | 321.6 | 294.5 | 251 | 253.5 | 313.6 | 218.1
973 | 846 | 527.1 | 415.8 | 463.2 | 411.4 | 322.4 | 294.8 | 251.2 | 253.7 | 313.9 | 218.4
974 | 847 | 527.1 | 415.9 | 463.3 | 411.6 | 323 | 295.1 | 251.5 | 253.9 | 314.2 | 218.8
975 | 848 | 527.1 | 416.1 | 463.4 | 411.8 | 323.5 | 295.4 | 251.7 | 254.2 | 314.4 | 219.2
976 | 849 | 527 | 416.3 | 463.5 | 411.9 | 324 | 295.7 | 252 | 254.5 | 314.7 | 219.5
977 | 850 | 527 | 416.4 | 463.7 | 412.1 | 324.5 | 296 | 252.2 | 254.7 | 315 | 219.9
978 | 851 | 527 | 416.6 | 463.8 | 412.2 | 325 | 296.3 | 252.5 | 255 | 315.3 | 220.3
979 | 852 | 527 | 416.7 | 463.9 | 412.3 | 325.5 | 296.5 | 252.8 | 255.2 | 315.6 | 220.6
980 | 853 | 526.9 | 416.9 | 464 | 412.5 | 325.9 | 296.8 | 253 | 255.4 | 315.9 | 221
981 | 854 | 526.9 | 417 | 464.1 | 412.7 | 326.5 | 297.1 | 253.3 | 255.7 | 316.1 | 221.3
982 | 855 | 526.9 | 417.1 | 464.3 | 412.8 | 327 | 297.4 | 253.5 | 255.9 | 316.4 | 221.7
983 | 856 | 526.9 | 417.3 | 464.4 | 412.9 | 327.4 | 297.7 | 253.7 | 256.2 | 316.6 | 222
984 | 857 | 526.8 | 417.4 | 464.5 | 413.1 | 327.7 | 298.1 | 254 | 256.4 | 316.9 | 222.4
985 | 858 | 526.8 | 417.6 | 464.6 | 413.3 | 328 | 298.5 | 254.3 | 256.6 | 317.1 | 222.7
986 | 859 | 526.8 | 417.8 | 464.7 | 413.4 | 328.4 | 298.8 | 254.5 | 256.8 | 317.3 | 223.1
987 | 860 | 526.7 | 417.9 | 464.8 | 413.6 | 328.9 | 299.1 | 254.8 | 257.1 | 317.6 | 223.4
988 | 861 | 526.7 | 418.1 | 464.9 | 413.7 | 329.1 | 299.5 | 255.1 | 257.4 | 317.8 | 223.8
989 | 862 | 526.7 | 418.2 | 465 | 413.9 | 329.5 | 299.9 | 255.3 | 257.7 | 318.1 | 224.1
990 | 863 | 526.7 | 418.4 | 465.1 | 414 | 329.8 | 300.2 | 255.5 | 258 | 318.3 | 224.5
991 | 864 | 526.7 | 418.5 | 465.2 | 414.2 | 330.2 | 300.5 | 255.8 | 258.2 | 318.5 | 224.9
992 | 865 | 526.7 | 418.7 | 465.3 | 414.3 | 330.6 | 300.9 | 256 | 258.6 | 318.7 | 225.2
993 | 866 | 526.7 | 418.8 | 465.4 | 414.5 | 331 | 301.3 | 256.2 | 258.8 | 319 | 225.5
994 | 867 | 526.7 | 418.9 | 465.5 | 414.6 | 331.4 | 301.6 | 256.5 | 259.2 | 319.2 | 225.9
995 | 868 | 526.7 | 419.1 | 465.6 | 414.8 | 331.9 | 301.9 | 256.7 | 259.4 | 319.5 | 226.2
996 | 869 | 526.7 | 419.2 | 465.7 | 414.9 | 332.3 | 302.3 | 257 | 259.8 | 319.7 | 226.5
997 | 870 | 526.7 | 419.3 | 465.9 | 415.1 | 332.5 | 302.7 | 257.2 | 260.1 | 320 | 226.9
998 | 871 | 526.7 | 419.5 | 466 | 415.2 | 332.8 | 303.1 | 257.4 | 260.4 | 320.3 | 227.2
999 | 872 | 526.7 | 419.6 | 466.1 | 415.4 | 333 | 303.5 | 257.7 | 260.7 | 320.5 | 227.6
1000 | 873 | 526.7 | 419.8 | 466.2 | 415.5 | 333.3 | 303.9 | 257.9 | 260.9 | 320.8 | 227.9
1001 | 874 | 526.7 | 419.9 | 466.2 | 415.6 | 333.6 | 304.3 | 258.2 | 261.2 | 321.1 | 228.2
1002 | 875 | 526.6 | 420.1 | 466.4 | 415.8 | 334 | 304.6 | 258.4 | 261.5 | 321.4 | 228.6
1003 | 876 | 526.6 | 420.2 | 466.5 | 415.9 | 334.3 | 305 | 258.7 | 261.8 | 321.6 | 228.9
1004 | 877 | 526.6 | 420.3 | 466.6 | 416.1 | 334.6 | 305.3 | 258.9 | 262.1 | 321.9 | 229.2
1005 | 878 | 526.7 | 420.5 | 466.7 | 416.2 | 334.9 | 305.7 | 259.2 | 262.3 | 322.2 | 229.6
1006 | 879 | 526.7 | 420.6 | 466.8 | 416.3 | 335.2 | 306.1 | 259.4 | 262.6 | 322.5 | 229.9
1007 | 880 | 526.7 | 420.8 | 466.9 | 416.5 | 335.4 | 306.5 | 259.7 | 262.9 | 322.8 | 230.3
1008 | 881 | 526.7 | 420.9 | 467 | 416.6 | 335.6 | 307 | 259.9 | 263.2 | 323.1 | 230.6
1009 | 882 | 526.7 | 421.1 | 467.1 | 416.8 | 335.7 | 307.4 | 260.2 | 263.5 | 323.3 | 230.9
1010 | 883 | 526.7 | 421.2 | 467.2 | 416.9 | 336 | 307.9 | 260.4 | 263.8 | 323.6 | 231.3
1011 | 884 | 526.7 | 421.3 | 467.3 | 417.1 | 336.3 | 308.3 | 260.6 | 264.1 | 323.9 | 231.6
1012 | 885 | 526.7 | 421.5 | 467.4 | 417.2 | 336.6 | 308.7 | 260.9 | 264.3 | 324.1 | 231.9
1013 | 886 | 526.7 | 421.6 | 467.5 | 417.3 | 337 | 309 | 261.1 | 264.6 | 324.4 | 232.3
1014 | 887 | 526.7 | 421.7 | 467.7 | 417.5 | 337.2 | 309.3 | 261.4 | 264.8 | 324.7 | 232.6
1015 | 888 | 526.6 | 421.8 | 467.8 | 417.6 | 337.5 | 309.6 | 261.6 | 265.1 | 324.9 | 233
1016 | 889 | 526.6 | 422 | 467.8 | 417.7 | 337.9 | 310 | 261.8 | 265.4 | 325.2 | 233.3
1017 | 890 | 526.7 | 422.1 | 468 | 417.9 | 338.1 | 310.3 | 262.1 | 265.6 | 325.5 | 233.7
1018 | 891 | 526.7 | 422.2 | 468.1 | 418 | 338.5 | 310.7 | 262.3 | 265.9 | 325.7 | 234
1019 | 892 | 526.7 | 422.4 | 468.2 | 418.2 | 338.8 | 311.1 | 262.6 | 266.2 | 326 | 234.3
1020 | 893 | 526.7 | 422.5 | 468.2 | 418.3 | 339.1 | 311.4 | 262.8 | 266.4 | 326.3 | 234.7
1021 | 894 | 526.7 | 422.6 | 468.4 | 418.5 | 339.4 | 311.8 | 263.1 | 266.6 | 326.6 | 235
1022 | 895 | 526.7 | 422.8 | 468.4 | 418.6 | 339.7 | 312.2 | 263.3 | 266.9 | 326.8 | 235.4
1023 | 896 | 526.7 | 422.9 | 468.5 | 418.7 | 340 | 312.6 | 263.5 | 267.2 | 327.1 | 235.7
1024 | 897 | 526.7 | 423 | 468.6 | 418.9 | 340.2 | 313 | 263.8 | 267.5 | 327.4 | 236.1
1025 | 898 | 526.6 | 423.2 | 468.8 | 419 | 340.5 | 313.3 | 264 | 267.8 | 327.7 | 236.5
1026 | 899 | 526.6 | 423.3 | 468.8 | 419.2 | 340.7 | 313.6 | 264.3 | 268.1 | 328 | 236.9
1027 | 900 | 526.6 | 423.4 | 468.9 | 419.3 | 341 | 314.1 | 264.6 | 268.5 | 328.2 | 237.2
1028 | 901 | 526.6 | 423.6 | 469 | 419.4 | 341.2 | 314.5 | 264.8 | 268.8 | 328.5 | 237.6
1029 | 902 | 526.6 | 423.7 | 469.1 | 419.6 | 341.3 | 314.9 | 265.1 | 269.1 | 328.8 | 237.9
1030 | 903 | 526.6 | 423.8 | 469.2 | 419.7 | 341.5 | 315.3 | 265.3 | 269.3 | 329.1 | 238.2
1031 | 904 | 526.5 | 424 | 469.3 | 419.8 | 341.7 | 315.7 | 265.6 | 269.5 | 329.4 | 238.5
1032 | 905 | 526.5 | 424.1 | 469.4 | 420 | 341.9 | 316.1 | 265.8 | 269.8 | 329.7 | 238.9
1033 | 906 | 526.4 | 424.2 | 469.5 | 420.1 | 342 | 316.5 | 266.1 | 270 | 330 | 239.2
1034 | 907 | 526.4 | 424.4 | 469.6 | 420.3 | 342.1 | 316.8 | 266.3 | 270.3 | 330.3 | 239.6
1035 | 908 | 526.3 | 424.5 | 469.7 | 420.4 | 342.3 | 317.2 | 266.5 | 270.5 | 330.6 | 239.9
1036 | 909 | 526.3 | 424.6 | 469.8 | 420.5 | 342.6 | 317.6 | 266.8 | 270.7 | 330.8 | 240.2
1037 | 910 | 526.3 | 424.7 | 469.8 | 420.7 | 342.8 | 317.9 | 267 | 271 | 331.1 | 240.6
1038 | 911 | 526.3 | 424.9 | 469.9 | 420.8 | 343 | 318.2 | 267.2 | 271.2 | 331.4 | 240.9
1039 | 912 | 526.3 | 425 | 470 | 420.9 | 343.2 | 318.6 | 267.5 | 271.4 | 331.7 | 241.2
1040 | 913 | 526.3 | 425.1 | 470.1 | 421.1 | 343.3 | 318.9 | 267.7 | 271.6 | 331.9 | 241.5
1041 | 914 | 526.3 | 425.3 | 470.2 | 421.2 | 343.5 | 319.3 | 267.9 | 271.8 | 332.2 | 241.9
1042 | 915 | 526.3 | 425.4 | 470.3 | 421.3 | 343.6 | 319.7 | 268.2 | 272 | 332.4 | 242.2
1043 | 916 | 526.3 | 425.5 | 470.4 | 421.5 | 343.5 | 320 | 268.4 | 272.3 | 332.7 | 242.6
1044 | 917 | 526.4 | 425.7 | 470.5 | 421.6 | 343.5 | 320.4 | 268.7 | 272.5 | 333 | 242.9
1045 | 918 | 526.4 | 425.8 | 470.6 | 421.7 | 343.5 | 320.7 | 268.9 | 272.7 | 333.2 | 243.3
1046 | 919 | 526.5 | 425.9 | 470.7 | 421.9 | 343.6 | 321.2 | 269.2 | 272.9 | 333.5 | 243.6
1047 | 920 | 526.5 | 426 | 470.8 | 422 | 343.7 | 321.5 | 269.4 | 273.1 | 333.7 | 243.9
1048 | 921 | 526.5 | 426.2 | 470.9 | 422.1 | 343.9 | 321.8 | 269.7 | 273.3 | 334 | 244.3
1049 | 922 | 526.5 | 426.3 | 471 | 422.2 | 344 | 322.3 | 269.9 | 273.6 | 334.3 | 244.6
1050 | 923 | 526.5 | 426.4 | 471.1 | 422.4 | 344.1 | 322.7 | 270.2 | 273.9 | 334.5 | 244.9
1051 | 924 | 526.5 | 426.6 | 471.1 | 422.5 | 344.3 | 323.1 | 270.4 | 274.1 | 334.8 | 245.3
1052 | 925 | 526.5 | 426.7 | 471.2 | 422.6 | 344.2 | 323.4 | 270.7 | 274.4 | 335 | 245.6
1053 | 926 | 526.6 | 426.8 | 471.3 | 422.8 | 344.2 | 323.9 | 270.9 | 274.7 | 335.3 | 245.9
1054 | 927 | 526.6 | 427 | 471.4 | 422.9 | 344.4 | 324.3 | 271.2 | 274.9 | 335.5 | 246.2
1055 | 928 | 526.6 | 427.1 | 471.5 | 423 | 344.5 | 324.6 | 271.4 | 275.1 | 335.8 | 246.5
1056 | 929 | 526.6 | 427.2 | 471.6 | 423.2 | 344.7 | 324.9 | 271.7 | 275.3 | 336 | 246.8
1057 | 930 | 526.6 | 427.4 | 471.7 | 423.3 | 345 | 325.3 | 271.9 | 275.6 | 336.3 | 247.1
1058 | 931 | 526.7 | 427.5 | 471.8 | 423.4 | 345.1 | 325.7 | 272.2 | 275.8 | 336.5 | 247.4
1059 | 932 | 526.8 | 427.6 | 471.9 | 423.6 | 345.2 | 326.1 | 272.4 | 276 | 336.8 | 247.7
1060 | 933 | 526.8 | 427.7 | 472 | 423.7 | 345.3 | 326.4 | 272.7 | 276.2 | 337 | 248
1061 | 934 | 526.8 | 427.9 | 472.1 | 423.8 | 345.4 | 326.8 | 273 | 276.4 | 337.3 | 248.3
1062 | 935 | 526.8 | 428 | 472.2 | 424 | 345.7 | 327.1 | 273.2 | 276.7 | 337.5 | 248.7
1063 | 936 | 526.9 | 428.1 | 472.2 | 424.1 | 345.7 | 327.5 | 273.5 | 277 | 337.8 | 249
1064 | 937 | 526.9 | 428.2 | 472.3 | 424.2 | 345.9 | 327.9 | 273.8 | 277.2 | 338 | 249.2
1065 | 938 | 526.9 | 428.4 | 472.4 | 424.3 | 346 | 328.3 | 274 | 277.3 | 338.3 | 249.5
1066 | 939 | 526.9 | 428.5 | 472.5 | 424.5 | 346.2 | 328.6 | 274.3 | 277.5 | 338.5 | 249.8
1067 | 940 | 526.9 | 428.6 | 472.6 | 424.6 | 346.2 | 328.9 | 274.6 | 277.8 | 338.8 | 250.1
1068 | 941 | 526.9 | 428.7 | 472.7 | 424.7 | 346.7 | 329.3 | 274.8 | 278.1 | 339.1 | 250.4
1069 | 942 | 526.9 | 428.9 | 472.8 | 424.8 | 346.9 | 329.6 | 275.1 | 278.4 | 339.3 | 250.7
1070 | 943 | 526.9 | 429 | 472.9 | 425 | 347.1 | 329.9 | 275.3 | 278.6 | 339.6 | 251
1071 | 944 | 526.8 | 429.1 | 472.9 | 425.1 | 347.4 | 330.3 | 275.6 | 278.8 | 339.8 | 251.4
1072 | 945 | 526.8 | 429.2 | 473 | 425.2 | 347.6 | 330.6 | 275.9 | 279 | 340.1 | 251.7
1073 | 946 | 526.7 | 429.3 | 473.1 | 425.3 | 347.8 | 331 | 276.2 | 279.2 | 340.3 | 251.9
1074 | 947 | 526.7 | 429.5 | 473.2 | 425.5 | 348.1 | 331.3 | 276.4 | 279.5 | 340.6 | 252.2
1075 | 948 | 526.6 | 429.6 | 473.3 | 425.6 | 348.4 | 331.6 | 276.7 | 279.8 | 340.8 | 252.5
1076 | 949 | 526.6 | 429.7 | 473.4 | 425.7 | 348.6 | 331.9 | 277 | 280.1 | 341.1 | 252.7
1077 | 950 | 526.6 | 429.8 | 473.5 | 425.8 | 348.9 | 332.3 | 277.3 | 280.4 | 341.3 | 253
1078 | 951 | 526.6 | 430 | 473.6 | 425.9 | 349.1 | 332.6 | 277.5 | 280.6 | 341.6 | 253.3
1079 | 952 | 526.6 | 430.1 | 473.6 | 426.1 | 349.4 | 332.9 | 277.8 | 280.8 | 341.8 | 253.6
1080 | 953 | 526.6 | 430.2 | 473.7 | 426.2 | 349.7 | 333.3 | 278.1 | 281.2 | 342.1 | 253.9
1081 | 954 | 526.6 | 430.3 | 473.8 | 426.3 | 350.1 | 333.7 | 278.4 | 281.4 | 342.3 | 254.1
1082 | 955 | 526.6 | 430.5 | 473.9 | 426.4 | 350.3 | 334.1 | 278.6 | 281.6 | 342.6 | 254.4
1083 | 956 | 526.6 | 430.6 | 473.9 | 426.6 | 350.7 | 334.3 | 278.9 | 281.8 | 342.8 | 254.7
1084 | 957 | 526.6 | 430.7 | 474 | 426.7 | 351 | 334.6 | 279.2 | 282.1 | 343.1 | 254.9
1085 | 958 | 526.6 | 430.8 | 474.2 | 426.8 | 351.3 | 334.9 | 279.5 | 282.4 | 343.3 | 255.2
1086 | 959 | 526.6 | 431 | 474.2 | 426.9 | 351.5 | 335.2 | 279.7 | 282.6 | 343.5 | 255.4
1087 | 960 | 526.6 | 431.1 | 474.2 | 427.1 | 351.8 | 335.6 | 280 | 282.9 | 343.8 | 255.7
1088 | 961 | 526.6 | 431.2 | 474.3 | 427.2 | 352.1 | 335.9 | 280.3 | 283.3 | 344 | 256
1089 | 962 | 526.5 | 431.3 | 474.4 | 427.3 | 352.3 | 336.2 | 280.6 | 283.6 | 344.3 | 256.2
1090 | 963 | 526.5 | 431.4 | 474.5 | 427.4 | 352.6 | 336.5 | 280.9 | 283.9 | 344.5 | 256.4
1091 | 964 | 526.5 | 431.6 | 474.6 | 427.5 | 352.8 | 336.8 | 281.1 | 284.1 | 344.8 | 256.7
1092 | 965 | 526.5 | 431.7 | 474.6 | 427.7 | 353 | 337.1 | 281.4 | 284.3 | 345.1 | 257
1093 | 966 | 526.5 | 431.8 | 474.7 | 427.8 | 353.3 | 337.4 | 281.7 | 284.6 | 345.3 | 257.2
1094 | 967 | 526.6 | 431.9 | 474.8 | 427.9 | 353.5 | 337.7 | 282 | 284.8 | 345.6 | 257.5
1095 | 968 | 526.6 | 432 | 474.9 | 428 | 353.7 | 338 | 282.3 | 285 | 345.8 | 257.7
1096 | 969 | 526.6 | 432.1 | 475 | 428.1 | 354 | 338.2 | 282.6 | 285.3 | 346.1 | 258
1097 | 970 | 526.6 | 432.3 | 475.1 | 428.3 | 354.2 | 338.5 | 282.8 | 285.5 | 346.3 | 258.3
1098 | 971 | 526.6 | 432.4 | 475.2 | 428.4 | 354.5 | 338.8 | 283.1 | 285.7 | 346.6 | 258.5
1099 | 972 | 526.6 | 432.5 | 475.2 | 428.5 | 354.6 | 339.1 | 283.4 | 286 | 346.8 | 258.8
1100 | 973 | 526.6 | 432.6 | 475.3 | 428.6 | 354.9 | 339.5 | 283.7 | 286.2 | 347.1 | 259
1101 | 974 | 526.6 | 432.8 | 475.4 | 428.7 | 355.1 | 339.8 | 284 | 286.3 | 347.3 | 259.3
1102 | 975 | 526.7 | 432.9 | 475.5 | 428.9 | 355.3 | 340.1 | 284.2 | 286.5 | 347.6 | 259.5
1103 | 976 | 526.7 | 433 | 475.5 | 429 | 355.5 | 340.3 | 284.5 | 286.6 | 347.8 | 259.8
1104 | 977 | 526.7 | 433.1 | 475.6 | 429.1 | 355.7 | 340.6 | 284.8 | 286.8 | 348.1 | 260
1105 | 978 | 526.7 | 433.2 | 475.7 | 429.2 | 356.1 | 340.9 | 285.1 | 286.9 | 348.3 | 260.2
1106 | 979 | 526.7 | 433.3 | 475.8 | 429.3 | 356.4 | 341.2 | 285.4 | 287.1 | 348.6 | 260.5
1107 | 980 | 526.7 | 433.5 | 475.9 | 429.4 | 356.8 | 341.5 | 285.6 | 287.2 | 348.8 | 260.7
1108 | 981 | 526.7 | 433.6 | 475.9 | 429.5 | 357.2 | 341.8 | 285.9 | 287.4 | 349.1 | 261
1109 | 982 | 526.7 | 433.7 | 476 | 429.6 | 357.3 | 342 | 286.2 | 287.7 | 349.3 | 261.2
1110 | 983 | 526.6 | 433.8 | 476.1 | 429.8 | 357.6 | 342.3 | 286.5 | 287.9 | 349.6 | 261.4
1111 | 984 | 526.6 | 433.9 | 476.2 | 429.9 | 357.8 | 342.6 | 286.8 | 288.1 | 349.8 | 261.7
1112 | 985 | 526.7 | 434 | 476.2 | 430 | 358 | 342.9 | 287 | 288.3 | 350.1 | 261.9
1113 | 986 | 526.7 | 434.1 | 476.3 | 430.1 | 358.3 | 343.2 | 287.3 | 288.4 | 350.3 | 262.1
1114 | 987 | 526.7 | 434.2 | 476.4 | 430.2 | 358.5 | 343.4 | 287.6 | 288.6 | 350.6 | 262.4
1115 | 988 | 526.7 | 434.4 | 476.5 | 430.4 | 358.7 | 343.7 | 287.9 | 288.9 | 350.8 | 262.6
1116 | 989 | 526.7 | 434.5 | 476.6 | 430.5 | 358.8 | 344 | 288.1 | 289.2 | 351.1 | 262.9
1117 | 990 | 526.7 | 434.6 | 476.7 | 430.6 | 358.9 | 344.3 | 288.4 | 289.5 | 351.3 | 263.1
1118 | 991 | 526.8 | 434.7 | 476.7 | 430.7 | 359.1 | 344.5 | 288.7 | 289.6 | 351.6 | 263.4
1119 | 992 | 526.8 | 434.8 | 476.8 | 430.8 | 359.3 | 344.8 | 289 | 289.8 | 351.8 | 263.6
1120 | 993 | 526.8 | 434.9 | 476.9 | 430.9 | 359.4 | 345 | 289.3 | 290.1 | 352.1 | 263.8
1121 | 994 | 526.8 | 435 | 477 | 431 | 359.7 | 345.3 | 289.5 | 290.4 | 352.3 | 264.1
1122 | 995 | 526.8 | 435.1 | 477 | 431.1 | 359.9 | 345.6 | 289.8 | 290.7 | 352.5 | 264.3
1123 | 996 | 526.8 | 435.2 | 477.1 | 431.2 | 360.1 | 345.9 | 290.1 | 290.8 | 352.8 | 264.6
1124 | 997 | 526.8 | 435.3 | 477.2 | 431.4 | 360.2 | 346.1 | 290.4 | 291 | 353 | 264.8
1125 | 998 | 526.8 | 435.4 | 477.3 | 431.5 | 360.5 | 346.4 | 290.6 | 291.3 | 353.3 | 265
1126 | 999 | 526.8 | 435.6 | 477.3 | 431.6 | 360.7 | 346.7 | 290.9 | 291.5 | 353.5 | 265.3
1127 | 1000 | 526.8 | 435.7 | 477.4 | 431.7 | 360.7 | 346.9 | 291.2 | 291.7 | 353.7 | 265.5
1128 | 1001 | 526.8 | 435.8 | 477.4 | 431.8 | 360.9 | 347.2 | 291.4 | 292 | 354 | 265.7
1129 | 1002 | 526.8 | 435.9 | 477.5 | 431.9 | 361 | 347.5 | 291.7 | 292.2 | 354.2 | 266
1130 | 1003 | 526.8 | 436 | 477.6 | 432 | 361.1 | 347.7 | 292 | 292.5 | 354.4 | 266.2
1131 | 1004 | 526.8 | 436.1 | 477.7 | 432.1 | 361.4 | 347.9 | 292.2 | 292.8 | 354.6 | 266.4
1132 | 1005 | 526.8 | 436.2 | 477.7 | 432.2 | 361.6 | 348.2 | 292.5 | 293.2 | 354.9 | 266.7
1133 | 1006 | 526.8 | 436.3 | 477.8 | 432.4 | 361.9 | 348.5 | 292.8 | 293.5 | 355.1 | 266.9
1134 | 1007 | 526.7 | 436.5 | 477.8 | 432.5 | 362 | 348.7 | 293.1 | 293.7 | 355.3 | 267.1
1135 | 1008 | 526.7 | 436.6 | 477.9 | 432.6 | 362.3 | 349 | 293.3 | 293.9 | 355.5 | 267.4
1136 | 1009 | 526.7 | 436.7 | 478 | 432.7 | 362.4 | 349.2 | 293.6 | 294.1 | 355.7 | 267.6
1137 | 1010 | 526.7 | 436.8 | 478.1 | 432.8 | 362.7 | 349.5 | 293.9 | 294.4 | 356 | 267.8
1138 | 1011 | 526.7 | 436.9 | 478.2 | 432.9 | 362.8 | 349.7 | 294.1 | 294.7 | 356.2 | 268.1
1139 | 1012 | 526.6 | 437 | 478.2 | 433 | 363.1 | 350 | 294.4 | 295 | 356.4 | 268.3
1140 | 1013 | 526.6 | 437.1 | 478.2 | 433.1 | 363.3 | 350.2 | 294.6 | 295.4 | 356.6 | 268.5
1141 | 1014 | 526.6 | 437.2 | 478.3 | 433.2 | 363.5 | 350.5 | 294.9 | 295.6 | 356.9 | 268.7
1142 | 1015 | 526.6 | 437.3 | 478.4 | 433.3 | 363.7 | 350.7 | 295.2 | 295.8 | 357.1 | 268.9
1143 | 1016 | 526.6 | 437.4 | 478.4 | 433.4 | 364 | 351 | 295.5 | 295.9 | 357.3 | 269.2
1144 | 1017 | 526.6 | 437.5 | 478.5 | 433.6 | 364.2 | 351.2 | 295.7 | 296.2 | 357.6 | 269.4
1145 | 1018 | 526.6 | 437.6 | 478.6 | 433.7 | 364.4 | 351.5 | 296 | 296.5 | 357.8 | 269.6
1146 | 1019 | 526.6 | 437.7 | 478.7 | 433.8 | 364.7 | 351.7 | 296.3 | 296.8 | 358 | 269.8
1147 | 1020 | 526.6 | 437.8 | 478.7 | 433.9 | 364.9 | 352 | 296.5 | 296.9 | 358.3 | 270
1148 | 1021 | 526.6 | 437.9 | 478.8 | 434 | 365.2 | 352.3 | 296.8 | 297.1 | 358.5 | 270.2
1149 | 1022 | 526.6 | 438.1 | 478.9 | 434.1 | 365.5 | 352.5 | 297.1 | 297.4 | 358.7 | 270.5
1150 | 1023 | 526.6 | 438.2 | 478.9 | 434.2 | 365.7 | 352.7 | 297.3 | 297.7 | 358.9 | 270.7
1151 | 1024 | 526.5 | 438.3 | 479 | 434.3 | 365.9 | 352.9 | 297.6 | 297.9 | 359.2 | 270.9
1152 | 1025 | 526.5 | 438.4 | 479 | 434.4 | 366.1 | 353.2 | 297.9 | 298.1 | 359.4 | 271.1
1153 | 1026 | 526.5 | 438.5 | 479.1 | 434.5 | 366.3 | 353.5 | 298.1 | 298.4 | 359.6 | 271.3
1154 | 1027 | 526.5 | 438.6 | 479.2 | 434.6 | 366.5 | 353.7 | 298.4 | 298.6 | 359.8 | 271.6
1155 | 1028 | 526.5 | 438.7 | 479.3 | 434.7 | 366.6 | 354 | 298.7 | 298.7 | 360 | 271.8
1156 | 1029 | 526.5 | 438.8 | 479.4 | 434.8 | 366.9 | 354.2 | 298.9 | 298.9 | 360.2 | 272
1157 | 1030 | 526.5 | 438.9 | 479.4 | 434.9 | 367.1 | 354.4 | 299.2 | 299.2 | 360.4 | 272.2
1158 | 1031 | 526.6 | 439 | 479.5 | 435 | 367.5 | 354.6 | 299.5 | 299.5 | 360.6 | 272.4
1159 | 1032 | 526.6 | 439.1 | 479.6 | 435.2 | 367.6 | 354.9 | 299.7 | 299.7 | 360.8 | 272.7
1160 | 1033 | 526.6 | 439.2 | 479.7 | 435.3 | 367.7 | 355.1 | 300 | 299.8 | 361 | 272.9
1161 | 1034 | 526.6 | 439.3 | 479.7 | 435.4 | 368 | 355.4 | 300.3 | 300.2 | 361.3 | 273.1
1162 | 1035 | 526.6 | 439.4 | 479.8 | 435.5 | 368.1 | 355.6 | 300.5 | 300.5 | 361.4 | 273.3
1163 | 1036 | 526.6 | 439.4 | 479.9 | 435.6 | 368.4 | 355.8 | 300.8 | 300.6 | 361.6 | 273.5
1164 | 1037 | 526.6 | 439.5 | 480 | 435.7 | 368.6 | 356 | 301.1 | 300.9 | 361.8 | 273.7
1165 | 1038 | 526.7 | 439.6 | 480 | 435.7 | 368.8 | 356.3 | 301.3 | 301.2 | 362 | 274
1166 | 1039 | 526.7 | 439.7 | 480.1 | 435.8 | 369 | 356.5 | 301.6 | 301.3 | 362.2 | 274.2
1167 | 1040 | 526.7 | 439.9 | 480.2 | 436 | 369.2 | 356.7 | 301.9 | 301.6 | 362.4 | 274.4
1168 | 1041 | 526.7 | 439.9 | 480.2 | 436.1 | 369.4 | 357 | 302.2 | 301.8 | 362.7 | 274.6
1169 | 1042 | 526.7 | 440 | 480.3 | 436.1 | 369.7 | 357.2 | 302.4 | 302.2 | 362.9 | 274.8
1170 | 1043 | 526.7 | 440.1 | 480.4 | 436.2 | 369.9 | 357.4 | 302.7 | 302.4 | 363.1 | 275
1171 | 1044 | 526.7 | 440.3 | 480.4 | 436.4 | 370.2 | 357.7 | 303 | 302.7 | 363.3 | 275.3
1172 | 1045 | 526.7 | 440.4 | 480.5 | 436.5 | 370.4 | 357.9 | 303.3 | 303 | 363.5 | 275.5
1173 | 1046 | 526.7 | 440.5 | 480.5 | 436.6 | 370.5 | 358.2 | 303.5 | 303.1 | 363.7 | 275.7
1174 | 1047 | 526.7 | 440.6 | 480.6 | 436.7 | 370.8 | 358.4 | 303.8 | 303.3 | 363.9 | 275.9
1175 | 1048 | 526.7 | 440.6 | 480.7 | 436.8 | 371.1 | 358.6 | 304.1 | 303.7 | 364.1 | 276.1
1176 | 1049 | 526.7 | 440.8 | 480.7 | 436.9 | 371.2 | 358.9 | 304.4 | 304 | 364.3 | 276.3
1177 | 1050 | 526.6 | 440.9 | 480.7 | 437 | 371.4 | 359.1 | 304.6 | 304.2 | 364.5 | 276.5
1178 | 1051 | 526.6 | 440.9 | 480.8 | 437.1 | 371.5 | 359.3 | 304.9 | 304.4 | 364.7 | 276.8
1179 | 1052 | 526.6 | 441.1 | 480.9 | 437.2 | 371.7 | 359.5 | 305.2 | 304.6 | 364.9 | 277
1180 | 1053 | 526.6 | 441.1 | 481 | 437.2 | 372 | 359.7 | 305.4 | 304.9 | 365.1 | 277.2
1181 | 1054 | 526.6 | 441.2 | 481 | 437.3 | 372.2 | 359.9 | 305.7 | 305.1 | 365.3 | 277.4
1182 | 1055 | 526.6 | 441.3 | 481.1 | 437.4 | 372.3 | 360.1 | 306 | 305.2 | 365.5 | 277.6
1183 | 1056 | 526.6 | 441.4 | 481.2 | 437.5 | 372.5 | 360.4 | 306.3 | 305.5 | 365.7 | 277.8
1184 | 1057 | 526.5 | 441.5 | 481.3 | 437.6 | 372.8 | 360.6 | 306.5 | 305.7 | 365.9 | 278.1
1185 | 1058 | 526.5 | 441.6 | 481.3 | 437.7 | 372.9 | 360.8 | 306.8 | 306 | 366.1 | 278.2
1186 | 1059 | 526.5 | 441.7 | 481.4 | 437.8 | 373.1 | 361 | 307.1 | 306.2 | 366.3 | 278.5
1187 | 1060 | 526.5 | 441.8 | 481.5 | 437.9 | 373.4 | 361.3 | 307.3 | 306.4 | 366.5 | 278.7
1188 | 1061 | 526.4 | 441.9 | 481.5 | 438 | 373.6 | 361.5 | 307.6 | 306.7 | 366.7 | 278.9
1189 | 1062 | 526.4 | 442 | 481.6 | 438.1 | 373.7 | 361.7 | 307.9 | 306.9 | 366.9 | 279.1
1190 | 1063 | 526.4 | 442 | 481.7 | 438.2 | 374 | 361.9 | 308.1 | 307.1 | 367.1 | 279.3
1191 | 1064 | 526.3 | 442.1 | 481.7 | 438.3 | 374.2 | 362.1 | 308.4 | 307.3 | 367.3 | 279.5
1192 | 1065 | 526.3 | 442.2 | 481.8 | 438.4 | 374.5 | 362.3 | 308.7 | 307.5 | 367.5 | 279.8
1193 | 1066 | 526.3 | 442.3 | 481.8 | 438.5 | 374.6 | 362.5 | 309 | 307.8 | 367.7 | 280
1194 | 1067 | 526.3 | 442.4 | 481.9 | 438.6 | 374.9 | 362.7 | 309.2 | 308 | 367.9 | 280.2
1195 | 1068 | 526.3 | 442.5 | 482 | 438.7 | 375.1 | 363 | 309.5 | 308.2 | 368.1 | 280.4
1196 | 1069 | 526.3 | 442.6 | 482 | 438.7 | 375.4 | 363.2 | 309.8 | 308.5 | 368.3 | 280.7
1197 | 1070 | 526.3 | 442.7 | 482.1 | 438.8 | 375.6 | 363.4 | 310 | 308.7 | 368.5 | 280.9
1198 | 1071 | 526.3 | 442.8 | 482.1 | 438.9 | 376 | 363.6 | 310.3 | 309 | 368.7 | 281.1
1199 | 1072 | 526.3 | 442.9 | 482.2 | 439 | 376.1 | 363.8 | 310.5 | 309.2 | 368.9 | 281.4
1200 | 1073 | 526.3 | 443 | 482.2 | 439.1 | 376.4 | 364.1 | 310.8 | 309.5 | 369.1 | 281.6
1201 | 1074 | 526.3 | 443 | 482.3 | 439.2 | 376.6 | 364.3 | 311.1 | 309.6 | 369.3 | 281.9
1202 | 1075 | 526.3 | 443.1 | 482.4 | 439.3 | 376.9 | 364.5 | 311.3 | 310 | 369.4 | 282.1
1203 | 1076 | 526.3 | 443.3 | 482.4 | 439.4 | 377.1 | 364.7 | 311.6 | 310.3 | 369.6 | 282.3
1204 | 1077 | 526.3 | 443.3 | 482.5 | 439.5 | 377.5 | 364.9 | 311.9 | 310.6 | 369.8 | 282.6
1205 | 1078 | 526.3 | 443.4 | 482.5 | 439.6 | 377.7 | 365.1 | 312.1 | 310.8 | 370 | 282.8
1206 | 1079 | 526.3 | 443.5 | 482.6 | 439.7 | 378 | 365.3 | 312.4 | 311.1 | 370.2 | 283
1207 | 1080 | 526.3 | 443.6 | 482.6 | 439.8 | 378.2 | 365.4 | 312.6 | 311.4 | 370.4 | 283.2
1208 | 1081 | 526.3 | 443.7 | 482.7 | 439.9 | 378.5 | 365.6 | 312.9 | 311.7 | 370.6 | 283.5
1209 | 1082 | 526.3 | 443.8 | 482.8 | 440 | 378.7 | 365.8 | 313.2 | 312.1 | 370.8 | 283.7
1210 | 1083 | 526.3 | 443.9 | 482.8 | 440 | 378.9 | 365.9 | 313.4 | 312.3 | 371 | 283.9
1211 | 1084 | 526.4 | 443.9 | 482.9 | 440.1 | 379.2 | 366.1 | 313.7 | 312.6 | 371.1 | 284.1
1212 | 1085 | 526.4 | 444 | 483 | 440.2 | 379.4 | 366.3 | 314 | 312.9 | 371.3 | 284.3
1213 | 1086 | 526.4 | 444.1 | 483 | 440.3 | 379.8 | 366.6 | 314.2 | 313.1 | 371.5 | 284.5
1214 | 1087 | 526.4 | 444.2 | 483.1 | 440.4 | 380 | 366.8 | 314.5 | 313.4 | 371.7 | 284.8
1215 | 1088 | 526.5 | 444.3 | 483.1 | 440.5 | 380.3 | 367 | 314.7 | 313.8 | 371.9 | 285
1216 | 1089 | 526.5 | 444.4 | 483.1 | 440.6 | 380.6 | 367.2 | 315 | 314 | 372.1 | 285.2
1217 | 1090 | 526.5 | 444.5 | 483.2 | 440.7 | 380.8 | 367.4 | 315.2 | 314.3 | 372.2 | 285.4
1218 | 1091 | 526.5 | 444.6 | 483.3 | 440.8 | 381.2 | 367.7 | 315.5 | 314.6 | 372.4 | 285.6
1219 | 1092 | 526.5 | 444.7 | 483.3 | 440.8 | 381.5 | 367.9 | 315.7 | 314.9 | 372.6 | 285.8
1220 | 1093 | 526.5 | 444.8 | 483.4 | 440.9 | 381.7 | 368.1 | 316 | 315.2 | 372.8 | 286
1221 | 1094 | 526.5 | 444.9 | 483.5 | 441 | 382 | 368.3 | 316.2 | 315.5 | 372.9 | 286.2
1222 | 1095 | 526.5 | 445 | 483.5 | 441.1 | 382.3 | 368.6 | 316.5 | 315.8 | 373.1 | 286.4
1223 | 1096 | 526.5 | 445 | 483.6 | 441.2 | 382.6 | 368.8 | 316.7 | 316 | 373.3 | 286.6
1224 | 1097 | 526.4 | 445.1 | 483.6 | 441.3 | 382.9 | 369 | 317 | 316.3 | 373.4 | 286.9
1225 | 1098 | 526.4 | 445.2 | 483.7 | 441.3 | 383.1 | 369.2 | 317.2 | 316.6 | 373.6 | 287.1
1226 | 1099 | 526.4 | 445.3 | 483.7 | 441.4 | 383.4 | 369.4 | 317.5 | 316.8 | 373.8 | 287.3
1227 | 1100 | 526.4 | 445.4 | 483.8 | 441.5 | 383.6 | 369.6 | 317.7 | 317.2 | 373.9 | 287.5
1228 | 1101 | 526.4 | 445.5 | 483.9 | 441.6 | 383.9 | 369.8 | 318 | 317.5 | 374.1 | 287.7
1229 | 1102 | 526.4 | 445.5 | 483.9 | 441.7 | 384.2 | 370 | 318.2 | 317.8 | 374.3 | 287.9
1230 | 1103 | 526.5 | 445.6 | 484 | 441.8 | 384.4 | 370.2 | 318.5 | 318.2 | 374.4 | 288.1
1231 | 1104 | 526.5 | 445.7 | 484 | 441.9 | 384.7 | 370.4 | 318.8 | 318.4 | 374.6 | 288.3
1232 | 1105 | 526.5 | 445.8 | 484.1 | 441.9 | 384.9 | 370.6 | 319 | 318.7 | 374.8 | 288.5
1233 | 1106 | 526.5 | 445.9 | 484.1 | 442 | 385.2 | 370.8 | 319.3 | 318.9 | 374.9 | 288.7
1234 | 1107 | 526.5 | 446 | 484.2 | 442.1 | 385.5 | 371.1 | 319.5 | 319.1 | 375.1 | 288.9
1235 | 1108 | 526.5 | 446.1 | 484.2 | 442.2 | 385.8 | 371.3 | 319.7 | 319.4 | 375.3 | 289.1
1236 | 1109 | 526.5 | 446.1 | 484.3 | 442.3 | 386 | 371.5 | 320 | 319.6 | 375.4 | 289.4
1237 | 1110 | 526.5 | 446.2 | 484.4 | 442.4 | 386.3 | 371.7 | 320.2 | 319.8 | 375.6 | 289.6
1238 | 1111 | 526.5 | 446.3 | 484.4 | 442.5 | 386.5 | 371.9 | 320.4 | 320 | 375.7 | 289.8
1239 | 1112 | 526.5 | 446.4 | 484.5 | 442.6 | 386.7 | 372.1 | 320.7 | 320.2 | 375.9 | 290
1240 | 1113 | 526.5 | 446.5 | 484.5 | 442.7 | 387 | 372.3 | 320.9 | 320.4 | 376.1 | 290.2
1241 | 1114 | 526.5 | 446.6 | 484.5 | 442.7 | 387.2 | 372.5 | 321.2 | 320.6 | 376.2 | 290.4
1242 | 1115 | 526.5 | 446.7 | 484.6 | 442.8 | 387.3 | 372.8 | 321.4 | 320.9 | 376.4 | 290.5
1243 | 1116 | 526.5 | 446.7 | 484.8 | 442.9 | 387.3 | 372.9 | 321.7 | 321.2 | 376.6 | 290.7
1244 | 1117 | 526.5 | 446.6 | 485.2 | 442.8 | 386.9 | 373 | 322 | 321.5 | 376.8 | 291
1245 | 1118 | 526.5 | 446.6 | 485.2 | 442.9 | 387 | 373.2 | 322.3 | 321.8 | 376.9 | 291.2
1246 | 1119 | 526.5 | 446.7 | 485.3 | 443 | 387.2 | 373.4 | 322.5 | 322 | 377.1 | 291.3
1247 | 1120 | 526.5 | 446.8 | 485.3 | 443 | 387.4 | 373.7 | 322.8 | 322.2 | 377.3 | 291.6
1248 | 1121 | 526.5 | 446.9 | 485.4 | 443.1 | 387.6 | 373.9 | 323 | 322.5 | 377.4 | 291.8
1249 | 1122 | 526.6 | 447 | 485.5 | 443.2 | 387.8 | 374.1 | 323.2 | 322.7 | 377.6 | 292
1250 | 1123 | 526.6 | 447.1 | 485.5 | 443.3 | 388 | 374.4 | 323.5 | 323.1 | 377.7 | 292.1
1251 | 1124 | 526.6 | 447.1 | 485.6 | 443.4 | 388.1 | 374.6 | 323.7 | 323.4 | 377.9 | 292.3
1252 | 1125 | 526.6 | 447.2 | 485.6 | 443.5 | 388.3 | 374.8 | 324 | 323.7 | 378.1 | 292.5
1253 | 1126 | 526.6 | 447.3 | 485.7 | 443.5 | 388.4 | 375.1 | 324.3 | 323.9 | 378.2 | 292.7
1254 | 1127 | 526.6 | 447.4 | 485.7 | 443.6 | 388.6 | 375.3 | 324.5 | 324.2 | 378.3 | 292.9
1255 | 1128 | 526.6 | 447.5 | 485.8 | 443.7 | 388.7 | 375.6 | 324.7 | 324.5 | 378.5 | 293.1
1256 | 1129 | 526.6 | 447.5 | 485.9 | 443.8 | 388.9 | 375.8 | 325 | 324.8 | 378.6 | 293.3
1257 | 1130 | 526.7 | 447.6 | 485.9 | 443.9 | 389.1 | 376.1 | 325.2 | 325.1 | 378.8 | 293.4
1258 | 1131 | 526.7 | 447.7 | 486 | 443.9 | 389.3 | 376.3 | 325.5 | 325.4 | 378.9 | 293.6
1259 | 1132 | 526.7 | 447.8 | 486 | 444 | 389.5 | 376.6 | 325.8 | 325.7 | 379 | 293.8
1260 | 1133 | 526.7 | 447.9 | 486.1 | 444.1 | 389.6 | 376.8 | 326 | 325.9 | 379.2 | 294
1261 | 1134 | 526.6 | 447.9 | 486.1 | 444.2 | 389.9 | 377.1 | 326.2 | 326.1 | 379.4 | 294.2
1262 | 1135 | 526.6 | 448 | 486.2 | 444.3 | 390.1 | 377.3 | 326.5 | 326.4 | 379.5 | 294.4
1263 | 1136 | 526.6 | 448.1 | 486.2 | 444.4 | 390.2 | 377.6 | 326.7 | 326.6 | 379.7 | 294.6
1264 | 1137 | 526.6 | 448.2 | 486.3 | 444.4 | 390.4 | 377.8 | 327 | 327 | 379.8 | 294.8
1265 | 1138 | 526.6 | 448.3 | 486.3 | 444.5 | 390.6 | 378.1 | 327.2 | 327.3 | 380 | 295
1266 | 1139 | 526.6 | 448.4 | 486.3 | 444.6 | 390.8 | 378.4 | 327.5 | 327.6 | 380.1 | 295.2
1267 | 1140 | 526.6 | 448.4 | 486.4 | 444.7 | 391 | 378.6 | 327.8 | 328 | 380.3 | 295.4
1268 | 1141 | 526.6 | 448.5 | 486.4 | 444.8 | 391.2 | 378.9 | 328 | 328.4 | 380.5 | 295.6
1269 | 1142 | 526.6 | 448.6 | 486.5 | 444.8 | 391.3 | 379.1 | 328.3 | 328.7 | 380.6 | 295.8
1270 | 1143 | 526.6 | 448.7 | 486.6 | 444.9 | 391.6 | 379.4 | 328.5 | 328.9 | 380.8 | 296
1271 | 1144 | 526.6 | 448.7 | 486.6 | 445 | 391.8 | 379.7 | 328.8 | 329.2 | 381 | 296.2
1272 | 1145 | 526.6 | 448.8 | 486.7 | 445.1 | 392 | 379.9 | 329 | 329.6 | 381.1 | 296.4
1273 | 1146 | 526.6 | 448.9 | 486.7 | 445.1 | 392.2 | 380.2 | 329.3 | 329.9 | 381.3 | 296.6
1274 | 1147 | 526.6 | 449 | 486.8 | 445.2 | 392.4 | 380.4 | 329.6 | 330.2 | 381.5 | 296.8
1275 | 1148 | 526.6 | 449.1 | 486.8 | 445.3 | 392.6 | 380.6 | 329.8 | 330.6 | 381.6 | 297
1276 | 1149 | 526.6 | 449.1 | 486.9 | 445.4 | 392.8 | 380.9 | 330.1 | 331 | 381.8 | 297.2
1277 | 1150 | 526.6 | 449.2 | 486.9 | 445.5 | 393 | 381.1 | 330.3 | 331.4 | 382 | 297.3
1278 | 1151 | 526.6 | 449.3 | 487 | 445.5 | 393.2 | 381.4 | 330.6 | 331.8 | 382.1 | 297.5
1279 | 1152 | 526.6 | 449.4 | 487.1 | 445.6 | 393.4 | 381.6 | 330.8 | 332.2 | 382.3 | 297.7
1280 | 1153 | 526.6 | 449.4 | 487.1 | 445.7 | 393.6 | 381.9 | 331.1 | 332.6 | 382.5 | 297.9
1281 | 1154 | 526.6 | 449.5 | 487.2 | 445.8 | 393.8 | 382.1 | 331.4 | 332.9 | 382.6 | 298.1
1282 | 1155 | 526.6 | 449.6 | 487.2 | 445.9 | 394 | 382.4 | 331.6 | 333.1 | 382.8 | 298.3
1283 | 1156 | 526.6 | 449.7 | 487.3 | 445.9 | 394.2 | 382.6 | 331.9 | 333.3 | 383 | 298.5
1284 | 1157 | 526.6 | 449.7 | 487.3 | 446 | 394.4 | 382.9 | 332.1 | 333.6 | 383.2 | 298.7
1285 | 1158 | 526.6 | 449.8 | 487.4 | 446.1 | 394.6 | 383.1 | 332.4 | 333.8 | 383.3 | 298.8
1286 | 1159 | 526.6 | 449.9 | 487.4 | 446.2 | 394.8 | 383.4 | 332.6 | 334.1 | 383.5 | 299
1287 | 1160 | 526.6 | 450 | 487.5 | 446.2 | 395 | 383.6 | 332.9 | 334.3 | 383.6 | 299.2
1288 | 1161 | 526.6 | 450 | 487.5 | 446.3 | 395.2 | 383.8 | 333.2 | 334.6 | 383.8 | 299.3
1289 | 1162 | 526.6 | 450.1 | 487.6 | 446.4 | 395.4 | 384 | 333.4 | 334.9 | 384 | 299.5
1290 | 1163 | 526.6 | 450.2 | 487.6 | 446.5 | 395.6 | 384.2 | 333.7 | 335.1 | 384.2 | 299.7
1291 | 1164 | 526.5 | 450.3 | 487.6 | 446.5 | 395.8 | 384.3 | 334 | 335.3 | 384.3 | 299.8
1292 | 1165 | 526.5 | 450.3 | 487.7 | 446.6 | 396 | 384.6 | 334.2 | 335.4 | 384.5 | 300
1293 | 1166 | 526.5 | 450.4 | 487.7 | 446.7 | 396.2 | 384.8 | 334.5 | 335.6 | 384.7 | 300.2
1294 | 1167 | 526.5 | 450.5 | 487.8 | 446.8 | 396.4 | 385 | 334.8 | 335.8 | 384.8 | 300.4
1295 | 1168 | 526.5 | 450.6 | 487.8 | 446.9 | 396.6 | 385.2 | 335 | 336 | 385 | 300.5
1296 | 1169 | 526.4 | 450.6 | 487.9 | 446.9 | 396.8 | 385.4 | 335.3 | 336.2 | 385.2 | 300.6
1297 | 1170 | 526.4 | 450.7 | 487.9 | 447 | 397 | 385.6 | 335.6 | 336.4 | 385.3 | 300.8
1298 | 1171 | 526.4 | 450.8 | 488 | 447.1 | 397.2 | 385.8 | 335.8 | 336.7 | 385.5 | 300.9
1299 | 1172 | 526.4 | 450.9 | 488 | 447.2 | 397.4 | 386 | 336.1 | 337 | 385.7 | 301.1
1300 | 1173 | 526.4 | 450.9 | 488 | 447.3 | 397.6 | 386.2 | 336.4 | 337.3 | 385.8 | 301.2
1301 | 1174 | 526.3 | 451 | 488.1 | 447.3 | 397.8 | 386.4 | 336.7 | 337.6 | 386 | 301.3
1302 | 1175 | 526.3 | 451.1 | 488.2 | 447.4 | 398 | 386.6 | 336.9 | 337.8 | 386.1 | 301.5
1303 | 1176 | 526.3 | 451.2 | 488.2 | 447.5 | 398.2 | 386.8 | 337.2 | 338 | 386.3 | 301.7
1304 | 1177 | 526.4 | 451.2 | 488.3 | 447.5 | 398.4 | 387.1 | 337.5 | 338.2 | 386.5 | 301.8
1305 | 1178 | 526.4 | 451.3 | 488.3 | 447.6 | 398.6 | 387.3 | 337.8 | 338.5 | 386.6 | 302
1306 | 1179 | 526.4 | 451.4 | 488.3 | 447.7 | 398.8 | 387.5 | 338.1 | 338.7 | 386.8 | 302.1
1307 | 1180 | 526.4 | 451.5 | 488.3 | 447.8 | 399 | 387.7 | 338.4 | 339 | 387 | 302.3
1308 | 1181 | 526.5 | 451.5 | 488.4 | 447.8 | 399.2 | 387.9 | 338.6 | 339.3 | 387.1 | 302.5
1309 | 1182 | 526.5 | 451.6 | 488.5 | 447.9 | 399.3 | 388.2 | 338.9 | 339.6 | 387.3 | 302.6
1310 | 1183 | 526.5 | 451.7 | 488.5 | 448 | 399.5 | 388.4 | 339.2 | 339.8 | 387.5 | 302.8
1311 | 1184 | 526.5 | 451.7 | 488.6 | 448.1 | 399.7 | 388.6 | 339.5 | 340.1 | 387.6 | 302.9
1312 | 1185 | 526.5 | 451.8 | 488.6 | 448.1 | 399.9 | 388.8 | 339.8 | 340.3 | 387.8 | 303.1
1313 | 1186 | 526.4 | 451.9 | 488.7 | 448.2 | 400.1 | 389 | 340.1 | 340.5 | 388 | 303.3
1314 | 1187 | 526.4 | 451.9 | 488.7 | 448.3 | 400.2 | 389.2 | 340.3 | 340.8 | 388.1 | 303.5
1315 | 1188 | 526.4 | 452 | 488.7 | 448.3 | 400.4 | 389.4 | 340.6 | 341 | 388.3 | 303.6
1316 | 1189 | 526.4 | 452.1 | 488.8 | 448.4 | 400.6 | 389.6 | 340.9 | 341.2 | 388.5 | 303.8
1317 | 1190 | 526.3 | 452.2 | 488.8 | 448.5 | 400.8 | 389.8 | 341.2 | 341.5 | 388.6 | 304
1318 | 1191 | 526.3 | 452.2 | 488.9 | 448.6 | 401 | 390 | 341.5 | 341.7 | 388.8 | 304.1
1319 | 1192 | 526.3 | 452.3 | 488.9 | 448.7 | 401.2 | 390.2 | 341.8 | 342 | 389 | 304.3
1320 | 1193 | 526.3 | 452.4 | 489 | 448.7 | 401.3 | 390.4 | 342 | 342.3 | 389.1 | 304.5
1321 | 1194 | 526.3 | 452.5 | 489 | 448.8 | 401.5 | 390.6 | 342.3 | 342.6 | 389.3 | 304.6
1322 | 1195 | 526.3 | 452.5 | 489 | 448.9 | 401.7 | 390.8 | 342.6 | 342.9 | 389.5 | 304.8
1323 | 1196 | 526.3 | 452.6 | 489.1 | 448.9 | 401.9 | 391.1 | 342.9 | 343.3 | 389.7 | 305
1324 | 1197 | 526.2 | 452.7 | 489.1 | 449 | 402.1 | 391.3 | 343.1 | 343.5 | 389.8 | 305.1
1325 | 1198 | 526.2 | 452.7 | 489.2 | 449.1 | 402.3 | 391.5 | 343.4 | 343.8 | 390 | 305.3
1326 | 1199 | 526.2 | 452.8 | 489.2 | 449.1 | 402.6 | 391.7 | 343.7 | 344.1 | 390.1 | 305.4
1327 | 1200 | 526.1 | 452.8 | 489.3 | 449.2 | 402.7 | 391.9 | 343.9 | 344.3 | 390.3 | 305.6
1328 | 1201 | 526.1 | 452.9 | 489.3 | 449.3 | 402.9 | 392.2 | 344.2 | 344.7 | 390.5 | 305.7
1329 | 1202 | 526.1 | 453 | 489.3 | 449.4 | 403.1 | 392.4 | 344.5 | 344.9 | 390.6 | 305.9
1330 | 1203 | 526.1 | 453.1 | 489.4 | 449.4 | 403.3 | 392.6 | 344.8 | 345.2 | 390.8 | 306.1
1331 | 1204 | 526.1 | 453.1 | 489.4 | 449.5 | 403.5 | 392.8 | 345.1 | 345.4 | 391 | 306.2
1332 | 1205 | 526.1 | 453.2 | 489.4 | 449.6 | 403.7 | 393.1 | 345.3 | 345.6 | 391.1 | 306.4
1333 | 1206 | 526.1 | 453.2 | 489.5 | 449.6 | 403.9 | 393.3 | 345.6 | 345.9 | 391.3 | 306.5
1334 | 1207 | 526.1 | 453.3 | 489.6 | 449.7 | 404 | 393.5 | 345.9 | 346.1 | 391.5 | 306.7
1335 | 1208 | 526 | 453.4 | 489.6 | 449.8 | 404.2 | 393.7 | 346.1 | 346.4 | 391.6 | 306.9
1336 | 1209 | 526 | 453.5 | 489.6 | 449.9 | 404.4 | 394 | 346.4 | 346.6 | 391.8 | 307
1337 | 1210 | 526 | 453.5 | 489.7 | 449.9 | 404.6 | 394.2 | 346.7 | 346.9 | 392 | 307.2
1338 | 1211 | 526 | 453.6 | 489.7 | 450 | 404.8 | 394.4 | 347 | 347.2 | 392.1 | 307.3
1339 | 1212 | 526 | 453.7 | 489.7 | 450.1 | 405 | 394.6 | 347.2 | 347.5 | 392.3 | 307.5
1340 | 1213 | 526.1 | 453.7 | 489.8 | 450.1 | 405.2 | 394.7 | 347.5 | 347.8 | 392.4 | 307.6
1341 | 1214 | 526.1 | 453.8 | 489.8 | 450.2 | 405.3 | 394.9 | 347.8 | 348 | 392.6 | 307.8
1342 | 1215 | 526.1 | 453.9 | 489.8 | 450.3 | 405.5 | 395.1 | 348.1 | 348.2 | 392.8 | 308
1343 | 1216 | 526.1 | 453.9 | 489.9 | 450.3 | 405.7 | 395.3 | 348.4 | 348.4 | 392.9 | 308.1
1344 | 1217 | 526.2 | 454 | 489.9 | 450.4 | 405.9 | 395.5 | 348.6 | 348.7 | 393.1 | 308.3
1345 | 1218 | 526.2 | 454.1 | 490 | 450.5 | 406.1 | 395.7 | 348.9 | 348.9 | 393.2 | 308.4
1346 | 1219 | 526.2 | 454.1 | 490 | 450.5 | 406.3 | 395.9 | 349.2 | 349.2 | 393.4 | 308.6
1347 | 1220 | 526.2 | 454.2 | 490 | 450.6 | 406.5 | 396.1 | 349.5 | 349.4 | 393.6 | 308.7
1348 | 1221 | 526.2 | 454.2 | 490.1 | 450.7 | 406.7 | 396.3 | 349.8 | 349.6 | 393.7 | 308.9
1349 | 1222 | 526.2 | 454.3 | 490.2 | 450.7 | 406.9 | 396.5 | 350.1 | 349.8 | 393.9 | 309
1350 | 1223 | 526.2 | 454.4 | 490.2 | 450.8 | 407 | 396.7 | 350.4 | 350.1 | 394.1 | 309.2
1351 | 1224 | 526.2 | 454.4 | 490.3 | 450.9 | 407.2 | 396.9 | 350.7 | 350.4 | 394.2 | 309.4
1352 | 1225 | 526.2 | 454.5 | 490.3 | 450.9 | 407.4 | 397.1 | 350.9 | 350.7 | 394.4 | 309.5
1353 | 1226 | 526.3 | 454.5 | 490.4 | 451 | 407.6 | 397.3 | 351.2 | 350.9 | 394.5 | 309.7
1354 | 1227 | 526.3 | 454.6 | 490.4 | 451.1 | 407.9 | 397.5 | 351.5 | 351.2 | 394.7 | 309.8
1355 | 1228 | 526.3 | 454.7 | 490.4 | 451.1 | 408.1 | 397.7 | 351.8 | 351.5 | 394.9 | 310
1356 | 1229 | 526.4 | 454.7 | 490.4 | 451.2 | 408.3 | 398 | 352 | 351.8 | 395 | 310.1
1357 | 1230 | 526.4 | 454.8 | 490.5 | 451.3 | 408.5 | 398.2 | 352.3 | 352.1 | 395.2 | 310.3
1358 | 1231 | 526.4 | 454.9 | 490.5 | 451.3 | 408.7 | 398.2 | 352.6 | 352.3 | 395.3 | 310.4
1359 | 1232 | 526.4 | 454.9 | 490.6 | 451.4 | 409 | 398.1 | 352.9 | 352.6 | 395.5 | 310.6
1360 | 1233 | 526.4 | 455 | 490.6 | 451.5 | 409.2 | 398.2 | 353.1 | 352.8 | 395.6 | 310.7
1361 | 1234 | 526.4 | 455.1 | 490.7 | 451.6 | 409.5 | 398.3 | 353.4 | 353.1 | 395.8 | 310.9
1362 | 1235 | 526.4 | 455.1 | 490.7 | 451.6 | 409.8 | 398.4 | 353.6 | 353.3 | 396 | 311.1
1363 | 1236 | 526.4 | 455.2 | 490.7 | 451.7 | 410.1 | 398.6 | 353.9 | 353.6 | 396.1 | 311.2
1364 | 1237 | 526.4 | 455.2 | 490.8 | 451.7 | 410.3 | 398.8 | 354.1 | 353.8 | 396.3 | 311.4
1365 | 1238 | 526.4 | 455.3 | 490.8 | 451.8 | 410.6 | 399 | 354.4 | 354 | 396.4 | 311.5
1366 | 1239 | 526.4 | 455.4 | 490.8 | 451.9 | 410.9 | 399.2 | 354.7 | 354.2 | 396.6 | 311.7
1367 | 1240 | 526.4 | 455.4 | 490.9 | 451.9 | 411.2 | 399.4 | 354.9 | 354.5 | 396.7 | 311.9
1368 | 1241 | 526.4 | 455.5 | 490.9 | 452 | 411.5 | 399.6 | 355.2 | 354.8 | 396.9 | 312
1369 | 1242 | 526.3 | 455.6 | 490.9 | 452.1 | 411.7 | 399.9 | 355.5 | 355 | 397 | 312.2
1370 | 1243 | 526.3 | 455.6 | 491 | 452.1 | 412 | 400.1 | 355.8 | 355.3 | 397.2 | 312.4
1371 | 1244 | 526.3 | 455.7 | 491 | 452.2 | 412.3 | 400.3 | 356 | 355.6 | 397.4 | 312.6
1372 | 1245 | 526.2 | 455.7 | 491 | 452.3 | 412.6 | 400.6 | 356.3 | 355.8 | 397.5 | 312.7
1373 | 1246 | 526.2 | 455.8 | 491 | 452.4 | 412.9 | 400.8 | 356.6 | 356.1 | 397.6 | 312.9
1374 | 1247 | 526.1 | 455.9 | 491.1 | 452.4 | 413.2 | 401.1 | 356.9 | 356.3 | 397.8 | 313.1
1375 | 1248 | 526.1 | 456 | 491.1 | 452.5 | 413.5 | 401.3 | 357.1 | 356.5 | 397.9 | 313.3
1376 | 1249 | 526.1 | 456 | 491.1 | 452.6 | 413.7 | 401.6 | 357.4 | 356.8 | 398.1 | 313.4
1377 | 1250 | 526.1 | 456.1 | 491.2 | 452.6 | 414 | 401.8 | 357.7 | 357.1 | 398.2 | 313.6
1378 | 1251 | 526.1 | 456.1 | 491.2 | 452.7 | 414.2 | 402.1 | 358 | 357.4 | 398.4 | 313.8
1379 | 1252 | 526.1 | 456.2 | 491.3 | 452.7 | 414.5 | 402.3 | 358.3 | 357.7 | 398.5 | 313.9
1380 | 1253 | 526.1 | 456.3 | 491.3 | 452.8 | 414.8 | 402.6 | 358.6 | 358 | 398.7 | 314.1
1381 | 1254 | 526.2 | 456.3 | 491.3 | 452.9 | 415.1 | 402.9 | 358.9 | 358.2 | 398.8 | 314.3
1382 | 1255 | 526.2 | 456.4 | 491.4 | 452.9 | 415.4 | 403.1 | 359.2 | 358.6 | 399 | 314.4
1383 | 1256 | 526.2 | 456.4 | 491.4 | 453 | 415.6 | 403.4 | 359.5 | 358.9 | 399.1 | 314.6
1384 | 1257 | 526.2 | 456.5 | 491.4 | 453.1 | 415.9 | 403.6 | 359.8 | 359.2 | 399.3 | 314.8
1385 | 1258 | 526.2 | 456.6 | 491.5 | 453.1 | 416.2 | 403.9 | 360.1 | 359.4 | 399.4 | 314.9
1386 | 1259 | 526.2 | 456.6 | 491.5 | 453.2 | 416.4 | 404.2 | 360.4 | 359.7 | 399.6 | 315.1
1387 | 1260 | 526.2 | 456.7 | 491.6 | 453.2 | 416.7 | 404.4 | 360.7 | 360 | 399.7 | 315.3
1388 | 1261 | 526.2 | 456.7 | 491.6 | 453.3 | 417 | 404.7 | 361 | 360.4 | 399.9 | 315.5
1389 | 1262 | 526.2 | 456.8 | 491.6 | 453.4 | 417.2 | 405 | 361.3 | 360.7 | 400 | 315.6
1390 | 1263 | 526.3 | 456.9 | 491.7 | 453.4 | 417.5 | 405.2 | 361.6 | 361 | 400.2 | 315.8
1391 | 1264 | 526.3 | 456.9 | 491.7 | 453.5 | 417.8 | 405.5 | 361.9 | 361.2 | 400.3 | 316
1392 | 1265 | 526.3 | 457 | 491.7 | 453.5 | 418.1 | 405.8 | 362.2 | 361.5 | 400.5 | 316.1
1393 | 1266 | 526.3 | 457 | 491.8 | 453.6 | 418.4 | 406 | 362.5 | 361.7 | 400.6 | 316.3
1394 | 1267 | 526.3 | 457.1 | 491.8 | 453.7 | 418.6 | 406.3 | 362.8 | 362 | 400.8 | 316.5
1395 | 1268 | 526.2 | 457.1 | 491.9 | 453.7 | 419 | 406.5 | 363 | 362.2 | 400.9 | 316.7
1396 | 1269 | 526.2 | 457.2 | 491.9 | 453.8 | 419.3 | 406.8 | 363.3 | 362.5 | 401.1 | 316.9
1397 | 1270 | 526.2 | 457.3 | 492 | 453.8 | 419.6 | 407 | 363.6 | 362.8 | 401.2 | 317.1
1398 | 1271 | 526.2 | 457.3 | 492 | 453.9 | 419.8 | 407.3 | 363.9 | 363 | 401.4 | 317.2
1399 | 1272 | 526.2 | 457.4 | 492 | 454 | 420.2 | 407.5 | 364.2 | 363.3 | 401.5 | 317.4
1400 | 1273 | 526.2 | 457.4 | 492 | 454 | 420.5 | 407.8 | 364.5 | 363.6 | 401.6 | 317.6
1401 | 1274 | 526.2 | 457.5 | 492.1 | 454.1 | 420.7 | 408 | 364.8 | 364 | 401.8 | 317.8
1402 | 1275 | 526.2 | 457.5 | 492.1 | 454.2 | 421 | 408.3 | 365.1 | 364.2 | 401.9 | 318
1403 | 1276 | 526.2 | 457.6 | 492.2 | 454.2 | 421.3 | 408.5 | 365.4 | 364.5 | 402.1 | 318.2
1404 | 1277 | 526.2 | 457.7 | 492.2 | 454.3 | 421.6 | 408.7 | 365.7 | 364.7 | 402.2 | 318.4
1405 | 1278 | 526.2 | 457.7 | 492.2 | 454.3 | 421.9 | 409 | 366 | 364.9 | 402.4 | 318.6
1406 | 1279 | 526.2 | 457.8 | 492.3 | 454.4 | 422.2 | 409.2 | 366.2 | 365.1 | 402.5 | 318.8
1407 | 1280 | 526.2 | 457.8 | 492.3 | 454.5 | 422.5 | 409.4 | 366.5 | 365.4 | 402.7 | 319
1408 | 1281 | 526.2 | 457.9 | 492.4 | 454.5 | 422.8 | 409.6 | 366.8 | 365.7 | 402.8 | 319.3
1409 | 1282 | 526.2 | 457.9 | 492.4 | 454.6 | 423 | 409.8 | 367 | 366 | 402.9 | 319.5
1410 | 1283 | 526.2 | 458 | 492.4 | 454.6 | 423.4 | 410 | 367.2 | 366.2 | 403.1 | 319.7
1411 | 1284 | 526.2 | 458.1 | 492.4 | 454.7 | 423.7 | 410.2 | 367.5 | 366.5 | 403.2 | 320
1412 | 1285 | 526.2 | 458.2 | 492.4 | 454.8 | 424 | 410.4 | 367.7 | 366.8 | 403.4 | 320.3
1413 | 1286 | 526.2 | 458.3 | 492.2 | 454.9 | 424.5 | 410.7 | 367.9 | 367 | 403.5 | 320.5
1414 | 1287 | 526.2 | 458.2 | 492.5 | 454.9 | 424.6 | 410.7 | 368.1 | 367.3 | 403.6 | 320.8
1415 | 1288 | 526.3 | 458.3 | 492.5 | 454.9 | 424.8 | 410.9 | 368.4 | 367.5 | 403.8 | 321
1416 | 1289 | 526.3 | 458.4 | 492.6 | 455 | 425.1 | 411.1 | 368.6 | 367.8 | 403.9 | 321.3
1417 | 1290 | 526.3 | 458.4 | 492.6 | 455 | 425.4 | 411.2 | 368.8 | 368 | 404.1 | 321.5
1418 | 1291 | 526.3 | 458.5 | 492.7 | 455.1 | 425.6 | 411.4 | 369 | 368.2 | 404.2 | 321.8
1419 | 1292 | 526.3 | 458.5 | 492.8 | 455.1 | 425.9 | 411.5 | 369.2 | 368.5 | 404.4 | 322.1
1420 | 1293 | 526.3 | 458.6 | 492.8 | 455.2 | 426.2 | 411.7 | 369.4 | 368.8 | 404.5 | 322.3
1421 | 1294 | 526.3 | 458.7 | 492.6 | 455.3 | 426.6 | 411.9 | 369.6 | 369.1 | 404.6 | 322.6
1422 | 1295 | 526.3 | 458.7 | 492.8 | 455.3 | 426.8 | 412 | 369.8 | 369.3 | 404.8 | 322.8
1423 | 1296 | 526.4 | 458.8 | 492.8 | 455.4 | 427.1 | 412.2 | 369.9 | 369.5 | 404.9 | 323
1424 | 1297 | 526.4 | 458.8 | 492.9 | 455.5 | 427.3 | 412.4 | 370.1 | 369.7 | 405.1 | 323.3
1425 | 1298 | 526.4 | 458.9 | 492.9 | 455.5 | 427.6 | 412.5 | 370.3 | 370 | 405.3 | 323.5
1426 | 1299 | 526.4 | 459 | 492.8 | 455.6 | 428 | 412.8 | 370.4 | 370.2 | 405.4 | 323.7
1427 | 1300 | 526.4 | 459.1 | 492.8 | 455.7 | 428.4 | 413 | 370.5 | 370.5 | 405.6 | 323.9
1428 | 1301 | 526.4 | 459.1 | 492.9 | 455.7 | 428.6 | 413.1 | 370.7 | 370.6 | 405.7 | 324.2
1429 | 1302 | 526.4 | 459.1 | 493 | 455.8 | 428.7 | 413.2 | 370.8 | 370.9 | 405.9 | 324.4
1430 | 1303 | 526.4 | 459.2 | 493 | 455.8 | 429.1 | 413.4 | 371 | 371.2 | 406 | 324.6
1431 | 1304 | 526.4 | 459.2 | 493.1 | 455.9 | 429.2 | 413.5 | 371.1 | 371.4 | 406.2 | 324.8
1432 | 1305 | 526.3 | 459.3 | 493.2 | 455.9 | 429.5 | 413.7 | 371.2 | 371.7 | 406.3 | 325
1433 | 1306 | 526.3 | 459.3 | 493.2 | 456 | 429.8 | 413.9 | 371.3 | 371.9 | 406.5 | 325.3
1434 | 1307 | 526.3 | 459.4 | 493.2 | 456 | 430 | 414 | 371.4 | 372.2 | 406.6 | 325.5
1435 | 1308 | 526.3 | 459.4 | 493.2 | 456.1 | 430.4 | 414.2 | 371.5 | 372.4 | 406.7 | 325.7
1436 | 1309 | 526.3 | 459.5 | 493.2 | 456.2 | 430.5 | 414.3 | 371.6 | 372.5 | 406.9 | 325.9
1437 | 1310 | 526.3 | 459.6 | 493.3 | 456.2 | 430.9 | 414.5 | 371.7 | 372.7 | 407 | 326.2
1438 | 1311 | 526.2 | 459.6 | 493.3 | 456.3 | 431.1 | 414.6 | 371.7 | 372.8 | 407.2 | 326.4
1439 | 1312 | 526.2 | 459.7 | 493.3 | 456.3 | 431.5 | 414.8 | 371.8 | 373 | 407.4 | 326.6
1440 | 1313 | 526.2 | 459.7 | 493.4 | 456.4 | 431.7 | 414.9 | 371.8 | 373.2 | 407.5 | 326.9
1441 | 1314 | 526.1 | 459.8 | 493.3 | 456.5 | 432 | 415.1 | 371.9 | 373.4 | 407.6 | 327.1
1442 | 1315 | 526.1 | 459.8 | 493.4 | 456.5 | 432.2 | 415.2 | 372 | 373.6 | 407.8 | 327.4
1443 | 1316 | 526.1 | 459.9 | 493.4 | 456.6 | 432.6 | 415.4 | 372 | 373.9 | 407.9 | 327.6
1444 | 1317 | 526 | 460 | 493.4 | 456.6 | 432.8 | 415.5 | 372 | 374 | 408.1 | 327.8
1445 | 1318 | 526 | 460 | 493.5 | 456.7 | 433 | 415.7 | 372.1 | 374.2 | 408.2 | 328.1
1446 | 1319 | 526 | 460.1 | 493.5 | 456.7 | 433.2 | 415.8 | 372.2 | 374.4 | 408.4 | 328.3
1447 | 1320 | 526 | 460.1 | 493.5 | 456.8 | 433.5 | 416 | 372.2 | 374.6 | 408.5 | 328.6
1448 | 1321 | 526 | 460.2 | 493.6 | 456.8 | 433.8 | 416.1 | 372.2 | 374.7 | 408.7 | 328.8
1449 | 1322 | 526 | 460.2 | 493.6 | 456.9 | 434 | 416.2 | 372.3 | 374.9 | 408.8 | 329.1
1450 | 1323 | 525.9 | 460.3 | 493.6 | 457 | 434.3 | 416.4 | 372.3 | 375 | 408.9 | 329.3
1451 | 1324 | 525.9 | 460.4 | 493.6 | 457 | 434.6 | 416.6 | 372.3 | 375.2 | 409.1 | 329.6
1452 | 1325 | 525.9 | 460.3 | 493.9 | 457 | 434.5 | 416.6 | 372.4 | 375.3 | 409.3 | 329.8
1453 | 1326 | 525.9 | 460.4 | 493.9 | 457 | 434.7 | 416.7 | 372.5 | 375.4 | 409.4 | 330.1
1454 | 1327 | 525.9 | 460.4 | 493.9 | 457.1 | 435 | 416.9 | 372.5 | 375.5 | 409.5 | 330.3
1455 | 1328 | 525.9 | 460.5 | 493.9 | 457.1 | 435.3 | 417.1 | 372.6 | 375.7 | 409.7 | 330.6
1456 | 1329 | 525.9 | 460.5 | 494 | 457.2 | 435.4 | 417.2 | 372.6 | 375.8 | 409.8 | 330.8
1457 | 1330 | 525.9 | 460.6 | 494 | 457.3 | 435.7 | 417.4 | 372.7 | 376 | 409.9 | 331
1458 | 1331 | 525.9 | 460.6 | 494 | 457.3 | 436 | 417.5 | 372.7 | 376.2 | 410.1 | 331.3
1459 | 1332 | 525.9 | 460.7 | 494.1 | 457.4 | 436.2 | 417.7 | 372.7 | 376.3 | 410.2 | 331.5
1460 | 1333 | 525.9 | 460.7 | 494.1 | 457.4 | 436.4 | 417.8 | 372.8 | 376.5 | 410.4 | 331.7
1461 | 1334 | 525.8 | 460.8 | 494 | 457.5 | 436.7 | 418 | 372.9 | 376.7 | 410.5 | 331.9
1462 | 1335 | 525.8 | 460.8 | 494.1 | 457.5 | 436.9 | 418.2 | 372.9 | 376.8 | 410.6 | 332.2
1463 | 1336 | 525.8 | 460.9 | 494.2 | 457.6 | 437.1 | 418.3 | 373 | 376.9 | 410.8 | 332.4
1464 | 1337 | 525.8 | 460.9 | 494.2 | 457.6 | 437.4 | 418.5 | 373 | 377 | 410.9 | 332.7
1465 | 1338 | 525.8 | 461 | 494.2 | 457.7 | 437.6 | 418.6 | 373.1 | 377.2 | 411 | 332.9
1466 | 1339 | 525.8 | 461 | 494.3 | 457.7 | 437.9 | 418.7 | 373.2 | 377.3 | 411.2 | 333.2
1467 | 1340 | 525.8 | 461.1 | 494.3 | 457.8 | 438.4 | 418.8 | 373.2 | 377.4 | 411.3 | 333.4
1468 | 1341 | 525.8 | 461.1 | 494.2 | 457.9 | 438.7 | 418.9 | 373.3 | 377.5 | 411.4 | 333.6
1469 | 1342 | 525.8 | 461.2 | 494.3 | 457.9 | 439 | 419.1 | 373.4 | 377.7 | 411.6 | 333.8
1470 | 1343 | 525.8 | 461.2 | 494.4 | 458 | 439.1 | 419.2 | 373.4 | 377.8 | 411.7 | 334
1471 | 1344 | 525.8 | 461.3 | 494.3 | 458 | 439.3 | 419.4 | 373.5 | 377.9 | 411.8 | 334.2
1472 | 1345 | 525.8 | 461.3 | 494.4 | 458.1 | 439.5 | 419.6 | 373.6 | 378.1 | 412 | 334.4
1473 | 1346 | 525.9 | 461.3 | 494.5 | 458.1 | 439.5 | 419.7 | 373.7 | 378.3 | 412.1 | 334.7
1474 | 1347 | 525.9 | 461.3 | 494.6 | 458.1 | 439.6 | 419.8 | 373.7 | 378.4 | 412.3 | 334.9
1475 | 1348 | 525.9 | 461.4 | 494.6 | 458.2 | 439.7 | 420 | 373.8 | 378.6 | 412.5 | 335.1
1476 | 1349 | 525.9 | 461.5 | 494.6 | 458.2 | 439.8 | 420.2 | 373.9 | 378.7 | 412.6 | 335.3
1477 | 1350 | 525.9 | 461.5 | 494.7 | 458.3 | 439.9 | 420.3 | 374 | 378.8 | 412.8 | 335.6
1478 | 1351 | 525.9 | 461.6 | 494.7 | 458.3 | 440.1 | 420.5 | 374.1 | 379 | 412.9 | 335.8
1479 | 1352 | 525.9 | 461.6 | 494.7 | 458.4 | 440.2 | 420.7 | 374.2 | 379.1 | 413 | 336
1480 | 1353 | 526 | 461.6 | 494.8 | 458.4 | 440.3 | 420.8 | 374.2 | 379.3 | 413.1 | 336.2
1481 | 1354 | 526 | 461.7 | 494.8 | 458.5 | 440.3 | 421 | 374.3 | 379.4 | 413.3 | 336.5
1482 | 1355 | 526 | 461.8 | 494.8 | 458.6 | 440.5 | 421.2 | 374.4 | 379.5 | 413.4 | 336.7
1483 | 1356 | 526 | 461.8 | 494.8 | 458.6 | 440.5 | 421.3 | 374.5 | 379.6 | 413.5 | 336.9
1484 | 1357 | 526 | 461.8 | 494.9 | 458.6 | 440.6 | 421.5 | 374.6 | 379.7 | 413.7 | 337.1
1485 | 1358 | 526.1 | 461.9 | 494.8 | 458.7 | 440.8 | 421.7 | 374.7 | 379.8 | 413.8 | 337.4
1486 | 1359 | 526.1 | 461.9 | 494.9 | 458.8 | 440.9 | 421.8 | 374.8 | 379.9 | 413.9 | 337.6
1487 | 1360 | 526.2 | 462 | 495 | 458.8 | 440.9 | 422 | 374.9 | 380.1 | 414 | 337.8
1488 | 1361 | 526.2 | 462 | 495 | 458.9 | 441 | 422.1 | 375 | 380.2 | 414.1 | 338.1
1489 | 1362 | 526.2 | 462.1 | 495 | 458.9 | 441.2 | 422.3 | 375.1 | 380.3 | 414.3 | 338.3
1490 | 1363 | 526.2 | 462.1 | 495 | 459 | 441.2 | 422.5 | 375.2 | 380.4 | 414.4 | 338.5
1491 | 1364 | 526.2 | 462.2 | 495.1 | 459 | 441.3 | 422.7 | 375.3 | 380.6 | 414.6 | 338.7
1492 | 1365 | 526.2 | 462.3 | 495.1 | 459.1 | 441.4 | 422.9 | 375.4 | 380.7 | 414.7 | 339
1493 | 1366 | 526.2 | 462.3 | 495.1 | 459.1 | 441.5 | 423 | 375.5 | 380.7 | 414.8 | 339.2
1494 | 1367 | 526.2 | 462.3 | 495.2 | 459.2 | 441.5 | 423.2 | 375.6 | 380.8 | 414.9 | 339.5
1495 | 1368 | 526.3 | 462.4 | 495.2 | 459.2 | 441.6 | 423.4 | 375.7 | 381 | 415 | 339.7
1496 | 1369 | 526.3 | 462.4 | 495.2 | 459.3 | 441.8 | 423.6 | 375.8 | 381.1 | 415.2 | 339.9
1497 | 1370 | 526.3 | 462.5 | 495.2 | 459.3 | 441.9 | 423.8 | 375.9 | 381.2 | 415.3 | 340.2
1498 | 1371 | 526.3 | 462.5 | 495.3 | 459.4 | 441.9 | 423.9 | 376 | 381.4 | 415.4 | 340.4
1499 | 1372 | 526.3 | 462.6 | 495.3 | 459.5 | 442.1 | 424.1 | 376.1 | 381.5 | 415.5 | 340.6
1500 | 1373 | 526.3 | 462.6 | 495.3 | 459.5 | 442.2 | 424.3 | 376.2 | 381.6 | 415.7 | 340.8
1501 | 1374 | 526.3 | 462.7 | 495.4 | 459.5 | 442.3 | 424.5 | 376.3 | 381.7 | 415.8 | 341.1
1502 | 1375 | 526.3 | 462.7 | 495.4 | 459.6 | 442.3 | 424.7 | 376.4 | 381.8 | 415.9 | 341.3
1503 | 1376 | 526.3 | 462.8 | 495.3 | 459.7 | 442.5 | 424.9 | 376.5 | 382 | 416 | 341.6
1504 | 1377 | 526.4 | 462.9 | 495.4 | 459.7 | 442.6 | 425.1 | 376.6 | 382.2 | 416.1 | 341.8
1505 | 1378 | 526.4 | 462.9 | 495.5 | 459.7 | 442.6 | 425.3 | 376.7 | 382.4 | 416.3 | 342
1506 | 1379 | 526.4 | 462.9 | 495.4 | 459.8 | 442.7 | 425.5 | 376.9 | 382.4 | 416.4 | 342.2
1507 | 1380 | 526.4 | 463 | 495.4 | 459.9 | 442.9 | 425.8 | 377 | 382.6 | 416.5 | 342.4
1508 | 1381 | 526.5 | 463 | 495.5 | 459.9 | 442.9 | 426 | 377.1 | 382.7 | 416.6 | 342.7
1509 | 1382 | 526.5 | 463.1 | 495.6 | 460 | 443 | 426.2 | 377.2 | 382.9 | 416.7 | 342.9
1510 | 1383 | 526.5 | 463.1 | 495.6 | 460 | 443.2 | 426.4 | 377.3 | 383.1 | 416.8 | 343.1
1511 | 1384 | 526.5 | 463.2 | 495.6 | 460.1 | 443.2 | 426.6 | 377.4 | 383.2 | 416.9 | 343.3
1512 | 1385 | 526.5 | 463.2 | 495.7 | 460.1 | 443.2 | 426.8 | 377.5 | 383.4 | 417.1 | 343.5
1513 | 1386 | 526.5 | 463.3 | 495.6 | 460.2 | 443.4 | 427.1 | 377.6 | 383.6 | 417.2 | 343.7
1514 | 1387 | 526.4 | 463.3 | 495.6 | 460.2 | 443.5 | 427.3 | 377.8 | 383.7 | 417.3 | 343.9
1515 | 1388 | 526.4 | 463.3 | 495.7 | 460.2 | 443.5 | 427.6 | 377.9 | 383.8 | 417.4 | 344.1
1516 | 1389 | 526.4 | 463.4 | 495.8 | 460.3 | 443.6 | 427.8 | 378 | 383.9 | 417.5 | 344.3
1517 | 1390 | 526.4 | 463.5 | 495.7 | 460.4 | 443.7 | 428 | 378.1 | 384.1 | 417.6 | 344.5
1518 | 1391 | 526.4 | 463.5 | 495.8 | 460.4 | 443.8 | 428.2 | 378.2 | 384.3 | 417.7 | 344.7
1519 | 1392 | 526.4 | 463.5 | 495.8 | 460.4 | 443.7 | 428.4 | 378.3 | 384.4 | 417.9 | 345
1520 | 1393 | 526.3 | 463.6 | 495.8 | 460.5 | 444 | 428.6 | 378.5 | 384.4 | 418 | 345.2
1521 | 1394 | 526.3 | 463.6 | 495.8 | 460.6 | 444 | 428.8 | 378.6 | 384.5 | 418.1 | 345.4
1522 | 1395 | 526.3 | 463.7 | 495.9 | 460.6 | 444 | 429 | 378.7 | 384.6 | 418.2 | 345.6
1523 | 1396 | 526.2 | 463.7 | 495.9 | 460.6 | 444.1 | 429.2 | 378.8 | 384.7 | 418.3 | 345.8
1524 | 1397 | 526.2 | 463.8 | 495.9 | 460.7 | 444.2 | 429.4 | 378.9 | 384.8 | 418.4 | 346
1525 | 1398 | 526.2 | 463.8 | 495.9 | 460.7 | 444.3 | 429.5 | 379.1 | 384.9 | 418.5 | 346.2
1526 | 1399 | 526.2 | 463.9 | 496 | 460.8 | 444.3 | 429.7 | 379.2 | 385 | 418.6 | 346.4
1527 | 1400 | 526.2 | 463.9 | 495.9 | 460.9 | 444.5 | 429.9 | 379.3 | 385.1 | 418.7 | 346.6
1528 | 1401 | 526.2 | 464 | 495.9 | 460.9 | 444.6 | 430 | 379.4 | 385.3 | 418.8 | 346.8
1529 | 1402 | 526.2 | 464 | 496 | 460.9 | 444.6 | 430.2 | 379.6 | 385.5 | 418.9 | 347
1530 | 1403 | 526.2 | 464 | 496 | 461 | 444.7 | 430.3 | 379.7 | 385.7 | 419.1 | 347.2
1531 | 1404 | 526.2 | 464.1 | 496 | 461.1 | 444.8 | 430.5 | 379.8 | 385.8 | 419.1 | 347.3
1532 | 1405 | 526.2 | 464.1 | 496.1 | 461.1 | 444.8 | 430.6 | 380 | 386 | 419.3 | 347.5
1533 | 1406 | 526.1 | 464.2 | 496.2 | 461.1 | 444.9 | 430.8 | 380.1 | 386.1 | 419.4 | 347.7
1534 | 1407 | 526.1 | 464.2 | 496.1 | 461.2 | 445 | 431 | 380.2 | 386.3 | 419.5 | 347.9
1535 | 1408 | 526.1 | 464.3 | 496.2 | 461.2 | 445 | 431.1 | 380.3 | 386.4 | 419.6 | 348.1
1536 | 1409 | 526.1 | 464.3 | 496.3 | 461.3 | 445 | 431.3 | 380.5 | 386.6 | 419.7 | 348.3
1537 | 1410 | 526.1 | 464.3 | 496.2 | 461.3 | 445.1 | 431.5 | 380.6 | 386.7 | 419.8 | 348.5
1538 | 1411 | 526.1 | 464.4 | 496.3 | 461.4 | 445.2 | 431.6 | 380.7 | 386.8 | 419.9 | 348.7
1539 | 1412 | 526.1 | 464.4 | 496.3 | 461.4 | 445.2 | 431.7 | 380.9 | 386.9 | 420 | 348.9
1540 | 1413 | 526.1 | 464.5 | 496.4 | 461.4 | 445.2 | 431.9 | 381 | 387.1 | 420.1 | 349.1
1541 | 1414 | 526.1 | 464.5 | 496.3 | 461.5 | 445.4 | 432 | 381.1 | 387.2 | 420.1 | 349.3
1542 | 1415 | 526.1 | 464.6 | 496.4 | 461.5 | 445.4 | 432.1 | 381.3 | 387.3 | 420.2 | 349.5
1543 | 1416 | 526.1 | 464.6 | 496.4 | 461.6 | 445.4 | 432.2 | 381.4 | 387.5 | 420.3 | 349.7
1544 | 1417 | 526.1 | 464.6 | 496.4 | 461.6 | 445.5 | 432.4 | 381.5 | 387.7 | 420.4 | 349.8
1545 | 1418 | 526.1 | 464.7 | 496.4 | 461.7 | 445.6 | 432.5 | 381.7 | 387.7 | 420.5 | 350
1546 | 1419 | 526.1 | 464.7 | 496.4 | 461.7 | 445.6 | 432.7 | 381.8 | 387.9 | 420.6 | 350.2
1547 | 1420 | 526.1 | 464.8 | 496.5 | 461.8 | 445.6 | 432.8 | 381.9 | 388 | 420.7 | 350.4
1548 | 1421 | 526.1 | 464.8 | 496.4 | 461.8 | 445.7 | 432.9 | 382.1 | 388.1 | 420.8 | 350.5
1549 | 1422 | 526.1 | 464.9 | 496.5 | 461.9 | 445.9 | 433.1 | 382.2 | 388.2 | 420.8 | 350.7
1550 | 1423 | 526.1 | 464.9 | 496.5 | 461.9 | 445.9 | 433.2 | 382.4 | 388.3 | 420.9 | 350.8
1551 | 1424 | 526.1 | 465 | 496.5 | 462 | 446 | 433.3 | 382.5 | 388.5 | 421 | 351
1552 | 1425 | 526.1 | 465 | 496.5 | 462 | 446.1 | 433.3 | 382.6 | 388.6 | 421 | 351.2
1553 | 1426 | 526.1 | 465 | 496.6 | 462.1 | 446.1 | 433.4 | 382.8 | 388.8 | 421.1 | 351.4
1554 | 1427 | 526.1 | 465.1 | 496.6 | 462.1 | 446.1 | 433.3 | 382.9 | 388.9 | 421.1 | 351.6
1555 | 1428 | 526.1 | 465.1 | 496.6 | 462.2 | 446.3 | 433.3 | 383.1 | 389 | 421.2 | 351.7
1556 | 1429 | 526.1 | 465.2 | 496.6 | 462.2 | 446.3 | 433.2 | 383.2 | 389 | 421.2 | 351.9
1557 | 1430 | 526.1 | 465.2 | 496.7 | 462.3 | 446.4 | 433 | 383.4 | 389.2 | 421.3 | 352.1
1558 | 1431 | 526.1 | 465.2 | 496.7 | 462.3 | 446.6 | 433 | 383.5 | 389.4 | 421.3 | 352.3
1559 | 1432 | 526.1 | 465.3 | 496.7 | 462.4 | 446.8 | 433 | 383.7 | 389.6 | 421.4 | 352.4
1560 | 1433 | 526.1 | 465.3 | 496.7 | 462.4 | 446.9 | 432.9 | 383.8 | 389.7 | 421.5 | 352.6
1561 | 1434 | 526.1 | 465.3 | 496.8 | 462.4 | 446.9 | 432.9 | 383.9 | 389.9 | 421.5 | 352.7
1562 | 1435 | 526.1 | 465.4 | 496.7 | 462.5 | 447.1 | 432.9 | 384.1 | 390.1 | 421.6 | 352.9
1563 | 1436 | 526.2 | 465.5 | 496.8 | 462.5 | 447.2 | 432.9 | 384.2 | 390.2 | 421.6 | 353
1564 | 1437 | 526.2 | 465.5 | 496.8 | 462.6 | 447.3 | 432.9 | 384.4 | 390.3 | 421.7 | 353.2
1565 | 1438 | 526.2 | 465.5 | 496.8 | 462.6 | 447.4 | 433.1 | 384.5 | 390.5 | 421.8 | 353.3
1566 | 1439 | 526.2 | 465.6 | 496.8 | 462.7 | 447.6 | 433.4 | 384.7 | 390.6 | 421.8 | 353.5
1567 | 1440 | 526.2 | 465.7 | 496.8 | 462.7 | 447.7 | 433.7 | 384.8 | 390.7 | 421.9 | 353.6
1568 | 1441 | 526.2 | 465.7 | 496.9 | 462.8 | 447.6 | 434 | 385 | 390.8 | 421.9 | 353.8
1569 | 1442 | 526.3 | 465.7 | 496.9 | 462.8 | 447.7 | 434.2 | 385.1 | 390.9 | 422 | 353.9
1570 | 1443 | 526.3 | 465.8 | 496.9 | 462.9 | 447.7 | 434.4 | 385.3 | 391 | 422.1 | 354.1
1571 | 1444 | 526.3 | 465.8 | 496.9 | 462.9 | 447.7 | 434.6 | 385.4 | 391.2 | 422.1 | 354.2
1572 | 1445 | 526.3 | 465.8 | 497 | 462.9 | 447.7 | 434.8 | 385.6 | 391.3 | 422.2 | 354.4
1573 | 1446 | 526.3 | 465.9 | 497 | 463 | 447.7 | 435 | 385.7 | 391.4 | 422.2 | 354.5
1574 | 1447 | 526.3 | 465.9 | 497 | 463 | 447.6 | 435.1 | 385.9 | 391.6 | 422.3 | 354.6
1575 | 1448 | 526.3 | 465.9 | 497.1 | 463.1 | 447.5 | 435.3 | 386.1 | 391.8 | 422.4 | 354.8
1576 | 1449 | 526.3 | 466 | 497 | 463.1 | 447.5 | 435.6 | 386.2 | 391.9 | 422.4 | 354.9
1577 | 1450 | 526.3 | 466 | 497 | 463.2 | 447.4 | 435.8 | 386.4 | 392 | 422.5 | 355
1578 | 1451 | 526.2 | 466.1 | 497.1 | 463.2 | 447.3 | 436 | 386.6 | 392.1 | 422.5 | 355.1
1579 | 1452 | 526.2 | 466.1 | 497.1 | 463.3 | 447.3 | 436.2 | 386.7 | 392.3 | 422.6 | 355.2
1580 | 1453 | 526.1 | 466.2 | 497 | 463.3 | 447.3 | 436.4 | 386.9 | 392.4 | 422.7 | 355.3
1581 | 1454 | 526.1 | 466.2 | 497 | 463.4 | 447.2 | 436.6 | 387.1 | 392.5 | 422.7 | 355.5
1582 | 1455 | 526.1 | 466.2 | 497.1 | 463.4 | 447.2 | 436.7 | 387.2 | 392.7 | 422.8 | 355.6
1583 | 1456 | 526 | 466.3 | 497 | 463.5 | 447.2 | 436.9 | 387.4 | 392.8 | 422.8 | 355.7
1584 | 1457 | 526 | 466.4 | 497 | 463.5 | 447.3 | 437 | 387.6 | 393 | 422.9 | 355.9
1585 | 1458 | 526 | 466.4 | 497 | 463.5 | 447.2 | 437.1 | 387.7 | 393.1 | 422.9 | 356
1586 | 1459 | 526 | 466.4 | 497.1 | 463.6 | 447.2 | 437.3 | 387.9 | 393.4 | 423 | 356.2
1587 | 1460 | 525.9 | 466.5 | 497 | 463.6 | 447.3 | 437.4 | 388.1 | 393.5 | 423 | 356.3
1588 | 1461 | 525.9 | 466.5 | 497.1 | 463.7 | 447.2 | 437.4 | 388.3 | 393.6 | 423.1 | 356.4
1589 | 1462 | 525.9 | 466.6 | 497.1 | 463.7 | 447.1 | 437.5 | 388.4 | 393.8 | 423.1 | 356.6
1590 | 1463 | 525.9 | 466.6 | 497.1 | 463.8 | 447.2 | 437.6 | 388.6 | 393.9 | 423.2 | 356.7
1591 | 1464 | 525.9 | 466.6 | 497.1 | 463.8 | 447.1 | 437.7 | 388.8 | 394.1 | 423.3 | 356.8
1592 | 1465 | 525.9 | 466.7 | 497.2 | 463.8 | 447.1 | 437.7 | 389 | 394.3 | 423.3 | 357
1593 | 1466 | 525.9 | 466.7 | 497.2 | 463.9 | 447.1 | 437.8 | 389.2 | 394.5 | 423.4 | 357.1
1594 | 1467 | 525.9 | 466.8 | 497.1 | 463.9 | 447.1 | 437.9 | 389.4 | 394.6 | 423.5 | 357.3
1595 | 1468 | 525.9 | 466.8 | 497.2 | 464 | 447.1 | 437.9 | 389.6 | 394.8 | 423.5 | 357.4
1596 | 1469 | 525.9 | 466.8 | 497.3 | 464 | 447.1 | 438 | 389.8 | 395 | 423.6 | 357.6
1597 | 1470 | 525.9 | 466.9 | 497.2 | 464.1 | 447.2 | 438.1 | 390 | 395.2 | 423.7 | 357.7
1598 | 1471 | 525.9 | 466.9 | 497.2 | 464.1 | 447.2 | 438.1 | 390.2 | 395.3 | 423.7 | 357.9
1599 | 1472 | 525.9 | 466.9 | 497.3 | 464.1 | 447 | 438.2 | 390.4 | 395.5 | 423.8 | 358
1600 | 1473 | 525.9 | 466.9 | 497.5 | 464.1 | 446.9 | 438.2 | 390.6 | 395.6 | 423.9 | 358.2
1601 | 1474 | 525.9 | 466.9 | 497.4 | 464.1 | 447 | 438.2 | 390.8 | 395.8 | 423.9 | 358.3
1602 | 1475 | 525.9 | 467 | 497.5 | 464.2 | 446.9 | 438.3 | 391 | 396 | 424 | 358.5
1603 | 1476 | 525.9 | 467 | 497.5 | 464.2 | 446.9 | 438.3 | 391.2 | 396.1 | 424.1 | 358.6
1604 | 1477 | 525.9 | 467 | 497.5 | 464.2 | 447 | 438.4 | 391.4 | 396.3 | 424.1 | 358.7
1605 | 1478 | 525.9 | 467.1 | 497.5 | 464.3 | 447 | 438.4 | 391.6 | 396.5 | 424.2 | 358.9
1606 | 1479 | 525.9 | 467.1 | 497.5 | 464.3 | 447 | 438.5 | 391.8 | 396.7 | 424.2 | 359
1607 | 1480 | 525.9 | 467.1 | 497.6 | 464.3 | 447 | 438.5 | 392 | 396.9 | 424.3 | 359.1
1608 | 1481 | 525.9 | 467.2 | 497.6 | 464.4 | 447 | 438.6 | 392.2 | 397.1 | 424.4 | 359.2
1609 | 1482 | 525.9 | 467.2 | 497.6 | 464.4 | 447.1 | 438.6 | 392.5 | 397.3 | 424.4 | 359.4
1610 | 1483 | 525.9 | 467.3 | 497.6 | 464.5 | 447.1 | 438.7 | 392.7 | 397.5 | 424.5 | 359.5
1611 | 1484 | 525.9 | 467.3 | 497.5 | 464.5 | 447.2 | 438.7 | 392.9 | 397.7 | 424.6 | 359.6
1612 | 1485 | 525.9 | 467.4 | 497.6 | 464.6 | 447.2 | 438.8 | 393.1 | 397.9 | 424.6 | 359.7
1613 | 1486 | 525.8 | 467.4 | 497.6 | 464.6 | 447.2 | 438.8 | 393.3 | 398.1 | 424.7 | 359.8
1614 | 1487 | 525.8 | 467.4 | 497.7 | 464.6 | 447.3 | 438.9 | 393.5 | 398.3 | 424.8 | 360
1615 | 1488 | 525.8 | 467.5 | 497.6 | 464.7 | 447.3 | 438.9 | 393.7 | 398.5 | 424.8 | 360.1
1616 | 1489 | 525.8 | 467.5 | 497.6 | 464.7 | 447.4 | 439 | 394 | 398.7 | 424.9 | 360.2
1617 | 1490 | 525.8 | 467.5 | 497.7 | 464.7 | 447.4 | 439 | 394.2 | 398.8 | 424.9 | 360.3
1618 | 1491 | 525.8 | 467.6 | 497.6 | 464.8 | 447.4 | 439.1 | 394.4 | 399 | 425 | 360.5
1619 | 1492 | 525.8 | 467.6 | 497.7 | 464.8 | 447.4 | 439.1 | 394.6 | 399.1 | 425.1 | 360.6
1620 | 1493 | 525.8 | 467.6 | 497.7 | 464.8 | 447.4 | 439.2 | 394.9 | 399.4 | 425.2 | 360.7
1621 | 1494 | 525.8 | 467.7 | 497.7 | 464.9 | 447.5 | 439.2 | 395.1 | 399.6 | 425.2 | 360.8
1622 | 1495 | 525.8 | 467.7 | 497.7 | 464.9 | 447.6 | 439.3 | 395.3 | 399.8 | 425.3 | 360.9
1623 | 1496 | 525.8 | 467.7 | 497.7 | 465 | 447.6 | 439.3 | 395.5 | 400 | 425.4 | 361.1
1624 | 1497 | 525.8 | 467.8 | 497.8 | 465 | 447.5 | 439.3 | 395.8 | 400.1 | 425.4 | 361.2
1625 | 1498 | 525.8 | 467.8 | 497.7 | 465 | 447.6 | 439.4 | 396 | 400.3 | 425.5 | 361.3
1626 | 1499 | 525.8 | 467.9 | 497.8 | 465.1 | 447.7 | 439.5 | 396.2 | 400.5 | 425.6 | 361.4
1627 | 1500 | 525.7 | 467.9 | 497.8 | 465.1 | 447.6 | 439.5 | 396.4 | 400.7 | 425.6 | 361.5
1628 | 1501 | 525.7 | 467.9 | 497.8 | 465.1 | 447.7 | 439.5 | 396.7 | 400.9 | 425.7 | 361.6
1629 | 1502 | 525.7 | 468 | 497.7 | 465.2 | 447.7 | 439.6 | 396.9 | 401.1 | 425.8 | 361.8
1630 | 1503 | 525.7 | 468 | 497.8 | 465.2 | 447.7 | 439.6 | 397.1 | 401.4 | 425.8 | 361.9
1631 | 1504 | 525.7 | 468 | 497.8 | 465.2 | 447.7 | 439.7 | 397.3 | 401.6 | 425.9 | 362
1632 | 1505 | 525.7 | 468.1 | 497.8 | 465.3 | 447.8 | 439.7 | 397.6 | 401.9 | 426 | 362.1
1633 | 1506 | 525.8 | 468.1 | 497.8 | 465.3 | 447.8 | 439.8 | 397.8 | 402.1 | 426 | 362.3
1634 | 1507 | 525.8 | 468.1 | 497.9 | 465.3 | 447.8 | 439.8 | 398 | 402.4 | 426.1 | 362.4
1635 | 1508 | 525.8 | 468.2 | 497.9 | 465.4 | 447.8 | 439.9 | 398.3 | 402.6 | 426.2 | 362.5
1636 | 1509 | 525.8 | 468.2 | 497.9 | 465.4 | 447.9 | 439.9 | 398.5 | 402.8 | 426.3 | 362.6
1637 | 1510 | 525.9 | 468.2 | 497.9 | 465.5 | 447.9 | 440 | 398.7 | 403 | 426.3 | 362.7
1638 | 1511 | 525.9 | 468.2 | 497.9 | 465.5 | 447.9 | 440 | 398.9 | 403.2 | 426.4 | 362.9
1639 | 1512 | 525.9 | 468.3 | 497.9 | 465.5 | 447.9 | 440 | 399.1 | 403.5 | 426.5 | 363
1640 | 1513 | 525.9 | 468.3 | 497.9 | 465.6 | 448 | 440.1 | 399.4 | 403.6 | 426.5 | 363.1
1641 | 1514 | 525.9 | 468.3 | 498 | 465.6 | 448 | 440.1 | 399.6 | 403.9 | 426.6 | 363.3
1642 | 1515 | 525.9 | 468.4 | 498 | 465.6 | 448 | 440.2 | 399.8 | 404.1 | 426.7 | 363.4
1643 | 1516 | 525.9 | 468.4 | 498 | 465.7 | 448.1 | 440.3 | 400 | 404.3 | 426.7 | 363.5
1644 | 1517 | 525.9 | 468.5 | 498 | 465.7 | 448.1 | 440.3 | 400.3 | 404.4 | 426.8 | 363.6
1645 | 1518 | 525.9 | 468.5 | 498 | 465.7 | 448.1 | 440.3 | 400.5 | 404.6 | 426.9 | 363.8
1646 | 1519 | 526 | 468.5 | 498 | 465.8 | 448.2 | 440.4 | 400.7 | 404.8 | 426.9 | 363.9
1647 | 1520 | 526 | 468.6 | 498 | 465.8 | 448.2 | 440.5 | 400.9 | 405.1 | 427 | 364.1
1648 | 1521 | 526 | 468.6 | 498.1 | 465.8 | 448.2 | 440.5 | 401.1 | 405.3 | 427 | 364.2
1649 | 1522 | 526 | 468.6 | 498.1 | 465.9 | 448.2 | 440.5 | 401.4 | 405.5 | 427.1 | 364.3
1650 | 1523 | 526 | 468.7 | 498.1 | 465.9 | 448.3 | 440.6 | 401.6 | 405.7 | 427.2 | 364.4
1651 | 1524 | 526 | 468.7 | 498.1 | 465.9 | 448.3 | 440.6 | 401.8 | 405.9 | 427.3 | 364.6
1652 | 1525 | 526.1 | 468.7 | 498.2 | 465.9 | 448.3 | 440.7 | 402 | 406.2 | 427.3 | 364.7
1653 | 1526 | 526.1 | 468.8 | 498.2 | 466 | 448.4 | 440.7 | 402.2 | 406.4 | 427.4 | 364.8
1654 | 1527 | 526.1 | 468.8 | 498.2 | 466 | 448.4 | 440.8 | 402.4 | 406.6 | 427.5 | 364.9
1655 | 1528 | 526.2 | 468.8 | 498.2 | 466.1 | 448.4 | 440.8 | 402.7 | 406.9 | 427.5 | 365.1
1656 | 1529 | 526.2 | 468.9 | 498.2 | 466.1 | 448.4 | 440.9 | 402.9 | 407.1 | 427.6 | 365.2
1657 | 1530 | 526.2 | 468.9 | 498.2 | 466.1 | 448.4 | 440.9 | 403.1 | 407.3 | 427.6 | 365.3
1658 | 1531 | 526.2 | 468.9 | 498.2 | 466.2 | 448.5 | 441 | 403.3 | 407.5 | 427.7 | 365.5
1659 | 1532 | 526.1 | 468.9 | 498.3 | 466.2 | 448.4 | 441 | 403.5 | 407.8 | 427.8 | 365.6
1660 | 1533 | 526.1 | 469 | 498.3 | 466.2 | 448.5 | 441.1 | 403.7 | 408 | 427.9 | 365.7
1661 | 1534 | 526.1 | 469 | 498.3 | 466.3 | 448.6 | 441.1 | 403.9 | 408.2 | 427.9 | 365.9
1662 | 1535 | 526.1 | 469.1 | 498.3 | 466.3 | 448.6 | 441.2 | 404.1 | 408.4 | 428 | 366
1663 | 1536 | 526.1 | 469.1 | 498.3 | 466.3 | 448.6 | 441.2 | 404.4 | 408.6 | 428.1 | 366.1
1664 | 1537 | 526.1 | 469.1 | 498.4 | 466.4 | 448.6 | 441.3 | 404.6 | 408.8 | 428.1 | 366.2
1665 | 1538 | 526.1 | 469.2 | 498.4 | 466.4 | 448.7 | 441.3 | 404.8 | 409 | 428.2 | 366.4
1666 | 1539 | 526.1 | 469.2 | 498.5 | 466.4 | 448.6 | 441.3 | 405 | 409.1 | 428.3 | 366.5
1667 | 1540 | 526.1 | 469.2 | 498.4 | 466.4 | 448.7 | 441.4 | 405.2 | 409.4 | 428.3 | 366.6
1668 | 1541 | 526.1 | 469.3 | 498.4 | 466.5 | 448.7 | 441.4 | 405.4 | 409.6 | 428.4 | 366.8
1669 | 1542 | 526.1 | 469.3 | 498.4 | 466.5 | 448.6 | 441.4 | 405.6 | 409.9 | 428.4 | 366.9
1670 | 1543 | 526.1 | 469.3 | 498.5 | 466.5 | 448.7 | 441.5 | 405.8 | 410 | 428.5 | 367
1671 | 1544 | 526.1 | 469.4 | 498.4 | 466.6 | 448.7 | 441.5 | 406 | 410.2 | 428.6 | 367.1
1672 | 1545 | 526.1 | 469.4 | 498.5 | 466.6 | 448.8 | 441.6 | 406.2 | 410.4 | 428.7 | 367.3
1673 | 1546 | 526 | 469.4 | 498.6 | 466.6 | 448.7 | 441.6 | 406.4 | 410.6 | 428.7 | 367.4
1674 | 1547 | 526 | 469.4 | 498.5 | 466.7 | 448.8 | 441.7 | 406.6 | 410.8 | 428.8 | 367.5
1675 | 1548 | 526 | 469.5 | 498.5 | 466.7 | 448.9 | 441.8 | 406.8 | 411 | 428.8 | 367.7
1676 | 1549 | 526 | 469.5 | 498.6 | 466.7 | 448.9 | 441.8 | 407 | 411.1 | 428.9 | 367.8
1677 | 1550 | 526 | 469.5 | 498.6 | 466.8 | 448.8 | 441.9 | 407.2 | 411.3 | 429 | 367.9
1678 | 1551 | 526 | 469.6 | 498.6 | 466.8 | 448.9 | 442 | 407.4 | 411.5 | 429 | 368
1679 | 1552 | 526 | 469.6 | 498.6 | 466.8 | 449 | 442.1 | 407.6 | 411.7 | 429.1 | 368.2
1680 | 1553 | 526 | 469.6 | 498.7 | 466.8 | 449 | 442.1 | 407.8 | 411.9 | 429.2 | 368.3
1681 | 1554 | 526 | 469.7 | 498.6 | 466.9 | 449 | 442.2 | 408 | 412.1 | 429.2 | 368.4
1682 | 1555 | 526.1 | 469.7 | 498.6 | 466.9 | 449.1 | 442.3 | 408.2 | 412.2 | 429.3 | 368.5
1683 | 1556 | 526.1 | 469.7 | 498.7 | 467 | 449.1 | 442.4 | 408.4 | 412.4 | 429.4 | 368.6
1684 | 1557 | 526.1 | 469.7 | 498.7 | 467 | 449.1 | 442.5 | 408.6 | 412.7 | 429.4 | 368.7
1685 | 1558 | 526.1 | 469.8 | 498.7 | 467 | 449.1 | 442.6 | 408.8 | 412.9 | 429.5 | 368.9
1686 | 1559 | 526.1 | 469.8 | 498.7 | 467.1 | 449.1 | 442.7 | 409 | 413.2 | 429.5 | 369
1687 | 1560 | 526.1 | 469.8 | 498.7 | 467.1 | 449.1 | 442.8 | 409.1 | 413.4 | 429.6 | 369.1
1688 | 1561 | 526.1 | 469.9 | 498.7 | 467.1 | 449.2 | 442.9 | 409.3 | 413.6 | 429.7 | 369.2
1689 | 1562 | 526.1 | 469.9 | 498.7 | 467.2 | 449.3 | 443 | 409.5 | 413.8 | 429.7 | 369.4
1690 | 1563 | 526.1 | 469.9 | 498.7 | 467.2 | 449.3 | 443.1 | 409.7 | 414 | 429.8 | 369.5
1691 | 1564 | 526.1 | 470 | 498.8 | 467.2 | 449.3 | 443.2 | 409.9 | 414.2 | 429.8 | 369.6
1692 | 1565 | 526.1 | 470 | 498.7 | 467.3 | 449.4 | 443.2 | 410.1 | 414.4 | 429.9 | 369.7
1693 | 1566 | 526.1 | 470 | 498.8 | 467.3 | 449.4 | 443.3 | 410.3 | 414.6 | 430 | 369.8
1694 | 1567 | 526.1 | 470 | 498.8 | 467.3 | 449.3 | 443.4 | 410.5 | 414.7 | 430 | 370
1695 | 1568 | 526.1 | 470.1 | 498.8 | 467.4 | 449.4 | 443.5 | 410.7 | 414.9 | 430.1 | 370.1
1696 | 1569 | 526.1 | 470.1 | 498.8 | 467.4 | 449.4 | 443.6 | 410.8 | 415.1 | 430.1 | 370.2
1697 | 1570 | 526.1 | 470.1 | 498.9 | 467.4 | 449.4 | 443.7 | 411 | 415.3 | 430.2 | 370.3
1698 | 1571 | 526 | 470.2 | 498.9 | 467.4 | 449.4 | 443.8 | 411.2 | 415.5 | 430.2 | 370.5
1699 | 1572 | 526 | 470.2 | 498.9 | 467.5 | 449.6 | 443.9 | 411.4 | 415.7 | 430.3 | 370.6
1700 | 1573 | 526 | 470.2 | 498.9 | 467.5 | 449.7 | 444 | 411.6 | 415.8 | 430.4 | 370.7
1701 | 1574 | 525.9 | 470.2 | 498.9 | 467.5 | 449.7 | 444.1 | 411.7 | 416 | 430.4 | 370.8
1702 | 1575 | 525.9 | 470.3 | 498.9 | 467.6 | 449.8 | 444.3 | 411.9 | 416.2 | 430.5 | 371
1703 | 1576 | 525.9 | 470.3 | 498.9 | 467.6 | 449.8 | 444.4 | 412.1 | 416.4 | 430.6 | 371.1
1704 | 1577 | 525.9 | 470.3 | 498.9 | 467.6 | 449.8 | 444.6 | 412.3 | 416.6 | 430.6 | 371.2
1705 | 1578 | 525.8 | 470.4 | 499 | 467.6 | 449.8 | 444.7 | 412.5 | 416.7 | 430.7 | 371.3
1706 | 1579 | 525.9 | 470.4 | 499 | 467.7 | 449.9 | 444.8 | 412.6 | 416.9 | 430.8 | 371.5
1707 | 1580 | 525.9 | 470.4 | 499 | 467.7 | 449.9 | 445 | 412.8 | 417.1 | 430.8 | 371.6
1708 | 1581 | 525.9 | 470.4 | 499 | 467.7 | 449.9 | 445.1 | 413 | 417.3 | 430.9 | 371.7
1709 | 1582 | 525.8 | 470.5 | 499 | 467.8 | 450 | 445.2 | 413.2 | 417.5 | 430.9 | 371.8
1710 | 1583 | 525.8 | 470.5 | 499 | 467.8 | 450.1 | 445.4 | 413.4 | 417.6 | 431 | 372
1711 | 1584 | 525.8 | 470.5 | 499.1 | 467.8 | 450 | 445.5 | 413.5 | 417.8 | 431.1 | 372.1
1712 | 1585 | 525.8 | 470.6 | 499.1 | 467.9 | 450.1 | 445.6 | 413.7 | 417.9 | 431.1 | 372.2
1713 | 1586 | 525.8 | 470.6 | 499.1 | 467.9 | 450.2 | 445.7 | 413.9 | 418.1 | 431.2 | 372.3
1714 | 1587 | 525.8 | 470.6 | 499.1 | 467.9 | 450.2 | 445.8 | 414.1 | 418.3 | 431.3 | 372.5
1715 | 1588 | 525.8 | 470.6 | 499.1 | 468 | 450.2 | 445.9 | 414.2 | 418.5 | 431.3 | 372.6
1716 | 1589 | 525.8 | 470.7 | 499.1 | 468 | 450.3 | 446.1 | 414.4 | 418.6 | 431.4 | 372.7
1717 | 1590 | 525.8 | 470.7 | 499.1 | 468 | 450.4 | 446.2 | 414.6 | 418.8 | 431.4 | 372.8
1718 | 1591 | 525.8 | 470.7 | 499.2 | 468.1 | 450.4 | 446.3 | 414.8 | 418.9 | 431.5 | 373
1719 | 1592 | 525.9 | 470.8 | 499.2 | 468.1 | 450.5 | 446.5 | 414.9 | 419.1 | 431.6 | 373.1
1720 | 1593 | 525.9 | 470.8 | 499.2 | 468.1 | 450.6 | 446.6 | 415.1 | 419.3 | 431.6 | 373.2
1721 | 1594 | 525.9 | 470.8 | 499.2 | 468.2 | 450.6 | 446.7 | 415.3 | 419.4 | 431.7 | 373.3
1722 | 1595 | 525.9 | 470.8 | 499.2 | 468.2 | 450.6 | 446.8 | 415.4 | 419.6 | 431.7 | 373.5
1723 | 1596 | 525.9 | 470.9 | 499.2 | 468.2 | 450.7 | 447 | 415.6 | 419.8 | 431.8 | 373.6
1724 | 1597 | 525.9 | 470.9 | 499.2 | 468.2 | 450.8 | 447.1 | 415.8 | 420 | 431.8 | 373.7
1725 | 1598 | 525.9 | 470.9 | 499.3 | 468.2 | 450.8 | 447.2 | 415.9 | 420.1 | 431.9 | 373.8
1726 | 1599 | 525.9 | 470.9 | 499.3 | 468.3 | 450.8 | 447.4 | 416.1 | 420.2 | 432 | 374
1727 | 1600 | 526 | 471 | 499.3 | 468.3 | 450.9 | 447.5 | 416.3 | 420.5 | 432 | 374.1
1728 | 1601 | 525.9 | 471 | 499.3 | 468.3 | 450.9 | 447.6 | 416.4 | 420.7 | 432.1 | 374.2
1729 | 1602 | 526 | 471 | 499.4 | 468.4 | 450.9 | 447.7 | 416.6 | 420.8 | 432.1 | 374.3
1730 | 1603 | 526 | 471.1 | 499.3 | 468.4 | 451.1 | 447.9 | 416.8 | 421 | 432.2 | 374.5
1731 | 1604 | 526 | 471.1 | 499.3 | 468.4 | 451.1 | 448.1 | 416.9 | 421.1 | 432.2 | 374.6
1732 | 1605 | 526 | 471.1 | 499.4 | 468.4 | 451 | 448.2 | 417.1 | 421.2 | 432.3 | 374.7
1733 | 1606 | 526 | 471.1 | 499.4 | 468.5 | 451.1 | 448.3 | 417.2 | 421.5 | 432.3 | 374.8
1734 | 1607 | 526 | 471.2 | 499.4 | 468.5 | 451.2 | 448.5 | 417.4 | 421.7 | 432.4 | 375
1735 | 1608 | 526 | 471.2 | 499.4 | 468.5 | 451.3 | 448.6 | 417.6 | 421.8 | 432.5 | 375.1
1736 | 1609 | 525.9 | 471.2 | 499.5 | 468.5 | 451.3 | 448.7 | 417.7 | 421.9 | 432.5 | 375.2
1737 | 1610 | 525.9 | 471.3 | 499.4 | 468.6 | 451.4 | 448.9 | 417.9 | 422.1 | 432.6 | 375.3
1738 | 1611 | 525.9 | 471.3 | 499.4 | 468.6 | 451.4 | 449 | 418 | 422.2 | 432.6 | 375.5
1739 | 1612 | 525.9 | 471.3 | 499.5 | 468.6 | 451.4 | 449.1 | 418.2 | 422.3 | 432.7 | 375.6
1740 | 1613 | 525.9 | 471.3 | 499.5 | 468.7 | 451.4 | 449.3 | 418.4 | 422.5 | 432.8 | 375.7
1741 | 1614 | 525.9 | 471.4 | 499.5 | 468.7 | 451.5 | 449.4 | 418.5 | 422.7 | 432.8 | 375.8
1742 | 1615 | 525.9 | 471.4 | 499.5 | 468.7 | 451.5 | 449.5 | 418.7 | 422.9 | 432.9 | 376
1743 | 1616 | 525.9 | 471.4 | 499.6 | 468.7 | 451.5 | 449.6 | 418.8 | 423 | 433 | 376.1
1744 | 1617 | 525.9 | 471.5 | 499.5 | 468.8 | 451.6 | 449.8 | 419 | 423.1 | 433 | 376.2
1745 | 1618 | 525.9 | 471.5 | 499.5 | 468.8 | 451.6 | 449.9 | 419.2 | 423.2 | 433.1 | 376.3
1746 | 1619 | 525.9 | 471.5 | 499.6 | 468.8 | 451.7 | 450.1 | 419.3 | 423.4 | 433.1 | 376.5
1747 | 1620 | 525.8 | 471.5 | 499.6 | 468.9 | 451.7 | 450.2 | 419.5 | 423.5 | 433.2 | 376.6
1748 | 1621 | 525.9 | 471.6 | 499.6 | 468.9 | 451.8 | 450.3 | 419.6 | 423.7 | 433.3 | 376.7
1749 | 1622 | 525.9 | 471.6 | 499.6 | 468.9 | 451.8 | 450.5 | 419.8 | 423.9 | 433.3 | 376.8
1750 | 1623 | 525.9 | 471.6 | 499.6 | 468.9 | 451.8 | 450.6 | 419.9 | 424.1 | 433.4 | 377
1751 | 1624 | 525.9 | 471.6 | 499.6 | 469 | 451.9 | 450.6 | 420.1 | 424.3 | 433.5 | 377.1
1752 | 1625 | 525.9 | 471.7 | 499.6 | 469 | 452 | 450.7 | 420.2 | 424.5 | 433.5 | 377.2
1753 | 1626 | 526 | 471.7 | 499.7 | 469 | 452 | 450.8 | 420.4 | 424.6 | 433.6 | 377.3
1754 | 1627 | 526 | 471.7 | 499.7 | 469 | 452 | 451 | 420.6 | 424.8 | 433.6 | 377.4
1755 | 1628 | 526 | 471.8 | 499.7 | 469.1 | 452.1 | 451.1 | 420.7 | 424.9 | 433.7 | 377.5
1756 | 1629 | 526 | 471.8 | 499.7 | 469.1 | 452.1 | 451.2 | 420.9 | 425.1 | 433.7 | 377.7
1757 | 1630 | 526 | 471.8 | 499.7 | 469.1 | 452.2 | 451.3 | 421 | 425.3 | 433.8 | 377.8
1758 | 1631 | 526 | 471.8 | 499.7 | 469.2 | 452.2 | 451.4 | 421.2 | 425.4 | 433.9 | 377.9
1759 | 1632 | 526.1 | 471.8 | 499.7 | 469.2 | 452.3 | 451.5 | 421.3 | 425.6 | 433.9 | 378
1760 | 1633 | 526 | 471.8 | 499.8 | 469.2 | 452.3 | 451.5 | 421.5 | 425.7 | 434 | 378.1
1761 | 1634 | 526 | 471.9 | 499.8 | 469.2 | 452.4 | 451.6 | 421.6 | 425.9 | 434 | 378.3
1762 | 1635 | 526 | 471.9 | 499.8 | 469.3 | 452.5 | 451.7 | 421.8 | 426.1 | 434.1 | 378.4
1763 | 1636 | 526 | 471.9 | 499.8 | 469.3 | 452.5 | 451.8 | 421.9 | 426.2 | 434.1 | 378.5
1764 | 1637 | 526 | 471.9 | 499.9 | 469.3 | 452.5 | 451.8 | 422.1 | 426.3 | 434.2 | 378.6
1765 | 1638 | 526 | 472 | 499.8 | 469.3 | 452.6 | 452 | 422.2 | 426.5 | 434.3 | 378.7
1766 | 1639 | 526 | 472 | 499.8 | 469.4 | 452.6 | 452 | 422.4 | 426.7 | 434.3 | 378.8
1767 | 1640 | 526 | 472 | 499.8 | 469.4 | 452.7 | 452.1 | 422.6 | 426.7 | 434.4 | 379
1768 | 1641 | 526 | 472.1 | 499.9 | 469.4 | 452.7 | 452.1 | 422.7 | 426.8 | 434.4 | 379.1
1769 | 1642 | 525.9 | 472.1 | 499.9 | 469.4 | 452.9 | 452.2 | 422.9 | 426.9 | 434.5 | 379.2
1770 | 1643 | 525.9 | 472.1 | 499.9 | 469.5 | 452.9 | 452.2 | 423 | 427.1 | 434.6 | 379.3
1771 | 1644 | 525.9 | 472.1 | 499.9 | 469.5 | 452.9 | 452.3 | 423.2 | 427.2 | 434.6 | 379.4
1772 | 1645 | 525.9 | 472.2 | 499.9 | 469.5 | 453 | 452.3 | 423.3 | 427.4 | 434.7 | 379.5
1773 | 1646 | 525.9 | 472.2 | 499.9 | 469.6 | 453.1 | 452.2 | 423.4 | 427.6 | 434.7 | 379.6
1774 | 1647 | 525.9 | 472.2 | 500 | 469.6 | 453.1 | 452.2 | 423.6 | 427.8 | 434.8 | 379.8
1775 | 1648 | 525.9 | 472.2 | 500 | 469.6 | 453.1 | 452.2 | 423.7 | 428 | 434.9 | 379.9
1776 | 1649 | 525.9 | 472.2 | 500 | 469.7 | 453.2 | 452.2 | 423.9 | 428.2 | 434.9 | 380
1777 | 1650 | 525.9 | 472.3 | 500 | 469.7 | 453.3 | 452.2 | 424.1 | 428.3 | 435 | 380.1
1778 | 1651 | 525.9 | 472.3 | 500 | 469.7 | 453.3 | 452.1 | 424.2 | 428.5 | 435 | 380.2
1779 | 1652 | 526 | 472.3 | 500 | 469.7 | 453.4 | 452.1 | 424.4 | 428.6 | 435.1 | 380.3
1780 | 1653 | 526 | 472.4 | 500 | 469.8 | 453.5 | 452.1 | 424.5 | 428.7 | 435.2 | 380.4
1781 | 1654 | 526 | 472.4 | 500 | 469.8 | 453.5 | 452.1 | 424.7 | 428.9 | 435.2 | 380.5
1782 | 1655 | 526 | 472.4 | 500.1 | 469.8 | 453.6 | 452 | 424.8 | 429 | 435.3 | 380.6
1783 | 1656 | 526 | 472.5 | 500.1 | 469.8 | 453.6 | 452 | 425 | 429.1 | 435.3 | 380.7
1784 | 1657 | 526 | 472.5 | 500 | 469.9 | 453.6 | 452 | 425.2 | 429.2 | 435.4 | 380.8
1785 | 1658 | 526.1 | 472.5 | 500 | 469.9 | 453.7 | 452 | 425.3 | 429.4 | 435.5 | 380.9
1786 | 1659 | 526.1 | 472.5 | 500 | 469.9 | 453.8 | 451.9 | 425.5 | 429.5 | 435.5 | 381
1787 | 1660 | 526.1 | 472.5 | 500 | 470 | 453.8 | 451.9 | 425.6 | 429.6 | 435.6 | 381.2
1788 | 1661 | 526.1 | 472.5 | 500.1 | 470 | 453.9 | 451.9 | 425.8 | 429.7 | 435.6 | 381.3
1789 | 1662 | 526.1 | 472.6 | 500.1 | 470 | 453.9 | 451.9 | 425.9 | 429.8 | 435.7 | 381.4
1790 | 1663 | 526.1 | 472.6 | 500.1 | 470 | 454 | 451.9 | 426.1 | 430 | 435.8 | 381.5
1791 | 1664 | 526.1 | 472.6 | 500.1 | 470 | 454 | 451.9 | 426.2 | 430.1 | 435.8 | 381.6
1792 | 1665 | 526.1 | 472.6 | 500.1 | 470.1 | 454.1 | 452 | 426.4 | 430.2 | 435.9 | 381.7
1793 | 1666 | 526.1 | 472.6 | 500.1 | 470.1 | 454.2 | 452 | 426.5 | 430.3 | 435.9 | 381.8
1794 | 1667 | 526.1 | 472.7 | 500.1 | 470.1 | 454.2 | 452.1 | 426.7 | 430.4 | 436 | 381.9
1795 | 1668 | 526.1 | 472.7 | 500.1 | 470.2 | 454.2 | 452.1 | 426.8 | 430.6 | 436 | 382
1796 | 1669 | 526.1 | 472.7 | 500.2 | 470.2 | 454.3 | 452.1 | 427 | 430.6 | 436.1 | 382.1
1797 | 1670 | 526.1 | 472.7 | 500.2 | 470.2 | 454.3 | 452.2 | 427.1 | 430.8 | 436.1 | 382.1
1798 | 1671 | 526.1 | 472.8 | 500.2 | 470.2 | 454.4 | 452.2 | 427.3 | 430.8 | 436.2 | 382.2
1799 | 1672 | 526.1 | 472.7 | 500.3 | 470.3 | 454.3 | 452.2 | 427.5 | 431 | 436.2 | 382.3
1800 | 1673 | 526.1 | 472.8 | 500.2 | 470.3 | 454.5 | 452.3 | 427.6 | 431.1 | 436.3 | 382.4
1801 | 1674 | 526.1 | 472.8 | 500.2 | 470.3 | 454.5 | 452.3 | 427.8 | 431.2 | 436.4 | 382.5
1802 | 1675 | 526.1 | 472.8 | 500.3 | 470.3 | 454.5 | 452.3 | 428 | 431.3 | 436.4 | 382.6
1803 | 1676 | 526.1 | 472.8 | 500.3 | 470.4 | 454.5 | 452.4 | 428.1 | 431.4 | 436.5 | 382.7
1804 | 1677 | 526.1 | 472.9 | 500.2 | 470.4 | 454.6 | 452.4 | 428.3 | 431.6 | 436.5 | 382.8
1805 | 1678 | 526.1 | 472.9 | 500.3 | 470.4 | 454.6 | 452.4 | 428.4 | 431.7 | 436.6 | 382.9
1806 | 1679 | 526 | 472.9 | 500.4 | 470.4 | 454.6 | 452.4 | 428.6 | 431.7 | 436.7 | 383
1807 | 1680 | 526 | 472.9 | 500.3 | 470.5 | 454.7 | 452.5 | 428.8 | 431.8 | 436.7 | 383.1
1808 | 1681 | 526 | 472.9 | 500.3 | 470.5 | 454.7 | 452.5 | 428.9 | 431.9 | 436.8 | 383.2
1809 | 1682 | 526 | 472.9 | 500.4 | 470.5 | 454.7 | 452.6 | 429.1 | 432 | 436.8 | 383.3
1810 | 1683 | 525.9 | 473 | 500.4 | 470.5 | 454.8 | 452.6 | 429.2 | 432.1 | 436.9 | 383.4
1811 | 1684 | 525.9 | 473 | 500.4 | 470.6 | 454.8 | 452.6 | 429.4 | 432.2 | 436.9 | 383.4
1812 | 1685 | 525.9 | 473 | 500.4 | 470.6 | 454.8 | 452.6 | 429.5 | 432.3 | 437 | 383.5
1813 | 1686 | 525.9 | 473 | 500.5 | 470.6 | 454.8 | 452.6 | 429.7 | 432.4 | 437 | 383.6
1814 | 1687 | 525.8 | 473 | 500.4 | 470.7 | 454.9 | 452.7 | 429.9 | 432.5 | 437.1 | 383.7
1815 | 1688 | 525.9 | 473.1 | 500.4 | 470.7 | 454.9 | 452.7 | 430 | 432.6 | 437.2 | 383.8
1816 | 1689 | 525.8 | 473.1 | 500.5 | 470.7 | 454.9 | 452.7 | 430.2 | 432.7 | 437.2 | 383.9
1817 | 1690 | 525.8 | 473.1 | 500.5 | 470.7 | 454.9 | 452.7 | 430.4 | 432.8 | 437.3 | 384
1818 | 1691 | 525.8 | 473.1 | 500.5 | 470.7 | 454.9 | 452.7 | 430.6 | 432.9 | 437.3 | 384
1819 | 1692 | 525.8 | 473.1 | 500.5 | 470.8 | 454.9 | 452.7 | 430.8 | 432.9 | 437.4 | 384.1
1820 | 1693 | 525.8 | 473.1 | 500.6 | 470.8 | 454.8 | 452.7 | 430.9 | 433 | 437.4 | 384.2
1821 | 1694 | 525.8 | 473.2 | 500.5 | 470.8 | 454.9 | 452.6 | 431.1 | 433.2 | 437.5 | 384.3
1822 | 1695 | 525.7 | 473.2 | 500.5 | 470.9 | 455 | 452.6 | 431.2 | 433.3 | 437.5 | 384.4
1823 | 1696 | 525.8 | 473.2 | 500.5 | 470.9 | 455 | 452.6 | 431.4 | 433.3 | 437.6 | 384.5
1824 | 1697 | 525.8 | 473.2 | 500.6 | 470.9 | 455 | 452.6 | 431.5 | 433.4 | 437.6 | 384.6
1825 | 1698 | 525.8 | 473.2 | 500.5 | 470.9 | 455.1 | 452.6 | 431.7 | 433.5 | 437.6 | 384.7
1826 | 1699 | 525.8 | 473.3 | 500.5 | 471 | 455.2 | 452.6 | 431.8 | 433.6 | 437.7 | 384.8
1827 | 1700 | 525.8 | 473.3 | 500.6 | 471 | 455.1 | 452.5 | 431.9 | 433.7 | 437.7 | 384.9
1828 | 1701 | 525.8 | 473.3 | 500.6 | 471 | 455.2 | 452.4 | 432 | 433.8 | 437.8 | 385
1829 | 1702 | 525.9 | 473.3 | 500.6 | 471 | 455.2 | 452.4 | 432.1 | 433.9 | 437.8 | 385.1
1830 | 1703 | 525.9 | 473.3 | 500.6 | 471.1 | 455.2 | 452.3 | 432.3 | 434 | 437.9 | 385.3
1831 | 1704 | 525.9 | 473.3 | 500.7 | 471.1 | 455.2 | 452.2 | 432.4 | 434 | 437.9 | 385.4
1832 | 1705 | 525.9 | 473.4 | 500.6 | 471.1 | 455.3 | 452.1 | 432.5 | 434.1 | 437.9 | 385.5
1833 | 1706 | 525.9 | 473.4 | 500.7 | 471.1 | 455.3 | 452 | 432.7 | 434.3 | 438 | 385.6
1834 | 1707 | 525.9 | 473.4 | 500.7 | 471.1 | 455.3 | 451.9 | 432.8 | 434.4 | 438.1 | 385.7
1835 | 1708 | 525.8 | 473.4 | 500.7 | 471.2 | 455.4 | 451.8 | 432.9 | 434.5 | 438.1 | 385.8
1836 | 1709 | 525.9 | 473.4 | 500.7 | 471.2 | 455.3 | 451.7 | 433.1 | 434.5 | 438.1 | 386
1837 | 1710 | 525.9 | 473.4 | 500.7 | 471.2 | 455.3 | 451.4 | 433.2 | 434.6 | 438.2 | 386.1
1838 | 1711 | 525.9 | 473.5 | 500.7 | 471.3 | 455.4 | 451.2 | 433.3 | 434.7 | 438.2 | 386.2
1839 | 1712 | 525.9 | 473.5 | 500.7 | 471.3 | 455.4 | 451.2 | 433.4 | 434.8 | 438.3 | 386.3
1840 | 1713 | 525.9 | 473.5 | 500.7 | 471.3 | 455.5 | 451 | 433.5 | 435 | 438.3 | 386.4
1841 | 1714 | 525.9 | 473.5 | 500.8 | 471.3 | 455.5 | 450.7 | 433.7 | 435.1 | 438.4 | 386.5
1842 | 1715 | 525.9 | 473.5 | 500.8 | 471.3 | 455.5 | 450.6 | 433.8 | 435.3 | 438.4 | 386.6
1843 | 1716 | 525.9 | 473.6 | 500.8 | 471.4 | 455.5 | 450.4 | 433.9 | 435.4 | 438.5 | 386.7
1844 | 1717 | 525.9 | 473.6 | 500.8 | 471.4 | 455.6 | 450.3 | 434 | 435.4 | 438.5 | 386.8
1845 | 1718 | 525.9 | 473.6 | 500.9 | 471.4 | 455.6 | 450.1 | 434.1 | 435.5 | 438.6 | 386.9
1846 | 1719 | 525.9 | 473.6 | 500.9 | 471.4 | 455.6 | 450 | 434.3 | 435.6 | 438.6 | 387.1
1847 | 1720 | 525.9 | 473.7 | 500.9 | 471.5 | 455.7 | 449.9 | 434.4 | 435.6 | 438.7 | 387.2
1848 | 1721 | 525.9 | 473.7 | 500.9 | 471.4 | 455.7 | 449.8 | 434.5 | 435.8 | 438.7 | 387.3
1849 | 1722 | 525.9 | 473.7 | 500.9 | 471.5 | 455.7 | 449.7 | 434.6 | 435.9 | 438.8 | 387.4
1850 | 1723 | 525.8 | 473.8 | 500.8 | 471.6 | 455.8 | 449.8 | 434.8 | 436 | 438.9 | 387.5
1851 | 1724 | 525.8 | 473.9 | 500.6 | 471.6 | 456.1 | 449.8 | 434.9 | 436.1 | 438.9 | 387.6
1852 | 1725 | 525.8 | 473.7 | 501 | 471.5 | 455.8 | 449.7 | 435 | 436.2 | 439.1 | 387.7
1853 | 1726 | 525.9 | 473.8 | 501 | 471.6 | 455.9 | 449.7 | 435.1 | 436.2 | 439.1 | 387.8
1854 | 1727 | 525.9 | 473.8 | 501 | 471.6 | 455.8 | 449.8 | 435.3 | 436.3 | 439.1 | 388
1855 | 1728 | 525.9 | 473.8 | 501 | 471.6 | 455.8 | 449.7 | 435.4 | 436.3 | 439.2 | 388.1
1856 | 1729 | 525.9 | 473.8 | 501 | 471.6 | 455.9 | 449.9 | 435.5 | 436.4 | 439.2 | 388.1
1857 | 1730 | 525.8 | 473.9 | 501 | 471.7 | 456 | 449.9 | 435.6 | 436.5 | 439.2 | 388.2
1858 | 1731 | 525.8 | 473.9 | 501.1 | 471.7 | 456 | 450 | 435.8 | 436.6 | 439.3 | 388.3
1859 | 1732 | 525.8 | 473.9 | 501.1 | 471.7 | 455.9 | 450.1 | 435.9 | 436.6 | 439.3 | 388.4
1860 | 1733 | 525.8 | 473.9 | 501 | 471.7 | 456 | 450.1 | 436 | 436.7 | 439.4 | 388.5
1861 | 1734 | 525.7 | 473.9 | 501 | 471.8 | 456.1 | 450.1 | 436.1 | 436.7 | 439.4 | 388.5
1862 | 1735 | 525.7 | 473.9 | 501.1 | 471.8 | 456.1 | 450.1 | 436.2 | 436.8 | 439.4 | 388.6
1863 | 1736 | 525.6 | 474 | 501.1 | 471.8 | 456.2 | 450.2 | 436.3 | 436.9 | 439.5 | 388.7
1864 | 1737 | 525.6 | 474 | 501.1 | 471.8 | 456.2 | 450.3 | 436.5 | 436.9 | 439.5 | 388.7
1865 | 1738 | 525.6 | 474 | 501.1 | 471.8 | 456.2 | 450.4 | 436.6 | 436.9 | 439.6 | 388.8
1866 | 1739 | 525.6 | 474 | 501.1 | 471.9 | 456.2 | 450.4 | 436.7 | 437 | 439.6 | 388.9
1867 | 1740 | 525.6 | 474.1 | 501.1 | 471.9 | 456.2 | 450.5 | 436.8 | 437 | 439.6 | 389
1868 | 1741 | 525.6 | 474.1 | 501.1 | 471.9 | 456.3 | 450.7 | 437 | 437.1 | 439.7 | 389.1
1869 | 1742 | 525.6 | 474.1 | 501.2 | 471.9 | 456.3 | 451 | 437.1 | 437.1 | 439.7 | 389.1
1870 | 1743 | 525.6 | 474.1 | 501.2 | 471.9 | 456.3 | 451.1 | 437.2 | 437.2 | 439.8 | 389.2
1871 | 1744 | 525.6 | 474.2 | 501.2 | 472 | 456.4 | 451.1 | 437.4 | 437.2 | 439.8 | 389.3
1872 | 1745 | 525.6 | 474.2 | 501.2 | 472 | 456.5 | 451.3 | 437.5 | 437.3 | 439.8 | 389.3
1873 | 1746 | 525.6 | 474.2 | 501.2 | 472 | 456.5 | 451.5 | 437.6 | 437.2 | 439.8 | 389.4
1874 | 1747 | 525.6 | 474.2 | 501.2 | 472 | 456.6 | 451.5 | 437.7 | 437.2 | 439.9 | 389.5
1875 | 1748 | 525.6 | 474.3 | 501.2 | 472.1 | 456.7 | 451.6 | 437.8 | 437.3 | 439.9 | 389.6
1876 | 1749 | 525.6 | 474.3 | 501.3 | 472.1 | 456.7 | 451.7 | 437.9 | 437.3 | 439.9 | 389.6
1877 | 1750 | 525.6 | 474.3 | 501.3 | 472.1 | 456.8 | 451.9 | 438 | 437.3 | 440 | 389.7
1878 | 1751 | 525.6 | 474.3 | 501.3 | 472.1 | 456.8 | 452.1 | 438.1 | 437.3 | 440 | 389.8
1879 | 1752 | 525.6 | 474.3 | 501.3 | 472.1 | 456.8 | 452.5 | 438.2 | 437.3 | 440.1 | 389.9
1880 | 1753 | 525.6 | 474.4 | 501.3 | 472.1 | 456.9 | 452.7 | 438.3 | 437.5 | 440.1 | 390
1881 | 1754 | 525.6 | 474.4 | 501.3 | 472.2 | 456.9 | 452.9 | 438.5 | 437.5 | 440.2 | 390.1
1882 | 1755 | 525.7 | 474.4 | 501.3 | 472.2 | 456.9 | 453 | 438.5 | 437.6 | 440.3 | 390.2
1883 | 1756 | 525.7 | 474.4 | 501.4 | 472.2 | 456.9 | 453.2 | 438.7 | 437.6 | 440.3 | 390.2
1884 | 1757 | 525.7 | 474.5 | 501.4 | 472.2 | 457.1 | 453.8 | 438.8 | 437.6 | 440.4 | 390.3
1885 | 1758 | 525.7 | 474.5 | 501.4 | 472.3 | 457.2 | 454.2 | 438.9 | 437.7 | 440.4 | 390.4
1886 | 1759 | 525.7 | 474.5 | 501.4 | 472.3 | 457.2 | 454.4 | 439 | 437.8 | 440.5 | 390.5
1887 | 1760 | 525.6 | 474.5 | 501.5 | 472.3 | 457.2 | 454.5 | 439.1 | 437.8 | 440.5 | 390.6
1888 | 1761 | 525.6 | 474.5 | 501.4 | 472.3 | 457.3 | 454.6 | 439.2 | 437.9 | 440.6 | 390.6
1889 | 1762 | 525.6 | 474.6 | 501.5 | 472.3 | 457.3 | 454.7 | 439.3 | 437.9 | 440.6 | 390.8
1890 | 1763 | 525.7 | 474.6 | 501.5 | 472.3 | 457.3 | 454.7 | 439.4 | 438 | 440.7 | 390.9
1891 | 1764 | 525.7 | 474.6 | 501.5 | 472.4 | 457.4 | 454.9 | 439.5 | 438.1 | 440.8 | 391
1892 | 1765 | 525.7 | 474.6 | 501.5 | 472.4 | 457.5 | 454.8 | 439.6 | 438.2 | 440.8 | 391.1
1893 | 1766 | 525.7 | 474.6 | 501.6 | 472.4 | 457.5 | 454.7 | 439.7 | 438.2 | 440.9 | 391.2
1894 | 1767 | 525.7 | 474.6 | 501.6 | 472.4 | 457.5 | 454.7 | 439.8 | 438.3 | 440.9 | 391.3
1895 | 1768 | 525.7 | 474.7 | 501.6 | 472.5 | 457.6 | 454.9 | 439.9 | 438.3 | 441 | 391.4
1896 | 1769 | 525.7 | 474.7 | 501.6 | 472.5 | 457.6 | 454.7 | 440 | 438.4 | 441 | 391.5
1897 | 1770 | 525.7 | 474.7 | 501.6 | 472.5 | 457.6 | 454.8 | 440.1 | 438.4 | 441.1 | 391.6
1898 | 1771 | 525.6 | 474.8 | 501.6 | 472.5 | 457.7 | 455.1 | 440.2 | 438.5 | 441.1 | 391.6
1899 | 1772 | 525.6 | 474.8 | 501.6 | 472.5 | 457.7 | 455.2 | 440.3 | 438.5 | 441.1 | 391.7
1900 | 1773 | 525.6 | 474.8 | 501.6 | 472.6 | 457.7 | 455.3 | 440.4 | 438.6 | 441.1 | 391.9
1901 | 1774 | 525.6 | 474.8 | 501.7 | 472.6 | 457.8 | 455.7 | 440.5 | 438.6 | 441.2 | 392
1902 | 1775 | 525.6 | 474.9 | 501.7 | 472.6 | 457.9 | 456.1 | 440.7 | 438.6 | 441.2 | 392.1
1903 | 1776 | 525.7 | 474.9 | 501.7 | 472.6 | 458 | 456.1 | 440.7 | 438.7 | 441.3 | 392.1
1904 | 1777 | 525.7 | 474.9 | 501.7 | 472.6 | 458 | 456.1 | 440.8 | 438.8 | 441.3 | 392.2
1905 | 1778 | 525.7 | 474.9 | 501.7 | 472.7 | 458 | 456 | 440.9 | 438.8 | 441.4 | 392.3
1906 | 1779 | 525.7 | 474.9 | 501.7 | 472.7 | 458.2 | 456.2 | 441 | 438.9 | 441.4 | 392.4
1907 | 1780 | 525.7 | 475 | 501.7 | 472.7 | 458.3 | 456.1 | 441 | 439 | 441.5 | 392.5
1908 | 1781 | 525.7 | 475 | 501.8 | 472.7 | 458.4 | 456.2 | 441.1 | 439.1 | 441.5 | 392.6
1909 | 1782 | 525.7 | 475 | 501.7 | 472.7 | 458.6 | 456.3 | 441.2 | 439.1 | 441.6 | 392.7
1910 | 1783 | 525.7 | 475 | 501.8 | 472.7 | 458.6 | 456.4 | 441.3 | 439.3 | 441.6 | 392.8
1911 | 1784 | 525.7 | 475 | 501.8 | 472.8 | 458.5 | 456.4 | 441.4 | 439.4 | 441.6 | 392.9
1912 | 1785 | 525.6 | 475.1 | 501.8 | 472.8 | 458.7 | 456.5 | 441.5 | 439.4 | 441.7 | 393
1913 | 1786 | 525.6 | 475.1 | 501.8 | 472.8 | 458.8 | 456.5 | 441.6 | 439.4 | 441.7 | 393.1
1914 | 1787 | 525.6 | 475.1 | 501.8 | 472.8 | 458.8 | 456.7 | 441.6 | 439.4 | 441.7 | 393.2
1915 | 1788 | 525.6 | 475.1 | 501.8 | 472.8 | 458.8 | 457 | 441.7 | 439.4 | 441.8 | 393.3
1916 | 1789 | 525.6 | 475.2 | 501.8 | 472.9 | 459 | 457 | 441.8 | 439.5 | 441.8 | 393.4
1917 | 1790 | 525.6 | 475.2 | 501.8 | 472.9 | 459 | 457.1 | 441.9 | 439.6 | 441.8 | 393.5
1918 | 1791 | 525.6 | 475.2 | 501.9 | 472.9 | 459 | 457 | 442 | 439.7 | 441.8 | 393.6
1919 | 1792 | 525.6 | 475.2 | 501.8 | 472.9 | 459.1 | 457 | 442 | 439.7 | 441.9 | 393.7
1920 | 1793 | 525.6 | 475.3 | 501.8 | 473 | 459.2 | 457 | 442.1 | 439.7 | 441.9 | 393.8
1921 | 1794 | 525.6 | 475.3 | 501.9 | 473 | 459.3 | 457 | 442.2 | 439.8 | 441.9 | 393.9
1922 | 1795 | 525.6 | 475.3 | 501.9 | 473 | 459.4 | 457.1 | 442.2 | 440 | 442 | 394
1923 | 1796 | 525.6 | 475.3 | 501.9 | 473 | 459.5 | 457.2 | 442.3 | 440.1 | 442 | 394.1
1924 | 1797 | 525.6 | 475.3 | 501.9 | 473 | 459.5 | 457.1 | 442.3 | 440.3 | 442.1 | 394.2
1925 | 1798 | 525.6 | 475.3 | 502 | 473.1 | 459.6 | 457.1 | 442.4 | 440.3 | 442.1 | 394.3
1926 | 1799 | 525.7 | 475.4 | 501.9 | 473.1 | 459.6 | 457.1 | 442.5 | 440.4 | 442.1 | 394.4
1927 | 1800 | 525.7 | 475.4 | 501.9 | 473.1 | 459.7 | 457.4 | 442.6 | 440.4 | 442.2 | 394.5
1928 | 1801 | 525.7 | 475.4 | 502 | 473.1 | 459.7 | 457.8 | 442.7 | 440.5 | 442.2 | 394.6
1929 | 1802 | 525.8 | 475.4 | 502 | 473.1 | 459.7 | 457.9 | 442.8 | 440.6 | 442.2 | 394.7
1930 | 1803 | 525.8 | 475.4 | 502 | 473.2 | 459.9 | 457.9 | 442.9 | 440.7 | 442.2 | 394.8
1931 | 1804 | 525.9 | 475.5 | 502 | 473.2 | 460 | 458.1 | 442.9 | 440.8 | 442.3 | 394.9
1932 | 1805 | 525.9 | 475.4 | 502.1 | 473.2 | 460 | 458.1 | 443 | 440.9 | 442.3 | 395
1933 | 1806 | 525.9 | 475.5 | 502.1 | 473.2 | 460.1 | 458.1 | 443.1 | 440.8 | 442.3 | 395.1
1934 | 1807 | 525.9 | 475.5 | 502.1 | 473.3 | 460.2 | 458.2 | 443.2 | 440.7 | 442.4 | 395.2
1935 | 1808 | 526 | 475.5 | 502.1 | 473.3 | 460.3 | 458.1 | 443.2 | 440.6 | 442.4 | 395.3
1936 | 1809 | 526 | 475.5 | 502.1 | 473.3 | 460.4 | 458 | 443.3 | 440.7 | 442.4 | 395.4
1937 | 1810 | 526 | 475.6 | 502.1 | 473.3 | 460.5 | 457.9 | 443.3 | 440.8 | 442.4 | 395.5
1938 | 1811 | 526.1 | 475.6 | 502.1 | 473.3 | 460.5 | 458 | 443.4 | 441 | 442.4 | 395.6
1939 | 1812 | 526.1 | 475.6 | 502.2 | 473.3 | 460.5 | 458 | 443.4 | 441.2 | 442.5 | 395.7
1940 | 1813 | 526.1 | 475.6 | 502.2 | 473.4 | 460.6 | 458.2 | 443.5 | 441.4 | 442.5 | 395.8
1941 | 1814 | 526.1 | 475.6 | 502.2 | 473.4 | 460.7 | 458.1 | 443.5 | 441.4 | 442.5 | 395.9
1942 | 1815 | 526.1 | 475.7 | 502.2 | 473.4 | 460.7 | 458.1 | 443.6 | 441.3 | 442.5 | 396
1943 | 1816 | 526.1 | 475.7 | 502.2 | 473.4 | 460.8 | 458.1 | 443.7 | 441.4 | 442.6 | 396.1
1944 | 1817 | 526.1 | 475.7 | 502.2 | 473.5 | 460.9 | 458.2 | 443.8 | 441.4 | 442.6 | 396.2
1945 | 1818 | 526.1 | 475.7 | 502.2 | 473.5 | 460.9 | 458.2 | 443.9 | 441.5 | 442.6 | 396.3
1946 | 1819 | 526.1 | 475.7 | 502.3 | 473.5 | 460.9 | 458.2 | 443.9 | 441.6 | 442.7 | 396.4
1947 | 1820 | 526 | 475.8 | 502.2 | 473.5 | 461.1 | 458.2 | 443.9 | 441.5 | 442.7 | 396.4
1948 | 1821 | 526 | 475.8 | 502.2 | 473.5 | 461.1 | 458.6 | 444 | 441.6 | 442.8 | 396.5
1949 | 1822 | 526 | 475.8 | 502.3 | 473.5 | 461.1 | 458.7 | 444 | 441.7 | 442.8 | 396.6
1950 | 1823 | 526 | 475.8 | 502.3 | 473.6 | 461.1 | 458.8 | 444.1 | 441.8 | 442.8 | 396.7
1951 | 1824 | 526 | 475.9 | 502.3 | 473.6 | 461.3 | 458.7 | 444.1 | 442 | 442.8 | 396.8
1952 | 1825 | 526 | 475.9 | 502.3 | 473.6 | 461.4 | 458.5 | 444.1 | 442.1 | 442.8 | 396.9
1953 | 1826 | 526 | 475.9 | 502.4 | 473.6 | 461.4 | 458.4 | 444.2 | 442.2 | 442.9 | 397
1954 | 1827 | 526 | 475.9 | 502.3 | 473.7 | 461.5 | 458.5 | 444.3 | 442.2 | 442.9 | 397.1
1955 | 1828 | 526 | 475.9 | 502.3 | 473.7 | 461.5 | 458.7 | 444.4 | 442.3 | 442.9 | 397.2
1956 | 1829 | 525.9 | 475.9 | 502.4 | 473.7 | 461.6 | 458.7 | 444.4 | 442.5 | 442.9 | 397.3
1957 | 1830 | 525.9 | 475.9 | 502.4 | 473.7 | 461.7 | 458.5 | 444.5 | 442.5 | 443 | 397.4
1958 | 1831 | 525.9 | 476 | 502.4 | 473.7 | 461.8 | 458.6 | 444.5 | 442.5 | 443 | 397.5
1959 | 1832 | 525.8 | 476 | 502.4 | 473.8 | 461.9 | 458.6 | 444.5 | 442.6 | 443 | 397.6
1960 | 1833 | 525.8 | 476 | 502.5 | 473.8 | 461.9 | 458.6 | 444.6 | 442.7 | 443 | 397.7
1961 | 1834 | 525.8 | 476 | 502.4 | 473.8 | 462 | 458.7 | 444.6 | 442.7 | 443 | 397.7
1962 | 1835 | 525.8 | 476.1 | 502.4 | 473.8 | 462.1 | 458.9 | 444.7 | 442.9 | 443.1 | 397.8
1963 | 1836 | 525.8 | 476.1 | 502.5 | 473.8 | 462.1 | 458.8 | 444.7 | 442.9 | 443.1 | 397.9
1964 | 1837 | 525.8 | 476.1 | 502.5 | 473.8 | 462.1 | 459 | 444.8 | 443 | 443.1 | 398
1965 | 1838 | 525.8 | 476.1 | 502.5 | 473.9 | 462.2 | 459.1 | 444.8 | 443 | 443.1 | 398.1
1966 | 1839 | 525.8 | 476.1 | 502.5 | 473.9 | 462.2 | 459 | 444.9 | 443.1 | 443.1 | 398.2
1967 | 1840 | 525.8 | 476.1 | 502.5 | 473.9 | 462.2 | 459 | 445 | 443.2 | 443.2 | 398.3
1968 | 1841 | 525.7 | 476.2 | 502.5 | 473.9 | 462.3 | 459.2 | 445 | 443.3 | 443.2 | 398.4
1969 | 1842 | 525.7 | 476.2 | 502.5 | 473.9 | 462.3 | 459.3 | 445 | 443.5 | 443.2 | 398.5
1970 | 1843 | 525.7 | 476.2 | 502.6 | 474 | 462.3 | 459.4 | 445.1 | 443.8 | 443.2 | 398.6
1971 | 1844 | 525.7 | 476.2 | 502.6 | 474 | 462.3 | 459.4 | 445.2 | 444 | 443.2 | 398.7
1972 | 1845 | 525.7 | 476.2 | 502.5 | 474 | 462.3 | 459.3 | 445.2 | 443.9 | 443.3 | 398.8
1973 | 1846 | 525.7 | 476.3 | 502.5 | 474 | 462.4 | 459.4 | 445.3 | 444 | 443.3 | 398.9
1974 | 1847 | 525.7 | 476.3 | 502.6 | 474 | 462.4 | 459.4 | 445.3 | 443.9 | 443.3 | 399
1975 | 1848 | 525.7 | 476.3 | 502.6 | 474.1 | 462.5 | 459.5 | 445.4 | 443.9 | 443.3 | 399.1
1976 | 1849 | 525.7 | 476.3 | 502.6 | 474.1 | 462.5 | 459.6 | 445.5 | 443.9 | 443.4 | 399.2
1977 | 1850 | 525.7 | 476.3 | 502.6 | 474.1 | 462.5 | 459.6 | 445.6 | 443.9 | 443.4 | 399.3
1978 | 1851 | 525.7 | 476.3 | 502.6 | 474.1 | 462.5 | 459.6 | 445.7 | 443.9 | 443.4 | 399.4
1979 | 1852 | 525.8 | 476.4 | 502.6 | 474.1 | 462.6 | 459.7 | 445.8 | 443.8 | 443.4 | 399.5
1980 | 1853 | 525.8 | 476.4 | 502.6 | 474.1 | 462.6 | 459.8 | 445.8 | 443.8 | 443.5 | 399.6
1981 | 1854 | 525.8 | 476.4 | 502.7 | 474.1 | 462.6 | 459.9 | 445.9 | 443.8 | 443.5 | 399.7
1982 | 1855 | 525.8 | 476.4 | 502.7 | 474.2 | 462.7 | 460 | 446 | 443.9 | 443.5 | 399.8
1983 | 1856 | 525.8 | 476.5 | 502.6 | 474.2 | 462.7 | 460.1 | 446.1 | 443.9 | 443.6 | 399.9
1984 | 1857 | 525.8 | 476.5 | 502.7 | 474.2 | 462.6 | 460.1 | 446.1 | 444 | 443.6 | 400
1985 | 1858 | 525.9 | 476.5 | 502.7 | 474.3 | 462.6 | 460.1 | 446.2 | 444.1 | 443.6 | 400.1
1986 | 1859 | 525.9 | 476.5 | 502.7 | 474.3 | 462.7 | 460.2 | 446.3 | 444.2 | 443.7 | 400.1
1987 | 1860 | 525.9 | 476.5 | 502.7 | 474.3 | 462.7 | 460.2 | 446.4 | 444.3 | 443.7 | 400.2
1988 | 1861 | 525.9 | 476.5 | 502.8 | 474.3 | 462.7 | 460.2 | 446.4 | 444.4 | 443.7 | 400.3
1989 | 1862 | 525.9 | 476.5 | 502.7 | 474.3 | 462.7 | 460.2 | 446.5 | 444.5 | 443.8 | 400.5
1990 | 1863 | 525.9 | 476.6 | 502.7 | 474.4 | 462.8 | 460.3 | 446.5 | 444.7 | 443.8 | 400.6
1991 | 1864 | 525.9 | 476.6 | 502.8 | 474.4 | 462.8 | 460.3 | 446.6 | 444.7 | 443.8 | 400.8
1992 | 1865 | 525.9 | 476.6 | 502.8 | 474.4 | 462.8 | 460.3 | 446.6 | 444.7 | 443.8 | 400.9
1993 | 1866 | 525.9 | 476.6 | 502.8 | 474.4 | 462.9 | 460.4 | 446.7 | 444.7 | 443.8 | 401.1
1994 | 1867 | 525.9 | 476.6 | 502.8 | 474.4 | 463 | 460.4 | 446.7 | 444.7 | 443.9 | 401.2
1995 | 1868 | 525.9 | 476.6 | 502.9 | 474.4 | 463 | 460.4 | 446.8 | 444.8 | 443.9 | 401.3
1996 | 1869 | 525.9 | 476.7 | 502.8 | 474.5 | 463 | 460.4 | 446.9 | 444.9 | 443.9 | 401.4
1997 | 1870 | 525.9 | 476.7 | 502.8 | 474.5 | 463 | 460.5 | 446.9 | 444.9 | 444 | 401.5
1998 | 1871 | 525.9 | 476.7 | 502.9 | 474.5 | 463 | 460.6 | 446.9 | 444.9 | 444 | 401.6
1999 | 1872 | 525.9 | 476.7 | 502.9 | 474.5 | 463.1 | 460.6 | 447 | 444.9 | 444 | 401.7
2000 | 1873 | 526 | 476.8 | 502.9 | 474.5 | 463.1 | 460.6 | 447 | 444.9 | 444 | 401.8
2001 | 1874 | 526 | 476.8 | 502.9 | 474.6 | 463.1 | 460.6 | 447.1 | 445 | 444 | 401.9
2002 | 1875 | 526 | 476.8 | 502.9 | 474.6 | 463.2 | 460.6 | 447.1 | 445.1 | 444 | 402
2003 | 1876 | 526 | 476.8 | 502.9 | 474.6 | 463.2 | 460.7 | 447.2 | 445.1 | 444 | 402.1
2004 | 1877 | 525.9 | 476.8 | 502.9 | 474.6 | 463.2 | 460.7 | 447.2 | 445.1 | 444.1 | 402.1
2005 | 1878 | 525.9 | 476.8 | 502.9 | 474.6 | 463.2 | 460.7 | 447.2 | 445.2 | 444.1 | 402.2
2006 | 1879 | 526 | 476.9 | 502.9 | 474.7 | 463.2 | 460.8 | 447.3 | 445.2 | 444.1 | 402.3
2007 | 1880 | 526 | 476.9 | 502.9 | 474.7 | 463.2 | 460.8 | 447.3 | 445.3 | 444.1 | 402.4
2008 | 1881 | 525.9 | 476.9 | 502.9 | 474.7 | 463.3 | 460.8 | 447.4 | 445.3 | 444.1 | 402.5
2009 | 1882 | 526 | 476.9 | 503 | 474.7 | 463.3 | 460.8 | 447.4 | 445.4 | 444.1 | 402.6
2010 | 1883 | 526 | 476.9 | 503 | 474.7 | 463.4 | 460.9 | 447.4 | 445.4 | 444.1 | 402.6
2011 | 1884 | 526 | 477 | 503 | 474.8 | 463.4 | 460.9 | 447.5 | 445.4 | 444.1 | 402.7
2012 | 1885 | 526 | 477 | 503 | 474.8 | 463.5 | 460.9 | 447.5 | 445.5 | 444.1 | 402.8
2013 | 1886 | 526 | 477 | 503.1 | 474.8 | 463.5 | 460.9 | 447.6 | 445.6 | 444.1 | 403
2014 | 1887 | 526 | 477 | 503 | 474.8 | 463.5 | 460.9 | 447.6 | 445.6 | 444.1 | 403.1
2015 | 1888 | 526.1 | 477 | 503 | 474.9 | 463.5 | 460.9 | 447.6 | 445.7 | 444.1 | 403.2
2016 | 1889 | 526.1 | 477 | 503.1 | 474.9 | 463.5 | 461 | 447.7 | 445.8 | 444.1 | 403.2
2017 | 1890 | 526.1 | 477.1 | 503.1 | 474.9 | 463.6 | 461 | 447.7 | 445.9 | 444.1 | 403.3
2018 | 1891 | 526.1 | 477.1 | 503.1 | 474.9 | 463.6 | 461.1 | 447.8 | 445.9 | 444.1 | 403.4
2019 | 1892 | 526.1 | 477.1 | 503.1 | 474.9 | 463.7 | 461 | 447.8 | 445.9 | 444.1 | 403.5
2020 | 1893 | 526.1 | 477.1 | 503.1 | 475 | 463.6 | 461.1 | 447.8 | 445.9 | 444.1 | 403.6
2021 | 1894 | 526.1 | 477.1 | 503.1 | 475 | 463.7 | 461.2 | 447.9 | 446 | 444.1 | 403.8
2022 | 1895 | 526.1 | 477.1 | 503.1 | 475 | 463.8 | 461.2 | 447.9 | 446.1 | 444 | 403.9
2023 | 1896 | 526.1 | 477.1 | 503.2 | 475 | 463.7 | 461.3 | 447.9 | 446.2 | 444 | 404
2024 | 1897 | 526.2 | 477.1 | 503.2 | 475.1 | 463.8 | 461.3 | 448 | 446.2 | 444 | 404.2
2025 | 1898 | 526.2 | 477.2 | 503.2 | 475.1 | 463.9 | 461.4 | 448 | 446.3 | 444 | 404.3
2026 | 1899 | 526.2 | 477.2 | 503.2 | 475.1 | 463.9 | 461.5 | 448.1 | 446.3 | 444 | 404.4
2027 | 1900 | 526.2 | 477.2 | 503.2 | 475.1 | 463.9 | 461.5 | 448.1 | 446.3 | 444 | 404.6
2028 | 1901 | 526.2 | 477.2 | 503.2 | 475.1 | 463.9 | 461.6 | 448.1 | 446.4 | 444 | 404.8
2029 | 1902 | 526.2 | 477.2 | 503.2 | 475.2 | 463.9 | 461.8 | 448.2 | 446.6 | 444 | 404.9
2030 | 1903 | 526.2 | 477.2 | 503.2 | 475.2 | 463.8 | 461.9 | 448.2 | 446.6 | 444 | 405
2031 | 1904 | 526.2 | 477.3 | 503.3 | 475.2 | 464 | 462 | 448.2 | 446.6 | 444 | 405.2
2032 | 1905 | 526.2 | 477.3 | 503.2 | 475.2 | 464 | 462 | 448.3 | 446.7 | 443.9 | 405.3
2033 | 1906 | 526.2 | 477.3 | 503.3 | 475.2 | 464 | 462.1 | 448.3 | 446.9 | 443.9 | 405.4
2034 | 1907 | 526.1 | 477.3 | 503.3 | 475.2 | 464 | 462.1 | 448.3 | 446.9 | 443.9 | 405.5
2035 | 1908 | 526.1 | 477.3 | 503.3 | 475.3 | 464.1 | 462.2 | 448.4 | 446.9 | 443.9 | 405.6
2036 | 1909 | 526.1 | 477.3 | 503.3 | 475.3 | 464.1 | 462.3 | 448.4 | 447 | 443.9 | 405.8
2037 | 1910 | 526.1 | 477.3 | 503.4 | 475.3 | 464.1 | 462.3 | 448.4 | 447 | 443.9 | 405.9
2038 | 1911 | 526.1 | 477.4 | 503.3 | 475.4 | 464.2 | 462.4 | 448.5 | 447 | 443.9 | 406
2039 | 1912 | 526 | 477.4 | 503.3 | 475.4 | 464.3 | 462.5 | 448.5 | 447.1 | 443.8 | 406.1
2040 | 1913 | 526 | 477.4 | 503.4 | 475.4 | 464.2 | 462.5 | 448.6 | 447.2 | 443.9 | 406.2
2041 | 1914 | 526 | 477.4 | 503.4 | 475.4 | 464.3 | 462.5 | 448.6 | 447.2 | 443.9 | 406.4
2042 | 1915 | 525.9 | 477.4 | 503.3 | 475.4 | 464.3 | 462.6 | 448.6 | 447.3 | 443.8 | 406.5
2043 | 1916 | 525.9 | 477.4 | 503.4 | 475.5 | 464.4 | 462.7 | 448.7 | 447.5 | 443.9 | 406.6
2044 | 1917 | 525.9 | 477.4 | 503.4 | 475.5 | 464.4 | 462.7 | 448.7 | 447.5 | 443.9 | 406.8
2045 | 1918 | 525.9 | 477.5 | 503.4 | 475.5 | 464.4 | 462.8 | 448.8 | 447.6 | 443.9 | 406.9
2046 | 1919 | 525.9 | 477.5 | 503.4 | 475.5 | 464.5 | 462.8 | 448.8 | 447.6 | 443.8 | 407
2047 | 1920 | 525.8 | 477.5 | 503.4 | 475.6 | 464.4 | 462.9 | 448.8 | 447.7 | 443.8 | 407.1
2048 | 1921 | 525.8 | 477.5 | 503.4 | 475.6 | 464.4 | 463 | 448.9 | 447.7 | 443.8 | 407.3
2049 | 1922 | 525.8 | 477.5 | 503.4 | 475.6 | 464.5 | 463 | 448.9 | 447.8 | 443.8 | 407.4
2050 | 1923 | 525.8 | 477.5 | 503.4 | 475.6 | 464.6 | 463.1 | 448.9 | 447.8 | 443.8 | 407.5
2051 | 1924 | 525.8 | 477.5 | 503.5 | 475.6 | 464.5 | 463.1 | 449 | 447.9 | 443.8 | 407.7
2052 | 1925 | 525.9 | 477.6 | 503.5 | 475.7 | 464.6 | 463.2 | 449 | 447.9 | 443.8 | 407.8
2053 | 1926 | 525.9 | 477.6 | 503.5 | 475.7 | 464.6 | 463.2 | 449.1 | 448 | 443.8 | 407.9
2054 | 1927 | 525.9 | 477.6 | 503.5 | 475.7 | 464.6 | 463.2 | 449.1 | 448.1 | 443.8 | 408
2055 | 1928 | 525.8 | 477.6 | 503.5 | 475.7 | 464.6 | 463.3 | 449.1 | 448.1 | 443.8 | 408.1
2056 | 1929 | 525.8 | 477.6 | 503.5 | 475.7 | 464.7 | 463.4 | 449.2 | 448.3 | 443.8 | 408.2
2057 | 1930 | 525.8 | 477.7 | 503.5 | 475.8 | 464.7 | 463.4 | 449.2 | 448.3 | 443.8 | 408.3
2058 | 1931 | 525.8 | 477.6 | 503.6 | 475.8 | 464.7 | 463.4 | 449.2 | 448.5 | 443.8 | 408.5
2059 | 1932 | 525.8 | 477.7 | 503.6 | 475.8 | 464.7 | 463.5 | 449.3 | 448.6 | 443.8 | 408.6
2060 | 1933 | 525.8 | 477.7 | 503.6 | 475.8 | 464.8 | 463.5 | 449.3 | 448.6 | 443.8 | 408.6
2061 | 1934 | 525.8 | 477.7 | 503.6 | 475.8 | 464.8 | 463.5 | 449.3 | 448.7 | 443.8 | 408.8
2062 | 1935 | 525.8 | 477.7 | 503.7 | 475.9 | 464.8 | 463.6 | 449.4 | 448.7 | 443.8 | 408.9
2063 | 1936 | 525.8 | 477.7 | 503.6 | 475.9 | 464.8 | 463.6 | 449.4 | 448.7 | 443.8 | 409
2064 | 1937 | 525.9 | 477.7 | 503.6 | 475.9 | 464.8 | 463.7 | 449.5 | 448.8 | 443.8 | 409.1
2065 | 1938 | 525.9 | 477.7 | 503.7 | 475.9 | 464.8 | 463.7 | 449.5 | 448.9 | 443.8 | 409.2
2066 | 1939 | 525.9 | 477.8 | 503.6 | 475.9 | 464.9 | 463.8 | 449.5 | 449 | 443.8 | 409.3
2067 | 1940 | 525.9 | 477.8 | 503.6 | 476 | 464.9 | 463.8 | 449.6 | 449 | 443.8 | 409.4
2068 | 1941 | 525.9 | 477.8 | 503.7 | 476 | 464.9 | 463.8 | 449.6 | 449.1 | 443.8 | 409.5
2069 | 1942 | 525.9 | 477.8 | 503.7 | 476 | 464.9 | 463.8 | 449.6 | 449 | 443.9 | 409.6
2070 | 1943 | 525.8 | 477.8 | 503.7 | 476 | 465 | 463.9 | 449.7 | 449.1 | 443.9 | 409.8
2071 | 1944 | 525.8 | 477.8 | 503.7 | 476 | 464.9 | 463.9 | 449.7 | 449.2 | 443.9 | 409.9
2072 | 1945 | 525.9 | 477.8 | 503.7 | 476.1 | 464.9 | 463.9 | 449.8 | 449.2 | 443.9 | 410
2073 | 1946 | 525.8 | 477.9 | 503.7 | 476.1 | 464.9 | 464 | 449.8 | 449.3 | 443.9 | 410.1
2074 | 1947 | 525.8 | 477.9 | 503.7 | 476.1 | 465 | 464 | 449.8 | 449.4 | 443.9 | 410.2
2075 | 1948 | 525.8 | 477.9 | 503.8 | 476.1 | 465 | 464.1 | 449.9 | 449.4 | 444 | 410.3
2076 | 1949 | 525.8 | 477.9 | 503.8 | 476.1 | 465 | 464.1 | 449.9 | 449.4 | 444 | 410.4
2077 | 1950 | 525.8 | 477.9 | 503.7 | 476.2 | 465 | 464.1 | 449.9 | 449.4 | 444 | 410.5
2078 | 1951 | 525.8 | 477.9 | 503.7 | 476.2 | 465 | 464.2 | 450 | 449.5 | 444 | 410.6
2079 | 1952 | 525.8 | 477.9 | 503.8 | 476.2 | 465.1 | 464.2 | 450 | 449.5 | 444 | 410.7
2080 | 1953 | 525.8 | 478 | 503.8 | 476.2 | 465.1 | 464.2 | 450.1 | 449.6 | 444 | 410.8
2081 | 1954 | 525.8 | 478 | 503.8 | 476.3 | 465.2 | 464.3 | 450.1 | 449.7 | 444 | 410.9
2082 | 1955 | 525.8 | 478 | 503.8 | 476.3 | 465.2 | 464.3 | 450.1 | 449.8 | 444.1 | 411
2083 | 1956 | 525.7 | 478 | 503.8 | 476.3 | 465.2 | 464.3 | 450.2 | 449.7 | 444.1 | 411.1
2084 | 1957 | 525.7 | 478 | 503.8 | 476.3 | 465.3 | 464.4 | 450.2 | 449.7 | 444.1 | 411.1
2085 | 1958 | 525.7 | 478 | 503.8 | 476.3 | 465.4 | 464.4 | 450.3 | 449.7 | 444.1 | 411.2
2086 | 1959 | 525.6 | 478 | 503.9 | 476.3 | 465.4 | 464.5 | 450.3 | 449.7 | 444.1 | 411.3
2087 | 1960 | 525.6 | 478.1 | 503.9 | 476.4 | 465.4 | 464.5 | 450.3 | 449.7 | 444.1 | 411.4
2088 | 1961 | 525.6 | 478.1 | 503.9 | 476.4 | 465.5 | 464.5 | 450.4 | 449.8 | 444.2 | 411.5
2089 | 1962 | 525.6 | 478.1 | 503.9 | 476.4 | 465.5 | 464.6 | 450.4 | 449.9 | 444.2 | 411.6
2090 | 1963 | 525.7 | 478.1 | 503.9 | 476.4 | 465.5 | 464.6 | 450.4 | 449.9 | 444.2 | 411.7
2091 | 1964 | 525.7 | 478.1 | 503.9 | 476.4 | 465.6 | 464.7 | 450.5 | 450 | 444.2 | 411.8
2092 | 1965 | 525.7 | 478.2 | 503.9 | 476.5 | 465.7 | 464.7 | 450.5 | 450 | 444.2 | 411.9
2093 | 1966 | 525.7 | 478.1 | 503.9 | 476.5 | 465.7 | 464.7 | 450.5 | 450 | 444.3 | 412
2094 | 1967 | 525.7 | 478.2 | 503.9 | 476.5 | 465.8 | 464.8 | 450.6 | 450 | 444.3 | 412
2095 | 1968 | 525.8 | 478.2 | 503.9 | 476.5 | 465.9 | 464.8 | 450.6 | 450 | 444.3 | 412.1
2096 | 1969 | 525.8 | 478.2 | 503.9 | 476.5 | 465.9 | 464.8 | 450.7 | 450.1 | 444.3 | 412.1
2097 | 1970 | 525.9 | 478.2 | 504 | 476.5 | 465.9 | 464.9 | 450.7 | 450.2 | 444.4 | 412.2
2098 | 1971 | 525.9 | 478.2 | 503.9 | 476.6 | 466 | 464.9 | 450.7 | 450.2 | 444.4 | 412.2
2099 | 1972 | 525.9 | 478.3 | 503.9 | 476.6 | 466.1 | 465 | 450.8 | 450.3 | 444.4 | 412.3
2100 | 1973 | 525.9 | 478.2 | 504 | 476.6 | 466.1 | 465 | 450.8 | 450.4 | 444.5 | 412.3
2101 | 1974 | 525.9 | 478.3 | 504 | 476.6 | 466.2 | 465 | 450.8 | 450.5 | 444.5 | 412.4
2102 | 1975 | 525.9 | 478.3 | 504 | 476.6 | 466.2 | 465.1 | 450.9 | 450.6 | 444.5 | 412.5
2103 | 1976 | 525.9 | 478.3 | 504 | 476.6 | 466.2 | 465.1 | 450.9 | 450.6 | 444.6 | 412.6
2104 | 1977 | 525.9 | 478.3 | 504.1 | 476.6 | 466.2 | 465.1 | 450.9 | 450.6 | 444.6 | 412.7
2105 | 1978 | 526 | 478.3 | 504 | 476.7 | 466.3 | 465.2 | 451 | 450.7 | 444.6 | 412.7
2106 | 1979 | 526 | 478.4 | 504 | 476.7 | 466.4 | 465.2 | 451 | 450.8 | 444.6 | 412.8
2107 | 1980 | 526 | 478.4 | 504.1 | 476.7 | 466.4 | 465.2 | 451 | 451 | 444.7 | 412.8
2108 | 1981 | 526 | 478.4 | 504 | 476.7 | 466.5 | 465.3 | 451.1 | 451.1 | 444.7 | 412.8
2109 | 1982 | 526.1 | 478.4 | 504.1 | 476.8 | 466.5 | 465.3 | 451.1 | 451.1 | 444.7 | 412.9
2110 | 1983 | 526.1 | 478.4 | 504.1 | 476.8 | 466.5 | 465.4 | 451.1 | 451.1 | 444.7 | 412.9
2111 | 1984 | 526.1 | 478.4 | 504.1 | 476.8 | 466.6 | 465.4 | 451.2 | 451.2 | 444.8 | 413
2112 | 1985 | 526.1 | 478.4 | 504.1 | 476.8 | 466.6 | 465.5 | 451.2 | 451.3 | 444.8 | 413
2113 | 1986 | 526.1 | 478.5 | 504.1 | 476.8 | 466.7 | 465.5 | 451.3 | 451.3 | 444.8 | 413.1
2114 | 1987 | 526.1 | 478.5 | 504.2 | 476.8 | 466.7 | 465.5 | 451.3 | 451.4 | 444.8 | 413.1
2115 | 1988 | 526.1 | 478.5 | 504.1 | 476.9 | 466.8 | 465.6 | 451.3 | 451.4 | 444.9 | 413.2
2116 | 1989 | 526.1 | 478.5 | 504.1 | 476.9 | 466.8 | 465.6 | 451.4 | 451.5 | 444.9 | 413.3
2117 | 1990 | 526.1 | 478.5 | 504.2 | 476.9 | 466.8 | 465.7 | 451.4 | 451.4 | 444.9 | 413.3
2118 | 1991 | 526 | 478.5 | 504.2 | 476.9 | 466.9 | 465.7 | 451.4 | 451.5 | 445 | 413.4
2119 | 1992 | 526 | 478.6 | 504.2 | 476.9 | 466.9 | 465.8 | 451.5 | 451.5 | 445 | 413.4
2120 | 1993 | 526 | 478.6 | 504.2 | 477 | 467 | 465.8 | 451.5 | 451.5 | 445.1 | 413.5
2121 | 1994 | 526 | 478.6 | 504.2 | 477 | 467 | 465.8 | 451.5 | 451.6 | 445.1 | 413.5
2122 | 1995 | 526.1 | 478.6 | 504.2 | 477 | 467.1 | 465.9 | 451.6 | 451.7 | 445.1 | 413.5
2123 | 1996 | 526.1 | 478.6 | 504.2 | 477 | 467.1 | 465.9 | 451.6 | 451.9 | 445.2 | 413.5
2124 | 1997 | 526.1 | 478.6 | 504.2 | 477 | 467.1 | 465.9 | 451.6 | 451.9 | 445.2 | 413.6
2125 | 1998 | 526.1 | 478.6 | 504.2 | 477 | 467.1 | 466 | 451.7 | 451.9 | 445.2 | 413.6
2126 | 1999 | 526.1 | 478.6 | 504.2 | 477.1 | 467.2 | 466 | 451.7 | 452 | 445.3 | 413.7
2127 | 2000 | 526.2 | 478.7 | 504.3 | 477.1 | 467.3 | 466.1 | 451.8 | 452 | 445.3 | 413.7
2128 | 2001 | 526.2 | 478.7 | 504.3 | 477.1 | 467.3 | 466.1 | 451.8 | 452 | 445.3 | 413.8
2129 | 2002 | 526.2 | 478.7 | 504.3 | 477.1 | 467.3 | 466.1 | 451.8 | 452 | 445.4 | 413.9
2130 | 2003 | 526.2 | 478.7 | 504.3 | 477.1 | 467.4 | 466.2 | 451.9 | 452 | 445.4 | 413.9
2131 | 2004 | 526.2 | 478.7 | 504.3 | 477.2 | 467.4 | 466.2 | 451.9 | 452 | 445.4 | 414
2132 | 2005 | 526.3 | 478.7 | 504.3 | 477.2 | 467.4 | 466.2 | 451.9 | 452.1 | 445.5 | 414
2133 | 2006 | 526.3 | 478.8 | 504.3 | 477.2 | 467.5 | 466.3 | 452 | 452.2 | 445.5 | 414.1
2134 | 2007 | 526.3 | 478.8 | 504.3 | 477.2 | 467.5 | 466.3 | 452 | 452.3 | 445.5 | 414.1
2135 | 2008 | 526.3 | 478.7 | 504.4 | 477.2 | 467.5 | 466.3 | 452 | 452.4 | 445.6 | 414.2
2136 | 2009 | 526.3 | 478.8 | 504.4 | 477.3 | 467.6 | 466.4 | 452.1 | 452.4 | 445.6 | 414.3
2137 | 2010 | 526.4 | 478.8 | 504.4 | 477.3 | 467.6 | 466.4 | 452.1 | 452.4 | 445.6 | 414.3
2138 | 2011 | 526.4 | 478.8 | 504.4 | 477.3 | 467.7 | 466.5 | 452.1 | 452.4 | 445.7 | 414.3
2139 | 2012 | 526.4 | 478.8 | 504.4 | 477.3 | 467.7 | 466.5 | 452.2 | 452.5 | 445.7 | 414.4
2140 | 2013 | 526.4 | 478.8 | 504.4 | 477.3 | 467.8 | 466.5 | 452.2 | 452.5 | 445.7 | 414.4
2141 | 2014 | 526.4 | 478.9 | 504.4 | 477.3 | 467.8 | 466.6 | 452.2 | 452.6 | 445.8 | 414.5
2142 | 2015 | 526.4 | 478.8 | 504.5 | 477.4 | 467.8 | 466.6 | 452.3 | 452.6 | 445.8 | 414.5
2143 | 2016 | 526.4 | 478.9 | 504.5 | 477.4 | 467.8 | 466.6 | 452.3 | 452.6 | 445.8 | 414.5
2144 | 2017 | 526.4 | 478.9 | 504.4 | 477.4 | 467.9 | 466.7 | 452.3 | 452.6 | 445.9 | 414.6
2145 | 2018 | 526.4 | 478.9 | 504.5 | 477.4 | 467.9 | 466.7 | 452.4 | 452.6 | 445.9 | 414.6
2146 | 2019 | 526.3 | 478.9 | 504.5 | 477.4 | 467.9 | 466.7 | 452.4 | 452.6 | 445.9 | 414.6
2147 | 2020 | 526.3 | 478.9 | 504.5 | 477.5 | 468 | 466.8 | 452.4 | 452.7 | 446 | 414.7
2148 | 2021 | 526.3 | 479 | 504.5 | 477.5 | 468.1 | 466.8 | 452.5 | 452.7 | 446 | 414.7
2149 | 2022 | 526.3 | 478.9 | 504.5 | 477.5 | 468 | 466.9 | 452.5 | 452.7 | 446.1 | 414.7
2150 | 2023 | 526.3 | 479 | 504.5 | 477.5 | 468.1 | 466.9 | 452.6 | 452.7 | 446.1 | 414.8
2151 | 2024 | 526.3 | 479 | 504.5 | 477.6 | 468.1 | 466.9 | 452.6 | 452.7 | 446.1 | 414.8
2152 | 2025 | 526.2 | 479 | 504.5 | 477.6 | 468.2 | 467 | 452.6 | 452.7 | 446.1 | 414.9
2153 | 2026 | 526.2 | 479 | 504.6 | 477.6 | 468.2 | 467 | 452.7 | 452.7 | 446.2 | 414.9
2154 | 2027 | 526.2 | 479 | 504.5 | 477.6 | 468.3 | 467.1 | 452.7 | 452.7 | 446.2 | 414.9
2155 | 2028 | 526.2 | 479 | 504.6 | 477.6 | 468.3 | 467.1 | 452.7 | 452.8 | 446.3 | 415
2156 | 2029 | 526.2 | 479 | 504.6 | 477.6 | 468.3 | 467.1 | 452.8 | 452.8 | 446.3 | 415.1
2157 | 2030 | 526.1 | 479.1 | 504.6 | 477.7 | 468.4 | 467.2 | 452.8 | 452.9 | 446.3 | 415.1
2158 | 2031 | 526.1 | 479.1 | 504.6 | 477.7 | 468.4 | 467.2 | 452.8 | 452.9 | 446.4 | 415.2
2159 | 2032 | 526.1 | 479.1 | 504.6 | 477.7 | 468.4 | 467.2 | 452.9 | 453 | 446.4 | 415.2
2160 | 2033 | 526 | 479.1 | 504.7 | 477.7 | 468.4 | 467.3 | 452.9 | 453.1 | 446.4 | 415.3
2161 | 2034 | 526 | 479.1 | 504.6 | 477.7 | 468.5 | 467.3 | 452.9 | 453.1 | 446.5 | 415.3
2162 | 2035 | 525.9 | 479.1 | 504.6 | 477.7 | 468.6 | 467.4 | 452.9 | 453.2 | 446.5 | 415.4
2163 | 2036 | 525.9 | 479.1 | 504.7 | 477.7 | 468.5 | 467.4 | 453 | 453.3 | 446.5 | 415.4
2164 | 2037 | 525.9 | 479.2 | 504.6 | 477.8 | 468.6 | 467.4 | 453 | 453.3 | 446.6 | 415.4
2165 | 2038 | 525.9 | 479.2 | 504.6 | 477.8 | 468.7 | 467.5 | 453 | 453.3 | 446.6 | 415.5
2166 | 2039 | 525.8 | 479.2 | 504.7 | 477.8 | 468.7 | 467.5 | 453.1 | 453.3 | 446.6 | 415.5
2167 | 2040 | 525.8 | 479.2 | 504.7 | 477.8 | 468.7 | 467.5 | 453.1 | 453.4 | 446.7 | 415.6
2168 | 2041 | 525.8 | 479.2 | 504.7 | 477.8 | 468.8 | 467.6 | 453.1 | 453.4 | 446.7 | 415.6
2169 | 2042 | 525.8 | 479.2 | 504.7 | 477.9 | 468.8 | 467.6 | 453.2 | 453.5 | 446.7 | 415.7
2170 | 2043 | 525.8 | 479.2 | 504.7 | 477.8 | 468.8 | 467.7 | 453.2 | 453.5 | 446.7 | 415.7
2171 | 2044 | 525.8 | 479.2 | 504.7 | 477.9 | 468.9 | 467.7 | 453.2 | 453.5 | 446.8 | 415.8
2172 | 2045 | 525.8 | 479.3 | 504.7 | 477.9 | 468.9 | 467.7 | 453.3 | 453.5 | 446.8 | 415.8
2173 | 2046 | 525.8 | 479.3 | 504.7 | 477.9 | 468.9 | 467.8 | 453.3 | 453.5 | 446.8 | 415.9
2174 | 2047 | 525.8 | 479.3 | 504.8 | 477.9 | 468.9 | 467.8 | 453.3 | 453.5 | 446.9 | 415.9
2175 | 2048 | 525.8 | 479.3 | 504.7 | 477.9 | 469 | 467.9 | 453.4 | 453.7 | 446.9 | 416
2176 | 2049 | 525.8 | 479.3 | 504.7 | 478 | 469.1 | 467.9 | 453.4 | 453.7 | 446.9 | 416
2177 | 2050 | 525.8 | 479.3 | 504.8 | 478 | 469.1 | 467.9 | 453.4 | 453.7 | 446.9 | 416.1
2178 | 2051 | 525.8 | 479.3 | 504.8 | 478 | 469.1 | 468 | 453.5 | 453.7 | 447 | 416.1
2179 | 2052 | 525.8 | 479.4 | 504.8 | 478 | 469.2 | 468 | 453.5 | 453.8 | 447 | 416.2
2180 | 2053 | 525.8 | 479.4 | 504.8 | 478 | 469.2 | 468.1 | 453.5 | 453.8 | 447 | 416.2
2181 | 2054 | 525.8 | 479.4 | 504.8 | 478 | 469.2 | 468.1 | 453.6 | 453.7 | 447.1 | 416.3
2182 | 2055 | 525.8 | 479.4 | 504.7 | 478.1 | 469.3 | 468.2 | 453.6 | 453.8 | 447.1 | 416.3
2183 | 2056 | 525.8 | 479.4 | 504.8 | 478.1 | 469.3 | 468.2 | 453.6 | 453.9 | 447.1 | 416.4
2184 | 2057 | 525.7 | 479.4 | 504.8 | 478.1 | 469.3 | 468.2 | 453.7 | 454 | 447.2 | 416.4
2185 | 2058 | 525.7 | 479.4 | 504.8 | 478.1 | 469.4 | 468.3 | 453.7 | 454 | 447.2 | 416.5
2186 | 2059 | 525.8 | 479.5 | 504.8 | 478.1 | 469.5 | 468.3 | 453.7 | 454 | 447.2 | 416.5
2187 | 2060 | 525.8 | 479.5 | 504.8 | 478.1 | 469.5 | 468.3 | 453.8 | 453.9 | 447.2 | 416.6
2188 | 2061 | 525.8 | 479.5 | 504.9 | 478.1 | 469.5 | 468.4 | 453.8 | 453.9 | 447.2 | 416.7
2189 | 2062 | 525.8 | 479.5 | 504.9 | 478.2 | 469.6 | 468.4 | 453.8 | 453.9 | 447.3 | 416.8
2190 | 2063 | 525.9 | 479.5 | 504.9 | 478.2 | 469.6 | 468.5 | 453.9 | 454 | 447.3 | 416.9
2191 | 2064 | 525.9 | 479.5 | 504.9 | 478.2 | 469.6 | 468.5 | 453.9 | 454 | 447.4 | 416.9
2192 | 2065 | 525.9 | 479.5 | 504.9 | 478.2 | 469.7 | 468.5 | 453.9 | 454.1 | 447.4 | 417
2193 | 2066 | 525.9 | 479.5 | 504.9 | 478.2 | 469.7 | 468.6 | 453.9 | 454.1 | 447.4 | 417
2194 | 2067 | 525.9 | 479.5 | 504.9 | 478.2 | 469.7 | 468.6 | 454 | 454.2 | 447.4 | 417.1
2195 | 2068 | 525.9 | 479.5 | 505 | 478.3 | 469.7 | 468.7 | 454 | 454.2 | 447.4 | 417.2
2196 | 2069 | 525.9 | 479.6 | 504.9 | 478.3 | 469.8 | 468.7 | 454 | 454.2 | 447.4 | 417.3
2197 | 2070 | 525.9 | 479.6 | 504.9 | 478.3 | 469.8 | 468.8 | 454.1 | 454.2 | 447.4 | 417.4
2198 | 2071 | 525.9 | 479.6 | 505 | 478.3 | 469.8 | 468.8 | 454.1 | 454.3 | 447.5 | 417.5
2199 | 2072 | 525.9 | 479.6 | 505 | 478.3 | 469.9 | 468.8 | 454.1 | 454.4 | 447.5 | 417.6
2200 | 2073 | 525.9 | 479.6 | 505 | 478.3 | 469.9 | 468.9 | 454.2 | 454.5 | 447.5 | 417.6
2201 | 2074 | 525.9 | 479.6 | 505 | 478.4 | 470 | 468.9 | 454.2 | 454.5 | 447.6 | 417.7
2202 | 2075 | 525.9 | 479.6 | 505 | 478.4 | 469.9 | 468.9 | 454.2 | 454.5 | 447.6 | 417.8
2203 | 2076 | 525.9 | 479.6 | 505 | 478.4 | 470 | 469 | 454.3 | 454.5 | 447.6 | 417.8
2204 | 2077 | 525.9 | 479.7 | 505 | 478.4 | 470.1 | 469 | 454.3 | 454.5 | 447.6 | 417.9
2205 | 2078 | 525.9 | 479.7 | 505.1 | 478.4 | 470.1 | 469 | 454.3 | 454.6 | 447.6 | 417.9
2206 | 2079 | 525.9 | 479.7 | 505.1 | 478.4 | 470.1 | 469.1 | 454.4 | 454.5 | 447.7 | 418
2207 | 2080 | 525.9 | 479.7 | 505 | 478.4 | 470.2 | 469.1 | 454.4 | 454.5 | 447.7 | 418
2208 | 2081 | 525.9 | 479.7 | 505.1 | 478.4 | 470.2 | 469.1 | 454.4 | 454.6 | 447.7 | 418
2209 | 2082 | 525.9 | 479.7 | 505.1 | 478.5 | 470.2 | 469.2 | 454.4 | 454.6 | 447.7 | 418
2210 | 2083 | 525.9 | 479.7 | 505.1 | 478.5 | 470.3 | 469.2 | 454.5 | 454.6 | 447.7 | 418
2211 | 2084 | 525.9 | 479.8 | 505.1 | 478.5 | 470.3 | 469.3 | 454.5 | 454.6 | 447.8 | 418
2212 | 2085 | 525.9 | 479.7 | 505.1 | 478.5 | 470.3 | 469.3 | 454.5 | 454.7 | 447.8 | 418.1
2213 | 2086 | 525.9 | 479.8 | 505.1 | 478.5 | 470.4 | 469.3 | 454.6 | 454.8 | 447.8 | 418.1
2214 | 2087 | 525.9 | 479.8 | 505.1 | 478.5 | 470.4 | 469.4 | 454.6 | 454.7 | 447.8 | 418.1
2215 | 2088 | 525.8 | 479.8 | 505.1 | 478.5 | 470.5 | 469.4 | 454.6 | 454.7 | 447.9 | 418.1
2216 | 2089 | 525.8 | 479.8 | 505.2 | 478.6 | 470.5 | 469.5 | 454.7 | 454.7 | 447.9 | 418.1
2217 | 2090 | 525.8 | 479.8 | 505.1 | 478.6 | 470.5 | 469.5 | 454.7 | 454.8 | 447.9 | 418.1
2218 | 2091 | 525.8 | 479.8 | 505.2 | 478.6 | 470.6 | 469.5 | 454.7 | 454.8 | 447.9 | 418.1
2219 | 2092 | 525.8 | 479.8 | 505.2 | 478.6 | 470.6 | 469.6 | 454.8 | 454.8 | 448 | 418.2
2220 | 2093 | 525.8 | 479.9 | 505.2 | 478.6 | 470.6 | 469.6 | 454.8 | 454.8 | 448 | 418.2
2221 | 2094 | 525.8 | 479.9 | 505.2 | 478.6 | 470.7 | 469.7 | 454.8 | 454.8 | 448 | 418.2
2222 | 2095 | 525.8 | 479.9 | 505.2 | 478.7 | 470.7 | 469.7 | 454.8 | 454.8 | 448 | 418.3
2223 | 2096 | 525.8 | 479.9 | 505.2 | 478.7 | 470.7 | 469.7 | 454.9 | 454.8 | 448.1 | 418.3
2224 | 2097 | 525.8 | 479.9 | 505.1 | 478.7 | 470.8 | 469.8 | 454.9 | 454.9 | 448.1 | 418.4
2225 | 2098 | 525.7 | 479.9 | 505.1 | 478.7 | 470.9 | 469.8 | 454.9 | 454.9 | 448.1 | 418.5
2226 | 2099 | 525.8 | 479.9 | 505.2 | 478.7 | 470.9 | 469.9 | 455 | 455 | 448.2 | 418.5
2227 | 2100 | 525.8 | 479.9 | 505.2 | 478.7 | 470.9 | 469.9 | 455 | 455 | 448.2 | 418.6
2228 | 2101 | 525.8 | 480 | 505.2 | 478.7 | 471 | 469.9 | 455 | 455 | 448.2 | 418.6
2229 | 2102 | 525.8 | 480 | 505.3 | 478.7 | 471 | 470 | 455.1 | 455 | 448.3 | 418.7
2230 | 2103 | 525.8 | 480 | 505.3 | 478.7 | 471 | 470 | 455.1 | 455.2 | 448.3 | 418.7
2231 | 2104 | 525.8 | 480 | 505.2 | 478.8 | 471.1 | 470.1 | 455.1 | 455.2 | 448.3 | 418.8
2232 | 2105 | 525.8 | 480 | 505.2 | 478.8 | 471.1 | 470.1 | 455.1 | 455.2 | 448.4 | 418.9
2233 | 2106 | 525.8 | 480 | 505.3 | 478.8 | 471.1 | 470.1 | 455.2 | 455.2 | 448.4 | 418.9
2234 | 2107 | 525.8 | 480 | 505.3 | 478.8 | 471.1 | 470.2 | 455.2 | 455.1 | 448.4 | 419
2235 | 2108 | 525.8 | 480 | 505.3 | 478.8 | 471.2 | 470.2 | 455.2 | 455.2 | 448.4 | 419
2236 | 2109 | 525.8 | 480 | 505.3 | 478.8 | 471.2 | 470.2 | 455.3 | 455.2 | 448.4 | 419
2237 | 2110 | 525.7 | 480 | 505.3 | 478.8 | 471.2 | 470.3 | 455.3 | 455.2 | 448.4 | 419.1
2238 | 2111 | 525.7 | 480.1 | 505.3 | 478.9 | 471.3 | 470.3 | 455.3 | 455.3 | 448.4 | 419.1
2239 | 2112 | 525.7 | 480.1 | 505.3 | 478.9 | 471.3 | 470.3 | 455.3 | 455.3 | 448.5 | 419.1
2240 | 2113 | 525.7 | 480.1 | 505.4 | 478.9 | 471.3 | 470.4 | 455.4 | 455.3 | 448.5 | 419.2
2241 | 2114 | 525.7 | 480.1 | 505.3 | 478.9 | 471.4 | 470.4 | 455.4 | 455.3 | 448.5 | 419.2
2242 | 2115 | 525.6 | 480.1 | 505.3 | 478.9 | 471.4 | 470.5 | 455.4 | 455.3 | 448.5 | 419.2
2243 | 2116 | 525.6 | 480.1 | 505.4 | 478.9 | 471.4 | 470.5 | 455.5 | 455.3 | 448.5 | 419.2
2244 | 2117 | 525.7 | 480.1 | 505.4 | 478.9 | 471.5 | 470.5 | 455.5 | 455.3 | 448.6 | 419.2
2245 | 2118 | 525.7 | 480.2 | 505.3 | 479 | 471.5 | 470.6 | 455.5 | 455.1 | 448.6 | 419.2
2246 | 2119 | 525.7 | 480.2 | 505.4 | 479 | 471.6 | 470.6 | 455.5 | 455 | 448.6 | 419.2
2247 | 2120 | 525.7 | 480.2 | 505.4 | 479 | 471.6 | 470.6 | 455.6 | 455 | 448.6 | 419.2
2248 | 2121 | 525.7 | 480.2 | 505.4 | 479 | 471.6 | 470.7 | 455.6 | 455 | 448.7 | 419.2
2249 | 2122 | 525.7 | 480.2 | 505.4 | 479 | 471.7 | 470.7 | 455.6 | 454.9 | 448.7 | 419.3
2250 | 2123 | 525.7 | 480.2 | 505.4 | 479 | 471.7 | 470.8 | 455.7 | 455.1 | 448.7 | 419.2
2251 | 2124 | 525.7 | 480.2 | 505.5 | 479 | 471.7 | 470.8 | 455.7 | 455.3 | 448.7 | 419.2
2252 | 2125 | 525.7 | 480.2 | 505.4 | 479 | 471.8 | 470.8 | 455.7 | 455.3 | 448.7 | 419.2
2253 | 2126 | 525.7 | 480.3 | 505.4 | 479.1 | 471.8 | 470.9 | 455.7 | 455.2 | 448.7 | 419.2
2254 | 2127 | 525.7 | 480.2 | 505.5 | 479 | 471.8 | 470.9 | 455.8 | 455.1 | 448.7 | 419.2
2255 | 2128 | 525.7 | 480.3 | 505.5 | 479.1 | 471.8 | 470.9 | 455.8 | 455.1 | 448.8 | 419.3
2256 | 2129 | 525.7 | 480.3 | 505.5 | 479.1 | 471.9 | 471 | 455.8 | 455 | 448.8 | 419.3
2257 | 2130 | 525.7 | 480.3 | 505.5 | 479.1 | 471.9 | 471 | 455.9 | 455 | 448.8 | 419.3
2258 | 2131 | 525.8 | 480.3 | 505.5 | 479.1 | 471.9 | 471 | 455.9 | 455.1 | 448.8 | 419.3
2259 | 2132 | 525.7 | 480.3 | 505.5 | 479.1 | 472 | 471.1 | 455.9 | 455.1 | 448.9 | 419.4
2260 | 2133 | 525.8 | 480.3 | 505.5 | 479.1 | 472 | 471.2 | 456 | 455.1 | 448.9 | 419.4
2261 | 2134 | 525.8 | 480.3 | 505.5 | 479.1 | 472 | 471.2 | 456 | 455.2 | 448.9 | 419.4
2262 | 2135 | 525.8 | 480.3 | 505.5 | 479.1 | 472.1 | 471.2 | 456 | 455.3 | 448.9 | 419.4
2263 | 2136 | 525.8 | 480.4 | 505.5 | 479.2 | 472.1 | 471.3 | 456.1 | 455.3 | 449 | 419.5
2264 | 2137 | 525.8 | 480.3 | 505.6 | 479.2 | 472.1 | 471.3 | 456.1 | 455.4 | 449 | 419.5
2265 | 2138 | 525.8 | 480.4 | 505.6 | 479.2 | 472.2 | 471.3 | 456.1 | 455.4 | 449 | 419.5
2266 | 2139 | 525.8 | 480.4 | 505.6 | 479.2 | 472.2 | 471.4 | 456.2 | 455.4 | 449.1 | 419.5
2267 | 2140 | 525.8 | 480.4 | 505.6 | 479.2 | 472.3 | 471.4 | 456.2 | 455.3 | 449.1 | 419.5
2268 | 2141 | 525.8 | 480.4 | 505.6 | 479.2 | 472.3 | 471.5 | 456.2 | 455.3 | 449.1 | 419.5
2269 | 2142 | 525.8 | 480.4 | 505.6 | 479.2 | 472.3 | 471.5 | 456.2 | 455.3 | 449.2 | 419.5
2270 | 2143 | 525.8 | 480.4 | 505.6 | 479.2 | 472.4 | 471.5 | 456.3 | 455.4 | 449.2 | 419.5
2271 | 2144 | 525.8 | 480.4 | 505.6 | 479.2 | 472.4 | 471.6 | 456.3 | 455.5 | 449.3 | 419.5
2272 | 2145 | 525.8 | 480.4 | 505.6 | 479.2 | 472.4 | 471.6 | 456.3 | 455.6 | 449.3 | 419.5
2273 | 2146 | 525.7 | 480.5 | 505.6 | 479.3 | 472.5 | 471.7 | 456.4 | 455.6 | 449.3 | 419.5
2274 | 2147 | 525.7 | 480.5 | 505.6 | 479.3 | 472.5 | 471.7 | 456.4 | 455.6 | 449.4 | 419.5
2275 | 2148 | 525.7 | 480.4 | 505.6 | 479.3 | 472.5 | 471.7 | 456.4 | 455.7 | 449.4 | 419.5
2276 | 2149 | 525.7 | 480.5 | 505.6 | 479.3 | 472.6 | 471.8 | 456.4 | 455.7 | 449.4 | 419.5
2277 | 2150 | 525.8 | 480.5 | 505.6 | 479.3 | 472.6 | 471.8 | 456.5 | 455.8 | 449.4 | 419.5
2278 | 2151 | 525.8 | 480.5 | 505.6 | 479.3 | 472.6 | 471.8 | 456.5 | 455.9 | 449.4 | 419.5
2279 | 2152 | 525.8 | 480.5 | 505.7 | 479.3 | 472.6 | 471.9 | 456.5 | 455.9 | 449.4 | 419.5
2280 | 2153 | 525.8 | 480.5 | 505.7 | 479.3 | 472.7 | 471.9 | 456.6 | 455.9 | 449.4 | 419.5
2281 | 2154 | 525.8 | 480.5 | 505.6 | 479.4 | 472.8 | 472 | 456.6 | 456 | 449.5 | 419.5
2282 | 2155 | 525.8 | 480.5 | 505.7 | 479.3 | 472.8 | 472 | 456.6 | 456 | 449.5 | 419.5
2283 | 2156 | 525.8 | 480.6 | 505.7 | 479.4 | 472.8 | 472 | 456.7 | 456.1 | 449.5 | 419.5
2284 | 2157 | 525.8 | 480.6 | 505.7 | 479.4 | 472.9 | 472.1 | 456.7 | 456.1 | 449.5 | 419.5
2285 | 2158 | 525.8 | 480.6 | 505.7 | 479.4 | 472.9 | 472.1 | 456.7 | 456.2 | 449.5 | 419.5
2286 | 2159 | 525.8 | 480.6 | 505.7 | 479.4 | 472.9 | 472.1 | 456.7 | 456.3 | 449.5 | 419.5
2287 | 2160 | 525.8 | 480.6 | 505.7 | 479.4 | 473 | 472.2 | 456.8 | 456.3 | 449.6 | 419.5
2288 | 2161 | 525.8 | 480.6 | 505.7 | 479.4 | 473 | 472.2 | 456.8 | 456.4 | 449.6 | 419.5
2289 | 2162 | 525.8 | 480.6 | 505.7 | 479.4 | 473 | 472.2 | 456.8 | 456.4 | 449.7 | 419.5
2290 | 2163 | 525.8 | 480.6 | 505.7 | 479.4 | 473 | 472.3 | 456.9 | 456.4 | 449.7 | 419.5
2291 | 2164 | 525.8 | 480.6 | 505.7 | 479.4 | 473.1 | 472.3 | 456.9 | 456.4 | 449.7 | 419.5
2292 | 2165 | 525.8 | 480.6 | 505.7 | 479.4 | 473.1 | 472.4 | 456.9 | 456.4 | 449.7 | 419.5
2293 | 2166 | 525.8 | 480.6 | 505.8 | 479.5 | 473.1 | 472.4 | 457 | 456.4 | 449.8 | 419.5
2294 | 2167 | 525.8 | 480.7 | 505.7 | 479.5 | 473.2 | 472.5 | 457 | 456.4 | 449.8 | 419.4
2295 | 2168 | 525.8 | 480.7 | 505.7 | 479.5 | 473.2 | 472.5 | 457 | 456.4 | 449.8 | 419.4
2296 | 2169 | 525.8 | 480.7 | 505.8 | 479.5 | 473.2 | 472.5 | 457 | 456.5 | 449.8 | 419.4
2297 | 2170 | 525.8 | 480.7 | 505.8 | 479.5 | 473.3 | 472.5 | 457.1 | 456.5 | 449.9 | 419.4
2298 | 2171 | 525.8 | 480.7 | 505.8 | 479.5 | 473.3 | 472.6 | 457.1 | 456.6 | 449.9 | 419.4
2299 | 2172 | 525.8 | 480.7 | 505.8 | 479.5 | 473.3 | 472.6 | 457.1 | 456.7 | 449.9 | 419.4
2300 | 2173 | 525.8 | 480.7 | 505.8 | 479.5 | 473.3 | 472.7 | 457.2 | 456.7 | 449.9 | 419.4
2301 | 2174 | 525.9 | 480.8 | 505.8 | 479.6 | 473.4 | 472.7 | 457.2 | 456.7 | 449.9 | 419.4
2302 | 2175 | 525.9 | 480.8 | 505.8 | 479.6 | 473.4 | 472.7 | 457.2 | 456.8 | 449.8 | 419.4
2303 | 2176 | 525.9 | 480.8 | 505.9 | 479.6 | 473.4 | 472.8 | 457.2 | 456.8 | 449.8 | 419.4
2304 | 2177 | 525.9 | 480.8 | 505.9 | 479.6 | 473.5 | 472.8 | 457.3 | 456.8 | 449.8 | 419.4
2305 | 2178 | 525.9 | 480.8 | 505.9 | 479.6 | 473.6 | 472.9 | 457.3 | 456.8 | 449.8 | 419.4
2306 | 2179 | 525.9 | 480.8 | 505.9 | 479.6 | 473.6 | 472.9 | 457.3 | 456.8 | 449.9 | 419.4
2307 | 2180 | 525.9 | 480.8 | 505.9 | 479.6 | 473.6 | 472.9 | 457.4 | 456.7 | 449.9 | 419.4
2308 | 2181 | 525.9 | 480.8 | 505.9 | 479.6 | 473.6 | 473 | 457.4 | 456.8 | 449.9 | 419.4
2309 | 2182 | 525.9 | 480.9 | 505.9 | 479.6 | 473.7 | 473 | 457.4 | 456.8 | 449.9 | 419.4
2310 | 2183 | 525.9 | 480.8 | 506 | 479.6 | 473.6 | 473 | 457.5 | 456.8 | 449.9 | 419.4
2311 | 2184 | 525.9 | 480.9 | 506 | 479.6 | 473.7 | 473.1 | 457.5 | 456.7 | 449.9 | 419.4
2312 | 2185 | 525.9 | 480.9 | 505.9 | 479.7 | 473.8 | 473.1 | 457.5 | 456.7 | 449.9 | 419.4
2313 | 2186 | 525.9 | 480.9 | 506 | 479.7 | 473.8 | 473.1 | 457.5 | 456.7 | 449.9 | 419.4
2314 | 2187 | 525.9 | 480.9 | 506 | 479.7 | 473.8 | 473.2 | 457.6 | 456.8 | 450 | 419.4
2315 | 2188 | 525.9 | 480.9 | 506 | 479.7 | 473.9 | 473.2 | 457.6 | 456.8 | 450.1 | 419.4
2316 | 2189 | 525.9 | 480.9 | 506 | 479.7 | 473.9 | 473.3 | 457.6 | 456.8 | 450 | 419.4
2317 | 2190 | 525.8 | 480.9 | 506.1 | 479.7 | 473.9 | 473.3 | 457.6 | 456.9 | 450 | 419.5
2318 | 2191 | 525.8 | 480.9 | 506 | 479.7 | 473.9 | 473.3 | 457.7 | 457 | 450.1 | 419.5
2319 | 2192 | 525.8 | 481 | 506 | 479.7 | 474 | 473.4 | 457.7 | 457 | 450.1 | 419.5
2320 | 2193 | 525.8 | 481 | 506.1 | 479.7 | 474 | 473.4 | 457.7 | 457.1 | 450.2 | 419.5
2321 | 2194 | 525.8 | 481 | 506.1 | 479.7 | 474 | 473.4 | 457.8 | 457.1 | 450.3 | 419.5
2322 | 2195 | 525.7 | 481 | 506 | 479.7 | 474.1 | 473.5 | 457.8 | 457.1 | 450.3 | 419.5
2323 | 2196 | 525.7 | 481 | 506 | 479.8 | 474.1 | 473.5 | 457.8 | 457.2 | 450.3 | 419.5
2324 | 2197 | 525.7 | 481 | 506.1 | 479.7 | 474.1 | 473.5 | 457.9 | 457.2 | 450.3 | 419.5
2325 | 2198 | 525.7 | 481 | 506.1 | 479.8 | 474.1 | 473.6 | 457.9 | 457.3 | 450.2 | 419.5
2326 | 2199 | 525.7 | 481 | 506.1 | 479.8 | 474.2 | 473.6 | 457.9 | 457.4 | 450.2 | 419.6
2327 | 2200 | 525.6 | 481 | 506.1 | 479.8 | 474.2 | 473.6 | 457.9 | 457.5 | 450.3 | 419.6
2328 | 2201 | 525.6 | 481 | 506.1 | 479.8 | 474.2 | 473.7 | 458 | 457.5 | 450.2 | 419.6
2329 | 2202 | 525.6 | 481.1 | 506.1 | 479.8 | 474.3 | 473.7 | 458 | 457.6 | 450.2 | 419.6
2330 | 2203 | 525.6 | 481.1 | 506.1 | 479.8 | 474.3 | 473.8 | 458 | 457.6 | 450.3 | 419.6
2331 | 2204 | 525.5 | 481.1 | 506.2 | 479.8 | 474.3 | 473.8 | 458.1 | 457.6 | 450.3 | 419.6
2332 | 2205 | 525.5 | 481.1 | 506.1 | 479.8 | 474.4 | 473.8 | 458.1 | 457.7 | 450.4 | 419.6
2333 | 2206 | 525.4 | 481.1 | 506.1 | 479.8 | 474.5 | 473.9 | 458.1 | 457.7 | 450.4 | 419.7
2334 | 2207 | 525.4 | 481.1 | 506.2 | 479.8 | 474.5 | 473.9 | 458.2 | 457.7 | 450.4 | 419.7
2335 | 2208 | 525.4 | 481.1 | 506.2 | 479.8 | 474.5 | 474 | 458.2 | 457.7 | 450.4 | 419.7
2336 | 2209 | 525.4 | 481.2 | 506.2 | 479.9 | 474.5 | 474 | 458.2 | 457.8 | 450.4 | 419.7
2337 | 2210 | 525.4 | 481.2 | 506.2 | 479.9 | 474.6 | 474.1 | 458.3 | 457.9 | 450.4 | 419.7
2338 | 2211 | 525.3 | 481.1 | 506.2 | 479.9 | 474.6 | 474.1 | 458.3 | 457.9 | 450.5 | 419.8
2339 | 2212 | 525.3 | 481.2 | 506.2 | 479.9 | 474.6 | 474.1 | 458.3 | 457.9 | 450.5 | 419.8
2340 | 2213 | 525.3 | 481.2 | 506.2 | 479.9 | 474.7 | 474.2 | 458.4 | 457.9 | 450.5 | 419.8
2341 | 2214 | 525.3 | 481.2 | 506.2 | 479.9 | 474.7 | 474.2 | 458.4 | 457.9 | 450.5 | 419.8
2342 | 2215 | 525.3 | 481.2 | 506.2 | 479.9 | 474.7 | 474.2 | 458.4 | 458 | 450.5 | 419.8
2343 | 2216 | 525.2 | 481.2 | 506.2 | 480 | 474.8 | 474.3 | 458.4 | 458 | 450.5 | 419.9
2344 | 2217 | 525.2 | 481.2 | 506.2 | 480 | 474.8 | 474.3 | 458.5 | 458.1 | 450.6 | 419.9
2345 | 2218 | 525.2 | 481.2 | 506.2 | 479.9 | 474.8 | 474.3 | 458.5 | 458.2 | 450.7 | 419.9
2346 | 2219 | 525.2 | 481.3 | 506.2 | 480 | 474.9 | 474.4 | 458.5 | 458.2 | 450.7 | 419.9
2347 | 2220 | 525.1 | 481.3 | 506.2 | 480 | 474.9 | 474.4 | 458.5 | 458.2 | 450.6 | 419.9
2348 | 2221 | 525.1 | 481.3 | 506.2 | 480 | 474.9 | 474.5 | 458.6 | 458.2 | 450.7 | 419.9
2349 | 2222 | 525.1 | 481.3 | 506.3 | 480 | 474.9 | 474.5 | 458.6 | 458.2 | 450.7 | 420
2350 | 2223 | 525.1 | 481.3 | 506.3 | 480 | 475 | 474.5 | 458.6 | 458.3 | 450.7 | 420
2351 | 2224 | 525.1 | 481.3 | 506.3 | 480 | 475 | 474.6 | 458.7 | 458.3 | 450.8 | 420
2352 | 2225 | 525.1 | 481.3 | 506.3 | 480 | 475 | 474.6 | 458.7 | 458.3 | 450.8 | 420
2353 | 2226 | 525.1 | 481.3 | 506.2 | 480 | 475.1 | 474.6 | 458.7 | 458.4 | 450.8 | 420.1
2354 | 2227 | 525.1 | 481.3 | 506.3 | 480 | 475.1 | 474.7 | 458.8 | 458.4 | 450.8 | 420.1
2355 | 2228 | 525.1 | 481.3 | 506.3 | 480 | 475.1 | 474.7 | 458.8 | 458.5 | 450.8 | 420.1
2356 | 2229 | 525.1 | 481.3 | 506.3 | 480 | 475.1 | 474.8 | 458.8 | 458.5 | 450.9 | 420.1
2357 | 2230 | 525.1 | 481.4 | 506.3 | 480.1 | 475.2 | 474.8 | 458.9 | 458.6 | 450.9 | 420.1
2358 | 2231 | 525.1 | 481.4 | 506.3 | 480.1 | 475.3 | 474.9 | 458.9 | 458.6 | 450.9 | 420.2
2359 | 2232 | 525.1 | 481.4 | 506.4 | 480.1 | 475.3 | 474.9 | 458.9 | 458.7 | 451 | 420.2
2360 | 2233 | 525.1 | 481.4 | 506.3 | 480.1 | 475.3 | 474.9 | 459 | 458.7 | 451.1 | 420.2
2361 | 2234 | 525.1 | 481.4 | 506.3 | 480.1 | 475.4 | 475 | 459 | 458.7 | 451.2 | 420.2
2362 | 2235 | 525.1 | 481.4 | 506.3 | 480.1 | 475.4 | 475 | 459 | 458.7 | 451.1 | 420.3
2363 | 2236 | 525.1 | 481.4 | 506.4 | 480.1 | 475.4 | 475 | 459 | 458.8 | 451.2 | 420.3
2364 | 2237 | 525.1 | 481.5 | 506.3 | 480.1 | 475.5 | 475.1 | 459.1 | 458.8 | 451.1 | 420.3
2365 | 2238 | 525.1 | 481.5 | 506.4 | 480.1 | 475.5 | 475.1 | 459.1 | 458.8 | 451.1 | 420.3
2366 | 2239 | 525.1 | 481.5 | 506.4 | 480.1 | 475.5 | 475.1 | 459.1 | 458.8 | 451.2 | 420.3
2367 | 2240 | 525.1 | 481.5 | 506.4 | 480.1 | 475.5 | 475.2 | 459.1 | 458.9 | 451.2 | 420.4
2368 | 2241 | 525.1 | 481.5 | 506.3 | 480.1 | 475.6 | 475.2 | 459.2 | 458.9 | 451.2 | 420.4
2369 | 2242 | 525.1 | 481.5 | 506.4 | 480.1 | 475.6 | 475.2 | 459.2 | 458.9 | 451.3 | 420.4
2370 | 2243 | 525.2 | 481.5 | 506.4 | 480.1 | 475.6 | 475.3 | 459.2 | 458.9 | 451.3 | 420.4
2371 | 2244 | 525.2 | 481.6 | 506.4 | 480.2 | 475.7 | 475.3 | 459.3 | 459 | 451.3 | 420.4
2372 | 2245 | 525.2 | 481.6 | 506.4 | 480.2 | 475.7 | 475.4 | 459.3 | 459.1 | 451.3 | 420.5
2373 | 2246 | 525.2 | 481.5 | 506.5 | 480.2 | 475.7 | 475.4 | 459.3 | 459.1 | 451.4 | 420.5
2374 | 2247 | 525.3 | 481.6 | 506.5 | 480.2 | 475.8 | 475.4 | 459.4 | 459.1 | 451.4 | 420.5
2375 | 2248 | 525.3 | 481.6 | 506.4 | 480.2 | 475.8 | 475.5 | 459.4 | 459.1 | 451.4 | 420.5
2376 | 2249 | 525.3 | 481.6 | 506.5 | 480.2 | 475.8 | 475.5 | 459.4 | 459 | 451.4 | 420.5
2377 | 2250 | 525.3 | 481.6 | 506.5 | 480.2 | 475.8 | 475.5 | 459.5 | 459 | 451.5 | 420.6
2378 | 2251 | 525.3 | 481.6 | 506.4 | 480.2 | 475.9 | 475.6 | 459.5 | 459 | 451.5 | 420.6
2379 | 2252 | 525.4 | 481.6 | 506.5 | 480.2 | 475.9 | 475.6 | 459.5 | 459.1 | 451.5 | 420.6
2380 | 2253 | 525.3 | 481.6 | 506.5 | 480.2 | 475.9 | 475.6 | 459.5 | 459.2 | 451.5 | 420.6
2381 | 2254 | 525.3 | 481.7 | 506.5 | 480.2 | 476 | 475.7 | 459.6 | 459.2 | 451.5 | 420.7
2382 | 2255 | 525.3 | 481.7 | 506.5 | 480.2 | 476.1 | 475.8 | 459.6 | 459.3 | 451.6 | 420.7
2383 | 2256 | 525.3 | 481.7 | 506.5 | 480.2 | 476.1 | 475.8 | 459.6 | 459.3 | 451.6 | 420.7
2384 | 2257 | 525.4 | 481.7 | 506.6 | 480.3 | 476.1 | 475.8 | 459.7 | 459.4 | 451.6 | 420.7
2385 | 2258 | 525.4 | 481.7 | 506.5 | 480.3 | 476.2 | 475.9 | 459.7 | 459.4 | 451.6 | 420.7
2386 | 2259 | 525.4 | 481.7 | 506.5 | 480.3 | 476.2 | 475.9 | 459.7 | 459.4 | 451.6 | 420.8
2387 | 2260 | 525.3 | 481.7 | 506.6 | 480.3 | 476.2 | 475.9 | 459.8 | 459.3 | 451.7 | 420.8
2388 | 2261 | 525.3 | 481.7 | 506.6 | 480.3 | 476.3 | 476 | 459.8 | 459.4 | 451.7 | 420.8
2389 | 2262 | 525.3 | 481.8 | 506.5 | 480.3 | 476.3 | 476 | 459.8 | 459.4 | 451.7 | 420.8
2390 | 2263 | 525.3 | 481.8 | 506.5 | 480.3 | 476.3 | 476.1 | 459.9 | 459.3 | 451.8 | 420.9
2391 | 2264 | 525.3 | 481.8 | 506.6 | 480.3 | 476.3 | 476.1 | 459.9 | 459.4 | 451.8 | 420.9
2392 | 2265 | 525.3 | 481.8 | 506.5 | 480.3 | 476.4 | 476.2 | 459.9 | 459.4 | 451.8 | 420.9
2393 | 2266 | 525.3 | 481.8 | 506.6 | 480.3 | 476.5 | 476.2 | 460 | 459.5 | 451.8 | 420.9
2394 | 2267 | 525.3 | 481.8 | 506.6 | 480.3 | 476.4 | 476.2 | 460 | 459.6 | 451.9 | 421
2395 | 2268 | 525.3 | 481.8 | 506.6 | 480.4 | 476.5 | 476.3 | 460 | 459.7 | 451.9 | 421
2396 | 2269 | 525.3 | 481.8 | 506.6 | 480.4 | 476.6 | 476.3 | 460.1 | 459.7 | 451.9 | 421
2397 | 2270 | 525.3 | 481.8 | 506.6 | 480.4 | 476.6 | 476.3 | 460.1 | 459.7 | 452 | 421
2398 | 2271 | 525.3 | 481.8 | 506.7 | 480.4 | 476.5 | 476.4 | 460.1 | 459.7 | 452 | 421.1
2399 | 2272 | 525.3 | 481.9 | 506.6 | 480.4 | 476.7 | 476.4 | 460.2 | 459.7 | 452 | 421.1
2400 | 2273 | 525.4 | 481.9 | 506.6 | 480.4 | 476.7 | 476.5 | 460.2 | 459.8 | 452.1 | 421.1
2401 | 2274 | 525.4 | 481.9 | 506.7 | 480.4 | 476.7 | 476.5 | 460.2 | 459.9 | 452.1 | 421.1
2402 | 2275 | 525.4 | 481.9 | 506.7 | 480.4 | 476.8 | 476.6 | 460.3 | 459.9 | 452.1 | 421.2
2403 | 2276 | 525.4 | 481.9 | 506.7 | 480.4 | 476.8 | 476.6 | 460.3 | 460 | 452.1 | 421.2
2404 | 2277 | 525.4 | 481.9 | 506.7 | 480.4 | 476.8 | 476.6 | 460.3 | 460 | 452.1 | 421.2
2405 | 2278 | 525.4 | 481.9 | 506.7 | 480.4 | 476.8 | 476.7 | 460.4 | 460 | 452.1 | 421.2
2406 | 2279 | 525.4 | 482 | 506.7 | 480.5 | 476.9 | 476.7 | 460.4 | 460.1 | 452.1 | 421.3
2407 | 2280 | 525.4 | 482 | 506.7 | 480.5 | 477 | 476.8 | 460.4 | 460.1 | 452.1 | 421.3
2408 | 2281 | 525.5 | 481.9 | 506.8 | 480.5 | 476.9 | 476.8 | 460.5 | 460.2 | 452.1 | 421.3
2409 | 2282 | 525.5 | 482 | 506.8 | 480.5 | 477 | 476.9 | 460.5 | 460.2 | 452.2 | 421.3
2410 | 2283 | 525.5 | 482 | 506.8 | 480.5 | 477.1 | 476.9 | 460.6 | 460.3 | 452.2 | 421.3
2411 | 2284 | 525.5 | 482 | 506.8 | 480.5 | 477.1 | 476.9 | 460.6 | 460.3 | 452.2 | 421.4
2412 | 2285 | 525.5 | 482 | 506.8 | 480.5 | 477.1 | 477 | 460.6 | 460.4 | 452.2 | 421.4
2413 | 2286 | 525.5 | 482 | 506.8 | 480.5 | 477.2 | 477 | 460.7 | 460.4 | 452.3 | 421.4
2414 | 2287 | 525.6 | 482 | 506.8 | 480.5 | 477.2 | 477.1 | 460.7 | 460.3 | 452.3 | 421.4
2415 | 2288 | 525.6 | 482 | 506.8 | 480.5 | 477.2 | 477.1 | 460.7 | 460.4 | 452.4 | 421.5
2416 | 2289 | 525.6 | 482.1 | 506.8 | 480.6 | 477.3 | 477.1 | 460.8 | 460.4 | 452.3 | 421.5
2417 | 2290 | 525.6 | 482.1 | 506.8 | 480.6 | 477.3 | 477.2 | 460.8 | 460.5 | 452.3 | 421.5
2418 | 2291 | 525.6 | 482.1 | 506.8 | 480.6 | 477.4 | 477.2 | 460.8 | 460.6 | 452.4 | 421.5
2419 | 2292 | 525.6 | 482.1 | 506.8 | 480.6 | 477.4 | 477.3 | 460.9 | 460.6 | 452.4 | 421.6
2420 | 2293 | 525.7 | 482.1 | 506.8 | 480.6 | 477.4 | 477.3 | 460.9 | 460.7 | 452.5 | 421.6
2421 | 2294 | 525.7 | 482.1 | 506.8 | 480.6 | 477.5 | 477.3 | 460.9 | 460.6 | 452.5 | 421.6
2422 | 2295 | 525.7 | 482.1 | 506.9 | 480.6 | 477.5 | 477.4 | 461 | 460.6 | 452.5 | 421.6
2423 | 2296 | 525.7 | 482.1 | 506.9 | 480.6 | 477.5 | 477.4 | 461 | 460.6 | 452.6 | 421.6
2424 | 2297 | 525.8 | 482.1 | 506.9 | 480.7 | 477.6 | 477.5 | 461 | 460.6 | 452.6 | 421.7
2425 | 2298 | 525.8 | 482.1 | 506.9 | 480.6 | 477.6 | 477.5 | 461.1 | 460.6 | 452.7 | 421.7
2426 | 2299 | 525.8 | 482.1 | 506.9 | 480.7 | 477.6 | 477.5 | 461.1 | 460.7 | 452.7 | 421.7
2427 | 2300 | 525.8 | 482.2 | 506.9 | 480.7 | 477.7 | 477.6 | 461.1 | 460.7 | 452.7 | 421.7
2428 | 2301 | 525.7 | 482.2 | 506.9 | 480.7 | 477.8 | 477.6 | 461.2 | 460.7 | 452.7 | 421.8
2429 | 2302 | 525.7 | 482.2 | 507 | 480.7 | 477.7 | 477.6 | 461.2 | 460.7 | 452.7 | 421.8
2430 | 2303 | 525.7 | 482.2 | 506.9 | 480.7 | 477.8 | 477.7 | 461.2 | 460.8 | 452.8 | 421.8
2431 | 2304 | 525.7 | 482.2 | 506.9 | 480.7 | 477.8 | 477.7 | 461.3 | 460.9 | 452.8 | 421.8
2432 | 2305 | 525.7 | 482.2 | 507 | 480.7 | 477.9 | 477.8 | 461.3 | 461 | 452.8 | 421.8
2433 | 2306 | 525.7 | 482.2 | 507 | 480.7 | 477.9 | 477.8 | 461.3 | 461 | 452.8 | 421.9
2434 | 2307 | 525.8 | 482.3 | 507 | 480.7 | 478 | 477.8 | 461.3 | 461 | 452.9 | 421.9
2435 | 2308 | 525.8 | 482.3 | 507 | 480.7 | 478 | 477.9 | 461.4 | 461 | 452.9 | 421.9
2436 | 2309 | 525.8 | 482.3 | 507.1 | 480.7 | 478 | 477.9 | 461.4 | 461 | 452.9 | 421.9
2437 | 2310 | 525.8 | 482.3 | 507 | 480.8 | 478 | 477.9 | 461.5 | 461.1 | 453 | 421.9
2438 | 2311 | 525.8 | 482.3 | 507 | 480.8 | 478.1 | 478 | 461.5 | 461.1 | 453.1 | 422
2439 | 2312 | 525.8 | 482.3 | 507 | 480.8 | 478.1 | 478 | 461.5 | 461.1 | 453.1 | 422
2440 | 2313 | 525.8 | 482.3 | 507.1 | 480.8 | 478.1 | 478.1 | 461.6 | 461.1 | 453.2 | 422
2441 | 2314 | 525.7 | 482.3 | 507 | 480.8 | 478.3 | 478.1 | 461.6 | 461.1 | 453.2 | 422
2442 | 2315 | 525.7 | 482.3 | 507.1 | 480.8 | 478.3 | 478.2 | 461.6 | 461.1 | 453.3 | 422.1
2443 | 2316 | 525.7 | 482.3 | 507.1 | 480.8 | 478.3 | 478.2 | 461.7 | 461.1 | 453.4 | 422.1
2444 | 2317 | 525.7 | 482.4 | 507.1 | 480.8 | 478.3 | 478.2 | 461.7 | 461.2 | 453.4 | 422.1
2445 | 2318 | 525.7 | 482.4 | 507.1 | 480.9 | 478.4 | 478.3 | 461.8 | 461.2 | 453.5 | 422.1
2446 | 2319 | 525.7 | 482.4 | 507.1 | 480.9 | 478.4 | 478.3 | 461.8 | 461.2 | 453.5 | 422.2
2447 | 2320 | 525.7 | 482.4 | 507.1 | 480.9 | 478.4 | 478.3 | 461.8 | 461.2 | 453.5 | 422.2
2448 | 2321 | 525.7 | 482.4 | 507.1 | 480.9 | 478.5 | 478.4 | 461.9 | 461.3 | 453.5 | 422.2
2449 | 2322 | 525.7 | 482.4 | 507.1 | 480.9 | 478.6 | 478.5 | 461.9 | 461.4 | 453.6 | 422.2
2450 | 2323 | 525.7 | 482.4 | 507.2 | 480.9 | 478.5 | 478.5 | 461.9 | 461.4 | 453.7 | 422.2
2451 | 2324 | 525.7 | 482.4 | 507.1 | 480.9 | 478.6 | 478.5 | 462 | 461.4 | 453.6 | 422.3
2452 | 2325 | 525.7 | 482.4 | 507.1 | 480.9 | 478.7 | 478.6 | 462 | 461.5 | 453.6 | 422.3
2453 | 2326 | 525.7 | 482.4 | 507.2 | 480.9 | 478.7 | 478.6 | 462 | 461.5 | 453.6 | 422.3
2454 | 2327 | 525.7 | 482.4 | 507.2 | 480.9 | 478.7 | 478.6 | 462.1 | 461.5 | 453.6 | 422.3
2455 | 2328 | 525.7 | 482.5 | 507.1 | 481 | 478.8 | 478.7 | 462.1 | 461.6 | 453.7 | 422.4
2456 | 2329 | 525.7 | 482.5 | 507.2 | 481 | 478.9 | 478.7 | 462.1 | 461.6 | 453.7 | 422.4
2457 | 2330 | 525.7 | 482.4 | 507.2 | 481 | 478.8 | 478.7 | 462.2 | 461.6 | 453.6 | 422.4
2458 | 2331 | 525.7 | 482.5 | 507.2 | 481 | 478.9 | 478.8 | 462.2 | 461.6 | 453.7 | 422.4
2459 | 2332 | 525.7 | 482.5 | 507.2 | 481 | 479 | 478.8 | 462.2 | 461.7 | 453.8 | 422.4
2460 | 2333 | 525.8 | 482.5 | 507.2 | 481 | 479 | 478.9 | 462.3 | 461.7 | 453.7 | 422.5
2461 | 2334 | 525.7 | 482.5 | 507.2 | 481 | 479 | 478.9 | 462.3 | 461.7 | 453.8 | 422.5
2462 | 2335 | 525.7 | 482.5 | 507.2 | 481 | 479 | 478.9 | 462.3 | 461.7 | 453.8 | 422.5
2463 | 2336 | 525.7 | 482.5 | 507.2 | 481 | 479.1 | 479 | 462.4 | 461.7 | 453.8 | 422.5
2464 | 2337 | 525.7 | 482.5 | 507.3 | 481 | 479.1 | 479 | 462.4 | 461.8 | 453.8 | 422.5
2465 | 2338 | 525.7 | 482.5 | 507.3 | 481 | 479.2 | 479 | 462.5 | 461.8 | 453.9 | 422.5
2466 | 2339 | 525.7 | 482.6 | 507.3 | 481.1 | 479.2 | 479.1 | 462.5 | 461.8 | 453.9 | 422.6
2467 | 2340 | 525.7 | 482.6 | 507.3 | 481.1 | 479.3 | 479.1 | 462.5 | 461.9 | 453.9 | 422.6
2468 | 2341 | 525.6 | 482.6 | 507.3 | 481.1 | 479.3 | 479.2 | 462.6 | 461.9 | 454 | 422.6
2469 | 2342 | 525.7 | 482.6 | 507.3 | 481.1 | 479.4 | 479.2 | 462.6 | 461.9 | 454 | 422.6
2470 | 2343 | 525.7 | 482.6 | 507.3 | 481.1 | 479.4 | 479.3 | 462.6 | 461.9 | 454 | 422.6
2471 | 2344 | 525.6 | 482.6 | 507.3 | 481.1 | 479.4 | 479.3 | 462.7 | 462 | 454 | 422.7
2472 | 2345 | 525.6 | 482.6 | 507.3 | 481.1 | 479.5 | 479.3 | 462.7 | 462 | 454.1 | 422.6
2473 | 2346 | 525.6 | 482.6 | 507.3 | 481.1 | 479.5 | 479.4 | 462.8 | 462 | 454.1 | 422.7
2474 | 2347 | 525.6 | 482.6 | 507.3 | 481.1 | 479.5 | 479.4 | 462.8 | 462.1 | 454.1 | 422.7
2475 | 2348 | 525.6 | 482.6 | 507.3 | 481.1 | 479.6 | 479.4 | 462.8 | 462.1 | 454.1 | 422.7
2476 | 2349 | 525.6 | 482.6 | 507.3 | 481.2 | 479.7 | 479.5 | 462.9 | 462.1 | 454.1 | 422.7
2477 | 2350 | 525.5 | 482.7 | 507.3 | 481.2 | 479.7 | 479.5 | 462.9 | 462 | 454.2 | 422.7
2478 | 2351 | 525.5 | 482.6 | 507.4 | 481.2 | 479.7 | 479.5 | 462.9 | 462.1 | 454.2 | 422.7
2479 | 2352 | 525.5 | 482.7 | 507.4 | 481.2 | 479.7 | 479.6 | 463 | 462.3 | 454.3 | 422.7
2480 | 2353 | 525.5 | 482.7 | 507.4 | 481.2 | 479.8 | 479.6 | 463 | 462.4 | 454.3 | 422.7
2481 | 2354 | 525.5 | 482.7 | 507.4 | 481.2 | 479.8 | 479.6 | 463 | 462.4 | 454.3 | 422.8
2482 | 2355 | 525.5 | 482.7 | 507.5 | 481.2 | 479.8 | 479.7 | 463.1 | 462.4 | 454.3 | 422.8
2483 | 2356 | 525.5 | 482.7 | 507.4 | 481.2 | 479.9 | 479.7 | 463.1 | 462.5 | 454.4 | 422.8
2484 | 2357 | 525.5 | 482.7 | 507.4 | 481.2 | 479.9 | 479.8 | 463.1 | 462.5 | 454.4 | 422.8
2485 | 2358 | 525.5 | 482.7 | 507.5 | 481.2 | 479.9 | 479.8 | 463.2 | 462.6 | 454.4 | 422.8
2486 | 2359 | 525.5 | 482.7 | 507.4 | 481.3 | 480 | 479.8 | 463.2 | 462.5 | 454.4 | 422.8
2487 | 2360 | 525.5 | 482.8 | 507.4 | 481.3 | 480.1 | 479.9 | 463.3 | 462.6 | 454.4 | 422.9
2488 | 2361 | 525.5 | 482.8 | 507.4 | 481.3 | 480.1 | 479.9 | 463.3 | 462.7 | 454.4 | 422.9
2489 | 2362 | 525.6 | 482.7 | 507.5 | 481.3 | 480.1 | 479.9 | 463.3 | 462.7 | 454.5 | 422.9
2490 | 2363 | 525.5 | 482.8 | 507.5 | 481.3 | 480.2 | 480 | 463.4 | 462.7 | 454.5 | 422.9
2491 | 2364 | 525.5 | 482.8 | 507.5 | 481.3 | 480.2 | 480 | 463.4 | 462.8 | 454.5 | 422.9
2492.1 | 2365.1 | 525.5 | 482.8 | 507.5 | 481.3 | 480.2 | 480 | 463.4 | 462.8 | 454.6 | 422.9
2493.1 | 2366.1 | 525.5 | 482.8 | 507.5 | 481.3 | 480.2 | 480.1 | 463.5 | 462.9 | 454.6 | 422.9
2494.1 | 2367.1 | 525.5 | 482.8 | 507.5 | 481.3 | 480.3 | 480.1 | 463.5 | 463 | 454.6 | 423
2495.1 | 2368.1 | 525.4 | 482.8 | 507.5 | 481.3 | 480.3 | 480.2 | 463.5 | 463.1 | 454.6 | 423
2496.1 | 2369.1 | 525.4 | 482.8 | 507.6 | 481.3 | 480.3 | 480.2 | 463.6 | 463.1 | 454.6 | 423
2497.1 | 2370.1 | 525.4 | 482.8 | 507.5 | 481.4 | 480.4 | 480.2 | 463.6 | 463.2 | 454.7 | 423
2498.1 | 2371.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.5 | 480.3 | 463.6 | 463.3 | 454.8 | 423
2499.1 | 2372.1 | 525.3 | 482.8 | 507.5 | 481.3 | 480.5 | 480.3 | 463.7 | 463.2 | 454.7 | 423
2500.1 | 2373.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.5 | 480.3 | 463.7 | 463.2 | 454.7 | 423
2501.1 | 2374.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.6 | 480.4 | 463.7 | 463.2 | 454.8 | 423
2502.1 | 2375.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.6 | 480.4 | 463.8 | 463.3 | 454.8 | 423.1
2503.1 | 2376.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.6 | 480.4 | 463.8 | 463.3 | 454.8 | 423.1
2504.1 | 2377.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.7 | 480.5 | 463.8 | 463.3 | 454.9 | 423.1
2505.1 | 2378.1 | 525.3 | 482.9 | 507.5 | 481.4 | 480.7 | 480.5 | 463.9 | 463.3 | 454.9 | 423.1
2506.1 | 2379.1 | 525.3 | 482.9 | 507.6 | 481.4 | 480.7 | 480.5 | 463.9 | 463.4 | 454.9 | 423.1
2507.1 | 2380.1 | 525.4 | 482.9 | 507.5 | 481.4 | 480.8 | 480.6 | 464 | 463.4 | 454.9 | 423.1
2508.1 | 2381.1 | 525.4 | 483 | 507.5 | 481.4 | 480.8 | 480.6 | 464 | 463.4 | 454.9 | 423.1
2509.1 | 2382.1 | 525.4 | 483 | 507.6 | 481.4 | 480.8 | 480.6 | 464 | 463.4 | 455 | 423.2
2510.1 | 2383.1 | 525.4 | 483 | 507.6 | 481.4 | 480.8 | 480.6 | 464.1 | 463.4 | 455 | 423.2
2511.1 | 2384.1 | 525.4 | 483 | 507.6 | 481.4 | 480.9 | 480.7 | 464.1 | 463.5 | 455 | 423.2
2512.1 | 2385.1 | 525.4 | 483 | 507.6 | 481.4 | 480.9 | 480.7 | 464.1 | 463.6 | 455 | 423.2
2513.1 | 2386.1 | 525.4 | 483 | 507.7 | 481.4 | 480.9 | 480.7 | 464.2 | 463.5 | 455 | 423.2
2514.1 | 2387.1 | 525.4 | 483 | 507.6 | 481.5 | 481 | 480.8 | 464.2 | 463.6 | 455.1 | 423.2
2515.1 | 2388.1 | 525.4 | 483 | 507.6 | 481.5 | 481.1 | 480.8 | 464.3 | 463.7 | 455.1 | 423.3
2516.1 | 2389.1 | 525.4 | 483 | 507.7 | 481.5 | 481.1 | 480.9 | 464.3 | 463.7 | 455.1 | 423.3
2517.1 | 2390.1 | 525.4 | 483 | 507.7 | 481.5 | 481.1 | 480.9 | 464.3 | 463.7 | 455.1 | 423.3
2518.1 | 2391.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.2 | 480.9 | 464.4 | 463.8 | 455.1 | 423.3
2519.1 | 2392.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.2 | 481 | 464.4 | 463.8 | 455.2 | 423.3
2520.1 | 2393.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.2 | 481 | 464.5 | 463.8 | 455.2 | 423.3
2521.1 | 2394.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.3 | 481.1 | 464.5 | 463.8 | 455.2 | 423.3
2522.1 | 2395.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.3 | 481.1 | 464.6 | 463.8 | 455.2 | 423.4
2523.1 | 2396.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.3 | 481.1 | 464.6 | 463.9 | 455.2 | 423.4
2524.1 | 2397.1 | 525.4 | 483.1 | 507.8 | 481.5 | 481.3 | 481.2 | 464.6 | 464 | 455.3 | 423.4
2525.1 | 2398.1 | 525.4 | 483.1 | 507.7 | 481.5 | 481.4 | 481.2 | 464.7 | 464.1 | 455.3 | 423.4
2526.1 | 2399.1 | 525.4 | 483.1 | 507.7 | 481.6 | 481.5 | 481.3 | 464.7 | 464.1 | 455.4 | 423.4
2527.1 | 2400.1 | 525.4 | 483.1 | 507.8 | 481.5 | 481.5 | 481.3 | 464.8 | 464.1 | 455.3 | 423.5
2528.1 | 2401.1 | 525.4 | 483.1 | 507.8 | 481.6 | 481.5 | 481.3 | 464.8 | 464.1 | 455.4 | 423.5
2529.1 | 2402.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.6 | 481.4 | 464.8 | 464.1 | 455.4 | 423.5
2530.1 | 2403.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.6 | 481.4 | 464.9 | 464.1 | 455.4 | 423.5
2531.1 | 2404.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.6 | 481.4 | 464.9 | 464 | 455.4 | 423.5
2532.1 | 2405.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.7 | 481.5 | 464.9 | 464.1 | 455.4 | 423.6
2533.1 | 2406.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.8 | 481.5 | 465 | 464.1 | 455.5 | 423.6
2534.1 | 2407.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.8 | 481.5 | 465 | 464.1 | 455.5 | 423.6
2535.1 | 2408.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.8 | 481.6 | 465.1 | 464.1 | 455.5 | 423.6
2536.1 | 2409.1 | 525.4 | 483.2 | 507.8 | 481.6 | 481.9 | 481.6 | 465.1 | 464.2 | 455.5 | 423.6
2537.1 | 2410.1 | 525.4 | 483.3 | 507.8 | 481.6 | 481.9 | 481.6 | 465.1 | 464.2 | 455.5 | 423.6
2538.1 | 2411.1 | 525.4 | 483.2 | 507.9 | 481.6 | 481.8 | 481.6 | 465.1 | 464.2 | 455.5 | 423.7
2539.1 | 2412.1 | 525.4 | 483.3 | 507.8 | 481.7 | 482 | 481.7 | 465.2 | 464.2 | 455.5 | 423.7
2540.1 | 2413.1 | 525.5 | 483.3 | 507.8 | 481.7 | 482 | 481.7 | 465.2 | 464.2 | 455.5 | 423.7
2541.1 | 2414.1 | 525.5 | 483.3 | 507.9 | 481.6 | 482 | 481.7 | 465.3 | 464.2 | 455.6 | 423.7
2542.1 | 2415.1 | 525.5 | 483.3 | 507.9 | 481.7 | 482 | 481.8 | 465.3 | 464.2 | 455.6 | 423.7
2543.1 | 2416.1 | 525.6 | 483.3 | 507.9 | 481.7 | 482.1 | 481.8 | 465.3 | 464.2 | 455.6 | 423.8
2544.1 | 2417.1 | 525.6 | 483.3 | 507.9 | 481.7 | 482.1 | 481.8 | 465.4 | 464.3 | 455.6 | 423.8
2545.1 | 2418.1 | 525.7 | 483.3 | 507.9 | 481.7 | 482.1 | 481.9 | 465.4 | 464.3 | 455.6 | 423.8
2546.1 | 2419.1 | 525.8 | 483.4 | 507.9 | 481.7 | 482.2 | 481.9 | 465.5 | 464.3 | 455.7 | 423.8
2547.1 | 2420.1 | 525.8 | 483.4 | 507.9 | 481.7 | 482.2 | 482 | 465.5 | 464.3 | 455.7 | 423.8
2548.1 | 2421.1 | 525.9 | 483.4 | 508 | 481.7 | 482.2 | 482 | 465.5 | 464.3 | 455.7 | 423.8
2549.1 | 2422.1 | 525.9 | 483.4 | 507.9 | 481.7 | 482.3 | 482 | 465.6 | 464.2 | 455.7 | 423.9
2550.1 | 2423.1 | 526 | 483.4 | 507.9 | 481.7 | 482.4 | 482.1 | 465.6 | 464.2 | 455.8 | 423.9
2551.1 | 2424.1 | 526 | 483.4 | 508 | 481.7 | 482.4 | 482.1 | 465.7 | 464.2 | 455.8 | 423.9
2552.1 | 2425.1 | 526 | 483.4 | 508 | 481.7 | 482.4 | 482.1 | 465.7 | 464.3 | 455.8 | 423.9
2553.1 | 2426.1 | 526.1 | 483.4 | 508 | 481.8 | 482.5 | 482.2 | 465.8 | 464.4 | 455.8 | 424
2554.1 | 2427.1 | 526.1 | 483.4 | 508 | 481.8 | 482.5 | 482.3 | 465.8 | 464.4 | 455.8 | 424
2555.1 | 2428.1 | 526.1 | 483.4 | 508 | 481.8 | 482.5 | 482.3 | 465.9 | 464.5 | 455.9 | 424
2556.1 | 2429.1 | 526 | 483.4 | 508 | 481.8 | 482.6 | 482.3 | 465.9 | 464.5 | 455.9 | 424
2557.1 | 2430.1 | 526 | 483.5 | 508 | 481.8 | 482.6 | 482.4 | 466 | 464.6 | 455.9 | 424
2558.1 | 2431.1 | 526 | 483.5 | 508 | 481.8 | 482.7 | 482.4 | 466 | 464.7 | 455.9 | 424
2559.1 | 2432.1 | 526 | 483.4 | 508.1 | 481.8 | 482.6 | 482.4 | 466.1 | 464.8 | 455.9 | 424
2560.1 | 2433.1 | 526 | 483.5 | 508.1 | 481.8 | 482.7 | 482.5 | 466.1 | 464.7 | 456 | 424
2561.1 | 2434.1 | 526 | 483.5 | 508.1 | 481.8 | 482.8 | 482.5 | 466.1 | 464.8 | 456 | 424.1
2562.1 | 2435.1 | 526 | 483.5 | 508.1 | 481.8 | 482.8 | 482.5 | 466.2 | 464.8 | 456 | 424.1
2563.1 | 2436.1 | 525.9 | 483.5 | 508.1 | 481.9 | 482.8 | 482.6 | 466.2 | 464.8 | 456 | 424.1
2564.1 | 2437.1 | 525.9 | 483.5 | 508.1 | 481.9 | 482.9 | 482.6 | 466.3 | 464.8 | 456.1 | 424.1
2565.1 | 2438.1 | 525.9 | 483.5 | 508.1 | 481.9 | 482.9 | 482.6 | 466.3 | 464.8 | 456.1 | 424.2
2566.1 | 2439.1 | 525.9 | 483.5 | 508.2 | 481.9 | 482.9 | 482.7 | 466.3 | 464.8 | 456.1 | 424.2
2567.1 | 2440.1 | 525.9 | 483.6 | 508.1 | 481.9 | 483 | 482.7 | 466.4 | 464.9 | 456 | 424.2
2568.1 | 2441.1 | 525.9 | 483.6 | 508.1 | 481.9 | 483 | 482.8 | 466.4 | 465 | 456.2 | 424.2
2569.1 | 2442.1 | 525.9 | 483.5 | 508.1 | 481.9 | 483 | 482.8 | 466.5 | 465.1 | 456.2 | 424.2
2570.1 | 2443.1 | 525.9 | 483.6 | 508.1 | 481.9 | 483.1 | 482.8 | 466.5 | 465.1 | 456.2 | 424.2
2571.1 | 2444.1 | 525.9 | 483.6 | 508.1 | 481.9 | 483.1 | 482.9 | 466.5 | 465.2 | 456.2 | 424.2
2572.1 | 2445.1 | 525.9 | 483.6 | 508.2 | 481.9 | 483.1 | 482.9 | 466.6 | 465.2 | 456.2 | 424.3
2573.1 | 2446.1 | 525.8 | 483.6 | 508.2 | 481.9 | 483.1 | 482.9 | 466.6 | 465.3 | 456.3 | 424.3
2574.1 | 2447.1 | 525.8 | 483.6 | 508.2 | 482 | 483.2 | 483 | 466.6 | 465.4 | 456.3 | 424.3
2575.1 | 2448.1 | 525.8 | 483.6 | 508.2 | 482 | 483.3 | 483 | 466.7 | 465.4 | 456.3 | 424.3
2576.1 | 2449.1 | 525.8 | 483.6 | 508.2 | 482 | 483.3 | 483 | 466.7 | 465.4 | 456.3 | 424.3
2577.1 | 2450.1 | 525.7 | 483.6 | 508.2 | 482 | 483.3 | 483 | 466.8 | 465.5 | 456.3 | 424.3
2578.1 | 2451.1 | 525.7 | 483.7 | 508.2 | 482 | 483.4 | 483.1 | 466.8 | 465.5 | 456.4 | 424.4
2579.1 | 2452.1 | 525.7 | 483.7 | 508.2 | 482 | 483.4 | 483.1 | 466.8 | 465.4 | 456.4 | 424.4
2580.1 | 2453.1 | 525.7 | 483.7 | 508.2 | 482 | 483.4 | 483.1 | 466.9 | 465.5 | 456.4 | 424.4
2581.1 | 2454.1 | 525.7 | 483.7 | 508.2 | 482 | 483.5 | 483.2 | 466.9 | 465.6 | 456.4 | 424.4
2582.1 | 2455.1 | 525.7 | 483.7 | 508.2 | 482 | 483.5 | 483.2 | 467 | 465.6 | 456.4 | 424.4
2583.1 | 2456.1 | 525.6 | 483.7 | 508.2 | 482 | 483.5 | 483.3 | 467 | 465.6 | 456.4 | 424.4
2584.1 | 2457.1 | 525.6 | 483.7 | 508.2 | 482 | 483.6 | 483.3 | 467.1 | 465.5 | 456.4 | 424.4
2585.1 | 2458.1 | 525.6 | 483.7 | 508.2 | 482 | 483.6 | 483.3 | 467.1 | 465.6 | 456.4 | 424.5
2586.1 | 2459.1 | 525.6 | 483.7 | 508.2 | 482 | 483.7 | 483.4 | 467.1 | 465.6 | 456.5 | 424.5
2587.1 | 2460.1 | 525.7 | 483.7 | 508.3 | 482.1 | 483.7 | 483.4 | 467.2 | 465.7 | 456.5 | 424.5
2588.1 | 2461.1 | 525.7 | 483.7 | 508.2 | 482.1 | 483.7 | 483.4 | 467.2 | 465.8 | 456.5 | 424.5
2589.1 | 2462.1 | 525.7 | 483.8 | 508.3 | 482.1 | 483.8 | 483.5 | 467.3 | 465.8 | 456.5 | 424.5
2590.1 | 2463.1 | 525.7 | 483.7 | 508.3 | 482.1 | 483.8 | 483.5 | 467.3 | 465.9 | 456.6 | 424.6
2591.1 | 2464.1 | 525.8 | 483.8 | 508.3 | 482.1 | 483.8 | 483.5 | 467.3 | 466 | 456.6 | 424.6
2592.1 | 2465.1 | 525.8 | 483.8 | 508.3 | 482.1 | 483.9 | 483.6 | 467.4 | 466 | 456.6 | 424.6
2593.1 | 2466.1 | 525.8 | 483.8 | 508.3 | 482.1 | 483.9 | 483.6 | 467.4 | 466 | 456.6 | 424.6
2594.1 | 2467.1 | 525.8 | 483.8 | 508.3 | 482.1 | 483.9 | 483.6 | 467.5 | 466 | 456.7 | 424.6
2595.1 | 2468.1 | 525.8 | 483.8 | 508.3 | 482.1 | 484 | 483.7 | 467.5 | 466 | 456.7 | 424.6
2596.1 | 2469.1 | 525.8 | 483.8 | 508.3 | 482.1 | 484 | 483.7 | 467.5 | 466.2 | 456.7 | 424.7
2597.1 | 2470.1 | 525.8 | 483.8 | 508.4 | 482.1 | 484 | 483.7 | 467.6 | 466.2 | 456.7 | 424.7
2598.1 | 2471.1 | 525.8 | 483.8 | 508.4 | 482.1 | 484.1 | 483.8 | 467.6 | 466.2 | 456.7 | 424.7
2599.1 | 2472.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.1 | 483.8 | 467.7 | 466.3 | 456.8 | 424.7
2600.1 | 2473.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.2 | 483.8 | 467.7 | 466.3 | 456.8 | 424.8
2601.1 | 2474.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.1 | 483.9 | 467.8 | 466.3 | 456.8 | 424.8
2602.1 | 2475.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.2 | 483.9 | 467.8 | 466.5 | 456.8 | 424.8
2603.1 | 2476.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.3 | 483.9 | 467.8 | 466.5 | 456.8 | 424.8
2604.1 | 2477.1 | 525.8 | 483.9 | 508.5 | 482.2 | 484.2 | 484 | 467.9 | 466.5 | 456.9 | 424.8
2605.1 | 2478.1 | 525.8 | 483.9 | 508.5 | 482.2 | 484.3 | 484 | 467.9 | 466.6 | 456.9 | 424.9
2606.1 | 2479.1 | 525.8 | 483.9 | 508.4 | 482.2 | 484.4 | 484 | 468 | 466.6 | 456.9 | 424.9
2607.1 | 2480.1 | 525.8 | 483.9 | 508.5 | 482.2 | 484.4 | 484.1 | 468 | 466.6 | 457 | 424.9
2608.1 | 2481.1 | 525.8 | 483.9 | 508.5 | 482.2 | 484.4 | 484.1 | 468.1 | 466.6 | 457 | 424.9
2609.1 | 2482.1 | 525.8 | 483.9 | 508.5 | 482.2 | 484.5 | 484.1 | 468.1 | 466.6 | 457 | 425
2610.1 | 2483.1 | 525.7 | 484 | 508.5 | 482.2 | 484.5 | 484.2 | 468.1 | 466.6 | 457.1 | 425
2611.1 | 2484.1 | 525.7 | 484 | 508.5 | 482.2 | 484.5 | 484.2 | 468.2 | 466.6 | 457 | 425
2612.1 | 2485.1 | 525.7 | 484 | 508.5 | 482.2 | 484.6 | 484.2 | 468.2 | 466.7 | 457.1 | 425
2613.1 | 2486.1 | 525.7 | 484 | 508.5 | 482.3 | 484.6 | 484.3 | 468.3 | 466.7 | 457.1 | 425
2614.1 | 2487.1 | 525.7 | 484 | 508.5 | 482.3 | 484.6 | 484.3 | 468.3 | 466.7 | 457.1 | 425
2615.1 | 2488.1 | 525.7 | 484 | 508.6 | 482.3 | 484.6 | 484.3 | 468.4 | 466.8 | 457.2 | 425.1
2616.1 | 2489.1 | 525.7 | 484 | 508.5 | 482.3 | 484.7 | 484.4 | 468.4 | 466.8 | 457.2 | 425.1
2617.1 | 2490.1 | 525.7 | 484 | 508.5 | 482.3 | 484.8 | 484.4 | 468.5 | 466.9 | 457.2 | 425.1
2618.1 | 2491.1 | 525.7 | 484 | 508.6 | 482.3 | 484.8 | 484.4 | 468.5 | 466.9 | 457.1 | 425.1
2619.1 | 2492.1 | 525.7 | 484 | 508.6 | 482.3 | 484.8 | 484.5 | 468.5 | 466.9 | 457.2 | 425.1
2620.1 | 2493.1 | 525.7 | 484.1 | 508.5 | 482.3 | 484.9 | 484.5 | 468.6 | 466.9 | 457.2 | 425.1
2621.1 | 2494.1 | 525.7 | 484.1 | 508.6 | 482.3 | 484.9 | 484.6 | 468.6 | 467 | 457.2 | 425.2
2622.1 | 2495.1 | 525.7 | 484.1 | 508.6 | 482.3 | 484.9 | 484.6 | 468.7 | 467.1 | 457.3 | 425.2
2623.1 | 2496.1 | 525.7 | 484.1 | 508.5 | 482.3 | 485 | 484.6 | 468.7 | 467.2 | 457.3 | 425.2
2624.1 | 2497.1 | 525.7 | 484.1 | 508.6 | 482.4 | 485 | 484.7 | 468.7 | 467.2 | 457.3 | 425.2
2625.1 | 2498.1 | 525.7 | 484.1 | 508.6 | 482.3 | 485 | 484.7 | 468.8 | 467.2 | 457.4 | 425.2
2626.1 | 2499.1 | 525.8 | 484.1 | 508.6 | 482.4 | 485 | 484.7 | 468.8 | 467.1 | 457.3 | 425.2
2627.1 | 2500.1 | 525.7 | 484.1 | 508.6 | 482.4 | 485.1 | 484.7 | 468.8 | 467.2 | 457.4 | 425.3
2628.1 | 2501.1 | 525.8 | 484.1 | 508.6 | 482.4 | 485.1 | 484.8 | 468.9 | 467.2 | 457.4 | 425.3
2629.1 | 2502.1 | 525.8 | 484.1 | 508.6 | 482.4 | 485.1 | 484.8 | 468.9 | 467.3 | 457.4 | 425.3
2630.1 | 2503.1 | 525.8 | 484.1 | 508.6 | 482.4 | 485.2 | 484.8 | 469 | 467.3 | 457.5 | 425.3
2631.1 | 2504.1 | 525.8 | 484.2 | 508.6 | 482.4 | 485.3 | 484.9 | 469 | 467.2 | 457.5 | 425.3
2632.1 | 2505.1 | 525.8 | 484.1 | 508.7 | 482.4 | 485.2 | 484.9 | 469.1 | 467.2 | 457.6 | 425.3
2633.1 | 2506.1 | 525.8 | 484.2 | 508.6 | 482.4 | 485.3 | 484.9 | 469.1 | 467.1 | 457.6 | 425.4
2634.1 | 2507.1 | 525.8 | 484.2 | 508.7 | 482.4 | 485.4 | 485 | 469.2 | 467.1 | 457.6 | 425.4
2635.1 | 2508.1 | 525.9 | 484.2 | 508.7 | 482.4 | 485.4 | 485 | 469.2 | 467.2 | 457.6 | 425.4
2636.1 | 2509.1 | 525.9 | 484.2 | 508.7 | 482.4 | 485.4 | 485 | 469.3 | 467.2 | 457.7 | 425.4
2637.1 | 2510.1 | 525.9 | 484.2 | 508.6 | 482.5 | 485.5 | 485.1 | 469.3 | 467.3 | 457.7 | 425.4
2638.1 | 2511.1 | 525.9 | 484.2 | 508.6 | 482.5 | 485.5 | 485.1 | 469.3 | 467.3 | 457.7 | 425.4
2639.1 | 2512.1 | 525.9 | 484.2 | 508.7 | 482.5 | 485.5 | 485.2 | 469.4 | 467.3 | 457.8 | 425.5
2640.1 | 2513.1 | 525.9 | 484.2 | 508.7 | 482.5 | 485.6 | 485.2 | 469.4 | 467.4 | 457.8 | 425.5
2641.1 | 2514.1 | 525.9 | 484.2 | 508.7 | 482.5 | 485.6 | 485.2 | 469.5 | 467.4 | 457.8 | 425.5
2642.1 | 2515.1 | 525.9 | 484.2 | 508.7 | 482.5 | 485.6 | 485.3 | 469.5 | 467.5 | 457.8 | 425.5
2643.1 | 2516.1 | 525.9 | 484.2 | 508.7 | 482.5 | 485.6 | 485.3 | 469.6 | 467.5 | 457.9 | 425.5
2644.1 | 2517.1 | 525.9 | 484.3 | 508.7 | 482.5 | 485.7 | 485.3 | 469.6 | 467.4 | 457.9 | 425.5
2645.1 | 2518.1 | 525.9 | 484.3 | 508.7 | 482.5 | 485.8 | 485.4 | 469.6 | 467.4 | 457.9 | 425.6
2646.1 | 2519.1 | 525.9 | 484.3 | 508.8 | 482.5 | 485.7 | 485.4 | 469.7 | 467.5 | 457.9 | 425.6
2647.1 | 2520.1 | 526 | 484.3 | 508.7 | 482.5 | 485.8 | 485.4 | 469.7 | 467.5 | 458 | 425.6
2648.1 | 2521.1 | 526 | 484.3 | 508.7 | 482.5 | 485.8 | 485.4 | 469.8 | 467.5 | 458 | 425.6
2649.1 | 2522.1 | 526 | 484.3 | 508.8 | 482.5 | 485.8 | 485.5 | 469.8 | 467.5 | 458.1 | 425.6
2650.1 | 2523.1 | 526 | 484.3 | 508.8 | 482.5 | 485.8 | 485.5 | 469.8 | 467.6 | 458 | 425.6
2651.1 | 2524.1 | 526 | 484.4 | 508.8 | 482.6 | 485.9 | 485.5 | 469.9 | 467.6 | 458 | 425.6
2652.1 | 2525.1 | 526 | 484.4 | 508.7 | 482.6 | 486 | 485.6 | 469.9 | 467.7 | 458.1 | 425.6
2653.1 | 2526.1 | 526 | 484.3 | 508.8 | 482.6 | 486 | 485.6 | 470 | 467.8 | 458.1 | 425.7
2654.1 | 2527.1 | 526.1 | 484.3 | 508.8 | 482.6 | 486 | 485.6 | 470 | 467.8 | 458.1 | 425.7
2655.1 | 2528.1 | 526.1 | 484.4 | 508.8 | 482.6 | 486.1 | 485.7 | 470.1 | 467.9 | 458.1 | 425.7
2656.1 | 2529.1 | 526.1 | 484.4 | 508.8 | 482.6 | 486.1 | 485.7 | 470.1 | 467.9 | 458.2 | 425.7
2657.1 | 2530.1 | 526.1 | 484.4 | 508.9 | 482.6 | 486.1 | 485.7 | 470.1 | 467.8 | 458.2 | 425.7
2658.1 | 2531.1 | 526.1 | 484.4 | 508.8 | 482.6 | 486.2 | 485.8 | 470.2 | 467.9 | 458.3 | 425.8
2659.1 | 2532.1 | 526.1 | 484.4 | 508.8 | 482.6 | 486.2 | 485.8 | 470.2 | 467.9 | 458.3 | 425.8
2660.1 | 2533.1 | 526.1 | 484.6 | 508.5 | 482.8 | 486.6 | 486 | 470.2 | 467.9 | 458.2 | 425.8
2661.1 | 2534.1 | 526.1 | 484.7 | 508.3 | 482.9 | 486.9 | 486.1 | 470.2 | 468 | 458.3 | 425.8
2662.1 | 2535.1 | 526.1 | 484.7 | 508.3 | 482.9 | 487 | 486.1 | 470.3 | 468 | 458.3 | 425.8
2663.1 | 2536.1 | 526.1 | 484.7 | 508.3 | 482.9 | 487 | 486.1 | 470.3 | 468 | 458.3 | 425.8
2664.1 | 2537.1 | 526.1 | 484.7 | 508.4 | 482.9 | 487 | 486.2 | 470.4 | 468 | 458.4 | 425.8
2665.1 | 2538.1 | 526 | 484.7 | 508.3 | 482.9 | 487.1 | 486.2 | 470.4 | 468.1 | 458.4 | 425.8
2666.1 | 2539.1 | 526 | 484.8 | 508.3 | 482.9 | 487.2 | 486.3 | 470.5 | 468.1 | 458.4 | 425.9
2667.1 | 2540.1 | 526 | 484.7 | 508.4 | 482.9 | 487.1 | 486.3 | 470.5 | 468.1 | 458.5 | 425.9
2668.1 | 2541.1 | 525.9 | 484.8 | 508.4 | 482.9 | 487.2 | 486.3 | 470.6 | 468.1 | 458.5 | 425.9
2669.1 | 2542.1 | 525.9 | 484.8 | 508.3 | 483 | 487.3 | 486.4 | 470.6 | 468.1 | 458.5 | 425.9
2670.1 | 2543.1 | 525.9 | 484.8 | 508.3 | 483 | 487.3 | 486.4 | 470.6 | 468.1 | 458.5 | 425.9
2671.1 | 2544.1 | 525.9 | 484.8 | 508.4 | 482.9 | 487.2 | 486.4 | 470.7 | 468.3 | 458.6 | 425.9
2672.1 | 2545.1 | 525.8 | 484.8 | 508.3 | 483 | 487.4 | 486.5 | 470.7 | 468.3 | 458.6 | 426
2673.1 | 2546.1 | 525.8 | 484.8 | 508.3 | 483 | 487.4 | 486.5 | 470.8 | 468.4 | 458.6 | 426
2674.1 | 2547.1 | 525.7 | 484.8 | 508.4 | 482.9 | 487.3 | 486.5 | 470.8 | 468.5 | 458.7 | 426
2675.1 | 2548.1 | 525.7 | 484.8 | 508.4 | 483 | 487.4 | 486.5 | 470.9 | 468.6 | 458.7 | 426
2676.1 | 2549.1 | 525.7 | 484.9 | 508.3 | 483 | 487.5 | 486.6 | 470.9 | 468.7 | 458.7 | 426
2677.1 | 2550.1 | 525.7 | 484.8 | 508.4 | 483 | 487.5 | 486.6 | 470.9 | 468.7 | 458.7 | 426.1
2678.1 | 2551.1 | 525.7 | 484.8 | 508.4 | 483 | 487.5 | 486.6 | 471 | 468.8 | 458.8 | 426.1
2679.1 | 2552.1 | 525.6 | 484.9 | 508.4 | 483 | 487.6 | 486.7 | 471 | 468.8 | 458.8 | 426.1
2680.1 | 2553.1 | 525.6 | 484.9 | 508.4 | 483 | 487.6 | 486.7 | 471 | 468.9 | 458.8 | 426.1
2681.1 | 2554.1 | 525.5 | 484.9 | 508.4 | 483 | 487.6 | 486.7 | 471.1 | 468.8 | 458.9 | 426.1
2682.1 | 2555.1 | 525.5 | 484.9 | 508.4 | 483 | 487.6 | 486.7 | 471.1 | 468.9 | 458.9 | 426.1
2683.1 | 2556.1 | 525.5 | 484.9 | 508.4 | 483 | 487.7 | 486.8 | 471.2 | 468.9 | 458.9 | 426.2
2684.1 | 2557.1 | 525.5 | 484.9 | 508.4 | 483 | 487.7 | 486.8 | 471.2 | 468.8 | 459 | 426.2
2685.1 | 2558.1 | 525.5 | 484.9 | 508.5 | 483 | 487.6 | 486.8 | 471.2 | 468.9 | 459 | 426.2
2686.1 | 2559.1 | 525.5 | 484.9 | 508.4 | 483 | 487.7 | 486.9 | 471.3 | 469 | 459 | 426.2
2687.1 | 2560.1 | 525.5 | 485 | 508.4 | 483 | 487.8 | 486.9 | 471.3 | 469 | 459 | 426.2
2688.1 | 2561.1 | 525.5 | 484.9 | 508.5 | 483 | 487.7 | 486.9 | 471.4 | 469.2 | 459.1 | 426.2
2689.1 | 2562.1 | 525.5 | 484.9 | 508.5 | 483 | 487.8 | 486.9 | 471.4 | 469.2 | 459.1 | 426.3
2690.1 | 2563.1 | 525.5 | 485 | 508.5 | 483 | 487.8 | 487 | 471.4 | 469.3 | 459.1 | 426.3
2691.1 | 2564.1 | 525.5 | 485 | 508.5 | 483 | 487.9 | 487 | 471.5 | 469.3 | 459.1 | 426.3
2692.1 | 2565.1 | 525.5 | 484.9 | 508.6 | 483 | 487.8 | 487 | 471.5 | 469.4 | 459.2 | 426.3
2693.1 | 2566.1 | 525.5 | 485 | 508.4 | 483.1 | 488 | 487.1 | 471.6 | 469.4 | 459.2 | 426.3
2694.1 | 2567.1 | 525.5 | 485 | 508.5 | 483.1 | 488 | 487.1 | 471.6 | 469.5 | 459.2 | 426.4
2695.1 | 2568.1 | 525.5 | 485 | 508.5 | 483.1 | 488 | 487.1 | 471.7 | 469.5 | 459.3 | 426.4
2696.1 | 2569.1 | 525.4 | 485 | 508.5 | 483.1 | 488.1 | 487.2 | 471.7 | 469.5 | 459.2 | 426.4
2697.1 | 2570.1 | 525.4 | 485 | 508.5 | 483.1 | 488.1 | 487.2 | 471.8 | 469.6 | 459.3 | 426.4
2698.1 | 2571.1 | 525.5 | 485 | 508.5 | 483.1 | 488.2 | 487.2 | 471.8 | 469.6 | 459.4 | 426.5
2699.1 | 2572.1 | 525.4 | 485 | 508.5 | 483.1 | 488.1 | 487.3 | 471.9 | 469.7 | 459.4 | 426.5
2700.1 | 2573.1 | 525.4 | 485.1 | 508.5 | 483.1 | 488.2 | 487.3 | 471.9 | 469.7 | 459.4 | 426.5
2701.1 | 2574.1 | 525.4 | 485.1 | 508.5 | 483.1 | 488.2 | 487.3 | 471.9 | 469.8 | 459.4 | 426.5
2702.1 | 2575.1 | 525.4 | 485 | 508.6 | 483.1 | 488.2 | 487.3 | 472 | 469.8 | 459.4 | 426.5
2703.1 | 2576.1 | 525.4 | 485 | 508.6 | 483.1 | 488.2 | 487.4 | 472 | 469.8 | 459.5 | 426.5
2704.1 | 2577.1 | 525.5 | 485.1 | 508.5 | 483.1 | 488.3 | 487.4 | 472 | 469.9 | 459.5 | 426.6
2705.1 | 2578.1 | 525.5 | 485.1 | 508.6 | 483.1 | 488.3 | 487.4 | 472.1 | 470 | 459.5 | 426.6
2706.1 | 2579.1 | 525.5 | 485.1 | 508.6 | 483.1 | 488.2 | 487.4 | 472.1 | 470 | 459.6 | 426.6
2707.1 | 2580.1 | 525.5 | 485.1 | 508.6 | 483.1 | 488.4 | 487.5 | 472.1 | 469.9 | 459.6 | 426.6
2708.1 | 2581.1 | 525.5 | 485.1 | 508.6 | 483.1 | 488.4 | 487.5 | 472.2 | 470 | 459.6 | 426.6
2709.1 | 2582.1 | 525.6 | 485.1 | 508.6 | 483.1 | 488.4 | 487.5 | 472.2 | 470 | 459.7 | 426.7
2710.1 | 2583.1 | 525.6 | 485.1 | 508.6 | 483.1 | 488.4 | 487.6 | 472.3 | 470 | 459.6 | 426.7
2711.1 | 2584.1 | 525.6 | 485.2 | 508.6 | 483.2 | 488.5 | 487.6 | 472.3 | 470.1 | 459.7 | 426.7
2712.1 | 2585.1 | 525.6 | 485.1 | 508.6 | 483.2 | 488.5 | 487.6 | 472.4 | 470.1 | 459.7 | 426.7
2713.1 | 2586.1 | 525.6 | 485.1 | 508.7 | 483.1 | 488.5 | 487.7 | 472.4 | 470.2 | 459.7 | 426.7
2714.1 | 2587.1 | 525.6 | 485.2 | 508.6 | 483.2 | 488.6 | 487.7 | 472.5 | 470.2 | 459.8 | 426.7
2715.1 | 2588.1 | 525.6 | 485.2 | 508.6 | 483.2 | 488.7 | 487.8 | 472.5 | 470.3 | 459.8 | 426.8
2716.1 | 2589.1 | 525.7 | 485.2 | 508.7 | 483.2 | 488.6 | 487.8 | 472.6 | 470.4 | 459.9 | 426.8
2717.1 | 2590.1 | 525.7 | 485.2 | 508.6 | 483.2 | 488.7 | 487.8 | 472.6 | 470.5 | 459.9 | 426.8
2718.1 | 2591.1 | 525.7 | 485.2 | 508.6 | 483.2 | 488.8 | 487.9 | 472.7 | 470.5 | 459.9 | 426.8
2719.1 | 2592.1 | 525.7 | 485.2 | 508.6 | 483.2 | 488.8 | 487.9 | 472.7 | 470.5 | 459.9 | 426.8
2720.1 | 2593.1 | 525.7 | 485.2 | 508.7 | 483.2 | 488.8 | 487.9 | 472.8 | 470.5 | 460 | 426.8
2721.1 | 2594.1 | 525.7 | 485.2 | 508.7 | 483.2 | 488.9 | 488 | 472.8 | 470.5 | 460 | 426.9
2722.1 | 2595.1 | 525.7 | 485.2 | 508.7 | 483.2 | 488.9 | 488 | 472.9 | 470.6 | 460 | 426.9
2723.1 | 2596.1 | 525.7 | 485.2 | 508.7 | 483.2 | 488.9 | 488 | 472.9 | 470.7 | 460.1 | 426.9
2724.1 | 2597.1 | 525.7 | 485.2 | 508.7 | 483.2 | 489 | 488.1 | 473 | 470.6 | 460.1 | 426.9
2725.1 | 2598.1 | 525.7 | 485.3 | 508.7 | 483.3 | 489.1 | 488.1 | 473 | 470.7 | 460.1 | 426.9
2726.1 | 2599.1 | 525.7 | 485.3 | 508.7 | 483.3 | 489.1 | 488.2 | 473.1 | 470.6 | 460.1 | 426.9
2727.1 | 2600.1 | 525.7 | 485.2 | 508.7 | 483.3 | 489.1 | 488.2 | 473.1 | 470.7 | 460.2 | 427
2728.1 | 2601.1 | 525.7 | 485.3 | 508.7 | 483.3 | 489.2 | 488.2 | 473.2 | 470.6 | 460.2 | 427
2729.1 | 2602.1 | 525.7 | 485.3 | 508.7 | 483.3 | 489.2 | 488.3 | 473.2 | 470.6 | 460.2 | 427
2730.1 | 2603.1 | 525.7 | 485.3 | 508.8 | 483.3 | 489.2 | 488.3 | 473.3 | 470.7 | 460.2 | 427
2731.1 | 2604.1 | 525.7 | 485.3 | 508.7 | 483.3 | 489.2 | 488.3 | 473.3 | 470.8 | 460.3 | 427
2732.1 | 2605.1 | 525.8 | 485.3 | 508.7 | 483.3 | 489.3 | 488.4 | 473.3 | 470.7 | 460.3 | 427
2733.1 | 2606.1 | 525.8 | 485.3 | 508.8 | 483.3 | 489.3 | 488.4 | 473.4 | 470.8 | 460.3 | 427.1
2734.1 | 2607.1 | 525.8 | 485.3 | 508.8 | 483.3 | 489.3 | 488.4 | 473.4 | 470.8 | 460.3 | 427.1
2735.1 | 2608.1 | 525.8 | 485.3 | 508.7 | 483.4 | 489.4 | 488.5 | 473.5 | 470.8 | 460.3 | 427.1
2736.1 | 2609.1 | 525.8 | 485.3 | 508.7 | 483.4 | 489.4 | 488.5 | 473.5 | 470.9 | 460.3 | 427.1
2737.1 | 2610.1 | 525.9 | 485.3 | 508.8 | 483.4 | 489.4 | 488.5 | 473.6 | 470.9 | 460.4 | 427.1
2738.1 | 2611.1 | 525.9 | 485.3 | 508.8 | 483.4 | 489.4 | 488.5 | 473.6 | 470.9 | 460.4 | 427.2
2739.1 | 2612.1 | 525.9 | 485.4 | 508.7 | 483.4 | 489.5 | 488.6 | 473.6 | 471 | 460.4 | 427.2
2740.1 | 2613.1 | 525.9 | 485.4 | 508.8 | 483.4 | 489.5 | 488.6 | 473.7 | 471 | 460.5 | 427.2
2741.1 | 2614.1 | 525.9 | 485.3 | 508.8 | 483.4 | 489.5 | 488.6 | 473.7 | 471 | 460.4 | 427.2
2742.1 | 2615.1 | 525.9 | 485.4 | 508.8 | 483.4 | 489.6 | 488.7 | 473.8 | 471.1 | 460.5 | 427.2
2743.1 | 2616.1 | 525.9 | 485.4 | 508.8 | 483.4 | 489.6 | 488.7 | 473.8 | 471.1 | 460.5 | 427.2
2744.1 | 2617.1 | 525.9 | 485.4 | 508.8 | 483.4 | 489.6 | 488.7 | 473.8 | 471.1 | 460.5 | 427.3
2745.1 | 2618.1 | 526 | 485.4 | 508.8 | 483.4 | 489.6 | 488.7 | 473.9 | 471.2 | 460.6 | 427.3
2746.1 | 2619.1 | 525.9 | 485.4 | 508.8 | 483.5 | 489.7 | 488.8 | 473.9 | 471.3 | 460.6 | 427.3
2747.1 | 2620.1 | 525.9 | 485.4 | 508.8 | 483.4 | 489.7 | 488.8 | 474 | 471.3 | 460.6 | 427.3
2748.1 | 2621.1 | 526 | 485.4 | 508.9 | 483.4 | 489.7 | 488.8 | 474 | 471.3 | 460.7 | 427.3
2749.1 | 2622.1 | 526 | 485.5 | 508.8 | 483.5 | 489.8 | 488.9 | 474 | 471.3 | 460.7 | 427.3
2750.1 | 2623.1 | 526 | 485.5 | 508.8 | 483.5 | 489.8 | 488.9 | 474.1 | 471.3 | 460.6 | 427.3
2751.1 | 2624.1 | 525.9 | 485.4 | 508.9 | 483.5 | 489.8 | 488.9 | 474.1 | 471.4 | 460.8 | 427.4
2752.1 | 2625.1 | 525.9 | 485.4 | 508.8 | 483.5 | 489.9 | 489 | 474.2 | 471.4 | 460.7 | 427.4
2753.1 | 2626.1 | 525.9 | 485.5 | 508.8 | 483.5 | 489.9 | 489 | 474.2 | 471.4 | 460.7 | 427.4
2754.1 | 2627.1 | 525.9 | 485.5 | 508.8 | 483.5 | 489.9 | 489 | 474.3 | 471.5 | 460.8 | 427.4
2755.1 | 2628.1 | 525.9 | 485.5 | 508.9 | 483.5 | 489.9 | 489 | 474.3 | 471.5 | 460.7 | 427.4
2756.1 | 2629.1 | 525.9 | 485.5 | 508.9 | 483.5 | 490 | 489.1 | 474.4 | 471.6 | 460.8 | 427.4
2757.1 | 2630.1 | 525.8 | 485.5 | 508.9 | 483.5 | 490.1 | 489.1 | 474.4 | 471.7 | 460.9 | 427.5
2758.1 | 2631.1 | 525.9 | 485.5 | 508.9 | 483.5 | 490 | 489.1 | 474.5 | 471.7 | 460.9 | 427.5
2759.1 | 2632.1 | 525.9 | 485.5 | 508.9 | 483.5 | 490.1 | 489.2 | 474.5 | 471.7 | 460.9 | 427.5
2760.1 | 2633.1 | 525.9 | 485.5 | 508.9 | 483.5 | 490.1 | 489.2 | 474.5 | 471.7 | 461 | 427.5
2761.1 | 2634.1 | 525.9 | 485.5 | 508.9 | 483.5 | 490.1 | 489.2 | 474.6 | 471.8 | 461 | 427.5
2762.1 | 2635.1 | 525.9 | 485.5 | 509 | 483.5 | 490.1 | 489.2 | 474.6 | 471.8 | 461 | 427.6
2763.1 | 2636.1 | 525.9 | 485.5 | 508.9 | 483.6 | 490.2 | 489.3 | 474.7 | 471.9 | 461 | 427.6
2764.1 | 2637.1 | 525.8 | 485.5 | 508.9 | 483.6 | 490.2 | 489.3 | 474.7 | 471.9 | 461 | 427.6
2765.1 | 2638.1 | 525.8 | 485.5 | 509 | 483.6 | 490.2 | 489.3 | 474.8 | 471.9 | 461.1 | 427.6
2766.1 | 2639.1 | 525.8 | 485.5 | 509 | 483.6 | 490.3 | 489.4 | 474.8 | 471.9 | 461.1 | 427.6
2767.1 | 2640.1 | 525.8 | 485.6 | 508.9 | 483.6 | 490.3 | 489.4 | 474.8 | 471.9 | 461.1 | 427.6
2768.1 | 2641.1 | 525.8 | 485.6 | 508.9 | 483.6 | 490.3 | 489.4 | 474.9 | 472 | 461.2 | 427.7
2769.1 | 2642.1 | 525.8 | 485.5 | 509 | 483.6 | 490.3 | 489.5 | 474.9 | 472.1 | 461.2 | 427.7
2770.1 | 2643.1 | 525.8 | 485.6 | 509 | 483.6 | 490.3 | 489.5 | 475 | 472.1 | 461.2 | 427.7
2771.1 | 2644.1 | 525.7 | 485.6 | 509 | 483.6 | 490.4 | 489.5 | 475 | 472.2 | 461.2 | 427.7
2772.1 | 2645.1 | 525.7 | 485.6 | 509 | 483.6 | 490.4 | 489.6 | 475.1 | 472.2 | 461.3 | 427.7
2773.1 | 2646.1 | 525.7 | 485.5 | 509.2 | 483.5 | 490.1 | 489.5 | 475.1 | 472.2 | 461.3 | 427.8
2774.1 | 2647.1 | 525.7 | 485.4 | 509.4 | 483.5 | 490 | 489.4 | 475.2 | 472.3 | 461.3 | 427.8
2775.1 | 2648.1 | 525.7 | 485.3 | 509.6 | 483.4 | 489.9 | 489.4 | 475.2 | 472.3 | 461.3 | 427.8
2776.1 | 2649.1 | 525.5 | 485.3 | 509.7 | 483.4 | 489.8 | 489.4 | 475.3 | 472.5 | 461.4 | 427.8
2777.1 | 2650.1 | 525.3 | 485.3 | 509.6 | 483.4 | 489.9 | 489.5 | 475.3 | 472.4 | 461.4 | 427.8
2778.1 | 2651.1 | 525 | 485.3 | 509.6 | 483.4 | 490 | 489.5 | 475.4 | 472.6 | 461.3 | 427.9
2779.1 | 2652.1 | 524.6 | 485.3 | 509.6 | 483.4 | 489.9 | 489.5 | 475.4 | 472.6 | 461.5 | 427.9
2780.1 | 2653.1 | 524.1 | 485.3 | 509.6 | 483.4 | 490 | 489.5 | 475.4 | 472.6 | 461.4 | 427.9
2781.1 | 2654.1 | 523.6 | 485.3 | 509.5 | 483.4 | 490 | 489.6 | 475.5 | 472.5 | 461.4 | 427.9
2782.1 | 2655.1 | 523.1 | 485.3 | 509.4 | 483.4 | 490 | 489.6 | 475.5 | 472.6 | 461.5 | 427.9
2783.1 | 2656.1 | 522.5 | 485.2 | 509.5 | 483.3 | 490 | 489.6 | 475.6 | 472.6 | 461.4 | 428
2784.1 | 2657.1 | 521.9 | 485.2 | 509.4 | 483.3 | 490.1 | 489.7 | 475.6 | 472.7 | 461.6 | 428
2785.1 | 2658.1 | 521.2 | 485.2 | 509.3 | 483.3 | 490.1 | 489.7 | 475.6 | 472.8 | 461.5 | 428
2786.1 | 2659.1 | 520.5 | 485.2 | 509.3 | 483.3 | 490.1 | 489.7 | 475.7 | 472.7 | 461.6 | 428
2787.1 | 2660.1 | 519.8 | 485.1 | 509.2 | 483.2 | 490.1 | 489.7 | 475.7 | 472.6 | 461.6 | 428
2788.1 | 2661.1 | 519.1 | 485.1 | 509.1 | 483.2 | 490.2 | 489.8 | 475.8 | 472.6 | 461.6 | 428
2789.1 | 2662.1 | 518.4 | 485.1 | 509.1 | 483.2 | 490.2 | 489.8 | 475.8 | 472.7 | 461.6 | 428.1
2790.1 | 2663.1 | 517.6 | 485 | 509 | 483.1 | 490.2 | 489.8 | 475.9 | 472.7 | 461.7 | 428.1
2791.1 | 2664.1 | 516.9 | 485 | 508.9 | 483.1 | 490.3 | 489.9 | 475.9 | 472.7 | 461.6 | 428.1
2792.1 | 2665.1 | 516.2 | 485 | 508.8 | 483.1 | 490.4 | 489.9 | 476 | 472.9 | 461.6 | 428.1
2793.1 | 2666.1 | 515.4 | 485 | 508.8 | 483 | 490.3 | 489.9 | 476 | 473 | 461.8 | 428.1
2794.1 | 2667.1 | 514.6 | 484.9 | 508.7 | 483 | 490.4 | 489.9 | 476.1 | 473 | 461.7 | 428.1
2795.1 | 2668.1 | 513.9 | 484.9 | 508.6 | 483 | 490.4 | 490 | 476.1 | 473.1 | 461.7 | 428.2
2796.1 | 2669.1 | 513.1 | 484.8 | 508.5 | 482.9 | 490.4 | 490 | 476.1 | 473 | 461.8 | 428.2
2797.1 | 2670.1 | 512.4 | 484.8 | 508.4 | 482.9 | 490.4 | 490 | 476.2 | 473.1 | 461.8 | 428.2
2798.1 | 2671.1 | 511.6 | 484.7 | 508.3 | 482.8 | 490.5 | 490 | 476.2 | 473.1 | 461.8 | 428.2
2799.1 | 2672.1 | 510.8 | 484.7 | 508.2 | 482.8 | 490.5 | 490.1 | 476.3 | 473.2 | 461.8 | 428.2
2800.1 | 2673.1 | 510 | 484.6 | 508.2 | 482.7 | 490.5 | 490.1 | 476.3 | 473.2 | 461.9 | 428.2
2801.1 | 2674.1 | 509.2 | 484.5 | 508.1 | 482.6 | 490.5 | 490.1 | 476.4 | 473.3 | 461.9 | 428.3
2802.1 | 2675.1 | 508.4 | 484.5 | 507.9 | 482.6 | 490.6 | 490.1 | 476.4 | 473.4 | 461.9 | 428.3
2803.1 | 2676.1 | 507.6 | 484.4 | 507.8 | 482.5 | 490.6 | 490.1 | 476.4 | 473.5 | 461.9 | 428.3
2804.1 | 2677.1 | 506.8 | 484.3 | 507.7 | 482.5 | 490.5 | 490.1 | 476.5 | 473.5 | 461.9 | 428.3
2805.1 | 2678.1 | 506 | 484.3 | 507.6 | 482.4 | 490.6 | 490.2 | 476.5 | 473.5 | 461.9 | 428.3
2806.1 | 2679.1 | 505.2 | 484.2 | 507.5 | 482.3 | 490.6 | 490.2 | 476.6 | 473.5 | 461.9 | 428.3
2807.1 | 2680.1 | 504.5 | 484.1 | 507.4 | 482.3 | 490.6 | 490.2 | 476.6 | 473.6 | 461.9 | 428.3
2808.1 | 2681.1 | 503.7 | 484.1 | 507.3 | 482.2 | 490.6 | 490.2 | 476.7 | 473.7 | 461.9 | 428.4
2809.1 | 2682.1 | 502.9 | 484 | 507.1 | 482.1 | 490.7 | 490.2 | 476.7 | 473.7 | 461.9 | 428.4
2810.1 | 2683.1 | 502.1 | 483.9 | 507 | 482.1 | 490.7 | 490.2 | 476.7 | 473.7 | 462 | 428.4
2811.1 | 2684.1 | 501.3 | 483.8 | 507 | 482 | 490.6 | 490.2 | 476.8 | 473.7 | 462 | 428.4
2812.1 | 2685.1 | 500.5 | 483.8 | 506.8 | 481.9 | 490.7 | 490.2 | 476.8 | 473.7 | 462 | 428.4
2813.1 | 2686.1 | 499.9 | 483.7 | 506.6 | 481.8 | 490.7 | 490.3 | 476.9 | 473.8 | 462 | 428.4
2814.1 | 2687.1 | 499.1 | 483.6 | 506.5 | 481.7 | 490.7 | 490.2 | 476.9 | 473.8 | 462 | 428.4
2815.1 | 2688.1 | 498.3 | 483.5 | 506.4 | 481.6 | 490.7 | 490.3 | 476.9 | 473.9 | 462 | 428.4
2816.1 | 2689.1 | 497.5 | 483.5 | 506.2 | 481.6 | 490.7 | 490.3 | 477 | 473.9 | 461.9 | 428.5
2817.1 | 2690.1 | 496.7 | 483.3 | 506.1 | 481.5 | 490.7 | 490.3 | 477 | 473.8 | 462 | 428.5
2818.1 | 2691.1 | 495.9 | 483.2 | 506 | 481.4 | 490.7 | 490.2 | 477.1 | 473.9 | 462 | 428.5
2819.1 | 2692.1 | 495.1 | 483.2 | 505.8 | 481.3 | 490.7 | 490.3 | 477.1 | 474 | 461.9 | 428.5
2820.1 | 2693.1 | 494.4 | 483.1 | 505.6 | 481.2 | 490.8 | 490.3 | 477.1 | 474 | 461.9 | 428.5
2821.1 | 2694.1 | 493.6 | 483 | 505.5 | 481.1 | 490.7 | 490.2 | 477.2 | 474.1 | 462 | 428.5
2822.1 | 2695.1 | 492.8 | 482.9 | 505.3 | 481 | 490.7 | 490.2 | 477.2 | 474.1 | 461.9 | 428.5
2823.1 | 2696.1 | 492 | 482.8 | 505.2 | 480.9 | 490.8 | 490.3 | 477.2 | 474.1 | 461.9 | 428.6
2824.1 | 2697.1 | 491.2 | 482.7 | 505 | 480.8 | 490.7 | 490.2 | 477.3 | 474.2 | 461.9 | 428.6
2825.1 | 2698.1 | 490.4 | 482.5 | 504.9 | 480.7 | 490.7 | 490.2 | 477.3 | 474.3 | 461.8 | 428.6
2826.1 | 2699.1 | 489.6 | 482.5 | 504.7 | 480.6 | 490.7 | 490.2 | 477.3 | 474.3 | 461.9 | 428.6
2827.1 | 2700.1 | 488.9 | 482.3 | 504.6 | 480.5 | 490.7 | 490.2 | 477.4 | 474.3 | 461.9 | 428.6
2828.1 | 2701.1 | 488.1 | 482.2 | 504.4 | 480.4 | 490.7 | 490.2 | 477.4 | 474.3 | 461.9 | 428.6
2829.1 | 2702.1 | 487.4 | 482.1 | 504.2 | 480.3 | 490.7 | 490.2 | 477.4 | 474.3 | 461.9 | 428.6
2830.1 | 2703.1 | 486.7 | 482 | 504 | 480.2 | 490.7 | 490.2 | 477.5 | 474.4 | 461.9 | 428.7
2831.1 | 2704.1 | 485.9 | 481.9 | 503.9 | 480 | 490.7 | 490.2 | 477.5 | 474.4 | 461.9 | 428.7
2832.1 | 2705.1 | 485.2 | 481.8 | 503.8 | 479.9 | 490.6 | 490.1 | 477.5 | 474.4 | 461.9 | 428.7
2833.1 | 2706.1 | 484.4 | 481.7 | 503.5 | 479.8 | 490.6 | 490.1 | 477.5 | 474.3 | 461.9 | 428.7
2834.1 | 2707.1 | 483.7 | 481.6 | 503.3 | 479.7 | 490.6 | 490.1 | 477.6 | 474.4 | 461.8 | 428.7
2835.1 | 2708.1 | 482.9 | 481.4 | 503.2 | 479.5 | 490.6 | 490.1 | 477.6 | 474.4 | 461.9 | 428.7
2836.1 | 2709.1 | 482.2 | 481.3 | 503 | 479.4 | 490.6 | 490.1 | 477.6 | 474.3 | 461.7 | 428.7
2837.1 | 2710.1 | 481.5 | 481.2 | 502.8 | 479.3 | 490.6 | 490.1 | 477.7 | 474.4 | 461.7 | 428.8
2838.1 | 2711.1 | 480.7 | 481.1 | 502.6 | 479.2 | 490.6 | 490 | 477.7 | 474.4 | 461.7 | 428.8
2839.1 | 2712.1 | 480 | 480.9 | 502.5 | 479 | 490.5 | 490 | 477.7 | 474.4 | 461.6 | 428.8
2840.1 | 2713.1 | 479.2 | 480.8 | 502.3 | 478.9 | 490.5 | 490 | 477.8 | 474.4 | 461.7 | 428.8
2841.1 | 2714.1 | 478.5 | 480.7 | 502.1 | 478.8 | 490.5 | 490 | 477.8 | 474.5 | 461.7 | 428.8
2842.1 | 2715.1 | 477.8 | 480.5 | 501.9 | 478.6 | 490.4 | 489.9 | 477.8 | 474.5 | 461.7 | 428.8
2843.1 | 2716.1 | 477 | 480.4 | 501.7 | 478.5 | 490.4 | 489.9 | 477.9 | 474.5 | 461.6 | 428.8
2844.1 | 2717.1 | 476.3 | 480.3 | 501.5 | 478.4 | 490.5 | 489.9 | 477.9 | 474.6 | 461.6 | 428.8
2845.1 | 2718.1 | 475.5 | 480.1 | 501.3 | 478.2 | 490.4 | 489.8 | 477.9 | 474.6 | 461.6 | 428.8
2846.1 | 2719.1 | 474.8 | 480 | 501.2 | 478.1 | 490.3 | 489.8 | 478 | 474.6 | 461.6 | 428.8
2847.1 | 2720.1 | 474.1 | 479.9 | 500.9 | 478 | 490.4 | 489.8 | 478 | 474.7 | 461.5 | 428.8
2848.1 | 2721.1 | 473.4 | 479.7 | 500.7 | 477.8 | 490.4 | 489.8 | 478 | 474.7 | 461.5 | 428.8
2849.1 | 2722.1 | 472.7 | 479.5 | 500.6 | 477.7 | 490.3 | 489.7 | 478 | 474.7 | 461.5 | 428.8
2850.1 | 2723.1 | 471.9 | 479.4 | 500.4 | 477.5 | 490.3 | 489.7 | 478.1 | 474.8 | 461.4 | 428.8
2851.1 | 2724.1 | 471.2 | 479.3 | 500.1 | 477.4 | 490.3 | 489.7 | 478.1 | 474.7 | 461.4 | 428.9
2852.1 | 2725.1 | 470.5 | 479.1 | 500.1 | 477.2 | 490.2 | 489.6 | 478.1 | 474.6 | 461.4 | 428.9
2853.1 | 2726.1 | 469.8 | 479 | 499.9 | 477.1 | 490.1 | 489.6 | 478.1 | 474.6 | 461.3 | 428.9
2854.1 | 2727.1 | 469.1 | 478.8 | 499.6 | 476.9 | 490.2 | 489.6 | 478.2 | 474.7 | 461.3 | 428.9
2855.1 | 2728.1 | 468.4 | 478.7 | 499.4 | 476.8 | 490.2 | 489.5 | 478.2 | 474.8 | 461.3 | 428.9
2856.1 | 2729.1 | 467.7 | 478.5 | 499.3 | 476.6 | 490 | 489.4 | 478.2 | 474.9 | 461.2 | 428.9
2857.1 | 2730.1 | 467.1 | 478.3 | 499.1 | 476.5 | 490 | 489.4 | 478.2 | 474.9 | 461.2 | 428.9
2858.1 | 2731.1 | 466.4 | 478.2 | 498.8 | 476.3 | 490 | 489.4 | 478.2 | 475 | 461.2 | 428.9
2859.1 | 2732.1 | 465.7 | 478 | 498.6 | 476.2 | 490 | 489.3 | 478.3 | 475.1 | 461.2 | 428.9
2860.1 | 2733.1 | 465 | 477.9 | 498.5 | 476 | 489.9 | 489.3 | 478.3 | 475.1 | 461.1 | 428.9
2861.1 | 2734.1 | 464.3 | 477.7 | 498.2 | 475.9 | 489.9 | 489.3 | 478.3 | 475.1 | 461.1 | 428.9
2862.1 | 2735.1 | 463.6 | 477.6 | 497.9 | 475.7 | 489.9 | 489.2 | 478.3 | 475.1 | 461 | 428.9
2863.1 | 2736.1 | 462.9 | 477.4 | 497.8 | 475.5 | 489.8 | 489.1 | 478.3 | 475.2 | 460.9 | 428.9
2864.1 | 2737.1 | 462.3 | 477.2 | 497.6 | 475.4 | 489.8 | 489.1 | 478.3 | 475.2 | 461 | 428.9
2865.1 | 2738.1 | 461.6 | 477.1 | 497.3 | 475.2 | 489.8 | 489.1 | 478.3 | 475.2 | 460.9 | 428.9
2866.1 | 2739.1 | 460.9 | 476.9 | 497.1 | 475.1 | 489.7 | 489 | 478.4 | 475.2 | 460.8 | 428.9
2867.1 | 2740.1 | 460.2 | 476.7 | 496.9 | 474.9 | 489.6 | 488.9 | 478.4 | 475.2 | 460.9 | 429
2868.1 | 2741.1 | 459.5 | 476.6 | 496.7 | 474.8 | 489.6 | 488.9 | 478.4 | 475.2 | 460.7 | 428.9
2869.1 | 2742.1 | 458.9 | 476.4 | 496.4 | 474.6 | 489.6 | 488.9 | 478.4 | 475.2 | 460.6 | 428.9
2870.1 | 2743.1 | 458.2 | 476.2 | 496.2 | 474.4 | 489.5 | 488.8 | 478.4 | 475.2 | 460.6 | 429
2871.1 | 2744.1 | 457.5 | 476.1 | 496 | 474.2 | 489.4 | 488.7 | 478.4 | 475.2 | 460.5 | 429
2872.1 | 2745.1 | 456.8 | 475.9 | 495.8 | 474.1 | 489.4 | 488.7 | 478.4 | 475.2 | 460.5 | 429
2873.1 | 2746.1 | 456.1 | 475.7 | 495.5 | 473.9 | 489.3 | 488.6 | 478.4 | 475.3 | 460.5 | 429
2874.1 | 2747.1 | 455.5 | 475.5 | 495.4 | 473.7 | 489.2 | 488.5 | 478.4 | 475.4 | 460.4 | 429
2875.1 | 2748.1 | 454.8 | 475.4 | 495.1 | 473.6 | 489.2 | 488.5 | 478.4 | 475.3 | 460.3 | 429
2876.1 | 2749.1 | 454.2 | 475.2 | 494.8 | 473.4 | 489.2 | 488.4 | 478.4 | 475.4 | 460.3 | 429
2877.1 | 2750.1 | 453.5 | 475 | 494.7 | 473.2 | 489.1 | 488.3 | 478.4 | 475.4 | 460.3 | 429
2878.1 | 2751.1 | 452.8 | 474.9 | 494.4 | 473.1 | 489 | 488.3 | 478.4 | 475.4 | 460.1 | 429
2879.1 | 2752.1 | 452.2 | 474.7 | 494.1 | 472.9 | 489 | 488.2 | 478.4 | 475.4 | 460.1 | 429
2880.1 | 2753.1 | 451.5 | 474.5 | 493.9 | 472.7 | 488.9 | 488.2 | 478.4 | 475.4 | 460.1 | 429
2881.1 | 2754.1 | 450.9 | 474.3 | 493.7 | 472.5 | 488.8 | 488.1 | 478.4 | 475.3 | 459.9 | 429
2882.1 | 2755.1 | 450.2 | 474.1 | 493.4 | 472.3 | 488.8 | 488 | 478.4 | 475.4 | 459.9 | 429
2883.1 | 2756.1 | 449.5 | 474 | 493.2 | 472.2 | 488.7 | 487.9 | 478.4 | 475.3 | 459.9 | 428.9
2884.1 | 2757.1 | 448.9 | 473.8 | 493 | 472 | 488.6 | 487.9 | 478.4 | 475.2 | 459.8 | 429
2885.1 | 2758.1 | 448.2 | 473.6 | 492.7 | 471.8 | 488.5 | 487.8 | 478.4 | 475.2 | 459.8 | 428.9
2886.1 | 2759.1 | 447.6 | 473.4 | 492.5 | 471.6 | 488.5 | 487.7 | 478.4 | 475.2 | 459.7 | 428.9
2887.1 | 2760.1 | 446.9 | 473.2 | 492.2 | 471.4 | 488.4 | 487.6 | 478.4 | 475.2 | 459.6 | 428.9
2888.1 | 2761.1 | 446.3 | 473 | 492 | 471.2 | 488.3 | 487.5 | 478.4 | 475.2 | 459.6 | 428.9
2889.1 | 2762.1 | 445.7 | 472.9 | 491.7 | 471.1 | 488.3 | 487.5 | 478.3 | 475.1 | 459.5 | 428.9
2890.1 | 2763.1 | 445.1 | 472.7 | 491.5 | 470.9 | 488.2 | 487.4 | 478.3 | 475.1 | 459.4 | 428.9
2891.1 | 2764.1 | 444.5 | 472.5 | 491.3 | 470.6 | 488.1 | 487.3 | 478.3 | 475.1 | 459.4 | 428.9
2892.1 | 2765.1 | 443.9 | 472.3 | 491 | 470.5 | 488 | 487.2 | 478.3 | 475.2 | 459.3 | 428.9
2893.1 | 2766.1 | 443.2 | 472.1 | 490.8 | 470.3 | 488 | 487.2 | 478.3 | 475.1 | 459.2 | 428.9
2894.1 | 2767.1 | 442.6 | 471.9 | 490.5 | 470.1 | 487.9 | 487.1 | 478.3 | 475.1 | 459.2 | 428.9
2895.1 | 2768.1 | 442 | 471.7 | 490.3 | 469.9 | 487.8 | 487 | 478.3 | 475 | 459.1 | 428.9
2896.1 | 2769.1 | 441.4 | 471.5 | 490 | 469.7 | 487.8 | 486.9 | 478.3 | 475 | 459.1 | 428.9
2897.1 | 2770.1 | 440.8 | 471.4 | 489.8 | 469.5 | 487.7 | 486.8 | 478.2 | 475 | 459 | 428.8
2898.1 | 2771.1 | 440.2 | 471.1 | 489.6 | 469.3 | 487.5 | 486.7 | 478.2 | 475 | 458.9 | 428.8
2899.1 | 2772.1 | 439.6 | 470.9 | 489.3 | 469.1 | 487.5 | 486.6 | 478.2 | 475 | 458.9 | 428.8
2900.1 | 2773.1 | 439 | 470.8 | 489 | 468.9 | 487.4 | 486.6 | 478.2 | 474.9 | 458.8 | 428.8
2901.1 | 2774.1 | 438.3 | 470.6 | 488.8 | 468.7 | 487.3 | 486.5 | 478.2 | 475 | 458.7 | 428.8
2902.1 | 2775.1 | 437.7 | 470.3 | 488.6 | 468.5 | 487.2 | 486.3 | 478.2 | 475 | 458.7 | 428.8
2903.1 | 2776.1 | 437.1 | 470.2 | 488.3 | 468.3 | 487.2 | 486.3 | 478.1 | 474.9 | 458.5 | 428.8
2904.1 | 2777.1 | 436.5 | 470 | 488 | 468.1 | 487.1 | 486.2 | 478.1 | 474.9 | 458.4 | 428.8
2905.1 | 2778.1 | 435.8 | 469.7 | 487.8 | 467.9 | 486.9 | 486.1 | 478.1 | 474.9 | 458.4 | 428.7
2906.1 | 2779.1 | 435.2 | 469.6 | 487.5 | 467.7 | 486.9 | 486 | 478.1 | 474.9 | 458.4 | 428.7
2907.1 | 2780.1 | 434.6 | 469.4 | 487.2 | 467.5 | 486.8 | 485.9 | 478 | 474.9 | 458.2 | 428.7
2908.1 | 2781.1 | 434 | 469.2 | 487 | 467.3 | 486.7 | 485.8 | 478 | 474.9 | 458.2 | 428.7
2909.1 | 2782.1 | 433.4 | 468.9 | 486.8 | 467.1 | 486.6 | 485.7 | 478 | 474.9 | 458.2 | 428.7
2910.1 | 2783.1 | 432.8 | 468.7 | 486.6 | 466.9 | 486.5 | 485.6 | 478 | 474.8 | 458 | 428.6
2911.1 | 2784.1 | 432.2 | 468.4 | 486.5 | 466.6 | 486.1 | 485.4 | 478 | 474.8 | 458.1 | 428.6
2912.1 | 2785.1 | 431.6 | 468.2 | 486.4 | 466.4 | 485.9 | 485.3 | 478 | 474.9 | 458 | 428.6
2913.1 | 2786.1 | 431 | 468 | 486.1 | 466.2 | 485.9 | 485.2 | 477.9 | 474.9 | 457.8 | 428.6
2914.1 | 2787.1 | 430.4 | 467.8 | 485.8 | 466 | 485.8 | 485.1 | 477.9 | 474.8 | 457.8 | 428.6
2915.1 | 2788.1 | 429.8 | 467.6 | 485.6 | 465.8 | 485.7 | 485 | 477.9 | 474.7 | 457.7 | 428.6
2916.1 | 2789.1 | 429.2 | 467.3 | 485.4 | 465.6 | 485.5 | 484.8 | 477.8 | 474.6 | 457.6 | 428.5
2917.1 | 2790.1 | 428.6 | 467.2 | 485 | 465.3 | 485.5 | 484.8 | 477.8 | 474.5 | 457.6 | 428.5
2918.1 | 2791.1 | 428 | 467 | 484.8 | 465.2 | 485.4 | 484.7 | 477.8 | 474.5 | 457.5 | 428.5
2919.1 | 2792.1 | 427.5 | 466.7 | 484.5 | 464.9 | 485.3 | 484.5 | 477.7 | 474.5 | 457.3 | 428.5
2920.1 | 2793.1 | 426.9 | 466.5 | 484.3 | 464.7 | 485.2 | 484.4 | 477.7 | 474.5 | 457.3 | 428.5
2921.1 | 2794.1 | 426.3 | 466.3 | 484 | 464.5 | 485.1 | 484.3 | 477.7 | 474.5 | 457.2 | 428.4
2922.1 | 2795.1 | 425.8 | 466.1 | 483.8 | 464.3 | 485 | 484.2 | 477.6 | 474.5 | 457 | 428.4
2923.1 | 2796.1 | 425.2 | 465.9 | 483.5 | 464.1 | 484.8 | 484.1 | 477.6 | 474.5 | 457.1 | 428.4
2924.1 | 2797.1 | 424.7 | 465.7 | 483.2 | 463.9 | 484.8 | 484 | 477.6 | 474.5 | 456.8 | 428.4
2925.1 | 2798.1 | 424.1 | 465.5 | 482.9 | 463.7 | 484.7 | 483.9 | 477.5 | 474.4 | 456.7 | 428.3
2926.1 | 2799.1 | 423.6 | 465.3 | 482.7 | 463.4 | 484.6 | 483.8 | 477.5 | 474.4 | 456.7 | 428.3
2927.1 | 2800.1 | 423 | 465.1 | 482.5 | 463.2 | 484.5 | 483.7 | 477.5 | 474.4 | 456.6 | 428.3
2928.1 | 2801.1 | 422.4 | 464.9 | 482.1 | 463 | 484.4 | 483.6 | 477.4 | 474.4 | 456.5 | 428.3
2929.1 | 2802.1 | 421.9 | 464.6 | 481.9 | 462.8 | 484.3 | 483.4 | 477.4 | 474.4 | 456.4 | 428.2
2930.1 | 2803.1 | 421.3 | 464.4 | 481.7 | 462.6 | 484.1 | 483.3 | 477.3 | 474.4 | 456.3 | 428.2
2931.1 | 2804.1 | 420.7 | 464.2 | 481.3 | 462.4 | 484 | 483.2 | 477.3 | 474.3 | 456.2 | 428.2
2932.1 | 2805.1 | 420.2 | 464 | 481.1 | 462.2 | 483.9 | 483.1 | 477.2 | 474.3 | 456.1 | 428.1
2933.1 | 2806.1 | 419.6 | 463.8 | 480.9 | 461.9 | 483.8 | 483 | 477.2 | 474.2 | 456 | 428.1
2934.1 | 2807.1 | 419.1 | 463.5 | 480.6 | 461.7 | 483.7 | 482.8 | 477.1 | 474.2 | 455.9 | 428.1
2935.1 | 2808.1 | 418.5 | 463.3 | 480.3 | 461.5 | 483.6 | 482.7 | 477.1 | 474.2 | 455.8 | 428
2936.1 | 2809.1 | 418 | 463.1 | 480 | 461.3 | 483.5 | 482.6 | 477 | 474.2 | 455.7 | 428
2937.1 | 2810.1 | 417.4 | 462.9 | 479.8 | 461 | 483.3 | 482.5 | 477 | 474.1 | 455.6 | 428
2938.1 | 2811.1 | 416.9 | 462.7 | 479.5 | 460.8 | 483.2 | 482.4 | 476.9 | 474.1 | 455.5 | 428
2939.1 | 2812.1 | 416.3 | 462.5 | 479.2 | 460.6 | 483.1 | 482.2 | 476.9 | 474.1 | 455.4 | 427.9
2940.1 | 2813.1 | 415.8 | 462.3 | 479 | 460.4 | 483 | 482.1 | 476.8 | 474.1 | 455.3 | 427.9
2941.1 | 2814.1 | 415.3 | 462 | 478.7 | 460.2 | 482.9 | 482 | 476.8 | 474 | 455.2 | 427.9
2942.1 | 2815.1 | 414.7 | 461.8 | 478.4 | 460 | 482.8 | 481.9 | 476.7 | 473.9 | 455.2 | 427.8
2943.1 | 2816.1 | 414.2 | 461.6 | 478.1 | 459.8 | 482.7 | 481.8 | 476.6 | 473.8 | 455.1 | 427.8
2944.1 | 2817.1 | 413.6 | 461.3 | 477.9 | 459.5 | 482.5 | 481.6 | 476.6 | 473.6 | 455 | 427.8
2945.1 | 2818.1 | 413.1 | 461.2 | 477.6 | 459.3 | 482.4 | 481.5 | 476.5 | 473.5 | 454.8 | 427.7
2946.1 | 2819.1 | 412.6 | 460.9 | 477.3 | 459.1 | 482.3 | 481.4 | 476.5 | 473.5 | 454.8 | 427.7
2947.1 | 2820.1 | 412.1 | 460.7 | 477.1 | 458.9 | 482.2 | 481.2 | 476.4 | 473.5 | 454.7 | 427.7
2948.1 | 2821.1 | 411.5 | 460.5 | 476.8 | 458.6 | 482 | 481.1 | 476.3 | 473.4 | 454.5 | 427.6
2949.1 | 2822.1 | 411 | 460.3 | 476.5 | 458.5 | 482 | 481 | 476.3 | 473.5 | 454.4 | 427.6
2950.1 | 2823.1 | 410.5 | 460 | 476.2 | 458.2 | 481.8 | 480.9 | 476.2 | 473.6 | 454.4 | 427.5
2951.1 | 2824.1 | 410 | 459.8 | 476 | 458 | 481.7 | 480.7 | 476.1 | 473.5 | 454.2 | 427.5
2952.1 | 2825.1 | 409.4 | 459.6 | 475.7 | 457.8 | 481.6 | 480.6 | 476.1 | 473.4 | 454.2 | 427.5
2953.1 | 2826.1 | 408.9 | 459.4 | 475.4 | 457.5 | 481.5 | 480.5 | 476 | 473.3 | 454.1 | 427.4
2954.1 | 2827.1 | 408.4 | 459.1 | 475.2 | 457.3 | 481.3 | 480.3 | 476 | 473.2 | 454 | 427.4
2955.1 | 2828.1 | 407.9 | 458.9 | 474.9 | 457.1 | 481.2 | 480.2 | 475.9 | 473.1 | 453.8 | 427.3
2956.1 | 2829.1 | 407.4 | 458.7 | 474.6 | 456.9 | 481.1 | 480.1 | 475.8 | 473 | 453.8 | 427.3
2957.1 | 2830.1 | 406.9 | 458.5 | 474.3 | 456.7 | 481 | 479.9 | 475.8 | 473 | 453.7 | 427.3
2958.1 | 2831.1 | 406.3 | 458.2 | 474.1 | 456.4 | 480.8 | 479.8 | 475.7 | 472.9 | 453.5 | 427.2
2959.1 | 2832.1 | 405.8 | 458 | 473.8 | 456.2 | 480.8 | 479.6 | 475.6 | 472.9 | 453.4 | 427.2
2960.1 | 2833.1 | 405.3 | 457.8 | 473.5 | 456 | 480.6 | 479.5 | 475.6 | 472.9 | 453.3 | 427.1
2961.1 | 2834.1 | 404.8 | 457.6 | 473.3 | 455.7 | 480.5 | 479.4 | 475.5 | 472.9 | 453.1 | 427.1
2962.1 | 2835.1 | 404.3 | 457.3 | 473 | 455.5 | 480.3 | 479.2 | 475.4 | 472.9 | 453.1 | 427
2963.1 | 2836.1 | 403.8 | 457.1 | 472.7 | 455.3 | 480.2 | 479.1 | 475.4 | 472.9 | 452.9 | 427
2964.1 | 2837.1 | 403.3 | 456.9 | 472.4 | 455.1 | 480.1 | 478.9 | 475.3 | 472.8 | 452.8 | 426.9
2965.1 | 2838.1 | 402.9 | 456.6 | 472.2 | 454.8 | 479.9 | 478.8 | 475.3 | 472.7 | 452.7 | 426.9
2966.1 | 2839.1 | 402.4 | 456.5 | 471.9 | 454.6 | 479.8 | 478.7 | 475.2 | 472.6 | 452.6 | 426.8
2967.1 | 2840.1 | 401.9 | 456.2 | 471.6 | 454.4 | 479.7 | 478.5 | 475.1 | 472.6 | 452.4 | 426.8
2968.1 | 2841.1 | 401.4 | 456 | 471.4 | 454.1 | 479.5 | 478.4 | 475 | 472.6 | 452.3 | 426.8
2969.1 | 2842.1 | 400.9 | 455.7 | 471 | 453.9 | 479.4 | 478.2 | 475 | 472.6 | 452.2 | 426.7
2970.1 | 2843.1 | 400.4 | 455.5 | 470.7 | 453.7 | 479.3 | 478.1 | 474.9 | 472.5 | 452.1 | 426.6
2971.1 | 2844.1 | 399.9 | 455.3 | 470.5 | 453.5 | 479.2 | 478 | 474.8 | 472.5 | 451.9 | 426.6
2972.1 | 2845.1 | 399.4 | 455.1 | 470.3 | 453.2 | 479 | 477.8 | 474.8 | 472.5 | 451.8 | 426.5
2973.1 | 2846.1 | 398.9 | 454.8 | 469.9 | 453 | 478.9 | 477.7 | 474.7 | 472.4 | 451.7 | 426.5
2974.1 | 2847.1 | 398.4 | 454.6 | 469.6 | 452.8 | 478.8 | 477.5 | 474.6 | 472.4 | 451.5 | 426.4
2975.1 | 2848.1 | 398 | 454.4 | 469.4 | 452.6 | 478.6 | 477.4 | 474.5 | 472.4 | 451.4 | 426.4
2976.1 | 2849.1 | 397.5 | 454.1 | 469.1 | 452.3 | 478.5 | 477.2 | 474.4 | 472.4 | 451.3 | 426.3
2977.1 | 2850.1 | 397 | 453.9 | 468.8 | 452.1 | 478.4 | 477.1 | 474.4 | 472.4 | 451.2 | 426.3
2978.1 | 2851.1 | 396.5 | 453.7 | 468.6 | 451.9 | 478.2 | 477 | 474.3 | 472.3 | 451 | 426.2
2979.1 | 2852.1 | 396 | 453.4 | 468.3 | 451.6 | 478 | 476.8 | 474.2 | 472.1 | 450.9 | 426.2
2980.1 | 2853.1 | 395.6 | 453.2 | 467.9 | 451.4 | 477.9 | 476.7 | 474.1 | 471.9 | 450.8 | 426.1
2981.1 | 2854.1 | 395.1 | 453 | 467.7 | 451.2 | 477.8 | 476.5 | 474 | 471.9 | 450.7 | 426.1
2982.1 | 2855.1 | 394.6 | 452.7 | 467.4 | 450.9 | 477.6 | 476.3 | 474 | 471.8 | 450.5 | 426
2983.1 | 2856.1 | 394.1 | 452.5 | 467.2 | 450.7 | 477.5 | 476.2 | 473.9 | 471.7 | 450.4 | 425.9
2984.1 | 2857.1 | 393.7 | 452.3 | 466.9 | 450.5 | 477.4 | 476.1 | 473.8 | 471.6 | 450.3 | 425.9
2985.1 | 2858.1 | 393.2 | 452.1 | 466.6 | 450.2 | 477.2 | 475.9 | 473.7 | 471.6 | 450.1 | 425.8
2986.1 | 2859.1 | 392.7 | 451.8 | 466.4 | 450 | 477 | 475.7 | 473.6 | 471.6 | 450 | 425.8
2987.1 | 2860.1 | 392.2 | 451.6 | 466 | 449.8 | 476.9 | 475.6 | 473.5 | 471.5 | 449.9 | 425.7
2988.1 | 2861.1 | 391.7 | 451.4 | 465.8 | 449.6 | 476.8 | 475.5 | 473.4 | 471.4 | 449.7 | 425.7
2989.1 | 2862.1 | 391.3 | 451.1 | 465.5 | 449.3 | 476.6 | 475.3 | 473.3 | 471.4 | 449.7 | 425.6
2990.1 | 2863.1 | 390.8 | 450.9 | 465.2 | 449.1 | 476.5 | 475.2 | 473.2 | 471.3 | 449.6 | 425.5
2991.1 | 2864.1 | 390.3 | 450.7 | 464.9 | 448.9 | 476.4 | 475 | 473.1 | 471.2 | 449.4 | 425.5
2992.1 | 2865.1 | 389.9 | 450.4 | 464.6 | 448.6 | 476.2 | 474.9 | 473 | 471.1 | 449.3 | 425.4
2993.1 | 2866.1 | 389.4 | 450.2 | 464.4 | 448.4 | 476 | 474.7 | 473 | 471.1 | 449.1 | 425.4
2994.1 | 2867.1 | 388.9 | 450 | 464.1 | 448.2 | 476 | 474.6 | 472.9 | 471.1 | 449 | 425.3
2995.1 | 2868.1 | 388.5 | 449.8 | 463.8 | 448 | 475.8 | 474.4 | 472.8 | 471 | 448.8 | 425.3
2996.1 | 2869.1 | 388.1 | 449.5 | 463.6 | 447.7 | 475.6 | 474.2 | 472.7 | 471 | 448.8 | 425.2
2997.1 | 2870.1 | 387.6 | 449.3 | 463.3 | 447.5 | 475.5 | 474.1 | 472.6 | 471 | 448.6 | 425.1
2998.1 | 2871.1 | 387.1 | 449 | 463 | 447.3 | 475.4 | 474 | 472.5 | 470.8 | 448.4 | 425.1
2999.1 | 2872.1 | 386.7 | 448.8 | 462.7 | 447.1 | 475.2 | 473.8 | 472.4 | 470.8 | 448.3 | 425
3000.1 | 2873.1 | 386.2 | 448.5 | 462.5 | 446.8 | 475 | 473.6 | 472.3 | 470.7 | 448.3 | 424.9
3001.1 | 2874.1 | 385.8 | 448.3 | 462.1 | 446.6 | 475 | 473.5 | 472.2 | 470.5 | 448.1 | 424.9
3002.1 | 2875.1 | 385.3 | 448.1 | 461.8 | 446.4 | 474.8 | 473.4 | 472.1 | 470.5 | 447.9 | 424.8
3003.1 | 2876.1 | 384.8 | 447.8 | 461.6 | 446.1 | 474.6 | 473.2 | 472 | 470.5 | 447.9 | 424.7
3004.1 | 2877.1 | 384.4 | 447.6 | 461.3 | 445.9 | 474.5 | 473.1 | 471.9 | 470.4 | 447.7 | 424.7
3005.1 | 2878.1 | 383.9 | 447.4 | 461 | 445.7 | 474.4 | 472.9 | 471.9 | 470.3 | 447.6 | 424.6
3006.1 | 2879.1 | 383.5 | 447.1 | 460.7 | 445.5 | 474.2 | 472.8 | 471.8 | 470.3 | 447.4 | 424.6
3007.1 | 2880.1 | 383 | 446.9 | 460.5 | 445.2 | 474.1 | 472.6 | 471.7 | 470.2 | 447.3 | 424.5
3008.1 | 2881.1 | 382.6 | 446.7 | 460.1 | 445 | 474 | 472.5 | 471.6 | 470.1 | 447.2 | 424.4
3009.1 | 2882.1 | 382.1 | 446.5 | 459.8 | 444.8 | 473.8 | 472.3 | 471.5 | 470.1 | 447 | 424.4
3010.1 | 2883.1 | 381.7 | 446.2 | 459.6 | 444.6 | 473.6 | 472.2 | 471.4 | 470 | 446.9 | 424.3
3011.1 | 2884.1 | 381.2 | 446 | 459.4 | 444.3 | 473.5 | 472 | 471.3 | 470 | 446.7 | 424.2
3012.1 | 2885.1 | 380.8 | 445.7 | 459 | 444.2 | 473.4 | 471.9 | 471.2 | 469.8 | 446.6 | 424.1
3013.1 | 2886.1 | 380.3 | 445.5 | 458.8 | 443.9 | 473.2 | 471.7 | 471.1 | 469.6 | 446.4 | 424.1
3014.1 | 2887.1 | 379.9 | 445.2 | 458.6 | 443.7 | 473 | 471.5 | 471 | 469.5 | 446.3 | 424
3015.1 | 2888.1 | 379.5 | 445 | 458.2 | 443.5 | 473 | 471.4 | 470.9 | 469.3 | 446.1 | 423.9
3016.1 | 2889.1 | 379 | 444.8 | 457.9 | 443.3 | 472.8 | 471.2 | 470.9 | 469.3 | 446 | 423.9
3017.1 | 2890.1 | 378.6 | 444.5 | 457.7 | 443 | 472.6 | 471.1 | 470.8 | 469.2 | 445.9 | 423.8
3018.1 | 2891.1 | 378.2 | 444.3 | 457.4 | 442.8 | 472.5 | 470.9 | 470.7 | 469.1 | 445.7 | 423.7
3019.1 | 2892.1 | 377.7 | 444.1 | 457.1 | 442.6 | 472.4 | 470.8 | 470.6 | 469 | 445.6 | 423.6
3020.1 | 2893.1 | 377.3 | 443.9 | 456.8 | 442.4 | 472.2 | 470.6 | 470.5 | 468.9 | 445.4 | 423.6
3021.1 | 2894.1 | 376.9 | 443.6 | 456.6 | 442.2 | 472 | 470.4 | 470.4 | 468.8 | 445.3 | 423.5
3022.1 | 2895.1 | 376.4 | 443.4 | 456.3 | 442 | 471.9 | 470.3 | 470.3 | 468.7 | 445.1 | 423.4
3023.1 | 2896.1 | 376 | 443.1 | 456 | 441.8 | 471.7 | 470.1 | 470.2 | 468.6 | 445 | 423.4
3024.1 | 2897.1 | 375.6 | 442.9 | 455.8 | 441.5 | 471.5 | 470 | 470.1 | 468.5 | 444.9 | 423.3
3025.1 | 2898.1 | 375.1 | 442.7 | 455.5 | 441.3 | 471.4 | 469.8 | 470 | 468.4 | 444.7 | 423.2
3026.1 | 2899.1 | 374.7 | 442.4 | 455.1 | 441.1 | 471.3 | 469.7 | 469.9 | 468.4 | 444.5 | 423.1
3027.1 | 2900.1 | 374.3 | 442.2 | 454.9 | 440.9 | 471.1 | 469.5 | 469.7 | 468.4 | 444.4 | 423.1
3028.1 | 2901.1 | 373.9 | 441.9 | 454.7 | 440.7 | 470.9 | 469.3 | 469.6 | 468.4 | 444.3 | 423
3029.1 | 2902.1 | 373.4 | 441.7 | 454.3 | 440.5 | 470.8 | 469.2 | 469.5 | 468.3 | 444.1 | 422.9
3030.1 | 2903.1 | 373 | 441.5 | 454 | 440.3 | 470.7 | 469 | 469.4 | 468.3 | 443.9 | 422.8
3031.1 | 2904.1 | 372.6 | 441.2 | 453.8 | 440.1 | 470.5 | 468.8 | 469.3 | 468.2 | 443.8 | 422.7
3032.1 | 2905.1 | 372.2 | 441 | 453.5 | 439.9 | 470.3 | 468.7 | 469.2 | 468.1 | 443.6 | 422.6
3033.1 | 2906.1 | 371.8 | 440.8 | 453.2 | 439.7 | 470.2 | 468.5 | 469.1 | 468 | 443.5 | 422.6
3034.1 | 2907.1 | 371.3 | 440.5 | 452.9 | 439.4 | 470.1 | 468.4 | 469 | 467.9 | 443.4 | 422.5
3035.1 | 2908.1 | 370.9 | 440.3 | 452.7 | 439.2 | 469.9 | 468.2 | 468.9 | 467.7 | 443.2 | 422.4
3036.1 | 2909.1 | 370.5 | 440.1 | 452.4 | 439 | 469.7 | 468 | 468.8 | 467.7 | 443.1 | 422.3
3037.1 | 2910.1 | 370.1 | 439.8 | 452.1 | 438.8 | 469.6 | 467.9 | 468.7 | 467.6 | 442.9 | 422.2
3038.1 | 2911.1 | 369.7 | 439.6 | 451.8 | 438.6 | 469.4 | 467.7 | 468.5 | 467.5 | 442.8 | 422.2
3039.1 | 2912.1 | 369.3 | 439.3 | 451.5 | 438.3 | 469.2 | 467.5 | 468.4 | 467.4 | 442.6 | 422.1
3040.1 | 2913.1 | 368.9 | 439.1 | 451.2 | 438.1 | 469.1 | 467.4 | 468.3 | 467.2 | 442.5 | 422
3041.1 | 2914.1 | 368.5 | 438.9 | 450.9 | 437.9 | 468.9 | 467.2 | 468.2 | 467.2 | 442.3 | 421.9
3042.1 | 2915.1 | 368.1 | 438.6 | 450.7 | 437.7 | 468.7 | 467 | 468.1 | 467.1 | 442.2 | 421.8
3043.1 | 2916.1 | 367.7 | 438.4 | 450.4 | 437.5 | 468.6 | 466.9 | 468 | 467 | 442 | 421.7
3044.1 | 2917.1 | 367.3 | 438.1 | 450.1 | 437.3 | 468.5 | 466.7 | 467.9 | 466.9 | 441.9 | 421.7
3045.1 | 2918.1 | 366.9 | 437.9 | 449.9 | 437 | 468.2 | 466.5 | 467.7 | 466.8 | 441.7 | 421.6
3046.1 | 2919.1 | 366.5 | 437.6 | 449.6 | 436.8 | 468.1 | 466.3 | 467.6 | 466.7 | 441.6 | 421.5
3047.1 | 2920.1 | 366.1 | 437.4 | 449.3 | 436.7 | 468 | 466.2 | 467.5 | 466.5 | 441.4 | 421.4
3048.1 | 2921.1 | 365.6 | 437.2 | 449 | 436.5 | 467.8 | 466 | 467.4 | 466.5 | 441.3 | 421.3
3049.1 | 2922.1 | 365.3 | 436.9 | 448.8 | 436.2 | 467.6 | 465.8 | 467.3 | 466.3 | 441.1 | 421.2
3050.1 | 2923.1 | 364.8 | 436.7 | 448.5 | 436 | 467.5 | 465.7 | 467.2 | 466.1 | 441 | 421.1
3051.1 | 2924.1 | 364.4 | 436.5 | 448.2 | 435.8 | 467.3 | 465.5 | 467.1 | 466 | 440.8 | 421
3052.1 | 2925.1 | 364 | 436.2 | 448 | 435.6 | 467.1 | 465.3 | 467 | 465.8 | 440.7 | 421
3053.1 | 2926.1 | 363.6 | 436 | 447.7 | 435.4 | 467 | 465.2 | 466.8 | 465.7 | 440.5 | 420.9
3054.1 | 2927.1 | 363.2 | 435.8 | 447.4 | 435.2 | 466.8 | 465 | 466.7 | 465.6 | 440.4 | 420.8
3055.1 | 2928.1 | 362.9 | 435.5 | 447.1 | 435 | 466.7 | 464.8 | 466.6 | 465.5 | 440.2 | 420.7
3056.1 | 2929.1 | 362.5 | 435.3 | 446.9 | 434.8 | 466.4 | 464.7 | 466.5 | 465.3 | 440.1 | 420.6
3057.1 | 2930.1 | 362.1 | 435 | 446.5 | 434.6 | 466.3 | 464.5 | 466.4 | 465.3 | 439.9 | 420.5
3058.1 | 2931.1 | 361.7 | 434.8 | 446.3 | 434.3 | 466.2 | 464.3 | 466.3 | 465.2 | 439.8 | 420.4
3059.1 | 2932.1 | 361.3 | 434.5 | 446 | 434.1 | 466 | 464.2 | 466.1 | 465.2 | 439.6 | 420.3
3060.1 | 2933.1 | 360.9 | 434.3 | 445.7 | 433.9 | 465.8 | 464 | 466 | 465 | 439.5 | 420.2
3061.1 | 2934.1 | 360.5 | 434.1 | 445.4 | 433.7 | 465.7 | 463.8 | 465.9 | 465 | 439.3 | 420.1
3062.1 | 2935.1 | 360.2 | 433.8 | 445.2 | 433.5 | 465.5 | 463.7 | 465.8 | 464.8 | 439.2 | 420
3063.1 | 2936.1 | 359.8 | 433.6 | 445 | 433.3 | 465.3 | 463.5 | 465.7 | 464.7 | 439 | 419.9
3064.1 | 2937.1 | 359.4 | 433.4 | 444.6 | 433.1 | 465.2 | 463.3 | 465.5 | 464.7 | 438.9 | 419.8
3065.1 | 2938.1 | 359 | 433.1 | 444.3 | 432.9 | 465 | 463.1 | 465.4 | 464.6 | 438.7 | 419.7
3066.1 | 2939.1 | 358.6 | 432.9 | 444.1 | 432.7 | 464.8 | 462.9 | 465.3 | 464.6 | 438.6 | 419.6
3067.1 | 2940.1 | 358.2 | 432.6 | 443.8 | 432.5 | 464.6 | 462.8 | 465.2 | 464.5 | 438.4 | 419.5
3068.1 | 2941.1 | 357.9 | 432.4 | 443.5 | 432.3 | 464.5 | 462.6 | 465 | 464.5 | 438.3 | 419.4
3069.1 | 2942.1 | 357.5 | 432.2 | 443.3 | 432.1 | 464.3 | 462.4 | 464.9 | 464.3 | 438.1 | 419.4
3070.1 | 2943.1 | 357.1 | 431.9 | 443.1 | 431.9 | 464.1 | 462.2 | 464.8 | 464.1 | 438 | 419.3
3071.1 | 2944.1 | 356.7 | 431.7 | 442.7 | 431.7 | 464 | 462.1 | 464.7 | 464 | 437.8 | 419.2
3072.1 | 2945.1 | 356.4 | 431.5 | 442.4 | 431.5 | 463.8 | 461.9 | 464.5 | 463.9 | 437.7 | 419.1
3073.1 | 2946.1 | 356 | 431.2 | 442.2 | 431.3 | 463.6 | 461.7 | 464.4 | 463.9 | 437.5 | 419
3074.1 | 2947.1 | 355.6 | 431 | 441.9 | 431.1 | 463.5 | 461.5 | 464.3 | 463.9 | 437.4 | 418.9
3075.1 | 2948.1 | 355.2 | 430.7 | 441.6 | 430.9 | 463.3 | 461.4 | 464.2 | 463.8 | 437.2 | 418.8
3076.1 | 2949.1 | 354.8 | 430.5 | 441.3 | 430.7 | 463.1 | 461.2 | 464 | 463.8 | 437.1 | 418.7
3077.1 | 2950.1 | 354.4 | 430.2 | 441.1 | 430.5 | 462.9 | 461 | 463.9 | 463.6 | 436.9 | 418.6
3078.1 | 2951.1 | 354 | 430 | 440.8 | 430.3 | 462.8 | 460.9 | 463.8 | 463.4 | 436.8 | 418.5
3079.1 | 2952.1 | 353.6 | 429.8 | 440.5 | 430.1 | 462.6 | 460.7 | 463.6 | 463.3 | 436.6 | 418.4
3080.1 | 2953.1 | 353.3 | 429.5 | 440.3 | 429.9 | 462.4 | 460.5 | 463.5 | 463.2 | 436.5 | 418.2
3081.1 | 2954.1 | 352.9 | 429.3 | 440 | 429.7 | 462.3 | 460.3 | 463.4 | 463.1 | 436.3 | 418.2
3082.1 | 2955.1 | 352.5 | 429.1 | 439.7 | 429.5 | 462.1 | 460.2 | 463.2 | 463 | 436.2 | 418
3083.1 | 2956.1 | 352.1 | 428.8 | 439.4 | 429.3 | 461.9 | 460 | 463.1 | 462.9 | 436 | 417.9
3084.1 | 2957.1 | 351.7 | 428.6 | 439.2 | 429 | 461.7 | 459.8 | 463 | 462.9 | 435.9 | 417.9
3085.1 | 2958.1 | 351.4 | 428.4 | 438.9 | 428.9 | 461.6 | 459.6 | 462.9 | 462.8 | 435.7 | 417.7
3086.1 | 2959.1 | 351 | 428.1 | 438.6 | 428.7 | 461.4 | 459.4 | 462.7 | 462.6 | 435.6 | 417.6
3087.1 | 2960.1 | 350.6 | 427.9 | 438.4 | 428.4 | 461.2 | 459.2 | 462.6 | 462.5 | 435.4 | 417.5
3088.1 | 2961.1 | 350.2 | 427.6 | 438.1 | 428.2 | 461 | 459.1 | 462.5 | 462.4 | 435.3 | 417.4
3089.1 | 2962.1 | 349.9 | 427.4 | 437.8 | 428.1 | 460.9 | 458.9 | 462.3 | 462.2 | 435.1 | 417.3
3090.1 | 2963.1 | 349.5 | 427.2 | 437.5 | 427.9 | 460.7 | 458.7 | 462.2 | 462.1 | 435 | 417.2
3091.1 | 2964.1 | 349.1 | 426.9 | 437.3 | 427.6 | 460.5 | 458.5 | 462.1 | 461.9 | 434.8 | 417.1
3092.1 | 2965.1 | 348.7 | 426.7 | 437 | 427.4 | 460.4 | 458.4 | 461.9 | 461.8 | 434.7 | 417
3093.1 | 2966.1 | 348.3 | 426.5 | 436.7 | 427.2 | 460.2 | 458.2 | 461.8 | 461.7 | 434.5 | 416.9
3094.1 | 2967.1 | 348 | 426.2 | 436.5 | 427 | 460 | 458 | 461.7 | 461.6 | 434.3 | 416.8
3095.1 | 2968.1 | 347.6 | 426 | 436.2 | 426.8 | 459.8 | 457.8 | 461.5 | 461.5 | 434.2 | 416.7
3096.1 | 2969.1 | 347.3 | 425.7 | 435.9 | 426.6 | 459.7 | 457.6 | 461.4 | 461.3 | 434 | 416.6
3097.1 | 2970.1 | 346.9 | 425.5 | 435.6 | 426.4 | 459.5 | 457.5 | 461.2 | 461.3 | 433.9 | 416.4
3098.1 | 2971.1 | 346.5 | 425.2 | 435.4 | 426.2 | 459.2 | 457.2 | 461.1 | 461.2 | 433.8 | 416.3
3099.1 | 2972.1 | 346.2 | 425 | 435.1 | 426 | 459.1 | 457.1 | 461 | 461.2 | 433.6 | 416.2
3100.1 | 2973.1 | 345.8 | 424.8 | 434.8 | 425.8 | 458.9 | 456.9 | 460.8 | 461.2 | 433.4 | 416.1
3101.1 | 2974.1 | 345.5 | 424.5 | 434.6 | 425.5 | 458.7 | 456.7 | 460.7 | 461.1 | 433.3 | 416
3102.1 | 2975.1 | 345.1 | 424.3 | 434.3 | 425.4 | 458.5 | 456.5 | 460.5 | 461 | 433.1 | 415.9
3103.1 | 2976.1 | 344.8 | 424.1 | 434 | 425.2 | 458.4 | 456.3 | 460.4 | 460.8 | 433 | 415.8
3104.1 | 2977.1 | 344.4 | 423.8 | 433.8 | 424.9 | 458.2 | 456.2 | 460.3 | 460.6 | 432.8 | 415.7
3105.1 | 2978.1 | 344.1 | 423.6 | 433.5 | 424.7 | 458 | 456 | 460.1 | 460.5 | 432.7 | 415.5
3106.1 | 2979.1 | 343.7 | 423.3 | 433.2 | 424.5 | 457.8 | 455.8 | 460 | 460.4 | 432.5 | 415.4
3107.1 | 2980.1 | 343.4 | 423.1 | 433 | 424.3 | 457.7 | 455.6 | 459.8 | 460.3 | 432.4 | 415.3
3108.1 | 2981.1 | 343 | 422.9 | 432.7 | 424.1 | 457.4 | 455.4 | 459.7 | 460.1 | 432.2 | 415.2
3109.1 | 2982.1 | 342.7 | 422.6 | 432.4 | 423.9 | 457.2 | 455.2 | 459.6 | 459.9 | 432.1 | 415.1
3110.1 | 2983.1 | 342.3 | 422.4 | 432.2 | 423.7 | 457.1 | 455.1 | 459.4 | 459.9 | 431.9 | 415
3111.1 | 2984.1 | 342 | 422.2 | 431.9 | 423.5 | 456.9 | 454.9 | 459.3 | 459.7 | 431.8 | 414.8
3112.1 | 2985.1 | 341.6 | 421.9 | 431.7 | 423.3 | 456.7 | 454.7 | 459.1 | 459.6 | 431.6 | 414.7
3113.1 | 2986.1 | 341.3 | 421.7 | 431.3 | 423.1 | 456.5 | 454.5 | 459 | 459.5 | 431.5 | 414.6
3114.1 | 2987.1 | 341 | 421.5 | 431.1 | 422.9 | 456.4 | 454.3 | 458.8 | 459.3 | 431.3 | 414.5
3115.1 | 2988.1 | 340.6 | 421.2 | 430.8 | 422.7 | 456.1 | 454.1 | 458.7 | 459.1 | 431.1 | 414.4
3116.1 | 2989.1 | 340.3 | 421 | 430.6 | 422.4 | 456 | 453.9 | 458.6 | 459 | 431 | 414.3
3117.1 | 2990.1 | 340 | 420.8 | 430.3 | 422.2 | 455.8 | 453.8 | 458.4 | 458.8 | 430.8 | 414.2
3118.1 | 2991.1 | 339.6 | 420.5 | 430 | 422 | 455.6 | 453.6 | 458.3 | 458.7 | 430.7 | 414
3119.1 | 2992.1 | 339.3 | 420.3 | 429.8 | 421.8 | 455.4 | 453.3 | 458.1 | 458.6 | 430.5 | 413.9
3120.1 | 2993.1 | 339 | 420.1 | 429.5 | 421.6 | 455.3 | 453.2 | 458 | 458.5 | 430.4 | 413.8
3121.1 | 2994.1 | 338.6 | 419.8 | 429.2 | 421.4 | 455.1 | 453 | 457.8 | 458.5 | 430.2 | 413.7
3122.1 | 2995.1 | 338.3 | 419.6 | 429 | 421.2 | 454.8 | 452.8 | 457.7 | 458.3 | 430.1 | 413.5
3123.1 | 2996.1 | 338 | 419.3 | 428.7 | 421 | 454.7 | 452.6 | 457.5 | 458 | 429.9 | 413.4
3124.1 | 2997.1 | 337.6 | 419.1 | 428.4 | 420.8 | 454.5 | 452.4 | 457.4 | 457.9 | 429.8 | 413.3
3125.1 | 2998.1 | 337.3 | 418.9 | 428.2 | 420.5 | 454.3 | 452.2 | 457.2 | 457.8 | 429.6 | 413.2
3126.1 | 2999.1 | 336.9 | 418.6 | 428 | 420.3 | 454.1 | 452 | 457.1 | 457.7 | 429.5 | 413.1
3127.1 | 3000.1 | 336.6 | 418.4 | 427.7 | 420.1 | 453.9 | 451.9 | 456.9 | 457.6 | 429.3 | 413
3128.1 | 3001.1 | 336.2 | 418.2 | 427.4 | 419.9 | 453.8 | 451.7 | 456.8 | 457.4 | 429.1 | 412.8
3129.1 | 3002.1 | 335.9 | 417.9 | 427.2 | 419.7 | 453.5 | 451.5 | 456.6 | 457.3 | 429 | 412.7
3130.1 | 3003.1 | 335.6 | 417.7 | 426.9 | 419.5 | 453.4 | 451.3 | 456.5 | 457.2 | 428.9 | 412.6
3131.1 | 3004.1 | 335.2 | 417.5 | 426.6 | 419.3 | 453.2 | 451.1 | 456.3 | 457 | 428.7 | 412.5
3132.1 | 3005.1 | 334.9 | 417.2 | 426.3 | 419.1 | 453 | 450.9 | 456.2 | 456.9 | 428.6 | 412.3
3133.1 | 3006.1 | 334.5 | 417 | 426.2 | 418.9 | 452.8 | 450.7 | 456 | 456.8 | 428.4 | 412.2
3134.1 | 3007.1 | 334.2 | 416.8 | 425.8 | 418.7 | 452.6 | 450.5 | 455.9 | 456.5 | 428.3 | 412.1
3135.1 | 3008.1 | 333.9 | 416.5 | 425.6 | 418.5 | 452.5 | 450.4 | 455.7 | 456.3 | 428.1 | 412
3136.1 | 3009.1 | 333.5 | 416.3 | 425.3 | 418.3 | 452.2 | 450.1 | 455.6 | 456.2 | 428 | 411.9
3137.1 | 3010.1 | 333.2 | 416.1 | 425.1 | 418 | 452 | 450 | 455.4 | 456 | 427.8 | 411.7
3138.1 | 3011.1 | 332.9 | 415.8 | 424.8 | 417.9 | 451.9 | 449.8 | 455.3 | 455.7 | 427.7 | 411.6
3139.1 | 3012.1 | 332.6 | 415.6 | 424.5 | 417.6 | 451.7 | 449.6 | 455.1 | 455.6 | 427.5 | 411.5
3140.1 | 3013.1 | 332.2 | 415.3 | 424.3 | 417.4 | 451.5 | 449.4 | 455 | 455.6 | 427.4 | 411.3
3141.1 | 3014.1 | 331.9 | 415.1 | 424 | 417.2 | 451.3 | 449.2 | 454.8 | 455.5 | 427.2 | 411.2
3142.1 | 3015.1 | 331.6 | 414.9 | 423.7 | 417 | 451.2 | 449 | 454.7 | 455.3 | 427.1 | 411.1
3143.1 | 3016.1 | 331.2 | 414.6 | 423.5 | 416.8 | 450.9 | 448.8 | 454.5 | 455.2 | 426.9 | 411
3144.1 | 3017.1 | 330.9 | 414.4 | 423.2 | 416.6 | 450.7 | 448.6 | 454.4 | 455.1 | 426.7 | 410.8
3145.1 | 3018.1 | 330.6 | 414.2 | 422.9 | 416.4 | 450.6 | 448.4 | 454.2 | 454.9 | 426.6 | 410.7
3146.1 | 3019.1 | 330.2 | 414 | 422.7 | 416.2 | 450.4 | 448.3 | 454 | 454.7 | 426.4 | 410.6
3147.1 | 3020.1 | 329.9 | 413.7 | 422.5 | 416 | 450.1 | 448 | 453.9 | 454.6 | 426.3 | 410.5
3148.1 | 3021.1 | 329.6 | 413.5 | 422.2 | 415.8 | 450 | 447.9 | 453.7 | 454.4 | 426.1 | 410.3
3149.1 | 3022.1 | 329.2 | 413.3 | 421.9 | 415.5 | 449.8 | 447.7 | 453.6 | 454.2 | 426 | 410.2
3150.1 | 3023.1 | 328.9 | 413 | 421.7 | 415.3 | 449.6 | 447.5 | 453.4 | 454.2 | 425.8 | 410.1
3151.1 | 3024.1 | 328.5 | 412.8 | 421.4 | 415.1 | 449.4 | 447.3 | 453.3 | 454.2 | 425.6 | 409.9
3152.1 | 3025.1 | 328.2 | 412.6 | 421.1 | 414.9 | 449.2 | 447.1 | 453.1 | 454 | 425.5 | 409.8
3153.1 | 3026.1 | 327.9 | 412.3 | 420.9 | 414.7 | 449 | 446.9 | 452.9 | 453.8 | 425.3 | 409.7
3154.1 | 3027.1 | 327.5 | 412.1 | 420.7 | 414.5 | 448.8 | 446.7 | 452.8 | 453.7 | 425.2 | 409.5
3155.1 | 3028.1 | 327.2 | 411.9 | 420.4 | 414.3 | 448.6 | 446.5 | 452.6 | 453.5 | 425 | 409.4
3156.1 | 3029.1 | 326.9 | 411.6 | 420.1 | 414.1 | 448.5 | 446.3 | 452.5 | 453.3 | 424.9 | 409.3
3157.1 | 3030.1 | 326.5 | 411.4 | 419.9 | 413.8 | 448.2 | 446.1 | 452.3 | 453.2 | 424.7 | 409.1
3158.1 | 3031.1 | 326.2 | 411.1 | 419.6 | 413.6 | 448 | 445.9 | 452.1 | 453 | 424.5 | 409
3159.1 | 3032.1 | 325.9 | 410.9 | 419.3 | 413.4 | 447.9 | 445.7 | 452 | 452.9 | 424.4 | 408.9
3160.1 | 3033.1 | 325.6 | 410.7 | 419.1 | 413.2 | 447.7 | 445.5 | 451.8 | 452.6 | 424.2 | 408.7
3161.1 | 3034.1 | 325.2 | 410.4 | 418.9 | 413 | 447.4 | 445.3 | 451.7 | 452.4 | 424.1 | 408.6
3162.1 | 3035.1 | 324.9 | 410.2 | 418.6 | 412.8 | 447.3 | 445.1 | 451.5 | 452.2 | 423.9 | 408.5
3163.1 | 3036.1 | 324.6 | 410 | 418.3 | 412.6 | 447.1 | 444.9 | 451.3 | 452.1 | 423.7 | 408.4
3164.1 | 3037.1 | 324.3 | 409.8 | 418.1 | 412.4 | 446.9 | 444.7 | 451.2 | 451.9 | 423.6 | 408.2
3165.1 | 3038.1 | 324 | 409.5 | 417.8 | 412.2 | 446.7 | 444.5 | 451 | 451.8 | 423.4 | 408.1
3166.1 | 3039.1 | 323.7 | 409.3 | 417.5 | 412 | 446.5 | 444.3 | 450.8 | 451.6 | 423.3 | 408
3167.1 | 3040.1 | 323.4 | 409.1 | 417.3 | 411.8 | 446.3 | 444.2 | 450.7 | 451.4 | 423.1 | 407.8
3168.1 | 3041.1 | 323.1 | 408.8 | 417.1 | 411.5 | 446.1 | 443.9 | 450.5 | 451.2 | 422.9 | 407.7
3169.1 | 3042.1 | 322.8 | 408.6 | 416.8 | 411.3 | 445.9 | 443.8 | 450.3 | 451.1 | 422.8 | 407.6
3170.1 | 3043.1 | 322.4 | 408.4 | 416.5 | 411.1 | 445.7 | 443.6 | 450.2 | 450.9 | 422.6 | 407.4
3171.1 | 3044.1 | 322.1 | 408.1 | 416.3 | 410.9 | 445.5 | 443.4 | 450 | 450.8 | 422.5 | 407.3
3172.1 | 3045.1 | 321.8 | 407.9 | 416.1 | 410.7 | 445.3 | 443.2 | 449.8 | 450.7 | 422.3 | 407.2
3173.1 | 3046.1 | 321.5 | 407.7 | 415.8 | 410.5 | 445.1 | 443 | 449.7 | 450.5 | 422.1 | 407
3174.1 | 3047.1 | 321.2 | 407.5 | 415.5 | 410.3 | 444.9 | 442.8 | 449.5 | 450.4 | 422 | 406.9
3175.1 | 3048.1 | 320.9 | 407.2 | 415.3 | 410.1 | 444.7 | 442.6 | 449.3 | 450.2 | 421.8 | 406.7
3176.1 | 3049.1 | 320.6 | 407 | 415 | 409.8 | 444.5 | 442.4 | 449.2 | 450.1 | 421.7 | 406.6
3177.1 | 3050.1 | 320.3 | 406.8 | 414.8 | 409.6 | 444.4 | 442.2 | 449 | 450 | 421.5 | 406.5
3178.1 | 3051.1 | 320 | 406.5 | 414.6 | 409.4 | 444.1 | 442 | 448.8 | 449.8 | 421.4 | 406.3
3179.1 | 3052.1 | 319.7 | 406.3 | 414.3 | 409.2 | 443.9 | 441.8 | 448.7 | 449.7 | 421.2 | 406.2
3180.1 | 3053.1 | 319.3 | 406.1 | 414 | 409 | 443.8 | 441.6 | 448.5 | 449.5 | 421 | 406.1
3181.1 | 3054.1 | 319 | 405.9 | 413.8 | 408.8 | 443.6 | 441.4 | 448.3 | 449.4 | 420.9 | 405.9
3182.1 | 3055.1 | 318.7 | 405.6 | 413.6 | 408.6 | 443.3 | 441.2 | 448.2 | 449.4 | 420.7 | 405.8
3183.1 | 3056.1 | 318.4 | 405.4 | 413.3 | 408.4 | 443.2 | 441 | 448 | 449.2 | 420.6 | 405.6
3184.1 | 3057.1 | 318.1 | 405.2 | 413 | 408.2 | 443 | 440.8 | 447.8 | 449 | 420.4 | 405.5
3185.1 | 3058.1 | 317.8 | 404.9 | 412.8 | 408 | 442.8 | 440.6 | 447.7 | 448.8 | 420.3 | 405.4
3186.1 | 3059.1 | 317.5 | 404.7 | 412.5 | 407.7 | 442.6 | 440.4 | 447.5 | 448.7 | 420.1 | 405.2
3187.1 | 3060.1 | 317.2 | 404.5 | 412.2 | 407.5 | 442.4 | 440.2 | 447.3 | 448.5 | 420 | 405.1
3188.1 | 3061.1 | 316.9 | 404.3 | 412 | 407.3 | 442.2 | 440 | 447.1 | 448.2 | 419.8 | 404.9
3189.1 | 3062.1 | 316.6 | 404 | 411.8 | 407.1 | 441.9 | 439.8 | 447 | 448.1 | 419.6 | 404.8
3190.1 | 3063.1 | 316.3 | 403.8 | 411.5 | 406.9 | 441.8 | 439.6 | 446.8 | 447.8 | 419.5 | 404.7
3191.1 | 3064.1 | 316 | 403.6 | 411.2 | 406.7 | 441.6 | 439.4 | 446.6 | 447.7 | 419.3 | 404.5
3192.1 | 3065.1 | 315.8 | 403.3 | 411 | 406.5 | 441.4 | 439.2 | 446.5 | 447.6 | 419.2 | 404.4
3193.1 | 3066.1 | 315.5 | 403.1 | 410.8 | 406.3 | 441.2 | 439 | 446.3 | 447.6 | 419 | 404.2
3194.1 | 3067.1 | 315.2 | 402.9 | 410.5 | 406.1 | 441 | 438.8 | 446.1 | 447.5 | 418.9 | 404.1
3195.1 | 3068.1 | 314.9 | 402.7 | 410.2 | 405.9 | 440.8 | 438.6 | 446 | 447.4 | 418.7 | 403.9
3196.1 | 3069.1 | 314.6 | 402.4 | 410 | 405.7 | 440.6 | 438.4 | 445.8 | 447.3 | 418.6 | 403.8
3197.1 | 3070.1 | 314.3 | 402.2 | 409.7 | 405.5 | 440.4 | 438.2 | 445.6 | 447.1 | 418.4 | 403.7
3198.1 | 3071.1 | 314 | 402 | 409.5 | 405.3 | 440.3 | 438 | 445.4 | 447 | 418.2 | 403.5
3199.1 | 3072.1 | 313.7 | 401.8 | 409.3 | 405 | 440 | 437.8 | 445.3 | 446.9 | 418.1 | 403.4
3200.1 | 3073.1 | 313.4 | 401.5 | 409 | 404.8 | 439.8 | 437.6 | 445.1 | 446.7 | 417.9 | 403.2
3201.1 | 3074.1 | 313.1 | 401.3 | 408.7 | 404.6 | 439.7 | 437.4 | 444.9 | 446.6 | 417.7 | 403.1
3202.1 | 3075.1 | 312.8 | 401.1 | 408.5 | 404.4 | 439.5 | 437.2 | 444.8 | 446.4 | 417.6 | 403
3203.1 | 3076.1 | 312.5 | 400.8 | 408.3 | 404.2 | 439.2 | 437 | 444.6 | 446.3 | 417.4 | 402.8
3204.1 | 3077.1 | 312.2 | 400.6 | 408 | 404 | 439.1 | 436.9 | 444.4 | 446.2 | 417.3 | 402.7
3205.1 | 3078.1 | 311.9 | 400.4 | 407.7 | 403.8 | 438.9 | 436.7 | 444.2 | 446.1 | 417.1 | 402.5
3206.1 | 3079.1 | 311.6 | 400.2 | 407.5 | 403.6 | 438.6 | 436.4 | 444.1 | 445.9 | 417 | 402.4
3207.1 | 3080.1 | 311.3 | 400 | 407.3 | 403.4 | 438.5 | 436.2 | 443.9 | 445.8 | 416.8 | 402.2
3208.1 | 3081.1 | 311 | 399.8 | 407 | 403.1 | 438.3 | 436.1 | 443.7 | 445.6 | 416.6 | 402.1
3209.1 | 3082.1 | 310.7 | 399.5 | 406.8 | 402.9 | 438.1 | 435.8 | 443.6 | 445.4 | 416.5 | 401.9
3210.1 | 3083.1 | 310.4 | 399.3 | 406.6 | 402.7 | 437.8 | 435.6 | 443.4 | 445.3 | 416.3 | 401.8
3211.1 | 3084.1 | 310.1 | 399.1 | 406.3 | 402.5 | 437.7 | 435.4 | 443.2 | 445 | 416.2 | 401.6
3212.1 | 3085.1 | 309.9 | 398.8 | 406 | 402.3 | 437.5 | 435.3 | 443 | 444.8 | 416 | 401.5
3213.1 | 3086.1 | 309.6 | 398.6 | 405.8 | 402.1 | 437.3 | 435 | 442.9 | 444.7 | 415.9 | 401.4
3214.1 | 3087.1 | 309.3 | 398.4 | 405.6 | 401.9 | 437.1 | 434.8 | 442.7 | 444.6 | 415.7 | 401.2
3215.1 | 3088.1 | 309 | 398.2 | 405.3 | 401.7 | 436.9 | 434.7 | 442.5 | 444.4 | 415.6 | 401.1
3216.1 | 3089.1 | 308.7 | 397.9 | 405.1 | 401.5 | 436.7 | 434.5 | 442.3 | 444.2 | 415.4 | 400.9
3217.1 | 3090.1 | 308.4 | 397.7 | 404.9 | 401.2 | 436.5 | 434.2 | 442.2 | 444.1 | 415.3 | 400.8
3218.1 | 3091.1 | 308.2 | 397.5 | 404.6 | 401 | 436.3 | 434.1 | 442 | 444 | 415.1 | 400.6
3219.1 | 3092.1 | 307.9 | 397.3 | 404.3 | 400.8 | 436.1 | 433.9 | 441.8 | 443.8 | 415 | 400.5
3220.1 | 3093.1 | 307.6 | 397 | 404.1 | 400.6 | 435.9 | 433.6 | 441.6 | 443.7 | 414.8 | 400.3
3221.1 | 3094.1 | 307.3 | 396.8 | 403.9 | 400.4 | 435.7 | 433.4 | 441.5 | 443.5 | 414.7 | 400.2
3222.1 | 3095.1 | 307.1 | 396.6 | 403.6 | 400.2 | 435.5 | 433.3 | 441.3 | 443.3 | 414.5 | 400.1
3223.1 | 3096.1 | 306.8 | 396.4 | 403.3 | 400 | 435.3 | 433.1 | 441.1 | 443.1 | 414.4 | 399.9
3224.1 | 3097.1 | 306.5 | 396.1 | 403.2 | 399.8 | 435.1 | 432.8 | 440.9 | 442.9 | 414.2 | 399.8
3225.1 | 3098.1 | 306.2 | 395.9 | 402.9 | 399.6 | 434.9 | 432.7 | 440.8 | 442.8 | 414.1 | 399.6
3226.1 | 3099.1 | 305.9 | 395.7 | 402.6 | 399.4 | 434.8 | 432.5 | 440.6 | 442.7 | 413.9 | 399.5
3227.1 | 3100.1 | 305.7 | 395.5 | 402.4 | 399.2 | 434.5 | 432.2 | 440.4 | 442.5 | 413.7 | 399.3
3228.1 | 3101.1 | 305.4 | 395.3 | 402.2 | 399 | 434.3 | 432 | 440.2 | 442.4 | 413.6 | 399.2
3229.1 | 3102.1 | 305.1 | 395 | 401.9 | 398.8 | 434.2 | 431.9 | 440 | 442.2 | 413.4 | 399
3230.1 | 3103.1 | 304.8 | 394.8 | 401.7 | 398.5 | 434 | 431.7 | 439.9 | 442.1 | 413.3 | 398.9
3231.1 | 3104.1 | 304.6 | 394.6 | 401.5 | 398.3 | 433.7 | 431.4 | 439.7 | 442 | 413.1 | 398.7
3232.1 | 3105.1 | 304.3 | 394.4 | 401.2 | 398.1 | 433.6 | 431.3 | 439.5 | 441.9 | 413 | 398.6
3233.1 | 3106.1 | 304 | 394.2 | 401 | 397.9 | 433.4 | 431.1 | 439.3 | 441.7 | 412.8 | 398.4
3234.1 | 3107.1 | 303.7 | 393.9 | 400.8 | 397.7 | 433.1 | 430.9 | 439.2 | 441.5 | 412.7 | 398.3
3235.1 | 3108.1 | 303.4 | 393.7 | 400.5 | 397.5 | 432.9 | 430.7 | 439 | 441.3 | 412.5 | 398.1
3236.1 | 3109.1 | 303.1 | 393.5 | 400.2 | 397.3 | 432.8 | 430.5 | 438.8 | 441.1 | 412.4 | 398
3237.1 | 3110.1 | 302.9 | 393.3 | 400 | 397.1 | 432.6 | 430.3 | 438.6 | 441 | 412.2 | 397.8
3238.1 | 3111.1 | 302.6 | 393 | 399.8 | 396.9 | 432.3 | 430 | 438.5 | 440.9 | 412.1 | 397.7
3239.1 | 3112.1 | 302.3 | 392.8 | 399.5 | 396.7 | 432.2 | 429.9 | 438.3 | 440.7 | 411.9 | 397.5
3240.1 | 3113.1 | 302 | 392.6 | 399.3 | 396.5 | 432 | 429.7 | 438.1 | 440.5 | 411.8 | 397.4
3241.1 | 3114.1 | 301.7 | 392.4 | 399.1 | 396.3 | 431.8 | 429.5 | 437.9 | 440.4 | 411.6 | 397.2
3242.1 | 3115.1 | 301.5 | 392.2 | 398.8 | 396.1 | 431.6 | 429.3 | 437.7 | 440.3 | 411.5 | 397.1
3243.1 | 3116.1 | 301.2 | 392 | 398.6 | 395.9 | 431.4 | 429.1 | 437.6 | 440.1 | 411.3 | 396.9
3244.1 | 3117.1 | 300.9 | 391.7 | 398.3 | 395.6 | 431.2 | 428.9 | 437.4 | 439.9 | 411.2 | 396.8
3245.1 | 3118.1 | 300.6 | 391.5 | 398.1 | 395.4 | 431 | 428.7 | 437.2 | 439.8 | 411 | 396.6
3246.1 | 3119.1 | 300.3 | 391.3 | 397.8 | 395.2 | 430.8 | 428.5 | 437 | 439.6 | 410.9 | 396.5
3247.1 | 3120.1 | 300.1 | 391.1 | 397.6 | 395 | 430.6 | 428.3 | 436.8 | 439.4 | 410.7 | 396.3
3248.1 | 3121.1 | 299.8 | 390.8 | 397.4 | 394.8 | 430.4 | 428.1 | 436.7 | 439.2 | 410.5 | 396.2
3249.1 | 3122.1 | 299.5 | 390.6 | 397.2 | 394.6 | 430.2 | 427.9 | 436.5 | 439 | 410.4 | 396
3250.1 | 3123.1 | 299.3 | 390.4 | 396.9 | 394.4 | 430 | 427.7 | 436.3 | 439 | 410.2 | 395.9
3251.1 | 3124.1 | 299 | 390.2 | 396.7 | 394.2 | 429.8 | 427.5 | 436.1 | 438.8 | 410.1 | 395.7
3252.1 | 3125.1 | 298.8 | 389.9 | 396.5 | 393.9 | 429.6 | 427.2 | 435.9 | 438.6 | 409.9 | 395.6
3253.1 | 3126.1 | 298.5 | 389.7 | 396.2 | 393.8 | 429.4 | 427.1 | 435.8 | 438.4 | 409.8 | 395.4
3254.1 | 3127.1 | 298.2 | 389.5 | 395.9 | 393.6 | 429.2 | 426.9 | 435.6 | 438.2 | 409.6 | 395.3
3255.1 | 3128.1 | 298 | 389.3 | 395.8 | 393.3 | 429 | 426.7 | 435.4 | 438.1 | 409.5 | 395.1
3256.1 | 3129.1 | 297.7 | 389.1 | 395.5 | 393.1 | 428.8 | 426.5 | 435.2 | 437.8 | 409.3 | 395
3257.1 | 3130.1 | 297.4 | 388.9 | 395.2 | 392.9 | 428.7 | 426.3 | 435 | 437.5 | 409.2 | 394.8
3258.1 | 3131.1 | 297.2 | 388.7 | 395 | 392.7 | 428.4 | 426.1 | 434.9 | 437.4 | 409.1 | 394.7
3259.1 | 3132.1 | 296.9 | 388.4 | 394.8 | 392.5 | 428.2 | 425.8 | 434.7 | 437.2 | 408.9 | 394.5
3260.1 | 3133.1 | 296.6 | 388.2 | 394.5 | 392.3 | 428 | 425.7 | 434.5 | 437.1 | 408.8 | 394.4
3261.1 | 3134.1 | 296.4 | 388 | 394.3 | 392.1 | 427.8 | 425.5 | 434.3 | 436.9 | 408.6 | 394.2
3262.1 | 3135.1 | 296.1 | 387.8 | 394.1 | 391.9 | 427.6 | 425.2 | 434.1 | 436.8 | 408.5 | 394.1
3263.1 | 3136.1 | 295.8 | 387.6 | 393.9 | 391.7 | 427.4 | 425.1 | 433.9 | 436.7 | 408.3 | 393.9
3264.1 | 3137.1 | 295.6 | 387.4 | 393.6 | 391.5 | 427.3 | 424.9 | 433.8 | 436.4 | 408.2 | 393.8
3265.1 | 3138.1 | 295.3 | 387.1 | 393.4 | 391.3 | 427.1 | 424.7 | 433.6 | 436.2 | 408 | 393.6
3266.1 | 3139.1 | 295.1 | 386.9 | 393.2 | 391 | 426.8 | 424.4 | 433.4 | 436 | 407.9 | 393.5
3267.1 | 3140.1 | 294.8 | 386.7 | 392.9 | 390.8 | 426.7 | 424.3 | 433.2 | 435.7 | 407.7 | 393.3
3268.1 | 3141.1 | 294.6 | 386.5 | 392.7 | 390.6 | 426.5 | 424.1 | 433 | 435.5 | 407.6 | 393.1
3269.1 | 3142.1 | 294.3 | 386.3 | 392.5 | 390.4 | 426.2 | 423.9 | 432.9 | 435.4 | 407.5 | 393
3270.1 | 3143.1 | 294 | 386.1 | 392.3 | 390.2 | 426 | 423.7 | 432.7 | 435.3 | 407.3 | 392.8
3271.1 | 3144.1 | 293.8 | 385.9 | 392 | 390 | 425.9 | 423.5 | 432.5 | 435.1 | 407.2 | 392.7
3272.1 | 3145.1 | 293.5 | 385.7 | 391.8 | 389.8 | 425.7 | 423.3 | 432.3 | 435 | 407.1 | 392.5
3273.1 | 3146.1 | 293.3 | 385.4 | 391.6 | 389.6 | 425.4 | 423.1 | 432.1 | 434.9 | 406.9 | 392.4
3274.1 | 3147.1 | 293 | 385.2 | 391.3 | 389.4 | 425.3 | 422.9 | 432 | 434.8 | 406.8 | 392.2
3275.1 | 3148.1 | 292.8 | 385 | 391.1 | 389.2 | 425.1 | 422.7 | 431.8 | 434.7 | 406.6 | 392.1
3276.1 | 3149.1 | 292.5 | 384.8 | 390.9 | 389 | 424.9 | 422.5 | 431.6 | 434.5 | 406.5 | 391.9
3277.1 | 3150.1 | 292.3 | 384.6 | 390.7 | 388.8 | 424.7 | 422.3 | 431.4 | 434.3 | 406.4 | 391.8
3278.1 | 3151.1 | 292 | 384.4 | 390.4 | 388.6 | 424.5 | 422.1 | 431.2 | 434.1 | 406.2 | 391.6
3279.1 | 3152.1 | 291.7 | 384.1 | 390.2 | 388.4 | 424.3 | 421.9 | 431 | 434 | 406.1 | 391.5
3280.1 | 3153.1 | 291.5 | 383.9 | 390 | 388.2 | 424.1 | 421.7 | 430.9 | 433.8 | 406 | 391.3
3281.1 | 3154.1 | 291.2 | 383.7 | 389.7 | 388 | 423.9 | 421.5 | 430.7 | 433.6 | 405.8 | 391.1
3282.1 | 3155.1 | 291 | 383.5 | 389.5 | 387.8 | 423.7 | 421.3 | 430.5 | 433.4 | 405.7 | 391
3283.1 | 3156.1 | 290.7 | 383.3 | 389.3 | 387.5 | 423.5 | 421.1 | 430.3 | 433.2 | 405.5 | 390.8
3284.1 | 3157.1 | 290.5 | 383 | 389.1 | 387.3 | 423.3 | 420.9 | 430.1 | 433 | 405.4 | 390.7
3285.1 | 3158.1 | 290.2 | 382.9 | 388.8 | 387.1 | 423.1 | 420.7 | 430 | 432.8 | 405.3 | 390.5
3286.1 | 3159.1 | 290 | 382.6 | 388.6 | 386.9 | 422.9 | 420.5 | 429.8 | 432.6 | 405.1 | 390.4
3287.1 | 3160.1 | 289.7 | 382.4 | 388.4 | 386.7 | 422.7 | 420.3 | 429.6 | 432.5 | 405 | 390.2
3288.1 | 3161.1 | 289.4 | 382.2 | 388.1 | 386.6 | 422.6 | 420.1 | 429.4 | 432.4 | 404.8 | 390.1
3289.1 | 3162.1 | 289.2 | 382.2 | 387.6 | 386.4 | 422.7 | 420 | 429.2 | 432.3 | 404.6 | 389.9
3290.1 | 3163.1 | 288.9 | 381.9 | 387.4 | 386.2 | 422.5 | 419.8 | 429 | 432.2 | 404.5 | 389.7
3291.1 | 3164.1 | 288.7 | 381.7 | 387.1 | 386 | 422.3 | 419.6 | 428.8 | 432 | 404.4 | 389.6
3292.1 | 3165.1 | 288.4 | 381.5 | 386.9 | 385.8 | 422.2 | 419.5 | 428.6 | 431.8 | 404.2 | 389.4
3293.1 | 3166.1 | 288.2 | 381.3 | 386.7 | 385.6 | 422 | 419.3 | 428.5 | 431.6 | 404.1 | 389.3
3294.1 | 3167.1 | 287.9 | 381.1 | 386.5 | 385.4 | 421.7 | 419 | 428.3 | 431.4 | 404 | 389.1
3295.1 | 3168.1 | 287.7 | 380.9 | 386.2 | 385.2 | 421.6 | 418.9 | 428.1 | 431.3 | 403.8 | 389
3296.1 | 3169.1 | 287.4 | 380.7 | 386 | 385 | 421.4 | 418.7 | 427.9 | 431.1 | 403.7 | 388.8
3297.1 | 3170.1 | 287.2 | 380.4 | 385.8 | 384.8 | 421.2 | 418.4 | 427.7 | 431 | 403.6 | 388.7
3298.1 | 3171.1 | 286.9 | 380.2 | 385.5 | 384.6 | 421 | 418.3 | 427.5 | 430.8 | 403.4 | 388.5
3299.1 | 3172.1 | 286.7 | 380 | 385.3 | 384.4 | 420.8 | 418.1 | 427.4 | 430.7 | 403.3 | 388.3
3300.1 | 3173.1 | 286.4 | 379.8 | 385.1 | 384.2 | 420.6 | 417.9 | 427.2 | 430.5 | 403.2 | 388.2
3301.1 | 3174.1 | 286.2 | 379.6 | 384.9 | 384 | 420.4 | 417.7 | 427 | 430.2 | 403.1 | 388
3302.1 | 3175.1 | 285.9 | 379.4 | 384.6 | 383.8 | 420.2 | 417.5 | 426.8 | 430 | 402.9 | 387.9
3303.1 | 3176.1 | 285.7 | 379.2 | 384.4 | 383.6 | 420 | 417.3 | 426.6 | 429.8 | 402.8 | 387.7
3304.1 | 3177.1 | 285.4 | 379 | 384.2 | 383.4 | 419.8 | 417.1 | 426.4 | 429.6 | 402.6 | 387.6
3305.1 | 3178.1 | 285.2 | 378.8 | 384 | 383.2 | 419.6 | 416.9 | 426.3 | 429.5 | 402.5 | 387.4
3306.1 | 3179.1 | 284.9 | 378.6 | 383.7 | 383 | 419.5 | 416.7 | 426.1 | 429.3 | 402.3 | 387.3
3307.1 | 3180.1 | 284.7 | 378.4 | 383.5 | 382.8 | 419.3 | 416.5 | 425.9 | 429.1 | 402.2 | 387.1
3308.1 | 3181.1 | 284.4 | 378.1 | 383.4 | 382.6 | 419 | 416.3 | 425.7 | 428.9 | 402.1 | 387
3309.1 | 3182.1 | 284.2 | 377.9 | 383.1 | 382.4 | 418.9 | 416.1 | 425.5 | 428.6 | 401.9 | 386.8
3310.1 | 3183.1 | 284 | 377.7 | 382.9 | 382.1 | 418.7 | 415.9 | 425.3 | 428.5 | 401.8 | 386.6
3311.1 | 3184.1 | 283.7 | 377.5 | 382.7 | 381.9 | 418.5 | 415.7 | 425.1 | 428.3 | 401.7 | 386.5
3312.1 | 3185.1 | 283.5 | 377.3 | 382.4 | 381.7 | 418.3 | 415.5 | 425 | 428 | 401.6 | 386.3
3313.1 | 3186.1 | 283.3 | 377.1 | 382.2 | 381.6 | 418.1 | 415.3 | 424.8 | 427.9 | 401.4 | 386.2
3314.1 | 3187.1 | 283 | 376.9 | 382 | 381.4 | 417.9 | 415.1 | 424.6 | 427.8 | 401.3 | 386
3315.1 | 3188.1 | 282.8 | 376.6 | 381.8 | 381.1 | 417.7 | 414.9 | 424.4 | 427.6 | 401.2 | 385.9
3316.1 | 3189.1 | 282.6 | 376.5 | 381.5 | 381 | 417.6 | 414.7 | 424.2 | 427.4 | 401.1 | 385.7
3317.1 | 3190.1 | 282.3 | 376.3 | 381.3 | 380.8 | 417.4 | 414.6 | 424 | 427.3 | 401 | 385.6
3318.1 | 3191.1 | 282.1 | 376 | 381.1 | 380.5 | 417.1 | 414.3 | 423.9 | 427.3 | 400.8 | 385.4
3319.1 | 3192.1 | 281.8 | 375.8 | 380.9 | 380.3 | 416.9 | 414.1 | 423.7 | 427.2 | 400.7 | 385.2
3320.1 | 3193.1 | 281.6 | 375.6 | 380.6 | 380.1 | 416.8 | 414 | 423.5 | 427 | 400.5 | 385.1
3321.1 | 3194.1 | 281.4 | 375.4 | 380.4 | 379.9 | 416.6 | 413.8 | 423.3 | 426.8 | 400.4 | 384.9
3322.1 | 3195.1 | 281.1 | 375.2 | 380.3 | 379.7 | 416.4 | 413.6 | 423.1 | 426.6 | 400.3 | 384.8
3323.1 | 3196.1 | 280.9 | 375 | 380 | 379.5 | 416.2 | 413.4 | 422.9 | 426.5 | 400.1 | 384.6
3324.1 | 3197.1 | 280.7 | 374.8 | 379.8 | 379.3 | 416.1 | 413.2 | 422.8 | 426.4 | 400 | 384.5
3325.1 | 3198.1 | 280.4 | 374.6 | 379.6 | 379.1 | 415.8 | 413 | 422.6 | 426.3 | 399.8 | 384.3
3326.1 | 3199.1 | 280.2 | 374.4 | 379.4 | 378.9 | 415.6 | 412.8 | 422.4 | 426.2 | 399.7 | 384.2
3327.1 | 3200.1 | 279.9 | 374.2 | 379.1 | 378.7 | 415.5 | 412.6 | 422.2 | 426 | 399.5 | 384
3328.1 | 3201.1 | 279.7 | 374 | 378.9 | 378.5 | 415.3 | 412.4 | 422 | 425.8 | 399.4 | 383.8
3329.1 | 3202.1 | 279.5 | 373.7 | 378.7 | 378.3 | 415 | 412.2 | 421.8 | 425.7 | 399.2 | 383.7
3330.1 | 3203.1 | 279.2 | 373.6 | 378.5 | 378.1 | 414.9 | 412 | 421.7 | 425.5 | 399.1 | 383.5
3331.1 | 3204.1 | 279 | 373.4 | 378.2 | 377.9 | 414.7 | 411.8 | 421.5 | 425.4 | 398.9 | 383.4
3332.1 | 3205.1 | 278.7 | 373.1 | 378.1 | 377.7 | 414.5 | 411.6 | 421.3 | 425.3 | 398.7 | 383.2
3333.1 | 3206.1 | 278.5 | 372.9 | 377.9 | 377.5 | 414.3 | 411.4 | 421.1 | 425.1 | 398.6 | 383.1
3334.1 | 3207.1 | 278.2 | 372.7 | 377.6 | 377.3 | 414.1 | 411.2 | 420.9 | 424.9 | 398.4 | 382.9
3335.1 | 3208.1 | 278 | 372.7 | 377.1 | 377.2 | 414.4 | 411.1 | 420.7 | 424.7 | 398.2 | 382.7
3336.1 | 3209.1 | 277.8 | 372.4 | 376.9 | 377 | 414.2 | 410.9 | 420.5 | 424.6 | 398.1 | 382.6
3337.1 | 3210.1 | 277.5 | 372.3 | 376.6 | 376.8 | 414.1 | 410.8 | 420.3 | 424.4 | 397.9 | 382.4
3338.1 | 3211.1 | 277.3 | 372.1 | 376.4 | 376.6 | 413.9 | 410.6 | 420.1 | 424.1 | 397.8 | 382.3
3339.1 | 3212.1 | 277 | 371.9 | 376.2 | 376.4 | 413.7 | 410.4 | 419.9 | 423.9 | 397.6 | 382.1
3340.1 | 3213.1 | 276.8 | 371.6 | 376 | 376.2 | 413.5 | 410.2 | 419.8 | 423.6 | 397.5 | 381.9
3341.1 | 3214.1 | 276.6 | 371.5 | 375.7 | 376 | 413.3 | 410 | 419.6 | 423.3 | 397.3 | 381.8
3342.1 | 3215.1 | 276.3 | 371.3 | 375.5 | 375.8 | 413.1 | 409.8 | 419.4 | 423 | 397.2 | 381.6
3343.1 | 3216.1 | 276.1 | 371 | 375.4 | 375.6 | 412.9 | 409.6 | 419.2 | 422.8 | 397.1 | 381.5
3344.1 | 3217.1 | 275.9 | 370.9 | 375.1 | 375.4 | 412.8 | 409.4 | 419 | 422.6 | 396.9 | 381.3
3345.1 | 3218.1 | 275.7 | 370.7 | 374.9 | 375.2 | 412.6 | 409.2 | 418.8 | 422.3 | 396.8 | 381.2
3346.1 | 3219.1 | 275.4 | 370.4 | 374.7 | 375 | 412.4 | 409 | 418.6 | 422 | 396.7 | 381
3347.1 | 3220.1 | 275.2 | 370.2 | 374.5 | 374.8 | 412.1 | 408.8 | 418.5 | 421.9 | 396.5 | 380.8
3348.1 | 3221.1 | 275 | 370.1 | 374.2 | 374.6 | 412 | 408.6 | 418.3 | 421.7 | 396.4 | 380.7
3349.1 | 3222.1 | 274.7 | 369.8 | 374 | 374.4 | 411.8 | 408.4 | 418.1 | 421.5 | 396.2 | 380.5
3350.1 | 3223.1 | 274.5 | 369.6 | 373.8 | 374.2 | 411.6 | 408.2 | 417.9 | 421.4 | 396.1 | 380.4
3351.1 | 3224.1 | 274.3 | 369.4 | 373.6 | 374 | 411.4 | 408.1 | 417.7 | 421.1 | 396 | 380.2
3352.1 | 3225.1 | 274.1 | 369.2 | 373.4 | 373.8 | 411.3 | 407.9 | 417.5 | 421 | 395.9 | 380
3353.1 | 3226.1 | 273.9 | 369 | 373.2 | 373.6 | 411 | 407.7 | 417.4 | 420.9 | 395.8 | 379.9
3354.1 | 3227.1 | 273.7 | 368.8 | 373 | 373.4 | 410.8 | 407.5 | 417.2 | 420.8 | 395.7 | 379.7
3355.1 | 3228.1 | 273.4 | 368.6 | 372.7 | 373.2 | 410.7 | 407.3 | 417 | 420.6 | 395.6 | 379.6
3356.1 | 3229.1 | 273.2 | 368.4 | 372.5 | 373 | 410.5 | 407.1 | 416.8 | 420.5 | 395.5 | 379.4
3357.1 | 3230.1 | 273 | 368.2 | 372.4 | 372.8 | 410.2 | 406.9 | 416.6 | 420.4 | 395.3 | 379.3
3358.1 | 3231.1 | 272.8 | 368 | 372.1 | 372.6 | 410.1 | 406.7 | 416.4 | 420.2 | 395.2 | 379.1
3359.1 | 3232.1 | 272.5 | 367.8 | 371.9 | 372.4 | 409.9 | 406.5 | 416.2 | 419.9 | 395.1 | 378.9
3360.1 | 3233.1 | 272.3 | 367.6 | 371.8 | 372.2 | 409.7 | 406.3 | 416 | 419.7 | 394.9 | 378.8
3361.1 | 3234.1 | 272.1 | 367.4 | 371.5 | 372 | 409.5 | 406.1 | 415.9 | 419.5 | 394.8 | 378.6
3362.1 | 3235.1 | 271.9 | 367.2 | 371.3 | 371.9 | 409.3 | 406 | 415.7 | 419.4 | 394.6 | 378.5
3363.1 | 3236.1 | 271.6 | 367 | 371 | 371.7 | 409.2 | 405.8 | 415.5 | 419.3 | 394.4 | 378.3
3364.1 | 3237.1 | 271.4 | 366.8 | 370.9 | 371.5 | 408.9 | 405.5 | 415.3 | 419.1 | 394.3 | 378.2
3365.1 | 3238.1 | 271.2 | 366.6 | 370.6 | 371.3 | 408.8 | 405.4 | 415.1 | 419 | 394.1 | 378
3366.1 | 3239.1 | 270.9 | 366.4 | 370.4 | 371.1 | 408.6 | 405.2 | 414.9 | 418.8 | 393.9 | 377.9
3367.1 | 3240.1 | 270.7 | 366.2 | 370.2 | 370.9 | 408.4 | 405 | 414.7 | 418.6 | 393.8 | 377.7
3368.1 | 3241.1 | 270.5 | 366 | 370 | 370.7 | 408.2 | 404.8 | 414.6 | 418.4 | 393.6 | 377.5
3369.1 | 3242.1 | 270.3 | 365.8 | 369.8 | 370.5 | 408.1 | 404.6 | 414.4 | 418.2 | 393.4 | 377.4
3370.1 | 3243.1 | 270 | 365.6 | 369.6 | 370.3 | 407.9 | 404.4 | 414.2 | 418 | 393.3 | 377.2
3371.1 | 3244.1 | 269.8 | 365.4 | 369.4 | 370.1 | 407.6 | 404.2 | 414 | 417.7 | 393.2 | 377.1
3372.1 | 3245.1 | 269.6 | 365.2 | 369.2 | 369.9 | 407.4 | 404 | 413.8 | 417.5 | 393 | 376.9
3373.1 | 3246.1 | 269.4 | 365 | 368.9 | 369.7 | 407.3 | 403.8 | 413.6 | 417.3 | 392.9 | 376.7
3374.1 | 3247.1 | 269.2 | 364.8 | 368.8 | 369.5 | 407 | 403.6 | 413.5 | 417.2 | 392.8 | 376.6
3375.1 | 3248.1 | 268.9 | 364.6 | 368.6 | 369.3 | 406.8 | 403.4 | 413.3 | 417 | 392.7 | 376.4
3376.1 | 3249.1 | 268.7 | 364.4 | 368.3 | 369.1 | 406.7 | 403.2 | 413.1 | 416.9 | 392.6 | 376.3
3377.1 | 3250.1 | 268.5 | 364.2 | 368.1 | 368.9 | 406.5 | 403 | 412.9 | 416.6 | 392.5 | 376.1
3378.1 | 3251.1 | 268.3 | 364 | 368 | 368.7 | 406.2 | 402.8 | 412.7 | 416.4 | 392.4 | 376
3379.1 | 3252.1 | 268.1 | 363.8 | 367.7 | 368.5 | 406.2 | 402.7 | 412.5 | 416.2 | 392.3 | 375.8
3380.1 | 3253.1 | 267.8 | 363.6 | 367.5 | 368.3 | 405.9 | 402.5 | 412.3 | 416.1 | 392.2 | 375.6
3381.1 | 3254.1 | 267.6 | 363.4 | 367.3 | 368.1 | 405.7 | 402.3 | 412.2 | 416 | 392.1 | 375.5

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 47 |  |  | 2006-08-30 | 11:56
38959.4959 | 1 | 0 | 1 | XLPE & EPR | 7-C | Conduit
38959.4964 | 1 | 0 | 1 | 525 C | 23 kW/m2 |  | Bundle
38959.4969 | 1 | 0 | 1
38959.4974 | 1 | 0 | 1
38959.4979 | 1 | 0 | 1
38959.4984 | 1 | 0 | 1
38959.4989 | 1 | 0 | 1
38959.4993 | 1 | 0 | 1
38959.4998 | 1 | 0 | 1
38959.5003 | 1 | 0 | 1
38959.5008 | 1 | 0 | 1
38959.5013 | 1 | 0 | 1
38959.5018 | 1 | 0 | 1
38959.5023 | 1 | 0 | 1
38959.5027 | 1 | 0 | 1
38959.5032 | 1 | 0 | 1
38959.5037 | 1 | 0 | 1
38959.5042 | 1 | 0 | 1
38959.5047 | 1 | 0 | 1
38959.5052 | 1 | 0 | 1
38959.5057 | 1 | 0 | 1
38959.5061 | 1 | 0 | 1
38959.5066 | 1 | 0 | 1
38959.5071 | 1 | 0 | 1
38959.5076 | 1 | 0 | 1
38959.5081 | 1 | 0 | 1
38959.5086 | 1 | 0 | 1
38959.5091 | 1 | 0 | 1
38959.5095 | 1 | 0 | 1
38959.51 | 1 | 0 | 1
38959.5105 | 1 | 0 | 1
38959.511 | 1 | 0 | 1
38959.5115 | 1 | 0 | 1
38959.512 | 1 | 0 | 1
38959.5125 | 2 | 0 | 1
38959.5129 | 3 | 0 | 1
38959.5134 | 3 | 0 | 1
38959.5139 | 3 | 0 | 1
38959.5144 | 3 | 0 | 1
38959.5149 | 3 | 0 | 1
38959.5154 | 3 | 0 | 1
38959.5159 | 4 | 0 | 1
38959.5163 | 4 | 1 | 1
38959.5168 | 6 | 4 | 1
38959.5173 | 128 | 120 | 1
38959.5178 | 1206 | 963 | 1
38959.5183 | 1200 | 1172 | 1
38959.5188 | 1061 | 1101 | 1
38959.5193 | 1130 | 1095 | 1
38959.5197 | 948 | 914 | 1
38959.5202 | 951 | 914 | 1
38959.5207 | 1210 | 1179 | 1
38959.5212 | 1139 | 1099 | 1
38959.5217 | 990 | 1086 | 1
38959.5222 | 1032 | 990 | 1
38959.5227 | 1014 | 972 | 1
38959.5231 | 992 | 1014 | 1
38959.5236 | 1203 | 1159 | 1
38959.5241 | 1132 | 1082 | 1
38959.5246 | 1134 | 906 | 1
38959.5251 | 1063 | 1008 | 1
38959.5256 | 978 | 984 | 1
38959.5261 | 948 | 894 | 1
38959.5266 | 1211 | 1036 | 1
38959.527 | 1084 | 1081 | 1
38959.5275 | 1204 | 1155 | 1
38959.528 | 972 | 890 | 1
38959.5285 | 1064 | 963 | 1
38959.529 | 1085 | 971 | 1
38959.5295 | 1167 | 1026 | 1
38959.53 | 1259 | 1108 | 1
38959.5304 | 1003 | 853 | 1
38959.5309 | 1204 | 1075 | 1
38959.5314 | 2104 | 160 | 1
38959.5319 | 1896 | 85 | 1
38959.5324 | 2002 | 83 | 1
38959.5329 | 2306 | 85 | 1
38959.5334 | 1965 | 74 | 1
38959.5338 | 2141 | 76 | 1
38959.5343 | 2044 | 67 | 1
38959.5348 | 2205 | 81 | 1
1
38959.4959 | 1 | 0 | 2
38959.4964 | 1 | 0 | 2
38959.4969 | 1 | 0 | 2
38959.4974 | 1 | 0 | 2
38959.4979 | 1 | 0 | 2
38959.4984 | 1 | 0 | 2
38959.4989 | 1 | 0 | 2
38959.4994 | 1 | 0 | 2
38959.4998 | 1 | 0 | 2
38959.5003 | 1 | 0 | 2
38959.5008 | 1 | 0 | 2
38959.5013 | 1 | 0 | 2
38959.5018 | 1 | 0 | 2
38959.5023 | 1 | 0 | 2
38959.5028 | 1 | 0 | 2
38959.5032 | 1 | 0 | 2
38959.5037 | 1 | 0 | 2
38959.5042 | 1 | 0 | 2
38959.5047 | 1 | 0 | 2
38959.5052 | 1 | 0 | 2
38959.5057 | 1 | 0 | 2
38959.5062 | 1 | 0 | 2
38959.5066 | 1 | 0 | 2
38959.5071 | 1 | 0 | 2
38959.5076 | 1 | 0 | 2
38959.5081 | 1 | 0 | 2
38959.5086 | 1 | 0 | 2
38959.5091 | 1 | 0 | 2
38959.5096 | 1 | 0 | 2
38959.51 | 1 | 0 | 2
38959.5105 | 1 | 0 | 2
38959.511 | 1 | 0 | 2
38959.5115 | 1 | 0 | 2
38959.512 | 1 | 0 | 2
38959.5125 | 1 | 0 | 2
38959.513 | 2 | 0 | 2
38959.5134 | 2 | 0 | 2
38959.5139 | 3 | 0 | 2
38959.5144 | 3 | 0 | 2
38959.5149 | 3 | 0 | 2
38959.5154 | 2 | 0 | 2
38959.5159 | 3 | 0 | 2
38959.5164 | 4 | 1 | 2
38959.5169 | 6 | 2 | 2
38959.5173 | 1081 | 1130 | 2
38959.5178 | 1198 | 1125 | 2
38959.5183 | 1177 | 1196 | 2
38959.5188 | 1168 | 1135 | 2
38959.5193 | 1053 | 1020 | 2
38959.5198 | 1142 | 1182 | 2
38959.5203 | 1063 | 1023 | 2
38959.5207 | 1162 | 1120 | 2
38959.5212 | 1047 | 1079 | 2
38959.5217 | 1028 | 988 | 2
38959.5222 | 1085 | 1043 | 2
38959.5227 | 1165 | 1122 | 2
38959.5232 | 1101 | 1134 | 2
38959.5237 | 1062 | 1015 | 2
38959.5241 | 1068 | 1019 | 2
38959.5246 | 1195 | 1145 | 2
38959.5251 | 1165 | 1168 | 2
38959.5256 | 961 | 908 | 2
38959.5261 | 1212 | 1021 | 2
38959.5266 | 959 | 1033 | 2
38959.5271 | 1153 | 1150 | 2
38959.5275 | 1181 | 1095 | 2
38959.528 | 1051 | 962 | 2
38959.5285 | 1164 | 1054 | 2
38959.529 | 1035 | 924 | 2
38959.5295 | 1249 | 1106 | 2
38959.53 | 1013 | 876 | 2
38959.5305 | 1132 | 964 | 2
38959.5309 | 1218 | 1012 | 2
38959.5314 | 1818 | 118 | 2
38959.5319 | 2170 | 89 | 2
38959.5324 | 2271 | 81 | 2
38959.5329 | 1815 | 64 | 2
38959.5334 | 2124 | 70 | 2
38959.5339 | 1935 | 64 | 2
38959.5344 | 1846 | 62 | 2
38959.5348 | 2254 | 80 | 2
2
38959.496 | 1 | 0 | 3
38959.4965 | 1 | 0 | 3
38959.4969 | 1 | 0 | 3
38959.4974 | 1 | 0 | 3
38959.4979 | 1 | 0 | 3
38959.4984 | 1 | 0 | 3
38959.4989 | 1 | 0 | 3
38959.4994 | 1 | 0 | 3
38959.4999 | 1 | 0 | 3
38959.5003 | 1 | 0 | 3
38959.5008 | 1 | 0 | 3
38959.5013 | 1 | 0 | 3
38959.5018 | 1 | 0 | 3
38959.5023 | 1 | 0 | 3
38959.5028 | 1 | 0 | 3
38959.5033 | 1 | 0 | 3
38959.5037 | 1 | 0 | 3
38959.5042 | 1 | 0 | 3
38959.5047 | 1 | 0 | 3
38959.5052 | 1 | 0 | 3
38959.5057 | 1 | 0 | 3
38959.5062 | 1 | 0 | 3
38959.5067 | 1 | 0 | 3
38959.5071 | 1 | 0 | 3
38959.5076 | 1 | 0 | 3
38959.5081 | 1 | 0 | 3
38959.5086 | 1 | 0 | 3
38959.5091 | 1 | 0 | 3
38959.5096 | 1 | 0 | 3
38959.5101 | 1 | 0 | 3
38959.5105 | 1 | 0 | 3
38959.511 | 1 | 0 | 3
38959.5115 | 1 | 0 | 3
38959.512 | 1 | 0 | 3
38959.5125 | 1 | 0 | 3
38959.513 | 3 | 0 | 3
38959.5135 | 3 | 0 | 3
38959.5139 | 3 | 0 | 3
38959.5144 | 2 | 0 | 3
38959.5149 | 2 | 0 | 3
38959.5154 | 2 | 0 | 3
38959.5159 | 2 | 0 | 3
38959.5164 | 3 | 0 | 3
38959.5169 | 2 | 0 | 3
38959.5173 | 3 | 2 | 3
38959.5178 | 3 | 3 | 3
38959.5183 | 3 | 2 | 3
38959.5188 | 3 | 2 | 3
38959.5193 | 3 | 2 | 3
38959.5198 | 2 | 2 | 3
38959.5203 | 3 | 2 | 3
38959.5208 | 3 | 3 | 3
38959.5212 | 3 | 2 | 3
38959.5217 | 3 | 3 | 3
38959.5222 | 2 | 2 | 3
38959.5227 | 2 | 2 | 3
38959.5232 | 2 | 2 | 3
38959.5237 | 2 | 2 | 3
38959.5242 | 2 | 3 | 3
38959.5246 | 2 | 2 | 3
38959.5251 | 2 | 2 | 3
38959.5256 | 3 | 2 | 3
38959.5261 | 2 | 2 | 3
38959.5266 | 3 | 2 | 3
38959.5271 | 3 | 2 | 3
38959.5276 | 4 | 2 | 3
38959.528 | 8 | 2 | 3
38959.5285 | 19 | 1 | 3
38959.529 | 37 | 2 | 3
38959.5295 | 60 | 1 | 3
38959.53 | 89 | 2 | 3
38959.5305 | 131 | 2 | 3
38959.531 | 169 | 1 | 3
38959.5314 | 1794 | 0 | 3
38959.5319 | 1894 | 0 | 3
38959.5324 | 1779 | 0 | 3
38959.5329 | 2220 | 0 | 3
38959.5334 | 2299 | 0 | 3
38959.5339 | 2211 | 0 | 3
38959.5344 | 1949 | 0 | 3
38959.5348 | 1927 | 0 | 3
3
38959.496 | 1 | 0 | 4
38959.4965 | 1 | 0 | 4
38959.497 | 1 | 0 | 4
38959.4974 | 1 | 0 | 4
38959.4979 | 1 | 0 | 4
38959.4984 | 1 | 0 | 4
38959.4989 | 1 | 0 | 4
38959.4994 | 1 | 0 | 4
38959.4999 | 1 | 0 | 4
38959.5004 | 1 | 0 | 4
38959.5008 | 1 | 0 | 4
38959.5013 | 1 | 0 | 4
38959.5018 | 1 | 0 | 4
38959.5023 | 1 | 0 | 4
38959.5028 | 1 | 0 | 4
38959.5033 | 1 | 0 | 4
38959.5038 | 1 | 0 | 4
38959.5042 | 1 | 0 | 4
38959.5047 | 1 | 0 | 4
38959.5052 | 1 | 0 | 4
38959.5057 | 1 | 0 | 4
38959.5062 | 2 | 0 | 4
38959.5067 | 1 | 0 | 4
38959.5072 | 1 | 0 | 4
38959.5077 | 1 | 0 | 4
38959.5081 | 1 | 0 | 4
38959.5086 | 1 | 0 | 4
38959.5091 | 1 | 0 | 4
38959.5096 | 1 | 0 | 4
38959.5101 | 1 | 0 | 4
38959.5106 | 1 | 0 | 4
38959.5111 | 1 | 0 | 4
38959.5115 | 1 | 0 | 4
38959.512 | 1 | 0 | 4
38959.5125 | 1 | 0 | 4
38959.513 | 2 | 1 | 4
38959.5135 | 2 | 0 | 4
38959.514 | 2 | 0 | 4
38959.5145 | 2 | 0 | 4
38959.5149 | 2 | 0 | 4
38959.5154 | 3 | 0 | 4
38959.5159 | 2 | 0 | 4
38959.5164 | 1077 | 0 | 4
38959.5169 | 2092 | 0 | 4
38959.5174 | 2303 | 0 | 4
38959.5179 | 1996 | 1 | 4
38959.5183 | 2153 | 1 | 4
38959.5188 | 1942 | 1 | 4
38959.5193 | 1978 | 1 | 4
38959.5198 | 1964 | 1 | 4
38959.5203 | 2341 | 1 | 4
38959.5208 | 1986 | 1 | 4
38959.5213 | 2289 | 1 | 4
38959.5217 | 2061 | 1 | 4
38959.5222 | 2208 | 1 | 4
38959.5227 | 1893 | 1 | 4
38959.5232 | 2364 | 1 | 4
38959.5237 | 2440 | 1 | 4
38959.5242 | 1899 | 1 | 4
38959.5247 | 1965 | 1 | 4
38959.5252 | 1997 | 2 | 4
38959.5256 | 1989 | 1 | 4
38959.5261 | 2362 | 1 | 4
38959.5266 | 2181 | 1 | 4
38959.5271 | 1984 | 1 | 4
38959.5276 | 2397 | 1 | 4
38959.5281 | 2391 | 1 | 4
38959.5285 | 2238 | 1 | 4
38959.529 | 2446 | 1 | 4
38959.5295 | 2274 | 1 | 4
38959.53 | 2126 | 1 | 4
38959.5305 | 2074 | 1 | 4
38959.531 | 2200 | 1 | 4
38959.5315 | 1912 | 0 | 4
38959.5319 | 2193 | 0 | 4
38959.5324 | 2030 | 0 | 4
38959.5329 | 2335 | 0 | 4
38959.5334 | 2320 | 0 | 4
38959.5339 | 2452 | 0 | 4
38959.5344 | 2468 | 0 | 4
38959.5349 | 2421 | 0 | 4
4
38959.496 | 1 | 0 | 5
38959.4965 | 1 | 0 | 5
38959.497 | 1 | 0 | 5
38959.4975 | 1 | 0 | 5
38959.4979 | 1 | 0 | 5
38959.4984 | 1 | 0 | 5
38959.4989 | 1 | 0 | 5
38959.4994 | 1 | 0 | 5
38959.4999 | 1 | 0 | 5
38959.5004 | 1 | 0 | 5
38959.5009 | 1 | 0 | 5
38959.5013 | 1 | 0 | 5
38959.5018 | 1 | 0 | 5
38959.5023 | 1 | 0 | 5
38959.5028 | 1 | 0 | 5
38959.5033 | 1 | 0 | 5
38959.5038 | 1 | 0 | 5
38959.5043 | 1 | 0 | 5
38959.5047 | 1 | 0 | 5
38959.5052 | 1 | 0 | 5
38959.5057 | 1 | 0 | 5
38959.5062 | 1 | 0 | 5
38959.5067 | 1 | 0 | 5
38959.5072 | 1 | 0 | 5
38959.5077 | 1 | 0 | 5
38959.5081 | 1 | 0 | 5
38959.5086 | 2 | 0 | 5
38959.5091 | 1 | 0 | 5
38959.5096 | 1 | 0 | 5
38959.5101 | 1 | 0 | 5
38959.5106 | 1 | 0 | 5
38959.5111 | 1 | 0 | 5
38959.5116 | 1 | 0 | 5
38959.512 | 1 | 0 | 5
38959.5125 | 1 | 0 | 5
38959.513 | 2 | 0 | 5
38959.5135 | 2 | 0 | 5
38959.514 | 2 | 0 | 5
38959.5145 | 2 | 0 | 5
38959.515 | 2 | 0 | 5
38959.5154 | 2 | 0 | 5
38959.5159 | 2 | 0 | 5
38959.5164 | 2 | 0 | 5
38959.5169 | 3 | 0 | 5
38959.5174 | 3 | 0 | 5
38959.5179 | 3 | 0 | 5
38959.5184 | 3 | 0 | 5
38959.5188 | 2 | 1 | 5
38959.5193 | 3 | 1 | 5
38959.5198 | 3 | 1 | 5
38959.5203 | 3 | 1 | 5
38959.5208 | 3 | 1 | 5
38959.5213 | 3 | 0 | 5
38959.5218 | 3 | 1 | 5
38959.5222 | 2 | 1 | 5
38959.5227 | 3 | 0 | 5
38959.5232 | 3 | 1 | 5
38959.5237 | 3 | 1 | 5
38959.5242 | 2 | 0 | 5
38959.5247 | 3 | 0 | 5
38959.5252 | 3 | 0 | 5
38959.5256 | 2 | 0 | 5
38959.5261 | 2 | 1 | 5
38959.5266 | 3 | 1 | 5
38959.5271 | 3 | 0 | 5
38959.5276 | 4 | 0 | 5
38959.5281 | 8 | 0 | 5
38959.5286 | 20 | 0 | 5
38959.5291 | 41 | 0 | 5
38959.5295 | 78 | 1 | 5
38959.53 | 93 | 0 | 5
38959.5305 | 125 | 0 | 5
38959.531 | 179 | 0 | 5
38959.5315 | 1840 | 2 | 5
38959.532 | 2205 | 2 | 5
38959.5325 | 1811 | 2 | 5
38959.5329 | 2056 | 2 | 5
38959.5334 | 1919 | 2 | 5
38959.5339 | 1823 | 2 | 5
38959.5344 | 2251 | 3 | 5
38959.5349 | 2034 | 4 | 5
5
38959.496 | 1 | 0 | 6
38959.4965 | 1 | 0 | 6
38959.497 | 1 | 0 | 6
38959.4975 | 1 | 0 | 6
38959.498 | 1 | 0 | 6
38959.4984 | 1 | 0 | 6
38959.4989 | 1 | 0 | 6
38959.4994 | 1 | 0 | 6
38959.4999 | 1 | 0 | 6
38959.5004 | 1 | 0 | 6
38959.5009 | 1 | 0 | 6
38959.5014 | 1 | 0 | 6
38959.5019 | 1 | 0 | 6
38959.5023 | 1 | 0 | 6
38959.5028 | 1 | 0 | 6
38959.5033 | 1 | 0 | 6
38959.5038 | 1 | 0 | 6
38959.5043 | 1 | 0 | 6
38959.5048 | 1 | 0 | 6
38959.5053 | 1 | 0 | 6
38959.5057 | 1 | 0 | 6
38959.5062 | 1 | 0 | 6
38959.5067 | 1 | 0 | 6
38959.5072 | 1 | 0 | 6
38959.5077 | 1 | 0 | 6
38959.5082 | 1 | 0 | 6
38959.5086 | 1 | 0 | 6
38959.5091 | 1 | 0 | 6
38959.5096 | 1 | 0 | 6
38959.5101 | 1 | 0 | 6
38959.5106 | 1 | 0 | 6
38959.5111 | 1 | 0 | 6
38959.5116 | 1 | 0 | 6
38959.512 | 1 | 0 | 6
38959.5125 | 1 | 0 | 6
38959.513 | 2 | 0 | 6
38959.5135 | 2 | 0 | 6
38959.514 | 2 | 0 | 6
38959.5145 | 3 | 0 | 6
38959.515 | 2 | 0 | 6
38959.5155 | 2 | 0 | 6
38959.5159 | 2 | 0 | 6
38959.5164 | 599 | 0 | 6
38959.5169 | 1112 | 0 | 6
38959.5174 | 972 | 0 | 6
38959.5179 | 1168 | 0 | 6
38959.5184 | 2153 | 0 | 6
38959.5189 | 1907 | 0 | 6
38959.5193 | 2189 | 0 | 6
38959.5198 | 1812 | 0 | 6
38959.5203 | 1840 | 0 | 6
38959.5208 | 2264 | 0 | 6
38959.5213 | 2005 | 1 | 6
38959.5218 | 2358 | 0 | 6
38959.5223 | 2143 | 1 | 6
38959.5227 | 2130 | 1 | 6
38959.5232 | 2323 | 0 | 6
38959.5237 | 2132 | 0 | 6
38959.5242 | 2103 | 0 | 6
38959.5247 | 1994 | 1 | 6
38959.5252 | 2281 | 0 | 6
38959.5257 | 2222 | 0 | 6
38959.5261 | 2063 | 0 | 6
38959.5266 | 2279 | 0 | 6
38959.5271 | 2109 | 0 | 6
38959.5276 | 1913 | 0 | 6
38959.5281 | 2073 | 0 | 6
38959.5286 | 1938 | 1 | 6
38959.5291 | 2373 | 0 | 6
38959.5295 | 2134 | 0 | 6
38959.53 | 2378 | 0 | 6
38959.5305 | 2309 | 0 | 6
38959.531 | 2429 | 0 | 6
38959.5315 | 2369 | 1 | 6
38959.532 | 2212 | 2 | 6
38959.5325 | 2090 | 1 | 6
38959.533 | 2304 | 2 | 6
38959.5334 | 1961 | 2 | 6
38959.5339 | 1897 | 2 | 6
38959.5344 | 2150 | 3 | 6
38959.5349 | 1958 | 3 | 6
6
38959.496 | 1 | 0 | 7
38959.4965 | 1 | 0 | 7
38959.497 | 1 | 0 | 7
38959.4975 | 1 | 0 | 7
38959.498 | 1 | 0 | 7
38959.4985 | 1 | 0 | 7
38959.4989 | 1 | 0 | 7
38959.4994 | 1 | 0 | 7
38959.4999 | 1 | 0 | 7
38959.5004 | 1 | 0 | 7
38959.5009 | 1 | 0 | 7
38959.5014 | 1 | 0 | 7
38959.5019 | 1 | 0 | 7
38959.5023 | 1 | 0 | 7
38959.5028 | 1 | 0 | 7
38959.5033 | 1 | 0 | 7
38959.5038 | 1 | 0 | 7
38959.5043 | 1 | 0 | 7
38959.5048 | 1 | 0 | 7
38959.5053 | 1 | 0 | 7
38959.5058 | 1 | 0 | 7
38959.5062 | 1 | 0 | 7
38959.5067 | 1 | 0 | 7
38959.5072 | 1 | 0 | 7
38959.5077 | 1 | 0 | 7
38959.5082 | 1 | 0 | 7
38959.5087 | 1 | 0 | 7
38959.5092 | 1 | 0 | 7
38959.5096 | 1 | 0 | 7
38959.5101 | 1 | 0 | 7
38959.5106 | 1 | 0 | 7
38959.5111 | 1 | 0 | 7
38959.5116 | 1 | 0 | 7
38959.5121 | 1 | 0 | 7
38959.5126 | 1 | 0 | 7
38959.513 | 2 | 0 | 7
38959.5135 | 2 | 0 | 7
38959.514 | 2 | 0 | 7
38959.5145 | 3 | 0 | 7
38959.515 | 2 | 0 | 7
38959.5155 | 2 | 0 | 7
38959.516 | 2 | 0 | 7
38959.5164 | 2 | 0 | 7
38959.5169 | 3 | 0 | 7
38959.5174 | 3 | 0 | 7
38959.5179 | 3 | 0 | 7
38959.5184 | 2 | 0 | 7
38959.5189 | 3 | 0 | 7
38959.5194 | 3 | 1 | 7
38959.5198 | 3 | 0 | 7
38959.5203 | 2 | 0 | 7
38959.5208 | 3 | 0 | 7
38959.5213 | 3 | 0 | 7
38959.5218 | 2 | 0 | 7
38959.5223 | 3 | 0 | 7
38959.5228 | 3 | 0 | 7
38959.5233 | 2 | 0 | 7
38959.5237 | 3 | 0 | 7
38959.5242 | 2 | 0 | 7
38959.5247 | 2 | 0 | 7
38959.5252 | 3 | 0 | 7
38959.5257 | 3 | 0 | 7
38959.5262 | 3 | 0 | 7
38959.5267 | 3 | 0 | 7
38959.5271 | 3 | 0 | 7
38959.5276 | 4 | 0 | 7
38959.5281 | 9 | 0 | 7
38959.5286 | 23 | 0 | 7
38959.5291 | 41 | 0 | 7
38959.5296 | 73 | 0 | 7
38959.5301 | 115 | 0 | 7
38959.5305 | 125 | 0 | 7
38959.531 | 184 | 0 | 7
38959.5315 | 2077 | 0 | 7
38959.532 | 1941 | 0 | 7
38959.5325 | 2026 | 0 | 7
38959.533 | 2293 | 0 | 7
38959.5335 | 2183 | 0 | 7
38959.5339 | 1851 | 0 | 7
38959.5344 | 2008 | 0 | 7
38959.5349 | 1997 | 0 | 7
7
38959.496 | 1 | 0 | 8
38959.4965 | 1 | 0 | 8
38959.497 | 1 | 0 | 8
38959.4975 | 1 | 0 | 8
38959.498 | 1 | 0 | 8
38959.4985 | 1 | 0 | 8
38959.499 | 1 | 0 | 8
38959.4994 | 1 | 0 | 8
38959.4999 | 1 | 0 | 8
38959.5004 | 1 | 0 | 8
38959.5009 | 1 | 0 | 8
38959.5014 | 1 | 0 | 8
38959.5019 | 1 | 0 | 8
38959.5024 | 1 | 0 | 8
38959.5028 | 1 | 0 | 8
38959.5033 | 1 | 0 | 8
38959.5038 | 1 | 0 | 8
38959.5043 | 1 | 0 | 8
38959.5048 | 1 | 0 | 8
38959.5053 | 1 | 0 | 8
38959.5058 | 1 | 0 | 8
38959.5062 | 1 | 0 | 8
38959.5067 | 1 | 0 | 8
38959.5072 | 1 | 0 | 8
38959.5077 | 1 | 0 | 8
38959.5082 | 1 | 0 | 8
38959.5087 | 1 | 0 | 8
38959.5092 | 1 | 0 | 8
38959.5097 | 1 | 0 | 8
38959.5101 | 1 | 0 | 8
38959.5106 | 1 | 0 | 8
38959.5111 | 1 | 0 | 8
38959.5116 | 1 | 0 | 8
38959.5121 | 1 | 0 | 8
38959.5126 | 1850 | 0 | 8
38959.5131 | 1950 | 0 | 8
38959.5135 | 2459 | 0 | 8
38959.514 | 1601 | 0 | 8
38959.5145 | 2338 | 0 | 8
38959.515 | 2310 | 0 | 8
38959.5155 | 2423 | 0 | 8
38959.516 | 2399 | 0 | 8
38959.5165 | 2469 | 0 | 8
38959.5169 | 2460 | 0 | 8
38959.5174 | 2218 | 0 | 8
38959.5179 | 2092 | 0 | 8
38959.5184 | 2070 | 0 | 8
38959.5189 | 2403 | 0 | 8
38959.5194 | 2061 | 0 | 8
38959.5199 | 1980 | 0 | 8
38959.5203 | 2356 | 0 | 8
38959.5208 | 2403 | 0 | 8
38959.5213 | 2182 | 0 | 8
38959.5218 | 2041 | 0 | 8
38959.5223 | 2232 | 0 | 8
38959.5228 | 2257 | 0 | 8
38959.5233 | 1984 | 0 | 8
38959.5238 | 1996 | 0 | 8
38959.5242 | 1926 | 0 | 8
38959.5247 | 2203 | 0 | 8
38959.5252 | 2156 | 0 | 8
38959.5257 | 2003 | 0 | 8
38959.5262 | 1972 | 0 | 8
38959.5267 | 2453 | 0 | 8
38959.5272 | 2143 | 0 | 8
38959.5276 | 1999 | 0 | 8
38959.5281 | 1935 | 0 | 8
38959.5286 | 1928 | 0 | 8
38959.5291 | 2135 | 0 | 8
38959.5296 | 2248 | 0 | 8
38959.5301 | 2194 | 0 | 8
38959.5306 | 1971 | 0 | 8
38959.531 | 1992 | 0 | 8
38959.5315 | 2435 | 0 | 8
38959.532 | 2294 | 0 | 8
38959.5325 | 2415 | 0 | 8
38959.533 | 1959 | 0 | 8
38959.5335 | 2258 | 0 | 8
38959.534 | 1927 | 0 | 8
38959.5344 | 1997 | 0 | 8
38959.5349 | 2376 | 0 | 8
8
38959.4961 | 1 | 0 | 9
38959.4966 | 1 | 0 | 9
38959.497 | 1 | 0 | 9
38959.4975 | 1 | 0 | 9
38959.498 | 1 | 0 | 9
38959.4985 | 1 | 0 | 9
38959.499 | 1 | 0 | 9
38959.4995 | 1 | 0 | 9
38959.5 | 1 | 0 | 9
38959.5004 | 1 | 0 | 9
38959.5009 | 1 | 0 | 9
38959.5014 | 1 | 0 | 9
38959.5019 | 1 | 0 | 9
38959.5024 | 1 | 0 | 9
38959.5029 | 1 | 0 | 9
38959.5034 | 1 | 0 | 9
38959.5038 | 1 | 0 | 9
38959.5043 | 1 | 0 | 9
38959.5048 | 1 | 0 | 9
38959.5053 | 1 | 0 | 9
38959.5058 | 1 | 0 | 9
38959.5063 | 1 | 0 | 9
38959.5068 | 1 | 0 | 9
38959.5072 | 1 | 0 | 9
38959.5077 | 1 | 0 | 9
38959.5082 | 1 | 0 | 9
38959.5087 | 1 | 0 | 9
38959.5092 | 1 | 0 | 9
38959.5097 | 1 | 0 | 9
38959.5102 | 1 | 0 | 9
38959.5106 | 1 | 0 | 9
38959.5111 | 1 | 0 | 9
38959.5116 | 1 | 0 | 9
38959.5121 | 1 | 0 | 9
38959.5126 | 2 | 0 | 9
38959.5131 | 3 | 0 | 9
38959.5136 | 3 | 0 | 9
38959.5141 | 3 | 0 | 9
38959.5145 | 3 | 0 | 9
38959.515 | 3 | 0 | 9
38959.5155 | 3 | 0 | 9
38959.516 | 3 | 0 | 9
38959.5165 | 3 | 0 | 9
38959.517 | 3 | 0 | 9
38959.5175 | 3 | 0 | 9
38959.5179 | 2 | 0 | 9
38959.5184 | 3 | 0 | 9
38959.5189 | 3 | 0 | 9
38959.5194 | 3 | 0 | 9
38959.5199 | 3 | 0 | 9
38959.5204 | 2 | 0 | 9
38959.5209 | 3 | 0 | 9
38959.5213 | 2 | 0 | 9
38959.5218 | 3 | 0 | 9
38959.5223 | 2 | 0 | 9
38959.5228 | 2 | 1 | 9
38959.5233 | 2 | 0 | 9
38959.5238 | 2 | 0 | 9
38959.5242 | 2 | 0 | 9
38959.5247 | 3 | 0 | 9
38959.5252 | 3 | 0 | 9
38959.5257 | 2 | 0 | 9
38959.5262 | 3 | 0 | 9
38959.5267 | 2 | 0 | 9
38959.5272 | 3 | 1 | 9
38959.5277 | 5 | 0 | 9
38959.5281 | 9 | 0 | 9
38959.5286 | 25 | 0 | 9
38959.5291 | 47 | 0 | 9
38959.5296 | 79 | 0 | 9
38959.5301 | 104 | 0 | 9
38959.5306 | 129 | 0 | 9
38959.5311 | 186 | 0 | 9
38959.5315 | 2176 | 0 | 9
38959.532 | 1963 | 0 | 9
38959.5325 | 1892 | 0 | 9
38959.533 | 2289 | 0 | 9
38959.5335 | 2022 | 0 | 9
38959.534 | 1855 | 0 | 9
38959.5345 | 2120 | 0 | 9
38959.5349 | 1843 | 0 | 9
9
38959.4961 | 1 | 0 | 10
38959.4966 | 1 | 0 | 10
38959.497 | 1 | 0 | 10
38959.4975 | 1 | 0 | 10
38959.498 | 1 | 0 | 10
38959.4985 | 1 | 0 | 10
38959.499 | 1 | 0 | 10
38959.4995 | 1 | 0 | 10
38959.5 | 1 | 0 | 10
38959.5005 | 1 | 0 | 10
38959.5009 | 1 | 0 | 10
38959.5014 | 1 | 0 | 10
38959.5019 | 1 | 0 | 10
38959.5024 | 1 | 0 | 10
38959.5029 | 1 | 0 | 10
38959.5034 | 1 | 0 | 10
38959.5039 | 1 | 0 | 10
38959.5043 | 1 | 0 | 10
38959.5048 | 1 | 0 | 10
38959.5053 | 1 | 0 | 10
38959.5058 | 1 | 0 | 10
38959.5063 | 1 | 0 | 10
38959.5068 | 1 | 0 | 10
38959.5073 | 1 | 0 | 10
38959.5077 | 1 | 0 | 10
38959.5082 | 1 | 0 | 10
38959.5087 | 1 | 0 | 10
38959.5092 | 1 | 0 | 10
38959.5097 | 1 | 0 | 10
38959.5102 | 1 | 0 | 10
38959.5107 | 1 | 0 | 10
38959.5111 | 1 | 0 | 10
38959.5116 | 1 | 0 | 10
38959.5126 | 1481 | 0 | 10
38959.5131 | 1947 | 0 | 10
38959.5136 | 1919 | 0 | 10
38959.5141 | 1947 | 0 | 10
38959.5145 | 2280 | 0 | 10
38959.515 | 1949 | 0 | 10
38959.5155 | 2384 | 0 | 10
38959.516 | 2063 | 0 | 10
38959.5165 | 1985 | 0 | 10
38959.5175 | 1925 | 0 | 10
38959.518 | 2421 | 0 | 10
38959.5184 | 2405 | 0 | 10
38959.5189 | 2091 | 0 | 10
38959.5194 | 2069 | 1 | 10
38959.5199 | 2385 | 0 | 10
38959.5204 | 2249 | 0 | 10
38959.5209 | 2402 | 0 | 10
38959.5214 | 2344 | 0 | 10
38959.5218 | 2244 | 0 | 10
38959.5223 | 2204 | 0 | 10
38959.5228 | 2380 | 0 | 10
38959.5233 | 2030 | 0 | 10
38959.5238 | 2337 | 0 | 10
38959.5243 | 1989 | 0 | 10
38959.5248 | 2453 | 0 | 10
38959.5252 | 2339 | 0 | 10
38959.5257 | 2445 | 0 | 10
38959.5262 | 2394 | 0 | 10
38959.5267 | 2256 | 0 | 10
38959.5272 | 2372 | 0 | 10
38959.5277 | 2455 | 0 | 10
38959.5282 | 2350 | 0 | 10
38959.5286 | 2121 | 0 | 10
38959.5291 | 2388 | 0 | 10
38959.5296 | 2466 | 0 | 10
38959.5301 | 2275 | 0 | 10
38959.5306 | 2254 | 0 | 10
38959.5311 | 2242 | 0 | 10
38959.5316 | 2112 | 0 | 10
38959.532 | 2337 | 0 | 10
38959.5325 | 2442 | 0 | 10
38959.533 | 2007 | 0 | 10
38959.5335 | 1918 | 0 | 10
38959.534 | 2362 | 0 | 10
38959.5345 | 1972 | 0 | 10
38959.535 | 2399 | 0 | 10
10
38959.4961 | 1 | 0 | 11
38959.4966 | 1 | 0 | 11
38959.4971 | 1 | 0 | 11
38959.4976 | 1 | 0 | 11
38959.498 | 1 | 0 | 11
38959.4985 | 1 | 0 | 11
38959.499 | 1 | 0 | 11
38959.4995 | 1 | 0 | 11
38959.5 | 1 | 0 | 11
38959.5005 | 1 | 0 | 11
38959.501 | 1 | 0 | 11
38959.5014 | 1 | 0 | 11
38959.5019 | 1 | 0 | 11
38959.5024 | 1 | 0 | 11
38959.5029 | 1 | 0 | 11
38959.5034 | 1 | 0 | 11
38959.5039 | 1 | 0 | 11
38959.5044 | 1 | 0 | 11
38959.5048 | 1 | 0 | 11
38959.5053 | 1 | 0 | 11
38959.5058 | 1 | 0 | 11
38959.5063 | 1 | 0 | 11
38959.5068 | 1 | 0 | 11
38959.5073 | 1 | 0 | 11
38959.5078 | 1 | 0 | 11
38959.5082 | 1 | 0 | 11
38959.5087 | 1 | 0 | 11
38959.5092 | 1 | 0 | 11
38959.5097 | 1 | 0 | 11
38959.5102 | 1 | 0 | 11
38959.5107 | 1 | 0 | 11
38959.5112 | 1 | 0 | 11
38959.5116 | 1 | 0 | 11
38959.5121 | 1 | 0 | 11
38959.5126 | 2 | 0 | 11
38959.5131 | 3 | 0 | 11
38959.5136 | 3 | 0 | 11
38959.5141 | 3 | 0 | 11
38959.5146 | 3 | 0 | 11
38959.515 | 3 | 0 | 11
38959.5155 | 3 | 0 | 11
38959.516 | 3 | 0 | 11
38959.5165 | 3 | 0 | 11
38959.517 | 3 | 0 | 11
38959.5175 | 2 | 0 | 11
38959.518 | 3 | 0 | 11
38959.5184 | 2 | 0 | 11
38959.5189 | 3 | 0 | 11
38959.5194 | 3 | 0 | 11
38959.5199 | 3 | 0 | 11
38959.5204 | 3 | 0 | 11
38959.5209 | 3 | 0 | 11
38959.5214 | 3 | 0 | 11
38959.5219 | 3 | 0 | 11
38959.5223 | 3 | 0 | 11
38959.5228 | 3 | 0 | 11
38959.5233 | 2 | 0 | 11
38959.5238 | 2 | 0 | 11
38959.5243 | 2 | 0 | 11
38959.5248 | 2 | 0 | 11
38959.5253 | 3 | 0 | 11
38959.5257 | 2 | 0 | 11
38959.5262 | 3 | 0 | 11
38959.5267 | 3 | 0 | 11
38959.5272 | 3 | 0 | 11
38959.5277 | 5 | 0 | 11
38959.5282 | 11 | 0 | 11
38959.5287 | 25 | 0 | 11
38959.5291 | 53 | 0 | 11
38959.5296 | 77 | 0 | 11
38959.5301 | 124 | 0 | 11
38959.5306 | 143 | 0 | 11
38959.5311 | 208 | 0 | 11
38959.5316 | 1803 | 0 | 11
38959.5321 | 2216 | 0 | 11
38959.5325 | 1983 | 0 | 11
38959.533 | 2301 | 0 | 11
38959.5335 | 2005 | 0 | 11
38959.534 | 1850 | 0 | 11
38959.5345 | 2039 | 0 | 11
38959.535 | 1882 | 0 | 11
11
38959.4961 | 1 | 0 | 12
38959.4966 | 1 | 0 | 12
38959.4971 | 1 | 0 | 12
38959.4976 | 1 | 0 | 12
38959.4981 | 1 | 0 | 12
38959.4985 | 1 | 0 | 12
38959.499 | 1 | 0 | 12
38959.4995 | 1 | 0 | 12
38959.5 | 1 | 0 | 12
38959.5005 | 1 | 0 | 12
38959.501 | 1 | 0 | 12
38959.5015 | 1 | 0 | 12
38959.5019 | 1 | 0 | 12
38959.5024 | 1 | 0 | 12
38959.5029 | 1 | 0 | 12
38959.5034 | 1 | 0 | 12
38959.5039 | 1 | 0 | 12
38959.5044 | 1 | 0 | 12
38959.5049 | 1 | 0 | 12
38959.5053 | 1 | 0 | 12
38959.5058 | 1 | 0 | 12
38959.5063 | 1 | 0 | 12
38959.5068 | 1 | 0 | 12
38959.5073 | 1 | 0 | 12
38959.5078 | 1 | 0 | 12
38959.5083 | 1 | 0 | 12
38959.5088 | 1 | 0 | 12
38959.5092 | 1 | 0 | 12
38959.5097 | 1 | 0 | 12
38959.5102 | 1 | 0 | 12
38959.5107 | 1 | 0 | 12
38959.5112 | 1 | 0 | 12
38959.5117 | 1 | 0 | 12
38959.5122 | 1 | 0 | 12
38959.5126 | 1 | 0 | 12
38959.5131 | 2 | 1 | 12
38959.5136 | 2 | 0 | 12
38959.5141 | 2 | 0 | 12
38959.5146 | 3 | 0 | 12
38959.5151 | 2 | 0 | 12
38959.5156 | 2 | 0 | 12
38959.516 | 3 | 0 | 12
38959.5165 | 965 | 0 | 12
38959.517 | 2087 | 0 | 12
38959.5175 | 1963 | 0 | 12
38959.518 | 2237 | 0 | 12
38959.5185 | 1979 | 0 | 12
38959.519 | 2358 | 0 | 12
38959.5194 | 2174 | 0 | 12
38959.5199 | 2030 | 0 | 12
38959.5204 | 2329 | 0 | 12
38959.5209 | 2032 | 0 | 12
38959.5214 | 2325 | 0 | 12
38959.5219 | 1992 | 0 | 12
38959.5224 | 1896 | 0 | 12
38959.5228 | 2285 | 0 | 12
38959.5233 | 2311 | 0 | 12
38959.5238 | 1942 | 0 | 12
38959.5243 | 1948 | 0 | 12
38959.5248 | 2180 | 0 | 12
38959.5253 | 2184 | 0 | 12
38959.5258 | 2430 | 0 | 12
38959.5263 | 1981 | 0 | 12
38959.5267 | 2109 | 0 | 12
38959.5272 | 2237 | 0 | 12
38959.5277 | 1996 | 0 | 12
38959.5282 | 1996 | 0 | 12
38959.5287 | 2164 | 0 | 12
38959.5292 | 2216 | 0 | 12
38959.5297 | 1919 | 0 | 12
38959.5301 | 1919 | 0 | 12
38959.5306 | 1911 | 0 | 12
38959.5311 | 2366 | 0 | 12
38959.5316 | 2408 | 0 | 12
38959.5321 | 2022 | 0 | 12
38959.5326 | 2438 | 0 | 12
38959.5331 | 2352 | 0 | 12
38959.5335 | 2299 | 0 | 12
38959.534 | 2221 | 0 | 12
38959.5345 | 2459 | 0 | 12
38959.535 | 2290 | 0 | 12
12
38959.4961 | 1 | 0 | 13
38959.4966 | 1 | 0 | 13
38959.4971 | 1 | 0 | 13
38959.4976 | 1 | 0 | 13
38959.4981 | 1 | 0 | 13
38959.4986 | 1 | 0 | 13
38959.499 | 1 | 0 | 13
38959.4995 | 1 | 0 | 13
38959.5 | 1 | 0 | 13
38959.5005 | 1 | 0 | 13
38959.501 | 1 | 0 | 13
38959.5015 | 1 | 0 | 13
38959.502 | 1 | 0 | 13
38959.5024 | 1 | 0 | 13
38959.5029 | 1 | 0 | 13
38959.5034 | 1 | 0 | 13
38959.5039 | 1 | 0 | 13
38959.5044 | 1 | 0 | 13
38959.5049 | 1 | 0 | 13
38959.5054 | 1 | 0 | 13
38959.5058 | 1 | 0 | 13
38959.5063 | 1 | 0 | 13
38959.5068 | 1 | 0 | 13
38959.5073 | 1 | 0 | 13
38959.5078 | 1 | 0 | 13
38959.5083 | 1 | 0 | 13
38959.5088 | 1 | 0 | 13
38959.5092 | 1 | 0 | 13
38959.5097 | 1 | 0 | 13
38959.5102 | 1 | 0 | 13
38959.5107 | 1 | 0 | 13
38959.5112 | 1 | 0 | 13
38959.5117 | 1 | 0 | 13
38959.5122 | 1 | 0 | 13
38959.5127 | 2 | 0 | 13
38959.5131 | 2 | 0 | 13
38959.5136 | 2 | 0 | 13
38959.5141 | 2 | 0 | 13
38959.5146 | 2 | 0 | 13
38959.5151 | 2 | 0 | 13
38959.5156 | 2 | 0 | 13
38959.5161 | 2 | 0 | 13
38959.5165 | 3 | 0 | 13
38959.517 | 3 | 0 | 13
38959.5175 | 3 | 0 | 13
38959.518 | 3 | 0 | 13
38959.5185 | 3 | 0 | 13
38959.519 | 3 | 0 | 13
38959.5195 | 3 | 0 | 13
38959.5199 | 3 | 0 | 13
38959.5204 | 2 | 0 | 13
38959.5209 | 3 | 0 | 13
38959.5214 | 3 | 0 | 13
38959.5219 | 3 | 0 | 13
38959.5224 | 2 | 0 | 13
38959.5229 | 2 | 0 | 13
38959.5233 | 2 | 0 | 13
38959.5238 | 3 | 0 | 13
38959.5243 | 2 | 0 | 13
38959.5248 | 2 | 0 | 13
38959.5253 | 3 | 0 | 13
38959.5258 | 2 | 0 | 13
38959.5263 | 2 | 0 | 13
38959.5267 | 3 | 0 | 13
38959.5272 | 3 | 0 | 13
38959.5277 | 5 | 0 | 13
38959.5282 | 11 | 0 | 13
38959.5287 | 28 | 0 | 13
38959.5292 | 51 | 0 | 13
38959.5297 | 82 | 0 | 13
38959.5302 | 113 | 0 | 13
38959.5306 | 170 | 0 | 13
38959.5311 | 212 | 0 | 13
38959.5316 | 1750 | 2 | 13
38959.5321 | 2264 | 2 | 13
38959.5326 | 1903 | 2 | 13
38959.5331 | 2268 | 2 | 13
38959.5336 | 2055 | 3 | 13
38959.534 | 1955 | 3 | 13
38959.5345 | 2219 | 3 | 13
38959.535 | 1886 | 4 | 13
13
38959.4961 | 1 | 0 | 14
38959.4966 | 1 | 0 | 14
38959.4971 | 1 | 0 | 14
38959.4976 | 1 | 0 | 14
38959.4981 | 1 | 0 | 14
38959.4986 | 1 | 0 | 14
38959.4991 | 1 | 0 | 14
38959.4995 | 1 | 0 | 14
38959.5 | 1 | 0 | 14
38959.5005 | 1 | 0 | 14
38959.501 | 1 | 0 | 14
38959.5015 | 1 | 0 | 14
38959.502 | 1 | 0 | 14
38959.5025 | 1 | 0 | 14
38959.503 | 1 | 0 | 14
38959.5034 | 1 | 0 | 14
38959.5039 | 1 | 0 | 14
38959.5044 | 1 | 0 | 14
38959.5049 | 1 | 0 | 14
38959.5054 | 1 | 0 | 14
38959.5059 | 1 | 0 | 14
38959.5064 | 1 | 0 | 14
38959.5068 | 1 | 0 | 14
38959.5073 | 1 | 0 | 14
38959.5078 | 1 | 0 | 14
38959.5083 | 1 | 0 | 14
38959.5088 | 1 | 0 | 14
38959.5093 | 1 | 0 | 14
38959.5098 | 1 | 0 | 14
38959.5102 | 1 | 0 | 14
38959.5107 | 1 | 0 | 14
38959.5112 | 1 | 0 | 14
38959.5117 | 1 | 0 | 14
38959.5122 | 1 | 0 | 14
38959.5127 | 2 | 0 | 14
38959.5132 | 2 | 0 | 14
38959.5136 | 2 | 0 | 14
38959.5141 | 2 | 1 | 14
38959.5146 | 2 | 0 | 14
38959.5151 | 2 | 0 | 14
38959.5156 | 2 | 0 | 14
38959.5161 | 2 | 0 | 14
38959.5166 | 2 | 0 | 14
38959.517 | 3 | 0 | 14
38959.5175 | 3 | 0 | 14
38959.518 | 2 | 0 | 14
38959.5185 | 3 | 0 | 14
38959.519 | 2 | 0 | 14
38959.5195 | 2 | 0 | 14
38959.52 | 2 | 0 | 14
38959.5205 | 2 | 0 | 14
38959.5209 | 2 | 0 | 14
38959.5214 | 2 | 0 | 14
38959.5219 | 2 | 0 | 14
38959.5224 | 2 | 0 | 14
38959.5229 | 2 | 0 | 14
38959.5234 | 2 | 0 | 14
38959.5239 | 2 | 0 | 14
38959.5243 | 2 | 0 | 14
38959.5248 | 2 | 0 | 14
38959.5253 | 2 | 0 | 14
38959.5258 | 2 | 0 | 14
38959.5263 | 2 | 0 | 14
38959.5268 | 2 | 0 | 14
38959.5272 | 3 | 0 | 14
38959.5277 | 5 | 0 | 14
38959.5282 | 13 | 0 | 14
38959.5287 | 24 | 0 | 14
38959.5292 | 45 | 0 | 14
38959.5297 | 93 | 0 | 14
38959.5302 | 124 | 0 | 14
38959.5307 | 148 | 0 | 14
38959.5311 | 231 | 0 | 14
38959.5316 | 2237 | 0 | 14
38959.5321 | 2106 | 0 | 14
38959.5326 | 1877 | 0 | 14
38959.5331 | 1996 | 0 | 14
38959.5336 | 2194 | 0 | 14
38959.5341 | 2008 | 0 | 14
38959.5345 | 1890 | 0 | 14
38959.535 | 1810 | 0 | 14
14
38959.4962 | 1 | 0 | 15
38959.4966 | 1 | 0 | 15
38959.4971 | 1 | 0 | 15
38959.4976 | 1 | 0 | 15
38959.4981 | 1 | 0 | 15
38959.4986 | 1 | 0 | 15
38959.4991 | 1 | 0 | 15
38959.4996 | 1 | 0 | 15
38959.5 | 1 | 0 | 15
38959.5005 | 1 | 0 | 15
38959.501 | 1 | 0 | 15
38959.5015 | 1 | 0 | 15
38959.502 | 1 | 0 | 15
38959.5025 | 1 | 0 | 15
38959.503 | 1 | 0 | 15
38959.5034 | 1 | 0 | 15
38959.5039 | 1 | 0 | 15
38959.5044 | 1 | 0 | 15
38959.5049 | 1 | 0 | 15
38959.5054 | 1 | 0 | 15
38959.5059 | 1 | 0 | 15
38959.5064 | 1 | 0 | 15
38959.5069 | 1 | 0 | 15
38959.5073 | 1 | 0 | 15
38959.5078 | 1 | 0 | 15
38959.5083 | 1 | 0 | 15
38959.5088 | 1 | 0 | 15
38959.5093 | 1 | 0 | 15
38959.5098 | 1 | 0 | 15
38959.5103 | 1 | 0 | 15
38959.5107 | 1 | 0 | 15
38959.5112 | 1 | 0 | 15
38959.5117 | 1 | 0 | 15
38959.5122 | 1 | 0 | 15
38959.5127 | 1 | 0 | 15
38959.5132 | 2 | 0 | 15
38959.5137 | 2 | 0 | 15
38959.5141 | 2 | 0 | 15
38959.5146 | 2 | 0 | 15
38959.5151 | 2 | 0 | 15
38959.5156 | 2 | 0 | 15
38959.5161 | 2 | 0 | 15
38959.5166 | 2 | 0 | 15
38959.5171 | 2 | 0 | 15
38959.5175 | 2 | 0 | 15
38959.518 | 2 | 0 | 15
38959.5185 | 2 | 0 | 15
38959.519 | 2 | 0 | 15
38959.5195 | 2 | 0 | 15
38959.52 | 3 | 0 | 15
38959.5205 | 3 | 0 | 15
38959.5209 | 2 | 0 | 15
38959.5214 | 2 | 0 | 15
38959.5219 | 3 | 0 | 15
38959.5224 | 2 | 0 | 15
38959.5229 | 2 | 0 | 15
38959.5234 | 2 | 0 | 15
38959.5239 | 2 | 0 | 15
38959.5244 | 2 | 0 | 15
38959.5248 | 2 | 0 | 15
38959.5253 | 2 | 0 | 15
38959.5258 | 2 | 0 | 15
38959.5263 | 2 | 0 | 15
38959.5268 | 2 | 0 | 15
38959.5273 | 3 | 0 | 15
38959.5278 | 4 | 0 | 15
38959.5282 | 13 | 0 | 15
38959.5287 | 22 | 0 | 15
38959.5292 | 47 | 0 | 15
38959.5297 | 88 | 0 | 15
38959.5302 | 110 | 0 | 15
38959.5307 | 185 | 0 | 15
38959.5312 | 1486 | 0 | 15
38959.5316 | 2118 | 0 | 15
38959.5321 | 2021 | 0 | 15
38959.5326 | 1854 | 0 | 15
38959.5331 | 2306 | 0 | 15
38959.5336 | 2182 | 0 | 15
38959.5341 | 2290 | 0 | 15
38959.5346 | 2050 | 0 | 15
38959.535 | 2035 | 0 | 15
15
38959.4962 | 1 | 0 | 16
38959.4967 | 1 | 0 | 16
38959.4972 | 1 | 0 | 16
38959.4976 | 1 | 0 | 16
38959.4981 | 1 | 0 | 16
38959.4986 | 1 | 0 | 16
38959.4991 | 1 | 0 | 16
38959.4996 | 1 | 0 | 16
38959.5001 | 1 | 0 | 16
38959.5006 | 1 | 0 | 16
38959.501 | 1 | 0 | 16
38959.5015 | 1 | 0 | 16
38959.502 | 1 | 0 | 16
38959.5025 | 1 | 0 | 16
38959.503 | 1 | 0 | 16
38959.5035 | 1 | 0 | 16
38959.504 | 1 | 0 | 16
38959.5044 | 1 | 0 | 16
38959.5049 | 1 | 0 | 16
38959.5054 | 1 | 0 | 16
38959.5059 | 1 | 0 | 16
38959.5064 | 1 | 0 | 16
38959.5069 | 1 | 0 | 16
38959.5074 | 1 | 0 | 16
38959.5078 | 1 | 0 | 16
38959.5083 | 1 | 0 | 16
38959.5088 | 1 | 0 | 16
38959.5093 | 1 | 0 | 16
38959.5098 | 1 | 0 | 16
38959.5103 | 1 | 0 | 16
38959.5108 | 1 | 0 | 16
38959.5113 | 1 | 0 | 16
38959.5117 | 1 | 0 | 16
38959.5122 | 1 | 0 | 16
38959.5127 | 2332 | 0 | 16
38959.5132 | 2403 | 0 | 16
38959.5137 | 2449 | 0 | 16
38959.5142 | 2339 | 0 | 16
38959.5146 | 2228 | 0 | 16
38959.5151 | 2430 | 0 | 16
38959.5156 | 2198 | 0 | 16
38959.5161 | 2333 | 0 | 16
38959.5166 | 2058 | 0 | 16
38959.5171 | 2376 | 0 | 16
38959.5176 | 2385 | 0 | 16
38959.518 | 1952 | 0 | 16
38959.5185 | 1921 | 0 | 16
38959.519 | 2460 | 0 | 16
38959.5195 | 2144 | 1 | 16
38959.52 | 2072 | 0 | 16
38959.5205 | 2255 | 0 | 16
38959.521 | 2475 | 1 | 16
38959.5214 | 2132 | 0 | 16
38959.5219 | 2313 | 0 | 16
38959.5224 | 2350 | 0 | 16
38959.5229 | 2086 | 0 | 16
38959.5234 | 2057 | 0 | 16
38959.5239 | 2314 | 0 | 16
38959.5244 | 2045 | 0 | 16
38959.5248 | 2235 | 0 | 16
38959.5253 | 2050 | 0 | 16
38959.5258 | 2134 | 0 | 16
38959.5263 | 2062 | 0 | 16
38959.5268 | 2235 | 0 | 16
38959.5273 | 2229 | 0 | 16
38959.5278 | 2420 | 0 | 16
38959.5283 | 2264 | 0 | 16
38959.5287 | 1985 | 0 | 16
38959.5292 | 2453 | 0 | 16
38959.5297 | 2385 | 0 | 16
38959.5302 | 2259 | 0 | 16
38959.5307 | 2184 | 0 | 16
38959.5312 | 2162 | 0 | 16
38959.5317 | 2142 | 0 | 16
38959.5321 | 1988 | 0 | 16
38959.5326 | 2030 | 0 | 16
38959.5331 | 2287 | 0 | 16
38959.5336 | 2445 | 0 | 16
38959.5341 | 1927 | 0 | 16
38959.5346 | 2468 | 0 | 16
38959.5351 | 2034 | 0 | 16
16
38959.4962 | 1 | 0 | 17
38959.4967 | 1 | 0 | 17
38959.4972 | 1 | 0 | 17
38959.4977 | 1 | 0 | 17
38959.4981 | 1 | 0 | 17
38959.4986 | 1 | 0 | 17
38959.4991 | 1 | 0 | 17
38959.4996 | 1 | 0 | 17
38959.5001 | 1 | 0 | 17
38959.5006 | 1 | 0 | 17
38959.5011 | 1 | 0 | 17
38959.5015 | 1 | 0 | 17
38959.502 | 1 | 0 | 17
38959.5025 | 1 | 0 | 17
38959.503 | 1 | 0 | 17
38959.5035 | 1 | 0 | 17
38959.504 | 1 | 0 | 17
38959.5045 | 1 | 0 | 17
38959.5049 | 1 | 0 | 17
38959.5054 | 1 | 0 | 17
38959.5059 | 1 | 0 | 17
38959.5064 | 1 | 0 | 17
38959.5069 | 1 | 0 | 17
38959.5074 | 1 | 0 | 17
38959.5079 | 1 | 0 | 17
38959.5083 | 1 | 0 | 17
38959.5088 | 1 | 0 | 17
38959.5093 | 1 | 0 | 17
38959.5098 | 1 | 0 | 17
38959.5103 | 1 | 0 | 17
38959.5108 | 1 | 0 | 17
38959.5113 | 1 | 0 | 17
38959.5117 | 1 | 0 | 17
38959.5122 | 1 | 0 | 17
38959.5127 | 2 | 0 | 17
38959.5132 | 2 | 0 | 17
38959.5137 | 3 | 0 | 17
38959.5142 | 3 | 0 | 17
38959.5147 | 3 | 0 | 17
38959.5152 | 3 | 0 | 17
38959.5156 | 3 | 0 | 17
38959.5161 | 3 | 0 | 17
38959.5166 | 2 | 0 | 17
38959.5171 | 3 | 0 | 17
38959.5176 | 3 | 0 | 17
38959.5181 | 3 | 0 | 17
38959.5186 | 3 | 0 | 17
38959.519 | 2 | 0 | 17
38959.5195 | 2 | 0 | 17
38959.52 | 2 | 1 | 17
38959.5205 | 3 | 0 | 17
38959.521 | 3 | 0 | 17
38959.5215 | 2 | 0 | 17
38959.522 | 3 | 0 | 17
38959.5224 | 2 | 0 | 17
38959.5229 | 3 | 0 | 17
38959.5234 | 2 | 0 | 17
38959.5239 | 3 | 0 | 17
38959.5244 | 2 | 0 | 17
38959.5249 | 2 | 0 | 17
38959.5254 | 2 | 0 | 17
38959.5258 | 3 | 0 | 17
38959.5263 | 2 | 0 | 17
38959.5268 | 3 | 0 | 17
38959.5273 | 3 | 0 | 17
38959.5278 | 5 | 0 | 17
38959.5283 | 14 | 0 | 17
38959.5288 | 30 | 0 | 17
38959.5292 | 52 | 0 | 17
38959.5297 | 99 | 0 | 17
38959.5302 | 109 | 0 | 17
38959.5307 | 174 | 0 | 17
38959.5312 | 1879 | 0 | 17
38959.5317 | 2005 | 0 | 17
38959.5322 | 2166 | 0 | 17
38959.5327 | 2179 | 0 | 17
38959.5331 | 2205 | 0 | 17
38959.5336 | 2006 | 0 | 17
38959.5341 | 1833 | 0 | 17
38959.5346 | 2216 | 0 | 17
38959.5351 | 1954 | 0 | 17
17
38959.4962 | 1 | 0 | 18
38959.4967 | 1 | 0 | 18
38959.4972 | 1 | 0 | 18
38959.4977 | 1 | 0 | 18
38959.4981 | 1 | 0 | 18
38959.4986 | 1 | 0 | 18
38959.4991 | 1 | 0 | 18
38959.4996 | 1 | 0 | 18
38959.5001 | 1 | 0 | 18
38959.5006 | 1 | 0 | 18
38959.5011 | 1 | 0 | 18
38959.5016 | 1 | 0 | 18
38959.502 | 1 | 0 | 18
38959.5025 | 1 | 0 | 18
38959.503 | 1 | 0 | 18
38959.5035 | 1 | 0 | 18
38959.504 | 1 | 0 | 18
38959.5045 | 1 | 0 | 18
38959.505 | 1 | 0 | 18
38959.5054 | 1 | 0 | 18
38959.5059 | 1 | 0 | 18
38959.5064 | 1 | 0 | 18
38959.5069 | 1 | 0 | 18
38959.5074 | 1 | 0 | 18
38959.5079 | 1 | 0 | 18
38959.5084 | 1 | 0 | 18
38959.5088 | 1 | 0 | 18
38959.5093 | 1 | 0 | 18
38959.5098 | 1 | 0 | 18
38959.5103 | 1 | 0 | 18
38959.5108 | 1 | 0 | 18
38959.5113 | 1 | 0 | 18
38959.5118 | 1 | 0 | 18
38959.5122 | 543 | 0 | 18
38959.5127 | 1302 | 0 | 18
38959.5132 | 2367 | 0 | 18
38959.5137 | 2264 | 0 | 18
38959.5142 | 2340 | 0 | 18
38959.5147 | 2426 | 0 | 18
38959.5152 | 2027 | 0 | 18
38959.5156 | 1942 | 0 | 18
38959.5161 | 2217 | 0 | 18
38959.5166 | 2446 | 0 | 18
38959.5171 | 2386 | 0 | 18
38959.5176 | 2175 | 0 | 18
38959.5181 | 1958 | 0 | 18
38959.5186 | 1886 | 0 | 18
38959.5191 | 2349 | 0 | 18
38959.5195 | 2161 | 0 | 18
38959.52 | 2011 | 0 | 18
38959.5205 | 2269 | 0 | 18
38959.521 | 2444 | 0 | 18
38959.5215 | 2449 | 0 | 18
38959.522 | 2048 | 0 | 18
38959.5225 | 2205 | 0 | 18
38959.5229 | 2371 | 0 | 18
38959.5234 | 2090 | 0 | 18
38959.5239 | 2016 | 0 | 18
38959.5244 | 2382 | 0 | 18
38959.5249 | 2259 | 0 | 18
38959.5254 | 2160 | 0 | 18
38959.5259 | 2314 | 0 | 18
38959.5263 | 2018 | 0 | 18
38959.5268 | 1930 | 0 | 18
38959.5273 | 2227 | 0 | 18
38959.5278 | 2012 | 0 | 18
38959.5283 | 2365 | 0 | 18
38959.5288 | 2408 | 0 | 18
38959.5293 | 2362 | 0 | 18
38959.5297 | 1920 | 0 | 18
38959.5302 | 2063 | 0 | 18
38959.5307 | 2236 | 0 | 18
38959.5312 | 2424 | 0 | 18
38959.5317 | 2458 | 0 | 18
38959.5322 | 1999 | 0 | 18
38959.5327 | 2161 | 0 | 18
38959.5331 | 2453 | 0 | 18
38959.5336 | 2007 | 0 | 18
38959.5341 | 1906 | 0 | 18
38959.5346 | 2081 | 0 | 18
38959.5351 | 2346 | 0 | 18
18
38959.4962 | 1 | 0 | 19
38959.4967 | 1 | 0 | 19
38959.4972 | 1 | 0 | 19
38959.4977 | 1 | 0 | 19
38959.4982 | 1 | 0 | 19
38959.4987 | 1 | 0 | 19
38959.4991 | 1 | 0 | 19
38959.4996 | 1 | 0 | 19
38959.5001 | 1 | 0 | 19
38959.5006 | 1 | 0 | 19
38959.5011 | 1 | 0 | 19
38959.5016 | 1 | 0 | 19
38959.5021 | 1 | 0 | 19
38959.5025 | 1 | 0 | 19
38959.503 | 1 | 0 | 19
38959.5035 | 1 | 0 | 19
38959.504 | 1 | 0 | 19
38959.5045 | 1 | 0 | 19
38959.505 | 1 | 0 | 19
38959.5055 | 1 | 0 | 19
38959.5059 | 1 | 0 | 19
38959.5064 | 1 | 0 | 19
38959.5069 | 1 | 0 | 19
38959.5074 | 1 | 0 | 19
38959.5079 | 1 | 0 | 19
38959.5084 | 1 | 0 | 19
38959.5089 | 1 | 0 | 19
38959.5094 | 1 | 0 | 19
38959.5098 | 1 | 0 | 19
38959.5103 | 1 | 0 | 19
38959.5108 | 1 | 0 | 19
38959.5113 | 1 | 0 | 19
38959.5118 | 1 | 0 | 19
38959.5123 | 1 | 0 | 19
38959.5128 | 3 | 0 | 19
38959.5132 | 3 | 0 | 19
38959.5137 | 3 | 0 | 19
38959.5142 | 3 | 0 | 19
38959.5147 | 3 | 0 | 19
38959.5152 | 3 | 0 | 19
38959.5157 | 3 | 0 | 19
38959.5162 | 24 | 0 | 19
38959.5166 | 1469 | 0 | 19
38959.5171 | 2268 | 0 | 19
38959.5176 | 2322 | 0 | 19
38959.5181 | 2234 | 0 | 19
38959.5186 | 2360 | 1 | 19
38959.5191 | 2038 | 1 | 19
38959.5196 | 2063 | 1 | 19
38959.52 | 2433 | 0 | 19
38959.5205 | 2412 | 0 | 19
38959.521 | 1913 | 0 | 19
38959.5215 | 1977 | 0 | 19
38959.522 | 1982 | 0 | 19
38959.5225 | 2027 | 0 | 19
38959.523 | 2308 | 0 | 19
38959.5234 | 2441 | 0 | 19
38959.5239 | 2424 | 0 | 19
38959.5244 | 1901 | 0 | 19
38959.5249 | 2344 | 0 | 19
38959.5254 | 1940 | 0 | 19
38959.5259 | 1993 | 0 | 19
38959.5264 | 2129 | 0 | 19
38959.5268 | 2368 | 0 | 19
38959.5273 | 2147 | 0 | 19
38959.5278 | 2176 | 0 | 19
38959.5283 | 2418 | 0 | 19
38959.5288 | 2429 | 0 | 19
38959.5293 | 2118 | 0 | 19
38959.5298 | 2128 | 0 | 19
38959.5302 | 1979 | 0 | 19
38959.5307 | 2078 | 0 | 19
38959.5312 | 2136 | 0 | 19
38959.5317 | 2227 | 0 | 19
38959.5322 | 2089 | 0 | 19
38959.5327 | 2005 | 0 | 19
38959.5332 | 2000 | 0 | 19
38959.5336 | 2447 | 0 | 19
38959.5341 | 2385 | 0 | 19
38959.5346 | 2017 | 0 | 19
38959.5351 | 2096 | 1 | 19
19
38959.4962 | 1 | 0 | 20
38959.4967 | 1 | 0 | 20
38959.4972 | 1 | 0 | 20
38959.4977 | 1 | 0 | 20
38959.4982 | 1 | 0 | 20
38959.4987 | 1 | 0 | 20
38959.4992 | 1 | 0 | 20
38959.4996 | 1 | 0 | 20
38959.5001 | 1 | 0 | 20
38959.5006 | 1 | 0 | 20
38959.5011 | 1 | 0 | 20
38959.5016 | 1 | 0 | 20
38959.5021 | 1 | 0 | 20
38959.5026 | 1 | 0 | 20
38959.503 | 1 | 0 | 20
38959.5035 | 1 | 0 | 20
38959.504 | 1 | 0 | 20
38959.5045 | 1 | 0 | 20
38959.505 | 1 | 0 | 20
38959.5055 | 1 | 0 | 20
38959.506 | 1 | 0 | 20
38959.5064 | 1 | 0 | 20
38959.5069 | 1 | 0 | 20
38959.5074 | 1 | 0 | 20
38959.5079 | 1 | 0 | 20
38959.5084 | 1 | 0 | 20
38959.5089 | 1 | 0 | 20
38959.5094 | 1 | 0 | 20
38959.5098 | 1 | 0 | 20
38959.5103 | 1 | 0 | 20
38959.5108 | 1 | 0 | 20
38959.5113 | 1 | 0 | 20
38959.5118 | 1 | 0 | 20
38959.5123 | 1 | 0 | 20
38959.5128 | 2 | 0 | 20
38959.5133 | 2 | 0 | 20
38959.5137 | 3 | 0 | 20
38959.5142 | 2 | 0 | 20
38959.5147 | 2 | 0 | 20
38959.5152 | 2 | 0 | 20
38959.5157 | 2 | 0 | 20
38959.5162 | 103 | 0 | 20
38959.5167 | 895 | 0 | 20
38959.5171 | 1231 | 0 | 20
38959.5176 | 1158 | 0 | 20
38959.5181 | 1604 | 0 | 20
38959.5186 | 2200 | 1 | 20
38959.5191 | 2121 | 1 | 20
38959.5196 | 2028 | 1 | 20
38959.5201 | 1911 | 0 | 20
38959.5205 | 2034 | 0 | 20
38959.521 | 1976 | 0 | 20
38959.5215 | 1831 | 0 | 20
38959.522 | 2176 | 0 | 20
38959.5225 | 2202 | 0 | 20
38959.523 | 1900 | 0 | 20
38959.5235 | 2129 | 0 | 20
38959.5239 | 2077 | 0 | 20
38959.5244 | 1846 | 0 | 20
38959.5249 | 2373 | 0 | 20
38959.5254 | 2388 | 0 | 20
38959.5259 | 2244 | 0 | 20
38959.5264 | 2349 | 0 | 20
38959.5269 | 2148 | 0 | 20
38959.5273 | 2213 | 0 | 20
38959.5278 | 1936 | 0 | 20
38959.5283 | 2092 | 0 | 20
38959.5288 | 1989 | 0 | 20
38959.5293 | 1867 | 0 | 20
38959.5298 | 2108 | 0 | 20
38959.5303 | 2164 | 0 | 20
38959.5308 | 2219 | 1 | 20
38959.5312 | 1970 | 0 | 20
38959.5317 | 2065 | 0 | 20
38959.5322 | 2393 | 1 | 20
38959.5327 | 2056 | 0 | 20
38959.5332 | 2280 | 0 | 20
38959.5337 | 2135 | 0 | 20
38959.5342 | 2034 | 0 | 20
38959.5346 | 2152 | 1 | 20
38959.5351 | 2255 | 1 | 20
20
38959.4963 | 1 | 0 | 21
38959.4967 | 1 | 0 | 21
38959.4972 | 1 | 0 | 21
38959.4977 | 1 | 0 | 21
38959.4982 | 1 | 0 | 21
38959.4987 | 1 | 0 | 21
38959.4992 | 1 | 0 | 21
38959.4997 | 1 | 0 | 21
38959.5002 | 1 | 0 | 21
38959.5006 | 1 | 0 | 21
38959.5011 | 1 | 0 | 21
38959.5016 | 1 | 0 | 21
38959.5021 | 1 | 0 | 21
38959.5026 | 1 | 0 | 21
38959.5031 | 1 | 0 | 21
38959.5036 | 1 | 0 | 21
38959.504 | 1 | 0 | 21
38959.5045 | 1 | 0 | 21
38959.505 | 1 | 0 | 21
38959.5055 | 1 | 0 | 21
38959.506 | 1 | 0 | 21
38959.5065 | 1 | 0 | 21
38959.507 | 1 | 0 | 21
38959.5074 | 1 | 0 | 21
38959.5079 | 1 | 0 | 21
38959.5084 | 1 | 0 | 21
38959.5089 | 1 | 0 | 21
38959.5094 | 1 | 0 | 21
38959.5099 | 1 | 0 | 21
38959.5103 | 1 | 0 | 21
38959.5108 | 1 | 0 | 21
38959.5113 | 1 | 0 | 21
38959.5118 | 1 | 0 | 21
38959.5123 | 1 | 0 | 21
38959.5128 | 2 | 0 | 21
38959.5133 | 2 | 0 | 21
38959.5138 | 2 | 0 | 21
38959.5142 | 2 | 0 | 21
38959.5147 | 2 | 0 | 21
38959.5152 | 2 | 0 | 21
38959.5157 | 2 | 0 | 21
38959.5162 | 139 | 0 | 21
38959.5167 | 1738 | 0 | 21
38959.5172 | 2008 | 0 | 21
38959.5176 | 1943 | 0 | 21
38959.5181 | 2124 | 0 | 21
38959.5186 | 2068 | 0 | 21
38959.5191 | 2312 | 0 | 21
38959.5196 | 2321 | 0 | 21
38959.5201 | 1893 | 0 | 21
38959.5206 | 2345 | 0 | 21
38959.521 | 1987 | 0 | 21
38959.5215 | 1960 | 0 | 21
38959.522 | 1980 | 0 | 21
38959.5225 | 2435 | 0 | 21
38959.523 | 2452 | 0 | 21
38959.5235 | 2267 | 0 | 21
38959.524 | 2329 | 0 | 21
38959.5244 | 2458 | 0 | 21
38959.5249 | 2313 | 0 | 21
38959.5254 | 2182 | 1 | 21
38959.5259 | 2285 | 0 | 21
38959.5264 | 2278 | 0 | 21
38959.5269 | 1953 | 0 | 21
38959.5274 | 2006 | 0 | 21
38959.5278 | 1916 | 0 | 21
38959.5283 | 2422 | 0 | 21
38959.5288 | 2419 | 0 | 21
38959.5293 | 2295 | 0 | 21
38959.5298 | 2372 | 0 | 21
38959.5303 | 2127 | 0 | 21
38959.5308 | 2092 | 0 | 21
38959.5312 | 1975 | 0 | 21
38959.5317 | 2223 | 0 | 21
38959.5322 | 2425 | 0 | 21
38959.5327 | 1973 | 0 | 21
38959.5332 | 1912 | 0 | 21
38959.5337 | 2464 | 0 | 21
38959.5342 | 2239 | 0 | 21
38959.5347 | 2289 | 0 | 21
38959.5351 | 2061 | 0 | 21
21
38959.4963 | 1 | 0 | 22
38959.4968 | 1 | 0 | 22
38959.4972 | 1 | 0 | 22
38959.4977 | 1 | 0 | 22
38959.4982 | 1 | 0 | 22
38959.4987 | 1 | 0 | 22
38959.4992 | 1 | 0 | 22
38959.4997 | 1 | 0 | 22
38959.5002 | 1 | 0 | 22
38959.5006 | 1 | 0 | 22
38959.5011 | 1 | 0 | 22
38959.5016 | 1 | 0 | 22
38959.5021 | 1 | 0 | 22
38959.5026 | 1 | 0 | 22
38959.5031 | 1 | 0 | 22
38959.5036 | 1 | 0 | 22
38959.5041 | 1 | 0 | 22
38959.5045 | 1 | 0 | 22
38959.505 | 1 | 0 | 22
38959.5055 | 1 | 0 | 22
38959.506 | 1 | 0 | 22
38959.5065 | 1 | 0 | 22
38959.507 | 1 | 0 | 22
38959.5075 | 1 | 0 | 22
38959.5079 | 1 | 0 | 22
38959.5084 | 1 | 0 | 22
38959.5089 | 1 | 0 | 22
38959.5094 | 1 | 0 | 22
38959.5099 | 1 | 0 | 22
38959.5104 | 1 | 0 | 22
38959.5109 | 1 | 0 | 22
38959.5113 | 1 | 0 | 22
38959.5118 | 1 | 0 | 22
38959.5123 | 1 | 0 | 22
38959.5128 | 1960 | 0 | 22
38959.5133 | 1925 | 0 | 22
38959.5138 | 2276 | 0 | 22
38959.5143 | 2053 | 0 | 22
38959.5147 | 2262 | 0 | 22
38959.5152 | 2322 | 0 | 22
38959.5157 | 2166 | 0 | 22
38959.5162 | 2134 | 0 | 22
38959.5167 | 2291 | 0 | 22
38959.5172 | 1845 | 0 | 22
38959.5177 | 1934 | 0 | 22
38959.5181 | 1978 | 0 | 22
38959.5186 | 2021 | 0 | 22
38959.5191 | 1992 | 1 | 22
38959.5196 | 2461 | 0 | 22
38959.5201 | 2061 | 0 | 22
38959.5206 | 1912 | 0 | 22
38959.5211 | 2344 | 0 | 22
38959.5216 | 2187 | 0 | 22
38959.522 | 2400 | 0 | 22
38959.5225 | 1964 | 0 | 22
38959.523 | 2327 | 0 | 22
38959.5235 | 1921 | 0 | 22
38959.524 | 1940 | 0 | 22
38959.5245 | 2002 | 0 | 22
38959.525 | 1931 | 0 | 22
38959.5254 | 2479 | 0 | 22
38959.5259 | 2087 | 0 | 22
38959.5264 | 2395 | 0 | 22
38959.5269 | 2238 | 0 | 22
38959.5274 | 1955 | 0 | 22
38959.5279 | 2044 | 0 | 22
38959.5284 | 2158 | 0 | 22
38959.5288 | 2235 | 0 | 22
38959.5293 | 2128 | 0 | 22
38959.5298 | 1944 | 0 | 22
38959.5303 | 2028 | 0 | 22
38959.5308 | 1955 | 0 | 22
38959.5313 | 2108 | 0 | 22
38959.5318 | 2475 | 0 | 22
38959.5322 | 2346 | 0 | 22
38959.5327 | 2029 | 0 | 22
38959.5332 | 2184 | 0 | 22
38959.5337 | 1937 | 0 | 22
38959.5342 | 2250 | 0 | 22
38959.5347 | 2157 | 0 | 22
38959.5352 | 2115 | 0 | 22
22
38959.4963 | 1 | 0 | 23
38959.4968 | 1 | 0 | 23
38959.4973 | 1 | 0 | 23
38959.4977 | 1 | 0 | 23
38959.4982 | 1 | 0 | 23
38959.4987 | 1 | 0 | 23
38959.4992 | 1 | 0 | 23
38959.4997 | 1 | 0 | 23
38959.5002 | 1 | 0 | 23
38959.5007 | 1 | 0 | 23
38959.5011 | 1 | 0 | 23
38959.5016 | 1 | 0 | 23
38959.5021 | 1 | 0 | 23
38959.5026 | 1 | 0 | 23
38959.5031 | 1 | 0 | 23
38959.5036 | 1 | 0 | 23
38959.5041 | 1 | 0 | 23
38959.5045 | 1 | 0 | 23
38959.505 | 1 | 0 | 23
38959.5055 | 1 | 0 | 23
38959.506 | 1 | 0 | 23
38959.5065 | 1 | 0 | 23
38959.507 | 1 | 0 | 23
38959.5075 | 1 | 0 | 23
38959.508 | 1 | 0 | 23
38959.5084 | 1 | 0 | 23
38959.5089 | 1 | 0 | 23
38959.5094 | 1 | 0 | 23
38959.5099 | 1 | 0 | 23
38959.5104 | 1 | 0 | 23
38959.5109 | 1 | 0 | 23
38959.5114 | 1 | 0 | 23
38959.5118 | 1 | 0 | 23
38959.5123 | 1 | 0 | 23
38959.5128 | 3 | 0 | 23
38959.5133 | 3 | 0 | 23
38959.5138 | 3 | 0 | 23
38959.5143 | 3 | 0 | 23
38959.5148 | 3 | 0 | 23
38959.5152 | 3 | 0 | 23
38959.5157 | 3 | 0 | 23
38959.5162 | 242 | 0 | 23
38959.5167 | 1931 | 0 | 23
38959.5172 | 1888 | 0 | 23
38959.5177 | 2115 | 0 | 23
38959.5182 | 2075 | 0 | 23
38959.5186 | 2180 | 0 | 23
38959.5191 | 2161 | 0 | 23
38959.5196 | 2052 | 0 | 23
38959.5201 | 2439 | 0 | 23
38959.5206 | 2362 | 0 | 23
38959.5211 | 1895 | 0 | 23
38959.5216 | 2114 | 0 | 23
38959.522 | 2024 | 0 | 23
38959.5225 | 1984 | 0 | 23
38959.523 | 2447 | 0 | 23
38959.5235 | 2009 | 0 | 23
38959.524 | 2348 | 0 | 23
38959.5245 | 2170 | 0 | 23
38959.525 | 1900 | 0 | 23
38959.5255 | 2097 | 0 | 23
38959.5259 | 2286 | 0 | 23
38959.5264 | 2279 | 0 | 23
38959.5269 | 2104 | 0 | 23
38959.5274 | 2340 | 0 | 23
38959.5279 | 2199 | 0 | 23
38959.5284 | 2417 | 0 | 23
38959.5289 | 2438 | 0 | 23
38959.5293 | 2124 | 0 | 23
38959.5298 | 2463 | 0 | 23
38959.5303 | 2398 | 0 | 23
38959.5308 | 2137 | 0 | 23
38959.5313 | 2436 | 0 | 23
38959.5318 | 1945 | 0 | 23
38959.5323 | 2233 | 0 | 23
38959.5327 | 2248 | 0 | 23
38959.5332 | 2381 | 0 | 23
38959.5337 | 2032 | 0 | 23
38959.5342 | 1914 | 0 | 23
38959.5347 | 2251 | 0 | 23
38959.5352 | 1991 | 0 | 23
23
38959.4963 | 1 | 0 | 24
38959.4968 | 1 | 0 | 24
38959.4973 | 1 | 0 | 24
38959.4978 | 1 | 0 | 24
38959.4983 | 1 | 0 | 24
38959.4987 | 1 | 0 | 24
38959.4992 | 1 | 0 | 24
38959.4997 | 1 | 0 | 24
38959.5002 | 1 | 0 | 24
38959.5007 | 1 | 0 | 24
38959.5012 | 1 | 0 | 24
38959.5017 | 1 | 0 | 24
38959.5021 | 1 | 0 | 24
38959.5026 | 1 | 0 | 24
38959.5031 | 1 | 0 | 24
38959.5036 | 1 | 0 | 24
38959.5041 | 1 | 0 | 24
38959.5046 | 1 | 0 | 24
38959.5051 | 1 | 0 | 24
38959.5055 | 1 | 0 | 24
38959.506 | 1 | 0 | 24
38959.5065 | 1 | 0 | 24
38959.507 | 1 | 0 | 24
38959.5075 | 1 | 0 | 24
38959.508 | 1 | 0 | 24
38959.5085 | 1 | 0 | 24
38959.5089 | 1 | 0 | 24
38959.5094 | 1 | 0 | 24
38959.5099 | 1 | 0 | 24
38959.5104 | 1 | 0 | 24
38959.5109 | 1 | 0 | 24
38959.5114 | 1 | 0 | 24
38959.5119 | 1 | 0 | 24
38959.5123 | 62 | 0 | 24
38959.5128 | 731 | 0 | 24
38959.5133 | 2432 | 0 | 24
38959.5138 | 2287 | 0 | 24
38959.5143 | 2354 | 0 | 24
38959.5148 | 2235 | 0 | 24
38959.5153 | 1938 | 0 | 24
38959.5158 | 1968 | 0 | 24
38959.5162 | 2428 | 0 | 24
38959.5167 | 1975 | 0 | 24
38959.5172 | 2334 | 0 | 24
38959.5177 | 2055 | 0 | 24
38959.5182 | 1885 | 0 | 24
38959.5187 | 1988 | 0 | 24
38959.5192 | 1960 | 0 | 24
38959.5196 | 2130 | 0 | 24
38959.5201 | 2134 | 0 | 24
38959.5206 | 2173 | 0 | 24
38959.5211 | 2445 | 0 | 24
38959.5216 | 2430 | 0 | 24
38959.5221 | 2369 | 0 | 24
38959.5226 | 2414 | 0 | 24
38959.523 | 2355 | 0 | 24
38959.5235 | 2227 | 0 | 24
38959.524 | 1923 | 0 | 24
38959.5245 | 2407 | 0 | 24
38959.525 | 2440 | 0 | 24
38959.5255 | 2146 | 0 | 24
38959.5259 | 2119 | 0 | 24
38959.5264 | 1913 | 0 | 24
38959.5269 | 2276 | 0 | 24
38959.5274 | 2430 | 0 | 24
38959.5279 | 2251 | 0 | 24
38959.5284 | 2009 | 0 | 24
38959.5289 | 2237 | 0 | 24
38959.5294 | 2472 | 0 | 24
38959.5298 | 2001 | 0 | 24
38959.5303 | 2244 | 0 | 24
38959.5308 | 2300 | 0 | 24
38959.5313 | 2164 | 0 | 24
38959.5318 | 2140 | 0 | 24
38959.5323 | 1939 | 0 | 24
38959.5328 | 2429 | 0 | 24
38959.5332 | 2167 | 0 | 24
38959.5337 | 2127 | 0 | 24
38959.5342 | 2092 | 0 | 24
38959.5347 | 2382 | 0 | 24
38959.5352 | 2000 | 0 | 24
24
38959.4963 | 1 | 0 | 25
38959.4968 | 1 | 0 | 25
38959.4973 | 1 | 0 | 25
38959.4978 | 1 | 0 | 25
38959.4983 | 1 | 0 | 25
38959.4987 | 1 | 0 | 25
38959.4992 | 1 | 0 | 25
38959.4997 | 1 | 0 | 25
38959.5002 | 1 | 0 | 25
38959.5007 | 1 | 0 | 25
38959.5012 | 1 | 0 | 25
38959.5017 | 1 | 0 | 25
38959.5022 | 1 | 0 | 25
38959.5026 | 1 | 0 | 25
38959.5031 | 1 | 0 | 25
38959.5036 | 1 | 0 | 25
38959.5041 | 1 | 0 | 25
38959.5046 | 1 | 0 | 25
38959.5051 | 1 | 0 | 25
38959.5056 | 1 | 0 | 25
38959.506 | 1 | 0 | 25
38959.5065 | 1 | 0 | 25
38959.507 | 1 | 0 | 25
38959.5075 | 1 | 0 | 25
38959.508 | 1 | 0 | 25
38959.5085 | 1 | 0 | 25
38959.509 | 1 | 0 | 25
38959.5094 | 1 | 0 | 25
38959.5099 | 1 | 0 | 25
38959.5104 | 1 | 0 | 25
38959.5109 | 1 | 0 | 25
38959.5114 | 1 | 0 | 25
38959.5119 | 1 | 0 | 25
38959.5124 | 2 | 0 | 25
38959.5128 | 2 | 0 | 25
38959.5133 | 3 | 0 | 25
38959.5138 | 3 | 0 | 25
38959.5143 | 3 | 0 | 25
38959.5148 | 3 | 0 | 25
38959.5153 | 3 | 0 | 25
38959.5158 | 3 | 0 | 25
38959.5163 | 283 | 0 | 25
38959.5167 | 1058 | 0 | 25
38959.5172 | 1119 | 0 | 25
38959.5177 | 1021 | 0 | 25
38959.5182 | 1366 | 0 | 25
38959.5187 | 2193 | 0 | 25
38959.5192 | 2038 | 0 | 25
38959.5197 | 2236 | 0 | 25
38959.5201 | 2054 | 0 | 25
38959.5206 | 1855 | 0 | 25
38959.5211 | 2062 | 0 | 25
38959.5216 | 1833 | 0 | 25
38959.5221 | 2311 | 0 | 25
38959.5226 | 2189 | 0 | 25
38959.5231 | 2138 | 0 | 25
38959.5235 | 2375 | 0 | 25
38959.524 | 2173 | 0 | 25
38959.5245 | 2286 | 0 | 25
38959.525 | 2013 | 0 | 25
38959.5255 | 2299 | 0 | 25
38959.526 | 2214 | 0 | 25
38959.5265 | 2368 | 0 | 25
38959.5269 | 2302 | 0 | 25
38959.5274 | 2101 | 0 | 25
38959.5279 | 2200 | 0 | 25
38959.5284 | 2390 | 0 | 25
38959.5289 | 2393 | 0 | 25
38959.5294 | 2212 | 0 | 25
38959.5299 | 2398 | 0 | 25
38959.5303 | 2425 | 0 | 25
38959.5308 | 2044 | 0 | 25
38959.5313 | 2399 | 0 | 25
38959.5318 | 2040 | 0 | 25
38959.5323 | 1990 | 0 | 25
38959.5328 | 1894 | 0 | 25
38959.5333 | 2283 | 0 | 25
38959.5338 | 2433 | 0 | 25
38959.5342 | 2287 | 0 | 25
38959.5347 | 1995 | 0 | 25
38959.5352 | 2107 | 0 | 25
25
38959.4963 | 1 | 0 | 26
38959.4968 | 1 | 0 | 26
38959.4973 | 1 | 0 | 26
38959.4978 | 1 | 0 | 26
38959.4983 | 1 | 0 | 26
38959.4988 | 1 | 0 | 26
38959.4993 | 1 | 0 | 26
38959.4997 | 1 | 0 | 26
38959.5002 | 1 | 0 | 26
38959.5007 | 1 | 0 | 26
38959.5012 | 1 | 0 | 26
38959.5017 | 1 | 0 | 26
38959.5022 | 1 | 0 | 26
38959.5027 | 1 | 0 | 26
38959.5031 | 1 | 0 | 26
38959.5036 | 1 | 0 | 26
38959.5041 | 1 | 0 | 26
38959.5046 | 1 | 0 | 26
38959.5051 | 1 | 0 | 26
38959.5056 | 1 | 0 | 26
38959.5061 | 1 | 0 | 26
38959.5065 | 1 | 0 | 26
38959.507 | 1 | 0 | 26
38959.5075 | 1 | 0 | 26
38959.508 | 1 | 0 | 26
38959.5085 | 1 | 0 | 26
38959.509 | 1 | 0 | 26
38959.5095 | 1 | 0 | 26
38959.51 | 1 | 0 | 26
38959.5104 | 1 | 0 | 26
38959.5109 | 1 | 0 | 26
38959.5114 | 1 | 0 | 26
38959.5119 | 1 | 0 | 26
38959.5124 | 1 | 0 | 26
38959.5129 | 2046 | 0 | 26
38959.5134 | 2312 | 0 | 26
38959.5138 | 2359 | 0 | 26
38959.5143 | 2166 | 0 | 26
38959.5148 | 1905 | 0 | 26
38959.5153 | 2124 | 0 | 26
38959.5158 | 2001 | 0 | 26
38959.5163 | 2067 | 0 | 26
38959.5167 | 2318 | 0 | 26
38959.5172 | 1924 | 0 | 26
38959.5177 | 2074 | 0 | 26
38959.5182 | 2324 | 0 | 26
38959.5187 | 2028 | 0 | 26
38959.5192 | 2459 | 0 | 26
38959.5197 | 2060 | 0 | 26
38959.5202 | 2044 | 0 | 26
38959.5206 | 2465 | 0 | 26
38959.5211 | 2092 | 0 | 26
38959.5216 | 2166 | 0 | 26
38959.5221 | 1946 | 0 | 26
38959.5226 | 2098 | 0 | 26
38959.5231 | 2213 | 0 | 26
38959.5236 | 2021 | 0 | 26
38959.524 | 2140 | 0 | 26
38959.5245 | 2104 | 0 | 26
38959.525 | 2479 | 0 | 26
38959.5255 | 1972 | 0 | 26
38959.526 | 2136 | 0 | 26
38959.5265 | 2097 | 0 | 26
38959.527 | 2485 | 0 | 26
38959.5274 | 2141 | 0 | 26
38959.5279 | 2091 | 0 | 26
38959.5284 | 2043 | 0 | 26
38959.5289 | 2220 | 0 | 26
38959.5294 | 2391 | 0 | 26
38959.5299 | 2329 | 0 | 26
38959.5304 | 2206 | 0 | 26
38959.5308 | 2423 | 0 | 26
38959.5313 | 2484 | 0 | 26
38959.5318 | 2483 | 0 | 26
38959.5323 | 1974 | 0 | 26
38959.5328 | 2386 | 0 | 26
38959.5333 | 2437 | 0 | 26
38959.5338 | 2438 | 0 | 26
38959.5342 | 2100 | 0 | 26
38959.5347 | 2081 | 0 | 26
38959.5352 | 2395 | 0 | 26
26
38959.4964 | 1 | 0 | 27
38959.4968 | 1 | 0 | 27
38959.4973 | 9 | 0 | 27
38959.4978 | 1 | 0 | 27
38959.4983 | 1 | 0 | 27
38959.4988 | 1 | 0 | 27
38959.4993 | 1 | 0 | 27
38959.4998 | 1 | 0 | 27
38959.5002 | 1 | 0 | 27
38959.5007 | 1 | 0 | 27
38959.5012 | 1 | 0 | 27
38959.5022 | 1 | 0 | 27
38959.5027 | 1 | 0 | 27
38959.5032 | 1 | 0 | 27
38959.5036 | 1 | 0 | 27
38959.5041 | 1 | 0 | 27
38959.5046 | 1 | 0 | 27
38959.5051 | 1 | 0 | 27
38959.5056 | 1 | 0 | 27
38959.5061 | 1 | 0 | 27
38959.5066 | 1 | 0 | 27
38959.507 | 1 | 0 | 27
38959.5075 | 1 | 0 | 27
38959.508 | 1 | 0 | 27
38959.5085 | 1 | 0 | 27
38959.509 | 1 | 0 | 27
38959.5095 | 1 | 0 | 27
38959.51 | 1 | 0 | 27
38959.5105 | 1 | 0 | 27
38959.5109 | 1 | 0 | 27
38959.5114 | 1 | 0 | 27
38959.5119 | 1 | 0 | 27
38959.5124 | 1 | 0 | 27
38959.5129 | 3 | 0 | 27
38959.5134 | 3 | 0 | 27
38959.5139 | 3 | 0 | 27
38959.5143 | 3 | 0 | 27
38959.5148 | 3 | 0 | 27
38959.5153 | 3 | 0 | 27
38959.5158 | 3 | 0 | 27
38959.5163 | 491 | 0 | 27
38959.5168 | 978 | 0 | 27
38959.5173 | 1113 | 0 | 27
38959.5177 | 1143 | 0 | 27
38959.5182 | 1813 | 0 | 27
38959.5187 | 2197 | 0 | 27
38959.5192 | 2083 | 0 | 27
38959.5197 | 1867 | 0 | 27
38959.5202 | 1847 | 0 | 27
38959.5207 | 2359 | 0 | 27
38959.5211 | 2114 | 0 | 27
38959.5216 | 2285 | 0 | 27
38959.5221 | 2129 | 0 | 27
38959.5226 | 2175 | 0 | 27
38959.5231 | 2093 | 0 | 27
38959.5236 | 1933 | 0 | 27
38959.5241 | 1868 | 0 | 27
38959.5245 | 2230 | 0 | 27
38959.525 | 2326 | 0 | 27
38959.5255 | 1904 | 0 | 27
38959.526 | 1931 | 0 | 27
38959.5265 | 1977 | 0 | 27
38959.527 | 2379 | 0 | 27
38959.5275 | 1863 | 0 | 27
38959.528 | 2405 | 0 | 27
38959.5284 | 2323 | 0 | 27
38959.5289 | 2409 | 0 | 27
38959.5294 | 2288 | 0 | 27
38959.5299 | 1977 | 0 | 27
38959.5304 | 2061 | 0 | 27
38959.5309 | 2088 | 0 | 27
38959.5314 | 2015 | 0 | 27
38959.5318 | 2386 | 0 | 27
38959.5323 | 2105 | 0 | 27
38959.5328 | 1958 | 0 | 27
38959.5333 | 2430 | 0 | 27
38959.5338 | 1986 | 0 | 27
38959.5343 | 1981 | 0 | 27
38959.5348 | 2311 | 0 | 27
38959.5352 | 2435 | 0 | 27
27
38959.4964 | 1 | 0 | 28
38959.4969 | 1 | 0 | 28
38959.4973 | 1 | 0 | 28
38959.4978 | 1 | 0 | 28
38959.4983 | 1 | 0 | 28
38959.4988 | 1 | 0 | 28
38959.4993 | 1 | 0 | 28
38959.4998 | 1 | 0 | 28
38959.5003 | 1 | 0 | 28
38959.5007 | 1 | 0 | 28
38959.5012 | 1 | 0 | 28
38959.5017 | 1 | 0 | 28
38959.5022 | 1 | 0 | 28
38959.5027 | 1 | 0 | 28
38959.5032 | 1 | 0 | 28
38959.5037 | 1 | 0 | 28
38959.5041 | 1 | 0 | 28
38959.5046 | 1 | 0 | 28
38959.5051 | 1 | 0 | 28
38959.5056 | 1 | 0 | 28
38959.5061 | 1 | 0 | 28
38959.5066 | 1 | 0 | 28
38959.5071 | 1 | 0 | 28
38959.5075 | 1 | 0 | 28
38959.508 | 1 | 0 | 28
38959.5085 | 1 | 0 | 28
38959.509 | 1 | 0 | 28
38959.5095 | 1 | 0 | 28
38959.51 | 1 | 0 | 28
38959.5105 | 1 | 0 | 28
38959.5109 | 1 | 0 | 28
38959.5114 | 1 | 0 | 28
38959.5119 | 1 | 0 | 28
38959.5124 | 1012 | 0 | 28
38959.5129 | 1594 | 0 | 28
38959.5134 | 2046 | 0 | 28
38959.5139 | 2011 | 0 | 28
38959.5144 | 2126 | 0 | 28
38959.5148 | 2202 | 0 | 28
38959.5153 | 2277 | 0 | 28
38959.5158 | 2294 | 0 | 28
38959.5163 | 2443 | 0 | 28
38959.5168 | 2233 | 0 | 28
38959.5173 | 2090 | 0 | 28
38959.5178 | 2444 | 0 | 28
38959.5182 | 2208 | 0 | 28
38959.5187 | 1989 | 0 | 28
38959.5192 | 2044 | 0 | 28
38959.5197 | 2155 | 0 | 28
38959.5202 | 2445 | 0 | 28
38959.5207 | 2447 | 0 | 28
38959.5212 | 1904 | 0 | 28
38959.5216 | 2074 | 0 | 28
38959.5221 | 2185 | 0 | 28
38959.5226 | 2440 | 0 | 28
38959.5231 | 2245 | 0 | 28
38959.5236 | 2260 | 0 | 28
38959.5241 | 2457 | 0 | 28
38959.5246 | 2416 | 0 | 28
38959.525 | 2390 | 0 | 28
38959.5255 | 1964 | 0 | 28
38959.526 | 2463 | 0 | 28
38959.5265 | 2342 | 0 | 28
38959.527 | 2080 | 0 | 28
38959.5275 | 1938 | 0 | 28
38959.528 | 2474 | 0 | 28
38959.5284 | 2285 | 0 | 28
38959.5289 | 1916 | 0 | 28
38959.5294 | 2108 | 0 | 28
38959.5299 | 1915 | 0 | 28
38959.5304 | 2467 | 0 | 28
38959.5309 | 1907 | 0 | 28
38959.5314 | 2301 | 0 | 28
38959.5319 | 2246 | 0 | 28
38959.5323 | 2253 | 0 | 28
38959.5328 | 1997 | 0 | 28
38959.5333 | 2395 | 0 | 28
38959.5338 | 1958 | 0 | 28
38959.5343 | 2451 | 0 | 28
38959.5348 | 2252 | 0 | 28
38959.5353 | 2447 | 0 | 28
28
38959.4964 | 1 | 0 | 29
38959.4969 | 1 | 0 | 29
38959.4974 | 1 | 0 | 29
38959.4978 | 1 | 0 | 29
38959.4983 | 1 | 0 | 29
38959.4988 | 1 | 0 | 29
38959.4993 | 1 | 0 | 29
38959.4998 | 1 | 0 | 29
38959.5003 | 1 | 0 | 29
38959.5008 | 1 | 0 | 29
38959.5013 | 1 | 0 | 29
38959.5017 | 1 | 0 | 29
38959.5022 | 1 | 0 | 29
38959.5027 | 1 | 0 | 29
38959.5032 | 1 | 0 | 29
38959.5037 | 1 | 0 | 29
38959.5042 | 1 | 0 | 29
38959.5047 | 1 | 0 | 29
38959.5051 | 1 | 0 | 29
38959.5056 | 1 | 0 | 29
38959.5061 | 1 | 0 | 29
38959.5066 | 1 | 0 | 29
38959.5071 | 1 | 0 | 29
38959.5076 | 1 | 0 | 29
38959.5081 | 1 | 0 | 29
38959.5085 | 1 | 0 | 29
38959.509 | 1 | 0 | 29
38959.5095 | 1 | 0 | 29
38959.51 | 1 | 0 | 29
38959.5105 | 1 | 0 | 29
38959.511 | 1 | 0 | 29
38959.5115 | 1 | 0 | 29
38959.5119 | 1 | 0 | 29
38959.5124 | 463 | 0 | 29
38959.5129 | 1951 | 0 | 29
38959.5134 | 2107 | 0 | 29
38959.5139 | 1932 | 0 | 29
38959.5144 | 2405 | 0 | 29
38959.5149 | 2370 | 1 | 29
38959.5153 | 2001 | 1 | 29
38959.5158 | 2429 | 1 | 29
38959.5163 | 2077 | 0 | 29
38959.5168 | 1926 | 0 | 29
38959.5173 | 2059 | 1 | 29
38959.5178 | 1911 | 0 | 29
38959.5183 | 1971 | 0 | 29
38959.5188 | 2234 | 0 | 29
38959.5192 | 2020 | 0 | 29
38959.5197 | 2351 | 0 | 29
38959.5202 | 2347 | 0 | 29
38959.5207 | 2449 | 0 | 29
38959.5212 | 2268 | 0 | 29
38959.5217 | 2318 | 0 | 29
38959.5222 | 2430 | 0 | 29
38959.5226 | 2461 | 0 | 29
38959.5231 | 2180 | 0 | 29
38959.5236 | 1971 | 0 | 29
38959.5241 | 2034 | 0 | 29
38959.5246 | 1979 | 0 | 29
38959.5251 | 2334 | 0 | 29
38959.5256 | 2051 | 0 | 29
38959.526 | 2375 | 0 | 29
38959.5265 | 2174 | 0 | 29
38959.527 | 2328 | 0 | 29
38959.5275 | 2224 | 0 | 29
38959.528 | 2277 | 0 | 29
38959.5285 | 2287 | 0 | 29
38959.5289 | 2256 | 0 | 29
38959.5294 | 2262 | 0 | 29
38959.5299 | 2168 | 0 | 29
38959.5304 | 1972 | 0 | 29
38959.5309 | 2431 | 0 | 29
38959.5314 | 2067 | 0 | 29
38959.5319 | 2102 | 0 | 29
38959.5323 | 2366 | 0 | 29
38959.5328 | 2208 | 0 | 29
38959.5333 | 2438 | 0 | 29
38959.5338 | 1916 | 0 | 29
38959.5343 | 2053 | 0 | 29
38959.5348 | 2291 | 0 | 29
38959.5353 | 2413 | 0 | 29
29
38959.4964 | 1 | 0 | 30
38959.4969 | 1 | 0 | 30
38959.4974 | 1 | 0 | 30
38959.4979 | 1 | 0 | 30
38959.4983 | 1 | 0 | 30
38959.4988 | 1 | 0 | 30
38959.4993 | 1 | 0 | 30
38959.4998 | 1 | 0 | 30
38959.5003 | 1 | 0 | 30
38959.5008 | 1 | 0 | 30
38959.5013 | 1 | 0 | 30
38959.5017 | 1 | 0 | 30
38959.5022 | 1 | 0 | 30
38959.5027 | 1 | 0 | 30
38959.5032 | 1 | 0 | 30
38959.5037 | 1 | 0 | 30
38959.5042 | 1 | 0 | 30
38959.5047 | 1 | 0 | 30
38959.5052 | 1 | 0 | 30
38959.5056 | 1 | 0 | 30
38959.5061 | 1 | 0 | 30
38959.5066 | 1 | 0 | 30
38959.5071 | 1 | 0 | 30
38959.5076 | 1 | 0 | 30
38959.5081 | 1 | 0 | 30
38959.5086 | 1 | 0 | 30
38959.509 | 1 | 0 | 30
38959.5095 | 1 | 0 | 30
38959.51 | 1 | 0 | 30
38959.5105 | 1 | 0 | 30
38959.511 | 1 | 0 | 30
38959.5115 | 1 | 0 | 30
38959.512 | 1 | 0 | 30
38959.5124 | 1555 | 0 | 30
38959.5129 | 2028 | 0 | 30
38959.5134 | 2111 | 0 | 30
38959.5139 | 1962 | 0 | 30
38959.5144 | 2465 | 0 | 30
38959.5149 | 1968 | 0 | 30
38959.5154 | 1900 | 1 | 30
38959.5158 | 2237 | 1 | 30
38959.5163 | 2022 | 1 | 30
38959.5168 | 2325 | 1 | 30
38959.5173 | 2032 | 0 | 30
38959.5178 | 1930 | 1 | 30
38959.5183 | 2262 | 0 | 30
38959.5188 | 1984 | 0 | 30
38959.5192 | 2017 | 0 | 30
38959.5197 | 2423 | 0 | 30
38959.5202 | 1993 | 0 | 30
38959.5207 | 2289 | 1 | 30
38959.5212 | 2051 | 0 | 30
38959.5217 | 2454 | 0 | 30
38959.5222 | 1970 | 0 | 30
38959.5227 | 2257 | 0 | 30
38959.5231 | 2034 | 0 | 30
38959.5236 | 2158 | 0 | 30
38959.5241 | 2140 | 0 | 30
38959.5246 | 2451 | 0 | 30
38959.5251 | 2070 | 0 | 30
38959.5256 | 2095 | 0 | 30
38959.5261 | 2084 | 0 | 30
38959.5265 | 1958 | 0 | 30
38959.527 | 2466 | 0 | 30
38959.5275 | 2414 | 0 | 30
38959.528 | 2051 | 0 | 30
38959.5285 | 2448 | 0 | 30
38959.529 | 1976 | 0 | 30
38959.5295 | 2447 | 0 | 30
38959.5299 | 2036 | 0 | 30
38959.5304 | 2157 | 0 | 30
38959.5309 | 2468 | 0 | 30
38959.5314 | 2125 | 0 | 30
38959.5319 | 2389 | 0 | 30
38959.5324 | 2334 | 0 | 30
38959.5329 | 2005 | 0 | 30
38959.5333 | 1978 | 0 | 30
38959.5338 | 2052 | 0 | 30
38959.5343 | 2018 | 0 | 30
38959.5348 | 2110 | 0 | 30
38959.5353 | 1942 | 0 | 30
30

## Test Facts
Last row in IRMS data sheets: | 86
Time when Penlight power was initiated: | 127